## Test Conditions
DESIREE-FIRE Intermediate Scale Test 2 - Circuit Simulator Data Only
Test Date: | 2009-12-02
DCSim DAQ Start Time | 12:25
DCSim Time for Synchronization | 12:27
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 12:26
Fire Time | 13:59
Offset | 1:34 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 5640 | seconds
Heat Source Offset | 1:33 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 5605 | seconds
Heat Source Stop Time | 15:40
Test Duration | 1:41 | hour:minutes:seconds
| 6060 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 2, 3, and 4 represents the air temperature 3', 5', and 7' down the cable tray located in C-Position. These are labeled as "C-Position - 3'", "C-Position - Middle", " C-Position - 7'", respectively.
SOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 which is defined as "A Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.85938 | 121.7651 | -61.528 | 60.1135 | 1.4211e-13 | -0.026572 | 0.0014317 | 0.064073 | -0.0058951 | 0.05482 | -0.0099192 | -0.0016621 | -0.00084406 | 0.064052 | 0.020442 | 0.059231 | -61.5508 | 0.015142 | -61.6092 | 59.9924 | 59.9568 | 59.8378 | -61.5397 | -61.5277 | 0.073618 | -61.6217 | 59.7927 | 59.9247 | 59.9462 | -61.676 | -0.011683 | -0.12114 | -0.022784 | -0.081159 | -0.069476 | -0.15673 | -0.27574 | -0.14796 | -0.32086 | 0.00036 | -0.093669 | 0.054295 | -0.18881 | -0.16729 | 121.5204 | 121.4848 | 121.3658 | 61.5432 | -121.6532 | 121.3207 | 121.4527 | 121.4743 | 61.6016 | -121.7895
0.875 | 121.7743 | -61.5372 | 60.1089 | 1.4211e-13 | -0.026572 | 0.0016453 | 0.063645 | -0.0056813 | 0.05482 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.020015 | 0.059445 | -61.5462 | 0.010564 | -61.6046 | 59.9832 | 59.9705 | 59.8332 | -61.5489 | -61.5231 | 0.06904 | -61.6263 | 59.7927 | 59.9247 | 59.9417 | -61.676 | -0.011686 | -0.12572 | -0.00905 | -0.067426 | -0.05574 | -0.13841 | -0.27574 | -0.13881 | -0.31628 | 0.014093 | -0.089093 | 0.049716 | -0.18423 | -0.16729 | 121.5204 | 121.5077 | 121.3704 | 61.5477 | -121.6578 | 121.3298 | 121.4619 | 121.4788 | 61.6062 | -121.7849
2.5469 | 121.7606 | -61.6058 | 60.0311 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.063645 | -0.0056813 | 0.05482 | -0.01755 | -0.0014485 | -0.0016987 | 0.063838 | 0.020015 | 0.059872 | -61.5508 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8286 | -61.5397 | -61.5368 | 0.073618 | -61.6263 | 59.7927 | 59.9339 | 59.9417 | -61.6806 | 0.066137 | -0.043325 | 0.055036 | 0.005818 | -0.060319 | -0.060594 | -0.2025 | -0.074723 | -0.23846 | 0.069022 | -0.020428 | 0.054295 | -0.09725 | -0.08947 | 121.5936 | 121.5764 | 121.4345 | 61.6256 | -121.5708 | 121.3985 | 121.5397 | 121.5475 | 61.6795 | -121.7117
4.2812 | 121.8613 | -61.5509 | 60.0174 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063432 | -0.0058951 | 0.055033 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063624 | 0.020442 | 0.059231 | -61.5508 | 0.0243 | -61.6 | 59.9878 | 59.9614 | 59.8286 | -61.5397 | -61.5322 | 0.06904 | -61.6263 | 59.7881 | 59.9293 | 59.9462 | -61.676 | 0.011205 | -0.029592 | 0.000104 | -0.049114 | -0.060319 | -0.056019 | -0.18877 | -0.12508 | -0.22931 | 0.018669 | -0.07536 | 0.049716 | -0.088096 | -0.071159 | 121.5387 | 121.5123 | 121.3795 | 61.5752 | -121.5571 | 121.339 | 121.4802 | 121.4971 | 61.6199 | -121.6934
6.0156 | 121.8979 | -61.5646 | 59.9945 | 1.4211e-13 | -0.026572 | 0.0012179 | 0.063645 | -0.0056813 | 0.055033 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.020656 | 0.059231 | -61.5416 | 0.015142 | -61.6092 | 59.9924 | 59.9614 | 59.8286 | -61.5305 | -61.5277 | 0.078197 | -61.6263 | 59.7972 | 59.9385 | 59.9417 | -61.676 | 0.034096 | -0.002125 | 0.022994 | -0.044538 | -0.078634 | -0.033131 | -0.16588 | -0.11134 | -0.19727 | 0.036981 | -0.061627 | 0.049716 | -0.056051 | -0.052849 | 121.557 | 121.526 | 121.3933 | 61.5798 | -121.525 | 121.3619 | 121.5031 | 121.5063 | 61.6428 | -121.6705
7.7031 | 121.8338 | -61.5143 | 60.0952 | 1.4211e-13 | -0.026572 | 0.0014317 | 0.063859 | -0.0061087 | 0.05482 | 0.0053413 | -0.0018757 | -0.0012713 | 0.063624 | 0.020228 | 0.059445 | -61.5508 | 0.015142 | -61.6046 | 59.9924 | 59.966 | 59.8286 | -61.5443 | -61.5231 | 0.073618 | -61.6308 | 59.7927 | 59.9247 | 59.9417 | -61.676 | -0.029995 | -0.10283 | -0.036517 | -0.090314 | -0.060319 | -0.12926 | -0.26659 | -0.1617 | -0.30255 | -0.008795 | -0.11656 | 0.045138 | -0.1705 | -0.15356 | 121.5067 | 121.4802 | 121.3429 | 61.5294 | -121.6395 | 121.3069 | 121.439 | 121.4559 | 61.5879 | -121.7712
9.4375 | 121.8658 | -61.5601 | 59.9899 | 1.4211e-13 | -0.026786 | 0.0018589 | 0.063859 | -0.0061087 | 0.054392 | -0.0022892 | -0.0018757 | -0.00084406 | 0.064052 | 0.020228 | 0.059445 | -61.5462 | 0.015142 | -61.6092 | 59.9924 | 59.966 | 59.8378 | -61.5351 | -61.5277 | 0.078197 | -61.6308 | 59.7881 | 59.9339 | 59.9508 | -61.6668 | 0.02494 | 0.002453 | 0.013839 | -0.049115 | -0.074055 | -0.023974 | -0.15214 | -0.10676 | -0.20184 | 0.032404 | -0.070782 | 0.03598 | -0.056051 | -0.039114 | 121.5524 | 121.526 | 121.3978 | 61.5752 | -121.525 | 121.3481 | 121.4939 | 121.5109 | 61.6383 | -121.6567
11.1094 | 121.9025 | -61.5601 | 59.9716 | 1.4211e-13 | -0.026786 | 0.0012179 | 0.063432 | -0.0056813 | 0.05482 | -0.01755 | -0.0016621 | -0.0010577 | 0.063838 | 0.020442 | 0.059658 | -61.5508 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8332 | -61.5397 | -61.5277 | 0.078197 | -61.6263 | 59.7927 | 59.9247 | 59.9371 | -61.6714 | 0.020361 | 0.016184 | 0.00926 | -0.039958 | -0.060319 | -0.001085 | -0.13841 | -0.11134 | -0.17895 | 0.032404 | -0.066204 | 0.045137 | -0.046899 | -0.03454 | 121.5479 | 121.5306 | 121.3933 | 61.5798 | -121.5113 | 121.3527 | 121.4848 | 121.4971 | 61.6383 | -121.643
12.8594 | 121.7743 | -61.5463 | 60.1273 | 1.4211e-13 | -0.026359 | 0.0014317 | 0.063432 | -0.0061087 | 0.054606 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064052 | 0.020228 | 0.059445 | -61.5508 | 0.015142 | -61.6046 | 59.9924 | 59.9568 | 59.8378 | -61.5397 | -61.5277 | 0.073618 | -61.6263 | 59.7972 | 59.9293 | 59.9508 | -61.676 | 0.006628 | -0.13488 | -0.004473 | -0.05827 | -0.064898 | -0.17046 | -0.28947 | -0.12965 | -0.33002 | 0.018671 | -0.079937 | 0.049716 | -0.19796 | -0.17644 | 121.5387 | 121.5031 | 121.3841 | 61.5615 | -121.667 | 121.3436 | 121.4756 | 121.4971 | 61.6199 | -121.8032
14.5312 | 121.8155 | -61.5463 | 60.0632 | 1.4211e-13 | -0.026786 | 0.0018589 | 0.063859 | -0.0063223 | 0.05482 | -0.0099192 | -0.0020893 | -0.0014849 | 0.063838 | 0.020015 | 0.059445 | -61.5462 | 0.015142 | -61.6046 | 59.9924 | 59.9614 | 59.8286 | -61.5351 | -61.5231 | 0.073618 | -61.6263 | 59.7927 | 59.9293 | 59.9371 | -61.6806 | 0.011207 | -0.070789 | 0.000106 | -0.05827 | -0.069477 | -0.10179 | -0.23454 | -0.13423 | -0.27051 | 0.023249 | -0.079937 | 0.054295 | -0.13387 | -0.12609 | 121.5387 | 121.5077 | 121.375 | 61.5615 | -121.5983 | 121.339 | 121.4756 | 121.4834 | 61.6199 | -121.7437
16.25 | 121.8475 | -61.5601 | 60.0403 | 1.4211e-13 | -0.027 | 0.0010043 | 0.063645 | -0.0054677 | 0.05482 | -0.01755 | -0.0016621 | -0.0010577 | 0.063838 | 0.020656 | 0.059231 | -61.5508 | 0.019721 | -61.6 | 59.997 | 59.9705 | 59.8332 | -61.5397 | -61.5185 | 0.073618 | -61.6263 | 59.7927 | 59.9247 | 59.9417 | -61.676 | 0.020361 | -0.043323 | 0.00926 | -0.039958 | -0.060319 | -0.069749 | -0.20708 | -0.11592 | -0.24762 | 0.041561 | -0.066204 | 0.049716 | -0.11556 | -0.098625 | 121.557 | 121.5306 | 121.3933 | 61.5798 | -121.58 | 121.3527 | 121.4848 | 121.5017 | 61.6337 | -121.7163
18 | 121.9116 | -61.5143 | 60.0403 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.063645 | -0.0056813 | 0.054392 | -0.0022892 | -0.0012349 | -0.0010577 | 0.064265 | 0.020442 | 0.059445 | -61.5508 | 0.019721 | -61.6092 | 59.9878 | 59.966 | 59.8332 | -61.5443 | -61.5322 | 0.073618 | -61.6217 | 59.7927 | 59.9247 | 59.9417 | -61.6806 | -0.029995 | -0.05248 | -0.036517 | -0.094892 | -0.064897 | -0.074328 | -0.20708 | -0.16628 | -0.24762 | -0.017952 | -0.1074 | 0.058874 | -0.11556 | -0.098625 | 121.5021 | 121.4802 | 121.3475 | 61.534 | -121.5846 | 121.3069 | 121.439 | 121.4559 | 61.5879 | -121.7208
19.75 | 121.8063 | -61.5326 | 60.0815 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063645 | -0.0061087 | 0.05482 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.020442 | 0.059658 | -61.5508 | 0.015142 | -61.6046 | 59.9878 | 59.9705 | 59.8286 | -61.5397 | -61.5368 | 0.073618 | -61.6308 | 59.7927 | 59.9293 | 59.9371 | -61.676 | -0.007105 | -0.093679 | -0.018206 | -0.072003 | -0.064898 | -0.11095 | -0.25285 | -0.14339 | -0.28882 | -0.00422 | -0.098248 | 0.045138 | -0.15218 | -0.1444 | 121.5204 | 121.5031 | 121.3612 | 61.5477 | -121.6212 | 121.3253 | 121.4619 | 121.4697 | 61.6062 | -121.7575
21.4219 | 121.9025 | -61.4914 | 60.054 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.063645 | -0.0061087 | 0.054606 | -0.01755 | -0.0016621 | -0.0012713 | 0.063624 | 0.020442 | 0.059658 | -61.5462 | 0.019721 | -61.6 | 59.9924 | 59.9614 | 59.824 | -61.5489 | -61.5277 | 0.06904 | -61.6263 | 59.7927 | 59.9201 | 59.9462 | -61.6714 | -0.057462 | -0.061634 | -0.054826 | -0.10862 | -0.051161 | -0.09264 | -0.22997 | -0.18001 | -0.26135 | -0.036261 | -0.13487 | 0.045137 | -0.13387 | -0.10778 | 121.4838 | 121.4528 | 121.3154 | 61.5111 | -121.6029 | 121.2841 | 121.4115 | 121.4376 | 61.5604 | -121.7254
23.1562 | 121.7697 | -61.5234 | 60.1135 | 1.4211e-13 | -0.026572 | 0.0014317 | 0.063645 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.020442 | 0.059658 | -61.5416 | 0.019721 | -61.6 | 59.9832 | 59.9568 | 59.8286 | -61.5397 | -61.5185 | 0.073618 | -61.6263 | 59.8018 | 59.9247 | 59.9508 | -61.676 | -0.016261 | -0.1303 | -0.018205 | -0.07658 | -0.060319 | -0.15673 | -0.2849 | -0.15254 | -0.3117 | 0.004939 | -0.10283 | 0.049716 | -0.18881 | -0.16271 | 121.5067 | 121.4802 | 121.3521 | 61.5432 | -121.6532 | 121.3253 | 121.4482 | 121.4743 | 61.5971 | -121.7895
24.8906 | 121.8887 | -61.5143 | 60.022 | 1.4211e-13 | -0.026786 | 0.0016453 | 0.063645 | -0.0061087 | 0.054606 | -0.0022892 | -0.0012349 | -0.0010577 | 0.064265 | 0.020442 | 0.059872 | -61.5462 | 0.019721 | -61.6046 | 59.9786 | 59.9705 | 59.8286 | -61.5443 | -61.5231 | 0.073618 | -61.6308 | 59.7927 | 59.9247 | 59.9371 | -61.6714 | -0.029995 | -0.043327 | -0.031938 | -0.090314 | -0.060319 | -0.051439 | -0.19335 | -0.15712 | -0.22931 | -0.008795 | -0.11656 | 0.040559 | -0.097253 | -0.084894 | 121.4929 | 121.4848 | 121.3429 | 61.534 | -121.5662 | 121.3069 | 121.439 | 121.4514 | 61.5879 | -121.6934
26.5625 | 121.8109 | -61.5189 | 60.0632 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063859 | -0.0056813 | 0.054606 | -0.01755 | -0.0016621 | -0.0014849 | 0.063838 | 0.020015 | 0.059658 | -61.5416 | 0.019721 | -61.6 | 59.9832 | 59.9614 | 59.8378 | -61.5397 | -61.5231 | 0.078197 | -61.6263 | 59.7881 | 59.9293 | 59.9462 | -61.6714 | -0.020838 | -0.079946 | -0.022782 | -0.081157 | -0.060319 | -0.10179 | -0.22538 | -0.15254 | -0.27509 | -0.004217 | -0.1074 | 0.045137 | -0.13387 | -0.11693 | 121.5021 | 121.4802 | 121.3566 | 61.5386 | -121.6029 | 121.3069 | 121.4482 | 121.4651 | 61.5971 | -121.7346
28.2969 | 121.7972 | -61.5326 | 60.1044 | 1.4211e-13 | -0.026786 | 0.0012179 | 0.063645 | -0.0061087 | 0.054392 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064265 | 0.020442 | 0.059445 | -61.5462 | 0.0243 | -61.6046 | 59.9878 | 59.9568 | 59.8332 | -61.5489 | -61.5231 | 0.06904 | -61.6308 | 59.7972 | 59.9339 | 59.9417 | -61.6714 | -0.016263 | -0.11657 | -0.013627 | -0.072003 | -0.05574 | -0.14757 | -0.27116 | -0.13881 | -0.30713 | 0.009516 | -0.098248 | 0.040559 | -0.17049 | -0.16271 | 121.5204 | 121.4894 | 121.3658 | 61.5569 | -121.6532 | 121.3298 | 121.4665 | 121.4743 | 61.6016 | -121.7758
30.0469 | 121.8475 | -61.5326 | 60.0723 | 1.4211e-13 | -0.026786 | 0.0012179 | 0.063645 | -0.0056813 | 0.054606 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.020228 | 0.059658 | -61.5508 | 0.015142 | -61.6092 | 59.9878 | 59.966 | 59.8286 | -61.5397 | -61.5322 | 0.073618 | -61.6308 | 59.7927 | 59.9293 | 59.9371 | -61.676 | -0.007105 | -0.084524 | -0.018206 | -0.076581 | -0.069476 | -0.10637 | -0.2437 | -0.14339 | -0.27966 | 0.000359 | -0.098248 | 0.045138 | -0.14303 | -0.13525 | 121.5204 | 121.4985 | 121.3612 | 61.5477 | -121.612 | 121.3253 | 121.4619 | 121.4697 | 61.6062 | -121.7483
31.7344 | 121.7926 | -61.5967 | 60.0357 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.064073 | -0.0063223 | 0.054392 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.020442 | 0.059445 | -61.5462 | 0.0243 | -61.6 | 59.997 | 59.9614 | 59.8378 | -61.5443 | -61.5231 | 0.06904 | -61.6263 | 59.7881 | 59.9247 | 59.9508 | -61.6806 | 0.052403 | -0.038746 | 0.05046 | -0.003337 | -0.05574 | -0.07433 | -0.19792 | -0.083878 | -0.24762 | 0.073603 | -0.029583 | 0.054295 | -0.11099 | -0.084891 | 121.5936 | 121.5581 | 121.4345 | 61.621 | -121.58 | 121.3848 | 121.5214 | 121.5475 | 61.6657 | -121.7163
33.4844 | 121.8018 | -61.5417 | 60.1044 | 1.4211e-13 | -0.026786 | 0.0016453 | 0.063432 | -0.0061087 | 0.054606 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063838 | 0.020442 | 0.059445 | -61.5462 | 0.028878 | -61.6 | 59.9832 | 59.966 | 59.8332 | -61.5443 | -61.5322 | 0.073618 | -61.6308 | 59.7972 | 59.9247 | 59.9417 | -61.6806 | -0.002529 | -0.12115 | -0.004472 | -0.058269 | -0.05574 | -0.13842 | -0.27116 | -0.13881 | -0.30713 | 0.009514 | -0.089093 | 0.049717 | -0.17965 | -0.16271 | 121.525 | 121.5077 | 121.375 | 61.5706 | -121.6486 | 121.339 | 121.4665 | 121.4834 | 61.6154 | -121.7849
35.1562 | 121.756 | -61.615 | 60.0449 | 1.4211e-13 | -0.026572 | 0.0010043 | 0.063645 | -0.0065361 | 0.055033 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.020442 | 0.059872 | -61.5462 | 0.015142 | -61.6 | 59.9878 | 59.9614 | 59.8378 | -61.5443 | -61.5277 | 0.078197 | -61.6217 | 59.7972 | 59.9385 | 59.9371 | -61.676 | 0.070713 | -0.057058 | 0.06877 | 0.014973 | -0.05574 | -0.083485 | -0.20707 | -0.060989 | -0.24762 | 0.087335 | -0.006694 | 0.054295 | -0.1064 | -0.10778 | 121.6028 | 121.5764 | 121.4528 | 61.6301 | -121.5891 | 121.4122 | 121.5534 | 121.5521 | 61.6932 | -121.7208
36.9062 | 121.8796 | -61.5005 | 60.0952 | 1.4211e-13 | -0.027213 | 0.0012179 | 0.063645 | -0.0058951 | 0.054606 | -0.01755 | -0.0016621 | -0.0014849 | 0.063624 | 0.020228 | 0.059658 | -61.5462 | 0.0243 | -61.6092 | 59.9832 | 59.966 | 59.8195 | -61.5397 | -61.5277 | 0.06904 | -61.6263 | 59.7835 | 59.9201 | 59.9462 | -61.6806 | -0.039149 | -0.11199 | -0.045671 | -0.10863 | -0.069476 | -0.12926 | -0.27574 | -0.18001 | -0.31171 | -0.027106 | -0.12571 | 0.054295 | -0.17507 | -0.14898 | 121.4838 | 121.4665 | 121.32 | 61.5248 | -121.6349 | 121.2841 | 121.4207 | 121.4468 | 61.5696 | -121.7758
38.6406 | 121.8796 | -61.6013 | 60.0082 | 1.4211e-13 | -0.026786 | 0.0010043 | 0.064073 | -0.0061087 | 0.054606 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.020442 | 0.059658 | -61.5462 | 0.028878 | -61.6046 | 59.9924 | 59.966 | 59.8378 | -61.5397 | -61.5277 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9417 | -61.6714 | 0.061559 | -0.015858 | 0.055037 | -0.003339 | -0.064898 | -0.042285 | -0.17045 | -0.070143 | -0.22931 | 0.073602 | -0.025006 | 0.045137 | -0.074362 | -0.066582 | 121.5936 | 121.5672 | 121.439 | 61.6301 | -121.5479 | 121.3802 | 121.5351 | 121.5429 | 61.6795 | -121.6796
40.3125 | 121.8567 | -61.5646 | 60.0266 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.064073 | -0.0061087 | 0.054606 | -0.0022892 | -0.0016621 | -0.0014849 | 0.064052 | 0.020442 | 0.059445 | -61.5462 | 0.015142 | -61.6046 | 59.9878 | 59.9614 | 59.8378 | -61.5351 | -61.5231 | 0.06904 | -61.6308 | 59.7789 | 59.9201 | 59.9417 | -61.676 | 0.029517 | -0.038747 | 0.018416 | -0.03996 | -0.069477 | -0.065174 | -0.18876 | -0.11134 | -0.24762 | 0.041559 | -0.066205 | 0.045138 | -0.10641 | -0.084892 | 121.5524 | 121.526 | 121.4024 | 61.5798 | -121.5617 | 121.3436 | 121.4848 | 121.5063 | 61.6337 | -121.7025
42.0469 | 121.8979 | -61.5646 | 59.9579 | 1.4211e-13 | -0.027 | 0.0018589 | 0.063218 | -0.0061087 | 0.054392 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063624 | 0.020228 | 0.059445 | -61.5462 | 0.0243 | -61.6046 | 59.9924 | 59.9705 | 59.8332 | -61.5397 | -61.5277 | 0.073618 | -61.6308 | 59.7835 | 59.9247 | 59.9325 | -61.676 | 0.024938 | 0.034496 | 0.018416 | -0.03996 | -0.064898 | 0.012648 | -0.12468 | -0.11134 | -0.17438 | 0.036981 | -0.066205 | 0.045138 | -0.033166 | -0.025386 | 121.557 | 121.5352 | 121.3978 | 61.5889 | -121.4976 | 121.3481 | 121.4894 | 121.4971 | 61.6383 | -121.6339
43.7969 | 121.8521 | -61.5463 | 60.0357 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.064073 | -0.0058951 | 0.055033 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.020656 | 0.059658 | -61.5462 | 0.028878 | -61.6046 | 59.9924 | 59.9705 | 59.8378 | -61.5443 | -61.5231 | 0.082776 | -61.6308 | 59.7835 | 59.9247 | 59.9417 | -61.6668 | 0.002049 | -0.043324 | 0.000106 | -0.05827 | -0.060319 | -0.065172 | -0.19792 | -0.12049 | -0.2522 | 0.023249 | -0.084515 | 0.03598 | -0.11099 | -0.094048 | 121.5387 | 121.5169 | 121.3841 | 61.5752 | -121.58 | 121.3298 | 121.471 | 121.488 | 61.6291 | -121.7025
45.4688 | 121.875 | -61.5738 | 59.9716 | 1.4211e-13 | -0.026572 | 0.0016453 | 0.064073 | -0.0061087 | 0.05482 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063624 | 0.020442 | 0.059445 | -61.5554 | 0.015142 | -61.6046 | 59.9924 | 59.9705 | 59.8332 | -61.5397 | -61.5185 | 0.073618 | -61.6263 | 59.7835 | 59.9247 | 59.9417 | -61.6714 | 0.034094 | 0.020763 | 0.018415 | -0.030804 | -0.064898 | -0.001085 | -0.13841 | -0.097608 | -0.18811 | 0.055294 | -0.052471 | 0.045137 | -0.046899 | -0.029961 | 121.5662 | 121.5443 | 121.407 | 61.5889 | -121.5113 | 121.3573 | 121.4985 | 121.5154 | 61.6474 | -121.643
47.2031 | 121.7651 | -61.6196 | 60.0494 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.063645 | -0.0061087 | 0.054606 | -0.0022892 | -0.0018757 | -0.0012713 | 0.064265 | 0.020656 | 0.059445 | -61.5508 | 0.019721 | -61.6 | 59.9924 | 59.966 | 59.8378 | -61.5443 | -61.5277 | 0.06904 | -61.6217 | 59.7789 | 59.9293 | 59.9462 | -61.6714 | 0.075291 | -0.057056 | 0.068769 | 0.019551 | -0.05574 | -0.083483 | -0.21165 | -0.051832 | -0.27051 | 0.091913 | -0.002116 | 0.049716 | -0.12014 | -0.1032 | 121.612 | 121.5855 | 121.4574 | 61.6393 | -121.5937 | 121.3985 | 121.5489 | 121.5658 | 61.6886 | -121.7208
48.8906 | 121.907 | -61.5051 | 60.054 | 1.4211e-13 | -0.026572 | 0.0014317 | 0.063432 | -0.0063223 | 0.05482 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063624 | 0.020442 | 0.059445 | -61.5508 | 0.015142 | -61.6 | 59.9878 | 59.966 | 59.8378 | -61.5443 | -61.5231 | 0.06904 | -61.6217 | 59.7789 | 59.9293 | 59.9371 | -61.676 | -0.03915 | -0.066213 | -0.045672 | -0.09489 | -0.05574 | -0.088061 | -0.21623 | -0.17085 | -0.27509 | -0.01795 | -0.11656 | 0.054295 | -0.12472 | -0.11694 | 121.4929 | 121.4711 | 121.3429 | 61.5203 | -121.5983 | 121.2841 | 121.4344 | 121.4422 | 61.5742 | -121.73
50.625 | 121.8704 | -61.5509 | 60.0357 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.064073 | -0.0058951 | 0.05482 | -0.0099192 | -0.0014485 | -0.0010577 | 0.064052 | 0.020656 | 0.059445 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.9614 | 59.8332 | -61.5351 | -61.5277 | 0.078197 | -61.6263 | 59.7789 | 59.9293 | 59.9462 | -61.676 | 0.015784 | -0.047903 | 0.004683 | -0.049114 | -0.064898 | -0.07433 | -0.2025 | -0.12508 | -0.25678 | 0.023248 | -0.07536 | 0.049716 | -0.10641 | -0.08947 | 121.5387 | 121.5123 | 121.3841 | 61.5706 | -121.5708 | 121.3298 | 121.4802 | 121.4971 | 61.6291 | -121.7117
52.3594 | 121.9116 | -61.5234 | 60.0266 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063432 | -0.0061087 | 0.054606 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.020656 | 0.059445 | -61.5416 | 0.0243 | -61.6092 | 59.9878 | 59.966 | 59.8286 | -61.5351 | -61.5231 | 0.078197 | -61.6171 | 59.7789 | 59.9247 | 59.9462 | -61.6668 | -0.011682 | -0.038747 | -0.018205 | -0.085737 | -0.074055 | -0.060595 | -0.19792 | -0.14338 | -0.24762 | 0.00036 | -0.093668 | 0.049716 | -0.10183 | -0.080314 | 121.5112 | 121.4894 | 121.3521 | 61.5477 | -121.5617 | 121.3024 | 121.4482 | 121.4697 | 61.6016 | -121.6934
54.0469 | 121.907 | -61.4914 | 60.0769 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063859 | -0.0061087 | 0.05482 | -0.0022892 | -0.0014485 | -0.0010577 | 0.063838 | 0.020656 | 0.059658 | -61.5508 | 0.019721 | -61.6046 | 59.9832 | 59.966 | 59.8332 | -61.5351 | -61.5231 | 0.073618 | -61.6308 | 59.7789 | 59.9293 | 59.9371 | -61.676 | -0.043725 | -0.093679 | -0.059405 | -0.1132 | -0.069477 | -0.11095 | -0.2437 | -0.18458 | -0.29798 | -0.031683 | -0.13945 | 0.045138 | -0.1476 | -0.13983 | 121.4746 | 121.4573 | 121.3246 | 61.5111 | -121.612 | 121.2703 | 121.4207 | 121.4285 | 61.565 | -121.7529
55.7812 | 121.7743 | -61.6104 | 60.0174 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063645 | -0.0061087 | 0.05482 | -0.0099192 | -0.0016621 | -0.0010577 | 0.064052 | 0.020442 | 0.059658 | -61.5462 | 0.019721 | -61.5954 | 59.9878 | 59.966 | 59.8332 | -61.5489 | -61.5277 | 0.073618 | -61.6263 | 59.7835 | 59.9247 | 59.9417 | -61.676 | 0.061557 | -0.029592 | 0.064193 | 0.014974 | -0.046583 | -0.05144 | -0.18419 | -0.065566 | -0.23389 | 0.082758 | -0.01585 | 0.049716 | -0.092675 | -0.075737 | 121.5982 | 121.5764 | 121.4436 | 61.6301 | -121.5663 | 121.3939 | 121.5351 | 121.5521 | 61.684 | -121.6934
57.4531 | 121.7834 | -61.5921 | 60.0128 | 1.4211e-13 | -0.026572 | 0.0016453 | 0.064073 | -0.0058951 | 0.054606 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.020656 | 0.059658 | -61.5462 | 0.0243 | -61.6 | 59.9924 | 59.9705 | 59.8378 | -61.5443 | -61.5277 | 0.06904 | -61.6217 | 59.7835 | 59.9293 | 59.9417 | -61.676 | 0.047825 | -0.020435 | 0.045882 | -0.007915 | -0.05574 | -0.042283 | -0.17503 | -0.083877 | -0.22931 | 0.064447 | -0.029582 | 0.054295 | -0.083518 | -0.071159 | 121.5845 | 121.5626 | 121.4299 | 61.6164 | -121.5571 | 121.3756 | 121.5214 | 121.5338 | 61.6611 | -121.6888
59.2031 | 121.8842 | -61.5097 | 60.0311 | 1.4211e-13 | -0.027 | 0.0014317 | 0.064073 | -0.0058951 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.020442 | 0.059872 | -61.5508 | 0.0243 | -61.6 | 59.9878 | 59.966 | 59.8378 | -61.5397 | -61.5185 | 0.073618 | -61.6217 | 59.7881 | 59.9247 | 59.9371 | -61.676 | -0.029993 | -0.043325 | -0.041094 | -0.090312 | -0.060319 | -0.065173 | -0.19334 | -0.16627 | -0.24304 | -0.008793 | -0.11198 | 0.054295 | -0.10641 | -0.094049 | 121.4975 | 121.4757 | 121.3475 | 61.534 | -121.5708 | 121.2978 | 121.4344 | 121.4468 | 61.5833 | -121.7071
60.9531 | 121.7743 | -61.5189 | 60.0998 | 1.4211e-13 | -0.026786 | 0.0016453 | 0.063645 | -0.0058951 | 0.05482 | -0.01755 | -0.0014485 | -0.0010577 | 0.063838 | 0.020442 | 0.059872 | -61.5508 | 0.0243 | -61.5954 | 59.9924 | 59.966 | 59.8332 | -61.5397 | -61.5277 | 0.064461 | -61.6263 | 59.7789 | 59.9293 | 59.9417 | -61.6806 | -0.020838 | -0.10741 | -0.031939 | -0.076579 | -0.055741 | -0.13384 | -0.26658 | -0.1617 | -0.32086 | -0.008795 | -0.1074 | 0.054295 | -0.17049 | -0.15813 | 121.5112 | 121.4848 | 121.3521 | 61.5432 | -121.6395 | 121.2978 | 121.4482 | 121.4605 | 61.5833 | -121.7803
62.6406 | 121.788 | -61.528 | 60.0952 | 1.4211e-13 | -0.027213 | 0.0012179 | 0.063645 | -0.0065361 | 0.054392 | -0.0099192 | -0.0018757 | -0.0010577 | 0.064052 | 0.020869 | 0.059658 | -61.5416 | 0.019721 | -61.6 | 59.9924 | 59.9614 | 59.8332 | -61.5443 | -61.5277 | 0.06904 | -61.6217 | 59.7835 | 59.9247 | 59.9325 | -61.6806 | -0.016262 | -0.10283 | -0.013627 | -0.072002 | -0.05574 | -0.13384 | -0.26201 | -0.15254 | -0.31171 | 0.00036 | -0.093669 | 0.058874 | -0.1705 | -0.16272 | 121.5204 | 121.4894 | 121.3612 | 61.5477 | -121.6395 | 121.3115 | 121.4527 | 121.4605 | 61.5971 | -121.7758
64.3906 | 121.7606 | -61.5875 | 60.0494 | 1.4211e-13 | -0.027213 | 0.0010043 | 0.064073 | -0.0063223 | 0.05482 | -0.0022892 | -0.0014485 | -0.0014849 | 0.063624 | 0.020442 | 0.059872 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8332 | -61.5397 | -61.5277 | 0.078197 | -61.6263 | 59.7835 | 59.9201 | 59.9462 | -61.6714 | 0.047826 | -0.061635 | 0.041304 | -0.012493 | -0.060319 | -0.078904 | -0.21623 | -0.083876 | -0.26593 | 0.059869 | -0.038739 | 0.045137 | -0.1293 | -0.1032 | 121.5753 | 121.5581 | 121.4207 | 61.6072 | -121.5891 | 121.371 | 121.5077 | 121.5338 | 61.6657 | -121.7208
66.0781 | 121.8018 | -61.5326 | 60.0403 | 1.4211e-13 | -0.027 | 0.0014317 | 0.064073 | -0.0061087 | 0.05482 | -0.0022892 | -0.0016621 | -0.0016987 | 0.063838 | 0.020656 | 0.059658 | -61.5508 | 0.015142 | -61.6046 | 59.9878 | 59.9614 | 59.8378 | -61.5397 | -61.5231 | 0.073618 | -61.6354 | 59.7835 | 59.9339 | 59.9417 | -61.6806 | -0.007105 | -0.05248 | -0.018206 | -0.072003 | -0.064898 | -0.078907 | -0.2025 | -0.14796 | -0.25678 | 0.009516 | -0.10283 | 0.045138 | -0.10641 | -0.098625 | 121.5204 | 121.494 | 121.3704 | 61.5477 | -121.58 | 121.3161 | 121.4665 | 121.4743 | 61.6062 | -121.7208
67.8125 | 121.8109 | -61.5601 | 60.1044 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.064073 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.020442 | 0.059231 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8378 | -61.5489 | -61.5231 | 0.078197 | -61.6217 | 59.7743 | 59.9247 | 59.9371 | -61.676 | 0.011203 | -0.11657 | 0.013839 | -0.039958 | -0.051161 | -0.13384 | -0.26658 | -0.11592 | -0.33002 | 0.036982 | -0.061625 | 0.054295 | -0.17965 | -0.16729 | 121.5479 | 121.5306 | 121.3978 | 61.5798 | -121.6532 | 121.3344 | 121.4848 | 121.4971 | 61.6383 | -121.7803
69.5 | 121.8613 | -61.5601 | 60.0174 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.020656 | 0.059658 | -61.5416 | 0.0243 | -61.6046 | 59.9832 | 59.966 | 59.8424 | -61.5443 | -61.5231 | 0.073618 | -61.6263 | 59.7835 | 59.9247 | 59.9371 | -61.6714 | 0.015782 | -0.03417 | 0.018417 | -0.044537 | -0.060319 | -0.05144 | -0.17503 | -0.11134 | -0.23389 | 0.036982 | -0.066204 | 0.045137 | -0.092675 | -0.080316 | 121.5433 | 121.526 | 121.4024 | 61.5844 | -121.5617 | 121.3436 | 121.4848 | 121.4971 | 61.6337 | -121.6888
71.2344 | 121.8109 | -61.5555 | 60.0906 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063645 | -0.0063223 | 0.054392 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.020656 | 0.059658 | -61.5371 | 0.0243 | -61.6046 | 59.997 | 59.966 | 59.8332 | -61.5397 | -61.5231 | 0.073618 | -61.6263 | 59.7743 | 59.9201 | 59.9371 | -61.6714 | 0.015783 | -0.093677 | 0.018417 | -0.049115 | -0.064898 | -0.12468 | -0.25743 | -0.11592 | -0.31629 | 0.032404 | -0.070782 | 0.045137 | -0.1705 | -0.15356 | 121.5524 | 121.5214 | 121.3887 | 61.5798 | -121.6303 | 121.3298 | 121.4756 | 121.4926 | 61.6291 | -121.762
72.9062 | 121.8933 | -61.5738 | 59.9991 | 1.4211e-13 | -0.027213 | 0.0016453 | 0.063645 | -0.0063223 | 0.054606 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.020442 | 0.059445 | -61.5462 | 0.028878 | -61.6 | 59.9924 | 59.9614 | 59.8332 | -61.5443 | -61.5185 | 0.073618 | -61.6263 | 59.7789 | 59.9247 | 59.9417 | -61.6714 | 0.029515 | -0.006702 | 0.027572 | -0.026225 | -0.05574 | -0.037708 | -0.16588 | -0.097608 | -0.22016 | 0.055294 | -0.052471 | 0.045137 | -0.074364 | -0.057426 | 121.5662 | 121.5352 | 121.407 | 61.6027 | -121.5434 | 121.3527 | 121.4985 | 121.5154 | 61.6474 | -121.6705
74.6562 | 121.788 | -61.5784 | 60.0403 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063859 | -0.0061087 | 0.054606 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.020869 | 0.059231 | -61.5508 | 0.019721 | -61.5954 | 59.9878 | 59.966 | 59.8378 | -61.5443 | -61.5185 | 0.06904 | -61.6308 | 59.7743 | 59.9247 | 59.9508 | -61.676 | 0.034092 | -0.05248 | 0.02757 | -0.01707 | -0.051162 | -0.074328 | -0.2025 | -0.09761 | -0.26593 | 0.059871 | -0.052472 | 0.045138 | -0.11556 | -0.089468 | 121.5662 | 121.5443 | 121.4162 | 61.5981 | -121.5846 | 121.3527 | 121.5031 | 121.5292 | 61.6474 | -121.7163
76.3906 | 121.8704 | -61.5189 | 60.0677 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063859 | -0.0061087 | 0.054606 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.020869 | 0.059658 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.9614 | 59.8286 | -61.5397 | -61.5185 | 0.082776 | -61.6263 | 59.7743 | 59.9339 | 59.9417 | -61.676 | -0.020838 | -0.079946 | -0.02736 | -0.081157 | -0.060319 | -0.10637 | -0.23912 | -0.15712 | -0.2934 | 0.000362 | -0.1074 | 0.049716 | -0.13387 | -0.12609 | 121.5067 | 121.4802 | 121.3475 | 61.5386 | -121.6074 | 121.2932 | 121.4527 | 121.4605 | 61.6016 | -121.7437
78.125 | 121.8887 | -61.5097 | 60.0449 | 1.4211e-13 | -0.027213 | 0.0016453 | 0.064073 | -0.0058951 | 0.05482 | -0.0022892 | -0.0016621 | -0.0014849 | 0.064052 | 0.020442 | 0.059445 | -61.5462 | 0.0243 | -61.6092 | 59.9832 | 59.966 | 59.8424 | -61.5397 | -61.5231 | 0.078197 | -61.6308 | 59.7835 | 59.9247 | 59.9417 | -61.6806 | -0.029993 | -0.061636 | -0.036515 | -0.099469 | -0.069476 | -0.078906 | -0.2025 | -0.17085 | -0.26135 | -0.013372 | -0.12114 | 0.049717 | -0.12014 | -0.1032 | 121.4929 | 121.4757 | 121.3521 | 61.534 | -121.5846 | 121.2932 | 121.4344 | 121.4514 | 61.5879 | -121.7254
79.7969 | 121.7926 | -61.6013 | 60.0311 | 1.4211e-13 | -0.026786 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | 0.0053413 | -0.0014485 | -0.0012713 | 0.064265 | 0.020228 | 0.059872 | -61.5462 | 0.0243 | -61.6046 | 59.9878 | 59.9705 | 59.8332 | -61.5489 | -61.5322 | 0.06904 | -61.6217 | 59.7881 | 59.9293 | 59.9371 | -61.676 | 0.052401 | -0.043325 | 0.055037 | -0.003339 | -0.05574 | -0.060594 | -0.19792 | -0.074722 | -0.24304 | 0.069023 | -0.020427 | 0.054295 | -0.10183 | -0.094049 | 121.5891 | 121.5718 | 121.4345 | 61.6256 | -121.58 | 121.3893 | 121.5306 | 121.5383 | 61.6703 | -121.7071
81.5469 | 121.7926 | -61.5692 | 60.054 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063624 | 0.020656 | 0.059658 | -61.5462 | 0.019721 | -61.6046 | 59.9878 | 59.9614 | 59.8378 | -61.5443 | -61.5231 | 0.064461 | -61.6217 | 59.7835 | 59.9293 | 59.9417 | -61.6714 | 0.024937 | -0.066213 | 0.022994 | -0.035382 | -0.060319 | -0.09264 | -0.21623 | -0.10219 | -0.27051 | 0.046137 | -0.05247 | 0.049716 | -0.12472 | -0.11236 | 121.557 | 121.5306 | 121.407 | 61.5889 | -121.5983 | 121.3527 | 121.4985 | 121.5109 | 61.6337 | -121.7254
83.2188 | 121.8475 | -61.5326 | 60.0952 | 1.4211e-13 | -0.027 | 0.0016453 | 0.063859 | -0.0058951 | 0.05482 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063838 | 0.020656 | 0.059445 | -61.5416 | 0.0243 | -61.5954 | 59.9924 | 59.9614 | 59.8332 | -61.5351 | -61.5185 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9462 | -61.676 | -0.002526 | -0.10283 | -0.009049 | -0.062846 | -0.06032 | -0.13384 | -0.26201 | -0.14339 | -0.31629 | 0.014095 | -0.09367 | 0.049716 | -0.16134 | -0.14898 | 121.525 | 121.494 | 121.3658 | 61.5569 | -121.6303 | 121.3115 | 121.4665 | 121.4788 | 61.6108 | -121.7712
84.9688 | 121.8658 | -61.5463 | 60.022 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.063859 | -0.0063223 | 0.05482 | 0.0053413 | -0.0020893 | -0.0014849 | 0.063838 | 0.020228 | 0.059445 | -61.5508 | 0.019721 | -61.6046 | 59.9924 | 59.9705 | 59.8332 | -61.5351 | -61.5277 | 0.078197 | -61.6263 | 59.7881 | 59.9293 | 59.9371 | -61.6714 | 0.011207 | -0.029591 | -0.004473 | -0.05827 | -0.069477 | -0.051439 | -0.18877 | -0.12507 | -0.23389 | 0.018671 | -0.079937 | 0.045137 | -0.092674 | -0.084894 | 121.5387 | 121.5169 | 121.3795 | 61.566 | -121.5571 | 121.3344 | 121.4756 | 121.4834 | 61.6245 | -121.6934
86.7188 | 121.8521 | -61.5143 | 60.0952 | 1.4211e-13 | -0.027213 | 0.0016453 | 0.063432 | -0.0061087 | 0.054392 | 0.0053413 | -0.0016621 | -0.0010577 | 0.064052 | 0.020656 | 0.059445 | -61.5462 | 0.015142 | -61.6 | 59.9924 | 59.9705 | 59.824 | -61.5397 | -61.5231 | 0.078197 | -61.6263 | 59.7789 | 59.9201 | 59.9325 | -61.676 | -0.025416 | -0.10283 | -0.031938 | -0.085735 | -0.060319 | -0.12468 | -0.27117 | -0.1617 | -0.31629 | -0.008795 | -0.11198 | 0.049716 | -0.17507 | -0.16272 | 121.5067 | 121.4848 | 121.3383 | 61.5294 | -121.6349 | 121.2932 | 121.4344 | 121.4468 | 61.5925 | -121.7712
88.4688 | 121.7743 | -61.6013 | 60.0266 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063432 | -0.0063223 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.020442 | 0.059872 | -61.5462 | 0.0243 | -61.6046 | 59.9832 | 59.966 | 59.8378 | -61.5489 | -61.5277 | 0.078197 | -61.6308 | 59.7789 | 59.9293 | 59.9417 | -61.676 | 0.052401 | -0.043325 | 0.055037 | -0.003339 | -0.05574 | -0.060595 | -0.18876 | -0.074722 | -0.24762 | 0.073602 | -0.029584 | 0.045138 | -0.097251 | -0.084892 | 121.5845 | 121.5672 | 121.439 | 61.6256 | -121.5754 | 121.3802 | 121.5306 | 121.5429 | 61.6795 | -121.7025
90.2031 | 121.756 | -61.5326 | 60.1181 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063859 | -0.0065361 | 0.054606 | -0.0099192 | -0.0012349 | -0.0012713 | 0.063624 | 0.020442 | 0.059658 | -61.5508 | 0.019721 | -61.6046 | 59.9832 | 59.9705 | 59.8332 | -61.5443 | -61.5185 | 0.06904 | -61.6263 | 59.7743 | 59.9247 | 59.9371 | -61.6714 | -0.011684 | -0.13488 | -0.018206 | -0.072003 | -0.060319 | -0.14757 | -0.2849 | -0.13881 | -0.34375 | 0.014095 | -0.09367 | 0.045137 | -0.19338 | -0.18102 | 121.5158 | 121.5031 | 121.3658 | 61.5523 | -121.6624 | 121.3069 | 121.4573 | 121.4697 | 61.6016 | -121.7895
91.9062 | 121.8567 | -61.5097 | 60.0952 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063645 | -0.0058951 | 0.05482 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.020656 | 0.059658 | -61.5508 | 0.0243 | -61.5954 | 59.9924 | 59.9751 | 59.8424 | -61.5443 | -61.5231 | 0.073618 | -61.6217 | 59.7789 | 59.9293 | 59.9371 | -61.6714 | -0.034572 | -0.10283 | -0.041094 | -0.085734 | -0.051162 | -0.1201 | -0.25285 | -0.1617 | -0.31629 | -0.013372 | -0.11198 | 0.049716 | -0.16592 | -0.15814 | 121.5021 | 121.4848 | 121.3521 | 61.534 | -121.6395 | 121.2886 | 121.439 | 121.4468 | 61.5833 | -121.7666
93.6406 | 121.9025 | -61.5051 | 60.0403 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.0645 | -0.0063223 | 0.054606 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.020656 | 0.059658 | -61.5554 | 0.0243 | -61.6046 | 59.9924 | 59.9705 | 59.8286 | -61.5397 | -61.5185 | 0.078197 | -61.6263 | 59.7789 | 59.9247 | 59.9371 | -61.6851 | -0.034571 | -0.047901 | -0.05025 | -0.099469 | -0.064898 | -0.069749 | -0.21166 | -0.18001 | -0.26136 | -0.013371 | -0.12114 | 0.058874 | -0.11556 | -0.1032 | 121.4975 | 121.4757 | 121.3338 | 61.5294 | -121.58 | 121.2841 | 121.4298 | 121.4422 | 61.5833 | -121.7254
95.3125 | 121.9025 | -61.4822 | 60.054 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063645 | -0.0065361 | 0.05482 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063838 | 0.020656 | 0.059872 | -61.5416 | 0.015142 | -61.5954 | 59.9878 | 59.9568 | 59.8286 | -61.5443 | -61.5231 | 0.073618 | -61.6217 | 59.7743 | 59.9247 | 59.9417 | -61.6714 | -0.062038 | -0.066213 | -0.059403 | -0.1132 | -0.051162 | -0.097219 | -0.22539 | -0.18916 | -0.27967 | -0.040838 | -0.13945 | 0.049716 | -0.1293 | -0.11236 | 121.47 | 121.439 | 121.3109 | 61.4974 | -121.5983 | 121.2566 | 121.407 | 121.4239 | 61.5559 | -121.7254
97.0469 | 121.8613 | -61.5921 | 59.9854 | 1.4211e-13 | -0.026786 | 0.0016453 | 0.063859 | -0.0061087 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.020869 | 0.059658 | -61.5416 | 0.019721 | -61.6 | 59.9832 | 59.9614 | 59.8469 | -61.5489 | -61.5185 | 0.073618 | -61.6308 | 59.7835 | 59.9339 | 59.9462 | -61.6714 | 0.043246 | -0.002127 | 0.05046 | -0.007915 | -0.051161 | -0.023976 | -0.13841 | -0.079298 | -0.20184 | 0.073604 | -0.038739 | 0.040559 | -0.051474 | -0.039116 | 121.5753 | 121.5535 | 121.439 | 61.6118 | -121.5342 | 121.3756 | 121.526 | 121.5383 | 61.6657 | -121.6568
98.7969 | 121.8658 | -61.5784 | 59.9899 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063645 | -0.0063223 | 0.054606 | -0.01755 | -0.0016621 | -0.0010577 | 0.064052 | 0.020656 | 0.059658 | -61.5416 | 0.0243 | -61.5954 | 59.9878 | 59.9705 | 59.8424 | -61.5305 | -61.5231 | 0.087354 | -61.6217 | 59.7881 | 59.9201 | 59.9371 | -61.676 | 0.047829 | -0.002126 | 0.036727 | -0.01707 | -0.064899 | -0.019395 | -0.14756 | -0.09761 | -0.20184 | 0.055292 | -0.043315 | 0.054295 | -0.069787 | -0.05285 | 121.5662 | 121.5489 | 121.4207 | 61.6027 | -121.5205 | 121.3665 | 121.4985 | 121.5154 | 61.6657 | -121.6659
100.5469 | 121.8979 | -61.5738 | 59.9579 | 1.4211e-13 | -0.027213 | 0.0016453 | 0.063432 | -0.0063223 | 0.054606 | -0.01755 | -0.0014485 | -0.0010577 | 0.063838 | 0.020869 | 0.059658 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9705 | 59.8286 | -61.5397 | -61.5231 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9462 | -61.676 | 0.034094 | 0.029917 | 0.03215 | -0.026225 | -0.060319 | 0.012648 | -0.12926 | -0.10219 | -0.17896 | 0.050715 | -0.052471 | 0.049716 | -0.024008 | -0.01165 | 121.5616 | 121.5443 | 121.4024 | 61.6027 | -121.4976 | 121.3527 | 121.5077 | 121.52 | 61.652 | -121.6339
102.2969 | 121.8201 | -61.5417 | 60.0586 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063859 | -0.0061087 | 0.054606 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.020656 | 0.059658 | -61.5416 | 0.019721 | -61.5954 | 59.9832 | 59.9614 | 59.8332 | -61.5443 | -61.5185 | 0.06904 | -61.6217 | 59.7789 | 59.9293 | 59.9325 | -61.6714 | -0.002529 | -0.075369 | 0.000106 | -0.053691 | -0.051162 | -0.097218 | -0.22539 | -0.12965 | -0.27967 | 0.02325 | -0.079936 | 0.049716 | -0.12929 | -0.12609 | 121.525 | 121.5031 | 121.375 | 61.5615 | -121.6029 | 121.3207 | 121.471 | 121.4742 | 61.6108 | -121.73
103.9688 | 121.843 | -61.5555 | 60.0128 | 1.4211e-13 | -0.027213 | 0.0016453 | 0.064286 | -0.0061087 | 0.054606 | -0.0022892 | -0.0018757 | -0.0014849 | 0.064052 | 0.020869 | 0.059445 | -61.5371 | 0.0243 | -61.6 | 59.9878 | 59.9614 | 59.8378 | -61.5443 | -61.5139 | 0.073618 | -61.6263 | 59.7743 | 59.9293 | 59.9371 | -61.6714 | 0.011204 | -0.025014 | 0.018417 | -0.044536 | -0.05574 | -0.051441 | -0.17503 | -0.11592 | -0.23847 | 0.041562 | -0.070782 | 0.045137 | -0.083518 | -0.075738 | 121.5433 | 121.5169 | 121.3933 | 61.5798 | -121.5571 | 121.3298 | 121.4848 | 121.4926 | 61.6291 | -121.6842
105.7031 | 121.8613 | -61.5463 | 60.0357 | 1.4211e-13 | -0.027213 | 0.0018589 | 0.064073 | -0.0063223 | 0.054606 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.020869 | 0.059872 | -61.5508 | 0.028878 | -61.6 | 59.9878 | 59.9568 | 59.8378 | -61.5443 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6714 | 0.002049 | -0.047903 | -0.004473 | -0.053691 | -0.05574 | -0.078909 | -0.19792 | -0.12507 | -0.2522 | 0.027828 | -0.075358 | 0.049716 | -0.10183 | -0.098627 | 121.5341 | 121.5031 | 121.3841 | 61.5752 | -121.58 | 121.3298 | 121.4802 | 121.4834 | 61.6199 | -121.7071
107.375 | 121.8842 | -61.5692 | 59.9808 | 1.4211e-13 | -0.027427 | 0.0016453 | 0.063645 | -0.0063223 | 0.054392 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063838 | 0.020656 | 0.059658 | -61.5416 | 0.0243 | -61.6 | 59.9832 | 59.966 | 59.8332 | -61.5397 | -61.5185 | 0.073618 | -61.6263 | 59.7881 | 59.9247 | 59.9417 | -61.6714 | 0.029516 | 0.002451 | 0.027572 | -0.030803 | -0.060319 | -0.014819 | -0.14757 | -0.10219 | -0.19269 | 0.050716 | -0.057049 | 0.045137 | -0.056054 | -0.039116 | 121.5524 | 121.5352 | 121.4024 | 61.5935 | -121.5205 | 121.3573 | 121.4939 | 121.5109 | 61.6428 | -121.6522
109.125 | 121.8842 | -61.5601 | 59.9762 | 1.4211e-13 | -0.027427 | 0.0012179 | 0.063645 | -0.0061087 | 0.05482 | -0.0099192 | -0.0018757 | -0.0014849 | 0.064265 | 0.021083 | 0.059445 | -61.5416 | 0.028878 | -61.5954 | 59.9924 | 59.966 | 59.8378 | -61.5443 | -61.5231 | 0.078197 | -61.6171 | 59.7789 | 59.9339 | 59.9371 | -61.676 | 0.015782 | 0.016186 | 0.018417 | -0.03538 | -0.051162 | -0.010241 | -0.13841 | -0.11592 | -0.19727 | 0.036982 | -0.057046 | 0.058874 | -0.042318 | -0.039117 | 121.5524 | 121.526 | 121.3978 | 61.5889 | -121.5205 | 121.339 | 121.4939 | 121.4971 | 61.6383 | -121.6522
110.875 | 121.7834 | -61.5738 | 60.0311 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063859 | -0.0063223 | 0.05482 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063838 | 0.020656 | 0.059872 | -61.5462 | 0.0243 | -61.6 | 59.997 | 59.9705 | 59.8332 | -61.5443 | -61.5322 | 0.073618 | -61.6217 | 59.7789 | 59.9293 | 59.9417 | -61.6806 | 0.029515 | -0.034168 | 0.027572 | -0.026225 | -0.05574 | -0.060594 | -0.19792 | -0.10677 | -0.2522 | 0.041558 | -0.047892 | 0.058874 | -0.10183 | -0.08947 | 121.5708 | 121.5443 | 121.407 | 61.5981 | -121.5754 | 121.3527 | 121.5031 | 121.5154 | 61.6474 | -121.7117
112.625 | 121.8796 | -61.5097 | 60.0586 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.064073 | -0.0063223 | 0.054392 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063624 | 0.020656 | 0.059445 | -61.5508 | 0.0243 | -61.5954 | 59.9832 | 59.9568 | 59.8286 | -61.5397 | -61.5185 | 0.06904 | -61.6308 | 59.7789 | 59.9293 | 59.9325 | -61.6714 | -0.029993 | -0.075369 | -0.041094 | -0.085734 | -0.055741 | -0.1018 | -0.22997 | -0.1617 | -0.27967 | -0.008793 | -0.12114 | 0.040559 | -0.12929 | -0.12609 | 121.4929 | 121.4665 | 121.3383 | 61.534 | -121.5983 | 121.2886 | 121.439 | 121.4422 | 61.5787 | -121.73
114.375 | 121.7514 | -61.615 | 60.0357 | 1.4211e-13 | -0.027427 | 0.0018589 | 0.063645 | -0.0061087 | 0.055033 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.020442 | 0.059658 | -61.5416 | 0.028878 | -61.5909 | 59.9878 | 59.966 | 59.8424 | -61.5443 | -61.5231 | 0.073618 | -61.6217 | 59.7835 | 59.9293 | 59.9462 | -61.676 | 0.070713 | -0.047903 | 0.073348 | 0.024129 | -0.046584 | -0.069751 | -0.19334 | -0.060989 | -0.2522 | 0.091913 | -0.006694 | 0.054295 | -0.10641 | -0.08947 | 121.6028 | 121.5809 | 121.4574 | 61.6439 | -121.58 | 121.3985 | 121.5443 | 121.5612 | 61.6886 | -121.7117
116.0469 | 121.907 | -61.5738 | 59.9625 | 1.4211e-13 | -0.027213 | 0.0012179 | 0.063859 | -0.0061087 | 0.05482 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064265 | 0.020656 | 0.059658 | -61.5371 | 0.028878 | -61.5909 | 59.9832 | 59.966 | 59.8332 | -61.5397 | -61.5139 | 0.078197 | -61.6308 | 59.7789 | 59.9293 | 59.9417 | -61.6806 | 0.034094 | 0.020762 | 0.036728 | -0.017069 | -0.051163 | 0.003492 | -0.12926 | -0.10677 | -0.18353 | 0.059873 | -0.057049 | 0.049717 | -0.033164 | -0.020805 | 121.557 | 121.5397 | 121.407 | 61.6027 | -121.5022 | 121.3527 | 121.5031 | 121.5154 | 61.652 | -121.643
117.7812 | 121.8567 | -61.5509 | 60.022 | 1.4211e-13 | -0.027213 | 0.0018589 | 0.063432 | -0.0063223 | 0.054606 | -0.0022892 | -0.0018757 | -0.0014849 | 0.064052 | 0.020869 | 0.059872 | -61.5462 | 0.0243 | -61.6 | 59.9878 | 59.9614 | 59.8378 | -61.5305 | -61.5185 | 0.078197 | -61.6263 | 59.7743 | 59.9339 | 59.9325 | -61.6668 | 0.020363 | -0.03417 | 0.004683 | -0.049114 | -0.069477 | -0.060597 | -0.18419 | -0.11592 | -0.24762 | 0.032405 | -0.07536 | 0.040558 | -0.088095 | -0.089473 | 121.5387 | 121.5123 | 121.3887 | 61.5752 | -121.5525 | 121.3253 | 121.4848 | 121.4834 | 61.6291 | -121.6888
119.5312 | 121.7743 | -61.5921 | 60.0082 | 1.4211e-13 | -0.027641 | 0.0012179 | 0.063432 | -0.0061087 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.020869 | 0.059658 | -61.5462 | 0.028878 | -61.6 | 59.9924 | 59.9705 | 59.8424 | -61.5443 | -61.5139 | 0.073618 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6806 | 0.047825 | -0.015858 | 0.045882 | -0.007915 | -0.05574 | -0.037706 | -0.16588 | -0.088456 | -0.22473 | 0.078183 | -0.029582 | 0.058874 | -0.074362 | -0.071161 | 121.5845 | 121.5626 | 121.4345 | 61.621 | -121.5525 | 121.3756 | 121.526 | 121.5292 | 61.6657 | -121.6888
121.2031 | 121.8155 | -61.5509 | 60.0586 | 1.4211e-13 | -0.027641 | 0.0016453 | 0.063859 | -0.0063223 | 0.05482 | -0.0022892 | -0.0014485 | -0.0010577 | 0.063624 | 0.020656 | 0.059658 | -61.5416 | 0.019721 | -61.6046 | 59.9832 | 59.966 | 59.8378 | -61.5397 | -61.5185 | 0.078197 | -61.6263 | 59.7743 | 59.9339 | 59.9417 | -61.6806 | 0.011205 | -0.075369 | 0.009261 | -0.053693 | -0.064898 | -0.092639 | -0.22081 | -0.12965 | -0.28424 | 0.032405 | -0.07536 | 0.054295 | -0.12472 | -0.11694 | 121.5341 | 121.5169 | 121.3887 | 61.5706 | -121.5983 | 121.3253 | 121.4848 | 121.4926 | 61.6291 | -121.7392
122.9531 | 121.8155 | -61.5509 | 60.0586 | 1.4211e-13 | -0.027 | 0.0014317 | 0.064073 | -0.0065361 | 0.055033 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.020656 | 0.059445 | -61.5371 | 0.028878 | -61.5954 | 59.9878 | 59.9751 | 59.8332 | -61.5443 | -61.5231 | 0.073618 | -61.6217 | 59.7835 | 59.9385 | 59.9417 | -61.676 | 0.006626 | -0.070791 | 0.013839 | -0.044536 | -0.051162 | -0.083481 | -0.22539 | -0.12508 | -0.27509 | 0.027826 | -0.070781 | 0.054295 | -0.12014 | -0.11694 | 121.5387 | 121.526 | 121.3841 | 61.5798 | -121.6029 | 121.3344 | 121.4894 | 121.4926 | 61.6245 | -121.7346
124.7031 | 121.7926 | -61.5234 | 60.0952 | 1.4211e-13 | -0.027 | 0.0014317 | 0.063859 | -0.0061087 | 0.05482 | -0.01755 | -0.0016621 | -0.0012713 | 0.063411 | 0.020442 | 0.059872 | -61.5462 | 0.015142 | -61.6 | 59.9832 | 59.9705 | 59.8378 | -61.5443 | -61.5139 | 0.073618 | -61.6217 | 59.7743 | 59.9339 | 59.9417 | -61.6806 | -0.02084 | -0.11199 | -0.022783 | -0.07658 | -0.05574 | -0.12468 | -0.25743 | -0.15712 | -0.32087 | 0.009518 | -0.098247 | 0.058874 | -0.16134 | -0.15356 | 121.5067 | 121.494 | 121.3612 | 61.5386 | -121.6395 | 121.2978 | 121.4573 | 121.4651 | 61.5971 | -121.7758
126.375 | 121.8201 | -61.5372 | 60.0403 | 1.4211e-13 | -0.027427 | 0.0016453 | 0.063859 | -0.0063223 | 0.05482 | -0.0022892 | -0.0018757 | -0.0012713 | 0.064052 | 0.020869 | 0.059658 | -61.5508 | 0.028878 | -61.6046 | 59.9878 | 59.966 | 59.8424 | -61.5397 | -61.5139 | 0.06904 | -61.6263 | 59.7835 | 59.9293 | 59.9371 | -61.6714 | -0.002528 | -0.05248 | -0.013629 | -0.067426 | -0.064898 | -0.074328 | -0.19792 | -0.13423 | -0.25678 | 0.023251 | -0.089093 | 0.045137 | -0.11098 | -0.1032 | 121.525 | 121.5031 | 121.3795 | 61.566 | -121.58 | 121.3207 | 121.4665 | 121.4742 | 61.6062 | -121.7117
128.1094 | 121.788 | -61.5234 | 60.1318 | 1.4211e-13 | -0.027427 | 0.0018589 | 0.063645 | -0.0058951 | 0.055033 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.020869 | 0.059658 | -61.5508 | 0.019721 | -61.6 | 59.9832 | 59.9751 | 59.8378 | -61.5397 | -61.5139 | 0.078197 | -61.6263 | 59.7835 | 59.9339 | 59.9371 | -61.6668 | -0.016261 | -0.14861 | -0.027362 | -0.07658 | -0.060319 | -0.15672 | -0.29405 | -0.14338 | -0.34833 | 0.009518 | -0.10283 | 0.040558 | -0.19796 | -0.19476 | 121.5067 | 121.4985 | 121.3612 | 61.5432 | -121.6715 | 121.3069 | 121.4573 | 121.4605 | 61.6016 | -121.7987
129.8438 | 121.7606 | -61.5875 | 60.022 | 1.4211e-13 | -0.027641 | 0.0012179 | 0.064073 | -0.0061087 | 0.05482 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063838 | 0.021083 | 0.059445 | -61.5462 | 0.019721 | -61.5909 | 59.9878 | 59.966 | 59.8286 | -61.5397 | -61.5185 | 0.06904 | -61.6263 | 59.7789 | 59.9293 | 59.9417 | -61.6714 | 0.047826 | -0.03417 | 0.041304 | -0.003337 | -0.051163 | -0.056018 | -0.19335 | -0.083876 | -0.24305 | 0.069026 | -0.038739 | 0.045137 | -0.092674 | -0.080315 | 121.5753 | 121.5535 | 121.4162 | 61.6072 | -121.5617 | 121.3665 | 121.5168 | 121.5292 | 61.6566 | -121.6934
131.5781 | 121.8018 | -61.5692 | 60.0677 | 1.4211e-13 | -0.027427 | 0.0016453 | 0.063859 | -0.0063223 | 0.054606 | -0.02518 | -0.0014485 | -0.0010577 | 0.064265 | 0.020656 | 0.059872 | -61.5416 | 0.0243 | -61.5954 | 59.9924 | 59.9705 | 59.8332 | -61.5397 | -61.5231 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9417 | -61.676 | 0.029516 | -0.075367 | 0.027572 | -0.026225 | -0.055741 | -0.097215 | -0.23454 | -0.10676 | -0.28882 | 0.046137 | -0.057049 | 0.049716 | -0.13387 | -0.12609 | 121.5616 | 121.5397 | 121.4024 | 61.5935 | -121.6074 | 121.3481 | 121.5031 | 121.5109 | 61.6474 | -121.7437
133.3125 | 121.7834 | -61.5417 | 60.0815 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.063645 | -0.0065361 | 0.055033 | 0.0053413 | -0.0018757 | -0.0016987 | 0.063624 | 0.020869 | 0.059872 | -61.5554 | 0.019721 | -61.6046 | 59.9832 | 59.966 | 59.8286 | -61.5443 | -61.5231 | 0.073618 | -61.6217 | 59.7789 | 59.9339 | 59.9371 | -61.6714 | -0.002529 | -0.098257 | -0.013629 | -0.062848 | -0.060319 | -0.11553 | -0.25285 | -0.12965 | -0.30255 | 0.018671 | -0.079936 | 0.049716 | -0.1476 | -0.1444 | 121.525 | 121.5077 | 121.3704 | 61.5615 | -121.6258 | 121.3207 | 121.4756 | 121.4788 | 61.6154 | -121.7529
135 | 121.8979 | -61.5509 | 59.9762 | 1.4211e-13 | -0.027641 | 0.0016453 | 0.064073 | -0.0061087 | 0.054606 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063838 | 0.021297 | 0.059445 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.966 | 59.8332 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7835 | 59.9385 | 59.9417 | -61.6668 | 0.011205 | 0.011607 | 0.004683 | -0.049114 | -0.060319 | -0.010241 | -0.14299 | -0.11592 | -0.19269 | 0.036984 | -0.066202 | 0.049716 | -0.03774 | -0.034538 | 121.5387 | 121.5169 | 121.3841 | 61.5706 | -121.5159 | 121.3344 | 121.4894 | 121.4926 | 61.6291 | -121.643
136.7344 | 121.756 | -61.6013 | 60.0357 | 1.4211e-13 | -0.027641 | 0.0016453 | 0.063859 | -0.0061087 | 0.054606 | -0.01755 | -0.0014485 | -0.0012713 | 0.064052 | 0.020869 | 0.059231 | -61.5371 | 0.019721 | -61.6 | 59.997 | 59.966 | 59.8332 | -61.5443 | -61.5185 | 0.082776 | -61.6217 | 59.7789 | 59.9293 | 59.9371 | -61.6714 | 0.05698 | -0.038746 | 0.064193 | 0.00124 | -0.05574 | -0.069751 | -0.2025 | -0.070143 | -0.25678 | 0.082759 | -0.020427 | 0.049716 | -0.10641 | -0.098627 | 121.5982 | 121.5672 | 121.4345 | 61.621 | -121.58 | 121.3802 | 121.5306 | 121.5383 | 61.684 | -121.7071
138.4844 | 121.756 | -61.5189 | 60.141 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063859 | -0.0058951 | 0.05482 | 0.012972 | -0.0016621 | -0.0010577 | 0.063624 | 0.020656 | 0.059445 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.966 | 59.8286 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7789 | 59.9339 | 59.9417 | -61.6714 | -0.020838 | -0.15319 | -0.02736 | -0.081157 | -0.060319 | -0.17504 | -0.31236 | -0.15254 | -0.36206 | 0.004941 | -0.10282 | 0.049716 | -0.20711 | -0.19933 | 121.5067 | 121.4848 | 121.3475 | 61.5386 | -121.6807 | 121.2978 | 121.4527 | 121.4605 | 61.5971 | -121.8124
140.1719 | 121.9208 | -61.5692 | 59.9762 | 1.4211e-13 | -0.027427 | 0.0016453 | 0.063859 | -0.0063223 | 0.055033 | 0.0053413 | -0.0014485 | -0.0014849 | 0.063624 | 0.020869 | 0.059658 | -61.5462 | 0.028878 | -61.5954 | 59.9832 | 59.9751 | 59.8378 | -61.5351 | -61.5185 | 0.073618 | -61.6263 | 59.7789 | 59.9293 | 59.9371 | -61.6714 | 0.034095 | 0.007029 | 0.022994 | -0.026225 | -0.06032 | -0.001083 | -0.13841 | -0.10219 | -0.19727 | 0.050716 | -0.057049 | 0.045137 | -0.046897 | -0.039117 | 121.5524 | 121.5443 | 121.407 | 61.5981 | -121.5113 | 121.3481 | 121.4985 | 121.5063 | 61.6428 | -121.6476
141.9219 | 121.756 | -61.5829 | 60.0449 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.064073 | -0.0065361 | 0.05482 | 0.012972 | -0.0014485 | -0.0010577 | 0.064052 | 0.021297 | 0.059445 | -61.5462 | 0.0243 | -61.6 | 59.9924 | 59.966 | 59.8378 | -61.5443 | -61.5277 | 0.078197 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.6668 | 0.03867 | -0.052479 | 0.036727 | -0.01707 | -0.05574 | -0.078906 | -0.20707 | -0.083874 | -0.26135 | 0.055292 | -0.029579 | 0.054295 | -0.11098 | -0.10778 | 121.5753 | 121.5489 | 121.4207 | 61.6072 | -121.5891 | 121.3665 | 121.5168 | 121.52 | 61.6611 | -121.7117
143.6562 | 121.9162 | -61.5189 | 60.0403 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.020869 | 0.059231 | -61.5462 | 0.028878 | -61.6 | 59.9832 | 59.9705 | 59.8332 | -61.5305 | -61.5185 | 0.073618 | -61.6217 | 59.7743 | 59.9385 | 59.9417 | -61.6714 | -0.01168 | -0.057058 | -0.02736 | -0.081157 | -0.069477 | -0.069749 | -0.20708 | -0.15254 | -0.26593 | 0.000362 | -0.10282 | 0.049716 | -0.10183 | -0.098625 | 121.5021 | 121.4894 | 121.3521 | 61.5477 | -121.5708 | 121.2932 | 121.4573 | 121.4605 | 61.5925 | -121.7117
145.3906 | 121.8979 | -61.5692 | 59.9579 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0099192 | -0.0020893 | -0.0014849 | 0.063838 | 0.020869 | 0.059872 | -61.5462 | 0.0243 | -61.5863 | 59.9878 | 59.9705 | 59.8286 | -61.5305 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9293 | 59.9371 | -61.6806 | 0.038674 | 0.029917 | 0.022994 | -0.017069 | -0.055743 | 0.012648 | -0.12926 | -0.11134 | -0.17438 | 0.050716 | -0.05247 | 0.058874 | -0.028587 | -0.020807 | 121.557 | 121.5397 | 121.3978 | 61.5935 | -121.4884 | 121.3527 | 121.4985 | 121.5063 | 61.6428 | -121.6384
147.125 | 121.7789 | -61.6013 | 60.022 | 1.4211e-13 | -0.027641 | 0.0014317 | 0.064073 | -0.0063223 | 0.05482 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063838 | 0.020869 | 0.059658 | -61.5416 | 0.019721 | -61.6 | 59.9832 | 59.9705 | 59.8378 | -61.5443 | -61.5185 | 0.078197 | -61.6125 | 59.7835 | 59.9293 | 59.9325 | -61.6714 | 0.05698 | -0.038748 | 0.059615 | 0.00124 | -0.05574 | -0.051439 | -0.18419 | -0.070143 | -0.23847 | 0.082759 | -0.011269 | 0.058874 | -0.092674 | -0.089473 | 121.5845 | 121.5718 | 121.439 | 61.621 | -121.5662 | 121.3848 | 121.5306 | 121.5338 | 61.6795 | -121.6934
148.7969 | 121.8521 | -61.5555 | 60.0037 | 1.4211e-13 | -0.027213 | 0.0014317 | 0.063859 | -0.0061087 | 0.054606 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.020656 | 0.059445 | -61.5462 | 0.019721 | -61.5954 | 59.9878 | 59.9614 | 59.8424 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9385 | 59.9279 | -61.676 | 0.015783 | -0.015859 | 0.009261 | -0.039958 | -0.055741 | -0.042286 | -0.1613 | -0.1205 | -0.22015 | 0.036983 | -0.061624 | 0.058874 | -0.065206 | -0.07574 | 121.5433 | 121.5169 | 121.3978 | 61.5752 | -121.5434 | 121.339 | 121.4939 | 121.4834 | 61.6337 | -121.6796
150.5469 | 121.7834 | -61.5326 | 60.0952 | 1.4211e-13 | -0.027641 | 0.0014317 | 0.063859 | -0.0065361 | 0.055033 | -0.01755 | -0.0014485 | -0.0010577 | 0.064052 | 0.020869 | 0.059658 | -61.5416 | 0.0243 | -61.6 | 59.9878 | 59.966 | 59.8378 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7789 | 59.9339 | 59.9325 | -61.6714 | -0.011684 | -0.10741 | -0.009049 | -0.067424 | -0.05574 | -0.12926 | -0.25743 | -0.13881 | -0.31629 | 0.014095 | -0.089091 | 0.049716 | -0.16134 | -0.16272 | 121.5204 | 121.4985 | 121.3704 | 61.5569 | -121.6395 | 121.3115 | 121.4665 | 121.4651 | 61.6108 | -121.7666
152.2969 | 121.9116 | -61.5051 | 60.0449 | 1.4211e-13 | -0.027641 | 0.0016453 | 0.063859 | -0.0061087 | 0.054606 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.020869 | 0.059872 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.966 | 59.8332 | -61.5397 | -61.5185 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9462 | -61.6806 | -0.034571 | -0.057058 | -0.041093 | -0.09489 | -0.060319 | -0.078906 | -0.21165 | -0.17543 | -0.26593 | -0.013371 | -0.12114 | 0.054295 | -0.11098 | -0.098625 | 121.4929 | 121.4711 | 121.3383 | 61.5248 | -121.5846 | 121.2841 | 121.439 | 121.4514 | 61.5833 | -121.7254
154.0469 | 121.7651 | -61.5326 | 60.1089 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063859 | -0.0063223 | 0.055033 | 0.0053413 | -0.0016621 | -0.0016987 | 0.064052 | 0.020656 | 0.059872 | -61.5416 | 0.0243 | -61.6 | 59.9832 | 59.9705 | 59.8378 | -61.5351 | -61.5231 | 0.06904 | -61.6125 | 59.7789 | 59.9293 | 59.9417 | -61.6714 | -0.002526 | -0.12572 | -0.009049 | -0.067424 | -0.064898 | -0.13841 | -0.27116 | -0.13881 | -0.33002 | 0.009516 | -0.079933 | 0.058874 | -0.17965 | -0.16729 | 121.5158 | 121.5031 | 121.3704 | 61.5569 | -121.6441 | 121.3115 | 121.4619 | 121.4743 | 61.6016 | -121.7803
155.7344 | 121.8338 | -61.6013 | 59.9991 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.064073 | -0.0061087 | 0.05482 | -0.0022892 | -0.0014485 | -0.0010577 | 0.063624 | 0.020869 | 0.059445 | -61.5416 | 0.033457 | -61.5954 | 59.9878 | 59.9568 | 59.8424 | -61.5351 | -61.5139 | 0.073618 | -61.6217 | 59.7835 | 59.9247 | 59.9508 | -61.6714 | 0.066138 | -0.011281 | 0.059615 | 0.005818 | -0.06032 | -0.042287 | -0.15672 | -0.070143 | -0.21558 | 0.087338 | -0.020427 | 0.049716 | -0.074364 | -0.048269 | 121.5891 | 121.5581 | 121.4436 | 61.6347 | -121.5342 | 121.3848 | 121.526 | 121.5521 | 61.6749 | -121.6705
157.4688 | 121.7651 | -61.5509 | 60.1227 | 1.4211e-13 | -0.028068 | 0.0016453 | 0.063432 | -0.0063223 | 0.054606 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.020869 | 0.059445 | -61.5416 | 0.019721 | -61.5954 | 59.9878 | 59.966 | 59.8332 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7743 | 59.9385 | 59.9417 | -61.676 | 0.011205 | -0.13488 | 0.009261 | -0.044536 | -0.055741 | -0.15673 | -0.28947 | -0.12508 | -0.34833 | 0.036984 | -0.066202 | 0.058874 | -0.18422 | -0.18102 | 121.5387 | 121.5169 | 121.3841 | 61.5706 | -121.6624 | 121.3253 | 121.4894 | 121.4926 | 61.6245 | -121.7987
159.1562 | 121.8155 | -61.5417 | 60.0769 | 1.4211e-13 | -0.027854 | 0.0012179 | 0.063432 | -0.0065361 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.020869 | 0.059231 | -61.5371 | 0.019721 | -61.5954 | 59.9924 | 59.966 | 59.8332 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7789 | 59.9339 | 59.9417 | -61.6714 | -0.002529 | -0.084522 | 0.004684 | -0.053691 | -0.051162 | -0.11095 | -0.2437 | -0.12965 | -0.29798 | 0.02325 | -0.079936 | 0.049716 | -0.14303 | -0.13525 | 121.5341 | 121.5077 | 121.375 | 61.5615 | -121.6212 | 121.3207 | 121.4756 | 121.4834 | 61.6199 | -121.7483
160.9062 | 121.8658 | -61.5875 | 59.9945 | 1.4211e-13 | -0.027641 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.020869 | 0.059231 | -61.5416 | 0.019721 | -61.5954 | 59.997 | 59.966 | 59.8378 | -61.5397 | -61.5185 | 0.073618 | -61.6217 | 59.7789 | 59.9293 | 59.9371 | -61.676 | 0.047826 | 0.002453 | 0.045882 | -0.007915 | -0.055741 | -0.028552 | -0.15672 | -0.088455 | -0.21558 | 0.069026 | -0.03416 | 0.054295 | -0.065208 | -0.057428 | 121.5845 | 121.5535 | 121.4253 | 61.6072 | -121.5342 | 121.3665 | 121.5168 | 121.5246 | 61.6611 | -121.6705
162.6562 | 121.9025 | -61.5692 | 59.967 | 1.4211e-13 | -0.028068 | 0.0012179 | 0.064073 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0016987 | 0.063838 | 0.020869 | 0.059658 | -61.5462 | 0.033457 | -61.6 | 59.9924 | 59.9705 | 59.8332 | -61.5351 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9476 | 59.9417 | -61.676 | 0.034095 | 0.025341 | 0.022994 | -0.030803 | -0.064898 | 0.003493 | -0.13383 | -0.10676 | -0.18353 | 0.050716 | -0.047891 | 0.058874 | -0.019428 | -0.025383 | 121.5616 | 121.5397 | 121.4024 | 61.6027 | -121.5022 | 121.3527 | 121.5168 | 121.5109 | 61.6474 | -121.643
164.3438 | 121.875 | -61.5005 | 60.0494 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063645 | -0.0061087 | 0.054606 | -0.0022892 | -0.0016621 | -0.0014849 | 0.064052 | 0.020869 | 0.059658 | -61.5462 | 0.0243 | -61.5954 | 59.9832 | 59.9614 | 59.8332 | -61.5397 | -61.5139 | 0.082776 | -61.6308 | 59.7789 | 59.943 | 59.9371 | -61.676 | -0.039149 | -0.066213 | -0.045671 | -0.09489 | -0.055741 | -0.088062 | -0.21623 | -0.17543 | -0.27051 | -0.01337 | -0.13029 | 0.045138 | -0.1064 | -0.11236 | 121.4838 | 121.4619 | 121.3338 | 61.5248 | -121.5891 | 121.2795 | 121.4436 | 121.4376 | 61.5833 | -121.7254
166.0781 | 121.7651 | -61.5051 | 60.0906 | 1.4211e-13 | -0.027854 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.01755 | -0.0016621 | -0.0014849 | 0.063624 | 0.021083 | 0.059658 | -61.5462 | 0.028878 | -61.6 | 59.9878 | 59.966 | 59.8424 | -61.5443 | -61.5185 | 0.078197 | -61.6263 | 59.7789 | 59.9293 | 59.9371 | -61.6714 | -0.03915 | -0.10283 | -0.041093 | -0.09489 | -0.05574 | -0.12468 | -0.24827 | -0.16627 | -0.31171 | -0.013371 | -0.12114 | 0.045137 | -0.16134 | -0.15356 | 121.4929 | 121.4711 | 121.3475 | 61.534 | -121.6349 | 121.2841 | 121.4344 | 121.4422 | 61.5833 | -121.762
167.8125 | 121.907 | -61.5097 | 60.0357 | 1.4211e-13 | -0.027641 | 0.0014317 | 0.063859 | -0.0061087 | 0.054606 | 0.0053413 | -0.0014485 | -0.0014849 | 0.064052 | 0.020869 | 0.059445 | -61.5371 | 0.0243 | -61.6046 | 59.9878 | 59.9614 | 59.8332 | -61.5351 | -61.5231 | 0.078197 | -61.6263 | 59.7789 | 59.9385 | 59.9417 | -61.676 | -0.025414 | -0.047903 | -0.027359 | -0.094891 | -0.069477 | -0.07433 | -0.2025 | -0.16627 | -0.25678 | -0.013372 | -0.11656 | 0.049716 | -0.09725 | -0.094048 | 121.4975 | 121.4711 | 121.3429 | 61.534 | -121.5708 | 121.2886 | 121.4482 | 121.4514 | 61.5879 | -121.7117
169.5781 | 121.843 | -61.5875 | 59.9762 | 1.4211e-13 | -0.027854 | 0.0014317 | 0.063645 | -0.0061087 | 0.05482 | -0.0022892 | -0.0014485 | -0.0014849 | 0.063411 | 0.020869 | 0.059445 | -61.5371 | 0.028878 | -61.6 | 59.9924 | 59.966 | 59.8332 | -61.5397 | -61.5185 | 0.078197 | -61.6217 | 59.7789 | 59.9385 | 59.9417 | -61.676 | 0.047826 | 0.016186 | 0.05046 | -0.012493 | -0.060319 | -0.010241 | -0.14299 | -0.088455 | -0.19727 | 0.069026 | -0.03416 | 0.054295 | -0.03774 | -0.034538 | 121.5799 | 121.5535 | 121.4207 | 61.6164 | -121.5159 | 121.3665 | 121.526 | 121.5292 | 61.6657 | -121.6522
171.25 | 121.7377 | -61.5738 | 60.0449 | 1.4211e-13 | -0.027641 | 0.0012179 | 0.063645 | -0.0065361 | 0.05482 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.020656 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.9832 | 59.9705 | 59.8378 | -61.5489 | -61.5231 | 0.082776 | -61.6308 | 59.7743 | 59.9385 | 59.9371 | -61.6714 | 0.024936 | -0.061636 | 0.036728 | -0.021647 | -0.046583 | -0.074327 | -0.20707 | -0.097608 | -0.27051 | 0.050715 | -0.057049 | 0.040559 | -0.1064 | -0.10778 | 121.557 | 121.5443 | 121.4116 | 61.6027 | -121.5937 | 121.3481 | 121.5122 | 121.5109 | 61.6566 | -121.7163
172.9844 | 121.8338 | -61.5005 | 60.0952 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063645 | -0.0063223 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.020869 | 0.059445 | -61.5416 | 0.019721 | -61.6046 | 59.9832 | 59.9705 | 59.8332 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7881 | 59.943 | 59.9417 | -61.676 | -0.039149 | -0.11199 | -0.041093 | -0.10405 | -0.064898 | -0.12468 | -0.26201 | -0.17543 | -0.30713 | -0.01337 | -0.11656 | 0.058874 | -0.15218 | -0.15356 | 121.4838 | 121.4711 | 121.3338 | 61.5203 | -121.6349 | 121.2886 | 121.4436 | 121.4422 | 61.5787 | -121.7712
174.7344 | 121.8018 | -61.5234 | 60.0677 | 1.4211e-13 | -0.027641 | 0.0014317 | 0.063859 | -0.0065361 | 0.05482 | -0.01755 | -0.0016621 | -0.0012713 | 0.063838 | 0.020656 | 0.059658 | -61.5462 | 0.019721 | -61.5954 | 59.9878 | 59.9614 | 59.8332 | -61.5443 | -61.5139 | 0.073618 | -61.6263 | 59.7835 | 59.9385 | 59.9371 | -61.6668 | -0.02084 | -0.079946 | -0.022783 | -0.072002 | -0.051162 | -0.10637 | -0.23454 | -0.14338 | -0.28424 | 0.009518 | -0.10283 | 0.040558 | -0.12929 | -0.13067 | 121.5112 | 121.4848 | 121.3566 | 61.5432 | -121.612 | 121.3069 | 121.4619 | 121.4605 | 61.5971 | -121.7346
176.4688 | 121.9162 | -61.5005 | 60.054 | 1.4211e-13 | -0.027427 | 0.0014317 | 0.063645 | -0.0065361 | 0.05482 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063838 | 0.021083 | 0.059658 | -61.5462 | 0.0243 | -61.6 | 59.9878 | 59.966 | 59.8332 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.6714 | -0.039149 | -0.066213 | -0.045671 | -0.099468 | -0.060319 | -0.088061 | -0.22081 | -0.17085 | -0.27051 | -0.01337 | -0.11656 | 0.054295 | -0.11556 | -0.11694 | 121.4884 | 121.4665 | 121.3338 | 61.5248 | -121.5937 | 121.2841 | 121.439 | 121.4376 | 61.5742 | -121.7254
178.1406 | 121.9299 | -61.4914 | 60.0494 | 1.4211e-13 | -0.027854 | 0.0014317 | 0.063645 | -0.0058951 | 0.05482 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063838 | 0.021083 | 0.059658 | -61.5371 | 0.028878 | -61.5954 | 59.9878 | 59.966 | 59.8378 | -61.5351 | -61.5139 | 0.078197 | -61.6263 | 59.7789 | 59.9385 | 59.9279 | -61.6714 | -0.043725 | -0.061635 | -0.04567 | -0.10404 | -0.06032 | -0.083483 | -0.21165 | -0.18001 | -0.27051 | -0.022525 | -0.13487 | 0.045137 | -0.11098 | -0.12152 | 121.4792 | 121.4573 | 121.3292 | 61.5203 | -121.5846 | 121.2703 | 121.4299 | 121.4193 | 61.5696 | -121.7208
179.875 | 121.7834 | -61.5417 | 60.1089 | 1.4211e-13 | -0.028068 | 0.0016453 | 0.063859 | -0.0065361 | 0.05482 | -0.02518 | -0.0020893 | -0.0014849 | 0.064052 | 0.021083 | 0.059231 | -61.5416 | 0.0243 | -61.6 | 59.9832 | 59.9705 | 59.8424 | -61.5351 | -61.5185 | 0.06904 | -61.6263 | 59.7743 | 59.9339 | 59.9417 | -61.6714 | 0.006629 | -0.12572 | 0.000106 | -0.058269 | -0.064898 | -0.13841 | -0.26658 | -0.12965 | -0.3346 | 0.02325 | -0.084515 | 0.045137 | -0.17507 | -0.16729 | 121.525 | 121.5123 | 121.3841 | 61.566 | -121.6441 | 121.3161 | 121.4756 | 121.4834 | 61.6108 | -121.7803
181.6094 | 121.8155 | -61.5738 | 60.0586 | 1.4211e-13 | -0.028068 | 0.0012179 | 0.063432 | -0.0067497 | 0.05482 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.021083 | 0.059445 | -61.5416 | 0.038035 | -61.5863 | 59.9878 | 59.9614 | 59.8378 | -61.5443 | -61.5185 | 0.073618 | -61.6171 | 59.7789 | 59.9293 | 59.9371 | -61.676 | 0.029515 | -0.070791 | 0.03215 | -0.012491 | -0.042006 | -0.097218 | -0.22081 | -0.10219 | -0.27967 | 0.055294 | -0.043313 | 0.058874 | -0.12929 | -0.12152 | 121.5616 | 121.5352 | 121.4116 | 61.6118 | -121.6029 | 121.3527 | 121.5031 | 121.5109 | 61.6474 | -121.7346
183.3438 | 121.9025 | -61.5738 | 59.967 | 1.4211e-13 | -0.027641 | 0.0014317 | 0.063859 | -0.0067497 | 0.05482 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.020656 | 0.059658 | -61.5462 | 0.028878 | -61.5954 | 59.9878 | 59.966 | 59.8378 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6714 | 0.034094 | 0.020762 | 0.027572 | -0.021647 | -0.055741 | -0.001086 | -0.12926 | -0.097608 | -0.18353 | 0.059873 | -0.047892 | 0.049716 | -0.033163 | -0.029962 | 121.5616 | 121.5397 | 121.4116 | 61.6027 | -121.5067 | 121.3573 | 121.5077 | 121.5109 | 61.652 | -121.6384
185.0312 | 121.8018 | -61.5463 | 60.0632 | 1.4211e-13 | -0.027641 | 0.0012179 | 0.063432 | -0.0063223 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063411 | 0.021083 | 0.059872 | -61.5462 | 0.0243 | -61.5954 | 59.9878 | 59.966 | 59.8378 | -61.5443 | -61.5185 | 0.078197 | -61.6308 | 59.7789 | 59.9339 | 59.9417 | -61.676 | 0.002049 | -0.075368 | 0.000106 | -0.049113 | -0.051162 | -0.097216 | -0.22538 | -0.12965 | -0.28424 | 0.027828 | -0.084515 | 0.045138 | -0.12929 | -0.12151 | 121.5341 | 121.5123 | 121.3841 | 61.5706 | -121.6074 | 121.3253 | 121.4802 | 121.488 | 61.6245 | -121.7391
186.7656 | 121.875 | -61.5646 | 59.9945 | 1.4211e-13 | -0.027641 | 0.00079051 | 0.063859 | -0.0063223 | 0.055033 | 0.0053413 | -0.0014485 | -0.0012713 | 0.063838 | 0.021297 | 0.059445 | -61.5416 | 0.028878 | -61.5909 | 59.9878 | 59.9797 | 59.8332 | -61.5351 | -61.5231 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.676 | 0.029517 | -0.006704 | 0.022994 | -0.026225 | -0.055742 | -0.014815 | -0.1613 | -0.11134 | -0.211 | 0.041559 | -0.052469 | 0.058874 | -0.051472 | -0.057428 | 121.5524 | 121.5443 | 121.3978 | 61.5935 | -121.5296 | 121.3481 | 121.5077 | 121.5017 | 61.6428 | -121.6705
188.4375 | 121.9025 | -61.4639 | 60.0494 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063645 | -0.0063223 | 0.05482 | -0.0099192 | -0.0016621 | -0.0010577 | 0.064052 | 0.021297 | 0.059445 | -61.5462 | 0.033457 | -61.5909 | 59.9924 | 59.9797 | 59.8424 | -61.5397 | -61.5139 | 0.073618 | -61.6217 | 59.7789 | 59.9293 | 59.9325 | -61.676 | -0.07577 | -0.057056 | -0.082292 | -0.12693 | -0.051163 | -0.069746 | -0.20707 | -0.21205 | -0.27051 | -0.049991 | -0.15776 | 0.054295 | -0.12014 | -0.11694 | 121.4563 | 121.4436 | 121.3063 | 61.4974 | -121.5891 | 121.2429 | 121.3932 | 121.3964 | 61.5375 | -121.7254
190.1719 | 121.8155 | -61.5097 | 60.0815 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063645 | -0.0063223 | 0.054392 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.021083 | 0.060086 | -61.5416 | 0.0243 | -61.5954 | 59.9878 | 59.9705 | 59.8378 | -61.5397 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.6714 | -0.029993 | -0.093679 | -0.031937 | -0.085734 | -0.055741 | -0.11095 | -0.2437 | -0.1617 | -0.29798 | -0.004214 | -0.10282 | 0.058874 | -0.1476 | -0.1444 | 121.4975 | 121.4802 | 121.3475 | 61.534 | -121.6212 | 121.2932 | 121.4436 | 121.4468 | 61.5879 | -121.7529
191.9062 | 121.7743 | -61.5326 | 60.0952 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063645 | -0.0063223 | 0.055033 | -0.01755 | -0.0014485 | -0.00084406 | 0.063624 | 0.021083 | 0.059445 | -61.5462 | 0.019721 | -61.5909 | 59.9878 | 59.966 | 59.8286 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7835 | 59.943 | 59.9371 | -61.676 | -0.007105 | -0.10741 | -0.013627 | -0.058268 | -0.051163 | -0.12926 | -0.26659 | -0.14339 | -0.31171 | 0.018674 | -0.089091 | 0.054295 | -0.15218 | -0.15814 | 121.5204 | 121.4985 | 121.3612 | 61.5523 | -121.6349 | 121.3161 | 121.4756 | 121.4697 | 61.6108 | -121.7712
193.5781 | 121.7651 | -61.5967 | 60.0449 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063432 | -0.0065361 | 0.055033 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063411 | 0.020869 | 0.059658 | -61.5462 | 0.028878 | -61.5954 | 59.9832 | 59.9751 | 59.8424 | -61.5443 | -61.5185 | 0.073618 | -61.6217 | 59.7881 | 59.9385 | 59.9417 | -61.6714 | 0.052403 | -0.061636 | 0.05046 | 0.001241 | -0.051162 | -0.069748 | -0.2025 | -0.07472 | -0.25678 | 0.078182 | -0.025004 | 0.049716 | -0.1064 | -0.1032 | 121.5799 | 121.5718 | 121.439 | 61.6256 | -121.5891 | 121.3848 | 121.5351 | 121.5383 | 61.6703 | -121.7163
195.3281 | 121.8796 | -61.5738 | 59.9716 | 1.4211e-13 | -0.028068 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0099192 | -0.0016621 | -0.0016987 | 0.064052 | 0.020869 | 0.059445 | -61.5416 | 0.019721 | -61.5954 | 59.9832 | 59.9705 | 59.8424 | -61.5305 | -61.5185 | 0.078197 | -61.6125 | 59.7881 | 59.9385 | 59.9417 | -61.676 | 0.043252 | 0.011606 | 0.03215 | -0.021647 | -0.064899 | -0.001085 | -0.12925 | -0.10219 | -0.18353 | 0.055294 | -0.038734 | 0.063453 | -0.033163 | -0.029961 | 121.557 | 121.5443 | 121.4162 | 61.5935 | -121.5022 | 121.3619 | 121.5122 | 121.5154 | 61.652 | -121.6476
197.0156 | 121.7606 | -61.615 | 60.0266 | 1.4211e-13 | -0.028068 | 0.0016453 | 0.063645 | -0.0067497 | 0.055033 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021297 | 0.059231 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.966 | 59.8515 | -61.5397 | -61.5139 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9371 | -61.6851 | 0.075292 | -0.02959 | 0.082505 | 0.019551 | -0.055741 | -0.060595 | -0.17503 | -0.070147 | -0.24762 | 0.10107 | -0.011273 | 0.058874 | -0.092672 | -0.089471 | 121.612 | 121.5809 | 121.4665 | 61.6393 | -121.5662 | 121.3939 | 121.5489 | 121.5521 | 61.6932 | -121.7117
198.75 | 121.7834 | -61.5417 | 60.1364 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063645 | -0.0065361 | 0.054392 | -0.01755 | -0.0016621 | -0.0014849 | 0.063838 | 0.020869 | 0.059658 | -61.5508 | 0.0243 | -61.6 | 59.9878 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.078197 | -61.6263 | 59.7743 | 59.9339 | 59.9371 | -61.676 | 0.00205 | -0.14861 | -0.009051 | -0.058269 | -0.060319 | -0.16588 | -0.29405 | -0.13423 | -0.36206 | 0.027829 | -0.084515 | 0.049716 | -0.20254 | -0.19934 | 121.5296 | 121.5123 | 121.3841 | 61.566 | -121.6761 | 121.3161 | 121.4756 | 121.4788 | 61.6199 | -121.8124
200.4375 | 121.8842 | -61.5143 | 60.0449 | 1.4211e-13 | -0.028068 | 0.0010043 | 0.063859 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.021083 | 0.059658 | -61.5371 | 0.028878 | -61.5909 | 59.9924 | 59.966 | 59.8378 | -61.5397 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9385 | 59.9417 | -61.676 | -0.025416 | -0.052479 | -0.022782 | -0.076579 | -0.051163 | -0.078906 | -0.20707 | -0.1617 | -0.26135 | -0.004216 | -0.1074 | 0.054295 | -0.1064 | -0.1032 | 121.5067 | 121.4802 | 121.3521 | 61.5432 | -121.5846 | 121.2978 | 121.4527 | 121.4559 | 61.5879 | -121.7208
202.1719 | 121.8887 | -61.5189 | 60.0311 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.064073 | -0.0061087 | 0.055033 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.021297 | 0.059658 | -61.5416 | 0.033457 | -61.6 | 59.9924 | 59.9705 | 59.8469 | -61.5443 | -61.5185 | 0.078197 | -61.6263 | 59.7789 | 59.9293 | 59.9325 | -61.6714 | -0.025417 | -0.038746 | -0.022782 | -0.081157 | -0.05574 | -0.060594 | -0.18418 | -0.15254 | -0.2522 | 0.000362 | -0.1074 | 0.045137 | -0.10183 | -0.098628 | 121.5112 | 121.4894 | 121.3658 | 61.5523 | -121.5754 | 121.2978 | 121.4482 | 121.4514 | 61.5971 | -121.7025
203.9062 | 121.8933 | -61.5646 | 59.9808 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063432 | -0.0061087 | 0.05482 | -0.0022892 | -0.0020893 | -0.0012713 | 0.064265 | 0.020869 | 0.059445 | -61.5416 | 0.0243 | -61.5954 | 59.9832 | 59.966 | 59.8378 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6714 | 0.024938 | 0.002451 | 0.022994 | -0.030803 | -0.055741 | -0.014819 | -0.14299 | -0.10676 | -0.19727 | 0.050717 | -0.057048 | 0.049716 | -0.046896 | -0.043695 | 121.5479 | 121.5306 | 121.4024 | 61.5889 | -121.5205 | 121.3481 | 121.4985 | 121.5017 | 61.6474 | -121.6522
205.5938 | 121.8796 | -61.5005 | 60.0906 | 1.4211e-13 | -0.027854 | 0.0012179 | 0.063859 | -0.0065361 | 0.055033 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063838 | 0.021297 | 0.059445 | -61.5416 | 0.028878 | -61.6 | 59.9832 | 59.966 | 59.8424 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7835 | 59.9293 | 59.9371 | -61.676 | -0.039149 | -0.10741 | -0.041093 | -0.099468 | -0.060319 | -0.12468 | -0.24827 | -0.17543 | -0.30713 | -0.01337 | -0.12114 | 0.054295 | -0.16134 | -0.15356 | 121.4838 | 121.4665 | 121.3429 | 61.5294 | -121.6303 | 121.2841 | 121.4298 | 121.4376 | 61.5787 | -121.7666
207.3281 | 121.756 | -61.6013 | 60.0403 | 1.4211e-13 | -0.027641 | 0.0016453 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021083 | 0.059231 | -61.5371 | 0.015142 | -61.5909 | 59.997 | 59.966 | 59.8424 | -61.5443 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9339 | 59.9325 | -61.6714 | 0.05698 | -0.043323 | 0.064193 | 0.010396 | -0.046584 | -0.074328 | -0.19792 | -0.070143 | -0.25678 | 0.082759 | -0.020427 | 0.049716 | -0.10641 | -0.10778 | 121.5982 | 121.5672 | 121.4436 | 61.6164 | -121.5846 | 121.3848 | 121.5351 | 121.5338 | 61.6749 | -121.7117
209.0625 | 121.9162 | -61.5005 | 60.0357 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063645 | -0.0061087 | 0.05482 | 0.0053413 | -0.0014485 | -0.0012713 | 0.064052 | 0.021083 | 0.059445 | -61.5371 | 0.0243 | -61.6046 | 59.9878 | 59.9705 | 59.8424 | -61.5397 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9293 | 59.9417 | -61.676 | -0.039149 | -0.047903 | -0.036515 | -0.10405 | -0.064898 | -0.065172 | -0.19334 | -0.17543 | -0.2522 | -0.017949 | -0.12114 | 0.054295 | -0.10641 | -0.094048 | 121.4884 | 121.4711 | 121.3429 | 61.5248 | -121.5754 | 121.2841 | 121.4298 | 121.4422 | 61.5742 | -121.7117
210.8125 | 121.9116 | -61.496 | 60.0449 | 1.4211e-13 | -0.027854 | 0.0018589 | 0.063859 | -0.0063223 | 0.055033 | -0.0099192 | -0.0020893 | -0.0010577 | 0.064052 | 0.020656 | 0.059445 | -61.5508 | 0.028878 | -61.6046 | 59.9878 | 59.966 | 59.8332 | -61.5397 | -61.5185 | 0.073618 | -61.6263 | 59.7789 | 59.9385 | 59.9279 | -61.676 | -0.043726 | -0.057058 | -0.054827 | -0.10862 | -0.064898 | -0.078906 | -0.21165 | -0.18001 | -0.26593 | -0.022526 | -0.13029 | 0.049716 | -0.1064 | -0.11694 | 121.4838 | 121.4619 | 121.3292 | 61.5249 | -121.5846 | 121.2749 | 121.4344 | 121.4239 | 61.5696 | -121.7208
212.4844 | 121.7651 | -61.5234 | 60.1044 | 1.4211e-13 | -0.027641 | 0.0014317 | 0.063859 | -0.0063223 | 0.05482 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.021297 | 0.059231 | -61.5462 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8332 | -61.5351 | -61.5093 | 0.073618 | -61.6125 | 59.7743 | 59.9339 | 59.9279 | -61.676 | -0.011682 | -0.11657 | -0.022783 | -0.07658 | -0.064898 | -0.13384 | -0.27116 | -0.15254 | -0.33002 | 0.014096 | -0.089089 | 0.063453 | -0.17049 | -0.17645 | 121.5112 | 121.494 | 121.3566 | 61.5432 | -121.6395 | 121.2978 | 121.4573 | 121.4514 | 61.5971 | -121.7803
214.2188 | 121.8063 | -61.5143 | 60.0403 | 1.4211e-13 | -0.027854 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0099192 | -0.0012349 | -0.0016987 | 0.063838 | 0.021511 | 0.059658 | -61.5462 | 0.0243 | -61.6046 | 59.9924 | 59.9705 | 59.8332 | -61.5351 | -61.5185 | 0.078197 | -61.6263 | 59.7835 | 59.9293 | 59.9417 | -61.6806 | -0.020837 | -0.047901 | -0.031938 | -0.090314 | -0.069477 | -0.069749 | -0.20708 | -0.16628 | -0.25678 | -0.004216 | -0.11198 | 0.054295 | -0.11098 | -0.098625 | 121.5067 | 121.4848 | 121.3475 | 61.5386 | -121.5754 | 121.2978 | 121.4436 | 121.4559 | 61.5925 | -121.7208
215.9062 | 121.8613 | -61.528 | 60.0174 | 1.4211e-13 | -0.028068 | 0.0012179 | 0.063645 | -0.0063223 | 0.054606 | -0.0022892 | -0.0016621 | -0.00084406 | 0.063624 | 0.021297 | 0.059445 | -61.5371 | 0.028878 | -61.6046 | 59.9878 | 59.9705 | 59.8378 | -61.5397 | -61.5139 | 0.073618 | -61.6263 | 59.7835 | 59.9293 | 59.9325 | -61.6714 | -0.011683 | -0.029592 | -0.009049 | -0.076581 | -0.064898 | -0.046861 | -0.17961 | -0.14338 | -0.23389 | 0.014096 | -0.098248 | 0.045137 | -0.088096 | -0.084895 | 121.5158 | 121.4985 | 121.3658 | 61.5569 | -121.5571 | 121.3115 | 121.4573 | 121.4605 | 61.6016 | -121.6888
217.6562 | 121.8475 | -61.5372 | 60.0174 | 1.4211e-13 | -0.027854 | 0.0012179 | 0.063432 | -0.0065361 | 0.05482 | -0.0099192 | -0.0014485 | -0.0014849 | 0.063838 | 0.021297 | 0.059658 | -61.5416 | 0.0243 | -61.6092 | 59.9878 | 59.966 | 59.8378 | -61.5351 | -61.5139 | 0.078197 | -61.6171 | 59.7743 | 59.9385 | 59.9371 | -61.6714 | 0.002051 | -0.029592 | -0.004472 | -0.072004 | -0.074055 | -0.05144 | -0.17961 | -0.13423 | -0.24305 | 0.023251 | -0.079935 | 0.054295 | -0.078939 | -0.080316 | 121.525 | 121.5031 | 121.375 | 61.5615 | -121.5525 | 121.3115 | 121.4756 | 121.4742 | 61.6154 | -121.6888
219.4062 | 121.8796 | -61.5555 | 59.9854 | 1.4211e-13 | -0.027854 | 0.0016453 | 0.063645 | -0.0063223 | 0.054392 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.021083 | 0.059231 | -61.5371 | 0.028878 | -61.6 | 59.9878 | 59.966 | 59.8378 | -61.5443 | -61.5139 | 0.078197 | -61.6217 | 59.7789 | 59.9339 | 59.9371 | -61.6806 | 0.011204 | 0.002451 | 0.018417 | -0.044536 | -0.05574 | -0.019397 | -0.14757 | -0.12508 | -0.20642 | 0.041562 | -0.066203 | 0.058874 | -0.051474 | -0.048273 | 121.5433 | 121.5214 | 121.3933 | 61.5844 | -121.5296 | 121.3344 | 121.4894 | 121.4926 | 61.6337 | -121.6659
221.1719 | 121.7651 | -61.5921 | 60.0037 | 1.4211e-13 | -0.027854 | 0.0014317 | 0.064073 | -0.0063223 | 0.054606 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063838 | 0.021297 | 0.059445 | -61.5416 | 0.038035 | -61.5954 | 59.9924 | 59.9705 | 59.8332 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.6668 | 0.052404 | -0.01128 | 0.05046 | -0.003337 | -0.055741 | -0.033128 | -0.17045 | -0.074719 | -0.22015 | 0.073604 | -0.025003 | 0.049716 | -0.065206 | -0.066583 | 121.5845 | 121.5626 | 121.4253 | 61.6301 | -121.5434 | 121.3756 | 121.5306 | 121.5292 | 61.6703 | -121.6705
222.8906 | 121.7606 | -61.5097 | 60.1044 | 1.4211e-13 | -0.028068 | 0.00079051 | 0.063645 | -0.0061087 | 0.055033 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063624 | 0.021511 | 0.059445 | -61.5371 | 0.019721 | -61.6 | 59.9832 | 59.9705 | 59.8378 | -61.5397 | -61.5139 | 0.073618 | -61.6217 | 59.7743 | 59.943 | 59.9417 | -61.676 | -0.029993 | -0.12115 | -0.027359 | -0.090312 | -0.060319 | -0.13384 | -0.26658 | -0.16627 | -0.33002 | -0.004214 | -0.11198 | 0.054295 | -0.16134 | -0.16271 | 121.4929 | 121.4802 | 121.3475 | 61.5294 | -121.6441 | 121.2841 | 121.4527 | 121.4514 | 61.5833 | -121.7803
224.5625 | 121.7468 | -61.528 | 60.1135 | 1.4211e-13 | -0.028282 | 0.0012179 | 0.063645 | -0.0061087 | 0.05482 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.021297 | 0.059231 | -61.5371 | 0.028878 | -61.6046 | 59.9878 | 59.9705 | 59.8378 | -61.5305 | -61.5139 | 0.073618 | -61.6171 | 59.7789 | 59.9385 | 59.9279 | -61.6806 | -0.002525 | -0.12572 | -0.009049 | -0.076581 | -0.074056 | -0.14299 | -0.27574 | -0.15254 | -0.3346 | 0.014096 | -0.08909 | 0.063453 | -0.17507 | -0.1856 | 121.5158 | 121.4985 | 121.3658 | 61.5569 | -121.6441 | 121.3069 | 121.4665 | 121.4559 | 61.6016 | -121.7941
226.2969 | 121.8613 | -61.5601 | 59.9716 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063645 | -0.0065361 | 0.054392 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063838 | 0.021083 | 0.059445 | -61.5416 | 0.038035 | -61.5954 | 59.9832 | 59.9705 | 59.8378 | -61.5351 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9385 | 59.9325 | -61.6806 | 0.02494 | 0.011606 | 0.018417 | -0.03538 | -0.06032 | -0.001085 | -0.13383 | -0.1205 | -0.18811 | 0.041561 | -0.061625 | 0.058874 | -0.033163 | -0.039119 | 121.5433 | 121.5306 | 121.3978 | 61.5981 | -121.5067 | 121.3436 | 121.4985 | 121.4926 | 61.6337 | -121.6522
227.9688 | 121.8658 | -61.4822 | 60.0677 | 1.4211e-13 | -0.028282 | 0.0012179 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0014485 | -0.0010577 | 0.064052 | 0.021083 | 0.059445 | -61.5462 | 0.0243 | -61.6 | 59.9878 | 59.966 | 59.8378 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9339 | 59.9325 | -61.676 | -0.057459 | -0.079946 | -0.063981 | -0.11778 | -0.060319 | -0.10179 | -0.22996 | -0.19374 | -0.28424 | -0.036259 | -0.13487 | 0.058874 | -0.13387 | -0.13525 | 121.47 | 121.4482 | 121.32 | 61.5065 | -121.6074 | 121.2657 | 121.4161 | 121.4147 | 61.5604 | -121.7437
229.6562 | 121.756 | -61.5784 | 60.0494 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063432 | -0.0061087 | 0.05482 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.021297 | 0.059445 | -61.5416 | 0.028878 | -61.5909 | 59.9878 | 59.966 | 59.8378 | -61.5443 | -61.5231 | 0.082776 | -61.6171 | 59.7743 | 59.9339 | 59.9371 | -61.676 | 0.034092 | -0.061635 | 0.036727 | -0.012492 | -0.046584 | -0.083483 | -0.21165 | -0.09761 | -0.27509 | 0.055292 | -0.038736 | 0.058874 | -0.11556 | -0.11236 | 121.5662 | 121.5443 | 121.4162 | 61.6072 | -121.5937 | 121.3527 | 121.5122 | 121.5154 | 61.6611 | -121.7254
231.3281 | 121.788 | -61.528 | 60.1135 | 1.4211e-13 | -0.028068 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.021511 | 0.059445 | -61.5416 | 0.033457 | -61.5954 | 59.9878 | 59.9705 | 59.8378 | -61.5443 | -61.5093 | 0.078197 | -61.6171 | 59.7743 | 59.9385 | 59.9417 | -61.6714 | -0.016262 | -0.12572 | -0.013627 | -0.067424 | -0.051162 | -0.14299 | -0.27574 | -0.14338 | -0.33918 | 0.018674 | -0.08909 | 0.054295 | -0.17507 | -0.17187 | 121.5158 | 121.4985 | 121.3658 | 61.5615 | -121.6578 | 121.3024 | 121.4665 | 121.4697 | 61.6062 | -121.7849
233.0625 | 121.8155 | -61.5372 | 60.0632 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063859 | -0.0063223 | 0.05482 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021297 | 0.059445 | -61.5371 | 0.028878 | -61.6 | 59.9832 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7743 | 59.9339 | 59.9325 | -61.676 | -0.002528 | -0.079946 | 0.000106 | -0.062847 | -0.060319 | -0.092637 | -0.22081 | -0.13881 | -0.28882 | 0.023251 | -0.079935 | 0.058874 | -0.12929 | -0.13067 | 121.5204 | 121.5077 | 121.3795 | 61.566 | -121.6029 | 121.3115 | 121.471 | 121.4697 | 61.6108 | -121.7391
234.75 | 121.8063 | -61.5555 | 60.054 | 1.4211e-13 | -0.028068 | 0.0016453 | 0.063645 | -0.0063223 | 0.054606 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063838 | 0.020869 | 0.059658 | -61.5416 | 0.0243 | -61.6 | 59.9832 | 59.966 | 59.8378 | -61.5443 | -61.5139 | 0.073618 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6714 | 0.011204 | -0.070791 | 0.013839 | -0.044536 | -0.05574 | -0.088061 | -0.21623 | -0.11592 | -0.27051 | 0.041562 | -0.066203 | 0.049716 | -0.12014 | -0.11694 | 121.5387 | 121.5214 | 121.3933 | 61.5798 | -121.5983 | 121.339 | 121.4894 | 121.4926 | 61.6291 | -121.7254
236.4219 | 121.7514 | -61.5829 | 60.0449 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063645 | -0.0065361 | 0.05482 | -0.01755 | -0.0018757 | -0.0014849 | 0.063624 | 0.021083 | 0.059445 | -61.5416 | 0.033457 | -61.5954 | 59.9878 | 59.966 | 59.8424 | -61.5443 | -61.5231 | 0.082776 | -61.6171 | 59.7743 | 59.943 | 59.9417 | -61.6806 | 0.03867 | -0.057058 | 0.041305 | -0.012492 | -0.051162 | -0.078906 | -0.2025 | -0.097611 | -0.27051 | 0.05987 | -0.034158 | 0.063453 | -0.10183 | -0.1032 | 121.5708 | 121.5489 | 121.4253 | 61.6164 | -121.5891 | 121.3573 | 121.526 | 121.5246 | 61.6657 | -121.7254
238.0938 | 121.8704 | -61.5555 | 59.9808 | 1.4211e-13 | -0.027854 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063411 | 0.021297 | 0.059231 | -61.5416 | 0.028878 | -61.6 | 59.9924 | 59.9705 | 59.8378 | -61.5489 | -61.5139 | 0.073618 | -61.6217 | 59.7789 | 59.943 | 59.9325 | -61.6714 | 0.006625 | 0.011608 | 0.013839 | -0.044536 | -0.051161 | -0.01024 | -0.14299 | -0.11592 | -0.20185 | 0.041562 | -0.066203 | 0.049716 | -0.037739 | -0.048274 | 121.5479 | 121.526 | 121.3933 | 61.5844 | -121.5296 | 121.3344 | 121.4985 | 121.488 | 61.6291 | -121.6522
239.7656 | 121.8521 | -61.5738 | 59.9854 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063645 | -0.0063223 | 0.054606 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063624 | 0.021083 | 0.059231 | -61.5416 | 0.028878 | -61.6092 | 59.9924 | 59.9614 | 59.8469 | -61.5305 | -61.5185 | 0.087354 | -61.6125 | 59.7835 | 59.9339 | 59.9417 | -61.6806 | 0.043252 | 0.00703 | 0.03215 | -0.035382 | -0.078634 | -0.023976 | -0.13841 | -0.10677 | -0.20184 | 0.055294 | -0.038734 | 0.068032 | -0.051474 | -0.043694 | 121.5662 | 121.5352 | 121.4207 | 61.6027 | -121.5159 | 121.3573 | 121.5077 | 121.5154 | 61.6611 | -121.6659
241.4375 | 121.7743 | -61.615 | 60.0357 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0014485 | -0.0010577 | 0.063624 | 0.020656 | 0.059231 | -61.5371 | 0.0243 | -61.6 | 59.9786 | 59.966 | 59.8424 | -61.5351 | -61.5277 | 0.078197 | -61.6034 | 59.7789 | 59.943 | 59.9462 | -61.6668 | 0.079871 | -0.05706 | 0.077926 | 0.014973 | -0.064898 | -0.069751 | -0.19334 | -0.051831 | -0.25678 | 0.087335 | 0.011621 | 0.063452 | -0.092671 | -0.08947 | 121.5936 | 121.5809 | 121.4574 | 61.6393 | -121.5708 | 121.3939 | 121.558 | 121.5612 | 61.6932 | -121.7025
243.1406 | 121.7651 | -61.615 | 60.0357 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063859 | -0.0065361 | 0.054392 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064265 | 0.021297 | 0.059445 | -61.5371 | 0.028878 | -61.6 | 59.9832 | 59.9751 | 59.8424 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7789 | 59.9339 | 59.9371 | -61.6668 | 0.070713 | -0.052481 | 0.077926 | 0.014973 | -0.05574 | -0.060593 | -0.19334 | -0.051831 | -0.25678 | 0.096492 | -0.006694 | 0.045137 | -0.10183 | -0.098627 | 121.5982 | 121.5901 | 121.4574 | 61.6439 | -121.58 | 121.3939 | 121.5489 | 121.5521 | 61.6932 | -121.7025
244.8594 | 121.8109 | -61.5509 | 60.0815 | 1.4211e-13 | -0.028282 | 0.0010043 | 0.064073 | -0.0063223 | 0.054392 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063411 | 0.021083 | 0.059231 | -61.5462 | 0.033457 | -61.5954 | 59.9832 | 59.9614 | 59.8378 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7789 | 59.943 | 59.9417 | -61.6668 | 0.006626 | -0.098257 | 0.004683 | -0.044536 | -0.051162 | -0.12011 | -0.2437 | -0.11592 | -0.30255 | 0.032405 | -0.070781 | 0.045137 | -0.13845 | -0.13982 | 121.5341 | 121.5123 | 121.3887 | 61.5844 | -121.6258 | 121.3298 | 121.4939 | 121.4926 | 61.6291 | -121.7483
246.5469 | 121.7743 | -61.5784 | 60.0266 | 1.4211e-13 | -0.028495 | 0.0014317 | 0.063859 | -0.0063223 | 0.054392 | -0.01755 | -0.0016621 | -0.0012713 | 0.063624 | 0.021083 | 0.059445 | -61.5325 | 0.0243 | -61.6 | 59.9924 | 59.9751 | 59.8424 | -61.5305 | -61.5185 | 0.082776 | -61.6217 | 59.7835 | 59.943 | 59.9417 | -61.676 | 0.047829 | -0.034168 | 0.045884 | -0.021648 | -0.069477 | -0.051437 | -0.18419 | -0.09761 | -0.24304 | 0.059871 | -0.043315 | 0.054295 | -0.083515 | -0.084892 | 121.5708 | 121.5535 | 121.4207 | 61.6027 | -121.5571 | 121.3619 | 121.5214 | 121.52 | 61.6611 | -121.7025
248.25 | 121.7926 | -61.5509 | 60.0586 | 1.4211e-13 | -0.028282 | 0.0012179 | 0.063645 | -0.0061087 | 0.054606 | -0.0099192 | -0.0014485 | -0.0012713 | 0.064052 | 0.021511 | 0.059445 | -61.5416 | 0.033457 | -61.5909 | 59.9878 | 59.966 | 59.8424 | -61.5351 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.943 | 59.9417 | -61.6668 | 0.015784 | -0.070791 | 0.009261 | -0.039958 | -0.055742 | -0.092639 | -0.21623 | -0.11592 | -0.27509 | 0.036984 | -0.070781 | 0.045137 | -0.11556 | -0.11694 | 121.5387 | 121.5169 | 121.3933 | 61.5844 | -121.5937 | 121.3344 | 121.4939 | 121.4926 | 61.6337 | -121.7254
249.9688 | 121.7789 | -61.5875 | 60.0357 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063859 | -0.0063223 | 0.05482 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063838 | 0.021297 | 0.059231 | -61.5371 | 0.033457 | -61.6 | 59.9832 | 59.9751 | 59.8424 | -61.5397 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9385 | 59.9371 | -61.6714 | 0.047826 | -0.052481 | 0.05046 | -0.012493 | -0.060319 | -0.060593 | -0.19334 | -0.083876 | -0.2522 | 0.069026 | -0.03416 | 0.049716 | -0.09725 | -0.098627 | 121.5707 | 121.5626 | 121.4299 | 61.621 | -121.5754 | 121.371 | 121.526 | 121.5246 | 61.6611 | -121.7071
251.6719 | 121.9025 | -61.5189 | 60.0494 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.021297 | 0.059231 | -61.5416 | 0.019721 | -61.6 | 59.9924 | 59.9751 | 59.8378 | -61.5305 | -61.5093 | 0.073618 | -61.6171 | 59.7743 | 59.943 | 59.9325 | -61.676 | -0.01168 | -0.057056 | -0.022782 | -0.081157 | -0.069477 | -0.074325 | -0.21165 | -0.15712 | -0.27509 | 0.009519 | -0.098245 | 0.058874 | -0.1064 | -0.11694 | 121.5112 | 121.494 | 121.3566 | 61.5386 | -121.58 | 121.2932 | 121.4619 | 121.4514 | 61.5925 | -121.7254
253.3438 | 121.875 | -61.4685 | 60.0723 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.064286 | -0.0063223 | 0.054606 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063624 | 0.021083 | 0.059231 | -61.5416 | 0.028878 | -61.6046 | 59.9832 | 59.9614 | 59.8378 | -61.5443 | -61.5231 | 0.073618 | -61.6171 | 59.7743 | 59.943 | 59.9371 | -61.676 | -0.075771 | -0.089102 | -0.073136 | -0.13609 | -0.060319 | -0.11095 | -0.23454 | -0.20747 | -0.29798 | -0.054571 | -0.1486 | 0.058874 | -0.12929 | -0.13525 | 121.4517 | 121.4299 | 121.3063 | 61.4974 | -121.6166 | 121.2429 | 121.4115 | 121.4056 | 61.5421 | -121.7483
255.0156 | 121.8063 | -61.5417 | 60.0586 | 1.4211e-13 | -0.028709 | 0.0016453 | 0.063859 | -0.0065361 | 0.054392 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063411 | 0.021297 | 0.059658 | -61.5371 | 0.0243 | -61.6046 | 59.9832 | 59.9705 | 59.8469 | -61.5351 | -61.5139 | 0.073618 | -61.6171 | 59.7789 | 59.9476 | 59.9371 | -61.6714 | 0.006629 | -0.075369 | 0.004684 | -0.062848 | -0.069477 | -0.08806 | -0.21165 | -0.12965 | -0.27967 | 0.027829 | -0.075357 | 0.054295 | -0.11098 | -0.12152 | 121.525 | 121.5123 | 121.3887 | 61.566 | -121.5937 | 121.3207 | 121.4894 | 121.4788 | 61.6154 | -121.73
256.7344 | 121.8475 | -61.4914 | 60.0723 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063859 | -0.0063223 | 0.054392 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063411 | 0.021297 | 0.059231 | -61.5371 | 0.0243 | -61.6 | 59.9924 | 59.966 | 59.8424 | -61.5443 | -61.5139 | 0.073618 | -61.6217 | 59.7789 | 59.943 | 59.9325 | -61.676 | -0.052883 | -0.079945 | -0.04567 | -0.10862 | -0.05574 | -0.10637 | -0.22996 | -0.18458 | -0.2934 | -0.022525 | -0.13029 | 0.054295 | -0.12929 | -0.13983 | 121.4838 | 121.4573 | 121.3338 | 61.5157 | -121.6166 | 121.2703 | 121.4344 | 121.4239 | 61.565 | -121.7483
258.4531 | 121.8109 | -61.5372 | 60.0449 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063432 | -0.0067497 | 0.054606 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063624 | 0.021511 | 0.059017 | -61.5416 | 0.0243 | -61.5954 | 59.9924 | 59.966 | 59.8424 | -61.5397 | -61.5185 | 0.073618 | -61.6171 | 59.7789 | 59.943 | 59.9371 | -61.676 | -0.002528 | -0.052479 | -0.004472 | -0.058269 | -0.055741 | -0.078906 | -0.2025 | -0.13881 | -0.26593 | 0.018672 | -0.079935 | 0.058874 | -0.10183 | -0.10778 | 121.5296 | 121.5031 | 121.3795 | 61.5615 | -121.5846 | 121.3161 | 121.4802 | 121.4742 | 61.6108 | -121.7208
260.1406 | 121.8979 | -61.4914 | 60.0494 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063838 | 0.021083 | 0.059231 | -61.5371 | 0.0243 | -61.6 | 59.9924 | 59.966 | 59.8378 | -61.5351 | -61.5139 | 0.073618 | -61.6171 | 59.7789 | 59.9339 | 59.9325 | -61.676 | -0.043725 | -0.057056 | -0.04567 | -0.10862 | -0.064898 | -0.083483 | -0.21165 | -0.18458 | -0.27051 | -0.022525 | -0.12571 | 0.058874 | -0.11556 | -0.11694 | 121.4838 | 121.4573 | 121.3292 | 61.5157 | -121.5846 | 121.2703 | 121.4253 | 121.4239 | 61.565 | -121.7254
261.8281 | 121.7743 | -61.5829 | 59.9899 | 1.4211e-13 | -0.028282 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063624 | 0.021297 | 0.059231 | -61.5371 | 0.033457 | -61.6 | 59.9832 | 59.966 | 59.8424 | -61.5397 | -61.5185 | 0.087354 | -61.6125 | 59.7743 | 59.943 | 59.9417 | -61.6714 | 0.043249 | -0.006704 | 0.045883 | -0.01707 | -0.060319 | -0.023974 | -0.14756 | -0.088453 | -0.21558 | 0.064449 | -0.029579 | 0.058874 | -0.046894 | -0.048271 | 121.5662 | 121.5489 | 121.4253 | 61.6164 | -121.5296 | 121.3573 | 121.526 | 121.5246 | 61.6703 | -121.6613
263.5156 | 121.8842 | -61.5738 | 59.9579 | 1.4211e-13 | -0.028495 | 0.0014317 | 0.063645 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064265 | 0.021297 | 0.059231 | -61.5371 | 0.0243 | -61.5909 | 59.9924 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7835 | 59.943 | 59.9371 | -61.676 | 0.034094 | 0.034496 | 0.036728 | -0.017069 | -0.051163 | 0.012648 | -0.11552 | -0.10219 | -0.17438 | 0.059873 | -0.047892 | 0.054295 | -0.014851 | -0.020807 | 121.5662 | 121.5443 | 121.4162 | 61.5981 | -121.4976 | 121.3573 | 121.5168 | 121.5109 | 61.652 | -121.6339
265.1875 | 121.7834 | -61.5921 | 59.9991 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063432 | -0.0065361 | 0.054392 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063838 | 0.021511 | 0.059231 | -61.5371 | 0.028878 | -61.5909 | 59.9878 | 59.966 | 59.8469 | -61.5397 | -61.5139 | 0.078197 | -61.6125 | 59.7789 | 59.943 | 59.9325 | -61.676 | 0.052404 | -0.011281 | 0.055038 | 0.001241 | -0.051163 | -0.033129 | -0.15214 | -0.083877 | -0.22016 | 0.078183 | -0.020424 | 0.063453 | -0.056049 | -0.066584 | 121.5799 | 121.5581 | 121.439 | 61.621 | -121.5388 | 121.371 | 121.5351 | 121.5246 | 61.6703 | -121.6751
266.875 | 121.8521 | -61.5051 | 60.0677 | 1.4211e-13 | -0.028495 | 0.0010043 | 0.063859 | -0.0063223 | 0.054392 | -0.01755 | -0.0014485 | -0.0012713 | 0.063624 | 0.021511 | 0.059445 | -61.5371 | 0.0243 | -61.6046 | 59.9924 | 59.9705 | 59.8469 | -61.5305 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.676 | -0.025413 | -0.075367 | -0.031937 | -0.099469 | -0.074056 | -0.097215 | -0.22081 | -0.17085 | -0.28424 | -0.008792 | -0.1074 | 0.063453 | -0.13387 | -0.13067 | 121.4975 | 121.4757 | 121.3521 | 61.5294 | -121.5983 | 121.2886 | 121.439 | 121.4422 | 61.5833 | -121.7437
268.5781 | 121.8842 | -61.5097 | 60.0632 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063645 | -0.0065361 | 0.054606 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021083 | 0.059445 | -61.5371 | 0.028878 | -61.5909 | 59.9832 | 59.9705 | 59.8424 | -61.5351 | -61.5139 | 0.073618 | -61.6171 | 59.7743 | 59.9293 | 59.9371 | -61.6668 | -0.025414 | -0.079946 | -0.027359 | -0.081156 | -0.055742 | -0.092637 | -0.22081 | -0.15712 | -0.28882 | -0.004214 | -0.1074 | 0.049716 | -0.13387 | -0.12609 | 121.4929 | 121.4802 | 121.3521 | 61.5386 | -121.5983 | 121.2841 | 121.439 | 121.4468 | 61.5833 | -121.73
270.3125 | 121.7743 | -61.5692 | 60.0082 | 1.4211e-13 | -0.028495 | 0.0014317 | 0.063645 | -0.0065361 | 0.054606 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063624 | 0.021297 | 0.059658 | -61.5416 | 0.028878 | -61.6 | 59.9924 | 59.9705 | 59.8469 | -61.5397 | -61.5185 | 0.087354 | -61.6171 | 59.7789 | 59.9339 | 59.9371 | -61.676 | 0.029516 | -0.015858 | 0.027572 | -0.030803 | -0.060319 | -0.037706 | -0.1613 | -0.10676 | -0.22931 | 0.050716 | -0.047891 | 0.058874 | -0.074362 | -0.071161 | 121.5616 | 121.5397 | 121.4162 | 61.5981 | -121.5479 | 121.3481 | 121.5031 | 121.5063 | 61.6566 | -121.6842
272 | 121.8933 | -61.5509 | 59.9808 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063645 | -0.0063223 | 0.054392 | -0.01755 | -0.0018757 | -0.0010577 | 0.063624 | 0.021297 | 0.059445 | -61.5371 | 0.028878 | -61.6 | 59.9878 | 59.966 | 59.8469 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9385 | 59.9371 | -61.6668 | 0.006626 | 0.007029 | 0.013839 | -0.049114 | -0.05574 | -0.014819 | -0.13383 | -0.11592 | -0.19727 | 0.036984 | -0.061623 | 0.054295 | -0.042318 | -0.043695 | 121.5387 | 121.5169 | 121.3978 | 61.5798 | -121.5251 | 121.3344 | 121.4894 | 121.488 | 61.6291 | -121.6476
273.6875 | 121.8521 | -61.5372 | 60.022 | 1.4211e-13 | -0.028495 | 0.0012179 | 0.063645 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.021297 | 0.059231 | -61.5371 | 0.033457 | -61.6 | 59.9878 | 59.966 | 59.8469 | -61.5397 | -61.5139 | 0.073618 | -61.6217 | 59.7789 | 59.9339 | 59.9325 | -61.6851 | -0.002528 | -0.03417 | 0.000106 | -0.062847 | -0.060319 | -0.056018 | -0.17503 | -0.14797 | -0.24305 | 0.023251 | -0.084514 | 0.063453 | -0.088095 | -0.089473 | 121.525 | 121.5031 | 121.3841 | 61.5706 | -121.5617 | 121.3161 | 121.471 | 121.4697 | 61.6108 | -121.7071
275.4531 | 121.8155 | -61.5005 | 60.0815 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0014485 | -0.0014849 | 0.063838 | 0.021511 | 0.059445 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9751 | 59.8424 | -61.5351 | -61.5139 | 0.082776 | -61.6308 | 59.7835 | 59.9339 | 59.9371 | -61.676 | -0.03457 | -0.093679 | -0.041093 | -0.099468 | -0.064898 | -0.10637 | -0.23912 | -0.17543 | -0.29798 | -0.01337 | -0.13029 | 0.045138 | -0.1476 | -0.1444 | 121.4884 | 121.4757 | 121.3429 | 61.5294 | -121.6166 | 121.2841 | 121.4344 | 121.4376 | 61.5833 | -121.7575
277.1406 | 121.7606 | -61.5875 | 60.0174 | 1.4211e-13 | -0.028495 | 0.0014317 | 0.063859 | -0.0065361 | 0.054392 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.021297 | 0.059017 | -61.5371 | 0.0243 | -61.5954 | 59.9832 | 59.9751 | 59.8424 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7789 | 59.943 | 59.9417 | -61.6714 | 0.047826 | -0.03417 | 0.05046 | -0.007915 | -0.055741 | -0.042282 | -0.17503 | -0.083876 | -0.23847 | 0.073605 | -0.029581 | 0.054295 | -0.07436 | -0.075737 | 121.5707 | 121.5626 | 121.4299 | 61.6118 | -121.5571 | 121.3665 | 121.5306 | 121.5292 | 61.6611 | -121.6888
278.8594 | 121.8567 | -61.5234 | 60.0174 | 1.4211e-13 | -0.028923 | 0.0016453 | 0.063859 | -0.0065361 | 0.054606 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063838 | 0.021938 | 0.059445 | -61.5416 | 0.028878 | -61.5909 | 59.9832 | 59.9751 | 59.8469 | -61.5397 | -61.5093 | 0.082776 | -61.6171 | 59.7835 | 59.9339 | 59.9371 | -61.6806 | -0.016261 | -0.03417 | -0.018205 | -0.067424 | -0.051163 | -0.042282 | -0.17045 | -0.15712 | -0.23389 | 0.014096 | -0.093668 | 0.063453 | -0.083517 | -0.080316 | 121.5067 | 121.4985 | 121.3704 | 61.5523 | -121.5571 | 121.3069 | 121.4573 | 121.4605 | 61.6062 | -121.698
280.5469 | 121.7697 | -61.5601 | 60.0494 | 1.4211e-13 | -0.028068 | 0.0014317 | 0.063859 | -0.0063223 | 0.054606 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.021297 | 0.059445 | -61.5462 | 0.0243 | -61.5909 | 59.9878 | 59.966 | 59.8378 | -61.5351 | -61.5139 | 0.078197 | -61.6217 | 59.7789 | 59.9385 | 59.9371 | -61.676 | 0.02494 | -0.061635 | 0.013839 | -0.030802 | -0.055742 | -0.083483 | -0.21165 | -0.11592 | -0.27051 | 0.04614 | -0.061625 | 0.054295 | -0.11098 | -0.11236 | 121.5479 | 121.526 | 121.3978 | 61.5844 | -121.5846 | 121.339 | 121.4985 | 121.4971 | 61.6383 | -121.7254
282.3281 | 121.7468 | -61.5921 | 60.0311 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063432 | -0.0065361 | 0.054606 | -0.0099192 | -0.0018757 | -0.0012713 | 0.064052 | 0.021297 | 0.059445 | -61.5325 | 0.0243 | -61.5954 | 59.9924 | 59.9751 | 59.8378 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7881 | 59.943 | 59.9371 | -61.676 | 0.047825 | -0.038746 | 0.059617 | -0.003337 | -0.051162 | -0.056015 | -0.19334 | -0.083877 | -0.24304 | 0.073604 | -0.029582 | 0.054295 | -0.088093 | -0.094049 | 121.5845 | 121.5672 | 121.4299 | 61.6164 | -121.5754 | 121.3802 | 121.5351 | 121.5292 | 61.6703 | -121.7071
284.0312 | 121.7606 | -61.6013 | 60.0357 | 1.4211e-13 | -0.028709 | 0.0010043 | 0.063645 | -0.0061087 | 0.054606 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021297 | 0.059445 | -61.5371 | 0.015142 | -61.5909 | 59.9924 | 59.9705 | 59.8469 | -61.5397 | -61.5093 | 0.073618 | -61.6217 | 59.7789 | 59.9385 | 59.9325 | -61.6714 | 0.061559 | -0.043324 | 0.064193 | 0.010396 | -0.051163 | -0.065172 | -0.18876 | -0.070143 | -0.25678 | 0.091916 | -0.020427 | 0.049716 | -0.09725 | -0.10321 | 121.5936 | 121.5718 | 121.4482 | 61.6164 | -121.5754 | 121.3802 | 121.5397 | 121.5338 | 61.6749 | -121.7071
285.7031 | 121.7422 | -61.5875 | 60.0494 | 1.4211e-13 | -0.028709 | 0.0012179 | 0.063859 | -0.0063223 | 0.05482 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.021511 | 0.059017 | -61.5325 | 0.0243 | -61.5909 | 59.9832 | 59.966 | 59.8469 | -61.5351 | -61.5139 | 0.082776 | -61.6171 | 59.7881 | 59.9339 | 59.9371 | -61.6668 | 0.052405 | -0.066213 | 0.055039 | -0.003337 | -0.055742 | -0.083483 | -0.20249 | -0.079297 | -0.26135 | 0.073605 | -0.029581 | 0.049716 | -0.11556 | -0.11236 | 121.5707 | 121.5535 | 121.4345 | 61.6118 | -121.5846 | 121.3756 | 121.5214 | 121.5246 | 61.6703 | -121.7163
287.4062 | 121.756 | -61.5189 | 60.1089 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063859 | -0.0061087 | 0.05482 | -0.0022892 | -0.0016621 | -0.0016987 | 0.063624 | 0.021297 | 0.059445 | -61.5371 | 0.0243 | -61.6 | 59.9924 | 59.9751 | 59.8424 | -61.5351 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.9385 | 59.9417 | -61.6806 | -0.016259 | -0.11657 | -0.018204 | -0.081157 | -0.064898 | -0.13383 | -0.26658 | -0.1617 | -0.32544 | 0.004941 | -0.10282 | 0.058874 | -0.17049 | -0.16729 | 121.5112 | 121.494 | 121.3612 | 61.5432 | -121.6441 | 121.3024 | 121.4573 | 121.4605 | 61.6016 | -121.7895
289.125 | 121.788 | -61.5509 | 60.0266 | 1.4211e-13 | -0.028282 | 0.0014317 | 0.063645 | -0.0063223 | 0.054606 | -0.0099192 | -0.0016621 | -0.0010577 | 0.064052 | 0.021724 | 0.059231 | -61.5462 | 0.0243 | -61.5954 | 59.9832 | 59.966 | 59.8469 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.9339 | 59.9417 | -61.676 | 0.011205 | -0.043325 | 0.004683 | -0.044536 | -0.055741 | -0.060595 | -0.17961 | -0.12508 | -0.24762 | 0.036984 | -0.066202 | 0.058874 | -0.092672 | -0.084892 | 121.5341 | 121.5169 | 121.3978 | 61.5752 | -121.5662 | 121.3298 | 121.4848 | 121.4926 | 61.6291 | -121.7025
290.8281 | 121.8887 | -61.4685 | 60.0494 | 1.4211e-13 | -0.028495 | 0.0016453 | 0.063645 | -0.0063223 | 0.054606 | -0.0022892 | -0.0014485 | -0.00084406 | 0.064052 | 0.021083 | 0.059445 | -61.5416 | 0.028878 | -61.5863 | 59.9878 | 59.9751 | 59.8424 | -61.5397 | -61.5185 | 0.06904 | -61.6171 | 59.7835 | 59.943 | 59.9417 | -61.676 | -0.071192 | -0.061635 | -0.073136 | -0.11778 | -0.046585 | -0.074325 | -0.20707 | -0.20747 | -0.26593 | -0.049992 | -0.1486 | 0.058874 | -0.1064 | -0.10778 | 121.4563 | 121.4436 | 121.3109 | 61.4974 | -121.5891 | 121.252 | 121.4115 | 121.4102 | 61.5375 | -121.7254
292.5156 | 121.7331 | -61.6013 | 60.0266 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063624 | 0.021083 | 0.059445 | -61.5325 | 0.0243 | -61.6 | 59.9924 | 59.9705 | 59.8515 | -61.5443 | -61.5185 | 0.082776 | -61.6125 | 59.7789 | 59.9385 | 59.9462 | -61.676 | 0.05698 | -0.034168 | 0.068772 | 0.00124 | -0.05574 | -0.056016 | -0.17503 | -0.074722 | -0.24762 | 0.082759 | -0.011269 | 0.063453 | -0.088094 | -0.080314 | 121.5936 | 121.5718 | 121.4528 | 61.6256 | -121.5708 | 121.3802 | 121.5397 | 121.5475 | 61.684 | -121.7025
294.2031 | 121.8887 | -61.5784 | 59.967 | 1.4211e-13 | -0.028495 | 0.0014317 | 0.063645 | -0.0063223 | 0.054606 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063624 | 0.021297 | 0.059017 | -61.5325 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8469 | -61.5443 | -61.5139 | 0.073618 | -61.6217 | 59.7881 | 59.9385 | 59.9279 | -61.6714 | 0.034092 | 0.020762 | 0.045884 | -0.021648 | -0.05574 | 0.003493 | -0.1201 | -0.093031 | -0.17896 | 0.06445 | -0.043315 | 0.049716 | -0.028585 | -0.039119 | 121.5662 | 121.5489 | 121.4253 | 61.5981 | -121.5113 | 121.3665 | 121.5168 | 121.5063 | 61.652 | -121.6384
295.9062 | 121.8979 | -61.5005 | 60.0586 | 1.4211e-13 | -0.028709 | 0.0012179 | 0.063645 | -0.0063223 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063838 | 0.021511 | 0.059231 | -61.5416 | 0.028878 | -61.5954 | 59.9832 | 59.9751 | 59.8424 | -61.5443 | -61.5277 | 0.078197 | -61.6171 | 59.7789 | 59.9339 | 59.9417 | -61.676 | -0.043728 | -0.075369 | -0.041093 | -0.09489 | -0.051162 | -0.083481 | -0.21623 | -0.17543 | -0.27967 | -0.027106 | -0.11656 | 0.058874 | -0.12472 | -0.11694 | 121.4838 | 121.4757 | 121.3429 | 61.5294 | -121.6029 | 121.2795 | 121.4344 | 121.4422 | 61.5787 | -121.7346
297.6094 | 121.8933 | -61.5005 | 60.054 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063645 | -0.0065361 | 0.05482 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.021511 | 0.059445 | -61.5416 | 0.028878 | -61.5909 | 59.9878 | 59.966 | 59.8378 | -61.5397 | -61.5231 | 0.082776 | -61.6171 | 59.7789 | 59.9339 | 59.9325 | -61.676 | -0.039149 | -0.066213 | -0.041093 | -0.090312 | -0.051163 | -0.088061 | -0.21623 | -0.17543 | -0.27509 | -0.022528 | -0.11656 | 0.058874 | -0.12014 | -0.12152 | 121.4884 | 121.4665 | 121.3383 | 61.5294 | -121.5937 | 121.2795 | 121.4344 | 121.433 | 61.5833 | -121.73
299.3438 | 121.7697 | -61.5463 | 60.0494 | 1.4211e-13 | -0.028709 | 0.0016453 | 0.063859 | -0.0065361 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.021511 | 0.059231 | -61.5416 | 0.033457 | -61.5909 | 59.9878 | 59.9751 | 59.8378 | -61.5443 | -61.5231 | 0.078197 | -61.6171 | 59.7743 | 59.9293 | 59.9417 | -61.676 | 0.002049 | -0.061635 | 0.004684 | -0.044535 | -0.046584 | -0.074325 | -0.21165 | -0.12965 | -0.27509 | 0.023249 | -0.070779 | 0.058874 | -0.12014 | -0.10778 | 121.5341 | 121.5214 | 121.3841 | 61.5798 | -121.5937 | 121.3207 | 121.4756 | 121.488 | 61.6245 | -121.7254
301.0312 | 121.7972 | -61.5005 | 60.0861 | 1.4211e-13 | -0.028923 | 0.0014317 | 0.063432 | -0.0063223 | 0.054392 | -0.01755 | -0.0016621 | -0.0012713 | 0.063624 | 0.021511 | 0.059231 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7881 | 59.9339 | 59.9417 | -61.6714 | -0.039149 | -0.098257 | -0.041093 | -0.099468 | -0.060319 | -0.11553 | -0.2437 | -0.17085 | -0.29798 | -0.01337 | -0.11656 | 0.054295 | -0.15218 | -0.1444 | 121.4884 | 121.4711 | 121.3429 | 61.5294 | -121.6258 | 121.2886 | 121.4344 | 121.4422 | 61.5742 | -121.7575
302.7344 | 121.7514 | -61.5646 | 60.0174 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021511 | 0.059231 | -61.5325 | 0.0243 | -61.5909 | 59.997 | 59.9705 | 59.8469 | -61.5351 | -61.5185 | 0.078197 | -61.6125 | 59.7789 | 59.9339 | 59.9417 | -61.6714 | 0.029517 | -0.020435 | 0.032151 | -0.026225 | -0.055742 | -0.046861 | -0.17045 | -0.10676 | -0.23847 | 0.046138 | -0.04789 | 0.058874 | -0.083517 | -0.075737 | 121.5616 | 121.5352 | 121.4116 | 61.5889 | -121.5525 | 121.3436 | 121.4985 | 121.5063 | 61.6428 | -121.6888
304.4219 | 121.8201 | -61.5097 | 60.0815 | 1.4211e-13 | -0.028709 | 0.0012179 | 0.064073 | -0.0067497 | 0.054392 | -0.0099192 | -0.0020893 | -0.0014849 | 0.063838 | 0.021724 | 0.059445 | -61.5462 | 0.028878 | -61.6 | 59.9878 | 59.9705 | 59.8424 | -61.5443 | -61.5139 | 0.06904 | -61.6171 | 59.7881 | 59.9339 | 59.9325 | -61.6806 | -0.034572 | -0.093679 | -0.036515 | -0.090312 | -0.05574 | -0.11095 | -0.23912 | -0.17085 | -0.2934 | -0.004214 | -0.1074 | 0.063453 | -0.1476 | -0.14898 | 121.4975 | 121.4802 | 121.3521 | 61.5386 | -121.6258 | 121.2978 | 121.4436 | 121.4422 | 61.5787 | -121.762
306.125 | 121.875 | -61.5509 | 59.9625 | 1.4211e-13 | -0.028923 | 0.0014317 | 0.063645 | -0.0063223 | 0.05482 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064052 | 0.021083 | 0.059445 | -61.5279 | 0.0243 | -61.5909 | 59.9878 | 59.9705 | 59.8469 | -61.5351 | -61.5185 | 0.073618 | -61.6171 | 59.7835 | 59.9385 | 59.9417 | -61.6668 | 0.015784 | 0.02534 | 0.022996 | -0.039958 | -0.055742 | 0.008071 | -0.11552 | -0.11592 | -0.17896 | 0.032405 | -0.066202 | 0.049716 | -0.024007 | -0.020805 | 121.5387 | 121.5214 | 121.3978 | 61.5752 | -121.4976 | 121.3344 | 121.4894 | 121.4926 | 61.6245 | -121.6293
307.8281 | 121.8109 | -61.5372 | 60.0586 | 1.4211e-13 | -0.028495 | 0.0010043 | 0.063859 | -0.0065361 | 0.054179 | -0.0022892 | -0.0012349 | -0.0010577 | 0.063838 | 0.021511 | 0.059017 | -61.5371 | 0.0243 | -61.6 | 59.9924 | 59.9751 | 59.8469 | -61.5351 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.9385 | 59.9417 | -61.676 | 0.002051 | -0.066212 | 0.000106 | -0.062847 | -0.064898 | -0.083481 | -0.21165 | -0.13881 | -0.27967 | 0.023251 | -0.079935 | 0.058874 | -0.12014 | -0.11694 | 121.5296 | 121.5123 | 121.3841 | 61.5615 | -121.5937 | 121.3161 | 121.4756 | 121.4788 | 61.6154 | -121.7346
309.5312 | 121.8842 | -61.496 | 60.0449 | 1.4211e-13 | -0.028923 | 0.0016453 | 0.063859 | -0.0065361 | 0.054392 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.021724 | 0.059445 | -61.5462 | 0.0243 | -61.6046 | 59.9924 | 59.966 | 59.8378 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7743 | 59.943 | 59.9417 | -61.676 | -0.043726 | -0.052479 | -0.050248 | -0.10862 | -0.064898 | -0.078906 | -0.20707 | -0.18001 | -0.27051 | -0.017947 | -0.12113 | 0.058874 | -0.10183 | -0.1032 | 121.4884 | 121.4619 | 121.3338 | 61.5203 | -121.5846 | 121.2703 | 121.439 | 121.4376 | 61.5696 | -121.7208
311.2031 | 121.7468 | -61.5189 | 60.1135 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063432 | -0.0065361 | 0.054392 | -0.01755 | -0.0014485 | -0.0012713 | 0.063624 | 0.021297 | 0.059445 | -61.5508 | 0.019721 | -61.6092 | 59.9878 | 59.9751 | 59.8424 | -61.5397 | -61.5185 | 0.078197 | -61.6217 | 59.7835 | 59.9385 | 59.9371 | -61.6714 | -0.020838 | -0.12572 | -0.031939 | -0.090314 | -0.069476 | -0.13841 | -0.27116 | -0.15254 | -0.33002 | 0.000362 | -0.10282 | 0.049716 | -0.17507 | -0.17645 | 121.5067 | 121.494 | 121.3612 | 61.5386 | -121.6532 | 121.3024 | 121.4573 | 121.4559 | 61.5971 | -121.7849
312.875 | 121.8796 | -61.5555 | 59.9899 | 1.4211e-13 | -0.029136 | 0.0016453 | 0.063645 | -0.0065361 | 0.054392 | -0.01755 | -0.0018757 | -0.0010577 | 0.064052 | 0.021724 | 0.059017 | -61.5325 | 0.033457 | -61.6 | 59.9924 | 59.9705 | 59.8469 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9339 | 59.9325 | -61.6714 | 0.011204 | 0.002453 | 0.022996 | -0.044536 | -0.05574 | -0.019395 | -0.14299 | -0.11592 | -0.20642 | 0.041562 | -0.057045 | 0.058874 | -0.056051 | -0.057429 | 121.5479 | 121.526 | 121.4024 | 61.5889 | -121.5342 | 121.339 | 121.4894 | 121.488 | 61.6337 | -121.6613
314.5625 | 121.8246 | -61.5326 | 60.0082 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063859 | -0.0065361 | 0.054606 | -0.0022892 | -0.0014485 | -0.0014849 | 0.063838 | 0.021724 | 0.059445 | -61.5416 | 0.033457 | -61.5954 | 59.9924 | 59.9843 | 59.8469 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7743 | 59.9339 | 59.9325 | -61.6622 | -0.007105 | -0.015858 | -0.009049 | -0.062846 | -0.055741 | -0.02397 | -0.1613 | -0.12965 | -0.23389 | 0.014095 | -0.084512 | 0.045138 | -0.074362 | -0.07574 | 121.525 | 121.5169 | 121.3795 | 61.566 | -121.5479 | 121.3069 | 121.4665 | 121.4651 | 61.6108 | -121.6705
316.2969 | 121.8246 | -61.5738 | 59.9945 | 1.4211e-13 | -0.028709 | 0.0016453 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0020893 | -0.0010577 | 0.063838 | 0.021083 | 0.059231 | -61.5325 | 0.0243 | -61.5909 | 59.9878 | 59.9797 | 59.8469 | -61.5351 | -61.5185 | 0.073618 | -61.6217 | 59.7835 | 59.9385 | 59.9371 | -61.6714 | 0.038673 | -0.006704 | 0.041307 | -0.017069 | -0.055742 | -0.014815 | -0.14756 | -0.097608 | -0.211 | 0.055294 | -0.047892 | 0.049716 | -0.056051 | -0.057428 | 121.5616 | 121.5535 | 121.4207 | 61.5981 | -121.5296 | 121.3573 | 121.5122 | 121.5109 | 61.6474 | -121.6659
317.9844 | 121.8887 | -61.5509 | 59.9487 | 1.4211e-13 | -0.028709 | 0.0016453 | 0.063645 | -0.0065361 | 0.054392 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021724 | 0.059445 | -61.5325 | 0.0243 | -61.6 | 59.9878 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.9339 | 59.9371 | -61.6714 | 0.011205 | 0.039073 | 0.018418 | -0.049114 | -0.060319 | 0.021804 | -0.10637 | -0.1205 | -0.16522 | 0.036984 | -0.066202 | 0.054295 | -0.014852 | -0.011651 | 121.5387 | 121.5214 | 121.3933 | 61.5752 | -121.4884 | 121.3344 | 121.4848 | 121.488 | 61.6337 | -121.6201
319.6875 | 121.756 | -61.5189 | 60.1181 | 1.4211e-13 | -0.028709 | 0.0018589 | 0.063645 | -0.0063223 | 0.054179 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063838 | 0.021724 | 0.059658 | -61.5325 | 0.0243 | -61.5909 | 59.9832 | 59.9705 | 59.8469 | -61.5397 | -61.5139 | 0.078197 | -61.6263 | 59.7835 | 59.9293 | 59.9371 | -61.676 | -0.020838 | -0.13488 | -0.013625 | -0.072001 | -0.051163 | -0.14757 | -0.27116 | -0.15712 | -0.3346 | 0.004941 | -0.1074 | 0.049716 | -0.1888 | -0.18102 | 121.5021 | 121.4894 | 121.3658 | 61.5432 | -121.6578 | 121.3024 | 121.4482 | 121.4559 | 61.5971 | -121.7941
321.3594 | 121.7789 | -61.5326 | 60.0952 | 1.4211e-13 | -0.028923 | 0.0016453 | 0.063645 | -0.0065361 | 0.05482 | -0.0022892 | -0.0016621 | -0.00084406 | 0.063624 | 0.021511 | 0.059445 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9751 | 59.8469 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.676 | -0.007105 | -0.10741 | 0.000108 | -0.062846 | -0.055741 | -0.1201 | -0.24827 | -0.14339 | -0.31171 | 0.018674 | -0.089091 | 0.054295 | -0.16134 | -0.15814 | 121.5204 | 121.5077 | 121.3795 | 61.5569 | -121.6349 | 121.3161 | 121.4665 | 121.4697 | 61.6154 | -121.7712
323.0625 | 121.8292 | -61.5417 | 60.0403 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063432 | -0.0063223 | 0.054392 | -0.02518 | -0.0016621 | -0.0014849 | 0.063838 | 0.021511 | 0.059231 | -61.5371 | 0.0243 | -61.5954 | 59.9832 | 59.9751 | 59.8469 | -61.5351 | -61.5093 | 0.078197 | -61.6171 | 59.7835 | 59.9247 | 59.9325 | -61.6714 | 0.006629 | -0.057058 | 0.004684 | -0.053691 | -0.06032 | -0.06517 | -0.19334 | -0.12965 | -0.25678 | 0.032407 | -0.075357 | 0.054295 | -0.11556 | -0.10778 | 121.525 | 121.5169 | 121.3887 | 61.566 | -121.5754 | 121.3253 | 121.4665 | 121.4742 | 61.6199 | -121.7117
324.75 | 121.8842 | -61.4822 | 60.0769 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063645 | -0.0065361 | 0.054606 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021297 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8469 | -61.5397 | -61.5185 | 0.078197 | -61.6217 | 59.7789 | 59.9293 | 59.9417 | -61.676 | -0.057459 | -0.089101 | -0.054825 | -0.11778 | -0.060319 | -0.10637 | -0.22996 | -0.19374 | -0.29798 | -0.036259 | -0.13945 | 0.054295 | -0.1476 | -0.13525 | 121.47 | 121.4528 | 121.3292 | 61.502 | -121.6166 | 121.2612 | 121.4115 | 121.4239 | 61.5604 | -121.7529
326.4219 | 121.8658 | -61.5509 | 59.9854 | 1.4211e-13 | -0.028709 | 0.0016453 | 0.063859 | -0.0069633 | 0.05482 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.021297 | 0.059231 | -61.5371 | 0.028878 | -61.6 | 59.9832 | 59.9705 | 59.8424 | -61.5397 | -61.5093 | 0.078197 | -61.6217 | 59.7835 | 59.9385 | 59.9371 | -61.6714 | 0.011205 | -0.002127 | 0.013839 | -0.049114 | -0.060319 | -0.014818 | -0.14299 | -0.1205 | -0.20184 | 0.041562 | -0.070781 | 0.049716 | -0.046896 | -0.048273 | 121.5341 | 121.5214 | 121.3933 | 61.5798 | -121.525 | 121.3344 | 121.4894 | 121.488 | 61.6291 | -121.6568
328.1406 | 121.8292 | -61.5417 | 60.0082 | 1.4211e-13 | -0.029136 | 0.0012179 | 0.063645 | -0.0063223 | 0.05482 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021724 | 0.059658 | -61.5416 | 0.0243 | -61.5954 | 59.9878 | 59.9705 | 59.8332 | -61.5397 | -61.5093 | 0.082776 | -61.6125 | 59.7835 | 59.9339 | 59.9325 | -61.6806 | 0.00205 | -0.020437 | 0.000106 | -0.053691 | -0.055741 | -0.037706 | -0.17503 | -0.13881 | -0.22473 | 0.032407 | -0.070778 | 0.068032 | -0.074362 | -0.07574 | 121.5296 | 121.5123 | 121.375 | 61.566 | -121.5479 | 121.3253 | 121.4756 | 121.4742 | 61.6245 | -121.6888
329.875 | 121.9116 | -61.496 | 60.0586 | 1.4211e-13 | -0.029136 | 0.0016453 | 0.063859 | -0.0061087 | 0.054179 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.021511 | 0.059445 | -61.5325 | 0.028878 | -61.6046 | 59.9832 | 59.9705 | 59.8469 | -61.5351 | -61.5093 | 0.078197 | -61.6171 | 59.7743 | 59.9476 | 59.9325 | -61.676 | -0.039147 | -0.075369 | -0.036513 | -0.10862 | -0.069477 | -0.08806 | -0.21165 | -0.18001 | -0.28424 | -0.013369 | -0.12113 | 0.058874 | -0.11098 | -0.12609 | 121.4792 | 121.4665 | 121.3429 | 61.5249 | -121.5937 | 121.2703 | 121.4436 | 121.4285 | 61.5742 | -121.7346
331.5625 | 121.7377 | -61.6058 | 60.0266 | 1.4211e-13 | -0.029136 | 0.0016453 | 0.063645 | -0.0067497 | 0.054179 | -0.01755 | -0.0016621 | -0.0010577 | 0.063624 | 0.021511 | 0.059231 | -61.5371 | 0.0243 | -61.6 | 59.9924 | 59.9705 | 59.8469 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7743 | 59.943 | 59.9371 | -61.6714 | 0.066137 | -0.034168 | 0.068771 | 0.005818 | -0.060319 | -0.056016 | -0.17961 | -0.065565 | -0.2522 | 0.091916 | -0.01127 | 0.054295 | -0.083515 | -0.089471 | 121.5982 | 121.5764 | 121.4528 | 61.6301 | -121.5662 | 121.3802 | 121.5489 | 121.5429 | 61.6795 | -121.6979
333.2812 | 121.8796 | -61.4868 | 60.0311 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063432 | -0.0067497 | 0.054392 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.021511 | 0.059445 | -61.5371 | 0.0243 | -61.5954 | 59.9832 | 59.9705 | 59.8378 | -61.5351 | -61.5093 | 0.073618 | -61.6171 | 59.7835 | 59.9339 | 59.9371 | -61.676 | -0.048303 | -0.047903 | -0.050248 | -0.10862 | -0.06032 | -0.060594 | -0.19334 | -0.18916 | -0.24762 | -0.022525 | -0.13029 | 0.058874 | -0.09725 | -0.094049 | 121.47 | 121.4573 | 121.3246 | 61.5111 | -121.5662 | 121.2703 | 121.4207 | 121.4239 | 61.5604 | -121.7071
335.0312 | 121.8933 | -61.5738 | 59.9899 | 1.4211e-13 | -0.028923 | 0.0012179 | 0.063645 | -0.0067497 | 0.054606 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.021511 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.9878 | 59.9751 | 59.8515 | -61.5443 | -61.5185 | 0.082776 | -61.6171 | 59.7698 | 59.9476 | 59.9371 | -61.6714 | 0.029515 | -0.002126 | 0.036728 | -0.021647 | -0.051162 | -0.014816 | -0.13841 | -0.097608 | -0.22016 | 0.055294 | -0.043313 | 0.054295 | -0.042316 | -0.05285 | 121.5616 | 121.5489 | 121.4253 | 61.6027 | -121.5342 | 121.3436 | 121.5214 | 121.5109 | 61.6566 | -121.6613
336.7188 | 121.788 | -61.5875 | 60.0403 | 1.4211e-13 | -0.028923 | 0.0014317 | 0.063432 | -0.0065361 | 0.054179 | -0.0099192 | -0.0016621 | -0.00063026 | 0.063624 | 0.021297 | 0.058804 | -61.5371 | 0.0243 | -61.5954 | 59.9878 | 59.9705 | 59.8561 | -61.5397 | -61.5185 | 0.073618 | -61.6263 | 59.7789 | 59.9476 | 59.9417 | -61.676 | 0.047826 | -0.05248 | 0.05046 | -0.007915 | -0.055741 | -0.069749 | -0.18418 | -0.088455 | -0.26136 | 0.069026 | -0.038739 | 0.049716 | -0.09267 | -0.098625 | 121.5753 | 121.5581 | 121.4436 | 61.6118 | -121.58 | 121.3665 | 121.5351 | 121.5292 | 61.6611 | -121.7163
338.4062 | 121.843 | -61.5601 | 60.0037 | 1.4211e-13 | -0.029136 | 0.0012179 | 0.063432 | -0.0065361 | 0.054606 | -0.0099192 | -0.0016621 | -0.00084406 | 0.063624 | 0.021724 | 0.059231 | -61.5416 | 0.0243 | -61.5954 | 59.9832 | 59.9705 | 59.8378 | -61.5305 | -61.5139 | 0.073618 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.676 | 0.029519 | -0.020437 | 0.018417 | -0.03538 | -0.064899 | -0.033128 | -0.16588 | -0.11592 | -0.22015 | 0.04614 | -0.057046 | 0.058874 | -0.060627 | -0.066583 | 121.5433 | 121.5306 | 121.3978 | 61.5844 | -121.5342 | 121.3436 | 121.5031 | 121.4971 | 61.6337 | -121.6796
340.1094 | 121.8933 | -61.4777 | 60.0403 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063859 | -0.0067497 | 0.054179 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063624 | 0.021511 | 0.059017 | -61.5371 | 0.0243 | -61.6046 | 59.9924 | 59.9751 | 59.8469 | -61.5351 | -61.5185 | 0.087354 | -61.6171 | 59.7743 | 59.9339 | 59.9279 | -61.6806 | -0.057458 | -0.047901 | -0.059403 | -0.12694 | -0.069477 | -0.06517 | -0.19334 | -0.2029 | -0.26593 | -0.040837 | -0.13944 | 0.063453 | -0.10641 | -0.11236 | 121.47 | 121.4528 | 121.3246 | 61.502 | -121.5754 | 121.252 | 121.4115 | 121.4056 | 61.565 | -121.7208
341.8281 | 121.8338 | -61.528 | 59.9991 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063432 | -0.0067497 | 0.053965 | -0.0022892 | -0.0020893 | -0.0010577 | 0.063411 | 0.021511 | 0.059017 | -61.5371 | 0.0243 | -61.5954 | 59.9832 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.078197 | -61.6079 | 59.7789 | 59.9385 | 59.9325 | -61.676 | -0.011683 | -0.015859 | -0.009049 | -0.067424 | -0.055741 | -0.02855 | -0.15672 | -0.14796 | -0.22016 | 0.014096 | -0.079933 | 0.068031 | -0.060628 | -0.066584 | 121.5112 | 121.4985 | 121.3704 | 61.5523 | -121.5388 | 121.3069 | 121.4665 | 121.4605 | 61.6062 | -121.6751
343.5156 | 121.8292 | -61.5555 | 60.0037 | 1.4211e-13 | -0.028923 | 0.0012179 | 0.063432 | -0.0065361 | 0.054392 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063624 | 0.021724 | 0.059231 | -61.5325 | 0.028878 | -61.6046 | 59.9878 | 59.9751 | 59.8515 | -61.5397 | -61.5139 | 0.073618 | -61.6171 | 59.7835 | 59.9293 | 59.9371 | -61.676 | 0.015783 | -0.015859 | 0.022996 | -0.049115 | -0.064898 | -0.028549 | -0.15214 | -0.1205 | -0.22015 | 0.041562 | -0.061624 | 0.058874 | -0.074363 | -0.066583 | 121.5433 | 121.5306 | 121.407 | 61.5844 | -121.5434 | 121.339 | 121.4848 | 121.4926 | 61.6291 | -121.6796
345.25 | 121.7789 | -61.5143 | 60.1044 | 1.4211e-13 | -0.029136 | 0.0016453 | 0.063859 | -0.0065361 | 0.054392 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021511 | 0.059231 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.966 | 59.8469 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.9339 | 59.9371 | -61.6806 | -0.029995 | -0.11657 | -0.018203 | -0.081157 | -0.051162 | -0.13842 | -0.25743 | -0.16628 | -0.32544 | 0.000363 | -0.10282 | 0.063453 | -0.17049 | -0.16729 | 121.5021 | 121.4802 | 121.3612 | 61.5386 | -121.6486 | 121.2932 | 121.4482 | 121.4514 | 61.5925 | -121.7849
346.9375 | 121.8887 | -61.4914 | 60.0494 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063645 | -0.0063223 | 0.054179 | -0.0099192 | -0.0018757 | -0.00084406 | 0.064052 | 0.021511 | 0.059231 | -61.5325 | 0.028878 | -61.6 | 59.9878 | 59.9705 | 59.8424 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6668 | -0.052883 | -0.061635 | -0.041091 | -0.10862 | -0.05574 | -0.078904 | -0.20707 | -0.17543 | -0.26593 | -0.027104 | -0.13029 | 0.045137 | -0.11556 | -0.11236 | 121.4792 | 121.4619 | 121.3338 | 61.5203 | -121.5937 | 121.2749 | 121.4253 | 121.4285 | 61.5696 | -121.7163
348.625 | 121.8704 | -61.5234 | 60.0311 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063859 | -0.0065361 | 0.054392 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063411 | 0.021511 | 0.059445 | -61.5371 | 0.028878 | -61.6 | 59.9924 | 59.9705 | 59.8424 | -61.5351 | -61.5139 | 0.078197 | -61.6263 | 59.7789 | 59.9339 | 59.9371 | -61.676 | -0.011682 | -0.038746 | -0.013627 | -0.07658 | -0.064898 | -0.060594 | -0.18876 | -0.15254 | -0.2522 | 0.009518 | -0.10283 | 0.049716 | -0.09725 | -0.094049 | 121.5158 | 121.494 | 121.3658 | 61.5523 | -121.5662 | 121.3024 | 121.4573 | 121.4605 | 61.6016 | -121.7071
350.3438 | 121.756 | -61.5784 | 60.0311 | 1.4211e-13 | -0.028709 | 0.0014317 | 0.063432 | -0.0061087 | 0.054606 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063838 | 0.021938 | 0.059231 | -61.5325 | 0.028878 | -61.6 | 59.9924 | 59.9705 | 59.8424 | -61.5397 | -61.5139 | 0.082776 | -61.6079 | 59.7789 | 59.9385 | 59.9325 | -61.6806 | 0.038671 | -0.038746 | 0.045884 | -0.021648 | -0.060319 | -0.060594 | -0.18876 | -0.10219 | -0.2522 | 0.06445 | -0.029579 | 0.07261 | -0.092672 | -0.098628 | 121.5708 | 121.5489 | 121.4207 | 61.6072 | -121.5708 | 121.3573 | 121.5168 | 121.5109 | 61.6611 | -121.7117
352.0469 | 121.7789 | -61.528 | 60.0952 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063645 | -0.0065361 | 0.054606 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.021511 | 0.059231 | -61.5508 | 0.019721 | -61.6 | 59.9832 | 59.9751 | 59.8424 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.6851 | -0.011683 | -0.11199 | -0.022784 | -0.072002 | -0.060319 | -0.1201 | -0.25285 | -0.15712 | -0.31171 | 0.009517 | -0.08909 | 0.068032 | -0.15676 | -0.15814 | 121.5112 | 121.5031 | 121.3704 | 61.5477 | -121.6349 | 121.3115 | 121.4665 | 121.4651 | 61.6062 | -121.7804
353.7344 | 121.8475 | -61.5509 | 59.9945 | 1.4211e-13 | -0.029564 | 0.0014317 | 0.063645 | -0.0067497 | 0.054606 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063838 | 0.021938 | 0.059231 | -61.5325 | 0.0243 | -61.5909 | 59.9878 | 59.9751 | 59.8469 | -61.5351 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9385 | 59.9417 | -61.6714 | 0.015784 | -0.006704 | 0.018418 | -0.039958 | -0.055742 | -0.019394 | -0.14756 | -0.1205 | -0.211 | 0.032405 | -0.066202 | 0.054295 | -0.056051 | -0.052849 | 121.5387 | 121.526 | 121.3978 | 61.5752 | -121.5296 | 121.3344 | 121.4894 | 121.4926 | 61.6291 | -121.6659
355.4375 | 121.8933 | -61.4685 | 60.0174 | 1.4211e-13 | -0.029136 | 0.0010043 | 0.063432 | -0.0067497 | 0.054392 | 0.0053413 | -0.0016621 | -0.0014849 | 0.063624 | 0.021938 | 0.059231 | -61.5462 | 0.033457 | -61.6 | 59.9878 | 59.9705 | 59.8424 | -61.5443 | -61.5185 | 0.078197 | -61.6125 | 59.7789 | 59.9385 | 59.9371 | -61.6851 | -0.075771 | -0.029592 | -0.077714 | -0.13151 | -0.05574 | -0.046861 | -0.17503 | -0.21663 | -0.23847 | -0.049992 | -0.14402 | 0.072611 | -0.078939 | -0.080316 | 121.4563 | 121.439 | 121.3109 | 61.502 | -121.5617 | 121.2474 | 121.407 | 121.4056 | 61.5467 | -121.7025
357.1562 | 121.8292 | -61.5463 | 59.9945 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063859 | -0.0067497 | 0.054392 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.021724 | 0.058804 | -61.5325 | 0.028878 | -61.5954 | 59.9924 | 59.9705 | 59.8469 | -61.5351 | -61.5231 | 0.078197 | -61.6125 | 59.7881 | 59.9385 | 59.9462 | -61.6714 | 0.011207 | -0.002125 | 0.013841 | -0.049113 | -0.06032 | -0.023973 | -0.14756 | -0.12507 | -0.20642 | 0.023249 | -0.0662 | 0.058874 | -0.056051 | -0.048271 | 121.5387 | 121.5169 | 121.3933 | 61.5752 | -121.5296 | 121.3344 | 121.4848 | 121.4926 | 61.6245 | -121.6659
358.9219 | 121.8109 | -61.5417 | 60.0769 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063645 | -0.0063223 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.021724 | 0.059231 | -61.5371 | 0.0243 | -61.5954 | 59.9878 | 59.966 | 59.8515 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9325 | -61.676 | 0.00205 | -0.089101 | 0.004684 | -0.053691 | -0.055741 | -0.11095 | -0.22538 | -0.13423 | -0.2934 | 0.02325 | -0.075357 | 0.058874 | -0.13387 | -0.1444 | 121.5296 | 121.5077 | 121.3933 | 61.566 | -121.6166 | 121.3253 | 121.4848 | 121.4742 | 61.6199 | -121.7529
360.6406 | 121.7514 | -61.5234 | 60.1135 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063859 | -0.0065361 | 0.054392 | -0.01755 | -0.0018757 | -0.0014849 | 0.063838 | 0.021938 | 0.059445 | -61.5416 | 0.0243 | -61.5954 | 59.9832 | 59.9797 | 59.8561 | -61.5305 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.676 | -0.007103 | -0.1303 | -0.018205 | -0.072002 | -0.064899 | -0.13383 | -0.25743 | -0.15254 | -0.33002 | 0.004939 | -0.093668 | 0.058874 | -0.17507 | -0.17645 | 121.5067 | 121.5031 | 121.3795 | 61.5477 | -121.6441 | 121.3069 | 121.4619 | 121.4605 | 61.6016 | -121.7895
362.4219 | 121.7422 | -61.5829 | 60.0128 | 1.4211e-13 | -0.028923 | 0.0016453 | 0.063645 | -0.0063223 | 0.053751 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021938 | 0.059017 | -61.5371 | 0.0243 | -61.6046 | 59.9924 | 59.9751 | 59.8515 | -61.5351 | -61.5093 | 0.078197 | -61.6171 | 59.7789 | 59.9339 | 59.9508 | -61.6714 | 0.047828 | -0.020435 | 0.045883 | -0.021649 | -0.069477 | -0.037704 | -0.1613 | -0.088453 | -0.23389 | 0.073606 | -0.034158 | 0.054295 | -0.078939 | -0.062002 | 121.5753 | 121.5581 | 121.4345 | 61.6072 | -121.5479 | 121.3619 | 121.5168 | 121.5338 | 61.6611 | -121.6842
364.1094 | 121.788 | -61.5326 | 60.0494 | 1.4211e-13 | -0.029136 | 0.0014317 | 0.063432 | -0.0063223 | 0.054392 | -0.0022892 | -0.0016621 | -0.00084406 | 0.063838 | 0.021724 | 0.059017 | -61.5325 | 0.0243 | -61.6046 | 59.9878 | 59.9705 | 59.8515 | -61.5489 | -61.5139 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9462 | -61.6714 | -0.016263 | -0.061635 | 0.000108 | -0.072003 | -0.05574 | -0.078904 | -0.19792 | -0.13881 | -0.26593 | 0.018674 | -0.084512 | 0.054295 | -0.1064 | -0.1032 | 121.5204 | 121.5031 | 121.3841 | 61.5569 | -121.5983 | 121.3161 | 121.4756 | 121.4788 | 61.6108 | -121.7208
365.8594 | 121.8246 | -61.5372 | 60.0174 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.021724 | 0.059231 | -61.5416 | 0.0243 | -61.6046 | 59.9924 | 59.9705 | 59.8515 | -61.5397 | -61.5185 | 0.073618 | -61.6171 | 59.7835 | 59.943 | 59.9325 | -61.6806 | -0.002528 | -0.025013 | -0.004472 | -0.067426 | -0.064898 | -0.046861 | -0.16587 | -0.14339 | -0.23389 | 0.018672 | -0.079935 | 0.063453 | -0.07436 | -0.084895 | 121.5296 | 121.5077 | 121.3887 | 61.5615 | -121.5571 | 121.3207 | 121.4802 | 121.4697 | 61.6108 | -121.698
367.5469 | 121.8246 | -61.5509 | 60.0128 | 1.4211e-13 | -0.029136 | 0.0016453 | 0.063432 | -0.0067497 | 0.053965 | -0.0099192 | -0.0016621 | -0.00084406 | 0.063838 | 0.021724 | 0.059445 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9751 | 59.8469 | -61.5397 | -61.5139 | 0.082776 | -61.6125 | 59.7789 | 59.943 | 59.9371 | -61.6714 | 0.011205 | -0.025014 | 0.009261 | -0.049114 | -0.060319 | -0.037704 | -0.16587 | -0.1205 | -0.23389 | 0.036984 | -0.061623 | 0.058874 | -0.069782 | -0.075738 | 121.5387 | 121.526 | 121.3978 | 61.5798 | -121.5525 | 121.3298 | 121.4939 | 121.488 | 61.6337 | -121.6842
369.3125 | 121.875 | -61.5738 | 59.9808 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063645 | -0.0065361 | 0.053965 | -0.01755 | -0.0018757 | -0.0012713 | 0.063411 | 0.021724 | 0.059017 | -61.5416 | 0.0243 | -61.5909 | 59.9832 | 59.9705 | 59.8515 | -61.5397 | -61.5185 | 0.082776 | -61.6171 | 59.7789 | 59.943 | 59.9417 | -61.6806 | 0.034094 | 0.002451 | 0.03215 | -0.017069 | -0.051163 | -0.01024 | -0.12925 | -0.10677 | -0.20185 | 0.055294 | -0.043313 | 0.063453 | -0.037739 | -0.039116 | 121.557 | 121.5443 | 121.4253 | 61.5981 | -121.5205 | 121.3527 | 121.5168 | 121.5154 | 61.6566 | -121.6613
371.0781 | 121.7743 | -61.5509 | 60.0357 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.064073 | -0.0063223 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.021511 | 0.059231 | -61.5325 | 0.028878 | -61.6 | 59.9924 | 59.9751 | 59.8469 | -61.5489 | -61.5093 | 0.073618 | -61.6171 | 59.7789 | 59.943 | 59.9462 | -61.676 | 0.002047 | -0.043324 | 0.018418 | -0.049114 | -0.051161 | -0.060593 | -0.18876 | -0.12508 | -0.25678 | 0.041562 | -0.066202 | 0.058874 | -0.092671 | -0.08947 | 121.5433 | 121.526 | 121.3978 | 61.5798 | -121.5846 | 121.3298 | 121.4939 | 121.4971 | 61.6245 | -121.7117
372.8438 | 121.7697 | -61.5646 | 60.0357 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063859 | -0.0065361 | 0.053965 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063411 | 0.021724 | 0.059017 | -61.5371 | 0.028878 | -61.5954 | 59.9878 | 59.9705 | 59.8607 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7743 | 59.943 | 59.9462 | -61.6806 | 0.020359 | -0.047903 | 0.027572 | -0.030803 | -0.051162 | -0.065172 | -0.17503 | -0.11592 | -0.26136 | 0.046138 | -0.057048 | 0.058874 | -0.092671 | -0.08947 | 121.5524 | 121.5352 | 121.4253 | 61.5935 | -121.58 | 121.339 | 121.5077 | 121.5109 | 61.6428 | -121.7163
374.5312 | 121.7697 | -61.5097 | 60.1044 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063432 | -0.0063223 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063624 | 0.021724 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8469 | -61.5397 | -61.5093 | 0.078197 | -61.6217 | 59.7743 | 59.9293 | 59.9371 | -61.6851 | -0.029993 | -0.11657 | -0.027359 | -0.090312 | -0.060319 | -0.13384 | -0.25743 | -0.17543 | -0.33002 | 0.000364 | -0.11198 | 0.063453 | -0.17507 | -0.16729 | 121.4975 | 121.4802 | 121.3566 | 61.5294 | -121.6441 | 121.2841 | 121.439 | 121.4468 | 61.5879 | -121.7895
376.2656 | 121.756 | -61.6196 | 60.0403 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063859 | -0.0065361 | 0.053965 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063624 | 0.021511 | 0.059017 | -61.5279 | 0.028878 | -61.6 | 59.9878 | 59.966 | 59.8469 | -61.5351 | -61.5139 | 0.082776 | -61.6171 | 59.7789 | 59.9385 | 59.9417 | -61.676 | 0.084449 | -0.05248 | 0.091661 | 0.019551 | -0.064898 | -0.074328 | -0.19334 | -0.056411 | -0.26136 | 0.10565 | 0.002463 | 0.058874 | -0.10183 | -0.098625 | 121.6074 | 121.5855 | 121.4665 | 61.6484 | -121.5754 | 121.3985 | 121.558 | 121.5612 | 61.7023 | -121.7163
378.0312 | 121.7743 | -61.5921 | 60.022 | 1.4211e-13 | -0.02935 | 0.0018589 | 0.063645 | -0.0063223 | 0.054179 | 0.0053413 | -0.0014485 | -0.0012713 | 0.063838 | 0.021938 | 0.059231 | -61.5325 | 0.019721 | -61.6138 | 59.9878 | 59.9705 | 59.8469 | -61.5397 | -61.5185 | 0.087354 | -61.6125 | 59.7835 | 59.9339 | 59.9417 | -61.6806 | 0.052404 | -0.03417 | 0.059617 | -0.02165 | -0.074054 | -0.051439 | -0.17503 | -0.088456 | -0.23847 | 0.073604 | -0.020424 | 0.068032 | -0.088095 | -0.080315 | 121.5799 | 121.5626 | 121.439 | 61.6118 | -121.5617 | 121.3756 | 121.526 | 121.5338 | 61.6795 | -121.7025
379.7812 | 121.8658 | -61.4731 | 60.0586 | 1.4211e-13 | -0.02935 | 0.0018589 | 0.063859 | -0.0065361 | 0.053751 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063624 | 0.021938 | 0.059445 | -61.5371 | 0.019721 | -61.6 | 59.9924 | 59.9751 | 59.8515 | -61.5397 | -61.5231 | 0.073618 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.676 | -0.066615 | -0.066212 | -0.063981 | -0.12693 | -0.060319 | -0.083481 | -0.20707 | -0.2029 | -0.27509 | -0.049994 | -0.13944 | 0.063453 | -0.12472 | -0.12152 | 121.4655 | 121.4482 | 121.3246 | 61.4928 | -121.5983 | 121.2566 | 121.407 | 121.4102 | 61.5467 | -121.7346
381.4531 | 121.7651 | -61.5875 | 60.022 | 1.4211e-13 | -0.029564 | 0.0018589 | 0.063645 | -0.0065361 | 0.053751 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021938 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.9751 | 59.8515 | -61.5443 | -61.5185 | 0.082776 | -61.6217 | 59.7789 | 59.9339 | 59.9462 | -61.6714 | 0.043247 | -0.025013 | 0.055039 | -0.007915 | -0.051162 | -0.04686 | -0.17045 | -0.083876 | -0.24305 | 0.069026 | -0.03416 | 0.049716 | -0.088095 | -0.075737 | 121.5845 | 121.5626 | 121.439 | 61.6118 | -121.5662 | 121.3665 | 121.5214 | 121.5338 | 61.6703 | -121.6934
383.2031 | 121.7468 | -61.5646 | 60.022 | 1.4211e-13 | -0.02935 | 0.0014317 | 0.063432 | -0.0065361 | 0.054392 | 0.0053413 | -0.0018757 | -0.00084406 | 0.063838 | 0.021297 | 0.059017 | -61.5371 | 0.028878 | -61.6 | 59.9878 | 59.9705 | 59.8469 | -61.5397 | -61.5139 | 0.082776 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.676 | 0.024938 | -0.03417 | 0.027572 | -0.035381 | -0.060319 | -0.051439 | -0.17503 | -0.11134 | -0.23847 | 0.050717 | -0.04789 | 0.063453 | -0.088095 | -0.084894 | 121.5524 | 121.5352 | 121.4116 | 61.5935 | -121.5617 | 121.3481 | 121.4985 | 121.5017 | 61.6474 | -121.698
384.9531 | 121.7606 | -61.5601 | 60.054 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063218 | -0.0065361 | 0.053751 | 0.0053413 | -0.0016621 | -0.0014849 | 0.063411 | 0.021724 | 0.058804 | -61.5371 | 0.033457 | -61.6 | 59.9878 | 59.9705 | 59.8515 | -61.5351 | -61.5139 | 0.078197 | -61.6217 | 59.7881 | 59.9385 | 59.9371 | -61.6714 | 0.02494 | -0.066213 | 0.022995 | -0.039958 | -0.064898 | -0.083482 | -0.20249 | -0.11134 | -0.26593 | 0.04614 | -0.061625 | 0.049716 | -0.11556 | -0.11694 | 121.5479 | 121.5306 | 121.4116 | 61.5935 | -121.5891 | 121.3481 | 121.4985 | 121.4971 | 61.6383 | -121.7254
386.6406 | 121.7606 | -61.5097 | 60.1135 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063645 | -0.0063223 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.021724 | 0.059017 | -61.5371 | 0.019721 | -61.5954 | 59.9878 | 59.9705 | 59.8469 | -61.5443 | -61.5185 | 0.082776 | -61.6263 | 59.7835 | 59.9385 | 59.9371 | -61.6714 | -0.034572 | -0.12572 | -0.027359 | -0.085734 | -0.051162 | -0.14299 | -0.26658 | -0.1617 | -0.33002 | -0.008793 | -0.11656 | 0.045137 | -0.17507 | -0.17645 | 121.4975 | 121.4802 | 121.3566 | 61.5294 | -121.6578 | 121.2932 | 121.4482 | 121.4468 | 61.5925 | -121.7849
388.3438 | 121.7514 | -61.5921 | 60.0266 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063432 | -0.0067497 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021724 | 0.059231 | -61.5325 | 0.028878 | -61.5954 | 59.9832 | 59.9797 | 59.8469 | -61.5305 | -61.5139 | 0.082776 | -61.6079 | 59.7789 | 59.9385 | 59.9417 | -61.6806 | 0.061562 | -0.043325 | 0.059617 | -0.003337 | -0.064899 | -0.046858 | -0.17961 | -0.088456 | -0.24762 | 0.078183 | -0.015846 | 0.07261 | -0.088094 | -0.084892 | 121.5753 | 121.5718 | 121.439 | 61.621 | -121.5571 | 121.371 | 121.5306 | 121.5338 | 61.6749 | -121.7071
390.0938 | 121.8567 | -61.5417 | 60.0403 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063859 | -0.0067497 | 0.053751 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.021938 | 0.059231 | -61.5371 | 0.0243 | -61.6 | 59.997 | 59.9751 | 59.8469 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.9339 | 59.9371 | -61.6851 | 0.00205 | -0.043323 | 0.004684 | -0.058269 | -0.060319 | -0.06517 | -0.19334 | -0.14339 | -0.25678 | 0.027829 | -0.079936 | 0.063453 | -0.10641 | -0.1032 | 121.5387 | 121.5169 | 121.3887 | 61.566 | -121.58 | 121.3253 | 121.4756 | 121.4788 | 61.6245 | -121.7254
391.8438 | 121.7789 | -61.5417 | 60.022 | 1.4211e-13 | -0.029564 | 0.0014317 | 0.063432 | -0.0067497 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.021724 | 0.059017 | -61.5416 | 0.028878 | -61.5954 | 59.9832 | 59.9705 | 59.8515 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7835 | 59.9339 | 59.9417 | -61.6806 | -0.002529 | -0.038748 | 0.000106 | -0.053691 | -0.051162 | -0.051439 | -0.17045 | -0.13881 | -0.23847 | 0.027829 | -0.075357 | 0.063453 | -0.088095 | -0.080315 | 121.525 | 121.5123 | 121.3933 | 61.5706 | -121.5662 | 121.3253 | 121.4756 | 121.4834 | 61.6199 | -121.7025
393.6094 | 121.756 | -61.5372 | 60.1227 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063624 | 0.021511 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9878 | 59.966 | 59.8469 | -61.5397 | -61.5185 | 0.078197 | -61.6125 | 59.7881 | 59.9339 | 59.9371 | -61.676 | -0.002528 | -0.13488 | 0.000106 | -0.062847 | -0.060319 | -0.15673 | -0.27574 | -0.13881 | -0.3346 | 0.018672 | -0.075356 | 0.063453 | -0.1888 | -0.1856 | 121.525 | 121.5031 | 121.3841 | 61.5569 | -121.6624 | 121.3253 | 121.471 | 121.4742 | 61.6154 | -121.7987
395.3594 | 121.7606 | -61.5784 | 60.0403 | 1.4211e-13 | -0.029777 | 0.0018589 | 0.063859 | -0.0067497 | 0.054179 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063838 | 0.022152 | 0.058804 | -61.5279 | 0.019721 | -61.6 | 59.9832 | 59.9705 | 59.8515 | -61.5443 | -61.5231 | 0.087354 | -61.6079 | 59.7789 | 59.9339 | 59.9371 | -61.6806 | 0.034092 | -0.057058 | 0.050462 | -0.021648 | -0.05574 | -0.069749 | -0.18876 | -0.10219 | -0.26136 | 0.055292 | -0.029579 | 0.07261 | -0.10641 | -0.1032 | 121.5616 | 121.5489 | 121.4299 | 61.5981 | -121.5846 | 121.3573 | 121.5122 | 121.5154 | 61.6657 | -121.7208
397.0625 | 121.7972 | -61.5692 | 60.0677 | 1.4211e-13 | -0.02935 | 0.0016453 | 0.063432 | -0.0063223 | 0.053965 | -0.0022892 | -0.0020893 | -0.0010577 | 0.063838 | 0.022152 | 0.059017 | -61.5325 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8515 | -61.5397 | -61.5139 | 0.087354 | -61.6217 | 59.7881 | 59.943 | 59.9462 | -61.6806 | 0.029516 | -0.079946 | 0.036729 | -0.030803 | -0.060319 | -0.097215 | -0.21623 | -0.11134 | -0.27966 | 0.055295 | -0.05247 | 0.058874 | -0.12471 | -0.12151 | 121.557 | 121.5397 | 121.4207 | 61.5889 | -121.6074 | 121.3573 | 121.5122 | 121.5155 | 61.6566 | -121.7483
398.8281 | 121.8658 | -61.5555 | 59.9854 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063645 | -0.0063223 | 0.054179 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063838 | 0.021724 | 0.058804 | -61.5371 | 0.028878 | -61.5909 | 59.9832 | 59.9751 | 59.8469 | -61.5397 | -61.5093 | 0.078197 | -61.6217 | 59.7881 | 59.943 | 59.9371 | -61.6806 | 0.015783 | -0.002127 | 0.018417 | -0.03538 | -0.051163 | -0.010239 | -0.13841 | -0.12508 | -0.19727 | 0.04614 | -0.066203 | 0.058874 | -0.042317 | -0.048273 | 121.5387 | 121.5306 | 121.4024 | 61.5844 | -121.525 | 121.3436 | 121.4985 | 121.4926 | 61.6337 | -121.6659
400.5156 | 121.788 | -61.5967 | 60.0082 | 1.4211e-13 | -0.029777 | 0.0018589 | 0.063859 | -0.0069633 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063411 | 0.021724 | 0.059017 | -61.5416 | 0.0243 | -61.6 | 59.9878 | 59.9705 | 59.8561 | -61.5351 | -61.5185 | 0.087354 | -61.6079 | 59.7743 | 59.9385 | 59.9371 | -61.6806 | 0.061561 | -0.020437 | 0.055038 | -0.003337 | -0.064898 | -0.037706 | -0.15214 | -0.083878 | -0.23389 | 0.078182 | -0.011268 | 0.07261 | -0.069784 | -0.071161 | 121.5845 | 121.5672 | 121.4528 | 61.621 | -121.5434 | 121.371 | 121.5351 | 121.5338 | 61.684 | -121.6888
402.2969 | 121.8842 | -61.5692 | 59.9762 | 1.4211e-13 | -0.029564 | 0.0018589 | 0.063645 | -0.0065361 | 0.054392 | 0.012972 | -0.0014485 | -0.0010577 | 0.063838 | 0.021511 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.9832 | 59.9751 | 59.8515 | -61.5397 | -61.5185 | 0.087354 | -61.6171 | 59.7789 | 59.9476 | 59.9371 | -61.6714 | 0.029516 | 0.007029 | 0.03215 | -0.026225 | -0.055741 | -0.001083 | -0.12468 | -0.10219 | -0.19727 | 0.050716 | -0.047891 | 0.054295 | -0.028583 | -0.039117 | 121.5524 | 121.5443 | 121.4207 | 61.5981 | -121.5159 | 121.3481 | 121.5168 | 121.5063 | 61.6566 | -121.6476
404.0625 | 121.8338 | -61.5509 | 60.0266 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063432 | -0.0065361 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.021938 | 0.059231 | -61.5371 | 0.0243 | -61.5954 | 59.9878 | 59.9797 | 59.8469 | -61.5443 | -61.5093 | 0.082776 | -61.6079 | 59.7881 | 59.943 | 59.9325 | -61.676 | 0.006626 | -0.038747 | 0.013839 | -0.044536 | -0.051162 | -0.046858 | -0.17961 | -0.12508 | -0.23846 | 0.041562 | -0.057045 | 0.068031 | -0.083515 | -0.09405 | 121.5387 | 121.5306 | 121.3978 | 61.5752 | -121.5708 | 121.339 | 121.4939 | 121.4834 | 61.6337 | -121.7025
405.75 | 121.7651 | -61.6104 | 60.0266 | 1.4211e-13 | -0.029777 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.064052 | 0.022152 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9878 | 59.9751 | 59.8469 | -61.5443 | -61.5185 | 0.087354 | -61.6079 | 59.7835 | 59.9385 | 59.9325 | -61.6806 | 0.066136 | -0.038747 | 0.073349 | 0.010396 | -0.05574 | -0.051437 | -0.17961 | -0.070145 | -0.24304 | 0.091915 | 0.002465 | 0.07261 | -0.088094 | -0.09405 | 121.5982 | 121.5855 | 121.4574 | 61.6301 | -121.5708 | 121.3939 | 121.5489 | 121.5429 | 61.6978 | -121.7071
407.4375 | 121.8796 | -61.4822 | 60.0677 | 1.4211e-13 | -0.029777 | 0.0018589 | 0.063432 | -0.0065361 | 0.053751 | -0.0099192 | -0.0014485 | -0.0014849 | 0.063624 | 0.022152 | 0.058804 | -61.5371 | 0.0243 | -61.6046 | 59.9832 | 59.9705 | 59.8424 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7835 | 59.9476 | 59.9417 | -61.6806 | -0.062038 | -0.084524 | -0.054825 | -0.12236 | -0.060319 | -0.097215 | -0.22538 | -0.19832 | -0.28424 | -0.03168 | -0.13487 | 0.063453 | -0.12014 | -0.12609 | 121.4655 | 121.4528 | 121.3246 | 61.5065 | -121.612 | 121.2657 | 121.4299 | 121.4239 | 61.5604 | -121.7483
409.2031 | 121.8842 | -61.5601 | 59.9579 | 1.4211e-13 | -0.029991 | 0.0020727 | 0.063432 | -0.0065361 | 0.053965 | 0.0053413 | -0.0018757 | -0.0014849 | 0.063624 | 0.021724 | 0.059017 | -61.5325 | 0.033457 | -61.6 | 59.9878 | 59.9751 | 59.8515 | -61.5351 | -61.5093 | 0.087354 | -61.6217 | 59.7835 | 59.943 | 59.9417 | -61.6806 | 0.02494 | 0.029917 | 0.027574 | -0.039958 | -0.064898 | 0.017227 | -0.10637 | -0.1205 | -0.17438 | 0.050718 | -0.061625 | 0.058874 | -0.014851 | -0.016228 | 121.5479 | 121.5352 | 121.4116 | 61.5935 | -121.493 | 121.3436 | 121.5031 | 121.5017 | 61.6474 | -121.6384
410.8906 | 121.7972 | -61.5875 | 59.9945 | 1.4211e-13 | -0.029564 | 0.0018589 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0012349 | -0.0010577 | 0.063411 | 0.021938 | 0.059017 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.966 | 59.8515 | -61.5443 | -61.5093 | 0.087354 | -61.6171 | 59.7743 | 59.943 | 59.9417 | -61.6851 | 0.043247 | 0.002453 | 0.055039 | -0.007915 | -0.051162 | -0.028552 | -0.14299 | -0.097613 | -0.22016 | 0.078183 | -0.029581 | 0.068032 | -0.051472 | -0.052849 | 121.5845 | 121.5535 | 121.439 | 61.6118 | -121.5388 | 121.3619 | 121.5306 | 121.5292 | 61.6749 | -121.6796
412.6406 | 121.7743 | -61.5967 | 60.0311 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.064073 | -0.0067497 | 0.053965 | -0.0099192 | -0.0016621 | -0.00084406 | 0.063624 | 0.022152 | 0.059231 | -61.5325 | 0.028878 | -61.6046 | 59.997 | 59.9705 | 59.8469 | -61.5351 | -61.5139 | 0.082776 | -61.6125 | 59.7789 | 59.943 | 59.9371 | -61.6806 | 0.061561 | -0.034168 | 0.064195 | -0.007916 | -0.069477 | -0.060594 | -0.18418 | -0.083878 | -0.2522 | 0.082761 | -0.015846 | 0.068032 | -0.088093 | -0.094049 | 121.5936 | 121.5672 | 121.4436 | 61.6256 | -121.5662 | 121.3756 | 121.5397 | 121.5338 | 61.6795 | -121.7117
414.3906 | 121.8796 | -61.5555 | 59.9854 | 1.4211e-13 | -0.029564 | 0.0020727 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063838 | 0.021511 | 0.059017 | -61.5371 | 0.019721 | -61.5909 | 59.9924 | 59.966 | 59.8469 | -61.5351 | -61.5139 | 0.087354 | -61.6125 | 59.7835 | 59.9385 | 59.9417 | -61.6851 | 0.020362 | 0.00703 | 0.018417 | -0.03538 | -0.055742 | -0.019397 | -0.13841 | -0.12966 | -0.20184 | 0.041562 | -0.057045 | 0.072611 | -0.046896 | -0.043694 | 121.5479 | 121.5214 | 121.4024 | 61.5752 | -121.5205 | 121.339 | 121.4939 | 121.4971 | 61.6428 | -121.6705
416.1406 | 121.875 | -61.5692 | 59.9899 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0020893 | -0.0010577 | 0.063624 | 0.021938 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.9832 | 59.9751 | 59.8561 | -61.5351 | -61.5093 | 0.087354 | -61.6079 | 59.7835 | 59.9476 | 59.9417 | -61.6806 | 0.034095 | -0.006704 | 0.036729 | -0.026225 | -0.06032 | -0.014816 | -0.13383 | -0.11134 | -0.20642 | 0.059873 | -0.038734 | 0.07261 | -0.042316 | -0.048271 | 121.5524 | 121.5443 | 121.4253 | 61.5935 | -121.525 | 121.3527 | 121.5168 | 121.5109 | 61.6566 | -121.6705
417.8906 | 121.788 | -61.5967 | 60.0128 | 1.4211e-13 | -0.029564 | 0.0020727 | 0.063645 | -0.0065361 | 0.053751 | -0.0099192 | -0.0016621 | -0.0010577 | 0.064265 | 0.022152 | 0.059445 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.9705 | 59.8561 | -61.5489 | -61.5139 | 0.087354 | -61.6171 | 59.7835 | 59.943 | 59.9417 | -61.6851 | 0.047824 | -0.015857 | 0.064195 | 0.001241 | -0.046583 | -0.042283 | -0.15672 | -0.088457 | -0.22931 | 0.082761 | -0.020425 | 0.068032 | -0.069782 | -0.071159 | 121.5936 | 121.5672 | 121.4528 | 61.621 | -121.5617 | 121.3802 | 121.5397 | 121.5383 | 61.684 | -121.698
419.5781 | 121.875 | -61.5555 | 59.967 | 1.4211e-13 | -0.029777 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.021938 | 0.059445 | -61.5279 | 0.028878 | -61.6 | 59.9878 | 59.9797 | 59.8515 | -61.5397 | -61.5185 | 0.082776 | -61.6125 | 59.7835 | 59.9339 | 59.9417 | -61.6806 | 0.015783 | 0.020762 | 0.027574 | -0.044536 | -0.060319 | 0.012651 | -0.11552 | -0.12508 | -0.18353 | 0.036983 | -0.057045 | 0.068032 | -0.033163 | -0.025383 | 121.5433 | 121.5352 | 121.407 | 61.5844 | -121.5067 | 121.339 | 121.4894 | 121.4971 | 61.6383 | -121.6476
421.3125 | 121.8796 | -61.5051 | 60.0403 | 1.4211e-13 | -0.029777 | 0.0018589 | 0.063859 | -0.0065361 | 0.053751 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.021724 | 0.059017 | -61.5416 | 0.028878 | -61.6046 | 59.9878 | 59.9751 | 59.8561 | -61.5351 | -61.5093 | 0.078197 | -61.6171 | 59.7789 | 59.9476 | 59.9325 | -61.6806 | -0.029992 | -0.05248 | -0.036515 | -0.099469 | -0.069477 | -0.06517 | -0.18418 | -0.17543 | -0.26136 | -0.004214 | -0.11198 | 0.063453 | -0.09267 | -0.10778 | 121.4929 | 121.4802 | 121.3612 | 61.534 | -121.5754 | 121.2841 | 121.4527 | 121.4376 | 61.5833 | -121.7208
423.0625 | 121.8063 | -61.528 | 60.0677 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063645 | -0.0063223 | 0.054179 | -0.0022892 | -0.0016621 | -0.0010577 | 0.064052 | 0.021938 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.9878 | 59.9705 | 59.8515 | -61.5397 | -61.5093 | 0.082776 | -61.6125 | 59.7881 | 59.9385 | 59.9371 | -61.676 | -0.011683 | -0.079946 | -0.009049 | -0.067424 | -0.055741 | -0.097215 | -0.21623 | -0.14796 | -0.27966 | 0.018674 | -0.084511 | 0.063453 | -0.12929 | -0.13067 | 121.5158 | 121.4985 | 121.3795 | 61.5569 | -121.6074 | 121.3161 | 121.4665 | 121.4651 | 61.6108 | -121.7437
424.75 | 121.7468 | -61.5189 | 60.1227 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063218 | -0.0065361 | 0.053965 | 0.0053413 | -0.0020893 | -0.0010577 | 0.063411 | 0.021724 | 0.058804 | -61.5325 | 0.015142 | -61.6046 | 59.9786 | 59.966 | 59.8469 | -61.5305 | -61.5185 | 0.078197 | -61.6217 | 59.7835 | 59.9339 | 59.9325 | -61.676 | -0.01168 | -0.14404 | -0.013625 | -0.085736 | -0.074056 | -0.15673 | -0.27574 | -0.15712 | -0.33917 | 0.000362 | -0.10282 | 0.054295 | -0.1888 | -0.19018 | 121.4975 | 121.4848 | 121.3658 | 61.534 | -121.6532 | 121.3024 | 121.4527 | 121.4514 | 61.5971 | -121.7987
426.5 | 121.8063 | -61.6013 | 59.9899 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063645 | -0.0067497 | 0.054606 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063838 | 0.021938 | 0.059231 | -61.5371 | 0.0243 | -61.6 | 59.997 | 59.9705 | 59.8469 | -61.5397 | -61.5048 | 0.082776 | -61.6171 | 59.7881 | 59.9385 | 59.9417 | -61.676 | 0.061559 | 0.007031 | 0.064193 | 0.00124 | -0.060319 | -0.019395 | -0.14299 | -0.074722 | -0.20184 | 0.096495 | -0.015848 | 0.058874 | -0.051473 | -0.048271 | 121.5982 | 121.5718 | 121.4482 | 61.6256 | -121.5296 | 121.3893 | 121.5397 | 121.5429 | 61.684 | -121.6659
428.2656 | 121.8704 | -61.5601 | 59.9762 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063218 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.0010577 | 0.064052 | 0.022152 | 0.059017 | -61.5371 | 0.0243 | -61.6 | 59.9878 | 59.9705 | 59.8561 | -61.5351 | -61.5048 | 0.082776 | -61.6217 | 59.7743 | 59.9339 | 59.9417 | -61.6851 | 0.02494 | 0.011607 | 0.022995 | -0.039958 | -0.064898 | -0.005662 | -0.1201 | -0.12508 | -0.20185 | 0.055297 | -0.061625 | 0.063453 | -0.042318 | -0.034538 | 121.5479 | 121.5306 | 121.4162 | 61.5844 | -121.5113 | 121.3344 | 121.4939 | 121.5017 | 61.6428 | -121.6613
430.0156 | 121.8018 | -61.5372 | 60.0861 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063218 | -0.0069633 | 0.053751 | 0.0053413 | -0.0014485 | -0.0010577 | 0.063838 | 0.022365 | 0.059231 | -61.5325 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8515 | -61.5351 | -61.5139 | 0.082776 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.6806 | 0.002051 | -0.098257 | 0.004685 | -0.062847 | -0.064898 | -0.11553 | -0.23454 | -0.14339 | -0.30255 | 0.023251 | -0.075356 | 0.068032 | -0.15218 | -0.14898 | 121.525 | 121.5077 | 121.3887 | 61.5569 | -121.6212 | 121.3207 | 121.471 | 121.4742 | 61.6199 | -121.7666
431.7031 | 121.8567 | -61.5372 | 60.0311 | 1.4211e-13 | -0.029777 | 0.0020727 | 0.063218 | -0.0065361 | 0.053965 | -0.0099192 | -0.0014485 | -0.0016987 | 0.063838 | 0.021724 | 0.059231 | -61.5416 | 0.028878 | -61.6092 | 59.9878 | 59.9751 | 59.8469 | -61.5397 | -61.5185 | 0.087354 | -61.6171 | 59.7789 | 59.9385 | 59.9371 | -61.676 | -0.002528 | -0.043325 | -0.004472 | -0.072004 | -0.069476 | -0.056015 | -0.18418 | -0.13881 | -0.2522 | 0.018672 | -0.079935 | 0.058874 | -0.092672 | -0.094049 | 121.525 | 121.5123 | 121.3841 | 61.566 | -121.5708 | 121.3161 | 121.4756 | 121.4742 | 61.6245 | -121.7071
433.4531 | 121.8109 | -61.5326 | 60.0723 | 1.4211e-13 | -0.029777 | 0.0014317 | 0.063004 | -0.0069633 | 0.053965 | -0.01755 | -0.0016621 | -0.0012713 | 0.063624 | 0.022152 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9832 | 59.9751 | 59.8515 | -61.5305 | -61.5139 | 0.087354 | -61.6125 | 59.7835 | 59.943 | 59.9417 | -61.6851 | 0.002053 | -0.089102 | -0.004471 | -0.067424 | -0.069477 | -0.097214 | -0.22081 | -0.15254 | -0.28882 | 0.018674 | -0.079933 | 0.072611 | -0.12929 | -0.13067 | 121.5158 | 121.5077 | 121.3841 | 61.5523 | -121.6029 | 121.3161 | 121.4756 | 121.4743 | 61.6199 | -121.7575
435.2031 | 121.8613 | -61.5051 | 60.0174 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063432 | -0.0065361 | 0.053751 | -0.0099192 | -0.0016621 | -0.00084406 | 0.063838 | 0.022365 | 0.059017 | -61.5371 | 0.0243 | -61.6 | 59.9878 | 59.9751 | 59.8515 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.6806 | -0.03915 | -0.029592 | -0.031937 | -0.09489 | -0.05574 | -0.042282 | -0.16587 | -0.17543 | -0.23389 | -0.008792 | -0.11198 | 0.063453 | -0.07436 | -0.080316 | 121.4929 | 121.4802 | 121.3566 | 61.5294 | -121.5617 | 121.2886 | 121.4482 | 121.4422 | 61.5833 | -121.698
436.8906 | 121.843 | -61.5372 | 60.0174 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063432 | -0.0067497 | 0.053965 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063624 | 0.022152 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9832 | 59.9705 | 59.8561 | -61.5351 | -61.5093 | 0.082776 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.6851 | 0.002051 | -0.03417 | 0.000106 | -0.062847 | -0.064898 | -0.046861 | -0.1613 | -0.14797 | -0.23389 | 0.027829 | -0.079935 | 0.068032 | -0.07436 | -0.080316 | 121.5204 | 121.5077 | 121.3933 | 61.5569 | -121.5525 | 121.3207 | 121.4802 | 121.4742 | 61.6199 | -121.7025
438.6406 | 121.8246 | -61.5463 | 60.0174 | 1.4211e-13 | -0.029777 | 0.0016453 | 0.063218 | -0.0071769 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063624 | 0.021938 | 0.059017 | -61.5371 | 0.019721 | -61.5954 | 59.9878 | 59.9751 | 59.8515 | -61.5351 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.943 | 59.9325 | -61.6806 | 0.011207 | -0.029592 | 0.009262 | -0.049113 | -0.06032 | -0.042282 | -0.16587 | -0.13423 | -0.23389 | 0.032407 | -0.075358 | 0.058874 | -0.07436 | -0.084895 | 121.5341 | 121.5214 | 121.3978 | 61.566 | -121.5525 | 121.3298 | 121.4894 | 121.4788 | 61.6291 | -121.698
440.3906 | 121.756 | -61.5921 | 60.0082 | 1.4211e-13 | -0.029564 | 0.0018589 | 0.063432 | -0.0067497 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.021724 | 0.058804 | -61.5325 | 0.019721 | -61.5954 | 59.9878 | 59.9705 | 59.8561 | -61.5443 | -61.5048 | 0.087354 | -61.6171 | 59.7789 | 59.9385 | 59.9417 | -61.6806 | 0.047825 | -0.020437 | 0.059617 | -0.003337 | -0.051162 | -0.037706 | -0.15214 | -0.088456 | -0.22931 | 0.08734 | -0.025003 | 0.063453 | -0.069784 | -0.066582 | 121.5799 | 121.5626 | 121.4482 | 61.6118 | -121.5525 | 121.371 | 121.5306 | 121.5338 | 61.6795 | -121.6888
442.1406 | 121.875 | -61.5692 | 59.9487 | 1.4211e-13 | -0.029777 | 0.0018589 | 0.063432 | -0.0067497 | 0.053965 | -0.0099192 | -0.0014485 | -0.0014849 | 0.063624 | 0.021938 | 0.059231 | -61.5416 | 0.0243 | -61.6 | 59.9924 | 59.9705 | 59.8561 | -61.5351 | -61.5093 | 0.096512 | -61.6125 | 59.7835 | 59.9476 | 59.9371 | -61.6806 | 0.034095 | 0.043652 | 0.027572 | -0.030803 | -0.064898 | 0.021804 | -0.09263 | -0.11134 | -0.16522 | 0.059873 | -0.043312 | 0.068032 | -0.001117 | -0.011651 | 121.5616 | 121.5397 | 121.4253 | 61.5935 | -121.4838 | 121.3527 | 121.5168 | 121.5063 | 61.6657 | -121.6293
443.8281 | 121.8704 | -61.4822 | 60.0449 | 1.4211e-13 | -0.030205 | 0.0020727 | 0.063432 | -0.0065361 | 0.054179 | -0.01755 | -0.0016621 | -0.00084406 | 0.063624 | 0.022152 | 0.059231 | -61.5416 | 0.0243 | -61.5909 | 59.9878 | 59.9751 | 59.8469 | -61.5351 | -61.5093 | 0.082776 | -61.6171 | 59.7789 | 59.943 | 59.9279 | -61.6806 | -0.05288 | -0.057058 | -0.059403 | -0.10862 | -0.055742 | -0.069748 | -0.19792 | -0.19832 | -0.26593 | -0.027102 | -0.13487 | 0.063453 | -0.10183 | -0.11694 | 121.47 | 121.4574 | 121.3292 | 61.5065 | -121.58 | 121.2612 | 121.4253 | 121.4102 | 61.565 | -121.7254
445.5156 | 121.8567 | -61.496 | 60.0494 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063432 | -0.0067497 | 0.053751 | 0.0053413 | -0.0020893 | -0.0010577 | 0.064052 | 0.021938 | 0.059017 | -61.5325 | 0.019721 | -61.5954 | 59.9878 | 59.9705 | 59.8561 | -61.5305 | -61.5139 | 0.082776 | -61.6125 | 59.7789 | 59.9385 | 59.9325 | -61.6806 | -0.034568 | -0.061635 | -0.036513 | -0.099467 | -0.064899 | -0.078904 | -0.19334 | -0.18459 | -0.27051 | -0.017947 | -0.11655 | 0.068032 | -0.11098 | -0.11694 | 121.4838 | 121.4665 | 121.3521 | 61.5157 | -121.58 | 121.2749 | 121.4344 | 121.4285 | 61.5787 | -121.73
447.2656 | 121.788 | -61.5784 | 60.0311 | 1.4211e-13 | -0.029991 | 0.0020727 | 0.063645 | -0.0067497 | 0.053751 | -0.01755 | -0.0018757 | -0.0012713 | 0.063838 | 0.021938 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.9924 | 59.9797 | 59.8515 | -61.5397 | -61.5093 | 0.087354 | -61.6171 | 59.7743 | 59.9385 | 59.9417 | -61.6806 | 0.038671 | -0.038746 | 0.041305 | -0.01707 | -0.055741 | -0.051436 | -0.17961 | -0.10219 | -0.25678 | 0.069028 | -0.038736 | 0.063453 | -0.092672 | -0.08947 | 121.5708 | 121.5581 | 121.4299 | 61.6072 | -121.5708 | 121.3527 | 121.5168 | 121.52 | 61.6657 | -121.7117
449.0312 | 121.756 | -61.615 | 60.0082 | 1.4211e-13 | -0.029777 | 0.0016453 | 0.063218 | -0.0065361 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.022152 | 0.059445 | -61.5279 | 0.028878 | -61.5954 | 59.9878 | 59.9751 | 59.8515 | -61.5489 | -61.5139 | 0.078197 | -61.6125 | 59.7743 | 59.9385 | 59.9325 | -61.6806 | 0.066134 | -0.020437 | 0.087083 | 0.019551 | -0.046583 | -0.033127 | -0.15672 | -0.065568 | -0.23389 | 0.10107 | 0.002464 | 0.068032 | -0.069784 | -0.07574 | 121.6028 | 121.5901 | 121.4665 | 61.6439 | -121.5571 | 121.3893 | 121.5534 | 121.5475 | 61.6932 | -121.6888
450.7969 | 121.7422 | -61.5875 | 60.0357 | 1.4211e-13 | -0.029991 | 0.0014317 | 0.063432 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063624 | 0.021938 | 0.059017 | -61.5279 | 0.0243 | -61.5954 | 59.9832 | 59.9751 | 59.8561 | -61.5489 | -61.5048 | 0.082776 | -61.6171 | 59.7881 | 59.9339 | 59.9417 | -61.6851 | 0.038668 | -0.052481 | 0.059617 | -0.007915 | -0.046583 | -0.060593 | -0.17961 | -0.097613 | -0.24762 | 0.082762 | -0.029581 | 0.068032 | -0.10183 | -0.094048 | 121.5707 | 121.5626 | 121.4436 | 61.6118 | -121.5846 | 121.3756 | 121.5214 | 121.5292 | 61.6703 | -121.7208
452.4844 | 121.8063 | -61.5189 | 60.0723 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063645 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.00084406 | 0.063838 | 0.022152 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8515 | -61.5443 | -61.5139 | 0.091933 | -61.6171 | 59.7835 | 59.9339 | 59.9371 | -61.676 | -0.025417 | -0.084524 | -0.018204 | -0.081157 | -0.05574 | -0.10179 | -0.22081 | -0.15712 | -0.28882 | 0.004941 | -0.098245 | 0.058874 | -0.13845 | -0.13525 | 121.5067 | 121.4894 | 121.3704 | 61.5386 | -121.6166 | 121.3024 | 121.4527 | 121.4559 | 61.6108 | -121.7483
454.25 | 121.7514 | -61.5738 | 59.9991 | 1.4211e-13 | -0.030205 | 0.0018589 | 0.063432 | -0.0065361 | 0.053965 | -0.0022892 | -0.0014485 | -0.0014849 | 0.063838 | 0.022152 | 0.059017 | -61.5279 | 0.0243 | -61.5954 | 60.0015 | 59.9705 | 59.8607 | -61.5305 | -61.5139 | 0.087354 | -61.6171 | 59.7972 | 59.943 | 59.9371 | -61.6897 | 0.043252 | 0.002454 | 0.045885 | -0.021647 | -0.064899 | -0.02855 | -0.13841 | -0.11592 | -0.20184 | 0.059873 | -0.043313 | 0.07261 | -0.056049 | -0.062005 | 121.5753 | 121.5443 | 121.4345 | 61.5981 | -121.5296 | 121.371 | 121.5168 | 121.5109 | 61.6611 | -121.6888
455.9375 | 121.7239 | -61.5784 | 60.0311 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063645 | -0.0067497 | 0.054392 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063411 | 0.022152 | 0.058804 | -61.5371 | 0.0243 | -61.5954 | 59.9832 | 59.9751 | 59.8515 | -61.5443 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.6806 | 0.034092 | -0.047903 | 0.041305 | -0.01707 | -0.051162 | -0.056015 | -0.17961 | -0.10219 | -0.24762 | 0.06445 | -0.038736 | 0.063453 | -0.088093 | -0.094049 | 121.5616 | 121.5535 | 121.4299 | 61.6027 | -121.5754 | 121.3619 | 121.5214 | 121.5154 | 61.6611 | -121.7117
457.6875 | 121.8567 | -61.5417 | 59.9716 | 1.4211e-13 | -0.030205 | 0.0014317 | 0.063218 | -0.0067497 | 0.054179 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063838 | 0.022365 | 0.059017 | -61.5279 | 0.0243 | -61.6046 | 59.9924 | 59.9751 | 59.8515 | -61.5397 | -61.5093 | 0.082776 | -61.6217 | 59.7789 | 59.9385 | 59.9325 | -61.6806 | 0.00205 | 0.020763 | 0.013841 | -0.062848 | -0.064898 | 0.003494 | -0.1201 | -0.13881 | -0.19269 | 0.032407 | -0.079936 | 0.058874 | -0.033163 | -0.039119 | 121.5341 | 121.5169 | 121.3933 | 61.566 | -121.5113 | 121.3207 | 121.4802 | 121.4742 | 61.6245 | -121.6522
459.3906 | 121.8475 | -61.5417 | 59.967 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0018757 | -0.0014849 | 0.064052 | 0.022152 | 0.058804 | -61.5325 | 0.028878 | -61.6 | 59.997 | 59.9751 | 59.8561 | -61.5489 | -61.5139 | 0.087354 | -61.6171 | 59.7881 | 59.9476 | 59.9371 | -61.676 | -0.007108 | 0.029919 | 0.009263 | -0.058269 | -0.051161 | 0.008072 | -0.11094 | -0.13423 | -0.17896 | 0.027829 | -0.075357 | 0.058874 | -0.019428 | -0.029962 | 121.5387 | 121.5169 | 121.3978 | 61.5706 | -121.5159 | 121.3298 | 121.4894 | 121.4788 | 61.6291 | -121.643
461.1406 | 121.8933 | -61.5143 | 60.0311 | 1.4211e-13 | -0.029777 | 0.0014317 | 0.063645 | -0.0063223 | 0.053751 | -0.01755 | -0.0016621 | -0.0010577 | 0.063624 | 0.021724 | 0.059017 | -61.5325 | 0.038035 | -61.5954 | 59.9878 | 59.9751 | 59.8561 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7835 | 59.9385 | 59.9325 | -61.6851 | -0.025416 | -0.043325 | -0.018203 | -0.081157 | -0.055741 | -0.056015 | -0.17503 | -0.17085 | -0.24762 | 0.000363 | -0.1074 | 0.063453 | -0.092672 | -0.098628 | 121.5021 | 121.4894 | 121.3704 | 61.5523 | -121.5708 | 121.2978 | 121.4527 | 121.4468 | 61.5925 | -121.7163
462.9062 | 121.8796 | -61.5555 | 59.9762 | 1.4211e-13 | -0.029991 | 0.0012179 | 0.063645 | -0.0065361 | 0.054179 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063411 | 0.022152 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.997 | 59.9797 | 59.8561 | -61.5305 | -61.5139 | 0.078197 | -61.6171 | 59.7881 | 59.9385 | 59.9325 | -61.6806 | 0.024941 | 0.020764 | 0.018417 | -0.039958 | -0.064899 | 0.003496 | -0.1201 | -0.12508 | -0.18811 | 0.041562 | -0.061624 | 0.063453 | -0.03774 | -0.043696 | 121.5524 | 121.5352 | 121.4116 | 61.5844 | -121.5067 | 121.3436 | 121.4939 | 121.488 | 61.6337 | -121.6568
464.6719 | 121.756 | -61.5051 | 60.1135 | 1.4211e-13 | -0.030205 | 0.0018589 | 0.063645 | -0.0065361 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063624 | 0.022365 | 0.059017 | -61.5371 | 0.019721 | -61.6 | 59.9878 | 59.9705 | 59.8515 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.943 | 59.9462 | -61.6806 | -0.03915 | -0.12572 | -0.031937 | -0.09489 | -0.05574 | -0.14299 | -0.262 | -0.17543 | -0.3346 | -0.008792 | -0.11198 | 0.063453 | -0.17049 | -0.16729 | 121.4929 | 121.4757 | 121.3566 | 61.5248 | -121.6578 | 121.2841 | 121.4482 | 121.4514 | 61.5833 | -121.7941
466.4062 | 121.7926 | -61.5509 | 60.0357 | 1.4211e-13 | -0.029564 | 0.0016453 | 0.063645 | -0.0067497 | 0.053965 | 0.012972 | -0.0014485 | -0.0012713 | 0.063624 | 0.022152 | 0.059017 | -61.5325 | 0.028878 | -61.5954 | 59.997 | 59.9705 | 59.8469 | -61.5397 | -61.5093 | 0.078197 | -61.6125 | 59.7881 | 59.943 | 59.9371 | -61.676 | 0.011205 | -0.038746 | 0.018418 | -0.044536 | -0.055741 | -0.065172 | -0.18876 | -0.12508 | -0.24762 | 0.041562 | -0.061623 | 0.063453 | -0.092671 | -0.098627 | 121.5479 | 121.5214 | 121.3978 | 61.5798 | -121.5754 | 121.339 | 121.4939 | 121.488 | 61.6291 | -121.7117
468.0938 | 121.788 | -61.5189 | 60.0677 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063218 | -0.0069633 | 0.054392 | -0.0099192 | -0.0016621 | -0.00084406 | 0.063624 | 0.021938 | 0.059017 | -61.5279 | 0.028878 | -61.6 | 59.9924 | 59.9751 | 59.8515 | -61.5397 | -61.5093 | 0.078197 | -61.6125 | 59.7789 | 59.943 | 59.9417 | -61.6851 | -0.020838 | -0.075367 | -0.009047 | -0.081157 | -0.060319 | -0.092636 | -0.21623 | -0.16628 | -0.28882 | 0.009519 | -0.093666 | 0.072611 | -0.12471 | -0.12609 | 121.5112 | 121.494 | 121.3704 | 61.5477 | -121.6074 | 121.2978 | 121.4619 | 121.4605 | 61.5971 | -121.7529
469.8594 | 121.7514 | -61.528 | 60.0906 | 1.4211e-13 | -0.030205 | 0.0018589 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0016621 | -0.00063026 | 0.063624 | 0.022152 | 0.058804 | -61.5325 | 0.0243 | -61.6 | 59.9832 | 59.9751 | 59.8561 | -61.5397 | -61.5093 | 0.078197 | -61.6217 | 59.7789 | 59.9385 | 59.9325 | -61.6851 | -0.011683 | -0.10741 | -0.00447 | -0.072002 | -0.060319 | -0.11552 | -0.23454 | -0.15712 | -0.31171 | 0.018674 | -0.093669 | 0.063453 | -0.15218 | -0.15814 | 121.5112 | 121.5031 | 121.3841 | 61.5523 | -121.6303 | 121.3069 | 121.4665 | 121.4605 | 61.6062 | -121.7758
471.5469 | 121.8704 | -61.4639 | 60.0174 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063411 | 0.021938 | 0.059231 | -61.5416 | 0.0243 | -61.6 | 59.9924 | 59.9751 | 59.8469 | -61.5351 | -61.5139 | 0.078197 | -61.6217 | 59.7835 | 59.943 | 59.9371 | -61.6851 | -0.071191 | -0.025013 | -0.077714 | -0.13609 | -0.064898 | -0.042282 | -0.17045 | -0.22121 | -0.23389 | -0.049991 | -0.15776 | 0.063453 | -0.07436 | -0.080316 | 121.4563 | 121.439 | 121.3109 | 61.4882 | -121.5525 | 121.2474 | 121.407 | 121.401 | 61.5421 | -121.7025
473.3125 | 121.8384 | -61.5784 | 59.967 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063218 | -0.0067497 | 0.053965 | -0.01755 | -0.0018757 | -0.0010577 | 0.063624 | 0.022365 | 0.059658 | -61.5325 | 0.028878 | -61.5954 | 59.9924 | 59.9797 | 59.8561 | -61.5351 | -61.5093 | 0.078197 | -61.6171 | 59.7789 | 59.9385 | 59.9462 | -61.6897 | 0.04325 | 0.025341 | 0.045884 | -0.01707 | -0.06032 | 0.012651 | -0.11094 | -0.11135 | -0.18811 | 0.069028 | -0.038736 | 0.07261 | -0.028585 | -0.020805 | 121.5708 | 121.5581 | 121.4345 | 61.6072 | -121.5022 | 121.3573 | 121.5168 | 121.5246 | 61.6566 | -121.6568
475 | 121.8475 | -61.5372 | 60.0357 | 1.4211e-13 | -0.029991 | 0.0012179 | 0.063218 | -0.0067497 | 0.053965 | 0.0053413 | -0.0018757 | -0.0014849 | 0.063838 | 0.021938 | 0.058804 | -61.5462 | 0.019721 | -61.5954 | 59.9878 | 59.9797 | 59.8561 | -61.5397 | -61.5093 | 0.082776 | -61.6171 | 59.7835 | 59.9339 | 59.9371 | -61.6851 | -0.002528 | -0.047903 | -0.00905 | -0.058269 | -0.055741 | -0.056014 | -0.17961 | -0.14797 | -0.2522 | 0.027829 | -0.079935 | 0.068032 | -0.10183 | -0.098627 | 121.525 | 121.5169 | 121.3933 | 61.5569 | -121.5754 | 121.3207 | 121.471 | 121.4742 | 61.6199 | -121.7208
476.7344 | 121.8155 | -61.5234 | 60.0632 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063432 | -0.0065361 | 0.054179 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.021938 | 0.058804 | -61.5325 | 0.019721 | -61.5954 | 59.9924 | 59.9705 | 59.8607 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7789 | 59.9385 | 59.9371 | -61.6851 | -0.016261 | -0.070789 | -0.009048 | -0.072002 | -0.055741 | -0.092637 | -0.20249 | -0.1617 | -0.28424 | 0.009518 | -0.098247 | 0.063453 | -0.12471 | -0.12609 | 121.5158 | 121.494 | 121.3841 | 61.5432 | -121.6029 | 121.3024 | 121.4619 | 121.4605 | 61.6062 | -121.7483
478.4844 | 121.8521 | -61.5509 | 59.9808 | 1.4211e-13 | -0.030205 | 0.0018589 | 0.063218 | -0.0067497 | 0.054179 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.022152 | 0.059231 | -61.5325 | 0.0243 | -61.5954 | 59.9924 | 59.9797 | 59.8607 | -61.5443 | -61.5093 | 0.073618 | -61.6171 | 59.7789 | 59.9339 | 59.9417 | -61.6851 | 0.006626 | 0.011608 | 0.018418 | -0.044536 | -0.051162 | -0.001082 | -0.12009 | -0.13423 | -0.20185 | 0.041562 | -0.066202 | 0.068032 | -0.046896 | -0.039116 | 121.5433 | 121.5306 | 121.4116 | 61.5752 | -121.5251 | 121.3298 | 121.4848 | 121.4926 | 61.6245 | -121.6659
480.1875 | 121.7514 | -61.5189 | 60.0861 | 1.4211e-13 | -0.029991 | 0.0018589 | 0.063004 | -0.0065361 | 0.053965 | -0.0022892 | -0.0012349 | -0.0016987 | 0.063624 | 0.022152 | 0.058804 | -61.5416 | 0.0243 | -61.5954 | 59.9924 | 59.9705 | 59.8561 | -61.5489 | -61.5093 | 0.078197 | -61.6171 | 59.7789 | 59.9339 | 59.9417 | -61.6851 | -0.029996 | -0.093678 | -0.022782 | -0.076579 | -0.046583 | -0.11553 | -0.22996 | -0.16628 | -0.30713 | 0.009519 | -0.098245 | 0.068032 | -0.15218 | -0.1444 | 121.5112 | 121.4894 | 121.375 | 61.5432 | -121.6349 | 121.2978 | 121.4527 | 121.4605 | 61.5971 | -121.7712
481.9375 | 121.8475 | -61.5509 | 59.9808 | 1.4211e-13 | -0.030418 | 0.0012179 | 0.063432 | -0.0065361 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.021938 | 0.059231 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9797 | 59.8515 | -61.5397 | -61.5093 | 0.082776 | -61.6217 | 59.7881 | 59.9339 | 59.9417 | -61.6943 | 0.011205 | 0.007029 | 0.018418 | -0.044536 | -0.055741 | -0.001082 | -0.12925 | -0.14339 | -0.19269 | 0.041562 | -0.070781 | 0.07261 | -0.046896 | -0.039116 | 121.5387 | 121.5306 | 121.4024 | 61.5752 | -121.5205 | 121.339 | 121.4848 | 121.4926 | 61.6337 | -121.6751
483.6875 | 121.7834 | -61.5601 | 60.0357 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063432 | -0.0067497 | 0.054179 | -0.01755 | -0.0020893 | -0.0012713 | 0.063838 | 0.021938 | 0.058804 | -61.5371 | 0.0243 | -61.6 | 59.9924 | 59.966 | 59.8561 | -61.5443 | -61.5139 | 0.078197 | -61.6217 | 59.7927 | 59.9385 | 59.9462 | -61.6806 | 0.015782 | -0.043324 | 0.022995 | -0.039958 | -0.05574 | -0.069751 | -0.17961 | -0.1205 | -0.24304 | 0.04614 | -0.061625 | 0.058874 | -0.09725 | -0.08947 | 121.5524 | 121.526 | 121.4162 | 61.5844 | -121.58 | 121.3527 | 121.4985 | 121.5063 | 61.6383 | -121.7163
485.4375 | 121.7743 | -61.5555 | 60.0403 | 1.4211e-13 | -0.029777 | 0.0014317 | 0.063218 | -0.0065361 | 0.054392 | -0.01755 | -0.0016621 | -0.0014849 | 0.064052 | 0.022365 | 0.058804 | -61.5325 | 0.019721 | -61.5909 | 59.9878 | 59.966 | 59.8561 | -61.5443 | -61.5185 | 0.087354 | -61.6171 | 59.7789 | 59.9385 | 59.9462 | -61.6806 | 0.011204 | -0.05248 | 0.022996 | -0.03538 | -0.046584 | -0.074328 | -0.18418 | -0.12508 | -0.26136 | 0.036983 | -0.061624 | 0.063453 | -0.10183 | -0.094047 | 121.5433 | 121.5214 | 121.4116 | 61.5752 | -121.5846 | 121.3344 | 121.4939 | 121.5017 | 61.6428 | -121.7208
487.125 | 121.8063 | -61.5372 | 60.0403 | 1.4211e-13 | -0.029991 | 0.0014317 | 0.063645 | -0.0065361 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.022152 | 0.058804 | -61.5325 | 0.0243 | -61.5863 | 59.9924 | 59.9705 | 59.8515 | -61.5397 | -61.5139 | 0.082776 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.6851 | -0.002528 | -0.047901 | 0.004685 | -0.049113 | -0.046585 | -0.069749 | -0.18876 | -0.14797 | -0.25678 | 0.023251 | -0.075356 | 0.072611 | -0.10641 | -0.1032 | 121.5296 | 121.5077 | 121.3887 | 61.5615 | -121.58 | 121.3207 | 121.471 | 121.4742 | 61.6199 | -121.7254
488.875 | 121.7697 | -61.6104 | 59.9899 | 1.4211e-13 | -0.029991 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063838 | 0.022579 | 0.059017 | -61.5371 | 0.028878 | -61.5863 | 59.997 | 59.9751 | 59.8515 | -61.5489 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.943 | 59.9462 | -61.676 | 0.061557 | 0.007031 | 0.073349 | 0.02413 | -0.037427 | -0.014816 | -0.13841 | -0.065566 | -0.20642 | 0.096494 | -0.002113 | 0.063453 | -0.046894 | -0.043693 | 121.6074 | 121.5855 | 121.4619 | 61.6393 | -121.5388 | 121.3939 | 121.5534 | 121.5566 | 61.6886 | -121.6659
490.625 | 121.7377 | -61.5921 | 60.022 | 1.4211e-13 | -0.029777 | 0.0016453 | 0.063218 | -0.0067497 | 0.053751 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063624 | 0.022365 | 0.059231 | -61.5279 | 0.0243 | -61.5954 | 59.9924 | 59.9751 | 59.8561 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.9385 | 59.9371 | -61.676 | 0.052404 | -0.029591 | 0.064195 | -0.003337 | -0.055741 | -0.04686 | -0.16587 | -0.083877 | -0.24305 | 0.078183 | -0.025003 | 0.058874 | -0.083517 | -0.084894 | 121.5845 | 121.5672 | 121.4482 | 61.6164 | -121.5617 | 121.371 | 121.5306 | 121.5292 | 61.6703 | -121.698
492.3906 | 121.8246 | -61.5372 | 60.0082 | 1.4211e-13 | -0.029991 | 0.0018589 | 0.063432 | -0.0065361 | 0.053751 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.022152 | 0.058804 | -61.5371 | 0.0243 | -61.5954 | 59.9878 | 59.9797 | 59.8515 | -61.5443 | -61.5139 | 0.073618 | -61.6171 | 59.7789 | 59.9385 | 59.9371 | -61.676 | -0.007107 | -0.020437 | 0.000106 | -0.058269 | -0.051162 | -0.028548 | -0.15672 | -0.13881 | -0.22931 | 0.023251 | -0.079935 | 0.058874 | -0.069784 | -0.071161 | 121.525 | 121.5169 | 121.3887 | 61.5615 | -121.5525 | 121.3161 | 121.4756 | 121.4742 | 61.6108 | -121.6842
494.0781 | 121.8246 | -61.5417 | 60.0403 | 1.4211e-13 | -0.029991 | 0.0018589 | 0.063432 | -0.0067497 | 0.053965 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.022152 | 0.058804 | -61.5325 | 0.028878 | -61.5954 | 59.997 | 59.9705 | 59.8469 | -61.5443 | -61.5139 | 0.078197 | -61.6217 | 59.7881 | 59.9339 | 59.9417 | -61.6806 | -0.002529 | -0.043323 | 0.009263 | -0.053691 | -0.051162 | -0.069749 | -0.19334 | -0.13881 | -0.2522 | 0.027829 | -0.079936 | 0.058874 | -0.10641 | -0.098625 | 121.5387 | 121.5123 | 121.3887 | 61.5706 | -121.5846 | 121.3298 | 121.4756 | 121.4834 | 61.6199 | -121.7208
495.8281 | 121.8384 | -61.5509 | 60.0082 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063645 | -0.0065361 | 0.053965 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063838 | 0.022152 | 0.05859 | -61.5416 | 0.0243 | -61.5954 | 59.9878 | 59.9751 | 59.8607 | -61.5443 | -61.5093 | 0.087354 | -61.6171 | 59.7835 | 59.9476 | 59.9371 | -61.6806 | 0.006626 | -0.020437 | 0.009261 | -0.044536 | -0.051162 | -0.033127 | -0.14756 | -0.12965 | -0.22473 | 0.041562 | -0.066202 | 0.063453 | -0.060627 | -0.071161 | 121.5387 | 121.526 | 121.4116 | 61.5752 | -121.5525 | 121.3344 | 121.4985 | 121.488 | 61.6383 | -121.6888
497.5156 | 121.7377 | -61.5829 | 60.0357 | 1.4211e-13 | -0.029991 | 0.0014317 | 0.063432 | -0.0069633 | 0.053965 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063624 | 0.022152 | 0.058804 | -61.5325 | 0.028878 | -61.5909 | 59.9878 | 59.9705 | 59.8561 | -61.5443 | -61.5139 | 0.087354 | -61.6034 | 59.7789 | 59.9385 | 59.9417 | -61.6851 | 0.03867 | -0.047903 | 0.050462 | -0.007914 | -0.046584 | -0.065172 | -0.17961 | -0.10219 | -0.25678 | 0.069028 | -0.020422 | 0.081768 | -0.09725 | -0.094048 | 121.5708 | 121.5535 | 121.439 | 61.6118 | -121.58 | 121.3619 | 121.5214 | 121.5246 | 61.6703 | -121.7208
499.2656 | 121.7651 | -61.5189 | 60.1044 | 1.4211e-13 | -0.030205 | 0.0012179 | 0.063859 | -0.0067497 | 0.053965 | 0.0053413 | -0.0014485 | -0.0010577 | 0.063838 | 0.022152 | 0.059017 | -61.5325 | 0.028878 | -61.5954 | 59.9832 | 59.9751 | 59.8561 | -61.5443 | -61.5231 | 0.078197 | -61.6217 | 59.7835 | 59.9385 | 59.9279 | -61.6851 | -0.025417 | -0.12115 | -0.013625 | -0.076579 | -0.051162 | -0.12926 | -0.24827 | -0.16628 | -0.32086 | -0.004217 | -0.10282 | 0.063453 | -0.16591 | -0.17645 | 121.5021 | 121.494 | 121.375 | 61.5477 | -121.6486 | 121.3024 | 121.4573 | 121.4468 | 61.5971 | -121.7895
501.0156 | 121.756 | -61.6104 | 59.9991 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063432 | -0.0069633 | 0.053965 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.022365 | 0.058804 | -61.5371 | 0.0243 | -61.5909 | 59.997 | 59.9751 | 59.8607 | -61.5443 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.943 | 59.9508 | -61.6806 | 0.066136 | -0.002124 | 0.073349 | 0.019552 | -0.046584 | -0.023971 | -0.13841 | -0.070145 | -0.21558 | 0.096494 | -0.006692 | 0.063453 | -0.056049 | -0.048269 | 121.6074 | 121.5855 | 121.4711 | 61.6347 | -121.5434 | 121.3939 | 121.5534 | 121.5612 | 61.6932 | -121.6796
502.7656 | 121.8933 | -61.4914 | 60.0449 | 1.4211e-13 | -0.030205 | 0.0014317 | 0.063218 | -0.0067497 | 0.054179 | -0.0022892 | -0.0020893 | -0.0016987 | 0.063624 | 0.022152 | 0.058804 | -61.5325 | 0.028878 | -61.5954 | 59.9786 | 59.9843 | 59.8561 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7743 | 59.9339 | 59.9371 | -61.6851 | -0.048304 | -0.066215 | -0.041091 | -0.10404 | -0.055741 | -0.060591 | -0.18876 | -0.19374 | -0.27051 | -0.022525 | -0.12571 | 0.068032 | -0.11098 | -0.10778 | 121.47 | 121.4757 | 121.3475 | 61.5203 | -121.5846 | 121.2657 | 121.4253 | 121.4285 | 61.5696 | -121.73
504.4531 | 121.7789 | -61.5326 | 60.0861 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063432 | -0.0069633 | 0.053965 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.021938 | 0.059231 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9751 | 59.8607 | -61.5443 | -61.5185 | 0.087354 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.6851 | -0.011684 | -0.098257 | -0.009049 | -0.067424 | -0.05574 | -0.11095 | -0.22538 | -0.15254 | -0.30255 | 0.014095 | -0.079933 | 0.072611 | -0.15218 | -0.14898 | 121.5204 | 121.5077 | 121.3933 | 61.5615 | -121.6303 | 121.3161 | 121.4665 | 121.4697 | 61.6199 | -121.7712
506.1875 | 121.7926 | -61.528 | 60.0494 | 1.4211e-13 | -0.030418 | 0.0018589 | 0.063645 | -0.0069633 | 0.053751 | -0.01755 | -0.0016621 | -0.0012713 | 0.063411 | 0.022365 | 0.059017 | -61.5325 | 0.028878 | -61.5909 | 59.9878 | 59.9751 | 59.8561 | -61.5489 | -61.5231 | 0.082776 | -61.6171 | 59.7881 | 59.943 | 59.9417 | -61.6806 | -0.020841 | -0.061635 | -0.00447 | -0.062846 | -0.042005 | -0.074325 | -0.19334 | -0.15254 | -0.26135 | 0.004938 | -0.08909 | 0.063453 | -0.1064 | -0.10778 | 121.5158 | 121.5031 | 121.3841 | 61.5569 | -121.5983 | 121.3161 | 121.4711 | 121.4697 | 61.6108 | -121.73
507.9375 | 121.7926 | -61.5829 | 60.0174 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063432 | -0.0069633 | 0.053965 | -0.0022892 | -0.0018757 | -0.00084406 | 0.063624 | 0.021724 | 0.059445 | -61.5371 | 0.0243 | -61.5909 | 59.9924 | 59.9797 | 59.8561 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7881 | 59.943 | 59.9371 | -61.6897 | 0.043249 | -0.025013 | 0.045883 | -0.007914 | -0.051163 | -0.037703 | -0.1613 | -0.10677 | -0.22931 | 0.069028 | -0.034158 | 0.07261 | -0.07436 | -0.080316 | 121.5753 | 121.5626 | 121.439 | 61.6072 | -121.5571 | 121.371 | 121.526 | 121.52 | 61.6611 | -121.7071
509.6406 | 121.7331 | -61.5921 | 60.0311 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063432 | -0.0071769 | 0.053751 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064052 | 0.022579 | 0.059017 | -61.5371 | 0.033457 | -61.5954 | 59.9924 | 59.9705 | 59.8607 | -61.5443 | -61.5139 | 0.078197 | -61.6034 | 59.7835 | 59.9476 | 59.9417 | -61.6851 | 0.047825 | -0.038746 | 0.055038 | -0.003337 | -0.051162 | -0.060594 | -0.17045 | -0.093035 | -0.24762 | 0.078183 | -0.011267 | 0.081768 | -0.083515 | -0.08947 | 121.5845 | 121.5626 | 121.4528 | 61.6256 | -121.5754 | 121.3756 | 121.5397 | 121.5338 | 61.6703 | -121.7163
511.3906 | 121.875 | -61.5646 | 59.9579 | 1.4211e-13 | -0.030418 | 0.0014317 | 0.063218 | -0.0067497 | 0.053751 | 0.0053413 | -0.0018757 | -0.0012713 | 0.063624 | 0.022365 | 0.059231 | -61.5325 | 0.028878 | -61.5909 | 59.9878 | 59.9751 | 59.8607 | -61.5397 | -61.5185 | 0.082776 | -61.6171 | 59.7789 | 59.9385 | 59.9462 | -61.6897 | 0.024938 | 0.029917 | 0.032151 | -0.026225 | -0.051163 | 0.017227 | -0.097207 | -0.12508 | -0.17896 | 0.046138 | -0.052469 | 0.07261 | -0.01943 | -0.01165 | 121.5524 | 121.5397 | 121.4253 | 61.5935 | -121.4976 | 121.3436 | 121.5031 | 121.5109 | 61.6474 | -121.6476
513.1406 | 121.8704 | -61.4914 | 60.0586 | 1.4211e-13 | -0.030205 | 0.0018589 | 0.063218 | -0.0065361 | 0.053965 | -0.01755 | -0.0016621 | -0.0010577 | 0.063838 | 0.022152 | 0.059017 | -61.5371 | 0.028878 | -61.5909 | 59.9924 | 59.9705 | 59.8561 | -61.5489 | -61.5185 | 0.078197 | -61.6263 | 59.7835 | 59.943 | 59.9371 | -61.6897 | -0.057462 | -0.066212 | -0.04567 | -0.099467 | -0.042005 | -0.08806 | -0.20249 | -0.19832 | -0.27509 | -0.027104 | -0.13487 | 0.063452 | -0.11556 | -0.12152 | 121.4838 | 121.4619 | 121.3475 | 61.5203 | -121.6075 | 121.2749 | 121.4344 | 121.4285 | 61.5696 | -121.7483
514.8281 | 121.7606 | -61.5509 | 60.0403 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063218 | -0.0067497 | 0.053965 | 0.0053413 | -0.0018757 | -0.0010577 | 0.063838 | 0.022365 | 0.058804 | -61.5416 | 0.028878 | -61.5954 | 59.9878 | 59.9705 | 59.8607 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7881 | 59.9339 | 59.9417 | -61.6851 | 0.011205 | -0.05248 | 0.009261 | -0.044536 | -0.055741 | -0.069749 | -0.1796 | -0.13423 | -0.2522 | 0.036984 | -0.066202 | 0.068032 | -0.10641 | -0.098625 | 121.5387 | 121.5214 | 121.4116 | 61.5798 | -121.58 | 121.339 | 121.4848 | 121.4926 | 61.6337 | -121.7254
516.5781 | 121.875 | -61.5601 | 59.9533 | 1.4211e-13 | -0.029991 | 0.0016453 | 0.063218 | -0.0067497 | 0.053538 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.022365 | 0.059017 | -61.5371 | 0.028878 | -61.5954 | 60.0015 | 59.9797 | 59.8561 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7789 | 59.9385 | 59.9371 | -61.6806 | 0.020361 | 0.04823 | 0.022995 | -0.03538 | -0.055741 | 0.026384 | -0.097208 | -0.1205 | -0.17438 | 0.04614 | -0.057046 | 0.063453 | -0.014852 | -0.016229 | 121.5616 | 121.5398 | 121.4162 | 61.5889 | -121.493 | 121.339 | 121.4985 | 121.4971 | 61.6428 | -121.6339
518.3281 | 121.7422 | -61.5692 | 60.0082 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | 0.0053413 | -0.0018757 | -0.0010577 | 0.063411 | 0.022793 | 0.059017 | -61.5371 | 0.0243 | -61.5863 | 59.9878 | 59.9751 | 59.8653 | -61.5397 | -61.5139 | 0.078197 | -61.6079 | 59.7835 | 59.943 | 59.9417 | -61.6897 | 0.029516 | -0.020437 | 0.03215 | -0.017069 | -0.046585 | -0.033127 | -0.14298 | -0.1205 | -0.22473 | 0.055295 | -0.038734 | 0.081767 | -0.065205 | -0.066582 | 121.557 | 121.5443 | 121.4345 | 61.5935 | -121.5479 | 121.3527 | 121.5122 | 121.5109 | 61.6474 | -121.698
520.0156 | 121.843 | -61.5189 | 60.0174 | 1.4211e-13 | -0.030632 | 0.0016453 | 0.063218 | -0.0063223 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.022579 | 0.059017 | -61.5371 | 0.019721 | -61.5909 | 59.9878 | 59.9751 | 59.8561 | -61.5305 | -61.5139 | 0.082776 | -61.6263 | 59.7881 | 59.9385 | 59.9417 | -61.6806 | -0.01168 | -0.029592 | -0.018204 | -0.072001 | -0.060321 | -0.042282 | -0.1613 | -0.1617 | -0.22931 | 0.004941 | -0.1074 | 0.054295 | -0.078939 | -0.075737 | 121.5067 | 121.494 | 121.375 | 61.5386 | -121.5479 | 121.3069 | 121.4573 | 121.4605 | 61.6016 | -121.698
521.7656 | 121.8475 | -61.5692 | 60.0037 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063218 | -0.0069633 | 0.053538 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063624 | 0.022793 | 0.05859 | -61.5371 | 0.028878 | -61.5954 | 59.9924 | 59.9705 | 59.8653 | -61.5351 | -61.5231 | 0.082776 | -61.6125 | 59.7835 | 59.9339 | 59.9371 | -61.6851 | 0.034095 | -0.01128 | 0.03215 | -0.026225 | -0.06032 | -0.033128 | -0.1384 | -0.11592 | -0.22015 | 0.046137 | -0.043312 | 0.072611 | -0.069784 | -0.066583 | 121.5616 | 121.5397 | 121.4345 | 61.5981 | -121.5388 | 121.3527 | 121.5031 | 121.5063 | 61.652 | -121.6888
523.4531 | 121.7422 | -61.5189 | 60.1044 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063645 | -0.0069633 | 0.054179 | -0.01755 | -0.0016621 | -0.0012713 | 0.063411 | 0.022152 | 0.059017 | -61.5325 | 0.0243 | -61.5954 | 59.9924 | 59.9751 | 59.8515 | -61.5397 | -61.5093 | 0.078197 | -61.6125 | 59.7835 | 59.9339 | 59.9417 | -61.6851 | -0.020838 | -0.11199 | -0.013625 | -0.076579 | -0.055741 | -0.12926 | -0.25285 | -0.16628 | -0.32086 | 0.009519 | -0.093666 | 0.072611 | -0.17049 | -0.16271 | 121.5112 | 121.494 | 121.3704 | 61.5432 | -121.6441 | 121.3024 | 121.4527 | 121.4605 | 61.5971 | -121.7895
525.2031 | 121.8567 | -61.4914 | 60.0311 | 1.4211e-13 | -0.030205 | 0.0016453 | 0.063432 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063838 | 0.022365 | 0.059017 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9797 | 59.8698 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7881 | 59.9385 | 59.9417 | -61.6851 | -0.048304 | -0.043325 | -0.050248 | -0.10862 | -0.060319 | -0.051436 | -0.16129 | -0.19374 | -0.24304 | -0.022525 | -0.12571 | 0.068032 | -0.092672 | -0.08947 | 121.4792 | 121.4711 | 121.3612 | 61.5203 | -121.5708 | 121.2795 | 121.4299 | 121.4331 | 61.5742 | -121.7163
526.9531 | 121.8475 | -61.5463 | 59.9716 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063432 | -0.0069633 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.022152 | 0.059231 | -61.5416 | 0.028878 | -61.6 | 59.9878 | 59.9797 | 59.8561 | -61.5443 | -61.5139 | 0.087354 | -61.6217 | 59.7835 | 59.9385 | 59.9371 | -61.6897 | 0.002049 | 0.016184 | 0.004684 | -0.053691 | -0.05574 | 0.008073 | -0.11552 | -0.14339 | -0.18811 | 0.032407 | -0.075358 | 0.068031 | -0.033163 | -0.03454 | 121.5341 | 121.526 | 121.4024 | 61.5752 | -121.5159 | 121.3298 | 121.4848 | 121.4834 | 61.6337 | -121.6613
528.6406 | 121.7606 | -61.5646 | 60.022 | 1.4211e-13 | -0.030418 | 0.0018589 | 0.063218 | -0.0065361 | 0.053965 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.022152 | 0.05859 | -61.5325 | 0.028878 | -61.5954 | 59.9878 | 59.9705 | 59.8607 | -61.5443 | -61.5185 | 0.082776 | -61.6171 | 59.7789 | 59.9385 | 59.9417 | -61.6851 | 0.020359 | -0.03417 | 0.032151 | -0.030803 | -0.051162 | -0.051439 | -0.16129 | -0.1205 | -0.24305 | 0.046138 | -0.052469 | 0.068032 | -0.083517 | -0.080315 | 121.5524 | 121.5352 | 121.4253 | 61.5935 | -121.5662 | 121.3436 | 121.5031 | 121.5063 | 61.6474 | -121.7071
530.4062 | 121.788 | -61.528 | 60.0723 | 1.4211e-13 | -0.030418 | 0.0018589 | 0.063004 | -0.0067497 | 0.054179 | -0.01755 | -0.0018757 | -0.0014849 | 0.064052 | 0.022152 | 0.059017 | -61.5325 | 0.0243 | -61.6 | 59.9924 | 59.9797 | 59.8561 | -61.5443 | -61.5139 | 0.078197 | -61.6217 | 59.7743 | 59.9385 | 59.9417 | -61.6851 | -0.016262 | -0.079945 | -0.00447 | -0.072002 | -0.05574 | -0.092635 | -0.21623 | -0.15712 | -0.29798 | 0.014096 | -0.093669 | 0.063453 | -0.13387 | -0.13067 | 121.5204 | 121.5077 | 121.3841 | 61.5523 | -121.6166 | 121.3024 | 121.4665 | 121.4697 | 61.6062 | -121.7575
532.1562 | 121.7422 | -61.528 | 60.0998 | 1.4211e-13 | -0.030205 | 0.0014317 | 0.063645 | -0.0067497 | 0.053751 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.022365 | 0.059017 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9705 | 59.8561 | -61.5443 | -61.5093 | 0.078197 | -61.6171 | 59.7789 | 59.9476 | 59.9371 | -61.6806 | -0.016262 | -0.11199 | -0.00447 | -0.067424 | -0.051162 | -0.12926 | -0.24369 | -0.15254 | -0.32086 | 0.018674 | -0.08909 | 0.063453 | -0.15218 | -0.16271 | 121.5158 | 121.4985 | 121.3841 | 61.5523 | -121.6441 | 121.3069 | 121.4756 | 121.4651 | 61.6062 | -121.7803
533.8438 | 121.8246 | -61.4914 | 60.0586 | 1.4211e-13 | -0.030632 | 0.0016453 | 0.063004 | -0.0065361 | 0.053965 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063838 | 0.022579 | 0.059017 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9705 | 59.8607 | -61.5443 | -61.5231 | 0.073618 | -61.6079 | 59.7743 | 59.9385 | 59.9325 | -61.6806 | -0.052883 | -0.070791 | -0.041091 | -0.10404 | -0.051162 | -0.08806 | -0.19792 | -0.18916 | -0.28424 | -0.031683 | -0.11655 | 0.07261 | -0.12014 | -0.12609 | 121.4792 | 121.4619 | 121.3521 | 61.5157 | -121.6029 | 121.2657 | 121.4299 | 121.4239 | 61.565 | -121.7392
535.5938 | 121.8201 | -61.5417 | 59.9991 | 1.4211e-13 | -0.030418 | 0.0014317 | 0.063432 | -0.0067497 | 0.053538 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.022152 | 0.059017 | -61.5416 | 0.028878 | -61.5954 | 59.9832 | 59.9751 | 59.8607 | -61.5489 | -61.5048 | 0.082776 | -61.6171 | 59.7881 | 59.9385 | 59.9417 | -61.6806 | -0.007108 | -0.015859 | 0.000106 | -0.053691 | -0.046583 | -0.023971 | -0.13841 | -0.13881 | -0.211 | 0.036986 | -0.075357 | 0.063453 | -0.060628 | -0.057426 | 121.525 | 121.5169 | 121.4024 | 61.5706 | -121.5479 | 121.3298 | 121.4802 | 121.4834 | 61.6245 | -121.6796
537.3438 | 121.7422 | -61.5051 | 60.1227 | 1.4211e-13 | -0.030632 | 0.0016453 | 0.063218 | -0.0067497 | 0.053965 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063411 | 0.022579 | 0.058804 | -61.5416 | 0.0243 | -61.5954 | 59.9924 | 59.9705 | 59.8653 | -61.5397 | -61.5139 | 0.078197 | -61.6079 | 59.7835 | 59.9339 | 59.9325 | -61.6851 | -0.034571 | -0.1303 | -0.036515 | -0.090312 | -0.055741 | -0.15215 | -0.25742 | -0.18001 | -0.33917 | -0.008792 | -0.10282 | 0.077189 | -0.1888 | -0.19018 | 121.4975 | 121.4757 | 121.3704 | 61.5294 | -121.6624 | 121.2886 | 121.439 | 121.4376 | 61.5833 | -121.8078
539.0312 | 121.8979 | -61.4594 | 60.0311 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063218 | -0.0069633 | 0.053538 | -0.01755 | -0.0018757 | -0.0010577 | 0.063624 | 0.022365 | 0.059231 | -61.5371 | 0.033457 | -61.5909 | 59.9878 | 59.966 | 59.8607 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.9293 | 59.9417 | -61.6851 | -0.080347 | -0.043325 | -0.077713 | -0.13151 | -0.051163 | -0.065173 | -0.17045 | -0.22579 | -0.24762 | -0.054568 | -0.15775 | 0.068032 | -0.10183 | -0.08947 | 121.4472 | 121.4253 | 121.32 | 61.4928 | -121.5708 | 121.2429 | 121.3886 | 121.401 | 61.5421 | -121.7163
540.7969 | 121.8201 | -61.528 | 60.022 | 1.4211e-13 | -0.030632 | 0.0020727 | 0.063004 | -0.0067497 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063624 | 0.022152 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.9924 | 59.9705 | 59.8515 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7881 | 59.943 | 59.9417 | -61.6851 | -0.011683 | -0.029591 | -0.00447 | -0.067424 | -0.055741 | -0.051439 | -0.17045 | -0.15712 | -0.23389 | 0.014096 | -0.08909 | 0.068032 | -0.078938 | -0.080315 | 121.5204 | 121.4985 | 121.3795 | 61.5523 | -121.5617 | 121.3161 | 121.4711 | 121.4697 | 61.6062 | -121.7071
542.5469 | 121.756 | -61.5601 | 60.022 | 1.4211e-13 | -0.030632 | 0.0018589 | 0.063218 | -0.0067497 | 0.053965 | -0.0099192 | -0.0020893 | -0.0010577 | 0.063624 | 0.022152 | 0.05859 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9751 | 59.8607 | -61.5443 | -61.5048 | 0.087354 | -61.6125 | 59.7789 | 59.943 | 59.9417 | -61.6851 | 0.015782 | -0.03417 | 0.027574 | -0.03538 | -0.051162 | -0.04686 | -0.16129 | -0.12508 | -0.24305 | 0.055297 | -0.052467 | 0.072611 | -0.078938 | -0.080315 | 121.5479 | 121.5352 | 121.4207 | 61.5844 | -121.5662 | 121.339 | 121.5031 | 121.5017 | 61.6474 | -121.7071
544.2969 | 121.8018 | -61.5326 | 60.0494 | 1.4211e-13 | -0.030632 | 0.0014317 | 0.063004 | -0.0067497 | 0.053965 | -0.02518 | -0.0014485 | -0.0014849 | 0.063838 | 0.022365 | 0.059017 | -61.5371 | 0.019721 | -61.5909 | 59.9924 | 59.966 | 59.8607 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7743 | 59.9385 | 59.9371 | -61.6851 | -0.007105 | -0.057056 | -0.004471 | -0.058268 | -0.051163 | -0.083483 | -0.18876 | -0.15254 | -0.27509 | 0.018674 | -0.089091 | 0.063453 | -0.11098 | -0.11236 | 121.525 | 121.4985 | 121.3933 | 61.5523 | -121.5891 | 121.3069 | 121.471 | 121.4697 | 61.6154 | -121.7346
546.0469 | 121.7377 | -61.5738 | 60.0403 | 1.4211e-13 | -0.030846 | 0.0018589 | 0.063218 | -0.0067497 | 0.054179 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.022152 | 0.059231 | -61.5279 | 0.0243 | -61.5909 | 59.9832 | 59.9751 | 59.8607 | -61.5443 | -61.5048 | 0.073618 | -61.6171 | 59.7789 | 59.943 | 59.9417 | -61.6806 | 0.029515 | -0.057058 | 0.045885 | -0.017069 | -0.046584 | -0.06517 | -0.1796 | -0.10677 | -0.26136 | 0.06903 | -0.043313 | 0.063453 | -0.097248 | -0.098625 | 121.557 | 121.5489 | 121.4345 | 61.5981 | -121.5846 | 121.3527 | 121.5168 | 121.5154 | 61.6474 | -121.7208
547.7344 | 121.7926 | -61.5601 | 60.0494 | 1.4211e-13 | -0.030846 | 0.0014317 | 0.063004 | -0.0069633 | 0.053751 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.022365 | 0.059017 | -61.5325 | 0.0243 | -61.5863 | 59.9924 | 59.9797 | 59.8561 | -61.5397 | -61.5185 | 0.082776 | -61.6171 | 59.7835 | 59.9476 | 59.9417 | -61.6851 | 0.020361 | -0.057056 | 0.027574 | -0.026224 | -0.046585 | -0.069746 | -0.19334 | -0.12508 | -0.26593 | 0.041561 | -0.057046 | 0.068032 | -0.10183 | -0.10778 | 121.5524 | 121.5398 | 121.4162 | 61.5844 | -121.5891 | 121.3436 | 121.5077 | 121.5017 | 61.6428 | -121.7346
549.4844 | 121.7468 | -61.5326 | 60.1044 | 1.4211e-13 | -0.030632 | 0.0016453 | 0.063004 | -0.0063223 | 0.053965 | -0.0022892 | -0.0018757 | -0.00084406 | 0.063624 | 0.021938 | 0.05859 | -61.5325 | 0.0243 | -61.5909 | 59.9924 | 59.9751 | 59.8561 | -61.5489 | -61.5185 | 0.082776 | -61.6079 | 59.7881 | 59.943 | 59.9371 | -61.6806 | -0.016263 | -0.11199 | 0.000108 | -0.058268 | -0.042005 | -0.12926 | -0.24827 | -0.14796 | -0.31629 | 0.014095 | -0.075355 | 0.07261 | -0.16134 | -0.16729 | 121.525 | 121.5077 | 121.3887 | 61.5569 | -121.6532 | 121.3207 | 121.4756 | 121.4697 | 61.6154 | -121.7849
551.25 | 121.8796 | -61.4777 | 60.0494 | 1.4211e-13 | -0.030632 | 0.0014317 | 0.063004 | -0.0067497 | 0.053965 | -0.01755 | -0.0018757 | -0.0014849 | 0.063838 | 0.022365 | 0.059017 | -61.5279 | 0.028878 | -61.5954 | 59.9878 | 59.9797 | 59.8607 | -61.5443 | -61.5185 | 0.078197 | -61.6125 | 59.7835 | 59.9476 | 59.9417 | -61.6806 | -0.066616 | -0.061635 | -0.050246 | -0.11778 | -0.051162 | -0.069746 | -0.18876 | -0.2029 | -0.26593 | -0.040837 | -0.13487 | 0.068032 | -0.10183 | -0.10778 | 121.4655 | 121.4574 | 121.3383 | 61.5065 | -121.5937 | 121.2612 | 121.4253 | 121.4193 | 61.5559 | -121.73
552.9531 | 121.8292 | -61.5326 | 60.0082 | 1.4211e-13 | -0.030846 | 0.0014317 | 0.063004 | -0.0067497 | 0.054179 | 0.0053413 | -0.0018757 | -0.0014849 | 0.063838 | 0.022152 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.9832 | 59.9751 | 59.8607 | -61.5397 | -61.5139 | 0.087354 | -61.6079 | 59.7743 | 59.9339 | 59.9371 | -61.6851 | -0.007105 | -0.025015 | 0.000108 | -0.062846 | -0.055741 | -0.033127 | -0.14756 | -0.15254 | -0.23389 | 0.018674 | -0.075355 | 0.077189 | -0.074362 | -0.071161 | 121.5158 | 121.5077 | 121.3933 | 61.5569 | -121.5479 | 121.3069 | 121.4665 | 121.4697 | 61.6199 | -121.6934
554.7031 | 121.843 | -61.4777 | 60.0952 | 1.4211e-13 | -0.030632 | 0.0014317 | 0.063432 | -0.0063223 | 0.054179 | -0.01755 | -0.0020893 | -0.0010577 | 0.064052 | 0.022579 | 0.058804 | -61.5325 | 0.028878 | -61.5909 | 59.9878 | 59.966 | 59.8561 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.9385 | 59.9371 | -61.6851 | -0.062037 | -0.10741 | -0.054824 | -0.1132 | -0.051163 | -0.12926 | -0.23912 | -0.20748 | -0.31171 | -0.036258 | -0.14402 | 0.063453 | -0.15676 | -0.15814 | 121.4655 | 121.4436 | 121.3338 | 61.5065 | -121.6349 | 121.2612 | 121.4161 | 121.4147 | 61.5604 | -121.7804
556.4688 | 121.8475 | -61.5326 | 59.9991 | 1.4211e-13 | -0.030632 | 0.0020727 | 0.063004 | -0.0065361 | 0.053965 | -0.0099192 | -0.0014485 | -0.0010577 | 0.063411 | 0.022365 | 0.058804 | -61.5416 | 0.028878 | -61.5954 | 59.9924 | 59.9797 | 59.8607 | -61.5489 | -61.5139 | 0.087354 | -61.6079 | 59.7835 | 59.9339 | 59.9417 | -61.6943 | -0.016263 | -0.006702 | -0.009049 | -0.062846 | -0.046583 | -0.019392 | -0.13841 | -0.1617 | -0.21558 | 0.018674 | -0.075355 | 0.086346 | -0.065206 | -0.057426 | 121.525 | 121.5123 | 121.3933 | 61.5615 | -121.5479 | 121.3161 | 121.4665 | 121.4743 | 61.6199 | -121.6934
558.2188 | 121.7834 | -61.5372 | 60.0815 | 1.4211e-13 | -0.030632 | 0.0014317 | 0.063004 | -0.0067497 | 0.053751 | 0.0053413 | -0.0018757 | -0.0012713 | 0.064052 | 0.021938 | 0.059017 | -61.5371 | 0.015142 | -61.5954 | 59.9878 | 59.9797 | 59.8561 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7881 | 59.9385 | 59.9371 | -61.6897 | -0.002528 | -0.093679 | 0.000106 | -0.058269 | -0.055741 | -0.10179 | -0.22538 | -0.15254 | -0.2934 | 0.023251 | -0.079935 | 0.07261 | -0.14303 | -0.1444 | 121.525 | 121.5169 | 121.3933 | 61.5523 | -121.6212 | 121.3253 | 121.4756 | 121.4742 | 61.6199 | -121.7712
559.9062 | 121.756 | -61.5601 | 60.0403 | 1.4211e-13 | -0.030418 | 0.0020727 | 0.063004 | -0.0067497 | 0.054392 | -0.01755 | -0.0016621 | -0.0010577 | 0.063624 | 0.022365 | 0.059017 | -61.5325 | 0.019721 | -61.5954 | 59.9924 | 59.9705 | 59.8607 | -61.5397 | -61.5139 | 0.082776 | -61.6079 | 59.7881 | 59.9339 | 59.9371 | -61.6806 | 0.020361 | -0.047901 | 0.027574 | -0.03538 | -0.055741 | -0.069749 | -0.1796 | -0.1205 | -0.2522 | 0.04614 | -0.047889 | 0.07261 | -0.10641 | -0.1032 | 121.5524 | 121.5306 | 121.4207 | 61.5798 | -121.58 | 121.3481 | 121.4939 | 121.4971 | 61.6428 | -121.7208
561.6562 | 121.8704 | -61.496 | 60.054 | 1.4211e-13 | -0.030632 | 0.0018589 | 0.063004 | -0.0067497 | 0.053965 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063624 | 0.022579 | 0.058804 | -61.5325 | 0.028878 | -61.5863 | 59.9878 | 59.9751 | 59.8607 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7789 | 59.9385 | 59.9417 | -61.6806 | -0.048305 | -0.066213 | -0.036513 | -0.090311 | -0.042006 | -0.078903 | -0.19334 | -0.18459 | -0.27509 | -0.017947 | -0.11655 | 0.068032 | -0.11556 | -0.11236 | 121.4838 | 121.4711 | 121.3567 | 61.5249 | -121.5983 | 121.2749 | 121.4344 | 121.4376 | 61.5742 | -121.7346
563.3438 | 121.875 | -61.5601 | 59.9579 | 1.4211e-13 | -0.030846 | 0.0012179 | 0.063218 | -0.0067497 | 0.053965 | 0.0053413 | -0.0014485 | -0.0010577 | 0.063411 | 0.022365 | 0.058804 | -61.5371 | 0.0243 | -61.5863 | 59.9878 | 59.9797 | 59.8607 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9385 | 59.9325 | -61.6851 | 0.015782 | 0.029917 | 0.022995 | -0.026224 | -0.042006 | 0.021806 | -0.097207 | -0.12508 | -0.17438 | 0.04614 | -0.052467 | 0.072611 | -0.01943 | -0.025386 | 121.5479 | 121.5398 | 121.4207 | 61.5844 | -121.5022 | 121.3436 | 121.4985 | 121.4926 | 61.6383 | -121.643
565.0938 | 121.7377 | -61.5097 | 60.0998 | 1.4211e-13 | -0.030418 | 0.0014317 | 0.063004 | -0.0067497 | 0.053751 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.022365 | 0.058804 | -61.5279 | 0.019721 | -61.5863 | 59.9924 | 59.9705 | 59.8515 | -61.5443 | -61.5185 | 0.078197 | -61.6125 | 59.7881 | 59.9339 | 59.9417 | -61.6851 | -0.034572 | -0.10741 | -0.018202 | -0.076578 | -0.042006 | -0.12926 | -0.24827 | -0.17543 | -0.31171 | -0.008793 | -0.10282 | 0.072611 | -0.16591 | -0.15813 | 121.5021 | 121.4802 | 121.3612 | 61.5294 | -121.6441 | 121.2978 | 121.4436 | 121.4514 | 61.5879 | -121.7849
566.8594 | 121.7972 | -61.5646 | 60.054 | 1.4211e-13 | -0.030846 | 0.0012179 | 0.063218 | -0.0069633 | 0.053751 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.022579 | 0.059017 | -61.5325 | 0.0243 | -61.6 | 59.9878 | 59.9751 | 59.8561 | -61.5443 | -61.5185 | 0.078197 | -61.6263 | 59.7835 | 59.9339 | 59.9371 | -61.6806 | 0.020359 | -0.066213 | 0.032151 | -0.035381 | -0.05574 | -0.078903 | -0.19792 | -0.11592 | -0.27051 | 0.046138 | -0.061627 | 0.054295 | -0.12014 | -0.11694 | 121.5524 | 121.5397 | 121.4207 | 61.5889 | -121.5983 | 121.3481 | 121.4985 | 121.5017 | 61.6428 | -121.7346
568.6094 | 121.8658 | -61.528 | 59.9487 | 1.4211e-13 | -0.030418 | 0.0016453 | 0.063218 | -0.0065361 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063411 | 0.022579 | 0.058804 | -61.5279 | 0.0243 | -61.6 | 59.9924 | 59.9797 | 59.8607 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.9339 | 59.9462 | -61.6851 | -0.011683 | 0.043652 | 0.000108 | -0.072002 | -0.060319 | 0.030962 | -0.088051 | -0.15712 | -0.16522 | 0.014096 | -0.093669 | 0.063453 | -0.014852 | -0.002494 | 121.5204 | 121.5077 | 121.3887 | 61.5523 | -121.4884 | 121.3115 | 121.4619 | 121.4743 | 61.6108 | -121.6339
570.3594 | 121.8613 | -61.5326 | 59.9716 | 1.4211e-13 | -0.030846 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | 0.0053413 | -0.0020893 | -0.0012713 | 0.063624 | 0.022579 | 0.059017 | -61.5279 | 0.028878 | -61.6 | 59.997 | 59.9751 | 59.8561 | -61.5397 | -61.5093 | 0.078197 | -61.6171 | 59.7881 | 59.9476 | 59.9462 | -61.6851 | -0.007105 | 0.025341 | 0.004686 | -0.067424 | -0.060319 | 0.003494 | -0.11552 | -0.15254 | -0.18353 | 0.023252 | -0.084512 | 0.068032 | -0.024006 | -0.025383 | 121.5296 | 121.5077 | 121.3887 | 61.5615 | -121.5113 | 121.3207 | 121.4802 | 121.4788 | 61.6108 | -121.6568
572.0469 | 121.843 | -61.5646 | 59.9945 | 1.4211e-13 | -0.031059 | 0.0018589 | 0.063004 | -0.0067497 | 0.053751 | -0.0099192 | -0.0016621 | -0.0012713 | 0.064052 | 0.022579 | 0.059231 | -61.5325 | 0.0243 | -61.5909 | 59.9878 | 59.9751 | 59.8607 | -61.5397 | -61.5048 | 0.087354 | -61.6217 | 59.7881 | 59.9476 | 59.9371 | -61.6897 | 0.024938 | -0.006704 | 0.032151 | -0.026225 | -0.051163 | -0.019394 | -0.13383 | -0.12508 | -0.20642 | 0.059874 | -0.057048 | 0.068031 | -0.046894 | -0.057428 | 121.5524 | 121.5397 | 121.4253 | 61.5889 | -121.5342 | 121.3527 | 121.5122 | 121.5017 | 61.652 | -121.6842
573.7969 | 121.8155 | -61.5921 | 59.9716 | 1.4211e-13 | -0.030846 | 0.0014317 | 0.062791 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.0016987 | 0.063838 | 0.022579 | 0.059231 | -61.5279 | 0.028878 | -61.5863 | 59.997 | 59.9797 | 59.8607 | -61.5443 | -61.5093 | 0.078197 | -61.6171 | 59.7835 | 59.9339 | 59.9417 | -61.6851 | 0.047825 | 0.025341 | 0.064195 | 0.005819 | -0.042006 | 0.008073 | -0.11094 | -0.093035 | -0.18811 | 0.082761 | -0.025003 | 0.068032 | -0.037741 | -0.029961 | 121.5891 | 121.5718 | 121.4528 | 61.621 | -121.5159 | 121.3756 | 121.526 | 121.5338 | 61.6703 | -121.6568
575.5625 | 121.7743 | -61.5692 | 60.0403 | 1.4211e-13 | -0.030846 | 0.0018589 | 0.063218 | -0.0067497 | 0.053751 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.022579 | 0.058804 | -61.5325 | 0.028878 | -61.6 | 59.9878 | 59.9843 | 59.8698 | -61.5443 | -61.5093 | 0.078197 | -61.6217 | 59.7835 | 59.9339 | 59.9417 | -61.6897 | 0.024937 | -0.05248 | 0.036729 | -0.030803 | -0.05574 | -0.056013 | -0.17045 | -0.1205 | -0.25678 | 0.059873 | -0.05247 | 0.068031 | -0.10641 | -0.098625 | 121.557 | 121.5535 | 121.4391 | 61.5981 | -121.5846 | 121.3527 | 121.5031 | 121.5109 | 61.6474 | -121.73
577.3125 | 121.8567 | -61.4822 | 60.0311 | 1.4211e-13 | -0.030632 | 0.0018589 | 0.062791 | -0.0067497 | 0.053751 | -0.01755 | -0.0016621 | -0.0014849 | 0.063411 | 0.022579 | 0.058804 | -61.5279 | 0.0243 | -61.5954 | 59.9924 | 59.9797 | 59.8653 | -61.5443 | -61.5185 | 0.087354 | -61.6217 | 59.7789 | 59.9476 | 59.9462 | -61.6851 | -0.062038 | -0.038746 | -0.045668 | -0.1132 | -0.051162 | -0.051436 | -0.16587 | -0.2029 | -0.2522 | -0.036259 | -0.13945 | 0.063453 | -0.083515 | -0.084892 | 121.4746 | 121.4619 | 121.3475 | 61.5065 | -121.5754 | 121.2612 | 121.4299 | 121.4285 | 61.5696 | -121.7163
579 | 121.8246 | -61.5738 | 59.967 | 1.4211e-13 | -0.031059 | 0.0018589 | 0.063004 | -0.0069633 | 0.053751 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063411 | 0.022793 | 0.059017 | -61.5325 | 0.0243 | -61.5954 | 59.9924 | 59.9843 | 59.8515 | -61.5397 | -61.5048 | 0.087354 | -61.6171 | 59.7743 | 59.9385 | 59.9417 | -61.6897 | 0.034094 | 0.025341 | 0.041307 | -0.021647 | -0.055741 | 0.017229 | -0.11552 | -0.11592 | -0.19269 | 0.06903 | -0.043313 | 0.07261 | -0.028585 | -0.025383 | 121.5662 | 121.5581 | 121.4253 | 61.5981 | -121.5067 | 121.3481 | 121.5122 | 121.5154 | 61.6611 | -121.6568
580.7812 | 121.7834 | -61.5372 | 60.0403 | 1.4211e-13 | -0.030846 | 0.0012179 | 0.063432 | -0.0065361 | 0.053965 | 0.0053413 | -0.0018757 | -0.0010577 | 0.063838 | 0.022365 | 0.059017 | -61.5325 | 0.028878 | -61.5863 | 59.9924 | 59.9797 | 59.8653 | -61.5443 | -61.5185 | 0.087354 | -61.6217 | 59.7835 | 59.9385 | 59.9325 | -61.6851 | -0.007107 | -0.047901 | 0.004685 | -0.049113 | -0.042006 | -0.060591 | -0.17503 | -0.14797 | -0.25678 | 0.018672 | -0.084514 | 0.063453 | -0.10183 | -0.10778 | 121.5296 | 121.5169 | 121.4024 | 61.566 | -121.5846 | 121.3207 | 121.4756 | 121.4697 | 61.6245 | -121.7254
582.4844 | 121.8384 | -61.5417 | 59.9899 | 1.4211e-13 | -0.030846 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0022892 | -0.0020893 | -0.0012713 | 0.064052 | 0.023006 | 0.058804 | -61.5371 | 0.028878 | -61.5954 | 59.997 | 59.9797 | 59.8653 | -61.5443 | -61.5139 | 0.073618 | -61.6171 | 59.7835 | 59.9385 | 59.9462 | -61.6851 | -0.002529 | 0.007031 | 0.004684 | -0.053691 | -0.051162 | -0.010237 | -0.12467 | -0.14339 | -0.20642 | 0.027829 | -0.075357 | 0.068032 | -0.051473 | -0.043693 | 121.5387 | 121.5214 | 121.407 | 61.5706 | -121.5342 | 121.3253 | 121.4802 | 121.488 | 61.6154 | -121.6751
584.25 | 121.8796 | -61.5555 | 59.9625 | 1.4211e-13 | -0.030632 | 0.0016453 | 0.063218 | -0.0067497 | 0.053965 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063411 | 0.022579 | 0.05859 | -61.5371 | 0.033457 | -61.6 | 59.9924 | 59.9797 | 59.8561 | -61.5443 | -61.5093 | 0.087354 | -61.6171 | 59.7835 | 59.9385 | 59.9417 | -61.6897 | 0.011204 | 0.029919 | 0.018417 | -0.044536 | -0.05574 | 0.017229 | -0.10636 | -0.13423 | -0.17896 | 0.04614 | -0.061624 | 0.07261 | -0.024007 | -0.020805 | 121.5479 | 121.5352 | 121.4116 | 61.5889 | -121.5067 | 121.339 | 121.4939 | 121.4971 | 61.6428 | -121.6522
586.0156 | 121.8018 | -61.5509 | 60.0769 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063004 | -0.0067497 | 0.053965 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.022579 | 0.058804 | -61.5416 | 0.0243 | -61.5863 | 59.9832 | 59.9797 | 59.8607 | -61.5443 | -61.5093 | 0.078197 | -61.6171 | 59.7789 | 59.9385 | 59.9371 | -61.6806 | 0.006626 | -0.093679 | 0.009261 | -0.03538 | -0.042006 | -0.097212 | -0.21623 | -0.12965 | -0.29798 | 0.041562 | -0.066202 | 0.063453 | -0.13845 | -0.13983 | 121.5341 | 121.5306 | 121.4116 | 61.5752 | -121.6212 | 121.3298 | 121.4894 | 121.488 | 61.6291 | -121.7575
587.7656 | 121.8796 | -61.5692 | 59.9579 | 1.4211e-13 | -0.030846 | 0.0016453 | 0.063004 | -0.0067497 | 0.053751 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.022579 | 0.059231 | -61.5325 | 0.028878 | -61.5909 | 59.9924 | 59.9843 | 59.8653 | -61.5397 | -61.5231 | 0.078197 | -61.6171 | 59.7927 | 59.9385 | 59.9462 | -61.6806 | 0.029516 | 0.034496 | 0.036729 | -0.021647 | -0.051163 | 0.026384 | -0.092629 | -0.11134 | -0.16522 | 0.046137 | -0.047891 | 0.063453 | -0.01943 | -0.01165 | 121.5616 | 121.5535 | 121.4345 | 61.5981 | -121.4976 | 121.3619 | 121.5077 | 121.5155 | 61.6474 | -121.6384
589.4688 | 121.7926 | -61.5875 | 59.9854 | 1.4211e-13 | -0.030632 | 0.0014317 | 0.063218 | -0.0065361 | 0.053751 | -0.0099192 | -0.0014485 | -0.0014849 | 0.063838 | 0.022793 | 0.059017 | -61.5371 | 0.028878 | -61.5954 | 59.9924 | 59.9797 | 59.8607 | -61.5443 | -61.5185 | 0.087354 | -61.6125 | 59.7835 | 59.943 | 59.9371 | -61.6897 | 0.043247 | 0.00703 | 0.05046 | -0.007915 | -0.051162 | -0.00566 | -0.12467 | -0.10219 | -0.20184 | 0.069026 | -0.025002 | 0.077189 | -0.042317 | -0.048273 | 121.5799 | 121.5672 | 121.4482 | 61.6164 | -121.5296 | 121.371 | 121.5306 | 121.5246 | 61.6749 | -121.6751
591.2188 | 121.7972 | -61.5646 | 60.0494 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063004 | -0.0067497 | 0.054179 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064265 | 0.022579 | 0.059231 | -61.5325 | 0.019721 | -61.6 | 59.9878 | 59.9797 | 59.8561 | -61.5443 | -61.5185 | 0.087354 | -61.6171 | 59.7835 | 59.943 | 59.9417 | -61.6897 | 0.020359 | -0.061635 | 0.032151 | -0.035381 | -0.05574 | -0.069746 | -0.19334 | -0.12508 | -0.26593 | 0.046138 | -0.052469 | 0.07261 | -0.1064 | -0.10778 | 121.5524 | 121.5443 | 121.4207 | 61.5844 | -121.5937 | 121.3481 | 121.5077 | 121.5063 | 61.652 | -121.7392
592.9062 | 121.7972 | -61.528 | 60.0494 | 1.4211e-13 | -0.030632 | 0.0020727 | 0.063218 | -0.0071769 | 0.053965 | -0.01755 | -0.0016621 | -0.0012713 | 0.063624 | 0.022793 | 0.059231 | -61.5325 | 0.019721 | -61.6 | 59.9878 | 59.9797 | 59.8607 | -61.5443 | -61.5185 | 0.087354 | -61.6217 | 59.7835 | 59.943 | 59.9417 | -61.6897 | -0.016262 | -0.061635 | -0.00447 | -0.072002 | -0.05574 | -0.069746 | -0.18876 | -0.1617 | -0.26593 | 0.009517 | -0.093669 | 0.068031 | -0.1064 | -0.10778 | 121.5158 | 121.5077 | 121.3887 | 61.5477 | -121.5937 | 121.3115 | 121.4711 | 121.4697 | 61.6154 | -121.7392
594.6719 | 121.8292 | -61.5601 | 59.9899 | 1.4211e-13 | -0.030846 | 0.0016453 | 0.063218 | -0.0067497 | 0.053965 | -0.0099192 | -0.0014485 | -0.0012713 | 0.063624 | 0.022365 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9797 | 59.8607 | -61.5397 | -61.5093 | 0.082776 | -61.6217 | 59.7881 | 59.9476 | 59.9462 | -61.6897 | 0.020361 | -0.002126 | 0.027574 | -0.03538 | -0.055741 | -0.010237 | -0.12925 | -0.12966 | -0.20184 | 0.050718 | -0.061625 | 0.068031 | -0.042316 | -0.043693 | 121.5479 | 121.5398 | 121.4207 | 61.5844 | -121.5296 | 121.3481 | 121.5077 | 121.5063 | 61.6428 | -121.6796
596.4375 | 121.788 | -61.5784 | 60.0082 | 1.4211e-13 | -0.030846 | 0.0016453 | 0.063004 | -0.0069633 | 0.053538 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.022579 | 0.058804 | -61.5325 | 0.028878 | -61.6 | 59.9924 | 59.9797 | 59.8607 | -61.5351 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.6943 | 0.04325 | -0.015858 | 0.045884 | -0.021648 | -0.064898 | -0.028548 | -0.14756 | -0.11592 | -0.22473 | 0.06445 | -0.038736 | 0.077189 | -0.069784 | -0.071161 | 121.5708 | 121.5581 | 121.439 | 61.6072 | -121.5434 | 121.3619 | 121.5168 | 121.5154 | 61.6611 | -121.7025
598.125 | 121.7606 | -61.5234 | 60.1135 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063432 | -0.0067497 | 0.053751 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.022579 | 0.059017 | -61.5325 | 0.0243 | -61.5909 | 59.9924 | 59.9751 | 59.8607 | -61.5397 | -61.5231 | 0.082776 | -61.6125 | 59.7835 | 59.9385 | 59.9371 | -61.6851 | -0.016261 | -0.12114 | -0.009048 | -0.067424 | -0.051163 | -0.13841 | -0.25285 | -0.1617 | -0.33002 | 0.00036 | -0.089089 | 0.072611 | -0.17507 | -0.17645 | 121.5158 | 121.4985 | 121.3841 | 61.5477 | -121.6532 | 121.3069 | 121.4619 | 121.4605 | 61.6062 | -121.7987
599.875 | 121.8475 | -61.5372 | 60.0037 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063004 | -0.0067497 | 0.053965 | -0.02518 | -0.0016621 | -0.0010577 | 0.063624 | 0.022579 | 0.058804 | -61.5279 | 0.028878 | -61.5909 | 59.9878 | 59.9751 | 59.8607 | -61.5397 | -61.5185 | 0.078197 | -61.6217 | 59.7835 | 59.9385 | 59.9417 | -61.6943 | -0.002528 | -0.015859 | 0.009263 | -0.053691 | -0.051163 | -0.028549 | -0.14298 | -0.15712 | -0.22015 | 0.018672 | -0.084514 | 0.07261 | -0.065206 | -0.062004 | 121.525 | 121.5123 | 121.3978 | 61.566 | -121.5434 | 121.3207 | 121.4756 | 121.4788 | 61.6154 | -121.698
601.625 | 121.7606 | -61.5097 | 60.1273 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0010577 | 0.063838 | 0.022579 | 0.058804 | -61.5325 | 0.0243 | -61.6 | 59.9878 | 59.9888 | 59.8653 | -61.5397 | -61.5139 | 0.087354 | -61.6079 | 59.7881 | 59.943 | 59.9417 | -61.6897 | -0.029993 | -0.13945 | -0.02278 | -0.090312 | -0.060319 | -0.13841 | -0.262 | -0.18001 | -0.33917 | -0.004214 | -0.098243 | 0.081767 | -0.18422 | -0.1856 | 121.4975 | 121.4986 | 121.375 | 61.534 | -121.667 | 121.2978 | 121.4527 | 121.4514 | 61.5971 | -121.817
603.375 | 121.843 | -61.5692 | 60.0082 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063004 | -0.0063223 | 0.053965 | -0.01755 | -0.0016621 | -0.0010577 | 0.063624 | 0.022365 | 0.058804 | -61.5233 | 0.028878 | -61.5909 | 59.9924 | 59.9843 | 59.8653 | -61.5443 | -61.5139 | 0.087354 | -61.6171 | 59.7835 | 59.9293 | 59.9417 | -61.6897 | 0.024937 | -0.015858 | 0.045885 | -0.021647 | -0.046584 | -0.02397 | -0.14298 | -0.1205 | -0.22473 | 0.055295 | -0.047891 | 0.07261 | -0.078941 | -0.066582 | 121.5616 | 121.5535 | 121.4345 | 61.5981 | -121.5525 | 121.3527 | 121.4985 | 121.5109 | 61.6566 | -121.698
605.125 | 121.7468 | -61.5097 | 60.1089 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063432 | -0.0069633 | 0.053965 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.022579 | 0.058804 | -61.5371 | 0.028878 | -61.5909 | 59.9832 | 59.9797 | 59.8607 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.943 | 59.9417 | -61.6851 | -0.034572 | -0.12572 | -0.027359 | -0.081156 | -0.046584 | -0.12926 | -0.24827 | -0.17543 | -0.33002 | -0.004214 | -0.1074 | 0.068032 | -0.16591 | -0.16729 | 121.4929 | 121.4894 | 121.3704 | 61.5386 | -121.6532 | 121.2886 | 121.4527 | 121.4514 | 61.5879 | -121.7941
606.8906 | 121.8979 | -61.5005 | 60.0449 | 1.4211e-13 | -0.030846 | 0.0018589 | 0.063432 | -0.0067497 | 0.053965 | 0.0053413 | -0.0018757 | -0.0012713 | 0.063838 | 0.022793 | 0.058804 | -61.5325 | 0.0243 | -61.6 | 59.9924 | 59.9843 | 59.8607 | -61.5443 | -61.5231 | 0.078197 | -61.6171 | 59.7835 | 59.9293 | 59.9417 | -61.6897 | -0.043728 | -0.052479 | -0.031936 | -0.099468 | -0.05574 | -0.060591 | -0.18418 | -0.18917 | -0.26135 | -0.022528 | -0.11656 | 0.07261 | -0.11556 | -0.1032 | 121.4929 | 121.4848 | 121.3612 | 61.5248 | -121.5891 | 121.2841 | 121.4298 | 121.4422 | 61.5787 | -121.7346
608.6406 | 121.7422 | -61.5875 | 59.9991 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063624 | 0.022793 | 0.05859 | -61.5233 | 0.028878 | -61.5954 | 59.997 | 59.9843 | 59.8653 | -61.5397 | -61.5185 | 0.087354 | -61.6079 | 59.7835 | 59.9339 | 59.9417 | -61.6897 | 0.047826 | -0.002124 | 0.064195 | -0.007915 | -0.055741 | -0.014814 | -0.13383 | -0.10219 | -0.21558 | 0.069026 | -0.020424 | 0.081767 | -0.065206 | -0.057426 | 121.5845 | 121.5718 | 121.4528 | 61.6164 | -121.5388 | 121.371 | 121.5214 | 121.5292 | 61.6749 | -121.6888
610.3281 | 121.8475 | -61.5326 | 59.9991 | 1.4211e-13 | -0.030846 | 0.0014317 | 0.063004 | -0.0067497 | 0.054392 | -0.0022892 | -0.0014485 | -0.0012713 | 0.063624 | 0.022579 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.9832 | 59.9797 | 59.8607 | -61.5489 | -61.5048 | 0.087354 | -61.6171 | 59.7835 | 59.9476 | 59.9371 | -61.6897 | -0.016263 | -0.015859 | 0.000108 | -0.062846 | -0.046583 | -0.019392 | -0.13841 | -0.15712 | -0.21558 | 0.027831 | -0.084512 | 0.07261 | -0.051471 | -0.062005 | 121.5158 | 121.5123 | 121.3933 | 61.5569 | -121.5479 | 121.3161 | 121.4802 | 121.4697 | 61.6199 | -121.6888
612.0781 | 121.7697 | -61.5829 | 60.0174 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063004 | -0.0071769 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.022793 | 0.059017 | -61.5279 | 0.0243 | -61.6 | 59.997 | 59.9797 | 59.8653 | -61.5397 | -61.5139 | 0.082776 | -61.6217 | 59.7927 | 59.9385 | 59.9371 | -61.6897 | 0.043249 | -0.020435 | 0.05504 | -0.01707 | -0.060319 | -0.037703 | -0.15214 | -0.10677 | -0.22473 | 0.069028 | -0.038737 | 0.068031 | -0.078939 | -0.080316 | 121.5799 | 121.5626 | 121.4482 | 61.6072 | -121.5571 | 121.3756 | 121.5214 | 121.52 | 61.6657 | -121.7071
613.8281 | 121.7606 | -61.496 | 60.1181 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063432 | -0.0071769 | 0.053751 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063838 | 0.023006 | 0.059017 | -61.5325 | 0.028878 | -61.5909 | 59.9924 | 59.9797 | 59.8653 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.9385 | 59.9417 | -61.6897 | -0.043726 | -0.12572 | -0.036513 | -0.094889 | -0.051163 | -0.13841 | -0.25285 | -0.19374 | -0.3346 | -0.017947 | -0.12113 | 0.07261 | -0.17965 | -0.17645 | 121.4884 | 121.4757 | 121.3612 | 61.5249 | -121.6578 | 121.2795 | 121.4344 | 121.4376 | 61.5787 | -121.8078
615.5781 | 121.7743 | -61.5784 | 60.0128 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063218 | -0.0067497 | 0.054179 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063624 | 0.023006 | 0.058804 | -61.5279 | 0.033457 | -61.6 | 59.997 | 59.9797 | 59.8653 | -61.5397 | -61.5139 | 0.078197 | -61.6217 | 59.7881 | 59.9476 | 59.9462 | -61.6806 | 0.038671 | -0.015857 | 0.050462 | -0.021648 | -0.060319 | -0.033125 | -0.14756 | -0.10219 | -0.22473 | 0.06445 | -0.043315 | 0.058874 | -0.065204 | -0.066581 | 121.5753 | 121.5581 | 121.4436 | 61.6118 | -121.5525 | 121.3665 | 121.526 | 121.5246 | 61.6566 | -121.6934
617.3281 | 121.7972 | -61.5417 | 60.0403 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063004 | -0.0071769 | 0.054179 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.022579 | 0.059017 | -61.5325 | 0.028878 | -61.5909 | 59.9878 | 59.9797 | 59.8607 | -61.5443 | -61.5185 | 0.078197 | -61.6125 | 59.7881 | 59.9293 | 59.9508 | -61.6851 | -0.002529 | -0.05248 | 0.009263 | -0.049113 | -0.046584 | -0.060591 | -0.1796 | -0.14339 | -0.2522 | 0.02325 | -0.070778 | 0.072611 | -0.11098 | -0.089468 | 121.5296 | 121.5214 | 121.4024 | 61.5706 | -121.5846 | 121.3298 | 121.471 | 121.4926 | 61.6199 | -121.7254
619.0156 | 121.7468 | -61.5005 | 60.1044 | 1.4211e-13 | -0.031487 | 0.0014317 | 0.063432 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.022793 | 0.058804 | -61.5279 | 0.0243 | -61.6 | 59.9832 | 59.9797 | 59.8698 | -61.5397 | -61.5139 | 0.082776 | -61.6171 | 59.7881 | 59.9385 | 59.9417 | -61.6943 | -0.039149 | -0.12115 | -0.027358 | -0.099468 | -0.060319 | -0.12468 | -0.23453 | -0.19374 | -0.31629 | -0.01337 | -0.11656 | 0.077189 | -0.16591 | -0.16271 | 121.4838 | 121.4802 | 121.3704 | 61.5248 | -121.6441 | 121.2886 | 121.439 | 121.4422 | 61.5833 | -121.7987
620.7656 | 121.7377 | -61.5738 | 60.0311 | 1.4211e-13 | -0.030846 | 0.0018589 | 0.063004 | -0.0069633 | 0.053751 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.023006 | 0.058804 | -61.5233 | 0.033457 | -61.5909 | 59.997 | 59.9751 | 59.8698 | -61.5397 | -61.5185 | 0.087354 | -61.6217 | 59.7789 | 59.9385 | 59.9417 | -61.6851 | 0.034094 | -0.034168 | 0.050463 | -0.017069 | -0.051163 | -0.056015 | -0.16129 | -0.11135 | -0.2522 | 0.055294 | -0.047892 | 0.063453 | -0.092672 | -0.08947 | 121.5708 | 121.5489 | 121.4436 | 61.6072 | -121.5708 | 121.3527 | 121.5122 | 121.5154 | 61.6611 | -121.7163
622.4688 | 121.8887 | -61.4914 | 60.054 | 1.4211e-13 | -0.031059 | 0.0018589 | 0.063218 | -0.0067497 | 0.053965 | -0.01755 | -0.0014485 | -0.0012713 | 0.063624 | 0.022793 | 0.059017 | -61.5279 | 0.0243 | -61.5909 | 59.9878 | 59.9797 | 59.8561 | -61.5397 | -61.5185 | 0.078197 | -61.6171 | 59.7881 | 59.943 | 59.9417 | -61.6897 | -0.048304 | -0.066213 | -0.036513 | -0.099467 | -0.051163 | -0.074324 | -0.19792 | -0.19832 | -0.26593 | -0.027104 | -0.12571 | 0.07261 | -0.11098 | -0.11236 | 121.4792 | 121.4711 | 121.3475 | 61.5157 | -121.5937 | 121.2795 | 121.4344 | 121.4331 | 61.5696 | -121.7437
624.2031 | 121.7285 | -61.5829 | 60.0357 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063004 | -0.0069633 | 0.054179 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.022579 | 0.058804 | -61.5371 | 0.0243 | -61.6 | 59.9878 | 59.9797 | 59.8653 | -61.5443 | -61.5139 | 0.087354 | -61.6171 | 59.7927 | 59.9476 | 59.9371 | -61.6897 | 0.03867 | -0.047903 | 0.045883 | -0.01707 | -0.05574 | -0.056014 | -0.17045 | -0.10677 | -0.24304 | 0.069028 | -0.034158 | 0.07261 | -0.088093 | -0.098627 | 121.5708 | 121.5626 | 121.4482 | 61.6072 | -121.58 | 121.3756 | 121.5306 | 121.52 | 61.6703 | -121.7254
625.9531 | 121.7834 | -61.5234 | 60.0677 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063004 | -0.0069633 | 0.053965 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063624 | 0.022579 | 0.058804 | -61.5371 | 0.028878 | -61.6 | 59.9924 | 59.9797 | 59.8561 | -61.5489 | -61.5139 | 0.082776 | -61.6217 | 59.7835 | 59.943 | 59.9325 | -61.6897 | -0.025419 | -0.075367 | -0.013627 | -0.07658 | -0.051161 | -0.088057 | -0.21165 | -0.16628 | -0.28424 | 0.009518 | -0.098247 | 0.068031 | -0.12471 | -0.13525 | 121.5158 | 121.5031 | 121.3795 | 61.5523 | -121.6166 | 121.3069 | 121.4665 | 121.4559 | 61.6062 | -121.7575
627.7031 | 121.7285 | -61.5875 | 60.0266 | 1.4211e-13 | -0.030846 | 0.0020727 | 0.063004 | -0.0069633 | 0.053965 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.023006 | 0.059231 | -61.5279 | 0.028878 | -61.5954 | 59.9878 | 59.9797 | 59.8607 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.943 | 59.9417 | -61.6897 | 0.043247 | -0.038747 | 0.059617 | -0.007915 | -0.051162 | -0.046858 | -0.16587 | -0.10219 | -0.24762 | 0.073605 | -0.029581 | 0.07261 | -0.083515 | -0.084892 | 121.5753 | 121.5672 | 121.4482 | 61.6164 | -121.5708 | 121.3665 | 121.5306 | 121.5292 | 61.6657 | -121.7163
629.4531 | 121.8842 | -61.4731 | 60.0449 | 1.4211e-13 | -0.030632 | 0.0016453 | 0.062791 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.023006 | 0.059017 | -61.5279 | 0.019721 | -61.5909 | 59.9924 | 59.9797 | 59.8561 | -61.5397 | -61.5093 | 0.082776 | -61.6125 | 59.7835 | 59.9476 | 59.9371 | -61.6897 | -0.066615 | -0.052479 | -0.054824 | -0.11778 | -0.051163 | -0.065169 | -0.18876 | -0.21663 | -0.26135 | -0.036258 | -0.13944 | 0.077189 | -0.097248 | -0.10778 | 121.4655 | 121.4528 | 121.3292 | 61.4928 | -121.5846 | 121.2566 | 121.4207 | 121.4102 | 61.5559 | -121.7346
631.1406 | 121.7377 | -61.4914 | 60.0952 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063004 | -0.0067497 | 0.054179 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064265 | 0.02322 | 0.059017 | -61.5279 | 0.0243 | -61.5954 | 59.997 | 59.9843 | 59.8653 | -61.5443 | -61.5139 | 0.087354 | -61.6171 | 59.7789 | 59.9476 | 59.9417 | -61.6897 | -0.052883 | -0.098255 | -0.036513 | -0.10404 | -0.051162 | -0.11095 | -0.22996 | -0.19832 | -0.31629 | -0.022525 | -0.12571 | 0.07261 | -0.1476 | -0.15356 | 121.4884 | 121.4757 | 121.3567 | 61.5157 | -121.6395 | 121.2703 | 121.439 | 121.4331 | 61.5787 | -121.7849
632.8906 | 121.8292 | -61.5601 | 60.0266 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063218 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0010577 | 0.063838 | 0.022793 | 0.058804 | -61.5371 | 0.019721 | -61.5909 | 59.9924 | 59.9843 | 59.8653 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9476 | 59.9417 | -61.6943 | 0.015782 | -0.034168 | 0.022995 | -0.030802 | -0.046584 | -0.04228 | -0.16129 | -0.13423 | -0.24304 | 0.04614 | -0.052467 | 0.081768 | -0.078937 | -0.084892 | 121.5524 | 121.5443 | 121.4253 | 61.5798 | -121.5708 | 121.3436 | 121.5077 | 121.5017 | 61.6383 | -121.7208
634.6406 | 121.7514 | -61.5005 | 60.1044 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063218 | -0.0071769 | 0.053965 | -0.01755 | -0.0020893 | -0.0010577 | 0.063624 | 0.022793 | 0.058804 | -61.5371 | 0.019721 | -61.5909 | 59.9878 | 59.9751 | 59.8607 | -61.5397 | -61.5139 | 0.096512 | -61.6171 | 59.7835 | 59.9476 | 59.9371 | -61.6943 | -0.039149 | -0.11657 | -0.036515 | -0.090312 | -0.051163 | -0.12926 | -0.24369 | -0.19374 | -0.32086 | -0.01337 | -0.11656 | 0.077189 | -0.15676 | -0.16729 | 121.4884 | 121.4757 | 121.3612 | 61.5203 | -121.6441 | 121.2841 | 121.4482 | 121.4376 | 61.5971 | -121.7987
636.3281 | 121.7468 | -61.5509 | 60.0174 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063004 | -0.0069633 | 0.054179 | -0.01755 | -0.0020893 | -0.0016987 | 0.063411 | 0.022579 | 0.059231 | -61.5325 | 0.0243 | -61.5954 | 59.9878 | 59.9797 | 59.8607 | -61.5443 | -61.5139 | 0.082776 | -61.6125 | 59.7927 | 59.9476 | 59.9417 | -61.6897 | 0.006626 | -0.029592 | 0.018418 | -0.044536 | -0.051162 | -0.037703 | -0.15672 | -0.13881 | -0.22473 | 0.036984 | -0.061623 | 0.077189 | -0.069782 | -0.075737 | 121.5387 | 121.5306 | 121.4116 | 61.5752 | -121.5617 | 121.3436 | 121.4985 | 121.4926 | 61.6337 | -121.7071
638.0781 | 121.8384 | -61.5326 | 59.967 | 1.4211e-13 | -0.031059 | 0.0014317 | 0.063218 | -0.0069633 | 0.054179 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063411 | 0.022793 | 0.058804 | -61.5279 | 0.0243 | -61.6 | 59.997 | 59.9751 | 59.8653 | -61.5351 | -61.5185 | 0.087354 | -61.6125 | 59.7881 | 59.9476 | 59.9371 | -61.6943 | -0.002526 | 0.029919 | 0.004686 | -0.067424 | -0.064898 | 0.008072 | -0.10178 | -0.1617 | -0.17896 | 0.014095 | -0.079933 | 0.081768 | -0.019428 | -0.029962 | 121.5296 | 121.5077 | 121.3979 | 61.5569 | -121.5022 | 121.3207 | 121.4802 | 121.4697 | 61.6199 | -121.6613
639.8281 | 121.8933 | -61.5051 | 60.0311 | 1.4211e-13 | -0.031487 | 0.0012179 | 0.063432 | -0.0067497 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.022579 | 0.058804 | -61.5325 | 0.0243 | -61.6 | 59.9924 | 59.9797 | 59.8653 | -61.5443 | -61.5231 | 0.078197 | -61.6171 | 59.7835 | 59.9522 | 59.9371 | -61.6897 | -0.03915 | -0.038746 | -0.027358 | -0.09489 | -0.05574 | -0.051436 | -0.16587 | -0.18459 | -0.24762 | -0.01795 | -0.11198 | 0.07261 | -0.078936 | -0.094049 | 121.4975 | 121.4848 | 121.3704 | 61.5294 | -121.5754 | 121.2886 | 121.4573 | 121.4422 | 61.5833 | -121.7208
641.5938 | 121.8658 | -61.4731 | 60.0403 | 1.4211e-13 | -0.031487 | 0.0018589 | 0.062791 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0014849 | 0.063624 | 0.023006 | 0.059017 | -61.5325 | 0.028878 | -61.5909 | 59.9878 | 59.9843 | 59.8607 | -61.5443 | -61.5093 | 0.082776 | -61.6171 | 59.7881 | 59.9476 | 59.9325 | -61.6897 | -0.071194 | -0.05248 | -0.059402 | -0.11778 | -0.046584 | -0.056013 | -0.1796 | -0.21663 | -0.2522 | -0.036258 | -0.14402 | 0.07261 | -0.09267 | -0.10778 | 121.4609 | 121.4574 | 121.3338 | 61.502 | -121.5846 | 121.2612 | 121.4207 | 121.4056 | 61.5559 | -121.73
643.3594 | 121.7514 | -61.528 | 60.0769 | 1.4211e-13 | -0.031273 | 0.0018589 | 0.063432 | -0.0069633 | 0.054179 | -0.01755 | -0.0018757 | -0.0010577 | 0.064052 | 0.022793 | 0.059017 | -61.5325 | 0.028878 | -61.5954 | 59.997 | 59.9888 | 59.8607 | -61.5443 | -61.5139 | 0.082776 | -61.6125 | 59.7835 | 59.9476 | 59.9371 | -61.7035 | -0.016262 | -0.079944 | -0.00447 | -0.067424 | -0.051162 | -0.088055 | -0.21623 | -0.17544 | -0.2934 | 0.014096 | -0.084511 | 0.090926 | -0.12929 | -0.13983 | 121.525 | 121.5169 | 121.3887 | 61.5569 | -121.6212 | 121.3115 | 121.4756 | 121.4651 | 61.6108 | -121.7804
645.1094 | 121.8704 | -61.5417 | 59.9487 | 1.4211e-13 | -0.031487 | 0.0018589 | 0.063004 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0014849 | 0.063838 | 0.02322 | 0.059017 | -61.5279 | 0.0243 | -61.5954 | 59.9924 | 59.9843 | 59.8607 | -61.5443 | -61.5093 | 0.082776 | -61.6125 | 59.7881 | 59.9476 | 59.9417 | -61.6897 | -0.002529 | 0.043652 | 0.013841 | -0.053691 | -0.051162 | 0.03554 | -0.088051 | -0.14797 | -0.16064 | 0.032407 | -0.070778 | 0.077189 | -0.001117 | -0.007072 | 121.5341 | 121.526 | 121.4024 | 61.566 | -121.493 | 121.3298 | 121.4894 | 121.4834 | 61.6245 | -121.6384
646.8125 | 121.7651 | -61.5189 | 60.0952 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063218 | -0.0067497 | 0.054392 | -0.01755 | -0.0014485 | -0.0012713 | 0.063624 | 0.022793 | 0.059231 | -61.5325 | 0.028878 | -61.6 | 59.9924 | 59.9843 | 59.8653 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7881 | 59.943 | 59.9417 | -61.6897 | -0.025417 | -0.10283 | -0.013625 | -0.081157 | -0.05574 | -0.11095 | -0.22996 | -0.17086 | -0.30713 | 0.004941 | -0.093666 | 0.077189 | -0.15218 | -0.15356 | 121.5112 | 121.5031 | 121.3841 | 61.5477 | -121.6395 | 121.3069 | 121.4619 | 121.4605 | 61.5971 | -121.7849
648.5625 | 121.7377 | -61.5738 | 60.0403 | 1.4211e-13 | -0.031487 | 0.0014317 | 0.063218 | -0.0071769 | 0.054606 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063624 | 0.022579 | 0.059231 | -61.5325 | 0.028878 | -61.5909 | 59.9924 | 59.9797 | 59.8653 | -61.5489 | -61.5139 | 0.078197 | -61.6171 | 59.7789 | 59.943 | 59.9417 | -61.6897 | 0.024936 | -0.047901 | 0.041307 | -0.017069 | -0.042005 | -0.060591 | -0.17503 | -0.11592 | -0.26136 | 0.059873 | -0.043313 | 0.07261 | -0.097248 | -0.098625 | 121.5662 | 121.5535 | 121.439 | 61.6027 | -121.5891 | 121.3527 | 121.5168 | 121.5154 | 61.652 | -121.73
650.3125 | 121.8842 | -61.496 | 60.0449 | 1.4211e-13 | -0.031487 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | 0.0053413 | -0.0020893 | -0.0014849 | 0.063624 | 0.022793 | 0.058804 | -61.5325 | 0.028878 | -61.5909 | 59.9924 | 59.9843 | 59.8653 | -61.5443 | -61.5185 | 0.078197 | -61.6217 | 59.7835 | 59.9522 | 59.9371 | -61.6943 | -0.048305 | -0.052479 | -0.036513 | -0.094889 | -0.046584 | -0.060591 | -0.1796 | -0.19832 | -0.26135 | -0.022526 | -0.12571 | 0.07261 | -0.092669 | -0.10778 | 121.4884 | 121.4802 | 121.3612 | 61.5249 | -121.5891 | 121.2795 | 121.4482 | 121.4331 | 61.5742 | -121.7392
652.0781 | 121.7926 | -61.5189 | 60.0723 | 1.4211e-13 | -0.031059 | 0.0016453 | 0.063432 | -0.0069633 | 0.054179 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063624 | 0.023006 | 0.059017 | -61.5325 | 0.033457 | -61.5863 | 59.9878 | 59.9705 | 59.8653 | -61.5443 | -61.5093 | 0.082776 | -61.6171 | 59.7835 | 59.9385 | 59.9417 | -61.6943 | -0.025417 | -0.084524 | -0.013625 | -0.067423 | -0.042006 | -0.10179 | -0.20707 | -0.17543 | -0.28882 | 0.009519 | -0.098245 | 0.077189 | -0.13387 | -0.13067 | 121.5067 | 121.4894 | 121.3841 | 61.5523 | -121.6166 | 121.3024 | 121.4573 | 121.4605 | 61.6016 | -121.7666
653.8281 | 121.8292 | -61.5646 | 60.022 | 1.4211e-13 | -0.031487 | 0.0016453 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063624 | 0.022793 | 0.05859 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.9797 | 59.8653 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7835 | 59.9476 | 59.9417 | -61.6943 | 0.020359 | -0.025013 | 0.032151 | -0.030803 | -0.051162 | -0.042281 | -0.15672 | -0.12966 | -0.23847 | 0.050717 | -0.052469 | 0.077189 | -0.07436 | -0.080315 | 121.5616 | 121.5443 | 121.4299 | 61.5889 | -121.5662 | 121.3481 | 121.5122 | 121.5063 | 61.6428 | -121.7163
655.5156 | 121.8246 | -61.5326 | 60.0266 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.062577 | -0.0069633 | 0.054179 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063411 | 0.022793 | 0.059017 | -61.5325 | 0.028878 | -61.5909 | 59.9924 | 59.9843 | 59.8653 | -61.5489 | -61.5093 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.6897 | -0.016263 | -0.034168 | 0.000108 | -0.058268 | -0.042005 | -0.04228 | -0.16129 | -0.15712 | -0.24304 | 0.023252 | -0.084512 | 0.07261 | -0.083515 | -0.089471 | 121.525 | 121.5169 | 121.3979 | 61.5615 | -121.5754 | 121.3161 | 121.4756 | 121.4697 | 61.6108 | -121.7163
657.2656 | 121.8384 | -61.5463 | 59.9808 | 1.4211e-13 | -0.031273 | 0.0014317 | 0.063218 | -0.0069633 | 0.054392 | 0.0053413 | -0.0018757 | -0.0014849 | 0.063197 | 0.023006 | 0.059017 | -61.5325 | 0.028878 | -61.5909 | 59.9924 | 59.9843 | 59.8698 | -61.5443 | -61.5093 | 0.087354 | -61.6125 | 59.7835 | 59.9522 | 59.9371 | -61.6851 | 0.002049 | 0.011608 | 0.013841 | -0.044535 | -0.046584 | 0.003496 | -0.11094 | -0.13881 | -0.19727 | 0.036985 | -0.0662 | 0.072611 | -0.028582 | -0.043695 | 121.5387 | 121.5306 | 121.4162 | 61.5752 | -121.5251 | 121.3298 | 121.4985 | 121.4834 | 61.6337 | -121.6659
659.0156 | 121.7972 | -61.4868 | 60.0952 | 1.4211e-13 | -0.031273 | 0.0018589 | 0.063218 | -0.0065361 | 0.054392 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.023006 | 0.05859 | -61.5279 | 0.028878 | -61.5954 | 59.9924 | 59.9751 | 59.8653 | -61.5489 | -61.5093 | 0.06904 | -61.6171 | 59.7881 | 59.9568 | 59.9417 | -61.6897 | -0.06204 | -0.10283 | -0.041091 | -0.10862 | -0.046583 | -0.1201 | -0.22996 | -0.2029 | -0.30713 | -0.022525 | -0.13029 | 0.07261 | -0.13844 | -0.15356 | 121.4792 | 121.4619 | 121.3521 | 61.5157 | -121.6441 | 121.2749 | 121.4436 | 121.4285 | 61.5559 | -121.7849
660.7656 | 121.7239 | -61.5829 | 60.0174 | 1.4211e-13 | -0.031273 | 0.0016453 | 0.063218 | -0.0071769 | 0.054606 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063624 | 0.022793 | 0.059231 | -61.5325 | 0.0243 | -61.5909 | 59.997 | 59.9843 | 59.8698 | -61.5489 | -61.5185 | 0.078197 | -61.6171 | 59.7881 | 59.943 | 59.9417 | -61.6897 | 0.034091 | -0.020435 | 0.050462 | -0.007914 | -0.042005 | -0.033125 | -0.14756 | -0.10677 | -0.22931 | 0.064449 | -0.034158 | 0.07261 | -0.07436 | -0.075737 | 121.5799 | 121.5672 | 121.4528 | 61.6072 | -121.5663 | 121.371 | 121.526 | 121.5246 | 61.6611 | -121.7071
662.4531 | 121.8704 | -61.5234 | 60.022 | 1.4211e-13 | -0.031487 | 0.0018589 | 0.063645 | -0.0069633 | 0.054392 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.023006 | 0.059017 | -61.5279 | 0.033457 | -61.5909 | 59.9924 | 59.9843 | 59.8653 | -61.5489 | -61.5139 | 0.082776 | -61.6079 | 59.7789 | 59.9522 | 59.9462 | -61.6897 | -0.025419 | -0.029591 | -0.00447 | -0.067424 | -0.042005 | -0.037703 | -0.15672 | -0.16628 | -0.24305 | 0.009518 | -0.084511 | 0.081767 | -0.069781 | -0.075737 | 121.5158 | 121.5077 | 121.3887 | 61.5569 | -121.5708 | 121.3024 | 121.4756 | 121.4697 | 61.6062 | -121.7117
664.2031 | 121.875 | -61.5692 | 59.967 | 1.4211e-13 | -0.031273 | 0.0012179 | 0.063218 | -0.0067497 | 0.054606 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063411 | 0.022793 | 0.059231 | -61.5325 | 0.0243 | -61.5863 | 59.997 | 59.9888 | 59.8607 | -61.5397 | -61.5139 | 0.078197 | -61.6125 | 59.7789 | 59.9476 | 59.9371 | -61.6943 | 0.029516 | 0.029919 | 0.036729 | -0.017069 | -0.046585 | 0.021808 | -0.10636 | -0.12508 | -0.18811 | 0.055295 | -0.043312 | 0.081768 | -0.019428 | -0.029962 | 121.5662 | 121.5581 | 121.4299 | 61.5935 | -121.5067 | 121.3481 | 121.5168 | 121.5063 | 61.6474 | -121.6613
665.9375 | 121.8979 | -61.496 | 60.0403 | 1.4211e-13 | -0.031487 | 0.0014317 | 0.063432 | -0.0069633 | 0.054179 | -0.02518 | -0.0020893 | -0.0010577 | 0.063838 | 0.023006 | 0.058804 | -61.5325 | 0.0243 | -61.5909 | 59.9924 | 59.9797 | 59.8653 | -61.5443 | -61.5185 | 0.082776 | -61.6171 | 59.7835 | 59.9476 | 59.9371 | -61.6943 | -0.048305 | -0.047901 | -0.036513 | -0.094889 | -0.046584 | -0.060591 | -0.17503 | -0.19832 | -0.25678 | -0.022526 | -0.12113 | 0.077189 | -0.09267 | -0.1032 | 121.4884 | 121.4757 | 121.3612 | 61.5203 | -121.5846 | 121.2795 | 121.4436 | 121.4331 | 61.5787 | -121.7346
667.6406 | 121.7606 | -61.5875 | 60.0311 | 1.4211e-13 | -0.0317 | 0.0016453 | 0.063218 | -0.0069633 | 0.054392 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063838 | 0.023006 | 0.058804 | -61.5325 | 0.028878 | -61.5863 | 59.9924 | 59.9797 | 59.8698 | -61.5443 | -61.5048 | 0.078197 | -61.6125 | 59.7881 | 59.943 | 59.9417 | -61.6897 | 0.043247 | -0.038746 | 0.055039 | 0.001241 | -0.042006 | -0.051436 | -0.16129 | -0.10219 | -0.24304 | 0.082762 | -0.025002 | 0.077189 | -0.088093 | -0.08947 | 121.5799 | 121.5672 | 121.4574 | 61.6164 | -121.5754 | 121.3756 | 121.5306 | 121.5292 | 61.6657 | -121.7208
669.3906 | 121.7789 | -61.4914 | 60.0952 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0022892 | -0.0016621 | -0.0014849 | 0.064052 | 0.023006 | 0.058804 | -61.5371 | 0.0243 | -61.5909 | 59.9878 | 59.9751 | 59.8653 | -61.5489 | -61.5139 | 0.082776 | -61.6125 | 59.7881 | 59.943 | 59.9417 | -61.6897 | -0.057462 | -0.10741 | -0.04567 | -0.099467 | -0.042005 | -0.1201 | -0.22996 | -0.19832 | -0.30713 | -0.022525 | -0.12113 | 0.077189 | -0.15218 | -0.15356 | 121.4792 | 121.4665 | 121.3567 | 61.5157 | -121.6441 | 121.2795 | 121.4344 | 121.4331 | 61.5742 | -121.7849
671.0781 | 121.8201 | -61.5143 | 60.022 | 1.4211e-13 | -0.0317 | 0.0018589 | 0.063432 | -0.0069633 | 0.054179 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.023647 | 0.058804 | -61.5416 | 0.0243 | -61.5954 | 59.997 | 59.9843 | 59.8698 | -61.5397 | -61.5093 | 0.078197 | -61.6171 | 59.7927 | 59.943 | 59.9417 | -61.6897 | -0.025416 | -0.025013 | -0.02736 | -0.081157 | -0.055741 | -0.037703 | -0.15214 | -0.17543 | -0.22931 | 0.004941 | -0.10282 | 0.07261 | -0.078938 | -0.080315 | 121.5112 | 121.4986 | 121.3841 | 61.5386 | -121.5617 | 121.3069 | 121.4573 | 121.4559 | 61.5925 | -121.7117
672.8438 | 121.756 | -61.5921 | 60.0266 | 1.4211e-13 | -0.031487 | 0.0016453 | 0.063218 | -0.0069633 | 0.054179 | -0.0022892 | -0.0023031 | -0.0014849 | 0.063624 | 0.022793 | 0.059017 | -61.5371 | 0.019721 | -61.5909 | 59.9924 | 59.9797 | 59.8744 | -61.5534 | -61.5139 | 0.082776 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.6943 | 0.038667 | -0.034168 | 0.055038 | 0.001241 | -0.037426 | -0.046858 | -0.15214 | -0.10219 | -0.24304 | 0.078183 | -0.025003 | 0.077189 | -0.088094 | -0.089471 | 121.5845 | 121.5718 | 121.4665 | 61.6118 | -121.58 | 121.3756 | 121.5306 | 121.5292 | 61.6749 | -121.7208
674.5469 | 121.8475 | -61.5463 | 59.9808 | 1.4211e-13 | -0.0317 | 0.0018589 | 0.063432 | -0.0069633 | 0.054392 | -0.01755 | -0.0016621 | -0.0014849 | 0.063624 | 0.022793 | 0.059017 | -61.5325 | 0.0243 | -61.5909 | 59.997 | 59.9843 | 59.8698 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7927 | 59.9476 | 59.9417 | -61.6943 | 0.002049 | 0.016186 | 0.013841 | -0.044535 | -0.046584 | 0.003496 | -0.11094 | -0.14797 | -0.18811 | 0.032407 | -0.070779 | 0.077189 | -0.033161 | -0.039116 | 121.5433 | 121.5306 | 121.4162 | 61.5706 | -121.5251 | 121.339 | 121.4939 | 121.488 | 61.6245 | -121.6751
676.2969 | 121.7834 | -61.5372 | 60.0861 | 1.4211e-13 | -0.031487 | 0.0014317 | 0.063218 | -0.0071769 | 0.054606 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063624 | 0.023006 | 0.059231 | -61.5371 | 0.028878 | -61.5954 | 59.997 | 59.9888 | 59.8607 | -61.5443 | -61.5139 | 0.073618 | -61.6079 | 59.7835 | 59.943 | 59.9417 | -61.7035 | -0.007107 | -0.0891 | 0.000106 | -0.058269 | -0.051162 | -0.097211 | -0.22538 | -0.16628 | -0.30255 | 0.023251 | -0.070778 | 0.095504 | -0.14303 | -0.1444 | 121.5341 | 121.526 | 121.3978 | 61.566 | -121.6303 | 121.3207 | 121.4802 | 121.4788 | 61.6108 | -121.7895
678.0469 | 121.8063 | -61.5326 | 60.054 | 1.4211e-13 | -0.031273 | 0.0014317 | 0.063004 | -0.0067497 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063411 | 0.023006 | 0.059017 | -61.5371 | 0.033457 | -61.5863 | 59.9878 | 59.9888 | 59.8698 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7927 | 59.943 | 59.9417 | -61.6897 | -0.007105 | -0.066213 | -0.004471 | -0.05369 | -0.046585 | -0.065167 | -0.18418 | -0.15712 | -0.26135 | 0.018674 | -0.084512 | 0.07261 | -0.11098 | -0.11236 | 121.5204 | 121.5214 | 121.4024 | 61.566 | -121.5937 | 121.3253 | 121.4756 | 121.4743 | 61.6108 | -121.7437
679.7344 | 121.8658 | -61.5326 | 59.9762 | 1.4211e-13 | -0.031487 | 0.0016453 | 0.063218 | -0.0069633 | 0.054392 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.023006 | 0.058804 | -61.5325 | 0.0243 | -61.6 | 59.9924 | 59.9751 | 59.8698 | -61.5443 | -61.5139 | 0.087354 | -61.6171 | 59.7881 | 59.943 | 59.9417 | -61.6897 | -0.011684 | 0.016186 | 0.000108 | -0.067424 | -0.05574 | -0.001083 | -0.10636 | -0.15712 | -0.18811 | 0.018674 | -0.084512 | 0.07261 | -0.033161 | -0.034538 | 121.525 | 121.5077 | 121.4024 | 61.5569 | -121.5205 | 121.3207 | 121.4756 | 121.4743 | 61.6199 | -121.6659
681.4844 | 121.7972 | -61.5051 | 60.0723 | 1.4211e-13 | -0.0317 | 0.0016453 | 0.063004 | -0.0071769 | 0.054179 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063838 | 0.023006 | 0.059017 | -61.5371 | 0.033457 | -61.5909 | 59.9878 | 59.9843 | 59.8698 | -61.5489 | -61.5185 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9462 | -61.6943 | -0.043729 | -0.084524 | -0.031937 | -0.085734 | -0.042005 | -0.088057 | -0.20249 | -0.18917 | -0.28882 | -0.013371 | -0.11198 | 0.077189 | -0.12929 | -0.12609 | 121.4929 | 121.4894 | 121.375 | 61.5386 | -121.6212 | 121.2886 | 121.4482 | 121.4514 | 61.5833 | -121.7666
683.25 | 121.8521 | -61.4731 | 60.1089 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.063432 | -0.0065361 | 0.054179 | 0.0053413 | -0.0020893 | -0.0012713 | 0.063838 | 0.023006 | 0.058804 | -61.5279 | 0.0243 | -61.5909 | 59.9924 | 59.9843 | 59.8744 | -61.5397 | -61.5185 | 0.073618 | -61.6171 | 59.7881 | 59.943 | 59.9462 | -61.6897 | -0.066615 | -0.11657 | -0.054824 | -0.11778 | -0.051163 | -0.12468 | -0.23453 | -0.21663 | -0.32086 | -0.045415 | -0.14402 | 0.07261 | -0.16591 | -0.16271 | 121.4655 | 121.4574 | 121.3475 | 61.4974 | -121.6486 | 121.2612 | 121.4161 | 121.4193 | 61.5467 | -121.7987
685.0156 | 121.8521 | -61.5372 | 60.0082 | 1.4211e-13 | -0.031487 | 0.0016453 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0016621 | -0.0010577 | 0.064052 | 0.023006 | 0.059231 | -61.5325 | 0.028878 | -61.5954 | 59.9878 | 59.9797 | 59.8698 | -61.5443 | -61.5139 | 0.073618 | -61.6171 | 59.7927 | 59.9476 | 59.9417 | -61.6897 | -0.007107 | -0.020437 | 0.004685 | -0.058269 | -0.051162 | -0.028548 | -0.1384 | -0.15254 | -0.21558 | 0.023251 | -0.079935 | 0.07261 | -0.060627 | -0.066582 | 121.525 | 121.5169 | 121.407 | 61.566 | -121.5525 | 121.3298 | 121.4848 | 121.4788 | 61.6108 | -121.698
686.7812 | 121.8567 | -61.5555 | 59.9716 | 1.4211e-13 | -0.0317 | 0.0012179 | 0.062791 | -0.0067497 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063197 | 0.023006 | 0.058376 | -61.5325 | 0.028878 | -61.5954 | 59.9924 | 59.9797 | 59.8698 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9522 | 59.9462 | -61.6943 | 0.011204 | 0.020763 | 0.022996 | -0.039958 | -0.051162 | 0.008073 | -0.10178 | -0.13881 | -0.18811 | 0.041562 | -0.057045 | 0.081768 | -0.019427 | -0.025383 | 121.5479 | 121.5352 | 121.4253 | 61.5844 | -121.5159 | 121.339 | 121.5077 | 121.5017 | 61.6337 | -121.6659
688.4844 | 121.875 | -61.5463 | 59.967 | 1.4211e-13 | -0.031487 | 0.0014317 | 0.063432 | -0.0067497 | 0.054179 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063411 | 0.02322 | 0.058804 | -61.5279 | 0.038035 | -61.5863 | 59.997 | 59.9888 | 59.8744 | -61.5443 | -61.5093 | 0.082776 | -61.6171 | 59.7881 | 59.9476 | 59.9417 | -61.6897 | 0.002049 | 0.029919 | 0.018419 | -0.039957 | -0.042006 | 0.021808 | -0.092627 | -0.14339 | -0.17896 | 0.036985 | -0.070779 | 0.07261 | -0.019428 | -0.025383 | 121.5433 | 121.5352 | 121.4207 | 61.5844 | -121.5113 | 121.3344 | 121.4939 | 121.488 | 61.6291 | -121.6568
690.2344 | 121.7377 | -61.5143 | 60.1089 | 1.4211e-13 | -0.031273 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.023006 | 0.05859 | -61.5371 | 0.028878 | -61.5909 | 59.9878 | 59.9797 | 59.8653 | -61.5489 | -61.5139 | 0.078197 | -61.6125 | 59.7881 | 59.943 | 59.9371 | -61.6943 | -0.034574 | -0.12114 | -0.022782 | -0.076579 | -0.042005 | -0.12926 | -0.24369 | -0.18001 | -0.32086 | 0.000363 | -0.098244 | 0.081768 | -0.16591 | -0.17187 | 121.5021 | 121.494 | 121.3795 | 61.5432 | -121.6578 | 121.3024 | 121.4573 | 121.4514 | 61.5925 | -121.8032
691.9844 | 121.7972 | -61.5143 | 60.0677 | 1.4211e-13 | -0.0317 | 0.0018589 | 0.063218 | -0.0071769 | 0.054392 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.022793 | 0.05859 | -61.5371 | 0.028878 | -61.5909 | 59.9924 | 59.9751 | 59.8698 | -61.5443 | -61.5139 | 0.078197 | -61.6125 | 59.7835 | 59.9385 | 59.9417 | -61.6897 | -0.029995 | -0.075367 | -0.022782 | -0.076579 | -0.046584 | -0.092636 | -0.19791 | -0.17543 | -0.28424 | 0.000363 | -0.098244 | 0.077189 | -0.12929 | -0.12609 | 121.5067 | 121.4894 | 121.3841 | 61.5432 | -121.612 | 121.2978 | 121.4527 | 121.4559 | 61.5925 | -121.7575
693.7344 | 121.8658 | -61.5189 | 60.0449 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.062791 | -0.0073907 | 0.054179 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.023006 | 0.058804 | -61.5371 | 0.033457 | -61.5863 | 59.9878 | 59.9797 | 59.8653 | -61.5443 | -61.5048 | 0.073618 | -61.6171 | 59.7881 | 59.943 | 59.9371 | -61.6943 | -0.025417 | -0.057058 | -0.018204 | -0.067423 | -0.042006 | -0.065169 | -0.1796 | -0.17543 | -0.25678 | 0.014098 | -0.098245 | 0.077189 | -0.10183 | -0.10778 | 121.5067 | 121.4986 | 121.3841 | 61.5523 | -121.5891 | 121.3069 | 121.4619 | 121.4559 | 61.5925 | -121.7392
695.4219 | 121.8613 | -61.5372 | 59.9808 | 1.4211e-13 | -0.032128 | 0.0016453 | 0.062791 | -0.0067497 | 0.054392 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.023434 | 0.059231 | -61.5279 | 0.019721 | -61.5909 | 60.0015 | 59.9888 | 59.8698 | -61.5489 | -61.5093 | 0.06904 | -61.6171 | 59.7789 | 59.9522 | 59.9371 | -61.6943 | -0.011686 | 0.020764 | 0.009263 | -0.053691 | -0.042005 | 0.008075 | -0.11094 | -0.15712 | -0.20185 | 0.027829 | -0.079935 | 0.077189 | -0.028582 | -0.043695 | 121.5387 | 121.526 | 121.407 | 61.5569 | -121.5296 | 121.3161 | 121.4894 | 121.4742 | 61.6062 | -121.6751
697.1719 | 121.7331 | -61.5738 | 60.0266 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.063004 | -0.0071769 | 0.053751 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.022793 | 0.059017 | -61.5279 | 0.028878 | -61.5863 | 59.9924 | 59.9843 | 59.8653 | -61.5443 | -61.5093 | 0.078197 | -61.6171 | 59.7881 | 59.9476 | 59.9417 | -61.6943 | 0.029515 | -0.034168 | 0.045885 | -0.012491 | -0.042006 | -0.04228 | -0.16129 | -0.1205 | -0.23846 | 0.064451 | -0.043313 | 0.077189 | -0.078937 | -0.084892 | 121.5662 | 121.5581 | 121.439 | 61.6027 | -121.5708 | 121.3619 | 121.5214 | 121.5154 | 61.652 | -121.7208
698.9062 | 121.8658 | -61.5555 | 59.9533 | 1.4211e-13 | -0.031914 | 0.0016453 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.02322 | 0.058804 | -61.5233 | 0.028878 | -61.5863 | 59.9924 | 59.9843 | 59.8698 | -61.5351 | -61.5139 | 0.073618 | -61.6079 | 59.7835 | 59.943 | 59.9417 | -61.6943 | 0.020362 | 0.039074 | 0.032152 | -0.030802 | -0.051164 | 0.030962 | -0.083472 | -0.13881 | -0.1698 | 0.041562 | -0.052467 | 0.086346 | -0.010273 | -0.01165 | 121.5479 | 121.5398 | 121.4253 | 61.5844 | -121.4884 | 121.339 | 121.4985 | 121.4971 | 61.6291 | -121.6476
700.6562 | 121.756 | -61.5509 | 60.0449 | 1.4211e-13 | -0.0317 | 0.0016453 | 0.063004 | -0.0067497 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063624 | 0.022793 | 0.059017 | -61.5325 | 0.028878 | -61.5863 | 59.9878 | 59.9797 | 59.8744 | -61.5397 | -61.5139 | 0.073618 | -61.6125 | 59.7881 | 59.9522 | 59.9417 | -61.6943 | 0.011205 | -0.057058 | 0.018418 | -0.03538 | -0.046585 | -0.065169 | -0.17045 | -0.14339 | -0.25678 | 0.036984 | -0.061623 | 0.081768 | -0.092669 | -0.1032 | 121.5387 | 121.5306 | 121.4253 | 61.5798 | -121.5846 | 121.339 | 121.5031 | 121.4926 | 61.6245 | -121.7392
702.3594 | 121.8704 | -61.4868 | 60.0723 | 1.4211e-13 | -0.031914 | 0.0014317 | 0.063004 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.023006 | 0.05859 | -61.5279 | 0.033457 | -61.5817 | 59.9924 | 59.9888 | 59.8653 | -61.5489 | -61.5093 | 0.078197 | -61.6171 | 59.7881 | 59.9476 | 59.9417 | -61.6989 | -0.06204 | -0.079945 | -0.041091 | -0.094888 | -0.032848 | -0.083478 | -0.20707 | -0.21206 | -0.28424 | -0.022525 | -0.13029 | 0.081768 | -0.12471 | -0.13067 | 121.4792 | 121.4757 | 121.3521 | 61.5203 | -121.6212 | 121.2749 | 121.4344 | 121.4285 | 61.565 | -121.7712
704.1094 | 121.8018 | -61.5509 | 60.0632 | 1.4211e-13 | -0.0317 | 0.0016453 | 0.063218 | -0.0071769 | 0.054392 | -0.01755 | -0.0018757 | -0.0012713 | 0.064052 | 0.022793 | 0.05859 | -61.5233 | 0.028878 | -61.6046 | 59.9878 | 59.9843 | 59.8653 | -61.5443 | -61.5185 | 0.078197 | -61.6079 | 59.7881 | 59.9476 | 59.9417 | -61.6897 | 0.006626 | -0.075368 | 0.027574 | -0.053693 | -0.060319 | -0.078901 | -0.19791 | -0.13881 | -0.27509 | 0.032405 | -0.057045 | 0.081767 | -0.11556 | -0.12151 | 121.5387 | 121.5352 | 121.4162 | 61.5798 | -121.6074 | 121.339 | 121.4985 | 121.4926 | 61.6291 | -121.7529
705.7969 | 121.7468 | -61.5143 | 60.1089 | 1.4211e-13 | -0.031914 | 0.0018589 | 0.063004 | -0.0071769 | 0.054179 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063411 | 0.02322 | 0.058804 | -61.5325 | 0.033457 | -61.5863 | 59.9924 | 59.9751 | 59.8698 | -61.5489 | -61.5093 | 0.078197 | -61.6171 | 59.7835 | 59.943 | 59.9371 | -61.6989 | -0.034574 | -0.11657 | -0.018203 | -0.072001 | -0.037427 | -0.13383 | -0.23911 | -0.18459 | -0.32544 | 0.004941 | -0.10282 | 0.081768 | -0.16591 | -0.17187 | 121.5067 | 121.4894 | 121.3841 | 61.5477 | -121.6578 | 121.2978 | 121.4573 | 121.4514 | 61.5925 | -121.8078
707.5625 | 121.8292 | -61.5692 | 60.0082 | 1.4211e-13 | -0.031914 | 0.0014317 | 0.063432 | -0.0071769 | 0.054179 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.023006 | 0.05859 | -61.5325 | 0.028878 | -61.5954 | 59.9878 | 59.9843 | 59.8653 | -61.5489 | -61.5139 | 0.073618 | -61.6171 | 59.7835 | 59.9568 | 59.9417 | -61.6897 | 0.020358 | -0.020437 | 0.036729 | -0.026225 | -0.046583 | -0.02397 | -0.14298 | -0.1205 | -0.22473 | 0.055295 | -0.047891 | 0.07261 | -0.051469 | -0.066582 | 121.557 | 121.5535 | 121.4345 | 61.5981 | -121.5571 | 121.3527 | 121.526 | 121.5109 | 61.6428 | -121.698
709.3125 | 121.7422 | -61.5829 | 60.0174 | 1.4211e-13 | -0.0317 | 0.0018589 | 0.063432 | -0.0071769 | 0.054179 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063624 | 0.023006 | 0.05859 | -61.5325 | 0.028878 | -61.5863 | 60.0015 | 59.9843 | 59.8744 | -61.5489 | -61.5139 | 0.078197 | -61.6125 | 59.7881 | 59.9476 | 59.9371 | -61.6989 | 0.034091 | -0.015857 | 0.050462 | -0.003336 | -0.037427 | -0.033125 | -0.14298 | -0.11593 | -0.22931 | 0.069028 | -0.029579 | 0.086347 | -0.069782 | -0.080316 | 121.5845 | 121.5672 | 121.4574 | 61.6118 | -121.5663 | 121.371 | 121.5306 | 121.52 | 61.6611 | -121.7163
711.0781 | 121.7422 | -61.5143 | 60.1089 | 1.4211e-13 | -0.031914 | 0.0014317 | 0.063218 | -0.0071769 | 0.054606 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.023006 | 0.058804 | -61.5279 | 0.038035 | -61.5954 | 59.9878 | 59.9934 | 59.8698 | -61.5489 | -61.5093 | 0.073618 | -61.6125 | 59.7881 | 59.943 | 59.9371 | -61.6851 | -0.034574 | -0.12114 | -0.013625 | -0.081157 | -0.046583 | -0.11552 | -0.23911 | -0.17085 | -0.32086 | 0.004941 | -0.098244 | 0.072611 | -0.16591 | -0.17187 | 121.5021 | 121.5077 | 121.3841 | 61.5523 | -121.6578 | 121.3024 | 121.4573 | 121.4514 | 61.5879 | -121.7941
712.8438 | 121.8201 | -61.5875 | 59.967 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.063218 | -0.0069633 | 0.054392 | -0.0099192 | -0.0023031 | -0.0010577 | 0.063624 | 0.023006 | 0.05859 | -61.5325 | 0.033457 | -61.5863 | 59.997 | 59.9888 | 59.8744 | -61.5489 | -61.5093 | 0.06904 | -61.6171 | 59.7835 | 59.9476 | 59.9462 | -61.6943 | 0.038668 | 0.029919 | 0.055039 | 0.001241 | -0.037427 | 0.021808 | -0.092627 | -0.10677 | -0.18353 | 0.078183 | -0.029581 | 0.077189 | -0.019428 | -0.020805 | 121.5845 | 121.5764 | 121.4619 | 61.621 | -121.5159 | 121.371 | 121.5351 | 121.5338 | 61.6566 | -121.6613
714.5312 | 121.8201 | -61.4822 | 60.0861 | 1.4211e-13 | -0.031914 | 0.0016453 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.023006 | 0.058804 | -61.5325 | 0.028878 | -61.5909 | 59.997 | 59.9888 | 59.8744 | -61.5443 | -61.5048 | 0.06904 | -61.6171 | 59.7835 | 59.9385 | 59.9371 | -61.6943 | -0.062038 | -0.0891 | -0.050246 | -0.10862 | -0.046584 | -0.097211 | -0.21165 | -0.21205 | -0.30255 | -0.022523 | -0.13487 | 0.077189 | -0.1476 | -0.14898 | 121.4792 | 121.4711 | 121.3567 | 61.5111 | -121.6303 | 121.2657 | 121.4207 | 121.4193 | 61.5513 | -121.7804
716.2969 | 121.7514 | -61.6058 | 60.0174 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.063004 | -0.0069633 | 0.054606 | -0.0099192 | -0.0020893 | -0.0010577 | 0.064052 | 0.023006 | 0.058804 | -61.5325 | 0.028878 | -61.5863 | 59.997 | 59.9797 | 59.8653 | -61.5397 | -61.5093 | 0.082776 | -61.6171 | 59.7835 | 59.9568 | 59.9417 | -61.6943 | 0.066137 | -0.020435 | 0.07335 | 0.019552 | -0.046585 | -0.037703 | -0.15214 | -0.088459 | -0.23389 | 0.096494 | -0.01127 | 0.077189 | -0.060624 | -0.075737 | 121.6028 | 121.5855 | 121.4711 | 61.6347 | -121.5571 | 121.3893 | 121.5626 | 121.5475 | 61.6886 | -121.7117
718 | 121.8567 | -61.5372 | 59.9762 | 1.4211e-13 | -0.031914 | 0.0016453 | 0.063004 | -0.0067497 | 0.054179 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063838 | 0.02322 | 0.058376 | -61.5279 | 0.033457 | -61.5954 | 59.9924 | 59.9797 | 59.8698 | -61.5489 | -61.5093 | 0.073618 | -61.6125 | 59.7835 | 59.9522 | 59.9462 | -61.6897 | -0.011686 | 0.016186 | 0.009263 | -0.058269 | -0.046583 | 0.003496 | -0.10636 | -0.15254 | -0.19269 | 0.027829 | -0.075356 | 0.077189 | -0.024004 | -0.02996 | 121.5296 | 121.5169 | 121.407 | 61.5706 | -121.5251 | 121.3207 | 121.4894 | 121.4834 | 61.6108 | -121.6659
719.75 | 121.7422 | -61.5051 | 60.0861 | 1.4211e-13 | -0.031914 | 0.0014317 | 0.063218 | -0.0069633 | 0.053751 | 0.0053413 | -0.0018757 | -0.00084406 | 0.063624 | 0.023434 | 0.058163 | -61.5279 | 0.0243 | -61.5954 | 59.9878 | 59.9797 | 59.8698 | -61.5489 | -61.5093 | 0.064461 | -61.6079 | 59.7835 | 59.9476 | 59.9417 | -61.6851 | -0.043729 | -0.098257 | -0.02278 | -0.090312 | -0.046583 | -0.10637 | -0.21622 | -0.18001 | -0.30255 | -0.004214 | -0.10282 | 0.077189 | -0.13845 | -0.1444 | 121.4929 | 121.4848 | 121.375 | 61.5294 | -121.6349 | 121.2886 | 121.4527 | 121.4468 | 61.5696 | -121.7712
721.5 | 121.7926 | -61.5463 | 60.022 | 1.4211e-13 | -0.032342 | 0.0016453 | 0.063004 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063197 | 0.023006 | 0.059017 | -61.5279 | 0.028878 | -61.5863 | 59.9924 | 59.9888 | 59.8698 | -61.5443 | -61.5139 | 0.073618 | -61.6171 | 59.7881 | 59.9568 | 59.9371 | -61.6943 | 0.002049 | -0.029591 | 0.018419 | -0.039957 | -0.042006 | -0.033124 | -0.15214 | -0.14797 | -0.23389 | 0.032407 | -0.070779 | 0.077189 | -0.065202 | -0.084894 | 121.5387 | 121.5352 | 121.4162 | 61.5752 | -121.5662 | 121.3344 | 121.5031 | 121.4834 | 61.6199 | -121.7163
723.2656 | 121.8338 | -61.5189 | 60.0082 | 1.4211e-13 | -0.031914 | 0.0014317 | 0.063218 | -0.0067497 | 0.054179 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.023006 | 0.05859 | -61.5279 | 0.028878 | -61.5909 | 59.9924 | 59.9843 | 59.8698 | -61.5397 | -61.5048 | 0.078197 | -61.6079 | 59.7835 | 59.9476 | 59.9417 | -61.6897 | -0.020838 | -0.015858 | -0.009047 | -0.072001 | -0.051163 | -0.02397 | -0.1384 | -0.17086 | -0.22473 | 0.014098 | -0.089088 | 0.081767 | -0.060627 | -0.066582 | 121.5112 | 121.5031 | 121.3887 | 61.5477 | -121.5479 | 121.3024 | 121.4665 | 121.4605 | 61.5971 | -121.698
724.9531 | 121.8796 | -61.5692 | 59.9487 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.063432 | -0.0071769 | 0.054179 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.022793 | 0.059017 | -61.5279 | 0.028878 | -61.5909 | 59.9832 | 59.9843 | 59.8653 | -61.5443 | -61.5048 | 0.082776 | -61.6217 | 59.7881 | 59.9522 | 59.9462 | -61.7035 | 0.024937 | 0.034495 | 0.041307 | -0.021647 | -0.046584 | 0.03554 | -0.083473 | -0.13424 | -0.16064 | 0.064452 | -0.05247 | 0.081768 | 0.003462 | -0.002494 | 121.5524 | 121.5535 | 121.4345 | 61.5981 | -121.493 | 121.3573 | 121.5214 | 121.5155 | 61.652 | -121.6522
726.7031 | 121.7972 | -61.5463 | 60.0632 | 1.4211e-13 | -0.031914 | 0.0020727 | 0.063432 | -0.0071769 | 0.054179 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063411 | 0.023434 | 0.059017 | -61.5279 | 0.0243 | -61.5863 | 59.9924 | 59.9888 | 59.8698 | -61.5489 | -61.5093 | 0.064461 | -61.6125 | 59.7881 | 59.9476 | 59.9417 | -61.6943 | -0.00253 | -0.070789 | 0.018419 | -0.039957 | -0.037427 | -0.074322 | -0.19333 | -0.14797 | -0.27509 | 0.036985 | -0.0662 | 0.081768 | -0.11556 | -0.12151 | 121.5387 | 121.5352 | 121.4162 | 61.5706 | -121.612 | 121.3344 | 121.4939 | 121.488 | 61.6108 | -121.7575
728.4531 | 121.8246 | -61.5326 | 59.9945 | 1.4211e-13 | -0.032342 | 0.0018589 | 0.063218 | -0.0065361 | 0.054392 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063624 | 0.02322 | 0.059231 | -61.5279 | 0.028878 | -61.5954 | 59.997 | 59.9888 | 59.8698 | -61.5397 | -61.5139 | 0.078197 | -61.6171 | 59.7881 | 59.9476 | 59.9371 | -61.6943 | -0.007105 | 0.002453 | 0.004686 | -0.062846 | -0.055741 | -0.005658 | -0.12467 | -0.1617 | -0.20642 | 0.018674 | -0.084512 | 0.077189 | -0.046894 | -0.057428 | 121.5296 | 121.5214 | 121.4024 | 61.5615 | -121.5342 | 121.3207 | 121.4802 | 121.4697 | 61.6108 | -121.6888
730.1406 | 121.7743 | -61.5646 | 60.022 | 1.4211e-13 | -0.0317 | 0.0014317 | 0.063432 | -0.0069633 | 0.054179 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.023006 | 0.05859 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.9888 | 59.8698 | -61.5443 | -61.5048 | 0.082776 | -61.6171 | 59.7835 | 59.9476 | 59.9371 | -61.6989 | 0.020359 | -0.025013 | 0.032151 | -0.030803 | -0.051162 | -0.033124 | -0.15214 | -0.13424 | -0.23847 | 0.059874 | -0.052469 | 0.081768 | -0.07436 | -0.084894 | 121.5616 | 121.5535 | 121.4345 | 61.5889 | -121.5662 | 121.3481 | 121.5122 | 121.5017 | 61.6474 | -121.7208
731.8906 | 121.8887 | -61.5005 | 60.0586 | 1.4211e-13 | -0.031914 | 0.0016453 | 0.063432 | -0.0071769 | 0.054392 | -0.01755 | -0.0018757 | -0.0012713 | 0.063838 | 0.02322 | 0.05859 | -61.5325 | 0.019721 | -61.5954 | 59.997 | 59.9843 | 59.8744 | -61.5443 | -61.5185 | 0.073618 | -61.6079 | 59.7881 | 59.9613 | 59.9417 | -61.6989 | -0.043728 | -0.061634 | -0.031936 | -0.09489 | -0.051162 | -0.074324 | -0.18418 | -0.19832 | -0.27051 | -0.017949 | -0.1074 | 0.090925 | -0.097245 | -0.11694 | 121.4975 | 121.4848 | 121.375 | 61.5203 | -121.6029 | 121.2886 | 121.4619 | 121.4422 | 61.5742 | -121.7575
733.6562 | 121.7422 | -61.5326 | 60.1089 | 1.4211e-13 | -0.032342 | 0.0018589 | 0.063004 | -0.0069633 | 0.054179 | 0.0053413 | -0.0018757 | -0.0012713 | 0.063624 | 0.02322 | 0.05859 | -61.5233 | 0.0243 | -61.5954 | 59.997 | 59.9843 | 59.8698 | -61.5397 | -61.5048 | 0.078197 | -61.6171 | 59.7881 | 59.9568 | 59.9462 | -61.6943 | -0.007105 | -0.11199 | 0.009264 | -0.062846 | -0.055741 | -0.12468 | -0.23911 | -0.1617 | -0.32086 | 0.027831 | -0.084512 | 0.077189 | -0.15218 | -0.16271 | 121.5296 | 121.5169 | 121.4024 | 61.5569 | -121.6486 | 121.3207 | 121.4894 | 121.4788 | 61.6108 | -121.8032
735.3906 | 121.7422 | -61.5005 | 60.0998 | 1.4211e-13 | -0.032128 | 0.0010043 | 0.063004 | -0.0071769 | 0.054392 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.023434 | 0.05859 | -61.5279 | 0.028878 | -61.5954 | 59.997 | 59.9888 | 59.879 | -61.5443 | -61.5093 | 0.078197 | -61.6171 | 59.7881 | 59.9522 | 59.9417 | -61.6897 | -0.043728 | -0.10283 | -0.027358 | -0.09489 | -0.051162 | -0.11094 | -0.2208 | -0.18917 | -0.31171 | -0.008792 | -0.11656 | 0.07261 | -0.1476 | -0.15813 | 121.4975 | 121.4894 | 121.3795 | 61.5294 | -121.6441 | 121.2886 | 121.4527 | 121.4422 | 61.5787 | -121.7895
737.0781 | 121.9025 | -61.4777 | 60.0494 | 1.4211e-13 | -0.031914 | 0.0012179 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063624 | 0.02322 | 0.058804 | -61.5371 | 0.028878 | -61.5909 | 59.9924 | 59.9888 | 59.879 | -61.5443 | -61.5093 | 0.073618 | -61.6079 | 59.7927 | 59.9522 | 59.9462 | -61.6943 | -0.066616 | -0.057056 | -0.059403 | -0.1132 | -0.046584 | -0.060589 | -0.17045 | -0.21663 | -0.25677 | -0.03168 | -0.13029 | 0.086346 | -0.097246 | -0.1032 | 121.47 | 121.4665 | 121.3567 | 61.5065 | -121.5937 | 121.2703 | 121.4299 | 121.4239 | 61.5513 | -121.7437
738.8438 | 121.8292 | -61.5601 | 59.9991 | 1.4211e-13 | -0.032342 | 0.0014317 | 0.062791 | -0.0067497 | 0.054179 | -0.0099192 | -0.0018757 | -0.0014849 | 0.064052 | 0.023647 | 0.05859 | -61.5279 | 0.0243 | -61.5954 | 59.9924 | 59.9888 | 59.8744 | -61.5397 | -61.5139 | 0.073618 | -61.6079 | 59.7881 | 59.9476 | 59.9462 | -61.6943 | 0.020361 | -0.006702 | 0.032152 | -0.03538 | -0.055741 | -0.010235 | -0.12467 | -0.13423 | -0.211 | 0.04614 | -0.047889 | 0.086346 | -0.051471 | -0.052848 | 121.5524 | 121.5489 | 121.4345 | 61.5844 | -121.5388 | 121.3481 | 121.5077 | 121.5063 | 61.6337 | -121.6934
740.5938 | 121.7514 | -61.5738 | 60.0357 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.063218 | -0.0069633 | 0.054392 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.02322 | 0.058804 | -61.5325 | 0.0243 | -61.5954 | 59.997 | 59.9888 | 59.8744 | -61.5443 | -61.5093 | 0.073618 | -61.6171 | 59.7881 | 59.9476 | 59.9462 | -61.6943 | 0.029515 | -0.038746 | 0.041307 | -0.021647 | -0.051162 | -0.046857 | -0.16129 | -0.1205 | -0.24762 | 0.064451 | -0.043313 | 0.077189 | -0.088093 | -0.08947 | 121.5708 | 121.5626 | 121.4482 | 61.5981 | -121.58 | 121.3619 | 121.5214 | 121.52 | 61.6474 | -121.73
742.2812 | 121.7972 | -61.5921 | 59.9945 | 1.4211e-13 | -0.031914 | 0.0016453 | 0.063432 | -0.0071769 | 0.053965 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063624 | 0.023434 | 0.05859 | -61.5233 | 0.0243 | -61.5909 | 59.997 | 59.9888 | 59.879 | -61.5443 | -61.5093 | 0.078197 | -61.6079 | 59.7835 | 59.9476 | 59.9462 | -61.6943 | 0.047825 | 0.002453 | 0.068773 | 0.001241 | -0.046584 | -0.005658 | -0.11551 | -0.10219 | -0.211 | 0.082761 | -0.015846 | 0.086346 | -0.046894 | -0.048271 | 121.5891 | 121.581 | 121.4711 | 61.6164 | -121.5388 | 121.3756 | 121.5397 | 121.5383 | 61.6703 | -121.6888
744.0312 | 121.756 | -61.5555 | 60.0449 | 1.4211e-13 | -0.032342 | 0.0014317 | 0.063218 | -0.0069633 | 0.053965 | -0.0099192 | -0.0020893 | -0.0014849 | 0.063838 | 0.023434 | 0.058804 | -61.5279 | 0.019721 | -61.5817 | 59.997 | 59.9843 | 59.8744 | -61.5443 | -61.5048 | 0.073618 | -61.6171 | 59.7927 | 59.9522 | 59.9417 | -61.6943 | 0.011204 | -0.047901 | 0.027574 | -0.026223 | -0.037427 | -0.060591 | -0.17045 | -0.13881 | -0.2522 | 0.050719 | -0.061624 | 0.077189 | -0.092669 | -0.1032 | 121.5524 | 121.5398 | 121.4299 | 61.5752 | -121.5891 | 121.3481 | 121.5077 | 121.4971 | 61.6291 | -121.7392
745.7812 | 121.8155 | -61.5189 | 60.0082 | 1.4211e-13 | -0.032128 | 0.0016453 | 0.063004 | -0.0069633 | 0.053751 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063411 | 0.023647 | 0.059017 | -61.5371 | 0.028878 | -61.5863 | 59.9878 | 59.9843 | 59.8744 | -61.5351 | -61.5048 | 0.064461 | -61.6217 | 59.7881 | 59.9568 | 59.9371 | -61.6897 | -0.016259 | -0.020437 | -0.018204 | -0.067423 | -0.051164 | -0.02397 | -0.13383 | -0.17086 | -0.22015 | 0.014098 | -0.10282 | 0.068031 | -0.051469 | -0.071161 | 121.5067 | 121.5031 | 121.3933 | 61.5477 | -121.5434 | 121.3069 | 121.4756 | 121.4559 | 61.5833 | -121.698
747.4844 | 121.7422 | -61.5738 | 60.022 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0023031 | -0.0014849 | 0.063411 | 0.023006 | 0.05859 | -61.5233 | 0.028878 | -61.5863 | 59.997 | 59.9888 | 59.879 | -61.5397 | -61.5048 | 0.082776 | -61.6171 | 59.7881 | 59.9522 | 59.9371 | -61.6897 | 0.034094 | -0.025013 | 0.050463 | -0.012491 | -0.046585 | -0.033124 | -0.14298 | -0.11592 | -0.23389 | 0.06903 | -0.043313 | 0.07261 | -0.069781 | -0.084894 | 121.5708 | 121.5626 | 121.4528 | 61.6027 | -121.5617 | 121.3619 | 121.526 | 121.5109 | 61.6566 | -121.7117
749.2344 | 121.8704 | -61.4822 | 60.0357 | 1.4211e-13 | -0.032128 | 0.0016453 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0020893 | -0.0010577 | 0.063411 | 0.02322 | 0.058804 | -61.5325 | 0.033457 | -61.5909 | 59.9878 | 59.9843 | 59.8836 | -61.5443 | -61.5139 | 0.078197 | -61.6171 | 59.7881 | 59.9568 | 59.9462 | -61.6989 | -0.062038 | -0.047903 | -0.050246 | -0.10862 | -0.046584 | -0.051436 | -0.15213 | -0.21663 | -0.24762 | -0.03168 | -0.13487 | 0.081768 | -0.078935 | -0.08947 | 121.47 | 121.4665 | 121.3658 | 61.5157 | -121.58 | 121.2703 | 121.439 | 121.4285 | 61.5604 | -121.7346
750.9844 | 121.7468 | -61.4914 | 60.1273 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063624 | 0.023006 | 0.058804 | -61.5371 | 0.0243 | -61.6 | 59.9878 | 59.9934 | 59.8836 | -61.5443 | -61.5093 | 0.073618 | -61.6079 | 59.7881 | 59.9522 | 59.9462 | -61.6943 | -0.052883 | -0.13945 | -0.04567 | -0.10862 | -0.05574 | -0.13383 | -0.24369 | -0.2029 | -0.33917 | -0.017947 | -0.11655 | 0.086346 | -0.17507 | -0.18102 | 121.4792 | 121.4848 | 121.375 | 61.5157 | -121.6715 | 121.2795 | 121.4436 | 121.4376 | 61.565 | -121.8216
752.75 | 121.875 | -61.4914 | 60.054 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063624 | 0.02322 | 0.058804 | -61.5279 | 0.0243 | -61.5863 | 60.0015 | 59.9888 | 59.8653 | -61.5351 | -61.5093 | 0.073618 | -61.6125 | 59.7972 | 59.9476 | 59.9417 | -61.6943 | -0.043725 | -0.052478 | -0.036513 | -0.094889 | -0.051164 | -0.065167 | -0.18876 | -0.2029 | -0.25677 | -0.017947 | -0.12113 | 0.081768 | -0.1064 | -0.11236 | 121.4929 | 121.4802 | 121.3567 | 61.5157 | -121.5891 | 121.2886 | 121.439 | 121.4331 | 61.565 | -121.7483
754.5 | 121.8887 | -61.5692 | 59.9442 | 1.4211e-13 | -0.031914 | 0.0014317 | 0.063004 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0010577 | 0.064052 | 0.022793 | 0.059231 | -61.5279 | 0.019721 | -61.5954 | 59.9924 | 59.9934 | 59.8836 | -61.5351 | -61.5048 | 0.082776 | -61.6034 | 59.7927 | 59.9522 | 59.9371 | -61.6897 | 0.034095 | 0.048229 | 0.041307 | -0.026225 | -0.06032 | 0.049275 | -0.060581 | -0.1205 | -0.15149 | 0.064452 | -0.034155 | 0.086346 | 0.008039 | -0.007074 | 121.5616 | 121.5626 | 121.4528 | 61.5889 | -121.4793 | 121.3619 | 121.5214 | 121.5063 | 61.652 | -121.6339
756.2656 | 121.8704 | -61.5051 | 60.0586 | 1.4211e-13 | -0.032128 | 0.0018589 | 0.063218 | -0.0069633 | 0.053965 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063411 | 0.02322 | 0.059017 | -61.5233 | 0.028878 | -61.5954 | 59.9924 | 59.9843 | 59.8882 | -61.5397 | -61.5002 | 0.073618 | -61.6217 | 59.7881 | 59.9476 | 59.9508 | -61.6989 | -0.034571 | -0.066212 | -0.018202 | -0.090312 | -0.055741 | -0.074324 | -0.17044 | -0.19375 | -0.27051 | 0.004944 | -0.11656 | 0.077189 | -0.11098 | -0.10778 | 121.4975 | 121.4894 | 121.3933 | 61.534 | -121.5983 | 121.2932 | 121.4527 | 121.4559 | 61.5787 | -121.7575
757.9688 | 121.7422 | -61.5921 | 60.0266 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.062791 | -0.0069633 | 0.054179 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.02322 | 0.05859 | -61.5233 | 0.033457 | -61.5909 | 60.0015 | 59.9888 | 59.8836 | -61.5443 | -61.5093 | 0.078197 | -61.6079 | 59.7881 | 59.9522 | 59.9417 | -61.6989 | 0.047825 | -0.025012 | 0.068773 | 0.001241 | -0.046584 | -0.037701 | -0.14298 | -0.10677 | -0.23846 | 0.082761 | -0.015846 | 0.090925 | -0.074358 | -0.084892 | 121.5936 | 121.581 | 121.4757 | 61.6256 | -121.5708 | 121.3802 | 121.5443 | 121.5338 | 61.6703 | -121.7254
759.7188 | 121.8521 | -61.5097 | 60.022 | 1.4211e-13 | -0.032342 | 0.0014317 | 0.063004 | -0.0069633 | 0.054392 | -0.0099192 | -0.0018757 | -0.00084406 | 0.063624 | 0.023006 | 0.058804 | -61.5233 | 0.028878 | -61.5954 | 59.9924 | 59.9888 | 59.8698 | -61.5397 | -61.5048 | 0.078197 | -61.6034 | 59.7881 | 59.9522 | 59.9462 | -61.7035 | -0.029993 | -0.029591 | -0.013624 | -0.085734 | -0.055741 | -0.033124 | -0.15214 | -0.19375 | -0.23389 | 0.004943 | -0.093664 | 0.10008 | -0.069781 | -0.075737 | 121.5021 | 121.4986 | 121.3795 | 61.5386 | -121.5617 | 121.2978 | 121.4619 | 121.4559 | 61.5879 | -121.7254
761.4688 | 121.8842 | -61.5509 | 59.9487 | 1.4211e-13 | -0.032342 | 0.0020727 | 0.063432 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.02322 | 0.058804 | -61.5233 | 0.0243 | -61.6 | 59.997 | 59.9934 | 59.8744 | -61.5397 | -61.5048 | 0.06904 | -61.6125 | 59.7927 | 59.9522 | 59.9462 | -61.6897 | 0.011205 | 0.04823 | 0.027574 | -0.049114 | -0.060319 | 0.044698 | -0.074316 | -0.13881 | -0.15607 | 0.046141 | -0.061623 | 0.077189 | 0.003462 | -0.002494 | 121.5479 | 121.5443 | 121.4253 | 61.5752 | -121.4884 | 121.3436 | 121.5031 | 121.4971 | 61.6199 | -121.6384
763.1719 | 121.7514 | -61.5051 | 60.0952 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063411 | 0.02322 | 0.05859 | -61.5371 | 0.028878 | -61.5954 | 60.0015 | 59.9888 | 59.8744 | -61.5397 | -61.5093 | 0.078197 | -61.6125 | 59.7972 | 59.9476 | 59.9417 | -61.6943 | -0.034571 | -0.093677 | -0.031937 | -0.090312 | -0.055741 | -0.10637 | -0.2208 | -0.18917 | -0.29797 | -0.004214 | -0.1074 | 0.081768 | -0.1476 | -0.15356 | 121.5067 | 121.494 | 121.3795 | 61.534 | -121.6349 | 121.3024 | 121.4527 | 121.4468 | 61.5833 | -121.7895
764.9219 | 121.788 | -61.5326 | 60.0494 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.063218 | -0.0071769 | 0.054392 | -0.0022892 | -0.0020893 | -0.0014849 | 0.063411 | 0.02322 | 0.058804 | -61.5279 | 0.033457 | -61.5954 | 59.997 | 59.9888 | 59.879 | -61.5534 | -61.5048 | 0.078197 | -61.6171 | 59.7835 | 59.9522 | 59.9417 | -61.6943 | -0.020842 | -0.052478 | 0.004686 | -0.062846 | -0.042004 | -0.060589 | -0.17045 | -0.1617 | -0.26593 | 0.027831 | -0.084512 | 0.077189 | -0.097246 | -0.10778 | 121.5296 | 121.5214 | 121.4116 | 61.566 | -121.6029 | 121.3161 | 121.4848 | 121.4743 | 61.6108 | -121.7437
766.6719 | 121.8246 | -61.5417 | 60.0128 | 1.4211e-13 | -0.032128 | 0.0014317 | 0.063218 | -0.0073907 | 0.054179 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063624 | 0.024075 | 0.058804 | -61.5279 | 0.033457 | -61.5954 | 59.997 | 59.998 | 59.879 | -61.5397 | -61.5093 | 0.073618 | -61.6034 | 59.7881 | 59.9476 | 59.9417 | -61.6897 | 0.00205 | -0.015857 | 0.013841 | -0.053691 | -0.055741 | -0.01481 | -0.13382 | -0.14797 | -0.22473 | 0.032407 | -0.061621 | 0.086346 | -0.065204 | -0.071159 | 121.5387 | 121.5398 | 121.4207 | 61.5752 | -121.5525 | 121.3298 | 121.4894 | 121.4834 | 61.6154 | -121.7025
768.4219 | 121.875 | -61.5509 | 59.9716 | 1.4211e-13 | -0.032128 | 0.0016453 | 0.063218 | -0.0071769 | 0.054392 | -0.01755 | -0.0016621 | -0.0010577 | 0.063624 | 0.023006 | 0.058804 | -61.5279 | 0.0243 | -61.5954 | 60.0061 | 59.9888 | 59.879 | -61.5351 | -61.5048 | 0.073618 | -61.6079 | 59.7881 | 59.9613 | 59.9462 | -61.6943 | 0.015784 | 0.034498 | 0.022996 | -0.044536 | -0.06032 | 0.01723 | -0.092626 | -0.14339 | -0.18353 | 0.046141 | -0.057045 | 0.086346 | -0.01027 | -0.025383 | 121.557 | 121.5398 | 121.4299 | 61.5752 | -121.5067 | 121.339 | 121.5123 | 121.4971 | 61.6245 | -121.6659
770.1094 | 121.8338 | -61.5097 | 60.0174 | 1.4211e-13 | -0.032342 | 0.0016453 | 0.063218 | -0.0069633 | 0.054392 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.023434 | 0.059017 | -61.5279 | 0.033457 | -61.5954 | 60.0015 | 59.998 | 59.879 | -61.5397 | -61.5093 | 0.078197 | -61.6079 | 59.7881 | 59.9568 | 59.9417 | -61.6989 | -0.029993 | -0.015857 | -0.018202 | -0.085734 | -0.055741 | -0.019388 | -0.1384 | -0.18917 | -0.22931 | 0.000364 | -0.098243 | 0.090925 | -0.060624 | -0.075737 | 121.5112 | 121.5077 | 121.3887 | 61.5432 | -121.5571 | 121.2978 | 121.4665 | 121.4514 | 61.5879 | -121.7163
771.8594 | 121.8338 | -61.5372 | 60.0266 | 1.4211e-13 | -0.032555 | 0.0012179 | 0.063218 | -0.0071769 | 0.053965 | -0.01755 | -0.0014485 | -0.0010577 | 0.063624 | 0.023647 | 0.058804 | -61.5279 | 0.0243 | -61.5909 | 59.997 | 59.9934 | 59.8836 | -61.5443 | -61.5093 | 0.078197 | -61.6125 | 59.7927 | 59.9476 | 59.9462 | -61.6989 | -0.007107 | -0.02959 | 0.009263 | -0.053691 | -0.046584 | -0.033122 | -0.14298 | -0.1617 | -0.23389 | 0.027829 | -0.075356 | 0.086347 | -0.078937 | -0.080314 | 121.5341 | 121.5306 | 121.4207 | 61.5615 | -121.5708 | 121.3298 | 121.4848 | 121.4834 | 61.6154 | -121.7254
773.5469 | 121.756 | -61.5189 | 60.0952 | 1.4211e-13 | -0.032128 | 0.0018589 | 0.063432 | -0.0071769 | 0.054179 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063624 | 0.02322 | 0.05859 | -61.5279 | 0.028878 | -61.5909 | 59.997 | 59.9934 | 59.879 | -61.5443 | -61.5093 | 0.06904 | -61.6079 | 59.7927 | 59.9522 | 59.9462 | -61.6989 | -0.025417 | -0.098255 | -0.009047 | -0.072001 | -0.046584 | -0.10179 | -0.21622 | -0.18001 | -0.30255 | 0.009519 | -0.089088 | 0.090925 | -0.14302 | -0.14898 | 121.5158 | 121.5123 | 121.3979 | 61.5477 | -121.6395 | 121.3115 | 121.4711 | 121.4651 | 61.5879 | -121.7941
775.2969 | 121.875 | -61.5509 | 59.9442 | 1.4211e-13 | -0.032555 | 0.0016453 | 0.063432 | -0.0073907 | 0.053965 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063411 | 0.023434 | 0.05859 | -61.5233 | 0.0243 | -61.5909 | 59.9924 | 59.9888 | 59.8836 | -61.5443 | -61.5048 | 0.073618 | -61.6125 | 59.7927 | 59.9659 | 59.9371 | -61.6943 | 0.006626 | 0.048229 | 0.027574 | -0.039958 | -0.046584 | 0.044696 | -0.060581 | -0.14339 | -0.15149 | 0.046141 | -0.061623 | 0.081768 | 0.021775 | -0.007074 | 121.5433 | 121.5398 | 121.4345 | 61.5752 | -121.4884 | 121.3436 | 121.5168 | 121.488 | 61.6245 | -121.6384
776.9844 | 121.7377 | -61.6013 | 60.0494 | 1.4211e-13 | -0.032342 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063411 | 0.023006 | 0.05859 | -61.5325 | 0.019721 | -61.5863 | 59.997 | 59.9888 | 59.879 | -61.5443 | -61.5002 | 0.078197 | -61.6125 | 59.7927 | 59.9613 | 59.9554 | -61.7035 | 0.05698 | -0.052478 | 0.068772 | 0.014974 | -0.042006 | -0.060589 | -0.17045 | -0.1022 | -0.25677 | 0.10107 | -0.011269 | 0.090926 | -0.088089 | -0.094045 | 121.5982 | 121.5901 | 121.4802 | 61.621 | -121.5937 | 121.3939 | 121.5626 | 121.5566 | 61.6795 | -121.7529
778.7344 | 121.788 | -61.528 | 60.0449 | 1.4211e-13 | -0.032128 | 0.0018589 | 0.063432 | -0.0071769 | 0.054179 | -0.01755 | -0.0018757 | -0.0010577 | 0.063838 | 0.023434 | 0.058804 | -61.5187 | 0.028878 | -61.5954 | 59.997 | 59.9843 | 59.8836 | -61.5397 | -61.5139 | 0.078197 | -61.6125 | 59.7881 | 59.9659 | 59.9417 | -61.6943 | -0.011683 | -0.047901 | 0.009265 | -0.067424 | -0.055741 | -0.060591 | -0.16129 | -0.16628 | -0.25678 | 0.014096 | -0.084511 | 0.081768 | -0.078933 | -0.1032 | 121.525 | 121.5123 | 121.4116 | 61.5569 | -121.5846 | 121.3161 | 121.4939 | 121.4697 | 61.6062 | -121.7392
780.4844 | 121.7743 | -61.5234 | 60.0998 | 1.4211e-13 | -0.032555 | 0.0016453 | 0.063004 | -0.0071769 | 0.054179 | -0.0099192 | -0.0020893 | -0.0012713 | 0.064052 | 0.023006 | 0.059017 | -61.5279 | 0.0243 | -61.5909 | 60.0015 | 59.9843 | 59.8836 | -61.5443 | -61.5048 | 0.082776 | -61.6125 | 59.7972 | 59.9613 | 59.9371 | -61.6943 | -0.02084 | -0.098254 | -0.00447 | -0.067424 | -0.046584 | -0.11552 | -0.21622 | -0.17086 | -0.30255 | 0.018675 | -0.089089 | 0.081768 | -0.13844 | -0.16271 | 121.525 | 121.5077 | 121.407 | 61.5477 | -121.6441 | 121.3207 | 121.4848 | 121.4605 | 61.6062 | -121.7941
782.1719 | 121.8292 | -61.5051 | 60.054 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0069633 | 0.053965 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063624 | 0.023647 | 0.058804 | -61.5279 | 0.028878 | -61.5954 | 60.0015 | 59.9888 | 59.8744 | -61.5305 | -61.5048 | 0.078197 | -61.6171 | 59.7972 | 59.9613 | 59.9508 | -61.7035 | -0.025413 | -0.052478 | -0.02278 | -0.090312 | -0.064899 | -0.065167 | -0.1796 | -0.19832 | -0.25677 | 0.000365 | -0.11198 | 0.086347 | -0.092667 | -0.1032 | 121.5067 | 121.494 | 121.3795 | 61.534 | -121.5846 | 121.3024 | 121.4665 | 121.4559 | 61.5833 | -121.7575
783.9375 | 121.8338 | -61.5372 | 59.9991 | 1.4211e-13 | -0.032342 | 0.0018589 | 0.063218 | -0.0069633 | 0.053751 | -0.01755 | -0.0018757 | -0.00084406 | 0.063624 | 0.023647 | 0.058804 | -61.5233 | 0.028878 | -61.5863 | 59.997 | 59.9888 | 59.879 | -61.5351 | -61.5002 | 0.06904 | -61.6079 | 59.7881 | 59.9613 | 59.9417 | -61.7035 | 0.002051 | -0.002124 | 0.013841 | -0.049113 | -0.051164 | -0.010235 | -0.12009 | -0.16628 | -0.211 | 0.036987 | -0.070778 | 0.095504 | -0.037735 | -0.057426 | 121.5341 | 121.526 | 121.4162 | 61.566 | -121.5342 | 121.3253 | 121.4985 | 121.4788 | 61.6062 | -121.7025
785.7031 | 121.7606 | -61.5005 | 60.0815 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063004 | -0.0071769 | 0.054179 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.023434 | 0.05859 | -61.5233 | 0.0243 | -61.5954 | 59.9924 | 59.9934 | 59.8744 | -61.5397 | -61.5002 | 0.06904 | -61.6079 | 59.7881 | 59.9659 | 59.9417 | -61.6943 | -0.039149 | -0.0891 | -0.02278 | -0.09489 | -0.055741 | -0.088054 | -0.20707 | -0.19374 | -0.2934 | 0.000366 | -0.1074 | 0.086346 | -0.11555 | -0.13982 | 121.4929 | 121.494 | 121.375 | 61.5248 | -121.6212 | 121.2886 | 121.4665 | 121.4422 | 61.5696 | -121.7758
787.4375 | 121.7514 | -61.4914 | 60.0998 | 1.4211e-13 | -0.032769 | 0.0018589 | 0.063645 | -0.0073907 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.023647 | 0.05859 | -61.5187 | 0.019721 | -61.5863 | 59.997 | 59.9934 | 59.8836 | -61.5397 | -61.5048 | 0.06904 | -61.5988 | 59.7789 | 59.9613 | 59.9462 | -61.6989 | -0.048304 | -0.10283 | -0.027356 | -0.094889 | -0.046585 | -0.10636 | -0.21622 | -0.20748 | -0.32086 | -0.013368 | -0.1074 | 0.10008 | -0.13844 | -0.15356 | 121.4884 | 121.4848 | 121.375 | 61.5111 | -121.6395 | 121.2703 | 121.4527 | 121.4376 | 61.5604 | -121.7987
789.125 | 121.8658 | -61.5646 | 59.9945 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0071769 | 0.054179 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.023434 | 0.05859 | -61.5233 | 0.033457 | -61.5863 | 60.0015 | 59.998 | 59.8836 | -61.526 | -61.5002 | 0.06904 | -61.6034 | 59.7972 | 59.9568 | 59.9462 | -61.6943 | 0.038675 | 0.007031 | 0.041307 | -0.021647 | -0.060322 | 0.0035 | -0.11093 | -0.12966 | -0.19727 | 0.064453 | -0.038733 | 0.090925 | -0.037736 | -0.048271 | 121.5662 | 121.5626 | 121.4482 | 61.5981 | -121.5205 | 121.3619 | 121.5214 | 121.5109 | 61.6337 | -121.6888
790.875 | 121.7697 | -61.528 | 60.0677 | 1.4211e-13 | -0.032555 | 0.0016453 | 0.063004 | -0.0071769 | 0.054392 | -0.0022892 | -0.0020893 | -0.0010577 | 0.064052 | 0.023647 | 0.058804 | -61.5279 | 0.033457 | -61.5954 | 60.0015 | 59.9888 | 59.8882 | -61.5351 | -61.5002 | 0.073618 | -61.6079 | 59.7972 | 59.9613 | 59.9417 | -61.6989 | -0.007104 | -0.066211 | 0.000108 | -0.067424 | -0.06032 | -0.0789 | -0.1796 | -0.17086 | -0.27051 | 0.027832 | -0.079933 | 0.090925 | -0.1064 | -0.12609 | 121.5296 | 121.5169 | 121.4162 | 61.5615 | -121.6029 | 121.3253 | 121.4894 | 121.4697 | 61.6016 | -121.7666
792.5625 | 121.8018 | -61.5005 | 60.0769 | 1.4211e-13 | -0.032555 | 0.0016453 | 0.062791 | -0.0071769 | 0.053965 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063411 | 0.023647 | 0.058804 | -61.5187 | 0.0243 | -61.5817 | 60.0015 | 59.9934 | 59.879 | -61.5397 | -61.5048 | 0.073618 | -61.5988 | 59.7927 | 59.9522 | 59.9508 | -61.7035 | -0.039149 | -0.075366 | -0.018201 | -0.081155 | -0.042006 | -0.083476 | -0.19791 | -0.2029 | -0.28424 | -0.004213 | -0.098241 | 0.10466 | -0.12471 | -0.12609 | 121.5021 | 121.494 | 121.3795 | 61.5248 | -121.6166 | 121.2932 | 121.4527 | 121.4514 | 61.5742 | -121.7804
794.3281 | 121.8201 | -61.5326 | 60.0403 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0067497 | 0.053751 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063411 | 0.023434 | 0.058804 | -61.5279 | 0.033457 | -61.5863 | 60.0015 | 60.0026 | 59.8882 | -61.5305 | -61.5002 | 0.073618 | -61.6079 | 59.7881 | 59.9613 | 59.9462 | -61.6943 | 0.002053 | -0.038745 | 0.004686 | -0.05369 | -0.055743 | -0.037697 | -0.15213 | -0.1617 | -0.2522 | 0.03241 | -0.075355 | 0.086346 | -0.078934 | -0.094047 | 121.5341 | 121.5352 | 121.4207 | 61.566 | -121.5708 | 121.3207 | 121.4939 | 121.4788 | 61.6062 | -121.7346
796.0156 | 121.8704 | -61.4868 | 60.0586 | 1.4211e-13 | -0.032769 | 0.0018589 | 0.063004 | -0.0073907 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.023647 | 0.05859 | -61.5187 | 0.028878 | -61.5863 | 59.9924 | 59.998 | 59.8882 | -61.5397 | -61.5002 | 0.073618 | -61.6034 | 59.7881 | 59.9568 | 59.9508 | -61.7035 | -0.052882 | -0.066212 | -0.031934 | -0.099467 | -0.046585 | -0.060587 | -0.17044 | -0.21664 | -0.27051 | -0.013367 | -0.11655 | 0.10008 | -0.10182 | -0.10778 | 121.4792 | 121.4848 | 121.375 | 61.5157 | -121.5983 | 121.2749 | 121.4436 | 121.4376 | 61.5604 | -121.762
797.7656 | 121.7331 | -61.5097 | 60.1089 | 1.4211e-13 | -0.032769 | 0.0014317 | 0.063218 | -0.0069633 | 0.054179 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063838 | 0.023647 | 0.058804 | -61.5279 | 0.0243 | -61.5863 | 59.997 | 59.9934 | 59.879 | -61.5397 | -61.5048 | 0.064461 | -61.6079 | 59.7927 | 59.9522 | 59.9508 | -61.7035 | -0.029993 | -0.11199 | -0.018202 | -0.076578 | -0.046585 | -0.11552 | -0.22995 | -0.19375 | -0.31628 | 0.004943 | -0.098243 | 0.095504 | -0.15676 | -0.15813 | 121.5067 | 121.5031 | 121.3887 | 61.534 | -121.6486 | 121.3024 | 121.4619 | 121.4605 | 61.5742 | -121.8124
799.5156 | 121.8109 | -61.5372 | 60.0632 | 1.4211e-13 | -0.032555 | 0.0014317 | 0.063218 | -0.0069633 | 0.054179 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.023647 | 0.058376 | -61.5233 | 0.028878 | -61.5863 | 60.0015 | 59.9934 | 59.8836 | -61.5351 | -61.5002 | 0.064461 | -61.6034 | 59.7927 | 59.9568 | 59.9554 | -61.6989 | 0.002051 | -0.061633 | 0.013841 | -0.049113 | -0.051164 | -0.069743 | -0.1796 | -0.1617 | -0.27051 | 0.036987 | -0.066199 | 0.095504 | -0.1064 | -0.10778 | 121.5387 | 121.5306 | 121.4207 | 61.566 | -121.5983 | 121.3298 | 121.4939 | 121.4926 | 61.6016 | -121.762
801.2656 | 121.8292 | -61.4777 | 60.0769 | 1.4211e-13 | -0.032342 | 0.0018589 | 0.063645 | -0.0067497 | 0.053751 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063411 | 0.023647 | 0.058804 | -61.5279 | 0.0243 | -61.5863 | 59.997 | 60.0026 | 59.8882 | -61.5397 | -61.5002 | 0.064461 | -61.6125 | 59.7927 | 59.9568 | 59.9508 | -61.6989 | -0.062037 | -0.079944 | -0.050246 | -0.10862 | -0.046585 | -0.074318 | -0.18875 | -0.22121 | -0.28424 | -0.022522 | -0.13487 | 0.086347 | -0.12013 | -0.12609 | 121.4746 | 121.4802 | 121.3658 | 61.502 | -121.6166 | 121.2703 | 121.4344 | 121.4285 | 61.5421 | -121.7758
803.0156 | 121.7926 | -61.5189 | 60.0815 | 1.4211e-13 | -0.032555 | 0.0016453 | 0.063432 | -0.0067497 | 0.053538 | 0.0053413 | -0.0018757 | -0.0010577 | 0.064052 | 0.023647 | 0.058804 | -61.5187 | 0.033457 | -61.5909 | 60.0015 | 60.0026 | 59.8836 | -61.5397 | -61.5002 | 0.06904 | -61.6079 | 59.7972 | 59.9613 | 59.9462 | -61.6989 | -0.020838 | -0.079944 | 0.00011 | -0.072001 | -0.051163 | -0.078896 | -0.19791 | -0.18001 | -0.28424 | 0.018677 | -0.089088 | 0.090925 | -0.12013 | -0.13525 | 121.5204 | 121.5214 | 121.4024 | 61.5523 | -121.6212 | 121.3161 | 121.4802 | 121.4651 | 61.5879 | -121.7804
804.7188 | 121.7651 | -61.5738 | 60.0586 | 1.4211e-13 | -0.032769 | 0.0012179 | 0.063432 | -0.0067497 | 0.054179 | -0.0099192 | -0.0018757 | -0.0014849 | 0.063838 | 0.023434 | 0.05859 | -61.5233 | 0.028878 | -61.5863 | 60.0061 | 59.998 | 59.8836 | -61.5351 | -61.5048 | 0.06904 | -61.6079 | 59.7881 | 59.9613 | 59.9508 | -61.7035 | 0.038673 | -0.052477 | 0.050463 | -0.012491 | -0.051164 | -0.060587 | -0.17502 | -0.12966 | -0.27051 | 0.06903 | -0.034156 | 0.095504 | -0.097245 | -0.10778 | 121.5799 | 121.5718 | 121.4574 | 61.6027 | -121.5937 | 121.3619 | 121.5351 | 121.5246 | 61.6428 | -121.762
806.4844 | 121.7285 | -61.5921 | 60.0403 | 1.4211e-13 | -0.032555 | 0.0016453 | 0.063004 | -0.0069633 | 0.053751 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063624 | 0.023647 | 0.058376 | -61.5233 | 0.019721 | -61.5863 | 59.997 | 59.9934 | 59.8882 | -61.5397 | -61.5048 | 0.073618 | -61.6034 | 59.7972 | 59.9568 | 59.9554 | -61.7035 | 0.052404 | -0.043323 | 0.068773 | 0.005819 | -0.046585 | -0.046855 | -0.15213 | -0.11135 | -0.24304 | 0.08734 | -0.011267 | 0.10008 | -0.083512 | -0.08489 | 121.5891 | 121.5855 | 121.4803 | 61.6118 | -121.58 | 121.3893 | 121.5489 | 121.5475 | 61.6657 | -121.7437
808.1719 | 121.788 | -61.5143 | 60.1044 | 1.4211e-13 | -0.032983 | 0.0014317 | 0.063004 | -0.0069633 | 0.053965 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.023647 | 0.05859 | -61.5187 | 0.0243 | -61.5863 | 60.0015 | 59.998 | 59.879 | -61.5443 | -61.5002 | 0.06904 | -61.6034 | 59.7927 | 59.9568 | 59.9508 | -61.708 | -0.029995 | -0.10283 | -0.004468 | -0.072001 | -0.042006 | -0.10636 | -0.22538 | -0.19375 | -0.31171 | 0.014099 | -0.089087 | 0.10466 | -0.1476 | -0.15356 | 121.5158 | 121.5123 | 121.3933 | 61.5386 | -121.6486 | 121.3069 | 121.4711 | 121.4651 | 61.5833 | -121.8124
809.9219 | 121.756 | -61.5601 | 60.0082 | 1.4211e-13 | -0.032342 | 0.0016453 | 0.063004 | -0.0071769 | 0.054179 | -0.0022892 | -0.0016621 | -0.0010577 | 0.064052 | 0.023647 | 0.058804 | -61.5233 | 0.0243 | -61.5863 | 59.997 | 59.998 | 59.8882 | -61.5443 | -61.5002 | 0.06904 | -61.5942 | 59.7972 | 59.9613 | 59.9417 | -61.708 | 0.015782 | -0.01128 | 0.03673 | -0.026224 | -0.042006 | -0.010233 | -0.12009 | -0.14797 | -0.211 | 0.059876 | -0.034153 | 0.11382 | -0.046891 | -0.066582 | 121.557 | 121.5581 | 121.4482 | 61.5844 | -121.5525 | 121.3573 | 121.5214 | 121.5017 | 61.6291 | -121.7163
811.6875 | 121.8704 | -61.4777 | 60.0677 | 1.4211e-13 | -0.032555 | 0.0012179 | 0.063004 | -0.0069633 | 0.053751 | -0.0022892 | -0.0016621 | -0.00084406 | 0.063624 | 0.023434 | 0.058804 | -61.5279 | 0.0243 | -61.5863 | 60.0061 | 59.998 | 59.8836 | -61.5397 | -61.5048 | 0.064461 | -61.5988 | 59.7927 | 59.9568 | 59.9554 | -61.7035 | -0.062037 | -0.061632 | -0.050246 | -0.10862 | -0.046585 | -0.069742 | -0.18418 | -0.22579 | -0.27508 | -0.027101 | -0.12113 | 0.10466 | -0.11098 | -0.11236 | 121.4838 | 121.4757 | 121.3612 | 61.502 | -121.6074 | 121.2703 | 121.4344 | 121.4331 | 61.5421 | -121.7712
813.4375 | 121.7743 | -61.5005 | 60.0952 | 1.4211e-13 | -0.032769 | 0.0014317 | 0.063218 | -0.0071769 | 0.053751 | -0.0099192 | -0.0016621 | -0.0016987 | 0.063838 | 0.023434 | 0.05859 | -61.5233 | 0.0243 | -61.5909 | 60.0061 | 60.0026 | 59.8882 | -61.5397 | -61.491 | 0.064461 | -61.5988 | 59.7927 | 59.9568 | 59.9417 | -61.7035 | -0.039149 | -0.089098 | -0.02278 | -0.090312 | -0.051163 | -0.092629 | -0.20707 | -0.2029 | -0.30255 | 0.009523 | -0.098241 | 0.10466 | -0.13844 | -0.15356 | 121.5067 | 121.5031 | 121.3887 | 61.5248 | -121.6349 | 121.2932 | 121.4573 | 121.4422 | 61.565 | -121.7987
815.125 | 121.8155 | -61.5234 | 60.0357 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063004 | -0.0069633 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.024075 | 0.058163 | -61.5279 | 0.0243 | -61.5863 | 60.0061 | 59.998 | 59.8836 | -61.5351 | -61.4956 | 0.064461 | -61.6125 | 59.8064 | 59.9568 | 59.9508 | -61.6989 | -0.011682 | -0.029589 | -0.00447 | -0.062846 | -0.051164 | -0.037699 | -0.15213 | -0.17544 | -0.22931 | 0.027833 | -0.089089 | 0.086347 | -0.078935 | -0.084891 | 121.5296 | 121.5214 | 121.407 | 61.5477 | -121.5708 | 121.3298 | 121.4802 | 121.4743 | 61.5879 | -121.7346
816.875 | 121.7926 | -61.5189 | 60.0449 | 1.4211e-13 | -0.032769 | 0.0018589 | 0.063432 | -0.0069633 | 0.054392 | -0.01755 | -0.0018757 | -0.0012713 | 0.063624 | 0.023861 | 0.058376 | -61.5233 | 0.028878 | -61.5909 | 60.0061 | 59.998 | 59.8836 | -61.5351 | -61.5048 | 0.064461 | -61.6034 | 59.7972 | 59.9522 | 59.9508 | -61.7035 | -0.016259 | -0.038744 | -0.004469 | -0.072001 | -0.055742 | -0.046854 | -0.16129 | -0.18459 | -0.24762 | 0.014098 | -0.084509 | 0.10008 | -0.092669 | -0.094046 | 121.525 | 121.5169 | 121.4024 | 61.5477 | -121.58 | 121.3161 | 121.4711 | 121.4697 | 61.5833 | -121.7483
818.625 | 121.7468 | -61.5692 | 60.0586 | 1.4211e-13 | -0.032769 | 0.0016453 | 0.063432 | -0.0073907 | 0.054179 | -0.01755 | -0.0020893 | -0.0010577 | 0.063624 | 0.023434 | 0.05859 | -61.5187 | 0.028878 | -61.5909 | 60.0107 | 60.0026 | 59.8744 | -61.5351 | -61.491 | 0.06904 | -61.6034 | 59.7927 | 59.9568 | 59.9462 | -61.7035 | 0.034095 | -0.047899 | 0.050464 | -0.021647 | -0.055742 | -0.056008 | -0.18418 | -0.13424 | -0.26593 | 0.078188 | -0.034155 | 0.10008 | -0.10182 | -0.11236 | 121.5799 | 121.5718 | 121.4436 | 61.5981 | -121.5937 | 121.3619 | 121.526 | 121.5155 | 61.6383 | -121.762
820.375 | 121.7789 | -61.528 | 60.0632 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063218 | -0.0073907 | 0.054179 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.023647 | 0.058804 | -61.5142 | 0.0243 | -61.5909 | 59.997 | 59.9934 | 59.8882 | -61.5351 | -61.5002 | 0.064461 | -61.6034 | 59.7972 | 59.9522 | 59.9508 | -61.708 | -0.007104 | -0.066211 | 0.013843 | -0.062846 | -0.055742 | -0.069743 | -0.17502 | -0.18002 | -0.26593 | 0.027832 | -0.075354 | 0.10466 | -0.11098 | -0.11236 | 121.525 | 121.5214 | 121.4162 | 61.5523 | -121.5983 | 121.3253 | 121.4802 | 121.4788 | 61.5925 | -121.7712
822.0625 | 121.8887 | -61.5051 | 60.0494 | 1.4211e-13 | -0.032983 | 0.0014317 | 0.063432 | -0.0069633 | 0.053751 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063624 | 0.023434 | 0.058804 | -61.5142 | 0.0243 | -61.5909 | 60.0015 | 60.0026 | 59.8927 | -61.5351 | -61.5048 | 0.064461 | -61.6034 | 59.7972 | 59.9568 | 59.9554 | -61.6989 | -0.029992 | -0.0479 | -0.009045 | -0.085734 | -0.055742 | -0.046852 | -0.15671 | -0.19375 | -0.2522 | 0.000365 | -0.098242 | 0.095504 | -0.092667 | -0.094045 | 121.5067 | 121.5077 | 121.3979 | 61.5294 | -121.5846 | 121.3024 | 121.4619 | 121.4605 | 61.5696 | -121.7483
823.8438 | 121.7514 | -61.5189 | 60.1089 | 1.4211e-13 | -0.032769 | 0.0014317 | 0.063004 | -0.0071769 | 0.053965 | -0.0099192 | -0.0018757 | -0.00084406 | 0.063624 | 0.023861 | 0.058804 | -61.5233 | 0.028878 | -61.5863 | 59.997 | 59.9934 | 59.8836 | -61.5397 | -61.5048 | 0.059882 | -61.5942 | 59.7972 | 59.9568 | 59.9417 | -61.708 | -0.020838 | -0.11199 | -0.004469 | -0.067423 | -0.046585 | -0.11552 | -0.22538 | -0.18917 | -0.31171 | 0.014098 | -0.075352 | 0.11382 | -0.15218 | -0.16729 | 121.5158 | 121.5123 | 121.4024 | 61.5477 | -121.6486 | 121.3161 | 121.4756 | 121.4605 | 61.5787 | -121.817
825.5312 | 121.8658 | -61.496 | 60.0677 | 1.4211e-13 | -0.032983 | 0.0014317 | 0.063218 | -0.0071769 | 0.053965 | -0.02518 | -0.0018757 | -0.0014849 | 0.063624 | 0.023861 | 0.058804 | -61.5142 | 0.0243 | -61.5954 | 59.997 | 60.0026 | 59.879 | -61.5351 | -61.5002 | 0.06904 | -61.6125 | 59.7972 | 59.9568 | 59.9462 | -61.708 | -0.039147 | -0.070789 | -0.0182 | -0.099467 | -0.06032 | -0.065163 | -0.18876 | -0.21206 | -0.27051 | -0.004211 | -0.11655 | 0.095505 | -0.11098 | -0.12151 | 121.4929 | 121.4986 | 121.375 | 61.5203 | -121.6029 | 121.2932 | 121.4527 | 121.4422 | 61.565 | -121.7758
827.2812 | 121.7422 | -61.5189 | 60.1181 | 1.4211e-13 | -0.032769 | 0.0018589 | 0.063004 | -0.0076043 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.064052 | 0.023647 | 0.058376 | -61.5233 | 0.0243 | -61.5863 | 60.0015 | 60.0026 | 59.8882 | -61.5351 | -61.4956 | 0.059882 | -61.6079 | 59.7972 | 59.9568 | 59.9554 | -61.7035 | -0.016259 | -0.11657 | -0.004469 | -0.067423 | -0.051164 | -0.11552 | -0.22995 | -0.18459 | -0.32086 | 0.023256 | -0.089088 | 0.095504 | -0.16133 | -0.16271 | 121.5204 | 121.5214 | 121.407 | 61.5432 | -121.6532 | 121.3161 | 121.4756 | 121.4743 | 61.5787 | -121.8216
829.0469 | 121.7422 | -61.5005 | 60.1089 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063004 | -0.0069633 | 0.053965 | -0.01755 | -0.0016621 | -0.0010577 | 0.064265 | 0.023647 | 0.05859 | -61.5233 | 0.0243 | -61.5863 | 60.0015 | 59.998 | 59.8836 | -61.5351 | -61.5002 | 0.064461 | -61.5988 | 59.8018 | 59.9613 | 59.9462 | -61.7035 | -0.03457 | -0.10741 | -0.02278 | -0.085734 | -0.051164 | -0.11094 | -0.22538 | -0.2029 | -0.30713 | 0.000366 | -0.098241 | 0.10466 | -0.1476 | -0.16271 | 121.5021 | 121.4986 | 121.3841 | 61.5248 | -121.6441 | 121.3024 | 121.4619 | 121.4468 | 61.565 | -121.8124
830.8125 | 121.8658 | -61.4868 | 60.0494 | 1.4211e-13 | -0.032983 | 0.0014317 | 0.063645 | -0.0069633 | 0.053965 | -0.01755 | -0.0018757 | -0.0012713 | 0.063838 | 0.023861 | 0.05859 | -61.5187 | 0.028878 | -61.5909 | 60.0015 | 59.998 | 59.8836 | -61.5443 | -61.5002 | 0.064461 | -61.6079 | 59.7972 | 59.9613 | 59.9508 | -61.7035 | -0.057461 | -0.0479 | -0.031934 | -0.10404 | -0.046584 | -0.051431 | -0.16587 | -0.21664 | -0.2522 | -0.013367 | -0.12113 | 0.095504 | -0.088089 | -0.098623 | 121.4884 | 121.4848 | 121.3704 | 61.5157 | -121.5937 | 121.2841 | 121.4482 | 121.4376 | 61.5513 | -121.7529
832.5 | 121.8979 | -61.4731 | 60.0311 | 1.4211e-13 | -0.032769 | 0.0014317 | 0.063218 | -0.0069633 | 0.053751 | -0.0022892 | -0.0018757 | -0.0010577 | 0.063624 | 0.023861 | 0.05859 | -61.5142 | 0.015142 | -61.5909 | 60.0015 | 60.0026 | 59.8882 | -61.5397 | -61.5048 | 0.059882 | -61.6079 | 59.7972 | 59.9613 | 59.9508 | -61.7035 | -0.066615 | -0.02959 | -0.041089 | -0.11778 | -0.051163 | -0.028542 | -0.14298 | -0.23037 | -0.23389 | -0.031679 | -0.13486 | 0.095504 | -0.069779 | -0.080313 | 121.4746 | 121.4757 | 121.3612 | 61.4882 | -121.5708 | 121.2703 | 121.4344 | 121.4239 | 61.533 | -121.7346
834.25 | 121.8842 | -61.4822 | 60.0906 | 1.4211e-13 | -0.032769 | 0.0016453 | 0.063218 | -0.0071769 | 0.054179 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.023647 | 0.058804 | -61.5233 | 0.028878 | -61.5954 | 60.0015 | 59.998 | 59.8882 | -61.5397 | -61.5002 | 0.059882 | -61.5988 | 59.8018 | 59.9568 | 59.9417 | -61.7035 | -0.057459 | -0.089099 | -0.04109 | -0.1132 | -0.055741 | -0.09263 | -0.20249 | -0.22121 | -0.28882 | -0.017944 | -0.11655 | 0.10466 | -0.13387 | -0.14898 | 121.4838 | 121.4802 | 121.3704 | 61.5111 | -121.6303 | 121.2841 | 121.439 | 121.4239 | 61.5421 | -121.7941
835.9375 | 121.907 | -61.4548 | 60.054 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063218 | -0.0069633 | 0.053965 | -0.0099192 | -0.0020893 | -0.0014849 | 0.063838 | 0.023861 | 0.058804 | -61.5233 | 0.0243 | -61.5909 | 59.997 | 59.998 | 59.8836 | -61.5443 | -61.5002 | 0.059882 | -61.6079 | 59.8018 | 59.9659 | 59.9508 | -61.7035 | -0.089504 | -0.057056 | -0.068556 | -0.13609 | -0.046584 | -0.056009 | -0.17044 | -0.24868 | -0.2522 | -0.04541 | -0.15317 | 0.095504 | -0.088088 | -0.1032 | 121.4517 | 121.4528 | 121.3383 | 61.4791 | -121.5983 | 121.2566 | 121.4207 | 121.4056 | 61.5147 | -121.7575
837.6875 | 121.8613 | -61.4914 | 60.0494 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063004 | -0.0067497 | 0.053751 | -0.0022892 | -0.0018757 | -0.0010577 | 0.064052 | 0.023434 | 0.058804 | -61.5233 | 0.019721 | -61.5954 | 59.997 | 60.0026 | 59.8882 | -61.5351 | -61.5093 | 0.059882 | -61.6034 | 59.7927 | 59.9659 | 59.9508 | -61.6989 | -0.043725 | -0.052478 | -0.031935 | -0.10404 | -0.06032 | -0.046852 | -0.16129 | -0.20748 | -0.25677 | -0.017947 | -0.11198 | 0.095504 | -0.08351 | -0.098623 | 121.4884 | 121.494 | 121.3795 | 61.5111 | -121.5846 | 121.2841 | 121.4573 | 121.4422 | 61.5513 | -121.7483
839.4375 | 121.8796 | -61.4777 | 60.0357 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | 0.0053413 | -0.0016621 | -0.0010577 | 0.063624 | 0.023434 | 0.05859 | -61.5233 | 0.028878 | -61.5954 | 60.0061 | 60.0026 | 59.8882 | -61.5351 | -61.5002 | 0.059882 | -61.5988 | 59.8018 | 59.9568 | 59.9462 | -61.708 | -0.057458 | -0.029589 | -0.045668 | -0.11778 | -0.06032 | -0.03312 | -0.14756 | -0.23037 | -0.23389 | -0.022522 | -0.12113 | 0.10924 | -0.078935 | -0.08947 | 121.4838 | 121.4802 | 121.3658 | 61.5065 | -121.5708 | 121.2795 | 121.4344 | 121.4239 | 61.5375 | -121.7437
841.1875 | 121.8842 | -61.5372 | 59.9716 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063218 | -0.0069633 | 0.053965 | -0.01755 | -0.0020893 | -0.00084406 | 0.063624 | 0.023861 | 0.059231 | -61.5187 | 0.0243 | -61.5863 | 60.0107 | 59.998 | 59.8836 | -61.5443 | -61.4956 | 0.073618 | -61.6079 | 59.7972 | 59.9613 | 59.9462 | -61.7126 | -0.007107 | 0.039076 | 0.01842 | -0.049113 | -0.042006 | 0.026388 | -0.088047 | -0.17544 | -0.17438 | 0.041566 | -0.070778 | 0.10466 | -0.01027 | -0.025383 | 121.5479 | 121.5352 | 121.4207 | 61.5615 | -121.5159 | 121.3344 | 121.4985 | 121.4834 | 61.6108 | -121.6842
842.9375 | 121.7285 | -61.5189 | 60.1181 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063004 | -0.0069633 | 0.053538 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.023861 | 0.058804 | -61.5187 | 0.028878 | -61.5909 | 60.0015 | 59.998 | 59.8927 | -61.5397 | -61.4956 | 0.064461 | -61.6079 | 59.7927 | 59.9568 | 59.9462 | -61.6989 | -0.020838 | -0.11657 | 0.00011 | -0.072001 | -0.051163 | -0.1201 | -0.22537 | -0.18001 | -0.32544 | 0.023256 | -0.089088 | 0.090925 | -0.16133 | -0.17187 | 121.5204 | 121.5169 | 121.4116 | 61.5477 | -121.6578 | 121.3115 | 121.4756 | 121.4651 | 61.5833 | -121.817
844.6875 | 121.788 | -61.496 | 60.1089 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063004 | -0.0069633 | 0.053965 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.023647 | 0.059231 | -61.5279 | 0.019721 | -61.6 | 60.0015 | 60.0026 | 59.8836 | -61.5443 | -61.491 | 0.059882 | -61.6034 | 59.7972 | 59.9613 | 59.9508 | -61.708 | -0.048305 | -0.10741 | -0.031935 | -0.10404 | -0.05574 | -0.10636 | -0.22538 | -0.21206 | -0.31171 | 0.004946 | -0.1074 | 0.10466 | -0.1476 | -0.15813 | 121.4975 | 121.4986 | 121.3795 | 61.5157 | -121.6532 | 121.2932 | 121.4573 | 121.4468 | 61.5559 | -121.817
846.375 | 121.7468 | -61.5692 | 60.0449 | 1.4211e-13 | -0.033196 | 0.0014317 | 0.063218 | -0.0071769 | 0.053965 | -0.0099192 | -0.0016621 | -0.0012713 | 0.063838 | 0.023861 | 0.059017 | -61.5233 | 0.0243 | -61.5954 | 60.0015 | 59.9888 | 59.879 | -61.5443 | -61.5002 | 0.064461 | -61.6079 | 59.7972 | 59.9659 | 59.9462 | -61.708 | 0.024937 | -0.043323 | 0.045885 | -0.026225 | -0.051162 | -0.056012 | -0.16587 | -0.13882 | -0.24762 | 0.069031 | -0.038734 | 0.10008 | -0.078933 | -0.098625 | 121.5708 | 121.5581 | 121.4482 | 61.5935 | -121.5891 | 121.3665 | 121.5351 | 121.5155 | 61.6337 | -121.7529
848.125 | 121.8613 | -61.5372 | 59.9854 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063004 | -0.0069633 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.064052 | 0.023647 | 0.05859 | -61.5279 | 0.0243 | -61.5954 | 59.997 | 60.0026 | 59.8927 | -61.5443 | -61.5002 | 0.064461 | -61.6034 | 59.7972 | 59.9659 | 59.9462 | -61.7035 | -0.007107 | 0.011608 | 0.009263 | -0.058269 | -0.051162 | 0.017234 | -0.092623 | -0.16628 | -0.18811 | 0.036987 | -0.066199 | 0.10008 | -0.019424 | -0.039116 | 121.5341 | 121.5398 | 121.4299 | 61.5615 | -121.5296 | 121.3344 | 121.5031 | 121.4834 | 61.6016 | -121.6888
849.8281 | 121.7422 | -61.5005 | 60.1089 | 1.4211e-13 | -0.032769 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063624 | 0.023861 | 0.059017 | -61.5187 | 0.0243 | -61.5954 | 60.0015 | 59.998 | 59.8836 | -61.5443 | -61.5002 | 0.050725 | -61.6079 | 59.7927 | 59.9613 | 59.9462 | -61.708 | -0.043728 | -0.10741 | -0.018201 | -0.09489 | -0.051162 | -0.11094 | -0.22538 | -0.20748 | -0.31628 | 0.000366 | -0.1074 | 0.10008 | -0.1476 | -0.16271 | 121.5021 | 121.4986 | 121.3841 | 61.5248 | -121.6532 | 121.2932 | 121.4619 | 121.4468 | 61.5513 | -121.817
851.5781 | 121.7651 | -61.5051 | 60.0998 | 1.4211e-13 | -0.033196 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | -0.0022892 | -0.0018757 | -0.0014849 | 0.064052 | 0.024288 | 0.05859 | -61.5142 | 0.028878 | -61.6 | 60.0015 | 59.9888 | 59.8836 | -61.5351 | -61.4956 | 0.059882 | -61.6034 | 59.7881 | 59.9613 | 59.9508 | -61.7035 | -0.029992 | -0.098254 | -0.009045 | -0.09489 | -0.064898 | -0.11094 | -0.21622 | -0.19832 | -0.31171 | 0.009523 | -0.098242 | 0.10008 | -0.13844 | -0.14898 | 121.5067 | 121.494 | 121.3887 | 61.534 | -121.6349 | 121.2932 | 121.4665 | 121.4559 | 61.565 | -121.8032
853.2656 | 121.875 | -61.4594 | 60.0632 | 1.4211e-13 | -0.032769 | 0.0016453 | 0.063645 | -0.0073907 | 0.053965 | -0.0099192 | -0.0018757 | -0.00084406 | 0.063838 | 0.024075 | 0.058804 | -61.5279 | 0.0243 | -61.6 | 60.0061 | 59.998 | 59.8882 | -61.5351 | -61.5002 | 0.064461 | -61.6079 | 59.7972 | 59.9613 | 59.9508 | -61.7035 | -0.075768 | -0.057054 | -0.068556 | -0.14067 | -0.064898 | -0.065164 | -0.17502 | -0.2441 | -0.26593 | -0.040832 | -0.1486 | 0.095504 | -0.10182 | -0.11236 | 121.4655 | 121.4574 | 121.3475 | 61.4837 | -121.5983 | 121.2566 | 121.4207 | 121.4102 | 61.5238 | -121.7666
855.0312 | 121.8155 | -61.5326 | 60.0082 | 1.4211e-13 | -0.032983 | 0.0014317 | 0.063218 | -0.0069633 | 0.054179 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.023861 | 0.058376 | -61.5187 | 0.028878 | -61.5909 | 60.0015 | 59.998 | 59.8927 | -61.5305 | -61.491 | 0.059882 | -61.5988 | 59.7927 | 59.9613 | 59.9508 | -61.7035 | 0.002053 | -0.006702 | 0.013843 | -0.058268 | -0.060321 | -0.010233 | -0.11551 | -0.17086 | -0.21558 | 0.041567 | -0.066197 | 0.10466 | -0.046891 | -0.057425 | 121.5341 | 121.5306 | 121.4253 | 61.5615 | -121.5388 | 121.3253 | 121.4939 | 121.4834 | 61.5925 | -121.7117
856.7969 | 121.8384 | -61.5143 | 60.0128 | 1.4211e-13 | -0.03341 | 0.0018589 | 0.063004 | -0.0069633 | 0.054179 | -0.0022892 | -0.0016621 | -0.0012713 | 0.063838 | 0.023434 | 0.059017 | -61.5233 | 0.028878 | -61.5909 | 60.0061 | 60.0026 | 59.8882 | -61.5397 | -61.4864 | 0.059882 | -61.5988 | 59.7927 | 59.9659 | 59.9554 | -61.708 | -0.025416 | -0.0067 | -0.009047 | -0.076579 | -0.051163 | -0.010231 | -0.12467 | -0.19375 | -0.22015 | 0.027835 | -0.084508 | 0.10924 | -0.046889 | -0.057424 | 121.5204 | 121.5169 | 121.4024 | 61.5432 | -121.5525 | 121.3069 | 121.4802 | 121.4697 | 61.5742 | -121.7208
858.5 | 121.7468 | -61.5646 | 60.0266 | 1.4211e-13 | -0.033196 | 0.0014317 | 0.063218 | -0.0073907 | 0.054179 | 0.0053413 | -0.0016621 | -0.0012713 | 0.063838 | 0.024075 | 0.058804 | -61.5096 | 0.019721 | -61.5863 | 60.0107 | 59.9934 | 59.8973 | -61.5397 | -61.4864 | 0.06904 | -61.6034 | 59.8064 | 59.9568 | 59.9508 | -61.7035 | 0.024938 | -0.015855 | 0.055043 | -0.021647 | -0.046585 | -0.033122 | -0.12924 | -0.13882 | -0.22015 | 0.078189 | -0.038733 | 0.10008 | -0.069779 | -0.075735 | 121.5753 | 121.5581 | 121.4619 | 61.5844 | -121.5662 | 121.371 | 121.5214 | 121.5155 | 61.6337 | -121.73
860.25 | 121.7789 | -61.4731 | 60.1044 | 1.4211e-13 | -0.032983 | 0.0014317 | 0.063218 | -0.0069633 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063411 | 0.023861 | 0.058376 | -61.5233 | 0.0243 | -61.5954 | 60.0107 | 59.998 | 59.8973 | -61.5351 | -61.4773 | 0.055303 | -61.6034 | 59.7972 | 59.9659 | 59.9554 | -61.708 | -0.062036 | -0.093675 | -0.050246 | -0.12236 | -0.06032 | -0.10636 | -0.20706 | -0.23495 | -0.30713 | -0.004207 | -0.13029 | 0.10466 | -0.13844 | -0.14898 | 121.4838 | 121.4711 | 121.3704 | 61.4974 | -121.6395 | 121.2703 | 121.439 | 121.4285 | 61.5284 | -121.8124
861.9531 | 121.7606 | -61.496 | 60.0815 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063218 | -0.0073907 | 0.053751 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.023861 | 0.059017 | -61.5142 | 0.019721 | -61.5863 | 59.997 | 59.998 | 59.8927 | -61.5443 | -61.4864 | 0.064461 | -61.6034 | 59.7972 | 59.9705 | 59.9508 | -61.7035 | -0.048305 | -0.084522 | -0.0182 | -0.090311 | -0.042006 | -0.083475 | -0.18875 | -0.20748 | -0.28424 | 0.009525 | -0.1074 | 0.10008 | -0.11098 | -0.13067 | 121.4929 | 121.494 | 121.3887 | 61.5157 | -121.6258 | 121.2932 | 121.4665 | 121.4468 | 61.5604 | -121.7849
863.7188 | 121.7148 | -61.5509 | 60.0357 | 1.4211e-13 | -0.033196 | 0.0016453 | 0.063645 | -0.0071769 | 0.054179 | -0.0099192 | -0.0016621 | -0.0014849 | 0.063838 | 0.023861 | 0.058376 | -61.5142 | 0.019721 | -61.5817 | 60.0061 | 60.0026 | 59.8882 | -61.5351 | -61.4819 | 0.064461 | -61.5988 | 59.8018 | 59.9613 | 59.96 | -61.7035 | 0.015784 | -0.029589 | 0.036731 | -0.030801 | -0.046585 | -0.03312 | -0.14756 | -0.15255 | -0.23389 | 0.069035 | -0.047887 | 0.10466 | -0.074357 | -0.075734 | 121.557 | 121.5535 | 121.4391 | 61.5706 | -121.5708 | 121.3527 | 121.5123 | 121.5109 | 61.6154 | -121.7392
865.4688 | 121.7422 | -61.496 | 60.1547 | 1.4211e-13 | -0.032769 | 0.0016453 | 0.063432 | -0.0071769 | 0.053538 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.024288 | 0.058804 | -61.5187 | 0.019721 | -61.5954 | 59.997 | 59.998 | 59.8973 | -61.5351 | -61.4819 | 0.064461 | -61.5988 | 59.7972 | 59.9568 | 59.9508 | -61.7035 | -0.039147 | -0.15776 | -0.022778 | -0.099467 | -0.06032 | -0.15672 | -0.25742 | -0.20748 | -0.35748 | 0.014104 | -0.10282 | 0.10466 | -0.19795 | -0.20391 | 121.4929 | 121.494 | 121.3933 | 61.5157 | -121.6898 | 121.2932 | 121.4527 | 121.4468 | 61.5604 | -121.8582
867.1719 | 121.8292 | -61.4594 | 60.0906 | 1.4211e-13 | -0.033196 | 0.0014317 | 0.063004 | -0.0071769 | 0.053751 | 0.0053413 | -0.0020893 | -0.0014849 | 0.063624 | 0.023861 | 0.058804 | -61.5233 | 0.028878 | -61.5909 | 60.0061 | 59.9934 | 59.8882 | -61.526 | -61.4727 | 0.059882 | -61.5988 | 59.7972 | 59.9705 | 59.9554 | -61.6989 | -0.06661 | -0.08452 | -0.063978 | -0.13151 | -0.0649 | -0.097209 | -0.20249 | -0.23952 | -0.2934 | -0.01336 | -0.13944 | 0.10008 | -0.12013 | -0.13524 | 121.4655 | 121.4528 | 121.3475 | 61.4882 | -121.6166 | 121.2566 | 121.4299 | 121.4147 | 61.5192 | -121.7895
868.9375 | 121.788 | -61.5097 | 60.1181 | 1.4211e-13 | -0.033196 | 0.0016453 | 0.063432 | -0.0073907 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.064052 | 0.023861 | 0.058804 | -61.5233 | 0.019721 | -61.5909 | 60.0015 | 60.0026 | 59.8973 | -61.5351 | -61.4773 | 0.059882 | -61.5988 | 59.8018 | 59.9568 | 59.96 | -61.708 | -0.025414 | -0.11657 | -0.013624 | -0.081156 | -0.055742 | -0.11552 | -0.2208 | -0.19833 | -0.31628 | 0.032415 | -0.089085 | 0.10924 | -0.16133 | -0.15813 | 121.5112 | 121.5123 | 121.407 | 61.5294 | -121.6532 | 121.3115 | 121.4665 | 121.4697 | 61.5696 | -121.8261
870.6406 | 121.7422 | -61.5875 | 60.0494 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.063218 | -0.0073907 | 0.053965 | -0.0099192 | -0.0025167 | -0.0012713 | 0.063838 | 0.024075 | 0.059017 | -61.5142 | 0.0243 | -61.5909 | 60.0107 | 60.0026 | 59.8973 | -61.5351 | -61.4819 | 0.050725 | -61.5988 | 59.8018 | 59.9568 | 59.9508 | -61.7035 | 0.052405 | -0.038743 | 0.073352 | -0.003337 | -0.055742 | -0.046852 | -0.15213 | -0.11593 | -0.24762 | 0.10566 | -0.011266 | 0.10466 | -0.092667 | -0.098623 | 121.5982 | 121.5901 | 121.4848 | 61.6118 | -121.5846 | 121.3893 | 121.5443 | 121.5383 | 61.6382 | -121.7529
872.3906 | 121.8521 | -61.4731 | 60.0815 | 1.4211e-13 | -0.03341 | 0.0018589 | 0.062791 | -0.0071769 | 0.053538 | -0.02518 | -0.0020893 | -0.0012713 | 0.063624 | 0.024075 | 0.05859 | -61.5142 | 0.028878 | -61.5909 | 60.0107 | 60.0072 | 59.8882 | -61.5305 | -61.4727 | 0.059882 | -61.5988 | 59.8018 | 59.9659 | 59.9508 | -61.7035 | -0.057457 | -0.070787 | -0.041089 | -0.11778 | -0.060321 | -0.074317 | -0.19333 | -0.23037 | -0.27966 | 0.000372 | -0.12571 | 0.10466 | -0.11555 | -0.13067 | 121.4838 | 121.4802 | 121.3612 | 61.502 | -121.612 | 121.2749 | 121.439 | 121.4239 | 61.533 | -121.7849
874.0781 | 121.7422 | -61.5097 | 60.1089 | 1.4211e-13 | -0.033196 | 0.0014317 | 0.063645 | -0.0069633 | 0.053965 | -0.0022892 | -0.0020893 | -0.0014849 | 0.064052 | 0.023647 | 0.058804 | -61.5142 | 0.0243 | -61.5909 | 60.0015 | 60.0072 | 59.8882 | -61.5351 | -61.4819 | 0.050725 | -61.5942 | 59.8018 | 59.9705 | 59.96 | -61.7035 | -0.025414 | -0.10741 | -0.004467 | -0.081156 | -0.055742 | -0.10178 | -0.2208 | -0.19375 | -0.30713 | 0.027837 | -0.084507 | 0.10924 | -0.13844 | -0.14898 | 121.5112 | 121.5169 | 121.3979 | 61.534 | -121.6441 | 121.3115 | 121.4802 | 121.4697 | 61.5604 | -121.8124
875.8281 | 121.8658 | -61.5463 | 59.967 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.063218 | -0.0073907 | 0.053965 | -0.0099192 | -0.0016621 | -0.00084406 | 0.063411 | 0.024288 | 0.058804 | -61.5096 | 0.0243 | -61.5909 | 60.0061 | 60.0072 | 59.8973 | -61.5305 | -61.4681 | 0.046146 | -61.5896 | 59.8064 | 59.9705 | 59.96 | -61.7035 | 0.015786 | 0.039076 | 0.036733 | -0.044535 | -0.060321 | 0.040124 | -0.069734 | -0.15713 | -0.16064 | 0.078194 | -0.043307 | 0.11382 | 0.003465 | -0.007069 | 121.5524 | 121.5535 | 121.4436 | 61.5706 | -121.4976 | 121.3527 | 121.5168 | 121.5063 | 61.5925 | -121.6705
877.5781 | 121.8796 | -61.4639 | 60.054 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.063218 | -0.0069633 | 0.053965 | 0.0053413 | -0.0016621 | -0.00084406 | 0.063838 | 0.023861 | 0.058804 | -61.5142 | 0.038035 | -61.6 | 60.0061 | 60.0163 | 59.9019 | -61.526 | -61.4819 | 0.036989 | -61.5942 | 59.8018 | 59.9705 | 59.9508 | -61.708 | -0.062033 | -0.047899 | -0.050244 | -0.13609 | -0.074056 | -0.037693 | -0.15213 | -0.2441 | -0.2522 | -0.01794 | -0.13028 | 0.11382 | -0.08351 | -0.1032 | 121.47 | 121.4803 | 121.3658 | 61.502 | -121.58 | 121.2657 | 121.4344 | 121.4147 | 61.5009 | -121.762
879.3281 | 121.7422 | -61.5005 | 60.1181 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.063004 | -0.0071769 | 0.053751 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063624 | 0.023647 | 0.058804 | -61.5142 | 0.019721 | -61.5817 | 60.0061 | 60.0072 | 59.8973 | -61.5214 | -61.4681 | 0.018674 | -61.5851 | 59.8018 | 59.9705 | 59.9554 | -61.6989 | -0.020833 | -0.11199 | -0.013623 | -0.081155 | -0.060322 | -0.11094 | -0.2208 | -0.19832 | -0.31628 | 0.032417 | -0.084505 | 0.11382 | -0.1476 | -0.16271 | 121.5067 | 121.5077 | 121.3979 | 61.5203 | -121.6395 | 121.3024 | 121.4711 | 121.4559 | 61.5192 | -121.817
881.0781 | 121.875 | -61.4777 | 60.054 | 1.4211e-13 | -0.03341 | 0.0018589 | 0.063432 | -0.0071769 | 0.054179 | -0.01755 | -0.0016621 | -0.0012713 | 0.063838 | 0.023861 | 0.05859 | -61.5142 | 0.0243 | -61.5863 | 60.0153 | 60.0072 | 59.8973 | -61.5305 | -61.4636 | 0.009516 | -61.5851 | 59.811 | 59.9751 | 59.9554 | -61.6943 | -0.052879 | -0.038742 | -0.036511 | -0.10862 | -0.055743 | -0.046851 | -0.15671 | -0.21663 | -0.24304 | 0.014108 | -0.10739 | 0.10924 | -0.078931 | -0.098623 | 121.4929 | 121.4848 | 121.375 | 61.502 | -121.5846 | 121.2886 | 121.4527 | 121.4331 | 61.4872 | -121.7483
882.8281 | 121.8338 | -61.4868 | 60.0266 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063624 | 0.023647 | 0.058376 | -61.5187 | 0.033457 | -61.5863 | 60.0107 | 60.0026 | 59.9019 | -61.526 | -61.4636 | -0.013377 | -61.5896 | 59.8064 | 59.9751 | 59.9554 | -61.6897 | -0.039145 | -0.015855 | -0.031934 | -0.099467 | -0.060322 | -0.023964 | -0.12466 | -0.2029 | -0.22015 | 0.023263 | -0.10282 | 0.10008 | -0.051465 | -0.071157 | 121.4975 | 121.4894 | 121.3887 | 61.5203 | -121.5525 | 121.2932 | 121.4619 | 121.4422 | 61.4734 | -121.7163
884.5156 | 121.756 | -61.5326 | 60.0494 | 1.4211e-13 | -0.03341 | 0.0018589 | 0.063218 | -0.0067497 | 0.053965 | -0.0099192 | -0.0018757 | -0.00084406 | 0.063838 | 0.024075 | 0.05859 | -61.5142 | 0.0243 | -61.5863 | 60.0061 | 59.998 | 59.9019 | -61.526 | -61.4636 | -0.040849 | -61.5805 | 59.7972 | 59.9705 | 59.9554 | -61.6943 | 0.006632 | -0.043321 | 0.018421 | -0.05369 | -0.060322 | -0.051431 | -0.14755 | -0.1617 | -0.2522 | 0.06904 | -0.047882 | 0.11382 | -0.078932 | -0.094045 | 121.5387 | 121.5306 | 121.4345 | 61.5569 | -121.5754 | 121.3298 | 121.5031 | 121.488 | 61.4917 | -121.7437
886.2656 | 121.7926 | -61.5326 | 60.0586 | 1.4211e-13 | -0.033624 | 0.0012179 | 0.063432 | -0.0073907 | 0.054179 | -0.01755 | -0.0016621 | -0.0010577 | 0.064052 | 0.023861 | 0.05859 | -61.5142 | 0.0243 | -61.5863 | 60.0153 | 60.0072 | 59.9065 | -61.5305 | -61.459 | -0.082058 | -61.5805 | 59.811 | 59.9705 | 59.9554 | -61.6897 | 0.002053 | -0.04332 | 0.018421 | -0.05369 | -0.055743 | -0.051429 | -0.15213 | -0.15712 | -0.24762 | 0.073618 | -0.047882 | 0.10924 | -0.088088 | -0.1032 | 121.5479 | 121.5398 | 121.4391 | 61.5569 | -121.5891 | 121.3436 | 121.5031 | 121.488 | 61.4505 | -121.7483
888.0156 | 121.875 | -61.4868 | 60.0769 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.062791 | -0.0071769 | 0.053965 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.023861 | 0.059017 | -61.505 | 0.0243 | -61.5863 | 60.0107 | 60.0117 | 59.8973 | -61.5168 | -61.459 | -0.11411 | -61.5896 | 59.8018 | 59.9751 | 59.96 | -61.6989 | -0.029988 | -0.066209 | -0.018199 | -0.099467 | -0.069479 | -0.06516 | -0.1796 | -0.21206 | -0.27508 | 0.027841 | -0.10282 | 0.10924 | -0.10182 | -0.11693 | 121.4975 | 121.4986 | 121.3841 | 61.5111 | -121.5937 | 121.2886 | 121.4619 | 121.4468 | 61.3727 | -121.7758
889.7812 | 121.7606 | -61.5189 | 60.0632 | 1.4211e-13 | -0.032983 | 0.0018589 | 0.063218 | -0.0071769 | 0.053751 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063838 | 0.023861 | 0.058804 | -61.5142 | 0.0243 | -61.5909 | 60.0153 | 60.0072 | 59.9019 | -61.526 | -61.4544 | -0.17363 | -61.5805 | 59.8064 | 59.9797 | 59.9691 | -61.6943 | -0.007101 | -0.047897 | 0.004688 | -0.072001 | -0.0649 | -0.056006 | -0.16128 | -0.17543 | -0.25677 | 0.064464 | -0.061615 | 0.11382 | -0.083507 | -0.094042 | 121.5341 | 121.526 | 121.4207 | 61.5432 | -121.5891 | 121.3253 | 121.4985 | 121.488 | 61.3452 | -121.7575
891.4688 | 121.7377 | -61.5738 | 60.054 | 1.4211e-13 | -0.033196 | 0.0016453 | 0.063004 | -0.0073907 | 0.053751 | -0.0022892 | -0.0020893 | -0.0012713 | 0.063838 | 0.023861 | 0.058804 | -61.505 | 0.019721 | -61.5863 | 60.0199 | 60.0163 | 59.9065 | -61.5305 | -61.459 | -0.224 | -61.5713 | 59.811 | 59.9751 | 59.9646 | -61.6851 | 0.043252 | -0.034164 | 0.068777 | -0.012491 | -0.055743 | -0.037693 | -0.14755 | -0.11135 | -0.24304 | 0.11482 | 0.002474 | 0.11382 | -0.078931 | -0.089465 | 121.5936 | 121.5901 | 121.4803 | 61.5935 | -121.5846 | 121.3848 | 121.5489 | 121.5383 | 61.3498 | -121.7392
893.2188 | 121.7606 | -61.4822 | 60.1181 | 1.4211e-13 | -0.03341 | 0.0012179 | 0.063004 | -0.0069633 | 0.054179 | -0.0022892 | -0.0020893 | -0.0010577 | 0.063624 | 0.024075 | 0.059017 | -61.5096 | 0.028878 | -61.5817 | 60.0107 | 60.0072 | 59.9065 | -61.5214 | -61.4544 | -0.30641 | -61.5759 | 59.811 | 59.9842 | 59.9691 | -61.6943 | -0.039143 | -0.10741 | -0.027354 | -0.099465 | -0.060322 | -0.11094 | -0.21164 | -0.21205 | -0.30712 | 0.027843 | -0.093658 | 0.1184 | -0.13386 | -0.14897 | 121.4929 | 121.4894 | 121.3887 | 61.5111 | -121.6395 | 121.2932 | 121.4665 | 121.4514 | 61.1758 | -121.8124
894.9062 | 121.7468 | -61.5372 | 60.0677 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063004 | -0.0071769 | 0.053965 | -0.0022892 | -0.0016621 | -0.0010577 | 0.063838 | 0.024075 | 0.058804 | -61.5004 | 0.019721 | -61.5817 | 60.029 | 60.0163 | 59.9019 | -61.526 | -61.4544 | -0.39799 | -61.5622 | 59.811 | 59.9797 | 59.96 | -61.6943 | 0.011209 | -0.03874 | 0.036733 | -0.044534 | -0.055743 | -0.051426 | -0.16586 | -0.15712 | -0.25677 | 0.082774 | -0.024991 | 0.13213 | -0.088085 | -0.10778 | 121.5662 | 121.5535 | 121.4391 | 61.5569 | -121.5937 | 121.3481 | 121.5168 | 121.4971 | 61.1392 | -121.762
896.6562 | 121.8796 | -61.5417 | 59.9899 | 1.4211e-13 | -0.032983 | 0.0016453 | 0.063218 | -0.0069633 | 0.054179 | -0.0022892 | -0.0020893 | -0.0014849 | 0.063411 | 0.024075 | 0.058804 | -61.5004 | 0.0243 | -61.5863 | 60.0244 | 60.0163 | 59.9019 | -61.5168 | -61.4407 | -0.51246 | -61.5576 | 59.8064 | 59.9751 | 59.9691 | -61.6989 | 0.024944 | 0.034501 | 0.041311 | -0.044535 | -0.069479 | 0.026394 | -0.088043 | -0.15713 | -0.18353 | 0.10109 | -0.015834 | 0.14129 | -0.014844 | -0.0208 | 121.5662 | 121.5581 | 121.4436 | 61.566 | -121.5067 | 121.3481 | 121.5168 | 121.5109 | 61.0293 | -121.6888
898.4062 | 121.7651 | -61.5051 | 60.1181 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.063432 | -0.0073907 | 0.053965 | -0.0099192 | -0.0020893 | -0.0010577 | 0.064265 | 0.024288 | 0.058804 | -61.5096 | 0.0243 | -61.5771 | 60.0153 | 60.0163 | 59.9065 | -61.5305 | -61.4452 | -0.64066 | -61.5667 | 59.8156 | 59.9888 | 59.96 | -61.6943 | -0.025413 | -0.10283 | -0.004466 | -0.071999 | -0.046586 | -0.10178 | -0.21164 | -0.18917 | -0.30255 | 0.059888 | -0.061612 | 0.12756 | -0.12928 | -0.15813 | 121.5204 | 121.5215 | 121.4116 | 61.5294 | -121.6486 | 121.3207 | 121.4939 | 121.4651 | 60.8645 | -121.8124
900.1719 | 121.7606 | -61.5509 | 60.0494 | 1.4211e-13 | -0.033196 | 0.0020727 | 0.063218 | -0.0071769 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.064052 | 0.023861 | 0.059231 | -61.5004 | 0.019721 | -61.5725 | 60.0244 | 60.0163 | 59.9156 | -61.5214 | -61.4452 | -0.75055 | -61.5667 | 59.811 | 59.9797 | 59.9737 | -61.6897 | 0.029521 | -0.025008 | 0.050466 | -0.021645 | -0.051166 | -0.033115 | -0.13382 | -0.13881 | -0.23846 | 0.10566 | -0.015836 | 0.12298 | -0.069774 | -0.07573 | 121.5753 | 121.5672 | 121.4665 | 61.5706 | -121.5708 | 121.3619 | 121.5306 | 121.5246 | 60.8004 | -121.7392
901.8594 | 121.7926 | -61.5234 | 60.0677 | 1.4211e-13 | -0.033624 | 0.0014317 | 0.063432 | -0.0069633 | 0.053965 | -0.01755 | -0.0020893 | -0.0014849 | 0.063838 | 0.024075 | 0.058804 | -61.505 | 0.0243 | -61.5771 | 60.0199 | 60.0209 | 59.9156 | -61.526 | -61.4407 | -0.91996 | -61.5622 | 59.811 | 59.9842 | 59.9646 | -61.6851 | -0.002524 | -0.047897 | 0.018422 | -0.053689 | -0.051165 | -0.046847 | -0.15213 | -0.1617 | -0.25677 | 0.082777 | -0.038724 | 0.12298 | -0.083507 | -0.1032 | 121.5433 | 121.5443 | 121.4391 | 61.5477 | -121.5937 | 121.3344 | 121.5077 | 121.488 | 60.6035 | -121.7529
903.625 | 121.8887 | -61.4502 | 60.0632 | 1.4211e-13 | -0.033624 | 0.0014317 | 0.063218 | -0.0067497 | 0.053538 | -0.0022892 | -0.0020893 | -0.0014849 | 0.063838 | 0.024502 | 0.05859 | -61.4959 | 0.028878 | -61.5771 | 60.0244 | 60.0255 | 59.911 | -61.5122 | -61.4315 | -1.0756 | -61.5576 | 59.8201 | 59.9888 | 59.9783 | -61.6897 | -0.06203 | -0.038741 | -0.045663 | -0.12693 | -0.064901 | -0.03769 | -0.15213 | -0.23952 | -0.24304 | 0.018692 | -0.10739 | 0.13213 | -0.07435 | -0.084885 | 121.4746 | 121.4757 | 121.3612 | 61.4791 | -121.5754 | 121.2703 | 121.439 | 121.4285 | 60.3746 | -121.7529
905.3906 | 121.7743 | -61.4594 | 60.1318 | 1.4211e-13 | -0.03341 | 0.0012179 | 0.063218 | -0.0069633 | 0.053538 | -0.0022892 | -0.0018757 | -0.0012713 | 0.064052 | 0.024288 | 0.058804 | -61.505 | 0.028878 | -61.5771 | 60.0244 | 60.0255 | 59.911 | -61.5214 | -61.4269 | -1.2359 | -61.5576 | 59.8201 | 59.9842 | 59.9737 | -61.676 | -0.062031 | -0.10741 | -0.045664 | -0.11778 | -0.055744 | -0.10636 | -0.22079 | -0.21663 | -0.3117 | 0.032427 | -0.098231 | 0.1184 | -0.14759 | -0.15813 | 121.4838 | 121.4848 | 121.3704 | 61.4882 | -121.6532 | 121.2795 | 121.4436 | 121.4331 | 60.2235 | -121.8078
907.0781 | 121.8338 | -61.4502 | 60.1089 | 1.4211e-13 | -0.03341 | 0.0016453 | 0.063432 | -0.0067497 | 0.053751 | -0.0099192 | -0.0018757 | -0.0010577 | 0.064265 | 0.024288 | 0.058804 | -61.4959 | 0.019721 | -61.5725 | 60.0244 | 60.0255 | 59.9156 | -61.5122 | -61.4361 | -1.4053 | -61.5438 | 59.8247 | 59.9888 | 59.9737 | -61.6897 | -0.06203 | -0.084518 | -0.045663 | -0.12235 | -0.060323 | -0.083467 | -0.19333 | -0.23952 | -0.28423 | 0.014114 | -0.093651 | 0.14587 | -0.12013 | -0.13524 | 121.4746 | 121.4757 | 121.3658 | 61.4699 | -121.6212 | 121.2749 | 121.439 | 121.4239 | 60.0449 | -121.7987
908.8594 | 121.8704 | -61.4319 | 60.0952 | 1.4211e-13 | -0.03341 | 0.0014317 | 0.063004 | -0.0071769 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.024075 | 0.059017 | -61.5004 | 0.033457 | -61.5771 | 60.0199 | 60.0209 | 59.9202 | -61.5168 | -61.4223 | -1.5839 | -61.5484 | 59.8247 | 59.998 | 59.9737 | -61.676 | -0.084919 | -0.075363 | -0.068552 | -0.14524 | -0.060322 | -0.074313 | -0.17502 | -0.24409 | -0.2705 | 0.00954 | -0.11654 | 0.12756 | -0.097237 | -0.12151 | 121.4517 | 121.4528 | 121.3521 | 61.4653 | -121.612 | 121.2566 | 121.4299 | 121.4056 | 59.848 | -121.7712
910.5625 | 121.7468 | -61.5326 | 60.0723 | 1.4211e-13 | -0.033624 | 0.0012179 | 0.063218 | -0.0069633 | 0.053751 | -0.0099192 | -0.0023031 | -0.0010577 | 0.063624 | 0.024502 | 0.05859 | -61.4913 | 0.028878 | -61.5634 | 60.0382 | 60.0255 | 59.9156 | -61.5122 | -61.4269 | -1.7533 | -61.5438 | 59.8293 | 59.9888 | 59.9783 | -61.6851 | 0.020368 | -0.034162 | 0.041313 | -0.030798 | -0.051166 | -0.046846 | -0.15671 | -0.15254 | -0.24303 | 0.10567 | -0.011253 | 0.14129 | -0.083506 | -0.094041 | 121.5708 | 121.5581 | 121.4482 | 61.5615 | -121.5846 | 121.3619 | 121.5214 | 121.5109 | 59.7793 | -121.7575
912.3281 | 121.7834 | -61.4777 | 60.1044 | 1.4211e-13 | -0.03341 | 0.0014317 | 0.063432 | -0.0071769 | 0.053751 | -0.0022892 | -0.0018757 | -0.0012713 | 0.063838 | 0.023861 | 0.058804 | -61.4867 | 0.019721 | -61.568 | 60.0336 | 60.0346 | 59.9248 | -61.5122 | -61.4132 | -1.8998 | -61.5393 | 59.8293 | 59.9888 | 59.9874 | -61.6714 | -0.034564 | -0.070783 | -0.00904 | -0.090309 | -0.055745 | -0.069731 | -0.17959 | -0.19374 | -0.27508 | 0.064473 | -0.061606 | 0.13213 | -0.11555 | -0.11693 | 121.5112 | 121.5123 | 121.4024 | 61.4974 | -121.6166 | 121.307 | 121.4665 | 121.4651 | 59.5779 | -121.7758
914.0781 | 121.8292 | -61.4822 | 60.0723 | 1.4211e-13 | -0.033624 | 0.0014317 | 0.063004 | -0.0071769 | 0.053965 | -0.0022892 | -0.0020893 | -0.0010577 | 0.064052 | 0.023861 | 0.058804 | -61.4821 | 0.0243 | -61.568 | 60.0382 | 60.0346 | 59.9248 | -61.5076 | -61.4132 | -2.0738 | -61.5347 | 59.8339 | 59.9934 | 59.9783 | -61.6806 | -0.025407 | -0.034162 | 0.000116 | -0.085731 | -0.060324 | -0.037688 | -0.14755 | -0.19832 | -0.23846 | 0.069051 | -0.052449 | 0.14587 | -0.078928 | -0.094041 | 121.5204 | 121.5169 | 121.407 | 61.5065 | -121.58 | 121.3161 | 121.4756 | 121.4605 | 59.4084 | -121.7529
915.7812 | 121.7972 | -61.4777 | 60.0952 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063432 | -0.0071769 | 0.053965 | -0.0022892 | -0.0016621 | -0.0014849 | 0.064052 | 0.024075 | 0.059017 | -61.4913 | 0.019721 | -61.5634 | 60.0382 | 60.0301 | 59.9294 | -61.5031 | -61.404 | -2.2295 | -61.5255 | 59.8247 | 60.0026 | 59.9783 | -61.676 | -0.025406 | -0.05705 | -0.013619 | -0.08573 | -0.060324 | -0.065155 | -0.16586 | -0.19832 | -0.2705 | 0.073631 | -0.04787 | 0.15045 | -0.092658 | -0.11693 | 121.5158 | 121.5077 | 121.407 | 61.4974 | -121.5983 | 121.3024 | 121.4802 | 121.4559 | 59.2482 | -121.7712
917.5312 | 121.7514 | -61.4685 | 60.141 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.062791 | -0.0071769 | 0.053751 | -0.01755 | -0.0018757 | -0.0010577 | 0.063838 | 0.024075 | 0.058804 | -61.473 | 0.028878 | -61.5497 | 60.0565 | 60.053 | 59.9385 | -61.4939 | -61.3857 | -2.408 | -61.5164 | 59.843 | 60.0026 | 59.9966 | -61.6622 | -0.025403 | -0.084512 | -0.00446 | -0.08115 | -0.055747 | -0.088037 | -0.20248 | -0.19374 | -0.29796 | 0.082791 | -0.047867 | 0.14587 | -0.13843 | -0.14439 | 121.525 | 121.5215 | 121.407 | 61.4974 | -121.6349 | 121.3115 | 121.4711 | 121.4651 | 59.0605 | -121.8032
919.2188 | 121.756 | -61.4456 | 60.1547 | 1.4211e-13 | -0.033837 | 0.0012179 | 0.063432 | -0.0069633 | 0.053751 | -0.0099192 | -0.0018757 | -0.0010577 | 0.063838 | 0.023861 | 0.059231 | -61.473 | 0.0243 | -61.5405 | 60.0565 | 60.053 | 59.9431 | -61.4802 | -61.3766 | -2.5958 | -61.4981 | 59.8522 | 60.0209 | 60.0058 | -61.6531 | -0.034554 | -0.098245 | -0.027348 | -0.094882 | -0.060328 | -0.10177 | -0.21163 | -0.20747 | -0.30254 | 0.06906 | -0.052441 | 0.15503 | -0.13385 | -0.14897 | 121.5021 | 121.4986 | 121.3887 | 61.4699 | -121.6349 | 121.2978 | 121.4665 | 121.4514 | 58.8498 | -121.8078
920.9688 | 121.7789 | -61.4868 | 60.0952 | 1.4211e-13 | -0.03341 | 0.0014317 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0018757 | -0.0014849 | 0.064052 | 0.023861 | 0.058804 | -61.4592 | 0.019721 | -61.5405 | 60.0611 | 60.0667 | 59.9614 | -61.4756 | -61.3628 | -2.7652 | -61.4889 | 59.8613 | 60.0254 | 60.0241 | -61.6485 | 0.011223 | -0.034158 | 0.027585 | -0.053684 | -0.064907 | -0.028524 | -0.13381 | -0.16169 | -0.23387 | 0.12399 | -0.002085 | 0.1596 | -0.069765 | -0.071143 | 121.5479 | 121.5535 | 121.4482 | 61.5065 | -121.5708 | 121.3482 | 121.5123 | 121.5109 | 58.7216 | -121.7437
922.7188 | 121.8155 | -61.4548 | 60.1273 | 1.4211e-13 | -0.034051 | 0.0014317 | 0.062791 | -0.0071769 | 0.053751 | -0.01755 | -0.0018757 | -0.0012713 | 0.063197 | 0.024075 | 0.058804 | -61.4501 | 0.028878 | -61.5313 | 60.0702 | 60.0713 | 59.9614 | -61.4619 | -61.3491 | -2.9209 | -61.4706 | 59.8705 | 60.0346 | 60.0195 | -61.6348 | -0.007083 | -0.057044 | 0.004699 | -0.07657 | -0.069487 | -0.055988 | -0.16585 | -0.18 | -0.25676 | 0.10569 | -0.015813 | 0.16418 | -0.092651 | -0.10776 | 121.525 | 121.526 | 121.4162 | 61.4837 | -121.5891 | 121.3253 | 121.4894 | 121.4743 | 58.5339 | -121.762
924.4062 | 121.875 | -61.4685 | 60.0311 | 1.4211e-13 | -0.033624 | 0.0018589 | 0.063432 | -0.0073907 | 0.053751 | -0.0099192 | -0.0016621 | -0.0010577 | 0.063624 | 0.024288 | 0.05859 | -61.4363 | 0.0243 | -61.5222 | 60.0748 | 60.0804 | 59.966 | -61.4619 | -61.3262 | -3.0491 | -61.4569 | 59.8705 | 60.0392 | 60.0241 | -61.6348 | 0.00665 | 0.043665 | 0.032167 | -0.053681 | -0.060331 | 0.0493 | -0.065142 | -0.16626 | -0.16063 | 0.14231 | 0.011656 | 0.17792 | 0.008058 | -0.007056 | 121.5433 | 121.5489 | 121.4345 | 61.4928 | -121.493 | 121.339 | 121.5077 | 121.4926 | 58.4194 | -121.6659
926.1562 | 121.7743 | -61.4639 | 60.141 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063432 | -0.0069633 | 0.053751 | -0.0099192 | -0.0018757 | -0.0012713 | 0.064052 | 0.024075 | 0.058804 | -61.4409 | 0.0243 | -61.5176 | 60.0839 | 60.0804 | 59.9706 | -61.4619 | -61.3308 | -3.159 | -61.4523 | 59.8751 | 60.0483 | 60.0287 | -61.6256 | 0.002072 | -0.057042 | 0.02301 | -0.05368 | -0.055752 | -0.060563 | -0.17043 | -0.16168 | -0.26591 | 0.13316 | 0.011656 | 0.17334 | -0.092648 | -0.11234 | 121.5479 | 121.5444 | 121.4345 | 61.4882 | -121.6028 | 121.339 | 121.5123 | 121.4926 | 58.305 | -121.7666
927.9062 | 121.8933 | -61.4227 | 60.1181 | 1.4211e-13 | -0.033837 | 0.0018589 | 0.063218 | -0.0071769 | 0.053751 | -0.0022892 | -0.0020893 | -0.0014849 | 0.063624 | 0.024288 | 0.058804 | -61.4363 | 0.019721 | -61.513 | 60.0885 | 60.0896 | 59.9706 | -61.4527 | -61.3216 | -3.31 | -61.4385 | 59.8888 | 60.0483 | 60.0332 | -61.621 | -0.02997 | -0.029575 | -0.01361 | -0.090301 | -0.060331 | -0.028517 | -0.14754 | -0.1983 | -0.22929 | 0.10112 | -0.015806 | 0.1825 | -0.06976 | -0.084873 | 121.5113 | 121.5123 | 121.3933 | 61.4424 | -121.5708 | 121.3115 | 121.4711 | 121.456 | 58.1127 | -121.7391
929.6562 | 121.8338 | -61.4273 | 60.141 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063432 | -0.0071769 | 0.054179 | -0.01755 | -0.0020893 | -0.0014849 | 0.063411 | 0.023861 | 0.059017 | -61.4272 | 0.028878 | -61.5085 | 60.0931 | 60.0987 | 59.9889 | -61.4481 | -61.2987 | -3.4337 | -61.4248 | 59.8888 | 60.0621 | 60.0378 | -61.6165 | -0.020813 | -0.047885 | 0.000125 | -0.081145 | -0.060332 | -0.042247 | -0.15211 | -0.18915 | -0.25218 | 0.12859 | 0.002508 | 0.19165 | -0.078912 | -0.10318 | 121.5204 | 121.5261 | 121.4162 | 61.4562 | -121.5891 | 121.3161 | 121.4894 | 121.4651 | 57.9936 | -121.7574
931.3594 | 121.7422 | -61.3953 | 60.2005 | 1.4211e-13 | -0.033624 | 0.0014317 | 0.064073 | -0.0071769 | 0.054179 | -0.0099192 | -0.0020893 | -0.0010577 | 0.064052 | 0.024502 | 0.05859 | -61.4318 | 0.028878 | -61.4993 | 60.1068 | 60.0987 | 59.9843 | -61.4435 | -61.285 | -3.571 | -61.4202 | 59.898 | 60.0575 | 60.0561 | -61.621 | -0.048277 | -0.093659 | -0.036497 | -0.10403 | -0.055754 | -0.10176 | -0.2162 | -0.22577 | -0.30253 | 0.11028 | -0.024957 | 0.20081 | -0.143 | -0.14438 | 121.5021 | 121.494 | 121.3796 | 61.4241 | -121.644 | 121.2932 | 121.4528 | 121.4514 | 57.8242 | -121.8215
933.1094 | 121.8704 | -61.4548 | 60.0815 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063218 | -0.0073907 | 0.053751 | -0.0099192 | -0.0016621 | -0.0010577 | 0.064052 | 0.023861 | 0.059017 | -61.418 | 0.0243 | -61.4901 | 60.1068 | 60.1079 | 60.0026 | -61.4344 | -61.2758 | -3.7908 | -61.4019 | 59.9071 | 60.0712 | 60.0607 | -61.6027 | 0.02039 | 0.025359 | 0.036747 | -0.035366 | -0.055756 | 0.026419 | -0.078867 | -0.14794 | -0.17436 | 0.17895 | 0.052867 | 0.20081 | -0.010246 | -0.020781 | 121.5616 | 121.5627 | 121.4574 | 61.4791 | -121.5159 | 121.3619 | 121.526 | 121.5155 | 57.664 | -121.6842
934.7969 | 121.8658 | -61.3998 | 60.1318 | 1.4211e-13 | -0.033837 | 0.0014317 | 0.063645 | -0.0071769 | 0.053965 | -0.0022892 | -0.0018757 | -0.0014849 | 0.064265 | 0.024075 | 0.058804 | -61.4089 | 0.028878 | -61.4901 | 60.116 | 60.1079 | 60.0072 | -61.4115 | -61.2575 | -3.9419 | -61.3973 | 59.9117 | 60.085 | 60.0653 | -61.589 | -0.011647 | -0.015838 | -0.009028 | -0.090298 | -0.078651 | -0.023935 | -0.12464 | -0.18914 | -0.22013 | 0.14233 | 0.002514 | 0.19165 | -0.046864 | -0.066556 | 121.5158 | 121.5077 | 121.407 | 61.4287 | -121.5433 | 121.3115 | 121.4848 | 121.4651 | 57.4579 | -121.7208
936.5625 | 121.7651 | -61.409 | 60.2051 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063432 | -0.0071769 | 0.053751 | -0.0022892 | -0.0018757 | -0.0014849 | 0.063838 | 0.024075 | 0.058804 | -61.4089 | 0.028878 | -61.4764 | 60.1252 | 60.1216 | 60.0072 | -61.4206 | -61.2438 | -4.0976 | -61.3927 | 59.9163 | 60.0758 | 60.0607 | -61.5936 | -0.011649 | -0.079923 | 0.000128 | -0.067407 | -0.055758 | -0.08344 | -0.19788 | -0.18456 | -0.2888 | 0.16522 | 0.016249 | 0.20081 | -0.12926 | -0.14438 | 121.5342 | 121.5306 | 121.4162 | 61.4379 | -121.6257 | 121.3253 | 121.4848 | 121.4697 | 57.3114 | -121.7986
938.3281 | 121.7514 | -61.3953 | 60.2234 | 1.4211e-13 | -0.034051 | 0.0016453 | 0.063432 | -0.0071769 | 0.053538 | 0.0053413 | -0.0018757 | -0.00063026 | 0.064052 | 0.024288 | 0.058804 | -61.4043 | 0.019721 | -61.4764 | 60.1206 | 60.1216 | 60.0118 | -61.4161 | -61.2346 | -4.2395 | -61.3653 | 59.9163 | 60.0804 | 60.0699 | -61.589 | -0.020803 | -0.10281 | -0.009026 | -0.08114 | -0.060337 | -0.10175 | -0.21162 | -0.19372 | -0.30711 | 0.16065 | 0.029988 | 0.2237 | -0.143 | -0.15353 | 121.5158 | 121.5169 | 121.407 | 61.415 | -121.6395 | 121.3115 | 121.4757 | 121.4651 | 57.1557 | -121.8124
940.0312 | 121.7377 | -61.377 | 60.2051 | 1.4211e-13 | -0.03341 | 0.0014317 | 0.063432 | -0.0073907 | 0.054179 | -0.0099192 | -0.0020893 | -0.0012713 | 0.063838 | 0.024716 | 0.059017 | -61.4043 | 0.0243 | -61.4672 | 60.1252 | 60.1216 | 60.0164 | -61.4252 | -61.2255 | -4.4044 | -61.3699 | 59.9117 | 60.0758 | 60.0699 | -61.5844 | -0.048272 | -0.079923 | -0.027337 | -0.090294 | -0.042022 | -0.08344 | -0.18873 | -0.20745 | -0.29337 | 0.15149 | 0.007098 | 0.21455 | -0.12926 | -0.13522 | 121.5021 | 121.4986 | 121.3933 | 61.4013 | -121.6303 | 121.2887 | 121.4528 | 121.4468 | 56.9726 | -121.7895
941.7812 | 121.8567 | -61.377 | 60.1547 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063004 | -0.0076043 | 0.053751 | -0.0022892 | -0.0016621 | -0.0014849 | 0.063838 | 0.024288 | 0.059445 | -61.3951 | 0.028878 | -61.4764 | 60.1252 | 60.1262 | 60.0164 | -61.4115 | -61.2163 | -4.5829 | -61.3607 | 59.9254 | 60.0896 | 60.0744 | -61.5844 | -0.034535 | -0.029569 | -0.018181 | -0.099451 | -0.064916 | -0.028507 | -0.13837 | -0.20745 | -0.22928 | 0.16065 | 0.016256 | 0.22371 | -0.065174 | -0.080287 | 121.5021 | 121.5032 | 121.3933 | 61.4058 | -121.5662 | 121.3024 | 121.4665 | 121.4514 | 56.794 | -121.7391
943.5312 | 121.8109 | -61.4227 | 60.1181 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063432 | -0.0071769 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.063838 | 0.024075 | 0.058804 | -61.3951 | 0.028878 | -61.4764 | 60.1252 | 60.1262 | 60.0164 | -61.4161 | -61.2026 | -4.7707 | -61.3515 | 59.9163 | 60.085 | 60.0699 | -61.589 | 0.006662 | 0.007052 | 0.027595 | -0.053675 | -0.060337 | 0.008114 | -0.10175 | -0.16625 | -0.20182 | 0.22016 | 0.071189 | 0.23744 | -0.033131 | -0.048245 | 121.5479 | 121.5489 | 121.4391 | 61.4516 | -121.5342 | 121.339 | 121.5077 | 121.4926 | 56.6521 | -121.7071
945.2812 | 121.8338 | -61.3998 | 60.141 | 1.4211e-13 | -0.03341 | 0.0014317 | 0.063218 | -0.0071769 | 0.053751 | -0.0099192 | -0.0018757 | -0.0014849 | 0.064265 | 0.024288 | 0.059017 | -61.4043 | 0.028878 | -61.4764 | 60.1297 | 60.1308 | 60.0118 | -61.4206 | -61.2026 | -5.0545 | -61.3378 | 59.9163 | 60.0804 | 60.0699 | -61.5981 | -0.020805 | -0.011258 | -0.004449 | -0.076563 | -0.055758 | -0.010195 | -0.12922 | -0.1983 | -0.22471 | 0.19727 | 0.062037 | 0.26034 | -0.060598 | -0.071133 | 121.5296 | 121.5306 | 121.4116 | 61.4287 | -121.5616 | 121.3161 | 121.4802 | 121.4697 | 56.3453 | -121.7391
947.0312 | 121.788 | -61.409 | 60.1959 | 1.4211e-13 | -0.033837 | 0.0014317 | 0.063218 | -0.0071769 | 0.053751 | -0.01755 | -0.0018757 | -0.0010577 | 0.063838 | 0.024288 | 0.059231 | -61.4134 | 0.028878 | -61.481 | 60.116 | 60.1171 | 60.0118 | -61.4206 | -61.1934 | -5.256 | -61.3424 | 59.9071 | 60.085 | 60.0653 | -61.5981 | -0.011649 | -0.079925 | -0.00445 | -0.071985 | -0.060336 | -0.078864 | -0.18415 | -0.18914 | -0.2888 | 0.21559 | 0.066615 | 0.25576 | -0.11095 | -0.13064 | 121.525 | 121.5261 | 121.4208 | 61.4379 | -121.6166 | 121.3161 | 121.494 | 121.4743 | 56.153 | -121.7941
948.7344 | 121.7789 | -61.409 | 60.173 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063432 | -0.0073907 | 0.053965 | -0.02518 | -0.0018757 | -0.0012713 | 0.064052 | 0.024502 | 0.059017 | -61.418 | 0.028878 | -61.481 | 60.1206 | 60.1125 | 59.998 | -61.4252 | -61.1888 | -5.4025 | -61.3378 | 59.9071 | 60.0758 | 60.0607 | -61.6027 | -0.016228 | -0.052459 | -0.009029 | -0.071985 | -0.055757 | -0.060555 | -0.175 | -0.19372 | -0.26591 | 0.22017 | 0.071193 | 0.26491 | -0.097221 | -0.11233 | 121.5296 | 121.5215 | 121.407 | 61.4379 | -121.5983 | 121.3161 | 121.4848 | 121.4697 | 56.0065 | -121.7758
950.5 | 121.8292 | -61.377 | 60.1501 | 1.4211e-13 | -0.034051 | 0.0016453 | 0.063004 | -0.0071769 | 0.053965 | -0.01755 | -0.0020893 | -0.00084406 | 0.063838 | 0.024502 | 0.059231 | -61.4134 | 0.0243 | -61.4901 | 60.1068 | 60.1125 | 60.0026 | -61.4298 | -61.1705 | -5.636 | -61.3241 | 59.9025 | 60.0758 | 60.0561 | -61.5981 | -0.052851 | -0.043305 | -0.036494 | -0.11319 | -0.060335 | -0.037666 | -0.14753 | -0.22119 | -0.2476 | 0.20644 | 0.052885 | 0.27407 | -0.074332 | -0.094023 | 121.4838 | 121.4894 | 121.3796 | 61.4013 | -121.5799 | 121.2795 | 121.4528 | 121.4331 | 55.7409 | -121.7483
952.25 | 121.8521 | -61.4456 | 60.0769 | 1.4211e-13 | -0.033624 | 0.0018589 | 0.063432 | -0.0073907 | 0.053965 | -0.0099192 | -0.0018757 | -0.0012713 | 0.064052 | 0.024502 | 0.058804 | -61.4226 | 0.0243 | -61.4901 | 60.1068 | 60.1171 | 59.998 | -61.4252 | -61.1568 | -5.9657 | -61.3149 | 59.9071 | 60.0621 | 60.0515 | -61.6027 | 0.020393 | 0.029937 | 0.023014 | -0.044521 | -0.064914 | 0.040155 | -0.078867 | -0.1571 | -0.16978 | 0.28884 | 0.13071 | 0.28781 | -0.014825 | -0.02536 | 121.5525 | 121.5627 | 121.4437 | 61.4699 | -121.5021 | 121.3527 | 121.5077 | 121.4972 | 55.4799 | -121.6796
953.9375 | 121.8338 | -61.3953 | 60.1456 | 1.4211e-13 | -0.034265 | 0.0014317 | 0.063004 | -0.0071769 | 0.053751 | -0.0099192 | -0.0020893 | -0.0010577 | 0.063838 | 0.024502 | 0.059231 | -61.418 | 0.028878 | -61.4947 | 60.1114 | 60.1125 | 60.0026 | -61.4298 | -61.1476 | -6.1443 | -61.3012 | 59.9163 | 60.0575 | 60.0607 | -61.6073 | -0.03454 | -0.034149 | -0.022762 | -0.099453 | -0.064913 | -0.033089 | -0.14295 | -0.21203 | -0.22929 | 0.24764 | 0.09409 | 0.30612 | -0.088069 | -0.084868 | 121.5067 | 121.5077 | 121.3979 | 61.4241 | -121.5754 | 121.3115 | 121.4528 | 121.456 | 55.251 | -121.7529
955.6875 | 121.7422 | -61.4548 | 60.1181 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063432 | -0.0073907 | 0.053751 | -0.01755 | -0.0018757 | -0.00063026 | 0.064052 | 0.024502 | 0.058804 | -61.4134 | 0.028878 | -61.4856 | 60.1114 | 60.1125 | 60.0026 | -61.4344 | -61.1247 | -6.451 | -61.2874 | 59.9025 | 60.0712 | 60.0607 | -61.6073 | 0.02039 | -0.006683 | 0.041326 | -0.030787 | -0.051177 | -0.005623 | -0.11549 | -0.15252 | -0.21555 | 0.33004 | 0.16734 | 0.31986 | -0.046867 | -0.057402 | 121.5662 | 121.5673 | 121.4574 | 61.4837 | -121.5525 | 121.3573 | 121.526 | 121.5155 | 55.0037 | -121.7254
957.4375 | 121.7789 | -61.377 | 60.1822 | 1.4211e-13 | -0.033837 | 0.0014317 | 0.063004 | -0.0073907 | 0.053751 | -0.01755 | -0.0020893 | -0.0012713 | 0.064052 | 0.024288 | 0.059017 | -61.4318 | 0.0243 | -61.4947 | 60.1023 | 60.0987 | 59.9935 | -61.439 | -61.1247 | -6.7487 | -61.2874 | 59.898 | 60.0621 | 60.047 | -61.6165 | -0.062009 | -0.079927 | -0.054808 | -0.11776 | -0.055755 | -0.083446 | -0.18873 | -0.2395 | -0.28422 | 0.25222 | 0.089515 | 0.32902 | -0.12011 | -0.13522 | 121.4792 | 121.4757 | 121.3704 | 61.4013 | -121.6212 | 121.2749 | 121.439 | 121.4239 | 54.6283 | -121.7986
959.1875 | 121.8018 | -61.441 | 60.1639 | 1.4211e-13 | -0.033624 | 0.0018589 | 0.063004 | -0.0069633 | 0.053965 | 0.0053413 | -0.0018757 | -0.0010577 | 0.063838 | 0.024502 | 0.058804 | -61.4409 | 0.028878 | -61.5039 | 60.0977 | 60.0987 | 59.9889 | -61.4481 | -61.111 | -6.9547 | -61.2783 | 59.8842 | 60.0483 | 60.0424 | -61.621 | -0.00708 | -0.066195 | 0.000122 | -0.062834 | -0.055754 | -0.065135 | -0.175 | -0.17999 | -0.27965 | 0.33005 | 0.16276 | 0.34275 | -0.11554 | -0.12149 | 121.5387 | 121.5398 | 121.4299 | 61.4699 | -121.612 | 121.3253 | 121.4894 | 121.4834 | 54.4863 | -121.7849
960.8906 | 121.7468 | -61.5051 | 60.1273 | 1.4211e-13 | -0.033624 | 0.0016453 | 0.063218 | -0.0071769 | 0.054179 | 0.0053413 | -0.0018757 | -0.0010577 | 0.064052 | 0.024288 | 0.059017 | -61.4363 | 0.028878 | -61.513 | 60.0885 | 60.0896 | 59.9843 | -61.4619 | -61.0973 | -7.1882 | -61.2691 | 59.8797 | 60.0483 | 60.0378 | -61.621 | 0.043271 | -0.03873 | 0.068788 | -0.007903 | -0.051174 | -0.037672 | -0.14296 | -0.11591 | -0.2476 | 0.40787 | 0.236 | 0.35191 | -0.078915 | -0.08945 | 121.5937 | 121.5947 | 121.4894 | 61.534 | -121.5891 | 121.3848 | 121.5535 | 121.5429 | 54.3169 | -121.7483
962.6562 | 121.8201 | -61.4456 | 60.1089 | 1.4211e-13 | -0.033837 | 0.0012179 | 0.063004 | -0.0067497 | 0.053751 | -0.0022892 | -0.0023031 | -0.0010577 | 0.064265 | 0.024288 | 0.058804 | -61.4409 | 0.015142 | -61.5176 | 60.0794 | 60.085 | 59.9797 | -61.4573 | -61.0835 | -7.4858 | -61.26 | 59.8751 | 60.0438 | 60.0241 | -61.6348 | -0.01166 | -0.029577 | 0.0047 | -0.07199 | -0.06033 | -0.023941 | -0.12923 | -0.18915 | -0.23387 | 0.3621 | 0.18565 | 0.3748 | -0.065184 | -0.084876 | 121.525 | 121.5306 | 121.4253 | 61.4608 | -121.5662 | 121.3207 | 121.4894 | 121.4697 | 53.9598 | -121.7437
964.3438 | 121.8246 | -61.441 | 60.0861 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063218 | -0.0076043 | 0.053751 | 0.0053413 | -0.0016621 | -0.00084406 | 0.064265 | 0.024502 | 0.059017 | -61.4455 | 0.015142 | -61.5222 | 60.0839 | 60.0804 | 59.9614 | -61.4619 | -61.0606 | -7.7514 | -61.2508 | 59.8751 | 60.0392 | 60.0241 | -61.6439 | -0.020816 | -0.002111 | -0.004456 | -0.081147 | -0.060331 | -0.005632 | -0.12465 | -0.20289 | -0.21098 | 0.38041 | 0.19023 | 0.39312 | -0.046874 | -0.061988 | 121.525 | 121.5215 | 121.4024 | 61.4562 | -121.5479 | 121.3161 | 121.4802 | 121.4651 | 53.6896 | -121.73
966.0938 | 121.8658 | -61.4639 | 60.054 | 1.4211e-13 | -0.033837 | 0.0014317 | 0.062791 | -0.0069633 | 0.053538 | -0.0099192 | -0.0018757 | -0.00084406 | 0.064265 | 0.024502 | 0.059017 | -61.4501 | 0.033457 | -61.5313 | 60.0748 | 60.0758 | 59.9706 | -61.4664 | -61.0423 | -8.049 | -61.2462 | 59.8705 | 60.0254 | 60.0195 | -61.6393 | -0.002507 | 0.020777 | 0.013854 | -0.067415 | -0.064908 | 0.021833 | -0.083451 | -0.17542 | -0.18352 | 0.42162 | 0.2177 | 0.39312 | -0.028566 | -0.034522 | 121.5387 | 121.5398 | 121.4345 | 61.4974 | -121.5205 | 121.3344 | 121.4894 | 121.4834 | 53.4149 | -121.6934
967.8594 | 121.8292 | -61.409 | 60.1364 | 1.4211e-13 | -0.033837 | 0.0018589 | 0.063218 | -0.0073907 | 0.053751 | -0.0022892 | -0.0018757 | -0.00084406 | 0.064052 | 0.024502 | 0.059231 | -61.473 | 0.0243 | -61.5451 | 60.0519 | 60.0484 | 59.9431 | -61.4848 | -61.0423 | -8.3375 | -61.2417 | 59.8522 | 60.0117 | 59.9966 | -61.6622 | -0.075754 | -0.084513 | -0.063969 | -0.13608 | -0.060327 | -0.088039 | -0.19332 | -0.25325 | -0.28423 | 0.36668 | 0.16735 | 0.42059 | -0.1247 | -0.13981 | 121.4609 | 121.4574 | 121.3521 | 61.4333 | -121.6212 | 121.2612 | 121.4207 | 121.4056 | 53.0715 | -121.7987
969.5625 | 121.756 | -61.5051 | 60.1044 | 1.4211e-13 | -0.034265 | 0.0016453 | 0.062791 | -0.0073907 | 0.053965 | -0.0022892 | -0.0018757 | -0.00084406 | 0.064265 | 0.024716 | 0.059017 | -61.5096 | 0.0243 | -61.5909 | 60.0153 | 60.0117 | 59.9065 | -61.5351 | -61.0606 | -8.6076 | -61.2737 | 59.8064 | 59.9659 | 59.9554 | -61.7035 | -0.029992 | -0.089096 | -0.004466 | -0.085734 | -0.055742 | -0.092626 | -0.19791 | -0.19832 | -0.29797 | 0.4445 | 0.23143 | 0.42975 | -0.13844 | -0.14898 | 121.5204 | 121.5169 | 121.4116 | 61.5294 | -121.6395 | 121.3115 | 121.4711 | 121.4605 | 52.8975 | -121.8078
971.3281 | 121.7468 | -61.528 | 60.0952 | 1.4211e-13 | -0.034051 | 0.0018589 | 0.063432 | -0.0071769 | 0.053751 | -0.0022892 | -0.0016621 | -0.0010577 | 0.064265 | 0.024716 | 0.059445 | -61.5462 | 0.028878 | -61.6138 | 59.9786 | 59.9797 | 59.8744 | -61.5626 | -61.0652 | -8.9968 | -61.2737 | 59.7835 | 59.9476 | 59.9371 | -61.7355 | -0.034578 | -0.11657 | -0.018205 | -0.085737 | -0.051159 | -0.11552 | -0.2208 | -0.20749 | -0.31171 | 0.46281 | 0.25431 | 0.4618 | -0.1476 | -0.15814 | 121.5067 | 121.5077 | 121.4024 | 61.5569 | -121.6578 | 121.3115 | 121.4756 | 121.4651 | 52.5312 | -121.8307
973.0938 | 121.8979 | -61.528 | 60.0128 | 1.4211e-13 | -0.034051 | 0.0014317 | 0.063218 | -0.0071769 | 0.053751 | -0.0099192 | -0.0018757 | -0.0010577 | 0.064693 | 0.024716 | 0.059231 | -61.5554 | 0.0243 | -61.6321 | 59.9695 | 59.966 | 59.8653 | -61.5718 | -61.0423 | -9.4043 | -61.2691 | 59.7652 | 59.9247 | 59.9188 | -61.7538 | -0.043736 | -0.043327 | -0.027362 | -0.10405 | -0.060314 | -0.046862 | -0.14756 | -0.2258 | -0.24762 | 0.4857 | 0.25889 | 0.4847 | -0.088097 | -0.094052 | 121.4975 | 121.494 | 121.3933 | 61.5523 | -121.5846 | 121.2932 | 121.4527 | 121.4468 | 52.1237 | -121.7666
974.8594 | 121.8658 | -61.528 | 60.0082 | 1.4211e-13 | -0.034265 | 0.0014317 | 0.063004 | -0.0071769 | 0.053538 | -0.0022892 | -0.0016621 | -0.00084406 | 0.064052 | 0.024288 | 0.059231 | -61.5737 | 0.0243 | -61.655 | 59.9466 | 59.9522 | 59.8424 | -61.5946 | -61.0286 | -9.7981 | -61.2737 | 59.7469 | 59.9064 | 59.8959 | -61.7676 | -0.06663 | -0.061642 | -0.045676 | -0.12694 | -0.060312 | -0.056022 | -0.16588 | -0.23954 | -0.26136 | 0.49944 | 0.25431 | 0.49385 | -0.10183 | -0.11237 | 121.4746 | 121.4802 | 121.3704 | 61.5523 | -121.6029 | 121.2749 | 121.4344 | 121.4239 | 51.7299 | -121.7758
976.5625 | 121.875 | -61.7294 | 59.8206 | 1.4211e-13 | -0.034265 | 0.0016453 | 0.063218 | -0.0073907 | 0.053751 | -0.0099192 | -0.0018757 | -0.0010577 | 0.064693 | 0.024716 | 0.059017 | -61.6515 | 0.019721 | -61.7282 | 59.8688 | 59.8652 | 59.7645 | -61.6725 | -61.0835 | -10.1964 | -61.3286 | 59.6736 | 59.8194 | 59.8135 | -61.8546 | 0.056944 | 0.048208 | 0.077908 | 0.001222 | -0.055722 | 0.044661 | -0.056029 | -0.12512 | -0.14693 | 0.64591 | 0.40078 | 0.52591 | -0.001144 | -0.0071 | 121.5982 | 121.5946 | 121.494 | 61.7492 | -121.493 | 121.4031 | 121.5488 | 121.5429 | 51.533 | -121.6751
978.3125 | 121.7651 | -61.9171 | 59.7107 | 1.4211e-13 | -0.034051 | 0.0014317 | 0.063432 | -0.0069633 | 0.053751 | -0.0099192 | -0.0018757 | -0.00063026 | 0.064479 | 0.024929 | 0.059231 | -61.7843 | 0.019721 | -61.8564 | 59.7451 | 59.7416 | 59.6363 | -61.8007 | -61.1705 | -10.6497 | -61.4431 | 59.5317 | 59.7004 | 59.6898 | -61.9828 | 0.11642 | 0.034456 | 0.13282 | 0.060713 | -0.055704 | 0.030894 | -0.074366 | -0.065646 | -0.179 | 0.7466 | 0.474 | 0.53965 | -0.010324 | -0.020859 | 121.6623 | 121.6587 | 121.5534 | 61.9368 | -121.5114 | 121.4488 | 121.6175 | 121.6069 | 51.2674 | -121.6935
980 | 121.7834 | -61.6974 | 59.8846 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063218 | -0.0073907 | 0.053751 | -0.0022892 | -0.0020893 | -0.0012713 | 0.064265 | 0.024716 | 0.059017 | -61.7477 | 0.019721 | -61.8289 | 59.7635 | 59.7691 | 59.6638 | -61.7824 | -61.1064 | -11.0847 | -61.3836 | 59.5637 | 59.7324 | 59.7219 | -61.9461 | -0.084993 | -0.12118 | -0.050282 | -0.13154 | -0.046551 | -0.11558 | -0.22085 | -0.24874 | -0.32091 | 0.59097 | 0.3138 | 0.56254 | -0.15223 | -0.16276 | 121.4608 | 121.4664 | 121.3612 | 61.7171 | -121.667 | 121.2611 | 121.4298 | 121.4193 | 50.6127 | -121.8308
981.7656 | 121.875 | -61.7477 | 59.7656 | 1.4211e-13 | -0.033837 | 0.0010043 | 0.063432 | -0.0076043 | 0.053751 | -0.0022892 | -0.0018757 | -0.00041666 | 0.064693 | 0.024502 | 0.059017 | -61.7522 | 0.028878 | -61.8244 | 59.768 | 59.7645 | 59.6638 | -61.7778 | -61.0606 | -11.483 | -61.3653 | 59.5683 | 59.7324 | 59.7127 | -61.9415 | -0.03006 | 0.002416 | -0.004506 | -0.076611 | -0.046551 | -0.001143 | -0.10183 | -0.19381 | -0.19731 | 0.68712 | 0.38247 | 0.57627 | -0.033206 | -0.052898 | 121.5158 | 121.5122 | 121.4115 | 61.7766 | -121.5434 | 121.3161 | 121.4802 | 121.4605 | 50.2647 | -121.7072
983.4531 | 121.8521 | -61.7569 | 59.7885 | 1.4211e-13 | -0.034265 | 0.0016453 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0018757 | -0.00063026 | 0.064693 | 0.024929 | 0.059445 | -61.7568 | 0.0243 | -61.8289 | 59.7635 | 59.7691 | 59.6592 | -61.7686 | -61.0194 | -11.9363 | -61.3515 | 59.5637 | 59.7233 | 59.7081 | -61.9553 | -0.011747 | -0.025051 | 7.1e-05 | -0.072035 | -0.060288 | -0.019452 | -0.12929 | -0.19839 | -0.22477 | 0.73748 | 0.40536 | 0.60375 | -0.065251 | -0.080364 | 121.5204 | 121.526 | 121.4161 | 61.7812 | -121.5572 | 121.3206 | 121.4802 | 121.465 | 49.8206 | -121.7438
985.2031 | 121.7422 | -61.8301 | 59.7702 | 1.4211e-13 | -0.034051 | 0.0016453 | 0.063004 | -0.0073907 | 0.053965 | -0.01755 | -0.0018757 | -0.00063026 | 0.064693 | 0.024716 | 0.059658 | -61.7751 | 0.0243 | -61.8472 | 59.7543 | 59.7462 | 59.6501 | -61.787 | -60.9919 | -12.3393 | -61.3424 | 59.55 | 59.7004 | 59.7036 | -61.9644 | 0.043179 | -0.015898 | 0.054999 | -0.017106 | -0.060285 | -0.024037 | -0.12014 | -0.1343 | -0.2202 | 0.83819 | 0.48776 | 0.62206 | -0.069834 | -0.066633 | 121.5844 | 121.5763 | 121.4802 | 61.8544 | -121.5572 | 121.3801 | 121.5305 | 121.5337 | 49.4909 | -121.7346
986.9062 | 121.8155 | -61.8851 | 59.6649 | 1.4211e-13 | -0.034051 | 0.0016453 | 0.063004 | -0.0069633 | 0.053965 | -0.01755 | -0.0014485 | -0.00063026 | 0.064693 | 0.024716 | 0.059445 | -61.8347 | 0.028878 | -61.9113 | 59.6902 | 59.6958 | 59.5905 | -61.8511 | -61.0103 | -12.7422 | -61.3744 | 59.4859 | 59.65 | 59.6395 | -62.024 | 0.034006 | 0.025291 | 0.050412 | -0.02627 | -0.060276 | 0.030881 | -0.074376 | -0.1389 | -0.17901 | 0.87481 | 0.51064 | 0.64954 | -0.014913 | -0.025447 | 121.5753 | 121.5809 | 121.4756 | 61.9139 | -121.516 | 121.371 | 121.5351 | 121.5245 | 49.1429 | -121.6889
988.6562 | 121.8201 | -61.9171 | 59.6191 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063432 | -0.0073907 | 0.053965 | -0.0099192 | -0.0016621 | -0.00063026 | 0.064693 | 0.024929 | 0.059231 | -62.0132 | 0.0243 | -62.0899 | 59.5162 | 59.5172 | 59.412 | -62.0342 | -61.1385 | -13.2504 | -61.5072 | 59.3028 | 59.476 | 59.4563 | -62.2071 | -0.11711 | -0.10291 | -0.096102 | -0.17278 | -0.055672 | -0.10192 | -0.20716 | -0.29001 | -0.31638 | 0.77865 | 0.4099 | 0.69991 | -0.14312 | -0.16282 | 121.4333 | 121.4343 | 121.3291 | 61.9414 | -121.6534 | 121.2199 | 121.3931 | 121.3734 | 48.6667 | -121.8263
990.3594 | 121.8292 | -61.972 | 59.5642 | 1.4211e-13 | -0.034265 | 0.0016453 | 0.063004 | -0.0071769 | 0.053965 | 0.0053413 | -0.0016621 | -0.00063026 | 0.065334 | 0.024929 | 0.059872 | -61.9354 | 0.0243 | -62.0075 | 59.5895 | 59.5905 | 59.4898 | -61.9564 | -61.0103 | -13.6167 | -61.3973 | 59.3898 | 59.5493 | 59.5387 | -62.1247 | 0.015666 | 0.025274 | 0.036663 | -0.035438 | -0.051104 | 0.026274 | -0.074397 | -0.15266 | -0.17445 | 0.96178 | 0.57472 | 0.72738 | -0.014934 | -0.025468 | 121.5615 | 121.5625 | 121.4619 | 61.9963 | -121.5206 | 121.3618 | 121.5213 | 121.5108 | 48.3553 | -121.6889
992.125 | 121.843 | -61.8668 | 59.6924 | 1.4211e-13 | -0.034265 | 0.0014317 | 0.063218 | -0.0071769 | 0.053965 | -0.0099192 | -0.0018757 | -0.00041666 | 0.06512 | 0.025143 | 0.059872 | -61.8759 | 0.0243 | -61.9525 | 59.6353 | 59.6454 | 59.5356 | -61.8969 | -60.8958 | -14.0197 | -61.3103 | 59.4447 | 59.6088 | 59.5937 | -62.0743 | -0.030094 | -0.057116 | -0.009104 | -0.085785 | -0.055691 | -0.046953 | -0.15678 | -0.20758 | -0.24768 | 0.97097 | 0.55643 | 0.764 | -0.083586 | -0.098699 | 121.502 | 121.5122 | 121.4024 | 61.8911 | -121.5892 | 121.3115 | 121.4756 | 121.4604 | 47.8471 | -121.7667
993.8906 | 121.788 | -61.9675 | 59.6008 | 1.4211e-13 | -0.034051 | 0.0018589 | 0.063218 | -0.0071769 | 0.053324 | -0.01755 | -0.0016621 | -0.00084406 | 0.064693 | 0.024929 | 0.059658 | -61.9125 | 0.0243 | -61.9892 | 59.617 | 59.618 | 59.5081 | -61.9197 | -60.8866 | -14.4729 | -61.3103 | 59.4126 | 59.5722 | 59.5616 | -62.1018 | 0.047719 | 0.016124 | 0.054976 | -0.021703 | -0.069422 | 0.017127 | -0.092704 | -0.13434 | -0.18818 | 1.0808 | 0.65714 | 0.79148 | -0.028662 | -0.039196 | 121.5844 | 121.5854 | 121.4756 | 61.9918 | -121.5206 | 121.3801 | 121.5396 | 121.5291 | 47.4945 | -121.7026
995.5781 | 121.7422 | -61.9675 | 59.6603 | 1.4211e-13 | -0.034692 | 0.0014317 | 0.063004 | -0.0076043 | 0.053751 | -0.0099192 | -0.0018757 | -0.00063026 | 0.064906 | 0.025143 | 0.059445 | -61.9216 | 0.0243 | -61.9983 | 59.6032 | 59.6088 | 59.499 | -61.9381 | -60.8271 | -15.0132 | -61.2645 | 59.3943 | 59.5584 | 59.5525 | -62.1155 | 0.029403 | -0.05712 | 0.04582 | -0.03086 | -0.060263 | -0.05154 | -0.16137 | -0.14808 | -0.266 | 1.1404 | 0.70292 | 0.851 | -0.10191 | -0.10786 | 121.5707 | 121.5763 | 121.4664 | 61.9918 | -121.5984 | 121.3618 | 121.5259 | 121.5199 | 46.9542 | -121.7759
997.3281 | 121.756 | -61.9949 | 59.6146 | 1.4211e-13 | -0.034265 | 0.0014317 | 0.063004 | -0.0073907 | 0.054179 | -0.0099192 | -0.0018757 | -0.00041666 | 0.06512 | 0.025143 | 0.059872 | -61.9537 | 0.028878 | -62.0304 | 59.5712 | 59.5722 | 59.4669 | -61.9793 | -60.8088 | -15.4619 | -61.26 | 59.3577 | 59.5264 | 59.525 | -62.143 | 0.015659 | -0.043393 | 0.041237 | -0.035442 | -0.051101 | -0.042396 | -0.14764 | -0.14808 | -0.25686 | 1.1861 | 0.73497 | 0.88305 | -0.088181 | -0.089558 | 121.5661 | 121.5671 | 121.4619 | 62.0238 | -121.5938 | 121.3526 | 121.5213 | 121.5199 | 46.533 | -121.7576
999.0781 | 121.7789 | -61.9812 | 59.61 | 1.4211e-13 | -0.034051 | 0.0016453 | 0.063004 | -0.0073907 | 0.053751 | -0.0099192 | -0.0016621 | -0.00063026 | 0.064906 | 0.025143 | 0.059872 | -62.0086 | 0.033457 | -62.0853 | 59.5162 | 59.5172 | 59.4166 | -62.0251 | -60.7996 | -15.8969 | -61.2645 | 59.3119 | 59.4806 | 59.4655 | -62.2025 | -0.043863 | -0.093756 | -0.027437 | -0.10411 | -0.060251 | -0.092765 | -0.19343 | -0.22134 | -0.29806 | 1.1816 | 0.71666 | 0.938 | -0.12939 | -0.1445 | 121.4974 | 121.4984 | 121.3978 | 62.0147 | -121.635 | 121.2931 | 121.4618 | 121.4467 | 46.0843 | -121.8125
1000.8281 | 121.8842 | -62.1002 | 59.4269 | 1.4211e-13 | -0.033624 | 0.0014317 | 0.063004 | -0.0071769 | 0.053751 | -0.0099192 | -0.0016621 | -0.00063026 | 0.06512 | 0.025143 | 0.059872 | -62.091 | 0.0243 | -62.154 | 59.4384 | 59.444 | 59.3387 | -62.1029 | -60.8042 | -16.3823 | -61.3012 | 59.2341 | 59.4028 | 59.3922 | -62.285 | -0.002686 | 0.011517 | 0.009171 | -0.053769 | -0.051083 | 0.017077 | -0.088162 | -0.18474 | -0.19279 | 1.296 | 0.79905 | 0.98379 | -0.02412 | -0.034655 | 121.5386 | 121.5442 | 121.4389 | 62.1245 | -121.5298 | 121.3343 | 121.503 | 121.4924 | 45.718 | -121.7118
1002.5312 | 121.8658 | -61.7615 | 59.7519 | 1.4211e-13 | -0.034265 | 0.0016453 | 0.063432 | -0.0076043 | 0.053965 | -0.0022892 | -0.0014485 | -0.00020306 | 0.065761 | 0.025357 | 0.059658 | -61.8026 | 0.028878 | -61.8884 | 59.7085 | 59.7187 | 59.6134 | -61.8282 | -60.4746 | -16.6295 | -60.7426 | 59.5134 | 59.6821 | 59.6669 | -62.0057 | -0.066695 | -0.04337 | -0.041135 | -0.12697 | -0.060279 | -0.033199 | -0.13846 | -0.24418 | -0.23852 | 1.2869 | 1.0189 | 1.2631 | -0.069837 | -0.084951 | 121.47 | 121.4802 | 121.3749 | 61.7904 | -121.5801 | 121.2749 | 121.4435 | 121.4284 | 45.132 | -121.7575
1004.2969 | 121.756 | -62.4573 | 59.1476 | 1.4211e-13 | -0.034265 | 0.0012179 | 0.063004 | -0.0076043 | 0.054179 | -0.0022892 | -0.0023031 | -0.00063026 | 0.065334 | 0.02557 | 0.059872 | -62.3841 | 0.033457 | -62.4562 | 59.1316 | 59.0914 | 59.0365 | -62.4005 | -60.9599 | -17.3438 | -61.2645 | 58.9319 | 59.1006 | 59.09 | -62.5826 | 0.056739 | -0.015999 | 0.07321 | 0.001119 | -0.05562 | -0.056264 | -0.11111 | -0.12531 | -0.21574 | 1.4974 | 1.1927 | 1.318 | -0.047072 | -0.057606 | 121.5889 | 121.5487 | 121.4938 | 62.4907 | -121.5482 | 121.3892 | 121.5578 | 121.5473 | 45.1135 | -121.7302
1006.0625 | 121.8521 | -62.8967 | 58.6349 | 1.4211e-13 | -0.033837 | 0.0016453 | 0.063218 | -0.0073907 | 0.053751 | -0.0022892 | -0.0018757 | -0.00020306 | 0.065547 | 0.025357 | 0.060086 | -62.9747 | 0.0243 | -63.0468 | 58.5456 | 58.487 | 58.4367 | -63.0004 | -61.4681 | -17.9436 | -61.988 | 58.3413 | 58.5008 | 58.4902 | -63.1733 | -0.10365 | -0.089338 | -0.077948 | -0.15002 | -0.046379 | -0.14799 | -0.19822 | -0.27652 | -0.29367 | 1.4286 | 0.90875 | 1.1853 | -0.13417 | -0.14471 | 121.4423 | 121.3837 | 121.3335 | 62.921 | -121.6353 | 121.238 | 121.3975 | 121.387 | 44.9531 | -121.8082
1007.8281 | 121.8567 | -63.2538 | 58.255 | 1.4211e-13 | -0.034478 | 0.0018589 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0016621 | -0.00063026 | 0.066402 | 0.025143 | 0.060513 | -63.286 | 0.019721 | -63.3581 | 58.2297 | 58.1802 | 58.13 | -63.3163 | -61.6879 | -18.5572 | -62.2352 | 58.0345 | 58.1894 | 58.1743 | -63.4892 | -0.062537 | -0.025303 | -0.032224 | -0.10429 | -0.041756 | -0.074831 | -0.12504 | -0.23541 | -0.22048 | 1.5659 | 1.0186 | 1.254 | -0.065575 | -0.080688 | 121.4835 | 121.434 | 121.3838 | 63.2735 | -121.5713 | 121.2883 | 121.4432 | 121.4281 | 44.6966 | -121.7442
1009.5156 | 121.8338 | -64.0411 | 57.5134 | 1.4211e-13 | -0.034265 | 0.0014317 | 0.063432 | -0.0069633 | 0.053751 | -0.0099192 | -0.0018757 | 1.0742e-05 | 0.066615 | 0.02557 | 0.060086 | -63.9911 | 0.019721 | -64.0769 | 57.5109 | 57.4567 | 57.4157 | -64.0306 | -62.3106 | -19.244 | -62.8442 | 57.3157 | 57.4752 | 57.4601 | -64.2081 | 0.010505 | -0.002533 | 0.050058 | -0.035729 | -0.046234 | -0.056724 | -0.097723 | -0.16693 | -0.19773 | 1.7305 | 1.1969 | 1.3639 | -0.03826 | -0.053373 | 121.552 | 121.4978 | 121.4568 | 64.0609 | -121.5441 | 121.3568 | 121.5163 | 121.5012 | 44.7972 | -121.7215
1011.2656 | 121.8063 | -64.4623 | 57.0923 | 1.4211e-13 | -0.034478 | 0.0016453 | 0.062791 | -0.0073907 | 0.053751 | -0.0099192 | -0.0016621 | 1.0742e-05 | 0.066829 | 0.025357 | 0.060086 | -64.4398 | 0.019721 | -64.5164 | 57.0714 | 57.0263 | 56.967 | -64.4748 | -62.6632 | -19.8255 | -63.1876 | 56.867 | 57.0265 | 57.0159 | -64.6522 | -0.012509 | -0.020915 | 0.022518 | -0.054102 | -0.041593 | -0.066 | -0.12528 | -0.18993 | -0.22528 | 1.7991 | 1.2747 | 1.4646 | -0.06582 | -0.076354 | 121.5337 | 121.4886 | 121.4293 | 64.482 | -121.5671 | 121.3293 | 121.4887 | 121.4782 | 44.6368 | -121.7445
1013.0156 | 121.7926 | -65.1169 | 56.4972 | 1.4211e-13 | -0.034478 | 0.0016453 | 0.063218 | -0.0073907 | 0.053751 | -0.01755 | -0.0016621 | -0.00020306 | 0.067256 | 0.02557 | 0.060086 | -65.067 | 0.015142 | -65.1528 | 56.4396 | 56.3807 | 56.3397 | -65.1067 | -63.1623 | -20.4985 | -63.6821 | 56.2398 | 56.39 | 56.3887 | -65.2887 | 0.010202 | -0.057639 | 0.049881 | -0.035881 | -0.046083 | -0.11653 | -0.15746 | -0.17178 | -0.25744 | 1.9546 | 1.4348 | 1.6066 | -0.10715 | -0.10853 | 121.5564 | 121.4975 | 121.4566 | 65.132 | -121.6039 | 121.3566 | 121.5069 | 121.5055 | 44.6184 | -121.7859
1014.7344 | 121.8979 | -71.0449 | 50.4639 | 1.4211e-13 | -0.034265 | 0.0014317 | 0.063218 | -0.0073907 | 0.053965 | -0.0022892 | -0.0016621 | -0.00041666 | 0.070247 | 0.025998 | 0.060727 | -70.9685 | -0.007751 | -71.0175 | 50.4922 | 50.4876 | 50.4608 | -71.0501 | -68.7666 | -23.374 | -69.3918 | 50.2969 | 50.4516 | 50.5006 | -71.2274 | -0.005202 | 0.02836 | 0.076379 | 0.027381 | 0.032583 | 0.023714 | -0.003059 | -0.18247 | -0.167 | 2.2783 | 1.6532 | 1.8356 | -0.012275 | 0.036712 | 121.5371 | 121.5325 | 121.5057 | 71.0372 | -121.514 | 121.3418 | 121.4965 | 121.5455 | 47.671 | -121.6913
1016.5156 | 121.8979 | -73.2559 | 48.2346 | 1.4211e-13 | -0.034478 | 0.0012179 | 0.063004 | -0.0073907 | 0.053965 | -0.0099192 | -0.0016621 | -0.00041666 | 0.071743 | 0.026211 | 0.06094 | -73.276 | 0.001407 | -73.3433 | 48.1527 | 48.1706 | 48.1349 | -73.3762 | -70.8408 | -24.8483 | -71.53 | 47.9847 | 48.1257 | 48.1792 | -73.5626 | -0.1203 | -0.081887 | -0.02013 | -0.087387 | 0.032911 | -0.063913 | -0.09968 | -0.30667 | -0.24983 | 2.4152 | 1.7259 | 2.0326 | -0.1089 | -0.05533 | 121.4086 | 121.4266 | 121.3908 | 73.2573 | -121.6108 | 121.2406 | 121.3816 | 121.4351 | 48.4076 | -121.7971
1018.2031 | 121.907 | -74.1486 | 47.3694 | 1.4211e-13 | -0.034478 | 0.0016453 | 0.062791 | -0.0071769 | 0.054179 | -0.0099192 | -0.0014485 | -0.00020306 | 0.07217 | 0.026211 | 0.060299 | -74.1185 | -0.003172 | -74.1857 | 47.3057 | 47.3235 | 47.2878 | -74.2187 | -71.4589 | -25.5488 | -72.258 | 47.1377 | 47.2878 | 47.3322 | -74.4097 | -0.07018 | -0.063716 | 0.030086 | -0.037151 | 0.033029 | -0.045841 | -0.081549 | -0.26111 | -0.23168 | 2.6897 | 1.8905 | 2.1516 | -0.081608 | -0.037199 | 121.4542 | 121.4721 | 121.4364 | 74.1454 | -121.5881 | 121.2863 | 121.4363 | 121.4807 | 48.5997 | -121.7791
1019.9531 | 121.7697 | -76.3733 | 45.2087 | 1.4211e-13 | -0.034478 | 0.0016453 | 0.062791 | -0.0073907 | 0.053965 | -0.0099192 | -0.0020893 | 1.0742e-05 | 0.073452 | 0.025998 | 0.061154 | -76.0277 | -0.003172 | -76.104 | 45.3827 | 45.405 | 45.3786 | -76.151 | -72.9241 | -26.6981 | -73.9476 | 45.2193 | 45.3648 | 45.4092 | -76.3236 | 0.22225 | 0.17401 | 0.34563 | 0.26928 | 0.047036 | 0.19624 | 0.16982 | 0.049676 | 0.010574 | 3.4492 | 2.4257 | 2.376 | 0.15602 | 0.20043 | 121.756 | 121.7783 | 121.7518 | 76.3701 | -121.3598 | 121.5926 | 121.7381 | 121.7825 | 49.6752 | -121.5324
1021.7344 | 121.8155 | -76.3733 | 45.1996 | 1.4211e-13 | -0.034478 | 0.0016453 | 0.063004 | -0.0071769 | 0.053751 | -0.0022892 | -0.0016621 | -0.00041666 | 0.074093 | 0.026639 | 0.061581 | -76.4992 | -0.007751 | -76.571 | 44.9112 | 44.9242 | 44.9024 | -76.6181 | -73.0981 | -27.2384 | -74.2543 | 44.7431 | 44.8932 | 44.9467 | -76.809 | -0.24481 | -0.28841 | -0.12594 | -0.1977 | 0.047102 | -0.2754 | -0.2972 | -0.43568 | -0.45643 | 3.2752 | 2.1189 | 2.5546 | -0.30642 | -0.25285 | 121.2845 | 121.2975 | 121.2757 | 76.3655 | -121.8177 | 121.1164 | 121.2665 | 121.32 | 49.1349 | -122.0086
1023.4844 | 121.9208 | -78.2684 | 43.222 | 1.4211e-13 | -0.034692 | 0.0016453 | 0.062791 | -0.0073907 | 0.053751 | -0.0022892 | -0.0018757 | 1.0742e-05 | 0.075375 | 0.026425 | 0.061795 | -78.2116 | 0.001407 | -78.2924 | 43.1805 | 43.2025 | 43.1763 | -78.3444 | -74.5678 | -28.3281 | -75.7607 | 43.0216 | 43.1533 | 43.216 | -78.5398 | -0.075918 | -0.041505 | 0.056881 | -0.023995 | 0.051923 | -0.019534 | -0.045795 | -0.27133 | -0.20041 | 3.7006 | 2.5077 | 2.779 | -0.068747 | -0.006023 | 121.449 | 121.4709 | 121.4447 | 78.2698 | -121.5664 | 121.2901 | 121.4217 | 121.4845 | 49.9403 | -121.7618
1025.2344 | 121.8933 | -79.747 | 41.7618 | 1.4211e-13 | -0.034906 | 0.0016453 | 0.063004 | -0.0073907 | 0.053965 | -0.0099192 | -0.0018757 | 1.0742e-05 | 0.076871 | 0.026852 | 0.062009 | -79.7362 | -0.007751 | -79.8307 | 41.6559 | 41.6732 | 41.647 | -79.9012 | -75.337 | -29.3125 | -77.0428 | 41.4878 | 41.624 | 41.6776 | -80.0645 | -0.15418 | -0.10584 | 0.010854 | -0.083722 | 0.070455 | -0.088629 | -0.11478 | -0.3175 | -0.27394 | 4.41 | 2.7042 | 3.0217 | -0.13773 | -0.084168 | 121.4029 | 121.4202 | 121.394 | 79.7393 | -121.663 | 121.2348 | 121.3711 | 121.4246 | 50.4345 | -121.8263
1026.9375 | 121.8155 | -83.6609 | 37.8891 | 1.4211e-13 | -0.034265 | 0.0012179 | 0.063004 | -0.0076043 | 0.053965 | -0.0022892 | -0.0016621 | 1.0742e-05 | 0.079434 | 0.02728 | 0.062649 | -83.4263 | -0.021486 | -83.5208 | 37.9154 | 37.9551 | 37.9383 | -83.6101 | -78.4918 | -31.1303 | -80.3394 | 37.7701 | 37.9154 | 37.9598 | -83.7962 | 0.050775 | 0.026296 | 0.23455 | 0.14006 | 0.089289 | 0.065966 | 0.049231 | -0.13536 | -0.119 | 5.1691 | 3.3214 | 3.4568 | 0.026279 | 0.070688 | 121.5763 | 121.616 | 121.5992 | 83.6394 | -121.4992 | 121.431 | 121.5763 | 121.6207 | 52.5306 | -121.6853
1028.6875 | 121.8933 | -72.2992 | 49.2599 | 1.4211e-13 | -0.034692 | 0.0014317 | 0.063218 | -0.0071769 | 0.053965 | -0.0099192 | -0.0016621 | 0.00043794 | 0.09033 | 0.04416 | 0.062222 | -72.0719 | 0.028878 | -72.1713 | 49.3659 | 49.3337 | 49.2978 | -72.1582 | -67.2923 | -21.7806 | -47.6795 | 49.1843 | 49.3481 | 49.3239 | -72.3492 | 0.14097 | 0.10599 | 0.22726 | 0.12793 | -0.013043 | 0.073743 | 0.037894 | -0.050008 | -0.075659 | 5.0069 | 24.6197 | 24.6697 | 0.0882 | 0.063929 | 121.6651 | 121.6329 | 121.597 | 72.3281 | -121.4182 | 121.4835 | 121.6473 | 121.6231 | 50.5186 | -121.6092
1030.4375 | 121.8475 | -97.5037 | 23.9868 | 1.4211e-13 | -0.034692 | 0.0012179 | 0.063004 | -0.0073907 | 0.054392 | -0.0022892 | -0.0018757 | 1.0742e-05 | 0.14524 | 0.08433 | 0.064145 | -96.1405 | -0.10848 | -96.2576 | 25.1417 | 25.1066 | 25.1549 | -96.4036 | -89.3433 | -23.3785 | -20.7338 | 24.9412 | 25.0861 | 25.0527 | -96.5986 | 1.1 | 1.1549 | 1.3631 | 1.2461 | 0.14603 | 1.1198 | 1.1681 | 0.90504 | 0.95434 | 8.1603 | 76.7699 | 75.8648 | 1.0993 | 1.0659 | 122.6454 | 122.6103 | 122.6585 | 97.3952 | -120.3904 | 122.4448 | 122.5898 | 122.5564 | 74.1251 | -120.5854
1032.2188 | 119.7647 | -108.1421 | 13.3347 | 1.4211e-13 | -0.034906 | 0.0010043 | 0.062791 | -0.0076043 | 0.054392 | 0.0053413 | -0.0020893 | -0.00020306 | 0.16788 | 0.099501 | 0.065 | -107.6643 | -0.081008 | -107.8407 | 13.5675 | 13.5723 | 13.6122 | -107.9929 | -99.0548 | -25.3703 | -13.037 | 13.4125 | 13.5389 | 13.5192 | -108.1922 | 0.1492 | 0.23287 | 0.47777 | 0.30144 | 0.15224 | 0.23763 | 0.27756 | -0.050093 | 0.077852 | 9.0873 | 95.1051 | 95.1552 | 0.20424 | 0.18455 | 121.7096 | 121.7144 | 121.7543 | 108.0611 | -121.3275 | 121.5546 | 121.681 | 121.6613 | 82.7718 | -121.5268
1033.9844 | 121.9208 | -110.6461 | 10.8307 | 1.4211e-13 | -0.034692 | 0.0012179 | 0.062363 | -0.0069633 | 0.054392 | -0.0022892 | -0.0023031 | 1.0742e-05 | 0.17387 | 0.10313 | 0.065854 | -110.2877 | -0.071851 | -110.4777 | 10.9258 | 10.944 | 10.9841 | -110.6349 | -100.1216 | -25.7274 | -10.8072 | 10.7982 | 10.9108 | 10.8819 | -110.8387 | 0.01113 | 0.095111 | 0.35832 | 0.16832 | 0.15719 | 0.1133 | 0.15341 | -0.19268 | -0.032501 | 10.5245 | 99.8389 | 100.0316 | 0.080092 | 0.051244 | 121.5719 | 121.59 | 121.6302 | 110.5742 | -121.4656 | 121.4442 | 121.5568 | 121.528 | 84.9186 | -121.6694
1035.6875 | 121.8338 | -111.7676 | 9.7961 | 1.4211e-13 | -0.035119 | 0.0014317 | 0.062577 | -0.0076043 | 0.053751 | -0.0022892 | -0.0020893 | 1.0742e-05 | 0.17664 | 0.10506 | 0.066709 | -111.3911 | -0.053537 | -111.5857 | 9.8178 | 9.8405 | 9.8761 | -111.7476 | -99.9018 | -25.8236 | -9.896 | 9.6856 | 9.8028 | 9.7785 | -111.9514 | 0.019972 | 0.021686 | 0.37645 | 0.18189 | 0.16192 | 0.044325 | 0.079932 | -0.18381 | -0.11053 | 11.8658 | 101.8716 | 102.0554 | 0.006616 | -0.017655 | 121.5854 | 121.608 | 121.6437 | 111.714 | -121.5437 | 121.4532 | 121.5703 | 121.5461 | 85.944 | -121.7475
1037.4375 | 121.8338 | -111.731 | 9.8053 | 1.4211e-13 | -0.034478 | 0.00079051 | 0.063004 | -0.0071769 | 0.053965 | -0.0022892 | -0.0023031 | 1.0742e-05 | 0.18647 | 0.10506 | 0.075682 | -111.469 | -0.044379 | -111.6727 | 9.7308 | 9.7443 | 9.7799 | -111.8392 | -83.4002 | -25.5672 | -9.2458 | 9.5849 | 9.7112 | 9.6915 | -112.0338 | -0.10823 | -0.074458 | 0.26199 | 0.058285 | 0.16651 | -0.060988 | -0.025374 | -0.30285 | -0.22041 | 28.3308 | 102.4851 | 102.788 | -0.094111 | -0.1138 | 121.4618 | 121.4753 | 121.5109 | 111.6866 | -121.6445 | 121.3158 | 121.4421 | 121.4225 | 86.1638 | -121.8391
1039.125 | 121.843 | -111.3922 | 10.1852 | 1.4211e-13 | -0.034906 | 0.0012179 | 0.062791 | -0.0071769 | 0.054179 | -0.0099192 | -0.0023031 | -0.00063026 | 0.21211 | 0.10548 | 0.10089 | -110.9928 | -0.048958 | -111.192 | 10.2161 | 10.2251 | 10.2698 | -111.3401 | -37.0087 | -23.4426 | -8.0462 | 10.0748 | 10.1919 | 10.1677 | -111.5439 | 0.052131 | 0.030907 | 0.3994 | 0.20026 | 0.14813 | 0.039855 | 0.084593 | -0.15166 | -0.11046 | 74.3835 | 103.346 | 103.4977 | 0.006698 | -0.017572 | 121.6084 | 121.6173 | 121.662 | 111.3433 | -121.5253 | 121.467 | 121.5842 | 121.5599 | 87.9496 | -121.7291
1040.875 | 121.7743 | -112.1475 | 9.4482 | 1.4211e-13 | -0.034478 | 0.0014317 | 0.062791 | -0.0071769 | 0.054179 | -0.0022892 | -0.0020893 | -0.00041666 | 0.21617 | 0.10527 | 0.10431 | -111.7666 | -0.039801 | -111.9794 | 9.4195 | 9.4375 | 9.4777 | -112.1322 | -31.4913 | -23.9417 | -9.1955 | 9.2781 | 9.3907 | 9.3847 | -112.3406 | 0.015287 | -0.028733 | 0.38096 | 0.1681 | 0.15282 | -0.01072 | 0.029495 | -0.19307 | -0.17012 | 80.6562 | 102.9521 | 103.1451 | -0.057558 | -0.063513 | 121.567 | 121.585 | 121.6253 | 112.1077 | -121.5805 | 121.4256 | 121.5382 | 121.5323 | 88.2058 | -121.7888
1042.6406 | 121.7651 | -112.6053 | 8.9722 | 1.4211e-13 | -0.034906 | 0.0012179 | 0.062577 | -0.0073907 | 0.054392 | 0.0053413 | -0.0025167 | -0.00063026 | 0.21895 | 0.10698 | 0.10559 | -112.1969 | -0.035222 | -112.4098 | 8.9891 | 8.9979 | 9.0473 | -112.5672 | -29.5316 | -23.873 | -7.6021 | 8.8432 | 8.9603 | 8.9498 | -112.7664 | 0.038053 | 0.016973 | 0.40836 | 0.19551 | 0.15746 | 0.025778 | 0.07518 | -0.16113 | -0.129 | 83.0737 | 105.0032 | 105.1644 | -0.011872 | -0.022407 | 121.5944 | 121.6032 | 121.6526 | 112.5701 | -121.5394 | 121.4485 | 121.5656 | 121.555 | 88.7323 | -121.7386
1044.3906 | 121.843 | -112.8754 | 8.6609 | 1.4211e-13 | -0.034692 | 0.0012179 | 0.063004 | -0.0071769 | 0.054606 | -0.0022892 | -0.0027303 | -0.00041666 | 0.2213 | 0.10677 | 0.10709 | -112.5174 | -0.039801 | -112.7257 | 8.6183 | 8.6728 | 8.7268 | -112.8786 | -28.039 | -24.189 | -7.9729 | 8.5227 | 8.6398 | 8.6247 | -113.0869 | -0.003234 | -0.042598 | 0.35795 | 0.14969 | 0.15292 | 0.011953 | 0.065957 | -0.21157 | -0.13821 | 84.8364 | 104.9024 | 105.114 | -0.021095 | -0.036208 | 121.4937 | 121.5482 | 121.6022 | 112.8356 | -121.5395 | 121.398 | 121.5152 | 121.5 | 88.6864 | -121.7478
1046.1406 | 121.7285 | -113.1683 | 8.4412 | 1.4211e-13 | -0.034692 | 0.0014317 | 0.063004 | -0.0073907 | 0.054179 | 0.0053413 | -0.0020893 | -0.00020306 | 0.22322 | 0.10762 | 0.10773 | -112.7692 | -0.035222 | -112.9821 | 8.3619 | 8.421 | 8.4613 | -113.1488 | -26.8943 | -24.2714 | -7.1259 | 8.2663 | 8.3697 | 8.3729 | -113.3479 | 0.019578 | -0.07926 | 0.39911 | 0.18627 | 0.1667 | -0.020161 | 0.020125 | -0.1796 | -0.17488 | 86.274 | 106.0425 | 106.2221 | -0.071506 | -0.068305 | 121.5302 | 121.5893 | 121.6296 | 113.1331 | -121.5899 | 121.4346 | 121.538 | 121.5412 | 88.897 | -121.7891
1047.8906 | 121.7468 | -113.3743 | 8.2306 | 1.4211e-13 | -0.035119 | 0.0012179 | 0.062791 | -0.0076043 | 0.054179 | -0.0099192 | -0.0027303 | -0.00063026 | 0.22471 | 0.10826 | 0.1088 | -112.9753 | -0.030644 | -113.1927 | 8.1559 | 8.2104 | 8.2598 | -113.3365 | -25.8458 | -24.4591 | -6.5947 | 8.074 | 8.1728 | 8.1531 | -113.5494 | 0.037836 | -0.074717 | 0.39908 | 0.18167 | 0.14383 | -0.02022 | 0.029237 | -0.17507 | -0.15661 | 87.5286 | 106.7796 | 106.9546 | -0.057815 | -0.077506 | 121.5302 | 121.5847 | 121.6342 | 113.3437 | -121.5671 | 121.4483 | 121.5471 | 121.5274 | 88.9152 | -121.78
1049.6406 | 121.8292 | -113.4476 | 8.0429 | 1.4211e-13 | -0.034906 | 0.0010043 | 0.062577 | -0.0071769 | 0.054179 | -0.0099192 | -0.0025167 | -0.00020306 | 0.226 | 0.10848 | 0.10965 | -113.1309 | -0.026065 | -113.3392 | 8.0002 | 8.0593 | 8.1042 | -113.5013 | -24.6736 | -24.7705 | -6.3475 | 7.9092 | 8.0125 | 8.002 | -113.7005 | -0.053763 | -0.042699 | 0.31665 | 0.1084 | 0.16217 | 0.016358 | 0.061248 | -0.25293 | -0.13375 | 88.774 | 107.1001 | 107.353 | -0.030383 | -0.040917 | 121.4478 | 121.5068 | 121.5517 | 113.4215 | -121.5442 | 121.3567 | 121.4601 | 121.4496 | 88.6771 | -121.7434
1051.3281 | 121.8201 | -113.6078 | 7.9239 | 1.4211e-13 | -0.034478 | 0.0012179 | 0.062791 | -0.0071769 | 0.054392 | -0.0022892 | -0.0025167 | -0.00041666 | 0.22685 | 0.1089 | 0.11008 | -113.2545 | -0.035222 | -113.4582 | 7.872 | 7.9311 | 7.9714 | -113.6204 | -24.1562 | -24.7293 | -5.9812 | 7.7764 | 7.8843 | 7.8692 | -113.8379 | -0.012598 | -0.051875 | 0.35326 | 0.14959 | 0.16218 | 0.007167 | 0.047487 | -0.23008 | -0.14751 | 89.4516 | 107.6266 | 107.8567 | -0.039565 | -0.054678 | 121.4798 | 121.5388 | 121.5792 | 113.5726 | -121.5443 | 121.3842 | 121.4921 | 121.477 | 88.8785 | -121.7618
1053.0781 | 121.788 | -113.6948 | 7.8827 | 1.4211e-13 | -0.034906 | 0.0010043 | 0.062363 | -0.0071769 | 0.054392 | -0.0022892 | -0.0025167 | -0.00041666 | 0.22771 | 0.10848 | 0.11115 | -113.3507 | -0.030644 | -113.5589 | 7.7804 | 7.8303 | 7.8752 | -113.7257 | -23.5427 | -24.6652 | -5.7431 | 7.6802 | 7.7928 | 7.7731 | -113.9203 | -0.030938 | -0.10224 | 0.34408 | 0.13584 | 0.16678 | -0.05237 | -0.007464 | -0.22552 | -0.20246 | 90.1521 | 107.9517 | 108.1772 | -0.089938 | -0.10963 | 121.4752 | 121.5251 | 121.57 | 113.6641 | -121.6084 | 121.375 | 121.4875 | 121.4678 | 89.0296 | -121.803
1054.7656 | 121.7743 | -113.7543 | 7.8049 | 1.4211e-13 | -0.034692 | 0.0012179 | 0.062791 | -0.0071769 | 0.053965 | -0.0022892 | -0.0025167 | -0.00041666 | 0.2292 | 0.1089 | 0.112 | -113.5018 | -0.026065 | -113.7192 | 7.6065 | 7.6792 | 7.715 | -113.8814 | -23.0894 | -24.6056 | -5.505 | 7.5246 | 7.6371 | 7.6174 | -114.0805 | -0.12711 | -0.1984 | 0.25251 | 0.035109 | 0.16222 | -0.12566 | -0.089896 | -0.32627 | -0.28031 | 90.6649 | 108.2493 | 108.5755 | -0.16779 | -0.18748 | 121.3607 | 121.4335 | 121.4692 | 113.7282 | -121.6863 | 121.2788 | 121.3914 | 121.3717 | 89.1486 | -121.8854
1056.5156 | 121.6965 | -113.9786 | 7.5897 | 1.4211e-13 | -0.034692 | 0.0010043 | 0.062577 | -0.0076043 | 0.053965 | -0.0099192 | -0.0027303 | -0.00020306 | 0.23048 | 0.10933 | 0.11307 | -113.575 | -0.030644 | -113.797 | 7.5378 | 7.5968 | 7.6463 | -113.9501 | -22.9658 | -24.8895 | -5.3539 | 7.4513 | 7.5501 | 7.5396 | -114.1492 | 0.028509 | -0.05193 | 0.40356 | 0.18158 | 0.15307 | 0.007073 | 0.056574 | -0.17065 | -0.13842 | 91.0128 | 108.6247 | 108.7953 | -0.039636 | -0.05017 | 121.5164 | 121.5754 | 121.6249 | 113.9479 | -121.5398 | 121.4299 | 121.5287 | 121.5181 | 89.0891 | -121.7389
1058.2812 | 121.7377 | -113.942 | 7.6035 | 1.4211e-13 | -0.034478 | 0.0014317 | 0.062577 | -0.0073907 | 0.054392 | 0.0053413 | -0.0023031 | -0.00041666 | 0.23112 | 0.1089 | 0.11329 | -113.575 | -0.021486 | -113.797 | 7.5286 | 7.5876 | 7.6371 | -113.9501 | -22.4896 | -24.4866 | -5.2074 | 7.433 | 7.5501 | 7.5258 | -114.163 | -0.008112 | -0.07482 | 0.36694 | 0.14496 | 0.15307 | -0.015818 | 0.033683 | -0.221 | -0.17046 | 91.4524 | 108.7346 | 108.9556 | -0.053369 | -0.077639 | 121.4706 | 121.5296 | 121.5791 | 113.9205 | -121.5535 | 121.3749 | 121.492 | 121.4678 | 89.4554 | -121.7664
1060.0469 | 121.7194 | -114.0793 | 7.5073 | 1.4211e-13 | -0.035119 | 0.0012179 | 0.062791 | -0.0078179 | 0.054392 | -0.0099192 | -0.0025167 | -0.00041666 | 0.23155 | 0.10933 | 0.11414 | -113.7124 | -0.030644 | -113.9298 | 7.3913 | 7.4548 | 7.4998 | -114.092 | -21.8257 | -24.3996 | -5.0609 | 7.3048 | 7.4127 | 7.393 | -114.2912 | -0.01273 | -0.11604 | 0.36691 | 0.14952 | 0.16225 | -0.052476 | -0.007544 | -0.21188 | -0.20253 | 92.2536 | 109.0184 | 109.2303 | -0.094596 | -0.11429 | 121.4706 | 121.5341 | 121.5791 | 114.0486 | -121.5993 | 121.3841 | 121.492 | 121.4723 | 89.6797 | -121.7985
1061.7344 | 121.7148 | -114.1983 | 7.3608 | 1.4211e-13 | -0.034906 | 0.0012179 | 0.062577 | -0.0076043 | 0.053965 | -0.0099192 | -0.0027303 | 1.0742e-05 | 0.23262 | 0.10933 | 0.11457 | -113.8314 | -0.026065 | -114.0625 | 7.2768 | 7.3358 | 7.3762 | -114.2111 | -21.5326 | -25.0543 | -4.8686 | 7.1812 | 7.2937 | 7.2648 | -114.4102 | -0.012764 | -0.084016 | 0.36689 | 0.13577 | 0.14853 | -0.025044 | 0.015318 | -0.21191 | -0.17966 | 92.6657 | 109.3297 | 109.5416 | -0.067155 | -0.096004 | 121.4751 | 121.5341 | 121.5745 | 114.1722 | -121.5719 | 121.3795 | 121.492 | 121.4631 | 89.144 | -121.7711
1063.4844 | 121.7377 | -114.3585 | 7.1548 | 1.4211e-13 | -0.034906 | 0.00079051 | 0.062791 | -0.0073907 | 0.054392 | -0.0022892 | -0.0023031 | 1.0742e-05 | 0.23241 | 0.10954 | 0.11435 | -113.9047 | -0.039801 | -114.1175 | 7.199 | 7.2625 | 7.3029 | -114.2798 | -21.1251 | -24.9673 | -4.8732 | 7.1171 | 7.2204 | 7.1962 | -114.4881 | 0.07877 | 0.044145 | 0.45386 | 0.24105 | 0.16228 | 0.10769 | 0.14805 | -0.12954 | -0.037769 | 93.2334 | 109.4854 | 109.6149 | 0.065581 | 0.041311 | 121.5575 | 121.6211 | 121.6614 | 114.3187 | -121.4346 | 121.4756 | 121.5789 | 121.5547 | 89.3912 | -121.6429
1065.1719 | 121.6919 | -114.299 | 7.2968 | 1.4211e-13 | -0.035333 | 0.0010043 | 0.063004 | -0.0073907 | 0.054392 | -0.0022892 | -0.0025167 | -0.00020306 | 0.23326 | 0.10933 | 0.11457 | -113.9138 | -0.030644 | -114.1312 | 7.199 | 7.2488 | 7.2937 | -114.2798 | -20.7222 | -24.9582 | -4.9693 | 7.0942 | 7.1975 | 7.187 | -114.4881 | 0.01926 | -0.097762 | 0.38519 | 0.1678 | 0.14854 | -0.047956 | -0.00301 | -0.18905 | -0.20257 | 93.5768 | 109.3297 | 109.5187 | -0.099219 | -0.10975 | 121.498 | 121.5478 | 121.5928 | 114.2684 | -121.5765 | 121.3932 | 121.4965 | 121.486 | 89.3408 | -121.7848
1066.9062 | 121.7102 | -114.2899 | 7.2922 | 1.4211e-13 | -0.034906 | 0.00079051 | 0.063004 | -0.0073907 | 0.053965 | 0.012972 | -0.0025167 | -0.00020306 | 0.2339 | 0.10954 | 0.11542 | -113.8955 | -0.026065 | -114.1221 | 7.199 | 7.2488 | 7.3029 | -114.2752 | -20.1956 | -24.7613 | -4.603 | 7.1125 | 7.2158 | 7.2007 | -114.4881 | 0.014684 | -0.093184 | 0.39435 | 0.1678 | 0.15312 | -0.043378 | 0.010725 | -0.1982 | -0.17968 | 94.0942 | 109.6868 | 109.885 | -0.076327 | -0.09144 | 121.4888 | 121.5387 | 121.5928 | 114.2638 | -121.5673 | 121.4024 | 121.5057 | 121.4906 | 89.5286 | -121.7802
1068.6719 | 121.7514 | -114.2807 | 7.2098 | 1.4211e-13 | -0.035119 | 0.0014317 | 0.062791 | -0.0071769 | 0.054179 | -0.0022892 | -0.0023031 | 0.00022434 | 0.23454 | 0.10933 | 0.11606 | -113.9367 | -0.021486 | -114.1587 | 7.1578 | 7.2167 | 7.2617 | -114.3164 | -19.8065 | -24.7109 | -4.4794 | 7.0713 | 7.1746 | 7.1549 | -114.5247 | -0.035681 | -0.051992 | 0.34399 | 0.12202 | 0.1577 | 0.006966 | 0.051915 | -0.24399 | -0.13849 | 94.4742 | 109.8013 | 110.0453 | -0.035137 | -0.054829 | 121.4385 | 121.4974 | 121.5424 | 114.2592 | -121.5262 | 121.352 | 121.4553 | 121.4356 | 89.5698 | -121.7345
1070.4062 | 121.701 | -114.2578 | 7.2784 | 1.4211e-13 | -0.035333 | 0.0012179 | 0.062577 | -0.0076043 | 0.053965 | -0.0022892 | -0.0023031 | 0.00086534 | 0.23454 | 0.10933 | 0.11628 | -113.9001 | -0.026065 | -114.1266 | 7.1944 | 7.2396 | 7.2892 | -114.2798 | -19.6279 | -24.8803 | -4.4885 | 7.0942 | 7.2113 | 7.187 | -114.4881 | -0.021939 | -0.084029 | 0.35773 | 0.13118 | 0.15312 | -0.038803 | 0.010723 | -0.23024 | -0.18426 | 94.6299 | 109.7693 | 109.9995 | -0.067172 | -0.091443 | 121.4522 | 121.4975 | 121.547 | 114.2317 | -121.5582 | 121.352 | 121.4691 | 121.4448 | 89.3775 | -121.7665
1072.1562 | 121.6736 | -114.4455 | 7.1503 | 1.4211e-13 | -0.035333 | 0.0010043 | 0.062791 | -0.0073907 | 0.054392 | -0.0099192 | -0.0020893 | 0.00065174 | 0.23561 | 0.10912 | 0.11713 | -113.9504 | -0.035222 | -114.1678 | 7.1349 | 7.1984 | 7.248 | -114.3393 | -18.964 | -24.8529 | -4.5755 | 7.053 | 7.1563 | 7.1412 | -114.5338 | 0.10622 | -0.015375 | 0.49505 | 0.27766 | 0.17144 | 0.048159 | 0.097688 | -0.088349 | -0.097291 | 95.4815 | 109.87 | 109.9583 | 0.006057 | -0.009056 | 121.5804 | 121.6439 | 121.6935 | 114.4103 | -121.4895 | 121.4985 | 121.6018 | 121.5867 | 89.5926 | -121.6841
1073.9219 | 121.7194 | -114.3906 | 7.1457 | 1.4211e-13 | -0.035333 | 0.00079051 | 0.062791 | -0.0073907 | 0.053965 | -0.0099192 | -0.0027303 | 0.00022434 | 0.23689 | 0.10933 | 0.11734 | -113.9825 | -0.030644 | -114.2136 | 7.0983 | 7.1526 | 7.2022 | -114.3759 | -18.4191 | -25.5122 | -4.2825 | 7.0026 | 7.1105 | 7.1 | -114.5796 | 0.014656 | -0.047424 | 0.40807 | 0.17695 | 0.16229 | 0.006948 | 0.05648 | -0.18907 | -0.14308 | 95.9715 | 110.1081 | 110.2971 | -0.035151 | -0.045685 | 121.4888 | 121.5432 | 121.5927 | 114.3599 | -121.5216 | 121.3932 | 121.5011 | 121.4906 | 88.8784 | -121.7253
1075.6719 | 121.6873 | -114.4684 | 7.077 | 1.4211e-13 | -0.035119 | 0.0010043 | 0.062791 | -0.0076043 | 0.054179 | -0.01755 | -0.0023031 | 0.0017199 | 0.23689 | 0.10976 | 0.1182 | -114.0603 | -0.026065 | -114.2869 | 7.025 | 7.0794 | 7.1335 | -114.4537 | -18.1123 | -25.1597 | -3.8338 | 6.9339 | 7.0419 | 7.0313 | -114.6437 | 0.014634 | -0.052014 | 0.40806 | 0.18151 | 0.16688 | 0.00235 | 0.056466 | -0.17535 | -0.14309 | 96.3561 | 110.6346 | 110.8099 | -0.035165 | -0.045699 | 121.4934 | 121.5478 | 121.6019 | 114.4423 | -121.5308 | 121.4023 | 121.5102 | 121.4997 | 89.3087 | -121.7208
1077.3594 | 121.6644 | -114.3814 | 7.2006 | 1.4211e-13 | -0.035119 | 0.0012179 | 0.063004 | -0.0073907 | 0.054392 | -0.01755 | -0.0025167 | 0.0027881 | 0.23775 | 0.10997 | 0.11927 | -113.9917 | -0.026065 | -114.2182 | 7.0891 | 7.1526 | 7.1976 | -114.3942 | -17.7094 | -25.0681 | -3.4721 | 7.0026 | 7.0968 | 7.0908 | -114.5842 | -0.012815 | -0.11151 | 0.38976 | 0.16321 | 0.17603 | -0.047984 | -0.003031 | -0.2028 | -0.19801 | 96.672 | 110.9093 | 111.1121 | -0.10382 | -0.10977 | 121.4705 | 121.534 | 121.579 | 114.3553 | -121.5948 | 121.384 | 121.4782 | 121.4723 | 89.3133 | -121.7848
1079.125 | 121.7972 | -114.3127 | 7.1365 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.062363 | -0.0073907 | 0.054392 | -0.0022892 | -0.0020893 | 0.0025745 | 0.23796 | 0.10997 | 0.11863 | -113.9962 | -0.026065 | -114.2136 | 7.08 | 7.1389 | 7.1884 | -114.3851 | -17.5675 | -24.047 | -3.0691 | 6.9935 | 7.0968 | 7.0908 | -114.5934 | -0.072322 | -0.056583 | 0.31651 | 0.099127 | 0.17145 | 0.002366 | 0.051899 | -0.28063 | -0.14308 | 96.7453 | 111.2436 | 111.5242 | -0.039731 | -0.045687 | 121.3927 | 121.4516 | 121.5012 | 114.2867 | -121.5216 | 121.3062 | 121.4095 | 121.4036 | 90.2657 | -121.7299
1080.8906 | 121.7834 | -114.2441 | 7.2235 | 1.4211e-13 | -0.035119 | 0.0010043 | 0.063004 | -0.0073907 | 0.053965 | -0.0099192 | -0.0025167 | 0.0030019 | 0.23988 | 0.11061 | 0.11905 | -113.9092 | -0.021486 | -114.1266 | 7.1807 | 7.2351 | 7.2709 | -114.2935 | -17.0913 | -23.7357 | -2.6891 | 7.0759 | 7.1975 | 7.1778 | -114.4972 | -0.049408 | -0.042833 | 0.33484 | 0.11745 | 0.16686 | 0.011549 | 0.047339 | -0.25313 | -0.14764 | 97.1528 | 111.555 | 111.8081 | -0.025977 | -0.045669 | 121.4248 | 121.4791 | 121.5149 | 114.2226 | -121.517 | 121.3199 | 121.4416 | 121.4219 | 90.5084 | -121.7207
1082.6406 | 121.6507 | -114.386 | 7.1365 | 1.4211e-13 | -0.035119 | 0.0012179 | 0.062791 | -0.0076043 | 0.054179 | -0.0022892 | -0.0023031 | 0.0032155 | 0.24117 | 0.11061 | 0.12205 | -114.0329 | -0.016908 | -114.2594 | 7.0342 | 7.0931 | 7.1472 | -114.4263 | -16.9402 | -25.7686 | -2.6525 | 6.9431 | 7.051 | 7.0451 | -114.6346 | -0.040291 | -0.10237 | 0.35313 | 0.12659 | 0.16688 | -0.043423 | 0.010692 | -0.24859 | -0.19344 | 97.4458 | 111.7335 | 111.9821 | -0.085517 | -0.091473 | 121.4202 | 121.4791 | 121.5332 | 114.3691 | -121.5628 | 121.3291 | 121.437 | 121.431 | 88.6174 | -121.7711
1084.3281 | 121.7422 | -113.9969 | 7.457 | 1.4211e-13 | -0.035333 | 0.0014317 | 0.063004 | -0.0073907 | 0.054179 | 0.0053413 | -0.0023031 | 0.0049247 | 0.24715 | 0.1104 | 0.12717 | -113.6757 | -0.021486 | -113.8794 | 7.4142 | 7.4686 | 7.5181 | -114.0462 | -16.5876 | -28.818 | -2.3915 | 7.3185 | 7.431 | 7.4068 | -114.2591 | -0.049339 | -0.042795 | 0.32114 | 0.11748 | 0.16682 | 0.011615 | 0.061125 | -0.26223 | -0.13844 | 97.4093 | 111.6054 | 111.8676 | -0.025927 | -0.050198 | 121.4111 | 121.4655 | 121.515 | 113.9754 | -121.5032 | 121.3154 | 121.4279 | 121.4037 | 85.1788 | -121.7161
1086.0781 | 121.6644 | -113.7588 | 7.7957 | 1.4211e-13 | -0.035333 | 0.0012179 | 0.063004 | -0.0076043 | 0.054392 | -0.0022892 | -0.0023031 | 0.0053521 | 0.25078 | 0.1104 | 0.13038 | -113.3644 | -0.016908 | -113.591 | 7.7072 | 7.7708 | 7.8065 | -113.7578 | -16.3816 | -29.6331 | -2.2312 | 7.6207 | 7.7149 | 7.7044 | -113.9569 | 0.001096 | -0.088523 | 0.39444 | 0.16788 | 0.16678 | -0.024921 | 0.010832 | -0.19806 | -0.175 | 97.3773 | 111.5276 | 111.7257 | -0.080799 | -0.091334 | 121.466 | 121.5296 | 121.5654 | 113.7419 | -121.5535 | 121.3796 | 121.4738 | 121.4632 | 84.1258 | -121.7526
1087.7656 | 121.7331 | -113.7222 | 7.7911 | 1.4211e-13 | -0.035333 | 0.0010043 | 0.062791 | -0.0073907 | 0.054392 | -0.0099192 | -0.0025167 | 0.0070613 | 0.25313 | 0.11018 | 0.13422 | -113.3827 | -0.021486 | -113.6001 | 7.6889 | 7.7479 | 7.7882 | -113.7578 | -16.1069 | -15.3749 | -2.1717 | 7.5932 | 7.6966 | 7.6906 | -113.9615 | -0.035525 | -0.10226 | 0.3395 | 0.1221 | 0.15763 | -0.043239 | -0.002906 | -0.23926 | -0.1979 | 97.6154 | 111.5505 | 111.7898 | -0.094536 | -0.10049 | 121.4111 | 121.4701 | 121.5105 | 113.7007 | -121.5489 | 121.3155 | 121.4188 | 121.4129 | 98.3473 | -121.7526
1089.5156 | 121.7285 | -113.7314 | 7.7728 | 1.4211e-13 | -0.035119 | 0.0012179 | 0.062577 | -0.0071769 | 0.054392 | -0.0022892 | -0.0023031 | 0.0062067 | 0.25868 | 0.11018 | 0.13828 | -113.3598 | -0.021486 | -113.5727 | 7.7163 | 7.7708 | 7.8157 | -113.7349 | -16.6288 | -22.7925 | -2.0939 | 7.6207 | 7.7332 | 7.7135 | -113.9432 | -0.003475 | -0.056478 | 0.37155 | 0.15873 | 0.1622 | -0.002033 | 0.042877 | -0.21179 | -0.15212 | 97.1026 | 111.6375 | 111.8493 | -0.039597 | -0.059288 | 121.4477 | 121.5022 | 121.5471 | 113.7099 | -121.5077 | 121.3521 | 121.4646 | 121.4449 | 90.9389 | -121.716
1091.2656 | 121.7743 | -113.7131 | 7.7179 | 1.4211e-13 | -0.034906 | 0.0012179 | 0.063004 | -0.0076043 | 0.054179 | -0.0099192 | -0.0018757 | 0.0077023 | 0.25933 | 0.11018 | 0.14021 | -113.4194 | -0.016908 | -113.6322 | 7.6431 | 7.7113 | 7.7516 | -113.8081 | -16.7387 | -26.9682 | -1.9748 | 7.5612 | 7.6646 | 7.6449 | -114.0073 | -0.095048 | -0.074801 | 0.29372 | 0.080898 | 0.17595 | -0.006628 | 0.033707 | -0.29421 | -0.1567 | 96.9744 | 111.7382 | 112.0325 | -0.053345 | -0.073036 | 121.3562 | 121.4243 | 121.4647 | 113.6962 | -121.526 | 121.2743 | 121.3776 | 121.3579 | 86.7448 | -121.7252
1093.0156 | 121.7468 | -113.4888 | 7.9971 | 1.4211e-13 | -0.035119 | 0.0014317 | 0.063218 | -0.0071769 | 0.053965 | -0.0022892 | -0.0018757 | 0.0081297 | 0.2636 | 0.10997 | 0.14427 | -113.1904 | -0.021486 | -113.3987 | 7.8812 | 7.9402 | 7.9851 | -113.57 | -17.1462 | -19.6103 | -1.842 | 7.7901 | 7.8889 | 7.8829 | -113.7646 | -0.081248 | -0.11596 | 0.29833 | 0.090086 | 0.17133 | -0.056917 | -0.012019 | -0.27583 | -0.20702 | 96.3425 | 111.6467 | 111.9226 | -0.10823 | -0.11418 | 121.3699 | 121.429 | 121.4739 | 113.4673 | -121.5671 | 121.2789 | 121.3777 | 121.3717 | 93.8785 | -121.7617
1094.7031 | 121.6736 | -81.7062 | 39.6561 | 1.4211e-13 | -0.034906 | 0.0016453 | 0.063004 | -0.0076043 | 0.053751 | 0.0053413 | -0.0018757 | 0.024795 | 0.82913 | 0.096296 | 0.76322 | -82.8403 | 0.038035 | -82.9806 | 38.4053 | 38.3717 | 38.3641 | -83.0835 | -8.6069 | -1.7167 | 11.1157 | 38.1226 | 38.2634 | 38.3078 | -83.1323 | -1.3773 | -1.2508 | -1.1341 | -1.2743 | 0.10295 | -1.2843 | -1.2919 | -1.4261 | -1.5334 | 73.0993 | 92.8219 | 94.248 | -1.3927 | -1.3483 | 120.1115 | 120.078 | 120.0704 | 81.7443 | -122.7396 | 119.8289 | 119.9696 | 120.014 | 79.9896 | -122.7884
1096.4531 | 121.4493 | -72.5876 | 48.7656 | 1.4211e-13 | -0.035333 | 0.0012179 | 0.062791 | -0.0071769 | 0.053965 | -0.0099192 | -0.0020893 | 0.01689 | 1.3645 | 0.10484 | 1.2781 | -92.052 | 0.4959 | -92.247 | 28.9555 | 29.0307 | 28.9734 | -92.3467 | -10.2507 | -3.5848 | 12.9106 | 28.8008 | 28.9047 | 28.9628 | -92.2625 | -19.7591 | -19.8101 | -19.4644 | -19.6594 | 0.099675 | -19.7348 | -19.7921 | -19.6749 | -19.9647 | 62.3369 | 85.4981 | 105.173 | -19.8609 | -19.8027 | 101.5431 | 101.6183 | 101.561 | 73.0835 | -141.1123 | 101.3884 | 101.4923 | 101.5504 | 69.0028 | -141.028
1098.2188 | 121.5546 | -77.9251 | 43.1168 | 1.4211e-13 | -0.034692 | 0.0012179 | 0.062791 | -0.0073907 | 0.053965 | -0.0022892 | -0.0016621 | 0.013899 | 1.3748 | 0.10677 | 1.2865 | -90.0696 | 0.58747 | -90.3654 | 30.8189 | 30.9997 | 30.7957 | -90.3823 | -7.6362 | -4.9675 | 17.503 | 30.733 | 30.7865 | 30.9545 | -90.2982 | -12.4572 | -12.2979 | -12.1445 | -12.4402 | 0.01699 | -12.1171 | -12.321 | -12.3731 | -12.3838 | 70.2889 | 95.4281 | 107.8012 | -12.3303 | -12.1622 | 108.744 | 108.9248 | 108.7208 | 78.5126 | -133.4991 | 108.6581 | 108.7116 | 108.8796 | 72.9576 | -133.4149
1099.9062 | 121.431 | -83.67 | 37.5183 | 1.4211e-13 | -0.034906 | 0.0014317 | 0.062791 | -0.0076043 | 0.053965 | -0.0022892 | -0.0014485 | 0.019667 | 2.1881 | 0.10356 | 2.1107 | -84.548 | 0.019721 | -84.7249 | 36.4549 | 36.4578 | 36.4091 | -84.8052 | -6.9723 | -78.8954 | 19.1513 | 36.0669 | 36.1847 | 36.2474 | -84.7074 | -1.1352 | -1.0634 | -0.878 | -1.0549 | 0.080302 | -1.0606 | -1.1092 | -1.0374 | -1.4514 | 76.6977 | 102.8214 | 103.8588 | -1.3336 | -1.2709 | 120.1249 | 120.1278 | 120.0791 | 83.6898 | -122.3235 | 119.7369 | 119.8547 | 119.9174 | 4.7747 | -122.2257
1101.6562 | 121.2799 | -52.652 | 68.3899 | 1.4211e-13 | -0.035333 | 0.0016453 | 0.063218 | -0.0073907 | 0.052897 | -0.0022892 | -0.0010211 | 0.028 | 2.8868 | 0.10442 | 2.8391 | -51.753 | 0.0884 | -51.8208 | 69.401 | 69.3436 | 69.2468 | -51.7729 | 6.9012 | -48.1631 | 54.0274 | 68.8535 | 69.0178 | 69.0164 | -51.5568 | 0.87913 | 1.0111 | 0.89893 | 0.83117 | -0.047958 | 0.9537 | 0.85692 | 1.0952 | 0.46361 | 59.5531 | 106.6793 | 105.5842 | 0.62793 | 0.62655 | 122.0529 | 121.9956 | 121.8988 | 52.7404 | -120.1627 | 121.5055 | 121.6698 | 121.6684 | 4.4889 | -119.9467
1103.4062 | 121.1472 | -55.6183 | 65.5746 | 1.4211e-13 | -0.034906 | 0.0016453 | 0.063218 | -0.0073907 | 0.053538 | -0.0099192 | -0.0014485 | 0.017744 | 3.2756 | 0.10506 | 3.2162 | -53.5386 | 0.10671 | -53.5834 | 67.5147 | 67.4571 | 67.365 | -53.5678 | 10.5641 | -49.99 | 52.6629 | 66.958 | 67.1131 | 67.1072 | -53.3013 | 2.0505 | 1.94 | 2.0797 | 2.0348 | -0.015657 | 1.8824 | 1.7904 | 2.317 | 1.3834 | 66.1824 | 108.2812 | 105.9642 | 1.5385 | 1.5325 | 123.133 | 123.0754 | 122.9833 | 55.725 | -119.1424 | 122.5763 | 122.7314 | 122.7255 | 5.6283 | -118.876
1105.1562 | 121.3074 | -55.2612 | 65.799 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063432 | -0.0076043 | 0.053538 | -0.0022892 | -0.00080746 | 0.017103 | 3.3752 | 0.1057 | 3.3142 | -54.2666 | 0.05635 | -54.2885 | 66.8004 | 66.7199 | 66.6691 | -54.3142 | 17.3773 | -50.8828 | 53.2307 | 66.1751 | 66.3485 | 66.3105 | -54.0294 | 0.94707 | 1.0015 | 0.99465 | 0.97273 | 0.025652 | 0.92092 | 0.87011 | 1.2319 | 0.37614 | 72.6385 | 108.4919 | 107.26 | 0.54955 | 0.51154 | 122.0617 | 121.9811 | 121.9303 | 55.3176 | -120.1131 | 121.4363 | 121.6097 | 121.5717 | 4.3784 | -119.8283
1106.9219 | 120.9366 | -49.0814 | 71.8506 | 1.4211e-13 | -0.034692 | 0.0016453 | 0.063004 | -0.0076043 | 0.05311 | -0.01755 | -0.0010211 | 0.018172 | 6.0434 | 0.10313 | 5.9855 | -52.0094 | 0.20744 | -52.1138 | 68.76 | 68.7895 | 68.6104 | -52.0201 | 14.717 | -46.8765 | 52.608 | 67.9149 | 68.0426 | 68.1236 | -51.4103 | -2.9387 | -3.0906 | -2.928 | -3.0324 | -0.093706 | -3.061 | -3.2402 | -2.3289 | -3.9357 | 63.7984 | 101.6894 | 104.0182 | -3.808 | -3.727 | 117.8414 | 117.871 | 117.6918 | 49.2889 | -123.8707 | 116.9963 | 117.124 | 117.205 | 2.2049 | -123.2609
1108.6875 | 120.6024 | -50.3128 | 70.1477 | 1.4211e-13 | -0.035119 | 0.0018589 | 0.062791 | -0.0078179 | 0.05311 | -0.0022892 | -0.0010211 | 0.025222 | 7.0414 | 0.10826 | 7.0271 | -54.8664 | 0.10671 | -54.9707 | 65.578 | 65.5797 | 65.4328 | -54.8911 | -7.3753 | -48.6988 | 57.411 | 63.9133 | 64.0363 | 63.9983 | -53.5486 | -4.5783 | -4.5697 | -4.5535 | -4.6579 | -0.079567 | -4.568 | -4.7149 | -3.2358 | -6.2344 | 42.9376 | 107.7238 | 110.9596 | -6.1114 | -6.1494 | 115.8908 | 115.8925 | 115.7456 | 50.4195 | -125.0388 | 114.2261 | 114.3491 | 114.3111 | 1.614 | -123.6963
1110.3906 | 121.1792 | -0.19684 | 121.0739 | 1.4211e-13 | -0.034265 | 0.0016453 | 0.063432 | -0.0076043 | 0.052469 | -0.01755 | -0.0029439 | -0.0016987 | 0.028159 | 0.025784 | 0.056667 | -0.13173 | 0.24407 | -0.21443 | 120.9674 | 120.8061 | 120.637 | -0.23706 | -0.07679 | -0.059164 | -0.038036 | -0.029954 | 0.06865 | 0.11306 | -0.29693 | -0.040218 | -0.10656 | 0.065112 | -0.017594 | 0.022624 | -0.26779 | -0.43687 | -0.1001 | -121.1039 | 0.12005 | 0.1588 | 0.2589 | -121.0053 | -120.9609 | 121.1642 | 121.003 | 120.8339 | 0.44091 | -121.311 | 0.16688 | 0.26549 | 0.3099 | 0.13767 | -121.3708
1112.1406 | 121.344 | -0.2243 | 121.1014 | 1.4211e-13 | -0.034265 | 0.0020727 | 0.063645 | -0.0078179 | 0.052683 | -0.0022892 | -0.0025167 | -0.0019123 | 0.022177 | 0.024929 | 0.051753 | -0.12715 | 0.19371 | -0.20985 | 121.1139 | 120.9618 | 120.8065 | -0.21416 | -0.058476 | -0.063743 | -0.070087 | -0.071161 | 0.0366 | 0.07643 | -0.29236 | 0.010142 | 0.012481 | 0.097157 | 0.01445 | 0.004308 | -0.13957 | -0.29492 | -0.068052 | -121.1725 | 0.16583 | 0.15422 | 0.22227 | -121.0648 | -121.0249 | 121.3382 | 121.1861 | 121.0308 | 0.41801 | -121.3155 | 0.15314 | 0.2609 | 0.30073 | 0.16056 | -121.3937
1113.8594 | 121.4447 | -0.23804 | 121.1151 | 1.4211e-13 | -0.034692 | 0.0016453 | 0.063432 | -0.0076043 | 0.052683 | -0.0099192 | -0.0025167 | -0.0019123 | 0.022177 | 0.025357 | 0.051753 | -0.15462 | 0.17081 | -0.22359 | 121.1505 | 120.9801 | 120.8248 | -0.25079 | -0.053897 | -0.082058 | -0.079245 | -0.075739 | 0.027442 | 0.067272 | -0.31525 | -0.012756 | 0.035375 | 0.083419 | 0.014448 | 0.027204 | -0.13499 | -0.29034 | -0.077213 | -121.1909 | 0.18414 | 0.15879 | 0.236 | -121.0877 | -121.0478 | 121.3885 | 121.2182 | 121.0628 | 0.40885 | -121.3659 | 0.1623 | 0.26548 | 0.30531 | 0.15598 | -121.4304
1115.6094 | 121.4493 | -0.35706 | 120.9869 | 1.4211e-13 | -0.034692 | 0.0020727 | 0.063004 | -0.0073907 | 0.052897 | -0.0099192 | -0.0029439 | -0.0014849 | 0.021536 | 0.025357 | 0.060727 | -0.25992 | 0.15708 | -0.32889 | 121.0406 | 120.8702 | 120.7103 | -0.34237 | -0.072212 | -0.16905 | -0.083823 | -0.084896 | 0.018285 | 0.058115 | -0.40683 | 0.014684 | 0.053667 | 0.097135 | 0.028167 | 0.013483 | -0.11671 | -0.27663 | -0.04977 | -121.0718 | 0.28484 | 0.27323 | 0.323 | -120.9687 | -120.9288 | 121.3977 | 121.2273 | 121.0674 | 0.51414 | -121.3293 | 0.27216 | 0.37534 | 0.41517 | 0.188 | -121.3938
1117.3125 | 121.4081 | -0.38452 | 120.9732 | 1.4211e-13 | -0.034692 | 0.0020727 | 0.063432 | -0.0076043 | 0.05311 | -0.01755 | -0.0027303 | -0.0014849 | 0.021322 | 0.025143 | 0.064572 | -0.28739 | 0.14792 | -0.37009 | 120.9857 | 120.8336 | 120.6737 | -0.37442 | -0.067633 | -0.2011 | -0.088402 | -0.084896 | 0.018285 | 0.067272 | -0.43888 | 0.010097 | 0.012459 | 0.09713 | 0.014427 | 0.00433 | -0.13961 | -0.29953 | -0.054357 | -121.0581 | 0.31689 | 0.29612 | 0.35048 | -120.9549 | -120.9059 | 121.3702 | 121.2181 | 121.0582 | 0.53244 | -121.3476 | 0.29963 | 0.40281 | 0.45179 | 0.18342 | -121.4121
1119.0781 | 121.4584 | -0.37537 | 120.9457 | 1.4211e-13 | -0.034692 | 0.0020727 | 0.063218 | -0.0076043 | 0.052683 | -0.0099192 | -0.0029439 | -0.0016987 | 0.021322 | 0.025143 | 0.065854 | -0.29655 | 0.14334 | -0.37925 | 120.9948 | 120.8382 | 120.6691 | -0.37442 | -0.11342 | -0.20568 | -0.074666 | -0.084896 | 0.032021 | 0.058115 | -0.44346 | 0.000942 | 0.049081 | 0.078818 | -0.003884 | -0.004826 | -0.10756 | -0.27664 | -0.068091 | -121.0306 | 0.26195 | 0.3007 | 0.36879 | -120.9137 | -120.8876 | 121.3702 | 121.2135 | 121.0445 | 0.51871 | -121.3202 | 0.29047 | 0.40739 | 0.43348 | 0.16968 | -121.3892
1120.7812 | 121.4722 | -0.39825 | 120.9 | 1.4211e-13 | -0.034265 | 0.0018589 | 0.064073 | -0.0073907 | 0.052897 | 0.0053413 | -0.0025167 | -0.0012713 | 0.021749 | 0.025357 | 0.066068 | -0.31028 | 0.12961 | -0.40214 | 120.9719 | 120.8153 | 120.6554 | -0.39732 | -0.11342 | -0.21484 | -0.074666 | -0.075739 | 0.027442 | 0.062694 | -0.45719 | 0.000935 | 0.071966 | 0.087971 | -0.003888 | -0.004823 | -0.08468 | -0.2446 | -0.058939 | -120.9757 | 0.28483 | 0.32359 | 0.38253 | -120.8725 | -120.8373 | 121.3702 | 121.2135 | 121.0536 | 0.52786 | -121.2973 | 0.32251 | 0.4257 | 0.46095 | 0.18341 | -121.3572
1122.5312 | 121.4172 | -0.44861 | 120.8679 | 1.4211e-13 | -0.034478 | 0.0020727 | 0.063432 | -0.0078179 | 0.052469 | -0.0099192 | -0.0027303 | -0.0019123 | 0.021536 | 0.025143 | 0.065854 | -0.35149 | 0.12961 | -0.43419 | 120.9307 | 120.7741 | 120.6187 | -0.43395 | -0.10884 | -0.21942 | -0.074666 | -0.094053 | 0.027442 | 0.062694 | -0.49382 | 0.014658 | 0.062804 | 0.09712 | 0.014419 | -0.000239 | -0.093847 | -0.24919 | -0.045216 | -120.962 | 0.33977 | 0.37394 | 0.41916 | -120.8405 | -120.8052 | 121.3793 | 121.2227 | 121.0673 | 0.57822 | -121.3019 | 0.35456 | 0.47605 | 0.5113 | 0.22919 | -121.3617
1124.2969 | 121.4218 | -0.47607 | 120.8908 | 1.4211e-13 | -0.034692 | 0.0020727 | 0.063645 | -0.0073907 | 0.05311 | -0.0022892 | -0.0027303 | -0.0016987 | 0.021536 | 0.025357 | 0.066923 | -0.38811 | 0.12503 | -0.46166 | 120.9078 | 120.7466 | 120.5867 | -0.45685 | -0.10426 | -0.21484 | -0.083823 | -0.084896 | 0.018285 | 0.062694 | -0.5213 | 0.019229 | 0.017024 | 0.087959 | 0.014415 | -0.004814 | -0.14421 | -0.30412 | -0.045223 | -120.9757 | 0.37181 | 0.39225 | 0.43747 | -120.8725 | -120.8281 | 121.3839 | 121.2227 | 121.0628 | 0.6011 | -121.3477 | 0.39118 | 0.49436 | 0.53877 | 0.26123 | -121.4121
1126.0469 | 121.3898 | -0.48523 | 120.8633 | 1.4211e-13 | -0.035119 | 0.0022863 | 0.063432 | -0.0078179 | 0.052683 | 0.0053413 | -0.0029439 | -0.0019123 | 0.021749 | 0.025357 | 0.068204 | -0.37896 | 0.12503 | -0.46166 | 120.9078 | 120.7466 | 120.5913 | -0.45685 | -0.099684 | -0.21484 | -0.074666 | -0.084896 | 0.018285 | 0.058115 | -0.51672 | 0.028384 | 0.04449 | 0.10627 | 0.02357 | -0.004814 | -0.11674 | -0.27208 | -0.031489 | -120.9482 | 0.38555 | 0.41056 | 0.44205 | -120.8451 | -120.8052 | 121.3931 | 121.2318 | 121.0765 | 0.61026 | -121.3202 | 0.40033 | 0.50351 | 0.54334 | 0.27039 | -121.3801
1127.7344 | 121.4264 | -0.47607 | 120.8542 | 1.4211e-13 | -0.034692 | 0.0018589 | 0.063645 | -0.0076043 | 0.052256 | -0.01755 | -0.0029439 | -0.0019123 | 0.021322 | 0.02557 | 0.0697 | -0.38354 | 0.12503 | -0.46624 | 120.9033 | 120.7512 | 120.5913 | -0.45227 | -0.118 | -0.22858 | -0.074666 | -0.094053 | 0.022864 | 0.058115 | -0.51672 | 0.023808 | 0.049067 | 0.092537 | 0.009837 | -0.013971 | -0.10301 | -0.26292 | -0.040644 | -120.9482 | 0.35807 | 0.40141 | 0.44205 | -120.8313 | -120.7961 | 121.3793 | 121.2273 | 121.0673 | 0.6011 | -121.3065 | 0.38202 | 0.49894 | 0.53419 | 0.2475 | -121.3709
1129.4844 | 121.3303 | -0.54016 | 120.8725 | 1.4211e-13 | -0.034692 | 0.0018589 | 0.063432 | -0.0076043 | 0.052897 | -0.0099192 | -0.0029439 | -0.0019123 | 0.021749 | 0.025357 | 0.071409 | -0.40185 | 0.12045 | -0.47539 | 120.8941 | 120.7374 | 120.5821 | -0.47516 | -0.15463 | -0.26063 | -0.1525 | -0.084896 | 0.022864 | 0.062694 | -0.53045 | 0.065001 | 0.021599 | 0.13831 | 0.064767 | -0.000234 | -0.13506 | -0.29039 | 0.009707 | -120.9574 | 0.38553 | 0.38766 | 0.37795 | -120.8496 | -120.8098 | 121.4343 | 121.2776 | 121.1223 | 0.66061 | -121.3477 | 0.45527 | 0.56302 | 0.60286 | 0.27953 | -121.403
1131.1875 | 121.376 | -0.51727 | 120.8725 | 1.4211e-13 | -0.034906 | 0.0018589 | 0.063645 | -0.0076043 | 0.052897 | -0.0099192 | -0.0029439 | -0.0019123 | 0.022177 | 0.025357 | 0.071623 | -0.40185 | 0.11129 | -0.47539 | 120.8895 | 120.742 | 120.5775 | -0.46142 | -0.15463 | -0.26063 | -0.18913 | -0.10321 | 0.022864 | 0.058115 | -0.53045 | 0.055849 | 0.01702 | 0.11542 | 0.041879 | -0.01397 | -0.13048 | -0.29497 | -0.013181 | -120.9757 | 0.36264 | 0.32814 | 0.34132 | -120.8496 | -120.8144 | 121.4068 | 121.2593 | 121.0948 | 0.62857 | -121.3339 | 0.41406 | 0.54014 | 0.57539 | 0.25665 | -121.403
1132.9375 | 121.3531 | -0.53558 | 120.845 | 1.4211e-13 | -0.034692 | 0.0016453 | 0.063218 | -0.0078179 | 0.052897 | -0.0022892 | -0.0029439 | -0.0016987 | 0.021963 | 0.02557 | 0.074187 | -0.39727 | 0.11129 | -0.48455 | 120.8804 | 120.7283 | 120.5775 | -0.47058 | -0.15921 | -0.27436 | -0.13419 | -0.094053 | 0.013707 | 0.062694 | -0.53045 | 0.065001 | 0.03533 | 0.13831 | 0.051032 | -0.013969 | -0.11675 | -0.2675 | 0.005129 | -120.9391 | 0.37638 | 0.40139 | 0.39626 | -120.8313 | -120.7823 | 121.4159 | 121.2639 | 121.1131 | 0.64688 | -121.3156 | 0.44153 | 0.54929 | 0.59828 | 0.26122 | -121.3755
1134.6875 | 121.4493 | -0.55389 | 120.7489 | 1.4211e-13 | -0.035119 | 0.0018589 | 0.063432 | -0.0078179 | 0.052897 | -0.0099192 | -0.0029439 | -0.0016987 | 0.021963 | 0.02557 | 0.070127 | -0.38354 | 0.12503 | -0.46624 | 120.9078 | 120.7603 | 120.6004 | -0.49806 | -0.14547 | -0.25605 | -0.083823 | -0.089475 | 0.018285 | 0.058115 | -0.54877 | 0.055839 | 0.15893 | 0.17036 | 0.087657 | 0.031818 | 0.011435 | -0.14848 | 0.005125 | -120.8384 | 0.40842 | 0.47007 | 0.46495 | -120.7306 | -120.6908 | 121.4617 | 121.3142 | 121.1543 | 0.67892 | -121.247 | 0.46442 | 0.57218 | 0.61201 | 0.29784 | -121.2977
1136.4375 | 121.4539 | -0.60883 | 120.6894 | 1.4211e-13 | -0.034478 | 0.0018589 | 0.063645 | -0.0076043 | 0.05311 | 0.0053413 | -0.0029439 | -0.0019123 | 0.022177 | 0.025357 | 0.071409 | -0.40185 | 0.12045 | -0.48455 | 120.8941 | 120.7374 | 120.5867 | -0.51637 | -0.16379 | -0.26063 | -0.083823 | -0.089475 | 0.018285 | 0.058115 | -0.58082 | 0.092455 | 0.20471 | 0.20697 | 0.12427 | 0.03182 | 0.048049 | -0.10271 | 0.028005 | -120.7789 | 0.44504 | 0.525 | 0.497 | -120.6711 | -120.6313 | 121.5029 | 121.3463 | 121.1955 | 0.72928 | -121.2058 | 0.51935 | 0.62711 | 0.66694 | 0.3482 | -121.2702
1138.125 | 121.4172 | -0.64087 | 120.7306 | 1.4211e-13 | -0.034692 | 0.0020727 | 0.063432 | -0.0076043 | 0.05311 | -0.0022892 | -0.0027303 | -0.0016987 | 0.021749 | 0.025357 | 0.068418 | -0.40185 | 0.097557 | -0.47082 | 120.9078 | 120.7603 | 120.605 | -0.49806 | -0.14547 | -0.21942 | -0.079245 | -0.098632 | 0.018285 | 0.048958 | -0.55335 | 0.14281 | 0.17724 | 0.23902 | 0.17005 | 0.027239 | 0.029745 | -0.12559 | 0.087521 | -120.8292 | 0.4954 | 0.56162 | 0.4741 | -120.7123 | -120.6816 | 121.5487 | 121.4012 | 121.2459 | 0.73843 | -121.2286 | 0.54224 | 0.65915 | 0.68983 | 0.42145 | -121.2839
1139.875 | 121.5179 | -0.42114 | 120.9045 | 1.4211e-13 | -0.034478 | 0.0018589 | 0.063859 | -0.0073907 | 0.05311 | -0.0099192 | -0.0029439 | -0.0014849 | 0.021963 | 0.02557 | 0.064786 | -0.35149 | 0.10671 | -0.42046 | 120.9857 | 120.829 | 120.6691 | -0.45685 | -0.13173 | -0.18737 | -0.083823 | -0.089475 | 0.013707 | 0.053537 | -0.50756 | -0.035702 | 0.081124 | 0.069655 | 0.000688 | 0.03639 | -0.075521 | -0.23544 | -0.086417 | -120.994 | 0.28941 | 0.33732 | 0.42374 | -120.8908 | -120.851 | 121.4068 | 121.2502 | 121.0902 | 0.52786 | -121.3614 | 0.33167 | 0.43485 | 0.47468 | 0.23377 | -121.4121
1141.6406 | 121.5179 | -0.49896 | 120.8817 | 1.4211e-13 | -0.034692 | 0.0018589 | 0.063645 | -0.0076043 | 0.05311 | -0.0099192 | -0.0029439 | -0.0016987 | 0.021963 | 0.025357 | 0.056881 | -0.29197 | 0.10214 | -0.36551 | 121.0498 | 120.9114 | 120.7515 | -0.39732 | -0.10426 | -0.14616 | -0.070087 | -0.089475 | 0.009128 | 0.053537 | -0.45719 | 0.10164 | 0.16811 | 0.20699 | 0.13345 | 0.031804 | 0.029787 | -0.13014 | 0.041769 | -120.9711 | 0.3947 | 0.42888 | 0.38711 | -120.8725 | -120.8281 | 121.5487 | 121.4104 | 121.2505 | 0.6011 | -121.279 | 0.40949 | 0.50809 | 0.5525 | 0.3528 | -121.3388
1143.3438 | 121.4127 | -0.36163 | 121.0281 | 1.4211e-13 | -0.034478 | 0.0018589 | 0.063432 | -0.0078179 | 0.052897 | 0.0053413 | -0.0029439 | -0.0016987 | 0.021749 | 0.025357 | 0.084442 | -0.498 | 0.12045 | -0.56696 | 120.83 | 120.6779 | 120.5088 | -0.59421 | -0.18668 | -0.24689 | -0.083823 | -0.094053 | -2.9e-05 | 0.048958 | -0.65408 | -0.23258 | -0.19814 | -0.13636 | -0.20533 | 0.027253 | -0.35022 | -0.51929 | -0.29245 | -121.1222 | 0.17495 | 0.27781 | 0.57026 | -121.0282 | -120.9792 | 121.1916 | 121.0395 | 120.8705 | 0.48208 | -121.6223 | 0.26758 | 0.3616 | 0.41059 | 0.11474 | -121.6822
1145.0938 | 121.3715 | -4.5868 | 116.803 | 1.4211e-13 | -0.034906 | 0.0018589 | 0.063645 | -0.0078179 | 0.052897 | -0.0099192 | -0.0018757 | -0.0014849 | 0.020467 | 0.027707 | 0.51624 | -3.7074 | 0.042614 | -3.7901 | 117.6526 | 117.4818 | 117.3588 | -3.8178 | -1.368 | -1.9914 | -0.24408 | -0.25888 | -0.15112 | -0.11129 | -3.8226 | 0.76902 | 0.84962 | 0.87934 | 0.79672 | 0.027706 | 0.67885 | 0.55579 | 0.76417 | -117.0619 | 3.2188 | 4.3427 | 3.5785 | -116.9541 | -116.9143 | 122.2394 | 122.0686 | 121.9456 | 4.6294 | -120.6208 | 4.3279 | 4.4357 | 4.4755 | 2.5954 | -120.6256
1146.8594 | 121.4355 | -5.5984 | 115.7455 | 1.4211e-13 | -0.034906 | 0.0018589 | 0.063645 | -0.0078179 | 0.053324 | -0.0099192 | -0.0020893 | -0.0019123 | 0.020467 | 0.028775 | 0.71579 | -4.8658 | 0.065507 | -4.953 | 116.4805 | 116.3279 | 116.1958 | -4.9579 | -1.8762 | -2.7377 | -0.28071 | -0.30009 | -0.19233 | -0.1525 | -4.9444 | 0.64052 | 0.73499 | 0.73267 | 0.6455 | 0.004976 | 0.58239 | 0.45026 | 0.65402 | -116.0456 | 3.7222 | 5.3177 | 4.6637 | -115.9379 | -115.898 | 122.079 | 121.9264 | 121.7943 | 5.664 | -120.7035 | 5.2984 | 5.4061 | 5.4459 | 2.8607 | -120.69
1148.5625 | 121.3028 | -4.9896 | 116.3589 | 1.4211e-13 | -0.034478 | 0.0016453 | 0.063859 | -0.0076043 | 0.052897 | -0.0099192 | -0.0023031 | -0.0016987 | 0.020895 | 0.028562 | 1.0025 | -4.8337 | 0.083821 | -4.9346 | 116.421 | 116.2684 | 116.1271 | -4.9213 | -1.7663 | -2.6553 | -0.3677 | -0.3825 | -0.2839 | -0.23949 | -4.8758 | 0.068328 | 0.062064 | 0.15589 | 0.054985 | -0.013343 | -0.090537 | -0.23182 | 0.11387 | -116.7414 | 3.2233 | 4.6219 | 4.508 | -116.6429 | -116.5984 | 121.4106 | 121.258 | 121.1167 | 5.0734 | -121.2802 | 4.6071 | 4.7057 | 4.7501 | 2.3343 | -121.2347
1150.3125 | 121.3577 | -5.1132 | 116.0477 | 1.4211e-13 | -0.034906 | 0.0016453 | 0.063218 | -0.0080317 | 0.05311 | -0.01755 | -0.0027303 | -0.0012713 | 0.020254 | 0.028562 | 1.2403 | -4.6918 | 0.11129 | -4.8064 | 116.5126 | 116.3646 | 116.1866 | -4.7656 | -1.7114 | -2.4447 | -0.42723 | -0.42828 | -0.32969 | -0.28986 | -4.6972 | 0.34761 | 0.46491 | 0.42142 | 0.30677 | -0.040834 | 0.3169 | 0.13898 | 0.41604 | -116.476 | 3.4018 | 4.686 | 4.27 | -116.3774 | -116.3375 | 121.6258 | 121.4778 | 121.2999 | 5.2245 | -120.8133 | 4.6849 | 4.7835 | 4.8234 | 2.6685 | -120.7448
1152.0625 | 121.2341 | -5.2139 | 116.0248 | 1.4211e-13 | -0.034906 | 0.0022863 | 0.063645 | -0.0073907 | 0.05311 | -0.0022892 | -0.0025167 | -0.0010577 | 0.020467 | 0.028134 | 1.0128 | -4.4537 | 0.079243 | -4.5409 | 116.7644 | 116.6256 | 116.4934 | -4.5367 | -1.6656 | -2.1608 | -0.3677 | -0.38708 | -0.27932 | -0.23949 | -4.4911 | 0.67726 | 0.73961 | 0.7602 | 0.67302 | -0.00424 | 0.60079 | 0.46863 | 0.7228 | -116.4119 | 3.5483 | 4.8462 | 4.1234 | -116.3041 | -116.2643 | 121.9783 | 121.8395 | 121.7073 | 5.2932 | -120.5614 | 4.8269 | 4.9346 | 4.9744 | 3.0531 | -120.5159
1153.8281 | 121.2708 | -0.10986 | 121.0144 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063432 | -0.0078179 | 0.052897 | -0.01755 | -0.0033713 | -0.0012713 | 0.020895 | 0.027921 | 1.6484 | -4.0875 | 0.20744 | -4.1975 | 116.9704 | 116.8637 | 116.6628 | -4.1383 | -3.0758 | -2.0784 | -0.47301 | -0.47865 | -0.38005 | -0.3448 | -4.0104 | -4.0284 | -4.044 | -3.9776 | -4.0877 | -0.059236 | -4.1507 | -4.3516 | -3.9005 | -121.4931 | -2.966 | -0.36315 | 3.5373 | -121.3945 | -121.3592 | 117.0803 | 116.9735 | 116.7727 | 0.31731 | -125.1527 | -0.36878 | -0.27019 | -0.23494 | -1.9685 | -125.0248
1155.5156 | 121.106 | -7.8964 | 113.2004 | 1.4211e-13 | -0.034906 | 0.0020727 | 0.063218 | -0.0076043 | 0.05311 | -0.0099192 | -0.0025167 | -0.00084406 | 0.020467 | 0.030698 | 3.5725 | -8.5376 | 0.10214 | -8.6522 | 112.4928 | 112.3992 | 112.2445 | -8.557 | -6.4366 | -4.4273 | -0.89426 | -0.90445 | -0.81044 | -0.76145 | -8.2229 | -0.66054 | -0.70762 | -0.64122 | -0.75578 | -0.095241 | -0.80116 | -0.95591 | -0.32644 | -114.1048 | 1.4598 | 7.0022 | 7.3286 | -114.0108 | -113.9618 | 120.3892 | 120.2956 | 120.1409 | 7.9986 | -121.7573 | 6.992 | 7.086 | 7.135 | 3.4692 | -121.4232
1157.25 | 121.1929 | -3.0533 | 117.8833 | 1.4211e-13 | -0.034692 | 0.0020727 | 0.063218 | -0.0080317 | 0.052683 | -0.0099192 | -0.0029439 | -0.0014849 | 0.021108 | 0.026852 | 1.4349 | -2.3797 | 0.11587 | -2.4624 | 118.582 | 118.4388 | 118.2928 | -2.4716 | -1.8304 | -1.1535 | -0.3036 | -0.30924 | -0.21064 | -0.16624 | -2.3666 | 0.58171 | 0.69871 | 0.67357 | 0.59092 | 0.009204 | 0.55552 | 0.4095 | 0.68672 | -118.1925 | 1.2228 | 2.7497 | 2.063 | -118.0939 | -118.0495 | 121.6353 | 121.4921 | 121.3461 | 3.1692 | -120.3549 | 2.744 | 2.8426 | 2.887 | 1.8998 | -120.2499
1159.0156 | 120.7352 | -13.5727 | 107.0389 | 1.4211e-13 | -0.034906 | 0.0018589 | 0.063218 | -0.0078179 | 0.052469 | -0.0022892 | -0.0025167 | -0.0012713 | 0.020467 | 0.031126 | 6.1571 | -10.1492 | -0.039801 | -10.2317 | 110.7209 | 110.5585 | 110.4726 | -10.1779 | -7.4897 | -5.0729 | -1.0682 | -1.0693 | -0.97527 | -0.93544 | -9.5049 | 3.3948 | 3.682 | 3.4235 | 3.341 | -0.053808 | 3.5196 | 3.4337 | 4.0678 | -108.1082 | 6.083 | 12.5044 | 8.4367 | -108.0142 | -107.9743 | 124.2936 | 124.1312 | 124.0452 | 13.5329 | -117.2168 | 12.5034 | 12.5974 | 12.6373 | 8.4998 | -116.5438
1160.7812 | 120.845 | -9.1736 | 111.3373 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063004 | -0.0073907 | 0.052683 | -0.0099192 | 0.010302 | 0.010694 | -0.0043158 | 0.02728 | 5.7242 | -8.1119 | 0.019721 | -8.2081 | 112.6118 | 112.4542 | 112.3498 | -8.1723 | -5.5804 | -4.1663 | -4.3787 | -4.2971 | -4.1895 | -3.9665 | -7.5177 | 1.0013 | 1.2745 | 1.0617 | 0.96547 | -0.035777 | 1.1169 | 1.0125 | 1.6559 | -115.6344 | 3.5932 | 4.7949 | 3.1391 | -115.5267 | -115.3038 | 121.7854 | 121.6278 | 121.5234 | 9.1933 | -119.5096 | 4.8765 | 4.9841 | 5.2071 | 5.0073 | -118.855
1162.4688 | 120.5521 | -13.4949 | 106.8054 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063004 | -0.0076043 | 0.052683 | -0.0022892 | 0.021838 | 0.021804 | -0.028244 | 0.026425 | 7.0271 | -11.9806 | 0.015142 | -12.0539 | 108.5965 | 108.4613 | 108.3481 | -11.9774 | -7.8606 | -7.6415 | -7.8814 | -7.5387 | -7.4586 | -7.405 | -10.755 | 1.5175 | 1.7911 | 1.5143 | 1.441 | -0.076446 | 1.6559 | 1.5427 | 2.7399 | -114.3441 | 5.6343 | 5.6135 | 2.8736 | -114.264 | -114.2104 | 122.0914 | 121.9562 | 121.843 | 13.51 | -118.7828 | 5.9562 | 6.0363 | 6.0899 | 5.8534 | -117.5604
1164.2188 | 121.0648 | -116.3818 | 4.6234 | 1.4211e-13 | -0.035547 | 0.00079051 | 0.062363 | -0.0076043 | 0.053751 | -0.01755 | -0.0048667 | -0.0014849 | 0.021536 | 0.025357 | 0.019705 | -115.9466 | -0.21837 | -116.1685 | 4.571 | 4.5839 | 4.6473 | -116.4044 | 0.037677 | 0.078197 | -0.051772 | -0.066582 | 0.032021 | 0.081008 | -0.1092 | -0.022536 | -0.052416 | 0.43521 | 0.21329 | 0.23583 | -0.039551 | 0.023898 | 116.2726 | -4.69 | 116.4195 | 116.3301 | 0.057431 | -4.5914 | -4.5424 | 120.9528 | 120.9657 | 121.0291 | 116.1635 | -121.0278 | 116.3153 | 116.4139 | 116.4628 | 116.46 | -4.7326
1165.9688 | 121.2296 | -116.629 | 4.3991 | 1.4211e-13 | -0.035547 | 0.0010043 | 0.062577 | -0.0076043 | 0.053751 | -0.0022892 | -0.0046531 | -0.0014849 | 0.021108 | 0.025357 | 0.018423 | -116.2259 | -0.14969 | -116.4478 | 4.365 | 4.3778 | 4.4504 | -116.6745 | 0.042256 | 0.082776 | -0.038036 | -0.062004 | 0.0366 | 0.081008 | -0.11378 | -0.045501 | -0.03414 | 0.40312 | 0.18121 | 0.22671 | -0.021298 | 0.051322 | 116.5152 | -4.4611 | 116.6713 | 116.591 | 0.075746 | -4.3625 | -4.3181 | 120.994 | 121.0068 | 121.0795 | 116.4793 | -121.0736 | 116.567 | 116.6656 | 116.71 | 116.7118 | -4.5129
1167.6562 | 121.3074 | -116.5558 | 4.4495 | 1.4211e-13 | -0.03576 | 0.0012179 | 0.062791 | -0.0078179 | 0.053538 | -0.0099192 | -0.0046531 | -0.0016987 | 0.021536 | 0.025143 | 0.01821 | -116.1298 | -0.12222 | -116.3517 | 4.4977 | 4.5152 | 4.5832 | -116.5829 | 0.042256 | 0.073618 | -0.047194 | -0.062004 | 0.0366 | 0.090166 | -0.11378 | -0.027164 | 0.048279 | 0.42602 | 0.20411 | 0.23128 | 0.065716 | 0.13375 | 116.442 | -4.5115 | 116.598 | 116.5086 | 0.066588 | -4.4129 | -4.3593 | 121.0535 | 121.071 | 121.139 | 116.4336 | -121.0324 | 116.4938 | 116.5924 | 116.646 | 116.6294 | -4.5632
1169.4062 | 121.3165 | -116.1758 | 4.8386 | 1.4211e-13 | -0.035974 | 0.00079051 | 0.062791 | -0.0078179 | 0.053965 | -0.0099192 | -0.0046531 | -0.0014849 | 0.021322 | 0.025143 | 0.01821 | -115.8184 | -0.10848 | -116.0358 | 4.8457 | 4.8586 | 4.9266 | -116.267 | 0.033099 | 0.078197 | -0.047194 | -0.066582 | 0.041178 | 0.085587 | -0.11378 | -0.091162 | 0.007138 | 0.35741 | 0.14007 | 0.23123 | 0.020036 | 0.088044 | 116.0621 | -4.9051 | 116.2089 | 116.1286 | 0.066588 | -4.7974 | -4.753 | 121.0215 | 121.0344 | 121.1024 | 116.0674 | -121.1056 | 116.1093 | 116.217 | 116.2614 | 116.254 | -4.9523
1171.1562 | 121.3531 | -116.4505 | 4.6097 | 1.4211e-13 | -0.035974 | 0.0010043 | 0.062577 | -0.0076043 | 0.053965 | -0.01755 | -0.0050803 | -0.0012713 | 0.021536 | 0.025143 | 0.01821 | -116.1069 | -0.085587 | -116.3242 | 4.5664 | 4.5976 | 4.6519 | -116.5555 | 0.042256 | 0.082776 | -0.042615 | -0.062004 | 0.041178 | 0.07643 | -0.10462 | -0.10498 | -0.043262 | 0.34363 | 0.12629 | 0.23127 | -0.012081 | 0.042209 | 116.3459 | -4.6717 | 116.4928 | 116.4079 | 0.062009 | -4.5685 | -4.5332 | 121.0169 | 121.0481 | 121.1024 | 116.3649 | -121.1652 | 116.3885 | 116.4917 | 116.5269 | 116.5333 | -4.7143
1172.9062 | 121.257 | -116.5375 | 4.5822 | 1.4211e-13 | -0.036188 | 0.0012179 | 0.062791 | -0.0076043 | 0.053751 | -0.0022892 | -0.0044395 | -0.0012713 | 0.021536 | 0.025357 | 0.017996 | -116.0886 | -0.07643 | -116.3059 | 4.5985 | 4.6205 | 4.6885 | -116.5417 | 0.042256 | 0.087354 | -0.042615 | -0.071161 | 0.0366 | 0.085587 | -0.1092 | -0.004264 | 0.016253 | 0.44892 | 0.23158 | 0.23585 | 0.03828 | 0.1063 | 116.4283 | -4.6534 | 116.5797 | 116.4949 | 0.066588 | -4.5456 | -4.4966 | 121.1359 | 121.158 | 121.226 | 116.461 | -121.124 | 116.4663 | 116.5741 | 116.6231 | 116.6248 | -4.6914
1174.6094 | 121.3165 | -107.0847 | 13.9938 | 1.4211e-13 | -0.03576 | 0.0012179 | 0.062791 | -0.0076043 | 0.053538 | -0.01755 | -0.0044395 | -0.0014849 | 0.021322 | 0.024929 | 0.01821 | -104.5602 | -0.090166 | -104.8053 | 16.1177 | 16.1365 | 16.1579 | -104.9342 | 0.046835 | 0.082776 | -0.042615 | -0.057425 | 0.041178 | 0.085587 | -0.10462 | 2.1505 | 2.1239 | 2.5245 | 2.2794 | 0.12892 | 2.1427 | 2.1641 | 106.98 | -14.0513 | 107.1315 | 107.042 | 0.062009 | -13.9527 | -13.9082 | 123.2023 | 123.2211 | 123.2426 | 106.9945 | -118.928 | 107.0272 | 107.1258 | 107.1702 | 107.1674 | -14.0985
1176.375 | 121.1975 | -1.3733 | 119.9707 | 1.4211e-13 | -0.035119 | 0.0020727 | 0.063218 | -0.0078179 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021536 | 0.024929 | 0.017996 | -1.2534 | 0.27154 | -1.327 | 119.9189 | 119.7667 | 119.6206 | -1.3039 | 0.02852 | 0.064461 | -0.065509 | -0.080318 | 0.018285 | 0.071851 | -0.1321 | 0.069345 | -0.051803 | 0.11986 | 0.046337 | -0.023008 | -0.20399 | -0.3501 | 1.2412 | -120.051 | 1.4018 | 1.3078 | 0.066588 | -119.9524 | -119.8989 | 121.2922 | 121.14 | 120.9939 | 1.6448 | -121.2746 | 1.293 | 1.3916 | 1.4451 | 1.4378 | -120.1028
1178.0625 | 121.2433 | -1.1856 | 120.1263 | 1.4211e-13 | -0.034906 | 0.0016453 | 0.063645 | -0.0080317 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.021536 | 0.02557 | 0.01821 | -1.1069 | 0.20744 | -1.1804 | 120.1112 | 119.959 | 119.8083 | -1.162 | 0.023941 | 0.059882 | -0.056351 | -0.080318 | 0.027442 | 0.062694 | -0.12752 | 0.023609 | -0.01515 | 0.078686 | 0.005159 | -0.01845 | -0.16732 | -0.31802 | 1.0581 | -120.2067 | 1.2095 | 1.1293 | 0.071167 | -120.0989 | -120.0636 | 121.2968 | 121.1446 | 120.9939 | 1.3931 | -121.2883 | 1.1053 | 1.213 | 1.2483 | 1.2455 | -120.2539
1179.8125 | 121.2982 | -0.9201 | 120.4147 | 1.4211e-13 | -0.034906 | 0.0020727 | 0.063432 | -0.0078179 | 0.052683 | -0.0099192 | -0.0046531 | -0.0010577 | 0.020681 | 0.02557 | 0.017996 | -0.82764 | 0.17539 | -0.90575 | 120.4134 | 120.2658 | 120.1014 | -0.88269 | 0.023941 | 0.064461 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.12294 | 0.03742 | -0.001368 | 0.092464 | 0.014353 | -0.023067 | -0.14892 | -0.31338 | 0.79717 | -120.4951 | 0.94405 | 0.85917 | 0.062009 | -120.3873 | -120.352 | 121.3335 | 121.1859 | 121.0215 | 1.0955 | -121.2974 | 0.83979 | 0.94755 | 0.9828 | 0.98457 | -120.5377
1181.5625 | 121.3806 | -1.03 | 120.2591 | 1.4211e-13 | -0.034906 | 0.0016453 | 0.063218 | -0.0078179 | 0.052683 | -0.0099192 | -0.0044395 | -0.0010577 | 0.021322 | 0.025357 | 0.017996 | -0.92836 | 0.14792 | -1.0111 | 120.3172 | 120.1742 | 120.0144 | -0.98342 | 0.023941 | 0.059882 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.12294 | 0.046547 | 0.058126 | 0.1016 | 0.018915 | -0.027632 | -0.08486 | -0.24474 | 0.90703 | -120.3394 | 1.0539 | 0.96904 | 0.062009 | -120.2362 | -120.1918 | 121.3472 | 121.2042 | 121.0443 | 1.1779 | -121.2425 | 0.94965 | 1.0528 | 1.0972 | 1.0898 | -120.382
1183.3125 | 121.3303 | -2.2156 | 119.0735 | 1.4211e-13 | -0.034692 | 0.0018589 | 0.063859 | -0.0076043 | 0.052683 | -0.0099192 | -0.0048667 | -0.0016987 | 0.021536 | 0.025143 | 0.017996 | -2.2424 | 0.14334 | -2.3342 | 118.9941 | 118.8555 | 118.7003 | -2.2976 | 0.023941 | 0.064461 | -0.06093 | -0.080318 | 0.022864 | 0.071851 | -0.1321 | -0.081996 | -0.07942 | -0.026787 | -0.1186 | -0.036604 | -0.21798 | -0.37319 | 2.0835 | -119.1538 | 2.2395 | 2.1546 | 0.071167 | -119.0506 | -119.0016 | 121.2096 | 121.0711 | 120.9159 | 2.3589 | -121.3711 | 2.1353 | 2.2384 | 2.2874 | 2.28 | -119.2056
1185.0938 | 121.3394 | -1.2955 | 120.0394 | 1.4211e-13 | -0.034906 | 0.0022863 | 0.063432 | -0.0078179 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021322 | 0.025357 | 0.017782 | -1.1893 | 0.12961 | -1.272 | 120.0837 | 119.9407 | 119.79 | -1.2444 | 0.023941 | 0.064461 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.12752 | 0.051051 | 0.044354 | 0.10614 | 0.023456 | -0.027595 | -0.09866 | -0.24936 | 1.168 | -120.1151 | 1.3194 | 1.2345 | 0.066588 | -120.0119 | -119.9721 | 121.3792 | 121.2362 | 121.0855 | 1.4251 | -121.2838 | 1.2197 | 1.3229 | 1.3627 | 1.3599 | -120.1669
1186.8438 | 121.3394 | -1.1398 | 120.2454 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063645 | -0.0078179 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.025357 | 0.01821 | -1.0016 | 0.12503 | -1.0751 | 120.2852 | 120.133 | 119.9823 | -1.0521 | 0.023941 | 0.064461 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.12294 | 0.087727 | 0.03981 | 0.13821 | 0.064683 | -0.023044 | -0.11234 | -0.26305 | 1.0169 | -120.3257 | 1.1638 | 1.0789 | 0.062009 | -120.2225 | -120.1781 | 121.425 | 121.2729 | 121.1221 | 1.2649 | -121.2975 | 1.0595 | 1.1627 | 1.2071 | 1.2043 | -120.3683
1188.5312 | 121.3028 | -1.0345 | 120.3964 | 1.4211e-13 | -0.035333 | 0.0020727 | 0.063645 | -0.0078179 | 0.05311 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021108 | 0.025357 | 0.017996 | -0.89632 | 0.11587 | -0.98358 | 120.3951 | 120.2521 | 120.0968 | -0.95595 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.009128 | 0.067272 | -0.12294 | 0.078598 | -0.00137 | 0.13823 | 0.050963 | -0.027635 | -0.14435 | -0.29965 | 0.91161 | -120.4767 | 1.0585 | 0.97362 | 0.062009 | -120.3873 | -120.3292 | 121.4296 | 121.2866 | 121.1313 | 1.1504 | -121.3524 | 0.95423 | 1.0437 | 1.1018 | 1.1082 | -120.5194
1190.2969 | 121.344 | -0.97961 | 120.4376 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063645 | -0.0080317 | 0.052897 | -0.0022892 | -0.0046531 | -0.0016987 | 0.021536 | 0.024929 | 0.017996 | -0.86427 | 0.11587 | -0.93322 | 120.4408 | 120.2933 | 120.1471 | -0.91474 | 0.033099 | 0.073618 | -0.056351 | -0.084896 | 0.018285 | 0.058115 | -0.12294 | 0.064877 | 0.003214 | 0.11535 | 0.046392 | -0.018485 | -0.14434 | -0.29048 | 0.85667 | -120.5225 | 1.0127 | 0.92326 | 0.066588 | -120.4193 | -120.3795 | 121.4205 | 121.2729 | 121.1268 | 1.0955 | -121.3524 | 0.89472 | 0.9979 | 1.0377 | 1.0532 | -120.5606
1192.0625 | 121.4905 | -0.92926 | 120.4102 | 1.4211e-13 | -0.035119 | 0.0020727 | 0.063432 | -0.0076043 | 0.052897 | -0.0022892 | -0.0044395 | -0.0010577 | 0.021322 | 0.024929 | 0.017782 | -0.85511 | 0.12045 | -0.93322 | 120.4591 | 120.3162 | 120.1609 | -0.901 | 0.033099 | 0.06904 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.11836 | 0.02826 | 0.048994 | 0.074149 | -0.003962 | -0.032222 | -0.093976 | -0.24928 | 0.8109 | -120.4951 | 0.96236 | 0.86833 | 0.057431 | -120.3919 | -120.3475 | 121.3884 | 121.2454 | 121.0901 | 1.0497 | -121.3112 | 0.84436 | 0.94754 | 0.99195 | 0.9983 | -120.5285
1193.8438 | 121.431 | -0.97046 | 120.4285 | 1.4211e-13 | -0.034906 | 0.0018589 | 0.063645 | -0.0078179 | 0.052897 | -0.01755 | -0.0046531 | -0.00084406 | 0.021108 | 0.025143 | 0.017782 | -0.86427 | 0.11129 | -0.94696 | 120.45 | 120.3024 | 120.1655 | -0.91016 | 0.019362 | 0.059882 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.12294 | 0.060301 | 0.021526 | 0.10619 | 0.023502 | -0.036799 | -0.12602 | -0.26301 | 0.84752 | -120.5134 | 0.98982 | 0.90953 | 0.062009 | -120.4102 | -120.3704 | 121.4205 | 121.2729 | 121.1359 | 1.0818 | -121.3386 | 0.88556 | 0.98874 | 1.0286 | 1.0303 | -120.5514
1195.5312 | 121.4081 | -1.0117 | 120.4147 | 1.4211e-13 | -0.035119 | 0.0020727 | 0.063432 | -0.0078179 | 0.052897 | -0.0022892 | -0.0042257 | -0.0012713 | 0.021322 | 0.025143 | 0.017782 | -0.88716 | 0.11129 | -0.96069 | 120.4454 | 120.2933 | 120.1471 | -0.93305 | 0.02852 | 0.064461 | -0.065509 | -0.084896 | 0.009128 | 0.067272 | -0.12294 | 0.078605 | 0.030681 | 0.1245 | 0.050966 | -0.027639 | -0.12145 | -0.2676 | 0.88872 | -120.4996 | 1.0402 | 0.94615 | 0.05743 | -120.4056 | -120.3475 | 121.4571 | 121.3049 | 121.1588 | 1.123 | -121.3478 | 0.92676 | 1.0208 | 1.0789 | 1.0761 | -120.5377
1197.2656 | 121.4081 | -1.0117 | 120.4102 | 1.4211e-13 | -0.034906 | 0.0020727 | 0.063859 | -0.0076043 | 0.052469 | -0.0099192 | -0.0046531 | -0.0010577 | 0.021749 | 0.025357 | 0.017782 | -0.86427 | 0.10214 | -0.94696 | 120.4683 | 120.3208 | 120.1792 | -0.9239 | 0.02852 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.12294 | 0.087763 | 0.058151 | 0.14739 | 0.064701 | -0.023062 | -0.089397 | -0.23097 | 0.88872 | -120.4905 | 1.0402 | 0.95073 | 0.062009 | -120.3919 | -120.3429 | 121.48 | 121.3324 | 121.1908 | 1.1138 | -121.3341 | 0.93134 | 1.0299 | 1.0789 | 1.0807 | -120.5331
1198.9531 | 121.3943 | -1.0391 | 120.3964 | 1.4211e-13 | -0.035119 | 0.0020727 | 0.063645 | -0.0076043 | 0.052683 | 0.0053413 | -0.0046531 | -0.0012713 | 0.021322 | 0.025143 | 0.017782 | -0.91463 | 0.10671 | -0.98816 | 120.4271 | 120.275 | 120.1288 | -0.9651 | 0.023941 | 0.059882 | -0.065509 | -0.084896 | 0.018285 | 0.058115 | -0.12752 | 0.074019 | 0.030678 | 0.12449 | 0.050963 | -0.023056 | -0.12145 | -0.2676 | 0.91161 | -120.4813 | 1.0631 | 0.97361 | 0.062009 | -120.3781 | -120.3383 | 121.4662 | 121.3141 | 121.1679 | 1.1458 | -121.3615 | 0.95423 | 1.0574 | 1.0972 | 1.099 | -120.5239
1200.7031 | 121.4767 | -1.0483 | 120.3461 | 1.4211e-13 | -0.035333 | 0.0016453 | 0.063645 | -0.0080317 | 0.052469 | -0.0022892 | -0.0044395 | -0.0014849 | 0.021749 | 0.025143 | 0.017782 | -0.95126 | 0.10671 | -1.0248 | 120.3951 | 120.2612 | 120.1059 | -0.99716 | 0.02852 | 0.064461 | -0.065509 | -0.080318 | 0.018285 | 0.058115 | -0.12752 | 0.051121 | 0.048984 | 0.097022 | 0.023491 | -0.02763 | -0.084836 | -0.24014 | 0.92076 | -120.4264 | 1.0768 | 0.98277 | 0.062009 | -120.3278 | -120.288 | 121.4433 | 121.3095 | 121.1542 | 1.155 | -121.3432 | 0.96796 | 1.0666 | 1.1064 | 1.1127 | -120.4736
1202.4688 | 121.5454 | -1.2451 | 120.1263 | 1.4211e-13 | -0.035547 | 0.0018589 | 0.063645 | -0.0078179 | 0.052683 | -0.0022892 | -0.0050803 | -0.0010577 | 0.021322 | 0.02557 | 0.017996 | -1.1527 | 0.10671 | -1.2354 | 120.189 | 120.0414 | 119.9045 | -1.2032 | 0.019362 | 0.064461 | -0.056351 | -0.075739 | 0.018285 | 0.062694 | -0.12294 | 0.041908 | 0.062682 | 0.092411 | 0.009728 | -0.03218 | -0.084898 | -0.22187 | 1.1222 | -120.2021 | 1.2645 | 1.1888 | 0.066588 | -120.1081 | -120.0636 | 121.4341 | 121.2866 | 121.1496 | 1.3518 | -121.3296 | 1.1694 | 1.2634 | 1.3078 | 1.3096 | -120.2493
1204.1719 | 121.4493 | -1.6251 | 119.7968 | 1.4211e-13 | -0.035119 | 0.0022863 | 0.063645 | -0.0080317 | 0.052683 | -0.0022892 | -0.0048667 | -0.0010577 | 0.021322 | 0.02557 | 0.017782 | -1.4778 | 0.10214 | -1.5604 | 119.8685 | 119.7301 | 119.5702 | -1.5329 | 0.023941 | 0.064461 | -0.051772 | -0.084896 | 0.018285 | 0.062694 | -0.11836 | 0.092169 | 0.071785 | 0.14729 | 0.064615 | -0.027554 | -0.066675 | -0.22652 | 1.5067 | -119.8816 | 1.649 | 1.5733 | 0.066589 | -119.7785 | -119.7341 | 121.4936 | 121.3551 | 121.1953 | 1.7272 | -121.3296 | 1.5402 | 1.6433 | 1.6878 | 1.6895 | -119.9151
1205.9375 | 121.4905 | -1.7258 | 119.6365 | 1.4211e-13 | -0.035119 | 0.0018589 | 0.063645 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.021322 | 0.025357 | 0.017782 | -1.6014 | 0.097557 | -1.6886 | 119.7587 | 119.611 | 119.4649 | -1.6474 | 0.019362 | 0.06904 | -0.065509 | -0.080318 | 0.018285 | 0.062694 | -0.11836 | 0.078404 | 0.12212 | 0.12438 | 0.037131 | -0.041273 | -0.02551 | -0.17161 | 1.6074 | -119.7169 | 1.7451 | 1.6603 | 0.052852 | -119.6183 | -119.5738 | 121.4844 | 121.3368 | 121.1907 | 1.8233 | -121.2839 | 1.6455 | 1.7441 | 1.7885 | 1.7948 | -119.7549
1207.6406 | 121.5042 | -2.2385 | 119.1605 | 1.4211e-13 | -0.035333 | 0.0016453 | 0.063432 | -0.0076043 | 0.052683 | -0.0099192 | -0.0048667 | -0.00084406 | 0.021536 | 0.025357 | 0.017782 | -2.1325 | 0.097557 | -2.2243 | 119.2276 | 119.0845 | 118.9475 | -2.1785 | 0.02852 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.071851 | -0.11836 | 0.059944 | 0.067103 | 0.10598 | 0.014167 | -0.045777 | -0.076011 | -0.21292 | 2.1201 | -119.2408 | 2.267 | 2.1775 | 0.057431 | -119.1422 | -119.0886 | 121.466 | 121.3229 | 121.186 | 2.336 | -121.339 | 2.1581 | 2.2567 | 2.3103 | 2.3075 | -119.2788
1209.3906 | 121.4813 | -2.4216 | 119.0094 | 1.4211e-13 | -0.035119 | 0.0018589 | 0.063859 | -0.0076043 | 0.052683 | -0.01755 | -0.0044395 | -0.00084406 | 0.021322 | 0.025357 | 0.017569 | -2.3065 | 0.10214 | -2.38 | 119.0673 | 118.9288 | 118.769 | -2.3479 | 0.02852 | 0.064461 | -0.056351 | -0.084896 | 0.009128 | 0.062694 | -0.11836 | 0.073629 | 0.057921 | 0.11511 | 0.041611 | -0.032018 | -0.080633 | -0.24042 | 2.3032 | -119.0943 | 2.4501 | 2.3652 | 0.06201 | -119.0003 | -118.9467 | 121.4889 | 121.3503 | 121.1905 | 2.5237 | -121.3573 | 2.3367 | 2.4307 | 2.4843 | 2.486 | -119.1278
1211.1562 | 121.5637 | -2.6184 | 118.7851 | 1.4211e-13 | -0.035119 | 0.0022863 | 0.063645 | -0.0076043 | 0.052683 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.025357 | 0.017996 | -2.4896 | 0.097557 | -2.5906 | 118.8796 | 118.7273 | 118.5996 | -2.5403 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.071851 | -0.11378 | 0.078153 | 0.094511 | 0.12881 | 0.027848 | -0.050305 | -0.057802 | -0.18552 | 2.5046 | -118.87 | 2.6423 | 2.5575 | 0.052852 | -118.7622 | -118.7132 | 121.498 | 121.3457 | 121.218 | 2.716 | -121.3254 | 2.5335 | 2.6413 | 2.6903 | 2.6874 | -118.8989
1212.9062 | 121.5179 | -2.6276 | 118.7759 | 1.4211e-13 | -0.035119 | 0.0022863 | 0.063645 | -0.0080317 | 0.052683 | -0.01755 | -0.0046531 | -0.0010577 | 0.021322 | 0.025357 | 0.017782 | -2.4713 | 0.097557 | -2.5539 | 118.9025 | 118.7639 | 118.6179 | -2.5219 | 0.019362 | 0.064461 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.10562 | 0.12656 | 0.15628 | 0.07363 | -0.031993 | -0.012015 | -0.15806 | 2.5092 | -118.8563 | 2.6469 | 2.5666 | 0.057431 | -118.7439 | -118.7087 | 121.5301 | 121.3915 | 121.2454 | 2.7251 | -121.2979 | 2.5472 | 2.6596 | 2.6948 | 2.692 | -118.8943
1214.6562 | 121.5088 | -2.6184 | 118.7851 | 1.4211e-13 | -0.034906 | 0.0018589 | 0.063859 | -0.0078179 | 0.052683 | -0.0099192 | -0.0044395 | -0.0012713 | 0.021536 | 0.025143 | 0.017996 | -2.5262 | 0.10214 | -2.618 | 118.8521 | 118.7181 | 118.5629 | -2.5723 | 0.023941 | 0.064461 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.11836 | 0.0461 | 0.067041 | 0.092185 | 0.000379 | -0.045721 | -0.066959 | -0.22215 | 2.5 | -118.8746 | 2.6423 | 2.5575 | 0.057431 | -118.7668 | -118.7224 | 121.4705 | 121.3365 | 121.1813 | 2.7205 | -121.3574 | 2.5289 | 2.6367 | 2.6811 | 2.6829 | -118.9035
1216.3438 | 121.5591 | -2.6825 | 118.7302 | 1.4211e-13 | -0.035333 | 0.0020727 | 0.063645 | -0.0078179 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.02557 | 0.017996 | -2.5812 | 0.097557 | -2.6684 | 118.7972 | 118.6632 | 118.5172 | -2.6227 | 0.02852 | 0.055303 | -0.065509 | -0.080318 | 0.022864 | 0.058115 | -0.12752 | 0.059819 | 0.067031 | 0.10133 | 0.014105 | -0.045714 | -0.066976 | -0.21301 | 2.555 | -118.8105 | 2.711 | 2.617 | 0.062009 | -118.7073 | -118.672 | 121.4797 | 121.3457 | 121.1997 | 2.7801 | -121.3528 | 2.6022 | 2.7054 | 2.7406 | 2.7378 | -118.8577
1218.0938 | 121.4539 | -2.6733 | 118.7897 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063859 | -0.0076043 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.02557 | 0.01821 | -2.5445 | 0.10671 | -2.6272 | 118.843 | 118.7044 | 118.5584 | -2.5906 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.11378 | 0.082716 | 0.053306 | 0.1288 | 0.046154 | -0.036562 | -0.085274 | -0.23131 | 2.5596 | -118.87 | 2.6973 | 2.6124 | 0.052852 | -118.7668 | -118.7316 | 121.5163 | 121.3777 | 121.2317 | 2.7801 | -121.3803 | 2.593 | 2.6962 | 2.7315 | 2.7424 | -118.9035
1219.8594 | 121.4447 | -2.6413 | 118.8309 | 1.4211e-13 | -0.035119 | 0.0020727 | 0.063859 | -0.0078179 | 0.052683 | 0.0053413 | -0.0044395 | -0.0010577 | 0.021749 | 0.025357 | 0.017569 | -2.5216 | 0.097557 | -2.6089 | 118.8796 | 118.7365 | 118.5858 | -2.5631 | 0.023941 | 0.064461 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.11378 | 0.078146 | 0.048734 | 0.11965 | 0.032423 | -0.045723 | -0.094421 | -0.24504 | 2.5275 | -118.9112 | 2.6652 | 2.5758 | 0.048273 | -118.8172 | -118.7728 | 121.5209 | 121.3777 | 121.2271 | 2.7389 | -121.394 | 2.561 | 2.655 | 2.6994 | 2.7058 | -118.9447
1221.5625 | 121.431 | -2.742 | 118.7485 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063432 | -0.0078179 | 0.05311 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021322 | 0.025357 | 0.017569 | -2.5995 | 0.092979 | -2.673 | 118.8018 | 118.654 | 118.5126 | -2.6456 | 0.023941 | 0.073618 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.096433 | 0.0533 | 0.14253 | 0.069035 | -0.027398 | -0.094443 | -0.2359 | 2.6282 | -118.8288 | 2.7659 | 2.6765 | 0.048273 | -118.721 | -118.6858 | 121.5438 | 121.396 | 121.2546 | 2.835 | -121.394 | 2.6617 | 2.7694 | 2.8047 | 2.8156 | -118.8623
1223.3281 | 121.4813 | -2.7969 | 118.7027 | 1.4211e-13 | -0.035119 | 0.0018589 | 0.063645 | -0.0080317 | 0.052897 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021322 | 0.02557 | 0.017569 | -2.6682 | 0.10214 | -2.7554 | 118.7285 | 118.5945 | 118.4531 | -2.7234 | 0.023941 | 0.064461 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.11836 | 0.073524 | 0.025821 | 0.12878 | 0.041558 | -0.031966 | -0.10819 | -0.24964 | 2.6786 | -118.783 | 2.8209 | 2.736 | 0.057431 | -118.6844 | -118.6354 | 121.5255 | 121.3914 | 121.25 | 2.8991 | -121.4261 | 2.7166 | 2.8152 | 2.8642 | 2.8614 | -118.8211
1225.0938 | 121.5775 | -3.2455 | 118.1992 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063859 | -0.0076043 | 0.052897 | -0.0022892 | -0.0050803 | -0.0010577 | 0.021108 | 0.02557 | 0.017782 | -3.1672 | 0.092979 | -3.2544 | 118.2386 | 118.0954 | 117.954 | -3.2042 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.071851 | -0.12294 | 0.041344 | 0.039474 | 0.078347 | -0.008866 | -0.05021 | -0.10376 | -0.24517 | 3.1226 | -118.2841 | 3.2695 | 3.18 | 0.05743 | -118.1855 | -118.1273 | 121.4842 | 121.3409 | 121.1995 | 3.3385 | -121.4034 | 3.1606 | 3.2593 | 3.3174 | 3.3192 | -118.3221
1226.8438 | 121.4859 | -3.6987 | 117.8192 | 1.4211e-13 | -0.035547 | 0.0020727 | 0.063432 | -0.0080317 | 0.052683 | -0.0099192 | -0.0048667 | -0.00084406 | 0.021108 | 0.025357 | 0.017569 | -3.4968 | 0.0884 | -3.584 | 117.9181 | 117.7795 | 117.6335 | -3.5293 | 0.019362 | 0.064461 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.11836 | 0.16943 | 0.098931 | 0.20189 | 0.11468 | -0.054743 | -0.039758 | -0.18573 | 3.5804 | -117.895 | 3.7181 | 3.6378 | 0.057431 | -117.8101 | -117.7611 | 121.6169 | 121.4782 | 121.3322 | 3.7871 | -121.3485 | 3.623 | 3.7079 | 3.7568 | 3.7632 | -117.9376
1228.5469 | 121.4813 | -3.6713 | 117.8284 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063432 | -0.0078179 | 0.052897 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021322 | 0.025784 | 0.017996 | -3.5243 | 0.092979 | -3.6207 | 117.8815 | 117.7474 | 117.6106 | -3.5705 | 0.023941 | 0.06904 | -0.065509 | -0.080318 | 0.018285 | 0.058115 | -0.12294 | 0.10075 | 0.053149 | 0.14695 | 0.050592 | -0.05016 | -0.080965 | -0.21778 | 3.5483 | -117.9087 | 3.6952 | 3.6058 | 0.05743 | -117.8101 | -117.7703 | 121.5528 | 121.4187 | 121.2819 | 3.7642 | -121.3989 | 3.5909 | 3.6896 | 3.7294 | 3.7403 | -117.9513
1230.3125 | 121.5225 | -3.6987 | 117.8192 | 1.4211e-13 | -0.035547 | 0.0020727 | 0.063432 | -0.0076043 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.021322 | 0.025143 | 0.017996 | -3.5838 | 0.092979 | -3.6756 | 117.8403 | 117.697 | 117.5556 | -3.6255 | 0.019362 | 0.06904 | -0.065509 | -0.084896 | 0.027442 | 0.058115 | -0.11836 | 0.073269 | 0.021098 | 0.1149 | 0.023118 | -0.050151 | -0.12218 | -0.26356 | 3.5804 | -117.9041 | 3.7181 | 3.6332 | 0.052852 | -117.7918 | -117.7611 | 121.539 | 121.3958 | 121.2544 | 3.7917 | -121.4447 | 3.6138 | 3.7262 | 3.7568 | 3.7678 | -117.9376
1232.0781 | 121.5134 | -3.6804 | 117.8238 | 1.4211e-13 | -0.035333 | 0.0022863 | 0.063859 | -0.0078179 | 0.052469 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021536 | 0.025784 | 0.017996 | -3.5472 | 0.097557 | -3.639 | 117.8815 | 117.7382 | 117.6014 | -3.5797 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.018285 | 0.067272 | -0.11836 | 0.10075 | 0.057726 | 0.13322 | 0.041434 | -0.059315 | -0.085546 | -0.22236 | 3.5621 | -117.9087 | 3.7044 | 3.6195 | 0.057431 | -117.8055 | -117.7565 | 121.5619 | 121.4187 | 121.2819 | 3.778 | -121.4035 | 3.5955 | 3.6987 | 3.7477 | 3.7495 | -117.9422
1233.8438 | 121.5546 | -3.0487 | 118.3731 | 1.4211e-13 | -0.035547 | 0.0016453 | 0.063645 | -0.0078179 | 0.053324 | -0.02518 | -0.0048667 | -0.0010577 | 0.021322 | 0.025998 | 0.01821 | -2.9612 | 0.092979 | -3.053 | 118.4584 | 118.3289 | 118.1829 | -2.9981 | 0.023941 | 0.064461 | -0.06093 | -0.084896 | 0.018285 | 0.067272 | -0.11836 | 0.050558 | 0.085287 | 0.087537 | -0.00426 | -0.054818 | -0.044181 | -0.19019 | 2.9303 | -118.458 | 3.0726 | 2.9878 | 0.057431 | -118.3548 | -118.3058 | 121.5071 | 121.3776 | 121.2316 | 3.1417 | -121.3713 | 2.9638 | 3.067 | 3.116 | 3.1132 | -118.4915
1235.5312 | 121.4676 | -2.9572 | 118.5471 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063645 | -0.0080317 | 0.052683 | -0.0099192 | -0.0050803 | -0.0012713 | 0.021322 | 0.02557 | 0.017996 | -2.8559 | 0.097557 | -2.9385 | 118.5683 | 118.448 | 118.302 | -2.8928 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.06432 | 0.021218 | 0.10129 | 0.018644 | -0.045676 | -0.099079 | -0.2451 | 2.8434 | -118.632 | 2.9811 | 2.8962 | 0.052852 | -118.5196 | -118.4798 | 121.5254 | 121.4051 | 121.2591 | 3.0547 | -121.4399 | 2.8723 | 2.9846 | 3.0244 | 3.0353 | -118.6608
1237.2812 | 121.6049 | -2.9617 | 118.4601 | 1.4211e-13 | -0.035333 | 0.0020727 | 0.063432 | -0.0076043 | 0.052683 | -0.0022892 | -0.0046531 | -0.0010577 | 0.021108 | 0.025357 | 0.017569 | -2.7689 | 0.097557 | -2.8515 | 118.6644 | 118.5258 | 118.3935 | -2.8104 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.15132 | 0.20434 | 0.19285 | 0.11021 | -0.04111 | 0.065738 | -0.06655 | 2.8479 | -118.545 | 2.9903 | 2.9008 | 0.052852 | -118.4372 | -118.3974 | 121.6262 | 121.4876 | 121.3553 | 3.0593 | -121.2705 | 2.8768 | 2.9846 | 3.0244 | 3.0353 | -118.5739
1239.0312 | 121.4859 | -3.2547 | 118.2816 | 1.4211e-13 | -0.035333 | 0.0022863 | 0.063432 | -0.0078179 | 0.052683 | -0.0022892 | -0.0048667 | -0.00084406 | 0.021536 | 0.02557 | 0.017996 | -3.1672 | 0.097557 | -3.2636 | 118.2615 | 118.1275 | 117.9906 | -3.2134 | 0.023941 | 0.06904 | -0.056351 | -0.089475 | 0.022864 | 0.058115 | -0.11378 | 0.041343 | -0.020031 | 0.087503 | -0.008867 | -0.05021 | -0.1541 | -0.29094 | 3.1409 | -118.371 | 3.2786 | 3.1983 | 0.057431 | -118.2587 | -118.2234 | 121.5162 | 121.3822 | 121.2453 | 3.3523 | -121.4949 | 3.1652 | 3.2776 | 3.3128 | 3.3237 | -118.3953
1240.7344 | 121.5454 | -3.3417 | 118.1717 | 1.4211e-13 | -0.035333 | 0.0016453 | 0.063645 | -0.0078179 | 0.052683 | -0.0099192 | -0.0048667 | -0.0010577 | 0.021322 | 0.025357 | 0.017996 | -3.2542 | 0.097557 | -3.346 | 118.1883 | 118.0542 | 117.9174 | -3.2958 | 0.023941 | 0.064461 | -0.056351 | -0.084896 | 0.027442 | 0.058115 | -0.11378 | 0.045897 | 0.016578 | 0.087489 | -0.004301 | -0.050198 | -0.1175 | -0.25433 | 3.2279 | -118.2566 | 3.3656 | 3.2853 | 0.057431 | -118.1442 | -118.1136 | 121.5299 | 121.3959 | 121.259 | 3.4392 | -121.4675 | 3.2568 | 3.3691 | 3.3998 | 3.4061 | -118.2855
1242.4844 | 121.637 | -3.0487 | 118.3777 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063859 | -0.0078179 | 0.052897 | -0.0099192 | -0.0046531 | -0.0016987 | 0.021536 | 0.025143 | 0.017782 | -3.0161 | 0.0884 | -3.0987 | 118.4309 | 118.3015 | 118.1554 | -3.0531 | 0.02852 | 0.064461 | -0.056351 | -0.084896 | 0.032021 | 0.067272 | -0.11378 | -0.004389 | 0.053238 | 0.032596 | -0.050043 | -0.045654 | -0.076233 | -0.22224 | 2.9349 | -118.4626 | 3.0772 | 2.9924 | 0.057431 | -118.3457 | -118.3104 | 121.4796 | 121.3502 | 121.2042 | 3.1371 | -121.4308 | 2.9638 | 3.0807 | 3.116 | 3.1132 | -118.4915
1244.25 | 121.6049 | -2.9068 | 118.5562 | 1.4211e-13 | -0.035547 | 0.0018589 | 0.063859 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.02557 | 0.017996 | -2.8238 | 0.092979 | -2.9202 | 118.6232 | 118.4938 | 118.3523 | -2.8745 | 0.023941 | 0.064461 | -0.065509 | -0.084896 | 0.022864 | 0.058115 | -0.11836 | 0.032282 | 0.067004 | 0.082981 | -0.013397 | -0.045679 | -0.062445 | -0.20389 | 2.7884 | -118.6411 | 2.9307 | 2.8413 | 0.052852 | -118.5333 | -118.4981 | 121.53 | 121.4006 | 121.2591 | 2.9998 | -121.4307 | 2.8219 | 2.9297 | 2.9649 | 2.9713 | -118.6746
1246.0156 | 121.6095 | -2.9572 | 118.4875 | 1.4211e-13 | -0.03576 | 0.0016453 | 0.063859 | -0.0078179 | 0.052897 | -0.01755 | -0.0046531 | -0.0012713 | 0.021536 | 0.02557 | 0.017569 | -2.8696 | 0.097557 | -2.966 | 118.5729 | 118.4388 | 118.302 | -2.9157 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.018285 | 0.058115 | -0.11836 | 0.041426 | 0.085305 | 0.087551 | -0.008826 | -0.050252 | -0.048728 | -0.18559 | 2.8388 | -118.5633 | 2.9811 | 2.8962 | 0.057431 | -118.4693 | -118.4294 | 121.53 | 121.396 | 121.2591 | 3.0547 | -121.4033 | 2.8814 | 2.9754 | 3.0153 | 3.0308 | -118.6059
1247.7031 | 121.5134 | -3.0853 | 118.4372 | 1.4211e-13 | -0.035547 | 0.0018589 | 0.063859 | -0.0084589 | 0.052683 | -0.0022892 | -0.0048667 | -0.0010577 | 0.021322 | 0.02557 | 0.017569 | -2.9657 | 0.10214 | -3.0575 | 118.4859 | 118.3564 | 118.2195 | -3.0165 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.068863 | 0.04867 | 0.11958 | 0.027783 | -0.04108 | -0.080794 | -0.21765 | 2.9715 | -118.5221 | 3.1047 | 3.0244 | 0.052852 | -118.4098 | -118.3699 | 121.5712 | 121.4417 | 121.3049 | 3.1875 | -121.4537 | 3.0004 | 3.1128 | 3.1526 | 3.1589 | -118.551
1249.4531 | 121.4996 | -3.241 | 118.3044 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063859 | -0.0080317 | 0.052897 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.02557 | 0.017996 | -3.1031 | 0.092979 | -3.1995 | 118.3531 | 118.2099 | 118.0776 | -3.1584 | 0.023941 | 0.064461 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.11378 | 0.082557 | 0.048649 | 0.13787 | 0.041496 | -0.041061 | -0.094568 | -0.22683 | 3.1272 | -118.3939 | 3.2649 | 3.1755 | 0.048273 | -118.2907 | -118.2417 | 121.5941 | 121.4508 | 121.3186 | 3.3339 | -121.4629 | 3.1515 | 3.2547 | 3.3037 | 3.3054 | -118.4182
1251.2344 | 121.5546 | -3.4058 | 118.1259 | 1.4211e-13 | -0.03576 | 0.0020727 | 0.063859 | -0.0082453 | 0.052897 | -0.0022892 | -0.0044395 | -0.0010577 | 0.021322 | 0.02557 | 0.017782 | -3.2954 | 0.092979 | -3.3872 | 118.1654 | 118.0359 | 117.8899 | -3.3416 | 0.023941 | 0.06904 | -0.051772 | -0.080318 | 0.018285 | 0.062694 | -0.11378 | 0.064195 | 0.039462 | 0.11037 | 0.018582 | -0.045613 | -0.09004 | -0.23603 | 3.292 | -118.2062 | 3.4297 | 3.354 | 0.06201 | -118.1076 | -118.0632 | 121.5711 | 121.4416 | 121.2956 | 3.4987 | -121.4675 | 3.3254 | 3.424 | 3.4685 | 3.4748 | -118.2397
1252.9844 | 121.637 | -3.3508 | 118.1213 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063645 | -0.0076043 | 0.052683 | -0.0022892 | -0.0046531 | -0.0010577 | 0.021322 | 0.02557 | 0.017782 | -3.2588 | 0.10214 | -3.346 | 118.2157 | 118.0771 | 117.9403 | -3.2958 | 0.02852 | 0.06904 | -0.056351 | -0.084896 | 0.013707 | 0.062694 | -0.12294 | 0.055052 | 0.094402 | 0.092065 | 0.004854 | -0.050198 | -0.044252 | -0.18109 | 3.2279 | -118.2062 | 3.3794 | 3.2945 | 0.066588 | -118.1076 | -118.0586 | 121.5666 | 121.4279 | 121.2911 | 3.453 | -121.4171 | 3.2659 | 3.3645 | 3.4135 | 3.4199 | -118.2443
1254.6875 | 121.6415 | -3.2135 | 118.277 | 1.4211e-13 | -0.035547 | 0.0018589 | 0.063645 | -0.0078179 | 0.052683 | -0.0022892 | -0.0050803 | -0.00084406 | 0.021536 | 0.025784 | 0.017996 | -3.1306 | 0.097557 | -3.2224 | 118.3439 | 118.2007 | 118.0639 | -3.1721 | 0.02852 | 0.064461 | -0.06093 | -0.084896 | 0.013707 | 0.062694 | -0.1092 | 0.041354 | 0.066957 | 0.082931 | -0.008861 | -0.050215 | -0.076261 | -0.2131 | 3.1043 | -118.3619 | 3.242 | 3.1526 | 0.048273 | -118.2633 | -118.2143 | 121.5574 | 121.4142 | 121.2774 | 3.3111 | -121.4491 | 3.1286 | 3.2272 | 3.2762 | 3.278 | -118.3862
1256.4531 | 121.5408 | -3.0121 | 118.5471 | 1.4211e-13 | -0.035119 | 0.0020727 | 0.063859 | -0.0082453 | 0.052897 | -0.0022892 | -0.0050803 | -0.0014849 | 0.021108 | 0.025784 | 0.017569 | -2.8696 | 0.10214 | -2.9568 | 118.5957 | 118.4663 | 118.3203 | -2.9157 | 0.023941 | 0.06904 | -0.056351 | -0.084896 | 0.013707 | 0.053537 | -0.11378 | 0.096358 | 0.048688 | 0.14248 | 0.055263 | -0.041095 | -0.080763 | -0.22678 | 2.8983 | -118.632 | 3.036 | 2.9557 | 0.057431 | -118.5334 | -118.4935 | 121.6078 | 121.4784 | 121.3324 | 3.1142 | -121.4628 | 2.9272 | 3.0258 | 3.0656 | 3.0811 | -118.6608
1258.2031 | 121.55 | -2.9022 | 118.6752 | 1.4211e-13 | -0.035119 | 0.0016453 | 0.063432 | -0.0078179 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021108 | 0.02557 | 0.017782 | -2.7826 | 0.097557 | -2.8744 | 118.6919 | 118.5579 | 118.4164 | -2.8241 | 0.023941 | 0.059882 | -0.056351 | -0.080318 | 0.013707 | 0.067272 | -0.11378 | 0.078073 | 0.01666 | 0.11961 | 0.027809 | -0.050264 | -0.11736 | -0.25881 | 2.7884 | -118.7555 | 2.9262 | 2.8459 | 0.057431 | -118.6615 | -118.608 | 121.5941 | 121.4601 | 121.3186 | 2.9998 | -121.4994 | 2.8219 | 2.9159 | 2.9695 | 2.9621 | -118.789
1259.9531 | 121.5088 | -2.8519 | 118.7393 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063645 | -0.0078179 | 0.052897 | -0.0099192 | -0.0046531 | -0.0014849 | 0.021322 | 0.02557 | 0.017996 | -2.7368 | 0.10214 | -2.8241 | 118.7423 | 118.6082 | 118.4759 | -2.7829 | 0.023941 | 0.073618 | -0.065509 | -0.071161 | 0.013707 | 0.062694 | -0.11378 | 0.06893 | 0.002936 | 0.11504 | 0.027816 | -0.041114 | -0.13108 | -0.26337 | 2.7381 | -118.8105 | 2.8758 | 2.7864 | 0.048273 | -118.7256 | -118.6766 | 121.5941 | 121.4601 | 121.3278 | 2.954 | -121.5223 | 2.7807 | 2.8656 | 2.9146 | 2.9255 | -118.8531
1261.6562 | 121.5775 | -2.7374 | 118.8126 | 1.4211e-13 | -0.035547 | 0.0022863 | 0.063645 | -0.0078179 | 0.052897 | 0.0053413 | -0.0048667 | -0.0012713 | 0.020895 | 0.026211 | 0.017782 | -2.6224 | 0.097557 | -2.7096 | 118.8521 | 118.7273 | 118.5904 | -2.6593 | 0.02852 | 0.064461 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.11836 | 0.078119 | 0.039575 | 0.11506 | 0.027832 | -0.050287 | -0.085268 | -0.22215 | 2.6191 | -118.902 | 2.7659 | 2.6765 | 0.057431 | -118.7943 | -118.7499 | 121.5896 | 121.4647 | 121.3278 | 2.835 | -121.4719 | 2.648 | 2.7557 | 2.8001 | 2.8019 | -118.9309
1263.3906 | 121.6461 | -2.7008 | 118.8034 | 1.4211e-13 | -0.03576 | 0.0016453 | 0.064073 | -0.0084589 | 0.052683 | -0.0022892 | -0.0046531 | -0.00084406 | 0.021322 | 0.025784 | 0.017782 | -2.6178 | 0.10214 | -2.705 | 118.8659 | 118.7365 | 118.5996 | -2.6593 | 0.019362 | 0.06904 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.11378 | 0.041498 | 0.062465 | 0.083016 | -0.004211 | -0.045709 | -0.066955 | -0.20384 | 2.587 | -118.8883 | 2.7202 | 2.6353 | 0.048273 | -118.7897 | -118.7453 | 121.5667 | 121.4373 | 121.3004 | 2.8029 | -121.4627 | 2.6159 | 2.7145 | 2.7589 | 2.7698 | -118.9172
1265.1562 | 121.6003 | -2.6001 | 118.9407 | 1.4211e-13 | -0.03576 | 0.0020727 | 0.063645 | -0.0080317 | 0.052897 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.02557 | 0.017996 | -2.4988 | 0.092979 | -2.586 | 118.9803 | 118.8555 | 118.7186 | -2.5357 | 0.023941 | 0.059882 | -0.065509 | -0.084896 | 0.018285 | 0.067272 | -0.11836 | 0.064421 | 0.039596 | 0.10135 | 0.014117 | -0.050304 | -0.085232 | -0.22212 | 2.4817 | -119.0256 | 2.624 | 2.5346 | 0.052852 | -118.9224 | -118.8735 | 121.5804 | 121.4556 | 121.3187 | 2.6931 | -121.4764 | 2.5152 | 2.6184 | 2.6674 | 2.66 | -119.0591
1266.9219 | 121.6782 | -2.449 | 119.014 | 1.4211e-13 | -0.035333 | 0.0018589 | 0.063859 | -0.0078179 | 0.052683 | -0.0099192 | -0.0044395 | -0.0010577 | 0.021108 | 0.025998 | 0.017355 | -2.3522 | 0.097557 | -2.4349 | 119.136 | 119.0066 | 118.8651 | -2.3892 | 0.019362 | 0.064461 | -0.056351 | -0.080318 | 0.018285 | 0.071851 | -0.10462 | 0.059885 | 0.12202 | 0.096792 | 0.014138 | -0.045747 | -0.007369 | -0.14885 | 2.3444 | -119.0943 | 2.4684 | 2.3927 | 0.048273 | -118.9957 | -118.9421 | 121.585 | 121.4556 | 121.3142 | 2.5466 | -121.4031 | 2.3687 | 2.4673 | 2.5209 | 2.5135 | -119.1186
1268.625 | 121.6324 | -2.623 | 118.9041 | 1.4211e-13 | -0.035974 | 0.0016453 | 0.064073 | -0.0080317 | 0.052897 | -0.0099192 | -0.0048667 | -0.0010577 | 0.021108 | 0.025357 | 0.017782 | -2.5354 | 0.097557 | -2.6226 | 118.9574 | 118.828 | 118.6866 | -2.5815 | 0.02852 | 0.06904 | -0.056351 | -0.080318 | 0.018285 | 0.062694 | -0.11378 | 0.04152 | 0.053325 | 0.087607 | 0.000378 | -0.041142 | -0.076084 | -0.21755 | 2.5092 | -118.9844 | 2.6515 | 2.5666 | 0.057431 | -118.8858 | -118.8414 | 121.5804 | 121.451 | 121.3096 | 2.7205 | -121.4856 | 2.5427 | 2.6413 | 2.6857 | 2.692 | -119.0179
1270.3906 | 121.637 | -2.504 | 119.014 | 1.4211e-13 | -0.035547 | 0.0022863 | 0.063859 | -0.0080317 | 0.052683 | -0.02518 | -0.0046531 | -0.0016987 | 0.021536 | 0.025998 | 0.017569 | -2.4163 | 0.097557 | -2.4944 | 119.0811 | 118.9562 | 118.8148 | -2.4533 | 0.023941 | 0.06904 | -0.06093 | -0.094053 | 0.018285 | 0.058115 | -0.1092 | 0.050711 | 0.067078 | 0.087626 | 0.009551 | -0.04116 | -0.057737 | -0.19921 | 2.3948 | -119.108 | 2.5279 | 2.443 | 0.048273 | -118.9957 | -118.9559 | 121.585 | 121.4602 | 121.3187 | 2.6015 | -121.4672 | 2.4099 | 2.5223 | 2.5621 | 2.573 | -119.1232
1272.1562 | 121.6415 | -2.179 | 119.3344 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.063645 | -0.0078179 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021536 | 0.02557 | 0.017782 | -2.1096 | 0.097557 | -2.1922 | 119.4015 | 119.2584 | 119.1307 | -2.151 | 0.019362 | 0.06904 | -0.065509 | -0.075739 | 0.009128 | 0.062694 | -0.11378 | 0.027908 | 0.06713 | 0.069366 | -0.013294 | -0.041202 | -0.075963 | -0.20372 | 2.0652 | -119.4102 | 2.1983 | 2.1134 | 0.048273 | -119.3253 | -119.2717 | 121.5805 | 121.4374 | 121.3096 | 2.2765 | -121.4855 | 2.1032 | 2.1881 | 2.2416 | 2.248 | -119.4482
1273.9219 | 121.5729 | -2.2339 | 119.3802 | 1.4211e-13 | -0.03576 | 0.0020727 | 0.064073 | -0.0076043 | 0.052683 | -0.0022892 | -0.0044395 | -0.0010577 | 0.021108 | 0.02557 | 0.017782 | -2.0821 | 0.10214 | -2.1602 | 119.4336 | 119.2997 | 119.1582 | -2.1144 | 0.033099 | 0.06904 | -0.06093 | -0.080318 | 0.013707 | 0.053537 | -0.1092 | 0.11947 | 0.053403 | 0.15177 | 0.073686 | -0.045786 | -0.080529 | -0.22203 | 2.1247 | -119.4605 | 2.267 | 2.173 | 0.048273 | -119.3665 | -119.3267 | 121.6675 | 121.5335 | 121.392 | 2.336 | -121.4946 | 2.1536 | 2.2476 | 2.2874 | 2.3029 | -119.4894
1275.6094 | 121.6461 | -1.8494 | 119.6732 | 1.4211e-13 | -0.035547 | 0.0020727 | 0.063645 | -0.0080317 | 0.052897 | -0.01755 | -0.0046531 | -0.0012713 | 0.021108 | 0.02557 | 0.017782 | -1.7204 | 0.10214 | -1.7985 | 119.7907 | 119.6614 | 119.5244 | -1.771 | 0.019362 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.062694 | -0.11378 | 0.078369 | 0.11755 | 0.12894 | 0.050848 | -0.027521 | -0.011763 | -0.14871 | 1.7356 | -119.7581 | 1.8687 | 1.7884 | 0.052852 | -119.6595 | -119.6105 | 121.6401 | 121.5108 | 121.3738 | 1.9515 | -121.4442 | 1.7645 | 1.8631 | 1.9121 | 1.9184 | -119.7869
1277.3594 | 121.6782 | -2.0737 | 119.4168 | 1.4211e-13 | -0.035547 | 0.0016453 | 0.063859 | -0.0082453 | 0.052683 | -0.01755 | -0.0046531 | -0.0010577 | 0.021322 | 0.025998 | 0.017996 | -2.0043 | 0.10671 | -2.0824 | 119.5068 | 119.3775 | 119.2452 | -2.0366 | 0.023941 | 0.064461 | -0.056351 | -0.084896 | 0.018285 | 0.062694 | -0.11378 | 0.037095 | 0.090036 | 0.069383 | -0.008701 | -0.045796 | -0.039308 | -0.17166 | 1.9599 | -119.5017 | 2.0976 | 2.0173 | 0.057431 | -119.3985 | -119.3541 | 121.5805 | 121.4512 | 121.3188 | 2.1804 | -121.4534 | 1.9888 | 2.092 | 2.1364 | 2.1381 | -119.5306
1279.125 | 121.6827 | -2.3071 | 119.2062 | 1.4211e-13 | -0.035547 | 0.0020727 | 0.063859 | -0.0078179 | 0.052469 | -0.0022892 | -0.0046531 | -0.0010577 | 0.021322 | 0.02557 | 0.017569 | -2.2195 | 0.10214 | -2.3021 | 119.2962 | 119.1623 | 119.0254 | -2.2609 | 0.019362 | 0.064461 | -0.056351 | -0.084896 | 0.009128 | 0.067272 | -0.11378 | 0.046188 | 0.090002 | 0.087658 | 0.005001 | -0.041187 | -0.043947 | -0.18086 | 2.1933 | -119.2911 | 2.3265 | 2.2508 | 0.057431 | -119.1971 | -119.139 | 121.6034 | 121.4694 | 121.3325 | 2.4093 | -121.4672 | 2.2222 | 2.3163 | 2.3744 | 2.3716 | -119.32
1280.8906 | 121.6049 | -2.1057 | 119.4763 | 1.4211e-13 | -0.035333 | 0.0016453 | 0.064073 | -0.0078179 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.021322 | 0.025998 | 0.017569 | -1.9997 | 0.097557 | -2.0778 | 119.5252 | 119.3912 | 119.2543 | -2.0366 | 0.02852 | 0.06904 | -0.070087 | -0.075739 | 0.013707 | 0.062694 | -0.10462 | 0.069139 | 0.048841 | 0.10601 | 0.027921 | -0.041218 | -0.085081 | -0.22201 | 2.0011 | -119.5521 | 2.1342 | 2.0356 | 0.034537 | -119.4626 | -119.4136 | 121.6309 | 121.4969 | 121.36 | 2.2033 | -121.5129 | 2.03 | 2.1194 | 2.1684 | 2.1748 | -119.5809
1282.5781 | 121.5408 | -1.9684 | 119.632 | 1.4211e-13 | -0.03576 | 0.0016453 | 0.063645 | -0.0078179 | 0.052683 | -0.01755 | -0.0048667 | -0.00084406 | 0.020895 | 0.025784 | 0.017996 | -1.844 | 0.097557 | -1.9359 | 119.6762 | 119.5423 | 119.41 | -1.8946 | 0.019362 | 0.064461 | -0.051772 | -0.080318 | 0.013707 | 0.058115 | -0.1092 | 0.073757 | 0.044288 | 0.12434 | 0.032519 | -0.041238 | -0.089616 | -0.22198 | 1.8592 | -119.7123 | 1.9877 | 1.9166 | 0.057431 | -119.6183 | -119.5738 | 121.6446 | 121.5107 | 121.3784 | 2.0659 | -121.5266 | 1.8881 | 1.9821 | 2.0265 | 2.0328 | -119.7412
1284.3281 | 121.6827 | -1.9043 | 119.6182 | 1.4211e-13 | -0.03576 | 0.0020727 | 0.063859 | -0.0082453 | 0.052469 | -0.0022892 | -0.0048667 | -0.0010577 | 0.021322 | 0.025357 | 0.017782 | -1.8166 | 0.10214 | -1.9038 | 119.6946 | 119.5652 | 119.4329 | -1.8672 | 0.023941 | 0.064461 | -0.056351 | -0.075739 | 0.013707 | 0.067272 | -0.1092 | 0.037143 | 0.076334 | 0.087725 | 0.000479 | -0.036664 | -0.052988 | -0.18535 | 1.7951 | -119.694 | 1.9282 | 1.8479 | 0.052852 | -119.6045 | -119.551 | 121.5989 | 121.4695 | 121.3372 | 2.0064 | -121.4854 | 1.8286 | 1.918 | 1.9716 | 1.9688 | -119.7274
1286.0938 | 121.6965 | -1.7899 | 119.7464 | 1.4211e-13 | -0.035333 | 0.0016453 | 0.063859 | -0.0073907 | 0.052683 | -0.01755 | -0.0044395 | -0.0012713 | 0.021108 | 0.025784 | 0.017782 | -1.7296 | 0.10214 | -1.8123 | 119.7953 | 119.6614 | 119.5336 | -1.7756 | 0.02852 | 0.073618 | -0.06093 | -0.075739 | 0.018285 | 0.062694 | -0.11836 | 0.014281 | 0.048885 | 0.060273 | -0.022396 | -0.036677 | -0.085005 | -0.21279 | 1.6715 | -119.8221 | 1.8184 | 1.7289 | 0.057431 | -119.7281 | -119.6837 | 121.5851 | 121.4513 | 121.3235 | 1.892 | -121.522 | 1.7141 | 1.8081 | 1.8525 | 1.8635 | -119.8648
1287.8438 | 121.7102 | -1.5793 | 119.9432 | 1.4211e-13 | -0.035547 | 0.0022863 | 0.063859 | -0.0076043 | 0.052897 | -0.0099192 | -0.0050803 | -0.0014849 | 0.021108 | 0.02557 | 0.017569 | -1.5144 | 0.092979 | -1.5971 | 120.015 | 119.8766 | 119.7396 | -1.5649 | 0.033099 | 0.064461 | -0.065509 | -0.080318 | 0.013707 | 0.067272 | -0.11378 | 0.01434 | 0.071809 | 0.064886 | -0.017788 | -0.032128 | -0.066634 | -0.20359 | 1.4655 | -120.0236 | 1.6124 | 1.5138 | 0.048273 | -119.9295 | -119.876 | 121.5943 | 121.4559 | 121.3189 | 1.6723 | -121.5082 | 1.499 | 1.593 | 1.6466 | 1.6437 | -120.057
1289.5312 | 121.6965 | -1.3779 | 120.1813 | 1.4211e-13 | -0.03576 | 0.0018589 | 0.064073 | -0.0080317 | 0.05311 | -0.0099192 | -0.0044395 | -0.0012713 | 0.021322 | 0.025357 | 0.017569 | -1.2809 | 0.10214 | -1.3636 | 120.244 | 120.1147 | 119.9777 | -1.3268 | 0.02852 | 0.064461 | -0.056351 | -0.080318 | 0.013707 | 0.062694 | -0.1092 | 0.051029 | 0.062692 | 0.096968 | 0.014289 | -0.03674 | -0.066566 | -0.20354 | 1.2687 | -120.2616 | 1.4064 | 1.3215 | 0.052852 | -120.1676 | -120.1186 | 121.6218 | 121.4926 | 121.3556 | 1.48 | -121.5081 | 1.2976 | 1.3916 | 1.4406 | 1.4423 | -120.2905
1291.2812 | 121.669 | -1.4145 | 120.1721 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.064286 | -0.0078179 | 0.052683 | -0.01755 | -0.0042257 | -0.00084406 | 0.021322 | 0.026211 | 0.017782 | -1.3175 | 0.10214 | -1.3956 | 120.2211 | 120.0918 | 119.9594 | -1.3543 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.018285 | 0.058115 | -0.11378 | 0.060176 | 0.048955 | 0.096962 | 0.018862 | -0.041314 | -0.080306 | -0.2127 | 1.3007 | -120.2524 | 1.4384 | 1.3581 | 0.057431 | -120.1538 | -120.114 | 121.6356 | 121.5063 | 121.3739 | 1.5166 | -121.5264 | 1.3342 | 1.4328 | 1.4726 | 1.4881 | -120.2859
1293.0312 | 121.6415 | -1.3962 | 120.1447 | 1.4211e-13 | -0.03576 | 0.0020727 | 0.063859 | -0.0078179 | 0.052469 | -0.01755 | -0.0048667 | -0.0012713 | 0.021108 | 0.02557 | 0.017996 | -1.313 | 0.10214 | -1.3819 | 120.2348 | 120.101 | 119.964 | -1.3497 | 0.019362 | 0.064461 | -0.056351 | -0.084896 | 0.018285 | 0.062694 | -0.11378 | 0.046444 | 0.090156 | 0.083229 | 0.014285 | -0.032159 | -0.043682 | -0.18066 | 1.2824 | -120.2295 | 1.4155 | 1.3398 | 0.057431 | -120.1264 | -120.082 | 121.631 | 121.4972 | 121.3602 | 1.4983 | -121.4944 | 1.3113 | 1.4145 | 1.4589 | 1.4606 | -120.2584
1294.7188 | 121.701 | -1.4923 | 120.0485 | 1.4211e-13 | -0.035547 | 0.0016453 | 0.064286 | -0.0078179 | 0.052683 | -0.01755 | -0.0044395 | -0.0010577 | 0.021108 | 0.025784 | 0.017569 | -1.432 | 0.10214 | -1.4964 | 120.1158 | 119.9819 | 119.8495 | -1.4642 | 0.023941 | 0.064461 | -0.06093 | -0.075739 | 0.013707 | 0.053537 | -0.11378 | 0.028102 | 0.067248 | 0.060322 | -0.004041 | -0.032143 | -0.066604 | -0.19899 | 1.3785 | -120.1243 | 1.5163 | 1.4314 | 0.052852 | -120.0348 | -119.995 | 121.6081 | 121.4742 | 121.3418 | 1.5944 | -121.5127 | 1.4166 | 1.506 | 1.5458 | 1.5568 | -120.1623
1296.4844 | 121.6507 | -1.4557 | 120.1263 | 1.4211e-13 | -0.03576 | 0.0022863 | 0.063859 | -0.0078179 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.026211 | 0.017782 | -1.3404 | 0.10214 | -1.4139 | 120.2073 | 120.0735 | 119.9411 | -1.3864 | 0.02852 | 0.073618 | -0.06093 | -0.071161 | 0.009128 | 0.067272 | -0.11378 | 0.069322 | 0.080996 | 0.11527 | 0.041746 | -0.027576 | -0.052846 | -0.18524 | 1.3419 | -120.1975 | 1.4842 | 1.3948 | 0.052852 | -120.1172 | -120.0591 | 121.663 | 121.5292 | 121.3968 | 1.5578 | -121.5127 | 1.3845 | 1.4648 | 1.523 | 1.5293 | -120.2401
1298.25 | 121.5866 | -1.4328 | 120.1904 | 1.4211e-13 | -0.035547 | 0.0020727 | 0.064073 | -0.0078179 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.021108 | 0.025998 | 0.017355 | -1.2855 | 0.097557 | -1.3773 | 120.2485 | 120.1239 | 119.9869 | -1.3406 | 0.023941 | 0.06904 | -0.056351 | -0.066582 | 0.009128 | 0.062694 | -0.11378 | 0.092223 | 0.058114 | 0.14732 | 0.055485 | -0.036738 | -0.066565 | -0.20354 | 1.319 | -120.257 | 1.4567 | 1.3764 | 0.057431 | -120.1813 | -120.1277 | 121.6813 | 121.5567 | 121.4197 | 1.5304 | -121.531 | 1.3662 | 1.4419 | 1.4955 | 1.5018 | -120.3042
1300.0156 | 121.701 | -1.3321 | 120.2042 | 1.4211e-13 | -0.03576 | 0.0018589 | 0.063645 | -0.0078179 | 0.052469 | -0.0022892 | -0.0044395 | -0.0010577 | 0.021108 | 0.025998 | 0.017782 | -1.2351 | 0.10214 | -1.3086 | 120.3081 | 120.1788 | 120.0464 | -1.2719 | 0.019362 | 0.064461 | -0.06093 | -0.071161 | 0.013707 | 0.062694 | -0.11378 | 0.060199 | 0.1039 | 0.096975 | 0.023451 | -0.036748 | -0.025351 | -0.15775 | 1.2183 | -120.2753 | 1.3515 | 1.2712 | 0.052852 | -120.1905 | -120.1415 | 121.6402 | 121.5109 | 121.3785 | 1.4342 | -121.4761 | 1.2609 | 1.3458 | 1.3948 | 1.3966 | -120.3179
1301.7188 | 121.7194 | -1.2955 | 120.282 | 1.4211e-13 | -0.035974 | 0.0020727 | 0.064073 | -0.0076043 | 0.052897 | -0.0022892 | -0.0048667 | -0.0010577 | 0.021322 | 0.02557 | 0.017355 | -1.1939 | 0.10214 | -1.272 | 120.3584 | 120.2292 | 120.0922 | -1.2353 | 0.02852 | 0.073618 | -0.065509 | -0.071161 | 0.013707 | 0.062694 | -0.11378 | 0.060209 | 0.076444 | 0.10156 | 0.023456 | -0.036753 | -0.052801 | -0.18979 | 1.1817 | -120.3531 | 1.324 | 1.23 | 0.048273 | -120.2683 | -120.2193 | 121.6539 | 121.5247 | 121.3877 | 1.3976 | -121.5172 | 1.2243 | 1.3092 | 1.3582 | 1.3691 | -120.3958
1303.4688 | 121.7331 | -1.2405 | 120.3049 | 1.4211e-13 | -0.035974 | 0.0020727 | 0.064073 | -0.0080317 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.026211 | 0.017569 | -1.1573 | 0.097557 | -1.2354 | 120.4042 | 120.2704 | 120.1334 | -1.1986 | 0.014784 | 0.06904 | -0.065509 | -0.066582 | 0.013707 | 0.058115 | -0.1092 | 0.041909 | 0.099338 | 0.083255 | 0.005151 | -0.036758 | -0.03448 | -0.17147 | 1.1313 | -120.3715 | 1.2553 | 1.175 | 0.043694 | -120.2912 | -120.2468 | 121.6447 | 121.5109 | 121.3739 | 1.3381 | -121.5035 | 1.174 | 1.2542 | 1.2987 | 1.3096 | -120.4141
1305.2344 | 121.6003 | -1.2909 | 120.3461 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.063859 | -0.0080317 | 0.052683 | -0.0022892 | -0.0048667 | -0.0012713 | 0.021108 | 0.025998 | 0.017782 | -1.1664 | 0.10214 | -1.2354 | 120.3951 | 120.2658 | 120.1288 | -1.2078 | 0.023941 | 0.06904 | -0.06093 | -0.071161 | 0.004549 | 0.058115 | -0.1092 | 0.083106 | 0.048984 | 0.12445 | 0.055505 | -0.027601 | -0.080257 | -0.21725 | 1.1817 | -120.4172 | 1.3148 | 1.23 | 0.048273 | -120.3415 | -120.288 | 121.6859 | 121.5567 | 121.4197 | 1.393 | -121.5539 | 1.2197 | 1.2954 | 1.349 | 1.3599 | -120.4553
1307 | 121.6919 | -1.3138 | 120.2866 | 1.4211e-13 | -0.035974 | 0.0022863 | 0.064073 | -0.0078179 | 0.052897 | -0.0022892 | -0.0046531 | -0.0010577 | 0.021322 | 0.02557 | 0.017782 | -1.2168 | 0.10214 | -1.2995 | 120.3401 | 120.2063 | 120.0785 | -1.2673 | 0.019362 | 0.06904 | -0.06093 | -0.071161 | 0.022864 | 0.062694 | -0.1092 | 0.046468 | 0.053552 | 0.096978 | 0.014298 | -0.03217 | -0.080274 | -0.2081 | 1.2046 | -120.3577 | 1.3331 | 1.2529 | 0.048273 | -120.2637 | -120.2239 | 121.6539 | 121.5201 | 121.3922 | 1.4159 | -121.5539 | 1.2426 | 1.3366 | 1.3765 | 1.3828 | -120.3958
1308.6875 | 121.7331 | -1.268 | 120.3094 | 1.4211e-13 | -0.035974 | 0.0020727 | 0.063859 | -0.0078179 | 0.052683 | -0.0022892 | -0.0048667 | -0.0012713 | 0.021536 | 0.025784 | 0.017569 | -1.1756 | 0.097557 | -1.2537 | 120.3859 | 120.2567 | 120.1197 | -1.2215 | 0.023941 | 0.06904 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.10462 | 0.04648 | 0.076448 | 0.092407 | 0.014303 | -0.032177 | -0.052794 | -0.18978 | 1.1634 | -120.3898 | 1.2919 | 1.2025 | 0.039115 | -120.2957 | -120.2513 | 121.6539 | 121.5247 | 121.3877 | 1.3656 | -121.531 | 1.1877 | 1.2817 | 1.3261 | 1.337 | -120.4141
1310.4375 | 121.7102 | -1.2039 | 120.369 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.064073 | -0.0080317 | 0.052897 | -0.0099192 | -0.0044395 | -0.0010577 | 0.021322 | 0.02557 | 0.017355 | -1.1115 | 0.10214 | -1.1942 | 120.4454 | 120.3253 | 120.1838 | -1.1574 | 0.02852 | 0.06904 | -0.056351 | -0.062004 | 0.018285 | 0.053537 | -0.1092 | 0.046498 | 0.076457 | 0.092417 | 0.009734 | -0.036764 | -0.04362 | -0.18519 | 1.0947 | -120.431 | 1.2324 | 1.1476 | 0.052852 | -120.3507 | -120.3154 | 121.6493 | 121.5293 | 121.3877 | 1.3061 | -121.5264 | 1.1419 | 1.2222 | 1.2575 | 1.273 | -120.4782
1312.2031 | 121.6919 | -1.1902 | 120.3873 | 1.4211e-13 | -0.03576 | 0.0020727 | 0.064073 | -0.0080317 | 0.052683 | -0.01755 | -0.0048667 | -0.00084406 | 0.021322 | 0.025998 | 0.017569 | -1.084 | 0.10214 | -1.1621 | 120.4866 | 120.3482 | 120.225 | -1.1254 | 0.023941 | 0.06904 | -0.065509 | -0.075739 | 0.009128 | 0.058115 | -0.11378 | 0.064818 | 0.099352 | 0.10616 | 0.02805 | -0.036768 | -0.039035 | -0.16229 | 1.0764 | -120.463 | 1.2141 | 1.1247 | 0.048273 | -120.3781 | -120.3292 | 121.6768 | 121.5384 | 121.4152 | 1.2923 | -121.5126 | 1.1144 | 1.1993 | 1.2483 | 1.2592 | -120.5011
1313.9688 | 121.5958 | -1.2177 | 120.4514 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.063645 | -0.0078179 | 0.052683 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.025784 | 0.017569 | -1.0932 | 0.097557 | -1.1713 | 120.4912 | 120.3528 | 120.2204 | -1.1391 | 0.023941 | 0.064461 | -0.065509 | -0.075739 | 0.013707 | 0.067272 | -0.1092 | 0.078546 | 0.039844 | 0.12446 | 0.046358 | -0.032188 | -0.098543 | -0.23096 | 1.1084 | -120.5271 | 1.2416 | 1.1521 | 0.043694 | -120.4376 | -120.3841 | 121.7088 | 121.5705 | 121.438 | 1.3152 | -121.5905 | 1.1419 | 1.2314 | 1.2849 | 1.2821 | -120.5606
1315.6562 | 121.5912 | -1.1719 | 120.5246 | 1.4211e-13 | -0.03576 | 0.0018589 | 0.064073 | -0.0076043 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021108 | 0.025784 | 0.017569 | -1.0382 | 0.10214 | -1.1209 | 120.5278 | 120.4032 | 120.2662 | -1.0842 | 0.023941 | 0.06904 | -0.070087 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.087718 | 0.003229 | 0.13363 | 0.050943 | -0.036775 | -0.12142 | -0.25841 | 1.0627 | -120.6003 | 1.1958 | 1.1018 | 0.039116 | -120.5109 | -120.4665 | 121.6997 | 121.5751 | 121.4381 | 1.274 | -121.6088 | 1.0961 | 1.1856 | 1.23 | 1.2409 | -120.6338
1317.4219 | 121.7331 | -1.0712 | 120.52 | 1.4211e-13 | -0.035974 | 0.0020727 | 0.063859 | -0.0080317 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.026211 | 0.017569 | -0.99246 | 0.10671 | -1.066 | 120.5873 | 120.4627 | 120.3211 | -1.0338 | 0.023941 | 0.064461 | -0.065509 | -0.071161 | 0.018285 | 0.062694 | -0.1092 | 0.037378 | 0.067325 | 0.078704 | 0.005175 | -0.032203 | -0.057314 | -0.1989 | 0.96196 | -120.5912 | 1.0951 | 1.0057 | 0.043694 | -120.5017 | -120.4573 | 121.6585 | 121.5339 | 121.3923 | 1.1779 | -121.5538 | 1 | 1.0895 | 1.1339 | 1.1356 | -120.6292
1319.1719 | 121.6461 | -1.1032 | 120.575 | 1.4211e-13 | -0.03576 | 0.0016453 | 0.063859 | -0.0078179 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020895 | 0.025784 | 0.017569 | -0.96041 | 0.10214 | -1.0294 | 120.6148 | 120.4948 | 120.3578 | -1.0017 | 0.019362 | 0.06904 | -0.065509 | -0.071161 | 0.009128 | 0.058115 | -0.10004 | 0.10147 | 0.039864 | 0.1428 | 0.073844 | -0.027629 | -0.080193 | -0.2172 | 1.0032 | -120.6461 | 1.1226 | 1.0377 | 0.034536 | -120.5658 | -120.5168 | 121.718 | 121.598 | 121.461 | 1.2053 | -121.5767 | 1.032 | 1.1123 | 1.1613 | 1.1723 | -120.675
1320.9375 | 121.6278 | -1.0483 | 120.5704 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.063859 | -0.0078179 | 0.052683 | -0.01755 | -0.0048667 | -0.0012713 | 0.021536 | 0.025784 | 0.017782 | -0.9421 | 0.097557 | -1.0156 | 120.6377 | 120.5085 | 120.3761 | -0.98342 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.009128 | 0.067272 | -0.10462 | 0.064858 | 0.067333 | 0.10618 | 0.032648 | -0.03221 | -0.061879 | -0.19431 | 0.94365 | -120.6507 | 1.0722 | 0.98735 | 0.043694 | -120.5612 | -120.5031 | 121.686 | 121.5568 | 121.4243 | 1.1458 | -121.5538 | 0.96796 | 1.0574 | 1.1156 | 1.1173 | -120.675
1322.6406 | 121.6415 | -1.0941 | 120.5978 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.063859 | -0.0080317 | 0.052683 | -0.0022892 | -0.0048667 | -0.0014849 | 0.020895 | 0.025784 | 0.017569 | -0.95584 | 0.10214 | -1.0294 | 120.624 | 120.5039 | 120.3669 | -0.99716 | 0.019362 | 0.06904 | -0.056351 | -0.075739 | 0.004549 | 0.062694 | -0.11378 | 0.096897 | 0.026133 | 0.13822 | 0.064689 | -0.032208 | -0.093923 | -0.23093 | 0.98027 | -120.6736 | 1.1134 | 1.0377 | 0.057431 | -120.5933 | -120.5351 | 121.718 | 121.598 | 121.461 | 1.1962 | -121.595 | 1.0183 | 1.0986 | 1.1567 | 1.1631 | -120.7116
1324.4062 | 121.6141 | -1.0895 | 120.6116 | 1.4211e-13 | -0.035974 | 0.0020727 | 0.063859 | -0.0080317 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.02557 | 0.017569 | -0.92836 | 0.10214 | -1.0019 | 120.6606 | 120.5405 | 120.4081 | -0.96968 | 0.019362 | 0.06904 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.1092 | 0.11979 | 0.049027 | 0.16111 | 0.087582 | -0.032212 | -0.071024 | -0.20345 | 0.98028 | -120.6873 | 1.1088 | 1.0285 | 0.048273 | -120.6024 | -120.5535 | 121.7501 | 121.63 | 121.4976 | 1.1916 | -121.5813 | 1.0137 | 1.0986 | 1.1476 | 1.1585 | -120.7208
1326.1719 | 121.7743 | -1.0162 | 120.5566 | 1.4211e-13 | -0.035974 | 0.0016453 | 0.0645 | -0.0080317 | 0.052683 | -0.0099192 | -0.0048667 | -0.0014849 | 0.021536 | 0.025998 | 0.017782 | -0.93294 | 0.10214 | -1.0111 | 120.6606 | 120.5314 | 120.3898 | -0.97426 | 0.023941 | 0.073618 | -0.056351 | -0.071161 | 0.013707 | 0.062694 | -0.1092 | 0.041972 | 0.10396 | 0.083291 | 0.005182 | -0.03679 | -0.025251 | -0.16684 | 0.90703 | -120.6278 | 1.0402 | 0.95988 | 0.052852 | -120.5429 | -120.4939 | 121.6768 | 121.5476 | 121.406 | 1.1184 | -121.5309 | 0.94507 | 1.0299 | 1.0789 | 1.0899 | -120.6658
1327.9219 | 121.6095 | -1.0803 | 120.6162 | 1.4211e-13 | -0.035974 | 0.0025001 | 0.064073 | -0.0080317 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.021322 | 0.02557 | 0.017996 | -0.93294 | 0.092979 | -1.0019 | 120.656 | 120.5314 | 120.399 | -0.96968 | 0.02852 | 0.06904 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.11064 | 0.039871 | 0.14738 | 0.078426 | -0.032212 | -0.08476 | -0.21719 | 0.97112 | -120.6919 | 1.1088 | 1.024 | 0.052852 | -120.6024 | -120.558 | 121.7363 | 121.6117 | 121.4793 | 1.1733 | -121.5858 | 1.0046 | 1.094 | 1.1384 | 1.1494 | -120.7254
1329.6094 | 121.6324 | -1.062 | 120.6253 | 1.4211e-13 | -0.03576 | 0.0016453 | 0.064286 | -0.0078179 | 0.052897 | -0.01755 | -0.0048667 | -0.0012713 | 0.020895 | 0.025998 | 0.017782 | -0.93294 | 0.10214 | -1.0065 | 120.656 | 120.536 | 120.4035 | -0.97426 | 0.02852 | 0.064461 | -0.056351 | -0.075739 | 0.009128 | 0.058115 | -0.1092 | 0.087749 | 0.030716 | 0.12907 | 0.055537 | -0.032212 | -0.089336 | -0.22176 | 0.95281 | -120.701 | 1.0905 | 1.0057 | 0.052852 | -120.6162 | -120.5672 | 121.718 | 121.598 | 121.4656 | 1.1641 | -121.5996 | 0.98627 | 1.0711 | 1.1201 | 1.1265 | -120.7345
1331.375 | 121.7194 | -1.0254 | 120.575 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.064073 | -0.0076043 | 0.052683 | -0.01755 | -0.0044395 | -0.0014849 | 0.021108 | 0.025998 | 0.017569 | -0.92836 | 0.10671 | -1.0065 | 120.6698 | 120.536 | 120.4035 | -0.96968 | 0.023941 | 0.064461 | -0.06093 | -0.075739 | 0.018285 | 0.058115 | -0.11378 | 0.055707 | 0.094805 | 0.097026 | 0.018916 | -0.036791 | -0.038982 | -0.17141 | 0.91161 | -120.6507 | 1.0493 | 0.96446 | 0.052852 | -120.5567 | -120.5168 | 121.6951 | 121.5614 | 121.4289 | 1.1321 | -121.5446 | 0.94965 | 1.0437 | 1.0835 | 1.0899 | -120.6887
1333.1406 | 121.7148 | -1.062 | 120.5338 | 1.4211e-13 | -0.03576 | 0.0022863 | 0.063859 | -0.0082453 | 0.052469 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021322 | 0.025998 | 0.017569 | -0.96957 | 0.097557 | -1.0477 | 120.6286 | 120.4902 | 120.3669 | -1.0109 | 0.02852 | 0.073618 | -0.06093 | -0.071161 | 0.018285 | 0.058115 | -0.10462 | 0.051117 | 0.094798 | 0.092441 | 0.014333 | -0.036784 | -0.043573 | -0.16684 | 0.95739 | -120.6049 | 1.0905 | 1.0011 | 0.043694 | -120.5155 | -120.4756 | 121.6906 | 121.5522 | 121.4289 | 1.1596 | -121.5446 | 0.99085 | 1.0803 | 1.1201 | 1.1356 | -120.6384
1334.9062 | 121.7468 | -1.1627 | 120.4834 | 1.4211e-13 | -0.036188 | 0.0018589 | 0.064073 | -0.0080317 | 0.052683 | -0.0099192 | -0.0042257 | -0.0012713 | 0.021322 | 0.026211 | 0.017996 | -1.052 | 0.092979 | -1.1255 | 120.5461 | 120.4215 | 120.2891 | -1.0933 | 0.019362 | 0.064461 | -0.065509 | -0.066582 | 0.018285 | 0.058115 | -0.11378 | 0.069405 | 0.062741 | 0.11074 | 0.03721 | -0.032195 | -0.061903 | -0.19432 | 1.0489 | -120.55 | 1.1821 | 1.0972 | 0.048273 | -120.4651 | -120.4253 | 121.7089 | 121.5842 | 121.4518 | 1.2557 | -121.5767 | 1.0961 | 1.181 | 1.2208 | 1.2272 | -120.5972
1336.6719 | 121.6782 | -1.2726 | 120.4102 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.064286 | -0.0082453 | 0.052683 | -0.0022892 | -0.0048667 | -0.0010577 | 0.021108 | 0.025998 | 0.017569 | -1.1344 | 0.092979 | -1.2079 | 120.4775 | 120.3391 | 120.2067 | -1.1757 | 0.023941 | 0.064461 | -0.056351 | -0.071161 | 0.009128 | 0.053537 | -0.10004 | 0.096847 | 0.067308 | 0.13819 | 0.064664 | -0.032183 | -0.071081 | -0.2035 | 1.1725 | -120.4813 | 1.2965 | 1.2162 | 0.043694 | -120.401 | -120.3566 | 121.75 | 121.6117 | 121.4792 | 1.3656 | -121.5859 | 1.2014 | 1.2817 | 1.3261 | 1.337 | -120.5102
1338.3594 | 121.6095 | -1.3504 | 120.3415 | 1.4211e-13 | -0.036188 | 0.0022863 | 0.063859 | -0.0080317 | 0.052897 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021322 | 0.025784 | 0.017569 | -1.1848 | 0.10214 | -1.2674 | 120.4088 | 120.2795 | 120.1655 | -1.2307 | 0.02852 | 0.064461 | -0.06093 | -0.075739 | 0.013707 | 0.062694 | -0.10462 | 0.11972 | 0.067296 | 0.16565 | 0.082966 | -0.036754 | -0.061943 | -0.17604 | 1.2458 | -120.4172 | 1.3789 | 1.2895 | 0.043694 | -120.3278 | -120.2788 | 121.7592 | 121.63 | 121.5159 | 1.4525 | -121.5722 | 1.2747 | 1.3641 | 1.4131 | 1.4149 | -120.4461
1340.1094 | 121.6187 | -1.3687 | 120.3415 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.064286 | -0.0080317 | 0.052256 | -0.0022892 | -0.0048667 | -0.0012713 | 0.020895 | 0.025998 | 0.017355 | -1.2214 | 0.097557 | -1.2995 | 120.3813 | 120.2567 | 120.1151 | -1.2582 | 0.014784 | 0.064461 | -0.06093 | -0.080318 | 0.004549 | 0.062694 | -0.11378 | 0.11056 | 0.039825 | 0.14733 | 0.069229 | -0.041327 | -0.084838 | -0.2264 | 1.2549 | -120.4218 | 1.3835 | 1.3078 | 0.052852 | -120.3369 | -120.2788 | 121.75 | 121.6254 | 121.4838 | 1.4663 | -121.5996 | 1.2884 | 1.3733 | 1.4314 | 1.4332 | -120.4553
1341.875 | 121.7697 | -1.3321 | 120.2866 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.063859 | -0.0078179 | 0.052469 | 0.0053413 | -0.0046531 | -0.0012713 | 0.021322 | 0.025998 | 0.017569 | -1.226 | 0.10671 | -1.2903 | 120.3722 | 120.2521 | 120.1197 | -1.2673 | 0.023941 | 0.06904 | -0.065509 | -0.071161 | 0.018285 | 0.062694 | -0.11378 | 0.064778 | 0.085601 | 0.10613 | 0.041764 | -0.023014 | -0.034485 | -0.16689 | 1.2183 | -120.3577 | 1.356 | 1.2666 | 0.048273 | -120.2683 | -120.2239 | 121.7043 | 121.5842 | 121.4518 | 1.4388 | -121.5539 | 1.2609 | 1.3504 | 1.3948 | 1.4011 | -120.4003
1343.5938 | 121.7194 | -1.442 | 120.2271 | 1.4211e-13 | -0.035974 | 0.0020727 | 0.063859 | -0.0078179 | 0.052469 | -0.01755 | -0.0044395 | -0.0014849 | 0.021108 | 0.025998 | 0.017782 | -1.3404 | 0.10671 | -1.4048 | 120.2669 | 120.1513 | 120.0098 | -1.3772 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.009128 | 0.053537 | -0.10462 | 0.064747 | 0.039807 | 0.10154 | 0.037171 | -0.027576 | -0.075712 | -0.21727 | 1.3373 | -120.3074 | 1.4659 | 1.381 | 0.043694 | -120.2179 | -120.1735 | 121.7088 | 121.5933 | 121.4517 | 1.5487 | -121.6043 | 1.3616 | 1.4511 | 1.4955 | 1.5202 | -120.3317
1345.3281 | 121.7743 | -1.5106 | 120.1309 | 1.4211e-13 | -0.036188 | 0.0018589 | 0.064073 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0010577 | 0.021108 | 0.025998 | 0.017782 | -1.4228 | 0.10214 | -1.5009 | 120.1844 | 120.0552 | 119.9136 | -1.4688 | 0.02852 | 0.06904 | -0.065509 | -0.066582 | 0.013707 | 0.062694 | -0.10462 | 0.041833 | 0.053527 | 0.087789 | 0.009691 | -0.032142 | -0.075738 | -0.21729 | 1.406 | -120.1975 | 1.5391 | 1.4451 | 0.039115 | -120.1172 | -120.0682 | 121.6951 | 121.5658 | 121.4242 | 1.6128 | -121.5997 | 1.444 | 1.5243 | 1.5733 | 1.5797 | -120.2355
1347.0938 | 121.7285 | -1.6205 | 120.0027 | 1.4211e-13 | -0.036188 | 0.0025001 | 0.063859 | -0.0082453 | 0.052469 | -0.0099192 | -0.0046531 | -0.0014849 | 0.021322 | 0.026211 | 0.017782 | -1.5098 | 0.10671 | -1.5879 | 120.0975 | 119.9682 | 119.8495 | -1.542 | 0.019362 | 0.06904 | -0.06093 | -0.071161 | 0.009128 | 0.062694 | -0.1092 | 0.078433 | 0.09471 | 0.11066 | 0.032567 | -0.045866 | -0.034565 | -0.15322 | 1.5113 | -120.0739 | 1.6398 | 1.5596 | 0.048273 | -119.9936 | -119.9401 | 121.7179 | 121.5887 | 121.47 | 1.7272 | -121.5448 | 1.5493 | 1.6296 | 1.6832 | 1.6895 | -120.1119
1348.8594 | 121.6461 | -1.7166 | 119.9661 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.063859 | -0.0080317 | 0.052683 | -0.0022892 | -0.0050803 | -0.0012713 | 0.021322 | 0.025998 | 0.017355 | -1.5877 | 0.10671 | -1.6657 | 120.0242 | 119.8903 | 119.7625 | -1.6336 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.009128 | 0.058115 | -0.10462 | 0.082986 | 0.058078 | 0.12896 | 0.050867 | -0.032119 | -0.075785 | -0.20359 | 1.612 | -120.0464 | 1.7406 | 1.6557 | 0.043694 | -119.957 | -119.908 | 121.7408 | 121.607 | 121.4791 | 1.8233 | -121.5998 | 1.6363 | 1.7257 | 1.7747 | 1.7857 | -120.0707
1350.5469 | 121.7056 | -1.6708 | 119.9661 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.063645 | -0.0082453 | 0.052256 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021108 | 0.025998 | 0.017996 | -1.5602 | 0.10671 | -1.6291 | 120.0563 | 119.927 | 119.8037 | -1.597 | 0.023941 | 0.064461 | -0.065509 | -0.071161 | 0.009128 | 0.058115 | -0.1092 | 0.07384 | 0.090127 | 0.11065 | 0.041716 | -0.032124 | -0.039153 | -0.16238 | 1.5616 | -120.0373 | 1.6948 | 1.6053 | 0.043694 | -119.957 | -119.908 | 121.7271 | 121.5978 | 121.4746 | 1.7776 | -121.5631 | 1.5997 | 1.68 | 1.729 | 1.7353 | -120.0753
1352.3125 | 121.788 | -1.6205 | 120.0165 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.063859 | -0.0080317 | 0.052469 | -0.01755 | -0.0046531 | -0.0014849 | 0.021108 | 0.025784 | 0.017782 | -1.5327 | 0.097557 | -1.6108 | 120.0791 | 119.9544 | 119.8358 | -1.5741 | 0.02852 | 0.064461 | -0.065509 | -0.075739 | 0.009128 | 0.062694 | -0.1092 | 0.046381 | 0.062665 | 0.087771 | 0.009675 | -0.036706 | -0.062034 | -0.18069 | 1.5113 | -120.0922 | 1.649 | 1.555 | 0.043694 | -120.0074 | -119.9538 | 121.6996 | 121.5749 | 121.4563 | 1.718 | -121.5906 | 1.5447 | 1.6296 | 1.6832 | 1.6849 | -120.1257
1354.0156 | 121.6919 | -1.6022 | 120.0806 | 1.4211e-13 | -0.03576 | 0.0022863 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.021108 | 0.026211 | 0.017569 | -1.4915 | 0.10671 | -1.5696 | 120.1249 | 120.0002 | 119.8678 | -1.5329 | 0.019362 | 0.073618 | -0.056351 | -0.066582 | 0.022864 | 0.062694 | -0.1092 | 0.069281 | 0.044362 | 0.11067 | 0.03257 | -0.036711 | -0.080332 | -0.21272 | 1.493 | -120.1471 | 1.6215 | 1.5458 | 0.052852 | -120.0577 | -120.0179 | 121.7271 | 121.6024 | 121.47 | 1.7089 | -121.6135 | 1.5356 | 1.625 | 1.6649 | 1.6758 | -120.1898
1355.7812 | 121.7926 | -1.5472 | 120.0806 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.063859 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020895 | 0.026425 | 0.017782 | -1.4686 | 0.097557 | -1.5513 | 120.1478 | 120.0277 | 119.8862 | -1.5192 | 0.033099 | 0.073618 | -0.056351 | -0.071161 | 0.013707 | 0.058115 | -0.10462 | 0.028086 | 0.067254 | 0.078626 | -0.004049 | -0.032135 | -0.052858 | -0.19441 | 1.4426 | -120.1517 | 1.5803 | 1.4909 | 0.048273 | -120.0669 | -120.0225 | 121.6951 | 121.5749 | 121.4334 | 1.6448 | -121.5997 | 1.4761 | 1.5609 | 1.6054 | 1.6209 | -120.1852
1357.5469 | 121.788 | -1.5289 | 120.1172 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.063859 | -0.0082453 | 0.052683 | -0.0099192 | -0.0046531 | -0.0010577 | 0.021536 | 0.025998 | 0.017355 | -1.4503 | 0.10214 | -1.5147 | 120.1799 | 120.0552 | 119.9274 | -1.4734 | 0.02852 | 0.064461 | -0.06093 | -0.075739 | 0.013707 | 0.062694 | -0.10004 | 0.055565 | 0.062681 | 0.07863 | 0.014267 | -0.041298 | -0.062005 | -0.18982 | 1.4289 | -120.1929 | 1.5575 | 1.468 | 0.039115 | -120.1035 | -120.0545 | 121.7088 | 121.5841 | 121.4563 | 1.6311 | -121.5906 | 1.4532 | 1.5426 | 1.5916 | 1.5934 | -120.2172
1359.3281 | 121.7651 | -1.5152 | 120.1172 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.064073 | -0.0080317 | 0.052256 | -0.01755 | -0.0044395 | -0.0010577 | 0.020895 | 0.025998 | 0.017569 | -1.4183 | 0.11129 | -1.4918 | 120.2028 | 120.0735 | 119.9548 | -1.455 | 0.019362 | 0.06904 | -0.06093 | -0.071161 | 0.013707 | 0.053537 | -0.1092 | 0.060148 | 0.085573 | 0.096945 | 0.023426 | -0.036722 | -0.04369 | -0.16235 | 1.406 | -120.1883 | 1.5346 | 1.4543 | 0.048273 | -120.1035 | -120.0636 | 121.718 | 121.5887 | 121.47 | 1.6265 | -121.5722 | 1.444 | 1.5289 | 1.5687 | 1.5842 | -120.2264
1361.0938 | 121.7422 | -1.506 | 120.1218 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.064073 | -0.0080317 | 0.052469 | -0.01755 | -0.0046531 | -0.0014849 | 0.021108 | 0.026211 | 0.017569 | -1.4091 | 0.10214 | -1.478 | 120.2211 | 120.0964 | 119.9686 | -1.4459 | 0.02852 | 0.06904 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.10462 | 0.06015 | 0.099309 | 0.096946 | 0.028005 | -0.032145 | -0.025373 | -0.15319 | 1.4014 | -120.1975 | 1.5346 | 1.4451 | 0.043694 | -120.1081 | -120.0636 | 121.7271 | 121.6024 | 121.4746 | 1.6082 | -121.5677 | 1.4303 | 1.5197 | 1.5642 | 1.5751 | -120.2264
1362.8594 | 121.6187 | -1.4923 | 120.2133 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.064286 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.021108 | 0.025998 | 0.017355 | -1.3633 | 0.10671 | -1.446 | 120.2623 | 120.1376 | 120.0052 | -1.4138 | 0.019362 | 0.064461 | -0.06093 | -0.075739 | 0.013707 | 0.053537 | -0.1092 | 0.07847 | 0.048961 | 0.129 | 0.046321 | -0.032149 | -0.075716 | -0.20812 | 1.3831 | -120.2891 | 1.5117 | 1.4314 | 0.048273 | -120.1996 | -120.1598 | 121.7546 | 121.6299 | 121.4975 | 1.599 | -121.6272 | 1.4166 | 1.506 | 1.5458 | 1.5568 | -120.3225
1364.5469 | 121.7926 | -1.4603 | 120.1721 | 1.4211e-13 | -0.036401 | 0.0022863 | 0.063859 | -0.0082453 | 0.052256 | -0.0022892 | -0.0046531 | -0.0010577 | 0.020681 | 0.026211 | 0.017355 | -1.3679 | 0.10671 | -1.4414 | 120.2531 | 120.1376 | 120.0098 | -1.4047 | 0.023941 | 0.073618 | -0.065509 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.055584 | 0.081004 | 0.092376 | 0.018855 | -0.036729 | -0.034517 | -0.16234 | 1.3602 | -120.2479 | 1.4842 | 1.3948 | 0.034536 | -120.163 | -120.114 | 121.7134 | 121.5979 | 121.47 | 1.567 | -121.5768 | 1.3845 | 1.4694 | 1.5184 | 1.5339 | -120.2722
1366.2969 | 121.701 | -1.474 | 120.2087 | 1.4211e-13 | -0.036615 | 0.0020727 | 0.064073 | -0.0078179 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021322 | 0.025998 | 0.017355 | -1.345 | 0.10671 | -1.4231 | 120.2852 | 120.1605 | 120.0327 | -1.3772 | 0.023941 | 0.064461 | -0.051772 | -0.071161 | 0.009128 | 0.058115 | -0.10004 | 0.09679 | 0.076431 | 0.129 | 0.050901 | -0.045889 | -0.048243 | -0.17607 | 1.374 | -120.2799 | 1.4979 | 1.4222 | 0.048273 | -120.1996 | -120.1506 | 121.7592 | 121.6345 | 121.5067 | 1.5807 | -121.5859 | 1.4028 | 1.4831 | 1.5321 | 1.5385 | -120.3088
1368.0469 | 121.7377 | -1.4374 | 120.2408 | 1.4211e-13 | -0.03576 | 0.0018589 | 0.064073 | -0.0078179 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.021536 | 0.026211 | 0.017569 | -1.3313 | 0.11129 | -1.4048 | 120.2989 | 120.1788 | 120.0418 | -1.3726 | 0.023941 | 0.06904 | -0.065509 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.064748 | 0.058122 | 0.10611 | 0.032593 | -0.032155 | -0.061972 | -0.19895 | 1.3282 | -120.3165 | 1.4613 | 1.3719 | 0.043694 | -120.2271 | -120.1827 | 121.7363 | 121.6162 | 121.4792 | 1.5487 | -121.6134 | 1.3616 | 1.4511 | 1.4955 | 1.5064 | -120.35
1369.75 | 121.6827 | -1.4603 | 120.2637 | 1.4211e-13 | -0.036188 | 0.0022863 | 0.064073 | -0.0078179 | 0.052683 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020895 | 0.025998 | 0.017355 | -1.3404 | 0.10214 | -1.4094 | 120.2943 | 120.1742 | 120.0418 | -1.3726 | 0.023941 | 0.06904 | -0.06093 | -0.071161 | 0.009128 | 0.058115 | -0.10462 | 0.087636 | 0.030656 | 0.11985 | 0.050903 | -0.036733 | -0.089438 | -0.22184 | 1.3556 | -120.3348 | 1.4842 | 1.3993 | 0.043694 | -120.2545 | -120.2056 | 121.7546 | 121.6345 | 121.5021 | 1.5624 | -121.6363 | 1.3891 | 1.4694 | 1.5184 | 1.5293 | -120.3683
1371.5 | 121.8155 | -1.4511 | 120.2225 | 1.4211e-13 | -0.036188 | 0.0018589 | 0.064073 | -0.0078179 | 0.052469 | -0.0022892 | -0.0048667 | -0.0012713 | 0.020895 | 0.025998 | 0.017569 | -1.3404 | 0.10671 | -1.4231 | 120.2852 | 120.1742 | 120.0418 | -1.3818 | 0.014784 | 0.059882 | -0.065509 | -0.066582 | 0.013707 | 0.062694 | -0.10462 | 0.069323 | 0.062698 | 0.11069 | 0.028013 | -0.04131 | -0.048239 | -0.18064 | 1.3465 | -120.2891 | 1.4659 | 1.3856 | 0.039115 | -120.2088 | -120.1598 | 121.7363 | 121.6253 | 121.4929 | 1.5578 | -121.6043 | 1.3845 | 1.4648 | 1.5138 | 1.511 | -120.3271
1373.2656 | 121.7102 | -1.474 | 120.2408 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.064073 | -0.0082453 | 0.052683 | -0.0022892 | -0.0048667 | -0.0012713 | 0.021108 | 0.025784 | 0.017569 | -1.345 | 0.097557 | -1.4231 | 120.2897 | 120.1697 | 120.0418 | -1.3909 | 0.02852 | 0.064461 | -0.06093 | -0.075739 | 0.013707 | 0.053537 | -0.1092 | 0.083054 | 0.048966 | 0.129 | 0.050901 | -0.032153 | -0.071129 | -0.19895 | 1.3648 | -120.3165 | 1.5025 | 1.4131 | 0.048273 | -120.2271 | -120.1872 | 121.7637 | 121.6437 | 121.5158 | 1.5716 | -121.6317 | 1.3983 | 1.4877 | 1.5275 | 1.5385 | -120.35
1375.0312 | 121.6644 | -1.5015 | 120.2362 | 1.4211e-13 | -0.036401 | 0.0016453 | 0.064073 | -0.0080317 | 0.052683 | -0.01755 | -0.0044395 | -0.0010577 | 0.021322 | 0.026211 | 0.017782 | -1.345 | 0.097557 | -1.4323 | 120.2897 | 120.1697 | 120.0418 | -1.3909 | 0.023941 | 0.073618 | -0.06093 | -0.071161 | 0.022864 | 0.058115 | -0.1092 | 0.11052 | 0.053544 | 0.15647 | 0.06921 | -0.04131 | -0.066551 | -0.19438 | 1.3923 | -120.3074 | 1.5254 | 1.4405 | 0.048273 | -120.2133 | -120.1781 | 121.7912 | 121.6711 | 121.5433 | 1.599 | -121.6272 | 1.4303 | 1.5243 | 1.5596 | 1.5751 | -120.3454
1376.7344 | 121.6873 | -1.4603 | 120.2774 | 1.4211e-13 | -0.036188 | 0.0020727 | 0.063859 | -0.0078179 | 0.052469 | 0.0053413 | -0.0048667 | -0.0012713 | 0.021108 | 0.025998 | 0.017569 | -1.3313 | 0.10214 | -1.4002 | 120.3172 | 120.2017 | 120.0739 | -1.3681 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.013707 | 0.053537 | -0.1092 | 0.092215 | 0.039815 | 0.129 | 0.060059 | -0.032156 | -0.075698 | -0.20352 | 1.3511 | -120.344 | 1.4842 | 1.3993 | 0.048273 | -120.2637 | -120.2239 | 121.7775 | 121.662 | 121.5341 | 1.5624 | -121.6455 | 1.3937 | 1.474 | 1.5138 | 1.5385 | -120.3866
1378.4844 | 121.8018 | -1.387 | 120.2545 | 1.4211e-13 | -0.036401 | 0.0018589 | 0.0645 | -0.0078179 | 0.052256 | -0.0099192 | -0.0050803 | -0.0014849 | 0.021322 | 0.025998 | 0.017569 | -1.3267 | 0.11129 | -1.4002 | 120.3264 | 120.2063 | 120.0785 | -1.3543 | 0.023941 | 0.073618 | -0.056351 | -0.071161 | 0.009128 | 0.058115 | -0.1092 | 0.03271 | 0.07186 | 0.060339 | -0.013183 | -0.045893 | -0.048231 | -0.17606 | 1.2778 | -120.3257 | 1.411 | 1.3307 | 0.052852 | -120.2454 | -120.1964 | 121.7134 | 121.5933 | 121.4655 | 1.4983 | -121.6088 | 1.3159 | 1.3962 | 1.4451 | 1.4606 | -120.3637
1380.2344 | 121.8063 | -1.4008 | 120.2454 | 1.4211e-13 | -0.035974 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.021322 | 0.025998 | 0.017569 | -1.3084 | 0.10214 | -1.3773 | 120.3355 | 120.2154 | 120.0968 | -1.3452 | 0.023941 | 0.064461 | -0.056351 | -0.071161 | 0.013707 | 0.062694 | -0.10462 | 0.055601 | 0.090173 | 0.092386 | 0.023442 | -0.032159 | -0.029917 | -0.14859 | 1.2961 | -120.3165 | 1.4247 | 1.3444 | 0.048273 | -120.2317 | -120.1827 | 121.7363 | 121.6162 | 121.4975 | 1.5029 | -121.5905 | 1.3296 | 1.4145 | 1.4635 | 1.4652 | -120.35
1381.9844 | 121.8338 | -1.3916 | 120.282 | 1.4211e-13 | -0.036615 | 0.0020727 | 0.064073 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.026211 | 0.017355 | -1.2901 | 0.10671 | -1.359 | 120.3538 | 120.2383 | 120.1059 | -1.3268 | 0.019362 | 0.059882 | -0.056351 | -0.075739 | 0.013707 | 0.053537 | -0.10462 | 0.064762 | 0.071865 | 0.10154 | 0.0326 | -0.032162 | -0.043643 | -0.17605 | 1.287 | -120.3577 | 1.411 | 1.3353 | 0.048273 | -120.2683 | -120.2284 | 121.7454 | 121.6299 | 121.4975 | 1.4983 | -121.6088 | 1.3159 | 1.4053 | 1.4451 | 1.4515 | -120.3866
1383.6719 | 121.6827 | -1.4236 | 120.3323 | 1.4211e-13 | -0.036615 | 0.0020727 | 0.064286 | -0.0080317 | 0.052469 | -0.0022892 | -0.0050803 | -0.0012713 | 0.021322 | 0.026211 | 0.017996 | -1.2717 | 0.10671 | -1.3498 | 120.3813 | 120.2567 | 120.1288 | -1.3085 | 0.023941 | 0.073618 | -0.051772 | -0.075739 | 0.013707 | 0.062694 | -0.1092 | 0.11512 | 0.048981 | 0.1519 | 0.073799 | -0.041321 | -0.075682 | -0.20351 | 1.3144 | -120.4081 | 1.4476 | 1.3719 | 0.057431 | -120.3186 | -120.2696 | 121.805 | 121.6803 | 121.5525 | 1.5304 | -121.6409 | 1.3479 | 1.4374 | 1.4863 | 1.4973 | -120.4415
1385.4219 | 121.7697 | -1.355 | 120.3278 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.064073 | -0.0078179 | 0.052683 | 0.0053413 | -0.0042257 | -0.0012713 | 0.021322 | 0.026425 | 0.017355 | -1.2443 | 0.10671 | -1.3178 | 120.4134 | 120.2841 | 120.1563 | -1.2811 | 0.019362 | 0.064461 | -0.056351 | -0.066582 | 0.013707 | 0.062694 | -0.10462 | 0.073929 | 0.085607 | 0.11071 | 0.037182 | -0.036747 | -0.043631 | -0.17146 | 1.2504 | -120.3943 | 1.3743 | 1.2986 | 0.048273 | -120.3141 | -120.2651 | 121.7683 | 121.6391 | 121.5113 | 1.4617 | -121.6088 | 1.2884 | 1.3687 | 1.4177 | 1.4194 | -120.4324
1387.1875 | 121.7377 | -1.3275 | 120.3735 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.064073 | -0.0080317 | 0.052469 | -0.0022892 | -0.0044395 | -0.0012713 | 0.021108 | 0.026211 | 0.017569 | -1.2031 | 0.11129 | -1.2812 | 120.4408 | 120.3299 | 120.1975 | -1.249 | 0.02852 | 0.06904 | -0.056351 | -0.071161 | 0.018285 | 0.062694 | -0.10462 | 0.078516 | 0.067301 | 0.12445 | 0.046344 | -0.032172 | -0.043618 | -0.17603 | 1.2229 | -120.4447 | 1.356 | 1.2712 | 0.048273 | -120.3552 | -120.3108 | 121.7684 | 121.6574 | 121.525 | 1.4388 | -121.6225 | 1.2564 | 1.3458 | 1.3902 | 1.3966 | -120.4782
1388.9531 | 121.7834 | -1.2955 | 120.3644 | 1.4211e-13 | -0.036401 | 0.0018589 | 0.064073 | -0.0078179 | 0.052683 | -0.01755 | -0.0046531 | -0.0012713 | 0.021108 | 0.025784 | 0.017569 | -1.1985 | 0.11129 | -1.2766 | 120.45 | 120.3299 | 120.2067 | -1.2353 | 0.02852 | 0.06904 | -0.056351 | -0.071161 | 0.013707 | 0.058115 | -0.1092 | 0.060209 | 0.085613 | 0.096981 | 0.018878 | -0.041331 | -0.034463 | -0.15772 | 1.1863 | -120.4355 | 1.324 | 1.2391 | 0.052852 | -120.3507 | -120.3063 | 121.7455 | 121.6254 | 121.5021 | 1.4068 | -121.5996 | 1.2243 | 1.3092 | 1.3536 | 1.3645 | -120.4736
1390.6406 | 121.8018 | -1.2955 | 120.3964 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064286 | -0.0082453 | 0.052042 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021322 | 0.025998 | 0.017569 | -1.1848 | 0.10671 | -1.2629 | 120.4729 | 120.3528 | 120.2296 | -1.2215 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.058115 | -0.10004 | 0.073946 | 0.076462 | 0.11072 | 0.032613 | -0.041333 | -0.043611 | -0.16687 | 1.1954 | -120.4767 | 1.3194 | 1.2345 | 0.039115 | -120.3827 | -120.3383 | 121.7684 | 121.6483 | 121.525 | 1.4022 | -121.6179 | 1.2152 | 1.3092 | 1.3536 | 1.3691 | -120.4965
1392.3906 | 121.7972 | -1.2451 | 120.4239 | 1.4211e-13 | -0.036188 | 0.0018589 | 0.063859 | -0.0078179 | 0.052256 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021108 | 0.025998 | 0.017569 | -1.1573 | 0.10214 | -1.24 | 120.4912 | 120.3711 | 120.2433 | -1.2032 | 0.019362 | 0.073618 | -0.065509 | -0.075739 | 0.018285 | 0.058115 | -0.10462 | 0.041908 | 0.06731 | 0.087832 | 0.00515 | -0.036758 | -0.052762 | -0.1806 | 1.1405 | -120.4996 | 1.2645 | 1.1796 | 0.039115 | -120.4056 | -120.3658 | 121.7363 | 121.6162 | 121.4884 | 1.3473 | -121.6271 | 1.1694 | 1.2634 | 1.3032 | 1.3187 | -120.5285
1394.1562 | 121.6782 | -1.2772 | 120.4697 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020895 | 0.025998 | 0.017569 | -1.1481 | 0.10671 | -1.2262 | 120.5187 | 120.394 | 120.2662 | -1.1895 | 0.010205 | 0.078197 | -0.056351 | -0.071161 | 0.013707 | 0.062694 | -0.11378 | 0.087688 | 0.049003 | 0.12903 | 0.050929 | -0.036759 | -0.075644 | -0.20348 | 1.1634 | -120.5408 | 1.2874 | 1.2208 | 0.057431 | -120.456 | -120.407 | 121.7958 | 121.6712 | 121.5433 | 1.3839 | -121.6591 | 1.206 | 1.2909 | 1.3399 | 1.3554 | -120.5834
1395.9219 | 121.7102 | -1.2589 | 120.4834 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0048667 | -0.0012713 | 0.020895 | 0.025998 | 0.017355 | -1.1298 | 0.10214 | -1.2125 | 120.5232 | 120.4123 | 120.2753 | -1.1757 | 0.023941 | 0.073618 | -0.056351 | -0.075739 | 0.018285 | 0.058115 | -0.10462 | 0.083114 | 0.039849 | 0.12904 | 0.046353 | -0.036761 | -0.07106 | -0.20806 | 1.1542 | -120.5591 | 1.2828 | 1.2025 | 0.048273 | -120.4651 | -120.4253 | 121.7821 | 121.6712 | 121.5342 | 1.361 | -121.6591 | 1.1831 | 1.2771 | 1.317 | 1.3325 | -120.588
1397.625 | 121.8063 | -1.1856 | 120.4834 | 1.4211e-13 | -0.036401 | 0.0018589 | 0.063859 | -0.0082453 | 0.052897 | -0.0099192 | -0.0050803 | -0.0014849 | 0.020895 | 0.026211 | 0.017355 | -1.0932 | 0.11129 | -1.1667 | 120.569 | 120.4535 | 120.3257 | -1.1299 | 0.023941 | 0.064461 | -0.056351 | -0.071161 | 0.004549 | 0.062694 | -0.10004 | 0.055661 | 0.085633 | 0.092421 | 0.018894 | -0.036767 | -0.02985 | -0.15769 | 1.0856 | -120.5546 | 1.2095 | 1.1293 | 0.043694 | -120.4788 | -120.4207 | 121.7546 | 121.6392 | 121.5113 | 1.2969 | -121.6133 | 1.1144 | 1.1902 | 1.2483 | 1.2501 | -120.5834
1399.375 | 121.7194 | -1.2177 | 120.5475 | 1.4211e-13 | -0.036829 | 0.0016453 | 0.064073 | -0.0080317 | 0.052897 | -0.0022892 | -0.0048667 | -0.0014849 | 0.021322 | 0.026211 | 0.017355 | -1.0749 | 0.10671 | -1.1392 | 120.6011 | 120.481 | 120.3578 | -1.1162 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.009128 | 0.062694 | -0.10462 | 0.10144 | 0.053595 | 0.14278 | 0.078406 | -0.023035 | -0.066463 | -0.18973 | 1.113 | -120.6232 | 1.2462 | 1.1567 | 0.043694 | -120.5384 | -120.4848 | 121.8187 | 121.6987 | 121.5754 | 1.3244 | -121.6637 | 1.1419 | 1.2268 | 1.2803 | 1.2958 | -120.6521
1401.1406 | 121.8063 | -1.149 | 120.5292 | 1.4211e-13 | -0.036401 | 0.0016453 | 0.063859 | -0.0082453 | 0.052469 | -0.0099192 | -0.0048667 | -0.0014849 | 0.021108 | 0.026211 | 0.017569 | -1.0611 | 0.10671 | -1.1392 | 120.6102 | 120.4856 | 120.3715 | -1.1025 | 0.023941 | 0.078197 | -0.051772 | -0.071161 | 0.022864 | 0.058115 | -0.11378 | 0.046514 | 0.081062 | 0.087849 | 0.009742 | -0.036772 | -0.043575 | -0.15769 | 1.0352 | -120.6003 | 1.1729 | 1.0972 | 0.06201 | -120.5063 | -120.4711 | 121.7592 | 121.6346 | 121.5205 | 1.2557 | -121.6316 | 1.0778 | 1.1719 | 1.2071 | 1.2272 | -120.643
1402.8906 | 121.8109 | -1.1261 | 120.5521 | 1.4211e-13 | -0.036401 | 0.0016453 | 0.064286 | -0.0080317 | 0.052256 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020895 | 0.026211 | 0.017355 | -1.0382 | 0.10671 | -1.1118 | 120.624 | 120.5131 | 120.3852 | -1.075 | 0.02852 | 0.073618 | -0.06093 | -0.071161 | 0.013707 | 0.062694 | -0.10004 | 0.051099 | 0.071909 | 0.087852 | 0.014324 | -0.036775 | -0.038989 | -0.16684 | 1.0261 | -120.6232 | 1.1546 | 1.0652 | 0.039115 | -120.5384 | -120.4894 | 121.7501 | 121.6392 | 121.5113 | 1.2328 | -121.6271 | 1.0549 | 1.1398 | 1.1888 | 1.1997 | -120.6521
1404.5781 | 121.7148 | -1.1673 | 120.5658 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.063859 | -0.0082453 | 0.052042 | -0.0022892 | -0.0048667 | -0.0010577 | 0.020895 | 0.025998 | 0.017355 | -1.0382 | 0.11129 | -1.1255 | 120.6286 | 120.5177 | 120.3852 | -1.0842 | 0.023941 | 0.078197 | -0.056351 | -0.071161 | 0.013707 | 0.058115 | -0.1092 | 0.08314 | 0.062754 | 0.12905 | 0.041787 | -0.041353 | -0.048143 | -0.18057 | 1.0581 | -120.637 | 1.1912 | 1.1109 | 0.052852 | -120.5521 | -120.5077 | 121.7958 | 121.685 | 121.5525 | 1.2786 | -121.65 | 1.0961 | 1.181 | 1.2254 | 1.2455 | -120.675
1406.3438 | 121.7972 | -1.1536 | 120.5612 | 1.4211e-13 | -0.036615 | 0.0022863 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0046531 | -0.0010577 | 0.021108 | 0.026425 | 0.017569 | -1.0474 | 0.10671 | -1.1164 | 120.624 | 120.5039 | 120.3898 | -1.0796 | 0.019362 | 0.073618 | -0.056351 | -0.075739 | 0.013707 | 0.053537 | -0.10462 | 0.073985 | 0.062754 | 0.10616 | 0.037211 | -0.036774 | -0.057302 | -0.17141 | 1.0489 | -120.637 | 1.1729 | 1.0972 | 0.048273 | -120.5475 | -120.5077 | 121.7775 | 121.6575 | 121.5434 | 1.2603 | -121.6408 | 1.0778 | 1.1673 | 1.2071 | 1.2272 | -120.6658
1408.0938 | 121.7194 | -1.1673 | 120.6162 | 1.4211e-13 | -0.036615 | 0.0020727 | 0.064286 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.00084406 | 0.021108 | 0.026639 | 0.017355 | -1.0337 | 0.10671 | -1.1072 | 120.6331 | 120.5222 | 120.3898 | -1.0796 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.018285 | 0.062694 | -0.10462 | 0.087718 | 0.016979 | 0.13363 | 0.0601 | -0.027618 | -0.093918 | -0.22635 | 1.0627 | -120.6873 | 1.1912 | 1.1064 | 0.043694 | -120.5979 | -120.5535 | 121.8004 | 121.6895 | 121.5571 | 1.274 | -121.6957 | 1.0961 | 1.1856 | 1.23 | 1.2455 | -120.7208
1409.8438 | 121.7148 | -1.1856 | 120.6024 | 1.4211e-13 | -0.036401 | 0.0018589 | 0.064073 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.021108 | 0.026211 | 0.017569 | -1.0382 | 0.11129 | -1.1118 | 120.6423 | 120.5131 | 120.399 | -1.0704 | 0.033099 | 0.064461 | -0.056351 | -0.075739 | 0.018285 | 0.062694 | -0.10462 | 0.11519 | 0.039869 | 0.14736 | 0.073833 | -0.041354 | -0.089343 | -0.20346 | 1.081 | -120.6782 | 1.2187 | 1.1293 | 0.048273 | -120.5841 | -120.5397 | 121.8279 | 121.6987 | 121.5846 | 1.2969 | -121.6728 | 1.1099 | 1.2039 | 1.2483 | 1.2501 | -120.707
1411.5312 | 121.6873 | -1.1993 | 120.5933 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.064073 | -0.0084589 | 0.052469 | -0.0022892 | -0.0048667 | -0.0012713 | 0.021322 | 0.026425 | 0.017355 | -1.0428 | 0.11129 | -1.1209 | 120.6377 | 120.5085 | 120.3944 | -1.0933 | 0.019362 | 0.06904 | -0.06093 | -0.080318 | 0.009128 | 0.058115 | -0.10004 | 0.10603 | 0.044445 | 0.15652 | 0.078409 | -0.027617 | -0.084767 | -0.19888 | 1.0993 | -120.6736 | 1.2187 | 1.1384 | 0.039115 | -120.5841 | -120.5351 | 121.837 | 121.7078 | 121.5937 | 1.3106 | -121.6866 | 1.119 | 1.2085 | 1.2575 | 1.2684 | -120.6933
1413.2969 | 121.7514 | -1.1307 | 120.6207 | 1.4211e-13 | -0.036829 | 0.0022863 | 0.063859 | -0.0084589 | 0.052256 | -0.0099192 | -0.0046531 | -0.0010577 | 0.021108 | 0.026852 | 0.017996 | -1.0016 | 0.11129 | -1.0797 | 120.6698 | 120.5634 | 120.4264 | -1.0429 | 0.023941 | 0.06904 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.10462 | 0.087729 | 0.049028 | 0.12906 | 0.050949 | -0.03678 | -0.057286 | -0.19429 | 1.0261 | -120.6965 | 1.1546 | 1.0743 | 0.048273 | -120.607 | -120.5626 | 121.8004 | 121.6941 | 121.5571 | 1.242 | -121.6637 | 1.0549 | 1.1444 | 1.1888 | 1.1997 | -120.7254
1415.0625 | 121.7331 | -1.0986 | 120.6665 | 1.4211e-13 | -0.036615 | 0.0020727 | 0.063859 | -0.0078179 | 0.052256 | -0.0099192 | -0.0048667 | -0.0010577 | 0.021322 | 0.026211 | 0.016714 | -0.98788 | 0.11129 | -1.0568 | 120.6972 | 120.5772 | 120.4539 | -1.0201 | 0.023941 | 0.073618 | -0.056351 | -0.066582 | 0.013707 | 0.062694 | -0.1092 | 0.07858 | 0.030722 | 0.11075 | 0.041797 | -0.036783 | -0.089325 | -0.2126 | 0.98943 | -120.7331 | 1.1226 | 1.0423 | 0.052852 | -120.6528 | -120.6038 | 121.7959 | 121.6758 | 121.5525 | 1.2099 | -121.6866 | 1.0321 | 1.1123 | 1.1613 | 1.1723 | -120.7757
1416.8281 | 121.7422 | -1.0941 | 120.6619 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.063859 | -0.0082453 | 0.052469 | -0.0099192 | -0.0046531 | -0.0014849 | 0.020895 | 0.026425 | 0.017355 | -0.97873 | 0.11587 | -1.0523 | 120.711 | 120.5863 | 120.4631 | -1.0155 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.013707 | 0.058115 | -0.10462 | 0.078581 | 0.049035 | 0.11533 | 0.041798 | -0.036783 | -0.075589 | -0.19886 | 0.98943 | -120.7331 | 1.118 | 1.0331 | 0.043694 | -120.6482 | -120.6038 | 121.805 | 121.6804 | 121.5571 | 1.2099 | -121.6774 | 1.0229 | 1.1078 | 1.1522 | 1.1723 | -120.7665
1418.5312 | 121.8246 | -1.062 | 120.6436 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.064073 | -0.0082453 | 0.052256 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021108 | 0.026211 | 0.017355 | -0.96499 | 0.11587 | -1.0385 | 120.7201 | 120.6047 | 120.4768 | -1.0017 | 0.023941 | 0.073618 | -0.06093 | -0.071161 | 0.013707 | 0.062694 | -0.10462 | 0.060275 | 0.076502 | 0.09702 | 0.023489 | -0.036786 | -0.038964 | -0.16682 | 0.95739 | -120.7148 | 1.086 | 1.0011 | 0.043694 | -120.6299 | -120.5809 | 121.7821 | 121.6667 | 121.5388 | 1.1779 | -121.6454 | 0.99085 | 1.0757 | 1.1247 | 1.1356 | -120.7482
1420.2812 | 121.8384 | -1.0437 | 120.6528 | 1.4211e-13 | -0.036401 | 0.0018589 | 0.063859 | -0.0080317 | 0.052256 | -0.0022892 | -0.0048667 | -0.0014849 | 0.020895 | 0.026211 | 0.017355 | -0.95126 | 0.11129 | -1.0202 | 120.7339 | 120.6184 | 120.4905 | -0.99258 | 0.019362 | 0.059882 | -0.065509 | -0.066582 | 0.013707 | 0.058115 | -0.10004 | 0.051122 | 0.081082 | 0.092444 | 0.023492 | -0.02763 | -0.034382 | -0.16224 | 0.94366 | -120.7194 | 1.0631 | 0.97819 | 0.034536 | -120.6391 | -120.5947 | 121.7776 | 121.6621 | 121.5342 | 1.155 | -121.6454 | 0.97712 | 1.0574 | 1.1018 | 1.1036 | -120.7528
1422.0469 | 121.7239 | -1.0666 | 120.6894 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.064073 | -0.0082453 | 0.052683 | -0.0099192 | -0.0046531 | -0.0014849 | 0.021322 | 0.026425 | 0.017569 | -0.94668 | 0.11587 | -1.0156 | 120.7476 | 120.6321 | 120.4997 | -0.97884 | 0.023941 | 0.06904 | -0.056351 | -0.066582 | 0.018285 | 0.053537 | -0.1092 | 0.087747 | 0.058196 | 0.11991 | 0.050958 | -0.036789 | -0.057266 | -0.1897 | 0.95739 | -120.756 | 1.0905 | 1.0102 | 0.052852 | -120.6711 | -120.6359 | 121.8142 | 121.6987 | 121.5663 | 1.1825 | -121.6682 | 1 | 1.0849 | 1.1201 | 1.1356 | -120.7986
1423.8281 | 121.7148 | -1.1124 | 120.7169 | 1.4211e-13 | -0.037042 | 0.0020727 | 0.0645 | -0.0082453 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020895 | 0.026211 | 0.017355 | -0.94668 | 0.11587 | -1.0294 | 120.7476 | 120.6184 | 120.4905 | -0.99716 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.009128 | 0.048958 | -0.095467 | 0.11521 | 0.03073 | 0.16569 | 0.083 | -0.032208 | -0.098469 | -0.22633 | 1.0169 | -120.7972 | 1.1363 | 1.0514 | 0.034537 | -120.7077 | -120.6679 | 121.86 | 121.7308 | 121.6029 | 1.2282 | -121.714 | 1.032 | 1.1215 | 1.1613 | 1.1814 | -120.8123
1425.5156 | 121.7285 | -1.0574 | 120.7306 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0016987 | 0.021536 | 0.026211 | 0.017782 | -0.92379 | 0.11587 | -0.99274 | 120.7659 | 120.655 | 120.5317 | -0.95595 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.10004 | 0.10149 | 0.035311 | 0.13365 | 0.064694 | -0.036792 | -0.07557 | -0.19885 | 0.95739 | -120.8109 | 1.0768 | 0.9965 | 0.039115 | -120.7169 | -120.6679 | 121.8233 | 121.7125 | 121.5892 | 1.1733 | -121.6865 | 0.97712 | 1.0711 | 1.1201 | 1.1311 | -120.8306
1427.2656 | 121.7285 | -1.03 | 120.7489 | 1.4211e-13 | -0.036401 | 0.0020727 | 0.064073 | -0.0080317 | 0.052469 | -0.01755 | -0.0048667 | -0.0016987 | 0.020895 | 0.026425 | 0.017569 | -0.90547 | 0.11587 | -0.98358 | 120.7888 | 120.6688 | 120.5455 | -0.94679 | 0.02852 | 0.06904 | -0.056351 | -0.071161 | 0.013707 | 0.058115 | -0.1092 | 0.083178 | 0.039893 | 0.1245 | 0.046385 | -0.036793 | -0.080144 | -0.20343 | 0.92077 | -120.8201 | 1.0585 | 0.97362 | 0.052852 | -120.7352 | -120.6908 | 121.8188 | 121.6987 | 121.5754 | 1.1458 | -121.6957 | 0.95881 | 1.0437 | 1.0881 | 1.099 | -120.8581
1429.0312 | 121.756 | -1.0162 | 120.7306 | 1.4211e-13 | -0.037042 | 0.0016453 | 0.064073 | -0.0080317 | 0.052683 | -0.0022892 | -0.0048667 | -0.0010577 | 0.021108 | 0.026425 | 0.017782 | -0.89174 | 0.11587 | -0.96985 | 120.8025 | 120.6825 | 120.5546 | -0.93763 | 0.02852 | 0.073618 | -0.06093 | -0.066582 | 0.013707 | 0.058115 | -0.10004 | 0.078603 | 0.071938 | 0.1245 | 0.046387 | -0.032216 | -0.048097 | -0.17596 | 0.91619 | -120.7972 | 1.0448 | 0.9553 | 0.039115 | -120.7169 | -120.6725 | 121.8188 | 121.6987 | 121.5709 | 1.1321 | -121.6682 | 0.94965 | 1.0299 | 1.0743 | 1.0899 | -120.8306
1430.7188 | 121.7056 | -1.0025 | 120.7535 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0084589 | 0.052256 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020895 | 0.026211 | 0.017782 | -0.88716 | 0.11129 | -0.96069 | 120.8117 | 120.6871 | 120.5729 | -0.93305 | 0.019362 | 0.078197 | -0.056351 | -0.062004 | 0.013707 | 0.058115 | -0.1092 | 0.069449 | 0.058207 | 0.11534 | 0.04181 | -0.027639 | -0.066406 | -0.18053 | 0.8933 | -120.8155 | 1.0219 | 0.94615 | 0.052852 | -120.7398 | -120.6954 | 121.8142 | 121.6896 | 121.5755 | 1.1138 | -121.6865 | 0.9405 | 1.0162 | 1.0606 | 1.0807 | -120.8627
1432.4688 | 121.7056 | -1.0345 | 120.7352 | 1.4211e-13 | -0.036615 | 0.0016453 | 0.064286 | -0.0082453 | 0.052256 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.026425 | 0.017141 | -0.87343 | 0.11587 | -0.95154 | 120.8208 | 120.6962 | 120.5775 | -0.91932 | 0.019362 | 0.073618 | -0.065509 | -0.071161 | 0.018285 | 0.062694 | -0.1092 | 0.11523 | 0.085675 | 0.16112 | 0.083011 | -0.032219 | -0.038937 | -0.15764 | 0.92534 | -120.8063 | 1.0539 | 0.96904 | 0.043694 | -120.7169 | -120.6725 | 121.8554 | 121.7308 | 121.6121 | 1.1504 | -121.6545 | 0.96338 | 1.0528 | 1.0972 | 1.1082 | -120.8444
1434.2188 | 121.7697 | -1.0208 | 120.7489 | 1.4211e-13 | -0.036829 | 0.0022863 | 0.064073 | -0.0082453 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.021108 | 0.025998 | 0.017569 | -0.88716 | 0.11587 | -0.95611 | 120.8163 | 120.7008 | 120.5729 | -0.91932 | 0.023941 | 0.06904 | -0.056351 | -0.080318 | 0.004549 | 0.058115 | -0.11378 | 0.1015 | 0.067363 | 0.13365 | 0.0647 | -0.036797 | -0.048091 | -0.17595 | 0.90703 | -120.8292 | 1.0448 | 0.96446 | 0.057431 | -120.7444 | -120.6908 | 121.8371 | 121.7216 | 121.5938 | 1.1367 | -121.6682 | 0.94049 | 1.0254 | 1.0789 | 1.0899 | -120.8627
1435.9688 | 121.8796 | -0.98877 | 120.7306 | 1.4211e-13 | -0.036829 | 0.0020727 | 0.064286 | -0.0080317 | 0.052469 | -0.0099192 | -0.0048667 | -0.0012713 | 0.020681 | 0.026425 | 0.017355 | -0.88258 | 0.11587 | -0.96069 | 120.8117 | 120.6871 | 120.5729 | -0.91932 | 0.023941 | 0.073618 | -0.065509 | -0.075739 | 0.009128 | 0.062694 | -0.10004 | 0.069454 | 0.081095 | 0.10619 | 0.028078 | -0.041376 | -0.043518 | -0.15764 | 0.88872 | -120.8063 | 1.0127 | 0.92326 | 0.034536 | -120.7215 | -120.6679 | 121.8005 | 121.6758 | 121.5617 | 1.1046 | -121.6499 | 0.91303 | 0.9979 | 1.0515 | 1.0624 | -120.8306
1437.6719 | 121.7422 | -1.03 | 120.7672 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0086727 | 0.052469 | -0.0099192 | -0.0046531 | -0.0014849 | 0.021108 | 0.026425 | 0.017141 | -0.89632 | 0.10671 | -0.96527 | 120.8117 | 120.6871 | 120.5775 | -0.92847 | 0.019362 | 0.06904 | -0.06093 | -0.071161 | 0.018285 | 0.058115 | -0.1092 | 0.10149 | 0.044474 | 0.13365 | 0.064698 | -0.036796 | -0.080139 | -0.18968 | 0.92077 | -120.8384 | 1.0493 | 0.96904 | 0.048273 | -120.7489 | -120.7091 | 121.8417 | 121.717 | 121.6075 | 1.1367 | -121.6957 | 0.95881 | 1.0483 | 1.0881 | 1.099 | -120.8764
1439.4219 | 121.7972 | -0.97046 | 120.7626 | 1.4211e-13 | -0.036829 | 0.0016453 | 0.064286 | -0.0078179 | 0.052469 | -0.01755 | -0.0044395 | -0.0012713 | 0.020681 | 0.026425 | 0.017141 | -0.89174 | 0.11587 | -0.96069 | 120.8071 | 120.6962 | 120.5775 | -0.9239 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.10004 | 0.046564 | 0.044474 | 0.078721 | 0.009767 | -0.036797 | -0.066403 | -0.18511 | 0.87041 | -120.8384 | 0.9944 | 0.90953 | 0.039115 | -120.7489 | -120.7045 | 121.7776 | 121.6667 | 121.548 | 1.0863 | -121.6865 | 0.89472 | 0.98417 | 1.0286 | 1.0578 | -120.8627
1441.125 | 121.8521 | -0.98877 | 120.7489 | 1.4211e-13 | -0.036401 | 0.0014317 | 0.064073 | -0.0084589 | 0.052256 | -0.0099192 | -0.0048667 | -0.0012713 | 0.020681 | 0.026639 | 0.017569 | -0.88716 | 0.11587 | -0.95611 | 120.8254 | 120.7008 | 120.5867 | -0.91932 | 0.014784 | 0.078197 | -0.06093 | -0.075739 | 0.013707 | 0.062694 | -0.095467 | 0.069454 | 0.07652 | 0.10161 | 0.032657 | -0.036797 | -0.048091 | -0.16222 | 0.8933 | -120.8246 | 1.0036 | 0.92784 | 0.034537 | -120.7352 | -120.6862 | 121.8142 | 121.6896 | 121.5755 | 1.1046 | -121.6682 | 0.91303 | 1.0025 | 1.0515 | 1.067 | -120.8444
1442.8906 | 121.7239 | -1.0208 | 120.7443 | 1.4211e-13 | -0.036615 | 0.0016453 | 0.064073 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020895 | 0.026211 | 0.017355 | -0.89174 | 0.11129 | -0.96527 | 120.83 | 120.6962 | 120.5821 | -0.93305 | 0.023941 | 0.087354 | -0.056351 | -0.075739 | 0.009128 | 0.062694 | -0.10462 | 0.08776 | 0.085675 | 0.12907 | 0.055543 | -0.032217 | -0.048093 | -0.16222 | 0.91619 | -120.8201 | 1.0448 | 0.96446 | 0.048273 | -120.7352 | -120.6816 | 121.8508 | 121.717 | 121.6029 | 1.1321 | -121.6774 | 0.94507 | 1.0299 | 1.0835 | 1.1082 | -120.8489
1444.6094 | 121.7422 | -1.0254 | 120.7443 | 1.4211e-13 | -0.036615 | 0.0018589 | 0.0645 | -0.0080317 | 0.052469 | -0.01755 | -0.0046531 | -0.0010577 | 0.021108 | 0.026211 | 0.017569 | -0.90547 | 0.11587 | -0.98358 | 120.7934 | 120.6779 | 120.5592 | -0.95137 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.004549 | 0.048958 | -0.10004 | 0.074022 | 0.049048 | 0.11992 | 0.041808 | -0.032214 | -0.066409 | -0.18511 | 0.92535 | -120.8201 | 1.0539 | 0.96904 | 0.043694 | -120.7398 | -120.6954 | 121.8188 | 121.7033 | 121.5846 | 1.1413 | -121.6957 | 0.94965 | 1.0299 | 1.0743 | 1.1127 | -120.8444
1446.3438 | 121.8658 | -0.99792 | 120.7077 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.01755 | -0.0048667 | -0.00084406 | 0.021322 | 0.026425 | 0.017141 | -0.9009 | 0.12045 | -0.98358 | 120.8163 | 120.6871 | 120.5821 | -0.93763 | 0.02852 | 0.073618 | -0.056351 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.060293 | 0.10856 | 0.09703 | 0.014342 | -0.045951 | -0.02063 | -0.1256 | 0.8933 | -120.7834 | 1.0264 | 0.94157 | 0.048273 | -120.6986 | -120.6496 | 121.8142 | 121.685 | 121.58 | 1.1184 | -121.6453 | 0.92219 | 1.0071 | 1.056 | 1.0715 | -120.8123
1448.0938 | 121.8842 | -1.0437 | 120.6985 | 1.4211e-13 | -0.036829 | 0.0016453 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020895 | 0.026211 | 0.017569 | -0.93752 | 0.11587 | -1.0019 | 120.7796 | 120.6596 | 120.5501 | -0.97426 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.018285 | 0.062694 | -0.1092 | 0.069438 | 0.08109 | 0.10618 | 0.041805 | -0.027633 | -0.038947 | -0.14849 | 0.9345 | -120.7743 | 1.0631 | 0.98735 | 0.052852 | -120.6803 | -120.6359 | 121.8233 | 121.7033 | 121.5938 | 1.1596 | -121.6728 | 0.96796 | 1.062 | 1.1064 | 1.1311 | -120.8077
1449.8438 | 121.8521 | -0.99792 | 120.7169 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.01755 | -0.0046531 | -0.0012713 | 0.020895 | 0.025998 | 0.017141 | -0.89632 | 0.11129 | -0.98358 | 120.8117 | 120.6917 | 120.5729 | -0.94221 | 0.023941 | 0.091933 | -0.06093 | -0.075739 | 0.009128 | 0.062694 | -0.10462 | 0.055714 | 0.094828 | 0.10161 | 0.014342 | -0.041372 | -0.025206 | -0.14391 | 0.8933 | -120.7926 | 1.0219 | 0.93699 | 0.043694 | -120.7077 | -120.6542 | 121.8096 | 121.6896 | 121.5709 | 1.1092 | -121.6591 | 0.92219 | 1.0071 | 1.0606 | 1.0899 | -120.8215
1451.5312 | 121.7697 | -1.0483 | 120.7581 | 1.4211e-13 | -0.037042 | 0.0016453 | 0.064073 | -0.0082453 | 0.052897 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020681 | 0.026425 | 0.017355 | -0.91005 | 0.11129 | -0.97901 | 120.8117 | 120.6917 | 120.5729 | -0.94221 | 0.02852 | 0.087354 | -0.065509 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.10607 | 0.053629 | 0.13823 | 0.069274 | -0.036794 | -0.066405 | -0.18511 | 0.93908 | -120.8338 | 1.0768 | 0.98277 | 0.043694 | -120.7443 | -120.6999 | 121.86 | 121.7399 | 121.6212 | 1.1596 | -121.7003 | 0.97254 | 1.062 | 1.1064 | 1.1356 | -120.8673
1453.2812 | 121.7422 | -1.0666 | 120.7626 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0080317 | 0.052256 | -0.0099192 | -0.0052939 | -0.0014849 | 0.020895 | 0.026211 | 0.017569 | -0.91921 | 0.11587 | -0.99732 | 120.8025 | 120.6825 | 120.5592 | -0.94679 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.013707 | 0.053537 | -0.10462 | 0.1198 | 0.039895 | 0.14738 | 0.069271 | -0.050528 | -0.08014 | -0.20342 | 0.96196 | -120.8338 | 1.0905 | 1.0102 | 0.048273 | -120.7489 | -120.7091 | 121.8691 | 121.7491 | 121.6258 | 1.1825 | -121.7094 | 0.99543 | 1.0803 | 1.1201 | 1.1494 | -120.8673
1455.0312 | 121.7789 | -1.03 | 120.7672 | 1.4211e-13 | -0.036829 | 0.0022863 | 0.064286 | -0.0082453 | 0.052683 | -0.0022892 | -0.0046531 | -0.0012713 | 0.021108 | 0.026639 | 0.017141 | -0.91463 | 0.12045 | -0.97901 | 120.8117 | 120.7008 | 120.5729 | -0.94221 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.018285 | 0.067272 | -0.095467 | 0.087757 | 0.044474 | 0.11534 | 0.050963 | -0.036794 | -0.066402 | -0.19426 | 0.9345 | -120.8384 | 1.0539 | 0.96446 | 0.029958 | -120.7489 | -120.6999 | 121.8417 | 121.7308 | 121.6029 | 1.1504 | -121.7094 | 0.95881 | 1.0483 | 1.0972 | 1.1173 | -120.8627
1456.7344 | 121.8613 | -1.0025 | 120.726 | 1.4211e-13 | -0.036829 | 0.0020727 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020681 | 0.026639 | 0.017355 | -0.91463 | 0.12503 | -0.98816 | 120.8071 | 120.6825 | 120.5775 | -0.95595 | 0.033099 | 0.091933 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.10004 | 0.046554 | 0.081095 | 0.087872 | 0.014341 | -0.032213 | -0.043519 | -0.14849 | 0.90246 | -120.8018 | 1.0356 | 0.94157 | 0.039115 | -120.7123 | -120.6679 | 121.8096 | 121.685 | 121.58 | 1.1275 | -121.682 | 0.92676 | 1.0162 | 1.0606 | 1.0944 | -120.8261
1458.5 | 121.7194 | -1.0849 | 120.7214 | 1.4211e-13 | -0.036829 | 0.0022863 | 0.064286 | -0.0080317 | 0.052683 | -0.0099192 | -0.0048667 | -0.0010577 | 0.020895 | 0.026211 | 0.017141 | -0.92836 | 0.12045 | -0.99732 | 120.8025 | 120.6825 | 120.5684 | -0.96053 | 0.019362 | 0.078197 | -0.056351 | -0.075739 | 0.009128 | 0.053537 | -0.10462 | 0.12437 | 0.081093 | 0.15653 | 0.087582 | -0.036792 | -0.038942 | -0.15307 | 0.98028 | -120.7972 | 1.1043 | 1.0285 | 0.048273 | -120.7123 | -120.6679 | 121.8874 | 121.7674 | 121.6533 | 1.2053 | -121.682 | 1.0092 | 1.094 | 1.1384 | 1.1631 | -120.8261
1460.2656 | 121.8201 | -1.0254 | 120.7123 | 1.4211e-13 | -0.036829 | 0.0022863 | 0.064073 | -0.0078179 | 0.052256 | -0.0022892 | -0.0046531 | -0.0010577 | 0.020895 | 0.026425 | 0.017355 | -0.92379 | 0.12503 | -0.99274 | 120.8025 | 120.6779 | 120.5638 | -0.95137 | 0.019362 | 0.082776 | -0.065509 | -0.071161 | 0.013707 | 0.058115 | -0.10004 | 0.074022 | 0.090249 | 0.1016 | 0.032651 | -0.041371 | -0.034365 | -0.14849 | 0.92535 | -120.7834 | 1.0448 | 0.95988 | 0.034536 | -120.6986 | -120.6542 | 121.8279 | 121.7033 | 121.5892 | 1.1504 | -121.6636 | 0.95423 | 1.0391 | 1.0835 | 1.1082 | -120.8123
1461.9688 | 121.8521 | -1.03 | 120.6985 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.064073 | -0.0082453 | 0.052042 | -0.0099192 | -0.0046531 | -0.0014849 | 0.021108 | 0.026211 | 0.017355 | -1.0016 | 0.12503 | -1.0797 | 120.711 | 120.6001 | 120.4951 | -1.0384 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.009128 | 0.062694 | -0.10004 | -0.0084 | 0.012414 | 0.028349 | -0.049759 | -0.041359 | -0.098473 | -0.20343 | 0.92992 | -120.7697 | 1.0539 | 0.97362 | 0.043694 | -120.6894 | -120.6359 | 121.7409 | 121.63 | 121.5251 | 1.155 | -121.7369 | 0.95881 | 1.0391 | 1.0927 | 1.1173 | -120.7986
1463.7344 | 121.788 | -1.0437 | 120.7443 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.063859 | -0.0078179 | 0.052256 | -0.0022892 | -0.0048667 | -0.0010577 | 0.020895 | 0.026639 | 0.017569 | -0.93752 | 0.11587 | -1.0019 | 120.7934 | 120.6733 | 120.5592 | -0.96968 | 0.019362 | 0.087354 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.10004 | 0.074017 | 0.049048 | 0.10618 | 0.041805 | -0.032212 | -0.070988 | -0.18511 | 0.94366 | -120.8201 | 1.0631 | 0.98277 | 0.039115 | -120.7306 | -120.6862 | 121.8371 | 121.717 | 121.6029 | 1.1596 | -121.714 | 0.96796 | 1.0574 | 1.1018 | 1.1311 | -120.8444
1465.4844 | 121.7697 | -1.0757 | 120.726 | 1.4211e-13 | -0.036615 | 0.0020727 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0046531 | -0.0010577 | 0.021108 | 0.026211 | 0.017355 | -0.92379 | 0.12045 | -0.99274 | 120.7934 | 120.6871 | 120.5684 | -0.96053 | 0.014784 | 0.078197 | -0.056351 | -0.071161 | 0.013707 | 0.053537 | -0.10462 | 0.11522 | 0.067359 | 0.15196 | 0.083005 | -0.032214 | -0.03894 | -0.15764 | 0.97112 | -120.7972 | 1.0905 | 1.0194 | 0.048273 | -120.7123 | -120.6725 | 121.8691 | 121.7628 | 121.6441 | 1.1962 | -121.6865 | 1.0046 | 1.0895 | 1.1293 | 1.1539 | -120.8306
1467.1875 | 121.8521 | -1.0712 | 120.6528 | 1.4211e-13 | -0.036829 | 0.0016453 | 0.064073 | -0.0080317 | 0.052683 | -0.01755 | -0.0046531 | -0.0014849 | 0.021108 | 0.026639 | 0.017355 | -0.98331 | 0.12045 | -1.0568 | 120.7384 | 120.6275 | 120.5088 | -1.0155 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.013707 | 0.053537 | -0.10462 | 0.055693 | 0.085661 | 0.087861 | 0.014331 | -0.041362 | -0.025224 | -0.14392 | 0.96654 | -120.7285 | 1.0951 | 1.0057 | 0.039115 | -120.6391 | -120.5992 | 121.8096 | 121.6987 | 121.58 | 1.1916 | -121.6682 | 0.99543 | 1.0849 | 1.1247 | 1.1539 | -120.7574
1468.9531 | 121.8155 | -1.1078 | 120.6528 | 1.4211e-13 | -0.036829 | 0.0020727 | 0.064286 | -0.0082453 | 0.052256 | -0.0099192 | -0.0048667 | -0.0014849 | 0.021108 | 0.026639 | 0.017141 | -1.0016 | 0.11587 | -1.0797 | 120.7201 | 120.6138 | 120.4951 | -1.0429 | 0.019362 | 0.091933 | -0.06093 | -0.066582 | 0.009128 | 0.053537 | -0.095467 | 0.064841 | 0.067347 | 0.10617 | 0.028061 | -0.03678 | -0.038961 | -0.15766 | 1.0123 | -120.7194 | 1.1272 | 1.0469 | 0.034537 | -120.6436 | -120.5992 | 121.8279 | 121.7216 | 121.6029 | 1.2237 | -121.6957 | 1.0412 | 1.1169 | 1.1613 | 1.1997 | -120.7482
1470.7188 | 121.8338 | -1.0574 | 120.6802 | 1.4211e-13 | -0.036829 | 0.0016453 | 0.064286 | -0.0084589 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020895 | 0.026425 | 0.017141 | -0.96499 | 0.11587 | -1.0385 | 120.7613 | 120.6504 | 120.5363 | -1.0017 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.055697 | 0.081087 | 0.092442 | 0.018911 | -0.036786 | -0.029795 | -0.14392 | 0.95281 | -120.756 | 1.0768 | 0.9965 | 0.043694 | -120.6711 | -120.6221 | 121.8188 | 121.7079 | 121.5938 | 1.1733 | -121.682 | 0.98169 | 1.0666 | 1.1155 | 1.1402 | -120.7849
1472.4219 | 121.8567 | -1.0941 | 120.639 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.063859 | -0.0084589 | 0.052256 | -0.0099192 | -0.0048667 | -0.0010577 | 0.021108 | 0.026211 | 0.017141 | -0.99246 | 0.12045 | -1.0614 | 120.7476 | 120.6275 | 120.518 | -1.0246 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.013707 | 0.053537 | -0.10004 | 0.069424 | 0.10855 | 0.10159 | 0.032641 | -0.036783 | -0.011491 | -0.12103 | 0.99401 | -120.7102 | 1.118 | 1.0285 | 0.034536 | -120.6253 | -120.5855 | 121.8416 | 121.7216 | 121.6121 | 1.2145 | -121.6637 | 1.0229 | 1.1078 | 1.1476 | 1.1768 | -120.7391
1474.1875 | 121.756 | -1.1765 | 120.6345 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0080317 | 0.052683 | -0.0099192 | -0.0046531 | -0.0014849 | 0.020895 | 0.026425 | 0.017141 | -1.0337 | 0.12045 | -1.1072 | 120.6972 | 120.5818 | 120.4676 | -1.075 | 0.023941 | 0.087354 | -0.056351 | -0.080318 | 0.009128 | 0.062694 | -0.10462 | 0.10145 | 0.062766 | 0.14278 | 0.069256 | -0.032197 | -0.052702 | -0.16682 | 1.0718 | -120.7148 | 1.2004 | 1.1201 | 0.048273 | -120.6253 | -120.5718 | 121.8737 | 121.7582 | 121.6441 | 1.2969 | -121.7095 | 1.0961 | 1.1856 | 1.2391 | 1.2638 | -120.7391
1475.9375 | 121.8063 | -1.1536 | 120.6207 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064073 | -0.0080317 | 0.052683 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020895 | 0.026639 | 0.017355 | -1.0382 | 0.11587 | -1.1164 | 120.6926 | 120.5772 | 120.4585 | -1.0796 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.022864 | 0.058115 | -0.10004 | 0.073985 | 0.07192 | 0.11532 | 0.037211 | -0.036774 | -0.043549 | -0.16224 | 1.0535 | -120.6919 | 1.1821 | 1.0926 | 0.039115 | -120.5979 | -120.5626 | 121.8462 | 121.7307 | 121.612 | 1.2694 | -121.7003 | 1.0824 | 1.1764 | 1.2117 | 1.2363 | -120.7208
1477.625 | 121.7651 | -1.1581 | 120.6299 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.064286 | -0.0082453 | 0.052469 | -0.01755 | -0.0048667 | -0.0010577 | 0.020895 | 0.026639 | 0.017355 | -1.0337 | 0.12045 | -1.1118 | 120.6972 | 120.5818 | 120.4722 | -1.0796 | 0.014784 | 0.082776 | -0.06093 | -0.071161 | 0.009128 | 0.053537 | -0.1092 | 0.078563 | 0.067343 | 0.12447 | 0.046367 | -0.032196 | -0.048125 | -0.15766 | 1.0489 | -120.701 | 1.1729 | 1.0972 | 0.048273 | -120.6208 | -120.5763 | 121.8554 | 121.7399 | 121.6304 | 1.2786 | -121.7095 | 1.087 | 1.1673 | 1.2117 | 1.2409 | -120.7391
1479.3906 | 121.8338 | -1.1673 | 120.5933 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.063859 | -0.0084589 | 0.052469 | -0.0022892 | -0.0046531 | -0.0010577 | 0.020895 | 0.026639 | 0.017141 | -1.0657 | 0.11587 | -1.1347 | 120.6698 | 120.5543 | 120.4447 | -1.1025 | 0.02852 | 0.087354 | -0.06093 | -0.075739 | 0.009128 | 0.062694 | -0.11378 | 0.064824 | 0.076494 | 0.10158 | 0.032631 | -0.032193 | -0.038978 | -0.14851 | 1.0535 | -120.669 | 1.1958 | 1.1064 | 0.052852 | -120.5841 | -120.5306 | 121.8371 | 121.7216 | 121.612 | 1.2832 | -121.6957 | 1.0916 | 1.1764 | 1.23 | 1.2547 | -120.707
1481.0938 | 121.8063 | -1.1581 | 120.607 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064286 | -0.0082453 | 0.052469 | -0.0022892 | -0.0044395 | -0.0010577 | 0.020895 | 0.026639 | 0.017141 | -1.0795 | 0.12045 | -1.153 | 120.656 | 120.5314 | 120.431 | -1.1254 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.018285 | 0.067272 | -0.10462 | 0.032774 | 0.049026 | 0.07869 | 0.005162 | -0.027612 | -0.075605 | -0.17598 | 1.0535 | -120.6782 | 1.1821 | 1.1018 | 0.048273 | -120.5887 | -120.5397 | 121.8142 | 121.6895 | 121.5892 | 1.2786 | -121.7324 | 1.087 | 1.1764 | 1.2254 | 1.2409 | -120.7116
1482.8594 | 121.8246 | -1.2634 | 120.4971 | 1.4211e-13 | -0.036829 | 0.0016453 | 0.064286 | -0.0080317 | 0.052469 | -0.0022892 | -0.0048667 | -0.0014849 | 0.020895 | 0.026425 | 0.017355 | -1.1527 | 0.11587 | -1.2262 | 120.5873 | 120.4627 | 120.3623 | -1.1895 | 0.023941 | 0.082776 | -0.074666 | -0.071161 | 0.018285 | 0.058115 | -0.10462 | 0.073955 | 0.090214 | 0.11072 | 0.037196 | -0.036759 | -0.034425 | -0.1348 | 1.1588 | -120.5683 | 1.2874 | 1.1888 | 0.029958 | -120.4788 | -120.439 | 121.8508 | 121.7261 | 121.6258 | 1.3793 | -121.6866 | 1.1923 | 1.2817 | 1.3215 | 1.3462 | -120.6018
1484.625 | 121.8018 | -1.2817 | 120.5246 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.063645 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020895 | 0.026211 | 0.017355 | -1.1527 | 0.11129 | -1.2262 | 120.5919 | 120.4719 | 120.3623 | -1.1849 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.10462 | 0.096844 | 0.067326 | 0.12903 | 0.055506 | -0.041338 | -0.052733 | -0.16227 | 1.1771 | -120.6003 | 1.3057 | 1.2208 | 0.043694 | -120.5109 | -120.4665 | 121.8737 | 121.7536 | 121.6441 | 1.393 | -121.7095 | 1.206 | 1.2954 | 1.3399 | 1.3691 | -120.6292
1486.3281 | 121.8933 | -1.2634 | 120.4834 | 1.4211e-13 | -0.037042 | 0.0020727 | 0.064286 | -0.0078179 | 0.052683 | -0.0022892 | -0.0048667 | -0.0012713 | 0.021108 | 0.026425 | 0.016928 | -1.1344 | 0.12045 | -1.2079 | 120.6057 | 120.4856 | 120.3944 | -1.162 | 0.014784 | 0.087354 | -0.06093 | -0.071161 | 0.009128 | 0.058115 | -0.10004 | 0.10143 | 0.12226 | 0.12904 | 0.055509 | -0.04592 | 0.002202 | -0.089015 | 1.1634 | -120.5546 | 1.2782 | 1.2025 | 0.039115 | -120.4743 | -120.4253 | 121.8691 | 121.749 | 121.6578 | 1.3839 | -121.6454 | 1.1923 | 1.2726 | 1.3215 | 1.3508 | -120.5834
1488.0781 | 121.875 | -1.2863 | 120.4742 | 1.4211e-13 | -0.037042 | 0.0020727 | 0.064286 | -0.0082453 | 0.052256 | 0.0053413 | -0.0046531 | -0.0014849 | 0.020895 | 0.026639 | 0.017355 | -1.1985 | 0.12045 | -1.2629 | 120.5416 | 120.4261 | 120.3165 | -1.2353 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.013707 | 0.062694 | -0.1092 | 0.051054 | 0.067318 | 0.087826 | 0.023458 | -0.027596 | -0.048169 | -0.1577 | 1.1771 | -120.55 | 1.3057 | 1.2254 | 0.048273 | -120.4605 | -120.4115 | 121.8279 | 121.7124 | 121.6029 | 1.4068 | -121.7095 | 1.2106 | 1.3 | 1.349 | 1.3691 | -120.5834
1489.8438 | 121.9025 | -1.268 | 120.4788 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.064073 | -0.0086727 | 0.052042 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020895 | 0.026425 | 0.016928 | -1.1939 | 0.11587 | -1.272 | 120.5507 | 120.4261 | 120.3211 | -1.2307 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.022864 | 0.058115 | -0.10462 | 0.037322 | 0.071897 | 0.074093 | -0.00401 | -0.041332 | -0.052747 | -0.1577 | 1.1634 | -120.5454 | 1.2919 | 1.2071 | 0.043694 | -120.456 | -120.4207 | 121.8187 | 121.6941 | 121.5891 | 1.3839 | -121.7095 | 1.2014 | 1.2909 | 1.3261 | 1.3554 | -120.5834
1491.5469 | 121.8155 | -1.3321 | 120.4834 | 1.4211e-13 | -0.036829 | 0.0018589 | 0.064073 | -0.0080317 | 0.052683 | -0.0099192 | -0.0048667 | -0.0012713 | 0.021322 | 0.026639 | 0.017569 | -1.2076 | 0.12045 | -1.2903 | 120.5324 | 120.4215 | 120.312 | -1.2444 | 0.014784 | 0.082776 | -0.06093 | -0.071161 | 0.013707 | 0.058115 | -0.10004 | 0.087672 | 0.049006 | 0.12445 | 0.041764 | -0.045908 | -0.061903 | -0.17143 | 1.232 | -120.5546 | 1.3469 | 1.2712 | 0.039115 | -120.4697 | -120.4253 | 121.8645 | 121.7536 | 121.6441 | 1.4525 | -121.7278 | 1.2609 | 1.3458 | 1.3902 | 1.4149 | -120.5834
1493.3125 | 121.7651 | -1.3824 | 120.4468 | 1.4211e-13 | -0.037042 | 0.0018589 | 0.064286 | -0.0080317 | 0.052256 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020681 | 0.026425 | 0.016928 | -1.2168 | 0.11587 | -1.2949 | 120.5278 | 120.4032 | 120.2937 | -1.2582 | 0.019362 | 0.082776 | -0.056351 | -0.075739 | 0.004549 | 0.058115 | -0.10462 | 0.12429 | 0.081049 | 0.16564 | 0.08754 | -0.036749 | -0.043597 | -0.15312 | 1.2778 | -120.5225 | 1.4018 | 1.3261 | 0.048273 | -120.4422 | -120.3887 | 121.9103 | 121.7856 | 121.6761 | 1.4983 | -121.7049 | 1.3067 | 1.387 | 1.4406 | 1.4652 | -120.5514
1495.0781 | 121.756 | -1.3687 | 120.4651 | 1.4211e-13 | -0.037042 | 0.0020727 | 0.063859 | -0.0084589 | 0.052256 | 0.0053413 | -0.0048667 | -0.0010577 | 0.020895 | 0.026425 | 0.017141 | -1.2305 | 0.12503 | -1.2995 | 120.5187 | 120.3986 | 120.2937 | -1.2627 | 0.023941 | 0.078197 | -0.056351 | -0.075739 | 0.013707 | 0.062694 | -0.10004 | 0.10598 | 0.053581 | 0.13817 | 0.069229 | -0.036748 | -0.066487 | -0.17143 | 1.2687 | -120.5408 | 1.3927 | 1.3124 | 0.043694 | -120.4514 | -120.4024 | 121.8874 | 121.7673 | 121.6624 | 1.4937 | -121.7278 | 1.293 | 1.3824 | 1.4314 | 1.4469 | -120.5651
1496.7812 | 121.8155 | -1.355 | 120.4605 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.064073 | -0.0084589 | 0.052256 | -0.0099192 | -0.0050803 | -0.0010577 | 0.020467 | 0.026639 | 0.017355 | -1.2122 | 0.11587 | -1.2995 | 120.5232 | 120.4032 | 120.3028 | -1.2582 | 0.02852 | 0.091933 | -0.06093 | -0.071161 | 0.013707 | 0.053537 | -0.10004 | 0.096823 | 0.062737 | 0.14275 | 0.055496 | -0.041327 | -0.05733 | -0.1577 | 1.2549 | -120.5317 | 1.3835 | 1.2941 | 0.039115 | -120.4468 | -120.407 | 121.8782 | 121.7582 | 121.6578 | 1.4709 | -121.7187 | 1.2838 | 1.3687 | 1.4085 | 1.4469 | -120.5606
1498.5469 | 121.8887 | -1.3046 | 120.433 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064073 | -0.0080317 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020467 | 0.026639 | 0.017355 | -1.2122 | 0.12045 | -1.3086 | 120.5232 | 120.4078 | 120.2982 | -1.2582 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.046469 | 0.090203 | 0.092401 | -0.004015 | -0.050484 | -0.025285 | -0.13481 | 1.2046 | -120.5088 | 1.3286 | 1.2437 | 0.039115 | -120.4239 | -120.3749 | 121.8279 | 121.7124 | 121.6029 | 1.4251 | -121.6912 | 1.2289 | 1.3138 | 1.3627 | 1.392 | -120.5331
1500.2344 | 121.8796 | -1.2451 | 120.52 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0080317 | 0.052469 | -0.01755 | -0.0046531 | -0.0012713 | 0.021108 | 0.026425 | 0.016928 | -1.1573 | 0.12503 | -1.2308 | 120.5873 | 120.4627 | 120.3669 | -1.1941 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.051065 | 0.067325 | 0.087832 | 0.014307 | -0.036758 | -0.057314 | -0.15311 | 1.1451 | -120.6049 | 1.2691 | 1.1842 | 0.039115 | -120.5063 | -120.4665 | 121.8325 | 121.7078 | 121.612 | 1.3701 | -121.7141 | 1.1602 | 1.2588 | 1.2987 | 1.3279 | -120.6201
1502 | 121.7697 | -1.3275 | 120.5109 | 1.4211e-13 | -0.036829 | 0.0022863 | 0.064073 | -0.0080317 | 0.052469 | -0.0099192 | -0.0048667 | -0.0012713 | 0.020895 | 0.026639 | 0.017141 | -1.1802 | 0.12503 | -1.2491 | 120.569 | 120.449 | 120.3486 | -1.2261 | 0.02852 | 0.082776 | -0.051772 | -0.071161 | 0.018285 | 0.048958 | -0.10462 | 0.10141 | 0.058167 | 0.14734 | 0.078392 | -0.023019 | -0.061895 | -0.16227 | 1.2229 | -120.582 | 1.356 | 1.2757 | 0.052852 | -120.4926 | -120.4619 | 121.8965 | 121.7765 | 121.6761 | 1.4525 | -121.737 | 1.2564 | 1.3458 | 1.3765 | 1.4103 | -120.6155
1503.7812 | 121.756 | -1.3458 | 120.4834 | 1.4211e-13 | -0.036829 | 0.0020727 | 0.064073 | -0.0080317 | 0.052469 | -0.01755 | -0.0048667 | -0.0012713 | 0.020895 | 0.026639 | 0.017141 | -1.2214 | 0.12045 | -1.2949 | 120.5416 | 120.4169 | 120.3165 | -1.2536 | 0.019362 | 0.082776 | -0.056351 | -0.071161 | 0.013707 | 0.053537 | -0.1092 | 0.092247 | 0.058163 | 0.12444 | 0.050919 | -0.041328 | -0.066481 | -0.16685 | 1.2366 | -120.5546 | 1.3652 | 1.2895 | 0.052852 | -120.4697 | -120.4299 | 121.8874 | 121.7627 | 121.6624 | 1.4663 | -121.737 | 1.2747 | 1.3595 | 1.3994 | 1.4286 | -120.5926
1505.4844 | 121.7834 | -1.3412 | 120.4742 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0099192 | -0.0048667 | -0.0014849 | 0.021108 | 0.026639 | 0.016928 | -1.2168 | 0.11587 | -1.2857 | 120.5416 | 120.4261 | 120.312 | -1.249 | 0.019362 | 0.082776 | -0.051772 | -0.071161 | 0.013707 | 0.058115 | -0.10004 | 0.092249 | 0.067318 | 0.12444 | 0.055498 | -0.036751 | -0.048169 | -0.16228 | 1.2412 | -120.5454 | 1.3606 | 1.2895 | 0.048273 | -120.4605 | -120.4161 | 121.8828 | 121.7673 | 121.6532 | 1.4571 | -121.7232 | 1.2701 | 1.355 | 1.3994 | 1.424 | -120.5743
1507.25 | 121.7789 | -1.3641 | 120.4605 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.063859 | -0.0080317 | 0.052683 | -0.0022892 | -0.0048667 | -0.0012713 | 0.020895 | 0.026425 | 0.016928 | -1.2168 | 0.12961 | -1.2949 | 120.5278 | 120.4123 | 120.3074 | -1.2582 | 0.019362 | 0.087354 | -0.065509 | -0.071161 | 0.018285 | 0.058115 | -0.1092 | 0.10598 | 0.067316 | 0.14733 | 0.06923 | -0.036749 | -0.048172 | -0.15312 | 1.2549 | -120.5317 | 1.3835 | 1.2986 | 0.043694 | -120.4422 | -120.4024 | 121.892 | 121.7765 | 121.6715 | 1.4937 | -121.7187 | 1.293 | 1.3824 | 1.4223 | 1.4515 | -120.5697
1509.0156 | 121.8658 | -1.3092 | 120.4559 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.064286 | -0.0082453 | 0.052683 | -0.0022892 | -0.0048667 | -0.0010577 | 0.020681 | 0.026639 | 0.017141 | -1.2076 | 0.12503 | -1.2857 | 120.5507 | 120.4398 | 120.3257 | -1.2353 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.013707 | 0.053537 | -0.10462 | 0.073942 | 0.094785 | 0.10156 | 0.023454 | -0.050488 | -0.016122 | -0.13023 | 1.2046 | -120.5225 | 1.3377 | 1.2483 | 0.043694 | -120.4422 | -120.4024 | 121.8599 | 121.749 | 121.6349 | 1.4342 | -121.6912 | 1.2426 | 1.3229 | 1.3627 | 1.3966 | -120.5606
1510.7031 | 121.8521 | -1.3092 | 120.4788 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | 0.0053413 | -0.0046531 | -0.0014849 | 0.020681 | 0.026852 | 0.017141 | -1.1985 | 0.12045 | -1.272 | 120.5599 | 120.4398 | 120.3394 | -1.2307 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.018285 | 0.058115 | -0.10004 | 0.078521 | 0.081054 | 0.11071 | 0.037189 | -0.041332 | -0.03901 | -0.13938 | 1.2092 | -120.5546 | 1.3331 | 1.2483 | 0.039115 | -120.4605 | -120.4207 | 121.8691 | 121.749 | 121.6486 | 1.4297 | -121.7095 | 1.2335 | 1.3275 | 1.3673 | 1.392 | -120.5789
1512.4688 | 121.7606 | -1.3046 | 120.5612 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0084589 | 0.052469 | -0.0099192 | -0.0046531 | -0.0016987 | 0.020895 | 0.026425 | 0.017141 | -1.1756 | 0.12045 | -1.2537 | 120.5782 | 120.4764 | 120.3578 | -1.2169 | 0.023941 | 0.087354 | -0.065509 | -0.080318 | 0.013707 | 0.053537 | -0.095467 | 0.08768 | 0.01697 | 0.12903 | 0.050924 | -0.036756 | -0.084775 | -0.20346 | 1.2092 | -120.6415 | 1.3286 | 1.2391 | 0.029958 | -120.5475 | -120.5077 | 121.8828 | 121.7811 | 121.6624 | 1.4251 | -121.7782 | 1.2243 | 1.3183 | 1.3582 | 1.392 | -120.6567
1514.2344 | 121.875 | -1.181 | 120.5795 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064286 | -0.0080317 | 0.052469 | -0.0022892 | -0.0048667 | -0.0014849 | 0.020681 | 0.026639 | 0.017141 | -1.1664 | 0.11587 | -1.24 | 120.5919 | 120.4856 | 120.3761 | -1.1941 | 0.014784 | 0.096512 | -0.06093 | -0.071161 | 0.009128 | 0.062694 | -0.10462 | -0.013022 | 0.012394 | 0.014589 | -0.058937 | -0.045915 | -0.093929 | -0.20346 | 1.0764 | -120.6507 | 1.1958 | 1.1201 | 0.043694 | -120.5704 | -120.5168 | 121.773 | 121.6666 | 121.5571 | 1.2969 | -121.7736 | 1.1099 | 1.1902 | 1.2437 | 1.2775 | -120.6842
1515.9844 | 121.8155 | -1.268 | 120.5429 | 1.4211e-13 | -0.037683 | 0.0016453 | 0.064286 | -0.0082453 | 0.052469 | -0.01755 | -0.0046531 | -0.0012713 | 0.020895 | 0.026425 | 0.0165 | -1.1527 | 0.12503 | -1.2262 | 120.6011 | 120.4902 | 120.3852 | -1.1941 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.009128 | 0.048958 | -0.095467 | 0.073953 | 0.058172 | 0.1153 | 0.041773 | -0.03218 | -0.052729 | -0.15768 | 1.1725 | -120.6141 | 1.2919 | 1.2117 | 0.039116 | -120.5338 | -120.4939 | 121.8691 | 121.7582 | 121.6532 | 1.393 | -121.737 | 1.1968 | 1.2771 | 1.317 | 1.3508 | -120.6384
1517.6719 | 121.8246 | -1.2863 | 120.5521 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.0645 | -0.0080317 | 0.052469 | -0.0022892 | -0.0048667 | -0.0010577 | 0.020681 | 0.026639 | 0.017141 | -1.1435 | 0.11587 | -1.2125 | 120.6102 | 120.5039 | 120.3898 | -1.1757 | 0.019362 | 0.082776 | -0.056351 | -0.071161 | 0.013707 | 0.062694 | -0.10462 | 0.11058 | 0.058174 | 0.14277 | 0.073819 | -0.036761 | -0.048147 | -0.16226 | 1.1817 | -120.6232 | 1.3057 | 1.23 | 0.048273 | -120.5384 | -120.4894 | 121.8966 | 121.7902 | 121.6761 | 1.4022 | -121.7278 | 1.2152 | 1.3 | 1.349 | 1.3691 | -120.6567
1519.4375 | 121.8063 | -1.2543 | 120.6116 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064286 | -0.0082453 | 0.052469 | -0.0099192 | -0.0046531 | -0.0014849 | 0.020467 | 0.026852 | 0.017141 | -1.1344 | 0.12503 | -1.2171 | 120.6286 | 120.5039 | 120.4035 | -1.1757 | 0.023941 | 0.087354 | -0.065509 | -0.080318 | 0.013707 | 0.067272 | -0.10462 | 0.078536 | 0.016978 | 0.11988 | 0.037197 | -0.041339 | -0.10766 | -0.20803 | 1.1496 | -120.6919 | 1.2782 | 1.1888 | 0.039115 | -120.5979 | -120.5443 | 121.8828 | 121.7582 | 121.6578 | 1.3793 | -121.7873 | 1.174 | 1.268 | 1.3215 | 1.3416 | -120.7162
1521.2031 | 121.8246 | -1.236 | 120.5795 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.064073 | -0.0082453 | 0.052256 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020895 | 0.026639 | 0.016928 | -1.0978 | 0.12961 | -1.1759 | 120.6652 | 120.5451 | 120.4493 | -1.1345 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.10144 | 0.085648 | 0.1382 | 0.060091 | -0.041345 | -0.034403 | -0.1302 | 1.1359 | -120.6553 | 1.2553 | 1.1796 | 0.043694 | -120.5704 | -120.5214 | 121.9011 | 121.7811 | 121.6853 | 1.3656 | -121.7141 | 1.1602 | 1.2451 | 1.2941 | 1.3233 | -120.6796
1522.8906 | 121.7972 | -1.0895 | 120.7764 | 1.4211e-13 | -0.03747 | 0.0020727 | 0.064286 | -0.0084589 | 0.052042 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020895 | 0.026852 | 0.016928 | -0.96499 | 0.12503 | -1.0477 | 120.798 | 120.6871 | 120.5821 | -1.0017 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.013707 | 0.053537 | -0.10462 | 0.087741 | 0.021584 | 0.12449 | 0.041799 | -0.045942 | -0.089294 | -0.19426 | 0.98485 | -120.8475 | 1.1134 | 1.0331 | 0.048273 | -120.7627 | -120.7228 | 121.8874 | 121.7766 | 121.6716 | 1.2145 | -121.7781 | 1.0183 | 1.1032 | 1.143 | 1.1723 | -120.881
1524.6562 | 121.8979 | -1.0483 | 120.7123 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064714 | -0.0082453 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020467 | 0.027066 | 0.016928 | -0.96041 | 0.12045 | -1.0385 | 120.8163 | 120.6962 | 120.6004 | -0.99716 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.009128 | 0.058115 | -0.095467 | 0.051121 | 0.10398 | 0.087865 | 0.009756 | -0.041365 | -0.016049 | -0.11186 | 0.95281 | -120.7834 | 1.0722 | 0.98277 | 0.029958 | -120.7032 | -120.6542 | 121.8645 | 121.7445 | 121.6487 | 1.1687 | -121.7094 | 0.97712 | 1.0574 | 1.1064 | 1.1311 | -120.8077
1526.3594 | 121.8658 | -1.0483 | 120.7535 | 1.4211e-13 | -0.037042 | 0.0016453 | 0.064073 | -0.0082453 | 0.052042 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020681 | 0.026852 | 0.017141 | -0.93752 | 0.12961 | -1.0111 | 120.8346 | 120.71 | 120.6142 | -0.97426 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.013707 | 0.058115 | -0.10462 | 0.074016 | 0.081099 | 0.11076 | 0.037226 | -0.03679 | -0.043511 | -0.13932 | 0.94365 | -120.8246 | 1.0722 | 0.98277 | 0.039115 | -120.7398 | -120.6954 | 121.8829 | 121.7582 | 121.6624 | 1.1779 | -121.7277 | 0.97712 | 1.062 | 1.1064 | 1.1356 | -120.8581
1528.1094 | 121.7697 | -1.0254 | 120.8221 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0084589 | 0.052256 | -0.01755 | -0.0044395 | -0.0014849 | 0.020467 | 0.026639 | 0.016928 | -0.89632 | 0.12503 | -0.97901 | 120.8712 | 120.7603 | 120.6554 | -0.9239 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.1015 | 0.049061 | 0.12907 | 0.046386 | -0.05511 | -0.061808 | -0.16678 | 0.92077 | -120.8979 | 1.0493 | 0.96446 | 0.043694 | -120.813 | -120.764 | 121.8966 | 121.7857 | 121.6808 | 1.1504 | -121.746 | 0.94965 | 1.0345 | 1.0835 | 1.1082 | -120.9268
1529.8125 | 121.8338 | -1.0391 | 120.7535 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.063859 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020681 | 0.026639 | 0.016928 | -0.92836 | 0.12961 | -1.0111 | 120.8437 | 120.7374 | 120.6279 | -0.9651 | 0.019362 | 0.087354 | -0.051772 | -0.075739 | 0.013707 | 0.058115 | -0.095467 | 0.074019 | 0.090256 | 0.11076 | 0.028071 | -0.045948 | -0.016038 | -0.12559 | 0.94366 | -120.8292 | 1.0585 | 0.98735 | 0.043695 | -120.7398 | -120.6954 | 121.8829 | 121.7766 | 121.667 | 1.1687 | -121.7186 | 0.96338 | 1.0528 | 1.0972 | 1.1265 | -120.8489
1531.5781 | 121.8842 | -1.0162 | 120.7718 | 1.4211e-13 | -0.037256 | 0.0016453 | 0.064073 | -0.0084589 | 0.052256 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020467 | 0.027066 | 0.016928 | -0.92379 | 0.12045 | -1.0019 | 120.8483 | 120.7329 | 120.637 | -0.96053 | 0.014784 | 0.082776 | -0.06093 | -0.080318 | 0.009128 | 0.062694 | -0.10004 | 0.055709 | 0.076523 | 0.092448 | 0.014339 | -0.04137 | -0.038928 | -0.13474 | 0.91619 | -120.8521 | 1.031 | 0.9553 | 0.039115 | -120.7627 | -120.7091 | 121.8645 | 121.7491 | 121.6533 | 1.1367 | -121.7323 | 0.93592 | 1.0254 | 1.0789 | 1.099 | -120.8718
1533.2656 | 121.875 | -1.0849 | 120.7077 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0084589 | 0.052256 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020467 | 0.026639 | 0.017141 | -0.96957 | 0.12045 | -1.0523 | 120.798 | 120.6825 | 120.5775 | -1.0063 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.009128 | 0.053537 | -0.1092 | 0.078584 | 0.090248 | 0.11533 | 0.032643 | -0.045941 | -0.025209 | -0.13018 | 0.9757 | -120.7834 | 1.1134 | 1.024 | 0.048273 | -120.6986 | -120.6542 | 121.8829 | 121.7674 | 121.6624 | 1.2053 | -121.714 | 1.0092 | 1.094 | 1.1384 | 1.1677 | -120.8169
1535.0156 | 121.9299 | -1.0757 | 120.7169 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0010577 | 0.020254 | 0.026852 | 0.016928 | -0.96499 | 0.12503 | -1.0568 | 120.798 | 120.6825 | 120.5958 | -1.0017 | 0.019362 | 0.073618 | -0.06093 | -0.071161 | 0.013707 | 0.058115 | -0.10004 | 0.074008 | 0.081093 | 0.11075 | 0.018909 | -0.055099 | -0.034364 | -0.12102 | 0.9757 | -120.788 | 1.0951 | 1.0148 | 0.039115 | -120.7032 | -120.6587 | 121.8737 | 121.7582 | 121.6716 | 1.2008 | -121.7186 | 1.0046 | 1.0895 | 1.1339 | 1.1494 | -120.8169
1536.7031 | 121.8292 | -1.0895 | 120.7581 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020681 | 0.026852 | 0.016928 | -0.96041 | 0.12045 | -1.0523 | 120.8071 | 120.6962 | 120.605 | -1.0017 | 0.019362 | 0.091933 | -0.051772 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.087741 | 0.049051 | 0.12906 | 0.037221 | -0.05052 | -0.061826 | -0.15306 | 0.98485 | -120.8338 | 1.1088 | 1.0377 | 0.052852 | -120.7489 | -120.6999 | 121.8966 | 121.7857 | 121.6945 | 1.2099 | -121.7598 | 1.0137 | 1.0986 | 1.1476 | 1.1814 | -120.8627
1538.4688 | 121.7789 | -1.0666 | 120.7718 | 1.4211e-13 | -0.037042 | 0.0014317 | 0.064073 | -0.0082453 | 0.052256 | -0.02518 | -0.0046531 | -0.0010577 | 0.020681 | 0.026852 | 0.017355 | -0.93294 | 0.12503 | -1.0111 | 120.8437 | 120.7283 | 120.6233 | -0.97884 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.009128 | 0.048958 | -0.095467 | 0.087747 | 0.071945 | 0.13365 | 0.055536 | -0.032211 | -0.043507 | -0.14848 | 0.97112 | -120.8475 | 1.086 | 1.0011 | 0.029958 | -120.7627 | -120.7228 | 121.9103 | 121.7949 | 121.6899 | 1.1916 | -121.7506 | 0.99085 | 1.0757 | 1.1155 | 1.1539 | -120.8673
1540.2344 | 121.8292 | -1.0208 | 120.813 | 1.4211e-13 | -0.037683 | 0.0016453 | 0.0645 | -0.0080317 | 0.052683 | -0.0099192 | -0.0046531 | -0.0010577 | 0.020467 | 0.026852 | 0.016928 | -0.9009 | 0.12045 | -0.97901 | 120.8804 | 120.7649 | 120.6691 | -0.92847 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.009128 | 0.053537 | -0.11378 | 0.092339 | 0.067374 | 0.11992 | 0.041808 | -0.050531 | -0.048073 | -0.14389 | 0.90703 | -120.8796 | 1.0402 | 0.9553 | 0.048273 | -120.8039 | -120.7595 | 121.9012 | 121.7857 | 121.6899 | 1.1413 | -121.7415 | 0.95423 | 1.0299 | 1.0743 | 1.1036 | -120.9268
1541.9219 | 121.9116 | -0.97961 | 120.8359 | 1.4211e-13 | -0.037256 | 0.0022863 | 0.064286 | -0.0082453 | 0.052256 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020681 | 0.026639 | 0.016928 | -0.86885 | 0.12503 | -0.95154 | 120.9033 | 120.7924 | 120.692 | -0.91016 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.004549 | 0.062694 | -0.10004 | 0.069456 | 0.067378 | 0.11077 | 0.028079 | -0.041377 | -0.043488 | -0.14388 | 0.87957 | -120.9116 | 1.0036 | 0.91868 | 0.039115 | -120.8313 | -120.7732 | 121.8829 | 121.772 | 121.6716 | 1.1046 | -121.746 | 0.90387 | 0.98416 | 1.0423 | 1.067 | -120.9359
1543.6719 | 121.907 | -0.9201 | 120.8725 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.063859 | -0.0084589 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020681 | 0.026425 | 0.016928 | -0.84138 | 0.12503 | -0.93322 | 120.9353 | 120.8153 | 120.7195 | -0.88726 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.009128 | 0.058115 | -0.095467 | 0.032841 | 0.062804 | 0.078729 | -0.013117 | -0.045958 | -0.057215 | -0.15303 | 0.82464 | -120.9482 | 0.93947 | 0.86375 | 0.039116 | -120.8634 | -120.8144 | 121.8554 | 121.7354 | 121.6396 | 1.0451 | -121.7598 | 0.84437 | 0.92923 | 0.97822 | 1.0075 | -120.968
1545.375 | 121.8018 | -0.98419 | 120.8633 | 1.4211e-13 | -0.037256 | 0.0018589 | 0.0645 | -0.0082453 | 0.052469 | -0.0099192 | -0.0046531 | -0.0010577 | 0.020467 | 0.026639 | 0.017141 | -0.84595 | 0.12503 | -0.92407 | 120.9261 | 120.8199 | 120.7195 | -0.87811 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.018285 | 0.058115 | -0.095467 | 0.10609 | 0.062804 | 0.13824 | 0.060127 | -0.045959 | -0.04348 | -0.14388 | 0.88872 | -120.9391 | 1.0081 | 0.92326 | 0.034537 | -120.8451 | -120.8052 | 121.9103 | 121.8041 | 121.7037 | 1.1092 | -121.7414 | 0.90845 | 1.0025 | 1.0423 | 1.067 | -120.9588
1547.125 | 121.8475 | -0.94299 | 120.8954 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020467 | 0.026639 | 0.016714 | -0.84138 | 0.11587 | -0.92407 | 120.9445 | 120.8382 | 120.7378 | -0.87811 | 0.019362 | 0.087354 | -0.056351 | -0.071161 | 0.013707 | 0.058115 | -0.10004 | 0.064887 | 0.049073 | 0.10162 | 0.018928 | -0.045959 | -0.057208 | -0.15761 | 0.84295 | -120.9665 | 0.96235 | 0.88664 | 0.043694 | -120.8817 | -120.8373 | 121.8875 | 121.7812 | 121.6808 | 1.0589 | -121.7735 | 0.87183 | 0.9567 | 1.0011 | 1.0303 | -120.9954
1548.8125 | 121.875 | -0.90179 | 120.8908 | 1.4211e-13 | -0.037683 | 0.0022863 | 0.064073 | -0.0082453 | 0.052042 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020681 | 0.026639 | 0.017141 | -0.80017 | 0.12045 | -0.8737 | 120.9857 | 120.8702 | 120.7698 | -0.84147 | 0.014784 | 0.082776 | -0.056351 | -0.075739 | 0.009128 | 0.048958 | -0.10462 | 0.06032 | 0.094857 | 0.10162 | 0.02809 | -0.03223 | -0.020578 | -0.12098 | 0.79717 | -120.9665 | 0.91658 | 0.84544 | 0.048273 | -120.8817 | -120.8419 | 121.8875 | 121.772 | 121.6716 | 1.0222 | -121.7323 | 0.82605 | 0.91092 | 0.95075 | 0.98457 | -120.9954
1550.5781 | 121.8384 | -0.87891 | 120.9869 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.064073 | -0.0084589 | 0.052469 | -0.0022892 | -0.0044395 | -0.0014849 | 0.020467 | 0.026639 | 0.016714 | -0.79101 | 0.12045 | -0.85997 | 120.9994 | 120.8885 | 120.7927 | -0.82774 | 0.019362 | 0.091933 | -0.065509 | -0.075739 | 0.022864 | 0.058115 | -0.10004 | 0.051168 | 0.012462 | 0.087892 | 0.018936 | -0.032232 | -0.098392 | -0.19422 | 0.77886 | -121.0627 | 0.89827 | 0.8134 | 0.034536 | -120.9641 | -120.9288 | 121.8783 | 121.7675 | 121.6716 | 0.99936 | -121.8147 | 0.80317 | 0.90177 | 0.93702 | 0.97084 | -121.087
1552.2656 | 121.7926 | -0.83771 | 121.0281 | 1.4211e-13 | -0.037256 | 0.0016453 | 0.064286 | -0.0082453 | 0.052256 | -0.0022892 | -0.0044395 | -0.0010577 | 0.020895 | 0.026425 | 0.017141 | -0.7315 | 0.12961 | -0.81419 | 121.0543 | 120.9435 | 120.8477 | -0.76821 | 0.023941 | 0.087354 | -0.065509 | -0.075739 | 0.018285 | 0.058115 | -0.10004 | 0.069496 | 0.026203 | 0.10621 | 0.023521 | -0.045975 | -0.084644 | -0.18047 | 0.73766 | -121.1039 | 0.86165 | 0.7722 | 0.034536 | -121.0099 | -120.97 | 121.892 | 121.7812 | 121.6854 | 0.96732 | -121.7963 | 0.76197 | 0.85599 | 0.89582 | 0.92506 | -121.1282
1554.0312 | 121.9254 | -0.77362 | 121.0373 | 1.4211e-13 | -0.03747 | 0.0016453 | 0.064286 | -0.0082453 | 0.052256 | -0.01755 | -0.0044395 | -0.0014849 | 0.020681 | 0.027066 | 0.016928 | -0.6674 | 0.12045 | -0.74093 | 121.1322 | 121.0076 | 120.9163 | -0.69953 | 0.019362 | 0.082776 | -0.065509 | -0.071161 | 0.018285 | 0.058115 | -0.10004 | 0.074093 | 0.094881 | 0.10622 | 0.032687 | -0.041406 | -0.029694 | -0.12095 | 0.67358 | -121.1085 | 0.79298 | 0.70811 | 0.034536 | -121.019 | -120.9792 | 121.9058 | 121.7812 | 121.69 | 0.89407 | -121.7368 | 0.70246 | 0.79191 | 0.83174 | 0.8564 | -121.1373
1555.7812 | 121.8842 | -0.76446 | 121.0648 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.063645 | -0.0082453 | 0.052469 | -0.0022892 | -0.0044395 | -0.00084406 | 0.020254 | 0.026852 | 0.017141 | -0.68113 | 0.12503 | -0.74551 | 121.1139 | 121.003 | 120.9118 | -0.70869 | 0.023941 | 0.087354 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.10004 | 0.055779 | 0.049102 | 0.083333 | 0.018952 | -0.036827 | -0.061739 | -0.15299 | 0.66442 | -121.1405 | 0.78841 | 0.70811 | 0.043694 | -121.0511 | -121.0066 | 121.8783 | 121.7675 | 121.6762 | 0.88949 | -121.7734 | 0.68873 | 0.77817 | 0.82258 | 0.85182 | -121.1648
1557.5312 | 121.9254 | -0.70953 | 121.0831 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.064286 | -0.0084589 | 0.052256 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020467 | 0.026639 | 0.016928 | -0.63993 | 0.12503 | -0.70431 | 121.1551 | 121.0488 | 120.9484 | -0.67663 | 0.023941 | 0.091933 | -0.056351 | -0.075739 | 0.018285 | 0.053537 | -0.10004 | 0.032901 | 0.071996 | 0.069607 | 0.005226 | -0.027675 | -0.034261 | -0.13468 | 0.60949 | -121.1588 | 0.73347 | 0.65318 | 0.043694 | -121.0648 | -121.0295 | 121.8646 | 121.7583 | 121.6579 | 0.83456 | -121.7597 | 0.63379 | 0.72782 | 0.76307 | 0.80147 | -121.1831
1559.2969 | 121.9345 | -0.72784 | 121.0648 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020467 | 0.026639 | 0.016928 | -0.64908 | 0.12503 | -0.72262 | 121.1505 | 121.0305 | 120.9392 | -0.69037 | 0.019362 | 0.091933 | -0.065509 | -0.066582 | 0.009128 | 0.058115 | -0.10004 | 0.037474 | 0.085729 | 0.07876 | 0.005223 | -0.032251 | -0.034266 | -0.12552 | 0.6278 | -121.1313 | 0.74721 | 0.66234 | 0.034536 | -121.0556 | -121.0066 | 121.8783 | 121.7583 | 121.6671 | 0.85287 | -121.7551 | 0.66126 | 0.73697 | 0.78596 | 0.81978 | -121.1648
1561.0625 | 121.8979 | -0.73242 | 121.0693 | 1.4211e-13 | -0.037683 | 0.0020727 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.02728 | 0.016928 | -0.65824 | 0.12961 | -0.7272 | 121.1368 | 121.0351 | 120.9392 | -0.68121 | 0.014784 | 0.082776 | -0.056351 | -0.071161 | 0.009128 | 0.058115 | -0.1092 | 0.05121 | 0.067415 | 0.074182 | 0.005223 | -0.045987 | -0.034265 | -0.1301 | 0.62322 | -121.1405 | 0.74721 | 0.67607 | 0.052852 | -121.0602 | -121.0112 | 121.8692 | 121.7675 | 121.6717 | 0.86203 | -121.7505 | 0.66126 | 0.74155 | 0.79054 | 0.8152 | -121.1785
1562.8438 | 121.9299 | -0.81482 | 120.9778 | 1.4211e-13 | -0.037256 | 0.0020727 | 0.064286 | -0.0082453 | 0.052256 | -0.0022892 | -0.0044395 | -0.0014849 | 0.020895 | 0.026639 | 0.016928 | -0.69945 | 0.12503 | -0.78214 | 121.0864 | 120.9847 | 120.8797 | -0.7499 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.009128 | 0.048958 | -0.10462 | 0.064923 | 0.10861 | 0.11537 | 0.03268 | -0.032243 | 0.00692 | -0.098069 | 0.71019 | -121.0581 | 0.84334 | 0.75847 | 0.048273 | -120.9687 | -120.9288 | 121.9012 | 121.7995 | 121.6945 | 0.93985 | -121.7277 | 0.7345 | 0.82395 | 0.86378 | 0.89759 | -121.0824
1564.5469 | 121.7972 | -0.86975 | 120.9869 | 1.4211e-13 | -0.03747 | 0.0018589 | 0.064073 | -0.0082453 | 0.052042 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020467 | 0.02728 | 0.016714 | -0.74065 | 0.12503 | -0.81876 | 121.0498 | 120.9343 | 120.8522 | -0.77737 | 0.02852 | 0.082776 | -0.065509 | -0.080318 | 0.009128 | 0.058115 | -0.10462 | 0.092381 | 0.062824 | 0.1291 | 0.050986 | -0.041395 | -0.052603 | -0.13469 | 0.76513 | -121.0673 | 0.89827 | 0.80424 | 0.039115 | -120.9778 | -120.9288 | 121.9195 | 121.8041 | 121.722 | 0.99478 | -121.7643 | 0.78943 | 0.87888 | 0.92787 | 0.95253 | -121.0916
1566.2969 | 121.7926 | -1.1261 | 120.7535 | 1.4211e-13 | -0.03747 | 0.0016453 | 0.0645 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020254 | 0.026639 | 0.017141 | -0.91463 | 0.12503 | -0.99732 | 120.8849 | 120.7649 | 120.6783 | -0.95137 | 0.023941 | 0.087354 | -0.065509 | -0.075739 | 0.018285 | 0.058115 | -0.10462 | 0.17473 | 0.13146 | 0.21147 | 0.12878 | -0.045949 | 0.011436 | -0.075223 | 1.0215 | -120.8292 | 1.15 | 1.0606 | 0.039115 | -120.7352 | -120.6954 | 122.011 | 121.891 | 121.8044 | 1.2511 | -121.7048 | 1.0504 | 1.1444 | 1.1842 | 1.2135 | -120.8581
1568.0469 | 121.8475 | -0.99335 | 120.8633 | 1.4211e-13 | -0.03747 | 0.0020727 | 0.064073 | -0.0084589 | 0.052683 | -0.0099192 | -0.0044395 | -0.0016987 | 0.020681 | 0.026639 | 0.017141 | -0.89174 | 0.12045 | -0.96985 | 120.9033 | 120.797 | 120.7057 | -0.9239 | 0.019362 | 0.087354 | -0.06093 | -0.075739 | 0.009128 | 0.067272 | -0.10004 | 0.069452 | 0.039912 | 0.10161 | 0.023499 | -0.045953 | -0.066375 | -0.15762 | 0.8933 | -120.9391 | 1.0127 | 0.93242 | 0.039115 | -120.8542 | -120.7961 | 121.8966 | 121.7903 | 121.6991 | 1.1138 | -121.7872 | 0.91761 | 1.0025 | 1.0606 | 1.0807 | -120.9634
1569.8125 | 121.8201 | -0.99792 | 120.8725 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064073 | -0.0084589 | 0.052469 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020467 | 0.026639 | 0.016928 | -0.878 | 0.12503 | -0.96069 | 120.9216 | 120.8199 | 120.7195 | -0.91474 | 0.023941 | 0.078197 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.095467 | 0.083188 | 0.049069 | 0.11992 | 0.037233 | -0.045955 | -0.052636 | -0.15303 | 0.90246 | -120.9482 | 1.0219 | 0.94157 | 0.039116 | -120.8588 | -120.8144 | 121.9195 | 121.8178 | 121.7174 | 1.123 | -121.7872 | 0.92219 | 1.0116 | 1.056 | 1.0761 | -120.968
1571.5 | 121.9299 | -0.93384 | 120.8588 | 1.4211e-13 | -0.037256 | 0.0022863 | 0.064286 | -0.0082453 | 0.052256 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020467 | 0.026852 | 0.016928 | -0.84138 | 0.12961 | -0.91491 | 120.9628 | 120.8428 | 120.7561 | -0.87811 | 0.023941 | 0.073618 | -0.056351 | -0.071161 | 0.013707 | 0.053537 | -0.10462 | 0.055732 | 0.10401 | 0.092462 | 0.018929 | -0.036803 | -0.016008 | -0.10267 | 0.82921 | -120.9299 | 0.95778 | 0.87749 | 0.048273 | -120.8451 | -120.8052 | 121.8966 | 121.7766 | 121.6899 | 1.0634 | -121.7369 | 0.86268 | 0.94754 | 0.98737 | 1.0075 | -120.9634
1573.25 | 121.8704 | -0.93384 | 120.9229 | 1.4211e-13 | -0.03747 | 0.0020727 | 0.064286 | -0.0084589 | 0.052256 | -0.01755 | -0.0044395 | -0.0012713 | 0.020681 | 0.026852 | 0.016714 | -0.82306 | 0.13419 | -0.89202 | 120.9857 | 120.8657 | 120.779 | -0.85521 | 0.014784 | 0.087354 | -0.065509 | -0.075739 | 0.018285 | 0.062694 | -0.10004 | 0.078627 | 0.062813 | 0.11078 | 0.04182 | -0.036807 | -0.057201 | -0.14387 | 0.83379 | -120.9986 | 0.94862 | 0.86833 | 0.034536 | -120.9046 | -120.8602 | 121.9195 | 121.7995 | 121.7128 | 1.068 | -121.7781 | 0.8581 | 0.95212 | 0.99653 | 1.0212 | -121.0229
1575.0156 | 121.8018 | -0.97504 | 120.9137 | 1.4211e-13 | -0.03747 | 0.0016453 | 0.064286 | -0.0088863 | 0.052469 | -0.01755 | -0.0044395 | -0.0012713 | 0.020681 | 0.026639 | 0.016928 | -0.80933 | 0.12503 | -0.88286 | 120.9902 | 120.8794 | 120.7836 | -0.84605 | 0.019362 | 0.073618 | -0.056351 | -0.071161 | 0.013707 | 0.053537 | -0.10004 | 0.12898 | 0.076547 | 0.16571 | 0.092176 | -0.036808 | -0.034308 | -0.13013 | 0.87499 | -120.9849 | 0.9944 | 0.91869 | 0.043694 | -120.9 | -120.8602 | 121.9653 | 121.8544 | 121.7586 | 1.1001 | -121.7597 | 0.90388 | 0.98874 | 1.0286 | 1.0487 | -121.0137
1576.7812 | 121.9299 | -0.93842 | 120.8908 | 1.4211e-13 | -0.037256 | 0.0016453 | 0.064286 | -0.0086727 | 0.052256 | 0.0053413 | -0.0044395 | -0.0010577 | 0.020467 | 0.026852 | 0.016714 | -0.8368 | 0.12961 | -0.90117 | 120.9719 | 120.8611 | 120.7698 | -0.86437 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.074047 | 0.081121 | 0.10162 | 0.037242 | -0.036805 | -0.029736 | -0.12098 | 0.83837 | -120.9665 | 0.95778 | 0.87749 | 0.039115 | -120.8817 | -120.8327 | 121.9103 | 121.7995 | 121.7082 | 1.068 | -121.7552 | 0.86268 | 0.94754 | 0.99653 | 1.0212 | -120.9909
1578.4844 | 121.8155 | -0.85602 | 121.0327 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.063859 | -0.0086727 | 0.052256 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.026639 | 0.0165 | -0.71776 | 0.12961 | -0.79587 | 121.091 | 120.9801 | 120.8843 | -0.75448 | 0.019362 | 0.082776 | -0.056351 | -0.075739 | 0.013707 | 0.062694 | -0.10004 | 0.10154 | 0.058253 | 0.13826 | 0.060144 | -0.041399 | -0.052591 | -0.14842 | 0.75597 | -121.1085 | 0.87538 | 0.79967 | 0.043694 | -121.019 | -120.97 | 121.947 | 121.8361 | 121.7403 | 0.98562 | -121.7872 | 0.78028 | 0.86972 | 0.91871 | 0.93879 | -121.1328
1580.25 | 121.7972 | -0.88806 | 121.0236 | 1.4211e-13 | -0.037683 | 0.0016453 | 0.064286 | -0.0080317 | 0.052256 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020681 | 0.02728 | 0.016928 | -0.74065 | 0.12045 | -0.81876 | 121.0681 | 120.9572 | 120.8751 | -0.78195 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.009128 | 0.053537 | -0.10462 | 0.10611 | 0.044516 | 0.14741 | 0.069297 | -0.036817 | -0.06633 | -0.14842 | 0.78344 | -121.0993 | 0.91658 | 0.82713 | 0.043694 | -121.0144 | -120.97 | 121.9561 | 121.8453 | 121.7632 | 1.0085 | -121.8055 | 0.81232 | 0.89719 | 0.9416 | 0.97084 | -121.1282
1582 | 121.9666 | -0.89722 | 120.9 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064286 | -0.0086727 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020467 | 0.027066 | 0.016928 | -0.75439 | 0.12503 | -0.83708 | 121.0543 | 120.9435 | 120.8614 | -0.78653 | 0.02852 | 0.082776 | -0.070087 | -0.066582 | 0.013707 | 0.058115 | -0.10462 | 0.11069 | 0.15438 | 0.14283 | 0.060139 | -0.050551 | 0.04353 | -0.038563 | 0.79259 | -120.9665 | 0.92574 | 0.82713 | 0.034537 | -120.8863 | -120.8418 | 121.9516 | 121.8407 | 121.7586 | 1.0222 | -121.6865 | 0.83064 | 0.91092 | 0.95533 | 0.97999 | -121.0046
1583.7656 | 121.8567 | -0.84686 | 121.0281 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020467 | 0.027066 | 0.016928 | -0.74065 | 0.13419 | -0.81876 | 121.0727 | 120.9664 | 120.8751 | -0.76821 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.013707 | 0.053537 | -0.10004 | 0.078651 | 0.044517 | 0.10621 | 0.028098 | -0.050553 | -0.061749 | -0.153 | 0.74682 | -121.1085 | 0.86623 | 0.78135 | 0.034536 | -121.0144 | -120.9746 | 121.9195 | 121.8133 | 121.722 | 0.98105 | -121.7963 | 0.76655 | 0.86057 | 0.9004 | 0.92506 | -121.1282
1585.4688 | 121.8979 | -0.86517 | 120.9824 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064286 | -0.0082453 | 0.052469 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020467 | 0.02728 | 0.016928 | -0.7315 | 0.12503 | -0.80961 | 121.0772 | 120.9618 | 120.8751 | -0.76363 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.013707 | 0.053537 | -0.10462 | 0.10154 | 0.094871 | 0.13368 | 0.055565 | -0.045975 | -0.020552 | -0.10722 | 0.76055 | -121.0535 | 0.88911 | 0.79966 | 0.039115 | -120.9687 | -120.9288 | 121.9424 | 121.827 | 121.7403 | 0.9902 | -121.746 | 0.79401 | 0.87888 | 0.91871 | 0.95253 | -121.087
1587.2188 | 121.8567 | -0.88806 | 121.0052 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.064073 | -0.0082453 | 0.052256 | -0.0022892 | -0.0046531 | -0.0012713 | 0.02004 | 0.027066 | 0.016714 | -0.74065 | 0.12961 | -0.81876 | 121.0681 | 120.9618 | 120.866 | -0.78195 | 0.023941 | 0.087354 | -0.065509 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.10611 | 0.062827 | 0.14741 | 0.069297 | -0.036817 | -0.04344 | -0.13927 | 0.78802 | -121.081 | 0.912 | 0.82255 | 0.034536 | -120.9961 | -120.9471 | 121.9561 | 121.8499 | 121.754 | 1.0177 | -121.7872 | 0.81232 | 0.89719 | 0.94618 | 0.97542 | -121.1053
1588.9688 | 121.9482 | -0.70953 | 121.0648 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064286 | -0.0082453 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020681 | 0.026852 | 0.016928 | -0.63535 | 0.13419 | -0.71804 | 121.1642 | 121.058 | 120.9621 | -0.67663 | 0.019362 | 0.087354 | -0.056351 | -0.071161 | 0.013707 | 0.048958 | -0.095467 | 0.032901 | 0.099464 | 0.074186 | -0.008509 | -0.04141 | -0.006792 | -0.10263 | 0.61407 | -121.1359 | 0.7289 | 0.65318 | 0.039116 | -121.0511 | -121.0158 | 121.8738 | 121.7675 | 121.6717 | 0.84372 | -121.7414 | 0.63837 | 0.72324 | 0.75849 | 0.79689 | -121.1602
1590.7344 | 121.8246 | -0.85602 | 121.019 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.0645 | -0.0082453 | 0.052683 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020467 | 0.02728 | 0.016928 | -0.69029 | 0.13419 | -0.77298 | 121.1184 | 121.003 | 120.9163 | -0.74074 | 0.014784 | 0.082776 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.10004 | 0.11528 | 0.099456 | 0.16573 | 0.083036 | -0.032244 | -0.015963 | -0.10264 | 0.75597 | -121.0947 | 0.8708 | 0.79967 | 0.043694 | -121.0053 | -120.9609 | 121.9745 | 121.859 | 121.7724 | 0.9902 | -121.7597 | 0.78028 | 0.86972 | 0.91413 | 0.93879 | -121.119
1592.5 | 121.9528 | -0.76446 | 121.0464 | 1.4211e-13 | -0.037683 | 0.0016453 | 0.064286 | -0.0080317 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020895 | 0.02728 | 0.016714 | -0.68571 | 0.13876 | -0.76383 | 121.1276 | 121.0122 | 120.9255 | -0.71784 | 0.023941 | 0.078197 | -0.051772 | -0.075739 | 0.013707 | 0.058115 | -0.095467 | 0.046622 | 0.081147 | 0.078754 | 0.000639 | -0.045983 | -0.034271 | -0.12095 | 0.669 | -121.1222 | 0.78841 | 0.71269 | 0.043695 | -121.0327 | -120.9883 | 121.8921 | 121.7766 | 121.69 | 0.90323 | -121.7643 | 0.68873 | 0.77817 | 0.82258 | 0.84266 | -121.1419
1594.1875 | 121.8201 | -0.78278 | 121.1105 | 1.4211e-13 | -0.037683 | 0.0016453 | 0.0645 | -0.0080317 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.027066 | 0.016714 | -0.65824 | 0.13876 | -0.73636 | 121.1551 | 121.0488 | 120.9484 | -0.69037 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.009128 | 0.062694 | -0.10004 | 0.092406 | 0.04453 | 0.12454 | 0.04642 | -0.045986 | -0.061727 | -0.16214 | 0.68273 | -121.1863 | 0.80672 | 0.71727 | 0.034536 | -121.1014 | -121.0478 | 121.9378 | 121.8316 | 121.7312 | 0.92154 | -121.8009 | 0.70704 | 0.7919 | 0.84547 | 0.86097 | -121.2106
1595.9375 | 121.9574 | -0.72784 | 121.0648 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064286 | -0.0084589 | 0.052256 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020467 | 0.026852 | 0.016714 | -0.63077 | 0.13876 | -0.71347 | 121.178 | 121.0717 | 120.9759 | -0.65832 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.009128 | 0.053537 | -0.10462 | 0.069527 | 0.1132 | 0.097074 | 0.014379 | -0.055148 | 0.006945 | -0.088893 | 0.62322 | -121.1405 | 0.75179 | 0.66691 | 0.043694 | -121.0556 | -121.0112 | 121.9058 | 121.7995 | 121.7037 | 0.86661 | -121.7231 | 0.65211 | 0.73697 | 0.78138 | 0.8152 | -121.1694
1597.6875 | 121.9711 | -0.70953 | 121.106 | 1.4211e-13 | -0.037897 | 0.0016453 | 0.064286 | -0.0082453 | 0.052469 | -0.01755 | -0.0044395 | -0.0014849 | 0.020467 | 0.027066 | 0.016928 | -0.61246 | 0.12961 | -0.69057 | 121.2054 | 121.09 | 120.9942 | -0.65374 | 0.019362 | 0.082776 | -0.065509 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.055795 | 0.09947 | 0.097078 | 0.018961 | -0.036834 | -0.015939 | -0.11178 | 0.60491 | -121.1817 | 0.7289 | 0.64402 | 0.039115 | -121.0968 | -121.0478 | 121.915 | 121.7996 | 121.7037 | 0.83914 | -121.7597 | 0.63379 | 0.71866 | 0.76765 | 0.79231 | -121.2106
1599.375 | 121.8567 | -0.74158 | 121.1288 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.064286 | -0.0080317 | 0.052469 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020681 | 0.026852 | 0.016928 | -0.61704 | 0.12961 | -0.686 | 121.21 | 121.0992 | 120.9942 | -0.65374 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.004549 | 0.053537 | -0.095467 | 0.087838 | 0.081161 | 0.12454 | 0.055582 | -0.032256 | -0.029669 | -0.13467 | 0.64611 | -121.2092 | 0.76094 | 0.68523 | 0.039116 | -121.1243 | -121.0753 | 121.9516 | 121.8408 | 121.7358 | 0.87118 | -121.7826 | 0.66126 | 0.74613 | 0.79511 | 0.81977 | -121.2243
1601.125 | 121.9345 | -0.71411 | 121.1197 | 1.4211e-13 | -0.038111 | 0.0016453 | 0.0645 | -0.0078179 | 0.052683 | -0.01755 | -0.0046531 | -0.0010577 | 0.020254 | 0.026852 | 0.016714 | -0.58499 | 0.13419 | -0.66768 | 121.2283 | 121.1083 | 121.0171 | -0.63542 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.078688 | 0.10863 | 0.12913 | 0.046429 | -0.032259 | -0.011356 | -0.10262 | 0.61407 | -121.1954 | 0.74263 | 0.65776 | 0.043694 | -121.1106 | -121.0616 | 121.9424 | 121.8224 | 121.7312 | 0.8483 | -121.7551 | 0.63837 | 0.72324 | 0.77223 | 0.80147 | -121.2197
1602.8906 | 121.9528 | -0.74158 | 121.0785 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064286 | -0.0082453 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.026639 | 0.016714 | -0.62619 | 0.13419 | -0.70889 | 121.1917 | 121.0763 | 120.9759 | -0.66748 | 0.019362 | 0.082776 | -0.056351 | -0.071161 | 0.009128 | 0.058115 | -0.10462 | 0.074102 | 0.1132 | 0.11539 | 0.032691 | -0.041411 | -0.002209 | -0.10263 | 0.63695 | -121.1497 | 0.76094 | 0.68523 | 0.048273 | -121.0694 | -121.0204 | 121.9333 | 121.8179 | 121.7174 | 0.87576 | -121.746 | 0.67042 | 0.75071 | 0.79969 | 0.82435 | -121.1831
1604.5938 | 121.8567 | -0.77362 | 121.1334 | 1.4211e-13 | -0.037897 | 0.0016453 | 0.064286 | -0.0084589 | 0.052469 | -0.0022892 | -0.0042257 | -0.0010577 | 0.020467 | 0.027066 | 0.016928 | -0.64908 | 0.12961 | -0.7272 | 121.178 | 121.058 | 120.9621 | -0.68579 | 0.019362 | 0.082776 | -0.065509 | -0.071161 | 0.009128 | 0.053537 | -0.10004 | 0.08783 | 0.044534 | 0.12454 | 0.046422 | -0.041408 | -0.075457 | -0.17129 | 0.67358 | -121.2046 | 0.79298 | 0.70811 | 0.034536 | -121.1243 | -121.0799 | 121.9516 | 121.8316 | 121.7358 | 0.90323 | -121.8192 | 0.70246 | 0.78275 | 0.82716 | 0.8564 | -121.2335
1606.3594 | 121.843 | -0.84228 | 121.051 | 1.4211e-13 | -0.037683 | 0.0020727 | 0.064073 | -0.0084589 | 0.052469 | -0.01755 | -0.0046531 | -0.0016987 | 0.020681 | 0.02728 | 0.016928 | -0.67655 | 0.13419 | -0.76383 | 121.1368 | 121.0305 | 120.9163 | -0.70869 | 0.019362 | 0.078197 | -0.065509 | -0.075739 | 0.004549 | 0.053537 | -0.10004 | 0.1336 | 0.085726 | 0.16573 | 0.078459 | -0.05514 | -0.020533 | -0.13468 | 0.74224 | -121.1268 | 0.86165 | 0.77678 | 0.034536 | -121.0465 | -120.9975 | 121.979 | 121.8728 | 121.7586 | 0.97647 | -121.7597 | 0.76655 | 0.84683 | 0.89582 | 0.92048 | -121.1511
1608.0469 | 121.8704 | -0.90179 | 120.9824 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.0645 | -0.0082453 | 0.052469 | -0.0099192 | -0.0048667 | -0.0014849 | 0.020467 | 0.026852 | 0.016928 | -0.75439 | 0.12503 | -0.82792 | 121.0635 | 120.9481 | 120.8568 | -0.79111 | 0.019362 | 0.087354 | -0.06093 | -0.080318 | 0.009128 | 0.058115 | -0.095467 | 0.11069 | 0.081136 | 0.14741 | 0.073872 | -0.036816 | -0.034289 | -0.12554 | 0.80633 | -121.0627 | 0.92116 | 0.84086 | 0.034537 | -120.9732 | -120.9242 | 121.9653 | 121.8499 | 121.7586 | 1.0268 | -121.7735 | 0.82148 | 0.91092 | 0.95991 | 0.98915 | -121.0778
1609.8125 | 121.9666 | -0.85602 | 120.9961 | 1.4211e-13 | -0.038111 | 0.0018589 | 0.0645 | -0.0086727 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.02728 | 0.017141 | -0.74523 | 0.13419 | -0.82792 | 121.0818 | 120.9664 | 120.8568 | -0.77737 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.009128 | 0.053537 | -0.10004 | 0.078648 | 0.085717 | 0.11079 | 0.028096 | -0.050552 | -0.029706 | -0.13927 | 0.75597 | -121.0764 | 0.87538 | 0.79051 | 0.034536 | -120.987 | -120.9426 | 121.9378 | 121.8224 | 121.7128 | 0.9902 | -121.7735 | 0.7757 | 0.86515 | 0.90955 | 0.93421 | -121.0961
1611.5781 | 121.9299 | -1.0254 | 120.8038 | 1.4211e-13 | -0.037897 | 0.0020727 | 0.064286 | -0.0082453 | 0.052683 | -0.0099192 | -0.0046531 | -0.0014849 | 0.020467 | 0.027493 | 0.016714 | -0.93294 | 0.12961 | -1.0111 | 120.8941 | 120.7787 | 120.6874 | -0.9651 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.013707 | 0.048958 | -0.095467 | 0.060286 | 0.090264 | 0.092447 | 0.014338 | -0.045948 | -0.025181 | -0.11642 | 0.92992 | -120.8796 | 1.0493 | 0.96446 | 0.034537 | -120.7901 | -120.7549 | 121.9195 | 121.804 | 121.7128 | 1.155 | -121.7689 | 0.94965 | 1.0391 | 1.0743 | 1.1127 | -120.8993
1613.3281 | 121.8567 | -1.0345 | 120.8771 | 1.4211e-13 | -0.038111 | 0.0016453 | 0.064073 | -0.0082453 | 0.052256 | -0.0022892 | -0.0044395 | -0.0014849 | 0.020254 | 0.027066 | 0.016714 | -0.91005 | 0.12961 | -0.98358 | 120.917 | 120.8015 | 120.7011 | -0.93763 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.096914 | 0.039914 | 0.12449 | 0.050963 | -0.045951 | -0.075529 | -0.17593 | 0.92992 | -120.9528 | 1.0585 | 0.97362 | 0.043694 | -120.8679 | -120.819 | 121.9515 | 121.8361 | 121.7357 | 1.1642 | -121.8147 | 0.95881 | 1.0437 | 1.0927 | 1.1082 | -120.9817
1615.0156 | 121.9345 | -0.88806 | 120.9549 | 1.4211e-13 | -0.038111 | 0.0020727 | 0.063859 | -0.0084589 | 0.052469 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.027066 | 0.016928 | -0.97415 | 0.13419 | -1.0523 | 120.8529 | 120.742 | 120.637 | -1.0063 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.004549 | 0.058115 | -0.095467 | -0.11825 | -0.102 | -0.086087 | -0.16419 | -0.045941 | -0.21287 | -0.31785 | 0.7926 | -121.0261 | 0.90742 | 0.82713 | 0.034537 | -120.9503 | -120.8968 | 121.741 | 121.6301 | 121.5251 | 1.0222 | -121.9612 | 0.8169 | 0.89261 | 0.94618 | 0.97542 | -121.0504
1616.7656 | 121.9299 | -1.0254 | 120.8084 | 1.4211e-13 | -0.038111 | 0.0020727 | 0.064073 | -0.0084589 | 0.052256 | -0.0099192 | -0.0046531 | -0.0014849 | 0.020467 | 0.026852 | 0.016714 | -0.91463 | 0.13419 | -0.99732 | 120.9078 | 120.797 | 120.7011 | -0.94679 | 0.014784 | 0.087354 | -0.056351 | -0.071161 | 0.009128 | 0.053537 | -0.10004 | 0.078601 | 0.099421 | 0.11076 | 0.028073 | -0.050528 | -0.011444 | -0.10726 | 0.92535 | -120.8796 | 1.0402 | 0.96904 | 0.043694 | -120.7993 | -120.7549 | 121.9332 | 121.8224 | 121.7265 | 1.1596 | -121.7552 | 0.95423 | 1.0345 | 1.0789 | 1.1127 | -120.9085
1618.4531 | 121.962 | -1.03 | 120.8038 | 1.4211e-13 | -0.038111 | 0.0016453 | 0.064073 | -0.0082453 | 0.052256 | -0.0099192 | -0.0046531 | -0.0016987 | 0.020681 | 0.02728 | 0.016928 | -0.93294 | 0.13419 | -1.0111 | 120.8941 | 120.7695 | 120.6783 | -0.96968 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.10462 | 0.060284 | 0.090264 | 0.097024 | 0.018915 | -0.041369 | -0.034339 | -0.12558 | 0.92534 | -120.8796 | 1.0539 | 0.96904 | 0.043694 | -120.7947 | -120.7457 | 121.9241 | 121.7995 | 121.7082 | 1.1642 | -121.7735 | 0.95423 | 1.0391 | 1.0881 | 1.1082 | -120.9085
1620.2031 | 121.9025 | -0.99335 | 120.8954 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.064714 | -0.0084589 | 0.052683 | -0.01755 | -0.0046531 | -0.0012713 | 0.020467 | 0.027066 | 0.016714 | -0.86427 | 0.12961 | -0.94696 | 120.9628 | 120.8519 | 120.7424 | -0.89642 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.009128 | 0.048958 | -0.10004 | 0.096925 | 0.067387 | 0.12908 | 0.04639 | -0.050535 | -0.043472 | -0.15303 | 0.8933 | -120.962 | 1.0173 | 0.93242 | 0.039115 | -120.8863 | -120.8464 | 121.9561 | 121.8453 | 121.7357 | 1.123 | -121.7918 | 0.92676 | 1.0025 | 1.0423 | 1.0715 | -120.9954
1621.9531 | 121.9757 | -0.91095 | 120.9091 | 1.4211e-13 | -0.037683 | 0.0022863 | 0.0645 | -0.0080317 | 0.052042 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020681 | 0.027066 | 0.016714 | -0.95126 | 0.14334 | -1.0339 | 120.8804 | 120.7787 | 120.6737 | -0.97426 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.013707 | 0.053537 | -0.10004 | -0.063313 | -0.028757 | -0.040307 | -0.12299 | -0.059681 | -0.13047 | -0.23544 | 0.8109 | -120.9849 | 0.93031 | 0.84544 | 0.034536 | -120.8954 | -120.8556 | 121.7913 | 121.6896 | 121.5846 | 1.0543 | -121.8834 | 0.83521 | 0.92466 | 0.96449 | 0.9983 | -121.0092
1623.7031 | 121.9666 | -1.1124 | 120.7352 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0044395 | -0.0012713 | 0.02004 | 0.027066 | 0.016928 | -0.90547 | 0.12503 | -0.98358 | 120.9261 | 120.8153 | 120.7149 | -0.93763 | 0.023941 | 0.087354 | -0.070087 | -0.080318 | 0.009128 | 0.048958 | -0.10004 | 0.17473 | 0.19098 | 0.20689 | 0.12878 | -0.045951 | 0.080115 | -0.020283 | 1.0123 | -120.8155 | 1.1363 | 1.0423 | 0.029958 | -120.726 | -120.6862 | 122.0385 | 121.9276 | 121.8273 | 1.2374 | -121.6728 | 1.032 | 1.1215 | 1.1613 | 1.1997 | -120.8352
1625.3906 | 121.8109 | -0.65002 | 121.2479 | 1.4211e-13 | -0.037683 | 0.0018589 | 0.064073 | -0.0084589 | 0.052469 | 0.012972 | -0.0044395 | -0.0010577 | 0.020467 | 0.02728 | 0.016928 | -0.51631 | 0.13419 | -0.60359 | 121.3153 | 121.1999 | 121.0903 | -0.56216 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.009128 | 0.053537 | -0.10462 | 0.087864 | 0.067445 | 0.13371 | 0.046438 | -0.041426 | -0.047951 | -0.15753 | 0.5454 | -121.3282 | 0.67854 | 0.58909 | 0.043694 | -121.2387 | -121.1943 | 121.9653 | 121.8499 | 121.7404 | 0.78421 | -121.81 | 0.56971 | 0.65915 | 0.70356 | 0.72822 | -121.3525
1627.1406 | 121.8658 | -0.59967 | 121.3348 | 1.4211e-13 | -0.038111 | 0.0018589 | 0.064286 | -0.0084589 | 0.052897 | -0.0022892 | -0.0046531 | -0.0016987 | 0.020681 | 0.02728 | 0.016714 | -0.46595 | 0.13876 | -0.53949 | 121.3657 | 121.2549 | 121.1499 | -0.50721 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.013707 | 0.053537 | -0.095467 | 0.092457 | 0.030832 | 0.13372 | 0.06018 | -0.032277 | -0.079979 | -0.18499 | 0.5042 | -121.4106 | 0.62361 | 0.53874 | 0.034537 | -121.3211 | -121.2813 | 121.9653 | 121.8545 | 121.7495 | 0.73844 | -121.8421 | 0.52393 | 0.61338 | 0.65321 | 0.68245 | -121.4303
1628.8281 | 121.9299 | -0.49896 | 121.376 | 1.4211e-13 | -0.037897 | 0.0018589 | 0.064714 | -0.0082453 | 0.052469 | -0.0099192 | -0.0050803 | -0.0012713 | 0.020467 | 0.027493 | 0.016714 | -0.39727 | 0.13419 | -0.47082 | 121.4298 | 121.3281 | 121.2277 | -0.43853 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.013707 | 0.053537 | -0.1092 | 0.060433 | 0.05373 | 0.10169 | 0.028146 | -0.032287 | -0.047915 | -0.14835 | 0.38976 | -121.4472 | 0.5229 | 0.43803 | 0.048273 | -121.3623 | -121.3225 | 121.9287 | 121.8271 | 121.7267 | 0.63315 | -121.8146 | 0.4278 | 0.51267 | 0.5525 | 0.57716 | -121.4852
1630.6094 | 121.9849 | -0.44403 | 121.3989 | 1.4211e-13 | -0.038324 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0022892 | -0.0044395 | -0.0016987 | 0.020467 | 0.026852 | 0.0165 | -0.35607 | 0.12961 | -0.42961 | 121.4801 | 121.3739 | 121.2735 | -0.39732 | 0.014784 | 0.073618 | -0.06093 | -0.075739 | 0.013707 | 0.062694 | -0.10462 | 0.046712 | 0.081205 | 0.087964 | 0.01442 | -0.032292 | -0.025014 | -0.12545 | 0.33941 | -121.4747 | 0.45882 | 0.3831 | 0.043694 | -121.3852 | -121.3362 | 121.9242 | 121.8179 | 121.7175 | 0.57364 | -121.7962 | 0.36829 | 0.45774 | 0.50672 | 0.51765 | -121.5036
1632.375 | 121.9254 | -0.40283 | 121.4539 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.0645 | -0.0086727 | 0.052469 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020467 | 0.027066 | 0.016714 | -0.3057 | 0.13419 | -0.37009 | 121.5351 | 121.4289 | 121.3284 | -0.35153 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.013707 | 0.053537 | -0.10004 | 0.051302 | 0.081214 | 0.097128 | 0.032738 | -0.018564 | -0.024998 | -0.12544 | 0.30279 | -121.5342 | 0.42219 | 0.33732 | 0.034536 | -121.4402 | -121.4003 | 121.9379 | 121.8317 | 121.7312 | 0.53702 | -121.8054 | 0.32251 | 0.41654 | 0.45637 | 0.48103 | -121.5539
1634.0781 | 121.8292 | -0.41199 | 121.5271 | 1.4211e-13 | -0.038111 | 0.0016453 | 0.0645 | -0.0084589 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020895 | 0.026852 | 0.016714 | -0.26908 | 0.13419 | -0.33805 | 121.5671 | 121.4609 | 121.3605 | -0.31948 | 0.023941 | 0.06904 | -0.06093 | -0.075739 | 0.013707 | 0.048958 | -0.10462 | 0.09251 | 0.04002 | 0.14291 | 0.073941 | -0.018569 | -0.066189 | -0.16663 | 0.30736 | -121.6028 | 0.43593 | 0.35106 | 0.043694 | -121.5134 | -121.4781 | 121.9791 | 121.8729 | 121.7725 | 0.54617 | -121.8466 | 0.33625 | 0.42569 | 0.46094 | 0.48103 | -121.6317
1635.8438 | 121.9711 | -0.34332 | 121.4905 | 1.4211e-13 | -0.038111 | 0.0020727 | 0.0645 | -0.0084589 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.027066 | 0.0165 | -0.2645 | 0.13419 | -0.32889 | 121.5809 | 121.4701 | 121.3696 | -0.3149 | 0.023941 | 0.064461 | -0.065509 | -0.071161 | 0.013707 | 0.058115 | -0.10462 | 0.028425 | 0.090376 | 0.078824 | 0.014434 | -0.013991 | -0.02041 | -0.12085 | 0.2387 | -121.5616 | 0.36726 | 0.27781 | 0.039115 | -121.4768 | -121.4324 | 121.9242 | 121.8134 | 121.7129 | 0.47751 | -121.8054 | 0.27216 | 0.35703 | 0.40144 | 0.40778 | -121.5951
1637.6094 | 121.8796 | -0.37994 | 121.4996 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.064286 | -0.0084589 | 0.052256 | -0.01755 | -0.0044395 | -0.0012713 | 0.02004 | 0.02728 | 0.016714 | -0.25992 | 0.13876 | -0.32889 | 121.59 | 121.4746 | 121.365 | -0.31032 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.013707 | 0.058115 | -0.095467 | 0.069625 | 0.090378 | 0.12002 | 0.051055 | -0.01857 | -0.024986 | -0.13459 | 0.28448 | -121.5662 | 0.40388 | 0.32359 | 0.039116 | -121.4859 | -121.4415 | 121.97 | 121.8546 | 121.745 | 0.51871 | -121.81 | 0.31336 | 0.39365 | 0.43806 | 0.45814 | -121.5951
1639.3594 | 121.843 | -0.41657 | 121.5408 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.064286 | -0.0082453 | 0.052256 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.027066 | 0.016928 | -0.2645 | 0.13876 | -0.33805 | 121.5809 | 121.4746 | 121.3742 | -0.31948 | 0.019362 | 0.073618 | -0.056351 | -0.066582 | 0.009128 | 0.058115 | -0.10004 | 0.097088 | 0.040022 | 0.15207 | 0.078519 | -0.018569 | -0.066185 | -0.16663 | 0.31652 | -121.6074 | 0.43593 | 0.36021 | 0.043694 | -121.5317 | -121.4827 | 121.9974 | 121.8912 | 121.7908 | 0.55533 | -121.8603 | 0.34998 | 0.42569 | 0.47468 | 0.49018 | -121.6409
1641.125 | 121.9528 | -0.34332 | 121.4722 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.0645 | -0.0084589 | 0.052897 | -0.0099192 | -0.0048667 | -0.0014849 | 0.020895 | 0.027493 | 0.016928 | -0.25992 | 0.14334 | -0.33347 | 121.5946 | 121.4746 | 121.3696 | -0.31032 | 0.019362 | 0.06904 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.033004 | 0.12242 | 0.083402 | 0.009856 | -0.023148 | 0.00248 | -0.10254 | 0.23412 | -121.5479 | 0.36268 | 0.28697 | 0.052852 | -121.4585 | -121.4141 | 121.9379 | 121.818 | 121.7129 | 0.48667 | -121.7825 | 0.26758 | 0.35703 | 0.40144 | 0.41236 | -121.5814
1642.8906 | 121.8521 | -0.39368 | 121.5225 | 1.4211e-13 | -0.037897 | 0.0016453 | 0.0645 | -0.0082453 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020254 | 0.027493 | 0.016714 | -0.26908 | 0.13876 | -0.34262 | 121.5763 | 121.4655 | 121.365 | -0.31948 | 0.023941 | 0.059882 | -0.070087 | -0.075739 | 0.013707 | 0.058115 | -0.10462 | 0.0742 | 0.053755 | 0.1246 | 0.051053 | -0.023147 | -0.057032 | -0.15748 | 0.28905 | -121.5983 | 0.41762 | 0.32359 | 0.034537 | -121.5088 | -121.4644 | 121.97 | 121.8592 | 121.7587 | 0.53244 | -121.842 | 0.31794 | 0.40738 | 0.45179 | 0.45356 | -121.6271
1644.5938 | 121.8292 | -0.41657 | 121.5179 | 1.4211e-13 | -0.038111 | 0.0020727 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0040121 | -0.0012713 | 0.020254 | 0.026852 | 0.016928 | -0.26908 | 0.13419 | -0.34262 | 121.5854 | 121.4746 | 121.3788 | -0.3149 | 0.014784 | 0.073618 | -0.06093 | -0.080318 | 0.004549 | 0.053537 | -0.1092 | 0.10167 | 0.067489 | 0.14749 | 0.073941 | -0.027726 | -0.043296 | -0.13916 | 0.30736 | -121.5983 | 0.43135 | 0.35564 | 0.048273 | -121.5134 | -121.4644 | 122.002 | 121.8912 | 121.7953 | 0.55075 | -121.8328 | 0.33625 | 0.42111 | 0.4701 | 0.49018 | -121.6271
1646.3594 | 121.8613 | -0.37079 | 121.5363 | 1.4211e-13 | -0.038111 | 0.0018589 | 0.064073 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.02728 | 0.016714 | -0.24618 | 0.13876 | -0.32431 | 121.6037 | 121.5021 | 121.3879 | -0.29658 | 0.019362 | 0.06904 | -0.06093 | -0.075739 | 0.009128 | 0.053537 | -0.10004 | 0.074207 | 0.067492 | 0.1246 | 0.046478 | -0.027729 | -0.034133 | -0.14832 | 0.27074 | -121.612 | 0.39015 | 0.30986 | 0.039115 | -121.5271 | -121.4827 | 121.9745 | 121.8729 | 121.7587 | 0.50955 | -121.8328 | 0.29505 | 0.37992 | 0.42433 | 0.43983 | -121.6363
1648.1094 | 121.8338 | -0.36163 | 121.55 | 1.4211e-13 | -0.038111 | 0.0018589 | 0.063859 | -0.0084589 | 0.052683 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020254 | 0.02728 | 0.016714 | -0.23703 | 0.14334 | -0.306 | 121.6129 | 121.5067 | 121.4017 | -0.292 | 0.019362 | 0.078197 | -0.056351 | -0.075739 | 0.013707 | 0.058115 | -0.10004 | 0.069629 | 0.062916 | 0.1246 | 0.055635 | -0.013994 | -0.043287 | -0.14831 | 0.26159 | -121.6257 | 0.38099 | 0.30528 | 0.043694 | -121.5363 | -121.4919 | 121.9745 | 121.8683 | 121.7633 | 0.50498 | -121.842 | 0.28589 | 0.37534 | 0.41975 | 0.43983 | -121.65
1649.7969 | 121.9711 | -0.29755 | 121.5271 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064286 | -0.0086727 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.027493 | 0.016928 | -0.22329 | 0.13419 | -0.29226 | 121.6175 | 121.5113 | 121.4108 | -0.28285 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | -2.9e-05 | 0.053537 | -0.10004 | 0.0147 | 0.090382 | 0.074253 | 0.005283 | -0.009417 | -0.01582 | -0.11627 | 0.1975 | -121.6028 | 0.32149 | 0.23662 | 0.039115 | -121.5271 | -121.4736 | 121.915 | 121.8088 | 121.7084 | 0.43173 | -121.8099 | 0.22181 | 0.29752 | 0.35108 | 0.37116 | -121.6271
1651.5625 | 121.875 | -0.35248 | 121.5729 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.0645 | -0.0082453 | 0.052897 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020467 | 0.027493 | 0.0165 | -0.22787 | 0.13419 | -0.29226 | 121.6312 | 121.525 | 121.4108 | -0.27369 | 0.023941 | 0.064461 | -0.06093 | -0.080318 | 0.009128 | 0.058115 | -0.10462 | 0.07879 | 0.058341 | 0.12461 | 0.060215 | -0.018575 | -0.04786 | -0.16204 | 0.24785 | -121.6532 | 0.37642 | 0.29155 | 0.043694 | -121.5637 | -121.5148 | 121.9837 | 121.8775 | 121.7633 | 0.48666 | -121.8466 | 0.27216 | 0.36161 | 0.41059 | 0.41694 | -121.6775
1653.25 | 121.8475 | -0.35706 | 121.55 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.02728 | 0.016928 | -0.21871 | 0.13876 | -0.29226 | 121.6312 | 121.525 | 121.4246 | -0.28285 | 0.023941 | 0.073618 | -0.056351 | -0.075739 | 0.009128 | 0.058115 | -0.10004 | 0.07421 | 0.081229 | 0.13834 | 0.064793 | -0.009417 | -0.024972 | -0.12542 | 0.25701 | -121.6257 | 0.381 | 0.30071 | 0.043694 | -121.5409 | -121.4919 | 121.9883 | 121.8821 | 121.7816 | 0.49582 | -121.8328 | 0.28132 | 0.36618 | 0.41517 | 0.43067 | -121.65
1655.0156 | 121.9208 | -0.33417 | 121.5546 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.0645 | -0.0084589 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020254 | 0.027707 | 0.016928 | -0.21871 | 0.13876 | -0.29226 | 121.6312 | 121.525 | 121.4154 | -0.26911 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.009128 | 0.058115 | -0.10004 | 0.065058 | 0.076652 | 0.11545 | 0.041904 | -0.023154 | -0.029549 | -0.13915 | 0.23412 | -121.6257 | 0.35811 | 0.27324 | 0.039115 | -121.5454 | -121.4964 | 121.9654 | 121.8592 | 121.7496 | 0.47293 | -121.8237 | 0.26301 | 0.3433 | 0.39228 | 0.41236 | -121.6546
1656.7812 | 121.9894 | -0.3067 | 121.5225 | 1.4211e-13 | -0.038538 | 0.0018589 | 0.064286 | -0.0086727 | 0.052469 | -0.0022892 | -0.0048667 | -0.0014849 | 0.020681 | 0.027066 | 0.017355 | -0.22787 | 0.14334 | -0.30142 | 121.6312 | 121.525 | 121.42 | -0.27369 | 0.019362 | 0.078197 | -0.06093 | -0.071161 | 0.018285 | 0.058115 | -0.10462 | 0.033014 | 0.1087 | 0.07883 | 0.005283 | -0.027731 | 0.002494 | -0.10253 | 0.20208 | -121.5937 | 0.32606 | 0.24577 | 0.043694 | -121.5042 | -121.4644 | 121.9379 | 121.8317 | 121.7267 | 0.45004 | -121.7962 | 0.23554 | 0.32499 | 0.36482 | 0.3849 | -121.6271
1658.4688 | 121.9482 | -0.30212 | 121.5637 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020254 | 0.027066 | 0.017141 | -0.22329 | 0.14334 | -0.28768 | 121.6358 | 121.5296 | 121.4246 | -0.27369 | 0.023941 | 0.059882 | -0.06093 | -0.071161 | 0.009128 | 0.058115 | -0.10462 | 0.028436 | 0.072075 | 0.078831 | 0.01444 | -0.013996 | -0.034126 | -0.13915 | 0.1975 | -121.6349 | 0.32606 | 0.24119 | 0.043694 | -121.5546 | -121.5056 | 121.9379 | 121.8317 | 121.7267 | 0.44547 | -121.8374 | 0.23096 | 0.31125 | 0.36024 | 0.36201 | -121.6683
1660.2188 | 121.8521 | -0.34332 | 121.5866 | 1.4211e-13 | -0.038111 | 0.0018589 | 0.0645 | -0.0086727 | 0.052683 | -0.0099192 | -0.0048667 | -0.00063026 | 0.020467 | 0.02728 | 0.0165 | -0.21871 | 0.13876 | -0.28311 | 121.645 | 121.5342 | 121.4337 | -0.26911 | 0.02852 | 0.073618 | -0.06093 | -0.075739 | 0.009128 | 0.053537 | -0.10462 | 0.074214 | 0.058343 | 0.12461 | 0.060217 | -0.013997 | -0.052435 | -0.15288 | 0.2387 | -121.6623 | 0.37184 | 0.28239 | 0.043694 | -121.5775 | -121.5331 | 121.9883 | 121.8775 | 121.777 | 0.48209 | -121.8557 | 0.26758 | 0.35245 | 0.39686 | 0.41694 | -121.6912
1661.9688 | 121.8979 | -0.34332 | 121.582 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.0645 | -0.0084589 | 0.052469 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020467 | 0.027493 | 0.016714 | -0.21414 | 0.13419 | -0.27853 | 121.6541 | 121.5388 | 121.4291 | -0.26453 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.053537 | -0.10004 | 0.078793 | 0.072078 | 0.12919 | 0.064795 | -0.013998 | -0.043278 | -0.15288 | 0.24328 | -121.6623 | 0.36268 | 0.28239 | 0.039115 | -121.5637 | -121.5285 | 121.9974 | 121.8821 | 121.7725 | 0.47751 | -121.8466 | 0.263 | 0.36161 | 0.39686 | 0.41694 | -121.6821
1663.7344 | 121.843 | -0.3479 | 121.5775 | 1.4211e-13 | -0.038111 | 0.0018589 | 0.0645 | -0.0088863 | 0.052683 | -0.02518 | -0.0046531 | -0.0012713 | 0.020467 | 0.02728 | 0.0165 | -0.20498 | 0.13876 | -0.28768 | 121.645 | 121.5433 | 121.4337 | -0.26453 | 0.02852 | 0.06904 | -0.065509 | -0.071161 | 0.018285 | 0.053537 | -0.10462 | 0.08337 | 0.067498 | 0.14292 | 0.060216 | -0.023154 | -0.034122 | -0.14373 | 0.24328 | -121.6486 | 0.37642 | 0.28239 | 0.039115 | -121.5592 | -121.5239 | 121.9929 | 121.8912 | 121.7816 | 0.48667 | -121.842 | 0.27674 | 0.36618 | 0.40144 | 0.41694 | -121.6821
1665.4219 | 121.9666 | -0.31586 | 121.5866 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020681 | 0.02728 | 0.016714 | -0.21414 | 0.12961 | -0.28311 | 121.645 | 121.5433 | 121.4337 | -0.26911 | 0.019362 | 0.073618 | -0.065509 | -0.080318 | 0.004549 | 0.058115 | -0.10004 | 0.046748 | 0.058343 | 0.10172 | 0.032751 | -0.013997 | -0.043277 | -0.15288 | 0.21581 | -121.6669 | 0.33522 | 0.25035 | 0.034536 | -121.5821 | -121.5285 | 121.9608 | 121.8592 | 121.7496 | 0.44546 | -121.8557 | 0.23554 | 0.32041 | 0.37397 | 0.38948 | -121.6867
1667.1875 | 121.9482 | -0.29297 | 121.5591 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.064073 | -0.0084589 | 0.052897 | -0.01755 | -0.0046531 | -0.0012713 | 0.020254 | 0.02728 | 0.016714 | -0.21414 | 0.13419 | -0.27853 | 121.6495 | 121.5433 | 121.4429 | -0.25995 | 0.019362 | 0.073618 | -0.06093 | -0.075739 | 0.004549 | 0.053537 | -0.10004 | 0.033018 | 0.090388 | 0.078832 | 0.014441 | -0.018577 | -0.015811 | -0.11626 | 0.19292 | -121.6349 | 0.31233 | 0.23204 | 0.039115 | -121.5546 | -121.5056 | 121.9425 | 121.8363 | 121.7359 | 0.42715 | -121.8191 | 0.21723 | 0.29752 | 0.34651 | 0.36659 | -121.6592
1668.9375 | 121.8704 | -0.33417 | 121.6049 | 1.4211e-13 | -0.038324 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | -0.0099192 | -0.0048667 | -0.0012713 | 0.020895 | 0.027493 | 0.016714 | -0.20956 | 0.13876 | -0.28311 | 121.6495 | 121.5388 | 121.4383 | -0.26453 | 0.023941 | 0.06904 | -0.070087 | -0.071161 | 0.013707 | 0.058115 | -0.10462 | 0.069637 | 0.044612 | 0.12461 | 0.051061 | -0.018576 | -0.066166 | -0.16661 | 0.22954 | -121.6761 | 0.35811 | 0.26408 | 0.034537 | -121.5912 | -121.5468 | 121.9837 | 121.8729 | 121.7725 | 0.47293 | -121.8694 | 0.26301 | 0.34787 | 0.39228 | 0.40321 | -121.7095
1670.7031 | 121.8842 | -0.32959 | 121.5958 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.0645 | -0.0082453 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020254 | 0.027493 | 0.016714 | -0.20498 | 0.14792 | -0.28768 | 121.6495 | 121.5388 | 121.4337 | -0.26453 | 0.023941 | 0.06904 | -0.056351 | -0.080318 | 0.009128 | 0.058115 | -0.1092 | 0.06506 | 0.053767 | 0.12461 | 0.041906 | -0.023154 | -0.057011 | -0.16204 | 0.22039 | -121.6761 | 0.35353 | 0.27324 | 0.052852 | -121.5866 | -121.5376 | 121.9791 | 121.8683 | 121.7633 | 0.47751 | -121.8603 | 0.24927 | 0.33872 | 0.3877 | 0.39863 | -121.705
1672.4062 | 121.9482 | -0.31586 | 121.5591 | 1.4211e-13 | -0.038324 | 0.0020727 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0048667 | -0.0014849 | 0.020681 | 0.027493 | 0.016714 | -0.20498 | 0.13876 | -0.28768 | 121.6495 | 121.5342 | 121.4429 | -0.26911 | 0.019362 | 0.06904 | -0.06093 | -0.080318 | 0.004549 | 0.058115 | -0.1092 | 0.046748 | 0.090388 | 0.11088 | 0.028173 | -0.018575 | -0.024969 | -0.11626 | 0.20665 | -121.6395 | 0.33522 | 0.25493 | 0.048273 | -121.5546 | -121.501 | 121.9654 | 121.85 | 121.7587 | 0.45462 | -121.8283 | 0.23554 | 0.32041 | 0.37397 | 0.3849 | -121.6683
1674.1562 | 121.875 | -0.3479 | 121.5637 | 1.4211e-13 | -0.038324 | 0.0020727 | 0.064073 | -0.0086727 | 0.052256 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020681 | 0.027493 | 0.016714 | -0.20498 | 0.13876 | -0.28311 | 121.6541 | 121.5479 | 121.4383 | -0.26911 | 0.019362 | 0.06904 | -0.065509 | -0.080318 | 0.013707 | 0.053537 | -0.10004 | 0.078791 | 0.090388 | 0.14292 | 0.064794 | -0.013997 | -0.01581 | -0.12542 | 0.24785 | -121.644 | 0.36726 | 0.28239 | 0.034536 | -121.55 | -121.5102 | 122.002 | 121.8958 | 121.7862 | 0.48667 | -121.8328 | 0.26758 | 0.36161 | 0.40144 | 0.41694 | -121.6638
1675.9062 | 121.8658 | -0.32959 | 121.5866 | 1.4211e-13 | -0.038752 | 0.0020727 | 0.064073 | -0.0086727 | 0.052469 | -0.01755 | -0.0046531 | -0.0010577 | 0.020681 | 0.027493 | 0.0165 | -0.20498 | 0.13876 | -0.27853 | 121.6541 | 121.5525 | 121.452 | -0.25995 | 0.014784 | 0.064461 | -0.065509 | -0.075739 | 0.013707 | 0.062694 | -0.10462 | 0.069639 | 0.0675 | 0.12461 | 0.051062 | -0.018577 | -0.034119 | -0.13457 | 0.22497 | -121.6623 | 0.34437 | 0.26408 | 0.039115 | -121.5729 | -121.5239 | 121.9837 | 121.8821 | 121.7816 | 0.46835 | -121.8466 | 0.25385 | 0.3433 | 0.39228 | 0.39405 | -121.6912
1677.6719 | 121.843 | -0.31586 | 121.6187 | 1.4211e-13 | -0.038324 | 0.0014317 | 0.064714 | -0.0084589 | 0.052683 | -0.0099192 | -0.0042257 | -0.0010577 | 0.020467 | 0.027493 | 0.0165 | -0.19582 | 0.13876 | -0.27395 | 121.6678 | 121.5571 | 121.4566 | -0.25995 | 0.023941 | 0.064461 | -0.056351 | -0.080318 | 0.004549 | 0.058115 | -0.10004 | 0.055906 | 0.049192 | 0.12003 | 0.041907 | -0.013999 | -0.061583 | -0.16203 | 0.21581 | -121.699 | 0.3398 | 0.25951 | 0.043694 | -121.6141 | -121.5605 | 121.9837 | 121.8729 | 121.7725 | 0.45462 | -121.8786 | 0.23554 | 0.32041 | 0.37397 | 0.38032 | -121.7187
1679.4375 | 121.8521 | -0.33875 | 121.6049 | 1.4211e-13 | -0.038538 | 0.0020727 | 0.064073 | -0.0086727 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020681 | 0.027493 | 0.0165 | -0.2004 | 0.14334 | -0.27853 | 121.6724 | 121.5571 | 121.452 | -0.25995 | 0.02852 | 0.06904 | -0.056351 | -0.071161 | 0.004549 | 0.058115 | -0.10004 | 0.078794 | 0.067504 | 0.13834 | 0.060217 | -0.018577 | -0.04785 | -0.15288 | 0.2387 | -121.6761 | 0.36727 | 0.28239 | 0.043694 | -121.6004 | -121.5468 | 122.0112 | 121.8958 | 121.7908 | 0.48209 | -121.8649 | 0.26758 | 0.34329 | 0.39686 | 0.40779 | -121.705
1681.2188 | 121.8887 | -0.31586 | 121.6141 | 1.4211e-13 | -0.038324 | 0.0020727 | 0.0645 | -0.0084589 | 0.052683 | -0.0099192 | -0.0046531 | -0.0010577 | 0.020681 | 0.02728 | 0.016714 | -0.19582 | 0.13876 | -0.27395 | 121.6724 | 121.5571 | 121.4566 | -0.25537 | 0.019362 | 0.06904 | -0.056351 | -0.071161 | 0.009128 | 0.053537 | -0.10004 | 0.060485 | 0.058348 | 0.12003 | 0.041907 | -0.018578 | -0.057006 | -0.15746 | 0.21581 | -121.6852 | 0.33522 | 0.25951 | 0.043694 | -121.6049 | -121.5605 | 121.9883 | 121.8729 | 121.7725 | 0.45462 | -121.8694 | 0.2447 | 0.32499 | 0.36939 | 0.3849 | -121.7141
1682.9219 | 121.9025 | -0.33875 | 121.5958 | 1.4211e-13 | -0.038538 | 0.0018589 | 0.064286 | -0.0084589 | 0.052683 | -0.02518 | -0.0044395 | -0.0014849 | 0.020467 | 0.027707 | 0.016714 | -0.19582 | 0.14334 | -0.26937 | 121.6724 | 121.5662 | 121.4612 | -0.25079 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | -2.9e-05 | 0.058115 | -0.095467 | 0.087952 | 0.076659 | 0.14292 | 0.069374 | -0.018578 | -0.029537 | -0.13457 | 0.24328 | -121.6761 | 0.36269 | 0.27782 | 0.034537 | -121.5958 | -121.5376 | 122.0112 | 121.905 | 121.7999 | 0.48209 | -121.8466 | 0.25843 | 0.33872 | 0.39686 | 0.41694 | -121.6912
1684.6875 | 121.9208 | -0.32959 | 121.5958 | 1.4211e-13 | -0.038324 | 0.0016453 | 0.064073 | -0.0086727 | 0.052683 | -0.01755 | -0.0046531 | -0.0010577 | 0.02004 | 0.02728 | 0.0165 | -0.19582 | 0.14334 | -0.27853 | 121.677 | 121.5662 | 121.4566 | -0.26453 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.009128 | 0.062694 | -0.10462 | 0.06506 | 0.081237 | 0.13377 | 0.051062 | -0.013998 | -0.029537 | -0.13915 | 0.22497 | -121.6669 | 0.35811 | 0.26866 | 0.043694 | -121.5866 | -121.5331 | 122.0066 | 121.8958 | 121.7862 | 0.47293 | -121.8603 | 0.25843 | 0.33872 | 0.39228 | 0.40779 | -121.7004
1686.4531 | 121.8521 | -0.38452 | 121.5912 | 1.4211e-13 | -0.038111 | 0.0020727 | 0.064286 | -0.0082453 | 0.052683 | -0.0022892 | -0.0046531 | -0.0012713 | 0.020467 | 0.027707 | 0.016714 | -0.21871 | 0.12961 | -0.28768 | 121.6495 | 121.5388 | 121.4383 | -0.27369 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.009128 | 0.067272 | -0.10004 | 0.11083 | 0.058344 | 0.16581 | 0.096837 | -0.013996 | -0.052434 | -0.15288 | 0.28448 | -121.6669 | 0.40846 | 0.32359 | 0.039115 | -121.5821 | -121.5239 | 122.0341 | 121.9233 | 121.8228 | 0.51413 | -121.8649 | 0.30878 | 0.39365 | 0.45179 | 0.45814 | -121.6912
1688.1562 | 121.9025 | -0.41657 | 121.5042 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.0645 | -0.0080317 | 0.052683 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020681 | 0.027707 | 0.016928 | -0.27366 | 0.13419 | -0.35178 | 121.5854 | 121.4746 | 121.3742 | -0.32864 | 0.019362 | 0.073618 | -0.056351 | -0.071161 | 0.009128 | 0.053537 | -0.10462 | 0.08793 | 0.081222 | 0.14291 | 0.064785 | -0.023145 | -0.029563 | -0.13001 | 0.31194 | -121.5754 | 0.43593 | 0.36021 | 0.048273 | -121.4951 | -121.4507 | 122.002 | 121.8912 | 121.7908 | 0.55075 | -121.8328 | 0.3454 | 0.42569 | 0.4701 | 0.49018 | -121.6088
1689.9219 | 121.9666 | -0.40283 | 121.463 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064073 | -0.0086727 | 0.052469 | 0.0053413 | -0.0044395 | -0.0012713 | 0.020467 | 0.027707 | 0.0165 | -0.3057 | 0.14334 | -0.38383 | 121.5625 | 121.4472 | 121.3513 | -0.35153 | 0.014784 | 0.06904 | -0.06093 | -0.071161 | 0.009128 | 0.048958 | -0.10462 | 0.051302 | 0.099529 | 0.097128 | 0.019004 | -0.032298 | -0.015838 | -0.1117 | 0.29821 | -121.5342 | 0.41762 | 0.3419 | 0.043694 | -121.4539 | -121.4141 | 121.9654 | 121.85 | 121.7541 | 0.54618 | -121.8145 | 0.33167 | 0.41196 | 0.45179 | 0.47187 | -121.5676
1691.625 | 121.8704 | -0.4303 | 121.4996 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.027707 | 0.016714 | -0.3057 | 0.14334 | -0.37467 | 121.5717 | 121.4563 | 121.3696 | -0.35153 | 0.019362 | 0.073618 | -0.06093 | -0.071161 | 0.009128 | 0.053537 | -0.095467 | 0.078768 | 0.072064 | 0.12459 | 0.055626 | -0.023142 | -0.043302 | -0.13001 | 0.33483 | -121.5708 | 0.44966 | 0.36937 | 0.034537 | -121.4905 | -121.4461 | 122.002 | 121.8866 | 121.7999 | 0.57364 | -121.8512 | 0.35914 | 0.43943 | 0.48384 | 0.50392 | -121.5951
1693.375 | 121.962 | -0.40283 | 121.4584 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.0645 | -0.0086727 | 0.052683 | -0.0022892 | -0.0048667 | -0.0016987 | 0.020467 | 0.027493 | 0.016714 | -0.31028 | 0.14334 | -0.38383 | 121.5534 | 121.4563 | 121.3467 | -0.36527 | 0.019362 | 0.073618 | -0.06093 | -0.075739 | 0.018285 | 0.058115 | -0.1092 | 0.037566 | 0.09495 | 0.092549 | 0.019004 | -0.018562 | -0.002103 | -0.1117 | 0.29363 | -121.5342 | 0.42219 | 0.3419 | 0.048273 | -121.4401 | -121.4003 | 121.9562 | 121.8592 | 121.7496 | 0.54618 | -121.8237 | 0.32709 | 0.42112 | 0.46095 | 0.47645 | -121.5676
1695.0781 | 121.994 | -0.41199 | 121.4493 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.0645 | -0.0084589 | 0.052683 | -0.0099192 | -0.0048667 | -0.0014849 | 0.020254 | 0.027493 | 0.016928 | -0.31486 | 0.13876 | -0.38383 | 121.5625 | 121.4472 | 121.3422 | -0.36527 | 0.023941 | 0.06904 | -0.065509 | -0.080318 | 0.009128 | 0.053537 | -0.10462 | 0.046721 | 0.11326 | 0.097126 | 0.028159 | -0.018562 | -0.002105 | -0.10713 | 0.30736 | -121.5296 | 0.43593 | 0.34648 | 0.039115 | -121.4402 | -121.3957 | 121.9745 | 121.8592 | 121.7541 | 0.55075 | -121.8145 | 0.33167 | 0.42112 | 0.46552 | 0.48103 | -121.5539
1696.8438 | 121.8842 | -0.44403 | 121.4813 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.0645 | -0.0084589 | 0.05311 | -0.01755 | -0.0044395 | -0.0010577 | 0.020254 | 0.027707 | 0.016714 | -0.31486 | 0.14334 | -0.38841 | 121.5534 | 121.4426 | 121.3422 | -0.36984 | 0.023941 | 0.073618 | -0.065509 | -0.071161 | 0.013707 | 0.058115 | -0.10462 | 0.074186 | 0.072062 | 0.12917 | 0.055624 | -0.018562 | -0.038727 | -0.13917 | 0.33941 | -121.5525 | 0.46797 | 0.37852 | 0.039115 | -121.4676 | -121.4232 | 121.9974 | 121.8866 | 121.7862 | 0.58737 | -121.8512 | 0.37287 | 0.45774 | 0.50215 | 0.51765 | -121.5859
1698.5312 | 121.962 | -0.40741 | 121.4493 | 1.4211e-13 | -0.038538 | 0.0020727 | 0.064286 | -0.0084589 | 0.052897 | -0.0022892 | -0.0046531 | -0.0012713 | 0.02004 | 0.027707 | 0.016928 | -0.31486 | 0.13419 | -0.39298 | 121.5534 | 121.4518 | 121.3467 | -0.36069 | 0.019362 | 0.059882 | -0.06093 | -0.071161 | 0.013707 | 0.048958 | -0.10462 | 0.046723 | 0.10411 | 0.092549 | 0.014425 | -0.032298 | 0.002474 | -0.10255 | 0.30279 | -121.5204 | 0.42677 | 0.34648 | 0.043694 | -121.4356 | -121.4003 | 121.9608 | 121.8592 | 121.7541 | 0.5416 | -121.81 | 0.33625 | 0.42112 | 0.45637 | 0.46729 | -121.5539
1700.2812 | 121.9666 | -0.40283 | 121.4676 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0046531 | -0.0010577 | 0.020467 | 0.027921 | 0.016714 | -0.31944 | 0.15708 | -0.39298 | 121.5534 | 121.4426 | 121.3467 | -0.36984 | 0.019362 | 0.073618 | -0.065509 | -0.071161 | 0.004549 | 0.053537 | -0.090888 | 0.032987 | 0.085795 | 0.083392 | 0.009847 | -0.02314 | -0.024994 | -0.12086 | 0.31194 | -121.5388 | 0.42219 | 0.33732 | 0.025379 | -121.463 | -121.4141 | 121.9562 | 121.8454 | 121.7496 | 0.55991 | -121.8374 | 0.33167 | 0.40738 | 0.45637 | 0.47645 | -121.5585
1701.9844 | 121.9116 | -0.44403 | 121.4813 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064073 | -0.0084589 | 0.052897 | -0.01755 | -0.0046531 | -0.0014849 | 0.020254 | 0.027707 | 0.016714 | -0.31486 | 0.14334 | -0.38383 | 121.5671 | 121.4518 | 121.3513 | -0.36984 | 0.023941 | 0.06904 | -0.065509 | -0.080318 | 0.009128 | 0.062694 | -0.10004 | 0.074186 | 0.085797 | 0.12917 | 0.060203 | -0.013983 | -0.029569 | -0.13001 | 0.34399 | -121.5616 | 0.46797 | 0.37852 | 0.034536 | -121.4722 | -121.4186 | 122.0112 | 121.8958 | 121.7953 | 0.58737 | -121.8512 | 0.36371 | 0.45316 | 0.50672 | 0.51307 | -121.5814
1703.75 | 121.8292 | -0.45319 | 121.4996 | 1.4211e-13 | -0.038965 | 0.0020727 | 0.064073 | -0.0086727 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.027707 | 0.0165 | -0.3286 | 0.14334 | -0.39756 | 121.5534 | 121.4472 | 121.3422 | -0.36984 | 0.019362 | 0.064461 | -0.056351 | -0.080318 | 0.018285 | 0.053537 | -0.10004 | 0.083341 | 0.053751 | 0.12459 | 0.055623 | -0.027718 | -0.052459 | -0.15748 | 0.35314 | -121.58 | 0.47255 | 0.39683 | 0.043694 | -121.4813 | -121.4461 | 122.0066 | 121.9004 | 121.7953 | 0.59653 | -121.8695 | 0.37287 | 0.47147 | 0.50672 | 0.51765 | -121.5997
1705.4375 | 121.843 | -0.44861 | 121.5179 | 1.4211e-13 | -0.038538 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020254 | 0.027493 | 0.016714 | -0.31944 | 0.14792 | -0.40214 | 121.5488 | 121.4334 | 121.3513 | -0.37442 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.048958 | -0.095467 | 0.074184 | 0.030862 | 0.12917 | 0.046466 | -0.027718 | -0.084506 | -0.16663 | 0.35314 | -121.5983 | 0.47255 | 0.38768 | 0.034537 | -121.5042 | -121.469 | 121.9974 | 121.882 | 121.7999 | 0.59653 | -121.8924 | 0.36829 | 0.46232 | 0.49757 | 0.52223 | -121.6134
1707.2031 | 121.9025 | -0.44403 | 121.4905 | 1.4211e-13 | -0.038538 | 0.0018589 | 0.064286 | -0.0084589 | 0.052469 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020254 | 0.027707 | 0.016714 | -0.32402 | 0.13876 | -0.40672 | 121.5488 | 121.4472 | 121.3422 | -0.37442 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.095467 | 0.069607 | 0.058327 | 0.12001 | 0.037311 | -0.032296 | -0.043304 | -0.14833 | 0.34856 | -121.5708 | 0.46339 | 0.3831 | 0.034537 | -121.4768 | -121.4278 | 121.9928 | 121.8912 | 121.7862 | 0.5828 | -121.8649 | 0.36371 | 0.45774 | 0.50672 | 0.51765 | -121.5859
1708.9531 | 121.8658 | -0.48065 | 121.4722 | 1.4211e-13 | -0.038538 | 0.0018589 | 0.0645 | -0.0084589 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020467 | 0.027493 | 0.016714 | -0.3286 | 0.14334 | -0.4113 | 121.5442 | 121.438 | 121.3376 | -0.379 | 0.014784 | 0.06904 | -0.056351 | -0.075739 | 0.009128 | 0.053537 | -0.10004 | 0.10165 | 0.07206 | 0.15206 | 0.069354 | -0.032295 | -0.034151 | -0.13459 | 0.38061 | -121.5479 | 0.49544 | 0.4243 | 0.043694 | -121.463 | -121.4186 | 122.0249 | 121.9187 | 121.8182 | 0.624 | -121.8512 | 0.40491 | 0.48978 | 0.53419 | 0.54969 | -121.5722
1710.7188 | 121.8658 | -0.47607 | 121.4951 | 1.4211e-13 | -0.038538 | 0.0014317 | 0.064714 | -0.0084589 | 0.052683 | -0.0099192 | -0.0048667 | -0.0012713 | 0.020254 | 0.027707 | 0.016714 | -0.32402 | 0.14792 | -0.40214 | 121.5625 | 121.438 | 121.3422 | -0.36984 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.058115 | -0.1092 | 0.10623 | 0.067486 | 0.15206 | 0.073932 | -0.032297 | -0.057039 | -0.1529 | 0.36687 | -121.5754 | 0.49544 | 0.41514 | 0.048273 | -121.4813 | -121.4369 | 122.0386 | 121.9141 | 121.8182 | 0.624 | -121.8649 | 0.39576 | 0.48978 | 0.53419 | 0.54969 | -121.6043
1712.4219 | 121.8842 | -0.47607 | 121.4767 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.063859 | -0.0084589 | 0.052897 | -0.0099192 | -0.0046531 | -0.0016987 | 0.020254 | 0.027707 | 0.016714 | -0.31944 | 0.14792 | -0.40672 | 121.5442 | 121.4426 | 121.3422 | -0.379 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.004549 | 0.044379 | -0.10462 | 0.097071 | 0.067482 | 0.15663 | 0.069354 | -0.027717 | -0.03415 | -0.13459 | 0.37145 | -121.5525 | 0.50001 | 0.41514 | 0.043694 | -121.4722 | -121.4324 | 122.0203 | 121.9187 | 121.8182 | 0.624 | -121.8557 | 0.40033 | 0.48062 | 0.52045 | 0.54969 | -121.5814
1714.1719 | 121.8887 | -0.4715 | 121.4676 | 1.4211e-13 | -0.038538 | 0.0018589 | 0.0645 | -0.0082453 | 0.052897 | -0.01755 | -0.0048667 | -0.0012713 | 0.02004 | 0.027707 | 0.016287 | -0.33775 | 0.1525 | -0.4113 | 121.5396 | 121.4426 | 121.3376 | -0.38816 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.048958 | -0.10004 | 0.083336 | 0.07206 | 0.13374 | 0.060199 | -0.023137 | -0.024994 | -0.13002 | 0.37145 | -121.5525 | 0.49544 | 0.41057 | 0.039115 | -121.4493 | -121.4186 | 122.0111 | 121.9141 | 121.8091 | 0.624 | -121.8558 | 0.3866 | 0.48978 | 0.52046 | 0.54969 | -121.5676
1715.9219 | 121.907 | -0.50812 | 121.4264 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.064073 | -0.0086727 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.027493 | 0.016714 | -0.38811 | 0.14334 | -0.46166 | 121.4893 | 121.3831 | 121.2826 | -0.42937 | 0.023941 | 0.06904 | -0.070087 | -0.075739 | 0.013707 | 0.062694 | -0.10004 | 0.078747 | 0.062895 | 0.12 | 0.046459 | -0.032288 | -0.043322 | -0.14376 | 0.40807 | -121.5021 | 0.53206 | 0.43803 | 0.029958 | -121.4127 | -121.3637 | 121.9974 | 121.8912 | 121.7907 | 0.65146 | -121.8558 | 0.43238 | 0.52182 | 0.57081 | 0.57716 | -121.5264
1717.625 | 121.8658 | -0.52643 | 121.463 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.0645 | -0.0084589 | 0.05311 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020254 | 0.02728 | 0.016714 | -0.37896 | 0.14792 | -0.45708 | 121.4939 | 121.3922 | 121.2964 | -0.42479 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.013707 | 0.053537 | -0.1092 | 0.10164 | 0.030853 | 0.14747 | 0.069347 | -0.032289 | -0.070785 | -0.16665 | 0.41723 | -121.5342 | 0.54579 | 0.46092 | 0.043694 | -121.4493 | -121.4095 | 122.0203 | 121.9187 | 121.8228 | 0.67435 | -121.8878 | 0.45527 | 0.54014 | 0.57997 | 0.60462 | -121.5722
1719.375 | 121.9528 | -0.46692 | 121.3943 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064286 | -0.0084589 | 0.05311 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020254 | 0.027921 | 0.016714 | -0.37438 | 0.1525 | -0.44792 | 121.503 | 121.3968 | 121.3055 | -0.42479 | 0.014784 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.053537 | -0.10004 | 0.042127 | 0.10867 | 0.092539 | 0.018995 | -0.023132 | 0.002458 | -0.088824 | 0.36687 | -121.4747 | 0.4817 | 0.40141 | 0.034536 | -121.3806 | -121.3408 | 121.9699 | 121.8637 | 121.7724 | 0.61942 | -121.8191 | 0.3866 | 0.48063 | 0.52046 | 0.54054 | -121.4944
1721.125 | 121.8521 | -0.50812 | 121.463 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.064286 | -0.0082453 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.027921 | 0.016928 | -0.36522 | 0.14792 | -0.44792 | 121.5076 | 121.4014 | 121.3101 | -0.41106 | 0.019362 | 0.064461 | -0.065509 | -0.084896 | 0.009128 | 0.058115 | -0.10004 | 0.097062 | 0.044588 | 0.14289 | 0.060194 | -0.036868 | -0.061628 | -0.15291 | 0.40807 | -121.5479 | 0.52748 | 0.44261 | 0.034536 | -121.4539 | -121.4049 | 122.0157 | 121.9095 | 121.8182 | 0.65604 | -121.8741 | 0.42322 | 0.51725 | 0.56623 | 0.57258 | -121.5631
1722.8281 | 122.0123 | -0.44861 | 121.431 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | -0.01755 | -0.0044395 | -0.0012713 | 0.020681 | 0.027707 | 0.016714 | -0.36064 | 0.15708 | -0.43877 | 121.5213 | 121.4105 | 121.3238 | -0.40648 | 0.023941 | 0.06904 | -0.051772 | -0.075739 | 0.009128 | 0.048958 | -0.10462 | 0.042131 | 0.090367 | 0.087963 | 0.00984 | -0.032291 | -0.020426 | -0.10713 | 0.34398 | -121.5067 | 0.47255 | 0.39684 | 0.052852 | -121.4218 | -121.382 | 121.9699 | 121.8592 | 121.7724 | 0.60569 | -121.8374 | 0.37287 | 0.45774 | 0.49757 | 0.51765 | -121.5356
1724.5938 | 122.0032 | -0.37994 | 121.5225 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.064073 | -0.0082453 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020254 | 0.027493 | 0.016928 | -0.28281 | 0.14792 | -0.36094 | 121.6037 | 121.4975 | 121.3971 | -0.33321 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.009128 | 0.048958 | -0.10462 | 0.04673 | 0.081225 | 0.097131 | 0.019007 | -0.027723 | -0.024979 | -0.12543 | 0.27532 | -121.6028 | 0.39931 | 0.31901 | 0.043694 | -121.5134 | -121.4736 | 121.9837 | 121.8775 | 121.777 | 0.52787 | -121.8557 | 0.29963 | 0.38907 | 0.4289 | 0.45356 | -121.6271
1726.3594 | 121.9254 | -0.32959 | 121.6003 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.0645 | -0.0084589 | 0.052683 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020254 | 0.027707 | 0.016714 | -0.21871 | 0.14792 | -0.29226 | 121.6633 | 121.5525 | 121.4612 | -0.27827 | 0.019362 | 0.073618 | -0.06093 | -0.071161 | 0.009128 | 0.053537 | -0.095467 | 0.051323 | 0.062924 | 0.11088 | 0.037327 | -0.013996 | -0.047852 | -0.13914 | 0.23412 | -121.6715 | 0.34895 | 0.26866 | 0.034537 | -121.5912 | -121.5468 | 121.9929 | 121.8821 | 121.7908 | 0.47751 | -121.8786 | 0.25843 | 0.33872 | 0.38313 | 0.40321 | -121.6958
1728.0625 | 121.9894 | -0.29755 | 121.6095 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.064286 | -0.0088863 | 0.052683 | -0.0099192 | -0.0046531 | -0.0012713 | 0.020254 | 0.027921 | 0.016928 | -0.19582 | 0.13876 | -0.26479 | 121.6999 | 121.5845 | 121.4887 | -0.25079 | 0.023941 | 0.064461 | -0.065509 | -0.075739 | 0.022864 | 0.058115 | -0.095467 | 0.046753 | 0.090396 | 0.10172 | 0.032753 | -0.014 | -0.024955 | -0.12083 | 0.20208 | -121.6852 | 0.32149 | 0.23204 | 0.029958 | -121.5866 | -121.5514 | 121.9974 | 121.8821 | 121.7862 | 0.43631 | -121.8603 | 0.22181 | 0.32041 | 0.35566 | 0.36201 | -121.705
1729.8281 | 121.9254 | -0.32044 | 121.6415 | 1.4211e-13 | -0.038752 | 0.0014317 | 0.064286 | -0.0084589 | 0.052897 | -0.01755 | -0.0044395 | -0.0012713 | 0.020467 | 0.027493 | 0.0165 | -0.18667 | 0.14792 | -0.26021 | 121.6999 | 121.5937 | 121.4978 | -0.24621 | 0.019362 | 0.06904 | -0.06093 | -0.071161 | 0.018285 | 0.058115 | -0.095467 | 0.074221 | 0.058352 | 0.13377 | 0.06022 | -0.014001 | -0.047841 | -0.14372 | 0.22497 | -121.7127 | 0.3398 | 0.25951 | 0.034537 | -121.6233 | -121.5834 | 122.0203 | 121.9141 | 121.8183 | 0.46836 | -121.8878 | 0.24927 | 0.33872 | 0.37855 | 0.38948 | -121.737
1731.5156 | 121.9894 | -0.27924 | 121.6141 | 1.4211e-13 | -0.038538 | 0.0016453 | 0.0645 | -0.0086727 | 0.052256 | -0.0099192 | -0.0046531 | -0.0012713 | 0.02004 | 0.027493 | 0.016287 | -0.17293 | 0.14792 | -0.25106 | 121.7045 | 121.6074 | 121.5024 | -0.24163 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.009128 | 0.058115 | -0.1092 | 0.037601 | 0.090397 | 0.1063 | 0.028178 | -0.009423 | -0.006638 | -0.11167 | 0.17003 | -121.6898 | 0.30318 | 0.21831 | 0.048273 | -121.6049 | -121.556 | 121.9837 | 121.8867 | 121.7816 | 0.42716 | -121.8557 | 0.2035 | 0.28836 | 0.33735 | 0.35285 | -121.7233
1733.2656 | 121.9528 | -0.27008 | 121.6507 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064286 | -0.0082453 | 0.052683 | 0.0053413 | -0.0046531 | -0.0012713 | 0.020254 | 0.027493 | 0.0165 | -0.17751 | 0.14792 | -0.25106 | 121.7182 | 121.6074 | 121.507 | -0.2279 | 0.014784 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.058115 | -0.10004 | 0.042182 | 0.067511 | 0.092571 | 0.019023 | -0.023159 | -0.043259 | -0.14371 | 0.17004 | -121.731 | 0.28487 | 0.20915 | 0.039115 | -121.637 | -121.5926 | 121.9883 | 121.8775 | 121.7771 | 0.418 | -121.8786 | 0.18976 | 0.28379 | 0.3282 | 0.3437 | -121.7507
1734.9531 | 121.9666 | -0.27466 | 121.6232 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.064286 | -0.0084589 | 0.05311 | -0.0099192 | -0.0046531 | -0.0012713 | 0.02004 | 0.027921 | 0.0165 | -0.18209 | 0.14334 | -0.25106 | 121.7136 | 121.6029 | 121.5024 | -0.23706 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.037602 | 0.090398 | 0.09257 | 0.0236 | -0.014002 | -0.020372 | -0.12083 | 0.17003 | -121.7127 | 0.2986 | 0.20915 | 0.039115 | -121.6095 | -121.5651 | 121.9883 | 121.8775 | 121.7771 | 0.418 | -121.8603 | 0.18518 | 0.28837 | 0.33277 | 0.34828 | -121.7279
1736.7188 | 121.9116 | -0.3067 | 121.6461 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.064286 | -0.0084589 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020467 | 0.028134 | 0.016928 | -0.18209 | 0.14792 | -0.24648 | 121.7045 | 121.6029 | 121.5024 | -0.23248 | 0.014784 | 0.064461 | -0.065509 | -0.089475 | 0.009128 | 0.053537 | -0.10462 | 0.074225 | 0.058354 | 0.12461 | 0.060222 | -0.014003 | -0.04326 | -0.14371 | 0.20208 | -121.7356 | 0.32149 | 0.24119 | 0.039115 | -121.637 | -121.5926 | 122.0112 | 121.9096 | 121.8091 | 0.45462 | -121.8786 | 0.21723 | 0.31583 | 0.36024 | 0.37116 | -121.7507
1738.4844 | 122.0123 | -0.27924 | 121.6049 | 1.4211e-13 | -0.038752 | 0.0020727 | 0.0645 | -0.0086727 | 0.052683 | -0.0022892 | -0.0046531 | -0.0010577 | 0.02004 | 0.027493 | 0.0165 | -0.19582 | 0.15708 | -0.27395 | 121.6953 | 121.5937 | 121.4887 | -0.25537 | 0.023941 | 0.06904 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.023864 | 0.090396 | 0.083413 | 0.005286 | -0.018578 | -0.011219 | -0.11625 | 0.17461 | -121.6944 | 0.30318 | 0.21373 | 0.039115 | -121.5912 | -121.5468 | 121.9746 | 121.8729 | 121.7679 | 0.43632 | -121.8603 | 0.18976 | 0.29294 | 0.33735 | 0.34828 | -121.7095
1740.2344 | 122.0123 | -0.29755 | 121.5866 | 1.4211e-13 | -0.038965 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.027707 | 0.0165 | -0.21414 | 0.14334 | -0.28768 | 121.6724 | 121.5662 | 121.4841 | -0.25995 | 0.023941 | 0.073618 | -0.070087 | -0.089475 | 0.009128 | 0.058115 | -0.10004 | 0.037595 | 0.085814 | 0.083409 | 0.009862 | -0.027733 | -0.020382 | -0.10252 | 0.1975 | -121.6761 | 0.32149 | 0.22746 | 0.029958 | -121.5775 | -121.5285 | 121.97 | 121.8638 | 121.7816 | 0.44089 | -121.8466 | 0.20807 | 0.30667 | 0.35566 | 0.37116 | -121.6867
1741.9844 | 121.9528 | -0.3067 | 121.6095 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.0645 | -0.0086727 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020467 | 0.02728 | 0.016928 | -0.2004 | 0.14334 | -0.28311 | 121.6999 | 121.5937 | 121.4932 | -0.25995 | 0.019362 | 0.073618 | -0.06093 | -0.094053 | 0.009128 | 0.058115 | -0.1092 | 0.046751 | 0.090396 | 0.1063 | 0.023596 | -0.023155 | -0.015797 | -0.11625 | 0.1975 | -121.7036 | 0.32606 | 0.24577 | 0.048273 | -121.6004 | -121.5514 | 122.0066 | 121.9004 | 121.7999 | 0.45004 | -121.8694 | 0.21265 | 0.31583 | 0.36482 | 0.38032 | -121.7187
1743.6875 | 121.9666 | -0.28381 | 121.6003 | 1.4211e-13 | -0.038752 | 0.0016453 | 0.0645 | -0.0084589 | 0.052469 | -0.0022892 | -0.0042257 | -0.0010577 | 0.020467 | 0.027921 | 0.016714 | -0.17751 | 0.15708 | -0.24648 | 121.7136 | 121.612 | 121.5161 | -0.23706 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.004549 | 0.058115 | -0.10004 | 0.046757 | 0.11329 | 0.1063 | 0.037333 | -0.009424 | 0.011674 | -0.084202 | 0.18377 | -121.6852 | 0.30775 | 0.2183 | 0.034536 | -121.5958 | -121.5422 | 121.9974 | 121.8958 | 121.8 | 0.44089 | -121.8374 | 0.19892 | 0.28836 | 0.34193 | 0.35743 | -121.7004
1745.4531 | 121.8796 | -0.32501 | 121.637 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.064286 | -0.0086727 | 0.052897 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020254 | 0.028134 | 0.0165 | -0.18209 | 0.1525 | -0.26479 | 121.6999 | 121.5983 | 121.5024 | -0.24621 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.044379 | -0.10004 | 0.078798 | 0.06293 | 0.14292 | 0.060219 | -0.018579 | -0.038684 | -0.13456 | 0.22497 | -121.7219 | 0.34895 | 0.2595 | 0.034536 | -121.6233 | -121.5926 | 122.0249 | 121.9233 | 121.8274 | 0.47751 | -121.8832 | 0.24012 | 0.33872 | 0.36939 | 0.39863 | -121.737
1747.2344 | 122.0123 | -0.25635 | 121.6232 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.027493 | 0.016714 | -0.17293 | 0.15708 | -0.25564 | 121.7136 | 121.6074 | 121.5161 | -0.23706 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.019292 | 0.090398 | 0.083417 | 0.000711 | -0.018581 | -0.015793 | -0.10709 | 0.1563 | -121.7081 | 0.27571 | 0.19542 | 0.039115 | -121.6095 | -121.5697 | 121.97 | 121.8638 | 121.7725 | 0.41343 | -121.8603 | 0.17145 | 0.27006 | 0.30989 | 0.32997 | -121.7233
1748.9844 | 121.9528 | -0.31586 | 121.5912 | 1.4211e-13 | -0.038752 | 0.0020727 | 0.064286 | -0.0086727 | 0.052683 | -0.01755 | -0.0042257 | -0.0012713 | 0.020467 | 0.027707 | 0.0165 | -0.20498 | 0.1525 | -0.28311 | 121.6862 | 121.5845 | 121.4887 | -0.26453 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.027442 | 0.062694 | -0.10004 | 0.051327 | 0.094971 | 0.11088 | 0.032751 | -0.018576 | -0.006645 | -0.10252 | 0.21581 | -121.6807 | 0.3398 | 0.25035 | 0.034536 | -121.5637 | -121.5285 | 122.002 | 121.9004 | 121.8045 | 0.46836 | -121.8557 | 0.22638 | 0.3433 | 0.37855 | 0.39405 | -121.6912
1750.7031 | 121.9986 | -0.32501 | 121.5775 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.064286 | -0.0080317 | 0.052683 | -0.0022892 | -0.0044395 | -0.0016987 | 0.020681 | 0.027707 | 0.016287 | -0.21871 | 0.14792 | -0.28311 | 121.6816 | 121.58 | 121.4887 | -0.27827 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.046745 | 0.10413 | 0.1063 | 0.041906 | -0.004839 | 0.002509 | -0.088785 | 0.22039 | -121.6624 | 0.34437 | 0.26408 | 0.043694 | -121.5637 | -121.5193 | 122.0066 | 121.905 | 121.8137 | 0.47293 | -121.8557 | 0.24012 | 0.33872 | 0.38313 | 0.39863 | -121.6821
1752.4688 | 121.907 | -0.35706 | 121.5775 | 1.4211e-13 | -0.038752 | 0.0014317 | 0.064714 | -0.0084589 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.02004 | 0.027707 | 0.016287 | -0.21871 | 0.1525 | -0.29684 | 121.677 | 121.5662 | 121.4704 | -0.27827 | 0.019362 | 0.078197 | -0.065509 | -0.098632 | 0.009128 | 0.053537 | -0.10004 | 0.078789 | 0.099547 | 0.13834 | 0.060215 | -0.018574 | -0.011227 | -0.1071 | 0.25701 | -121.6761 | 0.37642 | 0.29155 | 0.034536 | -121.5683 | -121.5239 | 122.0341 | 121.9233 | 121.8274 | 0.50956 | -121.8557 | 0.25842 | 0.36618 | 0.41059 | 0.43525 | -121.6775
1754.2188 | 121.907 | -0.35706 | 121.5912 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.0645 | -0.0084589 | 0.052897 | -0.0099192 | -0.0042257 | -0.0012713 | 0.02004 | 0.027921 | 0.0165 | -0.23245 | 0.1525 | -0.306 | 121.6633 | 121.5571 | 121.4658 | -0.292 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.009128 | 0.058115 | -0.095467 | 0.065052 | 0.072079 | 0.12461 | 0.051058 | -0.013994 | -0.034118 | -0.12541 | 0.26159 | -121.6807 | 0.381 | 0.29613 | 0.034537 | -121.5821 | -121.5331 | 122.0203 | 121.9141 | 121.8228 | 0.50956 | -121.8832 | 0.26758 | 0.36618 | 0.41517 | 0.43067 | -121.6867
1755.9844 | 121.8842 | -0.46234 | 121.5271 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.0645 | -0.0088863 | 0.052469 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.027707 | 0.016928 | -0.3286 | 0.14334 | -0.39756 | 121.5625 | 121.4655 | 121.365 | -0.37442 | 0.02852 | 0.06904 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.087917 | 0.035442 | 0.13375 | 0.064778 | -0.023139 | -0.06161 | -0.16205 | 0.3623 | -121.6166 | 0.49086 | 0.40141 | 0.039115 | -121.5134 | -121.469 | 122.0249 | 121.9278 | 121.8274 | 0.60568 | -121.9015 | 0.37287 | 0.47605 | 0.52046 | 0.53138 | -121.6271
1757.6875 | 122.0352 | -0.39368 | 121.4722 | 1.4211e-13 | -0.038752 | 0.0018589 | 0.0645 | -0.0086727 | 0.05311 | -0.01755 | -0.0042257 | -0.0016987 | 0.02004 | 0.027921 | 0.016287 | -0.31028 | 0.13876 | -0.39756 | 121.5809 | 121.4746 | 121.3788 | -0.36069 | 0.019362 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10004 | 0.03299 | 0.10869 | 0.083394 | -0.003886 | -0.036876 | 0.00248 | -0.093386 | 0.29363 | -121.5571 | 0.41304 | 0.32817 | 0.034536 | -121.4539 | -121.4095 | 121.9745 | 121.8683 | 121.7725 | 0.53244 | -121.8329 | 0.30878 | 0.41196 | 0.45637 | 0.4673 | -121.5722
1759.4531 | 122.0306 | -0.43488 | 121.431 | 1.4211e-13 | -0.039179 | 0.0020727 | 0.0645 | -0.0082453 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.028134 | 0.0165 | -0.33775 | 0.14792 | -0.4113 | 121.558 | 121.4563 | 121.3605 | -0.37442 | 0.019362 | 0.06904 | -0.065509 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.060451 | 0.12699 | 0.097122 | 0.023577 | -0.036874 | 0.025363 | -0.070501 | 0.33483 | -121.5204 | 0.45424 | 0.36937 | 0.034536 | -121.4218 | -121.3683 | 121.9928 | 121.8912 | 121.7953 | 0.5828 | -121.8054 | 0.3454 | 0.444 | 0.49757 | 0.50392 | -121.531
1761.2188 | 122.0123 | -0.42572 | 121.4447 | 1.4211e-13 | -0.038965 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020467 | 0.027921 | 0.016714 | -0.3286 | 0.14792 | -0.39756 | 121.5625 | 121.4655 | 121.3742 | -0.379 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.046717 | 0.11784 | 0.097124 | 0.028157 | -0.01856 | 0.020788 | -0.070499 | 0.32567 | -121.5296 | 0.44966 | 0.36479 | 0.039115 | -121.431 | -121.3866 | 121.9883 | 121.8912 | 121.7999 | 0.57364 | -121.8237 | 0.34082 | 0.43943 | 0.48384 | 0.50392 | -121.5447
1762.9844 | 122.0032 | -0.42114 | 121.4905 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.064286 | -0.0086727 | 0.05311 | -0.02518 | -0.0044395 | -0.0014849 | 0.020467 | 0.027921 | 0.016714 | -0.32402 | 0.16166 | -0.40672 | 121.5625 | 121.4655 | 121.3696 | -0.37442 | 0.02852 | 0.073618 | -0.065509 | -0.089475 | 0.004549 | 0.058115 | -0.10004 | 0.046719 | 0.072063 | 0.097125 | 0.014423 | -0.032296 | -0.024989 | -0.12085 | 0.3211 | -121.58 | 0.44966 | 0.35563 | 0.034536 | -121.4859 | -121.4324 | 121.9837 | 121.8866 | 121.7908 | 0.5828 | -121.8649 | 0.33167 | 0.42569 | 0.47926 | 0.49476 | -121.5905
1764.6875 | 121.9757 | -0.41657 | 121.4996 | 1.4211e-13 | -0.039179 | 0.0020727 | 0.0645 | -0.0084589 | 0.052897 | -0.01755 | -0.0044395 | -0.0016987 | 0.020254 | 0.027707 | 0.016714 | -0.32402 | 0.1525 | -0.39756 | 121.5809 | 121.4701 | 121.3788 | -0.36984 | 0.019362 | 0.073618 | -0.056351 | -0.084896 | -2.9e-05 | 0.058115 | -0.1092 | 0.04672 | 0.081221 | 0.092547 | 0.019002 | -0.027718 | -0.029565 | -0.12085 | 0.30736 | -121.5845 | 0.43593 | 0.36021 | 0.052852 | -121.4997 | -121.4415 | 121.9974 | 121.8866 | 121.7953 | 0.56907 | -121.8695 | 0.33167 | 0.41654 | 0.47468 | 0.49018 | -121.6088
1766.4531 | 121.9025 | -0.46234 | 121.4996 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0046531 | -0.0016987 | 0.020254 | 0.027921 | 0.0165 | -0.32402 | 0.1525 | -0.40214 | 121.5717 | 121.4792 | 121.3788 | -0.37442 | 0.019362 | 0.073618 | -0.056351 | -0.089475 | 0.009128 | 0.053537 | -0.10004 | 0.087917 | 0.072064 | 0.13832 | 0.060199 | -0.027718 | -0.020407 | -0.12085 | 0.3623 | -121.5891 | 0.4817 | 0.40599 | 0.043694 | -121.4905 | -121.4461 | 122.034 | 121.9416 | 121.8411 | 0.61484 | -121.8741 | 0.37287 | 0.47147 | 0.51588 | 0.53596 | -121.5997
1768.2188 | 121.994 | -0.40283 | 121.4813 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020254 | 0.027921 | 0.0165 | -0.31486 | 0.16166 | -0.38383 | 121.5809 | 121.4792 | 121.3879 | -0.36069 | 0.02852 | 0.064461 | -0.065509 | -0.089475 | 0.004549 | 0.058115 | -0.10004 | 0.042145 | 0.099532 | 0.087971 | 0.019004 | -0.023141 | -0.002096 | -0.093384 | 0.30279 | -121.5708 | 0.43135 | 0.33732 | 0.034536 | -121.4768 | -121.4232 | 121.9837 | 121.8821 | 121.7908 | 0.56449 | -121.842 | 0.31336 | 0.40738 | 0.46095 | 0.46729 | -121.5814
1769.9688 | 121.8933 | -0.44861 | 121.5363 | 1.4211e-13 | -0.038965 | 0.0014317 | 0.064286 | -0.0084589 | 0.052683 | -0.01755 | -0.0042257 | -0.0010577 | 0.020254 | 0.027921 | 0.0165 | -0.31486 | 0.1525 | -0.38383 | 121.5809 | 121.4838 | 121.3788 | -0.36527 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | -2.9e-05 | 0.062694 | -0.095467 | 0.083342 | 0.0446 | 0.13375 | 0.06478 | -0.018562 | -0.052449 | -0.15747 | 0.35314 | -121.6257 | 0.46339 | 0.38768 | 0.034537 | -121.5363 | -121.4736 | 122.0295 | 121.9324 | 121.8274 | 0.60111 | -121.9015 | 0.35913 | 0.44858 | 0.5113 | 0.52223 | -121.6317
1771.6562 | 121.9116 | -0.36621 | 121.5729 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064286 | -0.0082453 | 0.052897 | -0.01755 | -0.0042257 | -0.0014849 | 0.020467 | 0.027493 | 0.0165 | -0.24618 | 0.16166 | -0.32889 | 121.6541 | 121.5525 | 121.4566 | -0.29658 | 0.02852 | 0.078197 | -0.06093 | -0.089475 | 0.009128 | 0.053537 | -0.10004 | 0.069629 | 0.081233 | 0.12003 | 0.037322 | -0.032307 | -0.020386 | -0.11626 | 0.26617 | -121.6624 | 0.39473 | 0.30528 | 0.039115 | -121.5637 | -121.5193 | 122.0203 | 121.9187 | 121.8228 | 0.52787 | -121.8695 | 0.27674 | 0.37534 | 0.41975 | 0.44441 | -121.6729
1773.4219 | 122.0306 | -0.28839 | 121.5775 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.064286 | -0.0088863 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020254 | 0.027707 | 0.016714 | -0.20956 | 0.1525 | -0.28311 | 121.6862 | 121.58 | 121.4887 | -0.26911 | 0.033099 | 0.078197 | -0.06093 | -0.094053 | 0.009128 | 0.048958 | -0.10004 | 0.019282 | 0.1087 | 0.078833 | 0.005285 | -0.013997 | 0.002509 | -0.088785 | 0.18835 | -121.6715 | 0.32149 | 0.22746 | 0.039115 | -121.5683 | -121.5285 | 121.9745 | 121.8684 | 121.7771 | 0.44089 | -121.8466 | 0.19434 | 0.29752 | 0.33735 | 0.36659 | -121.6775
1775.1875 | 122.0078 | -0.36621 | 121.5225 | 1.4211e-13 | -0.039179 | 0.0020727 | 0.0645 | -0.0086727 | 0.052897 | -0.01755 | -0.0044395 | -0.0014849 | 0.020681 | 0.028134 | 0.016714 | -0.28739 | 0.1525 | -0.36551 | 121.6083 | 121.5067 | 121.4108 | -0.34237 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.058115 | -0.10004 | 0.023839 | 0.085803 | 0.07882 | 0.000696 | -0.023143 | -0.015821 | -0.11169 | 0.26617 | -121.6074 | 0.39473 | 0.3007 | 0.034536 | -121.5042 | -121.4644 | 121.9745 | 121.8729 | 121.777 | 0.51871 | -121.8649 | 0.28131 | 0.3845 | 0.42433 | 0.43983 | -121.6226
1776.9375 | 121.9025 | -0.45319 | 121.5271 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.0645 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0016987 | 0.020467 | 0.027921 | 0.016287 | -0.31028 | 0.16166 | -0.38841 | 121.5854 | 121.493 | 121.3925 | -0.36069 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.092499 | 0.058333 | 0.1429 | 0.064779 | -0.02772 | -0.034136 | -0.13458 | 0.35314 | -121.612 | 0.47713 | 0.39226 | 0.039115 | -121.5134 | -121.469 | 122.0386 | 121.9462 | 121.8457 | 0.61484 | -121.8878 | 0.36829 | 0.46689 | 0.5113 | 0.53138 | -121.6271
1778.6562 | 122.0352 | -0.3891 | 121.4951 | 1.4211e-13 | -0.039179 | 0.0020727 | 0.0645 | -0.0082453 | 0.052683 | -0.0099192 | -0.0046531 | -0.0016987 | 0.020467 | 0.027921 | 0.0165 | -0.29655 | 0.15708 | -0.37467 | 121.6037 | 121.4975 | 121.3971 | -0.35153 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.048958 | -0.095467 | 0.037569 | 0.10869 | 0.092551 | 0.014427 | -0.023142 | 0.002487 | -0.09796 | 0.29363 | -121.5845 | 0.40388 | 0.32817 | 0.034537 | -121.4813 | -121.4461 | 121.9928 | 121.8866 | 121.7862 | 0.54618 | -121.8466 | 0.29962 | 0.40281 | 0.43806 | 0.46272 | -121.5905
1780.4062 | 121.9254 | -0.4303 | 121.5179 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.0645 | -0.0084589 | 0.052897 | 0.0053413 | -0.0044395 | -0.0012713 | 0.020254 | 0.027921 | 0.016714 | -0.30113 | 0.15708 | -0.37467 | 121.5992 | 121.5113 | 121.4063 | -0.35611 | 0.019362 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10004 | 0.07419 | 0.081225 | 0.12917 | 0.055626 | -0.018564 | -0.006664 | -0.11169 | 0.33025 | -121.6028 | 0.44966 | 0.36479 | 0.034536 | -121.4997 | -121.4553 | 122.0295 | 121.9416 | 121.8366 | 0.58738 | -121.8741 | 0.3454 | 0.44858 | 0.49299 | 0.50392 | -121.618
1782.1562 | 121.8704 | -0.4303 | 121.582 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.064286 | -0.0088863 | 0.052683 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020254 | 0.027921 | 0.016287 | -0.30113 | 0.16166 | -0.36551 | 121.6129 | 121.5113 | 121.42 | -0.34695 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.062694 | -0.10462 | 0.083347 | 0.030873 | 0.12917 | 0.064783 | -0.018564 | -0.070751 | -0.16204 | 0.32567 | -121.6715 | 0.44508 | 0.36937 | 0.043694 | -121.5683 | -121.5193 | 122.0432 | 121.9416 | 121.8503 | 0.59196 | -121.929 | 0.34082 | 0.44401 | 0.49299 | 0.50392 | -121.6867
1783.9219 | 121.9757 | -0.40283 | 121.5408 | 1.4211e-13 | -0.039179 | 0.0020727 | 0.064286 | -0.0084589 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020254 | 0.027921 | 0.016287 | -0.29197 | 0.16166 | -0.36094 | 121.6266 | 121.5113 | 121.42 | -0.34237 | 0.033099 | 0.06904 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.10004 | 0.06046 | 0.085806 | 0.11086 | 0.041895 | -0.018565 | -0.029553 | -0.12084 | 0.30279 | -121.6303 | 0.43593 | 0.3419 | 0.039115 | -121.5225 | -121.4827 | 122.0295 | 121.9141 | 121.8228 | 0.56449 | -121.8832 | 0.31336 | 0.42112 | 0.46095 | 0.47187 | -121.6409
1785.625 | 122.0123 | -0.36621 | 121.5363 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.064714 | -0.0086727 | 0.052683 | -0.0022892 | -0.0040121 | -0.0012713 | 0.020467 | 0.028134 | 0.0165 | -0.29197 | 0.15708 | -0.35636 | 121.6175 | 121.5159 | 121.42 | -0.33779 | 0.023941 | 0.06904 | -0.070087 | -0.089475 | 0.018285 | 0.053537 | -0.1092 | 0.028418 | 0.081227 | 0.074242 | 0.009852 | -0.018566 | -0.020397 | -0.11627 | 0.25701 | -121.6257 | 0.39015 | 0.29612 | 0.039116 | -121.518 | -121.4827 | 121.9837 | 121.8821 | 121.7862 | 0.52329 | -121.874 | 0.27674 | 0.3845 | 0.41975 | 0.43525 | -121.6455
1787.375 | 121.9254 | -0.39368 | 121.5591 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.0645 | -0.0086727 | 0.052897 | -0.02518 | -0.0044395 | -0.0014849 | 0.02004 | 0.027921 | 0.016928 | -0.28281 | 0.1525 | -0.36094 | 121.6266 | 121.5204 | 121.4246 | -0.33779 | 0.023941 | 0.073618 | -0.065509 | -0.094053 | 0.018285 | 0.058115 | -0.10462 | 0.055884 | 0.067496 | 0.11086 | 0.03274 | -0.023144 | -0.038706 | -0.13458 | 0.28905 | -121.6532 | 0.41762 | 0.32817 | 0.039115 | -121.5409 | -121.501 | 122.0203 | 121.9141 | 121.8182 | 0.54618 | -121.8969 | 0.29962 | 0.41196 | 0.45179 | 0.4673 | -121.6638
1789.125 | 121.9528 | -0.38452 | 121.5317 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064928 | -0.0086727 | 0.052469 | -0.0022892 | -0.0046531 | -0.0014849 | 0.020254 | 0.027921 | 0.016714 | -0.27366 | 0.14792 | -0.35636 | 121.6312 | 121.525 | 121.4291 | -0.32864 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.055886 | 0.09954 | 0.11086 | 0.028162 | -0.027724 | -0.006661 | -0.10253 | 0.2799 | -121.6166 | 0.41304 | 0.31901 | 0.039115 | -121.5088 | -121.469 | 122.0157 | 121.9095 | 121.8137 | 0.53244 | -121.8603 | 0.29963 | 0.40738 | 0.44722 | 0.46272 | -121.6363
1790.8125 | 122.0306 | -0.37079 | 121.5637 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.064286 | -0.0086727 | 0.052683 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020254 | 0.028134 | 0.016714 | -0.27366 | 0.16624 | -0.35178 | 121.6358 | 121.5342 | 121.4383 | -0.31948 | 0.019362 | 0.06904 | -0.065509 | -0.089475 | 0.013707 | 0.053537 | -0.10004 | 0.051312 | 0.072075 | 0.097133 | 0.019009 | -0.032303 | -0.029547 | -0.12542 | 0.27074 | -121.6532 | 0.39015 | 0.30528 | 0.034536 | -121.55 | -121.5102 | 122.0066 | 121.905 | 121.8091 | 0.53702 | -121.8832 | 0.28131 | 0.3845 | 0.42433 | 0.43983 | -121.6638
1792.5 | 122.0123 | -0.36621 | 121.5591 | 1.4211e-13 | -0.039393 | 0.0014317 | 0.064286 | -0.0084589 | 0.052469 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020254 | 0.028134 | 0.0165 | -0.25992 | 0.16166 | -0.33805 | 121.6312 | 121.5342 | 121.4475 | -0.31948 | 0.019362 | 0.073618 | -0.056351 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.046734 | 0.072074 | 0.10629 | 0.028165 | -0.018569 | -0.024969 | -0.11168 | 0.26159 | -121.644 | 0.38557 | 0.30986 | 0.048273 | -121.5454 | -121.5056 | 121.9974 | 121.9004 | 121.8137 | 0.52787 | -121.8786 | 0.28131 | 0.37992 | 0.41975 | 0.43983 | -121.6638
1794.2656 | 121.8887 | -0.42114 | 121.5683 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.064286 | -0.0084589 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020254 | 0.027921 | 0.016714 | -0.26908 | 0.15708 | -0.35178 | 121.6404 | 121.5388 | 121.4475 | -0.31032 | 0.014784 | 0.078197 | -0.065509 | -0.094053 | 0.013707 | 0.058115 | -0.095467 | 0.11082 | 0.072076 | 0.15207 | 0.069363 | -0.041461 | -0.029545 | -0.12084 | 0.32568 | -121.6624 | 0.43593 | 0.35563 | 0.029958 | -121.5546 | -121.5102 | 122.0615 | 121.9599 | 121.8686 | 0.57822 | -121.8786 | 0.32709 | 0.43485 | 0.47926 | 0.49934 | -121.6638
1796.0156 | 121.8933 | -0.40741 | 121.5958 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.064714 | -0.0084589 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.028134 | 0.0165 | -0.25992 | 0.15708 | -0.33805 | 121.6495 | 121.5479 | 121.452 | -0.3149 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.092512 | 0.053767 | 0.14749 | 0.069364 | -0.023148 | -0.047853 | -0.14372 | 0.30279 | -121.6807 | 0.43593 | 0.34648 | 0.043694 | -121.5775 | -121.5331 | 122.0569 | 121.9553 | 121.8594 | 0.56449 | -121.9107 | 0.32251 | 0.42569 | 0.4701 | 0.48561 | -121.7004
1797.7188 | 122.0169 | -0.36621 | 121.5637 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.0645 | -0.0088863 | 0.052469 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.027707 | 0.0165 | -0.25534 | 0.16166 | -0.32431 | 121.6541 | 121.5525 | 121.4612 | -0.31032 | 0.023941 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.10004 | 0.055892 | 0.090388 | 0.11087 | 0.0419 | -0.013992 | -0.011231 | -0.10252 | 0.26617 | -121.644 | 0.39015 | 0.3007 | 0.034536 | -121.55 | -121.5056 | 122.0203 | 121.9187 | 121.8274 | 0.52787 | -121.874 | 0.28589 | 0.37992 | 0.42433 | 0.43983 | -121.6638
1799.4844 | 121.9208 | -0.36621 | 121.5958 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.064073 | -0.0086727 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.020254 | 0.027921 | 0.0165 | -0.24161 | 0.1525 | -0.32889 | 121.6678 | 121.5616 | 121.4658 | -0.30574 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.10004 | 0.060471 | 0.07208 | 0.1246 | 0.037322 | -0.023149 | -0.034116 | -0.12999 | 0.26617 | -121.6852 | 0.38557 | 0.30528 | 0.039115 | -121.5729 | -121.5376 | 122.0341 | 121.9279 | 121.832 | 0.51871 | -121.9015 | 0.27674 | 0.38908 | 0.42433 | 0.43983 | -121.6958
1801.25 | 121.9345 | -0.37994 | 121.6049 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.0645 | -0.0086727 | 0.052683 | -0.0022892 | -0.0040121 | -0.0014849 | 0.020254 | 0.028134 | 0.016714 | -0.25076 | 0.16166 | -0.32889 | 121.6541 | 121.5571 | 121.4612 | -0.30574 | 0.023941 | 0.06904 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.095467 | 0.074204 | 0.04919 | 0.12918 | 0.051055 | -0.023149 | -0.04785 | -0.14372 | 0.28448 | -121.6944 | 0.40388 | 0.31444 | 0.029958 | -121.5912 | -121.5468 | 122.0341 | 121.937 | 121.8411 | 0.5416 | -121.9107 | 0.29047 | 0.39365 | 0.43806 | 0.44898 | -121.7004
1802.9688 | 121.907 | -0.3891 | 121.6003 | 1.4211e-13 | -0.039606 | 0.0020727 | 0.0645 | -0.0086727 | 0.052469 | -0.01755 | -0.0042257 | -0.0019123 | 0.02004 | 0.028134 | 0.0165 | -0.25534 | 0.16166 | -0.32889 | 121.6633 | 121.5616 | 121.4566 | -0.30574 | 0.019362 | 0.06904 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.10462 | 0.083359 | 0.062924 | 0.13376 | 0.06021 | -0.023149 | -0.038694 | -0.14372 | 0.28447 | -121.6898 | 0.40846 | 0.32817 | 0.043694 | -121.5775 | -121.5422 | 122.0524 | 121.9507 | 121.8457 | 0.55076 | -121.9061 | 0.29962 | 0.41196 | 0.44721 | 0.45814 | -121.705
1804.7188 | 121.907 | -0.40283 | 121.6095 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.064714 | -0.0086727 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.028134 | 0.016287 | -0.25076 | 0.16166 | -0.32889 | 121.6633 | 121.5571 | 121.4658 | -0.30116 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.10167 | 0.053769 | 0.15207 | 0.073943 | -0.027728 | -0.052428 | -0.14372 | 0.30279 | -121.6944 | 0.42677 | 0.33732 | 0.034536 | -121.5958 | -121.5514 | 122.0661 | 121.9599 | 121.8686 | 0.56449 | -121.9107 | 0.31794 | 0.41654 | 0.46095 | 0.47645 | -121.7095
1806.4062 | 121.9025 | -0.37079 | 121.6003 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.0645 | -0.0088863 | 0.052469 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.028348 | 0.016928 | -0.24161 | 0.16166 | -0.31515 | 121.6724 | 121.5754 | 121.4795 | -0.30116 | 0.033099 | 0.064461 | -0.070087 | -0.094053 | 0.013707 | 0.062694 | -0.095467 | 0.069628 | 0.072081 | 0.12918 | 0.055635 | -0.013993 | -0.024958 | -0.12083 | 0.27532 | -121.6944 | 0.40389 | 0.3007 | 0.02538 | -121.5866 | -121.5376 | 122.0432 | 121.9462 | 121.8503 | 0.53245 | -121.9015 | 0.27674 | 0.3845 | 0.43348 | 0.43525 | -121.6958
1808.1562 | 121.8979 | -0.37079 | 121.5912 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.0645 | -0.0088863 | 0.05311 | -0.0022892 | -0.0040121 | -0.0014849 | 0.020254 | 0.028134 | 0.016287 | -0.24161 | 0.16624 | -0.31973 | 121.677 | 121.58 | 121.4749 | -0.30116 | 0.023941 | 0.06904 | -0.070087 | -0.094053 | 0.009128 | 0.058115 | -0.10462 | 0.069628 | 0.085814 | 0.12918 | 0.051057 | -0.018571 | -0.011224 | -0.11625 | 0.26616 | -121.6852 | 0.39473 | 0.3007 | 0.034537 | -121.5821 | -121.5331 | 122.0478 | 121.9508 | 121.8457 | 0.53702 | -121.8923 | 0.27674 | 0.37992 | 0.4289 | 0.43983 | -121.6958
1809.9062 | 121.9025 | -0.37994 | 121.6278 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.0645 | -0.0088863 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020254 | 0.027921 | 0.0165 | -0.23245 | 0.16166 | -0.306 | 121.6816 | 121.5754 | 121.4932 | -0.292 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.004549 | 0.058115 | -0.10004 | 0.08794 | 0.053772 | 0.14749 | 0.073946 | -0.013994 | -0.052424 | -0.13456 | 0.2799 | -121.7127 | 0.40388 | 0.31901 | 0.039115 | -121.6233 | -121.5697 | 122.0615 | 121.9553 | 121.8732 | 0.5416 | -121.9198 | 0.29505 | 0.38449 | 0.43806 | 0.44898 | -121.7279
1811.6719 | 121.9711 | -0.35706 | 121.6095 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.064714 | -0.0088863 | 0.052469 | -0.01755 | -0.0042257 | -0.0010577 | 0.020467 | 0.028134 | 0.0165 | -0.22787 | 0.17081 | -0.306 | 121.6862 | 121.5891 | 121.4932 | -0.28742 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.004549 | 0.053537 | -0.10004 | 0.069631 | 0.076661 | 0.12918 | 0.051058 | -0.018573 | -0.020376 | -0.11625 | 0.25701 | -121.6898 | 0.38558 | 0.30071 | 0.043694 | -121.6049 | -121.556 | 122.0432 | 121.9462 | 121.8503 | 0.52787 | -121.8969 | 0.27674 | 0.36161 | 0.41059 | 0.43525 | -121.7095
1813.4219 | 122.0352 | -0.3067 | 121.6095 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.064714 | -0.0084589 | 0.052683 | -0.01755 | -0.0046531 | -0.0016987 | 0.020254 | 0.028348 | 0.016287 | -0.22329 | 0.16166 | -0.29684 | 121.6907 | 121.5937 | 121.507 | -0.28285 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.009128 | 0.058115 | -0.1092 | 0.023856 | 0.081239 | 0.083409 | 0.009861 | -0.013995 | -0.015797 | -0.10251 | 0.1975 | -121.6944 | 0.33064 | 0.24119 | 0.043694 | -121.6004 | -121.5514 | 121.9974 | 121.9004 | 121.8137 | 0.46836 | -121.8923 | 0.22181 | 0.31583 | 0.36482 | 0.38032 | -121.7187
1815.1875 | 121.9849 | -0.32044 | 121.6095 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.0645 | -0.0084589 | 0.052683 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.028134 | 0.0165 | -0.21871 | 0.16166 | -0.29226 | 121.6953 | 121.5983 | 121.5116 | -0.26453 | 0.033099 | 0.073618 | -0.070087 | -0.080318 | 0.013707 | 0.053537 | -0.10462 | 0.055905 | 0.085818 | 0.10172 | 0.028172 | -0.027733 | -0.011218 | -0.097935 | 0.21581 | -121.6898 | 0.35353 | 0.25035 | 0.034537 | -121.5958 | -121.556 | 122.0157 | 121.9187 | 121.832 | 0.48209 | -121.874 | 0.24012 | 0.33414 | 0.37397 | 0.39405 | -121.7141
1816.8906 | 121.9894 | -0.29297 | 121.6141 | 1.4211e-13 | -0.038965 | 0.0018589 | 0.064714 | -0.0084589 | 0.052683 | -0.0022892 | -0.0040121 | -0.0014849 | 0.020467 | 0.028562 | 0.0165 | -0.19582 | 0.16624 | -0.26937 | 121.7136 | 121.612 | 121.5299 | -0.25537 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | -2.9e-05 | 0.058115 | -0.10462 | 0.037597 | 0.099553 | 0.097146 | 0.023598 | -0.013999 | -0.002059 | -0.084199 | 0.18834 | -121.7035 | 0.30775 | 0.23204 | 0.043694 | -121.6141 | -121.556 | 122.0066 | 121.905 | 121.8228 | 0.4592 | -121.8694 | 0.20349 | 0.29294 | 0.35108 | 0.36659 | -121.7187
1818.6719 | 121.962 | -0.31128 | 121.6461 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.0645 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020254 | 0.028134 | 0.016287 | -0.19124 | 0.16166 | -0.26937 | 121.7274 | 121.6258 | 121.5253 | -0.24621 | 0.014784 | 0.078197 | -0.06093 | -0.080318 | 0.009128 | 0.058115 | -0.095467 | 0.065065 | 0.081245 | 0.12003 | 0.041908 | -0.023157 | -0.020365 | -0.12082 | 0.21581 | -121.7264 | 0.32606 | 0.25035 | 0.034537 | -121.637 | -121.588 | 122.0386 | 121.937 | 121.8366 | 0.47294 | -121.8923 | 0.23096 | 0.32041 | 0.36939 | 0.38948 | -121.7416
1820.4219 | 121.9254 | -0.32501 | 121.6553 | 1.4211e-13 | -0.039393 | 0.0020727 | 0.0645 | -0.0088863 | 0.052683 | -0.0099192 | -0.0042257 | -0.0012713 | 0.020681 | 0.028134 | 0.0165 | -0.19124 | 0.16624 | -0.26479 | 121.7228 | 121.6258 | 121.5299 | -0.25079 | 0.023941 | 0.064461 | -0.06093 | -0.080318 | 0.004549 | 0.062694 | -0.10462 | 0.074219 | 0.067512 | 0.13377 | 0.060219 | -0.014 | -0.02952 | -0.1254 | 0.22039 | -121.7356 | 0.34895 | 0.26408 | 0.043694 | -121.6507 | -121.5926 | 122.0478 | 121.9508 | 121.8549 | 0.49125 | -121.9061 | 0.24469 | 0.32956 | 0.38771 | 0.38947 | -121.7599
1822.125 | 121.9894 | -0.27924 | 121.669 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.064286 | -0.0086727 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.02004 | 0.027921 | 0.0165 | -0.17751 | 0.15708 | -0.25564 | 121.7365 | 121.6349 | 121.539 | -0.25079 | 0.014784 | 0.064461 | -0.06093 | -0.089475 | 0.013707 | 0.053537 | -0.10462 | 0.028443 | 0.067514 | 0.10173 | 0.023599 | -0.004844 | -0.034095 | -0.12997 | 0.17461 | -121.7585 | 0.29402 | 0.21831 | 0.043694 | -121.6553 | -121.6155 | 122.0158 | 121.9141 | 121.8183 | 0.43632 | -121.9198 | 0.18976 | 0.29294 | 0.33277 | 0.3437 | -121.7736
1823.8906 | 121.8933 | -0.29297 | 121.6919 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064286 | -0.0088863 | 0.052683 | 0.0053413 | -0.0042257 | -0.0016987 | 0.020254 | 0.027921 | 0.016714 | -0.17293 | 0.16624 | -0.24648 | 121.7411 | 121.6486 | 121.5528 | -0.23248 | 0.014784 | 0.06904 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.10004 | 0.060492 | 0.049204 | 0.12004 | 0.046489 | -0.014003 | -0.043248 | -0.13913 | 0.19292 | -121.7768 | 0.30775 | 0.23204 | 0.039115 | -121.6736 | -121.6384 | 122.0341 | 121.9416 | 121.8457 | 0.4592 | -121.9244 | 0.20807 | 0.31125 | 0.34651 | 0.36201 | -121.7919
1825.6406 | 121.9299 | -0.3067 | 121.6919 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.028348 | 0.016714 | -0.17293 | 0.16624 | -0.2419 | 121.7594 | 121.6532 | 121.5573 | -0.23248 | 0.014784 | 0.078197 | -0.070087 | -0.084896 | 0.018285 | 0.053537 | -0.095467 | 0.074225 | 0.067517 | 0.13377 | 0.0648 | -0.009425 | -0.038669 | -0.13455 | 0.21123 | -121.7768 | 0.32149 | 0.23661 | 0.02538 | -121.6736 | -121.6384 | 122.0661 | 121.9599 | 121.8641 | 0.47294 | -121.9244 | 0.22181 | 0.32499 | 0.36024 | 0.3849 | -121.7874
1827.3281 | 122.0444 | -0.27008 | 121.6553 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0042257 | -0.0010577 | 0.020467 | 0.028134 | 0.016073 | -0.16835 | 0.16166 | -0.25106 | 121.7548 | 121.6532 | 121.5573 | -0.2279 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.042182 | 0.099561 | 0.10173 | 0.019023 | -0.023159 | -0.002047 | -0.097925 | 0.16546 | -121.7402 | 0.29402 | 0.20915 | 0.043694 | -121.6416 | -121.6017 | 122.0249 | 121.9233 | 121.8274 | 0.43174 | -121.8832 | 0.18519 | 0.28379 | 0.32362 | 0.3437 | -121.7599
1829.0938 | 121.9391 | -0.29297 | 121.6965 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.064714 | -0.0088863 | 0.05311 | -0.0099192 | -0.0040121 | -0.0014849 | 0.020681 | 0.028134 | 0.016073 | -0.1592 | 0.16166 | -0.23732 | 121.7686 | 121.6624 | 121.5573 | -0.21874 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.074228 | 0.072097 | 0.13377 | 0.055646 | -0.018582 | -0.034088 | -0.13912 | 0.18834 | -121.7814 | 0.31691 | 0.22746 | 0.039115 | -121.6828 | -121.6429 | 122.0615 | 121.9554 | 121.8503 | 0.45463 | -121.9152 | 0.20807 | 0.30668 | 0.34651 | 0.37117 | -121.8011
1830.8438 | 122.0581 | -0.23346 | 121.669 | 1.4211e-13 | -0.039179 | 0.0018589 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.028134 | 0.0165 | -0.1592 | 0.16166 | -0.22359 | 121.7731 | 121.6761 | 121.5757 | -0.21416 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.009128 | 0.067272 | -0.10462 | 0.019297 | 0.10414 | 0.074263 | 0.00987 | -0.009427 | 0.007115 | -0.093344 | 0.12884 | -121.7539 | 0.2574 | 0.16795 | 0.039115 | -121.6599 | -121.6017 | 122.0066 | 121.9096 | 121.8091 | 0.39512 | -121.8832 | 0.14856 | 0.24259 | 0.30073 | 0.30708 | -121.7736
1832.5938 | 121.994 | -0.24719 | 121.6965 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064714 | -0.0088863 | 0.052897 | 0.0053413 | -0.0037985 | -0.0014849 | 0.020254 | 0.028348 | 0.016287 | -0.14088 | 0.16624 | -0.21443 | 121.7731 | 121.6853 | 121.594 | -0.19127 | 0.02852 | 0.06904 | -0.06093 | -0.094053 | 0.009128 | 0.048958 | -0.10004 | 0.055925 | 0.076675 | 0.10631 | 0.03276 | -0.023165 | -0.011193 | -0.1025 | 0.14715 | -121.7905 | 0.27571 | 0.18626 | 0.039115 | -121.6873 | -121.6475 | 122.0203 | 121.9325 | 121.8412 | 0.41343 | -121.8877 | 0.15314 | 0.25632 | 0.29615 | 0.31623 | -121.7965
1834.3594 | 121.9208 | -0.28839 | 121.7468 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.0645 | -0.0088863 | 0.052683 | -0.02518 | -0.0040121 | -0.0014849 | 0.020254 | 0.028348 | 0.0165 | -0.12257 | 0.16166 | -0.20528 | 121.796 | 121.7036 | 121.6077 | -0.18669 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.095467 | 0.1017 | 0.049213 | 0.16582 | 0.083116 | -0.018587 | -0.043232 | -0.13911 | 0.19292 | -121.8363 | 0.30775 | 0.22746 | 0.034537 | -121.7331 | -121.6887 | 122.0844 | 121.992 | 121.8961 | 0.45005 | -121.9335 | 0.19892 | 0.3021 | 0.34651 | 0.36201 | -121.8423
1836.125 | 121.9391 | -0.23346 | 121.7285 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.064286 | -0.0090999 | 0.05311 | -0.0099192 | -0.0040121 | -0.0014849 | 0.020254 | 0.028348 | 0.0165 | -0.11341 | 0.16624 | -0.18696 | 121.8052 | 121.7128 | 121.6169 | -0.18211 | 0.02852 | 0.078197 | -0.065509 | -0.089475 | 0.013707 | 0.053537 | -0.095467 | 0.05135 | 0.07668 | 0.12005 | 0.046497 | -0.004853 | -0.015764 | -0.11165 | 0.13799 | -121.818 | 0.26198 | 0.16795 | 0.029958 | -121.7148 | -121.675 | 122.0387 | 121.9462 | 121.8503 | 0.3997 | -121.9106 | 0.14398 | 0.24717 | 0.287 | 0.31166 | -121.824
1837.8906 | 122.0398 | -0.2243 | 121.6873 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.0645 | -0.0086727 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.02004 | 0.028348 | 0.0165 | -0.11799 | 0.16166 | -0.19612 | 121.8144 | 121.7173 | 121.6214 | -0.17295 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.095467 | 0.051353 | 0.12704 | 0.10631 | 0.028185 | -0.023168 | 0.030014 | -0.065869 | 0.12884 | -121.7768 | 0.24824 | 0.1588 | 0.029958 | -121.6736 | -121.6246 | 122.0387 | 121.9416 | 121.8458 | 0.38596 | -121.8603 | 0.13483 | 0.23801 | 0.287 | 0.29792 | -121.7828
1839.5938 | 122.0032 | -0.18768 | 121.7468 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064714 | -0.0086727 | 0.052683 | -0.0099192 | -0.0040121 | -0.0012713 | 0.02004 | 0.028348 | 0.016287 | -0.085942 | 0.16624 | -0.16407 | 121.8464 | 121.7494 | 121.6489 | -0.1409 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.009128 | 0.058115 | -0.10004 | 0.046784 | 0.099576 | 0.10174 | 0.023612 | -0.023172 | 0.002558 | -0.097906 | 0.087638 | -121.8317 | 0.21162 | 0.12675 | 0.039115 | -121.7377 | -121.6887 | 122.0341 | 121.9371 | 121.8366 | 0.35392 | -121.8877 | 0.10279 | 0.19681 | 0.2458 | 0.26588 | -121.8469
1841.3438 | 122.0444 | -0.15106 | 121.7468 | 1.4211e-13 | -0.039393 | 0.0014317 | 0.0645 | -0.0084589 | 0.052683 | -0.0022892 | -0.0040121 | -0.0012713 | 0.020254 | 0.028348 | 0.0165 | -0.067628 | 0.15708 | -0.1366 | 121.8647 | 121.7723 | 121.6718 | -0.13174 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.019321 | 0.11789 | 0.083434 | 0.014461 | -0.00486 | 0.025452 | -0.075013 | 0.051017 | -121.8317 | 0.175 | 0.080975 | 0.029958 | -121.7331 | -121.6887 | 122.0158 | 121.9233 | 121.8229 | 0.30814 | -121.8786 | 0.066166 | 0.16477 | 0.20918 | 0.22926 | -121.8469
1843.0312 | 122.0032 | -0.16022 | 121.8018 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.064928 | -0.0084589 | 0.052469 | -0.0022892 | -0.0040121 | -0.0012713 | 0.02004 | 0.028134 | 0.016287 | -0.053893 | 0.16166 | -0.13202 | 121.8693 | 121.7631 | 121.6718 | -0.11342 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.009128 | 0.053537 | -0.10462 | 0.046792 | 0.067535 | 0.10632 | 0.028194 | -0.018598 | -0.038638 | -0.12995 | 0.055593 | -121.8912 | 0.17958 | 0.099287 | 0.043694 | -121.7926 | -121.7482 | 122.0295 | 121.9233 | 121.832 | 0.32188 | -121.9152 | 0.070742 | 0.16934 | 0.21375 | 0.23384 | -121.9064
1844.7812 | 121.9254 | -0.19684 | 121.8109 | 1.4211e-13 | -0.039179 | 0.0016453 | 0.064286 | -0.0086727 | 0.052897 | -0.0099192 | -0.0046531 | -0.0014849 | 0.020467 | 0.028562 | 0.016287 | -0.058472 | 0.16166 | -0.12287 | 121.8693 | 121.7723 | 121.681 | -0.12258 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.009128 | 0.053537 | -0.095467 | 0.074255 | 0.05838 | 0.13837 | 0.073972 | -0.000283 | -0.038635 | -0.12994 | 0.10137 | -121.8912 | 0.22078 | 0.14049 | 0.039116 | -121.8018 | -121.7574 | 122.0661 | 121.9691 | 121.8778 | 0.3585 | -121.9335 | 0.11652 | 0.20597 | 0.25038 | 0.27046 | -121.9064
1846.5469 | 121.9391 | -0.16937 | 121.7834 | 1.4211e-13 | -0.03982 | 0.0016453 | 0.064714 | -0.0084589 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.028134 | 0.0165 | -0.044736 | 0.16166 | -0.11371 | 121.8922 | 121.7814 | 121.6947 | -0.11342 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.009128 | 0.058115 | -0.095467 | 0.055948 | 0.10874 | 0.12464 | 0.055663 | -0.000285 | -0.002011 | -0.088741 | 0.073906 | -121.8683 | 0.19789 | 0.10386 | 0.029958 | -121.7743 | -121.7253 | 122.0616 | 121.9508 | 121.8641 | 0.33103 | -121.8969 | 0.084477 | 0.1785 | 0.22749 | 0.24299 | -121.8789
1848.2656 | 121.9162 | -0.1831 | 121.8018 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.064714 | -0.0088863 | 0.052683 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020254 | 0.028348 | 0.016073 | -0.044736 | 0.16624 | -0.12287 | 121.883 | 121.786 | 121.6947 | -0.10885 | 0.010205 | 0.073618 | -0.056351 | -0.084896 | 0.013707 | 0.048958 | -0.10004 | 0.074258 | 0.081271 | 0.13837 | 0.060239 | -0.014019 | -0.015743 | -0.10705 | 0.08306 | -121.8867 | 0.19331 | 0.12675 | 0.043694 | -121.7881 | -121.7528 | 122.0661 | 121.9691 | 121.8778 | 0.34934 | -121.9106 | 0.098209 | 0.19681 | 0.23206 | 0.25672 | -121.9018
1850.0312 | 122.0398 | -0.12817 | 121.7789 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.02004 | 0.028348 | 0.016073 | -0.044736 | 0.17081 | -0.12287 | 121.8922 | 121.786 | 121.6993 | -0.11342 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.048958 | -0.095467 | 0.014749 | 0.11332 | 0.083438 | 0.005308 | -0.009441 | 0.007145 | -0.079586 | 0.032707 | -121.8638 | 0.15212 | 0.062665 | 0.029958 | -121.7606 | -121.7299 | 122.0204 | 121.9142 | 121.8275 | 0.29899 | -121.8923 | 0.043278 | 0.14646 | 0.17713 | 0.20179 | -121.8743
1851.7969 | 121.9894 | -0.15564 | 121.8063 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.064286 | -0.0086727 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.028775 | 0.016714 | -0.040158 | 0.16166 | -0.10913 | 121.883 | 121.7906 | 121.6993 | -0.099689 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.055951 | 0.076694 | 0.11548 | 0.046508 | -0.009443 | -0.015741 | -0.10705 | 0.055595 | -121.8958 | 0.17958 | 0.099289 | 0.043694 | -121.7926 | -121.7482 | 122.0387 | 121.9462 | 121.8549 | 0.3173 | -121.906 | 0.066165 | 0.16935 | 0.21376 | 0.22926 | -121.9064
1853.4844 | 121.9528 | -0.16937 | 121.8292 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.064286 | -0.0086727 | 0.052897 | -0.01755 | -0.0042257 | -0.0014849 | 0.02004 | 0.028134 | 0.016287 | -0.040158 | 0.17081 | -0.11371 | 121.8922 | 121.786 | 121.7084 | -0.10885 | 0.019362 | 0.06904 | -0.06093 | -0.089475 | 0.009128 | 0.048958 | -0.10004 | 0.060526 | 0.062961 | 0.12921 | 0.055663 | -0.004863 | -0.043209 | -0.12078 | 0.069328 | -121.9187 | 0.18873 | 0.10844 | 0.039115 | -121.8201 | -121.7803 | 122.0616 | 121.9554 | 121.8778 | 0.34019 | -121.9381 | 0.079898 | 0.1785 | 0.21833 | 0.23841 | -121.9293
1855.25 | 122.0398 | -0.13275 | 121.8018 | 1.4211e-13 | -0.03982 | 0.0016453 | 0.0645 | -0.0086727 | 0.052469 | -0.0099192 | -0.0044395 | -0.0016987 | 0.020467 | 0.028134 | 0.0165 | -0.031001 | 0.16624 | -0.10913 | 121.9013 | 121.7906 | 121.6993 | -0.10427 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.018285 | 0.058115 | -0.10004 | 0.028483 | 0.099584 | 0.10175 | 0.023619 | -0.004864 | -0.011164 | -0.10247 | 0.032706 | -121.8912 | 0.15669 | 0.0764 | 0.043694 | -121.7835 | -121.7436 | 122.0341 | 121.9233 | 121.832 | 0.29899 | -121.906 | 0.043276 | 0.15104 | 0.19087 | 0.20637 | -121.9018
1857.0156 | 121.9437 | -0.17853 | 121.8292 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.064714 | -0.0088863 | 0.052683 | -0.0022892 | -0.0040121 | -0.0012713 | 0.02004 | 0.028348 | 0.016714 | -0.031001 | 0.17081 | -0.10913 | 121.8968 | 121.7998 | 121.7084 | -0.099689 | 0.019362 | 0.078197 | -0.06093 | -0.089475 | 0.009128 | 0.058115 | -0.095467 | 0.078839 | 0.06754 | 0.14753 | 0.069396 | -0.009443 | -0.029472 | -0.12078 | 0.083061 | -121.9187 | 0.19789 | 0.1176 | 0.034537 | -121.8201 | -121.7711 | 122.0753 | 121.9783 | 121.887 | 0.34934 | -121.9289 | 0.089053 | 0.18766 | 0.23664 | 0.25672 | -121.9247
1858.7812 | 121.9803 | -0.14648 | 121.8063 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.0645 | -0.0088863 | 0.052897 | -0.01755 | -0.0046531 | -0.0016987 | 0.02004 | 0.028562 | 0.016287 | -0.03558 | 0.16624 | -0.11371 | 121.8968 | 121.7952 | 121.7084 | -0.099689 | 0.023941 | 0.06904 | -0.065509 | -0.084896 | 0.018285 | 0.067272 | -0.10462 | 0.046795 | 0.090429 | 0.1109 | 0.032774 | -0.014021 | -0.011162 | -0.097894 | 0.04186 | -121.8912 | 0.17042 | 0.080975 | 0.039115 | -121.788 | -121.7391 | 122.0432 | 121.9417 | 121.8549 | 0.31272 | -121.906 | 0.061588 | 0.16477 | 0.21376 | 0.21552 | -121.911
1860.4844 | 122.0032 | -0.15106 | 121.8201 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.0645 | -0.0084589 | 0.052897 | -0.0022892 | -0.0046531 | -0.0012713 | 0.02004 | 0.028134 | 0.0165 | -0.03558 | 0.16166 | -0.10913 | 121.9013 | 121.7998 | 121.713 | -0.099689 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.051373 | 0.081274 | 0.11548 | 0.04193 | -0.009443 | -0.020316 | -0.10705 | 0.051017 | -121.9095 | 0.175 | 0.085553 | 0.034536 | -121.8109 | -121.7574 | 122.0524 | 121.9508 | 121.8641 | 0.31272 | -121.9198 | 0.061587 | 0.16019 | 0.21376 | 0.22926 | -121.9201
1862.25 | 121.8979 | -0.17853 | 121.8384 | 1.4211e-13 | -0.03982 | 0.0018589 | 0.064286 | -0.0090999 | 0.052897 | -0.01755 | -0.0044395 | -0.0012713 | 0.020467 | 0.028348 | 0.0165 | -0.031001 | 0.16624 | -0.10913 | 121.9059 | 121.7998 | 121.713 | -0.10427 | 0.033099 | 0.073618 | -0.06093 | -0.094053 | 0.013707 | 0.053537 | -0.095467 | 0.07426 | 0.067542 | 0.14753 | 0.069396 | -0.004864 | -0.038627 | -0.12536 | 0.083061 | -121.9324 | 0.21163 | 0.1176 | 0.034537 | -121.8247 | -121.7848 | 122.0844 | 121.9783 | 121.8915 | 0.34476 | -121.9426 | 0.084475 | 0.19223 | 0.23206 | 0.25215 | -121.9338
1863.9531 | 121.9254 | -0.1831 | 121.8475 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064286 | -0.0086727 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.028348 | 0.0165 | -0.03558 | 0.16624 | -0.11371 | 121.9105 | 121.7998 | 121.7084 | -0.09511 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.087995 | 0.062965 | 0.14752 | 0.069395 | -0.0186 | -0.047782 | -0.13909 | 0.078481 | -121.9324 | 0.20247 | 0.12217 | 0.043694 | -121.8338 | -121.794 | 122.0936 | 121.9829 | 121.8915 | 0.34934 | -121.9426 | 0.098209 | 0.19681 | 0.23664 | 0.25672 | -121.9522
1865.7188 | 122.0123 | -0.11902 | 121.8063 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.064286 | -0.0090999 | 0.052897 | -0.01755 | -0.0040121 | -0.0014849 | 0.020254 | 0.028134 | 0.016287 | -0.031001 | 0.16624 | -0.10913 | 121.9105 | 121.8089 | 121.7176 | -0.10427 | 0.023941 | 0.082776 | -0.056351 | -0.094053 | 0.013707 | 0.058115 | -0.10004 | 0.014751 | 0.10416 | 0.088018 | 0.009887 | -0.004864 | 0.002575 | -0.088736 | 0.018974 | -121.9004 | 0.14296 | 0.062668 | 0.043694 | -121.7926 | -121.7482 | 122.0295 | 121.9279 | 121.8366 | 0.28525 | -121.9106 | 0.024966 | 0.13273 | 0.17713 | 0.2018 | -121.9064
1867.4844 | 121.907 | -0.15564 | 121.8521 | 1.4211e-13 | -0.03982 | 0.0018589 | 0.0645 | -0.0086727 | 0.052683 | -0.0022892 | -0.0042257 | -0.0016987 | 0.02004 | 0.028348 | 0.0165 | -0.031001 | 0.17081 | -0.10913 | 121.9059 | 121.8089 | 121.7176 | -0.099689 | 0.02852 | 0.078197 | -0.056351 | -0.084896 | 0.018285 | 0.058115 | -0.095467 | 0.055951 | 0.053809 | 0.12464 | 0.046508 | -0.009443 | -0.043202 | -0.13451 | 0.060173 | -121.937 | 0.18416 | 0.099289 | 0.039116 | -121.8338 | -121.794 | 122.0616 | 121.9646 | 121.8732 | 0.32645 | -121.9518 | 0.070744 | 0.17392 | 0.21376 | 0.23384 | -121.9476
1869.25 | 121.9299 | -0.18768 | 121.875 | 1.4211e-13 | -0.03982 | 0.0020727 | 0.064073 | -0.0086727 | 0.052897 | -0.0099192 | -0.0040121 | -0.0014849 | 0.020254 | 0.028348 | 0.016073 | -0.031001 | 0.16166 | -0.10455 | 121.9105 | 121.8043 | 121.7176 | -0.099689 | 0.02852 | 0.06904 | -0.056351 | -0.089475 | 0.013707 | 0.062694 | -0.10004 | 0.087994 | 0.035499 | 0.15668 | 0.08313 | -0.004864 | -0.070669 | -0.1574 | 0.087638 | -121.9645 | 0.2162 | 0.13133 | 0.043694 | -121.8613 | -121.8123 | 122.0982 | 121.992 | 121.9053 | 0.34934 | -121.9747 | 0.098208 | 0.20139 | 0.25038 | 0.25672 | -121.975
1871 | 122.0535 | -0.12817 | 121.8109 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.064073 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.028775 | 0.016073 | -0.026423 | 0.15708 | -0.095397 | 121.9105 | 121.8089 | 121.7176 | -0.090531 | 0.023941 | 0.064461 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.095467 | 0.037643 | 0.099586 | 0.10175 | 0.032777 | -0.004866 | -0.002003 | -0.093314 | 0.032707 | -121.8912 | 0.15212 | 0.062665 | 0.029958 | -121.7972 | -121.7528 | 122.0387 | 121.9371 | 121.8458 | 0.28525 | -121.9014 | 0.047856 | 0.14188 | 0.18629 | 0.19264 | -121.9064
1872.6875 | 121.9528 | -0.14648 | 121.8704 | 1.4211e-13 | -0.03982 | 0.0020727 | 0.0645 | -0.0084589 | 0.052897 | -0.0022892 | -0.0042257 | -0.0012713 | 0.020254 | 0.028348 | 0.0165 | -0.021844 | 0.17081 | -0.095397 | 121.9242 | 121.8181 | 121.7222 | -0.090531 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.10462 | 0.055953 | 0.053812 | 0.12464 | 0.051087 | -0.004866 | -0.052355 | -0.14825 | 0.04186 | -121.9553 | 0.16585 | 0.085554 | 0.043694 | -121.8521 | -121.8169 | 122.0707 | 121.9646 | 121.8687 | 0.3173 | -121.961 | 0.061588 | 0.16477 | 0.20002 | 0.22468 | -121.975
1874.4531 | 121.9299 | -0.16022 | 121.8063 | 1.4211e-13 | -0.039606 | 0.0016453 | 0.0645 | -0.0090999 | 0.052469 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.028562 | 0.0165 | -0.021844 | 0.16624 | -0.10455 | 121.9197 | 121.8135 | 121.7268 | -0.090531 | 0.033099 | 0.078197 | -0.056351 | -0.089475 | 0.009128 | 0.058115 | -0.095467 | 0.069686 | 0.11332 | 0.13837 | 0.055664 | -0.014022 | 0.007154 | -0.079579 | 0.06475 | -121.8958 | 0.19332 | 0.10387 | 0.039116 | -121.7972 | -121.7482 | 122.0799 | 121.9737 | 121.887 | 0.32645 | -121.8969 | 0.070742 | 0.16934 | 0.21833 | 0.23841 | -121.9018
1876.2031 | 121.9574 | -0.15564 | 121.8658 | 1.4211e-13 | -0.040034 | 0.0022863 | 0.064714 | -0.0086727 | 0.052683 | -0.0022892 | -0.0040121 | -0.0016987 | 0.02004 | 0.028562 | 0.016287 | -0.021844 | 0.17081 | -0.095397 | 121.9151 | 121.8226 | 121.7222 | -0.085952 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.009128 | 0.058115 | -0.10004 | 0.069688 | 0.049232 | 0.1338 | 0.060243 | -0.009445 | -0.043199 | -0.14367 | 0.055595 | -121.9507 | 0.17958 | 0.099289 | 0.043694 | -121.8567 | -121.8077 | 122.0707 | 121.9783 | 121.8778 | 0.32645 | -121.9518 | 0.070744 | 0.16477 | 0.21376 | 0.23384 | -121.9659
1877.9688 | 121.9666 | -0.16022 | 121.8475 | 1.4211e-13 | -0.039606 | 0.0022863 | 0.0645 | -0.0086727 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.020254 | 0.028562 | 0.0165 | -0.021844 | 0.17081 | -0.095397 | 121.9197 | 121.8272 | 121.7268 | -0.076794 | 0.019362 | 0.073618 | -0.070087 | -0.080318 | 0.004549 | 0.053537 | -0.10462 | 0.083423 | 0.072122 | 0.13837 | 0.06482 | -0.018603 | -0.020309 | -0.12078 | 0.055593 | -121.9279 | 0.17958 | 0.09013 | 0.034537 | -121.843 | -121.794 | 122.0799 | 121.9874 | 121.887 | 0.33103 | -121.9243 | 0.079899 | 0.16477 | 0.21375 | 0.23384 | -121.9522
1879.6719 | 121.9986 | -0.14648 | 121.8292 | 1.4211e-13 | -0.03982 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.028348 | 0.016287 | -0.021844 | 0.16624 | -0.095397 | 121.9197 | 121.8181 | 121.7313 | -0.085952 | 0.02852 | 0.073618 | -0.056351 | -0.089475 | 0.009128 | 0.058115 | -0.10462 | 0.060532 | 0.090432 | 0.12464 | 0.051087 | -0.009445 | -0.011157 | -0.09789 | 0.04186 | -121.9187 | 0.175 | 0.090133 | 0.048273 | -121.8201 | -121.7711 | 122.0661 | 121.9646 | 121.8778 | 0.31272 | -121.9152 | 0.057009 | 0.15561 | 0.2046 | 0.2201 | -121.9338
1881.4375 | 122.0535 | -0.11902 | 121.8201 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028562 | 0.0165 | -0.021844 | 0.17539 | -0.090818 | 121.9242 | 121.8272 | 121.7359 | -0.085952 | 0.014784 | 0.078197 | -0.06093 | -0.094053 | 0.018285 | 0.053537 | -0.10004 | 0.033067 | 0.10417 | 0.097175 | 0.028201 | -0.004866 | 0.007157 | -0.084155 | 0.018974 | -121.9141 | 0.1338 | 0.058089 | 0.039115 | -121.8018 | -121.7665 | 122.0433 | 121.9462 | 121.8549 | 0.29441 | -121.906 | 0.024966 | 0.1373 | 0.17256 | 0.19722 | -121.9201
1883.2031 | 122.0215 | -0.11444 | 121.8338 | 1.4211e-13 | -0.039393 | 0.0014317 | 0.064286 | -0.0086727 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.02004 | 0.028348 | 0.0165 | -0.012688 | 0.17997 | -0.095397 | 121.9288 | 121.8272 | 121.7268 | -0.085952 | 0.019362 | 0.073618 | -0.065509 | -0.094053 | 0.004549 | 0.053537 | -0.095467 | 0.028489 | 0.095012 | 0.10175 | 0.019044 | -0.009445 | -0.006576 | -0.10704 | 0.018974 | -121.9279 | 0.1338 | 0.048932 | 0.029958 | -121.8293 | -121.7803 | 122.0433 | 121.9417 | 121.8412 | 0.29441 | -121.9198 | 0.020388 | 0.11899 | 0.16798 | 0.18806 | -121.9293
1884.9844 | 121.9528 | -0.15106 | 121.8658 | 1.4211e-13 | -0.039393 | 0.0016453 | 0.064286 | -0.0086727 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019827 | 0.028348 | 0.0165 | -0.017266 | 0.17539 | -0.08624 | 121.9288 | 121.8272 | 121.7359 | -0.085952 | 0.02852 | 0.064461 | -0.056351 | -0.084896 | 0.013707 | 0.062694 | -0.10004 | 0.06511 | 0.062968 | 0.1338 | 0.064822 | -0.000288 | -0.03862 | -0.12993 | 0.051017 | -121.9507 | 0.17958 | 0.094711 | 0.043694 | -121.8521 | -121.8032 | 122.0799 | 121.9783 | 121.887 | 0.32645 | -121.9518 | 0.066166 | 0.16477 | 0.21376 | 0.21552 | -121.9659
1886.6875 | 121.9299 | -0.15564 | 121.8842 | 1.4211e-13 | -0.039393 | 0.0014317 | 0.064073 | -0.0086727 | 0.052469 | -0.01755 | -0.0040121 | -0.0014849 | 0.020254 | 0.028775 | 0.016287 | -0.017266 | 0.16624 | -0.095397 | 121.9288 | 121.8318 | 121.7359 | -0.081373 | 0.019362 | 0.073618 | -0.070087 | -0.089475 | 0.013707 | 0.053537 | -0.10004 | 0.074267 | 0.044658 | 0.13837 | 0.060243 | -0.014024 | -0.052351 | -0.14824 | 0.055595 | -121.9736 | 0.175 | 0.085553 | 0.029958 | -121.8704 | -121.8306 | 122.0845 | 121.9874 | 121.8916 | 0.32188 | -121.9655 | 0.066165 | 0.16935 | 0.20918 | 0.22926 | -121.9842
1888.4375 | 121.9711 | -0.15564 | 121.8475 | 1.4211e-13 | -0.040034 | 0.0018589 | 0.064286 | -0.0086727 | 0.053324 | -0.0099192 | -0.0042257 | -0.0012713 | 0.02004 | 0.028775 | 0.016287 | -0.017266 | 0.16166 | -0.095397 | 121.9288 | 121.8318 | 121.7451 | -0.085952 | 0.019362 | 0.078197 | -0.056351 | -0.089475 | 0.013707 | 0.053537 | -0.10004 | 0.069688 | 0.081279 | 0.13837 | 0.060243 | -0.009445 | -0.01573 | -0.10246 | 0.055595 | -121.937 | 0.175 | 0.099289 | 0.043694 | -121.8338 | -121.794 | 122.0845 | 121.9874 | 121.9007 | 0.3173 | -121.9335 | 0.066165 | 0.16935 | 0.20918 | 0.23384 | -121.9476
1890.1406 | 122.0123 | -0.11444 | 121.843 | 1.4211e-13 | -0.040247 | 0.0020727 | 0.0645 | -0.0086727 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.028348 | 0.0165 | -0.017266 | 0.16624 | -0.08624 | 121.9288 | 121.8318 | 121.7451 | -0.076794 | 0.023941 | 0.064461 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.037647 | 0.085856 | 0.097175 | 0.028201 | -0.009446 | -0.011153 | -0.097887 | 0.005238 | -121.9279 | 0.13838 | 0.048932 | 0.043694 | -121.8293 | -121.7848 | 122.0433 | 121.9462 | 121.8595 | 0.28068 | -121.9198 | 0.029545 | 0.12815 | 0.17256 | 0.1789 | -121.9522
1891.9062 | 121.9208 | -0.17853 | 121.8704 | 1.4211e-13 | -0.039606 | 0.0018589 | 0.064286 | -0.0086727 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.02004 | 0.028134 | 0.016287 | -0.026423 | 0.17539 | -0.099975 | 121.9151 | 121.8226 | 121.7268 | -0.090531 | 0.019362 | 0.073618 | -0.065509 | -0.094053 | 0.013707 | 0.058115 | -0.10004 | 0.087997 | 0.044655 | 0.1521 | 0.078553 | -0.009444 | -0.047776 | -0.14367 | 0.078483 | -121.9645 | 0.19789 | 0.11302 | 0.034536 | -121.8567 | -121.8123 | 122.0936 | 122.0012 | 121.9053 | 0.35392 | -121.961 | 0.084475 | 0.19223 | 0.23664 | 0.25215 | -121.9705
1893.6094 | 122.0306 | -0.14191 | 121.7972 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.0645 | -0.0090999 | 0.052683 | -0.0099192 | -0.0042257 | -0.0016987 | 0.020254 | 0.028348 | 0.016073 | -0.040158 | 0.17081 | -0.11829 | 121.8922 | 121.7952 | 121.7039 | -0.118 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.009128 | 0.053537 | -0.1092 | 0.023903 | 0.095005 | 0.10175 | 0.023619 | -0.000284 | -0.002007 | -0.093317 | 0.032704 | -121.8821 | 0.16585 | 0.080977 | 0.048273 | -121.7881 | -121.7436 | 122.0341 | 121.9371 | 121.8458 | 0.31272 | -121.9152 | 0.057011 | 0.15104 | 0.19544 | 0.21553 | -121.9064
1895.3906 | 122.0169 | -0.17853 | 121.788 | 1.4211e-13 | -0.03982 | 0.0016453 | 0.064286 | -0.0086727 | 0.05311 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019827 | 0.028134 | 0.016073 | -0.06305 | 0.17081 | -0.15034 | 121.8785 | 121.7723 | 121.6901 | -0.1409 | 0.02852 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.1092 | 0.037629 | 0.090425 | 0.11548 | 0.028192 | -0.009437 | -0.015747 | -0.097898 | 0.069325 | -121.8683 | 0.20705 | 0.1176 | 0.048273 | -121.7743 | -121.7253 | 122.057 | 121.9508 | 121.8687 | 0.34934 | -121.9289 | 0.09821 | 0.19223 | 0.24122 | 0.25215 | -121.8972
1897.1406 | 121.9711 | -0.19226 | 121.7834 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064286 | -0.0088863 | 0.052469 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019827 | 0.028775 | 0.0165 | -0.076785 | 0.17539 | -0.15491 | 121.8739 | 121.7769 | 121.681 | -0.13174 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.06052 | 0.090425 | 0.11548 | 0.037347 | -0.023173 | -0.00659 | -0.10248 | 0.092216 | -121.8683 | 0.2162 | 0.13133 | 0.039115 | -121.7697 | -121.7299 | 122.0661 | 121.9691 | 121.8732 | 0.36765 | -121.9152 | 0.10736 | 0.20597 | 0.2458 | 0.2613 | -121.8835
1898.9062 | 122.0581 | -0.16022 | 121.7743 | 1.4211e-13 | -0.040034 | 0.0018589 | 0.064073 | -0.0088863 | 0.052683 | -0.0022892 | -0.0040121 | -0.0014849 | 0.020467 | 0.028348 | 0.016073 | -0.072207 | 0.17997 | -0.14576 | 121.8693 | 121.7631 | 121.681 | -0.1409 | 0.023941 | 0.06904 | -0.056351 | -0.094053 | 0.013707 | 0.062694 | -0.10004 | 0.019318 | 0.095001 | 0.08801 | 0.014459 | -0.004859 | -0.011172 | -0.093322 | 0.060172 | -121.8683 | 0.18416 | 0.10387 | 0.043694 | -121.7606 | -121.7116 | 122.0295 | 121.9233 | 121.8412 | 0.34019 | -121.9152 | 0.066164 | 0.17392 | 0.22291 | 0.22926 | -121.8743
1900.6094 | 121.9803 | -0.20142 | 121.7926 | 1.4211e-13 | -0.039393 | 0.0018589 | 0.064286 | -0.0088863 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.028562 | 0.0165 | -0.081363 | 0.17539 | -0.15034 | 121.8693 | 121.7677 | 121.681 | -0.1409 | 0.023941 | 0.06904 | -0.056351 | -0.089475 | 0.009128 | 0.058115 | -0.10462 | 0.060517 | 0.07669 | 0.12005 | 0.05108 | -0.009437 | -0.024904 | -0.11163 | 0.096792 | -121.8821 | 0.22536 | 0.14506 | 0.048273 | -121.7835 | -121.7345 | 122.0707 | 121.9691 | 121.8824 | 0.37681 | -121.9335 | 0.11194 | 0.21054 | 0.25953 | 0.27046 | -121.8972
1902.3594 | 122.0398 | -0.19226 | 121.7789 | 1.4211e-13 | -0.040247 | 0.0014317 | 0.064286 | -0.0084589 | 0.052683 | -0.0099192 | -0.0042257 | -0.0016987 | 0.020254 | 0.028348 | 0.016287 | -0.081363 | 0.17539 | -0.15491 | 121.8693 | 121.7677 | 121.681 | -0.14548 | 0.02852 | 0.073618 | -0.056351 | -0.080318 | 0.009128 | 0.062694 | -0.1092 | 0.046783 | 0.090423 | 0.1109 | 0.037347 | -0.009436 | -0.011171 | -0.0979 | 0.083058 | -121.8592 | 0.22078 | 0.13591 | 0.052852 | -121.7697 | -121.7162 | 122.0616 | 121.96 | 121.8732 | 0.36765 | -121.9243 | 0.11194 | 0.20139 | 0.25495 | 0.26588 | -121.8881
1904.0469 | 122.081 | -0.16937 | 121.7834 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064286 | -0.0086727 | 0.05311 | -0.0099192 | -0.0040121 | -0.0012713 | 0.020254 | 0.028348 | 0.0165 | -0.076785 | 0.17081 | -0.15949 | 121.8693 | 121.7677 | 121.6855 | -0.1409 | 0.023941 | 0.06904 | -0.070087 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.028474 | 0.085846 | 0.092588 | 0.00988 | -0.018594 | -0.015748 | -0.097899 | 0.069328 | -121.8729 | 0.19331 | 0.099286 | 0.029958 | -121.7697 | -121.7253 | 122.0387 | 121.9371 | 121.8549 | 0.34019 | -121.9243 | 0.079898 | 0.18308 | 0.22749 | 0.23841 | -121.8835
1905.8125 | 122.0215 | -0.16022 | 121.7834 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.0645 | -0.0086727 | 0.052897 | -0.01755 | -0.0042257 | -0.0014849 | 0.019827 | 0.028562 | 0.0165 | -0.072207 | 0.18455 | -0.14118 | 121.8739 | 121.7814 | 121.681 | -0.14548 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.009128 | 0.058115 | -0.10004 | 0.014739 | 0.090425 | 0.08801 | 0.019037 | 0.004298 | -0.002011 | -0.10248 | 0.060172 | -121.8729 | 0.18416 | 0.10387 | 0.043694 | -121.7743 | -121.7253 | 122.0341 | 121.9417 | 121.8412 | 0.34477 | -121.9289 | 0.070742 | 0.16934 | 0.21833 | 0.23384 | -121.8835
1907.5625 | 122.049 | -0.16937 | 121.7834 | 1.4211e-13 | -0.040034 | 0.0016453 | 0.064286 | -0.0088863 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020467 | 0.028775 | 0.016287 | -0.072207 | 0.17997 | -0.15491 | 121.8739 | 121.7769 | 121.6901 | -0.1409 | 0.02852 | 0.073618 | -0.06093 | -0.094053 | 0.013707 | 0.058115 | -0.095467 | 0.028474 | 0.090425 | 0.097166 | 0.014459 | -0.014015 | -0.00659 | -0.09332 | 0.073906 | -121.8775 | 0.19789 | 0.10844 | 0.034537 | -121.7697 | -121.7253 | 122.0432 | 121.9462 | 121.8595 | 0.34935 | -121.9243 | 0.07532 | 0.18308 | 0.22749 | 0.24299 | -121.8789
1909.25 | 122.0718 | -0.16937 | 121.7789 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.0645 | -0.0088863 | 0.05311 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019613 | 0.028562 | 0.016073 | -0.072207 | 0.17539 | -0.14576 | 121.8785 | 121.7769 | 121.6901 | -0.13632 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.033053 | 0.09958 | 0.097166 | 0.023615 | -0.009438 | -0.002013 | -0.088743 | 0.064749 | -121.8638 | 0.19789 | 0.10844 | 0.043694 | -121.7652 | -121.7253 | 122.0478 | 121.9462 | 121.8595 | 0.34477 | -121.9152 | 0.084477 | 0.18308 | 0.22291 | 0.23841 | -121.8835
1911.0156 | 121.994 | -0.18768 | 121.8018 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064286 | -0.0084589 | 0.052897 | -0.0099192 | -0.0046531 | -0.0012713 | 0.02004 | 0.028562 | 0.016073 | -0.072207 | 0.16624 | -0.1366 | 121.8785 | 121.7814 | 121.6947 | -0.12258 | 0.02852 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.095467 | 0.0651 | 0.076692 | 0.11548 | 0.051082 | -0.014018 | -0.020322 | -0.10705 | 0.092216 | -121.8912 | 0.2162 | 0.12217 | 0.029958 | -121.7881 | -121.7436 | 122.0661 | 121.9691 | 121.8824 | 0.35392 | -121.9243 | 0.098208 | 0.20139 | 0.2458 | 0.2613 | -121.8972
1912.7188 | 121.9574 | -0.19684 | 121.7972 | 1.4211e-13 | -0.03982 | 0.0016453 | 0.0645 | -0.0088863 | 0.052683 | -0.0022892 | -0.0044395 | -0.0016987 | 0.02004 | 0.028775 | 0.016287 | -0.067628 | 0.17539 | -0.15034 | 121.8876 | 121.786 | 121.6993 | -0.12716 | 0.023941 | 0.073618 | -0.056351 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.069676 | 0.090427 | 0.12921 | 0.046502 | -0.023174 | -0.011165 | -0.097896 | 0.092214 | -121.8821 | 0.22078 | 0.14049 | 0.048273 | -121.7835 | -121.7391 | 122.0844 | 121.9829 | 121.8961 | 0.37223 | -121.9243 | 0.11194 | 0.21055 | 0.25495 | 0.27046 | -121.9018
1914.4844 | 122.0078 | -0.16937 | 121.8018 | 1.4211e-13 | -0.03982 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | 0.0053413 | -0.0044395 | -0.0012713 | 0.02004 | 0.028134 | 0.016287 | -0.067628 | 0.17539 | -0.14576 | 121.883 | 121.786 | 121.6901 | -0.13174 | 0.019362 | 0.073618 | -0.070087 | -0.094053 | 0.013707 | 0.062694 | -0.10462 | 0.037632 | 0.081271 | 0.10175 | 0.023615 | -0.014017 | -0.015743 | -0.11163 | 0.064749 | -121.8958 | 0.18873 | 0.099286 | 0.034537 | -121.7881 | -121.7391 | 122.0524 | 121.9554 | 121.8595 | 0.34477 | -121.9335 | 0.07532 | 0.18308 | 0.23207 | 0.24299 | -121.9064
1916.2656 | 121.9757 | -0.20599 | 121.7926 | 1.4211e-13 | -0.040034 | 0.0016453 | 0.064286 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028775 | 0.016287 | -0.067628 | 0.17539 | -0.14576 | 121.8739 | 121.7814 | 121.6901 | -0.13174 | 0.033099 | 0.06904 | -0.06093 | -0.089475 | 0.022864 | 0.048958 | -0.10462 | 0.074253 | 0.081269 | 0.13837 | 0.060236 | -0.014017 | -0.011167 | -0.10248 | 0.10137 | -121.8821 | 0.23909 | 0.14506 | 0.043694 | -121.7697 | -121.7436 | 122.0799 | 121.9874 | 121.8961 | 0.38139 | -121.9243 | 0.11652 | 0.22886 | 0.25495 | 0.27503 | -121.8972
1918.0312 | 121.9345 | -0.21973 | 121.8246 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.0645 | -0.0086727 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.019827 | 0.028348 | 0.0165 | -0.067628 | 0.17539 | -0.14118 | 121.8785 | 121.7769 | 121.6947 | -0.13174 | 0.023941 | 0.073618 | -0.06093 | -0.094053 | 0.018285 | 0.062694 | -0.10004 | 0.087986 | 0.053804 | 0.1521 | 0.078547 | -0.009439 | -0.047789 | -0.12994 | 0.11968 | -121.9187 | 0.24367 | 0.1588 | 0.039115 | -121.8064 | -121.762 | 122.0982 | 121.9966 | 121.9144 | 0.39512 | -121.9564 | 0.12567 | 0.23801 | 0.28242 | 0.29335 | -121.9247
1919.7344 | 121.9757 | -0.20142 | 121.788 | 1.4211e-13 | -0.040247 | 0.0012179 | 0.064286 | -0.0088863 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.028775 | 0.016287 | -0.067628 | 0.17997 | -0.14118 | 121.8876 | 121.7906 | 121.7039 | -0.13174 | 0.033099 | 0.06904 | -0.056351 | -0.080318 | 0.022864 | 0.058115 | -0.10462 | 0.069675 | 0.099582 | 0.13379 | 0.060236 | -0.009439 | 0.002569 | -0.084162 | 0.096792 | -121.8683 | 0.23452 | 0.14506 | 0.048273 | -121.7652 | -121.7299 | 122.089 | 121.992 | 121.9053 | 0.38139 | -121.9198 | 0.1211 | 0.22428 | 0.25953 | 0.27046 | -121.8926
1921.5 | 121.9437 | -0.21057 | 121.7972 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064286 | -0.0082453 | 0.052897 | -0.0099192 | -0.0037985 | -0.0012713 | 0.020254 | 0.028348 | 0.016287 | -0.067628 | 0.17997 | -0.14118 | 121.883 | 121.7906 | 121.6993 | -0.13174 | 0.023941 | 0.073618 | -0.070087 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.07883 | 0.085849 | 0.14294 | 0.069391 | -0.009439 | -0.006586 | -0.097896 | 0.11053 | -121.8821 | 0.23451 | 0.14048 | 0.029958 | -121.7835 | -121.7436 | 122.0936 | 122.0012 | 121.9099 | 0.39054 | -121.9289 | 0.12568 | 0.22428 | 0.26411 | 0.28419 | -121.8972
1923.2656 | 122.0535 | -0.15564 | 121.756 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.0645 | -0.0084589 | 0.052683 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.028348 | 0.016073 | -0.058472 | 0.17539 | -0.14118 | 121.883 | 121.7906 | 121.7039 | -0.118 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.058115 | -0.10004 | 0.037636 | 0.12705 | 0.097168 | 0.01446 | -0.023176 | 0.034613 | -0.052118 | 0.055595 | -121.8409 | 0.17958 | 0.09471 | 0.039115 | -121.7331 | -121.6979 | 122.0387 | 121.9462 | 121.8595 | 0.33103 | -121.874 | 0.070744 | 0.1785 | 0.21376 | 0.22468 | -121.856
1924.9688 | 121.9711 | -0.20142 | 121.8201 | 1.4211e-13 | -0.040034 | 0.0016453 | 0.064286 | -0.0088863 | 0.052469 | -0.0022892 | -0.0040121 | -0.0012713 | 0.019827 | 0.028348 | 0.016073 | -0.058472 | 0.17539 | -0.1366 | 121.8922 | 121.8043 | 121.7084 | -0.12258 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.078833 | 0.072117 | 0.14294 | 0.064815 | -0.014018 | -0.015737 | -0.11163 | 0.10137 | -121.9095 | 0.22536 | 0.14049 | 0.039115 | -121.8109 | -121.7574 | 122.0936 | 122.0057 | 121.9099 | 0.37681 | -121.9427 | 0.11194 | 0.21054 | 0.26411 | 0.27503 | -121.9201
1926.7344 | 121.9757 | -0.17395 | 121.8292 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.0645 | -0.0090999 | 0.052897 | -0.0022892 | -0.0044395 | -0.0016987 | 0.020467 | 0.028348 | 0.016287 | -0.053893 | 0.17081 | -0.13202 | 121.8876 | 121.7998 | 121.7084 | -0.12258 | 0.02852 | 0.073618 | -0.06093 | -0.094053 | 0.013707 | 0.053537 | -0.10004 | 0.051367 | 0.058383 | 0.12006 | 0.041927 | -0.00944 | -0.029472 | -0.12078 | 0.073905 | -121.9233 | 0.20247 | 0.11302 | 0.039115 | -121.8155 | -121.7757 | 122.0616 | 121.9737 | 121.8824 | 0.34476 | -121.9518 | 0.079897 | 0.18766 | 0.22749 | 0.24757 | -121.9293
1928.4844 | 121.9391 | -0.20142 | 121.8384 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064286 | -0.0088863 | 0.052683 | -0.0099192 | -0.0035849 | -0.0014849 | 0.02004 | 0.028562 | 0.016287 | -0.053893 | 0.17997 | -0.13202 | 121.9013 | 121.7998 | 121.713 | -0.118 | 0.02852 | 0.078197 | -0.06093 | -0.089475 | 0.013707 | 0.053537 | -0.095467 | 0.083412 | 0.062963 | 0.14752 | 0.069393 | -0.014019 | -0.038627 | -0.12536 | 0.10595 | -121.9279 | 0.22994 | 0.14049 | 0.034537 | -121.8247 | -121.7848 | 122.1028 | 122.0012 | 121.9144 | 0.38139 | -121.9564 | 0.11194 | 0.21512 | 0.25495 | 0.27961 | -121.9338
1930.1875 | 121.9116 | -0.1831 | 121.8475 | 1.4211e-13 | -0.03982 | 0.0014317 | 0.064286 | -0.0086727 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.020254 | 0.028775 | 0.016073 | -0.044736 | 0.17997 | -0.12287 | 121.9059 | 121.8089 | 121.7222 | -0.118 | 0.02852 | 0.073618 | -0.056351 | -0.084896 | 0.022864 | 0.053537 | -0.10004 | 0.065101 | 0.058387 | 0.13837 | 0.060239 | -0.004862 | -0.038624 | -0.12536 | 0.08306 | -121.9324 | 0.21162 | 0.12675 | 0.043694 | -121.8247 | -121.794 | 122.089 | 121.992 | 121.9053 | 0.36308 | -121.9655 | 0.098209 | 0.20597 | 0.23664 | 0.25672 | -121.9476
1931.9531 | 121.9711 | -0.1831 | 121.8338 | 1.4211e-13 | -0.040034 | 0.0016453 | 0.064714 | -0.0086727 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.028775 | 0.016073 | -0.044736 | 0.17997 | -0.12287 | 121.9059 | 121.8089 | 121.7176 | -0.118 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.009128 | 0.058115 | -0.095467 | 0.065101 | 0.07212 | 0.13837 | 0.060239 | -0.004862 | -0.024891 | -0.1162 | 0.087638 | -121.9187 | 0.20705 | 0.12217 | 0.034537 | -121.8247 | -121.7757 | 122.089 | 121.992 | 121.9007 | 0.36308 | -121.9518 | 0.098209 | 0.19223 | 0.24122 | 0.25215 | -121.9293
1933.6719 | 121.9391 | -0.19226 | 121.8384 | 1.4211e-13 | -0.040247 | 0.0014317 | 0.064286 | -0.0086727 | 0.05311 | -0.0099192 | -0.0042257 | -0.0021259 | 0.02004 | 0.028775 | 0.0165 | -0.044736 | 0.18455 | -0.11829 | 121.9105 | 121.8135 | 121.7222 | -0.10885 | 0.019362 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.048958 | -0.10462 | 0.083414 | 0.07212 | 0.14752 | 0.073973 | -0.009441 | -0.02489 | -0.1162 | 0.087637 | -121.9233 | 0.21162 | 0.13133 | 0.043694 | -121.8155 | -121.7894 | 122.1028 | 122.0058 | 121.9144 | 0.37681 | -121.9472 | 0.10736 | 0.21512 | 0.24122 | 0.2613 | -121.943
1935.4375 | 121.9391 | -0.17395 | 121.8292 | 1.4211e-13 | -0.040034 | 0.0016453 | 0.0645 | -0.0088863 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028989 | 0.016287 | -0.044736 | 0.18455 | -0.12287 | 121.9059 | 121.8135 | 121.7222 | -0.10885 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.065103 | 0.076697 | 0.12921 | 0.051084 | -0.014019 | -0.015735 | -0.10705 | 0.073905 | -121.9141 | 0.19789 | 0.10844 | 0.034536 | -121.8155 | -121.7711 | 122.0799 | 121.9874 | 121.8961 | 0.3585 | -121.9381 | 0.089054 | 0.18766 | 0.23206 | 0.24757 | -121.9293
1937.2031 | 121.9894 | -0.16479 | 121.8292 | 1.4211e-13 | -0.040034 | 0.0018589 | 0.0645 | -0.0084589 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028562 | 0.016287 | -0.044736 | 0.18455 | -0.11829 | 121.9151 | 121.8135 | 121.7222 | -0.11342 | 0.02852 | 0.073618 | -0.056351 | -0.084896 | 0.009128 | 0.053537 | -0.10462 | 0.05137 | 0.085853 | 0.12006 | 0.046507 | -0.004863 | -0.015735 | -0.10705 | 0.060171 | -121.9141 | 0.19331 | 0.10844 | 0.048273 | -121.8201 | -121.7757 | 122.0799 | 121.9783 | 121.887 | 0.34935 | -121.9426 | 0.079899 | 0.17392 | 0.21833 | 0.23841 | -121.9338
1938.9062 | 122.049 | -0.13733 | 121.8201 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064286 | -0.0088863 | 0.052897 | -0.01755 | -0.0044395 | -0.0014849 | 0.020254 | 0.028348 | 0.0165 | -0.040158 | 0.18455 | -0.12287 | 121.9151 | 121.8181 | 121.7222 | -0.10427 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.033061 | 0.095009 | 0.097171 | 0.014463 | -0.018598 | -0.002001 | -0.097891 | 0.037284 | -121.905 | 0.15669 | 0.076399 | 0.039115 | -121.8064 | -121.7665 | 122.0524 | 121.9554 | 121.8595 | 0.32188 | -121.9243 | 0.052433 | 0.15104 | 0.19087 | 0.21095 | -121.9201
1940.6719 | 121.9528 | -0.16937 | 121.8704 | 1.4211e-13 | -0.040034 | 0.0014317 | 0.064073 | -0.0084589 | 0.052897 | -0.01755 | -0.0042257 | -0.0016987 | 0.020254 | 0.028775 | 0.015859 | -0.040158 | 0.17997 | -0.12287 | 121.9197 | 121.8135 | 121.7313 | -0.10427 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | 0.022864 | 0.053537 | -0.10004 | 0.065105 | 0.049234 | 0.12921 | 0.046507 | -0.018598 | -0.056933 | -0.13909 | 0.069328 | -121.9599 | 0.18416 | 0.10844 | 0.039115 | -121.8476 | -121.8169 | 122.089 | 121.9829 | 121.9007 | 0.34935 | -121.9747 | 0.079898 | 0.19224 | 0.22291 | 0.24299 | -121.9705
1942.375 | 121.994 | -0.16022 | 121.8384 | 1.4211e-13 | -0.03982 | 0.0018589 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.02004 | 0.028348 | 0.016073 | -0.03558 | 0.18913 | -0.11829 | 121.9151 | 121.8226 | 121.7359 | -0.10427 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.10004 | 0.055949 | 0.076698 | 0.12464 | 0.041929 | -0.01402 | -0.015733 | -0.10247 | 0.060172 | -121.9233 | 0.18874 | 0.099287 | 0.039115 | -121.8201 | -121.7848 | 122.0753 | 121.9829 | 121.8961 | 0.34935 | -121.9426 | 0.075321 | 0.1785 | 0.21375 | 0.23384 | -121.9384
1944.125 | 121.9437 | -0.18768 | 121.8658 | 1.4211e-13 | -0.040034 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | 0.012972 | -0.0042257 | -0.0012713 | 0.019613 | 0.028562 | 0.016287 | -0.040158 | 0.17539 | -0.11371 | 121.9151 | 121.8181 | 121.7313 | -0.10427 | 0.014784 | 0.078197 | -0.06093 | -0.094053 | 0.018285 | 0.053537 | -0.1092 | 0.083415 | 0.049232 | 0.14752 | 0.073973 | -0.009442 | -0.047778 | -0.13451 | 0.07848 | -121.9599 | 0.20247 | 0.12675 | 0.048273 | -121.8476 | -121.8123 | 122.1028 | 122.0058 | 121.919 | 0.36308 | -121.9701 | 0.09363 | 0.20597 | 0.24122 | 0.26588 | -121.975
1945.9062 | 122.0078 | -0.16479 | 121.8475 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.064286 | -0.0088863 | 0.052683 | -0.02518 | -0.0044395 | -0.0010577 | 0.02004 | 0.028775 | 0.016287 | -0.040158 | 0.17997 | -0.11829 | 121.9197 | 121.8226 | 121.7359 | -0.10885 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.058115 | -0.10462 | 0.055948 | 0.072122 | 0.12464 | 0.046507 | -0.009441 | -0.024888 | -0.11162 | 0.060171 | -121.9324 | 0.18874 | 0.10386 | 0.043694 | -121.8247 | -121.7894 | 122.0845 | 121.9874 | 121.9007 | 0.34477 | -121.9564 | 0.079899 | 0.18766 | 0.22291 | 0.23384 | -121.9522
1947.5938 | 121.9528 | -0.16937 | 121.8704 | 1.4211e-13 | -0.040247 | 0.0020727 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.028562 | 0.016287 | -0.03558 | 0.18455 | -0.10913 | 121.9197 | 121.8272 | 121.7313 | -0.10427 | 0.019362 | 0.06904 | -0.051772 | -0.089475 | 0.018285 | 0.062694 | -0.095467 | 0.065105 | 0.049234 | 0.13379 | 0.060241 | -0.004864 | -0.043197 | -0.13909 | 0.073906 | -121.9599 | 0.18873 | 0.1176 | 0.043695 | -121.8521 | -121.8077 | 122.089 | 121.9966 | 121.9007 | 0.35392 | -121.9747 | 0.079898 | 0.18766 | 0.23207 | 0.23841 | -121.9659
1949.3438 | 122.0352 | -0.14648 | 121.7972 | 1.4211e-13 | -0.040034 | 0.0014317 | 0.064714 | -0.0090999 | 0.052683 | -0.0022892 | -0.0044395 | -0.0016987 | 0.02004 | 0.028989 | 0.016073 | -0.031001 | 0.18913 | -0.11371 | 121.9288 | 121.8318 | 121.7359 | -0.10427 | 0.019362 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.042216 | 0.13163 | 0.11548 | 0.032774 | -0.009442 | 0.034624 | -0.061267 | 0.04186 | -121.8821 | 0.16585 | 0.080975 | 0.039115 | -121.7835 | -121.7436 | 122.0753 | 121.9783 | 121.8824 | 0.33561 | -121.9014 | 0.061588 | 0.16019 | 0.20002 | 0.2201 | -121.9018
1951.1094 | 122.0352 | -0.13733 | 121.8384 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064286 | -0.0088863 | 0.052897 | 0.0053413 | -0.0044395 | -0.0014849 | 0.020467 | 0.028989 | 0.0165 | -0.03558 | 0.18455 | -0.10913 | 121.9242 | 121.8272 | 121.7405 | -0.10427 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.095467 | 0.033061 | 0.085855 | 0.10175 | 0.028197 | -0.004864 | -0.011154 | -0.097887 | 0.041862 | -121.9233 | 0.16127 | 0.07182 | 0.029958 | -121.8201 | -121.7757 | 122.0616 | 121.9646 | 121.8778 | 0.32188 | -121.9426 | 0.052433 | 0.15561 | 0.20002 | 0.21095 | -121.9338
1952.7969 | 121.962 | -0.14648 | 121.843 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.064286 | -0.0086727 | 0.052897 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019827 | 0.028775 | 0.016073 | -0.026423 | 0.18913 | -0.10455 | 121.9288 | 121.8318 | 121.7405 | -0.09511 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.051374 | 0.085856 | 0.12006 | 0.041931 | -0.009443 | -0.011153 | -0.10246 | 0.046439 | -121.9324 | 0.16127 | 0.085554 | 0.039115 | -121.8293 | -121.7848 | 122.0753 | 121.9783 | 121.887 | 0.33561 | -121.9381 | 0.057009 | 0.16019 | 0.2046 | 0.2201 | -121.943
1954.5469 | 122.0032 | -0.11902 | 121.843 | 1.4211e-13 | -0.040461 | 0.0020727 | 0.0645 | -0.0088863 | 0.052683 | -0.0022892 | -0.0042257 | -0.0016987 | 0.02004 | 0.028562 | 0.016287 | -0.003531 | 0.17997 | -0.081662 | 121.9425 | 121.8501 | 121.7588 | -0.072215 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.058115 | -0.10004 | 0.046804 | 0.099591 | 0.11549 | 0.037357 | -0.009447 | 0.007163 | -0.084151 | 0.018974 | -121.9279 | 0.14754 | 0.058089 | 0.039115 | -121.8201 | -121.7848 | 122.0616 | 121.9691 | 121.8778 | 0.29899 | -121.9152 | 0.034123 | 0.14188 | 0.17713 | 0.18806 | -121.943
1956.3281 | 121.9391 | -0.15564 | 121.8567 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064714 | -0.0088863 | 0.052897 | -0.0099192 | -0.0040121 | -0.0014849 | 0.020254 | 0.028989 | 0.016287 | -0.008109 | 0.18455 | -0.072505 | 121.9654 | 121.8684 | 121.7817 | -0.067636 | 0.019362 | 0.078197 | -0.070087 | -0.080318 | 0.018285 | 0.053537 | -0.095467 | 0.088004 | 0.10875 | 0.14753 | 0.083135 | -0.004869 | 0.011747 | -0.07499 | 0.060173 | -121.937 | 0.175 | 0.085553 | 0.02538 | -121.8384 | -121.8032 | 122.1211 | 122.0241 | 121.9373 | 0.34019 | -121.9243 | 0.075322 | 0.17392 | 0.20918 | 0.23384 | -121.9522
1958.0781 | 121.9711 | -0.14191 | 121.8842 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019827 | 0.028348 | 0.0165 | 0.001048 | 0.18455 | -0.072505 | 121.9563 | 121.8684 | 121.7771 | -0.067636 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.10462 | 0.074271 | 0.072128 | 0.14295 | 0.069402 | -0.004869 | -0.015719 | -0.10704 | 0.037283 | -121.9691 | 0.16127 | 0.080977 | 0.043694 | -121.8659 | -121.8306 | 122.0982 | 122.0103 | 121.919 | 0.32646 | -121.9518 | 0.057011 | 0.16019 | 0.19544 | 0.2201 | -121.9888
1959.7656 | 122.0673 | -0.07782 | 121.8475 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064286 | -0.0090999 | 0.05311 | -0.0099192 | -0.0040121 | -0.0014849 | 0.020254 | 0.028775 | 0.016073 | -0.008109 | 0.17997 | -0.081662 | 121.9746 | 121.8776 | 121.7725 | -0.063057 | 0.023941 | 0.06904 | -0.056351 | -0.084896 | 0.018285 | 0.053537 | -0.10004 | 0.014763 | 0.12706 | 0.069711 | -0.003842 | -0.018605 | 0.03006 | -0.074992 | -0.022225 | -121.9324 | 0.10176 | 0.021469 | 0.043694 | -121.8292 | -121.794 | 122.0524 | 121.9554 | 121.8504 | 0.25779 | -121.9106 | -0.007076 | 0.096105 | 0.13136 | 0.14686 | -121.9476
1961.5156 | 122.0215 | -0.11902 | 121.8521 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.0645 | -0.0086727 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028562 | 0.016287 | -0.003531 | 0.18455 | -0.072505 | 121.97 | 121.8684 | 121.7771 | -0.067636 | 0.02852 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.048958 | -0.095467 | 0.051383 | 0.11791 | 0.11549 | 0.046514 | -0.004869 | 0.016324 | -0.074992 | 0.023552 | -121.9416 | 0.14754 | 0.058089 | 0.034537 | -121.8292 | -121.8032 | 122.089 | 121.9875 | 121.8961 | 0.30357 | -121.9197 | 0.029544 | 0.14188 | 0.16798 | 0.19722 | -121.9476
1963.2656 | 122.0764 | -0.07782 | 121.875 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.0645 | -0.0088863 | 0.052683 | -0.0022892 | -0.0040121 | -0.0014849 | 0.02004 | 0.028562 | 0.016287 | -0.003531 | 0.18913 | -0.072505 | 121.9654 | 121.8639 | 121.7771 | -0.072215 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.005605 | 0.09044 | 0.074289 | 0.005315 | -0.00029 | -0.011143 | -0.09788 | -0.026804 | -121.9599 | 0.10634 | 0.01689 | 0.043694 | -121.8613 | -121.8169 | 122.0433 | 121.9417 | 121.8549 | 0.26695 | -121.9472 | -0.007076 | 0.091527 | 0.13594 | 0.15602 | -121.9796
1964.9688 | 121.962 | -0.14648 | 121.9162 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064714 | -0.0090999 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020254 | 0.028775 | 0.016287 | 0.001048 | 0.18455 | -0.072505 | 121.97 | 121.8639 | 121.7817 | -0.067636 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.053537 | -0.10462 | 0.078848 | 0.053819 | 0.14753 | 0.073979 | -0.004869 | -0.052342 | -0.1345 | 0.04186 | -121.9965 | 0.16585 | 0.085554 | 0.043694 | -121.9025 | -121.8627 | 122.1165 | 122.0103 | 121.9282 | 0.33103 | -121.9838 | 0.066166 | 0.16019 | 0.20002 | 0.22468 | -122.0208
1966.7344 | 122.0169 | -0.10986 | 121.8475 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064714 | -0.0086727 | 0.052683 | -0.0099192 | -0.0044395 | -0.0012713 | 0.02004 | 0.028989 | 0.0165 | -0.003531 | 0.17997 | -0.077084 | 121.9517 | 121.8684 | 121.7771 | -0.063057 | 0.023941 | 0.078197 | -0.070087 | -0.094053 | 0.018285 | 0.053537 | -0.10462 | 0.046806 | 0.10417 | 0.10633 | 0.032779 | -0.014027 | 0.020902 | -0.070414 | 0.005239 | -121.9416 | 0.1338 | 0.039776 | 0.034537 | -121.8292 | -121.794 | 122.0616 | 121.9783 | 121.887 | 0.28984 | -121.9106 | 0.01581 | 0.12815 | 0.1634 | 0.18806 | -121.9522
1968.4375 | 122.0673 | -0.082397 | 121.843 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.0645 | -0.0090999 | 0.05311 | -0.01755 | -0.0040121 | -0.0012713 | 0.02004 | 0.028775 | 0.016287 | 0.001048 | 0.18913 | -0.067927 | 121.97 | 121.8684 | 121.7817 | -0.067636 | 0.019362 | 0.073618 | -0.065509 | -0.094053 | 0.022864 | 0.053537 | -0.10462 | 0.014761 | 0.12706 | 0.083445 | 0.01447 | -0.000291 | 0.025479 | -0.061258 | -0.022227 | -121.937 | 0.10176 | 0.016888 | 0.039115 | -121.8201 | -121.7894 | 122.0524 | 121.9508 | 121.8641 | 0.27153 | -121.9106 | -0.011656 | 0.10526 | 0.13593 | 0.15602 | -121.9476
1970.1875 | 122.0581 | -0.10986 | 121.8613 | 1.4211e-13 | -0.040247 | 0.0020727 | 0.0645 | -0.0088863 | 0.052683 | -0.0099192 | -0.0042257 | -0.0016987 | 0.02004 | 0.028775 | 0.0165 | 0.001048 | 0.18913 | -0.067927 | 121.9654 | 121.8776 | 121.7771 | -0.067636 | 0.014784 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.053537 | -0.10462 | 0.042227 | 0.10417 | 0.11091 | 0.041936 | -0.000291 | 0.016327 | -0.084147 | 0.005239 | -121.9507 | 0.12465 | 0.048933 | 0.043694 | -121.843 | -121.8077 | 122.0753 | 121.9875 | 121.887 | 0.29899 | -121.9289 | 0.020388 | 0.12815 | 0.1634 | 0.18806 | -121.9659
1971.9531 | 121.9482 | -0.13733 | 121.907 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064286 | -0.0084589 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019827 | 0.028775 | 0.016287 | 0.005626 | 0.18913 | -0.077084 | 121.9654 | 121.873 | 121.7817 | -0.063057 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.10462 | 0.074272 | 0.058397 | 0.14295 | 0.060245 | -0.014027 | -0.034028 | -0.12534 | 0.032705 | -121.9965 | 0.16127 | 0.076399 | 0.043694 | -121.8888 | -121.8489 | 122.1028 | 122.0103 | 121.919 | 0.32646 | -121.9701 | 0.047854 | 0.15561 | 0.19544 | 0.21095 | -122.0117
1973.6562 | 122.0673 | -0.10529 | 121.875 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.0645 | -0.0086727 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.02004 | 0.028562 | 0.016287 | 0.001048 | 0.18455 | -0.072505 | 121.97 | 121.8822 | 121.7817 | -0.067636 | 0.014784 | 0.073618 | -0.056351 | -0.075739 | 0.013707 | 0.062694 | -0.10004 | 0.03765 | 0.095018 | 0.10633 | 0.032781 | -0.004869 | 0.007172 | -0.093301 | 0.005241 | -121.9507 | 0.12007 | 0.048935 | 0.043694 | -121.8613 | -121.8123 | 122.0753 | 121.9875 | 121.887 | 0.28984 | -121.9426 | 0.029547 | 0.11899 | 0.16798 | 0.1789 | -121.975
1975.4062 | 122.0673 | -0.086975 | 121.8521 | 1.4211e-13 | -0.040034 | 0.0020727 | 0.064286 | -0.0086727 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.020254 | 0.028775 | 0.016287 | -0.008109 | 0.18455 | -0.072505 | 121.97 | 121.873 | 121.7863 | -0.072215 | 0.019362 | 0.06904 | -0.070087 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.01476 | 0.11791 | 0.078866 | 0.01447 | -0.00029 | 0.020903 | -0.065834 | -0.017649 | -121.937 | 0.10634 | 0.016888 | 0.034537 | -121.8384 | -121.794 | 122.057 | 121.96 | 121.8733 | 0.27153 | -121.9243 | 0.002079 | 0.10068 | 0.14509 | 0.15602 | -121.9567
1977.0938 | 121.9345 | -0.13733 | 121.8887 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.0645 | -0.0088863 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019613 | 0.028989 | 0.016073 | 0.001048 | 0.18455 | -0.067927 | 121.9746 | 121.8684 | 121.7817 | -0.063057 | 0.02852 | 0.064461 | -0.051772 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.074272 | 0.085863 | 0.13838 | 0.069402 | -0.00487 | -0.020297 | -0.10703 | 0.032705 | -121.9736 | 0.16585 | 0.085557 | 0.052852 | -121.875 | -121.8306 | 122.1119 | 122.0058 | 121.919 | 0.32188 | -121.9518 | 0.052433 | 0.15104 | 0.19544 | 0.20179 | -121.9934
1978.8438 | 122.0535 | -0.086975 | 121.8704 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.0645 | -0.0088863 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.028562 | 0.016287 | 0.001048 | 0.18913 | -0.067927 | 121.9609 | 121.8822 | 121.7863 | -0.076794 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.013707 | 0.053537 | -0.10004 | 0.010181 | 0.090439 | 0.088023 | 0.019048 | 0.008867 | 0.01175 | -0.084144 | -0.01307 | -121.9599 | 0.11092 | 0.030624 | 0.043694 | -121.8567 | -121.8169 | 122.0478 | 121.9691 | 121.8733 | 0.2761 | -121.9472 | -0.0025 | 0.10068 | 0.14051 | 0.16517 | -121.9705
1980.5938 | 121.9528 | -0.13733 | 121.9208 | 1.4211e-13 | -0.03982 | 0.0018589 | 0.0645 | -0.0086727 | 0.052897 | -0.0022892 | -0.0044395 | -0.0016987 | 0.02004 | 0.028989 | 0.0165 | 0.001048 | 0.18455 | -0.067927 | 121.9746 | 121.873 | 121.7863 | -0.067636 | 0.023941 | 0.06904 | -0.06093 | -0.089475 | 0.009128 | 0.053537 | -0.10004 | 0.069693 | 0.05382 | 0.13838 | 0.069402 | -0.000291 | -0.047761 | -0.1345 | 0.037284 | -122.0103 | 0.16127 | 0.076399 | 0.039115 | -121.9116 | -121.8672 | 122.1119 | 122.0103 | 121.9236 | 0.32188 | -121.9884 | 0.047854 | 0.14646 | 0.19087 | 0.20637 | -122.0208
1982.3594 | 121.962 | -0.1236 | 121.907 | 1.4211e-13 | -0.040247 | 0.0014317 | 0.0645 | -0.0093137 | 0.052897 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.028989 | 0.0165 | 0.001048 | 0.19371 | -0.067927 | 121.9654 | 121.8776 | 121.7909 | -0.067636 | 0.023941 | 0.082776 | -0.056351 | -0.089475 | 0.009128 | 0.053537 | -0.10004 | 0.05596 | 0.058397 | 0.12464 | 0.055669 | -0.000291 | -0.029449 | -0.11619 | 0.023551 | -121.9965 | 0.14754 | 0.067245 | 0.043694 | -121.8979 | -121.8535 | 122.089 | 122.0012 | 121.9145 | 0.3173 | -121.9747 | 0.034121 | 0.13272 | 0.17713 | 0.20637 | -122.0071
1984.125 | 121.9574 | -0.11902 | 121.9116 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.0645 | -0.0090999 | 0.05311 | -0.0022892 | -0.0040121 | -0.0012713 | 0.019613 | 0.028775 | 0.016073 | 0.010204 | 0.19829 | -0.072505 | 121.97 | 121.873 | 121.7909 | -0.063057 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.055962 | 0.058397 | 0.12922 | 0.046514 | -0.009448 | -0.038606 | -0.12076 | 0.018974 | -121.9965 | 0.14754 | 0.05351 | 0.034536 | -121.8979 | -121.8535 | 122.089 | 121.992 | 121.9099 | 0.31731 | -121.9747 | 0.034123 | 0.13273 | 0.17713 | 0.19722 | -122.0117
1985.9062 | 121.962 | -0.1236 | 121.9437 | 1.4211e-13 | -0.040461 | 0.0020727 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.020467 | 0.028775 | 0.016287 | 0.010204 | 0.19371 | -0.077084 | 121.9792 | 121.8822 | 121.7909 | -0.067636 | 0.023941 | 0.073618 | -0.056351 | -0.084896 | 0.009128 | 0.053537 | -0.10462 | 0.05596 | 0.03551 | 0.1338 | 0.046512 | -0.009448 | -0.061493 | -0.15281 | 0.018972 | -122.0286 | 0.14754 | 0.067245 | 0.048273 | -121.9345 | -121.8901 | 122.1028 | 122.0058 | 121.9145 | 0.3173 | -122.0113 | 0.0387 | 0.13272 | 0.17713 | 0.19721 | -122.0483
1987.6094 | 121.9391 | -0.11902 | 121.8887 | 1.4211e-13 | -0.040675 | 0.0020727 | 0.0645 | -0.0088863 | 0.052897 | -0.01755 | -0.0044395 | -0.0012713 | 0.02004 | 0.028775 | 0.015859 | 0.010204 | 0.19371 | -0.067927 | 121.9746 | 121.8822 | 121.7909 | -0.063057 | 0.02852 | 0.078197 | -0.056351 | -0.089475 | 0.013707 | 0.058115 | -0.095467 | 0.055962 | 0.085863 | 0.12922 | 0.051092 | -0.00487 | -0.006561 | -0.097877 | 0.023552 | -121.9782 | 0.14754 | 0.062668 | 0.039116 | -121.875 | -121.8306 | 122.0936 | 122.0012 | 121.9099 | 0.31273 | -121.9518 | 0.029544 | 0.13273 | 0.17713 | 0.19722 | -121.9842
1989.3594 | 122.0901 | -0.09613 | 121.8704 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.0645 | -0.0086727 | 0.052897 | -0.0099192 | -0.0042257 | -0.0012713 | 0.02004 | 0.028989 | 0.016287 | 0.005626 | 0.19829 | -0.081662 | 121.9746 | 121.8776 | 121.7909 | -0.058478 | 0.019362 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.10462 | 0.037652 | 0.10417 | 0.10176 | 0.014468 | -0.023184 | 0.007172 | -0.079566 | -0.008494 | -121.9599 | 0.11549 | 0.030621 | 0.039115 | -121.8567 | -121.8077 | 122.0707 | 121.9737 | 121.887 | 0.29442 | -121.9289 | 0.006655 | 0.10984 | 0.15882 | 0.16975 | -121.975
1991.0625 | 122.0673 | -0.07782 | 121.8475 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.064286 | -0.0088863 | 0.052683 | -0.01755 | -0.0044395 | -0.0019123 | 0.020254 | 0.028775 | 0.016287 | 0.005626 | 0.19829 | -0.067927 | 121.9792 | 121.8776 | 121.7954 | -0.053899 | 0.014784 | 0.06904 | -0.06093 | -0.089475 | 0.009128 | 0.048958 | -0.10004 | 0.023921 | 0.13164 | 0.083446 | 0.009893 | -0.014028 | 0.03006 | -0.052099 | -0.022225 | -121.937 | 0.092604 | 0.01689 | 0.039115 | -121.8384 | -121.7986 | 122.057 | 121.9554 | 121.8733 | 0.27611 | -121.9014 | -0.011655 | 0.086948 | 0.12678 | 0.14686 | -121.9476
1992.8281 | 121.9757 | -0.13275 | 121.8933 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064714 | -0.0086727 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.028775 | 0.016287 | 0.010204 | 0.19371 | -0.072505 | 121.9746 | 121.8822 | 121.8 | -0.063057 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.069694 | 0.081285 | 0.14295 | 0.060246 | -0.009448 | -0.011139 | -0.093298 | 0.028127 | -121.9782 | 0.15669 | 0.062664 | 0.034537 | -121.8796 | -121.8352 | 122.1073 | 122.0149 | 121.9328 | 0.32646 | -121.9564 | 0.047855 | 0.14646 | 0.19087 | 0.21095 | -121.9979
1994.5938 | 121.9574 | -0.13275 | 121.9254 | 1.4211e-13 | -0.040247 | 0.0016453 | 0.064714 | -0.0088863 | 0.052683 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019827 | 0.028989 | 0.0165 | 0.010204 | 0.18913 | -0.072505 | 121.9746 | 121.8822 | 121.7954 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.095467 | 0.060536 | 0.049242 | 0.14295 | 0.060246 | -0.00029 | -0.043182 | -0.12992 | 0.037284 | -122.0102 | 0.15669 | 0.071821 | 0.034537 | -121.9116 | -121.8718 | 122.1073 | 122.0149 | 121.9282 | 0.32188 | -121.9976 | 0.047855 | 0.14646 | 0.18629 | 0.21095 | -122.0208
1996.3125 | 122.0032 | -0.11902 | 121.8933 | 1.4211e-13 | -0.040034 | 0.0018589 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028989 | 0.016073 | 0.010204 | 0.18913 | -0.063349 | 121.9792 | 121.8822 | 121.7954 | -0.058478 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.013707 | 0.053537 | -0.095467 | 0.060541 | 0.085864 | 0.12922 | 0.05567 | -0.004871 | -0.011139 | -0.097876 | 0.023552 | -121.9782 | 0.14296 | 0.062668 | 0.039116 | -121.8796 | -121.8398 | 122.0982 | 122.0012 | 121.9145 | 0.30815 | -121.9518 | 0.034123 | 0.13273 | 0.17256 | 0.19722 | -121.9888
1998.0625 | 122.0581 | -0.091553 | 121.9025 | 1.4211e-13 | -0.040461 | 0.0020727 | 0.0645 | -0.0086727 | 0.052897 | -0.02518 | -0.0044395 | -0.0014849 | 0.020254 | 0.028775 | 0.015859 | 0.010204 | 0.19371 | -0.072505 | 121.97 | 121.8822 | 121.7954 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.037654 | 0.067552 | 0.10176 | 0.019048 | -0.018606 | -0.020294 | -0.10703 | -0.01765 | -121.9828 | 0.11091 | 0.030623 | 0.048273 | -121.8842 | -121.8398 | 122.0616 | 121.9737 | 121.887 | 0.28526 | -121.9564 | 0.011235 | 0.10984 | 0.15425 | 0.16975 | -122.0117
1999.8125 | 122.0535 | -0.10071 | 121.8796 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.0645 | -0.0086727 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.028775 | 0.0165 | 0.005626 | 0.19829 | -0.077084 | 121.9746 | 121.8776 | 121.7909 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.04223 | 0.095018 | 0.10633 | 0.023624 | -0.018606 | -0.001984 | -0.088722 | 0.000663 | -121.9691 | 0.12465 | 0.039778 | 0.039115 | -121.8704 | -121.8169 | 122.0753 | 121.9783 | 121.8916 | 0.29899 | -121.9381 | 0.011233 | 0.10984 | 0.1634 | 0.17433 | -121.9796
2001.5625 | 122.0215 | -0.1236 | 121.8887 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064286 | -0.0086727 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.029203 | 0.016287 | 0.010204 | 0.18913 | -0.072505 | 121.9792 | 121.8868 | 121.8 | -0.063057 | 0.019362 | 0.078197 | -0.056351 | -0.084896 | 0.009128 | 0.062694 | -0.10004 | 0.060539 | 0.090442 | 0.1338 | 0.051091 | -0.009448 | -0.001982 | -0.08872 | 0.023551 | -121.9736 | 0.14296 | 0.067245 | 0.043694 | -121.8796 | -121.826 | 122.1028 | 122.0103 | 121.9236 | 0.31272 | -121.9518 | 0.0387 | 0.13272 | 0.18629 | 0.20179 | -121.9888
2003.3281 | 121.9482 | -0.13275 | 121.9025 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064286 | -0.0088863 | 0.052897 | -0.0022892 | -0.0046531 | -0.0016987 | 0.020467 | 0.028989 | 0.016287 | 0.005626 | 0.19371 | -0.067927 | 121.9792 | 121.8868 | 121.7954 | -0.063057 | 0.023941 | 0.06904 | -0.065509 | -0.089475 | 0.009128 | 0.058115 | -0.10462 | 0.069694 | 0.076709 | 0.13838 | 0.064824 | -0.00487 | -0.015715 | -0.10703 | 0.028127 | -121.9919 | 0.15669 | 0.067242 | 0.039115 | -121.8933 | -121.8444 | 122.1119 | 122.0195 | 121.9282 | 0.32646 | -121.9655 | 0.043276 | 0.14188 | 0.19087 | 0.20179 | -122.0071
2005.0938 | 121.9803 | -0.13275 | 121.8887 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0040121 | -0.0012713 | 0.020254 | 0.028989 | 0.016287 | 0.005626 | 0.19829 | -0.072505 | 121.9792 | 121.8913 | 121.7954 | -0.067636 | 0.019362 | 0.064461 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.1092 | 0.065115 | 0.090442 | 0.13838 | 0.060246 | -0.004869 | 0.002597 | -0.093298 | 0.023548 | -121.9736 | 0.15211 | 0.071821 | 0.048273 | -121.875 | -121.8352 | 122.1119 | 122.0241 | 121.9282 | 0.33104 | -121.9564 | 0.047855 | 0.14646 | 0.18629 | 0.19721 | -121.9979
2006.7969 | 121.9803 | -0.11444 | 121.9162 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.064286 | -0.0088863 | 0.052897 | 0.0053413 | -0.0042257 | -0.0012713 | 0.02004 | 0.028989 | 0.016073 | 0.005626 | 0.19829 | -0.067927 | 121.9792 | 121.8913 | 121.7954 | -0.058478 | 0.019362 | 0.078197 | -0.056351 | -0.084896 | 0.009128 | 0.062694 | -0.10004 | 0.055963 | 0.062976 | 0.12007 | 0.046514 | -0.009449 | -0.024869 | -0.12076 | 0.014396 | -122.0011 | 0.1338 | 0.05809 | 0.043694 | -121.9071 | -121.8535 | 122.0936 | 122.0058 | 121.9099 | 0.31273 | -121.9747 | 0.029545 | 0.12357 | 0.17713 | 0.19264 | -122.0162
2008.5469 | 122.0535 | -0.09613 | 121.8704 | 1.4211e-13 | -0.040461 | 0.0014317 | 0.064714 | -0.0088863 | 0.052897 | -0.0022892 | -0.0042257 | -0.0010577 | 0.019827 | 0.028989 | 0.015859 | 0.010204 | 0.19371 | -0.063349 | 121.9792 | 121.8868 | 121.8046 | -0.067636 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.028494 | 0.10875 | 0.10633 | 0.032781 | 0.004287 | 0.016329 | -0.06583 | -0.003915 | -121.9553 | 0.12465 | 0.030621 | 0.034536 | -121.8567 | -121.8169 | 122.0753 | 121.9829 | 121.9007 | 0.28984 | -121.9381 | 0.011234 | 0.10984 | 0.14967 | 0.17433 | -121.9705
2010.3125 | 121.9803 | -0.1236 | 121.9025 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064928 | -0.0086727 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.028775 | 0.016073 | 0.005626 | 0.19371 | -0.067927 | 121.9792 | 121.8822 | 121.7954 | -0.067636 | 0.033099 | 0.073618 | -0.056351 | -0.084896 | 0.009128 | 0.053537 | -0.1092 | 0.05596 | 0.076709 | 0.12922 | 0.055669 | -0.000291 | -0.020294 | -0.10703 | 0.014393 | -121.9874 | 0.1567 | 0.067245 | 0.052852 | -121.8933 | -121.8489 | 122.1028 | 122.0058 | 121.919 | 0.3173 | -121.9701 | 0.0387 | 0.13272 | 0.17713 | 0.19721 | -122.0117
2012.0156 | 122.0306 | -0.10529 | 121.8658 | 1.4211e-13 | -0.040888 | 0.0014317 | 0.064714 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.02004 | 0.028775 | 0.015859 | 0.001048 | 0.19829 | -0.067927 | 121.9792 | 121.8868 | 121.7954 | -0.067636 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.10004 | 0.03765 | 0.11333 | 0.10633 | 0.037359 | -0.000291 | 0.020906 | -0.07041 | 0.005241 | -121.9462 | 0.12923 | 0.044356 | 0.039115 | -121.8521 | -121.8032 | 122.0845 | 121.992 | 121.9007 | 0.30357 | -121.9335 | 0.024968 | 0.11899 | 0.16798 | 0.1789 | -121.9659
2013.7656 | 121.9574 | -0.13733 | 121.907 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | -0.0022892 | -0.0040121 | -0.0016987 | 0.02004 | 0.028989 | 0.016073 | 0.005626 | 0.19829 | -0.077084 | 121.9929 | 121.8868 | 121.8 | -0.063057 | 0.019362 | 0.078197 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.1092 | 0.074272 | 0.085867 | 0.14295 | 0.060245 | -0.014027 | -0.020292 | -0.10703 | 0.028126 | -121.9965 | 0.15669 | 0.07182 | 0.043694 | -121.8933 | -121.8443 | 122.1302 | 122.0241 | 121.9373 | 0.33561 | -121.9701 | 0.047854 | 0.15104 | 0.20002 | 0.21553 | -122.0162
2015.4688 | 121.9437 | -0.15106 | 121.8842 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.064714 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.029203 | 0.016073 | 0.010204 | 0.19371 | -0.072505 | 121.9838 | 121.8868 | 121.8 | -0.058478 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.092584 | 0.099598 | 0.16127 | 0.078557 | -0.014027 | 0.002596 | -0.084142 | 0.051017 | -121.9736 | 0.175 | 0.094711 | 0.043694 | -121.8704 | -121.826 | 122.1348 | 122.0378 | 121.9511 | 0.34477 | -121.9426 | 0.061587 | 0.16477 | 0.20918 | 0.22468 | -121.9842
2017.2344 | 121.962 | -0.14648 | 121.8933 | 1.4211e-13 | -0.040247 | 0.0018589 | 0.064714 | -0.0090999 | 0.052683 | -0.0022892 | -0.0042257 | -0.0016987 | 0.020254 | 0.028775 | 0.015859 | 0.014783 | 0.19829 | -0.077084 | 121.9838 | 121.8913 | 121.8046 | -0.063057 | 0.023941 | 0.073618 | -0.056351 | -0.084896 | 0.013707 | 0.053537 | -0.1092 | 0.083427 | 0.090442 | 0.16127 | 0.0694 | -0.014027 | -0.001981 | -0.088719 | 0.037281 | -121.9782 | 0.17042 | 0.090133 | 0.052852 | -121.8796 | -121.8398 | 122.1302 | 122.0378 | 121.9511 | 0.34477 | -121.9564 | 0.061588 | 0.16019 | 0.20002 | 0.2201 | -122.0025
2019 | 121.994 | -0.12817 | 121.9116 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064714 | -0.0086727 | 0.05311 | -0.0099192 | -0.0040121 | -0.0014849 | 0.02004 | 0.028989 | 0.015859 | 0.010204 | 0.20286 | -0.063349 | 121.9792 | 121.8868 | 121.8092 | -0.067636 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.048958 | -0.10462 | 0.060538 | 0.067554 | 0.13838 | 0.064825 | 0.004287 | -0.02487 | -0.10245 | 0.02355 | -122.0011 | 0.15212 | 0.062665 | 0.039115 | -121.8979 | -121.8627 | 122.1073 | 122.0149 | 121.9373 | 0.33104 | -121.9793 | 0.038699 | 0.14188 | 0.17713 | 0.20179 | -122.0162
2020.7031 | 121.9711 | -0.14191 | 121.9345 | 1.4211e-13 | -0.040675 | 0.0014317 | 0.064928 | -0.0086727 | 0.052683 | -0.0099192 | -0.0040121 | -0.0016987 | 0.02004 | 0.028989 | 0.016073 | 0.005626 | 0.19829 | -0.072505 | 121.9792 | 121.8913 | 121.8046 | -0.063057 | 0.019362 | 0.06904 | -0.056351 | -0.080318 | 0.018285 | 0.048958 | -0.10462 | 0.07885 | 0.044666 | 0.14753 | 0.069402 | -0.009448 | -0.043179 | -0.12992 | 0.037283 | -122.0148 | 0.16127 | 0.085556 | 0.048273 | -121.9162 | -121.8856 | 122.1211 | 122.0332 | 121.9465 | 0.34019 | -121.9976 | 0.061589 | 0.16019 | 0.19087 | 0.21095 | -122.0391
2022.4531 | 121.9757 | -0.13275 | 121.8979 | 1.4211e-13 | -0.040461 | 0.0014317 | 0.0645 | -0.0086727 | 0.052683 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019827 | 0.028775 | 0.016073 | 0.005626 | 0.19829 | -0.067927 | 121.9883 | 121.8959 | 121.8 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.053537 | -0.10004 | 0.074273 | 0.090444 | 0.13838 | 0.064824 | -0.009449 | -0.001979 | -0.097875 | 0.032706 | -121.9782 | 0.15211 | 0.071821 | 0.039115 | -121.8842 | -121.8444 | 122.1211 | 122.0287 | 121.9328 | 0.33104 | -121.9564 | 0.052433 | 0.14646 | 0.18629 | 0.21095 | -121.9979
2024.2031 | 121.962 | -0.12817 | 121.8933 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.0645 | -0.0088863 | 0.052683 | -0.0022892 | -0.0040121 | -0.0012713 | 0.019827 | 0.029203 | 0.015859 | 0.010204 | 0.20286 | -0.077084 | 121.9883 | 121.8822 | 121.8046 | -0.063057 | 0.014784 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.10462 | 0.065117 | 0.095021 | 0.13838 | 0.05109 | -0.014027 | -0.011139 | -0.088719 | 0.02355 | -121.9782 | 0.14296 | 0.067244 | 0.043694 | -121.875 | -121.8398 | 122.1165 | 122.0103 | 121.9328 | 0.33104 | -121.9564 | 0.043278 | 0.14646 | 0.18171 | 0.20637 | -121.9979
2025.9219 | 121.9391 | -0.13733 | 121.9345 | 1.4211e-13 | -0.040461 | 0.0016453 | 0.064286 | -0.0086727 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.029203 | 0.015859 | 0.005626 | 0.20286 | -0.072505 | 121.9792 | 121.8868 | 121.7954 | -0.067636 | 0.02852 | 0.06904 | -0.06093 | -0.094053 | 0.009128 | 0.053537 | -0.10462 | 0.069693 | 0.044666 | 0.14295 | 0.064824 | -0.004869 | -0.047758 | -0.13907 | 0.032705 | -122.0286 | 0.16585 | 0.076399 | 0.043694 | -121.9254 | -121.881 | 122.1165 | 122.0241 | 121.9328 | 0.34019 | -122.0021 | 0.043276 | 0.14646 | 0.19087 | 0.20637 | -122.0391
2027.6875 | 122.0856 | -0.086975 | 121.8567 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.0645 | -0.0088863 | 0.052897 | -0.01755 | -0.0040121 | -0.0012713 | 0.020254 | 0.028989 | 0.016073 | -0.003531 | 0.19371 | -0.081662 | 121.97 | 121.8822 | 121.8046 | -0.067636 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.019339 | 0.11333 | 0.083444 | 0.005313 | -0.014026 | 0.025483 | -0.052097 | -0.022228 | -121.9416 | 0.11092 | 0.026045 | 0.048273 | -121.843 | -121.7986 | 122.057 | 121.9691 | 121.8916 | 0.28068 | -121.9243 | 0.002079 | 0.10068 | 0.14509 | 0.15602 | -121.9659
2029.4375 | 122.0673 | -0.11444 | 121.8658 | 1.4211e-13 | -0.040675 | 0.0018589 | 0.064714 | -0.0086727 | 0.05311 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019827 | 0.028989 | 0.016073 | -0.008109 | 0.18913 | -0.095397 | 121.97 | 121.8776 | 121.7909 | -0.072215 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.042226 | 0.10417 | 0.10633 | 0.019044 | -0.023182 | 0.011749 | -0.074989 | 0.009817 | -121.9507 | 0.13838 | 0.048932 | 0.039115 | -121.8521 | -121.8077 | 122.0845 | 121.992 | 121.9053 | 0.30357 | -121.9381 | 0.029545 | 0.12815 | 0.17256 | 0.19264 | -121.9705
2031.125 | 121.9757 | -0.14191 | 121.8704 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.0645 | -0.0088863 | 0.052683 | 0.0053413 | -0.0042257 | -0.0014849 | 0.019827 | 0.029203 | 0.016073 | -0.003531 | 0.20744 | -0.08624 | 121.9654 | 121.8776 | 121.7909 | -0.076794 | 0.019362 | 0.073618 | -0.056351 | -0.089475 | 0.018285 | 0.062694 | -0.10004 | 0.065113 | 0.095018 | 0.13838 | 0.055667 | -0.009446 | 0.007172 | -0.079566 | 0.041862 | -121.9599 | 0.16127 | 0.085556 | 0.043694 | -121.8521 | -121.8077 | 122.1073 | 122.0195 | 121.9328 | 0.34935 | -121.9472 | 0.052432 | 0.16019 | 0.2046 | 0.21553 | -121.9705
2032.8906 | 122.0581 | -0.10986 | 121.8979 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.064714 | -0.0084589 | 0.052469 | -0.0099192 | -0.0042257 | -0.0019123 | 0.02004 | 0.028775 | 0.015859 | -0.012688 | 0.21202 | -0.090818 | 121.9746 | 121.8868 | 121.7909 | -0.076794 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.009128 | 0.067272 | -0.10462 | 0.033069 | 0.076708 | 0.097175 | 0.019045 | -0.014024 | -0.011137 | -0.10703 | 0.005239 | -121.9828 | 0.1338 | 0.048933 | 0.043694 | -121.8888 | -121.8306 | 122.0845 | 121.9966 | 121.9007 | 0.32188 | -121.9747 | 0.024967 | 0.11899 | 0.17713 | 0.18806 | -122.0025
2034.6406 | 122.1085 | -0.086975 | 121.8613 | 1.4211e-13 | -0.040675 | 0.0018589 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.02004 | 0.028775 | 0.016073 | -0.012688 | 0.19371 | -0.090818 | 121.9609 | 121.873 | 121.7954 | -0.081373 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.005602 | 0.099594 | 0.074287 | -0.003843 | -0.009445 | 0.011748 | -0.065832 | -0.017649 | -121.9462 | 0.1155 | 0.026045 | 0.043694 | -121.8476 | -121.8032 | 122.0478 | 121.96 | 121.8824 | 0.28068 | -121.9426 | 0.002079 | 0.10068 | 0.14509 | 0.16517 | -121.9659
2036.4062 | 121.9666 | -0.14648 | 121.9025 | 1.4211e-13 | -0.040675 | 0.0018589 | 0.064714 | -0.0086727 | 0.052683 | -0.0022892 | -0.0037985 | -0.0014849 | 0.019827 | 0.028989 | 0.015859 | -0.012688 | 0.20286 | -0.090818 | 121.9746 | 121.8822 | 121.7954 | -0.076794 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.06969 | 0.07213 | 0.1338 | 0.055666 | -0.014024 | -0.020294 | -0.10703 | 0.04186 | -121.9874 | 0.175 | 0.085554 | 0.043694 | -121.8888 | -121.8444 | 122.1211 | 122.0287 | 121.9419 | 0.34935 | -121.9793 | 0.061588 | 0.16019 | 0.2046 | 0.21552 | -122.0071
2038.1094 | 121.9574 | -0.15564 | 121.9116 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.0645 | -0.0088863 | 0.052469 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.029203 | 0.015859 | -0.012688 | 0.20286 | -0.090818 | 121.97 | 121.8776 | 121.7909 | -0.076794 | 0.019362 | 0.073618 | -0.056351 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.078846 | 0.058397 | 0.14295 | 0.064822 | -0.014024 | -0.034027 | -0.12076 | 0.046437 | -122.0011 | 0.175 | 0.099289 | 0.052852 | -121.8933 | -121.8535 | 122.1257 | 122.0332 | 121.9465 | 0.3585 | -121.9884 | 0.066165 | 0.17392 | 0.21376 | 0.22926 | -122.0208
2039.8594 | 121.9986 | -0.13275 | 121.8933 | 1.4211e-13 | -0.040675 | 0.0018589 | 0.064286 | -0.0086727 | 0.052897 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019827 | 0.028989 | 0.016073 | -0.003531 | 0.20286 | -0.090818 | 121.97 | 121.8822 | 121.8 | -0.076794 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.055957 | 0.076707 | 0.12922 | 0.041933 | -0.014024 | -0.011139 | -0.093298 | 0.023548 | -121.9782 | 0.16127 | 0.071821 | 0.048273 | -121.8796 | -121.8352 | 122.1028 | 122.0149 | 121.9328 | 0.33562 | -121.9701 | 0.047855 | 0.14646 | 0.19087 | 0.20637 | -122.0025
2041.5625 | 122.0947 | -0.10529 | 121.8796 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.064286 | -0.0090999 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019827 | 0.029203 | 0.015859 | -0.008109 | 0.20744 | -0.08624 | 121.9746 | 121.8776 | 121.7863 | -0.081373 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.013707 | 0.058115 | -0.10004 | 0.023913 | 0.095018 | 0.097177 | 0.019046 | -0.004867 | -0.001984 | -0.0933 | 0.005241 | -121.9599 | 0.12923 | 0.048935 | 0.043694 | -121.8659 | -121.8215 | 122.0799 | 121.9829 | 121.8916 | 0.31273 | -121.961 | 0.024968 | 0.11899 | 0.1634 | 0.18348 | -121.9796
2043.3281 | 122.1085 | -0.091553 | 121.8292 | 1.4211e-13 | -0.041102 | 0.0020727 | 0.0645 | -0.0086727 | 0.052683 | -0.01755 | -0.0046531 | -0.0012713 | 0.02004 | 0.028775 | 0.015859 | -0.012688 | 0.20744 | -0.08624 | 121.97 | 121.8776 | 121.7909 | -0.081373 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.009128 | 0.058115 | -0.10004 | 0.01018 | 0.14079 | 0.078865 | 0.005313 | -0.004867 | 0.04837 | -0.038368 | -0.008492 | -121.9141 | 0.12007 | 0.030623 | 0.039115 | -121.8201 | -121.7711 | 122.0616 | 121.9691 | 121.8824 | 0.299 | -121.9106 | 0.006657 | 0.10068 | 0.14967 | 0.16975 | -121.9293
2045.0938 | 122.0764 | -0.10071 | 121.8796 | 1.4211e-13 | -0.040675 | 0.0016453 | 0.0645 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.029203 | 0.015859 | -0.008109 | 0.21202 | -0.081662 | 121.97 | 121.8776 | 121.7909 | -0.085952 | 0.023941 | 0.06904 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.10004 | 0.014756 | 0.09044 | 0.092599 | 0.019046 | 0.00429 | -0.001984 | -0.088722 | 0.000663 | -121.9691 | 0.12465 | 0.039778 | 0.039115 | -121.8613 | -121.8215 | 122.0707 | 121.9783 | 121.8916 | 0.31273 | -121.9655 | 0.011233 | 0.11899 | 0.15882 | 0.16975 | -121.9796
2046.7969 | 121.9437 | -0.1236 | 121.8979 | 1.4211e-13 | -0.040888 | 0.0014317 | 0.0645 | -0.0086727 | 0.052469 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.028989 | 0.016287 | -0.003531 | 0.21202 | -0.077084 | 121.9792 | 121.8868 | 121.8 | -0.081373 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.042223 | 0.081287 | 0.12006 | 0.046512 | 0.004289 | -0.011137 | -0.097875 | 0.023551 | -121.9874 | 0.14296 | 0.062666 | 0.039115 | -121.8842 | -121.8398 | 122.1028 | 122.0103 | 121.9236 | 0.33562 | -121.9793 | 0.034121 | 0.1373 | 0.18171 | 0.19721 | -121.9979
2048.5469 | 121.9391 | -0.16022 | 121.8796 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.0645 | -0.0088863 | 0.05311 | -0.0099192 | -0.0044395 | -0.0012713 | 0.02004 | 0.029203 | 0.016287 | -0.003531 | 0.20286 | -0.077084 | 121.9792 | 121.8822 | 121.8 | -0.085952 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.074265 | 0.099597 | 0.15669 | 0.083133 | 0.008868 | 0.002594 | -0.079565 | 0.055593 | -121.9645 | 0.18416 | 0.099287 | 0.043694 | -121.8659 | -121.8215 | 122.1394 | 122.0424 | 121.9602 | 0.36308 | -121.9655 | 0.075321 | 0.17392 | 0.21833 | 0.23841 | -121.9842
2050.2969 | 121.9666 | -0.13275 | 121.875 | 1.4211e-13 | -0.040461 | 0.0018589 | 0.064714 | -0.0086727 | 0.052683 | -0.0022892 | -0.0037985 | -0.0012713 | 0.019827 | 0.028989 | 0.016073 | -0.003531 | 0.21202 | -0.077084 | 121.9792 | 121.8868 | 121.8 | -0.081373 | 0.023941 | 0.082776 | -0.056351 | -0.089475 | 0.009128 | 0.058115 | -0.10004 | 0.051378 | 0.10417 | 0.12922 | 0.055667 | 0.004289 | 0.011751 | -0.074987 | 0.032706 | -121.9645 | 0.15669 | 0.0764 | 0.043694 | -121.8659 | -121.8169 | 122.1119 | 122.0195 | 121.9328 | 0.34477 | -121.9564 | 0.043276 | 0.14188 | 0.19087 | 0.21553 | -121.975
2052 | 122.0856 | -0.10529 | 121.8521 | 1.4211e-13 | -0.040675 | 0.0020727 | 0.0645 | -0.0086727 | 0.052897 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019827 | 0.029416 | 0.016287 | -0.008109 | 0.2166 | -0.081662 | 121.9883 | 121.8868 | 121.8 | -0.076794 | 0.02852 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.028492 | 0.13622 | 0.097177 | 0.023624 | -0.004868 | 0.034639 | -0.052099 | 0.000662 | -121.9416 | 0.13381 | 0.044356 | 0.043694 | -121.8384 | -121.794 | 122.0936 | 121.992 | 121.9053 | 0.32189 | -121.9289 | 0.015811 | 0.11899 | 0.1634 | 0.1789 | -121.9567
2053.75 | 122.0764 | -0.13733 | 121.8796 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.0645 | -0.0086727 | 0.052897 | 0.0053413 | -0.0040121 | -0.0014849 | 0.02004 | 0.029203 | 0.015859 | -0.012688 | 0.21202 | -0.08624 | 121.9792 | 121.8868 | 121.8046 | -0.081373 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.009128 | 0.062694 | -0.095467 | 0.055956 | 0.099597 | 0.12464 | 0.051089 | -0.004867 | 0.007173 | -0.074986 | 0.041862 | -121.9691 | 0.16127 | 0.07182 | 0.029958 | -121.8704 | -121.8169 | 122.1165 | 122.0241 | 121.9419 | 0.34935 | -121.961 | 0.047854 | 0.14646 | 0.20002 | 0.21095 | -121.975
2055.5 | 122.0856 | -0.10529 | 121.8842 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0086727 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019827 | 0.028989 | 0.015859 | -0.003531 | 0.20744 | -0.08624 | 121.9792 | 121.8868 | 121.8 | -0.072215 | 0.019362 | 0.06904 | -0.065509 | -0.089475 | 0.013707 | 0.067272 | -0.10004 | 0.033071 | 0.09502 | 0.10175 | 0.019046 | -0.014025 | 0.002596 | -0.084142 | 0.005241 | -121.9736 | 0.12465 | 0.039777 | 0.034536 | -121.8704 | -121.8169 | 122.0845 | 121.992 | 121.9053 | 0.31273 | -121.9564 | 0.015811 | 0.11899 | 0.17256 | 0.17433 | -121.9842
2057.2812 | 122.0627 | -0.11444 | 121.8704 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028989 | 0.015859 | -0.012688 | 0.20744 | -0.081662 | 121.9792 | 121.8913 | 121.8 | -0.072215 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.1092 | 0.042226 | 0.10875 | 0.10175 | 0.032779 | -0.009447 | 0.020908 | -0.070409 | 0.005238 | -121.9507 | 0.13838 | 0.053511 | 0.048273 | -121.8521 | -121.8123 | 122.0936 | 122.0058 | 121.9145 | 0.32188 | -121.9426 | 0.034123 | 0.13273 | 0.17256 | 0.18806 | -121.9796
2059.0469 | 122.0352 | -0.11444 | 121.8613 | 1.4211e-13 | -0.040675 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.029203 | 0.015859 | -0.003531 | 0.21202 | -0.081662 | 121.9746 | 121.8822 | 121.8092 | -0.067636 | 0.019362 | 0.06904 | -0.056351 | -0.084896 | 0.013707 | 0.062694 | -0.10004 | 0.046805 | 0.11333 | 0.11091 | 0.032779 | -0.014026 | 0.020905 | -0.052096 | 0.014396 | -121.9462 | 0.1338 | 0.05809 | 0.043694 | -121.8476 | -121.7986 | 122.089 | 121.9966 | 121.9236 | 0.32646 | -121.9289 | 0.029545 | 0.12815 | 0.17713 | 0.18348 | -121.9613
2060.8125 | 122.0535 | -0.09613 | 121.8796 | 1.4211e-13 | -0.040675 | 0.0018589 | 0.064714 | -0.0088863 | 0.052256 | -0.01755 | -0.0040121 | -0.0014849 | 0.019827 | 0.029416 | 0.015646 | -0.003531 | 0.21202 | -0.08624 | 121.9883 | 121.8913 | 121.8092 | -0.072215 | 0.019362 | 0.073618 | -0.074666 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.023915 | 0.10875 | 0.092599 | 0.00989 | -0.014025 | 0.011752 | -0.070407 | -0.008494 | -121.9691 | 0.11549 | 0.021464 | 0.029958 | -121.8659 | -121.8215 | 122.0845 | 121.9875 | 121.9053 | 0.30815 | -121.9518 | 0.006655 | 0.10984 | 0.15424 | 0.16975 | -121.9842
2062.5156 | 122.0352 | -0.1236 | 121.8658 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.028989 | 0.016287 | 0.001048 | 0.21202 | -0.081662 | 121.9746 | 121.8913 | 121.8 | -0.072215 | 0.019362 | 0.078197 | -0.056351 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.051381 | 0.10875 | 0.12464 | 0.041934 | -0.009447 | 0.025485 | -0.065832 | 0.018972 | -121.9507 | 0.14296 | 0.067245 | 0.048273 | -121.8521 | -121.8077 | 122.0982 | 122.0149 | 121.9236 | 0.33562 | -121.9381 | 0.0387 | 0.1373 | 0.18171 | 0.20179 | -121.9705
2064.2812 | 122.0901 | -0.10986 | 121.8567 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.064286 | -0.0086727 | 0.052683 | -0.0099192 | -0.0040121 | -0.0014849 | 0.020254 | 0.029203 | 0.015859 | -0.008109 | 0.21202 | -0.077084 | 121.9838 | 121.8959 | 121.8 | -0.067636 | 0.019362 | 0.073618 | -0.056351 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.042227 | 0.12706 | 0.10175 | 0.032779 | -0.009448 | 0.03922 | -0.056676 | 0.009818 | -121.9416 | 0.12923 | 0.053512 | 0.043694 | -121.843 | -121.7986 | 122.0936 | 122.0058 | 121.9099 | 0.32188 | -121.9243 | 0.024967 | 0.12357 | 0.16798 | 0.18348 | -121.9567
2066.0469 | 122.0078 | -0.1236 | 121.8796 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.0645 | -0.0086727 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.02004 | 0.028775 | 0.016073 | 0.001048 | 0.21202 | -0.081662 | 121.9975 | 121.8913 | 121.8046 | -0.072215 | 0.02852 | 0.078197 | -0.06093 | -0.094053 | 0.018285 | 0.062694 | -0.1092 | 0.051381 | 0.11791 | 0.12464 | 0.041934 | -0.009447 | 0.011752 | -0.074986 | 0.014393 | -121.9736 | 0.15212 | 0.062666 | 0.048273 | -121.8613 | -121.8169 | 122.1211 | 122.0149 | 121.9282 | 0.33562 | -121.9518 | 0.029543 | 0.14188 | 0.18629 | 0.20179 | -121.9888
2067.75 | 121.962 | -0.15106 | 121.907 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064286 | -0.0086727 | 0.052683 | -0.0099192 | -0.0040121 | -0.0014849 | 0.02004 | 0.028989 | 0.015859 | 0.001048 | 0.2166 | -0.077084 | 121.9838 | 121.8959 | 121.8092 | -0.076794 | 0.023941 | 0.082776 | -0.056351 | -0.094053 | 0.018285 | 0.058115 | -0.10004 | 0.074268 | 0.07671 | 0.15211 | 0.073978 | -0.00029 | -0.011134 | -0.097872 | 0.051017 | -122.0011 | 0.175 | 0.094711 | 0.043694 | -121.8888 | -121.8489 | 122.1348 | 122.047 | 121.9602 | 0.36766 | -121.9838 | 0.057009 | 0.16935 | 0.20918 | 0.23384 | -122.0071
2069.5156 | 121.994 | -0.1236 | 121.907 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.064286 | -0.0088863 | 0.052683 | -0.0022892 | -0.0042257 | -0.0016987 | 0.02004 | 0.029203 | 0.016073 | -0.008109 | 0.21202 | -0.081662 | 121.9883 | 121.8959 | 121.8046 | -0.063057 | 0.023941 | 0.064461 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.095467 | 0.060539 | 0.081289 | 0.11549 | 0.041934 | -0.018605 | -0.011134 | -0.10245 | 0.028129 | -121.9874 | 0.14754 | 0.058087 | 0.029958 | -121.8933 | -121.8489 | 122.1119 | 122.0195 | 121.9282 | 0.33562 | -121.9701 | 0.043278 | 0.1373 | 0.18171 | 0.18806 | -122.0025
2071.2188 | 122.0627 | -0.10529 | 121.8887 | 1.4211e-13 | -0.041102 | 0.0014317 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019827 | 0.028989 | 0.015859 | -0.003531 | 0.20744 | -0.077084 | 121.9883 | 121.8913 | 121.8137 | -0.063057 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.042229 | 0.099599 | 0.10175 | 0.028202 | -0.014027 | 0.002597 | -0.074984 | 0.000662 | -121.9736 | 0.12465 | 0.044356 | 0.043694 | -121.875 | -121.8306 | 122.0936 | 121.9966 | 121.919 | 0.31273 | -121.9518 | 0.02039 | 0.11899 | 0.1634 | 0.18348 | -121.9934
2072.9844 | 122.0352 | -0.10071 | 121.8933 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.064928 | -0.0088863 | 0.052683 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019827 | 0.028989 | 0.016073 | -0.008109 | 0.2166 | -0.077084 | 121.9883 | 121.8913 | 121.8137 | -0.063057 | 0.014784 | 0.073618 | -0.065509 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.037651 | 0.095021 | 0.092599 | 0.023624 | -0.014027 | -0.001981 | -0.079562 | -0.003916 | -121.9736 | 0.11549 | 0.035199 | 0.039115 | -121.875 | -121.8352 | 122.089 | 121.992 | 121.9145 | 0.31731 | -121.9564 | 0.02039 | 0.11899 | 0.15882 | 0.17433 | -121.9979
2074.7344 | 122.0581 | -0.10986 | 121.8796 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.0645 | -0.0086727 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.029416 | 0.015859 | 0.001048 | 0.2166 | -0.081662 | 121.9883 | 121.9005 | 121.8092 | -0.072215 | 0.019362 | 0.078197 | -0.056351 | -0.084896 | 0.009128 | 0.058115 | -0.10462 | 0.037648 | 0.10875 | 0.11091 | 0.028201 | -0.009447 | 0.02091 | -0.070407 | 0.005239 | -121.9645 | 0.12923 | 0.053512 | 0.048273 | -121.8704 | -121.8215 | 122.0982 | 122.0104 | 121.919 | 0.32646 | -121.9518 | 0.024967 | 0.11899 | 0.16798 | 0.18806 | -121.9842
2076.4375 | 122.0032 | -0.13275 | 121.907 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0093137 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.02004 | 0.029203 | 0.015859 | -0.003531 | 0.21202 | -0.077084 | 121.9883 | 121.9005 | 121.8137 | -0.063057 | 0.02852 | 0.082776 | -0.051772 | -0.084896 | 0.009128 | 0.048958 | -0.1092 | 0.069694 | 0.081289 | 0.12922 | 0.055667 | -0.014027 | -0.006555 | -0.093294 | 0.023548 | -121.9919 | 0.16127 | 0.080979 | 0.057431 | -121.8979 | -121.8581 | 122.1211 | 122.0332 | 121.9465 | 0.34477 | -121.9701 | 0.047855 | 0.14188 | 0.18171 | 0.21553 | -122.0162
2078.2031 | 122.0856 | -0.068665 | 121.843 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064714 | -0.0088863 | 0.05311 | -0.01755 | -0.0044395 | -0.0014849 | 0.019827 | 0.029203 | 0.015646 | 0.005626 | 0.2166 | -0.072505 | 121.9929 | 121.9051 | 121.8137 | -0.072215 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.013707 | 0.048958 | -0.10462 | -0.00355 | 0.14995 | 0.074291 | -0.00384 | -0.00029 | 0.06211 | -0.029208 | -0.035959 | -121.9233 | 0.092606 | 0.003156 | 0.039115 | -121.8293 | -121.794 | 122.0616 | 121.9737 | 121.8824 | 0.28527 | -121.9152 | -0.011653 | 0.082372 | 0.11762 | 0.15144 | -121.9476
2079.9531 | 122.0352 | -0.09613 | 121.8842 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064714 | -0.0084589 | 0.052683 | -0.01755 | -0.0042257 | -0.0014849 | 0.02004 | 0.029203 | 0.015859 | 0.001048 | 0.2166 | -0.067927 | 121.9975 | 121.8959 | 121.8137 | -0.063057 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.013707 | 0.053537 | -0.1092 | 0.033073 | 0.11333 | 0.097178 | 0.028203 | -0.00487 | 0.011754 | -0.070406 | -0.013073 | -121.9736 | 0.12007 | 0.039779 | 0.052852 | -121.8704 | -121.8306 | 122.0936 | 121.992 | 121.9099 | 0.31273 | -121.9472 | 0.006655 | 0.10984 | 0.14967 | 0.16975 | -121.9934
2081.7031 | 122.0398 | -0.10529 | 121.8933 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.064928 | -0.0088863 | 0.052897 | -0.01755 | -0.0040121 | -0.0014849 | 0.019399 | 0.029203 | 0.015859 | 0.001048 | 0.22118 | -0.067927 | 121.9929 | 121.9005 | 121.8229 | -0.067636 | 0.014784 | 0.073618 | -0.06093 | -0.084896 | 0.009128 | 0.062694 | -0.10462 | 0.03765 | 0.099599 | 0.10633 | 0.037359 | -0.000291 | 0.007177 | -0.070405 | 0.000662 | -121.9782 | 0.12007 | 0.044356 | 0.043694 | -121.8842 | -121.8306 | 122.0982 | 122.0058 | 121.9282 | 0.32647 | -121.9609 | 0.02039 | 0.11441 | 0.16798 | 0.1789 | -121.9979
2083.4062 | 121.9482 | -0.12817 | 121.9208 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064286 | -0.0086727 | 0.052897 | 0.0053413 | -0.0042257 | -0.0012713 | 0.019827 | 0.029416 | 0.016073 | 0.005626 | 0.23034 | -0.072505 | 121.9883 | 121.9096 | 121.8137 | -0.067636 | 0.02852 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.067272 | -0.10462 | 0.060538 | 0.067556 | 0.1338 | 0.055669 | -0.004869 | -0.01113 | -0.10703 | 0.02355 | -122.0103 | 0.15669 | 0.067244 | 0.043694 | -121.9071 | -121.8535 | 122.1165 | 122.0378 | 121.9419 | 0.35851 | -121.9884 | 0.038699 | 0.14188 | 0.19545 | 0.20179 | -122.0254
2085.1719 | 121.9574 | -0.1236 | 121.9254 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019827 | 0.028989 | 0.016073 | 0.005626 | 0.21202 | -0.077084 | 121.9929 | 121.9005 | 121.8229 | -0.063057 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.009128 | 0.058115 | -0.1092 | 0.060539 | 0.067556 | 0.12922 | 0.046512 | -0.014027 | -0.024866 | -0.10245 | 0.014393 | -122.0148 | 0.14754 | 0.062666 | 0.048273 | -121.9162 | -121.8672 | 122.1165 | 122.0241 | 121.9465 | 0.33562 | -121.9884 | 0.034121 | 0.13272 | 0.18171 | 0.20179 | -122.0346
2086.9375 | 122.0352 | -0.10986 | 121.9208 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0090999 | 0.052683 | -0.01755 | -0.0044395 | -0.0016987 | 0.020254 | 0.029203 | 0.015859 | 0.005626 | 0.2166 | -0.077084 | 121.9929 | 121.8913 | 121.8183 | -0.063057 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.004549 | 0.058115 | -0.10004 | 0.046806 | 0.072134 | 0.11549 | 0.032779 | -0.014027 | -0.029446 | -0.10245 | 0.009818 | -122.0057 | 0.1338 | 0.053512 | 0.043694 | -121.9162 | -121.8627 | 122.1028 | 122.0012 | 121.9282 | 0.32646 | -121.9838 | 0.024967 | 0.11441 | 0.16798 | 0.18806 | -122.0208
2088.7031 | 122.049 | -0.082397 | 121.907 | 1.4211e-13 | -0.040888 | 0.0014317 | 0.064714 | -0.0088863 | 0.052469 | -0.0022892 | -0.0042257 | -0.0012713 | 0.02004 | 0.028989 | 0.015859 | 0.005626 | 0.22118 | -0.072505 | 121.9929 | 121.9051 | 121.8275 | -0.067636 | 0.02852 | 0.06904 | -0.06093 | -0.094053 | 0.022864 | 0.067272 | -0.1092 | 0.014761 | 0.085867 | 0.088023 | 0.009892 | -0.004869 | -0.001976 | -0.079558 | -0.026806 | -122.0011 | 0.11092 | 0.021467 | 0.048273 | -121.8842 | -121.8398 | 122.0753 | 121.9875 | 121.9099 | 0.30358 | -121.9747 | -0.011656 | 0.10526 | 0.14967 | 0.15144 | -122.0162
2090.3906 | 122.0078 | -0.12817 | 121.9025 | 1.4211e-13 | -0.041316 | 0.0018589 | 0.0645 | -0.0093137 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.028989 | 0.015859 | 0.005626 | 0.22576 | -0.067927 | 121.9975 | 121.9051 | 121.8229 | -0.067636 | 0.02852 | 0.087354 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.060538 | 0.095022 | 0.1338 | 0.060247 | -0.000291 | 0.002601 | -0.07956 | 0.018971 | -121.9874 | 0.15669 | 0.067244 | 0.048273 | -121.8888 | -121.8444 | 122.1257 | 122.0332 | 121.9511 | 0.35393 | -121.9701 | 0.043278 | 0.14188 | 0.18629 | 0.21553 | -122.0117
2092.1406 | 122.1039 | -0.086975 | 121.8979 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.064286 | -0.0086727 | 0.052469 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019827 | 0.028989 | 0.015646 | 0.001048 | 0.22118 | -0.072505 | 121.9975 | 121.9051 | 121.8229 | -0.072215 | 0.02852 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.062694 | -0.10004 | 0.01476 | 0.0996 | 0.088023 | 0.01447 | -0.00029 | 0.007179 | -0.074982 | -0.01307 | -121.9782 | 0.1155 | 0.021466 | 0.034536 | -121.8842 | -121.8352 | 122.0845 | 121.992 | 121.9099 | 0.30815 | -121.9701 | 0.006657 | 0.10068 | 0.14967 | 0.16059 | -121.9979
2093.9062 | 121.9849 | -0.1236 | 121.907 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.0645 | -0.0090999 | 0.052683 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028989 | 0.016287 | -0.003531 | 0.22118 | -0.077084 | 122.0021 | 121.9096 | 121.8183 | -0.063057 | 0.033099 | 0.073618 | -0.065509 | -0.094053 | 0.009128 | 0.062694 | -0.10462 | 0.060539 | 0.095024 | 0.12006 | 0.046512 | -0.014027 | 0.002603 | -0.088715 | 0.018972 | -122.0011 | 0.1567 | 0.058087 | 0.039115 | -121.8979 | -121.8443 | 122.1257 | 122.0332 | 121.9419 | 0.34477 | -121.9701 | 0.029543 | 0.13272 | 0.18629 | 0.19721 | -122.0117
2095.6719 | 122.0764 | -0.09613 | 121.8979 | 1.4211e-13 | -0.040888 | 0.0014317 | 0.0645 | -0.0086727 | 0.052683 | -0.01755 | -0.0040121 | -0.0010577 | 0.019613 | 0.029416 | 0.016073 | 0.014783 | 0.23034 | -0.072505 | 121.9975 | 121.9096 | 121.8229 | -0.063057 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.10004 | 0.033073 | 0.0996 | 0.11091 | 0.023625 | -0.009448 | 0.011758 | -0.074982 | -0.003915 | -121.9782 | 0.12007 | 0.0352 | 0.039115 | -121.8796 | -121.8352 | 122.0936 | 122.0058 | 121.919 | 0.32647 | -121.9609 | 0.015812 | 0.11441 | 0.15882 | 0.16517 | -121.9979
2097.3594 | 121.994 | -0.11902 | 121.9025 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064714 | -0.0088863 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.028989 | 0.015859 | 0.001048 | 0.23034 | -0.072505 | 121.9975 | 121.9142 | 121.8229 | -0.063057 | 0.014784 | 0.06904 | -0.06093 | -0.089475 | 0.009128 | 0.062694 | -0.10462 | 0.055962 | 0.095022 | 0.12007 | 0.046514 | -0.009448 | 0.011759 | -0.07956 | 0.014395 | -121.9919 | 0.1338 | 0.058089 | 0.043694 | -121.8933 | -121.8398 | 122.1165 | 122.0332 | 121.9419 | 0.34936 | -121.9655 | 0.029544 | 0.12815 | 0.18171 | 0.18806 | -122.0071
2099.125 | 122.0535 | -0.10529 | 121.9025 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.064714 | -0.0086727 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029203 | 0.015646 | 0.014783 | 0.22118 | -0.072505 | 121.9975 | 121.9051 | 121.8183 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.10004 | 0.051387 | 0.095022 | 0.12007 | 0.032781 | -0.018606 | 0.002601 | -0.084138 | 0.005241 | -121.9919 | 0.12923 | 0.039777 | 0.034536 | -121.8888 | -121.8444 | 122.1028 | 122.0104 | 121.9236 | 0.32647 | -121.9564 | 0.015811 | 0.11899 | 0.1634 | 0.1789 | -122.0025
2100.875 | 122.0901 | -0.07782 | 121.9025 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064714 | -0.0093137 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.02963 | 0.016073 | 0.014783 | 0.22576 | -0.067927 | 122.0021 | 121.9051 | 121.8229 | -0.072215 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.095467 | 0.005605 | 0.099601 | 0.092603 | 0.009893 | 0.004288 | 0.002601 | -0.07956 | -0.017647 | -121.9919 | 0.097182 | 0.01689 | 0.034537 | -121.8888 | -121.8444 | 122.0799 | 121.9829 | 121.9007 | 0.30358 | -121.9747 | -0.011655 | 0.091527 | 0.13594 | 0.15144 | -121.9979
2102.5781 | 122.0398 | -0.11444 | 121.8979 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.064714 | -0.0090999 | 0.052683 | -0.02518 | -0.0044395 | -0.0014849 | 0.019827 | 0.029416 | 0.016073 | 0.005626 | 0.22576 | -0.072505 | 122.0021 | 121.9096 | 121.8229 | -0.067636 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.10004 | 0.046805 | 0.10418 | 0.12007 | 0.041936 | -0.004869 | 0.011758 | -0.074982 | 0.014396 | -121.9874 | 0.13838 | 0.053511 | 0.039115 | -121.8796 | -121.8398 | 122.1165 | 122.0241 | 121.9373 | 0.3402 | -121.9655 | 0.024966 | 0.13273 | 0.17256 | 0.19264 | -121.9979
2104.3594 | 122.0901 | -0.082397 | 121.8933 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0093137 | 0.052897 | -0.0099192 | -0.0048667 | -0.0012713 | 0.02004 | 0.028989 | 0.016073 | 0.010204 | 0.22576 | -0.067927 | 122.0021 | 121.9142 | 121.8183 | -0.067636 | 0.033099 | 0.073618 | -0.065509 | -0.094053 | 0.013707 | 0.058115 | -0.10462 | 0.014761 | 0.10876 | 0.092601 | 0.01447 | -0.000291 | 0.020914 | -0.074983 | -0.022227 | -121.9874 | 0.1155 | 0.016888 | 0.039115 | -121.8796 | -121.8352 | 122.0845 | 121.9966 | 121.9007 | 0.30815 | -121.9609 | -0.011656 | 0.096104 | 0.14051 | 0.15602 | -121.9979
2106.0625 | 122.081 | -0.10071 | 121.907 | 1.4211e-13 | -0.040888 | 0.0014317 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.029203 | 0.015859 | 0.001048 | 0.22118 | -0.067927 | 122.0021 | 121.9142 | 121.8275 | -0.067636 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.067272 | -0.10462 | 0.033072 | 0.095024 | 0.10176 | 0.032781 | -0.000291 | 0.007182 | -0.079558 | -0.003916 | -121.9919 | 0.12465 | 0.039778 | 0.043694 | -121.8933 | -121.8398 | 122.1028 | 122.0149 | 121.9282 | 0.32189 | -121.9747 | 0.015812 | 0.11442 | 0.16798 | 0.17891 | -122.0117
2107.8125 | 122.0169 | -0.1236 | 121.9345 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.064286 | -0.0088863 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019827 | 0.029203 | 0.015646 | 0.010204 | 0.23034 | -0.067927 | 122.0021 | 121.9142 | 121.8366 | -0.063057 | 0.02852 | 0.073618 | -0.06093 | -0.075739 | 0.022864 | 0.058115 | -0.10462 | 0.060539 | 0.067558 | 0.1338 | 0.055669 | -0.00487 | -0.020284 | -0.097867 | 0.018972 | -122.0102 | 0.15212 | 0.062666 | 0.043694 | -121.9116 | -121.8764 | 122.1257 | 122.0378 | 121.9602 | 0.35393 | -121.9976 | 0.047857 | 0.14646 | 0.18171 | 0.19721 | -122.0391
2109.5 | 121.9894 | -0.12817 | 121.9437 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0090999 | 0.052897 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019827 | 0.029416 | 0.016073 | 0.014783 | 0.23034 | -0.063349 | 122.0066 | 121.9142 | 121.8366 | -0.063057 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.065117 | 0.06298 | 0.14296 | 0.064825 | -0.000292 | -0.02944 | -0.10702 | 0.018971 | -122.0331 | 0.15212 | 0.067244 | 0.048273 | -121.9254 | -121.8855 | 122.1348 | 122.0424 | 121.9648 | 0.35851 | -122.0067 | 0.038699 | 0.14646 | 0.18629 | 0.20179 | -122.0529
2111.25 | 122.0901 | -0.082397 | 121.8933 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.064928 | -0.0088863 | 0.052683 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019827 | 0.028989 | 0.016073 | 0.010204 | 0.22576 | -0.063349 | 122.0112 | 121.9188 | 121.8229 | -0.058478 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.053537 | -0.10462 | 0.023919 | 0.11791 | 0.092601 | 0.019048 | -0.004871 | 0.025493 | -0.070405 | -0.022227 | -121.9736 | 0.10176 | 0.021467 | 0.043694 | -121.875 | -121.8398 | 122.0936 | 122.0012 | 121.9053 | 0.30815 | -121.9518 | 0.002079 | 0.10068 | 0.13593 | 0.15602 | -121.9979
2113 | 121.9986 | -0.1236 | 121.9116 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0090999 | 0.052683 | -0.02518 | -0.0042257 | -0.0012713 | 0.02004 | 0.02963 | 0.015859 | 0.010204 | 0.22118 | -0.063349 | 122.0066 | 121.9142 | 121.8366 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.1092 | 0.065118 | 0.095024 | 0.1338 | 0.060247 | -0.004871 | 0.002604 | -0.074979 | 0.014393 | -122.0011 | 0.14754 | 0.062666 | 0.048273 | -121.8933 | -121.8489 | 122.1302 | 122.0378 | 121.9602 | 0.34477 | -121.9701 | 0.034121 | 0.14188 | 0.18629 | 0.19721 | -122.0208
2114.6875 | 122.0444 | -0.091553 | 121.8842 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064286 | -0.0088863 | 0.05311 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019827 | 0.028989 | 0.015859 | 0.010204 | 0.22576 | -0.072505 | 122.0066 | 121.928 | 121.8366 | -0.063057 | 0.02852 | 0.073618 | -0.065509 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.028496 | 0.12249 | 0.10176 | 0.019048 | -0.009448 | 0.043807 | -0.047513 | -0.01765 | -121.9645 | 0.12007 | 0.026044 | 0.043694 | -121.8613 | -121.826 | 122.0982 | 122.0195 | 121.9282 | 0.31731 | -121.9472 | 0.011235 | 0.11442 | 0.14967 | 0.16517 | -121.9934
2116.4375 | 122.0078 | -0.11444 | 121.9162 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.064714 | -0.0090999 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.029416 | 0.016073 | 0.014783 | 0.23034 | -0.063349 | 122.0066 | 121.9188 | 121.8321 | -0.053899 | 0.02852 | 0.078197 | -0.056351 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.060542 | 0.090446 | 0.12922 | 0.051092 | -0.00945 | 0.002605 | -0.084135 | 0.009817 | -122.0057 | 0.14296 | 0.05809 | 0.048273 | -121.9025 | -121.8581 | 122.1211 | 122.0332 | 121.9465 | 0.34478 | -121.9701 | 0.024966 | 0.12815 | 0.17256 | 0.19264 | -122.0208
2118.2031 | 122.0261 | -0.09613 | 121.9254 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064286 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.02004 | 0.029203 | 0.015859 | 0.014783 | 0.22576 | -0.072505 | 122.0066 | 121.9142 | 121.8458 | -0.058478 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.009128 | 0.058115 | -0.10462 | 0.037652 | 0.081291 | 0.11091 | 0.023625 | -0.014027 | -0.011129 | -0.079554 | -0.008494 | -122.0057 | 0.12007 | 0.039779 | 0.048273 | -121.9162 | -121.8672 | 122.1028 | 122.0104 | 121.9419 | 0.32189 | -121.9838 | 0.015812 | 0.10526 | 0.15424 | 0.16975 | -122.03
2119.9531 | 122.0123 | -0.1236 | 121.9437 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064714 | -0.0088863 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.029203 | 0.016073 | 0.010204 | 0.23492 | -0.063349 | 122.0112 | 121.9234 | 121.8321 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.074275 | 0.067559 | 0.1338 | 0.060247 | -0.014028 | -0.020282 | -0.1116 | 0.018972 | -122.0286 | 0.14754 | 0.058087 | 0.039115 | -121.9254 | -121.881 | 122.1348 | 122.047 | 121.9557 | 0.35851 | -121.993 | 0.0387 | 0.14188 | 0.18629 | 0.20179 | -122.0483
2121.7031 | 121.9894 | -0.13275 | 121.9162 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0090999 | 0.05311 | -0.0022892 | -0.0042257 | -0.0014849 | 0.02004 | 0.029203 | 0.016073 | 0.014783 | 0.23034 | -0.063349 | 122.0066 | 121.9188 | 121.8412 | -0.058478 | 0.019362 | 0.073618 | -0.056351 | -0.089475 | 0.013707 | 0.062694 | -0.10004 | 0.074273 | 0.090446 | 0.14753 | 0.069402 | -0.004871 | 0.002605 | -0.074978 | 0.032706 | -122.0057 | 0.15211 | 0.0764 | 0.043694 | -121.9025 | -121.8535 | 122.1394 | 122.0516 | 121.974 | 0.36309 | -121.9747 | 0.043276 | 0.14646 | 0.19545 | 0.20637 | -122.0162
2123.4062 | 122.0535 | -0.086975 | 121.9116 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064714 | -0.0088863 | 0.053324 | 0.0053413 | -0.0042257 | -0.0012713 | 0.019613 | 0.028989 | 0.015859 | 0.014783 | 0.23492 | -0.063349 | 122.0158 | 121.9234 | 121.8458 | -0.053899 | 0.014784 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.10462 | 0.033076 | 0.10418 | 0.10176 | 0.023626 | -0.00945 | 0.011762 | -0.065821 | -0.017649 | -121.9919 | 0.10176 | 0.026045 | 0.043694 | -121.8888 | -121.8535 | 122.1028 | 122.0104 | 121.9328 | 0.32189 | -121.9655 | 0.006657 | 0.10984 | 0.14509 | 0.16975 | -122.0162
2125.1562 | 122.0901 | -0.082397 | 121.9025 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.064714 | -0.0088863 | 0.052683 | -0.0099192 | -0.0044395 | -0.0010577 | 0.019827 | 0.029416 | 0.015646 | 0.014783 | 0.23034 | -0.063349 | 122.0158 | 121.9234 | 121.8412 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.10004 | 0.028498 | 0.11334 | 0.09718 | 0.019048 | -0.00945 | 0.020917 | -0.061245 | -0.017648 | -121.9874 | 0.10176 | 0.021467 | 0.039115 | -121.8796 | -121.8398 | 122.0982 | 122.0058 | 121.9236 | 0.31273 | -121.9564 | -0.002499 | 0.10526 | 0.14509 | 0.15602 | -122.0025
2126.9062 | 121.9803 | -0.13733 | 121.9391 | 1.4211e-13 | -0.040888 | 0.0018589 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.028989 | 0.015646 | 0.019361 | 0.23492 | -0.067927 | 122.0158 | 121.9234 | 121.8504 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.009128 | 0.058115 | -0.10462 | 0.08343 | 0.076715 | 0.15669 | 0.069402 | -0.014028 | -0.015704 | -0.088709 | 0.032705 | -122.0194 | 0.16127 | 0.080978 | 0.048273 | -121.93 | -121.881 | 122.1531 | 122.0607 | 121.9877 | 0.37224 | -121.993 | 0.057011 | 0.14646 | 0.19544 | 0.21553 | -122.0437
2128.6719 | 122.0078 | -0.12817 | 121.9391 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064928 | -0.0090999 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019613 | 0.028989 | 0.016073 | 0.010204 | 0.23492 | -0.05877 | 122.025 | 121.9234 | 121.8366 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.013707 | 0.053537 | -0.10462 | 0.069696 | 0.085872 | 0.13838 | 0.069404 | -0.000292 | -0.015704 | -0.10245 | 0.02355 | -122.0286 | 0.15212 | 0.067244 | 0.043694 | -121.9254 | -121.8855 | 122.1531 | 122.0516 | 121.9648 | 0.36309 | -121.9976 | 0.038699 | 0.14188 | 0.18171 | 0.20637 | -122.0437
2130.4375 | 121.9666 | -0.1236 | 121.9666 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.0645 | -0.0090999 | 0.052683 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019827 | 0.028989 | 0.015646 | 0.014783 | 0.23949 | -0.063349 | 122.0112 | 121.9234 | 121.8412 | -0.063057 | 0.023941 | 0.064461 | -0.06093 | -0.089475 | 0.013707 | 0.067272 | -0.10004 | 0.060539 | 0.044671 | 0.13838 | 0.060247 | -0.000292 | -0.04317 | -0.12533 | 0.023551 | -122.056 | 0.14754 | 0.062666 | 0.039115 | -121.9528 | -121.8993 | 122.1348 | 122.047 | 121.9648 | 0.36309 | -122.0296 | 0.034121 | 0.1373 | 0.19087 | 0.18806 | -122.0666
2132.1875 | 122.0627 | -0.086975 | 121.9254 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.0645 | -0.0088863 | 0.052683 | -0.01755 | -0.0042257 | -0.0014849 | 0.019827 | 0.029203 | 0.016287 | 0.019361 | 0.23034 | -0.067927 | 122.0112 | 121.9234 | 121.8412 | -0.053899 | 0.037677 | 0.078197 | -0.056351 | -0.089475 | 0.022864 | 0.062694 | -0.095467 | 0.033076 | 0.08587 | 0.10634 | 0.019048 | -0.014028 | -0.001971 | -0.084133 | -0.008492 | -122.0148 | 0.12465 | 0.030624 | 0.039116 | -121.9025 | -121.8627 | 122.0982 | 122.0104 | 121.9282 | 0.31731 | -121.9793 | -0.0025 | 0.10984 | 0.14967 | 0.16517 | -122.0208
2133.9062 | 122.0627 | -0.091553 | 121.9208 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.064714 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019613 | 0.029416 | 0.016073 | 0.010204 | 0.23492 | -0.067927 | 122.0158 | 121.928 | 121.8458 | -0.053899 | 0.02852 | 0.073618 | -0.056351 | -0.084896 | 0.022864 | 0.058115 | -0.10462 | 0.037654 | 0.095026 | 0.10176 | 0.023626 | -0.014028 | 0.007186 | -0.074976 | -0.013071 | -122.0057 | 0.12007 | 0.035202 | 0.048273 | -121.8979 | -121.8627 | 122.1074 | 122.0195 | 121.9374 | 0.32647 | -121.9747 | 0.006657 | 0.11442 | 0.14967 | 0.16517 | -122.0254
2135.6719 | 122.0947 | -0.073242 | 121.8933 | 1.4211e-13 | -0.041529 | 0.0014317 | 0.0645 | -0.0090999 | 0.052683 | -0.01755 | -0.0040121 | -0.0014849 | 0.019827 | 0.029203 | 0.015646 | 0.019361 | 0.23492 | -0.063349 | 122.025 | 121.928 | 121.8412 | -0.058478 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.027442 | 0.058115 | -0.10004 | 0.014764 | 0.13165 | 0.092603 | 0.009893 | -0.004871 | 0.034651 | -0.05209 | -0.026803 | -121.9782 | 0.10176 | 0.007733 | 0.034536 | -121.8659 | -121.8352 | 122.0982 | 122.0012 | 121.9145 | 0.30816 | -121.9518 | -0.011654 | 0.10068 | 0.13136 | 0.14686 | -121.9934
2137.4219 | 121.9803 | -0.11444 | 121.9528 | 1.4211e-13 | -0.040888 | 0.0016453 | 0.064286 | -0.0093137 | 0.052897 | -0.0022892 | -0.0044395 | -0.0019123 | 0.019827 | 0.029203 | 0.015859 | 0.019361 | 0.23949 | -0.05877 | 122.0204 | 121.9188 | 121.8504 | -0.049321 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.06512 | 0.06756 | 0.1338 | 0.055671 | -0.009449 | -0.034016 | -0.10244 | 0.009817 | -122.0377 | 0.1338 | 0.053511 | 0.043694 | -121.9391 | -121.8947 | 122.1348 | 122.0332 | 121.9648 | 0.35393 | -122.0021 | 0.029545 | 0.12815 | 0.17256 | 0.18806 | -122.0574
2139.125 | 121.9757 | -0.11444 | 121.9299 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0088863 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.02963 | 0.015859 | 0.014783 | 0.23949 | -0.05877 | 122.0158 | 121.9234 | 121.8412 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.027442 | 0.067272 | -0.10004 | 0.060542 | 0.08587 | 0.12922 | 0.055671 | -0.004871 | -0.006549 | -0.088711 | 0.014396 | -122.0194 | 0.13838 | 0.053511 | 0.039115 | -121.9025 | -121.8627 | 122.1302 | 122.0378 | 121.9557 | 0.35393 | -121.9838 | 0.024966 | 0.14188 | 0.18171 | 0.19264 | -122.03
2140.8906 | 122.1039 | -0.073242 | 121.9025 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019613 | 0.029203 | 0.015646 | 0.014783 | 0.23949 | -0.063349 | 122.0158 | 121.9234 | 121.855 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.014764 | 0.11334 | 0.088025 | 0.009893 | -0.004871 | 0.020917 | -0.047509 | -0.031382 | -121.9919 | 0.097183 | 0.012312 | 0.043694 | -121.8842 | -121.8398 | 122.089 | 121.9966 | 121.9282 | 0.31274 | -121.9609 | -0.016233 | 0.091527 | 0.13594 | 0.14686 | -122.0071
2142.5781 | 122.0627 | -0.082397 | 121.9299 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.064714 | -0.0088863 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019827 | 0.029203 | 0.015646 | 0.005626 | 0.23949 | -0.063349 | 122.0112 | 121.928 | 121.855 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.094053 | 0.004549 | 0.062694 | -0.10004 | 0.028498 | 0.081292 | 0.088023 | 0.019048 | -0.00945 | -0.00197 | -0.074975 | -0.017648 | -122.024 | 0.10634 | 0.016888 | 0.034536 | -121.9254 | -121.8672 | 122.0936 | 122.0104 | 121.9374 | 0.32189 | -121.9838 | -0.011656 | 0.086946 | 0.14509 | 0.16059 | -122.03
2144.3281 | 121.9757 | -0.13733 | 121.9528 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.065141 | -0.0093137 | 0.05311 | -0.0022892 | -0.0040121 | -0.0012713 | 0.02004 | 0.029416 | 0.015859 | 0.019361 | 0.23492 | -0.05877 | 122.0158 | 121.9325 | 121.8458 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.058115 | -0.10004 | 0.08343 | 0.062982 | 0.15669 | 0.078559 | -0.004871 | -0.020279 | -0.10702 | 0.037284 | -122.0377 | 0.16585 | 0.07182 | 0.034536 | -121.9345 | -121.8947 | 122.1531 | 122.0699 | 121.9831 | 0.37224 | -122.0067 | 0.052433 | 0.15561 | 0.19544 | 0.21095 | -122.0529
2146.1094 | 121.9986 | -0.10529 | 121.9528 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0090999 | 0.05311 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019827 | 0.029416 | 0.015859 | 0.010204 | 0.23492 | -0.05877 | 122.0204 | 121.9325 | 121.8458 | -0.067636 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.03765 | 0.06756 | 0.11549 | 0.046516 | 0.008866 | -0.020279 | -0.10702 | 0.005241 | -122.0377 | 0.12923 | 0.044356 | 0.039115 | -121.9391 | -121.8947 | 122.1257 | 122.0378 | 121.9511 | 0.3402 | -122.0205 | 0.02039 | 0.11899 | 0.1634 | 0.17433 | -122.0529
2147.8125 | 121.9849 | -0.10529 | 121.9299 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064714 | -0.0088863 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019827 | 0.028989 | 0.015859 | 0.014783 | 0.23949 | -0.05877 | 122.0158 | 121.928 | 121.8504 | -0.053899 | 0.023941 | 0.073618 | -0.051772 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.051387 | 0.08587 | 0.12007 | 0.046516 | -0.004871 | -0.00197 | -0.079554 | -0.003917 | -122.0148 | 0.12923 | 0.053514 | 0.057431 | -121.9116 | -121.8718 | 122.1211 | 122.0332 | 121.9557 | 0.34478 | -121.9838 | 0.02039 | 0.12357 | 0.1634 | 0.1789 | -122.0391
2149.5781 | 122.1405 | -0.073242 | 121.8887 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.0645 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.02004 | 0.029416 | 0.015646 | 0.014783 | 0.23492 | -0.05877 | 122.0112 | 121.9234 | 121.855 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.067272 | -0.10462 | 0.014764 | 0.12249 | 0.088025 | 0.014472 | -0.000292 | 0.03465 | -0.033776 | -0.031382 | -121.9736 | 0.097183 | 0.012312 | 0.043694 | -121.875 | -121.8215 | 122.0845 | 121.9966 | 121.9282 | 0.30816 | -121.9472 | -0.011654 | 0.086949 | 0.14051 | 0.15144 | -121.9934
2151.3281 | 122.1268 | -0.068665 | 121.9162 | 1.4211e-13 | -0.041102 | 0.0016453 | 0.064714 | -0.0093137 | 0.05311 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.029416 | 0.016073 | 0.019361 | 0.23492 | -0.063349 | 122.0204 | 121.928 | 121.8504 | -0.058478 | 0.014784 | 0.078197 | -0.056351 | -0.084896 | 0.013707 | 0.062694 | -0.10004 | 0.010187 | 0.10418 | 0.088026 | 0.005316 | -0.004871 | 0.011763 | -0.065821 | -0.03138 | -122.0011 | 0.083449 | 0.012314 | 0.043694 | -121.9025 | -121.8535 | 122.089 | 121.9966 | 121.919 | 0.30358 | -121.9747 | -0.016231 | 0.082372 | 0.13136 | 0.14686 | -122.0162
2153.0781 | 122.0673 | -0.07782 | 121.9025 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064286 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019613 | 0.029203 | 0.015646 | 0.014783 | 0.24407 | -0.05877 | 122.0204 | 121.9325 | 121.8504 | -0.063057 | 0.033099 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.10004 | 0.014763 | 0.11791 | 0.092603 | 0.01905 | 0.004287 | 0.030075 | -0.052088 | -0.022225 | -121.9874 | 0.11092 | 0.01689 | 0.039115 | -121.8888 | -121.8489 | 122.0982 | 122.0104 | 121.9282 | 0.32189 | -121.9655 | -0.007076 | 0.091527 | 0.13136 | 0.15602 | -122.0025
2154.8438 | 122.0627 | -0.082397 | 121.9116 | 1.4211e-13 | -0.041316 | 0.0018589 | 0.0645 | -0.0088863 | 0.052897 | -0.0099192 | -0.0040121 | -0.0012713 | 0.02004 | 0.028989 | 0.015859 | 0.019361 | 0.23949 | -0.063349 | 122.0204 | 121.9234 | 121.8504 | -0.058478 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.023919 | 0.10876 | 0.10176 | 0.019048 | -0.004871 | 0.011762 | -0.061243 | -0.026806 | -122.0011 | 0.10634 | 0.016888 | 0.043694 | -121.8933 | -121.8535 | 122.1028 | 122.0058 | 121.9328 | 0.32189 | -121.9701 | -0.007078 | 0.10068 | 0.14051 | 0.15602 | -122.0208
2156.5312 | 122.0169 | -0.1236 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.0645 | -0.0088863 | 0.052897 | -0.01755 | -0.0044395 | -0.0014849 | 0.019827 | 0.029203 | 0.016073 | 0.019361 | 0.24865 | -0.054192 | 122.0204 | 121.9417 | 121.8504 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.058115 | -0.10462 | 0.065118 | 0.081293 | 0.14296 | 0.069404 | 0.004286 | 0.002611 | -0.088709 | 0.018972 | -122.0194 | 0.14754 | 0.062666 | 0.043694 | -121.9254 | -121.881 | 122.144 | 122.0653 | 121.974 | 0.37225 | -121.9976 | 0.043278 | 0.1373 | 0.18171 | 0.19721 | -122.0437
2158.2812 | 122.0947 | -0.073242 | 121.9208 | 1.4211e-13 | -0.041316 | 0.0018589 | 0.064714 | -0.0090999 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019399 | 0.029416 | 0.015859 | 0.010204 | 0.23949 | -0.05877 | 122.025 | 121.9371 | 121.8504 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.023921 | 0.10418 | 0.083446 | 0.014472 | -0.009449 | 0.016344 | -0.070398 | -0.031382 | -122.0057 | 0.097183 | 0.007733 | 0.039115 | -121.9071 | -121.8581 | 122.0982 | 122.0104 | 121.9236 | 0.31274 | -121.9701 | -0.011654 | 0.086949 | 0.13594 | 0.15144 | -122.0254
2160.0312 | 121.994 | -0.1236 | 121.9482 | 1.4211e-13 | -0.041529 | 0.0014317 | 0.064714 | -0.0086727 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.02963 | 0.015646 | 0.019361 | 0.24407 | -0.063349 | 122.025 | 121.9371 | 121.855 | -0.058478 | 0.014784 | 0.064461 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.095467 | 0.065118 | 0.076717 | 0.14296 | 0.060247 | -0.004871 | -0.011122 | -0.093285 | 0.028129 | -122.0331 | 0.13838 | 0.062666 | 0.034537 | -121.9345 | -121.8901 | 122.1486 | 122.0607 | 121.9786 | 0.36767 | -122.0067 | 0.0387 | 0.1373 | 0.18171 | 0.18806 | -122.0437
2161.7969 | 122.0261 | -0.11444 | 121.907 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.064714 | -0.0093137 | 0.052897 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019827 | 0.029416 | 0.015859 | 0.023939 | 0.24865 | -0.05877 | 122.025 | 121.9371 | 121.8504 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10004 | 0.055963 | 0.11792 | 0.13838 | 0.055671 | -0.000292 | 0.030077 | -0.056665 | 0.014396 | -121.9919 | 0.13838 | 0.053511 | 0.039115 | -121.8933 | -121.8489 | 122.1394 | 122.0516 | 121.9648 | 0.36309 | -121.9655 | 0.029545 | 0.12815 | 0.17256 | 0.19264 | -122.0071
2163.5 | 122.1039 | -0.054932 | 121.8933 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019827 | 0.029416 | 0.015646 | 0.023939 | 0.24407 | -0.05877 | 122.025 | 121.9325 | 121.855 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.094053 | 0.009128 | 0.053537 | -0.10004 | 0.001033 | 0.13165 | 0.078871 | -0.003838 | -0.004871 | 0.03923 | -0.038354 | -0.045113 | -121.9874 | 0.074294 | -0.005998 | 0.039115 | -121.8842 | -121.8398 | 122.0799 | 121.9875 | 121.9099 | 0.299 | -121.9472 | -0.039121 | 0.06406 | 0.10847 | 0.12855 | -121.9934
2165.25 | 121.9757 | -0.12817 | 121.9482 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064714 | -0.0090999 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.02004 | 0.02963 | 0.015859 | 0.019361 | 0.23949 | -0.054192 | 122.025 | 121.9371 | 121.8504 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.009128 | 0.058115 | -0.10462 | 0.074275 | 0.076717 | 0.14753 | 0.073982 | -0.000293 | -0.011122 | -0.097864 | 0.02355 | -122.0331 | 0.15212 | 0.067244 | 0.043694 | -121.9391 | -121.8901 | 122.1531 | 122.0653 | 121.9786 | 0.36767 | -122.0021 | 0.043278 | 0.1373 | 0.18629 | 0.20637 | -122.0529
2166.9531 | 122.049 | -0.082397 | 121.9254 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.064928 | -0.0090999 | 0.052897 | -0.01755 | -0.0044395 | -0.0019123 | 0.019827 | 0.029416 | 0.015646 | 0.010204 | 0.24407 | -0.054192 | 122.0158 | 121.9371 | 121.855 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.018285 | 0.053537 | -0.10004 | 0.028498 | 0.090448 | 0.092601 | 0.028205 | -0.000293 | 0.011766 | -0.070397 | -0.017648 | -122.0148 | 0.10634 | 0.026046 | 0.043694 | -121.9071 | -121.8718 | 122.0982 | 122.0195 | 121.9374 | 0.32647 | -121.9793 | -0.007078 | 0.10068 | 0.13593 | 0.16059 | -122.0254
2168.7188 | 121.994 | -0.1236 | 121.9254 | 1.4211e-13 | -0.041102 | 0.0014317 | 0.064714 | -0.0093137 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.02004 | 0.029203 | 0.015859 | 0.019361 | 0.24407 | -0.05877 | 122.025 | 121.9417 | 121.8504 | -0.049321 | 0.019362 | 0.073618 | -0.051772 | -0.089475 | 0.018285 | 0.053537 | -0.10462 | 0.074275 | 0.099605 | 0.14296 | 0.064826 | -0.009449 | 0.016344 | -0.074976 | 0.018972 | -122.0148 | 0.14296 | 0.071824 | 0.052852 | -121.9071 | -121.8718 | 122.1486 | 122.0653 | 121.974 | 0.36767 | -121.9747 | 0.034121 | 0.14188 | 0.17713 | 0.19721 | -122.03
2170.4688 | 121.9849 | -0.10986 | 121.9391 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0097409 | 0.05311 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019399 | 0.029416 | 0.015646 | 0.019361 | 0.25323 | -0.067927 | 122.025 | 121.9371 | 121.855 | -0.058478 | 0.019362 | 0.078197 | -0.056351 | -0.094053 | 0.013707 | 0.058115 | -0.1092 | 0.051385 | 0.085872 | 0.12922 | 0.041936 | -0.009449 | -0.001967 | -0.08413 | 0.00066 | -122.0331 | 0.12923 | 0.053512 | 0.052852 | -121.9254 | -121.881 | 122.1348 | 122.047 | 121.9648 | 0.36309 | -121.9976 | 0.01581 | 0.12357 | 0.16798 | 0.18806 | -122.0483
2172.1562 | 122.1039 | -0.064087 | 121.9208 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064714 | -0.0090999 | 0.053324 | -0.02518 | -0.0044395 | -0.0016987 | 0.019827 | 0.029416 | 0.015859 | 0.014783 | 0.23949 | -0.063349 | 122.025 | 121.9417 | 121.855 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.058115 | -0.095467 | 0.005609 | 0.10418 | 0.07887 | 0.000738 | -0.004871 | 0.020922 | -0.065819 | -0.03138 | -122.0011 | 0.083449 | 0.003157 | 0.034537 | -121.9071 | -121.8627 | 122.089 | 122.0058 | 121.919 | 0.30358 | -121.9793 | -0.016231 | 0.077794 | 0.1222 | 0.14228 | -122.0162
2173.9219 | 122.0535 | -0.09613 | 121.9254 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0090999 | 0.052683 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.029416 | 0.015859 | 0.014783 | 0.24865 | -0.063349 | 122.025 | 121.9325 | 121.8595 | -0.053899 | 0.019362 | 0.06904 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.1092 | 0.042231 | 0.099605 | 0.11091 | 0.032781 | -0.00945 | 0.007187 | -0.065819 | -0.013073 | -122.0057 | 0.11549 | 0.030621 | 0.043694 | -121.9116 | -121.8672 | 122.1211 | 122.0287 | 121.9557 | 0.34478 | -121.9793 | 0.015812 | 0.10984 | 0.15424 | 0.16517 | -122.0346
2175.6875 | 121.9803 | -0.12817 | 121.9711 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.02963 | 0.015646 | 0.014783 | 0.24865 | -0.063349 | 122.025 | 121.9417 | 121.855 | -0.049321 | 0.02852 | 0.073618 | -0.056351 | -0.084896 | 0.018285 | 0.058115 | -0.10462 | 0.078853 | 0.053829 | 0.14296 | 0.064825 | -0.014028 | -0.029432 | -0.11617 | 0.02355 | -122.056 | 0.15669 | 0.071823 | 0.048273 | -121.9528 | -121.913 | 122.1531 | 122.0699 | 121.9831 | 0.37683 | -122.0205 | 0.043278 | 0.14646 | 0.18629 | 0.20179 | -122.0758
2177.3906 | 122.0215 | -0.11902 | 121.9437 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.065141 | -0.0088863 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.02004 | 0.029203 | 0.016073 | 0.019361 | 0.23949 | -0.063349 | 122.0295 | 121.9417 | 121.855 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.1092 | 0.06512 | 0.085872 | 0.13838 | 0.05567 | -0.00945 | -0.001967 | -0.088708 | 0.009816 | -122.024 | 0.14296 | 0.058089 | 0.048273 | -121.93 | -121.881 | 122.1486 | 122.0607 | 121.974 | 0.35851 | -121.9976 | 0.038701 | 0.13273 | 0.18171 | 0.19722 | -122.0529
2179.1719 | 121.9711 | -0.11444 | 121.9757 | 1.4211e-13 | -0.041316 | 0.0018589 | 0.064714 | -0.0090999 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019827 | 0.029203 | 0.015859 | 0.019361 | 0.24865 | -0.05877 | 122.0295 | 121.9325 | 121.8641 | -0.053899 | 0.023941 | 0.078197 | -0.051772 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.060542 | 0.053829 | 0.1338 | 0.055671 | -0.004871 | -0.043167 | -0.11159 | 0.009817 | -122.0606 | 0.13838 | 0.062669 | 0.052852 | -121.962 | -121.9176 | 122.144 | 122.047 | 121.9786 | 0.36309 | -122.0296 | 0.029545 | 0.12815 | 0.17256 | 0.19264 | -122.0803
2180.9375 | 122.0032 | -0.10071 | 121.9711 | 1.4211e-13 | -0.041102 | 0.0018589 | 0.064928 | -0.0090999 | 0.05311 | -0.01755 | -0.0040121 | -0.0014849 | 0.019827 | 0.02963 | 0.015859 | 0.019361 | 0.25323 | -0.05877 | 122.0341 | 121.9371 | 121.8595 | -0.053899 | 0.023941 | 0.06904 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.1092 | 0.046809 | 0.062985 | 0.12007 | 0.041938 | -0.004871 | -0.03401 | -0.1116 | -0.008495 | -122.0606 | 0.12465 | 0.035199 | 0.043694 | -121.9574 | -121.913 | 122.1348 | 122.0378 | 121.9602 | 0.35394 | -122.025 | 0.011233 | 0.11442 | 0.15882 | 0.16975 | -122.0803
2182.625 | 122.0627 | -0.073242 | 121.9162 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.0645 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.02963 | 0.015646 | 0.023939 | 0.24865 | -0.054192 | 122.025 | 121.9371 | 121.8595 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.053537 | -0.10462 | 0.014764 | 0.10876 | 0.097181 | 0.01905 | 0.004286 | 0.020921 | -0.056664 | -0.031382 | -121.9965 | 0.092604 | 0.012312 | 0.043694 | -121.9025 | -121.8627 | 122.0982 | 122.0104 | 121.9328 | 0.32189 | -121.9747 | -0.007076 | 0.086949 | 0.12678 | 0.15144 | -122.0208
2184.375 | 121.9803 | -0.11444 | 121.9666 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.064286 | -0.0086727 | 0.05311 | -0.0099192 | -0.0042257 | -0.0010577 | 0.019613 | 0.029203 | 0.015646 | 0.019361 | 0.25323 | -0.054192 | 122.025 | 121.9417 | 121.8641 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.06512 | 0.058406 | 0.1338 | 0.060249 | -0.004871 | -0.024855 | -0.10244 | 0.009817 | -122.0514 | 0.14296 | 0.053511 | 0.043694 | -121.9483 | -121.9039 | 122.1394 | 122.0561 | 121.9786 | 0.36767 | -122.0159 | 0.029545 | 0.13273 | 0.17713 | 0.18806 | -122.0712
2186.0781 | 122.0993 | -0.091553 | 121.9116 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019827 | 0.02963 | 0.015646 | 0.028518 | 0.24865 | -0.05877 | 122.0341 | 121.9325 | 121.855 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.042232 | 0.12249 | 0.12007 | 0.032783 | -0.009449 | 0.02092 | -0.056664 | -0.01765 | -122.0011 | 0.11549 | 0.035202 | 0.052852 | -121.8933 | -121.8535 | 122.1257 | 122.0241 | 121.9465 | 0.3402 | -121.9609 | 0.002078 | 0.10984 | 0.14967 | 0.16975 | -122.0208
2187.8281 | 121.994 | -0.10529 | 121.9574 | 1.4211e-13 | -0.041529 | 0.0018589 | 0.064928 | -0.0088863 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.020254 | 0.029416 | 0.015859 | 0.019361 | 0.25781 | -0.05877 | 122.0295 | 121.9371 | 121.855 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.058115 | -0.095467 | 0.051387 | 0.07214 | 0.12465 | 0.046516 | -0.004871 | -0.020277 | -0.10244 | 0.009819 | -122.0423 | 0.12465 | 0.044356 | 0.034537 | -121.9345 | -121.8993 | 122.1348 | 122.0424 | 121.9602 | 0.36309 | -122.0113 | 0.02039 | 0.12815 | 0.1634 | 0.1789 | -122.0529
2189.6094 | 122.0032 | -0.11902 | 121.9528 | 1.4211e-13 | -0.041529 | 0.0020727 | 0.0645 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.02004 | 0.029203 | 0.016073 | 0.014783 | 0.25781 | -0.049614 | 122.0295 | 121.9371 | 121.855 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.1092 | 0.06512 | 0.076717 | 0.1338 | 0.069405 | 0.004285 | -0.0157 | -0.097863 | 0.009816 | -122.0423 | 0.13838 | 0.058089 | 0.048273 | -121.9391 | -121.8947 | 122.1486 | 122.0561 | 121.974 | 0.37683 | -122.0067 | 0.029544 | 0.13273 | 0.17713 | 0.19264 | -122.062
2191.2969 | 122.049 | -0.10529 | 121.9162 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064286 | -0.0090999 | 0.052683 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019827 | 0.029203 | 0.015646 | 0.019361 | 0.24865 | -0.063349 | 122.025 | 121.9417 | 121.8595 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.051387 | 0.10876 | 0.12465 | 0.041937 | -0.00945 | 0.025499 | -0.056664 | 0.005241 | -122.0057 | 0.13381 | 0.039777 | 0.034536 | -121.9071 | -121.8535 | 122.1302 | 122.047 | 121.9648 | 0.35394 | -121.9701 | 0.015811 | 0.11441 | 0.16798 | 0.1789 | -122.0162
2193.0469 | 122.0673 | -0.086975 | 121.9391 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0090999 | 0.052897 | -0.01755 | -0.0044395 | -0.0014849 | 0.02004 | 0.029416 | 0.015646 | 0.019361 | 0.25323 | -0.049614 | 122.025 | 121.9417 | 121.8595 | -0.053899 | 0.019362 | 0.078197 | -0.070087 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.033076 | 0.085872 | 0.10634 | 0.037361 | 0.004285 | 0.002611 | -0.079552 | -0.017649 | -122.024 | 0.10634 | 0.016888 | 0.034537 | -121.9254 | -121.8764 | 122.1119 | 122.0287 | 121.9465 | 0.3402 | -121.993 | 0.002079 | 0.10068 | 0.14967 | 0.16517 | -122.0437
2194.8281 | 121.9894 | -0.13275 | 121.962 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.0645 | -0.0090999 | 0.052897 | -0.01755 | -0.0042257 | -0.0012713 | 0.02004 | 0.02963 | 0.015859 | 0.014783 | 0.25781 | -0.05877 | 122.0295 | 121.9463 | 121.8641 | -0.053899 | 0.02852 | 0.082776 | -0.056351 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.078852 | 0.067562 | 0.14753 | 0.073981 | -0.004871 | -0.015698 | -0.097861 | 0.032706 | -122.0514 | 0.16127 | 0.0764 | 0.043694 | -121.9528 | -121.8993 | 122.1623 | 122.079 | 121.9969 | 0.39056 | -122.0159 | 0.043276 | 0.14188 | 0.19545 | 0.21553 | -122.062
2196.5312 | 122.113 | -0.07782 | 121.907 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.0645 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0010577 | 0.02004 | 0.029416 | 0.015432 | 0.023939 | 0.26239 | -0.054192 | 122.0295 | 121.9463 | 121.8641 | -0.049321 | 0.02852 | 0.073618 | -0.056351 | -0.089475 | 0.018285 | 0.062694 | -0.10004 | 0.028499 | 0.12249 | 0.10176 | 0.023628 | -0.004871 | 0.039234 | -0.042929 | -0.022225 | -121.9965 | 0.10634 | 0.021469 | 0.043694 | -121.8888 | -121.8443 | 122.1074 | 122.0241 | 121.9419 | 0.34021 | -121.9564 | -0.011655 | 0.096105 | 0.14051 | 0.15144 | -122.0071
2198.2812 | 122.0352 | -0.12817 | 121.9482 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.0645 | -0.0090999 | 0.052897 | -0.02518 | -0.0042257 | -0.0014849 | 0.02004 | 0.029416 | 0.015859 | 0.023939 | 0.26239 | -0.063349 | 122.0295 | 121.9371 | 121.8595 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.067272 | -0.10004 | 0.069696 | 0.081295 | 0.15211 | 0.064825 | -0.004871 | -0.011122 | -0.088707 | 0.028129 | -122.0286 | 0.15212 | 0.067244 | 0.039115 | -121.9345 | -121.881 | 122.1577 | 122.0653 | 121.9877 | 0.39056 | -122.0067 | 0.047856 | 0.14188 | 0.19545 | 0.20637 | -122.0483
2200.0469 | 122.0764 | -0.10071 | 121.9299 | 1.4211e-13 | -0.041529 | 0.0018589 | 0.0645 | -0.0090999 | 0.053324 | -0.0099192 | -0.0046531 | -0.0010577 | 0.019613 | 0.029203 | 0.015859 | 0.023939 | 0.26239 | -0.05877 | 122.025 | 121.9417 | 121.8641 | -0.049321 | 0.019362 | 0.06904 | -0.06093 | -0.084896 | 0.009128 | 0.058115 | -0.10462 | 0.051387 | 0.095027 | 0.12465 | 0.041938 | -0.009449 | 0.011766 | -0.065818 | -0.003916 | -122.0148 | 0.12007 | 0.039778 | 0.043694 | -121.9208 | -121.8718 | 122.1257 | 122.0424 | 121.9648 | 0.3631 | -121.9793 | 0.015812 | 0.10984 | 0.15882 | 0.16975 | -122.0346
2201.8125 | 122.0398 | -0.10986 | 121.9391 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064714 | -0.0088863 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.029416 | 0.015646 | 0.014783 | 0.25781 | -0.05877 | 122.0295 | 121.9417 | 121.8641 | -0.058478 | 0.02852 | 0.073618 | -0.06093 | -0.089475 | 0.009128 | 0.062694 | -0.10004 | 0.051385 | 0.09045 | 0.12465 | 0.051093 | -0.000292 | 0.002611 | -0.074973 | 0.009818 | -122.0286 | 0.13838 | 0.048933 | 0.039115 | -121.93 | -121.8764 | 122.1394 | 122.0516 | 121.974 | 0.36767 | -121.9976 | 0.020388 | 0.11899 | 0.17256 | 0.18348 | -122.0391
2203.5156 | 121.9894 | -0.1236 | 121.9666 | 1.4211e-13 | -0.041529 | 0.0018589 | 0.064928 | -0.0088863 | 0.052897 | -0.01755 | -0.0040121 | -0.0016987 | 0.020254 | 0.029416 | 0.015646 | 0.014783 | 0.26239 | -0.05877 | 122.025 | 121.9371 | 121.8641 | -0.049321 | 0.02852 | 0.078197 | -0.051772 | -0.094053 | 0.013707 | 0.062694 | -0.10462 | 0.074275 | 0.058406 | 0.13838 | 0.064826 | -0.009449 | -0.029433 | -0.10244 | 0.018972 | -122.0606 | 0.15212 | 0.071824 | 0.052852 | -121.9528 | -121.9039 | 122.1486 | 122.0607 | 121.9877 | 0.38598 | -122.0159 | 0.029543 | 0.1373 | 0.18629 | 0.20179 | -122.0712
2205.2656 | 122.0306 | -0.1236 | 121.9391 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064714 | -0.0088863 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019827 | 0.029203 | 0.015859 | 0.019361 | 0.26239 | -0.05877 | 122.025 | 121.9509 | 121.8595 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.009128 | 0.058115 | -0.10462 | 0.065118 | 0.085872 | 0.14296 | 0.064826 | -0.000292 | 0.011769 | -0.079552 | 0.018972 | -122.024 | 0.15212 | 0.062666 | 0.043694 | -121.93 | -121.881 | 122.1486 | 122.0745 | 121.9831 | 0.38598 | -121.9976 | 0.0387 | 0.13272 | 0.18171 | 0.20179 | -122.0437
2207.0312 | 122.0535 | -0.09613 | 121.9116 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0088863 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019613 | 0.029203 | 0.015646 | 0.014783 | 0.26239 | -0.054192 | 122.0295 | 121.9463 | 121.8687 | -0.058478 | 0.02852 | 0.073618 | -0.065509 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.037652 | 0.11792 | 0.11091 | 0.041938 | 0.004286 | 0.034656 | -0.042928 | -0.013073 | -122.0011 | 0.12465 | 0.030621 | 0.043694 | -121.8933 | -121.8535 | 122.1257 | 122.0424 | 121.9648 | 0.35852 | -121.9701 | 0.006655 | 0.11441 | 0.15424 | 0.16975 | -122.0208
2208.7969 | 122.0764 | -0.068665 | 121.9528 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064928 | -0.0093137 | 0.052897 | -0.0022892 | -0.0046531 | -0.0014849 | 0.02004 | 0.029416 | 0.015859 | 0.014783 | 0.26697 | -0.05877 | 122.0341 | 121.9463 | 121.8595 | -0.049321 | 0.02852 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.10462 | 0.019344 | 0.081295 | 0.083448 | 0.009895 | -0.009449 | -0.006543 | -0.093285 | -0.035959 | -122.0331 | 0.097185 | 0.007735 | 0.043694 | -121.9345 | -121.8901 | 122.1028 | 122.0149 | 121.9282 | 0.33563 | -122.0021 | -0.011653 | 0.08695 | 0.13136 | 0.13771 | -122.0574
2210.5 | 122.0901 | -0.086975 | 121.9299 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064928 | -0.0090999 | 0.052897 | -0.01755 | -0.0042257 | -0.0014849 | 0.020254 | 0.029416 | 0.016073 | 0.010204 | 0.26239 | -0.063349 | 122.0341 | 121.9509 | 121.8687 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.013707 | 0.053537 | -0.1092 | 0.037654 | 0.10418 | 0.097179 | 0.023626 | -0.014028 | 0.020924 | -0.061239 | -0.022228 | -122.0194 | 0.11092 | 0.026045 | 0.048273 | -121.9162 | -121.8764 | 122.1211 | 122.0378 | 121.9557 | 0.34936 | -121.9793 | -0.0025 | 0.10068 | 0.14051 | 0.16517 | -122.0391
2212.2656 | 122.0627 | -0.10071 | 121.9528 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.0645 | -0.0090999 | 0.052683 | -0.0099192 | -0.0042257 | -0.0016987 | 0.020254 | 0.029416 | 0.015859 | 0.014783 | 0.26239 | -0.05877 | 122.025 | 121.9463 | 121.8687 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.013707 | 0.062694 | -0.10462 | 0.051387 | 0.072139 | 0.11549 | 0.041938 | -0.009449 | -0.006543 | -0.084127 | -0.003916 | -122.0423 | 0.12465 | 0.039778 | 0.043694 | -121.9391 | -121.8901 | 122.1257 | 122.047 | 121.9694 | 0.3631 | -122.0021 | 0.011233 | 0.11442 | 0.1634 | 0.17891 | -122.0574
2214.0312 | 122.1085 | -0.059509 | 121.9299 | 1.4211e-13 | -0.041529 | 0.0014317 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019827 | 0.028989 | 0.015646 | 0.023939 | 0.25781 | -0.054192 | 122.0295 | 121.9463 | 121.8733 | -0.049321 | 0.02852 | 0.06904 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.010188 | 0.099605 | 0.083448 | 0.005317 | -0.004871 | 0.016345 | -0.056661 | -0.045115 | -122.0148 | 0.088029 | -0.006 | 0.039115 | -121.9116 | -121.8672 | 122.089 | 122.0058 | 121.9328 | 0.31732 | -121.9793 | -0.025387 | 0.077794 | 0.1222 | 0.12855 | -122.0346
2215.75 | 122.0673 | -0.064087 | 121.9025 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064714 | -0.0093137 | 0.05311 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019613 | 0.029416 | 0.015646 | 0.019361 | 0.27154 | -0.054192 | 122.0341 | 121.9463 | 121.8641 | -0.049321 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.022864 | 0.067272 | -0.1092 | 0.014766 | 0.13165 | 0.083448 | 0.009895 | -0.004871 | 0.043811 | -0.038352 | -0.045116 | -121.9919 | 0.088028 | 0.007736 | 0.052852 | -121.8796 | -121.8352 | 122.0982 | 122.0104 | 121.9282 | 0.33563 | -121.9518 | -0.025388 | 0.086951 | 0.13136 | 0.13771 | -122.0117
2217.5 | 122.1085 | -0.064087 | 121.9208 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.0645 | -0.0093137 | 0.052897 | -0.0022892 | -0.0042257 | -0.0010577 | 0.02004 | 0.029844 | 0.015859 | 0.019361 | 0.25781 | -0.067927 | 122.0295 | 121.9463 | 121.8687 | -0.049321 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.022864 | 0.062694 | -0.10004 | 0.014766 | 0.10876 | 0.083448 | -0.00384 | -0.018606 | 0.025501 | -0.052083 | -0.035958 | -122.0103 | 0.083449 | 0.003157 | 0.039115 | -121.8979 | -121.8581 | 122.0936 | 122.0104 | 121.9328 | 0.32189 | -121.9701 | -0.025388 | 0.086951 | 0.12678 | 0.13771 | -122.0208
2219.2656 | 122.0947 | -0.10071 | 121.9299 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.064714 | -0.0090999 | 0.052683 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.029416 | 0.015859 | 0.019361 | 0.26239 | -0.054192 | 122.0295 | 121.9463 | 121.8687 | -0.049321 | 0.02852 | 0.064461 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.10004 | 0.051387 | 0.099605 | 0.12007 | 0.046516 | -0.004871 | 0.016345 | -0.061239 | 0.000663 | -122.0102 | 0.12923 | 0.039778 | 0.039115 | -121.9071 | -121.8672 | 122.1302 | 122.047 | 121.9694 | 0.3631 | -121.9793 | 0.02039 | 0.12357 | 0.1634 | 0.16517 | -122.03
2220.9844 | 122.0993 | -0.073242 | 121.8933 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.0645 | -0.0090999 | 0.052897 | -0.02518 | -0.0046531 | -0.0014849 | 0.019827 | 0.029203 | 0.015219 | 0.014783 | 0.26239 | -0.054192 | 122.0341 | 121.9463 | 121.8687 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.014764 | 0.1408 | 0.088025 | 0.01905 | 0.004286 | 0.052966 | -0.024618 | -0.031382 | -121.9782 | 0.10176 | 0.012312 | 0.043694 | -121.8796 | -121.8306 | 122.1074 | 122.0195 | 121.9419 | 0.33563 | -121.9518 | -0.011654 | 0.086949 | 0.13594 | 0.15144 | -121.9979
2222.75 | 122.0856 | -0.086975 | 121.9437 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064714 | -0.0093137 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.020254 | 0.02963 | 0.015432 | 0.014783 | 0.26239 | -0.05877 | 122.0295 | 121.9463 | 121.8641 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.10462 | 0.033076 | 0.085872 | 0.10176 | 0.028205 | -0.004871 | 0.002612 | -0.079551 | -0.017649 | -122.024 | 0.11092 | 0.026045 | 0.043694 | -121.9208 | -121.8764 | 122.1165 | 122.0333 | 121.9511 | 0.34936 | -121.9976 | 0.006657 | 0.10984 | 0.15425 | 0.16059 | -122.0483
2224.5156 | 121.994 | -0.14191 | 121.9482 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.0645 | -0.0090999 | 0.05311 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019827 | 0.02963 | 0.016073 | 0.014783 | 0.26239 | -0.05877 | 122.0295 | 121.9417 | 121.8733 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.058115 | -0.10004 | 0.088008 | 0.081295 | 0.15669 | 0.083137 | -0.004871 | -0.006544 | -0.074971 | 0.041862 | -122.0331 | 0.16585 | 0.080977 | 0.039115 | -121.9254 | -121.8901 | 122.1714 | 122.0836 | 122.0152 | 0.40429 | -122.0021 | 0.057011 | 0.16477 | 0.20002 | 0.21553 | -122.0483
2226.2188 | 122.0901 | -0.082397 | 121.9025 | 1.4211e-13 | -0.041743 | 0.0020727 | 0.064714 | -0.0086727 | 0.05311 | -0.01755 | -0.0040121 | -0.0014849 | 0.02004 | 0.029416 | 0.015859 | 0.010204 | 0.26239 | -0.054192 | 122.0295 | 121.9417 | 121.8733 | -0.053899 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.028498 | 0.12707 | 0.092601 | 0.028205 | -0.000293 | 0.039232 | -0.029195 | -0.026806 | -121.9874 | 0.11092 | 0.021467 | 0.048273 | -121.8888 | -121.8444 | 122.1119 | 122.0241 | 121.9557 | 0.34478 | -121.9564 | -0.002499 | 0.096104 | 0.14051 | 0.15144 | -122.0117
2227.9844 | 122.0718 | -0.09613 | 121.9482 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064714 | -0.0093137 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.02004 | 0.029416 | 0.015219 | 0.019361 | 0.26239 | -0.054192 | 122.0341 | 121.9509 | 121.8595 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.022864 | 0.058115 | -0.10462 | 0.046809 | 0.085873 | 0.11549 | 0.041938 | -0.004871 | 0.002614 | -0.088707 | -0.008494 | -122.024 | 0.12007 | 0.030621 | 0.039115 | -121.9254 | -121.8901 | 122.1302 | 122.047 | 121.9557 | 0.35852 | -121.9976 | 0.020391 | 0.11899 | 0.15424 | 0.17433 | -122.0529
2229.7031 | 122.0764 | -0.091553 | 121.9345 | 1.4211e-13 | -0.041316 | 0.0014317 | 0.064286 | -0.0093137 | 0.052897 | -0.01755 | -0.0042257 | -0.0014849 | 0.02004 | 0.029416 | 0.016073 | 0.019361 | 0.26697 | -0.05877 | 122.0341 | 121.9463 | 121.8733 | -0.058478 | 0.014784 | 0.06904 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.033075 | 0.099606 | 0.11091 | 0.032783 | -0.000292 | 0.011768 | -0.061238 | -0.013071 | -122.0194 | 0.10634 | 0.026044 | 0.039115 | -121.9162 | -121.8718 | 122.1257 | 122.0378 | 121.9648 | 0.35852 | -121.993 | 0.006657 | 0.10984 | 0.15425 | 0.16059 | -122.0391
2231.4688 | 122.0856 | -0.07782 | 121.9254 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0046531 | -0.0016987 | 0.02004 | 0.029416 | 0.015646 | 0.019361 | 0.27154 | -0.05877 | 122.025 | 121.9463 | 121.8641 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.10462 | 0.028499 | 0.099605 | 0.097181 | 0.01905 | -0.009449 | 0.020923 | -0.06124 | -0.026804 | -122.0057 | 0.10176 | 0.01689 | 0.043694 | -121.9025 | -121.8672 | 122.1028 | 122.0241 | 121.9419 | 0.34936 | -121.9747 | -0.002498 | 0.10068 | 0.13594 | 0.15602 | -122.03
2233.1719 | 121.9803 | -0.11902 | 121.9666 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.065141 | -0.0086727 | 0.052683 | -0.01755 | -0.0042257 | -0.0016987 | 0.019827 | 0.02963 | 0.015859 | 0.019361 | 0.27154 | -0.063349 | 122.0341 | 121.9463 | 121.8641 | -0.058478 | 0.014784 | 0.073618 | -0.056351 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.060541 | 0.067562 | 0.13838 | 0.05567 | -0.004871 | -0.020276 | -0.10244 | 0.014395 | -122.0469 | 0.1338 | 0.062668 | 0.048273 | -121.9483 | -121.9084 | 122.1531 | 122.0653 | 121.9831 | 0.39056 | -122.025 | 0.038701 | 0.1373 | 0.17713 | 0.19264 | -122.0712
2234.9375 | 122.0947 | -0.082397 | 121.9025 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.064928 | -0.0090999 | 0.052897 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019613 | 0.029416 | 0.016073 | 0.014783 | 0.27154 | -0.054192 | 122.0341 | 121.9509 | 121.8687 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.10004 | 0.028498 | 0.13165 | 0.09718 | 0.028205 | -0.000293 | 0.04839 | -0.033773 | -0.017648 | -121.9874 | 0.11092 | 0.021467 | 0.039115 | -121.8842 | -121.8444 | 122.1165 | 122.0333 | 121.9511 | 0.35394 | -121.9564 | -0.002499 | 0.10068 | 0.14051 | 0.16059 | -122.0025
2236.6406 | 122.0947 | -0.07782 | 121.9528 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064928 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.02963 | 0.016073 | 0.014783 | 0.26239 | -0.05877 | 122.0295 | 121.9509 | 121.8778 | -0.053899 | 0.019362 | 0.073618 | -0.065509 | -0.080318 | 0.022864 | 0.053537 | -0.1092 | 0.023921 | 0.076717 | 0.092603 | 0.01905 | -0.004871 | -0.001964 | -0.07497 | -0.031383 | -122.0331 | 0.097182 | 0.012311 | 0.043694 | -121.93 | -121.8993 | 122.1074 | 122.0287 | 121.9557 | 0.34021 | -122.0067 | -0.002498 | 0.10068 | 0.13136 | 0.15144 | -122.062
2238.3906 | 122.1313 | -0.086975 | 121.8979 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.064928 | -0.0090999 | 0.053324 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.02963 | 0.015432 | 0.014783 | 0.26697 | -0.063349 | 122.0341 | 121.9463 | 121.8733 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.094053 | 0.013707 | 0.058115 | -0.10004 | 0.037654 | 0.13623 | 0.10176 | 0.023626 | -0.014028 | 0.048389 | -0.024617 | -0.01307 | -121.9919 | 0.11092 | 0.026045 | 0.039115 | -121.8842 | -121.8398 | 122.1211 | 122.0333 | 121.9602 | 0.35394 | -121.9472 | -0.007078 | 0.10068 | 0.14509 | 0.16059 | -121.9979
2240.1562 | 122.1268 | -0.068665 | 121.9299 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0095273 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019613 | 0.029844 | 0.015432 | 0.010204 | 0.27154 | -0.05877 | 122.0295 | 121.9554 | 121.8733 | -0.058478 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.010187 | 0.099605 | 0.078869 | 0.009895 | -0.000292 | 0.025503 | -0.056661 | -0.035959 | -122.0148 | 0.092606 | 0.012314 | 0.048273 | -121.9162 | -121.8718 | 122.0982 | 122.0241 | 121.9419 | 0.34021 | -121.9884 | -0.016231 | 0.082372 | 0.12678 | 0.14686 | -122.0346
2241.8594 | 121.9711 | -0.13275 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064714 | -0.0088863 | 0.05311 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019827 | 0.029844 | 0.015859 | 0.019361 | 0.26697 | -0.054192 | 122.0387 | 121.9509 | 121.8733 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.078852 | 0.099607 | 0.15211 | 0.078559 | -0.000293 | 0.011769 | -0.065816 | 0.028127 | -122.0286 | 0.15669 | 0.0764 | 0.048273 | -121.9254 | -121.881 | 122.1714 | 122.0836 | 122.006 | 0.39972 | -121.993 | 0.043276 | 0.14646 | 0.19087 | 0.21095 | -122.0437
2243.625 | 122.0123 | -0.12817 | 121.9803 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064928 | -0.0090999 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.029416 | 0.015859 | 0.019361 | 0.27154 | -0.049614 | 122.0295 | 121.9417 | 121.8778 | -0.049321 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.067272 | -0.1092 | 0.078853 | 0.049251 | 0.14753 | 0.07856 | -0.000293 | -0.038588 | -0.10244 | 0.018971 | -122.0698 | 0.14754 | 0.067244 | 0.048273 | -121.9666 | -121.913 | 122.1577 | 122.0699 | 122.006 | 0.39972 | -122.0296 | 0.038699 | 0.14188 | 0.19545 | 0.20179 | -122.0895
2245.3281 | 122.0993 | -0.068665 | 121.9254 | 1.4211e-13 | -0.041529 | 0.0018589 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0016987 | 0.02004 | 0.02963 | 0.016073 | 0.019361 | 0.2807 | -0.049614 | 122.0341 | 121.9463 | 121.8687 | -0.053899 | 0.02852 | 0.06904 | -0.065509 | -0.089475 | 0.009128 | 0.067272 | -0.1092 | 0.014766 | 0.10876 | 0.088026 | 0.019051 | 0.004285 | 0.020923 | -0.056661 | -0.040538 | -122.0148 | 0.097185 | 0.003156 | 0.043694 | -121.9162 | -121.8581 | 122.1028 | 122.0149 | 121.9374 | 0.34937 | -121.9793 | -0.02081 | 0.077793 | 0.13594 | 0.13771 | -122.0346
2247.0781 | 122.049 | -0.09613 | 121.9254 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.065141 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.02963 | 0.015859 | 0.019361 | 0.26697 | -0.063349 | 122.0341 | 121.9463 | 121.8733 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.094053 | 0.009128 | 0.058115 | -0.10004 | 0.046809 | 0.10876 | 0.11549 | 0.032781 | -0.014028 | 0.020923 | -0.052083 | -0.003915 | -122.0194 | 0.12465 | 0.0352 | 0.039115 | -121.9162 | -121.8672 | 122.1302 | 122.0424 | 121.9694 | 0.3631 | -121.9747 | 0.002077 | 0.10526 | 0.15424 | 0.16975 | -122.0254
2248.8281 | 122.113 | -0.091553 | 121.907 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0086727 | 0.05311 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019827 | 0.029416 | 0.015646 | 0.019361 | 0.27154 | -0.049614 | 122.0433 | 121.9509 | 121.8733 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.11378 | 0.037654 | 0.13623 | 0.11091 | 0.041939 | 0.004285 | 0.043813 | -0.033772 | -0.022229 | -121.9919 | 0.11549 | 0.030623 | 0.052852 | -121.8888 | -121.8443 | 122.1348 | 122.0424 | 121.9648 | 0.3631 | -121.9609 | 0.006657 | 0.10984 | 0.15425 | 0.16975 | -122.0208
2250.5312 | 122.081 | -0.09613 | 121.9162 | 1.4211e-13 | -0.041529 | 0.0014317 | 0.064714 | -0.0086727 | 0.052683 | -0.01755 | -0.0044395 | -0.0014849 | 0.019827 | 0.029844 | 0.015859 | 0.014783 | 0.26697 | -0.054192 | 122.0433 | 121.9463 | 121.8733 | -0.049321 | 0.02852 | 0.06904 | -0.065509 | -0.094053 | 0.018285 | 0.067272 | -0.1092 | 0.046809 | 0.12707 | 0.11091 | 0.041938 | -0.004871 | 0.030078 | -0.042928 | -0.013073 | -122.0103 | 0.12465 | 0.030621 | 0.043694 | -121.8979 | -121.8489 | 122.1394 | 122.0424 | 121.9694 | 0.3631 | -121.9655 | 0.002077 | 0.11441 | 0.1634 | 0.16517 | -122.0254
2252.3125 | 121.994 | -0.10986 | 121.9482 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064928 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.019827 | 0.02963 | 0.015859 | 0.019361 | 0.27154 | -0.054192 | 122.0387 | 121.9554 | 121.8687 | -0.058478 | 0.014784 | 0.078197 | -0.056351 | -0.080318 | 0.018285 | 0.053537 | -0.1092 | 0.051385 | 0.090452 | 0.12922 | 0.055671 | 0.004286 | 0.007193 | -0.079549 | 0.00066 | -122.0286 | 0.12465 | 0.053512 | 0.052852 | -121.93 | -121.8947 | 122.1486 | 122.0653 | 121.9786 | 0.38141 | -122.0067 | 0.029545 | 0.12815 | 0.1634 | 0.18806 | -122.0574
2254.0156 | 122.1085 | -0.091553 | 121.9254 | 1.4211e-13 | -0.041316 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019827 | 0.029416 | 0.015432 | 0.019361 | 0.2807 | -0.054192 | 122.0341 | 121.9509 | 121.8733 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.10462 | 0.037654 | 0.10876 | 0.11091 | 0.037361 | -0.000293 | 0.025502 | -0.052083 | -0.013071 | -122.0148 | 0.11549 | 0.030623 | 0.043694 | -121.9071 | -121.8672 | 122.1257 | 122.0424 | 121.9648 | 0.37225 | -121.9793 | 0.002078 | 0.10984 | 0.14967 | 0.16975 | -122.03
2255.7812 | 121.9894 | -0.11444 | 121.9528 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0095273 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.029416 | 0.015646 | 0.019361 | 0.27154 | -0.054192 | 122.0387 | 121.96 | 121.8687 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.067272 | -0.10004 | 0.060542 | 0.085874 | 0.1338 | 0.060249 | -0.000293 | 0.007194 | -0.084127 | 0.014396 | -122.0377 | 0.13838 | 0.053511 | 0.039115 | -121.9391 | -121.8855 | 122.1531 | 122.0745 | 121.9831 | 0.38599 | -122.0067 | 0.029545 | 0.12815 | 0.18171 | 0.18806 | -122.0529
2257.5312 | 121.9803 | -0.09613 | 121.9482 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064928 | -0.0095273 | 0.05311 | -0.01755 | -0.0046531 | -0.0014849 | 0.019827 | 0.02963 | 0.015859 | 0.019361 | 0.27154 | -0.054192 | 122.0433 | 121.9554 | 121.8687 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.10004 | 0.037652 | 0.09503 | 0.11549 | 0.041938 | 0.004286 | 0.007193 | -0.079549 | -0.003915 | -122.0286 | 0.12465 | 0.0352 | 0.039115 | -121.93 | -121.8901 | 122.1394 | 122.0516 | 121.9648 | 0.36767 | -122.0067 | 0.015812 | 0.11441 | 0.15424 | 0.17433 | -122.0483
2259.2969 | 121.9986 | -0.1236 | 121.9574 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064714 | -0.0093137 | 0.052897 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019827 | 0.02963 | 0.015646 | 0.023939 | 0.27612 | -0.063349 | 122.0387 | 121.9509 | 121.8687 | -0.063057 | 0.02852 | 0.078197 | -0.070087 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.060539 | 0.081297 | 0.14753 | 0.060247 | -0.000292 | -0.006541 | -0.088704 | 0.018972 | -122.0469 | 0.15212 | 0.053509 | 0.034537 | -121.9391 | -121.8947 | 122.1623 | 122.0745 | 121.9923 | 0.39972 | -122.0205 | 0.034121 | 0.14188 | 0.18629 | 0.20179 | -122.062
2261 | 122.1176 | -0.064087 | 121.9254 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.064714 | -0.0093137 | 0.053324 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019827 | 0.029844 | 0.015646 | 0.019361 | 0.26697 | -0.054192 | 122.0341 | 121.9509 | 121.8778 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.048958 | -0.10004 | 0.010188 | 0.10876 | 0.083448 | 0.009895 | -0.000293 | 0.025502 | -0.047504 | -0.035958 | -122.0148 | 0.088028 | 0.003157 | 0.039115 | -121.9116 | -121.8764 | 122.0982 | 122.0149 | 121.9419 | 0.33105 | -121.9793 | -0.025388 | 0.077794 | 0.11305 | 0.13771 | -122.0254
2262.7656 | 122.1085 | -0.07782 | 121.9025 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.064928 | -0.0090999 | 0.05311 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019613 | 0.02963 | 0.015646 | 0.023939 | 0.27612 | -0.049614 | 122.0341 | 121.9509 | 121.8733 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.028499 | 0.13165 | 0.10176 | 0.028206 | -0.000293 | 0.04839 | -0.029195 | -0.026804 | -121.9919 | 0.10634 | 0.01689 | 0.043694 | -121.8842 | -121.8398 | 122.1119 | 122.0287 | 121.9511 | 0.35394 | -121.9518 | -0.011655 | 0.096105 | 0.14051 | 0.15144 | -122.0071
2264.5312 | 122.0398 | -0.10529 | 121.9528 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064714 | -0.0095273 | 0.052897 | -0.01755 | -0.0044395 | -0.0012713 | 0.019613 | 0.029203 | 0.015859 | 0.010204 | 0.27612 | -0.05877 | 122.0387 | 121.9509 | 121.8733 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.094053 | 0.009128 | 0.053537 | -0.10462 | 0.051387 | 0.085874 | 0.11549 | 0.046516 | -0.004871 | -0.001964 | -0.079549 | 0.000662 | -122.0469 | 0.12923 | 0.048935 | 0.048273 | -121.9437 | -121.8993 | 122.144 | 122.0561 | 121.9786 | 0.38141 | -122.0067 | 0.011233 | 0.11441 | 0.15882 | 0.18348 | -122.0574
2266.25 | 122.113 | -0.086975 | 121.9482 | 1.4211e-13 | -0.041529 | 0.0020727 | 0.064714 | -0.0090999 | 0.052897 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019399 | 0.029844 | 0.016073 | 0.019361 | 0.2807 | -0.05877 | 122.0433 | 121.9554 | 121.8824 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.037654 | 0.09503 | 0.10634 | 0.028205 | -0.009449 | 0.007193 | -0.065814 | -0.017649 | -122.0286 | 0.11092 | 0.026045 | 0.043694 | -121.9254 | -121.8855 | 122.1302 | 122.0424 | 121.9694 | 0.36768 | -121.9976 | 0.006657 | 0.10984 | 0.14967 | 0.16975 | -122.0529
2268 | 122.1222 | -0.07782 | 121.9254 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064714 | -0.0088863 | 0.052683 | -0.01755 | -0.0046531 | -0.0014849 | 0.019827 | 0.029844 | 0.016073 | 0.010204 | 0.28528 | -0.054192 | 122.0433 | 121.9463 | 121.8733 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.023921 | 0.11792 | 0.088024 | 0.023628 | -0.000293 | 0.020923 | -0.052083 | -0.031383 | -122.0102 | 0.10176 | 0.01689 | 0.048273 | -121.9116 | -121.8672 | 122.1211 | 122.0241 | 121.9511 | 0.3631 | -121.9793 | -0.007076 | 0.091527 | 0.13594 | 0.15144 | -122.0346
2269.7656 | 122.0718 | -0.07782 | 121.9299 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064928 | -0.0088863 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015859 | 0.014783 | 0.2807 | -0.05877 | 122.0387 | 121.9554 | 121.8824 | -0.053899 | 0.023941 | 0.078197 | -0.070087 | -0.089475 | 0.013707 | 0.062694 | -0.11378 | 0.023921 | 0.10876 | 0.092603 | 0.01905 | -0.004871 | 0.025503 | -0.047504 | -0.035962 | -122.0194 | 0.10176 | 0.007733 | 0.043695 | -121.9162 | -121.8672 | 122.1165 | 122.0333 | 121.9602 | 0.35852 | -121.9838 | -0.011655 | 0.091527 | 0.14051 | 0.15602 | -122.0437
2271.4688 | 122.0306 | -0.10986 | 121.9757 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064928 | -0.0090999 | 0.05311 | -0.0022892 | -0.0040121 | -0.0012713 | 0.019827 | 0.029844 | 0.015859 | 0.019361 | 0.28528 | -0.054192 | 122.0387 | 121.9509 | 121.8778 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.013707 | 0.058115 | -0.1092 | 0.055964 | 0.062986 | 0.12922 | 0.055671 | -0.000293 | -0.024852 | -0.097858 | 0.00066 | -122.0652 | 0.1338 | 0.053512 | 0.052852 | -121.962 | -121.9176 | 122.1486 | 122.0607 | 121.9877 | 0.39514 | -122.0296 | 0.020388 | 0.12357 | 0.16798 | 0.18806 | -122.0849
2273.2344 | 121.9986 | -0.10986 | 121.9437 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064714 | -0.0090999 | 0.052683 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019613 | 0.029416 | 0.015859 | 0.019361 | 0.28528 | -0.054192 | 122.0433 | 121.96 | 121.8733 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.009128 | 0.058115 | -0.10462 | 0.060542 | 0.099607 | 0.12922 | 0.055671 | -0.004871 | 0.016349 | -0.070394 | 0.005239 | -122.0286 | 0.1338 | 0.044354 | 0.039115 | -121.9345 | -121.8855 | 122.1531 | 122.0699 | 121.9831 | 0.39514 | -121.993 | 0.024967 | 0.11899 | 0.16798 | 0.18806 | -122.0483
2274.9844 | 122.0123 | -0.1236 | 121.9437 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0088863 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.029844 | 0.015859 | 0.019361 | 0.2807 | -0.054192 | 122.0387 | 121.96 | 121.8778 | -0.053899 | 0.019362 | 0.078197 | -0.051772 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.069697 | 0.095029 | 0.14296 | 0.069404 | -0.000293 | 0.016349 | -0.065815 | 0.018972 | -122.0286 | 0.14296 | 0.071824 | 0.052852 | -121.9208 | -121.881 | 122.1623 | 122.0836 | 122.0014 | 0.4043 | -121.9976 | 0.0387 | 0.14646 | 0.18629 | 0.20179 | -122.0483
2276.75 | 122.1313 | -0.082397 | 121.9299 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064928 | -0.0088863 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015859 | 0.019361 | 0.28986 | -0.049614 | 122.0433 | 121.96 | 121.8778 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.023919 | 0.11334 | 0.10176 | 0.032783 | 0.008864 | 0.030082 | -0.052082 | -0.026806 | -122.0194 | 0.10634 | 0.021467 | 0.048273 | -121.9116 | -121.8718 | 122.1257 | 122.0424 | 121.9602 | 0.37226 | -121.9884 | -0.007078 | 0.10068 | 0.14051 | 0.16059 | -122.0391
2278.4531 | 122.1313 | -0.068665 | 121.9116 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064928 | -0.0090999 | 0.052897 | -0.01755 | -0.0040121 | -0.0014849 | 0.02004 | 0.029844 | 0.015859 | 0.019361 | 0.28528 | -0.045036 | 122.0341 | 121.9554 | 121.8778 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.11378 | 0.019344 | 0.12249 | 0.088026 | 0.023629 | 0.004285 | 0.043814 | -0.033771 | -0.045117 | -121.9919 | 0.097185 | 0.007735 | 0.052852 | -121.8933 | -121.8535 | 122.1028 | 122.0241 | 121.9465 | 0.35394 | -121.9609 | -0.011653 | 0.08695 | 0.12678 | 0.14228 | -122.0254
2280.2031 | 122.1085 | -0.068665 | 121.9162 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.064714 | -0.0093137 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019613 | 0.029844 | 0.015859 | 0.014783 | 0.28528 | -0.05877 | 122.0387 | 121.9554 | 121.8778 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.014766 | 0.1225 | 0.083448 | 0.009895 | -0.004871 | 0.039236 | -0.038349 | -0.035959 | -122.0011 | 0.092606 | 0.012314 | 0.048273 | -121.9025 | -121.8581 | 122.1074 | 122.0241 | 121.9465 | 0.35394 | -121.9701 | -0.016231 | 0.082372 | 0.12678 | 0.14228 | -122.0208
2281.9531 | 122.0718 | -0.073242 | 121.9116 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.029844 | 0.015432 | 0.019361 | 0.28528 | -0.054192 | 122.0341 | 121.96 | 121.8733 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.013707 | 0.053537 | -0.10462 | 0.019343 | 0.12249 | 0.092603 | 0.01905 | -0.000293 | 0.048393 | -0.03835 | -0.031382 | -121.9919 | 0.097183 | 0.016891 | 0.048273 | -121.8979 | -121.8581 | 122.1074 | 122.0333 | 121.9465 | 0.35852 | -121.9655 | -0.007076 | 0.086949 | 0.12678 | 0.14686 | -122.0162
2283.7188 | 122.0947 | -0.091553 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0020727 | 0.064714 | -0.0095273 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019827 | 0.029844 | 0.015432 | 0.023939 | 0.28528 | -0.05877 | 122.0433 | 121.96 | 121.8778 | -0.058478 | 0.033099 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.062694 | -0.10004 | 0.033075 | 0.10419 | 0.11549 | 0.032783 | -0.000292 | 0.020927 | -0.061237 | -0.008492 | -122.0194 | 0.12465 | 0.026044 | 0.034536 | -121.9254 | -121.8764 | 122.1348 | 122.0516 | 121.9694 | 0.37683 | -121.9976 | 0.011235 | 0.10526 | 0.15425 | 0.16517 | -122.0391
2285.4219 | 122.0673 | -0.086975 | 121.9208 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.065141 | -0.0090999 | 0.05311 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.016073 | 0.014783 | 0.28528 | -0.05877 | 122.0433 | 121.96 | 121.8778 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.10462 | 0.033076 | 0.1225 | 0.10176 | 0.028205 | -0.004871 | 0.039238 | -0.042926 | -0.017649 | -122.0011 | 0.11092 | 0.026045 | 0.043694 | -121.8979 | -121.8535 | 122.1302 | 122.047 | 121.9648 | 0.37226 | -121.9747 | 0.006657 | 0.10984 | 0.15425 | 0.16517 | -122.0254
2287.1719 | 122.0993 | -0.086975 | 121.9254 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0086727 | 0.05311 | -0.0099192 | -0.0044395 | -0.0019123 | 0.02004 | 0.029844 | 0.015646 | 0.019361 | 0.28986 | -0.049614 | 122.0387 | 121.96 | 121.8778 | -0.049321 | 0.033099 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.10004 | 0.037654 | 0.11334 | 0.10634 | 0.037361 | -0.000293 | 0.03466 | -0.047504 | -0.01307 | -122.0057 | 0.12007 | 0.026045 | 0.039115 | -121.9071 | -121.8627 | 122.1257 | 122.047 | 121.9648 | 0.37683 | -121.9747 | 0.006657 | 0.10526 | 0.14967 | 0.16517 | -122.0254
2288.9219 | 122.1405 | -0.068665 | 121.907 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064714 | -0.0088863 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015646 | 0.014783 | 0.2807 | -0.054192 | 122.0433 | 121.96 | 121.8733 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.023923 | 0.13623 | 0.083448 | 0.014473 | -0.00945 | 0.052971 | -0.033772 | -0.040538 | -121.9919 | 0.092606 | 0.007735 | 0.048273 | -121.8842 | -121.8443 | 122.1119 | 122.0287 | 121.9419 | 0.34937 | -121.9518 | -0.016231 | 0.091529 | 0.13136 | 0.14686 | -122.0162
2290.625 | 122.1176 | -0.091553 | 121.9391 | 1.4211e-13 | -0.041529 | 0.0018589 | 0.065141 | -0.0090999 | 0.053324 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015646 | 0.023939 | 0.28528 | -0.054192 | 122.0479 | 121.96 | 121.8778 | -0.053899 | 0.02852 | 0.078197 | -0.070087 | -0.080318 | 0.013707 | 0.058115 | -0.10462 | 0.037654 | 0.10876 | 0.11549 | 0.037361 | -0.000293 | 0.020927 | -0.061237 | -0.013071 | -122.0194 | 0.12007 | 0.021466 | 0.034537 | -121.9254 | -121.881 | 122.1394 | 122.0516 | 121.9694 | 0.37683 | -121.993 | 0.011235 | 0.10526 | 0.14967 | 0.16975 | -122.0437
2292.375 | 122.0901 | -0.091553 | 121.9528 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064928 | -0.0090999 | 0.052897 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019613 | 0.02963 | 0.015432 | 0.023939 | 0.28986 | -0.05877 | 122.0433 | 121.9646 | 121.8733 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.1092 | 0.042232 | 0.090452 | 0.11549 | 0.032783 | -0.009449 | 0.011773 | -0.079549 | -0.01765 | -122.0377 | 0.11549 | 0.030623 | 0.048273 | -121.9345 | -121.8993 | 122.1348 | 122.0561 | 121.9648 | 0.38141 | -122.0021 | 0.006657 | 0.10984 | 0.14509 | 0.16975 | -122.062
2294.1406 | 122.0352 | -0.10071 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.065141 | -0.0090999 | 0.052897 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019827 | 0.029844 | 0.015646 | 0.019361 | 0.28986 | -0.05877 | 122.0433 | 121.96 | 121.8778 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.051387 | 0.10419 | 0.12007 | 0.041938 | -0.009449 | 0.020927 | -0.061237 | -0.008495 | -122.024 | 0.12923 | 0.039778 | 0.048273 | -121.9254 | -121.881 | 122.144 | 122.0607 | 121.9786 | 0.39057 | -121.9884 | 0.015812 | 0.11442 | 0.15882 | 0.17891 | -122.0483
2295.9219 | 121.9803 | -0.10986 | 121.9757 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.064928 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.019827 | 0.029844 | 0.015646 | 0.014783 | 0.28986 | -0.054192 | 122.0433 | 121.9692 | 121.8824 | -0.049321 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.009128 | 0.067272 | -0.10462 | 0.060542 | 0.067564 | 0.12465 | 0.055671 | -0.004871 | -0.006536 | -0.09328 | 0.005239 | -122.056 | 0.12923 | 0.044354 | 0.039115 | -121.9666 | -121.9084 | 122.1531 | 122.079 | 121.9923 | 0.39972 | -122.025 | 0.029545 | 0.11899 | 0.17713 | 0.18806 | -122.0803
2297.6875 | 122.1222 | -0.068665 | 121.907 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064928 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.029844 | 0.015646 | 0.019361 | 0.29444 | -0.045036 | 122.0433 | 121.9646 | 121.8824 | -0.053899 | 0.02852 | 0.078197 | -0.056351 | -0.094053 | 0.013707 | 0.062694 | -0.10462 | 0.014766 | 0.13623 | 0.088026 | 0.023629 | 0.008863 | 0.05755 | -0.024615 | -0.035959 | -122.0011 | 0.097185 | 0.012314 | 0.048273 | -121.8933 | -121.8443 | 122.1119 | 122.0333 | 121.9511 | 0.3631 | -121.9609 | -0.025388 | 0.082372 | 0.13136 | 0.14686 | -122.0117
2299.3906 | 122.0764 | -0.10071 | 121.9574 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064714 | -0.0088863 | 0.05311 | -0.0099192 | -0.0037985 | -0.0010577 | 0.02004 | 0.029844 | 0.015646 | 0.014783 | 0.28986 | -0.054192 | 122.0433 | 121.96 | 121.8733 | -0.053899 | 0.02852 | 0.06904 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.046809 | 0.085875 | 0.11549 | 0.046516 | -0.000293 | 0.002617 | -0.084126 | -0.003916 | -122.0423 | 0.12923 | 0.035199 | 0.039115 | -121.9391 | -121.8947 | 122.144 | 122.0607 | 121.974 | 0.39057 | -122.0113 | 0.015812 | 0.11899 | 0.1634 | 0.16975 | -122.062
2301.1719 | 122.0627 | -0.073242 | 121.9299 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064714 | -0.0095273 | 0.05311 | -0.01755 | -0.0044395 | -0.0010577 | 0.02004 | 0.030057 | 0.016073 | 0.005626 | 0.29444 | -0.054192 | 122.0433 | 121.96 | 121.8824 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.014764 | 0.11334 | 0.078868 | 0.01905 | 0.004286 | 0.030082 | -0.047504 | -0.031382 | -122.0148 | 0.097183 | 0.012312 | 0.043694 | -121.9116 | -121.8672 | 122.1165 | 122.0333 | 121.9557 | 0.36768 | -121.9884 | -0.011654 | 0.091527 | 0.13594 | 0.14686 | -122.0346
2302.9375 | 122.0627 | -0.082397 | 121.9528 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064928 | -0.0093137 | 0.052897 | -0.01755 | -0.0042257 | -0.0019123 | 0.019827 | 0.02963 | 0.015646 | 0.019361 | 0.30359 | -0.054192 | 122.0433 | 121.96 | 121.8778 | -0.053899 | 0.023941 | 0.078197 | -0.051772 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.028498 | 0.090452 | 0.10176 | 0.028205 | -0.000293 | 0.007194 | -0.07497 | -0.022227 | -122.0423 | 0.10634 | 0.030625 | 0.052852 | -121.9391 | -121.8947 | 122.1257 | 122.0424 | 121.9602 | 0.38599 | -122.0067 | -0.007078 | 0.096104 | 0.14051 | 0.16059 | -122.0574
2304.7031 | 122.0123 | -0.09613 | 121.9574 | 1.4211e-13 | -0.041529 | 0.0014317 | 0.064714 | -0.0090999 | 0.05311 | -0.0022892 | -0.0044395 | -0.0019123 | 0.019827 | 0.030057 | 0.015646 | 0.014783 | 0.29444 | -0.054192 | 122.0433 | 121.9692 | 121.8778 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.013707 | 0.053537 | -0.1092 | 0.046809 | 0.085875 | 0.11091 | 0.041938 | -0.004871 | 0.011775 | -0.079547 | -0.013073 | -122.0331 | 0.12007 | 0.0352 | 0.048273 | -121.9437 | -121.9039 | 122.1394 | 122.0653 | 121.974 | 0.39057 | -122.0067 | 0.020391 | 0.10984 | 0.14967 | 0.17433 | -122.0666
2306.4844 | 122.0032 | -0.11444 | 121.9574 | 1.4211e-13 | -0.041743 | 0.0020727 | 0.064928 | -0.0093137 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.019613 | 0.030057 | 0.015646 | 0.019361 | 0.28986 | -0.049614 | 122.0387 | 121.96 | 121.8778 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.067272 | -0.10004 | 0.069699 | 0.081297 | 0.1338 | 0.064827 | -0.004872 | 0.002617 | -0.079547 | 0.014396 | -122.0423 | 0.13838 | 0.053511 | 0.039115 | -121.9345 | -121.8901 | 122.1531 | 122.0745 | 121.9923 | 0.4043 | -122.0021 | 0.029545 | 0.13731 | 0.18171 | 0.19264 | -122.0574
2308.25 | 122.081 | -0.086975 | 121.9254 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0088863 | 0.052683 | -0.01755 | -0.0044395 | -0.0012713 | 0.019827 | 0.029844 | 0.015646 | 0.019361 | 0.29444 | -0.054192 | 122.0479 | 121.96 | 121.8778 | -0.053899 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.013707 | 0.053537 | -0.10462 | 0.033076 | 0.1225 | 0.10634 | 0.032783 | -0.000293 | 0.03466 | -0.047504 | -0.017649 | -122.0057 | 0.11092 | 0.026045 | 0.043694 | -121.9116 | -121.8718 | 122.1348 | 122.047 | 121.9648 | 0.38141 | -121.9793 | 0.006657 | 0.10068 | 0.14051 | 0.15602 | -122.03
2310 | 122.0306 | -0.10071 | 121.9757 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0093137 | 0.05311 | 0.0053413 | -0.0042257 | -0.0016987 | 0.019827 | 0.029844 | 0.015646 | 0.019361 | 0.28986 | -0.05877 | 122.0433 | 121.9692 | 121.8824 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.10462 | 0.046809 | 0.067564 | 0.12007 | 0.041938 | -0.004871 | -0.006536 | -0.09328 | -0.003916 | -122.0606 | 0.12923 | 0.039778 | 0.043694 | -121.9574 | -121.9176 | 122.144 | 122.0699 | 121.9831 | 0.39057 | -122.0296 | 0.015812 | 0.11899 | 0.15882 | 0.17891 | -122.0803
2311.7031 | 122.1497 | -0.064087 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.065141 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.02963 | 0.015859 | 0.023939 | 0.29902 | -0.049614 | 122.0387 | 121.96 | 121.8778 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.10462 | 0.010188 | 0.099607 | 0.088026 | 0.014473 | 0.004285 | 0.020927 | -0.061237 | -0.040537 | -122.0286 | 0.088028 | 0.003157 | 0.043694 | -121.9162 | -121.881 | 122.1028 | 122.0241 | 121.9419 | 0.3631 | -121.993 | -0.025388 | 0.086951 | 0.1222 | 0.14228 | -122.0437
2313.4531 | 122.1313 | -0.064087 | 121.9666 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064928 | -0.0088863 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019827 | 0.030057 | 0.016073 | 0.019361 | 0.29902 | -0.054192 | 122.0433 | 121.9692 | 121.8824 | -0.049321 | 0.023941 | 0.06904 | -0.056351 | -0.080318 | 0.018285 | 0.053537 | -0.10004 | 0.014766 | 0.076719 | 0.083448 | 0.009895 | -0.004871 | 0.002619 | -0.084125 | -0.035958 | -122.0469 | 0.088028 | 0.007736 | 0.043694 | -121.9483 | -121.913 | 122.1074 | 122.0333 | 121.9465 | 0.3631 | -122.0159 | -0.016231 | 0.082372 | 0.11762 | 0.13313 | -122.0666
2315.1406 | 121.9849 | -0.10529 | 121.9711 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019613 | 0.029844 | 0.015859 | 0.023939 | 0.29444 | -0.049614 | 122.057 | 121.9646 | 121.8916 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.11378 | 0.051387 | 0.085877 | 0.12923 | 0.055672 | 0.004285 | -0.006537 | -0.079544 | -0.008496 | -122.056 | 0.12923 | 0.039777 | 0.048273 | -121.9574 | -121.913 | 122.1623 | 122.0699 | 121.9969 | 0.39972 | -122.025 | 0.02039 | 0.11899 | 0.1634 | 0.1789 | -122.0849
2316.9062 | 122.0078 | -0.11444 | 121.9666 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.0645 | -0.0093137 | 0.05311 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019827 | 0.029416 | 0.016073 | 0.019361 | 0.29902 | -0.054192 | 122.0433 | 121.9646 | 121.8824 | -0.044742 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.10004 | 0.069699 | 0.076719 | 0.1338 | 0.060249 | -0.00945 | -0.00196 | -0.084125 | 0.014396 | -122.0514 | 0.13838 | 0.053511 | 0.039115 | -121.9483 | -121.913 | 122.1577 | 122.079 | 121.9969 | 0.41346 | -122.0113 | 0.029545 | 0.13273 | 0.16798 | 0.18806 | -122.0666
2318.6719 | 122.0398 | -0.09613 | 121.9528 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.065355 | -0.0097409 | 0.05311 | -0.0022892 | -0.0044395 | -0.0019123 | 0.019613 | 0.030271 | 0.015859 | 0.014783 | 0.29902 | -0.049614 | 122.0479 | 121.9692 | 121.887 | -0.049321 | 0.023941 | 0.087354 | -0.065509 | -0.084896 | 0.018285 | 0.053537 | -0.10462 | 0.046809 | 0.095031 | 0.11091 | 0.046516 | -0.000293 | 0.016352 | -0.065813 | -0.008494 | -122.0377 | 0.12007 | 0.030621 | 0.039115 | -121.9345 | -121.8993 | 122.144 | 122.0653 | 121.9831 | 0.39515 | -122.0021 | 0.011234 | 0.11441 | 0.14967 | 0.18348 | -122.0574
2320.3594 | 121.9849 | -0.11444 | 121.9803 | 1.4211e-13 | -0.041529 | 0.0014317 | 0.064928 | -0.0090999 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015646 | 0.014783 | 0.29902 | -0.054192 | 122.0479 | 121.9646 | 121.8824 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.10462 | 0.060542 | 0.067565 | 0.12922 | 0.060249 | -0.000293 | -0.015693 | -0.097858 | 0.009817 | -122.0606 | 0.13838 | 0.053511 | 0.043694 | -121.9666 | -121.9176 | 122.1623 | 122.079 | 121.9969 | 0.41346 | -122.0342 | 0.034123 | 0.12815 | 0.17713 | 0.19722 | -122.0849
2322.1094 | 122.0856 | -0.091553 | 121.9116 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | 0.012972 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015859 | 0.023939 | 0.30359 | -0.054192 | 122.0524 | 121.9692 | 121.8824 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.10462 | 0.042232 | 0.14081 | 0.11549 | 0.037361 | -0.004871 | 0.057551 | -0.029193 | -0.013071 | -121.9919 | 0.12007 | 0.030623 | 0.043694 | -121.8979 | -121.8489 | 122.144 | 122.0607 | 121.974 | 0.39515 | -121.9609 | 0.011235 | 0.10526 | 0.15425 | 0.16517 | -122.0162
2323.7969 | 122.0947 | -0.054932 | 121.9116 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064928 | -0.0090999 | 0.053324 | -0.01755 | -0.0046531 | -0.0014849 | 0.019613 | 0.030057 | 0.015646 | 0.019361 | 0.29902 | -0.05877 | 122.0433 | 121.9646 | 121.887 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.10462 | -0.003546 | 0.13165 | 0.074293 | -0.003838 | -0.000292 | 0.052972 | -0.024614 | -0.049692 | -122.0011 | 0.078873 | -0.005998 | 0.043694 | -121.8933 | -121.8535 | 122.0982 | 122.0195 | 121.9419 | 0.35395 | -121.9701 | -0.034543 | 0.073217 | 0.11305 | 0.13313 | -122.0162
2325.5625 | 122.1222 | -0.07782 | 121.9208 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.065141 | -0.0093137 | 0.053538 | -0.0022892 | -0.0044395 | -0.0016987 | 0.02004 | 0.030057 | 0.015646 | 0.019361 | 0.29902 | -0.054192 | 122.0433 | 121.9692 | 121.8824 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.094053 | 0.013707 | 0.062694 | -0.12294 | 0.023921 | 0.1225 | 0.097181 | 0.023628 | -0.000293 | 0.048396 | -0.038348 | -0.045119 | -122.0148 | 0.097182 | 0.01689 | 0.062009 | -121.9071 | -121.8581 | 122.1211 | 122.047 | 121.9602 | 0.37684 | -121.9747 | -0.016233 | 0.091527 | 0.14051 | 0.15602 | -122.0437
2327.3281 | 122.0169 | -0.12817 | 121.9482 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064928 | -0.0093137 | 0.05311 | 0.0053413 | -0.0044395 | -0.0016987 | 0.019613 | 0.02963 | 0.015432 | 0.028518 | 0.30359 | -0.054192 | 122.0433 | 121.9646 | 121.887 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.094053 | 0.022864 | 0.053537 | -0.1092 | 0.078853 | 0.09503 | 0.15669 | 0.073982 | -0.004871 | 0.016351 | -0.061235 | 0.018971 | -122.0423 | 0.15212 | 0.062665 | 0.043694 | -121.9254 | -121.8947 | 122.1714 | 122.0928 | 122.0152 | 0.43177 | -121.9976 | 0.034121 | 0.15104 | 0.18171 | 0.21095 | -122.0574
2329.0938 | 122.0901 | -0.086975 | 121.9345 | 1.4211e-13 | -0.041743 | 0.0012179 | 0.064928 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015432 | 0.019361 | 0.30359 | -0.054192 | 122.0479 | 121.9646 | 121.8824 | -0.053899 | 0.014784 | 0.06904 | -0.065509 | -0.075739 | 0.013707 | 0.062694 | -0.10004 | 0.033076 | 0.11334 | 0.10634 | 0.032783 | -0.000293 | 0.030084 | -0.052081 | -0.01307 | -122.0102 | 0.10176 | 0.021466 | 0.034536 | -121.9208 | -121.8718 | 122.1348 | 122.0516 | 121.9694 | 0.39057 | -121.9884 | 0.011236 | 0.10068 | 0.14967 | 0.15602 | -122.0346
2330.7969 | 122.0306 | -0.13275 | 121.9437 | 1.4211e-13 | -0.041957 | 0.0012179 | 0.064928 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.030057 | 0.015646 | 0.023939 | 0.29902 | -0.054192 | 122.0524 | 121.9646 | 121.8824 | -0.058478 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.074273 | 0.10876 | 0.15669 | 0.078559 | 0.004286 | 0.020928 | -0.061237 | 0.023548 | -122.0286 | 0.16127 | 0.067242 | 0.043694 | -121.9208 | -121.881 | 122.1852 | 122.0973 | 122.0152 | 0.43177 | -122.0021 | 0.047855 | 0.15562 | 0.19545 | 0.20637 | -122.0529
2332.5625 | 122.1497 | -0.073242 | 121.9299 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0090999 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.029844 | 0.015646 | 0.014783 | 0.30359 | -0.05877 | 122.0479 | 121.9692 | 121.8824 | -0.044742 | 0.023941 | 0.073618 | -0.051772 | -0.094053 | 0.013707 | 0.053537 | -0.1092 | 0.0285 | 0.11792 | 0.088025 | 0.014472 | -0.014028 | 0.03924 | -0.047504 | -0.035961 | -122.024 | 0.097183 | 0.02147 | 0.057431 | -121.9162 | -121.8764 | 122.1211 | 122.0424 | 121.9557 | 0.37684 | -121.9747 | -0.020811 | 0.086949 | 0.12678 | 0.14686 | -122.0391
2334.2656 | 122.0398 | -0.10071 | 121.9299 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064714 | -0.0090999 | 0.052897 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019613 | 0.029844 | 0.015646 | 0.014783 | 0.30817 | -0.045036 | 122.0479 | 121.9646 | 121.887 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.11378 | 0.046809 | 0.11792 | 0.11549 | 0.055672 | 0.008863 | 0.034661 | -0.042925 | -0.013074 | -122.0194 | 0.12007 | 0.039778 | 0.052852 | -121.9162 | -121.8718 | 122.1486 | 122.0653 | 121.9877 | 0.40888 | -121.9838 | 0.011233 | 0.11442 | 0.15882 | 0.17891 | -122.0437
2336.0469 | 121.994 | -0.12817 | 121.9803 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.065141 | -0.0088863 | 0.052897 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019613 | 0.029844 | 0.015646 | 0.014783 | 0.30817 | -0.054192 | 122.0433 | 121.9646 | 121.8824 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.094053 | 0.018285 | 0.067272 | -0.11378 | 0.078853 | 0.062986 | 0.14296 | 0.073982 | -0.004871 | -0.015693 | -0.097858 | 0.014392 | -122.0743 | 0.15212 | 0.067244 | 0.052852 | -121.962 | -121.913 | 122.1714 | 122.0928 | 122.0106 | 0.43635 | -122.0296 | 0.034121 | 0.14646 | 0.19545 | 0.20179 | -122.0941
2337.8125 | 122.0032 | -0.1236 | 121.9528 | 1.4211e-13 | -0.041743 | 0.0016453 | 0.064714 | -0.0093137 | 0.053324 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.029844 | 0.015646 | 0.019361 | 0.30359 | -0.054192 | 122.0433 | 121.9692 | 121.887 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.065118 | 0.090452 | 0.14296 | 0.069404 | 0.004286 | 0.016352 | -0.065813 | 0.018972 | -122.0377 | 0.14754 | 0.058087 | 0.039115 | -121.93 | -121.8901 | 122.1669 | 122.0928 | 122.0106 | 0.42719 | -122.0113 | 0.0387 | 0.14646 | 0.18629 | 0.20179 | -122.0574
2339.5 | 122.1222 | -0.068665 | 121.9574 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.064928 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015646 | 0.014783 | 0.31275 | -0.049614 | 122.0524 | 121.9646 | 121.8778 | -0.058478 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.010187 | 0.095032 | 0.083448 | 0.019051 | 0.008864 | 0.007196 | -0.079547 | -0.035959 | -122.0423 | 0.097185 | 0.007735 | 0.043694 | -121.9437 | -121.8993 | 122.1211 | 122.0333 | 121.9465 | 0.38142 | -122.0159 | -0.016231 | 0.082372 | 0.12678 | 0.13771 | -122.062
2341.2812 | 122.0169 | -0.1236 | 121.9711 | 1.4211e-13 | -0.041743 | 0.0018589 | 0.064928 | -0.0095273 | 0.053538 | 0.0053413 | -0.0040121 | -0.0016987 | 0.019827 | 0.029844 | 0.016073 | 0.019361 | 0.30817 | -0.054192 | 122.0433 | 121.9646 | 121.8916 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.074275 | 0.072142 | 0.14296 | 0.069404 | -0.004871 | -0.006537 | -0.079544 | 0.014393 | -122.0514 | 0.14754 | 0.067245 | 0.052852 | -121.9437 | -121.9084 | 122.1669 | 122.0882 | 122.0152 | 0.43177 | -122.0205 | 0.043278 | 0.15104 | 0.18629 | 0.20179 | -122.0803
2342.9844 | 122.1176 | -0.073242 | 121.9437 | 1.4211e-13 | -0.041529 | 0.0016453 | 0.064714 | -0.0095273 | 0.05311 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019613 | 0.030057 | 0.015432 | 0.023939 | 0.30817 | -0.054192 | 122.0479 | 121.9646 | 121.8778 | -0.049321 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.023921 | 0.10419 | 0.097181 | 0.01905 | -0.004871 | 0.020928 | -0.065815 | -0.031382 | -122.0286 | 0.10176 | 0.012312 | 0.043694 | -121.93 | -121.881 | 122.1211 | 122.0378 | 121.9511 | 0.38141 | -121.993 | -0.011654 | 0.086949 | 0.13594 | 0.14228 | -122.0483
2344.7344 | 122.1176 | -0.07782 | 121.9345 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.064928 | -0.0093137 | 0.05311 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019613 | 0.030271 | 0.015859 | 0.014783 | 0.30817 | -0.05877 | 122.0479 | 121.9738 | 121.887 | -0.058478 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.027442 | 0.053537 | -0.1092 | 0.019342 | 0.11334 | 0.092603 | 0.01905 | -0.000292 | 0.039242 | -0.047502 | -0.031383 | -122.0194 | 0.10176 | 0.012311 | 0.043694 | -121.9071 | -121.881 | 122.1257 | 122.0516 | 121.9648 | 0.38599 | -121.993 | -0.007076 | 0.10526 | 0.13136 | 0.15144 | -122.0437
2346.5 | 122.1176 | -0.073242 | 121.9299 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.065141 | -0.0088863 | 0.053538 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015432 | 0.019361 | 0.30359 | -0.054192 | 122.0479 | 121.96 | 121.887 | -0.058478 | 0.02852 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.014764 | 0.11792 | 0.092603 | 0.01905 | 0.004286 | 0.030082 | -0.042925 | -0.035961 | -122.0148 | 0.10176 | 0.012312 | 0.048273 | -121.9071 | -121.8672 | 122.1211 | 122.0333 | 121.9602 | 0.37684 | -121.9884 | -0.011654 | 0.096106 | 0.13594 | 0.14228 | -122.0391
2348.1875 | 122.0032 | -0.10986 | 121.994 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065141 | -0.0090999 | 0.053538 | -0.01755 | -0.0044395 | -0.0016987 | 0.019613 | 0.029844 | 0.015432 | 0.014783 | 0.31733 | -0.063349 | 122.0524 | 121.9646 | 121.887 | -0.053899 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.009128 | 0.067272 | -0.10462 | 0.055964 | 0.05841 | 0.12465 | 0.046514 | -0.00945 | -0.029426 | -0.10701 | 0.005239 | -122.0789 | 0.1338 | 0.039776 | 0.034537 | -121.9849 | -121.9267 | 122.1623 | 122.0745 | 121.9969 | 0.42719 | -122.0479 | 0.024967 | 0.11899 | 0.17713 | 0.18806 | -122.0986
2349.9375 | 122.1222 | -0.068665 | 121.962 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.065355 | -0.0095273 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015859 | 0.019361 | 0.31275 | -0.049614 | 122.0433 | 121.9692 | 121.8916 | -0.058478 | 0.02852 | 0.06904 | -0.065509 | -0.080318 | 0.022864 | 0.053537 | -0.10004 | 0.010187 | 0.081297 | 0.088026 | 0.019051 | 0.008864 | 0.007197 | -0.070389 | -0.03138 | -122.0423 | 0.097185 | 0.003156 | 0.034536 | -121.9391 | -121.9084 | 122.1119 | 122.0378 | 121.9603 | 0.38142 | -122.0205 | -0.011653 | 0.091529 | 0.1222 | 0.13771 | -122.062
2351.7031 | 121.9986 | -0.10986 | 121.9849 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.065141 | -0.0088863 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019399 | 0.029844 | 0.015646 | 0.019361 | 0.30817 | -0.049614 | 122.057 | 121.9692 | 121.8916 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.094053 | 0.013707 | 0.062694 | -0.1092 | 0.060542 | 0.072144 | 0.12922 | 0.060249 | -0.000293 | -0.015691 | -0.093277 | 0.00066 | -122.0789 | 0.1338 | 0.048933 | 0.048273 | -121.9712 | -121.9222 | 122.1669 | 122.079 | 122.0014 | 0.41804 | -122.0342 | 0.01581 | 0.12357 | 0.17256 | 0.18806 | -122.0941
2353.4062 | 122.1313 | -0.054932 | 121.9299 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.065141 | -0.0090999 | 0.053324 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019613 | 0.030057 | 0.015646 | 0.014783 | 0.31275 | -0.049614 | 122.0479 | 121.9692 | 121.8916 | -0.053899 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.001033 | 0.11792 | 0.069715 | 0.005318 | 0.004285 | 0.03924 | -0.038346 | -0.054271 | -122.0148 | 0.078873 | -0.015155 | 0.039116 | -121.9116 | -121.8718 | 122.1028 | 122.0241 | 121.9465 | 0.36768 | -121.9838 | -0.029964 | 0.073217 | 0.11305 | 0.13313 | -122.0391
2355.1719 | 122.081 | -0.09613 | 121.9482 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.065355 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.02004 | 0.029844 | 0.015646 | 0.014783 | 0.31733 | -0.054192 | 122.0524 | 121.9692 | 121.887 | -0.058478 | 0.02852 | 0.078197 | -0.056351 | -0.084896 | 0.018285 | 0.058115 | -0.10004 | 0.037652 | 0.10419 | 0.11091 | 0.041938 | 0.004286 | 0.02093 | -0.061235 | -0.003915 | -122.0331 | 0.12465 | 0.039779 | 0.043694 | -121.93 | -121.8901 | 122.1486 | 122.0653 | 121.9831 | 0.41346 | -122.0067 | 0.011234 | 0.11441 | 0.15424 | 0.17433 | -122.0483
2356.9375 | 121.9986 | -0.1236 | 121.9666 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.065141 | -0.0088863 | 0.053538 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015859 | 0.014783 | 0.31275 | -0.05877 | 122.0479 | 121.9692 | 121.8962 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.065118 | 0.081298 | 0.13838 | 0.064826 | -0.000292 | 0.002619 | -0.070389 | 0.014393 | -122.0514 | 0.15212 | 0.062666 | 0.048273 | -121.9391 | -121.9039 | 122.1714 | 122.0928 | 122.0198 | 0.43635 | -122.025 | 0.0387 | 0.15104 | 0.18629 | 0.20179 | -122.0758
2358.6406 | 122.0078 | -0.1236 | 121.9711 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064928 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.029844 | 0.015432 | 0.023939 | 0.32191 | -0.054192 | 122.0479 | 121.9692 | 121.8916 | -0.053899 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.069697 | 0.076721 | 0.14753 | 0.069404 | -0.000293 | -0.001958 | -0.079544 | 0.018972 | -122.0514 | 0.15212 | 0.058087 | 0.039115 | -121.9528 | -121.913 | 122.1714 | 122.0928 | 122.0152 | 0.4455 | -122.025 | 0.043278 | 0.14188 | 0.18171 | 0.20179 | -122.0758
2360.4062 | 122.0215 | -0.11902 | 121.9757 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.019827 | 0.029844 | 0.015432 | 0.014783 | 0.31275 | -0.049614 | 122.0387 | 121.9692 | 121.8916 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.094053 | 0.018285 | 0.062694 | -0.1092 | 0.06512 | 0.062986 | 0.1338 | 0.069405 | 0.004285 | -0.006536 | -0.084122 | 0.009816 | -122.0698 | 0.14296 | 0.058089 | 0.048273 | -121.9574 | -121.913 | 122.1577 | 122.0882 | 122.0106 | 0.43177 | -122.0296 | 0.024966 | 0.1373 | 0.18171 | 0.2018 | -122.0849
2362.1719 | 122.0444 | -0.12817 | 121.9574 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065141 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019613 | 0.029844 | 0.015646 | 0.014783 | 0.31275 | -0.049614 | 122.0479 | 121.9738 | 121.8916 | -0.058478 | 0.033099 | 0.073618 | -0.065509 | -0.089475 | 0.018285 | 0.067272 | -0.10462 | 0.069696 | 0.090454 | 0.14296 | 0.07856 | 0.008864 | 0.016354 | -0.065811 | 0.02355 | -122.0469 | 0.16127 | 0.062665 | 0.039115 | -121.9391 | -121.8901 | 122.176 | 122.1019 | 122.0198 | 0.44093 | -122.0159 | 0.038699 | 0.14646 | 0.19545 | 0.20179 | -122.062
2363.9375 | 121.9894 | -0.10986 | 121.9711 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064928 | -0.0090999 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015646 | 0.019361 | 0.31733 | -0.049614 | 122.057 | 121.9738 | 121.8916 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.075739 | 0.022864 | 0.062694 | -0.10462 | 0.055964 | 0.085877 | 0.12922 | 0.060249 | 0.004285 | 0.002621 | -0.079544 | 0.005239 | -122.0469 | 0.1338 | 0.044354 | 0.039115 | -121.9483 | -121.9084 | 122.1669 | 122.0836 | 122.0014 | 0.42719 | -122.025 | 0.034124 | 0.13273 | 0.17256 | 0.18348 | -122.0758
2365.6406 | 122.1542 | -0.068665 | 121.9574 | 1.4211e-13 | -0.041316 | 0.0018589 | 0.064714 | -0.0088863 | 0.052897 | -0.0022892 | -0.0044395 | -0.0012713 | 0.02004 | 0.02963 | 0.015432 | 0.019361 | 0.32191 | -0.049614 | 122.0524 | 121.9692 | 121.8916 | -0.053899 | 0.019362 | 0.06904 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.014766 | 0.095032 | 0.088026 | 0.019051 | 0.004285 | 0.011775 | -0.065811 | -0.035959 | -122.0423 | 0.088027 | 0.007735 | 0.043694 | -121.93 | -121.8947 | 122.1211 | 122.0378 | 121.9603 | 0.39057 | -122.0113 | -0.016231 | 0.096107 | 0.13136 | 0.13771 | -122.062
2367.3906 | 122.1268 | -0.086975 | 121.9299 | 1.4211e-13 | -0.041957 | 0.0016453 | 0.064714 | -0.0093137 | 0.053538 | -0.01755 | -0.0042257 | -0.0014849 | 0.019827 | 0.030057 | 0.015646 | 0.014783 | 0.32191 | -0.063349 | 122.0479 | 121.9692 | 121.887 | -0.058478 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.028497 | 0.11792 | 0.10176 | 0.023626 | -0.004871 | 0.03924 | -0.042925 | -0.022228 | -122.0148 | 0.11092 | 0.021466 | 0.043694 | -121.9071 | -121.8672 | 122.1348 | 122.0561 | 121.974 | 0.40888 | -121.9884 | 0.002079 | 0.10984 | 0.14967 | 0.16059 | -122.0391
2369.1406 | 122.0078 | -0.1236 | 121.9803 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065141 | -0.0093137 | 0.053324 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019827 | 0.029844 | 0.015859 | 0.023939 | 0.31733 | -0.054192 | 122.0479 | 121.9738 | 121.8916 | -0.049321 | 0.02852 | 0.06904 | -0.065509 | -0.089475 | 0.018285 | 0.058115 | -0.10004 | 0.074275 | 0.067565 | 0.14753 | 0.069404 | -0.004871 | -0.006535 | -0.0887 | 0.023551 | -122.0698 | 0.15212 | 0.058087 | 0.034536 | -121.962 | -121.9222 | 122.1714 | 122.0973 | 122.0152 | 0.44093 | -122.0296 | 0.034121 | 0.14188 | 0.18171 | 0.19264 | -122.0803
2370.8438 | 122.1451 | -0.064087 | 121.9254 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.064714 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0019123 | 0.019613 | 0.030057 | 0.015859 | 0.019361 | 0.32191 | -0.049614 | 122.0479 | 121.9783 | 121.8962 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.014766 | 0.1225 | 0.083448 | 0.014473 | -0.000293 | 0.052976 | -0.02919 | -0.040537 | -122.0057 | 0.088028 | 0.003157 | 0.043694 | -121.9071 | -121.8672 | 122.1119 | 122.0424 | 121.9603 | 0.386 | -121.9747 | -0.016231 | 0.082372 | 0.1222 | 0.14228 | -122.03
2372.6094 | 122.1085 | -0.07782 | 121.9116 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064928 | -0.0093137 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.030057 | 0.015646 | 0.019361 | 0.31733 | -0.054192 | 122.0524 | 121.9738 | 121.8962 | -0.053899 | 0.02852 | 0.064461 | -0.06093 | -0.094053 | 0.018285 | 0.062694 | -0.10462 | 0.023921 | 0.14081 | 0.097181 | 0.023628 | -0.000293 | 0.06213 | -0.015457 | -0.026804 | -122.0057 | 0.10634 | 0.01689 | 0.043694 | -121.8933 | -121.8489 | 122.1302 | 122.0516 | 121.974 | 0.39515 | -121.9655 | -0.016233 | 0.096105 | 0.14051 | 0.14228 | -122.0162
2374.3125 | 121.9803 | -0.1236 | 121.9757 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065141 | -0.0095273 | 0.05311 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019827 | 0.030057 | 0.015646 | 0.014783 | 0.32191 | -0.054192 | 122.0524 | 121.9783 | 121.8916 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.10462 | 0.069697 | 0.076721 | 0.13838 | 0.069404 | -0.000293 | 0.002622 | -0.084122 | 0.018972 | -122.056 | 0.15212 | 0.058087 | 0.039115 | -121.962 | -121.9176 | 122.176 | 122.1019 | 122.0152 | 0.4455 | -122.0296 | 0.043278 | 0.1373 | 0.18171 | 0.19721 | -122.0803
2376.0781 | 121.9986 | -0.11902 | 121.9574 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064928 | -0.0095273 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.030057 | 0.015646 | 0.019361 | 0.32191 | -0.049614 | 122.0524 | 121.9692 | 121.8916 | -0.058478 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.060541 | 0.095032 | 0.13838 | 0.069405 | 0.008864 | 0.011775 | -0.065811 | 0.009816 | -122.0423 | 0.13838 | 0.058089 | 0.048273 | -121.9345 | -121.8947 | 122.1714 | 122.0882 | 122.0106 | 0.44093 | -122.0159 | 0.034123 | 0.14188 | 0.18171 | 0.19264 | -122.0666
2377.8438 | 122.0901 | -0.064087 | 121.9574 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.065569 | -0.0095273 | 0.052897 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019399 | 0.030271 | 0.015646 | 0.019361 | 0.32649 | -0.054192 | 122.0479 | 121.9783 | 121.8916 | -0.058478 | 0.033099 | 0.078197 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.1092 | 0.005609 | 0.090454 | 0.083448 | 0.009895 | 0.004286 | 0.020933 | -0.065811 | -0.045116 | -122.0423 | 0.097186 | -0.001422 | 0.043694 | -121.9391 | -121.8947 | 122.1119 | 122.0424 | 121.9557 | 0.39057 | -122.0159 | -0.020809 | 0.082372 | 0.12678 | 0.14228 | -122.0666
2379.5312 | 122.0352 | -0.10986 | 121.9437 | 1.4211e-13 | -0.041957 | 0.0018589 | 0.064928 | -0.0093137 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.02963 | 0.015646 | 0.023939 | 0.32649 | -0.054192 | 122.0524 | 121.9783 | 121.8916 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.051385 | 0.10876 | 0.1338 | 0.055671 | 0.004286 | 0.034665 | -0.052079 | 0.00066 | -122.0331 | 0.1338 | 0.048933 | 0.048273 | -121.9254 | -121.8855 | 122.1623 | 122.0882 | 122.0014 | 0.43635 | -122.0021 | 0.020388 | 0.12815 | 0.16798 | 0.18348 | -122.0529
2381.2969 | 122.1359 | -0.059509 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.065355 | -0.0097409 | 0.053324 | -0.01755 | -0.0044395 | -0.0016987 | 0.019613 | 0.030057 | 0.015859 | 0.019361 | 0.33107 | -0.045036 | 122.0524 | 121.9783 | 121.8962 | -0.063057 | 0.019362 | 0.073618 | -0.056351 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | -0.003548 | 0.11334 | 0.07887 | 0.014473 | 0.018021 | 0.039243 | -0.042923 | -0.045115 | -122.024 | 0.078871 | 0.003158 | 0.048273 | -121.9208 | -121.8764 | 122.1119 | 122.0378 | 121.9557 | 0.39058 | -122.0021 | -0.025387 | 0.077794 | 0.1222 | 0.13313 | -122.0437
2383 | 122.0352 | -0.10529 | 121.9482 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.065141 | -0.0093137 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019827 | 0.02963 | 0.015646 | 0.023939 | 0.33107 | -0.049614 | 122.0479 | 121.9783 | 121.8916 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.009128 | 0.058115 | -0.10004 | 0.051387 | 0.099609 | 0.12923 | 0.055672 | 0.004285 | 0.030088 | -0.056656 | 0.005241 | -122.0331 | 0.13381 | 0.039777 | 0.034536 | -121.9391 | -121.8901 | 122.1531 | 122.0836 | 121.9969 | 0.43635 | -122.0021 | 0.02039 | 0.11441 | 0.1634 | 0.1789 | -122.0483
2384.75 | 122.0947 | -0.073242 | 121.9437 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.065141 | -0.0093137 | 0.05311 | 0.0053413 | -0.0044395 | -0.0019123 | 0.019399 | 0.030057 | 0.016073 | 0.014783 | 0.33107 | -0.054192 | 122.0524 | 121.9738 | 121.9007 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.10004 | 0.019343 | 0.10876 | 0.088025 | 0.01905 | -0.000293 | 0.030086 | -0.042922 | -0.026803 | -122.024 | 0.097183 | 0.012312 | 0.039115 | -121.9254 | -121.8855 | 122.1257 | 122.047 | 121.974 | 0.40431 | -121.9976 | -0.007076 | 0.091527 | 0.13136 | 0.14686 | -122.0437
2386.5 | 122.0078 | -0.11902 | 121.9574 | 1.4211e-13 | -0.041957 | 0.0014317 | 0.065141 | -0.0095273 | 0.053324 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019827 | 0.030057 | 0.015432 | 0.019361 | 0.33565 | -0.054192 | 122.0524 | 121.9783 | 121.9007 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.10462 | 0.06512 | 0.095032 | 0.13838 | 0.064827 | -0.000293 | 0.020933 | -0.056654 | 0.014395 | -122.0469 | 0.14296 | 0.058089 | 0.043694 | -121.9345 | -121.8993 | 122.1714 | 122.0973 | 122.0198 | 0.45466 | -122.0113 | 0.029544 | 0.14188 | 0.17713 | 0.19264 | -122.062
2388.2656 | 122.0078 | -0.11444 | 121.994 | 1.4211e-13 | -0.041743 | 0.0014317 | 0.065355 | -0.0095273 | 0.053324 | -0.01755 | -0.0044395 | -0.0014849 | 0.019613 | 0.029844 | 0.015432 | 0.023939 | 0.33565 | -0.049614 | 122.057 | 121.9829 | 121.8962 | -0.063057 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.053537 | -0.10462 | 0.051384 | 0.062988 | 0.13838 | 0.064827 | 0.013443 | -0.01111 | -0.097855 | 0.009817 | -122.0789 | 0.13838 | 0.048932 | 0.039115 | -121.9712 | -121.9405 | 122.1714 | 122.0974 | 122.0106 | 0.45009 | -122.0571 | 0.029545 | 0.13731 | 0.16798 | 0.19264 | -122.0986
2389.9531 | 122.113 | -0.073242 | 121.9711 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.065141 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019827 | 0.030057 | 0.015432 | 0.019361 | 0.33565 | -0.049614 | 122.0524 | 121.9738 | 121.887 | -0.053899 | 0.02852 | 0.078197 | -0.074666 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.019343 | 0.081299 | 0.092603 | 0.023628 | 0.004285 | 0.002621 | -0.084123 | -0.035961 | -122.0514 | 0.10176 | -0.001424 | 0.034537 | -121.9528 | -121.9039 | 122.1257 | 122.047 | 121.9602 | 0.40889 | -122.025 | -0.007076 | 0.091527 | 0.14051 | 0.15144 | -122.0803
2391.7188 | 122.1451 | -0.09613 | 121.9482 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.064928 | -0.0093137 | 0.053324 | -0.01755 | -0.0044395 | -0.0019123 | 0.019613 | 0.030485 | 0.015219 | 0.014783 | 0.33107 | -0.05877 | 122.0524 | 121.9783 | 121.9053 | -0.058478 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.037652 | 0.10419 | 0.11091 | 0.03736 | -0.000292 | 0.030088 | -0.042921 | -0.013073 | -122.0377 | 0.12007 | 0.030621 | 0.043694 | -121.9254 | -121.8855 | 122.1486 | 122.0745 | 122.0015 | 0.4272 | -122.0067 | 0.006655 | 0.11899 | 0.15882 | 0.16975 | -122.0574
2393.4844 | 122.0032 | -0.11444 | 121.9803 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.064928 | -0.0090999 | 0.053538 | -0.01755 | -0.0040121 | -0.0016987 | 0.019827 | 0.030057 | 0.015219 | 0.019361 | 0.33565 | -0.054192 | 122.0479 | 121.9783 | 121.8916 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.060542 | 0.067565 | 0.1338 | 0.060249 | -0.000293 | -0.001956 | -0.0887 | 0.005238 | -122.056 | 0.13838 | 0.053511 | 0.048273 | -121.9666 | -121.9222 | 122.1623 | 122.0928 | 122.006 | 0.45009 | -122.0342 | 0.038702 | 0.12815 | 0.17256 | 0.18806 | -122.0895
2395.25 | 122.1039 | -0.07782 | 121.9528 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.065141 | -0.0090999 | 0.053324 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019613 | 0.030271 | 0.016073 | 0.014783 | 0.34022 | -0.054192 | 122.0479 | 121.9783 | 121.9007 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.019342 | 0.095031 | 0.092603 | 0.023628 | 0.004286 | 0.02551 | -0.052077 | -0.026804 | -122.0423 | 0.10634 | 0.01689 | 0.043694 | -121.9345 | -121.8901 | 122.1257 | 122.0562 | 121.9786 | 0.41804 | -122.0113 | -0.011655 | 0.096105 | 0.14051 | 0.15602 | -122.0574
2397.0156 | 122.0032 | -0.10986 | 121.9757 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065141 | -0.0093137 | 0.053324 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019827 | 0.029844 | 0.015432 | 0.023939 | 0.3448 | -0.049614 | 122.0524 | 121.9738 | 121.9007 | -0.058478 | 0.02852 | 0.082776 | -0.065509 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.051385 | 0.076721 | 0.1338 | 0.060249 | 0.008864 | -0.001957 | -0.074965 | 0.005239 | -122.0652 | 0.13838 | 0.044354 | 0.039115 | -121.962 | -121.9176 | 122.1623 | 122.0836 | 122.0106 | 0.45466 | -122.0342 | 0.020388 | 0.12357 | 0.16798 | 0.19264 | -122.0803
2398.7031 | 122.1039 | -0.086975 | 121.9391 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.064928 | -0.0093137 | 0.053538 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.015646 | 0.019361 | 0.34938 | -0.054192 | 122.0479 | 121.9783 | 121.8962 | -0.053899 | 0.023941 | 0.064461 | -0.056351 | -0.080318 | 0.018285 | 0.071851 | -0.10004 | 0.033076 | 0.10876 | 0.10634 | 0.032783 | -0.000293 | 0.039243 | -0.042923 | -0.01307 | -122.0194 | 0.11092 | 0.030624 | 0.043694 | -121.9208 | -121.8672 | 122.1348 | 122.0653 | 121.9831 | 0.43636 | -121.993 | 0.006657 | 0.10526 | 0.15883 | 0.15144 | -122.0391
2400.4688 | 122.0947 | -0.082397 | 121.9803 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065141 | -0.0093137 | 0.05311 | -0.01755 | -0.0040121 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.019361 | 0.3448 | -0.054192 | 122.0524 | 121.9783 | 121.9007 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.027442 | 0.062694 | -0.10462 | 0.028498 | 0.072143 | 0.10176 | 0.028205 | -0.000293 | -0.001956 | -0.079543 | -0.022227 | -122.0698 | 0.10634 | 0.016888 | 0.039115 | -121.9528 | -121.9176 | 122.1348 | 122.0607 | 121.9831 | 0.4272 | -122.0342 | -0.007078 | 0.10984 | 0.14509 | 0.15602 | -122.0849
2402.2344 | 122.1359 | -0.07782 | 121.9299 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.064928 | -0.0093137 | 0.05311 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019827 | 0.029844 | 0.015646 | 0.014783 | 0.3448 | -0.049614 | 122.0524 | 121.9783 | 121.8916 | -0.058478 | 0.023941 | 0.06904 | -0.065509 | -0.089475 | 0.022864 | 0.058115 | -0.10004 | 0.019342 | 0.1225 | 0.092603 | 0.028206 | 0.008864 | 0.048398 | -0.038346 | -0.022225 | -122.0194 | 0.10176 | 0.012311 | 0.034536 | -121.9071 | -121.8718 | 122.1302 | 122.0562 | 121.9694 | 0.42262 | -121.9884 | -0.011655 | 0.10068 | 0.13594 | 0.14686 | -122.03
2403.9375 | 121.9986 | -0.13733 | 121.994 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065141 | -0.0095273 | 0.053324 | -0.01755 | -0.0044395 | -0.0016987 | 0.019827 | 0.030271 | 0.015646 | 0.019361 | 0.34938 | -0.054192 | 122.0479 | 121.9692 | 121.8962 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.032021 | 0.058115 | -0.095467 | 0.08343 | 0.053832 | 0.15669 | 0.083137 | -0.000293 | -0.024847 | -0.097855 | 0.041862 | -122.0743 | 0.16127 | 0.076399 | 0.034537 | -121.962 | -121.9359 | 122.1852 | 122.1065 | 122.0335 | 0.48671 | -122.0479 | 0.057011 | 0.16935 | 0.19544 | 0.21095 | -122.0895
2405.6875 | 122.1451 | -0.07782 | 121.9345 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065355 | -0.0095273 | 0.053538 | -0.0099192 | -0.0037985 | -0.0021259 | 0.019613 | 0.030057 | 0.015646 | 0.014783 | 0.34938 | -0.045036 | 122.0524 | 121.9738 | 121.8962 | -0.053899 | 0.023941 | 0.06904 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.10004 | 0.023921 | 0.11792 | 0.092603 | 0.032784 | 0.008863 | 0.039242 | -0.038345 | -0.022225 | -122.0148 | 0.10176 | 0.012311 | 0.034536 | -121.9162 | -121.8672 | 122.1302 | 122.0516 | 121.974 | 0.4272 | -121.9884 | -0.002498 | 0.096105 | 0.14509 | 0.14686 | -122.0346
2407.4531 | 122.0032 | -0.10986 | 122.0078 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.065355 | -0.0090999 | 0.052683 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.015646 | 0.019361 | 0.35854 | -0.05877 | 122.0433 | 121.9829 | 121.9007 | -0.053899 | 0.019362 | 0.073618 | -0.065509 | -0.089475 | 0.027442 | 0.062694 | -0.1092 | 0.055964 | 0.035521 | 0.12922 | 0.051093 | -0.004871 | -0.024842 | -0.10701 | 0.00066 | -122.0972 | 0.12923 | 0.044354 | 0.043694 | -121.9803 | -121.9451 | 122.1531 | 122.0928 | 122.0106 | 0.4684 | -122.0617 | 0.020388 | 0.13731 | 0.17256 | 0.18348 | -122.117
2409.1562 | 122.1222 | -0.073242 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.064928 | -0.0097409 | 0.053324 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019399 | 0.030057 | 0.015859 | 0.023939 | 0.35854 | -0.045036 | 122.057 | 121.9829 | 121.9007 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.075739 | 0.018285 | 0.058115 | -0.10462 | 0.019343 | 0.10419 | 0.097181 | 0.028206 | 0.008863 | 0.030089 | -0.052077 | -0.031382 | -122.0286 | 0.097183 | 0.016891 | 0.048273 | -121.9345 | -121.8947 | 122.1302 | 122.0562 | 121.974 | 0.43178 | -122.0067 | -0.002497 | 0.091527 | 0.13136 | 0.15144 | -122.0574
2410.9219 | 122.1497 | -0.086975 | 121.9528 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065355 | -0.0090999 | 0.052897 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019399 | 0.029844 | 0.015432 | 0.019361 | 0.3448 | -0.054192 | 122.057 | 121.9783 | 121.9007 | -0.058478 | 0.019362 | 0.064461 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.10004 | 0.028497 | 0.10419 | 0.10634 | 0.032783 | 0.004286 | 0.02551 | -0.052077 | -0.01307 | -122.0423 | 0.10634 | 0.026045 | 0.039115 | -121.93 | -121.8947 | 122.144 | 122.0653 | 121.9877 | 0.43178 | -122.0113 | -0.0025 | 0.10984 | 0.14509 | 0.15144 | -122.0529
2412.6875 | 122.0627 | -0.086975 | 121.9528 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030057 | 0.015646 | 0.014783 | 0.36312 | -0.049614 | 122.0524 | 121.9783 | 121.8916 | -0.044742 | 0.023941 | 0.073618 | -0.056351 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.042233 | 0.099609 | 0.10176 | 0.037361 | -0.004872 | 0.02551 | -0.061234 | -0.022228 | -122.0377 | 0.11092 | 0.030624 | 0.052852 | -121.93 | -121.8947 | 122.1394 | 122.0653 | 121.9786 | 0.45009 | -121.9976 | 0.002079 | 0.10984 | 0.14509 | 0.16059 | -122.062
2414.3906 | 122.1268 | -0.07782 | 121.9482 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065355 | -0.0093137 | 0.052897 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.029844 | 0.015646 | 0.014783 | 0.36312 | -0.054192 | 122.057 | 121.9829 | 121.9053 | -0.058478 | 0.014784 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.11378 | 0.019342 | 0.10877 | 0.092603 | 0.023628 | 0.004286 | 0.034667 | -0.042921 | -0.035962 | -122.0286 | 0.092604 | 0.01689 | 0.052852 | -121.93 | -121.881 | 122.1348 | 122.0607 | 121.9831 | 0.44094 | -122.0067 | -0.002498 | 0.096105 | 0.14509 | 0.14686 | -122.062
2416.1406 | 122.1359 | -0.082397 | 121.8979 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065141 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019399 | 0.030057 | 0.015646 | 0.014783 | 0.36769 | -0.05877 | 122.0479 | 121.9875 | 121.9007 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.094053 | 0.027442 | 0.067272 | -0.1092 | 0.033076 | 0.14996 | 0.09718 | 0.023627 | -0.009449 | 0.0896 | 0.002855 | -0.026806 | -121.9919 | 0.10634 | 0.021467 | 0.048273 | -121.8704 | -121.8306 | 122.1302 | 122.0699 | 121.9831 | 0.45009 | -121.9472 | -0.011656 | 0.10984 | 0.14967 | 0.16059 | -122.0071
2417.9062 | 122.0947 | -0.09613 | 121.9391 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065141 | -0.0090999 | 0.053538 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019613 | 0.030057 | 0.015432 | 0.014783 | 0.37685 | -0.05877 | 122.0524 | 121.9783 | 121.9007 | -0.053899 | 0.023941 | 0.06904 | -0.06093 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.042231 | 0.11334 | 0.11091 | 0.03736 | -0.004871 | 0.039243 | -0.038344 | -0.013073 | -122.0286 | 0.12007 | 0.0352 | 0.048273 | -121.9162 | -121.8764 | 122.1486 | 122.0745 | 121.9969 | 0.47298 | -121.993 | 0.006655 | 0.11899 | 0.15882 | 0.16517 | -122.0483
2419.6562 | 122.1405 | -0.07782 | 121.9437 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0022892 | -0.0040121 | -0.0012713 | 0.019613 | 0.029844 | 0.015859 | 0.014783 | 0.37227 | -0.054192 | 122.0616 | 121.9783 | 121.8962 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.1092 | 0.023921 | 0.11792 | 0.092603 | 0.023628 | -0.000293 | 0.034665 | -0.047501 | -0.031383 | -122.024 | 0.10176 | 0.01689 | 0.048273 | -121.9162 | -121.8764 | 122.1394 | 122.0562 | 121.974 | 0.45009 | -121.9976 | -0.002498 | 0.10526 | 0.14509 | 0.15602 | -122.0529
2421.4219 | 122.0306 | -0.11444 | 121.962 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065355 | -0.0093137 | 0.052897 | -0.01755 | -0.0042257 | -0.0019123 | 0.019613 | 0.030057 | 0.015859 | 0.014783 | 0.37685 | -0.049614 | 122.0524 | 121.9829 | 121.9053 | -0.058478 | 0.033099 | 0.087354 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.055963 | 0.090454 | 0.12922 | 0.064827 | 0.008864 | 0.020934 | -0.056654 | 0.009817 | -122.0469 | 0.14754 | 0.053511 | 0.043694 | -121.9437 | -121.8993 | 122.1669 | 122.0974 | 122.0198 | 0.49129 | -122.0205 | 0.029545 | 0.13273 | 0.17713 | 0.2018 | -122.0666
2423.1406 | 122.0261 | -0.1236 | 121.9757 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065355 | -0.0095273 | 0.053538 | -0.01755 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015432 | 0.019361 | 0.39059 | -0.049614 | 122.0524 | 121.9783 | 121.8962 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | 0.069697 | 0.076721 | 0.14296 | 0.073982 | 0.004285 | 0.002622 | -0.079544 | 0.014393 | -122.056 | 0.14754 | 0.058087 | 0.043694 | -121.9528 | -121.9084 | 122.176 | 122.1019 | 122.0198 | 0.51418 | -122.0296 | 0.043278 | 0.14646 | 0.19087 | 0.20179 | -122.0849
2424.9062 | 122.0947 | -0.10071 | 121.962 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.064928 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.015646 | 0.014783 | 0.38143 | -0.049614 | 122.0524 | 121.9783 | 121.8962 | -0.053899 | 0.033099 | 0.06904 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.046809 | 0.090454 | 0.11549 | 0.051094 | 0.004285 | 0.016355 | -0.065811 | -0.003916 | -122.0469 | 0.13381 | 0.039778 | 0.043694 | -121.9345 | -121.8993 | 122.1531 | 122.079 | 121.9969 | 0.48214 | -122.0159 | 0.015812 | 0.12815 | 0.1634 | 0.16975 | -122.0666
2426.5938 | 122.0078 | -0.11902 | 121.9666 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.064928 | -0.0088863 | 0.05311 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.023939 | 0.39059 | -0.054192 | 122.0524 | 121.9829 | 121.9007 | -0.053899 | 0.02852 | 0.082776 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.10462 | 0.06512 | 0.085876 | 0.14296 | 0.064827 | -0.000293 | 0.016356 | -0.06581 | 0.014395 | -122.056 | 0.14754 | 0.05351 | 0.039115 | -121.9528 | -121.9039 | 122.1714 | 122.1019 | 122.0198 | 0.50961 | -122.0205 | 0.029544 | 0.13273 | 0.18171 | 0.2018 | -122.0712
2428.375 | 122.0627 | -0.09613 | 121.9803 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065141 | -0.0093137 | 0.05311 | 0.0053413 | -0.0044395 | -0.0014849 | 0.019399 | 0.030057 | 0.015432 | 0.019361 | 0.38601 | -0.045036 | 122.057 | 121.9829 | 121.9007 | -0.053899 | 0.02852 | 0.064461 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.1092 | 0.042231 | 0.076721 | 0.11549 | 0.051094 | 0.008863 | 0.002623 | -0.079543 | -0.013073 | -122.0698 | 0.12465 | 0.030621 | 0.043694 | -121.9666 | -121.9176 | 122.1531 | 122.079 | 121.9969 | 0.48214 | -122.0342 | 0.006655 | 0.10984 | 0.15882 | 0.16059 | -122.0895
2430.0781 | 122.0032 | -0.1236 | 121.9849 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065141 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019399 | 0.030057 | 0.015859 | 0.019361 | 0.38601 | -0.049614 | 122.057 | 121.9829 | 121.9053 | -0.053899 | 0.02852 | 0.082776 | -0.065509 | -0.084896 | 0.013707 | 0.053537 | -0.1092 | 0.069697 | 0.072144 | 0.14296 | 0.073982 | 0.004285 | -0.001954 | -0.079542 | 0.014393 | -122.0698 | 0.15212 | 0.058087 | 0.043694 | -121.9712 | -121.9313 | 122.1806 | 122.1065 | 122.0289 | 0.5096 | -122.0388 | 0.0387 | 0.1373 | 0.17713 | 0.20637 | -122.0941
2431.8281 | 122.0947 | -0.082397 | 121.9757 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064928 | -0.0090999 | 0.053324 | -0.01755 | -0.0042257 | -0.0016987 | 0.019827 | 0.030271 | 0.015646 | 0.019361 | 0.39059 | -0.049614 | 122.057 | 121.9783 | 121.9007 | -0.053899 | 0.019362 | 0.073618 | -0.065509 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.028498 | 0.081299 | 0.10176 | 0.032783 | 0.004285 | 0.002622 | -0.074965 | -0.026806 | -122.0606 | 0.10176 | 0.016888 | 0.043694 | -121.9483 | -121.913 | 122.1394 | 122.0607 | 121.9831 | 0.47298 | -122.0296 | -0.002499 | 0.10984 | 0.14509 | 0.15602 | -122.0849
2433.5938 | 122.0444 | -0.10529 | 121.9666 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064928 | -0.0095273 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.023939 | 0.39059 | -0.045036 | 122.0616 | 121.9875 | 121.9007 | -0.044742 | 0.02852 | 0.073618 | -0.056351 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.060544 | 0.095033 | 0.12923 | 0.06025 | -0.000294 | 0.020935 | -0.06581 | 0.000662 | -122.0469 | 0.13381 | 0.048935 | 0.048273 | -121.9437 | -121.9039 | 122.1669 | 122.0928 | 122.006 | 0.49587 | -122.0113 | 0.024968 | 0.12815 | 0.16798 | 0.1789 | -122.0712
2435.2969 | 122.1085 | -0.07782 | 121.9208 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.064714 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030057 | 0.015432 | 0.014783 | 0.39975 | -0.054192 | 122.057 | 121.9783 | 121.9007 | -0.058478 | 0.023941 | 0.06904 | -0.065509 | -0.089475 | 0.018285 | 0.058115 | -0.10462 | 0.019342 | 0.13623 | 0.092603 | 0.023628 | 0.004286 | 0.057554 | -0.020033 | -0.026804 | -122.0103 | 0.10176 | 0.012311 | 0.039115 | -121.9025 | -121.8627 | 122.1348 | 122.0562 | 121.9786 | 0.47757 | -121.9793 | -0.011655 | 0.096105 | 0.13594 | 0.14686 | -122.0254
2437.0625 | 122.0261 | -0.11444 | 121.9894 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.065355 | -0.0093137 | 0.052897 | -0.0099192 | -0.0037985 | -0.0014849 | 0.019827 | 0.030271 | 0.015646 | 0.019361 | 0.39517 | -0.054192 | 122.0616 | 121.9783 | 121.9053 | -0.053899 | 0.023941 | 0.073618 | -0.051772 | -0.084896 | 0.018285 | 0.058115 | -0.10462 | 0.060542 | 0.072145 | 0.1338 | 0.060249 | -0.000293 | -0.011111 | -0.08412 | 0.009817 | -122.0743 | 0.13838 | 0.062669 | 0.052852 | -121.9712 | -121.9313 | 122.176 | 122.0928 | 122.0198 | 0.50961 | -122.0433 | 0.029545 | 0.13273 | 0.17256 | 0.18806 | -122.0941
2438.8125 | 122.1176 | -0.059509 | 121.9254 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.064928 | -0.0090999 | 0.05311 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019613 | 0.030057 | 0.015646 | 0.014783 | 0.40432 | -0.054192 | 122.057 | 121.9783 | 121.9099 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.00561 | 0.13165 | 0.074292 | 0.005317 | -0.000293 | 0.052976 | -0.015454 | -0.049694 | -122.0102 | 0.08345 | -0.006 | 0.043694 | -121.8979 | -121.8627 | 122.1165 | 122.0378 | 121.9694 | 0.46383 | -121.9793 | -0.025387 | 0.086951 | 0.1222 | 0.13313 | -122.0346
2440.5156 | 122.1039 | -0.068665 | 121.9391 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065355 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.029844 | 0.015432 | 0.014783 | 0.40432 | -0.045036 | 122.0616 | 121.9829 | 121.9007 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.089475 | 0.013707 | 0.062694 | -0.1092 | 0.014766 | 0.1225 | 0.083448 | 0.023629 | 0.008863 | 0.043822 | -0.038344 | -0.040538 | -122.0286 | 0.088027 | 0.007735 | 0.048273 | -121.9254 | -121.8764 | 122.1303 | 122.0516 | 121.9694 | 0.47299 | -121.993 | -0.02081 | 0.082372 | 0.13136 | 0.14228 | -122.0483
2442.2812 | 122.0535 | -0.11444 | 121.9711 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065355 | -0.0097409 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.030057 | 0.015432 | 0.014783 | 0.40432 | -0.054192 | 122.0616 | 121.9783 | 121.9007 | -0.058478 | 0.019362 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.055963 | 0.090456 | 0.12922 | 0.060249 | 0.004286 | 0.0072 | -0.070387 | 0.009817 | -122.056 | 0.1338 | 0.048932 | 0.039115 | -121.9574 | -121.9084 | 122.176 | 122.0928 | 122.0152 | 0.51877 | -122.0296 | 0.029545 | 0.12815 | 0.17713 | 0.19264 | -122.0758
2444.0312 | 122.0947 | -0.059509 | 121.9345 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065355 | -0.0093137 | 0.05311 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019827 | 0.029844 | 0.015859 | 0.010204 | 0.41348 | -0.054192 | 122.0524 | 121.9829 | 121.9053 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.027442 | 0.058115 | -0.10462 | 0.00561 | 0.11792 | 0.069713 | 0.005317 | -0.000293 | 0.0484 | -0.029188 | -0.045115 | -122.0194 | 0.078871 | -0.001421 | 0.043694 | -121.9071 | -121.8764 | 122.1119 | 122.0424 | 121.9648 | 0.47299 | -121.9884 | -0.025387 | 0.086951 | 0.11762 | 0.13313 | -122.0391
2445.9062 | 121.9711 | -0.11444 | 121.9711 | 1.4211e-13 | -0.04217 | 0.0020727 | 0.064928 | -0.0095273 | 0.053324 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030057 | 0.015646 | 0.019361 | 0.41348 | -0.054192 | 122.057 | 121.9921 | 121.8962 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.10004 | 0.06512 | 0.085877 | 0.1338 | 0.060249 | -0.004871 | 0.020937 | -0.074966 | 0.014396 | -122.056 | 0.13838 | 0.048932 | 0.034536 | -121.9528 | -121.9084 | 122.1714 | 122.1065 | 122.0106 | 0.52792 | -122.0205 | 0.029545 | 0.13273 | 0.17713 | 0.19264 | -122.0712
2449.4844 | 122.0856 | -0.082397 | 121.9528 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065355 | -0.0093137 | 0.053324 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019827 | 0.030271 | 0.015646 | 0.019361 | 0.42264 | -0.054192 | 122.057 | 121.9875 | 121.9099 | -0.049321 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.067272 | -0.10462 | 0.033076 | 0.10419 | 0.10176 | 0.028205 | -0.004871 | 0.034668 | -0.04292 | -0.022227 | -122.0377 | 0.10634 | 0.016888 | 0.039115 | -121.9391 | -121.8855 | 122.1394 | 122.0699 | 121.9923 | 0.50504 | -122.0021 | -0.002499 | 0.096104 | 0.14967 | 0.15602 | -122.0574
2453.375 | 122.1039 | -0.07782 | 121.9345 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.064928 | -0.0095273 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019827 | 0.030485 | 0.015646 | 0.019361 | 0.43179 | -0.049614 | 122.0616 | 121.9875 | 121.9007 | -0.044742 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.018285 | 0.062694 | -0.10462 | 0.033078 | 0.12708 | 0.097181 | 0.028206 | -0.004872 | 0.052979 | -0.033766 | -0.026804 | -122.0148 | 0.10634 | 0.021469 | 0.048273 | -121.9162 | -121.8718 | 122.1394 | 122.0653 | 121.9786 | 0.50961 | -121.9793 | -0.002498 | 0.096105 | 0.14051 | 0.15602 | -122.0391
2459.2188 | 122.0764 | -0.09613 | 121.9345 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065355 | -0.0093137 | 0.053324 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019399 | 0.030271 | 0.015859 | 0.023939 | 0.45011 | -0.05877 | 122.057 | 121.9829 | 121.9099 | -0.053899 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.10004 | 0.042231 | 0.1225 | 0.12007 | 0.03736 | -0.004871 | 0.0484 | -0.024609 | -0.003915 | -122.0194 | 0.12465 | 0.0352 | 0.039115 | -121.9162 | -121.8718 | 122.1531 | 122.079 | 122.006 | 0.54624 | -121.9884 | 0.011234 | 0.11441 | 0.15882 | 0.16975 | -122.0346
2460.9375 | 122.0856 | -0.10071 | 121.9757 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.064928 | -0.0095273 | 0.053324 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019613 | 0.030271 | 0.015432 | 0.023939 | 0.45927 | -0.054192 | 122.057 | 121.9829 | 121.9145 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.013707 | 0.062694 | -0.1092 | 0.046809 | 0.081299 | 0.12465 | 0.046516 | -0.000293 | 0.007201 | -0.061229 | -0.008495 | -122.0652 | 0.12465 | 0.044357 | 0.052852 | -121.962 | -121.913 | 122.1577 | 122.0836 | 122.0152 | 0.55998 | -122.0296 | 0.011233 | 0.11442 | 0.1634 | 0.17433 | -122.0849
2462.6406 | 121.9803 | -0.11444 | 121.9757 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.065355 | -0.0097409 | 0.052897 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015646 | 0.019361 | 0.45469 | -0.054192 | 122.0662 | 121.9875 | 121.9099 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.013707 | 0.067272 | -0.10462 | 0.060542 | 0.090456 | 0.1338 | 0.060249 | -0.000293 | 0.01178 | -0.065808 | 0.009817 | -122.056 | 0.13838 | 0.048932 | 0.039115 | -121.962 | -121.9084 | 122.1806 | 122.1019 | 122.0243 | 0.56913 | -122.0296 | 0.034123 | 0.12815 | 0.18171 | 0.19264 | -122.0803
2464.4062 | 122.1268 | -0.09613 | 121.9437 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065141 | -0.0095273 | 0.05311 | -0.01755 | -0.0044395 | -0.0016987 | 0.02004 | 0.030271 | 0.015432 | 0.019361 | 0.45927 | -0.063349 | 122.0616 | 121.9875 | 121.9053 | -0.049321 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.058115 | -0.11378 | 0.046809 | 0.11792 | 0.11549 | 0.032781 | -0.014028 | 0.043823 | -0.038344 | -0.017652 | -122.0286 | 0.12007 | 0.030621 | 0.048273 | -121.93 | -121.8855 | 122.1577 | 122.0836 | 122.0015 | 0.5554 | -121.993 | 0.011234 | 0.10984 | 0.15424 | 0.16975 | -122.0574
2466.1719 | 122.0535 | -0.10071 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065141 | -0.0093137 | 0.053751 | -0.0022892 | -0.0044395 | -0.0014849 | 0.02004 | 0.030057 | 0.015859 | 0.023939 | 0.473 | -0.049614 | 122.057 | 121.9783 | 121.9145 | -0.053899 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.018285 | 0.058115 | -0.1092 | 0.046809 | 0.10419 | 0.12465 | 0.051094 | 0.004285 | 0.02551 | -0.038341 | -0.008495 | -122.0331 | 0.12007 | 0.035199 | 0.043694 | -121.9345 | -121.8947 | 122.1577 | 122.079 | 122.0152 | 0.57371 | -122.0067 | 0.02039 | 0.11899 | 0.15882 | 0.17891 | -122.062
2467.9375 | 122.1405 | -0.082397 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065355 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030057 | 0.015219 | 0.023939 | 0.47758 | -0.049614 | 122.0616 | 121.9829 | 121.9007 | -0.049321 | 0.014784 | 0.073618 | -0.070087 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.033076 | 0.10877 | 0.10634 | 0.032783 | -0.000293 | 0.030089 | -0.052077 | -0.031385 | -122.0377 | 0.097181 | 0.01231 | 0.043695 | -121.93 | -121.8901 | 122.144 | 122.0653 | 121.9831 | 0.55998 | -122.0021 | -0.002499 | 0.10526 | 0.14509 | 0.15602 | -122.0666
2469.7031 | 122.049 | -0.1236 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0090999 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015219 | 0.019361 | 0.49132 | -0.049614 | 122.057 | 121.9875 | 121.9145 | -0.053899 | 0.023941 | 0.06904 | -0.065509 | -0.084896 | 0.009128 | 0.062694 | -0.1092 | 0.069697 | 0.10419 | 0.14296 | 0.073982 | 0.004285 | 0.034668 | -0.038341 | 0.014393 | -122.0377 | 0.14754 | 0.058087 | 0.043694 | -121.9437 | -121.8901 | 122.1806 | 122.1111 | 122.0381 | 0.61491 | -122.0067 | 0.0387 | 0.13272 | 0.18629 | 0.19264 | -122.062
2471.4062 | 122.0398 | -0.11902 | 121.9574 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065355 | -0.0099547 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.015432 | 0.028518 | 0.49132 | -0.049614 | 122.057 | 121.9829 | 121.9099 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.10462 | 0.06512 | 0.09961 | 0.14754 | 0.069405 | 0.004285 | 0.025512 | -0.047497 | 0.014395 | -122.0423 | 0.13838 | 0.058089 | 0.043694 | -121.9437 | -121.8993 | 122.176 | 122.1019 | 122.0289 | 0.61034 | -122.0113 | 0.034123 | 0.13273 | 0.17713 | 0.19722 | -122.062
2473.1094 | 122.1313 | -0.082397 | 121.9482 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065141 | -0.0095273 | 0.053324 | -0.01755 | -0.0044395 | -0.0019123 | 0.019399 | 0.030271 | 0.015432 | 0.023939 | 0.4959 | -0.05877 | 122.0616 | 121.9829 | 121.9053 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.028498 | 0.11334 | 0.10634 | 0.023627 | -0.004871 | 0.034667 | -0.042921 | -0.022227 | -122.0331 | 0.10634 | 0.021467 | 0.043694 | -121.9345 | -121.8855 | 122.144 | 122.0653 | 121.9877 | 0.57829 | -122.0021 | -0.002499 | 0.096104 | 0.14509 | 0.15602 | -122.0529
2474.875 | 122.0901 | -0.068665 | 121.9437 | 1.4211e-13 | -0.042598 | 0.0020727 | 0.065141 | -0.0093137 | 0.052897 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019613 | 0.030271 | 0.015219 | 0.028518 | 0.50505 | -0.054192 | 122.0707 | 121.9875 | 121.9053 | -0.044742 | 0.02852 | 0.073618 | -0.065509 | -0.094053 | 0.022864 | 0.062694 | -0.1092 | 0.023923 | 0.12708 | 0.097183 | 0.014473 | -0.00945 | 0.043823 | -0.038344 | -0.040538 | -122.0377 | 0.097185 | 0.003156 | 0.043694 | -121.9208 | -121.881 | 122.1394 | 122.0562 | 121.974 | 0.57372 | -121.9884 | -0.025388 | 0.091529 | 0.13136 | 0.14228 | -122.0529
2476.5625 | 122.1313 | -0.068665 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0012179 | 0.065141 | -0.0095273 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.015432 | 0.023939 | 0.50963 | -0.054192 | 122.0662 | 121.9921 | 121.9191 | -0.053899 | 0.02852 | 0.073618 | -0.056351 | -0.080318 | 0.018285 | 0.058115 | -0.11378 | 0.014766 | 0.13165 | 0.092604 | 0.014473 | -0.000293 | 0.057558 | -0.015452 | -0.045117 | -122.0148 | 0.097185 | 0.012314 | 0.057431 | -121.9162 | -121.8764 | 122.1348 | 122.0607 | 121.9877 | 0.5783 | -121.9884 | -0.011653 | 0.08695 | 0.12678 | 0.14228 | -122.0483
2478.3125 | 122.0444 | -0.10529 | 121.994 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065141 | -0.0090999 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.030057 | 0.015432 | 0.023939 | 0.52795 | -0.049614 | 122.0616 | 121.9875 | 121.9145 | -0.058478 | 0.02852 | 0.06904 | -0.06093 | -0.089475 | 0.013707 | 0.067272 | -0.10004 | 0.046808 | 0.067567 | 0.12923 | 0.055672 | 0.008864 | -0.006531 | -0.07954 | 0.005241 | -122.0835 | 0.13381 | 0.044356 | 0.039115 | -121.9803 | -121.9267 | 122.1669 | 122.0928 | 122.0198 | 0.63323 | -122.0525 | 0.015811 | 0.11899 | 0.17256 | 0.17433 | -122.0941
2480.0781 | 122.1313 | -0.064087 | 121.9391 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065141 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.02004 | 0.030057 | 0.015219 | 0.028518 | 0.54168 | -0.054192 | 122.0616 | 121.9829 | 121.9145 | -0.053899 | 0.033099 | 0.073618 | -0.070087 | -0.084896 | 0.027442 | 0.062694 | -0.11378 | 0.010188 | 0.1225 | 0.092605 | 0.009895 | -0.000293 | 0.043822 | -0.024608 | -0.049695 | -122.024 | 0.097186 | -0.006 | 0.043695 | -121.9116 | -121.8764 | 122.1257 | 122.047 | 121.9786 | 0.60577 | -121.993 | -0.020809 | 0.091529 | 0.12678 | 0.13771 | -122.0529
2481.8281 | 122.0581 | -0.13275 | 121.962 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065141 | -0.0095273 | 0.053538 | -0.0022892 | -0.0040121 | -0.0016987 | 0.02004 | 0.030271 | 0.015432 | 0.023939 | 0.54626 | -0.063349 | 122.0616 | 121.9829 | 121.9099 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.1092 | 0.078852 | 0.099611 | 0.15669 | 0.069402 | -0.00945 | 0.020934 | -0.052075 | 0.023548 | -122.0514 | 0.16127 | 0.071821 | 0.048273 | -121.9391 | -121.9039 | 122.1943 | 122.1157 | 122.0427 | 0.67901 | -122.0159 | 0.043276 | 0.15562 | 0.19087 | 0.21553 | -122.0712
2483.5312 | 122.0261 | -0.10986 | 121.9849 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065355 | -0.0095273 | 0.053538 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019613 | 0.030271 | 0.015646 | 0.019361 | 0.56458 | -0.049614 | 122.057 | 121.9921 | 121.9099 | -0.058478 | 0.033099 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.051385 | 0.072144 | 0.12922 | 0.060249 | 0.008864 | 0.007204 | -0.074963 | 0.00066 | -122.0698 | 0.14296 | 0.048933 | 0.048273 | -121.9666 | -121.9267 | 122.1669 | 122.1019 | 122.0198 | 0.67444 | -122.0433 | 0.024967 | 0.12815 | 0.16798 | 0.18348 | -122.0941
2485.2969 | 122.1085 | -0.073242 | 121.962 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065355 | -0.0095273 | 0.052897 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019613 | 0.030698 | 0.015646 | 0.023939 | 0.56915 | -0.05877 | 122.0616 | 121.9875 | 121.9191 | -0.058478 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.1092 | 0.014764 | 0.099611 | 0.097181 | 0.014472 | -0.000292 | 0.025513 | -0.042918 | -0.035961 | -122.0423 | 0.097183 | 0.012312 | 0.048273 | -121.9437 | -121.9039 | 122.1348 | 122.0607 | 121.9923 | 0.6424 | -122.0205 | -0.007076 | 0.091527 | 0.13136 | 0.14228 | -122.0712
2487.0469 | 122.0581 | -0.09613 | 121.9574 | 1.4211e-13 | -0.042384 | 0.0012179 | 0.065355 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019399 | 0.030057 | 0.015219 | 0.019361 | 0.58747 | -0.054192 | 122.0662 | 121.9966 | 121.9145 | -0.053899 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.018285 | 0.071851 | -0.10462 | 0.042231 | 0.10877 | 0.11549 | 0.041938 | -0.000293 | 0.039249 | -0.042918 | -0.008494 | -122.0423 | 0.12007 | 0.0352 | 0.043694 | -121.9391 | -121.8855 | 122.1623 | 122.0928 | 122.0106 | 0.6836 | -122.0113 | 0.011234 | 0.11441 | 0.16798 | 0.16517 | -122.062
2488.75 | 122.0947 | -0.09613 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065141 | -0.0093137 | 0.053324 | -0.02518 | -0.0042257 | -0.0021259 | 0.019613 | 0.030271 | 0.015432 | 0.023939 | 0.58289 | -0.05877 | 122.057 | 121.9829 | 121.9099 | -0.049321 | 0.014784 | 0.078197 | -0.070087 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.046809 | 0.09961 | 0.12007 | 0.03736 | -0.009449 | 0.025512 | -0.047497 | -0.008494 | -122.0377 | 0.11091 | 0.026043 | 0.034537 | -121.9391 | -121.8993 | 122.1531 | 122.079 | 122.006 | 0.67902 | -122.0067 | 0.015812 | 0.11441 | 0.15424 | 0.17433 | -122.062
2490.5312 | 122.1313 | -0.054932 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0090999 | 0.053324 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.015646 | 0.014783 | 0.61036 | -0.054192 | 122.057 | 121.9875 | 121.9145 | -0.053899 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.001033 | 0.11792 | 0.069715 | 0.00074 | -0.000293 | 0.048401 | -0.024608 | -0.049692 | -122.0194 | 0.083452 | -0.010577 | 0.039115 | -121.9162 | -121.8764 | 122.1119 | 122.0424 | 121.9694 | 0.66529 | -121.993 | -0.025386 | 0.077796 | 0.11763 | 0.13313 | -122.0437
2492.2969 | 122.0947 | -0.082397 | 121.9574 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065569 | -0.0090999 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.029844 | 0.015646 | 0.028518 | 0.61952 | -0.049614 | 122.0662 | 121.9875 | 121.9099 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.10462 | 0.033076 | 0.10877 | 0.11091 | 0.032783 | -0.000293 | 0.030091 | -0.047497 | -0.022227 | -122.0377 | 0.10634 | 0.021467 | 0.043694 | -121.9391 | -121.8947 | 122.1486 | 122.0699 | 121.9923 | 0.70192 | -122.0067 | 0.002079 | 0.10068 | 0.14509 | 0.15602 | -122.062
2494.0625 | 122.1497 | -0.07782 | 121.9666 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065141 | -0.0093137 | 0.052897 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030485 | 0.015219 | 0.023939 | 0.62867 | -0.054192 | 122.0616 | 121.9875 | 121.9191 | -0.049321 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.018285 | 0.053537 | -0.10004 | 0.028499 | 0.095033 | 0.10176 | 0.023628 | -0.004871 | 0.020935 | -0.047496 | -0.022225 | -122.0469 | 0.10176 | 0.021469 | 0.043694 | -121.9483 | -121.913 | 122.1394 | 122.0653 | 121.9969 | 0.70649 | -122.0159 | -0.002498 | 0.096105 | 0.13136 | 0.15144 | -122.0666
2495.8281 | 122.0993 | -0.07782 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065141 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019186 | 0.030271 | 0.015432 | 0.023939 | 0.63783 | -0.049614 | 122.0616 | 121.9966 | 121.9145 | -0.044742 | 0.033099 | 0.078197 | -0.06093 | -0.089475 | 0.027442 | 0.053537 | -0.1092 | 0.033078 | 0.10419 | 0.10176 | 0.028206 | -0.004872 | 0.039249 | -0.042918 | -0.031383 | -122.0469 | 0.11092 | 0.01689 | 0.048273 | -121.93 | -121.9039 | 122.1394 | 122.0745 | 121.9923 | 0.71565 | -122.0021 | -0.011655 | 0.10526 | 0.13136 | 0.15602 | -122.0666
2497.5312 | 122.1313 | -0.091553 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0093137 | 0.05311 | -0.01755 | -0.0040121 | -0.0016987 | 0.019399 | 0.030271 | 0.015219 | 0.023939 | 0.64699 | -0.045036 | 122.057 | 121.9875 | 121.9099 | -0.058478 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.053537 | -0.10004 | 0.033075 | 0.09961 | 0.11549 | 0.046517 | 0.013442 | 0.030091 | -0.047497 | -0.008492 | -122.0423 | 0.12007 | 0.026044 | 0.034536 | -121.9391 | -121.9039 | 122.1486 | 122.079 | 122.0015 | 0.73854 | -122.0159 | 0.006657 | 0.10984 | 0.14509 | 0.16517 | -122.0574
2499.2969 | 122.1222 | -0.073242 | 121.9482 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065355 | -0.0093137 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.019186 | 0.030271 | 0.015432 | 0.023939 | 0.6653 | -0.054192 | 122.0662 | 121.9921 | 121.9145 | -0.053899 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.018285 | 0.067272 | -0.1092 | 0.019343 | 0.11792 | 0.097181 | 0.01905 | -0.000293 | 0.043825 | -0.033763 | -0.035961 | -122.0331 | 0.097183 | 0.003155 | 0.039116 | -121.93 | -121.881 | 122.1394 | 122.0653 | 121.9877 | 0.73855 | -122.0021 | -0.011654 | 0.091527 | 0.14051 | 0.15144 | -122.0574
2501.0625 | 122.0627 | -0.10071 | 121.9711 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065355 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015432 | 0.019361 | 0.67446 | -0.054192 | 122.0616 | 121.9921 | 121.9145 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.094053 | 0.013707 | 0.062694 | -0.1092 | 0.051387 | 0.090456 | 0.12007 | 0.046516 | -0.004871 | 0.020937 | -0.056651 | -0.008495 | -122.0652 | 0.12923 | 0.039778 | 0.048273 | -121.9574 | -121.9084 | 122.1623 | 122.0928 | 122.0152 | 0.77517 | -122.0205 | 0.006655 | 0.11442 | 0.1634 | 0.18348 | -122.0803
2502.8281 | 122.1039 | -0.073242 | 121.9894 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065355 | -0.0093137 | 0.053751 | -0.01755 | -0.0044395 | -0.0014849 | 0.019613 | 0.030485 | 0.014791 | 0.023939 | 0.69278 | -0.049614 | 122.057 | 121.9921 | 121.9145 | -0.058478 | 0.023941 | 0.073618 | -0.070087 | -0.084896 | 0.018285 | 0.062694 | -0.10004 | 0.014764 | 0.067566 | 0.097181 | 0.023628 | 0.008864 | 0.002626 | -0.074962 | -0.026803 | -122.0743 | 0.097183 | 0.003155 | 0.029958 | -121.9712 | -121.9267 | 122.1302 | 122.0653 | 121.9877 | 0.76602 | -122.0479 | -0.011654 | 0.091527 | 0.13594 | 0.14686 | -122.0895
2504.5312 | 122.0032 | -0.11902 | 121.9849 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065355 | -0.0097409 | 0.05311 | -0.0022892 | -0.0044395 | -0.0019123 | 0.019613 | 0.030057 | 0.015646 | 0.028518 | 0.71109 | -0.054192 | 122.0662 | 121.9921 | 121.9099 | -0.053899 | 0.033099 | 0.073618 | -0.06093 | -0.089475 | 0.022864 | 0.062694 | -0.11378 | 0.06512 | 0.081301 | 0.14754 | 0.064827 | -0.000293 | 0.007204 | -0.074963 | 0.005237 | -122.0743 | 0.15212 | 0.058089 | 0.052852 | -121.962 | -121.9222 | 122.1852 | 122.1111 | 122.0289 | 0.83011 | -122.0388 | 0.029544 | 0.14188 | 0.18171 | 0.19264 | -122.0986
2506.3125 | 122.1268 | -0.086975 | 121.9299 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0095273 | 0.05311 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.030698 | 0.015859 | 0.023939 | 0.72483 | -0.049614 | 122.0662 | 121.9921 | 121.9191 | -0.053899 | 0.02852 | 0.06904 | -0.056351 | -0.089475 | 0.013707 | 0.067272 | -0.10462 | 0.033076 | 0.13623 | 0.11091 | 0.037361 | 0.004285 | 0.062135 | -0.010875 | -0.017649 | -122.0194 | 0.1155 | 0.030624 | 0.048273 | -121.9162 | -121.8627 | 122.1531 | 122.079 | 122.006 | 0.8118 | -121.9838 | -0.0025 | 0.10068 | 0.15425 | 0.15602 | -122.0346
2508.0781 | 122.0261 | -0.12817 | 122.0032 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0022892 | -0.0040121 | -0.0019123 | 0.019399 | 0.030057 | 0.015432 | 0.023939 | 0.73856 | -0.045036 | 122.0662 | 121.9966 | 121.9145 | -0.049321 | 0.02852 | 0.073618 | -0.070087 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.078853 | 0.06299 | 0.15211 | 0.083138 | 0.004285 | -0.006528 | -0.088695 | 0.018971 | -122.0835 | 0.15669 | 0.058087 | 0.039116 | -121.9803 | -121.9405 | 122.1943 | 122.1248 | 122.0427 | 0.86674 | -122.0525 | 0.047856 | 0.15104 | 0.19087 | 0.20179 | -122.1124
2509.7812 | 122.1268 | -0.054932 | 121.9391 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0093137 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019613 | 0.029844 | 0.015219 | 0.028518 | 0.75688 | -0.054192 | 122.0707 | 121.9875 | 121.9191 | -0.058478 | 0.014784 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.1092 | -0.003546 | 0.13166 | 0.08345 | 0.00074 | 0.004286 | 0.048401 | -0.02003 | -0.054271 | -122.0286 | 0.069716 | -0.005998 | 0.048273 | -121.9208 | -121.8764 | 122.1257 | 122.0424 | 121.974 | 0.81181 | -121.9976 | -0.034543 | 0.073217 | 0.11763 | 0.13313 | -122.0483
2511.5469 | 122.0947 | -0.091553 | 121.962 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065355 | -0.0093137 | 0.053324 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019399 | 0.030271 | 0.015219 | 0.019361 | 0.78435 | -0.054192 | 122.0662 | 121.9921 | 121.9191 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.067272 | -0.10462 | 0.037654 | 0.10419 | 0.11091 | 0.037361 | -0.000293 | 0.030092 | -0.042918 | -0.013071 | -122.0469 | 0.11549 | 0.026044 | 0.039115 | -121.9483 | -121.8947 | 122.1577 | 122.0836 | 122.0106 | 0.8759 | -122.0159 | 0.006657 | 0.10526 | 0.15882 | 0.16517 | -122.0666
2513.2969 | 122.0215 | -0.1236 | 121.9803 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065141 | -0.0095273 | 0.052897 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030485 | 0.015219 | 0.028518 | 0.80724 | -0.045036 | 122.0707 | 121.9966 | 121.9191 | -0.063057 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.060539 | 0.090457 | 0.15211 | 0.07856 | 0.018021 | 0.01636 | -0.061229 | 0.014393 | -122.0652 | 0.15212 | 0.062666 | 0.048273 | -121.9528 | -121.9176 | 122.1943 | 122.1202 | 122.0427 | 0.93084 | -122.0433 | 0.0387 | 0.15104 | 0.18629 | 0.19721 | -122.0895
2515.0625 | 122.049 | -0.10986 | 121.994 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.028518 | 0.83929 | -0.049614 | 122.0662 | 121.9921 | 121.9191 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.055964 | 0.072145 | 0.13838 | 0.060249 | 0.004285 | -0.001952 | -0.074962 | 0.005239 | -122.0789 | 0.1338 | 0.048933 | 0.043694 | -121.9712 | -121.9313 | 122.176 | 122.1019 | 122.0289 | 0.94915 | -122.0479 | 0.024967 | 0.13273 | 0.17256 | 0.19264 | -122.0986
2516.8281 | 122.1451 | -0.064087 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065355 | -0.0090999 | 0.05311 | 0.0053413 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.015432 | 0.028518 | 0.8576 | -0.054192 | 122.0662 | 121.9921 | 121.9236 | -0.049321 | 0.02852 | 0.073618 | -0.056351 | -0.084896 | 0.018285 | 0.048958 | -0.10462 | 0.014766 | 0.11334 | 0.092605 | 0.009895 | -0.004871 | 0.039247 | -0.029184 | -0.040537 | -122.0377 | 0.092607 | 0.007736 | 0.048273 | -121.9345 | -121.9039 | 122.1303 | 122.0562 | 121.9877 | 0.92169 | -122.0021 | -0.020809 | 0.082372 | 0.11305 | 0.13771 | -122.0574
2518.5469 | 122.1222 | -0.086975 | 121.9757 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065141 | -0.0095273 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030057 | 0.015432 | 0.028518 | 0.8805 | -0.049614 | 122.0707 | 121.9921 | 121.9145 | -0.058478 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.1092 | 0.028497 | 0.095035 | 0.11549 | 0.037361 | 0.008864 | 0.016359 | -0.061229 | -0.022228 | -122.056 | 0.10634 | 0.021466 | 0.043694 | -121.962 | -121.9176 | 122.1577 | 122.079 | 122.0015 | 0.96747 | -122.0342 | 0.006657 | 0.10068 | 0.14509 | 0.16517 | -122.0849
2520.3281 | 122.0078 | -0.13275 | 122.0032 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0093137 | 0.053324 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019827 | 0.030271 | 0.015646 | 0.028518 | 0.91713 | -0.040457 | 122.057 | 121.9966 | 121.9236 | -0.053899 | 0.02852 | 0.073618 | -0.06093 | -0.089475 | 0.009128 | 0.058115 | -0.10004 | 0.078852 | 0.053833 | 0.16127 | 0.092294 | 0.013442 | -0.006528 | -0.079538 | 0.032706 | -122.0926 | 0.16127 | 0.071821 | 0.039115 | -121.994 | -121.9451 | 122.1898 | 122.1294 | 122.0564 | 1.0499 | -122.0571 | 0.043276 | 0.14188 | 0.19087 | 0.20637 | -122.1032
2522.0312 | 122.0398 | -0.10529 | 121.9803 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0090999 | 0.053538 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019827 | 0.030485 | 0.015432 | 0.033096 | 0.94002 | -0.049614 | 122.0662 | 121.9966 | 121.9145 | -0.049321 | 0.02852 | 0.06904 | -0.065509 | -0.080318 | 0.018285 | 0.062694 | -0.10462 | 0.055965 | 0.085878 | 0.13838 | 0.055672 | -0.000293 | 0.01636 | -0.065807 | 0.000662 | -122.0606 | 0.13381 | 0.039777 | 0.039115 | -121.962 | -121.9176 | 122.1715 | 122.1019 | 122.0198 | 1.0453 | -122.0296 | 0.024968 | 0.12357 | 0.16798 | 0.17433 | -122.0849
2523.7812 | 122.0856 | -0.10071 | 121.9437 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0022892 | -0.0042257 | -0.0021259 | 0.019613 | 0.030485 | 0.015432 | 0.028518 | 0.97207 | -0.054192 | 122.0616 | 121.9875 | 121.9145 | -0.044742 | 0.02852 | 0.064461 | -0.056351 | -0.089475 | 0.018285 | 0.071851 | -0.1092 | 0.055966 | 0.11792 | 0.12923 | 0.046516 | -0.00945 | 0.043823 | -0.029186 | -0.008495 | -122.0331 | 0.12923 | 0.044357 | 0.052852 | -121.9254 | -121.8718 | 122.1623 | 122.0882 | 122.0152 | 1.0728 | -121.9884 | 0.011233 | 0.11899 | 0.17256 | 0.16517 | -122.0529
2525.5625 | 122.1039 | -0.07782 | 121.9437 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0019123 | 0.019399 | 0.030698 | 0.015646 | 0.028518 | 0.99954 | -0.054192 | 122.0616 | 121.9921 | 121.9191 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.058115 | -0.10462 | 0.023921 | 0.11792 | 0.10634 | 0.023628 | -0.000293 | 0.048402 | -0.024608 | -0.026804 | -122.024 | 0.10176 | 0.021469 | 0.048273 | -121.9208 | -121.8855 | 122.1394 | 122.0699 | 121.9969 | 1.0774 | -121.9976 | -0.002498 | 0.10068 | 0.13594 | 0.15602 | -122.0483
2527.2656 | 122.0993 | -0.064087 | 121.962 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065141 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019399 | 0.030271 | 0.015646 | 0.023939 | 1.027 | -0.049614 | 122.0707 | 121.9875 | 121.9145 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.094053 | 0.018285 | 0.058115 | -0.1092 | 0.005609 | 0.10877 | 0.088026 | 0.014473 | 0.008864 | 0.025513 | -0.047496 | -0.045116 | -122.056 | 0.088028 | -0.001422 | 0.043694 | -121.9437 | -121.9039 | 122.1348 | 122.0516 | 121.9786 | 1.0911 | -122.0205 | -0.029966 | 0.082372 | 0.1222 | 0.14228 | -122.0712
2529.0312 | 122.0306 | -0.10529 | 121.9711 | 1.4211e-13 | -0.042384 | 0.0012179 | 0.065569 | -0.0093137 | 0.052897 | -0.0022892 | -0.0044395 | -0.0019123 | 0.019399 | 0.030057 | 0.015646 | 0.033096 | 1.0545 | -0.045036 | 122.0662 | 121.9966 | 121.9236 | -0.058478 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.046808 | 0.095034 | 0.13838 | 0.06025 | 0.013442 | 0.025516 | -0.047494 | 0.000662 | -122.0514 | 0.12465 | 0.039777 | 0.039115 | -121.9528 | -121.913 | 122.1715 | 122.1019 | 122.0289 | 1.1598 | -122.0296 | 0.024968 | 0.12357 | 0.1634 | 0.18348 | -122.0758
2530.7969 | 122.1222 | -0.086975 | 121.9894 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0093137 | 0.052897 | -0.02518 | -0.0044395 | -0.0016987 | 0.019827 | 0.030271 | 0.015432 | 0.028518 | 1.0957 | -0.054192 | 122.0662 | 121.9921 | 121.9191 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.009128 | 0.062694 | -0.10462 | 0.033076 | 0.076723 | 0.11549 | 0.032783 | -0.000293 | 0.002626 | -0.070384 | -0.017649 | -122.0743 | 0.11092 | 0.021466 | 0.039115 | -121.9803 | -121.9267 | 122.1531 | 122.079 | 122.006 | 1.1827 | -122.0433 | 0.002079 | 0.096103 | 0.14967 | 0.16517 | -122.0941
2532.5469 | 122.0444 | -0.10071 | 121.994 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019613 | 0.030057 | 0.015432 | 0.033096 | 1.1323 | -0.049614 | 122.0662 | 121.9921 | 121.9191 | -0.058478 | 0.019362 | 0.078197 | -0.056351 | -0.084896 | 0.018285 | 0.062694 | -0.1092 | 0.04223 | 0.072145 | 0.1338 | 0.051094 | 0.008864 | -0.001952 | -0.074962 | -0.008495 | -122.0789 | 0.12007 | 0.044357 | 0.052852 | -121.9757 | -121.9313 | 122.1669 | 122.0928 | 122.0198 | 1.233 | -122.0525 | 0.015812 | 0.11899 | 0.1634 | 0.17891 | -122.1032
2534.2969 | 122.0352 | -0.10986 | 121.9757 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.053324 | -0.02518 | -0.0044395 | -0.0014849 | 0.019827 | 0.030271 | 0.015219 | 0.033096 | 1.1735 | -0.049614 | 122.0707 | 121.9921 | 121.9236 | -0.058478 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.051385 | 0.095035 | 0.14296 | 0.060249 | 0.008864 | 0.016359 | -0.052072 | 0.00066 | -122.0606 | 0.12923 | 0.048933 | 0.048273 | -121.9574 | -121.9176 | 122.1806 | 122.1019 | 122.0335 | 1.2834 | -122.0342 | 0.024967 | 0.12815 | 0.16798 | 0.18348 | -122.0849
2536 | 122.1222 | -0.073242 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0095273 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019613 | 0.030057 | 0.015432 | 0.028518 | 1.201 | -0.054192 | 122.0707 | 121.9921 | 121.9236 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.067272 | -0.10462 | 0.019343 | 0.11792 | 0.10176 | 0.01905 | -0.000293 | 0.039247 | -0.029184 | -0.031382 | -122.0377 | 0.10176 | 0.007733 | 0.039115 | -121.9345 | -121.8855 | 122.144 | 122.0653 | 121.9969 | 1.2742 | -122.0067 | -0.011654 | 0.091527 | 0.14051 | 0.14686 | -122.0574
2537.7656 | 121.994 | -0.11444 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065355 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.015219 | 0.033096 | 1.2559 | -0.045036 | 122.0707 | 121.9966 | 121.9236 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.013707 | 0.067272 | -0.10462 | 0.060542 | 0.08588 | 0.14754 | 0.069405 | 0.008863 | 0.011783 | -0.061227 | 0.009817 | -122.0698 | 0.13838 | 0.048932 | 0.039115 | -121.9712 | -121.9176 | 122.1852 | 122.1111 | 122.0381 | 1.3704 | -122.0388 | 0.029545 | 0.12815 | 0.18171 | 0.18806 | -122.0895
2539.4531 | 122.1451 | -0.050354 | 121.9391 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065569 | -0.0093137 | 0.052897 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019613 | 0.030271 | 0.015219 | 0.033096 | 1.2972 | -0.054192 | 122.0616 | 121.9921 | 121.9236 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.10462 | 0.001033 | 0.1225 | 0.08345 | -0.003838 | -0.004871 | 0.05298 | -0.015451 | -0.05427 | -122.024 | 0.078874 | -0.010576 | 0.043694 | -121.9208 | -121.881 | 122.1119 | 122.0424 | 121.974 | 1.3475 | -121.9884 | -0.034542 | 0.068639 | 0.10847 | 0.12397 | -122.0437
2541.2188 | 122.1359 | -0.064087 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0020727 | 0.065355 | -0.0095273 | 0.052683 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030485 | 0.015432 | 0.028518 | 1.3338 | -0.045036 | 122.0616 | 121.9966 | 121.9236 | -0.049321 | 0.023941 | 0.06904 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.10462 | 0.014766 | 0.12708 | 0.092605 | 0.019051 | 0.004285 | 0.062137 | -0.010873 | -0.040537 | -122.0148 | 0.088028 | 0.003157 | 0.043694 | -121.9162 | -121.8764 | 122.1257 | 122.0607 | 121.9877 | 1.3979 | -121.9838 | -0.016231 | 0.082372 | 0.1222 | 0.13313 | -122.0391
2542.9844 | 122.081 | -0.10071 | 121.9757 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065355 | -0.0095273 | 0.052683 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.033096 | 1.3979 | -0.054192 | 122.0707 | 122.0012 | 121.9236 | -0.063057 | 0.033099 | 0.073618 | -0.06093 | -0.089475 | 0.027442 | 0.062694 | -0.1092 | 0.037651 | 0.095035 | 0.1338 | 0.046516 | 0.008865 | 0.025516 | -0.052072 | -0.008495 | -122.0652 | 0.13381 | 0.039778 | 0.048273 | -121.9483 | -121.913 | 122.1715 | 122.1019 | 122.0243 | 1.4986 | -122.0388 | 0.011233 | 0.12815 | 0.1634 | 0.17433 | -122.0849
2544.6875 | 122.049 | -0.10986 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065355 | -0.0095273 | 0.05311 | -0.01755 | -0.0044395 | -0.0012713 | 0.019613 | 0.030057 | 0.015432 | 0.033096 | 1.4391 | -0.049614 | 122.0662 | 121.9875 | 121.9236 | -0.044742 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.018285 | 0.062694 | -0.11378 | 0.065121 | 0.081301 | 0.14296 | 0.060249 | -0.004872 | 0.002625 | -0.061227 | -0.003919 | -122.0652 | 0.1338 | 0.053512 | 0.057431 | -121.9666 | -121.9222 | 122.176 | 122.0974 | 122.0335 | 1.549 | -122.0296 | 0.029545 | 0.12815 | 0.17256 | 0.18348 | -122.0986
2546.4531 | 122.1176 | -0.07782 | 121.9437 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065355 | -0.0097409 | 0.052897 | -0.01755 | -0.0044395 | -0.0019123 | 0.019399 | 0.030057 | 0.015219 | 0.033096 | 1.5032 | -0.049614 | 122.0707 | 121.9966 | 121.9145 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.028499 | 0.12708 | 0.11092 | 0.028206 | -0.000293 | 0.052981 | -0.029186 | -0.031383 | -122.0286 | 0.10176 | 0.012311 | 0.043694 | -121.9208 | -121.881 | 122.1486 | 122.0745 | 121.9923 | 1.581 | -121.993 | -0.007076 | 0.10068 | 0.14051 | 0.15602 | -122.0529
2548.2188 | 122.0901 | -0.082397 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065355 | -0.0095273 | 0.05311 | -0.01755 | -0.0040121 | -0.0016987 | 0.019186 | 0.030485 | 0.015432 | 0.028518 | 1.5444 | -0.049614 | 122.0662 | 121.9966 | 121.9191 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.018285 | 0.062694 | -0.11836 | 0.023919 | 0.11334 | 0.11091 | 0.032783 | 0.008864 | 0.043826 | -0.033763 | -0.035964 | -122.0286 | 0.10634 | 0.016888 | 0.052852 | -121.9345 | -121.8901 | 122.1486 | 122.079 | 122.0015 | 1.6268 | -122.0113 | 0.006658 | 0.10068 | 0.14509 | 0.16059 | -122.0712
2549.9844 | 122.1497 | -0.059509 | 121.9666 | 1.4211e-13 | -0.043025 | 0.0014317 | 0.065569 | -0.0095273 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.033096 | 1.5993 | -0.045036 | 122.0616 | 121.9966 | 121.9236 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.00561 | 0.095033 | 0.092605 | 0.014473 | 0.008863 | 0.030093 | -0.042917 | -0.049694 | -122.056 | 0.088029 | -0.006 | 0.043694 | -121.9437 | -121.9039 | 122.1211 | 122.0562 | 121.9831 | 1.6588 | -122.0205 | -0.029966 | 0.082373 | 0.1222 | 0.13313 | -122.0758
2551.6875 | 122.1451 | -0.07782 | 121.9391 | 1.4211e-13 | -0.042384 | 0.0020727 | 0.065355 | -0.0097409 | 0.05311 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019613 | 0.030271 | 0.014791 | 0.033096 | 1.6497 | -0.049614 | 122.0707 | 121.9966 | 121.9236 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.013707 | 0.062694 | -0.11378 | 0.023921 | 0.13166 | 0.11092 | 0.028206 | 0.004285 | 0.057559 | -0.015451 | -0.035962 | -122.0286 | 0.10176 | 0.021469 | 0.057431 | -121.9254 | -121.8764 | 122.1486 | 122.0745 | 122.0015 | 1.7275 | -121.993 | -0.011655 | 0.091527 | 0.14051 | 0.15144 | -122.0529
2553.4531 | 122.0993 | -0.091553 | 121.9528 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065569 | -0.0093137 | 0.052897 | -0.0022892 | -0.0037985 | -0.0016987 | 0.019827 | 0.030698 | 0.015859 | 0.033096 | 1.6909 | -0.054192 | 122.0662 | 121.9921 | 121.9145 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.1092 | 0.033075 | 0.11334 | 0.12465 | 0.037361 | 0.004286 | 0.039247 | -0.038341 | -0.01765 | -122.0423 | 0.11549 | 0.026044 | 0.043694 | -121.9391 | -121.8901 | 122.1577 | 122.0836 | 122.006 | 1.7825 | -122.0113 | 0.002078 | 0.10526 | 0.15425 | 0.16975 | -122.062
2555.1562 | 122.0123 | -0.11444 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0097409 | 0.05311 | -0.01755 | -0.0040121 | -0.0014849 | 0.019613 | 0.030698 | 0.015432 | 0.033096 | 1.7459 | -0.045036 | 122.0662 | 122.0012 | 121.9191 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.060542 | 0.11334 | 0.14754 | 0.069405 | 0.008863 | 0.048404 | -0.033763 | 0.005238 | -122.0331 | 0.13838 | 0.05809 | 0.052852 | -121.93 | -121.8901 | 122.1806 | 122.1157 | 122.0335 | 1.8603 | -122.0067 | 0.034123 | 0.13731 | 0.17713 | 0.18806 | -122.062
2556.9219 | 122.0856 | -0.073242 | 121.962 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065355 | -0.0095273 | 0.052897 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015646 | 0.033096 | 1.8054 | -0.045036 | 122.0707 | 121.9966 | 121.9236 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.013707 | 0.058115 | -0.1092 | 0.019343 | 0.10877 | 0.10634 | 0.028206 | 0.008863 | 0.034671 | -0.038339 | -0.035961 | -122.0423 | 0.092604 | 0.012312 | 0.048273 | -121.9483 | -121.9039 | 122.144 | 122.0699 | 121.9969 | 1.8786 | -122.0159 | -0.007076 | 0.086949 | 0.13136 | 0.14686 | -122.0712
2558.625 | 122.1268 | -0.064087 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065782 | -0.0095273 | 0.05311 | -0.0022892 | -0.0037985 | -0.0016987 | 0.019186 | 0.030485 | 0.015646 | 0.037675 | 1.8649 | -0.045036 | 122.0707 | 121.9921 | 121.9282 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.094053 | 0.018285 | 0.062694 | -0.1092 | 0.014766 | 0.11792 | 0.10176 | 0.019051 | 0.004285 | 0.039247 | -0.024606 | -0.045116 | -122.0469 | 0.088028 | 0.007736 | 0.052852 | -121.9345 | -121.8901 | 122.1348 | 122.0562 | 121.9923 | 1.929 | -122.0021 | -0.029966 | 0.082372 | 0.12678 | 0.14228 | -122.062
2560.3906 | 122.0352 | -0.086975 | 121.9894 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065141 | -0.0093137 | 0.052897 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019613 | 0.030271 | 0.015432 | 0.033096 | 1.9244 | -0.049614 | 122.0662 | 121.9966 | 121.9191 | -0.058478 | 0.02852 | 0.06904 | -0.056351 | -0.084896 | 0.013707 | 0.053537 | -0.10462 | 0.028497 | 0.076723 | 0.12007 | 0.037361 | 0.008864 | 0.007205 | -0.070384 | -0.017649 | -122.0743 | 0.1155 | 0.030624 | 0.048273 | -121.9757 | -121.9359 | 122.1531 | 122.0836 | 122.006 | 2.0114 | -122.0479 | 0.002079 | 0.10068 | 0.14051 | 0.15602 | -122.0941
2562.0938 | 122.1039 | -0.07782 | 121.9299 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0095273 | 0.05311 | -0.02518 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.015219 | 0.037675 | 1.9244 | -0.049614 | 122.0662 | 122.0012 | 121.9236 | -0.044742 | 0.014784 | 0.073618 | -0.065509 | -0.094053 | 0.018285 | 0.067272 | -0.10462 | 0.033078 | 0.13623 | 0.1155 | 0.028206 | -0.004872 | 0.071292 | -0.006296 | -0.026804 | -122.024 | 0.092604 | 0.012311 | 0.039115 | -121.9116 | -121.8627 | 122.144 | 122.079 | 122.0015 | 2.0022 | -121.9747 | -0.016233 | 0.096105 | 0.14509 | 0.15144 | -122.0346
2563.8438 | 122.1542 | -0.050354 | 121.9666 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065141 | -0.0095273 | 0.053324 | -0.01755 | -0.0042257 | -0.0019123 | 0.019613 | 0.030271 | 0.015432 | 0.037675 | 2.016 | -0.049614 | 122.0707 | 121.9875 | 121.9236 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | -0.003545 | 0.10419 | 0.088029 | 0.00074 | 0.004285 | 0.020935 | -0.042917 | -0.058849 | -122.0469 | 0.069716 | -0.010576 | 0.048273 | -121.9437 | -121.8993 | 122.1211 | 122.0378 | 121.974 | 2.0663 | -122.0205 | -0.029964 | 0.073218 | 0.11763 | 0.12397 | -122.0758
2565.625 | 122.0032 | -0.1236 | 121.9894 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065355 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.030485 | 0.015646 | 0.037675 | 2.0709 | -0.045036 | 122.0707 | 121.9966 | 121.9236 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.094053 | 0.027442 | 0.062694 | -0.10462 | 0.065118 | 0.081302 | 0.16127 | 0.07856 | 0.013442 | 0.007205 | -0.065805 | 0.018972 | -122.0835 | 0.14296 | 0.062666 | 0.043694 | -121.962 | -121.9267 | 122.1943 | 122.1202 | 122.0472 | 2.1945 | -122.0479 | 0.029543 | 0.15104 | 0.18629 | 0.20179 | -122.0941
2567.3125 | 122.0352 | -0.11902 | 121.994 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065355 | -0.0097409 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019613 | 0.030698 | 0.015432 | 0.037675 | 2.135 | -0.045036 | 122.0753 | 122.0012 | 121.9236 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.013707 | 0.058115 | -0.10462 | 0.06512 | 0.081302 | 0.15669 | 0.073983 | 0.008863 | 0.007205 | -0.070383 | 0.014395 | -122.0835 | 0.14296 | 0.058089 | 0.043694 | -121.9803 | -121.9359 | 122.1943 | 122.1202 | 122.0427 | 2.2541 | -122.0479 | 0.029544 | 0.13273 | 0.17713 | 0.19722 | -122.0986
2569.0781 | 122.0856 | -0.09613 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0012179 | 0.065355 | -0.0095273 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019827 | 0.030485 | 0.015432 | 0.037675 | 2.2037 | -0.049614 | 122.0616 | 121.9921 | 121.9236 | -0.049321 | 0.02852 | 0.073618 | -0.070087 | -0.084896 | 0.027442 | 0.062694 | -0.10004 | 0.046809 | 0.1225 | 0.13381 | 0.046516 | -0.000293 | 0.05298 | -0.015451 | -0.003915 | -122.024 | 0.12465 | 0.026043 | 0.029958 | -121.9116 | -121.8764 | 122.1577 | 122.0882 | 122.0198 | 2.2998 | -121.9884 | 0.011234 | 0.12357 | 0.15882 | 0.16975 | -122.0391
2570.7812 | 122.0215 | -0.11902 | 121.9757 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.064928 | -0.0095273 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030271 | 0.015219 | 0.033096 | 2.2495 | -0.045036 | 122.0707 | 122.0012 | 121.9236 | -0.053899 | 0.02852 | 0.073618 | -0.070087 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.06512 | 0.095035 | 0.15212 | 0.073983 | 0.008863 | 0.025516 | -0.052072 | 0.014395 | -122.0652 | 0.14754 | 0.048932 | 0.034537 | -121.9574 | -121.913 | 122.1898 | 122.1202 | 122.0427 | 2.3685 | -122.0296 | 0.029544 | 0.1373 | 0.18171 | 0.19264 | -122.0803
2572.5469 | 122.1039 | -0.07782 | 121.9528 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065355 | -0.0093137 | 0.05311 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019827 | 0.030698 | 0.015646 | 0.033096 | 2.3182 | -0.049614 | 122.0662 | 122.0012 | 121.9328 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.023921 | 0.11334 | 0.11092 | 0.028206 | 0.004285 | 0.048404 | -0.020027 | -0.026804 | -122.0377 | 0.10176 | 0.01689 | 0.043694 | -121.9254 | -121.8901 | 122.144 | 122.079 | 122.0106 | 2.396 | -122.0067 | -0.007076 | 0.10526 | 0.14051 | 0.1606 | -122.0574
2574.2969 | 122.0215 | -0.11444 | 121.9803 | 1.4211e-13 | -0.042384 | 0.0012179 | 0.065355 | -0.0097409 | 0.052897 | -0.01755 | -0.0044395 | -0.0016987 | 0.019827 | 0.030271 | 0.015219 | 0.037675 | 2.3914 | -0.040457 | 122.0662 | 121.9966 | 121.9236 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.1092 | 0.060542 | 0.085878 | 0.15212 | 0.073984 | 0.013442 | 0.01636 | -0.05665 | 0.005238 | -122.0652 | 0.13838 | 0.053511 | 0.048273 | -121.9666 | -121.9222 | 122.1806 | 122.1111 | 122.0381 | 2.5059 | -122.0342 | 0.029545 | 0.12815 | 0.17256 | 0.19264 | -122.0895
2576 | 122.1268 | -0.064087 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0095273 | 0.052897 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019827 | 0.030485 | 0.015005 | 0.042253 | 2.4555 | -0.045036 | 122.0662 | 122.0012 | 121.9191 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.010188 | 0.13165 | 0.10634 | 0.019051 | 0.008863 | 0.066715 | -0.015452 | -0.045116 | -122.0194 | 0.088028 | 0.003157 | 0.048273 | -121.9116 | -121.8718 | 122.1303 | 122.0653 | 121.9831 | 2.5196 | -121.9884 | -0.020809 | 0.086951 | 0.12678 | 0.14686 | -122.0437
2577.7656 | 122.1085 | -0.073242 | 121.9437 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065355 | -0.0093137 | 0.053324 | -0.01755 | -0.0042257 | -0.0016987 | 0.019827 | 0.030485 | 0.015219 | 0.033096 | 2.5288 | -0.045036 | 122.0753 | 121.9966 | 121.9236 | -0.058478 | 0.02852 | 0.06904 | -0.065509 | -0.084896 | 0.018285 | 0.048958 | -0.1092 | 0.014764 | 0.13166 | 0.10634 | 0.028206 | 0.013442 | 0.052981 | -0.020029 | -0.035961 | -122.0286 | 0.10176 | 0.007733 | 0.043694 | -121.9254 | -121.8947 | 122.1486 | 122.0699 | 121.9969 | 2.602 | -122.0021 | -0.011654 | 0.091527 | 0.1222 | 0.14228 | -122.0529
2579.5156 | 122.0215 | -0.10986 | 122.0078 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065569 | -0.0095273 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.030485 | 0.015432 | 0.046831 | 2.57 | -0.045036 | 122.0753 | 121.9966 | 121.9282 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.022864 | 0.058115 | -0.10462 | 0.055964 | 0.06757 | 0.15669 | 0.064827 | 0.008863 | -0.011105 | -0.079537 | 0.005239 | -122.0972 | 0.1338 | 0.044354 | 0.039115 | -121.9849 | -121.9496 | 122.1852 | 122.1065 | 122.0381 | 2.6799 | -122.0617 | 0.020388 | 0.13273 | 0.16798 | 0.18806 | -122.1124
2581.2812 | 122.1588 | -0.07782 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0014849 | 0.019613 | 0.030485 | 0.015219 | 0.042253 | 2.6524 | -0.040457 | 122.0707 | 121.9921 | 121.9282 | -0.049321 | 0.019362 | 0.073618 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.11378 | 0.028499 | 0.11792 | 0.12007 | 0.037363 | 0.008864 | 0.039247 | -0.024606 | -0.035962 | -122.0377 | 0.097182 | 0.012311 | 0.048273 | -121.9345 | -121.8901 | 122.1486 | 122.0699 | 122.006 | 2.7302 | -122.0021 | -0.007076 | 0.096105 | 0.14051 | 0.15144 | -122.0666
2582.9844 | 122.0169 | -0.1236 | 121.9711 | 1.4211e-13 | -0.042384 | 0.0018589 | 0.065782 | -0.0097409 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.030057 | 0.015432 | 0.046831 | 2.7211 | -0.045036 | 122.0707 | 122.0012 | 121.9282 | -0.049321 | 0.019362 | 0.078197 | -0.056351 | -0.089475 | 0.022864 | 0.058115 | -0.10462 | 0.074275 | 0.099613 | 0.17043 | 0.07856 | 0.004285 | 0.030094 | -0.042916 | 0.018972 | -122.0606 | 0.14296 | 0.067245 | 0.048273 | -121.9483 | -121.913 | 122.1943 | 122.1248 | 122.0518 | 2.8447 | -122.0205 | 0.034121 | 0.14646 | 0.18171 | 0.20179 | -122.0758
2584.75 | 122.168 | -0.068665 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0090999 | 0.052897 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019613 | 0.030271 | 0.015219 | 0.042253 | 2.7989 | -0.049614 | 122.0707 | 122.0058 | 121.9236 | -0.049321 | 0.019362 | 0.073618 | -0.070087 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.019344 | 0.13166 | 0.11092 | 0.019051 | -0.000293 | 0.066716 | -0.015451 | -0.040538 | -122.024 | 0.088027 | -0.001422 | 0.039116 | -121.9162 | -121.881 | 122.1394 | 122.0745 | 121.9923 | 2.8676 | -121.9884 | -0.016231 | 0.091529 | 0.12678 | 0.14228 | -122.0483
2586.5 | 122.049 | -0.12817 | 121.9894 | 1.4211e-13 | -0.04217 | 0.0016453 | 0.065355 | -0.0093137 | 0.052897 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030485 | 0.015432 | 0.042253 | 2.8493 | -0.045036 | 122.0753 | 122.0012 | 121.9328 | -0.049321 | 0.033099 | 0.078197 | -0.065509 | -0.094053 | 0.027442 | 0.062694 | -0.11378 | 0.078853 | 0.08588 | 0.17043 | 0.083138 | 0.004285 | 0.011783 | -0.056648 | 0.014392 | -122.0835 | 0.16127 | 0.062665 | 0.048273 | -121.962 | -121.9267 | 122.2035 | 122.1294 | 122.061 | 2.9775 | -122.0388 | 0.034121 | 0.15562 | 0.19087 | 0.20637 | -122.1032
2588.2656 | 122.1359 | -0.073242 | 121.9299 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0095273 | 0.05311 | -0.01755 | -0.0044395 | -0.0014849 | 0.019613 | 0.030485 | 0.015646 | 0.042253 | 2.9409 | -0.045036 | 122.0707 | 121.9966 | 121.9282 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.053537 | -0.1092 | 0.014764 | 0.14081 | 0.1155 | 0.028206 | 0.013442 | 0.066714 | -0.001718 | -0.035961 | -122.0148 | 0.097183 | 0.012312 | 0.048273 | -121.9162 | -121.8764 | 122.144 | 122.0699 | 122.0015 | 3.0141 | -121.9884 | -0.011654 | 0.086949 | 0.12678 | 0.15144 | -122.0391
2589.9688 | 122.0123 | -0.10986 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065355 | -0.0097409 | 0.05311 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019613 | 0.029844 | 0.015432 | 0.046831 | 3.0141 | -0.049614 | 122.0753 | 122.0012 | 121.9282 | -0.058478 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.051385 | 0.090458 | 0.15669 | 0.060249 | 0.008864 | 0.016361 | -0.056649 | 0.00066 | -122.0652 | 0.13838 | 0.044354 | 0.043694 | -121.962 | -121.9222 | 122.1852 | 122.1111 | 122.0381 | 3.124 | -122.0433 | 0.029545 | 0.13273 | 0.17256 | 0.18806 | -122.0941
2591.7344 | 122.0169 | -0.11902 | 121.9757 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065355 | -0.0093137 | 0.05311 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.042253 | 3.1057 | -0.040457 | 122.0662 | 122.0012 | 121.9328 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.013707 | 0.067272 | -0.1092 | 0.060541 | 0.090456 | 0.16127 | 0.078562 | 0.018021 | 0.025516 | -0.042915 | 0.009816 | -122.0606 | 0.14296 | 0.05351 | 0.043694 | -121.962 | -121.9084 | 122.1852 | 122.1202 | 122.0518 | 3.2247 | -122.0342 | 0.034123 | 0.13273 | 0.18629 | 0.19722 | -122.0849
2593.4844 | 122.0261 | -0.12817 | 122.0078 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019186 | 0.030057 | 0.015646 | 0.046831 | 3.1835 | -0.040457 | 122.0707 | 121.9966 | 121.9282 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.089475 | 0.018285 | 0.062694 | -0.1092 | 0.074275 | 0.062992 | 0.17501 | 0.087717 | 0.013442 | -0.011105 | -0.079537 | 0.018971 | -122.0972 | 0.15212 | 0.071823 | 0.052852 | -121.9895 | -121.9451 | 122.1989 | 122.1248 | 122.0564 | 3.3117 | -122.0617 | 0.038699 | 0.14646 | 0.19087 | 0.20179 | -122.117
2595.1875 | 122.1313 | -0.07782 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0090999 | 0.05311 | -0.01755 | -0.0044395 | -0.0014849 | 0.019613 | 0.030485 | 0.015432 | 0.046831 | 3.266 | -0.045036 | 122.0662 | 121.9875 | 121.9282 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.028499 | 0.12708 | 0.12465 | 0.032784 | 0.004285 | 0.048401 | -0.010873 | -0.026804 | -122.0194 | 0.10176 | 0.01689 | 0.043694 | -121.9162 | -121.8764 | 122.144 | 122.0653 | 122.006 | 3.3438 | -121.9884 | -0.002498 | 0.10068 | 0.14051 | 0.15144 | -122.0437
2596.9688 | 122.0535 | -0.10529 | 121.9757 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0099547 | 0.05311 | -0.0022892 | -0.0042257 | -0.0019123 | 0.019186 | 0.030485 | 0.015859 | 0.042253 | 3.3392 | -0.040457 | 122.0707 | 121.9921 | 121.9328 | -0.049321 | 0.02852 | 0.073618 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.055965 | 0.095035 | 0.14754 | 0.064829 | 0.008864 | 0.016359 | -0.042915 | 0.000662 | -122.056 | 0.13381 | 0.039777 | 0.039115 | -121.9574 | -121.9084 | 122.176 | 122.0974 | 122.0381 | 3.4445 | -122.025 | 0.024968 | 0.12357 | 0.17256 | 0.1789 | -122.0803
2598.6719 | 122.1359 | -0.073242 | 121.9574 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065355 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030271 | 0.015432 | 0.042253 | 3.4079 | -0.040457 | 122.0707 | 122.0058 | 121.9282 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.058115 | -0.11378 | 0.023921 | 0.11335 | 0.1155 | 0.032785 | 0.008864 | 0.048406 | -0.029183 | -0.04054 | -122.0377 | 0.097183 | 0.007733 | 0.048273 | -121.93 | -121.8993 | 122.144 | 122.079 | 122.0015 | 3.4811 | -122.0067 | -0.007076 | 0.10068 | 0.13136 | 0.15144 | -122.0712
2600.4219 | 122.0261 | -0.14648 | 122.0078 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065355 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030271 | 0.015432 | 0.042253 | 3.4949 | -0.040457 | 122.0707 | 122.0012 | 121.9374 | -0.049321 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.022864 | 0.053537 | -0.10462 | 0.097163 | 0.062992 | 0.18874 | 0.10603 | 0.008864 | -0.006527 | -0.070379 | 0.04186 | -122.0926 | 0.17042 | 0.080975 | 0.039115 | -121.9849 | -121.9542 | 122.2172 | 122.1477 | 122.0839 | 3.6414 | -122.0571 | 0.061588 | 0.16935 | 0.20002 | 0.2201 | -122.1124
2602.1875 | 122.0169 | -0.10986 | 122.0032 | 1.4211e-13 | -0.04217 | 0.0014317 | 0.065569 | -0.0097409 | 0.05311 | -0.01755 | -0.0037985 | -0.0016987 | 0.019613 | 0.030485 | 0.015432 | 0.042253 | 3.5819 | -0.035879 | 122.0753 | 122.0012 | 121.9328 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.084896 | 0.027442 | 0.058115 | -0.1092 | 0.055964 | 0.072147 | 0.15212 | 0.073984 | 0.01802 | -0.00195 | -0.070381 | 0.00066 | -122.0881 | 0.1338 | 0.053512 | 0.052852 | -121.9757 | -121.9451 | 122.1852 | 122.1111 | 122.0427 | 3.6917 | -122.0571 | 0.024967 | 0.13731 | 0.16798 | 0.18348 | -122.1124
2603.9531 | 122.0993 | -0.07782 | 121.9574 | 1.4211e-13 | -0.042384 | 0.0014317 | 0.065141 | -0.0095273 | 0.05311 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019613 | 0.030271 | 0.015646 | 0.05141 | 3.678 | -0.031301 | 122.0616 | 122.0012 | 121.9328 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.080318 | 0.027442 | 0.058115 | -0.10462 | 0.023921 | 0.10419 | 0.12923 | 0.046519 | 0.022598 | 0.043827 | -0.024604 | -0.026804 | -122.0377 | 0.10176 | 0.012311 | 0.039115 | -121.93 | -121.8993 | 122.1394 | 122.079 | 122.0106 | 3.7558 | -122.0113 | -0.002498 | 0.10526 | 0.13594 | 0.15144 | -122.062
2605.6562 | 122.1542 | -0.059509 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065569 | -0.0095273 | 0.05311 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.05141 | 3.7513 | -0.035879 | 122.0753 | 122.0104 | 121.9328 | -0.063057 | 0.033099 | 0.078197 | -0.06093 | -0.089475 | 0.027442 | 0.071851 | -0.1092 | -0.003548 | 0.11792 | 0.11092 | 0.02363 | 0.027178 | 0.052985 | -0.024604 | -0.049694 | -122.0469 | 0.092608 | -0.001421 | 0.048273 | -121.93 | -121.8855 | 122.1348 | 122.0699 | 121.9923 | 3.8108 | -122.0205 | -0.029966 | 0.086951 | 0.13136 | 0.13771 | -122.0666
2607.3594 | 122.0718 | -0.09613 | 121.994 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065355 | -0.0095273 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.055988 | 3.8337 | -0.040457 | 122.0753 | 121.9966 | 121.9374 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.027442 | 0.071851 | -0.1092 | 0.046809 | 0.081302 | 0.15212 | 0.055673 | 0.008864 | 0.002627 | -0.056647 | -0.013073 | -122.0835 | 0.12007 | 0.039779 | 0.052852 | -121.9666 | -121.9222 | 122.1715 | 122.0928 | 122.0335 | 3.9298 | -122.0433 | 0.006655 | 0.12357 | 0.16798 | 0.17433 | -122.1032
2609.0469 | 122.1085 | -0.07782 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.05141 | 3.9161 | -0.035879 | 122.0662 | 121.9966 | 121.9236 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.022864 | 0.067272 | -0.11378 | 0.023921 | 0.11334 | 0.12923 | 0.041941 | 0.01802 | 0.043826 | -0.029184 | -0.035962 | -122.0286 | 0.10176 | 0.01689 | 0.052852 | -121.93 | -121.8855 | 122.144 | 122.0745 | 122.0015 | 3.9939 | -122.0067 | 0.002081 | 0.10068 | 0.14509 | 0.15144 | -122.0666
2610.8125 | 122.1451 | -0.068665 | 121.9574 | 1.4211e-13 | -0.043025 | 0.0014317 | 0.065782 | -0.0090999 | 0.05311 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.030271 | 0.015005 | 0.042253 | 3.9894 | -0.035879 | 122.0707 | 122.0012 | 121.9282 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10004 | 0.010187 | 0.11335 | 0.11092 | 0.032786 | 0.022599 | 0.043827 | -0.029183 | -0.03138 | -122.0423 | 0.097185 | 0.007735 | 0.039115 | -121.93 | -121.8947 | 122.1394 | 122.0699 | 121.9969 | 4.058 | -122.0159 | -0.016231 | 0.096107 | 0.13136 | 0.14686 | -122.0574
2612.5312 | 122.1222 | -0.068665 | 121.9757 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065782 | -0.0093137 | 0.052683 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019613 | 0.030485 | 0.015859 | 0.046831 | 4.0718 | -0.035879 | 122.0707 | 122.0058 | 121.9236 | -0.053899 | 0.023941 | 0.06904 | -0.065509 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.014766 | 0.095035 | 0.1155 | 0.032786 | 0.01802 | 0.030095 | -0.052072 | -0.040538 | -122.056 | 0.092606 | 0.003156 | 0.043694 | -121.9574 | -121.913 | 122.1394 | 122.0745 | 121.9923 | 4.1404 | -122.0296 | -0.011653 | 0.08695 | 0.13136 | 0.13771 | -122.0849
2614.2969 | 122.1085 | -0.082397 | 121.9849 | 1.4211e-13 | -0.04217 | 0.0018589 | 0.065355 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.046831 | 4.1542 | -0.035879 | 122.0707 | 121.9966 | 121.9282 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.028498 | 0.08588 | 0.12923 | 0.046518 | 0.01802 | 0.011783 | -0.056649 | -0.031385 | -122.0698 | 0.10176 | 0.021467 | 0.052852 | -121.962 | -121.9222 | 122.1531 | 122.079 | 122.0106 | 4.2366 | -122.0388 | -0.002499 | 0.10526 | 0.14509 | 0.16059 | -122.0986
2616 | 122.0352 | -0.1236 | 121.9894 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0090999 | 0.052897 | 0.0053413 | -0.0042257 | -0.0016987 | 0.019399 | 0.030271 | 0.015432 | 0.055988 | 4.2458 | -0.040457 | 122.0707 | 122.0012 | 121.9328 | -0.049321 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.074275 | 0.081302 | 0.17958 | 0.083139 | 0.008864 | 0.011783 | -0.056648 | 0.014393 | -122.0743 | 0.15212 | 0.058087 | 0.043694 | -121.9666 | -121.9267 | 122.1943 | 122.1248 | 122.0564 | 4.3694 | -122.0388 | 0.0387 | 0.14646 | 0.18629 | 0.20179 | -122.0986
2617.7812 | 122.0078 | -0.10529 | 121.994 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065355 | -0.0095273 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019613 | 0.030485 | 0.015432 | 0.055988 | 4.3099 | -0.035879 | 122.0753 | 122.0058 | 121.9328 | -0.053899 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.1092 | 0.051387 | 0.081302 | 0.16127 | 0.069407 | 0.01802 | 0.011784 | -0.061226 | -0.003917 | -122.0789 | 0.12923 | 0.039777 | 0.043694 | -121.9757 | -121.9313 | 122.1806 | 122.1111 | 122.0381 | 4.4152 | -122.0479 | 0.02039 | 0.12357 | 0.16798 | 0.18806 | -122.1032
2619.4688 | 122.1542 | -0.068665 | 121.962 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065355 | -0.0095273 | 0.053538 | 0.0053413 | -0.0042257 | -0.0019123 | 0.019613 | 0.030271 | 0.015219 | 0.055988 | 4.3511 | -0.031301 | 122.0753 | 122.0012 | 121.9282 | -0.058478 | 0.023941 | 0.082776 | -0.056351 | -0.089475 | 0.022864 | 0.053537 | -0.10462 | 0.010187 | 0.11335 | 0.12465 | 0.037364 | 0.027177 | 0.039249 | -0.033761 | -0.035959 | -122.0514 | 0.092606 | 0.012314 | 0.048273 | -121.9391 | -121.9084 | 122.144 | 122.0699 | 121.9969 | 4.4197 | -122.0205 | -0.02081 | 0.091529 | 0.1222 | 0.15144 | -122.0666
2621.1562 | 122.1313 | -0.082397 | 121.9803 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030057 | 0.015432 | 0.055988 | 4.4884 | -0.035879 | 122.0707 | 122.0012 | 121.9374 | -0.058478 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.023919 | 0.090457 | 0.13839 | 0.046518 | 0.022599 | 0.020938 | -0.042914 | -0.026806 | -122.0606 | 0.10176 | 0.026046 | 0.052852 | -121.9574 | -121.9222 | 122.1531 | 122.0836 | 122.0198 | 4.5708 | -122.0388 | 0.002079 | 0.10526 | 0.14051 | 0.16059 | -122.0895
2622.9219 | 122.0581 | -0.09613 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065355 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019613 | 0.030698 | 0.015219 | 0.055988 | 4.5205 | -0.035879 | 122.0753 | 121.9966 | 121.9328 | -0.058478 | 0.014784 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.037652 | 0.11792 | 0.15212 | 0.060251 | 0.022599 | 0.039249 | -0.024604 | -0.008494 | -122.0423 | 0.11091 | 0.0352 | 0.043694 | -121.9345 | -121.8947 | 122.1715 | 122.0928 | 122.0289 | 4.6166 | -122.0159 | 0.011234 | 0.11899 | 0.15882 | 0.17891 | -122.062
2624.6875 | 122.1405 | -0.064087 | 121.9299 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065569 | -0.0097409 | 0.053324 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019827 | 0.030271 | 0.015219 | 0.060567 | 4.6029 | -0.035879 | 122.0753 | 122.0012 | 121.9374 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.032021 | 0.058115 | -0.1092 | 0.010188 | 0.14539 | 0.12465 | 0.028208 | 0.01802 | 0.071292 | 0.00744 | -0.045116 | -122.0102 | 0.088028 | 0.003157 | 0.048273 | -121.8979 | -121.8718 | 122.1394 | 122.0653 | 122.0015 | 4.667 | -121.9838 | -0.016231 | 0.096108 | 0.1222 | 0.14228 | -122.0391
2626.3906 | 122.1634 | -0.082397 | 121.9711 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065355 | -0.0095273 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015432 | 0.055988 | 4.6716 | -0.026723 | 122.0662 | 122.0104 | 121.942 | -0.049321 | 0.019362 | 0.073618 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.033076 | 0.095034 | 0.13839 | 0.055674 | 0.022598 | 0.039252 | -0.02918 | -0.031385 | -122.056 | 0.10176 | 0.021467 | 0.052852 | -121.9437 | -121.9039 | 122.1486 | 122.0928 | 122.0243 | 4.754 | -122.0205 | -0.002499 | 0.10984 | 0.14967 | 0.15602 | -122.0849
2628.1562 | 122.0535 | -0.086975 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0095273 | 0.052897 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019827 | 0.030485 | 0.015219 | 0.055988 | 4.7448 | -0.031301 | 122.0753 | 122.0012 | 121.9374 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.033076 | 0.11792 | 0.14296 | 0.055674 | 0.022598 | 0.043827 | -0.020025 | -0.017649 | -122.0423 | 0.1155 | 0.026045 | 0.043694 | -121.93 | -121.8947 | 122.1623 | 122.0882 | 122.0243 | 4.8318 | -122.0113 | 0.002079 | 0.11442 | 0.14967 | 0.16517 | -122.062
2629.9219 | 121.9757 | -0.10529 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065355 | -0.0095273 | 0.05311 | -0.01755 | -0.0044395 | -0.0016987 | 0.019613 | 0.030698 | 0.015219 | 0.05141 | 4.8318 | -0.040457 | 122.0707 | 122.0104 | 121.9328 | -0.058478 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.046808 | 0.08588 | 0.1567 | 0.064829 | 0.018021 | 0.025519 | -0.05207 | 0.000662 | -122.0698 | 0.12923 | 0.039777 | 0.039115 | -121.9574 | -121.9222 | 122.176 | 122.1157 | 122.0381 | 4.9371 | -122.0433 | 0.02039 | 0.13273 | 0.16798 | 0.18806 | -122.0895
2631.6406 | 122.0535 | -0.10529 | 121.9528 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0095273 | 0.05311 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019399 | 0.030698 | 0.015005 | 0.055988 | 4.9097 | -0.035879 | 122.0753 | 121.9966 | 121.9328 | -0.058478 | 0.019362 | 0.073618 | -0.065509 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.046808 | 0.1225 | 0.16127 | 0.069407 | 0.022599 | 0.043826 | -0.020027 | -0.003917 | -122.0331 | 0.12465 | 0.039777 | 0.043694 | -121.93 | -121.8901 | 122.1806 | 122.1019 | 122.0381 | 5.015 | -122.0113 | 0.024968 | 0.12815 | 0.16798 | 0.1789 | -122.062
2633.4062 | 122.0444 | -0.11444 | 121.9986 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019613 | 0.030271 | 0.015646 | 0.065145 | 5.0012 | -0.035879 | 122.0753 | 122.0058 | 121.9374 | -0.049321 | 0.014784 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.062694 | -0.11836 | 0.06512 | 0.076725 | 0.17959 | 0.078562 | 0.013442 | 0.007207 | -0.061224 | -0.00392 | -122.0881 | 0.12923 | 0.053511 | 0.057431 | -121.9757 | -121.9359 | 122.1898 | 122.1202 | 122.0518 | 5.1157 | -122.0479 | 0.024966 | 0.13731 | 0.17713 | 0.19264 | -122.117
2635.1719 | 122.0398 | -0.11444 | 122.0078 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0093137 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.030485 | 0.015432 | 0.060567 | 5.0882 | -0.031301 | 122.0707 | 122.0012 | 121.9374 | -0.058478 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.067272 | -0.10462 | 0.055963 | 0.062992 | 0.17501 | 0.08314 | 0.027177 | -0.006527 | -0.070379 | 0.009817 | -122.0881 | 0.1338 | 0.048932 | 0.039115 | -121.9803 | -121.9405 | 122.1852 | 122.1157 | 122.0518 | 5.2027 | -122.0662 | 0.034123 | 0.14188 | 0.18171 | 0.19264 | -122.1124
2636.9375 | 122.1359 | -0.059509 | 121.9345 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019399 | 0.030271 | 0.015432 | 0.060567 | 5.1569 | -0.035879 | 122.0707 | 121.9966 | 121.9374 | -0.063057 | 0.014784 | 0.06904 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.1092 | -0.003548 | 0.13623 | 0.12008 | 0.02363 | 0.027178 | 0.062137 | 0.002863 | -0.049694 | -122.0194 | 0.074293 | -0.006 | 0.043694 | -121.9162 | -121.8718 | 122.1303 | 122.0562 | 121.9969 | 5.2164 | -121.9976 | -0.025387 | 0.077794 | 0.1222 | 0.12855 | -122.0437
2638.6406 | 121.994 | -0.11444 | 121.994 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065569 | -0.0095273 | 0.053538 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019613 | 0.030057 | 0.015219 | 0.055988 | 5.2485 | -0.035879 | 122.0753 | 122.0104 | 121.942 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.060542 | 0.081302 | 0.17043 | 0.078562 | 0.01802 | 0.016363 | -0.052069 | 0.009817 | -122.0789 | 0.13838 | 0.053511 | 0.043694 | -121.9666 | -121.9313 | 122.1898 | 122.1248 | 122.0564 | 5.3629 | -122.0479 | 0.029545 | 0.14188 | 0.17713 | 0.19264 | -122.0986
2640.4062 | 122.0032 | -0.11902 | 121.9894 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0095273 | 0.05311 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.030698 | 0.015432 | 0.060567 | 5.3355 | -0.031301 | 122.0753 | 122.0104 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.018285 | 0.062694 | -0.1092 | 0.06512 | 0.08588 | 0.17959 | 0.087718 | 0.022598 | 0.020941 | -0.042912 | 0.009816 | -122.0652 | 0.14296 | 0.058089 | 0.048273 | -121.9712 | -121.9267 | 122.1943 | 122.1294 | 122.0655 | 5.4545 | -122.0433 | 0.04328 | 0.1373 | 0.18171 | 0.19722 | -122.0986
2642.1719 | 122.113 | -0.050354 | 121.9666 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065355 | -0.0097409 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030057 | 0.015432 | 0.055988 | 5.4316 | -0.035879 | 122.0753 | 122.0012 | 121.9328 | -0.049321 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.001033 | 0.10877 | 0.10634 | 0.014475 | 0.013442 | 0.034671 | -0.03376 | -0.058849 | -122.0514 | 0.074295 | -0.015155 | 0.043694 | -121.9437 | -121.9084 | 122.1257 | 122.0516 | 121.9831 | 5.482 | -122.0159 | -0.034542 | 0.073218 | 0.10847 | 0.12397 | -122.0758
2643.9375 | 122.1268 | -0.10071 | 121.9437 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065355 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.015219 | 0.065145 | 5.5369 | -0.031301 | 122.0707 | 122.0012 | 121.9328 | -0.063057 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.10462 | 0.037651 | 0.12708 | 0.16585 | 0.069407 | 0.031756 | 0.057559 | -0.010872 | -0.003916 | -122.024 | 0.12007 | 0.039778 | 0.043694 | -121.9208 | -121.8855 | 122.1715 | 122.1019 | 122.0335 | 5.6376 | -122.0067 | 0.02039 | 0.12357 | 0.15882 | 0.17433 | -122.0483
2645.6406 | 122.1359 | -0.068665 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0090999 | 0.05311 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019827 | 0.030698 | 0.015646 | 0.060567 | 5.6194 | -0.031301 | 122.0662 | 122.0104 | 121.9374 | -0.058478 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.013707 | 0.058115 | -0.1092 | 0.010187 | 0.11334 | 0.12923 | 0.037364 | 0.027177 | 0.057562 | -0.015448 | -0.040538 | -122.0331 | 0.097185 | 0.003156 | 0.043694 | -121.9391 | -121.8947 | 122.1348 | 122.079 | 122.006 | 5.688 | -122.0113 | -0.011653 | 0.082372 | 0.12678 | 0.14686 | -122.062
2647.4062 | 122.168 | -0.059509 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0093137 | 0.05311 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.030271 | 0.015432 | 0.060567 | 5.6926 | -0.040457 | 122.0707 | 122.0058 | 121.9328 | -0.049321 | 0.023941 | 0.06904 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.010188 | 0.11335 | 0.12008 | 0.019052 | 0.008864 | 0.048406 | -0.024604 | -0.049694 | -122.0423 | 0.08345 | -0.001421 | 0.048273 | -121.9345 | -121.8947 | 122.1303 | 122.0653 | 121.9923 | 5.7521 | -122.0067 | -0.025387 | 0.082373 | 0.1222 | 0.12855 | -122.0666
2649.1719 | 122.0856 | -0.10529 | 121.9666 | 1.4211e-13 | -0.042598 | 0.0020727 | 0.065355 | -0.0093137 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.060567 | 5.7704 | -0.026723 | 122.0707 | 122.0012 | 121.9374 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.055965 | 0.10419 | 0.16585 | 0.078563 | 0.022598 | 0.034671 | -0.029181 | -0.003917 | -122.0469 | 0.13381 | 0.044356 | 0.048273 | -121.9483 | -121.9039 | 122.176 | 122.1065 | 122.0427 | 5.8757 | -122.0159 | 0.024968 | 0.12357 | 0.16798 | 0.18806 | -122.0758
2650.9375 | 122.1085 | -0.09613 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019827 | 0.030485 | 0.015219 | 0.060567 | 5.8712 | -0.026723 | 122.0753 | 122.0104 | 121.942 | -0.058478 | 0.023941 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.067272 | -0.10004 | 0.037652 | 0.11792 | 0.1567 | 0.069407 | 0.031755 | 0.052985 | -0.015447 | -0.003915 | -122.0377 | 0.12007 | 0.030621 | 0.034536 | -121.9437 | -121.8901 | 122.1715 | 122.1065 | 122.0381 | 5.9673 | -122.0159 | 0.015812 | 0.10984 | 0.1634 | 0.16975 | -122.0574
2652.6562 | 122.0352 | -0.11902 | 121.9803 | 1.4211e-13 | -0.042384 | 0.0020727 | 0.065996 | -0.0095273 | 0.053538 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015219 | 0.069723 | 5.949 | -0.026723 | 122.0753 | 122.0058 | 121.9328 | -0.053899 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.10004 | 0.06512 | 0.095035 | 0.18874 | 0.092296 | 0.027176 | 0.025517 | -0.047493 | 0.018974 | -122.0652 | 0.14296 | 0.058089 | 0.039115 | -121.9574 | -121.9176 | 122.1943 | 122.1248 | 122.0518 | 6.068 | -122.0342 | 0.034123 | 0.14188 | 0.18171 | 0.19264 | -122.0803
2654.4219 | 122.1588 | -0.082397 | 121.962 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0093137 | 0.053324 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.030057 | 0.015646 | 0.069723 | 6.0131 | -0.026723 | 122.0707 | 122.0058 | 121.9374 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.053537 | -0.1092 | 0.023919 | 0.10877 | 0.15212 | 0.055674 | 0.031755 | 0.043828 | -0.024603 | -0.026806 | -122.0469 | 0.10634 | 0.021467 | 0.048273 | -121.9437 | -121.9084 | 122.1531 | 122.0882 | 122.0198 | 6.0955 | -122.0205 | -0.002499 | 0.10068 | 0.13593 | 0.15602 | -122.0712
2656.1875 | 122.0306 | -0.11444 | 122.0032 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0095273 | 0.052897 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019613 | 0.030698 | 0.015219 | 0.069723 | 6.1001 | -0.026723 | 122.0707 | 122.0104 | 121.9374 | -0.058478 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.055963 | 0.067569 | 0.18416 | 0.087718 | 0.031755 | 0.007208 | -0.065802 | 0.005238 | -122.0835 | 0.13838 | 0.05809 | 0.052852 | -121.9757 | -121.9405 | 122.1852 | 122.1248 | 122.0518 | 6.2145 | -122.0617 | 0.034123 | 0.14188 | 0.17713 | 0.18806 | -122.1124
2657.8906 | 122.0215 | -0.11902 | 122.0078 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065996 | -0.0090999 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030271 | 0.015219 | 0.065145 | 6.1734 | -0.026723 | 122.0707 | 122.0012 | 121.9465 | -0.053899 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.06512 | 0.062992 | 0.18416 | 0.092296 | 0.027176 | -0.006527 | -0.061222 | 0.009816 | -122.0926 | 0.14754 | 0.058089 | 0.048273 | -121.9895 | -121.9496 | 122.1898 | 122.1202 | 122.0655 | 6.2924 | -122.0617 | 0.034123 | 0.1373 | 0.17713 | 0.19264 | -122.117
2659.6562 | 122.0352 | -0.11444 | 122.0032 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0093137 | 0.052897 | -0.01755 | -0.0044395 | -0.0019123 | 0.019613 | 0.030485 | 0.015005 | 0.069723 | 6.2695 | -0.031301 | 122.0799 | 122.0058 | 121.9374 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.11378 | 0.060542 | 0.076725 | 0.18416 | 0.08314 | 0.022598 | 0.002629 | -0.065802 | 0.000659 | -122.0835 | 0.14296 | 0.053511 | 0.052852 | -121.9803 | -121.9405 | 122.1943 | 122.1202 | 122.0518 | 6.384 | -122.0571 | 0.034123 | 0.13731 | 0.17713 | 0.19264 | -122.117
2661.4062 | 122.0901 | -0.09613 | 121.9666 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0093137 | 0.053324 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030271 | 0.015219 | 0.065145 | 6.3153 | -0.035879 | 122.0707 | 122.0012 | 121.942 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.022864 | 0.071851 | -0.1092 | 0.037652 | 0.10419 | 0.16128 | 0.060251 | 0.022599 | 0.034671 | -0.024603 | -0.013073 | -122.0423 | 0.12007 | 0.0352 | 0.048273 | -121.9437 | -121.8947 | 122.1669 | 122.0974 | 122.0381 | 6.4114 | -122.025 | 0.020391 | 0.11899 | 0.16798 | 0.16975 | -122.0758
2663.1094 | 122.0078 | -0.11902 | 122.0032 | 1.4211e-13 | -0.043025 | 0.0020727 | 0.065355 | -0.0093137 | 0.052897 | -0.0099192 | -0.0037985 | -0.0014849 | 0.019399 | 0.030485 | 0.015646 | 0.069723 | 6.3794 | -0.035879 | 122.0662 | 122.0012 | 121.942 | -0.053899 | 0.023941 | 0.064461 | -0.056351 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.06512 | 0.06299 | 0.18874 | 0.08314 | 0.01802 | -0.00195 | -0.061224 | 0.014395 | -122.0881 | 0.14296 | 0.062668 | 0.048273 | -121.9803 | -121.9405 | 122.1852 | 122.1202 | 122.061 | 6.4984 | -122.0571 | 0.034123 | 0.14188 | 0.18171 | 0.18348 | -122.1078
2664.8594 | 122.0718 | -0.10529 | 121.9803 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065782 | -0.0090999 | 0.05311 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019613 | 0.030485 | 0.015432 | 0.069723 | 6.4481 | -0.017566 | 122.0753 | 122.0058 | 121.9465 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.055965 | 0.095035 | 0.17501 | 0.08772 | 0.031755 | 0.025517 | -0.033757 | -0.003917 | -122.0652 | 0.13381 | 0.044356 | 0.048273 | -121.9574 | -121.9176 | 122.1806 | 122.1111 | 122.0518 | 6.5534 | -122.0296 | 0.02039 | 0.12815 | 0.16798 | 0.1789 | -122.0895
2666.5625 | 122.1497 | -0.07782 | 121.9803 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0095273 | 0.053324 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.030485 | 0.015219 | 0.069723 | 6.5351 | -0.017566 | 122.0753 | 122.0012 | 121.9328 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.027442 | 0.058115 | -0.11378 | 0.023921 | 0.095035 | 0.14754 | 0.060254 | 0.036333 | 0.020938 | -0.047493 | -0.035962 | -122.0652 | 0.10634 | 0.012311 | 0.048273 | -121.9528 | -121.9222 | 122.1531 | 122.079 | 122.0106 | 6.6129 | -122.0342 | -0.007076 | 0.10526 | 0.13594 | 0.15144 | -122.0941
2668.3281 | 122.1542 | -0.068665 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065782 | -0.0090999 | 0.053324 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030271 | 0.015432 | 0.074302 | 6.6083 | -0.026723 | 122.0753 | 122.0058 | 121.942 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.067272 | -0.1092 | 0.019344 | 0.11792 | 0.14297 | 0.041942 | 0.022598 | 0.048406 | -0.015447 | -0.040538 | -122.0469 | 0.097185 | 0.007735 | 0.048273 | -121.9391 | -121.8901 | 122.144 | 122.0745 | 122.0106 | 6.677 | -122.0067 | -0.02081 | 0.08695 | 0.13594 | 0.14686 | -122.0666
2670.0156 | 122.1268 | -0.059509 | 121.9711 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065355 | -0.0097409 | 0.05311 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.030485 | 0.015432 | 0.074302 | 6.677 | -0.026723 | 122.0707 | 122.0058 | 121.942 | -0.044742 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.10462 | 0.014767 | 0.099613 | 0.13381 | 0.032786 | 0.018019 | 0.034673 | -0.02918 | -0.045115 | -122.0514 | 0.078871 | 0.003158 | 0.048273 | -121.9483 | -121.9039 | 122.1303 | 122.0653 | 122.0015 | 6.7365 | -122.0159 | -0.020809 | 0.082373 | 0.12678 | 0.13771 | -122.0758
2671.7656 | 121.994 | -0.11444 | 121.9803 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0093137 | 0.05311 | -0.01755 | -0.0040121 | -0.0012713 | 0.019186 | 0.030271 | 0.015432 | 0.07888 | 6.7457 | -0.017566 | 122.0753 | 122.0058 | 121.942 | -0.058478 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | 0.055963 | 0.095035 | 0.19332 | 0.096875 | 0.040912 | 0.025517 | -0.038336 | 0.005238 | -122.0606 | 0.13838 | 0.05809 | 0.052852 | -121.9574 | -121.913 | 122.1898 | 122.1202 | 122.0564 | 6.8601 | -122.0388 | 0.034123 | 0.13731 | 0.18171 | 0.19264 | -122.0895
2673.5312 | 122.0215 | -0.10986 | 121.9803 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0095273 | 0.05311 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019827 | 0.030698 | 0.015432 | 0.074302 | 6.8235 | -0.022144 | 122.0799 | 122.0058 | 121.9374 | -0.053899 | 0.023941 | 0.073618 | -0.070087 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.055964 | 0.099613 | 0.18417 | 0.087719 | 0.031755 | 0.025517 | -0.042914 | 0.005239 | -122.0606 | 0.1338 | 0.039776 | 0.034537 | -121.9574 | -121.9176 | 122.1898 | 122.1157 | 122.0472 | 6.9334 | -122.0342 | 0.029545 | 0.13273 | 0.17256 | 0.18348 | -122.0849
2675.2969 | 122.0581 | -0.10986 | 121.962 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0090999 | 0.053538 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030271 | 0.015432 | 0.07888 | 6.9014 | -0.026723 | 122.0799 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.094053 | 0.022864 | 0.058115 | -0.1092 | 0.055964 | 0.11792 | 0.18874 | 0.08314 | 0.027176 | 0.043828 | -0.010868 | 0.00066 | -122.056 | 0.1338 | 0.053512 | 0.052852 | -121.9391 | -121.9039 | 122.1898 | 122.1157 | 122.061 | 7.0112 | -122.0159 | 0.01581 | 0.13273 | 0.16798 | 0.19264 | -122.0712
2677.0625 | 122.1451 | -0.064087 | 121.962 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0090999 | 0.053324 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019613 | 0.030698 | 0.015432 | 0.07888 | 6.9975 | -0.026723 | 122.0707 | 122.0104 | 121.942 | -0.063057 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.00103 | 0.10877 | 0.14297 | 0.037364 | 0.036334 | 0.048407 | -0.020025 | -0.040537 | -122.0423 | 0.088028 | 0.003157 | 0.043694 | -121.9391 | -121.8993 | 122.1348 | 122.0745 | 122.006 | 7.0616 | -122.025 | -0.016231 | 0.086951 | 0.12678 | 0.13771 | -122.0666
2678.7812 | 122.0581 | -0.091553 | 121.9666 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065782 | -0.0093137 | 0.053324 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019613 | 0.030485 | 0.015432 | 0.074302 | 7.0296 | -0.017566 | 122.0753 | 122.0104 | 121.942 | -0.053899 | 0.019362 | 0.073618 | -0.065509 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.037654 | 0.10877 | 0.16586 | 0.073987 | 0.036333 | 0.043829 | -0.024603 | -0.01765 | -122.056 | 0.11091 | 0.026044 | 0.043694 | -121.9437 | -121.9039 | 122.1669 | 122.1019 | 122.0335 | 7.1211 | -122.0205 | 0.002078 | 0.11442 | 0.15425 | 0.16517 | -122.0758
2680.5469 | 122.1268 | -0.073242 | 121.9666 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0097409 | 0.05311 | -0.01755 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.015219 | 0.074302 | 7.1028 | -0.026723 | 122.0707 | 122.0058 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.019343 | 0.10419 | 0.14754 | 0.046519 | 0.027176 | 0.03925 | -0.020024 | -0.04054 | -122.0514 | 0.097183 | 0.007733 | 0.048273 | -121.9437 | -121.9039 | 122.144 | 122.079 | 122.0198 | 7.1761 | -122.0205 | -0.011654 | 0.096106 | 0.13594 | 0.15144 | -122.0803
2682.25 | 122.0673 | -0.11444 | 121.994 | 1.4211e-13 | -0.043025 | 0.0020727 | 0.065569 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030057 | 0.015432 | 0.088037 | 7.1807 | -0.026723 | 122.0753 | 122.0058 | 121.9328 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.1092 | 0.060542 | 0.081302 | 0.20248 | 0.087718 | 0.027176 | 0.011784 | -0.061226 | 0.005238 | -122.0835 | 0.13838 | 0.053511 | 0.048273 | -121.9712 | -121.9267 | 122.1898 | 122.1202 | 122.0472 | 7.2951 | -122.0479 | 0.024966 | 0.13731 | 0.18171 | 0.19264 | -122.1032
2684.0156 | 122.0169 | -0.11444 | 121.994 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0095273 | 0.05311 | 0.0053413 | -0.0046531 | -0.0014849 | 0.019613 | 0.030271 | 0.015432 | 0.083459 | 7.2631 | -0.017566 | 122.0845 | 122.0104 | 121.942 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.075739 | 0.018285 | 0.058115 | -0.1092 | 0.06512 | 0.090459 | 0.1979 | 0.096875 | 0.031755 | 0.016363 | -0.052069 | 0.005238 | -122.0698 | 0.13838 | 0.05809 | 0.052852 | -121.9757 | -121.9359 | 122.1989 | 122.1248 | 122.0564 | 7.3775 | -122.0433 | 0.038702 | 0.13273 | 0.17256 | 0.19264 | -122.1032
2685.7812 | 122.049 | -0.086975 | 121.9849 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065569 | -0.0093137 | 0.05311 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019827 | 0.030271 | 0.015219 | 0.07888 | 7.3592 | -0.017566 | 122.0662 | 122.0058 | 121.9374 | -0.058478 | 0.019362 | 0.082776 | -0.06093 | -0.089475 | 0.013707 | 0.062694 | -0.11378 | 0.028497 | 0.081301 | 0.16586 | 0.069409 | 0.040912 | 0.02094 | -0.047491 | -0.026807 | -122.0743 | 0.10634 | 0.026045 | 0.052852 | -121.9712 | -121.9222 | 122.1531 | 122.0928 | 122.0243 | 7.4462 | -122.0433 | -0.0025 | 0.10068 | 0.14967 | 0.16975 | -122.0986
2687.5469 | 121.9986 | -0.10529 | 121.994 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065782 | -0.0093137 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019613 | 0.030485 | 0.015219 | 0.088037 | 7.492 | -0.022144 | 122.0799 | 122.015 | 121.942 | -0.053899 | 0.02852 | 0.078197 | -0.056351 | -0.089475 | 0.022864 | 0.062694 | -0.10462 | 0.051387 | 0.08588 | 0.19332 | 0.083142 | 0.031755 | 0.020942 | -0.052069 | 0.000662 | -122.0835 | 0.13381 | 0.048935 | 0.048273 | -121.9712 | -121.9313 | 122.1852 | 122.1202 | 122.0472 | 7.5973 | -122.0479 | 0.015811 | 0.12815 | 0.16798 | 0.18348 | -122.0986
2689.3125 | 122.1313 | -0.059509 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065782 | -0.0097409 | 0.05311 | -0.01755 | -0.0042257 | -0.0019123 | 0.019613 | 0.030485 | 0.015219 | 0.092615 | 7.5561 | -0.017566 | 122.0753 | 122.0104 | 121.9374 | -0.053899 | 0.02852 | 0.082776 | -0.070087 | -0.084896 | 0.022864 | 0.067272 | -0.10004 | 0.00561 | 0.11792 | 0.15212 | 0.041943 | 0.036333 | 0.052985 | -0.020025 | -0.040536 | -122.0423 | 0.088029 | -0.010578 | 0.029958 | -121.9345 | -121.8901 | 122.1348 | 122.0699 | 121.9969 | 7.6156 | -122.0113 | -0.025387 | 0.082373 | 0.12678 | 0.14228 | -122.0574
2691.0625 | 122.1222 | -0.07782 | 121.9666 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0093137 | 0.05311 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019827 | 0.030057 | 0.015005 | 0.083459 | 7.6156 | -0.017566 | 122.0753 | 122.0012 | 121.9328 | -0.053899 | 0.019362 | 0.073618 | -0.065509 | -0.089475 | 0.032021 | 0.067272 | -0.10462 | 0.023921 | 0.10877 | 0.16128 | 0.060254 | 0.036333 | 0.034671 | -0.03376 | -0.026804 | -122.056 | 0.097182 | 0.012311 | 0.039115 | -121.9345 | -121.8993 | 122.1531 | 122.079 | 122.0106 | 7.6934 | -122.0205 | -0.011655 | 0.10984 | 0.14509 | 0.15144 | -122.0712
2692.7656 | 122.1222 | -0.07782 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0093137 | 0.053324 | -0.01755 | -0.0044395 | -0.0014849 | 0.019399 | 0.030057 | 0.015219 | 0.083459 | 7.7072 | -0.017566 | 122.0753 | 122.0012 | 121.9465 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.11378 | 0.019342 | 0.14081 | 0.16128 | 0.060254 | 0.040912 | 0.066715 | 0.01202 | -0.035962 | -122.0148 | 0.10634 | 0.01689 | 0.052852 | -121.9116 | -121.8764 | 122.1531 | 122.079 | 122.0243 | 7.785 | -121.993 | -0.002498 | 0.10068 | 0.13594 | 0.15602 | -122.0483
2694.5312 | 122.0581 | -0.10986 | 122.0078 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.030271 | 0.015859 | 0.092615 | 7.7805 | -0.012988 | 122.0753 | 122.0058 | 121.9465 | -0.053899 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.055964 | 0.06757 | 0.20248 | 0.096875 | 0.040911 | -0.001948 | -0.061222 | 0.00066 | -122.0926 | 0.13838 | 0.044354 | 0.043694 | -121.9849 | -121.9451 | 122.1852 | 122.1157 | 122.0564 | 7.8903 | -122.0617 | 0.024967 | 0.13273 | 0.17256 | 0.18806 | -122.117
2696.2969 | 122.1451 | -0.07782 | 121.9391 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0090999 | 0.05311 | -0.0022892 | -0.0040121 | -0.0019123 | 0.019186 | 0.030057 | 0.015005 | 0.10177 | 7.8446 | -0.017566 | 122.0707 | 122.0012 | 121.942 | -0.053899 | 0.023941 | 0.06904 | -0.065509 | -0.084896 | 0.032021 | 0.058115 | -0.10462 | 0.023921 | 0.13166 | 0.17959 | 0.060254 | 0.036333 | 0.062137 | 0.002863 | -0.026804 | -122.024 | 0.10176 | 0.012311 | 0.039115 | -121.9071 | -121.881 | 122.1486 | 122.079 | 122.0198 | 7.9224 | -121.993 | -0.007076 | 0.10984 | 0.13594 | 0.14686 | -122.0437
2698 | 122.0169 | -0.09613 | 122.0169 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065782 | -0.0095273 | 0.053538 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019613 | 0.030057 | 0.015219 | 0.097194 | 7.927 | -0.012988 | 122.0799 | 122.0058 | 121.9465 | -0.063057 | 0.019362 | 0.082776 | -0.065509 | -0.089475 | 0.018285 | 0.058115 | -0.10462 | 0.033073 | 0.062992 | 0.19332 | 0.083142 | 0.050069 | -0.011104 | -0.070378 | -0.008494 | -122.1064 | 0.11549 | 0.030621 | 0.039115 | -121.9986 | -121.9588 | 122.176 | 122.1019 | 122.0427 | 8.0231 | -122.08 | 0.006655 | 0.11441 | 0.15424 | 0.17891 | -122.1215
2699.7656 | 122.1313 | -0.064087 | 121.9437 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0090999 | 0.053538 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019399 | 0.030698 | 0.015005 | 0.083459 | 7.9911 | -0.012988 | 122.0707 | 122.0058 | 121.942 | -0.053899 | 0.02852 | 0.078197 | -0.070087 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | 0.010188 | 0.12708 | 0.14755 | 0.051099 | 0.040911 | 0.062138 | -0.001715 | -0.045116 | -122.024 | 0.092607 | -0.006 | 0.039116 | -121.9208 | -121.8764 | 122.1348 | 122.0699 | 122.006 | 8.0552 | -121.9976 | -0.016231 | 0.086951 | 0.13136 | 0.14228 | -122.0529
2701.5156 | 122.0352 | -0.10986 | 121.9849 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065782 | -0.0090999 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015219 | 0.092615 | 8.0872 | -0.008409 | 122.0707 | 122.0012 | 121.942 | -0.058478 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.051385 | 0.08588 | 0.20248 | 0.10145 | 0.050069 | 0.016361 | -0.042913 | 0.00066 | -122.0652 | 0.12923 | 0.048933 | 0.048273 | -121.962 | -121.9222 | 122.1806 | 122.1111 | 122.0518 | 8.1971 | -122.0433 | 0.029545 | 0.13273 | 0.17256 | 0.19264 | -122.0941
2703.2969 | 122.1039 | -0.07782 | 121.9711 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065355 | -0.0090999 | 0.053324 | -0.0099192 | -0.0046531 | -0.0019123 | 0.019186 | 0.030912 | 0.015005 | 0.092615 | 8.1696 | -0.017566 | 122.0753 | 122.0012 | 121.942 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.019342 | 0.10419 | 0.17044 | 0.060254 | 0.040912 | 0.030094 | -0.02918 | -0.031383 | -122.056 | 0.10176 | 0.012311 | 0.043694 | -121.9483 | -121.9084 | 122.1531 | 122.079 | 122.0198 | 8.2475 | -122.0296 | -0.007076 | 0.10068 | 0.14051 | 0.15602 | -122.0803
2705.0625 | 122.1313 | -0.086975 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065782 | -0.0097409 | 0.05311 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019613 | 0.030057 | 0.015219 | 0.092615 | 8.252 | -0.022144 | 122.0753 | 122.0012 | 121.942 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.013707 | 0.053537 | -0.1092 | 0.028497 | 0.13623 | 0.17959 | 0.064831 | 0.036334 | 0.062137 | 0.002863 | -0.022228 | -122.0286 | 0.11092 | 0.021466 | 0.043694 | -121.9254 | -121.8855 | 122.1623 | 122.0882 | 122.0289 | 8.339 | -121.9976 | -0.0025 | 0.10068 | 0.14051 | 0.16517 | -122.0483
2706.8281 | 122.0123 | -0.11902 | 121.9803 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0093137 | 0.05311 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030485 | 0.015432 | 0.10177 | 8.3253 | -0.012988 | 122.0753 | 122.0058 | 121.9374 | -0.058478 | 0.014784 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.1092 | 0.060541 | 0.095035 | 0.22079 | 0.10603 | 0.04549 | 0.025517 | -0.042914 | 0.009816 | -122.0698 | 0.1338 | 0.058089 | 0.048273 | -121.962 | -121.9176 | 122.1943 | 122.1248 | 122.0564 | 8.4443 | -122.0388 | 0.029544 | 0.1373 | 0.18171 | 0.19264 | -122.0895
2708.5469 | 122.1451 | -0.073242 | 121.9528 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065569 | -0.0095273 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030271 | 0.015432 | 0.092615 | 8.3894 | -0.012988 | 122.0662 | 122.0058 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.019343 | 0.11334 | 0.16586 | 0.060254 | 0.040911 | 0.052983 | -0.006291 | -0.035961 | -122.0331 | 0.097183 | 0.012312 | 0.048273 | -121.9345 | -121.8901 | 122.1394 | 122.079 | 122.0198 | 8.4626 | -122.0067 | -0.007076 | 0.091527 | 0.13594 | 0.15144 | -122.062
2710.3125 | 122.1085 | -0.068665 | 121.9711 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065569 | -0.0093137 | 0.053324 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019613 | 0.030271 | 0.015219 | 0.097194 | 8.4444 | -0.017566 | 122.0753 | 121.9966 | 121.9465 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.019344 | 0.10419 | 0.16586 | 0.051099 | 0.031755 | 0.025516 | -0.024601 | -0.040538 | -122.0514 | 0.097185 | 0.007735 | 0.048273 | -121.9437 | -121.9084 | 122.144 | 122.0653 | 122.0152 | 8.513 | -122.0205 | -0.011653 | 0.096107 | 0.13136 | 0.14686 | -122.0803
2712.0781 | 122.0215 | -0.13275 | 121.9849 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0090999 | 0.05311 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019399 | 0.030698 | 0.015219 | 0.097194 | 8.5588 | -0.008409 | 122.0753 | 122.0058 | 121.9511 | -0.058478 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.10004 | 0.074273 | 0.090458 | 0.22995 | 0.12434 | 0.050069 | 0.02094 | -0.033756 | 0.032706 | -122.0652 | 0.15669 | 0.071821 | 0.039115 | -121.9666 | -121.9222 | 122.2081 | 122.1386 | 122.0839 | 8.6916 | -122.0433 | 0.052433 | 0.15104 | 0.19545 | 0.21553 | -122.0849
2713.8438 | 121.994 | -0.11902 | 122.0169 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065996 | -0.0090999 | 0.05311 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019186 | 0.030271 | 0.015219 | 0.10635 | 8.6183 | -0.012988 | 122.0753 | 122.0195 | 121.9511 | -0.058478 | 0.023941 | 0.087354 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.1092 | 0.060541 | 0.058414 | 0.22537 | 0.10603 | 0.04549 | 0.002633 | -0.0658 | 0.009816 | -122.1018 | 0.14296 | 0.058089 | 0.048273 | -121.9986 | -121.9542 | 122.1943 | 122.1386 | 122.0701 | 8.7374 | -122.0754 | 0.034123 | 0.1373 | 0.18171 | 0.20637 | -122.1261
2715.5469 | 122.1359 | -0.068665 | 121.9345 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065355 | -0.0095273 | 0.053538 | 0.0053413 | -0.0042257 | -0.0012713 | 0.019399 | 0.030485 | 0.015005 | 0.10635 | 8.6916 | -0.017566 | 122.0799 | 122.0058 | 121.942 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.018285 | 0.067272 | -0.10004 | 0.019344 | 0.14539 | 0.17502 | 0.051099 | 0.031755 | 0.071294 | 0.007441 | -0.03138 | -122.0148 | 0.092606 | 0.012314 | 0.043694 | -121.9162 | -121.8672 | 122.1486 | 122.0745 | 122.0106 | 8.7603 | -121.9838 | -0.011653 | 0.08695 | 0.13594 | 0.15144 | -122.0346
2717.25 | 122.1176 | -0.068665 | 121.9574 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065782 | -0.0095273 | 0.05311 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019186 | 0.030485 | 0.014791 | 0.10177 | 8.774 | -0.012988 | 122.0799 | 122.0058 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.018285 | 0.062694 | -0.1092 | 0.014766 | 0.1225 | 0.17044 | 0.055677 | 0.040911 | 0.048406 | -0.010868 | -0.040538 | -122.0469 | 0.092606 | 0.012314 | 0.052852 | -121.9391 | -121.8947 | 122.1486 | 122.0745 | 122.0152 | 8.8427 | -122.0113 | -0.02081 | 0.08695 | 0.13136 | 0.14686 | -122.0666
2718.9688 | 122.0398 | -0.11444 | 121.9666 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065996 | -0.0099547 | 0.05311 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019399 | 0.030485 | 0.015219 | 0.10635 | 8.8518 | -0.008409 | 122.0753 | 122.015 | 121.942 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.060542 | 0.10877 | 0.22079 | 0.10603 | 0.04549 | 0.048408 | -0.024603 | 0.009817 | -122.056 | 0.1338 | 0.053511 | 0.043694 | -121.9483 | -121.9039 | 122.1898 | 122.1294 | 122.0564 | 8.9663 | -122.0205 | 0.024966 | 0.13273 | 0.17713 | 0.19264 | -122.0712
2720.6719 | 122.0444 | -0.10529 | 121.9574 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065569 | -0.0097409 | 0.053324 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030271 | 0.015432 | 0.11093 | 8.9297 | -0.017566 | 122.0707 | 122.0058 | 121.9465 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.046808 | 0.11335 | 0.21621 | 0.08772 | 0.040912 | 0.048406 | -0.010868 | 0.000662 | -122.0423 | 0.12923 | 0.044356 | 0.043694 | -121.9345 | -121.8947 | 122.176 | 122.1111 | 122.0518 | 9.035 | -122.0159 | 0.02039 | 0.12815 | 0.16798 | 0.18348 | -122.062
2722.375 | 122.1451 | -0.068665 | 121.9528 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065355 | -0.0093137 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019613 | 0.030698 | 0.015432 | 0.10177 | 8.9709 | -0.008409 | 122.0753 | 122.0058 | 121.9511 | -0.063057 | 0.023941 | 0.073618 | -0.070087 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.005608 | 0.1225 | 0.17044 | 0.060256 | 0.054648 | 0.052983 | -0.001713 | -0.040538 | -122.0331 | 0.092606 | -0.001422 | 0.039116 | -121.9345 | -121.8901 | 122.144 | 122.0745 | 122.0198 | 9.0396 | -122.0159 | -0.011653 | 0.08695 | 0.13136 | 0.14228 | -122.062
2724.0938 | 122.0169 | -0.12817 | 121.9894 | 1.4211e-13 | -0.043239 | 0.0014317 | 0.065569 | -0.0093137 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018972 | 0.030485 | 0.015219 | 0.10635 | 9.0579 | -0.003831 | 122.0753 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.082776 | -0.070087 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.074275 | 0.08588 | 0.23452 | 0.12434 | 0.050068 | 0.016362 | -0.038334 | 0.018971 | -122.0698 | 0.15212 | 0.058087 | 0.039116 | -121.962 | -121.9267 | 122.2035 | 122.134 | 122.0793 | 9.1861 | -122.0433 | 0.047856 | 0.15562 | 0.19087 | 0.21095 | -122.0986
2725.8594 | 122.0215 | -0.10529 | 121.994 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065569 | -0.0097409 | 0.053324 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.10635 | 9.1357 | -0.008409 | 122.0662 | 122.0012 | 121.942 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.009128 | 0.062694 | -0.10004 | 0.051387 | 0.072145 | 0.21164 | 0.096877 | 0.04549 | 0.007205 | -0.052069 | 0.005241 | -122.0789 | 0.12923 | 0.048935 | 0.043694 | -121.9849 | -121.9313 | 122.1715 | 122.1065 | 122.0472 | 9.241 | -122.0479 | 0.02039 | 0.11441 | 0.16798 | 0.18348 | -122.0941
2727.5469 | 122.1588 | -0.068665 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065569 | -0.0095273 | 0.052897 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.030485 | 0.015219 | 0.11093 | 9.1952 | -0.008409 | 122.0753 | 122.0058 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.014766 | 0.13623 | 0.17959 | 0.060256 | 0.04549 | 0.066716 | 0.007442 | -0.035959 | -122.0286 | 0.092606 | 0.003156 | 0.039115 | -121.9208 | -121.8764 | 122.144 | 122.0745 | 122.0152 | 9.2639 | -121.993 | -0.02081 | 0.08695 | 0.13136 | 0.14686 | -122.0437
2729.3125 | 122.168 | -0.068665 | 121.9116 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0097409 | 0.053324 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019399 | 0.030485 | 0.015005 | 0.10635 | 9.2639 | -0.008409 | 122.0707 | 122.0012 | 121.942 | -0.053899 | 0.033099 | 0.078197 | -0.056351 | -0.075739 | 0.022864 | 0.058115 | -0.10462 | 0.014766 | 0.15912 | 0.17502 | 0.060256 | 0.04549 | 0.089603 | 0.030329 | -0.035959 | -121.9874 | 0.10176 | 0.012314 | 0.048273 | -121.8888 | -121.8535 | 122.1394 | 122.0699 | 122.0106 | 9.3326 | -121.9655 | -0.007074 | 0.091529 | 0.12678 | 0.14686 | -122.0162
2731.0781 | 122.0306 | -0.11444 | 121.9803 | 1.4211e-13 | -0.042598 | 0.0020727 | 0.065782 | -0.0095273 | 0.05311 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015219 | 0.10635 | 9.3646 | -0.008409 | 122.0799 | 122.0012 | 121.9465 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.013707 | 0.058115 | -0.11378 | 0.060542 | 0.099613 | 0.22079 | 0.10603 | 0.04549 | 0.020938 | -0.033757 | 0.000659 | -122.0652 | 0.14296 | 0.053511 | 0.052852 | -121.9666 | -121.9222 | 122.1943 | 122.1157 | 122.061 | 9.4791 | -122.0342 | 0.029545 | 0.12815 | 0.17256 | 0.19264 | -122.0941
2732.8438 | 122.081 | -0.09613 | 121.9849 | 1.4211e-13 | -0.042598 | 0.0020727 | 0.065782 | -0.0093137 | 0.053538 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030698 | 0.015432 | 0.11093 | 9.4287 | -0.003831 | 122.0707 | 122.0104 | 121.942 | -0.053899 | 0.02852 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | 0.042231 | 0.08588 | 0.20706 | 0.092299 | 0.050068 | 0.025519 | -0.042913 | -0.013073 | -122.0652 | 0.12465 | 0.0352 | 0.048273 | -121.962 | -121.9176 | 122.1669 | 122.1065 | 122.0381 | 9.5249 | -122.0388 | 0.015812 | 0.11899 | 0.1634 | 0.16975 | -122.0941
2734.5625 | 122.0718 | -0.091553 | 121.9482 | 1.4211e-13 | -0.042598 | 0.0014317 | 0.065355 | -0.0095273 | 0.05311 | -0.01755 | -0.0042257 | -0.0016987 | 0.019399 | 0.030485 | 0.015005 | 0.11551 | 9.5157 | -0.003831 | 122.0799 | 122.0058 | 121.9511 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.080318 | 0.018285 | 0.058115 | -0.10004 | 0.042232 | 0.13166 | 0.20706 | 0.087722 | 0.04549 | 0.057561 | 0.002865 | -0.008492 | -122.0286 | 0.12007 | 0.030623 | 0.039115 | -121.93 | -121.8901 | 122.1715 | 122.0974 | 122.0427 | 9.6073 | -121.9976 | 0.011235 | 0.10984 | 0.14967 | 0.16517 | -122.0483
2736.3281 | 122.1085 | -0.07782 | 121.962 | 1.4211e-13 | -0.042811 | 0.0020727 | 0.065782 | -0.0095273 | 0.053324 | -0.0022892 | -0.0048667 | -0.0016987 | 0.019613 | 0.030271 | 0.015219 | 0.12466 | 9.5844 | -0.003831 | 122.0799 | 122.0058 | 121.9465 | -0.049321 | 0.02852 | 0.078197 | -0.051772 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.028499 | 0.11792 | 0.20248 | 0.073989 | 0.04549 | 0.043828 | -0.015446 | -0.031383 | -122.0423 | 0.10634 | 0.026048 | 0.057431 | -121.9437 | -121.8993 | 122.1577 | 122.0836 | 122.0243 | 9.6622 | -122.0113 | -0.002498 | 0.096105 | 0.14051 | 0.15602 | -122.0712
2738.0938 | 122.1497 | -0.07782 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0095273 | 0.052897 | -0.0099192 | -0.0037985 | -0.0014849 | 0.019399 | 0.030698 | 0.014578 | 0.11551 | 9.6852 | -0.003831 | 122.0707 | 122.0012 | 121.9465 | -0.058478 | 0.02852 | 0.082776 | -0.070087 | -0.084896 | 0.018285 | 0.067272 | -0.11836 | 0.019342 | 0.13166 | 0.19333 | 0.073989 | 0.054647 | 0.062137 | 0.007442 | -0.040541 | -122.024 | 0.10634 | 0.007733 | 0.048274 | -121.9208 | -121.8718 | 122.1486 | 122.079 | 122.0243 | 9.763 | -121.9976 | -0.007076 | 0.096105 | 0.14509 | 0.1606 | -122.0574
2739.8594 | 122.0215 | -0.11902 | 121.994 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0097409 | 0.053538 | -0.01755 | -0.0042257 | -0.0014849 | 0.019186 | 0.030057 | 0.015219 | 0.11551 | 9.7859 | 0.000747 | 122.0753 | 122.0012 | 121.9511 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.11378 | 0.06512 | 0.081302 | 0.23453 | 0.11977 | 0.054646 | 0.007205 | -0.042912 | 0.005237 | -122.0835 | 0.14296 | 0.058089 | 0.052852 | -121.9757 | -121.9359 | 122.1943 | 122.1202 | 122.0701 | 9.9049 | -122.0479 | 0.029544 | 0.1373 | 0.17713 | 0.19722 | -122.1078
2741.5625 | 122.081 | -0.10071 | 121.9711 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065782 | -0.0097409 | 0.053324 | -0.01755 | -0.0040121 | -0.0012713 | 0.019399 | 0.030698 | 0.015219 | 0.12009 | 9.882 | -0.008409 | 122.0753 | 122.0058 | 121.942 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.1092 | 0.04223 | 0.10419 | 0.22079 | 0.092299 | 0.050069 | 0.034673 | -0.02918 | -0.008495 | -122.0606 | 0.12465 | 0.039778 | 0.048273 | -121.9483 | -121.913 | 122.176 | 122.1065 | 122.0427 | 9.9827 | -122.0296 | 0.011233 | 0.12357 | 0.15882 | 0.17891 | -122.0803
2743.3125 | 122.1085 | -0.086975 | 122.0032 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0090999 | 0.05311 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019186 | 0.030271 | 0.014791 | 0.12466 | 9.9644 | -0.008409 | 122.0799 | 122.0058 | 121.942 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.067272 | -0.10004 | 0.033076 | 0.076725 | 0.21164 | 0.078566 | 0.04549 | 0.002629 | -0.061224 | -0.01307 | -122.0926 | 0.10634 | 0.026045 | 0.039115 | -121.9849 | -121.9359 | 122.1669 | 122.0928 | 122.0289 | 10.0514 | -122.0571 | -0.0025 | 0.10526 | 0.15425 | 0.16517 | -122.1032
2745.0938 | 122.0673 | -0.11444 | 121.9757 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0097409 | 0.053538 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030271 | 0.015432 | 0.12009 | 10.0606 | -0.003831 | 122.0707 | 122.0058 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.11378 | 0.060542 | 0.095035 | 0.23453 | 0.11061 | 0.050068 | 0.030095 | -0.029179 | 0.000659 | -122.0652 | 0.13838 | 0.053511 | 0.052852 | -121.9574 | -121.913 | 122.1852 | 122.1202 | 122.061 | 10.175 | -122.0296 | 0.024966 | 0.13273 | 0.17713 | 0.19264 | -122.0895
2746.8594 | 122.0306 | -0.1236 | 121.9711 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.12009 | 10.1842 | 0.000747 | 122.0707 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.073618 | -0.065509 | -0.080318 | 0.013707 | 0.062694 | -0.11378 | 0.069697 | 0.099613 | 0.24368 | 0.12434 | 0.054646 | 0.034673 | -0.020023 | 0.009814 | -122.0514 | 0.14754 | 0.058087 | 0.048273 | -121.9574 | -121.9084 | 122.1943 | 122.1294 | 122.0747 | 10.3078 | -122.025 | 0.043278 | 0.1373 | 0.18629 | 0.19721 | -122.0849
2748.5781 | 122.1451 | -0.086975 | 121.9757 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0097409 | 0.05311 | -0.01755 | -0.0042257 | -0.0019123 | 0.019399 | 0.030485 | 0.015432 | 0.12009 | 10.2666 | 0.005325 | 122.0707 | 122.0012 | 121.9465 | -0.049321 | 0.019362 | 0.082776 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.037654 | 0.095035 | 0.20706 | 0.0923 | 0.054646 | 0.025516 | -0.029179 | -0.026807 | -122.056 | 0.10634 | 0.021466 | 0.048273 | -121.9483 | -121.913 | 122.1577 | 122.0882 | 122.0335 | 10.3536 | -122.025 | 0.006657 | 0.11442 | 0.14967 | 0.16975 | -122.0895
2750.3438 | 122.1497 | -0.073242 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0095273 | 0.05311 | -0.0022892 | -0.0046531 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.13382 | 10.349 | -0.003831 | 122.0662 | 122.0104 | 121.9374 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.1092 | 0.019343 | 0.12708 | 0.20706 | 0.069411 | 0.050068 | 0.071295 | -0.001715 | -0.035961 | -122.0286 | 0.092604 | 0.012312 | 0.048273 | -121.9208 | -121.8764 | 122.1394 | 122.0836 | 122.0106 | 10.4223 | -121.993 | -0.016233 | 0.091527 | 0.13594 | 0.15144 | -122.0483
2752.0938 | 122.049 | -0.11444 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0020727 | 0.065141 | -0.0090999 | 0.053324 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030271 | 0.015432 | 0.12924 | 10.4589 | -0.003831 | 122.0799 | 122.0104 | 121.942 | -0.053899 | 0.02852 | 0.073618 | -0.065509 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.060542 | 0.1225 | 0.24368 | 0.11061 | 0.050068 | 0.052985 | -0.015447 | 0.005238 | -122.0423 | 0.14296 | 0.048932 | 0.043694 | -121.9345 | -121.8993 | 122.1943 | 122.1248 | 122.0564 | 10.5734 | -122.0113 | 0.029545 | 0.13731 | 0.17256 | 0.18806 | -122.0666
2753.8594 | 122.0215 | -0.13733 | 121.9894 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065355 | -0.0095273 | 0.053538 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019613 | 0.030698 | 0.015005 | 0.12466 | 10.5505 | -0.003831 | 122.0662 | 122.0058 | 121.9511 | -0.053899 | 0.019362 | 0.078197 | -0.070087 | -0.084896 | 0.022864 | 0.067272 | -0.10462 | 0.08343 | 0.076723 | 0.26199 | 0.1335 | 0.050068 | 0.016362 | -0.038334 | 0.032705 | -122.0743 | 0.15669 | 0.067242 | 0.034537 | -121.9666 | -121.9222 | 122.2035 | 122.1431 | 122.0884 | 10.6878 | -122.0433 | 0.052433 | 0.16019 | 0.2046 | 0.21553 | -122.0941
2755.5625 | 122.1313 | -0.064087 | 121.9666 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065569 | -0.0095273 | 0.053324 | 0.0053413 | -0.0042257 | -0.0016987 | 0.019613 | 0.030271 | 0.015219 | 0.12466 | 10.665 | 0.005325 | 122.0799 | 122.0058 | 121.9557 | -0.067636 | 0.019362 | 0.06904 | -0.065509 | -0.089475 | 0.013707 | 0.071851 | -0.1092 | -0.003549 | 0.11335 | 0.18875 | 0.069412 | 0.072961 | 0.03925 | -0.010867 | -0.045116 | -122.056 | 0.083449 | -0.001422 | 0.043694 | -121.9528 | -121.8947 | 122.144 | 122.0699 | 122.0198 | 10.7291 | -122.0342 | -0.025388 | 0.077794 | 0.13594 | 0.13313 | -122.0758
2757.3281 | 122.0261 | -0.11444 | 121.9711 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0097409 | 0.053538 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.015005 | 0.12924 | 10.7337 | 0.005325 | 122.0662 | 122.0058 | 121.9465 | -0.058478 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.055963 | 0.095034 | 0.24368 | 0.11977 | 0.063803 | 0.034673 | -0.024601 | 0.009817 | -122.0514 | 0.1338 | 0.053511 | 0.043694 | -121.9483 | -121.9084 | 122.1806 | 122.1202 | 122.061 | 10.8481 | -122.0296 | 0.034123 | 0.13731 | 0.17713 | 0.19722 | -122.0758
2759.0312 | 122.0215 | -0.10529 | 121.994 | 1.4211e-13 | -0.042384 | 0.0016453 | 0.065569 | -0.0097409 | 0.053751 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019399 | 0.030271 | 0.015005 | 0.1384 | 10.8573 | 0.005325 | 122.0753 | 122.015 | 121.9465 | -0.049321 | 0.019362 | 0.082776 | -0.056351 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.055965 | 0.081302 | 0.24368 | 0.11061 | 0.054646 | 0.020942 | -0.04749 | -0.003917 | -122.0835 | 0.12465 | 0.048935 | 0.052852 | -121.9712 | -121.9313 | 122.1806 | 122.1202 | 122.0518 | 10.9626 | -122.0433 | 0.015811 | 0.12815 | 0.16798 | 0.18806 | -122.1032
2760.7969 | 122.0352 | -0.11902 | 121.9711 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065996 | -0.0095273 | 0.05311 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.030698 | 0.015005 | 0.12924 | 10.9534 | 0.009904 | 122.0662 | 122.0058 | 121.9465 | -0.058478 | 0.02852 | 0.078197 | -0.065509 | -0.089475 | 0.018285 | 0.058115 | -0.10462 | 0.060541 | 0.095034 | 0.24826 | 0.12892 | 0.068382 | 0.034673 | -0.024601 | 0.014395 | -122.0606 | 0.14754 | 0.05351 | 0.039115 | -121.9528 | -121.913 | 122.1852 | 122.1248 | 122.0655 | 11.0724 | -122.0296 | 0.029544 | 0.1373 | 0.17713 | 0.19722 | -122.0758
2762.5625 | 122.0627 | -0.10071 | 121.9986 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019186 | 0.030271 | 0.015005 | 0.14298 | 11.0633 | 0.009904 | 122.0707 | 122.0012 | 121.942 | -0.058478 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.067272 | -0.10462 | 0.04223 | 0.072147 | 0.24369 | 0.11061 | 0.068382 | 0.002628 | -0.056646 | -0.003916 | -122.0789 | 0.12923 | 0.035199 | 0.039115 | -121.9757 | -121.9313 | 122.1715 | 122.1019 | 122.0427 | 11.164 | -122.0571 | 0.02039 | 0.12357 | 0.16798 | 0.17891 | -122.1032
2764.2656 | 122.0352 | -0.1236 | 122.0123 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065782 | -0.0097409 | 0.053324 | -0.0022892 | -0.0044395 | -0.0019123 | 0.019613 | 0.030271 | 0.014791 | 0.14756 | 11.1732 | 0.005325 | 122.0799 | 122.0012 | 121.9557 | -0.058478 | 0.02852 | 0.082776 | -0.065509 | -0.089475 | 0.022864 | 0.062694 | -0.10462 | 0.065118 | 0.06757 | 0.27115 | 0.12892 | 0.063803 | -0.011105 | -0.056643 | 0.018972 | -122.1018 | 0.15212 | 0.058087 | 0.039115 | -121.9895 | -121.9496 | 122.2035 | 122.1248 | 122.0793 | 11.2968 | -122.0708 | 0.034121 | 0.14646 | 0.18629 | 0.20637 | -122.117
2765.9531 | 122.1085 | -0.086975 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065355 | -0.0095273 | 0.053538 | -0.01755 | -0.0040121 | -0.0014849 | 0.019613 | 0.030271 | 0.015005 | 0.13382 | 11.2693 | 0.009904 | 122.0753 | 122.0058 | 121.9465 | -0.058478 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.013707 | 0.062694 | -0.10462 | 0.028497 | 0.11792 | 0.2208 | 0.096879 | 0.068382 | 0.048406 | -0.010868 | -0.017649 | -122.0331 | 0.11092 | 0.026045 | 0.043694 | -121.9437 | -121.8947 | 122.1623 | 122.0928 | 122.0335 | 11.3563 | -122.0159 | 0.011236 | 0.10068 | 0.14967 | 0.16975 | -122.062
2767.6562 | 122.1085 | -0.059509 | 121.9894 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0093137 | 0.053324 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030271 | 0.015219 | 0.14298 | 11.3655 | 0.005325 | 122.0753 | 122.0012 | 121.9465 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.022864 | 0.053537 | -0.1092 | 0.010188 | 0.08588 | 0.20249 | 0.064834 | 0.054646 | 0.011783 | -0.042912 | -0.049694 | -122.0789 | 0.08345 | -0.006 | 0.043694 | -121.9666 | -121.9359 | 122.1348 | 122.0607 | 122.006 | 11.425 | -122.0388 | -0.029966 | 0.082373 | 0.11305 | 0.13771 | -122.0986
2769.3594 | 122.1542 | -0.068665 | 121.9482 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030698 | 0.015219 | 0.14756 | 11.4754 | 0.009904 | 122.0753 | 122.0012 | 121.9465 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.062694 | -0.10462 | 0.014766 | 0.12708 | 0.21622 | 0.078569 | 0.063803 | 0.052982 | -0.001713 | -0.035959 | -122.0377 | 0.088027 | 0.007735 | 0.043694 | -121.9254 | -121.8855 | 122.144 | 122.0699 | 122.0152 | 11.544 | -122.0021 | -0.02081 | 0.091529 | 0.13136 | 0.14686 | -122.0529
2771.1094 | 122.1497 | -0.10071 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065782 | -0.0095273 | 0.05311 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.1384 | 11.5853 | 0.009904 | 122.0753 | 122.0058 | 121.9374 | -0.053899 | 0.023941 | 0.087354 | -0.056351 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.046809 | 0.11792 | 0.23911 | 0.11061 | 0.063803 | 0.048406 | -0.020025 | -0.003916 | -122.0469 | 0.12465 | 0.044357 | 0.048273 | -121.9391 | -121.8947 | 122.176 | 122.1065 | 122.0381 | 11.686 | -122.0113 | 0.011233 | 0.11899 | 0.1634 | 0.18806 | -122.062
2772.875 | 122.0261 | -0.11902 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065782 | -0.0095273 | 0.053538 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019399 | 0.030271 | 0.015005 | 0.14298 | 11.7638 | 0.009904 | 122.0707 | 122.0104 | 121.942 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.06512 | 0.08588 | 0.262 | 0.12892 | 0.063803 | 0.025519 | -0.042913 | 0.009816 | -122.0743 | 0.14296 | 0.062668 | 0.052852 | -121.962 | -121.9222 | 122.1898 | 122.1294 | 122.061 | 11.8829 | -122.0388 | 0.029544 | 0.14188 | 0.18171 | 0.2018 | -122.0941
2774.6406 | 122.1268 | -0.059509 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065569 | -0.0090999 | 0.053538 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019399 | 0.030485 | 0.015005 | 0.14298 | 11.8691 | 0.014482 | 122.0753 | 122.0058 | 121.9511 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.001031 | 0.14081 | 0.20249 | 0.073991 | 0.07296 | 0.071294 | 0.016598 | -0.049694 | -122.0194 | 0.078871 | -0.001421 | 0.048273 | -121.9116 | -121.8764 | 122.1348 | 122.0653 | 122.0106 | 11.9287 | -121.993 | -0.025387 | 0.082373 | 0.11762 | 0.13771 | -122.0437
2776.4062 | 122.1451 | -0.073242 | 121.9528 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019186 | 0.030698 | 0.014791 | 0.15213 | 12.034 | 0.01906 | 122.0707 | 122.015 | 121.9465 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.013707 | 0.067272 | -0.10462 | 0.019343 | 0.11792 | 0.22538 | 0.092302 | 0.072959 | 0.062141 | -0.006291 | -0.031382 | -122.0331 | 0.10176 | 0.012312 | 0.043694 | -121.9391 | -121.8855 | 122.144 | 122.0882 | 122.0198 | 12.1072 | -122.0067 | -0.007076 | 0.086949 | 0.14051 | 0.15144 | -122.0574
2778.1719 | 122.0398 | -0.10986 | 122.0123 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0095273 | 0.053538 | -0.0022892 | -0.0042257 | -0.0019123 | 0.019399 | 0.030912 | 0.015005 | 0.15671 | 12.208 | 0.005325 | 122.0753 | 122.0104 | 121.942 | -0.058478 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.10462 | 0.051385 | 0.062992 | 0.26658 | 0.11519 | 0.063803 | -0.001947 | -0.070379 | 0.005239 | -122.0972 | 0.1338 | 0.048933 | 0.043694 | -121.994 | -121.9542 | 122.1852 | 122.1202 | 122.0518 | 12.3178 | -122.0708 | 0.024967 | 0.12815 | 0.16798 | 0.19264 | -122.117
2779.8906 | 122.1451 | -0.07782 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065996 | -0.0093137 | 0.053538 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030698 | 0.015005 | 0.15213 | 12.295 | 0.014482 | 122.0707 | 122.0058 | 121.9557 | -0.058478 | 0.02852 | 0.082776 | -0.056351 | -0.084896 | 0.018285 | 0.058115 | -0.10462 | 0.019342 | 0.08588 | 0.22995 | 0.092302 | 0.07296 | 0.02094 | -0.029177 | -0.026804 | -122.0698 | 0.10634 | 0.021469 | 0.048273 | -121.9666 | -121.9267 | 122.1486 | 122.0836 | 122.0335 | 12.3728 | -122.0433 | -0.007076 | 0.096105 | 0.13594 | 0.1606 | -122.0895
2781.6719 | 122.0123 | -0.12817 | 122.0032 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065141 | -0.0093137 | 0.053538 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.015005 | 0.16129 | 12.4003 | 0.01906 | 122.0707 | 122.015 | 121.9511 | -0.058478 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.013707 | 0.071851 | -0.1092 | 0.069696 | 0.067569 | 0.28946 | 0.14723 | 0.077538 | 0.011787 | -0.052067 | 0.018971 | -122.0789 | 0.15212 | 0.071823 | 0.052852 | -121.9895 | -121.9313 | 122.1989 | 122.1431 | 122.0793 | 12.5284 | -122.0617 | 0.052435 | 0.14188 | 0.20003 | 0.21095 | -122.1124
2783.375 | 122.1039 | -0.09613 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0016453 | 0.065569 | -0.0099547 | 0.053324 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019613 | 0.030271 | 0.015219 | 0.15671 | 12.4735 | 0.009904 | 122.0707 | 122.0104 | 121.942 | -0.058478 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.037652 | 0.13623 | 0.25284 | 0.10603 | 0.068382 | 0.075873 | 0.007441 | -0.013073 | -122.0148 | 0.12465 | 0.030621 | 0.043694 | -121.9162 | -121.8718 | 122.1669 | 122.1065 | 122.0381 | 12.5697 | -121.993 | 0.015812 | 0.11441 | 0.15882 | 0.17433 | -122.0437
2785.1406 | 122.0215 | -0.1236 | 121.9894 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.015219 | 0.16129 | 12.6612 | 0.023639 | 122.0799 | 122.0012 | 121.9511 | -0.067636 | 0.023941 | 0.078197 | -0.056351 | -0.089475 | 0.027442 | 0.062694 | -0.11378 | 0.05596 | 0.090458 | 0.28489 | 0.14724 | 0.091275 | 0.011783 | -0.038334 | 0.009814 | -122.0789 | 0.14754 | 0.067245 | 0.057431 | -121.962 | -121.9267 | 122.2035 | 122.1248 | 122.0747 | 12.7848 | -122.0571 | 0.034121 | 0.15104 | 0.18629 | 0.20179 | -122.1032
2786.9062 | 122.0169 | -0.1236 | 121.9757 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065355 | -0.0093137 | 0.05311 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.030271 | 0.015219 | 0.15671 | 12.8444 | 0.009904 | 122.0707 | 122.0104 | 121.9511 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.065118 | 0.095035 | 0.28031 | 0.1335 | 0.068382 | 0.034674 | -0.024601 | 0.009814 | -122.0606 | 0.14754 | 0.062666 | 0.052852 | -121.9483 | -121.9084 | 122.1943 | 122.134 | 122.0747 | 12.968 | -122.0342 | 0.0387 | 0.15104 | 0.19087 | 0.20179 | -122.0895
2788.6094 | 122.0306 | -0.11444 | 121.9711 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0097409 | 0.053324 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019186 | 0.030485 | 0.015005 | 0.17045 | 13.0092 | 0.023639 | 122.0753 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.078197 | -0.070087 | -0.080318 | 0.027442 | 0.067272 | -0.1092 | 0.060542 | 0.10419 | 0.28489 | 0.13808 | 0.077538 | 0.034673 | -0.020023 | 0.005238 | -122.0514 | 0.13838 | 0.044354 | 0.039116 | -121.9437 | -121.9039 | 122.1898 | 122.1202 | 122.0655 | 13.1237 | -122.025 | 0.034123 | 0.14188 | 0.18171 | 0.19264 | -122.0803
2790.3906 | 122.0352 | -0.11444 | 122.0123 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065782 | -0.0093137 | 0.053324 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019399 | 0.030485 | 0.015005 | 0.17045 | 13.0871 | 0.01906 | 122.0707 | 122.0104 | 121.9465 | -0.058478 | 0.023941 | 0.087354 | -0.070087 | -0.089475 | 0.027442 | 0.062694 | -0.1092 | 0.055963 | 0.058414 | 0.28489 | 0.1335 | 0.077538 | -0.001947 | -0.0658 | 0.005238 | -122.1018 | 0.13838 | 0.044354 | 0.039116 | -121.9849 | -121.9496 | 122.1852 | 122.1248 | 122.061 | 13.2015 | -122.0708 | 0.024966 | 0.14188 | 0.17713 | 0.2018 | -122.1215
2792.0938 | 122.0947 | -0.07782 | 121.9482 | 1.4211e-13 | -0.042811 | 0.0014317 | 0.065996 | -0.0095273 | 0.053751 | -0.0022892 | -0.0048667 | -0.0016987 | 0.019399 | 0.030912 | 0.014791 | 0.17045 | 13.1924 | 0.01906 | 122.0753 | 122.0058 | 121.9465 | -0.058478 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.019342 | 0.12708 | 0.24827 | 0.09688 | 0.077538 | 0.057561 | -0.001713 | -0.026804 | -122.0286 | 0.097182 | 0.021469 | 0.048273 | -121.93 | -121.881 | 122.1531 | 122.0836 | 122.0243 | 13.2702 | -122.0067 | -0.002498 | 0.096105 | 0.14509 | 0.15602 | -122.0529
2793.8594 | 122.1268 | -0.07782 | 121.9391 | 1.4211e-13 | -0.043239 | 0.0014317 | 0.065782 | -0.0093137 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019399 | 0.030698 | 0.015219 | 0.17045 | 13.2977 | 0.009904 | 122.0753 | 122.0012 | 121.9465 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.023921 | 0.13623 | 0.24827 | 0.087724 | 0.063803 | 0.062137 | 0.007442 | -0.035962 | -122.024 | 0.10176 | 0.01689 | 0.052852 | -121.9116 | -121.8718 | 122.1531 | 122.079 | 122.0243 | 13.3755 | -121.993 | -0.007076 | 0.10526 | 0.14509 | 0.1606 | -122.0529
2795.625 | 122.1497 | -0.064087 | 121.9391 | 1.4211e-13 | -0.042811 | 0.0018589 | 0.065355 | -0.0093137 | 0.053538 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019613 | 0.030271 | 0.015005 | 0.1796 | 13.4762 | 0.028217 | 122.0753 | 122.0012 | 121.9511 | -0.063057 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.022864 | 0.067272 | -0.11378 | 0.00103 | 0.13623 | 0.24369 | 0.092304 | 0.091274 | 0.062137 | 0.01202 | -0.049695 | -122.024 | 0.088028 | -0.006 | 0.043695 | -121.9162 | -121.8718 | 122.1394 | 122.0653 | 122.0152 | 13.5403 | -122.0021 | -0.020809 | 0.086951 | 0.13136 | 0.14228 | -122.0529
2797.375 | 122.1085 | -0.10071 | 121.9711 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065355 | -0.0093137 | 0.053324 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019399 | 0.030485 | 0.015005 | 0.17503 | 13.5358 | 0.023639 | 122.0707 | 122.0058 | 121.9511 | -0.058478 | 0.033099 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.04223 | 0.099613 | 0.27573 | 0.12435 | 0.082117 | 0.034673 | -0.020023 | -0.008495 | -122.056 | 0.13381 | 0.039778 | 0.048273 | -121.9483 | -121.9084 | 122.1715 | 122.1065 | 122.0518 | 13.6365 | -122.0296 | 0.015812 | 0.12357 | 0.1634 | 0.17433 | -122.0803
2799.0781 | 122.0627 | -0.10529 | 121.9666 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0093137 | 0.053538 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030057 | 0.015219 | 0.17503 | 13.6273 | 0.023639 | 122.0662 | 122.0104 | 121.9465 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.051387 | 0.099611 | 0.28031 | 0.12893 | 0.077538 | 0.043829 | -0.020024 | -0.003917 | -122.0469 | 0.13381 | 0.044356 | 0.048273 | -121.9437 | -121.9084 | 122.1715 | 122.1157 | 122.0518 | 13.7326 | -122.0205 | 0.024968 | 0.12815 | 0.1634 | 0.18348 | -122.0758
2800.8438 | 122.1542 | -0.064087 | 121.9391 | 1.4211e-13 | -0.043025 | 0.0014317 | 0.065569 | -0.0093137 | 0.053324 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019613 | 0.030698 | 0.015005 | 0.1796 | 13.7006 | 0.023639 | 122.0799 | 122.0012 | 121.9465 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.005609 | 0.14081 | 0.24369 | 0.087726 | 0.082117 | 0.062137 | 0.007442 | -0.045116 | -122.0194 | 0.083449 | 0.003157 | 0.048273 | -121.9208 | -121.8718 | 122.144 | 122.0653 | 122.0106 | 13.7647 | -121.9976 | -0.016231 | 0.082372 | 0.13136 | 0.14228 | -122.0483
2802.6094 | 122.0535 | -0.10986 | 121.9666 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065569 | -0.0093137 | 0.053538 | -0.0022892 | -0.0042257 | -0.0021259 | 0.019186 | 0.030271 | 0.015432 | 0.18418 | 13.8288 | 0.01906 | 122.0707 | 122.0058 | 121.9511 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.032021 | 0.058115 | -0.11378 | 0.051385 | 0.10419 | 0.29405 | 0.12892 | 0.077538 | 0.03925 | -0.015446 | -0.003919 | -122.0514 | 0.13838 | 0.048933 | 0.052852 | -121.9345 | -121.9084 | 122.1806 | 122.1157 | 122.061 | 13.9386 | -122.025 | 0.024967 | 0.14188 | 0.16798 | 0.18806 | -122.0803
2804.3125 | 122.0261 | -0.13275 | 121.9894 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019186 | 0.030485 | 0.015432 | 0.1796 | 13.8975 | 0.01906 | 122.0707 | 122.0012 | 121.9557 | -0.053899 | 0.023941 | 0.087354 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.11378 | 0.078852 | 0.081302 | 0.31236 | 0.15181 | 0.072959 | 0.011783 | -0.033755 | 0.018969 | -122.0789 | 0.15669 | 0.071821 | 0.052852 | -121.9666 | -121.9222 | 122.2035 | 122.134 | 122.0884 | 14.0302 | -122.0433 | 0.043276 | 0.15562 | 0.20002 | 0.2201 | -122.1032
2806.0781 | 122.0078 | -0.12817 | 121.9894 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065569 | -0.0093137 | 0.053538 | -0.01755 | -0.0042257 | -0.0019123 | 0.019399 | 0.030698 | 0.015005 | 0.18418 | 13.8059 | 0.028217 | 122.0707 | 122.0058 | 121.9511 | -0.063057 | 0.019362 | 0.082776 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.11378 | 0.065117 | 0.081302 | 0.31236 | 0.15639 | 0.091274 | 0.016362 | -0.038334 | 0.014392 | -122.0789 | 0.14754 | 0.067244 | 0.052852 | -121.9666 | -121.9222 | 122.1989 | 122.134 | 122.0793 | 13.9341 | -122.0525 | 0.038699 | 0.15104 | 0.19545 | 0.21095 | -122.1032
2807.8281 | 122.0352 | -0.10071 | 121.9849 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.030698 | 0.014791 | 0.18418 | 13.9066 | 0.028217 | 122.0707 | 122.0058 | 121.9557 | -0.053899 | 0.023941 | 0.078197 | -0.051772 | -0.080318 | 0.022864 | 0.062694 | -0.11378 | 0.046809 | 0.08588 | 0.28489 | 0.12893 | 0.082116 | 0.02094 | -0.029177 | -0.013074 | -122.0652 | 0.12465 | 0.048936 | 0.06201 | -121.962 | -121.9222 | 122.1715 | 122.1065 | 122.0564 | 14.0073 | -122.0388 | 0.02039 | 0.12357 | 0.1634 | 0.17891 | -122.0986
2809.5938 | 122.1497 | -0.064087 | 121.9574 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065996 | -0.0093137 | 0.053324 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.015005 | 0.18876 | 13.9936 | 0.023639 | 122.0707 | 122.0058 | 121.9465 | -0.063057 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.00103 | 0.11335 | 0.25285 | 0.087726 | 0.086696 | 0.048406 | -0.010868 | -0.045116 | -122.0377 | 0.088028 | 0.003157 | 0.048273 | -121.93 | -121.8947 | 122.1348 | 122.0699 | 122.0106 | 14.0577 | -122.0205 | -0.016231 | 0.091529 | 0.12678 | 0.14686 | -122.0666
2811.3438 | 122.1268 | -0.073242 | 121.9574 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065782 | -0.0095273 | 0.053324 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019613 | 0.030912 | 0.015005 | 0.18418 | 14.076 | 0.023639 | 122.0616 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.019343 | 0.10419 | 0.25743 | 0.096881 | 0.077538 | 0.048406 | -0.00629 | -0.04054 | -122.0377 | 0.097183 | 0.012312 | 0.052852 | -121.93 | -121.8947 | 122.1348 | 122.079 | 122.0243 | 14.1493 | -122.0113 | -0.007076 | 0.10068 | 0.13594 | 0.15602 | -122.0712
2813.0469 | 122.0032 | -0.11902 | 121.994 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0097409 | 0.053538 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019613 | 0.030698 | 0.015005 | 0.18418 | 14.1905 | 0.032795 | 122.0707 | 122.0058 | 121.9557 | -0.058478 | 0.023941 | 0.082776 | -0.056351 | -0.084896 | 0.027442 | 0.071851 | -0.11378 | 0.060541 | 0.076724 | 0.3032 | 0.15181 | 0.091273 | 0.011784 | -0.038333 | 0.005237 | -122.0789 | 0.14296 | 0.062668 | 0.057431 | -121.9666 | -121.9222 | 122.1898 | 122.1248 | 122.0747 | 14.3095 | -122.0525 | 0.034123 | 0.14646 | 0.19087 | 0.2018 | -122.1078
2814.8281 | 122.1451 | -0.082397 | 121.9437 | 1.4211e-13 | -0.042811 | 0.0016453 | 0.065569 | -0.0090999 | 0.053538 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019186 | 0.030698 | 0.015219 | 0.18876 | 14.2592 | 0.037373 | 122.0662 | 122.0012 | 121.9465 | -0.058478 | 0.023941 | 0.082776 | -0.065509 | -0.089475 | 0.032021 | 0.062694 | -0.11378 | 0.023919 | 0.1225 | 0.27116 | 0.11977 | 0.095851 | 0.057559 | 0.002864 | -0.031385 | -122.0331 | 0.10634 | 0.016888 | 0.048273 | -121.9116 | -121.881 | 122.1486 | 122.0836 | 122.0289 | 14.3416 | -122.0021 | -0.007078 | 0.11442 | 0.14509 | 0.16517 | -122.0574
2816.5938 | 122.0673 | -0.11444 | 121.9711 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065569 | -0.0093137 | 0.053751 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019613 | 0.030912 | 0.015005 | 0.19334 | 14.3095 | 0.037373 | 122.0662 | 122.0104 | 121.9511 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.060542 | 0.095034 | 0.30778 | 0.15181 | 0.091272 | 0.039252 | -0.020023 | 0.005238 | -122.0514 | 0.13838 | 0.053511 | 0.048273 | -121.9483 | -121.913 | 122.1806 | 122.1248 | 122.0655 | 14.424 | -122.025 | 0.034123 | 0.13731 | 0.17256 | 0.19722 | -122.0803
2818.3594 | 122.0535 | -0.11444 | 121.9986 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065569 | -0.0095273 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030698 | 0.015219 | 0.19792 | 14.4011 | 0.032795 | 122.0707 | 122.0012 | 121.942 | -0.058478 | 0.019362 | 0.087354 | -0.06093 | -0.089475 | 0.027442 | 0.062694 | -0.10004 | 0.055963 | 0.072147 | 0.31236 | 0.14724 | 0.091273 | 0.002628 | -0.056646 | 0.014396 | -122.0881 | 0.1338 | 0.053511 | 0.039115 | -121.9712 | -121.9359 | 122.1852 | 122.1157 | 122.0564 | 14.5156 | -122.0571 | 0.024966 | 0.14188 | 0.17713 | 0.2018 | -122.0986
2820.0625 | 122.1405 | -0.068665 | 121.962 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.065782 | -0.0093137 | 0.053751 | -0.01755 | -0.0044395 | -0.0014849 | 0.019613 | 0.030698 | 0.015005 | 0.19792 | 14.5339 | 0.037373 | 122.0753 | 122.015 | 121.9465 | -0.058478 | 0.019362 | 0.082776 | -0.051772 | -0.084896 | 0.027442 | 0.067272 | -0.10004 | 0.010187 | 0.11335 | 0.26658 | 0.10604 | 0.095851 | 0.052986 | -0.015446 | -0.03138 | -122.0469 | 0.088027 | 0.016893 | 0.048273 | -121.9345 | -121.8947 | 122.144 | 122.0836 | 122.0152 | 14.6026 | -122.0205 | -0.016231 | 0.096107 | 0.13594 | 0.15144 | -122.062
2821.8281 | 122.1588 | -0.064087 | 121.9345 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065996 | -0.0097409 | 0.05311 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019613 | 0.030485 | 0.015005 | 0.2025 | 14.6529 | 0.041952 | 122.0707 | 122.0058 | 121.942 | -0.058478 | 0.019362 | 0.078197 | -0.065509 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.005609 | 0.13623 | 0.26658 | 0.10604 | 0.10043 | 0.071294 | 0.007441 | -0.045116 | -122.0194 | 0.083449 | -0.001422 | 0.043694 | -121.9116 | -121.8764 | 122.1348 | 122.0699 | 122.006 | 14.717 | -121.993 | -0.020809 | 0.086951 | 0.1222 | 0.14228 | -122.0437
2823.5156 | 122.0215 | -0.1236 | 121.9711 | 1.4211e-13 | -0.042598 | 0.0018589 | 0.065782 | -0.0095273 | 0.053751 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019186 | 0.030912 | 0.015219 | 0.20708 | 14.7995 | 0.037373 | 122.0707 | 122.0058 | 121.9511 | -0.058478 | 0.02852 | 0.082776 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.065118 | 0.099613 | 0.33067 | 0.16097 | 0.095851 | 0.034673 | -0.020023 | 0.018972 | -122.0514 | 0.15212 | 0.058087 | 0.039115 | -121.9528 | -121.9039 | 122.1943 | 122.1294 | 122.0747 | 14.923 | -122.0296 | 0.043278 | 0.14188 | 0.19087 | 0.20637 | -122.0758
2825.2812 | 122.0993 | -0.07782 | 121.9391 | 1.4211e-13 | -0.043239 | 0.0014317 | 0.065355 | -0.0095273 | 0.053538 | 0.0053413 | -0.0046531 | -0.0019123 | 0.019399 | 0.030485 | 0.015005 | 0.20708 | 14.9093 | 0.041952 | 122.0707 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.078197 | -0.070087 | -0.080318 | 0.022864 | 0.071851 | -0.11378 | 0.023921 | 0.13166 | 0.2849 | 0.11977 | 0.095851 | 0.066716 | 0.01202 | -0.035962 | -122.0194 | 0.10176 | 0.007733 | 0.043695 | -121.9162 | -121.8672 | 122.1486 | 122.0836 | 122.0289 | 14.9872 | -121.993 | -0.002498 | 0.10068 | 0.14967 | 0.15602 | -122.0529
2826.9844 | 122.0627 | -0.10986 | 121.9528 | 1.4211e-13 | -0.043025 | 0.0020727 | 0.065782 | -0.0097409 | 0.053751 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.015005 | 0.21623 | 14.9689 | 0.041952 | 122.0707 | 122.0012 | 121.9465 | -0.058478 | 0.02852 | 0.082776 | -0.06093 | -0.089475 | 0.013707 | 0.062694 | -0.1092 | 0.051385 | 0.11792 | 0.3261 | 0.15182 | 0.10043 | 0.048404 | -0.006291 | 0.00066 | -122.0423 | 0.13838 | 0.048933 | 0.048273 | -121.9391 | -121.8901 | 122.1806 | 122.1111 | 122.0564 | 15.0787 | -122.0113 | 0.020388 | 0.12357 | 0.17256 | 0.19264 | -122.062
2828.75 | 122.0581 | -0.091553 | 121.9574 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0040121 | -0.0019123 | 0.019399 | 0.030485 | 0.015005 | 0.20708 | 15.0925 | 0.04653 | 122.0662 | 122.0012 | 121.942 | -0.058478 | 0.023941 | 0.082776 | -0.056351 | -0.089475 | 0.027442 | 0.062694 | -0.1092 | 0.033075 | 0.10877 | 0.29863 | 0.13808 | 0.10501 | 0.043827 | -0.015447 | -0.01765 | -122.0469 | 0.11549 | 0.035202 | 0.052852 | -121.93 | -121.8947 | 122.1577 | 122.0928 | 122.0335 | 15.184 | -122.0159 | 0.002078 | 0.11899 | 0.15425 | 0.17433 | -122.0666
2830.4531 | 122.0261 | -0.11444 | 121.9803 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0095273 | 0.053324 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.030485 | 0.015005 | 0.21165 | 15.1566 | 0.051108 | 122.0662 | 122.0058 | 121.942 | -0.058478 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.013707 | 0.058115 | -0.1092 | 0.055963 | 0.085878 | 0.32609 | 0.16555 | 0.10959 | 0.025517 | -0.038336 | 0.005238 | -122.056 | 0.13838 | 0.053511 | 0.048273 | -121.9666 | -121.9222 | 122.1806 | 122.1202 | 122.0564 | 15.271 | -122.0388 | 0.038702 | 0.12815 | 0.17256 | 0.19722 | -122.0895
2832.2188 | 122.0718 | -0.091553 | 121.9803 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065782 | -0.0095273 | 0.053538 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.030698 | 0.014578 | 0.21165 | 15.1932 | 0.041952 | 122.0707 | 122.0012 | 121.942 | -0.058478 | 0.023941 | 0.073618 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.10462 | 0.033075 | 0.090457 | 0.30321 | 0.1335 | 0.10043 | 0.020938 | -0.038336 | -0.013071 | -122.0698 | 0.11549 | 0.026044 | 0.039115 | -121.9666 | -121.9176 | 122.1623 | 122.0928 | 122.0335 | 15.2848 | -122.0388 | 0.002078 | 0.10526 | 0.15425 | 0.16517 | -122.0849
2833.9844 | 122.1497 | -0.068665 | 121.9299 | 1.4211e-13 | -0.043025 | 0.0018589 | 0.065996 | -0.0095273 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019399 | 0.030698 | 0.015005 | 0.21165 | 15.2573 | 0.037373 | 122.0799 | 122.0058 | 121.9465 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.022864 | 0.062694 | -0.1092 | 0.010187 | 0.14997 | 0.28032 | 0.10604 | 0.095851 | 0.075871 | 0.016597 | -0.040538 | -122.0057 | 0.092606 | 0.003156 | 0.043694 | -121.9071 | -121.8672 | 122.1486 | 122.0745 | 122.0152 | 15.326 | -121.9884 | -0.007074 | 0.091529 | 0.13136 | 0.14686 | -122.0391
2835.7031 | 121.9894 | -0.10986 | 121.9849 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065782 | -0.0095273 | 0.053324 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019399 | 0.030485 | 0.015005 | 0.21623 | 15.3123 | 0.04653 | 122.0707 | 122.0012 | 121.9465 | -0.058478 | 0.019362 | 0.087354 | -0.056351 | -0.084896 | 0.018285 | 0.062694 | -0.10462 | 0.051385 | 0.08588 | 0.3261 | 0.15639 | 0.10501 | 0.016361 | -0.038334 | 0.005239 | -122.0698 | 0.12923 | 0.053512 | 0.048273 | -121.9666 | -121.9222 | 122.1806 | 122.1111 | 122.0564 | 15.4221 | -122.0433 | 0.024967 | 0.12815 | 0.17256 | 0.19722 | -122.0895
2837.4531 | 122.0627 | -0.09613 | 121.9803 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065996 | -0.0093137 | 0.053751 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.22081 | 15.3901 | 0.051108 | 122.0707 | 122.0012 | 121.9511 | -0.063057 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.11836 | 0.033073 | 0.090457 | 0.31694 | 0.14724 | 0.11417 | 0.020938 | -0.029179 | -0.022231 | -122.0606 | 0.12465 | 0.0352 | 0.057431 | -121.9574 | -121.9176 | 122.1669 | 122.0974 | 122.0472 | 15.4862 | -122.0433 | 0.015812 | 0.11899 | 0.15882 | 0.17433 | -122.0986
2839.1562 | 122.1313 | -0.091553 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065782 | -0.0090999 | 0.053538 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030057 | 0.015005 | 0.22997 | 15.4771 | 0.055687 | 122.0707 | 122.0012 | 121.9465 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.037654 | 0.10419 | 0.32152 | 0.14724 | 0.10959 | 0.034671 | -0.020024 | -0.01765 | -122.0514 | 0.11549 | 0.035202 | 0.052852 | -121.9437 | -121.9039 | 122.1623 | 122.0928 | 122.0381 | 15.5686 | -122.0205 | 0.006657 | 0.11442 | 0.15425 | 0.16975 | -122.0758
2840.9219 | 122.0078 | -0.11444 | 121.994 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065569 | -0.0093137 | 0.053538 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019613 | 0.030698 | 0.015005 | 0.22539 | 15.5687 | 0.055687 | 122.0799 | 122.0058 | 121.9465 | -0.058478 | 0.014784 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.055963 | 0.08588 | 0.33983 | 0.17013 | 0.11417 | 0.011784 | -0.04749 | 0.005238 | -122.0743 | 0.12923 | 0.053511 | 0.048273 | -121.9757 | -121.9267 | 122.1943 | 122.1202 | 122.061 | 15.6831 | -122.0525 | 0.034123 | 0.13273 | 0.18171 | 0.19264 | -122.1032
2842.6875 | 122.0261 | -0.1236 | 121.9849 | 1.4211e-13 | -0.043025 | 0.0020727 | 0.065569 | -0.0093137 | 0.053751 | -0.01755 | -0.0042257 | -0.0019123 | 0.019186 | 0.030912 | 0.015432 | 0.23912 | 15.6785 | 0.04653 | 122.0799 | 122.0058 | 121.9557 | -0.067636 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.05596 | 0.095036 | 0.36272 | 0.17013 | 0.11417 | 0.02094 | -0.029177 | 0.009814 | -122.0652 | 0.15212 | 0.067245 | 0.057431 | -121.962 | -121.9176 | 122.2035 | 122.1294 | 122.0793 | 15.8021 | -122.0525 | 0.043278 | 0.14646 | 0.19087 | 0.20637 | -122.0986
2844.3906 | 122.0215 | -0.12817 | 121.9757 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065782 | -0.0097409 | 0.053538 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030485 | 0.014791 | 0.22997 | 15.7426 | 0.055687 | 122.0707 | 122.0058 | 121.9557 | -0.063057 | 0.02852 | 0.073618 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.1092 | 0.065117 | 0.095035 | 0.35814 | 0.18386 | 0.11874 | 0.030095 | -0.020022 | 0.018971 | -122.0652 | 0.15669 | 0.067244 | 0.048273 | -121.9574 | -121.9176 | 122.1989 | 122.134 | 122.0839 | 15.8708 | -122.0388 | 0.038699 | 0.14646 | 0.18629 | 0.20179 | -122.0849
2846.1562 | 122.1588 | -0.091553 | 121.9299 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065996 | -0.0095273 | 0.053324 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030912 | 0.015005 | 0.23455 | 15.8571 | 0.04653 | 122.0753 | 122.0012 | 121.9465 | -0.058478 | 0.019362 | 0.073618 | -0.056351 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.033075 | 0.14539 | 0.3261 | 0.13808 | 0.10501 | 0.071292 | 0.016597 | -0.013071 | -122.0102 | 0.11091 | 0.035202 | 0.048273 | -121.9116 | -121.8627 | 122.1669 | 122.0928 | 122.0381 | 15.9487 | -121.9884 | 0.011235 | 0.10984 | 0.15882 | 0.16517 | -122.0346
2847.9219 | 122.1222 | -0.09613 | 121.9711 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065569 | -0.0095273 | 0.053538 | -0.0022892 | -0.0042257 | -0.0012713 | 0.019613 | 0.030912 | 0.015219 | 0.23455 | 15.9304 | 0.055687 | 122.0662 | 122.0058 | 121.9465 | -0.063057 | 0.014784 | 0.087354 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.11378 | 0.033073 | 0.095034 | 0.33067 | 0.15182 | 0.11874 | 0.034673 | -0.024601 | -0.017652 | -122.0606 | 0.11091 | 0.030621 | 0.048273 | -121.9574 | -121.9084 | 122.1623 | 122.1019 | 122.0427 | 16.0265 | -122.0342 | 0.006655 | 0.10984 | 0.15882 | 0.18348 | -122.0849
2849.6719 | 121.9986 | -0.14191 | 121.994 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065569 | -0.0095273 | 0.053965 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019186 | 0.030698 | 0.014791 | 0.23912 | 16.0403 | 0.055687 | 122.0753 | 122.0058 | 121.942 | -0.063057 | 0.023941 | 0.082776 | -0.065509 | -0.089475 | 0.018285 | 0.062694 | -0.10462 | 0.07885 | 0.081302 | 0.38103 | 0.19759 | 0.11874 | 0.011784 | -0.052069 | 0.037283 | -122.0835 | 0.16585 | 0.076398 | 0.039115 | -121.9757 | -121.9313 | 122.2172 | 122.1477 | 122.0839 | 16.1822 | -122.0571 | 0.052432 | 0.16019 | 0.2046 | 0.22468 | -122.0986
2851.4375 | 122.0444 | -0.11902 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0095273 | 0.053751 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030698 | 0.015005 | 0.24828 | 16.1364 | 0.055687 | 122.0799 | 121.9966 | 121.9603 | -0.058478 | 0.023941 | 0.087354 | -0.06093 | -0.084896 | 0.032021 | 0.062694 | -0.11378 | 0.060541 | 0.10419 | 0.3673 | 0.17471 | 0.11417 | 0.020938 | -0.015443 | 0.005237 | -122.0606 | 0.14296 | 0.058089 | 0.052852 | -121.9437 | -121.913 | 122.1989 | 122.1157 | 122.0793 | 16.2554 | -122.0342 | 0.034123 | 0.15104 | 0.18171 | 0.20637 | -122.0895
2853.2031 | 121.994 | -0.10986 | 122.0078 | 1.4211e-13 | -0.043239 | 0.0014317 | 0.065782 | -0.0095273 | 0.053965 | -0.0022892 | -0.0042257 | -0.0021259 | 0.019186 | 0.030912 | 0.015005 | 0.23912 | 16.2738 | 0.051108 | 122.0753 | 122.0012 | 121.9511 | -0.067636 | 0.02852 | 0.078197 | -0.06093 | -0.094053 | 0.032021 | 0.067272 | -0.1092 | 0.042227 | 0.06757 | 0.34899 | 0.16097 | 0.11874 | -0.006527 | -0.056644 | 0.00066 | -122.1018 | 0.13838 | 0.048933 | 0.048273 | -121.9757 | -121.9405 | 122.1852 | 122.1111 | 122.061 | 16.3836 | -122.0754 | 0.01581 | 0.14188 | 0.17713 | 0.18806 | -122.117
2854.9688 | 122.0261 | -0.10071 | 121.9849 | 1.4211e-13 | -0.043025 | 0.0016453 | 0.065569 | -0.0095273 | 0.053965 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.24828 | 16.3424 | 0.060265 | 122.0662 | 122.0058 | 121.9557 | -0.063057 | 0.023941 | 0.087354 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.037651 | 0.081301 | 0.34899 | 0.16097 | 0.12332 | 0.02094 | -0.029177 | -0.008495 | -122.0652 | 0.12465 | 0.039778 | 0.048273 | -121.9666 | -121.9222 | 122.1669 | 122.1065 | 122.0564 | 16.4431 | -122.0479 | 0.02039 | 0.11899 | 0.1634 | 0.18806 | -122.0941
2856.6875 | 122.0444 | -0.11902 | 121.962 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.065782 | -0.0090999 | 0.053751 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.030912 | 0.014791 | 0.25744 | 16.4477 | 0.069421 | 122.0707 | 122.0012 | 121.942 | -0.058478 | 0.02852 | 0.082776 | -0.056351 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.060541 | 0.10877 | 0.37646 | 0.18844 | 0.1279 | 0.039249 | -0.020025 | 0.005237 | -122.0469 | 0.14754 | 0.062668 | 0.057431 | -121.9391 | -121.8993 | 122.1898 | 122.1202 | 122.061 | 16.5668 | -122.0205 | 0.034123 | 0.14188 | 0.18171 | 0.2018 | -122.0758
2858.4531 | 122.1542 | -0.068665 | 121.9391 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018972 | 0.030485 | 0.015005 | 0.24828 | 16.5714 | 0.064843 | 122.0616 | 122.0058 | 121.9465 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.053537 | -0.10462 | 0.010187 | 0.1225 | 0.31695 | 0.13351 | 0.12332 | 0.066716 | 0.007442 | -0.035959 | -122.0286 | 0.092606 | 0.007735 | 0.043694 | -121.9162 | -121.8855 | 122.1303 | 122.0745 | 122.0152 | 16.64 | -121.9976 | -0.02081 | 0.091529 | 0.1222 | 0.14686 | -122.0437
2860.1562 | 122.1085 | -0.091553 | 121.9574 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065782 | -0.0095273 | 0.053538 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.030698 | 0.015005 | 0.25286 | 16.6446 | 0.060265 | 122.0753 | 122.0058 | 121.9465 | -0.053899 | 0.019362 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.10462 | 0.037654 | 0.11792 | 0.34441 | 0.15182 | 0.11416 | 0.048406 | -0.010868 | -0.013071 | -122.0377 | 0.11091 | 0.030623 | 0.043694 | -121.9345 | -121.8993 | 122.1669 | 122.0974 | 122.0381 | 16.7362 | -122.0113 | 0.011235 | 0.11442 | 0.14967 | 0.16517 | -122.062
2861.9219 | 122.0078 | -0.13733 | 121.9894 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.06621 | -0.0095273 | 0.053538 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019613 | 0.030698 | 0.015219 | 0.26202 | 16.7591 | 0.069421 | 122.0662 | 122.0058 | 121.9511 | -0.067636 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.062694 | -0.11378 | 0.069693 | 0.076723 | 0.39935 | 0.20675 | 0.13706 | 0.016362 | -0.038334 | 0.023547 | -122.0698 | 0.16585 | 0.076399 | 0.052852 | -121.9574 | -121.9267 | 122.2035 | 122.1431 | 122.0884 | 16.8964 | -122.0571 | 0.057011 | 0.16935 | 0.20002 | 0.2201 | -122.1032
2863.625 | 122.1222 | -0.086975 | 121.9482 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.06621 | -0.0097409 | 0.053538 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.031126 | 0.014578 | 0.26202 | 16.782 | 0.069421 | 122.0662 | 122.0012 | 121.9465 | -0.058478 | 0.023941 | 0.073618 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.1092 | 0.028497 | 0.11792 | 0.34899 | 0.1564 | 0.1279 | 0.052982 | -0.001713 | -0.022228 | -122.0377 | 0.11092 | 0.026045 | 0.048273 | -121.9254 | -121.881 | 122.1531 | 122.0882 | 122.0335 | 16.869 | -122.0067 | -0.0025 | 0.10984 | 0.15425 | 0.16059 | -122.0574
2865.3906 | 122.0169 | -0.13733 | 121.994 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065782 | -0.0095273 | 0.053538 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019399 | 0.030698 | 0.014578 | 0.27117 | 16.8781 | 0.064843 | 122.0707 | 122.0104 | 121.9557 | -0.058478 | 0.023941 | 0.091933 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.078851 | 0.076724 | 0.4085 | 0.20217 | 0.12332 | 0.016363 | -0.038333 | 0.028126 | -122.0789 | 0.16127 | 0.07182 | 0.043694 | -121.9712 | -121.9313 | 122.2081 | 122.1477 | 122.093 | 17.0155 | -122.0525 | 0.052433 | 0.16019 | 0.20002 | 0.22926 | -122.1032
2867.0938 | 122.1359 | -0.073242 | 121.9345 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065782 | -0.0093137 | 0.053538 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030485 | 0.015005 | 0.26202 | 16.9789 | 0.064843 | 122.0753 | 122.0012 | 121.9511 | -0.063057 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.027442 | 0.062694 | -0.1092 | 0.010185 | 0.14081 | 0.33526 | 0.13809 | 0.1279 | 0.066715 | 0.016598 | -0.035961 | -122.0102 | 0.10176 | 0.012312 | 0.048273 | -121.9071 | -121.8718 | 122.1486 | 122.0745 | 122.0243 | 17.0521 | -121.9976 | -0.002497 | 0.10068 | 0.13594 | 0.15602 | -122.0437
2868.875 | 122.1176 | -0.10071 | 121.962 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065782 | -0.0095273 | 0.053538 | -0.0022892 | -0.0046531 | -0.0012713 | 0.019399 | 0.030485 | 0.015005 | 0.27117 | 17.0842 | 0.078578 | 122.0662 | 122.0012 | 121.942 | -0.063057 | 0.014784 | 0.082776 | -0.056351 | -0.084896 | 0.027442 | 0.067272 | -0.1092 | 0.037651 | 0.10419 | 0.37188 | 0.17929 | 0.14164 | 0.039249 | -0.020025 | -0.008495 | -122.0469 | 0.11549 | 0.044357 | 0.052852 | -121.9345 | -121.8947 | 122.1669 | 122.1019 | 122.0427 | 17.1849 | -122.025 | 0.015812 | 0.12815 | 0.16798 | 0.18348 | -122.0712
2870.6406 | 122.0581 | -0.12817 | 122.0032 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065782 | -0.0095273 | 0.053965 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.030912 | 0.014364 | 0.27117 | 17.2032 | 0.069421 | 122.0707 | 122.0012 | 121.9511 | -0.058478 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.069696 | 0.067569 | 0.39935 | 0.1976 | 0.1279 | -0.00195 | -0.052067 | 0.014392 | -122.0835 | 0.14754 | 0.067244 | 0.052852 | -121.9757 | -121.9359 | 122.1989 | 122.1294 | 122.0793 | 17.3314 | -122.0617 | 0.047856 | 0.15562 | 0.19545 | 0.20637 | -122.117
2872.3281 | 122.0901 | -0.086975 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065996 | -0.0095273 | 0.053538 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019186 | 0.030698 | 0.014791 | 0.27575 | 17.3223 | 0.074 | 122.0707 | 122.0058 | 121.9511 | -0.063057 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.032021 | 0.071851 | -0.1092 | 0.023918 | 0.1225 | 0.36273 | 0.16097 | 0.13706 | 0.057561 | 0.002865 | -0.022228 | -122.0286 | 0.11092 | 0.021466 | 0.043694 | -121.9162 | -121.8764 | 122.1577 | 122.0928 | 122.0381 | 17.4092 | -122.0113 | 0.006657 | 0.119 | 0.15883 | 0.16517 | -122.0574
2874.0938 | 122.0169 | -0.11902 | 121.9894 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0093137 | 0.053965 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.030912 | 0.015219 | 0.27575 | 17.4138 | 0.069421 | 122.0662 | 122.0012 | 121.9557 | -0.063057 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.032021 | 0.062694 | -0.1092 | 0.055962 | 0.076723 | 0.39477 | 0.18844 | 0.13248 | 0.011783 | -0.033755 | 0.009816 | -122.0743 | 0.14754 | 0.05351 | 0.043694 | -121.9574 | -121.9267 | 122.1852 | 122.1202 | 122.0747 | 17.5329 | -122.0525 | 0.034123 | 0.15104 | 0.18171 | 0.19722 | -122.0986
2875.8438 | 122.0947 | -0.086975 | 121.9757 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065569 | -0.0095273 | 0.053538 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018972 | 0.030698 | 0.015005 | 0.27117 | 17.5191 | 0.078578 | 122.057 | 121.9966 | 121.9557 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.0366 | 0.053537 | -0.11378 | 0.033076 | 0.081299 | 0.35815 | 0.16555 | 0.13248 | 0.020938 | -0.020022 | -0.026807 | -122.056 | 0.11092 | 0.026045 | 0.052852 | -121.9391 | -121.9222 | 122.144 | 122.0836 | 122.0427 | 17.6061 | -122.0296 | 0.006657 | 0.12357 | 0.14051 | 0.16975 | -122.0895
2877.6094 | 122.0215 | -0.11444 | 121.9711 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.065355 | -0.0095273 | 0.053751 | -0.01755 | -0.0042257 | -0.0012713 | 0.019399 | 0.030698 | 0.015005 | 0.28491 | 17.6199 | 0.078578 | 122.0662 | 122.0012 | 121.9557 | -0.063057 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.051384 | 0.095034 | 0.39935 | 0.19302 | 0.14164 | 0.030094 | -0.015444 | 0.000659 | -122.0514 | 0.13838 | 0.053511 | 0.052852 | -121.9483 | -121.9039 | 122.1806 | 122.1157 | 122.0701 | 17.7343 | -122.0342 | 0.034123 | 0.13731 | 0.18171 | 0.19264 | -122.0849
2879.2969 | 122.1176 | -0.09613 | 121.9574 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.06621 | -0.0093137 | 0.053751 | -0.01755 | -0.0042257 | -0.0019123 | 0.018972 | 0.030485 | 0.015005 | 0.28949 | 17.6885 | 0.083156 | 122.0662 | 121.9966 | 121.9511 | -0.063057 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.027442 | 0.071851 | -0.11378 | 0.033073 | 0.10877 | 0.38562 | 0.17929 | 0.14621 | 0.039249 | -0.00629 | -0.017652 | -122.0423 | 0.12007 | 0.030621 | 0.048273 | -121.93 | -121.8855 | 122.1623 | 122.0928 | 122.0472 | 17.7847 | -122.0205 | 0.011234 | 0.12357 | 0.16798 | 0.17433 | -122.0712
2881.0625 | 122.0123 | -0.13275 | 121.9849 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.065782 | -0.0095273 | 0.053538 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.030912 | 0.015005 | 0.29406 | 17.771 | 0.087735 | 122.0662 | 121.9966 | 121.9511 | -0.058478 | 0.023941 | 0.087354 | -0.056351 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.074273 | 0.081301 | 0.42681 | 0.22049 | 0.14621 | 0.011783 | -0.033756 | 0.023548 | -122.0698 | 0.15669 | 0.0764 | 0.052852 | -121.9574 | -121.9222 | 122.1989 | 122.1294 | 122.0839 | 17.9037 | -122.0433 | 0.047855 | 0.16019 | 0.19545 | 0.2201 | -122.0941
2882.8281 | 122.0306 | -0.13275 | 121.9528 | 1.4211e-13 | -0.043239 | 0.0012179 | 0.065569 | -0.0099547 | 0.053538 | -0.01755 | -0.0042257 | -0.0016987 | 0.019186 | 0.030485 | 0.015005 | 0.28949 | 17.8122 | 0.096891 | 122.057 | 121.9966 | 121.9465 | -0.053899 | 0.033099 | 0.087354 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.078852 | 0.10419 | 0.42224 | 0.22964 | 0.15079 | 0.043826 | -0.006291 | 0.018969 | -122.0286 | 0.16585 | 0.071821 | 0.052852 | -121.9254 | -121.8855 | 122.1898 | 122.1294 | 122.0793 | 17.9449 | -122.0067 | 0.057012 | 0.16019 | 0.20002 | 0.2201 | -122.0666
2884.5312 | 121.9986 | -0.11902 | 121.9849 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065569 | -0.0095273 | 0.053751 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030912 | 0.015005 | 0.29864 | 17.9404 | 0.092313 | 122.0753 | 122.0104 | 121.9511 | -0.063057 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.022864 | 0.071851 | -0.11378 | 0.055962 | 0.090458 | 0.41766 | 0.21133 | 0.15537 | 0.025519 | -0.033756 | 0.005237 | -122.0698 | 0.14296 | 0.05351 | 0.048273 | -121.962 | -121.913 | 122.1943 | 122.1294 | 122.0701 | 18.0594 | -122.0479 | 0.034123 | 0.14188 | 0.19087 | 0.19264 | -122.0986
2886.2969 | 122.1176 | -0.082397 | 121.9437 | 1.4211e-13 | -0.04388 | 0.0018589 | 0.06621 | -0.0095273 | 0.053965 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030698 | 0.015005 | 0.29864 | 18.0365 | 0.092313 | 122.0662 | 122.0012 | 121.9557 | -0.063057 | 0.023941 | 0.082776 | -0.056351 | -0.084896 | 0.022864 | 0.058115 | -0.1092 | 0.01934 | 0.1225 | 0.38104 | 0.17471 | 0.15537 | 0.057559 | 0.012021 | -0.026806 | -122.0286 | 0.10634 | 0.026046 | 0.052852 | -121.9208 | -121.8855 | 122.1486 | 122.0836 | 122.0381 | 18.1189 | -122.0067 | -0.002499 | 0.10526 | 0.14051 | 0.16517 | -122.0529
2888.0625 | 122.049 | -0.11444 | 121.9482 | 1.4211e-13 | -0.043239 | 0.0014317 | 0.065569 | -0.0093137 | 0.053965 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.030485 | 0.015005 | 0.3078 | 18.1144 | 0.083156 | 122.0662 | 122.0012 | 121.9465 | -0.058478 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.055963 | 0.11792 | 0.42224 | 0.1976 | 0.14163 | 0.052982 | -0.001713 | 0.005238 | -122.0286 | 0.13838 | 0.053511 | 0.048273 | -121.9254 | -121.8855 | 122.1806 | 122.1157 | 122.061 | 18.2288 | -122.0067 | 0.034123 | 0.13731 | 0.17713 | 0.19722 | -122.0574
2889.8281 | 122.0901 | -0.11444 | 121.9391 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.065569 | -0.0093137 | 0.053965 | -0.0022892 | -0.0037985 | -0.0016987 | 0.019186 | 0.030912 | 0.014791 | 0.29864 | 18.2517 | 0.087735 | 122.0662 | 121.9921 | 121.9465 | -0.063057 | 0.014784 | 0.082776 | -0.065509 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.051384 | 0.12708 | 0.41308 | 0.20218 | 0.15079 | 0.05298 | 0.007442 | 0.005238 | -122.024 | 0.12923 | 0.048932 | 0.043694 | -121.9208 | -121.881 | 122.1806 | 122.1065 | 122.061 | 18.3662 | -122.0021 | 0.029545 | 0.13273 | 0.17256 | 0.19722 | -122.0483
2891.5469 | 122.1497 | -0.082397 | 121.9482 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.065569 | -0.0095273 | 0.053965 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019399 | 0.031126 | 0.015005 | 0.3078 | 18.325 | 0.096891 | 122.0662 | 122.0012 | 121.9511 | -0.063057 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.10462 | 0.01934 | 0.11792 | 0.3902 | 0.17929 | 0.15995 | 0.052982 | 0.002865 | -0.022227 | -122.0286 | 0.10634 | 0.021467 | 0.043694 | -121.9208 | -121.8855 | 122.1486 | 122.0836 | 122.0335 | 18.4074 | -122.0113 | 0.002079 | 0.10984 | 0.14509 | 0.16517 | -122.0529
2893.3125 | 121.994 | -0.10529 | 121.9711 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065996 | -0.0097409 | 0.053751 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030912 | 0.015005 | 0.31696 | 18.4394 | 0.096891 | 122.0662 | 122.0012 | 121.9603 | -0.067636 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | 0.03765 | 0.095034 | 0.42224 | 0.20218 | 0.16453 | 0.030094 | -0.010865 | 0.000662 | -122.0514 | 0.12465 | 0.044356 | 0.043694 | -121.9483 | -121.9084 | 122.1715 | 122.1065 | 122.0656 | 18.5447 | -122.0388 | 0.024968 | 0.12815 | 0.16798 | 0.18806 | -122.0758
2895.0625 | 122.1085 | -0.082397 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065996 | -0.0093137 | 0.053538 | -0.01755 | -0.0044395 | -0.0019123 | 0.019399 | 0.030485 | 0.014791 | 0.32154 | 18.4944 | 0.10147 | 122.0707 | 121.9966 | 121.9557 | -0.063057 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.01934 | 0.11792 | 0.40393 | 0.18387 | 0.16453 | 0.043826 | 0.002866 | -0.031385 | -122.0377 | 0.10634 | 0.016888 | 0.048273 | -121.9254 | -121.8855 | 122.1531 | 122.079 | 122.0381 | 18.5768 | -122.0159 | -0.002499 | 0.10984 | 0.14967 | 0.15602 | -122.0666
2896.7656 | 122.1222 | -0.082397 | 121.9528 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.065996 | -0.0093137 | 0.053965 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.030485 | 0.014791 | 0.31696 | 18.5676 | 0.10147 | 122.0616 | 122.0058 | 121.9465 | -0.067636 | 0.019362 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.058115 | -0.10462 | 0.014761 | 0.10877 | 0.39935 | 0.18387 | 0.16911 | 0.052983 | -0.006291 | -0.022227 | -122.0331 | 0.10176 | 0.026046 | 0.048273 | -121.9254 | -121.8947 | 122.144 | 122.0882 | 122.0289 | 18.65 | -122.0205 | 0.002079 | 0.10984 | 0.14051 | 0.16517 | -122.0574
2898.5312 | 122.1176 | -0.09613 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0095273 | 0.053751 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030698 | 0.015005 | 0.32611 | 18.6409 | 0.11063 | 122.0616 | 122.0058 | 121.9465 | -0.063057 | 0.02852 | 0.082776 | -0.065509 | -0.084896 | 0.032021 | 0.067272 | -0.1092 | 0.033073 | 0.11334 | 0.42224 | 0.20676 | 0.17368 | 0.057561 | -0.001713 | -0.013073 | -122.0331 | 0.12465 | 0.030621 | 0.043694 | -121.9162 | -121.881 | 122.1577 | 122.1019 | 122.0427 | 18.737 | -122.0113 | 0.011234 | 0.12815 | 0.1634 | 0.17891 | -122.0574
2900.2969 | 122.1222 | -0.07782 | 121.9345 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065569 | -0.0090999 | 0.053751 | -0.01755 | -0.0040121 | -0.0012713 | 0.019399 | 0.030912 | 0.014791 | 0.32154 | 18.7508 | 0.10605 | 122.0662 | 122.0058 | 121.9511 | -0.063057 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.014763 | 0.13165 | 0.39936 | 0.18387 | 0.16911 | 0.071294 | 0.016598 | -0.035962 | -122.0148 | 0.10176 | 0.012311 | 0.048273 | -121.9116 | -121.8672 | 122.144 | 122.0836 | 122.0289 | 18.8286 | -121.9976 | -0.002498 | 0.10068 | 0.14509 | 0.15602 | -122.0483
2902.0625 | 122.1313 | -0.07782 | 121.9162 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065996 | -0.0095273 | 0.053751 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019399 | 0.030057 | 0.014791 | 0.33527 | 18.8103 | 0.10147 | 122.0616 | 122.0012 | 121.9465 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.005605 | 0.14539 | 0.41309 | 0.17929 | 0.17368 | 0.085025 | 0.03033 | -0.031383 | -122.0011 | 0.10176 | 0.01689 | 0.048273 | -121.8933 | -121.8535 | 122.1394 | 122.079 | 122.0243 | 18.8881 | -121.9884 | -0.007076 | 0.10068 | 0.14051 | 0.15602 | -122.0254
2903.8281 | 121.9986 | -0.11902 | 122.0169 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065996 | -0.0090999 | 0.053538 | -0.0022892 | -0.0044395 | -0.0012713 | 0.019186 | 0.030698 | 0.015005 | 0.32611 | 18.8652 | 0.10605 | 122.0662 | 122.0058 | 121.9465 | -0.058478 | 0.019362 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.060541 | 0.049257 | 0.44513 | 0.22507 | 0.16453 | -0.011104 | -0.070378 | 0.005237 | -122.0972 | 0.13838 | 0.062668 | 0.057431 | -121.994 | -121.9496 | 122.1852 | 122.1248 | 122.0655 | 18.9843 | -122.0754 | 0.038701 | 0.14188 | 0.18629 | 0.2018 | -122.1307
2905.5156 | 122.1313 | -0.10529 | 121.9437 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.06621 | -0.0093137 | 0.053751 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 0.33069 | 18.9156 | 0.11063 | 122.0616 | 122.0012 | 121.9465 | -0.063057 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.027442 | 0.058115 | -0.11378 | 0.042229 | 0.11792 | 0.43598 | 0.21591 | 0.17368 | 0.057559 | 0.002864 | -0.008496 | -122.024 | 0.12923 | 0.044356 | 0.052852 | -121.9162 | -121.8855 | 122.1669 | 122.1065 | 122.0518 | 19.0209 | -122.0067 | 0.024968 | 0.13273 | 0.1634 | 0.1789 | -122.0574
2907.2812 | 122.0306 | -0.1236 | 121.9711 | 1.4211e-13 | -0.043025 | 0.0020727 | 0.065996 | -0.0095273 | 0.053751 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019186 | 0.030485 | 0.015005 | 0.33985 | 18.998 | 0.11978 | 122.057 | 122.0012 | 121.9511 | -0.063057 | 0.023941 | 0.087354 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.060539 | 0.085877 | 0.46344 | 0.24338 | 0.18284 | 0.030094 | -0.020023 | 0.009814 | -122.0514 | 0.14754 | 0.062666 | 0.052852 | -121.9437 | -121.9084 | 122.1806 | 122.1248 | 122.0747 | 19.1216 | -122.0342 | 0.043278 | 0.15104 | 0.18629 | 0.21095 | -122.0849
2909.0469 | 122.1405 | -0.068665 | 121.9391 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065996 | -0.0093137 | 0.053751 | -0.01755 | -0.0040121 | -0.0016987 | 0.019613 | 0.030912 | 0.014791 | 0.33527 | 18.966 | 0.11063 | 122.0616 | 122.0012 | 121.9511 | -0.058478 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.010187 | 0.1225 | 0.40394 | 0.17929 | 0.1691 | 0.062137 | 0.01202 | -0.040538 | -122.0194 | 0.092606 | 0.003156 | 0.043694 | -121.9162 | -121.881 | 122.1303 | 122.0699 | 122.0198 | 19.0346 | -121.9976 | -0.011653 | 0.091529 | 0.12678 | 0.14686 | -122.0483
2910.75 | 122.0123 | -0.1236 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066423 | -0.0097409 | 0.053751 | 0.0053413 | -0.0042257 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 0.33985 | 19.0072 | 0.1152 | 122.0707 | 122.0058 | 121.9465 | -0.058478 | 0.023941 | 0.082776 | -0.06093 | -0.089475 | 0.022864 | 0.062694 | -0.10462 | 0.065118 | 0.11792 | 0.46344 | 0.2388 | 0.17368 | 0.052983 | -0.006291 | 0.018972 | -122.0423 | 0.14754 | 0.062666 | 0.043694 | -121.93 | -121.8901 | 122.1943 | 122.1294 | 122.0701 | 19.1308 | -122.0113 | 0.034121 | 0.14646 | 0.18629 | 0.20637 | -122.0574
2912.5312 | 122.0444 | -0.13733 | 121.9757 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065569 | -0.0093137 | 0.053538 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019399 | 0.030485 | 0.015005 | 0.33985 | 19.0988 | 0.11063 | 122.0616 | 122.0058 | 121.9511 | -0.063057 | 0.023941 | 0.06904 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.074272 | 0.085878 | 0.47718 | 0.24796 | 0.17368 | 0.030095 | -0.024601 | 0.023547 | -122.0514 | 0.16127 | 0.07182 | 0.048273 | -121.9483 | -121.9084 | 122.1989 | 122.1431 | 122.0884 | 19.2361 | -122.0388 | 0.06159 | 0.16477 | 0.2046 | 0.20637 | -122.0895
2914.2969 | 122.0398 | -0.10529 | 121.9437 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065782 | -0.0095273 | 0.053751 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.014791 | 0.34901 | 19.1858 | 0.11978 | 122.0616 | 121.9966 | 121.9465 | -0.063057 | 0.023941 | 0.073618 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.11836 | 0.042229 | 0.11792 | 0.45429 | 0.22507 | 0.18284 | 0.052981 | 0.002864 | -0.013075 | -122.024 | 0.12923 | 0.039777 | 0.052852 | -121.9254 | -121.8764 | 122.1669 | 122.1019 | 122.0518 | 19.291 | -122.0067 | 0.024968 | 0.12357 | 0.17256 | 0.1789 | -122.062
2916.0156 | 121.994 | -0.11444 | 121.9849 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.066423 | -0.0095273 | 0.053965 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030912 | 0.014791 | 0.35358 | 19.2544 | 0.1152 | 122.057 | 122.0012 | 121.9557 | -0.063057 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.022864 | 0.067272 | -0.1092 | 0.051384 | 0.072144 | 0.46802 | 0.22964 | 0.17826 | 0.016361 | -0.029177 | 0.005238 | -122.0606 | 0.13838 | 0.053511 | 0.048273 | -121.962 | -121.9176 | 122.1714 | 122.1157 | 122.0701 | 19.3689 | -122.0479 | 0.038702 | 0.13731 | 0.18171 | 0.19722 | -122.0941
2917.7188 | 122.0123 | -0.11902 | 121.9894 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.065996 | -0.0090999 | 0.053965 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019399 | 0.030912 | 0.014578 | 0.34901 | 19.4009 | 0.12436 | 122.057 | 122.0012 | 121.9465 | -0.063057 | 0.02852 | 0.078197 | -0.065509 | -0.084896 | 0.018285 | 0.071851 | -0.10462 | 0.055962 | 0.067566 | 0.46802 | 0.24338 | 0.18742 | 0.011783 | -0.042912 | 0.014395 | -122.0743 | 0.14754 | 0.05351 | 0.039115 | -121.9712 | -121.9176 | 122.176 | 122.1202 | 122.0655 | 19.52 | -122.0525 | 0.034123 | 0.1373 | 0.19087 | 0.19722 | -122.0941
2919.4219 | 122.1222 | -0.07782 | 121.9391 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.065996 | -0.0095273 | 0.053751 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018972 | 0.030698 | 0.015005 | 0.34901 | 19.4376 | 0.12436 | 122.0662 | 121.9966 | 121.9465 | -0.058478 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.018285 | 0.067272 | -0.11378 | 0.019342 | 0.12708 | 0.42683 | 0.20218 | 0.18284 | 0.057559 | 0.007442 | -0.035962 | -122.0148 | 0.10176 | 0.012311 | 0.048273 | -121.9208 | -121.8718 | 122.144 | 122.0745 | 122.0243 | 19.5154 | -121.9976 | 0.002081 | 0.096105 | 0.14509 | 0.1606 | -122.0529
2921.1875 | 122.0078 | -0.13733 | 121.9894 | 1.4211e-13 | -0.043025 | 0.0014317 | 0.065996 | -0.0097409 | 0.053965 | -0.01755 | -0.0044395 | -0.0014849 | 0.019399 | 0.030485 | 0.015005 | 0.36274 | 19.4788 | 0.12436 | 122.0616 | 121.9966 | 121.9511 | -0.058478 | 0.019362 | 0.087354 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.078851 | 0.072145 | 0.50007 | 0.26169 | 0.18284 | 0.007205 | -0.038334 | 0.032705 | -122.0698 | 0.15669 | 0.076399 | 0.043694 | -121.9712 | -121.9222 | 122.1989 | 122.134 | 122.0884 | 19.6161 | -122.0479 | 0.057011 | 0.15561 | 0.2046 | 0.22468 | -122.0941
2922.9531 | 122.1085 | -0.07782 | 121.9299 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065996 | -0.0095273 | 0.053751 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030912 | 0.014791 | 0.36732 | 19.5932 | 0.12894 | 122.057 | 122.0012 | 121.9465 | -0.063057 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.067272 | -0.11836 | 0.014763 | 0.12708 | 0.44514 | 0.20676 | 0.192 | 0.071292 | 0.016597 | -0.040541 | -122.0102 | 0.097182 | 0.012311 | 0.052852 | -121.9071 | -121.8627 | 122.1348 | 122.079 | 122.0243 | 19.6711 | -121.993 | -0.002498 | 0.10068 | 0.14509 | 0.15602 | -122.0483
2924.7188 | 122.0856 | -0.09613 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.06621 | -0.0097409 | 0.053751 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.030485 | 0.015005 | 0.36274 | 19.6619 | 0.13352 | 122.0616 | 121.9921 | 121.9465 | -0.063057 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.11378 | 0.033073 | 0.095033 | 0.45887 | 0.22965 | 0.19657 | 0.025514 | -0.020024 | -0.017652 | -122.0469 | 0.12007 | 0.0352 | 0.052852 | -121.9437 | -121.9039 | 122.1577 | 122.0882 | 122.0427 | 19.7581 | -122.0296 | 0.015812 | 0.11899 | 0.15882 | 0.16975 | -122.0803
2926.5 | 122.1542 | -0.064087 | 121.9299 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065996 | -0.0095273 | 0.053751 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.030698 | 0.015005 | 0.3719 | 19.7169 | 0.1381 | 122.0662 | 121.9966 | 121.942 | -0.067636 | 0.019362 | 0.078197 | -0.056351 | -0.084896 | 0.022864 | 0.071851 | -0.11378 | -0.003549 | 0.13623 | 0.43598 | 0.20218 | 0.20573 | 0.066714 | 0.012018 | -0.049695 | -122.0148 | 0.083449 | 0.007736 | 0.057431 | -121.9071 | -121.8581 | 122.1303 | 122.0607 | 122.006 | 19.781 | -121.9976 | -0.020809 | 0.086951 | 0.13594 | 0.14228 | -122.0437
2928.2656 | 122.0123 | -0.11902 | 121.9803 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.06621 | -0.0095273 | 0.053965 | -0.01755 | -0.0044395 | -0.0014849 | 0.019399 | 0.030698 | 0.015432 | 0.37648 | 19.7993 | 0.13352 | 122.057 | 121.9966 | 121.942 | -0.063057 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.027442 | 0.062694 | -0.11836 | 0.055962 | 0.076721 | 0.49549 | 0.25254 | 0.19657 | 0.01636 | -0.038336 | 0.000658 | -122.0652 | 0.14296 | 0.05351 | 0.052852 | -121.9528 | -121.9176 | 122.176 | 122.1157 | 122.061 | 19.9183 | -122.0433 | 0.034123 | 0.14646 | 0.18171 | 0.19722 | -122.0986
2930.0312 | 122.0444 | -0.10529 | 121.9757 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.065996 | -0.0093137 | 0.053965 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019186 | 0.031126 | 0.015005 | 0.37648 | 19.8909 | 0.1381 | 122.0616 | 122.0012 | 121.9465 | -0.063057 | 0.023941 | 0.082776 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.1092 | 0.042229 | 0.085878 | 0.48176 | 0.24338 | 0.20115 | 0.025516 | -0.029179 | -0.003917 | -122.0652 | 0.12923 | 0.044356 | 0.048273 | -121.9528 | -121.9084 | 122.1669 | 122.1065 | 122.0518 | 19.9961 | -122.0388 | 0.015811 | 0.12815 | 0.17256 | 0.18806 | -122.0849
2931.75 | 122.0032 | -0.1236 | 121.9711 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.06621 | -0.0095273 | 0.053751 | -0.0099192 | -0.0040121 | -0.0019123 | 0.019186 | 0.030698 | 0.014791 | 0.37648 | 19.9916 | 0.14267 | 122.0616 | 121.9966 | 121.9465 | -0.067636 | 0.023941 | 0.078197 | -0.051772 | -0.084896 | 0.018285 | 0.067272 | -0.1092 | 0.05596 | 0.090456 | 0.50007 | 0.26627 | 0.21031 | 0.025516 | -0.024601 | 0.014393 | -122.056 | 0.14754 | 0.071824 | 0.057431 | -121.9528 | -121.9039 | 122.1852 | 122.1202 | 122.0701 | 20.1152 | -122.0388 | 0.0387 | 0.14188 | 0.19087 | 0.20179 | -122.0803
2933.5156 | 122.1451 | -0.068665 | 121.9208 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.06621 | -0.0095273 | 0.053751 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.030698 | 0.014578 | 0.38105 | 20.0557 | 0.14267 | 122.057 | 122.0012 | 121.9557 | -0.067636 | 0.014784 | 0.087354 | -0.051772 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.001029 | 0.13623 | 0.44972 | 0.21134 | 0.21031 | 0.080448 | 0.03491 | -0.035959 | -122.0011 | 0.083449 | 0.016893 | 0.052852 | -121.9025 | -121.8535 | 122.1257 | 122.0699 | 122.0244 | 20.1244 | -121.9884 | -0.011653 | 0.08695 | 0.13594 | 0.15602 | -122.0254
2935.2188 | 122.1451 | -0.073242 | 121.9391 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0097409 | 0.053751 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.030698 | 0.014791 | 0.38563 | 20.1381 | 0.14267 | 122.057 | 122.0012 | 121.942 | -0.067636 | 0.019362 | 0.073618 | -0.070087 | -0.080318 | 0.013707 | 0.062694 | -0.11378 | 0.005606 | 0.11792 | 0.45887 | 0.21592 | 0.21031 | 0.062137 | 0.002863 | -0.04054 | -122.0194 | 0.092604 | 0.003155 | 0.043695 | -121.9254 | -121.8764 | 122.1302 | 122.0745 | 122.0152 | 20.2113 | -122.0067 | -0.007076 | 0.086949 | 0.13594 | 0.14686 | -122.0529
2936.9844 | 122.0032 | -0.13275 | 121.994 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0095273 | 0.053751 | -0.01755 | -0.0042257 | -0.0016987 | 0.019186 | 0.030698 | 0.015005 | 0.38563 | 20.1976 | 0.14725 | 122.0616 | 122.0058 | 121.9465 | -0.067636 | 0.014784 | 0.087354 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.065115 | 0.067567 | 0.51838 | 0.28 | 0.21489 | 0.011784 | -0.04749 | 0.023548 | -122.0743 | 0.14753 | 0.071821 | 0.048273 | -121.9757 | -121.9267 | 122.1943 | 122.1386 | 122.0793 | 20.3304 | -122.0617 | 0.052433 | 0.15104 | 0.20002 | 0.2201 | -122.1032
2938.75 | 122.0718 | -0.091553 | 121.9803 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.06621 | -0.0095273 | 0.053538 | 0.0053413 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014578 | 0.39021 | 20.248 | 0.15183 | 122.0524 | 121.9966 | 121.9465 | -0.067636 | 0.019362 | 0.078197 | -0.065509 | -0.089475 | 0.013707 | 0.062694 | -0.11836 | 0.023917 | 0.072143 | 0.48176 | 0.24338 | 0.21947 | 0.01636 | -0.033757 | -0.026808 | -122.0698 | 0.11091 | 0.026044 | 0.052852 | -121.9666 | -121.9176 | 122.144 | 122.0882 | 122.0381 | 20.3395 | -122.0479 | 0.002078 | 0.10526 | 0.15425 | 0.16975 | -122.0986
2940.5156 | 122.0215 | -0.11902 | 121.9757 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.06621 | -0.0097409 | 0.053751 | -0.0022892 | -0.0048667 | -0.0016987 | 0.019613 | 0.030698 | 0.015005 | 0.39479 | 20.2984 | 0.15183 | 122.0524 | 121.9875 | 121.9511 | -0.067636 | 0.02852 | 0.078197 | -0.051772 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.051383 | 0.076721 | 0.51381 | 0.27085 | 0.21947 | 0.01178 | -0.024601 | 0.005237 | -122.056 | 0.14754 | 0.067247 | 0.06201 | -121.9528 | -121.9084 | 122.1714 | 122.1065 | 122.0701 | 20.4174 | -122.0433 | 0.038701 | 0.14188 | 0.18629 | 0.19722 | -122.0895
2942.2188 | 122.1039 | -0.09613 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0099547 | 0.053965 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019399 | 0.030912 | 0.014791 | 0.40395 | 20.3579 | 0.14725 | 122.0524 | 121.9966 | 121.9511 | -0.063057 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.11378 | 0.033073 | 0.099609 | 0.50008 | 0.24338 | 0.21031 | 0.043826 | -0.001713 | -0.017652 | -122.0331 | 0.12007 | 0.030621 | 0.048273 | -121.9345 | -121.8855 | 122.1486 | 122.0928 | 122.0472 | 20.454 | -122.0159 | 0.015812 | 0.11441 | 0.1634 | 0.17891 | -122.0666
2943.9844 | 122.0581 | -0.11902 | 121.9391 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.066423 | -0.0095273 | 0.053751 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019186 | 0.030485 | 0.014791 | 0.40395 | 20.4037 | 0.14725 | 122.0662 | 121.9966 | 121.942 | -0.063057 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.055962 | 0.12708 | 0.52297 | 0.26627 | 0.21031 | 0.057559 | 0.002863 | 0.009816 | -122.024 | 0.14296 | 0.062668 | 0.052852 | -121.9162 | -121.8764 | 122.1852 | 122.1157 | 122.061 | 20.5227 | -122.0021 | 0.034123 | 0.14188 | 0.18171 | 0.19722 | -122.0483
2945.75 | 122.0261 | -0.12817 | 121.962 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.066423 | -0.0093137 | 0.053751 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.030912 | 0.014791 | 0.40395 | 20.5135 | 0.15641 | 122.057 | 121.9966 | 121.9465 | -0.067636 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.060538 | 0.095032 | 0.53212 | 0.28458 | 0.22404 | 0.034671 | -0.015446 | 0.014392 | -122.0469 | 0.15212 | 0.067244 | 0.052852 | -121.9391 | -121.8993 | 122.1852 | 122.1248 | 122.0747 | 20.6417 | -122.0296 | 0.043278 | 0.15104 | 0.19087 | 0.21095 | -122.0758
2947.5156 | 122.049 | -0.11902 | 121.962 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.06621 | -0.0093137 | 0.053965 | -0.01755 | -0.0046531 | -0.0019123 | 0.018758 | 0.030698 | 0.014791 | 0.40852 | 20.454 | 0.15641 | 122.0616 | 121.9966 | 121.9374 | -0.067636 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.11378 | 0.051383 | 0.099611 | 0.52754 | 0.27543 | 0.22404 | 0.034671 | -0.024603 | 0.005237 | -122.0469 | 0.14296 | 0.058089 | 0.052852 | -121.9437 | -121.8993 | 122.1806 | 122.1157 | 122.0564 | 20.573 | -122.0296 | 0.034123 | 0.1373 | 0.18171 | 0.2018 | -122.0758
2949.2656 | 121.9894 | -0.13733 | 121.9711 | 1.4211e-13 | -0.043239 | 0.0016453 | 0.065996 | -0.0097409 | 0.053965 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019186 | 0.030698 | 0.015005 | 0.4131 | 20.4861 | 0.16099 | 122.0662 | 121.9966 | 121.9465 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | 0.065114 | 0.095034 | 0.55043 | 0.29832 | 0.2332 | 0.025516 | -0.024601 | 0.028126 | -122.0514 | 0.16127 | 0.076399 | 0.048273 | -121.9528 | -121.9084 | 122.2035 | 122.134 | 122.0839 | 20.6234 | -122.0433 | 0.057011 | 0.15561 | 0.20002 | 0.21553 | -122.0803
2950.9688 | 122.0581 | -0.10529 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065996 | -0.0093137 | 0.053965 | -0.0022892 | -0.0042257 | -0.0019123 | 0.019186 | 0.030485 | 0.014791 | 0.41768 | 20.5319 | 0.16099 | 122.0616 | 122.0012 | 121.9465 | -0.063057 | 0.02852 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.067272 | -0.1092 | 0.042229 | 0.11334 | 0.52297 | 0.26627 | 0.22404 | 0.052982 | -0.001713 | -0.003917 | -122.0331 | 0.13381 | 0.044356 | 0.048273 | -121.9254 | -121.881 | 122.1669 | 122.1065 | 122.0518 | 20.6371 | -122.0113 | 0.02039 | 0.12815 | 0.17256 | 0.18806 | -122.0574
2952.7344 | 122.0352 | -0.10529 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.066423 | -0.0095273 | 0.053965 | -0.01755 | -0.0044395 | -0.0019123 | 0.019186 | 0.030912 | 0.014791 | 0.41768 | 20.5822 | 0.16556 | 122.0616 | 121.9921 | 121.942 | -0.067636 | 0.019362 | 0.082776 | -0.06093 | -0.084896 | 0.018285 | 0.067272 | -0.10462 | 0.03765 | 0.10877 | 0.52297 | 0.27085 | 0.2332 | 0.039247 | -0.01087 | 0.000662 | -122.0377 | 0.12465 | 0.044356 | 0.043694 | -121.9345 | -121.8855 | 122.1669 | 122.0974 | 122.0472 | 20.6875 | -122.0205 | 0.02039 | 0.12357 | 0.17256 | 0.18806 | -122.0574
2954.4219 | 122.1451 | -0.082397 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.06621 | -0.0095273 | 0.053965 | -0.01755 | -0.0046531 | -0.0019123 | 0.018972 | 0.030698 | 0.014791 | 0.42226 | 20.628 | 0.16099 | 122.057 | 121.9921 | 121.9511 | -0.067636 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.067272 | -0.11378 | 0.014761 | 0.10419 | 0.50466 | 0.24338 | 0.22862 | 0.039247 | -0.001713 | -0.031385 | -122.0377 | 0.10634 | 0.021467 | 0.052852 | -121.93 | -121.8855 | 122.1394 | 122.0745 | 122.0335 | 20.7104 | -122.0205 | -0.002499 | 0.10526 | 0.14967 | 0.16059 | -122.0666
2956.1875 | 122.1313 | -0.068665 | 121.9528 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.066423 | -0.0095273 | 0.053538 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.030912 | 0.014791 | 0.43142 | 20.6463 | 0.16556 | 122.057 | 121.9966 | 121.9465 | -0.063057 | 0.014784 | 0.082776 | -0.06093 | -0.084896 | 0.032021 | 0.071851 | -0.11378 | 0.005608 | 0.10419 | 0.50008 | 0.23423 | 0.22862 | 0.043826 | -0.006291 | -0.045117 | -122.0377 | 0.083449 | 0.007735 | 0.052852 | -121.9208 | -121.881 | 122.1257 | 122.0653 | 122.0152 | 20.715 | -122.0159 | -0.016231 | 0.10069 | 0.14052 | 0.15144 | -122.0666
2957.9531 | 122.0169 | -0.13275 | 121.9711 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.06621 | -0.0095273 | 0.053965 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019399 | 0.030698 | 0.014578 | 0.43599 | 20.6875 | 0.17014 | 122.057 | 121.9921 | 121.9465 | -0.063057 | 0.02852 | 0.082776 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.10462 | 0.069694 | 0.085877 | 0.56875 | 0.3029 | 0.2332 | 0.020937 | -0.024601 | 0.028127 | -122.0514 | 0.16127 | 0.067242 | 0.039115 | -121.9437 | -121.9084 | 122.1898 | 122.1248 | 122.0793 | 20.8203 | -122.0342 | 0.052433 | 0.16019 | 0.19545 | 0.21553 | -122.0758
2959.7031 | 122.0901 | -0.11444 | 121.9437 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.06621 | -0.0093137 | 0.053965 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019186 | 0.030698 | 0.015219 | 0.43599 | 20.7425 | 0.16556 | 122.057 | 121.9921 | 121.942 | -0.067636 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.018285 | 0.058115 | -0.1092 | 0.046805 | 0.11334 | 0.55044 | 0.28001 | 0.2332 | 0.048402 | -0.001715 | 0.005238 | -122.0194 | 0.13838 | 0.05809 | 0.052852 | -121.9254 | -121.8855 | 122.1714 | 122.1065 | 122.0564 | 20.8569 | -122.0113 | 0.038702 | 0.13273 | 0.17256 | 0.19722 | -122.0529
2961.4062 | 122.0627 | -0.10529 | 121.9711 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0093137 | 0.053965 | -0.0099192 | -0.0040121 | -0.0019123 | 0.019186 | 0.030485 | 0.015005 | 0.43599 | 20.8112 | 0.17472 | 122.057 | 121.9875 | 121.9374 | -0.067636 | 0.033099 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.03765 | 0.085877 | 0.54128 | 0.28001 | 0.24236 | 0.016358 | -0.033758 | -0.003917 | -122.0514 | 0.13839 | 0.044356 | 0.048273 | -121.9437 | -121.9084 | 122.1623 | 122.0928 | 122.0427 | 20.9164 | -122.0388 | 0.024968 | 0.13273 | 0.16798 | 0.18806 | -122.0803
2963.1719 | 122.0535 | -0.10529 | 121.9162 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.06621 | -0.0095273 | 0.054179 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.030912 | 0.014791 | 0.44515 | 20.802 | 0.17472 | 122.0524 | 121.9966 | 121.942 | -0.072215 | 0.023941 | 0.087354 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.1092 | 0.033071 | 0.13623 | 0.55044 | 0.28001 | 0.24694 | 0.080447 | 0.025751 | -0.003917 | -121.9965 | 0.12923 | 0.048935 | 0.052852 | -121.8888 | -121.8489 | 122.1577 | 122.1019 | 122.0472 | 20.9073 | -121.9884 | 0.024968 | 0.13273 | 0.17256 | 0.19264 | -122.0254
2964.875 | 122.0306 | -0.12817 | 121.9666 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.066423 | -0.0095273 | 0.053965 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018972 | 0.031126 | 0.014578 | 0.44515 | 20.8432 | 0.17472 | 122.0524 | 121.9966 | 121.9465 | -0.063057 | 0.014784 | 0.082776 | -0.065509 | -0.089475 | 0.027442 | 0.067272 | -0.1092 | 0.065117 | 0.085876 | 0.57333 | 0.3029 | 0.23778 | 0.030093 | -0.020024 | 0.018971 | -122.056 | 0.14296 | 0.062665 | 0.043694 | -121.9391 | -121.8993 | 122.1806 | 122.1248 | 122.0747 | 20.9714 | -122.0296 | 0.038699 | 0.15562 | 0.19545 | 0.21095 | -122.0758
2966.6406 | 122.0856 | -0.10071 | 121.9574 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.066423 | -0.0093137 | 0.053965 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019186 | 0.030912 | 0.014791 | 0.44973 | 20.9348 | 0.1793 | 122.0479 | 121.9966 | 121.9374 | -0.072215 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.027442 | 0.071851 | -0.11378 | 0.028493 | 0.090454 | 0.55044 | 0.28001 | 0.25151 | 0.039249 | -0.020025 | -0.013074 | -122.0377 | 0.12465 | 0.035199 | 0.048273 | -121.93 | -121.8855 | 122.1486 | 122.0974 | 122.0381 | 21.0355 | -122.0296 | 0.02039 | 0.12815 | 0.17256 | 0.18348 | -122.0712
2968.3438 | 122.0169 | -0.13275 | 121.9849 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066423 | -0.0093137 | 0.054179 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.014791 | 0.45431 | 21.0355 | 0.1793 | 122.057 | 121.9875 | 121.942 | -0.063057 | 0.019362 | 0.087354 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.069694 | 0.072144 | 0.58706 | 0.31205 | 0.24236 | 0.002625 | -0.042913 | 0.023548 | -122.0652 | 0.15211 | 0.067242 | 0.043694 | -121.9666 | -121.9176 | 122.1898 | 122.1202 | 122.0747 | 21.1683 | -122.0479 | 0.052433 | 0.15104 | 0.20002 | 0.2201 | -122.0941
2970.0938 | 122.0261 | -0.13733 | 121.9666 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.06621 | -0.0095273 | 0.054179 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.030698 | 0.015005 | 0.46347 | 21.0538 | 0.18846 | 122.0479 | 121.9966 | 121.9465 | -0.067636 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.069693 | 0.081298 | 0.60079 | 0.32579 | 0.25609 | 0.030093 | -0.020024 | 0.028126 | -122.0469 | 0.16127 | 0.076399 | 0.048273 | -121.9437 | -121.9084 | 122.1852 | 122.134 | 122.0839 | 21.1912 | -122.0342 | 0.057011 | 0.16019 | 0.19544 | 0.2201 | -122.0758
2971.8594 | 122.0901 | -0.07782 | 121.9482 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.06621 | -0.0095273 | 0.054179 | 0.0053413 | -0.0044395 | -0.0016987 | 0.019399 | 0.030698 | 0.014578 | 0.46804 | 21.1317 | 0.18846 | 122.057 | 121.9921 | 121.942 | -0.067636 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.12294 | 0.010184 | 0.10877 | 0.54586 | 0.26628 | 0.25609 | 0.043825 | -0.006292 | -0.045119 | -122.0286 | 0.10176 | 0.01689 | 0.062009 | -121.9254 | -121.881 | 122.1348 | 122.0699 | 122.0198 | 21.2095 | -122.0159 | -0.002498 | 0.10068 | 0.14509 | 0.15144 | -122.0712
2973.5938 | 122.1222 | -0.082397 | 121.9299 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.065782 | -0.0093137 | 0.053965 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.030912 | 0.015005 | 0.46347 | 21.237 | 0.1793 | 122.0524 | 121.9921 | 121.9374 | -0.072215 | 0.014784 | 0.078197 | -0.056351 | -0.071161 | 0.022864 | 0.062694 | -0.11378 | 0.010182 | 0.1225 | 0.54586 | 0.2617 | 0.25151 | 0.062135 | 0.00744 | -0.031385 | -122.0011 | 0.097181 | 0.026046 | 0.057431 | -121.9071 | -121.8672 | 122.1348 | 122.0745 | 122.0198 | 21.3194 | -122.0021 | 0.011236 | 0.10526 | 0.14509 | 0.16059 | -122.0437
2975.3281 | 122.0261 | -0.13275 | 121.9574 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.06621 | -0.0093137 | 0.054179 | -0.0022892 | -0.0046531 | -0.0016987 | 0.019399 | 0.031126 | 0.014791 | 0.46804 | 21.2507 | 0.18846 | 122.0616 | 121.9921 | 121.9328 | -0.067636 | 0.019362 | 0.082776 | -0.070087 | -0.084896 | 0.032021 | 0.062694 | -0.1092 | 0.065115 | 0.10419 | 0.60079 | 0.32121 | 0.25609 | 0.03467 | -0.024604 | 0.023548 | -122.0423 | 0.15211 | 0.062664 | 0.039116 | -121.9254 | -121.8947 | 122.1943 | 122.1248 | 122.0655 | 21.3835 | -122.025 | 0.047855 | 0.16477 | 0.19545 | 0.21553 | -122.0666
2977.0938 | 122.0901 | -0.10071 | 121.9025 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.065996 | -0.0093137 | 0.054179 | 0.0053413 | -0.0040121 | -0.0016987 | 0.019399 | 0.030912 | 0.014578 | 0.47262 | 21.3056 | 0.18846 | 122.0479 | 121.9921 | 121.942 | -0.063057 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.022864 | 0.062694 | -0.11836 | 0.037651 | 0.14538 | 0.57333 | 0.28917 | 0.25151 | 0.089601 | 0.039484 | -0.017653 | -121.9782 | 0.12465 | 0.039778 | 0.057431 | -121.8796 | -121.8398 | 122.1486 | 122.0928 | 122.0427 | 21.4064 | -121.9655 | 0.024969 | 0.12357 | 0.1634 | 0.17891 | -122.0208
2978.8594 | 122.0398 | -0.10986 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066637 | -0.0093137 | 0.053538 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.031339 | 0.015005 | 0.4772 | 21.4018 | 0.19761 | 122.0524 | 121.9921 | 121.942 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.037648 | 0.085876 | 0.58706 | 0.30748 | 0.26983 | 0.025514 | -0.024603 | 0.005239 | -122.0514 | 0.1338 | 0.048933 | 0.043694 | -121.9437 | -121.9039 | 122.1623 | 122.1019 | 122.0518 | 21.5117 | -122.0388 | 0.024967 | 0.13273 | 0.17256 | 0.18806 | -122.0712
2980.6094 | 122.0215 | -0.12817 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.06621 | -0.0095273 | 0.053965 | -0.01755 | -0.0040121 | -0.0016987 | 0.018758 | 0.030912 | 0.014791 | 0.48178 | 21.4888 | 0.20219 | 122.057 | 122.0012 | 121.942 | -0.067636 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.062694 | -0.11378 | 0.060538 | 0.090454 | 0.60995 | 0.33037 | 0.26983 | 0.034671 | -0.024603 | 0.014392 | -122.0469 | 0.15669 | 0.071823 | 0.057431 | -121.9437 | -121.9039 | 122.1852 | 122.1294 | 122.0701 | 21.617 | -122.0342 | 0.047856 | 0.15104 | 0.19087 | 0.20637 | -122.0803
2982.375 | 122.0032 | -0.1236 | 121.9894 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.06621 | -0.0093137 | 0.053965 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.030698 | 0.014791 | 0.48178 | 21.4979 | 0.19761 | 122.0524 | 121.9829 | 121.9374 | -0.063057 | 0.019362 | 0.073618 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.060539 | 0.062988 | 0.60537 | 0.32121 | 0.26067 | -0.006532 | -0.052069 | 0.014393 | -122.0698 | 0.14296 | 0.058087 | 0.043694 | -121.9712 | -121.9222 | 122.176 | 122.1065 | 122.061 | 21.6215 | -122.0525 | 0.043278 | 0.14188 | 0.19087 | 0.19721 | -122.0986
2984.0781 | 122.1497 | -0.07782 | 121.9116 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066423 | -0.0095273 | 0.053751 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030912 | 0.014364 | 0.49094 | 21.5849 | 0.20677 | 122.0479 | 121.9875 | 121.9328 | -0.058478 | 0.02852 | 0.082776 | -0.06093 | -0.084896 | 0.018285 | 0.058115 | -0.1092 | 0.019342 | 0.13623 | 0.56876 | 0.28459 | 0.26525 | 0.075867 | 0.021172 | -0.031383 | -121.9965 | 0.10634 | 0.01689 | 0.048273 | -121.8933 | -121.8535 | 122.1257 | 122.0653 | 122.0106 | 21.6628 | -121.9701 | -0.007076 | 0.096105 | 0.13594 | 0.1606 | -122.0208
2985.8438 | 122.1176 | -0.086975 | 121.9254 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066423 | -0.0095273 | 0.054179 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019186 | 0.030912 | 0.015219 | 0.49094 | 21.6353 | 0.20677 | 122.0524 | 121.9875 | 121.9282 | -0.072215 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.022864 | 0.062694 | -0.10462 | 0.01476 | 0.12708 | 0.57791 | 0.29375 | 0.27899 | 0.062134 | 0.00286 | -0.017649 | -122.0011 | 0.11092 | 0.026045 | 0.043694 | -121.9025 | -121.8627 | 122.1394 | 122.0745 | 122.0152 | 21.7223 | -121.9976 | 0.011236 | 0.10984 | 0.14967 | 0.16975 | -122.03
2987.6094 | 122.0581 | -0.13275 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.066637 | -0.0093137 | 0.054392 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 0.49551 | 21.7086 | 0.21593 | 122.0479 | 121.9875 | 121.942 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.11378 | 0.060536 | 0.099609 | 0.62826 | 0.34868 | 0.28814 | 0.039246 | -0.006292 | 0.018969 | -122.0286 | 0.15669 | 0.071821 | 0.052852 | -121.93 | -121.881 | 122.1806 | 122.1202 | 122.0747 | 21.8413 | -122.0205 | 0.052433 | 0.15104 | 0.20002 | 0.21095 | -122.062
2989.3594 | 121.9986 | -0.13733 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.066637 | -0.0095273 | 0.054392 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019399 | 0.030912 | 0.014578 | 0.50467 | 21.791 | 0.20677 | 122.0479 | 121.9875 | 121.9328 | -0.063057 | 0.023941 | 0.091933 | -0.056351 | -0.084896 | 0.027442 | 0.058115 | -0.11378 | 0.074272 | 0.072143 | 0.642 | 0.3441 | 0.26983 | 0.01178 | -0.042915 | 0.023547 | -122.0606 | 0.16127 | 0.080978 | 0.057431 | -121.9483 | -121.9176 | 122.1852 | 122.1248 | 122.0701 | 21.9283 | -122.0388 | 0.052433 | 0.16477 | 0.19544 | 0.22926 | -122.0895
2991.0625 | 122.0673 | -0.10071 | 121.9345 | 1.4211e-13 | -0.04388 | 0.0020727 | 0.06621 | -0.0093137 | 0.054179 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.031126 | 0.014791 | 0.50467 | 21.8642 | 0.21135 | 122.0433 | 121.9829 | 121.9328 | -0.081373 | 0.019362 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.019335 | 0.10876 | 0.60538 | 0.31206 | 0.29272 | 0.0484 | -0.001716 | -0.013074 | -122.0148 | 0.12007 | 0.044357 | 0.057431 | -121.9116 | -121.8672 | 122.144 | 122.0836 | 122.0335 | 21.9649 | -122.0159 | 0.02039 | 0.12357 | 0.16798 | 0.18348 | -122.0483
2992.8438 | 122.113 | -0.10986 | 121.9208 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.06621 | -0.0095273 | 0.054179 | -0.01755 | -0.0044395 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 0.50925 | 21.9466 | 0.21593 | 122.0524 | 121.9875 | 121.9282 | -0.067636 | 0.019362 | 0.078197 | -0.06093 | -0.075739 | 0.022864 | 0.071851 | -0.11378 | 0.042227 | 0.13165 | 0.61911 | 0.32579 | 0.28356 | 0.066712 | 0.007438 | -0.003919 | -121.9965 | 0.12923 | 0.048933 | 0.052852 | -121.8979 | -121.8489 | 122.1623 | 122.0974 | 122.0381 | 22.0565 | -121.9884 | 0.034124 | 0.13273 | 0.18171 | 0.18806 | -122.0346
2994.5469 | 122.0856 | -0.10071 | 121.9391 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.065996 | -0.0095273 | 0.053965 | -0.02518 | -0.0044395 | -0.0019123 | 0.018972 | 0.030698 | 0.014791 | 0.52298 | 21.9924 | 0.22051 | 122.0433 | 121.9875 | 121.9282 | -0.081373 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.067272 | -0.11378 | 0.019335 | 0.10419 | 0.62369 | 0.32121 | 0.30188 | 0.048401 | -0.010873 | -0.013074 | -122.024 | 0.12465 | 0.039778 | 0.052852 | -121.9208 | -121.8718 | 122.144 | 122.0882 | 122.0289 | 22.0931 | -122.0205 | 0.015812 | 0.11899 | 0.16798 | 0.17891 | -122.0529
2996.3125 | 122.0123 | -0.13733 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066423 | -0.0093137 | 0.054392 | -0.01755 | -0.0042257 | -0.0019123 | 0.018972 | 0.030698 | 0.014791 | 0.51841 | 22.0474 | 0.22051 | 122.0433 | 121.9829 | 121.9374 | -0.076794 | 0.019362 | 0.091933 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.060535 | 0.076719 | 0.65573 | 0.35783 | 0.2973 | 0.016356 | -0.029181 | 0.028126 | -122.0514 | 0.15669 | 0.076399 | 0.048273 | -121.9391 | -121.9039 | 122.1806 | 122.1202 | 122.0747 | 22.1847 | -122.0433 | 0.052433 | 0.16477 | 0.20002 | 0.22926 | -122.0758
2998.0781 | 122.0169 | -0.13733 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.066423 | -0.0095273 | 0.054179 | -0.032811 | -0.0046531 | -0.0016987 | 0.019613 | 0.030698 | 0.015005 | 0.52298 | 22.1344 | 0.22966 | 122.0341 | 121.9783 | 121.9374 | -0.076794 | 0.033099 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.071851 | -0.1092 | 0.060535 | 0.067562 | 0.66031 | 0.36699 | 0.30646 | 0.011777 | -0.029181 | 0.028126 | -122.0514 | 0.17043 | 0.076399 | 0.048273 | -121.9483 | -121.8947 | 122.1714 | 122.1157 | 122.0747 | 22.2717 | -122.0433 | 0.052433 | 0.15561 | 0.20918 | 0.21553 | -122.0758
2999.8594 | 122.0856 | -0.10529 | 121.9208 | 1.4211e-13 | -0.043453 | 0.0018589 | 0.06621 | -0.0093137 | 0.053965 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014791 | 0.52298 | 22.1893 | 0.22508 | 122.0433 | 121.9829 | 121.9282 | -0.067636 | 0.019362 | 0.082776 | -0.065509 | -0.084896 | 0.022864 | 0.062694 | -0.11836 | 0.03765 | 0.1225 | 0.62827 | 0.33037 | 0.29272 | 0.062133 | 0.007438 | -0.013075 | -122.0057 | 0.12465 | 0.039777 | 0.052852 | -121.8979 | -121.8581 | 122.1486 | 122.0882 | 122.0335 | 22.2946 | -121.9884 | 0.02039 | 0.12815 | 0.16798 | 0.18806 | -122.0391
3001.5625 | 122.1039 | -0.09613 | 121.9299 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.06621 | -0.0093137 | 0.054392 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018972 | 0.030698 | 0.015005 | 0.53672 | 22.2626 | 0.22966 | 122.0433 | 121.9783 | 121.9282 | -0.072215 | 0.019362 | 0.082776 | -0.06093 | -0.089475 | 0.018285 | 0.058115 | -0.11836 | 0.023915 | 0.11334 | 0.63285 | 0.32579 | 0.30188 | 0.048398 | -0.001718 | -0.022231 | -122.0194 | 0.11549 | 0.0352 | 0.057431 | -121.9116 | -121.8718 | 122.1394 | 122.0745 | 122.0243 | 22.3587 | -122.0021 | 0.006655 | 0.11441 | 0.15424 | 0.17891 | -122.0483
3003.3281 | 122.1085 | -0.09613 | 121.9254 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.06621 | -0.0097409 | 0.054392 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030698 | 0.014791 | 0.53672 | 22.3587 | 0.23882 | 122.0341 | 121.9783 | 121.9328 | -0.072215 | 0.023941 | 0.078197 | -0.070087 | -0.084896 | 0.022864 | 0.062694 | -0.10462 | 0.023915 | 0.10876 | 0.63285 | 0.33495 | 0.31103 | 0.052976 | 0.007439 | -0.008494 | -122.0102 | 0.12007 | 0.026043 | 0.034537 | -121.9025 | -121.8627 | 122.1302 | 122.0745 | 122.0289 | 22.4549 | -121.9976 | 0.011234 | 0.11899 | 0.15882 | 0.17433 | -122.03
3005.0312 | 122.1497 | -0.091553 | 121.9208 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066851 | -0.0095273 | 0.054179 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.030485 | 0.015005 | 0.53214 | 22.3954 | 0.23424 | 122.0433 | 121.9738 | 121.9236 | -0.072215 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.022864 | 0.062694 | -0.11836 | 0.019338 | 0.1225 | 0.62369 | 0.32579 | 0.30645 | 0.052975 | 0.00286 | -0.026808 | -121.9965 | 0.12007 | 0.030623 | 0.057431 | -121.8979 | -121.8581 | 122.1348 | 122.0653 | 122.0152 | 22.4869 | -121.993 | 0.015814 | 0.11442 | 0.15425 | 0.16975 | -122.0391
3006.7969 | 122.0764 | -0.091553 | 121.9254 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.06621 | -0.0093137 | 0.054179 | -0.0022892 | -0.0042257 | -0.0012713 | 0.018758 | 0.030912 | 0.015005 | 0.53672 | 22.464 | 0.23424 | 122.025 | 121.9783 | 121.9236 | -0.076794 | 0.023941 | 0.087354 | -0.06093 | -0.089475 | 0.018285 | 0.062694 | -0.11378 | 0.014759 | 0.099605 | 0.62827 | 0.32579 | 0.31103 | 0.052976 | -0.001718 | -0.022229 | -122.0148 | 0.11549 | 0.030623 | 0.052852 | -121.9071 | -121.8627 | 122.1165 | 122.0699 | 122.0152 | 22.5556 | -122.0021 | 0.002078 | 0.10984 | 0.15425 | 0.17891 | -122.0391
3008.5625 | 122.0947 | -0.10071 | 121.8842 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066637 | -0.0093137 | 0.054179 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018972 | 0.030698 | 0.014791 | 0.55503 | 22.5098 | 0.23882 | 122.0295 | 121.9783 | 121.9236 | -0.072215 | 0.023941 | 0.087354 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.028493 | 0.14538 | 0.65574 | 0.33953 | 0.31103 | 0.094175 | 0.039481 | -0.013074 | -121.9691 | 0.12465 | 0.039778 | 0.052852 | -121.8613 | -121.8215 | 122.1302 | 122.079 | 122.0243 | 22.6105 | -121.9564 | 0.015812 | 0.12357 | 0.1634 | 0.18806 | -121.9979
3010.3125 | 122.0444 | -0.11444 | 121.9345 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.065782 | -0.0093137 | 0.054179 | -0.0022892 | -0.0040121 | -0.0019123 | 0.018972 | 0.030912 | 0.014578 | 0.55961 | 22.5922 | 0.24797 | 122.0341 | 121.9738 | 121.9282 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.089475 | 0.022864 | 0.058115 | -0.1092 | 0.042226 | 0.099606 | 0.67405 | 0.36241 | 0.32019 | 0.039242 | -0.006295 | 0.005238 | -122.024 | 0.13838 | 0.053511 | 0.048273 | -121.9116 | -121.8764 | 122.1486 | 122.0882 | 122.0427 | 22.7067 | -122.0067 | 0.024966 | 0.13731 | 0.17256 | 0.19264 | -122.0437
3012.0156 | 122.0901 | -0.10529 | 121.8979 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.066423 | -0.0095273 | 0.054392 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018972 | 0.031339 | 0.014578 | 0.54588 | 22.6792 | 0.24797 | 122.0295 | 121.9738 | 121.9191 | -0.076794 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.062694 | -0.1092 | 0.028492 | 0.13165 | 0.65116 | 0.35326 | 0.32477 | 0.075863 | 0.021169 | -0.003917 | -121.9828 | 0.12465 | 0.044356 | 0.048273 | -121.8796 | -121.8352 | 122.1348 | 122.079 | 122.0243 | 22.7845 | -121.9747 | 0.02039 | 0.12357 | 0.16798 | 0.18348 | -122.0071
3013.7812 | 122.1268 | -0.10986 | 121.907 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.06621 | -0.0093137 | 0.054179 | -0.0022892 | -0.0046531 | -0.0016987 | 0.019399 | 0.030912 | 0.014791 | 0.56419 | 22.7479 | 0.2434 | 122.0204 | 121.9554 | 121.9099 | -0.085952 | 0.019362 | 0.082776 | -0.056351 | -0.084896 | 0.022864 | 0.067272 | -0.1092 | 0.023911 | 0.11334 | 0.67405 | 0.35326 | 0.32935 | 0.048392 | 0.002857 | 0.00066 | -121.9919 | 0.12923 | 0.053512 | 0.052852 | -121.8842 | -121.8398 | 122.1302 | 122.0653 | 122.0198 | 22.8578 | -121.993 | 0.024967 | 0.13273 | 0.17713 | 0.19264 | -122.0162
3015.4688 | 122.0261 | -0.15106 | 121.8933 | 1.4211e-13 | -0.043453 | 0.0016453 | 0.06621 | -0.0090999 | 0.054179 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.030271 | 0.014578 | 0.55961 | 22.8441 | 0.2434 | 122.0112 | 121.9554 | 121.9053 | -0.09511 | 0.023941 | 0.087354 | -0.06093 | -0.080318 | 0.013707 | 0.062694 | -0.1092 | 0.055952 | 0.11791 | 0.71067 | 0.39446 | 0.33851 | 0.062124 | 0.01201 | 0.041859 | -121.9736 | 0.175 | 0.090132 | 0.048273 | -121.8796 | -121.8306 | 122.1623 | 122.1065 | 122.0564 | 22.9951 | -121.9884 | 0.070744 | 0.16477 | 0.21376 | 0.23842 | -122.0025
3017.2188 | 121.9986 | -0.091553 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0014317 | 0.06621 | -0.0095273 | 0.054179 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018972 | 0.030698 | 0.015005 | 0.6054 | 22.9036 | 0.2846 | 122.0433 | 121.9875 | 121.9374 | -0.072215 | 0.019362 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.10462 | 0.019338 | 0.090452 | 0.69695 | 0.37615 | 0.35682 | 0.034668 | -0.015448 | -0.013071 | -122.0331 | 0.11091 | 0.035202 | 0.048273 | -121.9254 | -121.8855 | 122.1348 | 122.079 | 122.0289 | 22.9951 | -122.025 | 0.011235 | 0.11899 | 0.15882 | 0.17433 | -122.0574
3018.9844 | 121.994 | -0.11444 | 121.9437 | 1.4211e-13 | -0.043666 | 0.0014317 | 0.06621 | -0.0093137 | 0.054179 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.030912 | 0.014578 | 0.60997 | 22.9585 | 0.2846 | 122.0433 | 121.9921 | 121.9465 | -0.072215 | 0.02852 | 0.087354 | -0.056351 | -0.084896 | 0.027442 | 0.062694 | -0.1092 | 0.042226 | 0.099607 | 0.72441 | 0.39904 | 0.35682 | 0.048402 | 0.002864 | 0.005238 | -122.0286 | 0.14296 | 0.05809 | 0.052852 | -121.9162 | -121.881 | 122.1577 | 122.1065 | 122.061 | 23.073 | -122.0159 | 0.029545 | 0.14188 | 0.17713 | 0.2018 | -122.0529
3020.6875 | 122.0535 | -0.09613 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.065782 | -0.0090999 | 0.054606 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019399 | 0.031339 | 0.015005 | 0.61455 | 22.9997 | 0.28918 | 122.0479 | 121.9875 | 121.9374 | -0.076794 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.019336 | 0.095031 | 0.71068 | 0.38531 | 0.36597 | 0.034668 | -0.015448 | -0.013073 | -122.0331 | 0.12465 | 0.039779 | 0.052852 | -121.93 | -121.8901 | 122.144 | 122.0836 | 122.0335 | 23.0959 | -122.0296 | 0.015812 | 0.11899 | 0.15882 | 0.17891 | -122.062
3022.4531 | 122.0306 | -0.09613 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.065996 | -0.0097409 | 0.054392 | -0.0099192 | -0.0040121 | -0.0019123 | 0.019399 | 0.030912 | 0.014578 | 0.60997 | 23.0455 | 0.29376 | 122.0524 | 121.9921 | 121.9465 | -0.072215 | 0.019362 | 0.078197 | -0.056351 | -0.089475 | 0.018285 | 0.067272 | -0.10462 | 0.023915 | 0.10419 | 0.7061 | 0.38989 | 0.36597 | 0.043825 | -0.001713 | -0.008494 | -122.0377 | 0.11549 | 0.039779 | 0.048273 | -121.93 | -121.881 | 122.1486 | 122.0882 | 122.0427 | 23.1416 | -122.0205 | 0.006655 | 0.11441 | 0.1634 | 0.17433 | -122.0529
3024.1562 | 121.9849 | -0.11902 | 121.9391 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066423 | -0.0095273 | 0.054392 | 0.0053413 | -0.0040121 | -0.0012713 | 0.018758 | 0.031126 | 0.015005 | 0.61455 | 23.1188 | 0.29376 | 122.0616 | 121.9921 | 121.9511 | -0.076794 | 0.023941 | 0.087354 | -0.051772 | -0.084896 | 0.018285 | 0.067272 | -0.1092 | 0.042225 | 0.1225 | 0.73357 | 0.41278 | 0.37055 | 0.05298 | 0.01202 | 0.009816 | -122.024 | 0.14296 | 0.067247 | 0.057431 | -121.9208 | -121.8718 | 122.1806 | 122.1111 | 122.0701 | 23.2378 | -122.0159 | 0.034123 | 0.1373 | 0.18629 | 0.20637 | -122.0483
3025.9062 | 122.0764 | -0.068665 | 121.9299 | 1.4211e-13 | -0.043239 | 0.0018589 | 0.066423 | -0.0095273 | 0.054179 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 0.62829 | 23.1874 | 0.29834 | 122.0479 | 121.9966 | 121.9511 | -0.072215 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.1092 | -0.00355 | 0.11792 | 0.69695 | 0.367 | 0.37055 | 0.066714 | 0.021175 | -0.040538 | -122.0102 | 0.097185 | 0.007735 | 0.048273 | -121.9116 | -121.8672 | 122.1165 | 122.0653 | 122.0198 | 23.2561 | -122.0021 | -0.011653 | 0.08695 | 0.13136 | 0.14686 | -122.0391
3027.6719 | 121.994 | -0.11444 | 121.9803 | 1.4211e-13 | -0.04388 | 0.0016453 | 0.066423 | -0.0088863 | 0.054392 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019399 | 0.031126 | 0.014791 | 0.61913 | 23.2332 | 0.29834 | 122.0616 | 121.9966 | 121.9511 | -0.072215 | 0.023941 | 0.087354 | -0.051772 | -0.084896 | 0.022864 | 0.062694 | -0.11836 | 0.042226 | 0.0813 | 0.73357 | 0.41278 | 0.37055 | 0.01636 | -0.029179 | -0.00392 | -122.0652 | 0.13838 | 0.062669 | 0.066589 | -121.9574 | -121.9176 | 122.176 | 122.1111 | 122.0655 | 23.3477 | -122.0525 | 0.029545 | 0.13731 | 0.17713 | 0.2018 | -122.0986
3029.375 | 122.113 | -0.064087 | 121.9299 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066423 | -0.0093137 | 0.054179 | -0.0022892 | -0.0040121 | -0.0019123 | 0.019186 | 0.030912 | 0.014791 | 0.63744 | 23.2699 | 0.30291 | 122.057 | 121.9921 | 121.9511 | -0.076794 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.018285 | 0.067272 | -0.11836 | -0.012707 | 0.12708 | 0.70153 | 0.367 | 0.37971 | 0.062135 | 0.021175 | -0.054274 | -122.0148 | 0.088028 | 0.003157 | 0.057431 | -121.9116 | -121.8627 | 122.1211 | 122.0562 | 122.0152 | 23.334 | -122.0067 | -0.020809 | 0.082372 | 0.13136 | 0.14686 | -122.0483
3031.1406 | 122.1405 | -0.082397 | 121.9437 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.06621 | -0.0090999 | 0.054392 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.030912 | 0.014364 | 0.63744 | 23.3523 | 0.30749 | 122.057 | 121.9966 | 121.9511 | -0.072215 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.071851 | -0.1092 | 0.010182 | 0.11334 | 0.71984 | 0.38989 | 0.37971 | 0.052981 | 0.007442 | -0.026806 | -122.024 | 0.11092 | 0.021467 | 0.048273 | -121.9254 | -121.8718 | 122.1394 | 122.079 | 122.0335 | 23.4347 | -122.0159 | 0.002079 | 0.10068 | 0.15425 | 0.16059 | -122.0529
3032.9062 | 122.0993 | -0.073242 | 121.8979 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066423 | -0.0090999 | 0.054606 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019613 | 0.031126 | 0.014791 | 0.63744 | 23.4164 | 0.31207 | 122.0616 | 122.0012 | 121.9557 | -0.072215 | 0.023941 | 0.087354 | -0.06093 | -0.084896 | 0.018285 | 0.067272 | -0.10462 | 0.001027 | 0.1637 | 0.71069 | 0.38531 | 0.38428 | 0.10334 | 0.057798 | -0.031382 | -121.9828 | 0.097183 | 0.012312 | 0.043694 | -121.8796 | -121.8306 | 122.1348 | 122.0745 | 122.0289 | 23.4896 | -121.9701 | -0.011654 | 0.091527 | 0.14051 | 0.1606 | -122.0025
3034.6719 | 121.9849 | -0.1236 | 121.962 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.065996 | -0.0093137 | 0.054179 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.030698 | 0.015005 | 0.65118 | 23.4667 | 0.32123 | 122.0616 | 121.9966 | 121.9511 | -0.072215 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.022864 | 0.071851 | -0.10462 | 0.051381 | 0.099611 | 0.77477 | 0.44482 | 0.39344 | 0.034671 | -0.010868 | 0.018972 | -122.0331 | 0.14754 | 0.067245 | 0.048273 | -121.9391 | -121.8901 | 122.1852 | 122.1202 | 122.0747 | 23.5903 | -122.0342 | 0.052435 | 0.14646 | 0.19545 | 0.20637 | -122.0666
3036.375 | 121.9986 | -0.12817 | 121.9849 | 1.4211e-13 | -0.04388 | 0.0016453 | 0.06621 | -0.0097409 | 0.054392 | -0.0022892 | -0.0044395 | -0.0012713 | 0.018972 | 0.030912 | 0.014791 | 0.66491 | 23.5308 | 0.32581 | 122.0662 | 122.0012 | 121.9511 | -0.072215 | 0.023941 | 0.087354 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.055959 | 0.081301 | 0.79309 | 0.45398 | 0.39802 | 0.016361 | -0.033756 | 0.014392 | -122.0652 | 0.15212 | 0.071823 | 0.057431 | -121.962 | -121.9176 | 122.1943 | 122.1294 | 122.0793 | 23.659 | -122.0571 | 0.047856 | 0.15104 | 0.19545 | 0.21553 | -122.0986
3038.1406 | 122.1039 | -0.068665 | 121.9574 | 1.4211e-13 | -0.04388 | 0.0018589 | 0.066851 | -0.0090999 | 0.054392 | -0.01755 | -0.0044395 | -0.0016987 | 0.019613 | 0.030485 | 0.014791 | 0.66034 | 23.5446 | 0.32581 | 122.0616 | 122.0012 | 121.9603 | -0.072215 | 0.033099 | 0.087354 | -0.056351 | -0.084896 | 0.022864 | 0.071851 | -0.11378 | -0.00355 | 0.10419 | 0.729 | 0.39447 | 0.39802 | 0.043827 | 0.002868 | -0.045117 | -122.0423 | 0.10176 | 0.012314 | 0.057431 | -121.9345 | -121.8855 | 122.1303 | 122.0699 | 122.0289 | 23.6132 | -122.0296 | -0.016231 | 0.091529 | 0.14052 | 0.15602 | -122.0712
3039.8438 | 122.0444 | -0.086975 | 121.994 | 1.4211e-13 | -0.04388 | 0.0014317 | 0.066423 | -0.0093137 | 0.054179 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030698 | 0.014578 | 0.67407 | 23.5629 | 0.32581 | 122.0753 | 121.9966 | 121.9557 | -0.081373 | 0.023941 | 0.087354 | -0.056351 | -0.084896 | 0.022864 | 0.062694 | -0.1092 | 0.005602 | 0.081302 | 0.76105 | 0.41278 | 0.40718 | 0.002627 | -0.038333 | -0.022228 | -122.0789 | 0.11092 | 0.030624 | 0.052852 | -121.9712 | -121.9313 | 122.1623 | 122.0836 | 122.0427 | 23.6499 | -122.0754 | 0.002079 | 0.10984 | 0.14967 | 0.17433 | -122.1032
3041.625 | 122.0261 | -0.10071 | 122.0078 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066423 | -0.0095273 | 0.054392 | -0.0022892 | -0.0046531 | -0.0021259 | 0.019399 | 0.030912 | 0.014791 | 0.66949 | 23.5949 | 0.33954 | 122.0707 | 122.0058 | 121.9557 | -0.072215 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.10462 | 0.028493 | 0.062992 | 0.7702 | 0.44025 | 0.41175 | -0.001948 | -0.052065 | -0.003916 | -122.0881 | 0.12465 | 0.039778 | 0.043694 | -121.9803 | -121.9451 | 122.1715 | 122.1065 | 122.0564 | 23.6957 | -122.08 | 0.02039 | 0.12815 | 0.1634 | 0.18348 | -122.1124
3043.3906 | 122.1497 | -0.068665 | 121.9299 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066423 | -0.0097409 | 0.054179 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.014791 | 0.67407 | 23.6545 | 0.33954 | 122.0616 | 122.0058 | 121.9511 | -0.067636 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.10462 | 0.001029 | 0.13165 | 0.74274 | 0.40821 | 0.40718 | 0.075871 | 0.021175 | -0.035959 | -122.0102 | 0.097185 | 0.007735 | 0.043694 | -121.9071 | -121.8627 | 122.1303 | 122.0745 | 122.0198 | 23.7231 | -121.9976 | -0.011653 | 0.091529 | 0.13594 | 0.15144 | -122.0346
3045.0938 | 122.113 | -0.054932 | 121.907 | 1.4211e-13 | -0.04388 | 0.0020727 | 0.066423 | -0.0095273 | 0.054179 | -0.0099192 | -0.0042257 | -0.0019123 | 0.019186 | 0.031339 | 0.015005 | 0.68781 | 23.6774 | 0.34412 | 122.0616 | 122.0012 | 121.9557 | -0.072215 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.022864 | 0.071851 | -0.1092 | -0.017283 | 0.15454 | 0.74274 | 0.39905 | 0.41633 | 0.094181 | 0.048643 | -0.054271 | -121.9874 | 0.078873 | -0.010577 | 0.043694 | -121.8842 | -121.8352 | 122.1165 | 122.0562 | 122.0106 | 23.7323 | -121.9793 | -0.025386 | 0.077796 | 0.12678 | 0.13313 | -122.0162
3046.8594 | 121.9803 | -0.10529 | 121.9757 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066637 | -0.0093137 | 0.054606 | -0.01755 | -0.0042257 | -0.0016987 | 0.018972 | 0.030698 | 0.014791 | 0.69238 | 23.7231 | 0.35328 | 122.0707 | 122.0012 | 121.9511 | -0.072215 | 0.023941 | 0.082776 | -0.06093 | -0.089475 | 0.009128 | 0.07643 | -0.11836 | 0.033071 | 0.095035 | 0.79767 | 0.45856 | 0.42549 | 0.025516 | -0.024601 | -0.013075 | -122.0652 | 0.12923 | 0.044356 | 0.057431 | -121.9666 | -121.8993 | 122.176 | 122.1065 | 122.0564 | 23.8284 | -122.0479 | 0.015811 | 0.11441 | 0.18172 | 0.18806 | -122.0941
3048.5781 | 122.0581 | -0.086975 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.066423 | -0.0093137 | 0.054606 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030271 | 0.014791 | 0.69696 | 23.7506 | 0.3487 | 122.0616 | 121.9966 | 121.9557 | -0.072215 | 0.02852 | 0.082776 | -0.065509 | -0.084896 | 0.013707 | 0.062694 | -0.10462 | 0.01476 | 0.085878 | 0.78394 | 0.43567 | 0.42091 | 0.020938 | -0.020022 | -0.017649 | -122.0606 | 0.1155 | 0.021466 | 0.039115 | -121.962 | -121.913 | 122.1486 | 122.0836 | 122.0427 | 23.8376 | -122.0479 | 0.002079 | 0.10068 | 0.14967 | 0.16975 | -122.0803
3050.3438 | 122.0901 | -0.068665 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0018589 | 0.066637 | -0.0093137 | 0.054392 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019399 | 0.031126 | 0.014578 | 0.70612 | 23.7781 | 0.3487 | 122.0662 | 122.0012 | 121.9557 | -0.076794 | 0.02852 | 0.078197 | -0.051772 | -0.084896 | 0.013707 | 0.062694 | -0.11378 | -0.008129 | 0.11334 | 0.77478 | 0.41736 | 0.42549 | 0.048404 | 0.002866 | -0.045117 | -122.0377 | 0.097185 | 0.016893 | 0.06201 | -121.9391 | -121.8901 | 122.1348 | 122.0699 | 122.0244 | 23.8468 | -122.0296 | -0.016231 | 0.082372 | 0.13136 | 0.14686 | -122.0666
3052.0938 | 122.1176 | -0.07782 | 121.9711 | 1.4211e-13 | -0.044094 | 0.0020727 | 0.066423 | -0.0095273 | 0.054392 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019399 | 0.030698 | 0.014791 | 0.71528 | 23.8926 | 0.36243 | 122.0707 | 122.0012 | 121.9603 | -0.076794 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.001026 | 0.099613 | 0.7931 | 0.44025 | 0.43922 | 0.030094 | -0.010865 | -0.031383 | -122.0514 | 0.10176 | 0.012311 | 0.043694 | -121.9528 | -121.9039 | 122.1486 | 122.079 | 122.0381 | 23.9704 | -122.0479 | -0.002498 | 0.096105 | 0.14509 | 0.15602 | -122.0803
3053.8125 | 121.9986 | -0.10529 | 121.9666 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.06621 | -0.0097409 | 0.05482 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019186 | 0.030912 | 0.014791 | 0.71528 | 23.9063 | 0.36243 | 122.0707 | 122.0104 | 121.9603 | -0.076794 | 0.023941 | 0.078197 | -0.056351 | -0.071161 | 0.018285 | 0.062694 | -0.11378 | 0.028492 | 0.10419 | 0.82056 | 0.46772 | 0.43922 | 0.043829 | -0.006288 | -0.008496 | -122.0377 | 0.12923 | 0.048935 | 0.057431 | -121.9483 | -121.9039 | 122.176 | 122.1157 | 122.0656 | 24.0116 | -122.0433 | 0.034125 | 0.12357 | 0.16798 | 0.18348 | -122.0803
3055.5781 | 122.081 | -0.07782 | 121.9482 | 1.4211e-13 | -0.043666 | 0.0016453 | 0.066851 | -0.0090999 | 0.054392 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.030912 | 0.014364 | 0.71985 | 23.9429 | 0.36701 | 122.0662 | 122.0058 | 121.9557 | -0.072215 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.005605 | 0.11792 | 0.79767 | 0.44483 | 0.43922 | 0.057561 | 0.007444 | -0.035962 | -122.0331 | 0.10176 | 0.01689 | 0.052852 | -121.9254 | -121.8855 | 122.144 | 122.0836 | 122.0335 | 24.0207 | -122.0205 | -0.007076 | 0.10068 | 0.14051 | 0.1606 | -122.062
3057.3438 | 122.0306 | -0.11444 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.06621 | -0.0093137 | 0.054392 | -0.01755 | -0.0042257 | -0.0016987 | 0.018972 | 0.030698 | 0.014791 | 0.73359 | 23.9521 | 0.36701 | 122.0616 | 122.0012 | 121.9557 | -0.081373 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.033068 | 0.10877 | 0.84803 | 0.48145 | 0.44838 | 0.048404 | 0.002866 | 0.000659 | -122.0331 | 0.13838 | 0.053511 | 0.052852 | -121.9254 | -121.8855 | 122.176 | 122.1157 | 122.0701 | 24.0665 | -122.0342 | 0.034123 | 0.14188 | 0.18171 | 0.19264 | -122.0666
3059.1406 | 122.1542 | -0.068665 | 121.9345 | 1.4211e-13 | -0.043025 | 0.0020727 | 0.065996 | -0.0093137 | 0.054179 | -0.01755 | -0.0042257 | -0.0014849 | 0.019186 | 0.031126 | 0.014791 | 0.73817 | 24.0024 | 0.38532 | 122.0662 | 122.0058 | 121.9557 | -0.072215 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.11836 | -0.00355 | 0.13165 | 0.80683 | 0.45399 | 0.45754 | 0.071294 | 0.021177 | -0.049696 | -122.0148 | 0.092606 | 0.007735 | 0.057431 | -121.9162 | -121.8718 | 122.1348 | 122.0745 | 122.0244 | 24.0711 | -122.0067 | -0.011653 | 0.08695 | 0.13136 | 0.14686 | -122.0529
3060.8438 | 122.0901 | -0.073242 | 121.9391 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066423 | -0.0095273 | 0.054606 | 0.0053413 | -0.0044395 | -0.0019123 | 0.019186 | 0.030912 | 0.014791 | 0.7519 | 24.0711 | 0.37617 | 122.0707 | 122.0012 | 121.9557 | -0.076794 | 0.023941 | 0.078197 | -0.051772 | -0.075739 | 0.022864 | 0.067272 | -0.1092 | -0.003552 | 0.13166 | 0.82515 | 0.44941 | 0.45296 | 0.062137 | 0.016599 | -0.035961 | -122.0148 | 0.097183 | 0.02147 | 0.057431 | -121.9162 | -121.8718 | 122.144 | 122.0745 | 122.0289 | 24.1444 | -122.0159 | -0.002497 | 0.096106 | 0.14051 | 0.15144 | -122.0483
3062.5938 | 122.0901 | -0.09613 | 121.9391 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.066423 | -0.0090999 | 0.05482 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019186 | 0.031126 | 0.015005 | 0.7519 | 24.1764 | 0.38532 | 122.0662 | 122.0058 | 121.9511 | -0.076794 | 0.019362 | 0.073618 | -0.065509 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.019336 | 0.12708 | 0.84803 | 0.48145 | 0.46212 | 0.066716 | 0.01202 | -0.022231 | -122.0194 | 0.11549 | 0.030621 | 0.052852 | -121.9071 | -121.8718 | 122.1623 | 122.1019 | 122.0472 | 24.2726 | -122.0159 | 0.015812 | 0.12815 | 0.1634 | 0.16975 | -122.0574
3064.2969 | 122.1405 | -0.068665 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.06621 | -0.0095273 | 0.054606 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031126 | 0.014578 | 0.76106 | 24.149 | 0.39906 | 122.0662 | 122.0058 | 121.9557 | -0.081373 | 0.014784 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | -0.012708 | 0.11792 | 0.82972 | 0.46772 | 0.48043 | 0.057561 | 0.007444 | -0.045117 | -122.0286 | 0.083449 | 0.007735 | 0.052852 | -121.9254 | -121.881 | 122.1348 | 122.0745 | 122.0244 | 24.2176 | -122.0296 | -0.011653 | 0.091529 | 0.13594 | 0.15144 | -122.062
3066.0469 | 122.081 | -0.10071 | 121.9849 | 1.4211e-13 | -0.04388 | 0.0020727 | 0.066423 | -0.0090999 | 0.054606 | -0.02518 | -0.0042257 | -0.0016987 | 0.019186 | 0.030912 | 0.014578 | 0.77022 | 24.1673 | 0.40821 | 122.0707 | 122.0104 | 121.9648 | -0.063057 | 0.02852 | 0.082776 | -0.065509 | -0.084896 | 0.022864 | 0.071851 | -0.10462 | 0.037651 | 0.08588 | 0.87093 | 0.50892 | 0.47127 | 0.025519 | -0.02002 | -0.003916 | -122.0698 | 0.12923 | 0.035199 | 0.039115 | -121.962 | -121.913 | 122.1715 | 122.1111 | 122.0656 | 24.268 | -122.0479 | 0.015812 | 0.12357 | 0.17256 | 0.18348 | -122.0895
3067.8125 | 122.1085 | -0.073242 | 121.9162 | 1.4211e-13 | -0.04388 | 0.0018589 | 0.066637 | -0.0095273 | 0.054392 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019613 | 0.030698 | 0.014578 | 0.78395 | 24.2588 | 0.40364 | 122.0707 | 122.0012 | 121.9694 | -0.076794 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.062694 | -0.11836 | -0.003552 | 0.15454 | 0.85719 | 0.47688 | 0.48043 | 0.085025 | 0.053223 | -0.045119 | -121.9965 | 0.10176 | 0.016891 | 0.06201 | -121.8933 | -121.8535 | 122.144 | 122.0745 | 122.0427 | 24.3321 | -121.993 | -0.007076 | 0.096106 | 0.13594 | 0.15144 | -122.0346
3069.5156 | 121.9986 | -0.1236 | 121.9849 | 1.4211e-13 | -0.04388 | 0.0020727 | 0.066637 | -0.0095273 | 0.054392 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.030698 | 0.014364 | 0.78853 | 24.2359 | 0.40821 | 122.0662 | 122.0058 | 121.9694 | -0.076794 | 0.023941 | 0.087354 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.10462 | 0.046802 | 0.081301 | 0.91213 | 0.53181 | 0.48501 | 0.02094 | -0.015441 | 0.018972 | -122.0652 | 0.14754 | 0.062666 | 0.043694 | -121.9574 | -121.9176 | 122.1898 | 122.1294 | 122.093 | 24.3595 | -122.0617 | 0.043278 | 0.15104 | 0.19087 | 0.21095 | -122.0895
3071.2656 | 122.0261 | -0.10071 | 121.9482 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066637 | -0.0093137 | 0.05482 | -0.01755 | -0.0040121 | -0.0019123 | 0.019399 | 0.030912 | 0.014578 | 0.79311 | 24.2817 | 0.41737 | 122.0662 | 122.0058 | 121.9603 | -0.076794 | 0.033099 | 0.078197 | -0.06093 | -0.080318 | 0.032021 | 0.062694 | -0.11378 | 0.023914 | 0.11792 | 0.89382 | 0.51808 | 0.49416 | 0.057561 | 0.012023 | -0.013074 | -122.0286 | 0.13381 | 0.039778 | 0.052852 | -121.9162 | -121.8855 | 122.1669 | 122.1065 | 122.061 | 24.3824 | -122.025 | 0.02039 | 0.13273 | 0.1634 | 0.17891 | -122.062
3072.9688 | 122.1588 | -0.068665 | 121.9757 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066423 | -0.0095273 | 0.05482 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019186 | 0.030912 | 0.014791 | 0.80684 | 24.3275 | 0.41737 | 122.0753 | 122.015 | 121.9694 | -0.067636 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.001029 | 0.099613 | 0.87551 | 0.48604 | 0.48501 | 0.039253 | -0.006286 | -0.045117 | -122.0606 | 0.092606 | 0.007735 | 0.052852 | -121.9528 | -121.913 | 122.144 | 122.0836 | 122.0381 | 24.3962 | -122.0433 | -0.016231 | 0.091529 | 0.13136 | 0.14686 | -122.0895
3074.75 | 122.0261 | -0.10986 | 121.9803 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.066637 | -0.0090999 | 0.05482 | -0.02518 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 0.80684 | 24.3367 | 0.42653 | 122.0707 | 122.015 | 121.9603 | -0.076794 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.022864 | 0.067272 | -0.11836 | 0.033069 | 0.090457 | 0.91671 | 0.53639 | 0.50332 | 0.034675 | -0.020021 | -0.008498 | -122.056 | 0.1338 | 0.048933 | 0.057431 | -121.9574 | -121.913 | 122.1806 | 122.1248 | 122.0701 | 24.4465 | -122.0571 | 0.034124 | 0.13273 | 0.17713 | 0.18348 | -122.0986
3076.5156 | 122.1451 | -0.054932 | 121.9437 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066423 | -0.0095273 | 0.054606 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019186 | 0.030912 | 0.015005 | 0.82058 | 24.3275 | 0.43111 | 122.0662 | 122.0104 | 121.9557 | -0.076794 | 0.02852 | 0.082776 | -0.06093 | -0.089475 | 0.027442 | 0.071851 | -0.1092 | -0.021862 | 0.1225 | 0.87551 | 0.48604 | 0.5079 | 0.066717 | 0.012021 | -0.054271 | -122.0331 | 0.083452 | -0.005998 | 0.048273 | -121.9162 | -121.8718 | 122.1211 | 122.0653 | 122.0106 | 24.3825 | -122.0205 | -0.034543 | 0.082374 | 0.12678 | 0.13771 | -122.0529
3078.2656 | 122.0673 | -0.10071 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066423 | -0.0090999 | 0.054392 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018972 | 0.030485 | 0.014791 | 0.82516 | 24.3962 | 0.44026 | 122.0662 | 122.0058 | 121.9694 | -0.072215 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.028493 | 0.099611 | 0.92587 | 0.54097 | 0.51248 | 0.03925 | 0.002869 | -0.003916 | -122.0514 | 0.12465 | 0.035199 | 0.039115 | -121.9391 | -121.9039 | 122.1669 | 122.1065 | 122.0701 | 24.4969 | -122.0388 | 0.015812 | 0.12815 | 0.1634 | 0.18348 | -122.0712
3079.9688 | 122.049 | -0.10986 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.066423 | -0.0093137 | 0.05482 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.014791 | 0.82974 | 24.4603 | 0.44942 | 122.0707 | 122.015 | 121.974 | -0.072215 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.018285 | 0.058115 | -0.11378 | 0.037648 | 0.095035 | 0.9396 | 0.55928 | 0.52163 | 0.039253 | -0.001708 | -0.003919 | -122.0606 | 0.1338 | 0.044354 | 0.048273 | -121.9574 | -121.9176 | 122.1806 | 122.1248 | 122.0839 | 24.5702 | -122.0479 | 0.024967 | 0.12815 | 0.16798 | 0.19264 | -122.0895
3081.6719 | 122.0444 | -0.10529 | 121.9803 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.06621 | -0.0093137 | 0.054392 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018758 | 0.030698 | 0.014578 | 0.83431 | 24.474 | 0.454 | 122.0707 | 122.015 | 121.9648 | -0.067636 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.018285 | 0.067272 | -0.10462 | 0.03765 | 0.090457 | 0.9396 | 0.55928 | 0.52163 | 0.034675 | -0.015443 | 0.000662 | -122.0606 | 0.13381 | 0.048935 | 0.048273 | -121.962 | -121.913 | 122.176 | 122.1202 | 122.0701 | 24.5793 | -122.0479 | 0.024968 | 0.12357 | 0.17256 | 0.18806 | -122.0849
3083.4219 | 122.0032 | -0.11444 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0020727 | 0.066637 | -0.0095273 | 0.054392 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.031339 | 0.014791 | 0.83889 | 24.5656 | 0.44942 | 122.0707 | 122.0104 | 121.9694 | -0.063057 | 0.023941 | 0.087354 | -0.065509 | -0.089475 | 0.022864 | 0.071851 | -0.11378 | 0.051384 | 0.095035 | 0.95333 | 0.56386 | 0.51248 | 0.034674 | -0.006286 | 0.000659 | -122.0652 | 0.13838 | 0.048932 | 0.048273 | -121.9528 | -121.9039 | 122.1852 | 122.1248 | 122.0839 | 24.68 | -122.0388 | 0.024966 | 0.13731 | 0.18629 | 0.2018 | -122.0895
3085.1875 | 122.0032 | -0.10529 | 121.9757 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.066637 | -0.0090999 | 0.055033 | -0.0022892 | -0.0046531 | -0.0016987 | 0.019186 | 0.030912 | 0.014364 | 0.85263 | 24.5381 | 0.45858 | 122.0753 | 122.0058 | 121.9694 | -0.067636 | 0.02852 | 0.082776 | -0.065509 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | 0.03765 | 0.099613 | 0.95791 | 0.56386 | 0.52621 | 0.030095 | -0.006286 | -0.003917 | -122.056 | 0.13381 | 0.039777 | 0.043694 | -121.9528 | -121.9084 | 122.1806 | 122.1111 | 122.0747 | 24.6434 | -122.0433 | 0.024968 | 0.12815 | 0.17256 | 0.18806 | -122.0849
3086.9531 | 122.1313 | -0.068665 | 121.9574 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066637 | -0.0093137 | 0.054606 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.030912 | 0.014578 | 0.86178 | 24.5793 | 0.47231 | 122.0799 | 122.0104 | 121.9694 | -0.072215 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | -0.00355 | 0.1225 | 0.93045 | 0.54097 | 0.54453 | 0.052985 | 0.012025 | -0.040538 | -122.0377 | 0.092606 | 0.003156 | 0.043694 | -121.93 | -121.8947 | 122.1486 | 122.079 | 122.0381 | 24.648 | -122.0296 | -0.011653 | 0.096107 | 0.13136 | 0.14686 | -122.0666
3088.6562 | 122.0169 | -0.10529 | 121.9711 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066423 | -0.0095273 | 0.05482 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018972 | 0.031126 | 0.014791 | 0.87552 | 24.6022 | 0.46315 | 122.0845 | 122.0104 | 121.9603 | -0.081373 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.058115 | -0.1092 | 0.023913 | 0.11335 | 0.98081 | 0.56844 | 0.54453 | 0.039252 | -0.010865 | -0.003917 | -122.0514 | 0.13381 | 0.044356 | 0.048273 | -121.9437 | -121.913 | 122.1898 | 122.1157 | 122.0656 | 24.7075 | -122.0525 | 0.024968 | 0.13273 | 0.1634 | 0.18806 | -122.0803
3090.4219 | 122.0901 | -0.082397 | 121.9666 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066423 | -0.0090999 | 0.05482 | -0.0099192 | -0.0042257 | -0.0021259 | 0.018972 | 0.030912 | 0.014791 | 0.88468 | 24.5565 | 0.47231 | 122.0707 | 122.0104 | 121.9603 | -0.067636 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.018285 | 0.062694 | -0.10462 | 0.014761 | 0.10419 | 0.96707 | 0.55471 | 0.53995 | 0.043829 | -0.006288 | -0.022227 | -122.0469 | 0.10634 | 0.016888 | 0.039115 | -121.9483 | -121.9039 | 122.1531 | 122.0928 | 122.0427 | 24.6388 | -122.0342 | 0.002079 | 0.10068 | 0.14509 | 0.16517 | -122.0712
3092.125 | 122.0215 | -0.10986 | 121.994 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066851 | -0.0090999 | 0.054606 | 0.0053413 | -0.0044395 | -0.0012713 | 0.018972 | 0.031126 | 0.015005 | 0.88468 | 24.5885 | 0.47689 | 122.0707 | 122.0104 | 121.974 | -0.072215 | 0.02852 | 0.082776 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.11836 | 0.037648 | 0.076724 | 0.99454 | 0.58675 | 0.5491 | 0.016363 | -0.020019 | -0.008498 | -122.0835 | 0.13838 | 0.048933 | 0.057431 | -121.9712 | -121.9267 | 122.1806 | 122.1202 | 122.0839 | 24.6984 | -122.0662 | 0.020388 | 0.13273 | 0.17713 | 0.19264 | -122.1124
3093.9062 | 122.0993 | -0.07782 | 121.962 | 1.4211e-13 | -0.044094 | 0.0025001 | 0.066423 | -0.0095273 | 0.054179 | -0.02518 | -0.0044395 | -0.0016987 | 0.019399 | 0.030912 | 0.014791 | 0.89383 | 24.6251 | 0.48605 | 122.0662 | 122.015 | 121.9648 | -0.072215 | 0.019362 | 0.087354 | -0.06093 | -0.080318 | 0.032021 | 0.062694 | -0.11836 | 0.005605 | 0.10419 | 0.97165 | 0.56387 | 0.55826 | 0.052986 | 0.002868 | -0.040541 | -122.0423 | 0.097182 | 0.01689 | 0.057431 | -121.93 | -121.8993 | 122.144 | 122.0928 | 122.0427 | 24.703 | -122.0342 | -0.002498 | 0.10984 | 0.14051 | 0.16517 | -122.0803
3095.6719 | 121.994 | -0.11444 | 121.9894 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.066637 | -0.0095273 | 0.05482 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018972 | 0.030912 | 0.014791 | 0.89841 | 24.735 | 0.4952 | 122.0662 | 122.0104 | 121.9694 | -0.076794 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.071851 | -0.1092 | 0.037647 | 0.076723 | 1.0129 | 0.60964 | 0.572 | 0.020941 | -0.020019 | 0.005238 | -122.0743 | 0.13838 | 0.048932 | 0.043694 | -121.962 | -121.9176 | 122.1806 | 122.1248 | 122.0839 | 24.8495 | -122.0662 | 0.029545 | 0.14188 | 0.18629 | 0.19722 | -122.0986
3097.4219 | 122.0627 | -0.10529 | 121.994 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066851 | -0.0093137 | 0.054606 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 0.91673 | 24.7304 | 0.4952 | 122.0753 | 122.0012 | 121.9648 | -0.076794 | 0.033099 | 0.078197 | -0.06093 | -0.080318 | 0.018285 | 0.062694 | -0.10462 | 0.028492 | 0.081302 | 1.022 | 0.60049 | 0.572 | 0.007205 | -0.029176 | 0.000662 | -122.0743 | 0.13839 | 0.044356 | 0.043694 | -121.9757 | -121.9313 | 122.1806 | 122.1065 | 122.0701 | 24.8357 | -122.0708 | 0.024968 | 0.12357 | 0.16798 | 0.18348 | -122.0986
3099.2031 | 122.0993 | -0.07782 | 121.9711 | 1.4211e-13 | -0.043025 | 0.0022863 | 0.066423 | -0.0093137 | 0.055033 | 0.0053413 | -0.0042257 | -0.0019123 | 0.018972 | 0.031339 | 0.014791 | 0.9213 | 24.7671 | 0.49978 | 122.0707 | 122.0104 | 121.974 | -0.076794 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.058115 | -0.1092 | 0.001026 | 0.099613 | 0.99912 | 0.5776 | 0.57657 | 0.039252 | 0.00287 | -0.031383 | -122.0514 | 0.10634 | 0.021469 | 0.052852 | -121.9483 | -121.913 | 122.1486 | 122.0882 | 122.0518 | 24.8449 | -122.0479 | -0.002498 | 0.10068 | 0.13594 | 0.1606 | -122.0803
3100.9688 | 122.0123 | -0.11444 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066637 | -0.0093137 | 0.055033 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 0.93046 | 24.7488 | 0.51352 | 122.0662 | 122.0058 | 121.9603 | -0.072215 | 0.023941 | 0.087354 | -0.065509 | -0.084896 | 0.022864 | 0.071851 | -0.1092 | 0.042226 | 0.099611 | 1.0449 | 0.62796 | 0.58573 | 0.03925 | -0.006288 | 0.005238 | -122.0514 | 0.13838 | 0.048932 | 0.043694 | -121.9437 | -121.8947 | 122.1806 | 122.1202 | 122.0747 | 24.8632 | -122.0388 | 0.029545 | 0.13731 | 0.18629 | 0.2018 | -122.0758
3102.6719 | 122.1451 | -0.073242 | 121.9345 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066637 | -0.0093137 | 0.05482 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014791 | 0.93046 | 24.7808 | 0.51809 | 122.0753 | 122.015 | 121.9648 | -0.081373 | 0.02852 | 0.087354 | -0.070087 | -0.080318 | 0.032021 | 0.071851 | -0.11836 | -0.008131 | 0.14081 | 1.0037 | 0.59134 | 0.59947 | 0.080452 | 0.030334 | -0.045119 | -122.0148 | 0.10176 | 0.003155 | 0.048274 | -121.9025 | -121.8627 | 122.1486 | 122.0882 | 122.0381 | 24.854 | -122.0159 | -0.007076 | 0.10526 | 0.14509 | 0.1606 | -122.0529
3104.4375 | 122.0306 | -0.10529 | 122.0169 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066851 | -0.0095273 | 0.05482 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 0.9442 | 24.7579 | 0.52267 | 122.0753 | 122.0195 | 121.9694 | -0.072215 | 0.019362 | 0.078197 | -0.065509 | -0.075739 | 0.018285 | 0.067272 | -0.10462 | 0.033071 | 0.058414 | 1.0495 | 0.62796 | 0.59489 | 0.002633 | -0.047485 | 0.000662 | -122.0926 | 0.12465 | 0.039777 | 0.039115 | -121.9986 | -121.9496 | 122.1806 | 122.1248 | 122.0747 | 24.8632 | -122.0891 | 0.029547 | 0.12357 | 0.17256 | 0.18348 | -122.1215
3106.1562 | 122.0032 | -0.10986 | 121.9803 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066851 | -0.0095273 | 0.05482 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 0.94877 | 24.7808 | 0.52725 | 122.0707 | 122.015 | 121.9603 | -0.076794 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.022864 | 0.071851 | -0.1092 | 0.033069 | 0.090457 | 1.0586 | 0.63711 | 0.60404 | 0.034675 | -0.020021 | 0.00066 | -122.0606 | 0.1338 | 0.053512 | 0.052852 | -121.9574 | -121.9084 | 122.1806 | 122.1248 | 122.0701 | 24.8907 | -122.0571 | 0.029545 | 0.13273 | 0.18171 | 0.18348 | -122.0895
3107.9219 | 122.0261 | -0.10071 | 121.9437 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.066851 | -0.0093137 | 0.054606 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.030698 | 0.014578 | 0.96251 | 24.7808 | 0.53183 | 122.0753 | 122.015 | 121.9648 | -0.076794 | 0.02852 | 0.078197 | -0.06093 | -0.084896 | 0.018285 | 0.071851 | -0.11378 | 0.023914 | 0.13166 | 1.0632 | 0.63254 | 0.60862 | 0.071296 | 0.021178 | -0.013074 | -122.0286 | 0.12923 | 0.039778 | 0.052852 | -121.9254 | -121.8718 | 122.176 | 122.1157 | 122.0656 | 24.8815 | -122.0205 | 0.015812 | 0.11899 | 0.17256 | 0.17891 | -122.0574
3109.7031 | 122.1405 | -0.073242 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.066637 | -0.0093137 | 0.05482 | -0.0022892 | -0.0046531 | -0.0012713 | 0.018758 | 0.031126 | 0.015005 | 0.96709 | 24.79 | 0.53641 | 122.0707 | 122.0104 | 121.9603 | -0.076794 | 0.02852 | 0.082776 | -0.065509 | -0.080318 | 0.032021 | 0.062694 | -0.1092 | -0.003552 | 0.1225 | 1.0403 | 0.60965 | 0.6132 | 0.06214 | 0.012023 | -0.035961 | -122.0286 | 0.10176 | 0.007733 | 0.043694 | -121.9162 | -121.8855 | 122.144 | 122.0836 | 122.0335 | 24.8632 | -122.025 | -0.007076 | 0.10526 | 0.13594 | 0.15602 | -122.0574
3111.4062 | 122.1542 | -0.032043 | 121.9482 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.066851 | -0.0093137 | 0.05482 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019399 | 0.031126 | 0.014578 | 0.98082 | 24.8312 | 0.54098 | 122.0662 | 122.0195 | 121.9603 | -0.072215 | 0.023941 | 0.091933 | -0.065509 | -0.075739 | 0.022864 | 0.062694 | -0.10462 | -0.040172 | 0.11792 | 1.0129 | 0.57303 | 0.6132 | 0.071298 | 0.012023 | -0.072581 | -122.024 | 0.055984 | -0.033466 | 0.039115 | -121.9254 | -121.8855 | 122.0982 | 122.0516 | 121.9923 | 24.8632 | -122.0205 | -0.043696 | 0.054907 | 0.094737 | 0.12398 | -122.0529
3113.1562 | 122.081 | -0.07782 | 121.962 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.066637 | -0.0093137 | 0.05482 | 0.0053413 | -0.0042257 | -0.0019123 | 0.019186 | 0.030912 | 0.014791 | 0.98082 | 24.8632 | 0.55472 | 122.0662 | 122.015 | 121.9603 | -0.072215 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.071851 | -0.11378 | 0.005605 | 0.10419 | 1.0586 | 0.63254 | 0.62693 | 0.052986 | -0.00171 | -0.035962 | -122.0423 | 0.10176 | 0.012311 | 0.048273 | -121.9345 | -121.8901 | 122.144 | 122.0928 | 122.0381 | 24.941 | -122.0342 | -0.002498 | 0.10526 | 0.14967 | 0.15602 | -122.0758
3114.9219 | 122.0444 | -0.11444 | 121.9666 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.066637 | -0.0093137 | 0.05482 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.030912 | 0.014791 | 0.98998 | 24.8907 | 0.56388 | 122.0662 | 122.015 | 121.9648 | -0.072215 | 0.023941 | 0.087354 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.11378 | 0.042226 | 0.099611 | 1.1044 | 0.67832 | 0.63609 | 0.048408 | -0.00171 | 0.000659 | -122.056 | 0.13838 | 0.053511 | 0.052852 | -121.9437 | -121.8993 | 122.1806 | 122.1294 | 122.0793 | 25.0051 | -122.0388 | 0.024966 | 0.13731 | 0.18171 | 0.2018 | -122.0803
3116.6875 | 122.0535 | -0.10529 | 121.9757 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066851 | -0.0090999 | 0.05482 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030698 | 0.014364 | 1.0037 | 24.9136 | 0.56845 | 122.0662 | 122.015 | 121.9648 | -0.072215 | 0.033099 | 0.073618 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.033071 | 0.090456 | 1.109 | 0.67374 | 0.64067 | 0.039253 | -0.010865 | -0.008496 | -122.056 | 0.13839 | 0.048935 | 0.057431 | -121.9483 | -121.9084 | 122.1715 | 122.1202 | 122.0701 | 25.0189 | -122.0479 | 0.024968 | 0.13273 | 0.17256 | 0.1789 | -122.0895
3118.3906 | 122.0947 | -0.064087 | 121.9437 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.066637 | -0.0088863 | 0.05482 | -0.0022892 | -0.0046531 | -0.0016987 | 0.019186 | 0.031126 | 0.014791 | 1.0174 | 24.9227 | 0.57303 | 122.0707 | 122.0012 | 121.9557 | -0.085952 | 0.023941 | 0.078197 | -0.065509 | -0.084896 | 0.027442 | 0.067272 | -0.1092 | -0.021865 | 0.12708 | 1.0815 | 0.63712 | 0.65898 | 0.057559 | 0.012021 | -0.045116 | -122.0286 | 0.088028 | -0.001422 | 0.043694 | -121.9162 | -121.8764 | 122.1348 | 122.0653 | 122.0198 | 24.9868 | -122.0296 | -0.020809 | 0.091529 | 0.13136 | 0.14228 | -122.0529
3120.1562 | 122.1313 | -0.059509 | 121.962 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.066851 | -0.0093137 | 0.054606 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.01415 | 1.0174 | 24.9548 | 0.57303 | 122.0662 | 122.0195 | 121.9648 | -0.081373 | 0.023941 | 0.087354 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | -0.021864 | 0.10419 | 1.077 | 0.63254 | 0.65441 | 0.057565 | 0.002868 | -0.054273 | -122.0469 | 0.08345 | -0.001421 | 0.052852 | -121.9345 | -121.8947 | 122.1257 | 122.079 | 122.0244 | 25.0143 | -122.0433 | -0.025387 | 0.086951 | 0.12678 | 0.14686 | -122.0758
3121.9062 | 122.1497 | -0.082397 | 121.9437 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066637 | -0.0093137 | 0.05482 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.01415 | 1.0358 | 25.0006 | 0.58219 | 122.0753 | 122.0058 | 121.9648 | -0.076794 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.018285 | 0.067272 | -0.11378 | 0.005603 | 0.13166 | 1.1182 | 0.66459 | 0.65898 | 0.062138 | 0.021178 | -0.031385 | -122.0194 | 0.10634 | 0.016888 | 0.048273 | -121.9254 | -121.8764 | 122.1577 | 122.0882 | 122.0472 | 25.083 | -122.0205 | 0.006658 | 0.10068 | 0.14967 | 0.16517 | -122.0574
3123.6562 | 122.0261 | -0.086975 | 121.9803 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066637 | -0.0090999 | 0.055033 | -0.0099192 | -0.0042257 | -0.0021259 | 0.018972 | 0.030698 | 0.014578 | 1.0403 | 24.9639 | 0.58677 | 122.0707 | 122.0012 | 121.9603 | -0.076794 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11836 | 0.010181 | 0.090457 | 1.1273 | 0.67374 | 0.66356 | 0.020938 | -0.020021 | -0.031386 | -122.0606 | 0.10634 | 0.026045 | 0.057431 | -121.9528 | -121.913 | 122.1577 | 122.0882 | 122.0472 | 25.0509 | -122.0571 | 0.006657 | 0.11442 | 0.15425 | 0.16975 | -122.0986
3125.3594 | 122.1313 | -0.082397 | 121.9482 | 1.4211e-13 | -0.043239 | 0.0025001 | 0.066637 | -0.0093137 | 0.05482 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018758 | 0.031339 | 0.014578 | 1.0358 | 24.9136 | 0.58677 | 122.0707 | 122.0058 | 121.9603 | -0.085952 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.022864 | 0.067272 | -0.10462 | -0.003555 | 0.1225 | 1.1182 | 0.66916 | 0.67272 | 0.057561 | 0.012023 | -0.022227 | -122.0331 | 0.10634 | 0.016888 | 0.039115 | -121.9254 | -121.881 | 122.1531 | 122.0882 | 122.0427 | 24.996 | -122.0342 | -0.002499 | 0.10526 | 0.14967 | 0.16517 | -122.0529
3127.125 | 122.0581 | -0.10071 | 121.9711 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066851 | -0.0090999 | 0.05482 | -0.0099192 | -0.0046531 | -0.0019123 | 0.019186 | 0.030698 | 0.015005 | 1.0541 | 25.0097 | 0.60966 | 122.0662 | 122.0104 | 121.9603 | -0.085952 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.058115 | -0.12294 | 0.014756 | 0.095034 | 1.1548 | 0.71037 | 0.69561 | 0.039252 | -0.010865 | -0.022231 | -122.0469 | 0.12923 | 0.039778 | 0.062009 | -121.9437 | -121.913 | 122.1669 | 122.1111 | 122.061 | 25.1104 | -122.0571 | 0.024969 | 0.12815 | 0.15882 | 0.17891 | -122.0941
3128.9062 | 121.994 | -0.12817 | 121.994 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.066851 | -0.0086727 | 0.05482 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019399 | 0.030698 | 0.014578 | 1.0587 | 24.9868 | 0.60966 | 122.0707 | 122.0104 | 121.9603 | -0.076794 | 0.02852 | 0.078197 | -0.051772 | -0.080318 | 0.022864 | 0.071851 | -0.11836 | 0.05138 | 0.076724 | 1.1868 | 0.73783 | 0.68645 | 0.016363 | -0.033754 | 0.009813 | -122.0743 | 0.15669 | 0.076402 | 0.066589 | -121.9712 | -121.9222 | 122.1989 | 122.1386 | 122.0884 | 25.115 | -122.0708 | 0.047856 | 0.15104 | 0.20003 | 0.20637 | -122.1124
3130.6719 | 122.1085 | -0.064087 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066851 | -0.0088863 | 0.05482 | -0.01755 | -0.0040121 | -0.0019123 | 0.019186 | 0.031126 | 0.014791 | 1.0724 | 24.9731 | 0.61424 | 122.0662 | 122.0012 | 121.9648 | -0.072215 | 0.033099 | 0.082776 | -0.056351 | -0.071161 | 0.027442 | 0.067272 | -0.11378 | -0.008128 | 0.11334 | 1.1365 | 0.67832 | 0.68645 | 0.048404 | 0.012023 | -0.049695 | -122.024 | 0.097186 | 0.007736 | 0.057431 | -121.9254 | -121.8855 | 122.1303 | 122.0653 | 122.0289 | 25.0372 | -122.025 | -0.007074 | 0.091529 | 0.13136 | 0.14686 | -122.0666
3132.3594 | 122.049 | -0.10529 | 121.994 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067064 | -0.0093137 | 0.05482 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018972 | 0.030912 | 0.014364 | 1.0815 | 24.9594 | 0.62797 | 122.0662 | 122.0058 | 121.9603 | -0.085952 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.1092 | 0.019334 | 0.072145 | 1.1868 | 0.73326 | 0.71392 | 0.011784 | -0.033754 | -0.003917 | -122.0743 | 0.13381 | 0.044356 | 0.048273 | -121.9666 | -121.9267 | 122.1715 | 122.1111 | 122.0656 | 25.0647 | -122.08 | 0.024968 | 0.13273 | 0.17256 | 0.18806 | -122.1032
3134.125 | 122.0947 | -0.091553 | 121.9528 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.066851 | -0.0093137 | 0.055033 | -0.0022892 | -0.0046531 | -0.0014849 | 0.018972 | 0.030912 | 0.014578 | 1.0953 | 24.9685 | 0.63713 | 122.0662 | 122.0104 | 121.9648 | -0.072215 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.11836 | 0.019338 | 0.11334 | 1.1868 | 0.72868 | 0.70934 | 0.057562 | 0.012023 | -0.026808 | -122.0331 | 0.12007 | 0.026044 | 0.052852 | -121.9254 | -121.8901 | 122.1577 | 122.1019 | 122.0564 | 25.0601 | -122.025 | 0.011235 | 0.11899 | 0.15425 | 0.16975 | -122.0712
3135.8906 | 122.081 | -0.09613 | 121.9711 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066851 | -0.0093137 | 0.055033 | -0.0022892 | -0.0042257 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 1.0999 | 24.9639 | 0.64171 | 122.0662 | 122.0058 | 121.9557 | -0.072215 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.032021 | 0.062694 | -0.11836 | 0.023915 | 0.095034 | 1.196 | 0.73784 | 0.71392 | 0.034673 | -0.015444 | -0.022231 | -122.056 | 0.12007 | 0.030621 | 0.052852 | -121.9391 | -121.9084 | 122.1623 | 122.1019 | 122.0518 | 25.0601 | -122.0433 | 0.011234 | 0.12815 | 0.15882 | 0.17891 | -122.0895
3137.5938 | 122.0993 | -0.086975 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066851 | -0.0090999 | 0.05482 | -0.0099192 | -0.0040121 | -0.0014849 | 0.018758 | 0.030912 | 0.014791 | 1.1273 | 25.0006 | 0.65544 | 122.0753 | 122.0104 | 121.974 | -0.076794 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.022864 | 0.067272 | -0.1092 | 0.010181 | 0.1225 | 1.2143 | 0.74242 | 0.73224 | 0.057562 | 0.02118 | -0.022228 | -122.0377 | 0.10634 | 0.026045 | 0.048273 | -121.93 | -121.8855 | 122.1623 | 122.0974 | 122.061 | 25.0876 | -122.0296 | 0.002079 | 0.10984 | 0.15425 | 0.16517 | -122.062
3139.3594 | 122.0993 | -0.068665 | 121.962 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.067064 | -0.0090999 | 0.05482 | -0.0099192 | -0.0040121 | -0.0019123 | 0.018758 | 0.031126 | 0.014791 | 1.1273 | 25.0006 | 0.6646 | 122.0753 | 122.015 | 121.9694 | -0.081373 | 0.014784 | 0.073618 | -0.06093 | -0.075739 | 0.022864 | 0.067272 | -0.1092 | -0.012708 | 0.11335 | 1.196 | 0.73326 | 0.74597 | 0.052986 | 0.007447 | -0.040538 | -122.0377 | 0.083449 | 0.007735 | 0.048273 | -121.9391 | -121.8947 | 122.144 | 122.0836 | 122.0381 | 25.0692 | -122.0433 | -0.007074 | 0.091529 | 0.13594 | 0.14228 | -122.0712
3141.125 | 122.1313 | -0.054932 | 121.9437 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.066851 | -0.0090999 | 0.05482 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 1.1273 | 25.0097 | 0.6646 | 122.0662 | 122.0104 | 121.9648 | -0.072215 | 0.019362 | 0.073618 | -0.065509 | -0.080318 | 0.022864 | 0.062694 | -0.10462 | -0.017283 | 0.1225 | 1.1823 | 0.71953 | 0.73681 | 0.066717 | 0.021178 | -0.049692 | -122.024 | 0.074294 | -0.010577 | 0.039115 | -121.9208 | -121.881 | 122.1211 | 122.0653 | 122.0198 | 25.0647 | -122.0159 | -0.025386 | 0.077796 | 0.11763 | 0.12855 | -122.0483
3142.8125 | 122.0032 | -0.10986 | 121.9894 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066851 | -0.0093137 | 0.05482 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014364 | 1.1456 | 25.0006 | 0.6646 | 122.0662 | 122.0104 | 121.9603 | -0.081373 | 0.019362 | 0.082776 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11378 | 0.02849 | 0.076723 | 1.2555 | 0.77446 | 0.74597 | 0.020941 | -0.029176 | -0.003919 | -122.0743 | 0.12923 | 0.048933 | 0.052852 | -121.962 | -121.9222 | 122.176 | 122.1202 | 122.0701 | 25.1104 | -122.0708 | 0.024967 | 0.13731 | 0.17713 | 0.19264 | -122.1032
3144.5781 | 122.081 | -0.082397 | 121.9528 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066851 | -0.0088863 | 0.055033 | -0.01755 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 1.1502 | 25.0143 | 0.67375 | 122.0662 | 122.0104 | 121.9648 | -0.076794 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.005603 | 0.11334 | 1.2326 | 0.75615 | 0.75055 | 0.057562 | 0.012023 | -0.031385 | -122.0286 | 0.11092 | 0.021467 | 0.052852 | -121.9254 | -121.8855 | 122.1486 | 122.0928 | 122.0472 | 25.0967 | -122.0296 | 0.006658 | 0.10984 | 0.14967 | 0.16059 | -122.0666
3146.3438 | 122.0261 | -0.11444 | 121.9666 | 1.4211e-13 | -0.04388 | 0.0022863 | 0.066851 | -0.0093137 | 0.055033 | -0.01755 | -0.0040121 | -0.0021259 | 0.018972 | 0.031339 | 0.014578 | 1.1685 | 24.9868 | 0.69665 | 122.0616 | 122.0104 | 121.974 | -0.076794 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.022864 | 0.062694 | -0.11378 | 0.037647 | 0.095033 | 1.283 | 0.81109 | 0.77344 | 0.043829 | 0.007447 | 0.000659 | -122.0514 | 0.13838 | 0.053511 | 0.052852 | -121.9437 | -121.9039 | 122.176 | 122.1248 | 122.0884 | 25.1013 | -122.0433 | 0.029545 | 0.13731 | 0.17713 | 0.18806 | -122.0803
3148.1094 | 122.1176 | -0.068665 | 121.9299 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.066851 | -0.0090999 | 0.055033 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018972 | 0.031126 | 0.014578 | 1.1731 | 24.9502 | 0.70122 | 122.0753 | 122.0195 | 121.9648 | -0.072215 | 0.02852 | 0.073618 | -0.065509 | -0.071161 | 0.032021 | 0.067272 | -0.11378 | -0.00355 | 0.14539 | 1.2418 | 0.76989 | 0.77344 | 0.089608 | 0.034911 | -0.045117 | -122.0011 | 0.097185 | 0.003156 | 0.048273 | -121.8979 | -121.8627 | 122.144 | 122.0882 | 122.0335 | 25.0189 | -122.0021 | -0.002496 | 0.10069 | 0.13594 | 0.14228 | -122.0437
3149.8281 | 122.1451 | -0.064087 | 121.9391 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.067064 | -0.0088863 | 0.055247 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014791 | 1.1868 | 24.9639 | 0.71954 | 122.0662 | 122.015 | 121.9648 | -0.076794 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | -0.012707 | 0.12708 | 1.2509 | 0.78362 | 0.79633 | 0.075874 | 0.025756 | -0.054274 | -122.0194 | 0.088028 | 0.003157 | 0.057431 | -121.9071 | -121.8718 | 122.1303 | 122.079 | 122.0289 | 25.028 | -122.0159 | -0.016231 | 0.096108 | 0.13136 | 0.14686 | -122.0574
3151.5938 | 122.0581 | -0.10529 | 122.0123 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.066637 | -0.0088863 | 0.05482 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019186 | 0.031339 | 0.014791 | 1.2006 | 24.996 | 0.72869 | 122.0753 | 122.015 | 121.9694 | -0.072215 | 0.02852 | 0.073618 | -0.056351 | -0.075739 | 0.032021 | 0.067272 | -0.1092 | 0.033071 | 0.062992 | 1.3059 | 0.83398 | 0.80091 | 0.002632 | -0.042907 | -0.003917 | -122.0881 | 0.13381 | 0.048935 | 0.052852 | -121.9803 | -121.9451 | 122.1806 | 122.1202 | 122.0747 | 25.1013 | -122.0845 | 0.029547 | 0.13731 | 0.17256 | 0.1789 | -122.1215
3153.3594 | 122.1313 | -0.064087 | 121.9391 | 1.4211e-13 | -0.043666 | 0.0020727 | 0.067064 | -0.0088863 | 0.055033 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018972 | 0.031126 | 0.014791 | 1.2189 | 25.0052 | 0.73785 | 122.0662 | 122.0058 | 121.974 | -0.072215 | 0.014784 | 0.087354 | -0.051772 | -0.080318 | 0.027442 | 0.067272 | -0.11836 | -0.008128 | 0.12708 | 1.283 | 0.80194 | 0.81007 | 0.066716 | 0.034913 | -0.054274 | -122.0194 | 0.078871 | 0.012315 | 0.066589 | -121.9116 | -121.8718 | 122.1303 | 122.0699 | 122.0381 | 25.0692 | -122.0113 | -0.016231 | 0.091529 | 0.13136 | 0.15144 | -122.0574
3155.1406 | 122.0444 | -0.091553 | 121.9849 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.066851 | -0.0090999 | 0.055033 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031553 | 0.014578 | 1.2281 | 25.0372 | 0.74243 | 122.0753 | 122.0195 | 121.9648 | -0.072215 | 0.019362 | 0.087354 | -0.056351 | -0.089475 | 0.022864 | 0.067272 | -0.1092 | 0.019338 | 0.090458 | 1.3196 | 0.83398 | 0.81464 | 0.034677 | -0.02002 | -0.01765 | -122.0743 | 0.11091 | 0.035202 | 0.052852 | -121.962 | -121.9176 | 122.1669 | 122.1111 | 122.0564 | 25.1288 | -122.0571 | 0.002078 | 0.11442 | 0.15882 | 0.17891 | -122.0941
3156.9062 | 122.1039 | -0.07782 | 121.9528 | 1.4211e-13 | -0.04388 | 0.0027137 | 0.067064 | -0.0090999 | 0.054606 | -0.01755 | -0.0042257 | -0.0014849 | 0.019399 | 0.031126 | 0.014791 | 1.2326 | 25.0097 | 0.75158 | 122.0662 | 122.015 | 121.974 | -0.072215 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.032021 | 0.067272 | -0.1092 | 0.005605 | 0.11334 | 1.3105 | 0.8294 | 0.8238 | 0.062141 | 0.02118 | -0.031383 | -122.0286 | 0.10176 | 0.021469 | 0.052852 | -121.9208 | -121.8855 | 122.144 | 122.0928 | 122.0518 | 25.0876 | -122.025 | 0.002081 | 0.10984 | 0.14509 | 0.1606 | -122.062
3158.6562 | 122.0261 | -0.12817 | 121.9803 | 1.4211e-13 | -0.04388 | 0.0027137 | 0.066851 | -0.0090999 | 0.055033 | 0.0053413 | -0.0042257 | -0.0016987 | 0.018758 | 0.031126 | 0.014578 | 1.2509 | 25.0143 | 0.76074 | 122.0662 | 122.0241 | 121.9648 | -0.067636 | 0.019362 | 0.091933 | -0.056351 | -0.084896 | 0.022864 | 0.071851 | -0.11378 | 0.060538 | 0.085878 | 1.3791 | 0.88892 | 0.82838 | 0.043833 | -0.015443 | 0.014392 | -122.0652 | 0.14754 | 0.071823 | 0.057431 | -121.9574 | -121.9084 | 122.1943 | 122.1523 | 122.093 | 25.1425 | -122.0479 | 0.043278 | 0.15104 | 0.20003 | 0.22011 | -122.0941
3160.3594 | 122.0581 | -0.086975 | 121.9666 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.066637 | -0.0088863 | 0.055033 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018972 | 0.030912 | 0.014364 | 1.2601 | 25.0052 | 0.77448 | 122.0753 | 122.0195 | 121.9648 | -0.072215 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.01476 | 0.10877 | 1.3471 | 0.86145 | 0.84669 | 0.052987 | -0.00171 | -0.022228 | -122.0469 | 0.10634 | 0.026045 | 0.048273 | -121.9437 | -121.9039 | 122.1623 | 122.1065 | 122.0518 | 25.0921 | -122.0388 | 0.006657 | 0.10984 | 0.14967 | 0.16517 | -122.0758
3162.125 | 122.0398 | -0.09613 | 121.9986 | 1.4211e-13 | -0.044094 | 0.0020727 | 0.066851 | -0.0093137 | 0.05482 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014578 | 1.2647 | 24.9731 | 0.77906 | 122.0707 | 122.015 | 121.9694 | -0.072215 | 0.033099 | 0.082776 | -0.06093 | -0.075739 | 0.032021 | 0.062694 | -0.11836 | 0.023915 | 0.072147 | 1.3608 | 0.87519 | 0.85127 | 0.016365 | -0.029174 | -0.022231 | -122.0743 | 0.12923 | 0.0352 | 0.057431 | -121.9666 | -121.9359 | 122.1669 | 122.1111 | 122.0656 | 25.0692 | -122.0708 | 0.020391 | 0.12815 | 0.15882 | 0.17891 | -122.117
3163.9062 | 121.9986 | -0.11444 | 121.9894 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.067064 | -0.0090999 | 0.055033 | 0.0053413 | -0.0044395 | -0.0019123 | 0.018758 | 0.030912 | 0.014791 | 1.2784 | 24.9639 | 0.78821 | 122.0616 | 122.0058 | 121.9557 | -0.067636 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.013707 | 0.053537 | -0.1092 | 0.046805 | 0.072145 | 1.3929 | 0.90265 | 0.85585 | 0.016362 | -0.033755 | 0.005238 | -122.0789 | 0.13838 | 0.048932 | 0.043694 | -121.9757 | -121.9359 | 122.176 | 122.1202 | 122.0701 | 25.0784 | -122.0571 | 0.024966 | 0.12815 | 0.16798 | 0.19264 | -122.0986
3165.625 | 122.1313 | -0.064087 | 121.9482 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067064 | -0.0088863 | 0.055247 | -0.0022892 | -0.0040121 | -0.0019123 | 0.019186 | 0.031126 | 0.014791 | 1.283 | 24.8586 | 0.79279 | 122.0662 | 122.0012 | 121.9511 | -0.081373 | 0.023941 | 0.087354 | -0.065509 | -0.089475 | 0.027442 | 0.067272 | -0.1092 | -0.017286 | 0.11792 | 1.3471 | 0.85688 | 0.87416 | 0.052982 | 0.002865 | -0.045116 | -122.0377 | 0.088028 | -0.001422 | 0.043694 | -121.9208 | -121.881 | 122.1303 | 122.0653 | 122.0152 | 24.9227 | -122.0296 | -0.025388 | 0.091529 | 0.13136 | 0.15144 | -122.0574
3167.3906 | 122.0352 | -0.1236 | 121.9803 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.066851 | -0.0093137 | 0.055247 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018972 | 0.030912 | 0.014578 | 1.2922 | 24.9319 | 0.79737 | 122.0616 | 122.0058 | 121.9511 | -0.076794 | 0.019362 | 0.087354 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11836 | 0.046802 | 0.0813 | 1.4157 | 0.92096 | 0.87416 | 0.025517 | -0.029179 | 0.005235 | -122.0652 | 0.14296 | 0.062666 | 0.057431 | -121.9528 | -121.913 | 122.1852 | 122.1294 | 122.0747 | 25.0555 | -122.0571 | 0.0387 | 0.15104 | 0.19087 | 0.21095 | -122.0986
3169.0938 | 122.0535 | -0.11902 | 121.9711 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.066423 | -0.0090999 | 0.05482 | -0.01755 | -0.0042257 | -0.0016987 | 0.018758 | 0.030912 | 0.014578 | 1.3105 | 24.8953 | 0.80653 | 122.0524 | 121.9966 | 121.9511 | -0.076794 | 0.019362 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.058115 | -0.11836 | 0.042225 | 0.081299 | 1.4295 | 0.92554 | 0.88332 | 0.025516 | -0.020023 | 0.000658 | -122.056 | 0.13838 | 0.05351 | 0.052852 | -121.9437 | -121.913 | 122.1714 | 122.1157 | 122.0701 | 25.0143 | -122.0479 | 0.034123 | 0.14646 | 0.17713 | 0.2018 | -122.0895
3170.8594 | 122.0673 | -0.10529 | 121.9574 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.066637 | -0.0090999 | 0.055247 | -0.01755 | -0.0044395 | -0.0012713 | 0.019186 | 0.031126 | 0.014578 | 1.315 | 24.8266 | 0.81568 | 122.0524 | 121.9966 | 121.9511 | -0.081373 | 0.02852 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.07643 | -0.11378 | 0.023913 | 0.095032 | 1.4203 | 0.92097 | 0.89705 | 0.039249 | -0.00629 | -0.008496 | -122.0423 | 0.13381 | 0.039777 | 0.048273 | -121.93 | -121.881 | 122.1577 | 122.1019 | 122.0564 | 24.9319 | -122.0388 | 0.02039 | 0.13273 | 0.18172 | 0.18806 | -122.0712
3172.5625 | 122.1313 | -0.073242 | 121.9345 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067064 | -0.0090999 | 0.055247 | -0.01755 | -0.0042257 | -0.0012713 | 0.018758 | 0.031126 | 0.014578 | 1.3242 | 24.9502 | 0.82484 | 122.0524 | 122.0058 | 121.9557 | -0.085952 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.032021 | 0.071851 | -0.11836 | -0.01271 | 0.11792 | 1.3974 | 0.89808 | 0.91079 | 0.071294 | 0.021177 | -0.045119 | -122.0148 | 0.097183 | 0.012312 | 0.057431 | -121.9025 | -121.8627 | 122.1257 | 122.079 | 122.0289 | 25.0235 | -122.0205 | -0.007076 | 0.10526 | 0.14509 | 0.14686 | -122.0529
3174.3281 | 122.0444 | -0.11444 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0025001 | 0.067064 | -0.0086727 | 0.055247 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.030912 | 0.014364 | 1.3517 | 24.9456 | 0.84773 | 122.057 | 121.9921 | 121.9511 | -0.081373 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11836 | 0.033068 | 0.081299 | 1.4661 | 0.96217 | 0.9291 | 0.016359 | -0.024601 | -0.00392 | -122.056 | 0.14296 | 0.053511 | 0.057431 | -121.9483 | -121.913 | 122.1714 | 122.1065 | 122.0655 | 25.0601 | -122.0571 | 0.034123 | 0.14188 | 0.17713 | 0.19722 | -122.0941
3176.0938 | 122.1268 | -0.091553 | 121.907 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067064 | -0.0090999 | 0.055247 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 1.3517 | 24.9044 | 0.85689 | 122.0524 | 121.9966 | 121.942 | -0.085952 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.0366 | 0.067272 | -0.11836 | 0.005601 | 0.14539 | 1.4432 | 0.94844 | 0.94284 | 0.089603 | 0.034907 | -0.026808 | -121.9874 | 0.11549 | 0.035202 | 0.06201 | -121.8704 | -121.8398 | 122.144 | 122.0882 | 122.0335 | 24.996 | -121.993 | 0.011235 | 0.12815 | 0.15882 | 0.17433 | -122.0254
3177.8594 | 122.0947 | -0.10529 | 121.9482 | 1.4211e-13 | -0.043239 | 0.0025001 | 0.066851 | -0.0090999 | 0.055247 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.031339 | 0.014791 | 1.3654 | 24.8495 | 0.86146 | 122.0479 | 121.9875 | 121.9557 | -0.081373 | 0.033099 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.1092 | 0.023913 | 0.099609 | 1.4707 | 0.96675 | 0.94284 | 0.039246 | 0.007444 | -0.003917 | -122.0286 | 0.13839 | 0.044356 | 0.048273 | -121.9208 | -121.881 | 122.1531 | 122.0928 | 122.061 | 24.9548 | -122.0296 | 0.024968 | 0.13273 | 0.17256 | 0.18348 | -122.0574
3179.6406 | 122.0123 | -0.10529 | 121.9666 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067278 | -0.0090999 | 0.055247 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.031339 | 0.014791 | 1.3929 | 24.9319 | 0.8752 | 122.0524 | 121.9966 | 121.942 | -0.085952 | 0.02852 | 0.082776 | -0.056351 | -0.084896 | 0.022864 | 0.071851 | -0.11836 | 0.019334 | 0.085876 | 1.4982 | 0.98048 | 0.96115 | 0.030093 | -0.024603 | -0.013075 | -122.0514 | 0.13381 | 0.048935 | 0.06201 | -121.9437 | -121.8947 | 122.1577 | 122.1019 | 122.0472 | 25.0372 | -122.0525 | 0.02039 | 0.12815 | 0.17714 | 0.18806 | -122.0849
3181.4062 | 122.0123 | -0.10986 | 121.962 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.067064 | -0.0086727 | 0.055461 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018758 | 0.031126 | 0.014791 | 1.3975 | 24.9548 | 0.87978 | 122.0433 | 121.9921 | 121.9465 | -0.085952 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.0366 | 0.062694 | -0.11378 | 0.023911 | 0.081297 | 1.5073 | 0.98964 | 0.96573 | 0.030092 | -0.015446 | -0.003919 | -122.0423 | 0.13838 | 0.048933 | 0.052852 | -121.9254 | -121.8993 | 122.1531 | 122.1019 | 122.0564 | 25.0647 | -122.0479 | 0.029545 | 0.14646 | 0.17256 | 0.19264 | -122.0758
3183.1094 | 122.0901 | -0.10071 | 121.9666 | 1.4211e-13 | -0.043666 | 0.0027137 | 0.066851 | -0.0090999 | 0.055247 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.030698 | 0.014578 | 1.4066 | 24.9456 | 0.89809 | 122.0524 | 121.9875 | 121.9465 | -0.085952 | 0.02852 | 0.082776 | -0.06093 | -0.084896 | 0.027442 | 0.062694 | -0.10462 | 0.014756 | 0.085876 | 1.5073 | 0.9988 | 0.98404 | 0.020935 | -0.020024 | -0.003916 | -122.0514 | 0.12923 | 0.039778 | 0.043694 | -121.9391 | -121.9039 | 122.1531 | 122.0882 | 122.0472 | 25.0463 | -122.0525 | 0.015812 | 0.12815 | 0.1634 | 0.18348 | -122.0712
3184.875 | 122.0169 | -0.13733 | 121.9437 | 1.4211e-13 | -0.043239 | 0.0025001 | 0.067278 | -0.0088863 | 0.055461 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 1.4158 | 24.8586 | 0.90267 | 122.0479 | 121.9829 | 121.942 | -0.085952 | 0.023941 | 0.078197 | -0.065509 | -0.089475 | 0.022864 | 0.062694 | -0.1092 | 0.051377 | 0.10419 | 1.5531 | 1.04 | 0.98862 | 0.039244 | -0.001715 | 0.028126 | -122.0331 | 0.16127 | 0.07182 | 0.043694 | -121.9208 | -121.881 | 122.1852 | 122.1202 | 122.0793 | 24.996 | -122.0296 | 0.047854 | 0.16019 | 0.20002 | 0.21553 | -122.0529
3186.5781 | 121.9849 | -0.1236 | 121.9666 | 1.4211e-13 | -0.043453 | 0.0022863 | 0.067278 | -0.0090999 | 0.055247 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.030912 | 0.014791 | 1.4387 | 24.8861 | 0.92098 | 122.0524 | 121.9921 | 121.9511 | -0.090531 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.071851 | -0.1092 | 0.033065 | 0.085876 | 1.5623 | 1.0446 | 1.0115 | 0.025514 | -0.015446 | 0.014393 | -122.0469 | 0.15212 | 0.062666 | 0.048273 | -121.9437 | -121.8947 | 122.176 | 122.1157 | 122.0747 | 25.0097 | -122.0571 | 0.043278 | 0.14646 | 0.19545 | 0.20179 | -122.0758
3188.3438 | 122.0901 | -0.086975 | 121.9254 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067278 | -0.0090999 | 0.055247 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 1.4432 | 24.8266 | 0.92556 | 122.0524 | 121.9921 | 121.942 | -0.085952 | 0.019362 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.071851 | -0.11378 | 0.001023 | 0.12708 | 1.5302 | 1.0125 | 1.0115 | 0.066713 | 0.016596 | -0.026807 | -122.0057 | 0.10634 | 0.030624 | 0.057431 | -121.9025 | -121.8535 | 122.1394 | 122.079 | 122.0289 | 24.9136 | -122.0113 | 0.006657 | 0.10984 | 0.15883 | 0.16975 | -122.0391
3190.0469 | 122.0261 | -0.11444 | 121.9345 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067064 | -0.0090999 | 0.055247 | -0.01755 | -0.0042257 | -0.0016987 | 0.018972 | 0.030698 | 0.014364 | 1.457 | 24.7579 | 0.9164 | 122.0479 | 121.9875 | 121.9374 | -0.081373 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.12294 | 0.033068 | 0.11334 | 1.5714 | 1.0308 | 0.99778 | 0.052979 | 0.002863 | -0.008498 | -122.0102 | 0.13838 | 0.053511 | 0.062009 | -121.9071 | -121.8672 | 122.1623 | 122.1019 | 122.0518 | 24.8724 | -122.0159 | 0.038702 | 0.14188 | 0.18171 | 0.19264 | -122.0574
3191.8125 | 121.994 | -0.11902 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0027137 | 0.067064 | -0.0090999 | 0.055247 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.030698 | 0.014364 | 1.4707 | 24.7396 | 0.93014 | 122.0479 | 121.9829 | 121.942 | -0.085952 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.033067 | 0.095031 | 1.5897 | 1.0492 | 1.0161 | 0.030089 | -0.01087 | 0.005237 | -122.0331 | 0.14296 | 0.062668 | 0.057431 | -121.9254 | -121.8855 | 122.1669 | 122.1019 | 122.061 | 24.8586 | -122.0388 | 0.038701 | 0.14646 | 0.18629 | 0.2018 | -122.0666
3193.5781 | 122.1176 | -0.064087 | 121.9254 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.067278 | -0.0088863 | 0.055461 | -0.01755 | -0.0042257 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 1.4844 | 24.7259 | 0.94387 | 122.0433 | 121.9829 | 121.9328 | -0.081373 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | -0.017286 | 0.11792 | 1.5485 | 1.008 | 1.0252 | 0.057555 | 0.007439 | -0.049695 | -122.0057 | 0.083449 | 0.003157 | 0.052852 | -121.8979 | -121.8627 | 122.1074 | 122.047 | 121.9969 | 24.7899 | -122.0067 | -0.016231 | 0.091529 | 0.12678 | 0.14228 | -122.0391
3195.2812 | 121.994 | -0.12817 | 121.9666 | 1.4211e-13 | -0.044094 | 0.0027137 | 0.067064 | -0.0093137 | 0.055247 | -0.01755 | -0.0042257 | -0.0016987 | 0.019186 | 0.030912 | 0.014578 | 1.489 | 24.7075 | 0.95303 | 122.0433 | 121.9875 | 121.9374 | -0.085952 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | 0.042222 | 0.076719 | 1.6172 | 1.0812 | 1.039 | 0.020935 | -0.029181 | 0.018971 | -122.0469 | 0.15212 | 0.067244 | 0.048273 | -121.9437 | -121.9039 | 122.1714 | 122.1157 | 122.0655 | 24.8357 | -122.0525 | 0.047856 | 0.15104 | 0.19087 | 0.20637 | -122.0758
3197.0469 | 122.1176 | -0.073242 | 121.9116 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067064 | -0.0088863 | 0.055247 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.031339 | 0.014791 | 1.5028 | 24.6343 | 0.96676 | 122.0387 | 121.9783 | 121.9374 | -0.090531 | 0.014784 | 0.078197 | -0.065509 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | -0.017289 | 0.12707 | 1.576 | 1.04 | 1.0573 | 0.066709 | 0.025751 | -0.04054 | -121.9874 | 0.088026 | 0.007733 | 0.048273 | -121.8842 | -121.8398 | 122.1119 | 122.0516 | 122.0106 | 24.7075 | -122.0022 | -0.002497 | 0.10068 | 0.14509 | 0.15144 | -122.0254
3198.8125 | 122.0673 | -0.091553 | 121.9299 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067278 | -0.0090999 | 0.055461 | -0.02518 | -0.0040121 | -0.0016987 | 0.019399 | 0.031339 | 0.014578 | 1.5165 | 24.7167 | 0.9805 | 122.0341 | 121.9738 | 121.9236 | -0.09511 | 0.023941 | 0.087354 | -0.065509 | -0.080318 | 0.022864 | 0.062694 | -0.1092 | -0.003557 | 0.10418 | 1.608 | 1.0721 | 1.0756 | 0.043819 | -0.006296 | -0.01765 | -122.0102 | 0.11549 | 0.026044 | 0.043694 | -121.9071 | -121.8672 | 122.1257 | 122.0653 | 122.0152 | 24.8083 | -122.025 | 0.011235 | 0.11442 | 0.15425 | 0.17891 | -122.0391
3200.5156 | 121.843 | -1.6983 | 119.9615 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.067064 | -0.0093137 | 0.055247 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019399 | 0.031126 | 0.014364 | 0.20708 | 23.7231 | -0.33347 | 120.4408 | 120.3894 | 120.3486 | -1.4093 | -0.00811 | 0.041567 | -0.10672 | -0.11695 | -0.013765 | 0.026065 | -0.11836 | 0.28904 | 0.47929 | 1.9054 | 1.3648 | 1.0758 | 0.4279 | 0.38705 | 1.5799 | -120.0785 | 1.6902 | 1.5916 | 0.011644 | -119.9753 | -119.9355 | 122.1391 | 122.0877 | 122.0469 | 25.4214 | -121.3708 | 1.5814 | 1.6845 | 1.7244 | 1.7399 | -120.0799
3202.2812 | 122.0352 | -0.041199 | 121.8246 | 1.4211e-13 | -0.043666 | 0.0022863 | 0.067064 | -0.0088863 | 0.055247 | -0.0022892 | -0.0037985 | -0.0016987 | 0.019399 | 0.031126 | 0.015005 | 1.576 | 24.7167 | 1.0263 | 121.9425 | 121.8822 | 121.8366 | -0.040163 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.022864 | 0.062694 | -0.11378 | 0.001036 | 0.1179 | 1.6172 | 1.0675 | 1.0664 | 0.057526 | 0.011996 | -0.072583 | -121.8958 | 0.06514 | -0.015152 | 0.057431 | -121.8018 | -121.762 | 121.9837 | 121.9234 | 121.8778 | 24.7579 | -121.8648 | -0.029962 | 0.064063 | 0.10389 | 0.12398 | -121.9384
3203.9844 | 122.0581 | -0.050354 | 121.8475 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067064 | -0.0086727 | 0.055247 | -0.01755 | -0.0040121 | -0.0014849 | 0.018972 | 0.030912 | 0.014791 | 1.5852 | 24.6938 | 1.04 | 121.9746 | 121.9234 | 121.8824 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.084896 | 0.032021 | 0.071851 | -0.1092 | -0.003545 | 0.12706 | 1.6355 | 1.0904 | 1.0939 | 0.075849 | 0.034894 | -0.058849 | -121.9324 | 0.078874 | -0.010576 | 0.048273 | -121.8155 | -121.7757 | 122.025 | 121.9737 | 121.9328 | 24.7442 | -121.9014 | -0.034542 | 0.082375 | 0.12221 | 0.13313 | -121.9567
3205.75 | 121.9208 | -0.10986 | 121.9162 | 1.4211e-13 | -0.044094 | 0.0022863 | 0.067278 | -0.0088863 | 0.055461 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019186 | 0.031126 | 0.014578 | 1.5989 | 24.6984 | 1.0492 | 121.9883 | 121.9463 | 121.887 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.11378 | 0.060542 | 0.072133 | 1.7088 | 1.159 | 1.0985 | 0.030078 | -0.029192 | -0.003919 | -121.9965 | 0.1338 | 0.048933 | 0.052852 | -121.8979 | -121.8489 | 122.0982 | 122.0561 | 121.9969 | 24.8083 | -121.9655 | 0.029545 | 0.12815 | 0.17713 | 0.19264 | -122.03
3207.5156 | 122.0444 | -0.059509 | 121.8704 | 1.4211e-13 | -0.043666 | 0.0027137 | 0.067278 | -0.0088863 | 0.055033 | -0.0022892 | -0.0046531 | -0.0012713 | 0.019399 | 0.031339 | 0.01415 | 1.6126 | 24.7762 | 1.0583 | 122.0021 | 121.9417 | 121.9007 | -0.049321 | 0.023941 | 0.087354 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.010188 | 0.13164 | 1.6721 | 1.1178 | 1.1077 | 0.071276 | 0.030321 | -0.054273 | -121.9507 | 0.08345 | -0.006 | 0.048273 | -121.843 | -121.8077 | 122.0616 | 122.0012 | 121.9603 | 24.8357 | -121.9197 | -0.020809 | 0.086951 | 0.1222 | 0.14686 | -121.9842
3209.2969 | 122.0673 | -0.054932 | 121.8842 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067064 | -0.0088863 | 0.055247 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.014578 | 1.631 | 24.79 | 1.0812 | 122.0112 | 121.9509 | 121.9053 | -0.040163 | 0.02852 | 0.078197 | -0.056351 | -0.075739 | 0.022864 | 0.071851 | -0.11378 | 0.014769 | 0.12707 | 1.6859 | 1.1362 | 1.1214 | 0.066701 | 0.021166 | -0.05885 | -121.9599 | 0.083452 | -0.001419 | 0.057431 | -121.8613 | -121.8123 | 122.0662 | 122.0058 | 121.9603 | 24.8449 | -121.9243 | -0.020807 | 0.077796 | 0.12678 | 0.13313 | -121.9979
3211 | 122.0581 | -0.064087 | 121.8842 | 1.4211e-13 | -0.043666 | 0.0027137 | 0.067492 | -0.0086727 | 0.055674 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 1.6493 | 24.8174 | 1.095 | 122.0112 | 121.9554 | 121.9053 | -0.044742 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.022864 | 0.062694 | -0.11378 | 0.019345 | 0.12707 | 1.7134 | 1.159 | 1.1397 | 0.07128 | 0.021166 | -0.049695 | -121.9645 | 0.088028 | 0.007736 | 0.057431 | -121.8613 | -121.8215 | 122.0753 | 122.0195 | 121.9694 | 24.8815 | -121.9289 | -0.016231 | 0.086951 | 0.12678 | 0.14228 | -121.9979
3212.7656 | 121.9711 | -0.09613 | 121.8979 | 1.4211e-13 | -0.043453 | 0.0029273 | 0.067705 | -0.0088863 | 0.055247 | 0.0053413 | -0.0042257 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 1.6722 | 24.8632 | 1.1087 | 122.0158 | 121.96 | 121.9145 | -0.049321 | 0.02852 | 0.078197 | -0.056351 | -0.084896 | 0.027442 | 0.058115 | -0.11836 | 0.046809 | 0.11791 | 1.7683 | 1.2048 | 1.158 | 0.062126 | 0.016591 | -0.022231 | -121.9828 | 0.12465 | 0.039779 | 0.06201 | -121.8704 | -121.8398 | 122.1119 | 122.0561 | 122.0106 | 24.9593 | -121.9472 | 0.011234 | 0.12357 | 0.15424 | 0.17433 | -122.0162
3214.5312 | 121.9803 | -0.10529 | 121.9254 | 1.4211e-13 | -0.043666 | 0.0027137 | 0.067278 | -0.0086727 | 0.055247 | -0.01755 | -0.0044395 | -0.0014849 | 0.019186 | 0.031339 | 0.014578 | 1.6813 | 24.8312 | 1.1178 | 122.0204 | 121.9646 | 121.9145 | -0.053899 | 0.033099 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.062694 | -0.11378 | 0.051387 | 0.095026 | 1.7866 | 1.2231 | 1.1717 | 0.039239 | -0.010875 | -0.008496 | -122.0102 | 0.13839 | 0.039777 | 0.048273 | -121.8979 | -121.8627 | 122.1257 | 122.0699 | 122.0198 | 24.9365 | -121.9793 | 0.02039 | 0.13273 | 0.16798 | 0.18806 | -122.0391
3216.25 | 122.0718 | -0.054932 | 121.9025 | 1.4211e-13 | -0.043666 | 0.0027137 | 0.067492 | -0.0086727 | 0.055674 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.030912 | 0.014791 | 1.6951 | 24.7762 | 1.1362 | 122.025 | 121.9692 | 121.9145 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.10462 | 0.005611 | 0.12249 | 1.75 | 1.1911 | 1.1855 | 0.066706 | 0.012013 | -0.049692 | -121.9828 | 0.083452 | -0.005998 | 0.043694 | -121.8704 | -121.8352 | 122.0799 | 122.0241 | 121.9694 | 24.8312 | -121.9518 | -0.025386 | 0.086953 | 0.1222 | 0.13313 | -122.0071
3218.0156 | 122.081 | -0.054932 | 121.8842 | 1.4211e-13 | -0.04388 | 0.0027137 | 0.067064 | -0.0090999 | 0.055461 | 0.0053413 | -0.0044395 | -0.0014849 | 0.018972 | 0.030912 | 0.014578 | 1.7088 | 24.8129 | 1.1453 | 122.0341 | 121.9692 | 121.9236 | -0.049321 | 0.023941 | 0.087354 | -0.056351 | -0.080318 | 0.022864 | 0.071851 | -0.10462 | 0.005611 | 0.14996 | 1.7637 | 1.2002 | 1.1946 | 0.085017 | 0.039481 | -0.049692 | -121.9645 | 0.078873 | -0.001419 | 0.048273 | -121.8613 | -121.8123 | 122.089 | 122.0241 | 121.9786 | 24.8678 | -121.9335 | -0.025386 | 0.077796 | 0.12678 | 0.14229 | -121.9888
3219.7812 | 122.0627 | -0.07782 | 121.9025 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067278 | -0.0086727 | 0.055461 | -0.01755 | -0.0044395 | -0.0014849 | 0.019186 | 0.030912 | 0.014578 | 1.7271 | 24.8586 | 1.1545 | 122.0295 | 121.9692 | 121.9236 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.022864 | 0.067272 | -0.11378 | 0.028499 | 0.12707 | 1.8049 | 1.2323 | 1.2038 | 0.066706 | 0.02117 | -0.035962 | -121.9736 | 0.10176 | 0.021469 | 0.057431 | -121.8796 | -121.8352 | 122.1074 | 122.047 | 122.0015 | 24.9365 | -121.9518 | 0.006659 | 0.10068 | 0.14509 | 0.1606 | -122.0162
3221.4844 | 122.0261 | -0.068665 | 121.8796 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.067492 | -0.0086727 | 0.055461 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.030912 | 0.01415 | 1.7454 | 24.8815 | 1.1636 | 122.0387 | 121.9738 | 121.9282 | -0.049321 | 0.033099 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.062694 | -0.1092 | 0.019344 | 0.15912 | 1.8141 | 1.2323 | 1.213 | 0.094173 | 0.048636 | -0.040538 | -121.9553 | 0.10176 | 0.012314 | 0.052852 | -121.8521 | -121.8169 | 122.1074 | 122.0424 | 121.9969 | 24.9502 | -121.9289 | -0.007074 | 0.096107 | 0.13136 | 0.15144 | -121.9888
3223.25 | 122.0169 | -0.11444 | 121.9528 | 1.4211e-13 | -0.043453 | 0.0029273 | 0.067492 | -0.0086727 | 0.055247 | -0.01755 | -0.0040121 | -0.0016987 | 0.018758 | 0.031126 | 0.014578 | 1.7546 | 24.8495 | 1.1819 | 122.0341 | 121.9783 | 121.9328 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.022864 | 0.071851 | -0.11378 | 0.06512 | 0.081295 | 1.869 | 1.2964 | 1.2313 | 0.02551 | -0.020027 | 0.000659 | -122.0286 | 0.13838 | 0.053511 | 0.052852 | -121.93 | -121.881 | 122.1486 | 122.0928 | 122.0472 | 24.9639 | -122.0021 | 0.038702 | 0.13731 | 0.18629 | 0.19722 | -122.0666
3225.0156 | 121.9574 | -0.11444 | 121.9574 | 1.4211e-13 | -0.043239 | 0.0025001 | 0.067278 | -0.0090999 | 0.055674 | -0.01755 | -0.0044395 | -0.0016987 | 0.019399 | 0.031126 | 0.014364 | 1.7729 | 24.8449 | 1.2048 | 122.0341 | 121.9875 | 121.942 | -0.049321 | 0.033099 | 0.087354 | -0.056351 | -0.080318 | 0.027442 | 0.071851 | -0.11836 | 0.06512 | 0.076718 | 1.8873 | 1.3193 | 1.2542 | 0.030091 | -0.015447 | -0.00392 | -122.0377 | 0.14754 | 0.05809 | 0.06201 | -121.93 | -121.8855 | 122.1486 | 122.1019 | 122.0564 | 24.9593 | -122.0067 | 0.034123 | 0.14188 | 0.18629 | 0.2018 | -122.0758
3226.7344 | 122.1268 | -0.050354 | 121.9116 | 1.4211e-13 | -0.043239 | 0.0027137 | 0.067278 | -0.0086727 | 0.055674 | -0.0022892 | -0.0040121 | -0.0016987 | 0.019186 | 0.031339 | 0.014791 | 1.7912 | 24.8907 | 1.2094 | 122.0387 | 121.9829 | 121.9374 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.001033 | 0.12707 | 1.8416 | 1.2598 | 1.2587 | 0.071288 | 0.025751 | -0.058849 | -121.9919 | 0.074295 | -0.015155 | 0.043694 | -121.8842 | -121.8489 | 122.089 | 122.0333 | 121.9877 | 24.941 | -121.9609 | -0.029964 | 0.077796 | 0.11305 | 0.13313 | -122.0208
3228.4844 | 122.0078 | -0.10071 | 121.9574 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067064 | -0.0088863 | 0.055888 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018758 | 0.031339 | 0.014578 | 1.8004 | 24.9365 | 1.2323 | 122.0479 | 121.9829 | 121.9374 | -0.049321 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.051387 | 0.090454 | 1.9011 | 1.333 | 1.2816 | 0.025512 | -0.020025 | -0.013074 | -122.0377 | 0.12923 | 0.044357 | 0.057431 | -121.93 | -121.8901 | 122.1486 | 122.0836 | 122.0381 | 25.0372 | -122.0067 | 0.02039 | 0.12815 | 0.16798 | 0.17891 | -122.0712
3230.25 | 121.9574 | -0.086975 | 121.9437 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067492 | -0.0088863 | 0.055674 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018758 | 0.030912 | 0.014578 | 1.8278 | 24.9777 | 1.246 | 122.0479 | 121.9921 | 121.9374 | -0.049321 | 0.033099 | 0.082776 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.037654 | 0.10419 | 1.9148 | 1.333 | 1.2954 | 0.048402 | -0.006293 | -0.026807 | -122.0194 | 0.12007 | 0.026045 | 0.052852 | -121.9162 | -121.8764 | 122.1348 | 122.079 | 122.0243 | 25.0647 | -121.993 | 0.011236 | 0.11442 | 0.15425 | 0.16975 | -122.0574
3231.9531 | 121.9757 | -0.10986 | 121.9757 | 1.4211e-13 | -0.043239 | 0.0027137 | 0.067492 | -0.0086727 | 0.055461 | -0.0099192 | -0.0044395 | -0.0012713 | 0.019186 | 0.031126 | 0.014578 | 1.8416 | 24.9685 | 1.2506 | 122.0479 | 121.9875 | 121.9465 | -0.049321 | 0.02852 | 0.087354 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.060542 | 0.072143 | 1.9514 | 1.3605 | 1.2999 | 0.01178 | -0.029179 | -0.003919 | -122.0514 | 0.13838 | 0.048933 | 0.052852 | -121.9483 | -121.9084 | 122.1577 | 122.0974 | 122.0564 | 25.0784 | -122.025 | 0.034124 | 0.13731 | 0.17713 | 0.19722 | -122.0895
3233.7188 | 122.0718 | -0.064087 | 121.9162 | 1.4211e-13 | -0.043453 | 0.0020727 | 0.067492 | -0.0088863 | 0.055888 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.031339 | 0.014791 | 1.8645 | 24.9823 | 1.2735 | 122.0479 | 121.9875 | 121.942 | -0.053899 | 0.023941 | 0.082776 | -0.070087 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.010188 | 0.13165 | 1.9285 | 1.3376 | 1.3274 | 0.071289 | 0.025751 | -0.045116 | -121.9965 | 0.088028 | -0.006 | 0.039116 | -121.8888 | -121.8535 | 122.1119 | 122.0516 | 122.006 | 25.0463 | -121.9701 | -0.016231 | 0.091529 | 0.12678 | 0.14686 | -122.0254
3235.4219 | 122.113 | -0.064087 | 121.9528 | 1.4211e-13 | -0.043239 | 0.0022863 | 0.067492 | -0.0090999 | 0.055461 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018972 | 0.031339 | 0.01415 | 1.8828 | 24.9914 | 1.2872 | 122.0433 | 121.9875 | 121.9465 | -0.049321 | 0.019362 | 0.082776 | -0.051772 | -0.075739 | 0.022864 | 0.067272 | -0.11378 | 0.014766 | 0.090452 | 1.9469 | 1.3513 | 1.3366 | 0.034668 | -0.006291 | -0.049695 | -122.0286 | 0.083449 | 0.012315 | 0.06201 | -121.93 | -121.8855 | 122.1074 | 122.0516 | 122.0106 | 25.0555 | -122.0021 | -0.011652 | 0.086951 | 0.13136 | 0.14686 | -122.0666
3237.2031 | 122.0673 | -0.082397 | 121.9437 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.067492 | -0.0086727 | 0.055247 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 1.9011 | 25.0509 | 1.301 | 122.0479 | 121.9966 | 121.9511 | -0.053899 | 0.033099 | 0.082776 | -0.065509 | -0.075739 | 0.022864 | 0.058115 | -0.11378 | 0.028498 | 0.10419 | 1.9835 | 1.3834 | 1.3549 | 0.052981 | 0.007442 | -0.031385 | -122.0194 | 0.1155 | 0.016888 | 0.048273 | -121.9208 | -121.8855 | 122.1302 | 122.079 | 122.0335 | 25.1333 | -121.9976 | 0.006658 | 0.10526 | 0.14051 | 0.16517 | -122.0574
3238.9531 | 122.0215 | -0.091553 | 121.9482 | 1.4211e-13 | -0.043025 | 0.0025001 | 0.067705 | -0.0086727 | 0.055888 | -0.01755 | -0.0042257 | -0.0019123 | 0.019186 | 0.031339 | 0.014791 | 1.9194 | 25.0876 | 1.3239 | 122.0433 | 121.9921 | 121.9465 | -0.053899 | 0.019362 | 0.078197 | -0.06093 | -0.084896 | 0.0366 | 0.062694 | -0.11378 | 0.037654 | 0.09503 | 2.0109 | 1.4154 | 1.3778 | 0.043825 | -0.001713 | -0.022229 | -122.0331 | 0.11091 | 0.030623 | 0.052852 | -121.9116 | -121.8855 | 122.1348 | 122.0836 | 122.0381 | 25.1791 | -122.0021 | 0.006657 | 0.12815 | 0.15425 | 0.16975 | -122.062
3240.7188 | 122.1176 | -0.045776 | 121.9162 | 1.4211e-13 | -0.043239 | 0.0027137 | 0.067278 | -0.0086727 | 0.055674 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.030912 | 0.01415 | 1.9423 | 25.1425 | 1.3468 | 122.057 | 121.9875 | 121.9465 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | -0.008123 | 0.14081 | 1.9881 | 1.3925 | 1.4007 | 0.071289 | 0.03033 | -0.068006 | -121.9965 | 0.069717 | -0.010575 | 0.057431 | -121.8888 | -121.8489 | 122.1028 | 122.0333 | 121.9923 | 25.1883 | -121.9701 | -0.034542 | 0.073218 | 0.11305 | 0.12855 | -122.03
3242.4375 | 122.1085 | -0.059509 | 121.9437 | 1.4211e-13 | -0.043453 | 0.0027137 | 0.067492 | -0.0086727 | 0.055461 | -0.0022892 | -0.0046531 | -0.0014849 | 0.019186 | 0.031339 | 0.014791 | 1.9698 | 25.2066 | 1.3605 | 122.0524 | 121.9966 | 121.942 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11836 | 0.010188 | 0.10876 | 2.0293 | 1.42 | 1.4098 | 0.052981 | -0.001715 | -0.058852 | -122.024 | 0.088029 | -0.001421 | 0.057431 | -121.9162 | -121.8764 | 122.1119 | 122.0562 | 122.0015 | 25.2661 | -121.993 | -0.020809 | 0.086951 | 0.12678 | 0.13771 | -122.062
3244.2031 | 121.9894 | -0.10529 | 121.9482 | 1.4211e-13 | -0.043453 | 0.0027137 | 0.067705 | -0.0086727 | 0.055888 | -0.0022892 | -0.0046531 | -0.0016987 | 0.019186 | 0.031126 | 0.01415 | 1.9835 | 25.2982 | 1.3834 | 122.0524 | 121.9966 | 121.9511 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.055965 | 0.10419 | 2.0888 | 1.4887 | 1.4327 | 0.048404 | 0.002865 | -0.008496 | -122.024 | 0.12923 | 0.039777 | 0.048273 | -121.9208 | -121.881 | 122.1577 | 122.1019 | 122.0564 | 25.4035 | -121.9976 | 0.029547 | 0.13273 | 0.17256 | 0.18806 | -122.062
3245.9688 | 122.0535 | -0.091553 | 121.9208 | 1.4211e-13 | -0.04388 | 0.0025001 | 0.067705 | -0.0084589 | 0.055888 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031126 | 0.014364 | 2.0064 | 25.3394 | 1.4017 | 122.0479 | 122.0012 | 121.942 | -0.049321 | 0.02852 | 0.091933 | -0.065509 | -0.075739 | 0.0366 | 0.071851 | -0.11378 | 0.042232 | 0.12707 | 2.0979 | 1.4933 | 1.451 | 0.080448 | 0.021174 | -0.022229 | -121.9965 | 0.12007 | 0.026044 | 0.048273 | -121.8842 | -121.8489 | 122.1394 | 122.0928 | 122.0335 | 25.4309 | -121.9701 | 0.015814 | 0.12815 | 0.1634 | 0.18349 | -122.0346
3247.75 | 122.0078 | -0.10071 | 121.9437 | 1.4211e-13 | -0.043239 | 0.0029273 | 0.067705 | -0.0084589 | 0.055888 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018758 | 0.030912 | 0.014791 | 2.0293 | 25.4951 | 1.4246 | 122.0524 | 122.0012 | 121.9511 | -0.049321 | 0.033099 | 0.078197 | -0.056351 | -0.084896 | 0.032021 | 0.071851 | -0.1092 | 0.051387 | 0.10876 | 2.13 | 1.5253 | 1.4739 | 0.057559 | 0.007442 | -0.008495 | -122.0286 | 0.13381 | 0.044357 | 0.052852 | -121.9116 | -121.8718 | 122.1531 | 122.1019 | 122.0518 | 25.5958 | -121.993 | 0.015812 | 0.13273 | 0.17256 | 0.17891 | -122.0529
3249.4531 | 122.0947 | -0.07782 | 121.962 | 1.4211e-13 | -0.043666 | 0.0029273 | 0.067705 | -0.0086727 | 0.056315 | -0.01755 | -0.0042257 | -0.0016987 | 0.019186 | 0.031339 | 0.01415 | 2.0659 | 25.5592 | 1.4475 | 122.057 | 122.0012 | 121.9557 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.0366 | 0.071851 | -0.11378 | 0.023921 | 0.095032 | 2.1437 | 1.5253 | 1.5014 | 0.039249 | -0.006289 | -0.035962 | -122.0423 | 0.10176 | 0.012311 | 0.048273 | -121.9254 | -121.8901 | 122.1348 | 122.079 | 122.0335 | 25.637 | -122.0159 | -0.002498 | 0.11442 | 0.14967 | 0.15602 | -122.0758
3251.2188 | 122.0215 | -0.10529 | 121.9208 | 1.4211e-13 | -0.043666 | 0.0027137 | 0.067919 | -0.0084589 | 0.055888 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018972 | 0.031339 | 0.014364 | 2.0796 | 25.6553 | 1.4658 | 122.057 | 121.9966 | 121.9557 | -0.053899 | 0.02852 | 0.082776 | -0.065509 | -0.080318 | 0.032021 | 0.067272 | -0.11378 | 0.051387 | 0.13623 | 2.1849 | 1.5711 | 1.5197 | 0.07587 | 0.03491 | -0.008496 | -122.0011 | 0.13381 | 0.039777 | 0.048273 | -121.8888 | -121.8535 | 122.1623 | 122.1019 | 122.061 | 25.7606 | -121.9747 | 0.024968 | 0.13731 | 0.17256 | 0.18806 | -122.0346
3253 | 122.0032 | -0.12817 | 121.9574 | 1.4211e-13 | -0.043453 | 0.0029273 | 0.067705 | -0.0082453 | 0.056101 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019186 | 0.031339 | 0.014364 | 2.1163 | 25.7698 | 1.4933 | 122.0616 | 121.9966 | 121.9511 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.074275 | 0.10419 | 2.2444 | 1.6214 | 1.5472 | 0.039249 | -0.00629 | 0.014392 | -122.0377 | 0.15212 | 0.067244 | 0.052852 | -121.93 | -121.8901 | 122.1898 | 122.1248 | 122.0793 | 25.898 | -122.0113 | 0.047856 | 0.15562 | 0.19545 | 0.21095 | -122.0712
3254.7031 | 121.9757 | -0.11902 | 121.9711 | 1.4211e-13 | -0.043453 | 0.0027137 | 0.067919 | -0.0086727 | 0.056101 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019399 | 0.031553 | 0.015005 | 2.1208 | 25.9071 | 1.5116 | 122.057 | 122.0012 | 121.9603 | -0.044742 | 0.033099 | 0.091933 | -0.06093 | -0.075739 | 0.027442 | 0.062694 | -0.1092 | 0.074277 | 0.085877 | 2.2399 | 1.6306 | 1.5563 | 0.030094 | -0.010865 | 0.009816 | -122.0469 | 0.15212 | 0.058089 | 0.048273 | -121.9437 | -121.9084 | 122.176 | 122.1202 | 122.0793 | 26.0262 | -122.0159 | 0.04328 | 0.14646 | 0.18171 | 0.21095 | -122.0803
3256.4219 | 122.049 | -0.086975 | 121.9711 | 1.4211e-13 | -0.043453 | 0.0027137 | 0.067705 | -0.0086727 | 0.056101 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018972 | 0.031339 | 0.014578 | 2.1575 | 26.0033 | 1.5207 | 122.0616 | 122.0058 | 121.9648 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.10462 | 0.037654 | 0.090456 | 2.2444 | 1.6077 | 1.5701 | 0.034673 | -0.006287 | -0.017649 | -122.056 | 0.11092 | 0.026045 | 0.043694 | -121.9437 | -121.9039 | 122.1486 | 122.0928 | 122.0518 | 26.0903 | -122.0205 | 0.002079 | 0.11442 | 0.15425 | 0.16517 | -122.0758
3258.1875 | 122.0718 | -0.073242 | 121.9528 | 1.4211e-13 | -0.043239 | 0.0029273 | 0.067919 | -0.0082453 | 0.056101 | 0.012972 | -0.0040121 | -0.0016987 | 0.018758 | 0.031126 | 0.014364 | 2.1804 | 26.0994 | 1.5574 | 122.057 | 121.9966 | 121.9603 | -0.049321 | 0.023941 | 0.087354 | -0.056351 | -0.084896 | 0.0366 | 0.071851 | -0.1092 | 0.023921 | 0.10419 | 2.2536 | 1.6306 | 1.6067 | 0.043826 | 0.007445 | -0.035961 | -122.0377 | 0.097183 | 0.016891 | 0.052852 | -121.9162 | -121.881 | 122.1302 | 122.0699 | 122.0335 | 26.1727 | -122.0021 | -0.011654 | 0.10984 | 0.14509 | 0.1606 | -122.062
3259.9531 | 121.9757 | -0.11444 | 121.9849 | 1.4211e-13 | -0.043666 | 0.0025001 | 0.067492 | -0.0086727 | 0.055888 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018972 | 0.031126 | 0.014364 | 2.2078 | 26.2093 | 1.5711 | 122.0616 | 122.0012 | 121.9557 | -0.053899 | 0.019362 | 0.082776 | -0.070087 | -0.075739 | 0.022864 | 0.067272 | -0.11378 | 0.060542 | 0.076723 | 2.3223 | 1.6855 | 1.625 | 0.016361 | -0.029177 | 0.000659 | -122.0606 | 0.1338 | 0.044354 | 0.043695 | -121.962 | -121.9176 | 122.176 | 122.1157 | 122.0701 | 26.3238 | -122.0388 | 0.038702 | 0.13731 | 0.18171 | 0.19722 | -122.0986
3261.6562 | 122.1085 | -0.068665 | 121.9208 | 1.4211e-13 | -0.043453 | 0.0025001 | 0.067278 | -0.0086727 | 0.055888 | -0.0022892 | -0.0044395 | -0.0012713 | 0.018758 | 0.031339 | 0.014791 | 2.2261 | 26.3375 | 1.5986 | 122.057 | 122.0058 | 121.9603 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11378 | 0.023923 | 0.13623 | 2.2948 | 1.6672 | 1.6433 | 0.085027 | 0.039489 | -0.045117 | -122.0011 | 0.097185 | 0.007735 | 0.052852 | -121.8888 | -121.8535 | 122.1257 | 122.0745 | 122.0289 | 26.4062 | -121.9655 | -0.011653 | 0.10069 | 0.13594 | 0.15144 | -122.0346
3263.4219 | 122.081 | -0.073242 | 121.9299 | 1.4211e-13 | -0.043239 | 0.0027137 | 0.067492 | -0.0084589 | 0.055888 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018972 | 0.031126 | 0.014578 | 2.2582 | 26.4199 | 1.6169 | 122.057 | 122.0104 | 121.9557 | -0.044742 | 0.023941 | 0.082776 | -0.070087 | -0.080318 | 0.027442 | 0.067272 | -0.12294 | 0.0285 | 0.12708 | 2.3314 | 1.6901 | 1.6616 | 0.08045 | 0.025754 | -0.049697 | -122.0102 | 0.097183 | 0.003155 | 0.052852 | -121.9025 | -121.8627 | 122.1302 | 122.0836 | 122.0289 | 26.4932 | -121.9747 | -0.007076 | 0.10068 | 0.14051 | 0.15602 | -122.0529
3265.125 | 122.0718 | -0.068665 | 121.9254 | 1.4211e-13 | -0.043025 | 0.0029273 | 0.067278 | -0.0086727 | 0.056742 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019186 | 0.031553 | 0.014578 | 2.2765 | 26.4978 | 1.6398 | 122.0662 | 122.0104 | 121.9511 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.11378 | 0.014766 | 0.14081 | 2.3452 | 1.7084 | 1.6937 | 0.085028 | 0.025753 | -0.045117 | -121.9965 | 0.097185 | 0.007735 | 0.052852 | -121.8888 | -121.8535 | 122.1348 | 122.079 | 122.0198 | 26.5664 | -121.9793 | -0.002496 | 0.10526 | 0.14052 | 0.14686 | -122.0391
3266.8906 | 121.9986 | -0.11902 | 121.994 | 1.4211e-13 | -0.043025 | 0.0031411 | 0.067705 | -0.0082453 | 0.056101 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.031339 | 0.014791 | 2.2948 | 26.5665 | 1.6627 | 122.0616 | 122.015 | 121.9648 | -0.044742 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.1092 | 0.074277 | 0.067567 | 2.4138 | 1.7817 | 1.7074 | 0.020942 | -0.029176 | 0.009816 | -122.0698 | 0.14296 | 0.05351 | 0.043694 | -121.9666 | -121.9267 | 122.1806 | 122.134 | 122.0839 | 26.6855 | -122.0388 | 0.04328 | 0.14646 | 0.18629 | 0.19722 | -122.1032
3268.5938 | 122.081 | -0.07782 | 121.9345 | 1.4211e-13 | -0.043239 | 0.0029273 | 0.067064 | -0.0084589 | 0.056101 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 2.3314 | 26.6397 | 1.6764 | 122.0616 | 122.0058 | 121.9648 | -0.053899 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.071851 | -0.10462 | 0.023921 | 0.12708 | 2.4093 | 1.7542 | 1.7303 | 0.071294 | 0.030334 | -0.026804 | -122.0148 | 0.10634 | 0.012311 | 0.039115 | -121.9071 | -121.8627 | 122.1394 | 122.0836 | 122.0427 | 26.7175 | -121.9884 | -0.002498 | 0.10526 | 0.14967 | 0.15602 | -122.0391
3270.3594 | 122.0581 | -0.073242 | 121.9803 | 1.4211e-13 | -0.043453 | 0.0031411 | 0.067705 | -0.0084589 | 0.055888 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031126 | 0.014578 | 2.3635 | 26.7817 | 1.7039 | 122.0662 | 122.0104 | 121.9648 | -0.053899 | 0.023941 | 0.082776 | -0.051772 | -0.080318 | 0.032021 | 0.071851 | -0.1092 | 0.019343 | 0.085878 | 2.4367 | 1.7771 | 1.7578 | 0.030096 | -0.015443 | -0.035961 | -122.0606 | 0.097183 | 0.02147 | 0.057431 | -121.9483 | -121.9084 | 122.1394 | 122.0836 | 122.0381 | 26.8549 | -122.0342 | -0.007076 | 0.10526 | 0.14509 | 0.15602 | -122.0895
3272.1406 | 121.9711 | -0.10529 | 121.9666 | 1.4211e-13 | -0.043025 | 0.0031411 | 0.067492 | -0.0084589 | 0.055888 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.014791 | 2.391 | 26.8366 | 1.7313 | 122.0707 | 122.0012 | 121.9557 | -0.049321 | 0.023941 | 0.082776 | -0.051772 | -0.080318 | 0.022864 | 0.071851 | -0.11378 | 0.055965 | 0.10419 | 2.4963 | 1.8366 | 1.7807 | 0.034671 | -0.010867 | -0.008496 | -122.0469 | 0.12923 | 0.053514 | 0.06201 | -121.9437 | -121.8947 | 122.176 | 122.1065 | 122.061 | 26.9419 | -122.0159 | 0.024968 | 0.12815 | 0.17714 | 0.18806 | -122.0803
3273.8594 | 121.994 | -0.11444 | 121.9849 | 1.4211e-13 | -0.043025 | 0.0029273 | 0.067919 | -0.0086727 | 0.056529 | 0.0053413 | -0.0040121 | -0.0019123 | 0.018972 | 0.031126 | 0.014791 | 2.423 | 26.9282 | 1.7405 | 122.0662 | 122.0104 | 121.9603 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.0366 | 0.067272 | -0.1092 | 0.060542 | 0.081301 | 2.5375 | 1.8549 | 1.7944 | 0.025519 | -0.024598 | 0.005238 | -122.0652 | 0.14296 | 0.053511 | 0.048273 | -121.9483 | -121.9176 | 122.1806 | 122.1248 | 122.0747 | 27.0426 | -122.0388 | 0.034123 | 0.15104 | 0.18171 | 0.19264 | -122.0941
3275.625 | 122.0993 | -0.059509 | 121.9482 | 1.4211e-13 | -0.043239 | 0.0025001 | 0.067492 | -0.0084589 | 0.056742 | -0.0022892 | -0.0046531 | -0.0016987 | 0.018972 | 0.031339 | 0.014578 | 2.4459 | 27.0609 | 1.7725 | 122.0662 | 122.0104 | 121.9648 | -0.053899 | 0.019362 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.00561 | 0.11792 | 2.5054 | 1.8321 | 1.8264 | 0.06214 | 0.016601 | -0.054273 | -122.0286 | 0.078871 | -0.006 | 0.048273 | -121.9208 | -121.881 | 122.1257 | 122.0699 | 122.0244 | 27.1205 | -122.0021 | -0.020809 | 0.086951 | 0.12678 | 0.13771 | -122.062
3277.3906 | 121.9803 | -0.11444 | 121.9894 | 1.4211e-13 | -0.042811 | 0.0029273 | 0.067705 | -0.0082453 | 0.056315 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.01415 | 2.4734 | 27.1937 | 1.7954 | 122.057 | 122.0104 | 121.9648 | -0.053899 | 0.023941 | 0.091933 | -0.06093 | -0.089475 | 0.022864 | 0.067272 | -0.11378 | 0.060542 | 0.067566 | 2.5878 | 1.9099 | 1.8493 | 0.020941 | -0.024598 | 0.000659 | -122.0789 | 0.13838 | 0.053511 | 0.052852 | -121.9666 | -121.9222 | 122.1714 | 122.1248 | 122.0793 | 27.3082 | -122.0433 | 0.024966 | 0.13731 | 0.18171 | 0.20637 | -122.1032
3279.1562 | 121.9894 | -0.10071 | 121.9849 | 1.4211e-13 | -0.042811 | 0.0027137 | 0.067919 | -0.0084589 | 0.056315 | -0.0022892 | -0.0046531 | -0.0014849 | 0.018972 | 0.031126 | 0.014578 | 2.51 | 27.3494 | 1.8183 | 122.0616 | 122.015 | 121.9648 | -0.049321 | 0.033099 | 0.087354 | -0.06093 | -0.075739 | 0.022864 | 0.067272 | -0.11836 | 0.051387 | 0.076723 | 2.6107 | 1.919 | 1.8676 | 0.030098 | -0.02002 | -0.017653 | -122.0606 | 0.13381 | 0.039778 | 0.057431 | -121.962 | -121.9176 | 122.1623 | 122.1157 | 122.0656 | 27.4501 | -122.0342 | 0.024969 | 0.12357 | 0.16798 | 0.18806 | -122.1032
3280.8594 | 121.994 | -0.11444 | 121.994 | 1.4211e-13 | -0.042598 | 0.0031411 | 0.067705 | -0.0080317 | 0.056101 | 0.0053413 | -0.0042257 | -0.0014849 | 0.019186 | 0.031339 | 0.014791 | 2.5466 | 27.5097 | 1.8504 | 122.0662 | 122.0058 | 121.9648 | -0.044742 | 0.02852 | 0.078197 | -0.056351 | -0.071161 | 0.032021 | 0.071851 | -0.11836 | 0.069699 | 0.072145 | 2.6611 | 1.9648 | 1.8951 | 0.011784 | -0.029176 | -0.00392 | -122.0652 | 0.14296 | 0.05809 | 0.06201 | -121.962 | -121.9222 | 122.1806 | 122.1202 | 122.0793 | 27.6241 | -122.0388 | 0.04328 | 0.14646 | 0.18629 | 0.19264 | -122.1124
3282.625 | 122.1176 | -0.082397 | 121.9574 | 1.4211e-13 | -0.042811 | 0.0031411 | 0.067705 | -0.0082453 | 0.056315 | -0.01755 | -0.0046531 | -0.0014849 | 0.019186 | 0.031126 | 0.014791 | 2.5741 | 27.6882 | 1.8733 | 122.0753 | 122.0104 | 121.9694 | -0.053899 | 0.023941 | 0.073618 | -0.056351 | -0.071161 | 0.022864 | 0.071851 | -0.1092 | 0.028498 | 0.11792 | 2.6565 | 1.9557 | 1.9272 | 0.052985 | 0.012025 | -0.026806 | -122.0286 | 0.10634 | 0.026046 | 0.052852 | -121.9345 | -121.8855 | 122.1577 | 122.0928 | 122.0518 | 27.7706 | -122.0113 | 0.011236 | 0.10526 | 0.15425 | 0.15602 | -122.0666
3284.4062 | 122.1176 | -0.054932 | 121.9482 | 1.4211e-13 | -0.043239 | 0.0029273 | 0.067919 | -0.0080317 | 0.056529 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018972 | 0.031339 | 0.014578 | 2.6153 | 27.9263 | 1.9007 | 122.0662 | 122.0104 | 121.9694 | -0.044742 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.067272 | -0.1092 | 0.01019 | 0.11792 | 2.6702 | 1.9557 | 1.9455 | 0.06214 | 0.02118 | -0.054271 | -122.0286 | 0.074294 | -0.005998 | 0.048273 | -121.9254 | -121.881 | 122.1211 | 122.0653 | 122.0244 | 27.9812 | -121.993 | -0.025386 | 0.077796 | 0.1222 | 0.13771 | -122.0574
3286.125 | 122.0581 | -0.09613 | 121.9482 | 1.4211e-13 | -0.042811 | 0.0031411 | 0.067919 | -0.0082453 | 0.056742 | -0.0099192 | -0.0042257 | -0.0021259 | 0.018972 | 0.031339 | 0.014791 | 2.6519 | 28.1186 | 1.9236 | 122.0616 | 122.0104 | 121.974 | -0.044742 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.018285 | 0.062694 | -0.11836 | 0.051388 | 0.11334 | 2.7481 | 2.0198 | 1.9684 | 0.06214 | 0.025758 | -0.022231 | -122.0331 | 0.12007 | 0.030621 | 0.052852 | -121.93 | -121.8855 | 122.1577 | 122.1065 | 122.0701 | 28.2147 | -121.993 | 0.011234 | 0.11441 | 0.15882 | 0.17891 | -122.0666
3287.8906 | 122.081 | -0.068665 | 121.9391 | 1.4211e-13 | -0.042811 | 0.0029273 | 0.068133 | -0.0082453 | 0.056529 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.030912 | 0.014578 | 2.684 | 28.3201 | 1.9648 | 122.0662 | 122.0104 | 121.9694 | -0.058478 | 0.02852 | 0.082776 | -0.06093 | -0.084896 | 0.041178 | 0.071851 | -0.12294 | 0.010187 | 0.12708 | 2.7526 | 2.0335 | 2.0233 | 0.071295 | 0.030335 | -0.054274 | -122.024 | 0.097185 | 0.007735 | 0.062009 | -121.8979 | -121.8672 | 122.1348 | 122.079 | 122.0381 | 28.3887 | -121.9976 | -0.016231 | 0.10984 | 0.14052 | 0.15144 | -122.062
3289.5938 | 122.0718 | -0.064087 | 121.9254 | 1.4211e-13 | -0.042811 | 0.0031411 | 0.067705 | -0.0084589 | 0.056529 | -0.01755 | -0.0040121 | -0.0014849 | 0.019186 | 0.031339 | 0.014578 | 2.716 | 28.5261 | 1.9786 | 122.0616 | 122.0104 | 121.9648 | -0.049321 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.032021 | 0.067272 | -0.1092 | 0.014766 | 0.13623 | 2.7801 | 2.0427 | 2.0279 | 0.085028 | 0.039489 | -0.045116 | -122.0057 | 0.092607 | 0.007736 | 0.052852 | -121.8933 | -121.8581 | 122.1257 | 122.0745 | 122.0289 | 28.5902 | -121.9747 | -0.016231 | 0.096108 | 0.13136 | 0.14228 | -122.0346
3291.3594 | 122.0215 | -0.10529 | 121.9849 | 1.4211e-13 | -0.042384 | 0.0031411 | 0.068133 | -0.0084589 | 0.056742 | -0.0022892 | -0.0042257 | -0.0012713 | 0.018972 | 0.031339 | 0.014364 | 2.7435 | 28.7184 | 2.006 | 122.0753 | 122.015 | 121.9648 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.032021 | 0.067272 | -0.11378 | 0.055965 | 0.090458 | 2.8488 | 2.1113 | 2.0554 | 0.030098 | -0.02002 | -0.008496 | -122.0606 | 0.13381 | 0.044356 | 0.052852 | -121.9528 | -121.9176 | 122.1806 | 122.1202 | 122.0701 | 28.8237 | -122.0342 | 0.029547 | 0.13731 | 0.17256 | 0.18348 | -122.0986
3293.1406 | 122.0032 | -0.1236 | 121.994 | 1.4211e-13 | -0.042384 | 0.0031411 | 0.068133 | -0.0084589 | 0.056529 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019186 | 0.031553 | 0.014364 | 2.7893 | 28.9107 | 2.0289 | 122.057 | 122.015 | 121.9694 | -0.049321 | 0.02852 | 0.078197 | -0.065509 | -0.075739 | 0.032021 | 0.067272 | -0.12294 | 0.074275 | 0.062988 | 2.9129 | 2.1525 | 2.0782 | 0.020942 | -0.024597 | 0.000657 | -122.0698 | 0.15212 | 0.058087 | 0.05743 | -121.962 | -121.9267 | 122.1806 | 122.1386 | 122.093 | 29.0343 | -122.0433 | 0.047857 | 0.15562 | 0.19087 | 0.20179 | -122.117
3294.9062 | 122.1313 | -0.054932 | 121.9437 | 1.4211e-13 | -0.042598 | 0.0031411 | 0.067705 | -0.0084589 | 0.056742 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018972 | 0.031126 | 0.014578 | 2.8168 | 29.1534 | 2.0656 | 122.0662 | 122.015 | 121.9694 | -0.053899 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.071851 | -0.11378 | 0.001033 | 0.1225 | 2.8717 | 2.1205 | 2.1195 | 0.071296 | 0.025757 | -0.05885 | -122.024 | 0.074294 | -0.001419 | 0.057431 | -121.9162 | -121.8718 | 122.1211 | 122.0699 | 122.0244 | 29.2083 | -121.9976 | -0.025386 | 0.082374 | 0.12678 | 0.13313 | -122.0574
3296.6094 | 122.113 | -0.082397 | 121.9345 | 1.4211e-13 | -0.042384 | 0.0033547 | 0.068133 | -0.0082453 | 0.056956 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.031553 | 0.014364 | 2.8625 | 29.3869 | 2.1022 | 122.0662 | 122.0104 | 121.9648 | -0.044742 | 0.019362 | 0.087354 | -0.06093 | -0.080318 | 0.022864 | 0.071851 | -0.11836 | 0.037655 | 0.13165 | 2.9449 | 2.1846 | 2.1469 | 0.075873 | 0.030334 | -0.035964 | -122.0148 | 0.10176 | 0.021467 | 0.057431 | -121.9116 | -121.8627 | 122.1486 | 122.0928 | 122.0472 | 29.4693 | -121.9793 | 0.002079 | 0.10526 | 0.15425 | 0.16975 | -122.0529
3298.375 | 122.0947 | -0.082397 | 121.9528 | 1.4211e-13 | -0.042598 | 0.0031411 | 0.068133 | -0.0078179 | 0.056956 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018972 | 0.031339 | 0.014364 | 2.9037 | 29.625 | 2.1342 | 122.0662 | 122.015 | 121.9648 | -0.044742 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.037655 | 0.11334 | 2.9861 | 2.2166 | 2.179 | 0.062141 | 0.012023 | -0.035964 | -122.0331 | 0.10634 | 0.016888 | 0.052852 | -121.9208 | -121.8855 | 122.1486 | 122.0974 | 122.0472 | 29.7074 | -121.9976 | 0.002079 | 0.11442 | 0.14967 | 0.16517 | -122.0712
3300.0781 | 122.1039 | -0.059509 | 121.9391 | 1.4211e-13 | -0.042598 | 0.0031411 | 0.067919 | -0.0080317 | 0.056956 | -0.01755 | -0.0042257 | -0.0014849 | 0.018972 | 0.031553 | 0.014364 | 2.945 | 29.8676 | 2.1709 | 122.0662 | 122.015 | 121.9694 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.018285 | 0.067272 | -0.1092 | 0.010188 | 0.12708 | 3.0045 | 2.2304 | 2.2202 | 0.075874 | 0.030335 | -0.049694 | -122.0148 | 0.08345 | 0.003158 | 0.052852 | -121.9208 | -121.8718 | 122.1257 | 122.0745 | 122.0289 | 29.9271 | -121.9884 | -0.01623 | 0.077794 | 0.12678 | 0.14228 | -122.0483
3301.8438 | 122.0261 | -0.10529 | 121.9528 | 1.4211e-13 | -0.042811 | 0.0029273 | 0.067919 | -0.0082453 | 0.056742 | -0.0099192 | -0.0040121 | -0.0016987 | 0.019186 | 0.031553 | 0.014364 | 2.9724 | 30.1423 | 2.1983 | 122.0662 | 122.0104 | 121.9648 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.055965 | 0.11334 | 3.0777 | 2.3036 | 2.2476 | 0.057562 | 0.012023 | -0.008496 | -122.0331 | 0.12923 | 0.048935 | 0.057431 | -121.93 | -121.8855 | 122.1715 | 122.1157 | 122.0701 | 30.2476 | -122.0021 | 0.024968 | 0.12815 | 0.17256 | 0.18806 | -122.0666
3303.6094 | 122.1405 | -0.050354 | 121.9437 | 1.4211e-13 | -0.04217 | 0.0031411 | 0.068346 | -0.0080317 | 0.056742 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.014578 | 3.0228 | 30.4216 | 2.2166 | 122.0707 | 122.015 | 121.9694 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.081008 | -0.1092 | -0.003545 | 0.12708 | 3.0731 | 2.267 | 2.2705 | 0.071296 | 0.025757 | -0.058849 | -122.0194 | 0.074295 | -0.005997 | 0.052852 | -121.9162 | -121.8627 | 122.1211 | 122.0653 | 122.0198 | 30.472 | -121.9976 | -0.025385 | 0.077796 | 0.13136 | 0.13313 | -122.0529
3305.3594 | 121.9986 | -0.13275 | 122.0032 | 1.4211e-13 | -0.042384 | 0.0027137 | 0.067919 | -0.0084589 | 0.056956 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.014364 | 3.0503 | 30.7284 | 2.2578 | 122.0707 | 122.0195 | 121.974 | -0.049321 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.11836 | 0.08343 | 0.067569 | 3.183 | 2.3906 | 2.3072 | 0.016366 | -0.029174 | 0.01439 | -122.0789 | 0.15211 | 0.071821 | 0.057431 | -121.9666 | -121.9267 | 122.2035 | 122.1523 | 122.1068 | 30.8612 | -122.0525 | 0.057012 | 0.16935 | 0.20918 | 0.21553 | -122.1215
3307.0625 | 122.0856 | -0.073242 | 121.962 | 1.4211e-13 | -0.042384 | 0.0031411 | 0.067919 | -0.0078179 | 0.05717 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018972 | 0.031553 | 0.014791 | 3.0869 | 31.0123 | 2.2853 | 122.0753 | 122.0195 | 121.974 | -0.053899 | 0.033099 | 0.082776 | -0.051772 | -0.084896 | 0.0366 | 0.07643 | -0.11378 | 0.019343 | 0.11335 | 3.1601 | 2.3586 | 2.3392 | 0.057565 | 0.012025 | -0.04054 | -122.0469 | 0.10634 | 0.02147 | 0.06201 | -121.9254 | -121.8855 | 122.1486 | 122.0928 | 122.0472 | 31.0855 | -122.0159 | -0.011654 | 0.10984 | 0.14967 | 0.15602 | -122.0758
3308.8438 | 122.1176 | -0.064087 | 121.9437 | 1.4211e-13 | -0.042384 | 0.0029273 | 0.067705 | -0.0080317 | 0.05717 | -0.01755 | -0.0046531 | -0.0014849 | 0.018972 | 0.030912 | 0.014578 | 3.1235 | 31.3236 | 2.3036 | 122.0662 | 122.015 | 121.974 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.019345 | 0.1225 | 3.1876 | 2.3677 | 2.3484 | 0.071296 | 0.030335 | -0.049695 | -122.024 | 0.092607 | 0.003157 | 0.052852 | -121.9162 | -121.881 | 122.1303 | 122.079 | 122.0381 | 31.3877 | -121.9884 | -0.016231 | 0.091529 | 0.12678 | 0.14686 | -122.0574
3310.5312 | 122.1359 | -0.045776 | 121.9345 | 1.4211e-13 | -0.042598 | 0.0029273 | 0.067919 | -0.0078179 | 0.057383 | 0.0053413 | -0.0042257 | -0.0016987 | 0.018972 | 0.031339 | 0.014578 | 3.1601 | 31.7082 | 2.3586 | 122.0707 | 122.0195 | 121.974 | -0.058478 | 0.02852 | 0.087354 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | -0.012702 | 0.13623 | 3.2059 | 2.4043 | 2.417 | 0.085031 | 0.039491 | -0.063427 | -122.0148 | 0.074296 | -0.015154 | 0.048273 | -121.9071 | -121.8718 | 122.1165 | 122.0653 | 122.0198 | 31.754 | -121.993 | -0.034542 | 0.073218 | 0.10847 | 0.13313 | -122.0437
3312.2969 | 122.0306 | -0.086975 | 121.9391 | 1.4211e-13 | -0.04217 | 0.0029273 | 0.067919 | -0.0078179 | 0.056956 | -0.0099192 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.015005 | 3.2013 | 32.0333 | 2.3998 | 122.0662 | 122.015 | 121.9694 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.028497 | 0.12708 | 3.2883 | 2.4867 | 2.4582 | 0.075874 | 0.030335 | -0.026807 | -122.0148 | 0.1155 | 0.026045 | 0.052852 | -121.9116 | -121.8718 | 122.1531 | 122.1019 | 122.0564 | 32.1203 | -121.9976 | 0.011236 | 0.11442 | 0.15425 | 0.16517 | -122.0529
3314 | 122.0627 | -0.073242 | 121.9666 | 1.4211e-13 | -0.04217 | 0.0031411 | 0.067919 | -0.0080317 | 0.05717 | -0.02518 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.014364 | 3.2288 | 32.3538 | 2.4272 | 122.0662 | 122.0104 | 121.9694 | -0.040163 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11836 | 0.033079 | 0.099611 | 3.3021 | 2.5005 | 2.4674 | 0.043829 | 0.002869 | -0.045119 | -122.0469 | 0.10176 | 0.012312 | 0.057431 | -121.9391 | -121.9039 | 122.1394 | 122.0836 | 122.0427 | 32.4271 | -122.0067 | -0.007076 | 0.10068 | 0.13594 | 0.15602 | -122.0849
3315.7656 | 122.1313 | -0.041199 | 121.9345 | 1.4211e-13 | -0.042384 | 0.0029273 | 0.067919 | -0.0078179 | 0.05717 | -0.0099192 | -0.0040121 | -0.0014849 | 0.018972 | 0.031553 | 0.014791 | 3.27 | 32.6789 | 2.4684 | 122.0753 | 122.0104 | 121.974 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.067272 | -0.1092 | -0.008122 | 0.14081 | 3.3112 | 2.5096 | 2.5178 | 0.075873 | 0.039491 | -0.068004 | -122.0057 | 0.069719 | -0.019731 | 0.048273 | -121.9025 | -121.8672 | 122.1165 | 122.0516 | 122.0152 | 32.7201 | -121.9838 | -0.029962 | 0.07322 | 0.10847 | 0.12398 | -122.0437
3317.4844 | 121.9894 | -0.091553 | 121.9757 | 1.4211e-13 | -0.04217 | 0.0033547 | 0.067919 | -0.0080317 | 0.05717 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031767 | 0.014578 | 3.3158 | 32.9811 | 2.5051 | 122.0753 | 122.0287 | 121.9694 | -0.058478 | 0.033099 | 0.082776 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.033075 | 0.099613 | 3.4074 | 2.5966 | 2.5635 | 0.05299 | -0.006286 | -0.022229 | -122.0514 | 0.12465 | 0.026044 | 0.048273 | -121.9483 | -121.9084 | 122.1669 | 122.1203 | 122.061 | 33.0726 | -122.0342 | 0.015814 | 0.11899 | 0.15882 | 0.17433 | -122.0895
3319.25 | 122.1085 | -0.082397 | 121.9437 | 1.4211e-13 | -0.041957 | 0.0029273 | 0.068346 | -0.0080317 | 0.057597 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018972 | 0.031339 | 0.01415 | 3.357 | 33.3428 | 2.5417 | 122.0662 | 122.0195 | 121.974 | -0.058478 | 0.019362 | 0.082776 | -0.070087 | -0.080318 | 0.032021 | 0.067272 | -0.1092 | 0.023919 | 0.1225 | 3.4394 | 2.6241 | 2.6002 | 0.075875 | 0.030335 | -0.026806 | -122.024 | 0.10176 | 0.01231 | 0.039116 | -121.9116 | -121.8764 | 122.1486 | 122.1019 | 122.0564 | 33.4252 | -122.0021 | 0.002079 | 0.11442 | 0.14967 | 0.16517 | -122.0529
3320.9531 | 122.0718 | -0.10071 | 121.9482 | 1.4211e-13 | -0.041743 | 0.0029273 | 0.068133 | -0.0078179 | 0.05717 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.014791 | 3.3982 | 33.7091 | 2.5783 | 122.0707 | 122.015 | 121.974 | -0.053899 | 0.02852 | 0.087354 | -0.056351 | -0.080318 | 0.022864 | 0.067272 | -0.11378 | 0.046809 | 0.1225 | 3.4989 | 2.679 | 2.6322 | 0.066719 | 0.025758 | -0.013074 | -122.0286 | 0.12923 | 0.044357 | 0.057431 | -121.9254 | -121.881 | 122.1715 | 122.1157 | 122.0747 | 33.8098 | -122.0021 | 0.02039 | 0.12357 | 0.16798 | 0.18806 | -122.062
3322.7188 | 122.081 | -0.073242 | 121.9437 | 1.4211e-13 | -0.041957 | 0.0031411 | 0.067919 | -0.0076043 | 0.057383 | -0.01755 | -0.0046531 | -0.0014849 | 0.018972 | 0.031339 | 0.014791 | 3.4394 | 34.0616 | 2.6104 | 122.0753 | 122.0195 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.022864 | 0.067272 | -0.11836 | 0.023921 | 0.13166 | 3.5127 | 2.6836 | 2.6597 | 0.075875 | 0.030335 | -0.045119 | -122.0194 | 0.097183 | 0.012312 | 0.057431 | -121.9208 | -121.8764 | 122.1486 | 122.0928 | 122.0472 | 34.1349 | -121.993 | -0.002497 | 0.096106 | 0.14051 | 0.15602 | -122.062
3324.4844 | 122.0947 | -0.07782 | 121.9391 | 1.4211e-13 | -0.041743 | 0.0031411 | 0.067919 | -0.0078179 | 0.057383 | 0.012972 | -0.0042257 | -0.0016987 | 0.019399 | 0.031339 | 0.014364 | 3.476 | 34.3455 | 2.6607 | 122.0616 | 122.0241 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.032021 | 0.067272 | -0.11378 | 0.028499 | 0.1225 | 3.5539 | 2.7385 | 2.71 | 0.085032 | 0.034913 | -0.035962 | -122.024 | 0.10176 | 0.01689 | 0.052852 | -121.9071 | -121.8718 | 122.1394 | 122.1019 | 122.0518 | 34.4233 | -121.9884 | -0.007076 | 0.10984 | 0.14509 | 0.1606 | -122.0529
3326.1875 | 122.0123 | -0.086975 | 121.9757 | 1.4211e-13 | -0.041743 | 0.0029273 | 0.06856 | -0.0078179 | 0.057597 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.014364 | 3.5172 | 34.6614 | 2.6882 | 122.0662 | 122.015 | 121.974 | -0.058478 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.071851 | -0.11836 | 0.028497 | 0.090456 | 3.6042 | 2.7752 | 2.7467 | 0.039253 | -0.001708 | -0.031386 | -122.056 | 0.1155 | 0.026045 | 0.057431 | -121.9483 | -121.9039 | 122.1531 | 122.1019 | 122.061 | 34.7484 | -122.0342 | 0.006657 | 0.11442 | 0.15883 | 0.16517 | -122.0941
3327.9688 | 121.9986 | -0.11902 | 121.9894 | 1.4211e-13 | -0.041743 | 0.0031411 | 0.068346 | -0.0078179 | 0.057597 | -0.0022892 | -0.0040121 | -0.0014849 | 0.019186 | 0.031126 | 0.014364 | 3.5722 | 35.0369 | 2.7248 | 122.0707 | 122.015 | 121.974 | -0.049321 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.032021 | 0.067272 | -0.1092 | 0.069698 | 0.081302 | 3.6912 | 2.8438 | 2.7741 | 0.02552 | -0.015441 | 0.009816 | -122.0652 | 0.13838 | 0.062668 | 0.052852 | -121.9574 | -121.9222 | 122.1898 | 122.134 | 122.093 | 35.1559 | -122.0388 | 0.04328 | 0.15104 | 0.18629 | 0.20637 | -122.0986
3329.7344 | 122.0123 | -0.10529 | 121.9757 | 1.4211e-13 | -0.041529 | 0.0033547 | 0.068133 | -0.0076043 | 0.057811 | -0.01755 | -0.0040121 | -0.0019123 | 0.018758 | 0.031339 | 0.01415 | 3.5905 | 35.2475 | 2.766 | 122.0753 | 122.015 | 121.974 | -0.053899 | 0.019362 | 0.087354 | -0.06093 | -0.080318 | 0.032021 | 0.071851 | -0.11836 | 0.051387 | 0.099613 | 3.6958 | 2.8713 | 2.8199 | 0.039253 | -0.001708 | -0.013075 | -122.056 | 0.12465 | 0.044356 | 0.057431 | -121.9437 | -121.9039 | 122.1806 | 122.1202 | 122.0793 | 35.3528 | -122.0296 | 0.024968 | 0.13731 | 0.17714 | 0.19264 | -122.0941
3331.4375 | 121.9986 | -0.10071 | 121.9803 | 1.4211e-13 | -0.041957 | 0.0031411 | 0.06856 | -0.0076043 | 0.057597 | -0.01755 | -0.0044395 | -0.0019123 | 0.018758 | 0.031339 | 0.014578 | 3.6546 | 35.6825 | 2.7981 | 122.0753 | 122.0195 | 121.9694 | -0.049321 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.071851 | -0.11378 | 0.051387 | 0.095035 | 3.7553 | 2.8988 | 2.8474 | 0.039254 | -0.010864 | -0.013074 | -122.0606 | 0.12923 | 0.044357 | 0.057431 | -121.9528 | -121.9084 | 122.176 | 122.1202 | 122.0701 | 35.7832 | -122.0296 | 0.02039 | 0.12815 | 0.17256 | 0.18348 | -122.0941
3333.2031 | 122.0718 | -0.082397 | 121.9574 | 1.4211e-13 | -0.041529 | 0.0031411 | 0.068346 | -0.0080317 | 0.057811 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.031339 | 0.014578 | 3.6867 | 36.0396 | 2.8393 | 122.0707 | 122.0195 | 121.9694 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.071851 | -0.11836 | 0.028498 | 0.11335 | 3.769 | 2.9217 | 2.8932 | 0.062143 | 0.012025 | -0.035964 | -122.0377 | 0.10634 | 0.021467 | 0.057431 | -121.93 | -121.8855 | 122.1531 | 122.1019 | 122.0518 | 36.122 | -122.0113 | 0.002079 | 0.10984 | 0.15425 | 0.16059 | -122.0758
3334.9688 | 121.9986 | -0.1236 | 121.9986 | 1.4211e-13 | -0.041743 | 0.0033547 | 0.068133 | -0.0076043 | 0.057597 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018758 | 0.031339 | 0.014364 | 3.7324 | 36.3235 | 2.8668 | 122.0707 | 122.015 | 121.9694 | -0.044742 | 0.019362 | 0.082776 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11836 | 0.078854 | 0.072147 | 3.856 | 2.9903 | 2.9115 | 0.016365 | -0.029174 | 0.005235 | -122.0835 | 0.14296 | 0.062666 | 0.057431 | -121.9712 | -121.9313 | 122.1943 | 122.1386 | 122.093 | 36.4471 | -122.0433 | 0.0387 | 0.15104 | 0.19087 | 0.20637 | -122.117
3336.75 | 122.113 | -0.082397 | 121.9528 | 1.4211e-13 | -0.041316 | 0.0029273 | 0.068346 | -0.0076043 | 0.058238 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.031126 | 0.014578 | 3.7782 | 36.6806 | 2.9125 | 122.0707 | 122.015 | 121.974 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.018285 | 0.067272 | -0.1092 | 0.028498 | 0.11792 | 3.8606 | 2.9949 | 2.9664 | 0.062141 | 0.02118 | -0.026806 | -122.0331 | 0.11092 | 0.021467 | 0.048273 | -121.9345 | -121.8855 | 122.1531 | 122.0974 | 122.0564 | 36.763 | -122.0067 | 0.002079 | 0.10068 | 0.14967 | 0.16517 | -122.062
3338.4688 | 122.049 | -0.09613 | 121.9528 | 1.4211e-13 | -0.041316 | 0.0031411 | 0.068346 | -0.0073907 | 0.057597 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.014791 | 3.824 | 37.0469 | 2.9354 | 122.0707 | 122.0241 | 121.9694 | -0.053899 | 0.02852 | 0.082776 | -0.056351 | -0.075739 | 0.022864 | 0.067272 | -0.11378 | 0.042231 | 0.11792 | 3.9201 | 3.0316 | 2.9893 | 0.071299 | 0.016602 | -0.017652 | -122.0286 | 0.12465 | 0.039779 | 0.057431 | -121.93 | -121.8855 | 122.1669 | 122.1202 | 122.0656 | 37.143 | -122.0067 | 0.020391 | 0.11899 | 0.1634 | 0.17891 | -122.0666
3340.2344 | 122.1222 | -0.045776 | 121.9254 | 1.4211e-13 | -0.041316 | 0.0033547 | 0.068346 | -0.0078179 | 0.058238 | 0.0053413 | -0.0044395 | -0.0019123 | 0.018972 | 0.031339 | 0.014364 | 3.8789 | 37.3949 | 2.9721 | 122.0753 | 122.0195 | 121.9786 | -0.053899 | 0.014784 | 0.082776 | -0.065509 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | -0.008123 | 0.14997 | 3.9247 | 3.0178 | 3.0259 | 0.094186 | 0.053225 | -0.072585 | -122.0057 | 0.06056 | -0.019733 | 0.052852 | -121.8933 | -121.8581 | 122.1211 | 122.0653 | 122.0244 | 37.4406 | -121.9793 | -0.034542 | 0.077797 | 0.11305 | 0.12855 | -122.0437
3341.9844 | 122.0993 | -0.064087 | 121.9574 | 1.4211e-13 | -0.041529 | 0.0031411 | 0.068346 | -0.0076043 | 0.058024 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.014791 | 3.9201 | 37.7611 | 3.0087 | 122.0707 | 122.015 | 121.9694 | -0.049321 | 0.023941 | 0.078197 | -0.070087 | -0.075739 | 0.027442 | 0.062694 | -0.11378 | 0.014766 | 0.11335 | 3.9842 | 3.0728 | 3.058 | 0.057564 | 0.012025 | -0.049695 | -122.0331 | 0.088028 | -0.006 | 0.043695 | -121.93 | -121.8947 | 122.1348 | 122.079 | 122.0335 | 37.8252 | -122.0067 | -0.011652 | 0.091529 | 0.12678 | 0.14228 | -122.0712
3343.75 | 121.962 | -0.11902 | 121.9986 | 1.4211e-13 | -0.041316 | 0.0033547 | 0.06856 | -0.0073907 | 0.058238 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018972 | 0.031126 | 0.014578 | 3.9659 | 38.1045 | 3.0453 | 122.0707 | 122.0241 | 121.9648 | -0.049321 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.07643 | -0.10462 | 0.069698 | 0.072147 | 4.085 | 3.1643 | 3.0946 | 0.025523 | -0.033753 | 0.014395 | -122.0789 | 0.14754 | 0.05351 | 0.039115 | -121.9712 | -121.9222 | 122.1898 | 122.1431 | 122.0839 | 38.2236 | -122.0479 | 0.038701 | 0.14646 | 0.19545 | 0.19722 | -122.1032
3345.5 | 122.0673 | -0.068665 | 121.9666 | 1.4211e-13 | -0.041316 | 0.0035685 | 0.068346 | -0.0073907 | 0.057811 | -0.01755 | -0.0042257 | -0.0014849 | 0.018758 | 0.031767 | 0.014364 | 4.0117 | 38.4662 | 3.0911 | 122.0662 | 122.0195 | 121.9694 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.032021 | 0.062694 | -0.10462 | 0.019344 | 0.099611 | 4.0804 | 3.1598 | 3.1404 | 0.052987 | 0.002869 | -0.035959 | -122.0469 | 0.092606 | 0.012314 | 0.048273 | -121.9345 | -121.9039 | 122.1348 | 122.0882 | 122.0381 | 38.5349 | -122.0159 | -0.011653 | 0.10069 | 0.13136 | 0.14686 | -122.0712
3347.2656 | 121.9894 | -0.10986 | 121.9757 | 1.4211e-13 | -0.040888 | 0.0033547 | 0.06856 | -0.0076043 | 0.058238 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.031339 | 0.01415 | 4.0529 | 38.9058 | 3.1186 | 122.0845 | 122.0195 | 121.9786 | -0.049321 | 0.033099 | 0.082776 | -0.056351 | -0.071161 | 0.022864 | 0.067272 | -0.11378 | 0.060542 | 0.10877 | 4.1628 | 3.2284 | 3.1679 | 0.043832 | 0.002871 | -0.003919 | -122.0469 | 0.14296 | 0.053512 | 0.057431 | -121.9528 | -121.9084 | 122.1943 | 122.1294 | 122.0884 | 39.0157 | -122.025 | 0.038702 | 0.13273 | 0.17713 | 0.19264 | -122.0895
3349.0312 | 121.994 | -0.10986 | 121.9803 | 1.4211e-13 | -0.041316 | 0.0031411 | 0.068133 | -0.0073907 | 0.058452 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018972 | 0.031339 | 0.014364 | 4.1079 | 39.2812 | 3.1506 | 122.0753 | 122.015 | 121.9786 | -0.049321 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.060542 | 0.095035 | 4.2177 | 3.2605 | 3.1999 | 0.034675 | -0.001707 | -0.003919 | -122.0606 | 0.12923 | 0.053512 | 0.057431 | -121.9528 | -121.9176 | 122.1852 | 122.1248 | 122.0884 | 39.3911 | -122.0296 | 0.029545 | 0.13731 | 0.17256 | 0.18806 | -122.0941
3350.7344 | 122.0078 | -0.09613 | 121.994 | 1.4211e-13 | -0.041102 | 0.0035685 | 0.06856 | -0.0073907 | 0.058024 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031767 | 0.014578 | 4.1491 | 39.5697 | 3.1827 | 122.0707 | 122.0241 | 121.974 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.022864 | 0.062694 | -0.11378 | 0.042231 | 0.076724 | 4.2452 | 3.2788 | 3.2366 | 0.0301 | -0.020019 | -0.017652 | -122.0698 | 0.12465 | 0.0352 | 0.052852 | -121.9712 | -121.9313 | 122.1669 | 122.1202 | 122.0701 | 39.6658 | -122.0479 | 0.020391 | 0.11899 | 0.15882 | 0.17891 | -122.1078
3352.5 | 122.0398 | -0.10071 | 121.9666 | 1.4211e-13 | -0.041102 | 0.0033547 | 0.068346 | -0.0076043 | 0.058238 | -0.0099192 | -0.0040121 | -0.0012713 | 0.019186 | 0.031767 | 0.014578 | 4.1857 | 39.849 | 3.2147 | 122.0799 | 122.0195 | 121.9786 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.018285 | 0.071851 | -0.10462 | 0.055966 | 0.11335 | 4.2864 | 3.3154 | 3.2594 | 0.052987 | 0.012026 | -0.003916 | -122.0423 | 0.12465 | 0.039778 | 0.043694 | -121.9483 | -121.8947 | 122.1806 | 122.1202 | 122.0793 | 39.9497 | -122.0113 | 0.024969 | 0.11899 | 0.17256 | 0.17891 | -122.0712
3354.2812 | 122.0123 | -0.1236 | 122.0261 | 1.4211e-13 | -0.041102 | 0.0035685 | 0.068346 | -0.0073907 | 0.058238 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018972 | 0.031553 | 0.014578 | 4.2452 | 40.142 | 3.2559 | 122.0707 | 122.0195 | 121.9832 | -0.044742 | 0.023941 | 0.087354 | -0.06093 | -0.080318 | 0.0366 | 0.071851 | -0.11378 | 0.078854 | 0.044681 | 4.3688 | 3.3795 | 3.3006 | -0.006522 | -0.042904 | 0.009814 | -122.1064 | 0.14754 | 0.062666 | 0.052852 | -121.9895 | -121.9542 | 122.1943 | 122.1431 | 122.1068 | 40.2656 | -122.0708 | 0.043278 | 0.1602 | 0.19545 | 0.21095 | -122.1398
3356.0469 | 121.994 | -0.10986 | 121.9849 | 1.4211e-13 | -0.040888 | 0.0035685 | 0.068133 | -0.0069633 | 0.058452 | -0.0099192 | -0.0042257 | -0.0016987 | 0.019186 | 0.031339 | 0.014364 | 4.3002 | 40.4579 | 3.2971 | 122.0662 | 122.0195 | 121.9694 | -0.053899 | 0.02852 | 0.087354 | -0.06093 | -0.080318 | 0.032021 | 0.071851 | -0.11378 | 0.055964 | 0.081301 | 4.41 | 3.407 | 3.351 | 0.034677 | -0.015441 | -0.003919 | -122.0652 | 0.13838 | 0.048933 | 0.052852 | -121.9528 | -121.913 | 122.176 | 122.1294 | 122.0793 | 40.5678 | -122.0388 | 0.029545 | 0.14188 | 0.18171 | 0.19722 | -122.0986
3357.75 | 122.0261 | -0.086975 | 122.0032 | 1.4211e-13 | -0.040888 | 0.0033547 | 0.06856 | -0.0071769 | 0.058452 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031339 | 0.014364 | 4.3459 | 40.7235 | 3.3154 | 122.0707 | 122.0195 | 121.9786 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.071851 | -0.11836 | 0.042233 | 0.067569 | 4.4329 | 3.4024 | 3.3602 | 0.016366 | -0.024595 | -0.031386 | -122.0835 | 0.11092 | 0.026045 | 0.057431 | -121.9757 | -121.9313 | 122.1577 | 122.1065 | 122.0656 | 40.8105 | -122.0479 | 0.006657 | 0.11442 | 0.15883 | 0.16517 | -122.1215
3359.5156 | 122.0856 | -0.068665 | 121.9757 | 1.4211e-13 | -0.041102 | 0.0033547 | 0.068346 | -0.0073907 | 0.058238 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019186 | 0.031339 | 0.014791 | 4.3917 | 40.9891 | 3.3475 | 122.0707 | 122.0241 | 121.974 | -0.053899 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.032021 | 0.07643 | -0.11836 | 0.014766 | 0.095035 | 4.4604 | 3.4161 | 3.4014 | 0.048411 | -0.001708 | -0.049696 | -122.056 | 0.088027 | 0.012314 | 0.06201 | -121.9437 | -121.8993 | 122.1394 | 122.0928 | 122.0427 | 41.0577 | -122.0296 | -0.011653 | 0.10069 | 0.1451 | 0.14686 | -122.0941
3361.2188 | 122.113 | -0.054932 | 121.9482 | 1.4211e-13 | -0.040888 | 0.0035685 | 0.06856 | -0.0071769 | 0.058665 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018972 | 0.031339 | 0.014364 | 4.4283 | 41.1768 | 3.3841 | 122.0707 | 122.0195 | 121.974 | -0.040163 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.032021 | 0.067272 | -0.1092 | 0.014769 | 0.1225 | 4.4833 | 3.439 | 3.4243 | 0.071298 | 0.025758 | -0.054271 | -122.0286 | 0.083452 | -0.001419 | 0.052852 | -121.9162 | -121.881 | 122.1257 | 122.0745 | 122.0289 | 41.2317 | -121.9884 | -0.025386 | 0.086953 | 0.1222 | 0.13313 | -122.0574
3362.9844 | 122.0215 | -0.07782 | 121.9437 | 1.4211e-13 | -0.040675 | 0.0033547 | 0.06856 | -0.0069633 | 0.058452 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018758 | 0.031126 | 0.014791 | 4.4833 | 41.4515 | 3.4207 | 122.0799 | 122.0195 | 121.9786 | -0.049321 | 0.023941 | 0.073618 | -0.065509 | -0.084896 | 0.0366 | 0.071851 | -0.11836 | 0.028499 | 0.13623 | 4.5611 | 3.4985 | 3.47 | 0.075875 | 0.034914 | -0.040541 | -122.0286 | 0.10176 | 0.012311 | 0.052852 | -121.9071 | -121.8718 | 122.1577 | 122.0974 | 122.0564 | 41.5293 | -121.993 | -0.007076 | 0.11442 | 0.14967 | 0.15144 | -122.062
3364.6875 | 122.0352 | -0.10986 | 121.994 | 1.4211e-13 | -0.040888 | 0.0033547 | 0.068988 | -0.0069633 | 0.058665 | -0.0022892 | -0.0042257 | -0.0019123 | 0.019399 | 0.031553 | 0.014578 | 4.5382 | 41.6392 | 3.4482 | 122.0753 | 122.0195 | 121.9786 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.062694 | -0.11378 | 0.060542 | 0.081302 | 4.6481 | 3.5581 | 3.4975 | 0.025521 | -0.01544 | -0.003919 | -122.0698 | 0.13838 | 0.048933 | 0.052852 | -121.9666 | -121.9313 | 122.1852 | 122.1294 | 122.0884 | 41.7491 | -122.0433 | 0.034124 | 0.13731 | 0.17256 | 0.18806 | -122.1078
3366.4531 | 122.1222 | -0.059509 | 121.9391 | 1.4211e-13 | -0.040675 | 0.0035685 | 0.06856 | -0.0069633 | 0.058879 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018972 | 0.031553 | 0.014364 | 4.5932 | 41.8544 | 3.4894 | 122.0753 | 122.0195 | 121.974 | -0.058478 | 0.023941 | 0.078197 | -0.051772 | -0.075739 | 0.0366 | 0.067272 | -0.11836 | 0.001031 | 0.13623 | 4.6527 | 3.5489 | 3.5479 | 0.080453 | 0.034913 | -0.058852 | -122.0148 | 0.08345 | 0.007737 | 0.066589 | -121.9025 | -121.8718 | 122.1348 | 122.079 | 122.0335 | 41.9139 | -121.9976 | -0.01623 | 0.096109 | 0.12678 | 0.13771 | -122.0574
3368.2344 | 122.049 | -0.091553 | 121.9849 | 1.4211e-13 | -0.040461 | 0.0033547 | 0.068774 | -0.0069633 | 0.058879 | -0.01755 | -0.0042257 | -0.0016987 | 0.018758 | 0.031553 | 0.014578 | 4.6435 | 42.0513 | 3.5031 | 122.0753 | 122.0241 | 121.9786 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.022864 | 0.067272 | -0.11378 | 0.042232 | 0.090458 | 4.7351 | 3.5947 | 3.5525 | 0.039256 | -0.006284 | -0.022229 | -122.0606 | 0.11549 | 0.035202 | 0.057431 | -121.962 | -121.9176 | 122.1669 | 122.1157 | 122.0701 | 42.1428 | -122.0342 | 0.015814 | 0.11442 | 0.15882 | 0.17433 | -122.0986
3369.9375 | 121.994 | -0.11444 | 121.9986 | 1.4211e-13 | -0.040675 | 0.0035685 | 0.068774 | -0.0071769 | 0.058879 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.031767 | 0.014364 | 4.6939 | 42.2344 | 3.526 | 122.0753 | 122.0195 | 121.974 | -0.044742 | 0.023941 | 0.078197 | -0.056351 | -0.084896 | 0.032021 | 0.058115 | -0.1092 | 0.069699 | 0.076725 | 4.8083 | 3.6405 | 3.5708 | 0.020944 | -0.024596 | 0.005238 | -122.0835 | 0.13838 | 0.05809 | 0.052852 | -121.9666 | -121.9405 | 122.1898 | 122.134 | 122.0884 | 42.3489 | -122.0433 | 0.029545 | 0.14646 | 0.17256 | 0.19264 | -122.1078
3371.7031 | 122.0444 | -0.09613 | 121.9986 | 1.4211e-13 | -0.040247 | 0.0037821 | 0.068774 | -0.0069633 | 0.058879 | -0.0099192 | -0.0046531 | -0.0016987 | 0.019186 | 0.031339 | 0.014364 | 4.7488 | 42.4084 | 3.5626 | 122.0799 | 122.0241 | 121.974 | -0.053899 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.0366 | 0.067272 | -0.11378 | 0.042231 | 0.081303 | 4.845 | 3.6588 | 3.6165 | 0.025523 | -0.024596 | -0.017652 | -122.0789 | 0.12465 | 0.039779 | 0.057431 | -121.962 | -121.9313 | 122.176 | 122.1202 | 122.0701 | 42.5046 | -122.0525 | 0.015812 | 0.13273 | 0.1634 | 0.17891 | -122.1124
3373.4531 | 122.0581 | -0.09613 | 121.994 | 1.4211e-13 | -0.040461 | 0.0033547 | 0.068774 | -0.0069633 | 0.058879 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031339 | 0.014364 | 4.8038 | 42.587 | 3.581 | 122.0753 | 122.0287 | 121.9786 | -0.049321 | 0.023941 | 0.091933 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | 0.046809 | 0.081302 | 4.8999 | 3.6771 | 3.6303 | 0.034679 | -0.01544 | -0.017652 | -122.0698 | 0.12007 | 0.0352 | 0.052852 | -121.9666 | -121.9222 | 122.1715 | 122.1248 | 122.0747 | 42.6831 | -122.0433 | 0.020391 | 0.12357 | 0.16798 | 0.18806 | -122.1078
3375.1562 | 122.1222 | -0.064087 | 121.9482 | 1.4211e-13 | -0.040461 | 0.0033547 | 0.068774 | -0.0071769 | 0.059093 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.014791 | 4.8496 | 42.7152 | 3.6176 | 122.0707 | 122.015 | 121.9694 | -0.058478 | 0.023941 | 0.078197 | -0.051772 | -0.080318 | 0.032021 | 0.067272 | -0.1092 | 0.005609 | 0.1225 | 4.9136 | 3.6817 | 3.6761 | 0.066719 | 0.02118 | -0.045116 | -122.0286 | 0.088028 | 0.012315 | 0.057431 | -121.9162 | -121.881 | 122.1348 | 122.079 | 122.0335 | 42.7793 | -122.0067 | -0.016231 | 0.096108 | 0.13136 | 0.14228 | -122.0574
3376.9219 | 122.0856 | -0.073242 | 121.962 | 1.4211e-13 | -0.040247 | 0.0037821 | 0.068774 | -0.0069633 | 0.058879 | -0.01755 | -0.0042257 | -0.0019123 | 0.019186 | 0.030912 | 0.014578 | 4.8999 | 42.8297 | 3.6313 | 122.0707 | 122.0195 | 121.974 | -0.049321 | 0.019362 | 0.082776 | -0.06093 | -0.084896 | 0.027442 | 0.067272 | -0.11836 | 0.023921 | 0.10877 | 4.9732 | 3.7046 | 3.6806 | 0.057565 | 0.012025 | -0.045119 | -122.0469 | 0.092604 | 0.012312 | 0.057431 | -121.9345 | -121.8947 | 122.144 | 122.0928 | 122.0472 | 42.9029 | -122.0113 | -0.011654 | 0.10068 | 0.14051 | 0.15602 | -122.0803
3378.6875 | 121.9849 | -0.10529 | 121.9803 | 1.4211e-13 | -0.040247 | 0.0033547 | 0.06856 | -0.0071769 | 0.059306 | -0.0022892 | -0.0042257 | -0.0016987 | 0.019186 | 0.031553 | 0.014364 | 4.9457 | 42.9762 | 3.6588 | 122.0753 | 122.0241 | 121.9786 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.055965 | 0.095035 | 5.051 | 3.7641 | 3.7081 | 0.043833 | -0.001707 | -0.013075 | -122.0606 | 0.12923 | 0.044356 | 0.057431 | -121.9483 | -121.913 | 122.1806 | 122.1294 | 122.0839 | 43.0815 | -122.0296 | 0.024968 | 0.13731 | 0.17256 | 0.18806 | -122.0986
3380.3906 | 122.1359 | -0.073242 | 121.9299 | 1.4211e-13 | -0.040461 | 0.0035685 | 0.06856 | -0.0071769 | 0.058879 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.014791 | 5.0098 | 43.1273 | 3.6908 | 122.0753 | 122.0195 | 121.9786 | -0.049321 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.027442 | 0.067272 | -0.1092 | 0.023921 | 0.14539 | 5.083 | 3.7641 | 3.7402 | 0.089608 | 0.048647 | -0.035961 | -122.0011 | 0.097183 | 0.012312 | 0.048273 | -121.9025 | -121.8627 | 122.1486 | 122.0928 | 122.0518 | 43.2005 | -121.9793 | 0.002081 | 0.10068 | 0.14051 | 0.1606 | -122.0391
3382.1562 | 122.0764 | -0.073242 | 121.9574 | 1.4211e-13 | -0.040461 | 0.0035685 | 0.068774 | -0.0069633 | 0.05952 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018972 | 0.031339 | 0.014578 | 5.0556 | 43.2784 | 3.7275 | 122.0707 | 122.015 | 121.9786 | -0.053899 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.12294 | 0.019343 | 0.11335 | 5.1288 | 3.8007 | 3.7814 | 0.057564 | 0.021182 | -0.049697 | -122.0331 | 0.097183 | 0.012312 | 0.062009 | -121.93 | -121.8855 | 122.144 | 122.0882 | 122.0518 | 43.3516 | -122.0113 | -0.002497 | 0.10068 | 0.14509 | 0.1606 | -122.0803
3383.9219 | 122.1313 | -0.041199 | 121.9482 | 1.4211e-13 | -0.040247 | 0.0037821 | 0.068774 | -0.0067497 | 0.059093 | -0.0022892 | -0.0044395 | -0.0014849 | 0.019186 | 0.031339 | 0.014364 | 5.1151 | 43.4111 | 3.7366 | 122.0707 | 122.015 | 121.9694 | -0.058478 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.027442 | 0.071851 | -0.1092 | -0.017279 | 0.1225 | 5.1563 | 3.7778 | 3.7951 | 0.066719 | 0.02118 | -0.068004 | -122.024 | 0.06514 | -0.02431 | 0.043694 | -121.9208 | -121.8764 | 122.1119 | 122.0562 | 122.0106 | 43.4523 | -122.0067 | -0.03454 | 0.068641 | 0.11305 | 0.12398 | -122.0574
3385.6406 | 122.0764 | -0.068665 | 121.9482 | 1.4211e-13 | -0.040034 | 0.0039957 | 0.068774 | -0.0069633 | 0.059093 | -0.0022892 | -0.0046531 | -0.0014849 | 0.018972 | 0.031553 | 0.014364 | 5.1609 | 43.5439 | 3.7687 | 122.0753 | 122.0241 | 121.9832 | -0.044742 | 0.02852 | 0.078197 | -0.065509 | -0.075739 | 0.027442 | 0.081008 | -0.1092 | 0.023923 | 0.12708 | 5.2296 | 3.8373 | 3.8134 | 0.075877 | 0.034916 | -0.040538 | -122.024 | 0.097185 | 0.003156 | 0.043694 | -121.9208 | -121.8672 | 122.144 | 122.0928 | 122.0518 | 43.6126 | -121.993 | -0.007074 | 0.096107 | 0.14967 | 0.14686 | -122.0574
3387.4062 | 122.0306 | -0.13275 | 121.994 | 1.4211e-13 | -0.040034 | 0.0037821 | 0.068988 | -0.0071769 | 0.059306 | -0.01755 | -0.0042257 | -0.0014849 | 0.018758 | 0.031339 | 0.01415 | 5.2204 | 43.6309 | 3.7961 | 122.0753 | 122.0195 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.0366 | 0.07643 | -0.11836 | 0.08343 | 0.081302 | 5.3532 | 3.9289 | 3.8455 | 0.025521 | -0.020019 | 0.01439 | -122.0789 | 0.15669 | 0.071821 | 0.057431 | -121.9574 | -121.9176 | 122.2081 | 122.1523 | 122.1068 | 43.7637 | -122.0433 | 0.047855 | 0.16935 | 0.20918 | 0.21553 | -122.1124
3389.125 | 122.0261 | -0.091553 | 121.9894 | 1.4211e-13 | -0.03982 | 0.0037821 | 0.068774 | -0.0069633 | 0.05952 | 0.0053413 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.01415 | 5.2754 | 43.7271 | 3.8282 | 122.0662 | 122.0241 | 121.9786 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.0366 | 0.07643 | -0.11378 | 0.042232 | 0.076723 | 5.3669 | 3.9197 | 3.8775 | 0.034678 | -0.010862 | -0.022229 | -122.0698 | 0.11549 | 0.030623 | 0.052852 | -121.9528 | -121.913 | 122.1577 | 122.1157 | 122.0701 | 43.8186 | -122.0388 | 0.011235 | 0.12815 | 0.16798 | 0.17433 | -122.1032
3390.8906 | 122.0947 | -0.064087 | 121.9391 | 1.4211e-13 | -0.03982 | 0.0039957 | 0.068774 | -0.0067497 | 0.059306 | -0.02518 | -0.0046531 | -0.0019123 | 0.019186 | 0.031339 | 0.014578 | 5.3257 | 43.8232 | 3.8373 | 122.0799 | 122.0333 | 121.974 | -0.053899 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.027442 | 0.081008 | -0.1092 | 0.010188 | 0.14081 | 5.3898 | 3.9014 | 3.8912 | 0.09419 | 0.034913 | -0.045116 | -122.024 | 0.088028 | -0.001422 | 0.043694 | -121.9116 | -121.8581 | 122.144 | 122.0974 | 122.0381 | 43.8873 | -121.993 | -0.020809 | 0.091529 | 0.1451 | 0.14686 | -122.0483
3392.5938 | 121.994 | -0.10986 | 121.9894 | 1.4211e-13 | -0.03982 | 0.0035685 | 0.06856 | -0.0069633 | 0.05952 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018972 | 0.031126 | 0.014578 | 5.3715 | 43.9148 | 3.8786 | 122.0707 | 122.0287 | 121.9832 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.062694 | -0.11378 | 0.060542 | 0.081302 | 5.4814 | 3.9884 | 3.9279 | 0.039257 | -0.006283 | -0.003919 | -122.0698 | 0.1338 | 0.053512 | 0.057431 | -121.962 | -121.9267 | 122.1806 | 122.1386 | 122.093 | 44.0246 | -122.0388 | 0.029545 | 0.13731 | 0.17256 | 0.18806 | -122.1032
3394.375 | 122.1405 | -0.068665 | 121.9803 | 1.4211e-13 | -0.040034 | 0.0037821 | 0.069201 | -0.0069633 | 0.059734 | -0.01755 | -0.0042257 | -0.0016987 | 0.018972 | 0.031339 | 0.01415 | 5.431 | 43.9789 | 3.906 | 122.0662 | 122.0241 | 121.974 | -0.044742 | 0.023941 | 0.087354 | -0.065509 | -0.080318 | 0.022864 | 0.062694 | -0.11378 | 0.023923 | 0.085878 | 5.4997 | 3.9747 | 3.9508 | 0.043833 | -0.006286 | -0.045117 | -122.0606 | 0.092606 | 0.003156 | 0.048273 | -121.9574 | -121.9176 | 122.1348 | 122.0928 | 122.0427 | 44.0475 | -122.025 | -0.011653 | 0.091529 | 0.13136 | 0.15602 | -122.0941
3396.1406 | 122.0901 | -0.082397 | 121.9482 | 1.4211e-13 | -0.040034 | 0.0037821 | 0.068774 | -0.0065361 | 0.05952 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031767 | 0.014364 | 5.3944 | 44.1025 | 3.9472 | 122.0707 | 122.0241 | 121.9832 | -0.044742 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.1092 | 0.037655 | 0.1225 | 5.4768 | 4.0296 | 3.992 | 0.075877 | 0.034916 | -0.026806 | -122.024 | 0.10176 | 0.016888 | 0.043694 | -121.9208 | -121.881 | 122.1531 | 122.1065 | 122.0656 | 44.1849 | -121.993 | 0.006658 | 0.10984 | 0.14967 | 0.16975 | -122.0574
3397.9062 | 121.9849 | -0.10071 | 121.9894 | 1.4211e-13 | -0.03982 | 0.0035685 | 0.069201 | -0.0067497 | 0.059093 | -0.01755 | -0.0040121 | -0.0014849 | 0.018972 | 0.031553 | 0.014364 | 5.4448 | 44.1666 | 3.9518 | 122.0753 | 122.0241 | 121.9832 | -0.044742 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | 0.055966 | 0.08588 | 5.5455 | 4.0525 | 3.9965 | 0.034678 | -0.006283 | -0.013074 | -122.0652 | 0.12465 | 0.044357 | 0.057431 | -121.962 | -121.9176 | 122.176 | 122.1248 | 122.0839 | 44.2673 | -122.0342 | 0.024969 | 0.12815 | 0.17256 | 0.18348 | -122.1032
3399.625 | 122.1359 | -0.036621 | 121.9391 | 1.4211e-13 | -0.040034 | 0.0039957 | 0.069415 | -0.0067497 | 0.059947 | -0.01755 | -0.0044395 | -0.0019123 | 0.018972 | 0.030912 | 0.014578 | 5.4997 | 44.2444 | 3.9747 | 122.0799 | 122.0241 | 121.9786 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.0366 | 0.062694 | -0.11378 | -0.017278 | 0.14081 | 5.5363 | 4.0113 | 4.0286 | 0.085032 | 0.039492 | -0.077161 | -122.024 | 0.060562 | -0.024309 | 0.052852 | -121.9025 | -121.8764 | 122.1165 | 122.0607 | 122.0152 | 44.2811 | -121.993 | -0.048275 | 0.073221 | 0.099315 | 0.1194 | -122.0529
3401.3906 | 122.0032 | -0.10529 | 121.9849 | 1.4211e-13 | -0.039606 | 0.0039957 | 0.068988 | -0.0067497 | 0.059734 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018545 | 0.031339 | 0.01415 | 5.5409 | 44.3223 | 4.0113 | 122.0707 | 122.0287 | 121.9786 | -0.053899 | 0.023941 | 0.087354 | -0.056351 | -0.075739 | 0.022864 | 0.071851 | -0.1092 | 0.051387 | 0.08588 | 5.6462 | 4.1166 | 4.0652 | 0.043835 | -0.006284 | -0.003917 | -122.0606 | 0.12923 | 0.048935 | 0.052852 | -121.962 | -121.913 | 122.176 | 122.134 | 122.0839 | 44.4276 | -122.0388 | 0.029547 | 0.12815 | 0.17714 | 0.19264 | -122.0941
3403.1875 | 122.1451 | -0.07782 | 121.9391 | 1.4211e-13 | -0.039606 | 0.0035685 | 0.068988 | -0.0065361 | 0.05952 | -0.01755 | -0.0042257 | -0.0019123 | 0.018331 | 0.031339 | 0.014578 | 5.605 | 44.391 | 4.0479 | 122.0753 | 122.0241 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.071851 | -0.11836 | 0.028499 | 0.13623 | 5.6828 | 4.1258 | 4.0973 | 0.085032 | 0.034913 | -0.040541 | -122.0194 | 0.10176 | 0.01689 | 0.057431 | -121.9162 | -121.8672 | 122.1531 | 122.1019 | 122.0518 | 44.4688 | -121.9884 | -0.002498 | 0.10068 | 0.14967 | 0.1606 | -122.0574
3404.9688 | 122.1405 | -0.07782 | 121.9482 | 1.4211e-13 | -0.039606 | 0.0037821 | 0.068774 | -0.0067497 | 0.059947 | -0.0022892 | -0.0040121 | -0.0019123 | 0.018972 | 0.031553 | 0.014364 | 5.6645 | 44.4596 | 4.0663 | 122.0616 | 122.0241 | 121.974 | -0.044742 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.027442 | 0.067272 | -0.12294 | 0.033078 | 0.11334 | 5.7423 | 4.1441 | 4.111 | 0.075877 | 0.025758 | -0.045119 | -122.0286 | 0.10634 | 0.012311 | 0.05743 | -121.9208 | -121.881 | 122.1394 | 122.1019 | 122.0518 | 44.5375 | -121.993 | -0.002498 | 0.10526 | 0.14509 | 0.15602 | -122.0712
3406.75 | 122.0169 | -0.10529 | 121.9757 | 1.4211e-13 | -0.039606 | 0.0037821 | 0.068988 | -0.0063223 | 0.059947 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018545 | 0.031126 | 0.014578 | 5.7286 | 44.5283 | 4.1029 | 122.0753 | 122.0241 | 121.9786 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.071851 | -0.11836 | 0.055965 | 0.099613 | 5.8339 | 4.2082 | 4.1522 | 0.048411 | 0.002871 | -0.013075 | -122.0514 | 0.12923 | 0.048935 | 0.06201 | -121.9483 | -121.9039 | 122.1806 | 122.1294 | 122.0839 | 44.6336 | -122.025 | 0.029547 | 0.13273 | 0.17714 | 0.18806 | -122.0941
3408.4688 | 122.1542 | -0.050354 | 121.9437 | 1.4211e-13 | -0.039606 | 0.0037821 | 0.068988 | -0.0067497 | 0.059947 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018758 | 0.031553 | 0.014364 | 5.7927 | 44.6016 | 4.1532 | 122.0707 | 122.0241 | 121.9786 | -0.049321 | 0.019362 | 0.082776 | -0.070087 | -0.080318 | 0.022864 | 0.058115 | -0.11378 | 0.001033 | 0.12708 | 5.8431 | 4.2036 | 4.2026 | 0.080454 | 0.034914 | -0.063428 | -122.024 | 0.069716 | -0.019733 | 0.043695 | -121.9208 | -121.8855 | 122.1211 | 122.0745 | 122.0289 | 44.6519 | -121.993 | -0.029964 | 0.073218 | 0.10847 | 0.13313 | -122.0574
3410.2344 | 122.049 | -0.09613 | 121.9986 | 1.4211e-13 | -0.039393 | 0.0039957 | 0.06856 | -0.0069633 | 0.059947 | 0.0053413 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.014578 | 5.8476 | 44.6611 | 4.1761 | 122.0799 | 122.0241 | 121.9694 | -0.049321 | 0.019362 | 0.087354 | -0.056351 | -0.084896 | 0.027442 | 0.067272 | -0.1092 | 0.046809 | 0.081303 | 5.9438 | 4.2723 | 4.2255 | 0.025523 | -0.029174 | -0.013073 | -122.0835 | 0.11549 | 0.039779 | 0.052852 | -121.9712 | -121.9313 | 122.176 | 122.1202 | 122.0656 | 44.7572 | -122.0479 | 0.011234 | 0.12357 | 0.1634 | 0.18348 | -122.1078
3411.9375 | 122.0764 | -0.07782 | 121.9711 | 1.4211e-13 | -0.039606 | 0.0033547 | 0.068988 | -0.0063223 | 0.059734 | -0.01755 | -0.0044395 | -0.0019123 | 0.018545 | 0.031553 | 0.014364 | 5.9117 | 44.6977 | 4.2036 | 122.0707 | 122.0195 | 121.974 | -0.053899 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.11836 | 0.023921 | 0.099613 | 5.9896 | 4.2814 | 4.2575 | 0.04841 | 0.00287 | -0.040541 | -122.0514 | 0.097182 | 0.021469 | 0.06201 | -121.9437 | -121.9039 | 122.1486 | 122.0974 | 122.0518 | 44.7755 | -122.025 | -0.002498 | 0.10526 | 0.14509 | 0.15602 | -122.0895
3413.7031 | 122.0444 | -0.082397 | 122.0078 | 1.4211e-13 | -0.039606 | 0.0039957 | 0.068988 | -0.0069633 | 0.060161 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.014364 | 5.9667 | 44.7527 | 4.2402 | 122.0707 | 122.0195 | 121.9786 | -0.044742 | 0.019362 | 0.082776 | -0.065509 | -0.084896 | 0.0366 | 0.067272 | -0.11836 | 0.037655 | 0.062992 | 6.0491 | 4.3226 | 4.285 | 0.011789 | -0.029172 | -0.035964 | -122.0926 | 0.10176 | 0.016888 | 0.052852 | -121.9712 | -121.9405 | 122.1531 | 122.1019 | 122.061 | 44.8351 | -122.0525 | -0.002499 | 0.119 | 0.14967 | 0.16517 | -122.1261
3415.4688 | 122.1497 | -0.059509 | 121.9666 | 1.4211e-13 | -0.039393 | 0.0039957 | 0.068988 | -0.0063223 | 0.059947 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018972 | 0.031553 | 0.014578 | 6.017 | 44.7893 | 4.2814 | 122.0662 | 122.015 | 121.974 | -0.044742 | 0.014784 | 0.087354 | -0.051772 | -0.071161 | 0.041178 | 0.07643 | -0.11378 | 0.014767 | 0.099611 | 6.0766 | 4.3409 | 4.3262 | 0.048408 | 0.007447 | -0.054273 | -122.0377 | 0.074293 | 0.007737 | 0.06201 | -121.9254 | -121.8901 | 122.1257 | 122.0745 | 122.0335 | 44.8488 | -122.0113 | -0.011652 | 0.10069 | 0.13594 | 0.14686 | -122.0803
3417.2344 | 122.0078 | -0.11444 | 121.9803 | 1.4211e-13 | -0.039393 | 0.0037821 | 0.068988 | -0.0065361 | 0.060161 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031339 | 0.01415 | 6.0811 | 44.8259 | 4.3318 | 122.0799 | 122.0241 | 121.9786 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.06512 | 0.099613 | 6.1956 | 4.4462 | 4.3811 | 0.043833 | -0.001707 | -0.00392 | -122.0606 | 0.14296 | 0.053511 | 0.057431 | -121.9483 | -121.913 | 122.1943 | 122.1386 | 122.093 | 44.9404 | -122.0296 | 0.034123 | 0.14646 | 0.18171 | 0.19722 | -122.0986
3419 | 122.049 | -0.086975 | 121.994 | 1.4211e-13 | -0.039179 | 0.0039957 | 0.068988 | -0.0065361 | 0.060161 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018758 | 0.031339 | 0.014364 | 6.1452 | 44.8122 | 4.3455 | 122.0753 | 122.0241 | 121.9786 | -0.053899 | 0.037677 | 0.082776 | -0.06093 | -0.075739 | 0.032021 | 0.067272 | -0.11378 | 0.033076 | 0.081302 | 6.2322 | 4.4325 | 4.3994 | 0.0301 | -0.01544 | -0.026807 | -122.0698 | 0.12465 | 0.026045 | 0.052852 | -121.962 | -121.9267 | 122.1623 | 122.1111 | 122.0656 | 44.8992 | -122.0479 | 0.011236 | 0.119 | 0.15425 | 0.16975 | -122.1078
3420.7656 | 122.0306 | -0.091553 | 121.9574 | 1.4211e-13 | -0.039179 | 0.0039957 | 0.068988 | -0.0065361 | 0.060375 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031767 | 0.014364 | 6.1956 | 44.8534 | 4.3776 | 122.0662 | 122.0195 | 121.9786 | -0.063057 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.027442 | 0.067272 | -0.11836 | 0.028496 | 0.10877 | 6.2872 | 4.4691 | 4.4406 | 0.062143 | 0.021182 | -0.026808 | -122.0331 | 0.11091 | 0.035202 | 0.06201 | -121.93 | -121.8901 | 122.1577 | 122.1111 | 122.0701 | 44.9449 | -122.0205 | 0.015814 | 0.11899 | 0.15882 | 0.17891 | -122.0758
3422.4688 | 122.0581 | -0.091553 | 121.9894 | 1.4211e-13 | -0.039179 | 0.0042095 | 0.068988 | -0.0061087 | 0.060375 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018758 | 0.031553 | 0.014364 | 6.2505 | 44.8992 | 4.4188 | 122.0707 | 122.0195 | 121.9832 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.10462 | 0.037654 | 0.081302 | 6.3421 | 4.5103 | 4.4727 | 0.030099 | -0.006283 | -0.013071 | -122.0652 | 0.12007 | 0.030623 | 0.043694 | -121.962 | -121.9176 | 122.1623 | 122.1111 | 122.0747 | 44.9907 | -122.0433 | 0.015814 | 0.11899 | 0.1634 | 0.16975 | -122.0941
3424.2344 | 122.1039 | -0.064087 | 121.9345 | 1.4211e-13 | -0.039179 | 0.0035685 | 0.068988 | -0.0061087 | 0.060588 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031126 | 0.01415 | 6.3055 | 44.9312 | 4.4463 | 122.0799 | 122.0241 | 121.9832 | -0.049321 | 0.014784 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.071851 | -0.1092 | 0.014766 | 0.14539 | 6.3696 | 4.5103 | 4.4956 | 0.08961 | 0.048649 | -0.045116 | -122.0148 | 0.078871 | 0.003157 | 0.048273 | -121.9071 | -121.8627 | 122.144 | 122.0882 | 122.0472 | 44.9953 | -121.9838 | -0.016231 | 0.091529 | 0.13594 | 0.14228 | -122.0437
3426.0156 | 122.0993 | -0.068665 | 121.9437 | 1.4211e-13 | -0.039393 | 0.0039957 | 0.068988 | -0.0063223 | 0.060375 | -0.01755 | -0.0044395 | -0.0014849 | 0.018972 | 0.031767 | 0.014364 | 6.365 | 44.977 | 4.4691 | 122.0753 | 122.0287 | 121.974 | -0.044742 | 0.014784 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.11836 | 0.023923 | 0.13166 | 6.4337 | 4.5378 | 4.5139 | 0.085033 | 0.030335 | -0.049696 | -122.024 | 0.083449 | 0.007735 | 0.057431 | -121.9162 | -121.881 | 122.144 | 122.0974 | 122.0427 | 45.0457 | -121.9884 | -0.011653 | 0.096107 | 0.13136 | 0.14686 | -122.062
3427.7812 | 122.0215 | -0.091553 | 121.9849 | 1.4211e-13 | -0.039393 | 0.0039957 | 0.069201 | -0.0063223 | 0.060588 | -0.01755 | -0.0044395 | -0.0019123 | 0.019186 | 0.031339 | 0.014364 | 6.4291 | 44.9908 | 4.5149 | 122.0753 | 122.0287 | 121.9832 | -0.049321 | 0.033099 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.1092 | 0.042232 | 0.090458 | 6.5207 | 4.6065 | 4.5643 | 0.043835 | -0.001705 | -0.01765 | -122.0652 | 0.12465 | 0.035202 | 0.052852 | -121.9574 | -121.9176 | 122.1669 | 122.1203 | 122.0747 | 45.0823 | -122.0342 | 0.011235 | 0.11899 | 0.15882 | 0.17433 | -122.0941
3429.5 | 122.0764 | -0.068665 | 121.962 | 1.4211e-13 | -0.038965 | 0.0039957 | 0.069201 | -0.0065361 | 0.060588 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.014578 | 6.484 | 45.0274 | 4.5058 | 122.0707 | 122.0241 | 121.9832 | -0.053899 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.0366 | 0.067272 | -0.11378 | 0.014766 | 0.10877 | 6.5527 | 4.5744 | 4.5597 | 0.062144 | 0.021183 | -0.045117 | -122.0377 | 0.088027 | 0.003156 | 0.048273 | -121.9254 | -121.8947 | 122.1394 | 122.0928 | 122.0518 | 45.096 | -122.0159 | -0.007074 | 0.10526 | 0.13594 | 0.15602 | -122.0758
3431.2656 | 122.0398 | -0.082397 | 121.962 | 1.4211e-13 | -0.038752 | 0.0039957 | 0.069415 | -0.0063223 | 0.060588 | 0.0053413 | -0.0044395 | -0.0019123 | 0.018545 | 0.031553 | 0.014364 | 6.539 | 45.0457 | 4.547 | 122.0799 | 122.0287 | 121.9832 | -0.044742 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.032021 | 0.067272 | -0.1092 | 0.037655 | 0.11792 | 6.6214 | 4.6294 | 4.5917 | 0.066723 | 0.021183 | -0.026806 | -122.0331 | 0.10176 | 0.016888 | 0.043694 | -121.93 | -121.8947 | 122.1623 | 122.1111 | 122.0656 | 45.1281 | -122.0067 | 0.011236 | 0.11442 | 0.14967 | 0.16059 | -122.0712
3432.9688 | 122.1176 | -0.064087 | 121.9574 | 1.4211e-13 | -0.039179 | 0.0037821 | 0.068988 | -0.0058951 | 0.060588 | -0.01755 | -0.0042257 | -0.0016987 | 0.018758 | 0.031553 | 0.014791 | 6.5893 | 45.0503 | 4.5882 | 122.0799 | 122.0195 | 121.974 | -0.049321 | 0.019362 | 0.087354 | -0.06093 | -0.075739 | 0.032021 | 0.071851 | -0.11378 | 0.014766 | 0.1225 | 6.6534 | 4.6523 | 4.6375 | 0.062143 | 0.016603 | -0.049695 | -122.0331 | 0.083449 | 0.003157 | 0.052852 | -121.9254 | -121.8855 | 122.144 | 122.0836 | 122.0381 | 45.1144 | -122.0067 | -0.011652 | 0.096108 | 0.13594 | 0.15144 | -122.0712
3434.7344 | 122.049 | -0.10071 | 121.9803 | 1.4211e-13 | -0.038752 | 0.0037821 | 0.069201 | -0.0063223 | 0.060375 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018972 | 0.031339 | 0.014578 | 6.626 | 45.0915 | 4.6111 | 122.0799 | 122.0241 | 121.9786 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.071851 | -0.1092 | 0.046809 | 0.099613 | 6.7267 | 4.7118 | 4.665 | 0.043833 | -0.001707 | -0.008495 | -122.0606 | 0.12923 | 0.039778 | 0.048273 | -121.9528 | -121.9084 | 122.1806 | 122.1248 | 122.0793 | 45.1922 | -122.0342 | 0.02039 | 0.12815 | 0.17256 | 0.17891 | -122.0895
3436.5 | 122.0306 | -0.10071 | 122.0078 | 1.4211e-13 | -0.038752 | 0.0042095 | 0.069201 | -0.0063223 | 0.060588 | -0.01755 | -0.0042257 | -0.0016987 | 0.018545 | 0.031339 | 0.01415 | 6.6992 | 45.1052 | 4.6523 | 122.0799 | 122.0287 | 121.9832 | -0.049321 | 0.02852 | 0.087354 | -0.065509 | -0.075739 | 0.032021 | 0.067272 | -0.11836 | 0.051387 | 0.072148 | 6.7999 | 4.753 | 4.7016 | 0.020947 | -0.024593 | -0.017653 | -122.0835 | 0.12923 | 0.035199 | 0.052852 | -121.9757 | -121.9405 | 122.1806 | 122.1294 | 122.0839 | 45.2059 | -122.0571 | 0.024969 | 0.13273 | 0.16798 | 0.18806 | -122.1261
3438.2812 | 121.9849 | -0.11444 | 121.9849 | 1.4211e-13 | -0.038965 | 0.0039957 | 0.068988 | -0.0063223 | 0.061016 | -0.02518 | -0.0042257 | -0.0016987 | 0.018758 | 0.031339 | 0.01415 | 6.745 | 45.1281 | 4.6798 | 122.0799 | 122.0241 | 121.9832 | -0.040163 | 0.019362 | 0.082776 | -0.056351 | -0.084896 | 0.0366 | 0.067272 | -0.1092 | 0.074278 | 0.095036 | 6.8595 | 4.7942 | 4.7199 | 0.039256 | -0.001705 | 0.005238 | -122.0698 | 0.1338 | 0.05809 | 0.052852 | -121.9483 | -121.9176 | 122.1943 | 122.1386 | 122.0976 | 45.2426 | -122.025 | 0.029545 | 0.15104 | 0.18171 | 0.19722 | -122.0941
3439.9844 | 122.0444 | -0.086975 | 121.9711 | 1.4211e-13 | -0.038538 | 0.0044231 | 0.068988 | -0.0058951 | 0.061016 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.014364 | 6.8091 | 45.1281 | 4.7347 | 122.0707 | 122.0195 | 121.9832 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.032021 | 0.067272 | -0.12294 | 0.037654 | 0.099613 | 6.8961 | 4.8217 | 4.784 | 0.04841 | 0.012028 | -0.035964 | -122.0514 | 0.11092 | 0.030624 | 0.066588 | -121.9391 | -121.9039 | 122.1577 | 122.1065 | 122.0701 | 45.2151 | -122.0205 | 0.006657 | 0.119 | 0.15425 | 0.16517 | -122.0941
3441.75 | 122.1313 | -0.068665 | 121.9574 | 1.4211e-13 | -0.039393 | 0.0039957 | 0.069201 | -0.0061087 | 0.061016 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018545 | 0.031126 | 0.014364 | 6.8457 | 45.1327 | 4.7713 | 122.0753 | 122.0195 | 121.974 | -0.049321 | 0.033099 | 0.06904 | -0.06093 | -0.080318 | 0.041178 | 0.062694 | -0.11378 | 0.019344 | 0.11792 | 6.9144 | 4.84 | 4.8206 | 0.062143 | 0.016603 | -0.045117 | -122.0377 | 0.10176 | 0.007735 | 0.052852 | -121.9162 | -121.8947 | 122.144 | 122.0882 | 122.0427 | 45.2014 | -122.0067 | -0.011653 | 0.10984 | 0.13136 | 0.13771 | -122.0712
3443.5156 | 122.049 | -0.09613 | 121.9757 | 1.4211e-13 | -0.038752 | 0.0039957 | 0.069201 | -0.0061087 | 0.061016 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031339 | 0.014364 | 6.8961 | 45.1693 | 4.8034 | 122.0799 | 122.0287 | 121.9786 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.032021 | 0.071851 | -0.11836 | 0.042231 | 0.10419 | 6.9922 | 4.8995 | 4.8573 | 0.05299 | 0.002871 | -0.022231 | -122.0606 | 0.12007 | 0.0352 | 0.057431 | -121.9437 | -121.9039 | 122.176 | 122.1248 | 122.0747 | 45.2655 | -122.0296 | 0.011234 | 0.12815 | 0.16798 | 0.17891 | -122.0941
3445.2188 | 122.1497 | -0.064087 | 121.9482 | 1.4211e-13 | -0.038752 | 0.0039957 | 0.069415 | -0.0058951 | 0.060588 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.014364 | 6.9602 | 45.1739 | 4.8217 | 122.0707 | 122.0241 | 121.9832 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.0366 | 0.067272 | -0.11378 | 0.019345 | 0.1225 | 7.0243 | 4.8858 | 4.8664 | 0.075877 | 0.034916 | -0.049695 | -122.0286 | 0.088028 | 0.003157 | 0.052852 | -121.9116 | -121.881 | 122.1348 | 122.0882 | 122.0472 | 45.238 | -121.993 | -0.016231 | 0.10069 | 0.13136 | 0.14228 | -122.062
3446.9844 | 122.0352 | -0.09613 | 121.994 | 1.4211e-13 | -0.038752 | 0.0037821 | 0.069415 | -0.0056813 | 0.061016 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.014578 | 7.0106 | 45.1785 | 4.8629 | 122.0799 | 122.0241 | 121.9786 | -0.044742 | 0.033099 | 0.087354 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.11836 | 0.051388 | 0.08588 | 7.1067 | 4.959 | 4.9076 | 0.0301 | -0.01544 | -0.022231 | -122.0698 | 0.12923 | 0.030621 | 0.052852 | -121.9666 | -121.9267 | 122.176 | 122.1202 | 122.0747 | 45.2746 | -122.0388 | 0.020391 | 0.12357 | 0.1634 | 0.18348 | -122.1124
3448.7656 | 122.081 | -0.091553 | 121.9803 | 1.4211e-13 | -0.038538 | 0.0039957 | 0.068988 | -0.0058951 | 0.060802 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.031767 | 0.014578 | 7.0563 | 45.1876 | 4.8949 | 122.0753 | 122.0241 | 121.9877 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.046811 | 0.095035 | 7.1479 | 4.9865 | 4.9397 | 0.043833 | 0.00745 | -0.022229 | -122.0606 | 0.11549 | 0.030623 | 0.052852 | -121.9528 | -121.913 | 122.1669 | 122.1157 | 122.0793 | 45.2792 | -122.025 | 0.011235 | 0.11899 | 0.15882 | 0.16975 | -122.0941
3450.4844 | 122.1313 | -0.086975 | 121.9391 | 1.4211e-13 | -0.038965 | 0.0037821 | 0.069415 | -0.0058951 | 0.061229 | -0.0022892 | -0.0048667 | -0.0016987 | 0.018758 | 0.031553 | 0.014578 | 7.1067 | 45.2105 | 4.9178 | 122.0753 | 122.0195 | 121.9832 | -0.053899 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.041178 | 0.07643 | -0.11836 | 0.033076 | 0.13623 | 7.1937 | 5.0048 | 4.9717 | 0.080453 | 0.044071 | -0.031386 | -122.0148 | 0.11092 | 0.026045 | 0.057431 | -121.8979 | -121.8627 | 122.1623 | 122.1065 | 122.0701 | 45.2975 | -121.993 | 0.011236 | 0.12815 | 0.1634 | 0.17433 | -122.0574
3452.25 | 122.0581 | -0.091553 | 121.994 | 1.4211e-13 | -0.038752 | 0.0042095 | 0.069415 | -0.0061087 | 0.061016 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.014364 | 7.1662 | 45.2243 | 4.959 | 122.0707 | 122.0195 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.0366 | 0.071851 | -0.11836 | 0.042232 | 0.076724 | 7.2578 | 5.0506 | 5.0083 | 0.025521 | -0.020019 | -0.026808 | -122.0789 | 0.11549 | 0.030623 | 0.057431 | -121.9574 | -121.9222 | 122.1623 | 122.1111 | 122.0656 | 45.3158 | -122.0433 | 0.006657 | 0.12815 | 0.1634 | 0.17433 | -122.1124
3453.9531 | 122.1313 | -0.054932 | 121.9391 | 1.4211e-13 | -0.038752 | 0.0039957 | 0.068774 | -0.0061087 | 0.060802 | -0.0022892 | -0.0040121 | -0.0014849 | 0.018758 | 0.031339 | 0.014578 | 7.1937 | 45.3433 | 4.9132 | 122.0753 | 122.0287 | 121.974 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.032021 | 0.067272 | -0.11378 | 0.01019 | 0.13623 | 7.2486 | 4.9682 | 4.958 | 0.089611 | 0.034913 | -0.05885 | -122.0102 | 0.078873 | -0.005998 | 0.052852 | -121.9071 | -121.8718 | 122.1303 | 122.0836 | 122.0289 | 45.3982 | -121.9838 | -0.016229 | 0.086953 | 0.1222 | 0.13313 | -122.0529
3455.7188 | 122.1085 | -0.041199 | 121.9482 | 1.4211e-13 | -0.038538 | 0.0042095 | 0.069201 | -0.0058951 | 0.061229 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031339 | 0.014364 | 7.2441 | 45.3708 | 4.9728 | 122.0707 | 122.0241 | 121.9786 | -0.044742 | 0.02852 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.07643 | -0.12294 | -0.003543 | 0.1225 | 7.2853 | 5.014 | 5.0175 | 0.075877 | 0.030337 | -0.08174 | -122.0194 | 0.069719 | -0.019731 | 0.062009 | -121.9116 | -121.8718 | 122.1119 | 122.0653 | 122.0198 | 45.412 | -121.993 | -0.029962 | 0.077799 | 0.11763 | 0.12855 | -122.0712
3457.4688 | 122.0764 | -0.068665 | 121.9208 | 1.4211e-13 | -0.038752 | 0.0039957 | 0.069201 | -0.0061087 | 0.061229 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018545 | 0.031767 | 0.014364 | 7.299 | 45.4028 | 5.0048 | 122.0707 | 122.0195 | 121.974 | -0.053899 | 0.02852 | 0.082776 | -0.056351 | -0.075739 | 0.0366 | 0.071851 | -0.11378 | 0.014766 | 0.14997 | 7.3677 | 5.0735 | 5.0587 | 0.098764 | 0.053224 | -0.045117 | -121.9965 | 0.097185 | 0.012314 | 0.057431 | -121.8842 | -121.8489 | 122.1394 | 122.0882 | 122.0427 | 45.4715 | -121.9747 | -0.007074 | 0.10526 | 0.14052 | 0.15144 | -122.0346
3459.1719 | 122.0993 | -0.054932 | 121.9345 | 1.4211e-13 | -0.038538 | 0.0044231 | 0.068988 | -0.0058951 | 0.061443 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018972 | 0.031339 | 0.014364 | 7.3494 | 45.412 | 5.046 | 122.0753 | 122.0241 | 121.9832 | -0.053899 | 0.019362 | 0.078197 | -0.056351 | -0.080318 | 0.0366 | 0.071851 | -0.11836 | 0.001033 | 0.14081 | 7.4043 | 5.1009 | 5.0999 | 0.08961 | 0.048649 | -0.063429 | -122.0148 | 0.074294 | -0.001419 | 0.06201 | -121.8979 | -121.8627 | 122.1303 | 122.0791 | 122.0381 | 45.4669 | -121.9884 | -0.025386 | 0.091532 | 0.12678 | 0.13313 | -122.0529
3460.9375 | 121.9986 | -0.091553 | 121.9711 | 1.4211e-13 | -0.038538 | 0.0039957 | 0.069201 | -0.0061087 | 0.061229 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031553 | 0.014364 | 7.3997 | 45.4257 | 5.101 | 122.0707 | 122.015 | 121.974 | -0.044742 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.071851 | -0.11836 | 0.046811 | 0.099613 | 7.4913 | 5.1925 | 5.1457 | 0.043831 | 0.00287 | -0.026808 | -122.0469 | 0.11549 | 0.035202 | 0.06201 | -121.9437 | -121.8993 | 122.1623 | 122.1065 | 122.0656 | 45.5173 | -122.0159 | 0.015814 | 0.11899 | 0.1634 | 0.17433 | -122.0895
3462.6562 | 122.0032 | -0.10986 | 122.0169 | 1.4211e-13 | -0.038111 | 0.0046369 | 0.069415 | -0.0058951 | 0.061229 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018972 | 0.031767 | 0.014578 | 7.4455 | 45.3983 | 5.1559 | 122.0707 | 122.0241 | 121.9786 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.084896 | 0.0366 | 0.07643 | -0.11378 | 0.060542 | 0.053836 | 7.5554 | 5.2658 | 5.2052 | 0.007212 | -0.038328 | -0.003919 | -122.1018 | 0.1338 | 0.044354 | 0.048273 | -121.9803 | -121.9405 | 122.1806 | 122.134 | 122.0884 | 45.5081 | -122.0662 | 0.024967 | 0.14646 | 0.18629 | 0.19264 | -122.1307
3464.4219 | 122.1222 | -0.050354 | 121.9254 | 1.4211e-13 | -0.038111 | 0.0046369 | 0.068988 | -0.0061087 | 0.061443 | -0.0022892 | -0.0046531 | -0.0016987 | 0.018545 | 0.031553 | 0.014578 | 7.5142 | 45.4486 | 5.22 | 122.0707 | 122.0241 | 121.9786 | -0.044742 | 0.019362 | 0.073618 | -0.056351 | -0.075739 | 0.032021 | 0.071851 | -0.11836 | 0.005612 | 0.14539 | 7.5645 | 5.2703 | 5.2647 | 0.098765 | 0.053225 | -0.068007 | -122.0011 | 0.069716 | -0.005997 | 0.06201 | -121.8933 | -121.8535 | 122.1211 | 122.0745 | 122.0289 | 45.499 | -121.9701 | -0.025385 | 0.082375 | 0.12221 | 0.12397 | -122.0437
3466.1406 | 122.049 | -0.10071 | 121.9666 | 1.4211e-13 | -0.038111 | 0.0048505 | 0.069629 | -0.0056813 | 0.061657 | -0.0099192 | -0.0042257 | -0.0012713 | 0.019399 | 0.031126 | 0.014578 | 7.5691 | 45.4898 | 5.2612 | 122.0753 | 122.0195 | 121.9786 | -0.044742 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.055966 | 0.10877 | 7.6698 | 5.3619 | 5.3059 | 0.052987 | 0.012026 | -0.013074 | -122.0423 | 0.12007 | 0.035199 | 0.048273 | -121.9391 | -121.8993 | 122.176 | 122.1202 | 122.0793 | 45.5905 | -122.0113 | 0.024969 | 0.12815 | 0.16798 | 0.18806 | -122.0803
3467.9062 | 122.1268 | -0.064087 | 121.9391 | 1.4211e-13 | -0.038111 | 0.0039957 | 0.069201 | -0.0054677 | 0.061443 | 0.0053413 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.014364 | 7.6332 | 45.499 | 5.3116 | 122.0707 | 122.0287 | 121.974 | -0.044742 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.022864 | 0.062694 | -0.11836 | 0.019345 | 0.13166 | 7.6973 | 5.3756 | 5.3563 | 0.089611 | 0.034913 | -0.054274 | -122.0148 | 0.088028 | -0.001422 | 0.052852 | -121.9162 | -121.8764 | 122.1348 | 122.0928 | 122.0381 | 45.5631 | -121.9838 | -0.011652 | 0.086951 | 0.12678 | 0.14228 | -122.0574
3469.6562 | 121.9986 | -0.10071 | 121.9711 | 1.4211e-13 | -0.037897 | 0.0042095 | 0.069415 | -0.0056813 | 0.062298 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018545 | 0.030912 | 0.01415 | 7.6836 | 45.5173 | 5.339 | 122.0799 | 122.0241 | 121.9832 | -0.049321 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.07643 | -0.11836 | 0.051387 | 0.10877 | 7.7843 | 5.4397 | 5.3883 | 0.052989 | 0.012028 | -0.017653 | -122.0514 | 0.12007 | 0.039778 | 0.057431 | -121.9391 | -121.8947 | 122.1806 | 122.1248 | 122.0839 | 45.618 | -122.0205 | 0.02039 | 0.13273 | 0.17714 | 0.18348 | -122.0895
3471.375 | 122.1176 | -0.050354 | 121.9299 | 1.4211e-13 | -0.037897 | 0.0044231 | 0.069415 | -0.0054677 | 0.061657 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.031553 | 0.014364 | 7.7248 | 45.5081 | 5.3894 | 122.0662 | 122.0241 | 121.9786 | -0.044742 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.027442 | 0.071851 | -0.11836 | 0.005612 | 0.13623 | 7.7751 | 5.4397 | 5.4341 | 0.094187 | 0.048647 | -0.068007 | -122.0057 | 0.078874 | -0.005997 | 0.06201 | -121.9025 | -121.8581 | 122.1165 | 122.0745 | 122.0289 | 45.5585 | -121.9747 | -0.025385 | 0.077796 | 0.12221 | 0.13771 | -122.0483
3473.1406 | 122.0032 | -0.10071 | 121.994 | 1.4211e-13 | -0.038538 | 0.0046369 | 0.069629 | -0.0056813 | 0.061443 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018972 | 0.031553 | 0.01415 | 7.7614 | 45.5265 | 5.4352 | 122.0707 | 122.0287 | 121.974 | -0.049321 | 0.02852 | 0.087354 | -0.056351 | -0.080318 | 0.027442 | 0.071851 | -0.1092 | 0.051387 | 0.076724 | 7.8621 | 5.5359 | 5.4845 | 0.034679 | -0.020019 | -0.008495 | -122.0743 | 0.12923 | 0.044357 | 0.052852 | -121.9666 | -121.9222 | 122.1715 | 122.1294 | 122.0747 | 45.6272 | -122.0433 | 0.02039 | 0.12815 | 0.17256 | 0.18806 | -122.1032
3474.8438 | 122.113 | -0.036621 | 121.9208 | 1.4211e-13 | -0.037897 | 0.0044231 | 0.069415 | -0.0054677 | 0.061657 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018758 | 0.031339 | 0.014364 | 7.8026 | 45.5493 | 5.4855 | 122.0799 | 122.0241 | 121.974 | -0.044742 | 0.014784 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | -0.008121 | 0.15912 | 7.8392 | 5.5221 | 5.5303 | 0.10334 | 0.053224 | -0.077161 | -121.9965 | 0.051405 | -0.01973 | 0.057431 | -121.8933 | -121.8535 | 122.1165 | 122.0607 | 122.0106 | 45.586 | -121.9655 | -0.039118 | 0.064063 | 0.10389 | 0.1194 | -122.0346
3476.6094 | 122.0444 | -0.082397 | 121.9803 | 1.4211e-13 | -0.037683 | 0.0044231 | 0.069629 | -0.0056813 | 0.061443 | -0.01755 | -0.0044395 | -0.0016987 | 0.019186 | 0.031553 | 0.01415 | 7.8438 | 45.531 | 5.4993 | 122.0707 | 122.015 | 121.9694 | -0.049321 | 0.019362 | 0.091933 | -0.056351 | -0.084896 | 0.0366 | 0.067272 | -0.1092 | 0.033076 | 0.090457 | 7.9262 | 5.5817 | 5.5486 | 0.034675 | -0.010864 | -0.026806 | -122.0652 | 0.10176 | 0.026046 | 0.052852 | -121.9437 | -121.913 | 122.1531 | 122.0974 | 122.0518 | 45.6134 | -122.0296 | -0.002499 | 0.119 | 0.14967 | 0.17433 | -122.0895
3478.375 | 122.081 | -0.073242 | 121.962 | 1.4211e-13 | -0.037683 | 0.0042095 | 0.069201 | -0.0056813 | 0.06187 | -0.032811 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.013937 | 7.8942 | 45.5677 | 5.5679 | 122.0753 | 122.0241 | 121.9694 | -0.044742 | 0.023941 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.12294 | 0.0285 | 0.11335 | 7.9674 | 5.6412 | 5.6127 | 0.062144 | 0.007447 | -0.049697 | -122.0423 | 0.097183 | 0.016891 | 0.066588 | -121.9345 | -121.8947 | 122.1486 | 122.0974 | 122.0427 | 45.6409 | -122.0067 | -0.007076 | 0.10068 | 0.14051 | 0.15144 | -122.0849
3480.0781 | 122.0535 | -0.073242 | 121.9574 | 1.4211e-13 | -0.03747 | 0.0046369 | 0.069415 | -0.0056813 | 0.061657 | -0.0022892 | -0.0037985 | -0.0016987 | 0.018758 | 0.031553 | 0.014578 | 7.9629 | 45.5722 | 5.6046 | 122.0662 | 122.0195 | 121.9786 | -0.044742 | 0.02852 | 0.082776 | -0.056351 | -0.075739 | 0.0366 | 0.067272 | -0.11378 | 0.0285 | 0.10877 | 8.0361 | 5.6778 | 5.6493 | 0.062143 | 0.021182 | -0.04054 | -122.0331 | 0.10176 | 0.016891 | 0.057431 | -121.9208 | -121.8901 | 122.1394 | 122.0928 | 122.0518 | 45.6455 | -122.0021 | -0.002497 | 0.10984 | 0.14051 | 0.15602 | -122.0712
3481.8438 | 122.049 | -0.086975 | 121.9849 | 1.4211e-13 | -0.03747 | 0.0044231 | 0.069415 | -0.0054677 | 0.062298 | 0.0053413 | -0.0048667 | -0.0016987 | 0.018758 | 0.031553 | 0.013937 | 7.9949 | 45.5814 | 5.6412 | 122.0753 | 122.0241 | 121.9786 | -0.049321 | 0.02852 | 0.087354 | -0.065509 | -0.075739 | 0.032021 | 0.062694 | -0.1092 | 0.037654 | 0.090458 | 8.0819 | 5.7282 | 5.6905 | 0.039256 | -0.006284 | -0.022228 | -122.0606 | 0.1155 | 0.021466 | 0.043694 | -121.9528 | -121.9222 | 122.1623 | 122.1111 | 122.0656 | 45.6684 | -122.0342 | 0.011236 | 0.119 | 0.14967 | 0.17433 | -122.0941
3483.6094 | 122.0215 | -0.10071 | 121.9849 | 1.4211e-13 | -0.03747 | 0.0044231 | 0.069415 | -0.0054677 | 0.062084 | -0.01755 | -0.0044395 | -0.0016987 | 0.018972 | 0.031339 | 0.01415 | 8.027 | 45.531 | 5.6916 | 122.0753 | 122.0195 | 121.974 | -0.049321 | 0.02852 | 0.082776 | -0.070087 | -0.075739 | 0.032021 | 0.067272 | -0.11836 | 0.051387 | 0.090458 | 8.1277 | 5.7923 | 5.7409 | 0.034677 | -0.010863 | -0.017653 | -122.0606 | 0.12923 | 0.030621 | 0.048274 | -121.9528 | -121.9176 | 122.176 | 122.1202 | 122.0747 | 45.6317 | -122.0342 | 0.024969 | 0.13273 | 0.16798 | 0.18348 | -122.1032
3485.3125 | 122.113 | -0.059509 | 121.9528 | 1.4211e-13 | -0.03747 | 0.0048505 | 0.069842 | -0.0052541 | 0.062084 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.01415 | 8.0911 | 45.531 | 5.7328 | 122.0662 | 122.0241 | 121.9786 | -0.053899 | 0.014784 | 0.082776 | -0.056351 | -0.084896 | 0.027442 | 0.067272 | -0.1092 | 0.00561 | 0.11334 | 8.1506 | 5.7923 | 5.7867 | 0.071299 | 0.025759 | -0.049694 | -122.0377 | 0.074293 | 0.003158 | 0.052852 | -121.9254 | -121.8855 | 122.1257 | 122.0836 | 122.0381 | 45.5905 | -122.0067 | -0.025387 | 0.086951 | 0.12678 | 0.14228 | -122.062
3487.0938 | 122.113 | -0.064087 | 121.9437 | 1.4211e-13 | -0.03747 | 0.0046369 | 0.069629 | -0.0054677 | 0.062084 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018545 | 0.031339 | 0.013937 | 8.1414 | 45.5631 | 5.7923 | 122.0707 | 122.0241 | 121.9786 | -0.044742 | 0.014784 | 0.078197 | -0.065509 | -0.075739 | 0.0366 | 0.071851 | -0.11378 | 0.019345 | 0.12708 | 8.2055 | 5.8564 | 5.837 | 0.080454 | 0.034914 | -0.049695 | -122.0194 | 0.078871 | -0.001422 | 0.048273 | -121.9071 | -121.8718 | 122.1348 | 122.0882 | 122.0427 | 45.6272 | -121.9884 | -0.011652 | 0.10069 | 0.13594 | 0.14228 | -122.0574
3488.8594 | 122.0032 | -0.12817 | 121.994 | 1.4211e-13 | -0.03747 | 0.0046369 | 0.069415 | -0.0054677 | 0.062084 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018758 | 0.031339 | 0.01415 | 8.2055 | 45.5585 | 5.8472 | 122.0707 | 122.0195 | 121.9832 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.078853 | 0.076724 | 8.3337 | 5.9754 | 5.8965 | 0.025521 | -0.010861 | 0.014392 | -122.0698 | 0.15669 | 0.067244 | 0.052852 | -121.9666 | -121.9267 | 122.1989 | 122.1477 | 122.1113 | 45.6867 | -122.0433 | 0.052435 | 0.15562 | 0.19545 | 0.21095 | -122.1078
3490.5625 | 122.0352 | -0.10529 | 121.9757 | 1.4211e-13 | -0.03747 | 0.0046369 | 0.069629 | -0.0054677 | 0.06187 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.014364 | 8.2467 | 45.5677 | 5.8976 | 122.0662 | 122.0241 | 121.9694 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.0366 | 0.071851 | -0.11378 | 0.051387 | 0.090456 | 8.352 | 6.0029 | 5.9515 | 0.048411 | -0.006286 | -0.008496 | -122.056 | 0.12923 | 0.039777 | 0.048273 | -121.9391 | -121.9039 | 122.1715 | 122.1294 | 122.0747 | 45.6729 | -122.0296 | 0.024968 | 0.14189 | 0.17714 | 0.18348 | -122.0895
3492.3281 | 122.1359 | -0.064087 | 121.9482 | 1.4211e-13 | -0.037683 | 0.0044231 | 0.069415 | -0.0050403 | 0.062084 | -0.0099192 | -0.0040121 | -0.0014849 | 0.018331 | 0.031553 | 0.014364 | 8.2788 | 45.5127 | 5.9571 | 122.0707 | 122.0241 | 121.9694 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.1092 | 0.019345 | 0.1225 | 8.3429 | 6.0212 | 6.0018 | 0.075877 | 0.02118 | -0.045116 | -122.024 | 0.092607 | 0.003157 | 0.048273 | -121.9208 | -121.881 | 122.1348 | 122.0882 | 122.0335 | 45.5768 | -121.993 | -0.011652 | 0.091529 | 0.13136 | 0.14686 | -122.0574
3494.0312 | 122.1039 | -0.050354 | 121.9345 | 1.4211e-13 | -0.037256 | 0.0042095 | 0.069629 | -0.0050403 | 0.062084 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018545 | 0.031767 | 0.014364 | 8.32 | 45.499 | 6.012 | 122.0707 | 122.0241 | 121.9786 | -0.044742 | 0.02852 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.062694 | -0.11378 | 0.005612 | 0.13623 | 8.3703 | 6.0624 | 6.0568 | 0.08961 | 0.04407 | -0.063428 | -122.0102 | 0.078874 | -0.005997 | 0.057431 | -121.9071 | -121.8718 | 122.1211 | 122.0745 | 122.0289 | 45.5493 | -121.9793 | -0.025385 | 0.077796 | 0.11305 | 0.13313 | -122.0483
3495.7969 | 122.0901 | -0.07782 | 121.9437 | 1.4211e-13 | -0.037256 | 0.0046369 | 0.070056 | -0.0052541 | 0.062298 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.014364 | 8.3841 | 45.4852 | 6.0624 | 122.0662 | 122.0287 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.028499 | 0.1225 | 8.4619 | 6.1402 | 6.1117 | 0.085033 | 0.030335 | -0.035962 | -122.024 | 0.10176 | 0.021469 | 0.057431 | -121.9162 | -121.8764 | 122.144 | 122.1065 | 122.0518 | 45.5631 | -121.993 | -0.002498 | 0.10526 | 0.14509 | 0.1606 | -122.0574
3497.5781 | 121.9894 | -0.11902 | 121.9849 | 1.4211e-13 | -0.037042 | 0.0046369 | 0.069415 | -0.0052541 | 0.062084 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031767 | 0.014364 | 8.4161 | 45.5173 | 6.1128 | 122.0707 | 122.0241 | 121.9786 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.069698 | 0.08588 | 8.5351 | 6.2318 | 6.1621 | 0.039256 | -0.006284 | 0.000658 | -122.0652 | 0.14754 | 0.058089 | 0.057431 | -121.9528 | -121.9176 | 122.1898 | 122.1431 | 122.0976 | 45.6363 | -122.0342 | 0.038701 | 0.15104 | 0.18629 | 0.2018 | -122.1032
3499.3438 | 122.081 | -0.059509 | 121.9437 | 1.4211e-13 | -0.037042 | 0.0044231 | 0.069629 | -0.0050403 | 0.062298 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018758 | 0.031553 | 0.014364 | 8.4344 | 45.5127 | 6.1402 | 122.0753 | 122.0195 | 121.9786 | -0.044742 | 0.023941 | 0.087354 | -0.065509 | -0.084896 | 0.027442 | 0.071851 | -0.11836 | 0.014767 | 0.13166 | 8.4939 | 6.1997 | 6.185 | 0.075875 | 0.034914 | -0.058852 | -122.0286 | 0.08345 | -0.006 | 0.052852 | -121.9162 | -121.8718 | 122.1348 | 122.079 | 122.0381 | 45.5722 | -121.9884 | -0.025387 | 0.086951 | 0.13136 | 0.14686 | -122.062
3501.0625 | 121.9986 | -0.10529 | 121.9803 | 1.4211e-13 | -0.037042 | 0.0048505 | 0.069629 | -0.0050403 | 0.062511 | -0.01755 | -0.0046531 | -0.0016987 | 0.018758 | 0.031553 | 0.014578 | 8.5031 | 45.4944 | 6.186 | 122.0707 | 122.0241 | 121.974 | -0.044742 | 0.02852 | 0.087354 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11836 | 0.060544 | 0.090457 | 8.6084 | 6.2913 | 6.2307 | 0.043833 | -0.006286 | -0.013075 | -122.0606 | 0.13381 | 0.044356 | 0.057431 | -121.9483 | -121.913 | 122.176 | 122.1294 | 122.0793 | 45.5997 | -122.025 | 0.024968 | 0.13731 | 0.17256 | 0.19264 | -122.0986
3502.8281 | 122.0673 | -0.09613 | 121.9574 | 1.4211e-13 | -0.037042 | 0.0044231 | 0.069629 | -0.0052541 | 0.062298 | -0.02518 | -0.0046531 | -0.0014849 | 0.018758 | 0.031981 | 0.01415 | 8.5123 | 45.5173 | 6.2318 | 122.0707 | 122.0241 | 121.974 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.084896 | 0.0366 | 0.067272 | -0.11836 | 0.042231 | 0.11335 | 8.6084 | 6.3279 | 6.2857 | 0.066722 | 0.016603 | -0.022231 | -122.0423 | 0.12007 | 0.0352 | 0.057431 | -121.9208 | -121.8901 | 122.1669 | 122.1202 | 122.0701 | 45.6134 | -122.0113 | 0.011234 | 0.13273 | 0.1634 | 0.17433 | -122.0758
3504.5938 | 122.1268 | -0.07782 | 121.9299 | 1.4211e-13 | -0.037042 | 0.0046369 | 0.069629 | -0.0050403 | 0.062298 | -0.0022892 | -0.0042257 | -0.0021259 | 0.018972 | 0.031339 | 0.014578 | 8.5535 | 45.499 | 6.3234 | 122.0662 | 122.0195 | 121.9786 | -0.044742 | 0.023941 | 0.073618 | -0.056351 | -0.080318 | 0.032021 | 0.071851 | -0.11378 | 0.033078 | 0.13623 | 8.6313 | 6.4012 | 6.3681 | 0.089608 | 0.048647 | -0.035962 | -122.0102 | 0.10176 | 0.021469 | 0.057431 | -121.8979 | -121.8581 | 122.144 | 122.0974 | 122.0564 | 45.5768 | -121.9747 | -0.002498 | 0.10984 | 0.14967 | 0.15144 | -122.0437
3506.3594 | 122.1359 | -0.073242 | 121.9254 | 1.4211e-13 | -0.03747 | 0.0046369 | 0.070056 | -0.0043993 | 0.062725 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031767 | 0.014364 | 8.613 | 45.5265 | 6.3371 | 122.0662 | 122.015 | 121.9832 | -0.049321 | 0.023941 | 0.078197 | -0.065509 | -0.080318 | 0.032021 | 0.067272 | -0.11378 | 0.023921 | 0.14081 | 8.6862 | 6.4103 | 6.3864 | 0.089607 | 0.057804 | -0.04054 | -122.0057 | 0.097183 | 0.007733 | 0.048273 | -121.8933 | -121.8581 | 122.1394 | 122.0882 | 122.0564 | 45.5997 | -121.9747 | -0.007076 | 0.10526 | 0.14051 | 0.15144 | -122.0391
3508.0625 | 122.1222 | -0.050354 | 121.9345 | 1.4211e-13 | -0.036829 | 0.0046369 | 0.069629 | -0.0046131 | 0.062511 | -0.01755 | -0.0042257 | -0.0014849 | 0.018972 | 0.031767 | 0.014364 | 8.6405 | 45.4898 | 6.4515 | 122.0662 | 122.0195 | 121.9786 | -0.044742 | 0.033099 | 0.078197 | -0.051772 | -0.084896 | 0.032021 | 0.067272 | -0.11378 | 0.005612 | 0.13165 | 8.6908 | 6.5019 | 6.4963 | 0.085031 | 0.04407 | -0.063428 | -122.0194 | 0.083453 | -0.001418 | 0.06201 | -121.9025 | -121.8672 | 122.1165 | 122.0699 | 122.0289 | 45.5402 | -121.9793 | -0.034542 | 0.082375 | 0.11763 | 0.12855 | -122.0483
3509.8281 | 122.0764 | -0.086975 | 121.9345 | 1.4211e-13 | -0.036829 | 0.0046369 | 0.069842 | -0.0046131 | 0.062511 | -0.01755 | -0.0046531 | -0.0016987 | 0.018758 | 0.031553 | 0.01415 | 8.6817 | 45.5081 | 6.4653 | 122.0662 | 122.0195 | 121.9786 | -0.049321 | 0.02852 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.067272 | -0.11836 | 0.037654 | 0.13165 | 8.7686 | 6.5523 | 6.5146 | 0.085031 | 0.04407 | -0.031386 | -122.0057 | 0.1155 | 0.026045 | 0.057431 | -121.8979 | -121.8672 | 122.1531 | 122.1065 | 122.0656 | 45.5951 | -121.9838 | 0.015814 | 0.12357 | 0.15425 | 0.17433 | -122.0529
3511.5469 | 122.0581 | -0.091553 | 121.962 | 1.4211e-13 | -0.037042 | 0.0046369 | 0.069629 | -0.0046131 | 0.062511 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.031553 | 0.01415 | 8.732 | 45.5356 | 6.4882 | 122.0707 | 122.0241 | 121.9694 | -0.044742 | 0.02852 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11836 | 0.046811 | 0.10877 | 8.8236 | 6.5797 | 6.5329 | 0.062144 | 0.007447 | -0.026808 | -122.0377 | 0.12007 | 0.030623 | 0.057431 | -121.9345 | -121.8901 | 122.1623 | 122.1157 | 122.061 | 45.6272 | -122.0067 | 0.015814 | 0.11899 | 0.1634 | 0.16975 | -122.0803
3513.3125 | 121.9986 | -0.10986 | 121.9849 | 1.4211e-13 | -0.036829 | 0.0046369 | 0.070056 | -0.0048267 | 0.062298 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.031767 | 0.01415 | 8.7778 | 45.5265 | 6.5385 | 122.0753 | 122.0241 | 121.9694 | -0.049321 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.032021 | 0.067272 | -0.11378 | 0.060542 | 0.090458 | 8.8877 | 6.6484 | 6.5879 | 0.039256 | -0.015441 | -0.003919 | -122.0606 | 0.12923 | 0.048933 | 0.052852 | -121.9528 | -121.9176 | 122.1852 | 122.134 | 122.0793 | 45.6363 | -122.0342 | 0.034124 | 0.14188 | 0.17713 | 0.19264 | -122.0986
3515.0781 | 122.0123 | -0.11444 | 121.9849 | 1.4211e-13 | -0.036829 | 0.0044231 | 0.069842 | -0.0048267 | 0.063152 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018972 | 0.031767 | 0.013723 | 8.8328 | 45.499 | 6.6164 | 122.0707 | 122.015 | 121.9786 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.06512 | 0.08588 | 8.9472 | 6.7308 | 6.6657 | 0.030098 | -0.006284 | 0.000659 | -122.0652 | 0.13838 | 0.053511 | 0.052852 | -121.9574 | -121.9176 | 122.1852 | 122.1294 | 122.093 | 45.6134 | -122.0342 | 0.034123 | 0.14188 | 0.18171 | 0.19264 | -122.0986
3516.8594 | 122.0215 | -0.09613 | 122.0032 | 1.4211e-13 | -0.036829 | 0.0044231 | 0.069842 | -0.0043993 | 0.062939 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.031767 | 0.014578 | 8.8007 | 45.5173 | 6.6484 | 122.0707 | 122.0241 | 121.974 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.071851 | -0.12294 | 0.042231 | 0.067569 | 8.8968 | 6.7445 | 6.7023 | 0.020945 | -0.029174 | -0.026809 | -122.0835 | 0.12465 | 0.0352 | 0.062009 | -121.9757 | -121.9313 | 122.1669 | 122.1202 | 122.0701 | 45.6134 | -122.0571 | 0.015812 | 0.12357 | 0.16798 | 0.17891 | -122.1261
3518.5625 | 122.0306 | -0.091553 | 121.9849 | 1.4211e-13 | -0.037042 | 0.0044231 | 0.069629 | -0.0048267 | 0.062939 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031767 | 0.014364 | 8.906 | 45.5173 | 6.6988 | 122.0662 | 122.0195 | 121.9786 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11836 | 0.042232 | 0.081301 | 8.9976 | 6.7903 | 6.7481 | 0.034677 | -0.006284 | -0.026808 | -122.0606 | 0.11549 | 0.030623 | 0.057431 | -121.9574 | -121.913 | 122.1577 | 122.1111 | 122.0701 | 45.6088 | -122.0342 | 0.015814 | 0.11899 | 0.1634 | 0.16517 | -122.1032
3520.3281 | 122.1176 | -0.068665 | 121.9345 | 1.4211e-13 | -0.036401 | 0.0046369 | 0.069842 | -0.0046131 | 0.062725 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018758 | 0.031767 | 0.013937 | 8.9472 | 45.5036 | 6.7583 | 122.0707 | 122.0195 | 121.9786 | -0.049321 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.027442 | 0.067272 | -0.12294 | 0.019344 | 0.13623 | 9.0159 | 6.827 | 6.8076 | 0.085031 | 0.04407 | -0.054274 | -122.0057 | 0.088027 | 0.003156 | 0.05743 | -121.9071 | -121.8672 | 122.1394 | 122.0882 | 122.0472 | 45.5722 | -121.9838 | -0.002496 | 0.096107 | 0.13594 | 0.14686 | -122.0574
3522.0469 | 122.1039 | -0.054932 | 121.9711 | 1.4211e-13 | -0.036615 | 0.0048505 | 0.069629 | -0.0046131 | 0.062725 | -0.0022892 | -0.0046531 | -0.0014849 | 0.018758 | 0.031553 | 0.014578 | 8.9838 | 45.5127 | 6.7995 | 122.0707 | 122.0195 | 121.974 | -0.044742 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.032021 | 0.071851 | -0.1092 | 0.01019 | 0.099613 | 9.0388 | 6.8544 | 6.8442 | 0.04841 | 0.00287 | -0.054271 | -122.0423 | 0.078873 | -0.001419 | 0.052852 | -121.9391 | -121.8993 | 122.1257 | 122.0745 | 122.0289 | 45.5676 | -122.0159 | -0.016229 | 0.086953 | 0.12678 | 0.13771 | -122.0803
3523.8125 | 121.9711 | -0.11444 | 121.994 | 1.4211e-13 | -0.036615 | 0.0042095 | 0.069842 | -0.0046131 | 0.062939 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018758 | 0.031767 | 0.014364 | 9.0525 | 45.5402 | 6.9185 | 122.0662 | 122.0195 | 121.9786 | -0.053899 | 0.033099 | 0.082776 | -0.06093 | -0.089475 | 0.032021 | 0.071851 | -0.11378 | 0.060542 | 0.072145 | 9.167 | 7.033 | 6.9724 | 0.025521 | -0.01544 | 0.000659 | -122.0835 | 0.14754 | 0.053511 | 0.052852 | -121.962 | -121.9222 | 122.1806 | 122.134 | 122.093 | 45.6546 | -122.0479 | 0.024966 | 0.14646 | 0.18629 | 0.19722 | -122.1078
3525.5781 | 122.0581 | -0.07782 | 121.9437 | 1.4211e-13 | -0.036829 | 0.0046369 | 0.070056 | -0.0041857 | 0.063152 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018331 | 0.031553 | 0.014364 | 9.1029 | 45.531 | 6.9643 | 122.0662 | 122.015 | 121.9786 | -0.049321 | 0.033099 | 0.082776 | -0.065509 | -0.071161 | 0.027442 | 0.071851 | -0.11378 | 0.028499 | 0.1225 | 9.1807 | 7.0421 | 7.0136 | 0.071296 | 0.034914 | -0.035962 | -122.0148 | 0.11092 | 0.012311 | 0.048273 | -121.9162 | -121.8718 | 122.144 | 122.0928 | 122.0564 | 45.6089 | -121.993 | 0.006659 | 0.10526 | 0.14967 | 0.1606 | -122.0574
3527.3594 | 122.1176 | -0.064087 | 121.9208 | 1.4211e-13 | -0.036188 | 0.0050641 | 0.069842 | -0.0043993 | 0.063152 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031767 | 0.013937 | 9.199 | 45.5219 | 7.0605 | 122.0616 | 122.0287 | 121.974 | -0.044742 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.032021 | 0.062694 | -0.11378 | 0.019345 | 0.14081 | 9.2631 | 7.1245 | 7.1052 | 0.10792 | 0.053224 | -0.049695 | -121.9965 | 0.088028 | -0.001422 | 0.048273 | -121.8888 | -121.8581 | 122.1257 | 122.0928 | 122.0381 | 45.586 | -121.9655 | -0.011652 | 0.096108 | 0.12678 | 0.14686 | -122.0346
3529.0625 | 121.9849 | -0.12817 | 121.994 | 1.4211e-13 | -0.036188 | 0.0048505 | 0.069842 | -0.0043993 | 0.063366 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018758 | 0.031767 | 0.014364 | 9.2082 | 45.5173 | 7.065 | 122.0662 | 122.0241 | 121.9786 | -0.049321 | 0.02852 | 0.078197 | -0.056351 | -0.080318 | 0.027442 | 0.07643 | -0.1092 | 0.078853 | 0.072145 | 9.3364 | 7.1932 | 7.1144 | 0.0301 | -0.01544 | 0.018971 | -122.0743 | 0.15669 | 0.071823 | 0.052852 | -121.9666 | -121.9176 | 122.1943 | 122.1523 | 122.1068 | 45.6455 | -122.0433 | 0.047856 | 0.15562 | 0.2046 | 0.20637 | -122.1032
3530.8438 | 122.0352 | -0.09613 | 121.9849 | 1.4211e-13 | -0.035974 | 0.0046369 | 0.070056 | -0.0041857 | 0.063366 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018545 | 0.031339 | 0.014578 | 9.2677 | 45.531 | 7.1703 | 122.0662 | 122.015 | 121.9786 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.027442 | 0.067272 | -0.1092 | 0.046809 | 0.081301 | 9.3638 | 7.2665 | 7.2197 | 0.030098 | -0.006284 | -0.013073 | -122.056 | 0.12007 | 0.039779 | 0.052852 | -121.9574 | -121.9176 | 122.1623 | 122.1111 | 122.0747 | 45.6272 | -122.0342 | 0.024969 | 0.12357 | 0.1634 | 0.17891 | -122.0941
3532.625 | 122.1222 | -0.059509 | 121.9437 | 1.4211e-13 | -0.035974 | 0.0048505 | 0.07027 | -0.0041857 | 0.06358 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.032194 | 0.014578 | 9.3226 | 45.5081 | 7.2115 | 122.0662 | 122.0195 | 121.9694 | -0.044742 | 0.033099 | 0.087354 | -0.065509 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | 0.014767 | 0.1225 | 9.3822 | 7.271 | 7.2563 | 0.075875 | 0.025757 | -0.054273 | -122.0194 | 0.092608 | -0.006 | 0.048273 | -121.9162 | -121.8718 | 122.1257 | 122.079 | 122.0289 | 45.5676 | -121.9884 | -0.01623 | 0.086951 | 0.13136 | 0.14686 | -122.0574
3534.3281 | 122.0718 | -0.073242 | 121.9482 | 1.4211e-13 | -0.036188 | 0.0048505 | 0.069842 | -0.0039721 | 0.063366 | -0.02518 | -0.0042257 | -0.0016987 | 0.018758 | 0.031553 | 0.014364 | 9.3776 | 45.4944 | 7.2299 | 122.0616 | 122.0287 | 121.974 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.1092 | 0.0285 | 0.11334 | 9.4508 | 7.3031 | 7.2746 | 0.080456 | 0.025758 | -0.035961 | -122.0286 | 0.097183 | 0.012312 | 0.048273 | -121.9208 | -121.8855 | 122.1348 | 122.1019 | 122.0472 | 45.5676 | -121.993 | -0.007076 | 0.10068 | 0.13594 | 0.15144 | -122.0574
3536.0781 | 121.9894 | -0.10986 | 121.9894 | 1.4211e-13 | -0.03576 | 0.0050641 | 0.070056 | -0.0043993 | 0.063366 | -0.01755 | -0.0046531 | -0.0019123 | 0.018758 | 0.031553 | 0.014364 | 9.4234 | 45.4486 | 7.2894 | 122.0616 | 122.0333 | 121.974 | -0.049321 | 0.023941 | 0.087354 | -0.06093 | -0.080318 | 0.027442 | 0.07643 | -0.11378 | 0.060542 | 0.072145 | 9.5332 | 7.3992 | 7.3387 | 0.043836 | -0.015441 | -0.003919 | -122.0698 | 0.1338 | 0.048933 | 0.052852 | -121.962 | -121.913 | 122.1714 | 122.1431 | 122.0839 | 45.5585 | -122.0388 | 0.029545 | 0.13731 | 0.18629 | 0.19722 | -122.1032
3537.7812 | 122.0306 | -0.091553 | 121.962 | 1.4211e-13 | -0.036188 | 0.0050641 | 0.070056 | -0.0041857 | 0.06358 | -0.0022892 | -0.0040121 | -0.0014849 | 0.018758 | 0.032194 | 0.01415 | 9.5287 | 45.4715 | 7.2985 | 122.0707 | 122.0241 | 121.9832 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.084896 | 0.022864 | 0.071851 | -0.11378 | 0.042232 | 0.10877 | 9.6202 | 7.3901 | 7.3478 | 0.062144 | 0.021183 | -0.022229 | -122.0469 | 0.11549 | 0.035202 | 0.057431 | -121.9391 | -121.8901 | 122.1623 | 122.1157 | 122.0747 | 45.5631 | -122.0113 | 0.006657 | 0.11442 | 0.1634 | 0.17433 | -122.0758
3539.5469 | 122.1176 | -0.059509 | 121.9528 | 1.4211e-13 | -0.035974 | 0.0046369 | 0.070056 | -0.0039721 | 0.06358 | 0.0053413 | -0.0046531 | -0.0014849 | 0.018758 | 0.031553 | 0.014578 | 9.5928 | 45.4486 | 7.3947 | 122.0662 | 122.0287 | 121.9694 | -0.049321 | 0.019362 | 0.082776 | -0.056351 | -0.080318 | 0.032021 | 0.07643 | -0.12294 | 0.010188 | 0.11334 | 9.6523 | 7.4542 | 7.444 | 0.075878 | 0.016602 | -0.06343 | -122.0331 | 0.078871 | 0.003158 | 0.066588 | -121.9208 | -121.8764 | 122.1257 | 122.0882 | 122.0289 | 45.5081 | -122.0021 | -0.020809 | 0.09153 | 0.13594 | 0.14228 | -122.0758
3541.3125 | 122.1039 | -0.059509 | 121.9482 | 1.4211e-13 | -0.035974 | 0.0046369 | 0.069629 | -0.0039721 | 0.06358 | -0.0099192 | -0.0046531 | -0.0012713 | 0.018972 | 0.031981 | 0.01415 | 9.6386 | 45.4532 | 7.413 | 122.0616 | 122.015 | 121.974 | -0.044742 | 0.023941 | 0.078197 | -0.056351 | -0.075739 | 0.027442 | 0.071851 | -0.12294 | 0.014767 | 0.11334 | 9.6981 | 7.4725 | 7.4577 | 0.066719 | 0.025758 | -0.06343 | -122.024 | 0.08345 | 0.003158 | 0.066588 | -121.9208 | -121.8764 | 122.1211 | 122.0745 | 122.0335 | 45.5127 | -121.993 | -0.01623 | 0.086951 | 0.13136 | 0.13771 | -122.0712
3543.0156 | 122.0306 | -0.082397 | 121.994 | 1.4211e-13 | -0.035547 | 0.0046369 | 0.07027 | -0.0041857 | 0.063366 | -0.0099192 | -0.0042257 | -0.0014849 | 0.019399 | 0.031767 | 0.014364 | 9.6431 | 45.3296 | 7.4908 | 122.0707 | 122.015 | 121.9694 | -0.049321 | 0.023941 | 0.087354 | -0.065509 | -0.075739 | 0.022864 | 0.067272 | -0.11836 | 0.033076 | 0.076724 | 9.7255 | 7.5732 | 7.5401 | 0.020942 | -0.024597 | -0.035964 | -122.0698 | 0.10634 | 0.016888 | 0.052852 | -121.9712 | -121.9267 | 122.1531 | 122.0974 | 122.0518 | 45.412 | -122.0433 | 0.006658 | 0.10526 | 0.14967 | 0.16975 | -122.1124
3544.7812 | 122.0078 | -0.10529 | 121.9528 | 1.4211e-13 | -0.035547 | 0.0046369 | 0.069842 | -0.0037583 | 0.064007 | -0.01755 | -0.0042257 | -0.0016987 | 0.018545 | 0.031553 | 0.01415 | 9.634 | 45.3754 | 7.532 | 122.0662 | 122.0195 | 121.974 | -0.044742 | 0.02852 | 0.087354 | -0.06093 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.060544 | 0.11334 | 9.7393 | 7.6373 | 7.5768 | 0.06672 | 0.02118 | -0.008496 | -122.0286 | 0.13381 | 0.044356 | 0.052852 | -121.9254 | -121.8855 | 122.1715 | 122.1248 | 122.0793 | 45.4806 | -121.9976 | 0.029547 | 0.13273 | 0.17256 | 0.19264 | -122.0666
3546.5469 | 122.0947 | -0.059509 | 121.9849 | 1.4211e-13 | -0.035547 | 0.0046369 | 0.069842 | -0.0039721 | 0.06358 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.031553 | 0.014364 | 9.7576 | 45.3525 | 7.5274 | 122.0707 | 122.0195 | 121.9786 | -0.040163 | 0.02852 | 0.082776 | -0.065509 | -0.071161 | 0.0366 | 0.067272 | -0.11378 | 0.019346 | 0.08588 | 9.8171 | 7.5869 | 7.5676 | 0.034677 | -0.006284 | -0.054273 | -122.056 | 0.088029 | -0.006 | 0.048273 | -121.9483 | -121.9176 | 122.1303 | 122.079 | 122.0381 | 45.412 | -122.025 | -0.011652 | 0.096109 | 0.12678 | 0.14228 | -122.0986
3548.25 | 122.0352 | -0.10071 | 121.9986 | 1.4211e-13 | -0.035333 | 0.0048505 | 0.070056 | -0.0037583 | 0.06358 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018758 | 0.031981 | 0.014364 | 9.8537 | 45.3387 | 7.6785 | 122.0616 | 122.0195 | 121.9694 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.084896 | 0.022864 | 0.067272 | -0.11378 | 0.051387 | 0.06299 | 9.9544 | 7.7792 | 7.7278 | 0.020944 | -0.029174 | -0.013074 | -122.0835 | 0.12465 | 0.039778 | 0.052852 | -121.9757 | -121.9313 | 122.1623 | 122.1202 | 122.0701 | 45.4394 | -122.0479 | 0.015812 | 0.12357 | 0.16798 | 0.18348 | -122.1124
3550.0156 | 122.1268 | -0.059509 | 121.9162 | 1.4211e-13 | -0.035547 | 0.0046369 | 0.069842 | -0.0039721 | 0.06358 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018758 | 0.031339 | 0.014364 | 9.8675 | 45.3204 | 7.6968 | 122.0616 | 122.0195 | 121.974 | -0.044742 | 0.02852 | 0.082776 | -0.065509 | -0.075739 | 0.0366 | 0.062694 | -0.11836 | 0.014767 | 0.14539 | 9.927 | 7.7563 | 7.7416 | 0.10334 | 0.057801 | -0.058852 | -121.9919 | 0.088029 | -0.006 | 0.052852 | -121.8796 | -121.8535 | 122.1211 | 122.079 | 122.0335 | 45.3799 | -121.9609 | -0.01623 | 0.096109 | 0.1222 | 0.14228 | -122.0346
3551.7812 | 122.0535 | -0.09613 | 121.9574 | 1.4211e-13 | -0.035119 | 0.0050641 | 0.07027 | -0.0035447 | 0.064007 | -0.01755 | -0.0046531 | -0.0021259 | 0.019186 | 0.031981 | 0.014364 | 9.9453 | 45.3296 | 7.8159 | 122.0616 | 122.0241 | 121.9786 | -0.044742 | 0.02852 | 0.078197 | -0.065509 | -0.075739 | 0.027442 | 0.062694 | -0.11836 | 0.051388 | 0.10419 | 10.0414 | 7.912 | 7.8606 | 0.066722 | 0.021182 | -0.022231 | -122.0331 | 0.12465 | 0.030621 | 0.052852 | -121.93 | -121.8947 | 122.1577 | 122.1202 | 122.0747 | 45.4257 | -122.0021 | 0.020391 | 0.12357 | 0.15882 | 0.17433 | -122.0758
3553.5469 | 122.0261 | -0.10071 | 121.9849 | 1.4211e-13 | -0.035333 | 0.0048505 | 0.07027 | -0.0039721 | 0.064007 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031767 | 0.014578 | 10.0231 | 45.3158 | 7.8983 | 122.0616 | 122.0195 | 121.9648 | -0.049321 | 0.02852 | 0.082776 | -0.070087 | -0.075739 | 0.0366 | 0.067272 | -0.11378 | 0.051387 | 0.076723 | 10.1238 | 7.999 | 7.9476 | 0.034677 | -0.02002 | -0.013074 | -122.0606 | 0.12923 | 0.030621 | 0.043695 | -121.9483 | -121.9176 | 122.1623 | 122.1202 | 122.0656 | 45.4165 | -122.0342 | 0.024969 | 0.13731 | 0.16798 | 0.18348 | -122.0986
3555.3125 | 122.081 | -0.068665 | 121.962 | 1.4211e-13 | -0.035333 | 0.0048505 | 0.070056 | -0.0037583 | 0.064221 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031553 | 0.014364 | 10.0918 | 45.2792 | 7.967 | 122.0662 | 122.0195 | 121.9694 | -0.049321 | 0.02852 | 0.082776 | -0.070087 | -0.075739 | 0.027442 | 0.07643 | -0.12294 | 0.019344 | 0.10419 | 10.1605 | 8.0356 | 8.0163 | 0.057565 | 0.007447 | -0.054274 | -122.0377 | 0.097185 | -0.001422 | 0.052852 | -121.9345 | -121.8855 | 122.1348 | 122.0882 | 122.0381 | 45.3479 | -122.0113 | -0.007074 | 0.096107 | 0.1451 | 0.15144 | -122.0849
3557.0781 | 122.1268 | -0.059509 | 121.9299 | 1.4211e-13 | -0.034692 | 0.0050641 | 0.070056 | -0.0035447 | 0.064221 | -0.01755 | -0.0042257 | -0.0016987 | 0.018972 | 0.031553 | 0.014791 | 10.1605 | 45.2975 | 8.0311 | 122.0616 | 122.015 | 121.974 | -0.049321 | 0.02852 | 0.078197 | -0.065509 | -0.080318 | 0.032021 | 0.071851 | -0.11836 | 0.010188 | 0.13165 | 10.22 | 8.0906 | 8.0804 | 0.085029 | 0.044068 | -0.058852 | -122.0102 | 0.088029 | -0.006 | 0.052852 | -121.8979 | -121.8581 | 122.1211 | 122.0745 | 122.0335 | 45.357 | -121.9793 | -0.020809 | 0.09153 | 0.13136 | 0.13771 | -122.0483
3558.7812 | 122.113 | -0.068665 | 121.9208 | 1.4211e-13 | -0.034692 | 0.0048505 | 0.07027 | -0.0035447 | 0.064007 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018758 | 0.031553 | 0.01415 | 10.2475 | 45.27 | 8.0814 | 122.0616 | 122.0195 | 121.974 | -0.049321 | 0.019362 | 0.082776 | -0.056351 | -0.075739 | 0.027442 | 0.067272 | -0.12294 | 0.019344 | 0.14081 | 10.3161 | 8.1501 | 8.1307 | 0.098764 | 0.053224 | -0.054274 | -121.9965 | 0.088027 | 0.012314 | 0.066588 | -121.8933 | -121.8535 | 122.1303 | 122.0882 | 122.0427 | 45.3387 | -121.9701 | -0.007074 | 0.096107 | 0.13594 | 0.15144 | -122.0437
3560.5469 | 122.0306 | -0.073242 | 121.9849 | 1.4211e-13 | -0.034906 | 0.0048505 | 0.070056 | -0.0033311 | 0.064434 | -0.01755 | -0.0042257 | -0.0014849 | 0.018545 | 0.031767 | 0.01415 | 10.3528 | 45.2746 | 8.1592 | 122.0662 | 122.0104 | 121.9786 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.080318 | 0.027442 | 0.067272 | -0.11378 | 0.0285 | 0.081301 | 10.426 | 8.2325 | 8.204 | 0.025519 | -0.006284 | -0.04054 | -122.0652 | 0.097183 | 0.012312 | 0.052852 | -121.9574 | -121.9176 | 122.1394 | 122.0836 | 122.0518 | 45.3479 | -122.0296 | -0.007076 | 0.10068 | 0.14051 | 0.15144 | -122.0986
3562.3281 | 122.0398 | -0.09613 | 121.9711 | 1.4211e-13 | -0.034906 | 0.0050641 | 0.070483 | -0.0033311 | 0.064221 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.014364 | 10.394 | 45.2975 | 8.2417 | 122.0662 | 122.0241 | 121.974 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.032021 | 0.067272 | -0.12294 | 0.046809 | 0.095034 | 10.4901 | 8.3378 | 8.291 | 0.052989 | 0.00287 | -0.026809 | -122.0469 | 0.12007 | 0.039779 | 0.066588 | -121.9391 | -121.9039 | 122.1623 | 122.1202 | 122.0701 | 45.3937 | -122.0205 | 0.020391 | 0.12815 | 0.1634 | 0.17891 | -122.0941
3564.0938 | 122.0032 | -0.10986 | 121.9711 | 1.4211e-13 | -0.034692 | 0.0048505 | 0.069842 | -0.0035447 | 0.064434 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031553 | 0.014364 | 10.4352 | 45.27 | 8.3057 | 122.0616 | 122.015 | 121.974 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.022864 | 0.071851 | -0.11378 | 0.065121 | 0.090456 | 10.5451 | 8.4156 | 8.3505 | 0.043831 | 0.00287 | -0.003919 | -122.0514 | 0.13838 | 0.048933 | 0.052852 | -121.9483 | -121.8993 | 122.1714 | 122.1248 | 122.0839 | 45.3799 | -122.0159 | 0.029545 | 0.13273 | 0.18171 | 0.19264 | -122.0849
3565.7969 | 122.0627 | -0.068665 | 121.9162 | 1.4211e-13 | -0.034692 | 0.0050641 | 0.070697 | -0.0033311 | 0.064221 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018758 | 0.031767 | 0.014578 | 10.4581 | 45.2838 | 8.3378 | 122.0616 | 122.015 | 121.974 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | 0.019344 | 0.14539 | 10.5267 | 8.4065 | 8.3871 | 0.098762 | 0.057801 | -0.045117 | -121.9919 | 0.092606 | 0.007735 | 0.052852 | -121.8888 | -121.8443 | 122.1303 | 122.0836 | 122.0427 | 45.3525 | -121.9655 | -0.007074 | 0.096107 | 0.14052 | 0.14686 | -122.03
3567.5781 | 122.113 | -0.041199 | 121.9437 | 1.4211e-13 | -0.034478 | 0.0050641 | 0.07027 | -0.0035447 | 0.064221 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.01415 | 10.4856 | 45.2884 | 8.4889 | 122.0616 | 122.015 | 121.9648 | -0.053899 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.032021 | 0.067272 | -0.11836 | -0.0127 | 0.11792 | 10.5268 | 8.5301 | 8.5428 | 0.071296 | 0.021178 | -0.077162 | -122.0194 | 0.06514 | -0.019731 | 0.057431 | -121.9116 | -121.8764 | 122.1028 | 122.0562 | 122.006 | 45.3296 | -121.9976 | -0.03454 | 0.07322 | 0.10847 | 0.12855 | -122.062
3569.2656 | 121.9849 | -0.10529 | 121.9711 | 1.4211e-13 | -0.034265 | 0.0052779 | 0.070483 | -0.0031173 | 0.064434 | -0.02518 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.01415 | 10.5268 | 45.3067 | 8.5759 | 122.0662 | 122.0287 | 121.9694 | -0.040163 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.07643 | -0.11378 | 0.065123 | 0.095034 | 10.632 | 8.6812 | 8.616 | 0.057568 | -0.001708 | -0.008496 | -122.0514 | 0.12923 | 0.048935 | 0.057431 | -121.9437 | -121.8947 | 122.1715 | 122.134 | 122.0747 | 45.412 | -122.0113 | 0.024968 | 0.13273 | 0.18172 | 0.18806 | -122.0849
3571.0312 | 122.0993 | -0.059509 | 121.9254 | 1.4211e-13 | -0.034478 | 0.0046369 | 0.070483 | -0.0029037 | 0.064434 | -0.0022892 | -0.0044395 | -0.0012713 | 0.018545 | 0.031767 | 0.01415 | 10.5634 | 45.2792 | 8.6262 | 122.0616 | 122.0195 | 121.974 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.032021 | 0.067272 | -0.11378 | 0.00561 | 0.13623 | 10.6229 | 8.6857 | 8.6801 | 0.094186 | 0.048646 | -0.054273 | -122.0057 | 0.08345 | 0.003158 | 0.057431 | -121.8933 | -121.8581 | 122.1211 | 122.079 | 122.0335 | 45.3387 | -121.9793 | -0.020809 | 0.09153 | 0.12678 | 0.14228 | -122.0391
3572.7969 | 122.0261 | -0.091553 | 121.9574 | 1.4211e-13 | -0.034265 | 0.0048505 | 0.070697 | -0.0031173 | 0.064434 | -0.01755 | -0.0042257 | -0.0014849 | 0.018972 | 0.031553 | 0.013937 | 10.6321 | 45.3296 | 8.7132 | 122.0616 | 122.015 | 121.9786 | -0.049321 | 0.019362 | 0.078197 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | 0.042232 | 0.10419 | 10.7236 | 8.8048 | 8.7625 | 0.057564 | 0.021182 | -0.022229 | -122.0331 | 0.11091 | 0.030623 | 0.052852 | -121.93 | -121.8855 | 122.1531 | 122.1065 | 122.0701 | 45.4211 | -122.0067 | 0.015814 | 0.11899 | 0.1634 | 0.16975 | -122.0712
3574.5 | 121.9803 | -0.09613 | 121.9757 | 1.4211e-13 | -0.034051 | 0.0046369 | 0.070056 | -0.0031173 | 0.064434 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018758 | 0.031553 | 0.013937 | 10.6962 | 45.325 | 8.7773 | 122.0616 | 122.0241 | 121.9694 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.071851 | -0.11378 | 0.042231 | 0.085878 | 10.7923 | 8.8734 | 8.8312 | 0.048411 | -0.006286 | -0.017652 | -122.0469 | 0.12007 | 0.0352 | 0.052852 | -121.9437 | -121.9039 | 122.1577 | 122.1202 | 122.0656 | 45.4211 | -122.0296 | 0.024969 | 0.12815 | 0.16798 | 0.17891 | -122.0895
3576.2656 | 122.1176 | -0.032043 | 121.907 | 1.4211e-13 | -0.033837 | 0.0046369 | 0.07027 | -0.0029037 | 0.064648 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.031553 | 0.014364 | 10.8015 | 45.3342 | 8.8368 | 122.0662 | 122.015 | 121.9694 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.080318 | 0.0366 | 0.067272 | -0.12294 | -0.021856 | 0.15912 | 10.8335 | 8.8689 | 8.8907 | 0.10792 | 0.062379 | -0.090896 | -121.9874 | 0.055984 | -0.024308 | 0.066588 | -121.8704 | -121.8398 | 122.0982 | 122.047 | 122.0015 | 45.3662 | -121.9609 | -0.048275 | 0.068643 | 0.099315 | 0.11482 | -122.03
3578.0469 | 121.9849 | -0.1236 | 121.9528 | 1.4211e-13 | -0.034478 | 0.0052779 | 0.07027 | -0.0029037 | 0.064648 | -0.01755 | -0.0042257 | -0.0019123 | 0.018331 | 0.031553 | 0.014578 | 10.9297 | 45.3113 | 8.933 | 122.0616 | 122.015 | 121.9648 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.084896 | 0.032021 | 0.067272 | -0.11378 | 0.074275 | 0.10877 | 11.0533 | 9.0566 | 8.9823 | 0.062141 | 0.012023 | 0.009814 | -122.0377 | 0.14754 | 0.062666 | 0.052852 | -121.9208 | -121.8855 | 122.1852 | 122.1386 | 122.0884 | 45.4349 | -122.0021 | 0.0387 | 0.15562 | 0.19087 | 0.19721 | -122.0666
3579.75 | 122.1039 | -0.054932 | 121.8979 | 1.4211e-13 | -0.033837 | 0.0046369 | 0.070697 | -0.0029037 | 0.064648 | -0.01755 | -0.0040121 | -0.0014849 | 0.018758 | 0.031981 | 0.014364 | 11.0121 | 45.3113 | 8.9467 | 122.057 | 122.015 | 121.9694 | -0.049321 | 0.023941 | 0.073618 | -0.070087 | -0.075739 | 0.032021 | 0.071851 | -0.11378 | 0.005611 | 0.15912 | 11.067 | 9.0016 | 8.996 | 0.11707 | 0.071534 | -0.05885 | -121.9736 | 0.078873 | -0.015155 | 0.043695 | -121.8659 | -121.826 | 122.1119 | 122.0699 | 122.0244 | 45.3662 | -121.9472 | -0.020807 | 0.086953 | 0.12678 | 0.12855 | -122.0117
3581.5156 | 121.9894 | -0.11444 | 121.9574 | 1.4211e-13 | -0.034051 | 0.0050641 | 0.07027 | -0.0029037 | 0.064862 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018758 | 0.031553 | 0.014364 | 11.067 | 45.325 | 8.9879 | 122.057 | 122.015 | 121.974 | -0.044742 | 0.014784 | 0.087354 | -0.06093 | -0.084896 | 0.027442 | 0.071851 | -0.12294 | 0.069699 | 0.09961 | 11.1815 | 9.1024 | 9.0327 | 0.057564 | 0.016603 | -0.008498 | -122.0423 | 0.12923 | 0.053511 | 0.062009 | -121.93 | -121.8855 | 122.1714 | 122.1294 | 122.0884 | 45.4394 | -122.0021 | 0.029545 | 0.14188 | 0.18629 | 0.2018 | -122.0803
3583.2812 | 122.0764 | -0.07782 | 121.9574 | 1.4211e-13 | -0.033837 | 0.0048505 | 0.070483 | -0.0026901 | 0.065075 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.032194 | 0.014364 | 11.1815 | 45.3525 | 9.0474 | 122.0524 | 122.0104 | 121.9648 | -0.049321 | 0.019362 | 0.078197 | -0.056351 | -0.075739 | 0.032021 | 0.071851 | -0.1092 | 0.028499 | 0.095032 | 11.2593 | 9.1253 | 9.0968 | 0.052985 | 0.007446 | -0.031383 | -122.0331 | 0.097182 | 0.021469 | 0.052852 | -121.9254 | -121.8855 | 122.1302 | 122.0882 | 122.0427 | 45.4303 | -122.0067 | 0.002081 | 0.10984 | 0.14967 | 0.15602 | -122.0666
3584.9844 | 122.0169 | -0.082397 | 121.9437 | 1.4211e-13 | -0.033624 | 0.0048505 | 0.070483 | -0.0029037 | 0.065075 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.014364 | 11.2089 | 45.3342 | 9.1161 | 122.0616 | 122.0195 | 121.9603 | -0.044742 | 0.02852 | 0.087354 | -0.06093 | -0.089475 | 0.032021 | 0.071851 | -0.11378 | 0.037655 | 0.11792 | 11.2913 | 9.1985 | 9.1608 | 0.075875 | 0.0166 | -0.031385 | -122.0331 | 0.11092 | 0.021467 | 0.052852 | -121.9116 | -121.8718 | 122.144 | 122.1019 | 122.0427 | 45.4165 | -121.9884 | -0.007078 | 0.11442 | 0.15425 | 0.16975 | -122.0574
3586.75 | 121.994 | -0.09613 | 121.9666 | 1.4211e-13 | -0.033624 | 0.0048505 | 0.07027 | -0.0029037 | 0.065075 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031981 | 0.014578 | 11.2044 | 45.325 | 9.2947 | 122.0479 | 122.015 | 121.9694 | -0.049321 | 0.02852 | 0.082776 | -0.056351 | -0.075739 | 0.022864 | 0.071851 | -0.11836 | 0.046809 | 0.081298 | 11.3005 | 9.3908 | 9.344 | 0.048408 | 0.002869 | -0.022231 | -122.0423 | 0.12465 | 0.039779 | 0.06201 | -121.9437 | -121.8947 | 122.144 | 122.1111 | 122.0656 | 45.4211 | -122.0159 | 0.020391 | 0.11899 | 0.16798 | 0.17891 | -122.0849
3588.5156 | 122.0718 | -0.073242 | 121.9162 | 1.4211e-13 | -0.033624 | 0.0052779 | 0.070697 | -0.0026901 | 0.065289 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031981 | 0.01415 | 11.241 | 45.325 | 9.313 | 122.057 | 122.015 | 121.9648 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.12294 | 0.023921 | 0.14081 | 11.3142 | 9.3862 | 9.3623 | 0.098762 | 0.048644 | -0.049697 | -121.9874 | 0.10176 | 0.012312 | 0.062009 | -121.8842 | -121.8398 | 122.1302 | 122.0882 | 122.0381 | 45.3982 | -121.9655 | 0.002081 | 0.10526 | 0.14967 | 0.15602 | -122.0391
3590.2188 | 122.0901 | -0.050354 | 121.9345 | 1.4211e-13 | -0.03341 | 0.0048505 | 0.07027 | -0.0026901 | 0.064862 | -0.0022892 | -0.0044395 | -0.0016987 | 0.019186 | 0.031553 | 0.01415 | 11.3692 | 45.3113 | 9.3588 | 122.057 | 122.015 | 121.9648 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.032021 | 0.071851 | -0.11378 | 0.001033 | 0.1225 | 11.4195 | 9.4091 | 9.4081 | 0.080452 | 0.030334 | -0.063428 | -122.0148 | 0.074295 | -0.015155 | 0.048273 | -121.9025 | -121.8627 | 122.1074 | 122.0653 | 122.0152 | 45.3616 | -121.9838 | -0.029964 | 0.082375 | 0.12221 | 0.13313 | -122.0483
3591.9844 | 122.0535 | -0.073242 | 121.907 | 1.4211e-13 | -0.033624 | 0.0048505 | 0.070697 | -0.0024765 | 0.065075 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018758 | 0.031553 | 0.014578 | 11.4516 | 45.2517 | 9.4045 | 122.0616 | 122.015 | 121.9603 | -0.049321 | 0.019362 | 0.078197 | -0.065509 | -0.075739 | 0.027442 | 0.07643 | -0.1092 | 0.023921 | 0.15454 | 11.5248 | 9.4778 | 9.4539 | 0.10792 | 0.053222 | -0.035961 | -121.9828 | 0.092604 | 0.007733 | 0.043694 | -121.8796 | -121.8306 | 122.1348 | 122.0882 | 122.0335 | 45.325 | -121.9564 | -0.002497 | 0.10068 | 0.14967 | 0.15144 | -122.0162
3593.7656 | 122.0306 | -0.09613 | 121.9345 | 1.4211e-13 | -0.033196 | 0.0050641 | 0.070697 | -0.0020491 | 0.065289 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018972 | 0.031981 | 0.013723 | 11.5706 | 45.2517 | 9.5053 | 122.057 | 122.015 | 121.9694 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11836 | 0.046809 | 0.1225 | 11.6668 | 9.6014 | 9.5546 | 0.080452 | 0.034913 | -0.022231 | -122.0102 | 0.12007 | 0.0352 | 0.057431 | -121.9071 | -121.8627 | 122.1531 | 122.1111 | 122.0656 | 45.3479 | -121.9838 | 0.020391 | 0.12357 | 0.16798 | 0.17891 | -122.0529
3595.5312 | 122.0032 | -0.12817 | 121.9574 | 1.4211e-13 | -0.032769 | 0.0048505 | 0.070697 | -0.0024765 | 0.065289 | -0.01755 | -0.0040121 | -0.0016987 | 0.018545 | 0.031767 | 0.014578 | 11.5981 | 45.2472 | 9.5785 | 122.0616 | 122.0012 | 121.974 | -0.053899 | 0.019362 | 0.082776 | -0.051772 | -0.080318 | 0.032021 | 0.071851 | -0.11378 | 0.074275 | 0.10419 | 11.7263 | 9.7067 | 9.6324 | 0.043827 | 0.016603 | 0.014392 | -122.0377 | 0.14754 | 0.076402 | 0.06201 | -121.9254 | -121.8855 | 122.1898 | 122.1294 | 122.1022 | 45.3753 | -122.0113 | 0.047856 | 0.1602 | 0.20003 | 0.21095 | -122.0712
3597.2969 | 122.1176 | -0.059509 | 121.9208 | 1.4211e-13 | -0.032983 | 0.0052779 | 0.070483 | -0.0024765 | 0.065503 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018972 | 0.031767 | 0.01415 | 11.6851 | 45.2334 | 9.6838 | 122.057 | 122.015 | 121.9694 | -0.044742 | 0.019362 | 0.082776 | -0.065509 | -0.080318 | 0.022864 | 0.071851 | -0.11378 | 0.014767 | 0.13623 | 11.7446 | 9.7433 | 9.7286 | 0.094185 | 0.048646 | -0.054273 | -122.0011 | 0.078871 | -0.006 | 0.048273 | -121.8979 | -121.8489 | 122.1165 | 122.0745 | 122.0289 | 45.2929 | -121.9655 | -0.020809 | 0.082373 | 0.13136 | 0.14228 | -122.0346
3599 | 122.0627 | -0.09613 | 121.9208 | 1.4211e-13 | -0.032983 | 0.0050641 | 0.070697 | -0.0022627 | 0.065716 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.031981 | 0.014364 | 11.7171 | 45.1922 | 9.7571 | 122.0616 | 122.0104 | 121.9694 | -0.044742 | 0.02852 | 0.078197 | -0.065509 | -0.071161 | 0.022864 | 0.067272 | -0.12294 | 0.051388 | 0.14081 | 11.8133 | 9.8532 | 9.8018 | 0.089606 | 0.048646 | -0.026809 | -121.9919 | 0.12465 | 0.030621 | 0.05743 | -121.8979 | -121.8535 | 122.1577 | 122.1065 | 122.0656 | 45.2883 | -121.9655 | 0.024969 | 0.11899 | 0.1634 | 0.17433 | -122.0437
3600.7812 | 122.1268 | -0.045776 | 121.9299 | 1.4211e-13 | -0.032769 | 0.0052779 | 0.070911 | -0.0022627 | 0.065716 | -0.0099192 | -0.0044395 | -0.0014849 | 0.019186 | 0.031553 | 0.014364 | 11.7858 | 45.2105 | 9.7983 | 122.0662 | 122.015 | 121.9694 | -0.044742 | 0.02852 | 0.082776 | -0.056351 | -0.080318 | 0.027442 | 0.07643 | -0.11836 | 0.001034 | 0.13623 | 11.8316 | 9.844 | 9.843 | 0.085029 | 0.03949 | -0.072585 | -122.0102 | 0.074296 | -0.010575 | 0.06201 | -121.9025 | -121.8535 | 122.1119 | 122.0607 | 122.0152 | 45.2563 | -121.9747 | -0.034542 | 0.073218 | 0.12221 | 0.12855 | -122.0483
3602.5 | 122.0169 | -0.091553 | 121.9757 | 1.4211e-13 | -0.032983 | 0.0052779 | 0.070911 | -0.0022627 | 0.065716 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018758 | 0.031767 | 0.013937 | 11.8728 | 45.2059 | 9.899 | 122.0616 | 122.015 | 121.9648 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.080318 | 0.0366 | 0.071851 | -0.12294 | 0.042232 | 0.085878 | 11.9644 | 9.9905 | 9.9483 | 0.039253 | -0.010865 | -0.031386 | -122.056 | 0.11549 | 0.030623 | 0.062009 | -121.9391 | -121.9039 | 122.1531 | 122.1065 | 122.0564 | 45.2975 | -122.025 | 0.011235 | 0.12815 | 0.1634 | 0.16517 | -122.0986
3604.2812 | 122.0215 | -0.082397 | 121.9299 | 1.4211e-13 | -0.032983 | 0.0052779 | 0.070697 | -0.0018355 | 0.06593 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018758 | 0.031553 | 0.01415 | 11.9003 | 45.2243 | 9.9951 | 122.057 | 122.0104 | 121.9694 | -0.044742 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.027442 | 0.07643 | -0.11836 | 0.037655 | 0.12708 | 11.9827 | 10.0775 | 10.0399 | 0.08045 | 0.03949 | -0.035964 | -122.0057 | 0.10176 | 0.021467 | 0.057431 | -121.9025 | -121.8535 | 122.1394 | 122.0928 | 122.0518 | 45.3067 | -121.9747 | 0.006658 | 0.10984 | 0.15883 | 0.16517 | -122.0483
3605.9844 | 122.0215 | -0.086975 | 121.9666 | 1.4211e-13 | -0.032555 | 0.0050641 | 0.070911 | -0.0022627 | 0.065716 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018545 | 0.031553 | 0.01415 | 11.9094 | 45.1876 | 10.0638 | 122.057 | 122.015 | 121.9694 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.080318 | 0.027442 | 0.062694 | -0.12294 | 0.037654 | 0.090454 | 11.9964 | 10.1508 | 10.1131 | 0.048408 | 0.002869 | -0.035964 | -122.0469 | 0.1155 | 0.026045 | 0.062009 | -121.9391 | -121.9039 | 122.144 | 122.1019 | 122.0564 | 45.2746 | -122.0159 | 0.006657 | 0.11442 | 0.14967 | 0.16975 | -122.0895
3607.7656 | 122.0856 | -0.059509 | 121.9254 | 1.4211e-13 | -0.032555 | 0.0046369 | 0.070697 | -0.0020491 | 0.06593 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018545 | 0.031767 | 0.01415 | 12.0697 | 45.1785 | 10.0913 | 122.057 | 122.0195 | 121.9603 | -0.058478 | 0.02852 | 0.073618 | -0.06093 | -0.075739 | 0.027442 | 0.071851 | -0.11378 | 0.001031 | 0.13165 | 12.1292 | 10.1508 | 10.1498 | 0.094186 | 0.034911 | -0.054273 | -122.0011 | 0.088029 | -0.001421 | 0.052852 | -121.8979 | -121.8535 | 122.1165 | 122.079 | 122.0198 | 45.238 | -121.9838 | -0.01623 | 0.086951 | 0.13136 | 0.13313 | -122.0391
3609.5312 | 122.0947 | -0.059509 | 121.9345 | 1.4211e-13 | -0.032555 | 0.0046369 | 0.070697 | -0.0026901 | 0.065716 | 0.0053413 | -0.0042257 | -0.0016987 | 0.018545 | 0.031553 | 0.013937 | 12.2025 | 45.1739 | 10.073 | 122.0524 | 122.015 | 121.9694 | -0.053899 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.032021 | 0.062694 | -0.11378 | 0.00561 | 0.11792 | 12.262 | 10.1325 | 10.1269 | 0.080452 | 0.034913 | -0.054273 | -122.0102 | 0.08345 | -0.001421 | 0.052852 | -121.9025 | -121.8718 | 122.1119 | 122.0745 | 122.0289 | 45.2334 | -121.9884 | -0.01623 | 0.09153 | 0.1222 | 0.13771 | -122.0483
3611.2969 | 122.0306 | -0.10529 | 121.9666 | 1.4211e-13 | -0.032342 | 0.0050641 | 0.071124 | -0.0020491 | 0.066571 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018545 | 0.031767 | 0.013937 | 12.2986 | 45.1876 | 10.2332 | 122.057 | 122.015 | 121.9694 | -0.044742 | 0.023941 | 0.073618 | -0.06093 | -0.075739 | 0.041178 | 0.067272 | -0.11836 | 0.060544 | 0.090454 | 12.4039 | 10.3385 | 10.2779 | 0.048408 | 0.002869 | -0.013075 | -122.0423 | 0.12923 | 0.044356 | 0.057431 | -121.9254 | -121.8993 | 122.1623 | 122.1202 | 122.0747 | 45.2929 | -122.0113 | 0.029547 | 0.14646 | 0.17256 | 0.1789 | -122.0849
3613.0156 | 122.0078 | -0.09613 | 121.9574 | 1.4211e-13 | -0.032342 | 0.0052779 | 0.071124 | -0.0018355 | 0.066571 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018331 | 0.031981 | 0.01415 | 12.3719 | 45.151 | 10.2927 | 122.0616 | 122.0104 | 121.9694 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.032021 | 0.067272 | -0.11378 | 0.046809 | 0.10419 | 12.468 | 10.3889 | 10.342 | 0.052985 | 0.012025 | -0.017652 | -122.0377 | 0.12007 | 0.0352 | 0.052852 | -121.9254 | -121.8901 | 122.1577 | 122.1065 | 122.0656 | 45.2471 | -122.0067 | 0.015812 | 0.12815 | 0.1634 | 0.17891 | -122.0712
3614.7812 | 122.0673 | -0.059509 | 121.9437 | 1.4211e-13 | -0.032555 | 0.0052779 | 0.070697 | -0.0018355 | 0.06593 | -0.01755 | -0.0044395 | -0.0012713 | 0.018758 | 0.031767 | 0.01415 | 12.4314 | 45.1785 | 10.4575 | 122.0524 | 122.0104 | 121.9694 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.11836 | 0.001031 | 0.10876 | 12.4909 | 10.517 | 10.516 | 0.066717 | 0.025757 | -0.058852 | -122.0194 | 0.08345 | -0.001421 | 0.057431 | -121.9071 | -121.8672 | 122.1119 | 122.0699 | 122.0289 | 45.238 | -122.0021 | -0.01623 | 0.096109 | 0.13594 | 0.13771 | -122.062
3616.5625 | 122.0535 | -0.09613 | 121.9528 | 1.4211e-13 | -0.032128 | 0.0050641 | 0.070911 | -0.0016217 | 0.066357 | -0.0099192 | -0.0042257 | -0.0021259 | 0.018545 | 0.031767 | 0.014364 | 12.5138 | 45.2105 | 10.5445 | 122.0524 | 122.0104 | 121.9648 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.027442 | 0.07643 | -0.11378 | 0.051388 | 0.099609 | 12.6099 | 10.6407 | 10.5893 | 0.057562 | 0.012023 | -0.017652 | -122.0194 | 0.12007 | 0.0352 | 0.052852 | -121.9254 | -121.8764 | 122.1486 | 122.1065 | 122.061 | 45.3067 | -121.9976 | 0.029548 | 0.12357 | 0.17256 | 0.17433 | -122.0666
3618.2812 | 121.9437 | -0.091553 | 121.9803 | 1.4211e-13 | -0.031914 | 0.0048505 | 0.070911 | -0.0016217 | 0.066357 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018545 | 0.031981 | 0.013937 | 12.5687 | 45.2014 | 10.7048 | 122.0616 | 122.0058 | 121.9694 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 0.042232 | 0.0813 | 12.6603 | 10.7963 | 10.7541 | 0.025517 | -0.010864 | -0.031386 | -122.0469 | 0.11549 | 0.030623 | 0.062009 | -121.9437 | -121.9084 | 122.1531 | 122.0974 | 122.061 | 45.2929 | -122.0296 | 0.024971 | 0.12815 | 0.1634 | 0.16975 | -122.1032
3620.0469 | 122.0947 | -0.07782 | 121.9254 | 1.4211e-13 | -0.031914 | 0.0052779 | 0.071124 | -0.0014081 | 0.066785 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018972 | 0.031767 | 0.01415 | 12.6694 | 45.2059 | 10.7551 | 122.0479 | 122.0104 | 121.9648 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.11836 | 0.028499 | 0.1225 | 12.7473 | 10.8329 | 10.8044 | 0.085028 | 0.039489 | -0.040541 | -121.9919 | 0.10176 | 0.021469 | 0.06201 | -121.8888 | -121.8489 | 122.1257 | 122.0882 | 122.0427 | 45.2838 | -121.9747 | 0.011238 | 0.11442 | 0.15425 | 0.1606 | -122.0437
3621.7969 | 121.9803 | -0.11902 | 121.9666 | 1.4211e-13 | -0.031914 | 0.0054915 | 0.070911 | -0.0014081 | 0.066785 | -0.0099192 | -0.0040121 | -0.0014849 | 0.019186 | 0.032194 | 0.01415 | 12.729 | 45.3021 | 10.8696 | 122.0524 | 122.0104 | 121.9694 | -0.053899 | 0.02852 | 0.082776 | -0.070087 | -0.066582 | 0.0366 | 0.07643 | -0.11836 | 0.06512 | 0.085876 | 12.848 | 10.9886 | 10.9235 | 0.043829 | 0.002869 | 0.000658 | -122.0331 | 0.14754 | 0.048932 | 0.048274 | -121.93 | -121.8901 | 122.1714 | 122.1294 | 122.0884 | 45.4211 | -122.0205 | 0.052437 | 0.15562 | 0.19545 | 0.2018 | -122.0849
3623.5625 | 122.1359 | -0.064087 | 121.9345 | 1.4211e-13 | -0.0317 | 0.0050641 | 0.071338 | -0.0016217 | 0.066571 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018545 | 0.031339 | 0.014364 | 12.8434 | 45.3433 | 10.9154 | 122.0524 | 122.015 | 121.9648 | -0.049321 | 0.014784 | 0.082776 | -0.074666 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 0.014766 | 0.11792 | 12.9075 | 10.9795 | 10.9647 | 0.080452 | 0.030334 | -0.058852 | -121.9965 | 0.078871 | -0.010579 | 0.048273 | -121.9025 | -121.8627 | 122.1165 | 122.079 | 122.0289 | 45.4074 | -121.9838 | 0.002083 | 0.096108 | 0.13594 | 0.14686 | -122.0574
3625.3281 | 122.0169 | -0.09613 | 121.9528 | 1.4211e-13 | -0.031059 | 0.0052779 | 0.071124 | -0.0011945 | 0.066785 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.031981 | 0.014791 | 12.8938 | 45.357 | 11.0069 | 122.0524 | 122.0058 | 121.9603 | -0.053899 | 0.02852 | 0.087354 | -0.051772 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 0.042231 | 0.099609 | 12.9899 | 11.1031 | 11.0608 | 0.052983 | 0.007445 | -0.026809 | -122.0148 | 0.12465 | 0.044358 | 0.071167 | -121.9208 | -121.881 | 122.1486 | 122.1019 | 122.0564 | 45.4532 | -122.0067 | 0.034126 | 0.12815 | 0.16798 | 0.18348 | -122.0758
3627.0312 | 121.994 | -0.10529 | 121.9574 | 1.4211e-13 | -0.031487 | 0.0052779 | 0.071124 | -0.0011945 | 0.066998 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018758 | 0.031553 | 0.014364 | 12.7839 | 45.4074 | 11.1443 | 122.0524 | 122.015 | 121.974 | -0.053899 | 0.023941 | 0.078197 | -0.065509 | -0.071161 | 0.032021 | 0.067272 | -0.11378 | 0.051387 | 0.095032 | 12.8892 | 11.2496 | 11.1982 | 0.057564 | 0.016603 | -0.008496 | -122.0286 | 0.12923 | 0.039777 | 0.048273 | -121.9254 | -121.8901 | 122.1577 | 122.1202 | 122.0793 | 45.5127 | -122.0113 | 0.034125 | 0.13731 | 0.17256 | 0.18348 | -122.0712
3628.7969 | 122.0718 | -0.068665 | 121.9437 | 1.4211e-13 | -0.031487 | 0.0052779 | 0.070697 | -0.0014081 | 0.066785 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.031981 | 0.013937 | 12.9991 | 45.3891 | 11.1489 | 122.0479 | 122.0058 | 121.9603 | -0.049321 | 0.023941 | 0.073618 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.11836 | 0.019344 | 0.10419 | 13.0678 | 11.2175 | 11.1982 | 0.062138 | 0.0166 | -0.049696 | -122.0102 | 0.092606 | 0.007735 | 0.057431 | -121.9025 | -121.8672 | 122.1165 | 122.0745 | 122.0289 | 45.4578 | -121.993 | 0.002083 | 0.10984 | 0.1451 | 0.14228 | -122.062
3630.5625 | 122.0993 | -0.059509 | 121.9391 | 1.4211e-13 | -0.031487 | 0.0050641 | 0.071124 | -0.00098065 | 0.066785 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018545 | 0.031767 | 0.013937 | 13.0678 | 45.3525 | 11.2587 | 122.0524 | 122.0012 | 121.9648 | -0.044742 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.041178 | 0.071851 | -0.12294 | 0.014767 | 0.11334 | 13.1273 | 11.3182 | 11.3035 | 0.062137 | 0.025756 | -0.06343 | -122.0057 | 0.088029 | -0.006 | 0.05743 | -121.8979 | -121.8672 | 122.1119 | 122.0607 | 122.0244 | 45.412 | -121.9838 | -0.007073 | 0.10069 | 0.13136 | 0.13771 | -122.062
3632.3438 | 122.0352 | -0.10071 | 121.962 | 1.4211e-13 | -0.031273 | 0.0054915 | 0.071338 | -0.00098065 | 0.067639 | -0.01755 | -0.0042257 | -0.0021259 | 0.018758 | 0.031981 | 0.014364 | 13.3745 | 45.4349 | 11.3137 | 122.0479 | 122.0058 | 121.9694 | -0.044742 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.032021 | 0.067272 | -0.11378 | 0.055966 | 0.085876 | 13.4752 | 11.4144 | 11.3584 | 0.043828 | 0.007447 | -0.013074 | -122.024 | 0.12465 | 0.044357 | 0.057431 | -121.93 | -121.8947 | 122.1486 | 122.1065 | 122.0701 | 45.5356 | -122.0067 | 0.038704 | 0.13273 | 0.16798 | 0.18348 | -122.0758
3634.1094 | 121.994 | -0.09613 | 121.9666 | 1.4211e-13 | -0.030846 | 0.0054915 | 0.070697 | -0.00055345 | 0.066998 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031553 | 0.013723 | 13.434 | 45.4303 | 11.4419 | 122.0479 | 122.0012 | 121.9648 | -0.040163 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.027442 | 0.071851 | -0.12294 | 0.055967 | 0.081298 | 13.5302 | 11.538 | 11.482 | 0.034671 | -0.00171 | -0.026809 | -122.0377 | 0.11549 | 0.0352 | 0.062009 | -121.9391 | -121.8947 | 122.144 | 122.0974 | 122.061 | 45.5264 | -122.0067 | 0.024969 | 0.12357 | 0.16798 | 0.17891 | -122.0895
3635.8125 | 122.0993 | -0.068665 | 121.9345 | 1.4211e-13 | -0.031059 | 0.0050641 | 0.071338 | -0.0011945 | 0.067212 | -0.01755 | -0.0042257 | -0.0019123 | 0.018331 | 0.031981 | 0.014364 | 13.6034 | 45.4624 | 11.4693 | 122.0433 | 122.0012 | 121.9603 | -0.049321 | 0.023941 | 0.087354 | -0.065509 | -0.057425 | 0.032021 | 0.067272 | -0.11836 | 0.019344 | 0.10876 | 13.6721 | 11.538 | 11.5187 | 0.066715 | 0.025756 | -0.049696 | -121.9919 | 0.092606 | 0.003156 | 0.052852 | -121.9025 | -121.8672 | 122.1119 | 122.0699 | 122.0289 | 45.531 | -121.9838 | 0.01124 | 0.10069 | 0.13594 | 0.15602 | -122.0529
3637.5781 | 122.0901 | -0.073242 | 121.9345 | 1.4211e-13 | -0.030846 | 0.0054915 | 0.071338 | -0.00076705 | 0.067426 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018758 | 0.031767 | 0.01415 | 13.6492 | 45.531 | 11.6754 | 122.057 | 122.0058 | 121.9648 | -0.044742 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.032021 | 0.071851 | -0.11836 | 0.0285 | 0.1225 | 13.7225 | 11.7486 | 11.7201 | 0.071294 | 0.030334 | -0.045119 | -122.0057 | 0.097183 | 0.012312 | 0.057431 | -121.9025 | -121.8627 | 122.1302 | 122.079 | 122.0381 | 45.6043 | -121.9793 | 0.002081 | 0.10526 | 0.14509 | 0.1606 | -122.0529
3639.2812 | 122.0673 | -0.059509 | 121.9482 | 1.4211e-13 | -0.030846 | 0.0054915 | 0.071338 | -0.00076705 | 0.067426 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018758 | 0.031767 | 0.01415 | 13.8095 | 45.531 | 11.6433 | 122.0524 | 122.0104 | 121.9648 | -0.044742 | 0.033099 | 0.082776 | -0.065509 | -0.075739 | 0.027442 | 0.067272 | -0.11836 | 0.014767 | 0.10419 | 13.869 | 11.7028 | 11.6881 | 0.06214 | 0.016601 | -0.058852 | -122.024 | 0.092608 | -0.006 | 0.052852 | -121.9208 | -121.881 | 122.1119 | 122.0699 | 122.0244 | 45.5905 | -121.993 | -0.01623 | 0.086951 | 0.12678 | 0.14228 | -122.0666
3641.0312 | 122.0352 | -0.07782 | 121.9757 | 1.4211e-13 | -0.030632 | 0.0050641 | 0.071552 | -0.00076705 | 0.067853 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018972 | 0.031981 | 0.01415 | 13.782 | 45.5585 | 11.6983 | 122.057 | 122.015 | 121.9648 | -0.053899 | 0.02852 | 0.087354 | -0.051772 | -0.066582 | 0.041178 | 0.071851 | -0.12294 | 0.023921 | 0.081299 | 13.8598 | 11.7761 | 11.7522 | 0.039253 | -0.010865 | -0.045119 | -122.0423 | 0.10634 | 0.026048 | 0.071167 | -121.9345 | -121.9039 | 122.1348 | 122.0928 | 122.0427 | 45.6363 | -122.0296 | 0.011238 | 0.119 | 0.14967 | 0.16517 | -122.0986
3642.7969 | 121.9803 | -0.10071 | 121.9574 | 1.4211e-13 | -0.030632 | 0.0050641 | 0.071338 | -0.00055345 | 0.067639 | 0.0053413 | -0.0044395 | -0.0016987 | 0.018758 | 0.031981 | 0.01415 | 13.8552 | 45.5585 | 11.8768 | 122.057 | 122.0104 | 121.9648 | -0.044742 | 0.02852 | 0.087354 | -0.065509 | -0.066582 | 0.032021 | 0.067272 | -0.11378 | 0.055966 | 0.09961 | 13.956 | 11.9775 | 11.9215 | 0.052985 | 0.007446 | -0.013074 | -122.024 | 0.12923 | 0.035199 | 0.048273 | -121.9254 | -121.8901 | 122.1577 | 122.1111 | 122.0656 | 45.6592 | -122.0021 | 0.034126 | 0.13273 | 0.16798 | 0.18806 | -122.0712
3644.5781 | 121.9894 | -0.11902 | 121.9711 | 1.4211e-13 | -0.030205 | 0.0054915 | 0.071124 | -0.00055345 | 0.067853 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018331 | 0.031767 | 0.014364 | 13.9606 | 45.5036 | 11.8448 | 122.0524 | 122.0058 | 121.9603 | -0.040163 | 0.023941 | 0.087354 | -0.070087 | -0.066582 | 0.0366 | 0.067272 | -0.12294 | 0.078856 | 0.081299 | 14.0796 | 11.9638 | 11.8849 | 0.034673 | -0.010865 | -0.00392 | -122.0377 | 0.14296 | 0.048932 | 0.052852 | -121.9345 | -121.9039 | 122.1714 | 122.1248 | 122.0793 | 45.6226 | -122.0113 | 0.052437 | 0.15562 | 0.18629 | 0.20637 | -122.0941
3646.3594 | 121.9894 | -0.091553 | 121.9528 | 1.4211e-13 | -0.030418 | 0.0054915 | 0.071338 | -0.00033965 | 0.067639 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031767 | 0.013723 | 13.9514 | 45.5036 | 12.0325 | 122.0524 | 122.0012 | 121.9603 | -0.053899 | 0.033099 | 0.082776 | -0.065509 | -0.062004 | 0.032021 | 0.071851 | -0.11836 | 0.037654 | 0.099609 | 14.0429 | 12.124 | 12.0864 | 0.048404 | 0.007445 | -0.026808 | -122.0148 | 0.12465 | 0.026044 | 0.052852 | -121.9208 | -121.881 | 122.144 | 122.0928 | 122.0518 | 45.5951 | -122.0067 | 0.029549 | 0.12357 | 0.1634 | 0.17433 | -122.0712
3648.125 | 122.081 | -0.091553 | 121.9162 | 1.4211e-13 | -0.029777 | 0.0050641 | 0.071124 | -0.00012605 | 0.06828 | -0.01755 | -0.0042257 | -0.0021259 | 0.018758 | 0.031981 | 0.01415 | 14.1528 | 45.4532 | 12.1469 | 122.0524 | 122.0012 | 121.9648 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.11378 | 0.037654 | 0.13623 | 14.2444 | 12.2385 | 12.2008 | 0.085025 | 0.048644 | -0.022229 | -121.9736 | 0.11549 | 0.030623 | 0.052852 | -121.8796 | -121.8443 | 122.144 | 122.0928 | 122.0564 | 45.5447 | -121.9701 | 0.034128 | 0.12815 | 0.1634 | 0.17433 | -122.03
3649.8906 | 122.0901 | -0.036621 | 121.9162 | 1.4211e-13 | -0.029777 | 0.0052779 | 0.071338 | -0.00055345 | 0.06828 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.031339 | 0.014364 | 14.2353 | 45.5036 | 12.1423 | 122.0524 | 122.0058 | 121.9603 | -0.049321 | 0.033099 | 0.087354 | -0.056351 | -0.062004 | 0.041178 | 0.067272 | -0.11836 | -0.0127 | 0.13623 | 14.2719 | 12.179 | 12.1917 | 0.089604 | 0.044066 | -0.08174 | -121.9782 | 0.06972 | -0.01973 | 0.06201 | -121.875 | -121.8489 | 122.0891 | 122.0424 | 121.9969 | 45.5402 | -121.9655 | -0.025383 | 0.077799 | 0.10389 | 0.12398 | -122.0346
3651.6406 | 122.0535 | -0.073242 | 121.9345 | 1.4211e-13 | -0.029991 | 0.0052779 | 0.070911 | -0.00012605 | 0.06828 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.031553 | 0.013937 | 14.3177 | 45.4944 | 12.3117 | 122.0479 | 122.0058 | 121.9648 | -0.053899 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.0366 | 0.071851 | -0.12752 | 0.019343 | 0.11334 | 14.3909 | 12.385 | 12.3656 | 0.071294 | 0.030334 | -0.054276 | -122.0057 | 0.10176 | 0.016891 | 0.071167 | -121.8979 | -121.8627 | 122.1211 | 122.079 | 122.0381 | 45.5676 | -121.9884 | 0.002081 | 0.10984 | 0.14509 | 0.15602 | -122.062
3653.3594 | 122.0306 | -0.082397 | 121.9757 | 1.4211e-13 | -0.029777 | 0.0054915 | 0.071552 | -0.00012605 | 0.06828 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018758 | 0.031767 | 0.013723 | 14.3543 | 45.5081 | 12.3621 | 122.0479 | 122.0058 | 121.9511 | -0.053899 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.041178 | 0.062694 | -0.11378 | 0.028498 | 0.072143 | 14.4367 | 12.4445 | 12.416 | 0.030095 | -0.024601 | -0.031385 | -122.0423 | 0.10634 | 0.026046 | 0.057431 | -121.9345 | -121.913 | 122.1302 | 122.0882 | 122.0335 | 45.5905 | -122.0296 | 0.015815 | 0.12357 | 0.14509 | 0.16059 | -122.0895
3655.1406 | 121.9757 | -0.10529 | 121.962 | 1.4211e-13 | -0.02935 | 0.0054915 | 0.071124 | -0.00033965 | 0.06828 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031981 | 0.013937 | 14.5008 | 45.5036 | 12.4033 | 122.0387 | 122.0012 | 121.9603 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.071851 | -0.11836 | 0.055965 | 0.076719 | 14.6061 | 12.5086 | 12.4526 | 0.039249 | -0.00171 | -0.013075 | -122.0286 | 0.12923 | 0.044356 | 0.057431 | -121.9162 | -121.8901 | 122.144 | 122.1065 | 122.0656 | 45.6088 | -122.0113 | 0.038704 | 0.15104 | 0.17714 | 0.18806 | -122.0803
3656.9062 | 122.0581 | -0.082397 | 121.9254 | 1.4211e-13 | -0.02935 | 0.0052779 | 0.071552 | -0.00012605 | 0.067853 | -0.0022892 | -0.0044395 | -0.0021259 | 0.018331 | 0.031767 | 0.013937 | 14.6473 | 45.5539 | 12.4766 | 122.0433 | 122.0104 | 121.9603 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.062694 | -0.11836 | 0.033076 | 0.11792 | 14.7297 | 12.559 | 12.5259 | 0.085028 | 0.034911 | -0.035964 | -121.9828 | 0.11092 | 0.021467 | 0.057431 | -121.8888 | -121.8627 | 122.1257 | 122.0928 | 122.0427 | 45.6363 | -121.9747 | 0.024972 | 0.119 | 0.14509 | 0.16517 | -122.0437
3658.625 | 121.9986 | -0.10529 | 121.9482 | 1.4211e-13 | -0.029136 | 0.0054915 | 0.071552 | 0.00030135 | 0.068494 | -0.0022892 | -0.0040121 | -0.0014849 | 0.018545 | 0.032194 | 0.01415 | 14.8076 | 45.5493 | 12.6917 | 122.0433 | 122.0058 | 121.9557 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.11836 | 0.055965 | 0.09503 | 14.9128 | 12.797 | 12.7411 | 0.057561 | 0.007444 | -0.013075 | -122.0148 | 0.12923 | 0.044356 | 0.057431 | -121.9116 | -121.8718 | 122.1486 | 122.1111 | 122.061 | 45.6546 | -121.9976 | 0.038704 | 0.14189 | 0.18172 | 0.18806 | -122.0666
3660.3906 | 122.1085 | -0.064087 | 121.8979 | 1.4211e-13 | -0.028495 | 0.0052779 | 0.071552 | 0.00030135 | 0.068708 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031767 | 0.01415 | 14.8854 | 45.6089 | 12.8886 | 122.0433 | 122.0058 | 121.9603 | -0.049321 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.041178 | 0.071851 | -0.11836 | 0.014766 | 0.14538 | 14.9495 | 12.9527 | 12.9379 | 0.10792 | 0.062377 | -0.054274 | -121.9645 | 0.088028 | -0.001422 | 0.052852 | -121.8567 | -121.826 | 122.1074 | 122.0699 | 122.0244 | 45.673 | -121.9472 | -0.002495 | 0.10526 | 0.13594 | 0.15144 | -122.0162
3662.1562 | 122.0947 | -0.064087 | 121.9025 | 1.4211e-13 | -0.028495 | 0.0052779 | 0.071338 | 8.7546e-05 | 0.068708 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018758 | 0.031767 | 0.01415 | 15.0639 | 45.5539 | 12.797 | 122.0433 | 122.0058 | 121.9603 | -0.049321 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.041178 | 0.067272 | -0.11836 | 0.014766 | 0.14081 | 15.128 | 12.8611 | 12.8464 | 0.10334 | 0.057799 | -0.054274 | -121.969 | 0.092607 | 0.007736 | 0.06201 | -121.8613 | -121.8352 | 122.1074 | 122.0699 | 122.0244 | 45.618 | -121.9518 | -0.002495 | 0.10526 | 0.13136 | 0.15144 | -122.0208
3663.8594 | 122.081 | -0.064087 | 121.9208 | 1.4211e-13 | -0.028923 | 0.0054915 | 0.071124 | -0.00012605 | 0.068921 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018545 | 0.032194 | 0.014364 | 15.1921 | 45.5768 | 12.884 | 122.0479 | 122.0058 | 121.9557 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.0366 | 0.071851 | -0.11378 | 0.014766 | 0.12707 | 15.2562 | 12.9481 | 12.9334 | 0.085027 | 0.03491 | -0.049695 | -121.9782 | 0.088028 | -0.001422 | 0.048273 | -121.8842 | -121.8489 | 122.1119 | 122.0699 | 122.0198 | 45.6409 | -121.9701 | 0.006662 | 0.10069 | 0.13594 | 0.14686 | -122.0346
3665.6406 | 121.9757 | -0.13275 | 121.962 | 1.4211e-13 | -0.028495 | 0.0057051 | 0.071338 | -0.00033965 | 0.069135 | -0.01755 | -0.0040121 | -0.0014849 | 0.018758 | 0.031553 | 0.01415 | 15.3295 | 45.5539 | 12.971 | 122.0433 | 122.0058 | 121.9557 | -0.044742 | 0.02852 | 0.078197 | -0.056351 | -0.057425 | 0.0366 | 0.067272 | -0.12294 | 0.088009 | 0.081297 | 15.4622 | 13.1038 | 13.0158 | 0.043828 | -0.006289 | 0.009812 | -122.0194 | 0.16127 | 0.0764 | 0.066588 | -121.9254 | -121.8947 | 122.176 | 122.1386 | 122.0884 | 45.6867 | -122.0067 | 0.075326 | 0.16935 | 0.20002 | 0.21095 | -122.0849
3667.4062 | 122.0856 | -0.068665 | 121.8887 | 1.4211e-13 | -0.028282 | 0.0050641 | 0.071338 | 8.7546e-05 | 0.069562 | -0.02518 | -0.0044395 | -0.0014849 | 0.018758 | 0.031767 | 0.014364 | 15.4943 | 45.5173 | 13.0351 | 122.0387 | 121.9966 | 121.9511 | -0.044742 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.032021 | 0.07643 | -0.12294 | 0.023923 | 0.14996 | 15.563 | 13.1038 | 13.0799 | 0.10791 | 0.062374 | -0.054274 | -121.9507 | 0.088027 | 0.007735 | 0.062009 | -121.8567 | -121.8123 | 122.1074 | 122.0653 | 122.0198 | 45.586 | -121.9335 | 0.006661 | 0.10069 | 0.1451 | 0.14686 | -122.0117
3669.1719 | 121.9666 | -0.11444 | 121.9711 | 1.4211e-13 | -0.028282 | 0.0059189 | 0.071552 | 8.7546e-05 | 0.069135 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018972 | 0.031767 | 0.014364 | 15.6774 | 45.5402 | 13.1679 | 122.0433 | 121.9966 | 121.9648 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.1092 | 0.06512 | 0.072142 | 15.7919 | 13.2823 | 13.2172 | 0.025516 | -0.006287 | 0.005238 | -122.0377 | 0.13838 | 0.05809 | 0.052852 | -121.9345 | -121.8993 | 122.1577 | 122.1111 | 122.0793 | 45.6546 | -122.0205 | 0.047859 | 0.15104 | 0.18629 | 0.19264 | -122.0803
3670.875 | 122.0169 | -0.091553 | 121.9345 | 1.4211e-13 | -0.027641 | 0.0057051 | 0.071765 | 0.00030135 | 0.069562 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.031981 | 0.01415 | 15.8606 | 45.5402 | 13.264 | 122.0433 | 122.0012 | 121.9557 | -0.049321 | 0.02852 | 0.082776 | -0.056351 | -0.057425 | 0.0366 | 0.067272 | -0.1092 | 0.042232 | 0.10876 | 15.9521 | 13.3556 | 13.3133 | 0.066715 | 0.021177 | -0.01765 | -121.9919 | 0.12007 | 0.035202 | 0.052852 | -121.8979 | -121.8672 | 122.1348 | 122.0928 | 122.0472 | 45.6317 | -121.9838 | 0.034128 | 0.12815 | 0.15882 | 0.17433 | -122.0437
3672.6562 | 122.0215 | -0.10071 | 121.9528 | 1.4211e-13 | -0.027641 | 0.0057051 | 0.071552 | 0.00072855 | 0.06999 | -0.01755 | -0.0042257 | -0.0016987 | 0.018758 | 0.031553 | 0.013937 | 15.8102 | 45.5448 | 13.4426 | 122.0479 | 121.9966 | 121.9557 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.0366 | 0.07643 | -0.1092 | 0.051387 | 0.095031 | 15.9109 | 13.5433 | 13.4919 | 0.043826 | 0.002866 | -0.008495 | -122.0148 | 0.12923 | 0.039778 | 0.048273 | -121.9162 | -121.8764 | 122.1486 | 122.0974 | 122.0564 | 45.6455 | -122.0021 | 0.038704 | 0.13731 | 0.17714 | 0.17891 | -122.062
3674.4375 | 122.0123 | -0.10071 | 121.9528 | 1.4211e-13 | -0.027641 | 0.0057051 | 0.071552 | 0.00072855 | 0.06999 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018331 | 0.031553 | 0.01415 | 15.9934 | 45.5402 | 13.612 | 122.0479 | 122.0058 | 121.9511 | -0.049321 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.032021 | 0.071851 | -0.11836 | 0.051387 | 0.095031 | 16.0941 | 13.7127 | 13.6613 | 0.052983 | -0.001713 | -0.017653 | -122.024 | 0.12923 | 0.044357 | 0.06201 | -121.9208 | -121.881 | 122.1486 | 122.1065 | 122.0518 | 45.6409 | -122.0021 | 0.029547 | 0.13273 | 0.17256 | 0.18348 | -122.0712
3676.2031 | 122.0627 | -0.059509 | 121.9025 | 1.4211e-13 | -0.027641 | 0.0057051 | 0.071338 | 0.00051495 | 0.069562 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018972 | 0.031767 | 0.013937 | 15.9522 | 45.4761 | 13.5158 | 122.0479 | 122.0012 | 121.9603 | -0.049321 | 0.02852 | 0.087354 | -0.06093 | -0.071161 | 0.027442 | 0.067272 | -0.11378 | 0.010188 | 0.14538 | 16.0117 | 13.5753 | 13.5652 | 0.098758 | 0.057799 | -0.054273 | -121.9736 | 0.088029 | -0.001421 | 0.052852 | -121.875 | -121.8352 | 122.1074 | 122.0607 | 122.0198 | 45.5356 | -121.9518 | -0.011652 | 0.086951 | 0.12678 | 0.14686 | -122.0162
3677.9688 | 121.9711 | -0.091553 | 121.9528 | 1.4211e-13 | -0.027427 | 0.0054915 | 0.071765 | 0.00094235 | 0.06999 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.031767 | 0.01415 | 16.1399 | 45.5081 | 13.7631 | 122.0433 | 122.0058 | 121.9603 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.11378 | 0.037654 | 0.090452 | 16.2314 | 13.8546 | 13.817 | 0.052983 | 0.007445 | -0.022229 | -122.0194 | 0.11549 | 0.030623 | 0.052852 | -121.9162 | -121.8764 | 122.1348 | 122.0974 | 122.0518 | 45.5997 | -122.0067 | 0.024971 | 0.12815 | 0.16798 | 0.17433 | -122.0666
3679.6719 | 122.0535 | -0.064087 | 121.9208 | 1.4211e-13 | -0.027427 | 0.0057051 | 0.071552 | 0.00072855 | 0.069562 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031981 | 0.014364 | 16.3917 | 45.5081 | 13.6623 | 122.0479 | 122.0012 | 121.9557 | -0.044742 | 0.014784 | 0.082776 | -0.065509 | -0.057425 | 0.022864 | 0.067272 | -0.11836 | 0.019345 | 0.12707 | 16.4558 | 13.7264 | 13.7071 | 0.080448 | 0.03491 | -0.054274 | -121.9782 | 0.078871 | -0.001422 | 0.052852 | -121.8979 | -121.8535 | 122.1119 | 122.0653 | 122.0198 | 45.5722 | -121.9655 | 0.006662 | 0.086951 | 0.13136 | 0.14686 | -122.0391
3681.4219 | 122.1085 | -0.073242 | 121.907 | 1.4211e-13 | -0.027427 | 0.0052779 | 0.071338 | 0.0011559 | 0.06999 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018758 | 0.031981 | 0.01415 | 16.4558 | 45.5036 | 13.9004 | 122.0341 | 122.0012 | 121.9511 | -0.049321 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.022864 | 0.067272 | -0.11836 | 0.023921 | 0.12707 | 16.529 | 13.9736 | 13.9497 | 0.094181 | 0.044064 | -0.045119 | -121.9736 | 0.092604 | 0.012312 | 0.057431 | -121.8842 | -121.8398 | 122.1074 | 122.0745 | 122.0243 | 45.5768 | -121.9564 | 0.00666 | 0.096106 | 0.14051 | 0.15602 | -122.0254
3683.1875 | 122.0352 | -0.086975 | 121.9208 | 1.4211e-13 | -0.027213 | 0.0059189 | 0.071979 | 0.00072855 | 0.070417 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018972 | 0.031339 | 0.01415 | 16.3596 | 45.499 | 14.0469 | 122.0479 | 122.0058 | 121.9557 | -0.049321 | 0.02852 | 0.073618 | -0.06093 | -0.057425 | 0.027442 | 0.067272 | -0.11836 | 0.037654 | 0.12707 | 16.4466 | 14.1339 | 14.0962 | 0.085027 | 0.03491 | -0.031386 | -121.9782 | 0.1155 | 0.026045 | 0.057431 | -121.8933 | -121.8535 | 122.1348 | 122.0928 | 122.0427 | 45.586 | -121.9701 | 0.02955 | 0.11442 | 0.15425 | 0.16059 | -122.0391
3684.9531 | 121.9803 | -0.10529 | 121.9574 | 1.4211e-13 | -0.026786 | 0.0057051 | 0.071765 | 0.00094235 | 0.070203 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018758 | 0.031553 | 0.013937 | 16.5702 | 45.4486 | 14.1431 | 122.0479 | 121.9966 | 121.9511 | -0.044742 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.027442 | 0.071851 | -0.1092 | 0.060544 | 0.090454 | 16.6755 | 14.2483 | 14.1878 | 0.039249 | -0.00629 | -0.003917 | -122.024 | 0.12923 | 0.039777 | 0.043694 | -121.93 | -121.8855 | 122.1531 | 122.1019 | 122.0564 | 45.5539 | -122.0021 | 0.038704 | 0.13273 | 0.17714 | 0.19264 | -122.0666
3686.6719 | 122.113 | -0.064087 | 121.907 | 1.4211e-13 | -0.027 | 0.0057051 | 0.071552 | 0.0011559 | 0.070631 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031981 | 0.014364 | 16.6755 | 45.444 | 14.23 | 122.0387 | 122.0012 | 121.9557 | -0.053899 | 0.019362 | 0.06904 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.12294 | 0.010188 | 0.13165 | 16.7396 | 14.2941 | 14.2839 | 0.094181 | 0.048643 | -0.058852 | -121.9736 | 0.083449 | 0.003157 | 0.062009 | -121.8796 | -121.8352 | 122.1028 | 122.0653 | 122.0198 | 45.5081 | -121.9609 | -0.002495 | 0.091529 | 0.13594 | 0.13313 | -122.03
3688.4375 | 122.0398 | -0.086975 | 121.9162 | 1.4211e-13 | -0.026572 | 0.0052779 | 0.072193 | 0.0013695 | 0.070417 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018545 | 0.031767 | 0.01415 | 16.6939 | 45.4852 | 14.3445 | 122.0341 | 121.9921 | 121.9557 | -0.049321 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.11378 | 0.037654 | 0.11792 | 16.7808 | 14.4315 | 14.3938 | 0.075868 | 0.039487 | -0.026807 | -121.9828 | 0.11092 | 0.030624 | 0.057431 | -121.8796 | -121.8443 | 122.1211 | 122.079 | 122.0427 | 45.5722 | -121.9655 | 0.020393 | 0.12357 | 0.15883 | 0.16517 | -122.03
3690.2188 | 122.0535 | -0.086975 | 121.9254 | 1.4211e-13 | -0.026359 | 0.0057051 | 0.071765 | 0.0011559 | 0.070844 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018758 | 0.031981 | 0.014364 | 16.8678 | 45.4715 | 14.4635 | 122.0295 | 122.0012 | 121.9557 | -0.044742 | 0.033099 | 0.078197 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.042233 | 0.10418 | 16.9548 | 14.5505 | 14.5083 | 0.07587 | 0.030332 | -0.031386 | -121.9919 | 0.12007 | 0.030624 | 0.06201 | -121.8888 | -121.8535 | 122.1165 | 122.0882 | 122.0427 | 45.5585 | -121.9701 | 0.020393 | 0.12357 | 0.15883 | 0.16517 | -122.0437
3691.9375 | 121.9711 | -0.091553 | 121.9437 | 1.4211e-13 | -0.025931 | 0.0057051 | 0.071765 | 0.0015831 | 0.071058 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018545 | 0.031767 | 0.014364 | 16.996 | 45.4624 | 14.5597 | 122.0479 | 122.0012 | 121.9511 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.067272 | -0.1092 | 0.042232 | 0.10419 | 17.0876 | 14.6512 | 14.609 | 0.057559 | 0.007442 | -0.01765 | -122.0148 | 0.11549 | 0.030623 | 0.048273 | -121.9116 | -121.8764 | 122.1394 | 122.0928 | 122.0427 | 45.5539 | -121.993 | 0.020392 | 0.12357 | 0.15882 | 0.17433 | -122.0529
3693.6875 | 122.0764 | -0.073242 | 121.9025 | 1.4211e-13 | -0.025718 | 0.0059189 | 0.071979 | 0.0013695 | 0.071272 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018331 | 0.031767 | 0.013937 | 17.3028 | 45.4761 | 14.6833 | 122.0433 | 121.9966 | 121.9557 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.11378 | 0.0285 | 0.14081 | 17.376 | 14.7565 | 14.728 | 0.09418 | 0.05322 | -0.04054 | -121.9736 | 0.097183 | 0.012312 | 0.052852 | -121.8704 | -121.826 | 122.1165 | 122.0699 | 122.0289 | 45.5493 | -121.9472 | 0.002081 | 0.10526 | 0.14967 | 0.15144 | -122.0162
3695.4688 | 121.994 | -0.091553 | 121.9482 | 1.4211e-13 | -0.025718 | 0.0059189 | 0.071979 | 0.0015831 | 0.070631 | -0.0022892 | -0.0040121 | -0.0014849 | 0.018758 | 0.031767 | 0.013723 | 17.3257 | 45.444 | 14.752 | 122.0387 | 121.9921 | 121.9511 | -0.040163 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.027442 | 0.067272 | -0.12294 | 0.05139 | 0.090452 | 17.4172 | 14.8435 | 14.7921 | 0.043825 | 0.002865 | -0.031386 | -122.0148 | 0.11549 | 0.035202 | 0.066588 | -121.9208 | -121.881 | 122.1302 | 122.0836 | 122.0427 | 45.5356 | -121.9884 | 0.024971 | 0.11899 | 0.15882 | 0.17891 | -122.0712
3697.1719 | 122.0901 | -0.059509 | 121.8979 | 1.4211e-13 | -0.025718 | 0.0057051 | 0.071765 | 0.0017969 | 0.071272 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.031767 | 0.01415 | 17.5134 | 45.499 | 14.8161 | 122.0433 | 121.9921 | 121.9557 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 0.001031 | 0.14538 | 17.5729 | 14.8756 | 14.8745 | 0.094179 | 0.057798 | -0.058852 | -121.9599 | 0.08345 | -0.001421 | 0.057431 | -121.8613 | -121.826 | 122.1028 | 122.0516 | 122.0152 | 45.5585 | -121.9564 | -0.002495 | 0.096109 | 0.13136 | 0.13771 | -122.0162
3698.9375 | 122.049 | -0.07782 | 121.9254 | 1.4211e-13 | -0.025931 | 0.0059189 | 0.071979 | 0.0020105 | 0.071485 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.031767 | 0.01415 | 17.5042 | 45.4944 | 15.0587 | 122.0387 | 121.9966 | 121.9511 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.11836 | 0.033078 | 0.11334 | 17.582 | 15.1365 | 15.1035 | 0.071292 | 0.025753 | -0.040541 | -121.9965 | 0.10634 | 0.01689 | 0.057431 | -121.8933 | -121.8489 | 122.1165 | 122.0745 | 122.0289 | 45.5722 | -121.9701 | 0.006659 | 0.10984 | 0.15425 | 0.1606 | -122.0437
3700.7188 | 122.0901 | -0.054932 | 121.8796 | 1.4211e-13 | -0.02529 | 0.0059189 | 0.071765 | 0.0020105 | 0.071485 | -0.01755 | -0.0044395 | -0.0016987 | 0.018758 | 0.031767 | 0.01415 | 17.6233 | 45.4395 | 15.1594 | 122.0433 | 121.9966 | 121.9465 | -0.044742 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.032021 | 0.067272 | -0.12294 | 0.01019 | 0.16369 | 17.6782 | 15.2144 | 15.2042 | 0.11707 | 0.066951 | -0.068007 | -121.9462 | 0.078873 | -0.001419 | 0.066588 | -121.8476 | -121.8123 | 122.0982 | 122.0516 | 122.0015 | 45.4944 | -121.9243 | -0.01165 | 0.086953 | 0.1222 | 0.13771 | -122.0025
3702.4688 | 121.9986 | -0.082397 | 121.9757 | 1.4211e-13 | -0.025504 | 0.0059189 | 0.071338 | 0.0017969 | 0.071699 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018758 | 0.031767 | 0.01415 | 17.6278 | 45.4211 | 15.3471 | 122.0387 | 122.0012 | 121.9557 | -0.049321 | 0.033099 | 0.087354 | -0.056351 | -0.071161 | 0.0366 | 0.071851 | -0.11836 | 0.033076 | 0.062986 | 17.7102 | 15.4295 | 15.3965 | 0.025516 | -0.020022 | -0.035964 | -122.0469 | 0.1155 | 0.026046 | 0.06201 | -121.9391 | -121.9039 | 122.1211 | 122.0836 | 122.0381 | 45.5035 | -122.025 | 0.011236 | 0.119 | 0.15425 | 0.16975 | -122.0941
3704.25 | 121.9528 | -0.09613 | 121.9391 | 1.4211e-13 | -0.024863 | 0.0061325 | 0.071979 | 0.0024379 | 0.071913 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018545 | 0.031767 | 0.013937 | 17.9025 | 45.3662 | 15.4112 | 122.0387 | 121.9921 | 121.9511 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.042231 | 0.099607 | 17.9987 | 15.5074 | 15.4651 | 0.05298 | 0.01202 | -0.022231 | -122.0057 | 0.12465 | 0.0352 | 0.057431 | -121.9025 | -121.8672 | 122.1348 | 122.0882 | 122.0472 | 45.4623 | -121.993 | 0.029548 | 0.13273 | 0.16798 | 0.17891 | -122.0574
3705.9844 | 122.049 | -0.073242 | 121.9345 | 1.4211e-13 | -0.024863 | 0.0059189 | 0.071979 | 0.0020105 | 0.072126 | -0.01755 | -0.0040121 | -0.0019123 | 0.018545 | 0.031981 | 0.013937 | 18.017 | 45.3845 | 15.4891 | 122.0341 | 121.9966 | 121.9511 | -0.044742 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.032021 | 0.067272 | -0.12294 | 0.0285 | 0.099606 | 18.0902 | 15.5623 | 15.5338 | 0.062137 | 0.016598 | -0.049697 | -122.0057 | 0.097183 | 0.007733 | 0.05743 | -121.9025 | -121.8672 | 122.1074 | 122.0699 | 122.0243 | 45.4578 | -121.9793 | 0.002081 | 0.10526 | 0.14051 | 0.15602 | -122.0574
3707.7344 | 122.0993 | -0.050354 | 121.9162 | 1.4211e-13 | -0.024863 | 0.0059189 | 0.071979 | 0.0024379 | 0.071913 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018758 | 0.031981 | 0.01415 | 18.1498 | 45.4257 | 15.6585 | 122.0295 | 121.9966 | 121.9465 | -0.053899 | 0.033099 | 0.078197 | -0.056351 | -0.062004 | 0.0366 | 0.067272 | -0.11378 | -0.003545 | 0.11334 | 18.2001 | 15.7088 | 15.7124 | 0.080447 | 0.03033 | -0.063428 | -121.9782 | 0.083453 | -0.005997 | 0.057431 | -121.8796 | -121.8489 | 122.0799 | 122.047 | 121.9969 | 45.4761 | -121.9701 | -0.01165 | 0.086954 | 0.11763 | 0.12855 | -122.03
3709.4531 | 121.9574 | -0.11444 | 121.9528 | 1.4211e-13 | -0.024222 | 0.0061325 | 0.071765 | 0.0024379 | 0.07234 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018545 | 0.031767 | 0.013723 | 18.1956 | 45.3983 | 15.6951 | 122.0387 | 121.9966 | 121.9511 | -0.053899 | 0.014784 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.067272 | -0.11836 | 0.060542 | 0.085874 | 18.31 | 15.8095 | 15.749 | 0.043826 | -0.001713 | -0.00392 | -122.0148 | 0.12923 | 0.05809 | 0.06201 | -121.9162 | -121.8855 | 122.1531 | 122.1111 | 122.0655 | 45.5127 | -122.0067 | 0.052437 | 0.15104 | 0.18171 | 0.19722 | -122.0712
3711.1875 | 122.0398 | -0.09613 | 121.9254 | 1.4211e-13 | -0.024222 | 0.0059189 | 0.071979 | 0.0020105 | 0.072554 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018972 | 0.031981 | 0.01415 | 18.3375 | 45.4028 | 15.9332 | 122.0295 | 121.9921 | 121.9511 | -0.049321 | 0.033099 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.062694 | -0.11836 | 0.046809 | 0.10418 | 18.4336 | 16.0293 | 15.9825 | 0.066713 | 0.025753 | -0.022231 | -121.9965 | 0.12923 | 0.0352 | 0.057431 | -121.8933 | -121.8627 | 122.1257 | 122.0882 | 122.0472 | 45.499 | -121.9747 | 0.024969 | 0.12815 | 0.15882 | 0.17891 | -122.0437
3713 | 121.9803 | -0.10529 | 121.9391 | 1.4211e-13 | -0.024222 | 0.0059189 | 0.072193 | 0.0022241 | 0.07234 | -0.01755 | -0.0040121 | -0.0016987 | 0.018545 | 0.031767 | 0.013723 | 18.4336 | 45.3525 | 15.7317 | 122.0387 | 121.9966 | 121.942 | -0.044742 | 0.02852 | 0.078197 | -0.051772 | -0.075739 | 0.027442 | 0.067272 | -0.11378 | 0.060544 | 0.099607 | 18.5389 | 15.837 | 15.7765 | 0.057559 | 0.002863 | -0.008496 | -122.0148 | 0.13381 | 0.053514 | 0.06201 | -121.9116 | -121.8718 | 122.144 | 122.1019 | 122.0472 | 45.4577 | -121.9838 | 0.029547 | 0.13273 | 0.17256 | 0.18348 | -122.0529
3714.7031 | 122.0215 | -0.073242 | 121.9299 | 1.4211e-13 | -0.024008 | 0.0061325 | 0.072193 | 0.0020105 | 0.07234 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.031767 | 0.013937 | 18.5527 | 45.3204 | 15.8416 | 122.0295 | 121.9921 | 121.942 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.07643 | -0.11836 | 0.023921 | 0.099605 | 18.6259 | 15.9148 | 15.8909 | 0.062135 | 0.012018 | -0.045119 | -121.9919 | 0.10176 | 0.012312 | 0.057431 | -121.8933 | -121.8535 | 122.1028 | 122.0653 | 122.0152 | 45.3937 | -121.9793 | 0.011238 | 0.10984 | 0.14967 | 0.15602 | -122.0483
3716.4844 | 121.9711 | -0.10071 | 121.994 | 1.4211e-13 | -0.023367 | 0.0063463 | 0.072406 | 0.0024379 | 0.072767 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018545 | 0.031981 | 0.014364 | 18.7129 | 45.2884 | 16.0339 | 122.0341 | 121.9966 | 121.942 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.0366 | 0.067272 | -0.11836 | 0.046809 | 0.040096 | 18.8136 | 16.1346 | 16.0878 | 0.002627 | -0.052069 | -0.017653 | -122.0606 | 0.12923 | 0.039778 | 0.057431 | -121.9574 | -121.9267 | 122.1348 | 122.0974 | 122.0427 | 45.3891 | -122.0479 | 0.034126 | 0.13731 | 0.16798 | 0.17891 | -122.1124
3718.2344 | 121.994 | -0.09613 | 121.9482 | 1.4211e-13 | -0.023795 | 0.0061325 | 0.072406 | 0.0026515 | 0.072981 | -0.0099192 | -0.0035849 | -0.0014849 | 0.018972 | 0.032194 | 0.01415 | 18.8915 | 45.3479 | 16.2903 | 122.0387 | 121.9966 | 121.9465 | -0.044742 | 0.02852 | 0.087354 | -0.070087 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 0.051388 | 0.090452 | 18.9876 | 16.3864 | 16.335 | 0.048404 | -0.001713 | -0.022231 | -122.0102 | 0.12465 | 0.026043 | 0.048274 | -121.9116 | -121.8764 | 122.1348 | 122.0928 | 122.0427 | 45.444 | -121.993 | 0.034126 | 0.13273 | 0.16798 | 0.18348 | -122.0666
3720 | 122.0032 | -0.10986 | 121.9574 | 1.4211e-13 | -0.023367 | 0.0059189 | 0.071979 | 0.0026515 | 0.072981 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 18.9968 | 45.3296 | 16.1895 | 122.0341 | 121.9875 | 121.9465 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.022864 | 0.071851 | -0.11836 | 0.060542 | 0.076718 | 19.1066 | 16.2994 | 16.2389 | 0.030091 | -0.010868 | -0.008498 | -122.024 | 0.13838 | 0.048933 | 0.057431 | -121.9345 | -121.8855 | 122.144 | 122.0974 | 122.0564 | 45.4394 | -122.0067 | 0.043281 | 0.13273 | 0.18171 | 0.19264 | -122.0758
3721.7656 | 121.9482 | -0.10529 | 121.9391 | 1.4211e-13 | -0.023367 | 0.0061325 | 0.072406 | 0.0026515 | 0.073408 | -0.0099192 | -0.0044395 | -0.0019123 | 0.019186 | 0.031981 | 0.01415 | 19.1616 | 45.4349 | 16.3773 | 122.0387 | 122.0012 | 121.9557 | -0.049321 | 0.033099 | 0.082776 | -0.06093 | -0.057425 | 0.032021 | 0.062694 | -0.11836 | 0.055965 | 0.099607 | 19.2669 | 16.4825 | 16.4266 | 0.062137 | 0.016599 | -0.013075 | -121.9965 | 0.13839 | 0.044356 | 0.057431 | -121.9071 | -121.8764 | 122.144 | 122.1065 | 122.061 | 45.5402 | -121.9884 | 0.047861 | 0.13731 | 0.16798 | 0.18806 | -122.0574
3723.4688 | 122.1085 | -0.064087 | 121.8979 | 1.4211e-13 | -0.023581 | 0.0061325 | 0.07262 | 0.0028651 | 0.072981 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018758 | 0.031981 | 0.01415 | 19.1708 | 45.4028 | 16.5009 | 122.0295 | 121.9921 | 121.9465 | -0.049321 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 0.014766 | 0.13165 | 19.2348 | 16.565 | 16.5502 | 0.094179 | 0.048641 | -0.058852 | -121.9599 | 0.088028 | 0.007736 | 0.066588 | -121.8613 | -121.826 | 122.0936 | 122.0562 | 122.0106 | 45.4669 | -121.9472 | 0.002083 | 0.10069 | 0.13594 | 0.15144 | -122.0208
3725.25 | 121.9666 | -0.10071 | 121.9254 | 1.4211e-13 | -0.023367 | 0.0061325 | 0.072406 | 0.0028651 | 0.073408 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.031767 | 0.014364 | 19.4775 | 45.4852 | 16.5054 | 122.0387 | 121.9875 | 121.942 | -0.049321 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.041178 | 0.071851 | -0.11836 | 0.051387 | 0.11334 | 19.5782 | 16.6062 | 16.5548 | 0.062134 | 0.016596 | -0.017653 | -121.9874 | 0.12007 | 0.044357 | 0.06201 | -121.8842 | -121.8535 | 122.1394 | 122.0882 | 122.0427 | 45.586 | -121.9747 | 0.038704 | 0.14189 | 0.17256 | 0.18348 | -122.0437
3727 | 121.9437 | -0.10986 | 121.9345 | 1.4211e-13 | -0.022726 | 0.0059189 | 0.072193 | 0.0026515 | 0.073836 | -0.01755 | -0.0044395 | -0.0016987 | 0.018545 | 0.031981 | 0.014364 | 19.7064 | 45.5402 | 16.6703 | 122.0387 | 121.9921 | 121.9511 | -0.053899 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.071851 | -0.11378 | 0.055964 | 0.10419 | 19.8163 | 16.7801 | 16.7242 | 0.057558 | 0.016598 | -0.003919 | -122.0011 | 0.13838 | 0.048933 | 0.052852 | -121.8933 | -121.8627 | 122.1486 | 122.1019 | 122.061 | 45.6501 | -121.9884 | 0.043281 | 0.15104 | 0.18171 | 0.19722 | -122.0483
3728.7031 | 121.9574 | -0.10529 | 121.9299 | 1.4211e-13 | -0.022726 | 0.0063463 | 0.072406 | 0.0026515 | 0.073836 | -0.01755 | -0.0044395 | -0.0016987 | 0.018545 | 0.031981 | 0.01415 | 19.9033 | 45.4807 | 16.8259 | 122.0341 | 121.9875 | 121.9557 | -0.053899 | 0.033099 | 0.078197 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.11378 | 0.051387 | 0.10418 | 20.0086 | 16.9312 | 16.8798 | 0.057556 | 0.025754 | -0.008496 | -121.9965 | 0.13839 | 0.044356 | 0.052852 | -121.8979 | -121.8535 | 122.1394 | 122.0928 | 122.061 | 45.586 | -121.9838 | 0.038704 | 0.13731 | 0.18172 | 0.18348 | -122.0437
3730.4688 | 121.9803 | -0.11902 | 121.9528 | 1.4211e-13 | -0.022726 | 0.0059189 | 0.072193 | 0.0032925 | 0.073622 | -0.0022892 | -0.0044395 | -0.0021259 | 0.018331 | 0.031767 | 0.014364 | 20.0956 | 45.5173 | 16.8442 | 122.0387 | 121.9875 | 121.9465 | -0.049321 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.0366 | 0.067272 | -0.12294 | 0.069698 | 0.085874 | 20.2146 | 16.9633 | 16.8936 | 0.034668 | -0.006291 | -0.00392 | -122.0148 | 0.14754 | 0.058089 | 0.062009 | -121.9162 | -121.8855 | 122.1577 | 122.1065 | 122.0655 | 45.6363 | -122.0021 | 0.057015 | 0.15562 | 0.18629 | 0.19722 | -122.0758
3732.2188 | 122.0673 | -0.073242 | 121.8933 | 1.4211e-13 | -0.022513 | 0.0063463 | 0.072193 | 0.0035061 | 0.074049 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.031981 | 0.01415 | 20.1734 | 45.5036 | 16.8763 | 122.0387 | 121.9875 | 121.942 | -0.053899 | 0.033099 | 0.082776 | -0.06093 | -0.071161 | 0.041178 | 0.067272 | -0.11378 | 0.019343 | 0.14538 | 20.2467 | 16.9495 | 16.9302 | 0.094177 | 0.048639 | -0.04054 | -121.9645 | 0.10634 | 0.012312 | 0.052852 | -121.8521 | -121.826 | 122.1119 | 122.0607 | 122.0152 | 45.5768 | -121.9472 | 0.002081 | 0.11442 | 0.14051 | 0.15602 | -122.0071
3733.9844 | 121.994 | -0.09613 | 121.9391 | 1.4211e-13 | -0.021872 | 0.0061325 | 0.072406 | 0.0030789 | 0.07469 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.032194 | 0.014364 | 20.4298 | 45.5493 | 17.0274 | 122.0341 | 121.9921 | 121.9374 | -0.044742 | 0.02852 | 0.082776 | -0.056351 | -0.066582 | 0.041178 | 0.067272 | -0.11836 | 0.051388 | 0.095028 | 20.5259 | 17.1235 | 17.0721 | 0.05298 | -0.001715 | -0.022231 | -122.0057 | 0.12465 | 0.039779 | 0.06201 | -121.8979 | -121.8718 | 122.1302 | 122.0882 | 122.0335 | 45.6455 | -121.9838 | 0.029548 | 0.13731 | 0.1634 | 0.17891 | -122.0574
3735.7031 | 122.0764 | -0.059509 | 121.9025 | 1.4211e-13 | -0.021872 | 0.0063463 | 0.072834 | 0.0032925 | 0.074477 | -0.0099192 | -0.0040121 | -0.0019123 | 0.018545 | 0.031767 | 0.01415 | 20.2741 | 45.618 | 17.2838 | 122.0295 | 121.9875 | 121.942 | -0.049321 | 0.033099 | 0.082776 | -0.056351 | -0.071161 | 0.027442 | 0.067272 | -0.11836 | 0.010188 | 0.12707 | 20.3337 | 17.3433 | 17.3331 | 0.085022 | 0.039484 | -0.058852 | -121.9736 | 0.092608 | 0.003158 | 0.06201 | -121.875 | -121.8352 | 122.089 | 122.047 | 122.0015 | 45.6775 | -121.9518 | -0.011652 | 0.086951 | 0.12678 | 0.14228 | -122.0208
3737.4688 | 121.9666 | -0.11902 | 121.9482 | 1.4211e-13 | -0.021017 | 0.0061325 | 0.072834 | 0.0032925 | 0.07469 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018758 | 0.032194 | 0.014364 | 20.7366 | 45.6043 | 17.4394 | 122.0295 | 121.9875 | 121.9374 | -0.049321 | 0.033099 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.069698 | 0.081295 | 20.8556 | 17.5584 | 17.4887 | 0.039246 | -0.01087 | 0.000658 | -122.0148 | 0.15212 | 0.062668 | 0.06201 | -121.9116 | -121.8764 | 122.1486 | 122.1065 | 122.0564 | 45.7233 | -121.9976 | 0.052437 | 0.15562 | 0.19087 | 0.20637 | -122.0666
3739.2344 | 122.0901 | -0.064087 | 121.9162 | 1.4211e-13 | -0.021444 | 0.0063463 | 0.072406 | 0.0037199 | 0.07469 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.031767 | 0.01415 | 20.9197 | 45.5768 | 17.4028 | 122.025 | 121.9875 | 121.942 | -0.053899 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.0366 | 0.067272 | -0.12752 | 0.010188 | 0.10876 | 20.9838 | 17.4669 | 17.4567 | 0.071289 | 0.025751 | -0.063431 | -121.9828 | 0.083449 | -0.001422 | 0.062009 | -121.8796 | -121.8489 | 122.089 | 122.0516 | 122.006 | 45.6409 | -121.9701 | -0.002495 | 0.10069 | 0.13136 | 0.14686 | -122.0437
3741 | 122.081 | -0.073242 | 121.9025 | 1.4211e-13 | -0.021017 | 0.0061325 | 0.07262 | 0.0037199 | 0.074904 | 0.0053413 | -0.0046531 | -0.0014849 | 0.018758 | 0.031981 | 0.01415 | 20.558 | 45.6318 | 17.6958 | 122.0204 | 121.9966 | 121.9374 | -0.053899 | 0.023941 | 0.091933 | -0.065509 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 0.019343 | 0.11791 | 20.6313 | 17.769 | 17.7497 | 0.09418 | 0.034906 | -0.049697 | -121.9599 | 0.097183 | 0.007733 | 0.05743 | -121.8659 | -121.826 | 122.0936 | 122.0699 | 122.0106 | 45.705 | -121.9564 | 0.015817 | 0.10984 | 0.14967 | 0.16518 | -122.0254
3742.7031 | 122.081 | -0.045776 | 121.9162 | 1.4211e-13 | -0.021444 | 0.0063463 | 0.072834 | 0.0039335 | 0.075118 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018545 | 0.031981 | 0.01415 | 20.7549 | 45.6409 | 17.8698 | 122.0295 | 121.9875 | 121.942 | -0.044742 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.032021 | 0.071851 | -0.12294 | 0.001034 | 0.11334 | 20.8007 | 17.9156 | 17.9145 | 0.071289 | 0.025751 | -0.077163 | -121.9919 | 0.069717 | -0.019733 | 0.05743 | -121.8842 | -121.8443 | 122.0753 | 122.0333 | 121.9877 | 45.6867 | -121.9609 | -0.029963 | 0.077797 | 0.11763 | 0.12855 | -122.0391
3744.4688 | 122.0856 | -0.036621 | 121.9025 | 1.4211e-13 | -0.020589 | 0.0063463 | 0.072834 | 0.0041471 | 0.075118 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018972 | 0.031553 | 0.013723 | 21.1807 | 45.6867 | 17.9339 | 122.0295 | 121.9875 | 121.942 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.0366 | 0.067272 | -0.11378 | -0.017278 | 0.12707 | 21.2173 | 17.9705 | 17.9878 | 0.085022 | 0.039484 | -0.077161 | -121.969 | 0.065141 | -0.024309 | 0.052852 | -121.8659 | -121.8352 | 122.0662 | 122.0241 | 121.9786 | 45.7233 | -121.9564 | -0.029961 | 0.073221 | 0.10389 | 0.11482 | -122.0162
3746.25 | 122.049 | -0.054932 | 121.9025 | 1.4211e-13 | -0.020803 | 0.0061325 | 0.072834 | 0.0039335 | 0.075545 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018545 | 0.031981 | 0.01415 | 21.4737 | 45.7004 | 18.0117 | 122.025 | 121.9829 | 121.9374 | -0.053899 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.027442 | 0.07643 | -0.12752 | 0.001033 | 0.12249 | 21.5286 | 18.0666 | 18.0656 | 0.080443 | 0.034906 | -0.072586 | -121.969 | 0.083452 | -0.010577 | 0.062009 | -121.875 | -121.826 | 122.0799 | 122.0378 | 121.9923 | 45.7554 | -121.9564 | -0.01165 | 0.082374 | 0.13136 | 0.13313 | -122.03
3747.9531 | 122.0764 | -0.073242 | 121.907 | 1.4211e-13 | -0.020376 | 0.0063463 | 0.07262 | 0.0043609 | 0.075545 | -0.0099192 | -0.0048667 | -0.0016987 | 0.018545 | 0.031767 | 0.01415 | 21.1166 | 45.7645 | 18.1948 | 122.025 | 121.9829 | 121.942 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 0.023921 | 0.11792 | 21.1898 | 18.2681 | 18.2442 | 0.075866 | 0.034907 | -0.045119 | -121.9736 | 0.097183 | 0.012312 | 0.057431 | -121.875 | -121.8352 | 122.0982 | 122.0562 | 122.0152 | 45.8378 | -121.9564 | 0.00666 | 0.10526 | 0.14509 | 0.15144 | -122.0254
3749.7188 | 121.9711 | -0.09613 | 121.9299 | 1.4211e-13 | -0.020162 | 0.0063463 | 0.07262 | 0.0039335 | 0.075331 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.031767 | 0.014364 | 21.4325 | 45.7691 | 18.291 | 122.025 | 121.9875 | 121.942 | -0.049321 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.11836 | 0.046809 | 0.095027 | 21.5286 | 18.3871 | 18.3403 | 0.057556 | 0.012018 | -0.022231 | -121.9919 | 0.12007 | 0.039779 | 0.06201 | -121.8933 | -121.8535 | 122.1211 | 122.0836 | 122.0381 | 45.8652 | -121.9793 | 0.034126 | 0.13273 | 0.17256 | 0.18348 | -122.0483
3751.4844 | 122.0306 | -0.07782 | 121.9025 | 1.4211e-13 | -0.020162 | 0.0061325 | 0.073048 | 0.0043609 | 0.075759 | -0.0099192 | -0.0040121 | -0.0019123 | 0.018758 | 0.031767 | 0.01415 | 21.5836 | 45.7966 | 18.3642 | 122.025 | 121.9875 | 121.942 | -0.053899 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.081008 | -0.11836 | 0.023921 | 0.12249 | 21.6614 | 18.442 | 18.4181 | 0.085022 | 0.039484 | -0.040541 | -121.9645 | 0.10176 | 0.01689 | 0.057431 | -121.8659 | -121.8215 | 122.1028 | 122.0653 | 122.0198 | 45.8744 | -121.9564 | 0.015816 | 0.11442 | 0.15883 | 0.16517 | -122.0208
3753.1875 | 122.0398 | -0.045776 | 121.8796 | 1.4211e-13 | -0.019735 | 0.0061325 | 0.073261 | 0.0043609 | 0.075759 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018758 | 0.031981 | 0.014364 | 21.9636 | 45.8057 | 18.4558 | 122.0158 | 121.9875 | 121.942 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.071851 | -0.11836 | -0.003545 | 0.13622 | 22.0094 | 18.5016 | 18.5051 | 0.10791 | 0.062372 | -0.072585 | -121.9416 | 0.069717 | -0.015154 | 0.057431 | -121.8476 | -121.8077 | 122.0616 | 122.0333 | 121.9877 | 45.8515 | -121.9289 | -0.016228 | 0.077797 | 0.11763 | 0.12855 | -121.9979
3754.8906 | 121.9803 | -0.09613 | 121.9299 | 1.4211e-13 | -0.019948 | 0.0061325 | 0.07262 | 0.0045745 | 0.075759 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018545 | 0.031981 | 0.01415 | 21.7713 | 45.8561 | 18.6069 | 122.025 | 121.9829 | 121.9328 | -0.049321 | 0.033099 | 0.082776 | -0.065509 | -0.057425 | 0.027442 | 0.067272 | -0.12294 | 0.046809 | 0.095027 | 21.8674 | 18.703 | 18.6562 | 0.052977 | 0.002861 | -0.026809 | -121.9874 | 0.12923 | 0.030621 | 0.05743 | -121.9025 | -121.8627 | 122.1211 | 122.079 | 122.0289 | 45.9522 | -121.9793 | 0.038705 | 0.12357 | 0.1634 | 0.17891 | -122.0529
3756.6562 | 121.9299 | -0.11444 | 121.9345 | 1.4211e-13 | -0.019307 | 0.0063463 | 0.072834 | 0.0045745 | 0.076399 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018331 | 0.031767 | 0.013937 | 22.1055 | 45.8698 | 18.8129 | 122.025 | 121.9875 | 121.9374 | -0.053899 | 0.033099 | 0.087354 | -0.065509 | -0.071161 | 0.0366 | 0.071851 | -0.12294 | 0.060542 | 0.09045 | 22.2199 | 18.9273 | 18.8668 | 0.052979 | 0.002863 | -0.008498 | -122.0057 | 0.14754 | 0.048932 | 0.05743 | -121.8979 | -121.8627 | 122.1394 | 122.1019 | 122.0518 | 45.9843 | -121.9884 | 0.04328 | 0.15104 | 0.18629 | 0.2018 | -122.0574
3758.375 | 121.9574 | -0.10071 | 121.9299 | 1.4211e-13 | -0.01888 | 0.0061325 | 0.073048 | 0.0045745 | 0.076613 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.031981 | 0.01415 | 22.3939 | 45.9019 | 18.8129 | 122.025 | 121.9783 | 121.942 | -0.049321 | 0.019362 | 0.082776 | -0.051772 | -0.066582 | 0.032021 | 0.071851 | -0.11378 | 0.051387 | 0.095027 | 22.4947 | 18.9136 | 18.8622 | 0.048398 | 0.012018 | -0.013074 | -121.9965 | 0.12007 | 0.048936 | 0.06201 | -121.8979 | -121.8581 | 122.1257 | 122.079 | 122.0427 | 46.0026 | -121.9793 | 0.034126 | 0.13273 | 0.17256 | 0.18348 | -122.0437
3760.1406 | 122.0856 | -0.054932 | 121.8842 | 1.4211e-13 | -0.019094 | 0.0063463 | 0.07262 | 0.0043609 | 0.076827 | -0.01755 | -0.0040121 | -0.0019123 | 0.018331 | 0.031981 | 0.01415 | 22.4535 | 45.9339 | 18.7992 | 122.0295 | 121.9829 | 121.9465 | -0.053899 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.027442 | 0.067272 | -0.11378 | 0.001033 | 0.14538 | 22.5084 | 18.8541 | 18.8531 | 0.098754 | 0.062374 | -0.05885 | -121.9507 | 0.083452 | -0.005998 | 0.052852 | -121.8567 | -121.8169 | 122.0845 | 122.0378 | 122.0015 | 45.9889 | -121.9381 | -0.01165 | 0.082374 | 0.1222 | 0.14229 | -121.9979
3761.9062 | 122.081 | -0.073242 | 121.8979 | 1.4211e-13 | -0.01888 | 0.0063463 | 0.073048 | 0.0043609 | 0.076827 | -0.01755 | -0.0040121 | -0.0016987 | 0.018758 | 0.031767 | 0.013937 | 22.4214 | 45.9385 | 18.9777 | 122.0204 | 121.9783 | 121.9465 | -0.053899 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.032021 | 0.07643 | -0.11378 | 0.019343 | 0.12249 | 22.4947 | 19.051 | 19.0316 | 0.080442 | 0.048641 | -0.04054 | -121.9599 | 0.10176 | 0.007733 | 0.048273 | -121.8659 | -121.8215 | 122.0936 | 122.0516 | 122.0198 | 46.0118 | -121.9518 | 0.011238 | 0.10526 | 0.14967 | 0.15602 | -122.0117
3763.6094 | 121.9574 | -0.10071 | 121.9299 | 1.4211e-13 | -0.018666 | 0.0061325 | 0.07262 | 0.0047881 | 0.07704 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.01415 | 22.9342 | 45.998 | 18.9686 | 122.0158 | 121.9829 | 121.9374 | -0.040163 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.027442 | 0.067272 | -0.11836 | 0.060545 | 0.08587 | 23.0349 | 19.0693 | 19.0087 | 0.052977 | 0.00744 | -0.017653 | -121.9965 | 0.12007 | 0.039778 | 0.057431 | -121.9025 | -121.8627 | 122.1165 | 122.0836 | 122.0381 | 46.0988 | -121.9701 | 0.034126 | 0.12815 | 0.16798 | 0.18348 | -122.0483
3765.375 | 122.113 | -0.050354 | 121.8887 | 1.4211e-13 | -0.017812 | 0.0063463 | 0.07262 | 0.0050019 | 0.07704 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.031767 | 0.014364 | 23.0212 | 46.1491 | 19.3394 | 122.0204 | 121.9829 | 121.9328 | -0.044742 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.12294 | 0.005612 | 0.13165 | 23.0715 | 19.3898 | 19.3841 | 0.094176 | 0.04406 | -0.072585 | -121.9553 | 0.078874 | -0.010576 | 0.062009 | -121.8613 | -121.8169 | 122.0707 | 122.0333 | 121.9831 | 46.1995 | -121.9335 | -0.016228 | 0.077796 | 0.12221 | 0.12855 | -122.0117
3767.1562 | 122.0764 | -0.054932 | 121.9482 | 1.4211e-13 | -0.017812 | 0.0061325 | 0.07262 | 0.0050019 | 0.077468 | -0.01755 | -0.0040121 | -0.0016987 | 0.018758 | 0.031767 | 0.01415 | 23.1768 | 46.0988 | 19.463 | 122.0158 | 121.9875 | 121.9282 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 0.001033 | 0.06756 | 23.2318 | 19.518 | 19.5169 | 0.039246 | -0.020028 | -0.063429 | -122.0148 | 0.083452 | -0.005998 | 0.057431 | -121.9162 | -121.8764 | 122.0707 | 122.0424 | 121.9831 | 46.1537 | -122.0021 | -0.01165 | 0.086953 | 0.12678 | 0.13771 | -122.0666
3768.9219 | 122.081 | -0.041199 | 121.875 | 1.4211e-13 | -0.017812 | 0.0061325 | 0.072834 | 0.0050019 | 0.077895 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018758 | 0.031767 | 0.014364 | 23.4103 | 46.1354 | 19.5363 | 122.025 | 121.9829 | 121.942 | -0.044742 | 0.033099 | 0.078197 | -0.06093 | -0.062004 | 0.0366 | 0.07643 | -0.11836 | -0.003543 | 0.14996 | 23.4515 | 19.5775 | 19.581 | 0.10791 | 0.06695 | -0.077162 | -121.937 | 0.074298 | -0.019731 | 0.057431 | -121.8384 | -121.7986 | 122.0662 | 122.0241 | 121.9831 | 46.1766 | -121.9197 | -0.020805 | 0.077799 | 0.11763 | 0.1194 | -121.9934
3770.6406 | 121.9757 | -0.086975 | 121.9208 | 1.4211e-13 | -0.017598 | 0.0063463 | 0.07262 | 0.0052155 | 0.077895 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 23.447 | 46.1491 | 19.6004 | 122.0204 | 121.9738 | 121.9374 | -0.053899 | 0.033099 | 0.087354 | -0.051772 | -0.071161 | 0.032021 | 0.071851 | -0.11378 | 0.033076 | 0.099604 | 23.5339 | 19.6873 | 19.6543 | 0.052975 | 0.016596 | -0.026807 | -121.9919 | 0.12007 | 0.035203 | 0.06201 | -121.8888 | -121.8489 | 122.1074 | 122.0607 | 122.0243 | 46.2361 | -121.9747 | 0.015814 | 0.119 | 0.15883 | 0.17433 | -122.0346
3772.4062 | 122.0032 | -0.10071 | 121.9162 | 1.4211e-13 | -0.017171 | 0.0065599 | 0.073261 | 0.0052155 | 0.077895 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.031767 | 0.013723 | 23.7354 | 46.2544 | 19.811 | 122.025 | 121.9783 | 121.9374 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.027442 | 0.071851 | -0.1092 | 0.055966 | 0.10876 | 23.8361 | 19.9117 | 19.8557 | 0.062131 | 0.021173 | -0.008495 | -121.9782 | 0.12923 | 0.039778 | 0.048273 | -121.8888 | -121.8443 | 122.1257 | 122.079 | 122.0381 | 46.3552 | -121.9609 | 0.038704 | 0.12815 | 0.17256 | 0.18348 | -122.0254
3774.1094 | 121.9803 | -0.10529 | 121.9574 | 1.4211e-13 | -0.016743 | 0.0063463 | 0.073048 | 0.0050019 | 0.07875 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.031981 | 0.013723 | 24.0238 | 46.3048 | 19.8751 | 122.0204 | 121.9829 | 121.9374 | -0.053899 | 0.023941 | 0.091933 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 0.051387 | 0.062983 | 24.1291 | 19.9803 | 19.929 | 0.025512 | -0.020025 | -0.017653 | -122.0194 | 0.12923 | 0.048935 | 0.066588 | -121.9208 | -121.8855 | 122.1257 | 122.0882 | 122.0427 | 46.4101 | -122.0113 | 0.043282 | 0.14189 | 0.17714 | 0.19722 | -122.0803
3775.9062 | 122.0947 | -0.059509 | 121.8842 | 1.4211e-13 | -0.01653 | 0.0067735 | 0.073048 | 0.0054291 | 0.07875 | -0.0099192 | -0.0046531 | -0.0014849 | 0.019186 | 0.032194 | 0.01415 | 24.1063 | 46.4147 | 20.0902 | 122.0204 | 121.9783 | 121.9374 | -0.049321 | 0.033099 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.067272 | -0.12752 | 0.010188 | 0.13622 | 24.1658 | 20.1498 | 20.1396 | 0.094175 | 0.053217 | -0.068009 | -121.9553 | 0.092608 | -0.001421 | 0.066588 | -121.8476 | -121.8169 | 122.0799 | 122.0378 | 121.9969 | 46.4742 | -121.9335 | -0.011652 | 0.096109 | 0.12678 | 0.14228 | -122.0117
3777.6875 | 121.994 | -0.10529 | 121.9162 | 1.4211e-13 | -0.01653 | 0.0067735 | 0.073261 | 0.0056427 | 0.078322 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.031767 | 0.014364 | 24.2482 | 46.5109 | 20.1086 | 122.025 | 121.9829 | 121.9328 | -0.049321 | 0.02852 | 0.073618 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.11836 | 0.055965 | 0.10876 | 24.3535 | 20.2138 | 20.1579 | 0.06671 | 0.016594 | -0.013075 | -121.9782 | 0.13381 | 0.048935 | 0.06201 | -121.8842 | -121.8443 | 122.1302 | 122.0882 | 122.0381 | 46.6161 | -121.9655 | 0.043282 | 0.13731 | 0.17714 | 0.1789 | -122.0346
3779.4375 | 121.9666 | -0.09613 | 121.9254 | 1.4211e-13 | -0.016316 | 0.0069873 | 0.073048 | 0.0056427 | 0.079391 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.031981 | 0.013937 | 24.6602 | 46.6482 | 20.2322 | 122.0204 | 121.9738 | 121.9328 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.1092 | 0.046809 | 0.095026 | 24.7564 | 20.3283 | 20.2815 | 0.048397 | 0.007439 | -0.013073 | -121.9919 | 0.12007 | 0.0352 | 0.048273 | -121.8888 | -121.8489 | 122.1165 | 122.0699 | 122.0289 | 46.7443 | -121.9747 | 0.029548 | 0.13273 | 0.17256 | 0.17891 | -122.0346
3781.1562 | 121.994 | -0.082397 | 121.907 | 1.4211e-13 | -0.016102 | 0.0065599 | 0.073261 | 0.0056427 | 0.079177 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018331 | 0.032194 | 0.013937 | 24.5687 | 46.6848 | 20.4748 | 122.0158 | 121.9783 | 121.9282 | -0.040163 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.032021 | 0.067272 | -0.12294 | 0.042234 | 0.10876 | 24.6511 | 20.5572 | 20.515 | 0.071287 | 0.021171 | -0.040542 | -121.969 | 0.10176 | 0.021467 | 0.062009 | -121.875 | -121.8398 | 122.0982 | 122.0607 | 122.0106 | 46.7672 | -121.9472 | 0.020393 | 0.11442 | 0.14967 | 0.16059 | -122.03
3782.9219 | 121.9528 | -0.091553 | 121.9208 | 1.4211e-13 | -0.015461 | 0.0065599 | 0.073048 | 0.0056427 | 0.079391 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018331 | 0.031767 | 0.013937 | 24.8846 | 46.7398 | 20.5801 | 122.0204 | 121.9783 | 121.9328 | -0.044742 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.022864 | 0.07643 | -0.11836 | 0.046811 | 0.099604 | 24.9761 | 20.6717 | 20.6249 | 0.057554 | 0.012017 | -0.026808 | -121.9874 | 0.11549 | 0.030623 | 0.057431 | -121.8979 | -121.8443 | 122.1119 | 122.0699 | 122.0243 | 46.8313 | -121.9655 | 0.024971 | 0.11442 | 0.16798 | 0.16975 | -122.0391
3784.6719 | 121.9666 | -0.1236 | 121.9437 | 1.4211e-13 | -0.015248 | 0.0067735 | 0.073689 | 0.0062837 | 0.079818 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018758 | 0.031553 | 0.01415 | 25.2829 | 46.8542 | 20.8823 | 122.0158 | 121.9783 | 121.9374 | -0.053899 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.027442 | 0.071851 | -0.1092 | 0.069697 | 0.072137 | 25.4065 | 21.0059 | 20.9362 | 0.034665 | -0.006293 | 0.014393 | -122.0057 | 0.14754 | 0.067245 | 0.052852 | -121.9162 | -121.8718 | 122.1394 | 122.1019 | 122.061 | 46.9778 | -121.9976 | 0.061592 | 0.15104 | 0.19545 | 0.21095 | -122.0529
3786.4375 | 122.0673 | -0.054932 | 121.9162 | 1.4211e-13 | -0.015248 | 0.0069873 | 0.073475 | 0.0058565 | 0.080245 | -0.01755 | -0.0040121 | -0.0014849 | 0.018545 | 0.031767 | 0.013937 | 25.4111 | 46.8726 | 20.809 | 122.0158 | 121.9738 | 121.9236 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.027442 | 0.071851 | -0.11836 | 0.005611 | 0.099603 | 25.466 | 20.864 | 20.8584 | 0.057552 | 0.007437 | -0.063429 | -121.9874 | 0.083452 | -0.005998 | 0.057431 | -121.8888 | -121.8443 | 122.0707 | 122.0287 | 121.9786 | 46.9275 | -121.9655 | -0.016229 | 0.082374 | 0.12678 | 0.13771 | -122.0346
3788.1406 | 122.0718 | -0.041199 | 121.8842 | 1.4211e-13 | -0.015034 | 0.0067735 | 0.073048 | 0.0062837 | 0.080032 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018758 | 0.031981 | 0.01415 | 25.4615 | 47.0099 | 20.9098 | 122.0112 | 121.9738 | 121.9282 | -0.049321 | 0.02852 | 0.091933 | -0.06093 | -0.080318 | 0.0366 | 0.062694 | -0.11836 | -0.008122 | 0.12707 | 25.5027 | 20.951 | 20.9591 | 0.089596 | 0.044059 | -0.077162 | -121.9645 | 0.069719 | -0.019731 | 0.057431 | -121.8476 | -121.8215 | 122.0524 | 122.0149 | 121.9694 | 47.0511 | -121.9335 | -0.039119 | 0.077799 | 0.10389 | 0.13313 | -122.0025
3789.9219 | 121.9254 | -0.09613 | 121.9208 | 1.4211e-13 | -0.01482 | 0.0067735 | 0.073475 | 0.0067111 | 0.080245 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018545 | 0.031767 | 0.01415 | 25.4248 | 47.216 | 21.4271 | 122.0158 | 121.9783 | 121.9236 | -0.053899 | 0.02852 | 0.087354 | -0.051772 | -0.057425 | 0.032021 | 0.07643 | -0.11836 | 0.042231 | 0.095026 | 25.521 | 21.5232 | 21.481 | 0.057554 | 0.00286 | -0.022231 | -121.9782 | 0.12465 | 0.044358 | 0.066589 | -121.8888 | -121.8443 | 122.1119 | 122.0745 | 122.0198 | 47.3121 | -121.9747 | 0.038705 | 0.12815 | 0.17256 | 0.18348 | -122.0391
3791.7031 | 121.9345 | -0.091553 | 121.9116 | 1.4211e-13 | -0.014393 | 0.0069873 | 0.073261 | 0.0067111 | 0.080245 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 25.6217 | 47.2709 | 21.4958 | 122.0158 | 121.9738 | 121.9328 | -0.053899 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.11836 | 0.037654 | 0.10418 | 25.7133 | 21.5873 | 21.5497 | 0.06213 | 0.021172 | -0.026808 | -121.9782 | 0.12007 | 0.030623 | 0.057431 | -121.8842 | -121.8398 | 122.1074 | 122.0653 | 122.0243 | 47.3625 | -121.9655 | 0.024971 | 0.11899 | 0.1634 | 0.17433 | -122.03
3793.4062 | 122.0993 | -0.045776 | 121.875 | 1.4211e-13 | -0.013966 | 0.0067735 | 0.073475 | 0.0069247 | 0.080245 | -0.01755 | -0.0044395 | -0.0019123 | 0.018331 | 0.031767 | 0.01415 | 25.8003 | 47.3899 | 21.7201 | 122.0066 | 121.9829 | 121.9282 | -0.040163 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.081008 | -0.12752 | 0.005613 | 0.13165 | 25.846 | 21.7659 | 21.7603 | 0.10791 | 0.053214 | -0.081742 | -121.9462 | 0.069717 | -0.015154 | 0.066588 | -121.8384 | -121.794 | 122.0524 | 122.0287 | 121.974 | 47.4357 | -121.9152 | -0.025385 | 0.082376 | 0.12678 | 0.13313 | -122.0025
3795.1562 | 121.9391 | -0.1236 | 121.9162 | 1.4211e-13 | -0.014179 | 0.0069873 | 0.073902 | 0.0067111 | 0.080459 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018545 | 0.031767 | 0.01415 | 25.9651 | 47.5639 | 21.9856 | 122.0158 | 121.9738 | 121.9282 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.11378 | 0.074275 | 0.099603 | 26.0887 | 22.1092 | 22.035 | 0.057552 | 0.012015 | 0.009814 | -121.9828 | 0.14754 | 0.062666 | 0.052852 | -121.8888 | -121.8443 | 122.1394 | 122.0973 | 122.0518 | 47.6875 | -121.9655 | 0.057014 | 0.15104 | 0.19545 | 0.20179 | -122.03
3796.8594 | 121.962 | -0.10071 | 121.9254 | 1.4211e-13 | -0.013752 | 0.0069873 | 0.073475 | 0.0067111 | 0.080459 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018545 | 0.032194 | 0.013937 | 26.2306 | 47.6097 | 22.0131 | 122.0021 | 121.9692 | 121.9236 | -0.058478 | 0.023941 | 0.082776 | -0.047194 | -0.062004 | 0.032021 | 0.067272 | -0.11836 | 0.04223 | 0.076713 | 26.3313 | 22.1138 | 22.0716 | 0.043818 | -0.001718 | -0.017653 | -121.9874 | 0.12465 | 0.053514 | 0.071167 | -121.8933 | -121.8581 | 122.1028 | 122.0699 | 122.0243 | 47.7104 | -121.9838 | 0.038704 | 0.13273 | 0.16798 | 0.18348 | -122.0437
3798.625 | 122.0444 | -0.045776 | 121.8842 | 1.4211e-13 | -0.012897 | 0.0067735 | 0.073475 | 0.0071385 | 0.0811 | -0.01755 | -0.0042257 | -0.0016987 | 0.018331 | 0.031767 | 0.013937 | 26.6198 | 47.7013 | 22.2603 | 122.0066 | 121.9692 | 121.9191 | -0.049321 | 0.023941 | 0.078197 | -0.051772 | -0.062004 | 0.032021 | 0.067272 | -0.12752 | -0.003545 | 0.12249 | 26.6656 | 22.3061 | 22.3097 | 0.085017 | 0.034902 | -0.081742 | -121.9462 | 0.069717 | -0.005996 | 0.075746 | -121.8521 | -121.8169 | 122.0524 | 122.0149 | 121.9648 | 47.7471 | -121.9335 | -0.016228 | 0.077797 | 0.11305 | 0.12397 | -122.0117
3800.3906 | 121.9757 | -0.1236 | 121.9208 | 1.4211e-13 | -0.01247 | 0.0076283 | 0.073475 | 0.0069247 | 0.081527 | -0.01755 | -0.0044395 | -0.0023397 | 0.018545 | 0.031767 | 0.01415 | 27.0593 | 47.7562 | 22.2695 | 122.0066 | 121.9692 | 121.9328 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.027442 | 0.071851 | -0.11836 | 0.074275 | 0.085869 | 27.1829 | 22.3931 | 22.3188 | 0.048396 | 0.012017 | 0.005235 | -121.9828 | 0.14754 | 0.067245 | 0.06201 | -121.8933 | -121.8489 | 122.1302 | 122.0928 | 122.0564 | 47.8798 | -121.9701 | 0.061592 | 0.15104 | 0.19545 | 0.20637 | -122.0391
3802.0938 | 121.9391 | -0.09613 | 121.9391 | 1.4211e-13 | -0.012684 | 0.0074147 | 0.073261 | 0.0073521 | 0.081314 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018758 | 0.031553 | 0.014364 | 26.8716 | 47.8432 | 22.6495 | 122.0158 | 121.9646 | 121.9236 | -0.049321 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.067272 | -0.12294 | 0.046809 | 0.076715 | 26.9677 | 22.7456 | 22.6988 | 0.025506 | -0.015451 | -0.026809 | -122.0057 | 0.12007 | 0.0352 | 0.062009 | -121.9025 | -121.8718 | 122.1119 | 122.0607 | 122.0198 | 47.9394 | -121.9884 | 0.029548 | 0.13273 | 0.1634 | 0.18348 | -122.062
3803.8594 | 122.0718 | -0.041199 | 121.8796 | 1.4211e-13 | -0.012256 | 0.0072009 | 0.073475 | 0.0073521 | 0.082382 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018545 | 0.031981 | 0.01415 | 27.4943 | 47.8478 | 22.5488 | 122.0112 | 121.9646 | 121.9282 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.032021 | 0.067272 | -0.11836 | -0.008122 | 0.13165 | 27.5355 | 22.59 | 22.5981 | 0.085015 | 0.048636 | -0.077162 | -121.9462 | 0.06514 | -0.019731 | 0.057431 | -121.8476 | -121.8123 | 122.0524 | 122.0058 | 121.9694 | 47.889 | -121.9289 | -0.025383 | 0.07322 | 0.10847 | 0.12398 | -121.9979
3805.625 | 121.9894 | -0.10529 | 121.8979 | 1.4211e-13 | -0.012256 | 0.0074147 | 0.073689 | 0.0075657 | 0.081741 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018758 | 0.031981 | 0.013937 | 27.4347 | 47.9852 | 22.8601 | 122.0112 | 121.9692 | 121.9191 | -0.058478 | 0.02852 | 0.078197 | -0.047194 | -0.066582 | 0.0366 | 0.07643 | -0.11836 | 0.046808 | 0.11334 | 27.54 | 22.9654 | 22.9186 | 0.071284 | 0.021169 | -0.013075 | -121.9645 | 0.13381 | 0.058092 | 0.071167 | -121.8613 | -121.8215 | 122.1165 | 122.0745 | 122.0243 | 48.0904 | -121.9564 | 0.038704 | 0.14189 | 0.18172 | 0.18348 | -122.0162
3807.3906 | 121.9986 | -0.10071 | 121.907 | 1.4211e-13 | -0.011615 | 0.0072009 | 0.073475 | 0.0079931 | 0.082596 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.031767 | 0.013937 | 27.3386 | 48.1179 | 23.1668 | 122.0066 | 121.9692 | 121.9282 | -0.044742 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.12294 | 0.055966 | 0.099602 | 27.4393 | 23.2676 | 23.2116 | 0.062129 | 0.021171 | -0.022231 | -121.9782 | 0.12465 | 0.039778 | 0.062009 | -121.8704 | -121.8352 | 122.1074 | 122.0699 | 122.0289 | 48.2186 | -121.9518 | 0.029547 | 0.13731 | 0.17256 | 0.18348 | -122.03
3809.0938 | 121.9345 | -0.1236 | 121.9299 | 1.4211e-13 | -0.011402 | 0.0072009 | 0.073475 | 0.0075657 | 0.082596 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.032194 | 0.013723 | 27.5034 | 48.2232 | 23.1394 | 122.0112 | 121.9646 | 121.9145 | -0.049321 | 0.033099 | 0.091933 | -0.051772 | -0.066582 | 0.027442 | 0.07643 | -0.11836 | 0.074275 | 0.081292 | 27.627 | 23.263 | 23.1887 | 0.034661 | -0.015453 | 0.005235 | -121.9965 | 0.1567 | 0.071824 | 0.066589 | -121.9025 | -121.8535 | 122.1348 | 122.0882 | 122.0381 | 48.3468 | -121.9793 | 0.057014 | 0.15104 | 0.20003 | 0.21553 | -122.0483
3810.8594 | 121.9894 | -0.10529 | 121.9208 | 1.4211e-13 | -0.010974 | 0.0072009 | 0.073261 | 0.0079931 | 0.082809 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018331 | 0.032194 | 0.013937 | 28.0254 | 48.3102 | 23.1256 | 122.0021 | 121.9646 | 121.9191 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11378 | 0.051387 | 0.081291 | 28.1306 | 23.2309 | 23.1795 | 0.043817 | -0.001719 | -0.008496 | -121.9874 | 0.12923 | 0.044356 | 0.052852 | -121.8842 | -121.8489 | 122.1074 | 122.0699 | 122.0243 | 48.4155 | -121.9747 | 0.038704 | 0.14189 | 0.17714 | 0.18806 | -122.0346
3812.5625 | 122.0627 | -0.050354 | 121.8796 | 1.4211e-13 | -0.011188 | 0.0072009 | 0.073689 | 0.0079931 | 0.082809 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018331 | 0.031767 | 0.013723 | 27.888 | 48.4476 | 23.0661 | 122.0112 | 121.96 | 121.9145 | -0.044742 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 0.005612 | 0.13165 | 27.9384 | 23.1165 | 23.1109 | 0.080436 | 0.034901 | -0.068007 | -121.9462 | 0.078874 | -0.010576 | 0.057431 | -121.8476 | -121.8077 | 122.0616 | 122.0104 | 121.9648 | 48.498 | -121.9243 | -0.016228 | 0.082375 | 0.12221 | 0.12855 | -121.9979
3814.3281 | 121.9894 | -0.07782 | 121.9025 | 1.4211e-13 | -0.010761 | 0.0072009 | 0.073475 | 0.0079931 | 0.082809 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.031767 | 0.01415 | 28.355 | 48.6307 | 23.4782 | 122.0021 | 121.9646 | 121.9236 | -0.053899 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.027442 | 0.07643 | -0.11378 | 0.023921 | 0.099601 | 28.4328 | 23.556 | 23.5321 | 0.062127 | 0.02117 | -0.035962 | -121.969 | 0.10634 | 0.012311 | 0.048273 | -121.875 | -121.826 | 122.0799 | 122.0424 | 122.0015 | 48.7086 | -121.9564 | 0.011238 | 0.10526 | 0.15425 | 0.1606 | -122.0162
3816.0312 | 122.0947 | -0.064087 | 121.8613 | 1.4211e-13 | -0.010761 | 0.0072009 | 0.073902 | 0.0082067 | 0.083237 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.031981 | 0.013937 | 28.4969 | 48.7132 | 23.524 | 122.0021 | 121.9692 | 121.9236 | -0.053899 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.067272 | -0.11378 | 0.010188 | 0.1408 | 28.561 | 23.588 | 23.5779 | 0.10791 | 0.062369 | -0.049695 | -121.9233 | 0.083449 | 0.003157 | 0.052852 | -121.8292 | -121.794 | 122.0662 | 122.0333 | 121.9877 | 48.7772 | -121.9152 | 0.002083 | 0.096108 | 0.13136 | 0.14686 | -121.975
3817.7969 | 122.0673 | -0.068665 | 121.8842 | 1.4211e-13 | -0.01012 | 0.0072009 | 0.073902 | 0.0084205 | 0.083237 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018545 | 0.032194 | 0.013937 | 28.4786 | 48.8414 | 23.6933 | 122.0021 | 121.9554 | 121.9191 | -0.044742 | 0.033099 | 0.087354 | -0.070087 | -0.071161 | 0.0366 | 0.067272 | -0.11836 | 0.023923 | 0.11791 | 28.5473 | 23.762 | 23.7381 | 0.07128 | 0.034902 | -0.049696 | -121.9553 | 0.10176 | -0.001422 | 0.048274 | -121.8476 | -121.8169 | 122.0707 | 122.0241 | 121.9877 | 48.91 | -121.9289 | -0.002496 | 0.10526 | 0.13594 | 0.15602 | -122.0025
3819.5625 | 121.9849 | -0.091553 | 121.8979 | 1.4211e-13 | -0.010333 | 0.0072009 | 0.073902 | 0.0082067 | 0.08345 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018331 | 0.031553 | 0.014364 | 28.7259 | 48.9696 | 23.7666 | 121.9975 | 121.9646 | 121.9099 | -0.049321 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.032021 | 0.071851 | -0.12294 | 0.042232 | 0.0996 | 28.8174 | 23.8582 | 23.8159 | 0.066705 | 0.012012 | -0.031386 | -121.9645 | 0.11091 | 0.026044 | 0.05743 | -121.8659 | -121.826 | 122.089 | 122.0561 | 122.0015 | 49.0611 | -121.9472 | 0.024971 | 0.12357 | 0.1634 | 0.17433 | -122.0208
3821.2656 | 121.9528 | -0.10986 | 121.9299 | 1.4211e-13 | -0.0099059 | 0.0074147 | 0.073689 | 0.0086341 | 0.083664 | 0.0053413 | -0.0042257 | -0.0014849 | 0.018758 | 0.032194 | 0.013937 | 29.0875 | 49.139 | 23.8811 | 121.9975 | 121.9554 | 121.9145 | -0.049321 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.032021 | 0.062694 | -0.11836 | 0.060542 | 0.067556 | 29.1974 | 23.9909 | 23.9304 | 0.025503 | -0.015453 | -0.008498 | -121.9965 | 0.1338 | 0.044354 | 0.052852 | -121.8979 | -121.8672 | 122.1074 | 122.0653 | 122.0243 | 49.2488 | -121.9793 | 0.043281 | 0.14188 | 0.17256 | 0.19264 | -122.0483
3823.0312 | 122.0215 | -0.054932 | 121.8796 | 1.4211e-13 | -0.0092649 | 0.0072009 | 0.073902 | 0.0086341 | 0.083664 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018972 | 0.031767 | 0.013937 | 28.9502 | 49.2626 | 24.1558 | 121.9929 | 121.9554 | 121.9145 | -0.049321 | 0.014784 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.067272 | -0.11378 | 0.005611 | 0.11333 | 29.0051 | 24.2107 | 24.2051 | 0.075857 | 0.034901 | -0.05885 | -121.9416 | 0.069716 | -0.005998 | 0.052852 | -121.843 | -121.8123 | 122.0478 | 122.0104 | 121.9694 | 49.3175 | -121.9289 | -0.007072 | 0.091532 | 0.1222 | 0.13771 | -121.9934
3824.7969 | 122.0444 | -0.059509 | 121.8796 | 1.4211e-13 | -0.0088375 | 0.0074147 | 0.073902 | 0.0090615 | 0.084091 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.031981 | 0.013723 | 29.3165 | 49.4732 | 24.3847 | 122.0021 | 121.96 | 121.9145 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.067272 | -0.11378 | 0.014767 | 0.12249 | 29.376 | 24.4442 | 24.4294 | 0.080436 | 0.034901 | -0.054273 | -121.9416 | 0.088029 | -0.001421 | 0.052852 | -121.843 | -121.8123 | 122.0616 | 122.0195 | 121.974 | 49.5327 | -121.9243 | -0.002495 | 0.096109 | 0.12678 | 0.14228 | -121.9934
3826.5 | 122.0306 | -0.068665 | 121.843 | 1.4211e-13 | -0.0088375 | 0.0072009 | 0.073902 | 0.0094887 | 0.083878 | -0.01755 | -0.0040121 | -0.0016987 | 0.018545 | 0.031767 | 0.013937 | 29.4767 | 49.6472 | 24.7372 | 121.9975 | 121.9554 | 121.9191 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.019344 | 0.15453 | 29.5454 | 24.8059 | 24.7865 | 0.11248 | 0.0761 | -0.049696 | -121.9095 | 0.097185 | 0.007735 | 0.057431 | -121.8064 | -121.7711 | 122.0662 | 122.0241 | 121.9877 | 49.7159 | -121.8923 | 0.002083 | 0.10526 | 0.14052 | 0.15144 | -121.9613
3828.2656 | 121.9711 | -0.091553 | 121.8979 | 1.4211e-13 | -0.0081965 | 0.0069873 | 0.073902 | 0.0092751 | 0.084519 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.031981 | 0.013723 | 29.8384 | 49.7937 | 24.8837 | 122.0066 | 121.9554 | 121.9145 | -0.053899 | 0.033099 | 0.082776 | -0.056351 | -0.071161 | 0.032021 | 0.071851 | -0.11836 | 0.037654 | 0.10876 | 29.93 | 24.9753 | 24.9376 | 0.057547 | 0.016591 | -0.026808 | -121.969 | 0.12465 | 0.035202 | 0.06201 | -121.8659 | -121.826 | 122.0982 | 122.047 | 122.006 | 49.8853 | -121.9518 | 0.020392 | 0.12357 | 0.1634 | 0.17433 | -122.0162
3830.0469 | 121.9574 | -0.091553 | 121.9025 | 1.4211e-13 | -0.0079829 | 0.0072009 | 0.073689 | 0.0090615 | 0.084519 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.031981 | 0.013937 | 29.9574 | 49.8212 | 24.957 | 121.9929 | 121.9554 | 121.9191 | -0.058478 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.081008 | -0.11836 | 0.033075 | 0.090444 | 30.049 | 25.0485 | 25.0154 | 0.052969 | 0.016591 | -0.026808 | -121.9645 | 0.12007 | 0.030623 | 0.057431 | -121.8659 | -121.8215 | 122.0845 | 122.047 | 122.0106 | 49.9127 | -121.9609 | 0.029549 | 0.12815 | 0.17256 | 0.17891 | -122.0208
3831.75 | 121.9162 | -0.11902 | 121.8979 | 1.4211e-13 | -0.0077693 | 0.0074147 | 0.073689 | 0.0097023 | 0.084946 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018331 | 0.031767 | 0.013937 | 30.2047 | 50.0226 | 25.4789 | 121.9975 | 121.9463 | 121.9145 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 0.069698 | 0.0996 | 30.3237 | 25.5979 | 25.5282 | 0.048389 | 0.016591 | -0.00392 | -121.9599 | 0.14754 | 0.058089 | 0.062009 | -121.8659 | -121.826 | 122.1165 | 122.0653 | 122.0335 | 50.1417 | -121.9472 | 0.057015 | 0.15104 | 0.19087 | 0.2018 | -122.0208
3833.5156 | 122.0444 | -0.059509 | 121.8521 | 1.4211e-13 | -0.0071281 | 0.0074147 | 0.073902 | 0.01013 | 0.08516 | 0.0053413 | -0.0042257 | -0.0016987 | 0.018545 | 0.032194 | 0.014364 | 30.342 | 50.2333 | 25.8818 | 121.9929 | 121.9509 | 121.9191 | -0.049321 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.027442 | 0.067272 | -0.12294 | 0.010188 | 0.1408 | 30.4015 | 25.9413 | 25.9311 | 0.098744 | 0.066945 | -0.06343 | -121.9095 | 0.088029 | -0.001421 | 0.062009 | -121.8247 | -121.7848 | 122.0524 | 122.0104 | 121.9786 | 50.2928 | -121.9014 | 0.002084 | 0.086951 | 0.12678 | 0.14686 | -121.9751
3835.2188 | 121.9345 | -0.10071 | 121.8979 | 1.4211e-13 | -0.0069145 | 0.0074147 | 0.073475 | 0.0099161 | 0.085373 | 0.0053413 | -0.0042257 | -0.0014849 | 0.018545 | 0.031767 | 0.013937 | 30.5389 | 50.2882 | 25.8085 | 121.9975 | 121.9509 | 121.9099 | -0.040163 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.067272 | -0.11836 | 0.060545 | 0.0996 | 30.6396 | 25.9092 | 25.8487 | 0.052968 | 0.012012 | -0.017653 | -121.9553 | 0.12465 | 0.039778 | 0.057431 | -121.8613 | -121.8306 | 122.0982 | 122.0516 | 122.0106 | 50.3889 | -121.9381 | 0.043283 | 0.13731 | 0.16798 | 0.18806 | -122.0162
3837 | 121.9711 | -0.086975 | 121.907 | 1.4211e-13 | -0.0069145 | 0.0072009 | 0.073689 | 0.01013 | 0.084946 | -0.02518 | -0.0042257 | -0.0016987 | 0.018331 | 0.031767 | 0.01415 | 30.5252 | 50.421 | 25.836 | 121.9838 | 121.9554 | 121.9099 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 0.037654 | 0.07671 | 30.6121 | 25.923 | 25.8853 | 0.048392 | 0.002857 | -0.035964 | -121.969 | 0.11092 | 0.030624 | 0.066588 | -121.875 | -121.8352 | 122.0707 | 122.0424 | 121.9969 | 50.508 | -121.9564 | 0.024971 | 0.119 | 0.15883 | 0.16975 | -122.03
3838.7656 | 122.0535 | -0.059509 | 121.8475 | 1.4211e-13 | -0.0064871 | 0.0072009 | 0.073902 | 0.01013 | 0.085587 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018331 | 0.031767 | 0.013937 | 30.864 | 50.6179 | 26.2022 | 121.9975 | 121.9509 | 121.9145 | -0.040163 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.032021 | 0.067272 | -0.11836 | 0.019346 | 0.14995 | 30.9235 | 26.2618 | 26.2424 | 0.10332 | 0.066945 | -0.058852 | -121.9187 | 0.08345 | -0.001421 | 0.057431 | -121.8155 | -121.7803 | 122.057 | 122.0104 | 121.974 | 50.6774 | -121.8877 | -0.011652 | 0.09153 | 0.12678 | 0.14686 | -121.9659
3840.5312 | 121.9345 | -0.10071 | 121.8979 | 1.4211e-13 | -0.0062735 | 0.0076283 | 0.074116 | 0.0099161 | 0.086014 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.031981 | 0.013723 | 31.1616 | 50.6545 | 26.2022 | 121.9883 | 121.96 | 121.9007 | -0.049321 | 0.033099 | 0.087354 | -0.056351 | -0.066582 | 0.027442 | 0.067272 | -0.11836 | 0.051387 | 0.090444 | 31.2623 | 26.303 | 26.2516 | 0.062126 | 0.002855 | -0.017653 | -121.9645 | 0.13381 | 0.044357 | 0.06201 | -121.8704 | -121.8306 | 122.089 | 122.0607 | 122.0015 | 50.7552 | -121.9472 | 0.034126 | 0.12815 | 0.16798 | 0.18806 | -122.0162
3842.3125 | 121.9025 | -0.091553 | 121.8887 | 1.4211e-13 | -0.0062735 | 0.0072009 | 0.074116 | 0.01013 | 0.086228 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018758 | 0.031981 | 0.013937 | 31.4271 | 50.801 | 26.248 | 121.9838 | 121.9554 | 121.9099 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.027442 | 0.071851 | -0.11836 | 0.042232 | 0.09502 | 31.5187 | 26.3396 | 26.2974 | 0.066702 | 0.021167 | -0.026808 | -121.9507 | 0.11549 | 0.035202 | 0.06201 | -121.8613 | -121.8169 | 122.0753 | 122.047 | 122.0015 | 50.8926 | -121.9381 | 0.029549 | 0.11899 | 0.1634 | 0.17433 | -122.0071
3844.0156 | 121.9254 | -0.10986 | 121.8887 | 1.4211e-13 | -0.0058461 | 0.0067735 | 0.073902 | 0.010557 | 0.086442 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 31.4042 | 50.9063 | 26.4632 | 121.9883 | 121.96 | 121.8962 | -0.049321 | 0.019362 | 0.078197 | -0.056351 | -0.066582 | 0.032021 | 0.07643 | -0.12752 | 0.060542 | 0.099599 | 31.5141 | 26.5731 | 26.5125 | 0.071281 | 0.007431 | -0.017655 | -121.9553 | 0.12923 | 0.053512 | 0.071167 | -121.8567 | -121.8123 | 122.0982 | 122.0699 | 122.006 | 51.0162 | -121.9381 | 0.043281 | 0.14188 | 0.18629 | 0.18806 | -122.0163
3845.7188 | 122.0398 | -0.064087 | 121.8887 | 1.4211e-13 | -0.0054189 | 0.0074147 | 0.073689 | 0.010984 | 0.085801 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018758 | 0.032194 | 0.01415 | 31.4546 | 50.9796 | 26.4128 | 121.9929 | 121.9554 | 121.9053 | -0.053899 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.11836 | 0.010188 | 0.10418 | 31.5187 | 26.4769 | 26.4667 | 0.066702 | 0.016588 | -0.054274 | -121.9507 | 0.083449 | 0.007736 | 0.06201 | -121.8567 | -121.8169 | 122.057 | 122.0195 | 121.9694 | 51.0437 | -121.9426 | 0.002083 | 0.096108 | 0.13594 | 0.14686 | -122.0071
3847.4844 | 121.9666 | -0.11902 | 121.8887 | 1.4211e-13 | -0.0049915 | 0.0074147 | 0.073475 | 0.010771 | 0.086655 | -0.0099192 | -0.0048667 | -0.0019123 | 0.018545 | 0.031767 | 0.013723 | 31.8117 | 51.1719 | 26.9806 | 121.9883 | 121.9554 | 121.9007 | -0.049321 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.027442 | 0.071851 | -0.11378 | 0.069698 | 0.099599 | 31.9307 | 27.0996 | 27.0299 | 0.066702 | 0.01201 | 0.005237 | -121.9599 | 0.13838 | 0.05351 | 0.048273 | -121.8613 | -121.8169 | 122.1074 | 122.0745 | 122.0198 | 51.2909 | -121.9381 | 0.047858 | 0.14646 | 0.19087 | 0.19722 | -122.0025
3849.2656 | 121.9437 | -0.10071 | 121.8796 | 1.4211e-13 | -0.0045641 | 0.0074147 | 0.073902 | 0.010771 | 0.086869 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 31.949 | 51.2405 | 27.0172 | 121.9838 | 121.9463 | 121.9053 | -0.044742 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.022864 | 0.07643 | -0.12294 | 0.055966 | 0.10417 | 32.0497 | 27.1179 | 27.0619 | 0.066699 | 0.025743 | -0.022231 | -121.9462 | 0.12465 | 0.044357 | 0.066588 | -121.8567 | -121.8031 | 122.0845 | 122.047 | 122.006 | 51.3413 | -121.9243 | 0.034126 | 0.12357 | 0.17714 | 0.18806 | -122.0025
3850.9844 | 121.907 | -0.10986 | 121.907 | 1.4211e-13 | -0.0041367 | 0.0074147 | 0.073902 | 0.010984 | 0.087296 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018972 | 0.031553 | 0.01415 | 32.3611 | 51.3459 | 27.1912 | 121.9838 | 121.9509 | 121.9053 | -0.053899 | 0.033099 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.12294 | 0.055964 | 0.07671 | 32.471 | 27.301 | 27.2451 | 0.043813 | -0.001722 | -0.013076 | -121.9736 | 0.14296 | 0.048933 | 0.062009 | -121.875 | -121.8306 | 122.0936 | 122.0607 | 122.0152 | 51.4557 | -121.9609 | 0.043281 | 0.14188 | 0.18629 | 0.19722 | -122.03
3852.7656 | 121.9208 | -0.11902 | 121.8933 | 1.4211e-13 | -0.0039231 | 0.0076283 | 0.07433 | 0.010984 | 0.086869 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.032194 | 0.013723 | 32.2695 | 51.5336 | 27.6307 | 121.9838 | 121.9509 | 121.9099 | -0.049321 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 0.069698 | 0.090442 | 32.3885 | 27.7497 | 27.68 | 0.057545 | 0.016589 | 0.000658 | -121.9599 | 0.14754 | 0.058089 | 0.057431 | -121.8613 | -121.8215 | 122.1028 | 122.0699 | 122.0289 | 51.6526 | -121.9426 | 0.052437 | 0.15104 | 0.19087 | 0.20637 | -122.0117
3854.5312 | 122.0535 | -0.045776 | 121.8613 | 1.4211e-13 | -0.0037095 | 0.0078419 | 0.074116 | 0.011412 | 0.08751 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.01415 | 32.4435 | 51.5656 | 27.6765 | 121.9792 | 121.9371 | 121.9007 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | -0.008123 | 0.11791 | 32.4893 | 27.7222 | 27.7304 | 0.075853 | 0.039476 | -0.072585 | -121.9278 | 0.069717 | -0.010575 | 0.06201 | -121.8292 | -121.7894 | 122.025 | 121.9829 | 121.9465 | 51.6114 | -121.9152 | -0.020806 | 0.077797 | 0.11763 | 0.12855 | -121.9796
3856.2344 | 121.9391 | -0.10986 | 121.8933 | 1.4211e-13 | -0.0037095 | 0.0074147 | 0.073902 | 0.011412 | 0.087083 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018545 | 0.031981 | 0.013723 | 32.4343 | 51.5977 | 27.8596 | 121.9838 | 121.9463 | 121.9007 | -0.049321 | 0.019362 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 0.060542 | 0.090442 | 32.5442 | 27.9694 | 27.9089 | 0.052966 | 0.007432 | -0.013076 | -121.9507 | 0.12923 | 0.048933 | 0.062009 | -121.8567 | -121.8169 | 122.0936 | 122.0561 | 122.0106 | 51.7075 | -121.9426 | 0.052438 | 0.14646 | 0.18629 | 0.19722 | -122.0162
3858.0156 | 121.9528 | -0.10529 | 121.8933 | 1.4211e-13 | -0.0028547 | 0.0076283 | 0.07433 | 0.011839 | 0.087296 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031981 | 0.01415 | 32.5122 | 51.79 | 28.203 | 121.9838 | 121.9509 | 121.9099 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.032021 | 0.071851 | -0.12294 | 0.055965 | 0.090442 | 32.6175 | 28.3082 | 28.2523 | 0.057545 | 0.016589 | -0.017653 | -121.9507 | 0.12923 | 0.048935 | 0.066588 | -121.8613 | -121.8215 | 122.089 | 122.0561 | 122.0152 | 51.8953 | -121.9426 | 0.047861 | 0.13731 | 0.17714 | 0.18806 | -122.0162
3859.7969 | 121.9116 | -0.09613 | 121.9116 | 1.4211e-13 | -0.0028547 | 0.0074147 | 0.074116 | 0.011625 | 0.087937 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018758 | 0.031767 | 0.013937 | 32.9288 | 51.909 | 28.3449 | 121.9883 | 121.9371 | 121.9007 | -0.049321 | 0.023941 | 0.087354 | -0.051772 | -0.066582 | 0.022864 | 0.071851 | -0.11836 | 0.046809 | 0.076711 | 33.0249 | 28.441 | 28.3942 | 0.025499 | -0.010878 | -0.022231 | -121.9782 | 0.12007 | 0.044358 | 0.066589 | -121.8888 | -121.8398 | 122.0845 | 122.0332 | 121.9969 | 52.0052 | -121.9609 | 0.029548 | 0.11899 | 0.16798 | 0.18348 | -122.03
3861.5 | 122.0078 | -0.073242 | 121.8384 | 1.4211e-13 | -0.0026411 | 0.0074147 | 0.074116 | 0.011839 | 0.087937 | -0.02518 | -0.0040121 | -0.0021259 | 0.018545 | 0.032194 | 0.013937 | 32.9654 | 51.909 | 28.3678 | 121.9838 | 121.9371 | 121.9053 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.032021 | 0.07643 | -0.11378 | 0.023921 | 0.14537 | 33.0387 | 28.441 | 28.4171 | 0.098741 | 0.066942 | -0.04054 | -121.905 | 0.097183 | 0.016891 | 0.057431 | -121.8064 | -121.7619 | 122.057 | 122.0104 | 121.9786 | 51.9823 | -121.8877 | 0.00666 | 0.10526 | 0.14967 | 0.15602 | -121.9522
3863.2656 | 121.9849 | -0.082397 | 121.8842 | 1.4211e-13 | -0.0026411 | 0.0074147 | 0.074116 | 0.011412 | 0.088151 | -0.01755 | -0.0044395 | -0.0016987 | 0.018545 | 0.031981 | 0.013937 | 33.0021 | 51.9457 | 28.3815 | 121.9838 | 121.9463 | 121.8962 | -0.053899 | 0.014784 | 0.073618 | -0.06093 | -0.071161 | 0.027442 | 0.07643 | -0.12752 | 0.028498 | 0.099598 | 33.0845 | 28.4639 | 28.4354 | 0.062122 | 0.012009 | -0.045121 | -121.9553 | 0.097181 | 0.021467 | 0.066588 | -121.8567 | -121.8077 | 122.0661 | 122.0287 | 121.9786 | 52.028 | -121.9381 | 0.011236 | 0.10984 | 0.15883 | 0.15602 | -122.0117
3865.0469 | 121.9025 | -0.09613 | 121.8979 | 1.4211e-13 | -0.0020001 | 0.0074147 | 0.074116 | 0.012053 | 0.087937 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018331 | 0.031767 | 0.013723 | 33.2218 | 52.0464 | 28.528 | 121.9838 | 121.9417 | 121.9053 | -0.044742 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.067272 | -0.12294 | 0.051388 | 0.085865 | 33.318 | 28.6241 | 28.5728 | 0.04381 | 0.007433 | -0.026809 | -121.9599 | 0.12465 | 0.0352 | 0.062009 | -121.8659 | -121.8306 | 122.0799 | 122.0378 | 122.0015 | 52.1425 | -121.9426 | 0.034126 | 0.12815 | 0.1634 | 0.17891 | -122.0208
3866.8125 | 122.0444 | -0.050354 | 121.843 | 1.4211e-13 | -0.0020001 | 0.0076283 | 0.074116 | 0.012053 | 0.088792 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.032194 | 0.013723 | 33.8079 | 52.0372 | 28.4685 | 121.9792 | 121.9371 | 121.9007 | -0.049321 | 0.023941 | 0.082776 | -0.070087 | -0.062004 | 0.032021 | 0.081008 | -0.11378 | 0.001033 | 0.13622 | 33.8582 | 28.5188 | 28.5178 | 0.094163 | 0.057786 | -0.063428 | -121.905 | 0.074295 | -0.019733 | 0.043695 | -121.8109 | -121.7619 | 122.0295 | 121.9875 | 121.9511 | 52.0876 | -121.8923 | -0.01165 | 0.082375 | 0.13136 | 0.13313 | -121.9567
3868.5938 | 121.9803 | -0.09613 | 121.843 | 1.4211e-13 | -0.0022137 | 0.0076283 | 0.074116 | 0.012053 | 0.088365 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.032408 | 0.013937 | 33.8353 | 52.0143 | 28.3998 | 121.9746 | 121.9371 | 121.8916 | -0.049321 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.12294 | 0.046809 | 0.13164 | 33.9315 | 28.496 | 28.4491 | 0.094163 | 0.048629 | -0.026809 | -121.9095 | 0.12007 | 0.0352 | 0.062009 | -121.8064 | -121.7665 | 122.0707 | 122.0332 | 121.9877 | 52.1105 | -121.8923 | 0.029548 | 0.13273 | 0.17256 | 0.18806 | -121.9659
3870.3594 | 122.0261 | -0.045776 | 121.8246 | 1.4211e-13 | -0.0015727 | 0.0076283 | 0.074116 | 0.012053 | 0.088792 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018545 | 0.032408 | 0.013937 | 33.9544 | 52.138 | 28.7707 | 121.9838 | 121.9417 | 121.9053 | -0.049321 | 0.02852 | 0.078197 | -0.056351 | -0.062004 | 0.032021 | 0.07643 | -0.12294 | -0.003545 | 0.15911 | 34.0001 | 28.8164 | 28.82 | 0.11705 | 0.080675 | -0.077163 | -121.8867 | 0.074296 | -0.010575 | 0.066588 | -121.7926 | -121.7482 | 122.0295 | 121.9875 | 121.9511 | 52.1837 | -121.874 | -0.016228 | 0.077797 | 0.12221 | 0.12397 | -121.9476
3872.125 | 121.8887 | -0.11444 | 121.907 | 1.4211e-13 | -0.0011453 | 0.0072009 | 0.07433 | 0.01248 | 0.089006 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.031767 | 0.013723 | 34.5541 | 52.2616 | 29.0545 | 121.9838 | 121.9371 | 121.8962 | -0.049321 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.032021 | 0.07643 | -0.11378 | 0.06512 | 0.07671 | 34.6686 | 29.169 | 29.1038 | 0.030077 | -0.010879 | 0.000659 | -121.9782 | 0.13838 | 0.05809 | 0.057431 | -121.875 | -121.8306 | 122.0982 | 122.0516 | 122.0106 | 52.376 | -121.9564 | 0.04328 | 0.14646 | 0.19087 | 0.19722 | -122.0208
3873.9062 | 121.9208 | -0.10071 | 121.8796 | 1.4211e-13 | -0.00071787 | 0.0076283 | 0.074116 | 0.012694 | 0.089647 | -0.01755 | -0.0042257 | -0.0019123 | 0.018117 | 0.031981 | 0.01415 | 34.6869 | 52.3165 | 29.1461 | 121.9792 | 121.9325 | 121.8962 | -0.049321 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.027442 | 0.067272 | -0.12752 | 0.051387 | 0.099597 | 34.7876 | 29.2468 | 29.1954 | 0.052963 | 0.016586 | -0.02681 | -121.9462 | 0.12465 | 0.044357 | 0.071167 | -121.8521 | -121.8123 | 122.0799 | 122.0332 | 121.9969 | 52.4172 | -121.9289 | 0.034126 | 0.12815 | 0.16798 | 0.18806 | -122.0071
3875.6094 | 121.9299 | -0.09613 | 121.875 | 1.4211e-13 | -0.00071787 | 0.0076283 | 0.074757 | 0.012266 | 0.089433 | -0.01755 | -0.0044395 | -0.0016987 | 0.018545 | 0.031981 | 0.014364 | 34.8655 | 52.3074 | 29.1598 | 121.9792 | 121.9371 | 121.8962 | -0.049321 | 0.014784 | 0.091933 | -0.056351 | -0.071161 | 0.0366 | 0.067272 | -0.11836 | 0.046809 | 0.10417 | 34.9616 | 29.2559 | 29.2091 | 0.06212 | 0.021164 | -0.022231 | -121.9462 | 0.11091 | 0.039779 | 0.06201 | -121.8384 | -121.8077 | 122.0753 | 122.0332 | 121.9923 | 52.4035 | -121.9243 | 0.024969 | 0.13273 | 0.1634 | 0.18806 | -121.9934
3877.3594 | 121.8842 | -0.10986 | 121.9025 | 1.4211e-13 | -0.00029067 | 0.0076283 | 0.07433 | 0.01248 | 0.090074 | -0.01755 | -0.0042257 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 35.012 | 52.344 | 29.3017 | 121.9746 | 121.9325 | 121.8916 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.060542 | 0.07213 | 35.1218 | 29.4116 | 29.3511 | 0.030075 | -0.01088 | -0.008498 | -121.969 | 0.1338 | 0.048933 | 0.057431 | -121.8659 | -121.8306 | 122.0845 | 122.0424 | 122.0014 | 52.4539 | -121.9518 | 0.043281 | 0.14646 | 0.18171 | 0.18806 | -122.0208
3879.1406 | 121.8979 | -0.10986 | 121.8842 | 1.4211e-13 | 0.00035033 | 0.0078419 | 0.074543 | 0.012907 | 0.090288 | -0.01755 | -0.0044395 | -0.0019123 | 0.018545 | 0.031981 | 0.013937 | 35.1402 | 52.5042 | 29.7184 | 121.9746 | 121.9371 | 121.887 | -0.049321 | 0.023941 | 0.082776 | -0.051772 | -0.071161 | 0.0366 | 0.07643 | -0.11836 | 0.060542 | 0.090441 | 35.25 | 29.8282 | 29.7677 | 0.052965 | 0.002852 | -0.008498 | -121.9553 | 0.1338 | 0.058091 | 0.066589 | -121.8476 | -121.8077 | 122.0845 | 122.047 | 121.9969 | 52.6141 | -121.9335 | 0.038702 | 0.14646 | 0.18629 | 0.19264 | -122.0025
3880.8438 | 121.962 | -0.09613 | 121.8842 | 1.4211e-13 | 0.00099133 | 0.0076283 | 0.074543 | 0.013335 | 0.090501 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018545 | 0.031767 | 0.013937 | 35.4011 | 52.5867 | 30.1396 | 121.9746 | 121.928 | 121.9007 | -0.044742 | 0.033099 | 0.091933 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.11836 | 0.051388 | 0.090441 | 35.4973 | 30.2357 | 30.1843 | 0.043807 | 0.016588 | -0.022231 | -121.9462 | 0.12923 | 0.039779 | 0.06201 | -121.8521 | -121.8123 | 122.0707 | 122.0241 | 121.9969 | 52.6828 | -121.9289 | 0.034126 | 0.12815 | 0.16798 | 0.18806 | -122.0025
3882.625 | 121.9391 | -0.091553 | 121.9162 | 1.4211e-13 | 0.00035033 | 0.0076283 | 0.074543 | 0.013335 | 0.090501 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018545 | 0.031767 | 0.01415 | 35.4103 | 52.6553 | 30.3135 | 121.9746 | 121.9325 | 121.887 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.11836 | 0.037654 | 0.058397 | 35.5019 | 30.4051 | 30.3674 | 0.016342 | -0.029192 | -0.026808 | -121.9782 | 0.11549 | 0.035202 | 0.06201 | -121.8842 | -121.8443 | 122.0661 | 122.0241 | 121.9786 | 52.7469 | -121.9701 | 0.029549 | 0.12357 | 0.1634 | 0.17433 | -122.0346
3884.3906 | 121.9849 | -0.07782 | 121.8292 | 1.4211e-13 | 0.0012051 | 0.0076283 | 0.074757 | 0.013121 | 0.091142 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018758 | 0.032194 | 0.01415 | 35.8819 | 52.6599 | 30.341 | 121.9746 | 121.9325 | 121.8962 | -0.044742 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.071851 | -0.11836 | 0.033078 | 0.14537 | 35.9597 | 30.4188 | 30.3858 | 0.10332 | 0.06694 | -0.040541 | -121.9004 | 0.10176 | 0.01689 | 0.057431 | -121.788 | -121.7574 | 122.0524 | 122.0104 | 121.974 | 52.7377 | -121.874 | 0.006659 | 0.119 | 0.14967 | 0.16517 | -121.9476
3886.1562 | 121.9482 | -0.082397 | 121.8475 | 1.4211e-13 | 0.00099133 | 0.0080557 | 0.074757 | 0.013548 | 0.091356 | -0.01755 | -0.0042257 | -0.0012713 | 0.018545 | 0.032408 | 0.013937 | 36.3718 | 52.6691 | 30.3456 | 121.97 | 121.9325 | 121.887 | -0.044742 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.12294 | 0.037655 | 0.12248 | 36.4542 | 30.428 | 30.3903 | 0.085007 | 0.039473 | -0.040542 | -121.9141 | 0.11092 | 0.021467 | 0.062009 | -121.8155 | -121.7757 | 122.0524 | 122.0149 | 121.9694 | 52.7515 | -121.8923 | 0.015815 | 0.11442 | 0.15425 | 0.16975 | -121.9705
3887.9375 | 121.9437 | -0.09613 | 121.8796 | 1.4211e-13 | 0.0018461 | 0.0078419 | 0.074116 | 0.013762 | 0.091142 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 36.5869 | 52.8156 | 30.9499 | 121.97 | 121.9325 | 121.887 | -0.049321 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.11836 | 0.046809 | 0.09044 | 36.6831 | 31.0461 | 30.9992 | 0.052963 | 0.007429 | -0.022231 | -121.9462 | 0.12007 | 0.0352 | 0.057431 | -121.8521 | -121.8077 | 122.0661 | 122.0287 | 121.9831 | 52.9117 | -121.9289 | 0.029548 | 0.12357 | 0.16798 | 0.17891 | -121.9979
3889.6562 | 121.8796 | -0.086975 | 121.9025 | 1.4211e-13 | 0.0020597 | 0.0078419 | 0.07433 | 0.013976 | 0.09157 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018545 | 0.031767 | 0.013723 | 36.5412 | 52.8247 | 31.0919 | 121.97 | 121.928 | 121.8824 | -0.049321 | 0.02852 | 0.091933 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.11378 | 0.037654 | 0.067552 | 36.6281 | 31.1788 | 31.1412 | 0.025496 | -0.020038 | -0.026807 | -121.969 | 0.1155 | 0.026045 | 0.052852 | -121.8659 | -121.826 | 122.057 | 122.0149 | 121.9694 | 52.9117 | -121.9518 | 0.020393 | 0.12357 | 0.1634 | 0.17891 | -122.0162
3891.4219 | 122.0078 | -0.059509 | 121.8246 | 1.4211e-13 | 0.0024871 | 0.0080557 | 0.074757 | 0.013762 | 0.092211 | -0.02518 | -0.0044395 | -0.0016987 | 0.018117 | 0.031981 | 0.013937 | 36.7151 | 52.8888 | 31.5314 | 121.9746 | 121.9325 | 121.8824 | -0.044742 | 0.023941 | 0.082776 | -0.051772 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.014767 | 0.14995 | 36.7746 | 31.5909 | 31.5761 | 0.10789 | 0.057782 | -0.058852 | -121.8912 | 0.08345 | 0.007737 | 0.066589 | -121.788 | -121.7528 | 122.0341 | 121.9921 | 121.9419 | 52.9484 | -121.8694 | -0.007073 | 0.096109 | 0.13136 | 0.14228 | -121.943
3893.125 | 121.9986 | -0.054932 | 121.8796 | 1.4211e-13 | 0.0035555 | 0.0080557 | 0.07433 | 0.015044 | 0.092638 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.032194 | 0.013937 | 37.1226 | 53.1086 | 32.4653 | 121.97 | 121.928 | 121.8824 | -0.049321 | 0.02852 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 0.005611 | 0.09044 | 37.1775 | 32.5203 | 32.5147 | 0.048384 | 0.00285 | -0.063429 | -121.9416 | 0.083452 | -0.001419 | 0.06201 | -121.843 | -121.8077 | 122.0249 | 121.9829 | 121.9374 | 53.1635 | -121.9289 | -0.007072 | 0.091532 | 0.12678 | 0.14229 | -121.9979
3894.8906 | 121.9025 | -0.10986 | 121.8658 | 1.4211e-13 | 0.0039829 | 0.0080557 | 0.07433 | 0.01483 | 0.092424 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018545 | 0.032194 | 0.013937 | 37.1501 | 53.0857 | 32.3509 | 121.9654 | 121.9325 | 121.887 | -0.044742 | 0.02852 | 0.091933 | -0.065509 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 0.065121 | 0.099595 | 37.2599 | 32.4607 | 32.3956 | 0.066696 | 0.021162 | -0.008498 | -121.9278 | 0.13838 | 0.044354 | 0.052852 | -121.8292 | -121.794 | 122.0753 | 122.0424 | 121.9969 | 53.1956 | -121.9106 | 0.047859 | 0.14646 | 0.18171 | 0.2018 | -121.9842
3896.6562 | 121.8887 | -0.1236 | 121.8979 | 1.4211e-13 | 0.0039829 | 0.0078419 | 0.07433 | 0.014617 | 0.092852 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018331 | 0.031981 | 0.013723 | 37.0677 | 53.0354 | 32.3921 | 121.9654 | 121.9234 | 121.887 | -0.049321 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.12294 | 0.074275 | 0.067552 | 37.1913 | 32.5157 | 32.4414 | 0.025495 | -0.010881 | 0.000657 | -121.9645 | 0.14754 | 0.062666 | 0.062009 | -121.8704 | -121.826 | 122.089 | 122.047 | 122.0106 | 53.159 | -121.9472 | 0.057014 | 0.15104 | 0.19545 | 0.20179 | -122.0208
3898.4531 | 121.9528 | -0.10986 | 121.8842 | 1.4211e-13 | 0.0050511 | 0.0080557 | 0.074971 | 0.015471 | 0.093065 | -0.0022892 | -0.0040121 | -0.0016987 | 0.018545 | 0.032194 | 0.013937 | 36.967 | 53.333 | 33.2986 | 121.9563 | 121.9234 | 121.8778 | -0.044742 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.067272 | -0.11378 | 0.065121 | 0.072128 | 37.0768 | 33.4084 | 33.3433 | 0.039228 | -0.006305 | -0.003919 | -121.9553 | 0.12923 | 0.048933 | 0.052852 | -121.8476 | -121.8169 | 122.0661 | 122.0332 | 121.9877 | 53.4428 | -121.9289 | 0.038702 | 0.14646 | 0.17713 | 0.19264 | -121.9979
3900.1562 | 121.9986 | -0.068665 | 121.8384 | 1.4211e-13 | 0.0056923 | 0.0078419 | 0.07433 | 0.016112 | 0.092852 | 0.0053413 | -0.0042257 | -0.0019123 | 0.018331 | 0.031767 | 0.013937 | 37.0265 | 53.4383 | 33.793 | 121.9654 | 121.9234 | 121.8733 | -0.044742 | 0.014784 | 0.087354 | -0.065509 | -0.062004 | 0.032021 | 0.067272 | -0.12294 | 0.023923 | 0.12706 | 37.0951 | 33.8617 | 33.8378 | 0.085004 | 0.034892 | -0.054274 | -121.9004 | 0.083449 | 0.003156 | 0.05743 | -121.8064 | -121.7711 | 122.0341 | 121.992 | 121.9419 | 53.5069 | -121.8831 | 0.006661 | 0.10069 | 0.13594 | 0.15602 | -121.9613
3901.9219 | 121.8933 | -0.10529 | 121.8704 | 1.4211e-13 | 0.0054785 | 0.0078419 | 0.074543 | 0.015471 | 0.093279 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018545 | 0.032194 | 0.013723 | 37.4797 | 53.3192 | 33.2894 | 121.97 | 121.928 | 121.8733 | -0.044742 | 0.02852 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 0.060544 | 0.099596 | 37.585 | 33.3947 | 33.3342 | 0.05754 | 0.002849 | -0.017653 | -121.9324 | 0.13381 | 0.048935 | 0.066588 | -121.8338 | -121.794 | 122.0753 | 122.0332 | 121.9786 | 53.4245 | -121.9152 | 0.043282 | 0.14189 | 0.18172 | 0.19264 | -121.9934
3903.6406 | 121.8887 | -0.10986 | 121.8521 | 1.4211e-13 | 0.0071879 | 0.0076283 | 0.074543 | 0.01654 | 0.09392 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018331 | 0.032194 | 0.013937 | 38.052 | 53.5894 | 34.0769 | 121.9563 | 121.928 | 121.8778 | -0.053899 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.12294 | 0.055964 | 0.10417 | 38.1619 | 34.1868 | 34.1308 | 0.07585 | 0.025738 | -0.013076 | -121.9187 | 0.1338 | 0.048933 | 0.062009 | -121.8155 | -121.7757 | 122.0661 | 122.0378 | 121.9877 | 53.6992 | -121.906 | 0.043281 | 0.14646 | 0.18629 | 0.19722 | -121.9751
3905.4062 | 121.8979 | -0.10986 | 121.875 | 1.4211e-13 | 0.0074015 | 0.0080557 | 0.074971 | 0.016112 | 0.094134 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018331 | 0.032194 | 0.013937 | 38.0887 | 53.7496 | 34.5256 | 121.9563 | 121.9234 | 121.8778 | -0.049321 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.041178 | 0.067272 | -0.12294 | 0.060542 | 0.081283 | 38.1985 | 34.6354 | 34.5749 | 0.048383 | 0.00285 | -0.013076 | -121.9324 | 0.13838 | 0.048933 | 0.062009 | -121.8338 | -121.8077 | 122.0661 | 122.0332 | 121.9877 | 53.8595 | -121.9243 | 0.052438 | 0.15104 | 0.17713 | 0.19264 | -121.9979
3907.1875 | 121.8933 | -0.10071 | 121.8796 | 1.4211e-13 | 0.0091109 | 0.0080557 | 0.074757 | 0.018035 | 0.094561 | -0.01755 | -0.0040121 | -0.0014849 | 0.018545 | 0.032194 | 0.013937 | 38.2947 | 54.2441 | 36.2928 | 121.9609 | 121.9234 | 121.8733 | -0.044742 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.11836 | 0.055966 | 0.081283 | 38.3954 | 36.3935 | 36.3375 | 0.043805 | -0.006307 | -0.017653 | -121.9462 | 0.12465 | 0.044357 | 0.06201 | -121.843 | -121.8031 | 122.0616 | 122.0241 | 121.974 | 54.3448 | -121.9243 | 0.034126 | 0.13731 | 0.17714 | 0.18348 | -121.9979
3908.9062 | 122.0078 | -0.045776 | 121.8292 | 1.4211e-13 | 0.078555 | 0.0074147 | 0.069201 | 0.077861 | 0.09627 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018758 | 0.031981 | 0.014364 | 38.8166 | 75.9192 | 114.2288 | 121.938 | 121.9096 | 121.8595 | -0.040163 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.12294 | 0.005613 | 0.10874 | 38.8624 | 114.2746 | 114.269 | 0.080422 | 0.030311 | -0.077163 | -121.8958 | 0.069717 | -0.015154 | 0.062009 | -121.7972 | -121.7528 | 121.9837 | 121.9554 | 121.9053 | 75.965 | -121.8694 | -0.020806 | 0.077797 | 0.12221 | 0.13313 | -121.9522
3910.6875 | 122.0215 | -0.045776 | 121.8201 | 1.4211e-13 | 0.079837 | 0.0072009 | 0.068988 | 0.078502 | 0.09627 | -0.0022892 | -0.0042257 | -0.0021259 | 0.018331 | 0.032408 | 0.013937 | 38.8716 | 76.1253 | 115.1125 | 121.9471 | 121.9051 | 121.8641 | -0.035584 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.032021 | 0.067272 | -0.11836 | 0.010192 | 0.12706 | 38.9173 | 115.1582 | 115.148 | 0.084999 | 0.044046 | -0.072585 | -121.8821 | 0.069717 | -0.019733 | 0.052852 | -121.788 | -121.7528 | 121.9929 | 121.9508 | 121.9099 | 76.171 | -121.8557 | -0.016228 | 0.077797 | 0.11305 | 0.12397 | -121.9384
3912.3906 | 121.9986 | -0.068665 | 121.7972 | 1.4211e-13 | 0.077914 | 0.0072009 | 0.06856 | 0.075297 | 0.096697 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.031981 | 0.013937 | 38.78 | 75.0996 | 111.5093 | 121.9425 | 121.8868 | 121.855 | -0.053899 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 0.014766 | 0.14537 | 38.8487 | 111.578 | 111.5632 | 0.089571 | 0.057777 | -0.054274 | -121.8592 | 0.097185 | 0.007735 | 0.062009 | -121.7606 | -121.7253 | 122.0112 | 121.9554 | 121.9236 | 75.1683 | -121.8511 | 0.006661 | 0.10526 | 0.14052 | 0.14686 | -121.9201
3914.1562 | 121.9849 | -0.041199 | 121.7834 | 1.4211e-13 | 0.079623 | 0.0072009 | 0.068774 | 0.076365 | 0.097125 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.031981 | 0.013937 | 39.6499 | 75.4568 | 113.0705 | 121.9334 | 121.8959 | 121.855 | -0.058478 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.067272 | -0.12294 | -0.017279 | 0.14994 | 39.6911 | 113.1117 | 113.129 | 0.11246 | 0.07151 | -0.08174 | -121.85 | 0.06514 | -0.019731 | 0.062009 | -121.7468 | -121.7162 | 121.9746 | 121.9371 | 121.8962 | 75.498 | -121.8419 | -0.025383 | 0.077799 | 0.10847 | 0.12855 | -121.9064
3915.9219 | 121.8842 | -0.091553 | 121.8475 | 1.4211e-13 | 0.080264 | 0.0076283 | 0.068774 | 0.076793 | 0.097338 | -0.0099192 | -0.0040121 | -0.0019123 | 0.018545 | 0.032194 | 0.013937 | 39.3248 | 75.5483 | 113.446 | 121.9334 | 121.8913 | 121.8504 | -0.058478 | 0.023941 | 0.087354 | -0.06093 | -0.052847 | 0.027442 | 0.07643 | -0.12752 | 0.033075 | 0.085857 | 39.4164 | 113.5375 | 113.5044 | 0.043796 | 0.002844 | -0.035965 | -121.9004 | 0.11549 | 0.030623 | 0.066588 | -121.8201 | -121.7711 | 122.0249 | 121.9829 | 121.9419 | 75.6399 | -121.906 | 0.038706 | 0.11899 | 0.16798 | 0.17891 | -121.9751
3917.6406 | 122.0261 | -0.082397 | 121.8201 | 1.4211e-13 | 0.080478 | 0.0074147 | 0.068774 | 0.076793 | 0.097766 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018545 | 0.032194 | 0.013723 | 39.7186 | 75.5438 | 113.6795 | 121.9334 | 121.8822 | 121.8458 | -0.063057 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.12752 | 0.01934 | 0.11332 | 39.801 | 113.7618 | 113.7425 | 0.062104 | 0.025732 | -0.045121 | -121.8867 | 0.10634 | 0.016888 | 0.062009 | -121.7789 | -121.7436 | 122.0158 | 121.9646 | 121.9282 | 75.6262 | -121.8831 | 0.015815 | 0.12357 | 0.15883 | 0.16975 | -121.9476
3919.4062 | 121.8567 | -0.09613 | 121.843 | 1.4211e-13 | 0.080905 | 0.0076283 | 0.06856 | 0.076579 | 0.098407 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018545 | 0.032408 | 0.01415 | 40.2451 | 75.5804 | 113.8809 | 121.9334 | 121.8913 | 121.8458 | -0.049321 | 0.02852 | 0.091933 | -0.065509 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 0.046809 | 0.090434 | 40.3412 | 113.977 | 113.9302 | 0.048373 | 0.002843 | -0.031388 | -121.9095 | 0.12465 | 0.030621 | 0.062009 | -121.8064 | -121.7711 | 122.0295 | 121.9875 | 121.9419 | 75.6765 | -121.8923 | 0.029548 | 0.13273 | 0.16798 | 0.18806 | -121.9705
3921.1562 | 121.9574 | -0.068665 | 121.8613 | 1.4211e-13 | 0.081119 | 0.0074147 | 0.068774 | 0.076793 | 0.099048 | 0.0053413 | -0.0042257 | -0.0019123 | 0.018545 | 0.032194 | 0.01415 | 40.5244 | 75.5758 | 114.0228 | 121.938 | 121.8959 | 121.8412 | -0.067636 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 0.001029 | 0.076702 | 40.593 | 114.0915 | 114.0905 | 0.034642 | -0.020046 | -0.054274 | -121.9278 | 0.088027 | 0.007735 | 0.062009 | -121.8247 | -121.7894 | 122.0066 | 121.9646 | 121.9099 | 75.6445 | -121.9289 | 0.002083 | 0.10526 | 0.14052 | 0.15144 | -121.9842
3922.8594 | 121.8842 | -0.07782 | 121.843 | 1.4211e-13 | 0.081546 | 0.0074147 | 0.068346 | 0.077006 | 0.099048 | -0.0022892 | -0.0044395 | -0.0021259 | 0.018545 | 0.031981 | 0.01415 | 40.8082 | 75.6262 | 114.151 | 121.9288 | 121.8868 | 121.8458 | -0.063057 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 0.014763 | 0.085856 | 40.886 | 114.2288 | 114.2141 | 0.043794 | 0.002843 | -0.040541 | -121.9095 | 0.10634 | 0.01689 | 0.057431 | -121.8109 | -121.7711 | 122.0066 | 121.9646 | 121.9236 | 75.704 | -121.906 | 0.011238 | 0.10984 | 0.14967 | 0.16517 | -121.9613
3924.6406 | 121.962 | -0.082397 | 121.7972 | 1.4211e-13 | 0.082401 | 0.0076283 | 0.068774 | 0.076793 | 0.099902 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018117 | 0.032194 | 0.01415 | 41.4309 | 75.6033 | 114.238 | 121.9242 | 121.8868 | 121.8412 | -0.063057 | 0.023941 | 0.096512 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.01934 | 0.12705 | 41.5133 | 114.3204 | 114.3011 | 0.089571 | 0.044041 | -0.035964 | -121.8638 | 0.10634 | 0.021467 | 0.057431 | -121.7606 | -121.7253 | 122.0066 | 121.9691 | 121.9236 | 75.6857 | -121.8602 | 0.015815 | 0.119 | 0.15425 | 0.17891 | -121.9155
3926.3438 | 121.8338 | -0.10071 | 121.843 | 1.4211e-13 | 0.082828 | 0.0074147 | 0.068774 | 0.076793 | 0.10054 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018545 | 0.032194 | 0.014364 | 41.3897 | 75.6079 | 114.3204 | 121.9151 | 121.8776 | 121.8412 | -0.063057 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.07643 | -0.12752 | 0.037651 | 0.07212 | 41.4904 | 114.4211 | 114.3835 | 0.034637 | -0.001736 | -0.02681 | -121.905 | 0.12465 | 0.039778 | 0.066588 | -121.8064 | -121.7665 | 122.0158 | 121.9783 | 121.9419 | 75.7086 | -121.906 | 0.038704 | 0.13731 | 0.17714 | 0.18806 | -121.9705
3928.1094 | 122.0123 | -0.068665 | 121.7926 | 1.4211e-13 | 0.082615 | 0.0078419 | 0.068774 | 0.076793 | 0.10033 | -0.0099192 | -0.0040121 | -0.0021259 | 0.018545 | 0.031767 | 0.01415 | 41.1104 | 75.585 | 114.4394 | 121.9105 | 121.8776 | 121.8366 | -0.063057 | 0.02852 | 0.078197 | -0.056351 | -0.062004 | 0.0366 | 0.081008 | -0.11836 | 0.005608 | 0.1179 | 41.1791 | 114.5081 | 114.5025 | 0.084991 | 0.044039 | -0.049696 | -121.8546 | 0.097185 | 0.012314 | 0.06201 | -121.756 | -121.7116 | 121.9792 | 121.9463 | 121.9053 | 75.6536 | -121.8557 | 0.006661 | 0.10526 | 0.14967 | 0.14686 | -121.911
3929.875 | 121.9757 | -0.064087 | 121.8292 | 1.4211e-13 | 0.083042 | 0.0080557 | 0.068774 | 0.077006 | 0.10054 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018331 | 0.032408 | 0.013723 | 41.3668 | 75.5896 | 114.5173 | 121.9059 | 121.873 | 121.8275 | -0.063057 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.11378 | 0.00103 | 0.076697 | 41.4309 | 114.5814 | 114.5803 | 0.043791 | -0.001739 | -0.049695 | -121.8958 | 0.092607 | 0.003157 | 0.052852 | -121.7926 | -121.7528 | 121.97 | 121.9371 | 121.8916 | 75.6536 | -121.8923 | -0.002495 | 0.10069 | 0.14052 | 0.14686 | -121.943
3931.5781 | 121.9803 | -0.059509 | 121.7834 | 1.4211e-13 | 0.082828 | 0.0072009 | 0.068988 | 0.077006 | 0.10097 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018331 | 0.031981 | 0.014364 | 41.7376 | 75.6079 | 114.5905 | 121.9105 | 121.873 | 121.8321 | -0.063057 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.07643 | -0.12294 | -0.003548 | 0.12705 | 41.7971 | 114.65 | 114.6536 | 0.089568 | 0.048617 | -0.06343 | -121.8455 | 0.088029 | -0.001421 | 0.062009 | -121.7514 | -121.707 | 121.97 | 121.9325 | 121.8916 | 75.6674 | -121.8465 | -0.002495 | 0.09153 | 0.13594 | 0.14228 | -121.9064
3933.3438 | 121.8933 | -0.11444 | 121.8475 | 1.4211e-13 | 0.082828 | 0.0076283 | 0.068774 | 0.076579 | 0.10118 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.032408 | 0.01415 | 41.9849 | 75.6491 | 114.65 | 121.9151 | 121.873 | 121.8321 | -0.058478 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.032021 | 0.067272 | -0.11836 | 0.055963 | 0.067543 | 42.0993 | 114.7645 | 114.7085 | 0.025481 | -0.01547 | -0.00392 | -121.9095 | 0.13838 | 0.048932 | 0.052852 | -121.8155 | -121.7803 | 122.0295 | 121.9875 | 121.9465 | 75.7635 | -121.906 | 0.052437 | 0.14646 | 0.18171 | 0.19722 | -121.9659
3935.0781 | 121.9803 | -0.041199 | 121.8063 | 1.4211e-13 | 0.082828 | 0.0076283 | 0.06856 | 0.076579 | 0.10118 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018758 | 0.032194 | 0.013723 | 42.2046 | 75.6491 | 114.705 | 121.9151 | 121.8639 | 121.8321 | -0.063057 | 0.019362 | 0.087354 | -0.065509 | -0.062004 | 0.027442 | 0.07643 | -0.11836 | -0.021858 | 0.10874 | 42.2458 | 114.7462 | 114.768 | 0.057522 | 0.025729 | -0.077162 | -121.8683 | 0.060561 | -0.02431 | 0.052852 | -121.7789 | -121.7299 | 121.9563 | 121.9051 | 121.8733 | 75.6903 | -121.8694 | -0.020805 | 0.068641 | 0.11763 | 0.12855 | -121.9247
3936.8438 | 121.9986 | -0.050354 | 121.7926 | 1.4211e-13 | 0.083683 | 0.0074147 | 0.06856 | 0.077006 | 0.10161 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.031981 | 0.014364 | 42.5617 | 75.5621 | 114.7599 | 121.9059 | 121.8547 | 121.8229 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.027442 | 0.071851 | -0.11836 | -0.003545 | 0.11332 | 42.6121 | 114.8103 | 114.8138 | 0.062096 | 0.030303 | -0.068007 | -121.85 | 0.074295 | -0.010576 | 0.057431 | -121.7652 | -121.7208 | 121.9563 | 121.9051 | 121.8733 | 75.6124 | -121.8465 | -0.007071 | 0.077796 | 0.12221 | 0.13313 | -121.911
3938.5469 | 121.9437 | -0.07782 | 121.788 | 1.4211e-13 | 0.083897 | 0.0080557 | 0.06856 | 0.076365 | 0.10225 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018117 | 0.032194 | 0.013723 | 42.8502 | 75.5438 | 114.8011 | 121.9013 | 121.8684 | 121.8229 | -0.058478 | 0.019362 | 0.082776 | -0.056351 | -0.066582 | 0.027442 | 0.071851 | -0.12294 | 0.019342 | 0.11332 | 42.928 | 114.879 | 114.8596 | 0.080411 | 0.034881 | -0.045119 | -121.8546 | 0.097182 | 0.021469 | 0.066588 | -121.7606 | -121.7162 | 121.9792 | 121.9463 | 121.9007 | 75.6216 | -121.8465 | 0.011238 | 0.10526 | 0.14967 | 0.1606 | -121.911
3940.3125 | 121.9803 | -0.082397 | 121.788 | 1.4211e-13 | 0.08411 | 0.0080557 | 0.06856 | 0.076365 | 0.10247 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018331 | 0.031981 | 0.01415 | 43.2851 | 75.5438 | 114.824 | 121.9059 | 121.8639 | 121.8229 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.0366 | 0.067272 | -0.11836 | 0.023919 | 0.1179 | 43.3675 | 114.9064 | 114.8825 | 0.075832 | 0.034881 | -0.035964 | -121.8454 | 0.10634 | 0.021467 | 0.057431 | -121.7514 | -121.7208 | 121.9883 | 121.9463 | 121.9053 | 75.6262 | -121.8465 | 0.024972 | 0.119 | 0.14967 | 0.16059 | -121.9064
3942.0781 | 121.8979 | -0.091553 | 121.7972 | 1.4211e-13 | 0.084538 | 0.0078419 | 0.068774 | 0.076152 | 0.10289 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.031981 | 0.013937 | 43.7201 | 75.5071 | 114.8744 | 121.9059 | 121.8684 | 121.8275 | -0.058478 | 0.033099 | 0.091933 | -0.051772 | -0.062004 | 0.032021 | 0.07643 | -0.12294 | 0.033075 | 0.10874 | 43.8116 | 114.9659 | 114.9329 | 0.071256 | 0.030305 | -0.031386 | -121.8592 | 0.12465 | 0.039781 | 0.071167 | -121.7652 | -121.7207 | 121.9975 | 121.96 | 121.919 | 75.5987 | -121.8557 | 0.029549 | 0.12357 | 0.16798 | 0.18349 | -121.9201
3943.8594 | 121.9574 | -0.07782 | 121.8063 | 1.4211e-13 | 0.084538 | 0.0078419 | 0.068774 | 0.076152 | 0.10289 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018117 | 0.032408 | 0.01415 | 43.0058 | 75.5026 | 114.9247 | 121.9013 | 121.8639 | 121.8183 | -0.058478 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.11378 | 0.019342 | 0.095007 | 43.0837 | 115.0026 | 114.9832 | 0.057522 | 0.011993 | -0.035962 | -121.8775 | 0.10176 | 0.01689 | 0.052852 | -121.7697 | -121.7345 | 121.9792 | 121.9417 | 121.8961 | 75.5804 | -121.8648 | 0.006659 | 0.11442 | 0.14967 | 0.15602 | -121.9201
3945.625 | 121.843 | -0.10071 | 121.7789 | 1.4211e-13 | 0.084965 | 0.0078419 | 0.068988 | 0.076793 | 0.10332 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018117 | 0.032194 | 0.013937 | 43.6651 | 75.6033 | 115.3505 | 121.9013 | 121.8639 | 121.8229 | -0.067636 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.067272 | -0.11836 | 0.033072 | 0.12247 | 43.7658 | 115.4512 | 115.4182 | 0.084987 | 0.044036 | -0.017653 | -121.8455 | 0.12465 | 0.039778 | 0.057431 | -121.7468 | -121.7116 | 122.002 | 121.9646 | 121.9236 | 75.704 | -121.8465 | 0.034126 | 0.13273 | 0.16798 | 0.18806 | -121.8972
3947.3281 | 121.9757 | -0.082397 | 121.7743 | 1.4211e-13 | 0.086461 | 0.0080557 | 0.068774 | 0.077006 | 0.1046 | -0.02518 | -0.0044395 | -0.0016987 | 0.018545 | 0.032194 | 0.01415 | 44.1413 | 75.672 | 115.6069 | 121.8968 | 121.8639 | 121.8092 | -0.063057 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 0.01934 | 0.12247 | 44.2237 | 115.6893 | 115.67 | 0.089565 | 0.034879 | -0.035964 | -121.8409 | 0.11092 | 0.021467 | 0.057431 | -121.7377 | -121.7024 | 121.9792 | 121.9463 | 121.8916 | 75.7544 | -121.8373 | 0.015815 | 0.119 | 0.15425 | 0.16975 | -121.8927
3949.0938 | 121.994 | -0.068665 | 121.7926 | 1.4211e-13 | 0.086461 | 0.0080557 | 0.06856 | 0.076793 | 0.10503 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018331 | 0.031981 | 0.01415 | 44.3336 | 75.5712 | 115.7076 | 121.8968 | 121.8547 | 121.8046 | -0.063057 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.12294 | 0.005608 | 0.10416 | 44.4022 | 115.7763 | 115.7707 | 0.062096 | 0.011989 | -0.054274 | -121.8592 | 0.097185 | 0.007735 | 0.062009 | -121.7606 | -121.7162 | 121.9654 | 121.9234 | 121.8733 | 75.6399 | -121.8557 | 0.002083 | 0.10069 | 0.1451 | 0.15602 | -121.9155
3950.875 | 121.9116 | -0.068665 | 121.8018 | 1.4211e-13 | 0.087529 | 0.0076283 | 0.068988 | 0.076793 | 0.10524 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.032408 | 0.014364 | 44.6312 | 75.5987 | 115.7626 | 121.8922 | 121.8547 | 121.8137 | -0.058478 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.032021 | 0.071851 | -0.11836 | 0.010187 | 0.090427 | 44.6998 | 115.8312 | 115.821 | 0.052941 | 0.011991 | -0.049696 | -121.8592 | 0.097185 | 0.007735 | 0.057431 | -121.7697 | -121.7299 | 121.9608 | 121.9234 | 121.8824 | 75.6674 | -121.8602 | 0.01124 | 0.10069 | 0.14052 | 0.15144 | -121.9201
3952.5781 | 121.9711 | -0.073242 | 121.7743 | 1.4211e-13 | 0.087102 | 0.0080557 | 0.068988 | 0.076365 | 0.10589 | -0.0099192 | -0.0042257 | -0.0021259 | 0.018758 | 0.031981 | 0.01415 | 44.5076 | 75.5667 | 115.8038 | 121.8922 | 121.8547 | 121.8183 | -0.072215 | 0.02852 | 0.087354 | -0.070087 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 0.001027 | 0.11789 | 44.5808 | 115.877 | 115.876 | 0.080407 | 0.044036 | -0.049697 | -121.8363 | 0.10176 | 0.003155 | 0.052852 | -121.7423 | -121.7024 | 121.9654 | 121.9279 | 121.8916 | 75.6399 | -121.8465 | 0.011238 | 0.10526 | 0.14509 | 0.1606 | -121.8972
3954.3594 | 121.9574 | -0.054932 | 121.7651 | 1.4211e-13 | 0.087956 | 0.0078419 | 0.068774 | 0.076579 | 0.1061 | -0.0022892 | -0.0042257 | -0.0019123 | 0.017904 | 0.031981 | 0.013723 | 44.5213 | 75.4705 | 115.8404 | 121.8922 | 121.8455 | 121.8046 | -0.058478 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.11378 | -0.003546 | 0.12705 | 44.5762 | 115.8953 | 115.8989 | 0.080404 | 0.039455 | -0.05885 | -121.8226 | 0.078873 | -0.005998 | 0.052852 | -121.7285 | -121.6933 | 121.9471 | 121.9005 | 121.8595 | 75.5254 | -121.8236 | -0.002493 | 0.091532 | 0.12678 | 0.14229 | -121.8789
3956.0625 | 121.907 | -0.068665 | 121.756 | 1.4211e-13 | 0.087743 | 0.0076283 | 0.06856 | 0.076365 | 0.10631 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018331 | 0.032408 | 0.01415 | 45.0753 | 75.4888 | 115.8862 | 121.8922 | 121.8593 | 121.8092 | -0.058478 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.022864 | 0.07643 | -0.11836 | 0.010187 | 0.1362 | 45.1439 | 115.9548 | 115.9447 | 0.1033 | 0.05319 | -0.049696 | -121.8134 | 0.092606 | 0.003156 | 0.052852 | -121.7331 | -121.6796 | 121.9608 | 121.9279 | 121.8778 | 75.5575 | -121.8145 | 0.01124 | 0.091529 | 0.1451 | 0.15144 | -121.8743
3957.8281 | 121.8613 | -0.09613 | 121.7834 | 1.4211e-13 | 0.087956 | 0.0080557 | 0.068774 | 0.076365 | 0.10695 | -0.01755 | -0.0042257 | -0.0019123 | 0.018331 | 0.032194 | 0.013937 | 44.8921 | 75.3881 | 115.9091 | 121.8922 | 121.8455 | 121.8 | -0.053899 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.067272 | -0.12752 | 0.042231 | 0.10874 | 44.9883 | 116.0052 | 115.963 | 0.062094 | 0.016566 | -0.031388 | -121.8455 | 0.12007 | 0.0352 | 0.066588 | -121.7514 | -121.7162 | 121.9883 | 121.9417 | 121.8961 | 75.4842 | -121.8373 | 0.034126 | 0.12815 | 0.1634 | 0.17891 | -121.911
3959.6094 | 121.8933 | -0.059509 | 121.7743 | 1.4211e-13 | 0.089238 | 0.0080557 | 0.06856 | 0.076793 | 0.10781 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018331 | 0.032194 | 0.013723 | 45.4232 | 75.3515 | 115.9182 | 121.8876 | 121.8501 | 121.8137 | -0.053899 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 0.00561 | 0.11332 | 45.4827 | 115.9777 | 115.9721 | 0.075828 | 0.039457 | -0.06343 | -121.8363 | 0.08345 | 0.003158 | 0.066588 | -121.7423 | -121.7024 | 121.9471 | 121.9096 | 121.8733 | 75.411 | -121.8282 | -0.002495 | 0.09153 | 0.13136 | 0.14228 | -121.8972
3961.375 | 121.9025 | -0.086975 | 121.7377 | 1.4211e-13 | 0.090093 | 0.0080557 | 0.068774 | 0.076365 | 0.10866 | -0.02518 | -0.0044395 | -0.0016987 | 0.018331 | 0.032194 | 0.013937 | 45.5835 | 75.3377 | 115.9457 | 121.8876 | 121.8501 | 121.8046 | -0.058478 | 0.014784 | 0.087354 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.12294 | 0.028497 | 0.14994 | 45.6705 | 116.0327 | 116.0042 | 0.11245 | 0.066921 | -0.035964 | -121.8043 | 0.10176 | 0.026045 | 0.062009 | -121.7102 | -121.6658 | 121.9746 | 121.9371 | 121.8916 | 75.4247 | -121.7961 | 0.020393 | 0.11442 | 0.15883 | 0.17433 | -121.8606
3963.0938 | 121.8384 | -0.09613 | 121.8155 | 1.4211e-13 | 0.091162 | 0.0082693 | 0.068774 | 0.076579 | 0.10952 | -0.01755 | -0.0044395 | -0.0019123 | 0.018545 | 0.032194 | 0.013937 | 46.316 | 75.411 | 115.9594 | 121.8876 | 121.8455 | 121.8137 | -0.058478 | 0.033099 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.067272 | -0.12294 | 0.037652 | 0.072116 | 46.4121 | 116.0556 | 116.0179 | 0.03005 | -0.001742 | -0.026809 | -121.8821 | 0.12923 | 0.039779 | 0.066588 | -121.7789 | -121.7482 | 121.9837 | 121.9417 | 121.9099 | 75.5071 | -121.874 | 0.029548 | 0.13273 | 0.1634 | 0.18348 | -121.9384
3964.875 | 121.9437 | -0.054932 | 121.7514 | 1.4211e-13 | 0.091375 | 0.0078419 | 0.068988 | 0.076152 | 0.11037 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018331 | 0.032194 | 0.013937 | 47.0852 | 75.443 | 115.9732 | 121.883 | 121.8455 | 121.8 | -0.063057 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.0366 | 0.07643 | -0.11836 | -0.008125 | 0.13162 | 47.1401 | 116.0281 | 116.0362 | 0.094137 | 0.048609 | -0.063429 | -121.8088 | 0.083452 | -0.010577 | 0.052852 | -121.7148 | -121.675 | 121.938 | 121.9005 | 121.8549 | 75.498 | -121.8145 | -0.002493 | 0.091532 | 0.13136 | 0.13313 | -121.8698
3966.5938 | 121.875 | -0.073242 | 121.7651 | 1.4211e-13 | 0.091803 | 0.0080557 | 0.068774 | 0.076579 | 0.11101 | -0.01755 | -0.0044395 | -0.0019123 | 0.018545 | 0.032194 | 0.01415 | 46.5495 | 75.3881 | 115.9915 | 121.883 | 121.8364 | 121.8046 | -0.063057 | 0.033099 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 0.010185 | 0.11789 | 46.6228 | 116.0647 | 116.0545 | 0.071246 | 0.039455 | -0.049697 | -121.8317 | 0.10634 | 0.012312 | 0.062009 | -121.7285 | -121.6933 | 121.9563 | 121.9096 | 121.8778 | 75.4613 | -121.8282 | 0.00666 | 0.10984 | 0.14509 | 0.15602 | -121.8881
3968.375 | 121.9482 | -0.045776 | 121.7285 | 1.4211e-13 | 0.092444 | 0.0082693 | 0.068774 | 0.076579 | 0.11165 | -0.01755 | -0.0044395 | -0.0019123 | 0.018331 | 0.032408 | 0.013937 | 46.7327 | 75.4797 | 116.0006 | 121.883 | 121.8364 | 121.8046 | -0.063057 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.081008 | -0.12294 | -0.017281 | 0.15451 | 46.7784 | 116.0464 | 116.0637 | 0.10787 | 0.076076 | -0.077163 | -121.7905 | 0.069717 | -0.010575 | 0.066588 | -121.6919 | -121.6475 | 121.9288 | 121.8822 | 121.8504 | 75.5254 | -121.7916 | -0.016228 | 0.082376 | 0.12678 | 0.13313 | -121.8515
3970.0938 | 121.8201 | -0.11444 | 121.8201 | 1.4211e-13 | 0.094153 | 0.0080557 | 0.068346 | 0.076365 | 0.11315 | -0.01755 | -0.0046531 | -0.0019123 | 0.018331 | 0.031981 | 0.013937 | 47.5522 | 75.411 | 116.0235 | 121.8785 | 121.8364 | 121.7954 | -0.067636 | 0.023941 | 0.078197 | -0.056351 | -0.057425 | 0.0366 | 0.067272 | -0.12294 | 0.046805 | 0.058382 | 47.6666 | 116.138 | 116.0912 | 0.016315 | -0.024633 | -0.008498 | -121.8775 | 0.13838 | 0.05809 | 0.066588 | -121.7835 | -121.7528 | 121.9929 | 121.9508 | 121.9099 | 75.5254 | -121.8877 | 0.057016 | 0.15104 | 0.18171 | 0.19264 | -121.943
3971.8594 | 121.8796 | -0.091553 | 121.7606 | 1.4211e-13 | 0.093726 | 0.0080557 | 0.068774 | 0.075938 | 0.11272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018545 | 0.032408 | 0.013723 | 47.6666 | 75.3881 | 116.051 | 121.8785 | 121.8364 | 121.8 | -0.063057 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.12294 | 0.028496 | 0.11789 | 47.7582 | 116.1426 | 116.1141 | 0.075824 | 0.039454 | -0.031386 | -121.8363 | 0.11549 | 0.030623 | 0.062009 | -121.724 | -121.6841 | 121.97 | 121.9279 | 121.8916 | 75.4797 | -121.8236 | 0.015814 | 0.12815 | 0.16798 | 0.17891 | -121.8835
3973.5625 | 121.9437 | -0.064087 | 121.7606 | 1.4211e-13 | 0.092657 | 0.0084831 | 0.068346 | 0.075938 | 0.11208 | 0.0053413 | -0.0046531 | -0.0019123 | 0.018331 | 0.032194 | 0.01415 | 48.0604 | 75.3881 | 116.0098 | 121.8739 | 121.841 | 121.7909 | -0.067636 | 0.019362 | 0.078197 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.11836 | -0.003549 | 0.11331 | 48.1245 | 116.0739 | 116.0774 | 0.080403 | 0.030297 | -0.054274 | -121.8271 | 0.083449 | 0.003157 | 0.057431 | -121.7285 | -121.6841 | 121.938 | 121.905 | 121.8549 | 75.4522 | -121.8282 | -0.002495 | 0.096108 | 0.14052 | 0.14228 | -121.8789
3975.3281 | 121.7926 | -0.091553 | 121.7606 | 1.4211e-13 | 0.10377 | 0.0080557 | 0.068774 | 0.075938 | 0.12319 | -0.0022892 | -0.0040121 | -0.0019123 | 0.018545 | 0.032194 | 0.013937 | 49.8231 | 75.3973 | 116.0464 | 121.8647 | 121.8181 | 121.7725 | -0.035584 | 0.033099 | 0.082776 | -0.065509 | -0.062004 | 0.032021 | 0.07643 | -0.11836 | 0.055969 | 0.10416 | 49.9146 | 116.138 | 116.082 | 0.057508 | 0.011983 | -0.026808 | -121.8226 | 0.12465 | 0.026044 | 0.052852 | -121.7285 | -121.6841 | 121.9563 | 121.9096 | 121.8641 | 75.4888 | -121.7961 | 0.029549 | 0.12357 | 0.16798 | 0.17433 | -121.8789
3977.0312 | 121.9437 | -0.064087 | 121.7514 | 1.4211e-13 | 0.17214 | 0.0078419 | 0.068774 | 0.075511 | 0.19242 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018758 | 0.032194 | 0.013937 | 51.073 | 75.2553 | 115.6893 | 121.851 | 121.8089 | 121.7817 | -0.021847 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.027442 | 0.071851 | -0.11836 | 0.04224 | 0.099576 | 51.1371 | 115.7534 | 115.7112 | 0.057506 | 0.030295 | -0.054274 | -121.818 | 0.092607 | 0.003157 | 0.057431 | -121.724 | -121.6796 | 121.9151 | 121.873 | 121.8458 | 75.3194 | -121.7733 | -0.002495 | 0.091529 | 0.13594 | 0.15144 | -121.8698
3978.7969 | 121.9116 | -0.073242 | 121.8018 | 1.4211e-13 | -0.027213 | 0.00036331 | -0.0030235 | -0.0097409 | 0.0078136 | -0.02518 | -0.0042257 | -0.0016987 | 0.018117 | 0.032408 | 0.013723 | 4.9686 | 5.0791 | 4.9728 | 5.1525 | 5.202 | 5.3387 | 4.8135 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.0366 | 0.067272 | -0.12294 | 4.8867 | -116.6493 | 5.0418 | 5.046 | 0.15926 | -116.5997 | -116.4631 | -0.049697 | -121.8592 | 0.097183 | 0.016891 | 0.066588 | -121.7652 | -121.7345 | 5.2257 | 5.2753 | 5.4119 | 5.1523 | -116.9883 | 0.015817 | 0.10984 | 0.14051 | 0.1606 | -121.9247
3980.5781 | 121.9803 | -0.054932 | 121.8201 | 1.4211e-13 | -0.027213 | 0.00057691 | -0.0030235 | -0.0097409 | 0.0078136 | -0.01755 | -0.0042257 | -0.0016987 | 0.018758 | 0.031981 | 0.013509 | 4.8404 | 4.928 | 4.7896 | 4.9647 | 5.0234 | 5.1601 | 4.6807 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.13668 | 4.7356 | -116.8553 | 4.8953 | 4.8446 | 0.10892 | -116.7966 | -116.66 | -0.081744 | -121.8867 | 0.083452 | -0.001419 | 0.080325 | -121.7835 | -121.7436 | 5.0197 | 5.0784 | 5.215 | 4.9829 | -117.1394 | -0.01165 | 0.091532 | 0.13136 | 0.14229 | -121.9567
3982.2969 | 121.8613 | -0.10529 | 121.8384 | 1.4211e-13 | -0.027213 | 0.00079051 | -0.0032373 | -0.0099547 | 0.0080272 | -0.01755 | -0.0046531 | -0.0016987 | 0.018545 | 0.032408 | 0.013937 | 4.8175 | 4.9142 | 4.7622 | 4.9418 | 4.9868 | 5.1281 | 4.6074 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.041178 | 0.067272 | -0.12294 | 4.7127 | -116.8965 | 4.9228 | 4.8674 | 0.15471 | -116.8516 | -116.7103 | -0.017653 | -121.905 | 0.12923 | 0.048935 | 0.066588 | -121.7972 | -121.7711 | 5.0471 | 5.0921 | 5.2334 | 5.0195 | -117.2309 | 0.038704 | 0.14646 | 0.17256 | 0.19264 | -121.9613
3984.0625 | 121.9666 | -0.068665 | 121.8018 | 1.4211e-13 | -0.028068 | 0.00014951 | -0.0032373 | -0.0097409 | 0.0086682 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018545 | 0.032408 | 0.013937 | 4.8084 | 4.8868 | 4.7393 | 4.9098 | 4.9776 | 5.1052 | 4.6074 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.067272 | -0.11836 | 4.6761 | -116.892 | 4.877 | 4.8079 | 0.13182 | -116.8241 | -116.6966 | -0.049696 | -121.8683 | 0.097185 | 0.007735 | 0.057431 | -121.7606 | -121.7345 | 4.9785 | 5.0463 | 5.1738 | 4.9554 | -117.1943 | 0.002083 | 0.10984 | 0.13594 | 0.15144 | -121.9201
3985.8281 | 121.907 | -0.091553 | 121.8613 | 1.4211e-13 | -0.028282 | 0.00057691 | -0.0034509 | -0.010168 | 0.0084546 | -0.0099192 | -0.0048667 | -0.0014849 | 0.018545 | 0.031981 | 0.013937 | 4.8541 | 4.9371 | 4.7805 | 4.9464 | 5.0051 | 5.1372 | 4.6349 | 0.023941 | 0.087354 | -0.065509 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.7265 | -116.9148 | 4.9457 | 4.872 | 0.14555 | -116.8561 | -116.724 | -0.031386 | -121.9233 | 0.11549 | 0.026044 | 0.05743 | -121.8247 | -121.7894 | 5.038 | 5.0967 | 5.2288 | 5.0287 | -117.2263 | 0.029549 | 0.12815 | 0.1634 | 0.17891 | -121.9842
3987.6094 | 121.9574 | -0.064087 | 121.8201 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0034509 | -0.0099547 | 0.0084546 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018331 | 0.031981 | 0.013509 | 4.8725 | 4.9463 | 4.7942 | 4.9556 | 5.0189 | 5.151 | 4.6532 | 0.02852 | 0.087354 | -0.056351 | -0.057425 | 0.0366 | 0.07643 | -0.11836 | 4.7173 | -116.8645 | 4.9365 | 4.8583 | 0.14097 | -116.8012 | -116.6691 | -0.054274 | -121.8775 | 0.092607 | 0.007736 | 0.06201 | -121.7835 | -121.7436 | 5.0197 | 5.0829 | 5.215 | 5.0104 | -117.1668 | 0.006662 | 0.10069 | 0.14052 | 0.15144 | -121.9384
3989.3125 | 121.9208 | -0.086975 | 121.8704 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0032373 | -0.0097409 | 0.008241 | -0.01755 | -0.0044395 | -0.0019123 | 0.017904 | 0.031981 | 0.013937 | 4.8679 | 4.9509 | 4.7851 | 4.9464 | 5.0005 | 5.1418 | 4.6487 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 4.7356 | -116.924 | 4.9548 | 4.872 | 0.13639 | -116.8699 | -116.7286 | -0.031386 | -121.937 | 0.1155 | 0.026045 | 0.057431 | -121.8338 | -121.7986 | 5.0334 | 5.0875 | 5.2288 | 5.0379 | -117.2218 | 0.020393 | 0.12357 | 0.15883 | 0.16975 | -121.9888
3991.0938 | 121.8887 | -0.10529 | 121.8704 | 1.4211e-13 | -0.028282 | 0.00014951 | -0.0030235 | -0.0099547 | 0.0084546 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018117 | 0.031981 | 0.013723 | 4.877 | 4.9646 | 4.8079 | 4.9647 | 5.0234 | 5.1464 | 4.667 | 0.023941 | 0.078197 | -0.056351 | -0.062004 | 0.045757 | 0.07643 | -0.11836 | 4.7723 | -116.9057 | 4.9823 | 4.9132 | 0.14097 | -116.847 | -116.724 | -0.013075 | -121.9324 | 0.12923 | 0.048935 | 0.06201 | -121.8247 | -121.794 | 5.07 | 5.1287 | 5.2517 | 5.0699 | -117.2035 | 0.043282 | 0.15104 | 0.18172 | 0.18348 | -121.9888
3992.875 | 121.9849 | -0.086975 | 121.8292 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0032373 | -0.0097409 | 0.008241 | -0.01755 | -0.0042257 | -0.0021259 | 0.018331 | 0.032622 | 0.013296 | 4.8725 | 4.9555 | 4.7988 | 4.9556 | 5.0097 | 5.1372 | 4.6487 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.11836 | 4.7356 | -116.8736 | 4.9594 | 4.8858 | 0.15013 | -116.8195 | -116.692 | -0.031386 | -121.8912 | 0.11092 | 0.026045 | 0.057431 | -121.788 | -121.7528 | 5.0426 | 5.0967 | 5.2242 | 5.0424 | -117.1806 | 0.024971 | 0.12815 | 0.1634 | 0.16975 | -121.9476
3994.5938 | 122.0444 | -0.050354 | 121.8384 | 1.4211e-13 | -0.028495 | 0.00014951 | -0.0032373 | -0.010168 | 0.0084546 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.031981 | 0.013937 | 4.8816 | 4.96 | 4.7942 | 4.9556 | 5.0051 | 5.1418 | 4.6624 | 0.033099 | 0.078197 | -0.051772 | -0.057425 | 0.045757 | 0.071851 | -0.12294 | 4.7127 | -116.8828 | 4.932 | 4.8446 | 0.13181 | -116.8333 | -116.6966 | -0.072585 | -121.8958 | 0.083453 | -0.001418 | 0.071167 | -121.7926 | -121.7665 | 5.0059 | 5.0555 | 5.1922 | 5.0104 | -117.176 | -0.007071 | 0.096111 | 0.12221 | 0.12855 | -121.9613
3996.3594 | 122.0123 | -0.068665 | 121.8201 | 1.4211e-13 | -0.028282 | 0.00057691 | -0.0036647 | -0.0097409 | 0.0086682 | -0.0099192 | -0.0048667 | -0.0016987 | 0.018331 | 0.032408 | 0.013509 | 4.8633 | 4.9371 | 4.7805 | 4.9052 | 4.9914 | 5.1281 | 4.6487 | 0.019362 | 0.082776 | -0.056351 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 4.7173 | -116.9148 | 4.932 | 4.8491 | 0.13182 | -116.8287 | -116.692 | -0.054274 | -121.8867 | 0.088027 | 0.012314 | 0.066588 | -121.7789 | -121.7436 | 4.9739 | 5.0601 | 5.1967 | 5.0058 | -117.1714 | 0.002083 | 0.10984 | 0.1451 | 0.15144 | -121.943
3998.125 | 122.0352 | -0.064087 | 121.8521 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018545 | 0.031981 | 0.01415 | 4.845 | 4.928 | 4.7667 | 4.8869 | 4.9822 | 5.1143 | 4.6395 | 0.019362 | 0.087354 | -0.051772 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.7036 | -116.9652 | 4.9091 | 4.8308 | 0.12724 | -116.8699 | -116.7378 | -0.058852 | -121.9141 | 0.083449 | 0.012315 | 0.071167 | -121.8155 | -121.7803 | 4.951 | 5.0463 | 5.1784 | 4.9921 | -117.2126 | 0.002083 | 0.10069 | 0.13594 | 0.15144 | -121.9751
3999.9062 | 121.9299 | -0.09613 | 121.8842 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0032373 | -0.010168 | 0.0084546 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018117 | 0.031981 | 0.013509 | 4.8496 | 4.9234 | 4.7667 | 4.8777 | 4.9731 | 5.1098 | 4.6395 | 0.033099 | 0.087354 | -0.047194 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 4.7356 | -117.0064 | 4.9457 | 4.8629 | 0.12724 | -116.9111 | -116.7744 | -0.026809 | -121.9507 | 0.12923 | 0.048936 | 0.075745 | -121.843 | -121.8077 | 4.9739 | 5.0692 | 5.2059 | 5.0195 | -117.2447 | 0.029548 | 0.13731 | 0.17256 | 0.18348 | -122.0071
4001.6094 | 121.9116 | -0.10529 | 121.9116 | 1.4211e-13 | -0.028068 | 0.00014951 | -0.0030235 | -0.0097409 | 0.0086682 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.032194 | 0.013723 | 4.8496 | 4.928 | 4.7667 | 4.8823 | 4.9731 | 5.1052 | 4.6395 | 0.023941 | 0.082776 | -0.051772 | -0.071161 | 0.0366 | 0.071851 | -0.12294 | 4.7448 | -117.0293 | 4.9548 | 4.872 | 0.12724 | -116.9385 | -116.8064 | -0.017653 | -121.9828 | 0.12923 | 0.053514 | 0.071167 | -121.875 | -121.8398 | 4.9876 | 5.0784 | 5.2105 | 5.0333 | -117.2721 | 0.034125 | 0.14189 | 0.17714 | 0.18806 | -122.0346
4003.3594 | 122.0169 | -0.059509 | 121.8521 | 1.4211e-13 | -0.028495 | 0.00057691 | -0.0034509 | -0.0097409 | 0.008241 | -0.01755 | -0.0040121 | -0.0016987 | 0.018545 | 0.032194 | 0.013509 | 4.8404 | 4.9234 | 4.7622 | 4.8777 | 4.9685 | 5.096 | 4.6349 | 0.019362 | 0.087354 | -0.065509 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 4.6944 | -116.9744 | 4.8999 | 4.8217 | 0.12724 | -116.8836 | -116.7561 | -0.058852 | -121.9141 | 0.078871 | -0.006 | 0.052852 | -121.8155 | -121.7803 | 4.9373 | 5.028 | 5.1555 | 4.9829 | -117.2172 | -0.002495 | 0.096109 | 0.13136 | 0.14686 | -121.9705
4005.0781 | 121.9391 | -0.091553 | 121.907 | 1.4211e-13 | -0.028282 | 0.00036331 | -0.0034509 | -0.010168 | 0.008241 | -0.01755 | -0.0044395 | -0.0019123 | 0.018545 | 0.032408 | 0.013509 | 4.8038 | 4.8914 | 4.7301 | 4.8411 | 4.941 | 5.0731 | 4.6029 | 0.02852 | 0.087354 | -0.06093 | -0.052847 | 0.041178 | 0.081008 | -0.11836 | 4.6944 | -117.0659 | 4.8953 | 4.8217 | 0.12724 | -116.966 | -116.8339 | -0.026808 | -121.9599 | 0.12007 | 0.030623 | 0.057431 | -121.8659 | -121.826 | 4.9327 | 5.0326 | 5.1647 | 4.9829 | -117.3042 | 0.038706 | 0.13273 | 0.17256 | 0.17891 | -122.0254
4006.8594 | 122.0032 | -0.073242 | 121.8842 | 1.4211e-13 | -0.028282 | 0.00057691 | -0.0034509 | -0.0099547 | 0.0084546 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018331 | 0.032408 | 0.013723 | 4.8312 | 4.9097 | 4.753 | 4.8686 | 4.9593 | 5.0869 | 4.6258 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.0366 | 0.081008 | -0.11836 | 4.699 | -117.0156 | 4.9045 | 4.8262 | 0.12724 | -116.9248 | -116.7973 | -0.045119 | -121.9416 | 0.097183 | 0.016891 | 0.06201 | -121.8476 | -121.8031 | 4.9418 | 5.0326 | 5.1601 | 4.9829 | -117.2584 | 0.015817 | 0.10984 | 0.15425 | 0.15602 | -122.0025
4008.625 | 121.9666 | -0.09613 | 121.9116 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008882 | -0.0022892 | -0.0044395 | -0.0021259 | 0.018331 | 0.031981 | 0.013723 | 4.8496 | 4.9234 | 4.7622 | 4.8777 | 4.9639 | 5.096 | 4.6395 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.032021 | 0.07643 | -0.12752 | 4.7356 | -117.0339 | 4.9457 | 4.8583 | 0.12266 | -116.9477 | -116.8156 | -0.031388 | -121.9782 | 0.12007 | 0.039779 | 0.071167 | -121.8796 | -121.8352 | 4.9739 | 5.06 | 5.1921 | 5.0195 | -117.2721 | 0.029548 | 0.12815 | 0.17256 | 0.17891 | -122.0391
4010.3281 | 121.9803 | -0.082397 | 121.9162 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0034509 | -0.0099547 | 0.0084546 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018331 | 0.032408 | 0.013723 | 4.845 | 4.9142 | 4.7576 | 4.8686 | 4.9593 | 5.096 | 4.6441 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 4.7265 | -117.0476 | 4.9274 | 4.84 | 0.1135 | -116.9569 | -116.8202 | -0.045121 | -121.9828 | 0.10634 | 0.026046 | 0.071167 | -121.8796 | -121.8398 | 4.951 | 5.0417 | 5.1784 | 4.9966 | -117.2721 | 0.015815 | 0.119 | 0.15883 | 0.16975 | -122.0437
4012.0938 | 122.0078 | -0.068665 | 121.8979 | 1.4211e-13 | -0.028495 | 0.00057691 | -0.0036647 | -0.010168 | 0.008241 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018545 | 0.032194 | 0.013937 | 4.6985 | 4.7769 | 4.6202 | 4.7267 | 4.822 | 4.9541 | 4.493 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 4.5616 | -117.1712 | 4.7671 | 4.6889 | 0.12726 | -117.0759 | -116.9438 | -0.054274 | -121.9553 | 0.097185 | 0.007735 | 0.062009 | -121.8613 | -121.8215 | 4.7953 | 4.8906 | 5.0227 | 4.8456 | -117.4049 | 0.01124 | 0.10526 | 0.1451 | 0.15144 | -122.0208
4013.8594 | 122.0123 | -0.059509 | 121.8979 | 1.4211e-13 | -0.028495 | 0.00014951 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0040121 | -0.0019123 | 0.018331 | 0.031981 | 0.013937 | 4.7122 | 4.7906 | 4.6385 | 4.745 | 4.8357 | 4.9632 | 4.5021 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.11836 | 4.5616 | -117.1529 | 4.7717 | 4.6981 | 0.13641 | -117.0622 | -116.9347 | -0.058852 | -121.9553 | 0.08345 | -0.001421 | 0.057431 | -121.8613 | -121.8215 | 4.8045 | 4.8952 | 5.0227 | 4.8501 | -117.3958 | 0.002084 | 0.096109 | 0.13594 | 0.14228 | -122.0162
4015.5625 | 122.0352 | -0.068665 | 121.9025 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0030235 | -0.0099547 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.018331 | 0.031981 | 0.013937 | 4.7214 | 4.7998 | 4.6385 | 4.745 | 4.8449 | 4.9678 | 4.5159 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.032021 | 0.07643 | -0.12752 | 4.5845 | -117.1575 | 4.79 | 4.7072 | 0.12268 | -117.0576 | -116.9347 | -0.058853 | -121.9645 | 0.097185 | 0.003156 | 0.062009 | -121.8704 | -121.826 | 4.8136 | 4.9135 | 5.0365 | 4.8684 | -117.3866 | 0.006661 | 0.10069 | 0.1451 | 0.14686 | -122.03
4017.3281 | 121.9849 | -0.10986 | 121.907 | 1.4211e-13 | -0.028495 | 0.00079051 | -0.0032373 | -0.010382 | 0.008241 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018331 | 0.032408 | 0.013723 | 4.7168 | 4.7952 | 4.634 | 4.745 | 4.8403 | 4.9678 | 4.5159 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.041178 | 0.071851 | -0.11836 | 4.6257 | -117.1621 | 4.8266 | 4.7438 | 0.1181 | -117.0668 | -116.9392 | -0.008498 | -121.9645 | 0.13838 | 0.044354 | 0.052852 | -121.8659 | -121.8352 | 4.8548 | 4.9501 | 5.0777 | 4.9051 | -117.3912 | 0.052438 | 0.15104 | 0.18171 | 0.19264 | -122.0254
4019.0938 | 122.0306 | -0.068665 | 121.9025 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018117 | 0.032194 | 0.013509 | 4.7168 | 4.7952 | 4.6385 | 4.745 | 4.8311 | 4.9587 | 4.5067 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.027442 | 0.081008 | -0.12294 | 4.5754 | -117.1575 | 4.7855 | 4.7072 | 0.13184 | -117.0713 | -116.9438 | -0.054274 | -121.9599 | 0.097185 | 0.007735 | 0.062009 | -121.875 | -121.8215 | 4.8136 | 4.8998 | 5.0273 | 4.8639 | -117.3958 | 0.01124 | 0.096107 | 0.14967 | 0.15144 | -122.0254
4020.8125 | 122.0306 | -0.086975 | 121.9162 | 1.4211e-13 | -0.028709 | 0.00057691 | -0.0032373 | -0.010168 | 0.008241 | -0.01755 | -0.0040121 | -0.0016987 | 0.018331 | 0.032194 | 0.013937 | 4.7122 | 4.7906 | 4.6385 | 4.745 | 4.8357 | 4.9678 | 4.5067 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.027442 | 0.07643 | -0.12294 | 4.5937 | -117.1712 | 4.7992 | 4.7255 | 0.13184 | -117.0805 | -116.9484 | -0.035964 | -121.9782 | 0.11092 | 0.030624 | 0.066588 | -121.8888 | -121.8398 | 4.8319 | 4.9227 | 5.0548 | 4.8776 | -117.4095 | 0.024971 | 0.11442 | 0.1634 | 0.17433 | -122.0391
4022.5781 | 121.9986 | -0.091553 | 121.9254 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0028099 | -0.0097409 | 0.0086682 | -0.0099192 | -0.0040121 | -0.0019123 | 0.018545 | 0.032408 | 0.013937 | 4.7076 | 4.7769 | 4.634 | 4.7404 | 4.8265 | 4.9541 | 4.5021 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.032021 | 0.07643 | -0.12294 | 4.5937 | -117.185 | 4.7992 | 4.7255 | 0.13184 | -117.0988 | -116.9713 | -0.031386 | -121.9919 | 0.11549 | 0.035202 | 0.066588 | -121.8933 | -121.8489 | 4.8319 | 4.9181 | 5.0456 | 4.8684 | -117.4232 | 0.024971 | 0.12357 | 0.16798 | 0.17891 | -122.0483
4024.3438 | 121.9849 | -0.10071 | 121.9437 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0034509 | -0.010382 | 0.0080272 | -0.01755 | -0.0042257 | -0.0016987 | 0.018117 | 0.032194 | 0.013509 | 4.6985 | 4.7677 | 4.6157 | 4.7175 | 4.8082 | 4.9403 | 4.493 | 0.019362 | 0.091933 | -0.056351 | -0.062004 | 0.027442 | 0.067272 | -0.11378 | 4.5937 | -117.2262 | 4.7992 | 4.7164 | 0.12268 | -117.1354 | -117.0033 | -0.013074 | -122.0057 | 0.12007 | 0.044357 | 0.057431 | -121.9162 | -121.8764 | 4.8182 | 4.9089 | 5.041 | 4.8684 | -117.4507 | 0.038704 | 0.12815 | 0.16798 | 0.19264 | -122.0574
4026.0625 | 121.9986 | -0.082397 | 121.907 | 1.4211e-13 | -0.028495 | 0.00014951 | -0.0034509 | -0.0099547 | 0.0080272 | -0.02518 | -0.0042257 | -0.0014849 | 0.018331 | 0.032622 | 0.013723 | 4.6985 | 4.7769 | 4.6111 | 4.7267 | 4.8037 | 4.9403 | 4.4884 | 0.033099 | 0.087354 | -0.056351 | -0.066582 | 0.032021 | 0.071851 | -0.12752 | 4.5708 | -117.1804 | 4.7809 | 4.6935 | 0.12268 | -117.1034 | -116.9667 | -0.045121 | -121.9736 | 0.1155 | 0.026046 | 0.071167 | -121.875 | -121.8352 | 4.8091 | 4.886 | 5.0227 | 4.8593 | -117.4186 | 0.015815 | 0.11442 | 0.15425 | 0.16975 | -122.0346
4027.8438 | 122.0032 | -0.09613 | 121.9482 | 1.4211e-13 | -0.028495 | 0.00057691 | -0.0032373 | -0.0099547 | 0.0084546 | -0.0022892 | -0.0044395 | -0.0021259 | 0.018331 | 0.031981 | 0.013723 | 4.7168 | 4.786 | 4.634 | 4.7312 | 4.822 | 4.9541 | 4.5021 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.067272 | -0.1321 | 4.5983 | -117.217 | 4.8129 | 4.7301 | 0.13184 | -117.1263 | -116.9942 | -0.035967 | -122.0148 | 0.12007 | 0.0352 | 0.071167 | -121.9116 | -121.881 | 4.8274 | 4.9181 | 5.0502 | 4.8822 | -117.4461 | 0.029548 | 0.13273 | 0.1634 | 0.17891 | -122.0803
4029.5625 | 121.9711 | -0.10986 | 121.9299 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0030235 | -0.010168 | 0.008241 | -0.01755 | -0.0040121 | -0.0016987 | 0.018331 | 0.032194 | 0.013723 | 4.7214 | 4.7815 | 4.6294 | 4.7358 | 4.8311 | 4.9632 | 4.5021 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 4.612 | -117.1941 | 4.8312 | 4.7393 | 0.12726 | -117.0988 | -116.9667 | -0.013076 | -121.9874 | 0.1338 | 0.044354 | 0.05743 | -121.8933 | -121.8535 | 4.8457 | 4.941 | 5.0731 | 4.8913 | -117.4278 | 0.052438 | 0.14646 | 0.18629 | 0.18806 | -122.0529
4031.3438 | 121.9666 | -0.11444 | 121.9482 | 1.4211e-13 | -0.028068 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.032194 | 0.013723 | 4.7122 | 4.7998 | 4.6477 | 4.745 | 4.8403 | 4.9587 | 4.5113 | 0.02852 | 0.087354 | -0.051772 | -0.062004 | 0.032021 | 0.07643 | -0.11836 | 4.6257 | -117.2033 | 4.8266 | 4.7621 | 0.13641 | -117.108 | -116.9896 | -0.00392 | -122.0102 | 0.14296 | 0.062669 | 0.066589 | -121.9162 | -121.8718 | 4.8594 | 4.9547 | 5.0731 | 4.9142 | -117.437 | 0.052437 | 0.14646 | 0.19087 | 0.2018 | -122.0666
4033.125 | 122.0901 | -0.064087 | 121.8887 | 1.4211e-13 | -0.028923 | -6.4092e-05 | -0.0036647 | -0.0099547 | 0.0080272 | -0.0099192 | -0.0040121 | -0.0016987 | 0.018117 | 0.032408 | 0.01415 | 4.7122 | 4.7815 | 4.6294 | 4.7358 | 4.8311 | 4.9449 | 4.5021 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.032021 | 0.07643 | -0.12752 | 4.5662 | -117.1529 | 4.7763 | 4.6935 | 0.12726 | -117.0576 | -116.9438 | -0.063431 | -121.9462 | 0.088028 | -0.001422 | 0.062009 | -121.8567 | -121.8123 | 4.7999 | 4.8952 | 5.009 | 4.8456 | -117.3866 | 0.006662 | 0.096108 | 0.14052 | 0.14228 | -122.0163
4034.8438 | 122.0947 | -0.036621 | 121.9116 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0030235 | -0.010382 | 0.0084546 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018117 | 0.032194 | 0.013723 | 4.6939 | 4.7632 | 4.6157 | 4.7221 | 4.8082 | 4.9358 | 4.4884 | 0.019362 | 0.087354 | -0.065509 | -0.062004 | 0.027442 | 0.081008 | -0.11836 | 4.525 | -117.1895 | 4.7305 | 4.6523 | 0.12726 | -117.1034 | -116.9759 | -0.08174 | -121.9736 | 0.055983 | -0.028888 | 0.052852 | -121.8842 | -121.8306 | 4.7587 | 4.8449 | 4.9724 | 4.7998 | -117.4232 | -0.025383 | 0.064063 | 0.11763 | 0.12398 | -122.03
4036.625 | 122.0535 | -0.054932 | 121.9162 | 1.4211e-13 | -0.028709 | 0.00014951 | -0.0034509 | -0.0099547 | 0.008241 | -0.02518 | -0.0042257 | -0.0019123 | 0.018331 | 0.032194 | 0.013723 | 4.7305 | 4.8044 | 4.6569 | 4.7541 | 4.8403 | 4.9724 | 4.525 | 0.02852 | 0.091933 | -0.06093 | -0.057425 | 0.041178 | 0.081008 | -0.11836 | 4.58 | -117.1621 | 4.7855 | 4.7118 | 0.13183 | -117.0759 | -116.9438 | -0.063429 | -121.9736 | 0.083452 | -0.005998 | 0.057431 | -121.875 | -121.8352 | 4.8091 | 4.8952 | 5.0273 | 4.8593 | -117.3912 | -0.002493 | 0.09611 | 0.13594 | 0.14686 | -122.0346
4038.3281 | 122.081 | -0.050354 | 121.9025 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0034509 | -0.010168 | 0.0080272 | -0.01755 | -0.0042257 | -0.0016987 | 0.018117 | 0.032408 | 0.013723 | 4.7443 | 4.8044 | 4.6614 | 4.7633 | 4.8403 | 4.977 | 4.5342 | 0.033099 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.081008 | -0.12294 | 4.5845 | -117.1392 | 4.7946 | 4.7118 | 0.12725 | -117.0622 | -116.9255 | -0.072585 | -121.9645 | 0.083453 | -0.005997 | 0.066588 | -121.8659 | -121.8215 | 4.8136 | 4.8906 | 5.0273 | 4.8547 | -117.3683 | -0.01165 | 0.086954 | 0.13136 | 0.13771 | -122.0254
4040.0938 | 121.9528 | -0.11444 | 121.9345 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0034509 | -0.010382 | 0.0084546 | -0.02518 | -0.0042257 | -0.0016987 | 0.018758 | 0.032408 | 0.013937 | 4.7443 | 4.8135 | 4.6614 | 4.7679 | 4.854 | 4.977 | 4.5388 | 0.02852 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.11836 | 4.6532 | -117.1666 | 4.8587 | 4.7759 | 0.12268 | -117.0805 | -116.9575 | -0.00392 | -121.9965 | 0.14296 | 0.05809 | 0.06201 | -121.8979 | -121.8581 | 4.8823 | 4.9685 | 5.0914 | 4.928 | -117.3957 | 0.052437 | 0.15104 | 0.19087 | 0.2018 | -122.0529
4041.875 | 122.0444 | -0.054932 | 121.8979 | 1.4211e-13 | -0.028709 | 0.00057691 | -0.0032373 | -0.0097409 | 0.0084546 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018117 | 0.032408 | 0.013509 | 4.7397 | 4.8044 | 4.6477 | 4.7496 | 4.8449 | 4.9724 | 4.5296 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.11836 | 4.5845 | -117.1483 | 4.7946 | 4.7026 | 0.1181 | -117.053 | -116.9255 | -0.063429 | -121.9599 | 0.078873 | -0.005998 | 0.057431 | -121.8567 | -121.8215 | 4.8045 | 4.8998 | 5.0273 | 4.8593 | -117.3683 | -0.007072 | 0.09611 | 0.13136 | 0.13771 | -122.0162
4043.625 | 121.962 | -0.10529 | 121.962 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0034509 | -0.0099547 | 0.0084546 | -0.01755 | -0.0040121 | -0.0016987 | 0.018545 | 0.032408 | 0.013509 | 4.7259 | 4.8044 | 4.6569 | 4.7587 | 4.8449 | 4.9724 | 4.5296 | 0.02852 | 0.087354 | -0.056351 | -0.057425 | 0.027442 | 0.07643 | -0.11836 | 4.6349 | -117.2033 | 4.8312 | 4.7621 | 0.12725 | -117.1171 | -116.9896 | -0.013075 | -122.0194 | 0.13381 | 0.048935 | 0.06201 | -121.9345 | -121.8855 | 4.864 | 4.9501 | 5.0777 | 4.9096 | -117.4324 | 0.047861 | 0.13273 | 0.18172 | 0.19264 | -122.0803
4045.3438 | 122.0123 | -0.09613 | 121.9482 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0034509 | -0.010168 | 0.0084546 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.032408 | 0.013937 | 4.7443 | 4.7998 | 4.6614 | 4.7587 | 4.8403 | 4.9678 | 4.5342 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.027442 | 0.07643 | -0.11836 | 4.6303 | -117.1895 | 4.8404 | 4.7576 | 0.12725 | -117.108 | -116.9804 | -0.022231 | -122.0057 | 0.12007 | 0.039779 | 0.06201 | -121.9208 | -121.8718 | 4.8548 | 4.9364 | 5.0639 | 4.8959 | -117.4141 | 0.038705 | 0.12357 | 0.17256 | 0.18348 | -122.0666
4047.1094 | 122.0581 | -0.054932 | 121.9162 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0042257 | -0.0016987 | 0.017904 | 0.032408 | 0.01415 | 4.7259 | 4.7906 | 4.6431 | 4.7404 | 4.8403 | 4.9632 | 4.525 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.58 | -117.1758 | 4.7809 | 4.6981 | 0.1181 | -117.0759 | -116.953 | -0.068007 | -121.9782 | 0.083452 | -0.005998 | 0.062009 | -121.8796 | -121.8443 | 4.7953 | 4.8952 | 5.0182 | 4.8456 | -117.3912 | -0.007072 | 0.091532 | 0.12678 | 0.13771 | -122.0391
4048.8125 | 122.0398 | -0.07782 | 121.907 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0034509 | -0.010168 | 0.0084546 | -0.0022892 | -0.0037985 | -0.0016987 | 0.018331 | 0.032408 | 0.013723 | 4.7259 | 4.7906 | 4.6385 | 4.7404 | 4.8311 | 4.9541 | 4.5113 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.12294 | 4.5891 | -117.1666 | 4.8038 | 4.7164 | 0.12726 | -117.0759 | -116.953 | -0.045119 | -121.9736 | 0.10634 | 0.01689 | 0.062009 | -121.875 | -121.8352 | 4.8182 | 4.9089 | 5.0319 | 4.8684 | -117.3958 | 0.011238 | 0.10984 | 0.14967 | 0.1606 | -122.03
4050.5781 | 122.049 | -0.059509 | 121.9208 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0030235 | -0.0097409 | 0.0084546 | -0.01755 | -0.0044395 | -0.0019123 | 0.018545 | 0.032622 | 0.013723 | 4.7122 | 4.7723 | 4.6294 | 4.7267 | 4.8128 | 4.9403 | 4.4976 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.041178 | 0.081008 | -0.12294 | 4.5571 | -117.1941 | 4.7717 | 4.6889 | 0.13184 | -117.108 | -116.9804 | -0.06343 | -121.9828 | 0.078871 | -0.001421 | 0.062009 | -121.8796 | -121.8398 | 4.7862 | 4.8723 | 4.9999 | 4.8318 | -117.4232 | -0.002495 | 0.10069 | 0.14052 | 0.14686 | -122.0437
4052.3594 | 122.0947 | -0.064087 | 121.9025 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0034509 | -0.0095273 | 0.0084546 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018331 | 0.032408 | 0.013509 | 4.7122 | 4.7677 | 4.6248 | 4.7175 | 4.8128 | 4.9358 | 4.493 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.5571 | -117.185 | 4.7763 | 4.6889 | 0.13184 | -117.0897 | -116.9667 | -0.058852 | -121.9645 | 0.083449 | 0.007736 | 0.066588 | -121.8659 | -121.8306 | 4.7816 | 4.8769 | 4.9998 | 4.8318 | -117.4095 | 0.002083 | 0.10069 | 0.13594 | 0.14686 | -122.0254
4054.0625 | 122.0718 | -0.068665 | 121.907 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0032373 | -0.010168 | 0.008241 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018331 | 0.032408 | 0.013937 | 4.7031 | 4.754 | 4.6157 | 4.7129 | 4.8037 | 4.922 | 4.4884 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.0366 | 0.081008 | -0.11836 | 4.5571 | -117.1941 | 4.7717 | 4.6843 | 0.12726 | -117.1034 | -116.985 | -0.049696 | -121.9645 | 0.092606 | 0.012314 | 0.06201 | -121.8704 | -121.826 | 4.7816 | 4.8723 | 4.9907 | 4.8227 | -117.4186 | 0.01124 | 0.10526 | 0.14967 | 0.15602 | -122.0254
4055.8438 | 122.0398 | -0.07782 | 121.9254 | 1.4211e-13 | -0.028495 | 0.00057691 | -0.0034509 | -0.010168 | 0.0086682 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.032408 | 0.013509 | 4.6985 | 4.7586 | 4.6157 | 4.7129 | 4.8128 | 4.9312 | 4.4884 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.032021 | 0.07643 | -0.12752 | 4.5662 | -117.2124 | 4.7763 | 4.6935 | 0.12726 | -117.1125 | -116.9942 | -0.049698 | -121.9828 | 0.10634 | 0.01689 | 0.066588 | -121.8933 | -121.8489 | 4.7907 | 4.8906 | 5.009 | 4.8364 | -117.437 | 0.020395 | 0.10984 | 0.15425 | 0.16517 | -122.0529
4057.5625 | 122.0398 | -0.07782 | 121.9391 | 1.4211e-13 | -0.028709 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0084546 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018331 | 0.032408 | 0.013937 | 4.6893 | 4.7403 | 4.6065 | 4.7038 | 4.7853 | 4.9083 | 4.4838 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.032021 | 0.07643 | -0.11836 | 4.5616 | -117.2353 | 4.7671 | 4.6843 | 0.12268 | -117.1538 | -117.0308 | -0.040541 | -122.0011 | 0.10634 | 0.01689 | 0.057431 | -121.9071 | -121.8627 | 4.7816 | 4.8632 | 4.9861 | 4.8181 | -117.4553 | 0.015816 | 0.10984 | 0.15425 | 0.16517 | -122.0574
4059.3281 | 122.1085 | -0.068665 | 121.9025 | 1.4211e-13 | -0.028495 | 0.00057691 | -0.0032373 | -0.0099547 | 0.0084546 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018117 | 0.032194 | 0.013723 | 4.6939 | 4.7494 | 4.6065 | 4.6992 | 4.8037 | 4.9129 | 4.4884 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.032021 | 0.081008 | -0.12294 | 4.5571 | -117.2033 | 4.7626 | 4.6752 | 0.1181 | -117.0988 | -116.9896 | -0.054274 | -121.9645 | 0.097185 | 0.003156 | 0.05743 | -121.8704 | -121.8215 | 4.7679 | 4.8723 | 4.9815 | 4.8181 | -117.4141 | 0.006661 | 0.10069 | 0.14967 | 0.14686 | -122.0254
4061.1094 | 121.9711 | -0.10071 | 121.9299 | 1.4211e-13 | -0.028709 | 0.00014951 | -0.0034509 | -0.0097409 | 0.0086682 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013723 | 4.6985 | 4.7448 | 4.6111 | 4.7038 | 4.7853 | 4.922 | 4.493 | 0.033099 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.12294 | 4.5937 | -117.2262 | 4.7992 | 4.7118 | 0.1181 | -117.1446 | -117.0079 | -0.022231 | -121.9965 | 0.13381 | 0.044357 | 0.066588 | -121.8933 | -121.8535 | 4.8045 | 4.886 | 5.0227 | 4.8455 | -117.437 | 0.034126 | 0.13731 | 0.17714 | 0.18806 | -122.0529
4062.875 | 121.9666 | -0.10529 | 121.9711 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.032408 | 0.013937 | 4.6939 | 4.7494 | 4.6019 | 4.6992 | 4.7853 | 4.9083 | 4.4838 | 0.023941 | 0.096512 | -0.056351 | -0.057425 | 0.027442 | 0.07643 | -0.12752 | 4.5891 | -117.2719 | 4.7992 | 4.7072 | 0.1181 | -117.1858 | -117.0628 | -0.022232 | -122.0286 | 0.12923 | 0.048935 | 0.071167 | -121.9437 | -121.8947 | 4.8045 | 4.8906 | 5.0136 | 4.8547 | -117.4873 | 0.047861 | 0.13273 | 0.18172 | 0.2018 | -122.0986
4064.5781 | 121.962 | -0.091553 | 121.9711 | 1.4211e-13 | -0.028495 | -6.4092e-05 | -0.0032373 | -0.010168 | 0.008241 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.031981 | 0.013723 | 4.6939 | 4.7494 | 4.6111 | 4.7129 | 4.7945 | 4.9174 | 4.4884 | 0.02852 | 0.082776 | -0.056351 | -0.057425 | 0.027442 | 0.07643 | -0.12294 | 4.5799 | -117.2582 | 4.7854 | 4.7026 | 0.12268 | -117.1766 | -117.0537 | -0.031386 | -122.0286 | 0.12007 | 0.035202 | 0.066588 | -121.9437 | -121.8947 | 4.8045 | 4.886 | 5.009 | 4.841 | -117.4827 | 0.034128 | 0.11899 | 0.16798 | 0.17433 | -122.0941
4066.3438 | 122.0444 | -0.082397 | 121.9482 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0032373 | -0.0099547 | 0.008241 | -0.01755 | -0.0042257 | -0.0019123 | 0.017904 | 0.032408 | 0.013723 | 4.6939 | 4.7586 | 4.6111 | 4.7083 | 4.7945 | 4.9129 | 4.4976 | 0.02852 | 0.073618 | -0.056351 | -0.066582 | 0.032021 | 0.085587 | -0.12294 | 4.5799 | -117.2399 | 4.7763 | 4.6935 | 0.11352 | -117.1537 | -117.0354 | -0.040542 | -122.0148 | 0.11092 | 0.026046 | 0.066588 | -121.9162 | -121.8627 | 4.7907 | 4.8769 | 4.9953 | 4.841 | -117.4507 | 0.015815 | 0.11442 | 0.16798 | 0.15602 | -122.0712
4068.0469 | 122.0215 | -0.07782 | 121.9666 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018117 | 0.032408 | 0.013937 | 4.6939 | 4.7494 | 4.6065 | 4.7038 | 4.7899 | 4.9083 | 4.4884 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.032021 | 0.07643 | -0.11836 | 4.5662 | -117.2628 | 4.7717 | 4.6843 | 0.1181 | -117.1766 | -117.0583 | -0.040541 | -122.0331 | 0.10634 | 0.021469 | 0.06201 | -121.9345 | -121.8901 | 4.7816 | 4.8677 | 4.9861 | 4.8272 | -117.4782 | 0.011238 | 0.10984 | 0.15425 | 0.16517 | -122.0849
4069.8125 | 121.9803 | -0.10529 | 121.9666 | 1.4211e-13 | -0.028495 | 0.00014951 | -0.0030235 | -0.0099547 | 0.008241 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018117 | 0.032194 | 0.013937 | 4.465 | 4.5113 | 4.3822 | 4.4794 | 4.561 | 4.6885 | 4.2594 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 4.3647 | -117.4871 | 4.5703 | 4.4874 | 0.12272 | -117.4056 | -117.278 | -0.017653 | -122.0331 | 0.12923 | 0.048935 | 0.066588 | -121.93 | -121.8947 | 4.5847 | 4.6663 | 4.7938 | 4.6166 | -117.7071 | 0.038704 | 0.14189 | 0.17714 | 0.18806 | -122.0895
4071.5781 | 121.9803 | -0.10986 | 121.9711 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0034509 | -0.010382 | 0.008241 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018331 | 0.032194 | 0.013937 | 4.4924 | 4.5388 | 4.4005 | 4.5023 | 4.5839 | 4.7114 | 4.2732 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.11836 | 4.383 | -117.4688 | 4.6023 | 4.5103 | 0.12729 | -117.3873 | -117.2597 | -0.008498 | -122.0286 | 0.1338 | 0.048933 | 0.057431 | -121.9345 | -121.8947 | 4.6122 | 4.6937 | 4.8213 | 4.6487 | -117.6979 | 0.052438 | 0.14646 | 0.18629 | 0.19264 | -122.0895
4073.2812 | 122.0901 | -0.036621 | 121.9162 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0032373 | -0.010382 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018117 | 0.032408 | 0.013937 | 4.1994 | 4.232 | 4.1212 | 4.2185 | 4.3091 | 4.4321 | 3.9984 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 4.0351 | -117.6977 | 4.2361 | 4.1578 | 0.12275 | -117.6071 | -117.4841 | -0.086318 | -121.9782 | 0.065141 | -0.028888 | 0.05743 | -121.8842 | -121.8443 | 4.2551 | 4.3457 | 4.4687 | 4.2687 | -117.9178 | -0.025383 | 0.068642 | 0.10847 | 0.1194 | -122.0391
4075.0469 | 122.1176 | -0.050354 | 121.9437 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0034509 | -0.0099547 | 0.0080272 | -0.01755 | -0.0042257 | -0.0019123 | 0.018117 | 0.032622 | 0.013723 | 4.0529 | 4.0489 | 3.961 | 4.0582 | 4.1443 | 4.2719 | 3.8428 | 0.023941 | 0.087354 | -0.065509 | -0.062004 | 0.0366 | 0.067272 | -0.12294 | 3.8931 | -117.8854 | 4.1033 | 4.0113 | 0.1182 | -117.7994 | -117.6718 | -0.072585 | -122.0057 | 0.074295 | -0.015155 | 0.05743 | -121.9071 | -121.8764 | 4.1086 | 4.1946 | 4.3222 | 4.0992 | -118.1009 | -0.01165 | 0.086954 | 0.11763 | 0.13771 | -122.0666
4076.8125 | 122.1039 | -0.041199 | 121.9574 | 1.4211e-13 | -0.028923 | -6.4092e-05 | -0.0030235 | -0.0099547 | 0.0086682 | -0.01755 | -0.0044395 | -0.0014849 | 0.018331 | 0.032194 | 0.013509 | 4.0346 | 4.0352 | 3.9426 | 4.0491 | 4.1305 | 4.2581 | 3.829 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.11378 | 3.8702 | -117.9083 | 4.0758 | 3.9838 | 0.11362 | -117.8268 | -117.6993 | -0.072583 | -122.0194 | 0.06514 | -0.019731 | 0.052852 | -121.9208 | -121.8855 | 4.0903 | 4.1717 | 4.2993 | 4.0764 | -118.1284 | -0.020805 | 0.077799 | 0.11305 | 0.12398 | -122.0712
4078.5781 | 122.081 | -0.064087 | 121.9345 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0030235 | -0.0099547 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.032408 | 0.013723 | 4.0483 | 4.0443 | 3.961 | 4.0491 | 4.1397 | 4.2673 | 3.8428 | 0.023941 | 0.096512 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.12294 | 3.9069 | -117.8854 | 4.1124 | 4.025 | 0.1182 | -117.7948 | -117.6672 | -0.058852 | -122.0011 | 0.088028 | 0.003157 | 0.062009 | -121.8979 | -121.8581 | 4.1131 | 4.2038 | 4.3314 | 4.1084 | -118.0917 | -0.002495 | 0.10069 | 0.14052 | 0.1606 | -122.0574
4080.375 | 121.994 | -0.091553 | 121.9666 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0030235 | -0.0097409 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013509 | 4.0758 | 4.0764 | 3.9839 | 4.0857 | 4.1672 | 4.2993 | 3.8794 | 0.019362 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.081008 | -0.11836 | 3.971 | -117.8809 | 4.1674 | 4.0754 | 0.10445 | -117.7994 | -117.6672 | -0.026808 | -122.0331 | 0.11091 | 0.030623 | 0.057431 | -121.9345 | -121.8855 | 4.1772 | 4.2587 | 4.3909 | 4.1679 | -118.0872 | 0.024971 | 0.12357 | 0.17256 | 0.17891 | -122.0849
4082.1562 | 122.1451 | -0.054932 | 121.9345 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0036647 | -0.010168 | 0.008241 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018117 | 0.032408 | 0.01415 | 4.085 | 4.0809 | 3.9976 | 4.0903 | 4.1855 | 4.3085 | 3.8794 | 0.019362 | 0.087354 | -0.051772 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 3.9343 | -117.8442 | 4.1399 | 4.0525 | 0.11819 | -117.749 | -117.626 | -0.063429 | -121.9965 | 0.074294 | 0.00316 | 0.066589 | -121.8979 | -121.8627 | 4.1452 | 4.2404 | 4.3634 | 4.1359 | -118.0551 | -0.007072 | 0.091532 | 0.12678 | 0.14229 | -122.0529
4083.8594 | 122.0856 | -0.064087 | 121.9299 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0030235 | -0.0097409 | 0.0084546 | -0.0022892 | -0.0046531 | -0.0014849 | 0.018117 | 0.032622 | 0.013509 | 4.1124 | 4.1176 | 4.0251 | 4.1269 | 4.2084 | 4.336 | 3.9023 | 0.019362 | 0.082776 | -0.056351 | -0.071161 | 0.0366 | 0.07643 | -0.12752 | 3.9664 | -117.803 | 4.1765 | 4.0891 | 0.12277 | -117.7215 | -117.594 | -0.063431 | -122.0011 | 0.083449 | 0.007736 | 0.071167 | -121.8933 | -121.8535 | 4.191 | 4.2725 | 4.4001 | 4.1817 | -118.0276 | -0.007074 | 0.10069 | 0.14052 | 0.14686 | -122.0574
4085.625 | 121.9666 | -0.11902 | 121.9757 | 1.4211e-13 | -0.028495 | 0.00036331 | -0.0032373 | -0.010168 | 0.008241 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018117 | 0.032194 | 0.013509 | 4.1308 | 4.145 | 4.0525 | 4.1544 | 4.2267 | 4.3543 | 3.9435 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.11378 | 4.0625 | -117.8213 | 4.2498 | 4.1715 | 0.10902 | -117.749 | -117.6214 | 0.005237 | -122.0423 | 0.14296 | 0.062668 | 0.057431 | -121.9391 | -121.8993 | 4.2734 | 4.3457 | 4.4733 | 4.2641 | -118.0322 | 0.052437 | 0.15562 | 0.19545 | 0.2018 | -122.0895
4087.3906 | 121.994 | -0.10529 | 121.9803 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018545 | 0.032408 | 0.013723 | 4.1399 | 4.145 | 4.0525 | 4.1452 | 4.2359 | 4.3543 | 3.9343 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.081008 | -0.11836 | 4.0396 | -117.8351 | 4.2452 | 4.1578 | 0.11818 | -117.7444 | -117.626 | -0.013075 | -122.0423 | 0.12923 | 0.044356 | 0.057431 | -121.9437 | -121.8993 | 4.2505 | 4.3412 | 4.4596 | 4.2503 | -118.0459 | 0.043282 | 0.14189 | 0.18629 | 0.19264 | -122.0986
4089.0938 | 122.1451 | -0.064087 | 121.9574 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0036647 | -0.010168 | 0.008241 | -0.01755 | -0.0042257 | -0.0016987 | 0.018331 | 0.032408 | 0.013509 | 4.1536 | 4.1588 | 4.0663 | 4.1589 | 4.2542 | 4.3772 | 3.9572 | 0.02852 | 0.091933 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 4.0213 | -117.7985 | 4.2177 | 4.1303 | 0.10902 | -117.7032 | -117.5802 | -0.054274 | -122.0194 | 0.092607 | 0.003157 | 0.057431 | -121.9208 | -121.8855 | 4.223 | 4.3183 | 4.4413 | 4.2229 | -118.0002 | 0.002083 | 0.10069 | 0.13594 | 0.15602 | -122.0758
4090.875 | 122.0901 | -0.054932 | 121.9299 | 1.4211e-13 | -0.028709 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013509 | 4.2773 | 4.3007 | 4.1853 | 4.2734 | 4.3641 | 4.4825 | 4.0671 | 0.033099 | 0.091933 | -0.056351 | -0.062004 | 0.027442 | 0.071851 | -0.12752 | 4.1221 | -117.6565 | 4.3322 | 4.2402 | 0.11816 | -117.5659 | -117.4475 | -0.072586 | -121.9919 | 0.088031 | -0.001419 | 0.071167 | -121.9025 | -121.8581 | 4.3283 | 4.419 | 4.5374 | 4.3556 | -117.8628 | -0.007072 | 0.082374 | 0.12678 | 0.14686 | -122.0574
4092.6094 | 122.0993 | -0.059509 | 121.9162 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018117 | 0.032408 | 0.013296 | 4.291 | 4.3236 | 4.2082 | 4.2963 | 4.3915 | 4.5008 | 4.0854 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.032021 | 0.071851 | -0.11836 | 4.145 | -117.6199 | 4.3505 | 4.2677 | 0.12274 | -117.5247 | -117.4154 | -0.058852 | -121.9736 | 0.08345 | 0.003158 | 0.06201 | -121.8842 | -121.8443 | 4.3558 | 4.4511 | 4.5603 | 4.3831 | -117.8308 | 0.002084 | 0.09153 | 0.13136 | 0.14228 | -122.0346
4094.375 | 121.9986 | -0.1236 | 121.9666 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0030235 | -0.010168 | 0.0080272 | -0.0022892 | -0.0042257 | -0.0019123 | 0.018331 | 0.032408 | 0.013509 | 4.2589 | 4.2824 | 4.1807 | 4.2642 | 4.3549 | 4.4733 | 4.0534 | 0.02852 | 0.087354 | -0.051772 | -0.062004 | 0.0366 | 0.071851 | -0.12752 | 4.177 | -117.7023 | 4.3825 | 4.3043 | 0.12732 | -117.6116 | -117.4932 | -0.003922 | -122.0286 | 0.15212 | 0.071824 | 0.075746 | -121.93 | -121.8947 | 4.3878 | 4.4785 | 4.5969 | 4.406 | -117.9132 | 0.061592 | 0.1602 | 0.19545 | 0.21095 | -122.0941
4096.0781 | 121.9894 | -0.086975 | 121.9574 | 1.4211e-13 | -0.028923 | 0.00014951 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018331 | 0.032408 | 0.013509 | 4.2635 | 4.287 | 4.1761 | 4.2688 | 4.3503 | 4.4733 | 4.0626 | 0.02852 | 0.091933 | -0.06093 | -0.057425 | 0.032021 | 0.081008 | -0.11836 | 4.1495 | -117.6886 | 4.3505 | 4.2631 | 0.11358 | -117.6071 | -117.4841 | -0.031386 | -122.0148 | 0.1155 | 0.026045 | 0.057431 | -121.9254 | -121.8764 | 4.3558 | 4.4373 | 4.5603 | 4.374 | -117.8948 | 0.02955 | 0.119 | 0.16798 | 0.17891 | -122.0758
4097.8438 | 121.9894 | -0.10529 | 121.994 | 1.4211e-13 | -0.029136 | 0.00014951 | -0.0036647 | -0.010168 | 0.008241 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018117 | 0.032622 | 0.013509 | 4.2589 | 4.2824 | 4.1716 | 4.2642 | 4.3458 | 4.4733 | 4.058 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.0366 | 0.081008 | -0.11836 | 4.1633 | -117.7298 | 4.3642 | 4.2768 | 0.11359 | -117.6483 | -117.5207 | -0.013075 | -122.0652 | 0.13381 | 0.044356 | 0.057431 | -121.9574 | -121.913 | 4.3695 | 4.451 | 4.5786 | 4.3877 | -117.936 | 0.034125 | 0.14189 | 0.18629 | 0.18348 | -122.1124
4099.5469 | 122.0627 | -0.07782 | 121.9528 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0034509 | -0.0099547 | 0.008241 | -0.01755 | -0.0044395 | -0.0014849 | 0.018331 | 0.032835 | 0.013937 | 4.2681 | 4.3007 | 4.1807 | 4.278 | 4.3641 | 4.4871 | 4.0671 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.0366 | 0.081008 | -0.1321 | 4.145 | -117.6748 | 4.3459 | 4.2585 | 0.11358 | -117.5887 | -117.4658 | -0.054277 | -122.024 | 0.10176 | 0.012311 | 0.066588 | -121.9162 | -121.8718 | 4.3558 | 4.4419 | 4.5649 | 4.3785 | -117.8857 | 0.006659 | 0.11442 | 0.15883 | 0.16517 | -122.0849
4101.3281 | 122.113 | -0.059509 | 121.9574 | 1.4211e-13 | -0.028709 | 0.00057691 | -0.0032373 | -0.0099547 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018331 | 0.032194 | 0.013937 | 4.2818 | 4.2961 | 4.1899 | 4.278 | 4.3641 | 4.4825 | 4.0671 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.07643 | -0.11836 | 4.1266 | -117.6794 | 4.3413 | 4.2494 | 0.12274 | -117.5933 | -117.4749 | -0.058852 | -122.0194 | 0.08345 | -0.001421 | 0.057431 | -121.9208 | -121.881 | 4.3375 | 4.4236 | 4.542 | 4.3556 | -117.8903 | -0.002495 | 0.096109 | 0.13594 | 0.14686 | -122.0758
4103.0938 | 121.9894 | -0.11902 | 121.9711 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0028099 | -0.010168 | 0.008241 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.032622 | 0.013723 | 4.2818 | 4.3144 | 4.1899 | 4.2871 | 4.3687 | 4.4962 | 4.0717 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.12294 | 4.1907 | -117.684 | 4.4009 | 4.3089 | 0.11816 | -117.6025 | -117.4749 | -0.00392 | -122.0377 | 0.14754 | 0.058089 | 0.062009 | -121.9391 | -121.8947 | 4.4062 | 4.4877 | 4.6152 | 4.4335 | -117.8994 | 0.052437 | 0.15104 | 0.19545 | 0.20637 | -122.0941
4104.875 | 121.9849 | -0.09613 | 121.9894 | 1.4211e-13 | -0.029136 | 0.00057691 | -0.0034509 | -0.0099547 | 0.0080272 | -0.0099192 | -0.0048667 | -0.0016987 | 0.018331 | 0.032408 | 0.013723 | 4.3093 | 4.3328 | 4.2082 | 4.3009 | 4.3961 | 4.51 | 4.0992 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.062694 | -0.11836 | 4.1953 | -117.6886 | 4.4054 | 4.3043 | 0.109 | -117.5933 | -117.4795 | -0.022231 | -122.056 | 0.12465 | 0.039779 | 0.06201 | -121.9528 | -121.9267 | 4.397 | 4.4923 | 4.6061 | 4.4289 | -117.8903 | 0.029548 | 0.13273 | 0.15882 | 0.18348 | -122.1078
4106.5938 | 122.0627 | -0.073242 | 121.962 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0030235 | -0.010168 | 0.008241 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018117 | 0.032622 | 0.01415 | 4.3139 | 4.3465 | 4.2219 | 4.3192 | 4.4007 | 4.5191 | 4.1038 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.12752 | 4.177 | -117.6428 | 4.3871 | 4.2952 | 0.11816 | -117.5613 | -117.4429 | -0.054276 | -122.024 | 0.097183 | 0.016891 | 0.071167 | -121.9254 | -121.8901 | 4.3924 | 4.4739 | 4.5924 | 4.4197 | -117.8582 | 0.011238 | 0.10984 | 0.14509 | 0.15602 | -122.0895
4108.375 | 122.0078 | -0.086975 | 121.9757 | 1.4211e-13 | -0.029136 | 0.00057691 | -0.0032373 | -0.010382 | 0.0080272 | -0.01755 | -0.0044395 | -0.0012713 | 0.018331 | 0.032622 | 0.013296 | 4.3322 | 4.3602 | 4.2357 | 4.3283 | 4.4144 | 4.542 | 4.1175 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.032021 | 0.07643 | -0.11836 | 4.2045 | -117.6474 | 4.4192 | 4.3226 | 0.11816 | -117.5613 | -117.4337 | -0.031386 | -122.0331 | 0.1155 | 0.026045 | 0.057431 | -121.9437 | -121.8993 | 4.4153 | 4.5014 | 4.629 | 4.4472 | -117.8582 | 0.02955 | 0.119 | 0.1634 | 0.17433 | -122.0941
4110.0938 | 121.9711 | -0.091553 | 121.9574 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0030235 | -0.010382 | 0.0080272 | -0.01755 | -0.0042257 | -0.0016987 | 0.018117 | 0.032622 | 0.013509 | 4.323 | 4.3511 | 4.2265 | 4.3192 | 4.4007 | 4.5283 | 4.1129 | 0.02852 | 0.087354 | -0.056351 | -0.057425 | 0.032021 | 0.081008 | -0.11378 | 4.2045 | -117.6382 | 4.4146 | 4.3181 | 0.11358 | -117.5567 | -117.4291 | -0.022229 | -122.0148 | 0.12007 | 0.035202 | 0.057431 | -121.9254 | -121.8764 | 4.4107 | 4.4923 | 4.6198 | 4.4426 | -117.8445 | 0.034128 | 0.12357 | 0.17256 | 0.17891 | -122.0712
4111.875 | 122.1039 | -0.07782 | 121.9437 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0036647 | -0.010382 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013723 | 4.3276 | 4.3602 | 4.2402 | 4.3283 | 4.4144 | 4.5374 | 4.1267 | 0.033099 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 4.2045 | -117.6153 | 4.4054 | 4.3181 | 0.11358 | -117.5292 | -117.4062 | -0.045119 | -122.0057 | 0.11092 | 0.021469 | 0.066588 | -121.9071 | -121.8672 | 4.4062 | 4.4923 | 4.6152 | 4.4381 | -117.817 | 0.015816 | 0.11442 | 0.15425 | 0.1606 | -122.0666
4113.5781 | 122.0398 | -0.10529 | 121.9803 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0034509 | -0.010168 | 0.008241 | -0.01755 | -0.0042257 | -0.0016987 | 0.018117 | 0.032622 | 0.013723 | 4.3368 | 4.3557 | 4.2494 | 4.3375 | 4.4236 | 4.542 | 4.1267 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 4.2319 | -117.6428 | 4.4421 | 4.3547 | 0.12273 | -117.5567 | -117.4383 | -0.017653 | -122.0469 | 0.12923 | 0.039777 | 0.05743 | -121.9437 | -121.9084 | 4.4428 | 4.5289 | 4.6473 | 4.4609 | -117.8536 | 0.038704 | 0.14189 | 0.17714 | 0.19264 | -122.1032
4115.3438 | 121.994 | -0.10529 | 121.9894 | 1.4211e-13 | -0.028709 | 0.00014951 | -0.0032373 | -0.0099547 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.018117 | 0.032622 | 0.013509 | 4.3414 | 4.3602 | 4.2448 | 4.3329 | 4.419 | 4.542 | 4.1267 | 0.023941 | 0.087354 | -0.065509 | -0.057425 | 0.041178 | 0.07643 | -0.11836 | 4.2319 | -117.6565 | 4.4466 | 4.3501 | 0.11815 | -117.5704 | -117.4474 | -0.013075 | -122.0469 | 0.12923 | 0.039777 | 0.052852 | -121.9483 | -121.913 | 4.4382 | 4.5243 | 4.6473 | 4.4655 | -117.8628 | 0.047861 | 0.14646 | 0.18172 | 0.19264 | -122.1078
4117.125 | 122.0123 | -0.091553 | 121.9803 | 1.4211e-13 | -0.029136 | 0.00014951 | -0.0034509 | -0.0099547 | 0.008241 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018117 | 0.032835 | 0.013937 | 4.3459 | 4.374 | 4.2585 | 4.3421 | 4.4373 | 4.5603 | 4.1404 | 0.037677 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.071851 | -0.12294 | 4.2319 | -117.6382 | 4.4375 | 4.3501 | 0.11815 | -117.5429 | -117.42 | -0.031386 | -122.0469 | 0.12923 | 0.030623 | 0.062009 | -121.9391 | -121.9084 | 4.4336 | 4.5289 | 4.6519 | 4.4655 | -117.8399 | 0.024971 | 0.13273 | 0.1634 | 0.17891 | -122.1032
4118.8906 | 122.0947 | -0.054932 | 121.9162 | 1.4211e-13 | -0.02935 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.01755 | -0.0042257 | -0.0012713 | 0.017904 | 0.032408 | 0.013296 | 4.3597 | 4.3877 | 4.2723 | 4.3512 | 4.4465 | 4.5649 | 4.1541 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.041178 | 0.071851 | -0.1321 | 4.2091 | -117.565 | 4.4146 | 4.3272 | 0.11815 | -117.4697 | -117.3513 | -0.077165 | -121.9828 | 0.083452 | -0.005998 | 0.071167 | -121.875 | -121.8443 | 4.4062 | 4.5014 | 4.6198 | 4.4426 | -117.7621 | -0.01165 | 0.09611 | 0.12678 | 0.13313 | -122.0483
4120.6406 | 122.0032 | -0.11444 | 121.9711 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0036647 | -0.010382 | 0.0080272 | -0.01755 | -0.0042257 | -0.0014849 | 0.018117 | 0.032622 | 0.013723 | 4.3734 | 4.3923 | 4.2814 | 4.3695 | 4.4602 | 4.5786 | 4.1633 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 4.2777 | -117.6016 | 4.4878 | 4.3959 | 0.11815 | -117.5109 | -117.3925 | -0.008498 | -122.0377 | 0.14296 | 0.053511 | 0.062009 | -121.93 | -121.8947 | 4.484 | 4.5747 | 4.6931 | 4.5067 | -117.8078 | 0.047859 | 0.15562 | 0.19087 | 0.19722 | -122.0941
4122.3594 | 122.0856 | -0.068665 | 121.9528 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0032373 | -0.0099547 | 0.008241 | -0.01755 | -0.0048667 | -0.0019123 | 0.018331 | 0.032835 | 0.013509 | 4.3871 | 4.406 | 4.2952 | 4.3833 | 4.474 | 4.5924 | 4.1816 | 0.033099 | 0.087354 | -0.056351 | -0.071161 | 0.032021 | 0.07643 | -0.11836 | 4.2503 | -117.5695 | 4.4558 | 4.3638 | 0.11357 | -117.4789 | -117.3605 | -0.049696 | -122.024 | 0.10176 | 0.012314 | 0.06201 | -121.9208 | -121.8764 | 4.4519 | 4.5426 | 4.661 | 4.4747 | -117.7712 | -0.002496 | 0.10069 | 0.1451 | 0.15602 | -122.0712
4124.1094 | 122.1039 | -0.059509 | 121.9345 | 1.4211e-13 | -0.028709 | 0.00014951 | -0.0032373 | -0.0099547 | 0.0078136 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.032194 | 0.013509 | 4.3917 | 4.4152 | 4.2952 | 4.3924 | 4.4785 | 4.5924 | 4.1862 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.081008 | -0.11836 | 4.2457 | -117.5421 | 4.4512 | 4.3547 | 0.10899 | -117.456 | -117.3421 | -0.058852 | -121.9965 | 0.08345 | -0.001421 | 0.057431 | -121.8933 | -121.8535 | 4.4519 | 4.5381 | 4.6519 | 4.4747 | -117.7483 | -0.002495 | 0.10069 | 0.14052 | 0.14228 | -122.0529
4125.875 | 122.1085 | -0.082397 | 121.9162 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0025963 | -0.010168 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0021259 | 0.018331 | 0.032622 | 0.013509 | 4.3414 | 4.3694 | 4.254 | 4.3467 | 4.4373 | 4.5466 | 4.1404 | 0.023941 | 0.091933 | -0.06093 | -0.057425 | 0.027442 | 0.07643 | -0.12752 | 4.2228 | -117.5695 | 4.4238 | 4.3364 | 0.11357 | -117.4789 | -117.3696 | -0.045121 | -121.9736 | 0.10634 | 0.021467 | 0.066588 | -121.8888 | -121.8398 | 4.4291 | 4.5197 | 4.629 | 4.4518 | -117.7758 | 0.024972 | 0.10984 | 0.15883 | 0.17433 | -122.0437
4127.6094 | 121.994 | -0.10986 | 121.9849 | 1.4211e-13 | -0.028923 | -6.4092e-05 | -0.0032373 | -0.0099547 | 0.0080272 | -0.01755 | -0.0042257 | -0.0016987 | 0.018117 | 0.032622 | 0.013509 | 4.3459 | 4.3786 | 4.2585 | 4.3421 | 4.4419 | 4.5466 | 4.1404 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.027442 | 0.085587 | -0.12294 | 4.2503 | -117.6428 | 4.4558 | 4.3684 | 0.11815 | -117.5429 | -117.4383 | -0.013076 | -122.0423 | 0.1338 | 0.053512 | 0.066588 | -121.9574 | -121.8993 | 4.4519 | 4.5518 | 4.6564 | 4.4884 | -117.8445 | 0.052438 | 0.13731 | 0.19545 | 0.19722 | -122.1078
4129.375 | 121.9666 | -0.09613 | 121.9803 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0032373 | -0.010168 | 0.008241 | -0.02518 | -0.0044395 | -0.0014849 | 0.018545 | 0.032194 | 0.013509 | 4.3505 | 4.3786 | 4.2585 | 4.3604 | 4.4328 | 4.5557 | 4.145 | 0.02852 | 0.091933 | -0.056351 | -0.057425 | 0.032021 | 0.07643 | -0.12294 | 4.2411 | -117.6199 | 4.4466 | 4.3547 | 0.11357 | -117.5475 | -117.4245 | -0.026809 | -122.0377 | 0.12465 | 0.039779 | 0.066588 | -121.9483 | -121.9039 | 4.4565 | 4.5289 | 4.6519 | 4.4747 | -117.8353 | 0.038705 | 0.12815 | 0.17256 | 0.18806 | -122.1032
4131.0781 | 122.0078 | -0.11902 | 121.9757 | 1.4211e-13 | -0.029136 | 0.00057691 | -0.0032373 | -0.010168 | 0.0084546 | -0.01755 | -0.0044395 | -0.0019123 | 0.018331 | 0.032622 | 0.013937 | 4.3597 | 4.3877 | 4.2631 | 4.3558 | 4.4465 | 4.5649 | 4.1541 | 0.033099 | 0.082776 | -0.065509 | -0.062004 | 0.041178 | 0.071851 | -0.12294 | 4.2732 | -117.6199 | 4.4787 | 4.3821 | 0.10899 | -117.5292 | -117.4108 | -0.00392 | -122.0377 | 0.15212 | 0.05351 | 0.05743 | -121.9345 | -121.9039 | 4.4748 | 4.5655 | 4.6839 | 4.5067 | -117.8216 | 0.057015 | 0.1602 | 0.19087 | 0.2018 | -122.0986
4132.8594 | 122.0993 | -0.064087 | 121.9528 | 1.4211e-13 | -0.028709 | 0.00036331 | -0.0036647 | -0.010168 | 0.0080272 | -0.01755 | -0.0042257 | -0.0014849 | 0.018117 | 0.032622 | 0.013723 | 4.3597 | 4.3786 | 4.2677 | 4.3604 | 4.4328 | 4.5695 | 4.1496 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 4.2136 | -117.5924 | 4.4238 | 4.3318 | 0.11815 | -117.5201 | -117.3833 | -0.058852 | -122.0148 | 0.088028 | 0.007736 | 0.066588 | -121.9208 | -121.881 | 4.4245 | 4.4968 | 4.6336 | 4.4426 | -117.8033 | 0.002083 | 0.096108 | 0.13594 | 0.14686 | -122.0758
4134.5625 | 122.1588 | -0.045776 | 121.9345 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0016987 | 0.017904 | 0.032622 | 0.013509 | 4.3688 | 4.4014 | 4.2769 | 4.3695 | 4.4511 | 4.5695 | 4.1587 | 0.033099 | 0.078197 | -0.056351 | -0.066582 | 0.041178 | 0.081008 | -0.12294 | 4.2045 | -117.565 | 4.4146 | 4.3226 | 0.11815 | -117.4834 | -117.365 | -0.077163 | -122.0011 | 0.078875 | -0.010575 | 0.066588 | -121.8933 | -121.8535 | 4.4153 | 4.4969 | 4.6153 | 4.4472 | -117.7758 | -0.020806 | 0.086954 | 0.12678 | 0.12397 | -122.0574
4136.3281 | 122.0627 | -0.068665 | 121.9528 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018331 | 0.032408 | 0.013723 | 4.3734 | 4.4014 | 4.2906 | 4.3741 | 4.4602 | 4.5695 | 4.1587 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.041178 | 0.067272 | -0.12294 | 4.2274 | -117.5787 | 4.4421 | 4.3593 | 0.13188 | -117.4926 | -117.3833 | -0.054274 | -122.0102 | 0.097185 | 0.003156 | 0.05743 | -121.9116 | -121.8855 | 4.4428 | 4.5289 | 4.6381 | 4.4701 | -117.7941 | 0.01124 | 0.10984 | 0.13594 | 0.15144 | -122.0758
4138.0938 | 122.1313 | -0.059509 | 121.9162 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0034509 | -0.010382 | 0.0080272 | -0.0022892 | -0.0042257 | -0.0016987 | 0.017904 | 0.032408 | 0.013723 | 4.3688 | 4.3969 | 4.2769 | 4.365 | 4.4557 | 4.5741 | 4.1633 | 0.02852 | 0.082776 | -0.056351 | -0.066582 | 0.0366 | 0.081008 | -0.1321 | 4.2228 | -117.5512 | 4.4283 | 4.3364 | 0.11357 | -117.4605 | -117.3421 | -0.072588 | -121.9828 | 0.088029 | 0.003158 | 0.075746 | -121.8796 | -121.8352 | 4.4245 | 4.5152 | 4.6336 | 4.4564 | -117.7529 | -0.007073 | 0.096109 | 0.14052 | 0.14228 | -122.0483
4139.875 | 121.9849 | -0.11444 | 121.9849 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0034509 | -0.010168 | 0.0076 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.032408 | 0.013723 | 4.378 | 4.3969 | 4.286 | 4.365 | 4.4557 | 4.5695 | 4.1633 | 0.02852 | 0.096512 | -0.065509 | -0.062004 | 0.045757 | 0.071851 | -0.12752 | 4.2777 | -117.6199 | 4.4924 | 4.4005 | 0.12273 | -117.5292 | -117.4154 | -0.013077 | -122.0469 | 0.14296 | 0.048932 | 0.062009 | -121.9391 | -121.913 | 4.4794 | 4.5701 | 4.6839 | 4.5113 | -117.8216 | 0.052437 | 0.1602 | 0.18629 | 0.21095 | -122.1124
4141.5781 | 122.1039 | -0.050354 | 121.9299 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0030235 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018117 | 0.032408 | 0.013296 | 4.3688 | 4.3923 | 4.2814 | 4.3695 | 4.4419 | 4.5695 | 4.1587 | 0.02852 | 0.091933 | -0.056351 | -0.057425 | 0.041178 | 0.071851 | -0.12294 | 4.2091 | -117.5604 | 4.4192 | 4.3318 | 0.12273 | -117.488 | -117.3605 | -0.072585 | -121.9874 | 0.078874 | -0.005997 | 0.066588 | -121.8888 | -121.8581 | 4.4199 | 4.4923 | 4.6198 | 4.4426 | -117.7712 | -0.007071 | 0.091532 | 0.12221 | 0.14229 | -122.0529
4143.3594 | 122.113 | -0.064087 | 121.9299 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0032373 | -0.010168 | 0.0080272 | -0.0022892 | -0.0042257 | -0.0014849 | 0.018117 | 0.032622 | 0.013723 | 4.3871 | 4.4152 | 4.2998 | 4.3833 | 4.4648 | 4.5878 | 4.1724 | 0.023941 | 0.087354 | -0.065509 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 4.2365 | -117.5466 | 4.4512 | 4.3638 | 0.1273 | -117.4651 | -117.3421 | -0.058852 | -121.9919 | 0.088028 | -0.001422 | 0.05743 | -121.8933 | -121.8535 | 4.4474 | 4.5289 | 4.6519 | 4.4793 | -117.7575 | 0.002083 | 0.10069 | 0.14052 | 0.15144 | -122.0529
4145.1406 | 122.1359 | -0.045776 | 121.9528 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0032373 | -0.010168 | 0.008241 | -0.02518 | -0.0044395 | -0.0014849 | 0.018331 | 0.032622 | 0.013937 | 4.3917 | 4.4243 | 4.3043 | 4.3924 | 4.4785 | 4.5924 | 4.1908 | 0.033099 | 0.087354 | -0.06093 | -0.052847 | 0.032021 | 0.07643 | -0.11836 | 4.2365 | -117.5604 | 4.4375 | 4.3501 | 0.11357 | -117.4743 | -117.3605 | -0.072585 | -122.0057 | 0.078875 | -0.015154 | 0.057431 | -121.9208 | -121.8764 | 4.4382 | 4.5243 | 4.6381 | 4.4701 | -117.7621 | -0.007071 | 0.077797 | 0.12221 | 0.13313 | -122.0712
4146.8438 | 122.0947 | -0.064087 | 121.9162 | 1.4211e-13 | -0.028923 | 0.00036331 | -0.0032373 | -0.0099547 | 0.0078136 | -0.0022892 | -0.0042257 | -0.0016987 | 0.018331 | 0.032408 | 0.013509 | 4.3917 | 4.4243 | 4.3181 | 4.3924 | 4.474 | 4.5924 | 4.1908 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 4.2549 | -117.5238 | 4.4558 | 4.3822 | 0.1273 | -117.4422 | -117.3238 | -0.054274 | -121.9782 | 0.088028 | 0.007736 | 0.06201 | -121.8796 | -121.8443 | 4.4565 | 4.5381 | 4.6565 | 4.4884 | -117.7254 | 0.002083 | 0.10069 | 0.13594 | 0.15144 | -122.0346
4148.6094 | 122.1085 | -0.041199 | 121.9208 | 1.4211e-13 | -0.029136 | 0.00014951 | -0.0032373 | -0.010382 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0016987 | 0.018545 | 0.032622 | 0.013723 | 4.41 | 4.4472 | 4.3272 | 4.4108 | 4.4923 | 4.6107 | 4.1953 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.027442 | 0.07643 | -0.11378 | 4.2365 | -117.51 | 4.4512 | 4.3684 | 0.13188 | -117.4285 | -117.3101 | -0.072583 | -121.9919 | 0.06514 | -0.019731 | 0.052852 | -121.8933 | -121.8443 | 4.452 | 4.5335 | 4.6519 | 4.4884 | -117.7254 | -0.029962 | 0.068641 | 0.11763 | 0.1194 | -122.0346
4150.3281 | 122.1085 | -0.073242 | 121.9482 | 1.4211e-13 | -0.028923 | 0.00057691 | -0.0032373 | -0.010168 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0016987 | 0.018331 | 0.032622 | 0.013723 | 4.4146 | 4.4518 | 4.3318 | 4.4153 | 4.5014 | 4.6153 | 4.1999 | 0.02852 | 0.091933 | -0.06093 | -0.057425 | 0.041178 | 0.07643 | -0.12294 | 4.2732 | -117.5329 | 4.4879 | 4.405 | 0.13188 | -117.4468 | -117.333 | -0.049697 | -122.0057 | 0.10176 | 0.012312 | 0.062009 | -121.9071 | -121.8718 | 4.4886 | 4.5747 | 4.6885 | 4.525 | -117.7483 | 0.015817 | 0.11442 | 0.14967 | 0.16518 | -122.0712
4152.0938 | 122.0535 | -0.045776 | 121.9391 | 1.4211e-13 | -0.029564 | 0.00014951 | -0.0030235 | -0.010382 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018117 | 0.032194 | 0.013296 | 4.4283 | 4.4564 | 4.3455 | 4.4245 | 4.506 | 4.6198 | 4.2182 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.12294 | 4.264 | -117.5146 | 4.4741 | 4.3913 | 0.1273 | -117.4331 | -117.3192 | -0.077163 | -122.0057 | 0.069717 | -0.015154 | 0.062009 | -121.8933 | -121.8581 | 4.4703 | 4.5518 | 4.6656 | 4.5022 | -117.7208 | -0.020806 | 0.091533 | 0.12678 | 0.13313 | -122.062
4153.875 | 122.0764 | -0.082397 | 121.962 | 1.4211e-13 | -0.02935 | 0.00057691 | -0.0036647 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0016987 | 0.017904 | 0.032622 | 0.013509 | 4.4329 | 4.4655 | 4.3501 | 4.4336 | 4.5106 | 4.6336 | 4.232 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.071851 | -0.11836 | 4.3144 | -117.5283 | 4.5153 | 4.4325 | 0.11814 | -117.4514 | -117.3284 | -0.035964 | -122.024 | 0.11092 | 0.021467 | 0.057431 | -121.9162 | -121.8901 | 4.516 | 4.593 | 4.716 | 4.5479 | -117.73 | 0.020393 | 0.12815 | 0.15425 | 0.16975 | -122.0803
4155.6406 | 122.0215 | -0.086975 | 121.9894 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0034509 | -0.010595 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018331 | 0.032194 | 0.013509 | 4.4512 | 4.4793 | 4.3547 | 4.4474 | 4.5289 | 4.6427 | 4.2457 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.1321 | 4.3327 | -117.5421 | 4.5382 | 4.4417 | 0.10898 | -117.4605 | -117.3467 | -0.045122 | -122.0469 | 0.1155 | 0.026045 | 0.071167 | -121.9528 | -121.9176 | 4.5344 | 4.6159 | 4.7297 | 4.5663 | -117.7437 | 0.02955 | 0.12357 | 0.15883 | 0.17433 | -122.1215
4157.3594 | 122.0947 | -0.073242 | 121.9528 | 1.4211e-13 | -0.02935 | 0.00036331 | -0.0032373 | -0.010168 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018331 | 0.032835 | 0.013723 | 4.465 | 4.4884 | 4.373 | 4.4611 | 4.5427 | 4.6565 | 4.2503 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.032021 | 0.081008 | -0.11836 | 4.3235 | -117.4917 | 4.5382 | 4.4462 | 0.12272 | -117.4102 | -117.2964 | -0.045119 | -122.0148 | 0.10176 | 0.012312 | 0.057431 | -121.9208 | -121.8718 | 4.5344 | 4.6159 | 4.7297 | 4.5617 | -117.7025 | 0.011238 | 0.10526 | 0.15425 | 0.15602 | -122.0712
4159.0625 | 122.0581 | -0.059509 | 121.962 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0032373 | -0.010382 | 0.008241 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018545 | 0.032622 | 0.013509 | 4.4833 | 4.5251 | 4.3959 | 4.4794 | 4.5655 | 4.6839 | 4.2686 | 0.023941 | 0.096512 | -0.051772 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 4.3281 | -117.4825 | 4.5428 | 4.4554 | 0.12729 | -117.3964 | -117.278 | -0.06343 | -122.024 | 0.08345 | 0.007737 | 0.071167 | -121.9254 | -121.8855 | 4.5389 | 4.6251 | 4.7434 | 4.5846 | -117.6934 | -0.002495 | 0.096109 | 0.13594 | 0.15602 | -122.0849
4160.8281 | 121.9849 | -0.091553 | 121.9528 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0030235 | -0.010168 | 0.008241 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013937 | 4.5016 | 4.5296 | 4.4142 | 4.4932 | 4.5839 | 4.6931 | 4.2915 | 0.033099 | 0.091933 | -0.06093 | -0.062004 | 0.045757 | 0.071851 | -0.12294 | 4.3831 | -117.4597 | 4.5932 | 4.5058 | 0.12271 | -117.369 | -117.2597 | -0.031386 | -122.0148 | 0.12465 | 0.030623 | 0.062009 | -121.9071 | -121.881 | 4.5847 | 4.6754 | 4.7847 | 4.6212 | -117.6613 | 0.029549 | 0.13731 | 0.1634 | 0.18349 | -122.0758
4162.5469 | 122.1039 | -0.068665 | 121.9116 | 1.4211e-13 | -0.02935 | 0.00036331 | -0.0034509 | -0.0099547 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0019123 | 0.018331 | 0.032408 | 0.013723 | 4.5108 | 4.548 | 4.4279 | 4.5023 | 4.5884 | 4.7023 | 4.3007 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.0366 | 0.071851 | -0.12752 | 4.3693 | -117.4093 | 4.5794 | 4.4966 | 0.12729 | -117.3232 | -117.2094 | -0.058853 | -121.969 | 0.092606 | 0.012314 | 0.071167 | -121.875 | -121.8398 | 4.571 | 4.6571 | 4.7709 | 4.6166 | -117.611 | 0.01124 | 0.10526 | 0.14052 | 0.15602 | -122.0391
4164.3125 | 122.0398 | -0.086975 | 121.9894 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0034509 | -0.010168 | 0.008241 | 0.0053413 | -0.0042257 | -0.0019123 | 0.017904 | 0.032408 | 0.013509 | 4.5108 | 4.5525 | 4.4142 | 4.5023 | 4.5884 | 4.7068 | 4.3007 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.041178 | 0.07643 | -0.11378 | 4.3876 | -117.4871 | 4.5977 | 4.5012 | 0.11355 | -117.401 | -117.2826 | -0.026807 | -122.0514 | 0.11092 | 0.030624 | 0.057431 | -121.9483 | -121.913 | 4.5893 | 4.6754 | 4.7938 | 4.6395 | -117.6888 | 0.024971 | 0.12815 | 0.1634 | 0.16975 | -122.1032
4166.0781 | 122.1405 | -0.059509 | 121.9162 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0030235 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0012713 | 0.017904 | 0.032622 | 0.013509 | 4.5153 | 4.5525 | 4.4325 | 4.5069 | 4.593 | 4.7068 | 4.3007 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.11836 | 4.3602 | -117.4093 | 4.5748 | 4.492 | 0.13186 | -117.3232 | -117.2094 | -0.058852 | -121.9782 | 0.08345 | -0.001421 | 0.057431 | -121.875 | -121.8443 | 4.5664 | 4.6525 | 4.7663 | 4.612 | -117.6155 | -0.002495 | 0.10069 | 0.13136 | 0.13771 | -122.0346
4167.8594 | 122.1176 | -0.064087 | 121.9391 | 1.4211e-13 | -0.029136 | 0.00036331 | -0.0036647 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0016987 | 0.018545 | 0.032194 | 0.013509 | 4.5245 | 4.5525 | 4.4279 | 4.5161 | 4.5976 | 4.7114 | 4.3098 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.11836 | 4.3739 | -117.423 | 4.5886 | 4.492 | 0.11813 | -117.3415 | -117.2277 | -0.054274 | -122.0057 | 0.092607 | 0.003157 | 0.057431 | -121.9025 | -121.8672 | 4.5801 | 4.6617 | 4.7755 | 4.6166 | -117.6293 | -0.002495 | 0.10069 | 0.13594 | 0.14686 | -122.0574
4169.5625 | 121.9666 | -0.10529 | 121.994 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.01755 | -0.0044395 | -0.0014849 | 0.017904 | 0.032408 | 0.013509 | 4.5199 | 4.5571 | 4.4279 | 4.5115 | 4.5976 | 4.7068 | 4.3052 | 0.033099 | 0.087354 | -0.056351 | -0.057425 | 0.041178 | 0.081008 | -0.11836 | 4.4105 | -117.4825 | 4.6252 | 4.5332 | 0.12271 | -117.3964 | -117.2872 | -0.013075 | -122.0514 | 0.13839 | 0.048935 | 0.06201 | -121.9528 | -121.913 | 4.6168 | 4.7029 | 4.8121 | 4.6624 | -117.6888 | 0.047861 | 0.14646 | 0.18629 | 0.19264 | -122.1124
4171.3281 | 122.0123 | -0.091553 | 121.9528 | 1.4211e-13 | -0.02935 | -6.4092e-05 | -0.0032373 | -0.0099547 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018117 | 0.032835 | 0.013937 | 4.5245 | 4.5617 | 4.4325 | 4.5161 | 4.5976 | 4.7114 | 4.3052 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.3968 | -117.4368 | 4.616 | 4.5241 | 0.12729 | -117.3552 | -117.2414 | -0.031386 | -122.0148 | 0.11549 | 0.026044 | 0.05743 | -121.9162 | -121.881 | 4.6076 | 4.6892 | 4.803 | 4.6532 | -117.6476 | 0.029549 | 0.12815 | 0.1634 | 0.17433 | -122.0758
4173.0938 | 122.0398 | -0.082397 | 121.9711 | 1.4211e-13 | -0.02935 | 0.00036331 | -0.0032373 | -0.010168 | 0.008241 | -0.01755 | -0.0046531 | -0.0016987 | 0.018117 | 0.032622 | 0.013509 | 4.5337 | 4.5663 | 4.4371 | 4.5161 | 4.6022 | 4.716 | 4.3236 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.12294 | 4.4059 | -117.4551 | 4.616 | 4.5195 | 0.11355 | -117.369 | -117.2551 | -0.040542 | -122.0377 | 0.10634 | 0.016888 | 0.05743 | -121.9345 | -121.8947 | 4.5985 | 4.6846 | 4.7984 | 4.6487 | -117.6476 | 0.015815 | 0.119 | 0.15883 | 0.16975 | -122.0941
4174.8594 | 122.0306 | -0.091553 | 121.9849 | 1.4211e-13 | -0.029136 | 0.00014951 | -0.0030235 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018117 | 0.032622 | 0.013509 | 4.5291 | 4.5663 | 4.4371 | 4.5206 | 4.6068 | 4.7068 | 4.319 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.11836 | 4.4105 | -117.4642 | 4.6206 | 4.5287 | 0.11813 | -117.3781 | -117.278 | -0.026808 | -122.0469 | 0.11549 | 0.030623 | 0.057431 | -121.9483 | -121.913 | 4.6122 | 4.6983 | 4.7984 | 4.6578 | -117.6659 | 0.029549 | 0.12815 | 0.1634 | 0.17891 | -122.1032
4176.5625 | 122.0261 | -0.11902 | 121.9986 | 1.4211e-13 | -0.029564 | 0.00014951 | -0.0030235 | -0.010168 | 0.0080272 | -0.01755 | -0.0042257 | -0.0019123 | 0.017904 | 0.032622 | 0.013723 | 4.5291 | 4.5617 | 4.4371 | 4.5206 | 4.6022 | 4.7206 | 4.3098 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.032021 | 0.07643 | -0.11836 | 4.4288 | -117.478 | 4.6481 | 4.5561 | 0.12729 | -117.3964 | -117.278 | 0.000658 | -122.0652 | 0.14296 | 0.058089 | 0.057431 | -121.9666 | -121.9222 | 4.6397 | 4.7212 | 4.8396 | 4.6807 | -117.6888 | 0.052437 | 0.15104 | 0.19545 | 0.2018 | -122.117
4178.3281 | 121.9894 | -0.10529 | 121.9666 | 1.4211e-13 | -0.029564 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0084546 | -0.0022892 | -0.0040121 | -0.0014849 | 0.018331 | 0.032835 | 0.013723 | 4.5382 | 4.5709 | 4.4463 | 4.5298 | 4.6068 | 4.7297 | 4.3281 | 0.033099 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.11836 | 4.4334 | -117.4368 | 4.6435 | 4.5515 | 0.11813 | -117.3598 | -117.2368 | -0.013075 | -122.024 | 0.13839 | 0.044356 | 0.057431 | -121.93 | -121.8901 | 4.6351 | 4.712 | 4.835 | 4.6761 | -117.6384 | 0.047861 | 0.14189 | 0.18172 | 0.19264 | -122.0849
4180.0938 | 122.1039 | -0.054932 | 121.9666 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0028099 | -0.010168 | 0.0078136 | -0.01755 | -0.0048667 | -0.0012713 | 0.018758 | 0.032622 | 0.013296 | 4.5428 | 4.5754 | 4.4417 | 4.5344 | 4.6113 | 4.7297 | 4.3281 | 0.023941 | 0.087354 | -0.065509 | -0.062004 | 0.041178 | 0.071851 | -0.12294 | 4.3831 | -117.4322 | 4.5977 | 4.4966 | 0.11355 | -117.3552 | -117.2368 | -0.068007 | -122.0286 | 0.078873 | -0.010577 | 0.05743 | -121.9254 | -121.8947 | 4.5893 | 4.6663 | 4.7847 | 4.6304 | -117.6384 | -0.007072 | 0.09611 | 0.12678 | 0.14229 | -122.0895
4181.8438 | 121.9986 | -0.086975 | 121.9849 | 1.4211e-13 | -0.02935 | 0.00057691 | -0.0032373 | -0.010382 | 0.0078136 | -0.02518 | -0.0044395 | -0.0016987 | 0.018117 | 0.032408 | 0.013509 | 4.5611 | 4.5983 | 4.4646 | 4.5481 | 4.6342 | 4.748 | 4.3419 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.07643 | -0.12294 | 4.4288 | -117.4368 | 4.6481 | 4.5515 | 0.1227 | -117.3506 | -117.2368 | -0.035964 | -122.056 | 0.1155 | 0.026045 | 0.062009 | -121.9483 | -121.9084 | 4.6351 | 4.7212 | 4.835 | 4.6853 | -117.643 | 0.015814 | 0.12357 | 0.1634 | 0.16975 | -122.1078
4183.5625 | 122.1313 | -0.054932 | 121.9208 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0036647 | -0.010168 | 0.0080272 | -0.01755 | -0.0046531 | -0.0016987 | 0.017904 | 0.032408 | 0.013723 | 4.584 | 4.6258 | 4.4966 | 4.571 | 4.6571 | 4.7664 | 4.3739 | 0.023941 | 0.087354 | -0.051772 | -0.062004 | 0.041178 | 0.081008 | -0.12294 | 4.4289 | -117.3498 | 4.6389 | 4.5516 | 0.1227 | -117.2637 | -117.1544 | -0.068007 | -121.9828 | 0.078873 | 0.00316 | 0.071167 | -121.8796 | -121.8398 | 4.6259 | 4.7121 | 4.8213 | 4.6807 | -117.5469 | -0.007072 | 0.09611 | 0.13594 | 0.14229 | -122.0437
4185.3281 | 122.0078 | -0.11444 | 121.9574 | 1.4211e-13 | -0.029564 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.01755 | -0.0046531 | -0.0016987 | 0.018331 | 0.032622 | 0.013296 | 4.6069 | 4.6441 | 4.5195 | 4.5939 | 4.68 | 4.7984 | 4.4014 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 4.5158 | -117.3635 | 4.7213 | 4.634 | 0.11812 | -117.2774 | -117.159 | -0.008498 | -122.024 | 0.14296 | 0.05809 | 0.066588 | -121.9208 | -121.8855 | 4.7083 | 4.7945 | 4.9128 | 4.7586 | -117.556 | 0.047859 | 0.15104 | 0.18629 | 0.2018 | -122.0803
4187.0938 | 122.113 | -0.07782 | 121.9437 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0034509 | -0.0099547 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0012713 | 0.018117 | 0.032835 | 0.013509 | 4.6161 | 4.6441 | 4.5195 | 4.5985 | 4.6892 | 4.7938 | 4.3968 | 0.02852 | 0.082776 | -0.051772 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 4.4746 | -117.3452 | 4.6939 | 4.5973 | 0.1227 | -117.2545 | -117.1498 | -0.045119 | -122.0102 | 0.10634 | 0.026048 | 0.071167 | -121.9025 | -121.8672 | 4.6763 | 4.767 | 4.8716 | 4.7219 | -117.5468 | 0.011238 | 0.119 | 0.15425 | 0.1606 | -122.0666
4188.8594 | 122.1085 | -0.059509 | 121.9299 | 1.4211e-13 | -0.02935 | -6.4092e-05 | -0.0034509 | -0.0097409 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018117 | 0.032622 | 0.013723 | 4.4787 | 4.5113 | 4.3867 | 4.4703 | 4.5427 | 4.6565 | 4.2594 | 0.02852 | 0.087354 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.12294 | 4.319 | -117.4597 | 4.5382 | 4.4462 | 0.12729 | -117.3873 | -117.2735 | -0.06343 | -122.0011 | 0.088029 | -0.006 | 0.05743 | -121.8888 | -121.8535 | 4.5298 | 4.6022 | 4.716 | 4.5708 | -117.6705 | -0.011652 | 0.10069 | 0.13594 | 0.14686 | -122.0529
4190.5781 | 121.9757 | -0.10986 | 121.962 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0028099 | -0.0099547 | 0.0080272 | -0.01755 | -0.0046531 | -0.0016987 | 0.018545 | 0.032835 | 0.013937 | 4.4787 | 4.5113 | 4.3776 | 4.4611 | 4.5472 | 4.6656 | 4.264 | 0.033099 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.085587 | -0.12752 | 4.3739 | -117.5009 | 4.5886 | 4.4874 | 0.11356 | -117.4147 | -117.2963 | -0.017655 | -122.024 | 0.14296 | 0.048933 | 0.066588 | -121.9254 | -121.8764 | 4.571 | 4.6571 | 4.7755 | 4.6212 | -117.6979 | 0.047859 | 0.14646 | 0.19545 | 0.19722 | -122.0895
4192.3594 | 122.0856 | -0.068665 | 121.9116 | 1.4211e-13 | -0.029564 | -6.4092e-05 | -0.0034509 | -0.0099547 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0014849 | 0.018331 | 0.032408 | 0.013723 | 4.4787 | 4.5251 | 4.3959 | 4.4703 | 4.5564 | 4.6748 | 4.2732 | 0.023941 | 0.091933 | -0.06093 | -0.062004 | 0.027442 | 0.07643 | -0.11836 | 4.3418 | -117.4413 | 4.5474 | 4.4646 | 0.12271 | -117.3552 | -117.2368 | -0.049696 | -121.9736 | 0.092606 | 0.007735 | 0.057431 | -121.8842 | -121.8352 | 4.5389 | 4.6251 | 4.7434 | 4.5937 | -117.6384 | 0.006661 | 0.096107 | 0.1451 | 0.1606 | -122.03
4194.1406 | 122.1176 | -0.045776 | 121.9254 | 1.4211e-13 | -0.029564 | 0.00014951 | -0.0032373 | -0.010382 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0016987 | 0.018331 | 0.032408 | 0.013723 | 4.4924 | 4.5342 | 4.3959 | 4.484 | 4.561 | 4.6748 | 4.2778 | 0.02852 | 0.087354 | -0.051772 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 4.3235 | -117.4413 | 4.5382 | 4.4417 | 0.11813 | -117.3644 | -117.2506 | -0.077163 | -121.9874 | 0.074296 | -0.005996 | 0.071167 | -121.8888 | -121.8489 | 4.5298 | 4.6067 | 4.7206 | 4.58 | -117.6476 | -0.016228 | 0.082376 | 0.12221 | 0.13313 | -122.0483
4195.9062 | 122.0261 | -0.082397 | 121.9849 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0032373 | -0.010168 | 0.0084546 | -0.0022892 | -0.0044395 | -0.0019123 | 0.018117 | 0.032622 | 0.013509 | 4.5016 | 4.5342 | 4.4142 | 4.4932 | 4.5701 | 4.6839 | 4.2961 | 0.02852 | 0.087354 | -0.051772 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 4.3785 | -117.4917 | 4.584 | 4.4966 | 0.11813 | -117.4147 | -117.3009 | -0.040542 | -122.0423 | 0.11092 | 0.030625 | 0.071167 | -121.9483 | -121.9084 | 4.5756 | 4.6525 | 4.7663 | 4.6166 | -117.6888 | 0.024972 | 0.119 | 0.15883 | 0.16975 | -122.1078
4197.625 | 121.9849 | -0.10071 | 121.9528 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0032373 | -0.010168 | 0.0078136 | -0.01755 | -0.0042257 | -0.0016987 | 0.017904 | 0.032622 | 0.013296 | 4.5153 | 4.5525 | 4.4188 | 4.4977 | 4.5884 | 4.6977 | 4.3007 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.0366 | 0.081008 | -0.11378 | 4.4014 | -117.4551 | 4.616 | 4.5195 | 0.11813 | -117.3644 | -117.2551 | -0.013074 | -122.0194 | 0.12923 | 0.035199 | 0.048273 | -121.9162 | -121.8718 | 4.5984 | 4.6891 | 4.7984 | 4.6532 | -117.6522 | 0.034126 | 0.13731 | 0.18172 | 0.18348 | -122.0666
4199.4062 | 122.0856 | -0.059509 | 121.9208 | 1.4211e-13 | -0.029777 | -6.4092e-05 | -0.0032373 | -0.010168 | 0.0078136 | 0.0053413 | -0.0044395 | -0.0019123 | 0.018117 | 0.032622 | 0.013509 | 4.5062 | 4.5525 | 4.4188 | 4.5023 | 4.5839 | 4.7023 | 4.3052 | 0.014784 | 0.087354 | -0.065509 | -0.057425 | 0.0366 | 0.07643 | -0.11836 | 4.3647 | -117.4185 | 4.5657 | 4.4783 | 0.11355 | -117.3369 | -117.2185 | -0.058852 | -121.9782 | 0.074293 | -0.006 | 0.052852 | -121.8842 | -121.8443 | 4.5618 | 4.6434 | 4.7618 | 4.612 | -117.6155 | 0.002084 | 0.096109 | 0.13594 | 0.14686 | -122.0391
4201.1094 | 122.0535 | -0.086975 | 121.9345 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0036647 | -0.010168 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0014849 | 0.018117 | 0.032835 | 0.013082 | 4.5062 | 4.5525 | 4.4142 | 4.4977 | 4.5793 | 4.6977 | 4.3052 | 0.02852 | 0.087354 | -0.065509 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 4.3922 | -117.4368 | 4.5932 | 4.5012 | 0.10897 | -117.3552 | -117.2368 | -0.035964 | -121.9965 | 0.1155 | 0.021466 | 0.05743 | -121.8979 | -121.8581 | 4.5847 | 4.6663 | 4.7847 | 4.6395 | -117.6293 | 0.024971 | 0.12357 | 0.1634 | 0.17433 | -122.0574
4202.875 | 122.0306 | -0.10986 | 121.9666 | 1.4211e-13 | -0.029136 | 0.00014951 | -0.0034509 | -0.0099547 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013509 | 4.5245 | 4.5617 | 4.4371 | 4.5161 | 4.5884 | 4.7023 | 4.3098 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.041178 | 0.081008 | -0.12294 | 4.4197 | -117.4505 | 4.6344 | 4.547 | 0.12729 | -117.3781 | -117.2643 | -0.013076 | -122.0286 | 0.13838 | 0.048933 | 0.062009 | -121.9254 | -121.8855 | 4.6259 | 4.6983 | 4.8121 | 4.6716 | -117.6567 | 0.047859 | 0.15104 | 0.19087 | 0.18806 | -122.0895
4204.6562 | 122.0718 | -0.086975 | 121.9574 | 1.4211e-13 | -0.029564 | 0.00057691 | -0.0032373 | -0.0099547 | 0.0078136 | -0.0099192 | -0.0040121 | -0.0019123 | 0.017904 | 0.032835 | 0.013937 | 4.5291 | 4.5663 | 4.4417 | 4.5206 | 4.6022 | 4.7114 | 4.3144 | 0.02852 | 0.091933 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.12294 | 4.4014 | -117.4368 | 4.616 | 4.5287 | 0.12728 | -117.3552 | -117.246 | -0.035964 | -122.0194 | 0.1155 | 0.026045 | 0.062009 | -121.9162 | -121.8855 | 4.6076 | 4.6892 | 4.7984 | 4.6532 | -117.643 | 0.024971 | 0.12815 | 0.15883 | 0.17891 | -122.0803
4206.4219 | 122.0215 | -0.10529 | 121.9757 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0030235 | -0.0099547 | 0.008241 | -0.02518 | -0.0044395 | -0.0016987 | 0.018331 | 0.032622 | 0.013723 | 4.5337 | 4.5754 | 4.4417 | 4.5161 | 4.6068 | 4.7297 | 4.3236 | 0.02852 | 0.078197 | -0.056351 | -0.057425 | 0.041178 | 0.07643 | -0.11836 | 4.4288 | -117.4597 | 4.6389 | 4.547 | 0.11813 | -117.369 | -117.246 | -0.013075 | -122.0331 | 0.13381 | 0.048935 | 0.06201 | -121.9345 | -121.8993 | 4.6213 | 4.712 | 4.835 | 4.6807 | -117.6522 | 0.047861 | 0.14646 | 0.18172 | 0.18348 | -122.0941
4208.2031 | 122.0901 | -0.059509 | 121.9391 | 1.4211e-13 | -0.02935 | 0.00036331 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0014849 | 0.017904 | 0.033049 | 0.013723 | 4.5337 | 4.5754 | 4.4463 | 4.5206 | 4.6022 | 4.716 | 4.3236 | 0.033099 | 0.091933 | -0.056351 | -0.062004 | 0.041178 | 0.07643 | -0.12752 | 4.3831 | -117.4185 | 4.5932 | 4.5058 | 0.12271 | -117.3369 | -117.2231 | -0.068009 | -122.0011 | 0.092608 | 0.003158 | 0.071167 | -121.8979 | -121.8627 | 4.5801 | 4.6617 | 4.7755 | 4.6349 | -117.6155 | -0.002495 | 0.10069 | 0.13594 | 0.15144 | -122.0666
4209.9062 | 122.0444 | -0.068665 | 121.9345 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0034509 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0019123 | 0.018117 | 0.032835 | 0.013723 | 4.5428 | 4.5846 | 4.4508 | 4.5344 | 4.6113 | 4.7297 | 4.3327 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.12752 | 4.4014 | -117.4001 | 4.6115 | 4.5195 | 0.11813 | -117.3232 | -117.2048 | -0.058853 | -122.0011 | 0.092606 | 0.007735 | 0.066588 | -121.9025 | -121.8627 | 4.603 | 4.68 | 4.7984 | 4.6533 | -117.6018 | 0.002083 | 0.10069 | 0.14052 | 0.15602 | -122.062
4211.6719 | 121.9666 | -0.1236 | 121.9666 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0032373 | -0.0099547 | 0.008241 | -0.0099192 | -0.0042257 | -0.0016987 | 0.018117 | 0.032408 | 0.013723 | 4.5428 | 4.5846 | 4.46 | 4.5298 | 4.6159 | 4.7297 | 4.3373 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.11378 | 4.4609 | -117.4368 | 4.6664 | 4.5836 | 0.1227 | -117.3506 | -117.2368 | 0.009814 | -122.024 | 0.14754 | 0.062666 | 0.052852 | -121.93 | -121.8947 | 4.6534 | 4.7395 | 4.8533 | 4.7082 | -117.6293 | 0.066171 | 0.1602 | 0.19545 | 0.20637 | -122.0803
4213.4531 | 122.0535 | -0.064087 | 121.9299 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0032373 | -0.010168 | 0.0078136 | -0.0099192 | -0.0042257 | -0.0012713 | 0.018117 | 0.032408 | 0.013509 | 4.5474 | 4.5892 | 4.4554 | 4.5344 | 4.6205 | 4.7297 | 4.3327 | 0.023941 | 0.082776 | -0.06093 | -0.052847 | 0.0366 | 0.067272 | -0.11836 | 4.3968 | -117.3956 | 4.6115 | 4.5195 | 0.1227 | -117.3094 | -117.2002 | -0.054274 | -121.9828 | 0.088028 | 0.003157 | 0.057431 | -121.8933 | -121.8627 | 4.5985 | 4.6846 | 4.7938 | 4.6533 | -117.5972 | 0.01124 | 0.10069 | 0.13136 | 0.14686 | -122.0483
4215.1562 | 122.0673 | -0.07782 | 121.9391 | 1.4211e-13 | -0.029564 | -0.00027769 | -0.0034509 | -0.0099547 | 0.008241 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018117 | 0.032622 | 0.013723 | 4.552 | 4.6029 | 4.4691 | 4.5481 | 4.6251 | 4.7389 | 4.3419 | 0.019362 | 0.091933 | -0.065509 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.4197 | -117.391 | 4.6298 | 4.547 | 0.12728 | -117.314 | -117.2002 | -0.045119 | -122.0011 | 0.097182 | 0.012311 | 0.05743 | -121.9025 | -121.8672 | 4.6259 | 4.7029 | 4.8167 | 4.6807 | -117.5972 | 0.015816 | 0.11442 | 0.14967 | 0.16975 | -122.062
4216.9219 | 121.9894 | -0.09613 | 121.9574 | 1.4211e-13 | -0.029564 | -6.4092e-05 | -0.0032373 | -0.010168 | 0.0076 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.032622 | 0.013723 | 4.5703 | 4.6121 | 4.4783 | 4.5618 | 4.6388 | 4.7526 | 4.3556 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.12294 | 4.4517 | -117.3956 | 4.6664 | 4.5744 | 0.1227 | -117.3186 | -117.2048 | -0.026809 | -122.0194 | 0.12465 | 0.0352 | 0.062009 | -121.9162 | -121.881 | 4.658 | 4.7349 | 4.8487 | 4.7082 | -117.6018 | 0.034126 | 0.13731 | 0.17256 | 0.17891 | -122.0803
4218.7031 | 122.0947 | -0.059509 | 121.9254 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0032373 | -0.010168 | 0.0076 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018117 | 0.032622 | 0.013296 | 4.584 | 4.6212 | 4.4875 | 4.571 | 4.6571 | 4.7618 | 4.3693 | 0.02852 | 0.091933 | -0.056351 | -0.062004 | 0.041178 | 0.067272 | -0.1321 | 4.4289 | -117.3544 | 4.6435 | 4.547 | 0.11812 | -117.2682 | -117.1636 | -0.072588 | -121.9874 | 0.088029 | 0.003158 | 0.075746 | -121.8842 | -121.8581 | 4.6305 | 4.7166 | 4.8213 | 4.6807 | -117.556 | -0.002495 | 0.10069 | 0.12678 | 0.15144 | -122.0575
4220.4688 | 122.0169 | -0.09613 | 121.9391 | 1.4211e-13 | -0.029777 | 0.00057691 | -0.0030235 | -0.010168 | 0.0076 | -0.01755 | -0.0046531 | -0.0019123 | 0.018331 | 0.032835 | 0.013296 | 4.584 | 4.6258 | 4.4966 | 4.5802 | 4.6617 | 4.7618 | 4.3785 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 4.4746 | -117.3589 | 4.6801 | 4.5927 | 0.11812 | -117.2774 | -117.1773 | -0.026809 | -122.0057 | 0.12007 | 0.039779 | 0.066588 | -121.8979 | -121.8627 | 4.6763 | 4.7578 | 4.8579 | 4.7219 | -117.5606 | 0.029548 | 0.13731 | 0.17256 | 0.17891 | -122.062
4222.1719 | 122.0123 | -0.07782 | 121.9437 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0016987 | 0.018117 | 0.032622 | 0.013509 | 4.5932 | 4.635 | 4.5058 | 4.5756 | 4.6571 | 4.7664 | 4.3831 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.027442 | 0.07643 | -0.11836 | 4.4609 | -117.3681 | 4.671 | 4.5836 | 0.1227 | -117.2865 | -117.1773 | -0.040541 | -122.0102 | 0.10634 | 0.021469 | 0.06201 | -121.9162 | -121.8672 | 4.6534 | 4.7349 | 4.8442 | 4.7128 | -117.5606 | 0.011238 | 0.10526 | 0.15425 | 0.16517 | -122.062
4223.9375 | 121.9574 | -0.091553 | 121.9208 | 1.4211e-13 | -0.029564 | 0.00057691 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0016987 | 0.017904 | 0.032408 | 0.013937 | 4.6069 | 4.6441 | 4.5058 | 4.5893 | 4.6617 | 4.7801 | 4.3922 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.032021 | 0.067272 | -0.12752 | 4.4838 | -117.3315 | 4.6985 | 4.5973 | 0.11354 | -117.2591 | -117.1407 | -0.035965 | -121.9782 | 0.11549 | 0.030623 | 0.066588 | -121.8888 | -121.8535 | 4.6809 | 4.7533 | 4.8716 | 4.7357 | -117.5285 | 0.034128 | 0.12357 | 0.15882 | 0.17891 | -122.0483
4225.7031 | 122.0444 | -0.091553 | 121.9254 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0032373 | -0.0099547 | 0.008241 | -0.0022892 | -0.0040121 | -0.0014849 | 0.018117 | 0.032622 | 0.013296 | 4.6069 | 4.6487 | 4.5149 | 4.5939 | 4.6663 | 4.7755 | 4.3922 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 4.4838 | -117.3315 | 4.6985 | 4.6065 | 0.1227 | -117.2591 | -117.1498 | -0.035965 | -121.9919 | 0.12007 | 0.026044 | 0.062009 | -121.8888 | -121.8489 | 4.6854 | 4.7578 | 4.8671 | 4.7402 | -117.5331 | 0.024971 | 0.12815 | 0.16798 | 0.17433 | -122.0529
4227.4844 | 122.0261 | -0.082397 | 121.9528 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0030235 | -0.010168 | 0.0076 | -0.01755 | -0.0046531 | -0.0014849 | 0.018331 | 0.032408 | 0.013509 | 4.6115 | 4.6487 | 4.5195 | 4.603 | 4.6709 | 4.7892 | 4.3968 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.07643 | -0.12294 | 4.4792 | -117.3498 | 4.6939 | 4.6019 | 0.1227 | -117.282 | -117.1636 | -0.040542 | -122.024 | 0.10634 | 0.021467 | 0.062009 | -121.9162 | -121.8764 | 4.6854 | 4.7533 | 4.8716 | 4.7311 | -117.556 | 0.011236 | 0.119 | 0.15883 | 0.16975 | -122.0758
4229.2031 | 122.1039 | -0.068665 | 121.9208 | 1.4211e-13 | -0.029564 | -6.4092e-05 | -0.0034509 | -0.0099547 | 0.0080272 | -0.02518 | -0.0042257 | -0.0019123 | 0.018331 | 0.032622 | 0.013296 | 4.6252 | 4.667 | 4.5378 | 4.6076 | 4.6846 | 4.8076 | 4.406 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 4.4746 | -117.3132 | 4.6939 | 4.6065 | 0.13185 | -117.2362 | -117.1132 | -0.058853 | -121.9874 | 0.097185 | 0.007735 | 0.066588 | -121.8842 | -121.8489 | 4.6763 | 4.7533 | 4.8762 | 4.7357 | -117.5148 | 0.002083 | 0.10526 | 0.14052 | 0.15602 | -122.0483
4230.9844 | 122.0169 | -0.086975 | 121.962 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0036647 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017904 | 0.032835 | 0.013509 | 4.6252 | 4.667 | 4.5287 | 4.603 | 4.6846 | 4.7984 | 4.4151 | 0.023941 | 0.087354 | -0.047194 | -0.062004 | 0.041178 | 0.07643 | -0.12752 | 4.5021 | -117.3589 | 4.7122 | 4.6156 | 0.11354 | -117.2774 | -117.1636 | -0.040543 | -122.024 | 0.11092 | 0.039781 | 0.080324 | -121.9208 | -121.8855 | 4.69 | 4.7716 | 4.8854 | 4.754 | -117.5468 | 0.024971 | 0.12815 | 0.1634 | 0.17433 | -122.0895
4232.75 | 122.0535 | -0.054932 | 121.9299 | 1.4211e-13 | -0.02935 | 0.00014951 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018331 | 0.033049 | 0.013509 | 4.6344 | 4.667 | 4.5378 | 4.6122 | 4.6938 | 4.803 | 4.406 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.11836 | 4.4609 | -117.3177 | 4.6893 | 4.5928 | 0.13185 | -117.2362 | -117.1269 | -0.063429 | -121.9919 | 0.078873 | -0.005998 | 0.057431 | -121.8888 | -121.8581 | 4.6671 | 4.7487 | 4.8579 | 4.7219 | -117.524 | -0.007072 | 0.09611 | 0.12678 | 0.13771 | -122.0483
4234.5312 | 121.9666 | -0.10529 | 121.9482 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0030235 | -0.010168 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0016987 | 0.017904 | 0.032622 | 0.013509 | 4.6344 | 4.6716 | 4.5424 | 4.6076 | 4.6938 | 4.8076 | 4.4106 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 4.5158 | -117.3406 | 4.7397 | 4.6477 | 0.13185 | -117.2545 | -117.1407 | -0.013075 | -122.0148 | 0.12923 | 0.044356 | 0.057431 | -121.9162 | -121.8764 | 4.7129 | 4.799 | 4.9128 | 4.7769 | -117.5377 | 0.038704 | 0.13731 | 0.17714 | 0.19722 | -122.0666
4236.2969 | 122.0993 | -0.068665 | 121.907 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0034509 | -0.010168 | 0.0080272 | -0.0022892 | -0.0040121 | -0.0016987 | 0.01769 | 0.032835 | 0.013509 | 4.6435 | 4.6762 | 4.5516 | 4.6122 | 4.6938 | 4.8076 | 4.4197 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.12294 | 4.4884 | -117.2948 | 4.7122 | 4.6202 | 0.13185 | -117.2133 | -117.0995 | -0.054274 | -121.969 | 0.097185 | 0.007735 | 0.062009 | -121.8659 | -121.8352 | 4.6809 | 4.7624 | 4.8762 | 4.7448 | -117.4873 | 0.006661 | 0.10984 | 0.14052 | 0.15144 | -122.03
4238.0625 | 122.0078 | -0.086975 | 121.9528 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0032373 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0014849 | 0.018117 | 0.032835 | 0.013723 | 4.6481 | 4.6807 | 4.5516 | 4.6214 | 4.7029 | 4.8121 | 4.4197 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.081008 | -0.12752 | 4.5067 | -117.3315 | 4.7351 | 4.6385 | 0.13185 | -117.2499 | -117.1407 | -0.040543 | -122.0194 | 0.11092 | 0.026045 | 0.066588 | -121.9162 | -121.8718 | 4.7083 | 4.7899 | 4.8991 | 4.7677 | -117.5331 | 0.020393 | 0.12357 | 0.16798 | 0.16975 | -122.0803
4239.8281 | 122.0718 | -0.059509 | 121.9254 | 1.4211e-13 | -0.029564 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | 0.0053413 | -0.0044395 | -0.0014849 | 0.018331 | 0.032622 | 0.013723 | 4.6527 | 4.6899 | 4.5561 | 4.6305 | 4.7121 | 4.8213 | 4.4334 | 0.023941 | 0.10109 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.12752 | 4.493 | -117.2948 | 4.7122 | 4.6156 | 0.12269 | -117.2133 | -117.1041 | -0.068009 | -121.9874 | 0.08345 | -0.001421 | 0.066588 | -121.8842 | -121.8489 | 4.69 | 4.7716 | 4.8808 | 4.7494 | -117.4919 | -0.002495 | 0.10069 | 0.13594 | 0.1606 | -122.0529
4241.5312 | 121.9711 | -0.11902 | 121.962 | 1.4211e-13 | -0.029564 | 0.00057691 | -0.0034509 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.018117 | 0.032835 | 0.013509 | 4.6573 | 4.6853 | 4.5561 | 4.6305 | 4.7029 | 4.8213 | 4.438 | 0.033099 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.12752 | 4.557 | -117.3315 | 4.7763 | 4.6752 | 0.11811 | -117.2591 | -117.1407 | -0.008499 | -122.024 | 0.15212 | 0.062668 | 0.071167 | -121.9254 | -121.8901 | 4.7495 | 4.8219 | 4.9403 | 4.8043 | -117.5239 | 0.057015 | 0.15562 | 0.19087 | 0.2018 | -122.0895
4243.2969 | 122.081 | -0.068665 | 121.9299 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0030235 | -0.010168 | 0.0078136 | -0.01755 | -0.0042257 | -0.0019123 | 0.018117 | 0.032622 | 0.013296 | 4.6435 | 4.6899 | 4.5607 | 4.6351 | 4.7121 | 4.8213 | 4.4334 | 0.02852 | 0.087354 | -0.056351 | -0.071161 | 0.041178 | 0.07643 | -0.1321 | 4.5021 | -117.2948 | 4.7122 | 4.6294 | 0.12727 | -117.2179 | -117.1086 | -0.063432 | -122.0011 | 0.097185 | 0.012314 | 0.075746 | -121.8888 | -121.8535 | 4.7038 | 4.7807 | 4.89 | 4.7586 | -117.4965 | -0.002496 | 0.10984 | 0.1451 | 0.15602 | -122.062
4245.0156 | 122.0123 | -0.082397 | 121.9528 | 1.4211e-13 | -0.029564 | 0.00014951 | -0.0034509 | -0.010595 | 0.0080272 | -0.01755 | -0.0048667 | -0.0019123 | 0.017904 | 0.032194 | 0.013509 | 4.6756 | 4.7174 | 4.579 | 4.6488 | 4.735 | 4.8442 | 4.4609 | 0.02852 | 0.091933 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 4.5433 | -117.304 | 4.758 | 4.6614 | 0.11811 | -117.2179 | -117.1086 | -0.040542 | -122.0148 | 0.11092 | 0.021467 | 0.062009 | -121.9162 | -121.881 | 4.7312 | 4.8174 | 4.9266 | 4.7998 | -117.4919 | 0.020393 | 0.119 | 0.15425 | 0.17433 | -122.0758
4246.7812 | 122.1222 | -0.064087 | 121.907 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018117 | 0.032835 | 0.013509 | 6.2643 | 6.2878 | 6.1173 | 6.2238 | 6.301 | 6.4147 | 5.9903 | 0.033099 | 0.091933 | -0.065509 | -0.062004 | 0.041178 | 0.07643 | -0.12294 | 6.0544 | -115.6832 | 6.3284 | 6.1814 | 0.12705 | -115.6061 | -115.4924 | -0.058852 | -121.969 | 0.097186 | -0.001422 | 0.05743 | -121.8659 | -121.8306 | 6.2879 | 6.365 | 6.4787 | 6.3519 | -115.9168 | 0.002083 | 0.10526 | 0.14052 | 0.15602 | -122.03
4248.5 | 122.0306 | -0.068665 | 121.9116 | 1.4211e-13 | -0.02935 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0046531 | -0.0019123 | 0.018331 | 0.032835 | 0.013296 | 6.3055 | 6.3428 | 6.1677 | 6.265 | 6.3467 | 6.4559 | 6.0361 | 0.019362 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 6.1047 | -115.6466 | 6.3742 | 6.2364 | 0.13162 | -115.5649 | -115.4558 | -0.054274 | -121.969 | 0.088027 | 0.007735 | 0.062009 | -121.875 | -121.8352 | 6.3337 | 6.4154 | 6.5245 | 6.4114 | -115.8756 | 0.01124 | 0.10526 | 0.1451 | 0.15144 | -122.0346
4250.2656 | 121.9437 | -0.10986 | 121.9391 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0032373 | -0.010382 | 0.0080272 | -0.02518 | -0.0046531 | -0.0019123 | 0.018117 | 0.032835 | 0.013296 | 6.333 | 6.384 | 6.2043 | 6.2879 | 6.3742 | 6.4833 | 6.0635 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.032021 | 0.07643 | -0.12752 | 6.1734 | -115.6512 | 6.4428 | 6.3142 | 0.14077 | -115.5649 | -115.4558 | -0.017655 | -122.0011 | 0.1338 | 0.044354 | 0.062009 | -121.9071 | -121.8627 | 6.3978 | 6.4841 | 6.5932 | 6.4938 | -115.8755 | 0.047859 | 0.14188 | 0.18629 | 0.19264 | -122.0666
4252.0312 | 122.0718 | -0.059509 | 121.8704 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0030235 | -0.0097409 | 0.0080272 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.033263 | 0.013296 | 6.3421 | 6.3702 | 6.2089 | 6.297 | 6.3834 | 6.4879 | 6.0681 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.032021 | 0.081008 | -0.1321 | 6.1276 | -115.5734 | 6.4016 | 6.2684 | 0.14077 | -115.487 | -115.3825 | -0.072588 | -121.9278 | 0.088029 | -0.001421 | 0.071167 | -121.8384 | -121.7894 | 6.3566 | 6.4429 | 6.5474 | 6.4298 | -115.8023 | 0.002084 | 0.09153 | 0.14052 | 0.14686 | -122.0025
4253.7969 | 121.994 | -0.09613 | 121.9437 | 1.4211e-13 | -0.029777 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.008241 | -0.01755 | -0.0044395 | -0.0016987 | 0.017904 | 0.032408 | 0.013723 | 6.3696 | 6.4069 | 6.2272 | 6.3291 | 6.4063 | 6.5154 | 6.0956 | 0.014784 | 0.096512 | -0.06093 | -0.062004 | 0.0366 | 0.067272 | -0.12294 | 6.1917 | -115.6146 | 6.4657 | 6.3233 | 0.13161 | -115.5374 | -115.4283 | -0.026809 | -122.0057 | 0.11091 | 0.0352 | 0.062009 | -121.9071 | -121.8764 | 6.4252 | 6.5024 | 6.6115 | 6.503 | -115.8481 | 0.034126 | 0.13273 | 0.1634 | 0.19264 | -122.0666
4255.5625 | 121.9437 | -0.11444 | 121.9299 | 1.4211e-13 | -0.029777 | 0.00036331 | -0.0032373 | -0.0099547 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.018117 | 0.032835 | 0.013509 | 6.3787 | 6.4023 | 6.2364 | 6.3337 | 6.4109 | 6.5154 | 6.1002 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.032021 | 0.071851 | -0.12294 | 6.2146 | -115.5963 | 6.4932 | 6.3508 | 0.13619 | -115.5191 | -115.4146 | -0.008498 | -121.9919 | 0.14296 | 0.053511 | 0.062009 | -121.8979 | -121.8581 | 6.4481 | 6.5253 | 6.6298 | 6.5167 | -115.8298 | 0.052437 | 0.14646 | 0.18629 | 0.2018 | -122.0529
4257.3281 | 122.0261 | -0.07782 | 121.9345 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0034509 | -0.0099547 | 0.008241 | -0.0022892 | -0.0042257 | -0.0014849 | 0.017904 | 0.033263 | 0.013296 | 6.3833 | 6.4115 | 6.2409 | 6.3291 | 6.4154 | 6.5245 | 6.1002 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.027442 | 0.071851 | -0.11836 | 6.178 | -115.6054 | 6.4611 | 6.3188 | 0.14077 | -115.5191 | -115.41 | -0.040541 | -121.9919 | 0.10634 | 0.01689 | 0.057431 | -121.9071 | -121.8627 | 6.4069 | 6.4933 | 6.6024 | 6.4893 | -115.8343 | 0.020395 | 0.10526 | 0.14967 | 0.1606 | -122.0529
4259.0312 | 121.9986 | -0.10529 | 121.9254 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0028099 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0019123 | 0.017904 | 0.032622 | 0.013509 | 6.3925 | 6.4115 | 6.2501 | 6.3383 | 6.42 | 6.5291 | 6.1048 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.12752 | 6.21 | -115.5871 | 6.4978 | 6.3554 | 0.14535 | -115.5053 | -115.3962 | -0.022232 | -121.9874 | 0.13381 | 0.044356 | 0.066588 | -121.8842 | -121.8489 | 6.4435 | 6.5253 | 6.6344 | 6.5167 | -115.8206 | 0.043282 | 0.14646 | 0.18172 | 0.18806 | -122.0529
4260.7969 | 122.0306 | -0.073242 | 121.9162 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0032373 | -0.0099547 | 0.008241 | -0.01755 | -0.0044395 | -0.0016987 | 0.018331 | 0.032835 | 0.013509 | 6.3971 | 6.4252 | 6.2501 | 6.3383 | 6.4292 | 6.5383 | 6.1231 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.12752 | 6.1963 | -115.5779 | 6.4703 | 6.3233 | 0.12703 | -115.487 | -115.3779 | -0.054276 | -121.9736 | 0.10176 | 0.012312 | 0.066588 | -121.8796 | -121.8443 | 6.4115 | 6.5024 | 6.6115 | 6.4984 | -115.7931 | 0.015817 | 0.10984 | 0.14509 | 0.1606 | -122.0437
4262.5781 | 121.9437 | -0.10529 | 121.9391 | 1.4211e-13 | -0.029991 | -6.4092e-05 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0014849 | 0.01769 | 0.032622 | 0.013509 | 6.4062 | 6.4298 | 6.2684 | 6.3657 | 6.4383 | 6.5429 | 6.1231 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.11836 | 6.2284 | -115.5734 | 6.5115 | 6.3737 | 0.14534 | -115.5008 | -115.3962 | -0.013075 | -122.0057 | 0.13381 | 0.044356 | 0.057431 | -121.8979 | -121.8627 | 6.471 | 6.5436 | 6.6481 | 6.5351 | -115.816 | 0.038704 | 0.14646 | 0.18172 | 0.19264 | -122.0574
4264.3594 | 122.0947 | -0.068665 | 121.8933 | 1.4211e-13 | -0.029777 | 0.00057691 | -0.0034509 | -0.010382 | 0.008241 | -0.01755 | -0.0044395 | -0.0016987 | 0.017904 | 0.032408 | 0.013509 | 6.4108 | 6.4389 | 6.2776 | 6.3611 | 6.4429 | 6.552 | 6.1322 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.12752 | 6.2009 | -115.5322 | 6.4795 | 6.3462 | 0.14534 | -115.4504 | -115.3413 | -0.058853 | -121.9507 | 0.092606 | 0.007735 | 0.066588 | -121.8567 | -121.8215 | 6.4298 | 6.5116 | 6.6207 | 6.5076 | -115.7611 | 0.01124 | 0.10526 | 0.14052 | 0.15602 | -122.0208
4266.1406 | 121.9116 | -0.10071 | 121.9482 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0034509 | -0.010382 | 0.008241 | -0.0099192 | -0.0044395 | -0.0019123 | 0.018117 | 0.032835 | 0.013082 | 6.4245 | 6.4572 | 6.2821 | 6.3703 | 6.4658 | 6.5703 | 6.1505 | 0.023941 | 0.082776 | -0.051772 | -0.052847 | 0.0366 | 0.07643 | -0.12752 | 6.2513 | -115.5779 | 6.5252 | 6.3829 | 0.13161 | -115.4824 | -115.3779 | -0.02681 | -122.0011 | 0.12465 | 0.048936 | 0.075746 | -121.9116 | -121.8718 | 6.471 | 6.5665 | 6.671 | 6.5579 | -115.7977 | 0.047861 | 0.13731 | 0.17714 | 0.18348 | -122.0758
4267.9219 | 122.1039 | -0.045776 | 121.8887 | 1.4211e-13 | -0.030205 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0012713 | 0.018117 | 0.032835 | 0.013509 | 6.452 | 6.4756 | 6.3096 | 6.3932 | 6.4841 | 6.5886 | 6.1597 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 6.2055 | -115.4955 | 6.4978 | 6.3554 | 0.14992 | -115.4046 | -115.3001 | -0.081742 | -121.9553 | 0.074296 | -0.015154 | 0.066588 | -121.8521 | -121.8169 | 6.439 | 6.5299 | 6.6344 | 6.5213 | -115.729 | -0.020806 | 0.082376 | 0.11763 | 0.12397 | -122.0163
4269.6406 | 122.049 | -0.07782 | 121.8979 | 1.4211e-13 | -0.029991 | 0.00057691 | -0.0030235 | -0.010168 | 0.0080272 | -0.032811 | -0.0046531 | -0.0019123 | 0.018331 | 0.032408 | 0.013296 | 6.4566 | 6.4893 | 6.3096 | 6.4115 | 6.4887 | 6.5932 | 6.1689 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.12752 | 6.2467 | -115.4864 | 6.5344 | 6.3874 | 0.14076 | -115.4092 | -115.3047 | -0.049698 | -121.9599 | 0.10176 | 0.01689 | 0.066588 | -121.8567 | -121.8215 | 6.4893 | 6.5665 | 6.671 | 6.5671 | -115.729 | 0.015816 | 0.119 | 0.15425 | 0.15602 | -122.0254
4271.4062 | 121.9803 | -0.082397 | 121.9025 | 1.4211e-13 | -0.029777 | 0.00014951 | -0.0032373 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018117 | 0.032622 | 0.013509 | 6.4703 | 6.4984 | 6.3325 | 6.4161 | 6.4979 | 6.6115 | 6.1826 | 0.023941 | 0.087354 | -0.051772 | -0.057425 | 0.0366 | 0.085587 | -0.11836 | 6.265 | -115.4864 | 6.5527 | 6.4149 | 0.14991 | -115.4046 | -115.2909 | -0.035964 | -121.9599 | 0.10634 | 0.030625 | 0.066589 | -121.8659 | -121.8169 | 6.4985 | 6.5803 | 6.6939 | 6.5808 | -115.7199 | 0.024972 | 0.119 | 0.16798 | 0.16975 | -122.0208
4273.125 | 121.9986 | -0.091553 | 121.9345 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0034509 | -0.010168 | 0.0080272 | -0.02518 | -0.0046531 | -0.0019123 | 0.018117 | 0.032835 | 0.013509 | 6.4703 | 6.503 | 6.3371 | 6.4207 | 6.4979 | 6.6024 | 6.1872 | 0.02852 | 0.078197 | -0.056351 | -0.062004 | 0.032021 | 0.07643 | -0.1321 | 6.2787 | -115.5138 | 6.5619 | 6.4286 | 0.14991 | -115.4367 | -115.3321 | -0.040544 | -121.9965 | 0.12007 | 0.035202 | 0.075746 | -121.9025 | -121.8581 | 6.5122 | 6.5894 | 6.6939 | 6.5946 | -115.7473 | 0.029549 | 0.12357 | 0.16798 | 0.16975 | -122.0666
4274.9062 | 121.9849 | -0.068665 | 121.907 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0032373 | -0.0099547 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.018117 | 0.032835 | 0.013509 | 6.4749 | 6.5122 | 6.3417 | 6.4298 | 6.5024 | 6.6207 | 6.1918 | 0.033099 | 0.091933 | -0.06093 | -0.057425 | 0.027442 | 0.071851 | -0.12294 | 6.2604 | -115.4772 | 6.5436 | 6.4103 | 0.14991 | -115.4046 | -115.2864 | -0.054274 | -121.9645 | 0.10176 | 0.007735 | 0.062009 | -121.8796 | -121.8352 | 6.4985 | 6.5711 | 6.6894 | 6.5808 | -115.7153 | 0.01124 | 0.096107 | 0.14052 | 0.1606 | -122.03
4276.6719 | 122.0764 | -0.050354 | 121.9025 | 1.4211e-13 | -0.030205 | 0.00057691 | -0.0036647 | -0.010168 | 0.0080272 | -0.0022892 | -0.0042257 | -0.0019123 | 0.017904 | 0.032835 | 0.013296 | 6.4932 | 6.5168 | 6.3508 | 6.4344 | 6.5162 | 6.6298 | 6.2055 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.081008 | -0.12294 | 6.2558 | -115.4681 | 6.5436 | 6.4012 | 0.14533 | -115.3863 | -115.2726 | -0.072585 | -121.9645 | 0.069716 | -0.005997 | 0.066588 | -121.8659 | -121.8215 | 6.4848 | 6.5665 | 6.6802 | 6.5671 | -115.697 | -0.01165 | 0.086954 | 0.13136 | 0.13313 | -122.0254
4278.4375 | 121.9528 | -0.11444 | 121.9391 | 1.4211e-13 | -0.029991 | 0.00057691 | -0.0030235 | -0.010168 | 0.0080272 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018331 | 0.032835 | 0.013082 | 6.4978 | 6.5213 | 6.3554 | 6.4436 | 6.5162 | 6.6298 | 6.2055 | 0.023941 | 0.091933 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 6.3199 | -115.4955 | 6.6122 | 6.4698 | 0.14991 | -115.4229 | -115.3092 | -0.013077 | -122.0057 | 0.13838 | 0.05809 | 0.071167 | -121.9025 | -121.8672 | 6.558 | 6.6306 | 6.7443 | 6.6358 | -115.7336 | 0.047859 | 0.15104 | 0.18629 | 0.20637 | -122.0666
4280.1562 | 121.9757 | -0.10529 | 121.9208 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0030235 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0019123 | 0.018331 | 0.032835 | 0.013509 | 6.4978 | 6.5397 | 6.3646 | 6.4481 | 6.5299 | 6.6344 | 6.2238 | 0.023941 | 0.078197 | -0.051772 | -0.066582 | 0.041178 | 0.071851 | -0.11836 | 6.3291 | -115.4726 | 6.6031 | 6.4698 | 0.14075 | -115.3909 | -115.2864 | -0.013075 | -121.9874 | 0.12923 | 0.053514 | 0.066589 | -121.8796 | -121.8489 | 6.5534 | 6.6352 | 6.7397 | 6.6449 | -115.697 | 0.038704 | 0.14646 | 0.17714 | 0.18348 | -122.0391
4281.9219 | 122.0627 | -0.059509 | 121.8796 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0032373 | -0.0099547 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0019123 | 0.017904 | 0.033263 | 0.013296 | 6.4978 | 6.5213 | 6.3508 | 6.4344 | 6.5116 | 6.6298 | 6.2055 | 0.019362 | 0.082776 | -0.06093 | -0.057425 | 0.041178 | 0.07643 | -0.12294 | 6.265 | -115.4452 | 6.5573 | 6.4103 | 0.14533 | -115.368 | -115.2497 | -0.06343 | -121.937 | 0.078871 | -0.001421 | 0.062009 | -121.8384 | -121.8031 | 6.4939 | 6.5711 | 6.6894 | 6.5808 | -115.6741 | 0.002084 | 0.10069 | 0.13594 | 0.14228 | -122.0025
4283.6719 | 122.0856 | -0.073242 | 121.9208 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0034509 | -0.010382 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0016987 | 0.017904 | 0.032835 | 0.013082 | 6.4978 | 6.5351 | 6.36 | 6.4436 | 6.5345 | 6.6436 | 6.2192 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.12752 | 6.2925 | -115.4772 | 6.571 | 6.4332 | 0.14075 | -115.3863 | -115.2772 | -0.054276 | -121.9828 | 0.097183 | 0.016891 | 0.071167 | -121.8842 | -121.8443 | 6.5168 | 6.6077 | 6.7168 | 6.6083 | -115.7015 | 0.011238 | 0.10984 | 0.14967 | 0.15602 | -122.0483
4285.375 | 121.994 | -0.09613 | 121.9208 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0032373 | -0.010168 | 0.0076 | -0.0099192 | -0.0042257 | -0.0014849 | 0.018117 | 0.032835 | 0.013082 | 6.5161 | 6.5442 | 6.3737 | 6.4619 | 6.5436 | 6.6527 | 6.233 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.12752 | 6.3291 | -115.4589 | 6.6122 | 6.4698 | 0.14075 | -115.3771 | -115.268 | -0.031388 | -121.9782 | 0.12007 | 0.0352 | 0.066588 | -121.8842 | -121.8443 | 6.558 | 6.6398 | 6.7489 | 6.6404 | -115.6878 | 0.038705 | 0.13273 | 0.17256 | 0.18348 | -122.0483
4287.1406 | 122.0215 | -0.064087 | 121.8887 | 1.4211e-13 | -0.029991 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0012713 | 0.018117 | 0.032622 | 0.013082 | 6.5115 | 6.5442 | 6.3691 | 6.4619 | 6.5345 | 6.6482 | 6.2284 | 0.014784 | 0.082776 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.12294 | 6.2925 | -115.4269 | 6.5756 | 6.4332 | 0.14075 | -115.3542 | -115.2406 | -0.058852 | -121.9507 | 0.078871 | 0.003157 | 0.062009 | -121.843 | -121.8077 | 6.526 | 6.5986 | 6.7122 | 6.6083 | -115.6603 | 0.002083 | 0.10984 | 0.1451 | 0.14686 | -122.0117
4288.9062 | 121.9894 | -0.082397 | 121.9162 | 1.4211e-13 | -0.030205 | -0.00027769 | -0.0034509 | -0.0099547 | 0.0080272 | -0.02518 | -0.0046531 | -0.0014849 | 0.018117 | 0.032835 | 0.013296 | 6.5069 | 6.5397 | 6.3646 | 6.4527 | 6.5391 | 6.639 | 6.2238 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.12752 | 6.3062 | -115.4635 | 6.5893 | 6.447 | 0.14075 | -115.3771 | -115.2772 | -0.045121 | -121.9782 | 0.10634 | 0.021467 | 0.066588 | -121.875 | -121.8443 | 6.5351 | 6.6215 | 6.7214 | 6.622 | -115.6924 | 0.020393 | 0.12357 | 0.15425 | 0.16517 | -122.0437
4290.6094 | 121.9299 | -0.1236 | 121.962 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0032373 | -0.010382 | 0.0080272 | -0.01755 | -0.0042257 | -0.0016987 | 0.017904 | 0.033049 | 0.013296 | 6.5207 | 6.5534 | 6.3737 | 6.4619 | 6.5436 | 6.6527 | 6.233 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12752 | 6.3566 | -115.5001 | 6.6443 | 6.4973 | 0.14075 | -115.4183 | -115.3092 | -0.003922 | -122.024 | 0.14754 | 0.062666 | 0.066588 | -121.9254 | -121.8901 | 6.5855 | 6.6672 | 6.7763 | 6.677 | -115.729 | 0.061592 | 0.1602 | 0.19545 | 0.20637 | -122.0895
4292.375 | 122.0398 | -0.059509 | 121.9116 | 1.4211e-13 | -0.030418 | 0.00036331 | -0.0032373 | -0.0099547 | 0.0080272 | -0.01755 | -0.0046531 | -0.0014849 | 0.018117 | 0.033263 | 0.013723 | 6.5252 | 6.5534 | 6.3783 | 6.471 | 6.5436 | 6.6527 | 6.233 | 0.019362 | 0.082776 | -0.06093 | -0.057425 | 0.041178 | 0.071851 | -0.12752 | 6.2925 | -115.4406 | 6.5848 | 6.4378 | 0.14533 | -115.368 | -115.2589 | -0.068009 | -121.969 | 0.078871 | -0.001421 | 0.066588 | -121.8704 | -121.8398 | 6.5305 | 6.6032 | 6.7122 | 6.6129 | -115.6787 | 0.002084 | 0.10069 | 0.13136 | 0.14228 | -122.0391
4294.1406 | 122.0306 | -0.073242 | 121.8979 | 1.4211e-13 | -0.030418 | 0.00036331 | -0.0034509 | -0.010382 | 0.0073864 | -0.0022892 | -0.0042257 | -0.0016987 | 0.017904 | 0.033049 | 0.013082 | 6.5252 | 6.5534 | 6.3737 | 6.4619 | 6.5482 | 6.6482 | 6.2375 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.081008 | -0.1321 | 6.3108 | -115.436 | 6.5985 | 6.447 | 0.13617 | -115.3497 | -115.2497 | -0.058855 | -121.9645 | 0.097183 | 0.012312 | 0.071167 | -121.8567 | -121.8169 | 6.5351 | 6.6215 | 6.7214 | 6.6266 | -115.6603 | 0.00666 | 0.11442 | 0.15425 | 0.15602 | -122.03
4295.9062 | 122.0673 | -0.059509 | 121.8613 | 1.4211e-13 | -0.030205 | 0.00057691 | -0.0034509 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0016987 | 0.01769 | 0.032835 | 0.012868 | 6.5161 | 6.5488 | 6.3737 | 6.4664 | 6.5482 | 6.6482 | 6.2284 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 6.2879 | -115.3948 | 6.5756 | 6.4332 | 0.14533 | -115.313 | -115.2131 | -0.06343 | -121.9233 | 0.088029 | -0.001421 | 0.062009 | -121.8247 | -121.7894 | 6.526 | 6.6077 | 6.7077 | 6.6083 | -115.6329 | -0.002495 | 0.096109 | 0.13136 | 0.14228 | -121.9842
4297.6719 | 121.9711 | -0.086975 | 121.9299 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017904 | 0.033049 | 0.013509 | 6.5252 | 6.558 | 6.3874 | 6.4664 | 6.5482 | 6.6573 | 6.2421 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.0366 | 0.081008 | -0.12294 | 6.3291 | -115.4635 | 6.6122 | 6.4744 | 0.14533 | -115.3817 | -115.2726 | -0.035964 | -121.9919 | 0.1155 | 0.021466 | 0.05743 | -121.8933 | -121.8489 | 6.5534 | 6.6352 | 6.7443 | 6.6449 | -115.6878 | 0.024971 | 0.12357 | 0.16798 | 0.16975 | -122.0529
4299.3906 | 121.9849 | -0.091553 | 121.8796 | 1.4211e-13 | -0.029991 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.008241 | -0.01755 | -0.0046531 | -0.0014849 | 0.017476 | 0.033049 | 0.013509 | 6.5207 | 6.5534 | 6.3783 | 6.4664 | 6.5482 | 6.6527 | 6.233 | 0.019362 | 0.082776 | -0.051772 | -0.071161 | 0.041178 | 0.07643 | -0.12294 | 6.3245 | -115.4131 | 6.6122 | 6.4698 | 0.14533 | -115.3314 | -115.2268 | -0.031386 | -121.9507 | 0.11091 | 0.039781 | 0.071167 | -121.8384 | -121.8031 | 6.558 | 6.6398 | 6.7443 | 6.6449 | -115.6466 | 0.020392 | 0.13273 | 0.16798 | 0.17433 | -122.0025
4301.1562 | 122.0764 | -0.064087 | 121.8658 | 1.4211e-13 | -0.030418 | 0.00057691 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0019123 | 0.017904 | 0.032835 | 0.013296 | 6.5252 | 6.5488 | 6.3737 | 6.4664 | 6.5436 | 6.6619 | 6.2375 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.032021 | 0.07643 | -0.12752 | 6.3016 | -115.3994 | 6.5893 | 6.4378 | 0.13617 | -115.3222 | -115.2039 | -0.063431 | -121.9233 | 0.088028 | 0.003157 | 0.066588 | -121.8338 | -121.7894 | 6.5305 | 6.6077 | 6.726 | 6.6129 | -115.6283 | 0.006662 | 0.096108 | 0.14052 | 0.14686 | -121.9934
4302.9219 | 121.9391 | -0.10529 | 121.8979 | 1.4211e-13 | -0.029777 | 0.00057691 | -0.0032373 | -0.0099547 | 0.0078136 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.033263 | 0.013296 | 6.5481 | 6.5763 | 6.4012 | 6.4893 | 6.5665 | 6.6802 | 6.2559 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12752 | 6.3611 | -115.4085 | 6.6534 | 6.5065 | 0.14532 | -115.3314 | -115.2177 | -0.022232 | -121.9599 | 0.12923 | 0.044356 | 0.066588 | -121.8613 | -121.826 | 6.5946 | 6.6718 | 6.7855 | 6.6816 | -115.642 | 0.043282 | 0.14189 | 0.17714 | 0.19264 | -122.0254
4304.6875 | 121.9666 | -0.10071 | 121.9162 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0032373 | -0.010382 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0019123 | 0.018117 | 0.032835 | 0.013296 | 6.5481 | 6.5809 | 6.3966 | 6.4893 | 6.5711 | 6.6711 | 6.2604 | 0.02852 | 0.082776 | -0.056351 | -0.057425 | 0.0366 | 0.071851 | -0.11836 | 6.3611 | -115.4269 | 6.6489 | 6.4973 | 0.13617 | -115.3451 | -115.2451 | -0.017653 | -121.9736 | 0.12923 | 0.044357 | 0.06201 | -121.8796 | -121.8443 | 6.59 | 6.6718 | 6.7718 | 6.6816 | -115.6558 | 0.043283 | 0.13731 | 0.17256 | 0.18348 | -122.0346
4306.3906 | 122.0261 | -0.082397 | 121.875 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0036647 | -0.010168 | 0.008241 | -0.0099192 | -0.0046531 | -0.0019123 | 0.018117 | 0.032408 | 0.013509 | 6.5344 | 6.5671 | 6.3874 | 6.4756 | 6.5574 | 6.6665 | 6.2421 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.041178 | 0.081008 | -0.12294 | 6.3245 | -115.3994 | 6.6168 | 6.4698 | 0.14533 | -115.3176 | -115.2085 | -0.040542 | -121.937 | 0.10176 | 0.021467 | 0.062009 | -121.8338 | -121.794 | 6.558 | 6.6398 | 6.7489 | 6.6495 | -115.6329 | 0.020393 | 0.12357 | 0.1634 | 0.16517 | -121.9979
4308.1562 | 121.9437 | -0.10529 | 121.907 | 1.4211e-13 | -0.030418 | -0.00027769 | -0.0034509 | -0.010382 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0014849 | 0.017904 | 0.032835 | 0.013296 | 6.5298 | 6.5625 | 6.3783 | 6.471 | 6.5436 | 6.6573 | 6.2421 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.032021 | 0.081008 | -0.12752 | 6.3474 | -115.436 | 6.6351 | 6.4836 | 0.13617 | -115.3634 | -115.2497 | -0.022232 | -121.969 | 0.12465 | 0.044356 | 0.066588 | -121.875 | -121.826 | 6.5763 | 6.6489 | 6.7626 | 6.6678 | -115.6649 | 0.043282 | 0.13731 | 0.18629 | 0.19264 | -122.0346
4309.9219 | 122.0169 | -0.073242 | 121.8842 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0032373 | -0.0099547 | 0.008241 | -0.01755 | -0.0044395 | -0.0014849 | 0.017904 | 0.032835 | 0.013082 | 6.5298 | 6.5625 | 6.3829 | 6.4664 | 6.5482 | 6.6619 | 6.2375 | 0.033099 | 0.082776 | -0.056351 | -0.057425 | 0.0366 | 0.07643 | -0.12294 | 6.3108 | -115.4177 | 6.6031 | 6.4561 | 0.14533 | -115.3359 | -115.2223 | -0.049697 | -121.9416 | 0.10634 | 0.016891 | 0.066588 | -121.8476 | -121.8077 | 6.5397 | 6.6215 | 6.7351 | 6.6358 | -115.6466 | 0.015817 | 0.10984 | 0.14967 | 0.15602 | -122.0071
4311.625 | 122.0581 | -0.054932 | 121.8796 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0032373 | -0.010168 | 0.0078136 | -0.02518 | -0.0046531 | -0.0019123 | 0.018117 | 0.032622 | 0.012868 | 6.5298 | 6.5625 | 6.3874 | 6.4664 | 6.5528 | 6.6573 | 6.2375 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.1321 | 6.2925 | -115.4131 | 6.5848 | 6.4424 | 0.14991 | -115.3268 | -115.2223 | -0.077165 | -121.9416 | 0.078873 | -0.005998 | 0.071167 | -121.8384 | -121.8077 | 6.5214 | 6.6077 | 6.7122 | 6.6175 | -115.642 | -0.007072 | 0.09611 | 0.12678 | 0.14229 | -122.0117
4313.3906 | 121.9666 | -0.10529 | 121.9116 | 1.4211e-13 | -0.030205 | 0.00036331 | -0.0032373 | -0.010168 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0016987 | 0.017904 | 0.032835 | 0.012868 | 6.5207 | 6.558 | 6.3783 | 6.4664 | 6.5436 | 6.6527 | 6.2375 | 0.02852 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.1321 | 6.3428 | -115.4452 | 6.626 | 6.4836 | 0.14075 | -115.368 | -115.2589 | -0.026811 | -121.9736 | 0.13381 | 0.048935 | 0.075746 | -121.875 | -121.8352 | 6.5717 | 6.6489 | 6.758 | 6.6633 | -115.6741 | 0.043282 | 0.14189 | 0.18172 | 0.19264 | -122.0437
4315.1094 | 122.0398 | -0.073242 | 121.875 | 1.4211e-13 | -0.030418 | -6.4092e-05 | -0.0032373 | -0.010809 | 0.0078136 | -0.01755 | -0.0046531 | -0.0016987 | 0.017904 | 0.033049 | 0.013296 | 6.5344 | 6.5625 | 6.392 | 6.4802 | 6.5528 | 6.6573 | 6.2467 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.041178 | 0.071851 | -0.1321 | 6.3199 | -115.3948 | 6.6076 | 6.4653 | 0.14533 | -115.3222 | -115.2177 | -0.058855 | -121.937 | 0.097183 | 0.007733 | 0.066588 | -121.8338 | -121.8031 | 6.5534 | 6.626 | 6.7306 | 6.6358 | -115.6283 | 0.011238 | 0.11442 | 0.14509 | 0.15602 | -122.0071
4316.875 | 122.0215 | -0.07782 | 121.8796 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0032373 | -0.010382 | 0.008241 | -0.0099192 | -0.0044395 | -0.0016987 | 0.01769 | 0.033049 | 0.013082 | 6.5344 | 6.5763 | 6.3966 | 6.4893 | 6.5574 | 6.6619 | 6.2559 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.11836 | 6.3337 | -115.3902 | 6.6122 | 6.4744 | 0.14075 | -115.3222 | -115.2177 | -0.040541 | -121.9416 | 0.10176 | 0.01689 | 0.057431 | -121.8384 | -121.8031 | 6.5672 | 6.6352 | 6.7397 | 6.6541 | -115.6237 | 0.015816 | 0.119 | 0.15425 | 0.16517 | -121.9979
4318.5781 | 121.9116 | -0.11444 | 121.9162 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0034509 | -0.010168 | 0.008241 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.033049 | 0.013082 | 6.571 | 6.6038 | 6.4332 | 6.5031 | 6.5894 | 6.7031 | 6.2788 | 0.033099 | 0.078197 | -0.056351 | -0.062004 | 0.041178 | 0.07643 | -0.12294 | 6.3932 | -115.4131 | 6.6855 | 6.5477 | 0.15448 | -115.3268 | -115.2131 | -0.008498 | -121.9782 | 0.14754 | 0.05809 | 0.066588 | -121.875 | -121.8398 | 6.6175 | 6.7039 | 6.8175 | 6.7182 | -115.6374 | 0.052437 | 0.15562 | 0.19087 | 0.19264 | -122.0391
4320.2969 | 122.0078 | -0.082397 | 121.8933 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.033049 | 0.013082 | 6.5619 | 6.5992 | 6.4241 | 6.5031 | 6.5894 | 6.6939 | 6.2833 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.081008 | -0.12752 | 6.3657 | -115.3902 | 6.6443 | 6.5065 | 0.14074 | -115.3039 | -115.1994 | -0.045121 | -121.9553 | 0.10634 | 0.021467 | 0.066588 | -121.8567 | -121.8123 | 6.5855 | 6.6718 | 6.7763 | 6.6816 | -115.61 | 0.020393 | 0.119 | 0.1634 | 0.16975 | -122.0208
4322.0625 | 121.9345 | -0.10986 | 121.9437 | 1.4211e-13 | -0.030418 | -6.4092e-05 | -0.0036647 | -0.010168 | 0.0078136 | -0.01755 | -0.0046531 | -0.0016987 | 0.018117 | 0.033049 | 0.013296 | 6.6626 | 6.677 | 6.5111 | 6.5901 | 6.681 | 6.7809 | 6.3749 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.032021 | 0.07643 | -0.11836 | 6.4848 | -115.3536 | 6.7725 | 6.6209 | 0.13615 | -115.2627 | -115.1627 | -0.008498 | -122.0011 | 0.13838 | 0.048933 | 0.057431 | -121.9116 | -121.8672 | 6.6999 | 6.7909 | 6.8908 | 6.7869 | -115.5688 | 0.052438 | 0.14188 | 0.18629 | 0.19722 | -122.062
4323.8438 | 122.0581 | -0.073242 | 121.8658 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0036647 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.017904 | 0.033263 | 0.013082 | 7.1662 | 7.2081 | 7.0193 | 7.1074 | 7.1847 | 7.2892 | 6.8374 | 0.02852 | 0.078197 | -0.065509 | -0.071161 | 0.041178 | 0.067272 | -0.12752 | 6.9106 | -114.7584 | 7.2395 | 7.0925 | 0.18187 | -114.6812 | -114.5767 | -0.054276 | -121.937 | 0.10176 | 0.007733 | 0.062009 | -121.8247 | -121.7986 | 7.1807 | 7.2579 | 7.3624 | 7.2814 | -115.0285 | 0.002081 | 0.11442 | 0.14051 | 0.15144 | -121.9934
4325.5625 | 121.9528 | -0.10529 | 121.8933 | 1.4211e-13 | -0.030205 | 0.00036331 | -0.0036647 | -0.010382 | 0.0078136 | -0.01755 | -0.0044395 | -0.0019123 | 0.018117 | 0.032835 | 0.013082 | 7.1845 | 7.2173 | 7.033 | 7.112 | 7.1893 | 7.3029 | 6.8465 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.1321 | 6.9518 | -114.7813 | 7.2898 | 7.1383 | 0.18645 | -114.704 | -114.5904 | -0.026811 | -121.9553 | 0.12923 | 0.048935 | 0.075746 | -121.8567 | -121.8169 | 7.2173 | 7.2946 | 7.4082 | 7.3226 | -115.0468 | 0.043282 | 0.14189 | 0.18172 | 0.18806 | -122.0254
4327.3281 | 122.0169 | -0.050354 | 121.8704 | 1.4211e-13 | -0.030418 | 0.00036331 | -0.0032373 | -0.0099547 | 0.0076 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018545 | 0.032835 | 0.013082 | 7.1754 | 7.2219 | 7.033 | 7.1074 | 7.1847 | 7.2937 | 6.8511 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.041178 | 0.071851 | -0.11836 | 6.9015 | -114.763 | 7.2257 | 7.0833 | 0.18187 | -114.6857 | -114.5767 | -0.068007 | -121.9324 | 0.078874 | -0.010576 | 0.057431 | -121.8292 | -121.7986 | 7.1578 | 7.235 | 7.3441 | 7.2722 | -115.0193 | -0.01165 | 0.091532 | 0.12221 | 0.13771 | -121.9888
4329.0938 | 121.8887 | -0.11444 | 121.8704 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0030235 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0014849 | 0.017904 | 0.033049 | 0.013296 | 7.18 | 7.2219 | 7.0513 | 7.112 | 7.1938 | 7.3121 | 6.8557 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.11836 | 6.9701 | -114.7584 | 7.2944 | 7.1657 | 0.1956 | -114.6766 | -114.5584 | -0.00392 | -121.9324 | 0.13838 | 0.05809 | 0.06201 | -121.8338 | -121.794 | 7.2264 | 7.3083 | 7.4265 | 7.3363 | -115.0147 | 0.052437 | 0.15104 | 0.19087 | 0.2018 | -121.9888
4330.7969 | 121.9482 | -0.082397 | 121.8704 | 1.4211e-13 | -0.030418 | 0.00057691 | -0.0034509 | -0.010168 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0016987 | 0.017904 | 0.033049 | 0.013082 | 7.1845 | 7.2219 | 7.033 | 7.112 | 7.1847 | 7.2937 | 6.8511 | 0.019362 | 0.087354 | -0.06093 | -0.057425 | 0.045757 | 0.07643 | -0.12294 | 6.9335 | -114.7584 | 7.2669 | 7.1154 | 0.18187 | -114.6857 | -114.5767 | -0.040542 | -121.9278 | 0.10176 | 0.021467 | 0.062009 | -121.8247 | -121.794 | 7.1944 | 7.2671 | 7.3761 | 7.3043 | -115.0193 | 0.024972 | 0.12815 | 0.15883 | 0.16975 | -121.9934
4332.5156 | 121.9849 | -0.073242 | 121.8338 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0032373 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0019123 | 0.017904 | 0.033049 | 0.013082 | 7.1754 | 7.2081 | 7.0238 | 7.1074 | 7.1893 | 7.2983 | 6.8465 | 0.023941 | 0.087354 | -0.070087 | -0.062004 | 0.0366 | 0.081008 | -0.11836 | 6.9198 | -114.7264 | 7.2486 | 7.0971 | 0.17729 | -114.6445 | -114.5355 | -0.045119 | -121.8958 | 0.097183 | 0.003155 | 0.048274 | -121.7972 | -121.7528 | 7.1807 | 7.2625 | 7.3716 | 7.2814 | -114.9873 | 0.011238 | 0.10984 | 0.15425 | 0.1606 | -121.9522
4334.2812 | 121.9437 | -0.09613 | 121.8796 | 1.4211e-13 | -0.029991 | 0.00014951 | -0.0032373 | -0.010382 | 0.0078136 | -0.01755 | -0.0044395 | -0.0021259 | 0.01769 | 0.032835 | 0.013082 | 7.1525 | 7.1944 | 7.0009 | 7.08 | 7.1664 | 7.2709 | 6.8191 | 0.023941 | 0.091933 | -0.056351 | -0.062004 | 0.041178 | 0.081008 | -0.12294 | 6.9152 | -114.7996 | 7.2486 | 7.0971 | 0.18187 | -114.7132 | -114.6087 | -0.026809 | -121.9416 | 0.12007 | 0.039779 | 0.066588 | -121.8384 | -121.7986 | 7.1761 | 7.2625 | 7.367 | 7.2905 | -115.0605 | 0.034126 | 0.13731 | 0.17714 | 0.18806 | -122.0025
4336.0625 | 121.9528 | -0.09613 | 121.8887 | 1.4211e-13 | -0.029991 | 0.00036331 | -0.0034509 | -0.0099547 | 0.0080272 | -0.01755 | -0.0046531 | -0.0019123 | 0.017904 | 0.033263 | 0.012868 | 7.1525 | 7.1898 | 7.0055 | 7.0891 | 7.1664 | 7.2709 | 6.8282 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.041178 | 0.07643 | -0.12752 | 6.9244 | -114.7996 | 7.2486 | 7.1016 | 0.17729 | -114.7224 | -114.6179 | -0.031388 | -121.9462 | 0.12007 | 0.0352 | 0.066588 | -121.8476 | -121.8123 | 7.1852 | 7.2625 | 7.367 | 7.2859 | -115.0605 | 0.038705 | 0.13731 | 0.17256 | 0.18348 | -122.0163
4337.7812 | 121.9162 | -0.11902 | 121.8933 | 1.4211e-13 | -0.029991 | 0.00057691 | -0.0032373 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017904 | 0.032835 | 0.012868 | 7.1433 | 7.1715 | 6.9964 | 7.08 | 7.1526 | 7.2617 | 6.8145 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 6.9335 | -114.8134 | 7.2624 | 7.1154 | 0.18187 | -114.7407 | -114.6316 | -0.00392 | -121.9599 | 0.14296 | 0.058089 | 0.062009 | -121.8521 | -121.8169 | 7.199 | 7.2717 | 7.3807 | 7.2905 | -115.0788 | 0.052437 | 0.1602 | 0.19545 | 0.20637 | -122.0162
4339.5625 | 121.9894 | -0.059509 | 121.8842 | 1.4211e-13 | -0.030205 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0080272 | -0.01755 | -0.0048667 | -0.0019123 | 0.018117 | 0.033049 | 0.012868 | 7.1342 | 7.1715 | 6.9964 | 7.0662 | 7.1435 | 7.2571 | 6.8099 | 0.019362 | 0.082776 | -0.070087 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 6.8694 | -114.8179 | 7.1937 | 7.0559 | 0.18645 | -114.7407 | -114.627 | -0.06343 | -121.9462 | 0.078871 | -0.010578 | 0.052852 | -121.8476 | -121.8077 | 7.1257 | 7.203 | 7.3166 | 7.231 | -115.0742 | -0.002495 | 0.096109 | 0.13594 | 0.14228 | -122.0071
4341.3438 | 122.049 | -0.050354 | 121.8384 | 1.4211e-13 | -0.030205 | 0.00057691 | -0.0030235 | -0.0099547 | 0.0076 | -0.0022892 | -0.0048667 | -0.0019123 | 0.017904 | 0.032835 | 0.013082 | 7.1479 | 7.1807 | 7.0055 | 7.0754 | 7.1618 | 7.2571 | 6.8236 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.07643 | -0.12752 | 6.874 | -114.763 | 7.1983 | 7.0559 | 0.18187 | -114.6766 | -114.5813 | -0.077164 | -121.9004 | 0.074295 | -0.005997 | 0.071167 | -121.8018 | -121.7619 | 7.1257 | 7.2122 | 7.3075 | 7.231 | -115.0147 | -0.01165 | 0.086954 | 0.12678 | 0.13771 | -121.9659
4343.0469 | 122.0306 | -0.050354 | 121.843 | 1.4211e-13 | -0.030418 | 0.00036331 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0014849 | 0.018117 | 0.033263 | 0.012655 | 7.1433 | 7.1761 | 6.9964 | 7.0708 | 7.1526 | 7.2617 | 6.8145 | 0.023941 | 0.091933 | -0.065509 | -0.057425 | 0.0366 | 0.071851 | -0.1321 | 6.8648 | -114.7722 | 7.1937 | 7.0467 | 0.18187 | -114.6903 | -114.5813 | -0.081743 | -121.9004 | 0.074295 | -0.015155 | 0.066588 | -121.8064 | -121.7711 | 7.1211 | 7.203 | 7.312 | 7.2264 | -115.0285 | -0.007071 | 0.086954 | 0.12221 | 0.14229 | -121.9751
4344.8125 | 121.9162 | -0.091553 | 121.8658 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0032373 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0021259 | 0.01769 | 0.033049 | 0.012868 | 7.1342 | 7.1669 | 6.9918 | 7.0662 | 7.1435 | 7.248 | 6.8099 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.027442 | 0.081008 | -0.12294 | 6.9015 | -114.7996 | 7.2257 | 7.0833 | 0.18187 | -114.7224 | -114.6179 | -0.031386 | -121.9278 | 0.12007 | 0.030623 | 0.062009 | -121.8384 | -121.7848 | 7.1578 | 7.235 | 7.3395 | 7.2585 | -115.0559 | 0.029549 | 0.11899 | 0.17256 | 0.17891 | -121.9888
4346.5312 | 122.0306 | -0.059509 | 121.8246 | 1.4211e-13 | -0.030205 | 0.00036331 | -0.0030235 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.01769 | 0.033049 | 0.012655 | 7.1433 | 7.1669 | 6.9918 | 7.0708 | 7.1481 | 7.2571 | 6.8099 | 0.019362 | 0.091933 | -0.06093 | -0.052847 | 0.027442 | 0.081008 | -0.11836 | 6.8694 | -114.7538 | 7.2028 | 7.0513 | 0.18187 | -114.6766 | -114.5675 | -0.058852 | -121.8775 | 0.078871 | -0.001421 | 0.057431 | -121.7972 | -121.7436 | 7.1303 | 7.2076 | 7.3166 | 7.2264 | -115.0147 | 0.006662 | 0.086951 | 0.14052 | 0.15144 | -121.943
4348.2969 | 121.9116 | -0.10986 | 121.8521 | 1.4211e-13 | -0.030632 | 0.00079051 | -0.0038783 | -0.010168 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0019123 | 0.017904 | 0.033263 | 0.013082 | 7.1479 | 7.1807 | 6.9964 | 7.0708 | 7.1481 | 7.2571 | 6.8145 | 0.019362 | 0.087354 | -0.065509 | -0.062004 | 0.041178 | 0.071851 | -0.12294 | 6.9243 | -114.7813 | 7.2578 | 7.1062 | 0.18187 | -114.7041 | -114.595 | -0.013076 | -121.9141 | 0.12923 | 0.044354 | 0.05743 | -121.8109 | -121.7803 | 7.1807 | 7.2579 | 7.367 | 7.2905 | -115.0376 | 0.047859 | 0.15104 | 0.18171 | 0.19722 | -121.9751
4350 | 121.9345 | -0.091553 | 121.8842 | 1.4211e-13 | -0.030418 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018331 | 0.033263 | 0.012868 | 7.1433 | 7.1807 | 6.9964 | 7.0754 | 7.1526 | 7.2525 | 6.8145 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.071851 | -0.1321 | 6.906 | -114.8088 | 7.2349 | 7.0879 | 0.18187 | -114.7315 | -114.6316 | -0.040544 | -121.9416 | 0.11549 | 0.030623 | 0.071167 | -121.8476 | -121.8123 | 7.1669 | 7.2442 | 7.3441 | 7.2722 | -115.0697 | 0.034128 | 0.12815 | 0.1634 | 0.17891 | -122.0163
4351.7656 | 122.0169 | -0.041199 | 121.8613 | 1.4211e-13 | -0.030205 | 0.00036331 | -0.0034509 | -0.010168 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018117 | 0.032835 | 0.012868 | 7.1479 | 7.1852 | 7.0055 | 7.08 | 7.1526 | 7.2571 | 6.8236 | 0.02852 | 0.082776 | -0.056351 | -0.057425 | 0.0366 | 0.07643 | -0.12752 | 6.8648 | -114.7813 | 7.1891 | 7.0467 | 0.18187 | -114.7086 | -114.6042 | -0.086319 | -121.9187 | 0.069719 | -0.015152 | 0.071167 | -121.8247 | -121.7848 | 7.1212 | 7.1938 | 7.2983 | 7.2264 | -115.0376 | -0.016226 | 0.077799 | 0.11763 | 0.12398 | -121.9888
4353.5312 | 121.9299 | -0.086975 | 121.875 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0032373 | -0.010168 | 0.008241 | -0.01755 | -0.0050803 | -0.0014849 | 0.018117 | 0.033049 | 0.013082 | 7.1525 | 7.1898 | 7.0101 | 7.0845 | 7.1572 | 7.2663 | 6.8191 | 0.02852 | 0.087354 | -0.06093 | -0.052847 | 0.0366 | 0.07643 | -0.11836 | 6.906 | -114.7905 | 7.2395 | 7.0971 | 0.19103 | -114.7178 | -114.6087 | -0.031386 | -121.9278 | 0.1155 | 0.026045 | 0.057431 | -121.8384 | -121.7986 | 7.1715 | 7.2442 | 7.3532 | 7.2768 | -115.0559 | 0.034128 | 0.12357 | 0.1634 | 0.17433 | -121.9934
4355.2969 | 121.994 | -0.045776 | 121.8338 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0046531 | -0.0016987 | 0.01769 | 0.032835 | 0.012868 | 7.1388 | 7.1761 | 6.9918 | 7.0616 | 7.1389 | 7.2617 | 6.8008 | 0.023941 | 0.091933 | -0.056351 | -0.052847 | 0.0366 | 0.067272 | -0.12294 | 6.8465 | -114.7722 | 7.1845 | 7.0376 | 0.19103 | -114.6949 | -114.5721 | -0.077163 | -121.8866 | 0.069717 | -0.010575 | 0.066588 | -121.7972 | -121.7665 | 7.1074 | 7.1847 | 7.3075 | 7.2219 | -115.033 | -0.007071 | 0.082376 | 0.11305 | 0.13771 | -121.9567
4357.0156 | 122.0032 | -0.059509 | 121.8292 | 1.4211e-13 | -0.030632 | 0.00057691 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0014849 | 0.01769 | 0.033263 | 0.012655 | 7.1388 | 7.1715 | 6.9872 | 7.0662 | 7.1481 | 7.2525 | 6.8053 | 0.037677 | 0.091933 | -0.065509 | -0.066582 | 0.027442 | 0.085587 | -0.12752 | 6.8648 | -114.763 | 7.1983 | 7.0467 | 0.18187 | -114.6812 | -114.5767 | -0.068009 | -121.8958 | 0.097186 | -0.006 | 0.062009 | -121.8018 | -121.7436 | 7.1257 | 7.2076 | 7.312 | 7.231 | -115.0239 | -0.007073 | 0.086951 | 0.1451 | 0.15144 | -121.9567
4358.7969 | 121.962 | -0.07782 | 121.8155 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0021259 | 0.018117 | 0.032835 | 0.013296 | 7.1296 | 7.1623 | 6.978 | 7.0571 | 7.1343 | 7.248 | 6.8053 | 0.019362 | 0.078197 | -0.06093 | -0.048268 | 0.0366 | 0.071851 | -0.12294 | 6.8831 | -114.7584 | 7.2074 | 7.0559 | 0.17272 | -114.6812 | -114.5675 | -0.045119 | -121.8638 | 0.097182 | 0.01689 | 0.062009 | -121.7789 | -121.7436 | 7.1349 | 7.2121 | 7.3258 | 7.2402 | -115.0102 | 0.029552 | 0.11442 | 0.14967 | 0.15602 | -121.9384
4360.5156 | 121.994 | -0.050354 | 121.7972 | 1.4211e-13 | -0.030205 | 0.00014951 | -0.0030235 | -0.010595 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0019123 | 0.017904 | 0.033263 | 0.012655 | 7.0655 | 7.0937 | 6.9231 | 6.9884 | 7.0794 | 7.1793 | 6.7504 | 0.023941 | 0.082776 | -0.06093 | -0.052847 | 0.0366 | 0.067272 | -0.12752 | 6.8007 | -114.8088 | 7.1159 | 6.9735 | 0.17272 | -114.7178 | -114.6179 | -0.077164 | -121.85 | 0.074295 | -0.010576 | 0.066588 | -121.7606 | -121.7299 | 7.0387 | 7.1297 | 7.2296 | 7.144 | -115.0468 | -0.002493 | 0.086954 | 0.11763 | 0.13313 | -121.9247
4362.2969 | 121.9986 | -0.054932 | 121.8201 | 1.4211e-13 | -0.030632 | 0.00036331 | -0.0032373 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0014849 | 0.017476 | 0.033049 | 0.012868 | 3.2425 | 3.2751 | 3.1643 | 3.2387 | 3.3201 | 3.434 | 3.0552 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.0366 | 0.07643 | -0.12294 | 3.1101 | -118.5814 | 3.2975 | 3.2193 | 0.10915 | -118.5 | -118.3861 | -0.068007 | -121.8821 | 0.078873 | -0.010577 | 0.05743 | -121.7835 | -121.7436 | 3.2936 | 3.375 | 3.4889 | 3.33 | -118.7649 | -0.007072 | 0.091532 | 0.13136 | 0.13771 | -121.943
4364.0625 | 121.9025 | -0.10986 | 121.8887 | 1.4211e-13 | -0.030846 | 0.00036331 | -0.0034509 | -0.010382 | 0.0078136 | -0.01755 | -0.0044395 | -0.0014849 | 0.017904 | 0.033049 | 0.013082 | 3.2563 | 3.2797 | 3.1781 | 3.2387 | 3.3201 | 3.4294 | 3.0735 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.071851 | -0.12294 | 3.1834 | -118.65 | 3.3661 | 3.2879 | 0.10457 | -118.5687 | -118.4593 | -0.013076 | -121.9507 | 0.13838 | 0.048933 | 0.062009 | -121.8521 | -121.8169 | 3.3485 | 3.4299 | 3.5393 | 3.3895 | -118.8152 | 0.047859 | 0.14646 | 0.18171 | 0.19722 | -122.0117
4365.7656 | 122.0261 | -0.073242 | 121.8658 | 1.4211e-13 | -0.030632 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0078136 | 0.0053413 | -0.0046531 | -0.0014849 | 0.017904 | 0.033049 | 0.013082 | 3.2517 | 3.2751 | 3.1689 | 3.2387 | 3.3109 | 3.4248 | 3.0552 | 0.023941 | 0.082776 | -0.056351 | -0.052847 | 0.041178 | 0.081008 | -0.11836 | 3.1284 | -118.6272 | 3.3249 | 3.2422 | 0.11373 | -118.5549 | -118.441 | -0.045119 | -121.9187 | 0.097183 | 0.016891 | 0.06201 | -121.8247 | -121.7848 | 3.3119 | 3.3842 | 3.4981 | 3.3483 | -118.8107 | 0.020395 | 0.11442 | 0.15425 | 0.15602 | -121.9842
4367.5469 | 122.0627 | -0.041199 | 121.8842 | 1.4211e-13 | -0.030418 | 0.00036331 | -0.0032373 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0014849 | 0.017904 | 0.033263 | 0.012868 | 3.2471 | 3.2751 | 3.1689 | 3.2341 | 3.3155 | 3.434 | 3.0689 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.0366 | 0.07643 | -0.12752 | 3.1101 | -118.65 | 3.2883 | 3.2101 | 0.09999 | -118.5687 | -118.4502 | -0.086319 | -121.9462 | 0.06514 | -0.02431 | 0.062009 | -121.8476 | -121.8077 | 3.2753 | 3.3567 | 3.4752 | 3.3163 | -118.8152 | -0.020805 | 0.077799 | 0.11763 | 0.12398 | -122.0117
4369.25 | 121.9757 | -0.086975 | 121.9345 | 1.4211e-13 | -0.030632 | -6.4092e-05 | -0.0032373 | -0.010168 | 0.0078136 | -0.01755 | -0.0046531 | -0.0021259 | 0.018117 | 0.032835 | 0.012868 | 3.2471 | 3.2751 | 3.1689 | 3.2387 | 3.3155 | 3.4248 | 3.0598 | 0.033099 | 0.087354 | -0.065509 | -0.057425 | 0.032021 | 0.07643 | -0.12752 | 3.1467 | -118.6958 | 3.3341 | 3.2559 | 0.10915 | -118.619 | -118.5097 | -0.040543 | -121.9919 | 0.12007 | 0.021466 | 0.062009 | -121.9025 | -121.8581 | 3.3257 | 3.4025 | 3.5118 | 3.3621 | -118.8747 | 0.02955 | 0.119 | 0.1634 | 0.17433 | -122.062
4371.0156 | 121.9803 | -0.11444 | 121.9162 | 1.4211e-13 | -0.030418 | 0.00036331 | -0.0030235 | -0.010382 | 0.0073864 | -0.01755 | -0.0046531 | -0.0019123 | 0.017904 | 0.032835 | 0.012868 | 3.2471 | 3.2751 | 3.1643 | 3.2387 | 3.3155 | 3.4248 | 3.0643 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.12752 | 3.1788 | -118.6775 | 3.3616 | 3.2788 | 0.099991 | -118.6007 | -118.4914 | -0.013077 | -121.9736 | 0.14296 | 0.053511 | 0.066588 | -121.8796 | -121.8398 | 3.3531 | 3.4299 | 3.5393 | 3.3895 | -118.8519 | 0.057016 | 0.15104 | 0.19087 | 0.2018 | -122.0437
4372.7188 | 121.994 | -0.073242 | 121.9299 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0034509 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0021259 | 0.017904 | 0.032835 | 0.013296 | 3.2425 | 3.266 | 3.1643 | 3.2295 | 3.3109 | 3.4202 | 3.0552 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.032021 | 0.07643 | -0.12294 | 3.1284 | -118.7004 | 3.3158 | 3.2376 | 0.10915 | -118.619 | -118.5097 | -0.049697 | -121.9874 | 0.097183 | 0.016891 | 0.066588 | -121.8979 | -121.8535 | 3.3028 | 3.3842 | 3.4935 | 3.3392 | -118.8747 | 0.015817 | 0.10526 | 0.14967 | 0.1606 | -122.0529
4374.4844 | 122.049 | -0.059509 | 121.9025 | 1.4211e-13 | -0.030632 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0080272 | -0.0099192 | -0.0046531 | -0.0016987 | 0.018117 | 0.033049 | 0.012868 | 3.2425 | 3.2751 | 3.1689 | 3.2387 | 3.3247 | 3.4294 | 3.0598 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.07643 | -0.1321 | 3.1193 | -118.6638 | 3.3021 | 3.2284 | 0.10915 | -118.5778 | -118.4731 | -0.072588 | -121.9599 | 0.08345 | -0.001421 | 0.071167 | -121.8659 | -121.826 | 3.2982 | 3.3842 | 3.4889 | 3.3346 | -118.8427 | 0.002084 | 0.096109 | 0.13594 | 0.14686 | -122.0346
4376.2031 | 122.0306 | -0.073242 | 121.9162 | 1.4211e-13 | -0.030846 | 0.00036331 | -0.0034509 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0019123 | 0.017904 | 0.033049 | 0.012868 | 3.2563 | 3.2934 | 3.1827 | 3.2433 | 3.3247 | 3.4386 | 3.0643 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.0366 | 0.085587 | -0.12752 | 3.1376 | -118.6729 | 3.3295 | 3.2559 | 0.1183 | -118.5915 | -118.4776 | -0.054276 | -121.9736 | 0.097183 | 0.012312 | 0.066588 | -121.8796 | -121.8306 | 3.3165 | 3.3979 | 3.5118 | 3.3667 | -118.8519 | 0.015817 | 0.10984 | 0.15883 | 0.1606 | -122.0437
4377.9688 | 121.962 | -0.13275 | 121.9482 | 1.4211e-13 | -0.030632 | 0.00057691 | -0.0034509 | -0.010382 | 0.0076 | -0.01755 | -0.0042257 | -0.0012713 | 0.017904 | 0.033049 | 0.012868 | 3.2609 | 3.2888 | 3.1781 | 3.2433 | 3.3155 | 3.4294 | 3.0643 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.081008 | -0.12752 | 3.1971 | -118.705 | 3.3936 | 3.3108 | 0.11373 | -118.6327 | -118.5188 | 0.005233 | -122.0057 | 0.16127 | 0.071821 | 0.066588 | -121.9116 | -121.8672 | 3.376 | 3.4483 | 3.5622 | 3.4216 | -118.8839 | 0.075326 | 0.16935 | 0.21376 | 0.21553 | -122.0758
4379.75 | 121.9711 | -0.10986 | 121.9803 | 1.4211e-13 | -0.030632 | 0.00036331 | -0.0032373 | -0.0099547 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0019123 | 0.017904 | 0.033049 | 0.012868 | 3.2563 | 3.2888 | 3.1689 | 3.2433 | 3.3201 | 3.434 | 3.0689 | 0.02852 | 0.096512 | -0.06093 | -0.057425 | 0.041178 | 0.07643 | -0.12752 | 3.1788 | -118.737 | 3.3661 | 3.2788 | 0.09999 | -118.6602 | -118.5463 | -0.017655 | -122.0377 | 0.13838 | 0.048933 | 0.066588 | -121.9391 | -121.9039 | 3.3531 | 3.4299 | 3.5438 | 3.3987 | -118.9114 | 0.052438 | 0.15104 | 0.18629 | 0.20638 | -122.1078
4381.4531 | 122.0032 | -0.10071 | 121.9666 | 1.4211e-13 | -0.030632 | 0.00036331 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0014849 | 0.01769 | 0.033263 | 0.012868 | 3.2471 | 3.2843 | 3.1689 | 3.2295 | 3.3201 | 3.4248 | 3.0643 | 0.033099 | 0.087354 | -0.06093 | -0.057425 | 0.041178 | 0.081008 | -0.1321 | 3.1651 | -118.737 | 3.3478 | 3.2696 | 0.10457 | -118.6465 | -118.5417 | -0.031389 | -122.024 | 0.13381 | 0.039778 | 0.071167 | -121.9254 | -121.8855 | 3.3302 | 3.4208 | 3.5255 | 3.385 | -118.9022 | 0.043283 | 0.14189 | 0.18172 | 0.18806 | -122.0987
4383.2188 | 122.0718 | -0.059509 | 121.9254 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0034509 | -0.010168 | 0.0076 | -0.0022892 | -0.0044395 | -0.0016987 | 0.018117 | 0.033263 | 0.013082 | 3.2425 | 3.2705 | 3.1598 | 3.225 | 3.3018 | 3.4157 | 3.0598 | 0.019362 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.071851 | -0.12752 | 3.1193 | -118.7004 | 3.3021 | 3.2193 | 0.099992 | -118.6236 | -118.5097 | -0.068009 | -121.9874 | 0.078871 | 0.003158 | 0.071167 | -121.8888 | -121.8535 | 3.2845 | 3.3613 | 3.4752 | 3.33 | -118.8656 | -0.002495 | 0.096109 | 0.13136 | 0.14686 | -122.0529
4384.9844 | 122.0306 | -0.091553 | 121.9666 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0036647 | -0.010168 | 0.008241 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.033049 | 0.012868 | 3.2563 | 3.2934 | 3.1872 | 3.2478 | 3.3247 | 3.4386 | 3.0735 | 0.02852 | 0.087354 | -0.065509 | -0.062004 | 0.041178 | 0.081008 | -0.12752 | 3.1651 | -118.7187 | 3.3478 | 3.2788 | 0.11372 | -118.6419 | -118.528 | -0.035965 | -122.0286 | 0.12007 | 0.026044 | 0.062009 | -121.9254 | -121.8855 | 3.3394 | 3.4162 | 3.5301 | 3.385 | -118.893 | 0.029549 | 0.13273 | 0.17256 | 0.17891 | -122.0941
4386.7656 | 122.0627 | -0.073242 | 121.9666 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0014849 | 0.017476 | 0.032835 | 0.012868 | 3.2654 | 3.2797 | 3.1872 | 3.2433 | 3.3247 | 3.434 | 3.0598 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.027442 | 0.07643 | -0.11836 | 3.133 | -118.7233 | 3.3387 | 3.2605 | 0.12746 | -118.6419 | -118.5326 | -0.045119 | -122.024 | 0.097183 | 0.012312 | 0.057431 | -121.9391 | -121.8901 | 3.3165 | 3.3979 | 3.5072 | 3.3529 | -118.9068 | 0.015817 | 0.10068 | 0.14967 | 0.15602 | -122.0849
4388.5 | 122.0901 | -0.082397 | 121.9757 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0048667 | -0.0014849 | 0.018331 | 0.033049 | 0.012655 | 3.2471 | 3.2751 | 3.1689 | 3.225 | 3.3155 | 3.4248 | 3.0552 | 0.02852 | 0.091933 | -0.06093 | -0.062004 | 0.032021 | 0.081008 | -0.12294 | 3.1376 | -118.7508 | 3.3295 | 3.2513 | 0.11373 | -118.6602 | -118.5509 | -0.040542 | -122.0377 | 0.11092 | 0.021467 | 0.062009 | -121.9437 | -121.8947 | 3.3073 | 3.3979 | 3.5072 | 3.3575 | -118.9205 | 0.020393 | 0.11442 | 0.1634 | 0.17433 | -122.0986
4390.2656 | 121.9894 | -0.09613 | 121.9803 | 1.4211e-13 | -0.031273 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.01769 | 0.033263 | 0.013082 | 3.2517 | 3.2797 | 3.1643 | 3.2295 | 3.3201 | 3.4248 | 3.0598 | 0.023941 | 0.091933 | -0.06093 | -0.057425 | 0.041178 | 0.071851 | -0.12294 | 3.1559 | -118.7508 | 3.3478 | 3.2605 | 0.10457 | -118.6602 | -118.5555 | -0.026809 | -122.0377 | 0.12007 | 0.0352 | 0.062009 | -121.9391 | -121.9084 | 3.3257 | 3.4162 | 3.521 | 3.3758 | -118.9205 | 0.038705 | 0.13731 | 0.16798 | 0.18806 | -122.1032
4392.0312 | 122.1222 | -0.073242 | 121.9482 | 1.4211e-13 | -0.030846 | 0.00036331 | -0.0034509 | -0.010168 | 0.0076 | -0.01755 | -0.0044395 | -0.0019123 | 0.017904 | 0.033263 | 0.012655 | 3.2838 | 3.3163 | 3.1964 | 3.2707 | 3.3476 | 3.4569 | 3.0964 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.041178 | 0.071851 | -0.12294 | 3.1696 | -118.6775 | 3.357 | 3.2696 | 0.099986 | -118.6007 | -118.4914 | -0.049697 | -122.0102 | 0.097183 | 0.007733 | 0.05743 | -121.9071 | -121.8764 | 3.344 | 3.4208 | 3.5301 | 3.3896 | -118.8518 | 0.011238 | 0.11442 | 0.14509 | 0.15602 | -122.0712
4393.7344 | 122.1268 | -0.050354 | 121.9437 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0036647 | -0.010168 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0016987 | 0.017904 | 0.033049 | 0.013082 | 3.2929 | 3.3163 | 3.2055 | 3.2662 | 3.3521 | 3.4615 | 3.0964 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.041178 | 0.081008 | -0.1321 | 3.1468 | -118.6775 | 3.3433 | 3.2559 | 0.10914 | -118.5915 | -118.4822 | -0.081743 | -122.0011 | 0.074295 | -0.019733 | 0.06201 | -121.9025 | -121.8627 | 3.3165 | 3.4025 | 3.5118 | 3.3667 | -118.8473 | -0.007071 | 0.091532 | 0.13136 | 0.13313 | -122.0758
4395.4844 | 122.049 | -0.11902 | 121.994 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0034509 | -0.010382 | 0.0078136 | -0.01755 | -0.0044395 | -0.0016987 | 0.017904 | 0.033049 | 0.013082 | 3.2975 | 3.3301 | 3.2147 | 3.2799 | 3.3567 | 3.466 | 3.1056 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.041178 | 0.07643 | -0.11836 | 3.2246 | -118.7141 | 3.4165 | 3.3337 | 0.10914 | -118.6373 | -118.528 | 0.000658 | -122.0514 | 0.14296 | 0.058089 | 0.057431 | -121.9528 | -121.9176 | 3.3989 | 3.4757 | 3.5851 | 3.4491 | -118.8885 | 0.061594 | 0.1602 | 0.19545 | 0.2018 | -122.1124
4397.2031 | 122.0169 | -0.10529 | 121.994 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0016987 | 0.017904 | 0.033049 | 0.013082 | 3.3021 | 3.3301 | 3.2193 | 3.2845 | 3.3659 | 3.4752 | 3.1101 | 0.033099 | 0.087354 | -0.06093 | -0.057425 | 0.041178 | 0.07643 | -0.12294 | 3.2154 | -118.7095 | 3.4074 | 3.3246 | 0.10914 | -118.6281 | -118.5188 | -0.017653 | -122.0514 | 0.13839 | 0.044356 | 0.062009 | -121.9528 | -121.9176 | 3.3898 | 3.4712 | 3.5805 | 3.4353 | -118.8839 | 0.047861 | 0.14646 | 0.18172 | 0.19264 | -122.117
4398.9688 | 122.1405 | -0.054932 | 121.962 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0030235 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0016987 | 0.01769 | 0.033049 | 0.012655 | 3.3021 | 3.3209 | 3.2193 | 3.2845 | 3.3613 | 3.466 | 3.1147 | 0.033099 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.07643 | -0.12752 | 3.1696 | -118.6775 | 3.357 | 3.2742 | 0.10456 | -118.6007 | -118.4959 | -0.072586 | -122.024 | 0.088031 | -0.005998 | 0.066588 | -121.9254 | -121.8855 | 3.3394 | 3.4162 | 3.521 | 3.3758 | -118.8473 | -0.007072 | 0.091532 | 0.13136 | 0.14229 | -122.0895
4400.75 | 122.0718 | -0.10071 | 121.9803 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0036647 | -0.0099547 | 0.0076 | -0.01755 | -0.0046531 | -0.0016987 | 0.017904 | 0.033049 | 0.012868 | 3.3066 | 3.3346 | 3.2193 | 3.2845 | 3.3613 | 3.4752 | 3.1101 | 0.019362 | 0.087354 | -0.056351 | -0.062004 | 0.0366 | 0.081008 | -0.11836 | 3.2108 | -118.6958 | 3.4074 | 3.32 | 0.10914 | -118.619 | -118.5051 | -0.017653 | -122.0423 | 0.12007 | 0.044357 | 0.06201 | -121.9437 | -121.8993 | 3.3852 | 3.462 | 3.5759 | 3.4353 | -118.8701 | 0.038704 | 0.13731 | 0.18172 | 0.18806 | -122.0986
4402.4688 | 122.1085 | -0.041199 | 121.962 | 1.4211e-13 | -0.030632 | 0.00057691 | -0.0032373 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0014849 | 0.017904 | 0.033263 | 0.012868 | 3.2975 | 3.3209 | 3.2101 | 3.2753 | 3.3613 | 3.466 | 3.101 | 0.02852 | 0.087354 | -0.056351 | -0.062004 | 0.041178 | 0.067272 | -0.12752 | 3.1422 | -118.6867 | 3.3387 | 3.2513 | 0.10914 | -118.6007 | -118.4959 | -0.086319 | -122.024 | 0.069719 | -0.015152 | 0.071167 | -121.9208 | -121.8947 | 3.3165 | 3.4025 | 3.5072 | 3.3621 | -118.861 | -0.020805 | 0.082377 | 0.10847 | 0.12855 | -122.0895
4404.2344 | 122.0581 | -0.10071 | 122.0032 | 1.4211e-13 | -0.030846 | 0.00036331 | -0.0032373 | -0.010595 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0016987 | 0.018117 | 0.033049 | 0.013082 | 3.2929 | 3.3163 | 3.201 | 3.2753 | 3.3521 | 3.4615 | 3.101 | 0.02852 | 0.091933 | -0.06093 | -0.057425 | 0.041178 | 0.081008 | -0.12752 | 3.2017 | -118.7279 | 3.3936 | 3.3017 | 0.099985 | -118.651 | -118.5417 | -0.02681 | -122.0606 | 0.12923 | 0.039778 | 0.066588 | -121.962 | -121.9222 | 3.376 | 3.4528 | 3.5622 | 3.417 | -118.9022 | 0.043283 | 0.14189 | 0.18172 | 0.19264 | -122.1307
4406 | 122.1176 | -0.073242 | 122.0078 | 1.4211e-13 | -0.030632 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0016987 | 0.017904 | 0.033263 | 0.013082 | 3.2975 | 3.3255 | 3.2101 | 3.2753 | 3.3521 | 3.466 | 3.1056 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 3.1788 | -118.7324 | 3.3707 | 3.2834 | 0.10456 | -118.6556 | -118.5417 | -0.049697 | -122.0743 | 0.10176 | 0.012312 | 0.062009 | -121.9712 | -121.9359 | 3.3486 | 3.4254 | 3.5393 | 3.3987 | -118.9022 | 0.00666 | 0.10984 | 0.14509 | 0.15144 | -122.1307
4407.7188 | 122.1588 | -0.050354 | 121.962 | 1.4211e-13 | -0.030418 | 0.00014951 | -0.0032373 | -0.010168 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0019123 | 0.01769 | 0.033263 | 0.012655 | 3.2929 | 3.3209 | 3.2055 | 3.2799 | 3.3521 | 3.466 | 3.1056 | 0.023941 | 0.087354 | -0.065509 | -0.075739 | 0.045757 | 0.085587 | -0.12294 | 3.1559 | -118.6821 | 3.3433 | 3.2559 | 0.099986 | -118.6098 | -118.4959 | -0.072585 | -122.0377 | 0.074295 | -0.015155 | 0.05743 | -121.9162 | -121.8764 | 3.3302 | 3.4025 | 3.5164 | 3.3712 | -118.8564 | -0.025385 | 0.096111 | 0.13594 | 0.13771 | -122.0849
4409.4844 | 122.0764 | -0.086975 | 122.0169 | 1.4211e-13 | -0.030846 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.008241 | -0.0099192 | -0.0044395 | -0.0016987 | 0.018117 | 0.033263 | 0.013082 | 3.2975 | 3.3301 | 3.2239 | 3.289 | 3.3613 | 3.4752 | 3.1193 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.032021 | 0.081008 | -0.12294 | 3.2063 | -118.7279 | 3.3845 | 3.3108 | 0.10456 | -118.6556 | -118.5417 | -0.035964 | -122.0835 | 0.11092 | 0.026045 | 0.062009 | -121.9849 | -121.9359 | 3.376 | 3.4483 | 3.5622 | 3.417 | -118.8976 | 0.020393 | 0.119 | 0.16798 | 0.17433 | -122.1398
4411.2031 | 122.0444 | -0.10071 | 121.9849 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0032373 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.01769 | 0.033476 | 0.012868 | 3.3021 | 3.3301 | 3.2284 | 3.2845 | 3.3659 | 3.4798 | 3.1101 | 0.014784 | 0.082776 | -0.056351 | -0.066582 | 0.0366 | 0.081008 | -0.12294 | 3.2108 | -118.7004 | 3.4028 | 3.3291 | 0.1183 | -118.619 | -118.5051 | -0.022231 | -122.0514 | 0.11549 | 0.044357 | 0.066588 | -121.9483 | -121.9039 | 3.3852 | 3.4666 | 3.5805 | 3.4308 | -118.8747 | 0.034126 | 0.13731 | 0.18172 | 0.18348 | -122.1078
4412.9688 | 122.1451 | -0.054932 | 121.9574 | 1.4211e-13 | -0.030846 | 0.00014951 | -0.0030235 | -0.010168 | 0.0080272 | -0.0099192 | -0.0046531 | -0.0016987 | 0.017904 | 0.033049 | 0.012868 | 3.2975 | 3.3301 | 3.2193 | 3.2845 | 3.3613 | 3.4706 | 3.1193 | 0.023941 | 0.091933 | -0.056351 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 3.1742 | -118.6729 | 3.3524 | 3.2742 | 0.099983 | -118.5961 | -118.4868 | -0.072586 | -122.024 | 0.078873 | -0.001419 | 0.071167 | -121.9208 | -121.8855 | 3.3394 | 3.4162 | 3.5255 | 3.385 | -118.8381 | -0.01165 | 0.091532 | 0.12678 | 0.14686 | -122.0849
4414.7344 | 122.1313 | -0.068665 | 121.9757 | 1.4211e-13 | -0.030846 | 0.00036331 | -0.0038783 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.01769 | 0.032835 | 0.012868 | 3.3021 | 3.3346 | 3.2284 | 3.289 | 3.3704 | 3.4752 | 3.1101 | 0.033099 | 0.091933 | -0.06093 | -0.071161 | 0.032021 | 0.081008 | -0.12752 | 3.1788 | -118.6867 | 3.3707 | 3.2971 | 0.1183 | -118.6053 | -118.5005 | -0.058853 | -122.0469 | 0.10176 | 0.007735 | 0.066588 | -121.9437 | -121.8947 | 3.3577 | 3.4391 | 3.5439 | 3.4033 | -118.8656 | -0.002496 | 0.10069 | 0.14967 | 0.1606 | -122.1032
4416.4375 | 122.113 | -0.059509 | 121.9574 | 1.4211e-13 | -0.030632 | 0.00036331 | -0.0034509 | -0.0099547 | 0.008241 | -0.01755 | -0.0046531 | -0.0021259 | 0.017904 | 0.033049 | 0.012655 | 3.3066 | 3.3346 | 3.2193 | 3.289 | 3.3613 | 3.4752 | 3.1147 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.045757 | 0.071851 | -0.12752 | 3.1742 | -118.6683 | 3.3662 | 3.2788 | 0.10456 | -118.5961 | -118.4822 | -0.068009 | -122.024 | 0.08345 | 0.003158 | 0.071167 | -121.9116 | -121.8855 | 3.3486 | 3.4208 | 3.5347 | 3.3941 | -118.8427 | -0.007073 | 0.10527 | 0.13136 | 0.14228 | -122.0849
4418.2188 | 122.1542 | -0.068665 | 121.962 | 1.4211e-13 | -0.031059 | 0.00036331 | -0.0034509 | -0.010168 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0016987 | 0.017476 | 0.033476 | 0.012441 | 3.3021 | 3.3301 | 3.2147 | 3.2845 | 3.3521 | 3.4752 | 3.1147 | 0.023941 | 0.082776 | -0.056351 | -0.075739 | 0.041178 | 0.085587 | -0.11836 | 3.1834 | -118.6775 | 3.3707 | 3.2834 | 0.099984 | -118.6098 | -118.4868 | -0.049696 | -122.0377 | 0.092606 | 0.012314 | 0.06201 | -121.9208 | -121.8764 | 3.3531 | 3.4208 | 3.5439 | 3.3987 | -118.8473 | -0.007074 | 0.10984 | 0.15425 | 0.15144 | -122.0803
4419.9844 | 122.0535 | -0.10529 | 121.9849 | 1.4211e-13 | -0.030846 | 0.00014951 | -0.0034509 | -0.010382 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018117 | 0.033263 | 0.013082 | 3.2929 | 3.3209 | 3.2101 | 3.2799 | 3.3567 | 3.4615 | 3.1056 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.081008 | -0.12294 | 3.2108 | -118.705 | 3.3982 | 3.3154 | 0.10456 | -118.6282 | -118.5234 | -0.017653 | -122.0514 | 0.12465 | 0.044356 | 0.062009 | -121.9483 | -121.9039 | 3.3852 | 3.462 | 3.5667 | 3.4262 | -118.8793 | 0.038704 | 0.14189 | 0.18629 | 0.18806 | -122.1078
4421.6875 | 122.0764 | -0.11444 | 122.0032 | 1.4211e-13 | -0.030846 | 0.00014951 | -0.0032373 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0016987 | 0.018117 | 0.033476 | 0.012655 | 3.2929 | 3.3255 | 3.2101 | 3.2799 | 3.3567 | 3.466 | 3.1056 | 0.033099 | 0.091933 | -0.06093 | -0.080318 | 0.0366 | 0.07643 | -0.12752 | 3.22 | -118.7233 | 3.4073 | 3.3246 | 0.10456 | -118.6465 | -118.5371 | -0.013077 | -122.0835 | 0.14754 | 0.053511 | 0.066588 | -121.9666 | -121.9267 | 3.3943 | 3.4712 | 3.5805 | 3.4399 | -118.8976 | 0.034123 | 0.15104 | 0.19087 | 0.20637 | -122.1307
4423.4531 | 122.1771 | -0.068665 | 121.9574 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0034509 | -0.010382 | 0.0078136 | -0.0022892 | -0.0048667 | -0.0014849 | 0.017904 | 0.033263 | 0.012868 | 3.2883 | 3.3163 | 3.2055 | 3.2662 | 3.3476 | 3.466 | 3.101 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.041178 | 0.081008 | -0.12294 | 3.1696 | -118.6912 | 3.357 | 3.2742 | 0.10456 | -118.6098 | -118.4914 | -0.054274 | -122.024 | 0.092606 | 0.003156 | 0.05743 | -121.9162 | -121.8764 | 3.3348 | 3.4162 | 3.5347 | 3.385 | -118.8564 | 0.002083 | 0.10984 | 0.14967 | 0.15144 | -122.0803
4425.2188 | 122.0627 | -0.10071 | 122.0169 | 1.4211e-13 | -0.030632 | 0.00036331 | -0.0032373 | -0.010595 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017904 | 0.033049 | 0.012655 | 3.2883 | 3.3163 | 3.2055 | 3.2707 | 3.343 | 3.4523 | 3.0964 | 0.023941 | 0.091933 | -0.06093 | -0.071161 | 0.0366 | 0.081008 | -0.12294 | 3.1971 | -118.7462 | 3.389 | 3.3063 | 0.10914 | -118.6739 | -118.5646 | -0.022231 | -122.0881 | 0.12465 | 0.039778 | 0.062009 | -121.9803 | -121.9359 | 3.3714 | 3.4437 | 3.553 | 3.417 | -118.9205 | 0.029547 | 0.13731 | 0.18172 | 0.19264 | -122.1398
4427 | 122.0352 | -0.12817 | 122.0398 | 1.4211e-13 | -0.030846 | 0.00014951 | -0.0036647 | -0.010595 | 0.0078136 | -0.01755 | -0.0044395 | -0.0014849 | 0.018331 | 0.033263 | 0.013082 | 3.2838 | 3.3117 | 3.201 | 3.2707 | 3.343 | 3.4615 | 3.0827 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.0366 | 0.081008 | -0.12752 | 3.2108 | -118.7691 | 3.4119 | 3.3291 | 0.1183 | -118.6968 | -118.5783 | 0.000656 | -122.111 | 0.15212 | 0.071823 | 0.071167 | -122.0032 | -121.9588 | 3.3989 | 3.4711 | 3.5896 | 3.4399 | -118.9571 | 0.057013 | 0.16477 | 0.20918 | 0.21553 | -122.1673
4428.7188 | 122.2046 | -0.059509 | 121.9757 | 1.4211e-13 | -0.030846 | 0.00036331 | -0.0032373 | -0.010382 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0019123 | 0.01769 | 0.033263 | 0.012868 | 3.2792 | 3.3072 | 3.1964 | 3.2662 | 3.343 | 3.4477 | 3.0918 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.0366 | 0.081008 | -0.12752 | 3.1513 | -118.7096 | 3.3387 | 3.2559 | 0.10457 | -118.6327 | -118.528 | -0.068009 | -122.0469 | 0.088029 | 0.003158 | 0.071167 | -121.9391 | -121.8947 | 3.3257 | 3.4025 | 3.5072 | 3.3667 | -118.8839 | -0.011652 | 0.096109 | 0.14052 | 0.14228 | -122.1032
4430.4844 | 122.0261 | -0.09613 | 122.0398 | 1.4211e-13 | -0.030632 | 0.00014951 | -0.0036647 | -0.010382 | 0.0080272 | -0.01755 | -0.0044395 | -0.0019123 | 0.01769 | 0.033476 | 0.012441 | 3.2792 | 3.3072 | 3.1964 | 3.2616 | 3.3292 | 3.4477 | 3.0872 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 3.1834 | -118.7782 | 3.3753 | 3.2925 | 0.10914 | -118.7106 | -118.5921 | -0.026809 | -122.1064 | 0.12007 | 0.030621 | 0.05743 | -122.0032 | -121.9679 | 3.3577 | 3.4254 | 3.5438 | 3.4033 | -118.9526 | 0.029548 | 0.13273 | 0.16798 | 0.17891 | -122.1627
4432.2031 | 122.0078 | -0.09613 | 122.0352 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.010168 | 0.0076 | -0.0099192 | -0.0046531 | -0.0019123 | 0.01769 | 0.033263 | 0.012655 | 3.27 | 3.3026 | 3.1827 | 3.257 | 3.3338 | 3.4477 | 3.0918 | 0.023941 | 0.091933 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.12294 | 3.188 | -118.7782 | 3.3661 | 3.2788 | 0.09083 | -118.7014 | -118.5875 | -0.026809 | -122.1064 | 0.12007 | 0.030621 | 0.05743 | -121.994 | -121.9588 | 3.3531 | 3.4299 | 3.5438 | 3.3987 | -118.9434 | 0.024969 | 0.13731 | 0.17256 | 0.18806 | -122.1582
4433.9688 | 122.1039 | -0.091553 | 122.0123 | 1.4211e-13 | -0.030632 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0080272 | -0.01755 | -0.0046531 | -0.0014849 | 0.017904 | 0.033263 | 0.012868 | 3.2654 | 3.3072 | 3.1827 | 3.2524 | 3.3292 | 3.434 | 3.0827 | 0.023941 | 0.091933 | -0.06093 | -0.071161 | 0.0366 | 0.081008 | -0.12752 | 3.1742 | -118.7599 | 3.357 | 3.2742 | 0.099988 | -118.6831 | -118.5783 | -0.035965 | -122.0835 | 0.11549 | 0.030623 | 0.066588 | -121.9757 | -121.9313 | 3.344 | 3.4208 | 3.5255 | 3.3987 | -118.9297 | 0.020392 | 0.12815 | 0.17256 | 0.18349 | -122.1398
4435.7344 | 122.1359 | -0.059509 | 121.9757 | 1.4211e-13 | -0.031059 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0080272 | -0.0099192 | -0.0050803 | -0.0019123 | 0.01769 | 0.033263 | 0.013082 | 3.2792 | 3.3026 | 3.1964 | 3.2524 | 3.3292 | 3.4431 | 3.0781 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.12294 | 3.1376 | -118.7233 | 3.3387 | 3.2559 | 0.1183 | -118.6465 | -118.5326 | -0.06343 | -122.0469 | 0.08345 | -0.001421 | 0.062009 | -121.9437 | -121.8993 | 3.3119 | 3.3887 | 3.5026 | 3.3621 | -118.8976 | -0.011652 | 0.09153 | 0.13594 | 0.14228 | -122.0986
4437.4375 | 122.0673 | -0.09613 | 122.0398 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0036647 | -0.010382 | 0.008241 | -0.01755 | -0.0046531 | -0.0014849 | 0.017904 | 0.033476 | 0.012655 | 3.27 | 3.298 | 3.1918 | 3.2524 | 3.3247 | 3.4431 | 3.0872 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.07643 | -0.12294 | 3.1834 | -118.7874 | 3.3661 | 3.2879 | 0.10457 | -118.7151 | -118.5967 | -0.026809 | -122.111 | 0.11549 | 0.0352 | 0.062009 | -122.0032 | -121.9634 | 3.3486 | 3.4208 | 3.5393 | 3.3941 | -118.9526 | 0.024969 | 0.13273 | 0.17256 | 0.18348 | -122.1627
4439.2031 | 122.1954 | -0.054932 | 121.9986 | 1.4211e-13 | -0.030846 | 0.00014951 | -0.0036647 | -0.010382 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0016987 | 0.017904 | 0.033476 | 0.012868 | 3.2654 | 3.298 | 3.1827 | 3.257 | 3.3247 | 3.4431 | 3.0827 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 3.1376 | -118.7416 | 3.3204 | 3.2376 | 0.099988 | -118.6739 | -118.5555 | -0.068007 | -122.0652 | 0.078873 | -0.010577 | 0.05743 | -121.9574 | -121.9222 | 3.3119 | 3.3796 | 3.4981 | 3.3529 | -118.9159 | -0.01165 | 0.09611 | 0.13136 | 0.14229 | -122.1215
4440.9688 | 122.0673 | -0.10529 | 122.0306 | 1.4211e-13 | -0.030846 | 0.00057691 | -0.0032373 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0014849 | 0.017904 | 0.03369 | 0.012868 | 3.2654 | 3.2934 | 3.1781 | 3.2387 | 3.3247 | 3.4294 | 3.0735 | 0.02852 | 0.096512 | -0.056351 | -0.075739 | 0.041178 | 0.07643 | -0.12294 | 3.1788 | -118.792 | 3.3707 | 3.2834 | 0.10457 | -118.706 | -118.6012 | -0.017653 | -122.1064 | 0.13381 | 0.048935 | 0.066588 | -121.9895 | -121.9542 | 3.344 | 3.4299 | 3.5347 | 3.3987 | -118.9571 | 0.029547 | 0.14646 | 0.18172 | 0.2018 | -122.1536
4442.7031 | 122.0856 | -0.10529 | 122.0627 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0032373 | -0.010168 | 0.0078136 | -0.01755 | -0.0046531 | -0.0014849 | 0.01769 | 0.033263 | 0.012441 | 3.27 | 3.2934 | 3.1872 | 3.2433 | 3.3155 | 3.434 | 3.0827 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.032021 | 0.081008 | -0.12294 | 3.1879 | -118.8194 | 3.3753 | 3.2925 | 0.10457 | -118.7472 | -118.6287 | -0.017653 | -122.1384 | 0.12923 | 0.044356 | 0.062009 | -122.0307 | -121.9817 | 3.3485 | 3.4208 | 3.5393 | 3.3987 | -118.98 | 0.029547 | 0.13731 | 0.18629 | 0.19264 | -122.1856
4444.4688 | 122.0627 | -0.10529 | 122.0352 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0048667 | -0.0014849 | 0.018117 | 0.033263 | 0.012868 | 3.27 | 3.298 | 3.1872 | 3.2478 | 3.3292 | 3.434 | 3.0918 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.027442 | 0.081008 | -0.12752 | 3.1971 | -118.7874 | 3.3753 | 3.2925 | 0.095408 | -118.706 | -118.6012 | -0.022232 | -122.111 | 0.13381 | 0.048935 | 0.071167 | -122.0078 | -121.9542 | 3.3531 | 3.4345 | 3.5393 | 3.4033 | -118.9434 | 0.029547 | 0.13273 | 0.18629 | 0.19264 | -122.1627
4446.2344 | 122.1725 | -0.064087 | 122.0032 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0036647 | -0.010382 | 0.0080272 | -0.01755 | -0.0050803 | -0.0019123 | 0.017904 | 0.033476 | 0.012655 | 3.2609 | 3.2843 | 3.1781 | 3.2387 | 3.3109 | 3.4294 | 3.0643 | 0.019362 | 0.091933 | -0.056351 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 3.1284 | -118.7645 | 3.3249 | 3.2422 | 0.11373 | -118.6923 | -118.5738 | -0.063431 | -122.0698 | 0.083449 | 0.007736 | 0.071167 | -121.9666 | -121.9267 | 3.3028 | 3.375 | 3.4935 | 3.3484 | -118.9388 | -0.002495 | 0.10069 | 0.14052 | 0.15602 | -122.1307
4448 | 122.2 | -0.064087 | 121.9894 | 1.4211e-13 | -0.031059 | -6.4092e-05 | -0.0036647 | -0.0099547 | 0.0080272 | -0.0099192 | -0.0048667 | -0.0014849 | 0.01769 | 0.033263 | 0.012868 | 3.2471 | 3.2751 | 3.1689 | 3.2295 | 3.3155 | 3.4157 | 3.0643 | 0.023941 | 0.091933 | -0.056351 | -0.066582 | 0.032021 | 0.071851 | -0.12294 | 3.1284 | -118.7599 | 3.3112 | 3.233 | 0.10457 | -118.6739 | -118.5738 | -0.058852 | -122.056 | 0.088028 | 0.007736 | 0.066588 | -121.9574 | -121.9176 | 3.2936 | 3.3796 | 3.4798 | 3.3392 | -118.9251 | -0.002495 | 0.096108 | 0.13594 | 0.15602 | -122.1124
4449.7031 | 122.1909 | -0.032043 | 122.0032 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.010168 | 0.0080272 | -0.01755 | -0.0044395 | -0.0016987 | 0.01769 | 0.033476 | 0.012655 | 3.2471 | 3.266 | 3.1643 | 3.2204 | 3.3018 | 3.4111 | 3.0506 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.081008 | -0.11836 | 3.0827 | -118.7828 | 3.2792 | 3.1964 | 0.11373 | -118.7014 | -118.5921 | -0.086318 | -122.0698 | 0.055984 | -0.028887 | 0.057431 | -121.9666 | -121.9222 | 3.2524 | 3.3338 | 3.4431 | 3.298 | -118.9526 | -0.034539 | 0.068643 | 0.11305 | 0.1194 | -122.1215
4451.4688 | 122.1634 | -0.054932 | 122.0078 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0032373 | -0.010168 | 0.0076 | -0.01755 | -0.0042257 | -0.0016987 | 0.017476 | 0.033263 | 0.012441 | 3.2334 | 3.266 | 3.1552 | 3.225 | 3.2972 | 3.4065 | 3.0506 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.081008 | -0.12294 | 3.1055 | -118.7828 | 3.2883 | 3.2101 | 0.10457 | -118.7106 | -118.6012 | -0.068007 | -122.0789 | 0.083452 | -0.005998 | 0.062009 | -121.9712 | -121.9267 | 3.2799 | 3.3521 | 3.4614 | 3.3209 | -118.9571 | -0.016229 | 0.091532 | 0.13594 | 0.13771 | -122.1307
4453.1719 | 122.1863 | -0.045776 | 122.0078 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0038783 | -0.010595 | 0.0076 | -0.0099192 | -0.0044395 | -0.0016987 | 0.01769 | 0.033263 | 0.012655 | 3.238 | 3.2568 | 3.146 | 3.2158 | 3.288 | 3.4065 | 3.046 | 0.037677 | 0.091933 | -0.06093 | -0.080318 | 0.0366 | 0.081008 | -0.1321 | 3.0918 | -118.792 | 3.2837 | 3.1918 | 0.099994 | -118.7197 | -118.6012 | -0.086321 | -122.0881 | 0.083453 | -0.015154 | 0.071167 | -121.9712 | -121.9267 | 3.2616 | 3.3338 | 3.4523 | 3.3026 | -118.9617 | -0.034542 | 0.082376 | 0.12678 | 0.13771 | -122.1398
4454.9688 | 122.0856 | -0.091553 | 122.0352 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0036647 | -0.010382 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0016987 | 0.01769 | 0.033049 | 0.012655 | 3.2334 | 3.2614 | 3.1414 | 3.2112 | 3.288 | 3.3974 | 3.0323 | 0.019362 | 0.087354 | -0.06093 | -0.075739 | 0.032021 | 0.07643 | -0.12752 | 3.1238 | -118.824 | 3.3249 | 3.233 | 0.10915 | -118.7472 | -118.6379 | -0.035965 | -122.111 | 0.11091 | 0.030623 | 0.066588 | -122.0032 | -121.9588 | 3.3028 | 3.3796 | 3.4889 | 3.3529 | -119.0029 | 0.015814 | 0.12357 | 0.16798 | 0.17891 | -122.1627
4456.7344 | 122.0673 | -0.11902 | 122.0627 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.010382 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017904 | 0.033476 | 0.012868 | 3.2334 | 3.2522 | 3.146 | 3.2066 | 3.288 | 3.4019 | 3.0369 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.032021 | 0.081008 | -0.12294 | 3.1559 | -118.856 | 3.3524 | 3.265 | 0.10915 | -118.7747 | -118.6608 | -0.00392 | -122.1384 | 0.14296 | 0.058089 | 0.062009 | -122.0307 | -121.9817 | 3.3257 | 3.407 | 3.521 | 3.3712 | -119.0258 | 0.04328 | 0.15104 | 0.20003 | 0.20637 | -122.1856
4458.4531 | 122.1863 | -0.050354 | 122.0169 | 1.4211e-13 | -0.031273 | 0.00036331 | -0.0034509 | -0.010168 | 0.0080272 | -0.0022892 | -0.0048667 | -0.0019123 | 0.017904 | 0.033263 | 0.012441 | 3.2242 | 3.2568 | 3.1323 | 3.2021 | 3.2926 | 3.3974 | 3.0323 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.045757 | 0.07643 | -0.12294 | 3.0827 | -118.8148 | 3.2746 | 3.1826 | 0.099995 | -118.7243 | -118.6196 | -0.072585 | -122.0835 | 0.078874 | -0.005997 | 0.066588 | -121.9712 | -121.9405 | 3.2524 | 3.343 | 3.4477 | 3.3071 | -118.9846 | -0.016228 | 0.096111 | 0.12678 | 0.13771 | -122.1398
4460.2188 | 122.0764 | -0.1236 | 122.0352 | 1.4211e-13 | -0.031273 | 0.00036331 | -0.0040921 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017476 | 0.033263 | 0.012655 | 3.2242 | 3.2568 | 3.1369 | 3.2112 | 3.2926 | 3.3928 | 3.0369 | 0.02852 | 0.082776 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.12752 | 3.1605 | -118.824 | 3.3478 | 3.2605 | 0.099994 | -118.7426 | -118.6424 | -0.003922 | -122.111 | 0.15212 | 0.062666 | 0.066588 | -121.9986 | -121.9588 | 3.3348 | 3.4162 | 3.5164 | 3.3804 | -118.9983 | 0.047857 | 0.1602 | 0.20003 | 0.20637 | -122.1627
4461.9219 | 122.1725 | -0.054932 | 122.0123 | 1.4211e-13 | -0.030846 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0019123 | 0.01769 | 0.033476 | 0.012655 | 3.2242 | 3.2476 | 3.146 | 3.2112 | 3.2789 | 3.3928 | 3.0369 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.0366 | 0.081008 | -0.12294 | 3.0918 | -118.8011 | 3.2792 | 3.201 | 0.10915 | -118.7335 | -118.6196 | -0.068007 | -122.0835 | 0.083452 | -0.001419 | 0.066588 | -121.9757 | -121.9313 | 3.2661 | 3.3338 | 3.4477 | 3.3026 | -118.9755 | -0.016229 | 0.091532 | 0.13594 | 0.13771 | -122.1353
4463.6875 | 122.1451 | -0.068665 | 122.0078 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.0099547 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0014849 | 0.017904 | 0.033476 | 0.013082 | 3.2197 | 3.2476 | 3.1369 | 3.1975 | 3.2743 | 3.3928 | 3.0277 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.12294 | 3.0964 | -118.8103 | 3.2883 | 3.2055 | 0.10915 | -118.7335 | -118.615 | -0.054274 | -122.0789 | 0.088027 | 0.007735 | 0.062009 | -121.9712 | -121.9359 | 3.2661 | 3.343 | 3.4614 | 3.3163 | -118.98 | -0.002496 | 0.10526 | 0.14052 | 0.15144 | -122.1307
4465.4531 | 122.1863 | -0.064087 | 122.0032 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0042257 | -0.0019123 | 0.01769 | 0.03369 | 0.012655 | 3.2242 | 3.2568 | 3.146 | 3.2021 | 3.288 | 3.3928 | 3.0323 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.041178 | 0.081008 | -0.1321 | 3.0964 | -118.8011 | 3.2883 | 3.2101 | 0.11373 | -118.7151 | -118.6104 | -0.06801 | -122.0698 | 0.092607 | -0.001422 | 0.066588 | -121.962 | -121.9222 | 3.2661 | 3.3521 | 3.4569 | 3.3209 | -118.9709 | -0.002495 | 0.10526 | 0.1451 | 0.14228 | -122.1353
4467.2188 | 122.0993 | -0.10986 | 122.0444 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0034509 | -0.010382 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0014849 | 0.017904 | 0.033263 | 0.012655 | 3.2288 | 3.2522 | 3.146 | 3.2066 | 3.288 | 3.3882 | 3.0323 | 0.019362 | 0.082776 | -0.056351 | -0.075739 | 0.045757 | 0.071851 | -0.12752 | 3.1422 | -118.8377 | 3.3387 | 3.2559 | 0.11373 | -118.7563 | -118.6562 | -0.017655 | -122.1201 | 0.12923 | 0.053512 | 0.071167 | -121.9986 | -121.9725 | 3.3165 | 3.3979 | 3.4981 | 3.3621 | -119.0121 | 0.034124 | 0.15562 | 0.18171 | 0.19264 | -122.1719
4468.9844 | 122.1313 | -0.091553 | 122.0398 | 1.4211e-13 | -0.030846 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.01755 | -0.0046531 | -0.0014849 | 0.01769 | 0.033476 | 0.012655 | 3.2334 | 3.2476 | 3.1414 | 3.2066 | 3.2789 | 3.3882 | 3.0323 | 0.02852 | 0.082776 | -0.056351 | -0.075739 | 0.045757 | 0.081008 | -0.12294 | 3.1238 | -118.8332 | 3.3249 | 3.233 | 0.10915 | -118.7609 | -118.6516 | -0.031386 | -122.1155 | 0.12007 | 0.035202 | 0.066588 | -121.994 | -121.9588 | 3.2982 | 3.3704 | 3.4797 | 3.3392 | -119.0075 | 0.015814 | 0.13731 | 0.17256 | 0.17433 | -122.1627
4470.6875 | 122.1039 | -0.09613 | 122.0261 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010382 | 0.0076 | -0.0022892 | -0.0048667 | -0.0019123 | 0.01769 | 0.033263 | 0.012868 | 3.2151 | 3.2476 | 3.1323 | 3.1975 | 3.2697 | 3.3836 | 3.0231 | 0.019362 | 0.091933 | -0.06093 | -0.071161 | 0.041178 | 0.081008 | -0.12752 | 3.1193 | -118.8286 | 3.3112 | 3.2284 | 0.10915 | -118.7564 | -118.6424 | -0.031388 | -122.0972 | 0.11549 | 0.0352 | 0.066588 | -121.9849 | -121.9451 | 3.2936 | 3.3658 | 3.4797 | 3.3438 | -119.0029 | 0.024969 | 0.13731 | 0.17714 | 0.18806 | -122.1536
4472.4531 | 122.1634 | -0.068665 | 122.0306 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.010168 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0012713 | 0.018117 | 0.033263 | 0.012655 | 3.2105 | 3.2385 | 3.1277 | 3.1929 | 3.2697 | 3.3745 | 3.0231 | 0.033099 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.071851 | -0.12294 | 3.0918 | -118.8377 | 3.2792 | 3.1964 | 0.10458 | -118.7609 | -118.6562 | -0.054274 | -122.1018 | 0.10176 | 0.007735 | 0.062009 | -121.9849 | -121.9588 | 3.2616 | 3.3384 | 3.4431 | 3.3071 | -119.0075 | -0.002496 | 0.11442 | 0.14052 | 0.15144 | -122.1536
4474.1562 | 122.1405 | -0.07782 | 122.0169 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.01755 | -0.0048667 | -0.0016987 | 0.01769 | 0.033263 | 0.012655 | 3.2151 | 3.2339 | 3.1277 | 3.1883 | 3.2651 | 3.379 | 3.014 | 0.023941 | 0.087354 | -0.065509 | -0.080318 | 0.027442 | 0.081008 | -0.12752 | 3.0918 | -118.8286 | 3.2929 | 3.2055 | 0.11373 | -118.7518 | -118.6379 | -0.049698 | -122.0972 | 0.10176 | 0.012311 | 0.062009 | -121.9895 | -121.9359 | 3.2661 | 3.343 | 3.4569 | 3.3117 | -119.0029 | -0.002498 | 0.10526 | 0.15883 | 0.16517 | -122.1444
4475.9219 | 122.1085 | -0.082397 | 122.0261 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0019123 | 0.017904 | 0.033476 | 0.012868 | 3.2013 | 3.2293 | 3.114 | 3.1883 | 3.2606 | 3.3653 | 3.014 | 0.02852 | 0.087354 | -0.06093 | -0.075739 | 0.041178 | 0.07643 | -0.1321 | 3.0964 | -118.8377 | 3.2837 | 3.1964 | 0.099998 | -118.7655 | -118.6608 | -0.0497 | -122.1018 | 0.11092 | 0.021467 | 0.071167 | -121.9849 | -121.9496 | 3.2707 | 3.3429 | 3.4477 | 3.3117 | -119.0121 | 0.006658 | 0.12357 | 0.15883 | 0.16975 | -122.1582
4477.6875 | 122.0627 | -0.10529 | 122.0398 | 1.4211e-13 | -0.031059 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0076 | -0.01755 | -0.0046531 | -0.0012713 | 0.01769 | 0.033476 | 0.012655 | 3.2059 | 3.2202 | 3.1186 | 3.1883 | 3.2606 | 3.3699 | 3.0094 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.045757 | 0.07643 | -0.12294 | 3.1147 | -118.8515 | 3.3112 | 3.2238 | 0.10915 | -118.7792 | -118.6699 | -0.017653 | -122.1155 | 0.12923 | 0.039777 | 0.05743 | -121.994 | -121.9634 | 3.2936 | 3.3658 | 3.4752 | 3.3255 | -119.0304 | 0.029547 | 0.15104 | 0.18172 | 0.18348 | -122.1627
4479.4531 | 122.1039 | -0.086975 | 122.0215 | 1.4211e-13 | -0.031059 | 0.00014951 | -0.0036647 | -0.010382 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0014849 | 0.017476 | 0.033476 | 0.012655 | 3.1968 | 3.2156 | 3.114 | 3.1746 | 3.2606 | 3.3561 | 3.0002 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.071851 | -0.12294 | 3.0872 | -118.8469 | 3.2837 | 3.201 | 0.11373 | -118.7609 | -118.6653 | -0.035964 | -122.0881 | 0.10634 | 0.026045 | 0.062009 | -121.9803 | -121.9496 | 3.2616 | 3.3475 | 3.4431 | 3.3026 | -119.0212 | 0.020393 | 0.12815 | 0.15883 | 0.16975 | -122.1444
4481.1562 | 122.1222 | -0.091553 | 122.0261 | 1.4211e-13 | -0.031273 | 0.00036331 | -0.0034509 | -0.010595 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0014849 | 0.01769 | 0.033263 | 0.012868 | 3.1922 | 3.2247 | 3.114 | 3.1746 | 3.2514 | 3.3561 | 3.0048 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.11836 | 3.0964 | -118.8515 | 3.2837 | 3.2055 | 0.10916 | -118.7747 | -118.6699 | -0.026808 | -122.0972 | 0.11549 | 0.030623 | 0.057431 | -121.9803 | -121.9496 | 3.2661 | 3.3429 | 3.4477 | 3.3163 | -119.0212 | 0.020392 | 0.13731 | 0.16798 | 0.17433 | -122.1444
4482.9219 | 122.1359 | -0.073242 | 122.0032 | 1.4211e-13 | -0.031273 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017476 | 0.033263 | 0.012655 | 3.2013 | 3.2293 | 3.114 | 3.17 | 3.256 | 3.3607 | 3.0094 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.041178 | 0.081008 | -0.12752 | 3.0826 | -118.8332 | 3.2746 | 3.1872 | 0.10458 | -118.7472 | -118.6424 | -0.054276 | -122.0743 | 0.10176 | 0.016891 | 0.071167 | -121.962 | -121.9222 | 3.2433 | 3.3292 | 3.434 | 3.3026 | -118.9938 | 0.002081 | 0.11442 | 0.15425 | 0.15602 | -122.1307
4484.6562 | 122.0718 | -0.10529 | 122.0352 | 1.4211e-13 | -0.0317 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.02518 | -0.0050803 | -0.0019123 | 0.01769 | 0.033049 | 0.012441 | 3.2013 | 3.2247 | 3.114 | 3.17 | 3.2514 | 3.3607 | 3.0048 | 0.023941 | 0.087354 | -0.056351 | -0.075739 | 0.041178 | 0.07643 | -0.12294 | 3.1101 | -118.8652 | 3.3066 | 3.2193 | 0.10916 | -118.7838 | -118.6745 | -0.017653 | -122.111 | 0.12923 | 0.048935 | 0.066588 | -121.994 | -121.9588 | 3.2753 | 3.3567 | 3.466 | 3.33 | -119.0304 | 0.029547 | 0.14646 | 0.18172 | 0.19264 | -122.1582
4486.4219 | 122.0581 | -0.10071 | 122.0398 | 1.4211e-13 | -0.031487 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0080272 | -0.0022892 | -0.0048667 | -0.0016987 | 0.017476 | 0.033476 | 0.012868 | 3.1876 | 3.2156 | 3.1048 | 3.17 | 3.2422 | 3.3516 | 3.0048 | 0.014784 | 0.087354 | -0.051772 | -0.066582 | 0.041178 | 0.07643 | -0.12752 | 3.1055 | -118.8698 | 3.2883 | 3.2055 | 0.099999 | -118.7976 | -118.6882 | -0.02681 | -122.1064 | 0.11549 | 0.048936 | 0.075746 | -121.9986 | -121.9634 | 3.2707 | 3.3429 | 3.4523 | 3.3163 | -119.035 | 0.034126 | 0.14189 | 0.17714 | 0.18806 | -122.1673
4488.1406 | 122.1909 | -0.086975 | 122.049 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0032373 | -0.010382 | 0.0080272 | -0.0099192 | -0.0048667 | -0.0014849 | 0.017476 | 0.033476 | 0.012227 | 3.1876 | 3.211 | 3.1048 | 3.1563 | 3.2422 | 3.3516 | 3.0002 | 0.019362 | 0.082776 | -0.065509 | -0.075739 | 0.041178 | 0.085587 | -0.12752 | 3.0872 | -118.8927 | 3.2746 | 3.1918 | 0.10458 | -118.8067 | -118.6974 | -0.040543 | -122.1247 | 0.10634 | 0.021466 | 0.062009 | -122.0078 | -121.9634 | 3.2432 | 3.3292 | 3.4385 | 3.298 | -119.0487 | 0.011236 | 0.12815 | 0.17256 | 0.16975 | -122.1765
4489.9062 | 122.1268 | -0.091553 | 122.0535 | 1.4211e-13 | -0.031273 | -0.00027769 | -0.0038783 | -0.010168 | 0.0078136 | -0.0099192 | -0.0042257 | -0.0019123 | 0.01769 | 0.033263 | 0.013082 | 3.1784 | 3.2064 | 3.0911 | 3.1517 | 3.2285 | 3.3378 | 2.9773 | 0.023941 | 0.087354 | -0.051772 | -0.071161 | 0.0366 | 0.081008 | -0.12294 | 3.0689 | -118.9018 | 3.27 | 3.1826 | 0.11374 | -118.825 | -118.7157 | -0.031386 | -122.1247 | 0.11549 | 0.039781 | 0.071167 | -122.0169 | -121.9725 | 3.2432 | 3.3201 | 3.4294 | 3.298 | -119.0762 | 0.020392 | 0.12815 | 0.17256 | 0.17891 | -122.1765
4491.6719 | 121.9666 | -0.10986 | 121.9528 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0036647 | -0.010595 | 0.0080272 | -0.0099192 | -0.0042257 | -0.0014849 | 0.017904 | 0.03369 | 0.012441 | 9.6248 | 9.6211 | 9.4549 | 9.4973 | 9.5245 | 9.6746 | 8.527 | 0.02852 | 0.087354 | -0.06093 | -0.075739 | 0.041178 | 0.07643 | -0.13668 | 8.6369 | -112.4555 | 9.7347 | 9.5648 | 0.92789 | -112.4283 | -112.2782 | -0.026813 | -122.0286 | 0.13838 | 0.048933 | 0.075746 | -121.9116 | -121.8764 | 9.6072 | 9.6344 | 9.7845 | 9.7309 | -113.4258 | 0.034124 | 0.15104 | 0.18629 | 0.19722 | -122.0895
4493.375 | 122.0398 | -0.11902 | 121.9894 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0016987 | 0.017263 | 0.033263 | 0.012441 | 9.6614 | 9.6577 | 9.4915 | 9.5294 | 9.5566 | 9.7021 | 8.5499 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.032021 | 0.071851 | -0.1321 | 8.6689 | -112.46 | 9.7805 | 9.6105 | 0.94162 | -112.4329 | -112.2874 | -0.013078 | -122.0606 | 0.14754 | 0.058089 | 0.071167 | -121.9574 | -121.9176 | 9.6484 | 9.6756 | 9.8211 | 9.7767 | -113.4395 | 0.047858 | 0.15104 | 0.19087 | 0.2018 | -122.1215
4495.1406 | 122.0535 | -0.1236 | 122.0535 | 1.4211e-13 | -0.031273 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0076 | -0.0099192 | -0.0044395 | -0.0016987 | 0.017904 | 0.033476 | 0.012655 | 9.634 | 9.6302 | 9.4686 | 9.5065 | 9.5383 | 9.6792 | 8.5407 | 0.023941 | 0.087354 | -0.056351 | -0.075739 | 0.0366 | 0.07643 | -0.1321 | 8.6643 | -112.547 | 9.7576 | 9.5922 | 0.92789 | -112.5153 | -112.3743 | -0.008501 | -122.1293 | 0.14754 | 0.067245 | 0.075746 | -122.0169 | -121.9771 | 9.6301 | 9.6619 | 9.8028 | 9.7538 | -113.5128 | 0.047857 | 0.1602 | 0.20003 | 0.21095 | -122.1856
4496.8438 | 122.1817 | -0.064087 | 122.0078 | 1.4211e-13 | -0.031487 | -6.4092e-05 | -0.0034509 | -0.010168 | 0.0078136 | -0.02518 | -0.0048667 | -0.0014849 | 0.017904 | 0.03369 | 0.012441 | 9.6294 | 9.6256 | 9.4503 | 9.5019 | 9.5245 | 9.67 | 8.5362 | 0.019362 | 0.082776 | -0.051772 | -0.071161 | 0.032021 | 0.07643 | -0.12294 | 8.6003 | -112.5058 | 9.6935 | 9.5144 | 0.91415 | -112.4832 | -112.3377 | -0.058852 | -122.0789 | 0.083449 | 0.012315 | 0.071167 | -121.9757 | -121.9313 | 9.566 | 9.5886 | 9.7341 | 9.6897 | -113.4716 | -0.007074 | 0.096108 | 0.14052 | 0.14686 | -122.1307
4498.625 | 122.0535 | -0.10529 | 122.0398 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0036647 | -0.010168 | 0.008241 | -0.02518 | -0.0048667 | -0.0016987 | 0.017476 | 0.033476 | 0.012655 | 9.6157 | 9.6073 | 9.4412 | 9.4836 | 9.5108 | 9.6563 | 8.5316 | 0.033099 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.07643 | -0.12294 | 8.6369 | -112.5562 | 9.7209 | 9.5464 | 0.90958 | -112.529 | -112.3835 | -0.017653 | -122.111 | 0.13839 | 0.044356 | 0.062009 | -121.9986 | -121.9634 | 9.5889 | 9.6161 | 9.7616 | 9.7126 | -113.5082 | 0.034125 | 0.14646 | 0.18172 | 0.19264 | -122.1627
4500.3281 | 122.1222 | -0.10071 | 122.0535 | 1.4211e-13 | -0.031487 | 0.00036331 | -0.0034509 | -0.010809 | 0.0078136 | -0.01755 | -0.0046531 | -0.0014849 | 0.01769 | 0.033263 | 0.012655 | 9.6019 | 9.5982 | 9.4274 | 9.4744 | 9.497 | 9.638 | 8.5224 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.0366 | 0.07643 | -0.12294 | 8.6231 | -112.5791 | 9.7026 | 9.5281 | 0.905 | -112.5565 | -112.4155 | -0.022231 | -122.1247 | 0.12465 | 0.044357 | 0.066588 | -122.0169 | -121.9771 | 9.5752 | 9.5978 | 9.7387 | 9.6989 | -113.5311 | 0.029547 | 0.13731 | 0.17714 | 0.18806 | -122.1765
4502.0938 | 122.2321 | -0.086975 | 122.0352 | 1.4211e-13 | -0.031487 | -6.4092e-05 | -0.0036647 | -0.010168 | 0.008241 | -0.01755 | -0.0048667 | -0.0014849 | 0.017904 | 0.033476 | 0.012441 | 9.5928 | 9.5798 | 9.4137 | 9.4561 | 9.4787 | 9.6288 | 8.5224 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.032021 | 0.071851 | -0.11836 | 8.6094 | -112.5791 | 9.6797 | 9.5007 | 0.89127 | -112.5565 | -112.4064 | -0.031386 | -122.1018 | 0.1155 | 0.021466 | 0.052852 | -122.0032 | -121.9634 | 9.5431 | 9.5657 | 9.7158 | 9.6668 | -113.5128 | 0.020393 | 0.119 | 0.15883 | 0.16975 | -122.1536
4503.8125 | 122.0764 | -0.091553 | 122.081 | 1.4211e-13 | -0.0317 | -0.00027769 | -0.0034509 | -0.010809 | 0.0078136 | -0.01755 | -0.0048667 | -0.0016987 | 0.01769 | 0.033263 | 0.012868 | 9.579 | 9.5753 | 9.4183 | 9.4561 | 9.4787 | 9.6197 | 8.5316 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.11836 | 8.6231 | -112.6249 | 9.6706 | 9.5098 | 0.88669 | -112.6023 | -112.4613 | -0.026808 | -122.1476 | 0.11549 | 0.030623 | 0.057431 | -122.0352 | -122.0046 | 9.5477 | 9.5703 | 9.7112 | 9.6668 | -113.5494 | 0.024971 | 0.13731 | 0.16798 | 0.17433 | -122.1994
4505.5781 | 122.1771 | -0.059509 | 122.0627 | 1.4211e-13 | -0.031273 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0016987 | 0.017476 | 0.033904 | 0.012441 | 9.5699 | 9.557 | 9.3862 | 9.4332 | 9.4604 | 9.6105 | 8.5133 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.027442 | 0.07643 | -0.12294 | 8.5728 | -112.6294 | 9.6294 | 9.4457 | 0.87295 | -112.6023 | -112.4522 | -0.06343 | -122.1293 | 0.078871 | -0.006 | 0.05743 | -122.0352 | -121.9863 | 9.4928 | 9.5199 | 9.67 | 9.6165 | -113.5494 | -0.007073 | 0.086951 | 0.13594 | 0.14686 | -122.1856
4507.3594 | 122.1817 | -0.086975 | 122.0581 | 1.4211e-13 | -0.0317 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.0022892 | -0.0044395 | -0.0014849 | 0.018117 | 0.033476 | 0.012441 | 9.5653 | 9.5524 | 9.3862 | 9.4332 | 9.4604 | 9.6059 | 8.5178 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.1321 | 8.6048 | -112.6249 | 9.6523 | 9.4732 | 0.86838 | -112.5977 | -112.4522 | -0.045122 | -122.1293 | 0.10634 | 0.026045 | 0.071167 | -122.0123 | -121.9817 | 9.5202 | 9.5474 | 9.6929 | 9.6393 | -113.5403 | 0.015814 | 0.13273 | 0.1634 | 0.16975 | -122.1902
4509.0781 | 122.1313 | -0.09613 | 122.081 | 1.4211e-13 | -0.031487 | 0.00057691 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0019123 | 0.01769 | 0.03369 | 0.012655 | 9.5561 | 9.5432 | 9.3771 | 9.4195 | 9.4375 | 9.5876 | 8.5087 | 0.02852 | 0.087354 | -0.065509 | -0.071161 | 0.045757 | 0.07643 | -0.12752 | 8.6048 | -112.6615 | 9.6523 | 9.4732 | 0.86838 | -112.6435 | -112.4934 | -0.031388 | -122.1522 | 0.12465 | 0.030621 | 0.062009 | -122.0352 | -122.0046 | 9.5156 | 9.5337 | 9.6838 | 9.6393 | -113.5723 | 0.024969 | 0.14189 | 0.17256 | 0.18348 | -122.2085
4510.8438 | 122.0993 | -0.091553 | 122.0718 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010382 | 0.0076 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017904 | 0.033476 | 0.012868 | 9.5424 | 9.5386 | 9.3588 | 9.4149 | 9.4329 | 9.5876 | 8.5087 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.045757 | 0.071851 | -0.12752 | 8.6002 | -112.6569 | 9.634 | 9.4503 | 0.85006 | -112.6389 | -112.4842 | -0.035965 | -122.1476 | 0.12007 | 0.035202 | 0.071167 | -122.0261 | -122 | 9.5065 | 9.5245 | 9.6792 | 9.6302 | -113.5631 | 0.015814 | 0.13731 | 0.1634 | 0.17891 | -122.1994
4512.6094 | 122.1497 | -0.09613 | 122.0856 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.01755 | -0.0046531 | -0.0027669 | 0.01769 | 0.03369 | 0.012655 | 9.5424 | 9.5295 | 9.3542 | 9.4104 | 9.4284 | 9.5739 | 8.5133 | 0.02852 | 0.091933 | -0.065509 | -0.062004 | 0.045757 | 0.081008 | -0.12752 | 8.6094 | -112.6752 | 9.6385 | 9.4503 | 0.84091 | -112.6572 | -112.5117 | -0.031388 | -122.1476 | 0.12465 | 0.030621 | 0.062009 | -122.0398 | -122.0046 | 9.5065 | 9.5245 | 9.67 | 9.6256 | -113.5723 | 0.034126 | 0.14189 | 0.17714 | 0.18806 | -122.2131
4514.3906 | 122.2137 | -0.073242 | 122.0901 | 1.4211e-13 | -0.0317 | -0.00027769 | -0.0032373 | -0.010382 | 0.0076 | -0.0099192 | -0.0044395 | -0.0029805 | 0.018117 | 0.033263 | 0.012441 | 9.5241 | 9.5157 | 9.3496 | 9.3966 | 9.4192 | 9.5693 | 8.4995 | 0.02852 | 0.091933 | -0.065509 | -0.071161 | 0.041178 | 0.081008 | -0.12294 | 8.5728 | -112.6935 | 9.5973 | 9.4228 | 0.85006 | -112.6709 | -112.5208 | -0.049697 | -122.1613 | 0.10176 | 0.007733 | 0.05743 | -122.049 | -122.0091 | 9.4699 | 9.4924 | 9.6426 | 9.589 | -113.5906 | 0.002081 | 0.11442 | 0.15425 | 0.16518 | -122.2131
4516.1094 | 122.2321 | -0.073242 | 122.0581 | 1.4211e-13 | -0.031487 | -0.00049149 | -0.0036647 | -0.010595 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0027669 | 0.018331 | 0.03369 | 0.012868 | 9.5287 | 9.5249 | 9.3542 | 9.392 | 9.4238 | 9.5647 | 8.5087 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.0366 | 0.081008 | -0.12294 | 8.5819 | -112.6661 | 9.6019 | 9.4274 | 0.84549 | -112.6343 | -112.4934 | -0.049697 | -122.1293 | 0.10176 | 0.012312 | 0.062009 | -122.0215 | -121.9771 | 9.4653 | 9.497 | 9.638 | 9.5981 | -113.5494 | 0.002081 | 0.10984 | 0.15425 | 0.15144 | -122.181
4517.875 | 122.1451 | -0.10529 | 122.113 | 1.4211e-13 | -0.031487 | 0.00036331 | -0.0038783 | -0.010382 | 0.0078136 | -0.0099192 | -0.0050803 | -0.0023397 | 0.017904 | 0.03369 | 0.012441 | 9.5241 | 9.5249 | 9.3542 | 9.3966 | 9.4192 | 9.5602 | 8.5041 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.12752 | 8.6094 | -112.7164 | 9.6294 | 9.4595 | 0.85006 | -112.6938 | -112.5529 | -0.022232 | -122.1796 | 0.12923 | 0.044356 | 0.066588 | -122.0719 | -122.0366 | 9.5019 | 9.5245 | 9.6654 | 9.6302 | -113.6089 | 0.038704 | 0.14646 | 0.18172 | 0.19264 | -122.2406
4519.6562 | 122.168 | -0.10986 | 122.1039 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0044395 | -0.0023397 | 0.018331 | 0.033476 | 0.012441 | 9.5287 | 9.5203 | 9.345 | 9.3966 | 9.4238 | 9.5693 | 8.5041 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.07643 | -0.12752 | 8.614 | -112.7073 | 9.6385 | 9.4549 | 0.84091 | -112.6801 | -112.5346 | -0.017655 | -122.175 | 0.12923 | 0.048933 | 0.066588 | -122.0673 | -122.0275 | 9.5065 | 9.5336 | 9.6792 | 9.6302 | -113.5998 | 0.038702 | 0.14646 | 0.18629 | 0.19722 | -122.2314
4521.4219 | 122.1359 | -0.10071 | 122.1039 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0023397 | 0.018331 | 0.033476 | 0.012655 | 9.5195 | 9.5203 | 9.3404 | 9.3875 | 9.41 | 9.5647 | 8.4995 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.1321 | 8.6002 | -112.7164 | 9.6202 | 9.4411 | 0.84091 | -112.6938 | -112.5392 | -0.031389 | -122.1796 | 0.12007 | 0.039778 | 0.071167 | -122.0673 | -122.0275 | 9.4882 | 9.5108 | 9.6654 | 9.621 | -113.6043 | 0.024969 | 0.13731 | 0.17714 | 0.18348 | -122.236
4523.125 | 122.1313 | -0.10529 | 122.1039 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0032373 | -0.010382 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0025533 | 0.018331 | 0.033263 | 0.012441 | 9.5104 | 9.5112 | 9.345 | 9.3783 | 9.41 | 9.551 | 8.5041 | 0.019362 | 0.078197 | -0.056351 | -0.071161 | 0.045757 | 0.07643 | -0.1321 | 8.6094 | -112.7256 | 9.6156 | 9.4503 | 0.84091 | -112.6938 | -112.5529 | -0.026811 | -122.175 | 0.12465 | 0.048935 | 0.075746 | -122.0581 | -122.0275 | 9.4836 | 9.5153 | 9.6563 | 9.6165 | -113.5998 | 0.034125 | 0.15104 | 0.18172 | 0.18348 | -122.236
4524.9062 | 122.1451 | -0.09613 | 122.1085 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0036647 | -0.010382 | 0.008241 | -0.01755 | -0.0046531 | -0.0023397 | 0.018117 | 0.033476 | 0.012441 | 9.5058 | 9.502 | 9.3313 | 9.3646 | 9.3872 | 9.5418 | 8.4995 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.041178 | 0.071851 | -0.1321 | 8.5957 | -112.7439 | 9.6019 | 9.4274 | 0.83175 | -112.7213 | -112.5666 | -0.035967 | -122.1842 | 0.12007 | 0.0352 | 0.071167 | -122.0673 | -122.0366 | 9.4607 | 9.4833 | 9.638 | 9.5981 | -113.6089 | 0.020391 | 0.13731 | 0.16798 | 0.18348 | -122.2406
4526.6094 | 122.1176 | -0.10986 | 122.1268 | 1.4211e-13 | -0.031487 | 0.00036331 | -0.0036647 | -0.010595 | 0.0076 | -0.01755 | -0.0044395 | -0.0023397 | 0.017904 | 0.033263 | 0.012441 | 9.4966 | 9.4974 | 9.3313 | 9.3691 | 9.3917 | 9.5418 | 8.495 | 0.023941 | 0.091933 | -0.056351 | -0.071161 | 0.041178 | 0.067272 | -0.13668 | 8.6048 | -112.7576 | 9.6065 | 9.4411 | 0.83633 | -112.735 | -112.5849 | -0.026813 | -122.1979 | 0.1338 | 0.053512 | 0.080325 | -122.0856 | -122.0595 | 9.479 | 9.5016 | 9.6517 | 9.6073 | -113.6318 | 0.038702 | 0.15104 | 0.17713 | 0.2018 | -122.2634
4528.375 | 122.2183 | -0.059509 | 122.0901 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0029805 | 0.018117 | 0.03369 | 0.012655 | 9.492 | 9.4791 | 9.313 | 9.36 | 9.378 | 9.5327 | 8.4904 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.0366 | 0.081008 | -0.1321 | 8.5499 | -112.7302 | 9.5516 | 9.3725 | 0.8226 | -112.7122 | -112.5575 | -0.072588 | -122.1522 | 0.078871 | -0.001421 | 0.071167 | -122.0535 | -122.0091 | 9.4195 | 9.4375 | 9.5922 | 9.5386 | -113.5998 | -0.002495 | 0.096109 | 0.14052 | 0.14686 | -122.2222
4530.0938 | 122.1771 | -0.086975 | 122.1268 | 1.4211e-13 | -0.031487 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017904 | 0.033476 | 0.012655 | 9.4875 | 9.4745 | 9.3038 | 9.36 | 9.378 | 9.5327 | 8.495 | 0.023941 | 0.087354 | -0.065509 | -0.075739 | 0.0366 | 0.071851 | -0.13668 | 8.5819 | -112.7668 | 9.5744 | 9.3908 | 0.80886 | -112.7488 | -112.5941 | -0.049701 | -122.2025 | 0.11092 | 0.021466 | 0.071167 | -122.0902 | -122.0549 | 9.447 | 9.465 | 9.6197 | 9.5615 | -113.6318 | 0.011236 | 0.12357 | 0.15883 | 0.17433 | -122.2634
4531.8594 | 122.2549 | -0.07782 | 122.0764 | 1.4211e-13 | -0.0317 | -6.4092e-05 | -0.0036647 | -0.010168 | 0.0080272 | -0.02518 | -0.0046531 | -0.0027669 | 0.018117 | 0.03369 | 0.012014 | 9.4692 | 9.47 | 9.3084 | 9.3463 | 9.3734 | 9.5144 | 8.4858 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.07643 | -0.1321 | 8.5636 | -112.7302 | 9.547 | 9.3862 | 0.8226 | -112.703 | -112.5621 | -0.054277 | -122.1476 | 0.10176 | 0.01689 | 0.071167 | -122.0398 | -122 | 9.4241 | 9.4512 | 9.5922 | 9.5478 | -113.5906 | 0.006659 | 0.11442 | 0.15425 | 0.1606 | -122.2085
4533.6406 | 122.2412 | -0.045776 | 122.0901 | 1.4211e-13 | -0.0317 | -0.00027769 | -0.0036647 | -0.010168 | 0.0080272 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017904 | 0.033476 | 0.012014 | 9.4692 | 9.47 | 9.2992 | 9.3463 | 9.3643 | 9.5189 | 8.4904 | 0.023941 | 0.078197 | -0.065509 | -0.075739 | 0.041178 | 0.07643 | -0.13668 | 8.5361 | -112.7439 | 9.5149 | 9.345 | 0.80886 | -112.7259 | -112.5712 | -0.0909 | -122.1659 | 0.069717 | -0.019733 | 0.071167 | -122.049 | -122.0137 | 9.392 | 9.41 | 9.5647 | 9.5157 | -113.5998 | -0.029963 | 0.086954 | 0.12221 | 0.12397 | -122.2268
4535.4062 | 122.2 | -0.091553 | 122.1268 | 1.4211e-13 | -0.031487 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0025533 | 0.018117 | 0.03369 | 0.012227 | 9.4692 | 9.47 | 9.2992 | 9.3417 | 9.3688 | 9.5144 | 8.4904 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.1321 | 8.5819 | -112.7851 | 9.5607 | 9.3908 | 0.80886 | -112.7579 | -112.6124 | -0.040544 | -122.1979 | 0.11549 | 0.030623 | 0.071167 | -122.0902 | -122.0549 | 9.4332 | 9.4604 | 9.6059 | 9.5615 | -113.6364 | 0.020392 | 0.12815 | 0.1634 | 0.17891 | -122.2589
4537.1094 | 122.1451 | -0.11444 | 122.168 | 1.4211e-13 | -0.031273 | 0.00014951 | -0.0032373 | -0.010382 | 0.0078136 | -0.01755 | -0.0048667 | -0.0025533 | 0.017476 | 0.033476 | 0.012227 | 9.4737 | 9.4608 | 9.2947 | 9.3417 | 9.3597 | 9.5098 | 8.4858 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.07643 | -0.12752 | 8.6002 | -112.8263 | 9.5882 | 9.4091 | 0.80886 | -112.8083 | -112.6582 | -0.013077 | -122.2391 | 0.1338 | 0.053511 | 0.066588 | -122.1268 | -122.0915 | 9.4561 | 9.4741 | 9.6242 | 9.5752 | -113.6822 | 0.04328 | 0.15562 | 0.19087 | 0.2018 | -122.2955
4538.875 | 122.1451 | -0.10986 | 122.1634 | 1.4211e-13 | -0.032128 | 0.00014951 | -0.0034509 | -0.010168 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0027669 | 0.01769 | 0.033904 | 0.012655 | 9.4554 | 9.4471 | 9.2855 | 9.3234 | 9.3505 | 9.4961 | 8.4858 | 0.02852 | 0.091933 | -0.06093 | -0.071161 | 0.041178 | 0.081008 | -0.12752 | 8.5957 | -112.84 | 9.5653 | 9.3954 | 0.79971 | -112.8129 | -112.6673 | -0.017655 | -122.2346 | 0.13838 | 0.048933 | 0.066588 | -122.1222 | -122.0824 | 9.4332 | 9.4604 | 9.6059 | 9.5569 | -113.6776 | 0.038702 | 0.15104 | 0.19087 | 0.2018 | -122.2909
4540.6406 | 122.1542 | -0.1236 | 122.1725 | 1.4211e-13 | -0.0317 | 0.00014951 | -0.0036647 | -0.010595 | 0.0078136 | -0.01755 | -0.0048667 | -0.0025533 | 0.017476 | 0.03369 | 0.012227 | 9.4508 | 9.4516 | 9.2763 | 9.3279 | 9.3459 | 9.5006 | 8.4812 | 0.033099 | 0.082776 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 8.6048 | -112.8446 | 9.5744 | 9.3999 | 0.79513 | -112.8266 | -112.6719 | -0.003922 | -122.2391 | 0.1567 | 0.058087 | 0.062009 | -122.1359 | -122.0961 | 9.4515 | 9.4695 | 9.6242 | 9.5752 | -113.6913 | 0.057014 | 0.1602 | 0.20003 | 0.20637 | -122.3001
4542.3438 | 122.2321 | -0.068665 | 122.1176 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0038783 | -0.010382 | 0.0078136 | -0.02518 | -0.0046531 | -0.0027669 | 0.017476 | 0.03369 | 0.012441 | 9.4508 | 9.4516 | 9.2763 | 9.3142 | 9.3505 | 9.4869 | 8.4812 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.041178 | 0.085587 | -0.1321 | 8.5499 | -112.8034 | 9.5195 | 9.345 | 0.79513 | -112.7671 | -112.6307 | -0.063432 | -122.1934 | 0.092606 | 0.007735 | 0.071167 | -122.0764 | -122.032 | 9.3829 | 9.4192 | 9.5556 | 9.5203 | -113.6364 | -0.007074 | 0.10984 | 0.15425 | 0.15602 | -122.2497
4544.1094 | 122.1588 | -0.09613 | 122.1359 | 1.4211e-13 | -0.0317 | -0.00027769 | -0.0034509 | -0.010595 | 0.0076 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.03369 | 0.012441 | 9.4417 | 9.4471 | 9.2809 | 9.3234 | 9.3414 | 9.4869 | 8.4812 | 0.02852 | 0.091933 | -0.065509 | -0.080318 | 0.032021 | 0.071851 | -0.1321 | 8.5773 | -112.8126 | 9.5378 | 9.3771 | 0.79971 | -112.7946 | -112.649 | -0.035967 | -122.2162 | 0.12465 | 0.030621 | 0.066588 | -122.1039 | -122.0641 | 9.4195 | 9.4375 | 9.583 | 9.5432 | -113.6547 | 0.015812 | 0.12815 | 0.16798 | 0.18806 | -122.268
4545.875 | 122.2458 | -0.068665 | 122.0718 | 1.4211e-13 | -0.0317 | -6.4092e-05 | -0.0036647 | -0.0099547 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0027669 | 0.01769 | 0.03369 | 0.012441 | 9.4279 | 9.4242 | 9.258 | 9.3005 | 9.3185 | 9.4732 | 8.4629 | 0.02852 | 0.091933 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.12752 | 8.5316 | -112.7714 | 9.4966 | 9.3267 | 0.79513 | -112.7534 | -112.5987 | -0.058853 | -122.1384 | 0.097185 | 0.003156 | 0.062009 | -122.0307 | -121.9954 | 9.3691 | 9.3871 | 9.5418 | 9.4928 | -113.6089 | 0.002083 | 0.10984 | 0.1451 | 0.1606 | -122.1994
4547.6562 | 122.1542 | -0.086975 | 122.168 | 1.4211e-13 | -0.0317 | 0.00014951 | -0.0034509 | -0.010168 | 0.0076 | -0.0099192 | -0.0046531 | -0.0025533 | 0.01769 | 0.033476 | 0.012441 | 9.4142 | 9.415 | 9.2351 | 9.2867 | 9.3002 | 9.4548 | 8.4675 | 0.023941 | 0.091933 | -0.070087 | -0.071161 | 0.0366 | 0.071851 | -0.12752 | 8.5545 | -112.8812 | 9.5012 | 9.3221 | 0.76766 | -112.8678 | -112.7131 | -0.040543 | -122.2391 | 0.11092 | 0.016888 | 0.057431 | -122.1314 | -122.0961 | 9.3737 | 9.3871 | 9.5418 | 9.502 | -113.7005 | 0.015814 | 0.12357 | 0.15883 | 0.17891 | -122.2955
4549.4219 | 122.2183 | -0.10071 | 122.1542 | 1.4211e-13 | -0.0317 | 0.00036331 | -0.0036647 | -0.010595 | 0.0078136 | -0.01755 | -0.0046531 | -0.0027669 | 0.01769 | 0.033263 | 0.012227 | 9.4051 | 9.4013 | 9.226 | 9.2638 | 9.3002 | 9.4503 | 8.4583 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.081008 | -0.13668 | 8.559 | -112.8904 | 9.5058 | 9.3267 | 0.76766 | -112.8541 | -112.704 | -0.035968 | -122.2208 | 0.12465 | 0.039778 | 0.075746 | -122.1131 | -122.0732 | 9.3646 | 9.4009 | 9.551 | 9.502 | -113.6959 | 0.034126 | 0.14189 | 0.18172 | 0.18806 | -122.2909
4551.125 | 122.1863 | -0.10529 | 122.1542 | 1.4211e-13 | -0.031914 | 0.00014951 | -0.0034509 | -0.010595 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0023397 | 0.017476 | 0.033476 | 0.012441 | 9.3867 | 9.383 | 9.2122 | 9.2501 | 9.2818 | 9.4274 | 8.4537 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.12752 | 8.559 | -112.9041 | 9.492 | 9.3175 | 0.75851 | -112.8724 | -112.7269 | -0.022232 | -122.2208 | 0.12465 | 0.039777 | 0.062009 | -122.1131 | -122.0778 | 9.3554 | 9.3871 | 9.5327 | 9.4882 | -113.7005 | 0.038704 | 0.14646 | 0.18172 | 0.19264 | -122.2818
4552.8906 | 122.2687 | -0.068665 | 122.0947 | 1.4211e-13 | -0.031914 | 0.00036331 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017476 | 0.03369 | 0.012014 | 9.3867 | 9.3784 | 9.2077 | 9.2501 | 9.2727 | 9.432 | 8.4492 | 0.019362 | 0.082776 | -0.070087 | -0.066582 | 0.0366 | 0.085587 | -0.12752 | 8.5178 | -112.8446 | 9.4554 | 9.2763 | 0.75851 | -112.822 | -112.6628 | -0.058853 | -122.1613 | 0.088027 | -0.001422 | 0.057431 | -122.0581 | -122.0091 | 9.3188 | 9.3413 | 9.5006 | 9.447 | -113.6456 | 0.002083 | 0.10526 | 0.15425 | 0.15144 | -122.2222
4554.6562 | 122.287 | -0.054932 | 122.113 | 1.4211e-13 | -0.031914 | 0.00014951 | -0.0030235 | -0.010168 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0025533 | 0.01769 | 0.033476 | 0.012441 | 9.3593 | 9.3601 | 9.2031 | 9.241 | 9.2727 | 9.4182 | 8.44 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.1321 | 8.4949 | -112.8721 | 9.4142 | 9.258 | 0.76309 | -112.8404 | -112.6948 | -0.077165 | -122.1796 | 0.078873 | -0.010577 | 0.066588 | -122.0764 | -122.0366 | 9.2959 | 9.3276 | 9.4731 | 9.415 | -113.673 | -0.01165 | 0.091532 | 0.13136 | 0.13771 | -122.2451
4556.3594 | 122.1771 | -0.11444 | 122.1725 | 1.4211e-13 | -0.031914 | 0.00014951 | -0.0036647 | -0.010595 | 0.0073864 | -0.02518 | -0.0044395 | -0.0023397 | 0.017476 | 0.033476 | 0.012014 | 9.3639 | 9.3509 | 9.1848 | 9.2272 | 9.2589 | 9.3999 | 8.44 | 0.02852 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.071851 | -0.1321 | 8.5544 | -112.9453 | 9.4783 | 9.2992 | 0.74477 | -112.9136 | -112.7726 | -0.017656 | -122.2391 | 0.14296 | 0.048932 | 0.066588 | -122.1359 | -122.1007 | 9.3417 | 9.3734 | 9.5143 | 9.4654 | -113.7325 | 0.047859 | 0.15104 | 0.18629 | 0.2018 | -122.3046
4558.125 | 122.2641 | -0.073242 | 122.1176 | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0076 | -0.0099192 | -0.0044395 | -0.0023397 | 0.017476 | 0.033476 | 0.012227 | 9.3501 | 9.3418 | 9.1756 | 9.2226 | 9.2498 | 9.3953 | 8.4354 | 0.023941 | 0.078197 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.12294 | 8.5087 | -112.895 | 9.4234 | 9.2489 | 0.74019 | -112.8678 | -112.7223 | -0.049697 | -122.1934 | 0.097183 | 0.012312 | 0.062009 | -122.081 | -122.0412 | 9.2959 | 9.323 | 9.4686 | 9.415 | -113.6822 | -0.002497 | 0.10984 | 0.14967 | 0.15144 | -122.2406
4559.8438 | 122.1771 | -0.091553 | 122.1542 | 1.4211e-13 | -0.031914 | 0.00014951 | -0.0034509 | -0.010382 | 0.0076 | -0.02518 | -0.0046531 | -0.0023397 | 0.01769 | 0.033904 | 0.012227 | 9.341 | 9.3418 | 9.1665 | 9.2181 | 9.2406 | 9.3816 | 8.44 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.13668 | 8.5316 | -112.9362 | 9.4325 | 9.258 | 0.72646 | -112.9136 | -112.7726 | -0.045123 | -122.2254 | 0.11549 | 0.030623 | 0.075746 | -122.1222 | -122.0778 | 9.3096 | 9.3322 | 9.4731 | 9.4333 | -113.7142 | 0.020392 | 0.12357 | 0.16798 | 0.17891 | -122.2909
4561.6094 | 122.2458 | -0.064087 | 122.1268 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0044395 | -0.0025533 | 0.01769 | 0.03369 | 0.012227 | 9.3318 | 9.3326 | 9.1573 | 9.2043 | 9.2315 | 9.3816 | 8.4263 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.032021 | 0.071851 | -0.12752 | 8.4904 | -112.9224 | 9.3959 | 9.2214 | 0.73104 | -112.8953 | -112.7452 | -0.063431 | -122.1934 | 0.092607 | 0.003157 | 0.066588 | -122.0947 | -122.0549 | 9.2684 | 9.2956 | 9.4457 | 9.3967 | -113.7005 | -0.002495 | 0.096108 | 0.13594 | 0.14686 | -122.2543
4563.3906 | 122.3099 | -0.050354 | 122.113 | 1.4211e-13 | -0.031914 | 0.00036331 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0044395 | -0.0021259 | 0.017476 | 0.033476 | 0.012227 | 9.3318 | 9.328 | 9.1527 | 9.1997 | 9.2269 | 9.377 | 8.4263 | 0.023941 | 0.087354 | -0.070087 | -0.071161 | 0.0366 | 0.071851 | -0.12752 | 8.4766 | -112.9133 | 9.3822 | 9.2031 | 0.72646 | -112.8861 | -112.736 | -0.077164 | -122.1842 | 0.074295 | -0.019733 | 0.057431 | -122.0764 | -122.0412 | 9.2501 | 9.2772 | 9.4274 | 9.3784 | -113.6868 | -0.020807 | 0.086954 | 0.12221 | 0.13771 | -122.2406
4565.1719 | 122.3007 | -0.064087 | 122.0993 | 1.4211e-13 | -0.032128 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017476 | 0.033476 | 0.012014 | 9.3272 | 9.3143 | 9.1527 | 9.1906 | 9.2223 | 9.3679 | 8.4263 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.12752 | 8.4904 | -112.9087 | 9.3913 | 9.2168 | 0.72646 | -112.877 | -112.7315 | -0.063431 | -122.1705 | 0.088028 | 0.003157 | 0.066588 | -122.0627 | -122.0275 | 9.2547 | 9.2864 | 9.4319 | 9.3784 | -113.673 | -0.007074 | 0.10069 | 0.13594 | 0.15144 | -122.2268
4566.9531 | 122.1954 | -0.11902 | 122.1634 | 1.4211e-13 | -0.031914 | -0.00027769 | -0.0036647 | -0.010809 | 0.0080272 | -0.0099192 | -0.0048667 | -0.0023397 | 0.01769 | 0.033904 | 0.012227 | 9.3226 | 9.3143 | 9.1436 | 9.1997 | 9.2223 | 9.3633 | 8.4308 | 0.019362 | 0.087354 | -0.070087 | -0.080318 | 0.0366 | 0.081008 | -0.1321 | 8.5499 | -112.9636 | 9.4417 | 9.2626 | 0.71273 | -112.9411 | -112.8001 | -0.013078 | -122.2437 | 0.13838 | 0.048932 | 0.06201 | -122.1268 | -122.0824 | 9.3188 | 9.3413 | 9.4823 | 9.4333 | -113.7325 | 0.038701 | 0.15562 | 0.20003 | 0.20637 | -122.2955
4568.6562 | 122.1909 | -0.11444 | 122.1542 | 1.4211e-13 | -0.0317 | -0.00049149 | -0.0036647 | -0.010382 | 0.0080272 | -0.0022892 | -0.0046531 | -0.0023397 | 0.01769 | 0.033904 | 0.012655 | 9.3226 | 9.3143 | 9.1482 | 9.1997 | 9.2269 | 9.3724 | 8.4263 | 0.023941 | 0.082776 | -0.070087 | -0.080318 | 0.0366 | 0.081008 | -0.1321 | 8.5407 | -112.9545 | 9.4371 | 9.2626 | 0.72188 | -112.9273 | -112.7818 | -0.017656 | -122.2346 | 0.13838 | 0.044354 | 0.06201 | -122.1176 | -122.0732 | 9.3142 | 9.3413 | 9.4869 | 9.4287 | -113.728 | 0.034123 | 0.15104 | 0.19545 | 0.19722 | -122.2863
4570.4375 | 122.2275 | -0.091553 | 122.1634 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0034509 | -0.0099547 | 0.0076 | -0.01755 | -0.0048667 | -0.0027669 | 0.017476 | 0.033904 | 0.012441 | 9.3135 | 9.3189 | 9.1527 | 9.1952 | 9.2132 | 9.3679 | 8.4217 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.081008 | -0.1321 | 8.5132 | -112.9682 | 9.405 | 9.2443 | 0.73104 | -112.9502 | -112.7955 | -0.040544 | -122.23 | 0.11091 | 0.026044 | 0.066588 | -122.1268 | -122.0824 | 9.2867 | 9.3047 | 9.4594 | 9.4104 | -113.7417 | 0.024971 | 0.12815 | 0.17256 | 0.17891 | -122.2955
4572.2031 | 122.3099 | -0.07782 | 122.1313 | 1.4211e-13 | -0.031914 | -0.00027769 | -0.0038783 | -0.010595 | 0.0071726 | -0.01755 | -0.0046531 | -0.0027669 | 0.017476 | 0.033904 | 0.012441 | 9.3135 | 9.3143 | 9.1436 | 9.186 | 9.2086 | 9.3587 | 8.4263 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.041178 | 0.07643 | -0.1321 | 8.5041 | -112.9453 | 9.3913 | 9.2214 | 0.7173 | -112.9228 | -112.7727 | -0.054277 | -122.2071 | 0.097182 | 0.021469 | 0.075746 | -122.0902 | -122.0549 | 9.2638 | 9.2864 | 9.4365 | 9.3921 | -113.7051 | 0.002081 | 0.119 | 0.15425 | 0.16517 | -122.2634
4573.9688 | 122.1863 | -0.10529 | 122.1817 | 1.4211e-13 | -0.0317 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.0076 | -0.01755 | -0.0046531 | -0.0027669 | 0.017476 | 0.033904 | 0.012227 | 9.3089 | 9.3143 | 9.1436 | 9.186 | 9.2086 | 9.3587 | 8.4263 | 0.019362 | 0.091933 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.12752 | 8.5316 | -112.9957 | 9.4142 | 9.2489 | 0.7173 | -112.9731 | -112.823 | -0.022232 | -122.2529 | 0.12465 | 0.044356 | 0.066588 | -122.1497 | -122.1053 | 9.2913 | 9.3139 | 9.464 | 9.4196 | -113.7554 | 0.034125 | 0.13731 | 0.18172 | 0.19722 | -122.3092
4575.6875 | 122.3236 | -0.064087 | 122.168 | 1.4211e-13 | -0.032128 | -0.00049149 | -0.0034509 | -0.010382 | 0.0080272 | 0.0053413 | -0.0046531 | -0.0027669 | 0.017476 | 0.03369 | 0.012227 | 9.2998 | 9.296 | 9.1298 | 9.1769 | 9.1994 | 9.345 | 8.4125 | 0.023941 | 0.087354 | -0.070087 | -0.071161 | 0.041178 | 0.07643 | -0.1321 | 8.4766 | -112.9911 | 9.3638 | 9.1939 | 0.71731 | -112.9686 | -112.823 | -0.06801 | -122.2391 | 0.088028 | -0.006 | 0.06201 | -122.1268 | -122.0915 | 9.2409 | 9.2635 | 9.409 | 9.3601 | -113.7554 | -0.007074 | 0.10526 | 0.14052 | 0.15144 | -122.3001
4577.4531 | 122.2046 | -0.11444 | 122.1771 | 1.4211e-13 | -0.031914 | 0.00036331 | -0.0034509 | -0.010595 | 0.0073864 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017476 | 0.03369 | 0.012227 | 9.2952 | 9.296 | 9.1298 | 9.1677 | 9.1857 | 9.3358 | 8.4125 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.041178 | 0.07643 | -0.1321 | 8.527 | -113.0094 | 9.4096 | 9.2443 | 0.71731 | -112.9914 | -112.8413 | -0.017656 | -122.2483 | 0.13838 | 0.05809 | 0.075746 | -122.1359 | -122.1007 | 9.2821 | 9.3001 | 9.4502 | 9.4104 | -113.7646 | 0.04328 | 0.15562 | 0.19087 | 0.2018 | -122.3092
4579.1562 | 122.2 | -0.12817 | 122.1725 | 1.4211e-13 | -0.031914 | -0.00027769 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017263 | 0.034117 | 0.012441 | 9.286 | 9.2868 | 9.1161 | 9.1585 | 9.1857 | 9.3404 | 8.4125 | 0.02852 | 0.082776 | -0.065509 | -0.075739 | 0.0366 | 0.07643 | -0.12752 | 8.5407 | -113.014 | 9.4142 | 9.2443 | 0.70357 | -112.9869 | -112.8322 | 0.000656 | -122.2483 | 0.15669 | 0.062665 | 0.062009 | -122.1359 | -122.0961 | 9.2867 | 9.3139 | 9.4686 | 9.415 | -113.76 | 0.052435 | 0.16477 | 0.2046 | 0.21095 | -122.3001
4580.9219 | 122.2504 | -0.086975 | 122.168 | 1.4211e-13 | -0.0317 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0044395 | -0.0023397 | 0.01769 | 0.033904 | 0.012441 | 9.286 | 9.2822 | 9.1161 | 9.1585 | 9.1765 | 9.3358 | 8.4125 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.050335 | 0.081008 | -0.1321 | 8.4995 | -113.0094 | 9.373 | 9.2031 | 0.70357 | -112.9914 | -112.8322 | -0.045122 | -122.2391 | 0.10634 | 0.026045 | 0.071167 | -122.1176 | -122.087 | 9.2455 | 9.2635 | 9.4228 | 9.3692 | -113.7554 | 0.015814 | 0.13731 | 0.16798 | 0.16975 | -122.3001
4582.7031 | 122.3328 | -0.064087 | 122.1405 | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0029805 | 0.01769 | 0.033904 | 0.012227 | 9.2631 | 9.2593 | 9.0886 | 9.1402 | 9.1674 | 9.3129 | 8.408 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.045757 | 0.07643 | -0.13668 | 8.472 | -113.0003 | 9.3272 | 9.1527 | 0.68068 | -112.9731 | -112.8276 | -0.072589 | -122.2117 | 0.088028 | -0.001422 | 0.071167 | -122.0947 | -122.0641 | 9.2043 | 9.2315 | 9.377 | 9.3234 | -113.7326 | -0.007074 | 0.10984 | 0.14052 | 0.15144 | -122.2772
4584.4688 | 122.3282 | -0.054932 | 122.1542 | 1.4211e-13 | -0.0317 | 0.00014951 | -0.0038783 | -0.010382 | 0.0076 | -0.01755 | -0.0044395 | -0.0027669 | 0.017476 | 0.033904 | 0.012227 | 9.2631 | 9.2548 | 9.0886 | 9.1219 | 9.1628 | 9.3129 | 8.4034 | 0.023941 | 0.078197 | -0.056351 | -0.075739 | 0.045757 | 0.07643 | -0.13668 | 8.4583 | -113.0323 | 9.3181 | 9.1436 | 0.68526 | -112.9914 | -112.8413 | -0.081744 | -122.23 | 0.078873 | -0.001419 | 0.080325 | -122.1085 | -122.0778 | 9.1768 | 9.2177 | 9.3678 | 9.3097 | -113.7509 | -0.020807 | 0.10069 | 0.13136 | 0.13313 | -122.2909
4586.1719 | 122.2092 | -0.11902 | 122.1954 | 1.4211e-13 | -0.032128 | -0.00027769 | -0.0034509 | -0.010595 | 0.0076 | 0.0053413 | -0.0046531 | -0.0027669 | 0.017476 | 0.03369 | 0.012441 | 9.2494 | 9.2502 | 9.0795 | 9.1265 | 9.1536 | 9.3038 | 8.3988 | 0.02852 | 0.087354 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.12752 | 8.5178 | -113.0689 | 9.3684 | 9.1985 | 0.68068 | -113.0418 | -112.8917 | -0.008499 | -122.2666 | 0.14754 | 0.05351 | 0.062009 | -122.1543 | -122.119 | 9.2455 | 9.2726 | 9.4228 | 9.3692 | -113.7966 | 0.047858 | 0.1602 | 0.19545 | 0.20637 | -122.323
4587.9375 | 122.3373 | -0.054932 | 122.1451 | 1.4211e-13 | -0.032128 | 0.00014951 | -0.0036647 | -0.010595 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0023397 | 0.01769 | 0.034117 | 0.012227 | 9.254 | 9.2456 | 9.0749 | 9.1173 | 9.1353 | 9.2854 | 8.3942 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.045757 | 0.07643 | -0.12752 | 8.4491 | -113.0277 | 9.3089 | 9.1298 | 0.68068 | -113.0098 | -112.8596 | -0.072586 | -122.2208 | 0.078873 | -0.005998 | 0.066588 | -122.0993 | -122.0687 | 9.1723 | 9.1902 | 9.3404 | 9.3005 | -113.7509 | -0.020807 | 0.10069 | 0.13136 | 0.14229 | -122.2726
4589.7188 | 122.2046 | -0.10529 | 122.1817 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0034509 | -0.010595 | 0.0076 | -0.01755 | -0.0044395 | -0.0029805 | 0.017476 | 0.03369 | 0.012441 | 9.2402 | 9.2319 | 9.0566 | 9.1036 | 9.1307 | 9.2809 | 8.3896 | 0.019362 | 0.082776 | -0.06093 | -0.075739 | 0.041178 | 0.067272 | -0.1321 | 8.4949 | -113.0781 | 9.3455 | 9.1619 | 0.66695 | -113.051 | -112.9008 | -0.026811 | -122.2574 | 0.12465 | 0.044356 | 0.071167 | -122.1405 | -122.1144 | 9.2089 | 9.236 | 9.3861 | 9.3372 | -113.7921 | 0.029547 | 0.14646 | 0.17256 | 0.18806 | -122.3138
4591.5 | 122.2961 | -0.073242 | 122.1725 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0032373 | -0.010168 | 0.0076 | -0.01755 | -0.0044395 | -0.0027669 | 0.01769 | 0.034117 | 0.012014 | 9.2311 | 9.2181 | 9.0612 | 9.099 | 9.1262 | 9.2763 | 8.3805 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.045757 | 0.081008 | -0.1321 | 8.4537 | -113.0735 | 9.3043 | 9.1344 | 0.68068 | -113.0464 | -112.8963 | -0.058855 | -122.2483 | 0.097183 | 0.007733 | 0.066588 | -122.1268 | -122.0915 | 9.1723 | 9.1994 | 9.3495 | 9.2914 | -113.7921 | -0.002497 | 0.119 | 0.15425 | 0.15602 | -122.3046
4593.2031 | 122.2961 | -0.082397 | 122.1497 | 1.4211e-13 | -0.031914 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0042257 | -0.0027669 | 0.01769 | 0.033904 | 0.012227 | 9.2128 | 9.2136 | 9.0429 | 9.0899 | 9.117 | 9.2671 | 8.3759 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.045757 | 0.071851 | -0.12752 | 8.4583 | -113.0598 | 9.2952 | 9.1252 | 0.66695 | -113.0327 | -112.8825 | -0.045121 | -122.2254 | 0.10176 | 0.016888 | 0.062009 | -122.1039 | -122.0778 | 9.1723 | 9.1994 | 9.3495 | 9.296 | -113.7738 | 0.006658 | 0.12815 | 0.15425 | 0.16975 | -122.2772
4594.9844 | 122.1771 | -0.10986 | 122.2 | 1.4211e-13 | -0.031914 | -0.00027769 | -0.0032373 | -0.010809 | 0.0076 | 0.0053413 | -0.0044395 | -0.0027669 | 0.017476 | 0.033263 | 0.012227 | 9.2036 | 9.209 | 9.0383 | 9.0807 | 9.1124 | 9.2534 | 8.3713 | 0.023941 | 0.096512 | -0.06093 | -0.075739 | 0.045757 | 0.07643 | -0.12294 | 8.4812 | -113.1193 | 9.3135 | 9.1481 | 0.66695 | -113.0876 | -112.9466 | -0.013076 | -122.2758 | 0.1338 | 0.048933 | 0.062009 | -122.1543 | -122.1236 | 9.1906 | 9.2223 | 9.3632 | 9.3188 | -113.8287 | 0.034124 | 0.15562 | 0.18629 | 0.20638 | -122.323
4596.7031 | 122.2092 | -0.10986 | 122.2046 | 1.4211e-13 | -0.032128 | 0.00014951 | -0.0034509 | -0.010595 | 0.0080272 | -0.0022892 | -0.0044395 | -0.0025533 | 0.017476 | 0.03369 | 0.012441 | 9.2082 | 9.209 | 9.0429 | 9.099 | 9.1078 | 9.258 | 8.3805 | 0.023941 | 0.082776 | -0.065509 | -0.080318 | 0.045757 | 0.081008 | -0.12752 | 8.4903 | -113.1056 | 9.318 | 9.1527 | 0.66237 | -113.0968 | -112.9466 | -0.017655 | -122.2849 | 0.1338 | 0.044354 | 0.062009 | -122.1588 | -122.1236 | 9.2089 | 9.2177 | 9.3678 | 9.3188 | -113.8241 | 0.029545 | 0.15562 | 0.19087 | 0.19264 | -122.3321
4598.4688 | 122.287 | -0.10071 | 122.1634 | 1.4211e-13 | -0.032128 | 0.00014951 | -0.0036647 | -0.010168 | 0.0076 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017476 | 0.03369 | 0.012441 | 9.2036 | 9.1998 | 9.0291 | 9.0761 | 9.1078 | 9.258 | 8.3759 | 0.023941 | 0.091933 | -0.065509 | -0.071161 | 0.045757 | 0.07643 | -0.12752 | 8.4766 | -113.0873 | 9.3043 | 9.1298 | 0.65321 | -113.0556 | -112.9054 | -0.02681 | -122.2346 | 0.12465 | 0.035199 | 0.062009 | -122.1176 | -122.087 | 9.1768 | 9.2085 | 9.3587 | 9.3005 | -113.7875 | 0.029547 | 0.14647 | 0.17714 | 0.19264 | -122.2909
4600.1875 | 122.2321 | -0.09613 | 122.2046 | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0032373 | -0.010809 | 0.0078136 | -0.01755 | -0.0048667 | -0.0027669 | 0.01769 | 0.033904 | 0.012014 | 9.199 | 9.1952 | 9.0337 | 9.0807 | 9.0987 | 9.2488 | 8.3713 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.050335 | 0.07643 | -0.1321 | 8.4675 | -113.1239 | 9.2952 | 9.1298 | 0.66237 | -113.1059 | -112.9558 | -0.035967 | -122.2758 | 0.12007 | 0.039779 | 0.075746 | -122.1543 | -122.1282 | 9.1768 | 9.1948 | 9.3449 | 9.2914 | -113.8333 | 0.024969 | 0.14646 | 0.17256 | 0.18348 | -122.3367
4601.9531 | 122.3419 | -0.07782 | 122.1542 | 1.4211e-13 | -0.032128 | -0.00027769 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0044395 | -0.0025533 | 0.017904 | 0.033904 | 0.0118 | 9.1899 | 9.1861 | 9.02 | 9.0624 | 9.0895 | 9.2396 | 8.3667 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.0366 | 0.081008 | -0.12752 | 8.4446 | -113.0918 | 9.2677 | 9.0978 | 0.65322 | -113.0647 | -112.9146 | -0.049698 | -122.2208 | 0.10176 | 0.021469 | 0.071167 | -122.1176 | -122.0732 | 9.1402 | 9.1673 | 9.3175 | 9.2639 | -113.7875 | 0.011238 | 0.11442 | 0.15883 | 0.16517 | -122.2818
4603.6562 | 122.3648 | -0.054932 | 122.1451 | 1.4211e-13 | -0.032128 | -6.4092e-05 | -0.0038783 | -0.010168 | 0.0078136 | -0.01755 | -0.0044395 | -0.0025533 | 0.017904 | 0.034117 | 0.012227 | 9.1578 | 9.1632 | 8.9833 | 9.0395 | 9.0529 | 9.2122 | 8.353 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.041178 | 0.07643 | -0.13668 | 8.4079 | -113.1056 | 9.2128 | 9.0383 | 0.63033 | -113.0922 | -112.9329 | -0.081744 | -122.2162 | 0.078873 | -0.005998 | 0.075746 | -122.1039 | -122.0687 | 9.0944 | 9.1078 | 9.2671 | 9.2181 | -113.7921 | -0.016229 | 0.09611 | 0.13136 | 0.13313 | -122.2818
4605.4219 | 122.3145 | -0.050354 | 122.1771 | 1.4211e-13 | -0.032128 | 0.00036331 | -0.0036647 | -0.010595 | 0.0078136 | -0.01755 | -0.0046531 | -0.0023397 | 0.017904 | 0.033476 | 0.012227 | 9.1578 | 9.154 | 8.9788 | 9.0303 | 9.0437 | 9.203 | 8.3484 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.045757 | 0.081008 | -0.1321 | 8.3988 | -113.1468 | 9.2082 | 9.0291 | 0.63033 | -113.1334 | -112.9741 | -0.081743 | -122.2529 | 0.074295 | -0.010576 | 0.071167 | -122.1314 | -122.0961 | 9.0807 | 9.0941 | 9.2534 | 9.2044 | -113.8287 | -0.025385 | 0.096111 | 0.13136 | 0.13771 | -122.3092
4607.125 | 122.3419 | -0.073242 | 122.1588 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0076 | -0.01755 | -0.0048667 | -0.0023397 | 0.017904 | 0.034117 | 0.012655 | 9.1395 | 9.1357 | 8.9696 | 9.0258 | 9.0346 | 9.1801 | 8.3438 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.050335 | 0.081008 | -0.12752 | 8.4171 | -113.133 | 9.2128 | 9.0428 | 0.62575 | -113.1242 | -112.9787 | -0.054276 | -122.23 | 0.092604 | 0.012312 | 0.066588 | -122.1085 | -122.0778 | 9.099 | 9.1078 | 9.2534 | 9.209 | -113.815 | 0.002081 | 0.12358 | 0.15425 | 0.1606 | -122.2863
4608.9062 | 122.2595 | -0.11444 | 122.2183 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0076 | -0.01755 | -0.0046531 | -0.0027669 | 0.017476 | 0.033904 | 0.012441 | 9.1395 | 9.1403 | 8.9604 | 9.012 | 9.0392 | 9.1893 | 8.3438 | 0.019362 | 0.096512 | -0.06093 | -0.071161 | 0.041178 | 0.085587 | -0.11836 | 8.4583 | -113.2063 | 9.254 | 9.0749 | 0.61659 | -113.1792 | -113.029 | -0.00392 | -122.2895 | 0.1338 | 0.053511 | 0.057431 | -122.1771 | -122.1327 | 9.1265 | 9.1536 | 9.3037 | 9.2547 | -113.8745 | 0.04328 | 0.15562 | 0.20003 | 0.21095 | -122.3367
4610.625 | 122.2549 | -0.10986 | 122.2092 | 1.4211e-13 | -0.032342 | -0.00027769 | -0.0034509 | -0.010168 | 0.0076 | -0.01755 | -0.0048667 | -0.0023397 | 0.01769 | 0.03369 | 0.012227 | 9.1212 | 9.122 | 8.9467 | 8.9983 | 9.0208 | 9.171 | 8.3301 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.041178 | 0.071851 | -0.1321 | 8.44 | -113.2109 | 9.2311 | 9.0566 | 0.6166 | -113.1883 | -113.0382 | -0.022234 | -122.2803 | 0.1338 | 0.048933 | 0.071167 | -122.168 | -122.1373 | 9.1082 | 9.1307 | 9.2808 | 9.2318 | -113.8791 | 0.038702 | 0.15104 | 0.18171 | 0.19264 | -122.3413
4612.4062 | 122.2595 | -0.10071 | 122.2046 | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0078136 | -0.01755 | -0.0044395 | -0.0029805 | 0.017904 | 0.033904 | 0.012014 | 9.1166 | 9.1037 | 8.9421 | 8.9937 | 9.0208 | 9.1618 | 8.3255 | 0.019362 | 0.087354 | -0.06093 | -0.075739 | 0.0366 | 0.081008 | -0.12752 | 8.4262 | -113.2109 | 9.2173 | 9.0428 | 0.6166 | -113.1838 | -113.0428 | -0.02681 | -122.2803 | 0.12007 | 0.039778 | 0.066588 | -122.168 | -122.1236 | 9.0944 | 9.1215 | 9.2625 | 9.2044 | -113.8791 | 0.024969 | 0.13731 | 0.18172 | 0.18806 | -122.3321
4614.125 | 122.2549 | -0.10529 | 122.1954 | 1.4211e-13 | -0.032128 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0073864 | -0.0022892 | -0.0044395 | -0.0025533 | 0.017904 | 0.033904 | 0.012441 | 9.1029 | 9.0945 | 8.933 | 8.9754 | 8.9979 | 9.1435 | 8.3255 | 0.02852 | 0.082776 | -0.070087 | -0.066582 | 0.0366 | 0.07643 | -0.1321 | 8.4308 | -113.22 | 9.2082 | 9.0383 | 0.60744 | -113.1975 | -113.0519 | -0.026811 | -122.262 | 0.13381 | 0.035199 | 0.06201 | -122.1588 | -122.119 | 9.0807 | 9.1032 | 9.2488 | 9.1998 | -113.8699 | 0.038704 | 0.14189 | 0.18172 | 0.18806 | -122.3275
4615.9062 | 122.2366 | -0.11444 | 122.2321 | 1.4211e-13 | -0.032128 | 0.00036331 | -0.0034509 | -0.010595 | 0.0073864 | -0.01755 | -0.0048667 | -0.0025533 | 0.01769 | 0.03369 | 0.012014 | 9.0937 | 9.0899 | 8.9238 | 8.9708 | 8.9979 | 9.1481 | 8.321 | 0.02852 | 0.091933 | -0.056351 | -0.062004 | 0.045757 | 0.07643 | -0.12752 | 8.4354 | -113.2612 | 9.2082 | 9.0383 | 0.60286 | -113.2341 | -113.084 | -0.013077 | -122.2941 | 0.14296 | 0.05809 | 0.071167 | -122.1863 | -122.1556 | 9.0853 | 9.1124 | 9.2625 | 9.2044 | -113.9111 | 0.052437 | 0.1602 | 0.19087 | 0.20637 | -122.3596
4617.6875 | 122.2641 | -0.091553 | 122.2137 | 1.4211e-13 | -0.032555 | -0.00027769 | -0.0034509 | -0.010595 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0023397 | 0.017904 | 0.03369 | 0.012227 | 9.0891 | 9.0808 | 8.9147 | 8.9662 | 8.9796 | 9.1343 | 8.3118 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 8.4033 | -113.2475 | 9.1807 | 9.0062 | 0.60286 | -113.2341 | -113.0794 | -0.035965 | -122.2803 | 0.11549 | 0.030623 | 0.066588 | -122.1771 | -122.1419 | 9.0578 | 9.0712 | 9.2259 | 9.1723 | -113.9019 | 0.024971 | 0.12815 | 0.1634 | 0.17891 | -122.3413
4619.4531 | 122.3282 | -0.07782 | 122.2092 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0078136 | -0.0022892 | -0.0046531 | -0.0025533 | 0.018117 | 0.03369 | 0.012227 | 9.0846 | 9.0808 | 8.9055 | 8.9525 | 8.9751 | 9.1252 | 8.3026 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.13668 | 8.3805 | -113.2567 | 9.1624 | 8.9833 | 0.60286 | -113.2341 | -113.084 | -0.058856 | -122.2803 | 0.10176 | 0.012311 | 0.071167 | -122.168 | -122.1327 | 9.0303 | 9.0529 | 9.203 | 9.1586 | -113.9065 | 0.006659 | 0.119 | 0.15425 | 0.16517 | -122.3458
4621.2344 | 122.319 | -0.064087 | 122.1863 | 1.4211e-13 | -0.032128 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0076 | -0.0099192 | -0.0044395 | -0.0023397 | 0.017904 | 0.033904 | 0.012441 | 9.0663 | 9.067 | 8.8963 | 8.9479 | 8.9705 | 9.1252 | 8.3072 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12294 | 8.3713 | -113.2383 | 9.1303 | 8.9604 | 0.58913 | -113.2158 | -113.0611 | -0.058852 | -122.2529 | 0.088028 | 0.003157 | 0.062009 | -122.1497 | -122.1144 | 9.012 | 9.0346 | 9.1893 | 9.1311 | -113.8791 | -0.002495 | 0.10069 | 0.13594 | 0.15144 | -122.3092
4622.9531 | 122.3282 | -0.068665 | 122.168 | 1.4211e-13 | -0.0317 | -6.4092e-05 | -0.0036647 | -0.010168 | 0.0076 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017904 | 0.034117 | 0.012227 | 9.0708 | 9.0625 | 8.8963 | 8.9388 | 8.9613 | 9.1069 | 8.3072 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.12752 | 8.3759 | -113.2292 | 9.1395 | 8.965 | 0.58913 | -113.2067 | -113.0611 | -0.058853 | -122.2391 | 0.088027 | 0.007735 | 0.066588 | -122.1222 | -122.0915 | 9.0074 | 9.03 | 9.1755 | 9.1311 | -113.8608 | -0.002496 | 0.11442 | 0.1451 | 0.15602 | -122.2955
4624.7188 | 122.2321 | -0.10529 | 122.2229 | 1.4211e-13 | -0.032555 | -6.4092e-05 | -0.0032373 | -0.010382 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017904 | 0.034117 | 0.012227 | 9.0708 | 9.0716 | 8.8918 | 8.9388 | 8.9705 | 9.1114 | 8.3026 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.1321 | 8.4079 | -113.2841 | 9.1761 | 8.9971 | 0.58913 | -113.2524 | -113.1115 | -0.026811 | -122.2986 | 0.12923 | 0.044356 | 0.071167 | -122.1863 | -122.1465 | 9.0441 | 9.0758 | 9.2167 | 9.1769 | -113.9203 | 0.029547 | 0.14189 | 0.18172 | 0.19264 | -122.355
4626.4844 | 122.2229 | -0.10986 | 122.2183 | 1.4211e-13 | -0.032342 | 0.00036331 | -0.0036647 | -0.010595 | 0.0076 | -0.02518 | -0.0046531 | -0.0025533 | 0.017904 | 0.034117 | 0.012441 | 9.0571 | 9.0579 | 8.8826 | 8.9296 | 8.9567 | 9.1023 | 8.3026 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.0366 | 0.085587 | -0.12752 | 8.4125 | -113.2887 | 9.167 | 8.9925 | 0.57997 | -113.2616 | -113.116 | -0.017655 | -122.2895 | 0.1338 | 0.048933 | 0.066588 | -122.1817 | -122.1327 | 9.0395 | 9.0666 | 9.2122 | 9.1677 | -113.9157 | 0.038702 | 0.14646 | 0.19545 | 0.19722 | -122.3458
4628.1875 | 122.2733 | -0.11902 | 122.2412 | 1.4211e-13 | -0.032128 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0078136 | -0.02518 | -0.0048667 | -0.0025533 | 0.017904 | 0.033904 | 0.012014 | 9.0479 | 9.0487 | 8.8826 | 8.9296 | 8.9613 | 9.1069 | 8.2935 | 0.019362 | 0.091933 | -0.065509 | -0.075739 | 0.041178 | 0.07643 | -0.12752 | 8.4125 | -113.3116 | 9.167 | 9.0016 | 0.58913 | -113.2799 | -113.1343 | -0.008499 | -122.317 | 0.13838 | 0.05351 | 0.062009 | -122.2 | -122.1648 | 9.0486 | 9.0803 | 9.2259 | 9.1677 | -113.9477 | 0.04328 | 0.1602 | 0.19545 | 0.21095 | -122.3687
4629.9531 | 122.3877 | -0.050354 | 122.1817 | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0036647 | -0.010595 | 0.0078136 | -0.0022892 | -0.0048667 | -0.0025533 | 0.017904 | 0.03369 | 0.012227 | 9.0388 | 9.0487 | 8.8735 | 8.9205 | 8.9384 | 9.1023 | 8.2889 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.041178 | 0.071851 | -0.12752 | 8.3393 | -113.2612 | 9.0891 | 8.9238 | 0.58455 | -113.2433 | -113.0794 | -0.077164 | -122.2529 | 0.074295 | -0.005997 | 0.071167 | -122.1405 | -122.1099 | 8.9708 | 8.9888 | 9.1526 | 9.0991 | -113.8928 | -0.020807 | 0.091532 | 0.12221 | 0.13771 | -122.3092
4631.6719 | 122.2275 | -0.10986 | 122.2412 | 1.4211e-13 | -0.031914 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.0078136 | -0.01755 | -0.0048667 | -0.0025533 | 0.017904 | 0.033904 | 0.012227 | 9.0388 | 9.0396 | 8.8689 | 8.9205 | 8.9293 | 9.0931 | 8.2981 | 0.019362 | 0.091933 | -0.06093 | -0.071161 | 0.0366 | 0.071851 | -0.12752 | 8.4079 | -113.3207 | 9.1486 | 8.9787 | 0.57082 | -113.3119 | -113.1481 | -0.017655 | -122.3124 | 0.12923 | 0.048933 | 0.066588 | -122.2046 | -122.1694 | 9.0303 | 9.0391 | 9.203 | 9.1494 | -113.9432 | 0.038702 | 0.14646 | 0.18171 | 0.2018 | -122.3687
4633.4375 | 122.374 | -0.073242 | 122.2092 | 1.4211e-13 | -0.032342 | -0.00027769 | -0.0036647 | -0.010382 | 0.0076 | -0.01755 | -0.0046531 | -0.0027669 | 0.017904 | 0.03369 | 0.012441 | 9.0571 | 9.0533 | 8.8826 | 8.925 | 8.943 | 9.1023 | 8.2935 | 0.02852 | 0.082776 | -0.051772 | -0.075739 | 0.0366 | 0.071851 | -0.13668 | 8.3667 | -113.2841 | 9.1303 | 8.9559 | 0.58913 | -113.2662 | -113.1069 | -0.063434 | -122.2849 | 0.10176 | 0.02147 | 0.084904 | -122.1726 | -122.1373 | 8.9983 | 9.0162 | 9.1755 | 9.1265 | -113.9157 | -0.002497 | 0.10984 | 0.14509 | 0.15602 | -122.3458
4635.2188 | 122.3831 | -0.050354 | 122.2137 | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0032373 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0023397 | 0.017904 | 0.033904 | 0.012014 | 9.0571 | 9.0487 | 8.8735 | 8.9205 | 8.943 | 9.0977 | 8.2935 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.041178 | 0.081008 | -0.13668 | 8.3438 | -113.2933 | 9.1075 | 8.9238 | 0.57997 | -113.2707 | -113.116 | -0.086322 | -122.2849 | 0.074295 | -0.015155 | 0.071167 | -122.1726 | -122.1327 | 8.9708 | 8.9934 | 9.1481 | 9.0991 | -113.9203 | -0.020807 | 0.091532 | 0.13136 | 0.13771 | -122.3504
4636.9375 | 122.3465 | -0.073242 | 122.1863 | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0038783 | -0.0099547 | 0.0076 | -0.01755 | -0.0044395 | -0.0025533 | 0.017904 | 0.034117 | 0.012227 | 9.0434 | 9.0441 | 8.878 | 8.925 | 8.943 | 9.0931 | 8.2935 | 0.019362 | 0.091933 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.13668 | 8.3667 | -113.2612 | 9.1166 | 8.9513 | 0.58455 | -113.2433 | -113.0931 | -0.063434 | -122.2574 | 0.092604 | 0.012312 | 0.075746 | -122.1405 | -122.1053 | 8.9983 | 9.0162 | 9.1664 | 9.1174 | -113.8928 | 0.002081 | 0.119 | 0.15425 | 0.16518 | -122.323
4638.6875 | 122.2458 | -0.1236 | 122.2275 | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0034509 | -0.011023 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0023397 | 0.018117 | 0.03369 | 0.012014 | 9.0388 | 9.0441 | 8.8689 | 8.9113 | 8.943 | 9.084 | 8.2843 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.071851 | -0.12752 | 8.4079 | -113.3162 | 9.1624 | 8.9925 | 0.58455 | -113.2845 | -113.1435 | -0.003922 | -122.2941 | 0.14754 | 0.062666 | 0.066588 | -122.1909 | -122.1556 | 9.0349 | 9.0666 | 9.2076 | 9.1677 | -113.9432 | 0.057014 | 0.1602 | 0.19545 | 0.20637 | -122.355
4640.3906 | 122.3145 | -0.082397 | 122.2137 | 1.4211e-13 | -0.032342 | -0.00027769 | -0.0036647 | -0.010595 | 0.0071726 | -0.01755 | -0.0046531 | -0.0021259 | 0.018117 | 0.034117 | 0.012227 | 9.0205 | 9.0213 | 8.8506 | 8.9067 | 8.9247 | 9.0748 | 8.2797 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.1321 | 8.3621 | -113.307 | 9.1029 | 8.933 | 0.57082 | -113.2891 | -113.1389 | -0.0497 | -122.2803 | 0.10634 | 0.021467 | 0.071167 | -122.1726 | -122.1373 | 8.9891 | 9.0071 | 9.1572 | 9.1037 | -113.934 | 0.015815 | 0.12357 | 0.15883 | 0.16517 | -122.3458
4642.1719 | 122.2458 | -0.10529 | 122.2549 | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0076 | -0.0022892 | -0.0044395 | -0.0025533 | 0.017904 | 0.033904 | 0.012227 | 9.0205 | 9.0258 | 8.8506 | 8.893 | 8.9109 | 9.0657 | 8.2797 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.13668 | 8.385 | -113.3619 | 9.1258 | 8.9558 | 0.57082 | -113.344 | -113.1893 | -0.03139 | -122.3261 | 0.12923 | 0.044356 | 0.075746 | -122.2092 | -122.1785 | 8.9983 | 9.0162 | 9.1709 | 9.1311 | -113.9752 | 0.034125 | 0.15104 | 0.18172 | 0.19264 | -122.3916
4643.9375 | 122.3053 | -0.09613 | 122.2458 | 1.4211e-13 | -0.032555 | -6.4092e-05 | -0.0032373 | -0.010809 | 0.0073864 | -0.01755 | -0.0048667 | -0.0027669 | 0.017904 | 0.033904 | 0.012014 | 9.0205 | 9.0121 | 8.846 | 8.8884 | 8.9109 | 9.0611 | 8.2752 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.07643 | -0.13668 | 8.3713 | -113.3574 | 9.1166 | 8.9421 | 0.57082 | -113.3348 | -113.1847 | -0.040546 | -122.3124 | 0.12007 | 0.0352 | 0.075746 | -122.2092 | -122.1694 | 8.9845 | 9.0071 | 9.1572 | 9.1082 | -113.9706 | 0.029548 | 0.13273 | 0.17256 | 0.17891 | -122.3825
4645.7188 | 122.2504 | -0.10071 | 122.2458 | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0034509 | -0.010595 | 0.0078136 | -0.0022892 | -0.0050803 | -0.0023397 | 0.017904 | 0.03369 | 0.012227 | 9.0067 | 9.0075 | 8.8368 | 8.8838 | 8.9064 | 9.0519 | 8.2797 | 0.019362 | 0.096512 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 8.3805 | -113.362 | 9.1074 | 8.9375 | 0.55709 | -113.3394 | -113.1939 | -0.02681 | -122.3124 | 0.12007 | 0.035199 | 0.062009 | -122.2092 | -122.1694 | 8.9845 | 9.0071 | 9.1526 | 9.1082 | -113.966 | 0.034126 | 0.13731 | 0.17714 | 0.19722 | -122.3733
4647.4375 | 122.3923 | -0.054932 | 122.2229 | 1.4211e-13 | -0.032555 | -0.00027769 | -0.0034509 | -0.010595 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017904 | 0.033904 | 0.0118 | 8.9976 | 9.0029 | 8.8368 | 8.8793 | 8.9018 | 9.0565 | 8.2706 | 0.023941 | 0.078197 | -0.065509 | -0.071161 | 0.0366 | 0.07643 | -0.13668 | 8.3255 | -113.3436 | 9.0525 | 8.8918 | 0.56624 | -113.3211 | -113.1664 | -0.081744 | -122.2941 | 0.078873 | -0.010577 | 0.071167 | -122.1863 | -122.1465 | 8.9342 | 8.9567 | 9.1114 | 9.0579 | -113.9523 | -0.016229 | 0.091532 | 0.13136 | 0.13313 | -122.3596
4649.1875 | 122.287 | -0.10529 | 122.2458 | 1.4211e-13 | -0.032769 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017263 | 0.03369 | 0.012227 | 8.993 | 8.9984 | 8.8277 | 8.8701 | 8.8926 | 9.0382 | 8.266 | 0.014784 | 0.087354 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.1321 | 8.3713 | -113.3757 | 9.0983 | 8.933 | 0.56167 | -113.3532 | -113.2076 | -0.026811 | -122.3124 | 0.12007 | 0.039777 | 0.066588 | -122.2046 | -122.1694 | 8.9754 | 8.9979 | 9.1435 | 9.1036 | -113.9798 | 0.038704 | 0.14646 | 0.18172 | 0.19264 | -122.3779
4650.9531 | 122.3419 | -0.054932 | 122.2275 | 1.4211e-13 | -0.032555 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.01755 | -0.0044395 | -0.0027669 | 0.017476 | 0.033904 | 0.012014 | 8.9747 | 8.98 | 8.8139 | 8.8472 | 8.8835 | 9.029 | 8.2523 | 0.014784 | 0.091933 | -0.065509 | -0.071161 | 0.041178 | 0.081008 | -0.12752 | 8.3072 | -113.3803 | 9.0296 | 8.8689 | 0.56167 | -113.344 | -113.1984 | -0.072586 | -122.2986 | 0.069716 | -0.010577 | 0.062009 | -122.1863 | -122.1465 | 8.9021 | 8.9384 | 9.084 | 9.035 | -113.9752 | -0.016229 | 0.09611 | 0.13594 | 0.14686 | -122.355
4652.7344 | 122.3236 | -0.09613 | 122.2504 | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0036647 | -0.010382 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017904 | 0.033904 | 0.012227 | 8.9747 | 8.9755 | 8.8002 | 8.8518 | 8.8652 | 9.0199 | 8.2477 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.041178 | 0.085587 | -0.12752 | 8.3438 | -113.3986 | 9.0708 | 8.8963 | 0.55251 | -113.3852 | -113.2305 | -0.031388 | -122.3215 | 0.12465 | 0.039779 | 0.071167 | -122.2092 | -122.1648 | 8.9479 | 8.9613 | 9.116 | 9.0716 | -114.0027 | 0.024969 | 0.13731 | 0.18172 | 0.17891 | -122.3779
4654.5156 | 122.2687 | -0.11444 | 122.2687 | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017049 | 0.034117 | 0.012441 | 8.9701 | 8.9755 | 8.8002 | 8.8472 | 8.8743 | 9.0153 | 8.2477 | 0.023941 | 0.091933 | -0.06093 | -0.075739 | 0.041178 | 0.071851 | -0.13668 | 8.3621 | -113.4215 | 9.0846 | 8.9146 | 0.55251 | -113.3944 | -113.2534 | -0.022235 | -122.3444 | 0.13838 | 0.053511 | 0.075746 | -122.2275 | -122.1968 | 8.9617 | 8.9888 | 9.1297 | 9.0899 | -114.021 | 0.038702 | 0.15562 | 0.18629 | 0.20637 | -122.4054
4656.2969 | 122.287 | -0.10529 | 122.2458 | 1.4211e-13 | -0.032555 | 0.00036331 | -0.0034509 | -0.010382 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017476 | 0.033904 | 0.012014 | 8.9747 | 8.9709 | 8.8048 | 8.8564 | 8.8743 | 9.0107 | 8.2568 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.081008 | -0.12752 | 8.3621 | -113.3894 | 9.08 | 8.9101 | 0.54793 | -113.3715 | -113.2351 | -0.022232 | -122.3124 | 0.12923 | 0.044356 | 0.066588 | -122.2046 | -122.1648 | 8.9617 | 8.9796 | 9.116 | 9.0762 | -113.9889 | 0.038704 | 0.14646 | 0.18629 | 0.18806 | -122.3733
4658.0625 | 122.2733 | -0.1236 | 122.2595 | 1.4211e-13 | -0.032769 | 0.00014951 | -0.0038783 | -0.010382 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017904 | 0.034117 | 0.012014 | 8.9655 | 8.9663 | 8.791 | 8.8381 | 8.856 | 9.0107 | 8.2477 | 0.02852 | 0.082776 | -0.065509 | -0.071161 | 0.041178 | 0.071851 | -0.13668 | 8.3713 | -113.4215 | 9.0891 | 8.9146 | 0.54336 | -113.4035 | -113.2488 | -0.01308 | -122.3307 | 0.15212 | 0.058087 | 0.071167 | -122.2183 | -122.1877 | 8.9616 | 8.9796 | 9.1343 | 9.0899 | -114.0118 | 0.052435 | 0.16477 | 0.19545 | 0.20637 | -122.3962
4659.7656 | 122.4152 | -0.068665 | 122.2229 | 1.4211e-13 | -0.032769 | 0.00014951 | -0.0036647 | -0.010382 | 0.0078136 | -0.0022892 | -0.0044395 | -0.0025533 | 0.017263 | 0.034117 | 0.012441 | 8.9472 | 8.948 | 8.7773 | 8.8243 | 8.8468 | 9.0061 | 8.2431 | 0.033099 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.14125 | 8.3118 | -113.3986 | 9.0159 | 8.846 | 0.5342 | -113.3761 | -113.2168 | -0.07259 | -122.2895 | 0.10176 | 0.007735 | 0.080325 | -122.1771 | -122.1465 | 8.893 | 8.9155 | 9.0748 | 9.0167 | -113.9798 | 0.002083 | 0.11442 | 0.1451 | 0.15144 | -122.3642
4661.5469 | 122.3328 | -0.082397 | 122.2549 | 1.4211e-13 | -0.032769 | -6.4092e-05 | -0.0034509 | -0.011023 | 0.0076 | -0.01755 | -0.0048667 | -0.0025533 | 0.017476 | 0.034331 | 0.012441 | 8.9472 | 8.9434 | 8.7727 | 8.8197 | 8.8423 | 8.9924 | 8.2294 | 0.02852 | 0.091933 | -0.056351 | -0.075739 | 0.045757 | 0.081008 | -0.13668 | 8.3118 | -113.4352 | 9.0296 | 8.8551 | 0.54336 | -113.4127 | -113.2625 | -0.054279 | -122.3307 | 0.11092 | 0.026046 | 0.080325 | -122.2092 | -122.1739 | 8.9021 | 8.9247 | 9.0748 | 9.0258 | -114.0256 | 0.006658 | 0.12815 | 0.1634 | 0.17433 | -122.3916
|  |  |  | 1.4211e-13 | -0.032555 | -0.00049149 | -0.0038783 | -0.010382 | 0.0078136 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017476 | 0.033904 | 0.0118 | 8.9381 | 8.9343 | 8.7682 | 8.8152 | 8.8331 | 8.9741 | 8.2294 | 0.02852 | 0.087354 | -0.056351 | -0.071161 | 0.0366 | 0.085587 | -0.12294 | 8.298 | -113.4077 | 9.0067 | 8.8368 | 0.53878 | -113.3898 | -113.2488 | -0.054274 | -122.2941 | 0.097185 | 0.012314 | 0.066588 | -122.1863 | -122.1373 | 8.8838 | 8.9018 | 9.0428 | 9.0029 | -113.9935 | -0.002496 | 0.10526 | 0.15425 | 0.15602 | -122.3458
|  |  |  | 1.4211e-13 | -0.032342 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0076 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017263 | 0.033904 | 0.012014 | 8.9243 | 8.9297 | 8.7636 | 8.806 | 8.8239 | 8.9741 | 8.2248 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.045757 | 0.07643 | -0.12752 | 8.2889 | -113.3986 | 8.9884 | 8.8277 | 0.53878 | -113.3806 | -113.2305 | -0.063431 | -122.2803 | 0.088028 | 0.003157 | 0.066588 | -122.1588 | -122.1282 | 8.8701 | 8.888 | 9.0382 | 8.9938 | -113.9798 | -0.011652 | 0.10984 | 0.14052 | 0.15144 | -122.3321
|  |  |  | 1.4211e-13 | -0.032555 | 0.00014951 | -0.0036647 | -0.010382 | 0.0076 | -0.0022892 | -0.0046531 | -0.0027669 | 0.017263 | 0.034117 | 0.012227 | 8.9197 | 8.9159 | 8.7453 | 8.7923 | 8.8148 | 8.9695 | 8.2111 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.045757 | 0.081008 | -0.12752 | 8.3255 | -113.481 | 9.0342 | 8.8597 | 0.5342 | -113.4585 | -113.3037 | -0.013077 | -122.349 | 0.14296 | 0.05809 | 0.071167 | -122.2275 | -122.1922 | 8.9067 | 8.9292 | 9.084 | 9.0304 | -114.0622 | 0.038702 | 0.1602 | 0.19545 | 0.2018 | -122.4008
|  |  |  | 1.4211e-13 | -0.032342 | 0.00014951 | -0.0034509 | -0.010595 | 0.0076 | -0.01755 | -0.0048667 | -0.0025533 | 0.017263 | 0.033476 | 0.012227 | 8.8969 | 8.8976 | 8.7407 | 8.7785 | 8.7965 | 8.9558 | 8.2156 | 0.023941 | 0.091933 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.1321 | 8.266 | -113.4261 | 8.9472 | 8.791 | 0.52505 | -113.4081 | -113.2488 | -0.081743 | -122.2712 | 0.074295 | -0.015155 | 0.066588 | -122.1588 | -122.119 | 8.8289 | 8.8468 | 9.0061 | 8.948 | -113.989 | -0.016228 | 0.096111 | 0.13594 | 0.14229 | -122.3367
|  |  |  | 1.4211e-13 | -0.032769 | -0.00049149 | -0.0034509 | -0.010382 | 0.0076 | -0.0099192 | -0.0048667 | -0.0025533 | 0.01769 | 0.034117 | 0.012014 | 8.8969 | 8.8976 | 8.7224 | 8.7694 | 8.7965 | 8.942 | 8.2019 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.045757 | 0.07643 | -0.1321 | 8.2706 | -113.4581 | 8.9655 | 8.791 | 0.52047 | -113.431 | -113.2854 | -0.063432 | -122.2986 | 0.092606 | 0.003156 | 0.066588 | -122.1817 | -122.151 | 8.838 | 8.8651 | 9.0107 | 8.9663 | -114.0256 | -0.002496 | 0.11442 | 0.1451 | 0.15144 | -122.3596
|  |  |  | 1.4211e-13 | -0.032555 | -6.4092e-05 | -0.0032373 | -0.010382 | 0.0076 | -0.02518 | -0.0048667 | -0.0025533 | 0.017263 | 0.033904 | 0.012441 | 8.8831 | 8.8931 | 8.7178 | 8.7648 | 8.7919 | 8.9375 | 8.1973 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.12294 | 8.2706 | -113.4947 | 8.9564 | 8.791 | 0.52047 | -113.4676 | -113.3221 | -0.049697 | -122.3261 | 0.10176 | 0.012312 | 0.062009 | -122.2183 | -122.1831 | 8.838 | 8.8651 | 9.0107 | 8.9663 | -114.0622 | 0.00666 | 0.11442 | 0.14967 | 0.1606 | -122.3825
|  |  |  | 1.4211e-13 | -0.032769 | 0.00014951 | -0.0034509 | -0.010809 | 0.0076 | -0.0022892 | -0.0044395 | -0.0027669 | 0.017476 | 0.034331 | 0.012441 | 8.8785 | 8.8793 | 8.7086 | 8.7511 | 8.7782 | 8.9375 | 8.2065 | 0.023941 | 0.091933 | -0.070087 | -0.075739 | 0.041178 | 0.07643 | -0.12752 | 8.2706 | -113.5085 | 8.9426 | 8.7727 | 0.50216 | -113.4814 | -113.3221 | -0.063431 | -122.3353 | 0.088028 | -0.006 | 0.057431 | -122.2183 | -122.1831 | 8.8152 | 8.8422 | 9.0015 | 8.9434 | -114.053 | -0.011652 | 0.10526 | 0.14052 | 0.15602 | -122.387
|  |  |  | 1.4211e-13 | -0.032769 | 0.00036331 | -0.0030235 | -0.010382 | 0.0076 | -0.01755 | -0.0046531 | -0.0025533 | 0.017476 | 0.034117 | 0.012441 | 8.8831 | 8.8747 | 8.7041 | 8.7465 | 8.7736 | 8.9191 | 8.1882 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.1321 | 8.2706 | -113.4718 | 8.9655 | 8.7865 | 0.51589 | -113.4447 | -113.2992 | -0.0497 | -122.2895 | 0.10176 | 0.021467 | 0.071167 | -122.1726 | -122.1419 | 8.8289 | 8.856 | 9.0015 | 8.9571 | -114.0302 | 0.011236 | 0.12815 | 0.15883 | 0.16517 | -122.3504
|  |  |  | 1.4211e-13 | -0.032769 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017476 | 0.033904 | 0.012227 | 8.8511 | 8.8564 | 8.6857 | 8.7373 | 8.769 | 8.91 | 8.1882 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.045757 | 0.07643 | -0.1321 | 8.2431 | -113.5085 | 8.906 | 8.7407 | 0.49758 | -113.4768 | -113.3358 | -0.077165 | -122.3124 | 0.078873 | -0.001419 | 0.075746 | -122.2 | -122.1694 | 8.7923 | 8.8239 | 8.9649 | 8.9114 | -114.0576 | -0.01165 | 0.10069 | 0.13136 | 0.13771 | -122.3779
|  |  |  | 1.4211e-13 | -0.032555 | 0.00014951 | -0.0036647 | -0.010382 | 0.0073864 | -0.01755 | -0.0046531 | -0.0027669 | 0.017476 | 0.034117 | 0.012227 | 8.8694 | 8.861 | 8.6949 | 8.7465 | 8.7644 | 8.91 | 8.1836 | 0.019362 | 0.087354 | -0.070087 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 8.2523 | -113.4947 | 8.938 | 8.7636 | 0.51132 | -113.4768 | -113.3312 | -0.058853 | -122.3078 | 0.088027 | -0.001422 | 0.057431 | -122.2046 | -122.1648 | 8.8152 | 8.8331 | 8.9787 | 8.9297 | -114.0576 | 0.002083 | 0.10526 | 0.1451 | 0.15602 | -122.3687
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0036647 | -0.010595 | 0.0073864 | -0.01755 | -0.0048667 | -0.0027669 | 0.017476 | 0.03369 | 0.012227 | 8.8648 | 8.8564 | 8.6903 | 8.7373 | 8.7598 | 8.9054 | 8.179 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.13668 | 8.2339 | -113.4947 | 8.9197 | 8.7453 | 0.51132 | -113.4722 | -113.3266 | -0.081744 | -122.2986 | 0.078873 | -0.005998 | 0.075746 | -122.1909 | -122.1556 | 8.7923 | 8.8148 | 8.9603 | 8.9114 | -114.053 | -0.01165 | 0.09611 | 0.13136 | 0.13313 | -122.3687
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0076 | -0.01755 | -0.0044395 | -0.0025533 | 0.017049 | 0.034117 | 0.012014 | 8.8419 | 8.8518 | 8.6812 | 8.7328 | 8.7461 | 8.8917 | 8.1744 | 0.023941 | 0.091933 | -0.06093 | -0.075739 | 0.041178 | 0.071851 | -0.12752 | 8.3026 | -113.5359 | 8.9701 | 8.8093 | 0.50674 | -113.5226 | -113.377 | 0.000656 | -122.3444 | 0.15212 | 0.067244 | 0.066588 | -122.2275 | -122.1968 | 8.8609 | 8.8743 | 9.0198 | 8.98 | -114.0942 | 0.052435 | 0.16935 | 0.20003 | 0.22011 | -122.3962
|  |  |  | 1.4211e-13 | -0.032769 | 0.00014951 | -0.0036647 | -0.010168 | 0.0073864 | -0.01755 | -0.0046531 | -0.0027669 | 0.01769 | 0.033904 | 0.012014 | 8.8282 | 8.829 | 8.6583 | 8.7053 | 8.7278 | 8.8779 | 8.1698 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.041178 | 0.07643 | -0.12752 | 8.2843 | -113.5542 | 8.9426 | 8.7727 | 0.48843 | -113.5317 | -113.3816 | -0.013077 | -122.3307 | 0.13838 | 0.05809 | 0.071167 | -122.2183 | -122.1831 | 8.8197 | 8.8422 | 8.9924 | 8.9434 | -114.0897 | 0.04328 | 0.15562 | 0.19087 | 0.2018 | -122.387
|  |  |  | 1.4211e-13 | -0.032555 | -6.4092e-05 | -0.0032373 | -0.010595 | 0.0076 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017476 | 0.03369 | 0.012014 | 8.819 | 8.8244 | 8.6445 | 8.6961 | 8.7232 | 8.8734 | 8.1607 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.041178 | 0.07643 | -0.11836 | 8.266 | -113.5588 | 8.9243 | 8.7498 | 0.48385 | -113.5317 | -113.3816 | -0.013075 | -122.3307 | 0.12465 | 0.048935 | 0.06201 | -122.2138 | -122.1785 | 8.8014 | 8.8285 | 8.9786 | 8.9297 | -114.0943 | 0.029547 | 0.14646 | 0.18172 | 0.19264 | -122.3733
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0073864 | -0.0022892 | -0.0046531 | -0.0029805 | 0.017263 | 0.034117 | 0.012227 | 8.8144 | 8.8152 | 8.6445 | 8.687 | 8.6912 | 8.8596 | 8.1515 | 0.019362 | 0.096512 | -0.056351 | -0.071161 | 0.045757 | 0.081008 | -0.13668 | 8.2202 | -113.5588 | 8.8831 | 8.7132 | 0.49301 | -113.5546 | -113.3862 | -0.068011 | -122.317 | 0.088027 | 0.012314 | 0.080325 | -122.2 | -122.1648 | 8.7556 | 8.7598 | 8.9283 | 8.8839 | -114.0943 | -0.002496 | 0.11442 | 0.14967 | 0.16518 | -122.3825
|  |  |  | 1.4211e-13 | -0.032769 | 0.00014951 | -0.0034509 | -0.010382 | 0.0076 | -0.02518 | -0.0048667 | -0.0029805 | 0.017263 | 0.034117 | 0.012014 | 8.8007 | 8.7969 | 8.64 | 8.6732 | 8.7095 | 8.8505 | 8.1515 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.1321 | 8.2568 | -113.6138 | 8.906 | 8.7452 | 0.48843 | -113.5775 | -113.4365 | -0.026811 | -122.3536 | 0.12923 | 0.039777 | 0.066588 | -122.2504 | -122.2106 | 8.7785 | 8.8148 | 8.9558 | 8.9022 | -114.1355 | 0.038704 | 0.14189 | 0.18172 | 0.19264 | -122.4191
|  |  |  | 1.4211e-13 | -0.032769 | 0.00014951 | -0.0036647 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0025533 | 0.017263 | 0.033904 | 0.012014 | 8.7916 | 8.7877 | 8.6171 | 8.6732 | 8.6957 | 8.8505 | 8.147 | 0.019362 | 0.082776 | -0.056351 | -0.066582 | 0.041178 | 0.085587 | -0.13668 | 8.211 | -113.5771 | 8.8556 | 8.6812 | 0.47012 | -113.5546 | -113.3999 | -0.072589 | -122.3169 | 0.083449 | 0.007736 | 0.080325 | -122.2092 | -122.1648 | 8.7373 | 8.7598 | 8.9146 | 8.8518 | -114.1034 | -0.002495 | 0.10526 | 0.14967 | 0.14686 | -122.387
|  |  |  | 1.4211e-13 | -0.033196 | -0.00027769 | -0.0036647 | -0.010382 | 0.0078136 | -0.0099192 | -0.0050803 | -0.0025533 | 0.017263 | 0.034117 | 0.0118 | 8.7916 | 8.7969 | 8.6171 | 8.6641 | 8.6866 | 8.8367 | 8.1424 | 0.019362 | 0.082776 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.1321 | 8.2431 | -113.6138 | 8.8923 | 8.7178 | 0.4747 | -113.5913 | -113.4411 | -0.031389 | -122.349 | 0.12007 | 0.035199 | 0.066588 | -122.2367 | -122.2014 | 8.7648 | 8.7873 | 8.9374 | 8.8976 | -114.1355 | 0.029547 | 0.14189 | 0.17714 | 0.18348 | -122.4099
|  |  |  | 1.4211e-13 | -0.032769 | -6.4092e-05 | -0.0038783 | -0.010168 | 0.0076 | -0.02518 | -0.0048667 | -0.0029805 | 0.017263 | 0.034331 | 0.012014 | 8.7824 | 8.7877 | 8.6125 | 8.6595 | 8.682 | 8.823 | 8.1424 | 0.02852 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 8.1973 | -113.5817 | 8.8373 | 8.6674 | 0.47012 | -113.5592 | -113.4182 | -0.072586 | -122.3078 | 0.083452 | -0.010577 | 0.062009 | -122.2046 | -122.1648 | 8.7144 | 8.7369 | 8.8779 | 8.8427 | -114.0988 | -0.01165 | 0.091532 | 0.13136 | 0.14229 | -122.3687
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0073864 | -0.01755 | -0.0044395 | -0.0027669 | 0.017049 | 0.034331 | 0.012227 | 8.7732 | 8.7786 | 8.6033 | 8.6549 | 8.6728 | 8.8276 | 8.1424 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.045757 | 0.07643 | -0.12752 | 8.2431 | -113.5817 | 8.8739 | 8.704 | 0.46096 | -113.5638 | -113.4091 | -0.02681 | -122.3032 | 0.12007 | 0.035199 | 0.062009 | -122.1909 | -122.1602 | 8.7556 | 8.7735 | 8.9283 | 8.8793 | -114.0943 | 0.034126 | 0.14647 | 0.17714 | 0.18348 | -122.3642
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0078136 | -0.01755 | -0.0046531 | -0.0027669 | 0.017049 | 0.034331 | 0.012014 | 8.7687 | 8.774 | 8.5942 | 8.6503 | 8.6637 | 8.8184 | 8.1286 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.045757 | 0.071851 | -0.1321 | 8.1973 | -113.6 | 8.8373 | 8.6628 | 0.46554 | -113.5867 | -113.4319 | -0.063432 | -122.3261 | 0.092606 | 0.003156 | 0.066588 | -122.2046 | -122.1785 | 8.719 | 8.7323 | 8.8871 | 8.8427 | -114.1217 | -0.007074 | 0.11442 | 0.14052 | 0.15144 | -122.3825
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0048667 | -0.0023397 | 0.017904 | 0.034117 | 0.012441 | 8.7641 | 8.7557 | 8.5896 | 8.6412 | 8.6591 | 8.8093 | 8.1195 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.085587 | -0.1321 | 8.2248 | -113.6366 | 8.8694 | 8.6949 | 0.47012 | -113.6187 | -113.4686 | -0.026811 | -122.349 | 0.12923 | 0.044356 | 0.071167 | -122.2321 | -122.1922 | 8.7465 | 8.7644 | 8.9145 | 8.861 | -114.1584 | 0.034125 | 0.15104 | 0.19087 | 0.19264 | -122.4099
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0036647 | -0.010809 | 0.006959 | -0.01755 | -0.0046531 | -0.0025533 | 0.01769 | 0.034331 | 0.012227 | 8.7503 | 8.7511 | 8.5759 | 8.6229 | 8.6499 | 8.8001 | 8.1103 | 0.019362 | 0.087354 | -0.065509 | -0.080318 | 0.041178 | 0.07643 | -0.1321 | 8.2293 | -113.6641 | 8.8694 | 8.6949 | 0.46554 | -113.637 | -113.4869 | -0.013078 | -122.3673 | 0.13838 | 0.05351 | 0.066588 | -122.2458 | -122.2106 | 8.7419 | 8.769 | 8.9191 | 8.8701 | -114.1767 | 0.038701 | 0.1602 | 0.19545 | 0.20637 | -122.4191
|  |  |  | 1.4211e-13 | -0.033196 | 0.00014951 | -0.0036647 | -0.010168 | 0.0076 | -0.0099192 | -0.0046531 | -0.0025533 | 0.01769 | 0.034117 | 0.012227 | 8.7366 | 8.7374 | 8.5667 | 8.6137 | 8.6362 | 8.7909 | 8.1057 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.041178 | 0.081008 | -0.1321 | 8.1744 | -113.6321 | 8.8053 | 8.6354 | 0.46097 | -113.6096 | -113.4548 | -0.063432 | -122.3124 | 0.088027 | 0.003156 | 0.066588 | -122.2046 | -122.1648 | 8.6824 | 8.7049 | 8.8596 | 8.806 | -114.14 | 0.002083 | 0.10984 | 0.14967 | 0.15602 | -122.3779
|  |  |  | 1.4211e-13 | -0.032769 | -0.00027769 | -0.0034509 | -0.010382 | 0.0076 | -0.01755 | -0.0044395 | -0.0025533 | 0.017904 | 0.034545 | 0.012227 | 8.7275 | 8.7328 | 8.5667 | 8.6046 | 8.6316 | 8.7772 | 8.1057 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.14125 | 8.1698 | -113.6779 | 8.7915 | 8.6308 | 0.46097 | -113.6508 | -113.5052 | -0.077168 | -122.349 | 0.088028 | 0.003157 | 0.080325 | -122.2412 | -122.206 | 8.6686 | 8.6957 | 8.8413 | 8.7969 | -114.1767 | -0.002495 | 0.10526 | 0.14052 | 0.15144 | -122.4237
|  |  |  | 1.4211e-13 | -0.032983 | -0.00027769 | -0.0036647 | -0.010595 | 0.0073864 | 0.0053413 | -0.0044395 | -0.0027669 | 0.01769 | 0.034331 | 0.012014 | 8.7137 | 8.7145 | 8.5438 | 8.5954 | 8.6179 | 8.7726 | 8.0874 | 0.019362 | 0.087354 | -0.06093 | -0.075739 | 0.045757 | 0.081008 | -0.13668 | 8.1332 | -113.6595 | 8.7595 | 8.5896 | 0.45639 | -113.637 | -113.4823 | -0.0909 | -122.3307 | 0.065138 | -0.015154 | 0.075746 | -122.2092 | -122.1739 | 8.6412 | 8.6637 | 8.8184 | 8.7603 | -114.1675 | -0.029963 | 0.091533 | 0.12678 | 0.13313 | -122.3916
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0030235 | -0.010595 | 0.0073864 | -0.01755 | -0.0048667 | -0.0023397 | 0.017904 | 0.034331 | 0.0118 | 8.7091 | 8.7145 | 8.5438 | 8.5862 | 8.6087 | 8.7681 | 8.092 | 0.023941 | 0.091933 | -0.06093 | -0.071161 | 0.032021 | 0.07643 | -0.1321 | 8.211 | -113.7053 | 8.8282 | 8.6628 | 0.45181 | -113.6828 | -113.5235 | -0.013078 | -122.3627 | 0.14296 | 0.058089 | 0.071167 | -122.2595 | -122.2151 | 8.7053 | 8.7278 | 8.8871 | 8.8335 | -114.1996 | 0.047858 | 0.15104 | 0.19545 | 0.21095 | -122.4237
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0078136 | -0.0099192 | -0.0046531 | -0.0025533 | 0.01769 | 0.034331 | 0.012227 | 8.6862 | 8.7008 | 8.5118 | 8.5634 | 8.5858 | 8.7406 | 8.0691 | 0.014784 | 0.087354 | -0.065509 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 8.1698 | -113.7282 | 8.787 | 8.6125 | 0.44266 | -113.7057 | -113.551 | -0.035968 | -122.3581 | 0.11549 | 0.035199 | 0.071167 | -122.2458 | -122.2151 | 8.6641 | 8.6866 | 8.8413 | 8.8015 | -114.2225 | 0.034126 | 0.14647 | 0.17714 | 0.18806 | -122.4282
|  |  |  | 1.4211e-13 | -0.033196 | 0.00014951 | -0.0034509 | -0.010809 | 0.0076 | -0.02518 | -0.0048667 | -0.0025533 | 0.017263 | 0.034331 | 0.012227 | 8.6725 | 8.6824 | 8.5026 | 8.5634 | 8.5767 | 8.7314 | 8.0645 | 0.019362 | 0.091933 | -0.06093 | -0.062004 | 0.050335 | 0.081008 | -0.13668 | 8.1698 | -113.7511 | 8.7778 | 8.6079 | 0.43808 | -113.7378 | -113.583 | -0.03139 | -122.3765 | 0.12465 | 0.044356 | 0.075746 | -122.2641 | -122.2334 | 8.6686 | 8.682 | 8.8367 | 8.7877 | -114.2499 | 0.043282 | 0.15562 | 0.18629 | 0.19722 | -122.4511
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0034509 | -0.010809 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017049 | 0.034117 | 0.012227 | 8.6725 | 8.6733 | 8.498 | 8.5542 | 8.5721 | 8.7223 | 8.06 | 0.023941 | 0.096512 | -0.06093 | -0.071161 | 0.0366 | 0.085587 | -0.1321 | 8.1607 | -113.7511 | 8.7732 | 8.5987 | 0.43808 | -113.7332 | -113.583 | -0.031389 | -122.3765 | 0.12465 | 0.039778 | 0.071167 | -122.2687 | -122.2197 | 8.6549 | 8.6728 | 8.823 | 8.774 | -114.2453 | 0.029547 | 0.13731 | 0.18629 | 0.19722 | -122.4374
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0076 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.034117 | 0.012014 | 8.6634 | 8.6641 | 8.4935 | 8.545 | 8.5629 | 8.7131 | 8.0554 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.0366 | 0.07643 | -0.12752 | 8.1286 | -113.7511 | 8.7366 | 8.5667 | 0.43808 | -113.7332 | -113.583 | -0.054276 | -122.3627 | 0.097183 | 0.007733 | 0.062009 | -122.2595 | -122.2197 | 8.6183 | 8.6362 | 8.7864 | 8.7374 | -114.2408 | 0.00666 | 0.10984 | 0.14967 | 0.1606 | -122.4237
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.0076 | -0.01755 | -0.0050803 | -0.0025533 | 0.017049 | 0.033904 | 0.012014 | 8.6542 | 8.655 | 8.4889 | 8.5313 | 8.5629 | 8.704 | 8.06 | 0.019362 | 0.078197 | -0.06093 | -0.080318 | 0.045757 | 0.085587 | -0.13668 | 8.1744 | -113.7603 | 8.7686 | 8.6033 | 0.42892 | -113.7286 | -113.5876 | -0.022235 | -122.3719 | 0.1338 | 0.053511 | 0.075746 | -122.2458 | -122.206 | 8.6457 | 8.6774 | 8.8184 | 8.7694 | -114.2316 | 0.034123 | 0.1602 | 0.20003 | 0.19264 | -122.4282
|  |  |  | 1.4211e-13 | -0.033196 | 0.00014951 | -0.0034509 | -0.010809 | 0.0073864 | -0.01755 | -0.0050803 | -0.0025533 | 0.017476 | 0.034117 | 0.012014 | 8.6313 | 8.6412 | 8.4614 | 8.5084 | 8.5355 | 8.6811 | 8.0371 | 0.023941 | 0.091933 | -0.065509 | -0.075739 | 0.045757 | 0.07643 | -0.1321 | 8.1423 | -113.806 | 8.7366 | 8.5667 | 0.42435 | -113.779 | -113.6334 | -0.026811 | -122.3902 | 0.12923 | 0.039777 | 0.066588 | -122.2687 | -122.238 | 8.6137 | 8.6408 | 8.7863 | 8.7465 | -114.2774 | 0.029547 | 0.15104 | 0.18172 | 0.19722 | -122.4466
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0034509 | -0.010382 | 0.0076 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017476 | 0.034117 | 0.012227 | 8.613 | 8.6229 | 8.4523 | 8.4947 | 8.5217 | 8.6719 | 8.0325 | 0.023941 | 0.091933 | -0.056351 | -0.075739 | 0.045757 | 0.07643 | -0.12752 | 8.1011 | -113.8015 | 8.6817 | 8.5209 | 0.41977 | -113.7744 | -113.6242 | -0.058853 | -122.3719 | 0.092606 | 0.012314 | 0.071167 | -122.2504 | -122.2197 | 8.5633 | 8.5904 | 8.7406 | 8.6916 | -114.2637 | -0.007074 | 0.11442 | 0.1451 | 0.1606 | -122.4237
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0032373 | -0.010382 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017049 | 0.034117 | 0.012227 | 8.6038 | 8.6046 | 8.4339 | 8.4855 | 8.508 | 8.6582 | 8.0187 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 8.0828 | -113.7969 | 8.6679 | 8.498 | 0.4152 | -113.7744 | -113.6242 | -0.072589 | -122.349 | 0.088028 | 0.007736 | 0.080325 | -122.2367 | -122.2014 | 8.5496 | 8.5721 | 8.7223 | 8.6687 | -114.2637 | -0.002495 | 0.10984 | 0.1451 | 0.15144 | -122.4191
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0076 | 0.0053413 | -0.0048667 | -0.0025533 | 0.017049 | 0.034545 | 0.012014 | 8.5947 | 8.5954 | 8.4294 | 8.4764 | 8.5034 | 8.6444 | 8.0096 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.041178 | 0.081008 | -0.13668 | 8.124 | -113.8335 | 8.7091 | 8.5438 | 0.41977 | -113.8065 | -113.6654 | -0.022235 | -122.3856 | 0.14296 | 0.05809 | 0.080325 | -122.2687 | -122.2289 | 8.5908 | 8.6179 | 8.7589 | 8.7099 | -114.3003 | 0.038702 | 0.15562 | 0.19545 | 0.2018 | -122.4466
|  |  |  | 1.4211e-13 | -0.033196 | -0.00027769 | -0.0036647 | -0.010382 | 0.0076 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017263 | 0.034331 | 0.012227 | 8.5809 | 8.5954 | 8.4156 | 8.4672 | 8.4851 | 8.6399 | 8.005 | 0.019362 | 0.078197 | -0.065509 | -0.075739 | 0.045757 | 0.071851 | -0.13668 | 8.0737 | -113.806 | 8.6496 | 8.4843 | 0.41062 | -113.7881 | -113.6334 | -0.068011 | -122.349 | 0.088027 | 0.003156 | 0.071167 | -122.2275 | -122.2014 | 8.5359 | 8.5538 | 8.7085 | 8.6641 | -114.2682 | -0.007074 | 0.11442 | 0.14052 | 0.14686 | -122.4099
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017476 | 0.034117 | 0.0118 | 8.5718 | 8.5725 | 8.4065 | 8.4535 | 8.4805 | 8.6261 | 8.0004 | 0.023941 | 0.082776 | -0.06093 | -0.075739 | 0.045757 | 0.081008 | -0.13668 | 8.1103 | -113.8335 | 8.6817 | 8.5163 | 0.40604 | -113.8065 | -113.6609 | -0.026813 | -122.3627 | 0.1338 | 0.048933 | 0.075746 | -122.2412 | -122.206 | 8.5633 | 8.5904 | 8.736 | 8.6824 | -114.2866 | 0.034124 | 0.15562 | 0.19087 | 0.19264 | -122.4237
|  |  |  | 1.4211e-13 | -0.033196 | 0.00014951 | -0.0034509 | -0.010809 | 0.0071726 | -0.01755 | -0.0046531 | -0.0025533 | 0.017263 | 0.034545 | 0.0118 | 8.5626 | 8.568 | 8.4019 | 8.4535 | 8.4759 | 8.6124 | 8.0004 | 0.019362 | 0.087354 | -0.056351 | -0.066582 | 0.041178 | 0.07643 | -0.1321 | 8.0645 | -113.8244 | 8.6267 | 8.466 | 0.40146 | -113.8019 | -113.6655 | -0.06801 | -122.3444 | 0.083449 | 0.007736 | 0.075746 | -122.2367 | -122.2014 | 8.5176 | 8.54 | 8.6765 | 8.6321 | -114.2774 | -0.002495 | 0.10526 | 0.14052 | 0.15144 | -122.4099
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.033904 | 0.012014 | 8.5443 | 8.5497 | 8.379 | 8.4397 | 8.4531 | 8.6078 | 7.9821 | 0.033099 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.085587 | -0.13668 | 8.0691 | -113.8473 | 8.6313 | 8.466 | 0.39689 | -113.8339 | -113.6792 | -0.049701 | -122.3581 | 0.12007 | 0.026045 | 0.075746 | -122.2458 | -122.2014 | 8.5267 | 8.54 | 8.6948 | 8.6366 | -114.3049 | 0.015814 | 0.12815 | 0.17256 | 0.17433 | -122.4237
|  |  |  | 1.4211e-13 | -0.033196 | 0.00057691 | -0.0036647 | -0.010595 | 0.006959 | -0.0022892 | -0.0050803 | -0.0027669 | 0.016835 | 0.034331 | 0.0118 | 8.5489 | 8.5451 | 8.3744 | 8.4306 | 8.4439 | 8.5986 | 7.9775 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.050335 | 0.07643 | -0.1321 | 8.0554 | -113.8885 | 8.6267 | 8.4522 | 0.39689 | -113.8751 | -113.7204 | -0.054277 | -122.3902 | 0.10176 | 0.01689 | 0.071167 | -122.2687 | -122.2426 | 8.5084 | 8.5217 | 8.6765 | 8.6229 | -114.3415 | 0.006659 | 0.12815 | 0.15425 | 0.15602 | -122.4511
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0034509 | -0.010595 | 0.0073864 | -0.01755 | -0.0046531 | -0.0027669 | 0.017263 | 0.034331 | 0.0118 | 8.5352 | 8.5451 | 8.3698 | 8.4214 | 8.4393 | 8.5941 | 7.9821 | 0.019362 | 0.091933 | -0.056351 | -0.071161 | 0.045757 | 0.07643 | -0.12752 | 8.0828 | -113.9068 | 8.6359 | 8.4706 | 0.38773 | -113.8889 | -113.7341 | -0.02681 | -122.3993 | 0.12007 | 0.044357 | 0.071167 | -122.2824 | -122.2518 | 8.5221 | 8.54 | 8.6948 | 8.6458 | -114.3461 | 0.029547 | 0.14647 | 0.17714 | 0.19264 | -122.4557
|  |  |  | 1.4211e-13 | -0.03341 | -0.00049149 | -0.0036647 | -0.010382 | 0.0076 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017476 | 0.034117 | 0.012014 | 8.5168 | 8.5313 | 8.3607 | 8.4031 | 8.4302 | 8.5758 | 7.9592 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.1321 | 8.0142 | -113.8793 | 8.5718 | 8.4156 | 0.40147 | -113.8523 | -113.7067 | -0.077165 | -122.3536 | 0.078873 | -0.005998 | 0.071167 | -122.2367 | -122.206 | 8.458 | 8.4851 | 8.6307 | 8.5863 | -114.3232 | -0.016229 | 0.10069 | 0.13136 | 0.13771 | -122.4145
|  |  |  | 1.4211e-13 | -0.032983 | 0.00014951 | -0.0034509 | -0.010595 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0029805 | 0.01769 | 0.034545 | 0.012014 | 8.5123 | 8.5176 | 8.3424 | 8.3985 | 8.4118 | 8.562 | 7.9546 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.045757 | 0.081008 | -0.13668 | 8.0233 | -113.8793 | 8.5809 | 8.411 | 0.38773 | -113.866 | -113.7158 | -0.068011 | -122.3353 | 0.092606 | 0.012314 | 0.080325 | -122.2321 | -122.1968 | 8.4672 | 8.4805 | 8.6307 | 8.5863 | -114.3232 | 0.01124 | 0.11442 | 0.14967 | 0.15602 | -122.4145
|  |  |  | 1.4211e-13 | -0.033196 | -6.4092e-05 | -0.0032373 | -0.010809 | 0.0076 | -0.01755 | -0.0046531 | -0.0025533 | 0.017476 | 0.034331 | 0.012441 | 8.5077 | 8.5039 | 8.3332 | 8.3894 | 8.4118 | 8.5529 | 7.9455 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.07643 | -0.13668 | 8.005 | -113.893 | 8.5672 | 8.3927 | 0.38774 | -113.8706 | -113.7296 | -0.077167 | -122.3444 | 0.078871 | -0.001421 | 0.075746 | -122.2321 | -122.206 | 8.4489 | 8.4714 | 8.6124 | 8.5634 | -114.3369 | -0.002495 | 0.10984 | 0.13594 | 0.14228 | -122.4191
|  |  |  | 1.4211e-13 | -0.033196 | -6.4092e-05 | -0.0034509 | -0.010595 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017904 | 0.034331 | 0.0118 | 8.4894 | 8.4901 | 8.3286 | 8.3711 | 8.3889 | 8.5483 | 7.9409 | 0.023941 | 0.087354 | -0.070087 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 8.0233 | -113.9251 | 8.5718 | 8.411 | 0.38774 | -113.9072 | -113.7479 | -0.054279 | -122.3627 | 0.10634 | 0.01231 | 0.066589 | -122.2504 | -122.2151 | 8.4535 | 8.4713 | 8.6307 | 8.5725 | -114.3552 | 0.015815 | 0.12815 | 0.1634 | 0.16975 | -122.4328
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0076 | -0.0099192 | -0.0044395 | -0.0021259 | 0.017904 | 0.034331 | 0.012014 | 8.4848 | 8.4856 | 8.3149 | 8.3619 | 8.3889 | 8.5391 | 7.9272 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.050335 | 0.07643 | -0.12752 | 7.9775 | -113.9297 | 8.5352 | 8.3653 | 0.38774 | -113.9026 | -113.7524 | -0.077164 | -122.3627 | 0.074295 | -0.005997 | 0.071167 | -122.2412 | -122.2151 | 8.4123 | 8.4393 | 8.5895 | 8.5359 | -114.3644 | -0.020807 | 0.10069 | 0.12678 | 0.13771 | -122.4191
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0036647 | -0.010382 | 0.0076 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017476 | 0.034117 | 0.012014 | 8.4665 | 8.4718 | 8.3057 | 8.3527 | 8.3706 | 8.5254 | 7.9226 | 0.019362 | 0.087354 | -0.06093 | -0.066582 | 0.054914 | 0.07643 | -0.1321 | 7.9913 | -113.9434 | 8.5352 | 8.3744 | 0.38316 | -113.9255 | -113.7708 | -0.063432 | -122.3627 | 0.088027 | 0.007735 | 0.071167 | -122.2412 | -122.2197 | 8.4214 | 8.4393 | 8.5941 | 8.5405 | -114.3736 | 0.002083 | 0.12358 | 0.1451 | 0.15602 | -122.4282
|  |  |  | 1.4211e-13 | -0.033196 | -0.00027769 | -0.0038783 | -0.010595 | 0.0080272 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017476 | 0.034545 | 0.0118 | 8.4573 | 8.4581 | 8.2966 | 8.339 | 8.3615 | 8.5117 | 7.918 | 0.023941 | 0.087354 | -0.06093 | -0.075739 | 0.045757 | 0.081008 | -0.1321 | 8.0279 | -114.0075 | 8.5672 | 8.4065 | 0.37858 | -113.985 | -113.8348 | -0.022234 | -122.4222 | 0.1338 | 0.048933 | 0.071167 | -122.3007 | -122.2655 | 8.4489 | 8.4713 | 8.6215 | 8.5679 | -114.4285 | 0.034124 | 0.15562 | 0.19087 | 0.19722 | -122.4786
|  |  |  | 1.4211e-13 | -0.033196 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0078136 | -0.02518 | -0.0046531 | -0.0025533 | 0.017263 | 0.034117 | 0.0118 | 8.4528 | 8.4535 | 8.2874 | 8.3299 | 8.3523 | 8.5025 | 7.9089 | 0.02852 | 0.091933 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.1321 | 7.9729 | -113.9617 | 8.5168 | 8.3515 | 0.37859 | -113.9392 | -113.7891 | -0.06801 | -122.3627 | 0.092607 | -0.001422 | 0.066588 | -122.2504 | -122.2151 | 8.3939 | 8.4164 | 8.5666 | 8.5176 | -114.3827 | -0.007074 | 0.10526 | 0.14052 | 0.15602 | -122.4237
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0034509 | -0.010382 | 0.0076 | -0.01755 | -0.0042257 | -0.0025533 | 0.017049 | 0.033904 | 0.0118 | 8.4436 | 8.4444 | 8.2737 | 8.3299 | 8.3386 | 8.4933 | 7.8997 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.1321 | 7.9775 | -113.9709 | 8.5214 | 8.3515 | 0.37401 | -113.9621 | -113.8074 | -0.054277 | -122.3719 | 0.10176 | 0.01689 | 0.071167 | -122.255 | -122.2197 | 8.4077 | 8.4164 | 8.5712 | 8.5222 | -114.401 | 0.006659 | 0.12358 | 0.15883 | 0.1606 | -122.4328
|  |  |  | 1.4211e-13 | -0.032983 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0076 | -0.0099192 | -0.0046531 | -0.0029805 | 0.016835 | 0.034117 | 0.0118 | 8.4299 | 8.426 | 8.26 | 8.3161 | 8.334 | 8.4842 | 7.8905 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.9775 | -113.98 | 8.5168 | 8.3469 | 0.36943 | -113.9621 | -113.812 | -0.045122 | -122.3627 | 0.10634 | 0.021466 | 0.066588 | -122.2504 | -122.2151 | 8.4031 | 8.421 | 8.5712 | 8.513 | -114.4056 | 0.020393 | 0.13273 | 0.16798 | 0.17433 | -122.4282
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0032373 | -0.010809 | 0.0071726 | -0.0022892 | -0.0048667 | -0.0023397 | 0.016835 | 0.034545 | 0.0118 | 8.4253 | 8.4215 | 8.26 | 8.3024 | 8.3248 | 8.4796 | 7.8814 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.13668 | 7.9592 | -113.9938 | 8.5031 | 8.3378 | 0.37859 | -113.9713 | -113.8165 | -0.058856 | -122.3627 | 0.097182 | 0.01689 | 0.075746 | -122.255 | -122.2197 | 8.3802 | 8.4027 | 8.5574 | 8.4993 | -114.4148 | 0.011238 | 0.119 | 0.15425 | 0.1606 | -122.4328
|  |  |  | 1.4211e-13 | -0.033196 | -0.00027769 | -0.0038783 | -0.010382 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0029805 | 0.017049 | 0.034331 | 0.0118 | 8.407 | 8.4169 | 8.2417 | 8.2932 | 8.3157 | 8.4613 | 7.8768 | 0.019362 | 0.082776 | -0.06093 | -0.057425 | 0.045757 | 0.07643 | -0.1321 | 7.9867 | -114.0395 | 8.5168 | 8.3515 | 0.36485 | -114.0171 | -113.8715 | -0.022234 | -122.3902 | 0.12923 | 0.048933 | 0.071167 | -122.287 | -122.2563 | 8.4031 | 8.4255 | 8.5712 | 8.5267 | -114.456 | 0.052438 | 0.15562 | 0.18629 | 0.19264 | -122.4649
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0034509 | -0.010809 | 0.0073864 | -0.0099192 | -0.0048667 | -0.0023397 | 0.017049 | 0.034331 | 0.0118 | 8.3887 | 8.4031 | 8.2325 | 8.2795 | 8.2928 | 8.4567 | 7.8585 | 0.023941 | 0.082776 | -0.065509 | -0.075739 | 0.045757 | 0.081008 | -0.1321 | 7.9271 | -114.0167 | 8.4573 | 8.3012 | 0.37401 | -114.0034 | -113.8394 | -0.063432 | -122.3719 | 0.092606 | 0.003156 | 0.066588 | -122.2504 | -122.2151 | 8.3482 | 8.3615 | 8.5254 | 8.4718 | -114.4377 | -0.007074 | 0.11442 | 0.14967 | 0.15144 | -122.4282
|  |  |  | 1.4211e-13 | -0.033624 | 0.00014951 | -0.0036647 | -0.010382 | 0.0073864 | -0.0022892 | -0.0044395 | -0.0029805 | 0.016835 | 0.034331 | 0.0118 | 8.4024 | 8.4031 | 8.2325 | 8.2795 | 8.3019 | 8.4521 | 7.8722 | 0.019362 | 0.091933 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.13668 | 7.9821 | -114.0579 | 8.5123 | 8.3424 | 0.36028 | -114.0354 | -113.8852 | -0.026813 | -122.4085 | 0.12923 | 0.048933 | 0.075746 | -122.2916 | -122.2563 | 8.3894 | 8.4118 | 8.562 | 8.513 | -114.4651 | 0.038702 | 0.15562 | 0.19087 | 0.2018 | -122.474
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0038783 | -0.010809 | 0.0078136 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017049 | 0.034545 | 0.0118 | 8.3795 | 8.3848 | 8.2142 | 8.2703 | 8.2791 | 8.4384 | 7.8585 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.12752 | 7.9271 | -114.0304 | 8.4482 | 8.2828 | 0.3557 | -114.0217 | -113.8623 | -0.058853 | -122.3673 | 0.097185 | 0.003156 | 0.062009 | -122.2504 | -122.2151 | 8.339 | 8.3477 | 8.5071 | 8.4535 | -114.4422 | 0.002083 | 0.119 | 0.15425 | 0.15144 | -122.4282
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0036647 | -0.010595 | 0.0073864 | -0.0022892 | -0.0046531 | -0.0027669 | 0.01769 | 0.034117 | 0.0118 | 8.3658 | 8.3665 | 8.1959 | 8.252 | 8.2607 | 8.4201 | 7.8402 | 0.023941 | 0.087354 | -0.051772 | -0.071161 | 0.045757 | 0.081008 | -0.13668 | 7.9134 | -114.0533 | 8.439 | 8.2691 | 0.3557 | -114.0446 | -113.8852 | -0.063434 | -122.3765 | 0.097183 | 0.02147 | 0.084904 | -122.2595 | -122.2243 | 8.3253 | 8.334 | 8.4933 | 8.4398 | -114.4651 | 0.002081 | 0.119 | 0.15425 | 0.1606 | -122.442
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0073864 | -0.0099192 | -0.0042257 | -0.0025533 | 0.016835 | 0.034545 | 0.012014 | 8.352 | 8.3619 | 8.1821 | 8.2337 | 8.2653 | 8.4155 | 7.8356 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.081008 | -0.13668 | 7.8859 | -114.0762 | 8.4024 | 8.2325 | 0.34655 | -114.0446 | -113.8944 | -0.086322 | -122.381 | 0.074295 | -0.010576 | 0.075746 | -122.2687 | -122.2289 | 8.2841 | 8.3157 | 8.4659 | 8.4123 | -114.4743 | -0.020807 | 0.091532 | 0.13136 | 0.13771 | -122.4466
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0036647 | -0.010595 | 0.0076 | -0.0022892 | -0.0044395 | -0.0023397 | 0.017263 | 0.034117 | 0.012014 | 8.3474 | 8.3436 | 8.1638 | 8.22 | 8.2378 | 8.3972 | 7.8264 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.041178 | 0.081008 | -0.13668 | 7.9363 | -114.1265 | 8.4573 | 8.2737 | 0.33739 | -114.1087 | -113.9493 | -0.026813 | -122.4177 | 0.1338 | 0.048933 | 0.075746 | -122.3053 | -122.2655 | 8.3298 | 8.3477 | 8.507 | 8.4535 | -114.5201 | 0.038702 | 0.15104 | 0.19087 | 0.19264 | -122.4832
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0036647 | -0.010595 | 0.0071726 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017049 | 0.034545 | 0.0118 | 8.3291 | 8.3299 | 8.1547 | 8.2017 | 8.2195 | 8.3835 | 7.8173 | 0.019362 | 0.087354 | -0.065509 | -0.071161 | 0.041178 | 0.07643 | -0.1321 | 7.9271 | -114.1265 | 8.439 | 8.2645 | 0.33739 | -114.1087 | -113.9447 | -0.022234 | -122.3993 | 0.12923 | 0.044354 | 0.066588 | -122.287 | -122.2518 | 8.3115 | 8.3294 | 8.4933 | 8.4397 | -114.5109 | 0.038702 | 0.15104 | 0.18629 | 0.19722 | -122.4603
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0034509 | -0.010595 | 0.0073864 | -0.01755 | -0.0046531 | -0.0029805 | 0.017476 | 0.034758 | 0.0118 | 8.3062 | 8.3207 | 8.1501 | 8.2017 | 8.2149 | 8.3743 | 7.8035 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 7.8768 | -114.0945 | 8.3795 | 8.2233 | 0.34655 | -114.0812 | -113.9219 | -0.063434 | -122.3627 | 0.097183 | 0.016891 | 0.080325 | -122.2458 | -122.2197 | 8.2749 | 8.2882 | 8.4475 | 8.394 | -114.4926 | 0.00666 | 0.12358 | 0.14967 | 0.1606 | -122.4328
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017263 | 0.034117 | 0.012227 | 8.3017 | 8.3024 | 8.1272 | 8.1833 | 8.2012 | 8.3514 | 7.7944 | 0.02852 | 0.087354 | -0.056351 | -0.075739 | 0.050335 | 0.081008 | -0.12752 | 7.8814 | -114.1494 | 8.3886 | 8.2142 | 0.33282 | -114.1316 | -113.9814 | -0.040543 | -122.4085 | 0.1155 | 0.030624 | 0.071167 | -122.2824 | -122.2518 | 8.2703 | 8.2882 | 8.4384 | 8.3894 | -114.5384 | 0.011236 | 0.13731 | 0.16798 | 0.17433 | -122.4603
|  |  |  | 1.4211e-13 | -0.033837 | -0.00027769 | -0.0034509 | -0.010809 | 0.0076 | -0.01755 | -0.0044395 | -0.0027669 | 0.017049 | 0.034545 | 0.012227 | 8.2879 | 8.2978 | 8.1226 | 8.1742 | 8.1966 | 8.3514 | 7.7898 | 0.02852 | 0.091933 | -0.06093 | -0.071161 | 0.050335 | 0.081008 | -0.12294 | 7.8493 | -114.1448 | 8.3474 | 8.1821 | 0.33282 | -114.1224 | -113.9676 | -0.06343 | -122.3902 | 0.088029 | -0.001421 | 0.062009 | -122.2687 | -122.238 | 8.2337 | 8.2561 | 8.4109 | 8.3573 | -114.5292 | -0.011652 | 0.10984 | 0.14052 | 0.15144 | -122.442
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0038783 | -0.010809 | 0.0076 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016835 | 0.034545 | 0.012014 | 8.2788 | 8.2841 | 8.118 | 8.165 | 8.1829 | 8.3285 | 7.7806 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.054914 | 0.07643 | -0.1321 | 7.8447 | -114.1494 | 8.3429 | 8.1821 | 0.3374 | -114.1316 | -113.9859 | -0.06801 | -122.3856 | 0.083449 | 0.003157 | 0.071167 | -122.2595 | -122.238 | 8.2291 | 8.247 | 8.3926 | 8.3482 | -114.5338 | -0.007074 | 0.119 | 0.14052 | 0.15144 | -122.4466
|  |  |  | 1.4211e-13 | -0.03341 | 0.00036331 | -0.0036647 | -0.010595 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016835 | 0.034758 | 0.012014 | 8.2742 | 8.2749 | 8.1043 | 8.1559 | 8.1783 | 8.3239 | 7.7715 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.050335 | 0.071851 | -0.1321 | 7.8768 | -114.1815 | 8.3795 | 8.2096 | 0.33282 | -114.159 | -114.0134 | -0.026811 | -122.4085 | 0.12923 | 0.048935 | 0.075746 | -122.287 | -122.2655 | 8.2612 | 8.2836 | 8.4292 | 8.3802 | -114.5659 | 0.034125 | 0.15562 | 0.17714 | 0.19264 | -122.4694
|  |  |  | 1.4211e-13 | -0.033837 | 0.00014951 | -0.0034509 | -0.010809 | 0.0073864 | -0.01755 | -0.0042257 | -0.0025533 | 0.017263 | 0.034545 | 0.0118 | 8.2696 | 8.2749 | 8.1089 | 8.1467 | 8.1783 | 8.3331 | 7.7761 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.0366 | 0.090166 | -0.1321 | 7.8539 | -114.1677 | 8.3474 | 8.1867 | 0.33282 | -114.1361 | -113.9814 | -0.054277 | -122.3856 | 0.10634 | 0.01689 | 0.071167 | -122.2779 | -122.2243 | 8.2245 | 8.2561 | 8.4109 | 8.3528 | -114.5384 | 0.006659 | 0.11442 | 0.16799 | 0.1606 | -122.4466
|  |  |  | 1.4211e-13 | -0.033196 | -6.4092e-05 | -0.0032373 | -0.011023 | 0.0073864 | -0.01755 | -0.0042257 | -0.0025533 | 0.017049 | 0.034545 | 0.0118 | 8.2605 | 8.2566 | 8.0951 | 8.1376 | 8.16 | 8.3102 | 7.7669 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.071851 | -0.1321 | 7.8813 | -114.2181 | 8.3749 | 8.2096 | 0.32824 | -114.1956 | -114.0455 | -0.017656 | -122.4222 | 0.13838 | 0.053511 | 0.071167 | -122.3145 | -122.2838 | 8.252 | 8.2744 | 8.4246 | 8.3711 | -114.5887 | 0.047859 | 0.15562 | 0.18629 | 0.2018 | -122.4877
|  |  |  | 1.4211e-13 | -0.033196 | 0.00014951 | -0.0036647 | -0.011236 | 0.0073864 | -0.02518 | -0.0044395 | -0.0023397 | 0.017049 | 0.034758 | 0.011586 | 8.2467 | 8.2475 | 8.0768 | 8.1192 | 8.1463 | 8.301 | 7.7532 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.1321 | 7.8676 | -114.2456 | 8.3612 | 8.1913 | 0.32367 | -114.2185 | -114.0638 | -0.017656 | -122.4268 | 0.1338 | 0.053511 | 0.071167 | -122.3191 | -122.2838 | 8.2337 | 8.2607 | 8.4155 | 8.3619 | -114.6116 | 0.052437 | 0.1602 | 0.19545 | 0.2018 | -122.4969
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0076 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017049 | 0.034545 | 0.011159 | 8.233 | 8.2337 | 8.0631 | 8.1192 | 8.1325 | 8.2827 | 7.744 | 0.023941 | 0.082776 | -0.06093 | -0.080318 | 0.050335 | 0.081008 | -0.13668 | 7.8401 | -114.2089 | 8.3291 | 8.1592 | 0.31909 | -114.1957 | -114.0455 | -0.040546 | -122.4085 | 0.12007 | 0.0352 | 0.075746 | -122.2779 | -122.2472 | 8.2154 | 8.2287 | 8.3789 | 8.3299 | -114.5842 | 0.015812 | 0.14646 | 0.17714 | 0.17891 | -122.4649
|  |  |  | 1.4211e-13 | -0.033624 | -0.00027769 | -0.0036647 | -0.010595 | 0.0073864 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016835 | 0.034331 | 0.011586 | 8.2238 | 8.2292 | 8.0539 | 8.1009 | 8.1325 | 8.2781 | 7.7349 | 0.023941 | 0.091933 | -0.056351 | -0.075739 | 0.045757 | 0.081008 | -0.13668 | 7.8081 | -114.241 | 8.2971 | 8.1272 | 0.31909 | -114.2094 | -114.0638 | -0.063434 | -122.4177 | 0.097183 | 0.016891 | 0.080325 | -122.2962 | -122.2609 | 8.1742 | 8.2058 | 8.3514 | 8.3024 | -114.6071 | -0.002497 | 0.119 | 0.15425 | 0.16518 | -122.4786
|  |  |  | 1.4211e-13 | -0.033624 | 0.00036331 | -0.0036647 | -0.010809 | 0.0080272 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017476 | 0.034545 | 0.0118 | 8.2055 | 8.2154 | 8.0356 | 8.0964 | 8.1142 | 8.269 | 7.7211 | 0.023941 | 0.091933 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.13668 | 7.8218 | -114.2273 | 8.3062 | 8.1363 | 0.31452 | -114.2094 | -114.0546 | -0.035968 | -122.3993 | 0.12465 | 0.039778 | 0.075746 | -122.287 | -122.2472 | 8.1971 | 8.2149 | 8.3697 | 8.3161 | -114.6025 | 0.024969 | 0.13731 | 0.17714 | 0.19264 | -122.4603
|  |  |  | 1.4211e-13 | -0.03341 | -0.00027769 | -0.0038783 | -0.010595 | 0.0076 | -0.0022892 | -0.0046531 | -0.0023397 | 0.017049 | 0.034331 | 0.0118 | 8.1964 | 8.2063 | 8.0356 | 8.0826 | 8.1051 | 8.2598 | 7.7165 | 0.02852 | 0.096512 | -0.065509 | -0.075739 | 0.041178 | 0.090166 | -0.13668 | 7.7852 | -114.2273 | 8.265 | 8.1043 | 0.31909 | -114.2048 | -114.05 | -0.068011 | -122.3856 | 0.097185 | 0.003156 | 0.071167 | -122.2687 | -122.2197 | 8.1513 | 8.1737 | 8.3285 | 8.2749 | -114.5933 | -0.007074 | 0.10984 | 0.15883 | 0.16518 | -122.4466
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0034509 | -0.011023 | 0.0071726 | -0.01755 | -0.0050803 | -0.0027669 | 0.017049 | 0.034545 | 0.0118 | 8.1964 | 8.1925 | 8.0356 | 8.078 | 8.1005 | 8.2507 | 7.712 | 0.019362 | 0.087354 | -0.056351 | -0.075739 | 0.045757 | 0.081008 | -0.13668 | 7.8127 | -114.2868 | 8.2971 | 8.1363 | 0.32367 | -114.2643 | -114.1141 | -0.035968 | -122.4405 | 0.12007 | 0.044357 | 0.080325 | -122.3191 | -122.2838 | 8.1787 | 8.2012 | 8.3514 | 8.2932 | -114.6529 | 0.024969 | 0.14647 | 0.18172 | 0.18806 | -122.5015
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0034509 | -0.010595 | 0.0076 | -0.0099192 | -0.0046531 | -0.0021259 | 0.01769 | 0.034545 | 0.0118 | 8.1735 | 8.1834 | 8.0082 | 8.0597 | 8.0867 | 8.2324 | 7.6982 | 0.02852 | 0.087354 | -0.051772 | -0.075739 | 0.050335 | 0.07643 | -0.13668 | 7.7943 | -114.3051 | 8.2696 | 8.1043 | 0.30994 | -114.2781 | -114.1325 | -0.040546 | -122.4405 | 0.12465 | 0.044358 | 0.084904 | -122.3145 | -122.2884 | 8.1559 | 8.1829 | 8.3285 | 8.2795 | -114.6666 | 0.020391 | 0.14646 | 0.17256 | 0.18348 | -122.5015
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0032373 | -0.010595 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.017476 | 0.034545 | 0.011373 | 8.1735 | 8.1788 | 8.0082 | 8.0643 | 8.073 | 8.2324 | 7.6891 | 0.02852 | 0.096512 | -0.065509 | -0.075739 | 0.0366 | 0.085587 | -0.13668 | 7.7623 | -114.2501 | 8.2467 | 8.0814 | 0.3191 | -114.2415 | -114.0821 | -0.063434 | -122.3902 | 0.10176 | 0.007733 | 0.071167 | -122.2779 | -122.2289 | 8.1375 | 8.1462 | 8.3056 | 8.252 | -114.6254 | -0.002497 | 0.10984 | 0.15883 | 0.16975 | -122.4511
|  |  |  | 1.4211e-13 | -0.033624 | 0.00036331 | -0.0032373 | -0.010809 | 0.0071726 | -0.01755 | -0.0046531 | -0.0027669 | 0.017476 | 0.034545 | 0.011586 | 8.1643 | 8.1742 | 8.0036 | 8.0551 | 8.0776 | 8.2278 | 7.6936 | 0.02852 | 0.091933 | -0.06093 | -0.075739 | 0.0366 | 0.07643 | -0.12752 | 7.7715 | -114.2822 | 8.2421 | 8.0814 | 0.30994 | -114.2598 | -114.1096 | -0.049698 | -122.4131 | 0.10634 | 0.01689 | 0.066588 | -122.3007 | -122.2609 | 8.133 | 8.1554 | 8.3056 | 8.252 | -114.6437 | 0.002081 | 0.11442 | 0.15425 | 0.16975 | -122.4649
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0036647 | -0.010595 | 0.0071726 | -0.01755 | -0.0046531 | -0.0025533 | 0.017049 | 0.034545 | 0.0118 | 8.1597 | 8.1559 | 7.9898 | 8.0414 | 8.0638 | 8.214 | 7.6799 | 0.019362 | 0.087354 | -0.056351 | -0.071161 | 0.041178 | 0.07643 | -0.13668 | 7.7531 | -114.2685 | 8.233 | 8.0631 | 0.30994 | -114.246 | -114.0958 | -0.063434 | -122.381 | 0.092604 | 0.016891 | 0.080325 | -122.2687 | -122.2334 | 8.1147 | 8.1371 | 8.2873 | 8.2291 | -114.63 | 0.002081 | 0.11442 | 0.14967 | 0.1606 | -122.4466
|  |  |  | 1.4211e-13 | -0.03341 | 0.00014951 | -0.0034509 | -0.010809 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.01769 | 0.034545 | 0.011586 | 8.1552 | 8.1513 | 7.9761 | 8.0323 | 8.0684 | 8.2095 | 7.6753 | 0.023941 | 0.091933 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.13668 | 7.7394 | -114.3005 | 8.2192 | 8.0402 | 0.30079 | -114.2643 | -114.1233 | -0.072589 | -122.3993 | 0.088028 | -0.001422 | 0.071167 | -122.2916 | -122.2563 | 8.0963 | 8.1325 | 8.2736 | 8.2154 | -114.6574 | -0.002495 | 0.10526 | 0.14052 | 0.15602 | -122.4694
|  |  |  | 1.4211e-13 | -0.033624 | 0.00014951 | -0.0036647 | -0.010595 | 0.0073864 | -0.0099192 | -0.0048667 | -0.0025533 | 0.01769 | 0.034758 | 0.011159 | 8.146 | 8.1422 | 7.9715 | 8.0277 | 8.0547 | 8.1911 | 7.6662 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.050335 | 0.085587 | -0.1321 | 7.7577 | -114.3417 | 8.2376 | 8.0631 | 0.30537 | -114.3147 | -114.1782 | -0.040544 | -122.4405 | 0.11549 | 0.030623 | 0.071167 | -122.319 | -122.2838 | 8.1192 | 8.1462 | 8.2827 | 8.2337 | -114.7032 | 0.020392 | 0.14189 | 0.17714 | 0.17891 | -122.5015
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0038783 | -0.010809 | 0.006959 | -0.01755 | -0.0048667 | -0.0027669 | 0.01769 | 0.034545 | 0.011586 | 8.1277 | 8.1376 | 7.9624 | 8.0139 | 8.0364 | 8.1911 | 7.6524 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.07643 | -0.13668 | 7.7119 | -114.3234 | 8.1872 | 8.0219 | 0.30995 | -114.301 | -114.1462 | -0.077167 | -122.4039 | 0.08345 | -0.001421 | 0.075746 | -122.2962 | -122.2609 | 8.0735 | 8.0959 | 8.2507 | 8.1971 | -114.6849 | -0.007073 | 0.10069 | 0.13594 | 0.14228 | -122.474
|  |  |  | 1.4211e-13 | -0.033624 | 0.00014951 | -0.0036647 | -0.010595 | 0.0076 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017476 | 0.034331 | 0.0118 | 8.1185 | 8.1238 | 7.9532 | 8.0094 | 8.0318 | 8.1774 | 7.657 | 0.019362 | 0.091933 | -0.056351 | -0.066582 | 0.041178 | 0.081008 | -0.1321 | 7.776 | -114.3463 | 8.2375 | 8.0722 | 0.29621 | -114.3239 | -114.1782 | -0.013078 | -122.4222 | 0.13838 | 0.062668 | 0.075746 | -122.3145 | -122.2746 | 8.1284 | 8.1508 | 8.2964 | 8.2429 | -114.6986 | 0.052437 | 0.1602 | 0.20003 | 0.21095 | -122.4877
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0073864 | -0.01755 | -0.0044395 | -0.0027669 | 0.017904 | 0.034331 | 0.0118 | 8.114 | 8.1238 | 7.9441 | 7.9956 | 8.0181 | 8.1728 | 7.6433 | 0.014784 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.085587 | -0.13668 | 7.7394 | -114.3646 | 8.2101 | 8.0402 | 0.30079 | -114.3422 | -114.1874 | -0.040546 | -122.4268 | 0.11091 | 0.0352 | 0.075746 | -122.3145 | -122.2746 | 8.0918 | 8.1142 | 8.269 | 8.22 | -114.717 | 0.029548 | 0.14189 | 0.18172 | 0.17891 | -122.4969
|  |  |  | 1.4211e-13 | -0.033624 | 0.00014951 | -0.0034509 | -0.010595 | 0.0078136 | -0.01755 | -0.0046531 | -0.0025533 | 0.017263 | 0.034117 | 0.011586 | 8.1048 | 8.101 | 7.9258 | 7.9865 | 8.0043 | 8.1545 | 7.6295 | 0.019362 | 0.091933 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.6936 | -114.36 | 8.1689 | 7.9898 | 0.29622 | -114.3422 | -114.192 | -0.06801 | -122.4131 | 0.083449 | -0.001422 | 0.066588 | -122.3007 | -122.2655 | 8.0506 | 8.0684 | 8.2186 | 8.165 | -114.717 | -0.002495 | 0.10984 | 0.1451 | 0.15602 | -122.4786
|  |  |  | 1.4211e-13 | -0.033196 | 0.00014951 | -0.0038783 | -0.010809 | 0.0073864 | -0.01755 | -0.0044395 | -0.0025533 | 0.017476 | 0.034545 | 0.011586 | 8.0865 | 8.0918 | 7.9258 | 7.9773 | 7.9906 | 8.1454 | 7.6204 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 7.6707 | -114.3738 | 8.1368 | 7.9761 | 0.30537 | -114.3605 | -114.2057 | -0.086322 | -122.4177 | 0.074295 | -0.005997 | 0.080325 | -122.3007 | -122.2701 | 8.0277 | 8.0409 | 8.1957 | 8.1422 | -114.7307 | -0.016228 | 0.10069 | 0.13136 | 0.13771 | -122.4877
|  |  |  | 1.4211e-13 | -0.033624 | 0.00014951 | -0.0034509 | -0.010382 | 0.0073864 | -0.0022892 | -0.0048667 | -0.0025533 | 0.017476 | 0.034545 | 0.0118 | 8.0773 | 8.0781 | 7.9029 | 7.9636 | 7.9814 | 8.1362 | 7.6066 | 0.019362 | 0.082776 | -0.056351 | -0.071161 | 0.050335 | 0.07643 | -0.1321 | 7.6616 | -114.36 | 8.1323 | 7.9578 | 0.29622 | -114.3422 | -114.1874 | -0.077165 | -122.3948 | 0.074294 | -0.001419 | 0.075746 | -122.2733 | -122.2472 | 8.0185 | 8.0364 | 8.1911 | 8.133 | -114.717 | -0.016229 | 0.10527 | 0.13136 | 0.13771 | -122.4557
|  |  |  | 1.4211e-13 | -0.03341 | 0.00036331 | -0.0036647 | -0.010809 | 0.0076 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017263 | 0.034545 | 0.0118 | 8.0636 | 8.0735 | 7.8983 | 7.9453 | 7.9723 | 8.1179 | 7.6066 | 0.023941 | 0.091933 | -0.06093 | -0.062004 | 0.050335 | 0.081008 | -0.1321 | 7.7165 | -114.4241 | 8.1735 | 8.0081 | 0.29164 | -114.3971 | -114.2515 | -0.022234 | -122.4314 | 0.1338 | 0.048933 | 0.071167 | -122.319 | -122.2884 | 8.0551 | 8.0821 | 8.2278 | 8.1833 | -114.7627 | 0.047859 | 0.1602 | 0.19087 | 0.2018 | -122.5015
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.0071726 | -0.0022892 | -0.0048667 | -0.0027669 | 0.017263 | 0.034545 | 0.0118 | 8.0499 | 8.0597 | 7.8891 | 7.9407 | 7.9585 | 8.1179 | 7.5975 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 7.6707 | -114.4104 | 8.1231 | 7.9624 | 0.29164 | -114.3925 | -114.2332 | -0.063434 | -122.4177 | 0.097183 | 0.012312 | 0.075746 | -122.3053 | -122.2746 | 8.0139 | 8.0318 | 8.1911 | 8.133 | -114.7536 | 0.00666 | 0.119 | 0.14967 | 0.1606 | -122.4877
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0073864 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017263 | 0.034758 | 0.0118 | 8.0499 | 8.0552 | 7.8891 | 7.9361 | 7.9494 | 8.1042 | 7.5975 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.085587 | -0.1321 | 7.7119 | -114.4424 | 8.1643 | 8.0036 | 0.29164 | -114.4292 | -114.2744 | -0.017656 | -122.4451 | 0.13838 | 0.053511 | 0.071167 | -122.3282 | -122.293 | 8.0506 | 8.0638 | 8.2186 | 8.1696 | -114.7811 | 0.047859 | 0.16478 | 0.20003 | 0.2018 | -122.5106
|  |  |  | 1.4211e-13 | -0.033624 | 0.00036331 | -0.0034509 | -0.010809 | 0.0071726 | -0.01755 | -0.0044395 | -0.0021259 | 0.017476 | 0.034545 | 0.0118 | 8.0453 | 8.0414 | 7.8754 | 7.9315 | 7.9585 | 8.1087 | 7.5929 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.085587 | -0.13668 | 7.6661 | -114.4195 | 8.1185 | 7.9486 | 0.28249 | -114.3925 | -114.2423 | -0.063434 | -122.4131 | 0.097183 | 0.012312 | 0.075746 | -122.3053 | -122.2655 | 8.0048 | 8.0318 | 8.182 | 8.1147 | -114.7582 | 0.011238 | 0.119 | 0.15883 | 0.1606 | -122.4877
|  |  |  | 1.4211e-13 | -0.033837 | 0.00036331 | -0.0038783 | -0.010809 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017904 | 0.034331 | 0.011373 | 8.0407 | 8.046 | 7.8708 | 7.927 | 7.9494 | 8.095 | 7.5883 | 0.019362 | 0.091933 | -0.056351 | -0.071161 | 0.050335 | 0.081008 | -0.12752 | 7.6433 | -114.4104 | 8.0956 | 7.9257 | 0.28248 | -114.388 | -114.2423 | -0.072586 | -122.4085 | 0.074294 | -0.001419 | 0.071167 | -122.287 | -122.2563 | 7.9819 | 8.0043 | 8.1499 | 8.1009 | -114.749 | -0.016229 | 0.10527 | 0.13594 | 0.14686 | -122.4649
|  |  |  | 1.4211e-13 | -0.033837 | 0.00014951 | -0.0038783 | -0.010595 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017049 | 0.034545 | 0.011586 | 8.027 | 8.0369 | 7.8525 | 7.9224 | 7.9356 | 8.095 | 7.5746 | 0.02852 | 0.096512 | -0.06093 | -0.071161 | 0.045757 | 0.071851 | -0.13668 | 7.6478 | -114.4607 | 8.1002 | 7.9257 | 0.27791 | -114.4475 | -114.2881 | -0.063434 | -122.4543 | 0.10176 | 0.012312 | 0.075746 | -122.3374 | -122.3113 | 7.9956 | 8.0089 | 8.1682 | 8.1101 | -114.8085 | 0.002081 | 0.119 | 0.14509 | 0.16975 | -122.5198
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0038783 | -0.010382 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.017476 | 0.034545 | 0.011373 | 8.027 | 8.0277 | 7.8617 | 7.9178 | 7.9265 | 8.0767 | 7.5792 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 7.6707 | -114.4562 | 8.1185 | 7.9532 | 0.28249 | -114.4475 | -114.2973 | -0.045123 | -122.4405 | 0.11549 | 0.030623 | 0.075746 | -122.3236 | -122.2975 | 8.0094 | 8.018 | 8.1682 | 8.1192 | -114.7948 | 0.024971 | 0.14189 | 0.16798 | 0.18349 | -122.5106
|  |  |  | 1.4211e-13 | -0.033624 | 0.00036331 | -0.0034509 | -0.010382 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017263 | 0.034331 | 0.011159 | 8.0132 | 8.0185 | 7.8433 | 7.9041 | 7.9219 | 8.0629 | 7.5654 | 0.023941 | 0.091933 | -0.06093 | -0.071161 | 0.050335 | 0.07643 | -0.14125 | 7.6616 | -114.4928 | 8.1094 | 7.9395 | 0.27791 | -114.475 | -114.3339 | -0.045125 | -122.468 | 0.12007 | 0.0352 | 0.080325 | -122.3465 | -122.3204 | 8.0002 | 8.018 | 8.1591 | 8.1147 | -114.8314 | 0.024969 | 0.14646 | 0.17256 | 0.18806 | -122.5381
|  |  |  | 1.4211e-13 | -0.034051 | 0.00057691 | -0.0034509 | -0.010809 | 0.0071726 | -0.0022892 | -0.0048667 | -0.0025533 | 0.017263 | 0.034545 | 0.011586 | 7.9949 | 8.014 | 7.8479 | 7.8995 | 7.9173 | 8.0675 | 7.5563 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.07643 | -0.13668 | 7.657 | -114.4745 | 8.0956 | 7.9486 | 0.29165 | -114.4566 | -114.3064 | -0.035968 | -122.436 | 0.12465 | 0.039778 | 0.075746 | -122.3282 | -122.2975 | 8.0002 | 8.018 | 8.1682 | 8.1147 | -114.8177 | 0.038704 | 0.14647 | 0.17714 | 0.18806 | -122.5106
|  |  |  | 1.4211e-13 | -0.033624 | -0.00049149 | -0.0036647 | -0.011023 | 0.0071726 | -0.01755 | -0.0048667 | -0.0027669 | 0.017476 | 0.034545 | 0.011586 | 7.9995 | 8.0048 | 7.8296 | 7.8949 | 7.9082 | 8.0538 | 7.5517 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.0366 | 0.085587 | -0.12752 | 7.6661 | -114.5065 | 8.1139 | 7.944 | 0.27791 | -114.4933 | -114.3476 | -0.013077 | -122.468 | 0.13838 | 0.053511 | 0.066588 | -122.3648 | -122.3158 | 8.0093 | 8.0226 | 8.1682 | 8.1192 | -114.8497 | 0.047859 | 0.15104 | 0.20003 | 0.19722 | -122.5289
|  |  |  | 1.4211e-13 | -0.033624 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0073864 | -0.0099192 | -0.0042257 | -0.0027669 | 0.017263 | 0.034545 | 0.012014 | 7.9858 | 7.9865 | 7.8159 | 7.8766 | 7.9036 | 8.0492 | 7.5425 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.13668 | 7.6158 | -114.4653 | 8.059 | 7.8891 | 0.27334 | -114.4383 | -114.2927 | -0.063434 | -122.4039 | 0.097183 | 0.012312 | 0.075746 | -122.2962 | -122.2609 | 7.9498 | 7.9768 | 8.1225 | 8.0597 | -114.7994 | 0.011238 | 0.119 | 0.15425 | 0.1606 | -122.4786
|  |  |  | 1.4211e-13 | -0.033624 | 0.00036331 | -0.0036647 | -0.010809 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0023397 | 0.017476 | 0.034545 | 0.011586 | 7.9812 | 7.9911 | 7.8159 | 7.8766 | 7.899 | 8.0446 | 7.5425 | 0.019362 | 0.091933 | -0.051772 | -0.066582 | 0.041178 | 0.07643 | -0.1321 | 7.6432 | -114.4928 | 8.0819 | 7.9166 | 0.27334 | -114.4704 | -114.3248 | -0.031389 | -122.436 | 0.12007 | 0.048936 | 0.080325 | -122.3282 | -122.293 | 7.9773 | 7.9997 | 8.1453 | 8.0918 | -114.8268 | 0.034126 | 0.14189 | 0.17714 | 0.19264 | -122.5015
|  |  |  | 1.4211e-13 | -0.033837 | 0.00014951 | -0.0034509 | -0.010595 | 0.0071726 | -0.01755 | -0.0044395 | -0.0021259 | 0.017476 | 0.034758 | 0.011159 | 8.0178 | 8.0277 | 7.8388 | 7.8995 | 7.9311 | 8.0767 | 7.5609 | 0.023941 | 0.087354 | -0.051772 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.6249 | -114.447 | 8.0819 | 7.9028 | 0.27791 | -114.4154 | -114.2698 | -0.06801 | -122.4131 | 0.088028 | 0.012315 | 0.080325 | -122.3007 | -122.2655 | 7.9636 | 7.9951 | 8.1408 | 8.0918 | -114.7856 | -0.002495 | 0.10984 | 0.1451 | 0.15144 | -122.4786
|  |  |  | 1.4211e-13 | -0.03341 | -6.4092e-05 | -0.0038783 | -0.010809 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017476 | 0.034545 | 0.011586 | 8.0041 | 8.0094 | 7.8342 | 7.8857 | 7.9082 | 8.0675 | 7.5563 | 0.019362 | 0.091933 | -0.056351 | -0.066582 | 0.041178 | 0.07643 | -0.14125 | 7.6707 | -114.5111 | 8.1185 | 7.9486 | 0.27791 | -114.4887 | -114.3293 | -0.026814 | -122.4634 | 0.1338 | 0.05809 | 0.084904 | -122.3557 | -122.3204 | 8.0002 | 8.0226 | 8.182 | 8.1238 | -114.8406 | 0.047859 | 0.15562 | 0.19087 | 0.20637 | -122.5381
|  |  |  | 1.4211e-13 | -0.034051 | 0.00014951 | -0.0032373 | -0.010595 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0023397 | 0.017049 | 0.034758 | 0.011586 | 7.9903 | 8.0002 | 7.8205 | 7.8766 | 7.9036 | 8.0538 | 7.538 | 0.023941 | 0.091933 | -0.056351 | -0.066582 | 0.041178 | 0.071851 | -0.1321 | 7.5929 | -114.4928 | 8.0453 | 7.8754 | 0.28249 | -114.4658 | -114.3156 | -0.077165 | -122.436 | 0.078873 | -0.001419 | 0.075746 | -122.3282 | -122.2975 | 7.9315 | 7.9585 | 8.1087 | 8.0552 | -114.8314 | -0.01165 | 0.09611 | 0.12678 | 0.14686 | -122.5015
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0034509 | -0.011023 | 0.0071726 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016622 | 0.034758 | 0.011586 | 7.9812 | 7.9956 | 7.8113 | 7.8674 | 7.8853 | 8.0401 | 7.538 | 0.019362 | 0.073618 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 7.602 | -114.4882 | 8.0453 | 7.8754 | 0.27334 | -114.4704 | -114.3156 | -0.072589 | -122.4222 | 0.083449 | -0.001422 | 0.071167 | -122.3099 | -122.2746 | 7.9315 | 7.9494 | 8.1041 | 8.0597 | -114.8177 | -0.002495 | 0.10984 | 0.1451 | 0.13771 | -122.4923
|  |  |  | 1.4211e-13 | -0.033624 | 0.00014951 | -0.0036647 | -0.011023 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017049 | 0.034758 | 0.011373 | 7.972 | 7.9865 | 7.8067 | 7.8583 | 7.8807 | 8.0263 | 7.5288 | 0.019362 | 0.091933 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 7.6478 | -114.5065 | 8.091 | 7.9257 | 0.27791 | -114.4841 | -114.3385 | -0.017657 | -122.4314 | 0.13838 | 0.058089 | 0.075746 | -122.3145 | -122.2838 | 7.9773 | 7.9997 | 8.1453 | 8.1055 | -114.836 | 0.052437 | 0.16935 | 0.20003 | 0.21095 | -122.5015
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0034509 | -0.011023 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.034545 | 0.011586 | 7.9583 | 7.959 | 7.7884 | 7.8445 | 7.867 | 8.0172 | 7.5105 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.6158 | -114.5569 | 8.0636 | 7.8937 | 0.27792 | -114.5345 | -114.3843 | -0.026811 | -122.468 | 0.12923 | 0.039777 | 0.066588 | -122.3557 | -122.3204 | 7.9498 | 7.9722 | 8.1224 | 8.0643 | -114.8909 | 0.038704 | 0.15104 | 0.18629 | 0.18806 | -122.5335
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017263 | 0.034758 | 0.011373 | 7.9445 | 7.9544 | 7.7792 | 7.84 | 7.8578 | 7.9988 | 7.5013 | 0.023941 | 0.091933 | -0.06093 | -0.071161 | 0.041178 | 0.081008 | -0.13668 | 7.6203 | -114.5477 | 8.0636 | 7.8983 | 0.27792 | -114.5299 | -114.3888 | -0.017657 | -122.4589 | 0.14296 | 0.058089 | 0.075746 | -122.3465 | -122.3067 | 7.959 | 7.9768 | 8.1179 | 8.0735 | -114.8864 | 0.047858 | 0.1602 | 0.20003 | 0.21095 | -122.5244
|  |  |  | 1.4211e-13 | -0.033837 | 0.00036331 | -0.0038783 | -0.011023 | 0.0071726 | -0.0099192 | -0.0044395 | -0.0023397 | 0.016835 | 0.034758 | 0.011586 | 7.9308 | 7.9407 | 7.7701 | 7.8217 | 7.8441 | 7.9988 | 7.4967 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.13668 | 7.5883 | -114.5615 | 8.0224 | 7.8616 | 0.27334 | -114.5391 | -114.3843 | -0.045123 | -122.4451 | 0.11549 | 0.030623 | 0.075746 | -122.3374 | -122.3021 | 7.9132 | 7.9356 | 8.0904 | 8.0323 | -114.8864 | 0.029549 | 0.13731 | 0.17256 | 0.17891 | -122.5198
|  |  |  | 1.4211e-13 | -0.034051 | 0.00014951 | -0.0036647 | -0.011023 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.016835 | 0.034972 | 0.011586 | 7.9308 | 7.9407 | 7.7655 | 7.8125 | 7.8395 | 7.9943 | 7.4922 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.14125 | 7.5654 | -114.5248 | 8.0041 | 7.8388 | 0.27334 | -114.4979 | -114.3431 | -0.068013 | -122.4085 | 0.097183 | 0.012312 | 0.080325 | -122.2916 | -122.2563 | 7.8857 | 7.9127 | 8.0675 | 8.0139 | -114.8452 | 0.002081 | 0.119 | 0.15425 | 0.1606 | -122.4786
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0071726 | -0.0099192 | -0.0044395 | -0.0027669 | 0.016835 | 0.034972 | 0.012014 | 7.9171 | 7.9224 | 7.7472 | 7.8079 | 7.8212 | 7.976 | 7.483 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 7.5425 | -114.5477 | 7.9766 | 7.8067 | 0.26419 | -114.5345 | -114.3797 | -0.081746 | -122.4222 | 0.08345 | -0.006 | 0.075746 | -122.3053 | -122.2746 | 7.8674 | 7.8807 | 8.0355 | 7.9819 | -114.8726 | -0.007073 | 0.10984 | 0.14052 | 0.13771 | -122.4969
|  |  |  | 1.4211e-13 | -0.033837 | -0.00027769 | -0.0034509 | -0.010595 | 0.0073864 | -0.01755 | -0.0046531 | -0.0029805 | 0.016622 | 0.034758 | 0.011373 | 7.9125 | 7.9178 | 7.7472 | 7.7988 | 7.8166 | 7.9714 | 7.4784 | 0.02852 | 0.087354 | -0.065509 | -0.066582 | 0.045757 | 0.090166 | -0.1321 | 7.5883 | -114.6164 | 8.0224 | 7.8571 | 0.26877 | -114.5986 | -114.4438 | -0.022234 | -122.4817 | 0.13838 | 0.044354 | 0.066588 | -122.3694 | -122.325 | 7.9086 | 7.9264 | 8.0812 | 8.0277 | -114.9367 | 0.043281 | 0.15562 | 0.20003 | 0.19722 | -122.5473
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016835 | 0.034545 | 0.0118 | 7.9033 | 7.8995 | 7.738 | 7.7896 | 7.8074 | 7.9531 | 7.4647 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.054914 | 0.081008 | -0.13668 | 7.57 | -114.5889 | 8.0086 | 7.8433 | 0.27335 | -114.5711 | -114.4255 | -0.03139 | -122.4497 | 0.13381 | 0.044356 | 0.075746 | -122.3236 | -122.2975 | 7.8949 | 7.9127 | 8.0583 | 8.0048 | -114.9138 | 0.034125 | 0.1602 | 0.18629 | 0.18806 | -122.5152
|  |  |  | 1.4211e-13 | -0.034051 | -0.00027769 | -0.0034509 | -0.010595 | 0.006959 | -0.0022892 | -0.0042257 | -0.0025533 | 0.016835 | 0.034758 | 0.011586 | 7.8942 | 7.8995 | 7.7243 | 7.7804 | 7.8028 | 7.9485 | 7.4555 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.050335 | 0.081008 | -0.13668 | 7.5517 | -114.5935 | 7.9903 | 7.8204 | 0.26877 | -114.5711 | -114.4255 | -0.040546 | -122.4451 | 0.12007 | 0.0352 | 0.075746 | -122.3236 | -122.293 | 7.8766 | 7.899 | 8.0446 | 7.9956 | -114.9184 | 0.024969 | 0.14646 | 0.17714 | 0.17433 | -122.5106
|  |  |  | 1.4211e-13 | -0.033837 | 0.00014951 | -0.0034509 | -0.011023 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017049 | 0.034972 | 0.0118 | 7.8805 | 7.8766 | 7.7197 | 7.7667 | 7.78 | 7.9439 | 7.451 | 0.019362 | 0.078197 | -0.051772 | -0.071161 | 0.050335 | 0.081008 | -0.1321 | 7.5242 | -114.621 | 7.9537 | 7.793 | 0.26877 | -114.6077 | -114.4438 | -0.058855 | -122.4589 | 0.092604 | 0.02147 | 0.080325 | -122.3374 | -122.3067 | 7.84 | 7.8532 | 8.0171 | 7.9498 | -114.9367 | 0.002081 | 0.12358 | 0.15425 | 0.15144 | -122.5198
|  |  |  | 1.4211e-13 | -0.034051 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.006959 | -0.02518 | -0.0046531 | -0.0021259 | 0.016835 | 0.034545 | 0.011373 | 7.8713 | 7.8766 | 7.706 | 7.7621 | 7.78 | 7.9393 | 7.4464 | 0.023941 | 0.078197 | -0.051772 | -0.066582 | 0.041178 | 0.07643 | -0.12752 | 7.4876 | -114.6027 | 7.9125 | 7.7472 | 0.25961 | -114.5849 | -114.4255 | -0.086319 | -122.4314 | 0.06514 | -0.010573 | 0.075746 | -122.3236 | -122.2884 | 7.8033 | 7.8212 | 7.9805 | 7.9178 | -114.9184 | -0.025383 | 0.082377 | 0.11763 | 0.1194 | -122.4923
|  |  |  | 1.4211e-13 | -0.034265 | 0.00014951 | -0.0036647 | -0.010595 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016622 | 0.034545 | 0.011586 | 7.8621 | 7.8766 | 7.7014 | 7.7576 | 7.7754 | 7.9256 | 7.4418 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.045757 | 0.071851 | -0.1321 | 7.5379 | -114.6347 | 7.9583 | 7.7975 | 0.25962 | -114.6169 | -114.4667 | -0.035967 | -122.4497 | 0.12007 | 0.039779 | 0.075746 | -122.3465 | -122.3204 | 7.8537 | 7.8715 | 8.0217 | 7.9727 | -114.9505 | 0.038705 | 0.14189 | 0.16798 | 0.17891 | -122.5244
|  |  |  | 1.4211e-13 | -0.034051 | 0.00014951 | -0.0038783 | -0.010595 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.017049 | 0.034972 | 0.011373 | 7.8484 | 7.8583 | 7.6831 | 7.7438 | 7.7571 | 7.921 | 7.4235 | 0.019362 | 0.087354 | -0.051772 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.4876 | -114.6118 | 7.9125 | 7.7472 | 0.25962 | -114.5986 | -114.4346 | -0.06801 | -122.4222 | 0.083449 | 0.012315 | 0.080325 | -122.3099 | -122.2746 | 7.8079 | 7.8211 | 7.9851 | 7.9224 | -114.9322 | -0.002495 | 0.10984 | 0.1451 | 0.15144 | -122.4877
|  |  |  | 1.4211e-13 | -0.033837 | -6.4092e-05 | -0.0038783 | -0.010595 | 0.006959 | -0.01755 | -0.0048667 | -0.0025533 | 0.017049 | 0.034972 | 0.011586 | 7.8484 | 7.8491 | 7.6877 | 7.7392 | 7.7433 | 7.9073 | 7.4189 | 0.019362 | 0.082776 | -0.06093 | -0.080318 | 0.045757 | 0.081008 | -0.13668 | 7.4921 | -114.6576 | 7.9216 | 7.7609 | 0.26878 | -114.6535 | -114.4896 | -0.063434 | -122.4772 | 0.092604 | 0.012312 | 0.075746 | -122.3511 | -122.3158 | 7.8125 | 7.8166 | 7.9805 | 7.9224 | -114.9779 | -0.007076 | 0.119 | 0.15425 | 0.15602 | -122.5335
|  |  |  | 1.4211e-13 | -0.033837 | -0.00027769 | -0.0032373 | -0.010809 | 0.0073864 | -0.01755 | -0.0048667 | -0.0027669 | 0.016835 | 0.034545 | 0.0118 | 7.8392 | 7.8537 | 7.6739 | 7.7347 | 7.7525 | 7.9073 | 7.4235 | 0.023941 | 0.10109 | -0.06093 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 7.5105 | -114.6668 | 7.9262 | 7.7609 | 0.25046 | -114.6489 | -114.4942 | -0.049701 | -122.468 | 0.11092 | 0.026045 | 0.075746 | -122.3511 | -122.325 | 7.8216 | 7.8395 | 7.9943 | 7.9407 | -114.9779 | 0.020393 | 0.13731 | 0.1634 | 0.18807 | -122.5381
|  |  |  | 1.4211e-13 | -0.034051 | 0.00014951 | -0.0038783 | -0.011023 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.017049 | 0.035186 | 0.011586 | 7.8301 | 7.8446 | 7.6694 | 7.7301 | 7.7433 | 7.9027 | 7.4143 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.13668 | 7.4647 | -114.6576 | 7.8804 | 7.7197 | 0.25504 | -114.6444 | -114.485 | -0.086322 | -122.4497 | 0.069716 | -0.010576 | 0.075746 | -122.3374 | -122.3021 | 7.7804 | 7.7937 | 7.9531 | 7.8949 | -114.9734 | -0.01165 | 0.10069 | 0.13594 | 0.13771 | -122.5244
|  |  |  | 1.4211e-13 | -0.034051 | -0.00027769 | -0.0034509 | -0.011023 | 0.0076 | -0.01755 | -0.0044395 | -0.0027669 | 0.016835 | 0.034758 | 0.011586 | 7.8301 | 7.8354 | 7.6556 | 7.7209 | 7.7342 | 7.8844 | 7.4097 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.050335 | 0.07643 | -0.1321 | 7.5196 | -114.6897 | 7.94 | 7.7655 | 0.24588 | -114.6764 | -114.5262 | -0.022234 | -122.4772 | 0.1338 | 0.044354 | 0.066588 | -122.3602 | -122.3342 | 7.8308 | 7.844 | 7.9942 | 7.9453 | -115.0008 | 0.043281 | 0.1602 | 0.18629 | 0.19722 | -122.5427
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0065316 | -0.01755 | -0.0046531 | -0.0025533 | 0.016622 | 0.034972 | 0.0118 | 7.8118 | 7.8262 | 7.6419 | 7.698 | 7.7204 | 7.8752 | 7.3914 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.1321 | 7.5013 | -114.7034 | 7.9216 | 7.7518 | 0.25047 | -114.681 | -114.5262 | -0.022234 | -122.4726 | 0.12923 | 0.048933 | 0.071167 | -122.3557 | -122.3204 | 7.8079 | 7.8303 | 7.9851 | 7.9361 | -115.01 | 0.038702 | 0.15562 | 0.19087 | 0.19722 | -122.5335
|  |  |  | 1.4211e-13 | -0.034051 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0071726 | -0.01755 | -0.0044395 | -0.0023397 | 0.017049 | 0.034758 | 0.011586 | 7.798 | 7.8171 | 7.6419 | 7.698 | 7.7113 | 7.8569 | 7.3823 | 0.023941 | 0.091933 | -0.070087 | -0.075739 | 0.041178 | 0.07643 | -0.14125 | 7.4921 | -114.7171 | 7.9079 | 7.7518 | 0.25962 | -114.7039 | -114.5583 | -0.031392 | -122.4909 | 0.1338 | 0.039776 | 0.071168 | -122.374 | -122.3387 | 7.8079 | 7.8211 | 7.9668 | 7.9269 | -115.0329 | 0.034124 | 0.15104 | 0.18629 | 0.2018 | -122.5564
|  |  |  | 1.4211e-13 | -0.034051 | 0.00036331 | -0.0038783 | -0.010595 | 0.006959 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016835 | 0.034758 | 0.011586 | 7.7935 | 7.8079 | 7.6327 | 7.6843 | 7.6975 | 7.8569 | 7.3731 | 0.02852 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.13668 | 7.4555 | -114.7171 | 7.8759 | 7.7151 | 0.25963 | -114.7039 | -114.5445 | -0.054279 | -122.4726 | 0.11092 | 0.021467 | 0.075746 | -122.3557 | -122.3204 | 7.7667 | 7.7799 | 7.9393 | 7.8903 | -115.0283 | 0.011236 | 0.12815 | 0.1634 | 0.16975 | -122.5381
|  |  |  | 1.4211e-13 | -0.034265 | -6.4092e-05 | -0.0034509 | -0.010809 | 0.0073864 | -0.02518 | -0.0048667 | -0.0023397 | 0.016835 | 0.034972 | 0.011586 | 7.7797 | 7.7896 | 7.6144 | 7.6843 | 7.693 | 7.8432 | 7.3594 | 0.02852 | 0.087354 | -0.056351 | -0.066582 | 0.045757 | 0.085587 | -0.14125 | 7.4647 | -114.7126 | 7.885 | 7.7197 | 0.25505 | -114.7039 | -114.5537 | -0.035969 | -122.4634 | 0.13381 | 0.048935 | 0.084904 | -122.3511 | -122.3113 | 7.7896 | 7.7982 | 7.9485 | 7.8949 | -115.0375 | 0.038704 | 0.15104 | 0.19087 | 0.19264 | -122.5381
|  |  |  | 1.4211e-13 | -0.034051 | 0.00036331 | -0.0036647 | -0.011023 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017049 | 0.034972 | 0.011373 | 7.7752 | 7.7805 | 7.6098 | 7.666 | 7.6746 | 7.8432 | 7.3594 | 0.014784 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 7.4143 | -114.7263 | 7.8301 | 7.6648 | 0.25047 | -114.7176 | -114.5491 | -0.081744 | -122.4589 | 0.069716 | -0.005998 | 0.075746 | -122.3419 | -122.3158 | 7.7209 | 7.7296 | 7.8981 | 7.8354 | -115.0329 | -0.01165 | 0.10527 | 0.13136 | 0.14229 | -122.5289
|  |  |  | 1.4211e-13 | -0.034265 | 0.00036331 | -0.0038783 | -0.011236 | 0.006959 | -0.01755 | -0.0044395 | -0.0027669 | 0.017476 | 0.034972 | 0.011586 | 7.7614 | 7.7621 | 7.5961 | 7.6523 | 7.6609 | 7.8203 | 7.3456 | 0.02852 | 0.082776 | -0.065509 | -0.071161 | 0.045757 | 0.085587 | -0.1321 | 7.4647 | -114.7675 | 7.8804 | 7.7151 | 0.25047 | -114.7588 | -114.5995 | -0.013078 | -122.4909 | 0.14754 | 0.05351 | 0.066588 | -122.374 | -122.3342 | 7.7713 | 7.7799 | 7.9393 | 7.8812 | -115.0741 | 0.047858 | 0.16478 | 0.20461 | 0.2018 | -122.5518
|  |  |  | 1.4211e-13 | -0.034051 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0073864 | -0.01755 | -0.0044395 | -0.0027669 | 0.017263 | 0.034758 | 0.011586 | 7.7431 | 7.7667 | 7.5915 | 7.6431 | 7.6701 | 7.8157 | 7.3502 | 0.019362 | 0.082776 | -0.065509 | -0.071161 | 0.041178 | 0.081008 | -0.1321 | 7.4189 | -114.7446 | 7.8118 | 7.6602 | 0.24131 | -114.7176 | -114.572 | -0.063432 | -122.4589 | 0.088027 | 0.003156 | 0.066588 | -122.3465 | -122.3067 | 7.7118 | 7.7387 | 7.8844 | 7.8354 | -115.0375 | -0.002496 | 0.10984 | 0.14967 | 0.15144 | -122.5198
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017476 | 0.034758 | 0.011586 | 7.7431 | 7.7438 | 7.5641 | 7.6294 | 7.6472 | 7.802 | 7.3227 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.14125 | 7.3777 | -114.7721 | 7.798 | 7.619 | 0.24132 | -114.7543 | -114.5995 | -0.086323 | -122.468 | 0.078873 | -0.005998 | 0.080325 | -122.3557 | -122.325 | 7.6843 | 7.7021 | 7.8569 | 7.7988 | -115.0787 | -0.01165 | 0.10069 | 0.13136 | 0.14229 | -122.5427
|  |  |  | 1.4211e-13 | -0.034051 | -6.4092e-05 | -0.0043057 | -0.010809 | 0.006959 | -0.01755 | -0.0048667 | -0.0025533 | 0.017263 | 0.034972 | 0.011586 | 7.7294 | 7.7347 | 7.5595 | 7.6248 | 7.638 | 7.7882 | 7.309 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.1321 | 7.3639 | -114.7583 | 7.7843 | 7.6144 | 0.25048 | -114.7451 | -114.5949 | -0.077165 | -122.4497 | 0.078873 | -0.010577 | 0.066588 | -122.3374 | -122.2975 | 7.6797 | 7.6929 | 7.8432 | 7.7896 | -115.0741 | -0.01165 | 0.10069 | 0.14052 | 0.13771 | -122.5152
|  |  |  | 1.4211e-13 | -0.034265 | -0.00027769 | -0.0034509 | -0.011236 | 0.0071726 | -0.01755 | -0.0044395 | -0.0025533 | 0.017476 | 0.034972 | 0.011586 | 7.7065 | 7.7164 | 7.5412 | 7.5973 | 7.6197 | 7.7699 | 7.2953 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.054914 | 0.081008 | -0.13668 | 7.3639 | -114.7904 | 7.7751 | 7.6098 | 0.2459 | -114.768 | -114.6178 | -0.068011 | -122.4589 | 0.092606 | 0.007735 | 0.075746 | -122.3328 | -122.3067 | 7.666 | 7.6884 | 7.8386 | 7.785 | -115.0924 | -0.002496 | 0.12358 | 0.14967 | 0.15144 | -122.5244
|  |  |  | 1.4211e-13 | -0.034265 | 0.00014951 | -0.0034509 | -0.011023 | 0.006959 | -0.0022892 | -0.0050803 | -0.0023397 | 0.017476 | 0.034972 | 0.011159 | 7.6973 | 7.7026 | 7.5274 | 7.5973 | 7.606 | 7.7608 | 7.2907 | 0.02852 | 0.087354 | -0.065509 | -0.071161 | 0.054914 | 0.07643 | -0.13668 | 7.3548 | -114.7721 | 7.7614 | 7.5915 | 0.23674 | -114.7634 | -114.6086 | -0.072589 | -122.4405 | 0.092607 | -0.001422 | 0.071167 | -122.3145 | -122.293 | 7.6614 | 7.67 | 7.8248 | 7.7667 | -115.0787 | -0.007074 | 0.119 | 0.14052 | 0.15144 | -122.5061
|  |  |  | 1.4211e-13 | -0.034265 | -0.00049149 | -0.0034509 | -0.010809 | 0.006959 | -0.0022892 | -0.0048667 | -0.0025533 | 0.017263 | 0.034758 | 0.011373 | 7.679 | 7.6889 | 7.5183 | 7.5744 | 7.6014 | 7.747 | 7.277 | 0.014784 | 0.091933 | -0.056351 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 7.3685 | -114.8545 | 7.7706 | 7.6098 | 0.24133 | -114.8275 | -114.6819 | -0.045123 | -122.4955 | 0.10634 | 0.035202 | 0.080325 | -122.3831 | -122.3525 | 7.666 | 7.6929 | 7.8386 | 7.7804 | -115.1519 | 0.024971 | 0.13731 | 0.16798 | 0.18349 | -122.5656
|  |  |  | 1.4211e-13 | -0.034478 | -0.00027769 | -0.0036647 | -0.011023 | 0.0071726 | -0.01755 | -0.0046531 | -0.0025533 | 0.017476 | 0.035186 | 0.011373 | 7.6698 | 7.6797 | 7.5091 | 7.5607 | 7.5876 | 7.7379 | 7.277 | 0.019362 | 0.091933 | -0.070087 | -0.062004 | 0.041178 | 0.085587 | -0.13668 | 7.3777 | -114.8728 | 7.7706 | 7.6098 | 0.23217 | -114.8458 | -114.6956 | -0.035968 | -122.4955 | 0.12007 | 0.030621 | 0.066589 | -122.3923 | -122.3479 | 7.6614 | 7.6883 | 7.8386 | 7.7804 | -115.1565 | 0.038704 | 0.14189 | 0.18629 | 0.19264 | -122.5701
|  |  |  | 1.4211e-13 | -0.034265 | -6.4092e-05 | -0.0032373 | -0.010809 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.017476 | 0.034758 | 0.011586 | 7.6561 | 7.6751 | 7.4954 | 7.5515 | 7.5647 | 7.7196 | 7.2495 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.085587 | -0.12752 | 7.3456 | -114.9003 | 7.7522 | 7.5915 | 0.24591 | -114.887 | -114.7322 | -0.031388 | -122.5229 | 0.12007 | 0.0352 | 0.066588 | -122.406 | -122.3662 | 7.6477 | 7.6609 | 7.8157 | 7.7713 | -115.2023 | 0.024969 | 0.14189 | 0.18172 | 0.17891 | -122.5793
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0038783 | -0.010809 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017263 | 0.034758 | 0.011586 | 7.6378 | 7.6523 | 7.4771 | 7.5332 | 7.5556 | 7.7058 | 7.2449 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.085587 | -0.13668 | 7.3227 | -114.827 | 7.7156 | 7.5549 | 0.23217 | -114.8046 | -114.6544 | -0.058856 | -122.4268 | 0.10176 | 0.01689 | 0.075746 | -122.3191 | -122.2746 | 7.611 | 7.6334 | 7.7836 | 7.7301 | -115.1153 | 0.011238 | 0.119 | 0.16341 | 0.16517 | -122.4969
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0034509 | -0.010595 | 0.0073864 | -0.01755 | -0.0046531 | -0.0027669 | 0.017049 | 0.034758 | 0.011373 | 7.6241 | 7.6339 | 7.4633 | 7.5195 | 7.5281 | 7.6875 | 7.2174 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.071851 | -0.14125 | 7.2724 | -114.8728 | 7.679 | 7.5183 | 0.24591 | -114.8642 | -114.7048 | -0.086323 | -122.4634 | 0.074294 | -0.005998 | 0.080325 | -122.3511 | -122.3204 | 7.5744 | 7.583 | 7.7424 | 7.6889 | -115.1748 | -0.016229 | 0.09611 | 0.12678 | 0.14229 | -122.5335
|  |  |  | 1.4211e-13 | -0.034906 | 0.00014951 | -0.0036647 | -0.010809 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017476 | 0.035186 | 0.011586 | 7.592 | 7.6065 | 7.4313 | 7.4966 | 7.5052 | 7.6692 | 7.2037 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.2815 | -114.9186 | 7.6698 | 7.5091 | 0.2276 | -114.9099 | -114.746 | -0.054277 | -122.4817 | 0.097182 | 0.01689 | 0.071167 | -122.3694 | -122.3342 | 7.5744 | 7.583 | 7.747 | 7.6843 | -115.2115 | 0.011238 | 0.12358 | 0.15883 | 0.1606 | -122.5473
|  |  |  | 1.4211e-13 | -0.034478 | -0.00027769 | -0.0034509 | -0.011023 | 0.0073864 | -0.0022892 | -0.0044395 | -0.0027669 | 0.017049 | 0.034972 | 0.011586 | 7.592 | 7.6065 | 7.4313 | 7.4874 | 7.5144 | 7.66 | 7.1991 | 0.023941 | 0.091933 | -0.065509 | -0.062004 | 0.045757 | 0.081008 | -0.1321 | 7.2678 | -114.9323 | 7.6607 | 7.5 | 0.23218 | -114.9054 | -114.7597 | -0.063432 | -122.4817 | 0.092606 | 0.003156 | 0.066588 | -122.374 | -122.3387 | 7.5561 | 7.583 | 7.7287 | 7.6751 | -115.2206 | 0.006661 | 0.11442 | 0.14967 | 0.1606 | -122.5518
|  |  |  | 1.4211e-13 | -0.034478 | -0.00027769 | -0.0036647 | -0.010595 | 0.006959 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016835 | 0.034972 | 0.011159 | 7.5783 | 7.5836 | 7.413 | 7.4783 | 7.4961 | 7.6463 | 7.1854 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.045757 | 0.07643 | -0.14125 | 7.2449 | -114.9506 | 7.6378 | 7.4725 | 0.2276 | -114.9328 | -114.7826 | -0.081746 | -122.4863 | 0.08345 | -0.006 | 0.075746 | -122.3831 | -122.3525 | 7.5378 | 7.5556 | 7.7058 | 7.6431 | -115.2435 | 0.002084 | 0.10527 | 0.13594 | 0.14228 | -122.5701
|  |  |  | 1.4211e-13 | -0.034265 | 0.00014951 | -0.0036647 | -0.010809 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0025533 | 0.01769 | 0.034972 | 0.0118 | 7.5645 | 7.5744 | 7.4084 | 7.46 | 7.4823 | 7.628 | 7.1762 | 0.023941 | 0.091933 | -0.06093 | -0.062004 | 0.050335 | 0.081008 | -0.1321 | 7.2724 | -114.9369 | 7.6607 | 7.5045 | 0.23218 | -114.9145 | -114.7689 | -0.035967 | -122.4589 | 0.12007 | 0.0352 | 0.071167 | -122.3465 | -122.3158 | 7.5561 | 7.5785 | 7.7241 | 7.6705 | -115.2206 | 0.034126 | 0.14646 | 0.17714 | 0.18806 | -122.5289
|  |  |  | 1.4211e-13 | -0.034265 | 0.00036331 | -0.0036647 | -0.010809 | 0.006959 | -0.01755 | -0.0046531 | -0.0025533 | 0.017263 | 0.034972 | 0.0118 | 7.5462 | 7.5561 | 7.3901 | 7.4554 | 7.4732 | 7.6188 | 7.1625 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.041178 | 0.07643 | -0.14583 | 7.2449 | -114.946 | 7.6286 | 7.4725 | 0.22761 | -114.9283 | -114.7826 | -0.063436 | -122.4726 | 0.10634 | 0.021467 | 0.084903 | -122.3602 | -122.325 | 7.5378 | 7.5556 | 7.7012 | 7.6385 | -115.2389 | 0.011236 | 0.12357 | 0.15883 | 0.16975 | -122.5473
|  |  |  | 1.4211e-13 | -0.034265 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017263 | 0.034758 | 0.011586 | 7.5371 | 7.5424 | 7.3764 | 7.4325 | 7.4457 | 7.6005 | 7.1442 | 0.023941 | 0.087354 | -0.065509 | -0.062004 | 0.045757 | 0.07643 | -0.1321 | 7.2266 | -114.9964 | 7.6195 | 7.4588 | 0.23219 | -114.9832 | -114.8284 | -0.0497 | -122.4909 | 0.10634 | 0.016888 | 0.066588 | -122.3831 | -122.3525 | 7.5149 | 7.5281 | 7.6829 | 7.6248 | -115.2847 | 0.020393 | 0.12815 | 0.15883 | 0.16975 | -122.561
|  |  |  | 1.4211e-13 | -0.034478 | -0.00027769 | -0.0036647 | -0.010809 | 0.0076 | 0.0053413 | -0.0048667 | -0.0027669 | 0.017049 | 0.034972 | 0.011586 | 7.5188 | 7.5286 | 7.3626 | 7.4188 | 7.4411 | 7.5914 | 7.1396 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 7.1991 | -114.9827 | 7.5783 | 7.4221 | 0.22303 | -114.9603 | -114.8101 | -0.077167 | -122.468 | 0.08345 | 0.003158 | 0.080325 | -122.3557 | -122.3204 | 7.4783 | 7.5006 | 7.6509 | 7.5881 | -115.2618 | -0.007073 | 0.10527 | 0.14052 | 0.14228 | -122.5381
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0038783 | -0.010809 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017476 | 0.035186 | 0.011373 | 7.5142 | 7.5195 | 7.3535 | 7.4096 | 7.4228 | 7.5822 | 7.135 | 0.02852 | 0.087354 | -0.056351 | -0.071161 | 0.045757 | 0.081008 | -0.1321 | 7.2495 | -115.033 | 7.6286 | 7.4679 | 0.21845 | -115.0198 | -114.8604 | -0.017656 | -122.5138 | 0.14296 | 0.05809 | 0.075746 | -122.3969 | -122.3616 | 7.524 | 7.5372 | 7.6966 | 7.6339 | -115.3076 | 0.04328 | 0.1602 | 0.19545 | 0.2018 | -122.5747
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0034509 | -0.010595 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017263 | 0.034972 | 0.011373 | 7.4959 | 7.5103 | 7.3397 | 7.4004 | 7.4136 | 7.5685 | 7.1167 | 0.023941 | 0.078197 | -0.070087 | -0.071161 | 0.050335 | 0.081008 | -0.14125 | 7.2128 | -115.0513 | 7.592 | 7.4359 | 0.22303 | -115.0381 | -114.8833 | -0.045125 | -122.5229 | 0.12007 | 0.026043 | 0.071168 | -122.4014 | -122.3708 | 7.4966 | 7.5098 | 7.6646 | 7.6064 | -115.3351 | 0.024969 | 0.14646 | 0.17714 | 0.17433 | -122.593
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0034509 | -0.011023 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0021259 | 0.017476 | 0.034972 | 0.011159 | 7.4959 | 7.5012 | 7.3352 | 7.3913 | 7.4045 | 7.5639 | 7.1075 | 0.019362 | 0.087354 | -0.070087 | -0.062004 | 0.041178 | 0.085587 | -0.1321 | 7.1991 | -115.033 | 7.5874 | 7.4267 | 0.22761 | -115.0198 | -114.8604 | -0.040544 | -122.4863 | 0.11091 | 0.021466 | 0.06201 | -122.3831 | -122.3387 | 7.4828 | 7.496 | 7.6554 | 7.5927 | -115.3168 | 0.029549 | 0.13273 | 0.17714 | 0.17891 | -122.5564
|  |  |  | 1.4211e-13 | -0.034478 | 0.00014951 | -0.0036647 | -0.011023 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017049 | 0.035186 | 0.011373 | 7.4821 | 7.4874 | 7.3214 | 7.373 | 7.3953 | 7.5547 | 7.103 | 0.019362 | 0.091933 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.1854 | -115.0285 | 7.5645 | 7.4038 | 0.21846 | -115.0061 | -114.8467 | -0.0497 | -122.468 | 0.10176 | 0.021467 | 0.071167 | -122.3557 | -122.3204 | 7.4554 | 7.4777 | 7.6371 | 7.5698 | -115.2985 | 0.015815 | 0.12815 | 0.1634 | 0.17433 | -122.5335
|  |  |  | 1.4211e-13 | -0.034265 | -0.00027769 | -0.0032373 | -0.011236 | 0.006959 | -0.0022892 | -0.0046531 | -0.0027669 | 0.017049 | 0.034972 | 0.011586 | 7.4638 | 7.4828 | 7.3077 | 7.3592 | 7.3862 | 7.541 | 7.0801 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 7.1442 | -115.0285 | 7.5279 | 7.3718 | 0.22762 | -115.0015 | -114.8467 | -0.06801 | -122.4543 | 0.088028 | 0.003157 | 0.071167 | -122.3419 | -122.3067 | 7.4233 | 7.4503 | 7.6051 | 7.5469 | -115.3076 | -0.002495 | 0.10984 | 0.1451 | 0.14686 | -122.5198
|  |  |  | 1.4211e-13 | -0.034478 | 0.00014951 | -0.0036647 | -0.011236 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0023397 | 0.017263 | 0.034972 | 0.0118 | 7.4501 | 7.4691 | 7.2848 | 7.3547 | 7.3678 | 7.5273 | 7.0755 | 0.02852 | 0.091933 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.13668 | 7.1442 | -115.0651 | 7.5187 | 7.3535 | 0.20931 | -115.0519 | -114.8925 | -0.068011 | -122.4817 | 0.097185 | 0.007735 | 0.075746 | -122.3694 | -122.3342 | 7.4233 | 7.4365 | 7.5959 | 7.5378 | -115.3443 | 0.006661 | 0.119 | 0.15425 | 0.1606 | -122.5564
|  |  |  | 1.4211e-13 | -0.034265 | -0.00027769 | -0.0034509 | -0.01145 | 0.006959 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017476 | 0.034758 | 0.011373 | 7.4455 | 7.4554 | 7.2802 | 7.3547 | 7.3633 | 7.5089 | 7.0709 | 0.023941 | 0.082776 | -0.056351 | -0.071161 | 0.041178 | 0.085587 | -0.13668 | 7.1716 | -115.0513 | 7.5462 | 7.3809 | 0.20931 | -115.0427 | -114.8971 | -0.035968 | -122.4772 | 0.12465 | 0.044357 | 0.080325 | -122.3648 | -122.3204 | 7.4554 | 7.464 | 7.6096 | 7.5561 | -115.3351 | 0.029547 | 0.14189 | 0.18629 | 0.18348 | -122.5427
|  |  |  | 1.4211e-13 | -0.034265 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.035186 | 0.011586 | 7.4272 | 7.4462 | 7.2756 | 7.3318 | 7.345 | 7.5089 | 7.0572 | 0.019362 | 0.091933 | -0.06093 | -0.066582 | 0.045757 | 0.085587 | -0.1321 | 7.1029 | -115.0651 | 7.473 | 7.3214 | 0.21847 | -115.0519 | -114.8879 | -0.086321 | -122.4634 | 0.065138 | -0.015154 | 0.071167 | -122.3511 | -122.3113 | 7.3775 | 7.3907 | 7.5547 | 7.492 | -115.3397 | -0.020806 | 0.091533 | 0.13136 | 0.13771 | -122.5289
|  |  |  | 1.4211e-13 | -0.034265 | -0.00027769 | -0.0034509 | -0.010809 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.035399 | 0.011586 | 7.4272 | 7.4233 | 7.2665 | 7.3226 | 7.3358 | 7.4906 | 7.0434 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.041178 | 0.081008 | -0.13668 | 7.1075 | -115.0926 | 7.4913 | 7.3306 | 0.22304 | -115.0794 | -114.9245 | -0.072589 | -122.4817 | 0.088028 | 0.003157 | 0.075746 | -122.374 | -122.3342 | 7.3867 | 7.3999 | 7.5547 | 7.4874 | -115.3717 | -0.002495 | 0.10526 | 0.1451 | 0.14686 | -122.5518
|  |  |  | 1.4211e-13 | -0.034478 | 0.00036331 | -0.0036647 | -0.011023 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0023397 | 0.017049 | 0.034972 | 0.011586 | 7.3951 | 7.4142 | 7.2482 | 7.3043 | 7.3175 | 7.4677 | 7.0251 | 0.02852 | 0.087354 | -0.056351 | -0.071161 | 0.041178 | 0.085587 | -0.14125 | 7.0846 | -115.1383 | 7.4547 | 7.3077 | 0.22305 | -115.1251 | -114.9749 | -0.081746 | -122.5138 | 0.088029 | 0.003158 | 0.084904 | -122.4014 | -122.357 | 7.3638 | 7.377 | 7.5272 | 7.4737 | -115.4175 | -0.011652 | 0.10069 | 0.1451 | 0.14686 | -122.5839
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0036647 | -0.011023 | 0.006959 | -0.0022892 | -0.0046531 | -0.0021259 | 0.017263 | 0.034972 | 0.011586 | 7.3906 | 7.4096 | 7.2344 | 7.2997 | 7.3175 | 7.4677 | 7.016 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.041178 | 0.085587 | -0.13668 | 7.1029 | -115.12 | 7.4775 | 7.3214 | 0.21847 | -115.1023 | -114.952 | -0.049701 | -122.4863 | 0.11092 | 0.026045 | 0.075746 | -122.3786 | -122.3342 | 7.3867 | 7.4045 | 7.5547 | 7.4966 | -115.4038 | 0.020393 | 0.12815 | 0.17256 | 0.17891 | -122.5564
|  |  |  | 1.4211e-13 | -0.034478 | -0.00027769 | -0.0036647 | -0.011236 | 0.0071726 | -0.02518 | -0.0046531 | -0.0023397 | 0.017049 | 0.035186 | 0.011373 | 7.3768 | 7.3959 | 7.2253 | 7.2814 | 7.2992 | 7.4586 | 7.016 | 0.019362 | 0.091933 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 7.1258 | -115.175 | 7.4867 | 7.3351 | 0.20931 | -115.1572 | -114.9978 | -0.026813 | -122.5229 | 0.12923 | 0.044354 | 0.071167 | -122.4106 | -122.3754 | 7.3913 | 7.409 | 7.5684 | 7.5057 | -115.4404 | 0.043281 | 0.15562 | 0.19087 | 0.2018 | -122.593
|  |  |  | 1.4211e-13 | -0.034692 | 0.00014951 | -0.0036647 | -0.011023 | 0.0071726 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017476 | 0.035186 | 0.011159 | 7.3768 | 7.3775 | 7.207 | 7.2677 | 7.29 | 7.4494 | 6.9976 | 0.019362 | 0.087354 | -0.065509 | -0.075739 | 0.045757 | 0.085587 | -0.1321 | 7.0617 | -115.1338 | 7.4409 | 7.271 | 0.20932 | -115.1114 | -114.952 | -0.06801 | -122.4772 | 0.083449 | -0.001422 | 0.066588 | -122.3557 | -122.3158 | 7.3318 | 7.3541 | 7.5135 | 7.4416 | -115.4038 | -0.011652 | 0.10984 | 0.14967 | 0.15144 | -122.5335
|  |  |  | 1.4211e-13 | -0.034906 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0021259 | 0.017263 | 0.035186 | 0.011586 | 7.3494 | 7.3684 | 7.1978 | 7.2539 | 7.2717 | 7.4219 | 6.9931 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.14125 | 7.1029 | -115.1841 | 7.4592 | 7.3077 | 0.20474 | -115.1664 | -115.0161 | -0.031392 | -122.5046 | 0.12923 | 0.044354 | 0.075746 | -122.3923 | -122.357 | 7.3638 | 7.3816 | 7.5318 | 7.4782 | -115.445 | 0.043281 | 0.15562 | 0.19087 | 0.19722 | -122.5793
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0036647 | -0.010809 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0023397 | 0.01769 | 0.035186 | 0.011373 | 7.3402 | 7.3501 | 7.1841 | 7.2402 | 7.2625 | 7.4128 | 6.9748 | 0.019362 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 7.048 | -115.1704 | 7.4134 | 7.2573 | 0.20932 | -115.148 | -114.9978 | -0.063434 | -122.4772 | 0.092604 | 0.012312 | 0.075746 | -122.3648 | -122.3296 | 7.3134 | 7.3358 | 7.486 | 7.4233 | -115.4358 | 0.00666 | 0.119 | 0.15425 | 0.1606 | -122.5473
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0029805 | 0.017263 | 0.035399 | 0.011373 | 7.3265 | 7.3317 | 7.1658 | 7.2265 | 7.2396 | 7.4036 | 6.961 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 7.0297 | -115.1979 | 7.3951 | 7.2344 | 0.20474 | -115.1847 | -115.0207 | -0.068011 | -122.4909 | 0.088027 | 0.007735 | 0.075746 | -122.3786 | -122.3433 | 7.2951 | 7.3083 | 7.4723 | 7.4004 | -115.4633 | 0.002083 | 0.11442 | 0.14967 | 0.15144 | -122.561
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0036647 | -0.011023 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017476 | 0.035186 | 0.011373 | 7.3265 | 7.3317 | 7.1612 | 7.2265 | 7.2351 | 7.3807 | 6.9519 | 0.02852 | 0.091933 | -0.056351 | -0.071161 | 0.050335 | 0.081008 | -0.1321 | 7.048 | -115.2482 | 7.4226 | 7.2573 | 0.20932 | -115.2396 | -115.0939 | -0.035967 | -122.5458 | 0.12465 | 0.039779 | 0.075746 | -122.4243 | -122.3937 | 7.3226 | 7.3312 | 7.4769 | 7.4279 | -115.5228 | 0.024969 | 0.14646 | 0.17714 | 0.18806 | -122.6068
|  |  |  | 1.4211e-13 | -0.034692 | -0.00049149 | -0.0038783 | -0.011236 | 0.0076 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.034972 | 0.011586 | 7.3082 | 7.318 | 7.152 | 7.2127 | 7.2305 | 7.3807 | 6.9473 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.081008 | -0.1321 | 7.0755 | -115.2391 | 7.4363 | 7.2802 | 0.20475 | -115.2213 | -115.071 | -0.003923 | -122.5184 | 0.15212 | 0.067244 | 0.071167 | -122.4106 | -122.3708 | 7.3409 | 7.3587 | 7.5089 | 7.4462 | -115.5045 | 0.061592 | 0.16935 | 0.20918 | 0.21553 | -122.5839
|  |  |  | 1.4211e-13 | -0.034906 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.01755 | -0.0044395 | -0.0025533 | 0.017263 | 0.035186 | 0.011159 | 7.299 | 7.318 | 7.1383 | 7.2081 | 7.2213 | 7.3716 | 6.9427 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.081008 | -0.13668 | 7.0526 | -115.2253 | 7.4089 | 7.2481 | 0.19559 | -115.2121 | -115.0619 | -0.026813 | -122.4955 | 0.12923 | 0.048933 | 0.075746 | -122.3831 | -122.3525 | 7.318 | 7.3312 | 7.4814 | 7.4279 | -115.4908 | 0.047859 | 0.1602 | 0.19087 | 0.19264 | -122.5701
|  |  |  | 1.4211e-13 | -0.034692 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0071726 | -0.01755 | -0.0046531 | -0.0027669 | 0.017263 | 0.035613 | 0.011586 | 7.2898 | 7.2951 | 7.1337 | 7.1944 | 7.2122 | 7.3578 | 6.9244 | 0.023941 | 0.091933 | -0.065509 | -0.066582 | 0.041178 | 0.07643 | -0.13668 | 7.0251 | -115.2482 | 7.3905 | 7.2344 | 0.20933 | -115.2305 | -115.0848 | -0.035968 | -122.5092 | 0.12465 | 0.035199 | 0.071167 | -122.4014 | -122.3662 | 7.2951 | 7.3129 | 7.4586 | 7.3958 | -115.5182 | 0.034126 | 0.14189 | 0.17714 | 0.19264 | -122.5793
|  |  |  | 1.4211e-13 | -0.034478 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017263 | 0.035399 | 0.011159 | 7.2761 | 7.2951 | 7.1246 | 7.1807 | 7.203 | 7.3487 | 6.9152 | 0.02852 | 0.091933 | -0.06093 | -0.071161 | 0.045757 | 0.085587 | -0.13668 | 7.0068 | -115.2848 | 7.3677 | 7.2161 | 0.20933 | -115.2625 | -115.1168 | -0.045123 | -122.5367 | 0.12007 | 0.030623 | 0.075746 | -122.4198 | -122.3799 | 7.2722 | 7.2946 | 7.4402 | 7.3867 | -115.5503 | 0.020392 | 0.13731 | 0.17714 | 0.18349 | -122.6022
|  |  |  | 1.4211e-13 | -0.034906 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.006959 | -0.01755 | -0.0048667 | -0.0027669 | 0.017476 | 0.034972 | 0.011586 | 7.2715 | 7.2768 | 7.1154 | 7.1761 | 7.1893 | 7.3441 | 6.9061 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 7.0068 | -115.294 | 7.3722 | 7.2161 | 0.20933 | -115.2808 | -115.126 | -0.035968 | -122.5367 | 0.12923 | 0.039778 | 0.075746 | -122.4243 | -122.3937 | 7.2768 | 7.29 | 7.4448 | 7.3775 | -115.564 | 0.034126 | 0.14647 | 0.17714 | 0.18806 | -122.6068
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0036647 | -0.011023 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017476 | 0.035186 | 0.011373 | 7.2532 | 7.2676 | 7.1017 | 7.1624 | 7.1801 | 7.3304 | 6.8969 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 7.0068 | -115.294 | 7.3631 | 7.2115 | 0.20475 | -115.2762 | -115.126 | -0.026813 | -122.5229 | 0.1338 | 0.048933 | 0.075746 | -122.4106 | -122.3799 | 7.2722 | 7.29 | 7.4402 | 7.3775 | -115.5595 | 0.043281 | 0.15562 | 0.18629 | 0.19722 | -122.593
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0036647 | -0.011236 | 0.0071726 | -0.01755 | -0.0046531 | -0.0023397 | 0.017049 | 0.035186 | 0.011159 | 7.2441 | 7.2631 | 7.0925 | 7.1624 | 7.1755 | 7.3212 | 6.8832 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.050335 | 0.081008 | -0.13668 | 6.9747 | -115.326 | 7.3356 | 7.1841 | 0.20933 | -115.3129 | -115.1672 | -0.045123 | -122.5596 | 0.11549 | 0.026044 | 0.071167 | -122.4381 | -122.4074 | 7.2539 | 7.2671 | 7.4128 | 7.3546 | -115.6052 | 0.020392 | 0.14189 | 0.17256 | 0.17891 | -122.6251
|  |  |  | 1.4211e-13 | -0.034692 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0067454 | -0.01755 | -0.0044395 | -0.0027669 | 0.017263 | 0.034758 | 0.011373 | 7.2395 | 7.2493 | 7.0742 | 7.1303 | 7.1572 | 7.3121 | 6.874 | 0.023941 | 0.091933 | -0.051772 | -0.071161 | 0.054914 | 0.07643 | -0.13668 | 6.9747 | -115.3169 | 7.3402 | 7.1749 | 0.20018 | -115.29 | -115.1351 | -0.035968 | -122.5184 | 0.12465 | 0.048936 | 0.084904 | -122.3923 | -122.3708 | 7.231 | 7.2579 | 7.4128 | 7.35 | -115.5732 | 0.029547 | 0.15562 | 0.17714 | 0.19264 | -122.5839
|  |  |  | 1.4211e-13 | -0.034692 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0076 | -0.0022892 | -0.0048667 | -0.0027669 | 0.016835 | 0.035186 | 0.011159 | 7.2212 | 7.2264 | 7.065 | 7.1303 | 7.1343 | 7.2937 | 6.8649 | 0.02852 | 0.082776 | -0.056351 | -0.062004 | 0.045757 | 0.07643 | -0.12752 | 6.9564 | -115.3215 | 7.3127 | 7.1566 | 0.20018 | -115.3175 | -115.158 | -0.035965 | -122.5138 | 0.12007 | 0.035202 | 0.071167 | -122.406 | -122.3754 | 7.2219 | 7.2259 | 7.3853 | 7.318 | -115.5869 | 0.029549 | 0.13731 | 0.16798 | 0.17433 | -122.5793
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0048667 | -0.0023397 | 0.017049 | 0.034972 | 0.011159 | 7.2074 | 7.2219 | 7.0421 | 7.1074 | 7.1297 | 7.2846 | 6.8511 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.054914 | 0.081008 | -0.13668 | 6.9106 | -115.3077 | 7.2669 | 7.1017 | 0.19102 | -115.2854 | -115.1306 | -0.077167 | -122.4772 | 0.08345 | -0.001421 | 0.075746 | -122.3602 | -122.3342 | 7.1669 | 7.1893 | 7.3441 | 7.2814 | -115.564 | -0.002495 | 0.11442 | 0.14052 | 0.14686 | -122.5518
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0036647 | -0.011236 | 0.0071726 | -0.02518 | -0.0046531 | -0.0029805 | 0.017049 | 0.035186 | 0.011373 | 7.1937 | 7.2127 | 7.0376 | 7.0983 | 7.1068 | 7.2754 | 6.8374 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.054914 | 0.081008 | -0.13668 | 6.9198 | -115.3581 | 7.2761 | 7.12 | 0.20018 | -115.3495 | -115.1809 | -0.054279 | -122.5275 | 0.10634 | 0.021467 | 0.075746 | -122.4014 | -122.3754 | 7.1807 | 7.1892 | 7.3578 | 7.2951 | -115.619 | 0.011236 | 0.13731 | 0.1634 | 0.16517 | -122.593
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0038783 | -0.011023 | 0.0073864 | -0.02518 | -0.0044395 | -0.0023397 | 0.017263 | 0.034972 | 0.010945 | 7.1937 | 7.1944 | 7.0284 | 7.0891 | 7.1114 | 7.2617 | 6.8328 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.050335 | 0.081008 | -0.14125 | 6.9152 | -115.3672 | 7.2761 | 7.1108 | 0.1956 | -115.3449 | -115.1947 | -0.058858 | -122.5275 | 0.10634 | 0.026046 | 0.084904 | -122.406 | -122.3754 | 7.1715 | 7.1938 | 7.3441 | 7.2768 | -115.6236 | 0.011236 | 0.13273 | 0.1634 | 0.16975 | -122.5976
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0036647 | -0.011236 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.017263 | 0.035399 | 0.010945 | 7.1708 | 7.1898 | 7.0193 | 7.0845 | 7.1023 | 7.248 | 6.8236 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.14125 | 6.9335 | -115.381 | 7.2807 | 7.1291 | 0.19561 | -115.3632 | -115.2176 | -0.031392 | -122.5367 | 0.1338 | 0.048933 | 0.080325 | -122.4198 | -122.3845 | 7.1944 | 7.2121 | 7.3578 | 7.2997 | -115.6419 | 0.038702 | 0.15562 | 0.19087 | 0.19722 | -122.6068
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0040921 | -0.011236 | 0.0073864 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017263 | 0.034972 | 0.011586 | 7.1571 | 7.1852 | 7.0055 | 7.0616 | 7.084 | 7.2342 | 6.8099 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.085587 | -0.1321 | 6.8694 | -115.3764 | 7.2166 | 7.065 | 0.19561 | -115.3541 | -115.2038 | -0.072588 | -122.5001 | 0.078871 | -0.001421 | 0.071167 | -122.3923 | -122.3525 | 7.1211 | 7.1435 | 7.2937 | 7.2447 | -115.6281 | -0.002495 | 0.10527 | 0.1451 | 0.14686 | -122.5701
|  |  |  | 1.4211e-13 | -0.034906 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.0022892 | -0.0048667 | -0.0027669 | 0.017263 | 0.035186 | 0.011373 | 7.1525 | 7.1669 | 6.9918 | 7.0571 | 7.0748 | 7.2296 | 6.8053 | 0.023941 | 0.078197 | -0.056351 | -0.071161 | 0.0366 | 0.085587 | -0.14125 | 6.9106 | -115.413 | 7.2578 | 7.0971 | 0.18645 | -115.3953 | -115.2405 | -0.035969 | -122.5413 | 0.12923 | 0.048935 | 0.084904 | -122.4335 | -122.3845 | 7.1623 | 7.1801 | 7.3349 | 7.2722 | -115.6648 | 0.034125 | 0.14189 | 0.19087 | 0.18348 | -122.6113
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0034509 | -0.011236 | 0.006959 | -0.01755 | -0.0048667 | -0.0025533 | 0.016835 | 0.035186 | 0.011159 | 7.1525 | 7.1578 | 6.9826 | 7.0387 | 7.0611 | 7.2159 | 6.7916 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.1321 | 6.8923 | -115.4497 | 7.2532 | 7.0833 | 0.19103 | -115.4273 | -115.2725 | -0.031389 | -122.5504 | 0.12465 | 0.039778 | 0.071167 | -122.4426 | -122.4074 | 7.1395 | 7.1618 | 7.3166 | 7.2585 | -115.6968 | 0.038704 | 0.14647 | 0.18172 | 0.18348 | -122.6205
|  |  |  | 1.4211e-13 | -0.035119 | -0.00049149 | -0.0036647 | -0.01145 | 0.0071726 | -0.02518 | -0.0046531 | -0.0025533 | 0.017263 | 0.035613 | 0.011373 | 7.125 | 7.1394 | 6.9735 | 7.0296 | 7.0473 | 7.2022 | 6.7733 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.045757 | 0.07643 | -0.1321 | 6.874 | -115.4268 | 7.2257 | 7.0742 | 0.20019 | -115.409 | -115.2542 | -0.031389 | -122.5184 | 0.12465 | 0.039778 | 0.071167 | -122.4106 | -122.3799 | 7.1303 | 7.148 | 7.3029 | 7.2402 | -115.6831 | 0.038704 | 0.14647 | 0.17714 | 0.17891 | -122.5885
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0036647 | -0.011023 | 0.0073864 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017049 | 0.035399 | 0.010945 | 7.1159 | 7.1257 | 6.9506 | 7.0113 | 7.0382 | 7.193 | 6.7641 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.07643 | -0.14125 | 6.8694 | -115.4451 | 7.2211 | 7.0559 | 0.18646 | -115.4182 | -115.2633 | -0.035969 | -122.5229 | 0.12465 | 0.044356 | 0.080325 | -122.406 | -122.3799 | 7.1166 | 7.1435 | 7.2983 | 7.231 | -115.6922 | 0.038704 | 0.15562 | 0.18172 | 0.18806 | -122.5976
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0067454 | -0.02518 | -0.0048667 | -0.0027669 | 0.017049 | 0.035399 | 0.011373 | 7.1021 | 7.1166 | 6.946 | 7.0067 | 7.029 | 7.1884 | 6.7504 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 6.8328 | -115.4497 | 7.1845 | 7.0284 | 0.19562 | -115.4274 | -115.2679 | -0.054279 | -122.5229 | 0.10176 | 0.021467 | 0.075746 | -122.406 | -122.3799 | 7.0891 | 7.1114 | 7.2708 | 7.199 | -115.706 | 0.015815 | 0.13273 | 0.15883 | 0.16517 | -122.593
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.0071726 | -0.0099192 | -0.0050803 | -0.0025533 | 0.017263 | 0.035399 | 0.011159 | 7.093 | 7.1028 | 6.946 | 7.0021 | 7.0153 | 7.1747 | 6.7458 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.045757 | 0.090166 | -0.13668 | 6.8557 | -115.4863 | 7.2028 | 7.0559 | 0.20019 | -115.4731 | -115.3137 | -0.026813 | -122.5596 | 0.1338 | 0.053512 | 0.080325 | -122.4426 | -122.3982 | 7.112 | 7.1251 | 7.2846 | 7.2127 | -115.7426 | 0.038702 | 0.15562 | 0.20003 | 0.19722 | -122.6251
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0034509 | -0.011236 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017476 | 0.035399 | 0.011159 | 7.0792 | 7.0937 | 6.9323 | 6.9884 | 6.9924 | 7.1564 | 6.7321 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 6.8282 | -115.5046 | 7.1754 | 7.0284 | 0.2002 | -115.5006 | -115.3366 | -0.040546 | -122.5596 | 0.12007 | 0.0352 | 0.075746 | -122.4472 | -122.4166 | 7.0845 | 7.0885 | 7.2525 | 7.1898 | -115.7609 | 0.029548 | 0.14189 | 0.17256 | 0.18806 | -122.6297
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017263 | 0.035399 | 0.011373 | 7.0655 | 7.0799 | 6.9048 | 6.9655 | 6.9878 | 7.1426 | 6.7229 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 6.8419 | -115.5092 | 7.1845 | 7.0238 | 0.18189 | -115.4869 | -115.332 | -0.017657 | -122.5413 | 0.14296 | 0.058089 | 0.075746 | -122.4289 | -122.3937 | 7.0845 | 7.1068 | 7.2617 | 7.1989 | -115.7518 | 0.052437 | 0.16478 | 0.20003 | 0.21095 | -122.6113
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.01769 | 0.035186 | 0.011586 | 7.0426 | 7.0479 | 6.8773 | 6.938 | 6.9649 | 7.1152 | 6.6909 | 0.014784 | 0.078197 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.14125 | 6.7641 | -115.4909 | 7.1159 | 6.9506 | 0.18647 | -115.464 | -115.3137 | -0.068013 | -122.4955 | 0.088026 | 0.007733 | 0.075746 | -122.3831 | -122.3479 | 7.0113 | 7.0381 | 7.1884 | 7.1211 | -115.738 | 0.00666 | 0.119 | 0.15425 | 0.15144 | -122.5701
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017476 | 0.035399 | 0.011373 | 7.0289 | 7.0433 | 6.8682 | 6.938 | 6.9512 | 7.106 | 6.6863 | 0.019362 | 0.091933 | -0.056351 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 6.7687 | -115.5046 | 7.1113 | 6.9506 | 0.18189 | -115.4915 | -115.3366 | -0.054279 | -122.5092 | 0.10176 | 0.026046 | 0.080325 | -122.3923 | -122.3616 | 7.0204 | 7.0336 | 7.1884 | 7.1257 | -115.7563 | 0.015815 | 0.13273 | 0.1634 | 0.17433 | -122.5793
|  |  |  | 1.4211e-13 | -0.034906 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0071726 | -0.01755 | -0.0046531 | -0.0023397 | 0.017476 | 0.035186 | 0.011373 | 7.0197 | 7.0341 | 6.859 | 6.9289 | 6.9374 | 7.0923 | 6.6817 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.085587 | -0.14125 | 6.7595 | -115.5595 | 7.0975 | 6.9368 | 0.17731 | -115.551 | -115.3961 | -0.063435 | -122.555 | 0.10176 | 0.01689 | 0.080325 | -122.4426 | -122.4028 | 7.0067 | 7.0152 | 7.1701 | 7.112 | -115.8067 | 0.011238 | 0.12358 | 0.16341 | 0.16517 | -122.6297
|  |  |  | 1.4211e-13 | -0.034692 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017049 | 0.035613 | 0.011373 | 7.006 | 7.0204 | 6.8453 | 6.906 | 6.9283 | 7.0831 | 6.6588 | 0.019362 | 0.087354 | -0.051772 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 6.7824 | -115.5733 | 7.1296 | 6.9689 | 0.18647 | -115.551 | -115.3961 | -0.01308 | -122.5458 | 0.14296 | 0.071824 | 0.084904 | -122.4335 | -122.4028 | 7.0296 | 7.0519 | 7.2067 | 7.144 | -115.8204 | 0.057014 | 0.16935 | 0.20003 | 0.21095 | -122.6159
|  |  |  | 1.4211e-13 | -0.034906 | -0.00049149 | -0.0036647 | -0.01145 | 0.006959 | -0.02518 | -0.0048667 | -0.0025533 | 0.017263 | 0.035186 | 0.011159 | 7.0014 | 7.0112 | 6.8407 | 6.906 | 6.9191 | 7.0694 | 6.6588 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.1321 | 6.7183 | -115.5641 | 7.0609 | 6.9002 | 0.18189 | -115.551 | -115.4007 | -0.072588 | -122.5367 | 0.088029 | -0.001421 | 0.071167 | -122.4198 | -122.3891 | 6.9655 | 6.9786 | 7.1289 | 7.0708 | -115.8113 | -0.007073 | 0.10984 | 0.14052 | 0.14686 | -122.6022
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0076 | -0.0099192 | -0.0042257 | -0.0025533 | 0.017263 | 0.035399 | 0.011159 | 6.9831 | 6.9929 | 6.8315 | 6.8785 | 6.8962 | 7.0648 | 6.6405 | 0.023941 | 0.096512 | -0.06093 | -0.062004 | 0.041178 | 0.07643 | -0.1321 | 6.732 | -115.6145 | 7.0746 | 6.9231 | 0.19105 | -115.5968 | -115.4282 | -0.040544 | -122.555 | 0.11549 | 0.030623 | 0.071167 | -122.4518 | -122.4166 | 6.9701 | 6.9878 | 7.1564 | 7.0845 | -115.8525 | 0.029549 | 0.13273 | 0.16798 | 0.18806 | -122.6251
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0036647 | -0.011023 | 0.0067454 | -0.01755 | -0.0048667 | -0.0027669 | 0.017263 | 0.035186 | 0.011159 | 6.9785 | 6.9884 | 6.8132 | 6.8739 | 6.8871 | 7.0511 | 6.6268 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.045757 | 0.07643 | -0.13668 | 6.6771 | -115.5641 | 7.0289 | 6.8636 | 0.18648 | -115.551 | -115.387 | -0.086322 | -122.5046 | 0.069716 | -0.015155 | 0.071167 | -122.3923 | -122.3616 | 6.9243 | 6.9374 | 7.1014 | 7.0387 | -115.8113 | -0.016228 | 0.096111 | 0.12678 | 0.13313 | -122.5747
|  |  |  | 1.4211e-13 | -0.035333 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.017049 | 0.035186 | 0.011159 | 6.9648 | 6.97 | 6.8041 | 6.8648 | 6.8871 | 7.0419 | 6.6313 | 0.014784 | 0.078197 | -0.065509 | -0.062004 | 0.045757 | 0.081008 | -0.13668 | 6.7 | -115.587 | 7.0334 | 6.8727 | 0.17274 | -115.5647 | -115.4099 | -0.068011 | -122.5138 | 0.083449 | 0.003156 | 0.071167 | -122.406 | -122.3708 | 6.9334 | 6.9557 | 7.1106 | 7.0387 | -115.8205 | 0.006661 | 0.11442 | 0.14967 | 0.14686 | -122.5885
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017049 | 0.035399 | 0.011373 | 6.951 | 6.97 | 6.8087 | 6.8602 | 6.8871 | 7.0419 | 6.6222 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.045757 | 0.081008 | -0.13668 | 6.7275 | -115.6145 | 7.0563 | 6.9139 | 0.18648 | -115.5876 | -115.4327 | -0.03139 | -122.5367 | 0.12923 | 0.048935 | 0.080325 | -122.4289 | -122.3937 | 6.9655 | 6.9923 | 7.1472 | 7.0753 | -115.8525 | 0.043282 | 0.15104 | 0.18629 | 0.19264 | -122.6113
|  |  |  | 1.4211e-13 | -0.034906 | -6.4092e-05 | -0.0038783 | -0.010809 | 0.0073864 | -0.0022892 | -0.0048667 | -0.0023397 | 0.017476 | 0.035186 | 0.010945 | 6.9465 | 6.9609 | 6.7949 | 6.8465 | 6.8779 | 7.0282 | 6.613 | 0.033099 | 0.087354 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.13668 | 6.7137 | -115.6603 | 7.0472 | 6.8956 | 0.1819 | -115.6288 | -115.4785 | -0.035968 | -122.5687 | 0.13381 | 0.039778 | 0.075746 | -122.4564 | -122.4211 | 6.9472 | 6.9786 | 7.1289 | 7.0616 | -115.8937 | 0.038704 | 0.15104 | 0.18629 | 0.18806 | -122.6434
|  |  |  | 1.4211e-13 | -0.035333 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017049 | 0.035186 | 0.011159 | 6.9281 | 6.9471 | 6.7812 | 6.8373 | 6.855 | 7.0236 | 6.5993 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.041178 | 0.081008 | -0.14125 | 6.6634 | -115.6099 | 6.9922 | 6.8453 | 0.1819 | -115.5922 | -115.4236 | -0.077168 | -122.5092 | 0.092607 | -0.001422 | 0.075746 | -122.406 | -122.3662 | 6.9014 | 6.9191 | 7.0877 | 7.0112 | -115.8479 | 0.002083 | 0.10526 | 0.1451 | 0.14686 | -122.5885
|  |  |  | 1.4211e-13 | -0.035333 | -0.00049149 | -0.0040921 | -0.011023 | 0.006959 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.035613 | 0.011373 | 6.9281 | 6.938 | 6.772 | 6.8327 | 6.855 | 7.0053 | 6.5947 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.050335 | 0.081008 | -0.13668 | 6.6496 | -115.5962 | 6.9831 | 6.827 | 0.17732 | -115.5739 | -115.4236 | -0.081744 | -122.5001 | 0.078873 | -0.010577 | 0.071167 | -122.3786 | -122.3479 | 6.8877 | 6.9099 | 7.0602 | 6.9929 | -115.8342 | -0.016229 | 0.10527 | 0.13594 | 0.14229 | -122.5656
|  |  |  | 1.4211e-13 | -0.035333 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0071726 | -0.02518 | -0.0044395 | -0.0025533 | 0.017263 | 0.035399 | 0.011373 | 6.9053 | 6.9243 | 6.7583 | 6.819 | 6.8413 | 6.9961 | 6.5855 | 0.019362 | 0.087354 | -0.056351 | -0.062004 | 0.050335 | 0.071851 | -0.1321 | 6.6817 | -115.6511 | 7.0014 | 6.8544 | 0.17275 | -115.6288 | -115.474 | -0.035967 | -122.5321 | 0.11549 | 0.039779 | 0.075746 | -122.4198 | -122.3982 | 6.9151 | 6.9374 | 7.0923 | 7.0204 | -115.8846 | 0.034126 | 0.14646 | 0.16798 | 0.18348 | -122.6022
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0029805 | 0.017476 | 0.03604 | 0.011159 | 6.9007 | 6.9197 | 6.7446 | 6.8098 | 6.8275 | 6.9778 | 6.5672 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.045757 | 0.081008 | -0.14125 | 6.6359 | -115.6282 | 6.9693 | 6.8132 | 0.17733 | -115.6105 | -115.4602 | -0.07259 | -122.5001 | 0.092606 | 0.003156 | 0.075746 | -122.3923 | -122.357 | 6.8785 | 6.8962 | 7.0465 | 6.9883 | -115.8708 | 0.006661 | 0.11442 | 0.14967 | 0.15144 | -122.5793
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0036647 | -0.011023 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017049 | 0.035613 | 0.010945 | 6.8915 | 6.9105 | 6.74 | 6.8007 | 6.823 | 6.9732 | 6.5626 | 0.023941 | 0.091933 | -0.065509 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 6.645 | -115.674 | 6.9739 | 6.8224 | 0.17733 | -115.6517 | -115.5014 | -0.054279 | -122.5413 | 0.10634 | 0.016888 | 0.071167 | -122.4243 | -122.3982 | 6.8831 | 6.9054 | 7.0556 | 6.9929 | -115.912 | 0.015815 | 0.13273 | 0.15883 | 0.17433 | -122.6113
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0040921 | -0.011023 | 0.0067454 | -0.01755 | -0.0046531 | -0.0025533 | 0.017263 | 0.035613 | 0.010945 | 6.8869 | 6.9014 | 6.74 | 6.7915 | 6.8138 | 6.9687 | 6.5581 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.085587 | -0.14583 | 6.645 | -115.7106 | 6.9739 | 6.827 | 0.18191 | -115.6883 | -115.5335 | -0.058858 | -122.5641 | 0.10634 | 0.026045 | 0.084903 | -122.4564 | -122.4165 | 6.8785 | 6.9008 | 7.0556 | 6.9883 | -115.9441 | 0.024971 | 0.13273 | 0.17256 | 0.17433 | -122.648
|  |  |  | 1.4211e-13 | -0.034692 | -0.00027769 | -0.0034509 | -0.011236 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0021259 | 0.016835 | 0.035399 | 0.011159 | 6.8824 | 6.8876 | 6.7262 | 6.7869 | 6.8001 | 6.9549 | 6.5489 | 0.019362 | 0.087354 | -0.065509 | -0.071161 | 0.045757 | 0.085587 | -0.1321 | 6.6267 | -115.674 | 6.9602 | 6.8041 | 0.17733 | -115.6609 | -115.506 | -0.054277 | -122.5321 | 0.097182 | 0.012311 | 0.066588 | -122.4152 | -122.3753 | 6.8648 | 6.8779 | 7.0327 | 6.9654 | -115.912 | 0.006659 | 0.12358 | 0.16341 | 0.16517 | -122.593
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0034509 | -0.011236 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017263 | 0.035186 | 0.011373 | 6.8686 | 6.8876 | 6.7125 | 6.7732 | 6.7955 | 6.9412 | 6.5398 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 6.6313 | -115.7198 | 6.9602 | 6.8041 | 0.17275 | -115.6975 | -115.5518 | -0.045123 | -122.5596 | 0.11549 | 0.030623 | 0.075746 | -122.4426 | -122.412 | 6.8648 | 6.887 | 7.0327 | 6.9792 | -115.9532 | 0.024971 | 0.14189 | 0.17256 | 0.17891 | -122.6297
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0040921 | -0.011023 | 0.006959 | -0.0099192 | -0.0044395 | -0.0023397 | 0.017263 | 0.035827 | 0.011373 | 6.8595 | 6.8693 | 6.6988 | 6.764 | 6.7863 | 6.9412 | 6.5352 | 0.019362 | 0.082776 | -0.056351 | -0.075739 | 0.041178 | 0.081008 | -0.13668 | 6.6313 | -115.7152 | 6.9556 | 6.7949 | 0.1636 | -115.6929 | -115.5381 | -0.040546 | -122.555 | 0.11549 | 0.039779 | 0.080325 | -122.4381 | -122.3982 | 6.8602 | 6.8825 | 7.0373 | 6.9654 | -115.9441 | 0.020391 | 0.13731 | 0.17714 | 0.17891 | -122.6159
|  |  |  | 1.4211e-13 | -0.035547 | -0.00049149 | -0.0036647 | -0.011236 | 0.006959 | -0.0022892 | -0.0048667 | -0.0027669 | 0.017049 | 0.035399 | 0.010945 | 6.8366 | 6.851 | 6.685 | 6.7457 | 6.7451 | 6.9229 | 6.5123 | 0.023941 | 0.091933 | -0.065509 | -0.062004 | 0.050335 | 0.07643 | -0.14125 | 6.5993 | -115.7198 | 6.9236 | 6.772 | 0.17276 | -115.7204 | -115.5426 | -0.05428 | -122.5275 | 0.11092 | 0.021466 | 0.075746 | -122.4152 | -122.3891 | 6.8327 | 6.8321 | 7.0099 | 6.938 | -115.9532 | 0.024971 | 0.13731 | 0.1634 | 0.17891 | -122.6068
|  |  |  | 1.4211e-13 | -0.035119 | 0.00014951 | -0.0036647 | -0.011236 | 0.0071726 | -0.02518 | -0.0046531 | -0.0027669 | 0.017263 | 0.035399 | 0.010945 | 6.8228 | 6.8327 | 6.6805 | 6.732 | 6.736 | 6.9091 | 6.5031 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.041178 | 0.081008 | -0.13668 | 6.613 | -115.7747 | 6.9327 | 6.7903 | 0.17734 | -115.7708 | -115.5976 | -0.026813 | -122.5733 | 0.1338 | 0.053512 | 0.080325 | -122.4655 | -122.4257 | 6.8419 | 6.8458 | 7.019 | 6.9425 | -116.0036 | 0.043281 | 0.15104 | 0.19087 | 0.19722 | -122.6434
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0038783 | -0.011023 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.017049 | 0.035613 | 0.011159 | 6.8137 | 6.8235 | 6.653 | 6.7228 | 6.7314 | 6.8954 | 6.4848 | 0.019362 | 0.087354 | -0.06093 | -0.066582 | 0.059493 | 0.07643 | -0.13668 | 6.5718 | -115.7427 | 6.9007 | 6.74 | 0.16818 | -115.7341 | -115.5701 | -0.049701 | -122.5321 | 0.10634 | 0.026045 | 0.075746 | -122.406 | -122.3891 | 6.8098 | 6.8184 | 6.9824 | 6.9105 | -115.9807 | 0.020393 | 0.14647 | 0.1634 | 0.17433 | -122.6022
|  |  |  | 1.4211e-13 | -0.035333 | -0.00049149 | -0.0040921 | -0.011023 | 0.0071726 | -0.01755 | -0.0046531 | -0.0027669 | 0.017263 | 0.035399 | 0.011159 | 6.7954 | 6.8098 | 6.6438 | 6.7045 | 6.7131 | 6.8817 | 6.4711 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.1321 | 6.5489 | -115.7473 | 6.8732 | 6.7217 | 0.17276 | -115.7387 | -115.5701 | -0.054277 | -122.5184 | 0.10176 | 0.01689 | 0.071167 | -122.3969 | -122.3662 | 6.7823 | 6.7909 | 6.9595 | 6.8876 | -115.9807 | 0.011238 | 0.13273 | 0.16341 | 0.1606 | -122.5839
|  |  |  | 1.4211e-13 | -0.034906 | -0.00027769 | -0.0036647 | -0.01145 | 0.0071726 | -0.02518 | -0.0048667 | -0.0027669 | 0.017049 | 0.035399 | 0.0118 | 6.7862 | 6.8098 | 6.6393 | 6.6908 | 6.7131 | 6.8725 | 6.4619 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.059493 | 0.081008 | -0.13668 | 6.5626 | -115.7839 | 6.8869 | 6.74 | 0.17734 | -115.7616 | -115.6022 | -0.035968 | -122.5413 | 0.12007 | 0.035199 | 0.071167 | -122.4152 | -122.3937 | 6.7915 | 6.8138 | 6.9732 | 6.9105 | -116.0128 | 0.034126 | 0.1602 | 0.18172 | 0.18806 | -122.6113
|  |  |  | 1.4211e-13 | -0.035333 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.006959 | -0.01755 | -0.0044395 | -0.0027669 | 0.016835 | 0.035399 | 0.011373 | 6.7816 | 6.7961 | 6.6255 | 6.6862 | 6.6947 | 6.8634 | 6.4573 | 0.023941 | 0.087354 | -0.070087 | -0.075739 | 0.045757 | 0.085587 | -0.13668 | 6.5214 | -115.7747 | 6.8457 | 6.6896 | 0.16819 | -115.7662 | -115.5976 | -0.072589 | -122.5367 | 0.088028 | -0.006 | 0.066589 | -122.4152 | -122.3753 | 6.7503 | 6.7588 | 6.9274 | 6.8601 | -116.0036 | -0.011652 | 0.10984 | 0.14967 | 0.15144 | -122.5976
|  |  |  | 1.4211e-13 | -0.034906 | -0.00049149 | -0.0038783 | -0.01145 | 0.0067454 | -0.0022892 | -0.0046531 | -0.0025533 | 0.016835 | 0.035827 | 0.010945 | 6.7679 | 6.7869 | 6.6255 | 6.6816 | 6.7039 | 6.8542 | 6.4528 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.050335 | 0.085587 | -0.13668 | 6.5077 | -115.7701 | 6.8228 | 6.6805 | 0.17277 | -115.7479 | -115.5976 | -0.081744 | -122.5229 | 0.074294 | -0.005998 | 0.075746 | -122.4014 | -122.3662 | 6.7366 | 6.7588 | 6.9091 | 6.8418 | -115.999 | -0.016229 | 0.10527 | 0.14052 | 0.13771 | -122.5885
|  |  |  | 1.4211e-13 | -0.035119 | 0.00014951 | -0.0038783 | -0.011236 | 0.0071726 | -0.01755 | -0.0046531 | -0.0023397 | 0.017049 | 0.035613 | 0.011159 | 6.7587 | 6.7777 | 6.6164 | 6.6679 | 6.6902 | 6.845 | 6.4436 | 0.023941 | 0.078197 | -0.056351 | -0.071161 | 0.045757 | 0.07643 | -0.13668 | 6.5123 | -115.8159 | 6.8274 | 6.685 | 0.17277 | -115.7937 | -115.6388 | -0.068011 | -122.555 | 0.092606 | 0.012314 | 0.080325 | -122.4381 | -122.4074 | 6.7366 | 6.7588 | 6.9137 | 6.8464 | -116.0402 | -0.002496 | 0.11442 | 0.1451 | 0.14686 | -122.6205
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0032373 | -0.01145 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017263 | 0.035186 | 0.010945 | 6.7496 | 6.7732 | 6.6026 | 6.6679 | 6.681 | 6.8405 | 6.4344 | 0.02852 | 0.087354 | -0.056351 | -0.071161 | 0.045757 | 0.081008 | -0.14125 | 6.5489 | -115.8297 | 6.864 | 6.7171 | 0.16819 | -115.8165 | -115.6571 | -0.026814 | -122.5687 | 0.14296 | 0.05809 | 0.084904 | -122.4518 | -122.4166 | 6.7823 | 6.7955 | 6.9549 | 6.8876 | -116.0631 | 0.04328 | 0.1602 | 0.19545 | 0.2018 | -122.6388
|  |  |  | 1.4211e-13 | -0.035333 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017263 | 0.035827 | 0.010945 | 6.745 | 6.7732 | 6.5935 | 6.6587 | 6.6719 | 6.8267 | 6.4299 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.13668 | 6.5351 | -115.848 | 6.8503 | 6.6988 | 0.16361 | -115.8349 | -115.68 | -0.03139 | -122.5733 | 0.12923 | 0.039777 | 0.071167 | -122.4564 | -122.4211 | 6.764 | 6.7771 | 6.932 | 6.8784 | -116.0769 | 0.038704 | 0.15562 | 0.19087 | 0.19264 | -122.6434
|  |  |  | 1.4211e-13 | -0.035119 | 0.00014951 | -0.0036647 | -0.011023 | 0.006959 | -0.01755 | -0.0042257 | -0.0025533 | 0.017049 | 0.035399 | 0.011159 | 6.745 | 6.7503 | 6.5889 | 6.6542 | 6.6719 | 6.8221 | 6.4161 | 0.019362 | 0.082776 | -0.06093 | -0.071161 | 0.054914 | 0.085587 | -0.13668 | 6.4665 | -115.8251 | 6.7954 | 6.6392 | 0.17277 | -115.8074 | -115.6571 | -0.086322 | -122.5504 | 0.069716 | -0.010576 | 0.075746 | -122.4243 | -122.3937 | 6.7045 | 6.7222 | 6.8725 | 6.8006 | -116.0631 | -0.020807 | 0.10527 | 0.13594 | 0.13313 | -122.6159
|  |  |  | 1.4211e-13 | -0.034906 | 0.00014951 | -0.0036647 | -0.01145 | 0.0073864 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017049 | 0.035613 | 0.010945 | 6.7221 | 6.7411 | 6.5614 | 6.6313 | 6.649 | 6.8084 | 6.4024 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.054914 | 0.081008 | -0.14583 | 6.4894 | -115.8434 | 6.8091 | 6.6484 | 0.15904 | -115.8257 | -115.6663 | -0.058858 | -122.5458 | 0.1155 | 0.026045 | 0.084903 | -122.4198 | -122.3937 | 6.7182 | 6.7359 | 6.8954 | 6.8281 | -116.0723 | 0.015814 | 0.14189 | 0.16798 | 0.16975 | -122.6205
|  |  |  | 1.4211e-13 | -0.034906 | 0.00014951 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0048667 | -0.0023397 | 0.016835 | 0.035186 | 0.011373 | 6.7175 | 6.732 | 6.566 | 6.6221 | 6.6444 | 6.8038 | 6.4024 | 0.02852 | 0.082776 | -0.056351 | -0.066582 | 0.045757 | 0.081008 | -0.14583 | 6.471 | -115.848 | 6.7862 | 6.6347 | 0.16362 | -115.8257 | -115.6663 | -0.077168 | -122.5367 | 0.097185 | 0.012314 | 0.089482 | -122.4243 | -122.3891 | 6.6908 | 6.713 | 6.8725 | 6.8006 | -116.0677 | 0.002083 | 0.11442 | 0.14967 | 0.15144 | -122.6159
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0038783 | -0.010809 | 0.006959 | -0.0022892 | -0.0044395 | -0.0027669 | 0.017049 | 0.035399 | 0.011159 | 6.7038 | 6.7228 | 6.5523 | 6.6038 | 6.6306 | 6.7855 | 6.3749 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.059493 | 0.07643 | -0.13668 | 6.4344 | -115.8892 | 6.7633 | 6.6118 | 0.17736 | -115.8623 | -115.7075 | -0.077167 | -122.5641 | 0.08345 | -0.001421 | 0.075746 | -122.4335 | -122.4166 | 6.6633 | 6.6902 | 6.845 | 6.7823 | -116.1181 | -0.011652 | 0.119 | 0.13594 | 0.14686 | -122.6297
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0034509 | -0.01145 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.016835 | 0.035613 | 0.011159 | 6.6947 | 6.7091 | 6.5385 | 6.5992 | 6.6077 | 6.7764 | 6.3703 | 0.014784 | 0.082776 | -0.056351 | -0.062004 | 0.045757 | 0.081008 | -0.14125 | 6.471 | -115.9166 | 6.7954 | 6.6392 | 0.1682 | -115.9081 | -115.7395 | -0.040547 | -122.5779 | 0.11549 | 0.044357 | 0.084904 | -122.4701 | -122.4349 | 6.6999 | 6.7085 | 6.8771 | 6.8098 | -116.1455 | 0.038704 | 0.14647 | 0.18172 | 0.18348 | -122.6571
|  |  |  | 1.4211e-13 | -0.035119 | -0.00027769 | -0.0038783 | -0.011023 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017049 | 0.035613 | 0.011159 | 6.6809 | 6.6907 | 6.5294 | 6.5855 | 6.6077 | 6.7672 | 6.3658 | 0.019362 | 0.078197 | -0.056351 | -0.066582 | 0.050335 | 0.085587 | -0.14125 | 6.4848 | -115.9166 | 6.7999 | 6.6484 | 0.16362 | -115.8944 | -115.7349 | -0.022236 | -122.5687 | 0.13838 | 0.062668 | 0.084904 | -122.4518 | -122.4165 | 6.7045 | 6.7268 | 6.8862 | 6.8098 | -116.1364 | 0.052437 | 0.16935 | 0.20461 | 0.19722 | -122.6434
|  |  |  | 1.4211e-13 | -0.035547 | -0.00027769 | -0.0034509 | -0.011236 | 0.0067454 | -0.0022892 | -0.0048667 | -0.0023397 | 0.016622 | 0.035399 | 0.010945 | 6.6718 | 6.6907 | 6.5248 | 6.5855 | 6.5986 | 6.758 | 6.3566 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 6.4253 | -115.8983 | 6.7404 | 6.5935 | 0.1682 | -115.8852 | -115.7258 | -0.068011 | -122.5504 | 0.092606 | 0.007735 | 0.075746 | -122.4381 | -122.4028 | 6.6542 | 6.6673 | 6.8267 | 6.7594 | -116.1272 | 0.002083 | 0.11442 | 0.14967 | 0.15602 | -122.6205
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0034509 | -0.01145 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017263 | 0.035399 | 0.011159 | 6.6672 | 6.677 | 6.5065 | 6.5763 | 6.5894 | 6.7397 | 6.3429 | 0.023941 | 0.091933 | -0.06093 | -0.066582 | 0.050335 | 0.085587 | -0.1321 | 6.4253 | -115.9029 | 6.7496 | 6.5889 | 0.16363 | -115.8898 | -115.7395 | -0.0497 | -122.5458 | 0.10634 | 0.021467 | 0.071167 | -122.4289 | -122.3937 | 6.6587 | 6.6718 | 6.8221 | 6.7594 | -116.1364 | 0.015815 | 0.13273 | 0.16798 | 0.17433 | -122.6113
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0036647 | -0.011236 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017049 | 0.035827 | 0.010945 | 6.6489 | 6.6724 | 6.5019 | 6.558 | 6.5757 | 6.7352 | 6.3383 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.085587 | -0.13668 | 6.4665 | -115.9533 | 6.777 | 6.6301 | 0.16363 | -115.9356 | -115.7761 | -0.008502 | -122.5779 | 0.15212 | 0.067244 | 0.075746 | -122.461 | -122.4257 | 6.6862 | 6.7039 | 6.8633 | 6.8006 | -116.173 | 0.061592 | 0.17851 | 0.21376 | 0.21553 | -122.648
|  |  |  | 1.4211e-13 | -0.035119 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.006959 | -0.0099192 | -0.0046531 | -0.0023397 | 0.017049 | 0.035399 | 0.010945 | 6.6397 | 6.6587 | 6.479 | 6.5534 | 6.562 | 6.7168 | 6.3291 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.14125 | 6.4298 | -115.9487 | 6.7404 | 6.5797 | 0.14989 | -115.9402 | -115.7853 | -0.040547 | -122.5641 | 0.12465 | 0.039778 | 0.080325 | -122.4472 | -122.4165 | 6.6541 | 6.6627 | 6.8175 | 6.7594 | -116.173 | 0.038704 | 0.15562 | 0.18629 | 0.18806 | -122.6434
|  |  |  | 1.4211e-13 | -0.035547 | -0.00027769 | -0.0038783 | -0.01145 | 0.006959 | -0.0022892 | -0.0046531 | -0.0021259 | 0.017049 | 0.035827 | 0.011159 | 6.6306 | 6.6404 | 6.4744 | 6.5351 | 6.5482 | 6.7123 | 6.3154 | 0.02852 | 0.082776 | -0.056351 | -0.062004 | 0.054914 | 0.081008 | -0.1321 | 6.4436 | -115.9945 | 6.7587 | 6.6026 | 0.15905 | -115.9814 | -115.8173 | -0.003923 | -122.5916 | 0.15669 | 0.071823 | 0.075746 | -122.4747 | -122.4486 | 6.6633 | 6.6764 | 6.8404 | 6.7686 | -116.2142 | 0.06617 | 0.18309 | 0.20918 | 0.21095 | -122.6617
|  |  |  | 1.4211e-13 | -0.035547 | -0.00027769 | -0.0034509 | -0.011236 | 0.0071726 | -0.0099192 | -0.0052939 | -0.0027669 | 0.017263 | 0.035613 | 0.011159 | 6.6122 | 6.6266 | 6.4607 | 6.5351 | 6.5528 | 6.7031 | 6.3062 | 0.014784 | 0.087354 | -0.06093 | -0.071161 | 0.054914 | 0.085587 | -0.13668 | 6.3932 | -115.9762 | 6.6992 | 6.5477 | 0.15447 | -115.9585 | -115.8082 | -0.049701 | -122.5825 | 0.10176 | 0.026045 | 0.075746 | -122.4564 | -122.4257 | 6.6221 | 6.6398 | 6.7901 | 6.7136 | -116.2051 | 0.015814 | 0.14189 | 0.17256 | 0.17433 | -122.648
|  |  |  | 1.4211e-13 | -0.035333 | -0.00049149 | -0.0038783 | -0.011664 | 0.0071726 | -0.01755 | -0.0050803 | -0.0023397 | 0.016835 | 0.035613 | 0.010945 | 6.6122 | 6.6266 | 6.4607 | 6.5214 | 6.5345 | 6.6939 | 6.2925 | 0.02852 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.085587 | -0.14125 | 6.3978 | -115.9579 | 6.7175 | 6.566 | 0.16821 | -115.9448 | -115.7853 | -0.035969 | -122.5413 | 0.13381 | 0.044356 | 0.080325 | -122.4335 | -122.3937 | 6.6267 | 6.6398 | 6.7992 | 6.7319 | -116.1868 | 0.043282 | 0.15104 | 0.19087 | 0.19264 | -122.6205
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0025533 | 0.017049 | 0.035399 | 0.010945 | 6.6077 | 6.6175 | 6.4424 | 6.5122 | 6.5345 | 6.6894 | 6.2925 | 0.033099 | 0.082776 | -0.06093 | -0.071161 | 0.050335 | 0.07643 | -0.14583 | 6.3795 | -115.9716 | 6.6946 | 6.5294 | 0.1499 | -115.9493 | -115.7945 | -0.058858 | -122.555 | 0.12007 | 0.026045 | 0.084903 | -122.4335 | -122.4074 | 6.5992 | 6.6215 | 6.7763 | 6.7045 | -116.1913 | 0.015814 | 0.13731 | 0.1634 | 0.16975 | -122.6297
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0038783 | -0.01145 | 0.0071726 | -0.0099192 | -0.0044395 | -0.0025533 | 0.017263 | 0.035613 | 0.011373 | 6.5848 | 6.5946 | 6.4332 | 6.4939 | 6.4933 | 6.6756 | 6.2742 | 0.023941 | 0.078197 | -0.056351 | -0.071161 | 0.045757 | 0.07643 | -0.13668 | 6.3749 | -116.0357 | 6.6855 | 6.5339 | 0.15906 | -116.0363 | -115.854 | -0.035968 | -122.6008 | 0.12465 | 0.044357 | 0.080325 | -122.4838 | -122.4532 | 6.5946 | 6.594 | 6.7763 | 6.6953 | -116.2554 | 0.029547 | 0.14647 | 0.17714 | 0.17891 | -122.6663
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0036647 | -0.011236 | 0.006959 | -0.01755 | -0.0048667 | -0.0027669 | 0.016622 | 0.035613 | 0.011159 | 6.5848 | 6.5946 | 6.4332 | 6.4939 | 6.5116 | 6.6665 | 6.2604 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 6.3199 | -115.9624 | 6.6443 | 6.4927 | 0.17279 | -115.9448 | -115.7899 | -0.081746 | -122.5229 | 0.08345 | -0.001421 | 0.080325 | -122.4014 | -122.3754 | 6.5534 | 6.5711 | 6.726 | 6.6541 | -116.1959 | -0.007073 | 0.11442 | 0.14052 | 0.14228 | -122.5976
|  |  |  | 1.4211e-13 | -0.035333 | -0.00049149 | -0.0038783 | -0.011236 | 0.006959 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016835 | 0.035613 | 0.011159 | 6.5665 | 6.5854 | 6.4103 | 6.4802 | 6.5024 | 6.6665 | 6.2604 | 0.023941 | 0.073618 | -0.06093 | -0.062004 | 0.045757 | 0.090166 | -0.14583 | 6.384 | -116.0357 | 6.6901 | 6.5339 | 0.1499 | -116.0134 | -115.8494 | -0.022237 | -122.5779 | 0.14754 | 0.062666 | 0.084903 | -122.4701 | -122.4257 | 6.6038 | 6.626 | 6.7901 | 6.709 | -116.2554 | 0.061592 | 0.16935 | 0.21376 | 0.19721 | -122.6617
|  |  |  | 1.4211e-13 | -0.035547 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.0071726 | -0.02518 | -0.0046531 | -0.0023397 | 0.017263 | 0.035613 | 0.010945 | 6.5619 | 6.5809 | 6.4149 | 6.471 | 6.4933 | 6.6482 | 6.2559 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.045757 | 0.081008 | -0.13668 | 6.3566 | -116.0357 | 6.6626 | 6.5156 | 0.15906 | -116.0134 | -115.8586 | -0.035968 | -122.5687 | 0.12465 | 0.044357 | 0.080325 | -122.461 | -122.4257 | 6.5717 | 6.594 | 6.7489 | 6.6816 | -116.2509 | 0.038704 | 0.14647 | 0.18172 | 0.18806 | -122.6434
|  |  |  | 1.4211e-13 | -0.035333 | -0.00027769 | -0.0036647 | -0.01145 | 0.006959 | -0.01755 | -0.0048667 | -0.0027669 | 0.017049 | 0.035613 | 0.010945 | 6.5573 | 6.5671 | 6.4103 | 6.4619 | 6.4795 | 6.6482 | 6.2513 | 0.02852 | 0.096512 | -0.065509 | -0.066582 | 0.045757 | 0.081008 | -0.1321 | 6.3474 | -116.0677 | 6.6534 | 6.5065 | 0.15906 | -116.0501 | -115.8814 | -0.035967 | -122.5962 | 0.12465 | 0.030621 | 0.066588 | -122.4838 | -122.4486 | 6.558 | 6.5757 | 6.7443 | 6.6633 | -116.2783 | 0.029548 | 0.14189 | 0.17714 | 0.19264 | -122.6617
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.0067454 | -0.01755 | -0.0048667 | -0.0027669 | 0.016835 | 0.035613 | 0.010945 | 6.5436 | 6.5488 | 6.4012 | 6.4619 | 6.4658 | 6.6344 | 6.233 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.085587 | -0.14125 | 6.3383 | -116.0586 | 6.6489 | 6.5065 | 0.16822 | -116.0546 | -115.886 | -0.035969 | -122.587 | 0.12923 | 0.044356 | 0.080325 | -122.4747 | -122.4349 | 6.5672 | 6.5711 | 6.7397 | 6.6541 | -116.2875 | 0.038704 | 0.15104 | 0.19087 | 0.18806 | -122.6617
|  |  |  | 1.4211e-13 | -0.035333 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.0071726 | -0.0022892 | -0.0046531 | -0.0029805 | 0.016835 | 0.035827 | 0.010732 | 6.5481 | 6.5488 | 6.3829 | 6.4436 | 6.4521 | 6.6207 | 6.2192 | 0.014784 | 0.082776 | -0.065509 | -0.062004 | 0.045757 | 0.085587 | -0.1321 | 6.3154 | -116.0769 | 6.6443 | 6.479 | 0.16364 | -116.0684 | -115.8998 | -0.035967 | -122.5825 | 0.11091 | 0.030621 | 0.066588 | -122.4747 | -122.4349 | 6.5397 | 6.5482 | 6.7168 | 6.6449 | -116.3012 | 0.034126 | 0.14189 | 0.18172 | 0.17891 | -122.6525
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0071726 | -0.01755 | -0.0046531 | -0.0025533 | 0.017049 | 0.035827 | 0.010945 | 6.5298 | 6.5351 | 6.3783 | 6.4481 | 6.4292 | 6.6115 | 6.2146 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.054914 | 0.090166 | -0.13668 | 6.3337 | -116.0586 | 6.6488 | 6.4973 | 0.16364 | -116.0775 | -115.8952 | -0.017657 | -122.5779 | 0.14296 | 0.05351 | 0.071167 | -122.4518 | -122.4165 | 6.5672 | 6.5482 | 6.7306 | 6.6541 | -116.2921 | 0.047858 | 0.17393 | 0.20919 | 0.20637 | -122.6434
|  |  |  | 1.4211e-13 | -0.035547 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.006959 | 0.0053413 | -0.0046531 | -0.0027669 | 0.016835 | 0.035827 | 0.010945 | 6.5207 | 6.5259 | 6.3691 | 6.4298 | 6.4246 | 6.607 | 6.2055 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.14125 | 6.2787 | -116.0677 | 6.5939 | 6.4424 | 0.16364 | -116.073 | -115.8906 | -0.068013 | -122.5596 | 0.097183 | 0.012312 | 0.080325 | -122.4426 | -122.412 | 6.5031 | 6.4978 | 6.6802 | 6.5992 | -116.2921 | 0.011238 | 0.12816 | 0.15883 | 0.15602 | -122.6388
|  |  |  | 1.4211e-13 | -0.035333 | 0.00014951 | -0.0038783 | -0.011023 | 0.0067454 | -0.01755 | -0.0044395 | -0.0021259 | 0.017049 | 0.035613 | 0.011373 | 6.5207 | 6.5213 | 6.36 | 6.4298 | 6.4337 | 6.5932 | 6.2055 | 0.019362 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.13668 | 6.3199 | -116.1135 | 6.6351 | 6.4744 | 0.15449 | -116.1096 | -115.9501 | -0.022235 | -122.6145 | 0.1338 | 0.053511 | 0.075746 | -122.4976 | -122.4623 | 6.5443 | 6.5482 | 6.7077 | 6.6358 | -116.3378 | 0.04328 | 0.1602 | 0.19545 | 0.2018 | -122.68
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.02518 | -0.0046531 | -0.0027669 | 0.017049 | 0.035827 | 0.011159 | 6.5115 | 6.5168 | 6.36 | 6.4298 | 6.4292 | 6.5978 | 6.2009 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 6.2604 | -116.0723 | 6.571 | 6.4195 | 0.15907 | -116.073 | -115.9043 | -0.081746 | -122.5687 | 0.08345 | 0.003158 | 0.084904 | -122.4518 | -122.4211 | 6.4893 | 6.4887 | 6.6573 | 6.5763 | -116.3012 | -0.007073 | 0.10984 | 0.14052 | 0.14228 | -122.6434
|  |  |  | 1.4211e-13 | -0.035547 | -0.00027769 | -0.0038783 | -0.011023 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0021259 | 0.017049 | 0.035827 | 0.010945 | 6.4886 | 6.5076 | 6.3371 | 6.4024 | 6.4063 | 6.5795 | 6.1872 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 6.3016 | -116.1318 | 6.6031 | 6.4515 | 0.14991 | -116.1279 | -115.9547 | -0.026814 | -122.6008 | 0.13838 | 0.053511 | 0.080325 | -122.4838 | -122.4532 | 6.5168 | 6.5207 | 6.6939 | 6.622 | -116.347 | 0.047859 | 0.16478 | 0.19545 | 0.2018 | -122.6754
|  |  |  | 1.4211e-13 | -0.035547 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016835 | 0.035827 | 0.010945 | 6.4886 | 6.4984 | 6.3279 | 6.3978 | 6.4154 | 6.5657 | 6.178 | 0.033099 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.13668 | 6.2833 | -116.1318 | 6.5939 | 6.4332 | 0.14991 | -116.1142 | -115.9639 | -0.03139 | -122.5916 | 0.13839 | 0.044356 | 0.075746 | -122.4747 | -122.444 | 6.5031 | 6.5207 | 6.671 | 6.6037 | -116.3516 | 0.043282 | 0.1602 | 0.19087 | 0.18806 | -122.6663
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0034509 | -0.01145 | 0.0071726 | -0.01755 | -0.0046531 | -0.0027669 | 0.017049 | 0.03604 | 0.011159 | 6.4703 | 6.4939 | 6.3234 | 6.384 | 6.4063 | 6.5612 | 6.1689 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.14125 | 6.2192 | -116.1181 | 6.5207 | 6.3737 | 0.15449 | -116.0959 | -115.941 | -0.090901 | -122.5641 | 0.069716 | -0.010576 | 0.080325 | -122.4564 | -122.4211 | 6.4344 | 6.4566 | 6.6115 | 6.5442 | -116.3333 | -0.01165 | 0.096111 | 0.13136 | 0.12855 | -122.6434
|  |  |  | 1.4211e-13 | -0.035974 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.035613 | 0.010732 | 6.4612 | 6.4801 | 6.305 | 6.384 | 6.3834 | 6.5474 | 6.1551 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 6.2467 | -116.1456 | 6.5527 | 6.3966 | 0.14992 | -116.1462 | -115.9822 | -0.045123 | -122.5962 | 0.12007 | 0.030623 | 0.075746 | -122.4838 | -122.4486 | 6.4756 | 6.4749 | 6.639 | 6.5717 | -116.3745 | 0.024971 | 0.13731 | 0.17256 | 0.17433 | -122.6663
|  |  |  | 1.4211e-13 | -0.035547 | -6.4092e-05 | -0.0038783 | -0.011664 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017049 | 0.035399 | 0.011159 | 6.4978 | 6.5076 | 6.3417 | 6.4115 | 6.42 | 6.5886 | 6.1872 | 0.02852 | 0.078197 | -0.065509 | -0.071161 | 0.050335 | 0.085587 | -0.14125 | 6.2467 | -116.0998 | 6.5573 | 6.4012 | 0.15449 | -116.0913 | -115.9227 | -0.081746 | -122.5825 | 0.088029 | -0.006 | 0.075746 | -122.461 | -122.4257 | 6.471 | 6.4795 | 6.6481 | 6.5671 | -116.3241 | -0.011652 | 0.10984 | 0.1451 | 0.13771 | -122.6525
|  |  |  | 1.4211e-13 | -0.03576 | -0.00027769 | -0.0034509 | -0.01145 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017049 | 0.035613 | 0.010945 | 6.5024 | 6.5168 | 6.3462 | 6.4115 | 6.4246 | 6.5841 | 6.1918 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.085587 | -0.13668 | 6.3062 | -116.1227 | 6.6168 | 6.4607 | 0.15449 | -116.1096 | -115.9501 | -0.022235 | -122.6008 | 0.13838 | 0.053511 | 0.075746 | -122.4838 | -122.4486 | 6.5259 | 6.539 | 6.6985 | 6.6312 | -116.3424 | 0.047859 | 0.16478 | 0.20003 | 0.19722 | -122.6709
|  |  |  | 1.4211e-13 | -0.03576 | -0.00049149 | -0.0034509 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016835 | 0.035399 | 0.010945 | 6.4932 | 6.5076 | 6.3462 | 6.4024 | 6.4154 | 6.5749 | 6.1826 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.1321 | 6.2833 | -116.1364 | 6.5939 | 6.447 | 0.16365 | -116.1233 | -115.9639 | -0.031389 | -122.6053 | 0.12465 | 0.039778 | 0.071167 | -122.493 | -122.4623 | 6.5031 | 6.5161 | 6.6756 | 6.6083 | -116.3562 | 0.034126 | 0.14647 | 0.17714 | 0.18348 | -122.6709
|  |  |  | 1.4211e-13 | -0.035547 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.01755 | -0.0046531 | -0.0023397 | 0.017049 | 0.035827 | 0.010945 | 6.4291 | 6.4435 | 6.2776 | 6.3428 | 6.3376 | 6.52 | 6.1231 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.045757 | 0.07643 | -0.14125 | 6.2238 | -116.2005 | 6.5298 | 6.3783 | 0.1545 | -116.2057 | -116.0234 | -0.040547 | -122.6099 | 0.12465 | 0.035199 | 0.075746 | -122.4976 | -122.4669 | 6.4435 | 6.4383 | 6.6207 | 6.5442 | -116.4203 | 0.034126 | 0.14647 | 0.17714 | 0.18806 | -122.6846
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0032373 | -0.011236 | 0.006959 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017263 | 0.035399 | 0.010945 | 6.4154 | 6.4343 | 6.2684 | 6.3383 | 6.3467 | 6.5016 | 6.1139 | 0.014784 | 0.087354 | -0.065509 | -0.062004 | 0.045757 | 0.085587 | -0.14125 | 6.2238 | -116.1959 | 6.5252 | 6.3783 | 0.1545 | -116.1874 | -116.0325 | -0.031392 | -122.5962 | 0.12465 | 0.044354 | 0.075746 | -122.4884 | -122.4486 | 6.4481 | 6.4566 | 6.6115 | 6.5442 | -116.4203 | 0.047859 | 0.15562 | 0.19545 | 0.19722 | -122.6754
|  |  |  | 1.4211e-13 | -0.03576 | -0.00027769 | -0.0034509 | -0.011236 | 0.006959 | -0.0099192 | -0.0050803 | -0.0023397 | 0.016835 | 0.03604 | 0.010945 | 6.4108 | 6.4252 | 6.2593 | 6.3291 | 6.3422 | 6.4971 | 6.1002 | 0.02852 | 0.087354 | -0.065509 | -0.071161 | 0.059493 | 0.07643 | -0.14125 | 6.178 | -116.1776 | 6.4886 | 6.3371 | 0.15908 | -116.1645 | -116.0096 | -0.063435 | -122.5779 | 0.10634 | 0.012311 | 0.075746 | -122.4472 | -122.4303 | 6.4069 | 6.42 | 6.5749 | 6.503 | -116.4065 | 0.006659 | 0.13731 | 0.15425 | 0.16517 | -122.648
|  |  |  | 1.4211e-13 | -0.03576 | 0.00014951 | -0.0034509 | -0.011236 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.035827 | 0.010945 | 6.4016 | 6.416 | 6.2501 | 6.3245 | 6.3101 | 6.4925 | 6.1002 | 0.019362 | 0.096512 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14125 | 6.1643 | -116.1868 | 6.4657 | 6.3142 | 0.14992 | -116.2012 | -116.0188 | -0.077168 | -122.5733 | 0.083449 | 0.003157 | 0.080325 | -122.461 | -122.4257 | 6.3886 | 6.3742 | 6.5566 | 6.4801 | -116.4111 | 0.002083 | 0.11442 | 0.14967 | 0.1606 | -122.6525
|  |  |  | 1.4211e-13 | -0.035547 | 0.00014951 | -0.0040921 | -0.01145 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016622 | 0.035613 | 0.010945 | 6.3971 | 6.4069 | 6.2409 | 6.3108 | 6.3193 | 6.4833 | 6.0864 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.045757 | 0.085587 | -0.13668 | 6.178 | -116.2051 | 6.4886 | 6.3325 | 0.15451 | -116.1966 | -116.0325 | -0.045123 | -122.5825 | 0.11549 | 0.035202 | 0.080325 | -122.4701 | -122.4303 | 6.4023 | 6.4108 | 6.5749 | 6.4984 | -116.4294 | 0.024971 | 0.13731 | 0.17714 | 0.17891 | -122.6525
|  |  |  | 1.4211e-13 | -0.03576 | -0.00027769 | -0.0034509 | -0.01145 | 0.006959 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016835 | 0.035827 | 0.010732 | 6.3833 | 6.4069 | 6.2364 | 6.3016 | 6.3055 | 6.4742 | 6.0727 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.059493 | 0.085587 | -0.13668 | 6.1871 | -116.228 | 6.4978 | 6.3508 | 0.16366 | -116.2241 | -116.0554 | -0.022235 | -122.5962 | 0.13838 | 0.05809 | 0.080325 | -122.4701 | -122.444 | 6.4161 | 6.42 | 6.5886 | 6.5213 | -116.4569 | 0.047859 | 0.17393 | 0.20003 | 0.19264 | -122.6663
|  |  |  | 1.4211e-13 | -0.03576 | -0.00049149 | -0.0038783 | -0.01145 | 0.006959 | -0.01755 | -0.0048667 | -0.0023397 | 0.017049 | 0.035399 | 0.010945 | 6.365 | 6.3886 | 6.2226 | 6.2879 | 6.2918 | 6.465 | 6.0773 | 0.023941 | 0.078197 | -0.065509 | -0.071161 | 0.054914 | 0.081008 | -0.14125 | 6.178 | -116.2463 | 6.4657 | 6.3233 | 0.14535 | -116.2424 | -116.0692 | -0.040547 | -122.6053 | 0.12465 | 0.035199 | 0.075746 | -122.4793 | -122.4532 | 6.3886 | 6.3925 | 6.5657 | 6.4893 | -116.4569 | 0.029547 | 0.15562 | 0.18172 | 0.17891 | -122.6754
|  |  |  | 1.4211e-13 | -0.03576 | -0.00027769 | -0.0038783 | -0.011236 | 0.0073864 | -0.0099192 | -0.0044395 | -0.0023397 | 0.016622 | 0.035827 | 0.011159 | 4.8312 | 4.873 | 4.721 | 4.7679 | 4.7808 | 4.9495 | 4.5891 | 0.014784 | 0.087354 | -0.056351 | -0.062004 | 0.059493 | 0.090166 | -0.13668 | 4.6624 | -117.7297 | 4.9045 | 4.7942 | 0.13182 | -117.7168 | -117.5481 | -0.063434 | -122.5596 | 0.088026 | 0.016891 | 0.080325 | -122.4381 | -122.4074 | 4.8411 | 4.854 | 5.0227 | 4.9463 | -117.9084 | 0.011238 | 0.13273 | 0.16341 | 0.1606 | -122.6342
|  |  |  | 1.4211e-13 | -0.03576 | 0.00014951 | -0.0036647 | -0.011236 | 0.0067454 | -0.01755 | -0.0048667 | -0.0027669 | 0.016835 | 0.03604 | 0.010732 | 4.8175 | 4.8639 | 4.7118 | 4.7496 | 4.7487 | 4.9403 | 4.5662 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.059493 | 0.085587 | -0.14125 | 4.6303 | -117.7388 | 4.8816 | 4.7759 | 0.14556 | -117.7397 | -117.5481 | -0.077168 | -122.555 | 0.092607 | 0.003157 | 0.080325 | -122.4289 | -122.4028 | 4.8136 | 4.8128 | 5.0044 | 4.928 | -117.9222 | -0.002495 | 0.12358 | 0.14967 | 0.14686 | -122.6297
|  |  |  | 1.4211e-13 | -0.035974 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.01755 | -0.0048667 | -0.0027669 | 0.016835 | 0.03604 | 0.010732 | 4.8038 | 4.8501 | 4.7072 | 4.7496 | 4.7441 | 4.9266 | 4.5662 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.14583 | 4.6715 | -117.7755 | 4.9091 | 4.8125 | 0.14099 | -117.7809 | -117.5984 | -0.040547 | -122.5916 | 0.12923 | 0.044356 | 0.084903 | -122.4747 | -122.444 | 4.8548 | 4.8494 | 5.0319 | 4.9554 | -117.9588 | 0.038704 | 0.15562 | 0.18629 | 0.18348 | -122.6709
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0038783 | -0.011664 | 0.0067454 | 0.0053413 | -0.0044395 | -0.0025533 | 0.016835 | 0.03604 | 0.010945 | 5.5455 | 5.5919 | 5.4306 | 5.505 | 5.5042 | 5.6638 | 5.2943 | 0.023941 | 0.073618 | -0.06093 | -0.071161 | 0.054914 | 0.081008 | -0.13668 | 5.3767 | -117.0063 | 5.6279 | 5.513 | 0.1363 | -117.0071 | -116.8475 | -0.054279 | -122.5825 | 0.10634 | 0.021467 | 0.075746 | -122.4564 | -122.4303 | 5.5874 | 5.5866 | 5.7462 | 5.6743 | -117.217 | 0.011236 | 0.13731 | 0.1634 | 0.15602 | -122.648
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0038783 | -0.011664 | 0.0071726 | -0.01755 | -0.0046531 | -0.0027669 | 0.016835 | 0.03604 | 0.010518 | 4.79 | 4.8318 | 4.6935 | 4.7358 | 4.8037 | 4.9037 | 4.5571 | 0.023941 | 0.078197 | -0.051772 | -0.066582 | 0.050335 | 0.090166 | -0.14125 | 4.6807 | -117.8075 | 4.9136 | 4.8171 | 0.13641 | -117.7397 | -117.6396 | -0.017659 | -122.6099 | 0.14754 | 0.071824 | 0.089483 | -122.493 | -122.4532 | 4.8594 | 4.9272 | 5.0273 | 4.9554 | -117.9863 | 0.057014 | 0.17393 | 0.21376 | 0.20179 | -122.6846
|  |  |  | 1.4211e-13 | -0.035974 | -6.4092e-05 | -0.0040921 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017263 | 0.035827 | 0.010732 | 4.7946 | 4.8364 | 4.6889 | 4.7267 | 4.8037 | 4.9083 | 4.5479 | 0.02852 | 0.078197 | -0.051772 | -0.066582 | 0.054914 | 0.085587 | -0.13668 | 4.6624 | -117.8258 | 4.9091 | 4.8033 | 0.14099 | -117.7488 | -117.6442 | -0.022235 | -122.6191 | 0.14296 | 0.062669 | 0.084904 | -122.4976 | -122.4669 | 4.8411 | 4.9181 | 5.0227 | 4.9509 | -118.0046 | 0.047859 | 0.16936 | 0.20003 | 0.19264 | -122.6892
|  |  |  | 1.4211e-13 | -0.035547 | -0.00049149 | -0.0036647 | -0.01145 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016835 | 0.03604 | 0.010945 | 6.3101 | 6.329 | 6.1585 | 6.2284 | 6.2964 | 6.3963 | 6.0178 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.045757 | 0.085587 | -0.13668 | 6.0681 | -116.2463 | 6.3604 | 6.2089 | 0.14078 | -116.1783 | -116.0783 | -0.086322 | -122.5458 | 0.078874 | -0.010576 | 0.075746 | -122.4289 | -122.3891 | 6.2787 | 6.3467 | 6.4467 | 6.3794 | -116.4569 | -0.020807 | 0.096111 | 0.13594 | 0.12855 | -122.6113
|  |  |  | 1.4211e-13 | -0.03576 | -0.00049149 | -0.0038783 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0021259 | 0.016835 | 0.03604 | 0.010945 | 6.3055 | 6.3199 | 6.1494 | 6.2146 | 6.2826 | 6.3918 | 5.9994 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.13668 | 6.0635 | -116.2967 | 6.3696 | 6.2135 | 0.14994 | -116.2286 | -116.1195 | -0.072589 | -122.5779 | 0.088028 | 0.003157 | 0.075746 | -122.4564 | -122.4257 | 6.2787 | 6.3467 | 6.4558 | 6.384 | -116.5119 | -0.002495 | 0.119 | 0.14967 | 0.14686 | -122.648
|  |  |  | 1.4211e-13 | -0.036188 | -0.00027769 | -0.0034509 | -0.01145 | 0.0067454 | -0.0099192 | -0.0044395 | -0.0027669 | 0.017049 | 0.03604 | 0.010732 | 6.2826 | 6.3061 | 6.1402 | 6.1963 | 6.2735 | 6.3826 | 5.9857 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.07643 | -0.13668 | 6.0498 | -116.3104 | 6.3467 | 6.2043 | 0.15452 | -116.2332 | -116.1241 | -0.072589 | -122.5687 | 0.088028 | 0.003157 | 0.075746 | -122.4518 | -122.4303 | 6.2604 | 6.3376 | 6.4467 | 6.3702 | -116.521 | 0.002083 | 0.119 | 0.14052 | 0.14228 | -122.6434
|  |  |  | 1.4211e-13 | -0.03576 | -6.4092e-05 | -0.0040921 | -0.011236 | 0.0067454 | -0.01755 | -0.0046531 | -0.0025533 | 0.017049 | 0.035827 | 0.010945 | 6.2826 | 6.3016 | 6.1265 | 6.1963 | 6.2689 | 6.3734 | 5.9811 | 0.019362 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.081008 | -0.14583 | 6.0498 | -116.3241 | 6.3513 | 6.1952 | 0.14536 | -116.2515 | -116.147 | -0.077168 | -122.5825 | 0.088027 | 0.003156 | 0.080324 | -122.461 | -122.4394 | 6.265 | 6.3376 | 6.4421 | 6.3702 | -116.5393 | 0.006661 | 0.12816 | 0.14967 | 0.14686 | -122.6663
|  |  |  | 1.4211e-13 | -0.036188 | -0.00049149 | -0.0036647 | -0.011664 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016835 | 0.035827 | 0.010518 | 6.2689 | 6.2924 | 6.1219 | 6.1826 | 6.2552 | 6.3551 | 5.9628 | 0.033099 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14125 | 6.0772 | -116.3562 | 6.3833 | 6.2363 | 0.1591 | -116.2836 | -116.1836 | -0.026814 | -122.6053 | 0.14754 | 0.053511 | 0.080325 | -122.4838 | -122.4532 | 6.297 | 6.3696 | 6.4696 | 6.4068 | -116.576 | 0.047859 | 0.16936 | 0.20003 | 0.19722 | -122.68
|  |  |  | 1.4211e-13 | -0.035974 | -0.00027769 | -0.0038783 | -0.011236 | 0.006959 | -0.0022892 | -0.0052939 | -0.0023397 | 0.016835 | 0.035827 | 0.010732 | 6.2551 | 6.2787 | 6.1082 | 6.1734 | 6.246 | 6.3506 | 5.9628 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.054914 | 0.07643 | -0.13668 | 6.0727 | -116.3699 | 6.365 | 6.218 | 0.14537 | -116.2973 | -116.1928 | -0.026813 | -122.6099 | 0.1338 | 0.053512 | 0.080325 | -122.4884 | -122.4669 | 6.2833 | 6.3559 | 6.4604 | 6.3885 | -116.5805 | 0.043281 | 0.16478 | 0.18629 | 0.19722 | -122.68
|  |  |  | 1.4211e-13 | -0.035974 | -0.00027769 | -0.0034509 | -0.011236 | 0.006959 | -0.01755 | -0.0050803 | -0.0025533 | 0.017049 | 0.035827 | 0.010732 | 6.2551 | 6.2604 | 6.099 | 6.1643 | 6.2369 | 6.3322 | 5.9491 | 0.033099 | 0.082776 | -0.056351 | -0.071161 | 0.054914 | 0.081008 | -0.14125 | 6.0772 | -116.3516 | 6.3833 | 6.2272 | 0.14995 | -116.279 | -116.1836 | -0.013081 | -122.587 | 0.16127 | 0.071823 | 0.084904 | -122.461 | -122.4349 | 6.2924 | 6.365 | 6.4604 | 6.3885 | -116.5668 | 0.057013 | 0.18309 | 0.20918 | 0.21095 | -122.6571
|  |  |  | 1.4211e-13 | -0.035974 | -0.00027769 | -0.0036647 | -0.01145 | 0.006959 | -0.02518 | -0.0046531 | -0.0027669 | 0.016622 | 0.035827 | 0.010732 | 6.2368 | 6.2512 | 6.0944 | 6.1505 | 6.2277 | 6.3322 | 5.9399 | 0.019362 | 0.078197 | -0.065509 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 6.0315 | -116.3791 | 6.3284 | 6.186 | 0.15453 | -116.3019 | -116.1974 | -0.049702 | -122.5962 | 0.11091 | 0.026044 | 0.075746 | -122.4747 | -122.4486 | 6.2421 | 6.3192 | 6.4238 | 6.3428 | -116.5897 | 0.024971 | 0.14647 | 0.17256 | 0.16975 | -122.6709
|  |  |  | 1.4211e-13 | -0.036188 | -0.00027769 | -0.0036647 | -0.01145 | 0.006959 | -0.01755 | -0.0048667 | -0.0023397 | 0.016622 | 0.035827 | 0.010945 | 6.2322 | 6.2466 | 6.0807 | 6.146 | 6.2185 | 6.3231 | 5.9308 | 0.019362 | 0.078197 | -0.051772 | -0.062004 | 0.050335 | 0.081008 | -0.13668 | 6.036 | -116.3928 | 6.3375 | 6.186 | 0.14995 | -116.3202 | -116.2157 | -0.03139 | -122.6008 | 0.12465 | 0.053514 | 0.084904 | -122.4884 | -122.4577 | 6.2512 | 6.3238 | 6.4284 | 6.3519 | -116.608 | 0.043282 | 0.15562 | 0.18629 | 0.18348 | -122.6754
|  |  |  | 1.4211e-13 | -0.036188 | -0.00027769 | -0.0034509 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0025533 | 0.017049 | 0.035827 | 0.010732 | 6.2185 | 6.2375 | 6.0715 | 6.1276 | 6.2048 | 6.3093 | 5.917 | 0.023941 | 0.087354 | -0.056351 | -0.071161 | 0.050335 | 0.085587 | -0.14125 | 6.0269 | -116.402 | 6.3284 | 6.1814 | 0.15453 | -116.3248 | -116.2203 | -0.031392 | -122.6008 | 0.1338 | 0.053512 | 0.084904 | -122.4793 | -122.444 | 6.2375 | 6.3147 | 6.4192 | 6.3473 | -116.6126 | 0.038702 | 0.1602 | 0.19545 | 0.19722 | -122.6709
|  |  |  | 1.4211e-13 | -0.035974 | -0.00049149 | -0.0034509 | -0.01145 | 0.0067454 | -0.01755 | -0.0050803 | -0.0023397 | 0.016835 | 0.035613 | 0.010732 | 6.2139 | 6.2329 | 6.0532 | 6.1276 | 6.1956 | 6.3048 | 5.9124 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.054914 | 0.085587 | -0.14125 | 6.036 | -116.434 | 6.3375 | 6.1768 | 0.14079 | -116.366 | -116.2569 | -0.017659 | -122.6282 | 0.14754 | 0.058087 | 0.075746 | -122.5067 | -122.4761 | 6.2512 | 6.3192 | 6.4284 | 6.3565 | -116.6492 | 0.057014 | 0.17851 | 0.20918 | 0.20637 | -122.7029
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.01755 | -0.0050803 | -0.0025533 | 0.016835 | 0.03604 | 0.010732 | 6.2002 | 6.2283 | 6.0532 | 6.1139 | 6.1865 | 6.2865 | 5.8987 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.14125 | 6.004 | -116.4203 | 6.3055 | 6.1585 | 0.15453 | -116.3477 | -116.2477 | -0.035969 | -122.6053 | 0.12923 | 0.044356 | 0.080325 | -122.4884 | -122.4532 | 6.2192 | 6.2918 | 6.3917 | 6.3336 | -116.6355 | 0.034125 | 0.15104 | 0.18629 | 0.19264 | -122.6754
|  |  |  | 1.4211e-13 | -0.03576 | -0.00027769 | -0.0036647 | -0.011236 | 0.0071726 | -0.01755 | -0.0044395 | -0.0023397 | 0.017049 | 0.036254 | 0.010945 | 6.1864 | 6.2054 | 6.0349 | 6.1048 | 6.1773 | 6.2819 | 5.8895 | 0.02852 | 0.082776 | -0.056351 | -0.062004 | 0.050335 | 0.081008 | -0.14125 | 5.9994 | -116.4203 | 6.2963 | 6.1448 | 0.14538 | -116.3477 | -116.2432 | -0.031392 | -122.587 | 0.13838 | 0.053512 | 0.084904 | -122.4747 | -122.444 | 6.2146 | 6.2872 | 6.3917 | 6.3153 | -116.6355 | 0.047859 | 0.1602 | 0.19087 | 0.19264 | -122.6663
|  |  |  | 1.4211e-13 | -0.036615 | -0.00070509 | -0.0038783 | -0.011236 | 0.006959 | -0.01755 | -0.0046531 | -0.0023397 | 0.016835 | 0.03604 | 0.010945 | 6.1773 | 6.2008 | 6.0349 | 6.0956 | 6.1682 | 6.2773 | 5.8804 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.9628 | -116.434 | 6.2597 | 6.1173 | 0.15453 | -116.3614 | -116.2523 | -0.054279 | -122.5962 | 0.11092 | 0.016888 | 0.071167 | -122.4793 | -122.4486 | 6.178 | 6.2506 | 6.3597 | 6.2832 | -116.6492 | 0.015815 | 0.13273 | 0.1634 | 0.16059 | -122.6663
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017049 | 0.036468 | 0.010945 | 6.1727 | 6.1871 | 6.0258 | 6.0819 | 6.159 | 6.259 | 5.8804 | 0.019362 | 0.087354 | -0.06093 | -0.066582 | 0.041178 | 0.085587 | -0.1321 | 5.9674 | -116.4798 | 6.2597 | 6.1127 | 0.14538 | -116.4026 | -116.3027 | -0.045122 | -122.6282 | 0.10634 | 0.026045 | 0.071167 | -122.5205 | -122.4761 | 6.1688 | 6.246 | 6.346 | 6.2741 | -116.6813 | 0.020393 | 0.12815 | 0.17256 | 0.17433 | -122.6937
|  |  |  | 1.4211e-13 | -0.036401 | -0.00027769 | -0.0032373 | -0.011236 | 0.0067454 | -0.02518 | -0.0048667 | -0.0025533 | 0.016835 | 0.036254 | 0.010518 | 6.1681 | 6.1779 | 6.0166 | 6.0773 | 6.1453 | 6.2544 | 5.8758 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.059493 | 0.085587 | -0.13668 | 5.9674 | -116.4844 | 6.2597 | 6.1082 | 0.1408 | -116.4164 | -116.3072 | -0.045123 | -122.6282 | 0.11549 | 0.030623 | 0.075746 | -122.5022 | -122.4761 | 6.1688 | 6.2368 | 6.346 | 6.2695 | -116.6858 | 0.024971 | 0.15105 | 0.17714 | 0.17433 | -122.6983
|  |  |  | 1.4211e-13 | -0.035974 | 0.00014951 | -0.0034509 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017049 | 0.03604 | 0.010518 | 6.1636 | 6.1734 | 5.9983 | 6.0681 | 6.1453 | 6.2452 | 5.8621 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.9216 | -116.4523 | 6.2231 | 6.0578 | 0.13622 | -116.3752 | -116.2752 | -0.077167 | -122.587 | 0.078871 | -0.001421 | 0.075746 | -122.4701 | -122.4394 | 6.1276 | 6.2048 | 6.3048 | 6.2329 | -116.6584 | -0.007073 | 0.10984 | 0.14052 | 0.14228 | -122.6571
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0071726 | -0.01755 | -0.0046531 | -0.0025533 | 0.016835 | 0.03604 | 0.010945 | 6.1452 | 6.1642 | 5.9891 | 6.059 | 6.1224 | 6.2315 | 5.8529 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.13668 | 5.9582 | -116.5118 | 6.2505 | 6.0944 | 0.13622 | -116.4484 | -116.3393 | -0.03139 | -122.6374 | 0.12923 | 0.044356 | 0.075746 | -122.5159 | -122.4852 | 6.1643 | 6.2277 | 6.3368 | 6.2695 | -116.7179 | 0.038704 | 0.1602 | 0.19087 | 0.19264 | -122.7075
|  |  |  | 1.4211e-13 | -0.035974 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0071726 | -0.01755 | -0.0044395 | -0.0025533 | 0.016835 | 0.036254 | 0.010732 | 6.1315 | 6.1459 | 5.9891 | 6.0544 | 6.1224 | 6.2269 | 5.8392 | 0.014784 | 0.082776 | -0.06093 | -0.071161 | 0.050335 | 0.081008 | -0.14583 | 5.8895 | -116.4844 | 6.1819 | 6.0395 | 0.14996 | -116.4164 | -116.3118 | -0.095479 | -122.6099 | 0.065138 | -0.010576 | 0.084903 | -122.4884 | -122.4577 | 6.1047 | 6.1727 | 6.2773 | 6.1962 | -116.6996 | -0.020807 | 0.10069 | 0.13136 | 0.13313 | -122.6846
|  |  |  | 1.4211e-13 | -0.036188 | -0.00027769 | -0.0036647 | -0.011236 | 0.0067454 | -0.02518 | -0.0048667 | -0.0027669 | 0.016835 | 0.03604 | 0.010732 | 6.1224 | 6.1459 | 5.9662 | 6.0498 | 6.1132 | 6.2178 | 5.8254 | 0.023941 | 0.073618 | -0.06093 | -0.066582 | 0.054914 | 0.07643 | -0.14125 | 5.9124 | -116.4798 | 6.2093 | 6.0532 | 0.14081 | -116.4164 | -116.3118 | -0.05428 | -122.5962 | 0.11092 | 0.026045 | 0.080325 | -122.4747 | -122.4532 | 6.1368 | 6.2002 | 6.3047 | 6.2329 | -116.7042 | 0.020393 | 0.14189 | 0.1634 | 0.16059 | -122.6709
|  |  |  | 1.4211e-13 | -0.035974 | -0.00027769 | -0.0034509 | -0.011023 | 0.0067454 | -0.0099192 | -0.0050803 | -0.0027669 | 0.016835 | 0.036254 | 0.010732 | 6.1086 | 6.1322 | 5.9662 | 6.0315 | 6.0949 | 6.1995 | 5.8209 | 0.023941 | 0.087354 | -0.065509 | -0.071161 | 0.054914 | 0.07643 | -0.14583 | 5.9216 | -116.5256 | 6.2093 | 6.067 | 0.14539 | -116.4622 | -116.3576 | -0.045125 | -122.6282 | 0.12465 | 0.035199 | 0.080324 | -122.5022 | -122.4806 | 6.1322 | 6.1956 | 6.3002 | 6.2329 | -116.7362 | 0.029547 | 0.15562 | 0.17714 | 0.18806 | -122.7029
|  |  |  | 1.4211e-13 | -0.036401 | -0.00027769 | -0.0036647 | -0.011664 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0025533 | 0.017049 | 0.036254 | 0.010732 | 6.104 | 6.123 | 5.9571 | 6.0269 | 6.0857 | 6.1995 | 5.8163 | 0.02852 | 0.082776 | -0.056351 | -0.071161 | 0.041178 | 0.081008 | -0.14583 | 5.9307 | -116.5256 | 6.2185 | 6.0715 | 0.14081 | -116.4667 | -116.353 | -0.031392 | -122.6237 | 0.14296 | 0.05809 | 0.089482 | -122.5113 | -122.4715 | 6.1414 | 6.2002 | 6.3139 | 6.2374 | -116.7362 | 0.04328 | 0.15562 | 0.19545 | 0.19722 | -122.6983
|  |  |  | 1.4211e-13 | -0.036188 | -0.00070509 | -0.0036647 | -0.011664 | 0.0073864 | -0.01755 | -0.0044395 | -0.0023397 | 0.017049 | 0.03604 | 0.010518 | 6.0857 | 6.1093 | 5.9342 | 6.0086 | 6.0857 | 6.1903 | 5.798 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.059493 | 0.081008 | -0.14125 | 5.8483 | -116.521 | 6.1361 | 5.9846 | 0.13623 | -116.4439 | -116.3393 | -0.090901 | -122.5962 | 0.074295 | -0.015155 | 0.075746 | -122.4701 | -122.4486 | 6.059 | 6.1361 | 6.2407 | 6.1596 | -116.7316 | -0.016228 | 0.10985 | 0.13136 | 0.12855 | -122.6709
|  |  |  | 1.4211e-13 | -0.036401 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.006959 | -0.02518 | -0.0046531 | -0.0027669 | 0.016835 | 0.03604 | 0.010518 | 6.0857 | 6.1093 | 5.9342 | 6.004 | 6.072 | 6.1857 | 5.8025 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.054914 | 0.085587 | -0.14125 | 5.8529 | -116.5393 | 6.1361 | 5.9846 | 0.13165 | -116.4713 | -116.3576 | -0.090901 | -122.6099 | 0.074295 | -0.015155 | 0.075746 | -122.4884 | -122.4577 | 6.0544 | 6.1224 | 6.2361 | 6.1596 | -116.7408 | -0.016228 | 0.10527 | 0.13594 | 0.13771 | -122.6846
|  |  |  | 1.4211e-13 | -0.036401 | -0.00027769 | -0.0036647 | -0.011236 | 0.006959 | -0.0022892 | -0.0046531 | -0.0025533 | 0.016835 | 0.036254 | 0.010732 | 6.0766 | 6.0955 | 5.925 | 5.9949 | 6.0629 | 6.172 | 5.7797 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.14125 | 5.8941 | -116.5713 | 6.191 | 6.0395 | 0.14539 | -116.5034 | -116.3942 | -0.026814 | -122.6328 | 0.13838 | 0.053511 | 0.080325 | -122.5205 | -122.4852 | 6.1093 | 6.1773 | 6.2864 | 6.21 | -116.7866 | 0.047859 | 0.1602 | 0.19545 | 0.19264 | -122.7075
|  |  |  | 1.4211e-13 | -0.036401 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.0071726 | -0.0099192 | -0.0048667 | -0.0023397 | 0.016408 | 0.03604 | 0.010945 | 6.0766 | 6.0909 | 5.925 | 5.9903 | 6.0583 | 6.1537 | 5.7797 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.054914 | 0.081008 | -0.14583 | 5.8758 | -116.5485 | 6.1727 | 6.0212 | 0.14539 | -116.4805 | -116.3851 | -0.049703 | -122.6099 | 0.12007 | 0.0352 | 0.084903 | -122.4838 | -122.4577 | 6.0864 | 6.1544 | 6.2498 | 6.1871 | -116.7591 | 0.024969 | 0.15104 | 0.17714 | 0.17891 | -122.6846
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0036647 | -0.011664 | 0.006959 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016622 | 0.03604 | 0.010732 | 6.0674 | 6.0772 | 5.9205 | 5.9903 | 6.0491 | 6.1582 | 5.7751 | 0.033099 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.8575 | -116.5759 | 6.1498 | 6.0029 | 0.14539 | -116.5171 | -116.408 | -0.054279 | -122.6328 | 0.1155 | 0.021467 | 0.075746 | -122.5159 | -122.4852 | 6.0727 | 6.1315 | 6.2406 | 6.1596 | -116.7912 | 0.015815 | 0.13273 | 0.1634 | 0.16517 | -122.7029
|  |  |  | 1.4211e-13 | -0.036401 | -0.00070509 | -0.0036647 | -0.011664 | 0.0067454 | -0.0022892 | -0.0048667 | -0.0027669 | 0.017049 | 0.036254 | 0.011159 | 6.0674 | 6.0864 | 5.9205 | 5.9857 | 6.0537 | 6.1582 | 5.7751 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 5.8575 | -116.5668 | 6.1498 | 6.0029 | 0.14539 | -116.4988 | -116.3942 | -0.058858 | -122.6191 | 0.10176 | 0.021467 | 0.080325 | -122.4976 | -122.4715 | 6.0681 | 6.1361 | 6.2406 | 6.1688 | -116.7774 | 0.015815 | 0.13731 | 0.1634 | 0.16517 | -122.6937
|  |  |  | 1.4211e-13 | -0.036401 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.03604 | 0.010732 | 6.0537 | 6.0818 | 5.9113 | 5.9811 | 6.0491 | 6.1491 | 5.7659 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.050335 | 0.085587 | -0.14583 | 5.8208 | -116.5485 | 6.1086 | 5.9662 | 0.14539 | -116.4805 | -116.3805 | -0.090901 | -122.587 | 0.078873 | -0.005998 | 0.084903 | -122.4793 | -122.444 | 6.0361 | 6.104 | 6.204 | 6.1367 | -116.7637 | -0.002493 | 0.10527 | 0.14052 | 0.14229 | -122.6754
|  |  |  | 1.4211e-13 | -0.036401 | -0.00027769 | -0.0038783 | -0.011236 | 0.006959 | -0.01755 | -0.0046531 | -0.0025533 | 0.016835 | 0.035827 | 0.010945 | 6.0491 | 6.0681 | 5.9022 | 5.972 | 6.04 | 6.1399 | 5.7613 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.081008 | -0.14583 | 5.8163 | -116.5073 | 6.104 | 5.9571 | 0.14082 | -116.4393 | -116.3393 | -0.090901 | -122.5413 | 0.074294 | -0.005998 | 0.084903 | -122.4243 | -122.3982 | 6.0269 | 6.0949 | 6.1949 | 6.123 | -116.7179 | -0.007072 | 0.10985 | 0.13594 | 0.13313 | -122.6251
|  |  |  | 1.4211e-13 | -0.036401 | -0.00049149 | -0.0036647 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0027669 | 0.017049 | 0.036254 | 0.010945 | 6.0399 | 6.0452 | 5.8838 | 5.9537 | 6.0308 | 6.1262 | 5.7522 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.054914 | 0.081008 | -0.14583 | 5.8392 | -116.5805 | 6.1269 | 5.9708 | 0.13166 | -116.5034 | -116.408 | -0.058858 | -122.6053 | 0.11092 | 0.021466 | 0.080324 | -122.4793 | -122.4532 | 6.0406 | 6.1178 | 6.2132 | 6.1321 | -116.782 | 0.015814 | 0.14189 | 0.16798 | 0.16975 | -122.68
|  |  |  | 1.4211e-13 | -0.036401 | -6.4092e-05 | -0.0036647 | -0.011664 | 0.0071726 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016835 | 0.036254 | 0.010945 | 6.0262 | 6.0406 | 5.8747 | 5.9445 | 6.0216 | 6.1216 | 5.7293 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 5.7934 | -116.5805 | 6.0903 | 5.9388 | 0.1454 | -116.5034 | -116.4034 | -0.077168 | -122.5916 | 0.088028 | 0.003157 | 0.080325 | -122.4747 | -122.444 | 6.0086 | 6.0857 | 6.1857 | 6.1047 | -116.7957 | -0.002495 | 0.11442 | 0.1451 | 0.14686 | -122.6663
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.006959 | -0.0099192 | -0.0044395 | -0.0027669 | 0.016622 | 0.036254 | 0.010945 | 6.017 | 6.0406 | 5.8655 | 5.9262 | 6.0033 | 6.1125 | 5.7247 | 0.019362 | 0.078197 | -0.06093 | -0.071161 | 0.050335 | 0.081008 | -0.13668 | 5.8117 | -116.6217 | 6.104 | 5.9525 | 0.14082 | -116.5446 | -116.4354 | -0.049701 | -122.6191 | 0.10634 | 0.026045 | 0.075746 | -122.4976 | -122.4669 | 6.0132 | 6.0903 | 6.1994 | 6.1276 | -116.8232 | 0.015814 | 0.13731 | 0.16798 | 0.16517 | -122.6846
|  |  |  | 1.4211e-13 | -0.036188 | -0.00049149 | -0.0040921 | -0.011236 | 0.006959 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016622 | 0.03604 | 0.010732 | 6.0125 | 6.0268 | 5.8609 | 5.9308 | 5.9988 | 6.1033 | 5.7201 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 5.8025 | -116.6126 | 6.0949 | 5.9433 | 0.14082 | -116.5446 | -116.44 | -0.058858 | -122.6099 | 0.10634 | 0.026046 | 0.084904 | -122.493 | -122.4623 | 6.0132 | 6.0811 | 6.1857 | 6.1092 | -116.8232 | 0.015815 | 0.13273 | 0.1634 | 0.16059 | -122.6846
|  |  |  | 1.4211e-13 | -0.036401 | -0.00049149 | -0.0034509 | -0.011664 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.036254 | 0.010732 | 5.9987 | 6.0223 | 5.8472 | 5.9216 | 5.9942 | 6.0941 | 5.711 | 0.033099 | 0.082776 | -0.056351 | -0.066582 | 0.054914 | 0.090166 | -0.14125 | 5.7888 | -116.6217 | 6.0766 | 5.925 | 0.13624 | -116.5492 | -116.4492 | -0.063435 | -122.6099 | 0.11092 | 0.021469 | 0.084904 | -122.4884 | -122.4532 | 5.9994 | 6.072 | 6.172 | 6.1001 | -116.8324 | 0.011238 | 0.13273 | 0.16799 | 0.1606 | -122.6846
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0036647 | -0.01145 | 0.0073864 | -0.01755 | -0.0046531 | -0.0025533 | 0.016835 | 0.036468 | 0.010945 | 5.985 | 6.0131 | 5.8426 | 5.9079 | 5.9804 | 6.0896 | 5.7064 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.054914 | 0.090166 | -0.14125 | 5.7842 | -116.6675 | 6.0628 | 5.9205 | 0.13625 | -116.5949 | -116.4858 | -0.063435 | -122.642 | 0.10176 | 0.021469 | 0.084904 | -122.5205 | -122.4852 | 5.9857 | 6.0583 | 6.1674 | 6.0909 | -116.869 | 0.011238 | 0.13273 | 0.16799 | 0.15602 | -122.7166
|  |  |  | 1.4211e-13 | -0.036615 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.02518 | -0.0048667 | -0.0027669 | 0.017049 | 0.036468 | 0.010732 | 5.9758 | 5.9902 | 5.8243 | 5.9033 | 5.9713 | 6.0758 | 5.6972 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 5.7659 | -116.64 | 6.0445 | 5.893 | 0.12709 | -116.5721 | -116.4675 | -0.07259 | -122.6099 | 0.092606 | 0.007735 | 0.080325 | -122.4884 | -122.4623 | 5.972 | 6.0399 | 6.1445 | 6.0589 | -116.8461 | 0.002083 | 0.12358 | 0.14967 | 0.14686 | -122.6846
|  |  |  | 1.4211e-13 | -0.036829 | -0.00027769 | -0.0034509 | -0.011236 | 0.0071726 | -0.01755 | -0.0048667 | -0.0029805 | 0.016835 | 0.036254 | 0.010732 | 5.9621 | 5.9856 | 5.8197 | 5.8896 | 5.9575 | 6.0621 | 5.6789 | 0.023941 | 0.087354 | -0.065509 | -0.062004 | 0.045757 | 0.085587 | -0.13668 | 5.7705 | -116.6858 | 6.0537 | 5.9113 | 0.14083 | -116.6178 | -116.5133 | -0.045123 | -122.6374 | 0.11549 | 0.026044 | 0.071167 | -122.5296 | -122.4898 | 5.9811 | 6.0491 | 6.1537 | 6.0772 | -116.8965 | 0.029549 | 0.13731 | 0.17714 | 0.17891 | -122.7121
|  |  |  | 1.4211e-13 | -0.036401 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.03604 | 0.010732 | 5.9621 | 5.9856 | 5.8152 | 5.8804 | 5.9575 | 6.0575 | 5.6698 | 0.033099 | 0.087354 | -0.056351 | -0.071161 | 0.054914 | 0.081008 | -0.13668 | 5.7384 | -116.6538 | 6.0308 | 5.8838 | 0.14541 | -116.5766 | -116.4767 | -0.068011 | -122.6053 | 0.10176 | 0.012314 | 0.080325 | -122.4793 | -122.4532 | 5.9491 | 6.0262 | 6.1262 | 6.0543 | -116.8644 | -0.002496 | 0.12358 | 0.14967 | 0.15602 | -122.6709
|  |  |  | 1.4211e-13 | -0.036401 | -0.00027769 | -0.0034509 | -0.011236 | 0.0067454 | -0.0099192 | -0.0044395 | -0.0023397 | 0.016622 | 0.03604 | 0.010518 | 5.953 | 5.9765 | 5.8014 | 5.8713 | 5.9438 | 6.0529 | 5.6743 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.14125 | 5.7384 | -116.6446 | 6.017 | 5.8655 | 0.12709 | -116.5721 | -116.4629 | -0.077168 | -122.5779 | 0.088028 | 0.003157 | 0.080325 | -122.4564 | -122.4303 | 5.9353 | 6.0079 | 6.117 | 6.0406 | -116.8415 | 0.002083 | 0.12358 | 0.14967 | 0.15144 | -122.6571
|  |  |  | 1.4211e-13 | -0.036615 | -0.00049149 | -0.0036647 | -0.011236 | 0.006959 | -0.01755 | -0.0044395 | -0.0023397 | 0.017049 | 0.03604 | 0.010732 | 5.9438 | 5.9811 | 5.8014 | 5.8621 | 5.9392 | 6.0484 | 5.6698 | 0.014784 | 0.082776 | -0.065509 | -0.066582 | 0.059493 | 0.081008 | -0.13668 | 5.775 | -116.7316 | 6.0491 | 5.9067 | 0.13167 | -116.6545 | -116.5453 | -0.03139 | -122.6603 | 0.12007 | 0.039777 | 0.071167 | -122.5342 | -122.5127 | 5.9674 | 6.0445 | 6.1536 | 6.0863 | -116.9239 | 0.038704 | 0.16478 | 0.18629 | 0.18806 | -122.7304
|  |  |  | 1.4211e-13 | -0.036615 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.036468 | 0.010304 | 5.9484 | 5.9627 | 5.806 | 5.8667 | 5.9301 | 6.0392 | 5.6606 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.14125 | 5.7613 | -116.7362 | 6.0491 | 5.9067 | 0.14541 | -116.6728 | -116.5636 | -0.040547 | -122.6694 | 0.12007 | 0.035199 | 0.075746 | -122.5571 | -122.5173 | 5.9674 | 6.0308 | 6.1399 | 6.0635 | -116.9422 | 0.034126 | 0.14647 | 0.18629 | 0.18806 | -122.7441
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0036647 | -0.011023 | 0.0071726 | -0.01755 | -0.0048667 | -0.0025533 | 0.016835 | 0.036254 | 0.010518 | 5.9484 | 5.9627 | 5.7923 | 5.8621 | 5.9346 | 6.0392 | 5.6469 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.6881 | -116.6812 | 5.9896 | 5.8335 | 0.14541 | -116.6087 | -116.5041 | -0.095477 | -122.6099 | 0.06514 | -0.019731 | 0.075746 | -122.493 | -122.4623 | 5.9033 | 5.9758 | 6.0804 | 6.0039 | -116.8965 | -0.025383 | 0.091534 | 0.12221 | 0.12855 | -122.68
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0036647 | -0.011664 | 0.0065316 | -0.01755 | -0.0046531 | -0.0025533 | 0.017049 | 0.036254 | 0.010732 | 5.9346 | 5.9536 | 5.7877 | 5.8621 | 5.9209 | 6.0255 | 5.6469 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.045757 | 0.07643 | -0.14125 | 5.775 | -116.7133 | 6.0628 | 5.9159 | 0.14083 | -116.6545 | -116.5499 | -0.013081 | -122.6328 | 0.15212 | 0.067244 | 0.080325 | -122.5296 | -122.4989 | 5.9903 | 6.0491 | 6.1536 | 6.0818 | -116.9285 | 0.070749 | 0.17393 | 0.2046 | 0.21095 | -122.7166
|  |  |  | 1.4211e-13 | -0.036615 | -6.4092e-05 | -0.0040921 | -0.011023 | 0.0067454 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.036468 | 0.010732 | 5.9255 | 5.949 | 5.7877 | 5.8484 | 5.9163 | 6.0255 | 5.6423 | 0.023941 | 0.073618 | -0.056351 | -0.066582 | 0.045757 | 0.085587 | -0.14583 | 5.7521 | -116.6995 | 6.0353 | 5.8976 | 0.14541 | -116.6316 | -116.5224 | -0.03597 | -122.6145 | 0.1338 | 0.053512 | 0.089482 | -122.5022 | -122.4623 | 5.9582 | 6.0262 | 6.1353 | 6.0589 | -116.9056 | 0.043281 | 0.15562 | 0.19545 | 0.18348 | -122.6937
|  |  |  | 1.4211e-13 | -0.036829 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.006959 | -0.01755 | -0.0048667 | -0.0025533 | 0.017049 | 0.036254 | 0.010518 | 5.9209 | 5.949 | 5.774 | 5.8484 | 5.9118 | 6.0163 | 5.6423 | 0.019362 | 0.082776 | -0.056351 | -0.066582 | 0.050335 | 0.085587 | -0.14125 | 5.7476 | -116.6995 | 6.0262 | 5.8792 | 0.13168 | -116.6362 | -116.5316 | -0.035969 | -122.6145 | 0.12465 | 0.048935 | 0.084904 | -122.4976 | -122.4623 | 5.9537 | 6.017 | 6.1216 | 6.0543 | -116.9056 | 0.038704 | 0.15562 | 0.19087 | 0.18806 | -122.6892
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0038783 | -0.01145 | 0.0067454 | -0.0022892 | -0.0044395 | -0.0025533 | 0.016622 | 0.03604 | 0.010518 | 5.9209 | 5.9307 | 5.7602 | 5.8438 | 5.9026 | 6.0072 | 5.624 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.0366 | 0.090166 | -0.13668 | 5.6926 | -116.6904 | 5.9896 | 5.8289 | 0.13626 | -116.6316 | -116.527 | -0.068011 | -122.5916 | 0.092606 | 0.007735 | 0.075746 | -122.4976 | -122.444 | 5.9125 | 5.9713 | 6.0758 | 5.9994 | -116.9102 | 0.01124 | 0.10526 | 0.15883 | 0.15144 | -122.6709
|  |  |  | 1.4211e-13 | -0.036401 | -0.00049149 | -0.0034509 | -0.011236 | 0.0067454 | -0.01755 | -0.0048667 | -0.0023397 | 0.016835 | 0.03604 | 0.010304 | 5.9072 | 5.9261 | 5.7648 | 5.8255 | 5.898 | 6.0026 | 5.624 | 0.023941 | 0.078197 | -0.056351 | -0.062004 | 0.050335 | 0.081008 | -0.14583 | 5.743 | -116.7682 | 6.0262 | 5.8838 | 0.14084 | -116.6957 | -116.5911 | -0.026814 | -122.6557 | 0.14296 | 0.062668 | 0.089482 | -122.5434 | -122.5127 | 5.9445 | 6.017 | 6.1216 | 6.0451 | -116.9697 | 0.057015 | 0.16935 | 0.20003 | 0.19722 | -122.7395
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0036647 | -0.01145 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.036254 | 0.010732 | 5.8889 | 5.9215 | 5.7419 | 5.8163 | 5.8797 | 5.9934 | 5.6057 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.045757 | 0.07643 | -0.14125 | 5.6789 | -116.7499 | 5.9621 | 5.8152 | 0.13626 | -116.6865 | -116.5728 | -0.068013 | -122.6282 | 0.10176 | 0.012312 | 0.080325 | -122.5205 | -122.4898 | 5.8896 | 5.9529 | 6.0667 | 5.9948 | -116.9606 | 0.011238 | 0.119 | 0.14967 | 0.15602 | -122.7075
|  |  |  | 1.4211e-13 | -0.036188 | -0.00049149 | -0.0036647 | -0.011236 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016835 | 0.036254 | 0.010732 | 5.8889 | 5.9124 | 5.7373 | 5.8163 | 5.8797 | 5.9797 | 5.6011 | 0.023941 | 0.073618 | -0.070087 | -0.075739 | 0.045757 | 0.07643 | -0.14125 | 5.688 | -116.7911 | 5.9758 | 5.8243 | 0.13626 | -116.7277 | -116.6277 | -0.05428 | -122.6832 | 0.11092 | 0.016888 | 0.071168 | -122.5617 | -122.531 | 5.9033 | 5.9667 | 6.0667 | 5.9994 | -117.0063 | 0.011236 | 0.13273 | 0.1634 | 0.16059 | -122.7487
|  |  |  | 1.4211e-13 | -0.036615 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006959 | -0.01755 | -0.0044395 | -0.0027669 | 0.016835 | 0.036254 | 0.010304 | 5.8797 | 5.9078 | 5.7419 | 5.8072 | 5.8797 | 5.9843 | 5.6011 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.050335 | 0.090166 | -0.14125 | 5.7109 | -116.7911 | 5.9896 | 5.8518 | 0.14084 | -116.7186 | -116.614 | -0.031392 | -122.6603 | 0.1338 | 0.044354 | 0.075746 | -122.5479 | -122.5081 | 5.917 | 5.9896 | 6.0941 | 6.0177 | -116.9972 | 0.047859 | 0.1602 | 0.20003 | 0.18806 | -122.7395
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0067454 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016835 | 0.036254 | 0.010304 | 5.8797 | 5.9078 | 5.7465 | 5.8117 | 5.8797 | 5.9797 | 5.6057 | 0.033099 | 0.091933 | -0.06093 | -0.066582 | 0.045757 | 0.07643 | -0.14583 | 5.7064 | -116.7682 | 5.9804 | 5.8472 | 0.14084 | -116.7003 | -116.6003 | -0.045125 | -122.6465 | 0.13381 | 0.039778 | 0.084903 | -122.5342 | -122.5035 | 5.9124 | 5.9804 | 6.0804 | 6.0085 | -116.9743 | 0.034126 | 0.14647 | 0.17714 | 0.19264 | -122.7258
|  |  |  | 1.4211e-13 | -0.036188 | -6.4092e-05 | -0.0032373 | -0.01145 | 0.006959 | -0.0099192 | -0.0048667 | -0.0023397 | 0.016835 | 0.036468 | 0.010518 | 5.8751 | 5.8986 | 5.7282 | 5.798 | 5.866 | 5.9659 | 5.5873 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.6514 | -116.7591 | 5.9392 | 5.7923 | 0.14084 | -116.6911 | -116.5911 | -0.072589 | -122.6236 | 0.083449 | -0.001422 | 0.071167 | -122.5067 | -122.4761 | 5.8621 | 5.93 | 6.03 | 5.9627 | -116.9697 | -0.002495 | 0.11442 | 0.1451 | 0.15144 | -122.6937
|  |  |  | 1.4211e-13 | -0.036829 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.0065316 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016835 | 0.036468 | 0.010945 | 5.8568 | 5.8849 | 5.7144 | 5.7888 | 5.8614 | 5.9659 | 5.5828 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.14583 | 5.6468 | -116.7728 | 5.9209 | 5.7785 | 0.13168 | -116.7003 | -116.5957 | -0.081746 | -122.6236 | 0.083449 | 0.003157 | 0.084903 | -122.5067 | -122.4761 | 5.8529 | 5.9255 | 6.03 | 5.949 | -116.9789 | 0.002083 | 0.119 | 0.14967 | 0.14228 | -122.7075
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0034509 | -0.011236 | 0.006959 | -0.02518 | -0.0048667 | -0.0029805 | 0.016622 | 0.036254 | 0.010518 | 5.866 | 5.8849 | 5.719 | 5.7797 | 5.8522 | 5.9568 | 5.5736 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.1321 | 5.6697 | -116.8186 | 5.9621 | 5.8152 | 0.14542 | -116.746 | -116.6415 | -0.035967 | -122.6603 | 0.12465 | 0.0352 | 0.071167 | -122.5479 | -122.5127 | 5.8758 | 5.9484 | 6.0529 | 5.981 | -117.0247 | 0.034126 | 0.14646 | 0.18172 | 0.17891 | -122.7304
|  |  |  | 1.4211e-13 | -0.036829 | -0.00027769 | -0.0038783 | -0.011236 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0029805 | 0.017049 | 0.036254 | 0.010518 | 5.8614 | 5.8849 | 5.7099 | 5.7888 | 5.8522 | 5.9614 | 5.569 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.13668 | 5.624 | -116.7774 | 5.9163 | 5.7648 | 0.14084 | -116.714 | -116.6049 | -0.081744 | -122.6328 | 0.074294 | -0.005998 | 0.075746 | -122.5205 | -122.4852 | 5.8438 | 5.9072 | 6.0163 | 5.9398 | -116.9972 | -0.01165 | 0.10069 | 0.13594 | 0.13771 | -122.7029
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0038783 | -0.011877 | 0.0067454 | -0.01755 | -0.0048667 | -0.0027669 | 0.016622 | 0.036254 | 0.010732 | 5.8522 | 5.8712 | 5.7099 | 5.7705 | 5.8431 | 5.9476 | 5.5736 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.085587 | -0.14125 | 5.6926 | -116.7957 | 5.9712 | 5.8289 | 0.13626 | -116.7232 | -116.6186 | -0.022236 | -122.6328 | 0.14296 | 0.058089 | 0.080325 | -122.5159 | -122.4806 | 5.8896 | 5.9621 | 6.0667 | 5.9902 | -116.9926 | 0.052437 | 0.16935 | 0.20461 | 0.2018 | -122.7075
|  |  |  | 1.4211e-13 | -0.036829 | 0.00014951 | -0.0038783 | -0.011236 | 0.0065316 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016622 | 0.036254 | 0.010732 | 5.8431 | 5.8712 | 5.7007 | 5.766 | 5.8431 | 5.9431 | 5.5644 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.050335 | 0.085587 | -0.14583 | 5.6423 | -116.7774 | 5.9209 | 5.7785 | 0.13626 | -116.7003 | -116.6003 | -0.068013 | -122.6145 | 0.10176 | 0.01689 | 0.084903 | -122.493 | -122.4577 | 5.8438 | 5.9209 | 6.0209 | 5.949 | -116.9789 | 0.006659 | 0.12815 | 0.16341 | 0.1606 | -122.6892
|  |  |  | 1.4211e-13 | -0.036615 | 0.00014951 | -0.0040921 | -0.011236 | 0.006959 | -0.0022892 | -0.0048667 | -0.0023397 | 0.016622 | 0.036681 | 0.010732 | 5.8385 | 5.8712 | 5.6916 | 5.7568 | 5.8339 | 5.9431 | 5.5553 | 0.023941 | 0.073618 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.14583 | 5.6926 | -116.8323 | 5.9758 | 5.8289 | 0.13627 | -116.7552 | -116.6461 | -0.008504 | -122.6557 | 0.16127 | 0.07182 | 0.080324 | -122.5434 | -122.5035 | 5.8941 | 5.9712 | 6.0804 | 6.0085 | -117.0338 | 0.070747 | 0.18309 | 0.22292 | 0.21095 | -122.7349
|  |  |  | 1.4211e-13 | -0.036401 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016835 | 0.036468 | 0.010732 | 5.8293 | 5.8574 | 5.6916 | 5.7614 | 5.8293 | 5.9339 | 5.5553 | 0.019362 | 0.091933 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.6606 | -116.8277 | 5.9346 | 5.7968 | 0.13627 | -116.7598 | -116.6552 | -0.03139 | -122.6557 | 0.12465 | 0.044356 | 0.075746 | -122.5388 | -122.5081 | 5.8667 | 5.9346 | 6.0392 | 5.9627 | -117.0338 | 0.038704 | 0.15562 | 0.18629 | 0.19722 | -122.7258
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0036647 | -0.011023 | 0.006959 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.036254 | 0.010945 | 5.8293 | 5.8529 | 5.6824 | 5.7522 | 5.8202 | 5.9247 | 5.5461 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.085587 | -0.1321 | 5.5919 | -116.8048 | 5.8751 | 5.7282 | 0.13627 | -116.7369 | -116.6323 | -0.086321 | -122.6236 | 0.069717 | -0.015154 | 0.071167 | -122.5113 | -122.4715 | 5.798 | 5.8659 | 5.9705 | 5.8986 | -117.0109 | -0.020806 | 0.091533 | 0.13136 | 0.12855 | -122.6892
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0038783 | -0.011236 | 0.006959 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016408 | 0.036254 | 0.010945 | 5.8248 | 5.8483 | 5.6778 | 5.7476 | 5.8202 | 5.9202 | 5.537 | 0.02852 | 0.078197 | -0.056351 | -0.062004 | 0.050335 | 0.090166 | -0.14125 | 5.6011 | -116.8048 | 5.8888 | 5.7419 | 0.14085 | -116.7323 | -116.6323 | -0.077168 | -122.6145 | 0.092607 | 0.007736 | 0.084904 | -122.5022 | -122.4623 | 5.8117 | 5.8843 | 5.9842 | 5.9124 | -117.0155 | 0.002083 | 0.11442 | 0.15425 | 0.14228 | -122.6937
|  |  |  | 1.4211e-13 | -0.036615 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.036468 | 0.010732 | 5.8156 | 5.8391 | 5.6641 | 5.7385 | 5.8064 | 5.9156 | 5.5324 | 0.023941 | 0.087354 | -0.056351 | -0.066582 | 0.054914 | 0.085587 | -0.13668 | 5.6423 | -116.8781 | 5.9255 | 5.7739 | 0.13169 | -116.8101 | -116.701 | -0.026813 | -122.6832 | 0.1338 | 0.053512 | 0.080325 | -122.5617 | -122.531 | 5.8483 | 5.9163 | 6.0254 | 5.949 | -117.0842 | 0.043281 | 0.16478 | 0.19545 | 0.19722 | -122.7533
|  |  |  | 1.4211e-13 | -0.036829 | -0.00027769 | -0.0036647 | -0.011236 | 0.006959 | -0.0099192 | -0.0044395 | -0.0025533 | 0.016835 | 0.036254 | 0.010732 | 5.8019 | 5.83 | 5.6549 | 5.7248 | 5.8064 | 5.9064 | 5.5232 | 0.019362 | 0.078197 | -0.065509 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 5.6377 | -116.8689 | 5.9163 | 5.7694 | 0.13169 | -116.7873 | -116.6873 | -0.026814 | -122.6603 | 0.1338 | 0.048932 | 0.075746 | -122.5434 | -122.5127 | 5.8392 | 5.9209 | 6.0209 | 5.9444 | -117.0705 | 0.047859 | 0.16478 | 0.19545 | 0.19264 | -122.7349
|  |  |  | 1.4211e-13 | -0.036829 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.006959 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016835 | 0.036468 | 0.010732 | 5.8064 | 5.8254 | 5.6549 | 5.7293 | 5.8064 | 5.9018 | 5.5187 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.13668 | 5.6194 | -116.8735 | 5.9072 | 5.7556 | 0.13627 | -116.7964 | -116.701 | -0.035968 | -122.6694 | 0.12465 | 0.035199 | 0.071167 | -122.5525 | -122.5173 | 5.83 | 5.9071 | 6.0026 | 5.9261 | -117.0842 | 0.034126 | 0.15104 | 0.18629 | 0.18806 | -122.7395
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0034509 | -0.01145 | 0.0071726 | -0.0099192 | -0.0046531 | -0.0021259 | 0.016622 | 0.036468 | 0.010304 | 5.8019 | 5.8162 | 5.6412 | 5.711 | 5.7881 | 5.8927 | 5.5003 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.090166 | -0.14125 | 5.5919 | -116.8415 | 5.8934 | 5.7327 | 0.14085 | -116.7644 | -116.6598 | -0.049702 | -122.6191 | 0.11549 | 0.030623 | 0.080325 | -122.5022 | -122.4623 | 5.8026 | 5.8797 | 5.9842 | 5.9078 | -117.0522 | 0.024971 | 0.14189 | 0.18172 | 0.17433 | -122.6937
|  |  |  | 1.4211e-13 | -0.036829 | -0.00027769 | -0.0036647 | -0.011023 | 0.006318 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.036681 | 0.010304 | 5.7836 | 5.8162 | 5.6366 | 5.711 | 5.7835 | 5.8835 | 5.5049 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 5.5873 | -116.8918 | 5.8659 | 5.719 | 0.1317 | -116.8193 | -116.7193 | -0.063436 | -122.6648 | 0.10176 | 0.021467 | 0.084903 | -122.5525 | -122.5173 | 5.7934 | 5.8659 | 5.9659 | 5.8986 | -117.0979 | 0.020393 | 0.13273 | 0.16798 | 0.16517 | -122.7487
|  |  |  | 1.4211e-13 | -0.036829 | -0.00049149 | -0.0036647 | -0.01145 | 0.0067454 | -0.0022892 | -0.0048667 | -0.0029805 | 0.016622 | 0.036468 | 0.010732 | 5.7744 | 5.8025 | 5.6183 | 5.6973 | 5.7698 | 5.8744 | 5.4912 | 0.014784 | 0.073618 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.13668 | 5.5598 | -116.8644 | 5.8431 | 5.687 | 0.12712 | -116.7918 | -116.6873 | -0.068011 | -122.6282 | 0.083449 | 0.003156 | 0.071167 | -122.5159 | -122.4761 | 5.7659 | 5.8385 | 5.943 | 5.8712 | -117.0705 | 0.002083 | 0.11442 | 0.15425 | 0.14228 | -122.6983
|  |  |  | 1.4211e-13 | -0.036615 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.036254 | 0.010518 | 5.7698 | 5.7933 | 5.6229 | 5.6927 | 5.7606 | 5.8744 | 5.4866 | 0.023941 | 0.078197 | -0.06093 | -0.071161 | 0.045757 | 0.081008 | -0.14125 | 5.5919 | -116.9193 | 5.8751 | 5.7282 | 0.13628 | -116.8514 | -116.7376 | -0.035969 | -122.6832 | 0.12923 | 0.044356 | 0.080325 | -122.5662 | -122.531 | 5.798 | 5.8659 | 5.9797 | 5.8986 | -117.1254 | 0.034125 | 0.15104 | 0.18629 | 0.18348 | -122.7533
|  |  |  | 1.4211e-13 | -0.037042 | -6.4092e-05 | -0.0036647 | -0.011664 | 0.006959 | -0.0099192 | -0.0048667 | -0.0023397 | 0.016408 | 0.036681 | 0.010304 | 5.7652 | 5.7888 | 5.6183 | 5.6927 | 5.7561 | 5.8652 | 5.4866 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.054914 | 0.081008 | -0.15041 | 5.569 | -116.8873 | 5.8476 | 5.7007 | 0.1317 | -116.8239 | -116.7147 | -0.068015 | -122.6465 | 0.10634 | 0.016888 | 0.084903 | -122.525 | -122.4989 | 5.7751 | 5.8385 | 5.9476 | 5.8712 | -117.0934 | 0.015815 | 0.13731 | 0.1634 | 0.16975 | -122.7304
|  |  |  | 1.4211e-13 | -0.036829 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0027669 | 0.017049 | 0.036681 | 0.010304 | 5.7652 | 5.7796 | 5.6091 | 5.679 | 5.7515 | 5.8561 | 5.482 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.045757 | 0.081008 | -0.14583 | 5.5507 | -116.901 | 5.8339 | 5.6778 | 0.12712 | -116.8285 | -116.7239 | -0.077168 | -122.642 | 0.092606 | 0.007735 | 0.084903 | -122.5342 | -122.4989 | 5.7476 | 5.8202 | 5.9247 | 5.8483 | -117.0979 | 0.006661 | 0.11442 | 0.14967 | 0.15144 | -122.7258
|  |  |  | 1.4211e-13 | -0.037042 | -6.4092e-05 | -0.0045193 | -0.011023 | 0.0065316 | -0.01755 | -0.0046531 | -0.0025533 | 0.016622 | 0.036681 | 0.010732 | 5.7469 | 5.775 | 5.6046 | 5.6698 | 5.7515 | 5.8423 | 5.4683 | 0.023941 | 0.087354 | -0.06093 | -0.066582 | 0.045757 | 0.085587 | -0.14125 | 5.5919 | -116.933 | 5.8705 | 5.7282 | 0.13628 | -116.8514 | -116.7605 | -0.017659 | -122.6694 | 0.14754 | 0.062666 | 0.080325 | -122.5571 | -122.5173 | 5.7934 | 5.8751 | 5.9659 | 5.8986 | -117.1346 | 0.057014 | 0.16935 | 0.20918 | 0.21095 | -122.7441
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0040921 | -0.011664 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016622 | 0.036468 | 0.010304 | 5.7515 | 5.7704 | 5.5954 | 5.6698 | 5.7423 | 5.8423 | 5.4774 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.14583 | 5.5415 | -116.8781 | 5.8156 | 5.6595 | 0.11796 | -116.8056 | -116.7056 | -0.081746 | -122.6145 | 0.092607 | -0.001422 | 0.080324 | -122.4976 | -122.4623 | 5.7339 | 5.8064 | 5.9064 | 5.8345 | -117.0705 | -0.002495 | 0.11442 | 0.14967 | 0.14228 | -122.6937
|  |  |  | 1.4211e-13 | -0.037042 | -6.4092e-05 | -0.0038783 | -0.011023 | 0.0065316 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.036468 | 0.010945 | 5.7286 | 5.7567 | 5.5862 | 5.6561 | 5.7286 | 5.8377 | 5.45 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.081008 | -0.13668 | 5.5324 | -116.9147 | 5.811 | 5.6686 | 0.13628 | -116.8422 | -116.7331 | -0.054279 | -122.6328 | 0.10634 | 0.021467 | 0.075746 | -122.5159 | -122.4898 | 5.7385 | 5.811 | 5.9201 | 5.8391 | -117.1208 | 0.020393 | 0.13731 | 0.1634 | 0.16517 | -122.7075
|  |  |  | 1.4211e-13 | -0.037256 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.0061044 | -0.02518 | -0.0048667 | -0.0027669 | 0.016408 | 0.036468 | 0.010304 | 5.7286 | 5.7567 | 5.5817 | 5.6515 | 5.724 | 5.824 | 5.4454 | 0.019362 | 0.087354 | -0.056351 | -0.071161 | 0.050335 | 0.081008 | -0.13668 | 5.5141 | -116.9513 | 5.7973 | 5.6503 | 0.13628 | -116.8788 | -116.7788 | -0.068011 | -122.674 | 0.088027 | 0.012314 | 0.080325 | -122.5525 | -122.5218 | 5.7202 | 5.7927 | 5.8927 | 5.8254 | -117.1575 | -0.002496 | 0.119 | 0.14967 | 0.15602 | -122.7395
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0034509 | -0.011236 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.036254 | 0.010304 | 5.7286 | 5.7476 | 5.5725 | 5.6515 | 5.7194 | 5.824 | 5.45 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14125 | 5.5507 | -116.9285 | 5.8293 | 5.6732 | 0.12255 | -116.8605 | -116.7559 | -0.040547 | -122.6465 | 0.12923 | 0.039778 | 0.080325 | -122.525 | -122.4944 | 5.7522 | 5.8201 | 5.9247 | 5.8483 | -117.13 | 0.034126 | 0.15562 | 0.18629 | 0.18806 | -122.7212
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0036647 | -0.011664 | 0.0067454 | -0.01755 | -0.0048667 | -0.0027669 | 0.016408 | 0.036468 | 0.010518 | 5.7195 | 5.743 | 5.5679 | 5.6469 | 5.7149 | 5.8194 | 5.4362 | 0.019362 | 0.082776 | -0.06093 | -0.057425 | 0.050335 | 0.081008 | -0.13668 | 5.5049 | -116.9376 | 5.7881 | 5.6366 | 0.13171 | -116.8697 | -116.7651 | -0.068011 | -122.642 | 0.088027 | 0.007735 | 0.075746 | -122.5342 | -122.5035 | 5.7156 | 5.7835 | 5.8881 | 5.8116 | -117.1483 | 0.01124 | 0.119 | 0.14967 | 0.15144 | -122.7212
|  |  |  | 1.4211e-13 | -0.036829 | -0.00027769 | -0.0034509 | -0.011236 | 0.006318 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016622 | 0.036254 | 0.010091 | 5.7057 | 5.7384 | 5.5679 | 5.6332 | 5.7057 | 5.8103 | 5.4271 | 0.019362 | 0.078197 | -0.065509 | -0.062004 | 0.050335 | 0.081008 | -0.13668 | 5.5049 | -116.9559 | 5.7835 | 5.6458 | 0.14086 | -116.8834 | -116.7788 | -0.058856 | -122.6511 | 0.097182 | 0.012311 | 0.071167 | -122.5388 | -122.5081 | 5.711 | 5.7835 | 5.8881 | 5.8162 | -117.162 | 0.015816 | 0.12815 | 0.15883 | 0.15602 | -122.7258
|  |  |  | 1.4211e-13 | -0.037042 | -0.00049149 | -0.0036647 | -0.011236 | 0.0065316 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016622 | 0.036895 | 0.010518 | 5.7011 | 5.7292 | 5.5588 | 5.624 | 5.6965 | 5.8011 | 5.4362 | 0.023941 | 0.091933 | -0.070087 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 5.5049 | -116.9651 | 5.7698 | 5.6274 | 0.12255 | -116.8926 | -116.788 | -0.077168 | -122.6511 | 0.092606 | -0.001422 | 0.075746 | -122.5388 | -122.5035 | 5.6927 | 5.7652 | 5.8698 | 5.7979 | -117.1529 | 0.006661 | 0.119 | 0.15425 | 0.1606 | -122.7349
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0034509 | -0.011023 | 0.0065316 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.036681 | 0.010304 | 5.6966 | 5.7247 | 5.5496 | 5.624 | 5.6874 | 5.7965 | 5.4179 | 0.033099 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.081008 | -0.13668 | 5.5369 | -116.9697 | 5.8156 | 5.6686 | 0.13171 | -116.9063 | -116.7971 | -0.017657 | -122.6603 | 0.15212 | 0.058089 | 0.075746 | -122.5388 | -122.5127 | 5.743 | 5.8064 | 5.9156 | 5.8437 | -117.1758 | 0.052437 | 0.17393 | 0.20003 | 0.19722 | -122.7304
|  |  |  | 1.4211e-13 | -0.037042 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0065316 | -0.0022892 | -0.0050803 | -0.0025533 | 0.016835 | 0.037109 | 0.010304 | 5.692 | 5.7201 | 5.5359 | 5.6103 | 5.6965 | 5.792 | 5.4179 | 0.019362 | 0.082776 | -0.065509 | -0.057425 | 0.045757 | 0.085587 | -0.14583 | 5.4683 | -116.9605 | 5.7423 | 5.5862 | 0.11797 | -116.8743 | -116.7788 | -0.095479 | -122.6282 | 0.069716 | -0.015155 | 0.080324 | -122.525 | -122.4852 | 5.6606 | 5.7469 | 5.8423 | 5.7704 | -117.1529 | -0.007071 | 0.096111 | 0.13594 | 0.13313 | -122.7166
|  |  |  | 1.4211e-13 | -0.036829 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0065316 | -0.01755 | -0.0046531 | -0.0025533 | 0.016622 | 0.036681 | 0.010518 | 5.6782 | 5.7109 | 5.5359 | 5.6057 | 5.6828 | 5.7782 | 5.4042 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.054914 | 0.081008 | -0.15041 | 5.5324 | -117.0109 | 5.8064 | 5.6641 | 0.13171 | -116.9338 | -116.8384 | -0.022238 | -122.6786 | 0.15669 | 0.062665 | 0.084903 | -122.5617 | -122.5356 | 5.7339 | 5.811 | 5.9064 | 5.8391 | -117.2124 | 0.06617 | 0.18309 | 0.20918 | 0.21095 | -122.767
|  |  |  | 1.4211e-13 | -0.036829 | -0.00027769 | -0.0038783 | -0.01145 | 0.0065316 | -0.0099192 | -0.0050803 | -0.0023397 | 0.016622 | 0.036681 | 0.010732 | 5.6737 | 5.7018 | 5.5267 | 5.5966 | 5.6599 | 5.7645 | 5.395 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.050335 | 0.081008 | -0.14125 | 5.4728 | -116.988 | 5.7515 | 5.6046 | 0.13171 | -116.9246 | -116.82 | -0.063435 | -122.6465 | 0.10634 | 0.012311 | 0.075746 | -122.5342 | -122.5035 | 5.6744 | 5.7377 | 5.8423 | 5.7796 | -117.1895 | 0.015816 | 0.12815 | 0.15883 | 0.15602 | -122.7258
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0038783 | -0.01145 | 0.0067454 | -0.01755 | -0.0052939 | -0.0023397 | 0.016835 | 0.036681 | 0.010518 | 5.6645 | 5.6972 | 5.513 | 5.592 | 5.6599 | 5.7645 | 5.3813 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.050335 | 0.085587 | -0.13668 | 5.4866 | -117.0063 | 5.7698 | 5.6183 | 0.13171 | -116.9384 | -116.8338 | -0.03139 | -122.6694 | 0.13381 | 0.044356 | 0.075746 | -122.5479 | -122.5127 | 5.6973 | 5.7652 | 5.8698 | 5.8025 | -117.217 | 0.034125 | 0.15562 | 0.19087 | 0.18348 | -122.7349
|  |  |  | 1.4211e-13 | -0.037042 | -0.00049149 | -0.0036647 | -0.01145 | 0.0065316 | -0.0099192 | -0.0044395 | -0.0027669 | 0.016408 | 0.036468 | 0.010945 | 5.6554 | 5.6835 | 5.5176 | 5.5828 | 5.6553 | 5.7599 | 5.3767 | 0.019362 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.07643 | -0.14125 | 5.4683 | -117.0154 | 5.7469 | 5.6091 | 0.14087 | -116.9429 | -116.8384 | -0.049702 | -122.6603 | 0.11091 | 0.030623 | 0.080325 | -122.5525 | -122.5218 | 5.6744 | 5.7469 | 5.8515 | 5.775 | -117.2216 | 0.029549 | 0.13731 | 0.16798 | 0.17891 | -122.7395
|  |  |  | 1.4211e-13 | -0.036615 | -0.00027769 | -0.0036647 | -0.011236 | 0.006318 | -0.02518 | -0.0046531 | -0.0025533 | 0.016622 | 0.036681 | 0.010518 | 5.6462 | 5.6743 | 5.5038 | 5.5737 | 5.6416 | 5.7508 | 5.3675 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.054914 | 0.085587 | -0.15041 | 5.4225 | -116.9834 | 5.7011 | 5.5588 | 0.13629 | -116.9155 | -116.8063 | -0.09548 | -122.6236 | 0.078873 | -0.001419 | 0.094061 | -122.5022 | -122.4715 | 5.6286 | 5.6965 | 5.8057 | 5.7292 | -117.1895 | -0.01165 | 0.10985 | 0.14052 | 0.13313 | -122.7075
|  |  |  | 1.4211e-13 | -0.037042 | -6.4092e-05 | -0.0038783 | -0.011664 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016622 | 0.036468 | 0.010304 | 5.6416 | 5.6697 | 5.4947 | 5.5691 | 5.6324 | 5.7462 | 5.363 | 0.023941 | 0.078197 | -0.06093 | -0.052847 | 0.054914 | 0.085587 | -0.13668 | 5.4545 | -117.0246 | 5.7332 | 5.5862 | 0.13172 | -116.9613 | -116.8475 | -0.045123 | -122.6465 | 0.11549 | 0.030623 | 0.075746 | -122.5388 | -122.5081 | 5.6606 | 5.724 | 5.8377 | 5.7613 | -117.2307 | 0.038706 | 0.14647 | 0.17714 | 0.16975 | -122.7304
|  |  |  | 1.4211e-13 | -0.037256 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0065316 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016835 | 0.036681 | 0.010518 | 5.6325 | 5.6651 | 5.4764 | 5.5553 | 5.6279 | 5.7324 | 5.3584 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.041178 | 0.085587 | -0.14583 | 5.4637 | -117.0521 | 5.7378 | 5.5817 | 0.11798 | -116.9796 | -116.875 | -0.040547 | -122.674 | 0.12923 | 0.044356 | 0.084903 | -122.5662 | -122.5218 | 5.6606 | 5.7331 | 5.8377 | 5.7704 | -117.249 | 0.038704 | 0.14646 | 0.19087 | 0.18348 | -122.7533
|  |  |  | 1.4211e-13 | -0.037256 | -6.4092e-05 | -0.0034509 | -0.01145 | 0.0065316 | -0.02518 | -0.0044395 | -0.0025533 | 0.016622 | 0.036895 | 0.010304 | 5.6233 | 5.6468 | 5.4764 | 5.5508 | 5.6187 | 5.7324 | 5.3401 | 0.023941 | 0.082776 | -0.06093 | -0.071161 | 0.045757 | 0.07643 | -0.14583 | 5.427 | -117.0475 | 5.7103 | 5.5633 | 0.1363 | -116.9796 | -116.8658 | -0.058858 | -122.6694 | 0.11092 | 0.026045 | 0.084903 | -122.5525 | -122.5218 | 5.6377 | 5.7057 | 5.8194 | 5.7338 | -117.2582 | 0.015814 | 0.13273 | 0.1634 | 0.16975 | -122.7441
|  |  |  | 1.4211e-13 | -0.037256 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016408 | 0.036895 | 0.010732 | 5.6187 | 5.6514 | 5.4672 | 5.537 | 5.6187 | 5.7233 | 5.3401 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.045757 | 0.090166 | -0.14125 | 5.4545 | -117.0383 | 5.7332 | 5.5817 | 0.12714 | -116.9567 | -116.8521 | -0.026814 | -122.6374 | 0.14296 | 0.048932 | 0.075746 | -122.5296 | -122.4852 | 5.6515 | 5.7331 | 5.8377 | 5.7658 | -117.2353 | 0.052437 | 0.1602 | 0.20461 | 0.19264 | -122.7166
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0036647 | -0.011236 | 0.0065316 | -0.0099192 | -0.0046531 | -0.0029805 | 0.016835 | 0.036681 | 0.010518 | 5.6142 | 5.6377 | 5.4581 | 5.5325 | 5.6095 | 5.7141 | 5.3309 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.050335 | 0.085587 | -0.13668 | 5.3996 | -117.0155 | 5.6828 | 5.5267 | 0.12714 | -116.9384 | -116.8338 | -0.068011 | -122.6099 | 0.092606 | 0.012314 | 0.080325 | -122.4976 | -122.4623 | 5.6011 | 5.6782 | 5.7828 | 5.7063 | -117.217 | 0.006661 | 0.119 | 0.15425 | 0.15602 | -122.6846
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0036647 | -0.011236 | 0.0065316 | -0.0022892 | -0.0048667 | -0.0023397 | 0.016622 | 0.036895 | 0.010304 | 5.605 | 5.6377 | 5.4535 | 5.5325 | 5.5958 | 5.7095 | 5.3263 | 0.02852 | 0.082776 | -0.070087 | -0.066582 | 0.050335 | 0.07643 | -0.13668 | 5.4454 | -117.0841 | 5.724 | 5.5725 | 0.12714 | -117.0208 | -116.907 | -0.017657 | -122.6832 | 0.14754 | 0.048932 | 0.066589 | -122.5662 | -122.5401 | 5.6515 | 5.7148 | 5.8286 | 5.7567 | -117.2902 | 0.052437 | 0.16935 | 0.19545 | 0.2018 | -122.7533
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0034509 | -0.011023 | 0.0065316 | -0.02518 | -0.0046531 | -0.0023397 | 0.017049 | 0.036468 | 0.010732 | 5.5958 | 5.6285 | 5.4489 | 5.5187 | 5.6004 | 5.7004 | 5.3172 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.050335 | 0.081008 | -0.14125 | 5.4042 | -117.0612 | 5.6828 | 5.5359 | 0.13172 | -116.9796 | -116.8796 | -0.05428 | -122.642 | 0.11092 | 0.026045 | 0.080325 | -122.5296 | -122.4989 | 5.6057 | 5.6874 | 5.7874 | 5.7155 | -117.2628 | 0.024971 | 0.13731 | 0.16798 | 0.16517 | -122.7212
|  |  |  | 1.4211e-13 | -0.037042 | -6.4092e-05 | -0.0034509 | -0.011236 | 0.0065316 | -0.01755 | -0.0046531 | -0.0025533 | 0.016622 | 0.036681 | 0.010732 | 5.5867 | 5.6239 | 5.4535 | 5.5187 | 5.5912 | 5.6958 | 5.3218 | 0.02852 | 0.082776 | -0.06093 | -0.071161 | 0.050335 | 0.085587 | -0.14125 | 5.3904 | -117.107 | 5.6553 | 5.5221 | 0.13172 | -117.0345 | -116.9299 | -0.07259 | -122.6969 | 0.097185 | 0.007735 | 0.080325 | -122.5754 | -122.5401 | 5.5874 | 5.6599 | 5.7645 | 5.6926 | -117.304 | -0.002496 | 0.119 | 0.15425 | 0.15144 | -122.767
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0036647 | -0.01145 | 0.0061044 | -0.01755 | -0.0044395 | -0.0029805 | 0.016195 | 0.036895 | 0.010304 | 5.5867 | 5.6194 | 5.4397 | 5.5187 | 5.5912 | 5.6912 | 5.3126 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.054914 | 0.090166 | -0.14583 | 5.3675 | -117.075 | 5.6416 | 5.4947 | 0.12714 | -117.0025 | -116.9025 | -0.090901 | -122.6603 | 0.078873 | -0.010577 | 0.080324 | -122.5388 | -122.5035 | 5.5737 | 5.6462 | 5.7462 | 5.6743 | -117.2811 | -0.01165 | 0.10985 | 0.1451 | 0.13313 | -122.7395
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0036647 | -0.011236 | 0.0065316 | -0.01755 | -0.0050803 | -0.0025533 | 0.016622 | 0.037109 | 0.010304 | 5.5821 | 5.6056 | 5.4443 | 5.505 | 5.5775 | 5.6867 | 5.308 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.050335 | 0.090166 | -0.13668 | 5.3721 | -117.0795 | 5.6462 | 5.5084 | 0.1363 | -117.007 | -116.8979 | -0.072589 | -122.6557 | 0.083449 | -0.001422 | 0.071167 | -122.5342 | -122.4944 | 5.5691 | 5.6416 | 5.7507 | 5.6697 | -117.2765 | -0.007074 | 0.11442 | 0.15425 | 0.14228 | -122.7212
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0034509 | -0.011664 | 0.006318 | -0.01755 | -0.0046531 | -0.0025533 | 0.016835 | 0.037109 | 0.010304 | 5.5729 | 5.5965 | 5.4306 | 5.505 | 5.5683 | 5.6821 | 5.2989 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.050335 | 0.090166 | -0.14583 | 5.395 | -117.0933 | 5.6691 | 5.5267 | 0.13173 | -117.0299 | -116.9162 | -0.049703 | -122.6603 | 0.12007 | 0.030621 | 0.080324 | -122.5479 | -122.5081 | 5.6011 | 5.6645 | 5.7782 | 5.6926 | -117.2994 | 0.034126 | 0.14646 | 0.1863 | 0.17433 | -122.7441
|  |  |  | 1.4211e-13 | -0.03747 | -6.4092e-05 | -0.0034509 | -0.01145 | 0.006318 | -0.0022892 | -0.0046531 | -0.0023397 | 0.016835 | 0.036895 | 0.010304 | 5.5775 | 5.5965 | 5.4169 | 5.4958 | 5.5683 | 5.6775 | 5.2943 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.054914 | 0.081008 | -0.15041 | 5.395 | -117.1207 | 5.6782 | 5.5176 | 0.12257 | -117.0482 | -116.9391 | -0.049704 | -122.6786 | 0.12007 | 0.044357 | 0.094061 | -122.5617 | -122.5356 | 5.5965 | 5.669 | 5.7782 | 5.6972 | -117.3223 | 0.038704 | 0.15562 | 0.18172 | 0.18348 | -122.767
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0034509 | -0.011236 | 0.0065316 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.036468 | 0.010518 | 5.5592 | 5.5965 | 5.4123 | 5.4913 | 5.5638 | 5.6683 | 5.2897 | 0.02852 | 0.091933 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.14583 | 5.3721 | -117.0704 | 5.6416 | 5.4947 | 0.12257 | -116.9979 | -116.8933 | -0.063436 | -122.6282 | 0.11092 | 0.021467 | 0.084903 | -122.5159 | -122.4806 | 5.5736 | 5.6461 | 5.7507 | 5.6789 | -117.2719 | 0.015815 | 0.12815 | 0.1634 | 0.17433 | -122.7075
|  |  |  | 1.4211e-13 | -0.037042 | 0.00014951 | -0.0038783 | -0.01145 | 0.0061044 | -0.0022892 | -0.0048667 | -0.0027669 | 0.016622 | 0.036895 | 0.010304 | 5.5592 | 5.5827 | 5.4077 | 5.4867 | 5.5638 | 5.6592 | 5.2805 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.13668 | 5.3401 | -117.075 | 5.6187 | 5.4672 | 0.12715 | -116.9979 | -116.9025 | -0.077167 | -122.6236 | 0.088029 | -0.001421 | 0.075746 | -122.5067 | -122.4761 | 5.5462 | 5.6233 | 5.7187 | 5.6422 | -117.2811 | -0.002495 | 0.11442 | 0.1451 | 0.13771 | -122.6983
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0036647 | -0.011023 | 0.006318 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016408 | 0.036681 | 0.010304 | 5.5455 | 5.5736 | 5.4031 | 5.4729 | 5.5454 | 5.6546 | 5.276 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.1321 | 5.3996 | -117.1253 | 5.6691 | 5.5267 | 0.12715 | -117.0528 | -116.9437 | -0.008501 | -122.6603 | 0.14754 | 0.062666 | 0.071167 | -122.5388 | -122.5127 | 5.5965 | 5.669 | 5.7782 | 5.6972 | -117.3223 | 0.061592 | 0.18309 | 0.20918 | 0.20179 | -122.7304
|  |  |  | 1.4211e-13 | -0.037256 | -6.4092e-05 | -0.0038783 | -0.011236 | 0.0065316 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016835 | 0.036895 | 0.010518 | 5.5409 | 5.5644 | 5.3985 | 5.4729 | 5.5409 | 5.6363 | 5.2668 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.090166 | -0.14125 | 5.3629 | -117.1482 | 5.637 | 5.4947 | 0.13173 | -117.0803 | -116.9849 | -0.045125 | -122.6877 | 0.12007 | 0.0352 | 0.080325 | -122.5708 | -122.531 | 5.5691 | 5.637 | 5.7324 | 5.6605 | -117.3543 | 0.029548 | 0.14646 | 0.1863 | 0.17891 | -122.7624
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0034509 | -0.011236 | 0.0065316 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.036895 | 0.010304 | 5.5409 | 5.569 | 5.394 | 5.4729 | 5.5363 | 5.6454 | 5.2714 | 0.023941 | 0.082776 | -0.070087 | -0.062004 | 0.059493 | 0.085587 | -0.13668 | 5.3446 | -117.1208 | 5.6141 | 5.4672 | 0.12257 | -117.0574 | -116.9482 | -0.063434 | -122.6557 | 0.097183 | 0.003155 | 0.066589 | -122.5342 | -122.5081 | 5.5462 | 5.6095 | 5.7187 | 5.6422 | -117.3223 | 0.011238 | 0.13273 | 0.15883 | 0.15602 | -122.7304
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0032373 | -0.011023 | 0.006318 | -0.02518 | -0.0046531 | -0.0025533 | 0.016622 | 0.036895 | 0.010518 | 5.5363 | 5.5598 | 5.3848 | 5.4684 | 5.5271 | 5.6363 | 5.2577 | 0.014784 | 0.082776 | -0.065509 | -0.066582 | 0.054914 | 0.090166 | -0.14125 | 5.3492 | -117.1482 | 5.6279 | 5.4764 | 0.12715 | -117.0895 | -116.9803 | -0.049702 | -122.6832 | 0.10634 | 0.026044 | 0.075746 | -122.5617 | -122.5264 | 5.5599 | 5.6187 | 5.7278 | 5.6514 | -117.3589 | 0.024971 | 0.14647 | 0.18172 | 0.17433 | -122.7578
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0036647 | -0.011664 | 0.006318 | -0.01755 | -0.0050803 | -0.0023397 | 0.016835 | 0.036681 | 0.010304 | 5.5272 | 5.5598 | 5.3802 | 5.4546 | 5.5225 | 5.6271 | 5.2577 | 0.023941 | 0.073618 | -0.06093 | -0.062004 | 0.050335 | 0.090166 | -0.14125 | 5.3263 | -117.162 | 5.5958 | 5.4489 | 0.12257 | -117.094 | -116.9894 | -0.07259 | -122.6786 | 0.092606 | 0.007735 | 0.080325 | -122.5662 | -122.5264 | 5.5233 | 5.5912 | 5.6958 | 5.6285 | -117.3589 | 0.006661 | 0.119 | 0.15883 | 0.14228 | -122.7578
|  |  |  | 1.4211e-13 | -0.03747 | -6.4092e-05 | -0.0040921 | -0.011236 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0023397 | 0.016622 | 0.036681 | 0.010304 | 5.5272 | 5.5507 | 5.3802 | 5.45 | 5.5317 | 5.618 | 5.2485 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.045757 | 0.085587 | -0.14583 | 5.3355 | -117.162 | 5.6141 | 5.4672 | 0.13173 | -117.0803 | -116.994 | -0.058858 | -122.674 | 0.10634 | 0.030624 | 0.089482 | -122.5662 | -122.5264 | 5.537 | 5.6187 | 5.705 | 5.6376 | -117.3635 | 0.024971 | 0.13273 | 0.17256 | 0.16975 | -122.7578
|  |  |  | 1.4211e-13 | -0.037042 | -0.00049149 | -0.0036647 | -0.011236 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016408 | 0.036681 | 0.010518 | 5.5272 | 5.5598 | 5.3756 | 5.4546 | 5.5134 | 5.6271 | 5.2531 | 0.023941 | 0.082776 | -0.070087 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 5.3675 | -117.1665 | 5.6416 | 5.4901 | 0.12258 | -117.1078 | -116.994 | -0.026814 | -122.6877 | 0.13838 | 0.044354 | 0.071168 | -122.5662 | -122.5401 | 5.5691 | 5.6278 | 5.7416 | 5.6743 | -117.3681 | 0.047859 | 0.16936 | 0.19545 | 0.19722 | -122.7624
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0043057 | -0.011664 | 0.0065316 | -0.01755 | -0.0048667 | -0.0027669 | 0.016408 | 0.036895 | 0.010091 | 5.518 | 5.5461 | 5.3619 | 5.4455 | 5.5088 | 5.618 | 5.2393 | 0.023941 | 0.087354 | -0.065509 | -0.066582 | 0.059493 | 0.085587 | -0.13668 | 5.308 | -117.1482 | 5.5867 | 5.4306 | 0.12258 | -117.0849 | -116.9757 | -0.068011 | -122.6603 | 0.092606 | 0.003156 | 0.071167 | -122.5342 | -122.5081 | 5.5141 | 5.5775 | 5.6866 | 5.6148 | -117.3544 | 0.002083 | 0.12816 | 0.15425 | 0.15602 | -122.7304
|  |  |  | 1.4211e-13 | -0.037042 | -0.00027769 | -0.0038783 | -0.01145 | 0.0065316 | -0.01755 | -0.0052939 | -0.0027669 | 0.016408 | 0.036895 | 0.010518 | 5.518 | 5.5507 | 5.3665 | 5.4409 | 5.518 | 5.6134 | 5.2348 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14125 | 5.3355 | -117.1803 | 5.6187 | 5.4672 | 0.13173 | -117.1032 | -117.0078 | -0.040547 | -122.6832 | 0.12923 | 0.039778 | 0.080325 | -122.5662 | -122.531 | 5.5416 | 5.6187 | 5.7141 | 5.6514 | -117.3864 | 0.038704 | 0.15562 | 0.19087 | 0.18348 | -122.7624
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0036647 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016622 | 0.036895 | 0.010518 | 5.5088 | 5.5369 | 5.3482 | 5.4317 | 5.5088 | 5.6042 | 5.2302 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.3034 | -117.1665 | 5.5821 | 5.4214 | 0.118 | -117.0895 | -116.994 | -0.063434 | -122.6648 | 0.097183 | 0.007733 | 0.071167 | -122.5479 | -122.5173 | 5.505 | 5.582 | 5.6775 | 5.6102 | -117.3681 | 0.00666 | 0.12358 | 0.15425 | 0.15602 | -122.7349
|  |  |  | 1.4211e-13 | -0.037256 | -0.00070509 | -0.0038783 | -0.011236 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0023397 | 0.016622 | 0.036895 | 0.010518 | 5.4997 | 5.5278 | 5.3482 | 5.4272 | 5.4996 | 5.5997 | 5.221 | 0.019362 | 0.078197 | -0.065509 | -0.052847 | 0.045757 | 0.085587 | -0.13668 | 5.2897 | -117.1528 | 5.5684 | 5.4168 | 0.12716 | -117.0803 | -116.9803 | -0.068011 | -122.6328 | 0.088027 | 0.003156 | 0.071167 | -122.5342 | -122.4944 | 5.4958 | 5.5683 | 5.6683 | 5.5964 | -117.3589 | 0.015818 | 0.11442 | 0.15425 | 0.14686 | -122.7166
|  |  |  | 1.4211e-13 | -0.037256 | -0.00049149 | -0.0036647 | -0.011236 | 0.0065316 | -0.01755 | -0.0044395 | -0.0025533 | 0.016408 | 0.036895 | 0.010732 | 5.4768 | 5.5186 | 5.339 | 5.4088 | 5.4859 | 5.5997 | 5.2119 | 0.023941 | 0.073618 | -0.070087 | -0.062004 | 0.054914 | 0.081008 | -0.14583 | 5.2851 | -117.1848 | 5.55 | 5.4123 | 0.12716 | -117.1078 | -116.994 | -0.072591 | -122.6557 | 0.097183 | 0.003155 | 0.075746 | -122.5388 | -122.5127 | 5.4821 | 5.5592 | 5.6729 | 5.5919 | -117.3818 | 0.011238 | 0.12816 | 0.15425 | 0.14686 | -122.7395
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0034509 | -0.01145 | 0.0061044 | -0.01755 | -0.0050803 | -0.0025533 | 0.016408 | 0.036895 | 0.010304 | 5.4768 | 5.514 | 5.339 | 5.4088 | 5.4813 | 5.5859 | 5.2164 | 0.019362 | 0.087354 | -0.056351 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 5.3172 | -117.2032 | 5.5775 | 5.4397 | 0.12258 | -117.1307 | -117.0261 | -0.045125 | -122.674 | 0.12007 | 0.044357 | 0.089482 | -122.5617 | -122.5264 | 5.5095 | 5.582 | 5.6866 | 5.6148 | -117.3956 | 0.038704 | 0.15104 | 0.18629 | 0.18806 | -122.7578
|  |  |  | 1.4211e-13 | -0.037256 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.006318 | -0.0022892 | -0.0046531 | -0.0027669 | 0.016622 | 0.036468 | 0.010304 | 5.4768 | 5.5095 | 5.3299 | 5.3905 | 5.4722 | 5.5813 | 5.1981 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 5.2622 | -117.1894 | 5.5409 | 5.394 | 0.13174 | -117.1078 | -116.9986 | -0.081746 | -122.642 | 0.088028 | -0.001422 | 0.080324 | -122.5296 | -122.4944 | 5.4546 | 5.5363 | 5.6454 | 5.5736 | -117.3818 | 0.002083 | 0.11442 | 0.14967 | 0.14228 | -122.7258
|  |  |  | 1.4211e-13 | -0.037042 | -0.00049149 | -0.0036647 | -0.011236 | 0.0065316 | -0.02518 | -0.0048667 | -0.0025533 | 0.016622 | 0.036681 | 0.010304 | 5.4585 | 5.5003 | 5.3161 | 5.3951 | 5.4676 | 5.563 | 5.1981 | 0.023941 | 0.078197 | -0.070087 | -0.066582 | 0.059493 | 0.090166 | -0.14125 | 5.2668 | -117.2123 | 5.5272 | 5.3848 | 0.118 | -117.1398 | -117.0444 | -0.07259 | -122.674 | 0.092606 | -0.001422 | 0.071168 | -122.5479 | -122.5173 | 5.4638 | 5.5363 | 5.6317 | 5.569 | -117.4093 | 0.002083 | 0.12816 | 0.15883 | 0.14686 | -122.7487
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0038783 | -0.011664 | 0.0065316 | -0.01755 | -0.0048667 | -0.0025533 | 0.016408 | 0.037109 | 0.010304 | 5.4585 | 5.4957 | 5.3207 | 5.3951 | 5.463 | 5.5722 | 5.1935 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.14125 | 5.3126 | -117.2535 | 5.5775 | 5.4397 | 0.12716 | -117.1856 | -117.0764 | -0.022236 | -122.7106 | 0.14296 | 0.058089 | 0.080325 | -122.5937 | -122.563 | 5.5141 | 5.582 | 5.6912 | 5.6147 | -117.4551 | 0.057015 | 0.17393 | 0.20461 | 0.19722 | -122.7899
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0036647 | -0.01145 | 0.0065316 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.036468 | 0.010304 | 5.4585 | 5.4912 | 5.3116 | 5.3814 | 5.463 | 5.5585 | 5.189 | 0.023941 | 0.087354 | -0.06093 | -0.062004 | 0.045757 | 0.07643 | -0.14125 | 5.2943 | -117.2123 | 5.5638 | 5.4168 | 0.12258 | -117.1307 | -117.0352 | -0.035969 | -122.6557 | 0.12923 | 0.044356 | 0.080325 | -122.5479 | -122.5173 | 5.4867 | 5.5683 | 5.6637 | 5.5964 | -117.4047 | 0.043282 | 0.15104 | 0.18172 | 0.19264 | -122.7349
|  |  |  | 1.4211e-13 | -0.037042 | -0.00049149 | -0.0036647 | -0.011236 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016408 | 0.036895 | 0.010518 | 5.4493 | 5.482 | 5.3024 | 5.3768 | 5.4401 | 5.5493 | 5.1798 | 0.019362 | 0.087354 | -0.056351 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 5.2851 | -117.2444 | 5.5546 | 5.4077 | 0.12258 | -117.181 | -117.0719 | -0.035969 | -122.6877 | 0.12465 | 0.048935 | 0.084904 | -122.5662 | -122.5401 | 5.4821 | 5.5454 | 5.6546 | 5.5873 | -117.4413 | 0.038704 | 0.1602 | 0.18629 | 0.19264 | -122.7624
|  |  |  | 1.4211e-13 | -0.037683 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0029805 | 0.016622 | 0.037109 | 0.010304 | 5.4356 | 5.4774 | 5.2932 | 5.3676 | 5.4447 | 5.5493 | 5.1707 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.2576 | -117.2444 | 5.5226 | 5.3802 | 0.12259 | -117.1673 | -117.0627 | -0.049701 | -122.6786 | 0.10634 | 0.021466 | 0.071167 | -122.5617 | -122.531 | 5.4546 | 5.5317 | 5.6363 | 5.5644 | -117.4413 | 0.020393 | 0.13731 | 0.16798 | 0.16975 | -122.7487
|  |  |  | 1.4211e-13 | -0.037256 | -0.00049149 | -0.0036647 | -0.011664 | 0.0067454 | -0.0099192 | -0.0046531 | -0.0029805 | 0.016195 | 0.037109 | 0.010091 | 5.431 | 5.4683 | 5.2841 | 5.3631 | 5.4355 | 5.5493 | 5.1615 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.045757 | 0.085587 | -0.1321 | 5.2118 | -117.2444 | 5.4814 | 5.3344 | 0.12259 | -117.1719 | -117.0581 | -0.081743 | -122.6786 | 0.069716 | -0.015155 | 0.066588 | -122.5617 | -122.5218 | 5.4134 | 5.4859 | 5.5996 | 5.5186 | -117.4459 | -0.020807 | 0.096111 | 0.13594 | 0.12855 | -122.7395
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0040921 | -0.011664 | 0.006318 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016622 | 0.036895 | 0.010304 | 5.4219 | 5.4545 | 5.2795 | 5.3493 | 5.4264 | 5.531 | 5.1569 | 0.019362 | 0.078197 | -0.070087 | -0.066582 | 0.054914 | 0.085587 | -0.14125 | 5.2164 | -117.2444 | 5.4814 | 5.339 | 0.12259 | -117.1673 | -117.0627 | -0.081746 | -122.6603 | 0.078871 | -0.010578 | 0.071168 | -122.5388 | -122.5081 | 5.4088 | 5.4859 | 5.5905 | 5.514 | -117.4368 | -0.007073 | 0.11442 | 0.1451 | 0.13771 | -122.7349
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0038783 | -0.011236 | 0.006318 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.037109 | 0.010304 | 5.4219 | 5.4545 | 5.2749 | 5.3585 | 5.4218 | 5.5264 | 5.1615 | 0.02852 | 0.078197 | -0.070087 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 5.2714 | -117.2673 | 5.5317 | 5.3848 | 0.11343 | -117.2039 | -117.0993 | -0.03597 | -122.6832 | 0.13838 | 0.039776 | 0.075746 | -122.5662 | -122.5401 | 5.4683 | 5.5317 | 5.6363 | 5.5644 | -117.4642 | 0.052438 | 0.16936 | 0.19545 | 0.18806 | -122.7716
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0036647 | -0.01145 | 0.0061044 | -0.0022892 | -0.0048667 | -0.0029805 | 0.016835 | 0.036895 | 0.010304 | 5.4219 | 5.4545 | 5.2749 | 5.3493 | 5.4172 | 5.5356 | 5.1478 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14583 | 5.221 | -117.2398 | 5.4951 | 5.3482 | 0.12717 | -117.1719 | -117.0536 | -0.072591 | -122.6557 | 0.10176 | 0.012312 | 0.084903 | -122.5342 | -122.5035 | 5.4226 | 5.4905 | 5.6088 | 5.5278 | -117.4414 | 0.00666 | 0.12816 | 0.15883 | 0.15602 | -122.7349
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0038783 | -0.011236 | 0.0065316 | -0.02518 | -0.0046531 | -0.0025533 | 0.016622 | 0.037322 | 0.010304 | 5.4127 | 5.4499 | 5.2703 | 5.3447 | 5.4126 | 5.5218 | 5.1386 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.090166 | -0.15041 | 5.2485 | -117.2856 | 5.5226 | 5.3802 | 0.13175 | -117.2177 | -117.1085 | -0.040549 | -122.6969 | 0.1338 | 0.048933 | 0.089482 | -122.5754 | -122.5401 | 5.4546 | 5.5225 | 5.6317 | 5.5598 | -117.4917 | 0.043281 | 0.16478 | 0.20003 | 0.19264 | -122.7807
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0038783 | -0.01145 | 0.0065316 | -0.0099192 | -0.0044395 | -0.0029805 | 0.016408 | 0.036895 | 0.010304 | 5.4127 | 5.4362 | 5.2566 | 5.331 | 5.4081 | 5.5172 | 5.1294 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.050335 | 0.085587 | -0.13668 | 5.2118 | -117.2856 | 5.4951 | 5.339 | 0.12717 | -117.2085 | -117.0993 | -0.054279 | -122.6877 | 0.10634 | 0.016888 | 0.071167 | -122.5662 | -122.531 | 5.4134 | 5.4905 | 5.5996 | 5.5186 | -117.4871 | 0.011236 | 0.13273 | 0.16798 | 0.16517 | -122.7533
|  |  |  | 1.4211e-13 | -0.036829 | -0.00070509 | -0.0038783 | -0.011236 | 0.006318 | -0.01755 | -0.0048667 | -0.0027669 | 0.016622 | 0.036681 | 0.010091 | 5.399 | 5.4362 | 5.2566 | 5.3219 | 5.4035 | 5.5035 | 5.1294 | 0.019362 | 0.078197 | -0.056351 | -0.057425 | 0.050335 | 0.090166 | -0.13668 | 5.2073 | -117.2856 | 5.4768 | 5.3344 | 0.12717 | -117.2039 | -117.1039 | -0.058856 | -122.6648 | 0.097182 | 0.021469 | 0.080325 | -122.5571 | -122.5173 | 5.3997 | 5.4813 | 5.5813 | 5.514 | -117.478 | 0.020395 | 0.12815 | 0.16799 | 0.15602 | -122.7441
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0040921 | -0.01145 | 0.006318 | -0.01755 | -0.0048667 | -0.0021259 | 0.016622 | 0.036895 | 0.010091 | 5.3898 | 5.4271 | 5.2566 | 5.3173 | 5.3989 | 5.5127 | 5.1203 | 0.019362 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.085587 | -0.1321 | 5.2073 | -117.2764 | 5.4768 | 5.3436 | 0.13633 | -117.1948 | -117.081 | -0.045122 | -122.6511 | 0.10634 | 0.021466 | 0.066588 | -122.5388 | -122.5081 | 5.4042 | 5.4859 | 5.5996 | 5.514 | -117.4734 | 0.02955 | 0.14189 | 0.17256 | 0.16975 | -122.7258
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0036647 | -0.011236 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0025533 | 0.016622 | 0.037109 | 0.010304 | 5.3852 | 5.4225 | 5.2383 | 5.3173 | 5.3898 | 5.5035 | 5.1294 | 0.023941 | 0.078197 | -0.056351 | -0.071161 | 0.050335 | 0.085587 | -0.14583 | 5.2256 | -117.281 | 5.4814 | 5.3344 | 0.10886 | -117.2085 | -117.0948 | -0.049703 | -122.6694 | 0.12007 | 0.039779 | 0.089482 | -122.5479 | -122.5127 | 5.4134 | 5.4859 | 5.5996 | 5.5186 | -117.4688 | 0.024969 | 0.14646 | 0.18172 | 0.17433 | -122.7441
|  |  |  | 1.4211e-13 | -0.037683 | -6.4092e-05 | -0.0036647 | -0.011023 | 0.0065316 | -0.01755 | -0.0046531 | -0.0025533 | 0.016195 | 0.037322 | 0.010091 | 5.3761 | 5.4087 | 5.2383 | 5.3081 | 5.3806 | 5.4852 | 5.1111 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.045757 | 0.085587 | -0.14583 | 5.1569 | -117.3039 | 5.4219 | 5.2841 | 0.12717 | -117.2314 | -117.1268 | -0.10006 | -122.674 | 0.065138 | -0.015154 | 0.084903 | -122.5662 | -122.5264 | 5.3539 | 5.4264 | 5.531 | 5.4545 | -117.5009 | -0.016228 | 0.091533 | 0.13136 | 0.12397 | -122.7578
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0034509 | -0.01145 | 0.0065316 | -0.01755 | -0.0048667 | -0.0025533 | 0.016195 | 0.036895 | 0.010304 | 5.3669 | 5.4042 | 5.2246 | 5.2944 | 5.3714 | 5.4852 | 5.102 | 0.02852 | 0.087354 | -0.065509 | -0.057425 | 0.045757 | 0.071851 | -0.14125 | 5.1523 | -117.2947 | 5.4173 | 5.2749 | 0.1226 | -117.2177 | -117.1039 | -0.090901 | -122.6465 | 0.078874 | -0.015155 | 0.075746 | -122.5434 | -122.5173 | 5.3447 | 5.4218 | 5.5355 | 5.4545 | -117.4871 | -0.007071 | 0.096111 | 0.12221 | 0.13771 | -122.7304
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0036647 | -0.01145 | 0.0065316 | -0.0099192 | -0.0050803 | -0.0023397 | 0.016622 | 0.036468 | 0.010518 | 5.3623 | 5.3996 | 5.2246 | 5.2898 | 5.3623 | 5.4669 | 5.0974 | 0.023941 | 0.073618 | -0.06093 | -0.066582 | 0.054914 | 0.081008 | -0.14125 | 5.221 | -117.3634 | 5.4859 | 5.3482 | 0.12717 | -117.2909 | -117.1863 | -0.017659 | -122.7198 | 0.14754 | 0.062666 | 0.080325 | -122.5983 | -122.5722 | 5.4134 | 5.4859 | 5.5905 | 5.5232 | -117.5558 | 0.057014 | 0.17851 | 0.2046 | 0.19721 | -122.7945
|  |  |  | 1.4211e-13 | -0.03747 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.006318 | -0.01755 | -0.0048667 | -0.0025533 | 0.016408 | 0.037109 | 0.010091 | 5.3532 | 5.3858 | 5.2108 | 5.2852 | 5.3577 | 5.4623 | 5.0882 | 0.02852 | 0.082776 | -0.056351 | -0.062004 | 0.050335 | 0.090166 | -0.13668 | 5.1706 | -117.2947 | 5.4356 | 5.2932 | 0.1226 | -117.2223 | -117.1177 | -0.054279 | -122.642 | 0.11092 | 0.026046 | 0.080325 | -122.5296 | -122.4898 | 5.3676 | 5.4401 | 5.5447 | 5.4682 | -117.4917 | 0.020393 | 0.13273 | 0.17256 | 0.16517 | -122.7166
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0038783 | -0.011664 | 0.0067454 | -0.0099192 | -0.0050803 | -0.0025533 | 0.016622 | 0.036895 | 0.0098772 | 5.3394 | 5.3721 | 5.1925 | 5.2715 | 5.3485 | 5.444 | 5.0745 | 0.019362 | 0.087354 | -0.065509 | -0.057425 | 0.054914 | 0.094744 | -0.14583 | 5.1386 | -117.3314 | 5.4035 | 5.2566 | 0.11802 | -117.2543 | -117.1589 | -0.081746 | -122.6603 | 0.083449 | -0.001422 | 0.080324 | -122.5479 | -122.5081 | 5.3356 | 5.4126 | 5.5081 | 5.4362 | -117.5283 | 0.006662 | 0.119 | 0.15883 | 0.15144 | -122.7487
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0038783 | -0.011664 | 0.0067454 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.037109 | 0.010304 | 5.3349 | 5.3675 | 5.1834 | 5.2715 | 5.3394 | 5.444 | 5.0653 | 0.010205 | 0.087354 | -0.056351 | -0.066582 | 0.054914 | 0.081008 | -0.14583 | 5.1432 | -117.3497 | 5.4127 | 5.2612 | 0.11802 | -117.2818 | -117.1772 | -0.068013 | -122.6877 | 0.088025 | 0.021469 | 0.089482 | -122.5662 | -122.5401 | 5.3493 | 5.4172 | 5.5218 | 5.4453 | -117.5558 | 0.011238 | 0.13273 | 0.15883 | 0.16517 | -122.767
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0038783 | -0.011236 | 0.006318 | -0.01755 | -0.0048667 | -0.0027669 | 0.016622 | 0.037109 | 0.010304 | 5.3257 | 5.3629 | 5.1879 | 5.2578 | 5.3302 | 5.444 | 5.0653 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.054914 | 0.085587 | -0.15041 | 5.1477 | -117.3634 | 5.4081 | 5.2703 | 0.1226 | -117.2909 | -117.1772 | -0.068015 | -122.6877 | 0.10634 | 0.016888 | 0.084903 | -122.5662 | -122.5356 | 5.3402 | 5.4126 | 5.5264 | 5.4453 | -117.5558 | 0.015815 | 0.13731 | 0.16798 | 0.16517 | -122.7716
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0036647 | -0.011877 | 0.006318 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016408 | 0.037109 | 0.010091 | 5.3257 | 5.3584 | 5.1788 | 5.2578 | 5.3256 | 5.4348 | 5.0608 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.045757 | 0.081008 | -0.14583 | 5.1248 | -117.3314 | 5.3898 | 5.2429 | 0.11802 | -117.2635 | -117.1543 | -0.081746 | -122.6557 | 0.092607 | 0.003157 | 0.084903 | -122.5434 | -122.5081 | 5.3218 | 5.3897 | 5.4989 | 5.4225 | -117.5284 | -0.002495 | 0.10984 | 0.1451 | 0.14686 | -122.7349
|  |  |  | 1.4211e-13 | -0.037683 | -0.00070509 | -0.0038783 | -0.01145 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016622 | 0.037109 | 0.010091 | 5.3211 | 5.3584 | 5.1834 | 5.244 | 5.3165 | 5.4211 | 5.0608 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.13668 | 5.1615 | -117.3817 | 5.4218 | 5.2841 | 0.1226 | -117.3092 | -117.2046 | -0.035968 | -122.6923 | 0.12923 | 0.039778 | 0.075746 | -122.5754 | -122.5447 | 5.3447 | 5.4172 | 5.5218 | 5.4591 | -117.565 | 0.034126 | 0.15104 | 0.18172 | 0.17891 | -122.7624
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0036647 | -0.01145 | 0.006318 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016408 | 0.036681 | 0.010304 | 5.3074 | 5.3538 | 5.165 | 5.2394 | 5.3256 | 5.4211 | 5.047 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.07643 | -0.14125 | 5.1706 | -117.3863 | 5.431 | 5.2886 | 0.11802 | -117.3001 | -117.2046 | -0.017659 | -122.6877 | 0.15212 | 0.058087 | 0.075746 | -122.5662 | -122.5493 | 5.363 | 5.4492 | 5.5447 | 5.4774 | -117.5787 | 0.061592 | 0.18309 | 0.20003 | 0.20179 | -122.767
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0038783 | -0.011236 | 0.006318 | -0.0099192 | -0.0050803 | -0.0023397 | 0.017049 | 0.037109 | 0.010304 | 5.312 | 5.3446 | 5.1559 | 5.2349 | 5.3119 | 5.4165 | 5.0379 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.045757 | 0.081008 | -0.14125 | 5.134 | -117.3954 | 5.4081 | 5.252 | 0.11803 | -117.3184 | -117.2138 | -0.045125 | -122.6877 | 0.12007 | 0.039779 | 0.084904 | -122.5846 | -122.5493 | 5.331 | 5.408 | 5.5126 | 5.4408 | -117.5924 | 0.038705 | 0.14189 | 0.17714 | 0.17891 | -122.7716
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0040921 | -0.01145 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.036895 | 0.010091 | 5.2891 | 5.3263 | 5.1467 | 5.2211 | 5.2936 | 5.3982 | 5.0241 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.045757 | 0.090166 | -0.14583 | 5.1431 | -117.4138 | 5.4081 | 5.2658 | 0.12261 | -117.3413 | -117.2367 | -0.026814 | -122.7015 | 0.14296 | 0.05351 | 0.080324 | -122.5891 | -122.5447 | 5.3401 | 5.4126 | 5.5172 | 5.4453 | -117.6108 | 0.052437 | 0.16478 | 0.20919 | 0.19722 | -122.7807
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0036647 | -0.011236 | 0.0065316 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.037109 | 0.010518 | 5.2845 | 5.3172 | 5.1422 | 5.2165 | 5.289 | 5.389 | 5.0241 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14125 | 5.1203 | -117.4183 | 5.3806 | 5.2383 | 0.11803 | -117.3459 | -117.2458 | -0.045125 | -122.6969 | 0.12007 | 0.0352 | 0.080325 | -122.5846 | -122.5493 | 5.3127 | 5.3851 | 5.4852 | 5.4133 | -117.6108 | 0.034126 | 0.14646 | 0.18172 | 0.17891 | -122.7761
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0034509 | -0.011664 | 0.006318 | -0.02518 | -0.0046531 | -0.0027669 | 0.016408 | 0.036895 | 0.010304 | 5.2799 | 5.3126 | 5.133 | 5.212 | 5.2844 | 5.3845 | 5.0104 | 0.019362 | 0.087354 | -0.056351 | -0.062004 | 0.045757 | 0.094744 | -0.14125 | 5.1294 | -117.455 | 5.3989 | 5.252 | 0.12261 | -117.3825 | -117.2825 | -0.022236 | -122.7289 | 0.13838 | 0.062668 | 0.084904 | -122.6212 | -122.5722 | 5.331 | 5.4035 | 5.5035 | 5.4316 | -117.6565 | 0.057015 | 0.16478 | 0.21376 | 0.20637 | -122.8082
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0038783 | -0.01145 | 0.0058906 | -0.02518 | -0.0050803 | -0.0027669 | 0.016835 | 0.037109 | 0.010091 | 5.2708 | 5.3034 | 5.133 | 5.2028 | 5.2753 | 5.3799 | 5.0012 | 0.019362 | 0.073618 | -0.06093 | -0.057425 | 0.059493 | 0.085587 | -0.13668 | 5.0836 | -117.4321 | 5.3532 | 5.2154 | 0.13177 | -117.3596 | -117.255 | -0.054279 | -122.6923 | 0.10176 | 0.021467 | 0.075746 | -122.5754 | -122.5493 | 5.2852 | 5.3577 | 5.4623 | 5.3858 | -117.6337 | 0.024972 | 0.14189 | 0.16798 | 0.15602 | -122.7716
|  |  |  | 1.4211e-13 | -0.037897 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.0061044 | -0.01755 | -0.0046531 | -0.0025533 | 0.016195 | 0.037109 | 0.010304 | 5.2616 | 5.2988 | 5.1193 | 5.2028 | 5.2615 | 5.3753 | 4.9967 | 0.019362 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14583 | 5.1065 | -117.4138 | 5.3715 | 5.2291 | 0.12261 | -117.355 | -117.2413 | -0.03597 | -122.6832 | 0.12923 | 0.048933 | 0.084903 | -122.5617 | -122.531 | 5.3127 | 5.3714 | 5.4852 | 5.4087 | -117.6199 | 0.043281 | 0.16478 | 0.19545 | 0.19264 | -122.7624
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0038783 | -0.011877 | 0.0065316 | -0.01755 | -0.0048667 | -0.0023397 | 0.016408 | 0.037322 | 0.010091 | 5.2616 | 5.2897 | 5.1147 | 5.1937 | 5.2661 | 5.3707 | 5.0012 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.054914 | 0.085587 | -0.13668 | 5.0974 | -117.4595 | 5.3577 | 5.2108 | 0.11345 | -117.3871 | -117.2825 | -0.040546 | -122.7198 | 0.12007 | 0.030621 | 0.071167 | -122.5983 | -122.5676 | 5.2898 | 5.3623 | 5.4669 | 5.3858 | -117.652 | 0.029548 | 0.15104 | 0.18172 | 0.17891 | -122.7899
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0034509 | -0.011236 | 0.0065316 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.037322 | 0.010304 | 5.257 | 5.2943 | 5.1147 | 5.1937 | 5.2661 | 5.3707 | 4.9967 | 0.019362 | 0.078197 | -0.06093 | -0.057425 | 0.050335 | 0.085587 | -0.14125 | 5.0836 | -117.4321 | 5.344 | 5.2017 | 0.11803 | -117.3596 | -117.255 | -0.05428 | -122.6832 | 0.10634 | 0.026045 | 0.080325 | -122.5754 | -122.5401 | 5.2806 | 5.3531 | 5.4577 | 5.3812 | -117.6291 | 0.02955 | 0.13731 | 0.17256 | 0.16517 | -122.767
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0036647 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016622 | 0.037109 | 0.010091 | 5.257 | 5.2988 | 5.1193 | 5.1937 | 5.2661 | 5.3616 | 4.9829 | 0.023941 | 0.087354 | -0.06093 | -0.071161 | 0.059493 | 0.094744 | -0.14125 | 5.1019 | -117.4367 | 5.3761 | 5.2383 | 0.13635 | -117.3642 | -117.2687 | -0.022236 | -122.7015 | 0.14296 | 0.058089 | 0.080325 | -122.5708 | -122.5356 | 5.3127 | 5.3851 | 5.4806 | 5.4179 | -117.6474 | 0.047858 | 0.17851 | 0.21376 | 0.20637 | -122.7716
|  |  |  | 1.4211e-13 | -0.03747 | -6.4092e-05 | -0.0034509 | -0.011877 | 0.006318 | -0.0022892 | -0.0048667 | -0.0027669 | 0.016408 | 0.037322 | 0.010304 | 5.2433 | 5.2851 | 5.1101 | 5.1799 | 5.2524 | 5.357 | 4.9783 | 0.033099 | 0.082776 | -0.065509 | -0.071161 | 0.050335 | 0.085587 | -0.14125 | 5.1019 | -117.4641 | 5.3669 | 5.2337 | 0.13177 | -117.3917 | -117.287 | -0.017659 | -122.7152 | 0.1567 | 0.058087 | 0.075746 | -122.5937 | -122.5585 | 5.3035 | 5.376 | 5.4806 | 5.4087 | -117.6657 | 0.052435 | 0.17393 | 0.20918 | 0.20637 | -122.7853
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0036647 | -0.011664 | 0.0061044 | -0.01755 | -0.0048667 | -0.0025533 | 0.016622 | 0.037109 | 0.010304 | 5.2341 | 5.276 | 5.0918 | 5.1799 | 5.2432 | 5.3524 | 4.9692 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.07643 | -0.14583 | 5.0333 | -117.4183 | 5.2982 | 5.1559 | 0.12261 | -117.355 | -117.2459 | -0.081746 | -122.6603 | 0.088028 | 0.003157 | 0.084903 | -122.5434 | -122.5218 | 5.244 | 5.3073 | 5.4165 | 5.34 | -117.6291 | 0.002083 | 0.119 | 0.14052 | 0.14228 | -122.7441
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0036647 | -0.011664 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0021259 | 0.016408 | 0.037109 | 0.0098772 | 5.2296 | 5.276 | 5.0918 | 5.1662 | 5.2386 | 5.3433 | 4.9646 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 5.047 | -117.4641 | 5.312 | 5.1742 | 0.12719 | -117.3917 | -117.2871 | -0.063436 | -122.6923 | 0.10634 | 0.021467 | 0.084903 | -122.58 | -122.5447 | 5.2486 | 5.321 | 5.4257 | 5.3584 | -117.6657 | 0.020393 | 0.13273 | 0.16798 | 0.16059 | -122.7761
|  |  |  | 1.4211e-13 | -0.037683 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016195 | 0.037322 | 0.010091 | 5.2296 | 5.2668 | 5.0826 | 5.157 | 5.2341 | 5.3387 | 4.9646 | 0.023941 | 0.078197 | -0.056351 | -0.062004 | 0.045757 | 0.085587 | -0.14125 | 5.0745 | -117.4962 | 5.3394 | 5.1925 | 0.11804 | -117.4191 | -117.3145 | -0.031392 | -122.7152 | 0.1338 | 0.053512 | 0.084904 | -122.6074 | -122.5676 | 5.2669 | 5.3439 | 5.4485 | 5.3767 | -117.6886 | 0.047859 | 0.15562 | 0.19545 | 0.18806 | -122.7945
|  |  |  | 1.4211e-13 | -0.037256 | -0.00027769 | -0.0038783 | -0.011877 | 0.006318 | -0.01755 | -0.0048667 | -0.0023397 | 0.016622 | 0.037109 | 0.010518 | 5.2204 | 5.2668 | 5.0826 | 5.1525 | 5.2295 | 5.3295 | 4.9692 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.14125 | 5.0745 | -117.4916 | 5.3257 | 5.1879 | 0.11346 | -117.4146 | -117.3145 | -0.035969 | -122.7106 | 0.13381 | 0.039777 | 0.075746 | -122.5937 | -122.5585 | 5.2577 | 5.3348 | 5.4348 | 5.3721 | -117.6749 | 0.038704 | 0.15562 | 0.19087 | 0.18806 | -122.7853
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0036647 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.036895 | 0.010091 | 5.2021 | 5.2531 | 5.0689 | 5.1433 | 5.2203 | 5.3204 | 4.9554 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.050335 | 0.081008 | -0.14583 | 5.0699 | -117.4824 | 5.3165 | 5.1833 | 0.11346 | -117.4054 | -117.3054 | -0.031392 | -122.6923 | 0.13838 | 0.053511 | 0.084903 | -122.5754 | -122.5447 | 5.2577 | 5.3348 | 5.4348 | 5.3675 | -117.6703 | 0.047859 | 0.16478 | 0.19545 | 0.19722 | -122.7716
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0036647 | -0.011236 | 0.0065316 | 0.0053413 | -0.0046531 | -0.0025533 | 0.016195 | 0.036895 | 0.010304 | 5.1975 | 5.2439 | 5.0689 | 5.1387 | 5.2112 | 5.3112 | 4.9417 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.054914 | 0.085587 | -0.14583 | 5.0378 | -117.5145 | 5.2936 | 5.165 | 0.1272 | -117.442 | -117.342 | -0.049703 | -122.7106 | 0.12007 | 0.0352 | 0.084903 | -122.5983 | -122.5676 | 5.2348 | 5.3073 | 5.4073 | 5.34 | -117.7115 | 0.038705 | 0.15104 | 0.18172 | 0.17433 | -122.799
|  |  |  | 1.4211e-13 | -0.037897 | 0.00014951 | -0.0038783 | -0.011664 | 0.006318 | -0.01755 | -0.0048667 | -0.0025533 | 0.016408 | 0.037322 | 0.010304 | 5.1929 | 5.2347 | 5.0597 | 5.1296 | 5.2112 | 5.3066 | 4.9325 | 0.019362 | 0.078197 | -0.056351 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 4.9966 | -117.4962 | 5.257 | 5.1238 | 0.1272 | -117.4146 | -117.3191 | -0.081746 | -122.6877 | 0.083449 | 0.007736 | 0.089482 | -122.5754 | -122.5401 | 5.1936 | 5.2753 | 5.3707 | 5.2988 | -117.6932 | 0.002083 | 0.11442 | 0.14967 | 0.14228 | -122.7716
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0038783 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016408 | 0.037322 | 0.010091 | 5.1929 | 5.2302 | 5.0414 | 5.1158 | 5.1974 | 5.2975 | 4.9325 | 0.023941 | 0.082776 | -0.056351 | -0.062004 | 0.050335 | 0.090166 | -0.14125 | 5.0241 | -117.5236 | 5.2845 | 5.133 | 0.10888 | -117.442 | -117.342 | -0.049702 | -122.7015 | 0.11549 | 0.035202 | 0.084904 | -122.5891 | -122.5493 | 5.2074 | 5.289 | 5.389 | 5.3217 | -117.7069 | 0.029549 | 0.14189 | 0.18172 | 0.17433 | -122.7807
|  |  |  | 1.4211e-13 | -0.037683 | -0.00070509 | -0.0040921 | -0.011877 | 0.0061044 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.037109 | 0.010091 | 5.1655 | 5.2302 | 5.0369 | 5.1112 | 5.1837 | 5.2883 | 4.9188 | 0.02852 | 0.073618 | -0.074666 | -0.062004 | 0.054914 | 0.081008 | -0.14583 | 4.9737 | -117.4962 | 5.2204 | 5.0918 | 0.11804 | -117.4237 | -117.3191 | -0.090901 | -122.6694 | 0.083452 | -0.019734 | 0.071167 | -122.5525 | -122.5264 | 5.1662 | 5.2386 | 5.3432 | 5.2851 | -117.6886 | -0.007072 | 0.10985 | 0.13594 | 0.12855 | -122.7533
|  |  |  | 1.4211e-13 | -0.03747 | -0.00049149 | -0.0036647 | -0.01145 | 0.006318 | -0.0022892 | -0.0046531 | -0.0027669 | 0.016408 | 0.037109 | 0.010304 | 5.1655 | 5.2073 | 5.0277 | 5.1158 | 5.1791 | 5.2792 | 4.9142 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.045757 | 0.094744 | -0.15041 | 4.9875 | -117.5099 | 5.2387 | 5.1009 | 0.11346 | -117.4466 | -117.3466 | -0.07717 | -122.6877 | 0.10176 | 0.007733 | 0.084903 | -122.58 | -122.531 | 5.1891 | 5.2524 | 5.3524 | 5.2805 | -117.7115 | 0.011238 | 0.119 | 0.16799 | 0.15602 | -122.7761
|  |  |  | 1.4211e-13 | -0.03747 | -0.00027769 | -0.0036647 | -0.011664 | 0.0065316 | -0.02518 | -0.0050803 | -0.0025533 | 0.016195 | 0.037322 | 0.010304 | 5.17 | 5.2119 | 5.0277 | 5.0975 | 5.1745 | 5.27 | 4.9097 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.14125 | 4.9829 | -117.5374 | 5.2433 | 5.1009 | 0.11804 | -117.4603 | -117.3649 | -0.068013 | -122.7015 | 0.10176 | 0.007733 | 0.075746 | -122.5846 | -122.5493 | 5.1708 | 5.2478 | 5.3432 | 5.2851 | -117.7252 | 0.00666 | 0.12358 | 0.15883 | 0.15602 | -122.7761
|  |  |  | 1.4211e-13 | -0.037683 | -6.4092e-05 | -0.0034509 | -0.011664 | 0.006318 | -0.0022892 | -0.0046531 | -0.0027669 | 0.016408 | 0.037536 | 0.0098772 | 5.1517 | 5.1981 | 5.014 | 5.0884 | 5.1608 | 5.2792 | 4.8959 | 0.02852 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14583 | 4.9646 | -117.5236 | 5.2204 | 5.0826 | 0.11805 | -117.4512 | -117.3328 | -0.077168 | -122.6786 | 0.097185 | 0.007735 | 0.084903 | -122.5571 | -122.5264 | 5.157 | 5.2295 | 5.3478 | 5.2668 | -117.7161 | 0.002083 | 0.12358 | 0.15425 | 0.15144 | -122.7578
|  |  |  | 1.4211e-13 | -0.037683 | -6.4092e-05 | -0.0036647 | -0.01145 | 0.0058906 | -0.01755 | -0.0046531 | -0.0025533 | 0.016195 | 0.037322 | 0.010091 | 5.1563 | 5.189 | 5.014 | 5.0884 | 5.1516 | 5.2608 | 4.8868 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.13668 | 4.9692 | -117.5374 | 5.2387 | 5.0964 | 0.1272 | -117.4741 | -117.3649 | -0.054279 | -122.6877 | 0.10634 | 0.021467 | 0.075746 | -122.5708 | -122.5401 | 5.1708 | 5.234 | 5.3432 | 5.2714 | -117.739 | 0.020393 | 0.13731 | 0.16798 | 0.16059 | -122.7624
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0034509 | -0.01145 | 0.0058906 | -0.01755 | -0.0048667 | -0.0025533 | 0.016408 | 0.037109 | 0.010304 | 5.138 | 5.1752 | 5.0002 | 5.0792 | 5.1516 | 5.2517 | 4.8868 | 0.023941 | 0.073618 | -0.06093 | -0.071161 | 0.054914 | 0.085587 | -0.14583 | 5.0058 | -117.5648 | 5.257 | 5.1192 | 0.11347 | -117.4924 | -117.3924 | -0.026814 | -122.7152 | 0.14296 | 0.058089 | 0.084903 | -122.5891 | -122.5585 | 5.1982 | 5.2707 | 5.3707 | 5.2942 | -117.7573 | 0.047858 | 0.17393 | 0.20461 | 0.19264 | -122.7899
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0038783 | -0.011664 | 0.005677 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.037536 | 0.010091 | 5.1288 | 5.1706 | 4.9911 | 5.0655 | 5.1425 | 5.2471 | 4.873 | 0.02852 | 0.087354 | -0.056351 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.9417 | -117.5374 | 5.1975 | 5.0597 | 0.11805 | -117.4604 | -117.3557 | -0.077168 | -122.6648 | 0.097185 | 0.012314 | 0.089482 | -122.5434 | -122.5127 | 5.1341 | 5.2112 | 5.3158 | 5.2393 | -117.7298 | 0.006661 | 0.12816 | 0.15883 | 0.15602 | -122.7487
|  |  |  | 1.4211e-13 | -0.037897 | -0.00049149 | -0.0038783 | -0.011877 | 0.0058906 | -0.02518 | -0.0048667 | -0.0025533 | 0.016195 | 0.037536 | 0.010091 | 5.1197 | 5.1615 | 4.9773 | 5.0609 | 5.1288 | 5.238 | 4.8684 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.9463 | -117.5465 | 5.1975 | 5.0552 | 0.10889 | -117.4787 | -117.3695 | -0.068013 | -122.6694 | 0.10176 | 0.012311 | 0.080324 | -122.5525 | -122.5173 | 5.1387 | 5.2066 | 5.3158 | 5.2393 | -117.739 | 0.015816 | 0.13273 | 0.16799 | 0.1606 | -122.7533
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0036647 | -0.011664 | 0.006318 | -0.01755 | -0.0052939 | -0.0023397 | 0.016195 | 0.037322 | 0.010091 | 5.1151 | 5.1523 | 4.9728 | 5.0471 | 5.1242 | 5.2288 | 4.8593 | 0.019362 | 0.082776 | -0.056351 | -0.062004 | 0.050335 | 0.081008 | -0.14125 | 4.96 | -117.5832 | 5.2158 | 5.0735 | 0.11347 | -117.5061 | -117.4015 | -0.040547 | -122.6923 | 0.12007 | 0.044357 | 0.084904 | -122.58 | -122.5493 | 5.1479 | 5.2249 | 5.3295 | 5.253 | -117.771 | 0.038704 | 0.15104 | 0.18172 | 0.18348 | -122.7716
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0038783 | -0.011877 | 0.006318 | -0.0099192 | -0.0048667 | -0.0029805 | 0.016195 | 0.037536 | 0.010304 | 5.1059 | 5.1523 | 4.9728 | 5.0563 | 5.1196 | 5.2242 | 4.8501 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.054914 | 0.094744 | -0.15041 | 4.9051 | -117.542 | 5.1609 | 5.0277 | 0.12263 | -117.4787 | -117.3741 | -0.09548 | -122.6603 | 0.078873 | -0.010577 | 0.084903 | -122.5434 | -122.5035 | 5.1112 | 5.1745 | 5.2791 | 5.2073 | -117.7481 | -0.007072 | 0.10985 | 0.14968 | 0.13313 | -122.7487
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0036647 | -0.011877 | 0.0065316 | -0.0022892 | -0.0050803 | -0.0027669 | 0.016835 | 0.037322 | 0.010304 | 5.1014 | 5.1386 | 4.959 | 5.038 | 5.1059 | 5.2151 | 4.841 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.050335 | 0.085587 | -0.15499 | 4.9417 | -117.6106 | 5.2021 | 5.0597 | 0.11805 | -117.5428 | -117.4336 | -0.054283 | -122.7152 | 0.12465 | 0.044357 | 0.09864 | -122.5983 | -122.563 | 5.1387 | 5.2066 | 5.3158 | 5.2393 | -117.8077 | 0.034126 | 0.15104 | 0.18629 | 0.18348 | -122.8036
|  |  |  | 1.4211e-13 | -0.037683 | -0.00049149 | -0.0038783 | -0.011664 | 0.006318 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016408 | 0.037536 | 0.010304 | 5.0968 | 5.1386 | 4.9499 | 5.0334 | 5.0967 | 5.2105 | 4.8456 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.054914 | 0.090166 | -0.14125 | 4.9051 | -117.5786 | 5.1563 | 5.0094 | 0.10432 | -117.5153 | -117.4015 | -0.081746 | -122.6832 | 0.08345 | -0.006 | 0.075746 | -122.5571 | -122.5218 | 5.0929 | 5.1562 | 5.27 | 5.1981 | -117.7664 | -0.011652 | 0.11442 | 0.14968 | 0.14228 | -122.7533
|  |  |  | 1.4211e-13 | -0.037897 | -6.4092e-05 | -0.0034509 | -0.011664 | 0.0058906 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.037322 | 0.010304 | 5.0785 | 5.1203 | 4.9361 | 5.0151 | 5.083 | 5.1922 | 4.8227 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.081008 | -0.14583 | 4.9463 | -117.6518 | 5.2021 | 5.0597 | 0.11348 | -117.584 | -117.4748 | -0.022237 | -122.7244 | 0.14754 | 0.058087 | 0.080324 | -122.612 | -122.5859 | 5.1387 | 5.2066 | 5.3158 | 5.2439 | -117.8443 | 0.066171 | 0.17851 | 0.2046 | 0.20637 | -122.8128
|  |  |  | 1.4211e-13 | -0.037897 | -6.4092e-05 | -0.0036647 | -0.011877 | 0.0061044 | -0.01755 | -0.0050803 | -0.0025533 | 0.016408 | 0.037322 | 0.010091 | 5.0647 | 5.1111 | 4.9361 | 5.0059 | 5.0784 | 5.183 | 4.8135 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14125 | 4.9051 | -117.6747 | 5.1563 | 5.0277 | 0.12264 | -117.6023 | -117.4977 | -0.049702 | -122.7427 | 0.12007 | 0.026044 | 0.075746 | -122.6257 | -122.5905 | 5.0975 | 5.1699 | 5.2746 | 5.2027 | -117.8672 | 0.029549 | 0.14647 | 0.18172 | 0.17433 | -122.8219
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0040921 | -0.01145 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0021259 | 0.016408 | 0.037536 | 0.010304 | 5.0602 | 5.102 | 4.9178 | 5.0014 | 5.0692 | 5.1784 | 4.8043 | 0.019362 | 0.082776 | -0.065509 | -0.071161 | 0.050335 | 0.090166 | -0.14583 | 4.905 | -117.6564 | 5.1609 | 5.0185 | 0.11348 | -117.5885 | -117.4793 | -0.045125 | -122.7289 | 0.12007 | 0.035199 | 0.080324 | -122.6074 | -122.5676 | 5.1021 | 5.1699 | 5.2791 | 5.2027 | -117.8534 | 0.029547 | 0.15104 | 0.19087 | 0.18348 | -122.8036
|  |  |  | 1.4211e-13 | -0.038111 | -0.00027769 | -0.0036647 | -0.01145 | 0.006318 | -0.01755 | -0.0048667 | -0.0023397 | 0.016408 | 0.037109 | 0.010304 | 5.0647 | 5.1065 | 4.9178 | 4.9922 | 5.0647 | 5.1693 | 4.7998 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.045757 | 0.090166 | -0.14583 | 4.8547 | -117.6335 | 5.1197 | 4.9728 | 0.11806 | -117.5611 | -117.4565 | -0.090901 | -122.6877 | 0.074294 | -0.005998 | 0.084903 | -122.58 | -122.5356 | 5.0471 | 5.1196 | 5.2242 | 5.1615 | -117.826 | -0.007072 | 0.10069 | 0.1451 | 0.13313 | -122.7716
|  |  |  | 1.4211e-13 | -0.037897 | -6.4092e-05 | -0.0036647 | -0.011236 | 0.006318 | -0.0099192 | -0.0050803 | -0.0025533 | 0.016408 | 0.037536 | 0.010304 | 5.0419 | 5.0974 | 4.9041 | 4.9922 | 5.0555 | 5.1693 | 4.7952 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.054914 | 0.085587 | -0.14125 | 4.8547 | -117.6518 | 5.1014 | 4.9636 | 0.1089 | -117.5886 | -117.4748 | -0.081746 | -122.706 | 0.088029 | -0.006 | 0.075746 | -122.5891 | -122.5585 | 5.0517 | 5.115 | 5.2288 | 5.1569 | -117.8489 | -0.002495 | 0.11442 | 0.1451 | 0.14228 | -122.7853
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0036647 | -0.011877 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0027669 | 0.016408 | 0.037109 | 0.010091 | 5.0373 | 5.0837 | 4.8949 | 4.9831 | 5.0509 | 5.1555 | 4.7723 | 0.033099 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.14583 | 4.8226 | -117.6656 | 5.0876 | 4.9453 | 0.12264 | -117.5977 | -117.4931 | -0.095479 | -122.7106 | 0.083453 | -0.010576 | 0.084903 | -122.5891 | -122.563 | 5.0334 | 5.1013 | 5.2059 | 5.134 | -117.8763 | -0.01165 | 0.10985 | 0.13594 | 0.12855 | -122.7945
|  |  |  | 1.4211e-13 | -0.038111 | -6.4092e-05 | -0.0036647 | -0.011877 | 0.006318 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016408 | 0.037322 | 0.010304 | 5.0327 | 5.0745 | 4.8904 | 4.9693 | 5.0418 | 5.151 | 4.7769 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.15499 | 4.8226 | -117.629 | 5.0785 | 4.9361 | 0.11348 | -117.5565 | -117.4473 | -0.10921 | -122.6603 | 0.074296 | -0.015154 | 0.094061 | -122.5479 | -122.5127 | 5.0151 | 5.0875 | 5.1967 | 5.1203 | -117.8214 | -0.016228 | 0.096111 | 0.13136 | 0.12397 | -122.7533
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0040921 | -0.011877 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016408 | 0.037322 | 0.010304 | 5.0235 | 5.0699 | 4.8812 | 4.9556 | 5.0372 | 5.1372 | 4.7677 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.081008 | -0.14125 | 4.8226 | -117.6702 | 5.0785 | 4.9361 | 0.11349 | -117.5886 | -117.4885 | -0.086323 | -122.6832 | 0.078873 | -0.010577 | 0.075746 | -122.5662 | -122.5447 | 5.0105 | 5.0921 | 5.1922 | 5.1249 | -117.858 | -0.002493 | 0.11442 | 0.13594 | 0.13313 | -122.767
|  |  |  | 1.4211e-13 | -0.037897 | -0.00049149 | -0.0036647 | -0.012305 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016195 | 0.037322 | 0.010091 | 5.0052 | 5.0608 | 4.872 | 4.951 | 5.028 | 5.1281 | 4.7494 | 0.019362 | 0.082776 | -0.06093 | -0.057425 | 0.054914 | 0.085587 | -0.14125 | 4.8226 | -117.693 | 5.0785 | 4.9453 | 0.12265 | -117.616 | -117.516 | -0.068013 | -122.7015 | 0.092604 | 0.012312 | 0.080325 | -122.5891 | -122.5585 | 5.0242 | 5.1013 | 5.2013 | 5.134 | -117.8947 | 0.015817 | 0.12816 | 0.15883 | 0.15602 | -122.7853
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0040921 | -0.01145 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016622 | 0.037322 | 0.010091 | 5.0052 | 5.047 | 4.872 | 4.9418 | 5.0189 | 5.1281 | 4.754 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.8272 | -117.6747 | 5.0785 | 4.9453 | 0.11807 | -117.5977 | -117.4885 | -0.072591 | -122.6786 | 0.10176 | 0.012312 | 0.084903 | -122.5617 | -122.5264 | 5.0151 | 5.0921 | 5.2013 | 5.1203 | -117.8626 | 0.011238 | 0.12816 | 0.16341 | 0.15144 | -122.7624
|  |  |  | 1.4211e-13 | -0.037683 | -0.00027769 | -0.0036647 | -0.011664 | 0.0058906 | -0.01755 | -0.0048667 | -0.0023397 | 0.016408 | 0.037109 | 0.010091 | 4.9961 | 5.0424 | 4.8583 | 4.9373 | 5.0097 | 5.1098 | 4.7357 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.14125 | 4.8226 | -117.7068 | 5.083 | 4.9453 | 0.12265 | -117.6343 | -117.5343 | -0.05428 | -122.706 | 0.10634 | 0.026045 | 0.080325 | -122.5845 | -122.5585 | 5.0242 | 5.0967 | 5.1967 | 5.1294 | -117.9084 | 0.024971 | 0.14647 | 0.17256 | 0.16517 | -122.7853
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0036647 | -0.011877 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016622 | 0.037109 | 0.010091 | 4.9915 | 5.0333 | 4.8537 | 4.9373 | 4.996 | 5.1006 | 4.7402 | 0.023941 | 0.087354 | -0.056351 | -0.062004 | 0.050335 | 0.090166 | -0.15041 | 4.8593 | -117.7526 | 5.1105 | 4.9727 | 0.11349 | -117.6939 | -117.5892 | -0.031393 | -122.7518 | 0.14296 | 0.062668 | 0.094061 | -122.6395 | -122.5997 | 5.0563 | 5.115 | 5.2196 | 5.1523 | -117.9496 | 0.057015 | 0.16935 | 0.20919 | 0.20637 | -122.8402
|  |  |  | 1.4211e-13 | -0.037897 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.006318 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.037536 | 0.010304 | 4.9869 | 5.0379 | 4.8491 | 4.9281 | 5.0051 | 5.1098 | 4.7357 | 0.019362 | 0.073618 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 4.8501 | -117.7342 | 5.1014 | 4.9636 | 0.11349 | -117.6572 | -117.5526 | -0.031392 | -122.7244 | 0.1338 | 0.053511 | 0.084903 | -122.612 | -122.5768 | 5.0426 | 5.1196 | 5.2242 | 5.1523 | -117.9267 | 0.052437 | 0.16478 | 0.20003 | 0.18806 | -122.8082
|  |  |  | 1.4211e-13 | -0.037897 | -0.00070509 | -0.0034509 | -0.011877 | 0.0061044 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.037322 | 0.010091 | 4.9915 | 5.0333 | 4.8491 | 4.9235 | 4.9914 | 5.1143 | 4.7219 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.059493 | 0.085587 | -0.13668 | 4.7997 | -117.6976 | 5.0693 | 4.927 | 0.12723 | -117.6298 | -117.5068 | -0.058856 | -122.6877 | 0.10176 | 0.012311 | 0.071167 | -122.5617 | -122.5356 | 5.0014 | 5.0692 | 5.1921 | 5.1111 | -117.8992 | 0.011238 | 0.13731 | 0.16341 | 0.1606 | -122.7578
|  |  |  | 1.4211e-13 | -0.038324 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.0061044 | -0.01755 | -0.0050803 | -0.0025533 | 0.016195 | 0.037322 | 0.010304 | 4.9778 | 5.0241 | 4.84 | 4.9235 | 4.9868 | 5.0914 | 4.7265 | 0.023941 | 0.082776 | -0.070087 | -0.062004 | 0.064071 | 0.085587 | -0.14125 | 4.8089 | -117.7205 | 5.0602 | 4.9224 | 0.11349 | -117.6572 | -117.5526 | -0.058858 | -122.706 | 0.10634 | 0.01231 | 0.071168 | -122.58 | -122.5585 | 5.0059 | 5.0692 | 5.1738 | 5.1065 | -117.9175 | 0.020393 | 0.14647 | 0.16798 | 0.16517 | -122.7853
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0036647 | -0.011877 | 0.0058906 | -0.0099192 | -0.0050803 | -0.0027669 | 0.016195 | 0.037109 | 0.010304 | 4.9732 | 5.0241 | 4.8354 | 4.9144 | 4.9822 | 5.0777 | 4.7173 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.054914 | 0.090166 | -0.14583 | 4.7768 | -117.7251 | 5.0327 | 4.8949 | 0.11807 | -117.6572 | -117.5618 | -0.086324 | -122.7106 | 0.088029 | -0.001421 | 0.084903 | -122.5846 | -122.5493 | 4.9739 | 5.0417 | 5.1372 | 5.0836 | -117.9221 | -0.011652 | 0.11442 | 0.14968 | 0.13771 | -122.7853
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0038783 | -0.011664 | 0.0061044 | -0.02518 | -0.0048667 | -0.0027669 | 0.016408 | 0.037536 | 0.010304 | 4.9686 | 5.0104 | 4.8308 | 4.9052 | 4.9822 | 5.0823 | 4.7173 | 0.023941 | 0.078197 | -0.056351 | -0.062004 | 0.059493 | 0.081008 | -0.14125 | 4.8135 | -117.7617 | 5.0647 | 4.927 | 0.11349 | -117.6847 | -117.5847 | -0.045125 | -122.7289 | 0.12007 | 0.039779 | 0.084904 | -122.6074 | -122.5859 | 5.0013 | 5.0784 | 5.1784 | 5.1065 | -117.9496 | 0.034126 | 0.15562 | 0.17714 | 0.17433 | -122.8082
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0038783 | -0.012091 | 0.005677 | -0.01755 | -0.0050803 | -0.0025533 | 0.015981 | 0.037322 | 0.010091 | 4.9686 | 5.015 | 4.8263 | 4.8961 | 4.9685 | 5.0823 | 4.7082 | 0.02852 | 0.087354 | -0.06093 | -0.057425 | 0.050335 | 0.081008 | -0.14583 | 4.818 | -117.78 | 5.0785 | 4.9361 | 0.11807 | -117.7076 | -117.5938 | -0.03597 | -122.7335 | 0.13838 | 0.048933 | 0.084903 | -122.6258 | -122.5951 | 5.0059 | 5.0784 | 5.1921 | 5.1248 | -117.9679 | 0.052438 | 0.1602 | 0.19087 | 0.19722 | -122.8219
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0036647 | -0.011664 | 0.0058906 | -0.02518 | -0.0048667 | -0.0027669 | 0.016408 | 0.037109 | 0.0096636 | 4.9594 | 5.0058 | 4.8171 | 4.8961 | 4.9593 | 5.0685 | 4.7036 | 0.019362 | 0.091933 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.8043 | -117.78 | 5.0602 | 4.9178 | 0.11349 | -117.7168 | -117.6075 | -0.045125 | -122.7381 | 0.12007 | 0.039778 | 0.084903 | -122.6212 | -122.5859 | 4.9968 | 5.06 | 5.1692 | 5.1065 | -117.9725 | 0.038704 | 0.15562 | 0.19087 | 0.19264 | -122.8219
|  |  |  | 1.4211e-13 | -0.037897 | -6.4092e-05 | -0.0036647 | -0.011664 | 0.006318 | -0.0099192 | -0.0044395 | -0.0027669 | 0.016408 | 0.037322 | 0.0098772 | 4.9503 | 4.9967 | 4.8079 | 4.8869 | 4.9593 | 5.0685 | 4.6944 | 0.014784 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.090166 | -0.14583 | 4.7997 | -117.7663 | 5.0556 | 4.9132 | 0.1135 | -117.6939 | -117.5847 | -0.040547 | -122.7198 | 0.12007 | 0.044356 | 0.084903 | -122.5983 | -122.563 | 4.9922 | 5.0646 | 5.1738 | 5.1019 | -117.9588 | 0.038704 | 0.1602 | 0.19545 | 0.18348 | -122.799
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0034509 | -0.01145 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015981 | 0.03775 | 0.010304 | 4.9366 | 4.9875 | 4.7988 | 4.8823 | 4.9502 | 5.0594 | 4.6944 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14125 | 4.818 | -117.78 | 5.0601 | 4.9224 | 0.10434 | -117.7122 | -117.603 | -0.017659 | -122.7244 | 0.14754 | 0.062666 | 0.080325 | -122.612 | -122.5768 | 5.0059 | 5.0738 | 5.183 | 5.1111 | -117.9679 | 0.061592 | 0.17393 | 0.20918 | 0.20637 | -122.8036
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0038783 | -0.011877 | 0.0061044 | -0.0022892 | -0.0048667 | -0.0023397 | 0.016195 | 0.037536 | 0.010091 | 4.932 | 4.9829 | 4.7988 | 4.8777 | 4.941 | 5.0548 | 4.6807 | 0.02852 | 0.078197 | -0.06093 | -0.071161 | 0.050335 | 0.085587 | -0.14125 | 4.7952 | -117.7755 | 5.0464 | 4.9132 | 0.11808 | -117.7122 | -117.5984 | -0.026814 | -122.7244 | 0.14296 | 0.053511 | 0.080325 | -122.6029 | -122.5676 | 4.9922 | 5.0555 | 5.1692 | 5.0974 | -117.9725 | 0.04328 | 0.16478 | 0.20003 | 0.19264 | -122.7945
|  |  |  | 1.4211e-13 | -0.037897 | -0.00027769 | -0.0036647 | -0.011664 | 0.0058906 | -0.01755 | -0.0046531 | -0.0025533 | 0.016408 | 0.037536 | 0.010304 | 4.932 | 4.9783 | 4.7942 | 4.8686 | 4.9364 | 5.0502 | 4.6716 | 0.033099 | 0.082776 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.7677 | -117.7755 | 5.0281 | 4.8903 | 0.12266 | -117.7076 | -117.5938 | -0.049703 | -122.706 | 0.12923 | 0.0352 | 0.084903 | -122.5845 | -122.5539 | 4.9647 | 5.0326 | 5.1464 | 5.0745 | -117.9725 | 0.034126 | 0.15562 | 0.1863 | 0.17891 | -122.7899
|  |  |  | 1.4211e-13 | -0.038111 | -0.00027769 | -0.0036647 | -0.011877 | 0.006318 | -0.0022892 | -0.0046531 | -0.0027669 | 0.016195 | 0.037322 | 0.0098772 | 4.9228 | 4.9783 | 4.7851 | 4.8686 | 4.9319 | 5.0456 | 4.6716 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.059493 | 0.090166 | -0.14583 | 4.7311 | -117.7709 | 4.9823 | 4.8446 | 0.1135 | -117.7076 | -117.5938 | -0.086324 | -122.706 | 0.088029 | -0.001421 | 0.084903 | -122.58 | -122.5493 | 4.9281 | 4.9914 | 5.1052 | 5.0379 | -117.9679 | -0.007073 | 0.119 | 0.14968 | 0.13771 | -122.7853
|  |  |  | 1.4211e-13 | -0.038111 | -0.00027769 | -0.0036647 | -0.011664 | 0.006318 | -0.01755 | -0.0048667 | -0.0025533 | 0.016408 | 0.037322 | 0.010091 | 4.9182 | 4.9646 | 4.7805 | 4.8594 | 4.9273 | 5.0273 | 4.6624 | 0.023941 | 0.078197 | -0.070087 | -0.066582 | 0.054914 | 0.081008 | -0.15041 | 4.7906 | -117.835 | 5.0464 | 4.9086 | 0.11808 | -117.7671 | -117.6671 | -0.022238 | -122.761 | 0.15212 | 0.058087 | 0.080325 | -122.6395 | -122.6134 | 4.9876 | 5.0555 | 5.1555 | 5.0928 | -118.032 | 0.061592 | 0.18309 | 0.20918 | 0.20637 | -122.8448
|  |  |  | 1.4211e-13 | -0.038324 | -0.00049149 | -0.0038783 | -0.012091 | 0.0061044 | -0.01755 | -0.0046531 | -0.0027669 | 0.016195 | 0.037536 | 0.010304 | 4.9091 | 4.9555 | 4.7713 | 4.8549 | 4.9227 | 5.0182 | 4.667 | 0.019362 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14583 | 4.786 | -117.8258 | 5.0281 | 4.8903 | 0.10434 | -117.758 | -117.6625 | -0.026814 | -122.7472 | 0.13838 | 0.058089 | 0.084903 | -122.6257 | -122.5951 | 4.9739 | 5.0417 | 5.1372 | 5.0745 | -118.0137 | 0.052437 | 0.17393 | 0.20461 | 0.19722 | -122.8265
|  |  |  | 1.4211e-13 | -0.038324 | -0.00027769 | -0.0036647 | -0.01145 | 0.006318 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016195 | 0.037536 | 0.010091 | 4.8999 | 4.9555 | 4.7667 | 4.8457 | 4.909 | 5.0182 | 4.6578 | 0.02852 | 0.082776 | -0.056351 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 4.7631 | -117.7983 | 5.0052 | 4.872 | 0.10892 | -117.7351 | -117.6259 | -0.040547 | -122.706 | 0.13381 | 0.048935 | 0.089482 | -122.5937 | -122.5585 | 4.951 | 5.0143 | 5.1235 | 5.0607 | -117.9862 | 0.043282 | 0.15562 | 0.19087 | 0.18806 | -122.7899
|  |  |  | 1.4211e-13 | -0.038538 | -0.00049149 | -0.0038783 | -0.012091 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016195 | 0.037536 | 0.0098772 | 4.8908 | 4.9463 | 4.753 | 4.8274 | 4.9044 | 4.9999 | 4.6441 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.054914 | 0.090166 | -0.15041 | 4.7494 | -117.8441 | 4.9961 | 4.8583 | 0.10893 | -117.7671 | -117.6716 | -0.045126 | -122.7381 | 0.13381 | 0.039777 | 0.084903 | -122.6166 | -122.5813 | 4.9327 | 5.0097 | 5.1051 | 5.0516 | -118.0274 | 0.038704 | 0.1602 | 0.19545 | 0.18806 | -122.8219
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0038783 | -0.011877 | 0.0061044 | -0.01755 | -0.0046531 | -0.0027669 | 0.016195 | 0.037322 | 0.010091 | 4.8862 | 4.9417 | 4.7484 | 4.832 | 4.8906 | 4.9999 | 4.6395 | 0.023941 | 0.078197 | -0.070087 | -0.057425 | 0.050335 | 0.094744 | -0.14583 | 4.7173 | -117.8121 | 4.964 | 4.8262 | 0.10893 | -117.7534 | -117.6442 | -0.068013 | -122.7015 | 0.10176 | 0.007733 | 0.075746 | -122.5937 | -122.5493 | 4.9098 | 4.9685 | 5.0777 | 5.0195 | -118.0045 | 0.020395 | 0.12815 | 0.17256 | 0.15602 | -122.7899
|  |  |  | 1.4211e-13 | -0.038324 | -0.00049149 | -0.0036647 | -0.011877 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0027669 | 0.016408 | 0.037322 | 0.010304 | 4.8679 | 4.9188 | 4.7393 | 4.8091 | 4.8815 | 4.9861 | 4.6212 | 0.019362 | 0.087354 | -0.070087 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 4.7265 | -117.8899 | 4.9732 | 4.8446 | 0.11808 | -117.8175 | -117.7128 | -0.035969 | -122.7656 | 0.12465 | 0.035199 | 0.071168 | -122.6486 | -122.618 | 4.9144 | 4.9868 | 5.0914 | 5.0241 | -118.0778 | 0.038704 | 0.15562 | 0.18629 | 0.19264 | -122.8402
|  |  |  | 1.4211e-13 | -0.038538 | -0.00070509 | -0.0038783 | -0.011664 | 0.0058906 | -0.01755 | -0.0048667 | -0.0027669 | 0.016408 | 0.037322 | 0.010091 | 4.8679 | 4.9051 | 4.7164 | 4.8045 | 4.8723 | 4.9815 | 4.6166 | 0.023941 | 0.073618 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15041 | 4.6853 | -117.835 | 4.9365 | 4.785 | 0.099772 | -117.7671 | -117.6579 | -0.081747 | -122.6969 | 0.092606 | 0.003156 | 0.084903 | -122.58 | -122.5447 | 4.8732 | 4.941 | 5.0502 | 4.9738 | -118.0229 | 0.01124 | 0.12816 | 0.16341 | 0.14228 | -122.7899
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0040921 | -0.011877 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016195 | 0.037536 | 0.0098772 | 4.8541 | 4.8959 | 4.7118 | 4.7953 | 4.8586 | 4.977 | 4.6029 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.090166 | -0.15041 | 4.6807 | -117.8762 | 4.932 | 4.7896 | 0.10893 | -117.8129 | -117.6945 | -0.072592 | -122.7381 | 0.10176 | 0.01689 | 0.089482 | -122.6166 | -122.5813 | 4.8732 | 4.9364 | 5.0548 | 4.9738 | -118.0686 | 0.011238 | 0.13273 | 0.16799 | 0.1606 | -122.8219
|  |  |  | 1.4211e-13 | -0.038538 | -0.00049149 | -0.0038783 | -0.01145 | 0.0061044 | -0.0022892 | -0.0046531 | -0.0025533 | 0.016408 | 0.037536 | 0.0098772 | 4.845 | 4.8959 | 4.7118 | 4.7908 | 4.854 | 4.9724 | 4.6029 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 4.6944 | -117.8762 | 4.9365 | 4.8034 | 0.10893 | -117.8129 | -117.6945 | -0.05428 | -122.7289 | 0.12007 | 0.030623 | 0.084903 | -122.6166 | -122.5813 | 4.8823 | 4.9456 | 5.0639 | 4.9875 | -118.0641 | 0.029549 | 0.14189 | 0.17714 | 0.17433 | -122.8128
|  |  |  | 1.4211e-13 | -0.038324 | -0.00049149 | -0.0036647 | -0.011664 | 0.0061044 | -0.02518 | -0.0050803 | -0.0027669 | 0.016408 | 0.037322 | 0.010091 | 4.8404 | 4.9051 | 4.7072 | 4.7862 | 4.8586 | 4.9587 | 4.5937 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.085587 | -0.14125 | 4.7036 | -117.8762 | 4.9503 | 4.8171 | 0.11351 | -117.8038 | -117.7037 | -0.031392 | -122.7198 | 0.1338 | 0.044354 | 0.075746 | -122.6074 | -122.5768 | 4.896 | 4.9685 | 5.0685 | 5.015 | -118.0686 | 0.052438 | 0.16478 | 0.19545 | 0.19264 | -122.8036
|  |  |  | 1.4211e-13 | -0.038111 | -0.00070509 | -0.0036647 | -0.011877 | 0.0061044 | -0.02518 | -0.0048667 | -0.0027669 | 0.016408 | 0.037536 | 0.010304 | 4.8358 | 4.8868 | 4.6981 | 4.777 | 4.8494 | 4.9541 | 4.5846 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.085587 | -0.14125 | 4.6349 | -117.8441 | 4.8862 | 4.7484 | 0.11351 | -117.7717 | -117.6671 | -0.090901 | -122.6832 | 0.074295 | -0.015155 | 0.075746 | -122.5617 | -122.5356 | 4.8274 | 4.8998 | 5.0044 | 4.9371 | -118.0366 | -0.01165 | 0.10985 | 0.13594 | 0.13313 | -122.7624
|  |  |  | 1.4211e-13 | -0.038752 | -0.00027769 | -0.0036647 | -0.012091 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.03775 | 0.0098772 | 4.8175 | 4.8776 | 4.6889 | 4.7633 | 4.8403 | 4.9449 | 4.5754 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.045757 | 0.094744 | -0.14125 | 4.6486 | -117.8899 | 4.8908 | 4.7621 | 0.11351 | -117.8129 | -117.7083 | -0.068013 | -122.7106 | 0.097183 | 0.016891 | 0.084904 | -122.6074 | -122.5585 | 4.8365 | 4.9135 | 5.0182 | 4.9509 | -118.0778 | 0.015817 | 0.119 | 0.16799 | 0.15602 | -122.7945
|  |  |  | 1.4211e-13 | -0.038324 | -0.00027769 | -0.0038783 | -0.011877 | 0.006318 | -0.01755 | -0.0046531 | -0.0025533 | 0.016408 | 0.037536 | 0.010091 | 4.8175 | 4.8776 | 4.6889 | 4.7633 | 4.8311 | 4.9495 | 4.5708 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 4.6349 | -117.8899 | 4.8816 | 4.753 | 0.11809 | -117.8221 | -117.7037 | -0.081746 | -122.7106 | 0.088028 | -0.001422 | 0.080324 | -122.5937 | -122.5676 | 4.8274 | 4.8952 | 5.0136 | 4.9417 | -118.0824 | 0.006662 | 0.12358 | 0.14967 | 0.14228 | -122.799
|  |  |  | 1.4211e-13 | -0.038111 | -0.00049149 | -0.0036647 | -0.012091 | 0.006318 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016835 | 0.037536 | 0.010091 | 4.8175 | 4.8685 | 4.6798 | 4.7541 | 4.8265 | 4.9358 | 4.5662 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.15499 | 4.6578 | -117.9036 | 4.9091 | 4.7713 | 0.11352 | -117.8312 | -117.722 | -0.063438 | -122.7244 | 0.11549 | 0.030623 | 0.094061 | -122.6029 | -122.5722 | 4.8457 | 4.9181 | 5.0273 | 4.96 | -118.0915 | 0.024971 | 0.14647 | 0.17714 | 0.16975 | -122.8128
|  |  |  | 1.4211e-13 | -0.038324 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.0061044 | -0.01755 | -0.0046531 | -0.0023397 | 0.016195 | 0.037536 | 0.0098772 | 4.8084 | 4.8593 | 4.6706 | 4.7496 | 4.8174 | 4.9174 | 4.5617 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.081008 | -0.14583 | 4.6486 | -117.922 | 4.8953 | 4.7576 | 0.10894 | -117.8541 | -117.7541 | -0.058858 | -122.7335 | 0.10634 | 0.026045 | 0.084903 | -122.6166 | -122.5905 | 4.8365 | 4.9044 | 5.0044 | 4.9463 | -118.1099 | 0.024971 | 0.14189 | 0.16798 | 0.16975 | -122.8173
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0036647 | -0.011877 | 0.0061044 | -0.01755 | -0.0050803 | -0.0023397 | 0.016195 | 0.037322 | 0.0098772 | 4.7946 | 4.8456 | 4.6614 | 4.7358 | 4.8082 | 4.9174 | 4.5433 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.6257 | -117.922 | 4.877 | 4.7438 | 0.1181 | -117.8495 | -117.7403 | -0.063436 | -122.7198 | 0.10634 | 0.016888 | 0.080324 | -122.5983 | -122.5676 | 4.8182 | 4.8906 | 4.9998 | 4.928 | -118.1144 | 0.020393 | 0.14189 | 0.17256 | 0.16059 | -122.8036
|  |  |  | 1.4211e-13 | -0.038324 | -6.4092e-05 | -0.0036647 | -0.011877 | 0.0058906 | -0.01755 | -0.0046531 | -0.0027669 | 0.016408 | 0.037536 | 0.0098772 | 4.79 | 4.841 | 4.6523 | 4.7312 | 4.8037 | 4.9083 | 4.5388 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.644 | -117.9494 | 4.8953 | 4.7576 | 0.11352 | -117.877 | -117.7724 | -0.040547 | -122.7427 | 0.13381 | 0.039777 | 0.080324 | -122.6257 | -122.5905 | 4.8365 | 4.9089 | 5.0136 | 4.9463 | -118.1419 | 0.043282 | 0.1602 | 0.19545 | 0.18348 | -122.8265
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0038783 | -0.011664 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016195 | 0.03775 | 0.0098772 | 4.7855 | 4.8456 | 4.6523 | 4.7267 | 4.7991 | 4.9083 | 4.5342 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.050335 | 0.085587 | -0.14125 | 4.6303 | -117.954 | 4.8816 | 4.7484 | 0.1181 | -117.8816 | -117.7724 | -0.045125 | -122.7472 | 0.12465 | 0.030621 | 0.075746 | -122.6303 | -122.5951 | 4.8228 | 4.8952 | 5.0044 | 4.9417 | -118.1465 | 0.029548 | 0.14646 | 0.18172 | 0.17433 | -122.8219
|  |  |  | 1.4211e-13 | -0.038324 | -0.00027769 | -0.0036647 | -0.012305 | 0.0065316 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016195 | 0.037536 | 0.010304 | 4.7855 | 4.8364 | 4.6477 | 4.7267 | 4.7991 | 4.9037 | 4.5296 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.059493 | 0.085587 | -0.14125 | 4.5708 | -117.9036 | 4.8267 | 4.6889 | 0.1181 | -117.8312 | -117.7266 | -0.10006 | -122.6877 | 0.069719 | -0.019731 | 0.080325 | -122.5708 | -122.5447 | 4.7679 | 4.8403 | 4.9449 | 4.8776 | -118.1007 | -0.016226 | 0.10069 | 0.12679 | 0.12398 | -122.7716
|  |  |  | 1.4211e-13 | -0.038538 | 0.00014951 | -0.0040921 | -0.012091 | 0.0065316 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016408 | 0.037536 | 0.0098772 | 4.7763 | 4.8273 | 4.6385 | 4.7221 | 4.7945 | 4.8991 | 4.525 | 0.02852 | 0.087354 | -0.065509 | -0.066582 | 0.054914 | 0.081008 | -0.14583 | 4.6028 | -117.922 | 4.8541 | 4.7164 | 0.11352 | -117.8495 | -117.7449 | -0.068013 | -122.7106 | 0.10634 | 0.012311 | 0.080324 | -122.5891 | -122.563 | 4.7999 | 4.8723 | 4.977 | 4.9051 | -118.119 | 0.011238 | 0.13273 | 0.15883 | 0.16517 | -122.7899
|  |  |  | 1.4211e-13 | -0.038752 | 0.00014951 | -0.0038783 | -0.011664 | 0.0061044 | -0.01755 | -0.0048667 | -0.0023397 | 0.016408 | 0.037963 | 0.0098772 | 4.7671 | 4.8227 | 4.6385 | 4.7129 | 4.7899 | 4.8854 | 4.5204 | 0.023941 | 0.082776 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.14583 | 4.5983 | -117.9265 | 4.845 | 4.7164 | 0.1181 | -117.8496 | -117.7541 | -0.068013 | -122.706 | 0.10176 | 0.012311 | 0.080324 | -122.5937 | -122.5539 | 4.7907 | 4.8677 | 4.9632 | 4.9005 | -118.119 | 0.011238 | 0.12358 | 0.16341 | 0.1606 | -122.7853
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0036647 | -0.011664 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016195 | 0.03775 | 0.010304 | 4.7717 | 4.8089 | 4.6294 | 4.7038 | 4.7762 | 4.8808 | 4.5204 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 4.6257 | -117.9769 | 4.877 | 4.7347 | 0.10894 | -117.9045 | -117.7998 | -0.045126 | -122.7381 | 0.13381 | 0.039777 | 0.084903 | -122.6257 | -122.5951 | 4.8091 | 4.8815 | 4.9861 | 4.9142 | -118.1602 | 0.047861 | 0.1602 | 0.19087 | 0.18806 | -122.8311
|  |  |  | 1.4211e-13 | -0.038324 | -0.00070509 | -0.0036647 | -0.011664 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016195 | 0.037536 | 0.0098772 | 4.7534 | 4.8089 | 4.6111 | 4.6946 | 4.767 | 4.8717 | 4.5021 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.085587 | -0.14583 | 4.5525 | -117.9677 | 4.8038 | 4.6614 | 0.10895 | -117.8953 | -117.7907 | -0.095479 | -122.7244 | 0.074295 | -0.015155 | 0.080324 | -122.6029 | -122.5768 | 4.745 | 4.8174 | 4.922 | 4.8593 | -118.1602 | -0.01165 | 0.10985 | 0.13594 | 0.13313 | -122.8082
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0038783 | -0.012091 | 0.0061044 | -0.02518 | -0.0046531 | -0.0027669 | 0.016195 | 0.03775 | 0.0098772 | 4.7488 | 4.7998 | 4.6111 | 4.6855 | 4.7624 | 4.8762 | 4.493 | 0.023941 | 0.073618 | -0.070087 | -0.062004 | 0.054914 | 0.081008 | -0.14125 | 4.5708 | -117.9632 | 4.8267 | 4.6889 | 0.1181 | -117.8862 | -117.7724 | -0.063435 | -122.7106 | 0.10176 | 0.007733 | 0.071168 | -122.5937 | -122.5676 | 4.7633 | 4.8403 | 4.9541 | 4.8776 | -118.1556 | 0.015816 | 0.13273 | 0.15883 | 0.15144 | -122.7899
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0036647 | -0.012091 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016195 | 0.037322 | 0.0098772 | 4.7351 | 4.7952 | 4.6065 | 4.6809 | 4.7533 | 4.8671 | 4.493 | 0.023941 | 0.078197 | -0.06093 | -0.066582 | 0.059493 | 0.094744 | -0.14583 | 4.6028 | -118.0181 | 4.845 | 4.7164 | 0.11352 | -117.9457 | -117.8319 | -0.03597 | -122.7656 | 0.1338 | 0.048933 | 0.084903 | -122.6395 | -122.6042 | 4.7907 | 4.8631 | 4.9769 | 4.9051 | -118.206 | 0.043281 | 0.16936 | 0.20461 | 0.18806 | -122.8448
|  |  |  | 1.4211e-13 | -0.038538 | -6.4092e-05 | -0.0034509 | -0.011877 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.03775 | 0.010091 | 4.7351 | 4.7906 | 4.5973 | 4.6809 | 4.7533 | 4.8533 | 4.4884 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.045757 | 0.085587 | -0.14583 | 4.5708 | -117.9952 | 4.8175 | 4.6797 | 0.10895 | -117.9228 | -117.8227 | -0.063436 | -122.7427 | 0.10634 | 0.016888 | 0.080324 | -122.6303 | -122.5905 | 4.7633 | 4.8357 | 4.9357 | 4.873 | -118.1877 | 0.015815 | 0.12815 | 0.16798 | 0.16059 | -122.8219
|  |  |  | 1.4211e-13 | -0.038111 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.0061044 | -0.0022892 | -0.0050803 | -0.0021259 | 0.016195 | 0.037322 | 0.010091 | 4.7259 | 4.7815 | 4.5882 | 4.6717 | 4.7441 | 4.8488 | 4.4838 | 0.02852 | 0.073618 | -0.065509 | -0.062004 | 0.050335 | 0.085587 | -0.14583 | 4.5525 | -117.9586 | 4.7946 | 4.6568 | 0.10437 | -117.8862 | -117.7815 | -0.077168 | -122.6923 | 0.097185 | 0.003156 | 0.080324 | -122.58 | -122.5447 | 4.7404 | 4.8128 | 4.9174 | 4.8501 | -118.1465 | 0.006661 | 0.119 | 0.15425 | 0.14228 | -122.7761
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0045193 | -0.012091 | 0.006318 | -0.02518 | -0.0050803 | -0.0029805 | 0.016195 | 0.038177 | 0.010304 | 4.7259 | 4.7769 | 4.5882 | 4.6671 | 4.7304 | 4.8442 | 4.4792 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.050335 | 0.081008 | -0.14125 | 4.5845 | -118.0135 | 4.8312 | 4.6935 | 0.10895 | -117.9503 | -117.8365 | -0.035969 | -122.7472 | 0.12923 | 0.048935 | 0.084904 | -122.6303 | -122.5997 | 4.7724 | 4.8357 | 4.9495 | 4.8822 | -118.2014 | 0.038704 | 0.15562 | 0.18629 | 0.18806 | -122.8219
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0040921 | -0.012091 | 0.006318 | -0.01755 | -0.0046531 | -0.0025533 | 0.016195 | 0.037536 | 0.0096636 | 4.7259 | 4.7769 | 4.579 | 4.6671 | 4.7212 | 4.835 | 4.4747 | 0.019362 | 0.087354 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.5525 | -117.9906 | 4.8038 | 4.6568 | 0.10437 | -117.9365 | -117.8227 | -0.068013 | -122.7198 | 0.097182 | 0.012311 | 0.080324 | -122.5983 | -122.5676 | 4.745 | 4.7991 | 4.9129 | 4.8547 | -118.1831 | 0.015816 | 0.13731 | 0.16799 | 0.16517 | -122.8036
|  |  |  | 1.4211e-13 | -0.038538 | -6.4092e-05 | -0.0036647 | -0.011877 | 0.006318 | -0.01755 | -0.0048667 | -0.0027669 | 0.016408 | 0.03775 | 0.0094498 | 4.7122 | 4.7632 | 4.5744 | 4.6534 | 4.7304 | 4.835 | 4.4563 | 0.014784 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.081008 | -0.14125 | 4.5204 | -118.0227 | 4.7763 | 4.6385 | 0.11811 | -117.9457 | -117.8411 | -0.077168 | -122.7335 | 0.078871 | -0.001422 | 0.075746 | -122.6166 | -122.5951 | 4.7175 | 4.7945 | 4.8991 | 4.8272 | -118.2197 | 0.006662 | 0.12358 | 0.1451 | 0.14686 | -122.8173
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0036647 | -0.011877 | 0.0061044 | -0.01755 | -0.0050803 | -0.0025533 | 0.016408 | 0.03775 | 0.010304 | 4.7122 | 4.7632 | 4.5699 | 4.6488 | 4.7212 | 4.8305 | 4.4609 | 0.023941 | 0.06904 | -0.056351 | -0.057425 | 0.054914 | 0.085587 | -0.14125 | 4.5662 | -118.0273 | 4.8175 | 4.6752 | 0.10895 | -117.9549 | -117.8456 | -0.035969 | -122.7335 | 0.12923 | 0.048935 | 0.084904 | -122.6212 | -122.5905 | 4.7541 | 4.8265 | 4.9357 | 4.8684 | -118.2152 | 0.047861 | 0.1602 | 0.19087 | 0.17433 | -122.8173
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0036647 | -0.011877 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.03775 | 0.010091 | 4.7122 | 4.7586 | 4.5653 | 4.6488 | 4.7258 | 4.8259 | 4.4609 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.045757 | 0.085587 | -0.15499 | 4.5342 | -118.0044 | 4.7855 | 4.6385 | 0.10437 | -117.9274 | -117.8273 | -0.081749 | -122.7152 | 0.092604 | 0.012312 | 0.094061 | -122.6074 | -122.5676 | 4.7221 | 4.7991 | 4.8991 | 4.8318 | -118.1923 | 0.011238 | 0.119 | 0.15883 | 0.15602 | -122.8082
|  |  |  | 1.4211e-13 | -0.038324 | -6.4092e-05 | -0.0036647 | -0.011664 | 0.0061044 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.037536 | 0.0098772 | 4.7031 | 4.7586 | 4.5516 | 4.6443 | 4.7121 | 4.8167 | 4.4518 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.050335 | 0.085587 | -0.14583 | 4.557 | -118.0364 | 4.8083 | 4.6568 | 0.099796 | -117.9686 | -117.8639 | -0.040547 | -122.7381 | 0.13381 | 0.039777 | 0.080324 | -122.6303 | -122.5951 | 4.7495 | 4.8174 | 4.922 | 4.8639 | -118.2289 | 0.047861 | 0.15562 | 0.19087 | 0.1789 | -122.8265
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0040921 | -0.012091 | 0.0058906 | -0.0099192 | -0.0050803 | -0.0025533 | 0.016195 | 0.03775 | 0.0096636 | 4.6893 | 4.7448 | 4.5561 | 4.6397 | 4.7029 | 4.8167 | 4.438 | 0.019362 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.081008 | -0.14125 | 4.4884 | -118.0135 | 4.7397 | 4.6065 | 0.11811 | -117.9503 | -117.8365 | -0.090901 | -122.7106 | 0.069716 | -0.015155 | 0.075746 | -122.5983 | -122.5722 | 4.69 | 4.7533 | 4.8671 | 4.7952 | -118.2152 | -0.007071 | 0.10527 | 0.13136 | 0.13313 | -122.7945
|  |  |  | 1.4211e-13 | -0.038538 | -0.00049149 | -0.0036647 | -0.012091 | 0.006318 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.03775 | 0.0098772 | 4.6939 | 4.7448 | 4.5561 | 4.6305 | 4.6983 | 4.8121 | 4.4426 | 0.037677 | 0.082776 | -0.06093 | -0.057425 | 0.050335 | 0.081008 | -0.15499 | 4.5387 | -118.0364 | 4.79 | 4.6523 | 0.11353 | -117.9686 | -117.8548 | -0.058861 | -122.7244 | 0.13381 | 0.0352 | 0.094061 | -122.6166 | -122.5859 | 4.7266 | 4.7945 | 4.9083 | 4.841 | -118.2243 | 0.038705 | 0.14646 | 0.17714 | 0.17891 | -122.8219
|  |  |  | 1.4211e-13 | -0.038752 | -0.00027769 | -0.0034509 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016408 | 0.03775 | 0.010091 | 4.6802 | 4.7265 | 4.5332 | 4.6259 | 4.6938 | 4.7938 | 4.438 | 0.023941 | 0.078197 | -0.070087 | -0.057425 | 0.054914 | 0.090166 | -0.15499 | 4.5158 | -118.0364 | 4.758 | 4.6111 | 0.095219 | -117.9686 | -117.8685 | -0.077171 | -122.7198 | 0.10176 | 0.007733 | 0.084904 | -122.6074 | -122.5722 | 4.7038 | 4.7716 | 4.8716 | 4.8043 | -118.2243 | 0.020395 | 0.13273 | 0.16799 | 0.15602 | -122.8173
|  |  |  | 1.4211e-13 | -0.038752 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.006318 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.03775 | 0.0096636 | 4.6756 | 4.7265 | 4.5378 | 4.6122 | 4.6846 | 4.7938 | 4.4197 | 0.023941 | 0.078197 | -0.070087 | -0.066582 | 0.059493 | 0.090166 | -0.14583 | 4.5525 | -118.0547 | 4.8083 | 4.6706 | 0.11811 | -117.9823 | -117.8731 | -0.013082 | -122.7335 | 0.15669 | 0.062664 | 0.075746 | -122.6074 | -122.5768 | 4.745 | 4.8174 | 4.9266 | 4.8593 | -118.2472 | 0.066169 | 0.19224 | 0.22292 | 0.21095 | -122.8128
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0038783 | -0.012518 | 0.006318 | -0.0022892 | -0.0046531 | -0.0023397 | 0.015981 | 0.037322 | 0.010091 | 4.6664 | 4.7311 | 4.5287 | 4.6076 | 4.6709 | 4.7847 | 4.4151 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14583 | 4.5021 | -118.0822 | 4.7534 | 4.6156 | 0.11354 | -118.019 | -117.9052 | -0.058858 | -122.7564 | 0.1155 | 0.026045 | 0.084903 | -122.6349 | -122.6042 | 4.6946 | 4.7578 | 4.8716 | 4.8181 | -118.2747 | 0.020393 | 0.14189 | 0.17256 | 0.16517 | -122.8357
|  |  |  | 1.4211e-13 | -0.038965 | -6.4092e-05 | -0.0038783 | -0.01145 | 0.0061044 | -0.02518 | -0.0050803 | -0.0025533 | 0.016195 | 0.038177 | 0.0098772 | 4.6618 | 4.7174 | 4.5149 | 4.6076 | 4.6709 | 4.7709 | 4.4106 | 0.033099 | 0.078197 | -0.056351 | -0.066582 | 0.064071 | 0.085587 | -0.14125 | 4.5296 | -118.0959 | 4.7809 | 4.634 | 0.10438 | -118.0327 | -117.9326 | -0.022236 | -122.7701 | 0.15212 | 0.062668 | 0.084904 | -122.6395 | -122.618 | 4.7266 | 4.7899 | 4.89 | 4.8364 | -118.293 | 0.052437 | 0.18309 | 0.20461 | 0.19722 | -122.8448
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0038783 | -0.011877 | 0.006318 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016408 | 0.037536 | 0.0098772 | 4.6527 | 4.7036 | 4.5104 | 4.5939 | 4.6617 | 4.7618 | 4.3922 | 0.023941 | 0.082776 | -0.070087 | -0.071161 | 0.059493 | 0.081008 | -0.14125 | 4.4792 | -118.0593 | 4.7397 | 4.5973 | 0.11812 | -117.9915 | -117.8914 | -0.05428 | -122.7244 | 0.11092 | 0.016888 | 0.071168 | -122.5937 | -122.5722 | 4.6809 | 4.7487 | 4.8488 | 4.7906 | -118.261 | 0.015814 | 0.14647 | 0.16798 | 0.16975 | -122.7945
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0040921 | -0.012305 | 0.0061044 | -0.02518 | -0.0048667 | -0.0027669 | 0.016408 | 0.03775 | 0.0098772 | 4.639 | 4.6945 | 4.5012 | 4.5847 | 4.6617 | 4.7572 | 4.3922 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 4.4884 | -118.1097 | 4.7351 | 4.5973 | 0.10896 | -118.0327 | -117.9372 | -0.054282 | -122.7518 | 0.12007 | 0.026043 | 0.080325 | -122.6395 | -122.6088 | 4.6809 | 4.7578 | 4.8533 | 4.7906 | -118.3022 | 0.038705 | 0.15104 | 0.18172 | 0.17891 | -122.8448
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0040921 | -0.011664 | 0.0058906 | -0.01755 | -0.0048667 | -0.0027669 | 0.016408 | 0.037963 | 0.0098772 | 4.6344 | 4.6899 | 4.492 | 4.5802 | 4.648 | 4.7572 | 4.3922 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.4746 | -118.1417 | 4.7168 | 4.5744 | 0.099804 | -118.0739 | -117.9647 | -0.063436 | -122.7839 | 0.10634 | 0.021467 | 0.084903 | -122.6669 | -122.6317 | 4.6626 | 4.7304 | 4.8396 | 4.7723 | -118.3296 | 0.020393 | 0.13731 | 0.17256 | 0.16059 | -122.8677
|  |  |  | 1.4211e-13 | -0.038752 | -6.4092e-05 | -0.0043057 | -0.011877 | 0.0058906 | -0.01755 | -0.0044395 | -0.0029805 | 0.016408 | 0.03775 | 0.0098772 | 4.6298 | 4.6807 | 4.4829 | 4.571 | 4.6525 | 4.748 | 4.3831 | 0.02852 | 0.073618 | -0.065509 | -0.052847 | 0.059493 | 0.090166 | -0.14583 | 4.4472 | -118.1005 | 4.6939 | 4.547 | 0.099806 | -118.019 | -117.9235 | -0.081746 | -122.7244 | 0.092607 | -0.001422 | 0.080324 | -122.612 | -122.5813 | 4.6351 | 4.7166 | 4.8121 | 4.7448 | -118.2884 | 0.01124 | 0.12358 | 0.15425 | 0.13771 | -122.8173
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0038783 | -0.012305 | 0.0058906 | -0.01755 | -0.0050803 | -0.0025533 | 0.016408 | 0.03775 | 0.0098772 | 4.6161 | 4.6807 | 4.4783 | 4.5664 | 4.6388 | 4.7389 | 4.3785 | 0.019362 | 0.078197 | -0.056351 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 4.4929 | -118.1326 | 4.7305 | 4.5927 | 0.099806 | -118.0602 | -117.9601 | -0.035971 | -122.7564 | 0.1338 | 0.05809 | 0.094061 | -122.6395 | -122.6088 | 4.6809 | 4.7533 | 4.8533 | 4.7952 | -118.3205 | 0.057016 | 0.17393 | 0.20461 | 0.19264 | -122.8494
|  |  |  | 1.4211e-13 | -0.038752 | -0.00027769 | -0.0036647 | -0.012091 | 0.0061044 | -0.01755 | -0.0050803 | -0.0025533 | 0.016195 | 0.037963 | 0.0096636 | 4.6161 | 4.667 | 4.4737 | 4.5573 | 4.6251 | 4.7389 | 4.3648 | 0.019362 | 0.078197 | -0.065509 | -0.057425 | 0.064071 | 0.085587 | -0.14583 | 4.438 | -118.1234 | 4.6893 | 4.547 | 0.10896 | -118.0556 | -117.9418 | -0.072591 | -122.7381 | 0.092604 | 0.007733 | 0.080324 | -122.6166 | -122.5951 | 4.6305 | 4.6983 | 4.8121 | 4.7402 | -118.3159 | 0.015817 | 0.13731 | 0.15883 | 0.15144 | -122.8265
|  |  |  | 1.4211e-13 | -0.038965 | -0.00049149 | -0.0038783 | -0.012091 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016195 | 0.03775 | 0.0098772 | 4.6023 | 4.6624 | 4.4691 | 4.5481 | 4.6205 | 4.7297 | 4.3602 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.059493 | 0.085587 | -0.14583 | 4.4655 | -118.1554 | 4.7076 | 4.5744 | 0.10896 | -118.0831 | -117.9738 | -0.040547 | -122.7701 | 0.12923 | 0.039777 | 0.080324 | -122.6441 | -122.618 | 4.6534 | 4.7258 | 4.835 | 4.7677 | -118.3434 | 0.038704 | 0.16478 | 0.19087 | 0.18348 | -122.8494
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0040921 | -0.011877 | 0.0061044 | -0.01755 | -0.0048667 | -0.0027669 | 0.015981 | 0.037536 | 0.0098772 | 4.5977 | 4.667 | 4.4646 | 4.5481 | 4.6205 | 4.7206 | 4.3556 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.090166 | -0.14125 | 4.4563 | -118.1371 | 4.6985 | 4.5653 | 0.10897 | -118.0647 | -117.9647 | -0.040547 | -122.7427 | 0.12465 | 0.035199 | 0.075746 | -122.6257 | -122.5951 | 4.6488 | 4.7212 | 4.8213 | 4.7677 | -118.3296 | 0.043283 | 0.1602 | 0.19087 | 0.17891 | -122.8265
|  |  |  | 1.4211e-13 | -0.038965 | -0.00049149 | -0.0036647 | -0.012305 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0023397 | 0.016195 | 0.037536 | 0.0098772 | 4.5977 | 4.6578 | 4.46 | 4.5389 | 4.6113 | 4.716 | 4.351 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.4151 | -118.1051 | 4.6618 | 4.5241 | 0.10897 | -118.0327 | -117.9281 | -0.081746 | -122.706 | 0.092607 | 0.003157 | 0.084903 | -122.5845 | -122.5539 | 4.603 | 4.6754 | 4.7801 | 4.7219 | -118.293 | 0.002083 | 0.12358 | 0.15425 | 0.14228 | -122.7899
|  |  |  | 1.4211e-13 | -0.038324 | -0.00027769 | -0.0043057 | -0.012305 | 0.0058906 | 0.0053413 | -0.0046531 | -0.0025533 | 0.016195 | 0.037963 | 0.010091 | 4.5886 | 4.6533 | 4.4508 | 4.5344 | 4.6113 | 4.7206 | 4.3373 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.406 | -118.1509 | 4.6573 | 4.5195 | 0.11355 | -118.0739 | -117.9647 | -0.077168 | -122.7472 | 0.097185 | 0.003156 | 0.080324 | -122.6303 | -122.5951 | 4.603 | 4.68 | 4.7892 | 4.7219 | -118.348 | 0.006661 | 0.12358 | 0.15883 | 0.14686 | -122.8311
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0038783 | -0.012091 | 0.006318 | -0.0099192 | -0.0050803 | -0.0027669 | 0.016195 | 0.03775 | 0.010091 | 4.584 | 4.6441 | 4.4554 | 4.5298 | 4.6022 | 4.7023 | 4.3464 | 0.014784 | 0.078197 | -0.065509 | -0.066582 | 0.06865 | 0.094744 | -0.14583 | 4.4105 | -118.1371 | 4.6481 | 4.5195 | 0.10897 | -118.0648 | -117.9647 | -0.081746 | -122.7335 | 0.078871 | -0.001422 | 0.080324 | -122.5983 | -122.5722 | 4.5939 | 4.6663 | 4.7663 | 4.7082 | -118.3205 | -0.002495 | 0.13274 | 0.15883 | 0.14228 | -122.8128
|  |  |  | 1.4211e-13 | -0.038965 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015981 | 0.037963 | 0.0096636 | 4.584 | 4.635 | 4.4463 | 4.5206 | 4.5884 | 4.6931 | 4.3281 | 0.02852 | 0.082776 | -0.056351 | -0.062004 | 0.059493 | 0.090166 | -0.14125 | 4.4243 | -118.1692 | 4.6801 | 4.5424 | 0.11813 | -118.1014 | -117.9967 | -0.045125 | -122.7518 | 0.12465 | 0.039779 | 0.084904 | -122.6303 | -122.5997 | 4.6168 | 4.6846 | 4.7892 | 4.7311 | -118.3617 | 0.034126 | 0.15562 | 0.1863 | 0.17891 | -122.8311
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0036647 | -0.01145 | 0.0061044 | -0.01755 | -0.0046531 | -0.0027669 | 0.015981 | 0.037963 | 0.010091 | 4.5657 | 4.6212 | 4.4234 | 4.5115 | 4.5839 | 4.6931 | 4.3144 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.064071 | 0.085587 | -0.14125 | 4.3922 | -118.1875 | 4.6435 | 4.5012 | 0.10897 | -118.1151 | -118.0059 | -0.063435 | -122.7656 | 0.10634 | 0.01689 | 0.080325 | -122.6349 | -122.6134 | 4.5893 | 4.6617 | 4.7709 | 4.699 | -118.3846 | 0.011238 | 0.14189 | 0.16341 | 0.15602 | -122.8402
|  |  |  | 1.4211e-13 | -0.038752 | -0.00027769 | -0.0040921 | -0.012091 | 0.0061044 | -0.0022892 | -0.0048667 | -0.0023397 | 0.015981 | 0.037963 | 0.0098772 | 4.5565 | 4.6258 | 4.4279 | 4.4977 | 4.5747 | 4.6748 | 4.319 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.14125 | 4.4243 | -118.1921 | 4.6618 | 4.5332 | 0.10897 | -118.1151 | -118.015 | -0.035969 | -122.7518 | 0.12923 | 0.044356 | 0.080325 | -122.6349 | -122.6042 | 4.603 | 4.68 | 4.7801 | 4.7311 | -118.3708 | 0.043282 | 0.1602 | 0.19087 | 0.18348 | -122.8311
|  |  |  | 1.4211e-13 | -0.038752 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.005677 | -0.01755 | -0.0048667 | -0.0025533 | 0.016195 | 0.038177 | 0.0098772 | 4.5611 | 4.6029 | 4.4142 | 4.4886 | 4.5747 | 4.6656 | 4.2961 | 0.023941 | 0.073618 | -0.06093 | -0.057425 | 0.054914 | 0.081008 | -0.14583 | 4.3739 | -118.1875 | 4.6389 | 4.492 | 0.11813 | -118.1014 | -118.0105 | -0.068013 | -122.7335 | 0.10176 | 0.01689 | 0.084903 | -122.6212 | -122.5951 | 4.5664 | 4.6525 | 4.7434 | 4.6807 | -118.38 | 0.020395 | 0.13273 | 0.15883 | 0.15144 | -122.8219
|  |  |  | 1.4211e-13 | -0.038538 | -0.00049149 | -0.0038783 | -0.012091 | 0.0061044 | -0.01755 | -0.0050803 | -0.0023397 | 0.016195 | 0.03775 | 0.0096636 | 4.5428 | 4.6121 | 4.4142 | 4.4932 | 4.5655 | 4.6702 | 4.3007 | 0.02852 | 0.078197 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.14583 | 4.4197 | -118.2287 | 4.6618 | 4.5332 | 0.11355 | -118.1563 | -118.0517 | -0.026814 | -122.7793 | 0.14754 | 0.058089 | 0.084903 | -122.6578 | -122.6317 | 4.6122 | 4.6846 | 4.7892 | 4.7311 | -118.4212 | 0.061594 | 0.18309 | 0.20919 | 0.19722 | -122.8677
|  |  |  | 1.4211e-13 | -0.038752 | -0.00027769 | -0.0038783 | -0.011877 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016622 | 0.03775 | 0.0098772 | 4.5428 | 4.5983 | 4.4005 | 4.4886 | 4.5564 | 4.6656 | 4.2915 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.085587 | -0.14583 | 4.3693 | -118.1509 | 4.6206 | 4.4783 | 0.10898 | -118.0831 | -117.9738 | -0.068013 | -122.7015 | 0.10176 | 0.012311 | 0.080324 | -122.5754 | -122.5539 | 4.5664 | 4.6342 | 4.7434 | 4.6761 | -118.348 | 0.015816 | 0.14189 | 0.16341 | 0.15602 | -122.7853
|  |  |  | 1.4211e-13 | -0.038752 | 0.00014951 | -0.0036647 | -0.012091 | 0.0058906 | -0.0022892 | -0.0050803 | -0.0023397 | 0.015981 | 0.037963 | 0.0096636 | 4.5337 | 4.5892 | 4.4005 | 4.4794 | 4.5427 | 4.6565 | 4.2915 | 0.02852 | 0.082776 | -0.056351 | -0.066582 | 0.059493 | 0.090166 | -0.15041 | 4.4014 | -118.2104 | 4.6435 | 4.5103 | 0.10898 | -118.1472 | -118.0334 | -0.040549 | -122.7564 | 0.13838 | 0.053512 | 0.094061 | -122.6303 | -122.5997 | 4.5893 | 4.6525 | 4.7663 | 4.699 | -118.3983 | 0.043281 | 0.16936 | 0.20003 | 0.19264 | -122.8402
|  |  |  | 1.4211e-13 | -0.039393 | -0.00049149 | -0.0038783 | -0.012091 | 0.006318 | -0.01755 | -0.0048667 | -0.0034079 | 0.016195 | 0.037963 | 0.0098772 | 4.5337 | 4.5754 | 4.3867 | 4.4703 | 4.5381 | 4.6427 | 4.2823 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.064071 | 0.081008 | -0.14583 | 4.3785 | -118.2241 | 4.6298 | 4.4829 | 0.1044 | -118.1563 | -118.0517 | -0.049703 | -122.7518 | 0.12465 | 0.030621 | 0.080324 | -122.6303 | -122.6134 | 4.5664 | 4.6342 | 4.7389 | 4.6716 | -118.4121 | 0.038705 | 0.1602 | 0.17714 | 0.16975 | -122.8402
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0038783 | -0.012305 | 0.0058906 | -0.01755 | -0.0048667 | -0.0025533 | 0.015767 | 0.03775 | 0.010091 | 4.5153 | 4.5846 | 4.3867 | 4.4703 | 4.5335 | 4.6427 | 4.2778 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15041 | 4.3693 | -118.2287 | 4.6069 | 4.4783 | 0.10898 | -118.1655 | -118.0562 | -0.058859 | -122.7564 | 0.11549 | 0.026044 | 0.084903 | -122.6395 | -122.6042 | 4.5618 | 4.625 | 4.7343 | 4.6761 | -118.4212 | 0.034128 | 0.15105 | 0.1863 | 0.17433 | -122.8494
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0034509 | -0.012305 | 0.006318 | -0.01755 | -0.0046531 | -0.0025533 | 0.016195 | 0.038177 | 0.0098772 | 4.5108 | 4.5754 | 4.3776 | 4.4611 | 4.5335 | 4.6336 | 4.2686 | 0.033099 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.085587 | -0.14125 | 4.383 | -118.2424 | 4.6252 | 4.492 | 0.10898 | -118.1701 | -118.07 | -0.026814 | -122.7656 | 0.14754 | 0.048932 | 0.075746 | -122.6395 | -122.618 | 4.5756 | 4.6479 | 4.748 | 4.6899 | -118.4349 | 0.052437 | 0.17851 | 0.20003 | 0.19264 | -122.8448
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0034509 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016195 | 0.037963 | 0.010091 | 4.5016 | 4.5663 | 4.3638 | 4.4428 | 4.5243 | 4.6244 | 4.264 | 0.02852 | 0.078197 | -0.056351 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 4.3739 | -118.2699 | 4.6115 | 4.4737 | 0.099823 | -118.1884 | -118.0883 | -0.040549 | -122.7701 | 0.13838 | 0.053512 | 0.094061 | -122.6532 | -122.6225 | 4.5527 | 4.6342 | 4.7343 | 4.6761 | -118.4487 | 0.052438 | 0.16936 | 0.20003 | 0.18806 | -122.8631
|  |  |  | 1.4211e-13 | -0.038965 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.0061044 | -0.01755 | -0.0050803 | -0.0023397 | 0.015981 | 0.03775 | 0.0096636 | 4.5016 | 4.5571 | 4.3638 | 4.4474 | 4.5106 | 4.629 | 4.2503 | 0.019362 | 0.078197 | -0.065509 | -0.071161 | 0.059493 | 0.085587 | -0.14583 | 4.3098 | -118.2196 | 4.5611 | 4.4234 | 0.11356 | -118.1563 | -118.0379 | -0.086324 | -122.7381 | 0.078871 | -0.006 | 0.080324 | -122.6074 | -122.5813 | 4.5069 | 4.5701 | 4.6885 | 4.6166 | -118.4166 | -0.011652 | 0.119 | 0.1451 | 0.13771 | -122.8128
|  |  |  | 1.4211e-13 | -0.038538 | -6.4092e-05 | -0.0040921 | -0.011877 | 0.0058906 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016195 | 0.038177 | 0.0098772 | 4.4924 | 4.5525 | 4.3593 | 4.4336 | 4.5106 | 4.6153 | 4.2411 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.094744 | -0.15041 | 4.3373 | -118.2745 | 4.5886 | 4.4554 | 0.11814 | -118.1975 | -118.0929 | -0.054282 | -122.7701 | 0.12465 | 0.030621 | 0.084903 | -122.6441 | -122.6134 | 4.5298 | 4.6067 | 4.7114 | 4.6487 | -118.467 | 0.034126 | 0.1602 | 0.19087 | 0.17433 | -122.8585
|  |  |  | 1.4211e-13 | -0.038538 | -0.00027769 | -0.0040921 | -0.012091 | 0.0058906 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.037963 | 0.0098772 | 4.4833 | 4.5434 | 4.3501 | 4.4336 | 4.4969 | 4.6061 | 4.2366 | 0.019362 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.099323 | -0.14583 | 4.2915 | -118.2424 | 4.5382 | 4.405 | 0.11356 | -118.1792 | -118.07 | -0.090901 | -122.7381 | 0.074294 | -0.005998 | 0.084903 | -122.6212 | -122.5768 | 4.4886 | 4.5518 | 4.661 | 4.5983 | -118.4395 | -0.007072 | 0.10985 | 0.15426 | 0.13771 | -122.8219
|  |  |  | 1.4211e-13 | -0.039179 | -6.4092e-05 | -0.0036647 | -0.011877 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016408 | 0.03775 | 0.010091 | 4.4787 | 4.5434 | 4.341 | 4.4199 | 4.4923 | 4.5924 | 4.232 | 0.02852 | 0.073618 | -0.06093 | -0.062004 | 0.050335 | 0.090166 | -0.14583 | 4.3647 | -118.2745 | 4.6115 | 4.4737 | 0.10898 | -118.2021 | -118.102 | -0.013082 | -122.7564 | 0.16127 | 0.071821 | 0.084903 | -122.6441 | -122.6042 | 4.5527 | 4.625 | 4.7251 | 4.6761 | -118.4624 | 0.070747 | 0.18309 | 0.22292 | 0.20637 | -122.8402
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0038783 | -0.012518 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0027669 | 0.015981 | 0.037963 | 0.0096636 | 4.4696 | 4.5388 | 4.3364 | 4.4153 | 4.4831 | 4.5924 | 4.2228 | 0.02852 | 0.078197 | -0.056351 | -0.066582 | 0.054914 | 0.081008 | -0.15041 | 4.2869 | -118.247 | 4.5336 | 4.4005 | 0.11356 | -118.1792 | -118.07 | -0.086325 | -122.7289 | 0.092607 | 0.007736 | 0.094061 | -122.6074 | -122.5813 | 4.4794 | 4.5472 | 4.6565 | 4.6029 | -118.4395 | -0.002495 | 0.119 | 0.1451 | 0.14228 | -122.8128
|  |  |  | 1.4211e-13 | -0.038752 | -0.00049149 | -0.0036647 | -0.011877 | 0.0058906 | -0.01755 | -0.0046531 | -0.0025533 | 0.016195 | 0.037963 | 0.0098772 | 4.465 | 4.5251 | 4.3272 | 4.4062 | 4.474 | 4.5832 | 4.2182 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.064071 | 0.085587 | -0.14583 | 4.3098 | -118.2928 | 4.5565 | 4.4188 | 0.10898 | -118.225 | -118.1158 | -0.05428 | -122.7564 | 0.11549 | 0.026044 | 0.080324 | -122.6349 | -122.6134 | 4.4977 | 4.5655 | 4.6748 | 4.6166 | -118.4807 | 0.034128 | 0.15562 | 0.17714 | 0.17433 | -122.8448
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0040921 | -0.012091 | 0.005677 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015767 | 0.03775 | 0.010091 | 4.4558 | 4.5205 | 4.3181 | 4.4016 | 4.474 | 4.5786 | 4.2137 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.3189 | -118.2928 | 4.5611 | 4.4234 | 0.10441 | -118.2204 | -118.1158 | -0.040547 | -122.7564 | 0.13381 | 0.039777 | 0.080324 | -122.6349 | -122.6042 | 4.5069 | 4.5793 | 4.6839 | 4.6258 | -118.4807 | 0.043282 | 0.16478 | 0.19545 | 0.18806 | -122.8402
|  |  |  | 1.4211e-13 | -0.038965 | -6.4092e-05 | -0.0040921 | -0.012305 | 0.0061044 | -0.01755 | -0.0048667 | -0.0031943 | 0.015981 | 0.038604 | 0.0094498 | 4.4467 | 4.5159 | 4.3089 | 4.397 | 4.4602 | 4.5695 | 4.1999 | 0.02852 | 0.087354 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.3006 | -118.2928 | 4.5474 | 4.4096 | 0.10899 | -118.2296 | -118.1203 | -0.045125 | -122.7518 | 0.12923 | 0.035199 | 0.080324 | -122.6349 | -122.5997 | 4.4977 | 4.5609 | 4.6702 | 4.6166 | -118.4899 | 0.038704 | 0.15562 | 0.19087 | 0.18806 | -122.8357
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0040921 | -0.012305 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016195 | 0.037963 | 0.0098772 | 4.4421 | 4.5068 | 4.3043 | 4.3924 | 4.4602 | 4.5695 | 4.1953 | 0.023941 | 0.078197 | -0.070087 | -0.062004 | 0.054914 | 0.085587 | -0.14583 | 4.2732 | -118.2791 | 4.5199 | 4.3822 | 0.10899 | -118.2113 | -118.102 | -0.068013 | -122.7335 | 0.10176 | 0.007733 | 0.075746 | -122.6166 | -122.5859 | 4.4703 | 4.5381 | 4.6473 | 4.5846 | -118.4762 | 0.015816 | 0.13273 | 0.16341 | 0.15602 | -122.8173
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0040921 | -0.012091 | 0.0058906 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.038177 | 0.0096636 | 4.4375 | 4.4976 | 4.2998 | 4.3787 | 4.4465 | 4.5649 | 4.1862 | 0.019362 | 0.082776 | -0.070087 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 4.2503 | -118.3065 | 4.5016 | 4.3638 | 0.11357 | -118.2387 | -118.1203 | -0.086325 | -122.7427 | 0.083449 | -0.006 | 0.080325 | -122.6303 | -122.5997 | 4.4428 | 4.5106 | 4.629 | 4.5617 | -118.4991 | 0.006662 | 0.119 | 0.14967 | 0.14686 | -122.8357
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0038783 | -0.012305 | 0.0058906 | -0.0022892 | -0.0046531 | -0.0025533 | 0.016195 | 0.037963 | 0.0098772 | 4.4283 | 4.4976 | 4.2814 | 4.3695 | 4.4373 | 4.5466 | 4.1816 | 0.019362 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.14583 | 4.2915 | -118.3386 | 4.5382 | 4.3913 | 0.099833 | -118.2708 | -118.1615 | -0.03597 | -122.7656 | 0.12923 | 0.044354 | 0.080324 | -122.6486 | -122.6134 | 4.4794 | 4.5472 | 4.6564 | 4.6075 | -118.5265 | 0.052438 | 0.16936 | 0.20461 | 0.18806 | -122.854
|  |  |  | 1.4211e-13 | -0.039393 | -0.00049149 | -0.0038783 | -0.011664 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.03775 | 0.0098772 | 4.4238 | 4.4884 | 4.2814 | 4.365 | 4.4373 | 4.5466 | 4.177 | 0.023941 | 0.078197 | -0.056351 | -0.066582 | 0.064071 | 0.081008 | -0.14125 | 4.2365 | -118.3477 | 4.4833 | 4.3409 | 0.10441 | -118.2754 | -118.1661 | -0.081746 | -122.7793 | 0.08345 | 0.003158 | 0.084904 | -122.6486 | -122.6317 | 4.4245 | 4.4968 | 4.6061 | 4.5479 | -118.5357 | -0.007073 | 0.12358 | 0.14052 | 0.13771 | -122.854
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0036647 | -0.012305 | 0.005677 | -0.0022892 | -0.0050803 | -0.0025533 | 0.016195 | 0.03775 | 0.0098772 | 4.4192 | 4.4793 | 4.2814 | 4.3604 | 4.4373 | 4.542 | 4.1816 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.059493 | 0.090166 | -0.15041 | 4.2503 | -118.3294 | 4.4879 | 4.3501 | 0.099833 | -118.2525 | -118.1478 | -0.081747 | -122.7564 | 0.092606 | 0.007735 | 0.089482 | -122.6303 | -122.5997 | 4.4291 | 4.506 | 4.6107 | 4.5479 | -118.5082 | 0.002083 | 0.12816 | 0.15883 | 0.15144 | -122.8402
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0036647 | -0.012091 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.03775 | 0.0098772 | 4.41 | 4.4747 | 4.2723 | 4.3604 | 4.419 | 4.5328 | 4.1679 | 0.033099 | 0.078197 | -0.065509 | -0.066582 | 0.050335 | 0.090166 | -0.14583 | 4.264 | -118.3844 | 4.5062 | 4.3684 | 0.10441 | -118.3257 | -118.2119 | -0.049703 | -122.8113 | 0.12923 | 0.030621 | 0.080324 | -122.6944 | -122.6546 | 4.4565 | 4.5152 | 4.629 | 4.5708 | -118.5769 | 0.029548 | 0.14646 | 0.1863 | 0.17433 | -122.8906
|  |  |  | 1.4211e-13 | -0.039393 | -0.00027769 | -0.0036647 | -0.012091 | 0.0058906 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016195 | 0.038177 | 0.0096636 | 4.3963 | 4.4655 | 4.2677 | 4.3512 | 4.4236 | 4.5374 | 4.1541 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.059493 | 0.099323 | -0.14125 | 4.232 | -118.3615 | 4.4741 | 4.3455 | 0.11357 | -118.2891 | -118.1753 | -0.063435 | -122.7701 | 0.10634 | 0.012311 | 0.075746 | -122.6532 | -122.6134 | 4.4291 | 4.5014 | 4.6152 | 4.5434 | -118.5586 | 0.020395 | 0.13731 | 0.17714 | 0.15144 | -122.854
|  |  |  | 1.4211e-13 | -0.038965 | -0.00049149 | -0.0038783 | -0.012091 | 0.0061044 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015767 | 0.038177 | 0.0096636 | 4.4055 | 4.461 | 4.254 | 4.3467 | 4.4099 | 4.5191 | 4.145 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.045757 | 0.085587 | -0.14125 | 4.2045 | -118.334 | 4.465 | 4.3135 | 0.109 | -118.2708 | -118.1616 | -0.081746 | -122.7381 | 0.08345 | -0.006 | 0.075746 | -122.6349 | -122.5951 | 4.4062 | 4.4694 | 4.5786 | 4.5205 | -118.5357 | 0.002084 | 0.10527 | 0.1451 | 0.13771 | -122.8219
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0036647 | -0.011877 | 0.006318 | -0.0099192 | -0.0046531 | -0.0023397 | 0.016195 | 0.038177 | 0.0096636 | 4.3871 | 4.4518 | 4.2494 | 4.3283 | 4.3961 | 4.5054 | 4.145 | 0.023941 | 0.073618 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.14583 | 4.2503 | -118.3935 | 4.4924 | 4.3547 | 0.10442 | -118.3257 | -118.2165 | -0.040547 | -122.7839 | 0.12923 | 0.044356 | 0.084903 | -122.6624 | -122.6363 | 4.4336 | 4.5014 | 4.6107 | 4.5571 | -118.5769 | 0.043282 | 0.16478 | 0.19087 | 0.1789 | -122.8677
|  |  |  | 1.4211e-13 | -0.038965 | -0.00049149 | -0.0040921 | -0.012305 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016408 | 0.037963 | 0.0096636 | 4.3734 | 4.4427 | 4.2494 | 4.3238 | 4.4007 | 4.5008 | 4.1358 | 0.02852 | 0.082776 | -0.070087 | -0.052847 | 0.059493 | 0.090166 | -0.14125 | 4.2319 | -118.3889 | 4.4695 | 4.3455 | 0.11357 | -118.312 | -118.2119 | -0.045125 | -122.7656 | 0.12465 | 0.026043 | 0.071168 | -122.6532 | -122.6225 | 4.4199 | 4.4968 | 4.5969 | 4.5388 | -118.5769 | 0.043283 | 0.15562 | 0.1863 | 0.17891 | -122.854
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0040921 | -0.012091 | 0.0061044 | -0.01755 | -0.0050803 | -0.0027669 | 0.015767 | 0.038391 | 0.0098772 | 4.3734 | 4.4427 | 4.2311 | 4.3238 | 4.3915 | 4.4962 | 4.1312 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.081008 | -0.15499 | 4.2594 | -118.3798 | 4.5016 | 4.3593 | 0.09984 | -118.312 | -118.2073 | -0.026817 | -122.7656 | 0.15212 | 0.067244 | 0.094061 | -122.6486 | -122.6225 | 4.4519 | 4.5197 | 4.6244 | 4.5708 | -118.5723 | 0.06617 | 0.18309 | 0.20918 | 0.21095 | -122.8585
|  |  |  | 1.4211e-13 | -0.038752 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.0061044 | -0.02518 | -0.0050803 | -0.0025533 | 0.015981 | 0.038391 | 0.0098772 | 4.3734 | 4.4335 | 4.2402 | 4.3192 | 4.3732 | 4.4962 | 4.1312 | 0.033099 | 0.078197 | -0.065509 | -0.062004 | 0.045757 | 0.090166 | -0.14583 | 4.2411 | -118.3844 | 4.4833 | 4.3501 | 0.109 | -118.3303 | -118.2073 | -0.03597 | -122.7656 | 0.14296 | 0.044354 | 0.080324 | -122.6578 | -122.6134 | 4.429 | 4.4831 | 4.6061 | 4.5434 | -118.5723 | 0.047859 | 0.15562 | 0.20003 | 0.18806 | -122.8494
|  |  |  | 1.4211e-13 | -0.038752 | -0.00027769 | -0.0038783 | -0.012091 | 0.0058906 | -0.0022892 | -0.0048667 | -0.0023397 | 0.016195 | 0.038177 | 0.0096636 | 4.3597 | 4.4289 | 4.2219 | 4.3055 | 4.3778 | 4.4871 | 4.1129 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.064071 | 0.085587 | -0.14125 | 4.2274 | -118.4027 | 4.4741 | 4.3364 | 0.109 | -118.3303 | -118.2211 | -0.026814 | -122.7656 | 0.13838 | 0.053511 | 0.080325 | -122.6441 | -122.6225 | 4.4199 | 4.4923 | 4.6015 | 4.5434 | -118.5952 | 0.057016 | 0.17851 | 0.20003 | 0.19722 | -122.8494
|  |  |  | 1.4211e-13 | -0.038752 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.0061044 | -0.0022892 | -0.0046531 | -0.0025533 | 0.015767 | 0.037963 | 0.0094498 | 4.3551 | 4.4243 | 4.2128 | 4.2963 | 4.3687 | 4.4825 | 4.1175 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.050335 | 0.085587 | -0.15957 | 4.1724 | -118.3935 | 4.41 | 4.2677 | 0.095264 | -118.3212 | -118.2073 | -0.10464 | -122.7472 | 0.078873 | -0.005998 | 0.09864 | -122.6395 | -122.6042 | 4.3512 | 4.4236 | 4.5374 | 4.4793 | -118.5723 | -0.002493 | 0.10527 | 0.14052 | 0.13313 | -122.8494
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0036647 | -0.011877 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.037963 | 0.0098772 | 4.3459 | 4.4152 | 4.2082 | 4.2917 | 4.3687 | 4.4733 | 4.1038 | 0.02852 | 0.078197 | -0.070087 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 4.1999 | -118.4347 | 4.4421 | 4.3043 | 0.10442 | -118.3578 | -118.2531 | -0.049703 | -122.7839 | 0.12465 | 0.026043 | 0.075746 | -122.6669 | -122.6409 | 4.3878 | 4.4648 | 4.5695 | 4.5113 | -118.6227 | 0.038705 | 0.15562 | 0.18172 | 0.17433 | -122.8723
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0038783 | -0.012091 | 0.0058906 | -0.0022892 | -0.0048667 | -0.0025533 | 0.016195 | 0.038177 | 0.0098772 | 4.3414 | 4.406 | 4.2036 | 4.2917 | 4.3595 | 4.4642 | 4.0946 | 0.033099 | 0.06904 | -0.065509 | -0.066582 | 0.059493 | 0.085587 | -0.13668 | 4.1953 | -118.421 | 4.4421 | 4.3043 | 0.109 | -118.3532 | -118.2485 | -0.035968 | -122.7793 | 0.13381 | 0.035199 | 0.071167 | -122.6532 | -122.6271 | 4.3924 | 4.4602 | 4.5649 | 4.5067 | -118.6181 | 0.034126 | 0.1602 | 0.18629 | 0.16975 | -122.8494
|  |  |  | 1.4211e-13 | -0.039393 | -0.00027769 | -0.0036647 | -0.012305 | 0.0061044 | -0.01755 | -0.0050803 | -0.0023397 | 0.016408 | 0.037963 | 0.0096636 | 4.3505 | 4.4106 | 4.2082 | 4.2871 | 4.3549 | 4.4642 | 4.09 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.1953 | -118.4027 | 4.4558 | 4.3135 | 0.11816 | -118.3349 | -118.2257 | -0.040547 | -122.7518 | 0.12923 | 0.044356 | 0.084903 | -122.6303 | -122.5997 | 4.3924 | 4.4602 | 4.5695 | 4.5159 | -118.5998 | 0.043282 | 0.16478 | 0.19545 | 0.18806 | -122.8357
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0038783 | -0.011877 | 0.005677 | -0.01755 | -0.0048667 | -0.0023397 | 0.016195 | 0.037963 | 0.0098772 | 4.3276 | 4.4014 | 4.1945 | 4.2734 | 4.3503 | 4.455 | 4.0854 | 0.023941 | 0.087354 | -0.065509 | -0.057425 | 0.045757 | 0.085587 | -0.14583 | 4.2045 | -118.4439 | 4.4466 | 4.3135 | 0.109 | -118.3669 | -118.2623 | -0.026814 | -122.7747 | 0.14296 | 0.05351 | 0.080324 | -122.6715 | -122.6317 | 4.3924 | 4.4694 | 4.574 | 4.5205 | -118.6318 | 0.061594 | 0.16478 | 0.20461 | 0.20637 | -122.8631
|  |  |  | 1.4211e-13 | -0.038965 | -6.4092e-05 | -0.0040921 | -0.012091 | 0.0058906 | -0.0022892 | -0.0050803 | -0.0025533 | 0.016408 | 0.037963 | 0.0096636 | 4.3276 | 4.3969 | 4.1945 | 4.2734 | 4.3412 | 4.4596 | 4.0854 | 0.019362 | 0.082776 | -0.065509 | -0.062004 | 0.050335 | 0.085587 | -0.15041 | 4.2045 | -118.4622 | 4.4466 | 4.3135 | 0.109 | -118.3944 | -118.276 | -0.031393 | -122.7976 | 0.13838 | 0.05351 | 0.084903 | -122.6853 | -122.65 | 4.3924 | 4.4602 | 4.5786 | 4.5159 | -118.6501 | 0.057015 | 0.16935 | 0.20461 | 0.2018 | -122.886
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0038783 | -0.011664 | 0.0058906 | -0.0099192 | -0.0050803 | -0.0025533 | 0.016195 | 0.037963 | 0.0096636 | 4.3185 | 4.3969 | 4.1807 | 4.2688 | 4.332 | 4.4504 | 4.0809 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.15041 | 4.1404 | -118.421 | 4.378 | 4.2402 | 0.099848 | -118.3578 | -118.2394 | -0.090903 | -122.7518 | 0.08345 | -0.001421 | 0.089482 | -122.6303 | -122.6042 | 4.3283 | 4.3915 | 4.5099 | 4.4564 | -118.6089 | -0.002495 | 0.119 | 0.1451 | 0.13771 | -122.8402
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0034509 | -0.012305 | 0.0061044 | -0.0022892 | -0.0048667 | -0.0027669 | 0.015981 | 0.037963 | 0.0098772 | 4.3139 | 4.3877 | 4.1853 | 4.2642 | 4.3366 | 4.4413 | 4.0763 | 0.023941 | 0.078197 | -0.070087 | -0.062004 | 0.059493 | 0.085587 | -0.15041 | 4.1907 | -118.453 | 4.4283 | 4.2997 | 0.10901 | -118.3807 | -118.276 | -0.035971 | -122.7793 | 0.13838 | 0.044354 | 0.080325 | -122.6578 | -122.6317 | 4.3787 | 4.451 | 4.5557 | 4.5021 | -118.641 | 0.052437 | 0.17393 | 0.20003 | 0.19264 | -122.8677
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.011877 | 0.0058906 | -0.01755 | -0.0046531 | -0.0027669 | 0.015981 | 0.03775 | 0.0094498 | 4.3139 | 4.3831 | 4.1716 | 4.2597 | 4.3229 | 4.4367 | 4.0671 | 0.019362 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.14125 | 4.1404 | -118.4393 | 4.3871 | 4.2448 | 0.10443 | -118.3761 | -118.2623 | -0.068013 | -122.761 | 0.092604 | 0.007733 | 0.075746 | -122.6395 | -122.6088 | 4.3329 | 4.3961 | 4.5099 | 4.4564 | -118.6318 | 0.011238 | 0.13273 | 0.16341 | 0.15144 | -122.8402
|  |  |  | 1.4211e-13 | -0.039179 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.0058906 | -0.0022892 | -0.0046531 | -0.0025533 | 0.015981 | 0.037963 | 0.0098772 | 4.3002 | 4.3694 | 4.167 | 4.2551 | 4.3274 | 4.4321 | 4.0626 | 0.019362 | 0.073618 | -0.06093 | -0.062004 | 0.050335 | 0.090166 | -0.14583 | 4.145 | -118.4668 | 4.3826 | 4.2494 | 0.10443 | -118.3944 | -118.2897 | -0.063436 | -122.7839 | 0.10176 | 0.021467 | 0.084903 | -122.6715 | -122.6317 | 4.3375 | 4.4098 | 4.5145 | 4.4518 | -118.6593 | 0.020393 | 0.13273 | 0.17256 | 0.15602 | -122.8677
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0036647 | -0.011877 | 0.0058906 | -0.0099192 | -0.0052939 | -0.0025533 | 0.016195 | 0.037963 | 0.0096636 | 4.3002 | 4.374 | 4.1624 | 4.2505 | 4.3229 | 4.4321 | 4.0626 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 4.1221 | -118.4622 | 4.3597 | 4.2219 | 0.09985 | -118.3898 | -118.2806 | -0.090903 | -122.7701 | 0.08345 | -0.010578 | 0.080325 | -122.6578 | -122.6271 | 4.31 | 4.3824 | 4.4916 | 4.4335 | -118.6502 | 0.002084 | 0.11442 | 0.1451 | 0.14228 | -122.8631
|  |  |  | 1.4211e-13 | -0.038965 | -0.00070509 | -0.0038783 | -0.011877 | 0.005677 | -0.0099192 | -0.0046531 | -0.0023397 | 0.015981 | 0.038177 | 0.0096636 | 4.291 | 4.3694 | 4.1624 | 4.2414 | 4.3137 | 4.4184 | 4.0488 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.15041 | 4.1495 | -118.4851 | 4.3917 | 4.2631 | 0.11359 | -118.4127 | -118.3081 | -0.049704 | -122.7839 | 0.12465 | 0.039778 | 0.089482 | -122.6624 | -122.6363 | 4.3421 | 4.4144 | 4.5191 | 4.4701 | -118.6776 | 0.043283 | 0.16478 | 0.19087 | 0.18348 | -122.8769
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0040921 | -0.012091 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.037963 | 0.0098772 | 4.2864 | 4.3557 | 4.1578 | 4.2276 | 4.3091 | 4.423 | 4.0534 | 0.033099 | 0.082776 | -0.065509 | -0.057425 | 0.064071 | 0.085587 | -0.14583 | 4.1541 | -118.5171 | 4.3871 | 4.2585 | 0.10443 | -118.4356 | -118.3218 | -0.045125 | -122.8022 | 0.13381 | 0.035199 | 0.080324 | -122.6807 | -122.6592 | 4.3283 | 4.4098 | 4.5237 | 4.4564 | -118.6914 | 0.043283 | 0.16478 | 0.18629 | 0.18348 | -122.8906
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0040921 | -0.012091 | 0.0052496 | -0.0099192 | -0.0048667 | -0.0027669 | 0.016195 | 0.038391 | 0.0098772 | 4.2818 | 4.3557 | 4.1441 | 4.2368 | 4.3045 | 4.4092 | 4.0442 | 0.023941 | 0.082776 | -0.065509 | -0.071161 | 0.059493 | 0.094744 | -0.15041 | 4.1404 | -118.4759 | 4.378 | 4.2402 | 0.099853 | -118.4082 | -118.3035 | -0.054282 | -122.7839 | 0.12007 | 0.030621 | 0.084903 | -122.6532 | -122.618 | 4.3329 | 4.4007 | 4.5054 | 4.4518 | -118.6685 | 0.024969 | 0.15562 | 0.19087 | 0.17891 | -122.8631
|  |  |  | 1.4211e-13 | -0.039393 | -0.00070509 | -0.0038783 | -0.012091 | 0.0061044 | -0.02518 | -0.0052939 | -0.0025533 | 0.016195 | 0.037963 | 0.0094498 | 4.2773 | 4.3465 | 4.1532 | 4.223 | 4.2954 | 4.4046 | 4.0397 | 0.02852 | 0.073618 | -0.056351 | -0.066582 | 0.059493 | 0.081008 | -0.14125 | 4.1404 | -118.4897 | 4.378 | 4.254 | 0.11359 | -118.4173 | -118.3081 | -0.040547 | -122.7793 | 0.12923 | 0.044357 | 0.084904 | -122.6532 | -122.6317 | 4.3237 | 4.3961 | 4.5054 | 4.4472 | -118.673 | 0.034126 | 0.1602 | 0.18172 | 0.17433 | -122.854
|  |  |  | 1.4211e-13 | -0.039393 | -0.00027769 | -0.0038783 | -0.012305 | 0.0058906 | -0.0022892 | -0.0048667 | -0.0021259 | 0.015981 | 0.038177 | 0.0096636 | 4.2773 | 4.3557 | 4.1441 | 4.2276 | 4.3 | 4.4092 | 4.0351 | 0.02852 | 0.082776 | -0.06093 | -0.052847 | 0.059493 | 0.090166 | -0.14583 | 4.1449 | -118.4714 | 4.3871 | 4.254 | 0.10901 | -118.399 | -118.2898 | -0.03597 | -122.7518 | 0.13838 | 0.048933 | 0.084903 | -122.6395 | -122.6088 | 4.3375 | 4.4098 | 4.5191 | 4.4655 | -118.6639 | 0.057016 | 0.16936 | 0.20003 | 0.19264 | -122.8448
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0036647 | -0.011877 | 0.0058906 | -0.01755 | -0.0046531 | -0.0025533 | 0.015981 | 0.038177 | 0.010091 | 4.2681 | 4.3419 | 4.1349 | 4.2185 | 4.2862 | 4.3909 | 4.0351 | 0.019362 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 4.1404 | -118.508 | 4.3734 | 4.2402 | 0.099855 | -118.4402 | -118.3355 | -0.040547 | -122.7884 | 0.12465 | 0.044356 | 0.084903 | -122.6669 | -122.6363 | 4.3237 | 4.3915 | 4.4962 | 4.4472 | -118.6914 | 0.043282 | 0.16478 | 0.19545 | 0.18348 | -122.8723
|  |  |  | 1.4211e-13 | -0.039393 | -0.00049149 | -0.0038783 | -0.012091 | 0.0058906 | -0.0022892 | -0.0048667 | -0.0025533 | 0.015981 | 0.038177 | 0.0094498 | 4.2589 | 4.3465 | 4.1212 | 4.2139 | 4.2908 | 4.3955 | 4.0259 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 4.09 | -118.4942 | 4.323 | 4.1853 | 0.095278 | -118.4173 | -118.3126 | -0.086325 | -122.7656 | 0.088028 | -0.001422 | 0.084903 | -122.6532 | -122.6225 | 4.278 | 4.3549 | 4.4596 | 4.4106 | -118.6822 | 0.006662 | 0.119 | 0.14967 | 0.14228 | -122.8585
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0038783 | -0.012305 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.038391 | 0.0094498 | 4.2681 | 4.3419 | 4.1395 | 4.2139 | 4.2862 | 4.3909 | 4.0259 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.045757 | 0.081008 | -0.15041 | 4.1495 | -118.508 | 4.3917 | 4.2631 | 0.11359 | -118.4356 | -118.331 | -0.026816 | -122.7793 | 0.14754 | 0.062666 | 0.089482 | -122.6761 | -122.6409 | 4.3375 | 4.4098 | 4.5145 | 4.4655 | -118.6959 | 0.066171 | 0.16935 | 0.2046 | 0.20179 | -122.8723
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0040921 | -0.012091 | 0.0058906 | -0.0099192 | -0.0055075 | -0.0029805 | 0.015981 | 0.038391 | 0.0098772 | 4.2589 | 4.3373 | 4.1258 | 4.2093 | 4.2908 | 4.3955 | 4.0213 | 0.02852 | 0.06904 | -0.06093 | -0.057425 | 0.054914 | 0.090166 | -0.14125 | 4.09 | -118.4805 | 4.3276 | 4.1944 | 0.10444 | -118.399 | -118.2943 | -0.07259 | -122.7472 | 0.097185 | 0.007735 | 0.080325 | -122.6349 | -122.5997 | 4.278 | 4.3595 | 4.4642 | 4.406 | -118.6685 | 0.01124 | 0.12358 | 0.15883 | 0.13771 | -122.8311
|  |  |  | 1.4211e-13 | -0.039606 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.005677 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.038177 | 0.0094498 | 4.2589 | 4.3373 | 4.1258 | 4.2047 | 4.2817 | 4.3863 | 4.0213 | 0.023941 | 0.06904 | -0.070087 | -0.052847 | 0.054914 | 0.090166 | -0.14583 | 4.1358 | -118.54 | 4.3734 | 4.2402 | 0.10444 | -118.4631 | -118.3584 | -0.031392 | -122.7976 | 0.13838 | 0.044354 | 0.075746 | -122.6898 | -122.6546 | 4.3192 | 4.3961 | 4.5008 | 4.4518 | -118.7234 | 0.061594 | 0.16936 | 0.20461 | 0.18348 | -122.8906
|  |  |  | 1.4211e-13 | -0.039179 | -0.00027769 | -0.0038783 | -0.012305 | 0.005677 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.038391 | 0.0094498 | 4.2589 | 4.3373 | 4.1212 | 4.2047 | 4.2817 | 4.3863 | 4.0168 | 0.02852 | 0.082776 | -0.056351 | -0.066582 | 0.054914 | 0.090166 | -0.14583 | 4.09 | -118.5034 | 4.3322 | 4.1944 | 0.10444 | -118.4265 | -118.3218 | -0.072591 | -122.7747 | 0.10176 | 0.016891 | 0.089482 | -122.6532 | -122.618 | 4.278 | 4.3549 | 4.4596 | 4.4106 | -118.6914 | 0.00666 | 0.12816 | 0.16341 | 0.15602 | -122.854
|  |  |  | 1.4211e-13 | -0.038965 | -0.00027769 | -0.0038783 | -0.012091 | 0.005677 | -0.01755 | -0.0050803 | -0.0023397 | 0.015981 | 0.037963 | 0.0092362 | 4.2498 | 4.319 | 4.1075 | 4.2001 | 4.2725 | 4.3818 | 4.003 | 0.02852 | 0.087354 | -0.06093 | -0.066582 | 0.054914 | 0.090166 | -0.15041 | 4.0717 | -118.54 | 4.3185 | 4.1761 | 0.10444 | -118.4677 | -118.3584 | -0.081747 | -122.8068 | 0.097185 | 0.007735 | 0.089482 | -122.6853 | -122.65 | 4.2688 | 4.3412 | 4.4504 | 4.3877 | -118.7371 | 0.002083 | 0.12358 | 0.15883 | 0.15602 | -122.8906
|  |  |  | 1.4211e-13 | -0.03982 | -0.00049149 | -0.0038783 | -0.011664 | 0.0052496 | -0.0099192 | -0.0050803 | -0.0027669 | 0.016195 | 0.037963 | 0.0096636 | 4.2452 | 4.3236 | 4.1166 | 4.1864 | 4.2725 | 4.3726 | 4.003 | 0.02852 | 0.078197 | -0.06093 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 4.1266 | -118.5446 | 4.3688 | 4.2402 | 0.11359 | -118.4585 | -118.3584 | -0.022237 | -122.7884 | 0.15212 | 0.062666 | 0.084903 | -122.6715 | -122.6454 | 4.31 | 4.3961 | 4.4962 | 4.4472 | -118.728 | 0.066171 | 0.18309 | 0.20918 | 0.20179 | -122.8769
|  |  |  | 1.4211e-13 | -0.039606 | -6.4092e-05 | -0.0043057 | -0.011877 | 0.0058906 | -0.0099192 | -0.0046531 | -0.0027669 | 0.016195 | 0.038177 | 0.0096636 | 4.2406 | 4.319 | 4.0983 | 4.1864 | 4.2633 | 4.368 | 4.003 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.15041 | 4.122 | -118.54 | 4.3597 | 4.2173 | 0.09528 | -118.4631 | -118.3584 | -0.031393 | -122.7884 | 0.14754 | 0.058089 | 0.089482 | -122.6669 | -122.6409 | 4.3054 | 4.3824 | 4.487 | 4.438 | -118.7234 | 0.057015 | 0.17851 | 0.20461 | 0.19722 | -122.8769
|  |  |  | 1.4211e-13 | -0.039393 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.005677 | -0.01755 | -0.0048667 | -0.0027669 | 0.015981 | 0.038604 | 0.0098772 | 4.2269 | 4.3144 | 4.1029 | 4.1818 | 4.2496 | 4.3634 | 3.9939 | 0.02852 | 0.073618 | -0.070087 | -0.066582 | 0.059493 | 0.094744 | -0.14583 | 4.0854 | -118.5446 | 4.3185 | 4.1944 | 0.10902 | -118.4768 | -118.363 | -0.05428 | -122.793 | 0.12007 | 0.021466 | 0.075746 | -122.6669 | -122.6317 | 4.2734 | 4.3412 | 4.455 | 4.406 | -118.7326 | 0.024971 | 0.15105 | 0.1863 | 0.16517 | -122.8723
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0036647 | -0.012091 | 0.0058906 | -0.032811 | -0.0046531 | -0.0027669 | 0.015981 | 0.037963 | 0.0094498 | 4.2269 | 4.3144 | 4.0983 | 4.1727 | 4.2542 | 4.3634 | 3.9984 | 0.023941 | 0.078197 | -0.056351 | -0.062004 | 0.054914 | 0.085587 | -0.14583 | 4.1037 | -118.5492 | 4.3322 | 4.2036 | 0.099859 | -118.4677 | -118.3584 | -0.040547 | -122.7839 | 0.12923 | 0.048935 | 0.089482 | -122.6669 | -122.6363 | 4.278 | 4.3595 | 4.4687 | 4.4197 | -118.7234 | 0.043282 | 0.1602 | 0.19087 | 0.18348 | -122.8677
|  |  |  | 1.4211e-13 | -0.039606 | -0.00027769 | -0.0038783 | -0.012305 | 0.005677 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.038177 | 0.0094498 | 4.2269 | 4.3099 | 4.0983 | 4.1727 | 4.245 | 4.3589 | 3.9893 | 0.02852 | 0.073618 | -0.06093 | -0.057425 | 0.054914 | 0.090166 | -0.14583 | 4.0534 | -118.5171 | 4.291 | 4.1624 | 0.10902 | -118.4448 | -118.331 | -0.081746 | -122.7472 | 0.092607 | 0.003157 | 0.084903 | -122.6349 | -122.5997 | 4.2368 | 4.3091 | 4.4229 | 4.374 | -118.7005 | 0.006662 | 0.119 | 0.15425 | 0.13771 | -122.8357
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0034509 | -0.012091 | 0.005677 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015981 | 0.038177 | 0.0094498 | 4.2223 | 4.3053 | 4.0892 | 4.1727 | 4.2542 | 4.3634 | 3.9893 | 0.019362 | 0.078197 | -0.06093 | -0.066582 | 0.06865 | 0.090166 | -0.14583 | 4.0808 | -118.5171 | 4.3139 | 4.1807 | 0.099861 | -118.4356 | -118.3264 | -0.05428 | -122.7564 | 0.11091 | 0.030623 | 0.084903 | -122.6212 | -122.5997 | 4.2642 | 4.3457 | 4.455 | 4.3968 | -118.7005 | 0.024971 | 0.1602 | 0.18172 | 0.16975 | -122.8357
|  |  |  | 1.4211e-13 | -0.039179 | -0.00070509 | -0.0034509 | -0.012091 | 0.005677 | 0.0053413 | -0.0048667 | -0.0027669 | 0.016195 | 0.038391 | 0.0096636 | 4.2223 | 4.2961 | 4.08 | 4.1727 | 4.2404 | 4.3497 | 3.9801 | 0.023941 | 0.073618 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.15041 | 4.09 | -118.5629 | 4.3322 | 4.1899 | 0.099862 | -118.4952 | -118.3859 | -0.040549 | -122.7976 | 0.1338 | 0.048933 | 0.089482 | -122.6807 | -122.6454 | 4.2825 | 4.3503 | 4.4596 | 4.406 | -118.7555 | 0.047859 | 0.16478 | 0.20003 | 0.18348 | -122.886
|  |  |  | 1.4211e-13 | -0.039179 | -6.4092e-05 | -0.0038783 | -0.012091 | 0.005677 | -0.01755 | -0.0050803 | -0.0023397 | 0.016195 | 0.038177 | 0.0096636 | 4.2132 | 4.2916 | 4.0892 | 4.1589 | 4.2313 | 4.3405 | 3.971 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.14125 | 4.0671 | -118.5355 | 4.3093 | 4.1853 | 0.11818 | -118.4631 | -118.3539 | -0.045125 | -122.7564 | 0.12465 | 0.030621 | 0.075746 | -122.6349 | -122.6042 | 4.2551 | 4.3274 | 4.4367 | 4.3877 | -118.7234 | 0.034126 | 0.15562 | 0.1863 | 0.17891 | -122.8357
|  |  |  | 1.4211e-13 | -0.039393 | -0.00027769 | -0.0040921 | -0.012305 | 0.0058906 | -0.01755 | -0.0048667 | -0.0029805 | 0.015767 | 0.03775 | 0.0098772 | 4.204 | 4.2824 | 4.0708 | 4.1589 | 4.2267 | 4.336 | 3.9664 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 4.0442 | -118.5217 | 4.2818 | 4.1487 | 0.10444 | -118.454 | -118.3447 | -0.068013 | -122.7427 | 0.10176 | 0.012311 | 0.080324 | -122.6257 | -122.5905 | 4.2368 | 4.3045 | 4.4138 | 4.3602 | -118.7143 | 0.015816 | 0.13273 | 0.16799 | 0.15602 | -122.8265
|  |  |  | 1.4211e-13 | -0.039606 | 0.00014951 | -0.0038783 | -0.011877 | 0.0058906 | -0.0099192 | -0.0050803 | -0.0027669 | 0.015767 | 0.037963 | 0.0096636 | 4.1949 | 4.2824 | 4.0571 | 4.1498 | 4.2175 | 4.336 | 3.9572 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.054914 | 0.085587 | -0.14583 | 4.0671 | -118.5812 | 4.3047 | 4.167 | 0.099866 | -118.5135 | -118.3951 | -0.03597 | -122.7976 | 0.13838 | 0.048933 | 0.084903 | -122.6761 | -122.6454 | 4.2596 | 4.3274 | 4.4458 | 4.3923 | -118.7738 | 0.043281 | 0.16478 | 0.19545 | 0.18806 | -122.8769
|  |  |  | 1.4211e-13 | -0.039393 | -0.00049149 | -0.0040921 | -0.012091 | 0.005677 | -0.01755 | -0.0048667 | -0.0027669 | 0.015981 | 0.038391 | 0.0096636 | 4.1994 | 4.2687 | 4.0663 | 4.1452 | 4.213 | 4.3222 | 3.9527 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.085587 | -0.15041 | 4.0076 | -118.5767 | 4.2544 | 4.1212 | 0.1136 | -118.5089 | -118.3996 | -0.09548 | -122.7793 | 0.078873 | -0.010577 | 0.084903 | -122.6624 | -122.6363 | 4.2001 | 4.2679 | 4.3772 | 4.3236 | -118.7692 | -0.002493 | 0.11442 | 0.14052 | 0.13313 | -122.8723
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0038783 | -0.012091 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.037963 | 0.0096636 | 4.1903 | 4.2732 | 4.0525 | 4.1361 | 4.2084 | 4.3177 | 3.9481 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.054914 | 0.090166 | -0.14583 | 4.0167 | -118.5812 | 4.2589 | 4.1212 | 0.10444 | -118.5089 | -118.3996 | -0.077168 | -122.7747 | 0.092606 | 0.007735 | 0.084903 | -122.6624 | -122.6271 | 4.2047 | 4.2771 | 4.3863 | 4.3419 | -118.7692 | 0.01124 | 0.12358 | 0.15883 | 0.14686 | -122.8631
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0043057 | -0.012305 | 0.005677 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.038391 | 0.0098772 | 4.1903 | 4.2595 | 4.0479 | 4.1315 | 4.1947 | 4.3177 | 3.9435 | 0.019362 | 0.073618 | -0.070087 | -0.062004 | 0.050335 | 0.085587 | -0.14125 | 4.0488 | -118.5904 | 4.2956 | 4.1532 | 0.10444 | -118.5272 | -118.4042 | -0.035969 | -122.7839 | 0.12465 | 0.035199 | 0.071168 | -122.6715 | -122.6363 | 4.2368 | 4.2999 | 4.4229 | 4.3648 | -118.7784 | 0.043282 | 0.15562 | 0.19087 | 0.1789 | -122.8631
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.012305 | 0.0058906 | -0.0022892 | -0.0048667 | -0.0027669 | 0.015767 | 0.038391 | 0.0096636 | 4.172 | 4.2549 | 4.0434 | 4.1223 | 4.1947 | 4.3085 | 3.9435 | 0.023941 | 0.073618 | -0.065509 | -0.057425 | 0.064071 | 0.081008 | -0.14583 | 4.0488 | -118.5995 | 4.2772 | 4.1487 | 0.099867 | -118.5272 | -118.4134 | -0.040547 | -122.7793 | 0.12923 | 0.039777 | 0.080324 | -122.6578 | -122.6409 | 4.2276 | 4.2999 | 4.4138 | 4.3602 | -118.7784 | 0.047861 | 0.16936 | 0.18629 | 0.1789 | -122.8677
|  |  |  | 1.4211e-13 | -0.039606 | -0.00027769 | -0.0038783 | -0.011664 | 0.0058906 | -0.0099192 | -0.0046531 | -0.0025533 | 0.016408 | 0.038177 | 0.0096636 | 4.172 | 4.2458 | 4.0342 | 4.1132 | 4.1855 | 4.2902 | 3.9206 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.059493 | 0.090166 | -0.14583 | 3.9938 | -118.5904 | 4.2452 | 4.1075 | 0.11361 | -118.5181 | -118.4134 | -0.072591 | -122.761 | 0.097183 | 0.012312 | 0.084903 | -122.6441 | -122.6134 | 4.1864 | 4.2587 | 4.3634 | 4.319 | -118.7829 | 0.015817 | 0.13273 | 0.16341 | 0.15144 | -122.8494
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.011664 | 0.0061044 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015767 | 0.038177 | 0.0094498 | 4.1628 | 4.2412 | 4.0296 | 4.1132 | 4.1855 | 4.2902 | 3.9206 | 0.033099 | 0.073618 | -0.065509 | -0.04369 | 0.054914 | 0.085587 | -0.14583 | 4.0167 | -118.6041 | 4.2589 | 4.1258 | 0.10903 | -118.5318 | -118.4271 | -0.049703 | -122.761 | 0.12923 | 0.030621 | 0.080324 | -122.6624 | -122.6317 | 4.2093 | 4.2816 | 4.3863 | 4.3373 | -118.7967 | 0.05244 | 0.15104 | 0.18172 | 0.16975 | -122.8631
|  |  |  | 1.4211e-13 | -0.039606 | -0.00070509 | -0.0038783 | -0.012305 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0029805 | 0.015981 | 0.038391 | 0.0096636 | 4.1536 | 4.2412 | 4.0159 | 4.0994 | 4.1763 | 4.2764 | 3.916 | 0.02852 | 0.078197 | -0.056351 | -0.071161 | 0.059493 | 0.085587 | -0.15041 | 4.0167 | -118.6453 | 4.2544 | 4.1166 | 0.099871 | -118.5684 | -118.4683 | -0.049704 | -122.8159 | 0.12923 | 0.044357 | 0.094061 | -122.6853 | -122.6592 | 4.2001 | 4.277 | 4.3772 | 4.3419 | -118.8287 | 0.029547 | 0.1602 | 0.18629 | 0.17891 | -122.8952
|  |  |  | 1.4211e-13 | -0.039393 | -0.00027769 | -0.0038783 | -0.011877 | 0.005677 | -0.02518 | -0.0050803 | -0.0027669 | 0.015981 | 0.038391 | 0.0094498 | 4.1582 | 4.232 | 4.0159 | 4.0948 | 4.1718 | 4.281 | 3.9114 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 3.9984 | -118.6408 | 4.2452 | 4.1029 | 0.10445 | -118.5638 | -118.4546 | -0.058858 | -122.7976 | 0.1155 | 0.021466 | 0.080324 | -122.6807 | -122.6454 | 4.1818 | 4.2587 | 4.368 | 4.319 | -118.8241 | 0.024971 | 0.14189 | 0.17714 | 0.16517 | -122.8814
|  |  |  | 1.4211e-13 | -0.039606 | -0.00091889 | -0.0040921 | -0.012091 | 0.005677 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.038177 | 0.0094498 | 4.1445 | 4.2275 | 4.0159 | 4.0903 | 4.1672 | 4.2719 | 3.9069 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14125 | 4.0167 | -118.6545 | 4.2544 | 4.1258 | 0.10903 | -118.5776 | -118.4729 | -0.031392 | -122.8068 | 0.1338 | 0.048933 | 0.080325 | -122.6898 | -122.6546 | 4.2001 | 4.277 | 4.3817 | 4.3373 | -118.8379 | 0.047859 | 0.16478 | 0.20003 | 0.18806 | -122.886
|  |  |  | 1.4211e-13 | -0.03982 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.005677 | -0.02518 | -0.0046531 | -0.0027669 | 0.015981 | 0.038391 | 0.0096636 | 4.1399 | 4.2183 | 4.0022 | 4.0857 | 4.1626 | 4.2673 | 3.8931 | 0.023941 | 0.073618 | -0.065509 | -0.066582 | 0.054914 | 0.085587 | -0.15041 | 4.0167 | -118.6545 | 4.2635 | 4.1258 | 0.10903 | -118.5776 | -118.4729 | -0.026816 | -122.8068 | 0.14754 | 0.058087 | 0.084903 | -122.6853 | -122.6546 | 4.2093 | 4.2862 | 4.3909 | 4.3419 | -118.847 | 0.057014 | 0.17851 | 0.20918 | 0.19721 | -122.8906
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0036647 | -0.012305 | 0.005677 | -0.01755 | -0.0050803 | -0.0025533 | 0.015981 | 0.038391 | 0.0098772 | 4.1308 | 4.2137 | 3.993 | 4.0811 | 4.1443 | 4.2673 | 3.8886 | 0.019362 | 0.078197 | -0.06093 | -0.057425 | 0.050335 | 0.090166 | -0.15041 | 3.9435 | -118.6179 | 4.1857 | 4.0479 | 0.10445 | -118.5547 | -118.4317 | -0.09548 | -122.7564 | 0.074294 | -0.005998 | 0.089482 | -122.6486 | -122.6088 | 4.136 | 4.1992 | 4.3222 | 4.2687 | -118.8104 | -0.002493 | 0.10527 | 0.1451 | 0.13313 | -122.8494
|  |  |  | 1.4211e-13 | -0.039393 | -0.00049149 | -0.0038783 | -0.012305 | 0.0061044 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.038391 | 0.0092362 | 4.1353 | 4.2091 | 3.9839 | 4.0811 | 4.1443 | 4.249 | 3.884 | 0.02852 | 0.078197 | -0.070087 | -0.057425 | 0.059493 | 0.085587 | -0.14125 | 3.9847 | -118.6408 | 4.236 | 4.0846 | 0.099875 | -118.5776 | -118.4729 | -0.040547 | -122.7793 | 0.12923 | 0.030621 | 0.071168 | -122.6624 | -122.6363 | 4.1818 | 4.245 | 4.3497 | 4.3098 | -118.8379 | 0.043283 | 0.1602 | 0.18629 | 0.17891 | -122.8631
|  |  |  | 1.4211e-13 | -0.040034 | -0.00049149 | -0.0036647 | -0.011877 | 0.0058906 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015767 | 0.038391 | 0.0096636 | 4.1262 | 4.2046 | 3.9793 | 4.0674 | 4.1443 | 4.2536 | 3.8794 | 0.023941 | 0.073618 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.15041 | 3.9526 | -118.6362 | 4.1994 | 4.0525 | 0.099876 | -118.5593 | -118.45 | -0.07717 | -122.7656 | 0.097183 | 0.012312 | 0.089482 | -122.6441 | -122.6134 | 4.1406 | 4.2175 | 4.3268 | 4.2778 | -118.8242 | 0.011238 | 0.13273 | 0.16341 | 0.14686 | -122.854
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.012091 | 0.0054634 | -0.01755 | -0.0050803 | -0.0027669 | 0.015767 | 0.038604 | 0.0094498 | 4.1124 | 4.1954 | 3.9839 | 4.0628 | 4.1397 | 4.249 | 3.8702 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.085587 | -0.14583 | 3.9435 | -118.6636 | 4.1857 | 4.0571 | 0.11361 | -118.5867 | -118.4775 | -0.072591 | -122.7884 | 0.10176 | 0.007733 | 0.080324 | -122.6624 | -122.6409 | 4.136 | 4.2129 | 4.3222 | 4.2686 | -118.8562 | 0.011238 | 0.13731 | 0.15883 | 0.15144 | -122.8723
|  |  |  | 1.4211e-13 | -0.039606 | -0.00027769 | -0.0038783 | -0.012305 | 0.005677 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015981 | 0.038604 | 0.0096636 | 4.1124 | 4.1908 | 3.9793 | 4.0628 | 4.1305 | 4.2398 | 3.8748 | 0.023941 | 0.073618 | -0.070087 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 3.9893 | -118.682 | 4.2269 | 4.0937 | 0.10446 | -118.6142 | -118.5049 | -0.031392 | -122.8022 | 0.13838 | 0.044354 | 0.075746 | -122.6853 | -122.6592 | 4.1772 | 4.245 | 4.3543 | 4.3053 | -118.8699 | 0.057016 | 0.17393 | 0.20003 | 0.18806 | -122.8906
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.012091 | 0.005677 | -0.01755 | -0.0050803 | -0.0025533 | 0.015981 | 0.038177 | 0.0094498 | 4.1033 | 4.1862 | 3.9701 | 4.0491 | 4.1305 | 4.2352 | 3.8657 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.064071 | 0.090166 | -0.14125 | 3.9435 | -118.6682 | 4.1811 | 4.0479 | 0.10446 | -118.5867 | -118.482 | -0.063435 | -122.7747 | 0.10634 | 0.012311 | 0.075746 | -122.6532 | -122.6271 | 4.1269 | 4.2084 | 4.3131 | 4.2641 | -118.8516 | 0.020395 | 0.14189 | 0.16799 | 0.15602 | -122.8585
|  |  |  | 1.4211e-13 | -0.039179 | -0.00049149 | -0.0038783 | -0.012091 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015981 | 0.037963 | 0.0096636 | 4.0941 | 4.1817 | 3.961 | 4.0399 | 4.1214 | 4.2261 | 3.8565 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 3.9709 | -118.6865 | 4.2086 | 4.0754 | 0.10446 | -118.605 | -118.5004 | -0.031392 | -122.7839 | 0.13838 | 0.053511 | 0.084903 | -122.6669 | -122.6409 | 4.1543 | 4.2358 | 4.3405 | 4.2961 | -118.8699 | 0.057016 | 0.17393 | 0.20003 | 0.19264 | -122.8723
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.011877 | 0.0054634 | -0.01755 | -0.0048667 | -0.0023397 | 0.015767 | 0.038604 | 0.0094498 | 4.0895 | 4.1679 | 3.9518 | 4.0262 | 4.1077 | 4.2123 | 3.8473 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 3.9709 | -118.714 | 4.2131 | 4.0754 | 0.10446 | -118.6325 | -118.5278 | -0.022237 | -122.8022 | 0.14754 | 0.062666 | 0.084903 | -122.6853 | -122.65 | 4.1498 | 4.2313 | 4.3359 | 4.2915 | -118.8928 | 0.061592 | 0.17851 | 0.21376 | 0.20637 | -122.886
|  |  |  | 1.4211e-13 | -0.03982 | -0.00070509 | -0.0038783 | -0.011877 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.038391 | 0.0096636 | 4.0804 | 4.1588 | 3.9472 | 4.0307 | 4.0985 | 4.2078 | 3.8382 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.054914 | 0.094744 | -0.14125 | 3.9252 | -118.7003 | 4.1674 | 4.0342 | 0.10904 | -118.6325 | -118.5233 | -0.05428 | -122.7884 | 0.1155 | 0.026045 | 0.080325 | -122.6761 | -122.6363 | 4.1177 | 4.1855 | 4.2947 | 4.2458 | -118.8928 | 0.02955 | 0.14189 | 0.18172 | 0.16975 | -122.8723
|  |  |  | 1.4211e-13 | -0.039606 | -0.00027769 | -0.0038783 | -0.012091 | 0.005677 | -0.0099192 | -0.0050803 | -0.0021259 | 0.015981 | 0.038391 | 0.0098772 | 4.0712 | 4.1588 | 3.9426 | 4.0262 | 4.0893 | 4.2123 | 3.8382 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.094744 | -0.14583 | 3.9526 | -118.7323 | 4.1857 | 4.0571 | 0.10446 | -118.6691 | -118.5461 | -0.031392 | -122.8205 | 0.13838 | 0.048932 | 0.080324 | -122.699 | -122.6637 | 4.1406 | 4.2038 | 4.3268 | 4.2732 | -118.9203 | 0.052437 | 0.17393 | 0.20919 | 0.19722 | -122.9043
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0038783 | -0.012091 | 0.0061044 | -0.01755 | -0.0048667 | -0.0027669 | 0.016195 | 0.038391 | 0.0092362 | 4.0758 | 4.1496 | 3.9335 | 4.017 | 4.0893 | 4.194 | 3.829 | 0.023941 | 0.073618 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.14583 | 3.9206 | -118.7323 | 4.1674 | 4.025 | 0.10446 | -118.66 | -118.5553 | -0.05428 | -122.8068 | 0.11549 | 0.030623 | 0.084903 | -122.6853 | -122.6592 | 4.1086 | 4.1809 | 4.2856 | 4.2412 | -118.9203 | 0.034128 | 0.15562 | 0.18172 | 0.16517 | -122.8952
|  |  |  | 1.4211e-13 | -0.039606 | -0.00049149 | -0.0036647 | -0.012091 | 0.0054634 | -0.01755 | -0.0050803 | -0.0027669 | 0.015981 | 0.038391 | 0.0090226 | 4.0621 | 4.145 | 3.9335 | 4.0033 | 4.0756 | 4.1895 | 3.829 | 0.02852 | 0.073618 | -0.06093 | -0.062004 | 0.059493 | 0.081008 | -0.14583 | 3.9343 | -118.7506 | 4.1674 | 4.0388 | 0.10446 | -118.6783 | -118.5645 | -0.040547 | -122.8159 | 0.13381 | 0.044356 | 0.084903 | -122.6944 | -122.6729 | 4.1086 | 4.1809 | 4.2947 | 4.2503 | -118.9249 | 0.043282 | 0.16478 | 0.18629 | 0.1789 | -122.8997
|  |  |  | 1.4211e-13 | -0.039606 | -0.00070509 | -0.0034509 | -0.012091 | 0.0058906 | -0.01755 | -0.0050803 | -0.0027669 | 0.015981 | 0.038604 | 0.0094498 | 4.0483 | 4.1405 | 3.9152 | 3.9987 | 4.0848 | 4.1803 | 3.8153 | 0.02852 | 0.06904 | -0.06093 | -0.057425 | 0.054914 | 0.090166 | -0.15041 | 3.8794 | -118.7049 | 4.1124 | 3.9793 | 0.099885 | -118.6188 | -118.5233 | -0.086325 | -122.761 | 0.092607 | 0.003157 | 0.089482 | -122.6486 | -122.6134 | 4.0628 | 4.1488 | 4.2444 | 4.2045 | -118.8883 | 0.006662 | 0.119 | 0.15425 | 0.13313 | -122.854
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0038783 | -0.012305 | 0.0054634 | -0.0099192 | -0.0050803 | -0.0027669 | 0.015981 | 0.038177 | 0.0092362 | 4.0483 | 4.1313 | 3.9152 | 3.9895 | 4.071 | 4.1757 | 3.8107 | 0.033099 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 3.8702 | -118.7369 | 4.1079 | 3.9747 | 0.10446 | -118.6554 | -118.5507 | -0.086324 | -122.7884 | 0.092608 | -0.001421 | 0.084903 | -122.6715 | -122.6363 | 4.0491 | 4.1305 | 4.2352 | 4.1908 | -118.9157 | -0.002495 | 0.11442 | 0.14968 | 0.13771 | -122.8723
|  |  |  | 1.4211e-13 | -0.039606 | -0.00027769 | -0.0038783 | -0.012305 | 0.0054634 | -0.0022892 | -0.0048667 | -0.0025533 | 0.015554 | 0.038391 | 0.0090226 | 4.0392 | 4.1221 | 3.9106 | 3.9895 | 4.0619 | 4.1711 | 3.8016 | 0.023941 | 0.082776 | -0.065509 | -0.052847 | 0.054914 | 0.090166 | -0.14583 | 3.8931 | -118.7506 | 4.1307 | 4.0022 | 0.10904 | -118.6783 | -118.569 | -0.05428 | -122.793 | 0.11549 | 0.026044 | 0.080324 | -122.6853 | -122.65 | 4.0811 | 4.1534 | 4.2627 | 4.2137 | -118.9386 | 0.038706 | 0.14647 | 0.18172 | 0.17433 | -122.886
|  |  |  | 1.4211e-13 | -0.03982 | -0.00070509 | -0.0038783 | -0.012305 | 0.0058906 | -0.01755 | -0.0050803 | -0.0025533 | 0.015554 | 0.038391 | 0.0094498 | 4.0255 | 4.1176 | 3.9014 | 3.9804 | 4.0619 | 4.162 | 3.7924 | 0.02852 | 0.091933 | -0.065509 | -0.062004 | 0.059493 | 0.085587 | -0.15499 | 3.8839 | -118.7552 | 4.117 | 3.993 | 0.10905 | -118.6737 | -118.5736 | -0.063438 | -122.7976 | 0.12007 | 0.026044 | 0.089482 | -122.6761 | -122.65 | 4.0719 | 4.1534 | 4.2535 | 4.2091 | -118.9432 | 0.029549 | 0.15105 | 0.17714 | 0.18349 | -122.8906
|  |  |  | 1.4211e-13 | -0.03982 | -0.00049149 | -0.0040921 | -0.012305 | 0.005677 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.038177 | 0.0092362 | 4.0255 | 4.1176 | 3.8877 | 3.9758 | 4.0481 | 4.1528 | 3.7832 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.094744 | -0.15041 | 3.9023 | -118.7689 | 4.1445 | 4.0067 | 0.10447 | -118.6966 | -118.5919 | -0.031393 | -122.8068 | 0.14754 | 0.05351 | 0.084903 | -122.6853 | -122.65 | 4.0948 | 4.1671 | 4.2718 | 4.2366 | -118.9615 | 0.057015 | 0.17851 | 0.21376 | 0.19722 | -122.8952
|  |  |  | 1.4211e-13 | -0.03982 | -0.00049149 | -0.0040921 | -0.012305 | 0.005677 | -0.01755 | -0.0050803 | -0.0027669 | 0.015767 | 0.038604 | 0.0094498 | 4.0255 | 4.1038 | 3.8831 | 3.9758 | 4.0435 | 4.1437 | 3.7832 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 3.8839 | -118.7506 | 4.1262 | 3.9838 | 0.09989 | -118.6829 | -118.5828 | -0.054283 | -122.7884 | 0.12923 | 0.035199 | 0.089482 | -122.6669 | -122.6363 | 4.0765 | 4.1443 | 4.2444 | 4.2045 | -118.9432 | 0.038704 | 0.1602 | 0.19087 | 0.17891 | -122.8814
|  |  |  | 1.4211e-13 | -0.040034 | -0.00027769 | -0.0038783 | -0.011877 | 0.005677 | -0.0099192 | -0.0050803 | -0.0027669 | 0.015981 | 0.038391 | 0.0092362 | 4.0071 | 4.0947 | 3.8694 | 3.9621 | 4.0344 | 4.1437 | 3.7741 | 0.023941 | 0.073618 | -0.06093 | -0.066582 | 0.059493 | 0.085587 | -0.15041 | 3.8519 | -118.7461 | 4.085 | 3.9472 | 0.095313 | -118.6737 | -118.5645 | -0.072592 | -122.7747 | 0.10176 | 0.01689 | 0.089482 | -122.6486 | -122.6225 | 4.0399 | 4.1122 | 4.2215 | 4.1725 | -118.934 | 0.011238 | 0.13731 | 0.16341 | 0.15144 | -122.8585
|  |  |  | 1.4211e-13 | -0.03982 | -6.4092e-05 | -0.0040921 | -0.012305 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.038818 | 0.0092362 | 4.0071 | 4.0993 | 3.8694 | 3.9575 | 4.0252 | 4.1345 | 3.7741 | 0.023941 | 0.073618 | -0.056351 | -0.062004 | 0.064071 | 0.090166 | -0.14583 | 3.8794 | -118.7827 | 4.1124 | 3.9747 | 0.095313 | -118.7149 | -118.6057 | -0.040547 | -122.8022 | 0.12923 | 0.048935 | 0.089482 | -122.6761 | -122.65 | 4.0628 | 4.1305 | 4.2398 | 4.2045 | -118.9661 | 0.043282 | 0.16936 | 0.19545 | 0.1789 | -122.886
|  |  |  | 1.4211e-13 | -0.03982 | -0.00070509 | -0.0040921 | -0.012091 | 0.0054634 | -0.0099192 | -0.0050803 | -0.0029805 | 0.015767 | 0.038391 | 0.0094498 | 4.0026 | 4.0901 | 3.874 | 3.9483 | 4.0207 | 4.1345 | 3.7695 | 0.023941 | 0.078197 | -0.056351 | -0.057425 | 0.054914 | 0.090166 | -0.15041 | 3.8519 | -118.7689 | 4.085 | 3.9564 | 0.10447 | -118.6966 | -118.5828 | -0.068015 | -122.7747 | 0.10634 | 0.026046 | 0.094061 | -122.6624 | -122.6271 | 4.0307 | 4.1031 | 4.2169 | 4.1725 | -118.9478 | 0.024972 | 0.13731 | 0.17256 | 0.16059 | -122.8677
|  |  |  | 1.4211e-13 | -0.03982 | -0.00091889 | -0.0038783 | -0.012091 | 0.005677 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.038604 | 0.0098772 | 3.9888 | 4.0809 | 3.8694 | 3.9438 | 4.0115 | 4.1254 | 3.7512 | 0.02852 | 0.073618 | -0.06093 | -0.052847 | 0.064071 | 0.085587 | -0.15499 | 3.829 | -118.7781 | 4.0666 | 3.9472 | 0.11821 | -118.7104 | -118.5965 | -0.077171 | -122.7747 | 0.10634 | 0.01689 | 0.094061 | -122.6578 | -122.6363 | 4.0216 | 4.0893 | 4.2032 | 4.1588 | -118.9707 | 0.024973 | 0.14189 | 0.16341 | 0.15144 | -122.8769
|  |  |  | 1.4211e-13 | -0.03982 | -0.00027769 | -0.0038783 | -0.012305 | 0.005677 | -0.01755 | -0.0044395 | -0.0023397 | 0.015981 | 0.038177 | 0.0090226 | 3.9842 | 4.0809 | 3.8602 | 3.9392 | 4.0069 | 4.1299 | 3.7512 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.064071 | 0.090166 | -0.15041 | 3.8336 | -118.7827 | 4.0666 | 3.9426 | 0.10905 | -118.7149 | -118.5919 | -0.068015 | -122.7839 | 0.10634 | 0.021467 | 0.089482 | -122.6578 | -122.6317 | 4.0216 | 4.0893 | 4.2123 | 4.1633 | -118.9707 | 0.020393 | 0.14647 | 0.17256 | 0.16059 | -122.8723
|  |  |  | 1.4211e-13 | -0.040034 | -0.00027769 | -0.0038783 | -0.012305 | 0.0054634 | -0.01755 | -0.0048667 | -0.0025533 | 0.015767 | 0.038391 | 0.0092362 | 3.9842 | 4.0764 | 3.8648 | 3.9392 | 4.0115 | 4.1299 | 3.7512 | 0.023941 | 0.082776 | -0.065509 | -0.048268 | 0.054914 | 0.094744 | -0.15041 | 3.8656 | -118.8056 | 4.0987 | 3.9793 | 0.11363 | -118.7333 | -118.6148 | -0.035971 | -122.793 | 0.13838 | 0.048932 | 0.084903 | -122.6898 | -122.65 | 4.0536 | 4.1259 | 4.2444 | 4.1908 | -118.9936 | 0.066173 | 0.16936 | 0.20919 | 0.19722 | -122.8952
|  |  |  | 1.4211e-13 | -0.040247 | -6.4092e-05 | -0.0040921 | -0.012091 | 0.005677 | -0.02518 | -0.0050803 | -0.0027669 | 0.015981 | 0.038604 | 0.0094498 | 3.9797 | 4.0809 | 3.8511 | 3.9254 | 4.0069 | 4.1162 | 3.7466 | 0.02852 | 0.082776 | -0.065509 | -0.066582 | 0.064071 | 0.090166 | -0.15041 | 3.8565 | -118.8376 | 4.0895 | 3.9609 | 0.10447 | -118.7561 | -118.6469 | -0.040549 | -122.8296 | 0.13838 | 0.044354 | 0.084903 | -122.699 | -122.6729 | 4.0353 | 4.1168 | 4.2261 | 4.1908 | -119.0165 | 0.043281 | 0.17393 | 0.20003 | 0.19264 | -122.9135
|  |  |  | 1.4211e-13 | -0.040247 | -0.00070509 | -0.0038783 | -0.012518 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.038604 | 0.0094498 | 3.9751 | 4.0626 | 3.8419 | 3.93 | 4.0023 | 4.1116 | 3.7466 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.085587 | -0.14583 | 3.8519 | -118.7781 | 4.0804 | 3.9472 | 0.095317 | -118.7058 | -118.5965 | -0.040547 | -122.7656 | 0.12923 | 0.039777 | 0.080324 | -122.6486 | -122.6225 | 4.0353 | 4.1076 | 4.2169 | 4.1679 | -118.9615 | 0.047861 | 0.16478 | 0.19087 | 0.18348 | -122.854
|  |  |  | 1.4211e-13 | -0.040034 | -0.00027769 | -0.0036647 | -0.012305 | 0.0058906 | -0.01755 | -0.0050803 | -0.0023397 | 0.015767 | 0.038391 | 0.0098772 | 3.9705 | 4.058 | 3.8328 | 3.9163 | 3.9886 | 4.1025 | 3.7374 | 0.033099 | 0.073618 | -0.06093 | -0.066582 | 0.054914 | 0.090166 | -0.14125 | 3.8519 | -118.8605 | 4.085 | 3.9472 | 0.095318 | -118.7882 | -118.6743 | -0.026814 | -122.8434 | 0.14754 | 0.053511 | 0.080325 | -122.7219 | -122.6866 | 4.0307 | 4.103 | 4.2169 | 4.1725 | -119.0393 | 0.047859 | 0.16936 | 0.20461 | 0.18806 | -122.918
|  |  |  | 1.4211e-13 | -0.040247 | -0.00070509 | -0.0036647 | -0.012305 | 0.0058906 | -0.02518 | -0.0048667 | -0.0025533 | 0.015767 | 0.038604 | 0.0094498 | 3.9659 | 4.0535 | 3.8373 | 3.9209 | 3.984 | 4.0979 | 3.7283 | 0.033099 | 0.078197 | -0.06093 | -0.057425 | 0.054914 | 0.085587 | -0.15499 | 3.8244 | -118.8239 | 4.0621 | 3.9335 | 0.10905 | -118.7607 | -118.6469 | -0.058861 | -122.8022 | 0.12923 | 0.0352 | 0.094061 | -122.6898 | -122.6592 | 4.017 | 4.0802 | 4.194 | 4.1496 | -119.0165 | 0.038705 | 0.15104 | 0.18172 | 0.17433 | -122.8997
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0040921 | -0.012305 | 0.005677 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015981 | 0.038391 | 0.0096636 | 3.9522 | 4.0535 | 3.8236 | 3.9026 | 3.984 | 4.0887 | 3.7191 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.054914 | 0.090166 | -0.15041 | 3.8336 | -118.8834 | 4.0666 | 3.9381 | 0.10448 | -118.8019 | -118.6972 | -0.035971 | -122.8434 | 0.14296 | 0.053511 | 0.089482 | -122.731 | -122.6958 | 4.017 | 4.0985 | 4.2032 | 4.1679 | -119.0668 | 0.057016 | 0.16936 | 0.20461 | 0.19722 | -122.9364
|  |  |  | 1.4211e-13 | -0.040034 | -0.00049149 | -0.0043057 | -0.012091 | 0.0054634 | -0.0022892 | -0.0048667 | -0.0023397 | 0.015767 | 0.038391 | 0.0096636 | 3.9568 | 4.0443 | 3.8236 | 3.9026 | 3.9794 | 4.0887 | 3.7146 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.090166 | -0.15041 | 3.8336 | -118.8285 | 4.0758 | 3.9426 | 0.10906 | -118.7516 | -118.6423 | -0.031393 | -122.7884 | 0.14754 | 0.05351 | 0.084903 | -122.6761 | -122.6409 | 4.0216 | 4.0985 | 4.2077 | 4.1633 | -119.0165 | 0.061594 | 0.17393 | 0.20919 | 0.2018 | -122.8814
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0038783 | -0.012091 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015554 | 0.038604 | 0.0096636 | 3.9476 | 4.0306 | 3.8099 | 3.8888 | 3.9703 | 4.075 | 3.7054 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.054914 | 0.094744 | -0.15041 | 3.7832 | -118.8468 | 4.0254 | 3.8877 | 0.10448 | -118.7653 | -118.6606 | -0.072592 | -122.8022 | 0.10176 | 0.01689 | 0.089482 | -122.6807 | -122.6409 | 3.9666 | 4.0481 | 4.1528 | 4.1084 | -119.0302 | 0.011238 | 0.13273 | 0.17256 | 0.1606 | -122.886
|  |  |  | 1.4211e-13 | -0.040034 | -0.00049149 | -0.0038783 | -0.011877 | 0.0054634 | -0.02518 | -0.0048667 | -0.0025533 | 0.015767 | 0.038391 | 0.0096636 | 3.9385 | 4.026 | 3.8053 | 3.8888 | 3.9566 | 4.0704 | 3.7054 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.054914 | 0.090166 | -0.15499 | 3.7924 | -118.8697 | 4.0254 | 3.8923 | 0.0999 | -118.8019 | -118.6881 | -0.068016 | -122.8159 | 0.11092 | 0.016888 | 0.084904 | -122.7036 | -122.6683 | 3.9758 | 4.0435 | 4.1574 | 4.113 | -119.0531 | 0.02955 | 0.14189 | 0.17714 | 0.16975 | -122.9135
|  |  |  | 1.4211e-13 | -0.040034 | -6.4092e-05 | -0.0038783 | -0.011877 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0025533 | 0.016195 | 0.038391 | 0.0090226 | 3.9293 | 4.026 | 3.8007 | 3.8888 | 3.9611 | 4.0613 | 3.6962 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.050335 | 0.094744 | -0.14583 | 3.8015 | -118.8468 | 4.0346 | 3.906 | 0.10448 | -118.7745 | -118.6743 | -0.040547 | -122.793 | 0.12923 | 0.039777 | 0.080324 | -122.6853 | -122.6409 | 3.9941 | 4.0664 | 4.1665 | 4.1313 | -119.0394 | 0.047861 | 0.15562 | 0.20003 | 0.18806 | -122.8814
|  |  |  | 1.4211e-13 | -0.03982 | -0.00027769 | -0.0034509 | -0.012091 | 0.0054634 | -0.01755 | -0.0044395 | -0.0027669 | 0.015767 | 0.038604 | 0.0092362 | 3.9247 | 4.0168 | 3.8053 | 3.8751 | 3.9566 | 4.0658 | 3.6917 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.050335 | 0.090166 | -0.14583 | 3.7741 | -118.8605 | 4.0071 | 3.8877 | 0.11364 | -118.779 | -118.6698 | -0.063436 | -122.793 | 0.11092 | 0.016888 | 0.080324 | -122.6853 | -122.6454 | 3.9575 | 4.0389 | 4.1482 | 4.0992 | -119.0439 | 0.024972 | 0.13273 | 0.17256 | 0.16059 | -122.8814
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0038783 | -0.011877 | 0.0058906 | 0.0053413 | -0.0046531 | -0.0025533 | 0.015767 | 0.038391 | 0.0094498 | 3.9247 | 4.0123 | 3.787 | 3.8705 | 3.952 | 4.0567 | 3.6825 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.090166 | -0.15041 | 3.7603 | -118.8514 | 4.0025 | 3.8648 | 0.10448 | -118.7699 | -118.6652 | -0.072592 | -122.7839 | 0.10176 | 0.01689 | 0.089482 | -122.6669 | -122.6317 | 3.9483 | 4.0298 | 4.1345 | 4.0901 | -119.0394 | 0.015816 | 0.13273 | 0.16799 | 0.1606 | -122.8723
|  |  |  | 1.4211e-13 | -0.03982 | -0.00027769 | -0.0038783 | -0.012305 | 0.0058906 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015767 | 0.038604 | 0.0094498 | 3.9201 | 4.0077 | 3.7824 | 3.8613 | 3.9474 | 4.0567 | 3.6871 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.050335 | 0.090166 | -0.15041 | 3.8061 | -118.8834 | 4.0392 | 3.9014 | 0.095325 | -118.7974 | -118.6881 | -0.031393 | -122.8022 | 0.14754 | 0.05351 | 0.084903 | -122.6944 | -122.6546 | 3.9804 | 4.0664 | 4.1757 | 4.1267 | -119.0577 | 0.061594 | 0.16935 | 0.20919 | 0.19722 | -122.8952
|  |  |  | 1.4211e-13 | -0.040034 | -0.00049149 | -0.0038783 | -0.012091 | 0.0054634 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.038604 | 0.0096636 | 3.9156 | 4.0077 | 3.7778 | 3.8659 | 3.9382 | 4.0475 | 3.6779 | 0.023941 | 0.078197 | -0.06093 | -0.052847 | 0.054914 | 0.085587 | -0.15499 | 3.742 | -118.8651 | 3.9797 | 3.8419 | 0.099905 | -118.7928 | -118.6835 | -0.090904 | -122.7839 | 0.088028 | 0.003157 | 0.094061 | -122.6761 | -122.6454 | 3.93 | 4.0023 | 4.1116 | 4.0718 | -119.0531 | 0.01124 | 0.119 | 0.14967 | 0.14228 | -122.886
|  |  |  | 1.4211e-13 | -0.040034 | -0.00049149 | -0.0036647 | -0.012091 | 0.0058906 | -0.01755 | -0.0048667 | -0.0029805 | 0.015981 | 0.038604 | 0.0098772 | 3.9064 | 3.9985 | 3.7732 | 3.8522 | 3.9291 | 4.0429 | 3.6825 | 0.023941 | 0.078197 | -0.070087 | -0.057425 | 0.050335 | 0.099323 | -0.15041 | 3.7969 | -118.9109 | 4.0209 | 3.8877 | 0.090747 | -118.834 | -118.7201 | -0.035971 | -122.8205 | 0.13838 | 0.044354 | 0.080325 | -122.7127 | -122.6637 | 3.9666 | 4.0435 | 4.1574 | 4.113 | -119.0806 | 0.057016 | 0.16478 | 0.21376 | 0.19264 | -122.9135
|  |  |  | 1.4211e-13 | -0.03982 | -0.00070509 | -0.0038783 | -0.011877 | 0.005677 | -0.0099192 | -0.0046531 | -0.0023397 | 0.015767 | 0.038604 | 0.0094498 | 3.8973 | 3.9939 | 3.7687 | 3.8522 | 3.9291 | 4.0384 | 3.6779 | 0.019362 | 0.073618 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.14583 | 3.7741 | -118.8926 | 3.9934 | 3.8648 | 0.090748 | -118.8157 | -118.7064 | -0.049703 | -122.8068 | 0.11549 | 0.030621 | 0.080324 | -122.6898 | -122.6546 | 3.9483 | 4.0252 | 4.1345 | 4.0901 | -119.0668 | 0.034126 | 0.15104 | 0.1863 | 0.16975 | -122.8906
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0038783 | -0.011877 | 0.0054634 | -0.02518 | -0.0050803 | -0.0025533 | 0.015767 | 0.038818 | 0.0090226 | 3.8927 | 3.9894 | 3.7641 | 3.8476 | 3.9245 | 4.0292 | 3.6642 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 3.7374 | -118.8468 | 3.9659 | 3.8373 | 0.099907 | -118.7699 | -118.6652 | -0.07717 | -122.7518 | 0.10176 | 0.007733 | 0.084903 | -122.6395 | -122.6088 | 3.9209 | 3.9977 | 4.1024 | 4.0626 | -119.0302 | 0.015817 | 0.12816 | 0.15883 | 0.15602 | -122.8448
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0038783 | -0.012091 | 0.005677 | -0.0022892 | -0.0050803 | -0.0027669 | 0.015767 | 0.038177 | 0.0092362 | 3.8927 | 3.9802 | 3.7549 | 3.8385 | 3.9153 | 4.0155 | 3.6642 | 0.019362 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.094744 | -0.15499 | 3.7832 | -118.9109 | 4.0117 | 3.874 | 0.09075 | -118.834 | -118.7339 | -0.035972 | -122.8113 | 0.13838 | 0.05351 | 0.089482 | -122.6853 | -122.6546 | 3.9575 | 4.0344 | 4.1345 | 4.0992 | -119.0851 | 0.057015 | 0.18309 | 0.21376 | 0.19722 | -122.9043
|  |  |  | 1.4211e-13 | -0.040461 | -6.4092e-05 | -0.0038783 | -0.011664 | 0.005677 | -0.0099192 | -0.0044395 | -0.0025533 | 0.01534 | 0.038391 | 0.0094498 | 3.8881 | 3.9802 | 3.7504 | 3.8339 | 3.9108 | 4.02 | 3.6367 | 0.033099 | 0.073618 | -0.06093 | -0.052847 | 0.059493 | 0.085587 | -0.15041 | 3.7145 | -118.8605 | 3.9659 | 3.8282 | 0.11364 | -118.7836 | -118.6744 | -0.072592 | -122.7472 | 0.11092 | 0.01689 | 0.089482 | -122.6349 | -122.6088 | 3.9117 | 3.9886 | 4.0979 | 4.058 | -119.0577 | 0.024973 | 0.13731 | 0.16341 | 0.15144 | -122.8448
|  |  |  | 1.4211e-13 | -0.03982 | -0.00027769 | -0.0038783 | -0.012091 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.038818 | 0.0092362 | 3.8789 | 3.9756 | 3.7504 | 3.8247 | 3.9016 | 4.0063 | 3.6459 | 0.023941 | 0.073618 | -0.06093 | -0.057425 | 0.059493 | 0.085587 | -0.15041 | 3.742 | -118.9292 | 3.9751 | 3.8465 | 0.10449 | -118.8523 | -118.7476 | -0.054282 | -122.8113 | 0.12007 | 0.0352 | 0.089482 | -122.6944 | -122.6683 | 3.9208 | 3.9977 | 4.1024 | 4.0718 | -119.108 | 0.038705 | 0.15562 | 0.18172 | 0.16975 | -122.9043
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0036647 | -0.012091 | 0.005677 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.038604 | 0.0094498 | 3.8744 | 3.9619 | 3.732 | 3.8201 | 3.9016 | 3.9971 | 3.6367 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.059493 | 0.085587 | -0.14583 | 3.7054 | -118.9155 | 3.943 | 3.8007 | 0.095332 | -118.834 | -118.7384 | -0.077168 | -122.7976 | 0.092606 | 0.007735 | 0.084903 | -122.6761 | -122.65 | 3.8888 | 3.9703 | 4.0658 | 4.0306 | -119.0989 | 0.006661 | 0.12816 | 0.15425 | 0.15144 | -122.8814
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0038783 | -0.012091 | 0.0054634 | -0.0022892 | -0.0044395 | -0.0025533 | 0.015767 | 0.039032 | 0.0092362 | 3.8652 | 3.9482 | 3.7275 | 3.8156 | 3.897 | 3.9971 | 3.6321 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.050335 | 0.090166 | -0.15499 | 3.6825 | -118.9155 | 3.9156 | 3.7778 | 0.095333 | -118.834 | -118.7339 | -0.10464 | -122.793 | 0.074295 | -0.010576 | 0.094061 | -122.6807 | -122.6409 | 3.8659 | 3.9474 | 4.0475 | 3.9985 | -119.0989 | -0.01165 | 0.10069 | 0.14052 | 0.13313 | -122.886
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0036647 | -0.012518 | 0.0054634 | -0.02518 | -0.0046531 | -0.0025533 | 0.015767 | 0.038391 | 0.0092362 | 3.8606 | 3.9436 | 3.7275 | 3.8018 | 3.8879 | 3.9926 | 3.6276 | 0.023941 | 0.078197 | -0.065509 | -0.052847 | 0.054914 | 0.094744 | -0.15041 | 3.6962 | -118.9612 | 3.9293 | 3.7961 | 0.099912 | -118.8752 | -118.7705 | -0.081747 | -122.8159 | 0.092606 | 0.003156 | 0.084903 | -122.7081 | -122.6683 | 3.8705 | 3.9565 | 4.0612 | 4.0122 | -119.1355 | 0.015818 | 0.12358 | 0.16341 | 0.14686 | -122.9135
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0038783 | -0.012091 | 0.0052496 | -0.0099192 | -0.0046531 | -0.0023397 | 0.015554 | 0.038391 | 0.0092362 | 3.8606 | 3.9482 | 3.7183 | 3.8018 | 3.8833 | 3.988 | 3.623 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.050335 | 0.085587 | -0.15041 | 3.742 | -118.9658 | 3.9796 | 3.8373 | 0.095334 | -118.8844 | -118.7796 | -0.031393 | -122.8251 | 0.14754 | 0.05351 | 0.084903 | -122.7173 | -122.6821 | 3.9208 | 4.0023 | 4.107 | 4.0672 | -119.1447 | 0.061594 | 0.16935 | 0.20461 | 0.19722 | -122.9181
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0038783 | -0.012305 | 0.005677 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015981 | 0.038818 | 0.0094498 | 3.8469 | 3.9344 | 3.7183 | 3.8018 | 3.8695 | 3.9834 | 3.6092 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.054914 | 0.094744 | -0.15499 | 3.6642 | -118.9383 | 3.9018 | 3.7732 | 0.10907 | -118.8706 | -118.7568 | -0.10006 | -122.7976 | 0.078873 | -0.005998 | 0.094061 | -122.6853 | -122.6454 | 3.8568 | 3.9245 | 4.0383 | 3.9894 | -119.1309 | -0.002493 | 0.10985 | 0.14968 | 0.13313 | -122.8952
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0036647 | -0.012091 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0029805 | 0.015767 | 0.038818 | 0.0090226 | 3.8377 | 3.939 | 3.7092 | 3.7927 | 3.8741 | 3.9788 | 3.6138 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.064071 | 0.085587 | -0.15499 | 3.6642 | -118.9429 | 3.8881 | 3.7595 | 0.095335 | -118.8615 | -118.7568 | -0.10464 | -122.793 | 0.074295 | -0.019733 | 0.084904 | -122.6715 | -122.65 | 3.843 | 3.9245 | 4.0292 | 3.9894 | -119.1218 | -0.007071 | 0.11442 | 0.13594 | 0.13313 | -122.8906
|  |  |  | 1.4211e-13 | -0.040247 | -0.00049149 | -0.0040921 | -0.012091 | 0.0054634 | -0.01755 | -0.0046531 | -0.0023397 | 0.015981 | 0.038818 | 0.0092362 | 3.8377 | 3.9298 | 3.7092 | 3.7927 | 3.865 | 3.9743 | 3.6047 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 3.7008 | -118.975 | 3.9339 | 3.8053 | 0.10449 | -118.9027 | -118.7934 | -0.054282 | -122.8251 | 0.12007 | 0.030621 | 0.084903 | -122.7081 | -122.6775 | 3.8888 | 3.9611 | 4.0704 | 4.026 | -119.163 | 0.038705 | 0.15562 | 0.1863 | 0.17433 | -122.9181
|  |  |  | 1.4211e-13 | -0.040034 | -0.00049149 | -0.0036647 | -0.012732 | 0.0052496 | -0.01755 | -0.0044395 | -0.0029805 | 0.015767 | 0.038818 | 0.0090226 | 3.8332 | 3.9207 | 3.6954 | 3.7835 | 3.8604 | 3.9743 | 3.6001 | 0.023941 | 0.078197 | -0.070087 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 3.6825 | -118.9383 | 3.9156 | 3.7778 | 0.095338 | -118.8615 | -118.7476 | -0.068015 | -122.7793 | 0.10634 | 0.01231 | 0.080325 | -122.6624 | -122.6317 | 3.8659 | 3.9428 | 4.0567 | 4.0031 | -119.1218 | 0.024972 | 0.14189 | 0.17256 | 0.16059 | -122.8723
|  |  |  | 1.4211e-13 | -0.040461 | -0.00027769 | -0.0038783 | -0.011877 | 0.005036 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015767 | 0.038604 | 0.0092362 | 3.8286 | 3.9207 | 3.6954 | 3.7698 | 3.8604 | 3.9651 | 3.5909 | 0.023941 | 0.087354 | -0.070087 | -0.066582 | 0.054914 | 0.090166 | -0.14583 | 3.6962 | -119.0299 | 3.9339 | 3.8007 | 0.1045 | -118.9393 | -118.8346 | -0.040547 | -122.8663 | 0.12923 | 0.035199 | 0.075746 | -122.7448 | -122.7095 | 3.8751 | 3.9657 | 4.0704 | 4.026 | -119.2088 | 0.038704 | 0.1602 | 0.19545 | 0.19264 | -122.9455
|  |  |  | 1.4211e-13 | -0.040461 | -0.00027769 | -0.0040921 | -0.012305 | 0.005677 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.038604 | 0.0090226 | 3.8194 | 3.9115 | 3.6908 | 3.7652 | 3.8421 | 3.9514 | 3.5909 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.050335 | 0.090166 | -0.15041 | 3.7099 | -118.9704 | 3.9384 | 3.8099 | 0.099917 | -118.8935 | -118.7842 | -0.031393 | -122.7976 | 0.14296 | 0.05351 | 0.084903 | -122.6853 | -122.6454 | 3.8842 | 3.9611 | 4.0704 | 4.0306 | -119.1447 | 0.057015 | 0.16935 | 0.20919 | 0.19722 | -122.886
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0038783 | -0.012091 | 0.0058906 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015981 | 0.038818 | 0.0094498 | 3.8148 | 3.907 | 3.6817 | 3.7698 | 3.8375 | 3.9422 | 3.5818 | 0.019362 | 0.073618 | -0.06093 | -0.048268 | 0.054914 | 0.085587 | -0.15041 | 3.6642 | -118.9658 | 3.8972 | 3.7641 | 0.099918 | -118.8981 | -118.7934 | -0.068015 | -122.7839 | 0.10176 | 0.021467 | 0.089482 | -122.6807 | -122.65 | 3.8522 | 3.9199 | 4.0246 | 3.9894 | -119.1538 | 0.034129 | 0.13731 | 0.16798 | 0.15602 | -122.886
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0040921 | -0.012091 | 0.0054634 | -0.0022892 | -0.0046531 | -0.0023397 | 0.015554 | 0.038604 | 0.0094498 | 3.8057 | 3.9024 | 3.6771 | 3.7652 | 3.8375 | 3.9422 | 3.5772 | 0.033099 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15499 | 3.6413 | -118.9521 | 3.8698 | 3.7412 | 0.099918 | -118.8798 | -118.7751 | -0.090904 | -122.7747 | 0.097186 | -0.001422 | 0.089482 | -122.6578 | -122.6225 | 3.8293 | 3.9016 | 4.0063 | 3.9665 | -119.1401 | 0.006662 | 0.12358 | 0.15883 | 0.14228 | -122.8723
|  |  |  | 1.4211e-13 | -0.040461 | -0.00027769 | -0.0036647 | -0.011877 | 0.005677 | -0.0022892 | -0.0050803 | -0.0025533 | 0.015981 | 0.039032 | 0.0092362 | 3.8057 | 3.8932 | 3.6634 | 3.7515 | 3.8283 | 3.9376 | 3.568 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.054914 | 0.094744 | -0.15041 | 3.655 | -118.9979 | 3.8927 | 3.7503 | 0.095342 | -118.921 | -118.8117 | -0.063437 | -122.8113 | 0.11092 | 0.026045 | 0.089482 | -122.6944 | -122.6546 | 3.8384 | 3.9153 | 4.0246 | 3.9802 | -119.1813 | 0.024971 | 0.14189 | 0.18172 | 0.16517 | -122.8997
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0036647 | -0.012091 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015554 | 0.038391 | 0.0090226 | 3.792 | 3.8932 | 3.6588 | 3.7469 | 3.8283 | 3.9285 | 3.568 | 0.033099 | 0.078197 | -0.06093 | -0.062004 | 0.064071 | 0.085587 | -0.15041 | 3.6687 | -118.975 | 3.8927 | 3.7595 | 0.090763 | -118.8935 | -118.7934 | -0.049704 | -122.7839 | 0.13381 | 0.039778 | 0.089482 | -122.6578 | -122.6363 | 3.8476 | 3.929 | 4.0292 | 3.9939 | -119.1538 | 0.038704 | 0.16478 | 0.18629 | 0.17891 | -122.8723
|  |  |  | 1.4211e-13 | -0.040461 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.0054634 | -0.01755 | -0.0048667 | -0.0027669 | 0.015554 | 0.038391 | 0.0094498 | 3.7874 | 3.8886 | 3.6634 | 3.7423 | 3.8283 | 3.9285 | 3.5589 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15957 | 3.6458 | -118.9979 | 3.8743 | 3.7503 | 0.1045 | -118.9118 | -118.8117 | -0.072595 | -122.7976 | 0.11092 | 0.021466 | 0.094061 | -122.6807 | -122.6454 | 3.8293 | 3.9153 | 4.0154 | 3.9756 | -119.1813 | 0.02955 | 0.14647 | 0.18172 | 0.16517 | -122.8997
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0036647 | -0.012305 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0023397 | 0.015767 | 0.038604 | 0.0090226 | 3.7874 | 3.8932 | 3.6588 | 3.7377 | 3.8146 | 3.9239 | 3.5543 | 0.02852 | 0.078197 | -0.06093 | -0.052847 | 0.054914 | 0.094744 | -0.15957 | 3.6687 | -119.0253 | 3.9018 | 3.7732 | 0.1045 | -118.9485 | -118.8392 | -0.045129 | -122.8159 | 0.14296 | 0.053511 | 0.09864 | -122.7081 | -122.6683 | 3.8522 | 3.929 | 4.0383 | 4.0077 | -119.2088 | 0.061594 | 0.16936 | 0.20919 | 0.19264 | -122.9226
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0040921 | -0.012305 | 0.0054634 | -0.01755 | -0.0048667 | -0.0027669 | 0.015767 | 0.038818 | 0.0090226 | 3.7874 | 3.8886 | 3.6496 | 3.7423 | 3.8238 | 3.9102 | 3.5543 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.090166 | -0.15499 | 3.6458 | -119.0162 | 3.8789 | 3.7412 | 0.095344 | -118.9347 | -118.8483 | -0.063438 | -122.8159 | 0.11549 | 0.026044 | 0.089482 | -122.699 | -122.6683 | 3.8339 | 3.9153 | 4.0017 | 3.9802 | -119.2042 | 0.034128 | 0.15105 | 0.18172 | 0.16975 | -122.9135
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0036647 | -0.012305 | 0.0054634 | -0.0099192 | -0.0048667 | -0.0029805 | 0.015767 | 0.038604 | 0.0092362 | 3.7782 | 3.8703 | 3.6405 | 3.724 | 3.8054 | 3.9102 | 3.5497 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.054914 | 0.090166 | -0.15957 | 3.6596 | -119.0345 | 3.8881 | 3.7503 | 0.090766 | -118.953 | -118.8483 | -0.049707 | -122.8205 | 0.1338 | 0.044354 | 0.094061 | -122.7036 | -122.6683 | 3.8339 | 3.9153 | 4.02 | 3.9802 | -119.2088 | 0.047859 | 0.16478 | 0.20003 | 0.18806 | -122.9181
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0038783 | -0.011877 | 0.0052496 | -0.02518 | -0.0046531 | -0.0027669 | 0.015767 | 0.038818 | 0.0094498 | 3.7645 | 3.8703 | 3.6359 | 3.724 | 3.8054 | 3.9147 | 3.5406 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.054914 | 0.094744 | -0.15499 | 3.6596 | -119.0299 | 3.8835 | 3.7549 | 0.095346 | -118.9485 | -118.8392 | -0.035972 | -122.8205 | 0.13838 | 0.05351 | 0.089482 | -122.699 | -122.6592 | 3.843 | 3.9245 | 4.0338 | 3.9893 | -119.2134 | 0.052437 | 0.17393 | 0.21376 | 0.20637 | -122.9089
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0038783 | -0.012305 | 0.0052496 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015554 | 0.038818 | 0.0094498 | 3.7736 | 3.8657 | 3.6313 | 3.7194 | 3.7917 | 3.8964 | 3.5314 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.050335 | 0.085587 | -0.15041 | 3.5955 | -119.0162 | 3.8377 | 3.6954 | 0.099926 | -118.9439 | -118.8392 | -0.086325 | -122.7976 | 0.088028 | -0.001422 | 0.084903 | -122.6853 | -122.65 | 3.7835 | 3.8558 | 3.9605 | 3.9298 | -119.2042 | 0.002083 | 0.11442 | 0.14967 | 0.14686 | -122.886
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0038783 | -0.012305 | 0.0052496 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.038604 | 0.0090226 | 3.7599 | 3.8566 | 3.6267 | 3.7103 | 3.7917 | 3.8918 | 3.5314 | 0.033099 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.085587 | -0.15499 | 3.6138 | -119.0162 | 3.8423 | 3.7091 | 0.095347 | -118.9347 | -118.8346 | -0.072594 | -122.7839 | 0.1155 | 0.016888 | 0.089482 | -122.6715 | -122.6409 | 3.7927 | 3.8741 | 3.9742 | 3.939 | -119.195 | 0.024972 | 0.13731 | 0.16798 | 0.16517 | -122.8814
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0040921 | -0.012305 | 0.0054634 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015767 | 0.038604 | 0.0092362 | 3.7507 | 3.8566 | 3.613 | 3.7103 | 3.7826 | 3.8918 | 3.5222 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 3.6138 | -119.0253 | 3.8423 | 3.7046 | 0.09077 | -118.953 | -118.8438 | -0.063438 | -122.7976 | 0.11549 | 0.030623 | 0.094061 | -122.6761 | -122.6454 | 3.8018 | 3.8741 | 3.9834 | 3.9481 | -119.2134 | 0.029549 | 0.15105 | 0.18172 | 0.16975 | -122.8906
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0038783 | -0.011877 | 0.0048224 | -0.01755 | -0.0048667 | -0.0023397 | 0.015767 | 0.038818 | 0.0094498 | 3.7507 | 3.8429 | 3.6222 | 3.6919 | 3.778 | 3.8781 | 3.5222 | 0.033099 | 0.078197 | -0.065509 | -0.066582 | 0.064071 | 0.094744 | -0.15041 | 3.6367 | -119.094 | 3.8652 | 3.7366 | 0.099926 | -119.008 | -118.9078 | -0.035971 | -122.8525 | 0.14754 | 0.048932 | 0.084903 | -122.7219 | -122.6912 | 3.8064 | 3.8924 | 3.9925 | 3.9573 | -119.2637 | 0.047859 | 0.17851 | 0.20919 | 0.19264 | -122.9364
|  |  |  | 1.4211e-13 | -0.040675 | -0.00070509 | -0.0038783 | -0.012518 | 0.0052496 | -0.02518 | -0.0048667 | -0.0027669 | 0.015767 | 0.038604 | 0.0096636 | 3.7462 | 3.8337 | 3.613 | 3.6919 | 3.7734 | 3.8873 | 3.5131 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.064071 | 0.094744 | -0.15041 | 3.5909 | -119.0803 | 3.824 | 3.6908 | 0.099928 | -118.9988 | -118.885 | -0.072592 | -122.8342 | 0.10176 | 0.01689 | 0.089482 | -122.7081 | -122.6775 | 3.7698 | 3.8512 | 3.9651 | 3.9115 | -119.2591 | 0.015816 | 0.14189 | 0.17256 | 0.1606 | -122.9226
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0040921 | -0.012091 | 0.005036 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015554 | 0.038604 | 0.0094498 | 3.737 | 3.8337 | 3.6084 | 3.6965 | 3.7688 | 3.8827 | 3.5085 | 0.023941 | 0.078197 | -0.065509 | -0.066582 | 0.059493 | 0.085587 | -0.15499 | 3.5909 | -119.0162 | 3.8194 | 3.6908 | 0.099928 | -118.9439 | -118.83 | -0.072594 | -122.7793 | 0.10634 | 0.016888 | 0.089482 | -122.6532 | -122.6271 | 3.7789 | 3.8512 | 3.9651 | 3.9161 | -119.2042 | 0.015815 | 0.14189 | 0.16798 | 0.16059 | -122.8677
|  |  |  | 1.4211e-13 | -0.040461 | -6.4092e-05 | -0.0040921 | -0.012305 | 0.0048224 | -0.01755 | -0.0048667 | -0.0025533 | 0.015554 | 0.038818 | 0.0092362 | 3.737 | 3.8383 | 3.6039 | 3.6828 | 3.7597 | 3.8735 | 3.5085 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.064071 | 0.085587 | -0.14583 | 3.6092 | -119.0803 | 3.8377 | 3.7046 | 0.09535 | -119.0034 | -118.8895 | -0.045125 | -122.8251 | 0.12465 | 0.039778 | 0.084903 | -122.699 | -122.6775 | 3.7835 | 3.8604 | 3.9742 | 3.939 | -119.2546 | 0.038704 | 0.16478 | 0.18629 | 0.18348 | -122.9089
|  |  |  | 1.4211e-13 | -0.040675 | -0.00070509 | -0.0040921 | -0.012091 | 0.0046086 | -0.0099192 | -0.0044395 | -0.0023397 | 0.015767 | 0.038604 | 0.008809 | 3.7324 | 3.8291 | 3.5947 | 3.6782 | 3.7551 | 3.8689 | 3.5039 | 0.023941 | 0.078197 | -0.065509 | -0.057425 | 0.06865 | 0.081008 | -0.15041 | 3.6275 | -119.0894 | 3.856 | 3.7183 | 0.090772 | -119.0126 | -118.8987 | -0.026816 | -122.8251 | 0.14754 | 0.058087 | 0.084903 | -122.699 | -122.6866 | 3.8018 | 3.8787 | 3.9925 | 3.9527 | -119.2637 | 0.066171 | 0.19225 | 0.2046 | 0.20179 | -122.9181
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0040921 | -0.012091 | 0.005036 | -0.0099192 | -0.0040121 | -0.0025533 | 0.015981 | 0.038391 | 0.0090226 | 3.7233 | 3.8337 | 3.5855 | 3.6736 | 3.7505 | 3.8644 | 3.4993 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.06865 | 0.090166 | -0.15041 | 3.5772 | -119.0391 | 3.8011 | 3.6634 | 0.086195 | -118.9622 | -118.8483 | -0.072592 | -122.7747 | 0.10176 | 0.012311 | 0.084903 | -122.6441 | -122.6225 | 3.7515 | 3.8283 | 3.9422 | 3.9115 | -119.2134 | 0.015816 | 0.14647 | 0.16799 | 0.15602 | -122.8631
|  |  |  | 1.4211e-13 | -0.040675 | -6.4092e-05 | -0.0040921 | -0.012091 | 0.0046086 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015767 | 0.038818 | 0.0094498 | 3.7141 | 3.8154 | 3.5855 | 3.6691 | 3.7505 | 3.8552 | 3.4902 | 0.02852 | 0.087354 | -0.065509 | -0.057425 | 0.06865 | 0.090166 | -0.15041 | 3.5726 | -119.1169 | 3.7965 | 3.6679 | 0.095353 | -119.0355 | -118.9307 | -0.068015 | -122.8434 | 0.11092 | 0.016888 | 0.084903 | -122.7173 | -122.6958 | 3.7515 | 3.8329 | 3.9376 | 3.8978 | -119.2958 | 0.024972 | 0.15105 | 0.17256 | 0.16975 | -122.9364
|  |  |  | 1.4211e-13 | -0.040247 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.005036 | -0.01755 | -0.0046531 | -0.0027669 | 0.01534 | 0.039032 | 0.0092362 | 3.7141 | 3.8108 | 3.5855 | 3.6599 | 3.7413 | 3.8461 | 3.481 | 0.02852 | 0.087354 | -0.065509 | -0.057425 | 0.064071 | 0.090166 | -0.15041 | 3.5543 | -119.0757 | 3.7874 | 3.6588 | 0.10451 | -118.9943 | -118.8895 | -0.07717 | -122.793 | 0.10176 | 0.007733 | 0.084903 | -122.6715 | -122.6454 | 3.7331 | 3.8146 | 3.9193 | 3.884 | -119.2546 | 0.015817 | 0.13731 | 0.16341 | 0.1606 | -122.886
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0036647 | -0.012305 | 0.0048224 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.038604 | 0.0090226 | 3.705 | 3.8108 | 3.5718 | 3.6599 | 3.7276 | 3.8415 | 3.481 | 0.033099 | 0.082776 | -0.06093 | -0.057425 | 0.064071 | 0.099323 | -0.14583 | 3.5589 | -119.0757 | 3.7828 | 3.6496 | 0.090776 | -119.008 | -118.8941 | -0.068013 | -122.793 | 0.11092 | 0.01689 | 0.084903 | -122.6715 | -122.6363 | 3.7377 | 3.8054 | 3.9193 | 3.8886 | -119.2546 | 0.020395 | 0.14189 | 0.17714 | 0.1606 | -122.8814
|  |  |  | 1.4211e-13 | -0.040461 | -0.00027769 | -0.0038783 | -0.012305 | 0.0046086 | -0.02518 | -0.0048667 | -0.0025533 | 0.015981 | 0.038604 | 0.0092362 | 3.7004 | 3.8016 | 3.5672 | 3.6507 | 3.7184 | 3.8415 | 3.4765 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.090166 | -0.15499 | 3.5863 | -119.1398 | 3.8102 | 3.6771 | 0.090777 | -119.0721 | -118.949 | -0.045128 | -122.8525 | 0.1338 | 0.044354 | 0.089482 | -122.7265 | -122.7004 | 3.7606 | 3.8283 | 3.9513 | 3.9115 | -119.3141 | 0.047859 | 0.17393 | 0.20003 | 0.18806 | -122.9455
|  |  |  | 1.4211e-13 | -0.040247 | -0.00070509 | -0.0038783 | -0.012091 | 0.0046086 | -0.01755 | -0.0048667 | -0.0025533 | 0.015554 | 0.038604 | 0.0094498 | 3.6912 | 3.7971 | 3.5626 | 3.6416 | 3.7276 | 3.8323 | 3.4581 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.06865 | 0.090166 | -0.15499 | 3.5314 | -119.1032 | 3.7645 | 3.6359 | 0.10451 | -119.0171 | -118.9124 | -0.081749 | -122.8022 | 0.097183 | 0.003155 | 0.084904 | -122.6761 | -122.6546 | 3.7148 | 3.8008 | 3.9056 | 3.8703 | -119.2866 | 0.015817 | 0.14189 | 0.16341 | 0.15602 | -122.8997
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0036647 | -0.012305 | 0.0048224 | -0.01755 | -0.0048667 | -0.0025533 | 0.015767 | 0.038604 | 0.0092362 | 3.6821 | 3.7971 | 3.5626 | 3.637 | 3.7184 | 3.8232 | 3.4581 | 0.023941 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.094744 | -0.15041 | 3.5588 | -119.0986 | 3.7828 | 3.6634 | 0.10451 | -119.0172 | -118.9124 | -0.049704 | -122.7976 | 0.12465 | 0.035199 | 0.084903 | -122.6761 | -122.6409 | 3.7377 | 3.8192 | 3.9239 | 3.8978 | -119.2775 | 0.038704 | 0.1602 | 0.19545 | 0.18348 | -122.886
|  |  |  | 1.4211e-13 | -0.040888 | -0.00070509 | -0.0036647 | -0.012091 | 0.0046086 | -0.01755 | -0.0048667 | -0.0021259 | 0.015554 | 0.039032 | 0.0090226 | 3.6867 | 3.7879 | 3.5626 | 3.637 | 3.7093 | 3.8232 | 3.4581 | 0.02852 | 0.082776 | -0.056351 | -0.052847 | 0.064071 | 0.099323 | -0.15041 | 3.568 | -119.1398 | 3.7965 | 3.6725 | 0.10451 | -119.0675 | -118.9536 | -0.040549 | -122.8296 | 0.13838 | 0.053512 | 0.094061 | -122.7127 | -122.6775 | 3.7469 | 3.8192 | 3.933 | 3.8978 | -119.3187 | 0.057016 | 0.17393 | 0.20919 | 0.19264 | -122.9272
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0036647 | -0.012091 | 0.0048224 | -0.0022892 | -0.0050803 | -0.0023397 | 0.015767 | 0.038818 | 0.008809 | 3.6821 | 3.7833 | 3.5398 | 3.6324 | 3.7093 | 3.8186 | 3.4581 | 0.02852 | 0.087354 | -0.065509 | -0.057425 | 0.06865 | 0.094744 | -0.15041 | 3.5314 | -119.1261 | 3.7553 | 3.613 | 0.081622 | -119.0492 | -118.9399 | -0.07717 | -122.8159 | 0.10176 | 0.007733 | 0.084903 | -122.6898 | -122.6637 | 3.7057 | 3.7825 | 3.8918 | 3.8566 | -119.3003 | 0.015817 | 0.14189 | 0.16799 | 0.1606 | -122.9089
|  |  |  | 1.4211e-13 | -0.040675 | -0.00070509 | -0.0040921 | -0.012305 | 0.0048224 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.039032 | 0.0092362 | 3.6775 | 3.7788 | 3.5398 | 3.6233 | 3.7139 | 3.814 | 3.4536 | 0.02852 | 0.078197 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.15041 | 3.5222 | -119.1169 | 3.7462 | 3.6084 | 0.086201 | -119.0263 | -118.9262 | -0.081747 | -122.7976 | 0.097185 | 0.007735 | 0.089482 | -122.6761 | -122.65 | 3.6919 | 3.7825 | 3.8827 | 3.8474 | -119.2866 | 0.01124 | 0.13274 | 0.15883 | 0.14686 | -122.8906
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0038783 | -0.012091 | 0.0046086 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015554 | 0.039032 | 0.008809 | 3.6729 | 3.7742 | 3.5443 | 3.6187 | 3.6956 | 3.8094 | 3.449 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.090166 | -0.15041 | 3.5726 | -119.1398 | 3.7965 | 3.6679 | 0.095358 | -119.0629 | -118.9491 | -0.026816 | -122.8205 | 0.14754 | 0.058087 | 0.084903 | -122.6944 | -122.6683 | 3.7423 | 3.8191 | 3.933 | 3.8978 | -119.3095 | 0.061592 | 0.18767 | 0.21376 | 0.20179 | -122.9089
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0038783 | -0.012518 | 0.0048224 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.039032 | 0.0094498 | 3.6638 | 3.765 | 3.5306 | 3.6187 | 3.691 | 3.8003 | 3.4352 | 0.023941 | 0.082776 | -0.065509 | -0.052847 | 0.054914 | 0.094744 | -0.15041 | 3.5039 | -119.0986 | 3.7324 | 3.5993 | 0.09536 | -119.0263 | -118.917 | -0.081747 | -122.7701 | 0.092606 | 0.003156 | 0.084903 | -122.6624 | -122.6225 | 3.6874 | 3.7596 | 3.8689 | 3.8337 | -119.282 | 0.015818 | 0.12358 | 0.16341 | 0.15144 | -122.8677
|  |  |  | 1.4211e-13 | -0.040461 | -0.00070509 | -0.0036647 | -0.012305 | 0.004395 | -0.01755 | -0.0046531 | -0.0027669 | 0.01534 | 0.039032 | 0.0092362 | 3.6546 | 3.7559 | 3.5214 | 3.6095 | 3.691 | 3.7957 | 3.4307 | 0.023941 | 0.073618 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 3.5359 | -119.181 | 3.7599 | 3.6267 | 0.090783 | -119.0996 | -118.9948 | -0.049705 | -122.8525 | 0.12923 | 0.039777 | 0.089482 | -122.731 | -122.7004 | 3.7148 | 3.7963 | 3.901 | 3.8611 | -119.3599 | 0.043282 | 0.16478 | 0.19545 | 0.1789 | -122.9455
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0040921 | -0.012091 | 0.0046086 | -0.01755 | -0.0048667 | -0.0027669 | 0.015554 | 0.038604 | 0.0092362 | 3.65 | 3.7513 | 3.526 | 3.6095 | 3.6818 | 3.7911 | 3.4169 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.054914 | 0.085587 | -0.15499 | 3.4719 | -119.1078 | 3.705 | 3.581 | 0.1091 | -119.0355 | -118.9262 | -0.10006 | -122.7793 | 0.078873 | -0.005998 | 0.094061 | -122.6624 | -122.6317 | 3.6645 | 3.7367 | 3.846 | 3.8062 | -119.3004 | -0.007072 | 0.10985 | 0.14052 | 0.13771 | -122.8723
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0038783 | -0.012732 | 0.004395 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015554 | 0.039032 | 0.0090226 | 3.65 | 3.7559 | 3.5214 | 3.5958 | 3.6772 | 3.7865 | 3.4123 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15957 | 3.5268 | -119.1856 | 3.7645 | 3.6359 | 0.1091 | -119.1041 | -118.9948 | -0.045129 | -122.8388 | 0.14296 | 0.048932 | 0.094061 | -122.7219 | -122.6866 | 3.7102 | 3.7917 | 3.901 | 3.8703 | -119.369 | 0.057016 | 0.17393 | 0.20919 | 0.19264 | -122.9409
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0043057 | -0.012091 | 0.0046086 | -0.01755 | -0.0048667 | -0.0023397 | 0.015554 | 0.038818 | 0.0090226 | 3.6363 | 3.7467 | 3.5077 | 3.5912 | 3.6635 | 3.7774 | 3.4123 | 0.019362 | 0.078197 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.15499 | 3.4902 | -119.181 | 3.7141 | 3.5855 | 0.095364 | -119.1087 | -118.9948 | -0.077171 | -122.8296 | 0.097182 | 0.01689 | 0.094061 | -122.7081 | -122.6821 | 3.669 | 3.7413 | 3.8552 | 3.8245 | -119.3599 | 0.020395 | 0.14189 | 0.16799 | 0.15602 | -122.9272
|  |  |  | 1.4211e-13 | -0.040247 | -0.00027769 | -0.0038783 | -0.012091 | 0.0048224 | -0.02518 | -0.0048667 | -0.0027669 | 0.016195 | 0.038818 | 0.0092362 | 3.6271 | 3.7375 | 3.5031 | 3.5866 | 3.6589 | 3.7728 | 3.4078 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.06865 | 0.085587 | -0.15499 | 3.5359 | -119.2222 | 3.7553 | 3.6313 | 0.095364 | -119.1499 | -119.036 | -0.026817 | -122.8663 | 0.15669 | 0.067244 | 0.094061 | -122.7402 | -122.7233 | 3.7148 | 3.7871 | 3.901 | 3.8657 | -119.4011 | 0.070749 | 0.19682 | 0.21376 | 0.21095 | -122.9638
|  |  |  | 1.4211e-13 | -0.040675 | -6.4092e-05 | -0.0040921 | -0.012518 | 0.0046086 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.039245 | 0.0094498 | 3.6317 | 3.7421 | 3.5077 | 3.5866 | 3.6498 | 3.7682 | 3.4032 | 0.023941 | 0.087354 | -0.056351 | -0.057425 | 0.064071 | 0.094744 | -0.15499 | 3.5268 | -119.1993 | 3.7553 | 3.6313 | 0.10452 | -119.1362 | -119.0177 | -0.031395 | -122.8434 | 0.14754 | 0.067245 | 0.09864 | -122.7219 | -122.6912 | 3.7102 | 3.7734 | 3.8918 | 3.8657 | -119.3828 | 0.066171 | 0.18767 | 0.21834 | 0.21095 | -122.9409
|  |  |  | 1.4211e-13 | -0.040461 | -0.00049149 | -0.0038783 | -0.012518 | 0.0046086 | -0.0022892 | -0.0048667 | -0.0027669 | 0.015767 | 0.038818 | 0.0090226 | 3.6226 | 3.7284 | 3.4986 | 3.5775 | 3.6498 | 3.7682 | 3.3986 | 0.019362 | 0.082776 | -0.065509 | -0.052847 | 0.06865 | 0.094744 | -0.15499 | 3.4673 | -119.1673 | 3.6912 | 3.5672 | 0.099944 | -119.095 | -118.9765 | -0.086326 | -122.7976 | 0.088027 | 0.003156 | 0.089482 | -122.6761 | -122.65 | 3.6462 | 3.7184 | 3.8369 | 3.7971 | -119.3461 | 0.015818 | 0.13732 | 0.16341 | 0.15144 | -122.8997
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0038783 | -0.012091 | 0.0046086 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015767 | 0.038604 | 0.0090226 | 3.618 | 3.7238 | 3.4848 | 3.5729 | 3.6452 | 3.7545 | 3.3895 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.064071 | 0.094744 | -0.15041 | 3.4856 | -119.1902 | 3.7141 | 3.5809 | 0.095367 | -119.1179 | -119.0086 | -0.054282 | -122.8205 | 0.12007 | 0.026043 | 0.080325 | -122.699 | -122.6683 | 3.669 | 3.7413 | 3.8506 | 3.8199 | -119.3736 | 0.038705 | 0.1602 | 0.19087 | 0.17891 | -122.9135
|  |  |  | 1.4211e-13 | -0.041102 | -0.00070509 | -0.0038783 | -0.012305 | 0.0048224 | -0.01755 | -0.0048667 | -0.0023397 | 0.015767 | 0.038818 | 0.0090226 | 3.6088 | 3.7147 | 3.4848 | 3.5638 | 3.636 | 3.7499 | 3.3757 | 0.014784 | 0.078197 | -0.070087 | -0.062004 | 0.064071 | 0.094744 | -0.14583 | 3.4398 | -119.1673 | 3.6729 | 3.5489 | 0.1091 | -119.095 | -118.9811 | -0.081746 | -122.793 | 0.078871 | -0.006 | 0.075746 | -122.6669 | -122.6363 | 3.6278 | 3.7001 | 3.814 | 3.7787 | -119.3553 | 0.002083 | 0.12816 | 0.15883 | 0.14228 | -122.8769
|  |  |  | 1.4211e-13 | -0.040888 | -0.00049149 | -0.0038783 | -0.012091 | 0.004395 | -0.01755 | -0.0050803 | -0.0023397 | 0.015767 | 0.038818 | 0.008809 | 3.6042 | 3.7147 | 3.4848 | 3.5592 | 3.636 | 3.7545 | 3.3757 | 0.02852 | 0.078197 | -0.06093 | -0.052847 | 0.059493 | 0.085587 | -0.15499 | 3.449 | -119.181 | 3.6775 | 3.5581 | 0.1091 | -119.1041 | -118.9857 | -0.081749 | -122.793 | 0.10176 | 0.012312 | 0.094061 | -122.6807 | -122.6546 | 3.6324 | 3.7093 | 3.8277 | 3.7879 | -119.3645 | 0.020395 | 0.13273 | 0.15883 | 0.15144 | -122.8952
|  |  |  | 1.4211e-13 | -0.040888 | -0.00027769 | -0.0038783 | -0.012091 | 0.0046086 | -0.0022892 | -0.0048667 | -0.0025533 | 0.015981 | 0.039032 | 0.008809 | 3.5951 | 3.7101 | 3.4711 | 3.55 | 3.6269 | 3.7453 | 3.3757 | 0.02852 | 0.078197 | -0.065509 | -0.066582 | 0.054914 | 0.085587 | -0.15499 | 3.4947 | -119.213 | 3.7141 | 3.5901 | 0.095369 | -119.1362 | -119.0177 | -0.035972 | -122.8296 | 0.14754 | 0.05351 | 0.089482 | -122.7081 | -122.6775 | 3.669 | 3.7459 | 3.8643 | 3.8291 | -119.3873 | 0.052437 | 0.17393 | 0.20461 | 0.19722 | -122.9181
|  |  |  | 1.4211e-13 | -0.040675 | -0.00070509 | -0.0036647 | -0.012305 | 0.004395 | -0.0022892 | -0.0046531 | -0.0027669 | 0.015981 | 0.038818 | 0.0090226 | 3.5951 | 3.7009 | 3.4665 | 3.55 | 3.6177 | 3.727 | 3.3711 | 0.02852 | 0.078197 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.15499 | 3.4764 | -119.2451 | 3.7004 | 3.5718 | 0.09537 | -119.1774 | -119.0681 | -0.049705 | -122.8525 | 0.13381 | 0.044356 | 0.094061 | -122.731 | -122.7049 | 3.6553 | 3.723 | 3.8323 | 3.8062 | -119.424 | 0.047861 | 0.16936 | 0.19545 | 0.18348 | -122.9501
|  |  |  | 1.4211e-13 | -0.040888 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.0046086 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.039032 | 0.0092362 | 3.5905 | 3.7009 | 3.4573 | 3.5409 | 3.6223 | 3.7316 | 3.362 | 0.02852 | 0.078197 | -0.074666 | -0.057425 | 0.064071 | 0.1039 | -0.15041 | 3.4215 | -119.2085 | 3.65 | 3.5169 | 0.095371 | -119.127 | -119.0177 | -0.090903 | -122.8068 | 0.088029 | -0.015157 | 0.075746 | -122.6853 | -122.6454 | 3.6004 | 3.6818 | 3.7911 | 3.7604 | -119.3874 | 0.002084 | 0.12358 | 0.16341 | 0.13771 | -122.8997
|  |  |  | 1.4211e-13 | -0.040888 | -0.00049149 | -0.0038783 | -0.012518 | 0.0046086 | -0.0022892 | -0.0048667 | -0.0027669 | 0.015767 | 0.039032 | 0.0090226 | 3.5768 | 3.6918 | 3.4528 | 3.5271 | 3.6131 | 3.727 | 3.3528 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.06865 | 0.090166 | -0.15041 | 3.4535 | -119.2451 | 3.6775 | 3.5535 | 0.099951 | -119.1591 | -119.0452 | -0.049704 | -122.8296 | 0.12465 | 0.035199 | 0.084903 | -122.7036 | -122.6821 | 3.6278 | 3.7138 | 3.8277 | 3.7925 | -119.4194 | 0.043283 | 0.16936 | 0.19087 | 0.18348 | -122.9226
|  |  |  | 1.4211e-13 | -0.040675 | -6.4092e-05 | -0.0040921 | -0.012305 | 0.0048224 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015981 | 0.039245 | 0.0092362 | 3.5722 | 3.6963 | 3.4528 | 3.5363 | 3.604 | 3.7179 | 3.3482 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.090166 | -0.15499 | 3.4261 | -119.2359 | 3.65 | 3.5306 | 0.10453 | -119.1682 | -119.0544 | -0.077171 | -122.8296 | 0.10634 | 0.012311 | 0.089482 | -122.7127 | -122.6821 | 3.6141 | 3.6818 | 3.7957 | 3.7742 | -119.424 | 0.020395 | 0.13731 | 0.16799 | 0.1606 | -122.9272
|  |  |  | 1.4211e-13 | -0.041316 | -0.00027769 | -0.0036647 | -0.012518 | 0.004395 | -0.01755 | -0.0048667 | -0.0025533 | 0.015767 | 0.038604 | 0.0094498 | 3.5722 | 3.6826 | 3.4528 | 3.5225 | 3.6086 | 3.7087 | 3.3437 | 0.033099 | 0.073618 | -0.06093 | -0.057425 | 0.059493 | 0.094744 | -0.15499 | 3.4535 | -119.2497 | 3.6821 | 3.5626 | 0.10911 | -119.1637 | -119.0635 | -0.045128 | -122.8296 | 0.14296 | 0.048933 | 0.094061 | -122.7127 | -122.6775 | 3.6324 | 3.7184 | 3.8186 | 3.7925 | -119.4286 | 0.052438 | 0.16936 | 0.20461 | 0.18348 | -122.9272
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0038783 | -0.012091 | 0.0046086 | -0.01755 | -0.0050803 | -0.0023397 | 0.015767 | 0.039032 | 0.008809 | 3.5676 | 3.6826 | 3.4345 | 3.5317 | 3.5994 | 3.7087 | 3.3391 | 0.019362 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.090166 | -0.14583 | 3.4489 | -119.213 | 3.6775 | 3.5443 | 0.095374 | -119.1454 | -119.0361 | -0.03597 | -122.8022 | 0.12923 | 0.044354 | 0.080324 | -122.6853 | -122.6546 | 3.6416 | 3.7093 | 3.8186 | 3.7925 | -119.4057 | 0.052438 | 0.16936 | 0.20003 | 0.19264 | -122.8906
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0040921 | -0.012091 | 0.0048224 | -0.0022892 | -0.0048667 | -0.0023397 | 0.015554 | 0.038818 | 0.008809 | 3.5722 | 3.6826 | 3.4345 | 3.518 | 3.5948 | 3.7133 | 3.3345 | 0.019362 | 0.082776 | -0.065509 | -0.057425 | 0.06865 | 0.1039 | -0.15499 | 3.4306 | -119.2634 | 3.6683 | 3.5306 | 0.099953 | -119.1866 | -119.0681 | -0.058861 | -122.8388 | 0.11549 | 0.030621 | 0.089482 | -122.7127 | -122.6775 | 3.6141 | 3.6909 | 3.8094 | 3.7787 | -119.4469 | 0.038705 | 0.16478 | 0.20003 | 0.17891 | -122.9364
|  |  |  | 1.4211e-13 | -0.041102 | -0.00049149 | -0.0043057 | -0.012305 | 0.004395 | -0.0099192 | -0.0044395 | -0.0023397 | 0.015554 | 0.039032 | 0.008809 | 3.563 | 3.6826 | 3.4345 | 3.5134 | 3.5902 | 3.6995 | 3.3391 | 0.019362 | 0.078197 | -0.065509 | -0.062004 | 0.064071 | 0.085587 | -0.15499 | 3.4444 | -119.2497 | 3.6683 | 3.5397 | 0.095374 | -119.1728 | -119.0635 | -0.049705 | -122.8251 | 0.12465 | 0.039777 | 0.089482 | -122.699 | -122.6775 | 3.6187 | 3.6955 | 3.8048 | 3.7879 | -119.424 | 0.043282 | 0.16936 | 0.19087 | 0.18348 | -122.9181
|  |  |  | 1.4211e-13 | -0.040675 | -6.4092e-05 | -0.0038783 | -0.012091 | 0.004395 | -0.01755 | -0.0048667 | -0.0027669 | 0.015981 | 0.039032 | 0.0090226 | 3.5493 | 3.6643 | 3.4253 | 3.5088 | 3.5857 | 3.6995 | 3.3345 | 0.02852 | 0.073618 | -0.070087 | -0.048268 | 0.059493 | 0.085587 | -0.15957 | 3.4123 | -119.2359 | 3.6271 | 3.5031 | 0.090796 | -119.1591 | -119.0452 | -0.08175 | -122.793 | 0.10634 | 0.007733 | 0.089483 | -122.6853 | -122.6592 | 3.5866 | 3.6635 | 3.7774 | 3.7421 | -119.4102 | 0.029552 | 0.13731 | 0.16341 | 0.15144 | -122.9043
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0038783 | -0.012305 | 0.0046086 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.039032 | 0.0090226 | 3.5447 | 3.6597 | 3.4207 | 3.5042 | 3.5811 | 3.6858 | 3.3208 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.06865 | 0.094744 | -0.15499 | 3.4306 | -119.3 | 3.6546 | 3.5306 | 0.099955 | -119.2232 | -119.1185 | -0.045128 | -122.8617 | 0.1338 | 0.048933 | 0.094061 | -122.7356 | -122.7095 | 3.6141 | 3.6909 | 3.7957 | 3.7696 | -119.4835 | 0.052438 | 0.17851 | 0.20461 | 0.19264 | -122.9593
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0040921 | -0.012305 | 0.004395 | -0.0099192 | -0.0046531 | -0.0021259 | 0.015767 | 0.038818 | 0.0092362 | 3.5401 | 3.6551 | 3.4116 | 3.4997 | 3.5765 | 3.6812 | 3.3162 | 0.019362 | 0.073618 | -0.06093 | -0.062004 | 0.064071 | 0.099323 | -0.15499 | 3.4169 | -119.2817 | 3.6408 | 3.5123 | 0.095377 | -119.2049 | -119.1001 | -0.054283 | -122.8434 | 0.12007 | 0.039778 | 0.094061 | -122.7173 | -122.682 | 3.6004 | 3.6772 | 3.7819 | 3.7558 | -119.4652 | 0.038704 | 0.16478 | 0.20003 | 0.17433 | -122.9364
|  |  |  | 1.4211e-13 | -0.040888 | -0.00070509 | -0.0040921 | -0.012305 | 0.0048224 | -0.0099192 | -0.0052939 | -0.0027669 | 0.015554 | 0.039032 | 0.0090226 | 3.531 | 3.6551 | 3.4116 | 3.4997 | 3.5582 | 3.6812 | 3.3116 | 0.023941 | 0.078197 | -0.070087 | -0.057425 | 0.064071 | 0.090166 | -0.15957 | 3.4169 | -119.3092 | 3.6363 | 3.5169 | 0.099956 | -119.2507 | -119.1276 | -0.054284 | -122.8663 | 0.12923 | 0.035199 | 0.089483 | -122.7448 | -122.7187 | 3.6049 | 3.6635 | 3.7865 | 3.7604 | -119.4972 | 0.047861 | 0.16936 | 0.19545 | 0.18348 | -122.9684
|  |  |  | 1.4211e-13 | -0.041102 | -0.00049149 | -0.0038783 | -0.012305 | 0.004395 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015554 | 0.039245 | 0.0085952 | 3.5356 | 3.6414 | 3.4116 | 3.4905 | 3.5673 | 3.6812 | 3.3025 | 0.019362 | 0.078197 | -0.070087 | -0.057425 | 0.064071 | 0.094744 | -0.15041 | 3.394 | -119.2451 | 3.6271 | 3.5031 | 0.10911 | -119.1683 | -119.0544 | -0.058859 | -122.793 | 0.11091 | 0.021466 | 0.080325 | -122.6715 | -122.6409 | 3.582 | 3.6589 | 3.7728 | 3.7329 | -119.4331 | 0.034128 | 0.15562 | 0.1863 | 0.16975 | -122.886
|  |  |  | 1.4211e-13 | -0.040888 | -0.00027769 | -0.0036647 | -0.012091 | 0.0046086 | -0.01755 | -0.0046531 | -0.0027669 | 0.015554 | 0.039245 | 0.008809 | 3.5218 | 3.6414 | 3.3933 | 3.4859 | 3.5582 | 3.6721 | 3.2979 | 0.019362 | 0.082776 | -0.065509 | -0.066582 | 0.064071 | 0.090166 | -0.15499 | 3.3757 | -119.2634 | 3.5996 | 3.4711 | 0.09538 | -119.1911 | -119.0773 | -0.077171 | -122.8159 | 0.097182 | 0.012311 | 0.089482 | -122.6853 | -122.6592 | 3.5637 | 3.636 | 3.7499 | 3.7192 | -119.4515 | 0.011238 | 0.14189 | 0.16799 | 0.1606 | -122.9043
|  |  |  | 1.4211e-13 | -0.040888 | -0.00070509 | -0.0036647 | -0.012091 | 0.004395 | -0.0022892 | -0.0048667 | -0.0025533 | 0.015554 | 0.039245 | 0.0092362 | 3.5264 | 3.6414 | 3.4024 | 3.4813 | 3.5582 | 3.6629 | 3.2979 | 0.02852 | 0.078197 | -0.06093 | -0.048268 | 0.06865 | 0.099323 | -0.15041 | 3.3986 | -119.2955 | 3.6271 | 3.5031 | 0.10454 | -119.2186 | -119.1139 | -0.049704 | -122.8251 | 0.12923 | 0.039778 | 0.089482 | -122.7081 | -122.6775 | 3.582 | 3.6589 | 3.7636 | 3.7421 | -119.4789 | 0.05244 | 0.16936 | 0.20003 | 0.17891 | -122.9272
|  |  |  | 1.4211e-13 | -0.041102 | -0.00027769 | -0.0038783 | -0.012518 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0023397 | 0.015554 | 0.039032 | 0.008809 | 3.5127 | 3.6414 | 3.3887 | 3.4813 | 3.5536 | 3.6629 | 3.2887 | 0.02852 | 0.087354 | -0.06093 | -0.052847 | 0.06865 | 0.094744 | -0.14583 | 3.394 | -119.3092 | 3.618 | 3.494 | 0.09996 | -119.2369 | -119.1276 | -0.040547 | -122.8434 | 0.13381 | 0.044356 | 0.084903 | -122.7219 | -122.6958 | 3.5866 | 3.6589 | 3.7682 | 3.7467 | -119.5018 | 0.052439 | 0.17394 | 0.20003 | 0.19264 | -122.9364
|  |  |  | 1.4211e-13 | -0.040675 | -0.00027769 | -0.0034509 | -0.012091 | 0.0039676 | -0.01755 | -0.0046531 | -0.0023397 | 0.015554 | 0.039459 | 0.0090226 | 3.5127 | 3.6277 | 3.3887 | 3.4768 | 3.549 | 3.6675 | 3.2887 | 0.023941 | 0.078197 | -0.06093 | -0.052847 | 0.059493 | 0.090166 | -0.15499 | 3.3711 | -119.2955 | 3.5951 | 3.4711 | 0.09996 | -119.2232 | -119.1047 | -0.072594 | -122.8251 | 0.10634 | 0.021467 | 0.094061 | -122.7127 | -122.6821 | 3.5592 | 3.6314 | 3.7499 | 3.7101 | -119.4835 | 0.02955 | 0.14189 | 0.17256 | 0.16059 | -122.9272
|  |  |  | 1.4211e-13 | -0.040675 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.004395 | -0.01755 | -0.0046531 | -0.0027669 | 0.015554 | 0.038818 | 0.0090226 | 3.5035 | 3.6277 | 3.3887 | 3.4722 | 3.5444 | 3.6492 | 3.2933 | 0.02852 | 0.06904 | -0.065509 | -0.052847 | 0.064071 | 0.090166 | -0.14583 | 3.4123 | -119.3229 | 3.6225 | 3.5077 | 0.095381 | -119.2507 | -119.1459 | -0.026814 | -122.848 | 0.14754 | 0.05351 | 0.080324 | -122.731 | -122.7049 | 3.5912 | 3.6635 | 3.7682 | 3.7467 | -119.5018 | 0.066172 | 0.18309 | 0.20919 | 0.18806 | -122.9409
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0036647 | -0.012091 | 0.004395 | -0.0099192 | -0.0044395 | -0.0025533 | 0.015554 | 0.039032 | 0.008809 | 3.5035 | 3.6139 | 3.3749 | 3.4584 | 3.5399 | 3.6446 | 3.275 | 0.02852 | 0.078197 | -0.070087 | -0.052847 | 0.054914 | 0.090166 | -0.15499 | 3.3848 | -119.3183 | 3.6134 | 3.4848 | 0.099961 | -119.2369 | -119.1322 | -0.045128 | -122.8296 | 0.13838 | 0.039776 | 0.084904 | -122.7219 | -122.6866 | 3.5683 | 3.6497 | 3.7545 | 3.7238 | -119.5018 | 0.057016 | 0.16478 | 0.20003 | 0.18806 | -122.9318
|  |  |  | 1.4211e-13 | -0.041102 | -0.00049149 | -0.0040921 | -0.012305 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0027669 | 0.01534 | 0.039032 | 0.0092362 | 3.4989 | 3.6093 | 3.3749 | 3.463 | 3.5261 | 3.6446 | 3.2704 | 0.033099 | 0.078197 | -0.056351 | -0.057425 | 0.064071 | 0.094744 | -0.15041 | 3.3803 | -119.3229 | 3.6088 | 3.4848 | 0.10454 | -119.2598 | -119.1414 | -0.040549 | -122.8434 | 0.14296 | 0.053512 | 0.094061 | -122.7219 | -122.6912 | 3.5729 | 3.636 | 3.7545 | 3.7192 | -119.5156 | 0.052438 | 0.17393 | 0.20461 | 0.18806 | -122.9364
|  |  |  | 1.4211e-13 | -0.040888 | -6.4092e-05 | -0.0036647 | -0.012305 | 0.0041814 | -0.01755 | -0.0046531 | -0.0027669 | 0.015554 | 0.038818 | 0.0090226 | 3.4944 | 3.6093 | 3.3658 | 3.4493 | 3.5261 | 3.64 | 3.2704 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.16415 | 3.3711 | -119.3458 | 3.5951 | 3.4665 | 0.095383 | -119.269 | -119.1551 | -0.063441 | -122.8571 | 0.12465 | 0.039778 | 0.10322 | -122.7356 | -122.7049 | 3.55 | 3.6268 | 3.7407 | 3.7101 | -119.5247 | 0.038704 | 0.1602 | 0.19087 | 0.17891 | -122.9593
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0038783 | -0.012305 | 0.004395 | -0.01755 | -0.0046531 | -0.0025533 | 0.015767 | 0.039459 | 0.0090226 | 3.4898 | 3.6002 | 3.3566 | 3.4539 | 3.517 | 3.6309 | 3.2612 | 0.02852 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 3.3665 | -119.3275 | 3.5951 | 3.4619 | 0.095385 | -119.2644 | -119.1505 | -0.049705 | -122.8434 | 0.13381 | 0.039777 | 0.089482 | -122.7219 | -122.6912 | 3.5592 | 3.6223 | 3.7361 | 3.7055 | -119.5201 | 0.043282 | 0.16478 | 0.19545 | 0.18348 | -122.9364
|  |  |  | 1.4211e-13 | -0.041316 | -0.00049149 | -0.0038783 | -0.012091 | 0.0046086 | -0.0099192 | -0.0048667 | -0.0027669 | 0.01534 | 0.039245 | 0.0090226 | 3.4852 | 3.6002 | 3.352 | 3.4447 | 3.517 | 3.6263 | 3.2567 | 0.02852 | 0.082776 | -0.070087 | -0.052847 | 0.064071 | 0.090166 | -0.15499 | 3.3253 | -119.3183 | 3.5539 | 3.4207 | 0.095386 | -119.2461 | -119.1368 | -0.086326 | -122.8159 | 0.097185 | -0.001422 | 0.084904 | -122.699 | -122.6729 | 3.5134 | 3.5856 | 3.6949 | 3.6689 | -119.5064 | 0.015818 | 0.13274 | 0.15883 | 0.15144 | -122.9181
|  |  |  | 1.4211e-13 | -0.040888 | -0.00070509 | -0.0038783 | -0.012091 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.039245 | 0.0092362 | 3.4806 | 3.5865 | 3.3566 | 3.4356 | 3.5124 | 3.6217 | 3.2567 | 0.023941 | 0.082776 | -0.056351 | -0.066582 | 0.064071 | 0.090166 | -0.15499 | 3.3757 | -119.355 | 3.5996 | 3.4756 | 0.099964 | -119.2781 | -119.1688 | -0.035972 | -122.8571 | 0.14296 | 0.062668 | 0.09864 | -122.7265 | -122.7004 | 3.5546 | 3.6314 | 3.7407 | 3.7055 | -119.5339 | 0.052437 | 0.18309 | 0.20919 | 0.2018 | -122.9455
|  |  |  | 1.4211e-13 | -0.041102 | -0.00027769 | -0.0036647 | -0.012091 | 0.0041814 | -0.0099192 | -0.0044395 | -0.0023397 | 0.015767 | 0.038818 | 0.0092362 | 3.4669 | 3.591 | 3.3475 | 3.4356 | 3.5078 | 3.6171 | 3.2521 | 0.019362 | 0.087354 | -0.065509 | -0.066582 | 0.064071 | 0.085587 | -0.15499 | 3.3482 | -119.355 | 3.563 | 3.4436 | 0.095386 | -119.2827 | -119.1734 | -0.058861 | -122.8571 | 0.11549 | 0.030621 | 0.089482 | -122.7265 | -122.7049 | 3.5317 | 3.6039 | 3.7133 | 3.6872 | -119.5384 | 0.029548 | 0.1602 | 0.18172 | 0.18348 | -122.9455
|  |  |  | 1.4211e-13 | -0.041102 | -0.00049149 | -0.0038783 | -0.012305 | 0.004395 | -0.0099192 | -0.0048667 | -0.0023397 | 0.01534 | 0.039032 | 0.0090226 | 3.4669 | 3.5865 | 3.3337 | 3.4264 | 3.5032 | 3.6125 | 3.2383 | 0.023941 | 0.073618 | -0.06093 | -0.052847 | 0.064071 | 0.094744 | -0.15041 | 3.3391 | -119.3641 | 3.5676 | 3.4344 | 0.095388 | -119.2873 | -119.178 | -0.049704 | -122.8434 | 0.12465 | 0.039778 | 0.089482 | -122.7265 | -122.6958 | 3.5271 | 3.6039 | 3.7133 | 3.6872 | -119.5522 | 0.047861 | 0.16478 | 0.19545 | 0.17433 | -122.9409
|  |  |  | 1.4211e-13 | -0.041316 | -0.00027769 | -0.0038783 | -0.012305 | 0.004395 | -0.02518 | -0.0050803 | -0.0025533 | 0.015767 | 0.039245 | 0.0090226 | 3.4577 | 3.5819 | 3.3337 | 3.4264 | 3.4941 | 3.6034 | 3.2383 | 0.014784 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15499 | 3.3574 | -119.3687 | 3.5767 | 3.4528 | 0.095388 | -119.301 | -119.1917 | -0.035972 | -122.8525 | 0.1338 | 0.05351 | 0.089482 | -122.7356 | -122.7004 | 3.5454 | 3.6131 | 3.7224 | 3.7009 | -119.5568 | 0.061594 | 0.17851 | 0.21376 | 0.2018 | -122.9501
|  |  |  | 1.4211e-13 | -0.041102 | -0.00070509 | -0.0040921 | -0.012305 | 0.0041814 | -0.01755 | -0.0048667 | -0.0023397 | 0.015767 | 0.039245 | 0.008809 | 3.4623 | 3.5819 | 3.3337 | 3.4218 | 3.4895 | 3.6034 | 3.2292 | 0.023941 | 0.078197 | -0.06093 | -0.052847 | 0.059493 | 0.090166 | -0.16415 | 3.3436 | -119.3779 | 3.5767 | 3.4482 | 0.10455 | -119.3102 | -119.1963 | -0.049708 | -122.8525 | 0.13838 | 0.053511 | 0.10322 | -122.7402 | -122.7095 | 3.5363 | 3.6039 | 3.7178 | 3.6963 | -119.5705 | 0.061594 | 0.17393 | 0.20461 | 0.19264 | -122.9638
|  |  |  | 1.4211e-13 | -0.040888 | -0.00049149 | -0.0038783 | -0.012305 | 0.0041814 | -0.0099192 | -0.0046531 | -0.0023397 | 0.01534 | 0.039032 | 0.0092362 | 3.4577 | 3.5773 | 3.3292 | 3.4127 | 3.4895 | 3.5942 | 3.2292 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 3.3299 | -119.3916 | 3.5584 | 3.4299 | 0.099968 | -119.3148 | -119.21 | -0.049704 | -122.8617 | 0.12465 | 0.039778 | 0.089482 | -122.7448 | -122.7141 | 3.5134 | 3.5902 | 3.6949 | 3.678 | -119.5751 | 0.043283 | 0.1602 | 0.19087 | 0.18348 | -122.9547
|  |  |  | 1.4211e-13 | -0.041316 | -0.00027769 | -0.0038783 | -0.012091 | 0.0046086 | -0.0099192 | -0.0044395 | -0.0027669 | 0.015554 | 0.039245 | 0.0092362 | 3.4532 | 3.5636 | 3.32 | 3.4035 | 3.4849 | 3.5897 | 3.2246 | 0.02852 | 0.087354 | -0.070087 | -0.062004 | 0.054914 | 0.099323 | -0.15041 | 3.3299 | -119.3733 | 3.5584 | 3.4253 | 0.09539 | -119.2919 | -119.1871 | -0.045126 | -122.8388 | 0.13381 | 0.035199 | 0.080325 | -122.7219 | -122.6775 | 3.5088 | 3.5902 | 3.6949 | 3.6688 | -119.5522 | 0.043282 | 0.1602 | 0.20461 | 0.19264 | -122.9272
|  |  |  | 1.4211e-13 | -0.041316 | -0.00049149 | -0.0040921 | -0.011877 | 0.004395 | -0.01755 | -0.0048667 | -0.0025533 | 0.015981 | 0.039245 | 0.0090226 | 3.444 | 3.5773 | 3.3292 | 3.4081 | 3.4758 | 3.5897 | 3.2292 | 0.023941 | 0.073618 | -0.06093 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 3.3436 | -119.3733 | 3.5584 | 3.4436 | 0.099968 | -119.3056 | -119.1917 | -0.035971 | -122.8388 | 0.13838 | 0.053511 | 0.089482 | -122.7219 | -122.6912 | 3.5225 | 3.5902 | 3.7041 | 3.6917 | -119.5522 | 0.057016 | 0.17393 | 0.20461 | 0.18806 | -122.9318
|  |  |  | 1.4211e-13 | -0.041316 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.004395 | -0.0022892 | -0.0046531 | -0.0025533 | 0.015767 | 0.039032 | 0.0090226 | 3.4486 | 3.5681 | 3.3108 | 3.3989 | 3.4803 | 3.5851 | 3.2155 | 0.014784 | 0.078197 | -0.06093 | -0.057425 | 0.059493 | 0.094744 | -0.15041 | 3.2978 | -119.3458 | 3.531 | 3.3932 | 0.095391 | -119.2644 | -119.1597 | -0.068015 | -122.8022 | 0.097181 | 0.021467 | 0.089482 | -122.6853 | -122.65 | 3.4813 | 3.5627 | 3.6675 | 3.6505 | -119.5293 | 0.024972 | 0.14189 | 0.17714 | 0.16059 | -122.8952
|  |  |  | 1.4211e-13 | -0.041529 | -0.00049149 | -0.0038783 | -0.012305 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.039459 | 0.0094498 | 3.4394 | 3.5681 | 3.32 | 3.3989 | 3.4666 | 3.5805 | 3.2109 | 0.019362 | 0.078197 | -0.070087 | -0.062004 | 0.059493 | 0.094744 | -0.15957 | 3.2704 | -119.3733 | 3.4989 | 3.3795 | 0.10913 | -119.3056 | -119.1917 | -0.10006 | -122.8342 | 0.078871 | -0.010578 | 0.089483 | -122.7127 | -122.6775 | 3.4584 | 3.5261 | 3.64 | 3.6276 | -119.5613 | -0.002495 | 0.119 | 0.15425 | 0.13771 | -122.9318
|  |  |  | 1.4211e-13 | -0.040888 | -0.00027769 | -0.0038783 | -0.012305 | 0.004395 | -0.0022892 | -0.0048667 | -0.0027669 | 0.015981 | 0.039245 | 0.0094498 | 3.4348 | 3.559 | 3.3108 | 3.3898 | 3.4666 | 3.5805 | 3.2017 | 0.02852 | 0.073618 | -0.06093 | -0.057425 | 0.059493 | 0.090166 | -0.15499 | 3.2887 | -119.387 | 3.5218 | 3.3978 | 0.10913 | -119.3102 | -119.1963 | -0.068016 | -122.8342 | 0.1155 | 0.026045 | 0.094061 | -122.7173 | -122.6866 | 3.4767 | 3.5536 | 3.6675 | 3.646 | -119.5751 | 0.02955 | 0.14647 | 0.17714 | 0.16059 | -122.9318
|  |  |  | 1.4211e-13 | -0.041102 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.0046086 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015767 | 0.039032 | 0.0090226 | 3.4303 | 3.5544 | 3.2971 | 3.3852 | 3.462 | 3.5713 | 3.1926 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 3.2658 | -119.3962 | 3.5035 | 3.3704 | 0.10455 | -119.3193 | -119.21 | -0.081749 | -122.8434 | 0.097183 | 0.007733 | 0.089482 | -122.7219 | -122.6912 | 3.4584 | 3.5353 | 3.6446 | 3.6276 | -119.5888 | 0.011238 | 0.13273 | 0.16341 | 0.15144 | -122.9364
|  |  |  | 1.4211e-13 | -0.041316 | -0.00070509 | -0.0034509 | -0.012091 | 0.0046086 | -0.0022892 | -0.0044395 | -0.0025533 | 0.01534 | 0.039245 | 0.0085952 | 3.4211 | 3.5498 | 3.3017 | 3.3898 | 3.462 | 3.5622 | 3.2017 | 0.033099 | 0.082776 | -0.070087 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 3.2933 | -119.3641 | 3.5127 | 3.3932 | 0.099971 | -119.2919 | -119.1917 | -0.058859 | -122.8113 | 0.12465 | 0.021466 | 0.080325 | -122.6944 | -122.6637 | 3.4813 | 3.5536 | 3.6537 | 3.6414 | -119.5522 | 0.034128 | 0.15105 | 0.18172 | 0.17433 | -122.9043
|  |  |  | 1.4211e-13 | -0.041102 | -0.00091889 | -0.0036647 | -0.012091 | 0.004395 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015554 | 0.039245 | 0.0090226 | 3.4119 | 3.5452 | 3.2925 | 3.376 | 3.4529 | 3.5622 | 3.1926 | 0.023941 | 0.078197 | -0.056351 | -0.048268 | 0.054914 | 0.085587 | -0.15957 | 3.2475 | -119.3687 | 3.4669 | 3.3475 | 0.099973 | -119.2919 | -119.1826 | -0.10464 | -122.793 | 0.078873 | -0.001419 | 0.10322 | -122.6898 | -122.6592 | 3.431 | 3.5078 | 3.6171 | 3.6002 | -119.5522 | 0.006664 | 0.10985 | 0.14052 | 0.13313 | -122.9043
|  |  |  | 1.4211e-13 | -0.041529 | -0.00049149 | -0.0036647 | -0.012305 | 0.004395 | -0.01755 | -0.0046531 | -0.0023397 | 0.015767 | 0.039245 | 0.0092362 | 3.4119 | 3.5407 | 3.288 | 3.3669 | 3.4529 | 3.5576 | 3.188 | 0.033099 | 0.073618 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.15041 | 3.2475 | -119.3962 | 3.4715 | 3.3475 | 0.099974 | -119.3102 | -119.2055 | -0.090903 | -122.8205 | 0.092608 | -0.001421 | 0.089482 | -122.699 | -122.6729 | 3.4264 | 3.5124 | 3.6171 | 3.6002 | -119.5751 | 0.002084 | 0.12358 | 0.14968 | 0.13313 | -122.9135
|  |  |  | 1.4211e-13 | -0.041102 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.039245 | 0.0092362 | 3.4074 | 3.5407 | 3.2834 | 3.3715 | 3.4437 | 3.553 | 3.1834 | 0.023941 | 0.082776 | -0.056351 | -0.052847 | 0.054914 | 0.090166 | -0.15041 | 3.2704 | -119.4099 | 3.4943 | 3.3703 | 0.099974 | -119.3377 | -119.2283 | -0.063437 | -122.8342 | 0.11092 | 0.030624 | 0.094061 | -122.7265 | -122.6912 | 3.4584 | 3.5307 | 3.64 | 3.6276 | -119.598 | 0.034128 | 0.14189 | 0.17714 | 0.16975 | -122.9318
|  |  |  | 1.4211e-13 | -0.041102 | -6.4092e-05 | -0.0043057 | -0.012518 | 0.0041814 | -0.0022892 | -0.0048667 | -0.0025533 | 0.015767 | 0.039245 | 0.008809 | 3.4028 | 3.5269 | 3.2788 | 3.3623 | 3.4391 | 3.553 | 3.1788 | 0.033099 | 0.078197 | -0.06093 | -0.052847 | 0.054914 | 0.094744 | -0.15957 | 3.2566 | -119.3733 | 3.4806 | 3.3566 | 0.099975 | -119.2965 | -119.1826 | -0.08175 | -122.7884 | 0.11092 | 0.01689 | 0.09864 | -122.6807 | -122.6409 | 3.4401 | 3.517 | 3.6308 | 3.6048 | -119.5568 | 0.024973 | 0.13273 | 0.17256 | 0.15602 | -122.8952
|  |  |  | 1.4211e-13 | -0.041102 | -0.00027769 | -0.0036647 | -0.012091 | 0.0046086 | -0.02518 | -0.0050803 | -0.0021259 | 0.015767 | 0.039245 | 0.008809 | 3.3936 | 3.5224 | 3.2742 | 3.3577 | 3.4391 | 3.5439 | 3.1788 | 0.019362 | 0.087354 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15041 | 3.2475 | -119.4099 | 3.4623 | 3.3429 | 0.095397 | -119.3285 | -119.2238 | -0.081747 | -122.8205 | 0.088027 | 0.007735 | 0.089482 | -122.7081 | -122.6729 | 3.4264 | 3.5078 | 3.6125 | 3.591 | -119.5888 | 0.015818 | 0.12816 | 0.16341 | 0.15602 | -122.9181
|  |  |  | 1.4211e-13 | -0.041316 | -0.00070509 | -0.0036647 | -0.012091 | 0.0041814 | -0.0022892 | -0.0046531 | -0.0029805 | 0.015554 | 0.039245 | 0.008809 | 3.3936 | 3.5315 | 3.2651 | 3.3531 | 3.4254 | 3.5393 | 3.1697 | 0.02852 | 0.078197 | -0.056351 | -0.052847 | 0.059493 | 0.090166 | -0.15499 | 3.2887 | -119.4603 | 3.5127 | 3.3841 | 0.095398 | -119.388 | -119.2741 | -0.035972 | -122.8663 | 0.14754 | 0.062668 | 0.09864 | -122.7539 | -122.7233 | 3.4722 | 3.5444 | 3.6583 | 3.6505 | -119.6438 | 0.066172 | 0.17851 | 0.20919 | 0.19722 | -122.9684
|  |  |  | 1.4211e-13 | -0.040675 | -0.00049149 | -0.0038783 | -0.012305 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0025533 | 0.01534 | 0.039032 | 0.008809 | 3.3936 | 3.5178 | 3.2605 | 3.3486 | 3.4208 | 3.5301 | 3.1651 | 0.02852 | 0.082776 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.16415 | 3.2383 | -119.4053 | 3.4669 | 3.3337 | 0.095398 | -119.3331 | -119.2238 | -0.090907 | -122.8068 | 0.10176 | 0.012312 | 0.10322 | -122.6944 | -122.6592 | 3.4218 | 3.4941 | 3.6034 | 3.591 | -119.5888 | 0.020395 | 0.13273 | 0.16799 | 0.15602 | -122.9181
|  |  |  | 1.4211e-13 | -0.041529 | -0.00049149 | -0.0036647 | -0.012091 | 0.004395 | -0.01755 | -0.0044395 | -0.0025533 | 0.01534 | 0.039459 | 0.0090226 | 3.3753 | 3.5132 | 3.2605 | 3.3486 | 3.4208 | 3.5347 | 3.1605 | 0.02852 | 0.078197 | -0.06093 | -0.062004 | 0.064071 | 0.085587 | -0.15041 | 3.2475 | -119.4099 | 3.4623 | 3.3475 | 0.099977 | -119.3377 | -119.2238 | -0.063437 | -122.8205 | 0.1155 | 0.026045 | 0.089482 | -122.6944 | -122.6729 | 3.4355 | 3.5078 | 3.6217 | 3.6002 | -119.598 | 0.024971 | 0.15105 | 0.17256 | 0.16517 | -122.9089
|  |  |  | 1.4211e-13 | -0.041102 | -0.00027769 | -0.0034509 | -0.012518 | 0.0046086 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015767 | 0.039032 | 0.0090226 | 3.3799 | 3.5086 | 3.2422 | 3.3348 | 3.4117 | 3.5164 | 3.1559 | 0.02852 | 0.078197 | -0.06093 | -0.057425 | 0.059493 | 0.090166 | -0.15499 | 3.2566 | -119.4557 | 3.4806 | 3.3429 | 0.086243 | -119.3789 | -119.2741 | -0.054283 | -122.848 | 0.12923 | 0.039778 | 0.094061 | -122.731 | -122.7004 | 3.4355 | 3.5124 | 3.6171 | 3.6093 | -119.6346 | 0.043283 | 0.1602 | 0.19087 | 0.17891 | -122.9455
|  |  |  | 1.4211e-13 | -0.041102 | -0.00027769 | -0.0038783 | -0.012305 | 0.004395 | -0.01755 | -0.0050803 | -0.0025533 | 0.015767 | 0.039673 | 0.0090226 | 3.3662 | 3.4995 | 3.2422 | 3.3303 | 3.4117 | 3.521 | 3.1468 | 0.02852 | 0.082776 | -0.065509 | -0.062004 | 0.059493 | 0.090166 | -0.14583 | 3.2566 | -119.474 | 3.476 | 3.352 | 0.095401 | -119.3926 | -119.2833 | -0.03597 | -122.8663 | 0.13838 | 0.044354 | 0.080324 | -122.7448 | -122.7141 | 3.4401 | 3.5215 | 3.6308 | 3.6093 | -119.6575 | 0.047859 | 0.16936 | 0.20003 | 0.19264 | -122.9501
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0034509 | -0.012091 | 0.004395 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015767 | 0.039459 | 0.0090226 | 3.3616 | 3.4949 | 3.2376 | 3.3211 | 3.3979 | 3.5118 | 3.1376 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.059493 | 0.1039 | -0.15041 | 3.2154 | -119.442 | 3.4394 | 3.3154 | 0.099981 | -119.3651 | -119.2512 | -0.072592 | -122.8205 | 0.10176 | 0.01689 | 0.089482 | -122.7036 | -122.6592 | 3.3989 | 3.4757 | 3.5896 | 3.5727 | -119.6255 | 0.020395 | 0.13731 | 0.18172 | 0.16517 | -122.9135
|  |  |  | 1.4211e-13 | -0.041102 | -0.00027769 | -0.0036647 | -0.012305 | 0.0046086 | -0.0022892 | -0.0050803 | -0.0025533 | 0.015554 | 0.039245 | 0.0090226 | 3.3662 | 3.4903 | 3.2376 | 3.3165 | 3.3888 | 3.5027 | 3.1422 | 0.023941 | 0.082776 | -0.06093 | -0.066582 | 0.059493 | 0.094744 | -0.15499 | 3.2063 | -119.4557 | 3.4303 | 3.3017 | 0.095402 | -119.3835 | -119.2696 | -0.090904 | -122.8388 | 0.088028 | 0.003157 | 0.094061 | -122.7127 | -122.6775 | 3.3806 | 3.4528 | 3.5667 | 3.5544 | -119.63 | -0.002495 | 0.12358 | 0.15883 | 0.14686 | -122.9272
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0038783 | -0.012091 | 0.004395 | -0.01755 | -0.0048667 | -0.0023397 | 0.015554 | 0.039245 | 0.0090226 | 3.3433 | 3.4857 | 3.2147 | 3.3165 | 3.3888 | 3.4935 | 3.1285 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15499 | 3.2337 | -119.5061 | 3.4486 | 3.32 | 0.086247 | -119.4338 | -119.3291 | -0.049705 | -122.88 | 0.13381 | 0.039777 | 0.089482 | -122.7631 | -122.7278 | 3.4218 | 3.494 | 3.5988 | 3.591 | -119.6941 | 0.047861 | 0.16478 | 0.20003 | 0.18806 | -122.9776
|  |  |  | 1.4211e-13 | -0.041529 | -6.4092e-05 | -0.0040921 | -0.012305 | 0.004395 | -0.01755 | -0.0046531 | -0.0025533 | 0.01534 | 0.039459 | 0.0090226 | 3.3524 | 3.4766 | 3.2284 | 3.3074 | 3.3888 | 3.4843 | 3.1285 | 0.02852 | 0.078197 | -0.056351 | -0.062004 | 0.059493 | 0.085587 | -0.14583 | 3.2292 | -119.4923 | 3.4531 | 3.3291 | 0.099982 | -119.4109 | -119.3153 | -0.045125 | -122.8617 | 0.12923 | 0.044357 | 0.089482 | -122.7402 | -122.7141 | 3.4081 | 3.4895 | 3.5851 | 3.5773 | -119.6712 | 0.038704 | 0.1602 | 0.18629 | 0.17891 | -122.9455
|  |  |  | 1.4211e-13 | -0.041529 | -6.4092e-05 | -0.0036647 | -0.012305 | 0.004395 | -0.01755 | -0.0046531 | -0.0025533 | 0.015126 | 0.039459 | 0.0092362 | 3.3433 | 3.472 | 3.2193 | 3.3028 | 3.3796 | 3.4889 | 3.1193 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.064071 | 0.090166 | -0.15041 | 3.2429 | -119.5106 | 3.4669 | 3.3429 | 0.099983 | -119.4338 | -119.3245 | -0.026816 | -122.8754 | 0.14754 | 0.062666 | 0.089482 | -122.7493 | -122.7233 | 3.4264 | 3.5032 | 3.6125 | 3.5956 | -119.6941 | 0.061592 | 0.18767 | 0.21376 | 0.20179 | -122.9638
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0034509 | -0.011877 | 0.004395 | -0.01755 | -0.0050803 | -0.0027669 | 0.01534 | 0.039032 | 0.0090226 | 3.3341 | 3.4674 | 3.2101 | 3.289 | 3.3659 | 3.4843 | 3.1147 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.054914 | 0.094744 | -0.16415 | 3.1925 | -119.4603 | 3.4119 | 3.2879 | 0.095406 | -119.3835 | -119.265 | -0.086329 | -122.8068 | 0.10634 | 0.012311 | 0.09864 | -122.6944 | -122.6546 | 3.3669 | 3.4437 | 3.5622 | 3.5452 | -119.6346 | 0.020395 | 0.13273 | 0.17256 | 0.15602 | -122.9135
|  |  |  | 1.4211e-13 | -0.041316 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.0046086 | -0.0022892 | -0.0048667 | -0.0027669 | 0.01534 | 0.039459 | 0.008809 | 3.3341 | 3.4628 | 3.2101 | 3.2845 | 3.3704 | 3.4798 | 3.1147 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.059493 | 0.090166 | -0.15041 | 3.2154 | -119.5427 | 3.4348 | 3.3108 | 0.095406 | -119.4567 | -119.3474 | -0.049704 | -122.8937 | 0.12923 | 0.039778 | 0.089482 | -122.7677 | -122.737 | 3.3852 | 3.4712 | 3.5805 | 3.5635 | -119.7124 | 0.034126 | 0.1602 | 0.19087 | 0.17891 | -122.9776
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0034509 | -0.012305 | 0.0048224 | 0.0053413 | -0.0046531 | -0.0027669 | 0.015767 | 0.039245 | 0.0090226 | 3.3204 | 3.4583 | 3.1964 | 3.2799 | 3.3613 | 3.4706 | 3.0964 | 0.02852 | 0.078197 | -0.065509 | -0.057425 | 0.054914 | 0.094744 | -0.15041 | 3.1788 | -119.474 | 3.4028 | 3.2788 | 0.099986 | -119.3926 | -119.2833 | -0.068015 | -122.8113 | 0.11092 | 0.016888 | 0.084903 | -122.699 | -122.6592 | 3.3623 | 3.4437 | 3.553 | 3.5406 | -119.6575 | 0.024972 | 0.13731 | 0.17714 | 0.16059 | -122.9043
|  |  |  | 1.4211e-13 | -0.041316 | -6.4092e-05 | -0.0038783 | -0.012305 | 0.0041814 | -0.01755 | -0.0046531 | -0.0025533 | 0.015554 | 0.039245 | 0.0090226 | 3.3158 | 3.4491 | 3.1872 | 3.2799 | 3.3521 | 3.4706 | 3.0918 | 0.023941 | 0.078197 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15499 | 3.1696 | -119.4649 | 3.3936 | 3.2651 | 0.095408 | -119.3926 | -119.2741 | -0.077171 | -122.7976 | 0.10176 | 0.01689 | 0.094061 | -122.6853 | -122.65 | 3.3577 | 3.43 | 3.5484 | 3.5269 | -119.6529 | 0.024973 | 0.13731 | 0.17256 | 0.15602 | -122.8997
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0034509 | -0.012091 | 0.0039676 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015767 | 0.039459 | 0.0090226 | 3.3066 | 3.4445 | 3.1827 | 3.2707 | 3.3476 | 3.4523 | 3.0964 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 3.2154 | -119.5289 | 3.4257 | 3.3017 | 0.086251 | -119.4521 | -119.3474 | -0.035972 | -122.8617 | 0.14296 | 0.058089 | 0.094061 | -122.7402 | -122.7095 | 3.3898 | 3.4666 | 3.5713 | 3.5635 | -119.7033 | 0.057015 | 0.17851 | 0.20919 | 0.19722 | -122.9547
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0038783 | -0.012305 | 0.0041814 | -0.01755 | -0.0050803 | -0.0027669 | 0.01534 | 0.039459 | 0.0090226 | 3.3066 | 3.4354 | 3.1827 | 3.2616 | 3.343 | 3.4523 | 3.0735 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.064071 | 0.085587 | -0.15041 | 3.1422 | -119.5106 | 3.3753 | 3.2513 | 0.10915 | -119.4292 | -119.3199 | -0.081747 | -122.8296 | 0.097185 | 0.003156 | 0.084903 | -122.7081 | -122.6866 | 3.3302 | 3.4116 | 3.521 | 3.504 | -119.6987 | 0.01124 | 0.13274 | 0.15425 | 0.14228 | -122.9226
|  |  |  | 1.4211e-13 | -0.041316 | -0.00049149 | -0.0034509 | -0.012518 | 0.0046086 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015554 | 0.039032 | 0.0090226 | 3.3021 | 3.4216 | 3.1598 | 3.257 | 3.3338 | 3.4431 | 3.0735 | 0.023941 | 0.073618 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15499 | 3.1422 | -119.5473 | 3.3707 | 3.2284 | 0.086255 | -119.4704 | -119.3611 | -0.086326 | -122.8571 | 0.092606 | 0.007735 | 0.094061 | -122.7448 | -122.7095 | 3.3257 | 3.4025 | 3.5118 | 3.4903 | -119.7308 | 0.015818 | 0.12816 | 0.16341 | 0.14228 | -122.9593
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0038783 | -0.012518 | 0.004395 | -0.02518 | -0.0048667 | -0.0025533 | 0.01534 | 0.039245 | 0.008809 | 3.2883 | 3.4308 | 3.1689 | 3.257 | 3.3338 | 3.4386 | 3.0781 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.06865 | 0.094744 | -0.15499 | 3.2017 | -119.5427 | 3.4119 | 3.2925 | 0.090832 | -119.4659 | -119.3611 | -0.031395 | -122.8571 | 0.15212 | 0.058087 | 0.089482 | -122.731 | -122.7049 | 3.3806 | 3.4574 | 3.5622 | 3.5544 | -119.7216 | 0.066171 | 0.19225 | 0.21834 | 0.20637 | -122.9547
|  |  |  | 1.4211e-13 | -0.041316 | -0.00027769 | -0.0034509 | -0.012305 | 0.0041814 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015767 | 0.039245 | 0.008809 | 3.2792 | 3.417 | 3.1598 | 3.2524 | 3.3201 | 3.4294 | 3.0689 | 0.019362 | 0.073618 | -0.070087 | -0.052847 | 0.06865 | 0.094744 | -0.15499 | 3.1376 | -119.5244 | 3.3478 | 3.2284 | 0.090834 | -119.4567 | -119.3474 | -0.086326 | -122.8296 | 0.088027 | -0.001422 | 0.084904 | -122.7081 | -122.682 | 3.3211 | 3.3887 | 3.4981 | 3.4857 | -119.7079 | 0.015818 | 0.13732 | 0.16341 | 0.14228 | -122.9318
|  |  |  | 1.4211e-13 | -0.041316 | -0.00027769 | -0.0036647 | -0.012518 | 0.0039676 | -0.02518 | -0.0050803 | -0.0023397 | 0.015554 | 0.039245 | 0.008809 | 3.2746 | 3.417 | 3.1643 | 3.2433 | 3.3109 | 3.434 | 3.0598 | 0.033099 | 0.073618 | -0.065509 | -0.052847 | 0.06865 | 0.090166 | -0.15499 | 3.1605 | -119.5335 | 3.3753 | 3.265 | 0.10457 | -119.4659 | -119.3428 | -0.054283 | -122.8296 | 0.13381 | 0.035199 | 0.089482 | -122.7081 | -122.6866 | 3.344 | 3.4116 | 3.5347 | 3.5178 | -119.717 | 0.047861 | 0.16936 | 0.19087 | 0.17433 | -122.9318
|  |  |  | 1.4211e-13 | -0.041529 | -0.00049149 | -0.0034509 | -0.012305 | 0.004395 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015767 | 0.039245 | 0.0085952 | 3.2746 | 3.4125 | 3.1552 | 3.2387 | 3.3155 | 3.4248 | 3.0506 | 0.02852 | 0.078197 | -0.06093 | -0.048268 | 0.064071 | 0.090166 | -0.15499 | 3.1651 | -119.561 | 3.389 | 3.2696 | 0.10457 | -119.4842 | -119.3749 | -0.04055 | -122.848 | 0.14296 | 0.053511 | 0.094061 | -122.7356 | -122.7095 | 3.3531 | 3.4299 | 3.5393 | 3.5269 | -119.7491 | 0.066173 | 0.17851 | 0.20461 | 0.19264 | -122.9547
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0038783 | -0.012518 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.01534 | 0.039459 | 0.0096636 | 3.2746 | 3.4079 | 3.1369 | 3.2295 | 3.3063 | 3.4248 | 3.0506 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.064071 | 0.085587 | -0.15957 | 3.1101 | -119.5335 | 3.3341 | 3.1964 | 0.086258 | -119.4567 | -119.3382 | -0.10006 | -122.8205 | 0.088029 | -0.006 | 0.094061 | -122.699 | -122.6775 | 3.289 | 3.3659 | 3.4843 | 3.4674 | -119.7125 | 0.002084 | 0.12358 | 0.1451 | 0.13313 | -122.9226
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0040921 | -0.012305 | 0.004395 | -0.01755 | -0.0048667 | -0.0029805 | 0.01534 | 0.039245 | 0.0085952 | 3.2654 | 3.4079 | 3.1369 | 3.2295 | 3.3018 | 3.4157 | 3.046 | 0.02852 | 0.078197 | -0.065509 | -0.052847 | 0.059493 | 0.090166 | -0.16415 | 3.1193 | -119.5427 | 3.3387 | 3.2101 | 0.090837 | -119.4705 | -119.3565 | -0.090907 | -122.8251 | 0.10176 | 0.007733 | 0.09864 | -122.7127 | -122.6821 | 3.3028 | 3.375 | 3.4889 | 3.4811 | -119.7262 | 0.020395 | 0.13273 | 0.16341 | 0.15144 | -122.9364
|  |  |  | 1.4211e-13 | -0.041529 | -0.00049149 | -0.0036647 | -0.012518 | 0.0041814 | -0.01755 | -0.0046531 | -0.0025533 | 0.015554 | 0.039245 | 0.0085952 | 3.2563 | 3.3987 | 3.1414 | 3.225 | 3.2926 | 3.4065 | 3.0369 | 0.019362 | 0.078197 | -0.065509 | -0.057425 | 0.064071 | 0.090166 | -0.15041 | 3.1376 | -119.5885 | 3.357 | 3.2422 | 0.10457 | -119.5208 | -119.4069 | -0.049704 | -122.8708 | 0.12007 | 0.035199 | 0.084903 | -122.7493 | -122.7233 | 3.3257 | 3.3933 | 3.5072 | 3.4994 | -119.7765 | 0.043283 | 0.16478 | 0.19087 | 0.17891 | -122.9638
|  |  |  | 1.4211e-13 | -0.041743 | -6.4092e-05 | -0.0036647 | -0.012305 | 0.0041814 | -0.01755 | -0.0046531 | -0.0027669 | 0.01534 | 0.039245 | 0.008809 | 3.2517 | 3.3896 | 3.1277 | 3.2204 | 3.288 | 3.4111 | 3.0277 | 0.02852 | 0.073618 | -0.06093 | -0.057425 | 0.059493 | 0.090166 | -0.15499 | 3.0826 | -119.561 | 3.3066 | 3.1826 | 0.099996 | -119.4933 | -119.3703 | -0.10006 | -122.8388 | 0.083452 | -0.005998 | 0.094061 | -122.7219 | -122.6912 | 3.2753 | 3.343 | 3.466 | 3.4445 | -119.7537 | -0.002493 | 0.11442 | 0.1451 | 0.12855 | -122.9364
|  |  |  | 1.4211e-13 | -0.041743 | -0.00049149 | -0.0036647 | -0.012091 | 0.005036 | -0.01755 | -0.0048667 | -0.0023397 | 0.01534 | 0.039245 | 0.0092362 | 3.2471 | 3.385 | 3.1231 | 3.2204 | 3.2834 | 3.4065 | 3.0231 | 0.033099 | 0.073618 | -0.065509 | -0.062004 | 0.064071 | 0.094744 | -0.15041 | 3.133 | -119.561 | 3.357 | 3.233 | 0.099997 | -119.4979 | -119.3749 | -0.040549 | -122.8434 | 0.14296 | 0.044354 | 0.084903 | -122.7173 | -122.6866 | 3.3302 | 3.3933 | 3.5164 | 3.4949 | -119.7582 | 0.047859 | 0.17393 | 0.20461 | 0.18348 | -122.9318
|  |  |  | 1.4211e-13 | -0.041316 | -6.4092e-05 | -0.0036647 | -0.012305 | 0.0041814 | -0.0022892 | -0.0046531 | -0.0025533 | 0.01534 | 0.039245 | 0.008809 | 3.2517 | 3.3758 | 3.1231 | 3.2066 | 3.2834 | 3.3974 | 3.0231 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.054914 | 0.090166 | -0.15957 | 3.1559 | -119.6251 | 3.3845 | 3.2559 | 0.099997 | -119.5483 | -119.4344 | -0.026819 | -122.8892 | 0.16127 | 0.067242 | 0.094061 | -122.7768 | -122.7416 | 3.3394 | 3.4162 | 3.5301 | 3.5086 | -119.8086 | 0.075326 | 0.18766 | 0.22292 | 0.21553 | -122.9913
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0036647 | -0.012518 | 0.0041814 | -0.01755 | -0.0048667 | -0.0025533 | 0.01534 | 0.039245 | 0.008809 | 3.2425 | 3.3758 | 3.114 | 3.1975 | 3.2789 | 3.3928 | 3.0231 | 0.023941 | 0.087354 | -0.06093 | -0.057425 | 0.054914 | 0.085587 | -0.15041 | 3.1238 | -119.6297 | 3.3433 | 3.2147 | 0.09084 | -119.5483 | -119.4344 | -0.049704 | -122.8846 | 0.12465 | 0.039778 | 0.089482 | -122.7722 | -122.7416 | 3.2982 | 3.3796 | 3.4935 | 3.4765 | -119.804 | 0.043283 | 0.15562 | 0.18629 | 0.18806 | -122.9776
|  |  |  | 1.4211e-13 | -0.041743 | -0.00070509 | -0.0034509 | -0.012305 | 0.0041814 | -0.0099192 | -0.0050803 | -0.0027669 | 0.015126 | 0.039459 | 0.0085952 | 3.2425 | 3.3713 | 3.114 | 3.2021 | 3.2697 | 3.3836 | 3.0094 | 0.02852 | 0.082776 | -0.070087 | -0.057425 | 0.064071 | 0.094744 | -0.15957 | 3.101 | -119.5885 | 3.3341 | 3.2055 | 0.10458 | -119.5208 | -119.4069 | -0.068017 | -122.848 | 0.12007 | 0.021466 | 0.089483 | -122.7265 | -122.6958 | 3.2936 | 3.3613 | 3.4752 | 3.4628 | -119.7811 | 0.034128 | 0.15562 | 0.1863 | 0.17433 | -122.9501
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0036647 | -0.012091 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.01534 | 0.039459 | 0.0085952 | 3.2288 | 3.3713 | 3.1002 | 3.1975 | 3.2606 | 3.379 | 3.014 | 0.023941 | 0.087354 | -0.051772 | -0.057425 | 0.059493 | 0.090166 | -0.15041 | 3.1284 | -119.5976 | 3.3433 | 3.2147 | 0.086263 | -119.5346 | -119.4161 | -0.035971 | -122.8525 | 0.13838 | 0.062669 | 0.09864 | -122.7356 | -122.7049 | 3.3119 | 3.375 | 3.4935 | 3.4857 | -119.7811 | 0.057016 | 0.17393 | 0.20461 | 0.2018 | -122.9455
|  |  |  | 1.4211e-13 | -0.041743 | -0.00049149 | -0.0036647 | -0.012305 | 0.0041814 | -0.01755 | -0.0048667 | -0.0025533 | 0.015554 | 0.039459 | 0.008809 | 3.2242 | 3.3575 | 3.1002 | 3.1837 | 3.256 | 3.3699 | 3.0002 | 0.02852 | 0.087354 | -0.065509 | -0.062004 | 0.059493 | 0.099323 | -0.15499 | 3.101 | -119.6205 | 3.3249 | 3.201 | 0.1 | -119.5483 | -119.4344 | -0.054283 | -122.8663 | 0.12923 | 0.035199 | 0.089482 | -122.7448 | -122.7049 | 3.2845 | 3.3567 | 3.4706 | 3.4582 | -119.804 | 0.038704 | 0.1602 | 0.20003 | 0.18806 | -122.9593
|  |  |  | 1.4211e-13 | -0.041957 | -0.00070509 | -0.0038783 | -0.012518 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0027669 | 0.015554 | 0.039459 | 0.008809 | 3.2151 | 3.3621 | 3.0957 | 3.1746 | 3.256 | 3.3653 | 3.0048 | 0.019362 | 0.078197 | -0.06093 | -0.066582 | 0.059493 | 0.094744 | -0.15499 | 3.1238 | -119.6114 | 3.3341 | 3.2147 | 0.090843 | -119.53 | -119.4206 | -0.035972 | -122.8525 | 0.13838 | 0.058089 | 0.094061 | -122.7265 | -122.6912 | 3.2936 | 3.375 | 3.4843 | 3.4811 | -119.7811 | 0.052437 | 0.17851 | 0.21376 | 0.19722 | -122.9409
|  |  |  | 1.4211e-13 | -0.041529 | -0.00027769 | -0.0036647 | -0.012732 | 0.0041814 | -0.0022892 | -0.0048667 | -0.0021259 | 0.015554 | 0.039245 | 0.0083816 | 3.2105 | 3.3529 | 3.0819 | 3.1746 | 3.2468 | 3.3607 | 2.9865 | 0.019362 | 0.078197 | -0.070087 | -0.066582 | 0.054914 | 0.094744 | -0.15957 | 3.0597 | -119.5976 | 3.2837 | 3.1552 | 0.095424 | -119.5254 | -119.4115 | -0.086328 | -122.8388 | 0.092604 | 0.003155 | 0.089483 | -122.7173 | -122.6775 | 3.2478 | 3.3201 | 3.434 | 3.4262 | -119.7857 | 0.00666 | 0.12816 | 0.16799 | 0.15144 | -122.9318
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0036647 | -0.012732 | 0.0039676 | -0.01755 | -0.0048667 | -0.0023397 | 0.015554 | 0.039673 | 0.0090226 | 3.2059 | 3.3484 | 3.0774 | 3.17 | 3.2422 | 3.3607 | 2.9819 | 0.023941 | 0.073618 | -0.065509 | -0.052847 | 0.059493 | 0.094744 | -0.15499 | 3.0552 | -119.6205 | 3.2792 | 3.1506 | 0.095424 | -119.5483 | -119.4298 | -0.081749 | -122.8434 | 0.097183 | 0.007733 | 0.089482 | -122.731 | -122.6958 | 3.2433 | 3.3155 | 3.434 | 3.4216 | -119.8086 | 0.020395 | 0.13273 | 0.16799 | 0.14686 | -122.9455
|  |  |  | 1.4211e-13 | -0.041743 | -0.00049149 | -0.0036647 | -0.012091 | 0.0041814 | -0.01755 | -0.0050803 | -0.0023397 | 0.01534 | 0.039459 | 0.008809 | 3.2013 | 3.3346 | 3.0774 | 3.1609 | 3.2331 | 3.3516 | 2.9682 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.059493 | 0.094744 | -0.15499 | 3.0689 | -119.6526 | 3.302 | 3.1781 | 0.10916 | -119.5803 | -119.4618 | -0.054283 | -122.8708 | 0.12923 | 0.035199 | 0.089482 | -122.7539 | -122.7187 | 3.2616 | 3.3338 | 3.4523 | 3.4353 | -119.8452 | 0.043283 | 0.1602 | 0.19545 | 0.17433 | -122.9684
|  |  |  | 1.4211e-13 | -0.041529 | -0.00070509 | -0.0036647 | -0.012305 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015981 | 0.039886 | 0.008809 | 3.1922 | 3.3301 | 3.0636 | 3.1517 | 3.2239 | 3.3378 | 2.9728 | 0.023941 | 0.078197 | -0.06093 | -0.062004 | 0.064071 | 0.090166 | -0.15499 | 3.0964 | -119.6297 | 3.3158 | 3.1872 | 0.090847 | -119.5575 | -119.4435 | -0.031395 | -122.8434 | 0.14754 | 0.062666 | 0.094061 | -122.7173 | -122.6912 | 3.2753 | 3.3475 | 3.4614 | 3.4536 | -119.8086 | 0.061592 | 0.18767 | 0.21376 | 0.20179 | -122.9364
|  |  |  | 1.4211e-13 | -0.041743 | -0.00070509 | -0.0040921 | -0.012305 | 0.004395 | -0.01755 | -0.0050803 | -0.0025533 | 0.015554 | 0.039459 | 0.008809 | 3.183 | 3.3209 | 3.0636 | 3.1471 | 3.2239 | 3.3378 | 2.9636 | 0.033099 | 0.073618 | -0.070087 | -0.062004 | 0.06865 | 0.094744 | -0.15499 | 3.0597 | -119.6343 | 3.2792 | 3.1597 | 0.1 | -119.5575 | -119.4435 | -0.058861 | -122.8434 | 0.12923 | 0.026043 | 0.084904 | -122.7127 | -122.6866 | 3.2432 | 3.3201 | 3.434 | 3.417 | -119.8178 | 0.034126 | 0.16478 | 0.19087 | 0.16975 | -122.9364
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0038783 | -0.012732 | 0.0041814 | -0.01755 | -0.0050803 | -0.0023397 | 0.014913 | 0.039673 | 0.0090226 | 3.1876 | 3.3209 | 3.059 | 3.1471 | 3.2239 | 3.3333 | 2.9682 | 0.023941 | 0.073618 | -0.065509 | -0.052847 | 0.059493 | 0.094744 | -0.15957 | 3.0277 | -119.648 | 3.2471 | 3.1185 | 0.090848 | -119.5712 | -119.4619 | -0.10006 | -122.848 | 0.08345 | -0.006 | 0.094061 | -122.7356 | -122.7004 | 3.2066 | 3.2834 | 3.3928 | 3.3804 | -119.8269 | 0.006662 | 0.119 | 0.15425 | 0.13313 | -122.9547
|  |  |  | 1.4211e-13 | -0.041529 | -6.4092e-05 | -0.0040921 | -0.012518 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0027669 | 0.014913 | 0.039673 | 0.008809 | 3.1784 | 3.3163 | 3.0545 | 3.1425 | 3.2239 | 3.3241 | 2.9545 | 0.023941 | 0.073618 | -0.065509 | -0.057425 | 0.064071 | 0.099323 | -0.15957 | 3.0414 | -119.6617 | 3.2654 | 3.1414 | 0.10001 | -119.5803 | -119.4802 | -0.072595 | -122.8617 | 0.11092 | 0.021466 | 0.094061 | -122.7402 | -122.7049 | 3.2295 | 3.3109 | 3.4111 | 3.4033 | -119.8498 | 0.02955 | 0.15105 | 0.1863 | 0.16059 | -122.9638
|  |  |  | 1.4211e-13 | -0.041957 | -0.00027769 | -0.0040921 | -0.012305 | 0.0041814 | -0.0099192 | -0.0050803 | -0.0021259 | 0.015554 | 0.039886 | 0.0085952 | 3.1784 | 3.3163 | 3.0453 | 3.1334 | 3.2102 | 3.3241 | 2.959 | 0.023941 | 0.087354 | -0.065509 | -0.052847 | 0.064071 | 0.090166 | -0.15957 | 3.0506 | -119.6571 | 3.27 | 3.1369 | 0.086271 | -119.5803 | -119.4664 | -0.068017 | -122.8434 | 0.11549 | 0.026044 | 0.094061 | -122.7265 | -122.7004 | 3.2249 | 3.3017 | 3.4156 | 3.4079 | -119.8315 | 0.038706 | 0.15562 | 0.18172 | 0.17891 | -122.9501
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0034509 | -0.012305 | 0.0039676 | -0.01755 | -0.0048667 | -0.0025533 | 0.015554 | 0.039459 | 0.008809 | 3.1693 | 3.3072 | 3.0407 | 3.1288 | 3.1964 | 3.3241 | 2.9453 | 0.02852 | 0.073618 | -0.065509 | -0.057425 | 0.073228 | 0.099323 | -0.15499 | 3.0002 | -119.6526 | 3.2242 | 3.0957 | 0.095429 | -119.5849 | -119.4573 | -0.10006 | -122.8388 | 0.083452 | -0.010577 | 0.089482 | -122.7081 | -122.682 | 3.1837 | 3.2514 | 3.379 | 3.3621 | -119.8361 | -0.002493 | 0.12816 | 0.15426 | 0.12855 | -122.9364
|  |  |  | 1.4211e-13 | -0.041957 | -0.00027769 | -0.0038783 | -0.012518 | 0.0046086 | -0.02518 | -0.0050803 | -0.0027669 | 0.01534 | 0.039459 | 0.008809 | 3.1647 | 3.3026 | 3.0361 | 3.1242 | 3.2056 | 3.3104 | 2.9453 | 0.019362 | 0.078197 | -0.070087 | -0.057425 | 0.064071 | 0.094744 | -0.15499 | 3.0185 | -119.6571 | 3.238 | 3.1094 | 0.090851 | -119.5758 | -119.471 | -0.081749 | -122.8388 | 0.092604 | 0.003155 | 0.084904 | -122.7173 | -122.6866 | 3.1975 | 3.2788 | 3.3836 | 3.3758 | -119.8361 | 0.015817 | 0.13731 | 0.16799 | 0.15144 | -122.9364
|  |  |  | 1.4211e-13 | -0.041743 | -0.00049149 | -0.0038783 | -0.012518 | 0.0041814 | -0.0099192 | -0.0046531 | -0.0023397 | 0.015554 | 0.039673 | 0.008809 | 3.1556 | 3.3026 | 3.0361 | 3.1242 | 3.1919 | 3.3012 | 2.9407 | 0.02852 | 0.073618 | -0.06093 | -0.057425 | 0.064071 | 0.085587 | -0.15041 | 3.0597 | -119.6892 | 3.2746 | 3.1552 | 0.09543 | -119.6215 | -119.5122 | -0.031393 | -122.8708 | 0.14754 | 0.058089 | 0.089482 | -122.7493 | -122.7278 | 3.2432 | 3.3109 | 3.4202 | 3.4216 | -119.8727 | 0.061594 | 0.18309 | 0.20461 | 0.19264 | -122.9638
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0036647 | -0.012946 | 0.004395 | -0.0022892 | -0.0052939 | -0.0027669 | 0.014913 | 0.038818 | 0.0090226 | 3.151 | 3.2934 | 3.0316 | 3.1151 | 3.1873 | 3.3012 | 2.927 | 0.033099 | 0.078197 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15957 | 3.0323 | -119.6938 | 3.2563 | 3.1369 | 0.10459 | -119.6215 | -119.5076 | -0.054284 | -122.8617 | 0.13839 | 0.044356 | 0.09864 | -122.7493 | -122.7141 | 3.2204 | 3.2926 | 3.4065 | 3.3987 | -119.8819 | 0.052439 | 0.16478 | 0.20003 | 0.18348 | -122.9684
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0038783 | -0.012518 | 0.004395 | -0.0099192 | -0.0050803 | -0.0025533 | 0.01534 | 0.039459 | 0.0085952 | 3.1418 | 3.2934 | 3.0178 | 3.1105 | 3.1827 | 3.292 | 2.927 | 0.023941 | 0.06904 | -0.065509 | -0.057425 | 0.06865 | 0.085587 | -0.15957 | 3.0094 | -119.6755 | 3.2242 | 3.1002 | 0.090854 | -119.6032 | -119.4939 | -0.077173 | -122.8434 | 0.10634 | 0.016888 | 0.094061 | -122.7173 | -122.7004 | 3.1929 | 3.2651 | 3.3744 | 3.3758 | -119.859 | 0.024972 | 0.15105 | 0.16798 | 0.15144 | -122.9455
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0038783 | -0.012305 | 0.0041814 | -0.0099192 | -0.0050803 | -0.0027669 | 0.015126 | 0.039673 | 0.008809 | 3.1372 | 3.2843 | 3.0133 | 3.1105 | 3.1781 | 3.292 | 2.927 | 0.02852 | 0.073618 | -0.056351 | -0.057425 | 0.059493 | 0.099323 | -0.15499 | 3.0323 | -119.7029 | 3.2425 | 3.1185 | 0.086276 | -119.6353 | -119.5214 | -0.049705 | -122.8708 | 0.13381 | 0.048935 | 0.09864 | -122.7539 | -122.7141 | 3.2158 | 3.2834 | 3.3973 | 3.3896 | -119.8864 | 0.047861 | 0.16478 | 0.20461 | 0.1789 | -122.9684
|  |  |  | 1.4211e-13 | -0.041957 | -0.00027769 | -0.0038783 | -0.012305 | 0.004395 | -0.01755 | -0.0050803 | -0.0025533 | 0.015554 | 0.039886 | 0.0083816 | 3.1372 | 3.2797 | 3.0041 | 3.0876 | 3.1644 | 3.2875 | 2.9224 | 0.02852 | 0.073618 | -0.056351 | -0.057425 | 0.06865 | 0.085587 | -0.15957 | 3.0094 | -119.7167 | 3.2242 | 3.0911 | 0.081697 | -119.6399 | -119.5168 | -0.072595 | -122.8617 | 0.1155 | 0.030624 | 0.10322 | -122.7356 | -122.7187 | 3.1746 | 3.2514 | 3.3744 | 3.3667 | -119.8819 | 0.02955 | 0.15563 | 0.17256 | 0.16059 | -122.9638
|  |  |  | 1.4211e-13 | -0.041957 | -0.00070509 | -0.0036647 | -0.012305 | 0.004395 | -0.01755 | -0.0048667 | -0.0025533 | 0.015126 | 0.039459 | 0.0083816 | 3.1327 | 3.2797 | 2.9995 | 3.0876 | 3.169 | 3.2829 | 2.9087 | 0.023941 | 0.078197 | -0.065509 | -0.052847 | 0.073228 | 0.090166 | -0.15957 | 2.9865 | -119.7167 | 3.2105 | 3.0773 | 0.090856 | -119.6353 | -119.5214 | -0.08175 | -122.8571 | 0.10176 | 0.012311 | 0.094061 | -122.731 | -122.7141 | 3.1654 | 3.2468 | 3.3607 | 3.3575 | -119.8956 | 0.024973 | 0.15105 | 0.16799 | 0.15602 | -122.9638
|  |  |  | 1.4211e-13 | -0.041743 | -0.00049149 | -0.0038783 | -0.012518 | 0.0041814 | -0.01755 | -0.0048667 | -0.0023397 | 0.01534 | 0.039459 | 0.008809 | 3.1235 | 3.2705 | 2.9995 | 3.0876 | 3.1644 | 3.2783 | 2.9041 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.064071 | 0.094744 | -0.15499 | 2.9728 | -119.7075 | 3.1922 | 3.0682 | 0.095435 | -119.6307 | -119.5168 | -0.086326 | -122.8617 | 0.097185 | 0.007735 | 0.094061 | -122.731 | -122.7004 | 3.1563 | 3.2331 | 3.347 | 3.3392 | -119.891 | 0.002083 | 0.13274 | 0.16341 | 0.14686 | -122.9501
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0036647 | -0.012305 | 0.0039676 | -0.0022892 | -0.0048667 | -0.0021259 | 0.015554 | 0.039673 | 0.008809 | 3.1189 | 3.266 | 2.9995 | 3.0876 | 3.1598 | 3.2692 | 2.8949 | 0.02852 | 0.078197 | -0.056351 | -0.057425 | 0.06865 | 0.094744 | -0.16415 | 2.9682 | -119.7121 | 3.1922 | 3.0728 | 0.10459 | -119.6399 | -119.5305 | -0.090907 | -122.8571 | 0.10176 | 0.016891 | 0.1078 | -122.731 | -122.7049 | 3.1608 | 3.2331 | 3.3424 | 3.3392 | -119.9048 | 0.015817 | 0.14189 | 0.16799 | 0.15144 | -122.9638
|  |  |  | 1.4211e-13 | -0.04217 | -6.4092e-05 | -0.0034509 | -0.011877 | 0.0041814 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015554 | 0.039459 | 0.008809 | 3.1098 | 3.2568 | 2.9812 | 3.0739 | 3.1507 | 3.2646 | 2.8949 | 0.023941 | 0.06904 | -0.065509 | -0.057425 | 0.06865 | 0.099323 | -0.16415 | 2.959 | -119.7075 | 3.1739 | 3.0453 | 0.08628 | -119.6307 | -119.5168 | -0.10006 | -122.8388 | 0.088028 | -0.001422 | 0.09864 | -122.7127 | -122.682 | 3.138 | 3.2147 | 3.3287 | 3.3209 | -119.8864 | 0.006662 | 0.13274 | 0.16341 | 0.13313 | -122.9455
|  |  |  | 1.4211e-13 | -0.041743 | -0.00027769 | -0.0034509 | -0.012732 | 0.0041814 | -0.0099192 | -0.0046531 | -0.0027669 | 0.015554 | 0.039673 | 0.0092362 | 3.1006 | 3.2476 | 2.9766 | 3.0647 | 3.1461 | 3.2508 | 2.8858 | 0.02852 | 0.082776 | -0.06093 | -0.062004 | 0.059493 | 0.090166 | -0.15499 | 2.9865 | -119.7762 | 3.2013 | 3.0773 | 0.09086 | -119.6948 | -119.59 | -0.054283 | -122.9029 | 0.12923 | 0.039778 | 0.094061 | -122.7814 | -122.7507 | 3.1654 | 3.2468 | 3.3515 | 3.3483 | -119.9551 | 0.038704 | 0.1602 | 0.19087 | 0.18348 | -122.9959
|  |  |  | 1.4211e-13 | -0.042384 | -6.4092e-05 | -0.0034509 | -0.012305 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0027669 | 0.01534 | 0.039459 | 0.008809 | 3.1006 | 3.2476 | 2.9812 | 3.0601 | 3.1369 | 3.2554 | 2.8766 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.064071 | 0.099323 | -0.15957 | 3.0002 | -119.7899 | 3.2242 | 3.1048 | 0.1046 | -119.7131 | -119.5946 | -0.035974 | -122.9166 | 0.15212 | 0.062666 | 0.09864 | -122.786 | -122.7507 | 3.1837 | 3.2605 | 3.379 | 3.3712 | -119.9734 | 0.057014 | 0.18767 | 0.22292 | 0.20179 | -123.0096
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0036647 | -0.012305 | 0.0041814 | -0.01755 | -0.0046531 | -0.0025533 | 0.01534 | 0.039673 | 0.008809 | 3.096 | 3.2476 | 2.9766 | 3.0601 | 3.1323 | 3.2508 | 2.8858 | 0.023941 | 0.082776 | -0.070087 | -0.057425 | 0.059493 | 0.085587 | -0.15957 | 2.9911 | -119.767 | 3.2013 | 3.0819 | 0.09086 | -119.6948 | -119.5763 | -0.054284 | -122.8846 | 0.12923 | 0.035199 | 0.089483 | -122.7677 | -122.7416 | 3.1654 | 3.2376 | 3.3561 | 3.3529 | -119.9414 | 0.047861 | 0.16478 | 0.19087 | 0.18806 | -122.9867
|  |  |  | 1.4211e-13 | -0.041957 | -0.00027769 | -0.0034509 | -0.012305 | 0.0039676 | -0.01755 | -0.0048667 | -0.0027669 | 0.015554 | 0.039673 | 0.0085952 | 3.096 | 3.2385 | 2.9721 | 3.0464 | 3.1369 | 3.2417 | 2.8766 | 0.023941 | 0.082776 | -0.06093 | -0.062004 | 0.064071 | 0.094744 | -0.15957 | 2.9499 | -119.767 | 3.1693 | 3.0453 | 0.095439 | -119.6765 | -119.5717 | -0.086328 | -122.8754 | 0.097183 | 0.012312 | 0.09864 | -122.7493 | -122.7187 | 3.1196 | 3.2102 | 3.3149 | 3.3117 | -119.9368 | 0.011238 | 0.13731 | 0.16799 | 0.15602 | -122.973
|  |  |  | 1.4211e-13 | -0.041957 | -0.00027769 | -0.0034509 | -0.012518 | 0.0039676 | -0.0022892 | -0.0050803 | -0.0021259 | 0.015554 | 0.039459 | 0.0090226 | 3.0823 | 3.2293 | 2.9721 | 3.051 | 3.1278 | 3.2417 | 2.872 | 0.023941 | 0.078197 | -0.065509 | -0.062004 | 0.059493 | 0.099323 | -0.15957 | 2.9865 | -119.7579 | 3.1967 | 3.0865 | 0.10002 | -119.6811 | -119.5672 | -0.045129 | -122.8708 | 0.13838 | 0.048932 | 0.094061 | -122.7493 | -122.7095 | 3.1654 | 3.2422 | 3.3561 | 3.3438 | -119.9368 | 0.052437 | 0.17393 | 0.21376 | 0.19264 | -122.9684
|  |  |  | 1.4211e-13 | -0.04217 | -0.00049149 | -0.0038783 | -0.012305 | 0.0041814 | -0.01755 | -0.0046531 | -0.0027669 | 0.01534 | 0.039673 | 0.0083816 | 3.0823 | 3.2202 | 2.9537 | 3.0418 | 3.1232 | 3.2325 | 2.8537 | 0.019362 | 0.078197 | -0.065509 | -0.057425 | 0.06865 | 0.090166 | -0.15499 | 2.9407 | -119.767 | 3.1693 | 3.0407 | 0.10002 | -119.6857 | -119.5763 | -0.068016 | -122.8663 | 0.10634 | 0.021466 | 0.089482 | -122.7402 | -122.7187 | 3.1288 | 3.2102 | 3.3195 | 3.3071 | -119.9551 | 0.02955 | 0.15563 | 0.17714 | 0.16517 | -122.9638
|  |  |  | 1.4211e-13 | -0.04217 | -0.00027769 | -0.0036647 | -0.012305 | 0.0041814 | 0.0053413 | -0.0050803 | -0.0027669 | 0.01534 | 0.039673 | 0.008809 | 3.0777 | 3.2156 | 2.9446 | 3.0372 | 3.114 | 3.2371 | 2.8583 | 0.02852 | 0.078197 | -0.06093 | -0.066582 | 0.064071 | 0.099323 | -0.15499 | 2.9544 | -119.7716 | 3.1739 | 3.0407 | 0.086285 | -119.6948 | -119.5717 | -0.058861 | -122.8754 | 0.12465 | 0.0352 | 0.094061 | -122.7448 | -122.7095 | 3.1334 | 3.2102 | 3.3332 | 3.3117 | -119.9505 | 0.029548 | 0.1602 | 0.19545 | 0.17433 | -122.9638
|  |  |  | 1.4211e-13 | -0.04217 | -0.00027769 | -0.0034509 | -0.012091 | 0.004395 | -0.01755 | -0.0048667 | -0.0027669 | 0.015554 | 0.039673 | 0.0085952 | 3.0686 | 3.2156 | 2.9446 | 3.0372 | 3.1003 | 3.2279 | 2.8491 | 0.023941 | 0.073618 | -0.070087 | -0.066582 | 0.064071 | 0.090166 | -0.15957 | 2.9178 | -119.7167 | 3.1372 | 3.0132 | 0.095443 | -119.6536 | -119.526 | -0.090905 | -122.8205 | 0.092606 | -0.001422 | 0.089483 | -122.6898 | -122.6637 | 3.1059 | 3.169 | 3.2966 | 3.2843 | -119.9048 | 0.002083 | 0.13274 | 0.15883 | 0.14228 | -122.9135
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0034509 | -0.012305 | 0.003754 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015767 | 0.039673 | 0.008809 | 3.0686 | 3.2156 | 2.9446 | 3.0281 | 3.1003 | 3.2188 | 2.84 | 0.023941 | 0.082776 | -0.06093 | -0.052847 | 0.064071 | 0.094744 | -0.15041 | 2.9453 | -119.7991 | 3.1739 | 3.0499 | 0.1046 | -119.7269 | -119.6084 | -0.045126 | -122.88 | 0.12923 | 0.044356 | 0.089482 | -122.7631 | -122.7324 | 3.1334 | 3.2056 | 3.3241 | 3.3209 | -119.9872 | 0.052439 | 0.16936 | 0.20003 | 0.18806 | -122.9776
|  |  |  | 1.4211e-13 | -0.04217 | -0.00049149 | -0.0034509 | -0.012518 | 0.004395 | -0.0099192 | -0.0046531 | -0.0025533 | 0.01534 | 0.039673 | 0.0085952 | 3.0548 | 3.2064 | 2.9263 | 3.0189 | 3.1094 | 3.2096 | 2.84 | 0.023941 | 0.078197 | -0.06093 | -0.057425 | 0.06865 | 0.090166 | -0.15957 | 2.9544 | -119.8036 | 3.1693 | 3.0407 | 0.086287 | -119.7131 | -119.6129 | -0.045129 | -122.88 | 0.13838 | 0.053511 | 0.09864 | -122.7539 | -122.7324 | 3.1334 | 3.2239 | 3.3241 | 3.3209 | -119.9826 | 0.057016 | 0.18309 | 0.20461 | 0.19264 | -122.9821
|  |  |  | 1.4211e-13 | -0.042384 | -6.4092e-05 | -0.0038783 | -0.012518 | 0.004395 | -0.0022892 | -0.0046531 | -0.0025533 | 0.015554 | 0.039673 | 0.0085952 | 3.0548 | 3.2064 | 2.9263 | 3.0235 | 3.1049 | 3.2005 | 2.8308 | 0.023941 | 0.073618 | -0.056351 | -0.052847 | 0.064071 | 0.090166 | -0.15499 | 2.8995 | -119.7533 | 3.1235 | 2.9949 | 0.095445 | -119.6719 | -119.5763 | -0.086326 | -122.8296 | 0.092606 | 0.012314 | 0.09864 | -122.7127 | -122.6866 | 3.0922 | 3.1735 | 3.2691 | 3.2751 | -119.946 | 0.015818 | 0.13274 | 0.15883 | 0.14228 | -122.9318
|  |  |  | 1.4211e-13 | -0.04217 | -0.00049149 | -0.0036647 | -0.012518 | 0.003754 | -0.01755 | -0.0048667 | -0.0025533 | 0.015126 | 0.039886 | 0.0085952 | 3.0457 | 3.1927 | 2.9354 | 3.0143 | 3.0866 | 3.2005 | 2.84 | 0.033099 | 0.078197 | -0.065509 | -0.048268 | 0.054914 | 0.085587 | -0.15499 | 2.9407 | -119.7945 | 3.1464 | 3.0361 | 0.095444 | -119.7223 | -119.6084 | -0.054283 | -122.8571 | 0.13381 | 0.035199 | 0.089482 | -122.7539 | -122.7233 | 3.1151 | 3.1873 | 3.3012 | 3.2934 | -119.9689 | 0.05244 | 0.15562 | 0.18629 | 0.17891 | -122.9638
|  |  |  | 1.4211e-13 | -0.041957 | -0.00049149 | -0.0034509 | -0.011877 | 0.0039676 | -0.01755 | -0.0050803 | -0.0027669 | 0.01534 | 0.039886 | 0.008809 | 3.0457 | 3.1835 | 2.9171 | 3.0006 | 3.0866 | 3.2005 | 2.8217 | 0.02852 | 0.078197 | -0.06093 | -0.052847 | 0.059493 | 0.094744 | -0.15041 | 2.9178 | -119.8449 | 3.1418 | 3.0132 | 0.095447 | -119.7589 | -119.645 | -0.054282 | -122.8983 | 0.12465 | 0.0352 | 0.089482 | -122.786 | -122.7507 | 3.0967 | 3.1827 | 3.2966 | 3.2797 | -120.0238 | 0.043283 | 0.15562 | 0.19087 | 0.17433 | -122.9959
|  |  |  | 1.4211e-13 | -0.04217 | -6.4092e-05 | -0.0034509 | -0.012305 | 0.0041814 | -0.0099192 | -0.0050803 | -0.0025533 | 0.015126 | 0.039886 | 0.0085952 | 3.0274 | 3.1835 | 2.908 | 3.0006 | 3.082 | 3.1822 | 2.8217 | 0.02852 | 0.078197 | -0.065509 | -0.052847 | 0.064071 | 0.090166 | -0.14583 | 2.9132 | -119.8037 | 3.1189 | 2.9995 | 0.08629 | -119.7223 | -119.6221 | -0.05428 | -122.8571 | 0.12007 | 0.026044 | 0.080324 | -122.7402 | -122.7141 | 3.0922 | 3.1735 | 3.2737 | 3.2751 | -119.9826 | 0.038706 | 0.15562 | 0.18172 | 0.16975 | -122.9501
|  |  |  | 1.4211e-13 | -0.042384 | -0.00070509 | -0.0038783 | -0.012305 | 0.004395 | -0.0099192 | -0.0048667 | -0.0023397 | 0.015126 | 0.039673 | 0.008809 | 3.0365 | 3.1835 | 2.908 | 3.0006 | 3.082 | 3.1867 | 2.8171 | 0.023941 | 0.082776 | -0.06093 | -0.057425 | 0.064071 | 0.085587 | -0.15957 | 2.8949 | -119.7991 | 3.1143 | 2.9858 | 0.090869 | -119.7177 | -119.6129 | -0.08175 | -122.8571 | 0.10176 | 0.01689 | 0.09864 | -122.7356 | -122.7141 | 3.0784 | 3.1598 | 3.2646 | 3.2614 | -119.9826 | 0.020395 | 0.14189 | 0.16341 | 0.1606 | -122.9593
|  |  |  | 1.4211e-13 | -0.04217 | -0.00027769 | -0.0038783 | -0.012305 | 0.0039676 | -0.01755 | -0.0048667 | -0.0023397 | 0.01534 | 0.039459 | 0.0085952 | 3.0365 | 3.1835 | 2.908 | 3.0006 | 3.0728 | 3.1867 | 2.8171 | 0.02852 | 0.078197 | -0.06093 | -0.057425 | 0.064071 | 0.094744 | -0.15957 | 2.9315 | -119.7991 | 3.151 | 3.0224 | 0.090869 | -119.7269 | -119.6129 | -0.045129 | -122.8571 | 0.14296 | 0.053511 | 0.09864 | -122.7356 | -122.7049 | 3.115 | 3.1873 | 3.3012 | 3.298 | -119.9826 | 0.057016 | 0.17851 | 0.20919 | 0.19264 | -122.9593
|  |  |  | 1.4211e-13 | -0.042598 | -0.00049149 | -0.0034509 | -0.012518 | 0.0041814 | -0.01755 | -0.0046531 | -0.0027669 | 0.015554 | 0.039886 | 0.0090226 | 3.0136 | 3.1698 | 2.8896 | 2.9823 | 3.0637 | 3.173 | 2.8033 | 0.02852 | 0.082776 | -0.06093 | -0.057425 | 0.064071 | 0.085587 | -0.15499 | 2.8995 | -119.7991 | 3.1098 | 2.9858 | 0.086293 | -119.7177 | -119.6084 | -0.058861 | -122.8388 | 0.12465 | 0.0352 | 0.094061 | -122.7173 | -122.6958 | 3.0784 | 3.1598 | 3.2691 | 3.2659 | -119.978 | 0.038705 | 0.1602 | 0.18172 | 0.17891 | -122.9364
|  |  |  | 1.4211e-13 | -0.04217 | -0.00070509 | -0.0036647 | -0.012305 | 0.0039676 | -0.01755 | -0.0048667 | -0.0029805 | 0.01534 | 0.039673 | 0.008809 | 3.0228 | 3.1652 | 2.8896 | 2.9731 | 3.0591 | 3.1684 | 2.7988 | 0.02852 | 0.078197 | -0.065509 | -0.052847 | 0.064071 | 0.099323 | -0.15499 | 2.8995 | -119.8174 | 3.1235 | 2.9903 | 0.090871 | -119.7314 | -119.6221 | -0.054283 | -122.8434 | 0.12923 | 0.035199 | 0.089482 | -122.7265 | -122.6912 | 3.0738 | 3.1598 | 3.2691 | 3.2659 | -119.9918 | 0.047861 | 0.16478 | 0.20003 | 0.17891 | -122.9455
|  |  |  | 1.4211e-13 | -0.041957 | -0.00070509 | -0.0036647 | -0.012518 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015126 | 0.039673 | 0.008809 | 3.0136 | 3.1652 | 2.8896 | 2.9823 | 3.0499 | 3.1547 | 2.7942 | 0.02852 | 0.078197 | -0.056351 | -0.052847 | 0.064071 | 0.094744 | -0.15957 | 2.8949 | -119.8357 | 3.1143 | 2.9903 | 0.09545 | -119.7681 | -119.6633 | -0.058862 | -122.8708 | 0.12923 | 0.044357 | 0.10322 | -122.7539 | -122.7232 | 3.083 | 3.1506 | 3.2554 | 3.2659 | -120.0238 | 0.047861 | 0.16478 | 0.19545 | 0.17891 | -122.9776
|  |  |  | 1.4211e-13 | -0.04217 | -0.00049149 | -0.0036647 | -0.012518 | 0.0041814 | -0.02518 | -0.0050803 | -0.0023397 | 0.015554 | 0.039459 | 0.008809 | 3.0045 | 3.1652 | 2.8851 | 2.9777 | 3.0499 | 3.1684 | 2.7988 | 0.023941 | 0.078197 | -0.065509 | -0.052847 | 0.059493 | 0.094744 | -0.15499 | 2.9041 | -119.8403 | 3.1098 | 2.9903 | 0.086293 | -119.7681 | -119.6496 | -0.049705 | -122.8708 | 0.12923 | 0.039777 | 0.089482 | -122.7585 | -122.7232 | 3.083 | 3.1552 | 3.2737 | 3.2705 | -120.0192 | 0.052439 | 0.16478 | 0.20003 | 0.18348 | -122.973
|  |  |  | 1.4211e-13 | -0.042384 | -0.00027769 | -0.0036647 | -0.012305 | 0.003754 | -0.01755 | -0.0048667 | -0.0021259 | 0.015554 | 0.039673 | 0.008809 | 3.009 | 3.1515 | 2.8759 | 2.9731 | 3.0408 | 3.1593 | 2.785 | 0.023941 | 0.078197 | -0.056351 | -0.052847 | 0.073228 | 0.099323 | -0.15957 | 2.9269 | -119.8494 | 3.151 | 3.0178 | 0.090873 | -119.7818 | -119.6633 | -0.017663 | -122.8754 | 0.16585 | 0.085556 | 0.10322 | -122.7493 | -122.7232 | 3.115 | 3.1827 | 3.3012 | 3.2934 | -120.0375 | 0.08906 | 0.21514 | 0.24123 | 0.2201 | -122.9821
|  |  |  | 1.4211e-13 | -0.042384 | -0.00049149 | -0.0038783 | -0.012732 | 0.0041814 | -0.0099192 | -0.0046531 | -0.0025533 | 0.015554 | 0.039886 | 0.0083816 | 2.9999 | 3.1423 | 2.8713 | 2.9594 | 3.0362 | 3.141 | 2.7667 | 0.023941 | 0.06904 | -0.065509 | -0.052847 | 0.064071 | 0.094744 | -0.15041 | 2.8262 | -119.7853 | 3.0594 | 2.9308 | 0.10461 | -119.7086 | -119.6038 | -0.090903 | -122.7976 | 0.08345 | -0.006 | 0.084903 | -122.6807 | -122.65 | 3.0189 | 3.0957 | 3.2005 | 3.2018 | -119.978 | 0.006662 | 0.12358 | 0.15425 | 0.12855 | -122.8952
|  |  |  | 1.4211e-13 | -0.042598 | -0.00027769 | -0.0038783 | -0.012518 | 0.0041814 | -0.0022892 | -0.0052939 | -0.0025533 | 0.015554 | 0.039673 | 0.0083816 | 2.9862 | 3.1469 | 2.8668 | 2.9548 | 3.0316 | 3.1501 | 2.7621 | 0.019362 | 0.078197 | -0.065509 | -0.057425 | 0.06865 | 0.094744 | -0.16415 | 2.8628 | -119.8723 | 3.0869 | 2.9675 | 0.10461 | -119.7955 | -119.677 | -0.063441 | -122.8846 | 0.12007 | 0.035199 | 0.09864 | -122.7585 | -122.7324 | 3.0555 | 3.1323 | 3.2508 | 3.2476 | -120.065 | 0.043283 | 0.16936 | 0.19545 | 0.17891 | -122.9913
|  |  |  | 1.4211e-13 | -0.042811 | -0.00027769 | -0.0034509 | -0.012091 | 0.0041814 | -0.0099192 | -0.0046531 | -0.0029805 | 0.015554 | 0.039886 | 0.0083816 | 2.9907 | 3.1332 | 2.8622 | 2.9502 | 3.0316 | 3.1455 | 2.7621 | 0.019362 | 0.082776 | -0.065509 | -0.057425 | 0.06865 | 0.099323 | -0.15041 | 2.8537 | -119.8494 | 3.0823 | 2.9537 | 0.10003 | -119.7681 | -119.6542 | -0.058859 | -122.8571 | 0.11091 | 0.026044 | 0.084903 | -122.731 | -122.7004 | 3.0418 | 3.1232 | 3.2371 | 3.2247 | -120.0375 | 0.034128 | 0.1602 | 0.19088 | 0.17433 | -122.9501
|  |  |  | 1.4211e-13 | -0.042598 | -0.00027769 | -0.0038783 | -0.012305 | 0.0039676 | -0.01755 | -0.0048667 | -0.0025533 | 0.015126 | 0.039032 | 0.0085952 | 2.977 | 3.1332 | 2.853 | 2.9411 | 3.0133 | 3.1364 | 2.7621 | 0.023941 | 0.082776 | -0.065509 | -0.052847 | 0.059493 | 0.1039 | -0.15957 | 2.84 | -119.8677 | 3.0548 | 2.9308 | 0.090877 | -119.7955 | -119.6725 | -0.08175 | -122.8617 | 0.10176 | 0.012311 | 0.094061 | -122.7493 | -122.7049 | 3.0189 | 3.0911 | 3.2142 | 3.211 | -120.0467 | 0.024973 | 0.13731 | 0.18172 | 0.1606 | -122.9684
|  |  |  | 1.4211e-13 | -0.042384 | -0.00027769 | -0.0034509 | -0.012518 | 0.0041814 | -0.01755 | -0.0042257 | -0.0025533 | 0.015126 | 0.039673 | 0.0085952 | 2.9724 | 3.1286 | 2.8484 | 2.9319 | 3.0179 | 3.1364 | 2.7576 | 0.023941 | 0.078197 | -0.056351 | -0.057425 | 0.06865 | 0.094744 | -0.15957 | 2.8354 | -119.8952 | 3.0502 | 2.9263 | 0.090878 | -119.8093 | -119.6908 | -0.08175 | -122.8846 | 0.10176 | 0.021469 | 0.10322 | -122.7585 | -122.7324 | 3.0098 | 3.0957 | 3.2142 | 3.2064 | -120.0696 | 0.020395 | 0.14647 | 0.17256 | 0.15602 | -122.9867
|  |  |  | 1.4211e-13 | -0.042384 | -6.4092e-05 | -0.0036647 | -0.012091 | 0.004395 | -0.0022892 | -0.0050803 | -0.0027669 | 0.014913 | 0.039673 | 0.0083816 | 2.9724 | 3.1194 | 2.8576 | 2.9457 | 3.0041 | 3.1318 | 2.753 | 0.023941 | 0.082776 | -0.06093 | -0.052847 | 0.054914 | 0.085587 | -0.15957 | 2.8125 | -119.8586 | 3.0319 | 2.9171 | 0.10461 | -119.8001 | -119.6725 | -0.10006 | -122.8571 | 0.08345 | -0.001421 | 0.09864 | -122.7493 | -122.7187 | 3.0052 | 3.0636 | 3.1913 | 3.1789 | -120.0513 | 0.006662 | 0.11442 | 0.1451 | 0.14228 | -122.9638
|  |  |  | 1.4211e-13 | -0.04217 | -0.00070509 | -0.0036647 | -0.012518 | 0.0039676 | -0.01755 | -0.0046531 | -0.0023397 | 0.01534 | 0.039459 | 0.0085952 | 2.9633 | 3.1149 | 2.8393 | 2.9319 | 3.0087 | 3.1226 | 2.7484 | 0.023941 | 0.073618 | -0.06093 | -0.052847 | 0.059493 | 0.090166 | -0.15499 | 2.8537 | -119.8952 | 3.0686 | 2.9446 | 0.090879 | -119.8184 | -119.7045 | -0.049705 | -122.88 | 0.12923 | 0.044356 | 0.094061 | -122.7677 | -122.737 | 3.0372 | 3.114 | 3.2279 | 3.2201 | -120.0787 | 0.052439 | 0.16478 | 0.19545 | 0.1789 | -122.9821
|  |  |  | 1.4211e-13 | -0.042384 | -0.00027769 | -0.0038783 | -0.012518 | 0.004395 | -0.0099192 | -0.0048667 | -0.0025533 | 0.01534 | 0.039886 | 0.008809 | 2.9587 | 3.1149 | 2.8393 | 2.9274 | 2.995 | 3.1181 | 2.7484 | 0.023941 | 0.073618 | -0.06093 | -0.057425 | 0.064071 | 0.094744 | -0.15957 | 2.8125 | -119.8586 | 3.0228 | 2.9034 | 0.090879 | -119.791 | -119.6679 | -0.095483 | -122.8434 | 0.088028 | 0.003157 | 0.09864 | -122.7219 | -122.6912 | 2.9914 | 3.0591 | 3.1821 | 3.1789 | -120.0375 | 0.006662 | 0.12816 | 0.15883 | 0.13771 | -122.9455
|  |  |  | 1.4211e-13 | -0.042598 | -0.00070509 | -0.0036647 | -0.012518 | 0.0039676 | -0.0099192 | -0.0048667 | -0.0025533 | 0.015126 | 0.039673 | 0.0083816 | 2.9541 | 3.1149 | 2.8393 | 2.9228 | 2.9904 | 3.1089 | 2.7347 | 0.02852 | 0.082776 | -0.065509 | -0.057425 | 0.073228 | 0.094744 | -0.16415 | 2.8308 | -119.8494 | 3.0502 | 2.9354 | 0.10462 | -119.7818 | -119.6633 | -0.068019 | -122.8296 | 0.12465 | 0.030621 | 0.09864 | -122.699 | -122.6775 | 3.0189 | 3.0865 | 3.205 | 3.211 | -120.0376 | 0.038705 | 0.16936 | 0.19087 | 0.17891 | -122.9364
|  |  |  | 1.4211e-13 | -0.042598 | -0.00049149 | -0.0034509 | -0.012518 | 0.0039676 | -0.01755 | -0.0048667 | -0.0025533 | 0.01534 | 0.039459 | 0.0085952 | 2.9587 | 3.1149 | 2.8255 | 2.9228 | 3.0041 | 3.1043 | 2.7347 | 0.02852 | 0.073618 | -0.06093 | -0.057425 | 0.064071 | 0.090166 | -0.15041 | 2.8354 | -119.9135 | 3.0594 | 2.9263 | 0.09088 | -119.8322 | -119.732 | -0.049704 | -122.8937 | 0.12923 | 0.039778 | 0.089482 | -122.7722 | -122.7461 | 3.0235 | 3.1048 | 3.205 | 3.2156 | -120.1016 | 0.043283 | 0.16478 | 0.19087 | 0.17433 | -122.9867
|  |  |  | 1.4211e-13 | -0.042384 | -0.00027769 | -0.0038783 | -0.012305 | 0.0041814 | -0.01755 | -0.0050803 | -0.0023397 | 0.015554 | 0.039886 | 0.0083816 | 2.945 | 3.1057 | 2.8255 | 2.9182 | 2.9904 | 3.1089 | 2.7347 | 0.019362 | 0.078197 | -0.056351 | -0.062004 | 0.06865 | 0.099323 | -0.15499 | 2.8125 | -119.8586 | 3.0228 | 2.9034 | 0.09088 | -119.7864 | -119.6679 | -0.077171 | -122.8388 | 0.097182 | 0.021469 | 0.09864 | -122.7081 | -122.6775 | 2.996 | 3.0682 | 3.1867 | 3.1835 | -120.0421 | 0.015816 | 0.14647 | 0.17714 | 0.15602 | -122.9318
|  |  |  | 1.4211e-13 | -0.04217 | -0.00049149 | -0.0036647 | -0.012305 | 0.0039676 | -0.01755 | -0.0050803 | -0.0027669 | 0.01534 | 0.039459 | 0.0085952 | 2.945 | 3.0965 | 2.8164 | 2.909 | 2.9858 | 3.0997 | 2.7255 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.064071 | 0.094744 | -0.15957 | 2.7988 | -119.909 | 3.0182 | 2.8896 | 0.090882 | -119.8322 | -119.7182 | -0.086328 | -122.8754 | 0.097183 | 0.007733 | 0.094061 | -122.7539 | -122.7232 | 2.9823 | 3.0591 | 3.173 | 3.1698 | -120.0925 | 0.015817 | 0.13731 | 0.16799 | 0.15602 | -122.9776
|  |  |  | 1.4211e-13 | -0.04217 | -0.00070509 | -0.0036647 | -0.012518 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0023397 | 0.015126 | 0.039459 | 0.0085952 | 2.9404 | 3.0828 | 2.821 | 2.9045 | 2.9721 | 3.0952 | 2.7209 | 0.037677 | 0.073618 | -0.070087 | -0.062004 | 0.073228 | 0.085587 | -0.16415 | 2.7759 | -119.8723 | 2.9953 | 2.8759 | 0.10004 | -119.8047 | -119.6816 | -0.10922 | -122.8388 | 0.092609 | -0.015155 | 0.094062 | -122.7036 | -122.6912 | 2.9594 | 3.027 | 3.1501 | 3.1377 | -120.0559 | -0.007072 | 0.12816 | 0.14052 | 0.12855 | -122.9409
|  |  |  | 1.4211e-13 | -0.042598 | -0.00027769 | -0.0036647 | -0.012518 | 0.0039676 | -0.0022892 | -0.0048667 | -0.0023397 | 0.01534 | 0.0401 | 0.0083816 | 2.9358 | 3.0828 | 2.8164 | 2.8953 | 2.9812 | 3.0814 | 2.7118 | 0.02852 | 0.073618 | -0.070087 | -0.062004 | 0.054914 | 0.094744 | -0.15957 | 2.8125 | -119.9227 | 3.0365 | 2.9171 | 0.10462 | -119.8368 | -119.7366 | -0.058862 | -122.88 | 0.12923 | 0.030621 | 0.089483 | -122.7631 | -122.7232 | 2.996 | 3.0819 | 3.1821 | 3.1835 | -120.1062 | 0.038704 | 0.15562 | 0.19545 | 0.17433 | -122.9776
|  |  |  | 1.4211e-13 | -0.042384 | -0.00070509 | -0.0038783 | -0.012091 | 0.004395 | -0.02518 | -0.0048667 | -0.0023397 | 0.015554 | 0.039886 | 0.0083816 | 2.9312 | 3.0828 | 2.8072 | 2.8907 | 2.9629 | 3.0814 | 2.7072 | 0.023941 | 0.073618 | -0.056351 | -0.057425 | 0.06865 | 0.094744 | -0.16415 | 2.7942 | -119.9044 | 3.0182 | 2.8942 | 0.10004 | -119.8322 | -119.7137 | -0.077174 | -122.8525 | 0.11092 | 0.030624 | 0.1078 | -122.7265 | -122.7004 | 2.9777 | 3.0499 | 3.1684 | 3.1698 | -120.0879 | 0.02955 | 0.15563 | 0.18172 | 0.16059 | -122.9593
|  |  |  | 1.4211e-13 | -0.042598 | -0.00070509 | -0.0036647 | -0.012732 | 0.0039676 | -0.0099192 | -0.0048667 | -0.0023397 | 0.01534 | 0.039886 | 0.0085952 | 2.9266 | 3.0782 | 2.8027 | 2.8907 | 2.9675 | 3.0723 | 2.7118 | 0.023941 | 0.082776 | -0.056351 | -0.057425 | 0.059493 | 0.090166 | -0.16415 | 2.8216 | -119.9135 | 3.0365 | 2.9125 | 0.090884 | -119.8368 | -119.732 | -0.054286 | -122.8617 | 0.1338 | 0.053512 | 0.1078 | -122.7448 | -122.7141 | 3.0006 | 3.0774 | 3.1821 | 3.1881 | -120.0925 | 0.052438 | 0.16936 | 0.20003 | 0.19264 | -122.9684
|  |  |  | 1.4211e-13 | -0.042384 | -0.00027769 | -0.0038783 | -0.012518 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0023397 | 0.01534 | 0.0401 | 0.008809 | 2.9037 | 3.0599 | 2.7843 | 2.877 | 2.9492 | 3.0631 | 2.6843 | 0.019362 | 0.078197 | -0.06093 | -0.057425 | 0.054914 | 0.090166 | -0.15957 | 2.7575 | -119.909 | 2.977 | 2.8576 | 0.10005 | -119.8368 | -119.7228 | -0.086328 | -122.8434 | 0.092604 | 0.012312 | 0.09864 | -122.731 | -122.6958 | 2.9502 | 3.0224 | 3.1364 | 3.1332 | -120.1017 | 0.015817 | 0.12816 | 0.16341 | 0.15144 | -122.9455
|  |  |  | 1.4211e-13 | -0.042598 | -6.4092e-05 | -0.0036647 | -0.012518 | 0.0041814 | -0.01755 | -0.0050803 | -0.0025533 | 0.01534 | 0.039673 | 0.0083816 | 2.9037 | 3.0508 | 2.7752 | 2.8633 | 2.9446 | 3.0585 | 2.6797 | 0.023941 | 0.082776 | -0.065509 | -0.057425 | 0.059493 | 0.090166 | -0.15499 | 2.785 | -119.9639 | 3.009 | 2.8805 | 0.095466 | -119.8825 | -119.7686 | -0.049705 | -122.8846 | 0.12923 | 0.039777 | 0.089482 | -122.7677 | -122.737 | 2.9685 | 3.0499 | 3.1638 | 3.156 | -120.1474 | 0.047861 | 0.16478 | 0.19545 | 0.18806 | -122.9821
|  |  |  | 1.4211e-13 | -0.042384 | -0.00070509 | -0.0036647 | -0.012305 | 0.0039676 | -0.01755 | -0.0050803 | -0.0027669 | 0.015126 | 0.039886 | 0.0085952 | 2.8809 | 3.037 | 2.7614 | 2.8495 | 2.9309 | 3.0402 | 2.6614 | 0.023941 | 0.073618 | -0.06093 | -0.052847 | 0.073228 | 0.090166 | -0.15499 | 2.7484 | -119.9456 | 2.9678 | 2.8484 | 0.10005 | -119.8642 | -119.7549 | -0.068016 | -122.848 | 0.11092 | 0.026045 | 0.094061 | -122.7219 | -122.7049 | 2.9365 | 3.0178 | 3.1272 | 3.124 | -120.1337 | 0.034128 | 0.1602 | 0.17714 | 0.16059 | -122.9501
|  |  |  | 1.4211e-13 | -0.043025 | -0.00027769 | -0.0034509 | -0.012732 | 0.0041814 | -0.0099192 | -0.0048667 | -0.0027669 | 0.01534 | 0.039886 | 0.008809 | 2.8717 | 3.0233 | 2.7569 | 2.8449 | 2.9263 | 3.0311 | 2.6522 | 0.023941 | 0.082776 | -0.06093 | -0.052847 | 0.054914 | 0.094744 | -0.15041 | 2.7392 | -119.9593 | 2.9587 | 2.8438 | 0.10463 | -119.878 | -119.7732 | -0.063437 | -122.8571 | 0.11092 | 0.026045 | 0.089482 | -122.7493 | -122.7095 | 2.9319 | 3.0133 | 3.118 | 3.1103 | -120.152 | 0.034128 | 0.14189 | 0.18172 | 0.16975 | -122.9547

## Thermal Data
Fire Time | A Position - Middle | C Position - 3' | C Position - Middle | C Position - 7'
-0.4021 | 3.6409 | 3.9559 | 4.556 | 3.9284
0.5979 | 3.738 | 3.9611 | 4.5507 | 3.941
1.5979 | 3.6475 | 3.9573 | 4.55 | 3.9362
2.5979 | 3.7 | 3.963 | 4.5479 | 3.9425
3.5979 | 3.7405 | 3.9643 | 4.5597 | 3.9425
4.5979 | 3.688 | 3.9554 | 4.5687 | 3.9475
5.5979 | 4.073 | 3.9576 | 4.5793 | 3.9766
6.5979 | 4.842 | 3.9645 | 4.6666 | 3.9978
7.5979 | 8.5275 | 4.8342 | 5.3208 | 4.8484
8.5979 | 13.596 | 4.9594 | 5.4494 | 4.8516
9.5979 | 18.2062 | 5.2154 | 5.5669 | 5.0278
10.5979 | 23.4352 | 5.6184 | 5.69 | 5.2665
11.5979 | 27.9588 | 6.6476 | 6.5995 | 6.7185
12.5979 | 34.218 | 7.5121 | 7.3129 | 9.2251
13.5979 | 51.8333 | 9.2282 | 9.3704 | 10.448
14.5979 | 61.1124 | 11.1273 | 10.614 | 11.2809
15.5979 | 67.5981 | 13.3912 | 12.2414 | 13.3954
16.5979 | 74.0906 | 15.7536 | 13.9482 | 15.1328
17.5979 | 83.4092 | 18.057 | 15.9907 | 17.8928
18.5979 | 90.108 | 20.8512 | 18.6105 | 20.8153
19.5979 | 98.175 | 23.2607 | 20.6018 | 23.2965
20.5979 | 126.0742 | 25.8278 | 23.0388 | 25.4147
21.5979 | 156.36 | 27.6436 | 25.4599 | 28.2342
22.5979 | 176.0744 | 29.0546 | 27.9818 | 31.1758
23.5979 | 186.8289 | 32.1857 | 29.3319 | 32.6363
24.5979 | 219.811 | 34.6637 | 31.2022 | 35.6405
25.5979 | 218.1273 | 36.2952 | 33.5293 | 38.2957
26.5979 | 225.4827 | 38.0457 | 35.4005 | 40.2245
27.5979 | 230.3719 | 40.5804 | 37.2474 | 43.5067
28.5979 | 232.3997 | 42.139 | 39.8373 | 45.7267
29.5979 | 253.7704 | 44.9273 | 42.1458 | 46.9069
30.5979 | 278.502 | 47.4585 | 44.1442 | 48.7023
31.5979 | 319.8576 | 49.0158 | 46.3836 | 50.8567
32.5979 | 345.0325 | 50.9928 | 48.2978 | 53.5761
33.5979 | 375.1523 | 52.9725 | 51.1965 | 55.5443
34.5979 | 401.8273 | 55.5081 | 53.0646 | 57.656
35.5979 | 438.6553 | 58.3375 | 55.1507 | 60.2042
36.5979 | 461.7209 | 61.3675 | 48.4112 | 63.4692
37.5979 | 487.3701 | 64.5942 | 52.2764 | 66.3449
38.5979 | 512.5745 | 66.6963 | 62.3377 | 68.9969
39.5979 | 517.2264 | 69.2637 | 64.723 | 71.1486
40.5979 | 552.9983 | 71.4965 | 67.5776 | 74.0782
41.5979 | 573.6097 | 74.1431 | 69.9879 | 76.5935
42.5979 | 591.8185 | 75.9156 | 73.1378 | 78.3769
43.5979 | 589.2465 | 76.907 | 75.4456 | 80.1639
44.5979 | 594.8596 | 79.279 | 77.8032 | 81.5279
45.5979 | 588.5777 | 80.0927 | 79.5894 | 83.5865
46.5979 | 582.0342 | 81.1575 | 81.3001 | 85.2809
47.5979 | 586.237 | 82.1813 | 83.1168 | 87.5917
48.5979 | 572.0841 | 83.6254 | 85.3713 | 89.3684
49.5979 | 560.0943 | 85.704 | 87.5364 | 90.7067
50.5979 | 558.351 | 86.4947 | 89.2572 | 92.3775
51.5979 | 563.7425 | 87.312 | 90.0947 | 93.5341
52.5979 | 558.1713 | 88.7029 | 91.5355 | 95.6632
53.5979 | 561.9051 | 90.2628 | 93.0109 | 97.6343
54.5979 | 549.0326 | 91.9174 | 94.5689 | 98.9122
55.5979 | 545.4347 | 93.6105 | 96.1185 | 99.9333
56.5979 | 554.2109 | 95.0105 | 97.9612 | 100.8165
57.5979 | 534.0569 | 96.4212 | 99.5374 | 102.255
58.5979 | 524.776 | 97.777 | 101.0284 | 104.0595
59.5979 | 515.779 | 99.1975 | 102.305 | 104.7834
60.5979 | 498.0919 | 99.5905 | 103.6766 | 105.3819
61.5979 | 485.2051 | 101.1233 | 104.6999 | 106.6741
62.5979 | 474.2637 | 102.2556 | 105.7047 | 107.5601
63.5979 | 458.4105 | 103.3471 | 106.901 | 108.6586
64.5979 | 444.1928 | 104.2268 | 108.1709 | 109.6212
65.5979 | 432.8178 | 104.8274 | 109.349 | 110.1616
66.5979 | 425.4974 | 105.5748 | 110.1817 | 110.7687
67.5979 | 416.2564 | 106.5013 | 111.3075 | 112.3487
68.5979 | 409.1468 | 107.462 | 112.5644 | 113.8518
69.5979 | 400.1816 | 108.2327 | 113.7575 | 114.6665
70.5979 | 394.5128 | 109.1098 | 115.2078 | 115.1212
71.5979 | 387.7552 | 110.1521 | 115.8769 | 115.672
72.5979 | 382.8252 | 111.3157 | 116.5665 | 117.1084
73.5979 | 377.1385 | 111.7022 | 117.5523 | 118.4188
74.5979 | 370.4996 | 112.7808 | 118.5017 | 119.8411
75.5979 | 363.9785 | 114.4174 | 119.1798 | 120.6846
76.5979 | 360.0879 | 115.125 | 120.0749 | 121.3799
77.5979 | 352.8133 | 116.2179 | 121.1304 | 122.2137
78.5979 | 351.1411 | 117.391 | 121.6155 | 122.4622
79.5979 | 351.6979 | 117.7166 | 122.8282 | 122.612
80.5979 | 354.7259 | 118.1605 | 124.0489 | 122.4889
81.5979 | 351.4456 | 118.6451 | 124.4782 | 123.3096
82.5979 | 346.6037 | 119.3926 | 124.9422 | 123.8053
83.5979 | 344.0043 | 120.2406 | 125.265 | 124.0127
84.6292 | 340.7738 | 121.1386 | 125.7139 | 123.7287
85.5979 | 338.1355 | 120.7631 | 126.3454 | 123.8355
86.5979 | 339.962 | 121.2934 | 126.7323 | 123.955
87.5979 | 337.0264 | 121.7686 | 127.0897 | 124.5177
88.5979 | 336.9518 | 122.0366 | 127.8285 | 125.5962
89.5979 | 338.262 | 122.3213 | 127.9248 | 125.9878
90.5979 | 334.9651 | 122.3811 | 128.3328 | 126.4537
91.5979 | 330.0973 | 123.1117 | 128.8952 | 127.3226
92.5979 | 326.0666 | 123.8809 | 129.501 | 127.9236
93.5979 | 321.385 | 124.7358 | 129.9569 | 128.1887
94.5979 | 318.9501 | 125.4318 | 130.1513 | 128.9093
95.6135 | 317.4945 | 125.11 | 130.3085 | 128.9204
96.5979 | 316.8591 | 124.8871 | 130.6812 | 129.1037
97.5979 | 313.9087 | 124.8607 | 130.9353 | 129.2409
98.5979 | 315.0761 | 124.7862 | 130.9054 | 129.9465
99.5979 | 316.308 | 125.0517 | 131.2553 | 130.176
100.5979 | 315.5429 | 125.402 | 131.1589 | 130.4865
101.5979 | 314.1208 | 125.7679 | 131.2833 | 131.081
102.5979 | 315.3969 | 126.1324 | 131.621 | 131.4246
103.5979 | 321.6148 | 126.5721 | 131.8683 | 131.526
104.5979 | 325.966 | 126.9757 | 132.7699 | 131.6846
105.5979 | 324.7786 | 127.269 | 133.1438 | 132.0838
106.5979 | 325.6348 | 127.7732 | 133.7449 | 132.8964
107.5979 | 324.2463 | 128.4913 | 133.9944 | 133.3526
108.5979 | 322.5654 | 128.3219 | 134.5064 | 133.6457
109.5979 | 319.7671 | 128.7707 | 134.4832 | 133.4916
110.5979 | 317.3474 | 128.9624 | 134.8093 | 133.8376
111.5979 | 314.8347 | 129.3365 | 134.8049 | 133.7165
112.5979 | 312.5196 | 129.8667 | 134.7372 | 133.9451
113.5979 | 311.8071 | 129.476 | 134.7672 | 134.4443
114.5979 | 310.1972 | 129.3915 | 134.7973 | 134.4894
115.5979 | 308.9496 | 129.2748 | 134.8006 | 135.1304
116.5979 | 309.0312 | 129.4642 | 134.6767 | 135.3875
117.5979 | 309.1246 | 129.4942 | 134.5184 | 135.7781
118.5979 | 308.5737 | 129.4941 | 134.471 | 135.0559
119.5979 | 307.9289 | 129.4884 | 134.4628 | 134.5555
120.5979 | 309.3246 | 129.7086 | 134.2289 | 134.2644
121.5979 | 308.0732 | 129.5541 | 134.0849 | 133.9421
122.5979 | 307.6391 | 129.9675 | 134.1368 | 133.7392
123.5979 | 308.3377 | 129.8776 | 134.0547 | 133.9326
124.5979 | 309.7781 | 129.6067 | 134.147 | 133.9003
125.5979 | 312.8956 | 129.329 | 133.9283 | 133.9646
126.5979 | 315.9116 | 129.3138 | 134.0404 | 133.6769
127.5979 | 315.0462 | 129.2891 | 134.0988 | 133.7459
128.5979 | 314.1919 | 129.2424 | 134.0212 | 133.5209
129.5979 | 314.89 | 129.3752 | 135.0617 | 133.668
130.5979 | 315.5102 | 129.6459 | 135.1211 | 133.3931
131.5979 | 316.2513 | 130.0878 | 135.1231 | 133.1609
132.5979 | 316.0774 | 130.446 | 135.3735 | 133.3459
133.5979 | 315.8128 | 130.5067 | 135.5297 | 134.6776
134.5979 | 315.6025 | 130.4501 | 135.7341 | 133.9939
135.5979 | 318.4692 | 131.2211 | 135.8986 | 134.5461
136.5979 | 318.8056 | 131.8989 | 135.8716 | 134.0926
137.5979 | 318.3633 | 132.2865 | 136.724 | 134.3068
138.5979 | 319.7389 | 132.4326 | 137.1852 | 134.448
139.5979 | 320.3725 | 132.4391 | 137.9191 | 134.8743
140.5979 | 317.9418 | 132.6484 | 138.1106 | 134.5472
141.5979 | 318.6559 | 132.7602 | 138.2637 | 135.3686
142.5979 | 320.2915 | 133.2356 | 138.9417 | 135.6392
143.5979 | 318.5351 | 133.4113 | 139.5224 | 136.0242
144.5979 | 316.619 | 133.3617 | 140.1234 | 136.9415
145.5979 | 313.8895 | 134.0977 | 141.338 | 137.7053
146.5979 | 311.2115 | 134.9063 | 140.9984 | 138.4981
147.5979 | 309.7719 | 135.0165 | 141.3311 | 138.8307
148.5979 | 308.0938 | 135.5878 | 141.6025 | 138.4998
149.5979 | 306.1574 | 136.0697 | 141.682 | 138.6507
150.5979 | 302.9559 | 136.4594 | 141.9007 | 138.8825
151.5979 | 302.4388 | 136.7008 | 142.0771 | 138.786
152.5979 | 300.1438 | 136.7862 | 142.0973 | 139.0431
153.5979 | 298.7685 | 136.7812 | 141.8245 | 138.8908
154.5979 | 298.0807 | 136.5292 | 141.7641 | 138.6245
155.5979 | 298.4092 | 136.5591 | 142.3001 | 138.9944
156.5979 | 299.4448 | 136.3227 | 142.5039 | 138.9424
157.5979 | 298.7729 | 136.0993 | 142.6296 | 138.5976
158.5979 | 298.7824 | 136.2551 | 142.6682 | 138.6521
159.5979 | 297.2358 | 136.1433 | 142.4609 | 138.975
160.5979 | 296.6109 | 136.515 | 142.4161 | 139.8665
161.5979 | 298.1543 | 136.5835 | 142.4709 | 139.9884
162.5979 | 296.0137 | 136.8819 | 142.5648 | 139.6789
163.5979 | 296.0063 | 136.9358 | 142.4834 | 140.0891
164.5979 | 293.5331 | 136.8894 | 143.0292 | 140.0364
165.5979 | 294.6773 | 137.1368 | 142.8516 | 140.8319
166.5979 | 292.5745 | 137.7321 | 142.6487 | 141.0574
167.5979 | 290.0227 | 138.0017 | 143.975 | 141.2019
168.5979 | 286.6141 | 138.416 | 144.1227 | 141.7653
169.5979 | 284.6845 | 138.6057 | 144.9409 | 141.9563
170.5979 | 284.5747 | 139.2958 | 145.0838 | 141.6075
171.5979 | 281.8953 | 138.4563 | 145.1087 | 141.614
172.5979 | 280.3069 | 138.2212 | 145.3195 | 143.6109
173.5979 | 278.5301 | 139.1367 | 146.1254 | 143.9013
174.5979 | 277.9357 | 139.029 | 145.975 | 143.8871
175.5979 | 277.0354 | 139.5755 | 146.2956 | 143.7972
176.5979 | 276.9946 | 139.8414 | 146.6342 | 144.514
177.5979 | 275.8385 | 140.191 | 146.6871 | 144.6787
178.5979 | 275.871 | 139.9832 | 146.5852 | 144.6714
179.5979 | 275.8182 | 140.5334 | 147.3382 | 145.2807
180.5979 | 275.9771 | 140.9309 | 147.4613 | 145.5986
181.5979 | 275.5487 | 141.0202 | 148.7607 | 145.734
182.5979 | 276.5689 | 141.1978 | 148.9617 | 145.9374
183.5979 | 278.2878 | 142.2022 | 148.9239 | 145.911
184.5979 | 279.1267 | 142.7429 | 149.3369 | 146.463
185.5979 | 278.0216 | 143.2334 | 149.4412 | 147.2151
186.5979 | 278.4582 | 143.4866 | 149.7681 | 147.1472
187.5979 | 278.8196 | 143.7942 | 150.2746 | 147.2737
188.5979 | 277.5749 | 144.0576 | 150.4825 | 147.8879
189.5979 | 275.5279 | 144.0613 | 151.0319 | 147.8158
190.5979 | 275.3576 | 144.398 | 150.9236 | 148.1828
191.5979 | 276.2804 | 143.9979 | 151.116 | 148.0805
192.5979 | 274.7451 | 144.6232 | 151.3978 | 148.3057
193.5979 | 273.8027 | 144.6578 | 151.4072 | 148.2004
194.5979 | 273.8053 | 144.9551 | 151.7518 | 148.7084
195.5979 | 273.6587 | 145.1323 | 151.9653 | 148.9064
196.5979 | 275.2417 | 145.7985 | 151.7113 | 148.8204
197.5979 | 275.8369 | 146.068 | 151.7784 | 148.9718
198.5979 | 277.1486 | 146.2485 | 151.7744 | 149.0893
199.5979 | 275.1372 | 146.299 | 151.6366 | 150.4226
200.5979 | 273.9607 | 145.8001 | 151.8414 | 151.366
201.5979 | 272.9745 | 146.2421 | 152.0361 | 152.0949
202.5979 | 272.6862 | 146.7366 | 152.7503 | 152.4976
203.5979 | 272.5048 | 146.7766 | 153.5086 | 152.7474
204.5979 | 273.0899 | 147.055 | 153.8501 | 152.4817
205.5979 | 273.3749 | 147.217 | 156.2061 | 153.632
206.5979 | 274.0755 | 147.6328 | 156.3674 | 153.755
207.5979 | 276.0719 | 147.5995 | 156.2576 | 153.6732
208.5979 | 276.1263 | 147.7615 | 156.5248 | 154.9025
209.5979 | 277.6615 | 148.1921 | 156.7752 | 155.0708
210.5979 | 281.1933 | 148.233 | 156.6157 | 155.8778
211.5979 | 283.2946 | 147.9018 | 156.6093 | 155.8639
212.5979 | 282.1868 | 148.4493 | 156.5738 | 155.7797
213.5979 | 284.3666 | 148.763 | 156.8378 | 155.4672
214.5979 | 284.1926 | 148.9125 | 156.8352 | 155.8907
215.5979 | 287.1069 | 149.1162 | 157.2998 | 156.078
216.5979 | 288.3441 | 149.6639 | 157.1984 | 156.1188
217.5979 | 289.2362 | 150.3326 | 157.0956 | 156.0334
218.5979 | 290.346 | 150.2847 | 156.9552 | 155.8094
219.5979 | 292.4237 | 149.9735 | 156.5592 | 155.2115
220.5979 | 293.2536 | 150.2548 | 157.0763 | 156.0008
221.5979 | 294.3171 | 149.9405 | 156.873 | 155.3831
222.5979 | 295.6818 | 150.1912 | 156.4024 | 155.2398
223.5979 | 297.0558 | 150.0683 | 156.1902 | 154.8958
224.5979 | 297.2248 | 149.7256 | 155.9901 | 154.912
225.5979 | 296.3668 | 149.2262 | 155.881 | 154.847
226.5979 | 295.266 | 149.1125 | 155.9231 | 154.9278
227.5979 | 294.539 | 149.1523 | 155.9523 | 155.1413
228.5979 | 293.0433 | 149.1101 | 155.812 | 155.1372
229.5979 | 292.1847 | 150.1804 | 155.942 | 155.205
230.5979 | 292.8373 | 149.6932 | 156.1119 | 156.0548
231.5979 | 295.1148 | 149.8659 | 156.3753 | 156.1765
232.5979 | 295.0255 | 149.7803 | 156.905 | 156.2579
233.5979 | 297.8865 | 150.9518 | 157.2108 | 156.2156
234.5979 | 297.1849 | 150.828 | 158.0326 | 156.8098
235.5979 | 296.3676 | 150.488 | 158.2978 | 156.9842
236.5979 | 299.3681 | 151.3525 | 158.3708 | 156.9377
237.5979 | 299.4312 | 151.5632 | 158.4022 | 156.7608
238.5979 | 299.9987 | 152.1045 | 158.6644 | 156.8144
239.5979 | 302.3637 | 152.8099 | 159.0972 | 156.5964
240.5979 | 304.3102 | 152.6157 | 159.0817 | 156.2914
241.5979 | 307.0221 | 152.5562 | 159.4225 | 156.5399
242.5979 | 308.0808 | 152.2567 | 159.4325 | 156.3657
243.5979 | 311.0177 | 151.9112 | 159.8694 | 156.3879
244.5979 | 312.6487 | 151.7653 | 160.0196 | 156.7574
245.5979 | 315.8672 | 151.594 | 160.132 | 156.5916
246.5979 | 317.2227 | 151.7312 | 159.8646 | 156.4462
247.5979 | 316.8819 | 151.7165 | 160.0628 | 156.99
248.5979 | 316.509 | 151.2 | 159.8376 | 157.1609
249.5979 | 316.705 | 150.9145 | 159.6211 | 156.9963
250.5979 | 319.0523 | 150.4033 | 159.4543 | 156.613
251.5979 | 320.5341 | 150.7169 | 159.7298 | 156.411
252.5979 | 321.9471 | 151.0779 | 159.6289 | 155.8519
253.5979 | 324.565 | 151.3498 | 159.2668 | 155.5198
254.5979 | 326.3526 | 151.6986 | 159.2436 | 155.5239
255.5979 | 326.0263 | 151.7943 | 159.3089 | 155.6649
256.5979 | 326.696 | 151.2418 | 159.4277 | 156.0493
257.5979 | 327.6084 | 151.4273 | 159.4488 | 156.7034
258.5979 | 327.5998 | 151.4915 | 159.6316 | 156.6386
259.5979 | 326.7756 | 152.044 | 159.8288 | 157.3348
260.5979 | 327.0135 | 152.6491 | 159.9086 | 157.7522
261.5979 | 325.601 | 152.8522 | 159.8419 | 157.8932
262.5979 | 324.4829 | 153.1004 | 160.123 | 157.8401
263.5979 | 321.7708 | 153.2125 | 160.3252 | 158.7553
264.5979 | 319.8134 | 153.7936 | 160.3476 | 158.8052
265.6135 | 318.9288 | 154.933 | 160.4231 | 158.8455
266.5979 | 318.0856 | 154.9366 | 161.031 | 159.7236
267.5979 | 319.3693 | 155.0589 | 161.0504 | 159.979
268.5979 | 321.3959 | 155.0939 | 161.197 | 160.4764
269.5979 | 322.3277 | 154.3642 | 161.1301 | 160.8591
270.5979 | 322.0509 | 154.2769 | 161.0519 | 160.5332
271.5979 | 322.3086 | 154.1003 | 161.5239 | 160.2537
272.5979 | 321.3163 | 154.5712 | 161.524 | 159.916
273.5979 | 320.9074 | 154.8547 | 161.7173 | 159.6871
274.5979 | 323.7081 | 154.9689 | 161.6865 | 159.4796
275.5979 | 322.3199 | 154.7661 | 161.5437 | 159.1764
276.5979 | 324.5191 | 154.6824 | 161.5794 | 159.2273
277.5979 | 324.1089 | 154.7626 | 161.5023 | 159.5062
278.5979 | 325.2387 | 154.8674 | 161.3655 | 159.3932
279.5979 | 326.2183 | 154.5193 | 161.2583 | 159.6585
280.5979 | 327.7741 | 154.9263 | 161.643 | 159.7134
281.5979 | 328.7097 | 154.8522 | 161.6748 | 159.4426
282.5979 | 329.7717 | 155.1741 | 161.6182 | 159.5711
283.5979 | 331.6977 | 155.6957 | 161.6159 | 160.1348
284.5979 | 333.09 | 155.3154 | 161.7093 | 159.8845
285.5979 | 334.1576 | 155.4156 | 162.0052 | 159.8235
286.5979 | 334.256 | 155.3918 | 161.7669 | 159.7314
287.5979 | 334.6918 | 155.0353 | 161.8662 | 159.7892
288.5979 | 333.2032 | 155.0954 | 162.5404 | 160.0094
289.5979 | 332.0198 | 154.8412 | 162.6308 | 159.5809
290.5979 | 333.8013 | 154.5989 | 162.7237 | 159.7859
291.5979 | 335.8857 | 153.9804 | 162.8993 | 160.2797
292.5979 | 336.9219 | 154.0192 | 163.1852 | 160.5444
293.5979 | 339.4748 | 153.3634 | 163.3734 | 161.0115
294.5979 | 344.3002 | 153.188 | 163.5862 | 161.3071
295.5979 | 360.0401 | 153.7029 | 164.6417 | 162.0751
296.5979 | 362.7237 | 153.1641 | 165.5335 | 162.4987
297.5979 | 385.0956 | 153.3433 | 166.5362 | 162.9845
298.5979 | 392.8631 | 153.5355 | 166.5901 | 162.6212
299.5979 | 407.1288 | 153.3708 | 166.0564 | 163.0412
300.5979 | 432.8111 | 153.543 | 166.456 | 162.7352
301.5979 | 449.5059 | 153.3985 | 166.4583 | 162.6699
302.5979 | 467.7968 | 153.9122 | 166.3221 | 162.9678
303.5979 | 488.4406 | 154 | 166.2966 | 162.568
304.5979 | 507.1812 | 153.5932 | 166.0578 | 162.9923
305.5979 | 529.9341 | 153.8436 | 166.3863 | 163.1269
306.5979 | 546.3615 | 153.3684 | 166.1238 | 163.376
307.5979 | 559.3237 | 153.4355 | 165.8057 | 163.3423
308.5979 | 572.8534 | 153.636 | 165.8479 | 163.6765
309.5979 | 591.5528 | 153.381 | 166.0912 | 163.8305
310.5979 | 609.2063 | 152.5907 | 166.5713 | 163.7644
311.5979 | 618.4977 | 152.372 | 166.5283 | 163.9114
312.5979 | 639.0754 | 152.449 | 166.6393 | 164.0128
313.5979 | 646.79 | 152.7655 | 167.0515 | 163.9654
314.5979 | 651.7774 | 151.8023 | 166.9195 | 164.1742
315.5979 | 653.7126 | 151.6004 | 166.6674 | 164.4916
316.5979 | 651.8163 | 152.0972 | 166.7446 | 164.0028
317.5979 | 657.2698 | 152.3596 | 166.8978 | 164.0892
318.5979 | 668.6127 | 152.7578 | 166.6987 | 164.2193
319.5979 | 671.5325 | 152.9915 | 166.7386 | 165.1386
320.5979 | 680.8166 | 153.6564 | 166.8509 | 166.0211
321.5979 | 683.4679 | 153.8825 | 166.9507 | 166.481
322.5979 | 685.3236 | 154.488 | 167.0377 | 166.4411
323.5979 | 682.9839 | 154.8088 | 167.5128 | 166.7286
324.6135 | 692.3483 | 154.3296 | 167.3873 | 166.9254
325.5979 | 690.4009 | 154.676 | 167.7772 | 167.7033
326.5979 | 686.8072 | 154.4235 | 167.4614 | 167.6576
327.5979 | 699.3744 | 154.682 | 167.9867 | 168.4505
328.5979 | 699.6288 | 154.4574 | 167.7981 | 168.6398
329.5979 | 707.026 | 154.479 | 167.5156 | 168.7075
330.5979 | 710.8362 | 154.8665 | 167.4396 | 168.8864
331.6135 | 712.0048 | 155.1143 | 167.6641 | 169.0794
332.5979 | 705.1863 | 155.0748 | 168.1843 | 169.7686
333.5979 | 705.0299 | 155.5861 | 168.4282 | 170.1379
334.5979 | 707.4839 | 155.8732 | 168.3909 | 170.282
335.5979 | 710.4258 | 156.3701 | 168.3028 | 170.7517
336.5979 | 716.1159 | 156.4047 | 168.3244 | 171.5649
337.5979 | 715.6165 | 156.4983 | 168.0248 | 172.1254
338.5979 | 721.2584 | 156.6345 | 167.6998 | 172.1692
339.5979 | 724.8515 | 157.1538 | 167.9151 | 172.4658
340.5979 | 726.6148 | 157.1455 | 168.1328 | 171.9998
341.5979 | 726.7537 | 156.6907 | 168.482 | 172.1805
342.5979 | 730.5355 | 156.2641 | 168.8749 | 171.9397
343.5979 | 737.5478 | 156.3327 | 169.9395 | 171.837
344.5979 | 732.8742 | 156.4983 | 169.9434 | 171.981
345.5979 | 743.2464 | 156.4838 | 169.9305 | 171.7176
346.5979 | 743.2143 | 157.0434 | 170.3596 | 171.7847
347.5979 | 738.5133 | 156.8169 | 170.2169 | 172.9142
348.5979 | 740.5622 | 157.1497 | 170.1655 | 172.8373
349.5979 | 736.8056 | 157.7076 | 170.44 | 172.4117
350.5979 | 736.3906 | 158.13 | 170.8126 | 172.6512
351.5979 | 738.2384 | 158.4324 | 170.6093 | 172.1788
352.5979 | 732.058 | 158.0785 | 170.7147 | 172.0532
353.5979 | 734.2403 | 157.766 | 170.7858 | 172.6309
354.5979 | 738.5977 | 158.0301 | 170.4938 | 172.3017
355.5979 | 743.7776 | 158.6875 | 171.016 | 172.6147
356.5979 | 746.1683 | 159.0659 | 170.9325 | 172.4046
357.5979 | 743.3892 | 159.4232 | 171.3034 | 173.0732
358.5979 | 744.5345 | 159.8977 | 171.4882 | 173.5701
359.5979 | 740.2072 | 160.0948 | 171.7872 | 174.0044
360.5979 | 738.4502 | 159.5935 | 172.2809 | 174.6003
361.5979 | 741.7896 | 160.3703 | 172.4084 | 175.4696
362.5979 | 741.7914 | 160.5502 | 172.703 | 175.6375
363.5979 | 743.751 | 160.6516 | 172.9429 | 176.1931
364.5979 | 749.6323 | 160.3977 | 172.9315 | 175.9612
365.5979 | 752.5296 | 160.2324 | 172.8301 | 175.9809
366.5979 | 754.2738 | 160.2769 | 173.0154 | 176.8258
367.5979 | 751.4469 | 159.9759 | 172.997 | 177.1525
368.5979 | 749.2119 | 159.8101 | 172.7704 | 177.7
369.5979 | 751.032 | 159.7496 | 172.7857 | 177.6863
370.5979 | 751.7449 | 159.0451 | 173.1802 | 178.0669
371.5979 | 749.4708 | 159.0315 | 173.4734 | 178.1026
372.5979 | 746.2953 | 159.3875 | 173.8734 | 177.8688
373.5979 | 743.1525 | 159.2761 | 174.0551 | 177.3474
374.5979 | 744.0381 | 159.372 | 174.4871 | 177.8122
375.5979 | 748.7127 | 159.3648 | 174.9711 | 178.3414
376.5979 | 748.4509 | 159.341 | 174.9181 | 178.8781
377.5979 | 743.7362 | 159.0301 | 174.4247 | 179.6333
378.5979 | 747.3181 | 159.4378 | 175.0244 | 180.0094
379.5979 | 748.3451 | 159.9316 | 174.7278 | 180.49
380.5979 | 745.9258 | 160.7392 | 176.0136 | 181.2078
381.5979 | 743.8245 | 160.3556 | 175.8524 | 181.4869
382.5979 | 734.6857 | 160.9216 | 175.6763 | 181.5401
383.5979 | 735.1543 | 160.8167 | 174.942 | 181.4654
384.5979 | 735.1565 | 160.7166 | 175.2846 | 182.0304
385.5979 | 737.8828 | 160.7591 | 175.5739 | 182.5021
386.5979 | 735.6568 | 160.7807 | 175.3034 | 182.7687
387.5979 | 735.8247 | 161.0999 | 175.31 | 183.183
388.5979 | 737.0449 | 161.5767 | 175.7161 | 183.3999
389.5979 | 738.2317 | 162.0806 | 175.5221 | 183.6207
390.5979 | 732.7301 | 162.185 | 175.7363 | 183.4462
391.5979 | 730.0084 | 161.9322 | 176.2117 | 183.4892
392.5979 | 730.8866 | 162.0283 | 176.7904 | 183.6952
393.5979 | 729.3744 | 162.3398 | 176.8438 | 183.206
394.5979 | 732.4416 | 162.2922 | 177.733 | 183.1551
395.5979 | 732.742 | 162.4503 | 177.761 | 183.0397
396.5979 | 727.3923 | 162.6963 | 177.7971 | 183.5007
397.5979 | 730.22 | 162.766 | 178.3423 | 182.9643
398.5979 | 730.5698 | 163.1383 | 178.3202 | 182.5581
399.5979 | 738.0706 | 163.2782 | 178.0912 | 182.0886
400.5979 | 736.6049 | 162.9645 | 177.874 | 181.976
401.5979 | 731.0476 | 163.3378 | 178.0501 | 181.6953
402.5979 | 734.1506 | 163.2997 | 178.0658 | 181.0715
403.5979 | 735.7105 | 162.5594 | 177.9654 | 180.9578
404.5979 | 735.4438 | 162.4512 | 177.871 | 180.405
405.5979 | 739.7368 | 161.7967 | 177.9694 | 179.9238
406.5979 | 730.8752 | 162.3588 | 177.8067 | 180.1227
407.5979 | 735.1473 | 162.9026 | 177.2602 | 180.4552
408.5979 | 732.4279 | 163.2555 | 177.5002 | 180.7443
409.5979 | 733.3076 | 163.5781 | 177.3614 | 180.908
410.5979 | 732.872 | 163.7631 | 177.4537 | 180.8446
411.5979 | 729.1311 | 164.1529 | 177.3624 | 180.4749
412.5979 | 725.0426 | 164.9471 | 177.161 | 180.0049
413.5979 | 728.1649 | 165.2224 | 177.5672 | 179.8899
414.5979 | 728.0987 | 165.1523 | 177.3573 | 180.0382
415.5979 | 732.6262 | 164.8902 | 177.1713 | 179.9314
416.5979 | 734.6347 | 165.2761 | 177.043 | 180.1533
417.5979 | 729.5398 | 164.5342 | 176.9695 | 179.7338
418.5979 | 729.0536 | 164.6346 | 177.2438 | 179.564
419.5979 | 726.409 | 164.6995 | 176.9334 | 179.2436
420.5979 | 728.1074 | 164.6662 | 177.2926 | 179.2909
421.5979 | 724.8408 | 164.9122 | 176.9205 | 179.5424
422.5979 | 720.3729 | 165.4907 | 177.1915 | 180.886
423.5979 | 718.0225 | 164.9848 | 177.3436 | 180.9915
424.5979 | 725.0983 | 165.4678 | 177.1735 | 181.1433
425.5979 | 724.6659 | 165.4443 | 177.6538 | 181.2298
426.5979 | 723.7006 | 165.7722 | 177.8037 | 181.5127
427.5979 | 725.1076 | 166.5156 | 178.0557 | 181.7489
428.5979 | 726.3929 | 166.7235 | 178.5795 | 182.0525
429.5979 | 729.2693 | 166.6721 | 178.9807 | 182.3889
430.5979 | 728.6133 | 166.6304 | 179.4075 | 182.8318
431.5979 | 725.7917 | 167.3954 | 179.325 | 182.3589
432.5979 | 730.8621 | 167.4268 | 178.9952 | 183.0884
433.5979 | 731.5741 | 167.5186 | 178.9833 | 183.1023
434.5979 | 723.6356 | 168.1182 | 179.452 | 182.8345
435.5979 | 729.2737 | 168.0276 | 180.1826 | 182.762
436.5979 | 726.9039 | 168.3597 | 179.8769 | 182.1871
437.5979 | 719.8138 | 168.4574 | 179.7481 | 182.5342
438.5979 | 716.5776 | 169.2241 | 179.7205 | 182.3025
439.5979 | 718.244 | 169.0419 | 179.7187 | 182.5296
440.5979 | 712.0869 | 169.1419 | 179.9016 | 182.2686
441.5979 | 710.2063 | 169.2615 | 179.6367 | 182.6493
442.5979 | 710.1449 | 169.1377 | 179.8384 | 182.7854
443.5979 | 711.1595 | 169.0724 | 179.9007 | 183.0927
444.5979 | 717.7295 | 169.113 | 180.5662 | 182.7946
445.5979 | 715.0595 | 168.834 | 180.6137 | 182.4435
446.5979 | 718.0588 | 168.4017 | 180.6456 | 183.0495
447.5979 | 724.2447 | 168.3698 | 180.5165 | 182.9552
448.5979 | 720.7698 | 169.0833 | 180.6189 | 183.3744
449.5979 | 721.0525 | 169.339 | 180.5268 | 182.6525
450.5979 | 722.4089 | 169.2405 | 180.3902 | 182.3597
451.6135 | 718.2806 | 168.7165 | 180.7046 | 182.5714
452.5979 | 719.0162 | 168.594 | 180.1044 | 182.5408
453.5979 | 721.9492 | 168.7457 | 179.9591 | 182.5727
454.5979 | 723.6167 | 168.3805 | 179.5793 | 182.9946
455.5979 | 714.9903 | 168.3426 | 179.6417 | 182.661
456.5979 | 712.3949 | 168.0442 | 179.0023 | 184.1414
457.5979 | 694.5546 | 167.84 | 178.7933 | 183.8857
458.5979 | 700.5421 | 167.6483 | 179.0066 | 183.5923
459.5979 | 694.5411 | 167.5638 | 179.246 | 183.7829
460.5979 | 680.6315 | 167.4901 | 179.5015 | 183.7661
461.5979 | 668.8542 | 167.2258 | 179.6148 | 184.1818
462.5979 | 670.4744 | 167.1816 | 179.8115 | 183.8536
463.5979 | 674.0597 | 166.9418 | 179.4412 | 183.6674
464.5979 | 676.0557 | 166.9099 | 179.2349 | 183.0862
465.5979 | 666.4551 | 166.9667 | 178.889 | 182.8494
466.5979 | 666.0149 | 167.2698 | 179.0484 | 183.3853
467.5979 | 661.4997 | 167.6444 | 178.9557 | 182.963
468.5979 | 650.2106 | 167.5828 | 179.1384 | 182.805
469.5979 | 662.1581 | 167.8842 | 179.4677 | 182.6669
470.5979 | 671.2559 | 167.9528 | 178.9822 | 182.9183
471.5979 | 673.497 | 168.2644 | 179.0571 | 182.8137
472.5979 | 669.0198 | 168.5289 | 179.7612 | 182.5567
473.5979 | 646.5625 | 168.2517 | 181.4338 | 182.3001
474.5979 | 624.2269 | 168.8183 | 181.3205 | 182.6726
475.5979 | 614.7001 | 168.822 | 180.6888 | 182.9917
476.5979 | 612.7766 | 168.9031 | 180.7082 | 183.4108
477.5979 | 606.1217 | 168.9099 | 181.1674 | 183.356
478.5979 | 583.9327 | 168.8512 | 181.5451 | 183.9838
479.5979 | 573.435 | 168.3988 | 181.8651 | 184.4204
480.5979 | 570.1964 | 168.4346 | 182.2644 | 184.5248
481.5979 | 570.602 | 167.769 | 181.9601 | 184.6107
482.5979 | 570.0676 | 167.7218 | 182.3168 | 184.2903
483.5979 | 562.6333 | 167.1807 | 182.3775 | 184.1075
484.5979 | 561.663 | 166.9823 | 182.1116 | 184.1351
485.5979 | 574.9575 | 167.3476 | 181.9997 | 183.6448
486.5979 | 577.5035 | 167.7145 | 182.1554 | 183.5878
487.5979 | 569.1876 | 168.0319 | 181.7758 | 183.449
488.5979 | 555.9856 | 167.8033 | 182.0142 | 183.3762
489.5979 | 547.3193 | 168.0248 | 182.2185 | 182.9792
490.5979 | 536.8025 | 168.0269 | 182.0338 | 182.7204
491.5979 | 525.9945 | 168.4229 | 181.8809 | 182.8153
492.5979 | 518.0731 | 168.2839 | 181.662 | 182.4828
493.5979 | 512.9839 | 168.7208 | 181.8056 | 181.9323
494.5979 | 507.6512 | 168.0683 | 182.4019 | 182.1013
495.5979 | 505.82 | 168.0746 | 182.0007 | 182.5889
496.5979 | 505.9506 | 168.3728 | 182.0374 | 182.5313
497.5979 | 516.4916 | 168.2269 | 181.8229 | 182.9807
498.5979 | 511.4508 | 167.6129 | 181.6207 | 182.8106
499.5979 | 504.0018 | 167.1904 | 181.457 | 183.0782
500.5979 | 501.4869 | 166.5827 | 181.0934 | 182.8032
501.5979 | 494.532 | 166.3365 | 180.6405 | 182.5664
502.5979 | 486.6909 | 166.4146 | 180.5188 | 182.2964
503.5979 | 483.582 | 166.7433 | 181.3313 | 182.4445
504.5979 | 480.0309 | 167.1133 | 181.1113 | 181.9947
505.5979 | 481.6842 | 167.1922 | 181.4259 | 182.1648
506.5979 | 480.892 | 167.3548 | 181.1707 | 182.1556
507.5979 | 490.8793 | 167.3413 | 181.1467 | 182.3032
508.5979 | 497.2918 | 167.2191 | 181.1985 | 182.1258
509.5979 | 504.0164 | 166.9995 | 181.0737 | 182.6663
510.5979 | 500.7709 | 166.8454 | 181.6864 | 182.3618
511.5979 | 503.503 | 167.3092 | 181.408 | 182.2259
512.5979 | 498.3286 | 167.488 | 181.9613 | 182.1482
513.5979 | 490.3018 | 167.4917 | 181.9512 | 182.131
514.5979 | 483.9029 | 167.2662 | 181.9541 | 182.2869
515.5979 | 477.8523 | 167.2149 | 182.0764 | 182.0753
516.5979 | 479.3797 | 166.5444 | 182.8369 | 182.629
517.5979 | 487.631 | 166.5543 | 182.9346 | 182.6635
518.5979 | 495.0668 | 166.4662 | 183.3451 | 182.7891
519.5979 | 494.9309 | 166.1611 | 183.918 | 182.63
520.5979 | 489.2608 | 167.7559 | 184.4618 | 182.6751
521.5979 | 487.2334 | 167.3753 | 184.9618 | 182.81
522.5979 | 497.2772 | 168.2321 | 185.1251 | 182.842
523.5979 | 498.1801 | 168.6241 | 185.5801 | 183.3076
524.5979 | 502.0067 | 169.1541 | 185.6945 | 183.7236
525.5979 | 495.7386 | 168.7035 | 185.549 | 184.0647
526.5979 | 485.1624 | 168.6646 | 185.5344 | 184.4263
527.5979 | 477.4909 | 169.1225 | 185.2607 | 184.7778
528.5979 | 472.2301 | 168.5259 | 184.9893 | 184.9137
529.5979 | 465.1356 | 168.757 | 185.0473 | 185.5106
530.5979 | 459.1285 | 168.6921 | 185.5589 | 186.0053
531.5979 | 454.4458 | 169.0521 | 185.4546 | 185.8801
532.5979 | 448.0214 | 169.4897 | 185.4309 | 185.8739
533.5979 | 446.1369 | 169.3555 | 185.3049 | 185.9519
534.5979 | 448.6555 | 169.1479 | 185.4993 | 185.7006
535.5979 | 454.1553 | 169.2432 | 186.0952 | 185.5619
536.5979 | 456.527 | 169.2773 | 185.8084 | 185.5954
537.5979 | 454.4186 | 169.4742 | 185.87 | 185.3775
538.5979 | 451.8647 | 169.4171 | 185.8138 | 184.9851
539.5979 | 449.0847 | 169.3826 | 185.3348 | 185.0429
540.5979 | 448.4812 | 169.3073 | 185.2374 | 184.8953
541.5979 | 448.7324 | 168.7015 | 185.2018 | 184.6923
542.5979 | 447.6663 | 168.8063 | 185.0294 | 184.2732
543.5979 | 446.1034 | 169.1244 | 185.0401 | 183.7401
544.5979 | 442.3388 | 168.9882 | 184.7806 | 183.2415
545.5979 | 448.9407 | 169.263 | 184.6477 | 183.1091
546.5979 | 444.8494 | 169.0927 | 184.5982 | 182.7876
547.5979 | 443.8651 | 168.8949 | 184.5898 | 182.6544
548.5979 | 457.4476 | 168.9159 | 184.579 | 182.4904
549.5979 | 464.7256 | 168.681 | 184.6698 | 182.7571
550.5979 | 463.8412 | 168.7692 | 184.6023 | 182.833
551.5979 | 461.9209 | 169.1641 | 184.5196 | 182.2428
552.5979 | 479.3531 | 169.0565 | 184.3526 | 182.1336
553.5979 | 486.6733 | 169.1358 | 184.9767 | 182.3068
554.5979 | 491.0392 | 168.6955 | 184.3975 | 181.8642
555.5979 | 490.5797 | 168.2017 | 184.3321 | 181.7826
556.5979 | 481.7255 | 168.1755 | 183.8982 | 181.4491
557.5979 | 472.6941 | 168.1915 | 184.1508 | 181.484
558.5979 | 465.146 | 168.0506 | 184.1582 | 181.4557
559.5979 | 457.5475 | 168.0813 | 184.0036 | 181.6999
560.5979 | 455.0165 | 168.0087 | 183.8448 | 182.0499
561.5979 | 453.6468 | 168.1133 | 184.0437 | 181.6042
562.5979 | 452.8113 | 168.3515 | 184.0965 | 181.4553
563.5979 | 453.0962 | 168.7305 | 184.1671 | 181.3841
564.6135 | 449.4514 | 169.4664 | 183.9072 | 181.8612
565.5979 | 447.8039 | 169.5798 | 183.8415 | 182.2463
566.5979 | 447.8092 | 169.7414 | 183.9707 | 182.3514
567.5979 | 446.8641 | 170.7387 | 184.0697 | 181.9526
568.5979 | 446.0359 | 170.7201 | 184.1868 | 182.0216
569.5979 | 443.6464 | 171.3476 | 184.2493 | 181.4754
570.5979 | 440.4468 | 171.0594 | 184.5676 | 181.7038
571.5979 | 436.5544 | 171.5507 | 184.6667 | 181.4408
572.5979 | 432.0612 | 171.1606 | 185.1023 | 181.4669
573.5979 | 431.0518 | 171.0655 | 185.3694 | 181.9546
574.5979 | 433.787 | 171.7331 | 184.9677 | 182.2417
575.5979 | 433.2354 | 171.8682 | 184.9323 | 181.7926
576.5979 | 437.3838 | 172.3889 | 185.395 | 182.0826
577.5979 | 440.7647 | 172.8132 | 185.6703 | 181.9562
578.5979 | 442.6669 | 173.2177 | 185.8093 | 182.1676
579.5979 | 442.8128 | 172.6222 | 185.5237 | 182.4071
580.5979 | 449.7069 | 172.7445 | 185.3819 | 182.4887
581.5979 | 456.8196 | 172.7836 | 184.803 | 182.823
582.5979 | 464.0172 | 173.7399 | 185.5206 | 182.8507
583.5979 | 469.591 | 173.9467 | 186.1893 | 183.3411
584.5979 | 475.8058 | 174.3803 | 186.5634 | 183.7188
585.5979 | 474.2841 | 174.2533 | 186.2175 | 183.8724
586.5979 | 475.3097 | 174.3014 | 186.362 | 184.1123
587.5979 | 475.6248 | 173.8874 | 186.5056 | 184.6806
588.5979 | 474.2172 | 173.7697 | 186.395 | 184.697
589.5979 | 469.7147 | 174.2015 | 187.05 | 184.9622
590.5979 | 469.9571 | 174.526 | 187.5125 | 184.3947
591.5979 | 471.2816 | 174.8534 | 187.8084 | 184.9419
592.5979 | 473.068 | 174.6693 | 188.1669 | 185.1775
593.5979 | 473.6414 | 174.8023 | 188.4727 | 185.5429
594.5979 | 474.4787 | 175.3391 | 188.6211 | 186.647
595.5979 | 472.7315 | 175.4907 | 189.3618 | 187.3508
596.5979 | 493.52 | 175.3154 | 189.8092 | 187.9624
597.5979 | 492.7561 | 175.2222 | 189.8646 | 188.7071
598.5979 | 494.6888 | 175.0767 | 189.8112 | 188.3865
599.5979 | 497.9851 | 174.9542 | 189.6945 | 188.7
600.5979 | 508.0136 | 175.0589 | 189.7 | 188.5009
601.5979 | 509.8662 | 175.4275 | 189.2589 | 188.5167
602.5979 | 506.1942 | 175.3648 | 189.678 | 188.2933
603.5979 | 502.8872 | 175.2358 | 189.61 | 188.2876
604.5979 | 505.1203 | 175.322 | 189.3364 | 188.3064
605.5979 | 515.0509 | 175.2609 | 189.012 | 188.8635
606.5979 | 532.5218 | 176.3225 | 189.1195 | 189.1278
607.5979 | 532.9822 | 176.6958 | 189.0987 | 189.4988
608.5979 | 533.8088 | 176.5142 | 189.2755 | 190.2008
609.5979 | 529.0405 | 176.3322 | 189.3828 | 190.2924
610.5979 | 525.2996 | 176.1648 | 189.0435 | 190.7442
611.5979 | 522.591 | 176.4475 | 187.9859 | 190.9461
612.5979 | 513.9855 | 176.2139 | 188.1893 | 191.2788
613.5979 | 506.4518 | 176.8077 | 188.2689 | 191.2125
614.5979 | 502.5208 | 177.3305 | 188.4156 | 190.9496
615.5979 | 499.6822 | 177.1869 | 188.4836 | 191.1091
616.5979 | 497.1611 | 177.2727 | 188.3805 | 190.7371
617.5979 | 508.693 | 177.2111 | 188.263 | 190.653
618.5979 | 507.827 | 177.3972 | 188.3 | 190.4084
619.5979 | 508.9583 | 176.9628 | 188.6353 | 190.5397
620.5979 | 515.1323 | 177.04 | 189.0495 | 190.4427
621.5979 | 520.0292 | 177.1494 | 189.1162 | 190.7362
622.5979 | 526.3475 | 177.5145 | 189.3037 | 191.1686
623.5979 | 539.2792 | 177.9742 | 189.5297 | 191.0932
624.5979 | 539.7284 | 178.4566 | 190.331 | 191.4694
625.5979 | 535.9656 | 178.3336 | 190.109 | 191.7903
626.5979 | 528.3504 | 178.2907 | 190.4944 | 192.0968
627.5979 | 530.176 | 177.9812 | 190.3815 | 192.1746
628.5979 | 534.224 | 177.8361 | 191.7525 | 191.948
629.5979 | 546.1874 | 177.8871 | 191.6202 | 191.6479
630.5979 | 552.4765 | 178.6243 | 192.0998 | 191.2879
631.5979 | 563.1564 | 177.9971 | 192.1259 | 191.6209
632.5979 | 583.2531 | 178.2536 | 192.2068 | 192.1313
633.5979 | 584.7768 | 178.6312 | 191.7558 | 191.6443
634.5979 | 612.6868 | 178.5864 | 191.4003 | 192.139
635.5979 | 601.0772 | 178.6041 | 191.1424 | 192.741
636.5979 | 590.6631 | 179.13 | 191.1718 | 193.1498
637.5979 | 577.8716 | 178.4459 | 190.7141 | 192.9529
638.5979 | 574.2887 | 178.4132 | 190.946 | 192.9469
639.5979 | 561.5219 | 178.6821 | 190.8475 | 192.9186
640.5979 | 546.7064 | 178.4888 | 190.3399 | 192.8448
641.5979 | 539.6448 | 178.598 | 190.0878 | 192.4105
642.5979 | 534.8118 | 178.7355 | 190.012 | 193.0243
643.5979 | 527.5491 | 178.6368 | 189.8653 | 193.1069
644.5979 | 538.3331 | 178.3082 | 189.7581 | 192.7264
645.5979 | 540.8268 | 179.0976 | 189.6895 | 192.0475
646.5979 | 546.1457 | 179.4752 | 189.9426 | 191.9376
647.5979 | 540.8718 | 179.7032 | 189.8759 | 191.9546
648.5979 | 539.3356 | 179.5348 | 190.2469 | 191.9576
649.5979 | 534.325 | 179.9205 | 189.7675 | 191.5299
650.5979 | 527.7584 | 179.4763 | 189.6411 | 191.3572
651.5979 | 528.5106 | 179.8845 | 189.6631 | 190.9108
652.5979 | 520.9082 | 179.8911 | 189.8073 | 190.8266
653.5979 | 514.4786 | 179.9898 | 189.9479 | 190.7638
654.6135 | 510.2106 | 180.475 | 189.4349 | 190.7088
655.5979 | 504.1687 | 180.3043 | 189.0825 | 191.4591
656.5979 | 501.587 | 180.2007 | 189.3948 | 191.4847
657.5979 | 498.899 | 180.8569 | 189.9215 | 191.3486
658.5979 | 496.0439 | 181.7582 | 190.0259 | 191.0651
659.5979 | 490.9089 | 181.5101 | 189.8009 | 190.7746
660.5979 | 487.5155 | 181.7923 | 190.1038 | 190.4937
661.5979 | 486.5258 | 181.8403 | 189.8559 | 190.156
662.5979 | 484.2403 | 182.176 | 189.8026 | 189.8026
663.5979 | 494.7547 | 181.9261 | 189.7721 | 190.3965
664.5979 | 487.0743 | 182.4624 | 190.0778 | 190.706
665.5979 | 483.1558 | 182.2787 | 190.0128 | 190.5822
666.5979 | 482.4056 | 182.019 | 190.8042 | 190.8019
667.5979 | 485.5965 | 182.4649 | 191.1492 | 190.9957
668.5979 | 484.6669 | 182.6593 | 191.7835 | 191.2095
669.5979 | 484.7157 | 182.7013 | 192.2696 | 190.9703
670.5979 | 484.0763 | 182.8033 | 192.3924 | 190.3646
671.5979 | 483.6384 | 183.1458 | 192.6164 | 190.1507
672.5979 | 482.7248 | 183.0559 | 192.6279 | 190.4484
673.5979 | 480.7797 | 182.5987 | 192.4588 | 190.1436
674.5979 | 483.1361 | 182.7651 | 192.3374 | 189.8656
675.5979 | 483.0853 | 182.4626 | 192.5537 | 189.4294
676.5979 | 480.8068 | 182.0795 | 192.6219 | 189.0771
677.5979 | 483.2704 | 182.1223 | 192.4549 | 188.7656
678.5979 | 482.897 | 181.7317 | 192.4774 | 189.3006
679.5979 | 486.7584 | 181.6019 | 192.4528 | 189.5129
680.5979 | 499.8092 | 181.3226 | 192.5135 | 189.3165
681.5979 | 507.4847 | 181.1813 | 192.357 | 188.9494
682.5979 | 504.4846 | 181.1261 | 192.4164 | 188.6275
683.5979 | 499.9717 | 180.9033 | 192.314 | 188.7686
684.5979 | 504.4232 | 180.8039 | 192.1901 | 189.0526
685.5979 | 500.0065 | 180.7933 | 192.2553 | 188.9422
686.5979 | 494.7605 | 181.1446 | 193.059 | 189.7232
687.5979 | 492.252 | 181.5631 | 193.4626 | 190.2666
688.5979 | 495.1259 | 181.179 | 193.4641 | 190.4272
689.5979 | 493.2649 | 181.9404 | 193.7465 | 190.4001
690.5979 | 490.597 | 181.9701 | 193.8607 | 190.9571
691.5979 | 486.3217 | 181.5583 | 193.5883 | 191.568
692.5979 | 481.9486 | 181.1212 | 194.3222 | 192.0109
693.5979 | 480.7801 | 181.1489 | 194.1779 | 191.8083
694.5979 | 479.3941 | 181.0363 | 194.1218 | 191.5221
695.5979 | 475.7648 | 180.8828 | 193.7764 | 191.2602
696.5979 | 478.6764 | 180.4967 | 193.7162 | 190.9255
697.5979 | 477.6753 | 181.056 | 193.9662 | 190.9266
698.5979 | 478.9041 | 181.1795 | 194.3557 | 191.4075
699.5979 | 480.6878 | 181.0107 | 195.0266 | 191.6003
700.5979 | 478.1018 | 180.536 | 194.8584 | 192.0676
701.5979 | 477.9546 | 180.48 | 194.6072 | 191.9963
702.5979 | 481.2618 | 180.6454 | 194.1263 | 192.0777
703.5979 | 496.2457 | 180.6088 | 193.5317 | 191.6735
704.5979 | 493.1021 | 180.3004 | 194.4835 | 191.3208
705.5979 | 494.4665 | 180.6159 | 194.4611 | 192.0095
706.5979 | 493.3379 | 180.7916 | 194.5748 | 191.971
707.5979 | 496.6979 | 181.0568 | 194.8328 | 191.6971
708.5979 | 523.3207 | 181.3929 | 194.4417 | 191.4826
709.5979 | 529.3748 | 181.1435 | 194.413 | 191.6874
710.5979 | 559.1579 | 180.9605 | 194.6048 | 191.826
711.5979 | 554.0574 | 181.2986 | 194.6565 | 192.1611
712.5979 | 548.952 | 181.3588 | 195.0809 | 192.9729
713.5979 | 537.6353 | 180.8563 | 195.1209 | 193.4193
714.5979 | 529.9857 | 180.8829 | 195.1064 | 194.5213
715.5979 | 523.6943 | 180.4821 | 195.689 | 194.2357
716.5979 | 515.7734 | 180.0696 | 196.0893 | 194.9925
717.5979 | 513.3637 | 180.1297 | 196.036 | 195.1574
718.5979 | 511.4216 | 179.5488 | 196.0621 | 194.6866
719.5979 | 509.0876 | 179.3936 | 196.1591 | 194.2054
720.5979 | 510.3351 | 180.3353 | 196.42 | 194.5003
721.5979 | 505.9818 | 180.7031 | 196.4873 | 194.5236
722.5979 | 505.6411 | 180.9764 | 195.6262 | 194.8098
723.5979 | 502.0191 | 181.2716 | 195.6899 | 195.0234
724.5979 | 497.5523 | 181.0155 | 196.1043 | 195.0365
725.5979 | 494.3778 | 180.8907 | 195.7232 | 194.8713
726.5979 | 509.5535 | 180.7044 | 195.8935 | 194.6022
727.5979 | 512.5661 | 181.426 | 195.65 | 195.0367
728.5979 | 518.5387 | 180.7716 | 195.5965 | 194.8131
729.5979 | 508.9318 | 180.8429 | 195.3557 | 194.4343
730.5979 | 500.7088 | 181.0597 | 195.405 | 194.2962
731.5979 | 495.8399 | 180.6989 | 194.8652 | 194.4535
732.5979 | 496.3166 | 181.1356 | 194.8509 | 194.7134
733.5979 | 526.0269 | 181.8272 | 194.8334 | 194.9221
734.5979 | 523.4691 | 182.4709 | 195.441 | 195.8528
735.5979 | 516.2217 | 182.97 | 195.4132 | 195.9233
736.5979 | 514.3635 | 182.9957 | 195.7998 | 195.6018
737.5979 | 515.0012 | 183.0155 | 196.3965 | 195.6607
738.5979 | 506.8198 | 183.3995 | 196.4502 | 195.6787
739.5979 | 495.9017 | 183.6906 | 197.2311 | 195.7428
740.5979 | 486.1555 | 183.8753 | 197.634 | 196.0761
741.5979 | 478.2744 | 183.4467 | 197.6074 | 196.1335
742.5979 | 471.0291 | 183.3458 | 197.6038 | 195.8755
743.5979 | 464.3871 | 183.4223 | 197.6096 | 195.7654
744.5979 | 460.3214 | 183.9773 | 197.586 | 195.7107
745.5979 | 456.0632 | 183.8904 | 197.534 | 195.4997
746.5979 | 451.7516 | 183.9777 | 197.2521 | 194.8995
747.5979 | 447.4959 | 184.2372 | 197.5061 | 194.4896
748.5979 | 444.7387 | 184.6011 | 197.7982 | 195.2272
749.5979 | 444.2768 | 184.7722 | 197.9773 | 195.106
750.6135 | 442.9256 | 185.1369 | 198.9061 | 195.2611
751.5979 | 442.0443 | 185.1433 | 198.8436 | 195.0537
752.6135 | 440.1283 | 185.5024 | 199.0695 | 195.1483
753.5979 | 442.0819 | 186.1879 | 199.1633 | 195.5434
754.6135 | 442.9276 | 186.7776 | 199.2582 | 196.1365
755.5979 | 441.3352 | 187.1184 | 198.6974 | 196.4735
756.6135 | 444.7608 | 186.9901 | 198.889 | 196.475
757.5979 | 448.0028 | 187.6496 | 199.3071 | 196.1129
758.5979 | 449.395 | 187.4578 | 198.501 | 196.0092
759.5979 | 449.052 | 187.4046 | 198.449 | 196.6138
760.5979 | 448.9947 | 187.1186 | 198.335 | 196.8359
761.5979 | 444.1353 | 186.8347 | 198.2967 | 196.7014
762.5979 | 442.2394 | 186.8716 | 197.9406 | 196.8562
763.5979 | 439.5099 | 187.6725 | 198.0247 | 196.4135
764.5979 | 441.1581 | 187.9823 | 197.9427 | 196.8175
765.5979 | 444.5138 | 188.3796 | 198.4034 | 197.0489
766.5979 | 445.7624 | 188.2085 | 198.6292 | 196.6094
767.5979 | 443.876 | 188.9136 | 198.9526 | 196.9798
768.5979 | 444.2023 | 188.2943 | 198.275 | 196.5883
769.5979 | 443.0616 | 188.1554 | 198.4007 | 197.0817
770.5979 | 442.1255 | 188.5395 | 198.1244 | 196.6233
771.5979 | 440.6324 | 188.5843 | 198.1946 | 196.2975
772.5979 | 438.1534 | 188.4722 | 198.2701 | 195.9459
773.5979 | 434.1752 | 189.1737 | 198.8026 | 196.4678
774.5979 | 432.4121 | 188.8638 | 199.0488 | 198.0811
775.5979 | 436.4261 | 188.9053 | 199.0342 | 197.7495
776.6135 | 440.227 | 188.4733 | 199.0292 | 197.7738
777.5979 | 441.5554 | 188.3593 | 200.2106 | 197.7515
778.5979 | 440.4241 | 188.5335 | 200.3574 | 197.4984
779.5979 | 437.4973 | 188.8445 | 200.3679 | 197.9245
780.5979 | 432.572 | 188.4544 | 200.4219 | 198.3038
781.6292 | 431.4923 | 188.1831 | 200.5788 | 198.4749
782.5979 | 434.3951 | 188.9518 | 200.5163 | 198.2153
783.5979 | 436.5662 | 188.618 | 200.3243 | 198.0108
784.5979 | 440.1996 | 188.1954 | 200.2132 | 197.8646
785.5979 | 439.4627 | 188.0002 | 201.6289 | 198.8385
786.5979 | 438.9026 | 187.2701 | 201.3883 | 198.4711
787.5979 | 437.0855 | 186.8062 | 201.4258 | 198.1272
788.5979 | 433.995 | 187.1623 | 201.3002 | 197.7284
789.5979 | 432.6507 | 187.2275 | 201.2183 | 197.5989
790.5979 | 430.723 | 187.8148 | 201.2082 | 197.8944
791.5979 | 428.3199 | 187.2402 | 201.0843 | 198.278
792.5979 | 425.5135 | 186.4554 | 200.9777 | 198.1518
793.5979 | 425.3231 | 185.7355 | 200.5066 | 198.1205
794.5979 | 421.4446 | 185.1762 | 200.1348 | 197.9545
795.5979 | 420.9388 | 186.0663 | 199.9952 | 198.3797
796.5979 | 417.1675 | 186.2328 | 199.8981 | 198.5657
797.5979 | 414.3604 | 186.0804 | 200.0888 | 198.4065
798.5979 | 411.7306 | 186.3239 | 200.3672 | 198.4733
799.5979 | 411.3801 | 186.4528 | 200.0884 | 198.0075
800.5979 | 409.5923 | 187.0021 | 200.2166 | 197.7582
801.5979 | 408.6745 | 186.7298 | 200.0215 | 197.8311
802.5979 | 410.5854 | 187.2431 | 200.0603 | 197.8382
803.5979 | 413.9959 | 186.9674 | 200.143 | 198.7673
804.5979 | 415.6647 | 187.2399 | 200.3864 | 198.5488
805.5979 | 418.065 | 187.1942 | 200.8306 | 198.8094
806.5979 | 418.2255 | 187.1108 | 200.7294 | 200.5889
807.5979 | 416.8933 | 187.089 | 200.711 | 200.7226
808.5979 | 417.6918 | 186.9384 | 200.5708 | 201.2823
809.5979 | 416.1101 | 187.0031 | 200.454 | 201.8593
810.5979 | 414.4573 | 186.5892 | 200.4447 | 201.549
811.5979 | 413.2964 | 187.4294 | 200.6598 | 201.6357
812.5979 | 413.1867 | 186.994 | 200.7712 | 201.4908
813.5979 | 417.1754 | 186.3424 | 200.8045 | 201.2592
814.5979 | 423.3178 | 186.375 | 201.7033 | 201.3193
815.5979 | 423.8396 | 185.8388 | 201.6581 | 201.4169
816.5979 | 426.4692 | 185.7121 | 201.4657 | 201.4872
817.5979 | 424.9161 | 185.7418 | 201.3657 | 201.0777
818.5979 | 423.6483 | 185.8043 | 201.145 | 201.3473
819.5979 | 420.7944 | 185.0435 | 200.8751 | 200.9219
820.5979 | 419.1496 | 184.351 | 200.9058 | 200.7868
821.5979 | 416.9444 | 184.3478 | 200.6341 | 200.5583
822.5979 | 415.4614 | 183.9382 | 200.4739 | 200.1805
823.5979 | 419.7146 | 183.9582 | 200.2922 | 200.018
824.5979 | 420.4772 | 183.4581 | 200.7614 | 199.4042
825.5979 | 419.6174 | 182.6763 | 200.9082 | 200.134
826.5979 | 422.1016 | 182.8132 | 200.7294 | 200.531
827.5979 | 425.2199 | 182.6417 | 201.1711 | 201.0821
828.5979 | 425.3314 | 182.2359 | 201.2458 | 200.8533
829.5979 | 422.8174 | 182.3046 | 201.1929 | 200.5304
830.5979 | 420.736 | 182.414 | 200.9494 | 200.571
831.5979 | 418.0036 | 182.9784 | 200.9283 | 200.3856
832.5979 | 418.9075 | 183.1021 | 201.197 | 200.6611
833.5979 | 416.3163 | 182.9776 | 201.5228 | 200.6046
834.5979 | 411.1306 | 183.8728 | 201.4316 | 200.933
835.5979 | 408.004 | 183.5968 | 201.5724 | 200.3389
836.5979 | 405.7474 | 184.222 | 201.5227 | 200.1614
837.5979 | 404.537 | 184.5966 | 201.5953 | 200.2138
838.5979 | 403.9608 | 185.1011 | 202.055 | 200.1429
839.5979 | 402.5813 | 184.9957 | 202.1128 | 200.3505
840.5979 | 399.6898 | 185.1659 | 202.3266 | 200.1624
841.5979 | 399.6499 | 185.693 | 202.5055 | 200.5705
842.5979 | 398.9905 | 185.7778 | 202.3876 | 200.7097
843.5979 | 396.9528 | 186.0772 | 202.2659 | 200.7048
844.5979 | 395.6774 | 185.9671 | 201.9904 | 200.8245
845.5979 | 394.601 | 185.9075 | 201.893 | 200.6366
846.5979 | 393.5852 | 186.5539 | 201.6548 | 200.1865
847.5979 | 394.7061 | 186.7102 | 201.701 | 200.0083
848.5979 | 392.1356 | 186.0262 | 201.7699 | 200.2487
849.5979 | 390.6905 | 185.6663 | 201.9104 | 200.9771
850.5979 | 388.9243 | 186.3274 | 202.2129 | 200.8806
851.5979 | 392.4154 | 186.8996 | 202.2393 | 201.497
852.5979 | 391.0259 | 187.1798 | 202.3606 | 201.6171
853.5979 | 388.6869 | 187.2895 | 202.1675 | 201.4542
854.5979 | 387.0428 | 187.9024 | 201.9199 | 200.628
855.5979 | 387.2961 | 188.0947 | 201.8615 | 200.1522
856.5979 | 386.7157 | 187.6685 | 201.9618 | 200.2693
857.5979 | 379.9545 | 187.7227 | 202.2011 | 199.8959
858.5979 | 380.1445 | 187.8277 | 202.2105 | 200.0798
859.5979 | 380.1129 | 187.5322 | 202.2316 | 200.0647
860.5979 | 379.6604 | 188.223 | 202.0986 | 199.8633
861.5979 | 380.0001 | 188.363 | 202.163 | 199.1866
862.5979 | 383.3995 | 188.1104 | 202.0352 | 198.792
863.5979 | 381.9222 | 187.374 | 202.3918 | 199.2333
864.5979 | 381.1277 | 187.7617 | 202.2885 | 199.1127
865.5979 | 382.0208 | 188.3002 | 202.0696 | 199.4942
866.5979 | 380.4379 | 188.3275 | 201.9064 | 199.8239
867.5979 | 381.8874 | 188.1511 | 201.9738 | 199.9987
868.5979 | 384.0371 | 188.3744 | 202.3882 | 199.969
869.5979 | 383.9331 | 188.4398 | 202.3839 | 200.3945
870.5979 | 385.2543 | 188.1283 | 202.1112 | 200.1407
871.5979 | 386.9724 | 187.8431 | 202.2186 | 200.8859
872.5979 | 390.7477 | 187.9207 | 202.1401 | 200.6768
873.5979 | 388.8493 | 187.7892 | 201.9127 | 200.5067
874.5979 | 386.7873 | 188.0904 | 202.4075 | 200.1255
875.5979 | 386.2982 | 187.3061 | 202.2711 | 199.7696
876.5979 | 385.4688 | 187.1083 | 202.3207 | 199.6544
877.5979 | 385.568 | 187.1932 | 202.9364 | 199.7202
878.5979 | 386.999 | 187.2308 | 202.9853 | 200.2826
879.5979 | 388.1272 | 187.7692 | 203.0663 | 200.4746
880.5979 | 390.4191 | 188.436 | 203.4795 | 200.5078
881.5979 | 388.8129 | 188.5401 | 203.6131 | 200.9607
882.5979 | 388.0889 | 188.7493 | 203.7702 | 200.8666
883.5979 | 388.4834 | 189.4364 | 203.2889 | 201.222
884.5979 | 391.7602 | 189.4969 | 203.2126 | 200.9517
885.5979 | 390.8576 | 189.3923 | 203.3981 | 201.2788
886.5979 | 390.2159 | 189.8987 | 203.6252 | 201.3372
887.5979 | 393.8667 | 189.8375 | 203.5731 | 201.4434
888.5979 | 391.6951 | 189.669 | 203.6996 | 201.4823
889.5979 | 391.7918 | 189.376 | 203.4822 | 201.9502
890.5979 | 389.8839 | 189.3938 | 203.3508 | 201.5538
891.5979 | 390.3326 | 189.5263 | 203.2069 | 201.616
892.5979 | 391.2079 | 189.573 | 203.4143 | 201.4977
893.5979 | 391.7354 | 190.1521 | 203.3342 | 201.2694
894.5979 | 392.8469 | 190.3773 | 203.6354 | 201.5794
895.5979 | 392.885 | 190.2443 | 203.908 | 201.853
896.5979 | 392.4626 | 190.3961 | 203.9528 | 201.9588
897.5979 | 392.9866 | 190.472 | 203.8464 | 202.5537
898.5979 | 391.7563 | 190.1135 | 203.6333 | 202.8866
899.5979 | 397.8643 | 189.6556 | 203.676 | 202.6907
900.5979 | 399.3891 | 189.3284 | 203.7631 | 202.8599
901.5979 | 397.9532 | 189.1886 | 204.0153 | 202.5387
902.5979 | 397.2492 | 189.8359 | 204.2293 | 202.5314
903.5979 | 399.9532 | 189.6944 | 204.1898 | 202.3631
904.5979 | 397.4974 | 190.2329 | 204.2335 | 202.1956
905.5979 | 400.1613 | 190.6737 | 204.1592 | 202.2746
906.5979 | 402.3378 | 190.4677 | 204.0272 | 202.1069
907.5979 | 401.4502 | 189.6228 | 203.9487 | 201.9458
908.5979 | 402.7582 | 189.71 | 203.7101 | 201.559
909.5979 | 410.539 | 189.7948 | 203.6694 | 201.4899
910.5979 | 410.3355 | 189.3636 | 203.6387 | 201.4139
911.5979 | 409.1386 | 188.9016 | 203.5043 | 201.2899
912.5979 | 410.3778 | 189.0479 | 203.6662 | 201.115
913.5979 | 413.902 | 189.6695 | 204.624 | 201.3078
914.5979 | 418.7713 | 190.5051 | 204.343 | 201.2108
915.5979 | 428.8677 | 190.7633 | 204.2576 | 202.5396
916.5979 | 427.9025 | 190.6394 | 204.6 | 203.0847
917.5979 | 428.0934 | 191.0983 | 204.7058 | 203.926
918.5979 | 431.4948 | 191.3343 | 205.1927 | 204.448
919.5979 | 431.7562 | 191.037 | 205.0821 | 205.5743
920.5979 | 431.3278 | 190.9215 | 206.0649 | 206.1659
921.5979 | 431.2401 | 191.3662 | 206.0378 | 206.5148
922.5979 | 436.3067 | 191.0429 | 206.4211 | 206.6904
923.5979 | 444.7062 | 191.0041 | 206.808 | 206.6764
924.5979 | 450.2256 | 190.3823 | 207.0202 | 206.4999
925.5979 | 451.5971 | 190.5377 | 207.397 | 206.3557
926.5979 | 450.7879 | 190.1662 | 207.1091 | 205.9009
927.5979 | 449.7269 | 190.7801 | 208.2268 | 205.8361
928.5979 | 449.6489 | 191.3215 | 208.3957 | 205.8722
929.5979 | 449.3593 | 191.8638 | 208.6881 | 205.9455
930.5979 | 446.8056 | 191.9584 | 209.6646 | 206.7763
931.5979 | 453.2134 | 191.9352 | 209.9775 | 206.3107
932.5979 | 451.6667 | 192.883 | 210.0718 | 206.5017
933.5979 | 454.2655 | 193.9558 | 210.0177 | 207.158
934.5979 | 452.8805 | 194.4741 | 210.0457 | 207.6902
935.5979 | 457.2377 | 195.0732 | 210.7704 | 207.8827
936.5979 | 453.8817 | 196.526 | 211.699 | 208.1239
937.5979 | 461.0757 | 196.9078 | 211.9537 | 208.7641
938.5979 | 461.3618 | 197.7993 | 211.9563 | 209.1844
939.5979 | 458.5592 | 198.3074 | 212.2889 | 209.4506
940.5979 | 458.3674 | 198.866 | 212.5927 | 209.6315
941.5979 | 459.5966 | 199.0315 | 213.3082 | 210.5372
942.5979 | 465.2819 | 199.2117 | 213.6428 | 210.6399
943.5979 | 466.029 | 199.6974 | 213.7322 | 210.8817
944.5979 | 465.9091 | 200.3676 | 213.9999 | 211.1923
945.5979 | 464.4135 | 200.4531 | 214.5168 | 211.863
946.5979 | 461.1157 | 199.9555 | 214.5509 | 211.8484
947.5979 | 462.8633 | 199.6566 | 214.9517 | 212.1842
948.5979 | 462.1435 | 199.1388 | 214.787 | 212.2529
949.5979 | 467.4352 | 199.1998 | 215.4332 | 212.0556
950.5979 | 466.2599 | 199.8982 | 215.2449 | 212.3852
951.5979 | 469.9795 | 199.526 | 215.2066 | 212.2896
952.5979 | 470.0224 | 199.7394 | 215.0929 | 211.8845
953.5979 | 467.9049 | 200.3772 | 215.2953 | 212.4559
954.5979 | 468.8483 | 200.0591 | 215.1164 | 212.5406
955.5979 | 468.9274 | 200.5677 | 216.0988 | 212.8168
956.5979 | 470.6903 | 201.0893 | 216.4507 | 213.3432
957.5979 | 470.4545 | 201.622 | 216.3989 | 213.503
958.5979 | 472.1744 | 202.1892 | 216.6623 | 213.5879
959.5979 | 470.0793 | 202.4222 | 216.6962 | 213.6302
960.5979 | 466.5583 | 202.4391 | 217.0035 | 214.629
961.5979 | 464.0201 | 202.2531 | 217.3286 | 214.679
962.5979 | 476.3855 | 202.1081 | 217.4257 | 215.2653
963.5979 | 475.6723 | 202.1914 | 218.082 | 215.7714
964.5979 | 476.432 | 202.0157 | 218.7205 | 215.8933
965.5979 | 479.2051 | 202.3395 | 218.4055 | 215.7388
966.5979 | 480.382 | 202.868 | 218.4002 | 215.3428
967.5979 | 477.8915 | 203.5764 | 219.1054 | 215.2717
968.5979 | 475.9019 | 204.3518 | 219.7772 | 215.9871
969.5979 | 476.3815 | 204.7714 | 220.058 | 216.3255
970.5979 | 474.5426 | 205.4358 | 219.9632 | 217.4475
971.5979 | 488.8055 | 206.0183 | 220.9516 | 218.139
972.5979 | 492.4562 | 205.849 | 220.7643 | 218.4881
973.5979 | 492.5846 | 206.0245 | 220.7069 | 218.3086
974.5979 | 492.141 | 206.2281 | 221.5027 | 218.2023
975.5979 | 489.1355 | 205.9746 | 221.0931 | 218.9781
976.5979 | 488.0107 | 206.1142 | 220.9922 | 219.1325
977.5979 | 494.5175 | 206.9524 | 221.2628 | 219.1645
978.5979 | 500.8556 | 207.169 | 221.119 | 218.7806
979.5979 | 503.9899 | 207.657 | 220.6733 | 219.2027
980.5979 | 512.7092 | 208.4558 | 221.219 | 219.7206
981.5979 | 513.8218 | 208.2495 | 221.3706 | 219.8555
982.5979 | 515.3537 | 207.7126 | 221.6155 | 220.1046
983.5979 | 516.8855 | 207.7112 | 221.4851 | 219.9489
984.5979 | 520.7015 | 207.9719 | 221.1875 | 219.7987
985.5979 | 522.2237 | 207.6005 | 221.4408 | 220.3297
986.6135 | 523.0386 | 207.7935 | 221.7502 | 220.429
987.5979 | 533.6302 | 208.119 | 222.6113 | 220.3863
988.5979 | 527.62 | 207.8955 | 222.5959 | 220.6747
989.5979 | 526.6735 | 208.572 | 222.6648 | 220.7488
990.5979 | 526.618 | 209.4414 | 222.9545 | 220.8217
991.5979 | 527.7251 | 209.5453 | 221.8098 | 221.1569
992.5979 | 532.2581 | 209.9871 | 222.1445 | 220.7689
993.5979 | 543.0728 | 210.0591 | 222.1613 | 220.9731
994.5979 | 541.3123 | 209.5648 | 222.8709 | 220.9179
995.5979 | 541.9353 | 209.7046 | 222.5901 | 221.0725
996.5979 | 537.4012 | 209.6473 | 223.0581 | 221.2956
997.5979 | 545.32 | 209.5804 | 223.4418 | 220.9264
998.5979 | 549.8473 | 210.0428 | 223.5229 | 221.1727
999.5979 | 545.1382 | 210.2169 | 223.0285 | 221.674
1000.5979 | 543.6297 | 210.826 | 222.9442 | 221.8626
1001.5979 | 540.9295 | 211.0909 | 223.3056 | 221.6147
1002.5979 | 551.032 | 211.4175 | 223.5354 | 222.0625
1003.5979 | 546.7183 | 212.6024 | 222.8833 | 223.3413
1004.5979 | 547.5668 | 212.6056 | 223.8454 | 223.483
1005.5979 | 546.0061 | 211.808 | 223.8051 | 223.0818
1006.5979 | 549.419 | 211.4782 | 223.7874 | 222.6642
1007.5979 | 547.2336 | 210.7505 | 223.3558 | 222.5158
1008.5979 | 541.9058 | 210.3582 | 222.8597 | 222.5411
1009.5979 | 541.564 | 210.7838 | 223.1062 | 222.3725
1010.5979 | 540.6441 | 211.3817 | 223.254 | 222.1639
1011.5979 | 542.1099 | 211.3338 | 223.2292 | 222.016
1012.5979 | 537.0882 | 211.0751 | 222.9791 | 221.6331
1013.5979 | 533.7157 | 211.5897 | 222.8752 | 222.0912
1014.5979 | 531.6374 | 211.6941 | 222.9213 | 221.881
1015.5979 | 529.578 | 211.7074 | 222.4638 | 222.368
1016.5979 | 529.4322 | 211.3929 | 222.3552 | 222.2543
1017.5979 | 528.7054 | 211.2929 | 222.1113 | 222.1247
1018.5979 | 523.4472 | 212.2611 | 222.4302 | 222.0293
1019.5979 | 523.8967 | 211.3642 | 222.2981 | 222.3903
1020.5979 | 523.1874 | 211.0493 | 222.8254 | 222.6517
1021.5979 | 529.5775 | 210.7293 | 223.2313 | 222.8166
1022.5979 | 532.2929 | 210.8268 | 223.3323 | 222.9731
1023.5979 | 534.9363 | 211.7944 | 223.741 | 223.4032
1024.5979 | 532.5173 | 211.8387 | 224.1558 | 223.5645
1025.5979 | 528.6751 | 211.4657 | 224.5796 | 223.7813
1026.5979 | 531.2863 | 211.8547 | 224.5445 | 223.5203
1027.5979 | 532.1417 | 212.6589 | 224.769 | 223.0864
1028.5979 | 530.8053 | 212.7155 | 225.4018 | 222.9348
1029.5979 | 526.7042 | 212.5891 | 225.2852 | 222.6198
1030.5979 | 526.0177 | 212.8944 | 225.1078 | 222.3254
1031.5979 | 526.8743 | 212.8232 | 224.7946 | 221.6805
1032.5979 | 526.9277 | 212.5202 | 224.5796 | 221.333
1033.5979 | 536.0546 | 212.4551 | 224.3946 | 221.3091
1034.5979 | 536.2166 | 212.1212 | 224.5114 | 220.5391
1035.5979 | 537.2178 | 212.2248 | 225.3461 | 220.34
1036.5979 | 533.2771 | 212.7926 | 225.7577 | 220.7142
1037.5979 | 531.143 | 213.741 | 226.5005 | 221.6606
1038.5979 | 530.2936 | 213.9906 | 227.3198 | 222.0251
1039.5979 | 538.1007 | 214.4871 | 227.6061 | 222.2776
1040.5979 | 541.4406 | 214.3071 | 227.1592 | 222.3803
1041.5979 | 544.0335 | 214.6559 | 226.8922 | 222.0311
1042.5979 | 546.2473 | 215.0524 | 227.2338 | 221.8393
1043.5979 | 556.4086 | 214.6902 | 226.9128 | 222.3525
1044.5979 | 559.6961 | 214.6975 | 226.5115 | 222.6505
1045.5979 | 559.0556 | 214.806 | 226.5981 | 223.0489
1046.5979 | 557.2627 | 215.0413 | 226.651 | 222.7457
1047.5979 | 565.1182 | 214.6983 | 227.3779 | 222.5909
1048.5979 | 567.9188 | 215.2532 | 227.595 | 222.9033
1049.5979 | 573.6722 | 214.7978 | 228.1368 | 223.2676
1050.5979 | 576.3727 | 214.3024 | 227.9641 | 223.5043
1051.5979 | 577.1369 | 213.5802 | 228.1403 | 223.9444
1052.5979 | 582.433 | 213.1779 | 227.831 | 223.7177
1053.5979 | 584.3317 | 213.7342 | 227.7732 | 223.8011
1054.5979 | 589.5129 | 213.3893 | 227.6034 | 223.9503
1055.5979 | 586.9441 | 213.827 | 227.9201 | 224.2817
1056.5979 | 590.4555 | 213.3641 | 227.8662 | 223.9962
1057.5979 | 599.7924 | 213.0748 | 227.5206 | 224.1232
1058.5979 | 603.6784 | 213.3564 | 228.257 | 224.5854
1059.5979 | 607.6555 | 212.6559 | 227.8992 | 224.6656
1060.5979 | 608.7876 | 212.3258 | 227.5141 | 224.6891
1061.5979 | 611.0764 | 212.9072 | 227.5864 | 225.0678
1062.5979 | 615.266 | 213.418 | 227.7152 | 225.667
1063.5979 | 615.473 | 215.1337 | 228.0449 | 224.9686
1064.5979 | 615.1154 | 215.8468 | 228.8479 | 225.398
1065.5979 | 611.4314 | 215.8026 | 228.8699 | 225.868
1066.5979 | 609.1342 | 216.2183 | 229.1873 | 227.0702
1067.5979 | 610.5253 | 216.6051 | 228.888 | 227.4844
1068.5979 | 613.9044 | 216.367 | 229.0223 | 227.7301
1069.5979 | 615.2546 | 216.394 | 229.2887 | 229.1674
1070.5979 | 618.6357 | 216.2284 | 229.2191 | 229.0472
1071.5979 | 620.0664 | 216.4679 | 229.9875 | 229.5175
1072.5979 | 622.6059 | 215.8844 | 229.5925 | 229.6618
1073.5979 | 625.4657 | 216.0034 | 229.7959 | 229.0569
1074.5979 | 622.9654 | 216.0338 | 229.8715 | 229.3273
1075.5979 | 620.243 | 215.8617 | 229.7631 | 229.4561
1076.5979 | 620.5058 | 215.9189 | 229.8271 | 229.5176
1077.5979 | 620.5958 | 216.2073 | 230.0175 | 229.1708
1078.5979 | 624.4431 | 216.3127 | 229.3829 | 228.4279
1079.5979 | 623.278 | 216.2866 | 229.673 | 228.5711
1080.5979 | 621.1309 | 216.2371 | 229.6688 | 228.5741
1081.5979 | 624.3454 | 216.6767 | 229.9702 | 228.1956
1082.5979 | 625.1691 | 216.7584 | 230.9326 | 228.832
1083.5979 | 626.6774 | 217.1578 | 231.0763 | 228.5686
1084.5979 | 628.3715 | 217.5005 | 231.1036 | 228.3065
1085.5979 | 631.0181 | 217.5199 | 230.8664 | 228.0209
1086.5979 | 632.8001 | 217.9657 | 231.213 | 227.7161
1087.5979 | 638.1954 | 217.3875 | 231.5145 | 227.1709
1088.5979 | 637.9264 | 216.8728 | 231.3684 | 226.8521
1089.5979 | 642.5385 | 216.8224 | 231.473 | 227.1156
1090.5979 | 641.1434 | 216.7771 | 231.5605 | 227.0663
1091.6135 | 641.8146 | 216.595 | 232.0211 | 227.534
1092.5979 | 639.8076 | 216.1203 | 231.8475 | 227.3547
1093.5979 | 639.6107 | 216.5291 | 231.9624 | 227.7569
1094.5979 | 638.8655 | 216.1355 | 231.9158 | 227.4553
1095.5979 | 638.9995 | 215.9872 | 231.944 | 227.6398
1096.5979 | 639.9484 | 216.1276 | 231.7808 | 227.3782
1097.5979 | 641.3936 | 216.8854 | 232.3964 | 227.3706
1098.5979 | 644.8578 | 216.9271 | 232.2049 | 227.9829
1099.5979 | 651.2594 | 217.3557 | 232.9669 | 228.2873
1100.5979 | 653.1605 | 218.9007 | 233.5752 | 228.3301
1101.5979 | 654.2931 | 218.2615 | 234.6881 | 229.2507
1102.5979 | 656.4741 | 218.0894 | 234.3824 | 229.2819
1103.5979 | 658.1614 | 218.1207 | 234.2077 | 229.0372
1104.5979 | 658.4123 | 218.633 | 233.605 | 228.9133
1105.5979 | 656.8004 | 219.307 | 234.4069 | 229.3632
1106.5979 | 654.5533 | 219.9839 | 233.3857 | 230.1835
1107.5979 | 658.1659 | 219.779 | 234.1344 | 230.1588
1108.5979 | 661.1924 | 220.1253 | 234.4826 | 230.1449
1109.5979 | 665.3953 | 220.5333 | 234.8649 | 230.642
1110.5979 | 667.3569 | 220.936 | 235.0029 | 230.9453
1111.5979 | 669.0425 | 221.2919 | 235.1321 | 230.6309
1112.5979 | 671.2135 | 221.6342 | 234.6298 | 230.9205
1113.5979 | 673.3992 | 221.6781 | 235.4755 | 231.2127
1114.5979 | 678.0635 | 221.8885 | 235.5603 | 231.5237
1115.5979 | 676.7169 | 222.8308 | 236.3359 | 231.5
1116.5979 | 682.4676 | 222.9987 | 237.0292 | 232.9477
1117.5979 | 685.2352 | 223.3913 | 237.114 | 234.059
1118.5979 | 687.5754 | 223.5768 | 236.3914 | 235.0421
1119.5979 | 684.8221 | 224.4843 | 236.5686 | 234.3785
1120.5979 | 685.5411 | 224.5594 | 237.0788 | 234.4219
1121.5979 | 693.3493 | 224.9 | 237.4166 | 234.5741
1122.5979 | 693.754 | 225.3114 | 237.2176 | 235.3574
1123.5979 | 695.4371 | 225.1877 | 237.3517 | 235.3078
1124.5979 | 699.7615 | 225.0291 | 237.4195 | 235.6039
1125.5979 | 701.1964 | 225.5167 | 237.897 | 235.7728
1126.6135 | 698.9982 | 225.302 | 237.9888 | 235.9039
1127.5979 | 699.0121 | 225.1481 | 238.2323 | 236.3959
1128.5979 | 697.3395 | 225.3757 | 238.2752 | 237.0067
1129.5979 | 698.4391 | 225.6586 | 238.6029 | 237.292
1130.5979 | 704.4767 | 226.0227 | 238.9145 | 237.7164
1131.5979 | 705.4885 | 226.5027 | 239.0642 | 237.8457
1132.5979 | 700.6704 | 226.4299 | 239.1727 | 237.9529
1133.5979 | 698.7176 | 227.1009 | 239.2303 | 237.9148
1134.5979 | 699.9388 | 227.0374 | 239.5632 | 237.574
1135.5979 | 695.3203 | 227.3341 | 239.6663 | 237.5164
1136.5979 | 690.2199 | 227.7201 | 239.5871 | 238.2766
1137.5979 | 684.9502 | 227.4692 | 239.2808 | 238.8892
1138.5979 | 683.5388 | 227.2685 | 239.0924 | 238.6561
1139.5979 | 677.0501 | 228.0956 | 240.0259 | 238.9988
1140.5979 | 676.5746 | 228.1659 | 239.6564 | 238.8707
1141.5979 | 678.9919 | 228.8355 | 239.9667 | 238.9384
1142.5979 | 690.5052 | 228.9262 | 240.8773 | 239.5305
1143.5979 | 688.6425 | 228.9503 | 242.0781 | 239.6572
1144.5979 | 690.3969 | 229.7524 | 243.2811 | 240.1291
1145.5979 | 688.813 | 229.8559 | 244.266 | 241.2944
1146.5979 | 690.2886 | 230.8195 | 244.7724 | 242.1566
1147.5979 | 690.5828 | 232.0618 | 246.4854 | 242.5878
1148.5979 | 686.3907 | 232.8275 | 246.7852 | 243.1741
1149.5979 | 685.5614 | 232.6573 | 247.6319 | 243.4419
1150.5979 | 691.9989 | 232.8714 | 248.2055 | 243.3281
1151.5979 | 689.388 | 232.5541 | 248.8319 | 243.3124
1152.5979 | 689.5328 | 232.7114 | 249.1311 | 243.5346
1153.5979 | 688.9424 | 231.9839 | 249.1018 | 243.5927
1154.5979 | 684.6083 | 232.1418 | 249.3281 | 244.3446
1155.5979 | 680.2011 | 232.1851 | 250.3111 | 245.0545
1156.5979 | 679.2733 | 231.5209 | 250.499 | 245.3396
1157.5979 | 679.6187 | 231.6635 | 250.8712 | 245.7358
1158.5979 | 674.6225 | 231.3596 | 251.2667 | 246.1332
1159.5979 | 669.0986 | 231.8119 | 251.8908 | 246.0975
1160.5979 | 671.3941 | 232.3097 | 251.8329 | 246.2752
1161.5979 | 672.253 | 232.0622 | 252.6068 | 246.1323
1162.5979 | 668.6306 | 232.3031 | 252.9204 | 246.5726
1163.5979 | 666.1359 | 233.1686 | 253.617 | 246.6561
1164.5979 | 663.1186 | 233.3509 | 254.3509 | 248.4975
1165.5979 | 665.6742 | 233.6871 | 255.2074 | 248.8094
1166.5979 | 660.8728 | 233.9982 | 256.1181 | 250.0324
1167.5979 | 658.031 | 234.2575 | 257.031 | 250.2918
1168.5979 | 661.8223 | 234.8565 | 256.8841 | 250.3425
1169.5979 | 660.868 | 235.5772 | 257.1332 | 250.4802
1170.5979 | 657.9332 | 235.9113 | 256.8699 | 250.5506
1171.5979 | 654.5259 | 236.2518 | 256.9012 | 251.3821
1172.5979 | 653.94 | 236.5734 | 257.3163 | 251.5064
1173.5979 | 654.9184 | 237.6729 | 257.1213 | 251.4394
1174.5979 | 657.1444 | 238.0139 | 256.8797 | 252.0195
1175.5979 | 659.2684 | 238.3936 | 256.5707 | 252.2498
1176.5979 | 658.0014 | 238.361 | 256.4555 | 251.7605
1177.5979 | 653.9063 | 238.7399 | 256.43 | 251.6831
1178.5979 | 653.6864 | 239.1464 | 256.2168 | 252.0737
1179.5979 | 652.8436 | 239.5044 | 256.3972 | 252.0445
1180.5979 | 652.992 | 239.9696 | 256.6769 | 252.0068
1181.6135 | 650.9797 | 240.793 | 258.0473 | 252.2222
1182.5979 | 649.6396 | 240.9491 | 258.1064 | 253.1651
1183.5979 | 647.307 | 241.5801 | 258.5686 | 254.3334
1184.5979 | 646.3176 | 242.3439 | 259.8021 | 254.1144
1185.5979 | 643.9624 | 242.6992 | 260.3082 | 254.4222
1186.5979 | 639.5969 | 242.6979 | 260.5324 | 255.5616
1187.5979 | 639.356 | 242.8162 | 260.4168 | 255.5497
1188.5979 | 639.9035 | 242.821 | 260.1888 | 255.6153
1189.5979 | 637.4361 | 241.7187 | 260.94 | 255.7302
1190.5979 | 638.1757 | 241.5867 | 260.748 | 256.0962
1191.5979 | 638.3305 | 241.6138 | 260.1601 | 256.4505
1192.5979 | 636.7484 | 241.204 | 259.9794 | 256.0412
1193.5979 | 636.2199 | 241.3408 | 259.7424 | 255.9722
1194.5979 | 634.9236 | 242.0383 | 260.5406 | 255.3651
1195.5979 | 635.1005 | 242.1319 | 260.9239 | 255.2628
1196.5979 | 636.1595 | 242.6046 | 261.1154 | 255.8936
1197.5979 | 634.5417 | 242.8049 | 261.3336 | 256.3059
1198.5979 | 631.8915 | 243.1488 | 262.5278 | 256.9659
1199.5979 | 633.3845 | 243.3784 | 262.7741 | 257.2613
1200.5979 | 634.6845 | 243.6182 | 262.9324 | 258.1699
1201.5979 | 633.5405 | 243.597 | 262.5893 | 258.2117
1202.5979 | 633.2303 | 244.2672 | 262.3693 | 258.0704
1203.5979 | 632.0464 | 243.5945 | 262.5444 | 259.0622
1204.5979 | 629.9903 | 243.5091 | 262.6859 | 258.1702
1205.5979 | 630.4455 | 243.7157 | 262.1267 | 257.3126
1206.5979 | 632.6975 | 243.6563 | 261.8363 | 256.7736
1207.5979 | 629.7981 | 244.357 | 261.5241 | 256.4075
1208.5979 | 628.0245 | 245.1876 | 261.9518 | 256.9956
1209.5979 | 627.2277 | 244.5679 | 261.3009 | 257.3119
1210.5979 | 626.7691 | 244.7105 | 261.8112 | 257.1699
1211.5979 | 625.0563 | 245.0189 | 262.0324 | 257.0937
1212.5979 | 626.6564 | 245.2288 | 261.5102 | 257.244
1213.5979 | 624.2826 | 245.3359 | 261.7122 | 257.0497
1214.5979 | 625.6897 | 245.1272 | 261.7122 | 257.515
1215.5979 | 623.7066 | 245.2919 | 261.8892 | 257.7257
1216.5979 | 624.7346 | 245.9157 | 262.0257 | 257.9826
1217.5979 | 623.0793 | 245.7892 | 262.0604 | 257.9636
1218.5979 | 623.5459 | 246.2065 | 262.0945 | 258.746
1219.5979 | 621.784 | 246.6906 | 262.6712 | 258.9973
1220.5979 | 621.2937 | 246.9205 | 262.92 | 259.6261
1221.5979 | 620.057 | 247.6624 | 263.1322 | 260.4698
1222.5979 | 617.6046 | 248.394 | 263.0488 | 260.5009
1223.5979 | 618.0179 | 248.9519 | 263.9866 | 259.8619
1224.5979 | 617.6048 | 248.8462 | 264.9386 | 259.3214
1225.5979 | 615.9965 | 249.7495 | 265.2756 | 259.9891
1226.5979 | 617.7021 | 250.677 | 265.7854 | 260.1017
1227.5979 | 617.9612 | 251.313 | 266.1357 | 260.1928
1228.5979 | 617.8812 | 252.1475 | 266.7815 | 260.2055
1229.5979 | 616.2333 | 253.2209 | 267.3447 | 260.1598
1230.5979 | 616.2624 | 254.8405 | 267.8922 | 260.6484
1231.5979 | 617.4415 | 255.9782 | 268.3685 | 260.4295
1232.5979 | 618.4847 | 256.5376 | 269.3113 | 260.9647
1233.5979 | 620.1708 | 256.7892 | 269.8413 | 260.851
1234.5979 | 621.2507 | 258.2483 | 270.6547 | 260.7164
1235.5979 | 622.2104 | 257.835 | 270.8343 | 261.0647
1236.5979 | 621.6704 | 258.4699 | 270.7395 | 261.4348
1237.5979 | 622.2616 | 258.7563 | 270.4739 | 262.4044
1238.5979 | 623.2876 | 258.5997 | 270.3556 | 262.7554
1239.5979 | 624.8423 | 258.6165 | 270.2065 | 262.6575
1240.5979 | 626.6778 | 259.1012 | 270.6125 | 262.8541
1241.6135 | 625.5843 | 259.5899 | 270.4641 | 263.2426
1242.5979 | 624.4094 | 259.1499 | 270.5797 | 263.9793
1243.5979 | 623.5637 | 258.8022 | 271.1398 | 265.1017
1244.5979 | 622.6286 | 258.8951 | 271.2257 | 266.3618
1245.5979 | 622.9652 | 258.9678 | 270.8617 | 266.5592
1246.5979 | 623.3387 | 258.4063 | 271.4399 | 266.8694
1247.5979 | 622.61 | 258.7158 | 271.3845 | 266.7314
1248.5979 | 622.2227 | 258.8652 | 271.0688 | 266.6863
1249.5979 | 622.6649 | 259.0634 | 271.3097 | 266.7326
1250.5979 | 623.9968 | 259.4408 | 271.6052 | 266.4586
1251.5979 | 624.0566 | 259.4064 | 271.4757 | 266.4446
1252.5979 | 624.9936 | 259.8964 | 272.2662 | 266.3185
1253.5979 | 628.4107 | 259.2567 | 272.7548 | 266.1477
1254.5979 | 629.8656 | 259.2048 | 273.474 | 266.3199
1255.5979 | 631.3358 | 259.3631 | 274.053 | 266.3895
1256.5979 | 630.1958 | 259.0995 | 274.1626 | 267.2232
1257.5979 | 626.4095 | 259.2134 | 274.2593 | 268.4053
1258.5979 | 627.2094 | 259.0486 | 273.7694 | 269.0725
1259.5979 | 629.8576 | 259.4142 | 274.2249 | 269.5229
1260.5979 | 632.2453 | 259.8829 | 274.6453 | 269.7389
1261.5979 | 631.6386 | 260.5582 | 274.9602 | 269.634
1262.5979 | 633.6696 | 260.8501 | 275.4125 | 270.4966
1263.5979 | 634.6569 | 261.1576 | 275.9898 | 270.7236
1264.5979 | 633.5293 | 261.3783 | 276.1836 | 271.3834
1265.5979 | 634.5613 | 262.0628 | 275.6818 | 271.3331
1266.5979 | 635.5728 | 262.2457 | 275.3123 | 271.7423
1267.5979 | 635.281 | 262.599 | 274.9775 | 271.6998
1268.5979 | 634.2311 | 263.2436 | 275.0843 | 271.1394
1269.5979 | 634.2854 | 263.1028 | 275.1022 | 270.7671
1270.5979 | 634.5386 | 263.7425 | 275.5174 | 271.1488
1271.5979 | 634.6568 | 264.1269 | 276.4654 | 271.5143
1272.5979 | 635.3922 | 264.6175 | 277.3395 | 271.3406
1273.5979 | 636.501 | 264.6041 | 277.3366 | 271.1156
1274.5979 | 636.3631 | 264.6609 | 277.7515 | 272.3213
1275.5979 | 633.3074 | 265.1199 | 278.5452 | 272.857
1276.5979 | 632.5355 | 265.8398 | 278.7089 | 272.5707
1277.5979 | 633.0446 | 265.6431 | 278.8281 | 272.7852
1278.5979 | 634.6116 | 266.3729 | 279.894 | 272.9886
1279.5979 | 635.0671 | 266.1475 | 279.8718 | 273.3201
1280.5979 | 635.9796 | 267.5303 | 280.1605 | 274.1835
1281.5979 | 635.3051 | 267.7066 | 280.8818 | 274.4834
1282.5979 | 635.3225 | 268.3108 | 281.3546 | 274.6583
1283.5979 | 636.4338 | 268.6742 | 282.1787 | 275.4576
1284.5979 | 638.2294 | 269.3385 | 282.5988 | 275.3914
1285.5979 | 642.5702 | 268.9128 | 282.4419 | 275.6017
1286.5979 | 642.6523 | 268.8439 | 282.1607 | 276.4929
1287.5979 | 641.675 | 270.1969 | 282.271 | 276.1529
1288.5979 | 641.5208 | 270.0857 | 282.7694 | 276.6522
1289.5979 | 641.4345 | 269.8542 | 283.1335 | 276.9447
1290.5979 | 643.5435 | 270.0645 | 282.9377 | 276.6598
1291.5979 | 645.8042 | 271.094 | 282.4254 | 277.1699
1292.5979 | 645.2166 | 270.5473 | 282.157 | 278.2371
1293.5979 | 646.2817 | 270.8179 | 281.9618 | 278.6097
1294.5979 | 647.1293 | 271.8423 | 281.7525 | 277.8455
1295.5979 | 647.7582 | 271.6743 | 281.4193 | 277.6176
1296.5979 | 650.1693 | 272.7776 | 280.8784 | 277.9674
1297.5979 | 652.2776 | 272.6046 | 280.7589 | 277.4735
1298.5979 | 654.3783 | 272.2091 | 280.5351 | 277.0626
1299.5979 | 653.9013 | 273.0124 | 280.6685 | 276.7713
1300.5979 | 653.4811 | 273.4077 | 280.7869 | 276.976
1301.6135 | 653.776 | 273.4366 | 280.5099 | 277.7951
1302.5979 | 655.9414 | 273.1996 | 280.1905 | 277.7404
1303.5979 | 660.6437 | 273.108 | 281.0924 | 277.8224
1304.5979 | 663.7789 | 272.3326 | 280.9532 | 277.3478
1305.5979 | 665.5038 | 272.3648 | 280.6722 | 276.8627
1306.5979 | 666.3975 | 272.8712 | 280.4229 | 276.7895
1307.5979 | 665.77 | 272.782 | 280.358 | 277.1784
1308.5979 | 665.2423 | 272.7847 | 280.5196 | 276.9228
1309.5979 | 666.6918 | 272.6832 | 281.0116 | 276.5288
1310.5979 | 668.2334 | 272.1187 | 281.1291 | 277.0651
1311.5979 | 668.3433 | 272.8948 | 281.3072 | 278.1312
1312.5979 | 667.1952 | 272.8957 | 281.8733 | 278.7146
1313.5979 | 666.0801 | 273.2737 | 282.0585 | 278.8144
1314.5979 | 664.1598 | 273.4845 | 282.0833 | 279.2357
1315.5979 | 666.7179 | 273.4893 | 282.351 | 279.114
1316.5979 | 668.3056 | 273.2451 | 282.5981 | 279.0666
1317.5979 | 668.2049 | 273.3027 | 283.0734 | 279.0331
1318.5979 | 669.119 | 273.3928 | 282.9179 | 279.4228
1319.5979 | 667.8025 | 273.3767 | 282.7834 | 279.5261
1320.5979 | 668.7848 | 273.6935 | 282.6884 | 279.0678
1321.5979 | 667.1741 | 274.0127 | 282.8943 | 279.8489
1322.6135 | 667.7019 | 273.7818 | 282.7611 | 279.9637
1323.5979 | 667.4144 | 273.6175 | 282.5608 | 280.5994
1324.5979 | 664.4787 | 274.0272 | 282.7056 | 280.083
1325.5979 | 665.0286 | 274.5569 | 282.9273 | 279.3636
1326.5979 | 665.9463 | 274.896 | 283.1799 | 279.2475
1327.5979 | 668.062 | 274.8245 | 282.6405 | 278.8112
1328.5979 | 669.0634 | 275.1222 | 282.5898 | 278.7367
1329.5979 | 669.1752 | 275.8047 | 282.6154 | 278.8945
1330.5979 | 668.6753 | 275.8549 | 282.5264 | 279.7935
1331.5979 | 669.3759 | 275.6683 | 283.5122 | 280.0872
1332.5979 | 668.0806 | 275.7369 | 282.9707 | 279.4041
1333.5979 | 670.5934 | 275.7538 | 282.327 | 279.2752
1334.5979 | 670.3163 | 275.3918 | 282.5224 | 278.3911
1335.5979 | 669.495 | 275.1982 | 283.5691 | 278.5691
1336.5979 | 669.6199 | 275.6561 | 285.018 | 279.6404
1337.5979 | 670.9907 | 275.7145 | 285.586 | 280.1228
1338.5979 | 672.3092 | 275.7353 | 286.4772 | 280.689
1339.5979 | 672.3628 | 276.2378 | 286.931 | 280.7458
1340.5979 | 670.087 | 276.3746 | 287.1148 | 281.0883
1341.5979 | 667.8565 | 276.684 | 287.6548 | 281.5146
1342.5979 | 665.7237 | 277.3027 | 288.3534 | 282.1576
1343.5979 | 664.2608 | 277.2119 | 289.065 | 283.0083
1344.5979 | 666.2989 | 277.5382 | 290.0906 | 283.1942
1345.5979 | 665.6723 | 278.5234 | 290.6983 | 283.2578
1346.5979 | 666.0019 | 278.5409 | 291.6268 | 283.2934
1347.5979 | 666.8512 | 278.6172 | 291.3015 | 283.7844
1348.5979 | 666.3929 | 278.7619 | 290.885 | 283.2627
1349.5979 | 665.3034 | 278.6972 | 292.4988 | 282.9387
1350.5979 | 665.7956 | 278.8119 | 293.2596 | 283.4013
1351.5979 | 664.7369 | 278.7731 | 293.8717 | 283.2216
1352.6135 | 664.9 | 278.9316 | 293.5221 | 283.2482
1353.5979 | 668.5389 | 278.9003 | 293.9641 | 282.7574
1354.5979 | 668.4988 | 279.2505 | 293.8827 | 282.1926
1355.5979 | 667.457 | 280.0245 | 293.0351 | 281.8848
1356.5979 | 668.8822 | 280.091 | 292.592 | 281.7491
1357.5979 | 670.4924 | 280.3368 | 292.8956 | 282.8088
1358.5979 | 670.6518 | 280.1946 | 293.4289 | 283.337
1359.6135 | 674.1418 | 279.946 | 293.1642 | 284.2421
1360.6135 | 674.9443 | 279.1745 | 293.0308 | 284.6218
1361.6135 | 676.0235 | 279.3068 | 292.9511 | 284.7601
1362.5979 | 675.8153 | 279.399 | 292.8988 | 284.7807
1363.5979 | 675.1453 | 279.2304 | 292.4772 | 285.5149
1364.5979 | 674.8887 | 279.3247 | 292.1459 | 285.968
1365.5979 | 675.7203 | 280.2149 | 291.8513 | 286.2943
1366.5979 | 678.0928 | 280.5467 | 292.4491 | 286.7867
1367.5979 | 678.7306 | 281.6017 | 292.3241 | 286.8315
1368.5979 | 680.1076 | 282.1847 | 292.478 | 287.4652
1369.5979 | 678.3948 | 282.4625 | 293.0486 | 287.6567
1370.5979 | 679.1666 | 282.424 | 294.9455 | 288.3941
1371.5979 | 677.6526 | 282.3187 | 294.9013 | 288.5507
1372.5979 | 677.8064 | 283.0776 | 294.9397 | 288.4912
1373.5979 | 678.6909 | 282.2729 | 294.5608 | 288.2027
1374.5979 | 678.0581 | 282.1956 | 294.7447 | 287.2879
1375.5979 | 676.8876 | 282.1053 | 294.7652 | 287.0415
1376.5979 | 676.1925 | 282.2056 | 294.4924 | 286.0112
1377.5979 | 672.6125 | 282.555 | 294.3253 | 286.6634
1378.5979 | 671.2125 | 282.7942 | 294.7558 | 286.1738
1379.5979 | 670.2867 | 283.4759 | 295.0301 | 286.3469
1380.5979 | 670.0686 | 283.6747 | 295.1559 | 286.4973
1381.5979 | 668.7428 | 284.0736 | 295.6259 | 286.745
1382.5979 | 670.319 | 284.0389 | 296.0415 | 286.8309
1383.5979 | 671.229 | 283.7143 | 295.62 | 287.5873
1384.5979 | 669.5735 | 284.1102 | 295.9046 | 288.2911
1385.5979 | 670.6914 | 284.2715 | 296.3823 | 288.2009
1386.5979 | 669.807 | 284.2321 | 296.2413 | 287.9276
1387.5979 | 671.5865 | 283.6167 | 295.8963 | 287.3477
1388.5979 | 673.0902 | 282.9778 | 295.6156 | 286.8171
1389.5979 | 672.3208 | 282.6551 | 295.8266 | 286.878
1390.5979 | 674.3824 | 283.3344 | 296.4747 | 287.6907
1391.5979 | 676.0147 | 284.2702 | 297.1488 | 287.5981
1392.5979 | 675.9406 | 283.913 | 297.3257 | 287.2951
1393.5979 | 676.7992 | 284.2001 | 298.0683 | 287.2864
1394.5979 | 678.3294 | 284.1778 | 298.8181 | 287.4647
1395.5979 | 679.4191 | 283.8891 | 299.0881 | 288.426
1396.5979 | 675.8368 | 283.4803 | 299.102 | 288.785
1397.5979 | 673.7496 | 283.6455 | 298.7344 | 288.6201
1398.5979 | 672.4123 | 283.9796 | 298.4709 | 288.1219
1399.5979 | 672.9937 | 284.5434 | 298.5844 | 288.3243
1400.5979 | 670.9382 | 284.4307 | 300.0009 | 289.2556
1401.5979 | 669.7842 | 284.3933 | 300.806 | 289.0921
1402.5979 | 668.6394 | 284.4332 | 301.9221 | 289.7297
1403.5979 | 668.8768 | 284.5678 | 302.3711 | 291.545
1404.5979 | 669.9303 | 284.3433 | 303.3773 | 291.985
1405.5979 | 672.5678 | 285.2077 | 304.8879 | 292.6672
1406.5979 | 677.0525 | 285.4824 | 306.3349 | 292.8653
1407.5979 | 680.0896 | 285.9394 | 306.8505 | 293.03
1408.5979 | 680.9635 | 286.2671 | 307.6647 | 293.6722
1409.5979 | 679.8505 | 286.9911 | 308.7133 | 293.9174
1410.5979 | 681.3849 | 287.1849 | 309.4377 | 294.7686
1411.5979 | 680.4249 | 287.1104 | 310.1674 | 295.0757
1412.6135 | 682.2942 | 288.4278 | 309.6796 | 295.7148
1413.5979 | 683.467 | 288.6169 | 309.4853 | 295.4803
1414.5979 | 682.1727 | 288.8432 | 309.7531 | 295.6588
1415.5979 | 682.2275 | 289.3896 | 310.4632 | 296.3479
1416.5979 | 682.1398 | 289.3988 | 311.1247 | 296.1988
1417.5979 | 682.6645 | 289.9243 | 311.0736 | 295.6192
1418.5979 | 681.7421 | 290.4048 | 311.7571 | 295.2928
1419.5979 | 682.0995 | 291.141 | 311.6525 | 294.7431
1420.5979 | 684.6096 | 291.3596 | 311.0574 | 294.2998
1421.5979 | 683.5461 | 291.7296 | 311.2978 | 294.5857
1422.5979 | 682.2261 | 291.877 | 310.7418 | 294.4456
1423.5979 | 677.4843 | 291.7541 | 310.2303 | 294.2511
1424.5979 | 675.6865 | 292.9217 | 309.9882 | 294.2332
1425.5979 | 677.9648 | 293.0658 | 310.7541 | 294.2821
1426.5979 | 680.2299 | 292.3765 | 311.5103 | 294.1818
1427.5979 | 679.7702 | 292.2193 | 311.6522 | 294.3437
1428.5979 | 680.8819 | 292.802 | 311.9932 | 294.4385
1429.5979 | 682.3701 | 293.175 | 311.6244 | 294.8162
1430.5979 | 681.6876 | 292.9293 | 311.4043 | 294.2558
1431.5979 | 676.6469 | 293.0254 | 311.1815 | 293.6474
1432.5979 | 676.2245 | 292.8573 | 310.4894 | 294.3576
1433.5979 | 676.4476 | 292.9339 | 310.1159 | 293.8961
1434.5979 | 677.4065 | 293.1834 | 309.7245 | 293.4959
1435.5979 | 678.6032 | 293.7729 | 309.2292 | 293.338
1436.5979 | 680.3829 | 294.517 | 309.125 | 293.4447
1437.5979 | 681.8422 | 294.4484 | 309.1447 | 293.563
1438.5979 | 684.9845 | 294.4687 | 308.6786 | 293.5577
1439.5979 | 688.2903 | 294.7655 | 308.7183 | 293.0878
1440.5979 | 689.9034 | 294.5567 | 309.294 | 293.9823
1441.5979 | 691.3199 | 295.4103 | 309.4793 | 293.7665
1442.5979 | 691.9407 | 295.2655 | 309.4119 | 293.6123
1443.5979 | 692.9918 | 295.5552 | 309.9954 | 293.9632
1444.5979 | 689.5601 | 294.3999 | 310.4471 | 293.4432
1445.5979 | 688.4237 | 294.64 | 310.5748 | 293.787
1446.5979 | 684.58 | 294.2862 | 310.2518 | 294.1589
1447.5979 | 684.4342 | 294.0343 | 308.8875 | 293.2872
1448.5979 | 684.5418 | 293.7177 | 308.2027 | 293.2851
1449.5979 | 685.3119 | 293.6169 | 307.8765 | 294.4389
1450.5979 | 685.102 | 293.569 | 307.9217 | 293.698
1451.5979 | 683.9143 | 293.4387 | 308.2872 | 293.8003
1452.5979 | 682.5235 | 293.1482 | 308.8737 | 293.4832
1453.5979 | 682.6772 | 292.9557 | 309.2275 | 293.0287
1454.5979 | 682.3446 | 292.6097 | 309.102 | 293.1126
1455.5979 | 681.3998 | 292.3384 | 309.0637 | 292.9174
1456.5979 | 684.0199 | 291.7863 | 309.593 | 293.0277
1457.5979 | 683.8902 | 292.1507 | 310.1147 | 293.3576
1458.5979 | 685.7468 | 291.6618 | 310.0516 | 292.4139
1459.5979 | 689.4166 | 291.8404 | 310.037 | 291.9963
1460.5979 | 689.6284 | 291.966 | 310.1445 | 292.0541
1461.5979 | 689.7194 | 291.9733 | 310.1341 | 292.2858
1462.5979 | 689.7767 | 292.8362 | 309.7261 | 293.4488
1463.5979 | 689.3995 | 293.3206 | 309.9264 | 294.1308
1464.5979 | 689.4442 | 293.1866 | 310.3137 | 294.0899
1465.5979 | 688.627 | 293.0894 | 309.9129 | 293.5162
1466.5979 | 686.8198 | 292.8461 | 308.8932 | 292.6804
1467.5979 | 684.068 | 293.5688 | 308.7825 | 292.5851
1468.5979 | 684.7664 | 294.002 | 309.1999 | 292.8096
1469.5979 | 686.2966 | 294.4171 | 309.0855 | 293.1053
1470.5979 | 688.8795 | 294.4795 | 308.8242 | 292.8632
1471.5979 | 692.5838 | 294.7756 | 309.9374 | 293.204
1472.5979 | 694.3097 | 294.2015 | 309.9758 | 293.5825
1473.5979 | 695.7332 | 293.9981 | 309.2203 | 293.5744
1474.5979 | 695.333 | 293.7574 | 309.3661 | 294.2205
1475.5979 | 696.2746 | 293.4884 | 309.2709 | 294.4383
1476.5979 | 694.5519 | 293.6525 | 309.2237 | 294.7831
1477.5979 | 691.1693 | 293.2837 | 308.6397 | 294.7523
1478.5979 | 687.9811 | 292.8826 | 308.7303 | 295.1473
1479.5979 | 687.8005 | 292.5636 | 308.2912 | 294.9432
1480.5979 | 687.8651 | 293.5101 | 309.1523 | 294.8458
1481.6135 | 688.0956 | 293.4464 | 308.9329 | 295.2429
1482.5979 | 687.4019 | 293.4014 | 308.6709 | 295.4954
1483.5979 | 687.1939 | 292.6674 | 308.5666 | 295.7723
1484.5979 | 683.1777 | 292.9195 | 308.6323 | 296.1175
1485.5979 | 680.7366 | 293.233 | 308.6239 | 295.8254
1486.5979 | 679.0135 | 293.85 | 308.877 | 295.4147
1487.5979 | 679.916 | 293.6152 | 308.4046 | 295.1868
1488.5979 | 679.4415 | 294.299 | 308.3343 | 295.406
1489.5979 | 681.9873 | 294.1995 | 308.541 | 294.7313
1490.5979 | 682.8638 | 294.4268 | 309.1096 | 296.0563
1491.5979 | 682.6296 | 293.98 | 308.7174 | 297.1444
1492.5979 | 681.8092 | 294.0343 | 308.6813 | 297.4517
1493.5979 | 683.7599 | 294.1759 | 308.6153 | 296.7289
1494.5979 | 681.5315 | 293.9966 | 308.6309 | 296.5164
1495.5979 | 682.1213 | 294.4508 | 308.8612 | 296.611
1496.5979 | 682.1425 | 294.583 | 309.0739 | 295.8534
1497.5979 | 679.3065 | 295.0924 | 308.6509 | 295.4816
1498.5979 | 675.1962 | 295.3458 | 308.7677 | 294.5287
1499.5979 | 671.2851 | 297.2314 | 308.3687 | 295.0927
1500.6135 | 669.1513 | 296.6762 | 309.1529 | 294.8754
1501.5979 | 670.467 | 296.8761 | 309.4131 | 295.8702
1502.5979 | 672.1185 | 297.507 | 310.4835 | 296.4398
1503.5979 | 675.5614 | 297.1598 | 310.9622 | 296.6208
1504.5979 | 675.3881 | 298.3196 | 311.4671 | 296.6337
1505.5979 | 675.7479 | 299.3095 | 310.9437 | 296.3883
1506.5979 | 679.8389 | 298.8682 | 310.9625 | 297.1068
1507.5979 | 680.9707 | 298.4474 | 311.0534 | 297.6441
1508.5979 | 682.187 | 299.4956 | 311.043 | 296.9523
1509.5979 | 681.5023 | 300.266 | 311.4968 | 297.4963
1510.5979 | 683.3417 | 300.871 | 312.2286 | 297.7679
1511.5979 | 680.9224 | 301.0047 | 313.5091 | 299.3026
1512.5979 | 682.4978 | 302.1841 | 314.5345 | 299.9361
1513.5979 | 684.081 | 302.4091 | 315.8183 | 300.2276
1514.5979 | 686.7329 | 303.249 | 316.5822 | 300.1828
1515.5979 | 689.8606 | 303.3501 | 317.0445 | 299.9964
1516.5979 | 693.1903 | 304.2502 | 317.2567 | 300.2499
1517.5979 | 696.5906 | 305.2544 | 317.598 | 299.7191
1518.5979 | 699.3131 | 305.6893 | 318.3571 | 301.6979
1519.5979 | 700.2037 | 306.4475 | 318.7369 | 302.4649
1520.5979 | 697.7508 | 306.6468 | 319.5999 | 302.3814
1521.5979 | 696.3624 | 307.6277 | 319.8754 | 302.9509
1522.5979 | 695.9692 | 307.9383 | 321.3467 | 303.4958
1523.5979 | 696.9407 | 307.8256 | 322.8695 | 305.9649
1524.5979 | 696.8816 | 309.1543 | 322.7977 | 306.5359
1525.5979 | 696.5493 | 309.6369 | 323.4912 | 307.1357
1526.5979 | 697.195 | 310.4237 | 323.8869 | 307.1909
1527.5979 | 696.4227 | 310.5137 | 324.1617 | 307.7149
1528.5979 | 697.4751 | 311.6225 | 324.311 | 306.9169
1529.5979 | 698.0625 | 312.0343 | 323.8276 | 308.3096
1530.5979 | 695.9524 | 311.9339 | 324.3805 | 308.1663
1531.5979 | 693.0213 | 312.5597 | 324.5333 | 308.2616
1532.6135 | 691.4544 | 312.3825 | 324.446 | 309.184
1533.5979 | 694.2855 | 312.0545 | 324.0752 | 308.8214
1534.5979 | 694.5054 | 312.2075 | 324.0982 | 308.3501
1535.5979 | 694.7348 | 312.8896 | 324.408 | 309.2815
1536.5979 | 694.9572 | 313.314 | 323.9109 | 309.6859
1537.5979 | 693.9275 | 313.5398 | 324.2329 | 308.6809
1538.5979 | 692.3749 | 313.9735 | 324.1317 | 308.2641
1539.5979 | 687.7501 | 313.8962 | 323.8108 | 308.1449
1540.5979 | 686.8589 | 313.8499 | 323.763 | 308.409
1541.5979 | 683.7989 | 314.0509 | 323.5404 | 308.6166
1542.5979 | 684.0914 | 314.6945 | 323.7172 | 309.7718
1543.5979 | 684.4488 | 315.1093 | 324.1657 | 310.9512
1544.5979 | 682.8235 | 315.6302 | 324.8455 | 311.1666
1545.5979 | 680.4083 | 316.3986 | 325.8946 | 311.281
1546.5979 | 679.799 | 316.7932 | 327.1521 | 312.1432
1547.5979 | 681.1499 | 316.8884 | 326.7581 | 312.8673
1548.5979 | 682.6335 | 316.635 | 326.9488 | 313.9442
1549.5979 | 686.8428 | 317.4314 | 326.8718 | 314.7757
1550.5979 | 688.9219 | 317.5093 | 327.5033 | 315.5103
1551.5979 | 691.657 | 317.3512 | 327.4511 | 316.5991
1552.5979 | 691.7116 | 317.5451 | 327.7116 | 316.2321
1553.5979 | 691.0502 | 318.3085 | 327.7415 | 315.3916
1554.5979 | 691.7194 | 319.1777 | 328.3215 | 315.2168
1555.5979 | 692.5049 | 319.062 | 327.8559 | 315.3807
1556.5979 | 692.124 | 318.6856 | 327.9308 | 316.1596
1557.5979 | 693.3696 | 319.5169 | 328.7244 | 316.4741
1558.5979 | 693.1554 | 319.5174 | 328.82 | 317.4295
1559.5979 | 691.6636 | 319.1248 | 328.7819 | 317.6362
1560.5979 | 689.1581 | 319.4913 | 329.437 | 317.2802
1561.5979 | 684.4117 | 320.4188 | 329.5865 | 317.36
1562.6135 | 681.7134 | 320.1259 | 329.6644 | 318.0051
1563.5979 | 682.6097 | 320.1877 | 329.1779 | 318.0131
1564.5979 | 680.7505 | 321.5344 | 329.6084 | 318.4195
1565.5979 | 678.8182 | 322.0587 | 328.8254 | 319.3898
1566.5979 | 675.0369 | 322.1355 | 328.8996 | 319.6128
1567.5979 | 672.3231 | 322.1475 | 328.3537 | 319.2371
1568.5979 | 672.7548 | 322.067 | 328.2242 | 319.6358
1569.5979 | 672.3179 | 322.4004 | 329.4064 | 319.6847
1570.5979 | 673.0806 | 322.6901 | 330.0632 | 319.6273
1571.5979 | 673.4336 | 322.7822 | 330.7314 | 319.5856
1572.5979 | 672.948 | 323.1272 | 330.539 | 320.2175
1573.5979 | 674.7966 | 323.7781 | 330.9468 | 319.9568
1574.5979 | 674.7489 | 323.0621 | 330.2842 | 319.5639
1575.5979 | 672.9289 | 323.7545 | 330.3738 | 320.0836
1576.5979 | 668.4023 | 324.2378 | 330.3332 | 319.4301
1577.5979 | 667.247 | 324.0691 | 330.8562 | 320.3745
1578.5979 | 668.2658 | 324.9793 | 331.0535 | 321.2995
1579.5979 | 667.4713 | 325.0975 | 332.7236 | 321.6729
1580.5979 | 667.651 | 325.4555 | 332.6023 | 322.0347
1581.5979 | 666.9269 | 325.3845 | 332.8003 | 322.8435
1582.5979 | 663.1554 | 326.786 | 335.1462 | 323.1418
1583.5979 | 659.9516 | 327.2467 | 334.4742 | 323.8093
1584.5979 | 657.1909 | 327.6793 | 335.2902 | 324.3796
1585.5979 | 658.1148 | 327.7748 | 334.9345 | 324.3517
1586.5979 | 660.0447 | 326.9547 | 334.3206 | 323.9398
1587.5979 | 658.9158 | 326.6569 | 333.7586 | 323.1633
1588.5979 | 656.3655 | 327.3329 | 333.0224 | 322.5722
1589.5979 | 652.9495 | 326.998 | 332.9551 | 323.6722
1590.5979 | 649.694 | 326.6409 | 333.8206 | 324.3932
1591.5979 | 651.5266 | 326.1994 | 334.0165 | 324.6799
1592.5979 | 654.1669 | 326.5483 | 334.8809 | 324.4673
1593.5979 | 657.5236 | 327.1099 | 335.093 | 324.2002
1594.5979 | 658.8028 | 327.4864 | 334.7828 | 324.457
1595.5979 | 658.9686 | 327.6618 | 335.4657 | 323.8704
1596.5979 | 655.9014 | 328.0079 | 336.9732 | 324.3383
1597.5979 | 655.9929 | 327.5739 | 337.3036 | 324.602
1598.5979 | 655.6084 | 328.4751 | 337.5869 | 324.5012
1599.5979 | 655.4519 | 330.0106 | 336.9929 | 324.2172
1600.5979 | 654.3749 | 331.0243 | 337.4939 | 324.3729
1601.5979 | 656.2613 | 331.4146 | 337.4655 | 324.5595
1602.6135 | 658.5676 | 331.9777 | 338.4277 | 324.6383
1603.5979 | 661.3092 | 332.8135 | 338.7134 | 325.4845
1604.5979 | 661.4048 | 333.9836 | 338.0131 | 325.1602
1605.5979 | 664.2546 | 333.804 | 337.3726 | 324.4379
1606.5979 | 662.1907 | 333.7552 | 337.2985 | 324.6231
1607.5979 | 659.2036 | 333.4311 | 336.5353 | 324.3818
1608.5979 | 655.4632 | 333.522 | 337.3343 | 323.5516
1609.5979 | 651.1977 | 333.633 | 337.6395 | 324.4536
1610.5979 | 648.8192 | 333.2895 | 338.1328 | 325.0649
1611.5979 | 649.5505 | 333.6271 | 338.755 | 325.3954
1612.5979 | 649.973 | 333.5381 | 339.0046 | 325.6771
1613.5979 | 651.6491 | 333.7469 | 338.9369 | 327.0275
1614.5979 | 653.6708 | 334.6967 | 338.7456 | 326.3719
1615.5979 | 654.7476 | 334.4341 | 339.7459 | 327.437
1616.5979 | 653.7505 | 334.0248 | 340.9612 | 328.6969
1617.5979 | 654.8037 | 333.7385 | 341.0825 | 329.707
1618.5979 | 657.3311 | 334.1305 | 340.5786 | 329.2698
1619.5979 | 657.3759 | 334.3296 | 340.0981 | 329.4669
1620.5979 | 658.5348 | 335.2215 | 339.8358 | 329.1899
1621.5979 | 660.4219 | 335.4976 | 340.3938 | 329.3601
1622.6135 | 662.8325 | 335.5195 | 340.8932 | 329.907
1623.5979 | 663.7101 | 335.9155 | 340.7543 | 329.717
1624.5979 | 665.2949 | 336.4534 | 341.2005 | 330.0444
1625.5979 | 665.7511 | 336.6309 | 341.897 | 331.0815
1626.5979 | 665.3257 | 336.24 | 341.6944 | 330.4078
1627.6135 | 665.8984 | 336.9583 | 342.9182 | 330.5423
1628.6135 | 666.7408 | 336.8427 | 344.8146 | 333.0702
1629.5979 | 667.5762 | 336.7422 | 344.6869 | 332.7601
1630.6135 | 667.8767 | 337.1513 | 344.3783 | 333.127
1631.6135 | 666.5541 | 337.7794 | 343.9492 | 332.6673
1632.5979 | 668.1197 | 338.0334 | 343.9164 | 333.4218
1633.5979 | 670.7104 | 337.8855 | 343.503 | 332.1732
1634.5979 | 672.8826 | 338.2892 | 343.3539 | 331.556
1635.5979 | 677.3517 | 339.2539 | 343.7476 | 333.0287
1636.5979 | 681.0904 | 339.3274 | 343.9254 | 332.7
1637.5979 | 682.6201 | 339.1579 | 343.6972 | 332.7912
1638.5979 | 681.1762 | 339.5592 | 343.9753 | 332.782
1639.5979 | 680.0565 | 339.6801 | 344.0494 | 332.7747
1640.5979 | 678.418 | 339.3155 | 344.4162 | 332.9712
1641.5979 | 677.606 | 339.1244 | 344.1932 | 332.8862
1642.5979 | 676.5028 | 338.9191 | 344.0368 | 332.9589
1643.5979 | 677.3827 | 339.3153 | 344.0414 | 333.7641
1644.5979 | 676.678 | 339.4658 | 343.7255 | 333.8
1645.5979 | 676.3363 | 339.2935 | 344.0105 | 334.1353
1646.5979 | 674.3468 | 338.6857 | 343.9014 | 333.7656
1647.5979 | 671.9665 | 338.4386 | 343.2398 | 333.1657
1648.5979 | 670.5535 | 338.4216 | 342.8393 | 332.1488
1649.5979 | 670.1726 | 338.8334 | 342.9504 | 332.2135
1650.5979 | 668.2497 | 338.707 | 342.632 | 332.5657
1651.5979 | 669.2655 | 338.3528 | 341.9334 | 332.8473
1652.5979 | 671.1418 | 337.9293 | 341.6288 | 332.3363
1653.5979 | 670.6675 | 339.2422 | 341.5568 | 331.6724
1654.5979 | 668.611 | 339.3241 | 341.6353 | 331.1056
1655.5979 | 666.5609 | 339.3857 | 342.2135 | 331.4373
1656.5979 | 666.2153 | 339.3595 | 342.0756 | 331.9559
1657.5979 | 666.5687 | 340.002 | 341.9602 | 332.4535
1658.5979 | 668.5511 | 340.0534 | 342.4427 | 332.5356
1659.5979 | 669.2927 | 340.6768 | 343.0428 | 333.1746
1660.5979 | 670.0747 | 341.2679 | 343.552 | 333.0682
1661.6135 | 670.0395 | 341.6344 | 343.2731 | 333.4839
1662.5979 | 670.4685 | 342.0391 | 343.7821 | 332.7746
1663.5979 | 669.3838 | 342.5988 | 344.7615 | 333.2455
1664.5979 | 671.2484 | 342.8354 | 344.9827 | 333.8384
1665.5979 | 671.9144 | 343.5628 | 344.8642 | 333.8336
1666.5979 | 670.8269 | 343.7201 | 344.7937 | 334.1799
1667.5979 | 671.6853 | 343.4012 | 344.5995 | 334.7364
1668.5979 | 670.0805 | 343.7676 | 344.2679 | 334.3832
1669.5979 | 667.4121 | 343.355 | 344.4963 | 334.8455
1670.5979 | 665.6437 | 343.7159 | 344.4319 | 334.7908
1671.5979 | 664.5849 | 344.0079 | 344.1988 | 334.2318
1672.5979 | 662.6827 | 344.245 | 344.0895 | 334.2204
1673.5979 | 663.1226 | 344.1074 | 343.4559 | 334.2607
1674.5979 | 662.5104 | 343.9296 | 344.4474 | 335.792
1675.5979 | 663.286 | 343.7904 | 343.9478 | 335.8989
1676.5979 | 662.5945 | 343.0026 | 343.1626 | 334.6861
1677.5979 | 662.8213 | 343.5103 | 342.6111 | 333.9836
1678.5979 | 661.3265 | 343.8181 | 342.4484 | 334.0231
1679.5979 | 663.3717 | 343.6473 | 342.3926 | 333.7125
1680.5979 | 663.97 | 342.9854 | 342.3287 | 333.0641
1681.5979 | 663.8863 | 342.2854 | 342.2571 | 332.5661
1682.5979 | 663.1738 | 342.3088 | 341.8691 | 332.5051
1683.5979 | 663.8179 | 342.4826 | 342.1299 | 331.7495
1684.5979 | 663.2317 | 342.9934 | 342.6483 | 332.8738
1685.5979 | 663.058 | 342.5389 | 343.4138 | 333.0558
1686.5979 | 663.9227 | 342.1615 | 342.6035 | 332.9806
1687.5979 | 663.0089 | 342.3428 | 342.1562 | 333.1314
1688.5979 | 661.8908 | 342.2949 | 341.8098 | 333.1382
1689.5979 | 660.5405 | 342.4463 | 341.3642 | 333.1851
1690.5979 | 660.4953 | 342.2053 | 341.4811 | 333.474
1691.5979 | 659.1967 | 341.8164 | 341.0371 | 333.7681
1692.5979 | 659.0237 | 342.8827 | 340.7509 | 333.2144
1693.5979 | 658.6036 | 342.7275 | 341.2236 | 332.505
1694.5979 | 659.7701 | 342.6306 | 341.2953 | 332.1196
1695.5979 | 659.5703 | 342.936 | 341.7911 | 332.0037
1696.5979 | 661.0037 | 342.7022 | 342.1815 | 332.8577
1697.5979 | 664.2465 | 342.8391 | 342.4335 | 333.6777
1698.5979 | 663.9068 | 343.92 | 343.4922 | 334.0164
1699.5979 | 661.3924 | 343.882 | 343.0919 | 333.7737
1700.5979 | 661.8937 | 343.4855 | 342.9276 | 334.4557
1701.5979 | 661.8182 | 343.0046 | 343.3086 | 334.188
1702.5979 | 662.315 | 342.9266 | 343.1799 | 333.7094
1703.5979 | 661.0091 | 343.0661 | 343.3373 | 334.0935
1704.5979 | 658.9876 | 343.2004 | 343.2146 | 334.1552
1705.5979 | 655.6066 | 344.0336 | 343.4605 | 334.0053
1706.5979 | 655.3661 | 344.4891 | 343.0227 | 333.7217
1707.5979 | 656.234 | 344.2898 | 342.3 | 333.6935
1708.5979 | 655.7237 | 344.6163 | 342.4615 | 333.5575
1709.5979 | 656.1918 | 344.3255 | 342.3323 | 333.6098
1710.5979 | 655.8617 | 344.7145 | 342.8476 | 333.5799
1711.5979 | 657.7975 | 344.7488 | 342.8528 | 333.5284
1712.6135 | 660.2374 | 345.6181 | 343.2419 | 333.9455
1713.5979 | 659.7862 | 346.0015 | 343.4306 | 334.2082
1714.5979 | 660.9271 | 345.9272 | 343.6035 | 334.5321
1715.5979 | 660.4821 | 345.7826 | 344.124 | 334.4814
1716.5979 | 658.6765 | 346.1002 | 344.3558 | 334.4334
1717.5979 | 658.7754 | 346.1387 | 344.1468 | 334.2904
1718.5979 | 660.3955 | 346.8927 | 344.7568 | 334.7971
1719.5979 | 661.7189 | 347.0995 | 344.6202 | 333.9359
1720.5979 | 661.5655 | 347.4362 | 344.6862 | 334.284
1721.5979 | 661.5676 | 347.2309 | 345.088 | 333.5308
1722.5979 | 661.0295 | 347.0279 | 346.2674 | 333.2464
1723.5979 | 659.4069 | 346.8471 | 346.3535 | 333.0182
1724.5979 | 661.5461 | 346.6384 | 346.8051 | 332.8459
1725.5979 | 662.255 | 346.7929 | 346.463 | 332.9494
1726.5979 | 661.9492 | 346.2919 | 345.6361 | 332.6937
1727.5979 | 664.088 | 345.9175 | 344.6551 | 331.6637
1728.5979 | 665.5075 | 346.7963 | 344.2355 | 330.9686
1729.5979 | 666.0098 | 346.2704 | 343.6752 | 330.9837
1730.5979 | 665.8298 | 346.5334 | 343.3319 | 330.4365
1731.5979 | 666.7126 | 346.4508 | 343.3962 | 329.9057
1732.5979 | 666.76 | 346.1056 | 343.1245 | 330.1123
1733.5979 | 666.954 | 346.6743 | 344.3429 | 330.0495
1734.5979 | 666.2863 | 347.3966 | 344.067 | 330.0838
1735.5979 | 664.6727 | 347.3255 | 344.6998 | 331.0351
1736.5979 | 663.2291 | 347.3212 | 345.2449 | 331.2701
1737.5979 | 661.3071 | 347.463 | 345.2284 | 331.2287
1738.5979 | 661.3585 | 346.9338 | 344.8931 | 331.3287
1739.6135 | 661.1444 | 345.8238 | 344.7402 | 331.2742
1740.5979 | 661.6837 | 344.9553 | 344.228 | 331.3803
1741.5979 | 660.7025 | 344.959 | 344.0559 | 331.2516
1742.6135 | 659.1752 | 345.0332 | 343.8597 | 330.4572
1743.5979 | 657.6466 | 345.2296 | 343.8682 | 329.865
1744.5979 | 657.9129 | 345.1972 | 343.9651 | 330.1552
1745.5979 | 657.6356 | 345.9049 | 344.2127 | 330.7346
1746.6135 | 656.0298 | 347.2341 | 344.3722 | 330.6986
1747.5979 | 656.2313 | 347.5086 | 344.9415 | 331.5337
1748.5979 | 658.8487 | 348.7387 | 344.9084 | 332.2425
1749.5979 | 660.8706 | 348.9181 | 344.8507 | 332.1201
1750.5979 | 659.9987 | 349.2477 | 345.5401 | 332.9114
1751.5979 | 659.4921 | 348.9973 | 346.196 | 332.7767
1752.5979 | 660.8873 | 349.1723 | 346.6873 | 333.8377
1753.5979 | 659.9173 | 349.4323 | 347.8343 | 335.7515
1754.6135 | 660.118 | 349.1843 | 348.1279 | 335.4896
1755.5979 | 660.9703 | 349.5595 | 349.2119 | 336.0489
1756.5979 | 660.692 | 349.9858 | 349.3909 | 336.0223
1757.5979 | 660.3051 | 349.8955 | 349.5783 | 335.0815
1758.5979 | 660.841 | 349.4209 | 349.5292 | 334.1975
1759.5979 | 660.8789 | 349.0819 | 349.7903 | 333.5116
1760.5979 | 664.4144 | 349.1232 | 349.6872 | 332.5354
1761.5979 | 668.9435 | 349.8465 | 349.4829 | 331.6819
1762.5979 | 670.3219 | 350.1029 | 349.3653 | 331.3121
1763.5979 | 670.8774 | 350.0878 | 349.9856 | 331.271
1764.5979 | 671.2813 | 349.9366 | 350.0222 | 332.5166
1765.5979 | 672.3571 | 350.0635 | 350.6084 | 333.3126
1766.5979 | 672.782 | 349.9004 | 350.3267 | 332.9714
1767.5979 | 670.0788 | 349.5713 | 350.0539 | 332.5877
1768.5979 | 670.2781 | 349.361 | 350.0425 | 332.6566
1769.5979 | 668.7728 | 349.1139 | 349.7678 | 332.7076
1770.5979 | 669.1085 | 349.5617 | 349.6923 | 333.2412
1771.5979 | 667.0765 | 349.5428 | 349.2501 | 332.6762
1772.5979 | 665.0235 | 349.5766 | 348.3458 | 332.6173
1773.5979 | 665.2876 | 349.0087 | 348.5231 | 331.8632
1774.5979 | 664.637 | 348.4647 | 348.2118 | 332.2017
1775.5979 | 662.5761 | 348.2395 | 347.8702 | 331.7719
1776.5979 | 661.2032 | 347.821 | 347.605 | 332.2258
1777.5979 | 660.0037 | 347.8325 | 347.5408 | 331.9708
1778.5979 | 661.3252 | 347.5306 | 348.0183 | 331.9073
1779.5979 | 661.8412 | 347.5223 | 347.7623 | 332.2594
1780.5979 | 661.7912 | 347.7377 | 347.5027 | 332.9027
1781.5979 | 663.0633 | 347.9467 | 347.3122 | 332.1116
1782.5979 | 662.5418 | 347.8467 | 347.5573 | 332.2415
1783.5979 | 658.8724 | 347.1141 | 346.5542 | 332.0185
1784.5979 | 658.0927 | 346.7872 | 346.5598 | 332.2328
1785.5979 | 657.6983 | 346.8048 | 346.0338 | 331.9794
1786.5979 | 657.1704 | 345.7332 | 345.0741 | 331.7013
1787.5979 | 654.5675 | 346.1169 | 344.8502 | 331.638
1788.5979 | 650.9594 | 345.9317 | 344.6736 | 332.0457
1789.5979 | 649.2962 | 345.6217 | 345.0057 | 331.8907
1790.5979 | 649.543 | 345.8831 | 345.4165 | 332.6841
1791.5979 | 651.3945 | 345.9602 | 344.1759 | 332.4506
1792.5979 | 651.5934 | 346.12 | 343.8747 | 331.7866
1793.5979 | 651.9921 | 345.951 | 343.5548 | 331.6484
1794.5979 | 650.7086 | 345.9383 | 343.3533 | 331.3073
1795.5979 | 654.331 | 345.4099 | 343.8018 | 331.4977
1796.5979 | 655.8928 | 345.1975 | 343.6088 | 331.4981
1797.5979 | 658.1938 | 344.9839 | 343.5997 | 332.5621
1798.5979 | 657.8007 | 345.5699 | 343.6818 | 332.1618
1799.5979 | 657.5446 | 345.7347 | 343.5021 | 331.3932
1800.5979 | 657.7801 | 346.0182 | 344.0656 | 331.405
1801.5979 | 657.7424 | 345.8561 | 343.8969 | 330.817
1802.5979 | 656.6062 | 346.5303 | 344.5011 | 330.6371
1803.5979 | 657.1777 | 346.2409 | 344.5646 | 331.1464
1804.5979 | 654.8113 | 347.3445 | 344.9919 | 331.3834
1805.5979 | 653.344 | 347.2968 | 344.6684 | 330.9479
1806.5979 | 651.4894 | 347.3739 | 344.3712 | 331.3022
1807.5979 | 650.2209 | 347.8557 | 344.2852 | 330.4946
1808.5979 | 648.5089 | 347.6078 | 344.0039 | 329.986
1809.5979 | 647.6571 | 348.2326 | 344.4286 | 331.1461
1810.5979 | 648.4378 | 348.0544 | 344.4241 | 331.3001
1811.5979 | 648.4987 | 348.0116 | 344.4844 | 332.9299
1812.5979 | 647.514 | 347.3852 | 343.8157 | 332.7629
1813.5979 | 646.0617 | 347.1907 | 343.2788 | 333.1225
1814.5979 | 646.9898 | 346.5273 | 342.9328 | 333.6299
1815.5979 | 648.7251 | 346.3397 | 342.0568 | 332.5433
1816.5979 | 650.0985 | 346.4492 | 341.2867 | 331.2501
1817.5979 | 650.0725 | 347.0589 | 341.2953 | 331.319
1818.5979 | 649.5557 | 346.5048 | 341.3688 | 330.5631
1819.5979 | 649.883 | 346.1355 | 341.5505 | 329.751
1820.5979 | 647.468 | 345.4962 | 340.875 | 329.0585
1821.5979 | 646.2042 | 345.6155 | 340.7208 | 328.3959
1822.5979 | 645.7422 | 345.638 | 340.5652 | 327.7984
1823.5979 | 645.885 | 344.8497 | 340.4288 | 327.8568
1824.5979 | 646.4936 | 344.8552 | 340.6654 | 327.8698
1825.5979 | 646.5567 | 344.9294 | 340.0326 | 328.5541
1826.5979 | 647.7889 | 344.3704 | 339.8484 | 329.0572
1827.5979 | 647.8901 | 344.4065 | 339.7567 | 329.3701
1828.5979 | 647.352 | 344.3551 | 339.4796 | 329.8705
1829.5979 | 645.5427 | 343.8401 | 339.5774 | 329.7476
1830.5979 | 647.0313 | 343.2149 | 339.5534 | 329.4206
1831.5979 | 647.8719 | 342.703 | 339.2525 | 329.5017
1832.5979 | 649.3233 | 342.2542 | 339.2433 | 329.3629
1833.5979 | 648.8552 | 342.2676 | 338.9797 | 329.5214
1834.5979 | 648.2985 | 341.7802 | 338.5028 | 329.3878
1835.5979 | 645.729 | 341.4721 | 338.157 | 329.4531
1836.5979 | 642.9811 | 340.9541 | 339.0157 | 329.2306
1837.5979 | 639.9695 | 340.5981 | 338.6865 | 329.6208
1838.5979 | 639.7859 | 340.6862 | 338.6027 | 329.3658
1839.5979 | 638.9847 | 341.2972 | 338.7912 | 329.1638
1840.5979 | 638.5438 | 341.8811 | 338.782 | 329.2913
1841.5979 | 639.3463 | 341.841 | 338.5811 | 329.5799
1842.5979 | 640.0168 | 341.9884 | 338.5987 | 329.2459
1843.5979 | 640.0653 | 341.8871 | 339.4683 | 329.9914
1844.5979 | 639.8424 | 342.0168 | 340.017 | 331.217
1845.5979 | 639.3728 | 341.863 | 340.3445 | 331.8208
1846.5979 | 639.8405 | 342.7513 | 340.9422 | 331.447
1847.5979 | 640.5418 | 342.8072 | 341.0446 | 331.1829
1848.5979 | 640.0604 | 342.7727 | 341.5721 | 331.2191
1849.5979 | 639.7791 | 343.3078 | 341.704 | 331.9176
1850.5979 | 637.3784 | 343.2409 | 341.9551 | 331.8418
1851.5979 | 637.6915 | 343.567 | 341.5934 | 332.2883
1852.5979 | 638.252 | 344.3335 | 341.7237 | 331.8748
1853.5979 | 641.5648 | 344.2308 | 341.5519 | 332.0191
1854.5979 | 640.6719 | 344.1142 | 340.9405 | 330.9059
1855.5979 | 640.8237 | 343.884 | 340.4492 | 330.4444
1856.5979 | 639.9123 | 343.5876 | 340.4631 | 330.1182
1857.5979 | 637.1411 | 343.9434 | 341.0627 | 330.1719
1858.5979 | 635.8267 | 343.6842 | 341.2209 | 330.378
1859.5979 | 632.1707 | 343.9882 | 340.855 | 330.5779
1860.5979 | 632.3268 | 343.9969 | 341.0791 | 330.482
1861.5979 | 632.6583 | 344.1634 | 341.8354 | 331.2043
1862.5979 | 632.8906 | 343.4522 | 341.7427 | 331.235
1863.5979 | 634.3139 | 342.8156 | 341.4195 | 331.2494
1864.5979 | 634.7679 | 342.4463 | 340.4154 | 330.8013
1865.5979 | 635.0307 | 341.959 | 340.5876 | 329.7318
1866.5979 | 635.9104 | 341.7322 | 340.5515 | 328.7112
1867.5979 | 635.6605 | 341.8137 | 340.9785 | 328.3871
1868.5979 | 635.8877 | 341.7368 | 340.5714 | 328.836
1869.5979 | 636.5438 | 341.4942 | 339.8576 | 329.1998
1870.5979 | 637.0154 | 341.435 | 339.2346 | 329.4409
1871.5979 | 637.1324 | 341.4347 | 339.3495 | 328.5546
1872.5979 | 637.1427 | 341.229 | 339.5515 | 328.0735
1873.5979 | 636.5574 | 340.9535 | 339.4786 | 328.2627
1874.5979 | 637.5203 | 340.5298 | 339.3313 | 328.7494
1875.5979 | 636.1484 | 340.2895 | 338.7145 | 328.9256
1876.5979 | 635.5556 | 340.3917 | 339.0634 | 329.3205
1877.5979 | 635.9637 | 340.2013 | 339.1461 | 329.431
1878.5979 | 634.957 | 339.9903 | 338.6237 | 328.7604
1879.5979 | 633.9963 | 339.945 | 338.1191 | 328.6603
1880.5979 | 632.3653 | 339.4872 | 337.4093 | 328.7795
1881.5979 | 632.515 | 339.4658 | 336.9559 | 328.7697
1882.5979 | 633.2965 | 338.756 | 336.9724 | 328.5343
1883.5979 | 633.3025 | 338.6223 | 336.6086 | 328.4238
1884.5979 | 633.8145 | 339.5456 | 336.1588 | 328.5712
1885.5979 | 631.8111 | 339.2427 | 335.9333 | 328.1771
1886.5979 | 632.2877 | 339.3192 | 335.49 | 328.3984
1887.5979 | 632.7514 | 339.3016 | 335.5156 | 327.5865
1888.5979 | 631.7907 | 339.7015 | 335.459 | 327.0291
1889.5979 | 631.3498 | 339.5062 | 336.0094 | 326.9176
1890.5979 | 630.0308 | 339.5643 | 336.3799 | 327.2735
1891.5979 | 629.3673 | 339.404 | 336.2339 | 326.7051
1892.5979 | 631.6885 | 339.1245 | 336.5177 | 326.6657
1893.5979 | 635.6271 | 338.6502 | 335.6171 | 326.7182
1894.5979 | 636.5648 | 338.0186 | 335.368 | 327.063
1895.5979 | 636.5326 | 337.7 | 335.294 | 326.8824
1896.5979 | 635.5347 | 337.7681 | 335.0696 | 326.9871
1897.5979 | 635.9685 | 337.9131 | 334.9379 | 326.3642
1898.5979 | 636.9346 | 337.958 | 335.2479 | 326.1696
1899.5979 | 638.6489 | 338.4439 | 335.3707 | 325.998
1900.5979 | 638.4369 | 338.2198 | 335.4136 | 325.7244
1901.6135 | 636.2129 | 337.9503 | 335.4697 | 326.1631
1902.5979 | 637.163 | 337.765 | 334.9047 | 325.7981
1903.5979 | 641.235 | 338.0981 | 334.7824 | 325.6531
1904.5979 | 643.8669 | 337.8713 | 334.9399 | 326.4686
1905.5979 | 646.3926 | 339.6276 | 336.4345 | 326.5612
1906.5979 | 649.0606 | 340.5568 | 337.2039 | 328.1403
1907.5979 | 652.5815 | 342.3626 | 338.647 | 329.3809
1908.5979 | 657.1117 | 343.6433 | 340.1885 | 329.8429
1909.5979 | 660.5091 | 345.4953 | 340.712 | 329.7925
1910.5979 | 661.1787 | 345.9638 | 341.6206 | 330.8925
1911.5979 | 659.8254 | 346.3794 | 341.9472 | 330.7811
1912.5979 | 657.5771 | 346.1958 | 342.5301 | 331.0647
1913.5979 | 655.5143 | 345.8014 | 342.6907 | 331.0051
1914.5979 | 655.5905 | 345.2187 | 342.4331 | 330.614
1915.5979 | 653.9187 | 344.8407 | 341.5785 | 330.8331
1916.5979 | 649.9362 | 345.3436 | 340.7892 | 330.3034
1917.5979 | 648.8397 | 344.8203 | 339.8562 | 329.4317
1918.5979 | 649.296 | 344.7891 | 339.5168 | 328.5592
1919.5979 | 653.6281 | 344.8378 | 339.4994 | 328.6994
1920.5979 | 660.2476 | 346.8911 | 340.8388 | 330.1677
1921.5979 | 671.4291 | 349.4135 | 342.6353 | 332.3086
1922.5979 | 685.4067 | 351.1831 | 346.3461 | 335.1228
1923.5979 | 692.8405 | 354.4702 | 348.7288 | 336.3314
1924.5979 | 697.3911 | 356.546 | 350.1657 | 337.9725
1925.5979 | 695.803 | 357.4171 | 351.1616 | 338.7558
1926.5979 | 693.7853 | 357.9079 | 351.2533 | 339.894
1927.5979 | 692.9417 | 359.0692 | 352.7082 | 341.1417
1928.5979 | 694.3136 | 359.2437 | 353.2537 | 341.1885
1929.5979 | 692.3476 | 359.7137 | 354.2682 | 341.8582
1930.5979 | 692.2363 | 359.8165 | 354.2412 | 342.8015
1931.5979 | 690.4805 | 359.7967 | 354.541 | 342.6941
1932.5979 | 690.3905 | 359.5593 | 354.2711 | 342.1809
1933.5979 | 687.6245 | 359.6442 | 355.1257 | 342.9074
1934.5979 | 685.3521 | 359.3115 | 355.1917 | 343.2236
1935.5979 | 685.8131 | 360.3461 | 355.0223 | 343.9782
1936.5979 | 686.762 | 361.2715 | 355.7375 | 344.3473
1937.5979 | 689.8393 | 361.6355 | 355.5645 | 344.1854
1938.5979 | 689.3747 | 362.1045 | 355.3796 | 343.8761
1939.5979 | 689.2334 | 363.2789 | 355.7008 | 343.6841
1940.5979 | 692.8186 | 362.945 | 355.8336 | 343.641
1941.5979 | 694.3961 | 363.0954 | 356.1047 | 344.1698
1942.5979 | 692.7314 | 363.2816 | 356.1032 | 344.4262
1943.5979 | 696.1785 | 363.16 | 356.7076 | 345.0569
1944.5979 | 698.4814 | 363.4759 | 357.5665 | 345.1791
1945.5979 | 699.982 | 364.6618 | 358.6547 | 345.6614
1946.5979 | 699.8628 | 365.031 | 358.8785 | 347.4225
1947.5979 | 698.4964 | 364.8453 | 359.2194 | 347.3921
1948.5979 | 697.7698 | 365.3111 | 358.7147 | 347.0635
1949.5979 | 697.4933 | 365.6184 | 358.2592 | 347.4415
1950.5979 | 701.9792 | 365.7045 | 358.0903 | 347.3586
1951.5979 | 705.4532 | 366.2394 | 358.1648 | 347.1829
1952.5979 | 708.3481 | 367.4252 | 358.965 | 346.6315
1953.5979 | 710.4642 | 367.7297 | 359.381 | 346.3233
1954.5979 | 712.382 | 367.9244 | 360.5793 | 346.3052
1955.5979 | 711.6216 | 367.7301 | 361.063 | 346.3271
1956.5979 | 708.019 | 368.4669 | 361.8437 | 347.3614
1957.5979 | 708.4982 | 368.6943 | 361.6716 | 347.4024
1958.5979 | 712.4077 | 369.7906 | 362.4027 | 347.6107
1959.5979 | 713.072 | 370.1733 | 361.5289 | 347.7481
1960.5979 | 713.0453 | 370.5113 | 361.8141 | 346.9881
1961.5979 | 715.3472 | 370.8999 | 362.1516 | 347.1235
1962.5979 | 715.3175 | 371.2271 | 362.7539 | 347.6767
1963.5979 | 713.5907 | 371.9639 | 362.5678 | 348.8945
1964.5979 | 711.644 | 372.3149 | 363.4225 | 349.0587
1965.5979 | 712.444 | 372.2339 | 363.1492 | 349.752
1966.5979 | 712.4636 | 372.4599 | 363.5082 | 349.5439
1967.5979 | 713.8673 | 372.6019 | 363.8818 | 349.3604
1968.5979 | 718.615 | 373.0805 | 363.8417 | 350.4745
1969.5979 | 718.4248 | 372.9833 | 363.87 | 350.2456
1970.5979 | 716.673 | 372.9287 | 364.0264 | 350.0909
1971.5979 | 714.7051 | 372.5521 | 364.4155 | 350.7973
1972.5979 | 711.6692 | 372.656 | 365.3789 | 351.4306
1973.5979 | 711.602 | 372.213 | 365.7217 | 351.3272
1974.5979 | 711.3447 | 372.48 | 365.813 | 352.193
1975.5979 | 710.8655 | 372.763 | 365.4877 | 352.7116
1976.5979 | 711.3294 | 373.4939 | 365.4785 | 352.255
1977.5979 | 713.7314 | 373.6257 | 365.7174 | 352.5827
1978.5979 | 717.4248 | 373.5242 | 366.0241 | 353.3255
1979.5979 | 720.9465 | 374.0655 | 365.9838 | 354.4256
1980.5979 | 722.1353 | 374.7722 | 366.2433 | 354.9386
1981.5979 | 722.8972 | 374.7165 | 366.5488 | 354.8984
1982.5979 | 727.409 | 374.4882 | 366.62 | 355.4006
1983.5979 | 729.1547 | 374.473 | 366.8965 | 355.7457
1984.5979 | 725.8625 | 374.5576 | 366.7773 | 355.852
1985.5979 | 722.5924 | 374.4718 | 366.9527 | 355.4094
1986.5979 | 720.6902 | 373.6706 | 367.1514 | 355.6965
1987.5979 | 719.2317 | 373.3612 | 366.9495 | 355.4712
1988.5979 | 719.9449 | 373.882 | 366.8087 | 355.0417
1989.5979 | 723.5628 | 375.2086 | 367.1738 | 354.1433
1990.5979 | 723.734 | 375.8146 | 367.3284 | 353.6227
1991.5979 | 721.8097 | 375.5193 | 366.7698 | 354.1128
1992.5979 | 717.5145 | 375.8792 | 366.9154 | 353.6227
1993.5979 | 712.2014 | 375.1993 | 366.7651 | 353.711
1994.5979 | 710.2275 | 374.6296 | 366.4141 | 353.0368
1995.5979 | 709.8556 | 373.8097 | 365.8715 | 353.018
1996.5979 | 711.8188 | 374.1843 | 365.77 | 353.0495
1997.5979 | 714.111 | 373.4677 | 365.5662 | 353.1304
1998.5979 | 715.7703 | 373.2527 | 365.4217 | 353.6011
1999.5979 | 713.2526 | 373.3298 | 365.4895 | 353.9196
2000.5979 | 708.0611 | 373.7262 | 365.4533 | 353.0796
2001.5979 | 704.4554 | 373.7427 | 365.1297 | 352.1696
2002.5979 | 700.3634 | 374.5785 | 365.0067 | 353.0437
2003.5979 | 700.1872 | 374.7038 | 365.3611 | 352.9553
2004.5979 | 700.3919 | 375.0321 | 365.3844 | 354.4987
2005.5979 | 700.3874 | 375.6923 | 365.6617 | 355.552
2006.5979 | 699.0865 | 375.82 | 365.8491 | 354.6699
2007.5979 | 698.3394 | 375.8996 | 365.7155 | 354.0657
2008.5979 | 696.7165 | 376.3294 | 366.1192 | 353.5637
2009.5979 | 696.9562 | 376.6158 | 366.3717 | 354.334
2010.5979 | 698.9129 | 376.2276 | 366.5361 | 354.8563
2011.5979 | 698.776 | 376.5262 | 366.4298 | 354.5068
2012.5979 | 699.4949 | 377.2726 | 366.155 | 354.5739
2013.5979 | 700.907 | 377.1921 | 366.2937 | 355.0861
2014.5979 | 701.3155 | 376.8038 | 365.4709 | 354.5868
2015.5979 | 702.7676 | 377.2632 | 365.5331 | 355.1881
2016.5979 | 705.0988 | 377.4978 | 365.703 | 354.8507
2017.5979 | 707.5624 | 377.7523 | 366.1428 | 355.0515
2018.5979 | 707.7455 | 378.0728 | 365.8658 | 355.8711
2019.5979 | 705.1917 | 377.9842 | 365.6113 | 355.0699
2020.5979 | 702.4066 | 378.0999 | 365.7195 | 354.635
2021.5979 | 702.679 | 377.6806 | 365.6176 | 355.2198
2022.5979 | 702.5203 | 378.0725 | 365.521 | 355.7998
2023.5979 | 699.9459 | 378.3557 | 365.5831 | 354.7522
2024.5979 | 696.3625 | 377.9892 | 365.6322 | 355.2736
2025.5979 | 693.622 | 378.0887 | 365.79 | 355.6577
2026.5979 | 693.4553 | 378.7875 | 366.4026 | 356.67
2027.5979 | 696.0757 | 378.7919 | 367.0408 | 356.848
2028.5979 | 696.5742 | 379.3367 | 367.6239 | 357.2377
2029.5979 | 695.0894 | 379.6894 | 368.3238 | 358.0587
2030.5979 | 696.4209 | 379.3037 | 368.4914 | 358.1436
2031.5979 | 698.6811 | 380.4468 | 370.263 | 358.7767
2032.5979 | 698.8991 | 380.3025 | 370.1807 | 360.0406
2033.5979 | 702.61 | 380.5484 | 370.935 | 361.408
2034.5979 | 706.4408 | 381.1215 | 371.7772 | 361.5663
2035.5979 | 708.2288 | 381.5829 | 372.2319 | 362.0809
2036.5979 | 710.2075 | 382.2618 | 372.1675 | 361.6996
2037.5979 | 713.1442 | 382.4318 | 371.9852 | 360.8108
2038.5979 | 712.3569 | 382.5071 | 372.3109 | 360.7592
2039.5979 | 715.5274 | 382.1186 | 372.5837 | 361.305
2040.5979 | 715.2063 | 382.3716 | 372.5385 | 360.6261
2041.5979 | 713.1902 | 382.5981 | 372.8118 | 360.0225
2042.5979 | 714.3172 | 382.8858 | 372.7487 | 359.7892
2043.5979 | 717.5645 | 382.857 | 373.3612 | 360.9575
2044.5979 | 718.1112 | 382.8644 | 373.4637 | 361.6639
2045.5979 | 714.7959 | 383.0049 | 373.9115 | 362.081
2046.5979 | 713.0901 | 382.8157 | 374.1544 | 361.9135
2047.5979 | 710.841 | 382.7386 | 374.448 | 361.4979
2048.5979 | 709.643 | 382.6352 | 374.3718 | 361.6422
2049.5979 | 710.4279 | 383.1268 | 374.0315 | 361.6936
2050.5979 | 713.2414 | 382.725 | 373.8647 | 362.6965
2051.5979 | 714.6121 | 383.3047 | 374.5122 | 362.5559
2052.5979 | 711.1931 | 383.2124 | 374.6355 | 362.4015
2053.5979 | 709.664 | 383.106 | 374.761 | 362.4275
2054.5979 | 706.4961 | 383.3394 | 374.5567 | 362.2885
2055.5979 | 705.3752 | 382.6832 | 375.0324 | 362.1765
2056.5979 | 704.1615 | 382.2396 | 375.2814 | 362.5038
2057.5979 | 705.0438 | 382.0274 | 375.0876 | 362.4989
2058.5979 | 704.4901 | 381.8385 | 374.6531 | 361.8457
2059.5979 | 704.9535 | 382.2096 | 374.005 | 361.7443
2060.5979 | 705.4053 | 382.2879 | 373.6336 | 361.1293
2061.5979 | 708.2394 | 382.1021 | 373.0901 | 361.3362
2062.5979 | 711.0301 | 382.3105 | 372.9576 | 360.6717
2063.5979 | 710.2383 | 382.85 | 372.6941 | 360.0814
2064.5979 | 710.1315 | 383.3718 | 372.7268 | 360.0173
2065.5979 | 711.0132 | 383.3108 | 372.5807 | 360.3483
2066.5979 | 716.4113 | 383.2624 | 372.2766 | 360.0448
2067.5979 | 718.8037 | 383.5386 | 372.6818 | 360.1691
2068.5979 | 720.2606 | 383.2112 | 372.6583 | 360.8533
2069.5979 | 717.6034 | 383.2835 | 372.8512 | 360.9652
2070.5979 | 715.2285 | 383.2442 | 373.7837 | 361.1963
2071.5979 | 713.2908 | 383.1592 | 373.7838 | 361.6295
2072.5979 | 711.6935 | 383.1123 | 374.3377 | 362.9665
2073.5979 | 710.2888 | 383.3628 | 374.1664 | 363.5995
2074.5979 | 710.6346 | 383.3873 | 374.321 | 364.6182
2075.5979 | 712.5271 | 383.5346 | 374.2394 | 365.2401
2076.5979 | 711.8272 | 383.9338 | 375.1453 | 365.7232
2077.5979 | 712.2939 | 384.2967 | 374.7235 | 365.0653
2078.5979 | 711.6639 | 384.3545 | 374.1681 | 364.9263
2079.5979 | 711.5499 | 384.1415 | 373.5943 | 364.5165
2080.5979 | 710.736 | 383.9937 | 372.8998 | 365.0567
2081.5979 | 708.2696 | 384.0837 | 372.2578 | 364.8896
2082.5979 | 709.1138 | 383.7976 | 371.6592 | 364.6187
2083.5979 | 711.274 | 383.4238 | 371.6454 | 364.4131
2084.5979 | 707.6554 | 383.3437 | 371.5939 | 364.6408
2085.5979 | 704.3999 | 383.4033 | 371.3924 | 364.9396
2086.5979 | 704.2209 | 383.5978 | 371.1267 | 364.3009
2087.5979 | 704.754 | 383.0962 | 370.9386 | 363.6451
2088.5979 | 706.0362 | 383.0439 | 370.1739 | 363.1066
2089.5979 | 706.2867 | 382.3795 | 369.587 | 362.7533
2090.5979 | 708.532 | 382.1165 | 369.5909 | 362.6281
2091.5979 | 709.6851 | 381.6663 | 369.7645 | 362.5394
2092.5979 | 710.4918 | 382.1613 | 370.5541 | 362.5209
2093.5979 | 709.8552 | 382.5903 | 370.8749 | 362.6306
2094.5979 | 709.4997 | 382.856 | 371.2836 | 363.5306
2095.5979 | 707.7937 | 382.8391 | 371.5051 | 363.5541
2096.5979 | 705.6432 | 383.0512 | 371.9365 | 363.2546
2097.5979 | 704.7593 | 382.9932 | 372.3072 | 363.6332
2098.5979 | 702.9032 | 383.2148 | 372.5103 | 363.393
2099.5979 | 700.8917 | 382.8493 | 372.6976 | 363.5102
2100.5979 | 701.8255 | 383.2659 | 373.0269 | 363.4377
2101.5979 | 703.5201 | 383.0698 | 373.0303 | 363.484
2102.5979 | 705.3373 | 382.9552 | 373.3391 | 363.8991
2103.5979 | 702.7408 | 382.7904 | 373.6341 | 363.6245
2104.5979 | 700.9993 | 382.6854 | 373.5689 | 363.6848
2105.5979 | 700.655 | 382.6252 | 373.1777 | 363.5113
2106.5979 | 699.4997 | 382.2196 | 373.4334 | 363.3794
2107.5979 | 699.8548 | 382.0816 | 373.3082 | 362.9847
2108.5979 | 700.7026 | 381.9983 | 373.1438 | 363.6983
2109.5979 | 700.615 | 381.8738 | 373.0589 | 363.5532
2110.5979 | 699.2544 | 381.8574 | 373.6808 | 364.2158
2111.5979 | 698.7741 | 381.9711 | 374.3075 | 364.2275
2112.5979 | 701.0546 | 382.6464 | 374.4285 | 365.3485
2113.5979 | 703.9208 | 383.4418 | 374.6071 | 365.981
2114.5979 | 708.7911 | 383.4328 | 374.5383 | 366.1202
2115.5979 | 707.95 | 383.6227 | 374.9785 | 367.2902
2116.5979 | 708.9962 | 383.5488 | 374.5539 | 367.201
2117.5979 | 711.2131 | 383.8275 | 374.9042 | 366.8699
2118.5979 | 712.2897 | 383.6737 | 374.4 | 366.341
2119.5979 | 710.0079 | 383.6364 | 373.8396 | 366.0254
2120.5979 | 706.7304 | 383.9349 | 374.0022 | 365.4681
2121.5979 | 706.2896 | 384.5323 | 374.0477 | 364.77
2122.5979 | 710.4672 | 384.353 | 373.6147 | 364.8685
2123.5979 | 713.4149 | 384.2664 | 373.3755 | 364.745
2124.5979 | 714.4134 | 384.1251 | 373.4151 | 364.3095
2125.5979 | 715.9912 | 383.8933 | 373.4567 | 364.473
2126.5979 | 720.0739 | 383.6084 | 373.7714 | 364.8818
2127.5979 | 720.8931 | 383.4689 | 373.7614 | 364.7907
2128.5979 | 719.0656 | 383.4651 | 374.2562 | 364.4152
2129.5979 | 716.4473 | 382.9864 | 374.2239 | 364.0247
2130.5979 | 712.0987 | 382.9571 | 374.2057 | 363.814
2131.5979 | 711.2123 | 382.9369 | 374.2842 | 363.0909
2132.5979 | 709.8942 | 383.3678 | 374.1653 | 364.4086
2133.5979 | 709.6839 | 383.4924 | 374.6189 | 364.4614
2134.5979 | 709.4984 | 383.3742 | 374.5165 | 365.1994
2135.5979 | 710.75 | 383.3496 | 374.5161 | 365.4533
2136.5979 | 709.8974 | 383.437 | 374.3272 | 364.8855
2137.5979 | 711.5302 | 383.4205 | 374.2678 | 364.5488
2138.5979 | 709.8985 | 383.3944 | 374.6427 | 364.3956
2139.5979 | 708.5355 | 383.4568 | 375.2236 | 365.1296
2140.5979 | 709.7026 | 383.0266 | 375.2715 | 365.2459
2141.5979 | 710.5626 | 383.1139 | 375.5832 | 365.4516
2142.5979 | 711.4288 | 383.0822 | 375.2024 | 365.8108
2143.5979 | 711.2275 | 382.8215 | 375.4342 | 365.7198
2144.5979 | 712.9546 | 382.2695 | 375.2174 | 365.4381
2145.5979 | 713.5154 | 381.9389 | 374.8132 | 365.3076
2146.5979 | 716.3474 | 382.1762 | 374.9751 | 365.5288
2147.5979 | 717.2332 | 382.3942 | 374.4471 | 366.1418
2148.5979 | 716.744 | 382.3309 | 374.1367 | 366.5278
2149.5979 | 715.4148 | 382.3366 | 373.9963 | 366.6456
2150.5979 | 716.5323 | 382.7571 | 374.7489 | 366.7153
2151.5979 | 718.9437 | 382.6857 | 374.7916 | 366.8943
2152.5979 | 722.3824 | 382.9013 | 374.6645 | 366.3084
2153.5979 | 722.2967 | 383.1597 | 374.8519 | 366.2917
2154.5979 | 723.5732 | 383.1307 | 375.348 | 366.478
2155.5979 | 725.0569 | 383.0894 | 375.217 | 366.3544
2156.5979 | 726.5212 | 383.0061 | 375.5723 | 366.3867
2157.6135 | 726.7577 | 383.1644 | 375.6038 | 366.0886
2158.5979 | 728.4194 | 382.5857 | 375.3322 | 366.7531
2159.5979 | 726.5633 | 382.5123 | 376.2823 | 367.4009
2160.5979 | 724.8599 | 382.8798 | 375.965 | 367.183
2161.5979 | 723.3185 | 382.7485 | 376.8112 | 367.2825
2162.5979 | 723.5791 | 382.6125 | 376.3017 | 366.8695
2163.5979 | 720.2686 | 382.8288 | 376.0676 | 367.3382
2164.5979 | 716.2908 | 383.0556 | 376.4185 | 367.3897
2165.5979 | 713.2324 | 383.197 | 376.8452 | 366.9442
2166.5979 | 707.9897 | 383.2159 | 376.8954 | 366.483
2167.5979 | 707.2178 | 384.5456 | 376.7355 | 366.3037
2168.5979 | 706.2593 | 384.9931 | 376.589 | 366.6424
2169.5979 | 710.0033 | 385.0786 | 376.8701 | 367.8277
2170.5979 | 714.1083 | 385.1675 | 377.194 | 368.1127
2171.5979 | 717.5236 | 385.241 | 378.1411 | 368.829
2172.5979 | 716.3085 | 385.2306 | 377.8579 | 368.824
2173.5979 | 712.1673 | 385.1755 | 377.9823 | 369.2804
2174.5979 | 713.952 | 384.8482 | 378.1534 | 370.6242
2175.5979 | 719.3467 | 384.8651 | 378.3184 | 370.5721
2176.5979 | 719.8267 | 384.4586 | 377.8052 | 370.939
2177.5979 | 722.3473 | 384.7307 | 378.056 | 370.7857
2178.5979 | 725.5741 | 384.9607 | 378.7427 | 371.67
2179.5979 | 728.9973 | 384.9277 | 380.1487 | 371.6744
2180.5979 | 730.6701 | 385.0222 | 379.9908 | 372.0887
2181.5979 | 732.8617 | 384.7746 | 379.714 | 371.9614
2182.5979 | 733.186 | 385.5279 | 379.6552 | 372.3222
2183.5979 | 731.4656 | 385.4778 | 379.6839 | 371.9374
2184.5979 | 728.9442 | 385.4839 | 379.249 | 372.2258
2185.5979 | 726.5539 | 385.4203 | 378.9378 | 372.3345
2186.5979 | 723.2887 | 385.4675 | 378.9484 | 372.2043
2187.5979 | 721.984 | 385.6667 | 378.941 | 372.0664
2188.5979 | 717.7164 | 386.0873 | 379.064 | 371.6705
2189.5979 | 715.9692 | 386.1345 | 379.5068 | 372.1314
2190.5979 | 715.1129 | 386.4714 | 379.8326 | 371.9534
2191.5979 | 712.9467 | 387.1957 | 380.4985 | 372.3402
2192.5979 | 710.7565 | 387.8305 | 380.6501 | 372.4567
2193.5979 | 708.4113 | 387.978 | 380.8447 | 373.8793
2194.5979 | 704.9974 | 388.2558 | 381.4115 | 373.8292
2195.5979 | 703.1565 | 388.4281 | 380.9502 | 374.1402
2196.5979 | 705.7653 | 388.2605 | 380.4715 | 373.9744
2197.5979 | 709.1762 | 388.0114 | 380.3735 | 374.2323
2198.5979 | 710.4942 | 387.6633 | 380.1934 | 374.4502
2199.5979 | 710.7951 | 387.541 | 380.2604 | 374.6037
2200.5979 | 710.5387 | 387.1559 | 380.9935 | 374.5229
2201.6135 | 713.1563 | 386.9458 | 381.0032 | 375.0009
2202.5979 | 714.6144 | 386.5012 | 380.8505 | 374.7607
2203.5979 | 713.7822 | 386.4322 | 381.459 | 374.7563
2204.5979 | 714.4901 | 386.378 | 381.8434 | 375.1054
2205.5979 | 717.2188 | 386.3248 | 381.6006 | 374.5107
2206.5979 | 720.799 | 386.2349 | 381.6798 | 375.2721
2207.5979 | 719.6159 | 386.0769 | 381.7025 | 375.1147
2208.5979 | 720.5065 | 386.1271 | 381.4185 | 374.7391
2209.5979 | 725.5758 | 386.247 | 381.2555 | 375.3852
2210.5979 | 730.0915 | 386.4622 | 381.7704 | 375.2566
2211.5979 | 733.5742 | 385.9963 | 381.5287 | 375.0671
2212.5979 | 732.9307 | 385.9603 | 381.5645 | 375.1084
2213.5979 | 732.9654 | 386.1259 | 382.037 | 375.1715
2214.5979 | 737.0921 | 385.9595 | 382.3679 | 375.0227
2215.5979 | 740.936 | 385.9783 | 382.6007 | 374.9142
2216.5979 | 741.6692 | 385.963 | 382.7656 | 375.137
2217.5979 | 741.6667 | 385.9599 | 382.6256 | 375.838
2218.5979 | 740.0979 | 385.7706 | 382.6788 | 375.8308
2219.5979 | 736.958 | 385.6117 | 382.7314 | 375.67
2220.5979 | 731.2563 | 386.3296 | 382.6097 | 375.7717
2221.5979 | 725.367 | 386.1595 | 382.423 | 375.4409
2222.5979 | 721.1527 | 386.3056 | 382.0322 | 375.2048
2223.5979 | 719.2254 | 386.5384 | 381.7996 | 375.0451
2224.5979 | 717.5646 | 387.146 | 381.6021 | 375.7583
2225.5979 | 717.0304 | 387.3505 | 381.996 | 375.8496
2226.5979 | 713.8597 | 387.3838 | 381.9093 | 375.2603
2227.5979 | 712.6658 | 387.4108 | 382.2464 | 375.0334
2228.5979 | 711.8996 | 387.8132 | 382.2523 | 374.227
2229.5979 | 711.7901 | 387.6485 | 382.0163 | 374.3258
2230.5979 | 710.7756 | 387.5509 | 382.0033 | 374.1973
2231.5979 | 710.7915 | 387.3144 | 381.9719 | 374.4218
2232.5979 | 711.085 | 387.4285 | 381.8335 | 374.1445
2233.5979 | 710.1135 | 387.0768 | 381.5165 | 374.0315
2234.5979 | 709.3607 | 387.243 | 381.177 | 373.6672
2235.5979 | 708.8592 | 386.9555 | 380.8616 | 374.3023
2236.5979 | 707.377 | 386.8618 | 380.9651 | 373.7841
2237.5979 | 707.5319 | 387.3661 | 382.1285 | 373.6809
2238.5979 | 707.9645 | 387.4905 | 382.6037 | 374.311
2239.5979 | 708.4861 | 387.5252 | 382.9063 | 374.8498
2240.5979 | 708.4893 | 387.7663 | 382.9885 | 375.2241
2241.5979 | 707.2782 | 387.8314 | 383.5098 | 375.4395
2242.5979 | 704.4824 | 387.8983 | 383.63 | 376.0315
2243.5979 | 702.4668 | 388.1541 | 383.8418 | 376.1227
2244.5979 | 703.4499 | 388.6453 | 383.8706 | 376.7604
2245.5979 | 703.3987 | 388.6118 | 384.1438 | 376.8437
2246.5979 | 702.612 | 388.6996 | 384.6721 | 377.0101
2247.5979 | 701.122 | 388.9651 | 384.4767 | 377.4719
2248.5979 | 700.3489 | 389.1231 | 385.0151 | 378.2447
2249.5979 | 698.7887 | 389.6803 | 384.9387 | 378.7843
2250.5979 | 698.145 | 390.1974 | 384.9691 | 379.0347
2251.5979 | 699.5122 | 390.6574 | 385.5282 | 378.4998
2252.5979 | 702.7295 | 391.3465 | 386.0786 | 378.9183
2253.5979 | 706.5586 | 391.5956 | 385.6853 | 378.5679
2254.5979 | 709.214 | 391.7003 | 385.2399 | 379.2899
2255.5979 | 709.5718 | 392.1392 | 385.6709 | 379.1596
2256.5979 | 708.6965 | 392.4773 | 385.6282 | 379.0076
2257.5979 | 707.1739 | 392.7782 | 385.3846 | 379.3573
2258.5979 | 706.5069 | 393.6906 | 385.9478 | 379.9582
2259.5979 | 708.74 | 394.1052 | 386.345 | 379.8338
2260.5979 | 709.3295 | 394.3835 | 386.5469 | 380.2953
2261.5979 | 710.4438 | 394.3612 | 386.6977 | 380.7086
2262.5979 | 710.6016 | 394.7084 | 386.655 | 381.323
2263.5979 | 713.2975 | 395.0683 | 386.804 | 381.6301
2264.5979 | 713.5035 | 395.5239 | 387.3398 | 382.401
2265.5979 | 710.8908 | 395.5735 | 387.1246 | 382.6759
2266.5979 | 710.3125 | 395.8471 | 386.8344 | 382.814
2267.5979 | 709.0514 | 396.3657 | 386.7054 | 382.4714
2268.5979 | 709.8187 | 396.5553 | 386.6951 | 382.9483
2269.5979 | 715.0973 | 396.5095 | 387.0846 | 382.9401
2270.5979 | 715.5462 | 396.5138 | 387.7102 | 383.1418
2271.5979 | 718.7286 | 396.4786 | 388.1921 | 383.3018
2272.5979 | 717.0707 | 396.3879 | 388.1707 | 382.8775
2273.5979 | 713.7071 | 396.7811 | 388.3746 | 382.4291
2274.5979 | 712.4842 | 396.9538 | 388.6292 | 382.9068
2275.5979 | 712.9314 | 396.93 | 389.0243 | 382.5938
2276.5979 | 713.5649 | 396.8828 | 389.0637 | 382.2663
2277.5979 | 714.9383 | 397.2706 | 389.1626 | 382.114
2278.5979 | 715.2549 | 397.3504 | 389.5695 | 382.4152
2279.5979 | 715.2097 | 397.1092 | 389.7084 | 382.6411
2280.5979 | 714.989 | 396.9008 | 389.6234 | 382.5698
2281.5979 | 714.4007 | 396.8587 | 389.5995 | 382.7061
2282.5979 | 714.6851 | 396.957 | 390.2338 | 382.5221
2283.5979 | 714.4289 | 397.3011 | 390.5585 | 382.6468
2284.5979 | 712.6304 | 397.0375 | 390.4381 | 383.0923
2285.5979 | 711.726 | 397.1809 | 390.4285 | 383.2317
2286.5979 | 710.9153 | 397.1847 | 390.2015 | 383.2588
2287.5979 | 709.4405 | 397.2238 | 389.8648 | 382.9718
2288.5979 | 707.9138 | 397.0795 | 389.874 | 382.3038
2289.5979 | 707.7966 | 396.9462 | 389.7082 | 381.9181
2290.5979 | 708.7631 | 396.9902 | 390.1527 | 381.5495
2291.5979 | 708.463 | 396.8728 | 389.4633 | 381.1826
2292.5979 | 706.749 | 397.1604 | 389.1742 | 380.5718
2293.5979 | 705.2957 | 397.1133 | 388.8145 | 380.0539
2294.5979 | 705.0044 | 396.9915 | 388.8308 | 379.4969
2295.5979 | 708.3236 | 396.9571 | 389.0625 | 379.5957
2296.5979 | 713.1628 | 397.0821 | 388.8089 | 379.5087
2297.5979 | 713.9132 | 396.8615 | 389.1282 | 379.4937
2298.5979 | 714.1161 | 396.5772 | 389.475 | 379.7867
2299.5979 | 715.6185 | 396.3973 | 389.5257 | 379.9103
2300.5979 | 714.8873 | 396.4564 | 389.8965 | 379.9759
2301.5979 | 715.6912 | 396.4132 | 390.3868 | 380.272
2302.6135 | 718.2868 | 396.1423 | 390.2132 | 380.7092
2303.5979 | 720.1247 | 396.088 | 390.0131 | 380.8681
2304.6135 | 720.0536 | 396.1809 | 390.0841 | 381.6516
2305.5979 | 718.9912 | 396.6853 | 390.2227 | 382.0931
2306.5979 | 719.4517 | 396.7401 | 390.2669 | 382.6706
2307.5979 | 720.4903 | 396.5947 | 390.1734 | 382.7837
2308.5979 | 718.2225 | 396.5729 | 390.2253 | 382.4472
2309.5979 | 716.4246 | 396.6562 | 389.9163 | 382.8831
2310.5979 | 713.7175 | 396.9689 | 390.0321 | 383.091
2311.5979 | 714.3292 | 396.9418 | 390.5795 | 383.7686
2312.5979 | 715.7756 | 397.3194 | 390.7903 | 384.311
2313.5979 | 716.0417 | 397.6806 | 391.0545 | 385.1347
2314.5979 | 716.7862 | 397.3587 | 391.2943 | 385.0296
2315.5979 | 716.5132 | 397.6314 | 391.2437 | 385.3063
2316.5979 | 714.6253 | 397.8247 | 391.651 | 385.3453
2317.5979 | 714.8431 | 398.1313 | 391.696 | 386.1678
2318.5979 | 715.9433 | 398.0278 | 391.4423 | 385.7677
2319.5979 | 715.1538 | 398.0179 | 391.8024 | 386.3082
2320.5979 | 715.7078 | 398.3845 | 392.35 | 386.0751
2321.5979 | 716.6112 | 398.6633 | 392.3821 | 386.5186
2322.5979 | 721.0991 | 398.2733 | 392.2202 | 386.4979
2323.5979 | 724.753 | 398.2036 | 392.9444 | 387.2893
2324.5979 | 726.6816 | 398.1294 | 392.6829 | 387.2953
2325.5979 | 725.6541 | 398.0288 | 392.5271 | 386.3397
2326.5979 | 722.5043 | 397.8046 | 392.6059 | 386.3995
2327.5979 | 719.0158 | 397.7812 | 392.8655 | 386.4244
2328.5979 | 715.5871 | 397.8786 | 393.1362 | 387.1552
2329.5979 | 713.1653 | 397.7392 | 393.2015 | 386.7951
2330.5979 | 710.5746 | 397.1726 | 392.9465 | 387.4891
2331.5979 | 708.2799 | 397.273 | 392.9481 | 388.1997
2332.5979 | 708.952 | 397.2482 | 392.7482 | 387.7379
2333.5979 | 710.0602 | 397.3435 | 392.3645 | 387.9654
2334.5979 | 713.7375 | 397.7274 | 392.3745 | 388.481
2335.5979 | 715.4736 | 398.05 | 393.4628 | 388.2499
2336.5979 | 716.2539 | 397.77 | 393.3154 | 388.509
2337.5979 | 716.0394 | 397.7579 | 393.0447 | 388.1364
2338.5979 | 715.4777 | 397.7078 | 392.9863 | 388.2728
2339.5979 | 712.6899 | 397.5278 | 393.1846 | 387.9664
2340.5979 | 711.5226 | 397.5226 | 393.2033 | 387.735
2341.5979 | 713.3031 | 397.5566 | 393.2921 | 387.7592
2342.5979 | 714.4525 | 397.9209 | 393.0884 | 387.8631
2343.5979 | 712.8151 | 397.8762 | 393.5718 | 388.4094
2344.5979 | 713.9093 | 398.235 | 393.7072 | 389.4996
2345.5979 | 715.1974 | 398.5747 | 394.3477 | 389.9113
2346.5979 | 716.3068 | 399.2005 | 394.7024 | 390.1161
2347.5979 | 718.0013 | 399.8318 | 395.7122 | 390.3795
2348.5979 | 719.0876 | 400.3748 | 396.2673 | 390.7902
2349.5979 | 719.5236 | 400.2476 | 396.3428 | 390.7178
2350.5979 | 720.8775 | 400.3189 | 396.4351 | 391.4291
2351.5979 | 725.4675 | 400.5871 | 396.9092 | 391.2408
2352.5979 | 728.0807 | 400.4144 | 397.2936 | 392.2727
2353.5979 | 730.1733 | 400.502 | 397.4407 | 391.8685
2354.5979 | 728.7418 | 400.77 | 397.5854 | 392.6065
2355.5979 | 726.5995 | 401.5409 | 398.1798 | 393.1486
2356.5979 | 728.8852 | 402.298 | 398.7023 | 392.8819
2357.5979 | 732.3415 | 402.5838 | 399.1687 | 393.7664
2358.5979 | 735.8258 | 402.9366 | 399.7707 | 394.5012
2359.5979 | 737.2504 | 403.0647 | 399.7156 | 394.3425
2360.5979 | 735.1264 | 403.0861 | 399.9513 | 394.4877
2361.5979 | 732.9675 | 403.1157 | 400.3859 | 394.7559
2362.5979 | 730.6 | 403.8502 | 401.325 | 395.3991
2363.5979 | 729.9787 | 404.2703 | 401.4471 | 396.2742
2364.6135 | 731.856 | 404.3417 | 401.2796 | 396.9549
2365.5979 | 731.0657 | 404.5072 | 401.3277 | 396.7387
2366.6135 | 729.135 | 404.669 | 401.8442 | 396.5792
2367.5979 | 729.1504 | 404.6007 | 401.9098 | 396.1506
2368.6135 | 726.6052 | 404.9462 | 403.1547 | 396.0241
2369.5979 | 725.8604 | 406.3299 | 403.4472 | 397.1725
2370.5979 | 725.3716 | 406.5721 | 403.9541 | 397.7074
2371.5979 | 723.8688 | 406.6011 | 404.0804 | 398.2166
2372.5979 | 721.7213 | 406.882 | 404.4585 | 398.4979
2373.5979 | 718.9777 | 406.9168 | 404.7394 | 398.4059
2374.5979 | 716.9806 | 407.1203 | 405.289 | 398.3264
2375.5979 | 717.9554 | 407.2169 | 404.9464 | 397.5942
2376.5979 | 715.2379 | 407.5251 | 404.6174 | 398.657
2377.5979 | 711.2745 | 407.6403 | 404.6334 | 398.4168
2378.5979 | 709.6981 | 407.8274 | 404.8923 | 397.7673
2379.5979 | 708.4504 | 408.087 | 404.7935 | 397.5521
2380.5979 | 707.7556 | 408.732 | 404.6676 | 397.2021
2381.5979 | 708.7387 | 408.662 | 404.4132 | 396.4845
2382.5979 | 708.7965 | 408.8685 | 404.4549 | 396.2243
2383.5979 | 708.3462 | 408.8854 | 404.5522 | 396.2042
2384.5979 | 707.1159 | 409.3553 | 404.22 | 396.3294
2385.5979 | 708.5386 | 409.5454 | 404.2997 | 397.4024
2386.5979 | 709.1625 | 409.6368 | 404.1508 | 398.0556
2387.5979 | 710.4008 | 409.3126 | 403.6447 | 398.3108
2388.5979 | 712.611 | 409.6197 | 403.4065 | 398.3149
2389.5979 | 712.5593 | 409.2605 | 402.988 | 398.0372
2390.5979 | 712.3214 | 408.9392 | 402.4171 | 398.7814
2391.5979 | 712.5982 | 408.5587 | 402.1363 | 398.0622
2392.5979 | 710.9076 | 408.3407 | 402.6296 | 398.8996
2393.5979 | 708.4015 | 407.8514 | 402.386 | 399.1285
2394.5979 | 705.6274 | 407.7512 | 401.9624 | 398.6834
2395.5979 | 705.2116 | 407.9533 | 402.5705 | 398.3849
2396.5979 | 703.665 | 407.6489 | 402.3609 | 398.2065
2397.5979 | 701.8959 | 407.8093 | 402.4478 | 397.7871
2398.5979 | 699.9321 | 408.0994 | 402.3909 | 397.5574
2399.5979 | 700.3347 | 407.7286 | 402.5278 | 397.7958
2400.5979 | 700.481 | 407.3591 | 402.3215 | 396.9505
2401.5979 | 702.1504 | 407.3284 | 401.8053 | 397.2293
2402.5979 | 703.2466 | 407.4348 | 402.0021 | 397.3373
2403.5979 | 703.1231 | 406.7741 | 401.935 | 396.7837
2404.5979 | 701.9535 | 406.6345 | 402.1029 | 396.3381
2405.5979 | 702.1134 | 406.8858 | 402.3653 | 396.3864
2406.5979 | 703.3188 | 406.8043 | 402.4698 | 395.7785
2407.5979 | 706.1104 | 407.3668 | 403.0765 | 395.9605
2408.5979 | 707.7212 | 407.599 | 403.3615 | 396.366
2409.5979 | 707.427 | 407.27 | 402.8575 | 396.2649
2410.5979 | 709.0571 | 407.5232 | 402.5318 | 395.5385
2411.5979 | 710.2814 | 407.4027 | 402.3286 | 395.4946
2412.5979 | 711.2225 | 407.2073 | 402.5206 | 394.9858
2413.5979 | 711.6875 | 407.088 | 402.2391 | 394.6571
2414.5979 | 710.7933 | 407.189 | 402.0924 | 394.1725
2415.5979 | 709.5003 | 407.1029 | 402.2311 | 394.5745
2416.5979 | 706.7839 | 406.8626 | 401.945 | 394.2995
2417.5979 | 705.1079 | 406.9367 | 402.2026 | 394.546
2418.5979 | 706.0995 | 406.8184 | 402.0533 | 395.3046
2419.5979 | 709.5325 | 406.4761 | 401.6822 | 396.2007
2420.5979 | 709.2742 | 406.4766 | 401.8857 | 395.5706
2421.5979 | 709.3609 | 406.5227 | 401.7464 | 394.9622
2422.5979 | 710.0185 | 406.7837 | 401.4557 | 394.9059
2423.5979 | 712.4997 | 406.9065 | 401.5144 | 394.6394
2424.5979 | 714.6856 | 407.0509 | 401.1597 | 394.45
2425.5979 | 715.9284 | 407.2513 | 400.9303 | 394.4125
2426.5979 | 720.5834 | 407.2948 | 400.8808 | 393.9958
2427.5979 | 723.3885 | 407.1513 | 400.8803 | 394.7579
2428.5979 | 722.3481 | 407.1264 | 400.7876 | 395.5377
2429.5979 | 721.8491 | 406.8342 | 400.6474 | 395.5495
2430.5979 | 720.9305 | 406.7111 | 400.3514 | 395.6198
2431.5979 | 720.3689 | 407.024 | 400.0655 | 395.994
2432.5979 | 720.3346 | 407.025 | 400.7166 | 397.2671
2433.5979 | 717.8195 | 407.1513 | 400.8912 | 397.4125
2434.6135 | 714.2715 | 407.7386 | 400.9162 | 397.3629
2435.5979 | 712.6141 | 407.9659 | 400.9985 | 397.2097
2436.5979 | 711.3179 | 408.2899 | 400.7776 | 396.9135
2437.5979 | 711.3355 | 408.8139 | 400.54 | 396.331
2438.5979 | 712.7167 | 408.8705 | 400.7348 | 396.2316
2439.5979 | 714.7109 | 408.6288 | 400.5648 | 396.1125
2440.5979 | 715.0082 | 408.6538 | 401.083 | 395.9673
2441.5979 | 714.6208 | 408.2962 | 400.9576 | 396.0867
2442.5979 | 714.0841 | 407.6349 | 400.6463 | 395.9173
2443.5979 | 714.2437 | 407.1475 | 400.1864 | 395.349
2444.5979 | 713.5223 | 407.0387 | 399.7282 | 395.0409
2445.5979 | 714.1523 | 406.7288 | 399.5899 | 395.1592
2446.5979 | 715.7817 | 406.8416 | 399.8501 | 395.9729
2447.5979 | 717.0954 | 407.2253 | 400.4059 | 395.882
2448.5979 | 717.7901 | 407.1268 | 400.8709 | 396.1096
2449.5979 | 720.044 | 406.9557 | 400.7455 | 396.4393
2450.5979 | 721.0379 | 406.8233 | 400.563 | 395.9635
2451.5979 | 720.9166 | 406.7367 | 400.5389 | 396.1267
2452.5979 | 722.8951 | 406.2946 | 400.7513 | 396.0317
2453.5979 | 723.8644 | 405.8225 | 400.5201 | 395.5942
2454.5979 | 723.4696 | 405.6191 | 400.8259 | 396.2105
2455.5979 | 722.3896 | 405.6144 | 401.4252 | 396.3934
2456.5979 | 722.0509 | 405.7892 | 401.2117 | 396.2809
2457.5979 | 721.2409 | 405.8599 | 401.0926 | 395.9177
2458.5979 | 721.4034 | 405.6431 | 401.2691 | 396.2084
2459.5979 | 721.3426 | 405.7357 | 401.5463 | 397.3176
2460.5979 | 721.5694 | 405.8306 | 401.4021 | 397.0857
2461.5979 | 723.0698 | 406.0987 | 401.5704 | 397.1638
2462.5979 | 722.5399 | 405.8109 | 402.2299 | 397.1936
2463.5979 | 720.8769 | 405.7031 | 401.8256 | 397.077
2464.5979 | 718.8122 | 406.2059 | 401.8949 | 397.3695
2465.5979 | 718.1655 | 406.58 | 401.943 | 397.7183
2466.5979 | 717.7975 | 406.8295 | 402.317 | 397.6123
2467.5979 | 717.1292 | 406.2504 | 401.7179 | 397.7586
2468.5979 | 717.0924 | 406.0944 | 401.2982 | 397.4724
2469.5979 | 717.1747 | 406.0674 | 401.432 | 396.8814
2470.5979 | 716.4039 | 406.0994 | 401.0789 | 396.5308
2471.5979 | 715.5111 | 406.0051 | 400.9525 | 396.4936
2472.5979 | 716.5652 | 405.7446 | 400.5609 | 396.0745
2473.5979 | 718.2489 | 405.7853 | 400.3993 | 396.0893
2474.5979 | 719.9144 | 405.7912 | 400.1419 | 395.4501
2475.5979 | 720.6092 | 405.7556 | 399.7934 | 394.9854
2476.5979 | 722.4757 | 406.4505 | 399.6207 | 395.0125
2477.5979 | 723.2544 | 406.4564 | 399.7123 | 395.1494
2478.5979 | 722.4197 | 406.4501 | 400.3223 | 395.5158
2479.5979 | 723.3427 | 406.3347 | 400.8827 | 395.922
2480.5979 | 724.9221 | 406.3686 | 400.6982 | 395.9602
2481.5979 | 729.4141 | 406.9605 | 400.7372 | 396.3514
2482.5979 | 733.957 | 406.6542 | 401.0712 | 396.7159
2483.5979 | 735.2837 | 406.5385 | 401.5942 | 396.9954
2484.6135 | 733.3246 | 406.4408 | 401.7973 | 398.1212
2485.5979 | 731.3923 | 407.0451 | 401.8835 | 398.5652
2486.6135 | 731.577 | 407.4232 | 401.988 | 399.1967
2487.5979 | 733.1384 | 407.8225 | 402.179 | 399.5526
2488.5979 | 734.4092 | 407.8643 | 402.3182 | 399.4939
2489.5979 | 734.8398 | 407.9551 | 402.877 | 400.1085
2490.5979 | 735.6684 | 407.9684 | 404.2658 | 399.9474
2491.5979 | 736.2184 | 407.9358 | 405.1226 | 400.3278
2492.5979 | 735.89 | 407.7035 | 405.297 | 400.734
2493.5979 | 737.3275 | 407.8354 | 405.4709 | 400.9142
2494.5979 | 737.682 | 407.7086 | 405.3868 | 401.845
2495.5979 | 735.5661 | 407.4603 | 404.9027 | 401.7615
2496.5979 | 732.455 | 407.3318 | 404.8974 | 401.3746
2497.5979 | 732.7648 | 407.8797 | 404.9462 | 401.7972
2498.5979 | 733.7679 | 408.1563 | 405.1538 | 401.6943
2499.5979 | 733.7105 | 407.6627 | 405.0187 | 401.8435
2500.5979 | 731.918 | 407.2844 | 404.6727 | 401.6676
2501.5979 | 731.0265 | 407.2488 | 404.3934 | 401.1801
2502.5979 | 730.9666 | 407.2481 | 403.8881 | 400.322
2503.5979 | 731.1899 | 407.0976 | 403.562 | 399.6795
2504.5979 | 731.5629 | 407.2094 | 403.5901 | 399.4669
2505.5979 | 731.9171 | 407.4018 | 403.4726 | 399.9028
2506.5979 | 731.4821 | 407.5659 | 403.7784 | 399.555
2507.5979 | 730.813 | 407.6809 | 403.5704 | 399.2939
2508.5979 | 731.9742 | 407.4895 | 403.4753 | 399.6876
2509.5979 | 733.5312 | 407.5531 | 403.7877 | 400.1481
2510.5979 | 734.6093 | 407.5203 | 404.6244 | 400.7382
2511.5979 | 733.354 | 407.444 | 405.4471 | 401.0312
2512.5979 | 734.6315 | 407.4221 | 406.0942 | 401.3125
2513.5979 | 735.2766 | 407.6675 | 406.6764 | 401.1987
2514.5979 | 736.0315 | 407.3049 | 406.7302 | 402.0931
2515.5979 | 737.5737 | 407.6708 | 407.0449 | 402.6673
2516.5979 | 738.5668 | 407.8782 | 408.0518 | 402.8289
2517.5979 | 739.3534 | 408.0141 | 407.9 | 402.5888
2518.5979 | 736.9331 | 407.6958 | 407.8335 | 403.1301
2519.5979 | 736.4368 | 407.9083 | 407.821 | 403.7748
2520.5979 | 737.287 | 407.9586 | 408.3143 | 403.5028
2521.5979 | 739.9374 | 408.236 | 408.3069 | 403.1889
2522.5979 | 743.5381 | 408.317 | 407.8781 | 403.3135
2523.5979 | 744.6255 | 408.2837 | 408.3609 | 403.4182
2524.5979 | 746.2623 | 408.9048 | 408.1443 | 403.9919
2525.5979 | 747.3164 | 409.1387 | 408.2295 | 404.4454
2526.5979 | 745.7194 | 409.3709 | 408.2372 | 405.1596
2527.5979 | 744.5197 | 410.024 | 408.5345 | 405.5829
2528.5979 | 742.5058 | 410.3431 | 409.3416 | 405.7794
2529.5979 | 739.4304 | 410.8448 | 409.2393 | 405.4564
2530.5979 | 736.5914 | 410.9726 | 408.7976 | 405.1554
2531.5979 | 734.5063 | 411.1175 | 408.2911 | 404.3623
2532.5979 | 733.8276 | 410.7949 | 407.5464 | 404.2066
2533.5979 | 734.0641 | 410.7918 | 407.0333 | 403.6634
2534.5979 | 734.425 | 410.5231 | 407.0341 | 403.4153
2535.5979 | 731.7308 | 410.3831 | 407.1064 | 402.9055
2536.5979 | 728.7756 | 410.4285 | 407.9384 | 402.7832
2537.5979 | 726.9062 | 410.673 | 408.1102 | 403.4306
2538.5979 | 725.2514 | 411.0814 | 408.153 | 403.0687
2539.5979 | 723.7251 | 410.9658 | 408.0008 | 402.6102
2540.5979 | 722.8098 | 410.5914 | 407.7809 | 402.2054
2541.5979 | 720.9981 | 410.4321 | 407.4271 | 402.2975
2542.5979 | 719.4063 | 410.3295 | 407.5188 | 402.1323
2543.5979 | 718.4293 | 410.3623 | 407.842 | 402.7793
2544.5979 | 716.4489 | 410.3738 | 407.4376 | 402.6426
2545.5979 | 716.7625 | 410.8107 | 407.665 | 402.4443
2546.5979 | 717.9931 | 410.908 | 408.0863 | 402.7918
2547.5979 | 719.2042 | 410.9175 | 407.6668 | 402.8264
2548.5979 | 720.4048 | 411.0205 | 407.4427 | 402.7736
2549.5979 | 722.011 | 410.9806 | 407.591 | 402.8871
2550.5979 | 724.0568 | 411.5416 | 407.9526 | 403.2471
2551.5979 | 726.1317 | 411.9149 | 408.0463 | 403.265
2552.5979 | 724.7681 | 411.8286 | 407.8113 | 403.5956
2553.5979 | 722.821 | 412.0095 | 407.3779 | 403.3844
2554.5979 | 721.6617 | 411.8666 | 407.0374 | 403.09
2555.6135 | 721.6959 | 411.8356 | 406.6848 | 403.5548
2556.6135 | 721.1629 | 411.5993 | 406.7895 | 403.3514
2557.6135 | 717.9467 | 411.539 | 406.6408 | 402.9143
2558.5979 | 715.8898 | 411.2502 | 406.3264 | 402.4625
2559.5979 | 715.1653 | 411.268 | 406.244 | 402.7774
2560.5979 | 716.015 | 410.854 | 406.2646 | 402.5805
2561.5979 | 716.6668 | 410.6073 | 406.0956 | 402.4118
2562.5979 | 715.7828 | 410.3417 | 405.8269 | 402.8804
2563.5979 | 715.6718 | 410.1879 | 405.8195 | 403.0758
2564.5979 | 715.9252 | 409.9114 | 405.7001 | 402.7659
2565.5979 | 716.2886 | 410.3164 | 405.6359 | 402.5412
2566.5979 | 715.886 | 410.5582 | 405.7338 | 402.3099
2567.5979 | 715.5603 | 410.6426 | 406.3257 | 402.3649
2568.5979 | 716.7754 | 411.0416 | 406.4724 | 402.0477
2569.5979 | 718.7846 | 411.4844 | 407.3592 | 401.7742
2570.5979 | 719.3874 | 411.4387 | 407.6779 | 401.3755
2571.5979 | 720.1393 | 411.414 | 407.7012 | 401.0201
2572.5979 | 721.5648 | 411.7564 | 408.0962 | 400.919
2573.5979 | 722.3441 | 411.8492 | 407.753 | 401.4117
2574.5979 | 723.1418 | 411.7127 | 408.1005 | 401.8504
2575.5979 | 723.4984 | 411.4859 | 407.877 | 401.914
2576.5979 | 724.516 | 411.3105 | 407.4163 | 402.6027
2577.5979 | 724.56 | 411.5551 | 406.9608 | 402.5321
2578.5979 | 726.1898 | 411.5536 | 407.1818 | 403.0391
2579.5979 | 728.0525 | 411.9475 | 406.9992 | 402.7406
2580.5979 | 728.982 | 412.075 | 406.835 | 402.2293
2581.5979 | 726.8957 | 411.9497 | 407.1768 | 402.2917
2582.5979 | 725.072 | 412.3058 | 407.7706 | 402.1481
2583.5979 | 725.9995 | 413.3812 | 408.1193 | 402.7067
2584.5979 | 727.9516 | 413.2859 | 409.1989 | 402.9115
2585.5979 | 728.4612 | 412.9339 | 409.0761 | 402.3758
2586.5979 | 728.9844 | 413.3362 | 408.968 | 402.2943
2587.5979 | 728.6609 | 413.4636 | 408.9143 | 402.3804
2588.5979 | 728.3042 | 413.9893 | 408.4764 | 402.5033
2589.5979 | 725.2676 | 413.8785 | 408.1076 | 402.3952
2590.5979 | 724.2671 | 414.4932 | 407.953 | 402.608
2591.5979 | 724.1188 | 414.6212 | 408.5405 | 402.4248
2592.5979 | 722.9683 | 414.15 | 408.3769 | 402.4845
2593.5979 | 720.4721 | 414.207 | 408.6065 | 402.5984
2594.5979 | 717.6202 | 414.3474 | 408.7003 | 402.5139
2595.5979 | 714.9468 | 414.1434 | 408.6297 | 402.0105
2596.5979 | 713.6876 | 413.9946 | 408.4402 | 401.5505
2597.5979 | 713.2743 | 413.6457 | 408.6392 | 402.7398
2598.5979 | 713.6649 | 413.6877 | 408.617 | 402.7022
2599.5979 | 714.0066 | 413.2319 | 408.4447 | 402.894
2600.5979 | 714.4774 | 413.2379 | 407.9892 | 402.5902
2601.5979 | 714.3623 | 413.3143 | 407.5282 | 402.0887
2602.5979 | 716.2233 | 412.8313 | 407.0339 | 401.7605
2603.5979 | 718.5155 | 412.6156 | 406.7009 | 401.6031
2604.5979 | 719.3742 | 412.1523 | 406.1938 | 401.0292
2605.5979 | 719.3107 | 411.8514 | 405.729 | 400.6529
2606.5979 | 719.7354 | 412.577 | 405.8612 | 401.2772
2607.5979 | 722.2553 | 412.8654 | 406.3486 | 401.5918
2608.5979 | 723.9478 | 412.7039 | 406.6841 | 401.5849
2609.5979 | 723.9893 | 412.4296 | 406.5843 | 401.9943
2610.5979 | 722.6952 | 412.5385 | 406.7183 | 402.3304
2611.5979 | 722.6412 | 412.8041 | 407.094 | 401.9054
2612.5979 | 724.1779 | 412.9096 | 407.1742 | 402.3519
2613.5979 | 729.1206 | 412.8097 | 407.4718 | 402.5082
2614.5979 | 733.704 | 412.9229 | 407.7414 | 402.765
2615.5979 | 736.1355 | 413.3086 | 408.3808 | 403.353
2616.5979 | 737.0849 | 413.3439 | 408.7649 | 403.9373
2617.5979 | 738.1036 | 413.3208 | 409.3811 | 404.3922
2618.5979 | 738.0276 | 413.6472 | 409.946 | 404.6287
2619.5979 | 740.6223 | 413.848 | 410.5204 | 405.3874
2620.5979 | 743.4078 | 413.8853 | 410.2146 | 405.7899
2621.5979 | 746.0627 | 413.5558 | 409.7512 | 406.0009
2622.5979 | 745.3728 | 413.5728 | 409.6144 | 405.9296
2623.5979 | 742.8519 | 413.5871 | 409.7822 | 406.0442
2624.5979 | 743.1975 | 413.7424 | 410.1456 | 405.8699
2625.5979 | 744.9744 | 414.1517 | 410.6075 | 406.1642
2626.5979 | 746.0358 | 414.3356 | 410.8395 | 407.1025
2627.5979 | 746.5257 | 414.699 | 410.8353 | 407.2919
2628.5979 | 746.2223 | 414.5366 | 410.7944 | 406.9758
2629.5979 | 744.885 | 414.7071 | 411.0079 | 407.2965
2630.5979 | 743.412 | 415.1888 | 411.4898 | 406.8075
2631.5979 | 742.6036 | 415.375 | 412.0189 | 406.7796
2632.5979 | 741.293 | 415.9761 | 412.1003 | 406.3504
2633.5979 | 741.3911 | 416.2354 | 412.22 | 407.37
2634.5979 | 741.8732 | 416.5617 | 412.4346 | 407.4512
2635.5979 | 739.9009 | 416.613 | 412.8918 | 407.1254
2636.5979 | 739.7612 | 416.7681 | 414.3322 | 407.3607
2637.5979 | 740.42 | 417.3451 | 414.1332 | 407.6505
2638.5979 | 740.5168 | 417.4523 | 413.8928 | 407.9042
2639.5979 | 740.6242 | 417.2194 | 413.4675 | 408.4033
2640.5979 | 739.6876 | 417.4539 | 414.1593 | 408.503
2641.5979 | 738.0389 | 417.233 | 413.9308 | 408.6582
2642.5979 | 736.2581 | 416.979 | 414.0049 | 408.8648
2643.5979 | 732.4439 | 417.255 | 413.6724 | 408.6848
2644.5979 | 727.7973 | 416.7946 | 413.2724 | 408.6705
2645.5979 | 723.6279 | 416.4311 | 413.2004 | 409.1696
2646.5979 | 721.2615 | 416.0987 | 412.8981 | 408.9886
2647.5979 | 719.6622 | 415.5794 | 412.3035 | 408.2081
2648.5979 | 718.0366 | 415.6088 | 412.0413 | 408.0397
2649.5979 | 716.961 | 415.755 | 411.422 | 407.8801
2650.5979 | 716.5306 | 415.8206 | 411.3997 | 408.0512
2651.5979 | 716.9197 | 415.557 | 411.3017 | 407.8595
2652.5979 | 718.4453 | 415.8413 | 411.2263 | 408.2286
2653.5979 | 718.5375 | 415.873 | 411.3969 | 408.4112
2654.5979 | 718.5129 | 415.8819 | 411.1848 | 408.0876
2655.5979 | 719.2366 | 415.9302 | 411.2015 | 407.9301
2656.5979 | 720.9785 | 415.8173 | 411.0088 | 407.5254
2657.5979 | 721.5103 | 415.5742 | 410.7763 | 407.1191
2658.5979 | 720.9237 | 415.4413 | 410.7166 | 407.2072
2659.5979 | 721.0966 | 415.8819 | 411.7837 | 407.7501
2660.5979 | 721.6612 | 416.0555 | 411.8184 | 408.2351
2661.5979 | 722.8481 | 416.6623 | 412.272 | 409.0103
2662.5979 | 724.8328 | 416.737 | 412.402 | 409.5635
2663.5979 | 727.2953 | 416.699 | 412.6523 | 410.1245
2664.5979 | 729.8854 | 417.1297 | 413.802 | 410.4347
2665.5979 | 731.8577 | 417.3391 | 414.3392 | 411.3711
2666.5979 | 732.671 | 417.6996 | 414.4281 | 411.6168
2667.5979 | 732.1571 | 417.3312 | 414.2619 | 411.0462
2668.5979 | 732.6802 | 417.2101 | 413.7916 | 410.7402
2669.5979 | 733.6895 | 417.0849 | 413.5706 | 410.2575
2670.5979 | 732.6489 | 417.0512 | 413.4876 | 410.0309
2671.5979 | 730.6149 | 417.0047 | 413.3584 | 409.8165
2672.5979 | 727.8629 | 417.3021 | 412.9871 | 409.0967
2673.5979 | 724.4086 | 417.3356 | 412.6605 | 408.8946
2674.5979 | 720.6403 | 417.1415 | 412.6571 | 408.4855
2675.5979 | 717.3316 | 417.0112 | 412.4646 | 407.7223
2676.5979 | 714.6884 | 416.7403 | 411.8278 | 407.7527
2677.5979 | 711.8788 | 416.6495 | 411.49 | 408.4691
2678.5979 | 710.2141 | 416.4118 | 411.8718 | 408.6041
2679.5979 | 709.4635 | 416.7594 | 411.4286 | 408.345
2680.5979 | 709.9915 | 417.1158 | 411.8131 | 407.8357
2681.5979 | 711.1833 | 417.7435 | 411.6823 | 407.4104
2682.5979 | 712.8034 | 418.4735 | 411.7018 | 407.4017
2683.5979 | 712.8121 | 418.6163 | 412.5794 | 407.5356
2684.5979 | 713.2786 | 418.8595 | 412.3349 | 407.4195
2685.5979 | 713.5437 | 418.9372 | 412.839 | 408.4242
2686.5979 | 714.5474 | 418.8275 | 413.0967 | 408.5133
2687.5979 | 714.8372 | 418.6544 | 413.0415 | 408.489
2688.5979 | 715.3569 | 418.6932 | 412.8482 | 408.2866
2689.5979 | 715.4219 | 418.8532 | 412.6027 | 408.491
2690.5979 | 716.9134 | 418.6558 | 412.3695 | 408.5146
2691.5979 | 719.2017 | 418.7328 | 412.163 | 409.0808
2692.5979 | 719.9963 | 418.8738 | 412.2883 | 409.9101
2693.5979 | 719.3566 | 419.085 | 412.9709 | 409.4844
2694.5979 | 717.6027 | 419.2495 | 412.8196 | 409.5099
2695.5979 | 718.9615 | 419.2212 | 413.2824 | 409.7075
2696.5979 | 723.0226 | 419.2537 | 413.3947 | 409.9371
2697.5979 | 728.7561 | 419.7567 | 415.5443 | 411.6246
2698.5979 | 735.3909 | 419.9139 | 416.2224 | 412.3221
2699.5979 | 743.6989 | 419.6036 | 416.4604 | 412.7022
2700.5979 | 749.3937 | 419.6757 | 416.7011 | 413.432
2701.5979 | 751.6253 | 419.7032 | 416.8759 | 413.8037
2702.5979 | 752.6912 | 420.2159 | 418.8152 | 414.7587
2703.6135 | 753.4527 | 420.9128 | 418.6491 | 414.6793
2704.5979 | 751.2238 | 421.443 | 419.1849 | 414.8812
2705.5979 | 748.7411 | 421.9779 | 419.2311 | 414.881
2706.5979 | 746.266 | 422.2871 | 419.6097 | 415.3432
2707.5979 | 745.6238 | 423.032 | 419.9221 | 415.2551
2708.5979 | 745.2619 | 423.315 | 419.6773 | 415.658
2709.5979 | 742.3295 | 423.2112 | 419.5631 | 416.0285
2710.5979 | 741.9138 | 423.3281 | 419.3981 | 416.3496
2711.5979 | 741.8202 | 423.6107 | 419.4365 | 417.0889
2712.5979 | 743.4658 | 423.8252 | 420.4353 | 416.7402
2713.5979 | 744.1725 | 423.7367 | 420.8872 | 416.3249
2714.5979 | 741.2832 | 423.4998 | 421.2021 | 416.2788
2715.5979 | 738.0586 | 422.8929 | 420.947 | 415.2418
2716.5979 | 737.8174 | 422.3909 | 420.2019 | 414.5158
2717.5979 | 736.4186 | 422.1563 | 419.7149 | 414.1638
2718.6135 | 735.8765 | 421.6751 | 419.3793 | 414.474
2719.5979 | 733.6847 | 421.4532 | 418.9077 | 414.7774
2720.5979 | 733.1153 | 421.1474 | 418.5703 | 414.744
2721.5979 | 730.9619 | 421.0424 | 418.2308 | 415.1784
2722.5979 | 729.6806 | 421.2434 | 418.153 | 415.0216
2723.5979 | 727.075 | 421.6664 | 418.4097 | 415.141
2724.5979 | 726.364 | 421.9904 | 418.1364 | 415.244
2725.5979 | 725.2308 | 422.9875 | 418.5859 | 415.231
2726.5979 | 726.2551 | 423.1751 | 418.2994 | 415.4311
2727.5979 | 727.6312 | 423.4378 | 418.2433 | 415.42
2728.5979 | 728.4636 | 423.8425 | 418.3469 | 416.0316
2729.5979 | 727.9598 | 424.045 | 418.4313 | 416.2935
2730.5979 | 726.0315 | 424.2378 | 418.3112 | 416.1595
2731.5979 | 725.0405 | 425.0271 | 418.8126 | 415.5824
2732.5979 | 725.8062 | 425.2759 | 419.4214 | 415.6958
2733.6135 | 728.0594 | 425.6921 | 419.9109 | 416.6981
2734.5979 | 729.8419 | 425.685 | 420.2584 | 416.7457
2735.5979 | 733.6814 | 426.3322 | 420.9145 | 417.7184
2736.5979 | 736.5675 | 426.4391 | 421.9735 | 418.808
2737.5979 | 739.4429 | 426.7964 | 422.2222 | 419.556
2738.5979 | 741.2651 | 427.0209 | 422.2701 | 419.685
2739.5979 | 742.6608 | 427.0808 | 422.2524 | 420.4491
2740.5979 | 744.1486 | 427.4614 | 422.4734 | 420.9014
2741.5979 | 744.2305 | 427.853 | 422.6863 | 421.1543
2742.5979 | 744.034 | 428.0701 | 422.3757 | 421.5926
2743.5979 | 743.8748 | 428.6917 | 423.1166 | 421.7127
2744.5979 | 747.8415 | 428.7841 | 423.5573 | 422.2264
2745.5979 | 750.0256 | 428.8185 | 423.6936 | 422.6381
2746.5979 | 751.5633 | 428.4665 | 423.8463 | 423.4101
2747.5979 | 752.0591 | 428.446 | 424.1403 | 423.6254
2748.5979 | 753.6736 | 428.882 | 424.959 | 424.2493
2749.5979 | 754.6554 | 429.2364 | 425.4807 | 424.9815
2750.5979 | 758.022 | 429.4827 | 427.2746 | 424.9499
2751.5979 | 759.8555 | 429.6257 | 426.9439 | 424.4172
2752.5979 | 761.5526 | 429.7349 | 426.8877 | 424.2324
2753.5979 | 763.671 | 429.2582 | 427.0872 | 424.3485
2754.5979 | 760.7933 | 428.5987 | 427.0041 | 424.6662
2755.5979 | 757.0857 | 428.4467 | 426.6287 | 424.2142
2756.5979 | 753.3494 | 428.3368 | 426.6279 | 423.8637
2757.5979 | 751.3344 | 427.8168 | 426.1931 | 423.5072
2758.5979 | 749.667 | 428.0747 | 426.1349 | 422.719
2759.5979 | 747.1267 | 428.5244 | 425.6057 | 422.0004
2760.5979 | 745.5781 | 428.8502 | 425.3754 | 422.3875
2761.5979 | 745.0736 | 429.22 | 425.7007 | 422.2565
2762.5979 | 745.3358 | 429.8669 | 425.7289 | 422.0436
2763.5979 | 744.2674 | 430.0761 | 425.9351 | 422.1308
2764.5979 | 742.8942 | 430.3405 | 425.7186 | 422.8568
2765.5979 | 739.0705 | 430.2729 | 425.7933 | 423.0127
2766.5979 | 737.5751 | 430.8659 | 426.1581 | 422.7177
2767.5979 | 736.9291 | 431.1587 | 426.492 | 422.7882
2768.5979 | 735.6492 | 431.4106 | 426.3951 | 422.7015
2769.5979 | 735.2315 | 431.633 | 426.4513 | 423.5886
2770.5979 | 734.0046 | 432.3083 | 426.6591 | 423.5805
2771.5979 | 731.5455 | 433.1118 | 427.5974 | 424.2368
2772.5979 | 731.4663 | 434.035 | 429.5662 | 424.9236
2773.5979 | 734.1859 | 434.8204 | 430.0138 | 424.7314
2774.5979 | 734.9117 | 434.464 | 430.2076 | 424.4086
2775.5979 | 733.5983 | 433.9833 | 430.3718 | 424.4774
2776.5979 | 734.7618 | 434.0271 | 430.0529 | 424.1628
2777.5979 | 733.5129 | 434.1972 | 429.6202 | 423.8131
2778.5979 | 733.7103 | 434.5934 | 429.6889 | 424.6788
2779.5979 | 734.4765 | 434.8604 | 429.4576 | 425.486
2780.5979 | 733.8217 | 435.8721 | 430.901 | 426.1095
2781.5979 | 735.3452 | 436.5578 | 430.9239 | 427.2003
2782.5979 | 739.2732 | 436.5246 | 431.0076 | 427.9183
2783.5979 | 741.4472 | 436.3597 | 431.1771 | 428.2051
2784.5979 | 741.9138 | 436.3316 | 431.2131 | 429.4423
2785.5979 | 741.2734 | 437.3492 | 431.4328 | 429.2605
2786.5979 | 740.3284 | 438.2339 | 432.8886 | 428.8759
2787.5979 | 737.8737 | 438.9636 | 432.612 | 428.705
2788.5979 | 736.5902 | 439.5858 | 433.157 | 428.6085
2789.5979 | 739.1108 | 440.0121 | 433.2794 | 428.777
2790.5979 | 742.0686 | 440.5596 | 434.3816 | 429.1734
2791.5979 | 745.5851 | 441.0404 | 434.7939 | 430.3448
2792.5979 | 746.0999 | 441.0562 | 434.814 | 431.3176
2793.5979 | 747.0852 | 441.9463 | 435.3416 | 431.4207
2794.5979 | 750.4015 | 443.2732 | 435.9043 | 431.4484
2795.5979 | 752.4553 | 443.3876 | 435.8508 | 432.1548
2796.5979 | 754.6173 | 442.869 | 436.0464 | 432.5087
2797.5979 | 755.7735 | 442.5355 | 436.0435 | 432.7656
2798.5979 | 755.6173 | 441.9994 | 435.8337 | 432.8363
2799.5979 | 756.2326 | 441.8466 | 436.0762 | 433.08
2800.5979 | 757.4076 | 442.5555 | 436.8169 | 433.282
2801.5979 | 759.1832 | 443.6844 | 437.3675 | 433.4869
2802.5979 | 760.4641 | 443.5286 | 437.6451 | 434.0081
2803.5979 | 763.1335 | 443.5495 | 437.7049 | 434.4263
2804.5979 | 767.0004 | 443.329 | 437.4926 | 434.5806
2805.5979 | 769.6237 | 443.0612 | 437.7824 | 434.7843
2806.5979 | 769.6926 | 442.6591 | 438.1846 | 434.9221
2807.5979 | 768.3419 | 442.2491 | 438.6119 | 434.92
2808.5979 | 768.17 | 441.7662 | 438.1641 | 435.6207
2809.5979 | 767.925 | 441.3878 | 438.4854 | 434.7943
2810.5979 | 767.7105 | 441.3177 | 438.2112 | 435.1394
2811.5979 | 766.6618 | 441.1138 | 437.6965 | 434.7264
2812.5979 | 766.2406 | 440.9701 | 437.493 | 434.7964
2813.5979 | 764.731 | 440.7688 | 437.5345 | 435.1134
2814.5979 | 763.2403 | 440.4645 | 437.3831 | 435.23
2815.5979 | 761.8165 | 441.0196 | 437.9759 | 435.499
2816.5979 | 760.9813 | 441.2483 | 438.3382 | 435.3142
2817.5979 | 761.4531 | 441.368 | 438.2346 | 435.0265
2818.5979 | 761.3341 | 441.0248 | 437.8652 | 435.423
2819.5979 | 760.7009 | 441.0781 | 438.5591 | 436.2864
2820.5979 | 760.5423 | 440.6305 | 438.408 | 436.5543
2821.5979 | 763.0534 | 440.6098 | 438.4253 | 436.575
2822.5979 | 764.9955 | 440.766 | 439.4162 | 437.135
2823.5979 | 762.6092 | 440.8029 | 439.0755 | 437.1371
2824.5979 | 759.5955 | 440.733 | 439.0938 | 437.5507
2825.5979 | 756.1712 | 440.3214 | 439.1042 | 437.7524
2826.5979 | 754.2344 | 440.3326 | 439.0938 | 437.4688
2827.5979 | 755.6602 | 440.595 | 439.0207 | 437.2076
2828.5979 | 757.5926 | 440.2073 | 439.137 | 437.3349
2829.5979 | 757.7229 | 440.5192 | 439.5657 | 437.5739
2830.5979 | 758.1974 | 440.4069 | 438.9711 | 438.0403
2831.5979 | 761.0885 | 439.9036 | 438.8297 | 438.6826
2832.5979 | 760.7787 | 439.7994 | 439.0039 | 439.063
2833.5979 | 758.6166 | 439.8837 | 439.4061 | 439.3694
2834.5979 | 757.2218 | 440.6401 | 439.6486 | 439.4453
2835.5979 | 757.4958 | 441.0381 | 439.5378 | 439.8306
2836.5979 | 755.7345 | 441.1259 | 439.1437 | 440.1936
2837.5979 | 753.9806 | 441.0135 | 438.7844 | 440.1493
2838.5979 | 752.4046 | 440.6644 | 439.2964 | 439.5689
2839.5979 | 749.8526 | 440.4796 | 439.1167 | 440.4285
2840.5979 | 746.6616 | 439.9099 | 438.9611 | 440.3597
2841.5979 | 744.6569 | 439.1884 | 438.498 | 439.6241
2842.5979 | 744.121 | 438.7665 | 438.2061 | 439.4846
2843.5979 | 746.0362 | 439.1467 | 438.8829 | 439.999
2844.5979 | 749.8431 | 438.6564 | 439.1491 | 440.0451
2845.6135 | 750.5529 | 438.522 | 439.1422 | 440.709
2846.5979 | 752.2339 | 438.4874 | 439.4019 | 440.7449
2847.5979 | 756.0305 | 438.383 | 439.0865 | 441.7383
2848.5979 | 761.2116 | 439.0833 | 439.3486 | 441.6501
2849.5979 | 763.4704 | 439.3768 | 439.8978 | 441.3351
2850.5979 | 766.2831 | 439.7515 | 441.1415 | 442.6935
2851.5979 | 766.6982 | 439.7671 | 441.3914 | 442.7974
2852.5979 | 764.7867 | 439.6374 | 442.742 | 444.2053
2853.5979 | 761.196 | 440.2209 | 442.7816 | 444.314
2854.5979 | 757.8951 | 440.1519 | 442.8934 | 444.1145
2855.6135 | 755.9383 | 439.8951 | 442.6802 | 444.6407
2856.5979 | 754.3315 | 440.1947 | 442.4877 | 444.1607
2857.5979 | 752.4976 | 440.5293 | 442.025 | 443.8743
2858.5979 | 752.1751 | 440.5959 | 441.7906 | 443.1129
2859.5979 | 753.1274 | 440.552 | 441.7489 | 443.6377
2860.5979 | 755.8616 | 441.1308 | 441.7638 | 442.937
2861.5979 | 756.7056 | 440.8088 | 441.731 | 443.7344
2862.5979 | 756.598 | 440.5869 | 441.5163 | 444.1022
2863.5979 | 757.6319 | 440.4244 | 441.2267 | 443.9334
2864.5979 | 757.9658 | 440.4803 | 440.7218 | 444.0351
2865.5979 | 757.5206 | 439.964 | 440.3185 | 444.1982
2866.5979 | 754.6896 | 439.9646 | 440.2111 | 444.0326
2867.5979 | 751.1211 | 440.1194 | 439.8338 | 443.4733
2868.5979 | 749.7051 | 439.9438 | 439.6989 | 443.146
2869.5979 | 746.6835 | 440.0559 | 439.925 | 443.6231
2870.5979 | 742.9373 | 439.7966 | 440.0451 | 442.9237
2871.5979 | 739.1656 | 439.924 | 440.7328 | 442.7602
2872.5979 | 736.4958 | 440.3779 | 441.2615 | 443.1744
2873.5979 | 732.7619 | 440.2686 | 441.3054 | 443.705
2874.5979 | 729.5539 | 440.5226 | 441.0998 | 444.4935
2875.5979 | 728.0008 | 440.8486 | 440.9158 | 443.5349
2876.5979 | 727.332 | 441.0093 | 440.793 | 443.553
2877.5979 | 725.3797 | 441.1539 | 440.3153 | 442.9186
2878.5979 | 724.9721 | 441.5126 | 440.186 | 442.6591
2879.5979 | 724.8128 | 441.6374 | 440.2714 | 442.8876
2880.5979 | 723.441 | 441.648 | 440.3313 | 442.3115
2881.5979 | 721.7225 | 441.9014 | 440.0734 | 441.6171
2882.5979 | 720.2966 | 442.3151 | 440.1942 | 441.9047
2883.5979 | 718.7374 | 442.3735 | 440.3479 | 442.2467
2884.5979 | 718.1574 | 442.5045 | 440.6421 | 442.2104
2885.5979 | 718.1818 | 441.7819 | 440.3251 | 442.6791
2886.5979 | 717.7778 | 440.9956 | 439.8954 | 442.6606
2887.5979 | 719.0837 | 440.5334 | 439.828 | 442.2015
2888.5979 | 719.6505 | 440.1036 | 439.6837 | 441.7181
2889.5979 | 718.9231 | 439.9896 | 439.2123 | 441.0285
2890.5979 | 717.8637 | 439.1849 | 439.5763 | 440.9603
2891.5979 | 716.7942 | 438.6137 | 439.168 | 440.4714
2892.5979 | 717.3584 | 437.988 | 438.9951 | 440.3014
2893.5979 | 718.92 | 437.5983 | 438.911 | 440.3728
2894.5979 | 724.6856 | 437.986 | 439.1573 | 440.632
2895.6135 | 730.7983 | 438.221 | 439.318 | 441.0896
2896.5979 | 735.6614 | 438.8302 | 439.2803 | 441.4595
2897.5979 | 740.9734 | 438.7961 | 441.1197 | 442.9366
2898.5979 | 745.2399 | 439.0046 | 441.4047 | 443.3282
2899.5979 | 749.4026 | 439.1665 | 441.9092 | 444.4857
2900.5979 | 752.4539 | 439.8749 | 442.8254 | 445.2731
2901.5979 | 755.1096 | 440.2147 | 443.3219 | 445.8277
2902.5979 | 757.101 | 440.7814 | 444.6936 | 446.8197
2903.5979 | 756.0214 | 441.388 | 445.4319 | 446.5547
2904.5979 | 752.3043 | 442.1296 | 446.1121 | 446.6798
2905.5979 | 748.3607 | 442.8257 | 446.3139 | 447.3709
2906.5979 | 746.5122 | 443.36 | 445.956 | 446.7501
2907.5979 | 746.4906 | 443.1313 | 446.0308 | 446.9163
2908.5979 | 746.3369 | 443.0412 | 445.7105 | 446.8311
2909.5979 | 744.5364 | 443.0327 | 446.3223 | 446.2626
2910.5979 | 742.397 | 442.9978 | 446.2236 | 446.2607
2911.5979 | 739.1317 | 442.4515 | 445.4937 | 445.772
2912.5979 | 736.6506 | 442.3068 | 445.1323 | 445.7488
2913.5979 | 736.1817 | 442.2352 | 444.6473 | 445.6663
2914.5979 | 736.4197 | 442.1028 | 444.3168 | 446.51
2915.5979 | 736.4024 | 442.0984 | 444.0914 | 445.9138
2916.5979 | 735.3127 | 442.0871 | 443.679 | 446.2067
2917.5979 | 731.1288 | 441.7809 | 443.2656 | 446.2156
2918.5979 | 727.1079 | 441.5863 | 443.3649 | 446.0006
2919.5979 | 723.4789 | 441.1751 | 442.9751 | 445.9259
2920.5979 | 723.113 | 440.6103 | 442.774 | 445.778
2921.5979 | 721.7307 | 439.9412 | 442.2367 | 445.9526
2922.5979 | 720.895 | 440.086 | 442.0218 | 445.42
2923.5979 | 719.8238 | 440.0759 | 441.6287 | 445.5056
2924.5979 | 720.8243 | 439.7971 | 441.057 | 445.5045
2925.5979 | 720.5515 | 440.0829 | 441.004 | 444.9757
2926.5979 | 720.5346 | 439.8771 | 441.6212 | 445.1948
2927.5979 | 719.4471 | 439.8123 | 441.2968 | 444.6365
2928.5979 | 720.0065 | 440.2134 | 441.2199 | 444.4459
2929.5979 | 722.0579 | 441.1514 | 441.6519 | 444.8112
2930.5979 | 727.5522 | 441.2635 | 441.558 | 444.8013
2931.5979 | 733.3622 | 441.5684 | 441.6836 | 445.3188
2932.5979 | 734.1907 | 441.2898 | 442.0077 | 445.7281
2933.5979 | 732.3443 | 441.0383 | 441.9708 | 446.1075
2934.5979 | 731.8877 | 440.9429 | 442.1998 | 446.6754
2935.5979 | 731.1525 | 440.54 | 442.19 | 446.7946
2936.5979 | 731.3646 | 440.3025 | 441.9898 | 447.683
2937.5979 | 732.4982 | 440.3896 | 442.2474 | 446.9854
2938.5979 | 733.1852 | 440.3259 | 441.9775 | 446.3561
2939.5979 | 735.2138 | 440.5404 | 441.9413 | 446.485
2940.5979 | 735.5486 | 440.2053 | 441.6788 | 446.8232
2941.5979 | 736.3809 | 440.2789 | 441.7526 | 446.6744
2942.5979 | 737.7677 | 440.1416 | 441.8042 | 447.3247
2943.5979 | 740.3417 | 439.9235 | 441.8883 | 447.1453
2944.5979 | 741.0569 | 439.7437 | 442.284 | 446.7644
2945.5979 | 741.2805 | 439.9649 | 442.5723 | 446.0969
2946.5979 | 740.9918 | 439.7886 | 442.7218 | 445.8437
2947.5979 | 740.4244 | 439.3731 | 442.6635 | 445.8252
2948.5979 | 738.5336 | 439.2019 | 442.184 | 446.0445
2949.5979 | 734.6745 | 438.668 | 442.0211 | 445.7603
2950.5979 | 731.2535 | 439.202 | 442.3066 | 445.683
2951.5979 | 730.4845 | 438.916 | 442.0082 | 445.3682
2952.5979 | 729.4158 | 438.6803 | 441.979 | 445.4756
2953.5979 | 726.9826 | 438.4764 | 442.2889 | 445.4081
2954.5979 | 726.8223 | 438.2582 | 442.1211 | 445.1326
2955.5979 | 726.5697 | 438.2454 | 441.9432 | 445.6638
2956.5979 | 726.6663 | 438.0371 | 441.6761 | 445.8983
2957.5979 | 726.8125 | 438.0159 | 441.8326 | 445.1579
2958.5979 | 727.2586 | 438.3053 | 442.2128 | 445.3408
2959.5979 | 727.1978 | 438.5844 | 441.7917 | 445.1957
2960.5979 | 727.4413 | 438.7934 | 442.04 | 445.2009
2961.5979 | 727.6944 | 438.465 | 441.521 | 444.8052
2962.5979 | 728.2516 | 438.5478 | 441.5199 | 444.6583
2963.5979 | 729.8285 | 438.8534 | 442.1062 | 444.7012
2964.5979 | 731.1695 | 438.7885 | 442.142 | 444.789
2965.5979 | 732.3235 | 438.5065 | 442.0769 | 444.347
2966.5979 | 734.8619 | 438.179 | 442.0749 | 444.2759
2967.5979 | 735.799 | 437.7992 | 441.8752 | 445.2657
2968.5979 | 735.5118 | 437.6619 | 441.8283 | 445.3648
2969.5979 | 734.7212 | 437.6776 | 441.4014 | 445.201
2970.5979 | 733.4979 | 438.3288 | 440.9719 | 445.1979
2971.5979 | 734.2557 | 438.7819 | 440.5957 | 445.1458
2972.5979 | 735.2405 | 438.9459 | 440.5418 | 444.861
2973.5979 | 734.8118 | 439.0959 | 440.3719 | 444.9505
2974.5979 | 734.8322 | 439.4208 | 440.1952 | 445.0372
2975.5979 | 734.4545 | 439.4411 | 440.2286 | 444.8924
2976.5979 | 734.0214 | 439.5441 | 440.2615 | 444.9593
2977.5979 | 732.411 | 439.9038 | 440.736 | 445.1034
2978.5979 | 731.3145 | 440.414 | 440.7847 | 445.5849
2979.5979 | 732.157 | 440.7762 | 441.0015 | 445.3284
2980.5979 | 734.0851 | 440.779 | 441.1886 | 446.0231
2981.5979 | 736.1302 | 440.531 | 441.036 | 446.5436
2982.5979 | 736.1752 | 440.3607 | 440.939 | 446.4691
2983.5979 | 735.2758 | 440.2834 | 440.841 | 446.341
2984.5979 | 732.6627 | 439.9919 | 440.4064 | 445.5934
2985.5979 | 730.7814 | 440.0316 | 440.2797 | 444.8741
2986.5979 | 730.9236 | 440.1587 | 440.2645 | 444.6908
2987.5979 | 731.1835 | 440.2058 | 440.1222 | 444.0781
2988.5979 | 729.629 | 439.8701 | 439.5734 | 443.2957
2989.5979 | 728.782 | 439.5367 | 439.923 | 443.3321
2990.5979 | 728.2777 | 439.1868 | 440.4394 | 443.7309
2991.5979 | 726.5593 | 439.3595 | 440.2978 | 443.6364
2992.5979 | 724.7011 | 439.2799 | 440.7834 | 444.287
2993.5979 | 722.7013 | 439.1134 | 441.0016 | 444.086
2994.5979 | 721.7229 | 439.0769 | 441.2218 | 444.506
2995.5979 | 721.2535 | 438.8711 | 441.2245 | 445.3795
2996.6135 | 723.3655 | 438.6755 | 441.0494 | 444.9287
2997.5979 | 724.9547 | 438.6049 | 440.7834 | 444.8161
2998.6135 | 726.7119 | 438.1715 | 440.2276 | 445.1048
2999.5979 | 729.9282 | 438.0393 | 440.6955 | 445.8733
3000.5979 | 735.503 | 438.1592 | 441.086 | 446.3528
3001.5979 | 738.5456 | 438.3222 | 441.1902 | 446.8016
3002.5979 | 741.6628 | 438.3169 | 440.8109 | 446.8922
3003.5979 | 745.3463 | 438.0523 | 441.4044 | 447.0886
3004.5979 | 746.027 | 438.105 | 441.5939 | 447.7714
3005.5979 | 747.0526 | 438.2858 | 441.604 | 447.8336
3006.5979 | 747.9703 | 438.1685 | 441.6781 | 447.1891
3007.5979 | 750.3257 | 438.4282 | 442.0343 | 447.7237
3008.5979 | 753.4833 | 438.2628 | 442.0484 | 447.793
3009.5979 | 756.7309 | 438.5219 | 441.913 | 447.5024
3010.5979 | 756.0817 | 438.3186 | 442.0676 | 447.6242
3011.5979 | 754.3737 | 438.1733 | 442.4249 | 448.1931
3012.5979 | 752.8462 | 437.9207 | 442.3543 | 448.0702
3013.5979 | 751.0629 | 437.9451 | 442.3479 | 448.7261
3014.5979 | 750.3875 | 437.7789 | 442.5169 | 448.4639
3015.5979 | 748.846 | 437.6763 | 442.2209 | 448.2899
3016.5979 | 747.0199 | 437.6065 | 442.5005 | 447.668
3017.5979 | 746.3302 | 437.7623 | 442.7132 | 447.8947
3018.5979 | 747.1193 | 437.6877 | 443.344 | 447.9718
3019.5979 | 746.1686 | 437.7697 | 443.4796 | 448.364
3020.5979 | 747.279 | 438.4368 | 443.5381 | 448.113
3021.5979 | 748.1635 | 438.6307 | 443.4014 | 447.8499
3022.5979 | 747.1936 | 438.4313 | 443.6959 | 448.0816
3023.5979 | 745.3432 | 438.1893 | 443.3332 | 447.6346
3024.5979 | 743.6005 | 437.9379 | 443.145 | 447.6929
3025.5979 | 739.6717 | 437.8953 | 442.9468 | 447.7821
3026.5979 | 737.1385 | 438.12 | 442.7866 | 447.1006
3027.5979 | 735.7937 | 437.643 | 442.4972 | 447.0771
3028.5979 | 735.7956 | 437.0339 | 442.2367 | 446.5839
3029.5979 | 735.2613 | 437.0024 | 442.0988 | 446.7447
3030.5979 | 734.8138 | 436.8186 | 441.9299 | 446.7732
3031.5979 | 734.4462 | 436.5838 | 441.5825 | 446.9308
3032.5979 | 731.8386 | 436.2175 | 441.3295 | 446.3631
3033.5979 | 730.5684 | 436.3484 | 441.0625 | 445.909
3034.5979 | 730.5412 | 436.0248 | 440.8156 | 445.6929
3035.5979 | 733.2327 | 435.6765 | 440.399 | 445.014
3036.5979 | 734.0713 | 435.6937 | 439.936 | 444.6747
3037.5979 | 735.8943 | 435.805 | 439.8471 | 444.7983
3038.5979 | 737.116 | 435.4776 | 439.8272 | 444.9657
3039.5979 | 736.6963 | 435.5452 | 439.8624 | 445.0288
3040.5979 | 735.9606 | 435.5162 | 439.4439 | 446.0022
3041.5979 | 734.5169 | 435.7499 | 439.5418 | 445.7232
3042.5979 | 732.5107 | 436.0053 | 439.5205 | 445.5676
3043.5979 | 730.0482 | 435.9855 | 439.4036 | 445.4911
3044.5979 | 728.1174 | 436.2051 | 440.1501 | 445.4304
3045.5979 | 727.4716 | 436.5106 | 440.0906 | 445.254
3046.5979 | 727.8068 | 436.4238 | 439.7272 | 444.7175
3047.5979 | 728.6069 | 436.2437 | 440.3605 | 444.8675
3048.5979 | 729.1378 | 436.1343 | 440.4199 | 444.8781
3049.5979 | 729.8364 | 436.0795 | 440.4988 | 444.833
3050.5979 | 729.1294 | 436.3026 | 440.7779 | 445.2422
3051.5979 | 726.6418 | 435.9932 | 440.8795 | 445.7242
3052.5979 | 724.0475 | 435.8191 | 440.4903 | 445.2107
3053.5979 | 721.8775 | 436.1142 | 440.5465 | 444.8481
3054.5979 | 721.2401 | 436.8627 | 440.9808 | 444.7977
3055.5979 | 722.2564 | 436.9251 | 441.1447 | 444.5749
3056.5979 | 724.2492 | 436.5388 | 441.1812 | 444.8062
3057.5979 | 724.7491 | 436.1217 | 440.7777 | 445.5128
3058.5979 | 725.4893 | 435.8206 | 440.6765 | 445.6852
3059.5979 | 725.3112 | 436.4192 | 440.7868 | 445.7838
3060.5979 | 724.6312 | 436.2125 | 440.7199 | 445.6662
3061.5979 | 725.027 | 436.028 | 440.4064 | 444.9498
3062.5979 | 725.7812 | 436.1122 | 440.284 | 444.7223
3063.5979 | 727.7255 | 436.1707 | 440.7678 | 444.1915
3064.5979 | 728.1479 | 435.9401 | 440.5041 | 443.989
3065.5979 | 728.72 | 435.7337 | 440.0468 | 443.8739
3066.5979 | 726.3192 | 435.4288 | 439.6398 | 443.8774
3067.5979 | 724.967 | 435.1655 | 440.5537 | 443.6859
3068.5979 | 724.8575 | 435.2761 | 440.69 | 443.5843
3069.5979 | 727.501 | 435.8489 | 440.919 | 443.4891
3070.5979 | 728.8953 | 435.7829 | 441.0616 | 443.9355
3071.5979 | 729.2083 | 435.6029 | 440.9805 | 444.1139
3072.5979 | 729.2533 | 435.2972 | 440.5006 | 444.2606
3073.5979 | 730.1423 | 435.1919 | 440.264 | 443.9369
3074.5979 | 728.7274 | 434.892 | 439.873 | 443.4363
3075.5979 | 726.9924 | 435.0172 | 439.5843 | 443.3522
3076.5979 | 726.4448 | 434.9737 | 439.1906 | 443.9687
3077.5979 | 724.1437 | 435.4742 | 439.1428 | 443.4062
3078.5979 | 725.0225 | 435.6792 | 438.9658 | 443.2112
3079.5979 | 722.7849 | 435.3512 | 438.9331 | 442.9361
3080.5979 | 717.4706 | 435.2711 | 438.9625 | 442.9515
3081.5979 | 714.0493 | 435.2656 | 438.9412 | 442.5516
3082.5979 | 714.4607 | 435.6134 | 439.1336 | 442.9458
3083.5979 | 716.2956 | 435.6594 | 439.2531 | 443.1503
3084.5979 | 720.4508 | 435.6439 | 439.1817 | 443.1054
3085.5979 | 722.0456 | 435.4366 | 439.1841 | 443.4821
3086.5979 | 723.0286 | 435.0675 | 438.828 | 443.465
3087.5979 | 726.0445 | 434.7692 | 438.9311 | 443.6355
3088.5979 | 726.3974 | 434.8859 | 438.8734 | 443.4967
3089.5979 | 726.4694 | 434.8721 | 438.6807 | 443.2171
3090.5979 | 726.709 | 434.9553 | 438.43 | 442.9686
3091.5979 | 727.6271 | 434.9495 | 437.9667 | 443.1198
3092.5979 | 728.7657 | 434.7576 | 437.6607 | 442.8521
3093.5979 | 729.8498 | 434.4443 | 437.7677 | 442.9236
3094.5979 | 730.4586 | 434.4381 | 437.8781 | 442.9066
3095.5979 | 730.7293 | 434.3595 | 437.9211 | 442.9264
3096.5979 | 730.3188 | 434.3351 | 437.8949 | 443.3939
3097.5979 | 730.7954 | 434.296 | 437.9061 | 443.8833
3098.5979 | 731.1395 | 434.3693 | 438.0431 | 444.0307
3099.5979 | 731.0026 | 434.0384 | 438.1302 | 444.3097
3100.5979 | 730.1658 | 433.8677 | 437.8807 | 444.0953
3101.5979 | 730.1355 | 433.862 | 438.0968 | 444.0653
3102.5979 | 730.5484 | 434.37 | 438.0583 | 443.7211
3103.5979 | 729.6153 | 434.26 | 438.0895 | 443.4935
3104.5979 | 727.3271 | 434.0802 | 437.8285 | 443.3841
3105.5979 | 725.0817 | 433.753 | 437.7433 | 443.5264
3106.5979 | 721.7669 | 433.9135 | 437.8382 | 442.9126
3107.5979 | 721.9024 | 433.8262 | 437.3543 | 442.4697
3108.5979 | 722.0777 | 433.4491 | 436.9566 | 442.2897
3109.5979 | 720.7896 | 433.0994 | 436.6467 | 441.735
3110.5979 | 718.5369 | 432.8581 | 436.7093 | 441.6842
3111.5979 | 716.9836 | 432.7741 | 436.7509 | 441.7941
3112.5979 | 714.9617 | 433.169 | 436.7048 | 441.4898
3113.5979 | 717.2985 | 433.0861 | 436.5434 | 441.5156
3114.5979 | 719.9507 | 432.9876 | 436.3897 | 441.1212
3115.5979 | 719.7648 | 432.9204 | 436.1885 | 441.2531
3116.5979 | 718.9048 | 432.6817 | 435.9918 | 440.9959
3117.5979 | 718.6568 | 432.5866 | 435.7947 | 441.1771
3118.5979 | 719.4686 | 432.6907 | 435.7839 | 440.9265
3119.5979 | 719.0778 | 432.9467 | 435.6168 | 441.2307
3120.5979 | 716.1083 | 432.8729 | 435.5549 | 441.253
3121.5979 | 712.6563 | 433.0677 | 435.5313 | 440.8817
3122.5979 | 709.2639 | 433.6076 | 435.8114 | 440.3719
3123.5979 | 707.0382 | 434.0426 | 435.8076 | 440.2955
3124.5979 | 707.2006 | 434.2499 | 435.9645 | 440.1894
3125.5979 | 706.9611 | 434.3668 | 436.1373 | 440.1993
3126.5979 | 706.748 | 434.772 | 436.6299 | 440.2022
3127.5979 | 707.7674 | 434.7858 | 436.643 | 440.1789
3128.5979 | 708.6147 | 434.6775 | 436.7359 | 440.0502
3129.5979 | 706.9243 | 434.9437 | 437.1517 | 440.4121
3130.6135 | 704.9127 | 435.1433 | 437.5315 | 440.6071
3131.5979 | 704.8213 | 435.8518 | 438.8202 | 441.0555
3132.5979 | 706.7157 | 436.0771 | 438.9955 | 440.9235
3133.5979 | 707.545 | 435.9477 | 438.8264 | 440.9199
3134.5979 | 709.0897 | 436.0749 | 438.6177 | 440.6554
3135.6135 | 711.2271 | 435.744 | 438.3147 | 440.4918
3136.6135 | 711.6396 | 436.354 | 438.9883 | 440.841
3137.6135 | 710.5403 | 436.8434 | 439.1845 | 441.1884
3138.5979 | 709.0138 | 436.5539 | 439.1494 | 440.8735
3139.5979 | 708.0587 | 436.2501 | 438.6331 | 440.5585
3140.5979 | 709.7375 | 436.4019 | 437.8863 | 440.4341
3141.5979 | 712.1524 | 435.9477 | 437.7973 | 440.3968
3142.5979 | 712.4406 | 436.2444 | 437.8261 | 440.0212
3143.5979 | 711.0653 | 435.9724 | 437.9161 | 440.1454
3144.5979 | 710.6022 | 435.6258 | 437.6813 | 440.3533
3145.5979 | 711.9389 | 436.112 | 437.6545 | 440.1994
3146.5979 | 710.7979 | 435.9619 | 437.6439 | 440.2932
3147.5979 | 709.688 | 435.5016 | 437.246 | 440.4383
3148.5979 | 708.5189 | 435.0437 | 436.8276 | 440.1473
3149.5979 | 709.421 | 434.8621 | 436.5283 | 439.8672
3150.5979 | 710.3787 | 434.5044 | 436.3812 | 439.9306
3151.5979 | 710.0514 | 434.0493 | 435.9381 | 439.6041
3152.5979 | 711.5202 | 433.7113 | 435.5905 | 439.3857
3153.5979 | 711.8261 | 433.6281 | 435.5083 | 439.7096
3154.5979 | 712.7607 | 433.7445 | 435.445 | 439.4585
3155.5979 | 715.7314 | 433.9894 | 435.4784 | 439.0313
3156.5979 | 715.26 | 434.063 | 435.4356 | 438.9181
3157.5979 | 713.3402 | 433.8521 | 435.9372 | 438.66
3158.5979 | 711.3173 | 433.5315 | 435.6094 | 439.1347
3159.5979 | 710.4288 | 433.0458 | 435.9395 | 438.7498
3160.5979 | 709.2413 | 433.1061 | 435.7465 | 438.7022
3161.5979 | 709.3077 | 433.0217 | 435.8907 | 438.5603
3162.5979 | 709.0677 | 432.9615 | 435.6624 | 438.0842
3163.5979 | 707.7941 | 432.6018 | 435.1349 | 438.3549
3164.5979 | 706.9633 | 432.3135 | 434.5864 | 437.908
3165.5979 | 706.6574 | 431.9397 | 434.1587 | 437.4904
3166.5979 | 705.8752 | 431.5048 | 433.8091 | 438.0611
3167.5979 | 704.8214 | 431.5169 | 433.9262 | 437.9662
3168.5979 | 703.3543 | 431.5751 | 433.9171 | 437.5255
3169.5979 | 703.2263 | 431.5097 | 433.7614 | 437.2201
3170.5979 | 701.8222 | 431.5043 | 433.382 | 436.8276
3171.5979 | 699.517 | 431.4986 | 433.1591 | 436.613
3172.5979 | 697.4286 | 431.6318 | 433.2548 | 436.867
3173.5979 | 697.1131 | 431.4441 | 433.4391 | 436.929
3174.5979 | 696.9004 | 431.2686 | 433.7583 | 437.123
3175.5979 | 695.6202 | 431.3403 | 433.9419 | 437.3841
3176.5979 | 694.4218 | 431.4163 | 434.079 | 437.8299
3177.5979 | 694.7967 | 431.3437 | 434.1238 | 437.6191
3178.5979 | 694.1429 | 431.1735 | 433.8111 | 436.9698
3179.5979 | 693.8167 | 431.361 | 433.7054 | 436.3779
3180.5979 | 694.1822 | 431.8955 | 433.7168 | 435.9785
3181.5979 | 693.8685 | 431.7529 | 433.8002 | 435.6386
3182.5979 | 692.9351 | 431.3269 | 433.5962 | 435.6684
3183.5979 | 692.1915 | 430.8477 | 433.284 | 435.4595
3184.5979 | 691.837 | 430.6103 | 432.9414 | 435.3208
3185.5979 | 692.3619 | 430.4979 | 432.7184 | 435.2766
3186.5979 | 692.1022 | 430.4367 | 432.5001 | 435.2226
3187.5979 | 691.7561 | 430.2366 | 432.1635 | 435.1635
3188.5979 | 691.7444 | 430.245 | 431.8108 | 434.9293
3189.5979 | 690.9837 | 430.656 | 431.5987 | 434.7387
3190.5979 | 690.627 | 430.5782 | 431.5279 | 435.5048
3191.5979 | 689.601 | 430.7496 | 431.6473 | 435.2299
3192.5979 | 689.6998 | 430.8359 | 431.7529 | 435.0726
3193.5979 | 689.5829 | 430.6688 | 431.6209 | 434.7998
3194.5979 | 689.9136 | 430.5637 | 431.6091 | 435.2949
3195.5979 | 691.6812 | 430.4029 | 431.4394 | 434.9423
3196.5979 | 692.4375 | 430.2947 | 431.3168 | 434.7116
3197.5979 | 691.8692 | 430.1701 | 431.2008 | 434.3293
3198.5979 | 690.8108 | 430.1703 | 431.0703 | 433.8656
3199.5979 | 690.4016 | 430.0075 | 431.046 | 433.266
3200.5979 | 689.1072 | 429.7193 | 430.7835 | 432.8161
3201.5979 | 687.7534 | 429.61 | 430.5002 | 432.4523
3202.5979 | 685.9342 | 429.7561 | 430.2304 | 432.0662
3203.5979 | 684.3059 | 429.7786 | 429.8139 | 431.7929
3204.5979 | 683.8522 | 429.6922 | 429.5449 | 431.433
3205.5979 | 683.529 | 430.082 | 429.177 | 431.7423
3206.5979 | 676.5108 | 453.5657 | 436.2035 | 433.5603
3207.5979 | 682.1384 | 429.126 | 428.5666 | 431.1195
3208.5979 | 680.0571 | 428.8866 | 428.3845 | 430.6549
3209.5979 | 677.6305 | 428.63 | 428.1694 | 430.6215
3210.5979 | 676.0105 | 428.4863 | 427.9678 | 430.3227
3211.5979 | 677.3286 | 428.5778 | 428.3682 | 430.5299
3212.5979 | 677.3799 | 428.7376 | 428.5325 | 430.3599
3213.5979 | 677.7849 | 429.2849 | 428.7014 | 430.2645
3214.5979 | 678.5895 | 429.2649 | 428.6704 | 430.0834
3215.5979 | 678.6221 | 429.4474 | 428.7592 | 430.0167
3216.5979 | 677.6774 | 429.4123 | 429.0171 | 429.9008
3217.5979 | 676.6007 | 429.2468 | 429.063 | 429.8369
3218.5979 | 675.1906 | 429.2847 | 429.2607 | 429.6562
3219.5979 | 675.4498 | 429.1303 | 429.1921 | 430.0153
3220.5979 | 674.3905 | 429.1556 | 429.041 | 429.8027
3221.5979 | 673.625 | 429.4081 | 428.7738 | 429.4758
3222.5979 | 673.4018 | 429.5121 | 428.69 | 429.4345
3223.5979 | 673.517 | 429.3972 | 428.5841 | 429.4584
3224.5979 | 673.0954 | 429.079 | 428.4985 | 429.4448
3225.5979 | 673.6627 | 428.9989 | 428.1142 | 429.4575
3226.5979 | 673.7985 | 428.9917 | 428.2866 | 429.8237
3227.5979 | 673.7636 | 429.3009 | 428.5512 | 430.1242
3228.5979 | 674.0616 | 429.4121 | 428.336 | 430.043
3229.5979 | 674.3075 | 429.4698 | 428.2514 | 429.5412
3230.5979 | 673.7148 | 429.3717 | 428.1735 | 429.5965
3231.5979 | 674.2057 | 429.9347 | 428.277 | 429.7655
3232.5979 | 674.1479 | 430.2644 | 428.2835 | 429.7173
3233.5979 | 675.0069 | 430.0098 | 428.3937 | 429.5247
3234.5979 | 675.2614 | 429.6869 | 428.0993 | 429.1704
3235.5979 | 675.5482 | 429.3071 | 427.9838 | 428.7499
3236.5979 | 675.006 | 429.1524 | 427.652 | 428.5524
3237.5979 | 673.798 | 429.0906 | 427.3086 | 428.0766
3238.5979 | 673.2454 | 429.2794 | 427.5248 | 427.7611
3239.5979 | 672.484 | 429.1431 | 427.5417 | 427.6139
3240.5979 | 673.2683 | 429.2943 | 427.9753 | 427.5071
3241.5979 | 673.2895 | 429.5216 | 428.208 | 427.6396
3242.5979 | 673.5244 | 429.6315 | 428.6263 | 427.4322
3243.5979 | 672.8938 | 429.2913 | 428.9818 | 427.6395
3244.5979 | 670.8177 | 429.2803 | 428.9611 | 427.4496
3245.5979 | 668.4482 | 429.4393 | 428.8253 | 427.3207
3246.5979 | 666.6495 | 430.1729 | 428.7269 | 427.4687
3247.5979 | 666.0025 | 430.2203 | 428.8551 | 427.9437
3248.5979 | 665.5014 | 429.9663 | 429.0008 | 428.2378
3249.5979 | 665.9405 | 429.6281 | 429.1587 | 428.0681
3250.5979 | 665.8324 | 429.4925 | 429.1154 | 427.906
3251.5979 | 665.8078 | 429.3429 | 429.0482 | 427.7238
3252.5979 | 664.5636 | 429.1143 | 428.895 | 427.4541
3253.5979 | 663.3245 | 428.9267 | 428.7932 | 427.5053
3254.5979 | 663.7112 | 428.9699 | 428.7367 | 427.4224
3255.5979 | 663.7148 | 429.1794 | 428.9448 | 427.3293
3256.5979 | 663.2013 | 429.0409 | 429.0328 | 427.073
3257.5979 | 663.5587 | 428.791 | 428.6495 | 426.6944
3258.5979 | 663.2583 | 428.4866 | 428.2751 | 426.0974
3259.5979 | 663.4795 | 428.1145 | 427.8542 | 425.4711
3260.5979 | 663.0714 | 427.8097 | 427.5395 | 424.8097
3261.5979 | 662.4571 | 427.265 | 427.1409 | 424.33
3262.5979 | 662.3668 | 426.8979 | 426.755 | 423.8927
3263.5979 | 662.774 | 426.5989 | 426.8525 | 423.5262
3264.5979 | 662.3445 | 426.1941 | 426.4752 | 423.0096
3265.5979 | 661.3899 | 425.8562 | 426.0254 | 422.5212
3266.5979 | 662.7091 | 425.592 | 425.731 | 422.6727
3267.5979 | 663.5657 | 425.2987 | 425.4303 | 422.6523
3268.5979 | 664.5632 | 425.112 | 425.4611 | 422.609
3269.5979 | 665.6374 | 425.1649 | 425.376 | 422.5201
3270.5979 | 664.4417 | 425.1026 | 425.4163 | 422.6356
3271.5979 | 663.0415 | 425.1465 | 425.0081 | 422.6361
3272.5979 | 661.9068 | 424.8912 | 424.5455 | 422.44
3273.5979 | 662.415 | 424.569 | 424.3724 | 422.474
3274.5979 | 662.8871 | 424.4825 | 423.941 | 422.518
3275.5979 | 662.996 | 424.7969 | 423.6279 | 422.2379
3276.5979 | 662.6582 | 425.2938 | 423.6216 | 422.164
3277.5979 | 661.5664 | 425.2694 | 423.6807 | 422.0143
3278.5979 | 659.7981 | 425.0988 | 423.4027 | 421.8179
3279.5979 | 659.0886 | 424.8226 | 423.0657 | 421.6352
3280.5979 | 656.8 | 424.2573 | 422.5959 | 421.6231
3281.5979 | 655.684 | 424.0213 | 422.1171 | 421.3161
3282.5979 | 654.5627 | 423.7137 | 421.6743 | 420.9754
3283.5979 | 654.1317 | 423.2561 | 421.2954 | 420.8704
3284.5979 | 656.1236 | 422.7041 | 420.8003 | 420.7909
3285.5979 | 657.4236 | 422.3236 | 420.4685 | 420.6314
3286.5979 | 655.1764 | 422.1033 | 420.1739 | 420.5678
3287.5979 | 654.9042 | 421.7506 | 419.9059 | 420.2941
3288.5979 | 655.0434 | 421.3933 | 419.6841 | 420.5223
3289.5979 | 655.2644 | 421.1425 | 419.5455 | 420.456
3290.5979 | 656.1637 | 421.0574 | 419.2905 | 420.6081
3291.5979 | 655.8429 | 420.8425 | 419.1658 | 420.3833
3292.5979 | 655.3503 | 420.8876 | 419.3112 | 420.7529
3293.5979 | 654.6515 | 421.0403 | 419.6495 | 420.656
3294.5979 | 652.9062 | 420.9495 | 419.6724 | 420.6179
3295.5979 | 652.6805 | 420.5592 | 419.2836 | 420.5847
3296.5979 | 652.1957 | 420.2734 | 418.7856 | 420.0575
3297.5979 | 651.6705 | 420.0968 | 418.4243 | 419.6132
3298.5979 | 650.1205 | 420.0048 | 418.2606 | 419.1814
3299.5979 | 648.2158 | 420.0256 | 418.498 | 419.0625
3300.5979 | 648.3611 | 420.1409 | 418.4595 | 419.0221
3301.5979 | 650.5632 | 420.5388 | 418.4978 | 418.8236
3302.5979 | 650.8139 | 420.3693 | 418.3826 | 418.5123
3303.5979 | 650.8179 | 420.1537 | 418.1978 | 418.2148
3304.5979 | 649.97 | 420.1745 | 418.1553 | 418.3392
3305.5979 | 648.1021 | 419.9062 | 417.934 | 417.9964
3306.5979 | 647.2117 | 419.6961 | 417.7858 | 417.9054
3307.5979 | 647.2598 | 419.5731 | 417.3809 | 417.8141
3308.5979 | 648.1934 | 419.064 | 416.907 | 417.8433
3309.5979 | 650.0063 | 418.9641 | 416.7268 | 417.6753
3310.5979 | 651.4809 | 418.7901 | 416.5208 | 417.5792
3311.5979 | 652.6979 | 418.7423 | 416.3598 | 417.4283
3312.5979 | 653.8572 | 418.6499 | 416.1771 | 417.2538
3313.5979 | 652.9643 | 418.3523 | 416.0425 | 417.0196
3314.5979 | 651.7869 | 418.389 | 415.8744 | 416.8348
3315.5979 | 651.4804 | 418.8645 | 416.0436 | 416.7671
3316.5979 | 651.6142 | 419.1734 | 415.9316 | 416.6342
3317.5979 | 652.2888 | 419.0771 | 415.8016 | 416.4493
3318.5979 | 652.359 | 418.9962 | 415.5149 | 416.124
3319.5979 | 652.7213 | 418.922 | 415.7221 | 416.0274
3320.5979 | 653.8856 | 418.8562 | 416.0732 | 415.9897
3321.5979 | 654.382 | 418.5066 | 415.9934 | 415.8105
3322.5979 | 654.7079 | 418.3972 | 416.0444 | 415.5975
3323.6135 | 654.2244 | 418.5879 | 415.8178 | 415.4942
3324.5979 | 654.1959 | 418.6081 | 415.7501 | 415.3967
3325.5979 | 653.4352 | 418.5785 | 415.4178 | 415.113
3326.5979 | 653.0388 | 418.3674 | 415.4757 | 414.7506
3327.5979 | 652.7481 | 418.1925 | 415.3422 | 414.6529
3328.5979 | 652.6973 | 418.1686 | 415.0675 | 414.4014
3329.5979 | 653.5292 | 417.9962 | 414.7575 | 414.018
3330.5979 | 653.6051 | 417.8403 | 414.3417 | 413.7641
3331.5979 | 654.4944 | 417.7496 | 414.1659 | 413.6474
3332.5979 | 654.1363 | 417.8502 | 414.2266 | 413.6581
3333.5979 | 653.0711 | 417.942 | 414.2383 | 413.608
3334.5979 | 651.7561 | 418.0431 | 414.2822 | 413.5831
3335.5979 | 651.9073 | 418.0566 | 414.1965 | 413.2506
3336.5979 | 650.8699 | 417.9825 | 414.2725 | 412.9651
3337.5979 | 649.95 | 418.1952 | 414.7243 | 413.1504
3338.5979 | 649.7261 | 418.2441 | 415.0357 | 413.1643
3339.5979 | 651.3181 | 418.1195 | 414.9264 | 412.9756
3340.5979 | 653.4244 | 418.0408 | 415.1724 | 412.7447
3341.5979 | 654.5545 | 417.7631 | 415.1115 | 412.5272
3342.5979 | 654.4737 | 417.5092 | 414.875 | 412.3215
3343.5979 | 654.098 | 417.4858 | 414.8115 | 412.1683
3344.5979 | 653.2536 | 417.4095 | 414.7583 | 412.1684
3345.5979 | 653.0551 | 417.5 | 414.7939 | 412.1253
3346.5979 | 652.2622 | 417.5297 | 414.8757 | 412.0186
3347.5979 | 652.1953 | 417.655 | 414.9341 | 411.8738
3348.5979 | 653.9978 | 417.626 | 414.8645 | 411.6085
3349.5979 | 654.5556 | 417.4148 | 414.5847 | 411.3564
3350.5979 | 654.3668 | 417.086 | 414.2346 | 411.1001
3351.5979 | 654.869 | 417.0442 | 413.8492 | 410.8326
3352.5979 | 655.1353 | 416.8265 | 413.5203 | 410.6868
3353.5979 | 655.5406 | 416.5442 | 413.4797 | 410.7288
3354.5979 | 655.5362 | 416.1758 | 413.5314 | 410.7304
3355.5979 | 653.9225 | 415.8619 | 413.2777 | 410.4675
3356.5979 | 652.5575 | 415.5189 | 412.9544 | 410.4174
3357.5979 | 651.7205 | 415.1435 | 412.8019 | 410.3519
3358.5979 | 650.3476 | 414.8147 | 412.6109 | 410.1962
3359.5979 | 648.2871 | 414.5284 | 412.2357 | 410.0615
3360.5979 | 646.9147 | 414.4558 | 412.1016 | 409.8579
3361.5979 | 646.3585 | 414.3683 | 412.0293 | 410.0884
3362.5979 | 644.787 | 414.0996 | 411.768 | 409.7827
3363.5979 | 642.4002 | 413.7901 | 411.6135 | 409.6936
3364.5979 | 641.2565 | 413.5325 | 411.2288 | 409.5523
3365.5979 | 641.8493 | 413.1361 | 410.9011 | 409.4841
3366.5979 | 641.7304 | 412.7753 | 410.6545 | 409.297
3367.5979 | 641.8086 | 412.6391 | 410.511 | 409.1949
3368.5979 | 641.6791 | 412.4347 | 410.4252 | 409.16
3369.5979 | 641.4985 | 412.1353 | 410.0792 | 409.1106
3370.5979 | 641.3751 | 411.84 | 409.7861 | 408.9374
3371.5979 | 640.3705 | 411.5575 | 409.3887 | 408.6067
3372.5979 | 640.1028 | 411.5246 | 409.1625 | 408.6087
3373.5979 | 639.9862 | 411.5077 | 408.9317 | 408.647
3374.5979 | 639.5308 | 411.3736 | 409.1409 | 408.5452
3375.5979 | 638.654 | 411.0984 | 409.1647 | 408.7518
3376.5979 | 638.463 | 410.8751 | 409.0716 | 408.8227
3377.5979 | 638.192 | 410.9323 | 409.0847 | 408.7386
3378.5979 | 638.0606 | 411.3247 | 409.2573 | 408.8228
3379.5979 | 638.8609 | 411.3279 | 409.2752 | 408.7982
3380.5979 | 638.9866 | 411.1538 | 409.1581 | 408.6991
3381.5979 | 639.213 | 411.0337 | 409.0774 | 408.4345
3382.5979 | 639.8926 | 410.9307 | 408.9553 | 408.305
3383.5979 | 639.8603 | 410.7859 | 408.7946 | 408.0341
3384.5979 | 640.9914 | 410.8479 | 408.7258 | 407.7716
3385.5979 | 641.8556 | 410.7301 | 408.5384 | 407.4927
3386.5979 | 642.4049 | 410.554 | 408.3093 | 407.2461
3387.5979 | 642.0282 | 410.2905 | 407.8798 | 407.218
3388.5979 | 641.007 | 410.3482 | 407.5546 | 406.934
3389.5979 | 639.4633 | 410.2307 | 407.4798 | 406.8245
3390.5979 | 637.9891 | 409.9768 | 407.2553 | 406.8196
3391.5979 | 637.3629 | 409.7617 | 407.3504 | 406.6746
3392.5979 | 636.8178 | 409.5791 | 407.3541 | 406.2994
3393.5979 | 637.1626 | 409.4714 | 407.2881 | 406.2363
3394.5979 | 638.6994 | 409.5692 | 407.1526 | 406.2417
3395.5979 | 639.0395 | 409.4082 | 407.1899 | 406.3774
3396.5979 | 638.802 | 409.2442 | 407.0074 | 406.2544
3397.5979 | 637.4136 | 409.0972 | 406.7973 | 406.1257
3398.5979 | 636.2014 | 408.9346 | 406.6938 | 406.0039
3399.5979 | 635.1826 | 408.7148 | 406.45 | 405.8954
3400.5979 | 635.8522 | 408.7214 | 406.1474 | 406.198
3401.5979 | 637.443 | 408.6102 | 405.9825 | 405.9292
3402.5979 | 637.3359 | 408.4159 | 405.7912 | 405.8085
3403.5979 | 637.4729 | 408.249 | 405.6646 | 405.6873
3404.5979 | 638.423 | 408.0359 | 405.6981 | 405.6759
3405.5979 | 640.0424 | 407.6499 | 405.5482 | 405.445
3406.5979 | 640.0747 | 407.3255 | 405.2507 | 405.1398
3407.5979 | 639.1349 | 407.2364 | 404.8252 | 404.958
3408.5979 | 639.5983 | 407.318 | 404.6334 | 404.8976
3409.5979 | 639.296 | 407.1698 | 404.4951 | 404.7719
3410.5979 | 638.5837 | 406.9223 | 404.2164 | 404.611
3411.5979 | 638.3599 | 406.5023 | 403.8556 | 404.4994
3412.5979 | 637.7413 | 406.1815 | 403.6844 | 404.2864
3413.5979 | 637.116 | 406.0876 | 403.5136 | 404.1277
3414.5979 | 637.2098 | 406.1073 | 403.4626 | 404.0002
3415.5979 | 637.5889 | 406.0607 | 403.3686 | 403.8219
3416.5979 | 637.2059 | 406.034 | 403.288 | 403.7105
3417.5979 | 637.3574 | 405.9138 | 403.5112 | 403.9731
3418.5979 | 637.6793 | 405.9481 | 403.7141 | 403.8642
3419.5979 | 637.6297 | 406.2696 | 403.9642 | 403.8367
3420.5979 | 636.971 | 406.2977 | 403.8367 | 403.6096
3421.5979 | 636.149 | 406.4152 | 403.7488 | 403.337
3422.5979 | 635.1829 | 406.4127 | 403.3398 | 403.1782
3423.5979 | 634.544 | 406.3791 | 403.0452 | 403.0339
3424.5979 | 634.1694 | 406.3635 | 403.0022 | 402.7542
3425.5979 | 633.9727 | 406.3175 | 403.0882 | 402.9016
3426.5979 | 633.531 | 406.186 | 403.0894 | 402.9329
3427.5979 | 633.9816 | 406.0425 | 402.9849 | 402.7727
3428.5979 | 634.5601 | 405.9509 | 403.3107 | 402.6003
3429.5979 | 635.1845 | 405.8394 | 403.348 | 402.4917
3430.5979 | 635.6048 | 405.7405 | 403.3683 | 402.2301
3431.5979 | 635.8179 | 405.6579 | 403.2281 | 401.9962
3432.5979 | 635.7878 | 405.614 | 403.0743 | 401.7911
3433.5979 | 635.557 | 405.5066 | 402.9631 | 401.5459
3434.5979 | 635.6876 | 405.423 | 402.7659 | 401.3375
3435.5979 | 635.0559 | 405.2764 | 402.4769 | 401.0431
3436.5979 | 634.8128 | 405.1637 | 402.49 | 400.7859
3437.5979 | 634.6899 | 404.8986 | 402.2487 | 400.5189
3438.5979 | 633.9496 | 404.6966 | 401.8506 | 400.3518
3439.5979 | 633.214 | 404.4922 | 401.5433 | 400.1141
3440.5979 | 632.6882 | 404.4283 | 401.4362 | 399.8797
3441.5979 | 633.0499 | 404.1891 | 401.254 | 400.097
3442.5979 | 633.6384 | 403.9178 | 401.0893 | 399.9148
3443.5979 | 633.0915 | 403.6202 | 400.7683 | 399.5445
3444.5979 | 633.2036 | 403.4278 | 400.5415 | 399.4351
3445.5979 | 632.8451 | 403.2927 | 400.2805 | 399.19
3446.5979 | 632.1673 | 403.1717 | 399.9854 | 398.9463
3447.5979 | 632.309 | 403.0572 | 399.9766 | 398.7596
3448.5979 | 633.3752 | 403.1756 | 400.2606 | 398.7384
3449.5979 | 634.8204 | 403.1394 | 400.2208 | 398.652
3450.5979 | 635.8632 | 403.1892 | 400.1356 | 398.5002
3451.5979 | 636.2402 | 403.0715 | 399.8501 | 398.3137
3452.5979 | 636.5856 | 402.9665 | 399.6179 | 398.0455
3453.5979 | 636.591 | 402.8352 | 399.7784 | 398.0022
3454.5979 | 636.3816 | 402.6982 | 399.6662 | 397.8893
3455.5979 | 635.6025 | 402.6029 | 399.4744 | 397.5257
3456.5979 | 633.9848 | 402.6102 | 399.4869 | 397.29
3457.5979 | 633.9758 | 402.5539 | 399.5307 | 397.1289
3458.5979 | 633.9958 | 402.432 | 399.3833 | 397.0527
3459.5979 | 632.2258 | 402.5368 | 399.3577 | 396.9839
3460.5979 | 629.3509 | 402.3731 | 399.0687 | 396.8943
3461.5979 | 626.3542 | 402.2861 | 398.691 | 396.7362
3462.5979 | 623.7875 | 401.9581 | 398.4867 | 396.4206
3463.5979 | 621.2551 | 401.559 | 398.1531 | 396.0905
3464.5979 | 619.062 | 401.0326 | 397.6863 | 395.793
3465.5979 | 616.4462 | 400.4463 | 397.4225 | 395.3729
3466.5979 | 614.0328 | 399.817 | 397.0761 | 394.8408
3467.5979 | 611.3997 | 399.0865 | 396.3586 | 394.4085
3468.5979 | 609.5273 | 398.4618 | 395.8708 | 394.1471
3469.5979 | 607.8248 | 397.9016 | 395.2695 | 393.5817
3470.5979 | 605.8783 | 397.4223 | 394.6148 | 393.1067
3471.5979 | 604.2692 | 396.7467 | 394.0365 | 392.7179
3472.5979 | 603.1882 | 396.1751 | 393.3753 | 392.2211
3473.5979 | 601.9939 | 395.8162 | 393.2296 | 391.99
3474.5979 | 600.4194 | 395.3722 | 392.8109 | 391.9853
3475.5979 | 598.5824 | 394.846 | 392.3617 | 391.4982
3476.5979 | 596.6592 | 394.3589 | 392.0099 | 391.0071
3477.5979 | 595.713 | 393.8533 | 391.5971 | 390.5109
3478.5979 | 594.6595 | 393.4062 | 391.034 | 390.0684
3479.5979 | 593.37 | 392.9219 | 390.6507 | 389.6475
3480.5979 | 592.3391 | 392.3493 | 390.2322 | 389.268
3481.5979 | 591.685 | 391.7534 | 389.7976 | 388.8517
3482.5979 | 591.0498 | 391.3789 | 389.2033 | 388.6407
3483.5979 | 590.0965 | 390.9327 | 388.9708 | 388.4634
3484.5979 | 589.5654 | 390.6354 | 388.6151 | 388.3998
3485.5979 | 588.9903 | 390.3695 | 388.2676 | 388.6436
3486.5979 | 588.7476 | 390.1905 | 388.0767 | 388.7723
3487.5979 | 588.4972 | 389.947 | 387.8816 | 388.8457
3488.5979 | 586.9955 | 389.6521 | 387.7603 | 388.7255
3489.5979 | 587.0401 | 389.2898 | 387.5479 | 388.6999
3490.5979 | 587.042 | 389.0059 | 387.2693 | 388.5116
3491.5979 | 586.8021 | 388.6881 | 386.9406 | 388.3429
3492.5979 | 586.5257 | 388.4984 | 386.6164 | 388.0931
3493.5979 | 586.0124 | 388.2573 | 386.1021 | 387.8025
3494.5979 | 585.0653 | 388.0696 | 385.8115 | 387.7336
3495.5979 | 584.5132 | 387.7614 | 385.7519 | 387.8287
3496.5979 | 583.9926 | 387.4839 | 385.9883 | 387.8017
3497.5979 | 583.4946 | 387.1713 | 385.7456 | 387.7641
3498.5979 | 583.2216 | 387.0847 | 385.7706 | 387.8136
3499.5979 | 582.6939 | 387.1126 | 385.8814 | 387.7346
3500.5979 | 582.0478 | 387.1482 | 385.9817 | 387.583
3501.5979 | 581.9983 | 387.1638 | 386.0096 | 387.4605
3502.5979 | 581.9992 | 386.9259 | 385.9693 | 387.4337
3503.5979 | 581.8332 | 386.5792 | 385.5603 | 386.9757
3504.5979 | 581.2883 | 386.1989 | 385.2721 | 386.5507
3505.5979 | 580.7333 | 385.763 | 384.7019 | 386.184
3506.5979 | 580.1187 | 385.3232 | 384.5369 | 385.8972
3507.5979 | 579.8084 | 385.0652 | 384.4879 | 385.7088
3508.5979 | 578.8833 | 384.6936 | 384.6612 | 385.5121
3509.5979 | 577.7935 | 384.3341 | 384.6206 | 385.1896
3510.5979 | 576.7594 | 383.9339 | 384.2003 | 385.0231
3511.5979 | 576.331 | 383.6751 | 383.8323 | 384.7298
3512.5979 | 576.4442 | 383.3815 | 383.5586 | 384.4146
3513.5979 | 577.1497 | 383.1422 | 382.9868 | 384.1606
3514.5979 | 577.1974 | 382.9576 | 382.5587 | 384.0634
3515.5979 | 577.8922 | 382.8347 | 382.1215 | 384.1029
3516.5979 | 579.5687 | 382.5872 | 381.8547 | 384.0432
3517.5979 | 581.704 | 382.3184 | 381.7559 | 384.1014
3518.5979 | 584.3072 | 382.2576 | 381.7995 | 384.1049
3519.5979 | 586.3852 | 382.271 | 381.7594 | 383.9954
3520.5979 | 587.4653 | 382.3185 | 381.7798 | 383.9118
3521.5979 | 589.3832 | 382.4444 | 381.874 | 384.1893
3522.5979 | 591.2661 | 382.5355 | 382.012 | 384.3758
3523.5979 | 593.0954 | 382.71 | 382.0467 | 384.3645
3524.5979 | 594.0712 | 382.9766 | 382.4844 | 384.4955
3525.5979 | 594.7797 | 383.2329 | 383.5797 | 384.6269
3526.5979 | 596.2712 | 383.6205 | 383.7843 | 385.0368
3527.5979 | 598.0228 | 383.8589 | 383.8362 | 385.0586
3528.5979 | 598.828 | 384.2158 | 383.8997 | 384.9816
3529.5979 | 599.4537 | 384.5129 | 383.9483 | 385.0702
3530.5979 | 599.5842 | 384.9631 | 384.0011 | 385.1684
3531.5979 | 601.1311 | 385.1599 | 383.943 | 385.1342
3532.5979 | 602.7635 | 385.5386 | 383.908 | 385.2106
3533.5979 | 603.6933 | 385.4575 | 383.7048 | 385.0765
3534.5979 | 604.3775 | 385.3149 | 383.822 | 384.9238
3535.5979 | 604.7371 | 385.2024 | 383.7684 | 384.9423
3536.5979 | 602.8378 | 385.1584 | 383.7241 | 384.9232
3537.5979 | 602.3016 | 384.9993 | 383.7673 | 385.366
3538.5979 | 602.2768 | 385.0441 | 383.9058 | 385.4714
3539.5979 | 602.3321 | 385.0499 | 384.0763 | 385.4027
3540.5979 | 602.4317 | 384.857 | 384.043 | 385.3531
3541.5979 | 602.5313 | 384.7294 | 383.9238 | 385.2558
3542.5979 | 602.6697 | 384.6334 | 383.9041 | 385.1036
3543.5979 | 603.6322 | 384.4886 | 384.3987 | 385.2078
3544.5979 | 605.981 | 384.3579 | 384.3894 | 385.222
3545.5979 | 607.4684 | 384.2832 | 384.2875 | 385.2098
3546.5979 | 608.2559 | 384.1582 | 384.2214 | 385.0476
3547.6135 | 608.3634 | 383.9991 | 384.1305 | 384.9216
3548.5979 | 609.4144 | 383.8155 | 383.9352 | 384.8103
3549.5979 | 610.1323 | 383.6122 | 383.711 | 384.6824
3550.5979 | 609.7046 | 383.4725 | 383.3511 | 384.6283
3551.5979 | 610.7709 | 383.4263 | 383.0737 | 384.4312
3552.5979 | 611.1583 | 383.4773 | 382.9615 | 384.1812
3553.5979 | 610.9997 | 383.4247 | 382.9769 | 384.5875
3554.5979 | 610.7063 | 383.3927 | 382.9865 | 384.5146
3555.5979 | 610.4895 | 383.4731 | 382.999 | 384.4025
3556.5979 | 611.0295 | 383.363 | 383.1037 | 384.5074
3557.5979 | 610.9747 | 383.4147 | 383.2523 | 384.8228
3558.5979 | 610.5168 | 383.2003 | 383.2051 | 384.7989
3559.5979 | 609.5553 | 383.1001 | 383.08 | 384.7203
3560.5979 | 609.8789 | 383.0619 | 382.8258 | 384.7633
3561.5979 | 610.3377 | 382.8783 | 382.6756 | 384.5929
3562.5979 | 609.9441 | 382.6407 | 382.4932 | 384.2467
3563.5979 | 609.3602 | 382.5118 | 382.4534 | 384.0555
3564.5979 | 608.2757 | 382.5187 | 382.2237 | 383.996
3565.5979 | 606.2983 | 382.6161 | 381.9562 | 383.7293
3566.5979 | 605.4976 | 382.6339 | 381.8919 | 383.7543
3567.5979 | 604.7967 | 382.7036 | 381.8425 | 383.6138
3568.5979 | 604.9364 | 382.6464 | 382.1437 | 384.0671
3569.5979 | 604.2568 | 382.5411 | 382.2723 | 384.3368
3570.5979 | 604.8578 | 382.4762 | 382.4323 | 384.1237
3571.5979 | 604.4241 | 382.3517 | 382.8054 | 384.3598
3572.5979 | 604.8052 | 382.3005 | 382.7548 | 384.3896
3573.5979 | 604.3725 | 382.4588 | 382.8728 | 384.4185
3574.6135 | 603.8664 | 382.5546 | 383.3472 | 384.8008
3575.5979 | 605.1353 | 382.5944 | 383.382 | 384.7956
3576.5979 | 605.4896 | 382.6589 | 383.238 | 384.4457
3577.5979 | 604.9124 | 382.5236 | 382.9729 | 384.4095
3578.5979 | 603.7191 | 382.5681 | 382.8311 | 384.4041
3579.5979 | 602.5897 | 382.7904 | 382.8015 | 384.151
3580.5979 | 602.1122 | 382.9351 | 382.8993 | 383.8587
3581.5979 | 601.9407 | 382.8303 | 383.1873 | 383.9607
3582.5979 | 602.1987 | 382.7222 | 382.9264 | 383.9343
3583.5979 | 602.7052 | 382.584 | 382.6112 | 383.675
3584.5979 | 603.574 | 382.4768 | 382.3285 | 383.3582
3585.5979 | 604.5662 | 382.3184 | 382.0234 | 383.0961
3586.5979 | 604.2842 | 382.0754 | 381.7929 | 382.982
3587.5979 | 604.3843 | 381.8718 | 381.5775 | 382.8003
3588.5979 | 604.6421 | 381.7349 | 381.4852 | 382.6369
3589.5979 | 604.5559 | 381.6578 | 381.381 | 382.6101
3590.5979 | 604.2905 | 381.4981 | 381.3402 | 382.6748
3591.5979 | 604.2082 | 381.5074 | 381.3617 | 382.5893
3592.5979 | 604.0321 | 381.5372 | 381.2912 | 382.6069
3593.5979 | 604.5254 | 381.5291 | 381.3469 | 382.5688
3594.5979 | 604.0441 | 381.4662 | 381.3386 | 382.8653
3595.5979 | 603.4728 | 381.5733 | 381.254 | 382.9262
3596.5979 | 602.594 | 381.3866 | 381.3338 | 383.1481
3597.5979 | 601.1069 | 381.2274 | 381.8464 | 383.1577
3598.5979 | 599.6689 | 381.0639 | 381.6535 | 383.2358
3599.5979 | 598.5097 | 381.001 | 381.3959 | 382.9233
3600.5979 | 597.2894 | 380.9117 | 381.1533 | 382.6342
3601.5979 | 596.6641 | 380.8008 | 380.913 | 382.6042
3602.5979 | 596.1424 | 380.6953 | 380.7271 | 382.4276
3603.5979 | 594.7708 | 380.6365 | 380.4661 | 382.0693
3604.6135 | 593.9747 | 380.6839 | 380.2597 | 381.6784
3605.5979 | 594.0488 | 380.5926 | 380.0753 | 381.4567
3606.5979 | 594.3432 | 380.6342 | 379.8474 | 381.5364
3607.5979 | 594.052 | 380.6099 | 379.7723 | 381.2807
3608.5979 | 593.7964 | 380.8263 | 380.1574 | 381.1501
3609.5979 | 593.2036 | 380.8883 | 379.8996 | 381.1493
3610.5979 | 593.1231 | 380.8441 | 379.9375 | 381.019
3611.5979 | 593.5359 | 380.7991 | 379.8235 | 381.007
3612.5979 | 594.4572 | 380.8398 | 379.7317 | 380.7545
3613.5979 | 595.5541 | 380.817 | 379.5466 | 380.4247
3614.5979 | 596.0058 | 380.6774 | 379.3394 | 380.2333
3615.5979 | 595.9798 | 380.6318 | 379.3842 | 379.9925
3616.5979 | 596.052 | 380.6266 | 379.2845 | 379.7542
3617.5979 | 597.2607 | 380.6473 | 379.3621 | 379.5065
3618.5979 | 598.0261 | 380.5424 | 379.1949 | 379.548
3619.5979 | 598.9988 | 380.4713 | 379.1485 | 379.3177
3620.5979 | 599.1686 | 380.6458 | 379.1042 | 379.203
3621.5979 | 598.6674 | 380.7052 | 379.0488 | 379.5685
3622.5979 | 598.2779 | 380.7438 | 378.9752 | 379.5264
3623.5979 | 598.0599 | 380.6265 | 378.7909 | 379.4276
3624.5979 | 598.4538 | 380.5631 | 378.6083 | 379.3812
3625.5979 | 598.0755 | 380.3594 | 378.4206 | 379.2257
3626.5979 | 598.9974 | 380.3756 | 378.2679 | 379.1491
3627.5979 | 599.8493 | 380.2368 | 378.1912 | 379.1388
3628.5979 | 601.035 | 380.15 | 378.0772 | 379.0946
3629.5979 | 601.2221 | 380.0534 | 378.0266 | 378.9171
3630.5979 | 601.1742 | 379.8944 | 378.211 | 378.9044
3631.5979 | 600.6146 | 379.7746 | 378.1304 | 379.1204
3632.5979 | 599.9385 | 379.5744 | 377.9465 | 378.9578
3633.5979 | 599.9624 | 379.4173 | 377.7524 | 378.7568
3634.5979 | 600.5118 | 379.3122 | 377.4876 | 378.596
3635.5979 | 601.5414 | 379.1207 | 377.2686 | 378.297
3636.5979 | 602.9575 | 378.862 | 377.0892 | 378.0243
3637.5979 | 603.9717 | 378.7331 | 377.0346 | 377.9491
3638.5979 | 603.5721 | 378.6529 | 376.9714 | 378.0047
3639.5979 | 602.6343 | 378.5937 | 376.705 | 377.7952
3640.5979 | 601.6029 | 378.6821 | 376.4673 | 377.5522
3641.5979 | 601.2195 | 378.6866 | 376.2927 | 377.3954
3642.5979 | 600.0152 | 378.6007 | 376.2903 | 377.3229
3643.5979 | 598.7511 | 378.6481 | 376.4274 | 377.4958
3644.5979 | 597.9534 | 378.6227 | 376.3914 | 377.434
3645.5979 | 598.8787 | 378.5832 | 376.5274 | 377.3204
3646.5979 | 599.5991 | 378.4894 | 376.4889 | 377.0822
3647.5979 | 600.0298 | 378.3981 | 376.5624 | 376.8888
3648.5979 | 600.4235 | 378.2394 | 376.4817 | 376.9004
3649.5979 | 600.0823 | 378.0313 | 376.2805 | 376.7335
3650.5979 | 600.0758 | 377.828 | 375.9563 | 376.7673
3651.5979 | 599.8924 | 377.8554 | 375.5737 | 376.7827
3652.5979 | 598.7159 | 377.8172 | 375.3235 | 376.7899
3653.5979 | 597.3077 | 377.6011 | 375.259 | 376.7896
3654.5979 | 596.4373 | 377.3971 | 374.7549 | 376.9396
3655.5979 | 595.8538 | 377.4027 | 375.4182 | 376.9649
3656.5979 | 595.9348 | 377.2464 | 375.6573 | 377.755
3657.6135 | 596.417 | 377.0812 | 375.469 | 377.6331
3658.5979 | 596.5077 | 377.08 | 375.2795 | 377.87
3659.5979 | 596.9246 | 377.1557 | 375.1879 | 377.8942
3660.5979 | 596.3856 | 377.0792 | 375.064 | 377.7596
3661.5979 | 596.1389 | 376.9445 | 374.9569 | 377.5169
3662.5979 | 596.1088 | 376.8276 | 374.825 | 377.2644
3663.5979 | 595.9549 | 376.6706 | 374.6065 | 377.3906
3664.5979 | 595.8769 | 376.4738 | 374.4106 | 377.1711
3665.5979 | 595.0197 | 376.36 | 374.313 | 377.1385
3666.5979 | 593.4626 | 376.2192 | 374.2872 | 376.8693
3667.5979 | 592.9055 | 376.0807 | 374.1432 | 376.9496
3668.5979 | 592.7316 | 376.1428 | 374.1425 | 376.9167
3669.5979 | 592.7964 | 376.1487 | 374.0334 | 376.6427
3670.5979 | 592.6426 | 376.112 | 373.9574 | 376.3398
3671.5979 | 591.9272 | 376.0477 | 373.6275 | 375.9972
3672.5979 | 591.209 | 375.9519 | 373.4246 | 375.7585
3673.5979 | 590.489 | 375.8792 | 373.2668 | 375.4596
3674.5979 | 590.4292 | 375.7561 | 373.1675 | 375.3028
3675.5979 | 590.3646 | 375.6651 | 373.1354 | 375.1412
3676.5979 | 590.4058 | 375.5651 | 372.997 | 374.8846
3677.5979 | 590.9135 | 375.437 | 372.829 | 374.6353
3678.5979 | 590.6549 | 375.4239 | 372.8919 | 374.5784
3679.5979 | 590.2131 | 375.3783 | 373.0135 | 374.9355
3680.5979 | 589.873 | 375.3287 | 373.0478 | 374.9506
3681.5979 | 589.8313 | 375.2112 | 373.0838 | 375.1382
3682.5979 | 590.4827 | 375.0353 | 372.9512 | 375.1362
3683.5979 | 591.2753 | 374.8258 | 372.6977 | 374.9321
3684.5979 | 591.3458 | 374.6228 | 372.5032 | 374.6194
3685.6135 | 590.8554 | 374.5025 | 372.3105 | 374.4615
3686.5979 | 590.3408 | 374.4008 | 372.1765 | 374.4688
3687.5979 | 589.8462 | 374.2796 | 372.0818 | 374.277
3688.5979 | 589.4343 | 374.0872 | 371.8953 | 374.3882
3689.5979 | 589.858 | 374.0119 | 371.8188 | 374.2992
3690.5979 | 590.8172 | 373.8993 | 371.6953 | 374.4734
3691.5979 | 591.509 | 373.8829 | 371.5117 | 374.2484
3692.5979 | 592.7573 | 373.8637 | 371.5559 | 374.1119
3693.5979 | 592.6728 | 373.7804 | 371.5296 | 374.1688
3694.6135 | 591.6347 | 373.8378 | 371.4788 | 373.9957
3695.5979 | 591.8764 | 373.844 | 371.644 | 373.9204
3696.5979 | 592.5188 | 373.8367 | 371.6356 | 373.9787
3697.5979 | 592.4471 | 373.7958 | 371.5421 | 373.7592
3698.5979 | 592.7375 | 373.6934 | 371.4231 | 373.5656
3699.5979 | 591.6816 | 373.5572 | 371.2793 | 373.6569
3700.5979 | 591.2227 | 373.5898 | 371.3999 | 373.8996
3701.5979 | 590.5071 | 373.7379 | 371.4787 | 373.8878
3702.5979 | 589.7029 | 373.6914 | 371.4521 | 373.9717
3703.5979 | 589.603 | 373.7059 | 371.6633 | 373.7997
3704.5979 | 590.5507 | 373.6486 | 371.5802 | 373.8693
3705.5979 | 591.5948 | 373.5009 | 371.5243 | 373.7113
3706.5979 | 592.5391 | 373.4072 | 371.4923 | 373.6219
3707.5979 | 593.3289 | 373.316 | 371.4329 | 373.518
3708.5979 | 594.0941 | 373.2229 | 371.3159 | 373.3488
3709.5979 | 594.8311 | 373.1535 | 371.4966 | 373.1414
3710.5979 | 594.2888 | 373.0803 | 371.4707 | 373.2254
3711.5979 | 593.3949 | 372.9847 | 371.4366 | 373.1416
3712.5979 | 593.9586 | 372.9267 | 371.429 | 373.1449
3713.5979 | 594.2506 | 372.7442 | 371.2293 | 372.9592
3714.5979 | 593.7027 | 372.6362 | 371.1137 | 373.0174
3715.5979 | 592.8795 | 372.5721 | 371.0898 | 373.0323
3716.5979 | 591.4441 | 372.4609 | 371.0893 | 373.0127
3717.5979 | 590.7619 | 372.4571 | 371.0929 | 372.9193
3718.5979 | 589.2814 | 372.4849 | 371.3128 | 373.0177
3719.5979 | 587.7449 | 372.3443 | 371.2886 | 373.4415
3720.5979 | 585.9972 | 372.5144 | 371.4792 | 373.6334
3721.5979 | 585.3187 | 372.5799 | 371.7293 | 373.8752
3722.5979 | 584.8517 | 372.6 | 371.7535 | 373.8025
3723.5979 | 584.9645 | 372.6252 | 371.928 | 374.0542
3724.5979 | 586.0433 | 372.9052 | 371.8321 | 374.0561
3725.5979 | 586.9354 | 372.762 | 371.6133 | 374.2929
3726.5979 | 587.9361 | 372.5878 | 371.6944 | 374.261
3727.5979 | 589.3848 | 372.4775 | 371.5738 | 374.0558
3728.5979 | 590.9154 | 372.3944 | 371.4972 | 374.2134
3729.5979 | 590.8217 | 372.3798 | 371.6163 | 374.6667
3730.5979 | 590.2198 | 372.5653 | 371.6462 | 374.6909
3731.5979 | 589.6781 | 372.632 | 371.6044 | 374.591
3732.5979 | 590.2322 | 372.5665 | 371.5918 | 374.6265
3733.5979 | 590.7286 | 372.2979 | 371.4736 | 374.8457
3734.5979 | 591.4481 | 372.0442 | 371.3996 | 374.8767
3735.5979 | 591.5741 | 371.8478 | 371.5084 | 374.6123
3736.5979 | 591.2648 | 371.7106 | 371.5429 | 374.7008
3737.5979 | 591.1148 | 371.6185 | 371.4257 | 374.9364
3738.5979 | 591.0327 | 371.5743 | 371.2839 | 374.6923
3739.5979 | 591.2559 | 371.5095 | 371.1086 | 374.5515
3740.5979 | 591.8414 | 371.3803 | 370.9905 | 374.3211
3741.5979 | 592.2796 | 371.1967 | 370.7497 | 374.2403
3742.5979 | 591.5251 | 371.3078 | 370.5814 | 373.9164
3743.5979 | 590.1385 | 371.3154 | 370.7588 | 374.2013
3744.5979 | 589.1534 | 371.2673 | 370.668 | 374.0985
3745.5979 | 587.6978 | 371.2386 | 370.7289 | 373.8946
3746.5979 | 586.4009 | 371.296 | 370.7364 | 373.9783
3747.5979 | 585.2822 | 371.3159 | 370.6653 | 373.9345
3748.5979 | 584.3981 | 371.2437 | 370.5802 | 373.7388
3749.5979 | 583.3286 | 371.0418 | 370.5962 | 373.4512
3750.5979 | 582.1065 | 370.9895 | 370.6967 | 373.289
3751.5979 | 580.964 | 370.8267 | 370.7866 | 373.1153
3752.5979 | 579.5021 | 370.811 | 370.6796 | 373.1654
3753.5979 | 579.4564 | 370.8183 | 370.6647 | 372.9051
3754.5979 | 580.0337 | 370.7204 | 370.6194 | 372.9813
3755.5979 | 580.0415 | 370.6439 | 370.3328 | 372.9461
3756.5979 | 580.2277 | 370.8131 | 370.3147 | 372.5461
3757.5979 | 579.9901 | 370.8864 | 370.0987 | 372.3241
3758.5979 | 579.8293 | 371.0118 | 370.0791 | 372.1738
3759.5979 | 579.4705 | 370.9011 | 369.9809 | 372.1623
3760.5979 | 578.9385 | 370.7331 | 369.8332 | 372.0133
3761.5979 | 578.6473 | 370.659 | 369.6073 | 371.8786
3762.5979 | 578.7746 | 370.4943 | 369.4172 | 371.8755
3763.5979 | 578.422 | 370.3728 | 369.2215 | 371.7302
3764.5979 | 577.7184 | 370.2169 | 369.219 | 371.4968
3765.5979 | 578.2084 | 370.2941 | 369.2978 | 371.382
3766.5979 | 580.1983 | 370.2417 | 368.9948 | 371.187
3767.5979 | 580.1932 | 370.0557 | 368.6396 | 370.7751
3768.5979 | 581.9513 | 370.0701 | 368.4602 | 370.4435
3769.5979 | 582.8414 | 370.0678 | 368.6519 | 370.423
3770.5979 | 583.5356 | 369.928 | 368.5153 | 370.5754
3771.5979 | 584.1937 | 369.7485 | 368.3838 | 370.4934
3772.5979 | 584.946 | 369.7055 | 368.0907 | 370.3142
3773.5979 | 586.4256 | 369.5241 | 367.9596 | 370.5003
3774.5979 | 587.5363 | 369.4099 | 367.8427 | 370.5706
3775.5979 | 588.0904 | 369.4097 | 367.78 | 370.4535
3776.5979 | 587.4392 | 369.6721 | 367.7497 | 370.4325
3777.5979 | 585.9436 | 369.6921 | 367.7619 | 370.4985
3778.5979 | 585.3535 | 369.6802 | 367.9235 | 370.7731
3779.5979 | 585.3353 | 369.4681 | 367.8881 | 370.8502
3780.5979 | 585.1911 | 369.1613 | 367.6163 | 370.5895
3781.5979 | 584.9139 | 368.8791 | 367.3304 | 370.3964
3782.5979 | 583.9321 | 368.7237 | 367.0837 | 370.2884
3783.5979 | 583.5422 | 368.7083 | 366.9425 | 370.096
3784.5979 | 583.1395 | 368.8478 | 367.1166 | 370.3585
3785.5979 | 583.1674 | 369.0778 | 367.18 | 370.7108
3786.5979 | 583.2941 | 369.1606 | 367.0423 | 370.6044
3787.5979 | 582.9077 | 369.1597 | 366.8597 | 370.5542
3788.5979 | 582.5294 | 369.0771 | 366.6059 | 370.2959
3789.5979 | 582.9 | 369.0214 | 366.336 | 370.0156
3790.5979 | 583.2086 | 368.9328 | 366.192 | 369.8469
3791.5979 | 582.8496 | 368.7821 | 365.9609 | 369.5531
3792.5979 | 582.5093 | 368.7462 | 365.9716 | 369.535
3793.5979 | 582.7583 | 368.9559 | 366.0491 | 369.8831
3794.5979 | 583.0216 | 368.8334 | 365.8989 | 369.7817
3795.5979 | 583.2712 | 368.6056 | 365.6578 | 369.4857
3796.5979 | 583.189 | 368.4294 | 365.4561 | 369.4147
3797.5979 | 583.8558 | 368.3539 | 365.2786 | 369.3253
3798.5979 | 583.9114 | 368.1937 | 365.1685 | 369.1385
3799.5979 | 583.0607 | 368.0149 | 364.8832 | 368.8112
3800.5979 | 582.2874 | 368.0321 | 364.8172 | 368.4555
3801.5979 | 581.479 | 368.0132 | 364.9037 | 368.4607
3802.5979 | 580.2052 | 367.8685 | 365.3469 | 368.473
3803.5979 | 579.7991 | 367.8669 | 365.4823 | 368.6686
3804.5979 | 578.9819 | 368.2218 | 365.714 | 368.7658
3805.5979 | 578.3694 | 368.4331 | 365.9858 | 368.9381
3806.5979 | 577.6481 | 368.4909 | 366.1374 | 369.1336
3807.5979 | 577.7614 | 368.7543 | 366.1855 | 369.1722
3808.5979 | 577.8712 | 368.7189 | 366.1588 | 369.385
3809.5979 | 577.9056 | 368.7098 | 366.3759 | 369.4917
3810.5979 | 578.6279 | 368.7149 | 366.4398 | 369.3308
3811.5979 | 578.8543 | 368.6513 | 366.2229 | 369.1809
3812.5979 | 579.4809 | 368.5457 | 366.215 | 369.234
3813.5979 | 580.2728 | 368.318 | 366.1872 | 369.3473
3814.5979 | 580.4553 | 368.1437 | 366.0523 | 369.345
3815.5979 | 580.7359 | 368.1093 | 366.2134 | 369.5606
3816.5979 | 581.1373 | 367.7986 | 366.2476 | 369.551
3817.5979 | 583.0578 | 367.5066 | 366.1127 | 369.3902
3818.5979 | 584.5651 | 367.2919 | 365.9659 | 369.4178
3819.5979 | 584.9709 | 367.1336 | 365.7555 | 369.1859
3820.5979 | 584.1416 | 366.9747 | 365.5637 | 368.9758
3821.5979 | 583.1951 | 366.9031 | 365.5252 | 368.9047
3822.5979 | 582.3899 | 366.9609 | 365.4429 | 368.9602
3823.5979 | 581.4752 | 366.9634 | 365.8194 | 368.7316
3824.5979 | 581.2025 | 367.0092 | 366.1134 | 369.0269
3825.5979 | 581.1509 | 366.9196 | 365.9432 | 368.9746
3826.5979 | 581.3227 | 366.6844 | 365.6483 | 368.6596
3827.5979 | 581.9964 | 366.4591 | 365.434 | 368.7093
3828.5979 | 583.4838 | 366.2922 | 365.2726 | 368.3719
3829.5979 | 584.0235 | 366.1198 | 365.0308 | 368.1688
3830.5979 | 583.3423 | 366.0273 | 364.9618 | 368.5875
3831.5979 | 582.8917 | 365.933 | 364.9606 | 368.2345
3832.5979 | 583.3883 | 366.0119 | 364.7971 | 368.0423
3833.5979 | 583.7995 | 365.9206 | 364.625 | 367.9482
3834.5979 | 583.9064 | 365.7172 | 364.4695 | 367.8472
3835.5979 | 582.6332 | 365.7054 | 364.4302 | 367.621
3836.5979 | 581.4542 | 365.8158 | 364.4745 | 367.6379
3837.5979 | 580.9447 | 365.7378 | 364.4069 | 367.34
3838.5979 | 580.6072 | 365.6131 | 364.4376 | 367.4381
3839.5979 | 580.9512 | 365.4214 | 364.3369 | 367.6384
3840.5979 | 581.1639 | 365.2163 | 364.2678 | 367.5586
3841.5979 | 581.6276 | 365.068 | 364.2592 | 367.6777
3842.5979 | 581.597 | 364.9568 | 363.9284 | 367.633
3843.5979 | 582.8842 | 364.8003 | 363.6582 | 367.412
3844.5979 | 584.5976 | 364.7382 | 363.8969 | 367.2827
3845.5979 | 585.1846 | 364.684 | 364.0655 | 367.2594
3846.5979 | 585.3706 | 364.5439 | 363.7516 | 367.008
3847.5979 | 584.9962 | 364.3553 | 363.4603 | 366.8875
3848.5979 | 584.6404 | 364.2139 | 363.3108 | 366.5996
3849.5979 | 583.345 | 364.0564 | 363.0942 | 366.2752
3850.5979 | 582.312 | 363.8366 | 362.8208 | 366.1433
3851.5979 | 581.264 | 363.6508 | 362.5576 | 366.1385
3852.5979 | 581.04 | 363.4866 | 362.2457 | 366.166
3853.5979 | 581.8746 | 363.3651 | 362.0258 | 365.7646
3854.5979 | 582.8779 | 363.3119 | 361.9013 | 365.6985
3855.5979 | 583.2886 | 363.3775 | 362.0618 | 365.5073
3856.5979 | 583.9211 | 363.5294 | 362.1486 | 365.3305
3857.5979 | 584.2351 | 363.7426 | 362.1794 | 365.4754
3858.5979 | 583.9664 | 363.7952 | 362.7632 | 365.6279
3859.5979 | 584.2286 | 364.2798 | 363.5172 | 365.7488
3860.5979 | 583.8897 | 364.427 | 363.5527 | 365.778
3861.5979 | 582.8516 | 364.4737 | 363.549 | 366.021
3862.5979 | 581.1213 | 364.5074 | 363.5345 | 366.1657
3863.5979 | 579.1251 | 364.616 | 363.5579 | 366.1146
3864.5979 | 577.9875 | 364.6312 | 363.5352 | 366.0413
3865.5979 | 576.9579 | 364.5011 | 363.4944 | 365.9327
3866.5979 | 576.0286 | 364.3341 | 363.9091 | 365.9938
3867.5979 | 574.6047 | 364.4478 | 363.7897 | 366.0575
3868.5979 | 573.9914 | 364.3196 | 363.5133 | 365.8725
3869.5979 | 574.4321 | 364.1948 | 363.6062 | 365.7885
3870.5979 | 574.2678 | 364.0138 | 363.437 | 366.0026
3871.5979 | 573.9655 | 363.8511 | 363.2434 | 365.8631
3872.5979 | 574.3114 | 363.6755 | 362.9865 | 365.6743
3873.5979 | 575.2417 | 363.5197 | 362.6521 | 365.3955
3874.5979 | 575.9995 | 363.4607 | 362.4448 | 365.3016
3875.5979 | 577.2729 | 363.3818 | 362.2264 | 365.2216
3876.5979 | 577.4485 | 363.2412 | 362.4622 | 365.132
3877.5979 | 576.7731 | 363.0613 | 362.4445 | 365.1804
3878.5979 | 575.8295 | 363.2791 | 362.3525 | 365.212
3879.5979 | 575.0821 | 363.2357 | 362.2274 | 364.972
3880.5979 | 574.0794 | 363.1552 | 362.0383 | 365.1455
3881.5979 | 574.1174 | 362.9675 | 361.7143 | 365.1616
3882.5979 | 574.6801 | 362.7365 | 361.6248 | 364.8097
3883.5979 | 573.9373 | 362.6295 | 361.4378 | 364.5069
3884.5979 | 573.3443 | 362.7172 | 361.2451 | 364.403
3885.5979 | 572.8865 | 362.7049 | 360.9715 | 364.2069
3886.5979 | 572.9321 | 362.5803 | 360.8226 | 363.9305
3887.5979 | 573.4409 | 362.5766 | 360.804 | 363.814
3888.5979 | 574.5424 | 362.3341 | 360.6201 | 363.6122
3889.5979 | 574.7 | 362.1606 | 360.3843 | 363.402
3890.5979 | 573.6119 | 362.3407 | 360.1763 | 363.1359
3891.5979 | 572.1102 | 362.4354 | 360.1674 | 363.0524
3892.5979 | 570.9695 | 362.5904 | 360.1945 | 362.9197
3893.5979 | 570.5549 | 362.5802 | 360.1502 | 362.9752
3894.5979 | 570.8598 | 362.338 | 359.8677 | 362.9884
3895.5979 | 570.7338 | 362.0274 | 359.5774 | 362.817
3896.5979 | 570.1388 | 361.7116 | 359.3095 | 362.5064
3897.5979 | 569.5078 | 361.5324 | 359.1195 | 362.3089
3898.5979 | 569.092 | 361.3279 | 358.8688 | 362.1253
3899.5979 | 568.3384 | 361.1781 | 358.6489 | 361.9954
3900.5979 | 568.2206 | 361.0028 | 358.4336 | 361.6957
3901.5979 | 568.3374 | 360.7405 | 358.2176 | 361.5069
3902.5979 | 568.4699 | 360.4748 | 357.8911 | 361.2472
3903.5979 | 568.1568 | 360.2456 | 357.6668 | 360.9361
3904.5979 | 567.9676 | 360.0028 | 357.3936 | 360.6036
3905.5979 | 568.584 | 359.8307 | 357.1815 | 360.4106
3906.5979 | 570.3136 | 359.6901 | 357.0593 | 360.2209
3907.5979 | 572.8247 | 359.5681 | 356.8536 | 359.9187
3908.5979 | 574.3216 | 359.4696 | 356.6177 | 359.5399
3909.5979 | 574.6678 | 359.557 | 356.7087 | 359.3208
3910.5979 | 575.4401 | 359.6323 | 356.6613 | 359.1676
3911.5979 | 575.4904 | 359.6533 | 356.6323 | 359.0724
3912.5979 | 575.4011 | 359.5077 | 356.7008 | 359.8724
3913.5979 | 574.4842 | 359.409 | 356.7349 | 359.9599
3914.5979 | 573.5741 | 359.4181 | 356.6905 | 360.0811
3915.5979 | 573.0324 | 359.3864 | 356.6117 | 359.9313
3916.5979 | 571.8038 | 359.243 | 356.5834 | 359.8541
3917.5979 | 571.1784 | 359.0671 | 356.3538 | 359.8917
3918.5979 | 570.605 | 358.8625 | 356.3089 | 359.7079
3919.5979 | 570.9 | 358.7729 | 356.2047 | 359.563
3920.5979 | 570.8564 | 358.7486 | 356.1356 | 359.4366
3921.5979 | 571.5749 | 358.7106 | 356.0412 | 359.3724
3922.5979 | 571.9452 | 358.7078 | 356.2005 | 359.6159
3923.5979 | 572.3088 | 358.769 | 356.4101 | 359.6997
3924.5979 | 571.7496 | 358.95 | 356.6889 | 359.7927
3925.5979 | 571.4715 | 359.0718 | 356.6986 | 359.94
3926.5979 | 571.3018 | 359.2443 | 356.8293 | 360.0934
3927.5979 | 571.1809 | 359.2343 | 356.9594 | 360.1703
3928.5979 | 569.8144 | 359.2051 | 357.2905 | 360.3284
3929.5979 | 569.1345 | 359.2714 | 357.3227 | 360.4165
3930.5979 | 568.4722 | 359.3712 | 357.2914 | 360.4166
3931.5979 | 567.1789 | 359.6174 | 357.3542 | 360.7029
3932.5979 | 566.5966 | 359.9645 | 357.3804 | 360.8818
3933.5979 | 567.7623 | 360.0675 | 357.4027 | 360.8703
3934.5979 | 568.387 | 359.9622 | 357.269 | 360.8086
3935.5979 | 568.7202 | 359.7678 | 357.0795 | 360.6016
3936.5979 | 569.1563 | 359.5603 | 356.8872 | 360.2954
3937.5979 | 569.3752 | 359.3265 | 356.6862 | 360.3985
3938.5979 | 569.2079 | 359.3257 | 356.599 | 360.2829
3939.5979 | 568.7691 | 359.34 | 356.556 | 360.098
3940.5979 | 568.3623 | 359.2508 | 356.7339 | 359.8862
3941.5979 | 567.9126 | 359.0748 | 356.7259 | 359.8231
3942.5979 | 567.5198 | 358.6914 | 356.5957 | 359.8202
3943.5979 | 567.5382 | 358.3966 | 356.3551 | 359.6732
3944.5979 | 567.5536 | 358.2376 | 356.1127 | 359.672
3945.5979 | 567.4708 | 358.1446 | 356.1397 | 360.0324
3946.5979 | 567.1797 | 358.0484 | 356.0089 | 359.8497
3947.5979 | 567.6686 | 357.7218 | 355.82 | 359.9041
3948.5979 | 567.8942 | 357.4903 | 355.7229 | 360.2192
3949.5979 | 567.8021 | 357.3349 | 355.7587 | 360.1589
3950.5979 | 567.3892 | 357.1605 | 355.5818 | 359.9354
3951.5979 | 567.0989 | 357.0288 | 355.3909 | 359.7113
3952.5979 | 567.7972 | 356.8554 | 355.0976 | 359.8119
3953.5979 | 568.393 | 356.6378 | 354.743 | 359.6591
3954.5979 | 569.1055 | 356.3956 | 354.427 | 359.3903
3955.5979 | 568.7608 | 356.2704 | 354.2067 | 359.1043
3956.5979 | 568.27 | 356.1945 | 354.0933 | 358.9798
3957.5979 | 567.9207 | 356.2211 | 354.0214 | 358.8941
3958.5979 | 567.9872 | 356.1545 | 353.8973 | 358.7163
3959.5979 | 568.2173 | 356.2076 | 353.8514 | 358.4155
3960.5979 | 568.9511 | 356.1134 | 353.6148 | 358.1917
3961.5979 | 569.2644 | 355.921 | 353.3996 | 358.0827
3962.5979 | 569.5869 | 355.7811 | 353.1841 | 357.8564
3963.5979 | 569.487 | 355.5877 | 352.9663 | 357.7037
3964.6135 | 570.1718 | 355.4051 | 352.8346 | 357.417
3965.5979 | 570.9834 | 355.2254 | 352.7244 | 357.2003
3966.5979 | 571.49 | 355.0092 | 352.5664 | 357.2064
3967.5979 | 571.9839 | 354.9486 | 352.466 | 356.9183
3968.5979 | 572.4594 | 354.9067 | 352.5878 | 356.7638
3969.5979 | 572.7963 | 354.9509 | 352.8839 | 357.2001
3970.5979 | 573.5127 | 354.8717 | 352.9662 | 357.2576
3971.5979 | 574.8064 | 354.6806 | 352.8697 | 357.2713
3972.5979 | 575.8223 | 354.4783 | 352.7126 | 357.5523
3973.5979 | 576.3159 | 354.3733 | 352.528 | 357.6369
3974.5979 | 576.4305 | 354.4931 | 352.4588 | 357.351
3975.5979 | 576.5616 | 355.0125 | 352.5017 | 357.3134
3976.5979 | 576.6928 | 355.2339 | 352.7098 | 357.5241
3977.5979 | 576.2995 | 355.3751 | 353.0583 | 357.6988
3978.5979 | 576.3431 | 355.3363 | 353.3441 | 358.063
3979.5979 | 576.6622 | 355.2508 | 353.4399 | 358.1747
3980.5979 | 577.7507 | 355.171 | 353.3434 | 358.0353
3981.5979 | 578.7523 | 355.0463 | 353.1511 | 357.8873
3982.5979 | 579.359 | 354.813 | 352.8911 | 357.6893
3983.5979 | 579.8058 | 354.6206 | 352.61 | 357.466
3984.5979 | 580.0472 | 354.4481 | 352.4941 | 357.3734
3985.5979 | 579.8046 | 354.3353 | 352.4519 | 357.1208
3986.5979 | 578.9462 | 354.2477 | 352.5211 | 357.152
3987.5979 | 578.0073 | 354.2992 | 352.6673 | 357.259
3988.5979 | 577.3248 | 354.5295 | 352.9881 | 357.2743
3989.5979 | 576.9694 | 354.5267 | 353.2106 | 357.3213
3990.5979 | 576.6371 | 354.4316 | 353.1402 | 357.2258
3991.5979 | 576.5558 | 354.3579 | 352.8668 | 357.0686
3992.5979 | 576.3451 | 354.193 | 352.5581 | 356.7188
3993.5979 | 576.3397 | 354.0424 | 352.2494 | 356.2991
3994.5979 | 576.3106 | 353.8857 | 352.0732 | 356.267
3995.5979 | 576.3521 | 353.8005 | 351.9395 | 356.3492
3996.5979 | 576.1161 | 353.705 | 351.7632 | 356.1557
3997.5979 | 575.6782 | 353.506 | 351.8247 | 356.2194
3998.5979 | 575.0261 | 353.3177 | 351.8435 | 356.3392
3999.5979 | 574.8968 | 353.2467 | 351.7503 | 356.1615
4000.5979 | 574.7714 | 353.3317 | 351.7335 | 356.029
4001.5979 | 574.7828 | 353.3188 | 351.5093 | 356.242
4002.5979 | 574.8899 | 353.1837 | 351.3016 | 356.0072
4003.5979 | 574.8169 | 353.0906 | 351.1391 | 355.7563
4004.5979 | 575.1155 | 353.0094 | 350.9491 | 355.5706
4005.5979 | 575.5768 | 352.8783 | 350.6885 | 355.2498
4006.5979 | 575.6445 | 352.6609 | 350.4537 | 354.8656
4007.5979 | 575.9937 | 352.3975 | 350.2008 | 354.9884
4008.5979 | 575.9634 | 352.2344 | 350.0707 | 354.825
4009.5979 | 575.5533 | 352.2479 | 349.9152 | 354.4961
4010.5979 | 575.4089 | 352.1476 | 349.7122 | 354.4369
4011.5979 | 576.0615 | 352.0715 | 349.5218 | 354.6248
4012.5979 | 576.7725 | 351.9593 | 349.297 | 354.529
4013.5979 | 577.3261 | 351.7933 | 349.1049 | 354.5519
4014.5979 | 577.2545 | 351.7404 | 349.2029 | 355.01
4015.5979 | 576.8135 | 351.9922 | 349.234 | 354.9844
4016.5979 | 576.5596 | 352.0691 | 349.2413 | 354.8133
4017.5979 | 576.3601 | 352.0378 | 349.4983 | 354.6384
4018.5979 | 576.9002 | 352.1617 | 349.8975 | 354.9111
4019.5979 | 577.3179 | 352.5445 | 350.4081 | 355.0899
4020.5979 | 577.103 | 352.7402 | 350.4978 | 355.1393
4021.5979 | 576.3946 | 352.7888 | 350.5043 | 355.2347
4022.5979 | 576.0423 | 352.7689 | 350.5174 | 355.5069
4023.5979 | 576.1789 | 352.7534 | 350.4197 | 355.3779
4024.5979 | 576.6285 | 352.6394 | 350.4207 | 355.2496
4025.5979 | 577.1163 | 352.4404 | 350.2452 | 355.1739
4026.5979 | 577.8194 | 352.2077 | 349.9466 | 354.8786
4027.5979 | 578.2585 | 352.0579 | 349.7429 | 354.6687
4028.5979 | 578.1768 | 352.0529 | 349.6328 | 354.4874
4029.5979 | 578.6537 | 352.0902 | 349.617 | 354.3219
4030.5979 | 578.6428 | 352.0668 | 349.8078 | 354.4069
4031.5979 | 578.1814 | 352.0173 | 349.9272 | 354.6336
4032.5979 | 577.8198 | 351.6911 | 350.1052 | 354.7229
4033.5979 | 577.6076 | 351.4927 | 349.9189 | 354.7682
4034.5979 | 577.3112 | 351.2057 | 349.6671 | 354.6257
4035.5979 | 577.0026 | 350.9999 | 349.5259 | 354.4943
4036.5979 | 577.1372 | 350.8509 | 349.3297 | 354.2698
4037.5979 | 576.7227 | 350.5619 | 349.2314 | 354.002
4038.5979 | 576.3649 | 350.4005 | 349.0402 | 354.0425
4039.5979 | 576.5677 | 350.2095 | 348.949 | 354.0062
4040.5979 | 577.753 | 350.0644 | 348.8412 | 353.8923
4041.5979 | 578.7658 | 349.9446 | 348.6556 | 353.8183
4042.5979 | 579.5898 | 349.8475 | 348.811 | 353.5344
4043.5979 | 579.9383 | 349.9336 | 349.1468 | 353.3995
4044.5979 | 579.6699 | 350.2038 | 349.0788 | 353.8315
4045.5979 | 579.0986 | 350.3418 | 349.1815 | 353.593
4046.5979 | 579.2932 | 350.2907 | 349.0276 | 353.3825
4047.5979 | 579.8532 | 350.1575 | 348.943 | 353.4605
4048.5979 | 579.538 | 350.1142 | 348.8421 | 353.3495
4049.5979 | 579.2256 | 350.0057 | 348.6853 | 353.1224
4050.5979 | 578.9974 | 349.9296 | 348.6176 | 352.9501
4051.5979 | 578.1367 | 349.9521 | 348.6371 | 352.8613
4052.5979 | 577.5058 | 349.9984 | 348.6493 | 352.9884
4053.5979 | 577.3201 | 350.0065 | 348.8773 | 353.0818
4054.5979 | 578.2436 | 349.9626 | 349.0515 | 352.9174
4055.5979 | 579.0329 | 349.7857 | 348.7983 | 352.7304
4056.5979 | 578.9963 | 349.4608 | 348.5328 | 352.4467
4057.5979 | 578.4948 | 349.1406 | 348.2708 | 352.2449
4058.5979 | 578.6014 | 348.9724 | 348.1317 | 352.0414
4059.5979 | 579.2733 | 348.83 | 347.9391 | 352.0102
4060.5979 | 579.4256 | 348.7767 | 347.8372 | 351.831
4061.5979 | 579.3474 | 348.8811 | 347.7721 | 351.6593
4062.5979 | 579.4697 | 348.8273 | 347.967 | 351.874
4063.5979 | 579.3657 | 348.8051 | 348.0791 | 352.0694
4064.5979 | 579.3832 | 348.9695 | 347.9964 | 352.2138
4065.5979 | 579.7944 | 349.1937 | 347.8734 | 352.4738
4066.5979 | 580.5363 | 349.1251 | 347.8846 | 352.3325
4067.5979 | 580.6692 | 349.0016 | 347.9517 | 352.1355
4068.5979 | 580.2741 | 348.9059 | 347.7859 | 352.0876
4069.5979 | 579.111 | 348.8865 | 347.907 | 351.9959
4070.5979 | 577.9312 | 349.163 | 348.2484 | 351.8897
4071.5979 | 577.0906 | 349.316 | 348.111 | 351.7803
4072.5979 | 576.6448 | 349.3108 | 348.2824 | 351.6287
4073.5979 | 576.3351 | 349.2259 | 348.0545 | 351.5138
4074.5979 | 577.004 | 349.139 | 347.9568 | 351.1755
4075.5979 | 577.416 | 349.1069 | 347.6468 | 350.8998
4076.5979 | 577.6634 | 348.917 | 347.2893 | 350.7243
4077.5979 | 577.4541 | 348.8308 | 347.3271 | 350.7143
4078.5979 | 576.724 | 348.9561 | 347.3151 | 350.6372
4079.5979 | 576.027 | 348.9557 | 347.128 | 350.5097
4080.5979 | 575.1526 | 348.8815 | 347.0162 | 350.4324
4081.5979 | 574.6478 | 348.6074 | 346.9564 | 350.2031
4082.5979 | 574.7249 | 348.4222 | 346.7204 | 350.1267
4083.5979 | 574.3251 | 348.2725 | 346.8227 | 350.316
4084.5979 | 573.6143 | 348.1852 | 346.6994 | 350.2071
4085.5979 | 573.1319 | 348.0309 | 346.3847 | 349.8895
4086.5979 | 572.9158 | 347.83 | 346.1603 | 349.8987
4087.5979 | 573.343 | 347.7085 | 346.0108 | 349.8911
4088.5979 | 573.4057 | 347.5519 | 345.7318 | 349.6386
4089.5979 | 573.8265 | 347.3418 | 345.3705 | 349.1703
4090.5979 | 574.6997 | 347.1374 | 345.0722 | 348.9365
4091.5979 | 575.6138 | 346.9444 | 344.7684 | 348.722
4092.5979 | 576.4308 | 346.752 | 344.4213 | 348.4363
4093.5979 | 576.8694 | 346.4482 | 343.9593 | 348.5776
4094.5979 | 577.2347 | 346.3323 | 343.7538 | 348.2659
4095.5979 | 577.7728 | 346.2563 | 343.4809 | 348.1393
4096.5979 | 578.1219 | 346.0643 | 343.4231 | 348.007
4097.5979 | 578.0764 | 345.9032 | 343.2981 | 348.3453
4098.5979 | 577.7784 | 345.7662 | 343.1301 | 348.1598
4099.5979 | 577.4378 | 345.6867 | 343.2718 | 347.9423
4100.5979 | 577.2969 | 345.4662 | 343.164 | 348.2221
4101.5979 | 577.1837 | 345.3037 | 342.9645 | 348.0787
4102.5979 | 577.8238 | 345.3036 | 342.9368 | 348.1408
4103.5979 | 578.029 | 345.1718 | 342.7733 | 348.1193
4104.5979 | 578.1711 | 345.0469 | 342.6734 | 347.8912
4105.5979 | 577.8768 | 344.9186 | 342.517 | 347.6458
4106.5979 | 577.915 | 344.8244 | 342.3672 | 347.4596
4107.5979 | 578.0245 | 344.6914 | 342.1503 | 347.2079
4108.5979 | 577.7966 | 344.5571 | 341.9228 | 346.9381
4109.5979 | 578.198 | 344.4365 | 341.7412 | 347.079
4110.5979 | 578.6953 | 344.3209 | 341.6455 | 347.3338
4111.5979 | 579.0793 | 344.2013 | 341.6176 | 347.1955
4112.5979 | 578.9439 | 344.1257 | 341.6332 | 347.0375
4113.5979 | 578.6992 | 344.1153 | 341.504 | 347.0986
4114.5979 | 578.6023 | 344.073 | 341.528 | 346.9289
4115.5979 | 578.5385 | 343.9291 | 341.5518 | 346.9948
4116.5979 | 578.0653 | 343.8404 | 341.4503 | 346.9522
4117.5979 | 577.2787 | 343.7069 | 341.5367 | 346.8085
4118.5979 | 576.5606 | 343.4847 | 341.4996 | 346.7846
4119.5979 | 575.9712 | 343.4007 | 341.3387 | 346.5688
4120.5979 | 576.282 | 343.2917 | 341.1355 | 346.3564
4121.5979 | 576.0918 | 343.1405 | 340.9115 | 346.0696
4122.5979 | 575.4606 | 342.9956 | 340.6349 | 345.7908
4123.5979 | 575.4296 | 342.9839 | 340.5925 | 345.5492
4124.5979 | 575.4128 | 342.8699 | 340.4193 | 345.5289
4125.5979 | 575.2682 | 342.7456 | 340.2404 | 345.3025
4126.5979 | 575.5112 | 342.5709 | 340.1443 | 345.2585
4127.5979 | 575.959 | 342.421 | 340.117 | 345.2082
4128.5979 | 575.9896 | 342.2338 | 339.8948 | 345.0769
4129.5979 | 576.1329 | 342.0315 | 339.8299 | 344.7718
4130.5979 | 576.6117 | 341.9012 | 339.5722 | 344.6479
4131.5979 | 576.7346 | 341.7528 | 339.3428 | 344.5483
4132.5979 | 576.9819 | 341.5353 | 339.1364 | 344.6696
4133.5979 | 576.7918 | 341.5002 | 339.1548 | 344.5684
4134.5979 | 576.0427 | 341.6398 | 339.2562 | 344.4394
4135.5979 | 574.5491 | 341.6886 | 339.4124 | 344.3116
4136.5979 | 574.2368 | 341.6344 | 339.3436 | 344.2323
4137.5979 | 573.5799 | 341.5298 | 339.3433 | 344.313
4138.5979 | 573.4911 | 341.4057 | 339.4027 | 344.4304
4139.5979 | 573.87 | 341.1966 | 339.3086 | 344.4141
4140.5979 | 574.3282 | 341.309 | 339.4437 | 344.4222
4141.5979 | 574.7231 | 341.5273 | 339.4655 | 344.832
4142.5979 | 575.0681 | 341.5173 | 339.533 | 345.0335
4143.5979 | 575.5219 | 341.512 | 339.7126 | 345.1469
4144.5979 | 575.5014 | 341.7065 | 340.1827 | 345.5017
4145.5979 | 575.3391 | 342.108 | 340.391 | 345.4074
4146.5979 | 575.3557 | 341.9831 | 340.5773 | 345.3671
4147.5979 | 575.7776 | 341.8513 | 340.6426 | 345.4299
4148.5979 | 575.8549 | 341.6982 | 340.5186 | 345.3923
4149.5979 | 575.7476 | 341.4915 | 340.3184 | 345.243
4150.5979 | 576.1632 | 341.329 | 340.1758 | 345.3618
4151.5979 | 576.2116 | 341.1918 | 340.0194 | 345.3456
4152.5979 | 576.4351 | 341.021 | 339.6575 | 344.9823
4153.5979 | 576.8124 | 340.7584 | 339.2021 | 344.5079
4154.5979 | 576.5001 | 340.5604 | 338.7995 | 344.3302
4155.5979 | 576.1687 | 340.4198 | 338.5469 | 344.1885
4156.5979 | 575.7713 | 340.3505 | 338.347 | 343.9016
4157.5979 | 575.1837 | 340.2415 | 338.0879 | 343.4867
4158.5979 | 574.5239 | 340.0852 | 337.8428 | 343.2003
4159.5979 | 573.998 | 339.9525 | 337.6333 | 342.8853
4160.5979 | 573.7388 | 339.8509 | 337.4438 | 342.6661
4161.5979 | 573.3673 | 339.7583 | 337.202 | 342.4725
4162.5979 | 573.5384 | 339.6904 | 336.9975 | 342.2391
4163.5979 | 573.5467 | 339.6444 | 336.8645 | 341.8819
4164.5979 | 573.1433 | 339.63 | 336.8769 | 341.6203
4165.5979 | 572.725 | 339.6649 | 336.769 | 341.7803
4166.5979 | 572.4949 | 339.6841 | 336.7205 | 341.7439
4167.5979 | 572.6211 | 339.725 | 336.6127 | 341.5563
4168.5979 | 572.7672 | 339.7213 | 336.5547 | 341.4072
4169.5979 | 572.5746 | 339.6075 | 336.4466 | 341.3556
4170.5979 | 571.8617 | 339.4677 | 336.3313 | 341.2351
4171.5979 | 571.3567 | 339.3074 | 336.1876 | 340.8136
4172.5979 | 570.9795 | 339.157 | 335.9789 | 340.4819
4173.5979 | 570.9455 | 339.0049 | 335.7424 | 340.2502
4174.5979 | 570.9686 | 338.9701 | 335.5933 | 340.0063
4175.5979 | 571.188 | 338.8375 | 335.5217 | 339.9252
4176.5979 | 570.9992 | 338.7482 | 335.4141 | 339.7994
4177.5979 | 570.9099 | 338.6629 | 335.2923 | 339.6354
4178.5979 | 571.221 | 338.6084 | 335.2339 | 339.4897
4179.5979 | 571.6471 | 338.5341 | 335.1224 | 339.2868
4180.5979 | 571.8908 | 338.3712 | 335.0107 | 339.1179
4181.5979 | 572.6478 | 338.2065 | 334.9191 | 339.097
4182.5979 | 573.5469 | 338.0884 | 334.813 | 339.0053
4183.5979 | 574.1855 | 338.0176 | 334.9377 | 338.9651
4184.5979 | 574.6781 | 337.9462 | 334.846 | 339.2011
4185.5979 | 574.3276 | 338.0384 | 334.925 | 339.3034
4186.5979 | 573.8753 | 338.2409 | 335.137 | 339.578
4187.5979 | 573.7657 | 338.3587 | 335.4143 | 340.0565
4188.5979 | 573.4987 | 338.2489 | 335.6488 | 340.3706
4189.5979 | 572.6558 | 338.128 | 335.7615 | 340.5982
4190.5979 | 571.8379 | 338.0884 | 335.8008 | 340.6671
4191.5979 | 571.6471 | 338.1794 | 335.8715 | 341.0446
4192.5979 | 571.5333 | 338.172 | 335.9784 | 341.2075
4193.5979 | 572.2445 | 338.1214 | 335.8785 | 341.1001
4194.5979 | 573.1324 | 338.0338 | 335.753 | 340.8999
4195.5979 | 573.1263 | 337.9549 | 335.6661 | 340.9501
4196.5979 | 572.7359 | 337.7622 | 335.5591 | 341.0198
4197.5979 | 572.2288 | 337.6585 | 335.3604 | 340.9284
4198.5979 | 571.743 | 337.583 | 335.1394 | 340.7645
4199.5979 | 571.1451 | 337.5123 | 334.9964 | 340.6435
4200.5979 | 570.8046 | 337.4612 | 334.9161 | 340.4369
4201.5979 | 570.8562 | 337.3954 | 334.9518 | 340.3248
4202.5979 | 571.3203 | 337.3403 | 334.8503 | 340.3317
4203.5979 | 571.9331 | 337.2555 | 334.6822 | 340.1532
4204.5979 | 571.7422 | 337.189 | 334.5221 | 339.8573
4205.5979 | 571.501 | 337.012 | 334.3498 | 339.6791
4206.5979 | 571.2539 | 336.8904 | 334.0794 | 339.613
4207.5979 | 570.7017 | 336.8171 | 333.8927 | 339.4927
4208.5979 | 570.1724 | 336.697 | 333.7141 | 339.205
4209.5979 | 570.4079 | 336.4469 | 333.5031 | 338.886
4210.5979 | 570.5525 | 336.2039 | 333.291 | 338.8567
4211.5979 | 570.4346 | 336.0756 | 333.1862 | 338.7793
4212.5979 | 570.4771 | 335.9786 | 333.0531 | 338.5508
4213.5979 | 570.603 | 335.9337 | 332.9751 | 338.3133
4214.5979 | 571.2707 | 335.8146 | 332.7918 | 338.3218
4215.5979 | 571.8766 | 335.7545 | 332.6347 | 338.2147
4216.5979 | 572.3597 | 335.6809 | 332.4414 | 338.0386
4217.5979 | 572.858 | 335.5176 | 332.3207 | 338.0022
4218.5979 | 573.4382 | 335.3647 | 332.2026 | 338.0724
4219.5979 | 573.8953 | 335.1154 | 332.0018 | 338.326
4220.5979 | 573.9364 | 335.0502 | 331.8941 | 338.21
4221.5979 | 573.7312 | 335.0551 | 331.842 | 338.2176
4222.5979 | 573.976 | 334.9829 | 331.9313 | 338.4442
4223.5979 | 574.246 | 334.8309 | 332.2015 | 338.9279
4224.5979 | 574.5012 | 334.7615 | 332.186 | 339.1881
4225.5979 | 574.776 | 334.7716 | 332.1753 | 339.0586
4226.5979 | 574.7678 | 334.8477 | 331.9798 | 339.0585
4227.5979 | 575.0098 | 334.7628 | 332.0393 | 338.9034
4228.5979 | 575.7501 | 334.6828 | 331.8571 | 339.0565
4229.5979 | 576.3657 | 334.5462 | 331.7055 | 338.8772
4230.5979 | 576.3988 | 334.4804 | 331.6164 | 339.0483
4231.5979 | 576.4845 | 334.5764 | 331.7552 | 338.8949
4232.5979 | 576.4672 | 334.6182 | 332.0136 | 338.7319
4233.5979 | 576.442 | 334.5765 | 331.95 | 338.555
4234.5979 | 576.0406 | 334.5084 | 331.8279 | 338.7587
4235.5979 | 575.854 | 334.3944 | 331.7628 | 338.7082
4236.5979 | 575.4987 | 334.3543 | 331.687 | 338.5167
4237.5979 | 574.9417 | 334.2529 | 331.4228 | 338.4484
4238.5979 | 574.9604 | 334.2496 | 331.3734 | 339.0397
4239.5979 | 574.97 | 334.2089 | 331.2217 | 339.0382
4240.5979 | 575.0457 | 334.0969 | 331.0462 | 338.6594
4241.5979 | 574.9939 | 333.9519 | 330.821 | 338.2301
4242.5979 | 574.7112 | 333.8397 | 330.6789 | 337.7769
4243.5979 | 575.0098 | 333.684 | 330.5244 | 337.553
4244.5979 | 575.1311 | 333.6441 | 330.4934 | 337.7125
4245.5979 | 574.9676 | 333.5413 | 330.4234 | 337.6193
4246.5979 | 574.5057 | 333.4261 | 330.3782 | 337.511
4247.5979 | 574.4295 | 333.2608 | 330.4599 | 337.6727
4248.5979 | 574.6681 | 333.2621 | 330.5687 | 337.5977
4249.5979 | 574.8307 | 333.3055 | 330.7971 | 337.507
4250.5979 | 574.6825 | 333.2934 | 331.1523 | 337.7675
4251.5979 | 574.6155 | 333.3938 | 331.2582 | 337.882
4252.5979 | 574.4066 | 333.4943 | 331.3655 | 337.7593
4253.5979 | 574.1607 | 333.3458 | 331.4623 | 337.7075
4254.5979 | 574.0398 | 333.1863 | 331.5312 | 337.7702
4255.5979 | 574.2819 | 333.2686 | 331.6376 | 337.6758
4256.5979 | 574.3443 | 333.2516 | 331.6951 | 337.6258
4257.5979 | 574.1886 | 333.1775 | 331.7753 | 337.9124
4258.5979 | 574.0112 | 333.1262 | 331.6059 | 337.8996
4259.5979 | 573.7306 | 332.8664 | 331.5476 | 337.7501
4260.5979 | 573.6673 | 332.9063 | 331.6681 | 337.85
4261.5979 | 573.6648 | 332.788 | 331.5542 | 337.8849
4262.5979 | 573.6447 | 332.7406 | 331.2867 | 337.6935
4263.5979 | 573.3878 | 332.6288 | 330.9381 | 337.3887
4264.5979 | 573.1542 | 332.4524 | 330.69 | 337.0186
4265.5979 | 572.9557 | 332.3236 | 330.4458 | 336.7399
4266.5979 | 573.1986 | 332.2494 | 330.2451 | 336.529
4267.5979 | 573.4759 | 332.2381 | 330.0813 | 336.2592
4268.5979 | 574.0358 | 332.239 | 329.8799 | 335.8627
4269.5979 | 574.4602 | 332.191 | 329.6644 | 335.4541
4270.5979 | 574.62 | 332.1455 | 329.4303 | 335.0778
4271.5979 | 574.8748 | 332.1 | 329.4611 | 335.2032
4272.5979 | 574.6678 | 332.1086 | 329.7478 | 335.126
4273.5979 | 574.5811 | 331.9076 | 329.7486 | 335.012
4274.5979 | 574.495 | 331.7184 | 329.7096 | 334.9392
4275.5979 | 574.7186 | 331.6728 | 329.6887 | 335.063
4276.5979 | 574.636 | 331.5695 | 329.7163 | 335.1344
4277.5979 | 574.8728 | 331.5737 | 329.6945 | 335.2683
4278.5979 | 574.7219 | 331.5257 | 329.6591 | 335.258
4279.5979 | 574.321 | 331.4282 | 329.5013 | 335.2958
4280.5979 | 574.4532 | 331.5472 | 329.7169 | 335.3415
4281.5979 | 574.7698 | 331.5501 | 329.6068 | 335.3198
4282.5979 | 575.1824 | 331.5243 | 329.4522 | 335.0352
4283.5979 | 575.4977 | 331.4842 | 329.1851 | 334.6866
4284.5979 | 576.3115 | 331.4873 | 329.1075 | 334.5513
4285.5979 | 576.6381 | 331.4498 | 329.328 | 334.6302
4286.5979 | 576.6496 | 331.3775 | 329.2868 | 334.6574
4287.5979 | 576.3971 | 331.2112 | 329.0932 | 334.8358
4288.5979 | 576.4211 | 330.6649 | 328.932 | 334.6215
4289.5979 | 577.1007 | 330.4875 | 328.9309 | 334.5672
4290.5979 | 577.4771 | 330.0824 | 328.7159 | 334.585
4291.5979 | 577.9657 | 329.96 | 328.8066 | 334.6365
4292.5979 | 578.3778 | 330.026 | 328.9005 | 334.5697
4293.5979 | 579.2398 | 329.9807 | 328.753 | 334.4098
4294.5979 | 579.6536 | 329.908 | 328.6374 | 334.2419
4295.5979 | 579.8134 | 329.8273 | 328.4555 | 333.9878
4296.5979 | 580.4801 | 329.7566 | 328.3992 | 334.0888
4297.5979 | 580.9707 | 329.7828 | 328.371 | 334.046
4298.5979 | 581.6347 | 329.8396 | 328.4002 | 334.0437
4299.5979 | 582.4282 | 329.8885 | 328.2787 | 334.0273
4300.5979 | 582.8829 | 329.8571 | 328.5652 | 334.1324
4301.5979 | 583.6627 | 330.1406 | 328.6995 | 334.2259
4302.5979 | 584.3687 | 330.2942 | 328.8381 | 334.3247
4303.5979 | 585.3107 | 330.3779 | 328.8845 | 334.3716
4304.5979 | 586.1422 | 330.51 | 329.0694 | 334.5979
4305.5979 | 586.3642 | 330.7207 | 329.3105 | 334.6449
4306.5979 | 586.8087 | 330.7334 | 329.3785 | 334.5286
4307.5979 | 587.6714 | 330.5598 | 329.3207 | 334.4192
4308.5979 | 588.3495 | 330.3283 | 329.1459 | 334.4137
4309.5979 | 588.682 | 330.0563 | 329.0518 | 334.3108
4310.5979 | 588.9333 | 329.8733 | 328.8895 | 334.4168
4311.5979 | 589.1667 | 329.6407 | 328.4861 | 334.2076
4312.5979 | 589.5651 | 329.4601 | 328.0071 | 333.7793
4313.5979 | 589.5133 | 329.3506 | 327.6893 | 333.4533
4314.5979 | 589.1884 | 329.2098 | 327.4614 | 333.2009
4315.5979 | 589.7553 | 329.0676 | 327.3536 | 332.7709
4316.5979 | 590.7175 | 329.0248 | 327.1415 | 332.5765
4317.5979 | 590.7291 | 328.9103 | 326.8463 | 332.3278
4318.5979 | 591.0956 | 328.809 | 326.638 | 332.1471
4319.5979 | 592.0046 | 328.7467 | 326.4434 | 332.0001
4320.5979 | 592.8102 | 328.6593 | 326.4092 | 331.8284
4321.5979 | 593.282 | 328.6298 | 326.3419 | 331.6657
4322.5979 | 593.7027 | 328.4271 | 326.2996 | 331.8296
4323.5979 | 593.9263 | 328.0962 | 326.2379 | 332.1592
4324.5979 | 593.7153 | 328.0781 | 326.0494 | 332.1776
4325.5979 | 593.703 | 328.3159 | 326.2855 | 332.1585
4326.5979 | 594.1684 | 328.516 | 326.5421 | 332.1596
4327.5979 | 594.2947 | 328.5042 | 326.7868 | 332.3284
4328.5979 | 594.2117 | 328.5325 | 326.9686 | 332.7039
4329.5979 | 593.9342 | 328.441 | 326.9653 | 332.8168
4330.5979 | 593.8545 | 328.2426 | 326.7993 | 332.7669
4331.5979 | 594.079 | 328.1241 | 326.7329 | 332.6124
4332.5979 | 594.592 | 327.9686 | 326.4919 | 332.2939
4333.5979 | 594.972 | 327.8471 | 326.2532 | 332.0225
4334.5979 | 594.9382 | 327.6422 | 325.9159 | 331.7681
4335.5979 | 595.4112 | 327.3893 | 325.5415 | 331.5247
4336.5979 | 596.0198 | 327.0641 | 325.3906 | 331.4069
4337.5979 | 596.1579 | 326.8031 | 325.1071 | 331.232
4338.5979 | 595.6478 | 326.7414 | 324.8993 | 330.9497
4339.5979 | 595.8233 | 326.6883 | 324.8597 | 330.766
4340.5979 | 596.5432 | 326.6122 | 324.7518 | 330.8429
4341.5979 | 596.8309 | 326.5711 | 324.5413 | 330.5978
4342.5979 | 596.5281 | 326.5488 | 324.3256 | 330.2892
4343.5979 | 596.5699 | 326.5432 | 324.2503 | 330.3487
4344.5979 | 597.0629 | 326.533 | 324.0954 | 330.1736
4345.5979 | 597.274 | 326.5432 | 324.0482 | 329.9138
4346.5979 | 597.4355 | 326.6613 | 324.0875 | 329.8043
4347.5979 | 597.3969 | 326.7283 | 324.1836 | 329.7429
4348.5979 | 596.7266 | 326.6704 | 324.1396 | 329.7675
4349.5979 | 596.4562 | 326.5933 | 324.0659 | 329.5556
4350.5979 | 596.6444 | 326.4997 | 323.9329 | 329.3725
4351.5979 | 596.8958 | 326.2691 | 323.7717 | 329.1699
4352.5979 | 597.3803 | 326.0234 | 323.5581 | 328.9806
4353.5979 | 597.6737 | 325.9455 | 323.4681 | 329.0775
4354.5979 | 597.6417 | 325.8535 | 323.4113 | 329.0107
4355.5979 | 597.4314 | 325.4735 | 323.3381 | 328.8256
4356.5979 | 597.9351 | 325.3947 | 323.1992 | 328.7825
4357.5979 | 598.2102 | 325.3823 | 323.0866 | 328.8199
4358.5979 | 598.8065 | 325.3174 | 322.9649 | 328.9997
4359.5979 | 598.9691 | 325.4958 | 323.111 | 329.2395
4360.5979 | 599.517 | 325.5776 | 323.2125 | 329.4282
4361.5979 | 599.7911 | 325.5873 | 323.1819 | 329.365
4362.5979 | 600.1058 | 325.5104 | 323.1659 | 329.4858
4363.5979 | 600.8171 | 325.6556 | 323.6908 | 329.7839
4364.5979 | 601.4465 | 325.7286 | 324.0122 | 329.8371
4365.5979 | 602.2685 | 325.789 | 324.0986 | 329.7611
4366.5979 | 602.572 | 325.4783 | 324.0786 | 329.615
4367.5979 | 602.9295 | 325.4038 | 323.959 | 329.7191
4368.5979 | 602.976 | 325.3334 | 323.7354 | 329.5247
4369.5979 | 603.509 | 325.1816 | 323.7514 | 329.3769
4370.5979 | 604.1029 | 324.8022 | 323.579 | 329.1516
4371.5979 | 604.5457 | 324.5532 | 323.1151 | 328.8648
4372.5979 | 604.9656 | 324.3606 | 322.8847 | 328.8292
4373.5979 | 605.4979 | 324.2262 | 322.6961 | 328.7349
4374.5979 | 605.391 | 324.1029 | 322.4417 | 328.5717
4375.5979 | 605.3478 | 324.0299 | 322.3133 | 328.5853
4376.5979 | 605.5558 | 324.079 | 322.2881 | 328.8085
4377.5979 | 606.2286 | 324.0803 | 321.9962 | 328.6983
4378.5979 | 606.5007 | 324.0813 | 321.7825 | 328.4884
4379.5979 | 607.3963 | 324.0619 | 321.5842 | 328.2917
4380.5979 | 607.6439 | 324.065 | 321.289 | 327.8144
4381.5979 | 607.7808 | 324.0428 | 321.1261 | 327.4526
4382.5979 | 608.6366 | 323.9797 | 320.8169 | 327.2034
4383.5979 | 609.4382 | 323.8557 | 320.5819 | 327.1765
4384.5979 | 609.8327 | 323.5521 | 320.0957 | 327.1811
4385.5979 | 609.8138 | 323.4785 | 320.2522 | 327.1004
4386.5979 | 609.8601 | 323.4485 | 320.3393 | 327.1418
4387.5979 | 610.1416 | 323.4984 | 320.3528 | 327.1873
4388.5979 | 610.9146 | 323.4322 | 320.3253 | 327.1207
4389.5979 | 610.6514 | 323.2607 | 320.0299 | 327.1037
4390.5979 | 610.2596 | 323.2865 | 320.0203 | 326.7238
4391.5979 | 611.049 | 323.4131 | 319.8791 | 327.0333
4392.5979 | 611.2356 | 323.3548 | 319.7275 | 326.8572
4393.5979 | 610.9691 | 323.1939 | 319.4935 | 326.5096
4394.5979 | 610.6307 | 323.0151 | 319.3393 | 326.2861
4395.5979 | 610.7595 | 322.8959 | 319.3846 | 326.2805
4396.5979 | 611.5772 | 322.9259 | 319.3327 | 326.4079
4397.5979 | 612.2714 | 322.8228 | 319.2011 | 326.2678
4398.5979 | 612.958 | 322.7522 | 318.9499 | 325.9821
4399.5979 | 613.9509 | 322.7084 | 318.9397 | 325.76
4400.5979 | 614.5018 | 322.637 | 318.8371 | 325.7332
4401.5979 | 615.2909 | 322.5701 | 318.6947 | 325.8134
4402.5979 | 615.6507 | 322.5503 | 318.5304 | 325.727
4403.5979 | 616.1587 | 322.4585 | 318.409 | 325.525
4404.5979 | 616.2898 | 322.4448 | 318.5296 | 325.6668
4405.5979 | 616.437 | 322.4258 | 318.4999 | 325.7704
4406.5979 | 616.7455 | 322.3757 | 318.439 | 325.7235
4407.5979 | 617.2651 | 322.3429 | 318.375 | 325.6104
4408.5979 | 617.4195 | 322.3844 | 318.5037 | 325.6599
4409.5979 | 618.1877 | 322.2769 | 318.49 | 325.5962
4410.5979 | 618.3265 | 322.225 | 318.5424 | 325.6197
4411.5979 | 617.6954 | 322.1231 | 318.583 | 325.5896
4412.5979 | 617.4377 | 322.0445 | 318.484 | 325.3853
4413.5979 | 616.8224 | 321.9907 | 318.6519 | 325.1822
4414.5979 | 616.2158 | 321.8668 | 318.4407 | 325.0668
4415.5979 | 616.111 | 321.525 | 318.3097 | 324.9618
4416.5979 | 616.3324 | 321.4556 | 318.2906 | 325.2758
4417.5979 | 616.3806 | 321.2615 | 317.9432 | 325.2839
4418.5979 | 616.266 | 321.117 | 317.7885 | 324.9869
4419.5979 | 615.8748 | 320.9864 | 317.4717 | 324.6846
4420.5979 | 615.9967 | 320.9103 | 317.467 | 324.6214
4421.5979 | 615.8615 | 320.8477 | 317.4501 | 324.709
4422.5979 | 615.96 | 320.8059 | 317.3135 | 324.6295
4423.5979 | 616.0177 | 320.7356 | 317.1782 | 324.4839
4424.5979 | 616.3132 | 320.6961 | 316.9743 | 324.3174
4425.5979 | 616.5674 | 320.6294 | 316.8148 | 323.9596
4426.5979 | 616.9723 | 320.5029 | 316.6419 | 323.6047
4427.5979 | 617.208 | 320.198 | 316.3553 | 323.3692
4428.5979 | 617.4582 | 320.0065 | 316.1801 | 323.4248
4429.5979 | 617.5399 | 319.7911 | 316.2443 | 323.5669
4430.5979 | 617.5632 | 319.7011 | 316.1284 | 323.4877
4431.5979 | 617.8212 | 319.543 | 316.0276 | 323.2999
4432.5979 | 617.6586 | 319.4721 | 315.9508 | 323.2303
4433.5979 | 617.5437 | 319.329 | 315.8543 | 323.213
4434.5979 | 618.0924 | 319.2308 | 315.7798 | 323.0412
4435.5979 | 619.1719 | 319.1311 | 315.732 | 322.9608
4436.5979 | 619.6766 | 319.1204 | 315.8693 | 322.9066
4437.5979 | 619.7973 | 319.1093 | 315.9472 | 322.8042
4438.5979 | 619.5085 | 318.9424 | 315.897 | 322.6198
4439.5979 | 619.2598 | 318.8233 | 315.683 | 322.6929
4440.5979 | 619.4311 | 318.7821 | 315.5465 | 322.7789
4441.5979 | 618.8107 | 318.6867 | 315.1878 | 322.7432
4442.5979 | 619.1002 | 318.6034 | 315.1319 | 322.9113
4443.5979 | 619.7648 | 318.6985 | 315.2677 | 322.7669
4444.5979 | 620.1336 | 318.7364 | 315.3823 | 322.6115
4445.5979 | 620.2075 | 318.7733 | 315.4144 | 322.6275
4446.5979 | 620.7033 | 318.7616 | 315.4204 | 322.6553
4447.5979 | 620.3036 | 318.4555 | 315.3623 | 322.5036
4448.5979 | 619.78 | 318.319 | 315.2514 | 322.2471
4449.5979 | 619.1903 | 318.0322 | 315.1286 | 322.2129
4450.5979 | 619.2158 | 318.0124 | 315.1217 | 322.1107
4451.5979 | 619.6726 | 318.0374 | 315.0672 | 322.0071
4452.5979 | 620.2162 | 317.9776 | 314.8857 | 321.8121
4453.5979 | 621.0049 | 317.8632 | 314.7813 | 321.5207
4454.5979 | 621.8856 | 317.8679 | 314.6229 | 321.3034
4455.5979 | 621.8328 | 317.7727 | 314.3961 | 321.0893
4456.5979 | 621.7511 | 317.6208 | 314.2764 | 320.8457
4457.5979 | 621.2232 | 317.6062 | 314.1802 | 320.6709
4458.5979 | 621.0988 | 317.626 | 313.9751 | 320.509
4459.5979 | 621.1168 | 317.5601 | 313.7345 | 320.3629
4460.5979 | 621.2536 | 317.4121 | 313.5159 | 320.3254
4461.5979 | 621.7317 | 317.3044 | 313.4194 | 320.3359
4462.5979 | 621.6934 | 317.191 | 313.1009 | 320.2707
4463.5979 | 621.782 | 317.0271 | 312.9515 | 320.1455
4464.5979 | 621.8943 | 316.8101 | 312.9488 | 320.0129
4465.5979 | 621.8316 | 316.7381 | 312.8959 | 319.8646
4466.5979 | 621.6422 | 316.6427 | 312.9515 | 319.7409
4467.5979 | 621.434 | 316.4273 | 312.754 | 319.6688
4468.5979 | 620.9002 | 316.2726 | 312.6936 | 319.7053
4469.5979 | 620.5042 | 316.3297 | 312.5406 | 319.6351
4470.5979 | 620.4153 | 316.2243 | 312.0855 | 319.4917
4471.5979 | 620.0228 | 316.0454 | 311.7607 | 319.4945
4472.5979 | 619.5178 | 315.8536 | 311.7853 | 319.5706
4473.5979 | 619.1269 | 315.7196 | 311.8689 | 319.6182
4474.5979 | 619.0894 | 315.8627 | 311.9258 | 319.4332
4475.5979 | 618.8572 | 315.8149 | 311.827 | 319.5383
4476.5979 | 618.8011 | 315.8014 | 311.9758 | 319.6892
4477.5979 | 618.3042 | 315.7912 | 311.9623 | 319.6402
4478.5979 | 618.2123 | 315.8131 | 311.9918 | 319.4303
4479.5979 | 617.9355 | 315.8538 | 311.9562 | 319.2445
4480.5979 | 617.5709 | 315.8992 | 311.9398 | 319.1031
4481.5979 | 617.2206 | 315.9093 | 311.7989 | 318.8841
4482.5979 | 617.4194 | 315.8935 | 311.6333 | 318.6938
4483.5979 | 617.1729 | 315.8337 | 311.4144 | 318.4742
4484.5979 | 617.3457 | 315.7755 | 311.2213 | 318.5202
4485.5979 | 617.3877 | 315.7525 | 311.0074 | 318.4345
4486.5979 | 617.4454 | 315.7489 | 310.9133 | 318.209
4487.5979 | 617.6512 | 315.7285 | 310.842 | 318.0888
4488.5979 | 618.0412 | 315.658 | 310.8618 | 317.8846
4489.5979 | 618.0561 | 315.4354 | 310.7651 | 317.802
4490.5979 | 618.2284 | 315.3614 | 310.7818 | 317.9247
4491.5979 | 618.0905 | 315.2282 | 310.6826 | 317.8561
4492.5979 | 618.0584 | 315.0054 | 310.6544 | 317.904
4493.5979 | 617.9425 | 314.7846 | 310.5047 | 317.7222
4494.5979 | 618.3832 | 314.5802 | 310.4593 | 317.5568
4495.5979 | 618.5188 | 314.5515 | 310.4122 | 317.3762
4496.5979 | 618.4674 | 314.5266 | 310.3233 | 317.2348
4497.5979 | 618.9205 | 314.1788 | 310.0576 | 317.2333
4498.5979 | 619.0205 | 314.1057 | 309.6861 | 317.2432
4499.5979 | 618.8106 | 313.95 | 309.5552 | 317.3108
4500.5979 | 618.5343 | 313.7751 | 309.4255 | 317.2815
4501.5979 | 618.8553 | 313.5011 | 309.3916 | 317.1255
4502.5979 | 619.3839 | 313.5042 | 309.2372 | 316.937
4503.5979 | 619.2373 | 313.4016 | 309.1523 | 317.0583
4504.5979 | 619.1885 | 313.3131 | 309.0821 | 317.1927
4505.5979 | 618.8536 | 313.2863 | 309.0043 | 317.0533
4506.5979 | 618.3592 | 313.1879 | 308.9809 | 317.0269
4507.5979 | 618.3259 | 313.2063 | 308.8403 | 316.9926
4508.5979 | 617.6474 | 313.2158 | 308.7844 | 316.8692
4509.5979 | 617.1437 | 313.2015 | 308.6951 | 316.6293
4510.5979 | 616.662 | 313.3051 | 308.6956 | 316.4919
4511.5979 | 616.4247 | 313.342 | 308.696 | 316.2315
4512.5979 | 616.3475 | 313.3625 | 308.6516 | 316.013
4513.5979 | 616.2905 | 313.317 | 308.5797 | 315.8024
4514.5979 | 616.069 | 313.3014 | 308.5416 | 315.6597
4515.5979 | 616.089 | 313.2478 | 308.4154 | 315.4931
4516.5979 | 616.2202 | 313.2574 | 308.4648 | 315.296
4517.5979 | 615.9449 | 313.2647 | 308.5202 | 315.204
4518.5979 | 615.5394 | 313.2902 | 308.6061 | 315.2674
4519.5979 | 616.1689 | 313.3034 | 308.6574 | 315.3356
4520.5979 | 616.866 | 313.3235 | 308.7752 | 315.4716
4521.5979 | 616.9111 | 313.4522 | 308.8582 | 315.4511
4522.5979 | 617.2743 | 313.5982 | 308.6832 | 315.4521
4523.5979 | 616.6777 | 313.732 | 308.8444 | 315.5187
4524.5979 | 616.22 | 313.5006 | 308.6616 | 315.6253
4525.5979 | 616.133 | 313.3374 | 308.8107 | 315.7237
4526.5979 | 616.3244 | 313.1889 | 308.6889 | 315.7858
4527.5979 | 616.6073 | 313.0576 | 308.7371 | 315.7609
4528.5979 | 616.7305 | 312.9256 | 308.5772 | 315.5341
4529.5979 | 617.0123 | 312.6729 | 308.4804 | 315.6058
4530.5979 | 617.1278 | 312.4347 | 308.1559 | 315.3659
4531.5979 | 616.8884 | 312.2325 | 307.7321 | 315.1995
4532.5979 | 616.7823 | 312.1422 | 307.5535 | 314.9009
4533.5979 | 616.4488 | 312.0916 | 307.4949 | 314.7661
4534.5979 | 616.8343 | 312.0367 | 307.2671 | 314.6599
4535.5979 | 616.809 | 311.9129 | 306.9999 | 314.4359
4536.5979 | 617.0649 | 311.891 | 306.7983 | 314.2871
4537.5979 | 617.7999 | 311.7524 | 306.5453 | 314.6316
4538.5979 | 618.503 | 311.7354 | 306.591 | 314.6268
4539.5979 | 618.5116 | 311.8644 | 306.668 | 314.5735
4540.5979 | 617.7608 | 311.7516 | 306.4681 | 314.3826
4541.5979 | 617.1149 | 311.5032 | 306.2398 | 314.4151
4542.5979 | 616.3191 | 311.4139 | 305.9008 | 314.576
4543.5979 | 616.1911 | 311.1036 | 305.9611 | 314.3681
4544.5979 | 616.2767 | 311.096 | 305.9 | 314.0348
4545.5979 | 616.4381 | 310.9307 | 305.8325 | 314.1022
4546.5979 | 616.8688 | 310.7748 | 305.8034 | 313.9237
4547.5979 | 616.62 | 310.6429 | 305.5944 | 313.8459
4548.5979 | 616.8835 | 310.4798 | 305.581 | 313.8512
4549.5979 | 616.6673 | 310.4657 | 305.8541 | 313.9842
4550.5979 | 616.4265 | 310.592 | 305.8802 | 313.9768
4551.5979 | 616.1984 | 310.424 | 306.0438 | 313.9175
4552.5979 | 615.8347 | 310.4035 | 306.419 | 313.9591
4553.5979 | 615.6455 | 310.3179 | 306.8241 | 314.0734
4554.5979 | 615.8556 | 310.242 | 306.9337 | 314.2131
4555.5979 | 615.7808 | 310.1895 | 306.885 | 314.184
4556.5979 | 615.4337 | 310.1229 | 306.8447 | 314.0527
4557.5979 | 614.6366 | 310.1046 | 306.8299 | 313.866
4558.5979 | 613.6923 | 310.112 | 306.6982 | 313.6657
4559.5979 | 612.9227 | 310.128 | 306.6005 | 313.4712
4560.5979 | 613.1818 | 310.1368 | 306.4976 | 313.3421
4561.5979 | 613.9597 | 310.1137 | 306.379 | 313.0838
4562.5979 | 614.4996 | 310.1583 | 306.0159 | 312.7797
4563.5979 | 614.4775 | 310.1592 | 305.9282 | 312.5804
4564.5979 | 614.6677 | 310.1557 | 305.8512 | 312.3928
4565.6135 | 614.5576 | 310.0609 | 305.7932 | 312.2563
4566.5979 | 614.4427 | 309.9159 | 305.758 | 312.1067
4567.5979 | 614.8239 | 309.8484 | 305.6569 | 311.9369
4568.5979 | 615.0728 | 309.8225 | 305.6522 | 312.0106
4569.5979 | 615.6521 | 309.8534 | 305.6716 | 312.2435
4570.5979 | 616.2467 | 309.842 | 305.4956 | 312.1246
4571.5979 | 616.8495 | 309.8821 | 305.4399 | 311.9876
4572.5979 | 617.2739 | 309.9058 | 305.2766 | 312.2012
4573.5979 | 617.294 | 309.8241 | 305.154 | 312.1713
4574.5979 | 617.8747 | 309.7179 | 305.0505 | 312.1674
4575.5979 | 617.8556 | 309.5722 | 304.9416 | 312.0894
4576.5979 | 617.8869 | 309.3049 | 304.9472 | 312.1212
4577.5979 | 618.2993 | 309.0889 | 304.6147 | 312.1056
4578.5979 | 618.2626 | 309.0528 | 304.5439 | 312.0962
4579.5979 | 617.7544 | 309.0621 | 304.5188 | 312.1378
4580.5979 | 617.3469 | 308.9838 | 304.3271 | 312.2953
4581.5979 | 616.9835 | 308.8384 | 304.2917 | 312.3318
4582.5979 | 616.56 | 308.7123 | 304.4272 | 312.6584
4583.5979 | 616.2672 | 308.7215 | 304.5212 | 312.6033
4584.5979 | 615.8064 | 309.0409 | 304.7369 | 312.4796
4585.5979 | 615.5578 | 309.202 | 304.9657 | 312.3799
4586.5979 | 615.8474 | 309.0876 | 305.2205 | 312.3137
4587.5979 | 616.2425 | 308.7254 | 305.3629 | 312.0192
4588.5979 | 615.7257 | 308.6294 | 305.3881 | 312.0142
4589.5979 | 615.1036 | 308.4812 | 305.1936 | 311.8338
4590.5979 | 614.4147 | 308.3007 | 304.9296 | 311.7297
4591.5979 | 614.3381 | 308.1032 | 304.7638 | 311.5568
4592.5979 | 614.7642 | 307.9598 | 304.5731 | 311.4236
4593.5979 | 614.5042 | 307.7857 | 304.3708 | 311.1
4594.5979 | 614.5093 | 307.6751 | 304.1218 | 310.9087
4595.6135 | 614.544 | 307.3623 | 303.9673 | 310.7191
4596.5979 | 614.4632 | 307.4432 | 303.8596 | 310.5421
4597.5979 | 614.4403 | 307.476 | 303.6428 | 310.3625
4598.5979 | 614.4048 | 307.4143 | 303.3804 | 310.1248
4599.5979 | 614.5716 | 307.349 | 303.1604 | 309.9843
4600.5979 | 614.6043 | 307.3088 | 302.7171 | 309.777
4601.5979 | 614.9795 | 306.8837 | 302.5128 | 309.2796
4602.6135 | 614.6044 | 306.5383 | 302.3253 | 309.1628
4603.5979 | 614.561 | 306.5022 | 302.1453 | 309.161
4604.5979 | 614.8223 | 306.3912 | 302.0183 | 309.1491
4605.5979 | 614.3676 | 306.373 | 301.927 | 309.0717
4606.5979 | 614.5766 | 306.396 | 301.9245 | 308.8971
4607.5979 | 614.3102 | 306.4656 | 301.9956 | 308.9105
4608.5979 | 614.6763 | 306.4438 | 301.9305 | 308.9134
4609.5979 | 614.6558 | 306.438 | 301.6851 | 308.6226
4610.5979 | 614.705 | 306.3806 | 301.7396 | 308.5941
4611.5979 | 614.1668 | 306.3735 | 301.6544 | 308.6348
4612.5979 | 614.2612 | 306.3678 | 301.7153 | 308.6578
4613.5979 | 613.9006 | 306.429 | 301.7663 | 308.7396
4614.5979 | 613.8305 | 306.3967 | 301.8205 | 308.7038
4615.5979 | 613.9233 | 306.3585 | 301.7215 | 308.5503
4616.5979 | 613.8959 | 306.3772 | 301.7525 | 308.4594
4617.5979 | 614.2435 | 306.4234 | 301.6742 | 308.3757
4618.5979 | 614.6729 | 306.4052 | 301.4091 | 308.2102
4619.5979 | 614.9725 | 306.4487 | 301.2612 | 307.8894
4620.5979 | 614.9746 | 306.2984 | 301.1886 | 307.8103
4621.5979 | 615.0815 | 306.1476 | 301.298 | 307.7171
4622.5979 | 615.2509 | 306.1313 | 301.1693 | 307.6599
4623.5979 | 615.1634 | 306.0623 | 300.982 | 307.4559
4624.5979 | 614.2619 | 305.8266 | 300.8552 | 307.2898
4625.5979 | 612.8151 | 305.7658 | 300.8306 | 307.2652
4626.5979 | 611.8559 | 305.5896 | 300.852 | 307.2822
4627.5979 | 611.5725 | 305.6584 | 300.9325 | 307.3169
4628.5979 | 611.6761 | 305.7105 | 300.9877 | 307.3487
4629.5979 | 611.8037 | 305.6381 | 300.8409 | 307.2936
4630.5979 | 611.8373 | 305.6067 | 300.6833 | 307.1096
4631.5979 | 611.7685 | 305.6114 | 300.5162 | 306.8445
4632.5979 | 611.6951 | 305.5745 | 300.4105 | 306.7543
4633.5979 | 611.3425 | 305.5152 | 300.3219 | 306.6546
4634.5979 | 611.6189 | 305.3565 | 300.2299 | 306.6057
4635.5979 | 611.5875 | 305.3648 | 300.1173 | 306.4994
4636.5979 | 611.5706 | 305.3478 | 300.1535 | 306.6257
4637.5979 | 611.6618 | 305.3255 | 300.1298 | 306.6996
4638.5979 | 611.8285 | 305.1354 | 300.2254 | 306.7959
4639.5979 | 610.996 | 304.9354 | 300.4548 | 306.8955
4640.5979 | 610.7146 | 304.8607 | 300.5859 | 307.0402
4641.5979 | 610.4741 | 304.8659 | 300.6456 | 307.1028
4642.5979 | 610.3108 | 305.1013 | 300.5448 | 307.1752
4643.5979 | 610.2112 | 305.2577 | 300.8631 | 307.3797
4644.5979 | 610.2401 | 305.4194 | 301.2664 | 307.6786
4645.5979 | 610.1178 | 305.5843 | 301.5619 | 307.9819
4646.5979 | 610.1091 | 305.7012 | 301.7258 | 308.0985
4647.5979 | 609.4079 | 305.8489 | 301.8679 | 308.1945
4648.5979 | 608.8124 | 305.7568 | 301.8597 | 308.293
4649.5979 | 608.627 | 305.5961 | 301.7933 | 308.3006
4650.5979 | 608.7634 | 305.4149 | 301.5838 | 308.2198
4651.5979 | 608.7246 | 305.1864 | 301.376 | 308.0926
4652.5979 | 608.803 | 305.0517 | 301.1234 | 308.011
4653.5979 | 608.9553 | 304.9358 | 300.9853 | 307.8672
4654.5979 | 609.134 | 304.7769 | 300.8779 | 307.6568
4655.5979 | 609.1864 | 304.6603 | 300.79 | 307.4655
4656.5979 | 608.9587 | 304.6588 | 300.6724 | 307.3648
4657.5979 | 608.5773 | 304.6527 | 300.685 | 307.4344
4658.5979 | 607.9358 | 304.5001 | 300.5727 | 307.5631
4659.5979 | 608.2668 | 304.364 | 300.6566 | 307.5079
4660.5979 | 607.8398 | 304.2925 | 300.6376 | 307.4243
4661.5979 | 607.6134 | 304.1548 | 300.7299 | 307.3748
4662.5979 | 607.0163 | 304.0479 | 300.7299 | 307.3642
4663.5979 | 606.7069 | 304.1249 | 300.5619 | 307.2111
4664.5979 | 606.9599 | 304.077 | 300.4676 | 307.0472
4665.5979 | 607.5819 | 304.1152 | 300.4001 | 306.912
4666.5979 | 607.7781 | 304.0189 | 300.2955 | 306.6627
4667.5979 | 608.614 | 304.0775 | 300.1655 | 306.4943
4668.5979 | 609.3615 | 304.0445 | 300.0364 | 306.2319
4669.5979 | 609.89 | 304.0254 | 299.7217 | 306.052
4670.5979 | 609.801 | 303.9764 | 299.4109 | 305.8685
4671.5979 | 609.8898 | 303.8789 | 299.0887 | 305.7926
4672.5979 | 609.4212 | 303.7865 | 299.0602 | 305.7609
4673.5979 | 609.0433 | 303.7836 | 298.8985 | 305.7166
4674.5979 | 609.6398 | 303.7556 | 298.8159 | 305.522
4675.5979 | 609.6847 | 303.691 | 298.6228 | 305.352
4676.5979 | 609.5806 | 303.6959 | 298.3031 | 305.1872
4677.5979 | 609.5979 | 303.7061 | 298.1541 | 305.0724
4678.5979 | 609.4624 | 303.4783 | 297.9341 | 305.0472
4679.5979 | 609.4021 | 303.1877 | 297.6373 | 304.8888
4680.5979 | 609.7993 | 302.9316 | 297.3087 | 304.5525
4681.5979 | 610.1115 | 302.7659 | 296.966 | 304.4229
4682.5979 | 610.2052 | 302.523 | 296.7511 | 304.3587
4683.5979 | 610.0301 | 302.3982 | 296.636 | 304.2728
4684.5979 | 609.5852 | 302.1765 | 296.6778 | 304.1532
4685.5979 | 609.6556 | 302.1424 | 296.5971 | 304.0821
4686.5979 | 609.6682 | 302.1235 | 296.6712 | 303.935
4687.5979 | 609.5716 | 302.1446 | 296.6609 | 303.9026
4688.5979 | 609.8102 | 302.0858 | 296.5989 | 303.7796
4689.5979 | 609.7276 | 301.9931 | 296.5546 | 303.5874
4690.5979 | 609.7261 | 301.9472 | 296.4686 | 303.4346
4691.5979 | 609.8098 | 301.9556 | 296.2664 | 303.1944
4692.5979 | 610.0701 | 301.9718 | 296.0958 | 303.2253
4693.5979 | 610.2338 | 301.9086 | 296.0586 | 303.0977
4694.5979 | 610.2844 | 301.8892 | 295.9315 | 302.9734
4695.5979 | 610.3055 | 301.7226 | 295.8024 | 303.0631
4696.5979 | 609.9166 | 301.5393 | 295.742 | 303.1081
4697.5979 | 609.3074 | 301.5101 | 295.6738 | 303.0109
4698.5979 | 608.5654 | 301.4909 | 295.7497 | 302.9239
4699.5979 | 608.3039 | 301.3056 | 295.7831 | 302.8855
4700.5979 | 608.1215 | 301.2349 | 295.8143 | 302.8316
4701.5979 | 607.9817 | 301.1568 | 295.9569 | 302.7726
4702.5979 | 607.4603 | 301.1253 | 296.0233 | 302.7995
4703.5979 | 606.7629 | 300.9782 | 296.0153 | 302.7632
4704.5979 | 606.7477 | 300.867 | 296.0105 | 302.7242
4705.5979 | 606.6129 | 300.5179 | 295.9945 | 302.7666
4706.5979 | 606.7693 | 300.38 | 295.9491 | 302.622
4707.5979 | 606.5781 | 300.3281 | 295.9221 | 302.5864
4708.5979 | 606.4475 | 300.1357 | 295.9305 | 302.7076
4709.5979 | 606.849 | 299.9299 | 295.8719 | 302.6663
4710.5979 | 607.305 | 299.8544 | 295.7295 | 302.589
4711.5979 | 607.5114 | 299.7768 | 295.8307 | 302.339
4712.5979 | 607.4526 | 299.872 | 295.8482 | 302.4525
4713.5979 | 607.352 | 299.8267 | 295.6907 | 302.3067
4714.5979 | 607.0569 | 299.8378 | 295.6509 | 302.293
4715.5979 | 606.6479 | 299.9044 | 295.5787 | 302.0699
4716.5979 | 606.5502 | 299.7972 | 295.5296 | 301.9305
4717.5979 | 606.444 | 299.7042 | 295.4805 | 301.6665
4718.5979 | 606.2136 | 299.5113 | 295.3668 | 301.3954
4719.5979 | 606.305 | 299.355 | 295.1347 | 301.0873
4720.5979 | 606.2706 | 299.149 | 294.8734 | 300.8924
4721.5979 | 606.2342 | 299.0754 | 294.3615 | 300.7967
4722.5979 | 606.3722 | 299.1428 | 294.123 | 300.8443
4723.5979 | 606.707 | 299.113 | 294.0217 | 300.7727
4724.5979 | 606.3333 | 299.1003 | 293.8339 | 300.6167
4725.5979 | 606.0562 | 299.1292 | 293.7098 | 300.451
4726.5979 | 605.6561 | 299.1288 | 293.6435 | 300.5932
4727.5979 | 605.571 | 299.1703 | 293.4943 | 300.5192
4728.5979 | 605.7179 | 299.1383 | 293.4657 | 300.397
4729.5979 | 605.4192 | 299.029 | 293.396 | 300.46
4730.5979 | 605.4229 | 299.1101 | 293.4246 | 300.4257
4731.5979 | 605.5912 | 299.1313 | 293.8048 | 300.4802
4732.5979 | 605.3287 | 299.3161 | 294.124 | 300.6466
4733.5979 | 605.1259 | 299.4247 | 294.2356 | 300.8242
4734.5979 | 604.9316 | 299.3141 | 294.1584 | 300.8383
4735.5979 | 604.1595 | 299.36 | 294.2739 | 300.7153
4736.5979 | 603.5306 | 299.3464 | 294.1553 | 300.5755
4737.5979 | 603.228 | 299.3182 | 294.0063 | 300.4823
4738.5979 | 603.0056 | 299.3191 | 293.9934 | 300.2058
4739.5979 | 602.9855 | 299.1812 | 293.9227 | 300.0856
4740.5979 | 603.1528 | 299.026 | 293.7392 | 299.849
4741.5979 | 603.3246 | 298.9986 | 293.6253 | 299.6257
4742.5979 | 603.1999 | 298.9441 | 293.4719 | 299.5899
4743.5979 | 602.771 | 298.9055 | 293.3129 | 299.4967
4744.5979 | 602.3699 | 298.8717 | 293.2203 | 299.3971
4745.5979 | 601.7607 | 298.7757 | 293.2207 | 299.3948
4746.5979 | 601.766 | 298.7284 | 293.1936 | 299.3698
4747.5979 | 601.8976 | 298.6909 | 293.0695 | 299.309
4748.5979 | 601.9827 | 298.6366 | 292.9105 | 299.1067
4749.5979 | 601.6689 | 298.6199 | 292.6626 | 298.9835
4750.5979 | 601.5624 | 298.5691 | 292.5572 | 298.7982
4751.5979 | 601.2036 | 298.3255 | 292.5204 | 298.7274
4752.5979 | 600.7244 | 298.1075 | 292.4528 | 298.729
4753.5979 | 600.5335 | 297.7755 | 292.4368 | 298.802
4754.5979 | 600.7322 | 297.5901 | 292.418 | 298.8422
4755.5979 | 601.0246 | 297.3592 | 292.3965 | 298.8136
4756.5979 | 600.9275 | 297.1428 | 292.5141 | 298.8433
4757.5979 | 600.9377 | 297.1395 | 292.5744 | 298.7744
4758.5979 | 600.5164 | 297.0722 | 292.5543 | 298.81
4759.5979 | 600.2587 | 297.0972 | 292.8476 | 298.9806
4760.5979 | 599.8866 | 297.1349 | 293.1244 | 299.0979
4761.5979 | 599.5968 | 297.0652 | 293.247 | 299.2411
4762.5979 | 599.4708 | 297.12 | 293.3653 | 299.3711
4763.5979 | 599.4816 | 297.1205 | 293.4236 | 299.431
4764.5979 | 599.3796 | 297.2249 | 293.4814 | 299.5022
4765.5979 | 599.1708 | 297.1484 | 293.6375 | 299.4495
4766.5979 | 598.9195 | 297.1342 | 293.6181 | 299.6551
4767.5979 | 598.8869 | 297.007 | 293.5002 | 299.7162
4768.5979 | 599.3769 | 297.0324 | 293.4163 | 299.7544
4769.5979 | 599.3287 | 297.0429 | 293.3594 | 299.4359
4770.5979 | 599.0356 | 296.9854 | 293.284 | 299.2313
4771.5979 | 598.8001 | 296.9725 | 293.243 | 299.3476
4772.5979 | 598.5697 | 296.9754 | 293.1526 | 299.2975
4773.5979 | 598.4856 | 296.9685 | 293.1731 | 299.2453
4774.5979 | 598.6096 | 297.0111 | 293.2814 | 299.3443
4775.5979 | 598.8058 | 297.1349 | 293.4358 | 299.5442
4776.5979 | 599.1549 | 297.2257 | 293.5221 | 299.6363
4777.5979 | 599.3764 | 297.3212 | 293.5364 | 299.6568
4778.5979 | 599.4497 | 297.3453 | 293.2906 | 299.6176
4779.5979 | 599.4127 | 297.3223 | 293.2048 | 299.5274
4780.5979 | 599.3508 | 297.2259 | 293.1556 | 299.4253
4781.5979 | 599.0617 | 296.8937 | 293 | 299.1602
4782.6135 | 598.2479 | 296.4501 | 292.773 | 298.951
4783.5979 | 598.1137 | 296.0929 | 292.5396 | 298.8252
4784.5979 | 598.1204 | 295.8576 | 292.4315 | 298.7599
4785.5979 | 598.0675 | 295.9029 | 292.3681 | 298.6816
4786.5979 | 598.0849 | 295.6589 | 292.3191 | 298.5195
4787.5979 | 597.8675 | 295.6052 | 292.2108 | 298.2636
4788.5979 | 598.1437 | 295.4851 | 291.9897 | 298.1231
4789.5979 | 598.3153 | 295.3053 | 291.9284 | 297.9793
4790.5979 | 598.679 | 295.249 | 291.7837 | 297.7147
4791.5979 | 599.0114 | 295.2135 | 291.5563 | 297.4524
4792.5979 | 599.3521 | 295.1461 | 291.5734 | 297.3555
4793.5979 | 599.1397 | 295.1071 | 291.4295 | 297.2056
4794.5979 | 599.434 | 295.1274 | 291.3848 | 297.0829
4795.6135 | 599.263 | 295.1709 | 291.2697 | 296.9044
4796.5979 | 599.2146 | 295.1702 | 291.1684 | 296.7774
4797.5979 | 599.725 | 295.234 | 291.1079 | 296.7804
4798.5979 | 599.6738 | 295.2671 | 290.9925 | 296.7209
4799.5979 | 599.8153 | 295.2012 | 290.8476 | 296.5993
4800.5979 | 599.3697 | 295.174 | 290.7824 | 296.4401
4801.5979 | 599.5345 | 294.8794 | 290.6991 | 296.348
4802.5979 | 600.1176 | 294.8322 | 290.7054 | 296.2053
4803.5979 | 600.0069 | 294.6862 | 290.5494 | 296.0855
4804.5979 | 599.8499 | 294.672 | 290.4797 | 295.8859
4805.6135 | 599.7033 | 294.6621 | 290.1585 | 295.8398
4806.5979 | 599.9207 | 294.5937 | 290.0501 | 295.8435
4807.5979 | 600.0467 | 294.481 | 289.9268 | 295.7905
4808.5979 | 599.8687 | 294.4165 | 289.8357 | 295.6995
4809.5979 | 600.1022 | 294.4089 | 289.7097 | 295.4884
4810.5979 | 600.3562 | 294.42 | 289.6798 | 295.3215
4811.5979 | 600.1892 | 294.4133 | 289.5054 | 295.2628
4812.5979 | 600.1549 | 294.4313 | 289.2715 | 295.0871
4813.5979 | 600.2959 | 294.4114 | 289.0242 | 294.8683
4814.5979 | 600.0374 | 294.3429 | 288.8937 | 294.6629
4815.5979 | 599.6645 | 294.2107 | 288.729 | 294.5196
4816.5979 | 599.249 | 294.1546 | 288.5192 | 294.4322
4817.5979 | 598.3112 | 294.1077 | 288.0922 | 294.3039
4818.5979 | 598.1222 | 294.0649 | 287.7937 | 294.1421
4819.5979 | 597.337 | 293.9372 | 287.6981 | 294.1543
4820.5979 | 596.8464 | 293.8904 | 287.6352 | 294.1732
4821.5979 | 596.5511 | 293.9151 | 287.6271 | 294.0667
4822.5979 | 596.2591 | 293.8281 | 287.6151 | 293.9539
4823.5979 | 596.1905 | 293.8793 | 287.707 | 293.8831
4824.5979 | 596.6654 | 293.8512 | 287.9483 | 293.7872
4825.5979 | 597.2855 | 293.8711 | 287.9198 | 293.6975
4826.5979 | 596.8907 | 293.9247 | 287.8899 | 293.6745
4827.5979 | 596.7457 | 293.936 | 287.9274 | 293.4655
4828.5979 | 596.5962 | 293.9174 | 287.9644 | 293.5525
4829.5979 | 596.2241 | 293.8692 | 287.892 | 293.565
4830.5979 | 595.7986 | 293.8301 | 287.7826 | 293.5172
4831.5979 | 594.6847 | 293.7634 | 287.6022 | 293.3163
4832.5979 | 594.5511 | 293.5555 | 287.565 | 293.3444
4833.5979 | 594.8035 | 293.4085 | 287.526 | 293.3923
4834.5979 | 594.883 | 293.3713 | 287.4991 | 293.4347
4835.5979 | 595.2764 | 293.264 | 287.4336 | 293.5328
4836.5979 | 595.3825 | 293.1451 | 287.3179 | 293.4231
4837.5979 | 595.3865 | 293.123 | 287.3611 | 293.3135
4838.5979 | 595.5199 | 292.9665 | 287.3824 | 293.3076
4839.5979 | 594.8983 | 292.9664 | 287.3707 | 293.1297
4840.5979 | 594.063 | 292.9834 | 287.3617 | 292.9916
4841.5979 | 593.8158 | 293.0066 | 287.3928 | 292.9071
4842.5979 | 593.7283 | 293.0263 | 287.3534 | 292.9523
4843.5979 | 593.7465 | 293.1181 | 287.3124 | 292.8893
4844.5979 | 593.6694 | 293.0983 | 287.2514 | 292.787
4845.5979 | 593.7078 | 293.0742 | 287.1967 | 292.6785
4846.5979 | 593.3735 | 293.0409 | 287.0373 | 292.5839
4847.5979 | 593.1306 | 292.9239 | 286.8447 | 292.5789
4848.5979 | 593.0675 | 292.8004 | 286.8425 | 292.4386
4849.5979 | 593.0239 | 292.7688 | 286.5158 | 292.2538
4850.5979 | 593.0907 | 292.7748 | 286.2852 | 291.8344
4851.5979 | 593.2325 | 292.6306 | 286.1497 | 291.7258
4852.5979 | 593.664 | 292.571 | 285.9955 | 291.7253
4853.5979 | 593.5127 | 292.4353 | 285.8178 | 291.6192
4854.5979 | 593.3829 | 292.2832 | 285.5907 | 291.4747
4855.5979 | 593.4062 | 292.2451 | 285.3709 | 291.3586
4856.5979 | 593.6024 | 292.2391 | 285.2214 | 291.2711
4857.5979 | 593.8132 | 292.0161 | 285.1009 | 291.2699
4858.5979 | 593.9659 | 291.6259 | 284.9085 | 291.2323
4859.5979 | 593.6595 | 291.5178 | 284.8362 | 291.4323
4860.5979 | 593.1879 | 291.3988 | 284.8296 | 291.4788
4861.5979 | 592.4802 | 291.2743 | 285.061 | 291.4986
4862.5979 | 592.4773 | 291.108 | 285.1976 | 291.5556
4863.5979 | 591.8008 | 290.9638 | 285.1544 | 291.5847
4864.5979 | 591.7722 | 290.8834 | 285.1239 | 291.5668
4865.5979 | 591.6697 | 290.7676 | 285.0192 | 291.4636
4866.5979 | 592.2869 | 290.7307 | 285.0909 | 291.2787
4867.5979 | 592.521 | 290.7218 | 285.2182 | 291.2285
4868.5979 | 592.4683 | 290.6975 | 285.3441 | 291.2628
4869.5979 | 592.6411 | 290.7892 | 285.4652 | 291.3078
4870.5979 | 592.4615 | 290.5926 | 285.4862 | 291.1979
4871.5979 | 592.4157 | 290.2639 | 285.2395 | 291.0944
4872.5979 | 592.3386 | 290.1899 | 285.0812 | 290.9572
4873.5979 | 592.1824 | 290.1982 | 284.8946 | 291.0439
4874.5979 | 592.4289 | 290.1478 | 284.6199 | 291.0962
4875.5979 | 592.4488 | 289.9339 | 284.4707 | 290.982
4876.5979 | 591.957 | 289.7152 | 284.6826 | 290.9423
4877.5979 | 591.1557 | 289.6219 | 284.6152 | 290.8578
4878.5979 | 590.3495 | 289.5672 | 284.6802 | 290.7828
4879.5979 | 589.7635 | 289.4408 | 284.6747 | 290.7111
4880.5979 | 589.3204 | 289.2692 | 284.5294 | 290.6736
4881.5979 | 589.3165 | 289.2735 | 284.5277 | 290.6322
4882.5979 | 589.0892 | 289.2564 | 284.5483 | 290.6207
4883.5979 | 588.8218 | 289.1315 | 284.6118 | 290.6192
4884.5979 | 588.3558 | 288.9751 | 284.4096 | 290.6322
4885.5979 | 588.4424 | 288.7857 | 284.3875 | 290.5552
4886.5979 | 588.0169 | 288.7869 | 284.5053 | 290.674
4887.5979 | 588.015 | 288.712 | 284.4755 | 290.7465
4888.5979 | 587.8938 | 288.7602 | 284.4579 | 290.5224
4889.5979 | 587.7207 | 288.7859 | 284.4902 | 290.3579
4890.5979 | 587.4852 | 288.5882 | 284.3814 | 290.2726
4891.5979 | 587.5582 | 288.6015 | 284.3008 | 290.2917
4892.5979 | 587.5767 | 288.6648 | 284.4528 | 290.2157
4893.5979 | 587.5121 | 288.71 | 284.5307 | 290.141
4894.5979 | 587.4234 | 288.7393 | 284.4532 | 290.0843
4895.5979 | 586.9555 | 288.5831 | 284.1767 | 289.91
4896.5979 | 586.618 | 288.4332 | 283.9459 | 289.831
4897.5979 | 585.9985 | 288.3002 | 283.7044 | 289.7555
4898.5979 | 585.832 | 288.2822 | 283.6207 | 289.6022
4899.5979 | 586.2366 | 288.2581 | 283.4729 | 289.4597
4900.5979 | 586.2455 | 288.3785 | 283.3842 | 289.3809
4901.5979 | 586.1874 | 288.2725 | 283.3499 | 289.4401
4902.5979 | 585.3837 | 288.2406 | 283.2705 | 289.3514
4903.5979 | 585.171 | 288.1828 | 283.1978 | 289.1041
4904.5979 | 585.3554 | 288.2518 | 283.2434 | 289.0284
4905.5979 | 585.8258 | 288.2737 | 283.1311 | 288.8879
4906.5979 | 586.1934 | 288.2307 | 283.0015 | 288.9141
4907.5979 | 586.0203 | 288.1028 | 283.126 | 288.9276
4908.5979 | 586.1868 | 288.047 | 283.1661 | 288.9339
4909.5979 | 586.1311 | 288.0058 | 283.2786 | 288.9591
4910.5979 | 586.384 | 288.068 | 283.3495 | 289.0029
4911.5979 | 586.2298 | 288.1843 | 283.3518 | 289.013
4912.5979 | 586.5988 | 288.2642 | 283.4052 | 289.0178
4913.5979 | 586.7261 | 288.3896 | 283.3453 | 289.0308
4914.5979 | 586.9431 | 288.434 | 283.0299 | 288.8492
4915.5979 | 586.8908 | 288.3668 | 282.826 | 288.6856
4916.5979 | 586.7167 | 288.3601 | 282.6387 | 288.5016
4917.5979 | 586.6111 | 288.3369 | 282.4615 | 288.3686
4918.5979 | 586.513 | 288.322 | 282.3187 | 288.3066
4919.5979 | 586.3203 | 288.1638 | 282.1775 | 288.2862
4920.5979 | 585.9149 | 287.8887 | 282.22 | 288.128
4921.5979 | 585.8814 | 287.6761 | 282.1296 | 287.9804
4922.5979 | 585.7289 | 287.3861 | 282.0903 | 287.8334
4923.5979 | 585.2297 | 287.1611 | 282.0743 | 287.8347
4924.5979 | 584.5637 | 287.0387 | 281.9715 | 287.7656
4925.5979 | 584.2674 | 286.9062 | 281.9029 | 287.6539
4926.5979 | 584.3682 | 286.7709 | 281.8731 | 287.5602
4927.5979 | 584.4404 | 286.6621 | 281.6896 | 287.4555
4928.5979 | 584.469 | 286.5542 | 281.5222 | 287.4407
4929.5979 | 584.2464 | 286.4803 | 281.2126 | 287.3581
4930.5979 | 583.2642 | 286.3886 | 280.98 | 287.2338
4931.5979 | 582.5375 | 286.3806 | 280.9981 | 287.1966
4932.5979 | 582.3928 | 286.4032 | 280.9246 | 287.1975
4933.5979 | 582.661 | 286.3224 | 280.8437 | 287.0779
4934.5979 | 582.8326 | 286.267 | 280.7102 | 286.9255
4935.5979 | 582.4901 | 286.3591 | 280.5096 | 286.7874
4936.5979 | 582.2378 | 286.4626 | 280.4005 | 286.6959
4937.5979 | 582.0481 | 286.4236 | 280.4149 | 286.7454
4938.5979 | 581.707 | 286.2864 | 280.42 | 286.6553
4939.5979 | 581.6442 | 286.1301 | 280.3965 | 286.5983
4940.5979 | 581.5555 | 286.1534 | 280.4192 | 286.6274
4941.5979 | 581.8756 | 286.1287 | 280.0761 | 286.5884
4942.5979 | 582.1926 | 286.0052 | 279.8686 | 286.5161
4943.5979 | 582.5437 | 285.9018 | 279.7805 | 286.4351
4944.5979 | 582.1396 | 285.9052 | 279.5535 | 286.4201
4945.5979 | 581.9552 | 285.9264 | 279.4232 | 286.405
4946.5979 | 581.4686 | 285.9276 | 279.2338 | 286.1628
4947.5979 | 581.5662 | 285.9287 | 279.136 | 285.8565
4948.5979 | 581.366 | 285.7476 | 278.9496 | 285.8776
4949.5979 | 581.3112 | 285.6053 | 278.8574 | 285.7573
4950.5979 | 581.1135 | 285.4378 | 278.8684 | 285.7584
4951.5979 | 581.1187 | 285.3001 | 278.9164 | 285.6075
4952.5979 | 581.2101 | 285.2343 | 278.9405 | 285.6945
4953.5979 | 581.2482 | 285.2697 | 278.9723 | 285.6989
4954.5979 | 581.4476 | 285.239 | 279.0773 | 285.6291
4955.5979 | 581.5552 | 285.3151 | 279.1691 | 285.4378
4956.5979 | 581.5757 | 285.4156 | 279.1088 | 285.4197
4957.5979 | 581.4581 | 285.3141 | 278.9484 | 285.2886
4958.5979 | 581.0042 | 285.2315 | 278.7408 | 284.9192
4959.5979 | 580.5513 | 285.3186 | 278.7045 | 284.6807
4960.5979 | 579.9921 | 285.3098 | 278.7256 | 284.6601
4961.5979 | 579.6091 | 285.3089 | 278.6804 | 284.6018
4962.5979 | 579.5768 | 285.3567 | 278.48 | 284.4353
4963.5979 | 579.9804 | 285.4265 | 278.3377 | 284.4668
4964.5979 | 580.0697 | 285.4521 | 278.2107 | 284.5668
4965.5979 | 579.87 | 285.4843 | 278.2393 | 284.6074
4966.5979 | 579.8783 | 285.5252 | 278.3732 | 284.5262
4967.5979 | 579.6505 | 285.5191 | 278.5627 | 284.399
4968.5979 | 579.4381 | 285.5008 | 278.57 | 284.2342
4969.5979 | 579.2382 | 285.1701 | 278.2035 | 284.0679
4970.5979 | 579.4735 | 284.76 | 277.9288 | 284.0961
4971.5979 | 579.9918 | 284.3795 | 277.8781 | 284.0379
4972.5979 | 579.6119 | 284.3216 | 277.601 | 283.9666
4973.5979 | 578.9498 | 284.3523 | 277.3529 | 283.836
4974.5979 | 578.3077 | 284.269 | 277.0413 | 283.631
4975.5979 | 578.029 | 284.2077 | 276.9797 | 283.4345
4976.5979 | 578.1762 | 284.1806 | 276.958 | 283.5051
4977.5979 | 578.1079 | 284.241 | 277.1214 | 283.556
4978.5979 | 578.2394 | 284.2332 | 277.2719 | 283.4947
4979.5979 | 577.7624 | 284.2686 | 277.3197 | 283.361
4980.5979 | 577.334 | 284.2475 | 277.3108 | 283.2603
4981.5979 | 577.2012 | 284.2701 | 277.2614 | 283.0842
4982.5979 | 576.8922 | 284.1924 | 277.2151 | 282.9377
4983.5979 | 575.9297 | 284.0722 | 277.3168 | 282.8761
4984.5979 | 575.5393 | 284.1559 | 277.2425 | 282.7898
4985.5979 | 575.3663 | 284.0099 | 277.2263 | 282.8026
4986.5979 | 575.8399 | 284.0391 | 277.2092 | 282.8927
4987.5979 | 576.3116 | 283.9957 | 277.048 | 282.7174
4988.5979 | 576.5583 | 283.7785 | 276.7961 | 282.6027
4989.5979 | 576.6192 | 283.6809 | 276.6217 | 282.4947
4990.5979 | 576.4002 | 283.6478 | 276.512 | 282.4581
4991.5979 | 576.2511 | 283.6858 | 276.5658 | 282.478
4992.5979 | 576.2317 | 283.619 | 276.6874 | 282.423
4993.5979 | 576.4217 | 283.6339 | 276.6737 | 282.4005
4994.5979 | 576.4345 | 283.5822 | 276.6245 | 282.3125
4995.5979 | 576.3694 | 283.5378 | 276.7174 | 282.2057
4996.5979 | 576.4242 | 283.2989 | 276.7983 | 282.3057
4997.5979 | 575.7769 | 283.0255 | 276.8138 | 282.4177
4998.5979 | 575.5035 | 282.9161 | 276.936 | 282.5503
4999.5979 | 575.3555 | 282.8159 | 277.0457 | 282.5961
5000.5979 | 575.096 | 282.7572 | 277.1327 | 282.5635
5001.5979 | 574.76 | 282.831 | 277.3216 | 282.683
5002.5979 | 574.7342 | 282.8402 | 277.4512 | 282.9137
5003.5979 | 574.9243 | 282.7357 | 277.5467 | 282.9732
5004.5979 | 574.8855 | 282.7652 | 277.6291 | 282.9256
5005.5979 | 574.85 | 282.6471 | 277.6849 | 282.8522
5006.5979 | 574.4163 | 282.6436 | 277.6675 | 282.8429
5007.5979 | 574.3895 | 282.6881 | 277.6356 | 282.8474
5008.5979 | 574.3276 | 282.4546 | 277.4577 | 282.749
5009.5979 | 574.4771 | 282.3626 | 277.0004 | 282.6769
5010.5979 | 574.7967 | 282.3178 | 276.7747 | 282.5606
5011.5979 | 574.7573 | 282.2228 | 276.6683 | 282.3204
5012.5979 | 574.5789 | 282.1221 | 276.5674 | 282.121
5013.5979 | 574.2661 | 282.023 | 276.3294 | 282.0185
5014.5979 | 573.9797 | 281.8872 | 276.1872 | 282.0096
5015.5979 | 573.7295 | 281.6699 | 276.1836 | 282.0287
5016.5979 | 573.4294 | 281.5807 | 276.1183 | 281.9916
5017.5979 | 573.1381 | 281.4326 | 276.1318 | 281.9492
5018.5979 | 572.8845 | 281.4058 | 276.1321 | 281.8983
5019.5979 | 572.6295 | 281.3098 | 276.0753 | 281.9014
5020.5979 | 572.378 | 281.1916 | 275.9687 | 281.7338
5021.5979 | 572.2872 | 280.9653 | 275.6739 | 281.6411
5022.5979 | 572.1688 | 280.8831 | 275.4705 | 281.435
5023.5979 | 572.083 | 280.8601 | 275.3971 | 281.4208
5024.5979 | 572.0353 | 280.7363 | 275.3245 | 281.4213
5025.5979 | 572.1946 | 280.6704 | 275.3703 | 281.3878
5026.5979 | 572.2714 | 280.6867 | 275.2279 | 281.233
5027.5979 | 572.0322 | 280.6587 | 275.1528 | 281.0663
5028.5979 | 572.0772 | 280.7217 | 275.1269 | 280.9719
5029.5979 | 571.9336 | 280.6175 | 275.218 | 280.8935
5030.5979 | 571.9387 | 280.4643 | 275.1228 | 280.8027
5031.5979 | 571.7629 | 280.3772 | 275.0434 | 280.7445
5032.5979 | 571.3447 | 280.275 | 274.9178 | 280.6904
5033.5979 | 571.1066 | 280.1013 | 274.5872 | 280.6336
5034.5979 | 570.7996 | 279.8362 | 274.3963 | 280.4917
5035.5979 | 570.5471 | 279.8451 | 274.1552 | 280.2534
5036.5979 | 570.2454 | 279.8516 | 274.0884 | 280.193
5037.5979 | 569.9983 | 279.8433 | 273.9322 | 280.2026
5038.5979 | 569.7763 | 279.8049 | 273.7869 | 280.1111
5039.5979 | 569.3823 | 279.697 | 273.8424 | 279.976
5040.5979 | 568.9537 | 279.7471 | 273.69 | 279.908
5041.5979 | 569.3735 | 279.522 | 273.5963 | 279.7957
5042.5979 | 569.3566 | 279.4985 | 273.4661 | 279.7087
5043.5979 | 569.2752 | 279.3762 | 273.5107 | 279.8688
5044.5979 | 569.006 | 279.4437 | 273.4444 | 279.9336
5045.5979 | 568.467 | 279.554 | 273.4349 | 279.8965
5046.5979 | 568.3104 | 279.6704 | 273.3995 | 279.8732
5047.5979 | 568.2037 | 279.8187 | 273.5085 | 279.7735
5048.5979 | 567.1993 | 279.7672 | 273.6584 | 279.6807
5049.5979 | 566.8847 | 279.8148 | 273.86 | 279.7302
5050.5979 | 566.909 | 279.7355 | 274.0201 | 279.8742
5051.5979 | 567.2697 | 279.6486 | 274.0251 | 279.9091
5052.5979 | 567.2043 | 279.6964 | 274.0088 | 279.9433
5053.5979 | 567.1519 | 279.6775 | 273.8755 | 279.9053
5054.5979 | 567.204 | 279.6493 | 273.6721 | 279.7546
5055.5979 | 567.4781 | 279.6734 | 273.6344 | 279.565
5056.5979 | 567.4782 | 279.7195 | 273.608 | 279.4657
5057.5979 | 567.0946 | 279.7126 | 273.3737 | 279.3987
5058.5979 | 567.0806 | 279.76 | 273.2183 | 279.3196
5059.5979 | 566.5854 | 279.551 | 273.0683 | 279.1722
5060.5979 | 566.5478 | 279.4197 | 273.0892 | 279.0992
5061.5979 | 566.7512 | 279.251 | 273.055 | 279.1144
5062.5979 | 567.1542 | 279.2393 | 272.9322 | 279.1307
5063.5979 | 567.3151 | 279.1727 | 272.7851 | 279.041
5064.5979 | 567.0923 | 278.9685 | 272.7602 | 279.0077
5065.5979 | 566.9274 | 278.8813 | 272.7844 | 279.1131
5066.5979 | 566.282 | 278.9358 | 272.7537 | 279.1461
5067.5979 | 566.0492 | 278.9622 | 272.7128 | 279.1447
5068.5979 | 565.4966 | 279.0484 | 272.5239 | 279.1629
5069.5979 | 565.3264 | 278.9552 | 272.5287 | 279.0569
5070.5979 | 565.2945 | 278.7639 | 272.4959 | 279.0485
5071.5979 | 565.3843 | 278.6069 | 272.6158 | 278.9783
5072.5979 | 565.3224 | 278.4072 | 272.6355 | 278.725
5073.5979 | 565.0621 | 278.4397 | 272.6031 | 278.4954
5074.5979 | 564.678 | 278.3451 | 272.5826 | 278.3527
5075.5979 | 564.2179 | 278.2705 | 272.5494 | 278.1671
5076.5979 | 564.0691 | 278.3016 | 272.4795 | 278.1048
5077.5979 | 564.2507 | 278.3144 | 272.412 | 277.9931
5078.5979 | 564.2958 | 278.2933 | 272.3084 | 277.834
5079.5979 | 564.3269 | 278.1057 | 272.1164 | 277.6723
5080.5979 | 564.3733 | 277.9424 | 272.0617 | 277.5873
5081.5979 | 564.6012 | 277.9508 | 271.9662 | 277.3983
5082.5979 | 564.9119 | 277.9274 | 271.9881 | 277.274
5083.5979 | 565.225 | 277.8728 | 271.7942 | 277.1285
5084.5979 | 565.3873 | 277.844 | 271.7781 | 277.1082
5085.5979 | 565.1534 | 277.8183 | 271.6663 | 277.2272
5086.5979 | 565.2116 | 277.5184 | 271.3782 | 277.279
5087.5979 | 564.8007 | 277.4539 | 271.2223 | 277.2446
5088.5979 | 564.4639 | 277.4477 | 271.3594 | 277.2525
5089.5979 | 564.2184 | 277.4971 | 271.339 | 277.1698
5090.5979 | 564.1207 | 277.5843 | 271.3433 | 277.1476
5091.5979 | 564.1742 | 277.6257 | 271.1119 | 277.1038
5092.5979 | 564.1614 | 277.6331 | 270.9229 | 277.1182
5093.5979 | 564.3689 | 277.5631 | 270.6553 | 277.0428
5094.5979 | 564.2666 | 277.3442 | 270.5605 | 277.1339
5095.5979 | 563.9541 | 277.1763 | 270.6708 | 277.0687
5096.5979 | 563.3196 | 277.104 | 270.6476 | 277.0534
5097.5979 | 563.4204 | 277.0284 | 270.7641 | 277.0437
5098.5979 | 563.2146 | 276.8964 | 270.8268 | 277.0323
5099.5979 | 562.8264 | 276.8979 | 270.6781 | 277.0414
5100.5979 | 562.6357 | 276.716 | 270.5762 | 277.0833
5101.5979 | 562.6452 | 276.5926 | 270.5826 | 277.0463
5102.5979 | 562.5427 | 276.5425 | 270.6031 | 276.9506
5103.5979 | 562.4095 | 276.5805 | 270.7074 | 276.9677
5104.5979 | 562.1591 | 276.5429 | 270.7626 | 276.894
5105.5979 | 561.8427 | 276.4423 | 270.7203 | 276.8068
5106.5979 | 561.7977 | 276.4391 | 270.602 | 276.7189
5107.5979 | 561.8788 | 276.4682 | 270.616 | 276.6848
5108.5979 | 561.9548 | 276.5207 | 270.5315 | 276.5282
5109.5979 | 561.96 | 276.4681 | 270.3637 | 276.3679
5110.5979 | 561.7682 | 276.2147 | 270.1408 | 276.296
5111.5979 | 561.3548 | 276.1276 | 270.0979 | 276.2664
5112.5979 | 561.1883 | 276.123 | 270.061 | 276.1978
5113.5979 | 560.8253 | 275.9894 | 270.0482 | 276.1394
5114.5979 | 560.5552 | 275.9377 | 270.0931 | 275.9639
5115.5979 | 560.3607 | 275.8444 | 270.0459 | 275.8927
5116.5979 | 560.2911 | 275.769 | 269.915 | 275.8131
5117.5979 | 560.2529 | 275.7848 | 269.858 | 275.7314
5118.5979 | 560.3474 | 275.5727 | 269.6035 | 275.7269
5119.5979 | 560.1027 | 275.5705 | 269.522 | 275.6126
5120.5979 | 559.984 | 275.5964 | 269.5535 | 275.5856
5121.5979 | 559.878 | 275.427 | 269.3463 | 275.5522
5122.5979 | 560.0816 | 275.2333 | 269.0963 | 275.1811
5123.5979 | 559.8641 | 275.1105 | 269.2398 | 275.11
5124.5979 | 559.7082 | 274.8774 | 269.0933 | 274.9527
5125.5979 | 559.6763 | 274.8483 | 269.0993 | 274.7161
5126.5979 | 559.6011 | 274.8372 | 269.0039 | 274.6116
5127.5979 | 559.5752 | 274.7252 | 268.9356 | 274.5372
5128.5979 | 559.2107 | 274.7305 | 268.6301 | 274.5239
5129.5979 | 559.2241 | 274.7163 | 268.4938 | 274.5961
5130.5979 | 559.2202 | 274.7891 | 268.2571 | 274.5389
5131.5979 | 559.0375 | 274.6855 | 268.2379 | 274.4303
5132.5979 | 559.0189 | 274.3543 | 268.3384 | 274.3688
5133.5979 | 558.7266 | 274.0945 | 268.2073 | 274.3421
5134.5979 | 558.3344 | 274.0289 | 267.9355 | 274.277
5135.5979 | 557.8878 | 274.1574 | 267.9772 | 274.2889
5136.5979 | 557.6116 | 274.2342 | 267.9236 | 274.2758
5137.5979 | 557.5406 | 274.2689 | 267.7504 | 274.1877
5138.5979 | 556.9992 | 274.0757 | 267.659 | 274.062
5139.5979 | 556.8461 | 273.9127 | 267.7507 | 274.1019
5140.5979 | 556.6518 | 273.7376 | 267.8422 | 274.196
5141.5979 | 556.4983 | 273.5322 | 267.9388 | 274.1888
5142.5979 | 556.4009 | 273.4886 | 268.1583 | 274.1401
5143.5979 | 556.3442 | 273.5415 | 268.2048 | 274.1723
5144.5979 | 556.3069 | 273.6781 | 268.1788 | 274.2189
5145.5979 | 556.0048 | 273.7485 | 268.1397 | 274.1715
5146.5979 | 555.6362 | 273.7166 | 268.0455 | 273.9516
5147.5979 | 555.4314 | 273.5828 | 267.9467 | 273.8681
5148.5979 | 555.2981 | 273.6165 | 267.6638 | 273.6155
5149.5979 | 555.015 | 273.471 | 267.4697 | 273.5514
5150.5979 | 554.7722 | 273.53 | 267.283 | 273.5052
5151.5979 | 554.5307 | 273.3874 | 267.2217 | 273.5077
5152.5979 | 554.2635 | 273.1653 | 267.2038 | 273.3999
5153.5979 | 554.2128 | 273.2265 | 267.2511 | 273.2622
5154.5979 | 554.4572 | 273.2932 | 267.2996 | 273.1594
5155.5979 | 554.4752 | 273.2994 | 267.289 | 273.0703
5156.5979 | 554.7729 | 273.4081 | 267.1729 | 272.9732
5157.5979 | 554.8123 | 273.5139 | 267.0118 | 272.8096
5158.5979 | 554.5975 | 273.5482 | 267.0626 | 272.707
5159.5979 | 554.4988 | 273.4552 | 267.046 | 272.5281
5160.5979 | 554.4787 | 273.42 | 267.1094 | 272.5607
5161.5979 | 554.204 | 273.5345 | 267.1076 | 272.4854
5162.5979 | 553.9144 | 273.6119 | 267.1689 | 272.416
5163.5979 | 553.5152 | 273.6847 | 267.2037 | 272.3153
5164.5979 | 553.495 | 273.7126 | 267.2186 | 272.3418
5165.5979 | 553.6734 | 273.7372 | 267.2051 | 272.3806
5166.5979 | 553.6129 | 273.7122 | 267.1605 | 272.4277
5167.5979 | 553.3425 | 273.6741 | 267.1475 | 272.3986
5168.5979 | 553.3041 | 273.5539 | 267.124 | 272.4556
5169.5979 | 553.2549 | 273.5991 | 267.1674 | 272.4276
5170.5979 | 552.9738 | 273.7181 | 267.2074 | 272.3324
5171.5979 | 552.6185 | 273.7362 | 267.1653 | 272.1961
5172.5979 | 552.5291 | 273.7399 | 267.1254 | 271.9622
5173.5979 | 552.3297 | 273.7312 | 267.0744 | 271.8248
5174.5979 | 552.0845 | 273.6266 | 267.0432 | 271.7746
5175.5979 | 551.96 | 273.5047 | 267.1878 | 271.8741
5176.5979 | 551.8859 | 273.5466 | 267.211 | 271.9112
5177.5979 | 551.741 | 273.606 | 267.2298 | 271.9272
5178.5979 | 551.9696 | 273.5931 | 267.3062 | 271.8287
5179.5979 | 552.0741 | 273.6042 | 267.3644 | 271.8506
5180.5979 | 551.8107 | 273.4639 | 267.2608 | 271.8359
5181.5979 | 551.0854 | 273.3928 | 267.2205 | 271.6668
5182.5979 | 551.0237 | 273.3599 | 267.1046 | 271.576
5183.5979 | 551.0002 | 273.3515 | 266.9833 | 271.4883
5184.5979 | 550.8673 | 273.3254 | 266.8148 | 271.3835
5185.5979 | 550.8143 | 273.1949 | 266.7145 | 271.3295
5186.5979 | 550.6594 | 273.1697 | 266.638 | 271.3389
5187.5979 | 550.3279 | 273.1885 | 266.5893 | 271.3909
5188.5979 | 550.3006 | 273.1509 | 266.5944 | 271.3837
5189.5979 | 550.3025 | 273.2041 | 266.5423 | 271.4149
5190.5979 | 550.0476 | 273.2543 | 266.5335 | 271.3192
5191.5979 | 550.1796 | 273.3084 | 266.6695 | 271.4101
5192.5979 | 550.7805 | 273.36 | 266.7093 | 271.3594
5193.5979 | 551.1208 | 273.3801 | 266.6759 | 271.2403
5194.5979 | 551.6587 | 273.4072 | 266.8747 | 271.117
5195.5979 | 551.7778 | 273.3964 | 266.8599 | 271.0662
5196.5979 | 551.7805 | 273.2901 | 266.7733 | 270.9872
5197.5979 | 551.4627 | 273.1 | 266.6184 | 270.8064
5198.5979 | 550.9482 | 272.8768 | 266.5339 | 270.6227
5199.5979 | 550.6306 | 272.7116 | 266.5696 | 270.5486
5200.5979 | 550.5005 | 272.7536 | 266.4824 | 270.559
5201.5979 | 550.0387 | 272.7409 | 266.4497 | 270.5954
5202.5979 | 549.8183 | 272.7567 | 266.4714 | 270.4905
5203.5979 | 549.5585 | 272.7978 | 266.3955 | 270.4082
5204.5979 | 549.5045 | 272.5942 | 266.3865 | 270.3758
5205.5979 | 549.4349 | 272.398 | 266.1738 | 270.1882
5206.5979 | 549.37 | 272.1369 | 266.0046 | 270.0064
5207.5979 | 549.2137 | 271.9607 | 265.9996 | 269.841
5208.5979 | 548.9969 | 271.6851 | 265.957 | 269.7567
5209.5979 | 548.8121 | 271.0182 | 265.6857 | 269.8554
5210.5979 | 548.4179 | 270.8759 | 265.3636 | 269.7888
5211.5979 | 548.1296 | 270.7101 | 265.1208 | 269.7338
5212.5979 | 547.8871 | 270.5004 | 264.907 | 269.686
5213.5979 | 547.3652 | 270.3761 | 264.7991 | 269.7101
5214.5979 | 546.7634 | 270.1303 | 264.7524 | 269.7103
5215.5979 | 546.5428 | 270.0428 | 264.6886 | 269.7438
5216.5979 | 546.5063 | 270.104 | 264.676 | 269.7738
5217.5979 | 546.4996 | 270.1482 | 264.5849 | 269.7788
5218.5979 | 546.6599 | 270.1167 | 264.4866 | 269.7591
5219.5979 | 546.55 | 270.2243 | 264.3234 | 269.6385
5220.5979 | 546.5866 | 270.2239 | 264.155 | 269.4083
5221.5979 | 546.8472 | 270.3394 | 263.9207 | 269.3024
5222.5979 | 546.8585 | 270.3928 | 263.8933 | 269.1908
5223.5979 | 546.6197 | 270.445 | 263.7557 | 269.0932
5224.5979 | 546.2393 | 270.505 | 263.6441 | 269.0584
5225.5979 | 545.8728 | 270.3061 | 263.5104 | 268.9875
5226.5979 | 545.3882 | 270.0702 | 263.3006 | 268.9632
5227.5979 | 545.1631 | 269.9836 | 263.196 | 268.8839
5228.5979 | 544.6611 | 270.0023 | 263.2477 | 268.8815
5229.5979 | 544.3026 | 269.949 | 263.2947 | 268.8751
5230.5979 | 544.3667 | 269.8016 | 263.3061 | 268.8497
5231.5979 | 544.3298 | 269.8474 | 263.3124 | 268.7548
5232.5979 | 543.9776 | 269.8088 | 263.4097 | 268.7544
5233.5979 | 543.912 | 269.7116 | 263.3725 | 268.7815
5234.5979 | 543.5978 | 269.7163 | 263.3257 | 268.7341
5235.5979 | 543.0944 | 269.7313 | 263.3659 | 268.7247
5236.5979 | 542.6808 | 269.7401 | 263.2944 | 268.657
5237.5979 | 542.2949 | 269.6616 | 263.3213 | 268.6964
5238.5979 | 542.3184 | 269.5925 | 263.2234 | 268.6906
5239.5979 | 541.9579 | 269.5361 | 262.9907 | 268.6564
5240.5979 | 541.5768 | 269.4061 | 263.0229 | 268.6753
5241.5979 | 541.4835 | 269.2852 | 263.1335 | 268.6819
5242.5979 | 541.488 | 269.3308 | 263.0246 | 268.6998
5243.5979 | 541.1896 | 269.1212 | 263.08 | 268.8017
5244.5979 | 541.101 | 269.0442 | 263.0428 | 268.8448
5245.5979 | 540.8201 | 269.1273 | 263.033 | 268.842
5246.5979 | 540.6863 | 268.955 | 262.9836 | 268.7618
5247.5979 | 540.6614 | 268.736 | 263.0278 | 268.8047
5248.5979 | 540.6138 | 268.5846 | 263.0719 | 268.7952
5249.5979 | 540.5492 | 268.4558 | 263.1931 | 268.7209
5250.5979 | 540.4376 | 268.3605 | 263.3335 | 268.6381
5251.5979 | 540.5242 | 268.3095 | 263.3823 | 268.6714
5252.5979 | 540.6445 | 268.1821 | 263.3098 | 268.6244
5253.5979 | 540.6083 | 268.0262 | 263.3278 | 268.4811
5254.5979 | 540.4277 | 268.0412 | 263.3722 | 268.4284
5255.5979 | 540.4086 | 267.8875 | 263.4563 | 268.3922
5256.5979 | 540.273 | 267.7917 | 263.5013 | 268.3974
5257.5979 | 539.7319 | 267.8187 | 263.4513 | 268.2999
5258.5979 | 539.3461 | 268.038 | 263.3956 | 268.1673
5259.5979 | 539.0474 | 268.219 | 263.4526 | 268.1048
5260.5979 | 538.8518 | 268.3329 | 263.481 | 268.057
5261.5979 | 538.8569 | 268.3899 | 263.3446 | 268.0498
5262.5979 | 538.6956 | 268.4321 | 263.1691 | 268.0748
5263.5979 | 538.2266 | 268.4781 | 263.1891 | 268.092
5264.5979 | 538.1333 | 268.593 | 263.2821 | 268.0789
5265.5979 | 537.7567 | 268.7067 | 263.4075 | 268.1509
5266.5979 | 537.5028 | 268.822 | 263.5242 | 268.2007
5267.5979 | 537.3244 | 268.8976 | 263.6039 | 268.1616
5268.5979 | 537.021 | 268.9401 | 263.6551 | 268.2055
5269.5979 | 536.7887 | 269.0413 | 263.5946 | 268.1504
5270.5979 | 536.7923 | 268.9767 | 263.5573 | 268.0641
5271.5979 | 537.0567 | 269.0793 | 263.5459 | 267.9681
5272.5979 | 537.1862 | 269.0917 | 263.4404 | 267.8316
5273.5979 | 537.306 | 269.146 | 263.3071 | 267.7644
5274.5979 | 537.2382 | 269.1223 | 263.205 | 267.6303
5275.5979 | 537.3771 | 268.994 | 263.0451 | 267.6022
5276.5979 | 537.4961 | 268.9782 | 263.0383 | 267.4776
5277.5979 | 537.3396 | 268.9341 | 262.9335 | 267.3062
5278.5979 | 537.3298 | 268.9047 | 262.7258 | 267.2047
5279.5979 | 537.5289 | 268.888 | 262.7145 | 267.0684
5280.5979 | 537.6597 | 268.8553 | 262.6094 | 267.0454
5281.5979 | 537.6796 | 268.8662 | 262.6546 | 267.0216
5282.5979 | 537.7112 | 268.742 | 262.4529 | 266.8881
5283.5979 | 537.3621 | 268.6723 | 262.1835 | 266.8065
5284.5979 | 537.0896 | 268.3788 | 261.7107 | 266.7055
5285.5979 | 536.7418 | 268.1188 | 261.554 | 266.5051
5286.5979 | 537.1705 | 268.034 | 261.5057 | 266.5004
5287.5979 | 537.3831 | 267.9433 | 261.4234 | 266.362
5288.5979 | 537.3735 | 267.8707 | 261.3622 | 266.2134
5289.5979 | 537.2838 | 267.7423 | 261.3569 | 266.0397
5290.5979 | 537.0077 | 267.6624 | 261.1813 | 265.8984
5291.5979 | 536.7679 | 267.5866 | 261.1415 | 265.8449
5292.5979 | 536.5101 | 267.5215 | 261.1138 | 265.7631
5293.5979 | 536.2337 | 267.4869 | 261.106 | 265.5559
5294.5979 | 535.8589 | 267.4305 | 261.1385 | 265.4274
5295.5979 | 535.4558 | 267.4852 | 260.9651 | 265.4945
5296.5979 | 535.3862 | 267.4103 | 260.756 | 265.4647
5297.5979 | 535.3679 | 267.1371 | 260.8215 | 265.551
5298.5979 | 535.2202 | 266.9694 | 260.8091 | 265.5627
5299.5979 | 534.8727 | 266.8216 | 260.7021 | 265.5286
5300.5979 | 534.754 | 266.8099 | 260.616 | 265.4344
5301.5979 | 534.8027 | 266.8256 | 260.4971 | 265.4637
5302.5979 | 534.7566 | 266.884 | 260.4536 | 265.3296
5303.5979 | 535.0042 | 266.8913 | 260.4541 | 265.2414
5304.5979 | 535.3965 | 266.9598 | 260.4866 | 265.2421
5305.5979 | 535.4979 | 266.9754 | 260.3907 | 265.2018
5306.5979 | 535.7409 | 267.0254 | 260.3878 | 265.1115
5307.5979 | 536.4243 | 267.0298 | 260.3822 | 265.094
5308.5979 | 536.8081 | 266.9841 | 260.1629 | 265.0259
5309.5979 | 536.7096 | 266.9284 | 259.9602 | 264.9997
5310.5979 | 536.3084 | 266.8974 | 259.8186 | 264.9326
5311.5979 | 536.0855 | 266.8818 | 259.6946 | 264.7696
5312.5979 | 535.9283 | 266.906 | 259.7074 | 264.7223
5313.5979 | 535.5234 | 266.9191 | 259.5993 | 264.6664
5314.5979 | 535.1413 | 266.9133 | 259.5915 | 264.593
5315.5979 | 534.922 | 266.908 | 259.7556 | 264.5636
5316.5979 | 534.7934 | 266.7724 | 259.6342 | 264.5834
5317.5979 | 534.7286 | 266.5606 | 259.6172 | 264.4855
5318.5979 | 534.6102 | 266.3466 | 259.3867 | 264.4457
5319.5979 | 534.5013 | 266.1714 | 259.2105 | 264.5298
5320.5979 | 534.2802 | 265.8186 | 259.0494 | 264.456
5321.5979 | 534.1083 | 265.6682 | 258.8466 | 264.2783
5322.5979 | 533.8519 | 265.4279 | 258.8073 | 264.1819
5323.5979 | 533.4925 | 265.1646 | 258.6771 | 263.9596
5324.5979 | 533.5203 | 265.19 | 258.5726 | 263.8155
5325.5979 | 533.3748 | 265.2674 | 258.4278 | 263.8603
5326.5979 | 533.4333 | 265.2405 | 258.3296 | 263.8879
5327.5979 | 533.2811 | 265.2858 | 258.2695 | 263.8436
5328.5979 | 533.3352 | 265.2996 | 258.2407 | 263.8317
5329.5979 | 533.0474 | 265.3157 | 258.1024 | 263.79
5330.5979 | 532.9553 | 265.403 | 257.8438 | 263.8508
5331.5979 | 532.6153 | 265.4296 | 257.7815 | 263.7536
5332.5979 | 532.2193 | 265.4653 | 257.8676 | 263.7312
5333.5979 | 532.1783 | 265.4061 | 257.9225 | 263.7555
5334.5979 | 532.1783 | 265.3274 | 257.8975 | 263.6937
5335.5979 | 532.1706 | 265.2586 | 257.8722 | 263.6416
5336.5979 | 532.1138 | 265.2705 | 257.8308 | 263.6092
5337.5979 | 532.0036 | 265.0971 | 257.9175 | 263.5898
5338.5979 | 531.8986 | 264.7262 | 257.7406 | 263.525
5339.5979 | 531.6613 | 264.5447 | 257.7056 | 263.4423
5340.5979 | 530.9817 | 264.5419 | 257.783 | 263.4162
5341.5979 | 530.8217 | 264.6441 | 257.9547 | 263.4191
5342.5979 | 530.6562 | 264.5887 | 258.0199 | 263.4625
5343.5979 | 530.7988 | 264.4997 | 258.162 | 263.4987
5344.5979 | 531.1673 | 264.3751 | 258.3346 | 263.4372
5345.5979 | 531.0941 | 264.287 | 258.3687 | 263.4456
5346.5979 | 530.9948 | 264.379 | 258.46 | 263.4539
5347.5979 | 530.591 | 264.4777 | 258.4045 | 263.5088
5348.5979 | 530.4198 | 264.558 | 258.3803 | 263.485
5349.5979 | 530.6674 | 264.6255 | 258.1952 | 263.4289
5350.5979 | 530.8933 | 264.673 | 257.9764 | 263.3923
5351.5979 | 530.7274 | 264.7446 | 257.9084 | 263.4077
5352.5979 | 530.6182 | 264.7178 | 257.7584 | 263.4035
5353.5979 | 530.5497 | 264.6291 | 257.4786 | 263.3021
5354.5979 | 530.6604 | 264.4434 | 257.3317 | 263.2324
5355.5979 | 530.3432 | 264.2981 | 257.3318 | 263.2115
5356.5979 | 530.3774 | 264.1185 | 257.3492 | 263.1543
5357.5979 | 530.5288 | 264.0332 | 257.4021 | 262.9353
5358.5979 | 530.701 | 264.1116 | 257.444 | 262.8122
5359.5979 | 530.8157 | 264.1422 | 257.4104 | 262.7494
5360.5979 | 530.4629 | 264.177 | 257.3165 | 262.6193
5361.5979 | 530.4184 | 264.1141 | 257.0437 | 262.5262
5362.5979 | 530.2801 | 264.0679 | 256.8671 | 262.3462
5363.5979 | 530.386 | 263.7722 | 256.7866 | 262.2227
5364.5979 | 530.1438 | 263.5804 | 256.6303 | 262.0032
5365.5979 | 529.9797 | 263.4347 | 256.3646 | 261.8609
5366.5979 | 529.7889 | 263.3087 | 256.2667 | 261.6649
5367.5979 | 529.4305 | 263.3527 | 256.3354 | 261.5094
5368.5979 | 529.177 | 263.38 | 256.3102 | 261.2974
5369.5979 | 528.946 | 263.4064 | 256.0775 | 261.011
5370.5979 | 528.7819 | 263.3304 | 256.0373 | 260.8312
5371.5979 | 528.6854 | 263.3754 | 255.9042 | 260.7927
5372.5979 | 528.6146 | 263.3591 | 255.7522 | 260.8756
5373.5979 | 528.5665 | 263.3176 | 255.6483 | 260.6979
5374.5979 | 528.4516 | 263.3533 | 255.6092 | 260.6059
5375.5979 | 528.1502 | 263.4373 | 255.4286 | 260.6048
5376.5979 | 527.8175 | 263.3932 | 255.4088 | 260.6022
5377.5979 | 527.6862 | 263.4617 | 255.5543 | 260.5786
5378.5979 | 527.6734 | 263.4994 | 255.5729 | 260.5853
5379.5979 | 527.9811 | 263.3905 | 255.725 | 260.6021
5380.5979 | 527.9242 | 263.2656 | 255.7996 | 260.6187
5381.5979 | 527.7268 | 263.343 | 255.7056 | 260.4083
5382.5979 | 527.4724 | 263.4286 | 255.7718 | 260.4887
5383.5979 | 527.2068 | 263.4753 | 255.8275 | 260.5106
5384.5979 | 527.0342 | 263.297 | 255.7699 | 260.4713
5385.5979 | 527.0076 | 263.1189 | 255.8123 | 260.3646
5386.5979 | 526.7716 | 262.8064 | 255.8953 | 260.3006
5387.5979 | 526.6849 | 262.4813 | 255.9433 | 260.3649
5388.5979 | 526.5289 | 262.4268 | 255.9221 | 260.4738
5389.5979 | 526.319 | 262.3034 | 255.8881 | 260.5305
5390.5979 | 526.1662 | 262.1745 | 255.9289 | 260.5948
5391.5979 | 525.8895 | 262.0662 | 255.9078 | 260.4493
5392.5979 | 525.6964 | 262.0451 | 255.9389 | 260.4039
5393.5979 | 525.5628 | 261.9378 | 255.8089 | 260.4203
5394.5979 | 525.4203 | 261.6469 | 255.6554 | 260.3168
5395.5979 | 525.2966 | 261.3376 | 255.5496 | 260.3051
5396.5979 | 525.0968 | 261.1253 | 255.4717 | 260.2741
5397.5979 | 524.6852 | 261.1048 | 255.2732 | 260.1896
5398.5979 | 523.9306 | 260.8597 | 255.1098 | 260.1496
5399.5979 | 523.3808 | 260.77 | 254.962 | 260.0816
5400.5979 | 523.2293 | 260.7206 | 254.9451 | 260.1018
5401.5979 | 522.9202 | 260.7744 | 254.8813 | 260.1593
5402.5979 | 522.9216 | 260.6894 | 254.8462 | 260.021
5403.5979 | 523.1186 | 260.5878 | 254.716 | 259.9364
5404.5979 | 522.9898 | 260.4439 | 254.763 | 259.862
5405.5979 | 522.8148 | 260.4857 | 254.7033 | 259.7899
5406.5979 | 522.6533 | 260.4342 | 254.4719 | 259.7941
5407.5979 | 522.2664 | 260.5299 | 254.3782 | 259.8198
5408.5979 | 521.8153 | 260.6256 | 254.4304 | 259.8883
5409.5979 | 521.4768 | 260.6728 | 254.4998 | 259.7208
5410.5979 | 521.2563 | 260.6931 | 254.6692 | 259.5374
5411.5979 | 521.0593 | 260.8081 | 254.6694 | 259.4147
5412.5979 | 521.0084 | 260.9565 | 254.579 | 259.3221
5413.5979 | 520.8309 | 260.8955 | 254.5108 | 259.3528
5414.5979 | 520.5522 | 261.0125 | 254.625 | 259.3402
5415.5979 | 520.4843 | 261.086 | 254.6161 | 259.2973
5416.5979 | 520.6456 | 260.896 | 254.479 | 259.3274
5417.5979 | 520.5287 | 260.7623 | 254.2663 | 259.2863
5418.5979 | 520.2196 | 260.465 | 254.0967 | 259.2014
5419.5979 | 520.1306 | 260.4664 | 253.9948 | 259.0719
5420.5979 | 520.2143 | 260.1025 | 253.8993 | 258.9993
5421.5979 | 520.3054 | 259.9167 | 253.9133 | 259.0107
5422.5979 | 520.2797 | 259.7916 | 253.8625 | 258.9287
5423.5979 | 520.1293 | 259.7192 | 253.9065 | 258.6816
5424.5979 | 520.1742 | 259.5825 | 253.9359 | 258.5268
5425.5979 | 520.413 | 259.4854 | 253.8222 | 258.3097
5426.5979 | 520.576 | 259.3289 | 253.7251 | 258.2019
5427.5979 | 520.736 | 259.3553 | 253.5681 | 258.0944
5428.5979 | 520.968 | 259.3666 | 253.4613 | 258.1067
5429.5979 | 521.1917 | 259.419 | 253.3222 | 258.0681
5430.5979 | 521.3434 | 259.367 | 253.179 | 258.1416
5431.5979 | 521.3606 | 259.4003 | 253.0667 | 258.1107
5432.5979 | 521.2739 | 259.363 | 253.0392 | 257.9969
5433.5979 | 520.851 | 259.3144 | 253.1104 | 257.9294
5434.5979 | 520.5332 | 259.2043 | 253.2388 | 257.8261
5435.5979 | 520.4172 | 259.2766 | 253.4089 | 257.8536
5436.5979 | 520.1586 | 259.4122 | 253.3925 | 257.9157
5437.5979 | 519.9205 | 259.3967 | 253.2549 | 257.923
5438.5979 | 519.44 | 259.3095 | 253.3089 | 257.9165
5439.5979 | 519.478 | 259.2382 | 253.0995 | 257.7576
5440.5979 | 519.446 | 259.2893 | 252.8903 | 257.4599
5441.5979 | 519.3501 | 259.3634 | 252.5838 | 257.3508
5442.5979 | 519.5212 | 259.3759 | 252.3049 | 257.3547
5443.5979 | 519.2578 | 259.3433 | 251.9322 | 257.297
5444.5979 | 519.1399 | 259.1013 | 252.0658 | 257.3227
5445.5979 | 518.703 | 259.0173 | 252.1145 | 257.4151
5446.5979 | 518.3656 | 258.8599 | 252.105 | 257.3844
5447.5979 | 518.294 | 258.8058 | 252.1255 | 257.4333
5448.5979 | 518.2953 | 258.8307 | 252.3243 | 257.3289
5449.5979 | 518.2258 | 258.8614 | 252.5151 | 257.2287
5450.5979 | 517.4774 | 259.0105 | 252.5081 | 257.2161
5451.5979 | 517.0067 | 258.9051 | 252.5432 | 257.2436
5452.5979 | 516.5938 | 258.8258 | 252.6362 | 257.2155
5453.5979 | 516.6131 | 258.7577 | 252.6358 | 257.1908
5454.5979 | 516.6688 | 258.8024 | 252.5831 | 257.2094
5455.5979 | 516.6481 | 258.9406 | 252.5632 | 257.2607
5456.5979 | 516.3278 | 258.9786 | 252.4778 | 257.1629
5457.5979 | 516.0367 | 259.0208 | 252.4405 | 257.063
5458.5979 | 515.9399 | 259.1124 | 252.4892 | 257.005
5459.5979 | 515.6599 | 259.1934 | 252.3556 | 256.847
5460.5979 | 515.3852 | 259.1286 | 252.3279 | 256.7781
5461.5979 | 515.3679 | 259.1342 | 252.3571 | 256.7756
5462.5979 | 515.1186 | 259.0136 | 252.4845 | 256.7495
5463.5979 | 514.8329 | 258.7871 | 252.4816 | 256.7674
5464.5979 | 514.4489 | 258.5815 | 252.4218 | 256.7047
5465.5979 | 513.8598 | 258.5556 | 252.476 | 256.6446
5466.5979 | 513.6703 | 258.4974 | 252.5526 | 256.7754
5467.5979 | 513.4772 | 258.4246 | 252.6623 | 256.7884
5468.5979 | 513.0938 | 258.3555 | 252.8134 | 256.8773
5469.5979 | 512.9414 | 258.2742 | 252.8925 | 256.9337
5470.5979 | 512.63 | 258.3703 | 253.0175 | 256.901
5471.5979 | 512.2959 | 258.4198 | 252.9775 | 256.9574
5472.5979 | 512.2255 | 258.3598 | 252.8143 | 256.6725
5473.5979 | 512.2895 | 258.167 | 252.803 | 256.4631
5474.5979 | 512.3854 | 258.0999 | 252.7185 | 256.2874
5475.5979 | 512.2737 | 258.1062 | 252.2946 | 256.1656
5476.5979 | 512.2398 | 258.1399 | 252.1135 | 256.0621
5477.5979 | 512.0711 | 258.0512 | 252.0691 | 256.0502
5478.5979 | 511.9539 | 257.9569 | 251.9943 | 256.1582
5479.5979 | 511.9821 | 257.9348 | 251.8053 | 256.1373
5480.5979 | 511.9982 | 257.8819 | 251.678 | 256.0736
5481.5979 | 512.1049 | 257.8681 | 251.529 | 255.9269
5482.5979 | 511.9996 | 257.8213 | 251.4744 | 255.8029
5483.5979 | 512.1476 | 257.7451 | 251.4278 | 255.7667
5484.5979 | 512.5006 | 257.557 | 251.1108 | 255.657
5485.5979 | 512.7524 | 257.2675 | 250.8346 | 255.6076
5486.5979 | 512.7579 | 257.082 | 250.6915 | 255.5665
5487.5979 | 512.4802 | 256.9701 | 250.7171 | 255.2759
5488.5979 | 512.5667 | 256.8598 | 250.7239 | 255.2647
5489.5979 | 512.6545 | 256.7173 | 250.7679 | 255.346
5490.5979 | 512.4565 | 256.8709 | 250.7205 | 255.3109
5491.5979 | 512.334 | 256.9547 | 250.7553 | 255.1886
5492.5979 | 512.1589 | 256.9929 | 250.8107 | 255.1575
5493.5979 | 512.1688 | 257.0158 | 250.8405 | 255.2209
5494.5979 | 511.8154 | 257.0462 | 250.8853 | 255.2537
5495.5979 | 511.4478 | 257.12 | 250.8917 | 255.3215
5496.5979 | 511.1354 | 257.1361 | 250.9232 | 255.3599
5497.5979 | 510.8098 | 257.2217 | 250.9497 | 255.2705
5498.5979 | 510.3971 | 257.2841 | 251.0438 | 255.2899
5499.5979 | 510.6499 | 257.333 | 251.0104 | 255.2864
5500.5979 | 510.8774 | 257.3069 | 251.066 | 255.172
5501.5979 | 511.0114 | 257.2753 | 251.0057 | 255.2631
5502.5979 | 510.9294 | 257.2239 | 250.9832 | 255.2879
5503.5979 | 510.8475 | 257.1788 | 250.8663 | 255.0936
5504.5979 | 510.6276 | 257.2167 | 250.7876 | 254.8718
5505.5979 | 510.6118 | 257.2328 | 250.6682 | 254.7914
5506.5979 | 510.4541 | 257.1611 | 250.54 | 254.7559
5507.5979 | 510.1987 | 257.1617 | 250.4506 | 254.7757
5508.5979 | 509.8736 | 257.1466 | 250.3951 | 254.92
5509.5979 | 509.5792 | 256.8988 | 250.4998 | 254.9327
5510.5979 | 509.4213 | 256.6611 | 250.5528 | 254.8712
5511.5979 | 509.4276 | 256.5909 | 250.6933 | 254.8066
5512.5979 | 508.9804 | 256.5211 | 250.649 | 254.7233
5513.5979 | 508.5124 | 256.314 | 250.6147 | 254.7087
5514.5979 | 508.1325 | 256.0245 | 250.5733 | 254.7664
5515.5979 | 507.9426 | 255.9124 | 250.605 | 254.6424
5516.5979 | 507.59 | 255.7206 | 250.6938 | 254.6776
5517.5979 | 507.4714 | 255.6346 | 250.4647 | 254.5929
5518.5979 | 507.6217 | 255.4601 | 250.166 | 254.3803
5519.5979 | 507.5166 | 255.5222 | 250.1171 | 254.498
5520.5979 | 507.5037 | 255.3558 | 250.1117 | 254.5572
5521.5979 | 507.3738 | 255.2433 | 250.0711 | 254.5492
5522.5979 | 507.2005 | 255.2148 | 249.965 | 254.5423
5523.5979 | 507.3503 | 255.2278 | 249.8995 | 254.4088
5524.5979 | 507.5348 | 255.0756 | 249.8573 | 254.3088
5525.5979 | 507.5865 | 254.9322 | 249.8598 | 254.3356
5526.5979 | 507.5036 | 254.7978 | 249.7318 | 254.1437
5527.5979 | 507.4592 | 254.7664 | 249.6587 | 254.062
5528.5979 | 507.2338 | 254.8189 | 249.644 | 254.0195
5529.5979 | 506.9491 | 254.8737 | 249.6675 | 254.0003
5530.5979 | 506.8393 | 254.9092 | 249.7224 | 253.9549
5531.5979 | 506.9602 | 254.9686 | 249.6673 | 253.9128
5532.5979 | 507.0631 | 255.0413 | 249.5387 | 253.8207
5533.5979 | 507.0701 | 255.1251 | 249.5157 | 253.7958
5534.5979 | 507.2454 | 255.2329 | 249.4479 | 253.7056
5535.5979 | 507.3256 | 255.3483 | 249.409 | 253.6119
5536.5979 | 507.3074 | 255.4068 | 249.1575 | 253.563
5537.5979 | 507.3093 | 255.5012 | 249.2259 | 253.4614
5538.5979 | 506.9253 | 255.6281 | 249.3402 | 253.474
5539.5979 | 506.8795 | 255.6842 | 249.2349 | 253.488
5540.5979 | 506.9335 | 255.7926 | 249.155 | 253.3181
5541.5979 | 506.8643 | 255.8368 | 249.0395 | 253.217
5542.5979 | 506.9441 | 255.7091 | 248.8974 | 253.0798
5543.5979 | 506.9413 | 255.6544 | 248.9103 | 253.1018
5544.5979 | 506.5961 | 255.416 | 248.9045 | 253.0719
5545.5979 | 506.3849 | 255.3928 | 248.9302 | 253.0962
5546.5979 | 506.1084 | 255.4164 | 248.7347 | 253.0736
5547.5979 | 506.0844 | 255.4442 | 248.4785 | 253.068
5548.5979 | 505.9788 | 255.2249 | 248.3871 | 252.9688
5549.5979 | 505.9459 | 255.0036 | 248.4883 | 252.884
5550.5979 | 505.8457 | 254.7941 | 248.5828 | 252.9032
5551.5979 | 505.5456 | 254.6688 | 248.6672 | 252.8543
5552.5979 | 505.4247 | 254.5297 | 248.7929 | 252.8316
5553.5979 | 505.5003 | 254.247 | 248.7078 | 252.7627
5554.5979 | 505.6805 | 254.0923 | 248.7409 | 252.7756
5555.5979 | 505.9327 | 254.0058 | 248.5801 | 252.7144
5556.5979 | 505.8916 | 254.0487 | 248.3391 | 252.7334
5557.5979 | 505.7599 | 253.9946 | 248.4388 | 252.6717
5558.5979 | 505.8138 | 254.1004 | 248.5939 | 252.5733
5559.5979 | 505.337 | 254.2129 | 248.6715 | 252.5667
5560.5979 | 505.0107 | 254.214 | 248.4847 | 252.4385
5561.5979 | 505.1053 | 254.216 | 248.1692 | 252.4756
5562.5979 | 504.8854 | 254.0143 | 248.0526 | 252.4098
5563.5979 | 504.7499 | 253.9611 | 247.9101 | 252.3704
5564.5979 | 504.5082 | 254.0469 | 247.8498 | 252.4569
5565.5979 | 504.2397 | 254.1608 | 247.6166 | 252.4367
5566.5979 | 503.9228 | 254.1431 | 247.466 | 252.4272
5567.5979 | 503.5645 | 253.969 | 247.413 | 252.4439
5568.5979 | 503.581 | 253.8773 | 247.496 | 252.3763
5569.5979 | 503.9274 | 253.7222 | 247.436 | 252.3848
5570.5979 | 504.0354 | 253.5824 | 247.3877 | 252.3422
5571.5979 | 503.6691 | 253.3633 | 247.3841 | 252.2419
5572.5979 | 503.5199 | 253.1702 | 247.5139 | 252.3283
5573.5979 | 503.7832 | 252.9868 | 247.5699 | 252.3791
5574.5979 | 503.8254 | 252.8818 | 247.7157 | 252.1998
5575.5979 | 503.7267 | 252.7118 | 247.688 | 252.0179
5576.5979 | 503.8463 | 252.7725 | 247.6237 | 252.0048
5577.5979 | 504.016 | 252.7238 | 247.5315 | 252.0498
5578.5979 | 504.1288 | 252.8033 | 247.3579 | 252.0099
5579.5979 | 504.0071 | 252.916 | 247.1125 | 251.9632
5580.5979 | 504.0184 | 252.9844 | 246.8688 | 251.8677
5581.5979 | 504.0338 | 253.0583 | 246.7296 | 251.7568
5582.5979 | 503.9794 | 253.0444 | 246.4804 | 251.67
5583.5979 | 503.8012 | 253.0421 | 246.0617 | 251.7001
5584.5979 | 503.8241 | 252.7711 | 245.7786 | 251.7594
5585.5979 | 503.9773 | 252.5833 | 245.7476 | 251.7529
5586.5979 | 503.7662 | 252.474 | 245.6286 | 251.6986
5587.5979 | 503.4836 | 252.4448 | 245.6096 | 251.6736
5588.5979 | 503.1882 | 252.428 | 245.6167 | 251.6769
5589.5979 | 502.8806 | 252.4457 | 245.5443 | 251.4621
5590.5979 | 502.7177 | 252.4298 | 245.5704 | 251.3191
5591.5979 | 502.4496 | 252.2756 | 245.6598 | 251.3694
5592.5979 | 502.3292 | 252.1907 | 245.9504 | 251.5105
5593.5979 | 502.2151 | 252.1306 | 245.9564 | 251.5264
5594.5979 | 502.1298 | 252.0871 | 245.9853 | 251.4964
5595.5979 | 502.1252 | 252.1099 | 245.9568 | 251.4728
5596.5979 | 501.8323 | 251.8445 | 245.8048 | 251.4295
5597.5979 | 501.1016 | 251.7212 | 245.8481 | 251.3866
5598.5979 | 500.3948 | 251.6747 | 245.8681 | 251.269
5599.5979 | 500.1148 | 251.7817 | 245.9324 | 251.1364
5600.5979 | 500.0154 | 251.8895 | 245.8422 | 251.0728
5601.5979 | 500.0447 | 251.9778 | 245.725 | 251.0881
5602.5979 | 499.8545 | 251.9677 | 245.6652 | 251.0632
5603.5979 | 499.6052 | 251.9663 | 245.6892 | 250.791
5604.5979 | 499.4474 | 251.8896 | 245.6863 | 250.5913
5605.5979 | 499.2704 | 251.6294 | 245.5857 | 250.4174
5606.5979 | 499.2497 | 251.3982 | 245.5663 | 250.0546
5607.5979 | 499.3661 | 251.3478 | 245.5754 | 249.8362
5608.5979 | 499.3536 | 251.2065 | 245.6363 | 249.8048
5609.5979 | 499.1806 | 251.138 | 245.7063 | 249.7191
5610.5979 | 499.1146 | 251.0533 | 245.5697 | 249.6144
5611.5979 | 498.7304 | 250.9422 | 245.3547 | 249.5223
5612.5979 | 498.3154 | 250.8162 | 245.1373 | 249.4404
5613.5979 | 498.4847 | 250.7844 | 245.0842 | 249.4829
5614.5979 | 498.5591 | 250.5542 | 245.0428 | 249.4555
5615.5979 | 498.6064 | 250.479 | 245.0068 | 249.4377
5616.5979 | 498.5488 | 250.3937 | 244.9934 | 249.3467
5617.5979 | 498.0974 | 250.4425 | 244.9349 | 249.2988
5618.5979 | 498.2645 | 250.554 | 244.7247 | 249.3471
5619.5979 | 498.0892 | 250.6986 | 244.7406 | 249.2375
5620.5979 | 498.0031 | 250.6927 | 244.6672 | 249.2095
5621.5979 | 498.1195 | 250.6023 | 244.6159 | 249.2432
5622.5979 | 498.1537 | 250.4483 | 244.6598 | 249.2831
5623.5979 | 498.1525 | 250.2416 | 244.6146 | 249.2501
5624.5979 | 498.0516 | 250.245 | 244.6105 | 249.1656
5625.5979 | 498.0009 | 250.2175 | 244.5718 | 249.0542
5626.5979 | 497.8944 | 250.0391 | 244.6335 | 249.025
5627.5979 | 497.6469 | 250.0484 | 244.6461 | 248.8469
5628.5979 | 497.4573 | 249.9847 | 244.4882 | 248.6634
5629.5979 | 497.1536 | 249.7781 | 244.5823 | 248.5599
5630.5979 | 497.0417 | 249.7445 | 244.5916 | 248.4303
5631.5979 | 496.9839 | 249.7793 | 244.4495 | 248.3492
5632.5979 | 496.6095 | 249.81 | 244.4159 | 248.1965
5633.5979 | 496.4424 | 249.7293 | 244.224 | 248.193
5634.5979 | 496.5395 | 249.6718 | 244.1763 | 248.093
5635.5979 | 496.4 | 249.6832 | 244.1416 | 248.1448
5636.5979 | 495.9655 | 249.7356 | 244.1214 | 248.1988
5637.5979 | 495.7373 | 249.8037 | 244.222 | 248.3053
5638.5979 | 495.3766 | 249.7757 | 244.1784 | 248.3944
5639.5979 | 494.9545 | 249.673 | 244.0759 | 248.3151
5640.5979 | 494.4217 | 249.6675 | 243.9735 | 248.2915
5641.5979 | 493.9268 | 249.5749 | 243.7506 | 248.1927
5642.5979 | 493.3593 | 249.2865 | 243.6396 | 248.1771
5643.5979 | 492.9709 | 249.2269 | 243.5643 | 248.2264
5644.5979 | 492.6367 | 249.0716 | 243.426 | 248.0524
5645.6135 | 492.2924 | 248.9596 | 243.262 | 248.019
5646.5979 | 492.2735 | 248.8268 | 243.1519 | 247.9149
5647.5979 | 492.1067 | 248.7919 | 243.2381 | 247.8984
5648.5979 | 491.8591 | 248.7339 | 243.3281 | 247.9545
5649.5979 | 491.4352 | 248.8721 | 243.3342 | 248.0046
5650.5979 | 491.3747 | 248.8924 | 243.2558 | 248.0872
5651.5979 | 491.3466 | 248.7631 | 243.0836 | 248.145
5652.5979 | 491.3158 | 248.6093 | 242.7055 | 247.9532
5653.5979 | 491.0769 | 248.6584 | 242.4498 | 247.8082
5654.5979 | 490.9475 | 248.6131 | 242.2733 | 247.5151
5655.5979 | 490.8071 | 248.3093 | 242.2182 | 247.2761
5656.5979 | 490.7191 | 248.1869 | 242.1896 | 247.1139
5657.5979 | 490.552 | 247.9354 | 242.2134 | 247.0823
5658.5979 | 490.2627 | 247.9116 | 242.2046 | 246.9962
5659.5979 | 489.8758 | 247.7565 | 242.2111 | 247.0334
5660.5979 | 489.5813 | 247.8158 | 242.2797 | 247.0589
5661.5979 | 489.2885 | 247.8808 | 242.3992 | 247.1122
5662.5979 | 489.2169 | 247.9432 | 242.5422 | 247.1782
5663.5979 | 489.0542 | 248.0714 | 242.7182 | 247.2356
5664.5979 | 488.766 | 248.1738 | 242.8104 | 247.2149
5665.5979 | 488.5513 | 248.2356 | 242.8893 | 247.2098
5666.5979 | 488.405 | 248.3704 | 242.9186 | 247.2736
5667.5979 | 488.0879 | 248.411 | 242.8933 | 247.3474
5668.5979 | 487.9409 | 248.4548 | 242.9492 | 247.4828
5669.5979 | 487.8357 | 248.5722 | 242.9334 | 247.4929
5670.5979 | 487.6428 | 248.7359 | 242.7929 | 247.4856
5671.5979 | 487.4977 | 248.8573 | 242.6839 | 247.3934
5672.5979 | 487.4844 | 248.9609 | 242.2908 | 247.222
5673.5979 | 487.3988 | 249.027 | 241.8641 | 247.1127
5674.5979 | 486.996 | 248.8475 | 241.634 | 247.0808
5675.5979 | 486.8001 | 248.5544 | 241.4744 | 247.0718
5676.6135 | 486.5003 | 248.466 | 241.3476 | 247.0534
5677.5979 | 486.0829 | 248.3986 | 241.3023 | 247.0613
5678.5979 | 485.8258 | 248.2801 | 241.3859 | 247.027
5679.5979 | 485.9294 | 248.3286 | 241.4767 | 247.0145
5680.5979 | 485.8804 | 248.3849 | 241.4298 | 246.9675
5681.5979 | 485.6787 | 248.3839 | 241.3114 | 247.0191
5682.5979 | 485.825 | 248.3328 | 241.243 | 247.0365
5683.5979 | 485.5647 | 248.207 | 240.8785 | 246.9522
5684.5979 | 485.2202 | 247.8661 | 240.6216 | 246.9225
5685.5979 | 485.0695 | 247.6129 | 240.6064 | 246.8223
5686.5979 | 485.0129 | 247.4989 | 240.6042 | 246.7202
5687.5979 | 484.9907 | 247.4107 | 240.6788 | 246.6044
5688.5979 | 484.8846 | 247.4088 | 240.6748 | 246.5727
5689.5979 | 484.8703 | 247.2539 | 240.6009 | 246.5556
5690.5979 | 484.7411 | 247.2105 | 240.4894 | 246.5557
5691.5979 | 484.5934 | 247.2737 | 240.4842 | 246.5744
5692.5979 | 484.6411 | 247.3172 | 240.4212 | 246.5546
5693.5979 | 484.6947 | 247.3014 | 240.5165 | 246.5042
5694.5979 | 484.6437 | 247.2655 | 240.6488 | 246.5505
5695.5979 | 484.8903 | 247.2328 | 240.8065 | 246.629
5696.5979 | 485.2029 | 247.1624 | 240.7564 | 246.6638
5697.5979 | 485.215 | 247.1936 | 240.8661 | 246.6525
5698.5979 | 485.25 | 247.3202 | 240.8026 | 246.5799
5699.5979 | 485.3092 | 247.4817 | 240.7481 | 246.4139
5700.5979 | 485.1512 | 247.4493 | 240.7552 | 246.2551
5701.5979 | 485.036 | 247.2531 | 240.6625 | 246.0792
5702.5979 | 485.2622 | 247.1289 | 240.6402 | 245.9655
5703.5979 | 485.5452 | 247.0353 | 240.6243 | 245.9524
5704.5979 | 485.3909 | 247.1197 | 240.5327 | 245.7854
5705.5979 | 485.1752 | 247.1748 | 240.2863 | 245.6429
5706.5979 | 484.9423 | 247.2678 | 240.1018 | 245.5602
5707.5979 | 484.7482 | 247.2408 | 239.9192 | 245.4314
5708.5979 | 484.5668 | 247.2275 | 239.9118 | 245.2895
5709.5979 | 484.107 | 247.2785 | 239.9688 | 245.265
5710.5979 | 484.0389 | 247.3563 | 240.0521 | 245.1691
5711.5979 | 483.8162 | 247.4125 | 240.1574 | 245.2483
5712.5979 | 483.6635 | 247.3568 | 240.0417 | 245.319
5713.5979 | 483.6112 | 247.2958 | 239.6856 | 245.2457
5714.5979 | 483.3035 | 247.3075 | 239.4774 | 245.1086
5715.5979 | 482.9175 | 247.0311 | 239.4439 | 245.0562
5716.5979 | 482.845 | 246.8508 | 239.5365 | 245.0917
5717.5979 | 482.8073 | 246.6187 | 239.5511 | 245.0433
5718.5979 | 482.9094 | 246.3672 | 239.6097 | 244.9113
5719.5979 | 482.898 | 246.3604 | 239.3575 | 244.6459
5720.5979 | 482.7843 | 246.3296 | 239.1758 | 244.5565
5721.5979 | 482.8298 | 246.2221 | 239.0977 | 244.2678
5722.5979 | 482.8001 | 246.2385 | 239.0385 | 244.1474
5723.5979 | 482.852 | 246.1366 | 239.0084 | 244.1766
5724.5979 | 482.8336 | 246.138 | 238.9872 | 244.2076
5725.5979 | 482.6129 | 246.1333 | 238.9513 | 244.2069
5726.5979 | 482.5599 | 246.1529 | 238.9795 | 244.1485
5727.5979 | 482.5922 | 246.2051 | 238.8745 | 244.0998
5728.5979 | 482.6034 | 246.2492 | 238.6476 | 244.0699
5729.5979 | 482.3444 | 246.202 | 238.5087 | 244.076
5730.5979 | 482.2362 | 246.0065 | 238.315 | 244.1324
5731.5979 | 481.8293 | 245.86 | 238.4406 | 243.9909
5732.5979 | 481.4437 | 245.9385 | 238.5863 | 244.0438
5733.5979 | 481.2793 | 245.9968 | 238.7587 | 244.0305
5734.5979 | 481.1998 | 246.0509 | 238.7716 | 243.9797
5735.5979 | 481.2507 | 246.1245 | 238.7298 | 244.0231
5736.5979 | 481.3132 | 246.0427 | 238.5141 | 243.9889
5737.5979 | 481.0189 | 245.9609 | 238.5103 | 244.0705
5738.5979 | 480.8656 | 245.9026 | 238.5772 | 244.089
5739.5979 | 480.7167 | 245.6443 | 238.2656 | 244.069
5740.5979 | 480.3776 | 245.4788 | 238.0774 | 243.9976
5741.5979 | 480.1038 | 245.3066 | 237.8568 | 243.9859
5742.5979 | 480.0427 | 245.1371 | 237.7139 | 243.9983
5743.5979 | 479.9372 | 245.1254 | 237.7496 | 244.0238
5744.5979 | 479.6672 | 244.8569 | 237.5622 | 243.9763
5745.5979 | 479.6669 | 244.8215 | 237.4964 | 243.9884
5746.5979 | 479.4243 | 244.8598 | 237.5414 | 243.9856
5747.5979 | 479.2417 | 244.9089 | 237.6738 | 243.9665
5748.5979 | 479.0898 | 244.8998 | 237.7041 | 243.936
5749.5979 | 478.9857 | 245.0054 | 237.6353 | 243.901
5750.5979 | 478.821 | 245.0903 | 237.6525 | 243.8437
5751.5979 | 478.8179 | 245.0714 | 237.7135 | 243.6768
5752.5979 | 478.7227 | 245.1954 | 237.8686 | 243.5147
5753.5979 | 478.7337 | 245.1439 | 238.0321 | 243.4617
5754.5979 | 478.5662 | 245.1596 | 238.0538 | 243.5059
5755.5979 | 478.5965 | 245.1663 | 238.1398 | 243.5297
5756.5979 | 478.4592 | 245.0114 | 238.2579 | 243.4855
5757.5979 | 478.2077 | 244.9341 | 238.1547 | 243.3262
5758.5979 | 478.1652 | 244.8792 | 238.264 | 243.0325
5759.5979 | 477.8949 | 244.8305 | 238.3568 | 242.8774
5760.5979 | 477.9856 | 244.8228 | 238.2432 | 242.8963
5761.5979 | 477.9154 | 244.8875 | 238.1837 | 242.7704
5762.5979 | 477.8017 | 244.8973 | 238.0172 | 242.6247
5763.5979 | 477.7065 | 244.9396 | 237.7504 | 242.5527
5764.5979 | 477.7077 | 244.7657 | 237.496 | 242.6414
5765.5979 | 477.5828 | 244.6604 | 237.4682 | 242.5682
5766.5979 | 477.4402 | 244.588 | 237.4175 | 242.5861
5767.5979 | 477.1992 | 244.5559 | 237.3101 | 242.577
5768.5979 | 477.0226 | 244.4707 | 237.4547 | 242.3954
5769.5979 | 476.9658 | 244.4665 | 237.2303 | 242.2599
5770.5979 | 476.8697 | 244.462 | 237.1003 | 242.1826
5771.5979 | 476.673 | 244.4697 | 237.0657 | 242.1908
5772.5979 | 476.4803 | 244.3469 | 237.0929 | 242.2592
5773.5979 | 476.3127 | 244.4603 | 236.8211 | 242.257
5774.5979 | 476.0105 | 244.4403 | 236.8848 | 242.2099
5775.5979 | 475.6881 | 244.4481 | 237.106 | 242.1857
5776.5979 | 475.5806 | 244.3026 | 237.2652 | 242.0859
5777.5979 | 475.4691 | 244.3178 | 237.3205 | 242.1569
5778.5979 | 475.5999 | 244.2438 | 237.2927 | 242.2542
5779.5979 | 475.4519 | 244.237 | 237.3373 | 242.3013
5780.5979 | 475.5445 | 244.2935 | 237.2817 | 242.3025
5781.5979 | 475.5209 | 244.2483 | 237.3597 | 242.1587
5782.5979 | 475.5255 | 244.1415 | 237.2712 | 242.0331
5783.5979 | 475.5419 | 244.0359 | 237.0812 | 241.9724
5784.5979 | 475.2379 | 243.8011 | 236.9643 | 241.9437
5785.5979 | 475.1289 | 243.773 | 236.9618 | 241.9464
5786.5979 | 474.7639 | 243.8102 | 237.0376 | 241.9535
5787.5979 | 474.438 | 243.8641 | 237.1977 | 242.0817
5788.5979 | 474.0609 | 243.8725 | 237.0081 | 242.1618
5789.5979 | 473.8398 | 243.9489 | 236.8492 | 242.2061
5790.5979 | 473.6027 | 244.0042 | 236.7722 | 242.2802
5791.5979 | 473.5588 | 243.9874 | 236.7373 | 242.3176
5792.5979 | 473.3579 | 244.0053 | 236.7364 | 242.3409
5793.5979 | 473.4349 | 243.9608 | 236.5616 | 242.2615
5794.5979 | 473.6564 | 243.7759 | 236.5556 | 241.9863
5795.5979 | 473.4321 | 243.4916 | 236.7254 | 241.8799
5796.5979 | 472.9961 | 243.4202 | 236.7024 | 241.67
5797.5979 | 472.6227 | 243.3439 | 236.7973 | 241.5371
5798.5979 | 472.1879 | 243.3923 | 236.8883 | 241.5291
5799.5979 | 471.947 | 243.4947 | 237.0244 | 241.5018
5800.5979 | 471.7276 | 243.46 | 237.0135 | 241.4504
5801.5979 | 471.5199 | 243.4558 | 237.0278 | 241.4051
5802.5979 | 471.7058 | 243.5087 | 237.0377 | 241.3004
5803.5979 | 472.1833 | 243.5858 | 236.9952 | 241.0241
5804.5979 | 472.2855 | 243.6378 | 236.9043 | 240.7323
5805.5979 | 472.3419 | 243.5597 | 236.7901 | 240.542
5806.5979 | 472.34 | 243.6231 | 236.7957 | 240.3916
5807.5979 | 472.2211 | 243.6368 | 236.817 | 240.2061
5808.5979 | 472.1054 | 243.5048 | 236.8799 | 239.9968
5809.5979 | 472.0212 | 243.2591 | 236.8108 | 239.8924
5810.5979 | 471.59 | 243.0593 | 236.7008 | 239.877
5811.5979 | 471.3773 | 243.0101 | 236.5899 | 239.8864
5812.5979 | 471.3154 | 242.9326 | 236.5648 | 239.8665
5813.5979 | 471.225 | 242.7976 | 236.5823 | 239.8461
5814.5979 | 471.0661 | 242.7753 | 236.5541 | 239.7724
5815.5979 | 470.9853 | 242.5878 | 236.4453 | 239.7571
5816.5979 | 470.856 | 242.3534 | 236.395 | 239.554
5817.5979 | 470.6051 | 242.3137 | 236.4167 | 239.5412
5818.5979 | 470.3221 | 242.3251 | 236.4648 | 239.4972
5819.5979 | 470.2335 | 242.4471 | 236.3915 | 239.4801
5820.5979 | 470.5819 | 242.643 | 236.3169 | 239.3335
5821.5979 | 470.7017 | 242.7297 | 236.2118 | 239.3598
5822.5979 | 470.7187 | 242.7461 | 236.091 | 239.3173
5823.5979 | 470.6879 | 242.6722 | 236.0935 | 239.3229
5824.5979 | 470.7657 | 242.709 | 236.1139 | 239.261
5825.5979 | 470.5627 | 242.5911 | 236.0071 | 239.2592
5826.5979 | 470.4981 | 242.4898 | 235.9614 | 239.2686
5827.5979 | 470.6342 | 242.4807 | 235.8119 | 239.2454
5828.5979 | 470.4111 | 242.5381 | 235.6681 | 239.2657
5829.5979 | 470.5548 | 242.5463 | 235.4974 | 239.3734
5830.5979 | 470.6298 | 242.5876 | 235.3942 | 239.1863
5831.5979 | 470.8855 | 242.6522 | 235.3901 | 238.9937
5832.5979 | 470.9201 | 242.669 | 235.4683 | 238.9806
5833.5979 | 470.7304 | 242.8073 | 235.3475 | 239.035
5834.5979 | 470.6757 | 242.7401 | 235.3624 | 238.9814
5835.5979 | 470.3926 | 242.6585 | 235.365 | 239.0052
5836.5979 | 470.0531 | 242.6862 | 235.1531 | 238.9356
5837.5979 | 469.7327 | 242.7199 | 234.9934 | 238.8784
5838.5979 | 469.675 | 242.6748 | 234.8077 | 238.7839
5839.5979 | 469.7369 | 242.6782 | 234.649 | 238.8076
5840.5979 | 469.6767 | 242.706 | 234.4344 | 238.7176
5841.5979 | 469.644 | 242.5112 | 234.2251 | 238.6195
5842.5979 | 469.5784 | 242.2521 | 234.0268 | 238.5997
5843.5979 | 469.75 | 242.0301 | 233.8984 | 238.4864
5844.5979 | 469.7377 | 242.034 | 233.836 | 238.4657
5845.5979 | 469.7839 | 242.0918 | 233.8149 | 238.51
5846.5979 | 469.5926 | 242.0214 | 233.737 | 238.3935
5847.5979 | 469.5629 | 241.7312 | 233.6037 | 238.3187
5848.5979 | 469.2337 | 241.5817 | 233.5988 | 238.2873
5849.5979 | 468.8871 | 241.4462 | 233.5877 | 238.2661
5850.5979 | 468.6836 | 241.3692 | 233.5803 | 238.2562
5851.5979 | 468.6505 | 241.2869 | 233.6338 | 238.3643
5852.5979 | 468.5157 | 241.3628 | 233.7572 | 238.4691
5853.5979 | 468.244 | 241.2644 | 233.8308 | 238.4656
5854.5979 | 467.7108 | 241.0362 | 233.8484 | 238.4336
5855.5979 | 467.1266 | 240.7688 | 233.8248 | 238.4685
5856.6135 | 467.0764 | 240.7368 | 233.883 | 238.4419
5857.5979 | 466.9652 | 240.5004 | 234.0191 | 238.4442
5858.5979 | 466.8363 | 240.3862 | 233.9301 | 238.4277
5859.5979 | 466.7794 | 240.3887 | 233.8963 | 238.3822
5860.5979 | 466.7219 | 240.44 | 233.7786 | 238.4085
5861.5979 | 466.7063 | 240.2652 | 233.7979 | 238.3905
5862.5979 | 466.6288 | 240.2545 | 233.6775 | 238.199
5863.5979 | 466.6171 | 240.2581 | 233.681 | 238.0373
5864.5979 | 466.6436 | 240.2946 | 233.5672 | 238.0205
5865.5979 | 466.7278 | 240.3642 | 233.4841 | 237.8972
5866.5979 | 466.8066 | 240.4768 | 233.4314 | 237.7909
5867.5979 | 466.6449 | 240.553 | 233.5457 | 237.6569
5868.5979 | 466.364 | 240.6138 | 233.6878 | 237.625
5869.5979 | 466.2999 | 240.6179 | 233.8421 | 237.582
5870.5979 | 466.4099 | 240.4992 | 233.924 | 237.5315
5871.5979 | 466.3101 | 240.4862 | 233.8262 | 237.5739
5872.5979 | 466.2606 | 240.6019 | 233.8147 | 237.5595
5873.5979 | 466.3667 | 240.6529 | 233.8937 | 237.5359
5874.5979 | 466.2845 | 240.6397 | 234.0483 | 237.4512
5875.5979 | 466.2492 | 240.7305 | 234.1545 | 237.3179
5876.5979 | 466.3928 | 240.8245 | 234.0837 | 237.1975
5877.5979 | 466.5334 | 240.9261 | 234.0531 | 237.1216
5878.5979 | 466.6587 | 240.8705 | 233.9474 | 237.1456
5879.5979 | 466.8553 | 240.8551 | 233.8715 | 237.1014
5880.5979 | 466.9138 | 240.7891 | 233.733 | 236.9419
5881.5979 | 466.9784 | 240.7412 | 233.8031 | 236.8461
5882.5979 | 466.9751 | 240.6304 | 233.882 | 236.9579
5883.5979 | 467.0195 | 240.5291 | 233.9483 | 236.997
5884.5979 | 466.7774 | 240.4148 | 233.8913 | 237.0279
5885.5979 | 466.4417 | 240.2858 | 233.6838 | 237.0878
5886.5979 | 466.0916 | 240.2975 | 233.5066 | 236.9462
5887.5979 | 466.0147 | 240.276 | 233.4384 | 236.9461
5888.5979 | 465.9448 | 240.2013 | 233.4295 | 236.9873
5889.5979 | 465.8689 | 240.1561 | 233.4031 | 237.0262
5890.5979 | 465.7258 | 240.1493 | 233.3049 | 236.9952
5891.5979 | 465.6639 | 240.1372 | 233.3308 | 236.9097
5892.5979 | 465.8067 | 240.1697 | 233.2479 | 236.9019
5893.5979 | 465.7509 | 240.2796 | 233.1092 | 236.919
5894.5979 | 465.601 | 240.2864 | 233.1874 | 236.9641
5895.5979 | 465.497 | 240.0323 | 233.2624 | 237.0437
5896.5979 | 465.6388 | 239.9978 | 233.2611 | 237.1045
5897.5979 | 465.7408 | 239.6651 | 232.9656 | 237.1103
5898.5979 | 465.6445 | 239.3655 | 232.7462 | 237.0886
5899.5979 | 465.4186 | 239.308 | 232.5173 | 237.0801
5900.5979 | 465.1667 | 239.2488 | 232.3047 | 237.0588
5901.5979 | 464.9416 | 239.2843 | 232.2972 | 237.1601
5902.5979 | 464.6602 | 239.3641 | 232.2615 | 237.1599
5903.5979 | 464.411 | 239.2753 | 232.1913 | 237.182
5904.5979 | 464.1868 | 239.1842 | 232.1218 | 237.1239
5905.5979 | 464.0078 | 239.1774 | 232.096 | 237.1784
5906.5979 | 463.7433 | 239.1489 | 232.1152 | 237.123
5907.5979 | 463.7266 | 239.1623 | 231.9875 | 237.1458
5908.5979 | 463.4936 | 239.1086 | 231.9333 | 237.0597
5909.5979 | 463.5098 | 238.8641 | 231.839 | 237.1883
5910.5979 | 463.5346 | 238.8962 | 231.6791 | 237.1176
5911.5979 | 463.5126 | 238.9163 | 231.6671 | 237.033
5912.5979 | 463.4414 | 239.0053 | 231.6806 | 236.9922
5913.5979 | 463.3877 | 239.086 | 231.7027 | 236.8291
5914.5979 | 463.5174 | 238.8255 | 231.6107 | 236.729
5915.5979 | 463.2577 | 238.5467 | 231.1911 | 236.71
5916.5979 | 463.0748 | 238.1815 | 230.7873 | 236.7516
5917.5979 | 463.0132 | 237.992 | 230.7252 | 236.7878
5918.5979 | 462.7899 | 237.7012 | 230.741 | 236.8781
5919.5979 | 462.6703 | 237.4378 | 230.5458 | 236.8685
5920.5979 | 462.6148 | 237.2269 | 230.4304 | 236.8172
5921.5979 | 462.3523 | 236.8956 | 230.5076 | 236.803
5922.5979 | 462.069 | 236.5889 | 230.1735 | 236.6909
5923.5979 | 461.9004 | 236.3783 | 230.116 | 236.651
5924.5979 | 461.6678 | 236.3305 | 230.226 | 236.6171
5925.5979 | 461.2537 | 236.3006 | 230.1808 | 236.6396
5926.5979 | 461.1345 | 236.2991 | 230.2147 | 236.6628
5927.5979 | 461.0617 | 236.4084 | 230.3498 | 236.6356
5928.5979 | 460.7367 | 236.4657 | 230.4431 | 236.6886
5929.5979 | 460.4608 | 236.6042 | 230.4883 | 236.5731
5930.5979 | 460.2289 | 236.761 | 230.4864 | 236.5322
5931.5979 | 460.0329 | 236.8983 | 230.4059 | 236.4708
5932.5979 | 459.9702 | 236.7982 | 230.4244 | 236.3829
5933.5979 | 459.7919 | 236.7591 | 230.4233 | 236.4275
5934.5979 | 459.5396 | 236.7311 | 230.5981 | 236.3832
5935.5979 | 459.2715 | 236.7634 | 230.7389 | 236.3513
5936.5979 | 458.9261 | 236.6526 | 230.7415 | 236.3247
5937.5979 | 458.7271 | 236.7364 | 230.7473 | 236.1603
5938.5979 | 458.6124 | 236.802 | 230.679 | 235.9709
5939.5979 | 458.5774 | 236.881 | 230.6365 | 235.8638
5940.5979 | 458.5414 | 237.0776 | 230.5417 | 235.8125
5941.5979 | 458.5283 | 237.2199 | 230.529 | 235.7565
5942.5979 | 458.3349 | 237.3491 | 230.4564 | 235.6887
5943.5979 | 458.0522 | 237.4596 | 230.3902 | 235.6065
5944.5979 | 457.6491 | 237.5254 | 230.4162 | 235.493
5945.5979 | 457.5033 | 237.5156 | 230.4459 | 235.5597
5946.6135 | 457.5001 | 237.5561 | 230.4747 | 235.6406
5947.5979 | 457.5691 | 237.5772 | 230.4478 | 235.6154
5948.5979 | 457.4867 | 237.6189 | 230.4064 | 235.6125
5949.5979 | 457.3264 | 237.6387 | 230.3166 | 235.4941
5950.5979 | 456.9237 | 237.6332 | 230.3907 | 235.4378
5951.5979 | 456.6618 | 237.6739 | 230.5084 | 235.2381
5952.5979 | 456.2755 | 237.7938 | 230.4298 | 235.115
5953.5979 | 455.8168 | 237.7778 | 230.1866 | 235.0397
5954.5979 | 455.6563 | 237.8783 | 229.9791 | 234.9463
5955.5979 | 455.5844 | 237.9237 | 229.8577 | 234.8978
5956.5979 | 455.4563 | 237.8022 | 229.8309 | 234.7252
5957.5979 | 455.3525 | 237.7876 | 229.7214 | 234.5251
5958.5979 | 455.1716 | 237.8032 | 229.587 | 234.4431
5959.5979 | 454.9357 | 237.7845 | 229.492 | 234.4793
5960.5979 | 454.7859 | 237.6715 | 229.6123 | 234.4283
5961.5979 | 454.4939 | 237.5689 | 229.6964 | 234.3401
5962.5979 | 454.1544 | 237.5787 | 229.6312 | 234.2618
5963.5979 | 453.889 | 237.6256 | 229.5816 | 234.1846
5964.5979 | 453.5943 | 237.609 | 229.6328 | 234.2261
5965.5979 | 453.2038 | 237.7177 | 229.5371 | 234.2538
5966.5979 | 453.1663 | 237.8165 | 229.5113 | 234.2842
5967.5979 | 452.7855 | 237.9329 | 229.5823 | 234.2963
5968.5979 | 452.5733 | 238.0041 | 229.6825 | 234.3272
5969.5979 | 452.5342 | 238.0086 | 229.7225 | 234.2736
5970.5979 | 452.4895 | 238.0473 | 229.6478 | 234.2366
5971.5979 | 452.2932 | 238.1328 | 229.5645 | 234.2552
5972.5979 | 452.0466 | 238.0993 | 229.5198 | 234.2691
5973.5979 | 451.9299 | 237.9864 | 229.5326 | 234.271
5974.5979 | 451.6776 | 237.9866 | 229.4628 | 234.3177
5975.5979 | 451.4862 | 237.9634 | 229.397 | 234.421
5976.5979 | 451.4335 | 237.9334 | 229.298 | 234.492
5977.5979 | 451.0969 | 237.9554 | 229.1183 | 234.5605
5978.5979 | 450.8118 | 237.5719 | 228.9055 | 234.6078
5979.5979 | 450.4807 | 237.3649 | 228.8749 | 234.4729
5980.5979 | 450.1802 | 237.1286 | 228.9624 | 234.3757
5981.5979 | 449.8298 | 236.7121 | 229.0712 | 234.2755
5982.5979 | 449.2399 | 236.5543 | 229.218 | 234.2039
5983.5979 | 448.6374 | 236.3622 | 229.404 | 234.1929
5984.5979 | 448.2013 | 236.2121 | 229.4523 | 234.257
5985.5979 | 447.8709 | 236.1399 | 229.4037 | 234.1078
5986.5979 | 447.413 | 236.1569 | 229.3358 | 233.9684
5987.5979 | 447.2344 | 236.0737 | 229.2921 | 233.8383
5988.5979 | 446.8912 | 236.0303 | 229.3207 | 233.6033
5989.5979 | 446.6257 | 235.9072 | 229.2654 | 233.5569
5990.5979 | 446.6543 | 235.7973 | 229.185 | 233.495
5991.5979 | 446.6246 | 235.8209 | 229.1661 | 233.4985
5992.5979 | 446.421 | 235.7634 | 229.2736 | 233.5506
5993.5979 | 446.3107 | 235.6698 | 229.3283 | 233.4576
5994.5979 | 446.1147 | 235.7197 | 229.3974 | 233.4473
5995.5979 | 445.9392 | 235.764 | 229.47 | 233.5557
5996.5979 | 445.6167 | 235.6933 | 229.3421 | 233.7015
5997.5979 | 445.3427 | 235.5751 | 229.1891 | 233.6578
5998.5979 | 445.2116 | 235.5766 | 229.1197 | 233.6173
5999.5979 | 445.0378 | 235.6237 | 229.1638 | 233.5517
6000.5979 | 445.0597 | 235.6005 | 228.9579 | 233.5356
6001.5979 | 445.1259 | 235.5405 | 228.9063 | 233.5669
6002.5979 | 445.2245 | 235.4991 | 229.0294 | 233.589
6003.5979 | 445.2385 | 235.5332 | 229.0839 | 233.522
6004.5979 | 445.3357 | 235.4383 | 229.1558 | 233.3689
6005.5979 | 445.2107 | 235.4125 | 229.1171 | 233.2247
6006.5979 | 445.0155 | 235.3264 | 229.1853 | 233.2212
6007.5979 | 444.9406 | 235.2682 | 229.2547 | 233.2502
6008.5979 | 444.9119 | 235.1668 | 229.4113 | 233.1221
6009.5979 | 444.6811 | 235.0167 | 229.3114 | 233.1082
6010.5979 | 444.5269 | 235.0126 | 229.2316 | 232.9606
6011.5979 | 444.3925 | 234.9903 | 229.2966 | 232.7954
6012.5979 | 444.1126 | 234.7784 | 229.217 | 232.7886
6013.5979 | 443.9136 | 234.7259 | 229.2274 | 232.7563
6014.5979 | 443.7123 | 234.624 | 229.1194 | 232.6611
6015.5979 | 443.5712 | 234.5416 | 228.9732 | 232.6117
6016.5979 | 443.7455 | 234.507 | 228.8792 | 232.519
6017.5979 | 443.866 | 234.5713 | 228.787 | 232.5392
6018.5979 | 444.0065 | 234.6077 | 228.7358 | 232.4939
6019.5979 | 444.1466 | 234.5949 | 228.7388 | 232.4763
6020.5979 | 444.2758 | 234.4833 | 228.7525 | 232.4201
6021.5979 | 444.3981 | 234.5233 | 228.7805 | 232.4355
6022.5979 | 444.4954 | 234.4994 | 228.9298 | 232.4107
6023.5979 | 444.2994 | 234.3983 | 228.8251 | 232.3239
6024.5979 | 444.0043 | 234.3272 | 228.7037 | 232.2267
6025.5979 | 443.97 | 234.3273 | 228.7062 | 232.2322
6026.5979 | 444.0531 | 234.2835 | 228.6999 | 232.2376
6027.5979 | 443.9396 | 234.2724 | 228.5378 | 232.3394
6028.5979 | 443.7303 | 234.3065 | 228.3274 | 232.2298
6029.5979 | 443.4431 | 234.2972 | 228.2928 | 232.1185
6030.5979 | 443.0835 | 234.3487 | 228.2536 | 231.9711
6031.5979 | 442.8804 | 234.3833 | 228.2085 | 231.8861
6032.5979 | 442.6886 | 234.4525 | 228.2393 | 231.932
6033.5979 | 442.6312 | 234.4423 | 228.1231 | 231.9225
6034.5979 | 442.4859 | 234.5283 | 228.1011 | 231.922
6035.5979 | 442.4263 | 234.4642 | 228.1727 | 231.8974
6036.5979 | 442.2932 | 234.4823 | 228.2559 | 231.8505
6037.5979 | 442.1139 | 234.3917 | 228.2013 | 231.8413
6038.5979 | 441.8187 | 234.4068 | 228.2798 | 231.7612
6039.5979 | 441.4956 | 234.4562 | 228.3539 | 231.7726
6040.5979 | 441.3245 | 234.5453 | 228.3096 | 231.8654
6041.5979 | 441.1755 | 234.6534 | 228.1864 | 231.803
6042.5979 | 441.0681 | 234.5564 | 227.998 | 231.7098
6043.5979 | 440.9196 | 234.1639 | 227.7444 | 231.6806
6044.5979 | 440.9003 | 234.0563 | 227.5421 | 231.7267
6045.5979 | 440.7883 | 233.9384 | 227.4701 | 231.6909
6046.5979 | 440.6713 | 233.9373 | 227.4443 | 231.6023
6047.5979 | 440.4894 | 233.7739 | 227.4419 | 231.5789
6048.5979 | 440.1797 | 233.7955 | 227.2691 | 231.4942
6049.5979 | 439.9584 | 233.866 | 227.1546 | 231.4194
6050.5979 | 439.6941 | 233.6641 | 226.9267 | 231.373
6051.5979 | 439.3917 | 233.5967 | 226.6989 | 231.3788
6052.5979 | 439.1087 | 233.5617 | 226.5551 | 231.2341
6053.5979 | 438.7658 | 233.4035 | 226.349 | 231.2757
6054.5979 | 438.431 | 233.3442 | 226.2769 | 231.3031
6055.5979 | 438.1825 | 233.3473 | 226.2024 | 231.3013
6056.5979 | 438.0054 | 233.3932 | 226.1728 | 231.2677
6057.5979 | 437.9334 | 233.4937 | 226.2552 | 231.2377
6058.5979 | 437.7774 | 233.5398 | 226.3875 | 231.1336
6059.5979 | 437.5346 | 233.5971 | 226.3962 | 231.0179
6060.5979 | 437.1625 | 233.3814 | 226.2747 | 231.0231