## Test Conditions
DESIREE-FIRE Intermediate Scale Test 3 - Circuit Simulator Data Only
Test Date: | 2010-02-17
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:27
Fire Time | 14:05
Offset | 0:40 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2390 | seconds
Heat Source Offset | 0:38 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2266 | seconds
Heat Source Stop Time | 15:01
Test Duration | 0:56 | hours:minutes:seconds
| 3370 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 0 represents the air temperature in the middle of the cable tray located in A Position. It is labeled as "A Position - Middle".
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-1.4844 | 121.5912 | -60.7132 | 60.7452 | 0.044018 | -0.035942 | 0.006315 | -0.057066 | 0.082044 | 0.030642 | -0.08103 | 60.6626 | 60.6387 | 60.658 | 60.575 | 60.6999 | 60.8154 | 60.415 | 60.5477 | 60.7572 | 60.6773 | 60.7195 | 60.6561 | 60.7952 | 60.7438 | 60.6322 | 60.6809 | 60.657 | 60.6763 | 60.5933 | 60.7182 | 60.8337 | 60.4333 | 60.5661 | -0.037267 | 0.24764 | -0.041876 | 0.24303
0.25 | 121.637 | -60.7315 | 60.6857 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.085608 | 60.6718 | 60.6295 | 60.658 | 60.5566 | 60.6861 | 60.8108 | 60.4241 | 60.5386 | 60.7755 | 60.6864 | 60.7332 | 60.679 | 60.8136 | 60.7759 | 60.6459 | 60.6901 | 60.6478 | 60.6763 | 60.575 | 60.7045 | 60.8291 | 60.4424 | 60.5569 | -0.014376 | 0.24764 | -0.028142 | 0.23387
1.9062 | 121.5363 | -60.7956 | 60.704 | 0.044018 | -0.040521 | 0.001736 | -0.047909 | 0.072888 | 0.039799 | -0.071874 | 60.658 | 60.6341 | 60.658 | 60.5658 | 60.6999 | 60.8154 | 60.4195 | 60.5432 | 60.8396 | 60.7551 | 60.7973 | 60.7477 | 60.8685 | 60.8354 | 60.7237 | 60.6763 | 60.6524 | 60.6763 | 60.5841 | 60.7182 | 60.8337 | 60.4379 | 60.5615 | -0.041845 | 0.23848 | -0.041876 | 0.23845
3.625 | 121.5775 | -60.759 | 60.6995 | 0.053175 | -0.035942 | 0.010893 | -0.043331 | 0.077466 | 0.048956 | -0.08103 | 60.6672 | 60.6341 | 60.6534 | 60.5704 | 60.6999 | 60.8108 | 60.4241 | 60.5386 | 60.8121 | 60.723 | 60.7699 | 60.7156 | 60.8364 | 60.8079 | 60.6779 | 60.6855 | 60.6524 | 60.6717 | 60.5887 | 60.7182 | 60.8291 | 60.4424 | 60.5569 | -0.032688 | 0.24306 | -0.046454 | 0.22929
5.2812 | 121.6187 | -60.7407 | 60.7086 | 0.044018 | -0.040521 | 0.010893 | -0.052488 | 0.072888 | 0.035221 | -0.08103 | 60.6672 | 60.6387 | 60.6443 | 60.5658 | 60.6907 | 60.8199 | 60.4058 | 60.534 | 60.7847 | 60.7001 | 60.7516 | 60.6882 | 60.8135 | 60.7759 | 60.6596 | 60.6855 | 60.657 | 60.6626 | 60.5841 | 60.709 | 60.8382 | 60.4241 | 60.5523 | -0.023532 | 0.26137 | -0.046455 | 0.23845
7.0156 | 121.582 | -60.7452 | 60.7315 | 0.048597 | -0.035942 | 0.010893 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 60.6672 | 60.6341 | 60.6534 | 60.5566 | 60.6953 | 60.8154 | 60.415 | 60.534 | 60.7938 | 60.7093 | 60.7561 | 60.6928 | 60.8181 | 60.7896 | 60.6688 | 60.6855 | 60.6524 | 60.6717 | 60.575 | 60.7136 | 60.8337 | 60.4333 | 60.5523 | -0.02811 | 0.25222 | -0.041876 | 0.23845
8.6875 | 121.6141 | -60.6949 | 60.7224 | 0.044018 | -0.040521 | 0.015472 | -0.043331 | 0.072888 | 0.039799 | -0.08103 | 60.6672 | 60.6341 | 60.6534 | 60.5612 | 60.6953 | 60.8062 | 60.4195 | 60.5386 | 60.7389 | 60.6544 | 60.7104 | 60.6516 | 60.7678 | 60.7347 | 60.6139 | 60.6855 | 60.6524 | 60.6717 | 60.5795 | 60.7136 | 60.8245 | 60.4379 | 60.5569 | -0.02811 | 0.24764 | -0.041876 | 0.23387
10.4219 | 121.5546 | -60.7544 | 60.7269 | 0.048597 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 60.6672 | 60.6432 | 60.658 | 60.575 | 60.6999 | 60.8108 | 60.4195 | 60.534 | 60.803 | 60.7139 | 60.7607 | 60.7019 | 60.8319 | 60.7942 | 60.6779 | 60.6855 | 60.6615 | 60.6763 | 60.5933 | 60.7182 | 60.8291 | 60.4379 | 60.5523 | -0.032688 | 0.24764 | -0.041876 | 0.23845
12.1406 | 121.6553 | -60.7361 | 60.6995 | 0.048597 | -0.031363 | 0.010893 | -0.052488 | 0.082044 | 0.039799 | -0.08103 | 60.6626 | 60.6295 | 60.658 | 60.5612 | 60.6861 | 60.8108 | 60.4195 | 60.534 | 60.7847 | 60.7047 | 60.747 | 60.6836 | 60.8181 | 60.7759 | 60.6551 | 60.6809 | 60.6478 | 60.6763 | 60.5795 | 60.7045 | 60.8291 | 60.4379 | 60.5523 | -0.023533 | 0.24306 | -0.028142 | 0.23845
13.8125 | 121.6232 | -60.7269 | 60.7452 | 0.048597 | -0.035942 | 0.015472 | -0.057066 | 0.06831 | 0.044377 | -0.076452 | 60.6626 | 60.6341 | 60.6488 | 60.5658 | 60.6907 | 60.8154 | 60.4195 | 60.5386 | 60.7755 | 60.691 | 60.7424 | 60.6699 | 60.7952 | 60.7713 | 60.6505 | 60.6809 | 60.6524 | 60.6672 | 60.5841 | 60.709 | 60.8337 | 60.4379 | 60.5569 | -0.028111 | 0.24306 | -0.041877 | 0.22929
15.5312 | 121.5454 | -60.7864 | 60.7819 | 0.053175 | -0.040521 | 0.010893 | -0.047909 | 0.072888 | 0.039799 | -0.067295 | 60.6626 | 60.6341 | 60.6534 | 60.5704 | 60.6953 | 60.8062 | 60.4195 | 60.534 | 60.8396 | 60.7459 | 60.7973 | 60.7385 | 60.8593 | 60.8262 | 60.7191 | 60.6809 | 60.6524 | 60.6717 | 60.5887 | 60.7136 | 60.8245 | 60.4379 | 60.5523 | -0.032689 | 0.24306 | -0.041876 | 0.23387
17.2656 | 121.637 | -60.7498 | 60.6812 | 0.044018 | -0.040521 | 0.015472 | -0.047909 | 0.072888 | 0.048956 | -0.08103 | 60.6626 | 60.6341 | 60.658 | 60.5658 | 60.6861 | 60.8108 | 60.415 | 60.5294 | 60.7938 | 60.7093 | 60.7653 | 60.7019 | 60.8227 | 60.7988 | 60.6688 | 60.6809 | 60.6524 | 60.6763 | 60.5841 | 60.7045 | 60.8291 | 60.4333 | 60.5477 | -0.023533 | 0.24764 | -0.028142 | 0.24303
18.9375 | 121.6965 | -60.6995 | 60.7315 | 0.048597 | -0.0451 | 0.010893 | -0.057066 | 0.072888 | 0.035221 | -0.076452 | 60.6626 | 60.6295 | 60.658 | 60.5658 | 60.6953 | 60.8062 | 60.415 | 60.5386 | 60.7481 | 60.6544 | 60.7104 | 60.6424 | 60.7724 | 60.7347 | 60.623 | 60.6809 | 60.6478 | 60.6763 | 60.5841 | 60.7136 | 60.8245 | 60.4333 | 60.5569 | -0.032689 | 0.24764 | -0.037298 | 0.24303
20.6719 | 121.6187 | -60.7132 | 60.7086 | 0.053175 | -0.035942 | 0.010893 | -0.052488 | 0.072888 | 0.039799 | -0.08103 | 60.658 | 60.6249 | 60.6534 | 60.5612 | 60.6861 | 60.8062 | 60.4195 | 60.5294 | 60.7664 | 60.6773 | 60.7241 | 60.6607 | 60.7861 | 60.753 | 60.6322 | 60.6763 | 60.6432 | 60.6717 | 60.5795 | 60.7045 | 60.8245 | 60.4379 | 60.5477 | -0.028111 | 0.23848 | -0.03272 | 0.23387
22.3438 | 121.6553 | -60.7269 | 60.6766 | 0.044018 | -0.035942 | 0.010893 | -0.047909 | 0.072888 | 0.035221 | -0.08103 | 60.6626 | 60.6295 | 60.6534 | 60.5658 | 60.6907 | 60.8062 | 60.4104 | 60.5294 | 60.7709 | 60.691 | 60.7378 | 60.679 | 60.7998 | 60.7621 | 60.6459 | 60.6809 | 60.6478 | 60.6717 | 60.5841 | 60.709 | 60.8245 | 60.4287 | 60.5477 | -0.028111 | 0.25221 | -0.037298 | 0.24303
24.0625 | 121.6736 | -60.7086 | 60.7132 | 0.057754 | -0.0451 | 0.010893 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 60.6626 | 60.6295 | 60.6443 | 60.5658 | 60.6953 | 60.8016 | 60.4195 | 60.5386 | 60.7664 | 60.6635 | 60.7195 | 60.6561 | 60.7861 | 60.753 | 60.6322 | 60.6809 | 60.6478 | 60.6626 | 60.5841 | 60.7136 | 60.8199 | 60.4379 | 60.5569 | -0.032689 | 0.24306 | -0.051033 | 0.22471
25.7188 | 121.5271 | -60.7956 | 60.6995 | 0.048597 | -0.035942 | 0.010893 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 60.6626 | 60.6249 | 60.6534 | 60.5612 | 60.6907 | 60.8108 | 60.415 | 60.5294 | 60.8442 | 60.7597 | 60.8065 | 60.7431 | 60.8731 | 60.8354 | 60.7146 | 60.6809 | 60.6432 | 60.6717 | 60.5795 | 60.709 | 60.8291 | 60.4333 | 60.5477 | -0.028111 | 0.24764 | -0.037298 | 0.23845
27.4375 | 121.6003 | -60.7681 | 60.6857 | 0.053175 | -0.035942 | 0.006315 | -0.052488 | 0.082044 | 0.039799 | -0.085608 | 60.658 | 60.6295 | 60.6534 | 60.5704 | 60.6907 | 60.8154 | 60.4104 | 60.5386 | 60.8213 | 60.7322 | 60.7744 | 60.7156 | 60.8502 | 60.8079 | 60.6825 | 60.6763 | 60.6478 | 60.6717 | 60.5887 | 60.709 | 60.8337 | 60.4287 | 60.5569 | -0.032689 | 0.24764 | -0.037298 | 0.24303
29.1719 | 121.6919 | -60.6949 | 60.7086 | 0.044018 | -0.035942 | 0.010893 | -0.052488 | 0.072888 | 0.035221 | -0.076452 | 60.658 | 60.6295 | 60.6488 | 60.5658 | 60.6953 | 60.8154 | 60.415 | 60.5386 | 60.7389 | 60.6589 | 60.7058 | 60.6424 | 60.7678 | 60.7301 | 60.6184 | 60.6763 | 60.6478 | 60.6672 | 60.5841 | 60.7136 | 60.8337 | 60.4333 | 60.5569 | -0.037267 | 0.24306 | -0.046455 | 0.23387
30.8906 | 121.6507 | -60.7086 | 60.6766 | 0.053175 | -0.040521 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.085608 | 60.6626 | 60.6341 | 60.6488 | 60.5704 | 60.6861 | 60.8108 | 60.4195 | 60.5294 | 60.7618 | 60.6681 | 60.7104 | 60.6607 | 60.7907 | 60.7484 | 60.623 | 60.6809 | 60.6524 | 60.6672 | 60.5887 | 60.7045 | 60.8291 | 60.4379 | 60.5477 | -0.023533 | 0.24306 | -0.037299 | 0.22929
32.5625 | 121.5454 | -60.8047 | 60.704 | 0.053175 | -0.031363 | 0.010893 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 60.6626 | 60.6341 | 60.6488 | 60.5612 | 60.6953 | 60.8016 | 60.4104 | 60.5294 | 60.8579 | 60.7734 | 60.8156 | 60.7568 | 60.8822 | 60.8445 | 60.7283 | 60.6809 | 60.6524 | 60.6672 | 60.5795 | 60.7136 | 60.8199 | 60.4287 | 60.5477 | -0.032689 | 0.25221 | -0.046455 | 0.23845
34.2812 | 121.5363 | -60.7956 | 60.7178 | 0.048597 | -0.035942 | 0.010893 | -0.052488 | 0.082044 | 0.035221 | -0.08103 | 60.6672 | 60.6387 | 60.6488 | 60.5566 | 60.6861 | 60.8062 | 60.4195 | 60.5294 | 60.8442 | 60.7597 | 60.8065 | 60.7431 | 60.8776 | 60.8308 | 60.7146 | 60.6855 | 60.657 | 60.6672 | 60.575 | 60.7045 | 60.8245 | 60.4379 | 60.5477 | -0.018954 | 0.24764 | -0.037299 | 0.22929
36 | 121.5408 | -60.791 | 60.6766 | 0.048597 | -0.031363 | 0.010893 | -0.047909 | 0.086622 | 0.044377 | -0.071874 | 60.6626 | 60.6295 | 60.6488 | 60.5658 | 60.6907 | 60.8154 | 60.415 | 60.534 | 60.8396 | 60.7597 | 60.8019 | 60.7431 | 60.8776 | 60.8354 | 60.7191 | 60.6809 | 60.6478 | 60.6672 | 60.5841 | 60.709 | 60.8337 | 60.4333 | 60.5523 | -0.028111 | 0.24764 | -0.041877 | 0.23387
37.7188 | 121.6324 | -60.7544 | 60.6674 | 0.057754 | -0.040521 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.076452 | 60.6672 | 60.6341 | 60.6534 | 60.5658 | 60.6861 | 60.8062 | 60.4104 | 60.534 | 60.8121 | 60.7139 | 60.7607 | 60.7065 | 60.8273 | 60.7988 | 60.6779 | 60.6855 | 60.6524 | 60.6717 | 60.5841 | 60.7045 | 60.8245 | 60.4287 | 60.5523 | -0.018954 | 0.25679 | -0.03272 | 0.24303
39.4375 | 121.6415 | -60.6995 | 60.6857 | 0.048597 | -0.040521 | 0.010893 | -0.047909 | 0.072888 | 0.039799 | -0.076452 | 60.6626 | 60.6295 | 60.6488 | 60.5704 | 60.6953 | 60.8108 | 60.415 | 60.5294 | 60.7481 | 60.6589 | 60.7104 | 60.6516 | 60.7724 | 60.7393 | 60.623 | 60.6809 | 60.6478 | 60.6672 | 60.5887 | 60.7136 | 60.8291 | 60.4333 | 60.5477 | -0.032689 | 0.24764 | -0.046455 | 0.23387
41.1094 | 121.5591 | -60.7269 | 60.7544 | 0.044018 | -0.040521 | 0.010893 | -0.047909 | 0.072888 | 0.048956 | -0.076452 | 60.6626 | 60.6249 | 60.6488 | 60.5658 | 60.6953 | 60.8062 | 60.4195 | 60.534 | 60.7709 | 60.6864 | 60.7378 | 60.679 | 60.7998 | 60.7759 | 60.6505 | 60.6809 | 60.6432 | 60.6672 | 60.5841 | 60.7136 | 60.8245 | 60.4379 | 60.5523 | -0.032689 | 0.24306 | -0.046455 | 0.22929
42.8125 | 121.6324 | -60.7315 | 60.704 | 0.044018 | -0.035942 | 0.006315 | -0.057066 | 0.072888 | 0.030642 | -0.071874 | 60.6672 | 60.6295 | 60.6443 | 60.5612 | 60.6816 | 60.8062 | 60.4195 | 60.5249 | 60.7755 | 60.6956 | 60.7378 | 60.6744 | 60.8044 | 60.7621 | 60.6596 | 60.6855 | 60.6478 | 60.6626 | 60.5795 | 60.6999 | 60.8245 | 60.4379 | 60.5432 | -0.014376 | 0.24764 | -0.037299 | 0.22471
44.5 | 121.5271 | -60.7498 | 60.7636 | 0.048597 | -0.035942 | 0.015472 | -0.043331 | 0.072888 | 0.035221 | -0.071874 | 60.6672 | 60.6387 | 60.6488 | 60.5658 | 60.6907 | 60.8062 | 60.4195 | 60.534 | 60.7984 | 60.7139 | 60.7653 | 60.7065 | 60.8227 | 60.785 | 60.6779 | 60.6855 | 60.657 | 60.6672 | 60.5841 | 60.709 | 60.8245 | 60.4379 | 60.5523 | -0.023532 | 0.24764 | -0.041877 | 0.22929
46.2188 | 121.637 | -60.7224 | 60.6674 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.072888 | 0.035221 | -0.08103 | 60.6718 | 60.6387 | 60.6443 | 60.5612 | 60.6816 | 60.8062 | 60.415 | 60.5249 | 60.7664 | 60.6818 | 60.7287 | 60.6744 | 60.7952 | 60.7576 | 60.6413 | 60.6901 | 60.657 | 60.6626 | 60.5795 | 60.6999 | 60.8245 | 60.4333 | 60.5432 | -0.009798 | 0.25679 | -0.037299 | 0.22929
47.9531 | 121.5408 | -60.7864 | 60.6995 | 0.044018 | -0.035942 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.071874 | 60.6672 | 60.6432 | 60.6534 | 60.5658 | 60.6953 | 60.8016 | 60.4058 | 60.5294 | 60.8305 | 60.7505 | 60.7928 | 60.7431 | 60.8685 | 60.8308 | 60.7146 | 60.6855 | 60.6615 | 60.6717 | 60.5841 | 60.7136 | 60.8199 | 60.4241 | 60.5477 | -0.02811 | 0.26137 | -0.041876 | 0.24761
49.6094 | 121.5271 | -60.7269 | 60.7407 | 0.048597 | -0.031363 | 0.006315 | -0.043331 | 0.072888 | 0.039799 | -0.085608 | 60.6672 | 60.6341 | 60.658 | 60.575 | 60.6953 | 60.8062 | 60.4195 | 60.5386 | 60.7755 | 60.6956 | 60.7332 | 60.6836 | 60.7998 | 60.7667 | 60.6413 | 60.6855 | 60.6524 | 60.6763 | 60.5933 | 60.7136 | 60.8245 | 60.4379 | 60.5569 | -0.02811 | 0.24764 | -0.037298 | 0.23845
51.3281 | 121.669 | -60.6812 | 60.7224 | 0.048597 | -0.040521 | 0.015472 | -0.043331 | 0.077466 | 0.044377 | -0.085608 | 60.6626 | 60.6341 | 60.6488 | 60.5658 | 60.6907 | 60.8062 | 60.415 | 60.534 | 60.7297 | 60.6406 | 60.6966 | 60.6378 | 60.7586 | 60.7255 | 60.5955 | 60.6809 | 60.6524 | 60.6672 | 60.5841 | 60.709 | 60.8245 | 60.4333 | 60.5523 | -0.028111 | 0.24764 | -0.041877 | 0.23387
53.0625 | 121.5729 | -60.759 | 60.7224 | 0.062332 | -0.035942 | 0.010893 | -0.047909 | 0.077466 | 0.039799 | -0.085608 | 60.6626 | 60.6295 | 60.6488 | 60.5566 | 60.6907 | 60.8016 | 60.4058 | 60.5249 | 60.8213 | 60.723 | 60.7699 | 60.7111 | 60.8364 | 60.7988 | 60.6734 | 60.6809 | 60.6478 | 60.6672 | 60.575 | 60.709 | 60.8199 | 60.4241 | 60.5432 | -0.028111 | 0.25679 | -0.041877 | 0.24303
54.7344 | 121.669 | -60.6903 | 60.6949 | 0.053175 | -0.035942 | 0.010893 | -0.047909 | 0.082044 | 0.044377 | -0.085608 | 60.658 | 60.6295 | 60.6534 | 60.5658 | 60.6907 | 60.8154 | 60.415 | 60.5477 | 60.7435 | 60.6544 | 60.7012 | 60.6424 | 60.7724 | 60.7347 | 60.6047 | 60.6763 | 60.6478 | 60.6717 | 60.5841 | 60.709 | 60.8337 | 60.4333 | 60.5661 | -0.032689 | 0.24306 | -0.037298 | 0.23845
56.4531 | 121.6278 | -60.7269 | 60.7132 | 0.044018 | -0.0451 | 0.010893 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 60.6626 | 60.6341 | 60.6534 | 60.5566 | 60.6953 | 60.797 | 60.415 | 60.534 | 60.7709 | 60.6818 | 60.7378 | 60.679 | 60.8044 | 60.7667 | 60.6505 | 60.6809 | 60.6524 | 60.6717 | 60.575 | 60.7136 | 60.8154 | 60.4333 | 60.5523 | -0.032689 | 0.24764 | -0.041876 | 0.23845
58.1875 | 121.5363 | -60.7498 | 60.7773 | 0.03944 | -0.040521 | 0.010893 | -0.043331 | 0.082044 | 0.048956 | -0.076452 | 60.6626 | 60.6249 | 60.6534 | 60.5566 | 60.6907 | 60.8062 | 60.4241 | 60.534 | 60.7893 | 60.7093 | 60.7607 | 60.7065 | 60.8319 | 60.7988 | 60.6734 | 60.6809 | 60.6432 | 60.6717 | 60.575 | 60.709 | 60.8245 | 60.4424 | 60.5523 | -0.028111 | 0.23848 | -0.037298 | 0.22929
59.9219 | 121.6141 | -60.704 | 60.7224 | 0.048597 | -0.035942 | 0.015472 | -0.047909 | 0.06831 | 0.044377 | -0.08103 | 60.6626 | 60.6249 | 60.6534 | 60.5566 | 60.6861 | 60.8016 | 60.4195 | 60.5294 | 60.7526 | 60.6681 | 60.7195 | 60.6561 | 60.7724 | 60.7484 | 60.623 | 60.6809 | 60.6432 | 60.6717 | 60.575 | 60.7045 | 60.8199 | 60.4379 | 60.5477 | -0.023533 | 0.24306 | -0.03272 | 0.23387
61.5938 | 121.5591 | -60.7452 | 60.7452 | 0.03944 | -0.035942 | 0.010893 | -0.047909 | 0.082044 | 0.039799 | -0.071874 | 60.6718 | 60.6341 | 60.6534 | 60.5566 | 60.6999 | 60.797 | 60.4287 | 60.534 | 60.7847 | 60.7093 | 60.7561 | 60.6973 | 60.8273 | 60.785 | 60.6734 | 60.6901 | 60.6524 | 60.6717 | 60.575 | 60.7182 | 60.8154 | 60.447 | 60.5523 | -0.02811 | 0.24306 | -0.046454 | 0.22471
63.3281 | 121.5225 | -60.8002 | 60.6766 | 0.048597 | -0.031363 | 0.015472 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6295 | 60.6534 | 60.5612 | 60.6816 | 60.8062 | 60.415 | 60.5294 | 60.8488 | 60.7688 | 60.8156 | 60.7523 | 60.8822 | 60.8445 | 60.7237 | 60.6809 | 60.6478 | 60.6717 | 60.5795 | 60.6999 | 60.8245 | 60.4333 | 60.5477 | -0.018955 | 0.24764 | -0.028142 | 0.23845
65 | 121.5866 | -60.6995 | 60.7773 | 0.044018 | -0.031363 | 0.015472 | -0.043331 | 0.072888 | 0.048956 | -0.076452 | 60.6626 | 60.6295 | 60.6488 | 60.5658 | 60.6953 | 60.8062 | 60.415 | 60.5294 | 60.7435 | 60.6681 | 60.7149 | 60.6561 | 60.7724 | 60.7484 | 60.623 | 60.6809 | 60.6478 | 60.6672 | 60.5841 | 60.7136 | 60.8245 | 60.4333 | 60.5477 | -0.032689 | 0.24764 | -0.046455 | 0.23387
66.6562 | 121.6187 | -60.7315 | 60.7178 | 0.044018 | -0.031363 | 0.015472 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 60.658 | 60.6341 | 60.6534 | 60.5475 | 60.6861 | 60.8062 | 60.415 | 60.534 | 60.7755 | 60.7001 | 60.747 | 60.6836 | 60.809 | 60.7759 | 60.6551 | 60.6763 | 60.6524 | 60.6717 | 60.5658 | 60.7045 | 60.8245 | 60.4333 | 60.5523 | -0.028111 | 0.24306 | -0.03272 | 0.23845
68.3906 | 121.5866 | -60.7315 | 60.7132 | 0.053175 | -0.040521 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.071874 | 60.658 | 60.6341 | 60.658 | 60.5612 | 60.6907 | 60.8016 | 60.4241 | 60.5386 | 60.7847 | 60.691 | 60.7378 | 60.6836 | 60.809 | 60.7713 | 60.6596 | 60.6763 | 60.6524 | 60.6763 | 60.5795 | 60.709 | 60.8199 | 60.4424 | 60.5569 | -0.032689 | 0.2339 | -0.03272 | 0.23387
70.0625 | 121.5363 | -60.7956 | 60.6995 | 0.048597 | -0.040521 | 0.006315 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6341 | 60.6488 | 60.5658 | 60.6907 | 60.8062 | 60.415 | 60.5294 | 60.8442 | 60.7551 | 60.8019 | 60.7477 | 60.8776 | 60.84 | 60.7191 | 60.6809 | 60.6524 | 60.6672 | 60.5841 | 60.709 | 60.8245 | 60.4333 | 60.5477 | -0.028111 | 0.24764 | -0.041877 | 0.23387
71.7344 | 121.6232 | -60.7086 | 60.7452 | 0.044018 | -0.035942 | 0.010893 | -0.047909 | 0.077466 | 0.044377 | -0.071874 | 60.6672 | 60.6341 | 60.6534 | 60.5612 | 60.6861 | 60.8016 | 60.415 | 60.534 | 60.7526 | 60.6727 | 60.7195 | 60.6607 | 60.7861 | 60.753 | 60.6367 | 60.6855 | 60.6524 | 60.6717 | 60.5795 | 60.7045 | 60.8199 | 60.4333 | 60.5523 | -0.018954 | 0.25222 | -0.03272 | 0.23845
73.4688 | 121.6415 | -60.7315 | 60.6674 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.077466 | 0.048956 | -0.076452 | 60.6626 | 60.6295 | 60.6534 | 60.5658 | 60.6816 | 60.8016 | 60.415 | 60.5249 | 60.7755 | 60.691 | 60.7378 | 60.6836 | 60.809 | 60.7805 | 60.6551 | 60.6809 | 60.6478 | 60.6717 | 60.5841 | 60.6999 | 60.8199 | 60.4333 | 60.5432 | -0.018955 | 0.24764 | -0.028142 | 0.23845
75.2031 | 121.5363 | -60.7407 | 60.759 | 0.044018 | -0.035942 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6387 | 60.658 | 60.5566 | 60.6861 | 60.797 | 60.4104 | 60.5386 | 60.7847 | 60.7047 | 60.7424 | 60.6928 | 60.8227 | 60.785 | 60.6642 | 60.6809 | 60.657 | 60.6763 | 60.575 | 60.7045 | 60.8154 | 60.4287 | 60.5569 | -0.023533 | 0.25221 | -0.028142 | 0.24761
76.875 | 121.6827 | -60.6949 | 60.7269 | 0.048597 | -0.040521 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.08103 | 60.6718 | 60.6295 | 60.6488 | 60.5521 | 60.6953 | 60.8016 | 60.415 | 60.5249 | 60.7435 | 60.6544 | 60.7012 | 60.647 | 60.7724 | 60.7347 | 60.6139 | 60.6901 | 60.6478 | 60.6672 | 60.5704 | 60.7136 | 60.8199 | 60.4333 | 60.5432 | -0.023532 | 0.25679 | -0.046455 | 0.23387
78.6094 | 121.5408 | -60.7727 | 60.6857 | 0.053175 | -0.035942 | 0.010893 | -0.043331 | 0.082044 | 0.044377 | -0.076452 | 60.6672 | 60.6295 | 60.6534 | 60.5521 | 60.6907 | 60.8062 | 60.4195 | 60.5203 | 60.8259 | 60.7368 | 60.7836 | 60.7294 | 60.8547 | 60.8171 | 60.6963 | 60.6855 | 60.6478 | 60.6717 | 60.5704 | 60.709 | 60.8245 | 60.4379 | 60.5386 | -0.023532 | 0.24764 | -0.037298 | 0.23387
80.3438 | 121.6324 | -60.6812 | 60.7269 | 0.057754 | -0.040521 | 0.010893 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 60.6626 | 60.6341 | 60.6397 | 60.5566 | 60.6861 | 60.8016 | 60.415 | 60.534 | 60.7389 | 60.6406 | 60.692 | 60.6287 | 60.7586 | 60.721 | 60.6001 | 60.6809 | 60.6524 | 60.658 | 60.575 | 60.7045 | 60.8199 | 60.4333 | 60.5523 | -0.023533 | 0.24764 | -0.046455 | 0.22472
82 | 121.6095 | -60.7178 | 60.6903 | 0.057754 | -0.035942 | 0.006315 | -0.052488 | 0.082044 | 0.039799 | -0.08103 | 60.6626 | 60.6341 | 60.6534 | 60.5612 | 60.6907 | 60.8016 | 60.415 | 60.534 | 60.7755 | 60.6818 | 60.7241 | 60.6653 | 60.7998 | 60.7576 | 60.6367 | 60.6809 | 60.6524 | 60.6717 | 60.5795 | 60.709 | 60.8199 | 60.4333 | 60.5523 | -0.028111 | 0.24764 | -0.037298 | 0.23845
83.6875 | 121.6415 | -60.6857 | 60.7269 | 0.048597 | -0.040521 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.085608 | 60.6626 | 60.6295 | 60.6488 | 60.5475 | 60.6907 | 60.8016 | 60.4104 | 60.5386 | 60.7343 | 60.6452 | 60.6875 | 60.6378 | 60.7632 | 60.7255 | 60.6001 | 60.6809 | 60.6478 | 60.6672 | 60.5658 | 60.709 | 60.8199 | 60.4287 | 60.5569 | -0.028111 | 0.25221 | -0.041877 | 0.23845
85.4062 | 121.6232 | -60.7178 | 60.7132 | 0.048597 | -0.040521 | 0.010893 | -0.047909 | 0.072888 | 0.035221 | -0.076452 | 60.6672 | 60.6249 | 60.6443 | 60.5658 | 60.6861 | 60.8062 | 60.4058 | 60.5294 | 60.7664 | 60.6773 | 60.7287 | 60.6699 | 60.7907 | 60.753 | 60.6413 | 60.6855 | 60.6432 | 60.6626 | 60.5841 | 60.7045 | 60.8245 | 60.4241 | 60.5477 | -0.018954 | 0.26137 | -0.041877 | 0.23845
87.125 | 121.6232 | -60.6949 | 60.7132 | 0.048597 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 60.6489 | 60.6295 | 60.6488 | 60.5566 | 60.6861 | 60.8062 | 60.415 | 60.5294 | 60.7435 | 60.6589 | 60.6966 | 60.6424 | 60.7724 | 60.7347 | 60.6184 | 60.6672 | 60.6478 | 60.6672 | 60.575 | 60.7045 | 60.8245 | 60.4333 | 60.5477 | -0.037268 | 0.2339 | -0.037299 | 0.23387
88.8438 | 121.5271 | -60.7452 | 60.7452 | 0.048597 | -0.040521 | 0.006315 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 60.6626 | 60.6249 | 60.6488 | 60.5612 | 60.6861 | 60.8062 | 60.415 | 60.5386 | 60.7938 | 60.7047 | 60.7516 | 60.6973 | 60.8227 | 60.7896 | 60.6688 | 60.6809 | 60.6432 | 60.6672 | 60.5795 | 60.7045 | 60.8245 | 60.4333 | 60.5569 | -0.023533 | 0.24764 | -0.037299 | 0.23387
90.5625 | 121.5546 | -60.7361 | 60.7132 | 0.044018 | -0.035942 | 0.006315 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 60.6672 | 60.6341 | 60.6488 | 60.5566 | 60.6861 | 60.8016 | 60.415 | 60.5294 | 60.7801 | 60.7001 | 60.7424 | 60.6836 | 60.809 | 60.7805 | 60.6596 | 60.6855 | 60.6524 | 60.6672 | 60.575 | 60.7045 | 60.8199 | 60.4333 | 60.5477 | -0.018954 | 0.25222 | -0.037299 | 0.23387
92.2969 | 121.6415 | -60.6766 | 60.6995 | 0.048597 | -0.035942 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.08103 | 60.6534 | 60.6295 | 60.6534 | 60.5658 | 60.6816 | 60.7925 | 60.4104 | 60.5386 | 60.7252 | 60.6406 | 60.6829 | 60.6241 | 60.7495 | 60.7164 | 60.5955 | 60.6718 | 60.6478 | 60.6717 | 60.5841 | 60.6999 | 60.8108 | 60.4287 | 60.5569 | -0.028112 | 0.24306 | -0.028142 | 0.24303
93.9688 | 121.6553 | -60.6949 | 60.7132 | 0.057754 | -0.035942 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.071874 | 60.6626 | 60.6295 | 60.6443 | 60.5475 | 60.6861 | 60.8016 | 60.415 | 60.5294 | 60.7526 | 60.6589 | 60.6966 | 60.6516 | 60.7724 | 60.7393 | 60.623 | 60.6809 | 60.6478 | 60.6626 | 60.5658 | 60.7045 | 60.8199 | 60.4333 | 60.5477 | -0.023533 | 0.24764 | -0.041877 | 0.22929
95.7031 | 121.6644 | -60.6949 | 60.6949 | 0.044018 | -0.035942 | 0.010893 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 60.6626 | 60.6249 | 60.6488 | 60.5521 | 60.6907 | 60.8016 | 60.4104 | 60.5294 | 60.7389 | 60.6589 | 60.7058 | 60.647 | 60.7724 | 60.7347 | 60.6184 | 60.6809 | 60.6432 | 60.6672 | 60.5704 | 60.709 | 60.8199 | 60.4287 | 60.5477 | -0.028111 | 0.25221 | -0.041877 | 0.23845
97.4375 | 121.6461 | -60.6857 | 60.7178 | 0.048597 | -0.031363 | 0.010893 | -0.043331 | 0.082044 | 0.039799 | -0.076452 | 60.6672 | 60.6295 | 60.6534 | 60.5566 | 60.6907 | 60.8062 | 60.415 | 60.5294 | 60.7343 | 60.6544 | 60.6966 | 60.6424 | 60.7678 | 60.7255 | 60.6093 | 60.6855 | 60.6478 | 60.6717 | 60.575 | 60.709 | 60.8245 | 60.4333 | 60.5477 | -0.023532 | 0.25222 | -0.037298 | 0.23845
99.1094 | 121.5225 | -60.7864 | 60.6903 | 0.053175 | -0.040521 | 0.015472 | -0.038752 | 0.082044 | 0.044377 | -0.08103 | 60.6534 | 60.6295 | 60.6443 | 60.5612 | 60.6816 | 60.8062 | 60.415 | 60.5294 | 60.8396 | 60.7459 | 60.8019 | 60.7477 | 60.8685 | 60.8308 | 60.7054 | 60.6718 | 60.6478 | 60.6626 | 60.5795 | 60.6999 | 60.8245 | 60.4333 | 60.5477 | -0.028112 | 0.23848 | -0.037299 | 0.22929
100.8438 | 121.5225 | -60.7452 | 60.7315 | 0.03944 | -0.0451 | 0.010893 | -0.052488 | 0.082044 | 0.039799 | -0.08103 | 60.6626 | 60.6341 | 60.6443 | 60.5521 | 60.6861 | 60.797 | 60.4012 | 60.5294 | 60.7847 | 60.7001 | 60.7561 | 60.6928 | 60.8273 | 60.785 | 60.6642 | 60.6809 | 60.6524 | 60.6626 | 60.5704 | 60.7045 | 60.8154 | 60.4195 | 60.5477 | -0.023533 | 0.26137 | -0.041877 | 0.24303
102.5781 | 121.582 | -60.7498 | 60.6812 | 0.053175 | -0.031363 | 0.001736 | -0.038752 | 0.082044 | 0.035221 | -0.076452 | 60.658 | 60.6249 | 60.6488 | 60.5521 | 60.6861 | 60.8108 | 60.415 | 60.5203 | 60.803 | 60.7185 | 60.7516 | 60.7111 | 60.8319 | 60.785 | 60.6734 | 60.6763 | 60.6432 | 60.6672 | 60.5704 | 60.7045 | 60.8291 | 60.4333 | 60.5386 | -0.028111 | 0.24306 | -0.037299 | 0.23387
104.25 | 121.6507 | -60.6995 | 60.7315 | 0.048597 | -0.035942 | 0.001736 | -0.047909 | 0.072888 | 0.035221 | -0.076452 | 60.6626 | 60.6249 | 60.6534 | 60.5566 | 60.6861 | 60.8062 | 60.415 | 60.534 | 60.7481 | 60.6635 | 60.7012 | 60.6516 | 60.7724 | 60.7347 | 60.623 | 60.6809 | 60.6432 | 60.6717 | 60.575 | 60.7045 | 60.8245 | 60.4333 | 60.5523 | -0.023533 | 0.24764 | -0.03272 | 0.23845
105.9844 | 121.6232 | -60.6857 | 60.7315 | 0.03944 | -0.035942 | 0.010893 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 60.6626 | 60.6249 | 60.6488 | 60.5612 | 60.6907 | 60.8016 | 60.4104 | 60.5294 | 60.7252 | 60.6498 | 60.6966 | 60.6332 | 60.7632 | 60.7255 | 60.6093 | 60.6809 | 60.6432 | 60.6672 | 60.5795 | 60.709 | 60.8199 | 60.4287 | 60.5477 | -0.028111 | 0.25221 | -0.041877 | 0.23845
107.7188 | 121.6415 | -60.7086 | 60.7224 | 0.048597 | -0.0451 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.071874 | 60.6626 | 60.6341 | 60.6488 | 60.5566 | 60.6907 | 60.8062 | 60.4195 | 60.5249 | 60.7572 | 60.6635 | 60.7149 | 60.6607 | 60.7861 | 60.7484 | 60.6367 | 60.6809 | 60.6524 | 60.6672 | 60.575 | 60.709 | 60.8245 | 60.4379 | 60.5432 | -0.028111 | 0.24306 | -0.041877 | 0.22929
109.4531 | 121.6232 | -60.6903 | 60.7178 | 0.048597 | -0.035942 | 0.010893 | -0.043331 | 0.082044 | 0.048956 | -0.08103 | 60.6626 | 60.6295 | 60.658 | 60.5566 | 60.6861 | 60.8062 | 60.4058 | 60.5294 | 60.7389 | 60.6544 | 60.7012 | 60.647 | 60.7724 | 60.7393 | 60.6093 | 60.6809 | 60.6478 | 60.6763 | 60.575 | 60.7045 | 60.8245 | 60.4241 | 60.5477 | -0.023533 | 0.25679 | -0.028142 | 0.25218
111.125 | 121.5179 | -60.7819 | 60.6995 | 0.053175 | -0.035942 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 60.658 | 60.6295 | 60.6534 | 60.5612 | 60.6816 | 60.797 | 60.4058 | 60.5249 | 60.835 | 60.7459 | 60.7882 | 60.7385 | 60.8639 | 60.8262 | 60.7146 | 60.6763 | 60.6478 | 60.6717 | 60.5795 | 60.6999 | 60.8154 | 60.4241 | 60.5432 | -0.023533 | 0.25221 | -0.028142 | 0.24761
112.8594 | 121.6415 | -60.7315 | 60.6903 | 0.048597 | -0.035942 | 0.006315 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 60.6672 | 60.6249 | 60.6534 | 60.5612 | 60.6861 | 60.8016 | 60.4012 | 60.5294 | 60.7801 | 60.6956 | 60.7378 | 60.6836 | 60.809 | 60.7759 | 60.6551 | 60.6855 | 60.6432 | 60.6717 | 60.5795 | 60.7045 | 60.8199 | 60.4195 | 60.5477 | -0.018954 | 0.26595 | -0.03272 | 0.25218
114.5781 | 121.6507 | -60.6857 | 60.6995 | 0.048597 | -0.040521 | 0.006315 | -0.038752 | 0.082044 | 0.044377 | -0.08103 | 60.6626 | 60.6295 | 60.6534 | 60.5475 | 60.6861 | 60.8108 | 60.415 | 60.5294 | 60.7343 | 60.6452 | 60.692 | 60.647 | 60.7678 | 60.7301 | 60.6047 | 60.6809 | 60.6478 | 60.6717 | 60.5658 | 60.7045 | 60.8291 | 60.4333 | 60.5477 | -0.023533 | 0.24764 | -0.03272 | 0.23845
116.2969 | 121.55 | -60.7727 | 60.704 | 0.048597 | -0.035942 | 0.010893 | -0.047909 | 0.082044 | 0.039799 | -0.067295 | 60.6626 | 60.6249 | 60.6443 | 60.5475 | 60.6861 | 60.797 | 60.4104 | 60.5386 | 60.8213 | 60.7368 | 60.7836 | 60.7248 | 60.8547 | 60.8125 | 60.7054 | 60.6809 | 60.6432 | 60.6626 | 60.5658 | 60.7045 | 60.8154 | 60.4287 | 60.5569 | -0.023533 | 0.25221 | -0.041877 | 0.23387
118.0312 | 121.6003 | -60.7315 | 60.7132 | 0.053175 | -0.040521 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.071874 | 60.6626 | 60.6295 | 60.6443 | 60.5521 | 60.6861 | 60.8062 | 60.4104 | 60.5294 | 60.7847 | 60.691 | 60.7424 | 60.6882 | 60.8044 | 60.7713 | 60.6596 | 60.6809 | 60.6478 | 60.6626 | 60.5704 | 60.7045 | 60.8245 | 60.4287 | 60.5477 | -0.023533 | 0.25221 | -0.041877 | 0.23387
119.7031 | 121.5591 | -60.759 | 60.672 | 0.044018 | -0.035942 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.067295 | 60.6672 | 60.6341 | 60.6488 | 60.5521 | 60.6816 | 60.8016 | 60.4058 | 60.5249 | 60.803 | 60.723 | 60.7607 | 60.7156 | 60.8364 | 60.8033 | 60.6917 | 60.6855 | 60.6524 | 60.6672 | 60.5704 | 60.6999 | 60.8199 | 60.4241 | 60.5432 | -0.014376 | 0.26137 | -0.032721 | 0.24303
121.4219 | 121.5454 | -60.759 | 60.6857 | 0.044018 | -0.035942 | 0.010893 | -0.043331 | 0.082044 | 0.044377 | -0.071874 | 60.658 | 60.6295 | 60.6488 | 60.5566 | 60.6816 | 60.797 | 60.4104 | 60.534 | 60.803 | 60.723 | 60.7699 | 60.7156 | 60.841 | 60.8033 | 60.6871 | 60.6763 | 60.6478 | 60.6672 | 60.575 | 60.6999 | 60.8154 | 60.4287 | 60.5523 | -0.023533 | 0.24764 | -0.032721 | 0.23845
123.0938 | 121.5088 | -60.759 | 60.7407 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.658 | 60.6295 | 60.6488 | 60.5612 | 60.6907 | 60.8062 | 60.4104 | 60.5249 | 60.803 | 60.7185 | 60.7653 | 60.7111 | 60.841 | 60.8033 | 60.6825 | 60.6763 | 60.6478 | 60.6672 | 60.5795 | 60.709 | 60.8245 | 60.4287 | 60.5432 | -0.032689 | 0.24764 | -0.041877 | 0.23845
124.8125 | 121.5134 | -60.7498 | 60.7086 | 0.053175 | -0.031363 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6295 | 60.6443 | 60.5521 | 60.6907 | 60.8062 | 60.4104 | 60.534 | 60.803 | 60.7185 | 60.7516 | 60.6973 | 60.8319 | 60.7942 | 60.6734 | 60.6809 | 60.6478 | 60.6626 | 60.5704 | 60.709 | 60.8245 | 60.4287 | 60.5523 | -0.028111 | 0.25221 | -0.046455 | 0.23387
126.5312 | 121.5729 | -60.7773 | 60.704 | 0.053175 | -0.0451 | 0.010893 | -0.047909 | 0.077466 | 0.048956 | -0.08103 | 60.6718 | 60.6341 | 60.6534 | 60.5612 | 60.6816 | 60.8062 | 60.415 | 60.5249 | 60.8305 | 60.7322 | 60.7882 | 60.7294 | 60.8547 | 60.8262 | 60.6963 | 60.6901 | 60.6524 | 60.6717 | 60.5795 | 60.6999 | 60.8245 | 60.4333 | 60.5432 | -0.009798 | 0.25679 | -0.028142 | 0.23845
128.2031 | 121.5546 | -60.7498 | 60.6995 | 0.048597 | -0.040521 | 0.006315 | -0.043331 | 0.082044 | 0.048956 | -0.071874 | 60.6626 | 60.6295 | 60.6443 | 60.5521 | 60.6861 | 60.8016 | 60.4195 | 60.5294 | 60.7984 | 60.7093 | 60.7561 | 60.7065 | 60.8319 | 60.7988 | 60.6779 | 60.6809 | 60.6478 | 60.6626 | 60.5704 | 60.7045 | 60.8199 | 60.4379 | 60.5477 | -0.023533 | 0.24306 | -0.041877 | 0.22471
129.9219 | 121.5591 | -60.7315 | 60.6949 | 0.053175 | -0.031363 | 0.006315 | -0.043331 | 0.077466 | 0.048956 | -0.076452 | 60.6626 | 60.6341 | 60.6488 | 60.5612 | 60.6907 | 60.8016 | 60.4104 | 60.5294 | 60.7847 | 60.7001 | 60.7378 | 60.6882 | 60.809 | 60.7805 | 60.6551 | 60.6809 | 60.6524 | 60.6672 | 60.5795 | 60.709 | 60.8199 | 60.4287 | 60.5477 | -0.028111 | 0.25221 | -0.041877 | 0.23845
131.5938 | 121.5591 | -60.7498 | 60.672 | 0.048597 | -0.0451 | 0.010893 | -0.038752 | 0.082044 | 0.035221 | -0.071874 | 60.658 | 60.6387 | 60.6488 | 60.5658 | 60.6816 | 60.8062 | 60.4058 | 60.5294 | 60.7984 | 60.7047 | 60.7607 | 60.7111 | 60.8319 | 60.785 | 60.6779 | 60.6763 | 60.657 | 60.6672 | 60.5841 | 60.6999 | 60.8245 | 60.4241 | 60.5477 | -0.023533 | 0.25221 | -0.032721 | 0.24303
133.3281 | 121.6187 | -60.7178 | 60.6857 | 0.03944 | -0.0451 | 0.010893 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6295 | 60.6488 | 60.5566 | 60.677 | 60.8062 | 60.4058 | 60.5249 | 60.7572 | 60.6727 | 60.7287 | 60.6699 | 60.7998 | 60.7621 | 60.6413 | 60.6809 | 60.6478 | 60.6672 | 60.575 | 60.6953 | 60.8245 | 60.4241 | 60.5432 | -0.014377 | 0.25679 | -0.028143 | 0.24303
135.0625 | 121.6232 | -60.7544 | 60.6812 | 0.053175 | -0.035942 | 0.010893 | -0.043331 | 0.072888 | 0.044377 | -0.076452 | 60.658 | 60.6295 | 60.6488 | 60.5566 | 60.677 | 60.8108 | 60.4012 | 60.5249 | 60.8076 | 60.7185 | 60.7653 | 60.7111 | 60.8273 | 60.7988 | 60.6779 | 60.6763 | 60.6478 | 60.6672 | 60.575 | 60.6953 | 60.8291 | 60.4195 | 60.5432 | -0.018955 | 0.25679 | -0.028143 | 0.24761
136.7812 | 121.5134 | -60.7773 | 60.7178 | 0.048597 | -0.040521 | 0.010893 | -0.047909 | 0.082044 | 0.044377 | -0.08103 | 60.6626 | 60.6341 | 60.6443 | 60.5612 | 60.677 | 60.8016 | 60.4012 | 60.5249 | 60.8259 | 60.7368 | 60.7882 | 60.7294 | 60.8593 | 60.8217 | 60.6963 | 60.6809 | 60.6524 | 60.6626 | 60.5795 | 60.6953 | 60.8199 | 60.4195 | 60.5432 | -0.014377 | 0.26137 | -0.032721 | 0.24303
138.5156 | 121.6599 | -60.7086 | 60.6903 | 0.044018 | -0.035942 | 0.006315 | -0.038752 | 0.082044 | 0.044377 | -0.08103 | 60.6626 | 60.6295 | 60.6488 | 60.5521 | 60.677 | 60.8108 | 60.415 | 60.5294 | 60.7526 | 60.6727 | 60.7149 | 60.6699 | 60.7907 | 60.753 | 60.6276 | 60.6809 | 60.6478 | 60.6672 | 60.5704 | 60.6953 | 60.8291 | 60.4333 | 60.5477 | -0.014377 | 0.24764 | -0.028143 | 0.23387
140.1875 | 121.5042 | -60.7819 | 60.7315 | 0.048597 | -0.0451 | 0.006315 | -0.047909 | 0.082044 | 0.048956 | -0.08103 | 60.6626 | 60.6249 | 60.6534 | 60.5612 | 60.6816 | 60.797 | 60.4104 | 60.5203 | 60.8305 | 60.7368 | 60.7882 | 60.734 | 60.8639 | 60.8308 | 60.7008 | 60.6809 | 60.6432 | 60.6717 | 60.5795 | 60.6999 | 60.8154 | 60.4287 | 60.5386 | -0.018955 | 0.25221 | -0.028142 | 0.24303
141.9219 | 121.5134 | -60.7727 | 60.6766 | 0.044018 | -0.026784 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.076452 | 60.6672 | 60.6249 | 60.6488 | 60.5612 | 60.677 | 60.8062 | 60.4104 | 60.5203 | 60.8167 | 60.7459 | 60.779 | 60.7294 | 60.8547 | 60.8125 | 60.6963 | 60.6855 | 60.6432 | 60.6672 | 60.5795 | 60.6953 | 60.8245 | 60.4287 | 60.5386 | -0.009798 | 0.25679 | -0.028143 | 0.23845
143.6719 | 121.6141 | -60.6949 | 60.6995 | 0.03944 | -0.040521 | 0.010893 | -0.038752 | 0.077466 | 0.044377 | -0.071874 | 60.658 | 60.6295 | 60.6488 | 60.5566 | 60.6816 | 60.8062 | 60.415 | 60.5249 | 60.7343 | 60.6544 | 60.7058 | 60.6561 | 60.7724 | 60.7393 | 60.623 | 60.6763 | 60.6478 | 60.6672 | 60.575 | 60.6999 | 60.8245 | 60.4333 | 60.5432 | -0.023533 | 0.24306 | -0.032721 | 0.23387
145.3594 | 121.637 | -60.6674 | 60.7315 | 0.048597 | -0.040521 | 0.010893 | -0.047909 | 0.072888 | 0.039799 | -0.08103 | 60.6626 | 60.6249 | 60.6443 | 60.5566 | 60.6816 | 60.8062 | 60.4104 | 60.534 | 60.716 | 60.6269 | 60.6783 | 60.6195 | 60.7403 | 60.7072 | 60.5864 | 60.6809 | 60.6432 | 60.6626 | 60.575 | 60.6999 | 60.8245 | 60.4287 | 60.5523 | -0.018955 | 0.25221 | -0.037299 | 0.23387
147.0156 | 121.5088 | -60.791 | 60.7086 | 0.044018 | -0.031363 | 0.010893 | -0.038752 | 0.072888 | 0.044377 | -0.076452 | 60.6626 | 60.6295 | 60.6443 | 60.5429 | 60.677 | 60.797 | 60.4058 | 60.5294 | 60.835 | 60.7597 | 60.8019 | 60.7523 | 60.8639 | 60.8354 | 60.7146 | 60.6809 | 60.6478 | 60.6626 | 60.5612 | 60.6953 | 60.8154 | 60.4241 | 60.5477 | -0.014377 | 0.25679 | -0.032721 | 0.23845
148.7031 | 121.5408 | -60.7315 | 60.7178 | 0.053175 | -0.0451 | 0.010893 | -0.038752 | 0.06831 | 0.035221 | -0.076452 | 60.6672 | 60.6249 | 60.6534 | 60.5521 | 60.6907 | 60.797 | 60.4104 | 60.5386 | 60.7847 | 60.6864 | 60.7424 | 60.6928 | 60.7998 | 60.7667 | 60.6551 | 60.6855 | 60.6432 | 60.6717 | 60.5704 | 60.709 | 60.8154 | 60.4287 | 60.5569 | -0.023532 | 0.25679 | -0.037298 | 0.24303
150.4219 | 121.5912 | -60.7636 | 60.6903 | 0.048597 | -0.035942 | 0.001736 | -0.043331 | 0.077466 | 0.048956 | -0.071874 | 60.6626 | 60.6387 | 60.6534 | 60.5521 | 60.6861 | 60.797 | 60.4104 | 60.5294 | 60.8121 | 60.7276 | 60.7653 | 60.7202 | 60.841 | 60.8125 | 60.6917 | 60.6809 | 60.657 | 60.6717 | 60.5704 | 60.7045 | 60.8154 | 60.4287 | 60.5477 | -0.023533 | 0.25221 | -0.03272 | 0.24303
152.0781 | 121.637 | -60.7361 | 60.6628 | 0.048597 | -0.040521 | 0.006315 | -0.047909 | 0.082044 | 0.039799 | -0.076452 | 60.6626 | 60.6341 | 60.6443 | 60.5521 | 60.6861 | 60.8016 | 60.4012 | 60.5203 | 60.7847 | 60.6956 | 60.7424 | 60.6882 | 60.8181 | 60.7759 | 60.6596 | 60.6809 | 60.6524 | 60.6626 | 60.5704 | 60.7045 | 60.8199 | 60.4195 | 60.5386 | -0.023533 | 0.26137 | -0.041877 | 0.24303
153.75 | 121.5729 | -60.7498 | 60.7086 | 0.048597 | -0.040521 | 0.010893 | -0.038752 | 0.077466 | 0.048956 | -0.067295 | 60.6626 | 60.6295 | 60.6488 | 60.5566 | 60.6861 | 60.8016 | 60.415 | 60.5294 | 60.7984 | 60.7093 | 60.7607 | 60.7111 | 60.8273 | 60.7988 | 60.6825 | 60.6809 | 60.6478 | 60.6672 | 60.575 | 60.7045 | 60.8199 | 60.4333 | 60.5477 | -0.023533 | 0.24764 | -0.037299 | 0.23387
155.4688 | 121.6187 | -60.7132 | 60.7269 | 0.044018 | -0.040521 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.076452 | 60.658 | 60.6295 | 60.6534 | 60.5612 | 60.6907 | 60.8062 | 60.4058 | 60.5294 | 60.7572 | 60.6727 | 60.7195 | 60.6699 | 60.7952 | 60.7576 | 60.6367 | 60.6763 | 60.6478 | 60.6717 | 60.5795 | 60.709 | 60.8245 | 60.4241 | 60.5477 | -0.032689 | 0.25221 | -0.037298 | 0.24761
157.125 | 121.5591 | -60.7498 | 60.6903 | 0.044018 | -0.035942 | 0.010893 | -0.038752 | 0.072888 | 0.048956 | -0.071874 | 60.6626 | 60.6341 | 60.6534 | 60.5521 | 60.6861 | 60.797 | 60.4104 | 60.5294 | 60.7938 | 60.7139 | 60.7607 | 60.7111 | 60.8227 | 60.7988 | 60.6779 | 60.6809 | 60.6524 | 60.6717 | 60.5704 | 60.7045 | 60.8154 | 60.4287 | 60.5477 | -0.023533 | 0.25221 | -0.03272 | 0.24303
159.2812 | 121.6553 | -60.7224 | 60.6537 | 0.048597 | -0.031363 | 0.010893 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6341 | 60.6443 | 60.5521 | 60.677 | 60.797 | 60.4058 | 60.5203 | 60.7709 | 60.691 | 60.7332 | 60.6699 | 60.8044 | 60.7667 | 60.6459 | 60.6809 | 60.6524 | 60.6626 | 60.5704 | 60.6953 | 60.8154 | 60.4241 | 60.5386 | -0.014377 | 0.25679 | -0.032721 | 0.23845
161.1719 | 121.6095 | -60.704 | 60.7178 | 0.044018 | -0.035942 | 0.010893 | -0.052488 | 0.086622 | 0.039799 | -0.076452 | 60.6626 | 60.6341 | 60.6443 | 60.5566 | 60.6953 | 60.8062 | 60.4104 | 60.5294 | 60.7481 | 60.6681 | 60.7149 | 60.6516 | 60.7907 | 60.7438 | 60.6276 | 60.6809 | 60.6524 | 60.6626 | 60.575 | 60.7136 | 60.8245 | 60.4287 | 60.5477 | -0.032689 | 0.25221 | -0.051033 | 0.23387
162.8906 | 121.5729 | -60.7498 | 60.6903 | 0.048597 | -0.031363 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.076452 | 60.6534 | 60.6341 | 60.6488 | 60.5521 | 60.6816 | 60.8016 | 60.415 | 60.5249 | 60.7984 | 60.7185 | 60.7561 | 60.7065 | 60.8319 | 60.7942 | 60.6734 | 60.6718 | 60.6524 | 60.6672 | 60.5704 | 60.6999 | 60.8199 | 60.4333 | 60.5432 | -0.028112 | 0.23848 | -0.032721 | 0.23387
164.5469 | 121.6415 | -60.6812 | 60.6903 | 0.048597 | -0.031363 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.08103 | 60.6626 | 60.6203 | 60.6397 | 60.5429 | 60.677 | 60.8016 | 60.4104 | 60.5249 | 60.7297 | 60.6498 | 60.6829 | 60.6378 | 60.7586 | 60.7255 | 60.6001 | 60.6809 | 60.6386 | 60.658 | 60.5612 | 60.6953 | 60.8199 | 60.4287 | 60.5432 | -0.014377 | 0.25221 | -0.037299 | 0.22929
166.2344 | 121.5225 | -60.7727 | 60.6949 | 0.048597 | -0.035942 | 0.006315 | -0.038752 | 0.077466 | 0.048956 | -0.076452 | 60.6534 | 60.6341 | 60.6443 | 60.5521 | 60.6861 | 60.7925 | 60.4104 | 60.5249 | 60.8213 | 60.7368 | 60.779 | 60.734 | 60.8502 | 60.8217 | 60.6963 | 60.6718 | 60.6524 | 60.6626 | 60.5704 | 60.7045 | 60.8108 | 60.4287 | 60.5432 | -0.03269 | 0.24306 | -0.041877 | 0.23387
167.9062 | 121.6187 | -60.6949 | 60.7086 | 0.044018 | -0.026784 | 0.006315 | -0.043331 | 0.077466 | 0.044377 | -0.071874 | 60.6626 | 60.6295 | 60.6443 | 60.5475 | 60.6861 | 60.8108 | 60.4058 | 60.5249 | 60.7389 | 60.6681 | 60.7012 | 60.6516 | 60.7724 | 60.7393 | 60.623 | 60.6809 | 60.6478 | 60.6626 | 60.5658 | 60.7045 | 60.8291 | 60.4241 | 60.5432 | -0.023533 | 0.25679 | -0.041877 | 0.23845
169.5781 | 121.6553 | -60.6766 | 60.7178 | 0.048597 | -0.035942 | 0.006315 | -0.043331 | 0.082044 | 0.048956 | -0.08103 | 60.658 | 60.6295 | 60.6397 | 60.5475 | 60.677 | 60.8016 | 60.415 | 60.5294 | 60.7252 | 60.6406 | 60.6829 | 60.6332 | 60.7586 | 60.7255 | 60.5955 | 60.6763 | 60.6478 | 60.658 | 60.5658 | 60.6953 | 60.8199 | 60.4333 | 60.5477 | -0.018955 | 0.24306 | -0.037299 | 0.22472
171.25 | 121.5363 | -60.7636 | 60.7498 | 0.044018 | -0.026784 | 0.006315 | -0.043331 | 0.077466 | 0.044377 | -0.076452 | 60.6626 | 60.6249 | 60.6534 | 60.5612 | 60.6816 | 60.797 | 60.4104 | 60.5294 | 60.8076 | 60.7368 | 60.7699 | 60.7202 | 60.841 | 60.8079 | 60.6871 | 60.6809 | 60.6432 | 60.6717 | 60.5795 | 60.6999 | 60.8154 | 60.4287 | 60.5477 | -0.018955 | 0.25221 | -0.028142 | 0.24303
172.9219 | 121.6141 | -60.7269 | 60.6491 | 0.048597 | -0.040521 | 0.006315 | -0.043331 | 0.077466 | 0.044377 | -0.08103 | 60.6626 | 60.6295 | 60.6443 | 60.5475 | 60.6816 | 60.797 | 60.4058 | 60.5294 | 60.7755 | 60.6864 | 60.7332 | 60.6836 | 60.8044 | 60.7713 | 60.6459 | 60.6809 | 60.6478 | 60.6626 | 60.5658 | 60.6999 | 60.8154 | 60.4241 | 60.5477 | -0.018955 | 0.25679 | -0.037299 | 0.23845
174.625 | 121.5729 | -60.759 | 60.6903 | 0.048597 | -0.040521 | 0.006315 | -0.038752 | 0.082044 | 0.039799 | -0.076452 | 60.6626 | 60.6341 | 60.6488 | 60.5521 | 60.6861 | 60.797 | 60.4104 | 60.5249 | 60.8076 | 60.7185 | 60.7653 | 60.7202 | 60.841 | 60.7988 | 60.6825 | 60.6809 | 60.6524 | 60.6672 | 60.5704 | 60.7045 | 60.8154 | 60.4287 | 60.5432 | -0.023533 | 0.25221 | -0.037299 | 0.23845
176.2812 | 121.582 | -60.672 | 60.6995 | 0.048597 | -0.040521 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.08103 | 60.6626 | 60.6295 | 60.6488 | 60.5475 | 60.677 | 60.8016 | 60.4058 | 60.5249 | 60.7206 | 60.6315 | 60.6829 | 60.6287 | 60.7449 | 60.7118 | 60.591 | 60.6809 | 60.6478 | 60.6672 | 60.5658 | 60.6953 | 60.8199 | 60.4241 | 60.5432 | -0.014377 | 0.25679 | -0.028143 | 0.24303
177.9375 | 121.5591 | -60.7636 | 60.7315 | 0.057754 | -0.035942 | 0.006315 | -0.043331 | 0.077466 | 0.048956 | -0.076452 | 60.6626 | 60.6249 | 60.6443 | 60.5521 | 60.6816 | 60.797 | 60.4195 | 60.5203 | 60.8213 | 60.7276 | 60.7699 | 60.7202 | 60.841 | 60.8125 | 60.6871 | 60.6809 | 60.6432 | 60.6626 | 60.5704 | 60.6999 | 60.8154 | 60.4379 | 60.5386 | -0.018955 | 0.24306 | -0.037299 | 0.22471
179.5938 | 121.6324 | -60.6949 | 60.7178 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.086622 | 0.044377 | -0.085608 | 60.6534 | 60.6295 | 60.6443 | 60.5521 | 60.6816 | 60.8016 | 60.4058 | 60.5249 | 60.7389 | 60.6544 | 60.7012 | 60.647 | 60.7815 | 60.7393 | 60.6093 | 60.6718 | 60.6478 | 60.6626 | 60.5704 | 60.6999 | 60.8199 | 60.4241 | 60.5432 | -0.028112 | 0.24764 | -0.037299 | 0.23845
181.25 | 121.6553 | -60.6949 | 60.7132 | 0.03944 | -0.040521 | 0.010893 | -0.043331 | 0.082044 | 0.048956 | -0.08103 | 60.6534 | 60.6295 | 60.6488 | 60.5475 | 60.6816 | 60.8016 | 60.4058 | 60.5203 | 60.7343 | 60.6544 | 60.7058 | 60.6516 | 60.7769 | 60.7438 | 60.6139 | 60.6718 | 60.6478 | 60.6672 | 60.5658 | 60.6999 | 60.8199 | 60.4241 | 60.5386 | -0.028112 | 0.24764 | -0.032721 | 0.24303
182.9062 | 121.5637 | -60.7361 | 60.6857 | 0.053175 | -0.035942 | 0.010893 | -0.038752 | 0.082044 | 0.053534 | -0.076452 | 60.658 | 60.6387 | 60.6488 | 60.5521 | 60.6816 | 60.8016 | 60.4104 | 60.5203 | 60.7893 | 60.7001 | 60.747 | 60.6973 | 60.8181 | 60.7896 | 60.6596 | 60.6763 | 60.657 | 60.6672 | 60.5704 | 60.6999 | 60.8199 | 60.4287 | 60.5386 | -0.023533 | 0.24764 | -0.032721 | 0.23845
184.5625 | 121.582 | -60.6995 | 60.7086 | 0.048597 | -0.040521 | 0.006315 | -0.043331 | 0.077466 | 0.044377 | -0.076452 | 60.658 | 60.6295 | 60.6443 | 60.5429 | 60.677 | 60.8016 | 60.4104 | 60.5157 | 60.7481 | 60.6589 | 60.7058 | 60.6561 | 60.7769 | 60.7438 | 60.623 | 60.6763 | 60.6478 | 60.6626 | 60.5612 | 60.6953 | 60.8199 | 60.4287 | 60.534 | -0.018955 | 0.24764 | -0.032721 | 0.23387
186.2656 | 121.5546 | -60.7544 | 60.7224 | 0.048597 | -0.026784 | 0.010893 | -0.043331 | 0.072888 | 0.039799 | -0.08103 | 60.6672 | 60.6249 | 60.6488 | 60.5566 | 60.6724 | 60.797 | 60.4012 | 60.5249 | 60.803 | 60.7276 | 60.7653 | 60.7111 | 60.8273 | 60.7942 | 60.6734 | 60.6855 | 60.6432 | 60.6672 | 60.575 | 60.6907 | 60.8154 | 60.4195 | 60.5432 | -0.005219 | 0.26595 | -0.023564 | 0.24761
187.9531 | 121.6415 | -60.7178 | 60.672 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.077466 | 0.048956 | -0.08103 | 60.6626 | 60.6387 | 60.6443 | 60.5566 | 60.6724 | 60.797 | 60.3967 | 60.5203 | 60.7618 | 60.6773 | 60.7241 | 60.6699 | 60.7952 | 60.7667 | 60.6367 | 60.6809 | 60.657 | 60.6626 | 60.575 | 60.6907 | 60.8154 | 60.415 | 60.5386 | -0.009798 | 0.26595 | -0.028142 | 0.24761
189.6094 | 121.5134 | -60.7361 | 60.7407 | 0.048597 | -0.040521 | 0.010893 | -0.047909 | 0.072888 | 0.048956 | -0.076452 | 60.6626 | 60.6295 | 60.6443 | 60.5612 | 60.6953 | 60.8062 | 60.4058 | 60.5157 | 60.7847 | 60.6956 | 60.747 | 60.6882 | 60.809 | 60.785 | 60.6596 | 60.6809 | 60.6478 | 60.6626 | 60.5795 | 60.7136 | 60.8245 | 60.4241 | 60.534 | -0.032689 | 0.25679 | -0.051033 | 0.23845
191.3125 | 121.6003 | -60.7407 | 60.6445 | 0.053175 | -0.031363 | 0.006315 | -0.052488 | 0.082044 | 0.039799 | -0.08103 | 60.6626 | 60.6341 | 60.6534 | 60.5475 | 60.6816 | 60.7925 | 60.4012 | 60.5203 | 60.7938 | 60.7093 | 60.747 | 60.6882 | 60.8227 | 60.7805 | 60.6596 | 60.6809 | 60.6524 | 60.6717 | 60.5658 | 60.6999 | 60.8108 | 60.4195 | 60.5386 | -0.018955 | 0.26137 | -0.028142 | 0.25218
192.9688 | 121.5225 | -60.759 | 60.7132 | 0.053175 | -0.035942 | 0.010893 | -0.043331 | 0.082044 | 0.048956 | -0.067295 | 60.6626 | 60.6249 | 60.6534 | 60.5521 | 60.6861 | 60.797 | 60.4058 | 60.5203 | 60.8121 | 60.723 | 60.7699 | 60.7156 | 60.841 | 60.8079 | 60.6917 | 60.6809 | 60.6432 | 60.6717 | 60.5704 | 60.7045 | 60.8154 | 60.4241 | 60.5386 | -0.023533 | 0.25679 | -0.03272 | 0.24761
194.625 | 121.5179 | -60.7727 | 60.6812 | 0.044018 | -0.040521 | 0.015472 | -0.043331 | 0.072888 | 0.044377 | -0.076452 | 60.6718 | 60.6249 | 60.6443 | 60.5612 | 60.677 | 60.797 | 60.3921 | 60.5249 | 60.8167 | 60.7322 | 60.7882 | 60.7294 | 60.8456 | 60.8171 | 60.6963 | 60.6901 | 60.6432 | 60.6626 | 60.5795 | 60.6953 | 60.8154 | 60.4104 | 60.5432 | -0.00522 | 0.27969 | -0.032721 | 0.25219
196.2812 | 121.669 | -60.6949 | 60.7178 | 0.053175 | -0.0451 | 0.006315 | -0.047909 | 0.072888 | 0.048956 | -0.085608 | 60.6626 | 60.6295 | 60.6443 | 60.5475 | 60.677 | 60.7925 | 60.4104 | 60.5249 | 60.7481 | 60.6498 | 60.7012 | 60.647 | 60.7678 | 60.7438 | 60.6093 | 60.6809 | 60.6478 | 60.6626 | 60.5658 | 60.6953 | 60.8108 | 60.4287 | 60.5432 | -0.014377 | 0.25221 | -0.032721 | 0.23387
197.9375 | 121.637 | -60.7132 | 60.6857 | 0.044018 | -0.035942 | 0.010893 | -0.043331 | 0.077466 | 0.044377 | -0.071874 | 60.6626 | 60.6295 | 60.6488 | 60.5566 | 60.6816 | 60.8016 | 60.4012 | 60.5203 | 60.7572 | 60.6773 | 60.7241 | 60.6699 | 60.7907 | 60.7576 | 60.6413 | 60.6809 | 60.6478 | 60.6672 | 60.575 | 60.6999 | 60.8199 | 60.4195 | 60.5386 | -0.018955 | 0.26137 | -0.032721 | 0.24761
199.625 | 121.5317 | -60.7636 | 60.704 | 0.048597 | -0.035942 | 0.010893 | -0.043331 | 0.082044 | 0.048956 | -0.08103 | 60.6626 | 60.6387 | 60.6534 | 60.5658 | 60.6724 | 60.8062 | 60.4058 | 60.5157 | 60.8121 | 60.7276 | 60.7744 | 60.7202 | 60.8456 | 60.8125 | 60.6825 | 60.6809 | 60.657 | 60.6717 | 60.5841 | 60.6907 | 60.8245 | 60.4241 | 60.534 | -0.009798 | 0.25679 | -0.018985 | 0.24761
201.3125 | 121.6415 | -60.6354 | 60.704 | 0.044018 | -0.035942 | 0.006315 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.658 | 60.6295 | 60.6443 | 60.5475 | 60.6861 | 60.7925 | 60.4058 | 60.5203 | 60.6794 | 60.5994 | 60.6417 | 60.5875 | 60.7174 | 60.6798 | 60.5589 | 60.6763 | 60.6478 | 60.6626 | 60.5658 | 60.7045 | 60.8108 | 60.4241 | 60.5386 | -0.028111 | 0.25221 | -0.041877 | 0.23845
202.9844 | 121.4996 | -60.7636 | 60.7086 | 0.053175 | -0.035942 | 0.010893 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 60.6626 | 60.6341 | 60.6443 | 60.5475 | 60.6816 | 60.7879 | 60.4012 | 60.5157 | 60.8167 | 60.7276 | 60.7744 | 60.7111 | 60.841 | 60.8079 | 60.6871 | 60.6809 | 60.6524 | 60.6626 | 60.5658 | 60.6999 | 60.8062 | 60.4195 | 60.534 | -0.018955 | 0.26137 | -0.037299 | 0.24303
204.6562 | 121.6553 | -60.6812 | 60.6995 | 0.053175 | -0.040521 | 0.010893 | -0.043331 | 0.072888 | 0.035221 | -0.08103 | 60.6626 | 60.6341 | 60.6534 | 60.5475 | 60.677 | 60.797 | 60.4058 | 60.5203 | 60.7343 | 60.6406 | 60.692 | 60.6378 | 60.754 | 60.7164 | 60.6001 | 60.6809 | 60.6524 | 60.6717 | 60.5658 | 60.6953 | 60.8154 | 60.4241 | 60.5386 | -0.014377 | 0.25679 | -0.023564 | 0.24761
206.3438 | 121.582 | -60.6995 | 60.7132 | 0.044018 | -0.035942 | 0.010893 | -0.047909 | 0.077466 | 0.039799 | -0.071874 | 60.6672 | 60.6387 | 60.6488 | 60.5566 | 60.6816 | 60.8016 | 60.4104 | 60.5203 | 60.7435 | 60.6635 | 60.7104 | 60.6516 | 60.7769 | 60.7393 | 60.6276 | 60.6855 | 60.657 | 60.6672 | 60.575 | 60.6999 | 60.8199 | 60.4287 | 60.5386 | -0.014376 | 0.25679 | -0.032721 | 0.23845
208.0156 | 121.6461 | -60.6949 | 60.6766 | 0.048597 | -0.040521 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.076452 | 60.6672 | 60.6295 | 60.658 | 60.5566 | 60.6724 | 60.8016 | 60.4012 | 60.5157 | 60.7435 | 60.6544 | 60.7012 | 60.647 | 60.7678 | 60.7393 | 60.6184 | 60.6855 | 60.6478 | 60.6763 | 60.575 | 60.6907 | 60.8199 | 60.4195 | 60.534 | -0.005219 | 0.26595 | -0.014407 | 0.25676
209.7031 | 121.637 | -60.6583 | 60.7224 | 0.053175 | -0.040521 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6387 | 60.6534 | 60.5612 | 60.6861 | 60.7925 | 60.4012 | 60.5249 | 60.7114 | 60.6177 | 60.66 | 60.6149 | 60.7403 | 60.7026 | 60.5818 | 60.6809 | 60.657 | 60.6717 | 60.5795 | 60.7045 | 60.8108 | 60.4195 | 60.5432 | -0.023533 | 0.26137 | -0.03272 | 0.25218
211.375 | 121.6187 | -60.6583 | 60.7269 | 0.048597 | -0.040521 | 0.001736 | -0.047909 | 0.072888 | 0.039799 | -0.08103 | 60.6626 | 60.6341 | 60.6488 | 60.5475 | 60.6816 | 60.7925 | 60.4104 | 60.5294 | 60.7069 | 60.6177 | 60.66 | 60.6104 | 60.7312 | 60.6981 | 60.5772 | 60.6809 | 60.6524 | 60.6672 | 60.5658 | 60.6999 | 60.8108 | 60.4287 | 60.5477 | -0.018955 | 0.25221 | -0.032721 | 0.23845
213.0625 | 121.6507 | -60.6628 | 60.6995 | 0.048597 | -0.031363 | 0.006315 | -0.043331 | 0.072888 | 0.044377 | -0.076452 | 60.658 | 60.6387 | 60.6488 | 60.5521 | 60.677 | 60.7925 | 60.3967 | 60.5249 | 60.7114 | 60.6315 | 60.6692 | 60.6195 | 60.7357 | 60.7072 | 60.5864 | 60.6763 | 60.657 | 60.6672 | 60.5704 | 60.6953 | 60.8108 | 60.415 | 60.5432 | -0.018955 | 0.26137 | -0.028143 | 0.25218
214.7188 | 121.5042 | -60.7727 | 60.6903 | 0.053175 | -0.040521 | 0.010893 | -0.047909 | 0.082044 | 0.044377 | -0.08103 | 60.6626 | 60.6387 | 60.6488 | 60.5566 | 60.677 | 60.7833 | 60.4058 | 60.5157 | 60.8259 | 60.7322 | 60.7836 | 60.7248 | 60.8547 | 60.8171 | 60.6917 | 60.6809 | 60.657 | 60.6672 | 60.575 | 60.6953 | 60.8016 | 60.4241 | 60.534 | -0.014377 | 0.25679 | -0.028143 | 0.24303
216.4062 | 121.4905 | -60.7636 | 60.6857 | 0.048597 | -0.031363 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.6626 | 60.6341 | 60.6534 | 60.5521 | 60.6724 | 60.7879 | 60.3967 | 60.5157 | 60.8121 | 60.7322 | 60.7653 | 60.7156 | 60.8456 | 60.8079 | 60.6871 | 60.6809 | 60.6524 | 60.6717 | 60.5704 | 60.6907 | 60.8062 | 60.415 | 60.534 | -0.009798 | 0.26595 | -0.018985 | 0.25676
218.0625 | 121.5454 | -60.7361 | 60.7315 | 0.048597 | -0.035942 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.085608 | 60.6672 | 60.6341 | 60.6534 | 60.5612 | 60.6861 | 60.7925 | 60.4012 | 60.5249 | 60.7847 | 60.7001 | 60.7378 | 60.6928 | 60.8181 | 60.7805 | 60.6505 | 60.6855 | 60.6524 | 60.6717 | 60.5795 | 60.7045 | 60.8108 | 60.4195 | 60.5432 | -0.018954 | 0.26595 | -0.03272 | 0.25218
219.75 | 121.5546 | -60.7407 | 60.6857 | 0.048597 | -0.040521 | 0.006315 | -0.047909 | 0.086622 | 0.039799 | -0.076452 | 60.6626 | 60.6341 | 60.6488 | 60.5612 | 60.677 | 60.7879 | 60.4012 | 60.5249 | 60.7893 | 60.7001 | 60.747 | 60.6928 | 60.8273 | 60.7805 | 60.6642 | 60.6809 | 60.6524 | 60.6672 | 60.5795 | 60.6953 | 60.8062 | 60.4195 | 60.5432 | -0.014377 | 0.26137 | -0.028143 | 0.24761
221.4688 | 121.5775 | -60.6995 | 60.7086 | 0.048597 | -0.031363 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 60.6672 | 60.6341 | 60.658 | 60.5566 | 60.677 | 60.7925 | 60.3967 | 60.5111 | 60.7481 | 60.6681 | 60.7012 | 60.647 | 60.7724 | 60.7393 | 60.623 | 60.6855 | 60.6524 | 60.6763 | 60.575 | 60.6953 | 60.8108 | 60.415 | 60.5294 | -0.009798 | 0.27053 | -0.018986 | 0.26134
223.1406 | 121.6324 | -60.6674 | 60.7224 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 60.6626 | 60.6432 | 60.6534 | 60.5704 | 60.6816 | 60.7879 | 60.3967 | 60.5203 | 60.7114 | 60.6269 | 60.6737 | 60.6195 | 60.7449 | 60.7072 | 60.591 | 60.6809 | 60.6615 | 60.6717 | 60.5887 | 60.6999 | 60.8062 | 60.415 | 60.5386 | -0.018955 | 0.26595 | -0.028142 | 0.25676
224.875 | 121.5912 | -60.6949 | 60.7178 | 0.048597 | -0.040521 | 0.006315 | -0.043331 | 0.072888 | 0.039799 | -0.076452 | 60.6672 | 60.6387 | 60.6488 | 60.5521 | 60.6724 | 60.797 | 60.3967 | 60.502 | 60.7435 | 60.6544 | 60.7012 | 60.6516 | 60.7678 | 60.7347 | 60.6184 | 60.6855 | 60.657 | 60.6672 | 60.5704 | 60.6907 | 60.8154 | 60.415 | 60.5203 | -0.005219 | 0.27053 | -0.023564 | 0.25218
226.5781 | 121.637 | -60.6903 | 60.6766 | 0.044018 | -0.040521 | -0.002842 | -0.047909 | 0.077466 | 0.048956 | -0.067295 | 60.6672 | 60.6387 | 60.658 | 60.5566 | 60.6678 | 60.7879 | 60.3875 | 60.5111 | 60.7343 | 60.6498 | 60.6875 | 60.6424 | 60.7678 | 60.7393 | 60.623 | 60.6855 | 60.657 | 60.6763 | 60.575 | 60.6861 | 60.8062 | 60.4058 | 60.5294 | -0.000641 | 0.27969 | -0.009829 | 0.2705
228.25 | 121.6507 | -60.6674 | 60.7269 | 0.048597 | -0.040521 | 0.010893 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 60.6763 | 60.6341 | 60.6534 | 60.5566 | 60.677 | 60.7879 | 60.4012 | 60.5157 | 60.716 | 60.6269 | 60.6783 | 60.6195 | 60.7449 | 60.7072 | 60.591 | 60.6947 | 60.6524 | 60.6717 | 60.575 | 60.6953 | 60.8062 | 60.4195 | 60.534 | -0.000641 | 0.27511 | -0.023564 | 0.25218
229.9531 | 121.6232 | -60.704 | 60.6903 | 0.053175 | -0.040521 | 0.006315 | -0.047909 | 0.072888 | 0.048956 | -0.08103 | 60.6718 | 60.6432 | 60.658 | 60.5521 | 60.6632 | 60.7925 | 60.3967 | 60.5065 | 60.7572 | 60.6635 | 60.7104 | 60.6561 | 60.7769 | 60.753 | 60.623 | 60.6901 | 60.6615 | 60.6763 | 60.5704 | 60.6816 | 60.8108 | 60.415 | 60.5249 | 0.008515 | 0.27511 | -0.005251 | 0.26134
231.6406 | 121.5134 | -60.7178 | 60.7407 | 0.044018 | -0.035942 | 0.010893 | -0.043331 | 0.072888 | 0.048956 | -0.08103 | 60.6763 | 60.6432 | 60.6534 | 60.5566 | 60.6724 | 60.7787 | 60.3967 | 60.5111 | 60.7618 | 60.6818 | 60.7287 | 60.6744 | 60.7907 | 60.7667 | 60.6367 | 60.6947 | 60.6615 | 60.6717 | 60.575 | 60.6907 | 60.797 | 60.415 | 60.5294 | 0.003938 | 0.27969 | -0.018985 | 0.25676
233.3125 | 121.5454 | -60.7361 | 60.6949 | 0.053175 | -0.040521 | 0.006315 | -0.043331 | 0.072888 | 0.048956 | -0.076452 | 60.6763 | 60.6432 | 60.658 | 60.5612 | 60.6678 | 60.7879 | 60.3921 | 60.5111 | 60.7893 | 60.6956 | 60.7424 | 60.6928 | 60.809 | 60.785 | 60.6596 | 60.6947 | 60.6615 | 60.6763 | 60.5795 | 60.6861 | 60.8062 | 60.4104 | 60.5294 | 0.008516 | 0.28427 | -0.009829 | 0.26592
234.9844 | 121.5912 | -60.7178 | 60.6995 | 0.053175 | -0.035942 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 60.6718 | 60.6432 | 60.6534 | 60.5612 | 60.6724 | 60.7833 | 60.3921 | 60.502 | 60.7709 | 60.6818 | 60.7195 | 60.6653 | 60.7998 | 60.7621 | 60.6413 | 60.6901 | 60.6615 | 60.6717 | 60.5795 | 60.6907 | 60.8016 | 60.4104 | 60.5203 | -0.000641 | 0.27969 | -0.018985 | 0.26134
236.6562 | 121.5179 | -60.7407 | 60.7178 | 0.053175 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 60.6763 | 60.6432 | 60.658 | 60.5704 | 60.6632 | 60.7787 | 60.3921 | 60.5065 | 60.7938 | 60.7001 | 60.747 | 60.6882 | 60.8181 | 60.785 | 60.6642 | 60.6947 | 60.6615 | 60.6763 | 60.5887 | 60.6816 | 60.797 | 60.4104 | 60.5249 | 0.013094 | 0.28427 | -0.005251 | 0.26592
238.3281 | 121.5042 | -60.7315 | 60.7681 | 0.048597 | -0.040521 | 0.001736 | -0.043331 | 0.06831 | 0.044377 | -0.08103 | 60.6809 | 60.657 | 60.6626 | 60.5612 | 60.6678 | 60.7787 | 60.3967 | 60.5111 | 60.7801 | 60.691 | 60.7332 | 60.6882 | 60.7998 | 60.7759 | 60.6505 | 60.6992 | 60.6753 | 60.6809 | 60.5795 | 60.6861 | 60.797 | 60.415 | 60.5294 | 0.013094 | 0.28426 | -0.005251 | 0.26592
239.9844 | 121.6232 | -60.6995 | 60.6903 | 0.03944 | -0.026784 | 0.006315 | -0.047909 | 0.072888 | 0.030642 | -0.076452 | 60.6763 | 60.6387 | 60.6626 | 60.5658 | 60.6632 | 60.7787 | 60.3829 | 60.502 | 60.7389 | 60.6727 | 60.7058 | 60.6516 | 60.7724 | 60.7301 | 60.623 | 60.6947 | 60.657 | 60.6809 | 60.5841 | 60.6816 | 60.797 | 60.4012 | 60.5203 | 0.013094 | 0.29342 | -0.000673 | 0.27965
241.6562 | 121.5866 | -60.6949 | 60.6995 | 0.048597 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.035221 | -0.076452 | 60.6855 | 60.6341 | 60.6672 | 60.5612 | 60.6632 | 60.7787 | 60.3875 | 60.502 | 60.7435 | 60.6498 | 60.7012 | 60.6424 | 60.7724 | 60.7301 | 60.6184 | 60.7038 | 60.6524 | 60.6855 | 60.5795 | 60.6816 | 60.797 | 60.4058 | 60.5203 | 0.022251 | 0.298 | 0.003905 | 0.27965
243.3438 | 121.5591 | -60.7315 | 60.7132 | 0.048597 | -0.0451 | 0.006315 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 60.6809 | 60.657 | 60.6672 | 60.5612 | 60.6587 | 60.7787 | 60.3875 | 60.5111 | 60.7801 | 60.6864 | 60.7378 | 60.6836 | 60.809 | 60.7759 | 60.6551 | 60.6992 | 60.6753 | 60.6855 | 60.5795 | 60.677 | 60.797 | 60.4058 | 60.5294 | 0.02225 | 0.29342 | 0.008483 | 0.27965
245.0312 | 121.4767 | -60.759 | 60.7361 | 0.03944 | -0.035942 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 60.6763 | 60.6478 | 60.6626 | 60.5704 | 60.6587 | 60.7833 | 60.3829 | 60.5065 | 60.7984 | 60.723 | 60.7653 | 60.7065 | 60.8319 | 60.7988 | 60.6825 | 60.6947 | 60.6661 | 60.6809 | 60.5887 | 60.677 | 60.8016 | 60.4012 | 60.5249 | 0.017672 | 0.29342 | 0.003905 | 0.27965
246.7031 | 121.5546 | -60.7224 | 60.7269 | 0.048597 | -0.040521 | 0.006315 | -0.052488 | 0.06831 | 0.035221 | -0.085608 | 60.6855 | 60.6478 | 60.6672 | 60.5704 | 60.6632 | 60.7833 | 60.3829 | 60.502 | 60.7709 | 60.6818 | 60.7287 | 60.6699 | 60.7907 | 60.7576 | 60.6367 | 60.7038 | 60.6661 | 60.6855 | 60.5887 | 60.6816 | 60.8016 | 60.4012 | 60.5203 | 0.022251 | 0.30258 | 0.003905 | 0.28423
248.3906 | 121.5866 | -60.6903 | 60.7452 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.072888 | 0.035221 | -0.08103 | 60.6855 | 60.6478 | 60.6672 | 60.5704 | 60.6541 | 60.7696 | 60.3738 | 60.4928 | 60.7343 | 60.6452 | 60.6966 | 60.6378 | 60.7632 | 60.7255 | 60.6093 | 60.7038 | 60.6661 | 60.6855 | 60.5887 | 60.6724 | 60.7879 | 60.3921 | 60.5111 | 0.031407 | 0.31173 | 0.013061 | 0.29339
250.0938 | 121.55 | -60.7407 | 60.7361 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.072888 | 0.035221 | -0.08103 | 60.6901 | 60.6661 | 60.6717 | 60.5841 | 60.6587 | 60.7696 | 60.3783 | 60.4974 | 60.7847 | 60.7001 | 60.747 | 60.6928 | 60.8135 | 60.7759 | 60.6596 | 60.7084 | 60.6844 | 60.69 | 60.6024 | 60.677 | 60.7879 | 60.3967 | 60.5157 | 0.031407 | 0.31173 | 0.013062 | 0.29339
251.7969 | 121.6187 | -60.7407 | 60.6903 | 0.057754 | -0.049678 | 0.001736 | -0.047909 | 0.072888 | 0.044377 | -0.08103 | 60.6809 | 60.657 | 60.6717 | 60.5704 | 60.6541 | 60.7742 | 60.3783 | 60.4837 | 60.7984 | 60.691 | 60.7424 | 60.6928 | 60.8135 | 60.785 | 60.6596 | 60.6992 | 60.6753 | 60.69 | 60.5887 | 60.6724 | 60.7925 | 60.3967 | 60.502 | 0.026828 | 0.30258 | 0.01764 | 0.29339
253.5156 | 121.6187 | -60.6537 | 60.6949 | 0.048597 | -0.0451 | 0.001736 | -0.052488 | 0.072888 | 0.035221 | -0.08103 | 60.6855 | 60.6615 | 60.6717 | 60.575 | 60.6495 | 60.7696 | 60.3646 | 60.4928 | 60.7023 | 60.6086 | 60.6554 | 60.6012 | 60.7266 | 60.6889 | 60.5727 | 60.7038 | 60.6799 | 60.69 | 60.5933 | 60.6678 | 60.7879 | 60.3829 | 60.5111 | 0.035985 | 0.32089 | 0.022218 | 0.30713
255.1875 | 121.5958 | -60.6812 | 60.7178 | 0.053175 | -0.0451 | 0.001736 | -0.047909 | 0.063733 | 0.044377 | -0.08103 | 60.6992 | 60.657 | 60.6717 | 60.5795 | 60.6495 | 60.7696 | 60.3692 | 60.4837 | 60.7343 | 60.6361 | 60.6829 | 60.6332 | 60.7449 | 60.7255 | 60.6001 | 60.7175 | 60.6753 | 60.69 | 60.5979 | 60.6678 | 60.7879 | 60.3875 | 60.502 | 0.04972 | 0.33005 | 0.022218 | 0.30255
256.875 | 121.582 | -60.6674 | 60.759 | 0.044018 | -0.049678 | -0.007421 | -0.057066 | 0.072888 | 0.035221 | -0.08103 | 60.6947 | 60.657 | 60.6809 | 60.5795 | 60.6449 | 60.765 | 60.3692 | 60.4837 | 60.7114 | 60.6177 | 60.66 | 60.6104 | 60.7403 | 60.7026 | 60.5864 | 60.713 | 60.6753 | 60.6992 | 60.5979 | 60.6632 | 60.7833 | 60.3875 | 60.502 | 0.049721 | 0.32547 | 0.035953 | 0.3117
258.5312 | 121.4951 | -60.7361 | 60.7498 | 0.044018 | -0.040521 | 0.006315 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 60.6992 | 60.6661 | 60.6809 | 60.5887 | 60.6404 | 60.7604 | 60.3646 | 60.4791 | 60.7801 | 60.6956 | 60.7424 | 60.6882 | 60.8181 | 60.7805 | 60.6596 | 60.7175 | 60.6844 | 60.6992 | 60.607 | 60.6587 | 60.7787 | 60.3829 | 60.4974 | 0.058877 | 0.33463 | 0.040531 | 0.31628
260.2188 | 121.5866 | -60.6445 | 60.7315 | 0.048597 | -0.0451 | 0.001736 | -0.052488 | 0.059155 | 0.039799 | -0.08103 | 60.7038 | 60.6661 | 60.6855 | 60.5795 | 60.6404 | 60.7558 | 60.3646 | 60.4837 | 60.6931 | 60.5994 | 60.6463 | 60.592 | 60.7037 | 60.6843 | 60.5635 | 60.7221 | 60.6844 | 60.7038 | 60.5979 | 60.6587 | 60.7742 | 60.3829 | 60.502 | 0.063456 | 0.33921 | 0.045109 | 0.32086
261.9062 | 121.5958 | -60.672 | 60.7224 | 0.048597 | -0.0451 | 0.006315 | -0.057066 | 0.077466 | 0.039799 | -0.08103 | 60.7038 | 60.6753 | 60.69 | 60.5887 | 60.6404 | 60.7558 | 60.3646 | 60.4791 | 60.7206 | 60.6269 | 60.6783 | 60.6149 | 60.7495 | 60.7118 | 60.591 | 60.7221 | 60.6936 | 60.7084 | 60.607 | 60.6587 | 60.7742 | 60.3829 | 60.4974 | 0.063456 | 0.33921 | 0.049688 | 0.32544
263.5625 | 121.5042 | -60.6812 | 60.7864 | 0.053175 | -0.040521 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 60.7084 | 60.6661 | 60.6855 | 60.5887 | 60.6404 | 60.7604 | 60.3738 | 60.4837 | 60.7343 | 60.6406 | 60.6829 | 60.6332 | 60.7586 | 60.721 | 60.6047 | 60.7267 | 60.6844 | 60.7038 | 60.607 | 60.6587 | 60.7787 | 60.3921 | 60.502 | 0.068034 | 0.33463 | 0.045109 | 0.3117
265.2344 | 121.5088 | -60.6812 | 60.8002 | 0.048597 | -0.0451 | -0.002842 | -0.052488 | 0.077466 | 0.030642 | -0.085608 | 60.7175 | 60.6707 | 60.6946 | 60.5979 | 60.6358 | 60.7513 | 60.3555 | 60.4745 | 60.7297 | 60.6361 | 60.6783 | 60.6287 | 60.7586 | 60.7118 | 60.5955 | 60.7359 | 60.689 | 60.7129 | 60.6162 | 60.6541 | 60.7696 | 60.3738 | 60.4928 | 0.081769 | 0.3621 | 0.058844 | 0.33917
266.9531 | 121.5317 | -60.704 | 60.759 | 0.053175 | -0.0451 | -0.007421 | -0.061645 | 0.077466 | 0.035221 | -0.085608 | 60.713 | 60.6799 | 60.6946 | 60.6024 | 60.6404 | 60.7467 | 60.3555 | 60.4699 | 60.7572 | 60.6589 | 60.6966 | 60.6424 | 60.7815 | 60.7393 | 60.6184 | 60.7313 | 60.6982 | 60.7129 | 60.6207 | 60.6587 | 60.765 | 60.3738 | 60.4882 | 0.072613 | 0.35752 | 0.054266 | 0.33917
268.6875 | 121.6324 | -60.6628 | 60.7224 | 0.03944 | -0.054257 | -0.012 | -0.061645 | 0.06831 | 0.035221 | -0.08103 | 60.713 | 60.6844 | 60.6992 | 60.6024 | 60.622 | 60.7467 | 60.3509 | 60.4608 | 60.7023 | 60.6086 | 60.6508 | 60.6012 | 60.7312 | 60.6981 | 60.5818 | 60.7313 | 60.7028 | 60.7175 | 60.6207 | 60.6404 | 60.765 | 60.3692 | 60.4791 | 0.090925 | 0.3621 | 0.077156 | 0.34833
270.3594 | 121.5454 | -60.704 | 60.7452 | 0.057754 | -0.049678 | 0.001736 | -0.052488 | 0.06831 | 0.035221 | -0.085608 | 60.7221 | 60.6936 | 60.7084 | 60.6116 | 60.6266 | 60.7375 | 60.3509 | 60.4608 | 60.7618 | 60.6544 | 60.7058 | 60.6516 | 60.7724 | 60.7393 | 60.6184 | 60.7404 | 60.7119 | 60.7267 | 60.6299 | 60.6449 | 60.7558 | 60.3692 | 60.4791 | 0.095504 | 0.37125 | 0.081735 | 0.35749
272.0312 | 121.5408 | -60.6583 | 60.7864 | 0.03944 | -0.0451 | 0.001736 | -0.057066 | 0.063733 | 0.035221 | -0.08103 | 60.7313 | 60.6936 | 60.7175 | 60.6116 | 60.6175 | 60.733 | 60.3509 | 60.4516 | 60.6977 | 60.6132 | 60.66 | 60.6012 | 60.722 | 60.6935 | 60.5772 | 60.7496 | 60.7119 | 60.7358 | 60.6299 | 60.6358 | 60.7513 | 60.3692 | 60.4699 | 0.11382 | 0.38041 | 0.10005 | 0.36664
273.7188 | 121.5912 | -60.6308 | 60.7773 | 0.044018 | -0.054257 | 0.001736 | -0.052488 | 0.063733 | 0.026064 | -0.090186 | 60.7313 | 60.6982 | 60.7129 | 60.6162 | 60.6083 | 60.7238 | 60.3326 | 60.4562 | 60.6748 | 60.5765 | 60.6325 | 60.5783 | 60.6945 | 60.6569 | 60.5406 | 60.7496 | 60.7165 | 60.7312 | 60.6345 | 60.6266 | 60.7421 | 60.3509 | 60.4745 | 0.12297 | 0.39873 | 0.10463 | 0.38038
275.3906 | 121.5683 | -60.6079 | 60.7681 | 0.048597 | -0.058836 | 0.006315 | -0.061645 | 0.06831 | 0.026064 | -0.085608 | 60.7359 | 60.7119 | 60.7175 | 60.6299 | 60.5946 | 60.7238 | 60.3188 | 60.4424 | 60.6565 | 60.5491 | 60.6142 | 60.5463 | 60.6762 | 60.634 | 60.5223 | 60.7542 | 60.7302 | 60.7358 | 60.6482 | 60.6129 | 60.7421 | 60.3371 | 60.4608 | 0.14129 | 0.41704 | 0.12294 | 0.39869
277.0781 | 121.5683 | -60.64 | 60.7773 | 0.048597 | -0.0451 | 0.006315 | -0.057066 | 0.063733 | 0.035221 | -0.094765 | 60.745 | 60.7165 | 60.7267 | 60.6345 | 60.5946 | 60.7101 | 60.3142 | 60.4333 | 60.6886 | 60.5949 | 60.6463 | 60.5829 | 60.7037 | 60.6752 | 60.5452 | 60.7633 | 60.7348 | 60.745 | 60.6528 | 60.6129 | 60.7284 | 60.3326 | 60.4516 | 0.15044 | 0.43077 | 0.13209 | 0.41243
278.7656 | 121.5408 | -60.6766 | 60.7681 | 0.053175 | -0.049678 | -0.002842 | -0.061645 | 0.06831 | 0.035221 | -0.085608 | 60.7542 | 60.7257 | 60.7358 | 60.6437 | 60.59 | 60.7101 | 60.3142 | 60.4196 | 60.7298 | 60.6269 | 60.6737 | 60.6149 | 60.7449 | 60.7118 | 60.591 | 60.7725 | 60.744 | 60.7541 | 60.662 | 60.6083 | 60.7284 | 60.3326 | 60.4379 | 0.16418 | 0.43993 | 0.14583 | 0.42158
280.4844 | 121.5958 | -60.5896 | 60.791 | 0.048597 | -0.049678 | 0.001736 | -0.057066 | 0.059155 | 0.030642 | -0.090186 | 60.7633 | 60.7257 | 60.7358 | 60.6528 | 60.5763 | 60.6963 | 60.3005 | 60.4196 | 60.6382 | 60.5399 | 60.5913 | 60.5325 | 60.6488 | 60.6202 | 60.4994 | 60.7816 | 60.744 | 60.7541 | 60.6711 | 60.5946 | 60.7146 | 60.3188 | 60.4379 | 0.18707 | 0.46282 | 0.15957 | 0.43532
282.1562 | 121.6415 | -60.5804 | 60.7727 | 0.048597 | -0.054257 | -0.002842 | -0.057066 | 0.06831 | 0.035221 | -0.090186 | 60.7725 | 60.7348 | 60.7541 | 60.6482 | 60.5717 | 60.6872 | 60.2959 | 60.4012 | 60.629 | 60.5262 | 60.5776 | 60.5234 | 60.6488 | 60.6157 | 60.4903 | 60.7908 | 60.7531 | 60.7725 | 60.6665 | 60.59 | 60.7055 | 60.3142 | 60.4196 | 0.20081 | 0.47656 | 0.18246 | 0.45821
283.8594 | 121.5317 | -60.6033 | 60.8505 | 0.048597 | -0.049678 | 0.001736 | -0.061645 | 0.059155 | 0.030642 | -0.085608 | 60.7771 | 60.7531 | 60.7725 | 60.6711 | 60.5625 | 60.6734 | 60.2822 | 60.4012 | 60.6519 | 60.5537 | 60.6051 | 60.5417 | 60.6625 | 60.634 | 60.5177 | 60.7954 | 60.7714 | 60.7908 | 60.6894 | 60.5808 | 60.6917 | 60.3005 | 60.4196 | 0.21454 | 0.49487 | 0.20993 | 0.49026
285.5469 | 121.5088 | -60.5988 | 60.8688 | 0.048597 | -0.054257 | -0.012 | -0.061645 | 0.059155 | 0.035221 | -0.085608 | 60.7908 | 60.7669 | 60.777 | 60.6803 | 60.558 | 60.6597 | 60.2776 | 60.3829 | 60.6474 | 60.5445 | 60.5868 | 60.5371 | 60.6579 | 60.634 | 60.5131 | 60.8091 | 60.7852 | 60.7953 | 60.6986 | 60.5763 | 60.678 | 60.2959 | 60.4012 | 0.23285 | 0.51319 | 0.21908 | 0.49941
287.2188 | 121.6049 | -60.5576 | 60.8368 | 0.048597 | -0.058836 | -0.002842 | -0.066223 | 0.059155 | 0.026064 | -0.094765 | 60.8045 | 60.7669 | 60.7862 | 60.6803 | 60.5442 | 60.6505 | 60.2593 | 60.3738 | 60.6062 | 60.4987 | 60.5547 | 60.4913 | 60.6167 | 60.5836 | 60.4628 | 60.8229 | 60.7852 | 60.8045 | 60.6986 | 60.5625 | 60.6689 | 60.2776 | 60.3921 | 0.26032 | 0.54524 | 0.24197 | 0.52689
288.9062 | 121.6278 | -60.5667 | 60.8276 | 0.053175 | -0.058836 | -0.012 | -0.066223 | 0.063733 | 0.026064 | -0.099343 | 60.8183 | 60.7806 | 60.7999 | 60.7078 | 60.5259 | 60.6414 | 60.2501 | 60.36 | 60.6199 | 60.5079 | 60.5547 | 60.5005 | 60.6304 | 60.5928 | 60.4674 | 60.8366 | 60.7989 | 60.8182 | 60.7261 | 60.5442 | 60.6597 | 60.2685 | 60.3784 | 0.29237 | 0.56813 | 0.27402 | 0.54978
290.6094 | 121.5317 | -60.5484 | 60.878 | 0.03944 | -0.063415 | -0.012 | -0.061645 | 0.049999 | 0.030642 | -0.085608 | 60.8274 | 60.7943 | 60.8045 | 60.7169 | 60.5167 | 60.6368 | 60.2456 | 60.3555 | 60.5878 | 60.485 | 60.5364 | 60.4868 | 60.5984 | 60.579 | 60.4628 | 60.8457 | 60.8126 | 60.8228 | 60.7352 | 60.5351 | 60.6551 | 60.2639 | 60.3738 | 0.31068 | 0.58186 | 0.28775 | 0.55893
292.2812 | 121.6278 | -60.5072 | 60.8963 | 0.053175 | -0.058836 | -0.016578 | -0.070802 | 0.054577 | 0.026064 | -0.099343 | 60.8366 | 60.8126 | 60.8228 | 60.7261 | 60.4984 | 60.6185 | 60.2273 | 60.3326 | 60.5604 | 60.4484 | 60.4906 | 60.4364 | 60.5618 | 60.5333 | 60.4079 | 60.8549 | 60.831 | 60.8411 | 60.7444 | 60.5167 | 60.6368 | 60.2456 | 60.3509 | 0.33816 | 0.60933 | 0.32438 | 0.59556
293.9531 | 121.5042 | -60.5255 | 60.9375 | 0.057754 | -0.054257 | -0.007421 | -0.070802 | 0.059155 | 0.030642 | -0.090186 | 60.8549 | 60.8218 | 60.8457 | 60.7444 | 60.4893 | 60.6048 | 60.2181 | 60.3326 | 60.5833 | 60.4713 | 60.5181 | 60.4547 | 60.5847 | 60.5562 | 60.4353 | 60.8732 | 60.8401 | 60.864 | 60.7627 | 60.5076 | 60.6231 | 60.2364 | 60.3509 | 0.36562 | 0.6368 | 0.35643 | 0.62761
295.6406 | 121.5958 | -60.5072 | 60.9009 | 0.053175 | -0.054257 | -0.016578 | -0.070802 | 0.059155 | 0.026064 | -0.090186 | 60.8732 | 60.8447 | 60.8594 | 60.7627 | 60.4664 | 60.5819 | 60.1952 | 60.3051 | 60.5604 | 60.4529 | 60.4906 | 60.4364 | 60.5664 | 60.5333 | 60.417 | 60.8915 | 60.863 | 60.8778 | 60.781 | 60.4847 | 60.6002 | 60.2135 | 60.3234 | 0.40683 | 0.67801 | 0.39305 | 0.66423
297.3125 | 121.6415 | -60.4889 | 60.9009 | 0.048597 | -0.058836 | -0.007421 | -0.070802 | 0.045421 | 0.026064 | -0.099343 | 60.8961 | 60.8539 | 60.8732 | 60.7764 | 60.4389 | 60.5727 | 60.1677 | 60.2914 | 60.5375 | 60.4301 | 60.4815 | 60.4181 | 60.5343 | 60.515 | 60.3895 | 60.9144 | 60.8722 | 60.8915 | 60.7948 | 60.4572 | 60.591 | 60.186 | 60.3097 | 0.45719 | 0.72837 | 0.43426 | 0.70544
298.9844 | 121.6232 | -60.4706 | 60.91 | 0.053175 | -0.058836 | -0.007421 | -0.066223 | 0.059155 | 0.026064 | -0.099343 | 60.9098 | 60.8768 | 60.8915 | 60.7948 | 60.4298 | 60.5453 | 60.154 | 60.2639 | 60.5238 | 60.4117 | 60.4632 | 60.4044 | 60.5297 | 60.4966 | 60.3712 | 60.9282 | 60.8951 | 60.9098 | 60.8131 | 60.4481 | 60.5636 | 60.1723 | 60.2822 | 0.48008 | 0.75584 | 0.46173 | 0.73749
300.6562 | 121.5591 | -60.4843 | 60.9421 | 0.048597 | -0.054257 | -0.002842 | -0.066223 | 0.059155 | 0.026064 | -0.099343 | 60.9327 | 60.8951 | 60.9052 | 60.8085 | 60.4252 | 60.5407 | 60.1448 | 60.2593 | 60.5329 | 60.4301 | 60.4815 | 60.4181 | 60.5435 | 60.5104 | 60.385 | 60.951 | 60.9134 | 60.9235 | 60.8268 | 60.4435 | 60.559 | 60.1632 | 60.2776 | 0.50755 | 0.78789 | 0.48004 | 0.76038
302.3281 | 121.5546 | -60.4431 | 60.965 | 0.048597 | -0.063415 | -0.007421 | -0.066223 | 0.045421 | 0.026064 | -0.099343 | 60.9602 | 60.918 | 60.9327 | 60.836 | 60.4023 | 60.5086 | 60.122 | 60.2227 | 60.4917 | 60.3797 | 60.4357 | 60.3769 | 60.4885 | 60.4692 | 60.3438 | 60.9785 | 60.9363 | 60.951 | 60.8543 | 60.4206 | 60.5269 | 60.1403 | 60.241 | 0.55792 | 0.83825 | 0.5304 | 0.81074
304 | 121.5683 | -60.4019 | 61.0565 | 0.044018 | -0.058836 | -0.012 | -0.066223 | 0.054577 | 0.026064 | -0.099343 | 60.9694 | 60.9454 | 60.9556 | 60.8543 | 60.3702 | 60.4812 | 60.0991 | 60.2044 | 60.4459 | 60.3431 | 60.3899 | 60.3357 | 60.4565 | 60.428 | 60.3026 | 60.9877 | 60.9637 | 60.9739 | 60.8726 | 60.3886 | 60.4995 | 60.1174 | 60.2227 | 0.59912 | 0.8703 | 0.58534 | 0.85652
305.6719 | 121.637 | -60.3241 | 61.0519 | 0.048597 | -0.058836 | -0.021157 | -0.079959 | 0.049999 | 0.021485 | -0.1085 | 60.9968 | 60.9729 | 60.9785 | 60.8909 | 60.3336 | 60.4583 | 60.067 | 60.1769 | 60.3727 | 60.2653 | 60.3029 | 60.2441 | 60.3741 | 60.3456 | 60.2156 | 61.0151 | 60.9912 | 60.9968 | 60.9092 | 60.3519 | 60.4766 | 60.0853 | 60.1952 | 0.66322 | 0.92982 | 0.64486 | 0.91146
307.3438 | 121.5775 | -60.3424 | 61.0474 | 0.053175 | -0.058836 | -0.016578 | -0.079959 | 0.049999 | 0.021485 | -0.094765 | 61.0335 | 60.9912 | 61.0151 | 60.9184 | 60.3016 | 60.4308 | 60.035 | 60.1494 | 60.3956 | 60.2836 | 60.3258 | 60.2624 | 60.3924 | 60.3639 | 60.2476 | 61.0518 | 61.0095 | 61.0334 | 60.9367 | 60.3199 | 60.4491 | 60.0533 | 60.1678 | 0.73189 | 0.9985 | 0.71353 | 0.98014
309.0156 | 121.6141 | -60.3378 | 61.0565 | 0.03944 | -0.058836 | -0.007421 | -0.079959 | 0.045421 | 0.021485 | -0.099343 | 61.0518 | 61.0324 | 61.0517 | 60.9459 | 60.2833 | 60.4033 | 60.0075 | 60.1128 | 60.3773 | 60.279 | 60.3304 | 60.2579 | 60.3833 | 60.3593 | 60.2385 | 61.0701 | 61.0507 | 61.07 | 60.9642 | 60.3016 | 60.4216 | 60.0258 | 60.1311 | 0.76852 | 1.0443 | 0.76847 | 1.0442
310.6875 | 121.55 | -60.3149 | 61.116 | 0.053175 | -0.058836 | -0.007421 | -0.07538 | 0.054577 | 0.016907 | -0.10392 | 61.0976 | 61.0599 | 61.0792 | 60.9733 | 60.2466 | 60.3713 | 59.9663 | 60.0808 | 60.3681 | 60.2561 | 60.3075 | 60.2396 | 60.3695 | 60.3318 | 60.211 | 61.1159 | 61.0782 | 61.0975 | 60.9917 | 60.2649 | 60.3896 | 59.9846 | 60.0991 | 0.85093 | 1.1313 | 0.83257 | 1.1129
312.375 | 121.5088 | -60.2737 | 61.2167 | 0.048597 | -0.067994 | -0.016578 | -0.079959 | 0.054577 | 0.016907 | -0.10392 | 61.1296 | 61.0965 | 61.1158 | 61.0191 | 60.2146 | 60.3301 | 59.9434 | 60.0441 | 60.3223 | 60.2057 | 60.2572 | 60.1938 | 60.3283 | 60.2907 | 60.1698 | 61.1479 | 61.1148 | 61.1341 | 61.0374 | 60.2329 | 60.3484 | 59.9617 | 60.0625 | 0.91503 | 1.1862 | 0.90124 | 1.1724
314.0469 | 121.6507 | -60.1776 | 61.1984 | 0.057754 | -0.072572 | -0.025735 | -0.07538 | 0.045421 | 0.016907 | -0.10392 | 61.1662 | 61.1332 | 61.1479 | 61.0512 | 60.178 | 60.2935 | 59.8976 | 60.0167 | 60.2354 | 60.105 | 60.1519 | 60.1022 | 60.223 | 60.1945 | 60.0737 | 61.1846 | 61.1515 | 61.1662 | 61.0695 | 60.1963 | 60.3118 | 59.9159 | 60.035 | 0.98828 | 1.2686 | 0.96991 | 1.2503
315.75 | 121.5088 | -60.1685 | 61.2854 | 0.048597 | -0.067994 | -0.012 | -0.079959 | 0.045421 | 0.016907 | -0.1085 | 61.2166 | 61.179 | 61.1937 | 61.0924 | 60.1413 | 60.2477 | 59.8564 | 59.9709 | 60.2171 | 60.1005 | 60.1565 | 60.0885 | 60.2139 | 60.1854 | 60.06 | 61.2349 | 61.1973 | 61.212 | 61.1107 | 60.1596 | 60.266 | 59.8747 | 59.9892 | 1.0753 | 1.3602 | 1.0523 | 1.3373
317.4844 | 121.5271 | -60.1501 | 61.3083 | 0.053175 | -0.072572 | -0.021157 | -0.079959 | 0.045421 | 0.012329 | -0.1085 | 61.2578 | 61.2293 | 61.2394 | 61.1473 | 60.0864 | 60.2019 | 59.8152 | 59.9251 | 60.2033 | 60.0776 | 60.129 | 60.0702 | 60.1956 | 60.1625 | 60.0416 | 61.2761 | 61.2476 | 61.2577 | 61.1657 | 60.1047 | 60.2202 | 59.8335 | 59.9434 | 1.1714 | 1.4426 | 1.153 | 1.4242
319.1562 | 121.5363 | -60.0998 | 61.3541 | 0.048597 | -0.072572 | -0.016578 | -0.079959 | 0.045421 | 0.012329 | -0.099343 | 61.299 | 61.2751 | 61.2898 | 61.184 | 60.0452 | 60.1561 | 59.7694 | 59.8793 | 60.1484 | 60.0272 | 60.0832 | 60.0198 | 60.1452 | 60.1121 | 60.0004 | 61.3173 | 61.2934 | 61.3081 | 61.2023 | 60.0635 | 60.1744 | 59.7877 | 59.8976 | 1.2538 | 1.5296 | 1.2446 | 1.5204
320.8281 | 121.5683 | -60.0311 | 61.3907 | 0.03944 | -0.077151 | -0.025735 | -0.084537 | 0.040843 | -0.001406 | -0.1085 | 61.354 | 61.3117 | 61.3356 | 61.2298 | 59.9903 | 60.1058 | 59.7145 | 59.8336 | 60.0706 | 59.954 | 60.0054 | 59.9466 | 60.072 | 60.0297 | 59.9226 | 61.3723 | 61.3301 | 61.3539 | 61.2481 | 60.0086 | 60.1241 | 59.7328 | 59.8519 | 1.3637 | 1.6395 | 1.3453 | 1.6211
322.5469 | 121.6324 | -59.9121 | 61.4731 | 0.044018 | -0.077151 | -0.025735 | -0.084537 | 0.036265 | 0.00775 | -0.11308 | 61.4135 | 61.3758 | 61.3951 | 61.2939 | 59.9399 | 60.0462 | 59.655 | 59.7649 | 59.9561 | 59.835 | 59.8864 | 59.8276 | 59.9484 | 59.9199 | 59.799 | 61.4318 | 61.3942 | 61.4134 | 61.3122 | 59.9582 | 60.0646 | 59.6733 | 59.7832 | 1.4736 | 1.7585 | 1.4552 | 1.7401
324.2188 | 121.6415 | -59.8938 | 61.5097 | 0.048597 | -0.077151 | -0.025735 | -0.084537 | 0.040843 | 0.012329 | -0.1085 | 61.4684 | 61.4308 | 61.4455 | 61.3488 | 59.8758 | 59.9959 | 59.6046 | 59.7191 | 59.9424 | 59.8166 | 59.8681 | 59.8093 | 59.9346 | 59.9061 | 59.7853 | 61.4867 | 61.4491 | 61.4638 | 61.3671 | 59.8941 | 60.0142 | 59.6229 | 59.7374 | 1.5926 | 1.8638 | 1.5697 | 1.8409
325.8906 | 121.5637 | -59.8251 | 61.5601 | 0.053175 | -0.077151 | -0.030314 | -0.089116 | 0.045421 | 0.012329 | -0.11765 | 61.5279 | 61.4857 | 61.5096 | 61.4038 | 59.8163 | 59.9409 | 59.5405 | 59.6596 | 59.8783 | 59.748 | 59.7948 | 59.736 | 59.8706 | 59.8375 | 59.7075 | 61.5463 | 61.504 | 61.5279 | 61.4221 | 59.8346 | 59.9593 | 59.5588 | 59.6779 | 1.7117 | 1.9874 | 1.6933 | 1.9691
327.5625 | 121.5134 | -59.8343 | 61.615 | 0.048597 | -0.072572 | -0.034893 | -0.089116 | 0.036265 | 0.012329 | -0.1085 | 61.5737 | 61.5453 | 61.5645 | 61.4587 | 59.7613 | 59.8814 | 59.4901 | 59.6001 | 59.8829 | 59.7617 | 59.7994 | 59.7452 | 59.8706 | 59.8466 | 59.7258 | 61.592 | 61.5636 | 61.5828 | 61.477 | 59.7797 | 59.8997 | 59.5084 | 59.6184 | 1.8124 | 2.0836 | 1.8031 | 2.0744
329.2344 | 121.5683 | -59.7519 | 61.6379 | 0.048597 | -0.086309 | -0.025735 | -0.089116 | 0.036265 | 0.012329 | -0.11308 | 61.6332 | 61.6048 | 61.6149 | 61.5182 | 59.6973 | 59.8219 | 59.426 | 59.5497 | 59.8005 | 59.6656 | 59.7262 | 59.6628 | 59.7882 | 59.7642 | 59.6388 | 61.6516 | 61.6231 | 61.6332 | 61.5366 | 59.7156 | 59.8402 | 59.4444 | 59.568 | 1.936 | 2.2072 | 1.9176 | 2.1888
330.9219 | 121.55 | -59.6878 | 61.7615 | 0.048597 | -0.08173 | -0.030314 | -0.084537 | 0.036265 | 0.00775 | -0.1085 | 61.7019 | 61.6689 | 61.6881 | 61.5824 | 59.6469 | 59.7578 | 59.3711 | 59.481 | 59.7364 | 59.6061 | 59.6575 | 59.6033 | 59.7241 | 59.6956 | 59.5793 | 61.7202 | 61.6872 | 61.7064 | 61.6007 | 59.6652 | 59.7761 | 59.3894 | 59.4993 | 2.055 | 2.3308 | 2.0412 | 2.317
332.5938 | 121.5134 | -59.61 | 61.8942 | 0.053175 | -0.08173 | -0.030314 | -0.084537 | 0.031687 | 0.016907 | -0.11765 | 61.7935 | 61.7559 | 61.7659 | 61.6694 | 59.5599 | 59.6754 | 59.2887 | 59.3986 | 59.6632 | 59.5283 | 59.5797 | 59.5254 | 59.6417 | 59.6269 | 59.4923 | 61.8118 | 61.7742 | 61.7843 | 61.6877 | 59.5782 | 59.6937 | 59.307 | 59.4169 | 2.2336 | 2.5048 | 2.206 | 2.4773
334.3125 | 121.5408 | -59.5413 | 61.8759 | 0.044018 | -0.077151 | -0.030314 | -0.079959 | 0.036265 | 0.00775 | -0.11308 | 61.8576 | 61.8291 | 61.8484 | 61.7472 | 59.4821 | 59.6022 | 59.2063 | 59.3208 | 59.5853 | 59.4642 | 59.511 | 59.4614 | 59.5776 | 59.5491 | 59.4282 | 61.8759 | 61.8475 | 61.8667 | 61.7655 | 59.5004 | 59.6205 | 59.2246 | 59.3391 | 2.3755 | 2.6513 | 2.3663 | 2.6421
336.0156 | 121.5042 | -59.5001 | 62.0087 | 0.053175 | -0.072572 | -0.034893 | -0.089116 | 0.031687 | 0.012329 | -0.10392 | 61.9171 | 61.8841 | 61.9033 | 61.8021 | 59.4363 | 59.5427 | 59.1513 | 59.2613 | 59.5533 | 59.4275 | 59.4652 | 59.411 | 59.5318 | 59.5125 | 59.3962 | 61.9354 | 61.9024 | 61.9216 | 61.8205 | 59.4546 | 59.561 | 59.1696 | 59.2796 | 2.4808 | 2.7658 | 2.467 | 2.752
337.6875 | 121.5408 | -59.4269 | 62.0682 | 0.053175 | -0.077151 | -0.030314 | -0.089116 | 0.031687 | 0.00775 | -0.10392 | 61.9995 | 61.9665 | 61.9765 | 61.88 | 59.3493 | 59.4694 | 59.0735 | 59.1835 | 59.4801 | 59.3497 | 59.3966 | 59.3378 | 59.4586 | 59.4346 | 59.323 | 62.0178 | 61.9848 | 61.9949 | 61.8983 | 59.3676 | 59.4877 | 59.0918 | 59.2018 | 2.6502 | 2.926 | 2.6272 | 2.903
339.375 | 121.5363 | -59.3216 | 62.1185 | 0.044018 | -0.072572 | -0.030314 | -0.089116 | 0.031687 | 0.00775 | -0.11308 | 62.0728 | 62.0398 | 62.0635 | 61.967 | 59.2715 | 59.3962 | 58.9911 | 59.1102 | 59.3656 | 59.249 | 59.2913 | 59.2325 | 59.3533 | 59.3293 | 59.2085 | 62.0911 | 62.0581 | 62.0818 | 61.9853 | 59.2898 | 59.4145 | 59.0094 | 59.1285 | 2.8013 | 3.0817 | 2.792 | 3.0724
341.0469 | 121.6003 | -59.1797 | 62.1826 | 0.044018 | -0.077151 | -0.030314 | -0.093694 | 0.031687 | 0.003172 | -0.11765 | 62.1552 | 62.1176 | 62.1322 | 62.0403 | 59.1891 | 59.3046 | 58.9178 | 59.0278 | 59.2237 | 59.1025 | 59.1494 | 59.086 | 59.2114 | 59.1829 | 59.062 | 62.1735 | 62.1359 | 62.1505 | 62.0586 | 59.2074 | 59.3229 | 58.9361 | 59.0461 | 2.9661 | 3.2374 | 2.9431 | 3.2144
342.7188 | 121.5729 | -59.1476 | 62.265 | 0.048597 | -0.072572 | -0.030314 | -0.084537 | 0.031687 | 0.00775 | -0.11308 | 62.233 | 62.2046 | 62.2283 | 62.1273 | 59.1067 | 59.2268 | 58.8263 | 58.9362 | 59.1962 | 59.0751 | 59.1173 | 59.0631 | 59.1793 | 59.1554 | 59.0346 | 62.2513 | 62.2229 | 62.2467 | 62.1456 | 59.125 | 59.2451 | 58.8446 | 58.9545 | 3.1264 | 3.4068 | 3.1217 | 3.4021
344.4531 | 121.5134 | -59.0469 | 62.4161 | 0.048597 | -0.072572 | -0.034893 | -0.084537 | 0.040843 | 0.003172 | -0.11765 | 62.3429 | 62.3053 | 62.3199 | 62.2372 | 59.0105 | 59.1123 | 58.7255 | 58.8447 | 59.0955 | 58.9744 | 59.012 | 58.9624 | 59.0878 | 59.0501 | 58.9293 | 62.3612 | 62.3237 | 62.3382 | 62.2555 | 59.0288 | 59.1306 | 58.7439 | 58.863 | 3.3324 | 3.6174 | 3.3094 | 3.5944
346.125 | 121.5363 | -58.9828 | 62.4619 | 0.048597 | -0.072572 | -0.025735 | -0.084537 | 0.031687 | 0.00775 | -0.11765 | 62.4391 | 62.4015 | 62.4252 | 62.3196 | 58.9144 | 59.0299 | 58.6386 | 58.7394 | 59.0314 | 58.9103 | 58.9571 | 58.8983 | 59.0145 | 58.9906 | 58.8652 | 62.4574 | 62.4198 | 62.4435 | 62.3379 | 58.9327 | 59.0482 | 58.6569 | 58.7577 | 3.5247 | 3.8005 | 3.5108 | 3.7867
347.7969 | 121.5088 | -58.8593 | 62.6083 | 0.044018 | -0.077151 | -0.034893 | -0.093694 | 0.027109 | 0.00775 | -0.11765 | 62.5306 | 62.5022 | 62.5168 | 62.4066 | 58.8137 | 58.9246 | 58.5378 | 58.6524 | 58.9033 | 58.7821 | 58.8244 | 58.7656 | 58.8864 | 58.867 | 58.7416 | 62.5489 | 62.5205 | 62.5351 | 62.4249 | 58.832 | 58.9429 | 58.5561 | 58.6707 | 3.717 | 3.9928 | 3.7031 | 3.9789
349.5312 | 121.5408 | -58.7769 | 62.6862 | 0.053175 | -0.086309 | -0.048628 | -0.093694 | 0.027109 | -0.005985 | -0.12223 | 62.6314 | 62.603 | 62.6129 | 62.5211 | 58.7175 | 58.8285 | 58.4371 | 58.5425 | 58.83 | 58.6905 | 58.7282 | 58.6832 | 58.804 | 58.7709 | 58.6546 | 62.6497 | 62.6213 | 62.6312 | 62.5394 | 58.7358 | 58.8468 | 58.4554 | 58.5608 | 3.9138 | 4.1943 | 3.8954 | 4.1758
351.2031 | 121.5088 | -58.6716 | 62.7823 | 0.053175 | -0.086309 | -0.048628 | -0.089116 | 0.022531 | 0.003172 | -0.12223 | 62.7321 | 62.6991 | 62.7136 | 62.6172 | 58.6214 | 58.7278 | 58.341 | 58.4555 | 58.7247 | 58.5853 | 58.6229 | 58.5825 | 58.6941 | 58.6747 | 58.5493 | 62.7504 | 62.7174 | 62.732 | 62.6355 | 58.6397 | 58.7461 | 58.3593 | 58.4738 | 4.1107 | 4.3911 | 4.0923 | 4.3727
352.8906 | 121.5042 | -58.5938 | 62.8693 | 0.048597 | -0.08173 | -0.039471 | -0.089116 | 0.031687 | 0.00775 | -0.11765 | 62.842 | 62.7953 | 62.8189 | 62.7225 | 58.5069 | 58.6179 | 58.2311 | 58.3411 | 58.6423 | 58.512 | 58.5543 | 58.5046 | 58.6254 | 58.6015 | 58.4761 | 62.8603 | 62.8136 | 62.8373 | 62.7408 | 58.5252 | 58.6362 | 58.2494 | 58.3594 | 4.335 | 4.6109 | 4.312 | 4.5879
354.5938 | 121.4951 | -58.4473 | 63.0066 | 0.044018 | -0.086309 | -0.030314 | -0.089116 | 0.031687 | 0.003172 | -0.12223 | 62.9564 | 62.9189 | 62.938 | 62.837 | 58.3879 | 58.508 | 58.1166 | 58.222 | 58.4913 | 58.361 | 58.417 | 58.3582 | 58.479 | 58.4504 | 58.325 | 62.9747 | 62.9372 | 62.9563 | 62.8553 | 58.4062 | 58.5263 | 58.1349 | 58.2403 | 4.5685 | 4.8398 | 4.5501 | 4.8214
356.2812 | 121.5225 | -58.3191 | 63.1348 | 0.03944 | -0.086309 | -0.034893 | -0.093694 | 0.027109 | -0.005985 | -0.12223 | 63.0617 | 63.0196 | 63.0433 | 62.9423 | 58.2872 | 58.4027 | 58.0113 | 58.1305 | 58.3585 | 58.2328 | 58.2842 | 58.2254 | 58.3462 | 58.3131 | 58.1969 | 63.08 | 63.0379 | 63.0616 | 62.9606 | 58.3055 | 58.421 | 58.0296 | 58.1488 | 4.7746 | 5.0504 | 4.7561 | 5.032
357.9844 | 121.6278 | -58.1909 | 63.1714 | 0.044018 | -0.077151 | -0.034893 | -0.089116 | 0.036265 | 0.003172 | -0.11765 | 63.1762 | 63.1341 | 63.1532 | 63.0614 | 58.1636 | 58.2791 | 57.8785 | 58.0069 | 58.2349 | 58.1138 | 58.156 | 58.1018 | 58.2272 | 58.1941 | 58.0733 | 63.1945 | 63.1524 | 63.1715 | 63.0797 | 58.1819 | 58.2974 | 57.8969 | 58.0252 | 5.0126 | 5.2977 | 4.9896 | 5.2746
359.6875 | 121.669 | -58.0399 | 63.3408 | 0.048597 | -0.086309 | -0.04405 | -0.093694 | 0.027109 | 0.003172 | -0.11765 | 63.2907 | 63.2532 | 63.2859 | 63.1804 | 58.0583 | 58.1647 | 57.7732 | 57.8832 | 58.0885 | 57.9535 | 57.9958 | 57.9462 | 58.067 | 58.043 | 57.9222 | 63.309 | 63.2715 | 63.3042 | 63.1987 | 58.0766 | 58.183 | 57.7916 | 57.9016 | 5.2324 | 5.5174 | 5.2277 | 5.5127
361.3906 | 121.5546 | -57.9529 | 63.4827 | 0.048597 | -0.077151 | -0.030314 | -0.089116 | 0.036265 | 0.00775 | -0.11308 | 63.4418 | 63.4134 | 63.4233 | 63.3315 | 57.898 | 58.0136 | 57.6222 | 57.7322 | 58.0015 | 57.8757 | 57.9226 | 57.8638 | 57.9891 | 57.9606 | 57.8398 | 63.4601 | 63.4317 | 63.4416 | 63.3499 | 57.9163 | 58.0319 | 57.6405 | 57.7505 | 5.5437 | 5.8196 | 5.5252 | 5.8011
363.0625 | 121.5363 | -57.811 | 63.6383 | 0.044018 | -0.072572 | -0.025735 | -0.07538 | 0.036265 | 0.016907 | -0.099343 | 63.57 | 63.5416 | 63.556 | 63.4598 | 57.7698 | 57.8854 | 57.4985 | 57.6131 | 57.855 | 57.7384 | 57.7852 | 57.7356 | 57.8472 | 57.8279 | 57.7116 | 63.5883 | 63.5599 | 63.5744 | 63.4781 | 57.7882 | 57.9037 | 57.5168 | 57.6314 | 5.8001 | 6.0714 | 5.7862 | 6.0575
364.7344 | 121.5088 | -57.6736 | 63.7894 | 0.044018 | -0.058836 | -0.012 | -0.070802 | 0.049999 | 0.026064 | -0.094765 | 63.7165 | 63.679 | 63.698 | 63.5971 | 57.6325 | 57.7435 | 57.3658 | 57.4758 | 57.7177 | 57.6148 | 57.6616 | 57.6028 | 57.7236 | 57.6997 | 57.5789 | 63.7348 | 63.6973 | 63.7163 | 63.6154 | 57.6508 | 57.7618 | 57.3841 | 57.4941 | 6.084 | 6.3507 | 6.0655 | 6.3322
366.4531 | 121.5134 | -57.5455 | 63.913 | 0.048597 | -0.063415 | -0.025735 | -0.079959 | 0.045421 | 0.012329 | -0.10392 | 63.8859 | 63.8484 | 63.8674 | 63.7666 | 57.4677 | 57.5787 | 57.1872 | 57.2972 | 57.5941 | 57.4821 | 57.5197 | 57.4655 | 57.5909 | 57.5578 | 57.4415 | 63.9042 | 63.8667 | 63.8857 | 63.7849 | 57.486 | 57.597 | 57.2055 | 57.3156 | 6.4182 | 6.6987 | 6.3997 | 6.6802
368.125 | 121.5042 | -57.4081 | 64.0411 | 0.053175 | -0.063415 | -0.025735 | -0.070802 | 0.049999 | 0.016907 | -0.099343 | 64.037 | 63.9903 | 64.0185 | 63.9131 | 57.312 | 57.4276 | 57.0361 | 57.1599 | 57.4613 | 57.3447 | 57.3824 | 57.3373 | 57.4581 | 57.425 | 57.3088 | 64.0553 | 64.0087 | 64.0368 | 63.9314 | 57.3303 | 57.4459 | 57.0544 | 57.1782 | 6.7249 | 7.0008 | 6.7064 | 6.9823
369.7969 | 121.5408 | -57.2342 | 64.2334 | 0.048597 | -0.072572 | -0.012 | -0.070802 | 0.054577 | 0.016907 | -0.099343 | 64.1743 | 64.146 | 64.165 | 64.0596 | 57.1747 | 57.2857 | 56.8988 | 57.0134 | 57.2828 | 57.1616 | 57.2222 | 57.1634 | 57.2888 | 57.2511 | 57.1348 | 64.1926 | 64.1643 | 64.1833 | 64.0779 | 57.193 | 57.304 | 56.9171 | 57.0317 | 6.9996 | 7.2755 | 6.9903 | 7.2662
371.5469 | 121.5912 | -56.955 | 64.4714 | 0.044018 | -0.049678 | 0.006315 | -0.047909 | 0.06831 | 0.030642 | -0.08103 | 64.3987 | 64.3567 | 64.3801 | 64.2702 | 56.9641 | 57.0705 | 56.6882 | 56.7936 | 56.999 | 56.9053 | 56.9613 | 56.907 | 57.0233 | 56.9856 | 56.8739 | 64.417 | 64.375 | 64.3985 | 64.2886 | 56.9824 | 57.0888 | 56.7065 | 56.812 | 7.4346 | 7.7105 | 7.4161 | 7.692
373.2188 | 121.6187 | -56.8039 | 64.6179 | 0.048597 | -0.054257 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 64.5498 | 64.5169 | 64.5266 | 64.4305 | 56.7947 | 56.9148 | 56.5279 | 56.6334 | 56.8525 | 56.7496 | 56.8102 | 56.7514 | 56.8768 | 56.8437 | 56.7274 | 64.5681 | 64.5352 | 64.545 | 64.4488 | 56.813 | 56.9332 | 56.5462 | 56.6517 | 7.7551 | 8.0218 | 7.732 | 7.9987
374.9062 | 121.6232 | -56.6254 | 64.7415 | 0.044018 | -0.026784 | 0.029208 | -0.034174 | 0.10036 | 0.058113 | -0.053561 | 64.7192 | 64.6817 | 64.7052 | 64.6045 | 56.6207 | 56.7409 | 56.3402 | 56.4549 | 56.6694 | 56.5986 | 56.6546 | 56.5912 | 56.7257 | 56.6835 | 56.5718 | 64.7375 | 64.7001 | 64.7235 | 64.6228 | 56.639 | 56.7592 | 56.3585 | 56.4732 | 8.0984 | 8.3789 | 8.0845 | 8.365
376.6094 | 121.5088 | -56.4835 | 65.0024 | 0.034862 | -0.040521 | 0.010893 | -0.043331 | 0.082044 | 0.062691 | -0.067295 | 64.9206 | 64.8924 | 64.9066 | 64.8106 | 56.4239 | 56.5349 | 56.1479 | 56.258 | 56.5183 | 56.4429 | 56.4944 | 56.4401 | 56.5655 | 56.5462 | 56.4162 | 64.9389 | 64.9107 | 64.925 | 64.8289 | 56.4422 | 56.5532 | 56.1662 | 56.2763 | 8.4967 | 8.7727 | 8.4828 | 8.7587
378.2812 | 121.4951 | -56.2683 | 65.1947 | 0.048597 | -0.026784 | 0.020051 | -0.034174 | 0.095778 | 0.076426 | -0.053561 | 65.1358 | 65.0938 | 65.1172 | 65.0166 | 56.2133 | 56.3243 | 55.9419 | 56.052 | 56.3169 | 56.2415 | 56.2884 | 56.2341 | 56.3641 | 56.3447 | 56.2147 | 65.1541 | 65.1122 | 65.1356 | 65.0349 | 56.2316 | 56.3426 | 55.9602 | 56.0703 | 8.9225 | 9.1939 | 8.904 | 9.1754
379.9688 | 121.55 | -56.0577 | 65.3641 | 0.044018 | -0.017627 | 0.024629 | -0.025017 | 0.10493 | 0.076426 | -0.044405 | 65.3235 | 65.2953 | 65.3141 | 65.2044 | 56.021 | 56.1274 | 55.745 | 55.8643 | 56.1018 | 56.0401 | 56.0824 | 56.0327 | 56.1627 | 56.1342 | 56.0133 | 65.3418 | 65.3136 | 65.3324 | 65.2227 | 56.0393 | 56.1457 | 55.7633 | 55.8826 | 9.3025 | 9.5785 | 9.2931 | 9.5691
381.6562 | 121.5958 | -55.8014 | 65.6021 | 0.048597 | -0.013048 | 0.029208 | -0.025017 | 0.10036 | 0.076426 | -0.058139 | 65.525 | 65.483 | 65.5064 | 65.3967 | 55.8241 | 55.9351 | 55.5527 | 55.6583 | 55.85 | 55.7883 | 55.8306 | 55.7764 | 55.9017 | 55.8778 | 55.7433 | 65.5433 | 65.5014 | 65.5247 | 65.415 | 55.8424 | 55.9534 | 55.571 | 55.6766 | 9.7008 | 9.9722 | 9.6823 | 9.9537
383.3281 | 121.5912 | -55.5542 | 65.831 | 0.044018 | -0.013048 | 0.047522 | -0.011281 | 0.11409 | 0.076426 | -0.035248 | 65.7722 | 65.7349 | 65.7536 | 65.6623 | 55.5769 | 55.6925 | 55.3009 | 55.411 | 55.5982 | 55.5412 | 55.6017 | 55.5429 | 55.6683 | 55.6306 | 55.519 | 65.7905 | 65.7532 | 65.7719 | 65.6806 | 55.5952 | 55.7108 | 55.3192 | 55.4293 | 10.1953 | 10.4713 | 10.1767 | 10.4527
385.0625 | 121.4996 | -55.4169 | 66.0461 | 0.044018 | 0.023583 | 0.079572 | 0.029925 | 0.14156 | 0.10848 | -0.007779 | 65.9645 | 65.9318 | 65.9413 | 65.8409 | 55.3984 | 55.5002 | 55.1086 | 55.2325 | 55.4609 | 55.4405 | 55.4964 | 55.4468 | 55.5584 | 55.5253 | 55.4091 | 65.9828 | 65.9501 | 65.9596 | 65.8592 | 55.4167 | 55.5185 | 55.1269 | 55.2508 | 10.5662 | 10.8559 | 10.543 | 10.8327
386.7344 | 121.4996 | -55.22 | 66.2613 | 0.048597 | 0.000689 | 0.047522 | -0.006703 | 0.11867 | 0.090161 | -0.035248 | 66.1751 | 66.1424 | 66.1565 | 66.0606 | 55.1786 | 55.2896 | 54.9117 | 55.0219 | 55.2686 | 55.2207 | 55.2676 | 55.2133 | 55.3387 | 55.3102 | 55.1848 | 66.1934 | 66.1607 | 66.1748 | 66.079 | 55.1969 | 55.3079 | 54.9301 | 55.0402 | 10.9965 | 11.2634 | 10.9779 | 11.2448
388.4062 | 121.55 | -54.95 | 66.4764 | 0.053175 | 0.037319 | 0.070415 | 0.025347 | 0.14156 | 0.12221 | -0.003201 | 66.4407 | 66.4034 | 66.4221 | 66.3262 | 54.9085 | 55.0241 | 54.637 | 54.7426 | 55.0031 | 54.9873 | 55.0204 | 54.9753 | 55.0915 | 55.0722 | 54.9468 | 66.459 | 66.4217 | 66.4404 | 66.3445 | 54.9268 | 55.0424 | 54.6554 | 54.7609 | 11.5322 | 11.8036 | 11.5136 | 11.785
390.1094 | 121.6187 | -54.5975 | 66.8152 | 0.03944 | 0.000689 | 0.052101 | 0.002454 | 0.12325 | 0.090161 | -0.035248 | 66.7612 | 66.7239 | 66.7425 | 66.6376 | 54.5834 | 54.7128 | 54.3166 | 54.4267 | 54.6369 | 54.5982 | 54.6496 | 54.5999 | 54.7207 | 54.6876 | 54.5622 | 66.7795 | 66.7422 | 66.7608 | 66.6559 | 54.6017 | 54.7311 | 54.3349 | 54.445 | 12.1777 | 12.4446 | 12.1591 | 12.426
391.7812 | 121.5546 | -54.3549 | 67.1036 | 0.048597 | 0.019004 | 0.070415 | 0.01619 | 0.14156 | 0.11305 | -0.007779 | 67.0359 | 67.0032 | 67.0172 | 66.9169 | 54.3042 | 54.429 | 54.0327 | 54.1475 | 54.4035 | 54.3739 | 54.4253 | 54.371 | 54.4964 | 54.4679 | 54.3471 | 67.0542 | 67.0215 | 67.0355 | 66.9352 | 54.3225 | 54.4473 | 54.051 | 54.1658 | 12.7317 | 13.0032 | 12.7131 | 12.9845
393.5 | 121.6232 | -53.9749 | 67.4286 | 0.048597 | 0.03274 | 0.10247 | 0.034504 | 0.16445 | 0.13595 | 0.005955 | 67.3976 | 67.342 | 67.3652 | 67.2695 | 53.97 | 54.0764 | 53.6893 | 53.8133 | 54.0235 | 54.0077 | 54.0774 | 54.0094 | 54.1394 | 54.1109 | 53.9809 | 67.4159 | 67.3604 | 67.3835 | 67.2878 | 53.9883 | 54.0948 | 53.7076 | 53.8316 | 13.4276 | 13.7083 | 13.3952 | 13.6759
395.1719 | 121.5958 | -53.6728 | 67.749 | 0.053175 | 0.041898 | 0.093308 | 0.039082 | 0.16903 | 0.1451 | 0.010533 | 67.6998 | 67.658 | 67.6948 | 67.5809 | 53.6449 | 53.756 | 53.3688 | 53.479 | 53.726 | 53.7147 | 53.7661 | 53.7119 | 53.8418 | 53.8179 | 53.6833 | 67.7181 | 67.6763 | 67.7131 | 67.5992 | 53.6632 | 53.7743 | 53.3871 | 53.4974 | 14.0548 | 14.3309 | 14.0499 | 14.326
396.8594 | 121.5775 | -53.3615 | 68.0374 | 0.044018 | 0.078529 | 0.12994 | 0.080288 | 0.2148 | 0.17715 | 0.047159 | 67.9836 | 67.9602 | 67.9741 | 67.8694 | 53.3565 | 53.4721 | 53.0896 | 53.2044 | 53.4055 | 53.44 | 53.4914 | 53.4418 | 53.5763 | 53.5387 | 53.4087 | 68.0019 | 67.9785 | 67.9924 | 67.8877 | 53.3748 | 53.4904 | 53.1079 | 53.2227 | 14.6271 | 14.8941 | 14.6176 | 14.8845
398.5625 | 121.55 | -52.9495 | 68.5043 | 0.048597 | 0.083107 | 0.12078 | 0.07571 | 0.20107 | 0.16799 | 0.047159 | 68.4644 | 68.4272 | 68.4457 | 68.3456 | 52.8849 | 52.996 | 52.618 | 52.7282 | 52.9981 | 53.0326 | 53.0703 | 53.0252 | 53.1506 | 53.1175 | 52.9967 | 68.4827 | 68.4455 | 68.464 | 68.3639 | 52.9032 | 53.0143 | 52.6363 | 52.7465 | 15.5794 | 15.8464 | 15.5607 | 15.8277
400.2344 | 121.5088 | -52.6108 | 68.8751 | 0.044018 | 0.087686 | 0.13452 | 0.084867 | 0.21023 | 0.17257 | 0.051737 | 68.7757 | 68.7386 | 68.757 | 68.657 | 52.5782 | 52.6984 | 52.3021 | 52.4261 | 52.6548 | 52.6985 | 52.7453 | 52.6956 | 52.821 | 52.7834 | 52.6625 | 68.794 | 68.7569 | 68.7753 | 68.6753 | 52.5965 | 52.7168 | 52.3204 | 52.4444 | 16.1975 | 16.4736 | 16.1788 | 16.4549
401.9219 | 121.6278 | -52.1347 | 69.2459 | 0.048597 | 0.11516 | 0.15741 | 0.10776 | 0.22854 | 0.20004 | 0.079206 | 69.2244 | 69.1827 | 69.2056 | 69.1011 | 52.1295 | 52.2452 | 51.8534 | 51.9683 | 52.1833 | 52.2499 | 52.2921 | 52.2425 | 52.3632 | 52.3347 | 52.2139 | 69.2427 | 69.201 | 69.224 | 69.1194 | 52.1478 | 52.2635 | 51.8717 | 51.9866 | 17.0949 | 17.371 | 17.0761 | 17.3523
403.5938 | 121.5866 | -51.5945 | 69.8364 | 0.044018 | 0.18842 | 0.23982 | 0.19017 | 0.31094 | 0.28703 | 0.15704 | 69.7509 | 69.7001 | 69.723 | 69.6277 | 51.603 | 51.7187 | 51.3314 | 51.4509 | 51.6386 | 51.783 | 51.8344 | 51.7847 | 51.9055 | 51.8816 | 51.7516 | 69.7692 | 69.7184 | 69.7413 | 69.646 | 51.6214 | 51.7371 | 51.3498 | 51.4692 | 18.1479 | 18.4195 | 18.1199 | 18.3915
405.2656 | 121.4767 | -51.1459 | 70.34 | 0.048597 | 0.15637 | 0.20319 | 0.15812 | 0.27432 | 0.25498 | 0.12041 | 70.2866 | 70.2404 | 70.2678 | 70.1589 | 51.0674 | 51.1785 | 50.8049 | 50.9061 | 51.1945 | 51.3023 | 51.3491 | 51.3041 | 51.4203 | 51.4009 | 51.2663 | 70.3049 | 70.2587 | 70.2861 | 70.1772 | 51.0857 | 51.1968 | 50.8232 | 50.9244 | 19.2192 | 19.4817 | 19.2004 | 19.4629
406.9375 | 121.4951 | -50.7614 | 70.7245 | 0.044018 | 0.17468 | 0.23067 | 0.17644 | 0.30636 | 0.27787 | 0.15246 | 70.717 | 70.6754 | 70.7027 | 70.5985 | 50.6416 | 50.7528 | 50.3654 | 50.4803 | 50.8054 | 50.9361 | 50.9921 | 50.9379 | 51.0678 | 51.0393 | 50.9139 | 70.7353 | 70.6937 | 70.7211 | 70.6168 | 50.6599 | 50.7711 | 50.3837 | 50.4987 | 20.0754 | 20.3516 | 20.0611 | 20.3373
408.6094 | 121.5408 | -50.1251 | 71.315 | 0.048597 | 0.23421 | 0.27187 | 0.2268 | 0.34757 | 0.31908 | 0.19366 | 71.2847 | 71.2386 | 71.2659 | 71.1617 | 50.0602 | 50.1851 | 49.8023 | 49.9127 | 50.1737 | 50.3593 | 50.397 | 50.3519 | 50.4727 | 50.4442 | 50.3188 | 71.303 | 71.2569 | 71.2842 | 71.18 | 50.0785 | 50.2034 | 49.8206 | 49.931 | 21.2245 | 21.4824 | 21.2057 | 21.4636
410.2812 | 121.6278 | -49.5392 | 71.8323 | 0.034862 | 0.20216 | 0.2444 | 0.19933 | 0.32468 | 0.29161 | 0.16619 | 71.8067 | 71.7606 | 71.7741 | 71.6745 | 49.5429 | 49.654 | 49.2803 | 49.3816 | 49.574 | 49.7413 | 49.7836 | 49.7385 | 49.8639 | 49.8308 | 49.7054 | 71.825 | 71.7789 | 71.7924 | 71.6928 | 49.5612 | 49.6723 | 49.2986 | 49.3999 | 22.2638 | 22.5263 | 22.2312 | 22.4937
411.9531 | 121.5271 | -48.9899 | 72.4319 | 0.048597 | 0.21589 | 0.26272 | 0.21307 | 0.33841 | 0.30992 | 0.18908 | 72.4019 | 72.3604 | 72.3784 | 72.279 | 48.9569 | 49.0635 | 48.6851 | 48.8002 | 49.0385 | 49.2058 | 49.2526 | 49.2029 | 49.3283 | 49.2998 | 49.179 | 72.4202 | 72.3787 | 72.3967 | 72.2973 | 48.9752 | 49.0818 | 48.7035 | 48.8185 | 23.445 | 23.7167 | 23.4215 | 23.6933
413.6406 | 121.5088 | -48.175 | 73.2925 | 0.044018 | 0.22963 | 0.28103 | 0.22222 | 0.35672 | 0.32824 | 0.19824 | 73.258 | 73.2121 | 73.2437 | 73.1307 | 48.1007 | 48.2074 | 47.829 | 47.9395 | 48.2191 | 48.4047 | 48.4561 | 48.3973 | 48.5318 | 48.5033 | 48.3733 | 73.2764 | 73.2304 | 73.262 | 73.149 | 48.1191 | 48.2257 | 47.8473 | 47.9578 | 25.1573 | 25.4291 | 25.1429 | 25.4147
415.3125 | 121.5317 | -47.2687 | 74.2081 | 0.044018 | 0.27084 | 0.32682 | 0.26801 | 0.39792 | 0.37402 | 0.23486 | 74.1737 | 74.1278 | 74.1685 | 74.0556 | 47.1805 | 47.2918 | 46.9133 | 47.0238 | 47.3127 | 47.5395 | 47.5955 | 47.5367 | 47.6666 | 47.6427 | 47.5035 | 74.1921 | 74.1462 | 74.1868 | 74.0739 | 47.1988 | 47.3101 | 46.9316 | 47.0421 | 26.9932 | 27.2604 | 26.988 | 27.2552
417 | 121.5225 | -46.6965 | 74.7986 | 0.057754 | 0.30289 | 0.35887 | 0.30006 | 0.43912 | 0.40607 | 0.28065 | 74.6591 | 74.6132 | 74.6355 | 74.5319 | 46.709 | 46.8156 | 46.4372 | 46.5431 | 46.7542 | 46.9994 | 47.0553 | 46.9965 | 47.1356 | 47.1025 | 46.9771 | 74.6774 | 74.6315 | 74.6538 | 74.5502 | 46.7273 | 46.8339 | 46.4555 | 46.5614 | 27.9501 | 28.2219 | 27.9265 | 28.1983
418.7031 | 121.4859 | -46.1746 | 75.325 | 0.053175 | 0.31663 | 0.36802 | 0.32295 | 0.4437 | 0.4198 | 0.28522 | 75.3138 | 75.2771 | 75.2948 | 75.1912 | 46.0543 | 46.1564 | 45.787 | 45.9067 | 46.2278 | 46.4912 | 46.5426 | 46.4976 | 46.6183 | 46.5944 | 46.4598 | 75.3321 | 75.2954 | 75.3131 | 75.2095 | 46.0726 | 46.1747 | 45.8053 | 45.9251 | 29.2595 | 29.5268 | 29.2405 | 29.5077
420.4219 | 121.6324 | -45.5017 | 75.9476 | 0.044018 | 0.24337 | 0.29477 | 0.24054 | 0.36588 | 0.34197 | 0.21197 | 75.8815 | 75.8403 | 75.8579 | 75.7636 | 45.4729 | 45.5841 | 45.2101 | 45.3162 | 45.5457 | 45.7451 | 45.7965 | 45.7422 | 45.8676 | 45.8437 | 45.7137 | 75.8998 | 75.8586 | 75.8762 | 75.7819 | 45.4912 | 45.6024 | 45.2285 | 45.3345 | 30.4087 | 30.6714 | 30.385 | 30.6477
422.1094 | 121.6415 | -44.6594 | 76.7349 | 0.057754 | 0.30289 | 0.35429 | 0.30006 | 0.43455 | 0.41065 | 0.28065 | 76.6828 | 76.6279 | 76.6545 | 76.5512 | 44.6808 | 44.7921 | 44.4181 | 44.5241 | 44.7172 | 44.9623 | 45.0137 | 44.9595 | 45.094 | 45.0701 | 44.9401 | 76.7011 | 76.6462 | 76.6728 | 76.5695 | 44.6992 | 44.8104 | 44.4364 | 44.5425 | 32.0019 | 32.2647 | 31.9737 | 32.2364
423.8281 | 121.5363 | -43.8446 | 77.6321 | 0.057754 | 0.32121 | 0.37718 | 0.32295 | 0.44828 | 0.42896 | 0.2898 | 77.5756 | 77.5299 | 77.561 | 77.4533 | 43.7927 | 43.8948 | 43.5299 | 43.6314 | 43.9024 | 44.1658 | 44.2218 | 44.1676 | 44.2929 | 44.2736 | 44.1344 | 77.5939 | 77.5482 | 77.5793 | 77.4716 | 43.811 | 43.9131 | 43.5482 | 43.6497 | 33.7829 | 34.0457 | 33.7683 | 34.0311
425.5625 | 121.5271 | -43.0847 | 78.3875 | 0.085224 | 0.41736 | 0.46875 | 0.40994 | 0.54442 | 0.52053 | 0.39052 | 78.244 | 78.1893 | 78.2249 | 78.1218 | 43.1197 | 43.2173 | 42.8614 | 42.963 | 43.1699 | 43.5021 | 43.5535 | 43.4947 | 43.6291 | 43.6052 | 43.4752 | 78.2623 | 78.2076 | 78.2432 | 78.1401 | 43.138 | 43.2356 | 42.8797 | 42.9813 | 35.1243 | 35.3826 | 35.1052 | 35.3634
427.3281 | 121.5134 | -42.3431 | 79.1565 | 0.080646 | 0.38989 | 0.44586 | 0.3962 | 0.52611 | 0.50222 | 0.36763 | 78.9766 | 78.9264 | 78.9574 | 78.8499 | 42.3872 | 42.4939 | 42.1243 | 42.2305 | 42.4238 | 42.733 | 42.789 | 42.7393 | 42.8692 | 42.8454 | 42.7108 | 78.9949 | 78.9448 | 78.9757 | 78.8682 | 42.4055 | 42.5122 | 42.1426 | 42.2488 | 36.5894 | 36.8523 | 36.5702 | 36.8331
429.0312 | 121.5546 | -41.3773 | 80.04 | 0.10354 | 0.47231 | 0.51912 | 0.47404 | 0.60851 | 0.57547 | 0.44088 | 79.9976 | 79.9521 | 79.9829 | 79.8756 | 41.3479 | 41.4547 | 41.0942 | 41.1958 | 41.4808 | 41.8496 | 41.8964 | 41.8513 | 41.9858 | 41.9527 | 41.8181 | 80.0159 | 79.9704 | 80.0012 | 79.8939 | 41.3662 | 41.473 | 41.1125 | 41.2141 | 38.6497 | 38.9034 | 38.635 | 38.8887
430.7031 | 121.6049 | -40.6815 | 80.7083 | 0.10354 | 0.42652 | 0.47791 | 0.44199 | 0.57189 | 0.53884 | 0.40884 | 80.634 | 80.5794 | 80.6101 | 80.5121 | 40.7207 | 40.8321 | 40.4624 | 40.5778 | 40.785 | 41.108 | 41.1594 | 41.1234 | 41.2533 | 41.2203 | 41.0903 | 80.6523 | 80.5977 | 80.6285 | 80.5304 | 40.739 | 40.8504 | 40.4807 | 40.5961 | 39.9133 | 40.1716 | 39.8894 | 40.1478
432.4531 | 121.6049 | -39.592 | 81.8253 | 0.10812 | 0.43568 | 0.49165 | 0.43741 | 0.57646 | 0.53884 | 0.41341 | 81.8977 | 81.834 | 81.8692 | 81.7667 | 39.4709 | 39.5777 | 39.2125 | 39.3096 | 39.7001 | 40.0277 | 40.0836 | 40.0294 | 40.1684 | 40.1308 | 40.0054 | 81.916 | 81.8523 | 81.8875 | 81.785 | 39.4892 | 39.596 | 39.2308 | 39.3279 | 42.4268 | 42.6852 | 42.3983 | 42.6567
434.125 | 121.5729 | -38.3423 | 83.0795 | 0.094381 | 0.3441 | 0.38176 | 0.34126 | 0.47117 | 0.4427 | 0.31269 | 82.937 | 82.8734 | 82.9084 | 82.8016 | 38.4316 | 38.5385 | 38.1777 | 38.2841 | 38.4367 | 38.6864 | 38.724 | 38.6835 | 38.8135 | 38.785 | 38.655 | 82.9553 | 82.8917 | 82.9268 | 82.8199 | 38.45 | 38.5568 | 38.1961 | 38.3024 | 44.5053 | 44.7592 | 44.4768 | 44.7307
435.8125 | 121.5729 | -37.3856 | 84.0408 | 0.089802 | 0.28458 | 0.33597 | 0.28174 | 0.41166 | 0.38776 | 0.25776 | 83.9763 | 83.9265 | 83.9614 | 83.8502 | 37.3832 | 37.4855 | 37.1293 | 37.2357 | 37.4754 | 37.6701 | 37.7215 | 37.6673 | 37.7972 | 37.7733 | 37.6433 | 83.9946 | 83.9448 | 83.9798 | 83.8685 | 37.4015 | 37.5038 | 37.1476 | 37.254 | 46.5931 | 46.847 | 46.5782 | 46.8322
437.5469 | 121.5637 | -36.9507 | 84.4986 | 0.10354 | 0.34868 | 0.38634 | 0.33668 | 0.46202 | 0.43354 | 0.30812 | 84.4021 | 84.3523 | 84.3781 | 84.276 | 36.9575 | 37.0689 | 36.7081 | 36.8145 | 37.0542 | 37.2994 | 37.337 | 37.2874 | 37.4127 | 37.3842 | 37.2588 | 84.4204 | 84.3707 | 84.3964 | 84.2943 | 36.9758 | 37.0872 | 36.7264 | 36.8328 | 47.4446 | 47.694 | 47.4206 | 47.67
439.2188 | 121.5912 | -36.3007 | 85.1212 | 0.11269 | 0.34868 | 0.3955 | 0.34584 | 0.47575 | 0.43812 | 0.32185 | 85.1484 | 85.1033 | 85.1335 | 85.0224 | 36.2204 | 36.3181 | 35.9618 | 36.0774 | 36.4134 | 36.6493 | 36.6962 | 36.6465 | 36.7764 | 36.7388 | 36.6225 | 85.1667 | 85.1216 | 85.1518 | 85.0407 | 36.2387 | 36.3364 | 35.9801 | 36.0957 | 48.928 | 49.1866 | 48.9131 | 49.1717
440.9688 | 121.582 | -36.0168 | 85.3592 | 0.098959 | 0.29831 | 0.34513 | 0.2909 | 0.42997 | 0.38776 | 0.26233 | 85.4277 | 85.3734 | 85.4082 | 85.2972 | 35.9365 | 36.048 | 35.6825 | 35.7936 | 36.1158 | 36.3152 | 36.362 | 36.3077 | 36.4468 | 36.4046 | 36.2792 | 85.446 | 85.3917 | 85.4265 | 85.3155 | 35.9548 | 36.0663 | 35.7008 | 35.8119 | 49.4912 | 49.7452 | 49.4716 | 49.7257
442.6562 | 121.5134 | -36.7538 | 84.7366 | 0.13559 | 0.39905 | 0.44128 | 0.39163 | 0.52611 | 0.49764 | 0.36763 | 84.7043 | 84.6454 | 84.6802 | 84.5737 | 36.669 | 36.7714 | 36.4105 | 36.5352 | 36.8894 | 37.1529 | 37.1951 | 37.1455 | 37.28 | 37.2515 | 37.1215 | 84.7226 | 84.6637 | 84.6985 | 84.592 | 36.6874 | 36.7897 | 36.4288 | 36.5535 | 48.0352 | 48.2938 | 48.0112 | 48.2698
444.3906 | 121.6095 | -36.676 | 84.6954 | 0.20884 | 0.6692 | 0.72058 | 0.66634 | 0.79163 | 0.76776 | 0.64232 | 84.6081 | 84.5584 | 84.5841 | 84.4775 | 36.7606 | 36.8629 | 36.5112 | 36.6176 | 36.8849 | 37.3452 | 37.3966 | 37.3424 | 37.4677 | 37.4438 | 37.3183 | 84.6264 | 84.5767 | 84.6024 | 84.4958 | 36.7789 | 36.8812 | 36.5295 | 36.6359 | 47.8475 | 48.0969 | 47.8235 | 48.0729
446.0625 | 121.5088 | -37.0377 | 84.4391 | 0.20426 | 0.59593 | 0.63358 | 0.57934 | 0.71838 | 0.68077 | 0.56449 | 84.2602 | 84.2012 | 84.2407 | 84.1341 | 37.1131 | 37.2154 | 36.8546 | 36.9656 | 37.2419 | 37.6336 | 37.6712 | 37.617 | 37.756 | 37.7184 | 37.6022 | 84.2785 | 84.2196 | 84.259 | 84.1524 | 37.1314 | 37.2337 | 36.8729 | 36.9839 | 47.147 | 47.4056 | 47.1276 | 47.3861
447.7344 | 121.4905 | -37.381 | 84.1187 | 0.218 | 0.65546 | 0.68395 | 0.64344 | 0.76416 | 0.74029 | 0.61943 | 84.0496 | 83.9952 | 84.0347 | 83.9234 | 37.3191 | 37.4214 | 37.056 | 37.167 | 37.599 | 38.0364 | 38.0649 | 38.0244 | 38.1451 | 38.1213 | 38.0004 | 84.0679 | 84.0135 | 84.053 | 83.9418 | 37.3375 | 37.4398 | 37.0743 | 37.1853 | 46.7304 | 46.9935 | 46.7156 | 46.9787
449.4688 | 121.5775 | -37.2528 | 84.1644 | 0.25005 | 0.78367 | 0.81673 | 0.75791 | 0.88777 | 0.86849 | 0.74762 | 84.3014 | 84.2516 | 84.2773 | 84.157 | 37.0673 | 37.1742 | 36.8134 | 36.9198 | 37.5029 | 38.0365 | 38.0695 | 38.0107 | 38.1406 | 38.1213 | 38.0004 | 84.3197 | 84.2699 | 84.2957 | 84.1753 | 37.0857 | 37.1925 | 36.8317 | 36.9381 | 47.234 | 47.488 | 47.21 | 47.464
451.1406 | 121.6415 | -35.6598 | 85.7071 | 0.2592 | 0.7333 | 0.76178 | 0.70296 | 0.83741 | 0.81812 | 0.70184 | 85.7665 | 85.6985 | 85.7378 | 85.636 | 35.6161 | 35.7138 | 35.3575 | 35.4685 | 35.919 | 36.3931 | 36.4216 | 36.3628 | 36.4972 | 36.4779 | 36.3616 | 85.7848 | 85.7168 | 85.7561 | 85.6543 | 35.6344 | 35.7321 | 35.3758 | 35.4868 | 50.1504 | 50.409 | 50.1218 | 50.3804
452.875 | 121.5729 | -36.1633 | 85.2676 | 0.24547 | 0.6463 | 0.67479 | 0.62971 | 0.75958 | 0.74487 | 0.61485 | 85.4735 | 85.4146 | 85.454 | 85.3384 | 35.8953 | 36.0022 | 35.6505 | 35.7478 | 36.4088 | 36.8096 | 36.8381 | 36.793 | 36.9229 | 36.9082 | 36.7782 | 85.4918 | 85.4329 | 85.4723 | 85.3567 | 35.9136 | 36.0206 | 35.6688 | 35.7661 | 49.5781 | 49.823 | 49.5586 | 49.8035
454.6094 | 121.4813 | -36.3876 | 85.1028 | 0.27294 | 0.71498 | 0.73889 | 0.68923 | 0.8191 | 0.78608 | 0.67437 | 85.0706 | 85.0071 | 85.0465 | 84.9354 | 36.3074 | 36.4097 | 36.0534 | 36.1507 | 36.6606 | 37.1026 | 37.1265 | 37.0769 | 37.2067 | 37.1737 | 37.062 | 85.0889 | 85.0254 | 85.0648 | 84.9537 | 36.3257 | 36.428 | 36.0717 | 36.169 | 48.7632 | 49.0172 | 48.7391 | 48.9931
456.3594 | 121.5317 | -35.7513 | 85.7162 | 0.29125 | 0.73788 | 0.76636 | 0.71212 | 0.83741 | 0.81355 | 0.70184 | 85.6475 | 85.5932 | 85.6325 | 85.517 | 35.7305 | 35.8283 | 35.4811 | 35.5784 | 36.0426 | 36.4892 | 36.5177 | 36.4635 | 36.5888 | 36.5649 | 36.4532 | 85.6658 | 85.6115 | 85.6508 | 85.5353 | 35.7488 | 35.8466 | 35.4994 | 35.5967 | 49.9169 | 50.1664 | 49.902 | 50.1514
458.0469 | 121.637 | -35.0281 | 86.3754 | 0.30956 | 0.79282 | 0.80757 | 0.74875 | 0.87861 | 0.85933 | 0.7522 | 86.261 | 86.2068 | 86.2323 | 86.126 | 35.1125 | 35.224 | 34.8584 | 34.9558 | 35.3376 | 35.8209 | 35.8356 | 35.7768 | 35.9067 | 35.8874 | 35.7803 | 86.2793 | 86.2251 | 86.2506 | 86.1443 | 35.1308 | 35.2423 | 34.8767 | 34.9741 | 51.1485 | 51.4026 | 51.1198 | 51.3739
459.7344 | 121.6187 | -35.0555 | 86.3617 | 0.36908 | 0.91187 | 0.92661 | 0.87237 | 0.99764 | 0.98752 | 0.87581 | 86.4991 | 86.4357 | 86.4749 | 86.3641 | 34.8836 | 34.9722 | 34.6203 | 34.7268 | 35.4246 | 35.9674 | 35.9822 | 35.9279 | 36.0532 | 36.0431 | 35.9314 | 86.5174 | 86.454 | 86.4932 | 86.3824 | 34.9019 | 34.9905 | 34.6386 | 34.7452 | 51.6155 | 51.8787 | 51.5914 | 51.8546
461.4688 | 121.6187 | -33.4534 | 87.9684 | 0.43776 | 1.0996 | 1.096 | 1.0372 | 1.1762 | 1.1569 | 1.0544 | 87.9367 | 87.8826 | 87.9079 | 87.811 | 33.4414 | 33.5347 | 33.1873 | 33.2985 | 33.8911 | 34.553 | 34.5494 | 34.4906 | 34.6295 | 34.6103 | 34.5077 | 87.955 | 87.9009 | 87.9262 | 87.8294 | 33.4597 | 33.553 | 33.2056 | 33.3168 | 54.4953 | 54.7494 | 54.4665 | 54.7206
463.2188 | 121.4767 | -31.7963 | 89.7171 | 0.42402 | 1.008 | 1.0136 | 0.95478 | 1.0938 | 1.0654 | 0.97195 | 89.7727 | 89.7187 | 89.753 | 89.6472 | 31.5918 | 31.6943 | 31.3422 | 31.4489 | 32.2203 | 32.8043 | 32.8099 | 32.751 | 32.89 | 32.8616 | 32.7682 | 89.791 | 89.737 | 89.7713 | 89.6655 | 31.6102 | 31.7126 | 31.3605 | 31.4672 | 58.1808 | 58.4305 | 58.1611 | 58.4108
464.8906 | 121.4951 | -29.9652 | 91.5619 | 0.45149 | 1.0447 | 1.0457 | 0.99141 | 1.1212 | 1.1066 | 0.99484 | 91.5079 | 91.4495 | 91.4836 | 91.3781 | 29.8659 | 29.9775 | 29.6207 | 29.7229 | 30.4167 | 31.0099 | 31.0109 | 30.9566 | 31.0865 | 31.0718 | 30.9601 | 91.5262 | 91.4678 | 91.5019 | 91.3964 | 29.8842 | 29.9958 | 29.639 | 29.7412 | 61.6421 | 61.8872 | 61.6177 | 61.8628
466.6406 | 121.5912 | -28.4866 | 92.9443 | 0.47439 | 1.0584 | 1.064 | 1.0097 | 1.1396 | 1.1295 | 1.0269 | 92.6526 | 92.5942 | 92.6327 | 92.5137 | 28.7259 | 28.8193 | 28.5082 | 28.6013 | 28.961 | 29.545 | 29.5506 | 29.4964 | 29.6262 | 29.6161 | 29.5135 | 92.6709 | 92.6125 | 92.651 | 92.532 | 28.7442 | 28.8376 | 28.5265 | 28.6196 | 63.9266 | 64.1444 | 63.9068 | 64.1245
468.375 | 121.4905 | -26.6876 | 94.7479 | 0.55222 | 1.2187 | 1.2013 | 1.1517 | 1.2769 | 1.2668 | 1.1734 | 94.9052 | 94.847 | 94.8806 | 94.7666 | 26.4643 | 26.5668 | 26.2373 | 26.3305 | 27.2398 | 27.9063 | 27.889 | 27.8393 | 27.9645 | 27.9544 | 27.861 | 94.9235 | 94.8653 | 94.899 | 94.7849 | 26.4826 | 26.5852 | 26.2556 | 26.3488 | 68.4409 | 68.6679 | 68.4163 | 68.6433
470.125 | 121.5042 | -26.1612 | 95.3751 | 0.61174 | 1.3057 | 1.2792 | 1.2158 | 1.3593 | 1.3492 | 1.2466 | 95.0654 | 95.0073 | 95.0363 | 94.9269 | 26.3224 | 26.4158 | 26.0908 | 26.1886 | 26.7729 | 27.4668 | 27.4404 | 27.3769 | 27.5205 | 27.5104 | 27.4078 | 95.0837 | 95.0256 | 95.0546 | 94.9452 | 26.3407 | 26.4341 | 26.1091 | 26.2069 | 68.743 | 68.9746 | 68.7139 | 68.9455
471.8125 | 121.4951 | -23.7808 | 97.7142 | 0.6621 | 1.3972 | 1.3616 | 1.289 | 1.428 | 1.4225 | 1.3336 | 97.3592 | 97.3058 | 97.33 | 97.2255 | 24.0104 | 24.1222 | 23.7879 | 23.8812 | 24.4429 | 25.1781 | 25.1424 | 25.0698 | 25.2088 | 25.2033 | 25.1144 | 97.3776 | 97.3241 | 97.3483 | 97.2438 | 24.0287 | 24.1405 | 23.8062 | 23.8995 | 73.3489 | 73.5714 | 73.3196 | 73.5422
473.5469 | 121.5317 | -23.8266 | 97.673 | 0.7674 | 1.5941 | 1.5218 | 1.4676 | 1.6111 | 1.6102 | 1.5305 | 97.7301 | 97.663 | 97.7009 | 97.5919 | 23.6625 | 23.7422 | 23.4353 | 23.5241 | 24.594 | 25.4207 | 25.3484 | 25.2942 | 25.4377 | 25.4368 | 25.3571 | 97.7484 | 97.6813 | 97.7192 | 97.6102 | 23.6808 | 23.7605 | 23.4536 | 23.5424 | 74.0677 | 74.2948 | 74.0384 | 74.2655
475.2812 | 121.4676 | -21.8628 | 99.6918 | 0.95054 | 1.9375 | 1.8378 | 1.7835 | 1.9224 | 1.9353 | 1.8647 | 99.3143 | 99.261 | 99.285 | 99.1762 | 22.0738 | 22.1627 | 21.8421 | 21.9446 | 22.8133 | 23.8003 | 23.7005 | 23.6463 | 23.7852 | 23.798 | 23.7275 | 99.3326 | 99.2793 | 99.3033 | 99.1945 | 22.0921 | 22.1811 | 21.8604 | 21.9629 | 77.2404 | 77.4722 | 77.2111 | 77.4429
476.9531 | 121.55 | -21.2769 | 100.1862 | 0.92765 | 1.8322 | 1.737 | 1.6873 | 1.8354 | 1.8391 | 1.7594 | 99.9095 | 99.8425 | 99.8847 | 99.7761 | 21.4604 | 21.563 | 21.2514 | 21.3357 | 22.2045 | 23.1091 | 23.0139 | 22.9642 | 23.1123 | 23.116 | 23.0363 | 99.9278 | 99.8608 | 99.903 | 99.7944 | 21.4787 | 21.5813 | 21.2698 | 21.354 | 78.4491 | 78.658 | 78.4244 | 78.6333
478.625 | 121.6095 | -19.6747 | 101.7792 | 0.93223 | 1.7956 | 1.6958 | 1.6324 | 1.7896 | 1.7979 | 1.7273 | 101.6951 | 101.6328 | 101.6702 | 101.5665 | 19.6886 | 19.7867 | 19.475 | 19.5594 | 20.6069 | 21.4703 | 21.3705 | 21.3071 | 21.4643 | 21.4726 | 21.402 | 101.7134 | 101.6511 | 101.6885 | 101.5848 | 19.7069 | 19.805 | 19.4933 | 19.5777 | 82.0065 | 82.2201 | 81.9816 | 82.1952
480.3594 | 121.5683 | -18.3884 | 103.0884 | 0.91391 | 1.7086 | 1.6271 | 1.5637 | 1.721 | 1.7201 | 1.6404 | 103.0045 | 102.9469 | 102.9796 | 102.8715 | 18.3747 | 18.4682 | 18.1656 | 18.2454 | 19.3023 | 20.097 | 20.0155 | 19.9521 | 20.1093 | 20.1084 | 20.0287 | 103.0228 | 102.9652 | 102.9979 | 102.8898 | 18.393 | 18.4866 | 18.1839 | 18.2637 | 84.6299 | 84.8389 | 84.605 | 84.814
482.0938 | 121.6187 | -17.482 | 103.9764 | 1.0055 | 1.8185 | 1.7096 | 1.6553 | 1.8034 | 1.8254 | 1.7548 | 103.792 | 103.7253 | 103.7717 | 103.6545 | 17.5918 | 17.69 | 17.3919 | 17.4671 | 18.4875 | 19.3005 | 19.1915 | 19.1373 | 19.2854 | 19.3074 | 19.2368 | 103.8103 | 103.7436 | 103.79 | 103.6728 | 17.6101 | 17.7083 | 17.4102 | 17.4854 | 86.2002 | 86.4002 | 86.1799 | 86.3798
483.7656 | 121.4996 | -17.8116 | 103.6789 | 1.0604 | 1.9009 | 1.7874 | 1.7331 | 1.8812 | 1.8986 | 1.8326 | 103.6501 | 103.5742 | 103.6206 | 103.5171 | 17.7383 | 17.8365 | 17.5384 | 17.6228 | 18.872 | 19.7125 | 19.599 | 19.5447 | 19.6928 | 19.7102 | 19.6442 | 103.6684 | 103.5925 | 103.6389 | 103.5354 | 17.7566 | 17.8548 | 17.5567 | 17.6411 | 85.9118 | 86.1117 | 85.8823 | 86.0822
485.4844 | 121.6141 | -17.5507 | 103.8895 | 1.1657 | 2.052 | 1.8973 | 1.8476 | 2.0094 | 2.0268 | 1.9746 | 104.021 | 103.9497 | 103.996 | 103.8834 | 17.3629 | 17.4611 | 17.1629 | 17.2291 | 18.7164 | 19.6027 | 19.4479 | 19.3982 | 19.56 | 19.5775 | 19.5252 | 104.0393 | 103.968 | 104.0143 | 103.9018 | 17.3812 | 17.4794 | 17.1813 | 17.2474 | 86.6581 | 86.858 | 86.6331 | 86.8331
487.2344 | 121.6187 | -16.7038 | 104.7226 | 1.2985 | 2.2672 | 2.0621 | 2.017 | 2.1879 | 2.21 | 2.176 | 104.7123 | 104.6457 | 104.6827 | 104.5795 | 16.6762 | 16.7744 | 16.4716 | 16.5607 | 18.0023 | 18.971 | 18.7659 | 18.7208 | 18.8917 | 18.9138 | 18.8798 | 104.7306 | 104.664 | 104.7011 | 104.5978 | 16.6945 | 16.7927 | 16.4899 | 16.579 | 88.0361 | 88.2407 | 88.0066 | 88.2111
488.9219 | 121.6095 | -16.9235 | 104.5349 | 1.4633 | 2.4916 | 2.2086 | 2.1818 | 2.3848 | 2.4435 | 2.4141 | 104.5246 | 104.4534 | 104.495 | 104.3826 | 16.8684 | 16.9621 | 16.6639 | 16.7438 | 18.3868 | 19.4151 | 19.1321 | 19.1053 | 19.3083 | 19.367 | 19.3376 | 104.5429 | 104.4717 | 104.5133 | 104.4009 | 16.8868 | 16.9804 | 16.6822 | 16.7621 | 87.6561 | 87.8607 | 87.6266 | 87.8311
490.6562 | 121.6278 | -16.8594 | 104.5944 | 1.6052 | 2.693 | 2.3597 | 2.3421 | 2.5496 | 2.6266 | 2.6109 | 104.607 | 104.5495 | 104.5958 | 104.4879 | 16.7631 | 16.8659 | 16.554 | 16.6385 | 18.4647 | 19.5525 | 19.2192 | 19.2015 | 19.409 | 19.486 | 19.4704 | 104.6253 | 104.5678 | 104.6141 | 104.5062 | 16.7815 | 16.8842 | 16.5723 | 16.6568 | 87.8439 | 88.053 | 87.8326 | 88.0417
492.3906 | 121.4996 | -16.745 | 104.805 | 1.7243 | 2.8396 | 2.4742 | 2.4611 | 2.6777 | 2.7594 | 2.7483 | 104.6894 | 104.6228 | 104.6599 | 104.5474 | 16.7036 | 16.8018 | 16.5082 | 16.5835 | 18.4693 | 19.5846 | 19.2192 | 19.2061 | 19.4227 | 19.5044 | 19.4933 | 104.7077 | 104.6411 | 104.6782 | 104.5657 | 16.7219 | 16.8201 | 16.5265 | 16.6019 | 87.9858 | 88.1812 | 87.9562 | 88.1516
494.0781 | 121.5637 | -16.0629 | 105.423 | 1.8571 | 3.0181 | 2.6115 | 2.6076 | 2.8288 | 2.9196 | 2.9268 | 105.3991 | 105.3325 | 105.3695 | 105.2617 | 15.9894 | 16.0831 | 15.7848 | 15.8602 | 17.92 | 19.0811 | 18.6745 | 18.6705 | 18.8917 | 18.9825 | 18.9898 | 105.4174 | 105.3508 | 105.3878 | 105.28 | 16.0077 | 16.1014 | 15.8032 | 15.8785 | 89.4096 | 89.6142 | 89.3801 | 89.5846
495.75 | 121.5683 | -15.7242 | 105.7388 | 1.8937 | 3.0502 | 2.5383 | 2.5481 | 2.8014 | 2.915 | 2.936 | 105.715 | 105.6438 | 105.6854 | 105.5731 | 15.6735 | 15.7718 | 15.4827 | 15.5626 | 17.6179 | 18.7744 | 18.2625 | 18.2723 | 18.5255 | 18.6392 | 18.6602 | 105.7333 | 105.6622 | 105.7037 | 105.5914 | 15.6919 | 15.7901 | 15.501 | 15.5809 | 90.0415 | 90.2323 | 90.0118 | 90.2027
497.4844 | 121.4859 | -15.2481 | 106.2515 | 1.9761 | 3.1875 | 2.5291 | 2.571 | 2.8563 | 3.0112 | 3.0688 | 106.2827 | 106.2116 | 106.2577 | 106.1501 | 15.1013 | 15.2087 | 14.9104 | 14.9903 | 17.2242 | 18.4357 | 17.7772 | 17.8191 | 18.1044 | 18.2593 | 18.3169 | 106.301 | 106.2299 | 106.276 | 106.1684 | 15.1196 | 15.227 | 14.9287 | 15.0087 | 91.1815 | 91.3724 | 91.1564 | 91.3473
499.2188 | 121.6507 | -29.3198 | 92.0334 | 16.192 | 26.9241 | 20.1934 | 20.9765 | 22.5415 | 24.3007 | 25.8681 | 92.4969 | 92.4294 | 92.4267 | 92.2985 | 28.9457 | 29.0344 | 28.7096 | 28.8027 | 45.5118 | 56.2439 | 49.5131 | 50.2963 | 51.8613 | 53.6204 | 55.1878 | 92.5152 | 92.4477 | 92.445 | 92.3168 | 28.964 | 29.0527 | 28.7279 | 28.821 | 63.5512 | 63.7872 | 63.481 | 63.7171
500.9531 | 121.6187 | -36.3876 | 84.9518 | 19.2458 | 31.9929 | 23.4945 | 24.5295 | 26.3961 | 28.5815 | 30.5744 | 85.0797 | 84.9659 | 84.9961 | 84.8759 | 36.3394 | 36.4417 | 36.09 | 36.1919 | 55.6334 | 68.3805 | 59.8822 | 60.9171 | 62.7838 | 64.9691 | 66.9621 | 85.098 | 84.9842 | 85.0144 | 84.8942 | 36.3577 | 36.46 | 36.1083 | 36.2102 | 48.7403 | 48.9897 | 48.6567 | 48.9061
502.6875 | 121.2112 | -62.0636 | 59.3079 | 14.3149 | 23.3343 | 17.6019 | 18.1608 | 19.4651 | 20.9447 | 22.3703 | 59.4401 | 59.407 | 59.4219 | 59.3203 | 62.1603 | 62.0835 | 61.7335 | 62.0036 | 76.3785 | 85.3979 | 79.6655 | 80.2244 | 81.5287 | 83.0083 | 84.4339 | 59.4585 | 59.4253 | 59.4402 | 59.3386 | 62.1786 | 62.1018 | 61.7519 | 62.0219 | -2.7202 | -2.2934 | -2.7385 | -2.3117
504.4219 | 121.582 | -60.2005 | 61.1572 | 14.8963 | 23.9983 | 18.0689 | 18.6049 | 19.9595 | 21.5903 | 23.0387 | 60.9419 | 60.8722 | 60.864 | 60.7673 | 60.4252 | 60.5498 | 60.1632 | 60.2776 | 75.0968 | 84.1988 | 78.2694 | 78.8054 | 80.16 | 81.7908 | 83.2392 | 60.9602 | 60.8905 | 60.8823 | 60.7856 | 60.4435 | 60.5681 | 60.1815 | 60.2959 | 0.51671 | 0.77874 | 0.43884 | 0.70086
506.0938 | 121.4859 | -57.9941 | 63.4415 | 16.2515 | 25.5688 | 19.5112 | 20.0746 | 21.4932 | 23.1927 | 24.7372 | 63.4097 | 63.3264 | 63.3454 | 63.2354 | 57.9621 | 58.0868 | 57.6954 | 57.8192 | 74.2456 | 83.5629 | 77.5052 | 78.0687 | 79.4872 | 81.1868 | 82.7313 | 63.428 | 63.3447 | 63.3638 | 63.2537 | 57.9804 | 58.1051 | 57.7137 | 57.8375 | 5.4476 | 5.7143 | 5.3833 | 5.65
507.8281 | 121.5225 | -56.012 | 65.4236 | 17.419 | 26.7776 | 20.349 | 21.1185 | 22.8482 | 24.9142 | 26.9531 | 65.3235 | 65.2358 | 65.2454 | 65.1403 | 56.0713 | 56.1686 | 55.8 | 55.9146 | 73.431 | 82.7896 | 76.361 | 77.1304 | 78.8602 | 80.9261 | 82.965 | 65.3418 | 65.2541 | 65.2637 | 65.1586 | 56.0897 | 56.1869 | 55.8183 | 55.9329 | 9.2522 | 9.5236 | 9.1741 | 9.4455
509.5625 | 121.5271 | -55.0552 | 66.3666 | 17.9638 | 27.2767 | 20.4544 | 21.3016 | 23.155 | 25.3903 | 27.5711 | 66.3766 | 66.2935 | 66.303 | 66.2026 | 54.9955 | 55.1157 | 54.7378 | 54.8525 | 73.0191 | 82.3319 | 75.5096 | 76.3569 | 78.2102 | 80.4456 | 82.6264 | 66.3949 | 66.3118 | 66.3213 | 66.2209 | 55.0138 | 55.134 | 54.7561 | 54.8708 | 11.3811 | 11.6388 | 11.3075 | 11.5652
511.25 | 121.5775 | -52.7618 | 68.6783 | 19.1725 | 28.5817 | 21.3655 | 22.3684 | 24.4643 | 26.9836 | 29.5718 | 68.2583 | 68.1616 | 68.1664 | 68.0617 | 53.1184 | 53.2432 | 52.8606 | 52.9754 | 71.9344 | 81.3435 | 74.1273 | 75.1302 | 77.2261 | 79.7455 | 82.3336 | 68.2766 | 68.18 | 68.1847 | 68.08 | 53.1367 | 53.2615 | 52.8789 | 52.9938 | 15.1399 | 15.3977 | 15.048 | 15.3057
512.9844 | 121.4584 | -48.967 | 72.5143 | 20.1431 | 29.6027 | 22.153 | 23.1605 | 25.357 | 28.0092 | 30.7438 | 70.1492 | 70.0848 | 70.0709 | 69.9757 | 51.2002 | 51.3204 | 50.9514 | 51.0709 | 69.1101 | 78.5697 | 71.12 | 72.1275 | 74.3239 | 76.9762 | 79.7108 | 70.1676 | 70.1031 | 70.0893 | 69.994 | 51.2185 | 51.3388 | 50.9698 | 51.0892 | 18.9491 | 19.1978 | 18.8708 | 19.1195
514.7188 | 121.4127 | -9.7229 | 111.8866 | 36.5063 | 53.5545 | 37.3494 | 40.1146 | 44.827 | 50.425 | 55.9879 | 111.6487 | 111.5826 | 111.5959 | 111.4801 | 9.6807 | 9.7653 | 9.5262 | 9.5973 | 46.2292 | 63.2774 | 47.0723 | 49.8375 | 54.5499 | 60.1479 | 65.7108 | 111.667 | 111.6009 | 111.6143 | 111.4984 | 9.699 | 9.7837 | 9.5445 | 9.6156 | 101.968 | 102.1225 | 101.9152 | 102.0698
516.4531 | 121.3715 | -8.8623 | 112.6923 | 44.6879 | 63.5089 | 45.1605 | 48.6169 | 54.5048 | 61.5642 | 68.8022 | 112.5232 | 112.4571 | 112.4567 | 112.3455 | 8.7605 | 8.8497 | 8.6334 | 8.6908 | 53.5502 | 72.3712 | 54.0228 | 57.4792 | 63.3671 | 70.4265 | 77.6645 | 112.5415 | 112.4754 | 112.475 | 112.3638 | 8.7788 | 8.868 | 8.6517 | 8.7091 | 103.7627 | 103.8898 | 103.6962 | 103.8233
518.125 | 121.4676 | -8.2397 | 113.1958 | 44.6375 | 64.3651 | 44.9178 | 47.7287 | 53.1681 | 59.7969 | 66.5863 | 113.5259 | 113.4553 | 113.4456 | 113.3346 | 7.7213 | 7.8105 | 7.6033 | 7.6698 | 52.8773 | 72.6049 | 53.1576 | 55.9684 | 61.4078 | 68.0367 | 74.8261 | 113.5442 | 113.4736 | 113.4639 | 113.3529 | 7.7396 | 7.8288 | 7.6216 | 7.6882 | 105.8047 | 105.9226 | 105.7243 | 105.8423
519.8594 | 121.4081 | -7.3334 | 114.093 | 41.1213 | 57.996 | 38.8878 | 42.4085 | 48.5809 | 55.8503 | 63.0611 | 113.9975 | 113.9223 | 113.8988 | 113.7925 | 7.2177 | 7.3023 | 7.1088 | 7.18 | 48.4547 | 65.3294 | 46.2212 | 49.7418 | 55.9143 | 63.1837 | 70.3945 | 114.0158 | 113.9407 | 113.9171 | 113.8108 | 7.236 | 7.3207 | 7.1271 | 7.1983 | 106.7798 | 106.8887 | 106.6812 | 106.79
521.5312 | 121.4905 | -38.9008 | 83.2672 | 27.7662 | 38.6734 | 26.1227 | 28.3845 | 32.668 | 37.6375 | 42.5509 | 75.8449 | 75.8495 | 75.7892 | 75.6995 | 45.5461 | 45.4697 | 45.375 | 45.481 | 66.6669 | 77.5741 | 65.0234 | 67.2853 | 71.5687 | 76.5383 | 81.4517 | 75.8632 | 75.8678 | 75.8075 | 75.7178 | 45.5644 | 45.488 | 45.3933 | 45.4993 | 30.2988 | 30.4699 | 30.2431 | 30.4142
523.2812 | 121.3303 | -4.4174 | 116.9952 | 44.0423 | 59.5116 | 40.7238 | 44.4551 | 51.3598 | 59.4993 | 67.5752 | 116.6942 | 116.6193 | 116.5863 | 116.4804 | 4.4433 | 4.5326 | 4.3847 | 4.4331 | 48.4597 | 63.929 | 45.1412 | 48.8725 | 55.7772 | 63.9167 | 71.9926 | 116.7125 | 116.6376 | 116.6046 | 116.4987 | 4.4616 | 4.5509 | 4.403 | 4.4514 | 112.2509 | 112.3096 | 112.143 | 112.2016
525.0156 | 121.3211 | -6.0287 | 115.2969 | 45.8096 | 61.5034 | 43.0406 | 46.1491 | 53.017 | 61.2116 | 69.4065 | 115.4809 | 115.3921 | 115.3181 | 115.1982 | 5.5924 | 5.6863 | 5.5613 | 5.6188 | 51.8383 | 67.5321 | 49.0693 | 52.1779 | 59.0457 | 67.2404 | 75.4352 | 115.4992 | 115.4105 | 115.3364 | 115.2165 | 5.6107 | 5.7046 | 5.5796 | 5.6371 | 109.8885 | 109.9196 | 109.7257 | 109.7568
526.75 | 121.1563 | -4.6555 | 116.6382 | 57.8095 | 75.1253 | 62.3531 | 62.2517 | 66.6364 | 72.7217 | 79.5471 | 116.6118 | 116.5414 | 116.4031 | 116.2972 | 4.3242 | 4.409 | 4.3618 | 4.4193 | 62.465 | 79.7808 | 67.0086 | 66.9071 | 71.2919 | 77.3772 | 84.2026 | 116.6301 | 116.5597 | 116.4215 | 116.3155 | 4.3426 | 4.4273 | 4.3801 | 4.4377 | 112.2876 | 112.2501 | 112.0789 | 112.0414
528.4844 | 121.2891 | -2.7374 | 118.5837 | 75.7293 | 96.6824 | 90.5436 | 85.4692 | 86.752 | 90.7285 | 96.111 | 118.37 | 118.3043 | 118.239 | 118.1334 | 2.6853 | 2.7609 | 2.6632 | 2.7025 | 78.4668 | 99.4198 | 93.281 | 88.2067 | 89.4894 | 93.4659 | 98.8484 | 118.3883 | 118.3226 | 118.2573 | 118.1517 | 2.7036 | 2.7792 | 2.6815 | 2.7208 | 115.6847 | 115.7068 | 115.5538 | 115.5758
530.1562 | 121.2616 | -5.1132 | 116.1209 | 57.1182 | 88.6008 | 78.4607 | 18.0188 | 42.0345 | 65.8953 | 87.2018 | 116.7858 | 116.7017 | 116.5771 | 116.4712 | 4.1686 | 4.2625 | 4.2061 | 4.2454 | 62.2314 | 93.714 | 83.5739 | 23.1321 | 47.1477 | 71.0085 | 92.3151 | 116.8041 | 116.72 | 116.5954 | 116.4895 | 4.1869 | 4.2808 | 4.2244 | 4.2637 | 112.6172 | 112.5797 | 112.4085 | 112.371
531.8906 | 121.2296 | -3.4012 | 118.0344 | 85.7011 | 104.4985 | 103.8536 | 102.1395 | 98.9843 | 98.9147 | 101.3896 | 118.2921 | 118.2127 | 118.1429 | 118.0418 | 2.7539 | 2.8296 | 2.7273 | 2.7804 | 89.1023 | 107.8996 | 107.2548 | 105.5407 | 102.3854 | 102.3158 | 104.7908 | 118.3104 | 118.231 | 118.1612 | 118.0601 | 2.7722 | 2.8479 | 2.7456 | 2.7987 | 115.5382 | 115.5648 | 115.389 | 115.4156
533.6406 | 121.1792 | -5.3192 | 115.9012 | 70.2582 | 91.9937 | 86.258 | 78.9586 | 62.4888 | 78.0143 | 89.3307 | 116.2867 | 116.2026 | 116.0552 | 115.94 | 4.5806 | 4.67 | 4.641 | 4.6986 | 75.5774 | 97.3129 | 91.5772 | 84.2778 | 67.808 | 83.3335 | 94.6499 | 116.3051 | 116.2209 | 116.0735 | 115.9584 | 4.5989 | 4.6883 | 4.6594 | 4.7169 | 111.7061 | 111.6457 | 111.4746 | 111.4141
535.375 | 121.1975 | -5.1819 | 115.8691 | 56.99 | 85.7161 | 77.371 | 67.4391 | 8.4368 | 53.7351 | 80.5543 | 116.1036 | 116.0286 | 115.8309 | 115.7157 | 4.663 | 4.734 | 4.7601 | 4.8131 | 62.1719 | 90.898 | 82.5528 | 72.621 | 13.6187 | 58.917 | 85.7362 | 116.1219 | 116.0469 | 115.8492 | 115.734 | 4.6813 | 4.7524 | 4.7784 | 4.8314 | 111.4406 | 111.3435 | 111.1678 | 111.0708
537.0469 | 121.0281 | -5.658 | 115.3244 | 59.444 | 89.2327 | 82.966 | 77.3195 | 5.9922 | 51.9953 | 79.8264 | 115.2932 | 115.2136 | 114.9198 | 114.809 | 5.2857 | 5.3567 | 5.4697 | 5.5181 | 65.102 | 94.8906 | 88.624 | 82.9775 | 11.6501 | 57.6533 | 85.4844 | 115.3115 | 115.2319 | 114.9381 | 114.8273 | 5.304 | 5.375 | 5.488 | 5.5364 | 110.0075 | 109.8235 | 109.6341 | 109.45
538.7969 | 120.9274 | -17.244 | 103.6926 | 50.5665 | 77.3964 | 69.0196 | 61.8717 | 4.3533 | 45.6268 | 70.0383 | 104.4422 | 104.3572 | 103.9456 | 103.8285 | 16.1176 | 16.0465 | 16.2289 | 16.4554 | 67.8105 | 94.6404 | 86.2635 | 79.1156 | 21.5972 | 62.8708 | 87.2822 | 104.4605 | 104.3755 | 103.964 | 103.8468 | 16.1359 | 16.0648 | 16.2473 | 16.4737 | 88.3246 | 88.2132 | 87.828 | 87.7167
540.5469 | 120.8267 | -7.7042 | 113.118 | 53.6936 | 82.25 | 73.47 | 65.7817 | 4.9805 | 49.1384 | 74.6485 | 111.168 | 111.1247 | 110.5658 | 110.4864 | 8.9162 | 9.0191 | 9.3247 | 9.4004 | 61.3977 | 89.9541 | 81.1742 | 73.4859 | 12.6846 | 56.8426 | 82.3527 | 111.1863 | 111.143 | 110.5841 | 110.5047 | 8.9345 | 9.0374 | 9.3431 | 9.4187 | 102.2518 | 101.8432 | 101.6497 | 101.2411
542.2188 | 120.7809 | -5.4382 | 115.2603 | 54.5314 | 82.8132 | 73.8912 | 66.9126 | 6.276 | 49.4498 | 75.0743 | 111.2367 | 111.143 | 110.5292 | 110.4223 | 8.7742 | 8.7673 | 9.2515 | 9.3363 | 59.9696 | 88.2514 | 79.3295 | 72.3508 | 11.7143 | 54.888 | 80.5125 | 111.255 | 111.1613 | 110.5475 | 110.4406 | 8.7925 | 8.7856 | 9.2698 | 9.3546 | 102.4624 | 101.9852 | 101.755 | 101.2777
543.9688 | 120.5841 | -8.1345 | 112.4588 | 52.1873 | 80.8031 | 70.3245 | 61.7068 | 1.8995 | 47.6184 | 73.4765 | 111.9509 | 111.8894 | 111.1976 | 111.0908 | 7.767 | 7.8426 | 8.3312 | 8.3978 | 60.3217 | 88.9375 | 78.459 | 69.8413 | 10.034 | 55.7529 | 81.6109 | 111.9692 | 111.9077 | 111.2159 | 111.1092 | 7.7853 | 7.8609 | 8.3495 | 8.4161 | 104.1839 | 103.6197 | 103.4306 | 102.8664
545.7031 | 120.9457 | -0.16937 | 120.9412 | 0.016548 | -0.008469 | 0.038365 | -0.020438 | 0.10036 | 0.062691 | -0.044405 | 120.8973 | 120.8135 | 0.15602 | 0.10885 | 0.089439 | 0.091891 | 0.012299 | 0.047188 | 0.18592 | 0.1609 | 0.20774 | 0.14893 | 0.26973 | 0.23206 | 0.12497 | 120.9156 | 120.8318 | 0.17433 | 0.12716 | 0.10775 | 0.1102 | 0.03061 | 0.065499 | 120.8079 | 120.885 | 0.066581 | 0.14372
547.375 | 121.2067 | -0.16479 | 121.0052 | -0.006344 | -0.035942 | 0.024629 | -0.034174 | 0.095778 | 0.048956 | -0.062717 | 121.0118 | 120.9325 | 0.11482 | 0.072217 | 0.089439 | 0.10105 | 0.007721 | 0.056344 | 0.15845 | 0.12885 | 0.18942 | 0.13062 | 0.26057 | 0.21375 | 0.10208 | 121.0301 | 120.9508 | 0.13313 | 0.090528 | 0.10775 | 0.11936 | 0.026032 | 0.074655 | 120.9223 | 121.004 | 0.025377 | 0.10709
549.1406 | 121.2112 | -0.15564 | 121.0419 | -0.001765 | -0.035942 | 0.020051 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 121.0575 | 120.9783 | 0.10108 | 0.067638 | 0.080283 | 0.096469 | 0.003143 | 0.047188 | 0.15388 | 0.1197 | 0.17569 | 0.11689 | 0.22853 | 0.19544 | 0.092923 | 121.0758 | 120.9966 | 0.11939 | 0.085949 | 0.098594 | 0.11478 | 0.021454 | 0.065499 | 120.9773 | 121.0544 | 0.020798 | 0.097938
550.8906 | 121.2662 | -0.12817 | 121.0648 | 0.007391 | -0.026784 | 0.020051 | -0.047909 | 0.072888 | 0.039799 | -0.076452 | 121.0942 | 121.0104 | 0.041563 | -0.055996 | 0.080283 | 0.10105 | 0.007721 | 0.051766 | 0.13557 | 0.10139 | 0.14822 | 0.080265 | 0.20106 | 0.16797 | 0.051722 | 121.1125 | 121.0287 | 0.059874 | -0.037685 | 0.098594 | 0.11936 | 0.026032 | 0.070077 | 121.0139 | 121.0864 | -0.03872 | 0.033842
552.5781 | 121.3348 | -0.15106 | 121.0831 | -0.006344 | -0.031363 | 0.015472 | -0.052488 | 0.072888 | 0.048956 | -0.067295 | 121.1216 | 121.0287 | 0.027829 | -0.10637 | 0.094017 | 0.10105 | 0.012299 | 0.051766 | 0.14472 | 0.1197 | 0.16653 | 0.098574 | 0.22395 | 0.20002 | 0.083767 | 121.1399 | 121.047 | 0.04614 | -0.088054 | 0.11233 | 0.11936 | 0.03061 | 0.070077 | 121.0276 | 121.1093 | -0.066188 | 0.01553
554.3125 | 121.3074 | -0.16022 | 121.1334 | -0.006344 | -0.035942 | 0.020051 | -0.047909 | 0.06831 | 0.048956 | -0.067295 | 121.1308 | 121.047 | 0.032407 | -0.11552 | 0.098596 | 0.10562 | 0.007721 | 0.051766 | 0.15387 | 0.12427 | 0.18027 | 0.11231 | 0.22853 | 0.20917 | 0.092922 | 121.1491 | 121.0653 | 0.050718 | -0.097212 | 0.11691 | 0.12394 | 0.026032 | 0.070077 | 121.0322 | 121.1231 | -0.066189 | 0.024686
556.0469 | 121.1975 | -0.21515 | 121.1426 | -0.010922 | -0.0451 | 0.010893 | -0.052488 | 0.072888 | 0.044377 | -0.067295 | 121.1445 | 121.0607 | 0.02325 | -0.11094 | 0.098596 | 0.10105 | 0.012299 | 0.051766 | 0.20423 | 0.17005 | 0.22604 | 0.16266 | 0.28804 | 0.25953 | 0.14785 | 121.1628 | 121.079 | 0.041561 | -0.092633 | 0.11691 | 0.11936 | 0.03061 | 0.070077 | 121.0459 | 121.1322 | -0.075346 | 0.010951
557.7969 | 121.2158 | -0.20142 | 121.1655 | -0.024657 | -0.040521 | 0.015472 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.1537 | 121.0607 | 0.018672 | -0.10637 | 0.094017 | 0.10562 | 0.012299 | 0.047188 | 0.17676 | 0.1609 | 0.21689 | 0.14893 | 0.27888 | 0.24579 | 0.12954 | 121.172 | 121.079 | 0.036983 | -0.088054 | 0.11233 | 0.12394 | 0.03061 | 0.065499 | 121.0597 | 121.1414 | -0.075345 | 0.006373
559.5312 | 121.2067 | -0.20599 | 121.1655 | -0.015501 | -0.040521 | 0.010893 | -0.052488 | 0.077466 | 0.048956 | -0.067295 | 121.1537 | 121.079 | 0.027829 | -0.1201 | 0.098596 | 0.11478 | 0.012299 | 0.056344 | 0.19049 | 0.16547 | 0.21689 | 0.15351 | 0.28346 | 0.25495 | 0.1387 | 121.172 | 121.0974 | 0.04614 | -0.10179 | 0.11691 | 0.13309 | 0.03061 | 0.074655 | 121.0551 | 121.1414 | -0.070767 | 0.01553
561.2188 | 121.2204 | -0.20599 | 121.1838 | -0.024657 | -0.0451 | 0.015472 | -0.057066 | 0.06831 | 0.044377 | -0.08103 | 121.1674 | 121.0836 | 0.02325 | -0.11094 | 0.094017 | 0.11478 | 0.012299 | 0.056344 | 0.18134 | 0.16089 | 0.22147 | 0.14893 | 0.2743 | 0.25037 | 0.12496 | 121.1857 | 121.1019 | 0.041561 | -0.092633 | 0.11233 | 0.13309 | 0.03061 | 0.074655 | 121.0734 | 121.1551 | -0.070767 | 0.010951
562.9688 | 121.3623 | -0.14648 | 121.138 | -0.024657 | -0.0451 | 0.015472 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.1766 | 121.0882 | 0.02325 | -0.11552 | 0.089439 | 0.10562 | 0.012299 | 0.047188 | 0.12183 | 0.10138 | 0.16196 | 0.093996 | 0.22395 | 0.19086 | 0.07461 | 121.1949 | 121.1065 | 0.041561 | -0.097212 | 0.10775 | 0.12394 | 0.03061 | 0.065499 | 121.0871 | 121.1643 | -0.066189 | 0.010951
564.6562 | 121.3348 | -0.18768 | 121.1426 | -0.029236 | -0.0451 | 0.015472 | -0.052488 | 0.06831 | 0.048956 | -0.071874 | 121.1766 | 121.0928 | 0.032407 | -0.11552 | 0.089439 | 0.1102 | 0.016878 | 0.056344 | 0.15845 | 0.14258 | 0.20315 | 0.13519 | 0.25599 | 0.23664 | 0.11581 | 121.1949 | 121.1111 | 0.050718 | -0.097212 | 0.10775 | 0.12851 | 0.035189 | 0.074655 | 121.0871 | 121.1597 | -0.057032 | 0.015529
566.4062 | 121.3852 | -0.15564 | 121.1609 | -0.029236 | -0.040521 | 0.010893 | -0.052488 | 0.063733 | 0.044377 | -0.071874 | 121.1903 | 121.1019 | 0.02325 | -0.11094 | 0.094017 | 0.11936 | 0.016878 | 0.060923 | 0.1264 | 0.11512 | 0.16653 | 0.10315 | 0.21937 | 0.20002 | 0.083766 | 121.2086 | 121.1202 | 0.041561 | -0.092633 | 0.11233 | 0.13767 | 0.035189 | 0.079234 | 121.0963 | 121.1734 | -0.070767 | 0.006372
568.1562 | 121.3348 | -0.16937 | 121.1655 | -0.042971 | -0.040521 | 0.010893 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 121.1857 | 121.1111 | 0.018672 | -0.11094 | 0.094017 | 0.11478 | 0.012299 | 0.056344 | 0.1264 | 0.12885 | 0.18027 | 0.11688 | 0.24226 | 0.20917 | 0.097499 | 121.204 | 121.1294 | 0.036983 | -0.092633 | 0.11233 | 0.13309 | 0.03061 | 0.074655 | 121.0917 | 121.1734 | -0.075345 | 0.006373
569.8906 | 121.3394 | -0.1831 | 121.1792 | -0.029236 | -0.0451 | 0.015472 | -0.052488 | 0.06831 | 0.044377 | -0.071874 | 121.2086 | 121.1157 | 0.02325 | -0.11552 | 0.094017 | 0.10105 | 0.016878 | 0.051766 | 0.15387 | 0.138 | 0.19858 | 0.13062 | 0.25141 | 0.22748 | 0.11123 | 121.2269 | 121.134 | 0.041561 | -0.097212 | 0.11233 | 0.11936 | 0.035189 | 0.070077 | 121.1146 | 121.1917 | -0.070767 | 0.006372
571.625 | 121.3394 | -0.17853 | 121.1838 | -0.033814 | -0.040521 | 0.020051 | -0.057066 | 0.077466 | 0.039799 | -0.067295 | 121.204 | 121.1248 | 0.02325 | -0.11094 | 0.089439 | 0.10105 | 0.012299 | 0.051766 | 0.14471 | 0.13801 | 0.19858 | 0.12146 | 0.25599 | 0.21833 | 0.11123 | 121.2224 | 121.1431 | 0.041561 | -0.092633 | 0.10775 | 0.11936 | 0.03061 | 0.070077 | 121.1146 | 121.1917 | -0.066189 | 0.010951
573.2969 | 121.2799 | -0.19684 | 121.2387 | -0.047549 | -0.040521 | 0.010893 | -0.057066 | 0.072888 | 0.048956 | -0.071874 | 121.2178 | 121.1386 | 0.027829 | -0.10637 | 0.089439 | 0.10562 | 0.016878 | 0.056344 | 0.14929 | 0.15632 | 0.20773 | 0.13977 | 0.26973 | 0.24579 | 0.12496 | 121.2361 | 121.1569 | 0.04614 | -0.088054 | 0.10775 | 0.12394 | 0.035189 | 0.074655 | 121.1283 | 121.2009 | -0.06161 | 0.010951
575.0312 | 121.3486 | -0.15564 | 121.2112 | -0.038393 | -0.040521 | 0.015472 | -0.043331 | 0.072888 | 0.048956 | -0.067295 | 121.2269 | 121.1431 | 0.018672 | -0.1201 | 0.089439 | 0.096469 | 0.016878 | 0.056344 | 0.11725 | 0.11512 | 0.17111 | 0.11231 | 0.22853 | 0.2046 | 0.088345 | 121.2453 | 121.1615 | 0.036983 | -0.10179 | 0.10775 | 0.11478 | 0.035189 | 0.074655 | 121.1375 | 121.2101 | -0.070767 | 0.001794
576.7656 | 121.3943 | -0.15564 | 121.1884 | -0.047549 | -0.049678 | 0.010893 | -0.052488 | 0.06831 | 0.044377 | -0.076452 | 121.2315 | 121.1386 | 0.018672 | -0.1201 | 0.089439 | 0.10562 | 0.007721 | 0.04261 | 0.10809 | 0.10596 | 0.16653 | 0.10315 | 0.22395 | 0.20002 | 0.079188 | 121.2498 | 121.1569 | 0.036983 | -0.10179 | 0.10775 | 0.12394 | 0.026032 | 0.060921 | 121.1421 | 121.2238 | -0.070767 | 0.010951
578.4531 | 121.2936 | -0.19226 | 121.2204 | -0.042971 | -0.0451 | 0.020051 | -0.052488 | 0.06831 | 0.039799 | -0.076452 | 121.2407 | 121.1569 | 0.014094 | -0.11552 | 0.094017 | 0.096469 | 0.007721 | 0.047188 | 0.14929 | 0.14716 | 0.21231 | 0.13977 | 0.26057 | 0.23206 | 0.11581 | 121.259 | 121.1752 | 0.032405 | -0.097212 | 0.11233 | 0.11478 | 0.026032 | 0.065499 | 121.1467 | 121.233 | -0.079923 | 0.006373
580.1875 | 121.4218 | -0.15564 | 121.1884 | -0.038393 | -0.0451 | 0.015472 | -0.057066 | 0.06831 | 0.044377 | -0.067295 | 121.2453 | 121.1477 | 0.018672 | -0.11094 | 0.089439 | 0.10105 | 0.012299 | 0.04261 | 0.11725 | 0.11054 | 0.17111 | 0.098574 | 0.22395 | 0.20002 | 0.088345 | 121.2636 | 121.166 | 0.036983 | -0.092633 | 0.10775 | 0.11936 | 0.03061 | 0.060921 | 121.1558 | 121.233 | -0.070767 | 0.006373
581.9219 | 121.4127 | -0.13733 | 121.225 | -0.047549 | -0.049678 | 0.015472 | -0.052488 | 0.072888 | 0.035221 | -0.076452 | 121.2407 | 121.1615 | 0.027829 | -0.10637 | 0.089439 | 0.091891 | 0.012299 | 0.04261 | 0.08978 | 0.087651 | 0.1528 | 0.084841 | 0.21022 | 0.17255 | 0.060877 | 121.259 | 121.1798 | 0.04614 | -0.088054 | 0.10775 | 0.1102 | 0.03061 | 0.060921 | 121.1512 | 121.2284 | -0.06161 | 0.01553
583.6719 | 121.2936 | -0.20142 | 121.2387 | -0.042971 | -0.040521 | 0.006315 | -0.052488 | 0.06831 | 0.053534 | -0.071874 | 121.2453 | 121.1569 | 0.014094 | -0.10179 | 0.080283 | 0.091891 | 0.012299 | 0.047188 | 0.15845 | 0.1609 | 0.20773 | 0.14893 | 0.26973 | 0.25495 | 0.12954 | 121.2636 | 121.1752 | 0.032405 | -0.083475 | 0.098594 | 0.1102 | 0.03061 | 0.065499 | 121.165 | 121.233 | -0.066189 | 0.001795
585.3438 | 121.2662 | -0.19684 | 121.2524 | -0.047549 | -0.049678 | 0.006315 | -0.052488 | 0.072888 | 0.044377 | -0.071874 | 121.2544 | 121.1752 | 0.014094 | -0.10637 | 0.084861 | 0.096469 | 0.012299 | 0.04261 | 0.14929 | 0.14716 | 0.20315 | 0.14435 | 0.26973 | 0.24122 | 0.12496 | 121.2727 | 121.1935 | 0.032405 | -0.088054 | 0.10317 | 0.11478 | 0.03061 | 0.060921 | 121.1696 | 121.2421 | -0.070767 | 0.001795
587.0781 | 121.4401 | -0.15106 | 121.1929 | -0.052128 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.044377 | -0.071874 | 121.259 | 121.166 | 0.009515 | -0.10637 | 0.080283 | 0.091891 | 0.007721 | 0.051766 | 0.098934 | 0.10596 | 0.1528 | 0.093996 | 0.22395 | 0.19544 | 0.079188 | 121.2773 | 121.1843 | 0.027826 | -0.088054 | 0.098594 | 0.1102 | 0.026032 | 0.070077 | 121.1787 | 121.2513 | -0.070768 | 0.001794
588.8281 | 121.2708 | -0.1831 | 121.2479 | -0.056706 | -0.0451 | 0.006315 | -0.057066 | 0.072888 | 0.044377 | -0.067295 | 121.2636 | 121.1706 | 0.018672 | -0.11552 | 0.080283 | 0.091891 | 0.003143 | 0.047188 | 0.1264 | 0.138 | 0.18942 | 0.12604 | 0.25599 | 0.22748 | 0.11581 | 121.2819 | 121.1889 | 0.036983 | -0.097212 | 0.098594 | 0.1102 | 0.021454 | 0.065499 | 121.1833 | 121.2604 | -0.061611 | 0.015529
590.5625 | 121.3074 | -0.19226 | 121.225 | -0.047549 | -0.040521 | 0.015472 | -0.052488 | 0.063733 | 0.039799 | -0.071874 | 121.2681 | 121.1706 | 0.009515 | -0.11552 | 0.080283 | 0.091891 | 0.003143 | 0.047188 | 0.14471 | 0.15174 | 0.20773 | 0.13977 | 0.25599 | 0.23206 | 0.12039 | 121.2865 | 121.1889 | 0.027826 | -0.097212 | 0.098594 | 0.1102 | 0.021454 | 0.065499 | 121.1879 | 121.265 | -0.070768 | 0.006372
592.2344 | 121.3348 | -0.19684 | 121.2708 | -0.052128 | -0.0451 | 0.015472 | -0.057066 | 0.06831 | 0.048956 | -0.071874 | 121.2727 | 121.1798 | 0.014094 | -0.11094 | 0.080283 | 0.096469 | 0.003143 | 0.047188 | 0.14471 | 0.15174 | 0.21231 | 0.13977 | 0.26515 | 0.24579 | 0.12496 | 121.291 | 121.1981 | 0.032405 | -0.092633 | 0.098594 | 0.11478 | 0.021454 | 0.065499 | 121.1924 | 121.2696 | -0.066189 | 0.010951
593.9844 | 121.3852 | -0.16937 | 121.2387 | -0.061284 | -0.054257 | 0.015472 | -0.061645 | 0.063733 | 0.039799 | -0.076452 | 121.2727 | 121.1798 | 0.009515 | -0.11094 | 0.080283 | 0.096469 | 0.007721 | 0.04261 | 0.10809 | 0.11512 | 0.18484 | 0.10773 | 0.23311 | 0.20917 | 0.092921 | 121.291 | 121.1981 | 0.027826 | -0.092633 | 0.098594 | 0.11478 | 0.026032 | 0.060921 | 121.1924 | 121.265 | -0.070768 | 0.001794
595.7188 | 121.4172 | -0.15564 | 121.2433 | -0.047549 | -0.0451 | 0.006315 | -0.061645 | 0.06831 | 0.039799 | -0.076452 | 121.2681 | 121.1889 | 0.014094 | -0.11094 | 0.075705 | 0.087313 | -0.001436 | 0.047188 | 0.10809 | 0.11054 | 0.16195 | 0.093995 | 0.22395 | 0.19544 | 0.079188 | 121.2865 | 121.2072 | 0.032405 | -0.092633 | 0.094016 | 0.10562 | 0.016875 | 0.065499 | 121.1924 | 121.2696 | -0.061611 | 0.01553
597.4531 | 121.3577 | -0.16022 | 121.2662 | -0.061284 | -0.031363 | 0.010893 | -0.061645 | 0.072888 | 0.044377 | -0.071874 | 121.2773 | 121.1798 | 0.004937 | -0.1201 | 0.084861 | 0.096469 | 0.007721 | 0.04261 | 0.098933 | 0.12885 | 0.17111 | 0.098572 | 0.23311 | 0.20459 | 0.088343 | 121.2956 | 121.1981 | 0.023248 | -0.10179 | 0.10317 | 0.11478 | 0.026032 | 0.060921 | 121.1924 | 121.2696 | -0.079924 | -0.002784
599.1562 | 121.3623 | -0.1831 | 121.2799 | -0.052128 | -0.049678 | 0.010893 | -0.052488 | 0.072888 | 0.048956 | -0.071874 | 121.2819 | 121.1981 | 0.009515 | -0.10637 | 0.080283 | 0.091891 | 0.003143 | 0.038032 | 0.13098 | 0.13343 | 0.194 | 0.13062 | 0.25599 | 0.23206 | 0.11123 | 121.3002 | 121.2164 | 0.027826 | -0.088054 | 0.098594 | 0.1102 | 0.021454 | 0.056343 | 121.2016 | 121.2787 | -0.070768 | 0.006372
600.8906 | 121.312 | -0.19226 | 121.2708 | -0.056706 | -0.0451 | 0.020051 | -0.057066 | 0.072888 | 0.044377 | -0.071874 | 121.2865 | 121.1935 | 0.004937 | -0.11094 | 0.084861 | 0.091891 | 0.007721 | 0.04261 | 0.13555 | 0.14716 | 0.21231 | 0.13519 | 0.26515 | 0.23664 | 0.12039 | 121.3048 | 121.2118 | 0.023248 | -0.092633 | 0.10317 | 0.1102 | 0.026032 | 0.060921 | 121.2016 | 121.2787 | -0.079924 | -0.002784
602.625 | 121.4172 | -0.14191 | 121.2479 | -0.061284 | -0.054257 | 0.006315 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.2865 | 121.2027 | 0.014094 | -0.11094 | 0.089439 | 0.091891 | -0.001436 | 0.047188 | 0.080623 | 0.08765 | 0.14822 | 0.084841 | 0.2148 | 0.18171 | 0.065455 | 121.3048 | 121.221 | 0.032405 | -0.092633 | 0.10775 | 0.1102 | 0.016875 | 0.065499 | 121.197 | 121.2879 | -0.075345 | 0.01553
604.3125 | 121.3577 | -0.17395 | 121.2662 | -0.061284 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.048956 | -0.067295 | 121.291 | 121.1981 | 0.004937 | -0.10637 | 0.075705 | 0.096469 | -0.006014 | 0.04261 | 0.11267 | 0.12885 | 0.17569 | 0.11688 | 0.25142 | 0.22291 | 0.10665 | 121.3094 | 121.2164 | 0.023248 | -0.088054 | 0.094016 | 0.11478 | 0.012297 | 0.060921 | 121.2153 | 121.2971 | -0.070768 | 0.010951
606.0469 | 121.344 | -0.19684 | 121.2708 | -0.056706 | -0.0451 | 0.010893 | -0.052488 | 0.072888 | 0.044377 | -0.067295 | 121.2865 | 121.2027 | 0.009515 | -0.11094 | 0.080283 | 0.091891 | 0.007721 | 0.047188 | 0.14013 | 0.15174 | 0.20773 | 0.14435 | 0.26973 | 0.24122 | 0.12954 | 121.3048 | 121.221 | 0.027826 | -0.092633 | 0.098594 | 0.1102 | 0.026032 | 0.065499 | 121.2062 | 121.2787 | -0.070768 | 0.001794
607.7344 | 121.4127 | -0.15564 | 121.2296 | -0.061284 | -0.035942 | 0.010893 | -0.057066 | 0.072888 | 0.044377 | -0.08103 | 121.291 | 121.2027 | 0.014094 | -0.11552 | 0.075705 | 0.091891 | 0.003143 | 0.04261 | 0.094356 | 0.1197 | 0.16653 | 0.098574 | 0.22853 | 0.20002 | 0.07461 | 121.3094 | 121.221 | 0.032405 | -0.097212 | 0.094016 | 0.1102 | 0.021454 | 0.060921 | 121.2153 | 121.2879 | -0.061611 | 0.010951
609.4844 | 121.3806 | -0.18768 | 121.2524 | -0.065863 | -0.049678 | 0.010893 | -0.057066 | 0.072888 | 0.048956 | -0.076452 | 121.3002 | 121.2072 | 0.004937 | -0.10637 | 0.084861 | 0.091891 | 0.007721 | 0.047188 | 0.12182 | 0.138 | 0.19858 | 0.13062 | 0.26057 | 0.23664 | 0.11123 | 121.3185 | 121.2256 | 0.023248 | -0.088054 | 0.10317 | 0.1102 | 0.026032 | 0.065499 | 121.2153 | 121.2925 | -0.079924 | -0.002784
611.1719 | 121.4767 | -0.15564 | 121.2479 | -0.070441 | -0.0451 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.3002 | 121.2072 | 0.004937 | -0.1201 | 0.084861 | 0.091891 | -0.001436 | 0.04261 | 0.085199 | 0.11054 | 0.16195 | 0.10315 | 0.22853 | 0.19544 | 0.079188 | 121.3185 | 121.2256 | 0.023248 | -0.10179 | 0.10317 | 0.1102 | 0.016875 | 0.060921 | 121.2153 | 121.3016 | -0.079924 | 0.006373
612.9219 | 121.4081 | -0.16022 | 121.2433 | -0.07502 | -0.054257 | 0.010893 | -0.052488 | 0.06831 | 0.044377 | -0.071874 | 121.3048 | 121.2072 | 0.004937 | -0.10637 | 0.080283 | 0.087313 | 0.003143 | 0.04261 | 0.085197 | 0.10596 | 0.17111 | 0.10773 | 0.22853 | 0.20459 | 0.088343 | 121.3231 | 121.2256 | 0.023248 | -0.088054 | 0.098594 | 0.10562 | 0.021454 | 0.060921 | 121.2245 | 121.3016 | -0.075346 | 0.001794
614.6562 | 121.4172 | -0.15106 | 121.2753 | -0.065863 | -0.0451 | 0.010893 | -0.057066 | 0.077466 | 0.039799 | -0.071874 | 121.3048 | 121.2164 | 0.009515 | -0.11552 | 0.084861 | 0.091891 | 0.007721 | 0.04261 | 0.085199 | 0.10596 | 0.16196 | 0.093996 | 0.22853 | 0.19086 | 0.079188 | 121.3231 | 121.2347 | 0.027826 | -0.097212 | 0.10317 | 0.1102 | 0.026032 | 0.060921 | 121.2199 | 121.2971 | -0.075346 | 0.001794
616.3281 | 121.3257 | -0.17853 | 121.312 | -0.070441 | -0.054257 | -0.002842 | -0.052488 | 0.063733 | 0.044377 | -0.085608 | 121.3094 | 121.221 | 0.009515 | -0.10637 | 0.080283 | 0.096469 | 0.003143 | 0.047188 | 0.10809 | 0.12427 | 0.17569 | 0.12604 | 0.24226 | 0.2229 | 0.09292 | 121.3277 | 121.2393 | 0.027826 | -0.088054 | 0.098594 | 0.11478 | 0.021454 | 0.065499 | 121.2291 | 121.3062 | -0.070768 | 0.006372
618.0625 | 121.344 | -0.17853 | 121.2616 | -0.061284 | -0.049678 | 0.001736 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.3048 | 121.2164 | 0.009515 | -0.11094 | 0.089439 | 0.087313 | -0.001436 | 0.047188 | 0.11724 | 0.12885 | 0.18026 | 0.12146 | 0.25142 | 0.21833 | 0.10208 | 121.3231 | 121.2347 | 0.027826 | -0.092633 | 0.10775 | 0.10562 | 0.016875 | 0.065499 | 121.2153 | 121.3062 | -0.079924 | 0.010951
619.75 | 121.4676 | -0.15106 | 121.2524 | -0.042971 | -0.0451 | -0.002842 | -0.057066 | 0.072888 | 0.044377 | -0.076452 | 121.3094 | 121.221 | 0.004937 | -0.11094 | 0.075705 | 0.096469 | 0.003143 | 0.04261 | 0.10809 | 0.10596 | 0.14822 | 0.093996 | 0.22395 | 0.19544 | 0.07461 | 121.3277 | 121.2393 | 0.023248 | -0.092633 | 0.094016 | 0.11478 | 0.021454 | 0.060921 | 121.2336 | 121.3062 | -0.070768 | 0.001794
621.4844 | 121.4172 | -0.16479 | 121.2891 | 0.007391 | -0.049678 | 0.001736 | -0.061645 | 0.077466 | 0.035221 | -0.076452 | 121.3139 | 121.2256 | 0.004937 | -0.10179 | 0.080283 | 0.087313 | -0.001436 | 0.038032 | 0.17219 | 0.11512 | 0.16653 | 0.10315 | 0.24226 | 0.20002 | 0.088343 | 121.3322 | 121.2439 | 0.023248 | -0.083475 | 0.098594 | 0.10562 | 0.016875 | 0.056343 | 121.2337 | 121.3154 | -0.075346 | 0.006373
623.2188 | 121.4447 | -0.16479 | 121.2799 | 0.044018 | -0.049678 | 0.001736 | -0.057066 | 0.063733 | 0.039799 | -0.08103 | 121.3139 | 121.2256 | 0.000359 | -0.11094 | 0.075705 | 0.087313 | -0.006014 | 0.04261 | 0.20881 | 0.11512 | 0.16653 | 0.10773 | 0.22853 | 0.20459 | 0.083765 | 121.3322 | 121.2439 | 0.01867 | -0.092633 | 0.094016 | 0.10562 | 0.012297 | 0.060921 | 121.2382 | 121.3199 | -0.075346 | 0.006373
624.9688 | 121.3577 | -0.19226 | 121.3028 | 0.044018 | -0.049678 | -0.002842 | -0.057066 | 0.077466 | 0.044377 | -0.085608 | 121.3185 | 121.2256 | 0.004937 | -0.11094 | 0.080283 | 0.087313 | 0.003143 | 0.04261 | 0.23628 | 0.14258 | 0.18942 | 0.13519 | 0.26973 | 0.23664 | 0.10665 | 121.3368 | 121.2439 | 0.023248 | -0.092633 | 0.098594 | 0.10562 | 0.021454 | 0.060921 | 121.2382 | 121.3154 | -0.075346 | 0.001794
626.6562 | 121.3348 | -0.17853 | 121.3074 | 0.03944 | -0.0451 | 0.001736 | -0.052488 | 0.072888 | 0.044377 | -0.08103 | 121.3185 | 121.2256 | 0.004937 | -0.11094 | 0.080283 | 0.087313 | 0.007721 | 0.038032 | 0.21797 | 0.13343 | 0.18026 | 0.12604 | 0.25142 | 0.2229 | 0.097498 | 121.3368 | 121.2439 | 0.023248 | -0.092633 | 0.098594 | 0.10562 | 0.026032 | 0.056343 | 121.2382 | 121.3108 | -0.075346 | -0.002784
628.3906 | 121.4996 | -0.13733 | 121.2708 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.076452 | 121.3185 | 121.2301 | 0.009515 | -0.10637 | 0.080283 | 0.087313 | -0.001436 | 0.04261 | 0.18135 | 0.096808 | 0.13906 | 0.080263 | 0.2148 | 0.17713 | 0.060877 | 121.3368 | 121.2485 | 0.027826 | -0.088054 | 0.098594 | 0.10562 | 0.016875 | 0.060921 | 121.2382 | 121.3199 | -0.070768 | 0.010951
630.1406 | 121.3943 | -0.17395 | 121.3165 | 0.044018 | -0.049678 | 0.006315 | -0.061645 | 0.072888 | 0.035221 | -0.076452 | 121.3185 | 121.2347 | 0.000359 | -0.11552 | 0.084861 | 0.082735 | -0.001436 | 0.04261 | 0.21797 | 0.12427 | 0.18026 | 0.1123 | 0.24684 | 0.20917 | 0.097498 | 121.3368 | 121.253 | 0.01867 | -0.097212 | 0.10317 | 0.10105 | 0.016875 | 0.060921 | 121.2336 | 121.3199 | -0.084502 | 0.001795
631.8125 | 121.344 | -0.18768 | 121.2982 | 0.044018 | -0.0451 | 0.006315 | -0.057066 | 0.06831 | 0.044377 | -0.071874 | 121.3231 | 121.2439 | 0.004937 | -0.11552 | 0.075705 | 0.082735 | -0.001436 | 0.04261 | 0.2317 | 0.14258 | 0.194 | 0.13062 | 0.25599 | 0.23206 | 0.11581 | 121.3414 | 121.2622 | 0.023248 | -0.097212 | 0.094016 | 0.10105 | 0.016875 | 0.060921 | 121.2474 | 121.3245 | -0.070768 | 0.006373
633.5469 | 121.4584 | -0.15106 | 121.2662 | 0.03944 | -0.0451 | 0.001736 | -0.057066 | 0.063733 | 0.048956 | -0.085608 | 121.3277 | 121.2301 | 0.000359 | -0.10637 | 0.080283 | 0.096469 | 0.003143 | 0.04261 | 0.1905 | 0.10596 | 0.1528 | 0.093996 | 0.2148 | 0.20002 | 0.065454 | 121.346 | 121.2485 | 0.01867 | -0.088054 | 0.098594 | 0.11478 | 0.021454 | 0.060921 | 121.2474 | 121.3245 | -0.079924 | -0.002784
635.2188 | 121.4813 | -0.14648 | 121.2387 | 0.034862 | -0.049678 | -0.002842 | -0.052488 | 0.06831 | 0.039799 | -0.076452 | 121.3231 | 121.2347 | 0.014094 | -0.10637 | 0.084861 | 0.087313 | -0.001436 | 0.04261 | 0.18135 | 0.096806 | 0.14364 | 0.093996 | 0.21479 | 0.18628 | 0.070032 | 121.3414 | 121.253 | 0.032405 | -0.088054 | 0.10317 | 0.10562 | 0.016875 | 0.060921 | 121.2382 | 121.3245 | -0.070767 | 0.01553
636.9531 | 121.4584 | -0.13275 | 121.2799 | 0.03944 | -0.049678 | 0.006315 | -0.061645 | 0.06831 | 0.048956 | -0.08103 | 121.3277 | 121.2439 | 0.004937 | -0.11094 | 0.075705 | 0.082735 | -0.006014 | 0.038032 | 0.17219 | 0.083073 | 0.13907 | 0.071106 | 0.20106 | 0.18171 | 0.051721 | 121.346 | 121.2622 | 0.023248 | -0.092633 | 0.094016 | 0.10105 | 0.012297 | 0.056343 | 121.252 | 121.3337 | -0.070768 | 0.010951
638.6406 | 121.3348 | -0.1831 | 121.3394 | 0.044018 | -0.035942 | 0.006315 | -0.052488 | 0.072888 | 0.035221 | -0.08103 | 121.3368 | 121.2439 | 0.009515 | -0.10179 | 0.080283 | 0.082735 | -0.001436 | 0.033454 | 0.22712 | 0.14716 | 0.18942 | 0.13062 | 0.25599 | 0.21833 | 0.10207 | 121.3551 | 121.2622 | 0.027826 | -0.083475 | 0.098594 | 0.10105 | 0.016875 | 0.051765 | 121.2565 | 121.3383 | -0.070768 | 0.010951
640.375 | 121.3531 | -0.1831 | 121.3165 | 0.044018 | -0.054257 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.3368 | 121.253 | 0.004937 | -0.11094 | 0.080283 | 0.087313 | 0.003143 | 0.04261 | 0.22712 | 0.12885 | 0.18484 | 0.13062 | 0.25599 | 0.2229 | 0.10665 | 121.3551 | 121.2713 | 0.023248 | -0.092633 | 0.098594 | 0.10562 | 0.021454 | 0.060921 | 121.2565 | 121.3337 | -0.075346 | 0.001794
642.1094 | 121.4539 | -0.15564 | 121.2845 | 0.03944 | -0.049678 | -0.002842 | -0.061645 | 0.06831 | 0.044377 | -0.08103 | 121.3322 | 121.2439 | 0.009515 | -0.11094 | 0.071126 | 0.087313 | -0.001436 | 0.038032 | 0.19508 | 0.10596 | 0.1528 | 0.093995 | 0.22395 | 0.20002 | 0.07461 | 121.3506 | 121.2622 | 0.027826 | -0.092633 | 0.089437 | 0.10562 | 0.016875 | 0.056343 | 121.2611 | 121.3337 | -0.061611 | 0.010951
643.8594 | 121.3669 | -0.17853 | 121.3486 | 0.044018 | -0.0451 | 0.010893 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.3368 | 121.2485 | 0.009515 | -0.11094 | 0.075705 | 0.087313 | 0.007721 | 0.038032 | 0.22255 | 0.13343 | 0.18942 | 0.12604 | 0.25599 | 0.2229 | 0.10208 | 121.3551 | 121.2668 | 0.027826 | -0.092633 | 0.094016 | 0.10562 | 0.026032 | 0.056343 | 121.2611 | 121.3291 | -0.06619 | 0.001794
645.5938 | 121.4401 | -0.14648 | 121.3028 | 0.03944 | -0.035942 | -0.002842 | -0.052488 | 0.072888 | 0.039799 | -0.08103 | 121.346 | 121.253 | 0.014094 | -0.11094 | 0.075705 | 0.087313 | 0.003143 | 0.038032 | 0.18592 | 0.11054 | 0.14364 | 0.093996 | 0.21937 | 0.18628 | 0.065454 | 121.3643 | 121.2713 | 0.032405 | -0.092633 | 0.094016 | 0.10562 | 0.021454 | 0.056343 | 121.2703 | 121.3428 | -0.061611 | 0.010951
647.2812 | 121.4447 | -0.13275 | 121.2891 | 0.044018 | -0.0451 | 0.006315 | -0.057066 | 0.06831 | 0.039799 | -0.076452 | 121.3414 | 121.2485 | 0.004937 | -0.10637 | 0.071126 | 0.082735 | -0.001436 | 0.04261 | 0.17677 | 0.087651 | 0.13907 | 0.075685 | 0.20106 | 0.17255 | 0.056299 | 121.3597 | 121.2668 | 0.023248 | -0.088054 | 0.089437 | 0.10105 | 0.016875 | 0.060921 | 121.2703 | 121.3428 | -0.066189 | 0.006373
649.0312 | 121.5042 | -0.13275 | 121.2891 | 0.03944 | -0.049678 | -0.002842 | -0.052488 | 0.06831 | 0.039799 | -0.076452 | 121.346 | 121.2576 | 0.000359 | -0.11094 | 0.075705 | 0.087313 | 0.003143 | 0.033454 | 0.17219 | 0.083073 | 0.12991 | 0.080263 | 0.20106 | 0.17255 | 0.056299 | 121.3643 | 121.2759 | 0.01867 | -0.092633 | 0.094016 | 0.10562 | 0.021454 | 0.051765 | 121.2703 | 121.3428 | -0.075346 | -0.002784
650.7031 | 121.5179 | -0.12817 | 121.2936 | 0.044018 | -0.0451 | 0.006315 | -0.061645 | 0.06831 | 0.039799 | -0.08103 | 121.346 | 121.253 | 0.004937 | -0.11552 | 0.080283 | 0.082735 | 0.003143 | 0.033454 | 0.17219 | 0.083074 | 0.13449 | 0.066529 | 0.19648 | 0.16797 | 0.047144 | 121.3643 | 121.2713 | 0.023248 | -0.097212 | 0.098594 | 0.10105 | 0.021454 | 0.051765 | 121.2657 | 121.3428 | -0.075346 | 0.001794
652.4375 | 121.3806 | -0.16022 | 121.3394 | 0.03944 | -0.0451 | 0.010893 | -0.061645 | 0.072888 | 0.044377 | -0.076452 | 121.3414 | 121.2576 | 0.000359 | -0.10179 | 0.075705 | 0.078157 | 0.003143 | 0.033454 | 0.19966 | 0.11512 | 0.17111 | 0.098572 | 0.23311 | 0.20459 | 0.083765 | 121.3597 | 121.2759 | 0.01867 | -0.083475 | 0.094016 | 0.096468 | 0.021454 | 0.051765 | 121.2657 | 121.3383 | -0.075346 | -0.002784
654.1875 | 121.4951 | -0.15564 | 121.2845 | 0.03944 | -0.049678 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 121.346 | 121.253 | 0.000359 | -0.10637 | 0.080283 | 0.078157 | 0.003143 | 0.038032 | 0.19508 | 0.10596 | 0.16195 | 0.10315 | 0.22853 | 0.19544 | 0.083766 | 121.3643 | 121.2713 | 0.01867 | -0.088054 | 0.098594 | 0.096468 | 0.021454 | 0.056343 | 121.2657 | 121.3428 | -0.079924 | -0.002784
655.8594 | 121.4355 | -0.16479 | 121.312 | 0.034862 | -0.0451 | -0.002842 | -0.066223 | 0.072888 | 0.044377 | -0.08103 | 121.346 | 121.2576 | 0.004937 | -0.11094 | 0.075705 | 0.082735 | -0.006014 | 0.028875 | 0.19966 | 0.11969 | 0.16195 | 0.098572 | 0.23768 | 0.20917 | 0.083765 | 121.3643 | 121.2759 | 0.023248 | -0.092633 | 0.094016 | 0.10105 | 0.012297 | 0.047186 | 121.2703 | 121.352 | -0.070768 | 0.010951
657.5938 | 121.431 | -0.16022 | 121.3165 | 0.044018 | -0.049678 | 0.001736 | -0.057066 | 0.06831 | 0.035221 | -0.076452 | 121.3506 | 121.2576 | -0.004219 | -0.10637 | 0.075705 | 0.082735 | -0.010593 | 0.04261 | 0.20423 | 0.11054 | 0.16195 | 0.10315 | 0.22853 | 0.19544 | 0.083765 | 121.3689 | 121.2759 | 0.014092 | -0.088054 | 0.094016 | 0.10105 | 0.007718 | 0.060921 | 121.2749 | 121.3612 | -0.079924 | 0.006374
659.2812 | 121.3623 | -0.17853 | 121.344 | 0.048597 | -0.040521 | 0.001736 | -0.052488 | 0.06831 | 0.035221 | -0.067295 | 121.3551 | 121.2622 | 0.000359 | -0.11552 | 0.075705 | 0.082735 | -0.001436 | 0.038032 | 0.22712 | 0.13801 | 0.18026 | 0.12604 | 0.24684 | 0.21375 | 0.11123 | 121.3734 | 121.2805 | 0.01867 | -0.097212 | 0.094016 | 0.10105 | 0.016875 | 0.056343 | 121.2794 | 121.3566 | -0.075346 | 0.001795
661.0156 | 121.5271 | -0.13275 | 121.2891 | 0.044018 | -0.0451 | -0.002842 | -0.057066 | 0.082044 | 0.035221 | -0.076452 | 121.346 | 121.2576 | 0.004937 | -0.11094 | 0.084861 | 0.087313 | 0.003143 | 0.038032 | 0.17677 | 0.087651 | 0.12991 | 0.075685 | 0.2148 | 0.16797 | 0.056299 | 121.3643 | 121.2759 | 0.023248 | -0.092633 | 0.10317 | 0.10562 | 0.021454 | 0.056343 | 121.2611 | 121.3428 | -0.079924 | 0.001794
662.75 | 121.4493 | -0.14648 | 121.2891 | 0.044018 | -0.0451 | -0.002842 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 121.346 | 121.2576 | 0.009515 | -0.11552 | 0.075705 | 0.087313 | -0.010593 | 0.04261 | 0.1905 | 0.10138 | 0.14364 | 0.093996 | 0.21937 | 0.18628 | 0.07461 | 121.3643 | 121.2759 | 0.027826 | -0.097212 | 0.094016 | 0.10562 | 0.007718 | 0.060921 | 121.2703 | 121.3566 | -0.06619 | 0.020108
664.4844 | 121.4996 | -0.14191 | 121.2936 | 0.044018 | -0.0451 | 0.001736 | -0.061645 | 0.077466 | 0.039799 | -0.08103 | 121.3597 | 121.2668 | 0.000359 | -0.10637 | 0.075705 | 0.082735 | -0.001436 | 0.04261 | 0.18593 | 0.096807 | 0.14364 | 0.080262 | 0.21937 | 0.18171 | 0.060877 | 121.378 | 121.2851 | 0.01867 | -0.088054 | 0.094016 | 0.10105 | 0.016875 | 0.060921 | 121.284 | 121.3612 | -0.075346 | 0.001795
666.1719 | 121.4127 | -0.18768 | 121.3623 | 0.048597 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.039799 | -0.071874 | 121.3551 | 121.2668 | 0.009515 | -0.10637 | 0.071126 | 0.082735 | -0.001436 | 0.038032 | 0.23628 | 0.14716 | 0.18942 | 0.13062 | 0.26057 | 0.22748 | 0.11581 | 121.3734 | 121.2851 | 0.027826 | -0.088054 | 0.089437 | 0.10105 | 0.016875 | 0.056343 | 121.284 | 121.3566 | -0.061611 | 0.010951
667.9062 | 121.4584 | -0.14191 | 121.3211 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.08103 | 121.3597 | 121.2714 | 0.009515 | -0.10637 | 0.075705 | 0.078157 | 0.003143 | 0.04261 | 0.18593 | 0.10139 | 0.14364 | 0.084841 | 0.21937 | 0.18628 | 0.060877 | 121.378 | 121.2897 | 0.027826 | -0.088054 | 0.094016 | 0.096468 | 0.021454 | 0.060921 | 121.284 | 121.3566 | -0.06619 | 0.006372
669.6406 | 121.4859 | -0.13733 | 121.3211 | 0.044018 | -0.049678 | -0.002842 | -0.052488 | 0.077466 | 0.035221 | -0.076452 | 121.3551 | 121.2668 | 0.004937 | -0.10637 | 0.089439 | 0.082735 | -0.001436 | 0.033454 | 0.18135 | 0.087651 | 0.13449 | 0.084841 | 0.2148 | 0.17255 | 0.060877 | 121.3734 | 121.2851 | 0.023248 | -0.088054 | 0.10775 | 0.10105 | 0.016875 | 0.051765 | 121.2657 | 121.3566 | -0.084502 | 0.006373
671.3125 | 121.4127 | -0.17853 | 121.3303 | 0.03944 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.076452 | 121.3551 | 121.2759 | 0.000359 | -0.11094 | 0.075705 | 0.078157 | -0.001436 | 0.038032 | 0.21797 | 0.13343 | 0.18026 | 0.12146 | 0.25599 | 0.21833 | 0.10208 | 121.3734 | 121.2942 | 0.01867 | -0.092633 | 0.094016 | 0.096468 | 0.016875 | 0.056343 | 121.2794 | 121.3566 | -0.075346 | 0.001795
673.0469 | 121.5179 | -0.13275 | 121.2982 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 121.3597 | 121.2714 | 0.004937 | -0.11094 | 0.075705 | 0.082735 | -0.006014 | 0.033454 | 0.16761 | 0.09223 | 0.13449 | 0.080263 | 0.20564 | 0.17713 | 0.056299 | 121.378 | 121.2897 | 0.023248 | -0.092633 | 0.094016 | 0.10105 | 0.012297 | 0.051765 | 121.284 | 121.3657 | -0.070768 | 0.010951
674.7969 | 121.3806 | -0.18768 | 121.3348 | 0.048597 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.035221 | -0.076452 | 121.3597 | 121.2759 | 0.000359 | -0.11094 | 0.084861 | 0.073579 | 0.003143 | 0.04261 | 0.23628 | 0.14716 | 0.18942 | 0.13519 | 0.26973 | 0.2229 | 0.11123 | 121.378 | 121.2942 | 0.01867 | -0.092633 | 0.10317 | 0.09189 | 0.021454 | 0.060921 | 121.2749 | 121.3566 | -0.084502 | -0.002784
676.5469 | 121.3989 | -0.16937 | 121.3531 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.072888 | 0.035221 | -0.076452 | 121.3689 | 121.2805 | 0.004937 | -0.11552 | 0.080283 | 0.082735 | -0.001436 | 0.033454 | 0.20423 | 0.12427 | 0.17111 | 0.11688 | 0.24226 | 0.20459 | 0.092921 | 121.3872 | 121.2988 | 0.023248 | -0.097212 | 0.098594 | 0.10105 | 0.016875 | 0.051765 | 121.2886 | 121.3703 | -0.075346 | 0.006373
678.2188 | 121.5042 | -0.12817 | 121.2982 | 0.044018 | -0.049678 | -0.002842 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.3643 | 121.2759 | 0.004937 | -0.11094 | 0.071126 | 0.082735 | -0.001436 | 0.038032 | 0.17219 | 0.078496 | 0.12533 | 0.071108 | 0.20106 | 0.16797 | 0.051722 | 121.3826 | 121.2942 | 0.023248 | -0.092633 | 0.089437 | 0.10105 | 0.016875 | 0.056343 | 121.2932 | 121.3657 | -0.066189 | 0.006373
679.9531 | 121.4996 | -0.14648 | 121.2936 | 0.048597 | -0.0451 | 0.001736 | -0.052488 | 0.072888 | 0.035221 | -0.071874 | 121.3735 | 121.2759 | 0.009515 | -0.11552 | 0.071126 | 0.087313 | -0.001436 | 0.033454 | 0.19508 | 0.10138 | 0.14822 | 0.093996 | 0.21937 | 0.18171 | 0.07461 | 121.3918 | 121.2942 | 0.027826 | -0.097212 | 0.089437 | 0.10562 | 0.016875 | 0.051765 | 121.3023 | 121.3749 | -0.061611 | 0.010951
681.6875 | 121.4172 | -0.16022 | 121.3348 | 0.044018 | -0.0451 | 0.006315 | -0.057066 | 0.072888 | 0.035221 | -0.08103 | 121.3735 | 121.2759 | 0.009515 | -0.10637 | 0.066548 | 0.082735 | -0.006014 | 0.038032 | 0.20423 | 0.11512 | 0.16653 | 0.10315 | 0.23311 | 0.19544 | 0.079187 | 121.3918 | 121.2942 | 0.027826 | -0.088054 | 0.084859 | 0.10105 | 0.012297 | 0.056343 | 121.3069 | 121.3795 | -0.057033 | 0.015529
683.4219 | 121.4767 | -0.14191 | 121.3074 | 0.034862 | -0.049678 | 0.001736 | -0.057066 | 0.06831 | 0.039799 | -0.076452 | 121.3689 | 121.2851 | 0.000359 | -0.11094 | 0.071126 | 0.082735 | -0.001436 | 0.038032 | 0.17677 | 0.092229 | 0.14364 | 0.084841 | 0.21022 | 0.18171 | 0.065455 | 121.3872 | 121.3034 | 0.01867 | -0.092633 | 0.089437 | 0.10105 | 0.016875 | 0.056343 | 121.2977 | 121.3703 | -0.070767 | 0.001795
685.1094 | 121.3898 | -0.16937 | 121.376 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.3689 | 121.2805 | 0.004937 | -0.11552 | 0.080283 | 0.078157 | -0.015171 | 0.038032 | 0.21339 | 0.12885 | 0.17111 | 0.11688 | 0.24226 | 0.20917 | 0.092921 | 121.3872 | 121.2988 | 0.023248 | -0.097212 | 0.098594 | 0.096468 | 0.00314 | 0.056343 | 121.2886 | 121.384 | -0.075346 | 0.020108
686.8438 | 121.4218 | -0.17853 | 121.3486 | 0.048597 | -0.040521 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.08103 | 121.3689 | 121.2897 | 0.004937 | -0.10179 | 0.084861 | 0.082735 | 0.003143 | 0.047188 | 0.22712 | 0.13801 | 0.17569 | 0.12604 | 0.25142 | 0.2229 | 0.097498 | 121.3872 | 121.308 | 0.023248 | -0.083475 | 0.10317 | 0.10105 | 0.021454 | 0.065499 | 121.284 | 121.3657 | -0.079924 | 0.001794
688.5781 | 121.4172 | -0.15564 | 121.3531 | 0.044018 | -0.049678 | 0.001736 | -0.052488 | 0.063733 | 0.039799 | -0.076452 | 121.378 | 121.2851 | 0.000359 | -0.10637 | 0.075705 | 0.073579 | -0.006014 | 0.033454 | 0.19966 | 0.10596 | 0.15738 | 0.10315 | 0.21937 | 0.19544 | 0.079188 | 121.3963 | 121.3034 | 0.01867 | -0.088054 | 0.094016 | 0.09189 | 0.012297 | 0.051765 | 121.3023 | 121.384 | -0.075346 | 0.006373
690.2656 | 121.3943 | -0.1831 | 121.3623 | 0.048597 | -0.040521 | -0.002842 | -0.057066 | 0.077466 | 0.044377 | -0.071874 | 121.3735 | 121.2851 | 0.000359 | -0.10179 | 0.075705 | 0.082735 | -0.006014 | 0.038032 | 0.2317 | 0.14258 | 0.18026 | 0.12604 | 0.26057 | 0.22748 | 0.11123 | 121.3918 | 121.3034 | 0.01867 | -0.083475 | 0.094016 | 0.10105 | 0.012297 | 0.056343 | 121.2977 | 121.3795 | -0.075346 | 0.006373
692.0156 | 121.4905 | -0.13275 | 121.3303 | 0.044018 | -0.035942 | 0.001736 | -0.057066 | 0.072888 | 0.035221 | -0.076452 | 121.3689 | 121.2897 | 0.004937 | -0.10637 | 0.066548 | 0.078157 | -0.010593 | 0.033454 | 0.17677 | 0.096809 | 0.13449 | 0.075685 | 0.20564 | 0.16797 | 0.056299 | 121.3872 | 121.308 | 0.023248 | -0.088054 | 0.084859 | 0.096468 | 0.007718 | 0.051765 | 121.3023 | 121.3795 | -0.061611 | 0.01553
693.6875 | 121.4722 | -0.13275 | 121.3211 | 0.048597 | -0.049678 | 0.001736 | -0.052488 | 0.06831 | 0.035221 | -0.085608 | 121.378 | 121.2942 | 0.000359 | -0.11094 | 0.080283 | 0.073579 | -0.006014 | 0.04261 | 0.18135 | 0.083073 | 0.13449 | 0.080263 | 0.20106 | 0.16797 | 0.047143 | 121.3963 | 121.3126 | 0.01867 | -0.092633 | 0.098594 | 0.09189 | 0.012297 | 0.060921 | 121.2977 | 121.384 | -0.079924 | 0.006373
695.4219 | 121.3989 | -0.17853 | 121.3486 | 0.030283 | -0.040521 | 0.001736 | -0.057066 | 0.06831 | 0.035221 | -0.08103 | 121.3826 | 121.2942 | 0.000359 | -0.11094 | 0.066548 | 0.078157 | -0.010593 | 0.04261 | 0.20881 | 0.13801 | 0.18026 | 0.12146 | 0.24684 | 0.21375 | 0.097498 | 121.4009 | 121.3126 | 0.01867 | -0.092633 | 0.084859 | 0.096468 | 0.007718 | 0.060921 | 121.3161 | 121.3932 | -0.066189 | 0.010952
697.1719 | 121.3852 | -0.20142 | 121.3531 | 0.044018 | -0.040521 | 0.001736 | -0.061645 | 0.072888 | 0.039799 | -0.071874 | 121.3918 | 121.2942 | 0.000359 | -0.10637 | 0.071126 | 0.078157 | -0.001436 | 0.038032 | 0.24543 | 0.1609 | 0.20315 | 0.13977 | 0.2743 | 0.24122 | 0.12954 | 121.4101 | 121.3126 | 0.01867 | -0.088054 | 0.089437 | 0.096468 | 0.016875 | 0.056343 | 121.3206 | 121.3932 | -0.070767 | 0.001795
698.8594 | 121.3806 | -0.17853 | 121.3394 | 0.044018 | -0.0451 | -0.007421 | -0.057066 | 0.072888 | 0.039799 | -0.071874 | 121.3826 | 121.2942 | -0.004219 | -0.10637 | 0.071126 | 0.078157 | -0.006014 | 0.04261 | 0.22255 | 0.13343 | 0.17111 | 0.12146 | 0.25142 | 0.21833 | 0.10665 | 121.4009 | 121.3126 | 0.014092 | -0.088054 | 0.089437 | 0.096468 | 0.012297 | 0.060921 | 121.3115 | 121.3886 | -0.075345 | 0.001795
700.6094 | 121.5271 | -0.13275 | 121.3394 | 0.03944 | -0.049678 | 0.006315 | -0.057066 | 0.072888 | 0.044377 | -0.08103 | 121.3826 | 121.2988 | -0.004219 | -0.10637 | 0.071126 | 0.073579 | -0.010593 | 0.033454 | 0.17219 | 0.083073 | 0.13907 | 0.075685 | 0.20564 | 0.17713 | 0.051721 | 121.4009 | 121.3171 | 0.014092 | -0.088054 | 0.089437 | 0.09189 | 0.007718 | 0.051765 | 121.3115 | 121.3932 | -0.075345 | 0.006374
702.3438 | 121.4401 | -0.16022 | 121.3623 | 0.044018 | -0.040521 | 0.001736 | -0.061645 | 0.077466 | 0.039799 | -0.076452 | 121.3918 | 121.2988 | 0.004937 | -0.11552 | 0.075705 | 0.069001 | -0.006014 | 0.033454 | 0.20423 | 0.1197 | 0.16195 | 0.098572 | 0.23768 | 0.20002 | 0.083765 | 121.4101 | 121.3171 | 0.023248 | -0.097212 | 0.094016 | 0.087312 | 0.012297 | 0.051765 | 121.3161 | 121.3978 | -0.070768 | 0.010951
704.0312 | 121.4767 | -0.1236 | 121.3623 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.063733 | 0.044377 | -0.085608 | 121.3872 | 121.2988 | -0.004219 | -0.10637 | 0.071126 | 0.073579 | -0.006014 | 0.033454 | 0.16761 | 0.078496 | 0.12533 | 0.06653 | 0.18733 | 0.16797 | 0.037988 | 121.4055 | 121.3171 | 0.014092 | -0.088054 | 0.089437 | 0.09189 | 0.012297 | 0.051765 | 121.3161 | 121.3932 | -0.075345 | 0.001795
705.7188 | 121.4264 | -0.16022 | 121.3669 | 0.044018 | -0.0451 | -0.002842 | -0.052488 | 0.06831 | 0.044377 | -0.08103 | 121.3963 | 121.2988 | 0.004937 | -0.11552 | 0.066548 | 0.073579 | -0.006014 | 0.028875 | 0.20423 | 0.11512 | 0.15737 | 0.10773 | 0.22853 | 0.20459 | 0.079187 | 121.4147 | 121.3171 | 0.023248 | -0.097212 | 0.084859 | 0.09189 | 0.012297 | 0.047186 | 121.3298 | 121.4024 | -0.061611 | 0.010951
707.4531 | 121.5271 | -0.1236 | 121.3165 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.08103 | 121.3918 | 121.2988 | 0.004937 | -0.10637 | 0.071126 | 0.082735 | -0.015171 | 0.033454 | 0.16761 | 0.083075 | 0.12533 | 0.06653 | 0.20106 | 0.1634 | 0.042566 | 121.4101 | 121.3171 | 0.023248 | -0.088054 | 0.089437 | 0.10105 | 0.00314 | 0.051765 | 121.3206 | 121.4069 | -0.066189 | 0.020108
709.2031 | 121.5271 | -0.11902 | 121.3348 | 0.044018 | -0.0451 | -0.002842 | -0.057066 | 0.06831 | 0.039799 | -0.076452 | 121.3826 | 121.2988 | -0.004219 | -0.10637 | 0.066548 | 0.073579 | -0.010593 | 0.033454 | 0.16304 | 0.073919 | 0.11618 | 0.061953 | 0.18733 | 0.15882 | 0.042567 | 121.4009 | 121.3171 | 0.014092 | -0.088054 | 0.084859 | 0.09189 | 0.007718 | 0.051765 | 121.3161 | 121.3932 | -0.070767 | 0.006374
710.875 | 121.4355 | -0.16479 | 121.3623 | 0.044018 | -0.0451 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 121.3963 | 121.3126 | 0.004937 | -0.11094 | 0.071126 | 0.073579 | -0.010593 | 0.038032 | 0.20881 | 0.11969 | 0.17111 | 0.11689 | 0.24226 | 0.20459 | 0.0975 | 121.4147 | 121.3309 | 0.023248 | -0.092633 | 0.089437 | 0.09189 | 0.007718 | 0.056343 | 121.3252 | 121.4069 | -0.066189 | 0.01553
712.6094 | 121.5408 | -0.13275 | 121.344 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 121.3963 | 121.308 | 0.000359 | -0.10637 | 0.066548 | 0.078157 | -0.001436 | 0.024297 | 0.17677 | 0.087651 | 0.13907 | 0.080263 | 0.20564 | 0.17713 | 0.056299 | 121.4147 | 121.3263 | 0.01867 | -0.088054 | 0.084859 | 0.096468 | 0.016875 | 0.042608 | 121.3298 | 121.3978 | -0.066189 | 0.001795
714.2969 | 121.4767 | -0.1236 | 121.3165 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 121.4055 | 121.2942 | -0.004219 | -0.11094 | 0.071126 | 0.069001 | -0.006014 | 0.038032 | 0.16304 | 0.083075 | 0.12075 | 0.071108 | 0.20106 | 0.1634 | 0.047144 | 121.4238 | 121.3126 | 0.014092 | -0.092633 | 0.089437 | 0.087312 | 0.012297 | 0.056343 | 121.3344 | 121.4115 | -0.075345 | 0.001795
716.0469 | 121.4035 | -0.17853 | 121.3669 | 0.044018 | -0.035942 | 0.010893 | -0.047909 | 0.06831 | 0.035221 | -0.08103 | 121.3918 | 121.308 | 0.004937 | -0.10637 | 0.075705 | 0.069001 | 0.003143 | 0.024297 | 0.22255 | 0.14259 | 0.18942 | 0.13062 | 0.24684 | 0.21375 | 0.097498 | 121.4101 | 121.3263 | 0.023248 | -0.088054 | 0.094016 | 0.087312 | 0.021454 | 0.042608 | 121.3161 | 121.3886 | -0.070768 | 0.001794
717.7188 | 121.4447 | -0.15564 | 121.3577 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 121.3918 | 121.3126 | 0.000359 | -0.1201 | 0.066548 | 0.073579 | -0.006014 | 0.033454 | 0.19966 | 0.11512 | 0.15738 | 0.10315 | 0.22853 | 0.19544 | 0.083766 | 121.4101 | 121.3309 | 0.01867 | -0.10179 | 0.084859 | 0.09189 | 0.012297 | 0.051765 | 121.3252 | 121.3978 | -0.066189 | 0.006373
719.4531 | 121.4859 | -0.14648 | 121.3165 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.4055 | 121.3126 | -0.004219 | -0.10637 | 0.066548 | 0.073579 | -0.006014 | 0.028875 | 0.1905 | 0.10596 | 0.14822 | 0.093996 | 0.21937 | 0.18628 | 0.070032 | 121.4238 | 121.3309 | 0.014092 | -0.088054 | 0.084859 | 0.09189 | 0.012297 | 0.047186 | 121.339 | 121.4115 | -0.070767 | 0.001795
721.2031 | 121.4081 | -0.16937 | 121.3715 | 0.048597 | -0.035942 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 121.4055 | 121.308 | 0.004937 | -0.11094 | 0.066548 | 0.073579 | -0.010593 | 0.033454 | 0.21797 | 0.13343 | 0.16653 | 0.12146 | 0.24684 | 0.21375 | 0.092921 | 121.4238 | 121.3263 | 0.023248 | -0.092633 | 0.084859 | 0.09189 | 0.007718 | 0.051765 | 121.339 | 121.4161 | -0.061611 | 0.01553
722.9375 | 121.5363 | -0.10986 | 121.3715 | 0.044018 | -0.040521 | -0.002842 | -0.052488 | 0.06831 | 0.039799 | -0.076452 | 121.4055 | 121.308 | 0.000359 | -0.10637 | 0.06197 | 0.069001 | -0.015171 | 0.033454 | 0.15388 | 0.069342 | 0.10702 | 0.057375 | 0.17817 | 0.14966 | 0.033411 | 121.4238 | 121.3263 | 0.01867 | -0.088054 | 0.080281 | 0.087312 | 0.00314 | 0.051765 | 121.3435 | 121.4207 | -0.061611 | 0.01553
724.6719 | 121.5042 | -0.1236 | 121.3669 | 0.044018 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.048956 | -0.08103 | 121.4055 | 121.3126 | 0.000359 | -0.10637 | 0.066548 | 0.073579 | -0.010593 | 0.028875 | 0.16761 | 0.087654 | 0.12533 | 0.071108 | 0.20106 | 0.17255 | 0.042566 | 121.4238 | 121.3309 | 0.01867 | -0.088054 | 0.084859 | 0.09189 | 0.007718 | 0.047186 | 121.339 | 121.4161 | -0.066189 | 0.010952
726.4219 | 121.5225 | -0.13733 | 121.3577 | 0.034862 | -0.049678 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.4055 | 121.3126 | 0.004937 | -0.11094 | 0.071126 | 0.073579 | -0.006014 | 0.028875 | 0.17219 | 0.087651 | 0.13906 | 0.084841 | 0.2148 | 0.18171 | 0.065455 | 121.4238 | 121.3309 | 0.023248 | -0.092633 | 0.089437 | 0.09189 | 0.012297 | 0.047186 | 121.3344 | 121.4115 | -0.066189 | 0.010951
728.0938 | 121.4584 | -0.14648 | 121.3989 | 0.03944 | -0.035942 | -0.002842 | -0.052488 | 0.06831 | 0.044377 | -0.067295 | 121.4147 | 121.3126 | 0.004937 | -0.11094 | 0.071126 | 0.073579 | -0.001436 | 0.033454 | 0.18592 | 0.11054 | 0.14364 | 0.093996 | 0.21479 | 0.19086 | 0.079189 | 121.433 | 121.3309 | 0.023248 | -0.092633 | 0.089437 | 0.09189 | 0.016875 | 0.051765 | 121.3435 | 121.4161 | -0.066189 | 0.006373
729.8438 | 121.5317 | -0.11902 | 121.3165 | 0.03944 | -0.0451 | 0.001736 | -0.052488 | 0.06831 | 0.035221 | -0.076452 | 121.4147 | 121.3171 | 0.000359 | -0.10179 | 0.066548 | 0.069001 | -0.001436 | 0.028875 | 0.15846 | 0.073919 | 0.12076 | 0.066531 | 0.18733 | 0.15424 | 0.042567 | 121.433 | 121.3354 | 0.01867 | -0.083475 | 0.084859 | 0.087312 | 0.016875 | 0.047186 | 121.3481 | 121.4161 | -0.066189 | 0.001795
731.5938 | 121.3989 | -0.1831 | 121.3898 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.071874 | 121.4055 | 121.3217 | -0.004219 | -0.11094 | 0.066548 | 0.064423 | -0.006014 | 0.033454 | 0.22712 | 0.138 | 0.18484 | 0.12604 | 0.26057 | 0.22748 | 0.11123 | 121.4238 | 121.34 | 0.014092 | -0.092633 | 0.084859 | 0.082734 | 0.012297 | 0.051765 | 121.339 | 121.4115 | -0.070767 | 0.001795
733.2656 | 121.4035 | -0.17853 | 121.4081 | 0.044018 | -0.0451 | 0.001736 | -0.061645 | 0.077466 | 0.044377 | -0.071874 | 121.4101 | 121.3171 | -0.004219 | -0.10179 | 0.071126 | 0.073579 | 0.003143 | 0.033454 | 0.22255 | 0.13343 | 0.18026 | 0.11688 | 0.25599 | 0.2229 | 0.10665 | 121.4284 | 121.3354 | 0.014092 | -0.083475 | 0.089437 | 0.09189 | 0.021454 | 0.051765 | 121.339 | 121.4069 | -0.075345 | -0.007362
735 | 121.4584 | -0.16937 | 121.3898 | 0.044018 | -0.040521 | -0.002842 | -0.061645 | 0.072888 | 0.039799 | -0.08103 | 121.4147 | 121.3263 | -0.008798 | -0.11094 | 0.066548 | 0.073579 | -0.010593 | 0.038032 | 0.21339 | 0.12885 | 0.16653 | 0.10773 | 0.24226 | 0.20917 | 0.088343 | 121.433 | 121.3446 | 0.009513 | -0.092633 | 0.084859 | 0.09189 | 0.007718 | 0.056343 | 121.3481 | 121.4253 | -0.075346 | 0.001795
736.6719 | 121.5042 | -0.1236 | 121.3531 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.063733 | 0.039799 | -0.08103 | 121.4238 | 121.3171 | 0.000359 | -0.11094 | 0.066548 | 0.069001 | -0.010593 | 0.028875 | 0.16304 | 0.083075 | 0.12075 | 0.071108 | 0.18733 | 0.1634 | 0.042566 | 121.4421 | 121.3354 | 0.01867 | -0.092633 | 0.084859 | 0.087312 | 0.007718 | 0.047186 | 121.3573 | 121.4344 | -0.066189 | 0.010952
738.4062 | 121.5454 | -0.10986 | 121.3348 | 0.044018 | -0.049678 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.071874 | 121.4147 | 121.3171 | 0.009515 | -0.11094 | 0.071126 | 0.073579 | -0.001436 | 0.038032 | 0.15388 | 0.060185 | 0.11618 | 0.061954 | 0.18275 | 0.15424 | 0.037989 | 121.433 | 121.3354 | 0.027826 | -0.092633 | 0.089437 | 0.09189 | 0.016875 | 0.056343 | 121.3435 | 121.4161 | -0.061611 | 0.010951
740.1562 | 121.4951 | -0.13733 | 121.3486 | 0.044018 | -0.0451 | -0.002842 | -0.061645 | 0.072888 | 0.044377 | -0.076452 | 121.4192 | 121.3171 | 0.000359 | -0.11094 | 0.066548 | 0.073579 | -0.001436 | 0.028875 | 0.18135 | 0.092229 | 0.13449 | 0.075684 | 0.21022 | 0.18171 | 0.060877 | 121.4375 | 121.3354 | 0.01867 | -0.092633 | 0.084859 | 0.09189 | 0.016875 | 0.047186 | 121.3527 | 121.4207 | -0.066189 | 0.001795
741.8906 | 121.4172 | -0.16479 | 121.4127 | 0.048597 | -0.035942 | 0.006315 | -0.057066 | 0.063733 | 0.039799 | -0.076452 | 121.4147 | 121.3217 | 0.004937 | -0.11094 | 0.06197 | 0.069001 | -0.006014 | 0.033454 | 0.21339 | 0.12885 | 0.17111 | 0.10773 | 0.22853 | 0.20459 | 0.088343 | 121.433 | 121.34 | 0.023248 | -0.092633 | 0.080281 | 0.087312 | 0.012297 | 0.051765 | 121.3527 | 121.4207 | -0.057033 | 0.010951
743.5625 | 121.4172 | -0.16022 | 121.3898 | 0.048597 | -0.049678 | 0.006315 | -0.057066 | 0.077466 | 0.030642 | -0.071874 | 121.4147 | 121.3171 | 0.004937 | -0.10637 | 0.071126 | 0.069001 | -0.006014 | 0.033454 | 0.20881 | 0.11054 | 0.16653 | 0.10315 | 0.23768 | 0.19086 | 0.088343 | 121.433 | 121.3354 | 0.023248 | -0.088054 | 0.089437 | 0.087312 | 0.012297 | 0.051765 | 121.3435 | 121.4207 | -0.066189 | 0.010951
745.3125 | 121.4859 | -0.13275 | 121.3623 | 0.044018 | -0.040521 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.071874 | 121.4147 | 121.3309 | 0.004937 | -0.10637 | 0.066548 | 0.069001 | -0.010593 | 0.028875 | 0.17677 | 0.09223 | 0.12991 | 0.080263 | 0.20564 | 0.17713 | 0.060877 | 121.433 | 121.3492 | 0.023248 | -0.088054 | 0.084859 | 0.087312 | 0.007718 | 0.047186 | 121.3481 | 121.4253 | -0.061611 | 0.01553
747.0625 | 121.4081 | -0.15106 | 121.376 | 0.03944 | -0.0451 | 0.001736 | -0.047909 | 0.072888 | 0.044377 | -0.076452 | 121.4147 | 121.3309 | -0.004219 | -0.11094 | 0.066548 | 0.073579 | -0.006014 | 0.033454 | 0.1905 | 0.10596 | 0.1528 | 0.10315 | 0.22395 | 0.19544 | 0.07461 | 121.433 | 121.3492 | 0.014092 | -0.092633 | 0.084859 | 0.09189 | 0.012297 | 0.051765 | 121.3481 | 121.4207 | -0.070767 | 0.001795
748.8125 | 121.4539 | -0.16937 | 121.3623 | 0.044018 | -0.035942 | 0.001736 | -0.057066 | 0.06831 | 0.044377 | -0.071874 | 121.4192 | 121.3263 | 0.000359 | -0.10179 | 0.071126 | 0.069001 | -0.001436 | 0.033454 | 0.21339 | 0.13343 | 0.17111 | 0.11231 | 0.23768 | 0.21375 | 0.097499 | 121.4375 | 121.3446 | 0.01867 | -0.083475 | 0.089437 | 0.087312 | 0.016875 | 0.051765 | 121.3481 | 121.4207 | -0.070767 | 0.001795
750.5469 | 121.4584 | -0.16479 | 121.3989 | 0.048597 | -0.040521 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.071874 | 121.4284 | 121.3217 | 0.000359 | -0.11094 | 0.066548 | 0.064423 | -0.010593 | 0.028875 | 0.21339 | 0.12427 | 0.16653 | 0.11689 | 0.24226 | 0.20917 | 0.092921 | 121.4467 | 121.34 | 0.01867 | -0.092633 | 0.084859 | 0.082734 | 0.007718 | 0.047186 | 121.3618 | 121.439 | -0.066189 | 0.010952
752.3594 | 121.3852 | -0.17395 | 121.4172 | 0.034862 | -0.0451 | -0.007421 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 121.4238 | 121.3309 | 0.000359 | -0.10637 | 0.06197 | 0.073579 | -0.010593 | 0.033454 | 0.20881 | 0.12885 | 0.16653 | 0.12146 | 0.25142 | 0.21375 | 0.097498 | 121.4421 | 121.3492 | 0.01867 | -0.088054 | 0.080281 | 0.09189 | 0.007718 | 0.051765 | 121.3618 | 121.4344 | -0.061611 | 0.010952
754.1094 | 121.4218 | -0.16022 | 121.3989 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 121.4192 | 121.3217 | -0.004219 | -0.10637 | 0.066548 | 0.078157 | -0.010593 | 0.033454 | 0.20423 | 0.1197 | 0.16195 | 0.10773 | 0.23311 | 0.20459 | 0.083765 | 121.4375 | 121.34 | 0.014092 | -0.088054 | 0.084859 | 0.096468 | 0.007718 | 0.051765 | 121.3527 | 121.4298 | -0.070767 | 0.006374
755.8281 | 121.5317 | -0.10071 | 121.344 | 0.03944 | -0.035942 | -0.007421 | -0.057066 | 0.072888 | 0.035221 | -0.076452 | 121.4238 | 121.3355 | 0.000359 | -0.11094 | 0.066548 | 0.069001 | -0.010593 | 0.028875 | 0.14015 | 0.064766 | 0.093287 | 0.043642 | 0.1736 | 0.13593 | 0.024256 | 121.4421 | 121.3538 | 0.01867 | -0.092633 | 0.084859 | 0.087312 | 0.007718 | 0.047186 | 121.3573 | 121.4344 | -0.066189 | 0.010952
757.5312 | 121.4401 | -0.15106 | 121.4035 | 0.048597 | -0.0451 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.08103 | 121.4284 | 121.3355 | 0.000359 | -0.10637 | 0.06197 | 0.069001 | -0.010593 | 0.028875 | 0.19966 | 0.10596 | 0.14822 | 0.10315 | 0.22853 | 0.19086 | 0.070032 | 121.4467 | 121.3538 | 0.01867 | -0.088054 | 0.080281 | 0.087312 | 0.007718 | 0.047186 | 121.3664 | 121.439 | -0.061611 | 0.010952
759.2344 | 121.5637 | -0.11902 | 121.3486 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.4238 | 121.3355 | -0.008798 | -0.1201 | 0.057392 | 0.069001 | -0.010593 | 0.033454 | 0.16304 | 0.078498 | 0.12076 | 0.066531 | 0.19191 | 0.15882 | 0.042567 | 121.4421 | 121.3538 | 0.009513 | -0.10179 | 0.075703 | 0.087312 | 0.007718 | 0.051765 | 121.3664 | 121.4344 | -0.06619 | 0.001795
760.9688 | 121.5454 | -0.13733 | 121.3348 | 0.03944 | -0.0451 | 0.006315 | -0.047909 | 0.06831 | 0.035221 | -0.08103 | 121.4284 | 121.3355 | 0.000359 | -0.11094 | 0.06197 | 0.069001 | -0.015171 | 0.028875 | 0.17677 | 0.092229 | 0.14364 | 0.08942 | 0.20564 | 0.17255 | 0.056299 | 121.4467 | 121.3538 | 0.01867 | -0.092633 | 0.080281 | 0.087312 | 0.00314 | 0.047186 | 121.3664 | 121.4436 | -0.061611 | 0.01553
762.6562 | 121.5546 | -0.10986 | 121.3715 | 0.03944 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.048956 | -0.076452 | 121.4284 | 121.34 | -0.004219 | -0.10637 | 0.071126 | 0.073579 | -0.010593 | 0.028875 | 0.1493 | 0.069342 | 0.1116 | 0.057375 | 0.18275 | 0.15882 | 0.033411 | 121.4467 | 121.3583 | 0.014092 | -0.088054 | 0.089437 | 0.09189 | 0.007718 | 0.047186 | 121.3573 | 121.439 | -0.075345 | 0.006374
764.3438 | 121.4996 | -0.14648 | 121.3669 | 0.030283 | -0.035942 | 0.001736 | -0.057066 | 0.072888 | 0.035221 | -0.085608 | 121.4376 | 121.34 | -0.004219 | -0.11094 | 0.066548 | 0.069001 | -0.010593 | 0.024297 | 0.17677 | 0.11054 | 0.14822 | 0.089418 | 0.21937 | 0.18171 | 0.060876 | 121.4559 | 121.3583 | 0.014092 | -0.092633 | 0.084859 | 0.087312 | 0.007718 | 0.042608 | 121.371 | 121.4481 | -0.070767 | 0.006374
766.0625 | 121.4264 | -0.16937 | 121.3898 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.072888 | 0.048956 | -0.076452 | 121.433 | 121.3446 | -0.008798 | -0.11094 | 0.066548 | 0.078157 | -0.010593 | 0.028875 | 0.21339 | 0.12885 | 0.17569 | 0.11231 | 0.24226 | 0.21833 | 0.092921 | 121.4513 | 121.3629 | 0.009513 | -0.092633 | 0.084859 | 0.096468 | 0.007718 | 0.047186 | 121.3664 | 121.4436 | -0.075346 | 0.001795
767.7344 | 121.5637 | -0.1236 | 121.3623 | 0.034862 | -0.0451 | -0.007421 | -0.057066 | 0.082044 | 0.035221 | -0.08103 | 121.433 | 121.34 | 0.000359 | -0.11552 | 0.06197 | 0.069001 | -0.006014 | 0.028875 | 0.15846 | 0.078496 | 0.11618 | 0.06653 | 0.20564 | 0.15882 | 0.042566 | 121.4513 | 121.3583 | 0.01867 | -0.097212 | 0.080281 | 0.087312 | 0.012297 | 0.047186 | 121.371 | 121.439 | -0.061611 | 0.006373
769.5 | 121.5271 | -0.13275 | 121.3852 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 121.4376 | 121.3492 | -0.004219 | -0.11094 | 0.06197 | 0.069001 | -0.010593 | 0.033454 | 0.16761 | 0.09223 | 0.13449 | 0.080263 | 0.2148 | 0.17713 | 0.056299 | 121.4559 | 121.3675 | 0.014092 | -0.092633 | 0.080281 | 0.087312 | 0.007718 | 0.051765 | 121.3756 | 121.4481 | -0.066189 | 0.006374
771.2031 | 121.55 | -0.13733 | 121.344 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.072888 | 0.035221 | -0.076452 | 121.433 | 121.34 | 0.000359 | -0.11094 | 0.066548 | 0.073579 | -0.006014 | 0.028875 | 0.17219 | 0.092229 | 0.13906 | 0.084841 | 0.21022 | 0.17255 | 0.060877 | 121.4513 | 121.3583 | 0.01867 | -0.092633 | 0.084859 | 0.09189 | 0.012297 | 0.047186 | 121.3664 | 121.439 | -0.066189 | 0.006373
772.9062 | 121.4676 | -0.14648 | 121.4081 | 0.03944 | -0.049678 | 0.001736 | -0.057066 | 0.082044 | 0.048956 | -0.071874 | 121.4376 | 121.3446 | -0.004219 | -0.11552 | 0.066548 | 0.069001 | -0.015171 | 0.028875 | 0.18592 | 0.096806 | 0.14822 | 0.089418 | 0.22853 | 0.19544 | 0.07461 | 121.4559 | 121.3629 | 0.014092 | -0.097212 | 0.084859 | 0.087312 | 0.00314 | 0.047186 | 121.371 | 121.4527 | -0.070767 | 0.010952
774.5938 | 121.3989 | -0.16022 | 121.3989 | 0.044018 | -0.0451 | -0.007421 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.433 | 121.3446 | 0.000359 | -0.10637 | 0.066548 | 0.064423 | -0.010593 | 0.033454 | 0.20423 | 0.11512 | 0.1528 | 0.10773 | 0.23768 | 0.20459 | 0.088343 | 121.4513 | 121.3629 | 0.01867 | -0.088054 | 0.084859 | 0.082734 | 0.007718 | 0.051765 | 121.3664 | 121.4436 | -0.066189 | 0.010952
776.2969 | 121.5088 | -0.14191 | 121.3715 | 0.044018 | -0.049678 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.4421 | 121.3492 | -0.004219 | -0.10637 | 0.06197 | 0.073579 | -0.010593 | 0.028875 | 0.18593 | 0.092229 | 0.14364 | 0.089419 | 0.2148 | 0.18171 | 0.065455 | 121.4604 | 121.3675 | 0.014092 | -0.088054 | 0.080281 | 0.09189 | 0.007718 | 0.047186 | 121.3802 | 121.4527 | -0.066189 | 0.006374
778 | 121.4722 | -0.14191 | 121.3989 | 0.048597 | -0.040521 | 0.010893 | -0.061645 | 0.072888 | 0.044377 | -0.076452 | 121.4376 | 121.34 | -0.004219 | -0.11094 | 0.066548 | 0.069001 | -0.015171 | 0.024297 | 0.1905 | 0.10139 | 0.1528 | 0.080262 | 0.2148 | 0.18628 | 0.065455 | 121.4559 | 121.3583 | 0.014092 | -0.092633 | 0.084859 | 0.087312 | 0.00314 | 0.042608 | 121.371 | 121.4527 | -0.070767 | 0.010952
779.6875 | 121.5042 | -0.14648 | 121.376 | 0.034862 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 121.4421 | 121.3492 | -0.004219 | -0.10637 | 0.071126 | 0.073579 | -0.010593 | 0.028875 | 0.18135 | 0.10138 | 0.1528 | 0.093996 | 0.22395 | 0.18628 | 0.065454 | 121.4604 | 121.3675 | 0.014092 | -0.088054 | 0.089437 | 0.09189 | 0.007718 | 0.047186 | 121.371 | 121.4527 | -0.075345 | 0.006374
781.3594 | 121.5134 | -0.15106 | 121.3989 | 0.044018 | -0.049678 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 121.4467 | 121.34 | -0.004219 | -0.11094 | 0.066548 | 0.069001 | -0.010593 | 0.038032 | 0.19508 | 0.10138 | 0.14822 | 0.098574 | 0.22395 | 0.19544 | 0.07461 | 121.465 | 121.3583 | 0.014092 | -0.092633 | 0.084859 | 0.087312 | 0.007718 | 0.056343 | 121.3802 | 121.4573 | -0.070767 | 0.006374
783.0312 | 121.5225 | -0.14648 | 121.3715 | 0.048597 | -0.054257 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.071874 | 121.4421 | 121.3492 | 0.004937 | -0.11094 | 0.06197 | 0.073579 | -0.010593 | 0.028875 | 0.19508 | 0.092227 | 0.14822 | 0.089418 | 0.22395 | 0.18628 | 0.07461 | 121.4604 | 121.3675 | 0.023248 | -0.092633 | 0.080281 | 0.09189 | 0.007718 | 0.047186 | 121.3802 | 121.4527 | -0.057033 | 0.01553
784.7188 | 121.5637 | -0.12817 | 121.3669 | 0.034862 | -0.035942 | 0.001736 | -0.061645 | 0.077466 | 0.044377 | -0.071874 | 121.4467 | 121.3583 | 0.004937 | -0.11094 | 0.06197 | 0.078157 | -0.010593 | 0.028875 | 0.16304 | 0.092232 | 0.12991 | 0.066529 | 0.20564 | 0.17255 | 0.0563 | 121.465 | 121.3767 | 0.023248 | -0.092633 | 0.080281 | 0.096468 | 0.007718 | 0.047186 | 121.3847 | 121.4573 | -0.057033 | 0.01553
786.4688 | 121.5271 | -0.13275 | 121.3715 | 0.053175 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.4467 | 121.3538 | -0.004219 | -0.11552 | 0.071126 | 0.073579 | -0.006014 | 0.033454 | 0.18593 | 0.087651 | 0.13449 | 0.075685 | 0.20564 | 0.17255 | 0.056299 | 121.465 | 121.3721 | 0.014092 | -0.097212 | 0.089437 | 0.09189 | 0.012297 | 0.051765 | 121.3756 | 121.4527 | -0.075345 | 0.001795
788.1406 | 121.5179 | -0.13733 | 121.3852 | 0.044018 | -0.049678 | -0.002842 | -0.052488 | 0.077466 | 0.048956 | -0.071874 | 121.4513 | 121.3538 | -0.008798 | -0.11552 | 0.066548 | 0.073579 | -0.006014 | 0.028875 | 0.18135 | 0.087651 | 0.13449 | 0.084841 | 0.2148 | 0.18629 | 0.065455 | 121.4696 | 121.3721 | 0.009513 | -0.097212 | 0.084859 | 0.09189 | 0.012297 | 0.047186 | 121.3847 | 121.4573 | -0.075346 | -0.002784
789.8125 | 121.463 | -0.16937 | 121.4172 | 0.03944 | -0.049678 | -0.002842 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 121.4513 | 121.3583 | -0.004219 | -0.10637 | 0.071126 | 0.069001 | -0.015171 | 0.028875 | 0.20881 | 0.11969 | 0.16653 | 0.11688 | 0.25142 | 0.21375 | 0.092921 | 121.4696 | 121.3767 | 0.014092 | -0.088054 | 0.089437 | 0.087312 | 0.00314 | 0.047186 | 121.3802 | 121.4665 | -0.075345 | 0.010952
791.5312 | 121.4767 | -0.15106 | 121.3943 | 0.044018 | -0.049678 | -0.002842 | -0.047909 | 0.072888 | 0.039799 | -0.076452 | 121.4513 | 121.3583 | 0.004937 | -0.10637 | 0.06197 | 0.069001 | -0.010593 | 0.028875 | 0.19508 | 0.10138 | 0.14822 | 0.10315 | 0.22395 | 0.19086 | 0.07461 | 121.4696 | 121.3767 | 0.023248 | -0.088054 | 0.080281 | 0.087312 | 0.007718 | 0.047186 | 121.3893 | 121.4619 | -0.057033 | 0.01553
793.2031 | 121.4539 | -0.17853 | 121.3943 | 0.03944 | -0.040521 | 0.001736 | -0.057066 | 0.06831 | 0.039799 | -0.08103 | 121.4513 | 121.3538 | 0.004937 | -0.10637 | 0.066548 | 0.064423 | -0.010593 | 0.038032 | 0.21797 | 0.13801 | 0.18026 | 0.12146 | 0.24684 | 0.21833 | 0.097498 | 121.4696 | 121.3721 | 0.023248 | -0.088054 | 0.084859 | 0.082734 | 0.007718 | 0.056343 | 121.3847 | 121.4619 | -0.061611 | 0.01553
794.9062 | 121.5088 | -0.11444 | 121.3577 | 0.034862 | -0.049678 | -0.002842 | -0.061645 | 0.082044 | 0.044377 | -0.076452 | 121.4513 | 121.3538 | 0.000359 | -0.11094 | 0.066548 | 0.064423 | -0.015171 | 0.028875 | 0.1493 | 0.064763 | 0.1116 | 0.052796 | 0.19649 | 0.15882 | 0.037989 | 121.4696 | 121.3721 | 0.01867 | -0.092633 | 0.084859 | 0.082734 | 0.00314 | 0.047186 | 121.3847 | 121.4665 | -0.066189 | 0.01553
796.5781 | 121.4813 | -0.13733 | 121.3898 | 0.044018 | -0.049678 | -0.002842 | -0.061645 | 0.072888 | 0.044377 | -0.071874 | 121.4559 | 121.3538 | 0.004937 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.028875 | 0.18135 | 0.087651 | 0.13449 | 0.075684 | 0.21022 | 0.18171 | 0.065455 | 121.4742 | 121.3721 | 0.023248 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.047186 | 121.3939 | 121.471 | -0.057033 | 0.020108
798.2812 | 121.5637 | -0.10986 | 121.3806 | 0.048597 | -0.040521 | -0.002842 | -0.061645 | 0.072888 | 0.044377 | -0.076452 | 121.4559 | 121.3583 | 0.000359 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 0.15846 | 0.069342 | 0.10702 | 0.048218 | 0.18275 | 0.15424 | 0.033411 | 121.4742 | 121.3767 | 0.01867 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | 121.3985 | 121.4756 | -0.057033 | 0.020108
799.9531 | 121.5729 | -0.1236 | 121.3715 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.076452 | 121.4513 | 121.3583 | 0.000359 | -0.10637 | 0.066548 | 0.073579 | -0.006014 | 0.019719 | 0.16761 | 0.078496 | 0.12533 | 0.06653 | 0.20106 | 0.1634 | 0.047144 | 121.4696 | 121.3767 | 0.01867 | -0.088054 | 0.084859 | 0.09189 | 0.012297 | 0.03803 | 121.3847 | 121.4573 | -0.066189 | 0.006373
801.625 | 121.463 | -0.17395 | 121.4172 | 0.030283 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.4559 | 121.3629 | -0.004219 | -0.11552 | 0.06197 | 0.073579 | -0.010593 | 0.028875 | 0.20423 | 0.12885 | 0.18026 | 0.12146 | 0.25142 | 0.21833 | 0.097498 | 121.4742 | 121.3812 | 0.014092 | -0.097212 | 0.080281 | 0.09189 | 0.007718 | 0.047186 | 121.3939 | 121.4665 | -0.066189 | 0.006374
803.2969 | 121.4401 | -0.16479 | 121.4035 | 0.03944 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.067295 | 121.4604 | 121.3583 | 0.000359 | -0.10637 | 0.066548 | 0.064423 | -0.010593 | 0.028875 | 0.20423 | 0.12885 | 0.16653 | 0.11231 | 0.24226 | 0.20917 | 0.0975 | 121.4788 | 121.3767 | 0.01867 | -0.088054 | 0.084859 | 0.082734 | 0.007718 | 0.047186 | 121.3939 | 121.471 | -0.066189 | 0.010952
804.9844 | 121.5683 | -0.12817 | 121.3623 | 0.044018 | -0.049678 | -0.002842 | -0.043331 | 0.072888 | 0.039799 | -0.071874 | 121.4604 | 121.3629 | 0.000359 | -0.10637 | 0.06197 | 0.073579 | -0.010593 | 0.024297 | 0.17219 | 0.078496 | 0.12533 | 0.084843 | 0.20106 | 0.16797 | 0.0563 | 121.4788 | 121.3812 | 0.01867 | -0.088054 | 0.080281 | 0.09189 | 0.007718 | 0.042608 | 121.3985 | 121.471 | -0.061611 | 0.010952
806.6562 | 121.431 | -0.14648 | 121.4172 | 0.034862 | -0.0451 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.076452 | 121.4559 | 121.3629 | -0.004219 | -0.11094 | 0.057392 | 0.069001 | -0.010593 | 0.024297 | 0.18135 | 0.10138 | 0.14822 | 0.098575 | 0.22853 | 0.18628 | 0.070032 | 121.4742 | 121.3812 | 0.014092 | -0.092633 | 0.075703 | 0.087312 | 0.007718 | 0.042608 | 121.3985 | 121.4665 | -0.061611 | 0.006374
808.3438 | 121.5546 | -0.10986 | 121.3806 | 0.034862 | -0.0451 | -0.002842 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.4604 | 121.3675 | 0.000359 | -0.10179 | 0.057392 | 0.064423 | -0.015171 | 0.033454 | 0.14472 | 0.064763 | 0.10702 | 0.052797 | 0.18275 | 0.14966 | 0.033411 | 121.4788 | 121.3858 | 0.01867 | -0.083475 | 0.075703 | 0.082734 | 0.00314 | 0.051765 | 121.4031 | 121.4756 | -0.057033 | 0.01553
810.0312 | 121.5134 | -0.14648 | 121.3806 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.08103 | 121.4604 | 121.3721 | -0.004219 | -0.11094 | 0.066548 | 0.069001 | -0.010593 | 0.028875 | 0.1905 | 0.10596 | 0.1528 | 0.093996 | 0.22395 | 0.19086 | 0.065454 | 121.4788 | 121.3904 | 0.014092 | -0.092633 | 0.084859 | 0.087312 | 0.007718 | 0.047186 | 121.3939 | 121.471 | -0.070767 | 0.006374
811.7188 | 121.4447 | -0.17853 | 121.4401 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.071874 | 121.4696 | 121.3675 | -0.004219 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.024297 | 0.22255 | 0.13343 | 0.18026 | 0.12146 | 0.25599 | 0.2229 | 0.10665 | 121.4879 | 121.3858 | 0.014092 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.042608 | 121.4076 | 121.4848 | -0.066189 | 0.010952
813.4688 | 121.4401 | -0.16022 | 121.4218 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.4559 | 121.3721 | -0.008798 | -0.10637 | 0.052814 | 0.069001 | -0.010593 | 0.033454 | 0.20423 | 0.11512 | 0.16653 | 0.10773 | 0.23768 | 0.20459 | 0.083765 | 121.4742 | 121.3904 | 0.009513 | -0.088054 | 0.071125 | 0.087312 | 0.007718 | 0.051765 | 121.4031 | 121.4665 | -0.061612 | 0.001795
815.2188 | 121.5729 | -0.11902 | 121.3898 | 0.034862 | -0.0451 | -0.002842 | -0.052488 | 0.082044 | 0.044377 | -0.08103 | 121.4604 | 121.3675 | 0.004937 | -0.10637 | 0.057392 | 0.073579 | -0.015171 | 0.024297 | 0.15388 | 0.073919 | 0.11618 | 0.066531 | 0.20106 | 0.1634 | 0.037989 | 121.4788 | 121.3858 | 0.023248 | -0.088054 | 0.075703 | 0.09189 | 0.00314 | 0.042608 | 121.4031 | 121.4756 | -0.052455 | 0.020108
816.9219 | 121.5042 | -0.14191 | 121.4081 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.086622 | 0.044377 | -0.076452 | 121.465 | 121.3721 | -0.004219 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.028875 | 0.17677 | 0.096807 | 0.14364 | 0.089419 | 0.22853 | 0.18628 | 0.065455 | 121.4833 | 121.3904 | 0.014092 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.047186 | 121.4076 | 121.4848 | -0.061611 | 0.01553
818.6719 | 121.5179 | -0.14191 | 121.3715 | 0.030283 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.048956 | -0.076452 | 121.465 | 121.3721 | -0.008798 | -0.10637 | 0.057392 | 0.069001 | -0.010593 | 0.024297 | 0.17219 | 0.10139 | 0.14364 | 0.084841 | 0.2148 | 0.19086 | 0.065455 | 121.4833 | 121.3904 | 0.009513 | -0.088054 | 0.075703 | 0.087312 | 0.007718 | 0.042608 | 121.4076 | 121.4756 | -0.06619 | 0.001795
820.3594 | 121.4813 | -0.15106 | 121.4264 | 0.034862 | -0.040521 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 121.4742 | 121.3721 | 0.000359 | -0.10637 | 0.052814 | 0.064423 | -0.015171 | 0.028875 | 0.18592 | 0.11054 | 0.1528 | 0.10315 | 0.22853 | 0.19544 | 0.07461 | 121.4925 | 121.3904 | 0.01867 | -0.088054 | 0.071125 | 0.082734 | 0.00314 | 0.047186 | 121.4214 | 121.4894 | -0.052455 | 0.01553
822.1094 | 121.5591 | -0.14191 | 121.4127 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.048956 | -0.076452 | 121.465 | 121.3767 | 0.000359 | -0.11552 | 0.06197 | 0.059844 | -0.010593 | 0.024297 | 0.18593 | 0.10139 | 0.14364 | 0.084841 | 0.2148 | 0.19086 | 0.065455 | 121.4833 | 121.395 | 0.01867 | -0.097212 | 0.080281 | 0.078155 | 0.007718 | 0.042608 | 121.4031 | 121.4756 | -0.061611 | 0.010952
823.7812 | 121.5179 | -0.11444 | 121.4035 | 0.034862 | -0.040521 | -0.002842 | -0.057066 | 0.077466 | 0.039799 | -0.08103 | 121.4604 | 121.3767 | -0.004219 | -0.10637 | 0.06197 | 0.069001 | -0.015171 | 0.024297 | 0.1493 | 0.07392 | 0.1116 | 0.057375 | 0.19191 | 0.15424 | 0.033411 | 121.4788 | 121.395 | 0.014092 | -0.088054 | 0.080281 | 0.087312 | 0.00314 | 0.042608 | 121.3985 | 121.4756 | -0.066189 | 0.010952
825.5312 | 121.5225 | -0.13733 | 121.3806 | 0.034862 | -0.040521 | 0.006315 | -0.057066 | 0.072888 | 0.044377 | -0.085608 | 121.465 | 121.3767 | -0.008798 | -0.11094 | 0.057392 | 0.069001 | -0.015171 | 0.024297 | 0.17219 | 0.096808 | 0.14364 | 0.080263 | 0.21022 | 0.18171 | 0.051721 | 121.4833 | 121.395 | 0.009513 | -0.092633 | 0.075703 | 0.087312 | 0.00314 | 0.042608 | 121.4076 | 121.4802 | -0.06619 | 0.006373
827.2188 | 121.582 | -0.11902 | 121.3898 | 0.044018 | -0.0451 | -0.002842 | -0.057066 | 0.077466 | 0.039799 | -0.071874 | 121.4696 | 121.3812 | -0.008798 | -0.10637 | 0.057392 | 0.064423 | -0.006014 | 0.028875 | 0.16304 | 0.073919 | 0.11618 | 0.061953 | 0.19648 | 0.15882 | 0.047145 | 121.4879 | 121.3996 | 0.009513 | -0.088054 | 0.075703 | 0.082734 | 0.012297 | 0.047186 | 121.4122 | 121.4756 | -0.06619 | -0.002784
828.8906 | 121.5179 | -0.12817 | 121.4172 | 0.034862 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.08103 | 121.465 | 121.3767 | -0.008798 | -0.10637 | 0.052814 | 0.059844 | -0.010593 | 0.024297 | 0.16304 | 0.087653 | 0.12991 | 0.071108 | 0.21022 | 0.16797 | 0.047144 | 121.4833 | 121.395 | 0.009513 | -0.088054 | 0.071125 | 0.078155 | 0.007718 | 0.042608 | 121.4122 | 121.4756 | -0.061612 | 0.001795
830.625 | 121.5317 | -0.13275 | 121.4081 | 0.034862 | -0.049678 | 0.001736 | -0.057066 | 0.086622 | 0.048956 | -0.076452 | 121.4696 | 121.3721 | 0.000359 | -0.11094 | 0.057392 | 0.064423 | -0.010593 | 0.028875 | 0.16761 | 0.083073 | 0.13449 | 0.075685 | 0.21937 | 0.18171 | 0.056299 | 121.4879 | 121.3904 | 0.01867 | -0.092633 | 0.075703 | 0.082734 | 0.007718 | 0.047186 | 121.4122 | 121.4802 | -0.057033 | 0.010952
832.2969 | 121.4401 | -0.15106 | 121.431 | 0.034862 | -0.040521 | 0.001736 | -0.047909 | 0.082044 | 0.035221 | -0.071874 | 121.4742 | 121.3812 | 0.000359 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.024297 | 0.18592 | 0.11054 | 0.1528 | 0.10315 | 0.23311 | 0.18628 | 0.079188 | 121.4925 | 121.3996 | 0.01867 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.042608 | 121.4168 | 121.4894 | -0.057033 | 0.01553
834.0312 | 121.4676 | -0.16022 | 121.4035 | 0.03944 | -0.0451 | 0.006315 | -0.057066 | 0.082044 | 0.035221 | -0.08103 | 121.4742 | 121.3767 | -0.004219 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.024297 | 0.19966 | 0.11512 | 0.16653 | 0.10315 | 0.24226 | 0.19544 | 0.079187 | 121.4925 | 121.395 | 0.014092 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.042608 | 121.4122 | 121.4939 | -0.066189 | 0.01553
835.7031 | 121.5408 | -0.11902 | 121.4127 | 0.03944 | -0.049678 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.08103 | 121.4742 | 121.3858 | -0.004219 | -0.10179 | 0.052814 | 0.064423 | -0.010593 | 0.019719 | 0.15846 | 0.069341 | 0.12076 | 0.07111 | 0.19648 | 0.15882 | 0.037989 | 121.4925 | 121.4041 | 0.014092 | -0.083475 | 0.071125 | 0.082734 | 0.007718 | 0.03803 | 121.4214 | 121.4848 | -0.057033 | 0.006374
837.4375 | 121.5225 | -0.1236 | 121.3989 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.076452 | 121.4788 | 121.3812 | -0.004219 | -0.10637 | 0.057392 | 0.064423 | -0.006014 | 0.033454 | 0.16761 | 0.083075 | 0.12533 | 0.06653 | 0.20564 | 0.1634 | 0.047144 | 121.4971 | 121.3996 | 0.014092 | -0.088054 | 0.075703 | 0.082734 | 0.012297 | 0.051765 | 121.4214 | 121.4848 | -0.061611 | 0.001795
839.1094 | 121.4996 | -0.16479 | 121.4081 | 0.03944 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.044377 | -0.08103 | 121.4742 | 121.3812 | 0.000359 | -0.11552 | 0.06197 | 0.064423 | -0.010593 | 0.028875 | 0.20423 | 0.11969 | 0.16653 | 0.10773 | 0.23768 | 0.20917 | 0.083765 | 121.4925 | 121.3996 | 0.01867 | -0.097212 | 0.080281 | 0.082734 | 0.007718 | 0.047186 | 121.4122 | 121.4848 | -0.061611 | 0.010952
840.8438 | 121.4905 | -0.16022 | 121.4081 | 0.03944 | -0.0451 | 0.001736 | -0.057066 | 0.082044 | 0.035221 | -0.076452 | 121.4833 | 121.3858 | 0.000359 | -0.11552 | 0.057392 | 0.064423 | -0.015171 | 0.028875 | 0.19966 | 0.11512 | 0.16195 | 0.10315 | 0.24226 | 0.19544 | 0.083765 | 121.5016 | 121.4041 | 0.01867 | -0.097212 | 0.075703 | 0.082734 | 0.00314 | 0.047186 | 121.4259 | 121.4985 | -0.057033 | 0.01553
842.5938 | 121.4264 | -0.13275 | 121.4539 | 0.03944 | -0.040521 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 121.4788 | 121.3858 | -0.004219 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.019719 | 0.17219 | 0.09223 | 0.13449 | 0.084842 | 0.21022 | 0.17255 | 0.056299 | 121.4971 | 121.4041 | 0.014092 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.03803 | 121.4214 | 121.4939 | -0.061611 | 0.010952
844.2812 | 121.5683 | -0.10986 | 121.3898 | 0.044018 | -0.049678 | 0.006315 | -0.057066 | 0.082044 | 0.039799 | -0.08103 | 121.4742 | 121.3812 | -0.004219 | -0.11094 | 0.06197 | 0.069001 | -0.006014 | 0.024297 | 0.15388 | 0.060185 | 0.11618 | 0.052797 | 0.19191 | 0.14966 | 0.028833 | 121.4925 | 121.3996 | 0.014092 | -0.092633 | 0.080281 | 0.087312 | 0.012297 | 0.042608 | 121.4122 | 121.4802 | -0.066189 | 0.001795
846.0312 | 121.5729 | -0.10529 | 121.3806 | 0.034862 | -0.040521 | 0.001736 | -0.061645 | 0.072888 | 0.039799 | -0.076452 | 121.4788 | 121.3858 | 0.000359 | -0.11094 | 0.066548 | 0.064423 | -0.015171 | 0.024297 | 0.14015 | 0.064765 | 0.10702 | 0.043641 | 0.17817 | 0.14509 | 0.028834 | 121.4971 | 121.4041 | 0.01867 | -0.092633 | 0.084859 | 0.082734 | 0.00314 | 0.042608 | 121.4122 | 121.4939 | -0.066189 | 0.01553
847.7812 | 121.5729 | -0.10986 | 121.3715 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.082044 | 0.039799 | -0.08103 | 121.4788 | 121.3812 | -0.004219 | -0.11094 | 0.066548 | 0.055266 | -0.010593 | 0.024297 | 0.15388 | 0.064763 | 0.1116 | 0.057375 | 0.19191 | 0.14966 | 0.028833 | 121.4971 | 121.3996 | 0.014092 | -0.092633 | 0.084859 | 0.073577 | 0.007718 | 0.042608 | 121.4122 | 121.4894 | -0.070767 | 0.006374
849.5312 | 121.5958 | -0.09613 | 121.4081 | 0.048597 | -0.0451 | -0.002842 | -0.052488 | 0.082044 | 0.035221 | -0.085608 | 121.4833 | 121.3858 | -0.004219 | -0.10179 | 0.057392 | 0.064423 | -0.015171 | 0.028875 | 0.14473 | 0.05103 | 0.093288 | 0.043642 | 0.17817 | 0.13135 | 0.010522 | 121.5016 | 121.4041 | 0.014092 | -0.083475 | 0.075703 | 0.082734 | 0.00314 | 0.047186 | 121.4259 | 121.4985 | -0.061611 | 0.010952
851.2188 | 121.4813 | -0.15564 | 121.4218 | 0.044018 | -0.0451 | -0.002842 | -0.057066 | 0.077466 | 0.039799 | -0.076452 | 121.4833 | 121.3904 | -0.008798 | -0.11094 | 0.057392 | 0.055266 | -0.019749 | 0.024297 | 0.19966 | 0.11054 | 0.1528 | 0.098574 | 0.23311 | 0.19544 | 0.079188 | 121.5016 | 121.4087 | 0.009513 | -0.092633 | 0.075703 | 0.073577 | -0.001438 | 0.042608 | 121.4259 | 121.5031 | -0.06619 | 0.010951
852.9062 | 121.5042 | -0.13275 | 121.4401 | 0.03944 | -0.0451 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.076452 | 121.4833 | 121.395 | -0.008798 | -0.11094 | 0.057392 | 0.069001 | -0.010593 | 0.019719 | 0.17219 | 0.087651 | 0.13907 | 0.084842 | 0.21022 | 0.17255 | 0.056299 | 121.5016 | 121.4133 | 0.009513 | -0.092633 | 0.075703 | 0.087312 | 0.007718 | 0.03803 | 121.4259 | 121.4939 | -0.06619 | 0.001795
854.6562 | 121.6003 | -0.13275 | 121.3943 | 0.03944 | -0.049678 | 0.006315 | -0.061645 | 0.077466 | 0.039799 | -0.08103 | 121.4879 | 121.3904 | -0.008798 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.019719 | 0.17219 | 0.083073 | 0.13907 | 0.071106 | 0.21022 | 0.17255 | 0.051721 | 121.5062 | 121.4087 | 0.009513 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.03803 | 121.4305 | 121.5031 | -0.06619 | 0.006373
856.3281 | 121.5088 | -0.16022 | 121.4264 | 0.044018 | -0.0451 | -0.007421 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 121.4925 | 121.3858 | -0.004219 | -0.11094 | 0.052814 | 0.064423 | -0.010593 | 0.028875 | 0.20423 | 0.11512 | 0.1528 | 0.10773 | 0.23768 | 0.20002 | 0.079187 | 121.5108 | 121.4041 | 0.014092 | -0.092633 | 0.071125 | 0.082734 | 0.007718 | 0.047186 | 121.4397 | 121.5031 | -0.057033 | 0.006374
858.0625 | 121.4951 | -0.14648 | 121.4035 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.08103 | 121.4833 | 121.395 | 0.000359 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.033454 | 0.1905 | 0.10596 | 0.1528 | 0.089418 | 0.22853 | 0.19086 | 0.065454 | 121.5016 | 121.4133 | 0.01867 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.051765 | 121.4259 | 121.4985 | -0.057033 | 0.01553
859.7344 | 121.5866 | -0.10986 | 121.3898 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.077466 | 0.039799 | -0.085608 | 121.4879 | 121.395 | -0.004219 | -0.11552 | 0.052814 | 0.064423 | -0.015171 | 0.028875 | 0.1493 | 0.064763 | 0.10702 | 0.057375 | 0.18733 | 0.14966 | 0.024255 | 121.5062 | 121.4133 | 0.014092 | -0.097212 | 0.071125 | 0.082734 | 0.00314 | 0.047186 | 121.4351 | 121.5031 | -0.057033 | 0.010952
861.5 | 121.5637 | -0.10986 | 121.431 | 0.044018 | -0.040521 | 0.006315 | -0.043331 | 0.072888 | 0.044377 | -0.076452 | 121.4879 | 121.3904 | 0.004937 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.024297 | 0.15388 | 0.069342 | 0.11618 | 0.066532 | 0.18275 | 0.15424 | 0.033411 | 121.5062 | 121.4087 | 0.023248 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.042608 | 121.4259 | 121.5077 | -0.057033 | 0.024686
863.25 | 121.5637 | -0.11444 | 121.4127 | 0.034862 | -0.0451 | 0.001736 | -0.043331 | 0.082044 | 0.035221 | -0.076452 | 121.4833 | 121.3904 | 0.000359 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.024297 | 0.1493 | 0.069341 | 0.11618 | 0.07111 | 0.19649 | 0.14966 | 0.037989 | 121.5016 | 121.4087 | 0.01867 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.042608 | 121.4259 | 121.5031 | -0.057033 | 0.020108
864.9219 | 121.5958 | -0.11902 | 121.4218 | 0.03944 | -0.040521 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 121.4788 | 121.3904 | -0.008798 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.024297 | 0.15846 | 0.078498 | 0.12076 | 0.07111 | 0.20106 | 0.1634 | 0.042567 | 121.4971 | 121.4087 | 0.009513 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.042608 | 121.4214 | 121.4939 | -0.06619 | 0.006373
866.6719 | 121.4584 | -0.12817 | 121.431 | 0.034862 | -0.049678 | 0.006315 | -0.057066 | 0.077466 | 0.044377 | -0.071874 | 121.4925 | 121.3996 | -0.008798 | -0.10637 | 0.06197 | 0.069001 | -0.010593 | 0.028875 | 0.16304 | 0.078496 | 0.13449 | 0.071108 | 0.20564 | 0.17255 | 0.0563 | 121.5108 | 121.4179 | 0.009513 | -0.088054 | 0.080281 | 0.087312 | 0.007718 | 0.047186 | 121.4305 | 121.5031 | -0.070768 | 0.001795
868.3594 | 121.5454 | -0.13733 | 121.3898 | 0.03944 | -0.049678 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 121.4925 | 121.395 | -0.008798 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.033454 | 0.17677 | 0.087651 | 0.14364 | 0.084841 | 0.2148 | 0.17713 | 0.056299 | 121.5108 | 121.4133 | 0.009513 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.051765 | 121.4351 | 121.5077 | -0.06619 | 0.006373
870.0938 | 121.5775 | -0.13733 | 121.4035 | 0.03944 | -0.040521 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.076452 | 121.4925 | 121.395 | 0.000359 | -0.11552 | 0.052814 | 0.055266 | -0.010593 | 0.028875 | 0.17677 | 0.096808 | 0.13906 | 0.08942 | 0.21937 | 0.18171 | 0.060877 | 121.5108 | 121.4133 | 0.01867 | -0.097212 | 0.071125 | 0.073577 | 0.007718 | 0.047186 | 121.4397 | 121.5031 | -0.052455 | 0.010952
871.8438 | 121.5088 | -0.14191 | 121.4584 | 0.030283 | -0.0451 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.071874 | 121.4971 | 121.4087 | -0.004219 | -0.11094 | 0.052814 | 0.064423 | -0.010593 | 0.024297 | 0.17219 | 0.096807 | 0.14822 | 0.093998 | 0.21937 | 0.18171 | 0.070033 | 121.5154 | 121.427 | 0.014092 | -0.092633 | 0.071125 | 0.082734 | 0.007718 | 0.042608 | 121.4443 | 121.5077 | -0.057033 | 0.006374
873.5938 | 121.463 | -0.17853 | 121.4218 | 0.034862 | -0.049678 | 0.001736 | -0.052488 | 0.082044 | 0.039799 | -0.076452 | 121.5017 | 121.3996 | 0.000359 | -0.10179 | 0.057392 | 0.050688 | -0.015171 | 0.028875 | 0.21339 | 0.12885 | 0.18026 | 0.12604 | 0.26057 | 0.21833 | 0.10208 | 121.52 | 121.4179 | 0.01867 | -0.083475 | 0.075703 | 0.068999 | 0.00314 | 0.047186 | 121.4443 | 121.5168 | -0.057033 | 0.01553
875.3281 | 121.463 | -0.15106 | 121.4447 | 0.044018 | -0.0451 | 0.006315 | -0.057066 | 0.077466 | 0.048956 | -0.08103 | 121.4971 | 121.3996 | 0.000359 | -0.11094 | 0.057392 | 0.064423 | -0.010593 | 0.024297 | 0.19508 | 0.10596 | 0.15738 | 0.093996 | 0.22853 | 0.20002 | 0.070032 | 121.5154 | 121.4179 | 0.01867 | -0.092633 | 0.075703 | 0.082734 | 0.007718 | 0.042608 | 121.4397 | 121.5077 | -0.057033 | 0.010952
877 | 121.6003 | -0.11444 | 121.3943 | 0.034862 | -0.049678 | 0.001736 | -0.052488 | 0.082044 | 0.048956 | -0.071874 | 121.4879 | 121.4041 | -0.004219 | -0.11094 | 0.06197 | 0.064423 | -0.015171 | 0.019719 | 0.1493 | 0.064763 | 0.11618 | 0.061953 | 0.19649 | 0.1634 | 0.042567 | 121.5062 | 121.4224 | 0.014092 | -0.092633 | 0.080281 | 0.082734 | 0.00314 | 0.03803 | 121.4259 | 121.5031 | -0.066189 | 0.010952
878.75 | 121.5317 | -0.13733 | 121.4081 | 0.03944 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.035221 | -0.08103 | 121.4971 | 121.4087 | 0.000359 | -0.10637 | 0.057392 | 0.064423 | -0.006014 | 0.019719 | 0.17677 | 0.096808 | 0.14364 | 0.084841 | 0.2148 | 0.17255 | 0.056299 | 121.5154 | 121.427 | 0.01867 | -0.088054 | 0.075703 | 0.082734 | 0.012297 | 0.03803 | 121.4397 | 121.5031 | -0.057033 | 0.006373
880.4375 | 121.5866 | -0.09613 | 121.4081 | 0.03944 | -0.0451 | -0.002842 | -0.061645 | 0.077466 | 0.044377 | -0.076452 | 121.4971 | 121.4087 | -0.004219 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.028875 | 0.13557 | 0.05103 | 0.093288 | 0.034485 | 0.1736 | 0.14051 | 0.019678 | 121.5154 | 121.427 | 0.014092 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.047186 | 121.4397 | 121.5168 | -0.061611 | 0.01553
882.1875 | 121.4813 | -0.14648 | 121.4493 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.06831 | 0.039799 | -0.076452 | 121.5017 | 121.3996 | -0.004219 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.019719 | 0.18592 | 0.10138 | 0.14364 | 0.093996 | 0.21479 | 0.18628 | 0.070032 | 121.52 | 121.4179 | 0.014092 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.03803 | 121.4488 | 121.5214 | -0.057033 | 0.01553
883.9219 | 121.5179 | -0.13733 | 121.4172 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.077466 | 0.048956 | -0.08103 | 121.4971 | 121.4041 | -0.004219 | -0.11094 | 0.057392 | 0.064423 | -0.010593 | 0.024297 | 0.18135 | 0.092229 | 0.13906 | 0.084841 | 0.2148 | 0.18629 | 0.056299 | 121.5154 | 121.4224 | 0.014092 | -0.092633 | 0.075703 | 0.082734 | 0.007718 | 0.042608 | 121.4397 | 121.5077 | -0.061611 | 0.006374
885.6562 | 121.5134 | -0.14191 | 121.4264 | 0.048597 | -0.040521 | 0.006315 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 121.5062 | 121.4041 | 0.000359 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 0.1905 | 0.10139 | 0.14822 | 0.089419 | 0.2148 | 0.18171 | 0.065455 | 121.5245 | 121.4224 | 0.01867 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | 121.4443 | 121.526 | -0.061611 | 0.020108
887.3438 | 121.5729 | -0.082397 | 121.3943 | 0.03944 | -0.040521 | -0.007421 | -0.057066 | 0.077466 | 0.048956 | -0.076452 | 121.4925 | 121.4041 | -0.008798 | -0.11094 | 0.052814 | 0.055266 | -0.015171 | 0.024297 | 0.12184 | 0.041876 | 0.074976 | 0.025331 | 0.15986 | 0.13135 | 0.005945 | 121.5108 | 121.4224 | 0.009513 | -0.092633 | 0.071125 | 0.073577 | 0.00314 | 0.042608 | 121.4397 | 121.5077 | -0.061612 | 0.006373
889.0938 | 121.6232 | -0.11902 | 121.4264 | 0.030283 | -0.049678 | -0.002842 | -0.061645 | 0.072888 | 0.039799 | -0.08103 | 121.4925 | 121.4087 | -0.004219 | -0.10179 | 0.057392 | 0.059844 | -0.015171 | 0.019719 | 0.1493 | 0.069341 | 0.11618 | 0.057374 | 0.19191 | 0.15882 | 0.037989 | 121.5108 | 121.427 | 0.014092 | -0.083475 | 0.075703 | 0.078155 | 0.00314 | 0.03803 | 121.4351 | 121.5077 | -0.061611 | 0.010952
890.8281 | 121.4813 | -0.16022 | 121.4493 | 0.044018 | -0.0451 | 0.001736 | -0.066223 | 0.077466 | 0.053534 | -0.071874 | 121.5017 | 121.4041 | -0.004219 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.024297 | 0.20423 | 0.11512 | 0.16195 | 0.093994 | 0.23768 | 0.21375 | 0.088343 | 121.52 | 121.4224 | 0.014092 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.042608 | 121.4443 | 121.5214 | -0.061611 | 0.01553
892.5781 | 121.6049 | -0.11902 | 121.431 | 0.044018 | -0.049678 | -0.002842 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 121.4971 | 121.4133 | -0.004219 | -0.11094 | 0.06197 | 0.059844 | -0.015171 | 0.024297 | 0.16304 | 0.069341 | 0.11618 | 0.066531 | 0.19648 | 0.15882 | 0.042567 | 121.5154 | 121.4316 | 0.014092 | -0.092633 | 0.080281 | 0.078155 | 0.00314 | 0.042608 | 121.4351 | 121.5122 | -0.066189 | 0.010952
894.3125 | 121.5775 | -0.11902 | 121.3943 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.077466 | 0.048956 | -0.076452 | 121.5017 | 121.4087 | -0.008798 | -0.11094 | 0.052814 | 0.059844 | -0.015171 | 0.028875 | 0.15388 | 0.073919 | 0.12076 | 0.066531 | 0.19648 | 0.16797 | 0.042567 | 121.52 | 121.427 | 0.009513 | -0.092633 | 0.071125 | 0.078155 | 0.00314 | 0.047186 | 121.4488 | 121.5168 | -0.061612 | 0.006373
895.9844 | 121.5179 | -0.13275 | 121.4218 | 0.044018 | -0.049678 | 0.001736 | -0.057066 | 0.082044 | 0.044377 | -0.076452 | 121.5017 | 121.4041 | 0.000359 | -0.11094 | 0.052814 | 0.059844 | -0.015171 | 0.024297 | 0.17677 | 0.083073 | 0.13449 | 0.075685 | 0.2148 | 0.17713 | 0.056299 | 121.52 | 121.4224 | 0.01867 | -0.092633 | 0.071125 | 0.078155 | 0.00314 | 0.042608 | 121.4488 | 121.5168 | -0.052455 | 0.01553
897.7188 | 121.5729 | -0.1236 | 121.4127 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.077466 | 0.048956 | -0.076452 | 121.4971 | 121.4087 | 0.000359 | -0.11552 | 0.057392 | 0.064423 | -0.015171 | 0.024297 | 0.16304 | 0.078496 | 0.12075 | 0.071108 | 0.20106 | 0.17255 | 0.047144 | 121.5154 | 121.427 | 0.01867 | -0.097212 | 0.075703 | 0.082734 | 0.00314 | 0.042608 | 121.4397 | 121.5122 | -0.057033 | 0.01553
899.4531 | 121.5591 | -0.10986 | 121.4127 | 0.03944 | -0.040521 | -0.007421 | -0.057066 | 0.082044 | 0.030642 | -0.076452 | 121.5062 | 121.4041 | -0.004219 | -0.10637 | 0.066548 | 0.050688 | -0.010593 | 0.024297 | 0.1493 | 0.069342 | 0.10244 | 0.052797 | 0.19191 | 0.1405 | 0.033411 | 121.5245 | 121.4224 | 0.014092 | -0.088054 | 0.084859 | 0.068999 | 0.007718 | 0.042608 | 121.4397 | 121.5168 | -0.070767 | 0.006374
901.1406 | 121.4767 | -0.16022 | 121.4676 | 0.034862 | -0.049678 | -0.002842 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.5108 | 121.4179 | -0.013376 | -0.10637 | 0.057392 | 0.059844 | -0.010593 | 0.028875 | 0.19508 | 0.11054 | 0.15737 | 0.10315 | 0.23311 | 0.20002 | 0.083765 | 121.5291 | 121.4362 | 0.004935 | -0.088054 | 0.075703 | 0.078155 | 0.007718 | 0.047186 | 121.4534 | 121.5214 | -0.070768 | -0.002783
902.8906 | 121.5546 | -0.12817 | 121.4355 | 0.034862 | -0.049678 | 0.006315 | -0.061645 | 0.072888 | 0.035221 | -0.076452 | 121.5062 | 121.4087 | 0.000359 | -0.11094 | 0.06197 | 0.059844 | -0.015171 | 0.024297 | 0.16304 | 0.078496 | 0.13449 | 0.066529 | 0.20106 | 0.1634 | 0.051722 | 121.5245 | 121.427 | 0.01867 | -0.092633 | 0.080281 | 0.078155 | 0.00314 | 0.042608 | 121.4443 | 121.5214 | -0.061611 | 0.01553
904.625 | 121.5225 | -0.1236 | 121.431 | 0.034862 | -0.054257 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 121.5062 | 121.4133 | -0.008798 | -0.11552 | 0.048236 | 0.064423 | -0.015171 | 0.024297 | 0.15846 | 0.069339 | 0.12075 | 0.071108 | 0.19648 | 0.16797 | 0.047144 | 121.5245 | 121.4316 | 0.009513 | -0.097212 | 0.066547 | 0.082734 | 0.00314 | 0.042608 | 121.458 | 121.5214 | -0.057034 | 0.006373
906.2969 | 121.5088 | -0.16479 | 121.4539 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.048956 | -0.076452 | 121.5062 | 121.4133 | 0.000359 | -0.10637 | 0.057392 | 0.055266 | -0.015171 | 0.024297 | 0.20881 | 0.12427 | 0.16653 | 0.10773 | 0.24226 | 0.21375 | 0.088343 | 121.5245 | 121.4316 | 0.01867 | -0.088054 | 0.075703 | 0.073577 | 0.00314 | 0.042608 | 121.4488 | 121.5214 | -0.057033 | 0.01553
908.0469 | 121.5546 | -0.10529 | 121.4539 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.077466 | 0.039799 | -0.076452 | 121.5062 | 121.4087 | -0.004219 | -0.10637 | 0.06197 | 0.059844 | -0.015171 | 0.024297 | 0.1493 | 0.064765 | 0.1116 | 0.04822 | 0.18275 | 0.14509 | 0.028834 | 121.5245 | 121.427 | 0.014092 | -0.088054 | 0.080281 | 0.078155 | 0.00314 | 0.042608 | 121.4443 | 121.5214 | -0.066189 | 0.010952
909.7188 | 121.5088 | -0.15564 | 121.431 | 0.034862 | -0.040521 | 0.001736 | -0.047909 | 0.072888 | 0.044377 | -0.076452 | 121.5017 | 121.4133 | -0.004219 | -0.10179 | 0.066548 | 0.059844 | -0.019749 | 0.024297 | 0.1905 | 0.11512 | 0.15738 | 0.10773 | 0.22853 | 0.20002 | 0.079188 | 121.52 | 121.4316 | 0.014092 | -0.083475 | 0.084859 | 0.078155 | -0.001438 | 0.042608 | 121.4351 | 121.5214 | -0.070767 | 0.01553
911.4844 | 121.5683 | -0.11902 | 121.4127 | 0.044018 | -0.0451 | -0.007421 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.5108 | 121.4179 | -0.004219 | -0.10179 | 0.066548 | 0.064423 | -0.010593 | 0.028875 | 0.16304 | 0.073919 | 0.1116 | 0.066531 | 0.19648 | 0.1634 | 0.047145 | 121.5291 | 121.4362 | 0.014092 | -0.083475 | 0.084859 | 0.082734 | 0.007718 | 0.047186 | 121.4443 | 121.5214 | -0.070767 | 0.006374
913.1719 | 121.5546 | -0.12817 | 121.4172 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.048956 | -0.08103 | 121.5062 | 121.4225 | -0.004219 | -0.10637 | 0.052814 | 0.059844 | -0.010593 | 0.033454 | 0.17219 | 0.083074 | 0.13449 | 0.075686 | 0.20564 | 0.17713 | 0.047144 | 121.5245 | 121.4408 | 0.014092 | -0.088054 | 0.071125 | 0.078155 | 0.007718 | 0.051765 | 121.4534 | 121.5168 | -0.057033 | 0.006374
914.8438 | 121.4996 | -0.15564 | 121.4539 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 121.5062 | 121.4179 | 0.000359 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.028875 | 0.1905 | 0.11054 | 0.15738 | 0.10315 | 0.23311 | 0.19544 | 0.07461 | 121.5245 | 121.4362 | 0.01867 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.047186 | 121.4488 | 121.5214 | -0.057033 | 0.01553
916.5938 | 121.5408 | -0.1236 | 121.4447 | 0.03944 | -0.0451 | -0.002842 | -0.057066 | 0.082044 | 0.048956 | -0.071874 | 121.5108 | 121.4179 | -0.008798 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.024297 | 0.16304 | 0.078496 | 0.12075 | 0.06653 | 0.20564 | 0.17255 | 0.051722 | 121.5291 | 121.4362 | 0.009513 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.042608 | 121.4534 | 121.5351 | -0.06619 | 0.01553
918.3438 | 121.4996 | -0.15564 | 121.4584 | 0.044018 | -0.035942 | 0.006315 | -0.057066 | 0.077466 | 0.048956 | -0.076452 | 121.5154 | 121.4179 | -0.008798 | -0.11094 | 0.06197 | 0.059844 | -0.015171 | 0.024297 | 0.19966 | 0.1197 | 0.16195 | 0.098574 | 0.23311 | 0.2046 | 0.079188 | 121.5337 | 121.4362 | 0.009513 | -0.092633 | 0.080281 | 0.078155 | 0.00314 | 0.042608 | 121.4534 | 121.5306 | -0.070768 | 0.006373
920.0781 | 121.4676 | -0.15106 | 121.4676 | 0.044018 | -0.049678 | 0.001736 | -0.057066 | 0.077466 | 0.058113 | -0.076452 | 121.5108 | 121.4133 | -0.004219 | -0.11094 | 0.057392 | 0.055266 | -0.015171 | 0.019719 | 0.19508 | 0.10138 | 0.1528 | 0.093996 | 0.22853 | 0.20917 | 0.07461 | 121.5291 | 121.4316 | 0.014092 | -0.092633 | 0.075703 | 0.073577 | 0.00314 | 0.03803 | 121.4534 | 121.526 | -0.061611 | 0.010952
921.75 | 121.4767 | -0.15106 | 121.4355 | 0.044018 | -0.035942 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.071874 | 121.5108 | 121.4179 | -0.008798 | -0.11094 | 0.052814 | 0.064423 | -0.015171 | 0.015141 | 0.19508 | 0.11512 | 0.1528 | 0.10315 | 0.23311 | 0.19086 | 0.079188 | 121.5291 | 121.4362 | 0.009513 | -0.092633 | 0.071125 | 0.082734 | 0.00314 | 0.033452 | 121.458 | 121.526 | -0.061612 | 0.006373
923.4844 | 121.4722 | -0.15106 | 121.4493 | 0.03944 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.035221 | -0.071874 | 121.5108 | 121.4133 | -0.004219 | -0.10179 | 0.057392 | 0.064423 | -0.019749 | 0.024297 | 0.1905 | 0.11054 | 0.15738 | 0.093996 | 0.23311 | 0.18628 | 0.079188 | 121.5291 | 121.4316 | 0.014092 | -0.083475 | 0.075703 | 0.082734 | -0.001438 | 0.042608 | 121.4534 | 121.5306 | -0.061611 | 0.01553
925.1562 | 121.5958 | -0.13275 | 121.4355 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.072888 | 0.030642 | -0.085608 | 121.5108 | 121.4133 | -0.004219 | -0.10637 | 0.06197 | 0.055266 | -0.006014 | 0.028875 | 0.17219 | 0.087651 | 0.12991 | 0.080263 | 0.20564 | 0.16339 | 0.047143 | 121.5291 | 121.4316 | 0.014092 | -0.088054 | 0.080281 | 0.073577 | 0.012297 | 0.047186 | 121.4488 | 121.5168 | -0.066189 | 0.001795
926.8281 | 121.4996 | -0.14648 | 121.463 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.048956 | -0.076452 | 121.5062 | 121.4225 | 0.000359 | -0.11552 | 0.057392 | 0.059844 | -0.010593 | 0.019719 | 0.1905 | 0.10596 | 0.14822 | 0.089418 | 0.22853 | 0.19544 | 0.070032 | 121.5245 | 121.4408 | 0.01867 | -0.097212 | 0.075703 | 0.078155 | 0.007718 | 0.03803 | 121.4488 | 121.5168 | -0.057033 | 0.010952
928.5781 | 121.6095 | -0.12817 | 121.4035 | 0.034862 | -0.049678 | -0.002842 | -0.047909 | 0.072888 | 0.039799 | -0.076452 | 121.5108 | 121.4179 | -0.008798 | -0.11094 | 0.057392 | 0.064423 | -0.010593 | 0.024297 | 0.16304 | 0.078496 | 0.12533 | 0.080265 | 0.20106 | 0.16797 | 0.051722 | 121.5291 | 121.4362 | 0.009513 | -0.092633 | 0.075703 | 0.082734 | 0.007718 | 0.042608 | 121.4534 | 121.5214 | -0.06619 | 0.001795
930.375 | 121.4813 | -0.16937 | 121.4401 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.52 | 121.4179 | -0.004219 | -0.11094 | 0.06197 | 0.064423 | -0.015171 | 0.028875 | 0.21339 | 0.12427 | 0.17569 | 0.11688 | 0.24684 | 0.21375 | 0.092921 | 121.5383 | 121.4362 | 0.014092 | -0.092633 | 0.080281 | 0.082734 | 0.00314 | 0.047186 | 121.458 | 121.5351 | -0.066189 | 0.010952
932.0469 | 121.4813 | -0.15106 | 121.4264 | 0.044018 | -0.049678 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 121.5108 | 121.427 | -0.008798 | -0.11094 | 0.06197 | 0.059844 | -0.015171 | 0.028875 | 0.19508 | 0.10138 | 0.1528 | 0.098574 | 0.23311 | 0.19544 | 0.07461 | 121.5291 | 121.4453 | 0.009513 | -0.092633 | 0.080281 | 0.078155 | 0.00314 | 0.047186 | 121.4488 | 121.526 | -0.070768 | 0.006373
933.7188 | 121.582 | -0.1236 | 121.4401 | 0.034862 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.071874 | 121.52 | 121.4179 | -0.008798 | -0.11094 | 0.052814 | 0.064423 | -0.015171 | 0.024297 | 0.15846 | 0.083075 | 0.12533 | 0.06653 | 0.20564 | 0.1634 | 0.051722 | 121.5383 | 121.4362 | 0.009513 | -0.092633 | 0.071125 | 0.082734 | 0.00314 | 0.042608 | 121.4672 | 121.5351 | -0.061612 | 0.006373
935.4688 | 121.4859 | -0.1831 | 121.4539 | 0.044018 | -0.0451 | -0.007421 | -0.047909 | 0.077466 | 0.044377 | -0.076452 | 121.5245 | 121.427 | -0.004219 | -0.10637 | 0.06197 | 0.073579 | -0.019749 | 0.024297 | 0.22712 | 0.138 | 0.17568 | 0.1352 | 0.26057 | 0.22748 | 0.10665 | 121.5429 | 121.4453 | 0.014092 | -0.088054 | 0.080281 | 0.09189 | -0.001438 | 0.042608 | 121.4626 | 121.5443 | -0.066189 | 0.01553
937.2031 | 121.4996 | -0.13733 | 121.4447 | 0.034862 | -0.0451 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.076452 | 121.5154 | 121.427 | 0.000359 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.028875 | 0.17219 | 0.092229 | 0.14364 | 0.080263 | 0.21937 | 0.18171 | 0.060877 | 121.5337 | 121.4453 | 0.01867 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.047186 | 121.458 | 121.5306 | -0.057033 | 0.01553
938.8906 | 121.6049 | -0.10529 | 121.431 | 0.044018 | -0.040521 | -0.002842 | -0.057066 | 0.077466 | 0.039799 | -0.08103 | 121.5108 | 121.4225 | -0.013376 | -0.11094 | 0.048236 | 0.059844 | -0.015171 | 0.028875 | 0.1493 | 0.064765 | 0.10244 | 0.04822 | 0.18275 | 0.14509 | 0.024256 | 121.5291 | 121.4408 | 0.004935 | -0.092633 | 0.066547 | 0.078155 | 0.00314 | 0.047186 | 121.4626 | 121.526 | -0.061612 | 0.001795
940.6406 | 121.5775 | -0.13733 | 121.4447 | 0.044018 | -0.054257 | 0.001736 | -0.061645 | 0.077466 | 0.044377 | -0.076452 | 121.5108 | 121.4316 | -0.004219 | -0.10637 | 0.06197 | 0.064423 | -0.010593 | 0.028875 | 0.18135 | 0.083072 | 0.13906 | 0.075684 | 0.2148 | 0.18171 | 0.060877 | 121.5291 | 121.4499 | 0.014092 | -0.088054 | 0.080281 | 0.082734 | 0.007718 | 0.047186 | 121.4488 | 121.5214 | -0.066189 | 0.006374
942.3281 | 121.6003 | -0.10529 | 121.4172 | 0.03944 | -0.0451 | -0.002842 | -0.061645 | 0.082044 | 0.044377 | -0.062717 | 121.52 | 121.4225 | 0.000359 | -0.10637 | 0.06197 | 0.059844 | -0.015171 | 0.024297 | 0.14473 | 0.060186 | 0.10244 | 0.043641 | 0.18733 | 0.14966 | 0.042569 | 121.5383 | 121.4408 | 0.01867 | -0.088054 | 0.080281 | 0.078155 | 0.00314 | 0.042608 | 121.458 | 121.5351 | -0.061611 | 0.01553
944.0156 | 121.5729 | -0.11444 | 121.4401 | 0.03944 | -0.0451 | 0.006315 | -0.057066 | 0.077466 | 0.044377 | -0.090186 | 121.5291 | 121.4225 | -0.008798 | -0.11552 | 0.057392 | 0.059844 | -0.015171 | 0.024297 | 0.15388 | 0.069341 | 0.12076 | 0.057375 | 0.19191 | 0.15882 | 0.024255 | 121.5474 | 121.4408 | 0.009513 | -0.097212 | 0.075703 | 0.078155 | 0.00314 | 0.042608 | 121.4717 | 121.5443 | -0.06619 | 0.006373
945.6875 | 121.5179 | -0.15564 | 121.4676 | 0.044018 | -0.0451 | 0.010893 | -0.047909 | 0.072888 | 0.048956 | -0.071874 | 121.5245 | 121.4316 | -0.004219 | -0.11552 | 0.066548 | 0.055266 | -0.015171 | 0.024297 | 0.19966 | 0.11054 | 0.16653 | 0.10773 | 0.22853 | 0.2046 | 0.083766 | 121.5429 | 121.4499 | 0.014092 | -0.097212 | 0.084859 | 0.073577 | 0.00314 | 0.042608 | 121.458 | 121.5397 | -0.070767 | 0.010952
947.4219 | 121.6187 | -0.10986 | 121.4264 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.044377 | -0.076452 | 121.5291 | 121.4179 | 0.000359 | -0.11094 | 0.066548 | 0.064423 | -0.019749 | 0.024297 | 0.15388 | 0.064763 | 0.1116 | 0.052797 | 0.18275 | 0.15424 | 0.033411 | 121.5474 | 121.4362 | 0.01867 | -0.092633 | 0.084859 | 0.082734 | -0.001438 | 0.042608 | 121.4626 | 121.5489 | -0.066189 | 0.020108
949.1875 | 121.6232 | -0.10071 | 121.4539 | 0.044018 | -0.049678 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.085608 | 121.5154 | 121.427 | -0.004219 | -0.11094 | 0.057392 | 0.050688 | -0.010593 | 0.024297 | 0.14473 | 0.05103 | 0.10244 | 0.04822 | 0.17817 | 0.14509 | 0.0151 | 121.5337 | 121.4453 | 0.014092 | -0.092633 | 0.075703 | 0.068999 | 0.007718 | 0.042608 | 121.458 | 121.526 | -0.061611 | 0.006374
950.8594 | 121.6599 | -0.1236 | 121.4264 | 0.048597 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.52 | 121.427 | -0.008798 | -0.10637 | 0.06197 | 0.064423 | -0.006014 | 0.019719 | 0.17219 | 0.078496 | 0.12533 | 0.06653 | 0.19648 | 0.1634 | 0.047144 | 121.5383 | 121.4453 | 0.009513 | -0.088054 | 0.080281 | 0.082734 | 0.012297 | 0.03803 | 121.458 | 121.526 | -0.070768 | -0.002784
952.6094 | 121.55 | -0.12817 | 121.4584 | 0.03944 | -0.049678 | 0.001736 | -0.057066 | 0.077466 | 0.035221 | -0.076452 | 121.52 | 121.4179 | -0.008798 | -0.10179 | 0.057392 | 0.069001 | -0.006014 | 0.028875 | 0.16761 | 0.078496 | 0.12991 | 0.071108 | 0.20564 | 0.1634 | 0.051722 | 121.5383 | 121.4362 | 0.009513 | -0.083475 | 0.075703 | 0.087312 | 0.012297 | 0.047186 | 121.4626 | 121.526 | -0.06619 | -0.002784
954.3594 | 121.5683 | -0.13275 | 121.4401 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.039799 | -0.071874 | 121.5245 | 121.4316 | -0.004219 | -0.10179 | 0.057392 | 0.064423 | -0.010593 | 0.028875 | 0.16761 | 0.09223 | 0.13449 | 0.080263 | 0.2148 | 0.17255 | 0.060877 | 121.5429 | 121.4499 | 0.014092 | -0.083475 | 0.075703 | 0.082734 | 0.007718 | 0.047186 | 121.4672 | 121.5351 | -0.061611 | 0.006374
956.0469 | 121.6003 | -0.11902 | 121.4401 | 0.03944 | -0.035942 | 0.001736 | -0.061645 | 0.082044 | 0.044377 | -0.076452 | 121.5245 | 121.4225 | 0.000359 | -0.11552 | 0.06197 | 0.064423 | -0.010593 | 0.028875 | 0.15846 | 0.083077 | 0.12076 | 0.057374 | 0.20106 | 0.1634 | 0.042567 | 121.5429 | 121.4408 | 0.01867 | -0.097212 | 0.080281 | 0.082734 | 0.007718 | 0.047186 | 121.4626 | 121.5351 | -0.061611 | 0.010952
957.7344 | 121.6095 | -0.12817 | 121.4401 | 0.03944 | -0.049678 | 0.001736 | -0.061645 | 0.082044 | 0.044377 | -0.08103 | 121.5245 | 121.4225 | -0.013376 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.024297 | 0.16761 | 0.078496 | 0.12991 | 0.066529 | 0.21022 | 0.17255 | 0.047144 | 121.5429 | 121.4408 | 0.004935 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.042608 | 121.4672 | 121.5443 | -0.070768 | 0.006373
959.4531 | 121.5088 | -0.16937 | 121.4447 | 0.03944 | -0.040521 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.071874 | 121.5154 | 121.4225 | -0.004219 | -0.11094 | 0.071126 | 0.059844 | -0.019749 | 0.024297 | 0.20881 | 0.12885 | 0.17111 | 0.12604 | 0.24226 | 0.21375 | 0.097499 | 121.5337 | 121.4408 | 0.014092 | -0.092633 | 0.089437 | 0.078155 | -0.001438 | 0.042608 | 121.4443 | 121.5351 | -0.075345 | 0.01553
961.2031 | 121.5225 | -0.15564 | 121.463 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.06831 | 0.044377 | -0.076452 | 121.5245 | 121.4316 | -0.004219 | -0.097207 | 0.057392 | 0.055266 | -0.024328 | 0.028875 | 0.19966 | 0.11054 | 0.15738 | 0.10315 | 0.22395 | 0.20002 | 0.079188 | 121.5429 | 121.4499 | 0.014092 | -0.078896 | 0.075703 | 0.073577 | -0.006017 | 0.047186 | 121.4672 | 121.5489 | -0.061611 | 0.020109
962.8906 | 121.6095 | -0.09613 | 121.4081 | 0.034862 | -0.035942 | 0.001736 | -0.061645 | 0.086622 | 0.039799 | -0.076452 | 121.5245 | 121.4362 | -0.008798 | -0.11094 | 0.06197 | 0.069001 | -0.019749 | 0.019719 | 0.13099 | 0.060188 | 0.097866 | 0.034485 | 0.18275 | 0.13593 | 0.019678 | 121.5429 | 121.4545 | 0.009513 | -0.092633 | 0.080281 | 0.087312 | -0.001438 | 0.03803 | 121.4626 | 121.5443 | -0.070768 | 0.010951
964.6406 | 121.4813 | -0.17853 | 121.4859 | 0.048597 | -0.049678 | 0.006315 | -0.057066 | 0.077466 | 0.044377 | -0.08103 | 121.5245 | 121.4362 | 0.000359 | -0.10179 | 0.057392 | 0.069001 | -0.010593 | 0.024297 | 0.22712 | 0.12885 | 0.18484 | 0.12146 | 0.25599 | 0.2229 | 0.097498 | 121.5429 | 121.4545 | 0.01867 | -0.083475 | 0.075703 | 0.087312 | 0.007718 | 0.042608 | 121.4672 | 121.5351 | -0.057033 | 0.010952
966.3906 | 121.6141 | -0.10529 | 121.4401 | 0.044018 | -0.0451 | 0.010893 | -0.057066 | 0.077466 | 0.039799 | -0.085608 | 121.5245 | 121.427 | -0.008798 | -0.10637 | 0.06197 | 0.059844 | -0.010593 | 0.024297 | 0.1493 | 0.060186 | 0.11618 | 0.04822 | 0.18275 | 0.14509 | 0.019678 | 121.5429 | 121.4453 | 0.009513 | -0.088054 | 0.080281 | 0.078155 | 0.007718 | 0.042608 | 121.4626 | 121.5351 | -0.070768 | 0.001795
968.125 | 121.4859 | -0.16022 | 121.4539 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.5291 | 121.4316 | -0.008798 | -0.10179 | 0.057392 | 0.069001 | -0.019749 | 0.028875 | 0.19508 | 0.11512 | 0.16195 | 0.10773 | 0.23768 | 0.20459 | 0.083765 | 121.5474 | 121.4499 | 0.009513 | -0.083475 | 0.075703 | 0.087312 | -0.001438 | 0.047186 | 121.4717 | 121.5489 | -0.06619 | 0.010951
969.8125 | 121.5637 | -0.11902 | 121.4722 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 121.5245 | 121.4316 | -0.008798 | -0.11094 | 0.06197 | 0.069001 | -0.019749 | 0.024297 | 0.15388 | 0.078498 | 0.12076 | 0.066531 | 0.19648 | 0.15882 | 0.037989 | 121.5429 | 121.4499 | 0.009513 | -0.092633 | 0.080281 | 0.087312 | -0.001438 | 0.042608 | 121.4626 | 121.5443 | -0.070768 | 0.010951
971.5469 | 121.5363 | -0.16022 | 121.4355 | 0.044018 | -0.054257 | -0.002842 | -0.057066 | 0.082044 | 0.048956 | -0.071874 | 121.5291 | 121.4362 | -0.004219 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.024297 | 0.20423 | 0.10596 | 0.15737 | 0.10315 | 0.24226 | 0.20917 | 0.088343 | 121.5474 | 121.4545 | 0.014092 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.042608 | 121.4717 | 121.5443 | -0.061611 | 0.010952
973.2969 | 121.5546 | -0.16479 | 121.4447 | 0.03944 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.08103 | 121.5245 | 121.4316 | -0.013376 | -0.10637 | 0.057392 | 0.069001 | -0.015171 | 0.033454 | 0.20423 | 0.12427 | 0.17111 | 0.11231 | 0.24226 | 0.20917 | 0.083765 | 121.5429 | 121.4499 | 0.004935 | -0.088054 | 0.075703 | 0.087312 | 0.00314 | 0.051765 | 121.4672 | 121.5397 | -0.070768 | 0.001795
974.9688 | 121.5088 | -0.16937 | 121.4813 | 0.03944 | -0.049678 | 0.006315 | -0.047909 | 0.086622 | 0.044377 | -0.076452 | 121.5291 | 121.4316 | -0.004219 | -0.10637 | 0.06197 | 0.059844 | -0.010593 | 0.024297 | 0.20881 | 0.11969 | 0.17569 | 0.12146 | 0.25599 | 0.21375 | 0.092921 | 121.5474 | 121.4499 | 0.014092 | -0.088054 | 0.080281 | 0.078155 | 0.007718 | 0.042608 | 121.4672 | 121.5397 | -0.066189 | 0.006374
976.6406 | 121.4859 | -0.15106 | 121.4676 | 0.044018 | -0.040521 | -0.002842 | -0.052488 | 0.06831 | 0.039799 | -0.076452 | 121.5291 | 121.4316 | -0.008798 | -0.10179 | 0.057392 | 0.055266 | -0.019749 | 0.024297 | 0.19508 | 0.11054 | 0.14822 | 0.098574 | 0.21937 | 0.19086 | 0.07461 | 121.5474 | 121.4499 | 0.009513 | -0.083475 | 0.075703 | 0.073577 | -0.001438 | 0.042608 | 121.4717 | 121.5489 | -0.06619 | 0.010951
978.3906 | 121.4951 | -0.16479 | 121.4813 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 121.5383 | 121.4408 | -0.004219 | -0.10637 | 0.06197 | 0.064423 | -0.010593 | 0.028875 | 0.20881 | 0.11969 | 0.17111 | 0.11231 | 0.24684 | 0.20917 | 0.092921 | 121.5566 | 121.4591 | 0.014092 | -0.088054 | 0.080281 | 0.082734 | 0.007718 | 0.047186 | 121.4763 | 121.5489 | -0.066189 | 0.006374
980.125 | 121.5317 | -0.16022 | 121.4447 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.5245 | 121.4316 | -0.008798 | -0.10637 | 0.066548 | 0.050688 | -0.010593 | 0.028875 | 0.19508 | 0.1197 | 0.16195 | 0.10773 | 0.23768 | 0.20459 | 0.088343 | 121.5429 | 121.4499 | 0.009513 | -0.088054 | 0.084859 | 0.068999 | 0.007718 | 0.047186 | 121.458 | 121.5351 | -0.075346 | 0.001795
981.7969 | 121.5271 | -0.13733 | 121.4722 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.076452 | 121.5245 | 121.427 | -0.013376 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.028875 | 0.18135 | 0.092229 | 0.13906 | 0.080263 | 0.2148 | 0.18171 | 0.060877 | 121.5429 | 121.4453 | 0.004935 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.047186 | 121.4672 | 121.5443 | -0.070768 | 0.006373
983.5469 | 121.5271 | -0.16479 | 121.4584 | 0.03944 | -0.049678 | 0.001736 | -0.061645 | 0.082044 | 0.044377 | -0.076452 | 121.5291 | 121.4408 | -0.004219 | -0.11094 | 0.06197 | 0.069001 | -0.015171 | 0.024297 | 0.20423 | 0.11512 | 0.16653 | 0.10315 | 0.24684 | 0.20917 | 0.088343 | 121.5474 | 121.4591 | 0.014092 | -0.092633 | 0.080281 | 0.087312 | 0.00314 | 0.042608 | 121.4672 | 121.5443 | -0.066189 | 0.010952
985.2812 | 121.5591 | -0.14191 | 121.4676 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.086622 | 0.035221 | -0.08103 | 121.5291 | 121.4362 | -0.008798 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.024297 | 0.18593 | 0.096807 | 0.14364 | 0.089419 | 0.22853 | 0.17713 | 0.060877 | 121.5474 | 121.4545 | 0.009513 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.042608 | 121.4717 | 121.5489 | -0.06619 | 0.010951
986.9531 | 121.6324 | -0.10529 | 121.4539 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.044377 | -0.08103 | 121.5291 | 121.4362 | -0.004219 | -0.10637 | 0.066548 | 0.064423 | -0.006014 | 0.024297 | 0.1493 | 0.060186 | 0.10702 | 0.04822 | 0.17817 | 0.14966 | 0.024256 | 121.5474 | 121.4545 | 0.014092 | -0.088054 | 0.084859 | 0.082734 | 0.012297 | 0.042608 | 121.4626 | 121.5351 | -0.070767 | 0.001795
988.625 | 121.4951 | -0.1831 | 121.463 | 0.03944 | -0.049678 | 0.006315 | -0.061645 | 0.072888 | 0.039799 | -0.076452 | 121.5337 | 121.4362 | -0.008798 | -0.10637 | 0.06197 | 0.073579 | -0.015171 | 0.028875 | 0.22254 | 0.13343 | 0.18942 | 0.12146 | 0.25599 | 0.2229 | 0.10665 | 121.552 | 121.4545 | 0.009513 | -0.088054 | 0.080281 | 0.09189 | 0.00314 | 0.047186 | 121.4717 | 121.5489 | -0.070768 | 0.006373
990.375 | 121.5225 | -0.14191 | 121.4722 | 0.03944 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.076452 | 121.5291 | 121.4408 | -0.008798 | -0.10637 | 0.066548 | 0.064423 | -0.010593 | 0.028875 | 0.18135 | 0.10139 | 0.14822 | 0.084841 | 0.22395 | 0.18628 | 0.065455 | 121.5474 | 121.4591 | 0.009513 | -0.088054 | 0.084859 | 0.082734 | 0.007718 | 0.047186 | 121.4626 | 121.5397 | -0.075346 | 0.001795
992.1094 | 121.5729 | -0.15564 | 121.4493 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.076452 | 121.5291 | 121.4408 | -0.004219 | -0.11094 | 0.06197 | 0.064423 | -0.010593 | 0.033454 | 0.19508 | 0.11054 | 0.1528 | 0.10315 | 0.22853 | 0.20002 | 0.079188 | 121.5474 | 121.4591 | 0.014092 | -0.092633 | 0.080281 | 0.082734 | 0.007718 | 0.051765 | 121.4672 | 121.5397 | -0.066189 | 0.006374
993.8125 | 121.6003 | -0.12817 | 121.4401 | 0.030283 | -0.054257 | 0.001736 | -0.061645 | 0.072888 | 0.039799 | -0.076452 | 121.5337 | 121.427 | -0.008798 | -0.1201 | 0.066548 | 0.064423 | -0.001436 | 0.024297 | 0.15846 | 0.073917 | 0.12991 | 0.066529 | 0.20106 | 0.16797 | 0.051722 | 121.552 | 121.4453 | 0.009513 | -0.10179 | 0.084859 | 0.082734 | 0.016875 | 0.042608 | 121.4672 | 121.5351 | -0.075346 | -0.007362
995.5469 | 121.5042 | -0.17853 | 121.4493 | 0.03944 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.048956 | -0.071874 | 121.5337 | 121.4362 | -0.004219 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.028875 | 0.21797 | 0.13801 | 0.18484 | 0.12146 | 0.26057 | 0.22748 | 0.10665 | 121.552 | 121.4545 | 0.014092 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.047186 | 121.4763 | 121.5489 | -0.061611 | 0.010952
997.2344 | 121.4676 | -0.16022 | 121.4951 | 0.03944 | -0.049678 | -0.002842 | -0.052488 | 0.072888 | 0.039799 | -0.067295 | 121.5337 | 121.4316 | 0.000359 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.024297 | 0.19966 | 0.11054 | 0.15737 | 0.10773 | 0.23311 | 0.20002 | 0.092922 | 121.552 | 121.4499 | 0.01867 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.042608 | 121.4763 | 121.5489 | -0.057033 | 0.01553
998.9844 | 121.6278 | -0.11902 | 121.431 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 121.5291 | 121.4362 | -0.008798 | -0.10637 | 0.057392 | 0.069001 | -0.015171 | 0.024297 | 0.15388 | 0.078498 | 0.12076 | 0.066531 | 0.19648 | 0.15882 | 0.042567 | 121.5474 | 121.4545 | 0.009513 | -0.088054 | 0.075703 | 0.087312 | 0.00314 | 0.042608 | 121.4717 | 121.5443 | -0.06619 | 0.006373
1000.7188 | 121.5408 | -0.15564 | 121.4813 | 0.034862 | -0.0451 | 0.006315 | -0.057066 | 0.086622 | 0.048956 | -0.076452 | 121.5337 | 121.4362 | -0.013376 | -0.11094 | 0.057392 | 0.064423 | -0.010593 | 0.028875 | 0.1905 | 0.11054 | 0.16195 | 0.098574 | 0.24226 | 0.2046 | 0.079188 | 121.552 | 121.4545 | 0.004935 | -0.092633 | 0.075703 | 0.082734 | 0.007718 | 0.047186 | 121.4763 | 121.5443 | -0.070768 | -0.002783
1002.4688 | 121.5866 | -0.12817 | 121.4355 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.08103 | 121.5291 | 121.4316 | -0.004219 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.033454 | 0.17219 | 0.083074 | 0.12991 | 0.071108 | 0.20564 | 0.17255 | 0.047144 | 121.5474 | 121.4499 | 0.014092 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.051765 | 121.4672 | 121.5443 | -0.066189 | 0.010952
1004.2188 | 121.5179 | -0.16937 | 121.4676 | 0.048597 | -0.0451 | -0.002842 | -0.047909 | 0.077466 | 0.035221 | -0.08103 | 121.5337 | 121.4362 | 0.000359 | -0.11094 | 0.066548 | 0.069001 | -0.015171 | 0.028875 | 0.21797 | 0.12427 | 0.16653 | 0.12146 | 0.24684 | 0.20459 | 0.088343 | 121.552 | 121.4545 | 0.01867 | -0.092633 | 0.084859 | 0.087312 | 0.00314 | 0.047186 | 121.4672 | 121.5489 | -0.066189 | 0.01553
1005.9062 | 121.5271 | -0.16479 | 121.4813 | 0.044018 | -0.040521 | 0.001736 | -0.061645 | 0.072888 | 0.044377 | -0.076452 | 121.5337 | 121.4362 | -0.004219 | -0.11094 | 0.057392 | 0.069001 | -0.010593 | 0.033454 | 0.20881 | 0.12427 | 0.16653 | 0.10315 | 0.23768 | 0.20917 | 0.088343 | 121.552 | 121.4545 | 0.014092 | -0.092633 | 0.075703 | 0.087312 | 0.007718 | 0.051765 | 121.4763 | 121.5443 | -0.061611 | 0.006374
1007.6406 | 121.5225 | -0.15564 | 121.4813 | 0.044018 | -0.040521 | -0.002842 | -0.047909 | 0.082044 | 0.053534 | -0.071874 | 121.5383 | 121.4408 | -0.004219 | -0.10179 | 0.06197 | 0.064423 | -0.015171 | 0.028875 | 0.19966 | 0.11512 | 0.1528 | 0.10773 | 0.23768 | 0.20917 | 0.083766 | 121.5566 | 121.4591 | 0.014092 | -0.083475 | 0.080281 | 0.082734 | 0.00314 | 0.047186 | 121.4763 | 121.5534 | -0.066189 | 0.010952
1009.3906 | 121.5729 | -0.14191 | 121.4813 | 0.03944 | -0.0451 | 0.006315 | -0.057066 | 0.077466 | 0.044377 | -0.076452 | 121.5383 | 121.4316 | -0.017954 | -0.10637 | 0.066548 | 0.069001 | -0.010593 | 0.033454 | 0.18135 | 0.096807 | 0.14822 | 0.084841 | 0.21937 | 0.18628 | 0.065455 | 121.5566 | 121.4499 | 0.000357 | -0.088054 | 0.084859 | 0.087312 | 0.007718 | 0.051765 | 121.4717 | 121.5489 | -0.084502 | -0.007361
1011.0625 | 121.5775 | -0.11902 | 121.463 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.5291 | 121.4453 | 0.000359 | -0.11094 | 0.052814 | 0.069001 | -0.010593 | 0.028875 | 0.15846 | 0.078498 | 0.11618 | 0.066531 | 0.19648 | 0.1634 | 0.042567 | 121.5474 | 121.4637 | 0.01867 | -0.092633 | 0.071125 | 0.087312 | 0.007718 | 0.047186 | 121.4763 | 121.5397 | -0.052455 | 0.010952
1012.7969 | 121.6278 | -0.10986 | 121.4355 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.08103 | 121.5383 | 121.4362 | -0.004219 | -0.10637 | 0.057392 | 0.064423 | -0.006014 | 0.028875 | 0.15388 | 0.069342 | 0.1116 | 0.057375 | 0.18733 | 0.15424 | 0.028833 | 121.5566 | 121.4545 | 0.014092 | -0.088054 | 0.075703 | 0.082734 | 0.012297 | 0.047186 | 121.4809 | 121.5443 | -0.061611 | 0.001795
1014.5469 | 121.5363 | -0.17853 | 121.4813 | 0.03944 | -0.035942 | 0.006315 | -0.047909 | 0.072888 | 0.039799 | -0.076452 | 121.5337 | 121.4408 | -0.017954 | -0.11094 | 0.066548 | 0.064423 | -0.006014 | 0.028875 | 0.21797 | 0.14259 | 0.18484 | 0.13062 | 0.25142 | 0.21833 | 0.10208 | 121.552 | 121.4591 | 0.000357 | -0.092633 | 0.084859 | 0.082734 | 0.012297 | 0.047186 | 121.4672 | 121.5397 | -0.084502 | -0.01194
1016.2344 | 121.5958 | -0.12817 | 121.4172 | 0.034862 | -0.040521 | 0.006315 | -0.047909 | 0.082044 | 0.048956 | -0.076452 | 121.5383 | 121.4362 | -0.013376 | -0.10179 | 0.06197 | 0.064423 | -0.010593 | 0.024297 | 0.16304 | 0.087653 | 0.13449 | 0.080265 | 0.21022 | 0.17713 | 0.051722 | 121.5566 | 121.4545 | 0.004935 | -0.083475 | 0.080281 | 0.082734 | 0.007718 | 0.042608 | 121.4763 | 121.5489 | -0.075346 | -0.002783
1017.9688 | 121.4996 | -0.16479 | 121.4722 | 0.034862 | -0.0451 | -0.002842 | -0.052488 | 0.086622 | 0.048956 | -0.076452 | 121.5337 | 121.4408 | 0.000359 | -0.11094 | 0.06197 | 0.069001 | -0.006014 | 0.024297 | 0.19966 | 0.11969 | 0.16195 | 0.11231 | 0.25142 | 0.21375 | 0.088343 | 121.552 | 121.4591 | 0.01867 | -0.092633 | 0.080281 | 0.087312 | 0.012297 | 0.042608 | 121.4717 | 121.5397 | -0.061611 | 0.006373
1019.7188 | 121.4722 | -0.15564 | 121.4813 | 0.034862 | -0.054257 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.08103 | 121.5337 | 121.4362 | -0.008798 | -0.11094 | 0.057392 | 0.059844 | -0.015171 | 0.033454 | 0.1905 | 0.10138 | 0.15738 | 0.10315 | 0.23311 | 0.19544 | 0.07461 | 121.552 | 121.4545 | 0.009513 | -0.092633 | 0.075703 | 0.078155 | 0.00314 | 0.051765 | 121.4763 | 121.5489 | -0.06619 | 0.006373
1021.4688 | 121.6232 | -0.11444 | 121.4355 | 0.044018 | -0.0451 | 0.006315 | -0.057066 | 0.082044 | 0.048956 | -0.071874 | 121.5383 | 121.4453 | -0.004219 | -0.11094 | 0.066548 | 0.069001 | -0.010593 | 0.019719 | 0.15846 | 0.069341 | 0.12076 | 0.057375 | 0.19649 | 0.1634 | 0.042567 | 121.5566 | 121.4637 | 0.014092 | -0.092633 | 0.084859 | 0.087312 | 0.007718 | 0.03803 | 121.4717 | 121.5489 | -0.070767 | 0.006374
1023.1406 | 121.5042 | -0.17395 | 121.4539 | 0.03944 | -0.0451 | 0.010893 | -0.052488 | 0.072888 | 0.044377 | -0.071874 | 121.5474 | 121.4408 | -0.008798 | -0.11094 | 0.071126 | 0.064423 | -0.010593 | 0.028875 | 0.21339 | 0.12885 | 0.18484 | 0.12146 | 0.24684 | 0.21833 | 0.10208 | 121.5657 | 121.4591 | 0.009513 | -0.092633 | 0.089437 | 0.082734 | 0.007718 | 0.047186 | 121.4763 | 121.558 | -0.079924 | 0.001795
1024.875 | 121.4951 | -0.16022 | 121.4722 | 0.03944 | -0.0451 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.5383 | 121.4453 | -0.004219 | -0.11094 | 0.057392 | 0.059844 | -0.015171 | 0.028875 | 0.19966 | 0.11512 | 0.16195 | 0.10773 | 0.23768 | 0.20459 | 0.088343 | 121.5566 | 121.4637 | 0.014092 | -0.092633 | 0.075703 | 0.078155 | 0.00314 | 0.047186 | 121.4809 | 121.5534 | -0.061611 | 0.010952
1026.6094 | 121.5775 | -0.1236 | 121.4493 | 0.034862 | -0.0451 | -0.002842 | -0.057066 | 0.082044 | 0.044377 | -0.076452 | 121.5383 | 121.4408 | -0.004219 | -0.10179 | 0.066548 | 0.069001 | -0.010593 | 0.019719 | 0.15846 | 0.078496 | 0.12075 | 0.06653 | 0.20564 | 0.16797 | 0.047144 | 121.5566 | 121.4591 | 0.014092 | -0.083475 | 0.084859 | 0.087312 | 0.007718 | 0.03803 | 121.4717 | 121.5489 | -0.070767 | 0.006374
1028.2969 | 121.5134 | -0.16479 | 121.4905 | 0.044018 | -0.049678 | 0.006315 | -0.052488 | 0.082044 | 0.048956 | -0.071874 | 121.5429 | 121.4591 | 0.000359 | -0.11094 | 0.057392 | 0.064423 | -0.006014 | 0.024297 | 0.20881 | 0.11512 | 0.17111 | 0.11231 | 0.24684 | 0.21375 | 0.092921 | 121.5612 | 121.4774 | 0.01867 | -0.092633 | 0.075703 | 0.082734 | 0.012297 | 0.042608 | 121.4855 | 121.5489 | -0.057033 | 0.006373
1030.0469 | 121.5088 | -0.1831 | 121.4905 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.048956 | -0.071874 | 121.5429 | 121.4453 | 0.000359 | -0.10637 | 0.06197 | 0.064423 | -0.010593 | 0.024297 | 0.22712 | 0.138 | 0.18942 | 0.13062 | 0.26057 | 0.23206 | 0.11123 | 121.5612 | 121.4637 | 0.01867 | -0.088054 | 0.080281 | 0.082734 | 0.007718 | 0.042608 | 121.4809 | 121.5535 | -0.061611 | 0.010952
1031.7969 | 121.5637 | -0.13275 | 121.4584 | 0.034862 | -0.0451 | 0.001736 | -0.047909 | 0.086622 | 0.044377 | -0.08103 | 121.5474 | 121.4362 | 0.004937 | -0.10637 | 0.06197 | 0.073579 | -0.010593 | 0.019719 | 0.16761 | 0.087651 | 0.13449 | 0.084842 | 0.21937 | 0.17713 | 0.051721 | 121.5657 | 121.4545 | 0.023248 | -0.088054 | 0.080281 | 0.09189 | 0.007718 | 0.03803 | 121.4855 | 121.558 | -0.057033 | 0.01553
1033.5469 | 121.4996 | -0.16022 | 121.4813 | 0.030283 | -0.0451 | -0.002842 | -0.061645 | 0.072888 | 0.039799 | -0.076452 | 121.5474 | 121.4453 | -0.008798 | -0.11094 | 0.057392 | 0.064423 | -0.006014 | 0.024297 | 0.1905 | 0.11512 | 0.15737 | 0.098572 | 0.23311 | 0.20002 | 0.083765 | 121.5657 | 121.4637 | 0.009513 | -0.092633 | 0.075703 | 0.082734 | 0.012297 | 0.042608 | 121.49 | 121.5534 | -0.06619 | -0.002784
1035.2344 | 121.6278 | -0.10986 | 121.4218 | 0.03944 | -0.0451 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 121.5474 | 121.4362 | -0.008798 | -0.11552 | 0.06197 | 0.069001 | -0.015171 | 0.033454 | 0.1493 | 0.064763 | 0.1116 | 0.057375 | 0.19191 | 0.15424 | 0.033411 | 121.5657 | 121.4545 | 0.009513 | -0.097212 | 0.080281 | 0.087312 | 0.00314 | 0.051765 | 121.4855 | 121.5626 | -0.070768 | 0.006373
1036.9688 | 121.5454 | -0.15564 | 121.4722 | 0.03944 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.071874 | 121.5474 | 121.4362 | -0.004219 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.028875 | 0.19508 | 0.11512 | 0.15738 | 0.098574 | 0.23768 | 0.19544 | 0.083766 | 121.5657 | 121.4545 | 0.014092 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.047186 | 121.4855 | 121.5718 | -0.066189 | 0.020109
1038.6562 | 121.6141 | -0.14191 | 121.4264 | 0.048597 | -0.054257 | 0.006315 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 121.5383 | 121.4453 | -0.013376 | -0.10637 | 0.06197 | 0.069001 | -0.010593 | 0.028875 | 0.1905 | 0.08765 | 0.14822 | 0.084841 | 0.2148 | 0.18171 | 0.065455 | 121.5566 | 121.4637 | 0.004935 | -0.088054 | 0.080281 | 0.087312 | 0.007718 | 0.047186 | 121.4763 | 121.5489 | -0.075346 | -0.002783
1040.4062 | 121.6095 | -0.11444 | 121.4447 | 0.044018 | -0.035942 | 0.006315 | -0.061645 | 0.077466 | 0.039799 | -0.071874 | 121.5429 | 121.4408 | -0.004219 | -0.10179 | 0.06197 | 0.064423 | -0.015171 | 0.028875 | 0.15846 | 0.078499 | 0.12076 | 0.052796 | 0.19191 | 0.15424 | 0.042567 | 121.5612 | 121.4591 | 0.014092 | -0.083475 | 0.080281 | 0.082734 | 0.00314 | 0.047186 | 121.4809 | 121.558 | -0.066189 | 0.010952
1042.1406 | 121.5912 | -0.14191 | 121.4722 | 0.044018 | -0.0451 | -0.002842 | -0.052488 | 0.082044 | 0.044377 | -0.067295 | 121.5383 | 121.4453 | -0.008798 | -0.11094 | 0.06197 | 0.069001 | -0.015171 | 0.028875 | 0.18593 | 0.096807 | 0.13906 | 0.089419 | 0.22395 | 0.18628 | 0.074612 | 121.5566 | 121.4637 | 0.009513 | -0.092633 | 0.080281 | 0.087312 | 0.00314 | 0.047186 | 121.4763 | 121.5534 | -0.070768 | 0.006373
1043.8906 | 121.5408 | -0.13733 | 121.4676 | 0.044018 | -0.0451 | 0.006315 | -0.057066 | 0.086622 | 0.039799 | -0.071874 | 121.5383 | 121.4499 | 0.000359 | -0.10637 | 0.057392 | 0.064423 | 0.003143 | 0.028875 | 0.18135 | 0.092229 | 0.14364 | 0.080263 | 0.22395 | 0.17713 | 0.065455 | 121.5566 | 121.4682 | 0.01867 | -0.088054 | 0.075703 | 0.082734 | 0.021454 | 0.047186 | 121.4809 | 121.5351 | -0.057033 | -0.002784
1045.6094 | 121.5179 | -0.16937 | 121.5042 | 0.034862 | -0.035942 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.071874 | 121.5429 | 121.4499 | -0.004219 | -0.11552 | 0.06197 | 0.059844 | -0.006014 | 0.033454 | 0.20423 | 0.13343 | 0.17569 | 0.11231 | 0.25142 | 0.21375 | 0.097499 | 121.5612 | 121.4682 | 0.014092 | -0.097212 | 0.080281 | 0.078155 | 0.012297 | 0.051765 | 121.4809 | 121.5489 | -0.066189 | 0.001795
1047.2969 | 121.5134 | -0.15564 | 121.4767 | 0.03944 | -0.040521 | 0.006315 | -0.061645 | 0.072888 | 0.030642 | -0.071874 | 121.5474 | 121.4453 | -0.008798 | -0.11094 | 0.06197 | 0.064423 | -0.006014 | 0.028875 | 0.19508 | 0.11512 | 0.16195 | 0.093995 | 0.22853 | 0.18628 | 0.083766 | 121.5657 | 121.4637 | 0.009513 | -0.092633 | 0.080281 | 0.082734 | 0.012297 | 0.047186 | 121.4855 | 121.5534 | -0.070768 | -0.002784
1049.0469 | 121.6278 | -0.12817 | 121.4035 | 0.048597 | -0.0451 | 0.001736 | -0.052488 | 0.077466 | 0.048956 | -0.071874 | 121.5474 | 121.4453 | -0.004219 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 0.17677 | 0.083074 | 0.12991 | 0.075686 | 0.20564 | 0.17713 | 0.0563 | 121.5657 | 121.4637 | 0.014092 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | 121.49 | 121.5672 | -0.061611 | 0.01553
1050.7344 | 121.5958 | -0.11902 | 121.4355 | 0.03944 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.5429 | 121.4408 | 0.000359 | -0.10637 | 0.052814 | 0.059844 | -0.010593 | 0.028875 | 0.15846 | 0.083077 | 0.12076 | 0.066531 | 0.19648 | 0.1634 | 0.042567 | 121.5612 | 121.4591 | 0.01867 | -0.088054 | 0.071125 | 0.078155 | 0.007718 | 0.047186 | 121.49 | 121.5535 | -0.052455 | 0.010952
1052.4844 | 121.6141 | -0.1236 | 121.4493 | 0.03944 | -0.035942 | -0.002842 | -0.047909 | 0.086622 | 0.039799 | -0.071874 | 121.5429 | 121.4453 | -0.008798 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.028875 | 0.16304 | 0.087654 | 0.12075 | 0.075687 | 0.21022 | 0.1634 | 0.051722 | 121.5612 | 121.4637 | 0.009513 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.047186 | 121.4855 | 121.558 | -0.06619 | 0.006373
1054.2344 | 121.5546 | -0.15564 | 121.4905 | 0.053175 | -0.049678 | 0.001736 | -0.061645 | 0.077466 | 0.048956 | -0.071874 | 121.5429 | 121.4499 | -0.013376 | -0.10637 | 0.071126 | 0.064423 | -0.015171 | 0.028875 | 0.20882 | 0.10596 | 0.15738 | 0.093995 | 0.23311 | 0.2046 | 0.083766 | 121.5612 | 121.4682 | 0.004935 | -0.088054 | 0.089437 | 0.082734 | 0.00314 | 0.047186 | 121.4717 | 121.558 | -0.084502 | 0.001795
1055.9062 | 121.5866 | -0.13733 | 121.4584 | 0.034862 | -0.0451 | 0.001736 | -0.057066 | 0.072888 | 0.044377 | -0.076452 | 121.5474 | 121.4499 | -0.004219 | -0.10637 | 0.06197 | 0.073579 | -0.019749 | 0.024297 | 0.17219 | 0.092229 | 0.13906 | 0.080263 | 0.21022 | 0.18171 | 0.060877 | 121.5657 | 121.4682 | 0.014092 | -0.088054 | 0.080281 | 0.09189 | -0.001438 | 0.042608 | 121.4855 | 121.5672 | -0.066189 | 0.01553
1057.6406 | 121.5912 | -0.11444 | 121.4264 | 0.030283 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.048956 | -0.076452 | 121.5429 | 121.4408 | -0.013376 | -0.10637 | 0.057392 | 0.069001 | -0.006014 | 0.024297 | 0.14472 | 0.07392 | 0.11618 | 0.057375 | 0.19649 | 0.1634 | 0.037989 | 121.5612 | 121.4591 | 0.004935 | -0.088054 | 0.075703 | 0.087312 | 0.012297 | 0.042608 | 121.4855 | 121.5489 | -0.070768 | -0.007362
1059.3281 | 121.5408 | -0.16479 | 121.4722 | 0.044018 | -0.0451 | 0.010893 | -0.057066 | 0.082044 | 0.044377 | -0.071874 | 121.5383 | 121.4408 | 0.000359 | -0.11094 | 0.06197 | 0.059844 | -0.010593 | 0.028875 | 0.20881 | 0.11969 | 0.17569 | 0.10773 | 0.24684 | 0.20917 | 0.092921 | 121.5566 | 121.4591 | 0.01867 | -0.092633 | 0.080281 | 0.078155 | 0.007718 | 0.047186 | 121.4763 | 121.5489 | -0.061611 | 0.010952
1061.0781 | 121.5637 | -0.14648 | 121.4493 | 0.034862 | -0.049678 | 0.010893 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 121.5383 | 121.4408 | -0.004219 | -0.10637 | 0.066548 | 0.064423 | -0.006014 | 0.024297 | 0.18135 | 0.096806 | 0.15738 | 0.093996 | 0.22853 | 0.19086 | 0.07461 | 121.5566 | 121.4591 | 0.014092 | -0.088054 | 0.084859 | 0.082734 | 0.012297 | 0.042608 | 121.4717 | 121.5443 | -0.070767 | 0.001795
1062.7656 | 121.6187 | -0.13275 | 121.4676 | 0.044018 | -0.0451 | 0.001736 | -0.061645 | 0.077466 | 0.044377 | -0.076452 | 121.5383 | 121.4408 | -0.008798 | -0.11094 | 0.057392 | 0.064423 | -0.001436 | 0.028875 | 0.17677 | 0.087651 | 0.13449 | 0.071106 | 0.21022 | 0.17713 | 0.056299 | 121.5566 | 121.4591 | 0.009513 | -0.092633 | 0.075703 | 0.082734 | 0.016875 | 0.047186 | 121.4809 | 121.5397 | -0.06619 | -0.007362
1064.5156 | 121.5271 | -0.15106 | 121.4722 | 0.03944 | -0.040521 | 0.006315 | -0.061645 | 0.072888 | 0.048956 | -0.071874 | 121.5337 | 121.4362 | 0.004937 | -0.11094 | 0.06197 | 0.064423 | -0.006014 | 0.024297 | 0.1905 | 0.11054 | 0.15738 | 0.089417 | 0.22395 | 0.20002 | 0.079188 | 121.552 | 121.4545 | 0.023248 | -0.092633 | 0.080281 | 0.082734 | 0.012297 | 0.042608 | 121.4717 | 121.5397 | -0.057033 | 0.010951
1066.2656 | 121.4951 | -0.16937 | 121.4584 | 0.044018 | -0.0451 | 0.006315 | -0.052488 | 0.077466 | 0.048956 | -0.076452 | 121.5383 | 121.4362 | -0.004219 | -0.1201 | 0.06197 | 0.073579 | -0.006014 | 0.028875 | 0.21339 | 0.12427 | 0.17569 | 0.11688 | 0.24684 | 0.21833 | 0.092921 | 121.5566 | 121.4545 | 0.014092 | -0.10179 | 0.080281 | 0.09189 | 0.012297 | 0.047186 | 121.4763 | 121.5443 | -0.066189 | 0.001795
1067.9375 | 121.4859 | -0.17853 | 121.4401 | 0.044018 | -0.040521 | -0.002842 | -0.052488 | 0.077466 | 0.048956 | -0.071874 | 121.5291 | 121.4225 | -0.004219 | -0.10637 | 0.06197 | 0.069001 | -0.010593 | 0.033454 | 0.22255 | 0.13801 | 0.17569 | 0.12604 | 0.25599 | 0.22748 | 0.10665 | 121.5474 | 121.4408 | 0.014092 | -0.088054 | 0.080281 | 0.087312 | 0.007718 | 0.051765 | 121.4672 | 121.5397 | -0.066189 | 0.006374
1069.6875 | 121.6095 | -0.14648 | 121.4539 | 0.044018 | -0.049678 | 0.010893 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 121.5245 | 121.4225 | 0.000359 | -0.10179 | 0.071126 | 0.082735 | -0.006014 | 0.033454 | 0.1905 | 0.096806 | 0.15738 | 0.093996 | 0.22853 | 0.19086 | 0.070032 | 121.5429 | 121.4408 | 0.01867 | -0.083475 | 0.089437 | 0.10105 | 0.012297 | 0.051765 | 121.4534 | 121.5306 | -0.070767 | 0.006373
1071.4375 | 121.6187 | -0.1236 | 121.4493 | 0.048597 | -0.0451 | 0.001736 | -0.047909 | 0.082044 | 0.048956 | -0.071874 | 121.5337 | 121.427 | -0.004219 | -0.10637 | 0.066548 | 0.064423 | 0.003143 | 0.028875 | 0.17219 | 0.078496 | 0.12533 | 0.075687 | 0.20564 | 0.17255 | 0.051722 | 121.552 | 121.4453 | 0.014092 | -0.088054 | 0.084859 | 0.082734 | 0.021454 | 0.047186 | 121.4672 | 121.5306 | -0.070767 | -0.007362
1073.1875 | 121.6278 | -0.14648 | 121.4355 | 0.034862 | -0.049678 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.076452 | 121.5154 | 121.4179 | -0.008798 | -0.11094 | 0.080283 | 0.082735 | -0.001436 | 0.04261 | 0.18135 | 0.096806 | 0.1528 | 0.089418 | 0.22853 | 0.19086 | 0.070032 | 121.5337 | 121.4362 | 0.009513 | -0.092633 | 0.098594 | 0.10105 | 0.016875 | 0.060921 | 121.4351 | 121.5168 | -0.089081 | -0.007362
1074.875 | 121.5179 | -0.20142 | 121.431 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 121.5017 | 121.4087 | -0.013376 | -0.10637 | 0.075705 | 0.091891 | -0.001436 | 0.051766 | 0.24086 | 0.1609 | 0.19857 | 0.14893 | 0.28346 | 0.24579 | 0.12954 | 121.52 | 121.427 | 0.004935 | -0.088054 | 0.094016 | 0.1102 | 0.016875 | 0.070077 | 121.4259 | 121.5031 | -0.089081 | -0.01194
1076.625 | 121.582 | -0.15564 | 121.376 | 0.03944 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.4879 | 121.3904 | -0.008798 | -0.11094 | 0.066548 | 0.069001 | -0.006014 | 0.038032 | 0.19508 | 0.1197 | 0.15738 | 0.10315 | 0.23311 | 0.20002 | 0.079188 | 121.5062 | 121.4087 | 0.009513 | -0.092633 | 0.084859 | 0.087312 | 0.012297 | 0.056343 | 121.4214 | 121.4939 | -0.075346 | -0.002784
1078.3594 | 121.5775 | -0.16022 | 121.3806 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.4833 | 121.3858 | -0.004219 | -0.11094 | 0.075705 | 0.087313 | 0.003143 | 0.051766 | 0.19966 | 0.1197 | 0.15737 | 0.10773 | 0.23768 | 0.20459 | 0.088343 | 121.5016 | 121.4041 | 0.014092 | -0.092633 | 0.094016 | 0.10562 | 0.021454 | 0.070077 | 121.4076 | 121.4802 | -0.079924 | -0.007362
1080.1094 | 121.55 | -0.16022 | 121.3715 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.044377 | -0.076452 | 121.4742 | 121.3767 | -0.004219 | -0.10179 | 0.084861 | 0.096469 | 0.012299 | 0.047188 | 0.20423 | 0.1197 | 0.16195 | 0.10315 | 0.23311 | 0.20459 | 0.083765 | 121.4925 | 121.395 | 0.014092 | -0.083475 | 0.10317 | 0.11478 | 0.03061 | 0.065499 | 121.3893 | 121.4619 | -0.08908 | -0.016518
1081.7812 | 121.4584 | -0.21057 | 121.3898 | 0.03944 | -0.0451 | 0.006315 | -0.057066 | 0.077466 | 0.048956 | -0.071874 | 121.465 | 121.3675 | -0.004219 | -0.10637 | 0.084861 | 0.096469 | 0.007721 | 0.056344 | 0.25001 | 0.16547 | 0.21689 | 0.15351 | 0.28804 | 0.25953 | 0.1387 | 121.4833 | 121.3858 | 0.014092 | -0.088054 | 0.10317 | 0.11478 | 0.026032 | 0.074655 | 121.3802 | 121.4573 | -0.08908 | -0.01194
1083.5156 | 121.4996 | -0.20142 | 121.3806 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.082044 | 0.039799 | -0.076452 | 121.465 | 121.3721 | -0.008798 | -0.10637 | 0.089439 | 0.10562 | 0.007721 | 0.056344 | 0.24543 | 0.15632 | 0.20315 | 0.14893 | 0.28346 | 0.24122 | 0.12496 | 121.4833 | 121.3904 | 0.009513 | -0.088054 | 0.10775 | 0.12394 | 0.026032 | 0.074655 | 121.3756 | 121.4573 | -0.098237 | -0.016519
1085.25 | 121.582 | -0.16479 | 121.3623 | 0.044018 | -0.0451 | -0.007421 | -0.052488 | 0.086622 | 0.039799 | -0.071874 | 121.4467 | 121.3492 | -0.004219 | -0.11094 | 0.089439 | 0.1102 | 0.012299 | 0.060923 | 0.20881 | 0.11969 | 0.15737 | 0.11231 | 0.25142 | 0.20459 | 0.092921 | 121.465 | 121.3675 | 0.014092 | -0.092633 | 0.10775 | 0.12851 | 0.03061 | 0.079234 | 121.3573 | 121.4344 | -0.093658 | -0.016518
1087 | 121.5408 | -0.2243 | 121.3165 | 0.044018 | -0.0451 | -0.002842 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 121.4147 | 121.3126 | -0.008798 | -0.11094 | 0.10775 | 0.13767 | 0.030613 | 0.079235 | 0.26832 | 0.1792 | 0.22146 | 0.17182 | 0.30177 | 0.26868 | 0.15243 | 121.433 | 121.3309 | 0.009513 | -0.092633 | 0.12606 | 0.15598 | 0.048924 | 0.097546 | 121.3069 | 121.384 | -0.11655 | -0.039411
1088.6875 | 121.5591 | -0.15564 | 121.344 | 0.044018 | -0.035942 | 0.006315 | -0.057066 | 0.072888 | 0.044377 | -0.071874 | 121.4604 | 121.3629 | 0.000359 | -0.10637 | 0.084861 | 0.091891 | 0.003143 | 0.047188 | 0.19966 | 0.1197 | 0.16195 | 0.098574 | 0.22853 | 0.20002 | 0.083766 | 121.4788 | 121.3812 | 0.01867 | -0.088054 | 0.10317 | 0.1102 | 0.021454 | 0.065499 | 121.3756 | 121.4573 | -0.084502 | -0.002784
1090.4375 | 121.4905 | -0.16479 | 121.3806 | 0.03944 | -0.035942 | 0.001736 | -0.057066 | 0.072888 | 0.048956 | -0.071874 | 121.4696 | 121.3767 | 0.004937 | -0.11094 | 0.071126 | 0.073579 | 0.007721 | 0.04261 | 0.20423 | 0.12885 | 0.16653 | 0.10773 | 0.23768 | 0.21375 | 0.092921 | 121.4879 | 121.395 | 0.023248 | -0.092633 | 0.089437 | 0.09189 | 0.026032 | 0.060921 | 121.3985 | 121.4619 | -0.066189 | -0.002784
1092.1719 | 121.5683 | -0.19226 | 121.3211 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 121.4376 | 121.3309 | -0.004219 | -0.11094 | 0.10317 | 0.11478 | 0.021456 | 0.060923 | 0.2317 | 0.14716 | 0.18942 | 0.13977 | 0.26973 | 0.23664 | 0.11581 | 121.4559 | 121.3492 | 0.014092 | -0.092633 | 0.12149 | 0.13309 | 0.039767 | 0.079234 | 121.3344 | 121.4161 | -0.10739 | -0.025675
1093.9062 | 121.3623 | -1.886 | 119.3573 | 0.002813 | -0.08173 | -0.039471 | -0.089116 | 0.031687 | 0.003172 | -0.11765 | 119.2902 | 119.1971 | -0.022532 | -0.10179 | 1.7559 | 1.7904 | 1.8986 | 1.9426 | 1.8888 | 1.8043 | 1.8465 | 1.7969 | 1.9177 | 1.8892 | 1.7683 | 119.3085 | 119.2155 | -0.004221 | -0.083475 | 1.7742 | 1.8087 | 1.9169 | 1.9609 | 117.5343 | 117.3916 | -1.7784 | -1.9211
1095.6562 | 121.3577 | -0.18768 | 121.3394 | 0.044018 | -0.040521 | 0.001736 | -0.047909 | 0.086622 | 0.039799 | -0.071874 | 121.4009 | 121.308 | -0.008798 | -0.10637 | 0.080283 | 0.078157 | 0.003143 | 0.04261 | 0.2317 | 0.14716 | 0.18942 | 0.13977 | 0.27431 | 0.22748 | 0.11581 | 121.4192 | 121.3263 | 0.009513 | -0.088054 | 0.098594 | 0.096468 | 0.021454 | 0.060921 | 121.3206 | 121.3978 | -0.089081 | -0.011941
1097.3906 | 121.3715 | -1.1444 | 120.1859 | 0.030283 | -0.058836 | -0.012 | -0.057066 | 0.063733 | 0.035221 | -0.08103 | 120.7233 | 120.6303 | -0.004219 | -0.11094 | 0.5793 | 0.5909 | 0.54797 | 0.59199 | 1.1747 | 1.0856 | 1.1324 | 1.0873 | 1.2081 | 1.1796 | 1.0634 | 120.7416 | 120.6486 | 0.014092 | -0.092633 | 0.59762 | 0.60921 | 0.56628 | 0.6103 | 120.144 | 120.1753 | -0.58352 | -0.55219
1099.0625 | 121.1975 | -1.9958 | 119.2566 | 0.016548 | -0.063415 | -0.025735 | -0.079959 | 0.054577 | 0.026064 | -0.094765 | 120.0045 | 119.9069 | -0.017954 | -0.10637 | 1.0737 | 1.1311 | 1.1203 | 1.1505 | 2.0124 | 1.9324 | 1.9701 | 1.9159 | 2.0504 | 2.0219 | 1.9011 | 120.0228 | 119.9252 | 0.000357 | -0.088054 | 1.0921 | 1.1494 | 1.1386 | 1.1688 | 118.9307 | 118.8842 | -1.0917 | -1.1382
1100.7969 | 121.0876 | -43.4326 | 77.8061 | 0.034862 | -0.054257 | -0.012 | -0.057066 | 0.06831 | 0.035221 | -0.08103 | 77.4611 | 77.4246 | 0.000359 | -0.10637 | 0.11233 | 0.14683 | 43.5665 | 43.6634 | 43.4675 | 43.3784 | 43.4206 | 43.3756 | 43.5009 | 43.4678 | 43.3516 | 77.4794 | 77.4429 | 0.01867 | -0.088054 | 0.13064 | 0.16514 | 43.5848 | 43.6818 | 77.3488 | 33.8946 | -0.11197 | -43.5661
1102.5469 | 121.2204 | -70.8801 | 50.1984 | 0.01197 | -0.063415 | -0.016578 | -0.084537 | 0.049999 | 0.021485 | -0.099343 | 47.6643 | 47.6623 | -0.008798 | -0.10637 | 0.20389 | 0.24754 | 73.2757 | 73.3758 | 70.8921 | 70.8167 | 70.8635 | 70.7956 | 70.9301 | 70.9016 | 70.7808 | 47.6826 | 47.6806 | 0.009513 | -0.088054 | 0.2222 | 0.26586 | 73.294 | 73.3941 | 47.4604 | -25.6114 | -0.21269 | -73.2845
1104.3125 | 121.0556 | -67.4377 | 53.5629 | -0.047549 | -0.12752 | -0.094414 | -0.14406 | -0.014093 | -0.042612 | -0.15886 | 58.3688 | 58.2577 | -0.027111 | -0.10179 | 0.31835 | 0.4032 | 62.4157 | 62.498 | 67.3902 | 67.3102 | 67.3433 | 67.2937 | 67.4237 | 67.3951 | 67.2789 | 58.3871 | 58.276 | -0.0088 | -0.083475 | 0.33666 | 0.42151 | 62.434 | 62.5164 | 58.0504 | -4.0469 | -0.34546 | -62.4428
1106 | 121.0098 | -51.7868 | 69.1269 | -0.061284 | -0.14583 | -0.11273 | -0.16237 | -0.027827 | -0.060926 | -0.18633 | 69.6822 | 69.5994 | -0.045424 | -0.092628 | 0.54726 | 0.64126 | 50.7775 | 51.0618 | 51.7255 | 51.641 | 51.6741 | 51.6244 | 51.759 | 51.7259 | 51.6005 | 69.7006 | 69.6177 | -0.027113 | -0.074317 | 0.56557 | 0.65957 | 50.7958 | 51.0801 | 69.135 | 18.9048 | -0.59268 | -50.8229
1107.6719 | 121.051 | -57.7057 | 63.0569 | -0.12538 | -0.1962 | -0.15851 | -0.21274 | -0.073606 | -0.11587 | -0.22753 | 69.7921 | 69.7368 | -0.063737 | -0.092628 | 0.30919 | 0.39404 | 50.8782 | 51.0251 | 57.5803 | 57.5095 | 57.5472 | 57.493 | 57.6321 | 57.5898 | 57.4782 | 69.8104 | 69.7551 | -0.045426 | -0.074317 | 0.3275 | 0.41235 | 50.8965 | 51.0435 | 69.4829 | 18.9139 | -0.37293 | -50.9419
1109.4062 | 121.0648 | -34.7168 | 86.142 | -0.12538 | -0.20078 | -0.16767 | -0.22189 | -0.082762 | -0.11587 | -0.23669 | 86.6227 | 86.5319 | -0.095785 | -0.08347 | 0.2863 | 0.37573 | 33.9702 | 34.1408 | 34.5914 | 34.516 | 34.5491 | 34.4949 | 34.634 | 34.6009 | 34.4801 | 86.641 | 86.5502 | -0.077474 | -0.065159 | 0.30461 | 0.39404 | 33.9885 | 34.1592 | 86.3364 | 52.6525 | -0.38209 | -34.066
1111.1406 | 120.9045 | -46.8109 | 73.938 | -0.029236 | -0.11378 | -0.066943 | -0.11659 | 0.013375 | -0.01972 | -0.14512 | 74.9704 | 74.8879 | -0.091207 | -0.078891 | 0.59304 | 0.56801 | 45.5947 | 45.7007 | 46.7817 | 46.6971 | 46.744 | 46.6943 | 46.8243 | 46.7912 | 46.6658 | 74.9887 | 74.9062 | -0.072896 | -0.06058 | 0.61135 | 0.58632 | 45.613 | 45.719 | 74.3774 | 29.3757 | -0.68424 | -45.6859
1112.8125 | 120.8496 | -36.9736 | 82.8644 | -0.020079 | -0.095467 | -0.062364 | -0.11201 | 0.013375 | -0.010563 | -0.13139 | 79.6405 | 79.8468 | -0.10494 | -0.078891 | 0.37329 | 0.31164 | 40.8973 | 41.0676 | 36.9535 | 36.8781 | 36.9112 | 36.8616 | 36.9869 | 36.963 | 36.8422 | 79.6588 | 79.8651 | -0.086631 | -0.06058 | 0.3916 | 0.32995 | 40.9156 | 41.0859 | 79.2672 | 38.7432 | -0.47823 | -41.0022
1114.5469 | 120.845 | -60.6995 | 59.9899 | -0.056706 | -0.14125 | -0.089836 | -0.14864 | -0.023249 | -0.056347 | -0.16801 | 59.0601 | 59.0544 | -0.12326 | -0.078891 | 0.44196 | 0.53138 | 61.3947 | 61.5 | 60.6428 | 60.5582 | 60.6096 | 60.5508 | 60.6762 | 60.6431 | 60.5314 | 59.0784 | 59.0727 | -0.10494 | -0.06058 | 0.46027 | 0.5497 | 61.4131 | 61.5183 | 58.6182 | -2.3346 | -0.56521 | -61.518
1116.2969 | 120.9686 | -43.721 | 77.2339 | -0.024657 | -0.1092 | -0.062364 | -0.12116 | 0.008797 | -0.01972 | -0.13597 | 78.1799 | 78.2213 | -0.12326 | -0.051417 | 0.26341 | 0.32079 | 42.4814 | 42.5967 | 43.6964 | 43.6118 | 43.6586 | 43.5998 | 43.7298 | 43.7013 | 43.585 | 78.1982 | 78.2396 | -0.10494 | -0.033106 | 0.28172 | 0.33911 | 42.4997 | 42.615 | 77.9165 | 35.6985 | -0.38666 | -42.6047
1117.9844 | 121.0098 | -59.6695 | 61.116 | -0.065863 | -0.14583 | -0.10815 | -0.16695 | -0.027827 | -0.065504 | -0.17717 | 60.8915 | 60.7898 | -0.036267 | -0.10179 | 0.47401 | 0.53138 | 59.6366 | 59.7237 | 59.6036 | 59.5237 | 59.5613 | 59.5025 | 59.6417 | 59.604 | 59.4923 | 60.9098 | 60.8081 | -0.017956 | -0.083475 | 0.49232 | 0.5497 | 59.655 | 59.742 | 60.4175 | 1.2549 | -0.51027 | -59.6729
1119.7344 | 120.9732 | -33.11 | 87.9822 | -0.061284 | -0.14125 | -0.098993 | -0.15779 | -0.018671 | -0.056347 | -0.17259 | 82.9828 | 82.9787 | -0.017954 | -0.10179 | 0.19016 | 0.24297 | 37.6879 | 37.9178 | 33.0488 | 32.9688 | 33.0111 | 32.9523 | 33.0914 | 33.0537 | 32.9375 | 83.0011 | 82.997 | 0.000357 | -0.083475 | 0.20847 | 0.26128 | 37.7062 | 37.9361 | 82.7926 | 45.2949 | -0.20811 | -37.7058
1121.4844 | 121.0144 | -35.9894 | 84.8053 | -0.1849 | -0.2603 | -0.21804 | -0.28141 | -0.1377 | -0.17081 | -0.29163 | 90.3633 | 90.2636 | 0.000359 | -0.10637 | 0.24968 | 0.32079 | 30.2663 | 30.3501 | 35.8045 | 35.7291 | 35.7713 | 35.708 | 35.8517 | 35.8186 | 35.6978 | 90.3816 | 90.2819 | 0.01867 | -0.088054 | 0.26799 | 0.33911 | 30.2846 | 30.3684 | 90.1136 | 60.097 | -0.24932 | -30.2659
1123.1719 | 120.7855 | -25.0717 | 95.7825 | -0.14369 | -0.21452 | -0.17683 | -0.23105 | -0.096496 | -0.1296 | -0.24584 | 92.6159 | 92.553 | -0.036267 | -0.10179 | 0.41449 | 0.49934 | 27.9862 | 28.0793 | 24.928 | 24.8572 | 24.8949 | 24.8407 | 24.9752 | 24.9421 | 24.8259 | 92.6342 | 92.5713 | -0.017956 | -0.083475 | 0.4328 | 0.51765 | 28.0046 | 28.0977 | 92.2014 | 64.6297 | -0.45076 | -28.0225
1124.8594 | 120.8725 | -26.4313 | 94.2856 | -0.23069 | -0.31525 | -0.27298 | -0.33636 | -0.19721 | -0.22575 | -0.35572 | 84.1366 | 84.0685 | -0.040846 | -0.097207 | 0.73496 | 0.80607 | 36.1266 | 36.288 | 26.2006 | 26.116 | 26.1583 | 26.0949 | 26.2341 | 26.2055 | 26.0756 | 84.1549 | 84.0868 | -0.022535 | -0.078896 | 0.75327 | 0.82438 | 36.1449 | 36.3063 | 83.4016 | 48.0099 | -0.77581 | -36.1675
1126.5938 | 120.845 | -41.3315 | 79.1428 | -0.30394 | -0.38393 | -0.35082 | -0.40961 | -0.25215 | -0.299 | -0.42439 | 81.1514 | 81.0464 | -0.095785 | -0.08347 | 0.71207 | 0.73282 | 39.098 | 39.186 | 41.0275 | 40.9475 | 40.9807 | 40.9219 | 41.0793 | 41.0325 | 40.9071 | 81.1697 | 81.0648 | -0.077474 | -0.065159 | 0.73038 | 0.75113 | 39.1163 | 39.2043 | 80.4393 | 42.0534 | -0.80786 | -39.1938
1128.3438 | 120.0714 | -81.6879 | 38.0173 | -0.91744 | -0.98376 | -0.96893 | -1.0094 | -0.86559 | -0.92166 | -1.0333 | 43.7725 | 43.5414 | -0.15988 | -0.10179 | 3.1614 | 3.1912 | 74.7728 | 74.7996 | 80.7705 | 80.7042 | 80.719 | 80.6785 | 80.8223 | 80.7663 | 80.6546 | 43.7908 | 43.5597 | -0.14157 | -0.083475 | 3.1797 | 3.2096 | 74.7911 | 74.8179 | 40.6111 | -31.0003 | -3.3213 | -74.9327
1130.0469 | 120.9229 | -0.32044 | 120.6848 | 0.053175 | -0.031363 | 0.010893 | -0.043331 | 0.095778 | 0.058113 | -0.062717 | 120.737 | 120.6441 | 0.055298 | -0.1201 | 0.057392 | 0.055266 | 0.10845 | 0.15706 | 0.37361 | 0.28907 | 0.33133 | 0.2771 | 0.41621 | 0.37855 | 0.25772 | 120.7554 | 120.6624 | 0.073609 | -0.10179 | 0.075703 | 0.073577 | 0.12676 | 0.17538 | 120.6797 | 120.6286 | -0.002094 | -0.053148
1131.8125 | 121.0785 | -0.33875 | 120.726 | 0.057754 | -0.031363 | 0.010893 | -0.043331 | 0.095778 | 0.058113 | -0.058139 | 120.7874 | 120.699 | 0.046142 | -0.12468 | 0.052814 | 0.064423 | 0.12676 | 0.16164 | 0.3965 | 0.30738 | 0.34964 | 0.29541 | 0.43452 | 0.39686 | 0.28061 | 120.8057 | 120.7173 | 0.064453 | -0.10637 | 0.071125 | 0.082734 | 0.14507 | 0.17995 | 120.7346 | 120.6606 | -0.006672 | -0.080617
1133.5469 | 120.9 | -3.7491 | 117.2195 | 0.18595 | 0.10142 | 0.14825 | 0.089445 | 0.23312 | 0.19089 | 0.07005 | 117.262 | 117.1825 | 1.9141 | 1.8077 | 0.24052 | 0.28875 | 3.3133 | 3.3572 | 3.935 | 3.8505 | 3.8973 | 3.8385 | 3.9822 | 3.94 | 3.8191 | 117.2803 | 117.2008 | 1.9324 | 1.826 | 0.25883 | 0.30706 | 3.3316 | 3.3755 | 117.0214 | 113.9486 | 1.6736 | -1.3992
1135.2344 | 121.0281 | -0.5127 | 120.6757 | 0.071489 | -0.008469 | 0.024629 | -0.025017 | 0.10493 | 0.071848 | -0.039826 | 120.2105 | 120.1358 | 0.39867 | 0.25996 | 0.084861 | 0.10105 | 0.64412 | 0.69729 | 0.58418 | 0.50423 | 0.53732 | 0.48768 | 0.61763 | 0.58454 | 0.47287 | 120.2288 | 120.1541 | 0.41698 | 0.27827 | 0.10317 | 0.11936 | 0.66243 | 0.7156 | 120.1257 | 119.5664 | 0.31381 | -0.24545
1136.9844 | 121.0693 | -0.64545 | 120.5338 | 0.071489 | -0.022205 | 0.029208 | -0.034174 | 0.10036 | 0.067269 | -0.048983 | 120.5493 | 120.4563 | 0.19723 | 0.13174 | 0.071126 | 0.073579 | 0.34652 | 0.39513 | 0.71694 | 0.62324 | 0.67466 | 0.61127 | 0.7458 | 0.71272 | 0.59646 | 120.5676 | 120.4746 | 0.21554 | 0.15005 | 0.089437 | 0.09189 | 0.36483 | 0.41344 | 120.4782 | 120.2028 | 0.1261 | -0.1493
1138.6719 | 121.1746 | -0.74616 | 120.3644 | 0.080646 | -0.008469 | 0.029208 | -0.01586 | 0.10036 | 0.076426 | -0.039826 | 120.4806 | 120.3831 | 0.19265 | 0.12717 | 0.071126 | 0.087313 | 0.41978 | 0.45922 | 0.8268 | 0.73769 | 0.77536 | 0.7303 | 0.84651 | 0.82258 | 0.70633 | 120.499 | 120.4014 | 0.21096 | 0.14548 | 0.089437 | 0.10562 | 0.43809 | 0.47754 | 120.4095 | 120.0609 | 0.12152 | -0.22713
1140.4219 | 121.138 | -4.097 | 116.9174 | 0.16764 | 0.087686 | 0.12536 | 0.071132 | 0.2148 | 0.17257 | 0.047159 | 117.1063 | 116.9902 | 1.8179 | 1.6932 | 0.22678 | 0.2979 | 3.5422 | 3.5815 | 4.2646 | 4.1847 | 4.2223 | 4.1681 | 4.3118 | 4.2696 | 4.1441 | 117.1246 | 117.0085 | 1.8362 | 1.7115 | 0.2451 | 0.31622 | 3.5605 | 3.5998 | 116.8795 | 113.5641 | 1.5912 | -1.7243
1142.1562 | 121.0785 | -2.243 | 118.8492 | 0.15848 | 0.069371 | 0.10704 | 0.061975 | 0.20107 | 0.16799 | 0.028846 | 119.1575 | 119.0781 | 0.56807 | 0.45686 | 0.11233 | 0.14225 | 1.5964 | 1.645 | 2.4015 | 2.3124 | 2.3501 | 2.305 | 2.4441 | 2.411 | 2.2719 | 119.1758 | 119.0964 | 0.58638 | 0.47517 | 0.13064 | 0.16056 | 1.6147 | 1.6633 | 119.0451 | 117.561 | 0.45574 | -1.0284
1143.9062 | 121.0785 | -1.2177 | 119.9341 | 0.13101 | 0.03274 | 0.074994 | 0.025347 | 0.1736 | 0.12221 | 0.010533 | 119.9999 | 119.9069 | 0.22927 | 0.1638 | 0.089439 | 0.10562 | 0.86388 | 0.90789 | 1.3487 | 1.2504 | 1.2926 | 1.243 | 1.3913 | 1.3399 | 1.2282 | 120.0182 | 119.9252 | 0.24758 | 0.18211 | 0.10775 | 0.12394 | 0.88219 | 0.9262 | 119.9105 | 119.136 | 0.13983 | -0.63461
1145.6562 | 121.0007 | -5.9875 | 114.6973 | 0.63005 | 0.53183 | 0.57864 | 0.51982 | 0.68634 | 0.63041 | 0.49582 | 115.2474 | 115.1495 | 1.1037 | 1.0109 | 0.30461 | 0.38947 | 5.2271 | 5.28 | 6.6176 | 6.5194 | 6.5662 | 6.5074 | 6.6739 | 6.618 | 6.4834 | 115.2657 | 115.1678 | 1.122 | 1.0292 | 0.32292 | 0.40778 | 5.2454 | 5.2984 | 114.9428 | 110.0203 | 0.79911 | -4.1234
1147.3438 | 121.0785 | -1.5152 | 119.6365 | 0.13101 | 0.046477 | 0.079572 | 0.029925 | 0.16445 | 0.12221 | 0.005955 | 119.6611 | 119.568 | 0.28879 | 0.20959 | 0.098596 | 0.11478 | 1.1889 | 1.2238 | 1.6462 | 1.5617 | 1.5948 | 1.5451 | 1.6796 | 1.6374 | 1.5212 | 119.6794 | 119.5863 | 0.3071 | 0.2279 | 0.11691 | 0.13309 | 1.2073 | 1.2421 | 119.5625 | 118.4722 | 0.1902 | -0.90015
1149.0781 | 121.106 | -2.536 | 118.5562 | 0.28667 | 0.18842 | 0.23525 | 0.19017 | 0.32468 | 0.29161 | 0.16161 | 118.608 | 118.5057 | 0.32999 | 0.24164 | 0.1398 | 0.1743 | 2.1916 | 2.2218 | 2.8227 | 2.7244 | 2.7713 | 2.7262 | 2.8607 | 2.8276 | 2.6976 | 118.6264 | 118.5241 | 0.34831 | 0.25995 | 0.15811 | 0.19261 | 2.2099 | 2.2401 | 118.4682 | 116.4164 | 0.1902 | -1.8616
1150.8281 | 121.0876 | -1.4191 | 119.751 | 0.1539 | 0.051056 | 0.10704 | 0.057396 | 0.19192 | 0.14968 | 0.033424 | 119.5604 | 119.4673 | 0.31626 | 0.2279 | 0.094017 | 0.11478 | 1.2759 | 1.3108 | 1.573 | 1.4701 | 1.5261 | 1.4765 | 1.611 | 1.5687 | 1.4525 | 119.5787 | 119.4856 | 0.33457 | 0.24621 | 0.11233 | 0.13309 | 1.2942 | 1.3291 | 119.4664 | 118.2844 | 0.22224 | -0.95967
1152.5781 | 120.9549 | -5.1407 | 115.9195 | 0.73078 | 0.61883 | 0.66563 | 0.61139 | 0.76874 | 0.72198 | 0.58281 | 116.2684 | 116.1339 | 0.45361 | 0.35154 | 0.24052 | 0.31622 | 4.3709 | 4.4148 | 5.8715 | 5.7595 | 5.8063 | 5.7521 | 5.9094 | 5.8627 | 5.7235 | 116.2867 | 116.1522 | 0.47192 | 0.36985 | 0.25883 | 0.33453 | 4.3892 | 4.4331 | 116.0279 | 111.8975 | 0.21309 | -3.9173
1154.25 | 121.0968 | -3.36 | 117.6086 | 0.20426 | 0.12432 | 0.15741 | 0.10776 | 0.24685 | 0.20004 | 0.088362 | 116.9781 | 116.8803 | 1.47 | 1.3406 | 0.20847 | 0.27959 | 3.5972 | 3.6411 | 3.5642 | 3.4843 | 3.5174 | 3.4677 | 3.6068 | 3.56 | 3.4483 | 116.9964 | 116.8986 | 1.4883 | 1.3589 | 0.22678 | 0.2979 | 3.6155 | 3.6594 | 116.7696 | 113.3809 | 1.2615 | -2.1272
1156 | 120.9778 | -5.2505 | 115.8966 | 0.94138 | 0.83403 | 0.88083 | 0.82658 | 0.99306 | 0.94174 | 0.81171 | 115.4992 | 115.3921 | 0.42614 | 0.31949 | 0.27257 | 0.35284 | 5.0531 | 5.1152 | 6.1919 | 6.0846 | 6.1314 | 6.0771 | 6.2436 | 6.1923 | 6.0623 | 115.5176 | 115.4105 | 0.44445 | 0.3378 | 0.29088 | 0.37115 | 5.0714 | 5.1335 | 115.2267 | 110.4461 | 0.15357 | -4.627
1157.6875 | 121.0281 | -6.1066 | 114.8071 | 0.77198 | 0.67378 | 0.72515 | 0.66634 | 0.82367 | 0.77692 | 0.64232 | 114.5652 | 114.4626 | 1.3372 | 1.2444 | 0.33208 | 0.43067 | 5.7948 | 5.8477 | 6.8785 | 6.7803 | 6.8317 | 6.7729 | 6.9302 | 6.8835 | 6.7489 | 114.5835 | 114.481 | 1.3555 | 1.2628 | 0.35039 | 0.44898 | 5.8131 | 5.866 | 114.2331 | 108.7704 | 1.0051 | -4.4576
1159.4219 | 120.7718 | -11.0092 | 109.6207 | 0.69415 | 0.60509 | 0.63816 | 0.59308 | 0.74127 | 0.69909 | 0.56907 | 110.7559 | 110.6714 | 3.7042 | 3.5935 | 0.69834 | 0.75113 | 9.1828 | 9.2493 | 11.7034 | 11.6143 | 11.6474 | 11.6023 | 11.7505 | 11.7083 | 11.5783 | 110.7742 | 110.6897 | 3.7225 | 3.6118 | 0.71665 | 0.76944 | 9.2011 | 9.2676 | 110.0576 | 101.5731 | 3.0059 | -5.4786
1161.1562 | 120.6253 | -12.7808 | 107.9315 | 2.2416 | 2.1253 | 2.172 | 2.1131 | 2.339 | 2.2374 | 2.0936 | 110.2111 | 110.1036 | 0.53602 | 0.42938 | 0.69834 | 0.7786 | 9.5216 | 9.6018 | 15.0224 | 14.906 | 14.9528 | 14.8939 | 15.1197 | 15.0182 | 14.8744 | 110.2294 | 110.1219 | 0.55433 | 0.44769 | 0.71665 | 0.79691 | 9.5399 | 9.6201 | 109.5127 | 100.6895 | -0.16232 | -8.9856
1162.8906 | 120.5292 | -8.3588 | 111.9095 | 0.30956 | 0.21589 | 0.24898 | 0.21307 | 0.33383 | 0.30535 | 0.1845 | 113.5259 | 113.4095 | 2.5917 | 2.5495 | 0.46943 | 0.53596 | 5.7628 | 5.8294 | 8.6683 | 8.5747 | 8.6077 | 8.5718 | 8.6926 | 8.6641 | 8.5433 | 113.5442 | 113.4278 | 2.61 | 2.5678 | 0.48774 | 0.55427 | 5.7811 | 5.8477 | 113.0565 | 107.7632 | 2.1222 | -3.1711
1164.5781 | 120.7947 | -2.9755 | 117.6361 | 0.55222 | 0.45857 | 0.50538 | 0.45572 | 0.59935 | 0.55258 | 0.42715 | 117.7015 | 117.5991 | 0.34831 | 0.25996 | 0.19931 | 0.24754 | 2.5304 | 2.5743 | 3.5277 | 3.434 | 3.4808 | 3.4312 | 3.5748 | 3.528 | 3.4026 | 117.7198 | 117.6174 | 0.36662 | 0.27827 | 0.21763 | 0.26586 | 2.5487 | 2.5927 | 117.5022 | 115.1711 | 0.14899 | -2.1821
1166.3281 | 120.1538 | -25.2869 | 94.8807 | 0.73993 | 0.63714 | 0.67479 | 0.62513 | 0.76874 | 0.73114 | 0.6057 | 97.7805 | 97.5577 | 7.5499 | 7.4719 | 1.3713 | 1.4653 | 20.4136 | 20.5299 | 26.0268 | 25.924 | 25.9617 | 25.912 | 26.0556 | 26.018 | 25.8926 | 97.7988 | 97.576 | 7.5683 | 7.4902 | 1.3896 | 1.4836 | 20.4319 | 20.5482 | 96.4091 | 77.3669 | 6.1786 | -12.8637
1168.0781 | 120.8038 | -0.14648 | 120.6757 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 0.20358 | 0.25779 | 0.000359 | -0.10637 | 0.043657 | 0.050688 | -0.001436 | 0.038032 | 0.18592 | 0.10596 | 0.14364 | 0.093996 | 0.22395 | 0.19086 | 0.07461 | 0.22189 | 0.2761 | 0.01867 | -0.088054 | 0.061968 | 0.068999 | 0.016875 | 0.056343 | 0.15992 | 0.20501 | -0.043298 | 0.001795
1169.8281 | 120.9549 | -0.14191 | 120.7397 | 0.044018 | -0.035942 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.067295 | 0.18526 | 0.2349 | -0.004219 | -0.11552 | 0.043657 | 0.041532 | -0.006014 | 0.047188 | 0.18593 | 0.10597 | 0.14364 | 0.089419 | 0.22395 | 0.18628 | 0.074612 | 0.20358 | 0.25321 | 0.014092 | -0.097212 | 0.061968 | 0.059843 | 0.012297 | 0.065499 | 0.14161 | 0.19128 | -0.047876 | 0.001795
1171.5781 | 120.8633 | -0.20599 | 120.8679 | 0.048597 | -0.026784 | -0.007421 | -0.052488 | 0.077466 | 0.053534 | -0.071874 | 0.18069 | 0.22574 | 0.000359 | -0.11094 | 0.048236 | 0.041532 | -0.001436 | 0.04261 | 0.25459 | 0.17921 | 0.19857 | 0.15351 | 0.28346 | 0.25953 | 0.13412 | 0.199 | 0.24405 | 0.01867 | -0.092633 | 0.066547 | 0.059843 | 0.016875 | 0.060921 | 0.13245 | 0.18212 | -0.047877 | 0.001795
1173.25 | 121.0236 | -0.13275 | 120.8359 | 0.03944 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 0.17153 | 0.22574 | -0.004219 | -0.10637 | 0.043657 | 0.041532 | 0.003143 | 0.04261 | 0.17219 | 0.096809 | 0.13449 | 0.080263 | 0.21022 | 0.17713 | 0.060877 | 0.18984 | 0.24405 | 0.014092 | -0.088054 | 0.061968 | 0.059843 | 0.021454 | 0.060921 | 0.12787 | 0.16839 | -0.047876 | -0.007362
1174.9844 | 121.0373 | -0.15106 | 120.8633 | 0.048597 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.039799 | -0.071874 | 0.17153 | 0.22574 | -0.008798 | -0.10637 | 0.039079 | 0.041532 | 0.003143 | 0.038032 | 0.19966 | 0.11054 | 0.1528 | 0.098574 | 0.23311 | 0.19086 | 0.079188 | 0.18984 | 0.24405 | 0.009513 | -0.088054 | 0.05739 | 0.059843 | 0.021454 | 0.056343 | 0.13245 | 0.16839 | -0.047877 | -0.011941
1176.6719 | 121.0007 | -0.1831 | 120.9183 | 0.03944 | -0.040521 | -0.002842 | -0.057066 | 0.077466 | 0.048956 | -0.067295 | 0.16695 | 0.22574 | -0.013376 | -0.11552 | 0.043657 | 0.041532 | 0.003143 | 0.038032 | 0.22254 | 0.14258 | 0.18026 | 0.12604 | 0.26057 | 0.23206 | 0.11581 | 0.18526 | 0.24405 | 0.004935 | -0.097212 | 0.061968 | 0.059843 | 0.021454 | 0.056343 | 0.12329 | 0.16381 | -0.057033 | -0.016519
1178.4219 | 121.0373 | -0.16479 | 120.9595 | 0.044018 | -0.035942 | 0.001736 | -0.052488 | 0.082044 | 0.053534 | -0.071874 | 0.16237 | 0.21658 | 0.000359 | -0.10637 | 0.048236 | 0.050688 | -0.001436 | 0.038032 | 0.20881 | 0.12885 | 0.16653 | 0.11231 | 0.24684 | 0.21833 | 0.092921 | 0.18068 | 0.23489 | 0.01867 | -0.088054 | 0.066547 | 0.068999 | 0.016875 | 0.056343 | 0.11414 | 0.16381 | -0.047877 | 0.001795
1180.1562 | 121.0007 | -0.1831 | 120.9641 | 0.03944 | -0.035942 | 0.006315 | -0.052488 | 0.082044 | 0.048956 | -0.071874 | 0.16237 | 0.21658 | 0.000359 | -0.10637 | 0.048236 | 0.041532 | -0.001436 | 0.038032 | 0.22254 | 0.14716 | 0.18942 | 0.13062 | 0.26515 | 0.23206 | 0.11123 | 0.18068 | 0.23489 | 0.01867 | -0.088054 | 0.066547 | 0.059843 | 0.016875 | 0.056343 | 0.11414 | 0.16381 | -0.047877 | 0.001795
1181.9219 | 121.0052 | -0.19226 | 120.9824 | 0.03944 | -0.035942 | -0.002842 | -0.057066 | 0.0912 | 0.048956 | -0.071874 | 0.15779 | 0.23032 | -0.013376 | -0.11552 | 0.043657 | 0.04611 | 0.003143 | 0.04261 | 0.2317 | 0.15632 | 0.18942 | 0.13519 | 0.28346 | 0.24122 | 0.12039 | 0.1761 | 0.24863 | 0.004935 | -0.097212 | 0.061968 | 0.064421 | 0.021454 | 0.060921 | 0.11414 | 0.15465 | -0.057033 | -0.016519
1183.6562 | 121.0876 | -0.1831 | 120.9915 | 0.03944 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 0.15321 | 0.20742 | -0.008798 | -0.10179 | 0.052814 | 0.04611 | -0.001436 | 0.038032 | 0.22254 | 0.14258 | 0.18942 | 0.13062 | 0.26057 | 0.22748 | 0.10665 | 0.17153 | 0.22573 | 0.009513 | -0.083475 | 0.071125 | 0.064421 | 0.016875 | 0.056343 | 0.1004 | 0.15465 | -0.061612 | -0.007362
1185.3438 | 121.17 | -0.14191 | 120.9824 | 0.03944 | -0.035942 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.071874 | 0.15779 | 0.21658 | -0.008798 | -0.10637 | 0.052814 | 0.04611 | -0.001436 | 0.038032 | 0.18135 | 0.10597 | 0.14364 | 0.093998 | 0.22395 | 0.18171 | 0.070033 | 0.1761 | 0.23489 | 0.009513 | -0.088054 | 0.071125 | 0.064421 | 0.016875 | 0.056343 | 0.10498 | 0.15923 | -0.061612 | -0.007362
1187.0938 | 121.1746 | -0.15564 | 120.9915 | 0.03944 | -0.040521 | 0.006315 | -0.052488 | 0.086622 | 0.048956 | -0.076452 | 0.16237 | 0.212 | -0.008798 | -0.11552 | 0.043657 | 0.04611 | 0.003143 | 0.038032 | 0.19508 | 0.11512 | 0.16195 | 0.10315 | 0.24226 | 0.2046 | 0.079188 | 0.18068 | 0.23031 | 0.009513 | -0.097212 | 0.061968 | 0.064421 | 0.021454 | 0.056343 | 0.11871 | 0.15923 | -0.052455 | -0.011941
1188.7812 | 121.1288 | -0.17853 | 121.0144 | 0.034862 | -0.0451 | 0.001736 | -0.052488 | 0.06831 | 0.053534 | -0.067295 | 0.15779 | 0.212 | -0.004219 | -0.10637 | 0.043657 | 0.036954 | 0.003143 | 0.047188 | 0.21339 | 0.13343 | 0.18026 | 0.12604 | 0.24684 | 0.23206 | 0.11123 | 0.1761 | 0.23031 | 0.014092 | -0.088054 | 0.061968 | 0.055265 | 0.021454 | 0.065499 | 0.11414 | 0.15465 | -0.047876 | -0.007362
1190.5156 | 121.0876 | -0.19226 | 121.0556 | 0.053175 | -0.035942 | 0.001736 | -0.047909 | 0.086622 | 0.048956 | -0.067295 | 0.15779 | 0.212 | -0.004219 | -0.11094 | 0.048236 | 0.04611 | -0.001436 | 0.04261 | 0.24544 | 0.15632 | 0.194 | 0.14435 | 0.27888 | 0.24122 | 0.12497 | 0.1761 | 0.23031 | 0.014092 | -0.092633 | 0.066547 | 0.064421 | 0.016875 | 0.060921 | 0.10956 | 0.15923 | -0.052455 | -0.002783
1192.2656 | 121.2204 | -0.13733 | 120.9869 | 0.03944 | -0.040521 | -0.002842 | -0.066223 | 0.086622 | 0.044377 | -0.067295 | 0.15321 | 0.21658 | -0.004219 | -0.10637 | 0.043657 | 0.041532 | 0.003143 | 0.038032 | 0.17677 | 0.096808 | 0.13449 | 0.071106 | 0.22395 | 0.18171 | 0.070034 | 0.17153 | 0.23489 | 0.014092 | -0.088054 | 0.061968 | 0.059843 | 0.021454 | 0.056343 | 0.10956 | 0.15007 | -0.047876 | -0.007362
1194.0156 | 121.2158 | -0.14648 | 121.0098 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 0.14864 | 0.212 | -0.004219 | -0.11094 | 0.048236 | 0.050688 | 0.003143 | 0.038032 | 0.1905 | 0.10596 | 0.1528 | 0.093996 | 0.22395 | 0.19086 | 0.07461 | 0.16695 | 0.23031 | 0.014092 | -0.092633 | 0.066547 | 0.068999 | 0.021454 | 0.056343 | 0.1004 | 0.14549 | -0.052455 | -0.007362
1195.7031 | 121.1838 | -0.16479 | 121.0236 | 0.048597 | -0.035942 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.08103 | 0.14864 | 0.212 | -0.004219 | -0.10637 | 0.048236 | 0.04611 | -0.001436 | 0.047188 | 0.21339 | 0.12885 | 0.16653 | 0.10773 | 0.24684 | 0.20459 | 0.083765 | 0.16695 | 0.23031 | 0.014092 | -0.088054 | 0.066547 | 0.064421 | 0.016875 | 0.065499 | 0.1004 | 0.15007 | -0.052455 | -0.002783
1197.4219 | 121.1472 | -0.18768 | 121.0373 | 0.044018 | -0.040521 | -0.002842 | -0.043331 | 0.086622 | 0.048956 | -0.071874 | 0.14406 | 0.22116 | 0.000359 | -0.11094 | 0.043657 | 0.04611 | 0.003143 | 0.04261 | 0.2317 | 0.14716 | 0.18484 | 0.14435 | 0.27431 | 0.23664 | 0.11581 | 0.16237 | 0.23947 | 0.01867 | -0.092633 | 0.061968 | 0.064421 | 0.021454 | 0.060921 | 0.1004 | 0.14091 | -0.043298 | -0.002784
1199.1562 | 121.1151 | -0.1831 | 121.0922 | 0.048597 | -0.040521 | 0.006315 | -0.052488 | 0.082044 | 0.048956 | -0.076452 | 0.14864 | 0.20742 | -0.004219 | -0.10637 | 0.043657 | 0.041532 | 0.003143 | 0.047188 | 0.2317 | 0.14258 | 0.18942 | 0.13062 | 0.26515 | 0.23206 | 0.10665 | 0.16695 | 0.22573 | 0.014092 | -0.088054 | 0.061968 | 0.059843 | 0.021454 | 0.065499 | 0.10498 | 0.14549 | -0.047876 | -0.007362
1200.8438 | 121.2524 | -0.15106 | 121.0419 | 0.03944 | -0.035942 | 0.001736 | -0.047909 | 0.072888 | 0.048956 | -0.071874 | 0.14406 | 0.20742 | -0.004219 | -0.11094 | 0.052814 | 0.04611 | 0.007721 | 0.04261 | 0.1905 | 0.11512 | 0.1528 | 0.10315 | 0.22395 | 0.20002 | 0.079188 | 0.16237 | 0.22573 | 0.014092 | -0.092633 | 0.071125 | 0.064421 | 0.026032 | 0.060921 | 0.091244 | 0.13634 | -0.057033 | -0.01194
1202.5938 | 121.2296 | -0.15106 | 121.0556 | 0.03944 | -0.031363 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.067295 | 0.15321 | 0.20742 | 0.000359 | -0.11094 | 0.043657 | 0.04611 | 0.003143 | 0.047188 | 0.1905 | 0.1197 | 0.1528 | 0.098574 | 0.23311 | 0.19544 | 0.083767 | 0.17153 | 0.22573 | 0.01867 | -0.092633 | 0.061968 | 0.064421 | 0.021454 | 0.065499 | 0.10956 | 0.15007 | -0.043298 | -0.002784
1204.2969 | 121.257 | -0.15106 | 121.0739 | 0.048597 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.071874 | 0.14406 | 0.20742 | -0.004219 | -0.10637 | 0.052814 | 0.050688 | 0.003143 | 0.04261 | 0.19966 | 0.11054 | 0.15738 | 0.093996 | 0.23311 | 0.19544 | 0.079188 | 0.16237 | 0.22573 | 0.014092 | -0.088054 | 0.071125 | 0.068999 | 0.021454 | 0.060921 | 0.091244 | 0.14091 | -0.057033 | -0.007362
1206.0469 | 121.1884 | -0.1831 | 121.0739 | 0.044018 | -0.035942 | 0.001736 | -0.061645 | 0.086622 | 0.044377 | -0.067295 | 0.14406 | 0.20742 | -0.008798 | -0.10637 | 0.052814 | 0.050688 | 0.003143 | 0.04261 | 0.22712 | 0.14716 | 0.18484 | 0.12146 | 0.26973 | 0.22748 | 0.11581 | 0.16237 | 0.22573 | 0.009513 | -0.088054 | 0.071125 | 0.068999 | 0.021454 | 0.060921 | 0.091244 | 0.14091 | -0.061612 | -0.011941
1207.7344 | 121.1792 | -0.21057 | 121.0693 | 0.044018 | -0.035942 | 0.001736 | -0.052488 | 0.082044 | 0.039799 | -0.067295 | 0.13948 | 0.20284 | -0.008798 | -0.10637 | 0.048236 | 0.04611 | -0.001436 | 0.051766 | 0.25459 | 0.17463 | 0.21231 | 0.15808 | 0.29262 | 0.25037 | 0.14328 | 0.15779 | 0.22116 | 0.009513 | -0.088054 | 0.066547 | 0.064421 | 0.016875 | 0.070077 | 0.091243 | 0.14091 | -0.057034 | -0.007362
1209.4844 | 121.2845 | -0.16937 | 121.0419 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 0.13948 | 0.212 | -0.008798 | -0.11094 | 0.052814 | 0.050688 | 0.007721 | 0.056344 | 0.20881 | 0.12885 | 0.16653 | 0.11688 | 0.25142 | 0.21375 | 0.097499 | 0.15779 | 0.23031 | 0.009513 | -0.092633 | 0.071125 | 0.068999 | 0.026032 | 0.074655 | 0.086665 | 0.13176 | -0.061612 | -0.016519
1211.1719 | 121.2799 | -0.15106 | 121.0556 | 0.044018 | -0.035942 | -0.002842 | -0.047909 | 0.082044 | 0.048956 | -0.067295 | 0.13948 | 0.19827 | -0.004219 | -0.11094 | 0.043657 | 0.050688 | 0.012299 | 0.056344 | 0.19508 | 0.11512 | 0.14822 | 0.10315 | 0.23311 | 0.20002 | 0.083767 | 0.15779 | 0.21658 | 0.014092 | -0.092633 | 0.061968 | 0.068999 | 0.03061 | 0.074655 | 0.095822 | 0.12718 | -0.047876 | -0.016518
1212.8594 | 121.2753 | -0.16022 | 121.051 | 0.048597 | -0.0451 | 0.006315 | -0.057066 | 0.086622 | 0.039799 | -0.076452 | 0.14406 | 0.20284 | -0.008798 | -0.10637 | 0.052814 | 0.04611 | 0.012299 | 0.051766 | 0.20881 | 0.11512 | 0.16653 | 0.10315 | 0.24684 | 0.20002 | 0.083765 | 0.16237 | 0.22116 | 0.009513 | -0.088054 | 0.071125 | 0.064421 | 0.03061 | 0.070077 | 0.091244 | 0.13176 | -0.061612 | -0.021097
1214.6094 | 121.2936 | -0.16479 | 121.0648 | 0.03944 | -0.0451 | 0.006315 | -0.057066 | 0.082044 | 0.039799 | -0.076452 | 0.14864 | 0.20284 | -0.004219 | -0.10637 | 0.043657 | 0.041532 | 0.012299 | 0.047188 | 0.20423 | 0.11969 | 0.17111 | 0.10773 | 0.24684 | 0.20459 | 0.088343 | 0.16695 | 0.22116 | 0.014092 | -0.088054 | 0.061968 | 0.059843 | 0.03061 | 0.065499 | 0.10498 | 0.13634 | -0.047876 | -0.016518
1216.2969 | 121.2845 | -0.16022 | 121.0648 | 0.044018 | -0.040521 | -0.002842 | -0.057066 | 0.072888 | 0.035221 | -0.071874 | 0.13948 | 0.20284 | -0.008798 | -0.10179 | 0.043657 | 0.050688 | 0.012299 | 0.056344 | 0.20423 | 0.1197 | 0.15737 | 0.10315 | 0.23311 | 0.19544 | 0.088343 | 0.15779 | 0.22116 | 0.009513 | -0.083475 | 0.061968 | 0.068999 | 0.03061 | 0.074655 | 0.095822 | 0.12718 | -0.052455 | -0.021097
1218.0312 | 121.2662 | -0.15564 | 121.0648 | 0.048597 | -0.035942 | -0.002842 | -0.052488 | 0.082044 | 0.048956 | -0.071874 | 0.1349 | 0.20742 | -0.008798 | -0.10637 | 0.052814 | 0.04611 | 0.012299 | 0.056344 | 0.20424 | 0.1197 | 0.1528 | 0.10315 | 0.23768 | 0.2046 | 0.083766 | 0.15321 | 0.22573 | 0.009513 | -0.088054 | 0.071125 | 0.064421 | 0.03061 | 0.074655 | 0.082087 | 0.1226 | -0.061612 | -0.021097
1219.7031 | 121.3303 | -0.16479 | 121.0693 | 0.044018 | -0.0451 | -0.007421 | -0.052488 | 0.082044 | 0.048956 | -0.076452 | 0.13948 | 0.20284 | 0.000359 | -0.11552 | 0.048236 | 0.04611 | 0.012299 | 0.056344 | 0.20881 | 0.11969 | 0.15737 | 0.11231 | 0.24684 | 0.21375 | 0.088343 | 0.15779 | 0.22116 | 0.01867 | -0.097212 | 0.066547 | 0.064421 | 0.03061 | 0.074655 | 0.091243 | 0.12718 | -0.047877 | -0.01194
1221.4531 | 121.1929 | -0.21973 | 121.1197 | 0.048597 | -0.0451 | 0.001736 | -0.057066 | 0.086622 | 0.044377 | -0.067295 | 0.13032 | 0.20742 | -0.004219 | -0.10637 | 0.043657 | 0.055266 | 0.016878 | 0.056344 | 0.26832 | 0.17463 | 0.22146 | 0.16266 | 0.30635 | 0.2641 | 0.15243 | 0.14863 | 0.22573 | 0.014092 | -0.088054 | 0.061968 | 0.073577 | 0.035189 | 0.074655 | 0.086665 | 0.11344 | -0.047876 | -0.021097
1223.2031 | 121.2204 | -0.21515 | 121.0876 | 0.044018 | -0.0451 | 0.001736 | -0.061645 | 0.082044 | 0.044377 | -0.071874 | 0.1349 | 0.19369 | 0.000359 | -0.11552 | 0.052814 | 0.04611 | 0.012299 | 0.060923 | 0.25917 | 0.17005 | 0.21688 | 0.1535 | 0.29719 | 0.25953 | 0.14328 | 0.15321 | 0.212 | 0.01867 | -0.097212 | 0.071125 | 0.064421 | 0.03061 | 0.079234 | 0.082087 | 0.1226 | -0.052455 | -0.01194
1224.8906 | 121.1929 | -0.20142 | 121.0968 | 0.044018 | -0.035942 | 0.006315 | -0.057066 | 0.077466 | 0.039799 | -0.071874 | 0.1349 | 0.20742 | -0.013376 | -0.10637 | 0.048236 | 0.04611 | 0.016878 | 0.056344 | 0.24543 | 0.16547 | 0.20773 | 0.14435 | 0.27888 | 0.24122 | 0.12954 | 0.15321 | 0.22573 | 0.004935 | -0.088054 | 0.066547 | 0.064421 | 0.035189 | 0.074655 | 0.086665 | 0.11802 | -0.061612 | -0.030254
1226.6562 | 121.1884 | -0.2243 | 121.1243 | 0.03944 | -0.0451 | 0.001736 | -0.052488 | 0.086622 | 0.048956 | -0.067295 | 0.13948 | 0.20284 | -0.008798 | -0.11094 | 0.043657 | 0.04611 | 0.012299 | 0.060923 | 0.26374 | 0.1792 | 0.22604 | 0.17182 | 0.31093 | 0.27326 | 0.15701 | 0.15779 | 0.22116 | 0.009513 | -0.092633 | 0.061968 | 0.064421 | 0.03061 | 0.079234 | 0.095822 | 0.12718 | -0.052455 | -0.021097
1228.3438 | 121.2799 | -0.19684 | 121.0922 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.067295 | 0.1349 | 0.20284 | 0.000359 | -0.10637 | 0.052814 | 0.04611 | 0.021456 | 0.070079 | 0.2317 | 0.15632 | 0.19857 | 0.14435 | 0.27888 | 0.24122 | 0.12954 | 0.15321 | 0.22116 | 0.01867 | -0.088054 | 0.071125 | 0.064421 | 0.039767 | 0.08839 | 0.082087 | 0.11344 | -0.052455 | -0.021097
1230.0938 | 121.1975 | -0.23804 | 121.106 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.086622 | 0.048956 | -0.071874 | 0.13032 | 0.20742 | -0.004219 | -0.10637 | 0.052814 | 0.04611 | 0.030613 | 0.065501 | 0.28206 | 0.19752 | 0.24435 | 0.18097 | 0.32466 | 0.28699 | 0.16616 | 0.14863 | 0.22573 | 0.014092 | -0.088054 | 0.071125 | 0.064421 | 0.048924 | 0.083812 | 0.077508 | 0.099709 | -0.057033 | -0.034832
1231.7656 | 121.2936 | -0.26093 | 121.0327 | 0.03944 | -0.0451 | -0.002842 | -0.057066 | 0.06831 | 0.039799 | -0.071874 | 0.12574 | 0.19369 | -0.013376 | -0.11094 | 0.052814 | 0.04611 | 0.053505 | 0.10213 | 0.30036 | 0.21583 | 0.25808 | 0.20386 | 0.32923 | 0.30072 | 0.18905 | 0.14405 | 0.212 | 0.004935 | -0.092633 | 0.071125 | 0.064421 | 0.071816 | 0.12044 | 0.07293 | 0.072239 | -0.06619 | -0.066881
1233.5 | 121.312 | -0.2655 | 121.0052 | 0.044018 | -0.0451 | -0.007421 | -0.061645 | 0.082044 | 0.039799 | -0.076452 | 0.12574 | 0.19369 | -0.008798 | -0.11094 | 0.052814 | 0.055266 | 0.062662 | 0.1067 | 0.30952 | 0.2204 | 0.25808 | 0.20386 | 0.34755 | 0.3053 | 0.18905 | 0.14405 | 0.212 | 0.009513 | -0.092633 | 0.071125 | 0.073577 | 0.080973 | 0.12501 | 0.07293 | 0.063082 | -0.061612 | -0.07146
1235.1719 | 121.2845 | -0.27008 | 121.0281 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.035221 | -0.076452 | 0.12116 | 0.19369 | -0.004219 | -0.11552 | 0.066548 | 0.050688 | 0.06724 | 0.11128 | 0.3141 | 0.22956 | 0.27182 | 0.21302 | 0.34297 | 0.3053 | 0.19363 | 0.13948 | 0.212 | 0.014092 | -0.097212 | 0.084859 | 0.068999 | 0.085551 | 0.12959 | 0.054617 | 0.053925 | -0.070767 | -0.071459
1236.9219 | 121.2341 | -0.27466 | 121.051 | 0.03944 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 0.12574 | 0.19369 | -0.013376 | -0.10179 | 0.048236 | 0.059844 | 0.06724 | 0.11128 | 0.3141 | 0.23414 | 0.28097 | 0.22217 | 0.35212 | 0.31446 | 0.19821 | 0.14405 | 0.212 | 0.004935 | -0.083475 | 0.066547 | 0.078155 | 0.085551 | 0.12959 | 0.077508 | 0.058504 | -0.061612 | -0.080616
1238.6719 | 121.257 | -0.29755 | 121.0373 | 0.034862 | -0.040521 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 0.12116 | 0.19369 | -0.008798 | -0.10637 | 0.052814 | 0.055266 | 0.06724 | 0.11586 | 0.33241 | 0.25702 | 0.29928 | 0.24506 | 0.37043 | 0.33735 | 0.22567 | 0.13948 | 0.212 | 0.009513 | -0.088054 | 0.071125 | 0.073577 | 0.085551 | 0.13417 | 0.068351 | 0.053925 | -0.061612 | -0.076038
1240.3594 | 121.2708 | -0.3067 | 121.0281 | 0.030283 | -0.0451 | 0.001736 | -0.061645 | 0.082044 | 0.035221 | -0.076452 | 0.13032 | 0.18911 | -0.013376 | -0.11094 | 0.052814 | 0.050688 | 0.06724 | 0.11128 | 0.33698 | 0.2616 | 0.30844 | 0.24506 | 0.38875 | 0.34192 | 0.23025 | 0.14863 | 0.20742 | 0.004935 | -0.092633 | 0.071125 | 0.068999 | 0.085551 | 0.12959 | 0.077508 | 0.063082 | -0.06619 | -0.080616
1242.1094 | 121.3531 | -0.27466 | 121.0052 | 0.044018 | -0.0451 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.076452 | 0.12574 | 0.18453 | -0.004219 | -0.10637 | 0.057392 | 0.055266 | 0.071818 | 0.12044 | 0.31868 | 0.22956 | 0.27639 | 0.22217 | 0.34755 | 0.31446 | 0.19821 | 0.14405 | 0.20284 | 0.014092 | -0.088054 | 0.075703 | 0.073577 | 0.090129 | 0.13875 | 0.068352 | 0.053926 | -0.061611 | -0.076037
1243.8438 | 121.3074 | -0.28839 | 121.0327 | 0.034862 | -0.040521 | 0.006315 | -0.061645 | 0.082044 | 0.035221 | -0.071874 | 0.12574 | 0.18911 | 0.000359 | -0.11094 | 0.048236 | 0.055266 | 0.06724 | 0.11128 | 0.32325 | 0.24787 | 0.29471 | 0.22675 | 0.37044 | 0.32361 | 0.21652 | 0.14405 | 0.20742 | 0.01867 | -0.092633 | 0.066547 | 0.073577 | 0.085551 | 0.12959 | 0.077508 | 0.058504 | -0.047877 | -0.066881
1245.5781 | 121.2021 | -0.30212 | 121.0602 | 0.034862 | -0.0451 | 0.001736 | -0.057066 | 0.077466 | 0.048956 | -0.071874 | 0.12574 | 0.18911 | -0.008798 | -0.11094 | 0.052814 | 0.055266 | 0.062662 | 0.10213 | 0.33699 | 0.25702 | 0.30386 | 0.24506 | 0.37959 | 0.35108 | 0.23025 | 0.14405 | 0.20742 | 0.009513 | -0.092633 | 0.071125 | 0.073577 | 0.080973 | 0.12044 | 0.07293 | 0.063082 | -0.061612 | -0.07146
1247.3281 | 121.2387 | -0.26093 | 121.1014 | 0.03944 | -0.0451 | -0.002842 | -0.057066 | 0.082044 | 0.044377 | -0.071874 | 0.13032 | 0.18911 | 0.000359 | -0.11094 | 0.057392 | 0.04611 | 0.044348 | 0.09297 | 0.30036 | 0.21583 | 0.25808 | 0.20386 | 0.34297 | 0.3053 | 0.18905 | 0.14863 | 0.20742 | 0.01867 | -0.092633 | 0.075703 | 0.064421 | 0.062659 | 0.11128 | 0.07293 | 0.085974 | -0.057033 | -0.043989
1249 | 121.2158 | -0.30212 | 121.0602 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.039799 | -0.076452 | 0.12116 | 0.18911 | 0.000359 | -0.11094 | 0.048236 | 0.055266 | 0.06724 | 0.11586 | 0.34614 | 0.2616 | 0.30844 | 0.24506 | 0.38417 | 0.34192 | 0.22567 | 0.13948 | 0.20742 | 0.01867 | -0.092633 | 0.066547 | 0.073577 | 0.085551 | 0.13417 | 0.072929 | 0.053925 | -0.047877 | -0.066881
1250.7344 | 121.2387 | -0.29297 | 121.051 | 0.044018 | -0.035942 | 0.001736 | -0.061645 | 0.082044 | 0.039799 | -0.067295 | 0.12116 | 0.18911 | -0.004219 | -0.10637 | 0.048236 | 0.055266 | 0.062662 | 0.11128 | 0.33699 | 0.25703 | 0.2947 | 0.23132 | 0.37501 | 0.33277 | 0.22567 | 0.13948 | 0.20742 | 0.014092 | -0.088054 | 0.066547 | 0.073577 | 0.080973 | 0.12959 | 0.072929 | 0.058503 | -0.052455 | -0.066881
1252.4844 | 121.3028 | -0.27924 | 121.0052 | 0.034862 | -0.040521 | -0.002842 | -0.061645 | 0.0912 | 0.044377 | -0.08103 | 0.13032 | 0.18453 | -0.004219 | -0.10179 | 0.052814 | 0.059844 | 0.06724 | 0.12044 | 0.3141 | 0.23871 | 0.27639 | 0.21759 | 0.37044 | 0.32361 | 0.19821 | 0.14863 | 0.20284 | 0.014092 | -0.083475 | 0.071125 | 0.078155 | 0.085551 | 0.13875 | 0.077508 | 0.063082 | -0.057033 | -0.071459
1254.1719 | 121.2845 | -0.37537 | 120.9366 | 0.034862 | -0.0451 | -0.002842 | -0.061645 | 0.077466 | 0.039799 | -0.071874 | 0.11659 | 0.19369 | -0.004219 | -0.10179 | 0.06197 | 0.055266 | 0.12218 | 0.16164 | 0.41023 | 0.33027 | 0.37252 | 0.31372 | 0.45283 | 0.41517 | 0.30349 | 0.1349 | 0.212 | 0.014092 | -0.083475 | 0.080281 | 0.073577 | 0.14049 | 0.17995 | 0.054617 | -0.005594 | -0.066189 | -0.1264
1255.9219 | 121.2158 | -0.2243 | 121.0968 | 0.03944 | -0.040521 | -0.002842 | -0.057066 | 0.082044 | 0.035221 | -0.071874 | 0.12574 | 0.19369 | -0.004219 | -0.10179 | 0.048236 | 0.050688 | 0.030613 | 0.070079 | 0.26374 | 0.18378 | 0.22146 | 0.16724 | 0.30635 | 0.25953 | 0.15243 | 0.14405 | 0.212 | 0.014092 | -0.083475 | 0.066547 | 0.068999 | 0.048924 | 0.08839 | 0.077508 | 0.095131 | -0.052455 | -0.034832
1257.6094 | 121.225 | -0.25635 | 121.1243 | 0.048597 | -0.031363 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.067295 | 0.12574 | 0.19369 | -0.004219 | -0.10637 | 0.052814 | 0.050688 | 0.03977 | 0.074657 | 0.30495 | 0.22499 | 0.26266 | 0.20386 | 0.33381 | 0.29615 | 0.18905 | 0.14405 | 0.212 | 0.014092 | -0.088054 | 0.071125 | 0.068999 | 0.058081 | 0.092968 | 0.07293 | 0.085974 | -0.057033 | -0.043989
1259.3438 | 121.3257 | -0.22888 | 121.0739 | 0.03944 | -0.049678 | -0.007421 | -0.061645 | 0.072888 | 0.039799 | -0.067295 | 0.12116 | 0.19369 | -0.008798 | -0.10637 | 0.057392 | 0.059844 | 0.044348 | 0.097548 | 0.26832 | 0.1792 | 0.22146 | 0.16724 | 0.30177 | 0.26868 | 0.16159 | 0.13948 | 0.212 | 0.009513 | -0.088054 | 0.075703 | 0.078155 | 0.062659 | 0.11586 | 0.063773 | 0.076817 | -0.06619 | -0.053146
1261.0938 | 121.225 | -0.30212 | 121.0556 | 0.03944 | -0.0451 | -0.007421 | -0.07538 | 0.077466 | 0.030642 | -0.08103 | 0.12116 | 0.17995 | -0.008798 | -0.10637 | 0.06197 | 0.078157 | 0.2458 | 0.28068 | 0.34156 | 0.25702 | 0.2947 | 0.22674 | 0.37959 | 0.33277 | 0.22109 | 0.13948 | 0.19826 | 0.009513 | -0.088054 | 0.080281 | 0.096468 | 0.26411 | 0.29899 | 0.059195 | -0.12463 | -0.070768 | -0.2546
1262.8438 | 121.2387 | -0.20599 | 121.1197 | 0.044018 | -0.031363 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.071874 | 0.13032 | 0.19369 | -0.004219 | -0.11094 | 0.043657 | 0.055266 | 0.016878 | 0.051766 | 0.25001 | 0.17463 | 0.20773 | 0.14893 | 0.28346 | 0.24579 | 0.13412 | 0.14863 | 0.212 | 0.014092 | -0.092633 | 0.061968 | 0.073577 | 0.035189 | 0.070077 | 0.086665 | 0.11344 | -0.047876 | -0.021097
1264.5938 | 121.2479 | -0.21973 | 121.1838 | 0.053175 | -0.035942 | 0.006315 | -0.061645 | 0.082044 | 0.039799 | -0.071874 | 0.1349 | 0.19827 | 0.000359 | -0.10637 | 0.052814 | 0.041532 | 0.012299 | 0.051766 | 0.2729 | 0.18379 | 0.22604 | 0.15808 | 0.30177 | 0.25953 | 0.14785 | 0.15321 | 0.21658 | 0.01867 | -0.088054 | 0.071125 | 0.059843 | 0.03061 | 0.070077 | 0.082087 | 0.1226 | -0.052455 | -0.01194
1266.2656 | 121.3531 | -0.16022 | 121.1288 | 0.044018 | -0.040521 | -0.002842 | -0.052488 | 0.077466 | 0.048956 | -0.067295 | 0.13032 | 0.19369 | -0.008798 | -0.11094 | 0.048236 | 0.041532 | 0.012299 | 0.047188 | 0.20423 | 0.1197 | 0.15737 | 0.10773 | 0.23768 | 0.20917 | 0.092922 | 0.14863 | 0.212 | 0.009513 | -0.092633 | 0.066547 | 0.059843 | 0.03061 | 0.065499 | 0.082086 | 0.11802 | -0.057034 | -0.021097
1268 | 121.312 | -0.17853 | 121.17 | 0.03944 | -0.0451 | -0.002842 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 0.13032 | 0.20284 | 0.000359 | -0.11094 | 0.048236 | 0.055266 | 0.016878 | 0.051766 | 0.21797 | 0.13343 | 0.17569 | 0.12604 | 0.25599 | 0.2229 | 0.10665 | 0.14863 | 0.22116 | 0.01867 | -0.092633 | 0.066547 | 0.073577 | 0.035189 | 0.070077 | 0.082086 | 0.11344 | -0.047877 | -0.016519
1269.7344 | 121.3165 | -0.17395 | 121.1746 | 0.044018 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.076452 | 0.12574 | 0.19827 | -0.008798 | -0.10637 | 0.048236 | 0.050688 | 0.012299 | 0.051766 | 0.21797 | 0.13801 | 0.17569 | 0.12146 | 0.25142 | 0.21375 | 0.097498 | 0.14405 | 0.21658 | 0.009513 | -0.088054 | 0.066547 | 0.068999 | 0.03061 | 0.070077 | 0.077508 | 0.11344 | -0.057034 | -0.021097
1271.5 | 121.4081 | -0.1831 | 121.1517 | 0.048597 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.067295 | 0.13032 | 0.19369 | 0.000359 | -0.10637 | 0.048236 | 0.04611 | 0.007721 | 0.04261 | 0.2317 | 0.14258 | 0.18484 | 0.12604 | 0.26515 | 0.2229 | 0.11581 | 0.14863 | 0.212 | 0.01867 | -0.088054 | 0.066547 | 0.064421 | 0.026032 | 0.060921 | 0.082086 | 0.1226 | -0.047877 | -0.007362
1273.1875 | 121.3715 | -0.15106 | 121.17 | 0.03944 | -0.035942 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.067295 | 0.12574 | 0.19827 | -0.004219 | -0.11094 | 0.039079 | 0.04611 | 0.003143 | 0.04261 | 0.1905 | 0.11512 | 0.1528 | 0.098574 | 0.22853 | 0.19086 | 0.083767 | 0.14405 | 0.21658 | 0.014092 | -0.092633 | 0.05739 | 0.064421 | 0.021454 | 0.060921 | 0.086665 | 0.1226 | -0.043298 | -0.007362
1274.9219 | 121.3623 | -0.16937 | 121.1517 | 0.03944 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.039799 | -0.08103 | 0.12116 | 0.18911 | -0.008798 | -0.11094 | 0.048236 | 0.050688 | 0.007721 | 0.051766 | 0.20881 | 0.12885 | 0.17111 | 0.11231 | 0.24684 | 0.20917 | 0.088343 | 0.13948 | 0.20742 | 0.009513 | -0.092633 | 0.066547 | 0.068999 | 0.026032 | 0.070077 | 0.072929 | 0.11344 | -0.057034 | -0.016519
1276.6719 | 121.2753 | -0.21057 | 121.2341 | 0.03944 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.071874 | 0.12574 | 0.19369 | 0.000359 | -0.10637 | 0.039079 | 0.041532 | 0.007721 | 0.047188 | 0.25001 | 0.17005 | 0.21689 | 0.15351 | 0.29262 | 0.25495 | 0.1387 | 0.14405 | 0.212 | 0.01867 | -0.088054 | 0.05739 | 0.059843 | 0.026032 | 0.065499 | 0.086665 | 0.11802 | -0.03872 | -0.007362
1278.3594 | 121.4264 | -0.15106 | 121.1746 | 0.03944 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.048956 | -0.071874 | 0.12574 | 0.19369 | 0.004937 | -0.11552 | 0.048236 | 0.04611 | 0.012299 | 0.051766 | 0.1905 | 0.11054 | 0.1528 | 0.093996 | 0.22853 | 0.20002 | 0.079188 | 0.14405 | 0.212 | 0.023248 | -0.097212 | 0.066547 | 0.064421 | 0.03061 | 0.070077 | 0.077508 | 0.11344 | -0.043299 | -0.007362
1280.0938 | 121.3943 | -0.16022 | 121.1792 | 0.03944 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.039799 | -0.076452 | 0.11659 | 0.19827 | 0.000359 | -0.11094 | 0.043657 | 0.04611 | -0.001436 | 0.047188 | 0.19966 | 0.1197 | 0.16195 | 0.10315 | 0.23311 | 0.20002 | 0.083765 | 0.1349 | 0.21658 | 0.01867 | -0.092633 | 0.061968 | 0.064421 | 0.016875 | 0.065499 | 0.07293 | 0.11802 | -0.043298 | 0.001795
1281.8438 | 121.2845 | -0.20599 | 121.225 | 0.03944 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 0.12574 | 0.19369 | 0.000359 | -0.10637 | 0.052814 | 0.041532 | 0.003143 | 0.051766 | 0.24543 | 0.16547 | 0.20773 | 0.15351 | 0.28804 | 0.25037 | 0.13412 | 0.14405 | 0.212 | 0.01867 | -0.088054 | 0.071125 | 0.059843 | 0.021454 | 0.070077 | 0.07293 | 0.1226 | -0.052455 | -0.002784
1283.5781 | 121.3715 | -0.17853 | 121.1929 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.082044 | 0.044377 | -0.076452 | 0.12574 | 0.19827 | -0.004219 | -0.11094 | 0.048236 | 0.041532 | 0.012299 | 0.047188 | 0.22255 | 0.13801 | 0.18484 | 0.12604 | 0.26057 | 0.2229 | 0.10208 | 0.14405 | 0.21658 | 0.014092 | -0.092633 | 0.066547 | 0.059843 | 0.03061 | 0.065499 | 0.077508 | 0.11344 | -0.052455 | -0.016518
1285.2656 | 121.3577 | -0.17395 | 121.2158 | 0.044018 | -0.040521 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 0.098273 | 0.19369 | -0.004219 | -0.10637 | 0.048236 | 0.050688 | 0.012299 | 0.04261 | 0.21797 | 0.13343 | 0.17569 | 0.12146 | 0.25142 | 0.21833 | 0.097498 | 0.11658 | 0.212 | 0.014092 | -0.088054 | 0.066547 | 0.068999 | 0.03061 | 0.060921 | 0.050037 | 0.085974 | -0.052455 | -0.016518
1287.0156 | 121.3028 | -0.1831 | 121.2341 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.071874 | 0.093694 | 0.19369 | 0.000359 | -0.11094 | 0.043657 | 0.04611 | 0.003143 | 0.047188 | 0.22712 | 0.138 | 0.18484 | 0.12604 | 0.26515 | 0.2229 | 0.11123 | 0.112 | 0.212 | 0.01867 | -0.092633 | 0.061968 | 0.064421 | 0.021454 | 0.065499 | 0.050037 | 0.090551 | -0.043298 | -0.002784
1288.75 | 121.2708 | -0.20142 | 121.225 | 0.044018 | -0.031363 | -0.002842 | -0.061645 | 0.082044 | 0.039799 | -0.067295 | 0.093694 | 0.19369 | -0.008798 | -0.10179 | 0.052814 | 0.041532 | 0.007721 | 0.047188 | 0.24543 | 0.17005 | 0.19857 | 0.13977 | 0.28346 | 0.24122 | 0.13412 | 0.112 | 0.212 | 0.009513 | -0.083475 | 0.071125 | 0.059843 | 0.026032 | 0.065499 | 0.04088 | 0.085973 | -0.061612 | -0.016519
1290.5 | 121.312 | -0.20599 | 121.2479 | 0.03944 | -0.035942 | 0.010893 | -0.052488 | 0.077466 | 0.044377 | -0.067295 | 0.093694 | 0.19827 | 0.000359 | -0.10637 | 0.039079 | 0.04611 | 0.007721 | 0.051766 | 0.24543 | 0.17005 | 0.21689 | 0.15351 | 0.28346 | 0.25037 | 0.1387 | 0.112 | 0.21658 | 0.01867 | -0.088054 | 0.05739 | 0.064421 | 0.026032 | 0.070077 | 0.054615 | 0.085973 | -0.03872 | -0.007362
1292.1875 | 121.3623 | -0.18768 | 121.2021 | 0.048597 | -0.040521 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.076452 | 0.089116 | 0.18911 | -0.008798 | -0.11552 | 0.048236 | 0.041532 | 0.012299 | 0.051766 | 0.23628 | 0.14716 | 0.18942 | 0.13977 | 0.26973 | 0.22748 | 0.11123 | 0.10743 | 0.20742 | 0.009513 | -0.097212 | 0.066547 | 0.059843 | 0.03061 | 0.070077 | 0.04088 | 0.076817 | -0.057034 | -0.021097
1293.9219 | 121.4264 | -0.16937 | 121.1975 | 0.044018 | -0.0451 | 0.001736 | -0.061645 | 0.086622 | 0.044377 | -0.067295 | 0.10285 | 0.19827 | -0.004219 | -0.10179 | 0.052814 | 0.04611 | 0.007721 | 0.047188 | 0.21339 | 0.12427 | 0.17111 | 0.10773 | 0.25599 | 0.21375 | 0.10208 | 0.12116 | 0.21658 | 0.014092 | -0.083475 | 0.071125 | 0.064421 | 0.026032 | 0.065499 | 0.050037 | 0.09513 | -0.057033 | -0.01194
1295.6562 | 121.3943 | -0.17853 | 121.2296 | 0.044018 | -0.0451 | 0.001736 | -0.061645 | 0.082044 | 0.039799 | -0.071874 | 0.089116 | 0.18911 | 0.000359 | -0.10637 | 0.043657 | 0.04611 | 0.012299 | 0.051766 | 0.22255 | 0.13343 | 0.18026 | 0.11688 | 0.26057 | 0.21833 | 0.10665 | 0.10743 | 0.20742 | 0.01867 | -0.088054 | 0.061968 | 0.064421 | 0.03061 | 0.070077 | 0.045459 | 0.076817 | -0.043298 | -0.01194
1297.3438 | 121.3623 | -0.19684 | 121.2296 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.044377 | -0.067295 | 0.093694 | 0.19369 | -0.004219 | -0.10179 | 0.043657 | 0.04611 | 0.012299 | 0.051766 | 0.24086 | 0.15632 | 0.20315 | 0.14435 | 0.2743 | 0.24122 | 0.12954 | 0.112 | 0.212 | 0.014092 | -0.083475 | 0.061968 | 0.064421 | 0.03061 | 0.070077 | 0.050037 | 0.081395 | -0.047876 | -0.016518
1299.0938 | 121.4081 | -0.16022 | 121.2112 | 0.048597 | -0.0451 | 0.001736 | -0.061645 | 0.086622 | 0.039799 | -0.067295 | 0.089116 | 0.19369 | -0.004219 | -0.10179 | 0.048236 | 0.04611 | 0.007721 | 0.047188 | 0.20881 | 0.11512 | 0.16195 | 0.098572 | 0.24684 | 0.20002 | 0.092922 | 0.10743 | 0.212 | 0.014092 | -0.083475 | 0.066547 | 0.064421 | 0.026032 | 0.065499 | 0.04088 | 0.081395 | -0.052455 | -0.01194
1300.7812 | 121.4264 | -0.17853 | 121.2204 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.039799 | -0.067295 | 0.084537 | 0.19369 | 0.000359 | -0.10637 | 0.048236 | 0.04611 | 0.007721 | 0.051766 | 0.22255 | 0.13801 | 0.18484 | 0.12146 | 0.26057 | 0.21833 | 0.11123 | 0.10285 | 0.212 | 0.01867 | -0.088054 | 0.066547 | 0.064421 | 0.026032 | 0.070077 | 0.036301 | 0.076816 | -0.047877 | -0.007362
1302.5469 | 121.3623 | -0.19226 | 121.2479 | 0.048597 | -0.040521 | 0.001736 | -0.052488 | 0.086622 | 0.044377 | -0.071874 | 0.089116 | 0.18911 | 0.000359 | -0.10179 | 0.052814 | 0.050688 | 0.012299 | 0.051766 | 0.24086 | 0.15174 | 0.194 | 0.13977 | 0.27888 | 0.23664 | 0.12039 | 0.10743 | 0.20742 | 0.01867 | -0.083475 | 0.071125 | 0.068999 | 0.03061 | 0.070077 | 0.036302 | 0.076817 | -0.052455 | -0.01194
1304.2188 | 121.4447 | -0.14191 | 121.2067 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.071874 | 0.10285 | 0.19369 | -0.004219 | -0.10179 | 0.043657 | 0.04611 | 0.007721 | 0.04261 | 0.18593 | 0.10139 | 0.14364 | 0.084841 | 0.22395 | 0.18171 | 0.070033 | 0.12116 | 0.212 | 0.014092 | -0.083475 | 0.061968 | 0.064421 | 0.026032 | 0.060921 | 0.059194 | 0.09513 | -0.047876 | -0.01194
1305.9531 | 121.4539 | -0.14191 | 121.1975 | 0.03944 | -0.035942 | 0.001736 | -0.061645 | 0.082044 | 0.044377 | -0.076452 | 0.089116 | 0.19369 | -0.008798 | -0.11552 | 0.048236 | 0.04611 | -0.001436 | 0.047188 | 0.18135 | 0.10597 | 0.14364 | 0.080262 | 0.22395 | 0.18628 | 0.065455 | 0.10743 | 0.212 | 0.009513 | -0.097212 | 0.066547 | 0.064421 | 0.016875 | 0.065499 | 0.04088 | 0.090552 | -0.057034 | -0.007362
1307.7031 | 121.3257 | -0.20599 | 121.2616 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.086622 | 0.044377 | -0.071874 | 0.089116 | 0.18453 | -0.004219 | -0.11094 | 0.048236 | 0.050688 | 0.003143 | 0.047188 | 0.25001 | 0.16089 | 0.20773 | 0.14893 | 0.29262 | 0.25037 | 0.13412 | 0.10743 | 0.20284 | 0.014092 | -0.092633 | 0.066547 | 0.068999 | 0.021454 | 0.065499 | 0.04088 | 0.085973 | -0.052455 | -0.007362
1309.4531 | 121.4081 | -0.14648 | 121.2479 | 0.044018 | -0.0451 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.071874 | 0.089116 | 0.18911 | -0.004219 | -0.11094 | 0.048236 | 0.050688 | 0.003143 | 0.04261 | 0.1905 | 0.10138 | 0.14364 | 0.098575 | 0.22395 | 0.19086 | 0.07461 | 0.10743 | 0.20742 | 0.014092 | -0.092633 | 0.066547 | 0.068999 | 0.021454 | 0.060921 | 0.04088 | 0.085973 | -0.052455 | -0.007362
1311.2031 | 121.3989 | -0.17853 | 121.2479 | 0.044018 | -0.040521 | -0.002842 | -0.061645 | 0.077466 | 0.044377 | -0.067295 | 0.084537 | 0.19369 | -0.004219 | -0.11094 | 0.043657 | 0.041532 | 0.003143 | 0.051766 | 0.22255 | 0.13801 | 0.17569 | 0.11688 | 0.25599 | 0.2229 | 0.11123 | 0.10285 | 0.212 | 0.014092 | -0.092633 | 0.061968 | 0.059843 | 0.021454 | 0.070077 | 0.04088 | 0.081394 | -0.047876 | -0.007362
1312.8906 | 121.4081 | -0.16937 | 121.2524 | 0.044018 | -0.049678 | 0.001736 | -0.061645 | 0.082044 | 0.044377 | -0.067295 | 0.084537 | 0.19369 | -0.004219 | -0.10637 | 0.048236 | 0.050688 | 0.003143 | 0.04261 | 0.21339 | 0.11969 | 0.17111 | 0.10773 | 0.25142 | 0.21375 | 0.10208 | 0.10285 | 0.212 | 0.014092 | -0.088054 | 0.066547 | 0.068999 | 0.021454 | 0.060921 | 0.036301 | 0.081394 | -0.052455 | -0.007362
1314.625 | 121.4081 | -0.17853 | 121.2662 | 0.034862 | -0.0451 | 0.010893 | -0.043331 | 0.086622 | 0.048956 | -0.067295 | 0.084537 | 0.19369 | -0.008798 | -0.10637 | 0.048236 | 0.04611 | -0.001436 | 0.047188 | 0.21339 | 0.13343 | 0.18942 | 0.1352 | 0.26515 | 0.22748 | 0.11123 | 0.10285 | 0.212 | 0.009513 | -0.088054 | 0.066547 | 0.064421 | 0.016875 | 0.065499 | 0.036301 | 0.085973 | -0.057034 | -0.007362
1316.3594 | 121.344 | -0.19684 | 121.2799 | 0.030283 | -0.040521 | 0.010893 | -0.052488 | 0.082044 | 0.048956 | -0.076452 | 0.084537 | 0.18911 | -0.004219 | -0.10637 | 0.043657 | 0.04611 | 0.003143 | 0.051766 | 0.22712 | 0.15632 | 0.20773 | 0.14435 | 0.27888 | 0.24579 | 0.12039 | 0.10285 | 0.20742 | 0.014092 | -0.088054 | 0.061968 | 0.064421 | 0.021454 | 0.070077 | 0.04088 | 0.081394 | -0.047876 | -0.007362
1318.0469 | 121.4035 | -0.16937 | 121.2524 | 0.053175 | -0.040521 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.071874 | 0.079959 | 0.18911 | -0.004219 | -0.11094 | 0.043657 | 0.04611 | 0.003143 | 0.047188 | 0.22255 | 0.12885 | 0.17111 | 0.11688 | 0.24684 | 0.21375 | 0.097499 | 0.09827 | 0.20742 | 0.014092 | -0.092633 | 0.061968 | 0.064421 | 0.021454 | 0.065499 | 0.036302 | 0.076816 | -0.047876 | -0.007362
1319.7969 | 121.4401 | -0.16022 | 121.2524 | 0.044018 | -0.0451 | 0.001736 | -0.057066 | 0.082044 | 0.035221 | -0.076452 | 0.093694 | 0.18911 | -0.013376 | -0.10637 | 0.048236 | 0.04611 | 0.003143 | 0.047188 | 0.20423 | 0.11512 | 0.16195 | 0.10315 | 0.24226 | 0.19544 | 0.083765 | 0.112 | 0.20742 | 0.004935 | -0.088054 | 0.066547 | 0.064421 | 0.021454 | 0.065499 | 0.045458 | 0.090551 | -0.061612 | -0.016519
1321.5469 | 121.3898 | -0.19684 | 121.2936 | 0.048597 | -0.040521 | 0.010893 | -0.052488 | 0.086622 | 0.044377 | -0.071874 | 0.084537 | 0.17995 | -0.004219 | -0.10179 | 0.052814 | 0.041532 | 0.003143 | 0.047188 | 0.24544 | 0.15632 | 0.20773 | 0.14435 | 0.28346 | 0.24122 | 0.12496 | 0.10285 | 0.19826 | 0.014092 | -0.083475 | 0.071125 | 0.059843 | 0.021454 | 0.065499 | 0.031723 | 0.081394 | -0.057033 | -0.007362
1323.2344 | 121.4218 | -0.14648 | 121.2662 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.082044 | 0.039799 | -0.071874 | 0.089116 | 0.19369 | -0.004219 | -0.11552 | 0.043657 | 0.041532 | 0.003143 | 0.047188 | 0.1905 | 0.10596 | 0.1528 | 0.093996 | 0.22853 | 0.18628 | 0.07461 | 0.10743 | 0.212 | 0.014092 | -0.097212 | 0.061968 | 0.059843 | 0.021454 | 0.065499 | 0.045459 | 0.085973 | -0.047876 | -0.007362
1324.9688 | 121.3257 | -0.19226 | 121.3028 | 0.044018 | -0.035942 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.071874 | 0.084537 | 0.18911 | 0.000359 | -0.11094 | 0.043657 | 0.04611 | -0.001436 | 0.047188 | 0.23628 | 0.15632 | 0.194 | 0.13519 | 0.26973 | 0.23664 | 0.12039 | 0.10285 | 0.20742 | 0.01867 | -0.092633 | 0.061968 | 0.064421 | 0.016875 | 0.065499 | 0.04088 | 0.085973 | -0.043298 | 0.001795
1326.7031 | 121.3531 | -0.17853 | 121.2936 | 0.048597 | -0.0451 | 0.001736 | -0.052488 | 0.086622 | 0.044377 | -0.067295 | 0.084537 | 0.18911 | -0.008798 | -0.11552 | 0.039079 | 0.050688 | 0.003143 | 0.04261 | 0.22712 | 0.13343 | 0.18026 | 0.12604 | 0.26515 | 0.2229 | 0.11123 | 0.10285 | 0.20742 | 0.009513 | -0.097212 | 0.05739 | 0.068999 | 0.021454 | 0.060921 | 0.045458 | 0.081394 | -0.047877 | -0.011941
1328.4531 | 121.3806 | -0.1831 | 121.2936 | 0.048597 | -0.0451 | 0.010893 | -0.061645 | 0.077466 | 0.035221 | -0.071874 | 0.089116 | 0.18453 | -0.008798 | -0.10637 | 0.043657 | 0.050688 | 0.003143 | 0.047188 | 0.2317 | 0.138 | 0.194 | 0.12146 | 0.26057 | 0.21833 | 0.11123 | 0.10743 | 0.20284 | 0.009513 | -0.088054 | 0.061968 | 0.068999 | 0.021454 | 0.065499 | 0.045459 | 0.085973 | -0.052455 | -0.011941
1330.1406 | 121.3989 | -0.16479 | 121.3028 | 0.03944 | -0.040521 | 0.001736 | -0.052488 | 0.082044 | 0.044377 | -0.067295 | 0.084537 | 0.18453 | -0.008798 | -0.11094 | 0.048236 | 0.04611 | -0.001436 | 0.033454 | 0.20423 | 0.12427 | 0.16653 | 0.11231 | 0.24684 | 0.20917 | 0.0975 | 0.10285 | 0.20284 | 0.009513 | -0.092633 | 0.066547 | 0.064421 | 0.016875 | 0.051765 | 0.036301 | 0.085973 | -0.057034 | -0.007362
1331.8906 | 121.4493 | -0.14191 | 121.2845 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.035221 | -0.071874 | 0.093694 | 0.18453 | -0.004219 | -0.11094 | 0.048236 | 0.04611 | -0.001436 | 0.033454 | 0.18593 | 0.10139 | 0.14822 | 0.089419 | 0.21937 | 0.17713 | 0.070033 | 0.112 | 0.20284 | 0.014092 | -0.092633 | 0.066547 | 0.064421 | 0.016875 | 0.051765 | 0.045458 | 0.09513 | -0.052455 | -0.002783
1333.625 | 121.3669 | -0.19684 | 121.3257 | 0.03944 | -0.035942 | 0.010893 | -0.057066 | 0.086622 | 0.044377 | -0.071874 | 0.084537 | 0.18453 | -0.004219 | -0.11552 | 0.048236 | 0.041532 | -0.001436 | 0.04261 | 0.23628 | 0.1609 | 0.20773 | 0.13977 | 0.28346 | 0.24122 | 0.12496 | 0.10285 | 0.20284 | 0.014092 | -0.097212 | 0.066547 | 0.059843 | 0.016875 | 0.060921 | 0.036301 | 0.085973 | -0.052455 | -0.002783
1335.3594 | 121.4859 | -0.14191 | 121.2616 | 0.048597 | -0.0451 | 0.006315 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 0.079959 | 0.18453 | -0.008798 | -0.11552 | 0.043657 | 0.04611 | 0.003143 | 0.04261 | 0.1905 | 0.096807 | 0.14822 | 0.089419 | 0.22395 | 0.18628 | 0.070033 | 0.09827 | 0.20284 | 0.009513 | -0.097212 | 0.061968 | 0.064421 | 0.021454 | 0.060921 | 0.036302 | 0.076816 | -0.052455 | -0.011941
1337.0469 | 121.3806 | -0.19684 | 121.3211 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.067295 | 0.089116 | 0.17995 | -0.008798 | -0.1201 | 0.039079 | 0.04611 | 0.007721 | 0.04261 | 0.24086 | 0.15632 | 0.19857 | 0.13977 | 0.27888 | 0.23664 | 0.12954 | 0.10743 | 0.19826 | 0.009513 | -0.10179 | 0.05739 | 0.064421 | 0.026032 | 0.060921 | 0.050037 | 0.081395 | -0.047877 | -0.016519
1338.7969 | 121.4539 | -0.16479 | 121.2662 | 0.03944 | -0.040521 | 0.006315 | -0.047909 | 0.082044 | 0.044377 | -0.071874 | 0.084537 | 0.17995 | -0.004219 | -0.10637 | 0.039079 | 0.050688 | 0.003143 | 0.04261 | 0.20423 | 0.12427 | 0.17111 | 0.11689 | 0.24684 | 0.20917 | 0.092921 | 0.10285 | 0.19826 | 0.014092 | -0.088054 | 0.05739 | 0.068999 | 0.021454 | 0.060921 | 0.045458 | 0.081394 | -0.043298 | -0.007362
1340.5469 | 121.4035 | -0.18768 | 121.2936 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.067295 | 0.079959 | 0.18453 | -0.004219 | -0.10637 | 0.043657 | 0.04611 | 0.003143 | 0.047188 | 0.2317 | 0.14716 | 0.18942 | 0.13062 | 0.26515 | 0.23206 | 0.12039 | 0.09827 | 0.20284 | 0.014092 | -0.088054 | 0.061968 | 0.064421 | 0.021454 | 0.065499 | 0.036302 | 0.076816 | -0.047876 | -0.007362
1342.2188 | 121.4905 | -0.16022 | 121.3074 | 0.048597 | -0.035942 | 0.001736 | -0.057066 | 0.082044 | 0.039799 | -0.071874 | 0.079959 | 0.18911 | -0.008798 | -0.10637 | 0.052814 | 0.04611 | 0.012299 | 0.047188 | 0.20881 | 0.12427 | 0.16195 | 0.10315 | 0.24226 | 0.20002 | 0.088343 | 0.09827 | 0.20742 | 0.009513 | -0.088054 | 0.071125 | 0.064421 | 0.03061 | 0.065499 | 0.027145 | 0.06766 | -0.061612 | -0.021097
1343.9688 | 121.4127 | -0.20599 | 121.312 | 0.044018 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.044377 | -0.067295 | 0.093694 | 0.17995 | 0.000359 | -0.10637 | 0.048236 | 0.050688 | 0.012299 | 0.04261 | 0.25001 | 0.16547 | 0.21231 | 0.14893 | 0.28804 | 0.25037 | 0.1387 | 0.112 | 0.19826 | 0.01867 | -0.088054 | 0.066547 | 0.068999 | 0.03061 | 0.060921 | 0.045458 | 0.081395 | -0.047877 | -0.01194
1345.6562 | 121.3669 | -0.20599 | 121.2982 | 0.03944 | -0.040521 | 0.006315 | -0.057066 | 0.082044 | 0.035221 | -0.062717 | 0.07538 | 0.17995 | 0.000359 | -0.11094 | 0.043657 | 0.04611 | 0.007721 | 0.04261 | 0.24543 | 0.16547 | 0.21231 | 0.14893 | 0.28804 | 0.24122 | 0.14328 | 0.093691 | 0.19826 | 0.01867 | -0.092633 | 0.061968 | 0.064421 | 0.026032 | 0.060921 | 0.031723 | 0.067659 | -0.043298 | -0.007362
1347.3906 | 121.431 | -0.19684 | 121.3211 | 0.048597 | -0.040521 | 0.006315 | -0.052488 | 0.082044 | 0.048956 | -0.071874 | 0.079959 | 0.17995 | 0.000359 | -0.10179 | 0.048236 | 0.055266 | 0.003143 | 0.051766 | 0.24544 | 0.15632 | 0.20315 | 0.14435 | 0.27888 | 0.24579 | 0.12496 | 0.09827 | 0.19826 | 0.01867 | -0.083475 | 0.066547 | 0.073577 | 0.021454 | 0.070077 | 0.031723 | 0.076816 | -0.047877 | -0.002784
1349.1406 | 121.4401 | -0.17853 | 121.2936 | 0.03944 | -0.031363 | -0.002842 | -0.061645 | 0.082044 | 0.044377 | -0.071874 | 0.084537 | 0.18911 | -0.008798 | -0.10637 | 0.039079 | 0.04611 | -0.001436 | 0.033454 | 0.21797 | 0.14716 | 0.17569 | 0.11688 | 0.26057 | 0.2229 | 0.10665 | 0.10285 | 0.20742 | 0.009513 | -0.088054 | 0.05739 | 0.064421 | 0.016875 | 0.051765 | 0.045458 | 0.085973 | -0.047877 | -0.007362
1350.8906 | 121.4859 | -0.15564 | 121.3165 | 0.044018 | -0.040521 | 0.001736 | -0.057066 | 0.072888 | 0.039799 | -0.067295 | 0.07538 | 0.18453 | -0.008798 | -0.10637 | 0.048236 | 0.055266 | 0.003143 | 0.04261 | 0.19966 | 0.11512 | 0.15738 | 0.098574 | 0.22853 | 0.19544 | 0.088345 | 0.093691 | 0.20284 | 0.009513 | -0.088054 | 0.066547 | 0.073577 | 0.021454 | 0.060921 | 0.027144 | 0.072237 | -0.057034 | -0.011941
1352.6406 | 121.4401 | -0.16937 | 121.3211 | 0.044018 | -0.040521 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.062717 | 0.079959 | 0.18453 | 0.000359 | -0.10637 | 0.048236 | 0.050688 | -0.001436 | 0.04261 | 0.21339 | 0.12885 | 0.17569 | 0.11688 | 0.24684 | 0.20917 | 0.10666 | 0.09827 | 0.20284 | 0.01867 | -0.088054 | 0.066547 | 0.068999 | 0.016875 | 0.060921 | 0.031723 | 0.081395 | -0.047877 | 0.001795
1354.3125 | 121.3943 | -0.17853 | 121.3211 | 0.048597 | -0.035942 | 0.001736 | -0.047909 | 0.082044 | 0.048956 | -0.062717 | 0.084537 | 0.17537 | -0.008798 | -0.11094 | 0.048236 | 0.050688 | -0.006014 | 0.047188 | 0.22712 | 0.14259 | 0.18026 | 0.13062 | 0.26057 | 0.22748 | 0.11581 | 0.10285 | 0.19368 | 0.009513 | -0.092633 | 0.066547 | 0.068999 | 0.012297 | 0.065499 | 0.036301 | 0.090551 | -0.057034 | -0.002784
1356.0469 | 121.4355 | -0.25177 | 121.2296 | 0.03944 | -0.0451 | 0.001736 | -0.066223 | 0.077466 | 0.035221 | -0.076452 | 0.07538 | 0.17079 | -0.008798 | -0.10637 | 0.052814 | 0.059844 | 0.03977 | 0.088392 | 0.29121 | 0.20667 | 0.25351 | 0.18555 | 0.32924 | 0.28699 | 0.17532 | 0.093691 | 0.1891 | 0.009513 | -0.088054 | 0.071125 | 0.078155 | 0.058081 | 0.1067 | 0.022566 | 0.03561 | -0.061612 | -0.048568
1357.7969 | 121.5271 | -0.16479 | 121.2753 | 0.044018 | -0.049678 | 0.001736 | -0.052488 | 0.082044 | 0.035221 | -0.071874 | 0.079959 | 0.17995 | 0.000359 | -0.10637 | 0.048236 | 0.050688 | 0.003143 | 0.047188 | 0.20881 | 0.11512 | 0.16653 | 0.11231 | 0.24684 | 0.20002 | 0.092921 | 0.09827 | 0.19826 | 0.01867 | -0.088054 | 0.066547 | 0.068999 | 0.021454 | 0.065499 | 0.031723 | 0.076816 | -0.047877 | -0.002784
1359.4844 | 121.3623 | -0.37079 | 121.1014 | 0.021127 | -0.063415 | -0.016578 | -0.070802 | 0.063733 | 0.026064 | -0.085608 | 0.034174 | 0.13874 | -0.017954 | -0.10637 | 0.089439 | 0.096469 | 0.3511 | 0.39513 | 0.39192 | 0.30737 | 0.35421 | 0.29999 | 0.43452 | 0.39685 | 0.28518 | 0.052485 | 0.15705 | 0.000357 | -0.088054 | 0.10775 | 0.11478 | 0.36941 | 0.41344 | -0.055265 | -0.31693 | -0.10739 | -0.36905
1361.2188 | 118.2678 | -92.2668 | 25.8408 | 0.057754 | -0.031363 | 0.015472 | -0.038752 | 0.095778 | 0.058113 | -0.053561 | 0.098273 | 0.19369 | 0.014094 | -0.10637 | 0.043657 | 0.032376 | 0.044348 | 0.079235 | 92.3246 | 92.2355 | 92.2823 | 92.2281 | 92.3626 | 92.325 | 92.2133 | 0.11658 | 0.212 | 0.032405 | -0.088054 | 0.061968 | 0.050687 | 0.062659 | 0.097546 | 0.054616 | 0.053925 | -0.029563 | -0.030254
1362.9375 | 119.751 | -118.9819 | 0.81482 | 0.06691 | -0.026784 | 0.020051 | -0.034174 | 0.10036 | 0.058113 | -0.048983 | 0.10285 | 0.19827 | 0.02325 | -0.11094 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 119.0488 | 118.9551 | 119.002 | 118.9478 | 119.0823 | 119.04 | 118.933 | 0.12116 | 0.21658 | 0.041561 | -0.092633 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.06835 | 0.14549 | -0.011251 | 0.065891
1364.7031 | 120.1859 | -33.4808 | 86.7142 | 0.048597 | -0.031363 | 0.020051 | -0.047909 | 0.0912 | 0.053534 | -0.062717 | 0.089116 | 0.19827 | 0.004937 | -0.11552 | 0.039079 | 0.036954 | -0.028906 | 0.005985 | 33.5294 | 33.4495 | 33.5009 | 33.4329 | 33.572 | 33.5344 | 33.4181 | 0.10743 | 0.21658 | 0.023248 | -0.097212 | 0.05739 | 0.055265 | -0.010595 | 0.024296 | 0.050037 | 0.11802 | -0.034142 | 0.033843
1366.3906 | 120.4788 | -20.7047 | 99.765 | 0.053175 | -0.031363 | 0.010893 | -0.052488 | 0.082044 | 0.044377 | -0.062717 | 0.084537 | 0.19369 | 0.004937 | -0.11552 | 0.043657 | 0.036954 | -0.028906 | 0.010563 | 20.7578 | 20.6733 | 20.7155 | 20.6522 | 20.7867 | 20.749 | 20.6419 | 0.10285 | 0.212 | 0.023248 | -0.097212 | 0.061968 | 0.055265 | -0.010595 | 0.028874 | 0.04088 | 0.11344 | -0.03872 | 0.033843
1368.1406 | 120.4559 | -24.6002 | 95.8237 | 0.053175 | -0.035942 | 0.010893 | -0.043331 | 0.0912 | 0.039799 | -0.058139 | 0.093694 | 0.18911 | 0.000359 | -0.11094 | 0.043657 | 0.036954 | -0.028906 | 0.005985 | 24.6534 | 24.5643 | 24.6111 | 24.5569 | 24.6914 | 24.64 | 24.5421 | 0.112 | 0.20742 | 0.01867 | -0.092633 | 0.061968 | 0.055265 | -0.010595 | 0.024296 | 0.050037 | 0.1226 | -0.043298 | 0.029265
1369.875 | 120.6207 | -8.0429 | 112.3581 | 0.03944 | -0.040521 | 0.001736 | -0.057066 | 0.0912 | 0.035221 | -0.058139 | 0.084537 | 0.18911 | 0.000359 | -0.11094 | 0.039079 | 0.032376 | -0.024328 | 0.005985 | 8.0823 | 8.0024 | 8.0446 | 7.9858 | 8.1341 | 8.0781 | 7.9848 | 0.10285 | 0.20742 | 0.01867 | -0.092633 | 0.05739 | 0.050687 | -0.006017 | 0.024296 | 0.045458 | 0.10887 | -0.03872 | 0.024687
1371.5625 | 120.6162 | -11.8195 | 108.7326 | 0.053175 | -0.031363 | 0.010893 | -0.047909 | 0.086622 | 0.044377 | -0.067295 | 0.093694 | 0.19827 | 0.009515 | -0.10637 | 0.043657 | 0.036954 | -0.028906 | 0.010563 | 11.8726 | 11.7881 | 11.8304 | 11.7715 | 11.9061 | 11.8638 | 11.7522 | 0.112 | 0.21658 | 0.027826 | -0.088054 | 0.061968 | 0.055265 | -0.010595 | 0.028874 | 0.050037 | 0.1226 | -0.034142 | 0.038421
1373.3125 | 119.7327 | -40.5579 | 79.2984 | 0.048597 | -0.040521 | 0.010893 | -0.052488 | 0.086622 | 0.048956 | -0.067295 | 0.084537 | 0.18911 | 0.004937 | -0.11094 | 0.034501 | 0.032376 | -0.028906 | 0.005985 | 40.6065 | 40.5173 | 40.5688 | 40.5054 | 40.6445 | 40.6068 | 40.4906 | 0.10285 | 0.20742 | 0.023248 | -0.092633 | 0.052812 | 0.050687 | -0.010595 | 0.024296 | 0.050036 | 0.11344 | -0.029564 | 0.033843
1375.0625 | 120.4376 | -117.5903 | 2.5269 | 0.06691 | -0.022205 | 0.024629 | -0.034174 | 0.10493 | 0.067269 | -0.048983 | 0.10285 | 0.212 | 0.018672 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.012328 | 117.6572 | 117.5681 | 117.615 | 117.5562 | 117.6953 | 117.6576 | 117.5413 | 0.12116 | 0.23031 | 0.036983 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.005983 | 0.06835 | 0.14091 | -0.015829 | 0.056735
1376.75 | 120.607 | -117.7231 | 2.4994 | 0.071489 | -0.022205 | 0.020051 | -0.034174 | 0.095778 | 0.053534 | -0.048983 | 0.093694 | 0.20742 | 0.009515 | -0.10637 | 0.029923 | 0.02322 | -0.042641 | 0.001406 | 117.7946 | 117.7009 | 117.7431 | 117.6889 | 117.8189 | 117.7766 | 117.6741 | 0.112 | 0.22573 | 0.027826 | -0.088054 | 0.048234 | 0.041531 | -0.02433 | 0.019717 | 0.063771 | 0.13633 | -0.020408 | 0.052156
1378.5 | 120.607 | -118.959 | 1.4923 | 0.06691 | -0.026784 | 0.024629 | -0.034174 | 0.10493 | 0.058113 | -0.053561 | 0.098273 | 0.21658 | 0.02325 | -0.11552 | 0.034501 | 0.014064 | -0.042641 | -0.003172 | 119.026 | 118.9323 | 118.9837 | 118.9249 | 119.064 | 119.0172 | 118.9055 | 0.11658 | 0.23489 | 0.041561 | -0.097212 | 0.052812 | 0.032375 | -0.02433 | 0.015139 | 0.063772 | 0.14091 | -0.011251 | 0.065891
1380.1875 | 120.575 | -118.9636 | 1.506 | 0.071489 | -0.017627 | 0.029208 | -0.034174 | 0.10493 | 0.058113 | -0.044405 | 0.10285 | 0.20742 | 0.018672 | -0.1201 | 0.025345 | 0.018642 | -0.033484 | 0.001406 | 119.0351 | 118.946 | 118.9928 | 118.9294 | 119.0686 | 119.0217 | 118.9192 | 0.12116 | 0.22573 | 0.036983 | -0.10179 | 0.043656 | 0.036953 | -0.015173 | 0.019717 | 0.077506 | 0.13633 | -0.006673 | 0.052156
1381.9219 | 120.6162 | -119.4077 | 1.1856 | 0.071489 | -0.017627 | 0.020051 | -0.038752 | 0.10493 | 0.067269 | -0.048983 | 0.10743 | 0.20742 | 0.018672 | -0.11552 | 0.025345 | 0.018642 | -0.033484 | -0.003172 | 119.4791 | 119.39 | 119.4277 | 119.3689 | 119.5126 | 119.4749 | 119.3587 | 0.12574 | 0.22573 | 0.036983 | -0.097212 | 0.043656 | 0.036953 | -0.015173 | 0.015139 | 0.082085 | 0.14091 | -0.006673 | 0.052156
1383.6562 | 120.575 | -119.3756 | 1.2222 | 0.071489 | -0.022205 | 0.029208 | -0.025017 | 0.10036 | 0.067269 | -0.044405 | 0.10743 | 0.20742 | 0.02325 | -0.11552 | 0.034501 | 0.014064 | -0.042641 | 0.001406 | 119.4471 | 119.3534 | 119.4048 | 119.3506 | 119.476 | 119.4429 | 119.3312 | 0.12574 | 0.22573 | 0.041561 | -0.097212 | 0.052812 | 0.032375 | -0.02433 | 0.019717 | 0.072929 | 0.15007 | -0.011251 | 0.065891
1385.3281 | 120.5841 | -118.6203 | 1.9821 | 0.06691 | -0.017627 | 0.038365 | -0.034174 | 0.10951 | 0.067269 | -0.053561 | 0.10743 | 0.20742 | 0.018672 | -0.11552 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 118.6872 | 118.6027 | 118.6587 | 118.5861 | 118.7298 | 118.6876 | 118.5667 | 0.12574 | 0.22573 | 0.036983 | -0.097212 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.077507 | 0.15007 | -0.011251 | 0.061313
1387.0781 | 120.4285 | -115.2145 | 4.9255 | 0.062332 | -0.022205 | 0.029208 | -0.034174 | 0.095778 | 0.062691 | -0.053561 | 0.098273 | 0.20742 | 0.018672 | -0.11094 | 0.025345 | 0.02322 | -0.038063 | -0.003172 | 115.2769 | 115.1923 | 115.2437 | 115.1804 | 115.3103 | 115.2772 | 115.161 | 0.11658 | 0.22573 | 0.036983 | -0.092633 | 0.043656 | 0.041531 | -0.019752 | 0.015139 | 0.072928 | 0.13634 | -0.006673 | 0.056735
1388.7656 | 120.5795 | -117.0456 | 3.3142 | 0.062332 | -0.022205 | 0.024629 | -0.047909 | 0.10493 | 0.048956 | -0.048983 | 0.10743 | 0.20742 | 0.02325 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | 0.005985 | 117.1079 | 117.0234 | 117.0702 | 116.9977 | 117.1505 | 117.0945 | 116.9966 | 0.12574 | 0.22573 | 0.041561 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.024296 | 0.082085 | 0.15007 | -0.002095 | 0.065891
1390.5156 | 120.6848 | -116.7801 | 3.6484 | 0.06691 | -0.022205 | 0.024629 | -0.029595 | 0.10036 | 0.062691 | -0.048983 | 0.10285 | 0.20284 | 0.02325 | -0.11552 | 0.029923 | 0.027798 | -0.033484 | 0.001406 | 116.847 | 116.7579 | 116.8047 | 116.7505 | 116.8804 | 116.8428 | 116.7311 | 0.12116 | 0.22116 | 0.041561 | -0.097212 | 0.048234 | 0.046109 | -0.015173 | 0.019717 | 0.072928 | 0.13633 | -0.006673 | 0.056734
1392.2031 | 120.5978 | -117.6773 | 2.8473 | 0.057754 | -0.031363 | 0.020051 | -0.038752 | 0.10493 | 0.067269 | -0.044405 | 0.10743 | 0.20284 | 0.02325 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 117.7351 | 117.6459 | 117.6974 | 117.6386 | 117.7822 | 117.7446 | 117.6329 | 0.12574 | 0.22116 | 0.041561 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.072929 | 0.15007 | -0.011251 | 0.065891
1393.9531 | 120.6985 | -118.0847 | 2.4307 | 0.06691 | -0.026784 | 0.020051 | -0.034174 | 0.10036 | 0.067269 | -0.039826 | 0.10743 | 0.20742 | 0.02325 | -0.11552 | 0.025345 | 0.027798 | -0.042641 | 0.010563 | 118.1516 | 118.0579 | 118.1048 | 118.0505 | 118.1851 | 118.152 | 118.0449 | 0.12574 | 0.22573 | 0.041561 | -0.097212 | 0.043656 | 0.046109 | -0.02433 | 0.028874 | 0.082085 | 0.15007 | -0.002095 | 0.065891
1395.7031 | 120.694 | -117.8604 | 2.6917 | 0.071489 | -0.008469 | 0.029208 | -0.029595 | 0.10951 | 0.058113 | -0.053561 | 0.098273 | 0.20742 | 0.018672 | -0.11552 | 0.025345 | 0.02322 | -0.038063 | -0.003172 | 117.9319 | 117.8519 | 117.8896 | 117.8308 | 117.9699 | 117.9185 | 117.8069 | 0.11658 | 0.22573 | 0.036983 | -0.097212 | 0.043656 | 0.041531 | -0.019752 | 0.015139 | 0.072928 | 0.13634 | -0.006673 | 0.056735
1397.4375 | 120.726 | -117.4118 | 3.1448 | 0.057754 | -0.022205 | 0.020051 | -0.029595 | 0.10951 | 0.058113 | -0.048983 | 0.10285 | 0.20742 | 0.02325 | -0.11094 | 0.025345 | 0.014064 | -0.04722 | -0.003172 | 117.4696 | 117.3896 | 117.4319 | 117.3822 | 117.5213 | 117.4699 | 117.3628 | 0.12116 | 0.22573 | 0.041561 | -0.092633 | 0.043656 | 0.032375 | -0.028909 | 0.015139 | 0.077506 | 0.15007 | -0.002095 | 0.07047
1399.1719 | 120.5475 | -112.0377 | 8.5052 | 0.062332 | -0.022205 | 0.029208 | -0.034174 | 0.10951 | 0.062691 | -0.053561 | 0.093694 | 0.20284 | 0.018672 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 112.1 | 112.0155 | 112.0669 | 112.0035 | 112.1472 | 112.1004 | 111.9841 | 0.112 | 0.22116 | 0.036983 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.063771 | 0.13176 | -0.011251 | 0.056735
1400.8594 | 120.6802 | -113.5025 | 6.9397 | 0.057754 | -0.026784 | 0.029208 | -0.029595 | 0.10036 | 0.058113 | -0.053561 | 0.098273 | 0.20742 | 0.014094 | -0.11094 | 0.029923 | 0.014064 | -0.042641 | -0.00775 | 113.5603 | 113.4757 | 113.5317 | 113.4729 | 113.6029 | 113.5606 | 113.4489 | 0.11658 | 0.22573 | 0.032405 | -0.092633 | 0.048234 | 0.032375 | -0.02433 | 0.010561 | 0.06835 | 0.14091 | -0.015829 | 0.056735
1402.5938 | 120.4788 | -115.8691 | 4.6463 | 0.071489 | -0.022205 | 0.024629 | -0.034174 | 0.10036 | 0.062691 | -0.044405 | 0.10743 | 0.20284 | 0.02325 | -0.1201 | 0.034501 | 0.02322 | -0.04722 | -0.003172 | 115.9406 | 115.8469 | 115.8938 | 115.835 | 115.9695 | 115.9318 | 115.8247 | 0.12574 | 0.22116 | 0.041561 | -0.10179 | 0.052812 | 0.041531 | -0.028909 | 0.015139 | 0.072929 | 0.15465 | -0.011251 | 0.07047
1404.2812 | 120.4788 | -113.0951 | 7.4203 | 0.06691 | -0.017627 | 0.024629 | -0.034174 | 0.10951 | 0.062691 | -0.053561 | 0.10285 | 0.20284 | 0.018672 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 113.162 | 113.0775 | 113.1197 | 113.0609 | 113.2046 | 113.1578 | 113.0415 | 0.12116 | 0.22116 | 0.036983 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.072928 | 0.14549 | -0.011251 | 0.061313
1406.0312 | 120.0165 | -114.1022 | 5.7037 | 0.062332 | -0.013048 | 0.029208 | -0.029595 | 0.10493 | 0.058113 | -0.044405 | 0.098273 | 0.20284 | 0.009515 | -0.11552 | 0.039079 | 0.014064 | -0.028906 | -0.00775 | 114.1645 | 114.0891 | 114.1314 | 114.0726 | 114.2071 | 114.1603 | 114.0578 | 0.11658 | 0.22116 | 0.027826 | -0.097212 | 0.05739 | 0.032375 | -0.010595 | 0.010561 | 0.059194 | 0.12718 | -0.029564 | 0.038421
1407.7188 | 120.1538 | -4.7104 | 115.2328 | 0.044018 | -0.040521 | 0.010893 | -0.052488 | 0.082044 | 0.039799 | -0.067295 | 0.079959 | 0.17995 | -0.004219 | -0.11552 | 0.039079 | 0.036954 | -0.024328 | 0.005985 | 4.7544 | 4.6699 | 4.7213 | 4.6579 | 4.7924 | 4.7502 | 4.6431 | 0.09827 | 0.19826 | 0.014092 | -0.097212 | 0.05739 | 0.055265 | -0.006017 | 0.024296 | 0.04088 | 0.10429 | -0.043298 | 0.020109
1409.4688 | 119.751 | -4.5364 | 115.8188 | 0.048597 | -0.035942 | 0.010893 | -0.052488 | 0.082044 | 0.048956 | -0.067295 | 0.070802 | 0.18911 | 0.009515 | -0.10637 | 0.052814 | 0.04611 | -0.024328 | 0.010563 | 4.585 | 4.5005 | 4.5473 | 4.484 | 4.6185 | 4.5854 | 4.4691 | 0.089113 | 0.20742 | 0.027826 | -0.088054 | 0.071125 | 0.064421 | -0.006017 | 0.028874 | 0.017988 | 0.09513 | -0.043299 | 0.033843
1411.2031 | 120.4056 | -4.3259 | 116.011 | 0.048597 | -0.035942 | 0.001736 | -0.052488 | 0.086622 | 0.048956 | -0.08103 | 0.079959 | 0.17995 | -0.004219 | -0.11094 | 0.048236 | 0.055266 | -0.019749 | 0.015141 | 4.3745 | 4.2899 | 4.3276 | 4.2734 | 4.4125 | 4.3748 | 4.2448 | 0.09827 | 0.19826 | 0.014092 | -0.092633 | 0.066547 | 0.073577 | -0.001438 | 0.033452 | 0.031723 | 0.099708 | -0.052455 | 0.01553
1412.9375 | 120.4147 | -3.8681 | 116.5695 | 0.044018 | -0.031363 | 0.010893 | -0.057066 | 0.082044 | 0.039799 | -0.058139 | 0.079959 | 0.18453 | 0.009515 | -0.11094 | 0.048236 | 0.036954 | -0.028906 | 0.010563 | 3.9121 | 3.8367 | 3.879 | 3.811 | 3.9501 | 3.9079 | 3.81 | 0.09827 | 0.20284 | 0.027826 | -0.092633 | 0.066547 | 0.055265 | -0.010595 | 0.028874 | 0.031723 | 0.10887 | -0.038721 | 0.038421
1414.625 | 119.5724 | -3.7033 | 116.6931 | 0.03944 | -0.040521 | -0.002842 | -0.052488 | 0.082044 | 0.044377 | -0.071874 | 0.066223 | 0.18453 | -0.004219 | -0.11094 | 0.043657 | 0.041532 | -0.028906 | 0.005985 | 3.7427 | 3.6628 | 3.7005 | 3.6508 | 3.7854 | 3.7477 | 3.6314 | 0.084534 | 0.20284 | 0.014092 | -0.092633 | 0.061968 | 0.059843 | -0.010595 | 0.024296 | 0.022566 | 0.095129 | -0.047876 | 0.024687
1416.3594 | 120.488 | -3.3737 | 117.0822 | 0.048597 | -0.035942 | 0.006315 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.07538 | 0.17537 | 0.004937 | -0.11094 | 0.048236 | 0.041532 | -0.033484 | 0.010563 | 3.4223 | 3.3378 | 3.38 | 3.3304 | 3.4512 | 3.4135 | 3.3064 | 0.093691 | 0.19368 | 0.023248 | -0.092633 | 0.066547 | 0.059843 | -0.015173 | 0.028874 | 0.027144 | 0.10886 | -0.043299 | 0.038421
1418.0938 | 120.5841 | -3.3737 | 117.1051 | 0.044018 | -0.040521 | 0.010893 | -0.057066 | 0.082044 | 0.035221 | -0.062717 | 0.07538 | 0.17995 | -0.004219 | -0.11094 | 0.039079 | 0.036954 | -0.028906 | 0.005985 | 3.4177 | 3.3332 | 3.3846 | 3.3167 | 3.4558 | 3.4089 | 3.311 | 0.093691 | 0.19826 | 0.014092 | -0.092633 | 0.05739 | 0.055265 | -0.010595 | 0.024296 | 0.036301 | 0.10429 | -0.043298 | 0.024687
1419.8438 | 119.957 | -119.7876 | 0.21057 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10493 | 0.067269 | -0.048983 | 0.10285 | 0.20284 | 0.018672 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 119.8545 | 119.77 | 119.8168 | 119.758 | 119.8925 | 119.8549 | 119.7386 | 0.12116 | 0.22116 | 0.036983 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.06835 | 0.14549 | -0.015829 | 0.061313
1421.5781 | 120.108 | -119.8425 | 0.1831 | 0.06691 | -0.013048 | 0.024629 | -0.025017 | 0.10036 | 0.067269 | -0.053561 | 0.10285 | 0.20742 | 0.02325 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 119.9094 | 119.8295 | 119.8672 | 119.8175 | 119.9429 | 119.9098 | 119.789 | 0.12116 | 0.22573 | 0.041561 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.072928 | 0.14549 | -0.006673 | 0.065891
1423.2656 | 115.6769 | -83.606 | 31.8695 | 0.071489 | -0.026784 | 0.020051 | -0.043331 | 0.10951 | 0.058113 | -0.053561 | 0.093694 | 0.19369 | 0.018672 | -0.11094 | 0.039079 | 0.032376 | -0.038063 | -0.003172 | 83.6774 | 83.5792 | 83.626 | 83.5626 | 83.7155 | 83.6641 | 83.5524 | 0.112 | 0.212 | 0.036983 | -0.092633 | 0.05739 | 0.050687 | -0.019752 | 0.015139 | 0.054615 | 0.13176 | -0.020407 | 0.056735
1425.0156 | 119.8517 | -119.5999 | 0.16022 | 0.06691 | -0.017627 | 0.024629 | -0.034174 | 0.10493 | 0.058113 | -0.044405 | 0.10285 | 0.20742 | 0.018672 | -0.11552 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 119.6668 | 119.5823 | 119.6245 | 119.5657 | 119.7048 | 119.658 | 119.5555 | 0.12116 | 0.22573 | 0.036983 | -0.097212 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.06835 | 0.14549 | -0.015829 | 0.061313
1426.6875 | 119.9112 | -119.7784 | 0.19684 | 0.062332 | -0.013048 | 0.020051 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.10285 | 0.20284 | 0.02325 | -0.11552 | 0.025345 | 0.027798 | -0.033484 | -0.00775 | 119.8408 | 119.7654 | 119.7985 | 119.7488 | 119.8834 | 119.8411 | 119.734 | 0.12116 | 0.22116 | 0.041561 | -0.097212 | 0.043656 | 0.046109 | -0.015173 | 0.010561 | 0.077506 | 0.13633 | -0.002095 | 0.056734
1428.4219 | 120.1218 | -119.8196 | 0.16937 | 0.06691 | -0.022205 | 0.024629 | -0.025017 | 0.10493 | 0.067269 | -0.044405 | 0.10743 | 0.20742 | 0.009515 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 119.8866 | 119.7974 | 119.8443 | 119.7946 | 119.9246 | 119.8869 | 119.7752 | 0.12574 | 0.22573 | 0.027826 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.082085 | 0.14549 | -0.01583 | 0.047578
1430.1094 | 120.1904 | -119.8517 | 0.13733 | 0.06691 | -0.017627 | 0.024629 | -0.029595 | 0.10493 | 0.058113 | -0.044405 | 0.098273 | 0.20742 | 0.02325 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 119.9186 | 119.8341 | 119.8763 | 119.8221 | 119.9566 | 119.9098 | 119.8073 | 0.11658 | 0.22573 | 0.041561 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.06835 | 0.14091 | -0.006673 | 0.065891
1431.8594 | 120.1447 | -119.7418 | 0.31586 | 0.06691 | -0.017627 | 0.029208 | -0.034174 | 0.10493 | 0.058113 | -0.048983 | 0.098273 | 0.20284 | 0.027829 | -0.12468 | 0.020767 | 0.02322 | -0.042641 | 0.001406 | 119.8087 | 119.7242 | 119.771 | 119.7076 | 119.8468 | 119.7999 | 119.6928 | 0.11658 | 0.22116 | 0.04614 | -0.10637 | 0.039078 | 0.041531 | -0.02433 | 0.019717 | 0.077506 | 0.14091 | 0.007062 | 0.07047
1433.5938 | 120.1309 | -119.87 | 0.21973 | 0.06691 | -0.013048 | 0.029208 | -0.029595 | 0.10493 | 0.062691 | -0.048983 | 0.10743 | 0.20284 | 0.02325 | -0.1201 | 0.020767 | 0.018642 | -0.038063 | -0.003172 | 119.9369 | 119.8569 | 119.8992 | 119.8404 | 119.9749 | 119.9327 | 119.821 | 0.12574 | 0.22116 | 0.041561 | -0.10179 | 0.039078 | 0.036953 | -0.019752 | 0.015139 | 0.086663 | 0.14549 | 0.002483 | 0.061313
1435.3438 | 120.2225 | -120.0302 | 0.19226 | 0.071489 | -0.017627 | 0.024629 | -0.034174 | 0.10493 | 0.067269 | -0.039826 | 0.098273 | 0.20742 | 0.02325 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | 0.001406 | 120.1017 | 120.0126 | 120.0548 | 119.996 | 120.1351 | 120.0975 | 119.9904 | 0.11658 | 0.22573 | 0.041561 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.019717 | 0.06835 | 0.13634 | -0.006673 | 0.061313
1437.0469 | 120.3094 | -120.0394 | 0.17853 | 0.06691 | -0.013048 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.098273 | 0.20742 | 0.032407 | -0.11552 | 0.034501 | 0.018642 | -0.04722 | 0.001406 | 120.1063 | 120.0263 | 120.064 | 120.0144 | 120.1489 | 120.1066 | 119.9904 | 0.11658 | 0.22573 | 0.050718 | -0.097212 | 0.052812 | 0.036953 | -0.028909 | 0.019717 | 0.063772 | 0.14549 | -0.002094 | 0.079627
1438.7969 | 120.1904 | -119.9615 | 0.30212 | 0.06691 | -0.008469 | 0.024629 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.098273 | 0.20284 | 0.018672 | -0.11552 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 120.0285 | 119.9531 | 119.9862 | 119.932 | 120.0665 | 120.0288 | 119.9171 | 0.11658 | 0.22116 | 0.036983 | -0.097212 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.06835 | 0.13634 | -0.011251 | 0.056735
1440.5469 | 120.2499 | -120.1218 | 0.19226 | 0.062332 | -0.017627 | 0.029208 | -0.025017 | 0.10493 | 0.062691 | -0.044405 | 0.10285 | 0.20742 | 0.018672 | -0.11552 | 0.025345 | 0.014064 | -0.042641 | -0.00775 | 120.1841 | 120.1041 | 120.151 | 120.0967 | 120.2267 | 120.1845 | 120.0774 | 0.12116 | 0.22573 | 0.036983 | -0.097212 | 0.043656 | 0.032375 | -0.02433 | 0.010561 | 0.077506 | 0.14549 | -0.006673 | 0.061313
1442.2188 | 120.2682 | -120.1538 | 0.19226 | 0.06691 | -0.013048 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.098273 | 0.20742 | 0.014094 | -0.1201 | 0.025345 | 0.018642 | -0.033484 | -0.003172 | 120.2207 | 120.1408 | 120.183 | 120.1288 | 120.2633 | 120.2211 | 120.1048 | 0.11658 | 0.22573 | 0.032405 | -0.10179 | 0.043656 | 0.036953 | -0.015173 | 0.015139 | 0.072928 | 0.13176 | -0.011251 | 0.047578
1443.9688 | 120.2957 | -120.1675 | 0.1831 | 0.062332 | -0.013048 | 0.024629 | -0.029595 | 0.10951 | 0.062691 | -0.048983 | 0.10743 | 0.20284 | 0.018672 | -0.11552 | 0.025345 | 0.018642 | -0.038063 | -0.00775 | 120.2299 | 120.1545 | 120.1922 | 120.1379 | 120.2771 | 120.2302 | 120.1186 | 0.12574 | 0.22116 | 0.036983 | -0.097212 | 0.043656 | 0.036953 | -0.019752 | 0.010561 | 0.082085 | 0.14549 | -0.006673 | 0.056735
1445.7188 | 120.2591 | -119.7784 | 0.50812 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.10493 | 0.067269 | -0.048983 | 0.098273 | 0.212 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 119.8499 | 119.7608 | 119.8076 | 119.7534 | 119.8834 | 119.8457 | 119.7295 | 0.11658 | 0.23031 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.06835 | 0.13634 | -0.002094 | 0.065892
1447.4688 | 120.369 | -120.2133 | 0.1831 | 0.071489 | -0.017627 | 0.024629 | -0.025017 | 0.10951 | 0.062691 | -0.044405 | 0.098273 | 0.20284 | 0.02325 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | 0.001406 | 120.2848 | 120.1957 | 120.2379 | 120.1883 | 120.3228 | 120.276 | 120.1689 | 0.11658 | 0.22116 | 0.041561 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.019717 | 0.072928 | 0.14091 | -0.002095 | 0.065891
1449.1562 | 120.3552 | -120.2408 | 0.19684 | 0.071489 | -0.022205 | 0.024629 | -0.029595 | 0.10493 | 0.062691 | -0.048983 | 0.10285 | 0.20742 | 0.02325 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.00775 | 120.3123 | 120.2186 | 120.2654 | 120.2112 | 120.3457 | 120.3035 | 120.1918 | 0.12116 | 0.22573 | 0.041561 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.010561 | 0.072928 | 0.14091 | -0.006673 | 0.061313
1450.8906 | 120.4056 | -120.0439 | 0.28381 | 0.06691 | -0.013048 | 0.029208 | -0.025017 | 0.10493 | 0.062691 | -0.048983 | 0.10285 | 0.212 | 0.02325 | -0.11552 | 0.029923 | 0.014064 | -0.04722 | -0.003172 | 120.1109 | 120.0309 | 120.0732 | 120.0189 | 120.1489 | 120.1066 | 119.995 | 0.12116 | 0.23031 | 0.041561 | -0.097212 | 0.048234 | 0.032375 | -0.028909 | 0.015139 | 0.072928 | 0.15007 | -0.006673 | 0.07047
1452.6406 | 120.4376 | -120.1996 | 0.16937 | 0.06691 | -0.008469 | 0.029208 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.10285 | 0.20742 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 120.2665 | 120.1911 | 120.2288 | 120.17 | 120.3045 | 120.2623 | 120.1552 | 0.12116 | 0.22573 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.077506 | 0.14091 | 0.002484 | 0.065892
1454.3438 | 120.4742 | -120.2271 | 0.15106 | 0.062332 | -0.017627 | 0.029208 | -0.029595 | 0.10036 | 0.071848 | -0.048983 | 0.098273 | 0.20742 | 0.018672 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | -0.003172 | 120.2894 | 120.2094 | 120.2563 | 120.1975 | 120.3274 | 120.2989 | 120.1781 | 0.11658 | 0.22573 | 0.036983 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.015139 | 0.072928 | 0.13634 | -0.006673 | 0.056735
1456.0938 | 120.5109 | -120.2133 | 0.14191 | 0.06691 | -0.013048 | 0.029208 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.098273 | 0.19369 | 0.02325 | -0.11094 | 0.025345 | 0.02322 | -0.038063 | -0.003172 | 120.2802 | 120.2003 | 120.2425 | 120.1837 | 120.3183 | 120.2806 | 120.1689 | 0.11658 | 0.212 | 0.041561 | -0.092633 | 0.043656 | 0.041531 | -0.019752 | 0.015139 | 0.072928 | 0.13634 | -0.002095 | 0.061313
1457.7969 | 120.4971 | -120.2408 | 0.19684 | 0.071489 | -0.017627 | 0.024629 | -0.029595 | 0.10951 | 0.067269 | -0.044405 | 0.10285 | 0.212 | 0.027829 | -0.12468 | 0.043657 | 0.018642 | -0.038063 | -0.003172 | 120.3123 | 120.2232 | 120.2654 | 120.2112 | 120.3503 | 120.3081 | 120.1964 | 0.12116 | 0.23031 | 0.04614 | -0.10637 | 0.061968 | 0.036953 | -0.019752 | 0.015139 | 0.059194 | 0.14091 | -0.015828 | 0.065892
1459.5156 | 120.1813 | -119.8471 | 0.15564 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.058113 | -0.048983 | 0.098273 | 0.20742 | 0.032407 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | -0.00775 | 119.914 | 119.8295 | 119.8763 | 119.8175 | 119.9566 | 119.9052 | 119.7981 | 0.11658 | 0.22573 | 0.050718 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.010561 | 0.072928 | 0.14091 | 0.007062 | 0.075048
1461.2656 | 120.4422 | -120.1904 | 0.2243 | 0.076067 | -0.017627 | 0.029208 | -0.034174 | 0.10951 | 0.067269 | -0.048983 | 0.10285 | 0.20284 | 0.02325 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 120.2665 | 120.1728 | 120.2196 | 120.1563 | 120.2999 | 120.2577 | 120.1414 | 0.12116 | 0.22116 | 0.041561 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.072928 | 0.14091 | -0.006673 | 0.061313
1463.0156 | 120.3552 | -119.8929 | 0.51727 | 0.071489 | -0.013048 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.10285 | 0.20284 | 0.02325 | -0.12468 | 0.029923 | 0.02322 | -0.033484 | -0.003172 | 119.9644 | 119.8798 | 119.9175 | 119.8724 | 120.0024 | 119.9602 | 119.8531 | 0.12116 | 0.22116 | 0.041561 | -0.10637 | 0.048234 | 0.041531 | -0.015173 | 0.015139 | 0.072928 | 0.13633 | -0.006673 | 0.056734
1464.7031 | 120.4742 | -120.2911 | 0.19226 | 0.071489 | -0.017627 | 0.024629 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.098273 | 0.20742 | 0.02325 | -0.11094 | 0.034501 | 0.014064 | -0.042641 | -0.003172 | 120.3626 | 120.2735 | 120.3158 | 120.2615 | 120.3961 | 120.3538 | 120.2467 | 0.11658 | 0.22573 | 0.041561 | -0.092633 | 0.052812 | 0.032375 | -0.02433 | 0.015139 | 0.063772 | 0.14091 | -0.011251 | 0.065891
1466.4375 | 120.607 | -120.2728 | 0.15106 | 0.071489 | -0.017627 | 0.024629 | -0.029595 | 0.10493 | 0.062691 | -0.053561 | 0.098273 | 0.20284 | 0.018672 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | 0.001406 | 120.3443 | 120.2552 | 120.2975 | 120.2432 | 120.3778 | 120.3355 | 120.2193 | 0.11658 | 0.22116 | 0.036983 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.019717 | 0.063772 | 0.13634 | -0.015829 | 0.056735
1468.1719 | 120.3003 | -119.2337 | 0.97961 | 0.06691 | -0.013048 | 0.024629 | -0.029595 | 0.11409 | 0.058113 | -0.039826 | 0.10285 | 0.20284 | 0.027829 | -0.11094 | 0.025345 | 0.027798 | -0.042641 | -0.012328 | 119.3006 | 119.2207 | 119.2583 | 119.2041 | 119.3478 | 119.2918 | 119.1939 | 0.12116 | 0.22116 | 0.04614 | -0.092633 | 0.043656 | 0.046109 | -0.02433 | 0.005983 | 0.077506 | 0.14549 | 0.002484 | 0.07047
1469.9219 | 120.3735 | -119.7327 | 0.53101 | 0.071489 | -0.013048 | 0.029208 | -0.029595 | 0.10951 | 0.067269 | -0.039826 | 0.10285 | 0.19827 | 0.02325 | -0.11094 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 119.8042 | 119.7196 | 119.7619 | 119.7031 | 119.8422 | 119.7999 | 119.6928 | 0.12116 | 0.21658 | 0.041561 | -0.092633 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.072928 | 0.14091 | -0.006673 | 0.061313
1471.5938 | 120.5429 | -120.2866 | 0.15106 | 0.071489 | -0.017627 | 0.020051 | -0.034174 | 0.11409 | 0.067269 | -0.048983 | 0.093694 | 0.20742 | 0.02325 | -0.11552 | 0.025345 | 0.014064 | -0.04722 | -0.003172 | 120.358 | 120.2689 | 120.3066 | 120.2524 | 120.4006 | 120.3538 | 120.2376 | 0.112 | 0.22573 | 0.041561 | -0.097212 | 0.043656 | 0.032375 | -0.028909 | 0.015139 | 0.068349 | 0.14091 | -0.002095 | 0.07047
1473.3281 | 120.4605 | -120.369 | 0.18768 | 0.071489 | -0.008469 | 0.029208 | -0.029595 | 0.10951 | 0.058113 | -0.044405 | 0.098273 | 0.20742 | 0.018672 | -0.11094 | 0.025345 | 0.014064 | -0.04722 | 0.001406 | 120.4404 | 120.3605 | 120.3982 | 120.3394 | 120.4785 | 120.4271 | 120.3246 | 0.11658 | 0.22573 | 0.036983 | -0.092633 | 0.043656 | 0.032375 | -0.028909 | 0.019717 | 0.072928 | 0.14549 | -0.006673 | 0.065892
1475.0781 | 120.5292 | -120.3827 | 0.18768 | 0.071489 | -0.013048 | 0.029208 | -0.038752 | 0.10951 | 0.062691 | -0.044405 | 0.10285 | 0.20742 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.4542 | 120.3696 | 120.4119 | 120.3439 | 120.4922 | 120.4454 | 120.3383 | 0.12116 | 0.22573 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.072928 | 0.14549 | -0.002094 | 0.07047
1476.7656 | 120.5795 | -120.3232 | 0.16022 | 0.071489 | -0.013048 | 0.024629 | -0.025017 | 0.10951 | 0.062691 | -0.039826 | 0.10743 | 0.20284 | 0.02325 | -0.11094 | 0.029923 | 0.009486 | -0.04722 | -0.012328 | 120.3947 | 120.3101 | 120.3478 | 120.2982 | 120.4327 | 120.3859 | 120.2834 | 0.12574 | 0.22116 | 0.041561 | -0.092633 | 0.048234 | 0.027797 | -0.028909 | 0.005983 | 0.077507 | 0.15465 | -0.006673 | 0.07047
1478.5 | 120.639 | -120.3461 | 0.13733 | 0.062332 | -0.017627 | 0.029208 | -0.029595 | 0.11867 | 0.067269 | -0.048983 | 0.10285 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | 0.001406 | 120.4084 | 120.3284 | 120.3753 | 120.3165 | 120.4647 | 120.4133 | 120.2971 | 0.12116 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.019717 | 0.072928 | 0.14091 | -0.002094 | 0.065892
1480.25 | 120.5612 | -120.4193 | 0.16937 | 0.071489 | -0.013048 | 0.033786 | -0.029595 | 0.10951 | 0.062691 | -0.044405 | 0.10285 | 0.20742 | 0.027829 | -0.11552 | 0.020767 | 0.018642 | -0.038063 | 0.001406 | 120.4908 | 120.4063 | 120.4531 | 120.3897 | 120.5288 | 120.482 | 120.3749 | 0.12116 | 0.22573 | 0.04614 | -0.097212 | 0.039078 | 0.036953 | -0.019752 | 0.019717 | 0.082084 | 0.14091 | 0.007062 | 0.065892
1481.9375 | 120.5887 | -120.3964 | 0.18768 | 0.071489 | -0.013048 | 0.029208 | -0.025017 | 0.10493 | 0.071848 | -0.048983 | 0.098273 | 0.212 | 0.027829 | -0.11552 | 0.025345 | 0.018642 | -0.038063 | -0.00775 | 120.4679 | 120.3834 | 120.4256 | 120.3714 | 120.5014 | 120.4683 | 120.3474 | 0.11658 | 0.23031 | 0.04614 | -0.097212 | 0.043656 | 0.036953 | -0.019752 | 0.010561 | 0.072928 | 0.13634 | 0.002484 | 0.065892
1483.6094 | 120.5246 | -119.8059 | 0.6134 | 0.06691 | -0.013048 | 0.029208 | -0.025017 | 0.10493 | 0.058113 | -0.039826 | 0.10285 | 0.20742 | 0.027829 | -0.11094 | 0.034501 | 0.014064 | -0.042641 | -0.003172 | 119.8728 | 119.7929 | 119.8351 | 119.7809 | 119.9108 | 119.864 | 119.7661 | 0.12116 | 0.22573 | 0.04614 | -0.092633 | 0.052812 | 0.032375 | -0.02433 | 0.015139 | 0.06835 | 0.14549 | -0.006672 | 0.07047
1485.3594 | 120.6665 | -120.076 | 0.46692 | 0.071489 | -0.017627 | 0.029208 | -0.01586 | 0.11867 | 0.071848 | -0.039826 | 0.098273 | 0.20284 | 0.036985 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | -0.00775 | 120.1475 | 120.0584 | 120.1052 | 120.0601 | 120.1947 | 120.1478 | 120.0362 | 0.11658 | 0.22116 | 0.055296 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.010561 | 0.072928 | 0.14091 | 0.01164 | 0.079626
1487.1094 | 120.5612 | -120.2271 | 0.31586 | 0.071489 | -0.017627 | 0.024629 | -0.025017 | 0.11409 | 0.062691 | -0.035248 | 0.098273 | 0.19827 | 0.02325 | -0.11552 | 0.034501 | 0.018642 | -0.038063 | -0.003172 | 120.2985 | 120.2094 | 120.2517 | 120.202 | 120.3411 | 120.2897 | 120.1918 | 0.11658 | 0.21658 | 0.041561 | -0.097212 | 0.052812 | 0.036953 | -0.019752 | 0.015139 | 0.063772 | 0.13634 | -0.011251 | 0.061313
1488.7969 | 120.5795 | -120.0439 | 0.44403 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.11409 | 0.067269 | -0.039826 | 0.098273 | 0.20742 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | -0.00775 | 120.1109 | 120.0263 | 120.0732 | 120.0143 | 120.158 | 120.1112 | 120.0041 | 0.11658 | 0.22573 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.010561 | 0.072928 | 0.14091 | 0.007062 | 0.075048
1490.5469 | 120.3278 | -120.0623 | 0.17395 | 0.076067 | -0.013048 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.098273 | 0.212 | 0.027829 | -0.11094 | 0.034501 | 0.018642 | -0.051798 | -0.00775 | 120.1383 | 120.0492 | 120.0915 | 120.0372 | 120.1718 | 120.1295 | 120.0224 | 0.11658 | 0.23031 | 0.04614 | -0.092633 | 0.052812 | 0.036953 | -0.033487 | 0.010561 | 0.063772 | 0.15007 | -0.006672 | 0.079627
1492.2344 | 120.52 | -120.1996 | 0.15564 | 0.062332 | -0.017627 | 0.024629 | -0.029595 | 0.11409 | 0.062691 | -0.044405 | 0.10285 | 0.19827 | 0.02325 | -0.1201 | 0.025345 | 0.014064 | -0.04722 | -0.012328 | 120.2619 | 120.182 | 120.2242 | 120.17 | 120.3137 | 120.2623 | 120.1552 | 0.12116 | 0.21658 | 0.041561 | -0.10179 | 0.043656 | 0.032375 | -0.028909 | 0.005983 | 0.077506 | 0.15007 | -0.002095 | 0.07047
1493.9844 | 120.5841 | -120.2362 | 0.15106 | 0.071489 | -0.017627 | 0.029208 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.098273 | 0.20284 | 0.027829 | -0.11552 | 0.029923 | 0.014064 | -0.042641 | 0.001406 | 120.3077 | 120.2186 | 120.2654 | 120.2066 | 120.3411 | 120.3035 | 120.1918 | 0.11658 | 0.22116 | 0.04614 | -0.097212 | 0.048234 | 0.032375 | -0.02433 | 0.019717 | 0.06835 | 0.14091 | -0.002094 | 0.07047
1495.6719 | 120.4697 | -120.3598 | 0.18768 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.062691 | -0.044405 | 0.098273 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.04722 | -0.003172 | 120.4267 | 120.3422 | 120.389 | 120.3302 | 120.4693 | 120.4225 | 120.3154 | 0.11658 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.028909 | 0.015139 | 0.06835 | 0.14549 | -0.002094 | 0.075049
1497.4062 | 120.5429 | -119.902 | 0.53101 | 0.071489 | -0.017627 | 0.033786 | -0.029595 | 0.10493 | 0.067269 | -0.048983 | 0.10285 | 0.20284 | 0.032407 | -0.11552 | 0.029923 | 0.009486 | -0.04722 | -0.003172 | 119.9735 | 119.8844 | 119.9358 | 119.8724 | 120.007 | 119.9693 | 119.8531 | 0.12116 | 0.22116 | 0.050718 | -0.097212 | 0.048234 | 0.027797 | -0.028909 | 0.015139 | 0.072928 | 0.15007 | 0.002484 | 0.079627
1499.1562 | 120.5841 | -119.9799 | 0.45776 | 0.06691 | -0.013048 | 0.024629 | -0.025017 | 0.11409 | 0.062691 | -0.048983 | 0.098273 | 0.20284 | 0.018672 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | -0.00775 | 120.0468 | 119.9668 | 120.0045 | 119.9548 | 120.0939 | 120.0425 | 119.9309 | 0.11658 | 0.22116 | 0.036983 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.010561 | 0.072928 | 0.13634 | -0.006673 | 0.056735
1500.9062 | 120.5612 | -120.401 | 0.20142 | 0.06691 | -0.013048 | 0.024629 | -0.029595 | 0.10951 | 0.067269 | -0.044405 | 0.098273 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.02322 | -0.033484 | -0.003172 | 120.4679 | 120.388 | 120.4256 | 120.3714 | 120.5105 | 120.4683 | 120.3566 | 0.11658 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.041531 | -0.015173 | 0.015139 | 0.06835 | 0.13176 | -0.002094 | 0.061313
1502.6406 | 120.6665 | -120.4147 | 0.17853 | 0.071489 | -0.013048 | 0.024629 | -0.025017 | 0.11867 | 0.071848 | -0.048983 | 0.093694 | 0.20284 | 0.036985 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | -0.012328 | 120.4862 | 120.4017 | 120.4394 | 120.3897 | 120.5334 | 120.4866 | 120.3658 | 0.112 | 0.22116 | 0.055296 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.005983 | 0.059193 | 0.13633 | 0.002484 | 0.079626
1504.3281 | 120.5887 | -120.4193 | 0.18768 | 0.071489 | -0.017627 | 0.033786 | -0.038752 | 0.10493 | 0.076426 | -0.044405 | 0.10285 | 0.20284 | 0.02325 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | 0.001406 | 120.4908 | 120.4017 | 120.4531 | 120.3806 | 120.5242 | 120.4957 | 120.3749 | 0.12116 | 0.22116 | 0.041561 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.019717 | 0.077506 | 0.14091 | -0.002095 | 0.061313
1506.0781 | 120.5978 | -120.4102 | 0.24261 | 0.06691 | -0.013048 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.098273 | 0.20284 | 0.032407 | -0.11552 | 0.034501 | 0.014064 | -0.042641 | 0.001406 | 120.4771 | 120.3971 | 120.4394 | 120.3851 | 120.5197 | 120.4774 | 120.3612 | 0.11658 | 0.22116 | 0.050718 | -0.097212 | 0.052812 | 0.032375 | -0.02433 | 0.019717 | 0.063772 | 0.14091 | -0.002094 | 0.075048
1507.8281 | 120.7123 | -120.3918 | 0.1831 | 0.071489 | -0.013048 | 0.024629 | -0.038752 | 0.10036 | 0.062691 | -0.039826 | 0.10743 | 0.20284 | 0.027829 | -0.11552 | 0.020767 | 0.02322 | -0.042641 | -0.00775 | 120.4633 | 120.3788 | 120.4165 | 120.3531 | 120.4922 | 120.4545 | 120.352 | 0.12574 | 0.22116 | 0.04614 | -0.097212 | 0.039078 | 0.041531 | -0.02433 | 0.010561 | 0.086663 | 0.15007 | 0.007062 | 0.07047
1509.5781 | 120.6757 | -120.1126 | 0.42114 | 0.071489 | -0.008469 | 0.033786 | -0.025017 | 0.11409 | 0.067269 | -0.039826 | 0.098273 | 0.20284 | 0.027829 | -0.1201 | 0.025345 | 0.018642 | -0.028906 | -0.012328 | 120.1841 | 120.1041 | 120.1464 | 120.0876 | 120.2267 | 120.1799 | 120.0728 | 0.11658 | 0.22116 | 0.04614 | -0.10179 | 0.043656 | 0.036953 | -0.010595 | 0.005983 | 0.072928 | 0.12718 | 0.002484 | 0.056735
1511.3125 | 120.5566 | -119.6503 | 0.81482 | 0.076067 | -0.008469 | 0.033786 | -0.034174 | 0.10951 | 0.071848 | -0.048983 | 0.098273 | 0.19827 | 0.027829 | -0.11552 | 0.020767 | 0.02322 | -0.042641 | -0.003172 | 119.7263 | 119.6418 | 119.6841 | 119.6161 | 119.7598 | 119.7221 | 119.6013 | 0.11658 | 0.21658 | 0.04614 | -0.097212 | 0.039078 | 0.041531 | -0.02433 | 0.015139 | 0.077506 | 0.14091 | 0.007062 | 0.07047
1513 | 120.6162 | -119.8013 | 0.60425 | 0.071489 | -0.017627 | 0.029208 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.093694 | 0.20742 | 0.032407 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | -0.012328 | 119.8728 | 119.7837 | 119.8305 | 119.7717 | 119.9063 | 119.864 | 119.7569 | 0.112 | 0.22573 | 0.050718 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.005983 | 0.063771 | 0.13176 | 0.002484 | 0.07047
1514.7344 | 120.5978 | -120.3918 | 0.24261 | 0.06691 | -0.008469 | 0.033786 | -0.020438 | 0.10951 | 0.067269 | -0.044405 | 0.098273 | 0.20742 | 0.02325 | -0.11552 | 0.020767 | 0.018642 | -0.04722 | -0.00775 | 120.4588 | 120.3834 | 120.4256 | 120.3714 | 120.5014 | 120.4591 | 120.3474 | 0.11658 | 0.22573 | 0.041561 | -0.097212 | 0.039078 | 0.036953 | -0.028909 | 0.010561 | 0.077506 | 0.14549 | 0.002483 | 0.07047
1516.4844 | 120.6482 | -120.3461 | 0.24719 | 0.06691 | -0.008469 | 0.020051 | -0.025017 | 0.10493 | 0.071848 | -0.044405 | 0.098273 | 0.20284 | 0.018672 | -0.12468 | 0.025345 | 0.02322 | -0.042641 | -0.012328 | 120.413 | 120.3376 | 120.3661 | 120.3211 | 120.451 | 120.4179 | 120.3017 | 0.11658 | 0.22116 | 0.036983 | -0.10637 | 0.043656 | 0.041531 | -0.02433 | 0.005983 | 0.072928 | 0.14091 | -0.006673 | 0.061313
1518.1719 | 120.52 | -120.0211 | 0.55389 | 0.071489 | -0.017627 | 0.029208 | -0.034174 | 0.10951 | 0.071848 | -0.044405 | 0.093694 | 0.20284 | 0.027829 | -0.1201 | 0.029923 | 0.014064 | -0.042641 | 0.005985 | 120.0925 | 120.0034 | 120.0503 | 119.9869 | 120.1306 | 120.0929 | 119.9767 | 0.112 | 0.22116 | 0.04614 | -0.10179 | 0.048234 | 0.032375 | -0.02433 | 0.024296 | 0.063771 | 0.13633 | -0.002094 | 0.07047
1519.9062 | 120.6482 | -120.4651 | 0.1831 | 0.071489 | -0.013048 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.098273 | 0.20284 | 0.027829 | -0.11094 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 120.5366 | 120.452 | 120.4943 | 120.4401 | 120.5746 | 120.5324 | 120.4161 | 0.11658 | 0.22116 | 0.04614 | -0.092633 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.063772 | 0.13634 | -0.006672 | 0.065892
1521.6406 | 119.9615 | -119.6045 | 0.21057 | 0.076067 | -0.008469 | 0.033786 | -0.029595 | 0.10493 | 0.062691 | -0.039826 | 0.093694 | 0.20284 | 0.02325 | -0.11552 | 0.020767 | 0.009486 | -0.04722 | -0.003172 | 119.6806 | 119.596 | 119.6383 | 119.5749 | 119.7094 | 119.6672 | 119.5647 | 0.112 | 0.22116 | 0.041561 | -0.097212 | 0.039078 | 0.027797 | -0.028909 | 0.015139 | 0.072927 | 0.14091 | 0.002483 | 0.07047
1523.3125 | 120.488 | -120.1859 | 0.15106 | 0.071489 | -0.008469 | 0.033786 | -0.029595 | 0.10036 | 0.062691 | -0.044405 | 0.10285 | 0.20742 | 0.02325 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | 0.001406 | 120.2573 | 120.1774 | 120.2196 | 120.1563 | 120.2862 | 120.2485 | 120.1414 | 0.12116 | 0.22573 | 0.041561 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.019717 | 0.077506 | 0.14549 | -0.002095 | 0.065891
1525.0469 | 120.401 | -119.9478 | 0.43488 | 0.06691 | -0.013048 | 0.024629 | -0.029595 | 0.10951 | 0.071848 | -0.039826 | 0.093694 | 0.20742 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.0147 | 119.9348 | 119.9724 | 119.9182 | 120.0573 | 120.0197 | 119.908 | 0.112 | 0.22573 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.063771 | 0.13633 | -0.002094 | 0.07047
1526.7969 | 120.5063 | -120.3186 | 0.17853 | 0.06691 | -0.008469 | 0.024629 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.098273 | 0.20284 | 0.027829 | -0.11094 | 0.020767 | 0.02322 | -0.042641 | 0.001406 | 120.3855 | 120.3101 | 120.3432 | 120.2982 | 120.4235 | 120.3859 | 120.2788 | 0.11658 | 0.22116 | 0.04614 | -0.092633 | 0.039078 | 0.041531 | -0.02433 | 0.019717 | 0.077506 | 0.14091 | 0.007062 | 0.07047
1528.5469 | 120.5658 | -120.1904 | 0.14191 | 0.06691 | -0.026784 | 0.024629 | -0.029595 | 0.10951 | 0.062691 | -0.044405 | 0.093694 | 0.20284 | 0.036985 | -0.11552 | 0.025345 | 0.02322 | -0.04722 | 0.001406 | 120.2573 | 120.1636 | 120.2151 | 120.1608 | 120.2999 | 120.2531 | 120.146 | 0.112 | 0.22116 | 0.055296 | -0.097212 | 0.043656 | 0.041531 | -0.028909 | 0.019717 | 0.068349 | 0.14091 | 0.01164 | 0.084205
1530.2344 | 120.5246 | -120.3827 | 0.14191 | 0.06691 | -0.013048 | 0.024629 | -0.034174 | 0.10951 | 0.053534 | -0.044405 | 0.093694 | 0.20284 | 0.027829 | -0.11552 | 0.029923 | 0.014064 | -0.038063 | -0.003172 | 120.4496 | 120.3696 | 120.4073 | 120.3485 | 120.4922 | 120.4362 | 120.3383 | 0.112 | 0.22116 | 0.04614 | -0.097212 | 0.048234 | 0.032375 | -0.019752 | 0.015139 | 0.063771 | 0.13176 | -0.002094 | 0.065892
1531.9844 | 120.6482 | -120.3964 | 0.13733 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.11409 | 0.058113 | -0.044405 | 0.098273 | 0.20284 | 0.027829 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | 0.001406 | 120.4679 | 120.3788 | 120.4256 | 120.3714 | 120.5105 | 120.4545 | 120.352 | 0.11658 | 0.22116 | 0.04614 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.019717 | 0.072928 | 0.14091 | 0.002484 | 0.07047
1533.7344 | 120.575 | -120.4742 | 0.15564 | 0.06691 | -0.008469 | 0.024629 | -0.029595 | 0.10493 | 0.071848 | -0.044405 | 0.093694 | 0.20284 | 0.032407 | -0.11552 | 0.025345 | 0.027798 | -0.033484 | 0.005985 | 120.5412 | 120.4658 | 120.4989 | 120.4446 | 120.5792 | 120.5461 | 120.4298 | 0.112 | 0.22116 | 0.050718 | -0.097212 | 0.043656 | 0.046109 | -0.015173 | 0.024296 | 0.068349 | 0.12718 | 0.007062 | 0.065891
1535.4688 | 120.726 | -120.4056 | 0.1236 | 0.06691 | -0.013048 | 0.024629 | -0.034174 | 0.10036 | 0.067269 | -0.039826 | 0.098273 | 0.19827 | 0.02325 | -0.11552 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 120.4725 | 120.3925 | 120.4302 | 120.3714 | 120.5059 | 120.4728 | 120.3658 | 0.11658 | 0.21658 | 0.041561 | -0.097212 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.06835 | 0.13634 | -0.006673 | 0.061313
1537.1562 | 120.6207 | -120.4834 | 0.17853 | 0.071489 | -0.008469 | 0.029208 | -0.025017 | 0.10493 | 0.067269 | -0.035248 | 0.093694 | 0.19827 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 120.5549 | 120.4749 | 120.5126 | 120.4584 | 120.5883 | 120.5507 | 120.4481 | 0.112 | 0.21658 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.059193 | 0.13633 | -0.006672 | 0.07047
1538.8906 | 120.6573 | -120.3964 | 0.25635 | 0.06691 | -0.008469 | 0.029208 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.098273 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | 0.001406 | 120.4633 | 120.388 | 120.4256 | 120.3668 | 120.5014 | 120.4637 | 120.352 | 0.11658 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.019717 | 0.06835 | 0.13634 | 0.002484 | 0.07047
1540.6406 | 120.6207 | -120.0668 | 0.48065 | 0.071489 | -0.022205 | 0.024629 | -0.034174 | 0.10951 | 0.058113 | -0.039826 | 0.098273 | 0.20284 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 120.1383 | 120.0446 | 120.0915 | 120.0327 | 120.1763 | 120.1249 | 120.027 | 0.11658 | 0.22116 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.06835 | 0.13634 | 0.002484 | 0.07047
1542.3281 | 120.607 | -120.52 | 0.17395 | 0.071489 | -0.017627 | 0.033786 | -0.043331 | 0.10951 | 0.067269 | -0.039826 | 0.10285 | 0.19827 | 0.027829 | -0.11094 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.5915 | 120.5024 | 120.5538 | 120.4767 | 120.6295 | 120.5873 | 120.4802 | 0.12116 | 0.21658 | 0.04614 | -0.092633 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.072928 | 0.14549 | -0.002094 | 0.07047
1544.0781 | 120.7535 | -120.5109 | 0.10986 | 0.06691 | -0.013048 | 0.024629 | -0.038752 | 0.10493 | 0.058113 | -0.044405 | 0.098273 | 0.19369 | 0.027829 | -0.12468 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 120.5778 | 120.4978 | 120.5355 | 120.4721 | 120.6158 | 120.569 | 120.4665 | 0.11658 | 0.212 | 0.04614 | -0.10637 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.06835 | 0.14549 | -0.002094 | 0.075049
1545.8281 | 120.6757 | -120.5841 | 0.16022 | 0.06691 | -0.013048 | 0.024629 | -0.025017 | 0.10951 | 0.062691 | -0.035248 | 0.098273 | 0.19369 | 0.027829 | -0.11552 | 0.034501 | 0.018642 | -0.033484 | -0.003172 | 120.651 | 120.5711 | 120.6087 | 120.5591 | 120.6936 | 120.6468 | 120.5489 | 0.11658 | 0.212 | 0.04614 | -0.097212 | 0.052812 | 0.036953 | -0.015173 | 0.015139 | 0.063772 | 0.13176 | -0.006672 | 0.061313
1547.5781 | 120.4834 | -119.7144 | 0.83771 | 0.06691 | -0.017627 | 0.015472 | -0.034174 | 0.10951 | 0.067269 | -0.044405 | 0.098273 | 0.20742 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.04722 | -0.00775 | 119.7813 | 119.6967 | 119.7298 | 119.6802 | 119.8239 | 119.7816 | 119.67 | 0.11658 | 0.22573 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.028909 | 0.010561 | 0.072928 | 0.14549 | 0.002484 | 0.075049
1549.3281 | 120.726 | -120.2499 | 0.28839 | 0.076067 | -0.008469 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.098273 | 0.19827 | 0.027829 | -0.11552 | 0.034501 | 0.014064 | -0.042641 | 0.001406 | 120.326 | 120.2415 | 120.2746 | 120.2249 | 120.3595 | 120.3172 | 120.2101 | 0.11658 | 0.21658 | 0.04614 | -0.097212 | 0.052812 | 0.032375 | -0.02433 | 0.019717 | 0.063772 | 0.14091 | -0.006672 | 0.07047
1551 | 120.7901 | -120.4926 | 0.13733 | 0.076067 | -0.022205 | 0.024629 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.098273 | 0.19827 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.038063 | -0.00775 | 120.5686 | 120.4703 | 120.5172 | 120.463 | 120.5975 | 120.5552 | 120.4481 | 0.11658 | 0.21658 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.019752 | 0.010561 | 0.072928 | 0.13634 | 0.002484 | 0.065892
1552.75 | 120.6619 | -120.488 | 0.21973 | 0.071489 | -0.013048 | 0.029208 | -0.025017 | 0.10951 | 0.062691 | -0.035248 | 0.093694 | 0.19827 | 0.02325 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.5595 | 120.4749 | 120.5172 | 120.463 | 120.5975 | 120.5507 | 120.4527 | 0.112 | 0.21658 | 0.041561 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.063771 | 0.13633 | -0.006673 | 0.065891
1554.5 | 120.694 | -120.5887 | 0.15564 | 0.062332 | -0.013048 | 0.029208 | -0.029595 | 0.10951 | 0.067269 | -0.044405 | 0.093694 | 0.20284 | 0.02325 | -0.1201 | 0.025345 | 0.027798 | -0.042641 | -0.00775 | 120.651 | 120.5756 | 120.6179 | 120.5591 | 120.6982 | 120.656 | 120.5443 | 0.112 | 0.22116 | 0.041561 | -0.10179 | 0.043656 | 0.046109 | -0.02433 | 0.010561 | 0.068349 | 0.13633 | -0.002095 | 0.065891
1556.1875 | 120.8084 | -120.5978 | 0.13275 | 0.071489 | -0.013048 | 0.024629 | -0.029595 | 0.10951 | 0.071848 | -0.044405 | 0.093694 | 0.19369 | 0.032407 | -0.12468 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 120.6693 | 120.5848 | 120.6225 | 120.5682 | 120.7074 | 120.6697 | 120.5534 | 0.112 | 0.212 | 0.050718 | -0.10637 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.068349 | 0.13633 | 0.007062 | 0.075048
1557.9219 | 120.7993 | -120.5841 | 0.14191 | 0.071489 | -0.017627 | 0.024629 | -0.043331 | 0.10036 | 0.071848 | -0.044405 | 0.089116 | 0.19827 | 0.018672 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | -0.00775 | 120.6556 | 120.5665 | 120.6087 | 120.5408 | 120.6845 | 120.656 | 120.5397 | 0.10743 | 0.21658 | 0.036983 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.010561 | 0.063771 | 0.12718 | -0.006673 | 0.056735
1559.6562 | 120.8176 | -120.575 | 0.14648 | 0.062332 | -0.022205 | 0.024629 | -0.029595 | 0.10951 | 0.062691 | -0.039826 | 0.093694 | 0.19827 | 0.02325 | -0.12468 | 0.025345 | 0.009486 | -0.038063 | 0.001406 | 120.6373 | 120.5527 | 120.5996 | 120.5454 | 120.6845 | 120.6376 | 120.5351 | 0.112 | 0.21658 | 0.041561 | -0.10637 | 0.043656 | 0.027797 | -0.019752 | 0.019717 | 0.068349 | 0.13176 | -0.002095 | 0.061313
1561.3438 | 120.726 | -120.6436 | 0.17853 | 0.06691 | -0.013048 | 0.020051 | -0.034174 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 120.7105 | 120.6306 | 120.6637 | 120.6094 | 120.7531 | 120.7109 | 120.6038 | 0.10743 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.059193 | 0.12718 | -0.002094 | 0.065892
1563.0938 | 120.7352 | -120.639 | 0.16479 | 0.06691 | -0.008469 | 0.024629 | -0.025017 | 0.10493 | 0.071848 | -0.039826 | 0.093694 | 0.20284 | 0.032407 | -0.11094 | 0.025345 | 0.018642 | -0.038063 | -0.003172 | 120.7059 | 120.6306 | 120.6637 | 120.614 | 120.744 | 120.7109 | 120.5992 | 0.112 | 0.22116 | 0.050718 | -0.092633 | 0.043656 | 0.036953 | -0.019752 | 0.015139 | 0.068349 | 0.13176 | 0.007062 | 0.07047
1564.8281 | 120.7809 | -120.6573 | 0.16022 | 0.071489 | -0.017627 | 0.033786 | -0.029595 | 0.10951 | 0.067269 | -0.039826 | 0.098273 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 120.7288 | 120.6397 | 120.6911 | 120.6278 | 120.7669 | 120.7246 | 120.6175 | 0.11658 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.06835 | 0.13634 | -0.002094 | 0.065892
1566.5781 | 120.8313 | -120.5887 | 0.13275 | 0.071489 | -0.008469 | 0.024629 | -0.029595 | 0.10493 | 0.062691 | -0.048983 | 0.098273 | 0.20284 | 0.027829 | -0.12468 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 120.6602 | 120.5802 | 120.6133 | 120.5591 | 120.6936 | 120.6514 | 120.5397 | 0.11658 | 0.22116 | 0.04614 | -0.10637 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.06835 | 0.14549 | -0.002094 | 0.075049
1568.2656 | 120.8817 | -120.639 | 0.11444 | 0.06691 | -0.013048 | 0.029208 | -0.029595 | 0.10951 | 0.058113 | -0.044405 | 0.098273 | 0.20284 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.04722 | 0.001406 | 120.7059 | 120.626 | 120.6682 | 120.6094 | 120.7485 | 120.6972 | 120.5946 | 0.11658 | 0.22116 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.028909 | 0.019717 | 0.06835 | 0.14549 | 0.002484 | 0.079627
1570.0156 | 120.9091 | -120.6619 | 0.1236 | 0.06691 | -0.013048 | 0.029208 | -0.029595 | 0.10493 | 0.058113 | -0.044405 | 0.093694 | 0.19827 | 0.032407 | -0.11552 | 0.025345 | 0.014064 | -0.038063 | -0.003172 | 120.7288 | 120.6489 | 120.6911 | 120.6323 | 120.7669 | 120.72 | 120.6175 | 0.112 | 0.21658 | 0.050718 | -0.097212 | 0.043656 | 0.032375 | -0.019752 | 0.015139 | 0.068349 | 0.13176 | 0.007062 | 0.07047
1571.7656 | 120.8084 | -120.6711 | 0.16022 | 0.071489 | -0.017627 | 0.024629 | -0.025017 | 0.10493 | 0.067269 | -0.044405 | 0.093694 | 0.19827 | 0.018672 | -0.11552 | 0.025345 | 0.018642 | -0.04722 | 0.001406 | 120.7426 | 120.6535 | 120.6957 | 120.6461 | 120.776 | 120.7384 | 120.6267 | 0.112 | 0.21658 | 0.036983 | -0.097212 | 0.043656 | 0.036953 | -0.028909 | 0.019717 | 0.068349 | 0.14091 | -0.006673 | 0.065892
1573.5 | 120.9412 | -120.6619 | 0.11902 | 0.076067 | -0.017627 | 0.024629 | -0.029595 | 0.10951 | 0.058113 | -0.035248 | 0.098273 | 0.19827 | 0.02325 | -0.11552 | 0.025345 | 0.02322 | -0.042641 | -0.00775 | 120.738 | 120.6443 | 120.6866 | 120.6323 | 120.7714 | 120.72 | 120.6267 | 0.11658 | 0.21658 | 0.041561 | -0.097212 | 0.043656 | 0.041531 | -0.02433 | 0.010561 | 0.072928 | 0.14091 | -0.002095 | 0.065891
1575.1875 | 120.8542 | -120.7077 | 0.16022 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.067269 | -0.039826 | 0.093694 | 0.19827 | 0.036985 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 120.7746 | 120.6901 | 120.7369 | 120.6781 | 120.8172 | 120.775 | 120.6679 | 0.112 | 0.21658 | 0.055296 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.068349 | 0.13633 | 0.01164 | 0.079626
1576.9531 | 120.9412 | -120.7123 | 0.15564 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10493 | 0.062691 | -0.058139 | 0.093694 | 0.19827 | 0.018672 | -0.11094 | 0.034501 | 0.018642 | -0.042641 | 0.001406 | 120.7792 | 120.6947 | 120.7415 | 120.6827 | 120.8172 | 120.775 | 120.6541 | 0.112 | 0.21658 | 0.036983 | -0.092633 | 0.052812 | 0.036953 | -0.02433 | 0.019717 | 0.059193 | 0.13633 | -0.015829 | 0.061313
1578.6406 | 120.8405 | -120.7397 | 0.16022 | 0.080646 | -0.008469 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.093694 | 0.20284 | 0.02325 | -0.12468 | 0.020767 | 0.02322 | -0.033484 | -0.003172 | 120.8204 | 120.7313 | 120.769 | 120.7147 | 120.8493 | 120.807 | 120.6999 | 0.112 | 0.22116 | 0.041561 | -0.10637 | 0.039078 | 0.041531 | -0.015173 | 0.015139 | 0.072927 | 0.12718 | 0.002483 | 0.056734
1580.375 | 120.845 | -120.7443 | 0.16022 | 0.071489 | -0.017627 | 0.020051 | -0.034174 | 0.10951 | 0.067269 | -0.044405 | 0.084537 | 0.19827 | 0.027829 | -0.11552 | 0.034501 | 0.018642 | -0.04722 | -0.003172 | 120.8158 | 120.7267 | 120.7644 | 120.7102 | 120.8538 | 120.8116 | 120.6999 | 0.10285 | 0.21658 | 0.04614 | -0.097212 | 0.052812 | 0.036953 | -0.028909 | 0.015139 | 0.050036 | 0.13176 | -0.006672 | 0.075049
1582.125 | 120.9915 | -120.7306 | 0.14191 | 0.06691 | -0.008469 | 0.020051 | -0.025017 | 0.10951 | 0.067269 | -0.044405 | 0.098273 | 0.19827 | 0.02325 | -0.11094 | 0.039079 | 0.014064 | -0.042641 | -0.00775 | 120.7975 | 120.7221 | 120.7506 | 120.7056 | 120.8401 | 120.7979 | 120.6862 | 0.11658 | 0.21658 | 0.041561 | -0.092633 | 0.05739 | 0.032375 | -0.02433 | 0.010561 | 0.059194 | 0.14091 | -0.015829 | 0.065891
1583.8594 | 120.9045 | -120.7397 | 0.14648 | 0.062332 | -0.008469 | 0.020051 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.089116 | 0.19369 | 0.032407 | -0.12468 | 0.025345 | 0.014064 | -0.042641 | 0.001406 | 120.8021 | 120.7313 | 120.7598 | 120.7147 | 120.8493 | 120.807 | 120.6908 | 0.10743 | 0.212 | 0.050718 | -0.10637 | 0.043656 | 0.032375 | -0.02433 | 0.019717 | 0.063771 | 0.13176 | 0.007062 | 0.075048
1585.5469 | 120.9641 | -120.7626 | 0.13733 | 0.06691 | -0.017627 | 0.015472 | -0.029595 | 0.10493 | 0.062691 | -0.048983 | 0.089116 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.012328 | 120.8295 | 120.745 | 120.7781 | 120.733 | 120.8676 | 120.8253 | 120.7137 | 0.10743 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.005983 | 0.059193 | 0.13176 | -0.002094 | 0.07047
1587.3125 | 121.0052 | -120.726 | 0.13275 | 0.06691 | -0.017627 | 0.020051 | -0.029595 | 0.11409 | 0.071848 | -0.039826 | 0.084537 | 0.19827 | 0.02325 | -0.11094 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 120.7929 | 120.7084 | 120.7461 | 120.6964 | 120.8401 | 120.7979 | 120.6862 | 0.10285 | 0.21658 | 0.041561 | -0.092633 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | -0.006673 | 0.065891
1589 | 120.9 | -120.7809 | 0.15564 | 0.071489 | -0.013048 | 0.020051 | -0.029595 | 0.10951 | 0.067269 | -0.035248 | 0.089116 | 0.19369 | 0.02325 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 120.8524 | 120.7679 | 120.801 | 120.7514 | 120.8905 | 120.8482 | 120.7457 | 0.10743 | 0.212 | 0.041561 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.059193 | 0.13176 | -0.006673 | 0.065891
1590.75 | 120.9824 | -120.7718 | 0.13733 | 0.06691 | -0.022205 | 0.020051 | -0.034174 | 0.095778 | 0.067269 | -0.044405 | 0.089116 | 0.18911 | 0.018672 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.8387 | 120.7496 | 120.7918 | 120.7376 | 120.8676 | 120.8391 | 120.7274 | 0.10743 | 0.20742 | 0.036983 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.059193 | 0.13176 | -0.011251 | 0.061313
1592.5 | 121.0419 | -120.7443 | 0.11902 | 0.076067 | -0.017627 | 0.020051 | -0.034174 | 0.10493 | 0.062691 | -0.039826 | 0.093694 | 0.20284 | 0.027829 | -0.11094 | 0.025345 | 0.018642 | -0.038063 | 0.001406 | 120.8204 | 120.7267 | 120.7644 | 120.7102 | 120.8493 | 120.807 | 120.7045 | 0.112 | 0.22116 | 0.04614 | -0.092633 | 0.043656 | 0.036953 | -0.019752 | 0.019717 | 0.068349 | 0.13176 | 0.002484 | 0.065892
1594.1875 | 121.0052 | -120.7764 | 0.13733 | 0.062332 | -0.017627 | 0.024629 | -0.029595 | 0.11409 | 0.067269 | -0.048983 | 0.089116 | 0.19827 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.016906 | 120.8387 | 120.7587 | 120.801 | 120.7468 | 120.8905 | 120.8436 | 120.7274 | 0.10743 | 0.21658 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.001405 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1595.9375 | 121.0602 | -120.7764 | 0.13733 | 0.071489 | -0.017627 | 0.024629 | -0.025017 | 0.11409 | 0.067269 | -0.039826 | 0.089116 | 0.19827 | 0.02325 | -0.11094 | 0.025345 | 0.018642 | -0.042641 | 0.001406 | 120.8479 | 120.7587 | 120.801 | 120.7513 | 120.8905 | 120.8436 | 120.7365 | 0.10743 | 0.21658 | 0.041561 | -0.092633 | 0.043656 | 0.036953 | -0.02433 | 0.019717 | 0.063771 | 0.13176 | -0.002095 | 0.065891
1597.6875 | 120.932 | -120.8267 | 0.15106 | 0.06691 | -0.017627 | 0.024629 | -0.025017 | 0.10493 | 0.067269 | -0.039826 | 0.084537 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.014064 | -0.042641 | 0.001406 | 120.8936 | 120.8091 | 120.8514 | 120.8017 | 120.9317 | 120.894 | 120.7869 | 0.10285 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.032375 | -0.02433 | 0.019717 | 0.059192 | 0.12718 | 0.002484 | 0.07047
1599.3906 | 121.0236 | -120.7993 | 0.12817 | 0.06691 | -0.013048 | 0.029208 | -0.029595 | 0.11409 | 0.067269 | -0.048983 | 0.084537 | 0.19827 | 0.027829 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 120.8662 | 120.7862 | 120.8285 | 120.7697 | 120.9133 | 120.8665 | 120.7503 | 0.10285 | 0.21658 | 0.04614 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.059192 | 0.1226 | 0.002484 | 0.065892
1601.125 | 120.9641 | -120.8359 | 0.17853 | 0.076067 | -0.00389 | 0.029208 | -0.029595 | 0.10951 | 0.067269 | -0.048983 | 0.089116 | 0.19827 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 120.9119 | 120.832 | 120.8651 | 120.8063 | 120.9454 | 120.9031 | 120.7869 | 0.10743 | 0.21658 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.063771 | 0.12718 | 0.002484 | 0.065892
1602.9219 | 120.9412 | -120.8542 | 0.16479 | 0.06691 | -0.017627 | 0.024629 | -0.029595 | 0.10951 | 0.062691 | -0.039826 | 0.089116 | 0.18911 | 0.032407 | -0.11094 | 0.025345 | 0.018642 | -0.038063 | -0.012328 | 120.9211 | 120.8366 | 120.8788 | 120.8246 | 120.9637 | 120.9169 | 120.8144 | 0.10743 | 0.20742 | 0.050718 | -0.092633 | 0.043656 | 0.036953 | -0.019752 | 0.005983 | 0.063771 | 0.12718 | 0.007062 | 0.07047
1604.6562 | 121.051 | -120.8313 | 0.1236 | 0.06691 | -0.008469 | 0.020051 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.084537 | 0.19827 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.033484 | -0.00775 | 120.8982 | 120.8228 | 120.8513 | 120.8017 | 120.9362 | 120.8986 | 120.7869 | 0.10285 | 0.21658 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.015173 | 0.010561 | 0.059192 | 0.11802 | 0.007062 | 0.065891
1606.3594 | 120.9641 | -120.8954 | 0.16022 | 0.071489 | -0.017627 | 0.020051 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.089116 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 120.9669 | 120.8778 | 120.9154 | 120.8658 | 121.0003 | 120.9627 | 120.851 | 0.10743 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.059193 | 0.13176 | -0.002094 | 0.07047
1608.0625 | 121.0098 | -120.8771 | 0.14648 | 0.071489 | -0.013048 | 0.024629 | -0.034174 | 0.10951 | 0.062691 | -0.039826 | 0.089116 | 0.19369 | 0.02325 | -0.11552 | 0.016188 | 0.027798 | -0.042641 | -0.00775 | 120.9486 | 120.864 | 120.9017 | 120.8429 | 120.9866 | 120.9398 | 120.8372 | 0.10743 | 0.212 | 0.041561 | -0.097212 | 0.034499 | 0.046109 | -0.02433 | 0.010561 | 0.072928 | 0.13176 | 0.007062 | 0.065891
1609.7656 | 120.9778 | -120.8862 | 0.15106 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.11409 | 0.067269 | -0.044405 | 0.084537 | 0.18911 | 0.027829 | -0.11094 | 0.029923 | 0.018642 | -0.033484 | 0.001406 | 120.9577 | 120.8686 | 120.9154 | 120.8612 | 121.0003 | 120.9535 | 120.8418 | 0.10285 | 0.20742 | 0.04614 | -0.092633 | 0.048234 | 0.036953 | -0.015173 | 0.019717 | 0.054614 | 0.11802 | -0.002094 | 0.061313
1611.5156 | 121.0968 | -120.845 | 0.1236 | 0.062332 | -0.017627 | 0.024629 | -0.029595 | 0.10951 | 0.062691 | -0.035248 | 0.089116 | 0.19369 | 0.02325 | -0.1201 | 0.020767 | 0.027798 | -0.042641 | -0.003172 | 120.9074 | 120.8274 | 120.8697 | 120.8154 | 120.9545 | 120.9077 | 120.8098 | 0.10743 | 0.212 | 0.041561 | -0.10179 | 0.039078 | 0.046109 | -0.02433 | 0.015139 | 0.068349 | 0.13176 | 0.002483 | 0.065891
1613.2031 | 121.0281 | -120.8908 | 0.14648 | 0.071489 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.067269 | -0.039826 | 0.093694 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.009486 | -0.04722 | -0.003172 | 120.9623 | 120.8732 | 120.92 | 120.8612 | 121.0003 | 120.9581 | 120.851 | 0.112 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.027797 | -0.028909 | 0.015139 | 0.063771 | 0.14091 | 0.002484 | 0.079627
1614.9062 | 121.138 | -120.8633 | 0.13733 | 0.06691 | -0.013048 | 0.024629 | -0.025017 | 0.10951 | 0.062691 | -0.039826 | 0.084537 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.003172 | 120.9303 | 120.8503 | 120.888 | 120.8383 | 120.9729 | 120.926 | 120.8235 | 0.10285 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | -0.002094 | 0.065892
1616.625 | 121.0007 | -120.9183 | 0.15106 | 0.071489 | -0.022205 | 0.029208 | -0.029595 | 0.10493 | 0.062691 | -0.039826 | 0.093694 | 0.19827 | 0.036985 | -0.11552 | 0.020767 | 0.014064 | -0.042641 | 0.001406 | 120.9898 | 120.8961 | 120.9475 | 120.8887 | 121.0232 | 120.981 | 120.8784 | 0.112 | 0.21658 | 0.055296 | -0.097212 | 0.039078 | 0.032375 | -0.02433 | 0.019717 | 0.072927 | 0.13633 | 0.016218 | 0.079626
1618.3281 | 121.0464 | -120.9091 | 0.15564 | 0.071489 | -0.017627 | 0.029208 | -0.034174 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 120.9806 | 120.8915 | 120.9383 | 120.8749 | 121.0186 | 120.9764 | 120.8693 | 0.10743 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.059193 | 0.13176 | -0.006673 | 0.065891
1620.0312 | 121.1014 | -120.9 | 0.16937 | 0.06691 | -0.022205 | 0.029208 | -0.029595 | 0.10493 | 0.071848 | -0.044405 | 0.10285 | 0.18911 | 0.02325 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 120.9669 | 120.8778 | 120.9292 | 120.8704 | 121.0049 | 120.9718 | 120.8556 | 0.12116 | 0.20742 | 0.041561 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.072928 | 0.14549 | -0.006673 | 0.065891
1621.75 | 121.1563 | -120.932 | 0.13275 | 0.06691 | -0.017627 | 0.020051 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.084537 | 0.19827 | 0.027829 | -0.11552 | 0.034501 | 0.018642 | -0.033484 | -0.003172 | 120.9989 | 120.9144 | 120.9521 | 120.9024 | 121.0369 | 120.9947 | 120.8876 | 0.10285 | 0.21658 | 0.04614 | -0.097212 | 0.052812 | 0.036953 | -0.015173 | 0.015139 | 0.050036 | 0.11802 | -0.006672 | 0.061313
1623.4844 | 121.1563 | -120.9366 | 0.10986 | 0.071489 | -0.022205 | 0.020051 | -0.025017 | 0.10493 | 0.062691 | -0.039826 | 0.093694 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 121.0081 | 120.9144 | 120.9566 | 120.9116 | 121.0415 | 120.9993 | 120.8968 | 0.112 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.063771 | 0.14091 | -0.006673 | 0.07047
1625.1562 | 121.0785 | -120.9549 | 0.13733 | 0.062332 | -0.013048 | 0.029208 | -0.029595 | 0.10951 | 0.062691 | -0.039826 | 0.084537 | 0.20284 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.0172 | 120.9418 | 120.9841 | 120.9253 | 121.0644 | 121.0176 | 120.9151 | 0.10285 | 0.22116 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | 0.002484 | 0.075048
1626.8438 | 121.1517 | -120.932 | 0.1236 | 0.062332 | -0.013048 | 0.020051 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.093694 | 0.20284 | 0.02325 | -0.11552 | 0.025345 | 0.018642 | -0.038063 | 0.005985 | 120.9943 | 120.919 | 120.9521 | 120.907 | 121.0415 | 120.9993 | 120.883 | 0.112 | 0.22116 | 0.041561 | -0.097212 | 0.043656 | 0.036953 | -0.019752 | 0.024296 | 0.068349 | 0.13176 | -0.002095 | 0.061313
1628.5625 | 121.0785 | -120.9732 | 0.16022 | 0.06691 | -0.017627 | 0.024629 | -0.029595 | 0.10951 | 0.067269 | -0.048983 | 0.089116 | 0.18911 | 0.018672 | -0.12468 | 0.034501 | 0.027798 | -0.033484 | -0.00775 | 121.0401 | 120.9556 | 120.9978 | 120.9436 | 121.0827 | 121.0405 | 120.9242 | 0.10743 | 0.20742 | 0.036983 | -0.10637 | 0.052812 | 0.046109 | -0.015173 | 0.010561 | 0.054615 | 0.1226 | -0.015829 | 0.052156
1630.25 | 121.0739 | -120.9915 | 0.17395 | 0.06691 | -0.008469 | 0.029208 | -0.029595 | 0.11409 | 0.071848 | -0.035248 | 0.093694 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 121.0584 | 120.983 | 121.0207 | 120.9619 | 121.1056 | 121.0634 | 120.9563 | 0.112 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.063771 | 0.13176 | -0.002094 | 0.065892
1631.9531 | 121.1838 | -120.9091 | 0.1236 | 0.062332 | -0.013048 | 0.024629 | -0.029595 | 0.10951 | 0.062691 | -0.035248 | 0.093694 | 0.18911 | 0.018672 | -0.11552 | 0.029923 | 0.032376 | -0.038063 | 0.001406 | 120.9715 | 120.8961 | 120.9337 | 120.8795 | 121.0186 | 120.9718 | 120.8739 | 0.112 | 0.20742 | 0.036983 | -0.097212 | 0.048234 | 0.050687 | -0.019752 | 0.019717 | 0.063771 | 0.13176 | -0.011251 | 0.056735
1633.6875 | 121.257 | -120.9549 | 0.1236 | 0.062332 | -0.022205 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.035248 | 0.093694 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 121.0172 | 120.9327 | 120.9841 | 120.9299 | 121.0644 | 121.0222 | 120.9196 | 0.112 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.063771 | 0.13633 | -0.002094 | 0.07047
1635.4688 | 121.225 | -120.9549 | 0.1236 | 0.06691 | -0.022205 | 0.024629 | -0.025017 | 0.10493 | 0.062691 | -0.044405 | 0.089116 | 0.18911 | 0.027829 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 121.0218 | 120.9327 | 120.9795 | 120.9299 | 121.0598 | 121.0176 | 120.9105 | 0.10743 | 0.20742 | 0.04614 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.054615 | 0.12718 | -0.006672 | 0.065892
1637.1719 | 121.0968 | -120.9778 | 0.15564 | 0.071489 | -0.013048 | 0.024629 | -0.029595 | 0.10951 | 0.067269 | -0.039826 | 0.084537 | 0.19827 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.0493 | 120.9647 | 121.0024 | 120.9482 | 121.0873 | 121.0451 | 120.938 | 0.10285 | 0.21658 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | 0.002484 | 0.075048
1638.8594 | 121.1197 | -121.0236 | 0.17853 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.18911 | 0.027829 | -0.1201 | 0.039079 | 0.027798 | -0.038063 | -0.00775 | 121.0905 | 121.0059 | 121.0528 | 120.994 | 121.1331 | 121.0908 | 120.9837 | 0.10743 | 0.20742 | 0.04614 | -0.10179 | 0.05739 | 0.046109 | -0.019752 | 0.010561 | 0.050037 | 0.12718 | -0.01125 | 0.065892
1640.5938 | 121.1288 | -121.0236 | 0.16479 | 0.071489 | -0.017627 | 0.029208 | -0.020438 | 0.11409 | 0.067269 | -0.039826 | 0.093694 | 0.19827 | 0.036985 | -0.1201 | 0.029923 | 0.014064 | -0.033484 | -0.003172 | 121.095 | 121.0059 | 121.0528 | 121.0031 | 121.1377 | 121.0908 | 120.9837 | 0.112 | 0.21658 | 0.055296 | -0.10179 | 0.048234 | 0.032375 | -0.015173 | 0.015139 | 0.063771 | 0.12718 | 0.007062 | 0.070469
1642.3438 | 121.1929 | -120.9869 | 0.14191 | 0.071489 | -0.013048 | 0.029208 | -0.029595 | 0.10951 | 0.062691 | -0.039826 | 0.089116 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.033484 | -0.003172 | 121.0584 | 120.9739 | 121.0161 | 120.9573 | 121.0964 | 121.0496 | 120.9471 | 0.10743 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.015173 | 0.015139 | 0.059193 | 0.1226 | -0.002094 | 0.061313
1644.0938 | 121.1746 | -121.0327 | 0.16022 | 0.071489 | -0.017627 | 0.029208 | -0.029595 | 0.10493 | 0.067269 | -0.044405 | 0.084537 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.1042 | 121.0151 | 121.0619 | 121.0031 | 121.1376 | 121.1 | 120.9883 | 0.10285 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | 0.002484 | 0.075048
1645.7656 | 121.2479 | -120.9686 | 0.12817 | 0.071489 | -0.022205 | 0.020051 | -0.029595 | 0.11409 | 0.062691 | -0.039826 | 0.098273 | 0.19827 | 0.02325 | -0.11094 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 121.0401 | 120.9464 | 120.9887 | 120.939 | 121.0827 | 121.0313 | 120.9288 | 0.11658 | 0.21658 | 0.041561 | -0.092633 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.072928 | 0.14091 | -0.002095 | 0.065891
1647.5 | 121.2708 | -120.9686 | 0.10986 | 0.06691 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.071848 | -0.044405 | 0.089116 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 121.0355 | 120.951 | 120.9978 | 120.939 | 121.0781 | 121.0405 | 120.9242 | 0.10743 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1649.1875 | 121.2662 | -120.9961 | 0.12817 | 0.062332 | -0.008469 | 0.024629 | -0.034174 | 0.10951 | 0.067269 | -0.039826 | 0.093694 | 0.19369 | 0.027829 | -0.10637 | 0.020767 | 0.018642 | -0.042641 | -0.003172 | 121.0584 | 120.9876 | 121.0207 | 120.9619 | 121.1056 | 121.0634 | 120.9563 | 0.112 | 0.212 | 0.04614 | -0.088054 | 0.039078 | 0.036953 | -0.02433 | 0.015139 | 0.072927 | 0.13633 | 0.007062 | 0.07047
1650.9375 | 121.1884 | -121.0464 | 0.15106 | 0.06691 | -0.013048 | 0.024629 | -0.025017 | 0.11409 | 0.062691 | -0.035248 | 0.084537 | 0.19827 | 0.032407 | -0.1201 | 0.034501 | 0.014064 | -0.04722 | -0.003172 | 121.1134 | 121.0334 | 121.0711 | 121.0214 | 121.1605 | 121.1091 | 121.0112 | 0.10285 | 0.21658 | 0.050718 | -0.10179 | 0.052812 | 0.032375 | -0.028909 | 0.015139 | 0.050036 | 0.13176 | -0.002094 | 0.079627
1652.625 | 121.2021 | -121.0556 | 0.15564 | 0.071489 | -0.00389 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.044405 | 0.084537 | 0.19369 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.1271 | 121.0517 | 121.0802 | 121.0306 | 121.1651 | 121.1229 | 121.0112 | 0.10285 | 0.212 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | -0.002094 | 0.07047
1654.3594 | 121.1609 | -121.0693 | 0.16479 | 0.071489 | -0.017627 | 0.020051 | -0.025017 | 0.10493 | 0.071848 | -0.044405 | 0.089116 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.033484 | 0.001406 | 121.1408 | 121.0517 | 121.0894 | 121.0443 | 121.1743 | 121.1412 | 121.0249 | 0.10743 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.015173 | 0.019717 | 0.059193 | 0.1226 | -0.002094 | 0.061313
1656.0938 | 121.2708 | -121.0281 | 0.1236 | 0.062332 | -0.017627 | 0.020051 | -0.020438 | 0.11409 | 0.062691 | -0.044405 | 0.079959 | 0.18453 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | 0.001406 | 121.0905 | 121.0105 | 121.0482 | 121.0077 | 121.1422 | 121.0908 | 120.9837 | 0.09827 | 0.20284 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.019717 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1657.7812 | 121.1975 | -121.0648 | 0.16022 | 0.06691 | -0.013048 | 0.020051 | -0.029595 | 0.10951 | 0.062691 | -0.035248 | 0.089116 | 0.19827 | 0.032407 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | 0.001406 | 121.1317 | 121.0517 | 121.0848 | 121.0352 | 121.1743 | 121.1274 | 121.0295 | 0.10743 | 0.21658 | 0.050718 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.019717 | 0.054615 | 0.13176 | -0.002094 | 0.075048
1659.5312 | 121.1975 | -121.106 | 0.17395 | 0.071489 | -0.017627 | 0.024629 | -0.029595 | 0.10493 | 0.067269 | -0.039826 | 0.079959 | 0.19827 | 0.027829 | -0.10179 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.1774 | 121.0883 | 121.1306 | 121.0764 | 121.2109 | 121.1732 | 121.0661 | 0.09827 | 0.21658 | 0.04614 | -0.083475 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | -0.006672 | 0.07047
1661.2188 | 121.1884 | -121.0876 | 0.16937 | 0.071489 | -0.008469 | 0.015472 | -0.029595 | 0.11409 | 0.062691 | -0.044405 | 0.084537 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 121.1591 | 121.0792 | 121.1031 | 121.0581 | 121.2017 | 121.1503 | 121.0432 | 0.10285 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | 0.002484 | 0.075048
1662.9688 | 121.2524 | -121.0739 | 0.13275 | 0.06691 | -0.017627 | 0.024629 | -0.025017 | 0.10493 | 0.067269 | -0.044405 | 0.084537 | 0.19369 | 0.027829 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 121.1408 | 121.0563 | 121.0985 | 121.0489 | 121.1788 | 121.1412 | 121.0295 | 0.10285 | 0.212 | 0.04614 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.059192 | 0.12718 | 0.002484 | 0.07047
1664.6562 | 121.3165 | -121.0602 | 0.11902 | 0.06691 | -0.022205 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.084537 | 0.19369 | 0.02325 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.1271 | 121.038 | 121.0894 | 121.0352 | 121.1697 | 121.1274 | 121.0112 | 0.10285 | 0.212 | 0.041561 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | -0.006673 | 0.061313
1666.3906 | 121.1975 | -121.1288 | 0.16022 | 0.071489 | -0.017627 | 0.024629 | -0.034174 | 0.10951 | 0.071848 | -0.053561 | 0.079959 | 0.19369 | 0.032407 | -0.12468 | 0.034501 | 0.027798 | -0.038063 | -0.003172 | 121.2003 | 121.1112 | 121.1535 | 121.0947 | 121.2384 | 121.2007 | 121.0753 | 0.09827 | 0.212 | 0.050718 | -0.10637 | 0.052812 | 0.046109 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | -0.002094 | 0.07047
1668.1406 | 121.3028 | -121.0648 | 0.1236 | 0.06691 | -0.013048 | 0.020051 | -0.020438 | 0.10951 | 0.058113 | -0.035248 | 0.079959 | 0.18911 | 0.027829 | -0.12468 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 121.1317 | 121.0517 | 121.0848 | 121.0443 | 121.1743 | 121.1229 | 121.0295 | 0.09827 | 0.20742 | 0.04614 | -0.10637 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | -0.002094 | 0.075049
1669.8906 | 121.2616 | -121.1014 | 0.13733 | 0.06691 | -0.013048 | 0.024629 | -0.034174 | 0.10951 | 0.067269 | -0.039826 | 0.079959 | 0.18911 | 0.02325 | -0.1201 | 0.020767 | 0.02322 | -0.038063 | -0.00775 | 121.1683 | 121.0883 | 121.126 | 121.0672 | 121.2109 | 121.1686 | 121.0616 | 0.09827 | 0.20742 | 0.041561 | -0.10179 | 0.039078 | 0.041531 | -0.019752 | 0.010561 | 0.059192 | 0.11802 | 0.002483 | 0.061313
1671.5781 | 121.2479 | -121.1151 | 0.15564 | 0.062332 | -0.017627 | 0.024629 | -0.01586 | 0.10493 | 0.067269 | -0.044405 | 0.089116 | 0.19827 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 121.1774 | 121.0975 | 121.1397 | 121.0993 | 121.22 | 121.1824 | 121.0707 | 0.10743 | 0.21658 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1673.3125 | 121.3486 | -121.0831 | 0.11444 | 0.071489 | -0.013048 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.044405 | 0.084537 | 0.20284 | 0.02325 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | -0.003172 | 121.1546 | 121.07 | 121.1077 | 121.0581 | 121.1926 | 121.1503 | 121.0387 | 0.10285 | 0.22116 | 0.041561 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.015139 | 0.059192 | 0.12718 | -0.002095 | 0.065891
1675.0625 | 121.3074 | -121.1197 | 0.13733 | 0.071489 | -0.017627 | 0.020051 | -0.020438 | 0.10493 | 0.067269 | -0.053561 | 0.084537 | 0.19369 | 0.036985 | -0.11552 | 0.029923 | 0.02322 | -0.04722 | -0.012328 | 121.1912 | 121.1021 | 121.1397 | 121.0993 | 121.2246 | 121.187 | 121.0661 | 0.10285 | 0.212 | 0.055296 | -0.097212 | 0.048234 | 0.041531 | -0.028909 | 0.005983 | 0.054614 | 0.13176 | 0.007062 | 0.084205
1676.75 | 120.9961 | -119.7601 | 1.1902 | 0.06691 | -0.022205 | 0.029208 | -0.025017 | 0.10951 | 0.071848 | -0.039826 | 0.084537 | 0.19827 | 0.027829 | -0.12468 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 119.827 | 119.7379 | 119.7893 | 119.7351 | 119.8696 | 119.832 | 119.7203 | 0.10285 | 0.21658 | 0.04614 | -0.10637 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.054614 | 0.12718 | -0.002094 | 0.07047
1678.5 | 120.4651 | -5.2414 | 115.4022 | 0.053175 | -0.040521 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 0.066223 | 0.16622 | 0.004937 | -0.11094 | 0.039079 | 0.041532 | -0.024328 | 0.015141 | 5.2946 | 5.2009 | 5.2477 | 5.1981 | 5.3234 | 5.2858 | 5.1741 | 0.084534 | 0.18453 | 0.023248 | -0.092633 | 0.05739 | 0.059843 | -0.006017 | 0.033452 | 0.027144 | 0.090551 | -0.034142 | 0.029265
1680.2344 | 120.8038 | -3.8315 | 116.9449 | 0.048597 | -0.035942 | 0.006315 | -0.047909 | 0.086622 | 0.044377 | -0.062717 | 0.061645 | 0.17079 | 0.004937 | -0.10637 | 0.043657 | 0.04611 | -0.019749 | 0.010563 | 3.8801 | 3.7955 | 3.8378 | 3.7836 | 3.9181 | 3.8759 | 3.7688 | 0.079956 | 0.1891 | 0.023248 | -0.088054 | 0.061968 | 0.064421 | -0.001438 | 0.028874 | 0.017988 | 0.081394 | -0.03872 | 0.024686
1681.9844 | 120.7718 | -2.7512 | 118.158 | 0.048597 | -0.040521 | -0.002842 | -0.052488 | 0.082044 | 0.039799 | -0.067295 | 0.066223 | 0.17079 | 0.000359 | -0.11094 | 0.048236 | 0.036954 | -0.019749 | 0.010563 | 2.7998 | 2.7106 | 2.7483 | 2.6987 | 2.8332 | 2.791 | 2.6839 | 0.084534 | 0.1891 | 0.01867 | -0.092633 | 0.066547 | 0.055265 | -0.001438 | 0.028874 | 0.017987 | 0.085972 | -0.047877 | 0.020108
1683.6719 | 120.9732 | -4.1153 | 116.748 | 0.044018 | -0.040521 | 0.001736 | -0.043331 | 0.082044 | 0.039799 | -0.067295 | 0.061645 | 0.17079 | 0.009515 | -0.10637 | 0.048236 | 0.041532 | -0.028906 | 0.015141 | 4.1593 | 4.0748 | 4.117 | 4.072 | 4.1973 | 4.1551 | 4.048 | 0.079956 | 0.1891 | 0.027826 | -0.088054 | 0.066547 | 0.059843 | -0.010595 | 0.033452 | 0.013409 | 0.090551 | -0.038721 | 0.038421
1685.4062 | 120.9686 | -114.9628 | 5.8548 | 0.062332 | -0.013048 | 0.029208 | -0.020438 | 0.10951 | 0.062691 | -0.044405 | 0.079959 | 0.19369 | 0.032407 | -0.11552 | 0.025345 | 0.027798 | -0.038063 | -0.00775 | 115.0251 | 114.9497 | 114.992 | 114.9423 | 115.0723 | 115.0255 | 114.9184 | 0.09827 | 0.212 | 0.050718 | -0.097212 | 0.043656 | 0.046109 | -0.019752 | 0.010561 | 0.054614 | 0.11802 | 0.007062 | 0.07047
1687.1562 | 121.1563 | -118.0344 | 2.7969 | 0.06691 | -0.00389 | 0.024629 | -0.020438 | 0.10493 | 0.071848 | -0.048983 | 0.079959 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 118.1013 | 118.0305 | 118.059 | 118.0139 | 118.1393 | 118.1062 | 117.9854 | 0.09827 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | 0.002484 | 0.075048
1688.8906 | 121.0556 | -119.101 | 1.8997 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.10951 | 0.062691 | -0.039826 | 0.089116 | 0.19827 | 0.032407 | -0.1201 | 0.020767 | 0.018642 | -0.038063 | 0.001406 | 119.1724 | 119.0833 | 119.1302 | 119.0759 | 119.2105 | 119.1636 | 119.0611 | 0.10743 | 0.21658 | 0.050718 | -0.10179 | 0.039078 | 0.036953 | -0.019752 | 0.019717 | 0.068349 | 0.12718 | 0.01164 | 0.07047
1690.625 | 121.0739 | -119.8746 | 1.1124 | 0.06691 | -0.017627 | 0.038365 | -0.029595 | 0.10493 | 0.067269 | -0.039826 | 0.084537 | 0.19369 | 0.036985 | -0.11094 | 0.034501 | 0.018642 | -0.033484 | -0.003172 | 119.9415 | 119.8569 | 119.9129 | 119.845 | 119.9795 | 119.9418 | 119.8347 | 0.10285 | 0.212 | 0.055296 | -0.092633 | 0.052812 | 0.036953 | -0.015173 | 0.015139 | 0.050036 | 0.11802 | 0.002484 | 0.070469
1692.3125 | 121.0373 | -120.0211 | 1.0162 | 0.071489 | -0.017627 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 120.0925 | 120.0034 | 120.0457 | 119.996 | 120.1306 | 120.0883 | 119.9812 | 0.10743 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.063771 | 0.13176 | 0.002484 | 0.07047
1694.0625 | 121.1975 | -119.4168 | 1.5884 | 0.071489 | -0.017627 | 0.020051 | -0.020438 | 0.10036 | 0.067269 | -0.039826 | 0.093694 | 0.19369 | 0.027829 | -0.11094 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 119.4883 | 119.3992 | 119.4369 | 119.3964 | 119.5172 | 119.4841 | 119.377 | 0.112 | 0.212 | 0.04614 | -0.092633 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.063771 | 0.13633 | -0.002094 | 0.07047
1695.75 | 121.1334 | -120.2591 | 0.79193 | 0.071489 | -0.013048 | 0.020051 | -0.029595 | 0.11409 | 0.062691 | -0.035248 | 0.084537 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.009486 | -0.033484 | -0.012328 | 120.3306 | 120.246 | 120.2791 | 120.2295 | 120.3732 | 120.3218 | 120.2238 | 0.10285 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.027797 | -0.015173 | 0.005983 | 0.054614 | 0.11802 | -0.002094 | 0.061313
1697.5 | 121.2524 | -117.572 | 3.3829 | 0.06691 | -0.017627 | 0.024629 | -0.029595 | 0.10493 | 0.067269 | -0.035248 | 0.084537 | 0.18453 | 0.036985 | -0.12468 | 0.025345 | 0.018642 | -0.042641 | 0.001406 | 117.6389 | 117.5544 | 117.5967 | 117.5424 | 117.677 | 117.6393 | 117.5368 | 0.10285 | 0.20284 | 0.055296 | -0.10637 | 0.043656 | 0.036953 | -0.02433 | 0.019717 | 0.059192 | 0.12718 | 0.01164 | 0.079626
1699.25 | 121.2341 | -118.4052 | 2.5909 | 0.062332 | -0.017627 | 0.029208 | -0.020438 | 0.10951 | 0.062691 | -0.039826 | 0.079959 | 0.20284 | 0.027829 | -0.11552 | 0.020767 | 0.018642 | -0.042641 | -0.003172 | 118.4675 | 118.3875 | 118.4344 | 118.3847 | 118.5147 | 118.4678 | 118.3653 | 0.09827 | 0.22116 | 0.04614 | -0.097212 | 0.039078 | 0.036953 | -0.02433 | 0.015139 | 0.059192 | 0.1226 | 0.007062 | 0.07047
1701 | 121.257 | -118.6844 | 2.3346 | 0.06691 | -0.022205 | 0.033786 | -0.034174 | 0.10951 | 0.071848 | -0.044405 | 0.084537 | 0.18453 | 0.02325 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 118.7513 | 118.6622 | 118.7182 | 118.6502 | 118.7939 | 118.7562 | 118.64 | 0.10285 | 0.20284 | 0.041561 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | -0.006673 | 0.061313
1702.75 | 121.1746 | -118.2999 | 2.8015 | 0.071489 | -0.017627 | 0.024629 | -0.029595 | 0.10036 | 0.067269 | -0.044405 | 0.079959 | 0.19827 | 0.027829 | -0.1201 | 0.025345 | 0.018642 | -0.04722 | -0.012328 | 118.3714 | 118.2822 | 118.3245 | 118.2703 | 118.4002 | 118.3671 | 118.2555 | 0.09827 | 0.21658 | 0.04614 | -0.10179 | 0.043656 | 0.036953 | -0.028909 | 0.005983 | 0.054614 | 0.12718 | 0.002484 | 0.075049
1704.5156 | 121.1197 | -118.7164 | 2.4765 | 0.06691 | -0.013048 | 0.024629 | -0.01586 | 0.10951 | 0.067269 | -0.035248 | 0.084537 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.027798 | -0.038063 | 0.001406 | 118.7833 | 118.7034 | 118.7411 | 118.7006 | 118.8259 | 118.7837 | 118.6812 | 0.10285 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.046109 | -0.019752 | 0.019717 | 0.050036 | 0.1226 | -0.002094 | 0.07047
1706.2656 | 121.1243 | -118.9911 | 2.1973 | 0.06691 | -0.017627 | 0.029208 | -0.025017 | 0.10493 | 0.071848 | -0.039826 | 0.084537 | 0.19369 | 0.02325 | -0.12468 | 0.029923 | 0.027798 | -0.038063 | -0.012328 | 119.058 | 118.9735 | 119.0203 | 118.9661 | 119.096 | 119.0629 | 118.9513 | 0.10285 | 0.212 | 0.041561 | -0.10637 | 0.048234 | 0.046109 | -0.019752 | 0.005983 | 0.054614 | 0.1226 | -0.006673 | 0.061313
1708.0156 | 121.257 | -118.8675 | 2.2614 | 0.06691 | -0.013048 | 0.024629 | -0.020438 | 0.10493 | 0.071848 | -0.035248 | 0.089116 | 0.19369 | 0.032407 | -0.11094 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 118.9344 | 118.8544 | 118.8921 | 118.8471 | 118.9724 | 118.9393 | 118.8322 | 0.10743 | 0.212 | 0.050718 | -0.092633 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1709.7031 | 121.2662 | -118.3044 | 2.8015 | 0.062332 | -0.022205 | 0.024629 | -0.025017 | 0.10493 | 0.062691 | -0.039826 | 0.079959 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.032376 | -0.038063 | -0.003172 | 118.3668 | 118.2822 | 118.3291 | 118.2794 | 118.4094 | 118.3671 | 118.2646 | 0.09827 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.050687 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | 0.002484 | 0.075048
1711.4531 | 121.1838 | -118.9911 | 2.1469 | 0.076067 | -0.017627 | 0.029208 | -0.01586 | 0.10493 | 0.062691 | -0.039826 | 0.084537 | 0.19827 | 0.027829 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 119.0672 | 118.9735 | 119.0203 | 118.9752 | 119.096 | 119.0538 | 118.9513 | 0.10285 | 0.21658 | 0.04614 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.050036 | 0.12718 | -0.006672 | 0.07047
1713.2031 | 121.2982 | -119.1513 | 2.0187 | 0.076067 | -0.017627 | 0.020051 | -0.025017 | 0.10036 | 0.067269 | -0.039826 | 0.084537 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.033484 | -0.003172 | 119.2274 | 119.1337 | 119.1714 | 119.1263 | 119.2517 | 119.2186 | 119.1115 | 0.10285 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.015173 | 0.015139 | 0.054614 | 0.11802 | -0.002094 | 0.061313
1714.9375 | 121.2524 | -119.4351 | 1.7441 | 0.06691 | -0.013048 | 0.015472 | -0.025017 | 0.10493 | 0.067269 | -0.039826 | 0.084537 | 0.19369 | 0.02325 | -0.11552 | 0.034501 | 0.018642 | -0.04722 | 0.001406 | 119.502 | 119.4221 | 119.4506 | 119.4101 | 119.5401 | 119.5024 | 119.3953 | 0.10285 | 0.212 | 0.041561 | -0.097212 | 0.052812 | 0.036953 | -0.028909 | 0.019717 | 0.050036 | 0.13176 | -0.011251 | 0.07047
1716.625 | 121.2936 | -119.371 | 1.7624 | 0.071489 | -0.017627 | 0.024629 | -0.011281 | 0.10493 | 0.067269 | -0.048983 | 0.079959 | 0.18911 | 0.027829 | -0.11552 | 0.034501 | 0.027798 | -0.038063 | -0.00775 | 119.4425 | 119.3534 | 119.3957 | 119.3598 | 119.476 | 119.4383 | 119.322 | 0.09827 | 0.20742 | 0.04614 | -0.097212 | 0.052812 | 0.046109 | -0.019752 | 0.010561 | 0.045458 | 0.11802 | -0.006672 | 0.065892
1718.375 | 121.1975 | -119.5541 | 1.68 | 0.071489 | -0.013048 | 0.024629 | -0.025017 | 0.11409 | 0.067269 | -0.044405 | 0.079959 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 119.6256 | 119.5411 | 119.5788 | 119.5291 | 119.6682 | 119.6214 | 119.5097 | 0.09827 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | 0.002484 | 0.07047
1720.0625 | 121.2708 | -119.6182 | 1.5472 | 0.06691 | -0.017627 | 0.020051 | -0.01586 | 0.10951 | 0.062691 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.00775 | 119.6851 | 119.6006 | 119.6383 | 119.6024 | 119.7277 | 119.6809 | 119.5784 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.010561 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1721.7969 | 121.3257 | -119.7556 | 1.3733 | 0.06691 | -0.022205 | 0.024629 | -0.025017 | 0.10951 | 0.071848 | -0.039826 | 0.093694 | 0.19827 | 0.027829 | -0.11552 | 0.025345 | 0.018642 | -0.033484 | 0.001406 | 119.8225 | 119.7333 | 119.7802 | 119.7305 | 119.8651 | 119.8274 | 119.7157 | 0.112 | 0.21658 | 0.04614 | -0.097212 | 0.043656 | 0.036953 | -0.015173 | 0.019717 | 0.068349 | 0.12718 | 0.002484 | 0.061313
1723.5469 | 121.2662 | -119.5129 | 1.7075 | 0.076067 | -0.013048 | 0.024629 | -0.020438 | 0.10951 | 0.062691 | -0.044405 | 0.084537 | 0.19827 | 0.032407 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | 0.001406 | 119.589 | 119.4999 | 119.5376 | 119.4925 | 119.6225 | 119.5756 | 119.4685 | 0.10285 | 0.21658 | 0.050718 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.019717 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1725.2969 | 121.2708 | -119.6732 | 1.5472 | 0.071489 | -0.022205 | 0.020051 | -0.020438 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18453 | 0.027829 | -0.1201 | 0.025345 | 0.027798 | -0.038063 | -0.003172 | 119.7446 | 119.651 | 119.6932 | 119.6527 | 119.7827 | 119.745 | 119.6333 | 0.09827 | 0.20284 | 0.04614 | -0.10179 | 0.043656 | 0.046109 | -0.019752 | 0.015139 | 0.054614 | 0.11802 | 0.002484 | 0.065892
1727.0469 | 121.225 | -119.7235 | 1.5472 | 0.062332 | -0.022205 | 0.020051 | -0.020438 | 0.10951 | 0.062691 | -0.044405 | 0.084537 | 0.19827 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 119.7858 | 119.7013 | 119.7436 | 119.7031 | 119.833 | 119.7862 | 119.6791 | 0.10285 | 0.21658 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | -0.002094 | 0.065892
1728.7344 | 121.344 | -119.8608 | 1.3184 | 0.062332 | -0.017627 | 0.029208 | -0.029595 | 0.10951 | 0.062691 | -0.044405 | 0.079959 | 0.18911 | 0.032407 | -0.11094 | 0.034501 | 0.027798 | -0.038063 | -0.003172 | 119.9232 | 119.8432 | 119.89 | 119.8312 | 119.9704 | 119.9235 | 119.8164 | 0.09827 | 0.20742 | 0.050718 | -0.092633 | 0.052812 | 0.046109 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | -0.002094 | 0.07047
1730.4844 | 121.2799 | -119.9295 | 1.3092 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.10493 | 0.062691 | -0.035248 | 0.093694 | 0.19369 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 120.001 | 119.9119 | 119.9587 | 119.9045 | 120.0344 | 119.9922 | 119.8943 | 0.112 | 0.212 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.063771 | 0.13176 | -0.006673 | 0.061313
1732.2344 | 121.2341 | -120.0119 | 1.2863 | 0.076067 | -0.017627 | 0.024629 | -0.020438 | 0.11867 | 0.067269 | -0.044405 | 0.084537 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.027798 | -0.033484 | -0.00775 | 120.088 | 119.9943 | 120.0365 | 119.9915 | 120.1306 | 120.0792 | 119.9675 | 0.10285 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.046109 | -0.015173 | 0.010561 | 0.059192 | 0.11802 | 0.002484 | 0.061313
1734 | 121.2341 | -119.9982 | 1.2726 | 0.076067 | -0.017627 | 0.024629 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.084537 | 0.19369 | 0.036985 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | 0.001406 | 120.0742 | 119.9805 | 120.0228 | 119.9777 | 120.1031 | 120.0654 | 119.9583 | 0.10285 | 0.212 | 0.055296 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.019717 | 0.059192 | 0.12718 | 0.01164 | 0.079626
1735.6875 | 121.3943 | -119.8883 | 1.3458 | 0.071489 | -0.017627 | 0.015472 | -0.020438 | 0.10951 | 0.071848 | -0.044405 | 0.084537 | 0.18453 | 0.027829 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 119.9598 | 119.8707 | 119.9038 | 119.8679 | 119.9978 | 119.9602 | 119.8439 | 0.10285 | 0.20284 | 0.04614 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.050036 | 0.12718 | -0.006672 | 0.07047
1737.4219 | 121.2616 | -119.9799 | 1.3458 | 0.076067 | -0.017627 | 0.020051 | -0.020438 | 0.10493 | 0.071848 | -0.039826 | 0.084537 | 0.19827 | 0.032407 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | 0.001406 | 120.0559 | 119.9622 | 119.9999 | 119.9594 | 120.0848 | 120.0517 | 119.94 | 0.10285 | 0.21658 | 0.050718 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.019717 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1739.1094 | 121.3852 | -119.8883 | 1.3367 | 0.071489 | -0.022205 | 0.020051 | -0.025017 | 0.10493 | 0.067269 | -0.044405 | 0.079959 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.042641 | -0.003172 | 119.9598 | 119.8661 | 119.9084 | 119.8633 | 119.9932 | 119.9556 | 119.8439 | 0.09827 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.02433 | 0.015139 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1740.7969 | 121.2753 | -119.902 | 1.4053 | 0.071489 | -0.022205 | 0.024629 | -0.020438 | 0.10493 | 0.067269 | -0.044405 | 0.084537 | 0.19369 | 0.027829 | -0.12468 | 0.025345 | 0.014064 | -0.038063 | -0.003172 | 119.9735 | 119.8798 | 119.9267 | 119.8816 | 120.007 | 119.9693 | 119.8576 | 0.10285 | 0.212 | 0.04614 | -0.10637 | 0.043656 | 0.032375 | -0.019752 | 0.015139 | 0.059192 | 0.1226 | 0.002484 | 0.065892
1742.5469 | 121.3486 | -120.0394 | 1.2085 | 0.076067 | -0.017627 | 0.020051 | -0.01586 | 0.10951 | 0.062691 | -0.035248 | 0.089116 | 0.18911 | 0.027829 | -0.11552 | 0.020767 | 0.018642 | -0.04722 | -0.003172 | 120.1154 | 120.0217 | 120.0594 | 120.0235 | 120.1489 | 120.1021 | 120.0041 | 0.10743 | 0.20742 | 0.04614 | -0.097212 | 0.039078 | 0.036953 | -0.028909 | 0.015139 | 0.068349 | 0.13634 | 0.007062 | 0.075049
1744.2969 | 121.2936 | -120.0714 | 1.2268 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.03067 | 0.079959 | 0.18453 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 120.1429 | 120.0538 | 120.1006 | 120.0464 | 120.1809 | 120.1387 | 120.0407 | 0.09827 | 0.20284 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | -0.006672 | 0.07047
1745.9844 | 121.3943 | -120.0989 | 1.1581 | 0.071489 | -0.022205 | 0.038365 | -0.025017 | 0.10493 | 0.067269 | -0.039826 | 0.089116 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | 0.001406 | 120.1704 | 120.0767 | 120.1372 | 120.0739 | 120.2038 | 120.1661 | 120.0591 | 0.10743 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.019717 | 0.059193 | 0.12718 | -0.002094 | 0.065892
1747.7344 | 121.344 | -120.1721 | 1.1353 | 0.071489 | -0.022205 | 0.020051 | -0.025017 | 0.10036 | 0.062691 | -0.039826 | 0.084537 | 0.19369 | 0.027829 | -0.11094 | 0.029923 | 0.02322 | -0.038063 | -0.00775 | 120.2436 | 120.1499 | 120.1922 | 120.1471 | 120.2725 | 120.2348 | 120.1323 | 0.10285 | 0.212 | 0.04614 | -0.092633 | 0.048234 | 0.041531 | -0.019752 | 0.010561 | 0.054614 | 0.1226 | -0.002094 | 0.065892
1749.5 | 121.3715 | -120.1584 | 1.1261 | 0.06691 | -0.017627 | 0.029208 | -0.025017 | 0.10493 | 0.062691 | -0.039826 | 0.084537 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.00775 | 120.2253 | 120.1408 | 120.1876 | 120.1334 | 120.2633 | 120.2211 | 120.1186 | 0.10285 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.010561 | 0.054614 | 0.1226 | -0.006673 | 0.061313
1751.1875 | 121.431 | -120.1538 | 1.1032 | 0.06691 | -0.022205 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.048983 | 0.084537 | 0.18911 | 0.027829 | -0.1201 | 0.020767 | 0.02322 | -0.038063 | -0.00775 | 120.2207 | 120.1316 | 120.183 | 120.1379 | 120.2633 | 120.2211 | 120.1048 | 0.10285 | 0.20742 | 0.04614 | -0.10179 | 0.039078 | 0.041531 | -0.019752 | 0.010561 | 0.06377 | 0.1226 | 0.007062 | 0.065892
1752.9375 | 121.376 | -120.1813 | 1.1444 | 0.071489 | -0.026784 | 0.020051 | -0.01586 | 0.10493 | 0.067269 | -0.039826 | 0.093694 | 0.18911 | 0.02325 | -0.12468 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 120.2528 | 120.1545 | 120.2013 | 120.1654 | 120.2862 | 120.2485 | 120.1414 | 0.112 | 0.20742 | 0.041561 | -0.10637 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.059193 | 0.13633 | -0.011251 | 0.065891
1754.6094 | 121.3348 | -120.3827 | 0.95673 | 0.057754 | -0.022205 | 0.020051 | -0.025017 | 0.10493 | 0.067269 | -0.044405 | 0.079959 | 0.18911 | 0.027829 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 120.4404 | 120.3605 | 120.4027 | 120.3577 | 120.4876 | 120.45 | 120.3383 | 0.09827 | 0.20742 | 0.04614 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.054614 | 0.11802 | 0.002484 | 0.065892
1756.3594 | 121.4264 | -120.3918 | 0.91095 | 0.076067 | -0.017627 | 0.024629 | -0.029595 | 0.10493 | 0.062691 | -0.044405 | 0.093694 | 0.18911 | 0.032407 | -0.11552 | 0.025345 | 0.018642 | -0.038063 | -0.00775 | 120.4679 | 120.3742 | 120.4165 | 120.3623 | 120.4968 | 120.4545 | 120.3474 | 0.112 | 0.20742 | 0.050718 | -0.097212 | 0.043656 | 0.036953 | -0.019752 | 0.010561 | 0.068349 | 0.13176 | 0.007062 | 0.07047
1758.1094 | 121.4401 | -120.401 | 0.88348 | 0.06691 | -0.022205 | 0.029208 | -0.025017 | 0.11409 | 0.071848 | -0.044405 | 0.079959 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.003172 | 120.4679 | 120.3788 | 120.4302 | 120.376 | 120.5151 | 120.4728 | 120.3566 | 0.09827 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1759.7969 | 121.3211 | -120.4514 | 0.92468 | 0.06691 | -0.017627 | 0.024629 | -0.025017 | 0.10493 | 0.062691 | -0.039826 | 0.089116 | 0.18911 | 0.032407 | -0.1201 | 0.039079 | 0.018642 | -0.04722 | -0.00775 | 120.5183 | 120.4337 | 120.476 | 120.4263 | 120.5563 | 120.514 | 120.4115 | 0.10743 | 0.20742 | 0.050718 | -0.10179 | 0.05739 | 0.036953 | -0.028909 | 0.010561 | 0.050037 | 0.13634 | -0.006672 | 0.079627
1761.5625 | 121.3806 | -120.4742 | 0.86975 | 0.071489 | -0.017627 | 0.033786 | -0.011281 | 0.10951 | 0.076426 | -0.048983 | 0.079959 | 0.18911 | 0.02325 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 120.5457 | 120.4566 | 120.508 | 120.463 | 120.5838 | 120.5507 | 120.4253 | 0.09827 | 0.20742 | 0.041561 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.045458 | 0.1226 | -0.011251 | 0.065891
1763.3281 | 121.4584 | -120.4971 | 0.82855 | 0.076067 | -0.022205 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.18911 | 0.02325 | -0.11094 | 0.029923 | 0.027798 | -0.038063 | -0.003172 | 120.5732 | 120.4749 | 120.5218 | 120.4767 | 120.6066 | 120.5644 | 120.4573 | 0.10743 | 0.20742 | 0.041561 | -0.092633 | 0.048234 | 0.046109 | -0.019752 | 0.015139 | 0.059193 | 0.12718 | -0.006673 | 0.061313
1765.0156 | 121.463 | -120.4971 | 0.81024 | 0.071489 | -0.022205 | 0.029208 | -0.020438 | 0.10493 | 0.062691 | -0.044405 | 0.084537 | 0.18911 | 0.027829 | -0.11552 | 0.029923 | 0.014064 | -0.033484 | 0.001406 | 120.5686 | 120.4749 | 120.5263 | 120.4767 | 120.6021 | 120.5598 | 120.4527 | 0.10285 | 0.20742 | 0.04614 | -0.097212 | 0.048234 | 0.032375 | -0.015173 | 0.019717 | 0.054614 | 0.11802 | -0.002094 | 0.061313
1766.75 | 121.344 | -120.5795 | 0.81024 | 0.076067 | -0.022205 | 0.033786 | -0.01586 | 0.11409 | 0.067269 | -0.044405 | 0.084537 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.032376 | -0.042641 | -0.003172 | 120.6556 | 120.5573 | 120.6133 | 120.5637 | 120.6936 | 120.6468 | 120.5351 | 0.10285 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.050687 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | -0.002094 | 0.07047
1768.5 | 121.4676 | -120.5383 | 0.77362 | 0.071489 | -0.022205 | 0.029208 | -0.01586 | 0.10493 | 0.058113 | -0.039826 | 0.084537 | 0.19369 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 120.6098 | 120.5161 | 120.5675 | 120.5225 | 120.6433 | 120.5964 | 120.4985 | 0.10285 | 0.212 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.054614 | 0.1226 | -0.002094 | 0.065892
1770.1875 | 121.3577 | -120.5978 | 0.80566 | 0.06691 | -0.017627 | 0.024629 | -0.020438 | 0.10951 | 0.062691 | -0.039826 | 0.07538 | 0.19369 | 0.032407 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | 0.005985 | 120.6647 | 120.5802 | 120.6225 | 120.5774 | 120.7074 | 120.6605 | 120.558 | 0.093691 | 0.212 | 0.050718 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.024296 | 0.050035 | 0.11802 | 0.007062 | 0.075048
1771.9375 | 121.4447 | -117.8787 | 3.392 | 0.071489 | -0.017627 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.048983 | 0.084537 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 117.9502 | 117.8611 | 117.9034 | 117.8629 | 117.9882 | 117.9506 | 117.8297 | 0.10285 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.054614 | 0.13176 | -0.006673 | 0.07047
1773.6875 | 121.5363 | -117.7185 | 3.5751 | 0.080646 | -0.026784 | 0.033786 | -0.020438 | 0.10951 | 0.062691 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 117.7992 | 117.6917 | 117.7523 | 117.6981 | 117.828 | 117.7812 | 117.6833 | 0.093691 | 0.20742 | 0.04614 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.050035 | 0.11802 | 0.002484 | 0.07047
1775.4219 | 121.4081 | -117.8696 | 3.4836 | 0.076067 | -0.022205 | 0.033786 | -0.020438 | 0.11409 | 0.067269 | -0.035248 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.025345 | 0.027798 | -0.042641 | -0.012328 | 117.9456 | 117.8474 | 117.9034 | 117.8491 | 117.9837 | 117.9368 | 117.8343 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.043656 | 0.046109 | -0.02433 | 0.005983 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1777.1719 | 121.431 | -118.3456 | 3.0716 | 0.076067 | -0.017627 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | -0.00775 | 118.4217 | 118.328 | 118.3703 | 118.3252 | 118.4552 | 118.4129 | 118.3058 | 0.09827 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.010561 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1778.8594 | 121.4355 | -119.0369 | 2.3621 | 0.071489 | -0.017627 | 0.033786 | -0.01586 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 119.1084 | 119.0192 | 119.0707 | 119.021 | 119.1464 | 119.1041 | 118.997 | 0.10743 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.059193 | 0.12718 | -0.002094 | 0.065892
1780.5938 | 121.2204 | -45.4971 | 75.8423 | 0.062332 | -0.026784 | 0.015472 | -0.029595 | 0.095778 | 0.058113 | -0.048983 | 0.07538 | 0.18453 | 0.014094 | -0.11094 | 0.048236 | 0.02322 | -0.028906 | 0.001406 | 45.5595 | 45.4703 | 45.5126 | 45.4675 | 45.5929 | 45.5552 | 45.4481 | 0.093691 | 0.20284 | 0.032405 | -0.092633 | 0.066547 | 0.041531 | -0.010595 | 0.019717 | 0.027144 | 0.10429 | -0.034142 | 0.043
1782.3281 | 121.5729 | -118.6569 | 2.5955 | 0.076067 | -0.022205 | 0.038365 | -0.020438 | 0.10951 | 0.067269 | -0.035248 | 0.084537 | 0.19369 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.033484 | -0.003172 | 118.733 | 118.6347 | 118.6953 | 118.6365 | 118.7664 | 118.7242 | 118.6217 | 0.10285 | 0.212 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.015173 | 0.015139 | 0.054614 | 0.11802 | -0.002094 | 0.061313
1784.0312 | 121.4996 | -118.2312 | 3.1082 | 0.071489 | -0.026784 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.11094 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 118.3027 | 118.2044 | 118.2604 | 118.2062 | 118.3407 | 118.2985 | 118.1914 | 0.09827 | 0.212 | 0.04614 | -0.092633 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1785.7188 | 121.5454 | -118.4052 | 2.916 | 0.071489 | -0.017627 | 0.024629 | -0.020438 | 0.10493 | 0.058113 | -0.039826 | 0.079959 | 0.19369 | 0.018672 | -0.12468 | 0.020767 | 0.018642 | -0.038063 | -0.003172 | 118.4766 | 118.3875 | 118.4298 | 118.3847 | 118.5101 | 118.4633 | 118.3653 | 0.09827 | 0.212 | 0.036983 | -0.10637 | 0.039078 | 0.036953 | -0.019752 | 0.015139 | 0.059192 | 0.11802 | -0.002095 | 0.056735
1787.4688 | 121.4493 | -118.6615 | 2.7832 | 0.076067 | -0.022205 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.039826 | 0.084537 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 118.7376 | 118.6393 | 118.6953 | 118.6456 | 118.7756 | 118.7333 | 118.6217 | 0.10285 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | 0.002484 | 0.075048
1789.1719 | 121.4127 | -118.9957 | 2.449 | 0.071489 | -0.017627 | 0.029208 | -0.020438 | 0.10036 | 0.076426 | -0.039826 | 0.084537 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 119.0672 | 118.978 | 119.0249 | 118.9752 | 119.096 | 119.0721 | 118.9558 | 0.10285 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.054614 | 0.1226 | -0.002094 | 0.065892
1790.9219 | 121.4127 | -119.989 | 1.4465 | 0.076067 | -0.013048 | 0.020051 | -0.011281 | 0.11409 | 0.071848 | -0.035248 | 0.084537 | 0.18911 | 0.027829 | -0.11552 | 0.034501 | 0.018642 | -0.038063 | 0.001406 | 120.0651 | 119.976 | 120.0091 | 119.9777 | 120.1031 | 120.0609 | 119.9538 | 0.10285 | 0.20742 | 0.04614 | -0.097212 | 0.052812 | 0.036953 | -0.019752 | 0.019717 | 0.050036 | 0.1226 | -0.006672 | 0.065892
1792.6719 | 121.4493 | -120.2637 | 1.1444 | 0.071489 | -0.017627 | 0.029208 | -0.01586 | 0.10493 | 0.067269 | -0.035248 | 0.089116 | 0.18911 | 0.02325 | -0.11552 | 0.025345 | 0.02322 | -0.033484 | -0.003172 | 120.3352 | 120.246 | 120.2929 | 120.2478 | 120.3686 | 120.3309 | 120.2284 | 0.10743 | 0.20742 | 0.041561 | -0.097212 | 0.043656 | 0.041531 | -0.015173 | 0.015139 | 0.063771 | 0.1226 | -0.002095 | 0.056734
1794.3594 | 121.4127 | -120.6985 | 0.7782 | 0.076067 | -0.026784 | 0.020051 | -0.01586 | 0.10951 | 0.067269 | -0.044405 | 0.07538 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.003172 | 120.7746 | 120.6718 | 120.7186 | 120.6827 | 120.8081 | 120.7658 | 120.6541 | 0.093691 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.015139 | 0.045457 | 0.1226 | -0.002094 | 0.075049
1796.1094 | 121.4218 | -120.8176 | 0.69122 | 0.076067 | -0.017627 | 0.029208 | -0.01586 | 0.10493 | 0.071848 | -0.035248 | 0.089116 | 0.19827 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.033484 | 0.001406 | 120.8936 | 120.7999 | 120.8468 | 120.8017 | 120.9225 | 120.8894 | 120.7823 | 0.10743 | 0.21658 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.015173 | 0.019717 | 0.059193 | 0.1226 | 0.002484 | 0.065891
1797.8281 | 121.4767 | -120.8313 | 0.64087 | 0.076067 | -0.017627 | 0.033786 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.084537 | 0.19827 | 0.027829 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | 0.001406 | 120.9074 | 120.8137 | 120.8651 | 120.8109 | 120.9362 | 120.8986 | 120.7915 | 0.10285 | 0.21658 | 0.04614 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.019717 | 0.050036 | 0.12718 | -0.006672 | 0.07047
1799.5312 | 121.4539 | -120.8771 | 0.60425 | 0.071489 | -0.026784 | 0.029208 | -0.020438 | 0.11409 | 0.067269 | -0.035248 | 0.084537 | 0.18911 | 0.036985 | -0.11552 | 0.034501 | 0.014064 | -0.042641 | -0.00775 | 120.9486 | 120.8503 | 120.9063 | 120.8566 | 120.9912 | 120.9443 | 120.8418 | 0.10285 | 0.20742 | 0.055296 | -0.097212 | 0.052812 | 0.032375 | -0.02433 | 0.010561 | 0.050036 | 0.12718 | 0.002484 | 0.079626
1801.2812 | 121.4081 | -120.9091 | 0.59967 | 0.076067 | -0.022205 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.03067 | 0.084537 | 0.19827 | 0.032407 | -0.1201 | 0.039079 | 0.018642 | -0.042641 | -0.00775 | 120.9852 | 120.8869 | 120.9383 | 120.8887 | 121.0232 | 120.981 | 120.8784 | 0.10285 | 0.21658 | 0.050718 | -0.10179 | 0.05739 | 0.036953 | -0.02433 | 0.010561 | 0.045458 | 0.12718 | -0.006672 | 0.075048
1802.9531 | 121.5683 | -120.8771 | 0.55389 | 0.071489 | -0.022205 | 0.029208 | -0.01586 | 0.10493 | 0.067269 | -0.03067 | 0.07538 | 0.19827 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 120.9486 | 120.8549 | 120.9063 | 120.8612 | 120.982 | 120.9443 | 120.8464 | 0.093691 | 0.21658 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.045457 | 0.11802 | 0.002484 | 0.075048
1804.6875 | 121.4264 | -120.3415 | 0.99792 | 0.071489 | -0.017627 | 0.029208 | -0.025017 | 0.10951 | 0.071848 | -0.039826 | 0.084537 | 0.18911 | 0.036985 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 120.413 | 120.3239 | 120.3707 | 120.3165 | 120.451 | 120.4133 | 120.3017 | 0.10285 | 0.20742 | 0.055296 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.050036 | 0.12718 | 0.002484 | 0.079626
1806.4375 | 121.5775 | -120.2866 | 1.0803 | 0.071489 | -0.022205 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.035248 | 0.079959 | 0.18911 | 0.027829 | -0.11094 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 120.358 | 120.2644 | 120.3112 | 120.2707 | 120.3961 | 120.3584 | 120.2513 | 0.09827 | 0.20742 | 0.04614 | -0.092633 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | -0.002094 | 0.07047
1808.1562 | 121.5958 | -120.6162 | 0.75989 | 0.076067 | -0.017627 | 0.024629 | -0.020438 | 0.11409 | 0.071848 | -0.044405 | 0.079959 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.027798 | -0.04722 | -0.003172 | 120.6922 | 120.5985 | 120.6408 | 120.5957 | 120.7302 | 120.688 | 120.5717 | 0.09827 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.046109 | -0.028909 | 0.015139 | 0.054614 | 0.12718 | 0.002484 | 0.075049
1809.8281 | 121.4767 | -120.7809 | 0.66834 | 0.076067 | -0.017627 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.044405 | 0.084537 | 0.18911 | 0.027829 | -0.12468 | 0.029923 | 0.02322 | -0.033484 | -0.003172 | 120.857 | 120.7633 | 120.8102 | 120.7651 | 120.8905 | 120.8482 | 120.7365 | 0.10285 | 0.20742 | 0.04614 | -0.10637 | 0.048234 | 0.041531 | -0.015173 | 0.015139 | 0.054614 | 0.11802 | -0.002094 | 0.061313
1811.5469 | 121.5775 | -120.813 | 0.59052 | 0.076067 | -0.026784 | 0.024629 | -0.01586 | 0.10036 | 0.071848 | -0.039826 | 0.084537 | 0.19369 | 0.027829 | -0.12468 | 0.025345 | 0.02322 | -0.042641 | -0.003172 | 120.8891 | 120.7862 | 120.8376 | 120.7971 | 120.9133 | 120.8848 | 120.7732 | 0.10285 | 0.212 | 0.04614 | -0.10637 | 0.043656 | 0.041531 | -0.02433 | 0.015139 | 0.059192 | 0.12718 | 0.002484 | 0.07047
1813.2344 | 121.5591 | -120.7901 | 0.65002 | 0.071489 | -0.013048 | 0.033786 | -0.01586 | 0.11867 | 0.067269 | -0.035248 | 0.079959 | 0.19827 | 0.032407 | -0.12468 | 0.025345 | 0.018642 | -0.033484 | -0.00775 | 120.8616 | 120.7771 | 120.8239 | 120.7742 | 120.9088 | 120.8574 | 120.7549 | 0.09827 | 0.21658 | 0.050718 | -0.10637 | 0.043656 | 0.036953 | -0.015173 | 0.010561 | 0.054614 | 0.11344 | 0.007062 | 0.065891
1814.9531 | 121.4996 | -120.8359 | 0.66376 | 0.071489 | -0.013048 | 0.029208 | -0.020438 | 0.10493 | 0.071848 | -0.039826 | 0.093694 | 0.19827 | 0.027829 | -0.11552 | 0.025345 | 0.014064 | -0.042641 | 0.001406 | 120.9074 | 120.8228 | 120.8651 | 120.8154 | 120.9408 | 120.9077 | 120.796 | 0.112 | 0.21658 | 0.04614 | -0.097212 | 0.043656 | 0.032375 | -0.02433 | 0.019717 | 0.068349 | 0.13633 | 0.002484 | 0.07047
1816.6406 | 121.4493 | -120.9045 | 0.61798 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.039826 | 0.084537 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.9806 | 120.8823 | 120.9337 | 120.8887 | 121.0141 | 120.9718 | 120.8647 | 0.10285 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | -0.002094 | 0.07047
1818.3281 | 121.4767 | -120.9412 | 0.6134 | 0.076067 | -0.017627 | 0.029208 | -0.020438 | 0.10493 | 0.071848 | -0.039826 | 0.079959 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.018642 | -0.028906 | -0.00775 | 121.0172 | 120.9235 | 120.9704 | 120.9207 | 121.0461 | 121.013 | 120.9013 | 0.09827 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.036953 | -0.010595 | 0.010561 | 0.050036 | 0.10887 | 0.007062 | 0.065891
1820.0938 | 121.4493 | -120.9412 | 0.54932 | 0.076067 | -0.013048 | 0.024629 | -0.011281 | 0.10951 | 0.071848 | -0.03067 | 0.084537 | 0.19827 | 0.036985 | -0.11552 | 0.034501 | 0.02322 | -0.051798 | -0.00775 | 121.0172 | 120.9281 | 120.9658 | 120.9299 | 121.0507 | 121.013 | 120.9105 | 0.10285 | 0.21658 | 0.055296 | -0.097212 | 0.052812 | 0.041531 | -0.033487 | 0.010561 | 0.050036 | 0.13633 | 0.002484 | 0.088783
1821.7812 | 121.5912 | -120.9457 | 0.49896 | 0.076067 | -0.017627 | 0.020051 | -0.01586 | 0.11409 | 0.071848 | -0.039826 | 0.079959 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | -0.003172 | 121.0218 | 120.9281 | 120.9658 | 120.9299 | 121.0598 | 121.0176 | 120.9059 | 0.09827 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | 0.002484 | 0.07047
1823.5156 | 121.5546 | -120.9824 | 0.4715 | 0.076067 | -0.013048 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.044405 | 0.084537 | 0.19827 | 0.032407 | -0.11552 | 0.025345 | 0.014064 | -0.04722 | -0.003172 | 121.0584 | 120.9693 | 121.007 | 120.9619 | 121.0919 | 121.0496 | 120.938 | 0.10285 | 0.21658 | 0.050718 | -0.097212 | 0.043656 | 0.032375 | -0.028909 | 0.015139 | 0.059192 | 0.13176 | 0.007062 | 0.079627
1825.1875 | 121.4539 | -121.0556 | 0.44861 | 0.080646 | -0.017627 | 0.029208 | -0.01586 | 0.11409 | 0.067269 | -0.035248 | 0.084537 | 0.19827 | 0.036985 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 121.1362 | 121.038 | 121.0848 | 121.0397 | 121.1697 | 121.1229 | 121.0204 | 0.10285 | 0.21658 | 0.055296 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.054614 | 0.12718 | 0.007062 | 0.079626
1826.875 | 121.5408 | -121.0602 | 0.44403 | 0.076067 | -0.013048 | 0.029208 | -0.011281 | 0.10951 | 0.067269 | -0.035248 | 0.084537 | 0.19369 | 0.032407 | -0.11552 | 0.025345 | 0.018642 | -0.042641 | -0.00775 | 121.1362 | 121.0471 | 121.0894 | 121.0489 | 121.1697 | 121.1274 | 121.0249 | 0.10285 | 0.212 | 0.050718 | -0.097212 | 0.043656 | 0.036953 | -0.02433 | 0.010561 | 0.059192 | 0.12718 | 0.007062 | 0.075048
1828.5781 | 121.4767 | -121.0602 | 0.44403 | 0.076067 | -0.013048 | 0.029208 | -0.020438 | 0.11867 | 0.067269 | -0.039826 | 0.079959 | 0.19827 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.04722 | -0.003172 | 121.1362 | 121.0471 | 121.0894 | 121.0397 | 121.1788 | 121.1274 | 121.0204 | 0.09827 | 0.21658 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.028909 | 0.015139 | 0.054614 | 0.12718 | 0.007062 | 0.079627
1830.2812 | 121.5179 | -121.0739 | 0.4303 | 0.076067 | -0.013048 | 0.024629 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.089116 | 0.19369 | 0.027829 | -0.11552 | 0.029923 | 0.02322 | -0.04722 | -0.00775 | 121.15 | 121.0609 | 121.0985 | 121.0535 | 121.1788 | 121.1412 | 121.0341 | 0.10743 | 0.212 | 0.04614 | -0.097212 | 0.048234 | 0.041531 | -0.028909 | 0.010561 | 0.059193 | 0.13634 | -0.002094 | 0.075049
1831.9688 | 121.6095 | -121.051 | 0.41199 | 0.076067 | -0.013048 | 0.029208 | -0.01586 | 0.11409 | 0.067269 | -0.039826 | 0.079959 | 0.19369 | 0.036985 | -0.11552 | 0.025345 | 0.018642 | -0.038063 | -0.003172 | 121.1271 | 121.038 | 121.0802 | 121.0352 | 121.1651 | 121.1183 | 121.0112 | 0.09827 | 0.212 | 0.055296 | -0.097212 | 0.043656 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.11802 | 0.01164 | 0.075048
1833.6406 | 121.4951 | -121.0968 | 0.41657 | 0.071489 | -0.017627 | 0.033786 | -0.025017 | 0.10951 | 0.071848 | -0.035248 | 0.07538 | 0.18911 | 0.036985 | -0.11094 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 121.1683 | 121.0792 | 121.1306 | 121.0718 | 121.2063 | 121.1686 | 121.0616 | 0.093691 | 0.20742 | 0.055296 | -0.092633 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.045457 | 0.1226 | 0.007062 | 0.084205
1835.3594 | 121.4996 | -121.1426 | 0.42572 | 0.076067 | -0.017627 | 0.024629 | -0.01586 | 0.10951 | 0.067269 | -0.03067 | 0.079959 | 0.19827 | 0.032407 | -0.11094 | 0.025345 | 0.009486 | -0.042641 | -0.00775 | 121.2186 | 121.125 | 121.1672 | 121.1267 | 121.2521 | 121.2098 | 121.1119 | 0.09827 | 0.21658 | 0.050718 | -0.092633 | 0.043656 | 0.027797 | -0.02433 | 0.010561 | 0.054614 | 0.1226 | 0.007062 | 0.075048
1837.0469 | 121.6049 | -121.1014 | 0.40283 | 0.076067 | -0.022205 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.035248 | 0.084537 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.003172 | 121.1774 | 121.0792 | 121.126 | 121.0809 | 121.2109 | 121.1686 | 121.0661 | 0.10285 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1838.7188 | 121.5546 | -121.1014 | 0.4303 | 0.071489 | -0.017627 | 0.029208 | -0.01586 | 0.10036 | 0.067269 | -0.039826 | 0.07538 | 0.19369 | 0.036985 | -0.11552 | 0.034501 | 0.018642 | -0.038063 | -0.003172 | 121.1729 | 121.0838 | 121.1306 | 121.0855 | 121.2017 | 121.1686 | 121.0616 | 0.093691 | 0.212 | 0.055296 | -0.097212 | 0.052812 | 0.036953 | -0.019752 | 0.015139 | 0.040879 | 0.11344 | 0.002484 | 0.075048
1840.4688 | 121.5225 | -121.1105 | 0.42114 | 0.080646 | -0.017627 | 0.033786 | -0.01586 | 0.10951 | 0.076426 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 121.1912 | 121.0929 | 121.1443 | 121.0947 | 121.22 | 121.187 | 121.0707 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | -0.006672 | 0.07047
1842.2031 | 121.5134 | -121.1655 | 0.40741 | 0.080646 | -0.017627 | 0.029208 | -0.01586 | 0.10951 | 0.071848 | -0.039826 | 0.084537 | 0.18453 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.2461 | 121.1478 | 121.1947 | 121.1496 | 121.275 | 121.2373 | 121.1256 | 0.10285 | 0.20284 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | 0.002484 | 0.07047
1843.875 | 121.5591 | -121.1517 | 0.38452 | 0.071489 | -0.017627 | 0.038365 | -0.020438 | 0.10951 | 0.071848 | -0.035248 | 0.07538 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 121.2232 | 121.1341 | 121.1901 | 121.1313 | 121.2612 | 121.2236 | 121.1165 | 0.093691 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.002484 | 0.075048
1845.5625 | 121.6003 | -121.1288 | 0.37537 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.18911 | 0.036985 | -0.11552 | 0.034501 | 0.018642 | -0.038063 | -0.003172 | 121.2049 | 121.1066 | 121.1581 | 121.113 | 121.2384 | 121.1961 | 121.089 | 0.10743 | 0.20742 | 0.055296 | -0.097212 | 0.052812 | 0.036953 | -0.019752 | 0.015139 | 0.054615 | 0.12718 | 0.002484 | 0.075048
1847.2344 | 121.5683 | -121.138 | 0.39825 | 0.080646 | -0.017627 | 0.024629 | -0.01586 | 0.11867 | 0.071848 | -0.035248 | 0.070802 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 121.2186 | 121.1204 | 121.1626 | 121.1221 | 121.2567 | 121.2098 | 121.1028 | 0.089113 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | 0.002484 | 0.075048
1848.9219 | 121.5454 | -121.1929 | 0.3891 | 0.080646 | -0.017627 | 0.029208 | -0.020438 | 0.11867 | 0.067269 | -0.039826 | 0.079959 | 0.19369 | 0.036985 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | -0.003172 | 121.2736 | 121.1753 | 121.2221 | 121.1725 | 121.3116 | 121.2602 | 121.1531 | 0.09827 | 0.212 | 0.055296 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.11802 | 0.01164 | 0.075048
1850.5938 | 121.6049 | -121.1426 | 0.36163 | 0.076067 | -0.022205 | 0.029208 | -0.020438 | 0.10951 | 0.067269 | -0.044405 | 0.079959 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.2186 | 121.1204 | 121.1718 | 121.1221 | 121.2521 | 121.2098 | 121.0982 | 0.09827 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | -0.002094 | 0.07047
1852.2969 | 121.6553 | -121.1151 | 0.36163 | 0.071489 | -0.013048 | 0.024629 | -0.020438 | 0.11409 | 0.067269 | -0.035248 | 0.089116 | 0.18911 | 0.032407 | -0.12926 | 0.025345 | 0.02322 | -0.038063 | -0.003172 | 121.1866 | 121.1021 | 121.1397 | 121.0947 | 121.2292 | 121.1824 | 121.0799 | 0.10743 | 0.20742 | 0.050718 | -0.11095 | 0.043656 | 0.041531 | -0.019752 | 0.015139 | 0.063771 | 0.12718 | 0.007062 | 0.07047
1854.0156 | 121.6644 | -121.1472 | 0.37079 | 0.076067 | -0.013048 | 0.029208 | -0.020438 | 0.11409 | 0.062691 | -0.039826 | 0.084537 | 0.18911 | 0.02325 | -0.11552 | 0.025345 | 0.02322 | -0.042641 | -0.003172 | 121.2232 | 121.1341 | 121.1764 | 121.1267 | 121.2612 | 121.2098 | 121.1073 | 0.10285 | 0.20742 | 0.041561 | -0.097212 | 0.043656 | 0.041531 | -0.02433 | 0.015139 | 0.059192 | 0.12718 | -0.002095 | 0.065891
1855.7031 | 121.5775 | -121.1792 | 0.3891 | 0.085224 | -0.013048 | 0.038365 | -0.01586 | 0.10493 | 0.062691 | -0.039826 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.014064 | -0.042641 | -0.00775 | 121.2644 | 121.1662 | 121.2176 | 121.1633 | 121.2841 | 121.2419 | 121.1394 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.032375 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.002484 | 0.075048
1857.3906 | 121.5866 | -121.1884 | 0.37537 | 0.076067 | -0.013048 | 0.029208 | -0.01586 | 0.11409 | 0.076426 | -0.044405 | 0.089116 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.2644 | 121.1753 | 121.2176 | 121.1725 | 121.3024 | 121.2648 | 121.1439 | 0.10743 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1859.125 | 121.6782 | -121.1426 | 0.37079 | 0.071489 | -0.017627 | 0.020051 | -0.020438 | 0.10951 | 0.062691 | -0.039826 | 0.084537 | 0.19369 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.2141 | 121.125 | 121.1626 | 121.1221 | 121.2521 | 121.2053 | 121.1028 | 0.10285 | 0.212 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.050036 | 0.12718 | -0.006672 | 0.07047
1860.8281 | 121.5912 | -121.1975 | 0.41657 | 0.076067 | -0.017627 | 0.029208 | -0.025017 | 0.11409 | 0.071848 | -0.035248 | 0.079959 | 0.19369 | 0.036985 | -0.12468 | 0.029923 | 0.018642 | -0.04722 | 0.001406 | 121.2736 | 121.1799 | 121.2267 | 121.1725 | 121.3116 | 121.2694 | 121.1623 | 0.09827 | 0.212 | 0.055296 | -0.10637 | 0.048234 | 0.036953 | -0.028909 | 0.019717 | 0.050036 | 0.12718 | 0.007062 | 0.084205
1862.5156 | 121.55 | -121.2021 | 0.41657 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.039826 | 0.089116 | 0.18911 | 0.027829 | -0.12468 | 0.034501 | 0.02322 | -0.04722 | 0.001406 | 121.2782 | 121.1799 | 121.2313 | 121.1862 | 121.3116 | 121.2694 | 121.1623 | 0.10743 | 0.20742 | 0.04614 | -0.10637 | 0.052812 | 0.041531 | -0.028909 | 0.019717 | 0.054615 | 0.13634 | -0.006672 | 0.075049
1864.2188 | 121.5546 | -121.2204 | 0.37079 | 0.076067 | -0.017627 | 0.033786 | -0.020438 | 0.10951 | 0.067269 | -0.044405 | 0.079959 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.04722 | -0.012328 | 121.2965 | 121.2028 | 121.2542 | 121.2 | 121.3299 | 121.2877 | 121.176 | 0.09827 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.028909 | 0.005983 | 0.050036 | 0.12718 | 0.002484 | 0.079627
1865.9219 | 121.5408 | -121.2341 | 0.36163 | 0.071489 | -0.017627 | 0.033786 | -0.025017 | 0.10951 | 0.067269 | -0.035248 | 0.084537 | 0.19369 | 0.027829 | -0.1201 | 0.020767 | 0.018642 | -0.051798 | -0.00775 | 121.3056 | 121.2165 | 121.2679 | 121.2091 | 121.3436 | 121.3014 | 121.1989 | 0.10285 | 0.212 | 0.04614 | -0.10179 | 0.039078 | 0.036953 | -0.033487 | 0.010561 | 0.06377 | 0.13633 | 0.007062 | 0.079627
1867.5938 | 121.7102 | -121.1792 | 0.34332 | 0.071489 | -0.031363 | 0.033786 | -0.01586 | 0.10951 | 0.067269 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.11094 | 0.039079 | 0.018642 | -0.042641 | -0.00775 | 121.2507 | 121.1478 | 121.213 | 121.1633 | 121.2887 | 121.2465 | 121.1394 | 0.09827 | 0.20742 | 0.050718 | -0.092633 | 0.05739 | 0.036953 | -0.02433 | 0.010561 | 0.04088 | 0.1226 | -0.006672 | 0.075048
1869.2812 | 121.6095 | -121.2524 | 0.37079 | 0.071489 | -0.026784 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.039826 | 0.084537 | 0.18453 | 0.032407 | -0.11552 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.3239 | 121.2257 | 121.2816 | 121.232 | 121.3665 | 121.3243 | 121.2126 | 0.10285 | 0.20284 | 0.050718 | -0.097212 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.054614 | 0.12718 | 0.002484 | 0.075048
1871 | 121.6599 | -121.2158 | 0.33875 | 0.080646 | -0.022205 | 0.029208 | -0.020438 | 0.10493 | 0.062691 | -0.035248 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.032376 | -0.042641 | -0.003172 | 121.2965 | 121.1936 | 121.245 | 121.1954 | 121.3208 | 121.2785 | 121.1806 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.050687 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | -0.002094 | 0.07047
1872.7031 | 121.5775 | -121.2387 | 0.37079 | 0.076067 | -0.017627 | 0.024629 | -0.01586 | 0.11867 | 0.071848 | -0.039826 | 0.079959 | 0.19827 | 0.032407 | -0.11094 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 121.3148 | 121.2211 | 121.2633 | 121.2228 | 121.3574 | 121.3106 | 121.1989 | 0.09827 | 0.21658 | 0.050718 | -0.092633 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.002484 | 0.075048
1874.4531 | 121.582 | -121.2708 | 0.37994 | 0.071489 | -0.026784 | 0.024629 | -0.01586 | 0.10951 | 0.062691 | -0.044405 | 0.07538 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.016906 | 121.3422 | 121.244 | 121.2954 | 121.2549 | 121.3803 | 121.3334 | 121.2263 | 0.093691 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.001405 | 0.045457 | 0.11802 | 0.007062 | 0.079626
1876.1406 | 121.7102 | -121.2158 | 0.32959 | 0.080646 | -0.017627 | 0.029208 | -0.025017 | 0.10036 | 0.062691 | -0.039826 | 0.084537 | 0.19369 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.00775 | 121.2965 | 121.1982 | 121.245 | 121.1908 | 121.3162 | 121.2785 | 121.176 | 0.10285 | 0.212 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.010561 | 0.054614 | 0.13176 | -0.006673 | 0.07047
1877.8281 | 121.5729 | -121.2708 | 0.35248 | 0.076067 | -0.017627 | 0.033786 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.079959 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.033484 | -0.003172 | 121.3468 | 121.2531 | 121.3045 | 121.2503 | 121.3803 | 121.338 | 121.2309 | 0.09827 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.015173 | 0.015139 | 0.050036 | 0.11344 | -0.002094 | 0.061313
1879.5469 | 121.6187 | -121.2753 | 0.34332 | 0.071489 | -0.017627 | 0.033786 | -0.01586 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.018642 | -0.04722 | -0.003172 | 121.3468 | 121.2577 | 121.3091 | 121.2595 | 121.3848 | 121.3426 | 121.2401 | 0.09827 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.036953 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | 0.002484 | 0.079627
1881.2344 | 121.7056 | -121.2479 | 0.32044 | 0.071489 | -0.017627 | 0.024629 | -0.020438 | 0.10951 | 0.076426 | -0.035248 | 0.079959 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 121.3194 | 121.2302 | 121.2725 | 121.2274 | 121.3574 | 121.3243 | 121.2126 | 0.09827 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.050036 | 0.11802 | 0.002484 | 0.07047
1882.9062 | 121.5958 | -121.2982 | 0.33417 | 0.076067 | -0.022205 | 0.033786 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 121.3743 | 121.276 | 121.332 | 121.2778 | 121.4032 | 121.3655 | 121.2584 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.045457 | 0.11344 | 0.002484 | 0.07047
1884.6094 | 121.5912 | -121.3074 | 0.34332 | 0.071489 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.035248 | 0.07538 | 0.18453 | 0.027829 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 121.3789 | 121.2806 | 121.3366 | 121.2869 | 121.4169 | 121.3792 | 121.2721 | 0.093691 | 0.20284 | 0.04614 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11802 | -0.006672 | 0.07047
1886.2969 | 121.6187 | -121.2753 | 0.34332 | 0.071489 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18453 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 121.3468 | 121.2485 | 121.3045 | 121.2549 | 121.3848 | 121.3472 | 121.2355 | 0.09827 | 0.20284 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.002484 | 0.079627
1887.9688 | 121.637 | -121.2936 | 0.33417 | 0.076067 | -0.017627 | 0.024629 | -0.011281 | 0.10951 | 0.071848 | -0.035248 | 0.084537 | 0.19369 | 0.036985 | -0.1201 | 0.039079 | 0.014064 | -0.033484 | -0.00775 | 121.3697 | 121.276 | 121.3183 | 121.2824 | 121.4032 | 121.3655 | 121.2584 | 0.10285 | 0.212 | 0.055296 | -0.10179 | 0.05739 | 0.032375 | -0.015173 | 0.010561 | 0.045458 | 0.11802 | -0.002094 | 0.070469
1889.6562 | 121.6141 | -121.2891 | 0.37537 | 0.076067 | -0.022205 | 0.024629 | -0.011281 | 0.10951 | 0.062691 | -0.039826 | 0.084537 | 0.18453 | 0.027829 | -0.12468 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 121.3651 | 121.2669 | 121.3137 | 121.2778 | 121.3986 | 121.3518 | 121.2492 | 0.10285 | 0.20284 | 0.04614 | -0.10637 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.054614 | 0.1226 | -0.002094 | 0.065892
1891.3281 | 121.6187 | -121.2845 | 0.35706 | 0.06691 | -0.013048 | 0.029208 | -0.025017 | 0.10951 | 0.062691 | -0.035248 | 0.079959 | 0.19369 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.033484 | -0.00775 | 121.3514 | 121.2714 | 121.3137 | 121.2595 | 121.394 | 121.3472 | 121.2492 | 0.09827 | 0.212 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.015173 | 0.010561 | 0.045458 | 0.11344 | -0.006672 | 0.061313
1893 | 121.7148 | -121.257 | 0.32044 | 0.071489 | -0.026784 | 0.024629 | -0.011281 | 0.10951 | 0.062691 | -0.039826 | 0.089116 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 121.3285 | 121.2302 | 121.2816 | 121.2457 | 121.3665 | 121.3197 | 121.2172 | 0.10743 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1894.6875 | 121.701 | -121.2799 | 0.33875 | 0.071489 | -0.022205 | 0.029208 | -0.020438 | 0.10036 | 0.071848 | -0.044405 | 0.084537 | 0.18911 | 0.032407 | -0.11094 | 0.025345 | 0.018642 | -0.033484 | -0.003172 | 121.3514 | 121.2577 | 121.3091 | 121.2595 | 121.3803 | 121.3518 | 121.2355 | 0.10285 | 0.20742 | 0.050718 | -0.092633 | 0.043656 | 0.036953 | -0.015173 | 0.015139 | 0.059192 | 0.11802 | 0.007062 | 0.065891
1896.375 | 121.7331 | -121.2708 | 0.31586 | 0.071489 | -0.017627 | 0.024629 | -0.025017 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.02322 | -0.04722 | -0.00775 | 121.3422 | 121.2531 | 121.2954 | 121.2457 | 121.3803 | 121.3426 | 121.2309 | 0.09827 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.041531 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.002484 | 0.079627
1898.0625 | 121.7148 | -121.2891 | 0.33417 | 0.076067 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.062691 | -0.039826 | 0.079959 | 0.19827 | 0.036985 | -0.11552 | 0.034501 | 0.02322 | -0.04722 | -0.00775 | 121.3651 | 121.2623 | 121.3183 | 121.2686 | 121.3986 | 121.3518 | 121.2492 | 0.09827 | 0.21658 | 0.055296 | -0.097212 | 0.052812 | 0.041531 | -0.028909 | 0.010561 | 0.045458 | 0.12718 | 0.002484 | 0.084205
1899.75 | 121.6187 | -121.3486 | 0.3479 | 0.06691 | -0.017627 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.07538 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.4155 | 121.3309 | 121.3732 | 121.3281 | 121.4581 | 121.4158 | 121.3087 | 0.093691 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.040879 | 0.11802 | -0.002094 | 0.075048
1901.5 | 121.6553 | -121.3486 | 0.31128 | 0.071489 | -0.026784 | 0.038365 | -0.029595 | 0.10493 | 0.071848 | -0.039826 | 0.089116 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 121.4201 | 121.3218 | 121.3869 | 121.319 | 121.4535 | 121.4204 | 121.3087 | 0.10743 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.059193 | 0.13176 | 0.002484 | 0.075048
1903.1875 | 121.7834 | -121.3074 | 0.30212 | 0.06691 | -0.017627 | 0.029208 | -0.020438 | 0.11409 | 0.067269 | -0.039826 | 0.07538 | 0.17995 | 0.027829 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | -0.00775 | 121.3743 | 121.2897 | 121.3366 | 121.2869 | 121.4215 | 121.3746 | 121.2675 | 0.093691 | 0.19826 | 0.04614 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.010561 | 0.050035 | 0.11802 | 0.002484 | 0.07047
1904.8906 | 121.637 | -121.3531 | 0.32044 | 0.071489 | -0.022205 | 0.029208 | -0.01586 | 0.10951 | 0.071848 | -0.03067 | 0.079959 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 121.4246 | 121.3309 | 121.3824 | 121.3373 | 121.4627 | 121.425 | 121.3225 | 0.09827 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.045458 | 0.1226 | 0.002484 | 0.079626
1906.5938 | 121.6095 | -121.3577 | 0.32959 | 0.076067 | -0.022205 | 0.029208 | -0.020438 | 0.10493 | 0.062691 | -0.035248 | 0.079959 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 121.4338 | 121.3355 | 121.3869 | 121.3373 | 121.4627 | 121.4204 | 121.3225 | 0.09827 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.050036 | 0.11802 | 0.002484 | 0.07047
1908.2969 | 121.7789 | -121.3577 | 0.27924 | 0.06691 | -0.022205 | 0.038365 | -0.011281 | 0.10493 | 0.067269 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 121.4246 | 121.3355 | 121.3961 | 121.3464 | 121.4627 | 121.425 | 121.3225 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.045457 | 0.11802 | 0.002484 | 0.075048
1909.9844 | 121.637 | -121.4035 | 0.3067 | 0.071489 | -0.017627 | 0.033786 | -0.020438 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 121.475 | 121.3859 | 121.4373 | 121.3831 | 121.513 | 121.4754 | 121.3637 | 0.09827 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | 0.002484 | 0.079627
1911.6719 | 121.6599 | -121.4035 | 0.27466 | 0.071489 | -0.017627 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.18911 | 0.02325 | -0.1201 | 0.034501 | 0.02322 | -0.04722 | -0.003172 | 121.475 | 121.3859 | 121.4281 | 121.3831 | 121.513 | 121.4708 | 121.3683 | 0.09827 | 0.20742 | 0.041561 | -0.10179 | 0.052812 | 0.041531 | -0.028909 | 0.015139 | 0.045458 | 0.12718 | -0.011251 | 0.07047
1913.4062 | 121.7331 | -121.3715 | 0.27466 | 0.071489 | -0.013048 | 0.029208 | -0.020438 | 0.10951 | 0.076426 | -0.039826 | 0.079959 | 0.19827 | 0.036985 | -0.12468 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 121.4429 | 121.3584 | 121.4007 | 121.351 | 121.481 | 121.4479 | 121.3316 | 0.09827 | 0.21658 | 0.055296 | -0.10637 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.050036 | 0.11802 | 0.007062 | 0.075048
1915.1406 | 121.7468 | -121.3806 | 0.26093 | 0.076067 | -0.017627 | 0.029208 | -0.020438 | 0.10493 | 0.067269 | -0.044405 | 0.07538 | 0.19827 | 0.027829 | -0.12468 | 0.025345 | 0.02322 | -0.038063 | -0.003172 | 121.4567 | 121.363 | 121.4098 | 121.3602 | 121.4855 | 121.4479 | 121.3362 | 0.093691 | 0.21658 | 0.04614 | -0.10637 | 0.043656 | 0.041531 | -0.019752 | 0.015139 | 0.050035 | 0.11344 | 0.002484 | 0.065892
1916.8281 | 121.5958 | -121.138 | 0.27008 | 0.06691 | -0.022205 | 0.029208 | -0.025017 | 0.10951 | 0.062691 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 121.2049 | 121.1158 | 121.1672 | 121.113 | 121.2475 | 121.2007 | 121.0982 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.050036 | 0.1226 | -0.002094 | 0.07047
1918.5469 | 121.6049 | -121.257 | 0.29755 | 0.071489 | -0.022205 | 0.024629 | -0.020438 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18911 | 0.02325 | -0.11094 | 0.034501 | 0.018642 | -0.04722 | -0.00775 | 121.3285 | 121.2348 | 121.2816 | 121.2366 | 121.3665 | 121.3289 | 121.2172 | 0.09827 | 0.20742 | 0.041561 | -0.092633 | 0.052812 | 0.036953 | -0.028909 | 0.010561 | 0.045458 | 0.12718 | -0.011251 | 0.07047
1920.2344 | 121.6507 | -121.2341 | 0.25177 | 0.071489 | -0.031363 | 0.024629 | -0.025017 | 0.11409 | 0.062691 | -0.035248 | 0.07538 | 0.19369 | 0.032407 | -0.1201 | 0.025345 | 0.02322 | -0.033484 | 0.001406 | 121.3056 | 121.2028 | 121.2588 | 121.2091 | 121.3482 | 121.2968 | 121.1989 | 0.093691 | 0.212 | 0.050718 | -0.10179 | 0.043656 | 0.041531 | -0.015173 | 0.019717 | 0.050035 | 0.10886 | 0.007062 | 0.065891
1921.9219 | 121.5683 | -121.3257 | 0.31128 | 0.080646 | -0.026784 | 0.029208 | -0.01586 | 0.11409 | 0.067269 | -0.039826 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 121.4063 | 121.2989 | 121.3549 | 121.3098 | 121.4398 | 121.393 | 121.2859 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.002484 | 0.075048
1923.6094 | 121.5958 | -121.3394 | 0.29297 | 0.080646 | -0.022205 | 0.024629 | -0.01586 | 0.10493 | 0.071848 | -0.035248 | 0.07538 | 0.18911 | 0.02325 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 121.4201 | 121.3172 | 121.364 | 121.3236 | 121.4444 | 121.4113 | 121.3042 | 0.093691 | 0.20742 | 0.041561 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.040879 | 0.11344 | -0.011251 | 0.061313
1925.2812 | 121.7102 | -121.2982 | 0.27466 | 0.076067 | -0.026784 | 0.024629 | -0.020438 | 0.10493 | 0.071848 | -0.039826 | 0.07538 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 121.3743 | 121.2714 | 121.3228 | 121.2778 | 121.4032 | 121.3701 | 121.2584 | 0.093691 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | -0.006673 | 0.061313
1926.9688 | 121.6599 | -121.3257 | 0.29297 | 0.071489 | -0.026784 | 0.029208 | -0.011281 | 0.10951 | 0.076426 | -0.026092 | 0.079959 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | 0.001406 | 121.3972 | 121.2989 | 121.3549 | 121.3144 | 121.4352 | 121.4021 | 121.2996 | 0.09827 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.019717 | 0.050036 | 0.1226 | 0.002484 | 0.075048
1928.6562 | 121.7331 | -121.312 | 0.26093 | 0.071489 | -0.022205 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.18453 | 0.027829 | -0.1201 | 0.039079 | 0.014064 | -0.042641 | -0.00775 | 121.3834 | 121.2897 | 121.3412 | 121.2869 | 121.4215 | 121.3792 | 121.2767 | 0.09827 | 0.20284 | 0.04614 | -0.10179 | 0.05739 | 0.032375 | -0.02433 | 0.010561 | 0.04088 | 0.1226 | -0.01125 | 0.07047
1930.375 | 121.6232 | -121.344 | 0.32044 | 0.076067 | -0.022205 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.039826 | 0.070802 | 0.18911 | 0.032407 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 121.4201 | 121.3218 | 121.3686 | 121.3281 | 121.4535 | 121.4158 | 121.3042 | 0.089113 | 0.20742 | 0.050718 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.036301 | 0.11344 | -0.002094 | 0.075048
1932.0469 | 121.7056 | -121.3348 | 0.28839 | 0.071489 | -0.031363 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.048983 | 0.079959 | 0.19369 | 0.027829 | -0.11552 | 0.034501 | 0.027798 | -0.033484 | 0.001406 | 121.4063 | 121.3035 | 121.3595 | 121.3098 | 121.4444 | 121.4021 | 121.2859 | 0.09827 | 0.212 | 0.04614 | -0.097212 | 0.052812 | 0.046109 | -0.015173 | 0.019717 | 0.045458 | 0.11344 | -0.006672 | 0.061313
1933.7188 | 121.7468 | -121.3394 | 0.29297 | 0.076067 | -0.026784 | 0.029208 | -0.020438 | 0.10036 | 0.071848 | -0.039826 | 0.079959 | 0.19369 | 0.02325 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.4155 | 121.3126 | 121.3686 | 121.319 | 121.4398 | 121.4113 | 121.2996 | 0.09827 | 0.212 | 0.041561 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | -0.011251 | 0.065891
1935.4062 | 121.6232 | -121.3806 | 0.31586 | 0.06691 | -0.017627 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.044405 | 0.084537 | 0.19369 | 0.036985 | -0.12468 | 0.029923 | 0.018642 | -0.033484 | -0.00775 | 121.4475 | 121.363 | 121.4098 | 121.3602 | 121.4947 | 121.4525 | 121.3362 | 0.10285 | 0.212 | 0.055296 | -0.10637 | 0.048234 | 0.036953 | -0.015173 | 0.010561 | 0.054614 | 0.11802 | 0.007062 | 0.070469
1937.0938 | 121.7102 | -121.3669 | 0.29755 | 0.076067 | -0.026784 | 0.029208 | -0.020438 | 0.10036 | 0.067269 | -0.039826 | 0.07538 | 0.18453 | 0.027829 | -0.12468 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 121.4429 | 121.3401 | 121.3961 | 121.3464 | 121.4672 | 121.4342 | 121.3271 | 0.093691 | 0.20284 | 0.04614 | -0.10637 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | -0.002094 | 0.07047
1938.7812 | 121.7606 | -121.2982 | 0.28381 | 0.076067 | -0.017627 | 0.024629 | -0.020438 | 0.10951 | 0.062691 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.11094 | 0.025345 | 0.02322 | -0.038063 | -0.00775 | 121.3743 | 121.2806 | 121.3228 | 121.2778 | 121.4077 | 121.3609 | 121.263 | 0.093691 | 0.20742 | 0.04614 | -0.092633 | 0.043656 | 0.041531 | -0.019752 | 0.010561 | 0.050035 | 0.11344 | 0.002484 | 0.065892
1940.5156 | 121.788 | -121.3486 | 0.27466 | 0.076067 | -0.022205 | 0.029208 | -0.025017 | 0.11409 | 0.062691 | -0.039826 | 0.070802 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.027798 | -0.042641 | -0.003172 | 121.4246 | 121.3264 | 121.3778 | 121.3236 | 121.4627 | 121.4113 | 121.3087 | 0.089113 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.046109 | -0.02433 | 0.015139 | 0.036301 | 0.11344 | -0.002094 | 0.075048
1942.2031 | 121.7285 | -121.2845 | 0.25635 | 0.071489 | -0.013048 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 121.356 | 121.2714 | 121.3137 | 121.2686 | 121.394 | 121.3518 | 121.2492 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1943.9062 | 121.6599 | -121.3211 | 0.28381 | 0.080646 | -0.022205 | 0.033786 | -0.020438 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.19369 | 0.027829 | -0.12468 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.4018 | 121.2989 | 121.3549 | 121.3007 | 121.4306 | 121.3884 | 121.2859 | 0.09827 | 0.212 | 0.04614 | -0.10637 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | -0.006672 | 0.07047
1945.6094 | 121.637 | -121.3486 | 0.28381 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.11409 | 0.076426 | -0.035248 | 0.070802 | 0.18911 | 0.027829 | -0.12468 | 0.025345 | 0.02322 | -0.038063 | -0.012328 | 121.4246 | 121.3264 | 121.3778 | 121.3327 | 121.4627 | 121.425 | 121.3133 | 0.089113 | 0.20742 | 0.04614 | -0.10637 | 0.043656 | 0.041531 | -0.019752 | 0.005983 | 0.045457 | 0.10887 | 0.002484 | 0.065892
1947.2812 | 121.7606 | -121.3211 | 0.2655 | 0.071489 | -0.022205 | 0.029208 | -0.020438 | 0.10493 | 0.076426 | -0.035248 | 0.070802 | 0.18453 | 0.036985 | -0.11552 | 0.029923 | 0.018642 | -0.033484 | -0.003172 | 121.3926 | 121.2989 | 121.3503 | 121.3007 | 121.426 | 121.3975 | 121.2859 | 0.089113 | 0.20284 | 0.055296 | -0.097212 | 0.048234 | 0.036953 | -0.015173 | 0.015139 | 0.040879 | 0.10429 | 0.007062 | 0.070469
1948.9688 | 121.6461 | -121.3943 | 0.29297 | 0.076067 | -0.017627 | 0.029208 | -0.01586 | 0.10493 | 0.067269 | -0.035248 | 0.07538 | 0.18453 | 0.036985 | -0.1201 | 0.034501 | 0.014064 | -0.042641 | -0.00775 | 121.4704 | 121.3767 | 121.4236 | 121.3785 | 121.4993 | 121.4616 | 121.3591 | 0.093691 | 0.20284 | 0.055296 | -0.10179 | 0.052812 | 0.032375 | -0.02433 | 0.010561 | 0.040879 | 0.11802 | 0.002484 | 0.079626
1950.6562 | 121.582 | -121.2479 | 0.21515 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.11409 | 0.071848 | -0.039826 | 0.079959 | 0.18453 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 121.3239 | 121.2257 | 121.2771 | 121.232 | 121.362 | 121.3197 | 121.208 | 0.09827 | 0.20284 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1952.3281 | 121.7194 | -121.3028 | 0.21515 | 0.071489 | -0.022205 | 0.029208 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.070802 | 0.19369 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.042641 | -0.003172 | 121.3743 | 121.2806 | 121.332 | 121.2824 | 121.4123 | 121.3701 | 121.263 | 0.089113 | 0.212 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.02433 | 0.015139 | 0.045457 | 0.11344 | 0.002484 | 0.07047
1954.0156 | 121.6507 | -121.3486 | 0.23346 | 0.076067 | -0.022205 | 0.024629 | -0.01586 | 0.10951 | 0.076426 | -0.039826 | 0.079959 | 0.18911 | 0.02325 | -0.12926 | 0.039079 | 0.018642 | -0.042641 | 0.005985 | 121.4246 | 121.3264 | 121.3732 | 121.3327 | 121.4581 | 121.425 | 121.3087 | 0.09827 | 0.20742 | 0.041561 | -0.11095 | 0.05739 | 0.036953 | -0.02433 | 0.024296 | 0.04088 | 0.1226 | -0.015829 | 0.065891
1955.7031 | 121.7194 | -121.3531 | 0.20142 | 0.071489 | -0.017627 | 0.033786 | -0.01586 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.19369 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | -0.00775 | 121.4246 | 121.3355 | 121.3869 | 121.3373 | 121.4627 | 121.4204 | 121.3179 | 0.09827 | 0.212 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.010561 | 0.050036 | 0.11802 | -0.006673 | 0.061313
1957.3906 | 121.7468 | -121.3486 | 0.19684 | 0.062332 | -0.013048 | 0.033786 | -0.020438 | 0.11409 | 0.067269 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 121.4109 | 121.3355 | 121.3824 | 121.3281 | 121.4627 | 121.4158 | 121.3133 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.045457 | 0.11344 | 0.002484 | 0.07047
1959.0781 | 121.6187 | -121.4081 | 0.29297 | 0.080646 | -0.022205 | 0.029208 | -0.01586 | 0.10493 | 0.071848 | -0.035248 | 0.079959 | 0.18453 | 0.036985 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.4887 | 121.3859 | 121.4373 | 121.3922 | 121.513 | 121.4799 | 121.3728 | 0.09827 | 0.20284 | 0.055296 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | 0.007062 | 0.075048
1960.7656 | 121.7468 | -121.3531 | 0.23804 | 0.076067 | -0.022205 | 0.029208 | -0.020438 | 0.10036 | 0.076426 | -0.039826 | 0.079959 | 0.19369 | 0.032407 | -0.11094 | 0.025345 | 0.018642 | -0.042641 | -0.00775 | 121.4292 | 121.3309 | 121.3824 | 121.3327 | 121.4535 | 121.4296 | 121.3133 | 0.09827 | 0.212 | 0.050718 | -0.092633 | 0.043656 | 0.036953 | -0.02433 | 0.010561 | 0.054614 | 0.1226 | 0.007062 | 0.075048
1962.5 | 121.7056 | -121.3943 | 0.23346 | 0.071489 | -0.026784 | 0.029208 | -0.020438 | 0.11867 | 0.071848 | -0.035248 | 0.079959 | 0.19369 | 0.032407 | -0.12468 | 0.020767 | 0.027798 | -0.038063 | -0.003172 | 121.4658 | 121.3676 | 121.4236 | 121.3739 | 121.513 | 121.4662 | 121.3591 | 0.09827 | 0.212 | 0.050718 | -0.10637 | 0.039078 | 0.046109 | -0.019752 | 0.015139 | 0.059192 | 0.11802 | 0.01164 | 0.07047
1964.1719 | 121.6782 | -121.4218 | 0.23804 | 0.076067 | -0.013048 | 0.033786 | -0.01586 | 0.11867 | 0.076426 | -0.035248 | 0.079959 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.003172 | 121.4979 | 121.4088 | 121.4556 | 121.406 | 121.5405 | 121.4982 | 121.3866 | 0.09827 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | 0.002484 | 0.075048
1965.8594 | 121.7743 | -121.3806 | 0.2243 | 0.076067 | -0.017627 | 0.033786 | -0.01586 | 0.11867 | 0.071848 | -0.035248 | 0.084537 | 0.18911 | 0.02325 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.4567 | 121.363 | 121.4144 | 121.3648 | 121.4993 | 121.4525 | 121.3454 | 0.10285 | 0.20742 | 0.041561 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | -0.006673 | 0.061313
1967.5781 | 121.7194 | -121.431 | 0.2243 | 0.071489 | -0.022205 | 0.024629 | -0.020438 | 0.11409 | 0.067269 | -0.035248 | 0.07538 | 0.19369 | 0.027829 | -0.1201 | 0.034501 | 0.014064 | -0.042641 | 0.001406 | 121.5025 | 121.4088 | 121.4556 | 121.4105 | 121.5451 | 121.4982 | 121.3957 | 0.093691 | 0.212 | 0.04614 | -0.10179 | 0.052812 | 0.032375 | -0.02433 | 0.019717 | 0.040879 | 0.11802 | -0.006672 | 0.07047
1969.2656 | 121.701 | -121.4264 | 0.2655 | 0.071489 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.081005 | -0.035248 | 0.07538 | 0.19369 | 0.032407 | -0.1201 | 0.025345 | 0.014064 | -0.042641 | 0.001406 | 121.4979 | 121.3996 | 121.4556 | 121.4105 | 121.5359 | 121.5074 | 121.3911 | 0.093691 | 0.212 | 0.050718 | -0.10179 | 0.043656 | 0.032375 | -0.02433 | 0.019717 | 0.050035 | 0.11802 | 0.007062 | 0.075048
1970.9531 | 121.6553 | -121.3806 | 0.31586 | 0.080646 | -0.017627 | 0.033786 | -0.01586 | 0.12325 | 0.067269 | -0.03067 | 0.079959 | 0.17995 | 0.02325 | -0.12468 | 0.020767 | 0.02322 | -0.038063 | -0.00775 | 121.4613 | 121.363 | 121.4144 | 121.3648 | 121.5039 | 121.4479 | 121.3499 | 0.09827 | 0.19826 | 0.041561 | -0.10637 | 0.039078 | 0.041531 | -0.019752 | 0.010561 | 0.059192 | 0.11802 | 0.002483 | 0.061313
1972.6562 | 121.7606 | -121.3943 | 0.23346 | 0.071489 | -0.017627 | 0.024629 | -0.020438 | 0.10493 | 0.076426 | -0.039826 | 0.079959 | 0.18911 | 0.027829 | -0.1201 | 0.034501 | 0.027798 | -0.038063 | -0.003172 | 121.4658 | 121.3767 | 121.419 | 121.3739 | 121.4993 | 121.4708 | 121.3545 | 0.09827 | 0.20742 | 0.04614 | -0.10179 | 0.052812 | 0.046109 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | -0.006672 | 0.065892
1974.3281 | 121.7834 | -121.3348 | 0.27008 | 0.071489 | -0.026784 | 0.024629 | -0.01586 | 0.10951 | 0.058113 | -0.044405 | 0.07538 | 0.19369 | 0.027829 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | -0.00775 | 121.4063 | 121.3081 | 121.3595 | 121.319 | 121.4444 | 121.393 | 121.2904 | 0.093691 | 0.212 | 0.04614 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.010561 | 0.050035 | 0.11802 | 0.002484 | 0.07047
1976.0156 | 120.9778 | -119.1422 | 1.7212 | 0.06691 | -0.017627 | 0.029208 | -0.01586 | 0.10951 | 0.071848 | -0.03067 | 0.07538 | 0.18911 | 0.032407 | -0.12468 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 119.2091 | 119.1245 | 119.1714 | 119.1263 | 119.2517 | 119.214 | 119.1115 | 0.093691 | 0.20742 | 0.050718 | -0.10637 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.040879 | 0.11344 | -0.002094 | 0.07047
1977.7031 | 121.344 | -120.3415 | 0.97504 | 0.071489 | -0.026784 | 0.024629 | -0.011281 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 120.413 | 120.3147 | 120.3661 | 120.3302 | 120.451 | 120.4133 | 120.3017 | 0.09827 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | -0.002094 | 0.07047
1979.4062 | 121.4493 | -120.6848 | 0.71411 | 0.071489 | -0.022205 | 0.024629 | -0.01586 | 0.11409 | 0.067269 | -0.044405 | 0.070802 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.012328 | 120.7563 | 120.6626 | 120.7094 | 120.669 | 120.7989 | 120.7521 | 120.6404 | 0.089113 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.005983 | 0.040879 | 0.10887 | 0.002484 | 0.07047
1981.1094 | 121.3989 | -120.5933 | 0.87433 | 0.06691 | -0.022205 | 0.033786 | -0.01586 | 0.10951 | 0.071848 | -0.035248 | 0.079959 | 0.18911 | 0.027829 | -0.11552 | 0.034501 | 0.018642 | -0.042641 | -0.00775 | 120.6602 | 120.5711 | 120.627 | 120.5774 | 120.7028 | 120.6651 | 120.558 | 0.09827 | 0.20742 | 0.04614 | -0.097212 | 0.052812 | 0.036953 | -0.02433 | 0.010561 | 0.045458 | 0.1226 | -0.006672 | 0.07047
1982.7969 | 121.5775 | -120.6573 | 0.74616 | 0.06691 | -0.026784 | 0.024629 | -0.020438 | 0.10951 | 0.076426 | -0.039826 | 0.084537 | 0.18911 | 0.036985 | -0.11552 | 0.029923 | 0.018642 | -0.033484 | -0.00775 | 120.7243 | 120.6306 | 120.682 | 120.6369 | 120.7669 | 120.7338 | 120.6175 | 0.10285 | 0.20742 | 0.055296 | -0.097212 | 0.048234 | 0.036953 | -0.015173 | 0.010561 | 0.054614 | 0.11802 | 0.007062 | 0.070469
1984.4844 | 121.6049 | -120.6894 | 0.71869 | 0.071489 | -0.022205 | 0.020051 | -0.011281 | 0.10493 | 0.062691 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 120.7609 | 120.6672 | 120.7094 | 120.6781 | 120.7943 | 120.7521 | 120.6541 | 0.093691 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.045457 | 0.1226 | -0.002094 | 0.075049
1986.1719 | 121.6278 | -120.8176 | 0.54016 | 0.071489 | -0.035942 | 0.024629 | -0.029595 | 0.10493 | 0.071848 | -0.039826 | 0.070802 | 0.18453 | 0.032407 | -0.1201 | 0.034501 | 0.027798 | -0.038063 | -0.00775 | 120.8891 | 120.7816 | 120.8422 | 120.788 | 120.9225 | 120.8894 | 120.7777 | 0.089113 | 0.20284 | 0.050718 | -0.10179 | 0.052812 | 0.046109 | -0.019752 | 0.010561 | 0.036301 | 0.10887 | -0.002094 | 0.07047
1987.8438 | 121.6003 | -120.8313 | 0.59509 | 0.076067 | -0.031363 | 0.029208 | -0.020438 | 0.11409 | 0.081005 | -0.03067 | 0.079959 | 0.18453 | 0.032407 | -0.11552 | 0.025345 | 0.014064 | -0.042641 | -0.012328 | 120.9074 | 120.7999 | 120.8605 | 120.8109 | 120.9454 | 120.9123 | 120.8006 | 0.09827 | 0.20284 | 0.050718 | -0.097212 | 0.043656 | 0.032375 | -0.02433 | 0.005983 | 0.054614 | 0.1226 | 0.007062 | 0.075048
1989.5156 | 121.6553 | -121.019 | 0.45319 | 0.06691 | -0.031363 | 0.024629 | -0.01586 | 0.11409 | 0.071848 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.11552 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.0859 | 120.9876 | 121.0436 | 121.0031 | 121.1331 | 121.0908 | 120.9792 | 0.09827 | 0.212 | 0.04614 | -0.097212 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | -0.002094 | 0.065892
1991.2344 | 121.5225 | -121.1014 | 0.49439 | 0.076067 | -0.017627 | 0.024629 | -0.011281 | 0.11409 | 0.076426 | -0.035248 | 0.07538 | 0.19369 | 0.036985 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 121.1774 | 121.0838 | 121.126 | 121.0901 | 121.2155 | 121.1778 | 121.0661 | 0.093691 | 0.212 | 0.055296 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.007062 | 0.079626
1992.9219 | 121.6049 | -121.1151 | 0.40741 | 0.071489 | -0.013048 | 0.029208 | -0.011281 | 0.11409 | 0.062691 | -0.039826 | 0.07538 | 0.19369 | 0.027829 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | -0.00775 | 121.1866 | 121.1021 | 121.1443 | 121.1038 | 121.2292 | 121.1778 | 121.0753 | 0.093691 | 0.212 | 0.04614 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.010561 | 0.050035 | 0.11802 | 0.002484 | 0.07047
1994.625 | 121.6461 | -121.106 | 0.39368 | 0.076067 | -0.017627 | 0.033786 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.084537 | 0.18911 | 0.02325 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | -0.016906 | 121.182 | 121.0883 | 121.1397 | 121.0809 | 121.2155 | 121.1732 | 121.0661 | 0.10285 | 0.20742 | 0.041561 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.001405 | 0.059192 | 0.1226 | -0.002095 | 0.061313
1996.3438 | 121.7056 | -121.0739 | 0.44861 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.11409 | 0.067269 | -0.048983 | 0.079959 | 0.19369 | 0.036985 | -0.11552 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 121.15 | 121.0517 | 121.1031 | 121.0581 | 121.188 | 121.1412 | 121.0249 | 0.09827 | 0.212 | 0.055296 | -0.097212 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | 0.007062 | 0.084205
1998.0312 | 121.6187 | -120.4514 | 0.93842 | 0.071489 | -0.013048 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.035248 | 0.079959 | 0.18911 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | -0.00775 | 120.5228 | 120.4383 | 120.4851 | 120.4355 | 120.5654 | 120.5232 | 120.4161 | 0.09827 | 0.20742 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.010561 | 0.054614 | 0.11802 | 0.007062 | 0.07047
1999.7188 | 121.6049 | -121.0556 | 0.54474 | 0.071489 | -0.017627 | 0.024629 | -0.020438 | 0.11409 | 0.071848 | -0.039826 | 0.079959 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.012328 | 121.1271 | 121.038 | 121.0802 | 121.0352 | 121.1697 | 121.1275 | 121.0158 | 0.09827 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.005983 | 0.050036 | 0.12718 | -0.002094 | 0.075049
2001.4531 | 121.6095 | -121.0602 | 0.50354 | 0.076067 | -0.022205 | 0.033786 | -0.020438 | 0.10951 | 0.071848 | -0.03067 | 0.079959 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 121.1362 | 121.038 | 121.094 | 121.0397 | 121.1697 | 121.132 | 121.0295 | 0.09827 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.050036 | 0.11802 | -0.002094 | 0.065892
2003.1406 | 121.701 | -120.7718 | 0.80566 | 0.080646 | -0.026784 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | -0.012328 | 120.8524 | 120.745 | 120.7964 | 120.7559 | 120.8813 | 120.8436 | 120.732 | 0.09827 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.005983 | 0.050036 | 0.11802 | 0.002484 | 0.07047
2004.9688 | 121.6965 | -121.138 | 0.39825 | 0.080646 | -0.022205 | 0.024629 | -0.025017 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.18911 | 0.032407 | -0.1201 | 0.034501 | 0.02322 | -0.033484 | -0.003172 | 121.2186 | 121.1158 | 121.1626 | 121.113 | 121.2475 | 121.2053 | 121.1028 | 0.09827 | 0.20742 | 0.050718 | -0.10179 | 0.052812 | 0.041531 | -0.015173 | 0.015139 | 0.045458 | 0.11344 | -0.002094 | 0.065891
2006.8125 | 121.637 | -121.1151 | 0.43945 | 0.06691 | -0.017627 | 0.029208 | -0.01586 | 0.11409 | 0.071848 | -0.035248 | 0.07538 | 0.18911 | 0.036985 | -0.12468 | 0.025345 | 0.02322 | -0.038063 | -0.012328 | 121.182 | 121.0975 | 121.1443 | 121.0993 | 121.2292 | 121.187 | 121.0799 | 0.093691 | 0.20742 | 0.055296 | -0.10637 | 0.043656 | 0.041531 | -0.019752 | 0.005983 | 0.050035 | 0.11344 | 0.01164 | 0.075048
2008.6719 | 121.6782 | -121.0693 | 0.48981 | 0.071489 | -0.022205 | 0.029208 | -0.01586 | 0.10951 | 0.062691 | -0.039826 | 0.070802 | 0.19369 | 0.027829 | -0.1201 | 0.025345 | 0.02322 | -0.042641 | 0.001406 | 121.1408 | 121.0471 | 121.0985 | 121.0535 | 121.1788 | 121.132 | 121.0295 | 0.089113 | 0.212 | 0.04614 | -0.10179 | 0.043656 | 0.041531 | -0.02433 | 0.019717 | 0.045457 | 0.11344 | 0.002484 | 0.07047
2010.7188 | 121.7331 | -121.1472 | 0.38452 | 0.080646 | -0.022205 | 0.024629 | -0.020438 | 0.10951 | 0.071848 | -0.035248 | 0.079959 | 0.18453 | 0.027829 | -0.1201 | 0.029923 | 0.014064 | -0.042641 | -0.003172 | 121.2278 | 121.125 | 121.1718 | 121.1267 | 121.2567 | 121.219 | 121.1119 | 0.09827 | 0.20284 | 0.04614 | -0.10179 | 0.048234 | 0.032375 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | -0.002094 | 0.07047
2012.6875 | 121.5912 | -121.2936 | 0.38452 | 0.071489 | -0.017627 | 0.038365 | -0.011281 | 0.10036 | 0.076426 | -0.039826 | 0.079959 | 0.19369 | 0.036985 | -0.1201 | 0.034501 | 0.027798 | -0.038063 | 0.001406 | 121.3651 | 121.276 | 121.332 | 121.2824 | 121.394 | 121.3701 | 121.2538 | 0.09827 | 0.212 | 0.055296 | -0.10179 | 0.052812 | 0.046109 | -0.019752 | 0.019717 | 0.045458 | 0.11802 | 0.002484 | 0.075048
2016.1875 | 121.5912 | -121.1746 | 0.48065 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.039826 | 0.07538 | 0.18453 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.012328 | 121.2507 | 121.1478 | 121.2038 | 121.1588 | 121.2841 | 121.251 | 121.1348 | 0.093691 | 0.20284 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.005983 | 0.045457 | 0.11802 | 0.002484 | 0.075048
2017.9844 | 121.0281 | -119.989 | 0.83771 | 0.085224 | -0.026784 | 0.033786 | -0.01586 | 0.11409 | 0.067269 | -0.035248 | 0.070802 | 0.19369 | 0.02325 | -0.1201 | 0.025345 | 0.02322 | -0.033484 | -0.003172 | 120.0742 | 119.9622 | 120.0228 | 119.9732 | 120.1031 | 120.0563 | 119.9538 | 0.089113 | 0.212 | 0.041561 | -0.10179 | 0.043656 | 0.041531 | -0.015173 | 0.015139 | 0.045457 | 0.10429 | -0.002095 | 0.056734
2019.6719 | 121.3715 | -120.7947 | 0.39825 | 0.076067 | -0.017627 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.03067 | 0.07538 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.027798 | -0.038063 | 0.001406 | 120.8707 | 120.7771 | 120.8193 | 120.7788 | 120.9042 | 120.8665 | 120.764 | 0.093691 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.046109 | -0.019752 | 0.019717 | 0.040879 | 0.11344 | -0.002094 | 0.07047
2021.3594 | 121.3715 | -120.8267 | 0.48065 | 0.071489 | -0.013048 | 0.033786 | -0.011281 | 0.11409 | 0.081005 | -0.03067 | 0.07538 | 0.19369 | 0.036985 | -0.11552 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 120.8982 | 120.8137 | 120.8605 | 120.8154 | 120.9408 | 120.9077 | 120.7961 | 0.093691 | 0.212 | 0.055296 | -0.097212 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11802 | 0.002484 | 0.079626
2023.0312 | 121.4584 | -121.0373 | 0.27466 | 0.06691 | -0.017627 | 0.029208 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.079959 | 0.18911 | 0.036985 | -0.12468 | 0.043657 | 0.018642 | -0.033484 | 0.001406 | 121.1042 | 121.0197 | 121.0665 | 121.0169 | 121.1422 | 121.1046 | 120.9975 | 0.09827 | 0.20742 | 0.055296 | -0.10637 | 0.061968 | 0.036953 | -0.015173 | 0.019717 | 0.036302 | 0.11344 | -0.006672 | 0.070469
2024.7188 | 121.5088 | -121.0144 | 0.3067 | 0.080646 | -0.017627 | 0.024629 | -0.025017 | 0.10951 | 0.076426 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | 0.001406 | 121.0951 | 120.9968 | 121.039 | 120.9894 | 121.1239 | 121.0908 | 120.9792 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.019717 | 0.050035 | 0.11344 | 0.007062 | 0.07047
2026.4531 | 120.9686 | -120.7855 | 0.17853 | 0.071489 | -0.022205 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.035248 | 0.084537 | 0.18911 | 0.032407 | -0.11094 | 0.034501 | 0.02322 | -0.042641 | -0.012328 | 120.857 | 120.7633 | 120.8147 | 120.7605 | 120.895 | 120.8528 | 120.7503 | 0.10285 | 0.20742 | 0.050718 | -0.092633 | 0.052812 | 0.041531 | -0.02433 | 0.005983 | 0.050036 | 0.12718 | -0.002094 | 0.075048
2028.1406 | 120.8725 | -120.7901 | 0.13733 | 0.076067 | -0.022205 | 0.033786 | -0.01586 | 0.11409 | 0.076426 | -0.039826 | 0.070802 | 0.17995 | 0.036985 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 120.8662 | 120.7679 | 120.8239 | 120.7742 | 120.9042 | 120.8665 | 120.7503 | 0.089113 | 0.19826 | 0.055296 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.040879 | 0.11344 | 0.007062 | 0.079626
2029.8125 | 120.7443 | -120.5887 | 0.11902 | 0.071489 | -0.017627 | 0.029208 | -0.020438 | 0.10951 | 0.067269 | -0.039826 | 0.084537 | 0.18911 | 0.027829 | -0.12468 | 0.034501 | 0.018642 | -0.042641 | -0.00775 | 120.6602 | 120.5711 | 120.6179 | 120.5682 | 120.6982 | 120.656 | 120.5489 | 0.10285 | 0.20742 | 0.04614 | -0.10637 | 0.052812 | 0.036953 | -0.02433 | 0.010561 | 0.050036 | 0.12718 | -0.006672 | 0.07047
2031.5312 | 121.0236 | -120.9595 | 0.13275 | 0.076067 | -0.026784 | 0.033786 | -0.020438 | 0.10951 | 0.076426 | -0.035248 | 0.079959 | 0.19369 | 0.036985 | -0.11552 | 0.029923 | 0.018642 | -0.04722 | -0.003172 | 121.0355 | 120.9327 | 120.9933 | 120.939 | 121.069 | 121.0359 | 120.9242 | 0.09827 | 0.212 | 0.055296 | -0.097212 | 0.048234 | 0.036953 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | 0.007062 | 0.084205
2033.2188 | 121.138 | -120.9869 | 0.11444 | 0.071489 | -0.026784 | 0.033786 | -0.020438 | 0.11867 | 0.067269 | -0.044405 | 0.079959 | 0.18453 | 0.02325 | -0.1201 | 0.029923 | 0.032376 | -0.038063 | -0.003172 | 121.0584 | 120.9602 | 121.0207 | 120.9665 | 121.1056 | 121.0542 | 120.9425 | 0.09827 | 0.20284 | 0.041561 | -0.10179 | 0.048234 | 0.050687 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | -0.006673 | 0.061313
2034.9219 | 121.2753 | -121.0052 | 0.11902 | 0.076067 | -0.022205 | 0.024629 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.07538 | 0.19369 | 0.036985 | -0.1201 | 0.034501 | 0.014064 | -0.033484 | -0.00775 | 121.0813 | 120.983 | 121.0299 | 120.9894 | 121.1148 | 121.0817 | 120.97 | 0.093691 | 0.212 | 0.055296 | -0.10179 | 0.052812 | 0.032375 | -0.015173 | 0.010561 | 0.040879 | 0.10886 | 0.002484 | 0.070469
2036.6094 | 121.2891 | -121.0464 | 0.11902 | 0.076067 | -0.022205 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.03067 | 0.084537 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.027798 | -0.033484 | 0.001406 | 121.1225 | 121.0242 | 121.0802 | 121.0306 | 121.1605 | 121.1183 | 121.0158 | 0.10285 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.046109 | -0.015173 | 0.019717 | 0.054614 | 0.11802 | -0.002094 | 0.061313
2038.2969 | 121.2021 | -121.1105 | 0.15564 | 0.076067 | -0.026784 | 0.033786 | -0.01586 | 0.10493 | 0.067269 | -0.039826 | 0.084537 | 0.18911 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.042641 | -0.012328 | 121.1866 | 121.0838 | 121.1443 | 121.0947 | 121.2155 | 121.1778 | 121.0707 | 0.10285 | 0.20742 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.02433 | 0.005983 | 0.050036 | 0.12718 | -0.006672 | 0.07047
2040 | 121.3394 | -121.0968 | 0.11902 | 0.071489 | -0.026784 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.039826 | 0.070802 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.04722 | 0.001406 | 121.1683 | 121.07 | 121.1306 | 121.0809 | 121.2109 | 121.1686 | 121.057 | 0.089113 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.028909 | 0.019717 | 0.040879 | 0.11802 | 0.002484 | 0.079627
2041.6875 | 121.2479 | -121.17 | 0.14191 | 0.080646 | -0.031363 | 0.033786 | -0.01586 | 0.11409 | 0.067269 | -0.039826 | 0.07538 | 0.18911 | 0.032407 | -0.11094 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 121.2507 | 121.1387 | 121.2038 | 121.1542 | 121.2841 | 121.2373 | 121.1302 | 0.093691 | 0.20742 | 0.050718 | -0.092633 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.002484 | 0.075048
2043.3594 | 121.3577 | -121.1105 | 0.10986 | 0.080646 | -0.026784 | 0.024629 | -0.020438 | 0.10951 | 0.067269 | -0.03067 | 0.07538 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.033484 | -0.00775 | 121.1912 | 121.0838 | 121.1352 | 121.0901 | 121.22 | 121.1778 | 121.0799 | 0.093691 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.015173 | 0.010561 | 0.045457 | 0.10886 | -0.002094 | 0.061313
2045.0469 | 121.3211 | -121.1746 | 0.13733 | 0.076067 | -0.022205 | 0.024629 | -0.011281 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.18911 | 0.036985 | -0.1201 | 0.025345 | 0.027798 | -0.042641 | -0.00775 | 121.2507 | 121.1524 | 121.1993 | 121.1633 | 121.2841 | 121.2419 | 121.1394 | 0.09827 | 0.20742 | 0.055296 | -0.10179 | 0.043656 | 0.046109 | -0.02433 | 0.010561 | 0.054614 | 0.1226 | 0.01164 | 0.079626
2046.75 | 121.3486 | -121.17 | 0.13275 | 0.076067 | -0.026784 | 0.033786 | -0.011281 | 0.11409 | 0.071848 | -0.026092 | 0.070802 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 121.2461 | 121.1433 | 121.2038 | 121.1588 | 121.2841 | 121.2419 | 121.144 | 0.089113 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | -0.002094 | 0.07047
2048.5 | 121.3074 | -121.1975 | 0.14191 | 0.080646 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.03067 | 0.079959 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.02322 | -0.038063 | -0.00775 | 121.2782 | 121.1707 | 121.2267 | 121.1771 | 121.307 | 121.2694 | 121.1668 | 0.09827 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.041531 | -0.019752 | 0.010561 | 0.045458 | 0.11802 | -0.002094 | 0.07047
2050.1875 | 121.4355 | -121.1975 | 0.10071 | 0.071489 | -0.022205 | 0.024629 | -0.01586 | 0.11409 | 0.076426 | -0.035248 | 0.070802 | 0.18453 | 0.027829 | -0.12926 | 0.029923 | 0.018642 | -0.042641 | 0.005985 | 121.269 | 121.1753 | 121.2221 | 121.1816 | 121.3116 | 121.2739 | 121.1623 | 0.089113 | 0.20284 | 0.04614 | -0.11095 | 0.048234 | 0.036953 | -0.02433 | 0.024296 | 0.040879 | 0.11344 | -0.002094 | 0.07047
2051.9062 | 121.4127 | -121.1792 | 0.10986 | 0.071489 | -0.031363 | 0.020051 | -0.01586 | 0.11409 | 0.071848 | -0.039826 | 0.070802 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 121.2507 | 121.1478 | 121.1992 | 121.1633 | 121.2933 | 121.251 | 121.1394 | 0.089113 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.036301 | 0.10887 | 0.002484 | 0.075048
2053.5938 | 121.431 | -121.2067 | 0.14191 | 0.076067 | -0.026784 | 0.029208 | -0.011281 | 0.10951 | 0.067269 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.014064 | -0.042641 | -0.00775 | 121.2827 | 121.1799 | 121.2359 | 121.1954 | 121.3162 | 121.2739 | 121.1668 | 0.09827 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.032375 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.002484 | 0.075048
2055.2812 | 121.3348 | -121.2479 | 0.15106 | 0.076067 | -0.017627 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.079959 | 0.18453 | 0.032407 | -0.1201 | 0.029923 | 0.027798 | -0.042641 | -0.012328 | 121.3239 | 121.2302 | 121.2771 | 121.232 | 121.3574 | 121.3243 | 121.2126 | 0.09827 | 0.20284 | 0.050718 | -0.10179 | 0.048234 | 0.046109 | -0.02433 | 0.005983 | 0.050036 | 0.1226 | 0.002484 | 0.075048
2056.9844 | 121.4722 | -121.1929 | 0.10529 | 0.076067 | -0.022205 | 0.029208 | -0.01586 | 0.10493 | 0.076426 | -0.039826 | 0.070802 | 0.19827 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | 0.001406 | 121.269 | 121.1707 | 121.2221 | 121.1771 | 121.2979 | 121.2694 | 121.1531 | 0.089113 | 0.21658 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.019717 | 0.040879 | 0.11802 | -0.002094 | 0.075049
2058.6719 | 121.3577 | -121.2845 | 0.15564 | 0.071489 | -0.026784 | 0.029208 | -0.020438 | 0.11409 | 0.067269 | -0.039826 | 0.070802 | 0.19369 | 0.027829 | -0.1201 | 0.020767 | 0.014064 | -0.042641 | 0.001406 | 121.356 | 121.2577 | 121.3137 | 121.264 | 121.3986 | 121.3518 | 121.2447 | 0.089113 | 0.212 | 0.04614 | -0.10179 | 0.039078 | 0.032375 | -0.02433 | 0.019717 | 0.050035 | 0.11344 | 0.007062 | 0.07047
2060.375 | 121.5042 | -121.2341 | 0.10986 | 0.076067 | -0.022205 | 0.029208 | -0.011281 | 0.10951 | 0.081005 | -0.035248 | 0.079959 | 0.18911 | 0.036985 | -0.12468 | 0.025345 | 0.027798 | -0.033484 | -0.00775 | 121.3102 | 121.2119 | 121.2633 | 121.2229 | 121.3436 | 121.3151 | 121.1989 | 0.09827 | 0.20742 | 0.055296 | -0.10637 | 0.043656 | 0.046109 | -0.015173 | 0.010561 | 0.054614 | 0.11344 | 0.01164 | 0.070469
2062.0781 | 121.5134 | -121.2753 | 0.10986 | 0.076067 | -0.026784 | 0.038365 | -0.01586 | 0.11409 | 0.067269 | -0.039826 | 0.079959 | 0.18453 | 0.032407 | -0.12468 | 0.039079 | 0.018642 | -0.038063 | -0.00775 | 121.3514 | 121.2485 | 121.3137 | 121.2595 | 121.3894 | 121.3426 | 121.2355 | 0.09827 | 0.20284 | 0.050718 | -0.10637 | 0.05739 | 0.036953 | -0.019752 | 0.010561 | 0.04088 | 0.11802 | -0.006672 | 0.07047
2063.7812 | 121.5088 | -121.2799 | 0.10529 | 0.071489 | -0.022205 | 0.024629 | -0.011281 | 0.10951 | 0.071848 | -0.039826 | 0.084537 | 0.19369 | 0.041563 | -0.12468 | 0.029923 | 0.032376 | -0.042641 | -0.003172 | 121.3514 | 121.2577 | 121.3045 | 121.2686 | 121.3894 | 121.3518 | 121.2401 | 0.10285 | 0.212 | 0.059874 | -0.10637 | 0.048234 | 0.050687 | -0.02433 | 0.015139 | 0.054614 | 0.12718 | 0.01164 | 0.084204
2065.5156 | 121.4813 | -121.2891 | 0.12817 | 0.076067 | -0.031363 | 0.024629 | -0.020438 | 0.10951 | 0.071848 | -0.035248 | 0.079959 | 0.18911 | 0.027829 | -0.1201 | 0.034501 | 0.02322 | -0.04722 | -0.00775 | 121.3651 | 121.2577 | 121.3137 | 121.2686 | 121.3986 | 121.3609 | 121.2538 | 0.09827 | 0.20742 | 0.04614 | -0.10179 | 0.052812 | 0.041531 | -0.028909 | 0.010561 | 0.045458 | 0.12718 | -0.006672 | 0.075049
2067.2031 | 121.3943 | -121.2891 | 0.13733 | 0.071489 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.044405 | 0.079959 | 0.18911 | 0.02325 | -0.1201 | 0.034501 | 0.014064 | -0.04722 | -0.003172 | 121.3606 | 121.2623 | 121.3183 | 121.2732 | 121.3986 | 121.3655 | 121.2447 | 0.09827 | 0.20742 | 0.041561 | -0.10179 | 0.052812 | 0.032375 | -0.028909 | 0.015139 | 0.045458 | 0.12718 | -0.011251 | 0.07047
2068.9062 | 121.4493 | -121.3028 | 0.14191 | 0.06691 | -0.035942 | 0.029208 | -0.01586 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18453 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 121.3697 | 121.2669 | 121.332 | 121.2869 | 121.4123 | 121.3746 | 121.263 | 0.09827 | 0.20284 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | 0.002484 | 0.07047
2070.6094 | 121.4172 | -121.3165 | 0.16022 | 0.06691 | -0.031363 | 0.033786 | -0.01586 | 0.10036 | 0.081005 | -0.03067 | 0.07538 | 0.19369 | 0.027829 | -0.12468 | 0.034501 | 0.02322 | -0.033484 | -0.003172 | 121.3834 | 121.2852 | 121.3503 | 121.3007 | 121.4169 | 121.3975 | 121.2859 | 0.093691 | 0.212 | 0.04614 | -0.10637 | 0.052812 | 0.041531 | -0.015173 | 0.015139 | 0.040879 | 0.10886 | -0.006672 | 0.061313
2072.2969 | 121.463 | -121.3074 | 0.12817 | 0.076067 | -0.031363 | 0.033786 | -0.011281 | 0.10951 | 0.067269 | -0.035248 | 0.07538 | 0.19369 | 0.027829 | -0.11094 | 0.025345 | 0.027798 | -0.04722 | -0.003172 | 121.3834 | 121.276 | 121.3412 | 121.2961 | 121.4169 | 121.3746 | 121.2721 | 0.093691 | 0.212 | 0.04614 | -0.092633 | 0.043656 | 0.046109 | -0.028909 | 0.015139 | 0.050035 | 0.1226 | 0.002484 | 0.075049
2074 | 121.4813 | -121.3303 | 0.14191 | 0.080646 | -0.031363 | 0.024629 | -0.011281 | 0.11409 | 0.071848 | -0.039826 | 0.079959 | 0.18453 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.012328 | 121.4109 | 121.2989 | 121.3549 | 121.319 | 121.4444 | 121.4021 | 121.2904 | 0.09827 | 0.20284 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.005983 | 0.050036 | 0.1226 | -0.002094 | 0.07047
2075.6875 | 121.5271 | -121.3028 | 0.10986 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.11409 | 0.062691 | -0.03067 | 0.07538 | 0.19369 | 0.027829 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.3789 | 121.276 | 121.332 | 121.2869 | 121.4169 | 121.3655 | 121.2721 | 0.093691 | 0.212 | 0.04614 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | -0.002094 | 0.065892
2077.375 | 121.4401 | -121.3577 | 0.13733 | 0.071489 | -0.031363 | 0.033786 | -0.011281 | 0.11409 | 0.076426 | -0.044405 | 0.079959 | 0.17995 | 0.036985 | -0.11552 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 121.4292 | 121.3264 | 121.3915 | 121.3464 | 121.4718 | 121.4342 | 121.3133 | 0.09827 | 0.19826 | 0.055296 | -0.097212 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.050036 | 0.1226 | 0.007062 | 0.079626
2079.0625 | 121.5408 | -121.3348 | 0.10986 | 0.076067 | -0.022205 | 0.024629 | -0.01586 | 0.10493 | 0.071848 | -0.039826 | 0.07538 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 121.4109 | 121.3126 | 121.3595 | 121.319 | 121.4398 | 121.4067 | 121.295 | 0.093691 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.040879 | 0.11344 | 0.002484 | 0.075048
2080.7656 | 121.4539 | -121.3531 | 0.15106 | 0.076067 | -0.026784 | 0.024629 | -0.01586 | 0.11409 | 0.071848 | -0.03067 | 0.070802 | 0.18453 | 0.032407 | -0.11094 | 0.025345 | 0.018642 | -0.042641 | -0.003172 | 121.4292 | 121.3264 | 121.3778 | 121.3373 | 121.4672 | 121.425 | 121.3225 | 0.089113 | 0.20284 | 0.050718 | -0.092633 | 0.043656 | 0.036953 | -0.02433 | 0.015139 | 0.045457 | 0.11344 | 0.007062 | 0.075048
2082.5156 | 121.4493 | -121.3852 | 0.14648 | 0.076067 | -0.026784 | 0.033786 | -0.011281 | 0.10951 | 0.071848 | -0.026092 | 0.079959 | 0.18911 | 0.027829 | -0.12468 | 0.034501 | 0.014064 | -0.04722 | -0.00775 | 121.4613 | 121.3584 | 121.419 | 121.3739 | 121.4947 | 121.457 | 121.3591 | 0.09827 | 0.20742 | 0.04614 | -0.10637 | 0.052812 | 0.032375 | -0.028909 | 0.010561 | 0.045458 | 0.12718 | -0.006672 | 0.075049
2084.2031 | 121.6232 | -121.3348 | 0.11444 | 0.076067 | -0.035942 | 0.033786 | -0.01586 | 0.11409 | 0.067269 | -0.039826 | 0.079959 | 0.18453 | 0.036985 | -0.11552 | 0.029923 | 0.014064 | -0.033484 | -0.003172 | 121.4109 | 121.2989 | 121.3686 | 121.319 | 121.4489 | 121.4021 | 121.295 | 0.09827 | 0.20284 | 0.055296 | -0.097212 | 0.048234 | 0.032375 | -0.015173 | 0.015139 | 0.050036 | 0.11344 | 0.007062 | 0.070469
2085.9062 | 121.6049 | -121.3348 | 0.1236 | 0.071489 | -0.022205 | 0.029208 | -0.01586 | 0.10493 | 0.076426 | -0.039826 | 0.079959 | 0.19369 | 0.032407 | -0.12468 | 0.034501 | 0.027798 | -0.038063 | 0.001406 | 121.4063 | 121.3126 | 121.364 | 121.319 | 121.4398 | 121.4113 | 121.295 | 0.09827 | 0.212 | 0.050718 | -0.10637 | 0.052812 | 0.046109 | -0.019752 | 0.019717 | 0.045458 | 0.11802 | -0.002094 | 0.07047
2087.5938 | 121.5454 | -121.3715 | 0.12817 | 0.071489 | -0.026784 | 0.038365 | -0.006703 | 0.11409 | 0.067269 | -0.044405 | 0.079959 | 0.19369 | 0.027829 | -0.11094 | 0.025345 | 0.02322 | -0.042641 | -0.00775 | 121.4429 | 121.3447 | 121.4098 | 121.3648 | 121.4856 | 121.4387 | 121.3271 | 0.09827 | 0.212 | 0.04614 | -0.092633 | 0.043656 | 0.041531 | -0.02433 | 0.010561 | 0.054614 | 0.1226 | 0.002484 | 0.07047
2089.2812 | 121.4859 | -121.3806 | 0.15564 | 0.080646 | -0.022205 | 0.033786 | -0.011281 | 0.10951 | 0.071848 | -0.035248 | 0.070802 | 0.18911 | 0.036985 | -0.12468 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 121.4613 | 121.3584 | 121.4144 | 121.3693 | 121.4901 | 121.4525 | 121.3454 | 0.089113 | 0.20742 | 0.055296 | -0.10637 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.036301 | 0.11344 | 0.002484 | 0.079626
2090.9688 | 121.4813 | -121.4035 | 0.15564 | 0.071489 | -0.031363 | 0.029208 | -0.006703 | 0.10951 | 0.071848 | -0.035248 | 0.07538 | 0.18453 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.038063 | 0.001406 | 121.475 | 121.3721 | 121.4327 | 121.3968 | 121.513 | 121.4754 | 121.3683 | 0.093691 | 0.20284 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.019752 | 0.019717 | 0.040879 | 0.11344 | -0.006672 | 0.065892
2092.6562 | 121.6278 | -121.3577 | 0.10071 | 0.071489 | -0.031363 | 0.024629 | -0.01586 | 0.10493 | 0.067269 | -0.044405 | 0.07538 | 0.18453 | 0.02325 | -0.11094 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.4292 | 121.3264 | 121.3824 | 121.3419 | 121.4627 | 121.425 | 121.3133 | 0.093691 | 0.20284 | 0.041561 | -0.092633 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | -0.006673 | 0.061313
2094.3438 | 121.5088 | -121.4081 | 0.12817 | 0.06691 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.062691 | -0.039826 | 0.084537 | 0.18453 | 0.02325 | -0.11094 | 0.034501 | 0.027798 | -0.042641 | -0.00775 | 121.475 | 121.3813 | 121.4373 | 121.3876 | 121.5176 | 121.4708 | 121.3683 | 0.10285 | 0.20284 | 0.041561 | -0.092633 | 0.052812 | 0.046109 | -0.02433 | 0.010561 | 0.050036 | 0.12718 | -0.011251 | 0.065891
2096.0312 | 121.5088 | -121.4264 | 0.14191 | 0.071489 | -0.022205 | 0.033786 | -0.01586 | 0.10951 | 0.067269 | -0.03067 | 0.079959 | 0.18453 | 0.032407 | -0.1201 | 0.025345 | 0.02322 | -0.051798 | -0.003172 | 121.4979 | 121.4042 | 121.4602 | 121.4105 | 121.5359 | 121.4937 | 121.3957 | 0.09827 | 0.20284 | 0.050718 | -0.10179 | 0.043656 | 0.041531 | -0.033487 | 0.015139 | 0.054614 | 0.13176 | 0.007062 | 0.084205
2097.7188 | 121.6324 | -121.3989 | 0.11444 | 0.071489 | -0.026784 | 0.029208 | -0.025017 | 0.10951 | 0.071848 | -0.035248 | 0.070802 | 0.19369 | 0.036985 | -0.11094 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 121.4704 | 121.3721 | 121.4281 | 121.3739 | 121.5084 | 121.4708 | 121.3637 | 0.089113 | 0.212 | 0.055296 | -0.092633 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | 0.007062 | 0.079626
2099.4531 | 121.5637 | -121.4035 | 0.12817 | 0.076067 | -0.031363 | 0.020051 | -0.011281 | 0.11409 | 0.076426 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.02322 | -0.04722 | -0.00775 | 121.4796 | 121.3721 | 121.4236 | 121.3922 | 121.5176 | 121.4799 | 121.3637 | 0.09827 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.041531 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.002484 | 0.079627
2101.1406 | 121.6553 | -121.3989 | 0.11902 | 0.071489 | -0.026784 | 0.033786 | -0.006703 | 0.10493 | 0.067269 | -0.039826 | 0.07538 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.027798 | -0.04722 | 0.001406 | 121.4704 | 121.3721 | 121.4327 | 121.3922 | 121.5039 | 121.4662 | 121.3591 | 0.093691 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.046109 | -0.028909 | 0.019717 | 0.040879 | 0.1226 | 0.002484 | 0.084205
2102.8281 | 121.6461 | -121.3806 | 0.11902 | 0.071489 | -0.031363 | 0.029208 | -0.020438 | 0.10493 | 0.076426 | -0.039826 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | -0.00775 | 121.4521 | 121.3493 | 121.4098 | 121.3602 | 121.4855 | 121.457 | 121.3408 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.010561 | 0.045457 | 0.11344 | 0.002484 | 0.07047
2104.5469 | 121.5591 | -121.4264 | 0.14648 | 0.071489 | -0.026784 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.03067 | 0.07538 | 0.19369 | 0.032407 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 121.4979 | 121.3996 | 121.4602 | 121.4105 | 121.5405 | 121.4982 | 121.3957 | 0.093691 | 0.212 | 0.050718 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11802 | -0.002094 | 0.075048
2106.2344 | 121.6644 | -121.376 | 0.11444 | 0.062332 | -0.031363 | 0.020051 | -0.01586 | 0.10951 | 0.062691 | -0.03067 | 0.07538 | 0.19369 | 0.036985 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 121.4384 | 121.3447 | 121.3961 | 121.3602 | 121.4855 | 121.4387 | 121.3454 | 0.093691 | 0.212 | 0.055296 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.007062 | 0.079626
2107.9375 | 121.6141 | -121.4081 | 0.11444 | 0.071489 | -0.026784 | 0.024629 | -0.011281 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.027798 | -0.04722 | -0.00775 | 121.4796 | 121.3813 | 121.4327 | 121.3968 | 121.5176 | 121.4799 | 121.3683 | 0.09827 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.046109 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.002484 | 0.079627
2109.6562 | 121.5454 | -121.4539 | 0.12817 | 0.071489 | -0.026784 | 0.038365 | -0.01586 | 0.10951 | 0.067269 | -0.03067 | 0.07538 | 0.19369 | 0.036985 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | 0.001406 | 121.5253 | 121.4271 | 121.4922 | 121.438 | 121.5634 | 121.5211 | 121.4232 | 0.093691 | 0.212 | 0.055296 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.019717 | 0.045457 | 0.11344 | 0.007062 | 0.075048
2111.375 | 121.5958 | -121.4401 | 0.16479 | 0.076067 | -0.026784 | 0.029208 | -0.011281 | 0.11409 | 0.085583 | -0.03067 | 0.084537 | 0.18911 | 0.036985 | -0.11552 | 0.034501 | 0.014064 | -0.042641 | -0.003172 | 121.5162 | 121.4133 | 121.4693 | 121.4288 | 121.5542 | 121.5257 | 121.4095 | 0.10285 | 0.20742 | 0.055296 | -0.097212 | 0.052812 | 0.032375 | -0.02433 | 0.015139 | 0.050036 | 0.12718 | 0.002484 | 0.079626
2113.0938 | 121.5958 | -121.4539 | 0.14191 | 0.071489 | -0.031363 | 0.024629 | -0.01586 | 0.11409 | 0.076426 | -0.03067 | 0.07538 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.014064 | -0.04722 | -0.012328 | 121.5253 | 121.4225 | 121.4785 | 121.438 | 121.5679 | 121.5303 | 121.4232 | 0.093691 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.032375 | -0.028909 | 0.005983 | 0.045457 | 0.1226 | 0.007062 | 0.084205
2114.7969 | 121.5454 | -121.4722 | 0.15106 | 0.071489 | -0.026784 | 0.038365 | -0.025017 | 0.11409 | 0.076426 | -0.026092 | 0.079959 | 0.17537 | 0.032407 | -0.1201 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 121.5437 | 121.4454 | 121.5105 | 121.4472 | 121.5863 | 121.5486 | 121.4461 | 0.09827 | 0.19368 | 0.050718 | -0.10179 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | -0.002094 | 0.07047
2116.5312 | 121.5912 | -121.4539 | 0.13733 | 0.071489 | -0.035942 | 0.033786 | -0.01586 | 0.10493 | 0.071848 | -0.03067 | 0.07538 | 0.18453 | 0.036985 | -0.1201 | 0.034501 | 0.018642 | -0.04722 | -0.00775 | 121.5253 | 121.4179 | 121.4876 | 121.438 | 121.5588 | 121.5257 | 121.4232 | 0.093691 | 0.20284 | 0.055296 | -0.10179 | 0.052812 | 0.036953 | -0.028909 | 0.010561 | 0.040879 | 0.1226 | 0.002484 | 0.084205
2118.2188 | 121.6461 | -121.431 | 0.11444 | 0.06691 | -0.031363 | 0.024629 | -0.006703 | 0.11409 | 0.071848 | -0.039826 | 0.07538 | 0.18911 | 0.036985 | -0.12468 | 0.039079 | 0.027798 | -0.033484 | -0.003172 | 121.4979 | 121.3996 | 121.4556 | 121.4243 | 121.5451 | 121.5028 | 121.3911 | 0.093691 | 0.20742 | 0.055296 | -0.10637 | 0.05739 | 0.046109 | -0.015173 | 0.015139 | 0.036301 | 0.10886 | -0.002094 | 0.070469
2119.9219 | 121.5683 | -121.4813 | 0.14648 | 0.071489 | -0.026784 | 0.033786 | -0.006703 | 0.10493 | 0.076426 | -0.03067 | 0.07538 | 0.18453 | 0.027829 | -0.11552 | 0.039079 | 0.014064 | -0.038063 | -0.00775 | 121.5528 | 121.4545 | 121.5151 | 121.4746 | 121.5863 | 121.5577 | 121.4507 | 0.093691 | 0.20284 | 0.04614 | -0.097212 | 0.05739 | 0.032375 | -0.019752 | 0.010561 | 0.036301 | 0.11344 | -0.01125 | 0.065892
2121.6094 | 121.6782 | -121.463 | 0.10529 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.03067 | 0.07538 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.014064 | -0.042641 | -0.003172 | 121.5391 | 121.4362 | 121.4922 | 121.4472 | 121.5725 | 121.5303 | 121.4323 | 0.093691 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.032375 | -0.02433 | 0.015139 | 0.045457 | 0.11802 | 0.002484 | 0.075048
2123.2812 | 121.582 | -121.463 | 0.16479 | 0.076067 | -0.026784 | 0.029208 | -0.020438 | 0.10493 | 0.071848 | -0.03067 | 0.070802 | 0.18911 | 0.032407 | -0.1201 | 0.039079 | 0.02322 | -0.038063 | -0.00775 | 121.5391 | 121.4362 | 121.4922 | 121.4426 | 121.5679 | 121.5349 | 121.4323 | 0.089113 | 0.20742 | 0.050718 | -0.10179 | 0.05739 | 0.041531 | -0.019752 | 0.010561 | 0.031723 | 0.10887 | -0.006672 | 0.07047
2124.9844 | 121.7056 | -121.431 | 0.11902 | 0.076067 | -0.022205 | 0.033786 | -0.020438 | 0.10951 | 0.067269 | -0.035248 | 0.079959 | 0.18911 | 0.032407 | -0.11094 | 0.034501 | 0.02322 | -0.04722 | -0.003172 | 121.507 | 121.4088 | 121.4648 | 121.4105 | 121.5405 | 121.4982 | 121.3957 | 0.09827 | 0.20742 | 0.050718 | -0.092633 | 0.052812 | 0.041531 | -0.028909 | 0.015139 | 0.045458 | 0.12718 | -0.002094 | 0.079627
2126.7188 | 121.6507 | -121.4722 | 0.12817 | 0.071489 | -0.026784 | 0.024629 | -0.020438 | 0.10493 | 0.071848 | -0.03067 | 0.079959 | 0.19369 | 0.036985 | -0.1201 | 0.029923 | 0.014064 | -0.042641 | -0.003172 | 121.5437 | 121.4454 | 121.4968 | 121.4517 | 121.5771 | 121.544 | 121.4415 | 0.09827 | 0.212 | 0.055296 | -0.10179 | 0.048234 | 0.032375 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | 0.007062 | 0.079626
2128.4688 | 121.5591 | -121.4767 | 0.14648 | 0.080646 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.039826 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | -0.003172 | 121.5574 | 121.45 | 121.506 | 121.4609 | 121.5863 | 121.5532 | 121.4369 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.015139 | 0.050035 | 0.11344 | 0.007062 | 0.07047
2130.1719 | 121.6095 | -121.4996 | 0.13275 | 0.071489 | -0.022205 | 0.029208 | -0.020438 | 0.10951 | 0.076426 | -0.035248 | 0.084537 | 0.18911 | 0.027829 | -0.1201 | 0.025345 | 0.02322 | -0.04722 | -0.003172 | 121.5711 | 121.4774 | 121.5288 | 121.4792 | 121.6091 | 121.5761 | 121.4644 | 0.10285 | 0.20742 | 0.04614 | -0.10179 | 0.043656 | 0.041531 | -0.028909 | 0.015139 | 0.059192 | 0.13176 | 0.002484 | 0.075049
2131.875 | 121.7194 | -121.4584 | 0.10986 | 0.071489 | -0.026784 | 0.033786 | -0.020438 | 0.10951 | 0.071848 | -0.03067 | 0.070802 | 0.18453 | 0.027829 | -0.12468 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.5299 | 121.4317 | 121.4922 | 121.438 | 121.5679 | 121.5303 | 121.4278 | 0.089113 | 0.20284 | 0.04614 | -0.10637 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | -0.002094 | 0.07047
2133.5938 | 121.7331 | -121.4493 | 0.11444 | 0.071489 | -0.031363 | 0.029208 | -0.01586 | 0.10493 | 0.071848 | -0.035248 | 0.070802 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 121.5208 | 121.4179 | 121.4785 | 121.4334 | 121.5542 | 121.5211 | 121.414 | 0.089113 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.040879 | 0.10887 | 0.002484 | 0.07047
2135.3125 | 121.6827 | -121.4722 | 0.10986 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.11867 | 0.076426 | -0.035248 | 0.070802 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 121.5482 | 121.4454 | 121.5014 | 121.4563 | 121.5908 | 121.5486 | 121.4369 | 0.089113 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.040879 | 0.10887 | 0.002484 | 0.07047
2137 | 121.6415 | -121.4951 | 0.1236 | 0.076067 | -0.026784 | 0.029208 | -0.020438 | 0.10493 | 0.067269 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.00775 | 121.5711 | 121.4683 | 121.5243 | 121.4746 | 121.6 | 121.5623 | 121.4598 | 0.093691 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.010561 | 0.045457 | 0.11344 | -0.002094 | 0.065892
2138.6875 | 121.7056 | -121.4493 | 0.11902 | 0.071489 | -0.026784 | 0.029208 | -0.011281 | 0.11409 | 0.076426 | -0.03067 | 0.079959 | 0.18453 | 0.032407 | -0.1201 | 0.039079 | 0.018642 | -0.038063 | -0.00775 | 121.5208 | 121.4225 | 121.4785 | 121.438 | 121.5634 | 121.5257 | 121.4186 | 0.09827 | 0.20284 | 0.050718 | -0.10179 | 0.05739 | 0.036953 | -0.019752 | 0.010561 | 0.04088 | 0.11802 | -0.006672 | 0.07047
2140.375 | 121.7422 | -121.4447 | 0.10986 | 0.071489 | -0.026784 | 0.029208 | -0.006703 | 0.10951 | 0.071848 | -0.03067 | 0.07538 | 0.18911 | 0.032407 | -0.12468 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 121.5162 | 121.4179 | 121.4739 | 121.438 | 121.5542 | 121.5166 | 121.414 | 0.093691 | 0.20742 | 0.050718 | -0.10637 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.045457 | 0.11802 | 0.002484 | 0.075048
2142.0625 | 121.6278 | -121.5088 | 0.14191 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.11867 | 0.076426 | -0.035248 | 0.070802 | 0.18453 | 0.036985 | -0.11552 | 0.034501 | 0.02322 | -0.038063 | -0.00775 | 121.5849 | 121.482 | 121.538 | 121.4929 | 121.6275 | 121.5852 | 121.4735 | 0.089113 | 0.20284 | 0.055296 | -0.097212 | 0.052812 | 0.041531 | -0.019752 | 0.010561 | 0.036301 | 0.10887 | 0.002484 | 0.075048
2143.75 | 121.6873 | -121.5042 | 0.13733 | 0.071489 | -0.031363 | 0.029208 | -0.01586 | 0.10493 | 0.076426 | -0.039826 | 0.07538 | 0.18453 | 0.032407 | -0.11552 | 0.025345 | 0.027798 | -0.038063 | -0.012328 | 121.5757 | 121.4728 | 121.5334 | 121.4884 | 121.6091 | 121.5806 | 121.4644 | 0.093691 | 0.20284 | 0.050718 | -0.097212 | 0.043656 | 0.046109 | -0.019752 | 0.005983 | 0.050035 | 0.11344 | 0.007062 | 0.07047
2145.4844 | 121.7056 | -121.4767 | 0.14648 | 0.06691 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.079959 | 0.18453 | 0.032407 | -0.11552 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 121.5437 | 121.45 | 121.506 | 121.4609 | 121.5863 | 121.5532 | 121.4415 | 0.09827 | 0.20284 | 0.050718 | -0.097212 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | 0.002484 | 0.075048
2147.1719 | 121.7148 | -121.4996 | 0.11902 | 0.071489 | -0.031363 | 0.029208 | -0.01586 | 0.10493 | 0.076426 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.027798 | -0.033484 | 0.001406 | 121.5711 | 121.4683 | 121.5288 | 121.4838 | 121.6046 | 121.5761 | 121.4644 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.046109 | -0.015173 | 0.019717 | 0.045457 | 0.10886 | 0.002484 | 0.065891
2148.8594 | 121.6507 | -121.5271 | 0.1236 | 0.071489 | -0.026784 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.03067 | 0.07538 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.042641 | -0.012328 | 121.5986 | 121.5003 | 121.5609 | 121.5112 | 121.6412 | 121.5989 | 121.4964 | 0.093691 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.02433 | 0.005983 | 0.045457 | 0.11802 | 0.002484 | 0.075048
2150.5625 | 121.6827 | -121.5088 | 0.15106 | 0.071489 | -0.026784 | 0.029208 | -0.01586 | 0.10493 | 0.067269 | -0.035248 | 0.070802 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 121.5803 | 121.482 | 121.538 | 121.4929 | 121.6137 | 121.5761 | 121.4735 | 0.089113 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.040879 | 0.10887 | 0.007062 | 0.075048
2152.2344 | 121.7743 | -121.463 | 0.11902 | 0.071489 | -0.031363 | 0.029208 | -0.020438 | 0.10493 | 0.067269 | -0.039826 | 0.079959 | 0.17995 | 0.032407 | -0.12468 | 0.034501 | 0.02322 | -0.042641 | 0.005985 | 121.5345 | 121.4317 | 121.4922 | 121.4426 | 121.5679 | 121.5303 | 121.4232 | 0.09827 | 0.19826 | 0.050718 | -0.10637 | 0.052812 | 0.041531 | -0.02433 | 0.024296 | 0.045458 | 0.1226 | -0.002094 | 0.075048
2153.9219 | 121.7468 | -121.4859 | 0.10529 | 0.071489 | -0.031363 | 0.024629 | -0.020438 | 0.10951 | 0.071848 | -0.039826 | 0.079959 | 0.19369 | 0.032407 | -0.12468 | 0.029923 | 0.027798 | -0.038063 | 0.005985 | 121.5574 | 121.4545 | 121.5105 | 121.4655 | 121.5954 | 121.5577 | 121.4461 | 0.09827 | 0.212 | 0.050718 | -0.10637 | 0.048234 | 0.046109 | -0.019752 | 0.024296 | 0.050036 | 0.11802 | 0.002484 | 0.07047
2155.6094 | 121.7331 | -121.4722 | 0.13275 | 0.06691 | -0.031363 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.035248 | 0.07538 | 0.18453 | 0.02325 | -0.11552 | 0.025345 | 0.018642 | -0.038063 | -0.003172 | 121.5391 | 121.4408 | 121.5014 | 121.4517 | 121.5863 | 121.544 | 121.4369 | 0.093691 | 0.20284 | 0.041561 | -0.097212 | 0.043656 | 0.036953 | -0.019752 | 0.015139 | 0.050035 | 0.11344 | -0.002095 | 0.061313
2157.2969 | 121.6827 | -121.5179 | 0.15564 | 0.080646 | -0.031363 | 0.029208 | -0.025017 | 0.11867 | 0.076426 | -0.035248 | 0.079959 | 0.18911 | 0.036985 | -0.11552 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 121.5986 | 121.4866 | 121.5472 | 121.4929 | 121.6366 | 121.5944 | 121.4827 | 0.09827 | 0.20742 | 0.055296 | -0.097212 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | 0.002484 | 0.079626
2158.9844 | 121.637 | -121.4859 | 0.16937 | 0.06691 | -0.026784 | 0.024629 | -0.01586 | 0.11409 | 0.076426 | -0.03067 | 0.07538 | 0.18911 | 0.036985 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | -0.00775 | 121.5528 | 121.4591 | 121.5105 | 121.47 | 121.6 | 121.5623 | 121.4552 | 0.093691 | 0.20742 | 0.055296 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.010561 | 0.050035 | 0.11344 | 0.01164 | 0.075048
2160.6719 | 121.6827 | -121.5225 | 0.17853 | 0.080646 | -0.022205 | 0.024629 | -0.011281 | 0.11409 | 0.076426 | -0.035248 | 0.070802 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.014064 | -0.042641 | -0.003172 | 121.6032 | 121.5003 | 121.5472 | 121.5112 | 121.6366 | 121.5989 | 121.4873 | 0.089113 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.032375 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | 0.002484 | 0.075048
2162.3906 | 121.6736 | -121.5042 | 0.16022 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.11409 | 0.071848 | -0.035248 | 0.070802 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.027798 | -0.04722 | -0.003172 | 121.5803 | 121.4774 | 121.5334 | 121.4884 | 121.6183 | 121.5761 | 121.469 | 0.089113 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.046109 | -0.028909 | 0.015139 | 0.040879 | 0.11802 | 0.002484 | 0.079627
2164.0938 | 121.7285 | -121.4767 | 0.13733 | 0.071489 | -0.035942 | 0.024629 | -0.011281 | 0.10493 | 0.071848 | -0.035248 | 0.070802 | 0.18911 | 0.027829 | -0.12468 | 0.034501 | 0.02322 | -0.038063 | 0.001406 | 121.5482 | 121.4408 | 121.5014 | 121.4655 | 121.5817 | 121.5486 | 121.4415 | 0.089113 | 0.20742 | 0.04614 | -0.10637 | 0.052812 | 0.041531 | -0.019752 | 0.019717 | 0.036301 | 0.10887 | -0.006672 | 0.065892
2165.7812 | 121.6644 | -121.5088 | 0.16022 | 0.071489 | -0.031363 | 0.020051 | -0.011281 | 0.11409 | 0.076426 | -0.03067 | 0.07538 | 0.18911 | 0.02325 | -0.11552 | 0.029923 | 0.032376 | -0.042641 | -0.012328 | 121.5803 | 121.4774 | 121.5288 | 121.4975 | 121.6229 | 121.5852 | 121.4781 | 0.093691 | 0.20742 | 0.041561 | -0.097212 | 0.048234 | 0.050687 | -0.02433 | 0.005983 | 0.045457 | 0.11802 | -0.006673 | 0.065891
2167.4844 | 121.7972 | -121.4767 | 0.14648 | 0.080646 | -0.026784 | 0.024629 | -0.01586 | 0.11409 | 0.071848 | -0.035248 | 0.07538 | 0.17995 | 0.036985 | -0.12468 | 0.029923 | 0.014064 | -0.038063 | 0.001406 | 121.5574 | 121.45 | 121.5014 | 121.4609 | 121.5908 | 121.5486 | 121.4415 | 0.093691 | 0.19826 | 0.055296 | -0.10637 | 0.048234 | 0.032375 | -0.019752 | 0.019717 | 0.045457 | 0.11344 | 0.007062 | 0.075048
2169.1875 | 121.7468 | -121.4081 | 0.10986 | 0.06691 | -0.031363 | 0.024629 | -0.01586 | 0.10951 | 0.062691 | -0.039826 | 0.070802 | 0.18911 | 0.032407 | -0.11094 | 0.029923 | 0.018642 | -0.042641 | -0.012328 | 121.475 | 121.3767 | 121.4327 | 121.3922 | 121.5176 | 121.4708 | 121.3683 | 0.089113 | 0.20742 | 0.050718 | -0.092633 | 0.048234 | 0.036953 | -0.02433 | 0.005983 | 0.040879 | 0.11344 | 0.002484 | 0.075048
2170.8906 | 121.6278 | -121.4859 | 0.13733 | 0.076067 | -0.035942 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.026092 | 0.070802 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.003172 | 121.562 | 121.45 | 121.5151 | 121.4655 | 121.6 | 121.5577 | 121.4598 | 0.089113 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.015139 | 0.040879 | 0.10887 | -0.006673 | 0.061313
2172.5938 | 121.6965 | -121.5088 | 0.12817 | 0.076067 | -0.035942 | 0.024629 | -0.006703 | 0.10493 | 0.071848 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.027798 | -0.042641 | -0.012328 | 121.5849 | 121.4728 | 121.5334 | 121.5021 | 121.6137 | 121.5806 | 121.4735 | 0.093691 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.046109 | -0.02433 | 0.005983 | 0.045457 | 0.11802 | -0.002094 | 0.07047
2174.2656 | 121.7606 | -121.4813 | 0.11902 | 0.071489 | -0.040521 | 0.024629 | -0.01586 | 0.10493 | 0.058113 | -0.039826 | 0.070802 | 0.19369 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | -0.003172 | 121.5528 | 121.4408 | 121.506 | 121.4655 | 121.5863 | 121.5394 | 121.4415 | 0.089113 | 0.212 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.015139 | 0.045457 | 0.10887 | 0.007062 | 0.07047
2175.9531 | 121.6324 | -121.5546 | 0.15564 | 0.071489 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.07538 | 0.18911 | 0.02325 | -0.11552 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 121.6261 | 121.5278 | 121.5838 | 121.5387 | 121.6641 | 121.631 | 121.5193 | 0.093691 | 0.20742 | 0.041561 | -0.097212 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.040879 | 0.11344 | -0.011251 | 0.061313
2177.6562 | 120.9824 | -98.877 | 21.7987 | 0.071489 | -0.040521 | 0.020051 | -0.025017 | 0.10951 | 0.071848 | -0.039826 | 0.066223 | 0.17995 | 0.027829 | -0.11094 | 0.071126 | 0.018642 | -0.042641 | -0.00775 | 98.9484 | 98.8364 | 98.897 | 98.8519 | 98.9865 | 98.9488 | 98.8371 | 0.084534 | 0.19826 | 0.04614 | -0.092633 | 0.089437 | 0.036953 | -0.02433 | 0.010561 | -0.004903 | 0.10886 | -0.043297 | 0.07047
2179.3281 | 121.2387 | -10.0067 | 111.1267 | 0.048597 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.16164 | 0.004937 | -0.11094 | 0.048236 | 0.050688 | -0.024328 | 0.001406 | 10.0553 | 9.9479 | 10.0084 | 9.9634 | 10.0888 | 10.0511 | 9.944 | 0.061642 | 0.17995 | 0.023248 | -0.092633 | 0.066547 | 0.068999 | -0.006017 | 0.019717 | -0.004905 | 0.067659 | -0.043299 | 0.029265
2181.0156 | 121.2662 | -70.2255 | 50.8392 | 0.048597 | -0.040521 | 0.010893 | -0.034174 | 0.0912 | 0.053534 | -0.048983 | 0.052488 | 0.17079 | 0.02325 | -0.11552 | 0.043657 | 0.04611 | -0.033484 | 0.001406 | 70.2741 | 70.185 | 70.2364 | 70.1914 | 70.3167 | 70.2791 | 70.1765 | 0.070799 | 0.1891 | 0.041561 | -0.097212 | 0.061968 | 0.064421 | -0.015173 | 0.019717 | 0.008831 | 0.085972 | -0.020407 | 0.056734
2182.7031 | 121.4951 | -118.8538 | 2.3621 | 0.076067 | -0.031363 | 0.029208 | -0.01586 | 0.10951 | 0.071848 | -0.035248 | 0.079959 | 0.19369 | 0.036985 | -0.1201 | 0.025345 | 0.018642 | -0.033484 | -0.003172 | 118.9298 | 118.8224 | 118.883 | 118.8379 | 118.9633 | 118.9256 | 118.8185 | 0.09827 | 0.212 | 0.055296 | -0.10179 | 0.043656 | 0.036953 | -0.015173 | 0.015139 | 0.054614 | 0.11344 | 0.01164 | 0.070469
2184.375 | 121.3989 | -96.1349 | 25.0854 | 0.057754 | -0.040521 | 0.015472 | -0.034174 | 0.0912 | 0.058113 | -0.044405 | 0.061645 | 0.17079 | 0.02325 | -0.11552 | 0.029923 | 0.036954 | -0.033484 | 0.001406 | 96.1927 | 96.0944 | 96.1504 | 96.1008 | 96.2261 | 96.1931 | 96.0905 | 0.079956 | 0.1891 | 0.041561 | -0.097212 | 0.048234 | 0.055265 | -0.015173 | 0.019717 | 0.031722 | 0.095129 | -0.006673 | 0.056734
2186.0625 | 121.4493 | -114.9399 | 6.3492 | 0.071489 | -0.031363 | 0.029208 | -0.01586 | 0.10493 | 0.067269 | -0.035248 | 0.070802 | 0.18911 | 0.032407 | -0.12468 | 0.025345 | 0.009486 | -0.04722 | -0.00775 | 115.0114 | 114.9085 | 114.9691 | 114.924 | 115.0448 | 115.0071 | 114.9046 | 0.089113 | 0.20742 | 0.050718 | -0.10637 | 0.043656 | 0.027797 | -0.028909 | 0.010561 | 0.045457 | 0.11802 | 0.007062 | 0.079627
2187.7656 | 121.4264 | -116.7526 | 4.6051 | 0.080646 | -0.031363 | 0.029208 | -0.020438 | 0.10951 | 0.076426 | -0.03067 | 0.066223 | 0.19369 | 0.032407 | -0.12468 | 0.029923 | 0.02322 | -0.033484 | -0.003172 | 116.8333 | 116.7213 | 116.7818 | 116.7322 | 116.8621 | 116.8291 | 116.722 | 0.084534 | 0.212 | 0.050718 | -0.10637 | 0.048234 | 0.041531 | -0.015173 | 0.015139 | 0.0363 | 0.099707 | 0.002484 | 0.065891
2189.5156 | 121.3943 | -117.2104 | 4.1656 | 0.076067 | -0.022205 | 0.038365 | -0.01586 | 0.10951 | 0.067269 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 117.2865 | 117.1882 | 117.2488 | 117.1945 | 117.3199 | 117.2777 | 117.1751 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.045457 | 0.11802 | 0.002484 | 0.075048
2191.2031 | 121.5271 | -117.3706 | 3.9368 | 0.071489 | -0.026784 | 0.024629 | -0.01586 | 0.12325 | 0.071848 | -0.039826 | 0.07538 | 0.18911 | 0.036985 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 117.4421 | 117.3438 | 117.3952 | 117.3547 | 117.4939 | 117.4425 | 117.3308 | 0.093691 | 0.20742 | 0.055296 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.045457 | 0.11344 | 0.007062 | 0.075048
2192.9688 | 121.3943 | -117.4667 | 3.9368 | 0.071489 | -0.035942 | 0.029208 | -0.01586 | 0.11409 | 0.076426 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.11552 | 0.034501 | 0.02322 | -0.038063 | -0.00775 | 117.5382 | 117.4308 | 117.4959 | 117.4509 | 117.5808 | 117.5432 | 117.4315 | 0.093691 | 0.20742 | 0.04614 | -0.097212 | 0.052812 | 0.041531 | -0.019752 | 0.010561 | 0.040879 | 0.11344 | -0.006672 | 0.065892
2194.7812 | 121.4447 | -117.5903 | 3.7674 | 0.071489 | -0.022205 | 0.029208 | -0.020438 | 0.11409 | 0.076426 | -0.039826 | 0.070802 | 0.19369 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 117.6618 | 117.5681 | 117.6195 | 117.5699 | 117.7044 | 117.6668 | 117.5505 | 0.089113 | 0.212 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | -0.002094 | 0.07047
2196.5625 | 121.4996 | -117.5674 | 3.7628 | 0.071489 | -0.035942 | 0.024629 | -0.011281 | 0.11867 | 0.071848 | -0.035248 | 0.066223 | 0.18911 | 0.027829 | -0.12926 | 0.034501 | 0.02322 | -0.04722 | -0.003172 | 117.6389 | 117.5315 | 117.5921 | 117.5562 | 117.6861 | 117.6393 | 117.5322 | 0.084534 | 0.20742 | 0.04614 | -0.11095 | 0.052812 | 0.041531 | -0.028909 | 0.015139 | 0.031722 | 0.11344 | -0.006672 | 0.075049
2198.3125 | 121.5225 | -117.6865 | 3.6255 | 0.076067 | -0.031363 | 0.029208 | -0.01586 | 0.10951 | 0.071848 | -0.03067 | 0.07538 | 0.18911 | 0.02325 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 117.7625 | 117.6551 | 117.7157 | 117.6706 | 117.796 | 117.7583 | 117.6558 | 0.093691 | 0.20742 | 0.041561 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.045457 | 0.11802 | -0.006673 | 0.065891
2200.0781 | 121.5317 | -117.8741 | 3.4195 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.11867 | 0.071848 | -0.03067 | 0.079959 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 117.9502 | 117.8474 | 117.9034 | 117.8583 | 117.9928 | 117.946 | 117.8435 | 0.09827 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | 0.002484 | 0.075048
2201.7812 | 121.5408 | -117.7551 | 3.5522 | 0.080646 | -0.035942 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.070802 | 0.19369 | 0.036985 | -0.1201 | 0.029923 | 0.027798 | -0.04722 | -0.003172 | 117.8358 | 117.7192 | 117.7843 | 117.7393 | 117.8646 | 117.8316 | 117.7199 | 0.089113 | 0.212 | 0.055296 | -0.10179 | 0.048234 | 0.046109 | -0.028909 | 0.015139 | 0.040879 | 0.11802 | 0.007062 | 0.084205
2203.5312 | 121.5179 | -117.7597 | 3.5614 | 0.071489 | -0.031363 | 0.029208 | -0.011281 | 0.11867 | 0.067269 | -0.035248 | 0.079959 | 0.18911 | 0.027829 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 117.8312 | 117.7283 | 117.7889 | 117.7484 | 117.8784 | 117.827 | 117.7245 | 0.09827 | 0.20742 | 0.04614 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | -0.002094 | 0.075049
2205.2812 | 121.4081 | -117.8009 | 3.598 | 0.071489 | -0.031363 | 0.029208 | -0.020438 | 0.10951 | 0.076426 | -0.03067 | 0.079959 | 0.18911 | 0.027829 | -0.11552 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 117.8724 | 117.7695 | 117.8301 | 117.7805 | 117.9104 | 117.8773 | 117.7702 | 0.09827 | 0.20742 | 0.04614 | -0.097212 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | -0.002094 | 0.075049
2207.0312 | 121.4767 | -117.8284 | 3.5294 | 0.080646 | -0.035942 | 0.029208 | -0.020438 | 0.10951 | 0.076426 | -0.035248 | 0.070802 | 0.17995 | 0.036985 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.003172 | 117.909 | 117.7924 | 117.8576 | 117.8079 | 117.9379 | 117.9048 | 117.7931 | 0.089113 | 0.19826 | 0.055296 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.015139 | 0.040879 | 0.11802 | 0.007062 | 0.084205
2208.7188 | 121.4081 | -117.7917 | 3.598 | 0.076067 | -0.026784 | 0.033786 | -0.01586 | 0.11409 | 0.076426 | -0.026092 | 0.070802 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 117.8678 | 117.765 | 117.8255 | 117.7759 | 117.9058 | 117.8682 | 117.7657 | 0.089113 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | 0.002484 | 0.075048
2210.4844 | 121.4355 | -117.8787 | 3.5248 | 0.076067 | -0.022205 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.035248 | 0.07538 | 0.19369 | 0.036985 | -0.12468 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 117.9548 | 117.8565 | 117.9034 | 117.8629 | 117.9882 | 117.9506 | 117.8435 | 0.093691 | 0.212 | 0.055296 | -0.10637 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.045457 | 0.11802 | 0.007062 | 0.079626
2212.2344 | 121.5088 | -117.6086 | 3.7354 | 0.06691 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.026092 | 0.070802 | 0.18911 | 0.036985 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.003172 | 117.6756 | 117.5819 | 117.6379 | 117.5882 | 117.7182 | 117.6805 | 117.5826 | 0.089113 | 0.20742 | 0.055296 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.015139 | 0.036301 | 0.10887 | 0.002484 | 0.075048
2213.9219 | 121.5317 | -117.7551 | 3.5797 | 0.076067 | -0.035942 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.070802 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.02322 | -0.033484 | -0.003172 | 117.8312 | 117.7192 | 117.7843 | 117.7393 | 117.8646 | 117.8316 | 117.7199 | 0.089113 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.041531 | -0.015173 | 0.015139 | 0.040879 | 0.10429 | 0.007062 | 0.070469
2215.6719 | 121.4264 | -117.897 | 3.5156 | 0.071489 | -0.031363 | 0.033786 | -0.01586 | 0.10493 | 0.076426 | -0.035248 | 0.070802 | 0.18911 | 0.032407 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | 0.001406 | 117.9685 | 117.8657 | 117.9308 | 117.8812 | 118.002 | 117.9735 | 117.8618 | 0.089113 | 0.20742 | 0.050718 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.019717 | 0.040879 | 0.11344 | 0.002484 | 0.075048
2217.4062 | 121.4218 | -117.9337 | 3.4103 | 0.076067 | -0.022205 | 0.029208 | -0.011281 | 0.11409 | 0.071848 | -0.035248 | 0.066223 | 0.18453 | 0.036985 | -0.1201 | 0.029923 | 0.027798 | -0.04722 | -0.003172 | 118.0097 | 117.9115 | 117.9629 | 117.9224 | 118.0477 | 118.0055 | 117.8984 | 0.084534 | 0.20284 | 0.055296 | -0.10179 | 0.048234 | 0.046109 | -0.028909 | 0.015139 | 0.0363 | 0.11344 | 0.007062 | 0.084205
2219.0938 | 121.5088 | -118.4738 | 2.8473 | 0.06691 | -0.026784 | 0.029208 | -0.020438 | 0.10493 | 0.081005 | -0.039826 | 0.07538 | 0.18911 | 0.036985 | -0.12468 | 0.025345 | 0.02322 | -0.038063 | -0.00775 | 118.5407 | 118.447 | 118.503 | 118.4534 | 118.5787 | 118.5548 | 118.434 | 0.093691 | 0.20742 | 0.055296 | -0.10637 | 0.043656 | 0.041531 | -0.019752 | 0.010561 | 0.050035 | 0.11344 | 0.01164 | 0.075048
2220.7969 | 121.4081 | -118.5013 | 2.8839 | 0.071489 | -0.031363 | 0.033786 | -0.01586 | 0.11409 | 0.071848 | -0.03067 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.034501 | 0.027798 | -0.042641 | -0.003172 | 118.5728 | 118.4699 | 118.5351 | 118.4854 | 118.6154 | 118.5731 | 118.4706 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.052812 | 0.046109 | -0.02433 | 0.015139 | 0.040879 | 0.11802 | -0.002094 | 0.075048
2222.4844 | 121.0373 | -32.4142 | 88.266 | 0.053175 | -0.049678 | 0.010893 | -0.034174 | 0.082044 | 0.044377 | -0.058139 | 0.047909 | 0.16164 | 0.004937 | -0.10637 | 0.043657 | 0.041532 | -0.028906 | 0.010563 | 32.4674 | 32.3646 | 32.4251 | 32.3801 | 32.4963 | 32.4586 | 32.3561 | 0.06622 | 0.17995 | 0.023248 | -0.088054 | 0.061968 | 0.059843 | -0.010595 | 0.028874 | 0.004252 | 0.076815 | -0.03872 | 0.033843
2224.2188 | 120.282 | -33.3618 | 87.085 | 0.057754 | -0.0451 | 0.006315 | -0.029595 | 0.0912 | 0.048956 | -0.053561 | 0.047909 | 0.17079 | 0.009515 | -0.11094 | 0.043657 | 0.041532 | -0.028906 | 0.005985 | 33.4196 | 33.3167 | 33.3681 | 33.3322 | 33.453 | 33.4108 | 33.3083 | 0.06622 | 0.1891 | 0.027826 | -0.092633 | 0.061968 | 0.059843 | -0.010595 | 0.024296 | 0.004252 | 0.076815 | -0.034142 | 0.038421
2225.9688 | 121.3943 | -116.011 | 4.9576 | 0.080646 | -0.026784 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.03067 | 0.070802 | 0.18911 | 0.036985 | -0.11552 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 116.0917 | 115.9843 | 116.0403 | 115.9906 | 116.1251 | 116.0829 | 115.9804 | 0.089113 | 0.20742 | 0.055296 | -0.097212 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.036301 | 0.10887 | 0.002484 | 0.075048
2227.6562 | 121.3394 | -116.684 | 4.3762 | 0.071489 | -0.022205 | 0.029208 | -0.011281 | 0.11409 | 0.076426 | -0.044405 | 0.070802 | 0.18911 | 0.027829 | -0.11552 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 116.7554 | 116.6618 | 116.7132 | 116.6727 | 116.7981 | 116.7604 | 116.6396 | 0.089113 | 0.20742 | 0.04614 | -0.097212 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.045457 | 0.10887 | 0.002484 | 0.065892
2229.4219 | 121.2936 | -117.16 | 3.9688 | 0.071489 | -0.031363 | 0.024629 | -0.011281 | 0.11867 | 0.076426 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.12468 | 0.034501 | 0.032376 | -0.04722 | -0.00775 | 117.2315 | 117.1287 | 117.1847 | 117.1488 | 117.2787 | 117.2365 | 117.1248 | 0.093691 | 0.20742 | 0.050718 | -0.10637 | 0.052812 | 0.050687 | -0.028909 | 0.010561 | 0.040879 | 0.1226 | -0.002094 | 0.079627
2231.1094 | 121.2524 | -118.1213 | 3.0304 | 0.080646 | -0.031363 | 0.024629 | -0.020438 | 0.10493 | 0.076426 | -0.035248 | 0.070802 | 0.17995 | 0.02325 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 118.202 | 118.09 | 118.146 | 118.1009 | 118.2263 | 118.1978 | 118.0861 | 0.089113 | 0.19826 | 0.041561 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.040879 | 0.11344 | -0.006673 | 0.065891
2232.8594 | 121.3806 | -118.3228 | 2.8564 | 0.076067 | -0.040521 | 0.020051 | -0.020438 | 0.10493 | 0.071848 | -0.035248 | 0.066223 | 0.19369 | 0.02325 | -0.1201 | 0.025345 | 0.027798 | -0.042641 | -0.00775 | 118.3988 | 118.2822 | 118.3428 | 118.3023 | 118.4277 | 118.3946 | 118.2875 | 0.084534 | 0.212 | 0.041561 | -0.10179 | 0.043656 | 0.046109 | -0.02433 | 0.010561 | 0.040878 | 0.10886 | -0.002095 | 0.065891
2234.625 | 121.3943 | -119.632 | 1.6937 | 0.071489 | -0.031363 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.03067 | 0.061645 | 0.18911 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 119.7034 | 119.6006 | 119.6566 | 119.6161 | 119.7415 | 119.7038 | 119.6013 | 0.079956 | 0.20742 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.031722 | 0.099708 | 0.002484 | 0.07047
2236.3125 | 121.4767 | -120.0485 | 1.2909 | 0.076067 | -0.031363 | 0.038365 | -0.020438 | 0.10493 | 0.085583 | -0.035248 | 0.066223 | 0.18453 | 0.036985 | -0.11094 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 120.1246 | 120.0172 | 120.0869 | 120.0281 | 120.1535 | 120.1341 | 120.0133 | 0.084534 | 0.20284 | 0.055296 | -0.092633 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.0363 | 0.10886 | 0.007062 | 0.079626
2238.0625 | 121.3531 | -120.076 | 1.3229 | 0.071489 | -0.031363 | 0.029208 | -0.006703 | 0.10493 | 0.071848 | -0.035248 | 0.07538 | 0.18911 | 0.027829 | -0.11552 | 0.039079 | 0.027798 | -0.038063 | -0.00775 | 120.1475 | 120.0446 | 120.1052 | 120.0693 | 120.1809 | 120.1478 | 120.0407 | 0.093691 | 0.20742 | 0.04614 | -0.097212 | 0.05739 | 0.046109 | -0.019752 | 0.010561 | 0.036301 | 0.11344 | -0.01125 | 0.065892
2239.75 | 121.3806 | -120.6802 | 0.75073 | 0.06691 | -0.031363 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.035248 | 0.07538 | 0.19369 | 0.027829 | -0.12468 | 0.034501 | 0.018642 | -0.038063 | -0.003172 | 120.7471 | 120.6489 | 120.7094 | 120.6644 | 120.7897 | 120.7567 | 120.645 | 0.093691 | 0.212 | 0.04614 | -0.10637 | 0.052812 | 0.036953 | -0.019752 | 0.015139 | 0.040879 | 0.11344 | -0.006672 | 0.065892
2241.5156 | 121.4264 | -120.8817 | 0.53101 | 0.071489 | -0.026784 | 0.038365 | -0.020438 | 0.10493 | 0.076426 | -0.035248 | 0.070802 | 0.18911 | 0.02325 | -0.11552 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 120.9531 | 120.8549 | 120.92 | 120.8612 | 120.9866 | 120.9581 | 120.8464 | 0.089113 | 0.20742 | 0.041561 | -0.097212 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.036301 | 0.10887 | -0.011251 | 0.061313
2243.2031 | 121.431 | -120.9 | 0.54016 | 0.076067 | -0.031363 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.035248 | 0.070802 | 0.19369 | 0.036985 | -0.1201 | 0.025345 | 0.027798 | -0.042641 | 0.005985 | 120.976 | 120.8686 | 120.9292 | 120.8795 | 121.0095 | 120.9718 | 120.8647 | 0.089113 | 0.212 | 0.055296 | -0.10179 | 0.043656 | 0.046109 | -0.02433 | 0.024296 | 0.045457 | 0.11344 | 0.01164 | 0.079626
2244.8906 | 121.0327 | -113.8412 | 6.8939 | 0.071489 | -0.026784 | 0.024629 | -0.01586 | 0.10951 | 0.067269 | -0.044405 | 0.066223 | 0.19369 | 0.027829 | -0.11552 | 0.034501 | 0.027798 | -0.038063 | 0.001406 | 113.9127 | 113.8145 | 113.8659 | 113.8254 | 113.9508 | 113.9085 | 113.7968 | 0.084534 | 0.212 | 0.04614 | -0.097212 | 0.052812 | 0.046109 | -0.019752 | 0.019717 | 0.031722 | 0.10429 | -0.006672 | 0.065892
2246.6406 | 121.1975 | -116.8625 | 4.216 | 0.071489 | -0.031363 | 0.024629 | -0.011281 | 0.10951 | 0.067269 | -0.039826 | 0.07538 | 0.19827 | 0.041563 | -0.11552 | 0.025345 | 0.027798 | -0.038063 | -0.003172 | 116.934 | 116.8311 | 116.8871 | 116.8512 | 116.972 | 116.9298 | 116.8227 | 0.093691 | 0.21658 | 0.059874 | -0.097212 | 0.043656 | 0.046109 | -0.019752 | 0.015139 | 0.050035 | 0.11344 | 0.016218 | 0.079626
2248.3906 | 121.2662 | -117.0273 | 4.1153 | 0.071489 | -0.035942 | 0.024629 | -0.025017 | 0.10493 | 0.071848 | -0.035248 | 0.070802 | 0.18911 | 0.036985 | -0.12468 | 0.034501 | 0.027798 | -0.038063 | -0.003172 | 117.0988 | 116.9913 | 117.0519 | 117.0023 | 117.1322 | 117.0991 | 116.992 | 0.089113 | 0.20742 | 0.055296 | -0.10637 | 0.052812 | 0.046109 | -0.019752 | 0.015139 | 0.036301 | 0.10887 | 0.002484 | 0.075048
2250.0781 | 121.376 | -117.4667 | 3.7399 | 0.071489 | -0.040521 | 0.029208 | -0.020438 | 0.11409 | 0.071848 | -0.039826 | 0.066223 | 0.17995 | 0.027829 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | 0.001406 | 117.5382 | 117.4262 | 117.4959 | 117.4463 | 117.5808 | 117.5386 | 117.4269 | 0.084534 | 0.19826 | 0.04614 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.019717 | 0.0363 | 0.10429 | -0.002094 | 0.065892
2251.7812 | 121.3486 | -117.8055 | 3.4378 | 0.076067 | -0.035942 | 0.029208 | -0.01586 | 0.10493 | 0.071848 | -0.035248 | 0.066223 | 0.18911 | 0.02325 | -0.11552 | 0.029923 | 0.027798 | -0.04722 | -0.00775 | 117.8815 | 117.7695 | 117.8347 | 117.7896 | 117.9104 | 117.8773 | 117.7702 | 0.084534 | 0.20742 | 0.041561 | -0.097212 | 0.048234 | 0.046109 | -0.028909 | 0.010561 | 0.0363 | 0.11344 | -0.006673 | 0.07047
2253.5156 | 121.3486 | -118.0893 | 3.2043 | 0.076067 | -0.031363 | 0.020051 | -0.011281 | 0.10951 | 0.071848 | -0.039826 | 0.070802 | 0.19369 | 0.032407 | -0.1201 | 0.029923 | 0.02322 | -0.028906 | -0.012328 | 118.1654 | 118.0579 | 118.1093 | 118.078 | 118.1988 | 118.1611 | 118.0495 | 0.089113 | 0.212 | 0.050718 | -0.10179 | 0.048234 | 0.041531 | -0.010595 | 0.005983 | 0.040879 | 0.099708 | 0.002484 | 0.061313
2255.2656 | 121.4584 | -118.1854 | 3.0624 | 0.076067 | -0.035942 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.03067 | 0.07538 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 118.2615 | 118.1495 | 118.2146 | 118.165 | 118.2949 | 118.2573 | 118.1548 | 0.093691 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | 0.007062 | 0.075048
2256.9688 | 121.3348 | -118.483 | 2.8564 | 0.076067 | -0.026784 | 0.029208 | -0.01586 | 0.10493 | 0.081005 | -0.035248 | 0.070802 | 0.18453 | 0.032407 | -0.1201 | 0.034501 | 0.032376 | -0.038063 | -0.00775 | 118.559 | 118.4562 | 118.5122 | 118.4671 | 118.5879 | 118.564 | 118.4477 | 0.089113 | 0.20284 | 0.050718 | -0.10179 | 0.052812 | 0.050687 | -0.019752 | 0.010561 | 0.036301 | 0.10887 | -0.002094 | 0.07047
2258.6562 | 121.3623 | -118.7439 | 2.623 | 0.071489 | -0.031363 | 0.024629 | -0.011281 | 0.11409 | 0.071848 | -0.044405 | 0.066223 | 0.19827 | 0.036985 | -0.12468 | 0.043657 | 0.02322 | -0.042641 | 0.001406 | 118.8154 | 118.7125 | 118.7685 | 118.7326 | 118.858 | 118.8157 | 118.6995 | 0.084534 | 0.21658 | 0.055296 | -0.10637 | 0.061968 | 0.041531 | -0.02433 | 0.019717 | 0.022566 | 0.10886 | -0.006672 | 0.079626
2260.4062 | 121.0876 | -118.1946 | 2.5223 | 0.071489 | -0.031363 | 0.029208 | -0.01586 | 0.10493 | 0.062691 | -0.039826 | 0.070802 | 0.18911 | 0.02325 | -0.1201 | 0.034501 | 0.018642 | -0.042641 | -0.012328 | 118.2661 | 118.1632 | 118.2238 | 118.1787 | 118.2995 | 118.2573 | 118.1548 | 0.089113 | 0.20742 | 0.041561 | -0.10179 | 0.052812 | 0.036953 | -0.02433 | 0.005983 | 0.036301 | 0.11344 | -0.011251 | 0.065891
2262.1562 | 121.2479 | -120.4971 | 0.45319 | 0.076067 | -0.031363 | 0.024629 | -0.020438 | 0.10951 | 0.076426 | -0.039826 | 0.07538 | 0.19369 | 0.041563 | -0.12468 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 120.5732 | 120.4658 | 120.5218 | 120.4767 | 120.6066 | 120.5736 | 120.4573 | 0.093691 | 0.212 | 0.059874 | -0.10637 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | 0.01164 | 0.079626
2263.9062 | 121.2204 | -119.7327 | 1.3733 | 0.06691 | -0.035942 | 0.033786 | -0.020438 | 0.10493 | 0.071848 | -0.044405 | 0.07538 | 0.19369 | 0.036985 | -0.1201 | 0.029923 | 0.027798 | -0.038063 | -0.00775 | 119.7996 | 119.6967 | 119.7665 | 119.7122 | 119.8376 | 119.8045 | 119.6883 | 0.093691 | 0.212 | 0.055296 | -0.10179 | 0.048234 | 0.046109 | -0.019752 | 0.010561 | 0.045457 | 0.11344 | 0.007062 | 0.075048
2265.6094 | 121.1975 | -120.6162 | 0.60883 | 0.071489 | -0.031363 | 0.033786 | -0.01586 | 0.11409 | 0.076426 | -0.03067 | 0.07538 | 0.18453 | 0.036985 | -0.1201 | 0.039079 | 0.018642 | -0.038063 | 0.005985 | 120.6876 | 120.5848 | 120.6499 | 120.6003 | 120.7302 | 120.6926 | 120.5855 | 0.093691 | 0.20284 | 0.055296 | -0.10179 | 0.05739 | 0.036953 | -0.019752 | 0.024296 | 0.036301 | 0.11344 | -0.002094 | 0.075048
2267.3594 | 121.3074 | -120.6985 | 0.48065 | 0.076067 | -0.031363 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.03067 | 0.070802 | 0.19369 | 0.032407 | -0.11552 | 0.029923 | 0.02322 | -0.033484 | 0.001406 | 120.7746 | 120.6672 | 120.7278 | 120.6827 | 120.8081 | 120.775 | 120.6679 | 0.089113 | 0.212 | 0.050718 | -0.097212 | 0.048234 | 0.041531 | -0.015173 | 0.019717 | 0.040879 | 0.10429 | 0.002484 | 0.065891
2269.1094 | 121.3486 | -120.7993 | 0.4303 | 0.06691 | -0.035942 | 0.038365 | -0.011281 | 0.11409 | 0.071848 | -0.035248 | 0.07538 | 0.19369 | 0.041563 | -0.12468 | 0.029923 | 0.027798 | -0.033484 | 0.005985 | 120.8662 | 120.7633 | 120.8376 | 120.788 | 120.9133 | 120.8711 | 120.764 | 0.093691 | 0.212 | 0.059874 | -0.10637 | 0.048234 | 0.046109 | -0.015173 | 0.024296 | 0.045457 | 0.10886 | 0.01164 | 0.075047
2270.8594 | 121.2708 | -120.9091 | 0.42572 | 0.071489 | -0.035942 | 0.024629 | -0.020438 | 0.11409 | 0.076426 | -0.03067 | 0.084537 | 0.18911 | 0.046142 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | -0.00775 | 120.9806 | 120.8732 | 120.9337 | 120.8887 | 121.0232 | 120.9855 | 120.8784 | 0.10285 | 0.20742 | 0.064453 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.010561 | 0.054614 | 0.12718 | 0.016219 | 0.088783
2272.5469 | 121.2799 | -120.8954 | 0.42572 | 0.06691 | -0.035942 | 0.033786 | -0.011281 | 0.10951 | 0.076426 | -0.026092 | 0.07538 | 0.18453 | 0.036985 | -0.1201 | 0.039079 | 0.027798 | -0.038063 | 0.001406 | 120.9623 | 120.8594 | 120.9292 | 120.8841 | 121.0049 | 120.9718 | 120.8693 | 0.093691 | 0.20284 | 0.055296 | -0.10179 | 0.05739 | 0.046109 | -0.019752 | 0.019717 | 0.036301 | 0.11344 | -0.002094 | 0.075048
2274.2969 | 121.2936 | -120.8817 | 0.45776 | 0.071489 | -0.031363 | 0.033786 | -0.006703 | 0.10493 | 0.071848 | -0.035248 | 0.07538 | 0.18453 | 0.032407 | -0.11552 | 0.043657 | 0.02322 | -0.033484 | -0.00775 | 120.9531 | 120.8503 | 120.9154 | 120.8749 | 120.9866 | 120.9535 | 120.8464 | 0.093691 | 0.20284 | 0.050718 | -0.097212 | 0.061968 | 0.041531 | -0.015173 | 0.010561 | 0.031723 | 0.10886 | -0.01125 | 0.065891
2275.9844 | 121.3028 | -120.9 | 0.42114 | 0.06691 | -0.026784 | 0.024629 | -0.01586 | 0.10951 | 0.071848 | -0.039826 | 0.070802 | 0.18453 | 0.032407 | -0.1201 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 120.9669 | 120.8732 | 120.9246 | 120.8841 | 121.0095 | 120.9718 | 120.8601 | 0.089113 | 0.20284 | 0.050718 | -0.10179 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.036301 | 0.10887 | -0.002094 | 0.07047
2277.6719 | 121.3577 | -120.8817 | 0.46234 | 0.076067 | -0.026784 | 0.029208 | -0.020438 | 0.10951 | 0.071848 | -0.039826 | 0.07538 | 0.18911 | 0.046142 | -0.12468 | 0.029923 | 0.018642 | -0.04722 | -0.003172 | 120.9577 | 120.8549 | 120.9109 | 120.8612 | 120.9912 | 120.9535 | 120.8418 | 0.093691 | 0.20742 | 0.064453 | -0.10637 | 0.048234 | 0.036953 | -0.028909 | 0.015139 | 0.045457 | 0.1226 | 0.016219 | 0.093362
2279.4062 | 121.3715 | -120.8908 | 0.45776 | 0.06691 | -0.031363 | 0.029208 | -0.011281 | 0.10951 | 0.067269 | -0.035248 | 0.07538 | 0.18911 | 0.032407 | -0.1201 | 0.025345 | 0.018642 | -0.042641 | 0.001406 | 120.9577 | 120.8594 | 120.92 | 120.8795 | 121.0003 | 120.9581 | 120.8556 | 0.093691 | 0.20742 | 0.050718 | -0.10179 | 0.043656 | 0.036953 | -0.02433 | 0.019717 | 0.050035 | 0.11802 | 0.007062 | 0.075048
2281.1562 | 121.2021 | -119.2474 | 1.593 | 0.062332 | -0.031363 | 0.024629 | -0.011281 | 0.10493 | 0.076426 | -0.039826 | 0.070802 | 0.18453 | 0.046142 | -0.11552 | 0.029923 | 0.02322 | -0.033484 | -0.003172 | 119.3098 | 119.2161 | 119.2721 | 119.2362 | 119.3524 | 119.3239 | 119.2076 | 0.089113 | 0.20284 | 0.064453 | -0.097212 | 0.048234 | 0.041531 | -0.015173 | 0.015139 | 0.040879 | 0.10429 | 0.016219 | 0.079626
2282.8438 | 121.3394 | -120.6162 | 0.45776 | 0.06691 | -0.026784 | 0.033786 | -0.01586 | 0.10493 | 0.076426 | -0.039826 | 0.079959 | 0.18453 | 0.041563 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.003172 | 120.6831 | 120.5894 | 120.6499 | 120.6003 | 120.7211 | 120.6926 | 120.5763 | 0.09827 | 0.20284 | 0.059874 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.015139 | 0.050036 | 0.11802 | 0.01164 | 0.079626
2284.5938 | 121.3486 | -120.6665 | 0.48523 | 0.062332 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.035248 | 0.070802 | 0.18911 | 0.036985 | -0.1201 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 120.7288 | 120.6397 | 120.6957 | 120.6506 | 120.776 | 120.7338 | 120.6313 | 0.089113 | 0.20742 | 0.055296 | -0.10179 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | 0.007062 | 0.079626
2286.2812 | 121.0648 | -2.092 | 118.5379 | 0.044018 | -0.063415 | -0.002842 | -0.047909 | 0.082044 | 0.048956 | -0.071874 | 0.038752 | 0.15248 | 0.000359 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 2.136 | 2.0286 | 2.0891 | 2.0441 | 2.174 | 2.1409 | 2.0201 | 0.057063 | 0.17079 | 0.01867 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.061611 | 0.020108
2288.0312 | 121.2158 | -0.1831 | 120.4605 | 0.03944 | -0.058836 | 0.001736 | -0.052488 | 0.086622 | 0.048956 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.050688 | -0.028906 | 0.015141 | 0.22254 | 0.12427 | 0.18484 | 0.13062 | 0.26973 | 0.23206 | 0.11581 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.068999 | -0.010595 | 0.033452 | -0.009483 | 0.072237 | -0.043299 | 0.038421
2289.7031 | 121.2662 | -0.14191 | 120.8679 | 0.034862 | -0.054257 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 0.17677 | 0.08765 | 0.14364 | 0.098576 | 0.2148 | 0.18628 | 0.074612 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2291.4688 | 116.7435 | -51.6174 | 64.4852 | 0.053175 | -0.049678 | 0.010893 | -0.029595 | 0.095778 | 0.058113 | -0.053561 | 0.047909 | 0.17079 | 0.02325 | -0.11094 | 0.052814 | 0.04611 | -0.028906 | 0.005985 | 51.6706 | 51.5678 | 51.6283 | 51.5878 | 51.7132 | 51.6755 | 51.5639 | 0.06622 | 0.1891 | 0.041561 | -0.092633 | 0.071125 | 0.064421 | -0.010595 | 0.024296 | -0.004905 | 0.076815 | -0.029564 | 0.052156
2293.1562 | 120.7443 | -0.89264 | 119.8746 | 0.03944 | -0.058836 | 0.006315 | -0.038752 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.010563 | 0.93208 | 0.8338 | 0.89895 | 0.85389 | 0.9701 | 0.93244 | 0.82992 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.028874 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2294.9062 | 120.9778 | -0.78735 | 120.0302 | 0.03944 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.005985 | 0.82679 | 0.72852 | 0.78451 | 0.73945 | 0.8694 | 0.83173 | 0.72006 | 0.061642 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.024296 | -0.009483 | 0.067659 | -0.047877 | 0.029265
2296.6562 | 121.019 | -0.70496 | 120.2271 | 0.044018 | -0.058836 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.058139 | 0.043331 | 0.15248 | 0.004937 | -0.11552 | 0.057392 | 0.059844 | -0.028906 | 0.019719 | 0.74897 | 0.64612 | 0.70211 | 0.65705 | 0.77784 | 0.74933 | 0.64682 | 0.061642 | 0.17079 | 0.023248 | -0.097212 | 0.075703 | 0.078155 | -0.010595 | 0.03803 | -0.014061 | 0.072237 | -0.052455 | 0.033843
2298.4062 | 120.5566 | -0.71411 | 120.3461 | 0.044018 | -0.063415 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.058139 | 0.047909 | 0.15248 | 0.004937 | -0.11094 | 0.052814 | 0.050688 | -0.024328 | 0.015141 | 0.75813 | 0.6507 | 0.72043 | 0.67078 | 0.79616 | 0.75849 | 0.65597 | 0.06622 | 0.17079 | 0.023248 | -0.092633 | 0.071125 | 0.068999 | -0.006017 | 0.033452 | -0.004905 | 0.072237 | -0.047877 | 0.029265
2300.1562 | 120.726 | -0.737 | 120.314 | 0.03944 | -0.063415 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.019719 | 0.77644 | 0.67358 | 0.74331 | 0.69367 | 0.81904 | 0.7768 | 0.67428 | 0.061642 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.03803 | -0.009483 | 0.067659 | -0.043299 | 0.033843
2301.9219 | 121.106 | -0.71411 | 120.3323 | 0.034862 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.067295 | 0.043331 | 0.16164 | 0.009515 | -0.11552 | 0.052814 | 0.059844 | -0.028906 | 0.019719 | 0.74897 | 0.65528 | 0.71585 | 0.67078 | 0.79158 | 0.75849 | 0.64682 | 0.061642 | 0.17995 | 0.027826 | -0.097212 | 0.071125 | 0.078155 | -0.010595 | 0.03803 | -0.009483 | 0.072237 | -0.043299 | 0.038421
2303.6094 | 120.7718 | -0.67291 | 120.3461 | 0.034862 | -0.058836 | 0.001736 | -0.047909 | 0.086622 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.005985 | 0.70777 | 0.61408 | 0.67465 | 0.625 | 0.75953 | 0.71729 | 0.60562 | 0.061642 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.024296 | -0.009483 | 0.06308 | -0.047877 | 0.024686
2305.3594 | 121.0098 | -0.69122 | 120.3003 | 0.053175 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.043657 | 0.059844 | -0.019749 | 0.010563 | 0.7444 | 0.62781 | 0.68838 | 0.64789 | 0.76869 | 0.7356 | 0.62851 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.061968 | 0.078155 | -0.001438 | 0.028874 | -0.004905 | 0.058501 | -0.03872 | 0.024686
2307.1094 | 120.3232 | -0.70496 | 120.0623 | 0.03944 | -0.054257 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.004937 | -0.11552 | 0.06197 | 0.055266 | -0.024328 | 0.005985 | 0.7444 | 0.6507 | 0.71127 | 0.66163 | 0.787 | 0.74476 | 0.64224 | 0.061642 | 0.17995 | 0.023248 | -0.097212 | 0.080281 | 0.073577 | -0.006017 | 0.024296 | -0.018639 | 0.067659 | -0.057033 | 0.029265
2308.7969 | 117.2974 | -0.72784 | 120.0897 | 0.044018 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.058139 | 0.043331 | 0.15706 | 0.009515 | -0.10637 | 0.052814 | 0.059844 | -0.015171 | 0.010563 | 0.77186 | 0.66901 | 0.72958 | 0.68451 | 0.80989 | 0.77222 | 0.6697 | 0.061642 | 0.17537 | 0.027826 | -0.088054 | 0.071125 | 0.078155 | 0.00314 | 0.028874 | -0.009483 | 0.058502 | -0.043299 | 0.024686
2310.5469 | 121.1929 | -0.70953 | 120.4514 | 0.034862 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.000359 | -0.11094 | 0.048236 | 0.059844 | -0.024328 | 0.010563 | 0.7444 | 0.6507 | 0.71127 | 0.6662 | 0.79158 | 0.75391 | 0.64682 | 0.061642 | 0.17079 | 0.01867 | -0.092633 | 0.066547 | 0.078155 | -0.006017 | 0.028874 | -0.004905 | 0.067659 | -0.047877 | 0.024687
2312.25 | 121.2204 | -0.71411 | 120.4376 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.06831 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.10637 | 0.048236 | 0.055266 | -0.019749 | 0.019719 | 0.75355 | 0.65528 | 0.71585 | 0.6662 | 0.78242 | 0.75391 | 0.65139 | 0.061642 | 0.17537 | 0.032405 | -0.088054 | 0.066547 | 0.073577 | -0.001438 | 0.03803 | -0.004905 | 0.06308 | -0.034142 | 0.033843
2314 | 120.7993 | -0.74616 | 120.1447 | 0.03944 | -0.054257 | 0.006315 | -0.043331 | 0.086622 | 0.035221 | -0.067295 | 0.038752 | 0.16164 | 0.014094 | -0.11552 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 0.7856 | 0.6919 | 0.75247 | 0.70282 | 0.83278 | 0.78138 | 0.67886 | 0.057063 | 0.17995 | 0.032405 | -0.097212 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.03872 | 0.038422
2315.75 | 120.6024 | -0.75531 | 120.3552 | 0.044018 | -0.054257 | -0.002842 | -0.047909 | 0.082044 | 0.048956 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.10179 | 0.052814 | 0.055266 | -0.019749 | 0.015141 | 0.79933 | 0.70105 | 0.75247 | 0.7074 | 0.83735 | 0.80427 | 0.69259 | 0.061642 | 0.17537 | 0.032405 | -0.083475 | 0.071125 | 0.073577 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.03872 | 0.033843
2317.5 | 120.4468 | -0.74158 | 120.3369 | 0.03944 | -0.054257 | -0.002842 | -0.043331 | 0.086622 | 0.044377 | -0.062717 | 0.047909 | 0.15248 | 0.009515 | -0.10637 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 0.78102 | 0.68732 | 0.73874 | 0.69825 | 0.8282 | 0.78595 | 0.67886 | 0.06622 | 0.17079 | 0.027826 | -0.088054 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.004905 | 0.072237 | -0.043299 | 0.033843
2319.25 | 120.5658 | -0.72784 | 120.5475 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.086622 | 0.053534 | -0.062717 | 0.038752 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.015141 | 0.76728 | 0.66901 | 0.72958 | 0.67994 | 0.81447 | 0.78138 | 0.66513 | 0.057063 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.033452 | -0.014062 | 0.058501 | -0.047877 | 0.024686
2320.9531 | 121.2524 | -0.70038 | 120.5521 | 0.030283 | -0.058836 | -0.002842 | -0.043331 | 0.082044 | 0.044377 | -0.058139 | 0.043331 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.019719 | 0.73066 | 0.64154 | 0.69754 | 0.65705 | 0.78242 | 0.74475 | 0.64224 | 0.061642 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.03803 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2322.6406 | 120.8633 | -0.737 | 120.575 | 0.044018 | -0.058836 | -0.002842 | -0.047909 | 0.086622 | 0.039799 | -0.058139 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.055266 | -0.019749 | 0.005985 | 0.78102 | 0.67816 | 0.73416 | 0.68909 | 0.82362 | 0.7768 | 0.67886 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.073577 | -0.001438 | 0.024296 | -0.01864 | 0.058501 | -0.043298 | 0.033843
2324.3906 | 120.9549 | -0.75073 | 120.5795 | 0.034862 | -0.058836 | -0.002842 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 0.78559 | 0.6919 | 0.74789 | 0.71198 | 0.82362 | 0.79053 | 0.68801 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2326.1406 | 121.3577 | -0.70038 | 120.5292 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.048956 | -0.067295 | 0.043331 | 0.16164 | 0.009515 | -0.11094 | 0.048236 | 0.050688 | -0.028906 | 0.010563 | 0.73524 | 0.64154 | 0.69754 | 0.65247 | 0.77784 | 0.74933 | 0.63308 | 0.061642 | 0.17995 | 0.027826 | -0.092633 | 0.066547 | 0.068999 | -0.010595 | 0.028874 | -0.004905 | 0.072237 | -0.038721 | 0.038421
2327.8281 | 120.9503 | -0.737 | 120.4376 | 0.048597 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.047909 | 0.16164 | 0.004937 | -0.11094 | 0.048236 | 0.055266 | -0.019749 | 0.015141 | 0.7856 | 0.67816 | 0.73874 | 0.69367 | 0.80989 | 0.78138 | 0.67428 | 0.06622 | 0.17995 | 0.023248 | -0.092633 | 0.066547 | 0.073577 | -0.001438 | 0.033452 | -0.000327 | 0.067658 | -0.043299 | 0.024686
2329.5156 | 121.3531 | -0.70496 | 120.5612 | 0.034862 | -0.067994 | -0.002842 | -0.043331 | 0.086622 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.014094 | -0.10637 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 0.73982 | 0.63696 | 0.70211 | 0.66163 | 0.79158 | 0.74933 | 0.63766 | 0.061642 | 0.17537 | 0.032405 | -0.088054 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2331.2656 | 121.2479 | -0.75989 | 120.6024 | 0.044018 | -0.067994 | -0.002842 | -0.043331 | 0.082044 | 0.053534 | -0.076452 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.06197 | 0.055266 | -0.019749 | 0.010563 | 0.80391 | 0.69189 | 0.75705 | 0.71656 | 0.84193 | 0.81342 | 0.68344 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.080281 | 0.073577 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.047876 | 0.033843
2333.0312 | 121.2891 | -0.72327 | 120.639 | 0.03944 | -0.054257 | 0.001736 | -0.052488 | 0.06831 | 0.044377 | -0.062717 | 0.052488 | 0.1479 | 0.014094 | -0.11094 | 0.057392 | 0.055266 | -0.019749 | 0.015141 | 0.76271 | 0.66901 | 0.725 | 0.67078 | 0.79158 | 0.76764 | 0.66055 | 0.070799 | 0.16621 | 0.032405 | -0.092633 | 0.075703 | 0.073577 | -0.001438 | 0.033452 | -0.004904 | 0.072237 | -0.043298 | 0.033843
2334.7188 | 121.3623 | -0.71411 | 120.5566 | 0.034862 | -0.063415 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.067295 | 0.047909 | 0.16164 | 0.004937 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 0.74897 | 0.6507 | 0.71585 | 0.6662 | 0.79616 | 0.75849 | 0.64682 | 0.06622 | 0.17995 | 0.023248 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.009483 | 0.072237 | -0.052455 | 0.029265
2336.4688 | 121.3989 | -0.72327 | 120.5521 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.039799 | -0.067295 | 0.043331 | 0.16164 | 0.004937 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.010563 | 0.76271 | 0.66443 | 0.725 | 0.67994 | 0.80531 | 0.76307 | 0.65597 | 0.061642 | 0.17995 | 0.023248 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.047877 | 0.029265
2338.2188 | 121.3348 | -0.78278 | 120.6162 | 0.044018 | -0.063415 | 0.010893 | -0.043331 | 0.077466 | 0.058113 | -0.067295 | 0.047909 | 0.1479 | 0.004937 | -0.10637 | 0.06197 | 0.055266 | -0.019749 | 0.010563 | 0.82679 | 0.71936 | 0.79367 | 0.73945 | 0.86024 | 0.84089 | 0.71548 | 0.06622 | 0.16621 | 0.023248 | -0.088054 | 0.080281 | 0.073577 | -0.001438 | 0.028874 | -0.014061 | 0.067658 | -0.057033 | 0.024686
2339.9688 | 121.3943 | -0.75989 | 120.5658 | 0.048597 | -0.058836 | -0.002842 | -0.038752 | 0.077466 | 0.058113 | -0.058139 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.010563 | 0.80849 | 0.70105 | 0.75705 | 0.72114 | 0.83735 | 0.818 | 0.70175 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2341.6562 | 121.4172 | -0.75531 | 120.5658 | 0.03944 | -0.058836 | 0.001736 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 0.052488 | 0.15706 | 0.009515 | -0.10637 | 0.043657 | 0.055266 | -0.019749 | 0.010563 | 0.79475 | 0.69647 | 0.75705 | 0.71656 | 0.8282 | 0.79511 | 0.69259 | 0.070799 | 0.17537 | 0.027826 | -0.088054 | 0.061968 | 0.073577 | -0.001438 | 0.028874 | 0.008831 | 0.072237 | -0.034142 | 0.029264
2343.4219 | 121.2753 | -0.80109 | 120.5933 | 0.044018 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.097207 | 0.052814 | 0.050688 | -0.019749 | 0.015141 | 0.8451 | 0.73767 | 0.79824 | 0.75775 | 0.87855 | 0.84546 | 0.73837 | 0.061642 | 0.17079 | 0.032405 | -0.078896 | 0.071125 | 0.068999 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.03872 | 0.033843
2345.1719 | 121.3211 | -0.81024 | 120.6116 | 0.034862 | -0.058836 | -0.002842 | -0.043331 | 0.06831 | 0.039799 | -0.062717 | 0.047909 | 0.15706 | 0.009515 | -0.11552 | 0.052814 | 0.050688 | -0.019749 | 0.010563 | 0.8451 | 0.75141 | 0.8074 | 0.76691 | 0.87855 | 0.85004 | 0.74752 | 0.06622 | 0.17537 | 0.027826 | -0.097212 | 0.071125 | 0.068999 | -0.001438 | 0.028874 | -0.004905 | 0.067658 | -0.043299 | 0.029264
2346.8594 | 121.376 | -0.80566 | 120.6253 | 0.03944 | -0.063415 | 0.001736 | -0.038752 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.16622 | 0.004937 | -0.11552 | 0.052814 | 0.055266 | -0.019749 | 0.015141 | 0.8451 | 0.74225 | 0.8074 | 0.76691 | 0.88771 | 0.85004 | 0.74295 | 0.061642 | 0.18453 | 0.023248 | -0.097212 | 0.071125 | 0.073577 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.047877 | 0.024686
2348.6094 | 121.4127 | -0.76904 | 120.6024 | 0.044018 | -0.063415 | 0.001736 | -0.047909 | 0.086622 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11552 | 0.057392 | 0.059844 | -0.024328 | 0.010563 | 0.81306 | 0.70563 | 0.77078 | 0.72113 | 0.85567 | 0.80884 | 0.70175 | 0.061642 | 0.17079 | 0.027826 | -0.097212 | 0.075703 | 0.078155 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.047877 | 0.033843
2350.375 | 121.4584 | -0.75531 | 120.5475 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.052488 | 0.16164 | 0.004937 | -0.10179 | 0.052814 | 0.050688 | -0.028906 | 0.010563 | 0.79475 | 0.69647 | 0.75705 | 0.7074 | 0.83735 | 0.79969 | 0.69259 | 0.070799 | 0.17995 | 0.023248 | -0.083475 | 0.071125 | 0.068999 | -0.010595 | 0.028874 | -0.000326 | 0.081394 | -0.047877 | 0.033843
2352.0938 | 121.4584 | -0.76904 | 120.5658 | 0.044018 | -0.063415 | 0.006315 | -0.047909 | 0.077466 | 0.048956 | -0.053561 | 0.043331 | 0.16164 | 0.004937 | -0.11552 | 0.06197 | 0.059844 | -0.028906 | 0.015141 | 0.81306 | 0.70563 | 0.77536 | 0.72113 | 0.84651 | 0.818 | 0.71548 | 0.061642 | 0.17995 | 0.023248 | -0.097212 | 0.080281 | 0.078155 | -0.010595 | 0.033452 | -0.018639 | 0.072237 | -0.057033 | 0.033843
2353.8438 | 121.4813 | -0.78735 | 120.5887 | 0.03944 | -0.063415 | -0.002842 | -0.052488 | 0.077466 | 0.035221 | -0.067295 | 0.047909 | 0.15248 | 0.014094 | -0.11552 | 0.048236 | 0.050688 | -0.028906 | 0.015141 | 0.82679 | 0.72394 | 0.78451 | 0.73487 | 0.86482 | 0.82258 | 0.72006 | 0.06622 | 0.17079 | 0.032405 | -0.097212 | 0.066547 | 0.068999 | -0.010595 | 0.033452 | -0.000327 | 0.076815 | -0.034142 | 0.043
2355.5781 | 121.3943 | -0.8194 | 120.639 | 0.048597 | -0.063415 | 0.001736 | -0.038752 | 0.072888 | 0.039799 | -0.053561 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 0.86799 | 0.75598 | 0.82113 | 0.78065 | 0.89228 | 0.8592 | 0.76584 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.01864 | 0.06308 | -0.043298 | 0.038422
2357.3281 | 121.3898 | -0.84228 | 120.639 | 0.044018 | -0.058836 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.048236 | 0.059844 | -0.019749 | 0.015141 | 0.8863 | 0.78345 | 0.8486 | 0.79895 | 0.92433 | 0.88666 | 0.77499 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.066547 | 0.078155 | -0.001438 | 0.033452 | -0.004905 | 0.06308 | -0.038721 | 0.029264
2359.0156 | 121.4722 | -0.80566 | 120.6207 | 0.044018 | -0.049678 | 0.001736 | -0.043331 | 0.086622 | 0.044377 | -0.067295 | 0.047909 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 0.84968 | 0.75599 | 0.8074 | 0.76233 | 0.89229 | 0.85004 | 0.73837 | 0.06622 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.004905 | 0.072237 | -0.043299 | 0.033843
2360.7656 | 121.4172 | -0.85602 | 120.607 | 0.034862 | -0.058836 | 0.001736 | -0.038752 | 0.086622 | 0.044377 | -0.058139 | 0.047909 | 0.15248 | 0.014094 | -0.11094 | 0.057392 | 0.055266 | -0.024328 | 0.019719 | 0.89088 | 0.79718 | 0.85775 | 0.81727 | 0.94264 | 0.90039 | 0.79788 | 0.06622 | 0.17079 | 0.032405 | -0.092633 | 0.075703 | 0.073577 | -0.006017 | 0.03803 | -0.009483 | 0.072237 | -0.043298 | 0.038422
2362.5156 | 121.3806 | -0.85602 | 120.6207 | 0.03944 | -0.067994 | 0.001736 | -0.038752 | 0.077466 | 0.053534 | -0.062717 | 0.043331 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.015141 | 0.89546 | 0.78802 | 0.85775 | 0.81727 | 0.93348 | 0.90955 | 0.7933 | 0.061642 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.047877 | 0.024686
2364.2031 | 121.4813 | -0.8606 | 120.5795 | 0.048597 | -0.054257 | 0.006315 | -0.047909 | 0.082044 | 0.048956 | -0.067295 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.084861 | 0.055266 | -0.015171 | 0.024297 | 0.90919 | 0.80634 | 0.86691 | 0.81269 | 0.94264 | 0.90955 | 0.7933 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.10317 | 0.073577 | 0.00314 | 0.042608 | -0.04153 | 0.058502 | -0.070767 | 0.029265
2365.9688 | 121.5729 | -0.83313 | 120.5612 | 0.03944 | -0.063415 | 0.006315 | -0.052488 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.15706 | 0.009515 | -0.11552 | 0.06197 | 0.059844 | -0.019749 | 0.005985 | 0.87257 | 0.76972 | 0.83944 | 0.78064 | 0.9106 | 0.88209 | 0.77041 | 0.061642 | 0.17537 | 0.027826 | -0.097212 | 0.080281 | 0.078155 | -0.001438 | 0.024296 | -0.018639 | 0.06308 | -0.052455 | 0.029264
2367.6719 | 121.4355 | -0.91095 | 120.5795 | 0.044018 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.019719 | 0.95497 | 0.85211 | 0.91269 | 0.86762 | 0.98384 | 0.95533 | 0.84823 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.03803 | -0.014062 | 0.058501 | -0.043299 | 0.029264
2369.4219 | 121.5225 | -0.90637 | 120.4971 | 0.044018 | -0.054257 | 0.001736 | -0.043331 | 0.06831 | 0.039799 | -0.058139 | 0.034174 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.028906 | 0.015141 | 0.95039 | 0.85211 | 0.90811 | 0.86304 | 0.97468 | 0.94617 | 0.84823 | 0.052485 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.010595 | 0.033452 | -0.01864 | 0.06308 | -0.043299 | 0.038421
2371.1719 | 121.5225 | -0.90637 | 120.5475 | 0.03944 | -0.058836 | -0.002842 | -0.034174 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.16622 | 0.004937 | -0.11552 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 0.94581 | 0.84754 | 0.90353 | 0.8722 | 0.98384 | 0.95075 | 0.84823 | 0.061642 | 0.18453 | 0.023248 | -0.097212 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.052455 | 0.029265
2372.8594 | 121.5088 | -0.90637 | 120.5475 | 0.044018 | -0.054257 | -0.002842 | -0.043331 | 0.082044 | 0.048956 | -0.071874 | 0.043331 | 0.16164 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.019719 | 0.95039 | 0.85211 | 0.90353 | 0.86304 | 0.98842 | 0.95533 | 0.8345 | 0.061642 | 0.17995 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.03803 | -0.009483 | 0.06308 | -0.043299 | 0.029264
2374.6094 | 121.4264 | -0.98419 | 120.5429 | 0.044018 | -0.063415 | 0.006315 | -0.043331 | 0.072888 | 0.039799 | -0.058139 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.052814 | 0.055266 | -0.024328 | 0.010563 | 1.0282 | 0.92078 | 0.99051 | 0.94086 | 1.0571 | 1.024 | 0.92605 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.071125 | 0.073577 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.043299 | 0.033843
2376.2969 | 121.4264 | -0.99335 | 120.5383 | 0.044018 | -0.049678 | 0.010893 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 1.0374 | 0.94367 | 1.0042 | 0.94544 | 1.0754 | 1.0377 | 0.93063 | 0.057063 | 0.17079 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.014062 | 0.058501 | -0.047877 | 0.024686
2378.0469 | 121.4676 | -1.2222 | 120.2042 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.053561 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.010563 | 1.2617 | 1.1634 | 1.224 | 1.1789 | 1.3043 | 1.2666 | 1.1687 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.047877 | 0.033843
2379.7969 | 121.431 | -1.1536 | 120.3781 | 0.044018 | -0.054257 | 0.001736 | -0.038752 | 0.082044 | 0.035221 | -0.058139 | 0.047909 | 0.16164 | 0.004937 | -0.10637 | 0.048236 | 0.059844 | -0.024328 | 0.010563 | 1.1976 | 1.0993 | 1.1553 | 1.1148 | 1.2356 | 1.1888 | 1.0954 | 0.06622 | 0.17995 | 0.023248 | -0.088054 | 0.066547 | 0.078155 | -0.006017 | 0.028874 | -0.000327 | 0.072237 | -0.043299 | 0.029265
2381.5469 | 121.5179 | -1.268 | 120.2454 | 0.03944 | -0.058836 | -0.007421 | -0.043331 | 0.082044 | 0.039799 | -0.058139 | 0.047909 | 0.15706 | 0.004937 | -0.11094 | 0.048236 | 0.04611 | -0.028906 | 0.019719 | 1.3074 | 1.2092 | 1.2606 | 1.2247 | 1.35 | 1.3078 | 1.2099 | 0.06622 | 0.17537 | 0.023248 | -0.092633 | 0.066547 | 0.064421 | -0.010595 | 0.03803 | -0.000327 | 0.076815 | -0.043299 | 0.033843
2383.3594 | 121.4676 | -1.2772 | 120.2728 | 0.03944 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.000359 | -0.11094 | 0.057392 | 0.055266 | -0.028906 | 0.015141 | 1.3166 | 1.2137 | 1.2789 | 1.2338 | 1.3546 | 1.3215 | 1.2099 | 0.057063 | 0.17079 | 0.01867 | -0.092633 | 0.075703 | 0.073577 | -0.010595 | 0.033452 | -0.01864 | 0.067658 | -0.057033 | 0.029265
2385.0625 | 121.6095 | -1.2589 | 120.2271 | 0.044018 | -0.063415 | -0.002842 | -0.047909 | 0.082044 | 0.039799 | -0.067295 | 0.043331 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.019719 | 1.3029 | 1.1954 | 1.256 | 1.2109 | 1.3409 | 1.2986 | 1.1916 | 0.061642 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.03803 | -0.014061 | 0.058502 | -0.047877 | 0.024686
2386.8438 | 121.5912 | -1.1032 | 120.3506 | 0.044018 | -0.063415 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.015141 | 1.1472 | 1.0398 | 1.1049 | 1.0553 | 1.1853 | 1.1476 | 1.0359 | 0.061642 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.033452 | -0.009483 | 0.067659 | -0.047877 | 0.029265
2388.625 | 117.1051 | -59.3079 | 57.5592 | 0.048597 | -0.049678 | 0.020051 | -0.034174 | 0.0912 | 0.048956 | -0.048983 | 0.057066 | 0.17537 | 0.018672 | -0.1201 | 0.057392 | 0.041532 | -0.033484 | 0.005985 | 59.3565 | 59.2582 | 59.3279 | 59.2737 | 59.3991 | 59.3568 | 59.2589 | 0.075377 | 0.19368 | 0.036983 | -0.10179 | 0.075703 | 0.059843 | -0.015173 | 0.024296 | -0.000326 | 0.09055 | -0.03872 | 0.052156
2390.3281 | 120.2637 | -0.16937 | 120.0714 | 0.03944 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.16622 | 0.004937 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.010563 | 0.20881 | 0.11054 | 0.16653 | 0.12604 | 0.24684 | 0.21375 | 0.10666 | 0.057063 | 0.18453 | 0.023248 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.028874 | -0.014062 | 0.058501 | -0.047877 | 0.024686
2392.0781 | 120.7031 | -0.14191 | 120.4468 | 0.044018 | -0.058836 | 0.006315 | -0.047909 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.16164 | 0.009515 | -0.11094 | 0.048236 | 0.059844 | -0.019749 | 0.010563 | 0.18593 | 0.083071 | 0.14822 | 0.093998 | 0.21937 | 0.18628 | 0.083768 | 0.061642 | 0.17995 | 0.027826 | -0.092633 | 0.066547 | 0.078155 | -0.001438 | 0.028874 | -0.004905 | 0.06308 | -0.038721 | 0.029264
2393.7812 | 120.8221 | -0.16022 | 120.52 | 0.048597 | -0.054257 | 0.001736 | -0.047909 | 0.077466 | 0.035221 | -0.058139 | 0.047909 | 0.16164 | 0.009515 | -0.11552 | 0.057392 | 0.055266 | -0.019749 | 0.010563 | 0.20881 | 0.10596 | 0.16195 | 0.11231 | 0.23768 | 0.19544 | 0.10208 | 0.06622 | 0.17995 | 0.027826 | -0.097212 | 0.075703 | 0.073577 | -0.001438 | 0.028874 | -0.009483 | 0.067658 | -0.047877 | 0.029264
2395.5625 | 120.8817 | -0.15106 | 120.5795 | 0.044018 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.034174 | 0.16164 | 0.004937 | -0.10179 | 0.066548 | 0.050688 | -0.019749 | 0.015141 | 0.19508 | 0.092226 | 0.14822 | 0.10773 | 0.22853 | 0.19544 | 0.088345 | 0.052485 | 0.17995 | 0.023248 | -0.083475 | 0.084859 | 0.068999 | -0.001438 | 0.033452 | -0.032374 | 0.053923 | -0.061611 | 0.024686
2397.2656 | 120.7947 | -0.19226 | 120.6573 | 0.048597 | -0.058836 | -0.002842 | -0.043331 | 0.086622 | 0.044377 | -0.053561 | 0.043331 | 0.16164 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.019719 | 0.24086 | 0.13342 | 0.18942 | 0.14893 | 0.27888 | 0.23664 | 0.1387 | 0.061642 | 0.17995 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.03803 | -0.009483 | 0.067659 | -0.047877 | 0.029265
2399.0312 | 120.9229 | -0.16022 | 120.6573 | 0.03944 | -0.063415 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 0.034174 | 0.15706 | 0.009515 | -0.10179 | 0.052814 | 0.050688 | -0.019749 | 0.010563 | 0.19966 | 0.096802 | 0.15737 | 0.11231 | 0.23311 | 0.20459 | 0.092922 | 0.052485 | 0.17537 | 0.027826 | -0.083475 | 0.071125 | 0.068999 | -0.001438 | 0.028874 | -0.01864 | 0.053923 | -0.043299 | 0.029264
2400.7188 | 120.9824 | -0.14191 | 120.694 | 0.030283 | -0.054257 | -0.002842 | -0.047909 | 0.06831 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.033484 | 0.010563 | 0.17219 | 0.08765 | 0.13906 | 0.093998 | 0.21022 | 0.18628 | 0.07919 | 0.057063 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.015173 | 0.028874 | -0.014062 | 0.072236 | -0.047877 | 0.038421
2402.4688 | 121.0007 | -0.18768 | 120.7169 | 0.034862 | -0.063415 | -0.002842 | -0.043331 | 0.072888 | 0.039799 | -0.067295 | 0.038752 | 0.15706 | 0.000359 | -0.10637 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 0.22254 | 0.12427 | 0.18484 | 0.14435 | 0.26057 | 0.22748 | 0.12039 | 0.057063 | 0.17537 | 0.01867 | -0.088054 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.014062 | 0.058501 | -0.052455 | 0.020108
2404.2188 | 121.0648 | -0.15564 | 120.7443 | 0.034862 | -0.058836 | 0.001736 | -0.047909 | 0.077466 | 0.035221 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.055266 | -0.019749 | 0.005985 | 0.1905 | 0.096804 | 0.15738 | 0.10773 | 0.23311 | 0.19086 | 0.088345 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.073577 | -0.001438 | 0.024296 | -0.023218 | 0.058501 | -0.052455 | 0.029264
2405.9062 | 120.9274 | -0.21515 | 120.813 | 0.03944 | -0.067994 | -0.002842 | -0.047909 | 0.086622 | 0.044377 | -0.058139 | 0.047909 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.055266 | -0.019749 | 0.010563 | 0.25459 | 0.14716 | 0.21231 | 0.16724 | 0.30177 | 0.25953 | 0.15701 | 0.06622 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.073577 | -0.001438 | 0.028874 | -0.009483 | 0.067658 | -0.03872 | 0.038421
2407.6562 | 120.9732 | -0.20599 | 120.8771 | 0.044018 | -0.063415 | -0.007421 | -0.043331 | 0.072888 | 0.048956 | -0.058139 | 0.043331 | 0.15248 | 0.009515 | -0.11552 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 0.25001 | 0.14258 | 0.19857 | 0.16266 | 0.27888 | 0.25495 | 0.14786 | 0.061642 | 0.17079 | 0.027826 | -0.097212 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.047877 | 0.033843
2409.4062 | 120.9778 | -0.20142 | 120.8633 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.039799 | -0.058139 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.019719 | 0.24086 | 0.14258 | 0.20315 | 0.15809 | 0.28346 | 0.24122 | 0.14328 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.03803 | -0.014062 | 0.058501 | -0.043299 | 0.029264
2411.1562 | 121.0602 | -0.19226 | 120.8771 | 0.044018 | -0.054257 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.15706 | 0.014094 | -0.10179 | 0.057392 | 0.064423 | -0.019749 | 0.010563 | 0.23628 | 0.138 | 0.194 | 0.14435 | 0.26973 | 0.23664 | 0.13412 | 0.061642 | 0.17537 | 0.032405 | -0.083475 | 0.075703 | 0.082734 | -0.001438 | 0.028874 | -0.014061 | 0.06308 | -0.043298 | 0.033843
2412.8594 | 121.1472 | -0.15564 | 120.8496 | 0.034862 | -0.063415 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.004937 | -0.11094 | 0.057392 | 0.064423 | -0.010593 | 0.015141 | 0.1905 | 0.092225 | 0.15738 | 0.10315 | 0.23311 | 0.19544 | 0.092923 | 0.057063 | 0.17537 | 0.023248 | -0.092633 | 0.075703 | 0.082734 | 0.007718 | 0.033452 | -0.01864 | 0.049345 | -0.052455 | 0.01553
2414.625 | 121.1426 | -0.25177 | 120.7764 | 0.044018 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.004937 | -0.11094 | 0.052814 | 0.069001 | -0.028906 | 0.015141 | 0.29579 | 0.19293 | 0.25351 | 0.20844 | 0.32924 | 0.29615 | 0.19363 | 0.057063 | 0.17995 | 0.023248 | -0.092633 | 0.071125 | 0.087312 | -0.010595 | 0.033452 | -0.014062 | 0.067658 | -0.047877 | 0.033843
2416.375 | 121.0602 | -0.29755 | 120.8405 | 0.03944 | -0.058836 | 0.006315 | -0.038752 | 0.072888 | 0.048956 | -0.058139 | 0.043331 | 0.15706 | 0.004937 | -0.10179 | 0.057392 | 0.055266 | -0.019749 | 0.015141 | 0.33699 | 0.23871 | 0.30386 | 0.25879 | 0.37043 | 0.3465 | 0.23941 | 0.061642 | 0.17537 | 0.023248 | -0.083475 | 0.075703 | 0.073577 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.052455 | 0.024686
2418.125 | 121.0693 | -0.31586 | 120.845 | 0.044018 | -0.063415 | -0.007421 | -0.043331 | 0.072888 | 0.035221 | -0.058139 | 0.034174 | 0.15248 | 0.004937 | -0.10637 | 0.052814 | 0.055266 | -0.028906 | 0.015141 | 0.35988 | 0.25244 | 0.30844 | 0.27253 | 0.38875 | 0.35108 | 0.25772 | 0.052485 | 0.17079 | 0.023248 | -0.088054 | 0.071125 | 0.073577 | -0.010595 | 0.033452 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2419.8125 | 121.1884 | -0.24261 | 120.845 | 0.044018 | -0.063415 | -0.002842 | -0.038752 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.16164 | 0.009515 | -0.11094 | 0.052814 | 0.059844 | -0.028906 | 0.019719 | 0.28663 | 0.1792 | 0.23977 | 0.20386 | 0.32008 | 0.28241 | 0.1799 | 0.057063 | 0.17995 | 0.027826 | -0.092633 | 0.071125 | 0.078155 | -0.010595 | 0.03803 | -0.014062 | 0.067658 | -0.043299 | 0.038421
2421.5625 | 120.3644 | -0.17395 | 120.1492 | 0.03944 | -0.058836 | -0.007421 | -0.043331 | 0.072888 | 0.044377 | -0.067295 | 0.038752 | 0.16164 | 0.004937 | -0.10179 | 0.052814 | 0.064423 | -0.015171 | 0.015141 | 0.21339 | 0.11511 | 0.16653 | 0.13062 | 0.24684 | 0.21833 | 0.10665 | 0.057063 | 0.17995 | 0.023248 | -0.083475 | 0.071125 | 0.082734 | 0.00314 | 0.033452 | -0.014062 | 0.053923 | -0.047877 | 0.020108
2423.3125 | 120.5795 | -0.1831 | 120.4376 | 0.034862 | -0.067994 | -0.002842 | -0.047909 | 0.082044 | 0.035221 | -0.058139 | 0.038752 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.010563 | 0.21797 | 0.11511 | 0.18026 | 0.1352 | 0.26515 | 0.21833 | 0.12497 | 0.057063 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.028874 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2425.0625 | 120.6757 | -0.19684 | 120.5063 | 0.034862 | -0.063415 | 0.006315 | -0.047909 | 0.072888 | 0.039799 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 0.2317 | 0.13342 | 0.20315 | 0.14893 | 0.26973 | 0.23664 | 0.13412 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.047877 | 0.029264
2426.7656 | 120.6894 | -0.21057 | 120.6024 | 0.044018 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.034174 | 0.14332 | 0.009515 | -0.10637 | 0.048236 | 0.059844 | -0.028906 | 0.019719 | 0.25459 | 0.14716 | 0.20773 | 0.16724 | 0.28804 | 0.25495 | 0.14785 | 0.052485 | 0.16163 | 0.027826 | -0.088054 | 0.066547 | 0.078155 | -0.010595 | 0.03803 | -0.014062 | 0.06308 | -0.038721 | 0.038421
2428.5312 | 120.7855 | -0.17853 | 120.6162 | 0.034862 | -0.063415 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 0.038752 | 0.16164 | 0.000359 | -0.11552 | 0.052814 | 0.055266 | -0.019749 | 0.015141 | 0.21339 | 0.11511 | 0.17569 | 0.13062 | 0.25142 | 0.2229 | 0.11123 | 0.057063 | 0.17995 | 0.01867 | -0.097212 | 0.071125 | 0.073577 | -0.001438 | 0.033452 | -0.014062 | 0.058501 | -0.052455 | 0.020108
2430.2812 | 120.9 | -0.16022 | 120.6619 | 0.044018 | -0.063415 | -0.007421 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 0.034174 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.050688 | -0.024328 | 0.019719 | 0.20423 | 0.096802 | 0.1528 | 0.11231 | 0.23311 | 0.20459 | 0.092922 | 0.052485 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.068999 | -0.006017 | 0.03803 | -0.01864 | 0.058502 | -0.047877 | 0.029265
2431.9844 | 120.3049 | -0.20142 | 120.1675 | 0.048597 | -0.063415 | 0.006315 | -0.038752 | 0.077466 | 0.048956 | -0.053561 | 0.043331 | 0.15248 | 0.018672 | -0.10637 | 0.048236 | 0.059844 | -0.024328 | 0.015141 | 0.25001 | 0.138 | 0.20773 | 0.16266 | 0.27888 | 0.25037 | 0.14786 | 0.061642 | 0.17079 | 0.036983 | -0.088054 | 0.066547 | 0.078155 | -0.006017 | 0.033452 | -0.004905 | 0.067659 | -0.029564 | 0.043
2433.6875 | 120.6619 | -0.15106 | 120.3964 | 0.03944 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 0.1905 | 0.087647 | 0.1528 | 0.10773 | 0.22853 | 0.19544 | 0.088345 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2435.4375 | 120.7443 | -0.15106 | 120.4834 | 0.044018 | -0.063415 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 0.19508 | 0.087647 | 0.15738 | 0.10315 | 0.22395 | 0.19544 | 0.083767 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.052455 | 0.029265
2437.1406 | 120.7443 | -0.16937 | 120.5338 | 0.044018 | -0.067994 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.071874 | 0.038752 | 0.15248 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 0.21339 | 0.10138 | 0.17111 | 0.11688 | 0.24684 | 0.20917 | 0.097499 | 0.057063 | 0.17079 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.047877 | 0.029264
2438.9062 | 120.7123 | -0.1831 | 120.6116 | 0.034862 | -0.067994 | 0.001736 | -0.047909 | 0.072888 | 0.039799 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 0.21797 | 0.11511 | 0.18484 | 0.1352 | 0.25599 | 0.2229 | 0.12039 | 0.057063 | 0.17079 | 0.023248 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.052455 | 0.029265
2440.6562 | 120.7443 | -0.20142 | 120.6116 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.034174 | 0.15706 | 0.009515 | -0.10637 | 0.048236 | 0.055266 | -0.028906 | 0.010563 | 0.24086 | 0.14258 | 0.20315 | 0.15809 | 0.27888 | 0.24579 | 0.1387 | 0.052485 | 0.17537 | 0.027826 | -0.088054 | 0.066547 | 0.073577 | -0.010595 | 0.028874 | -0.014062 | 0.06308 | -0.038721 | 0.038421
2442.4062 | 120.8038 | -0.20599 | 120.6436 | 0.034862 | -0.058836 | 0.001736 | -0.047909 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.015171 | 0.010563 | 0.24086 | 0.14716 | 0.20773 | 0.15809 | 0.28346 | 0.25495 | 0.14328 | 0.061642 | 0.17079 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | 0.00314 | 0.028874 | -0.009483 | 0.058502 | -0.03872 | 0.029265
2444.1719 | 120.9091 | -0.15564 | 120.694 | 0.044018 | -0.072572 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 0.038752 | 0.16164 | 0.004937 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.010563 | 0.19966 | 0.083068 | 0.15738 | 0.11231 | 0.23768 | 0.20002 | 0.088345 | 0.057063 | 0.17995 | 0.023248 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.057033 | 0.024686
2445.8594 | 120.8267 | -0.21515 | 120.7352 | 0.044018 | -0.063415 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.004937 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.010563 | 0.25917 | 0.15173 | 0.21688 | 0.17182 | 0.29719 | 0.25953 | 0.15243 | 0.061642 | 0.17079 | 0.023248 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.028874 | -0.014061 | 0.058502 | -0.052455 | 0.020108
2447.5469 | 120.9595 | -0.16937 | 120.694 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.072888 | 0.035221 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 0.20881 | 0.11054 | 0.17111 | 0.12146 | 0.24226 | 0.20459 | 0.10666 | 0.057063 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.043298 | 0.033843
2449.25 | 120.9183 | -0.18768 | 120.7581 | 0.03944 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.004937 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 0.22712 | 0.12427 | 0.18484 | 0.14435 | 0.26515 | 0.23206 | 0.12497 | 0.061642 | 0.17537 | 0.023248 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.018639 | 0.067659 | -0.057033 | 0.029265
2451 | 120.9641 | -0.16022 | 120.726 | 0.044018 | -0.058836 | -0.007421 | -0.052488 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.16164 | 0.014094 | -0.10637 | 0.052814 | 0.055266 | -0.015171 | 0.019719 | 0.20423 | 0.10138 | 0.1528 | 0.10773 | 0.23768 | 0.20002 | 0.092922 | 0.057063 | 0.17995 | 0.032405 | -0.088054 | 0.071125 | 0.073577 | 0.00314 | 0.03803 | -0.014062 | 0.053923 | -0.03872 | 0.029265
2452.75 | 120.932 | -0.21515 | 120.7993 | 0.034862 | -0.058836 | -0.002842 | -0.052488 | 0.072888 | 0.039799 | -0.067295 | 0.038752 | 0.14332 | -0.004219 | -0.11094 | 0.057392 | 0.055266 | -0.024328 | 0.019719 | 0.25001 | 0.15631 | 0.21231 | 0.16266 | 0.28804 | 0.25495 | 0.14785 | 0.057063 | 0.16163 | 0.014092 | -0.092633 | 0.075703 | 0.073577 | -0.006017 | 0.03803 | -0.01864 | 0.06308 | -0.061611 | 0.020109
2454.5156 | 120.8908 | -0.19684 | 120.813 | 0.048597 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.047909 | 0.15248 | 0.014094 | -0.11094 | 0.06197 | 0.055266 | -0.024328 | 0.019719 | 0.24544 | 0.13342 | 0.19857 | 0.15351 | 0.2743 | 0.23664 | 0.13412 | 0.06622 | 0.17079 | 0.032405 | -0.092633 | 0.080281 | 0.073577 | -0.006017 | 0.03803 | -0.014061 | 0.072237 | -0.047876 | 0.038422
2456.2812 | 120.9091 | -0.20599 | 120.8267 | 0.048597 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.053561 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 0.25459 | 0.14716 | 0.20773 | 0.16266 | 0.27888 | 0.25037 | 0.15243 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.047877 | 0.029264
2457.9688 | 121.0327 | -0.16937 | 120.813 | 0.044018 | -0.063415 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.15248 | 0.018672 | -0.10637 | 0.057392 | 0.050688 | -0.019749 | 0.010563 | 0.21339 | 0.10596 | 0.17569 | 0.12146 | 0.24684 | 0.20917 | 0.10208 | 0.057063 | 0.17079 | 0.036983 | -0.088054 | 0.075703 | 0.068999 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.03872 | 0.038421
2459.6719 | 121.0327 | -0.16479 | 120.8313 | 0.034862 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.004937 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 0.19966 | 0.10138 | 0.16195 | 0.11689 | 0.24226 | 0.20917 | 0.0975 | 0.061642 | 0.17079 | 0.023248 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.052455 | 0.029265
2461.4219 | 120.9641 | -0.20142 | 120.8496 | 0.044018 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11552 | 0.052814 | 0.055266 | -0.019749 | 0.015141 | 0.24543 | 0.14258 | 0.20315 | 0.15809 | 0.27888 | 0.24122 | 0.13412 | 0.061642 | 0.17079 | 0.027826 | -0.097212 | 0.071125 | 0.073577 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.043299 | 0.029264
2463.1094 | 121.0968 | -0.16022 | 120.8679 | 0.03944 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.16164 | 0.014094 | -0.10637 | 0.052814 | 0.064423 | -0.024328 | 0.015141 | 0.19966 | 0.096802 | 0.15737 | 0.11231 | 0.23768 | 0.20459 | 0.0975 | 0.057063 | 0.17995 | 0.032405 | -0.088054 | 0.071125 | 0.082734 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.03872 | 0.038422
2464.8125 | 120.9915 | -0.18768 | 120.8954 | 0.044018 | -0.058836 | -0.007421 | -0.038752 | 0.077466 | 0.035221 | -0.062717 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.010563 | 0.2317 | 0.12885 | 0.18026 | 0.14893 | 0.26515 | 0.2229 | 0.12497 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.028874 | -0.01864 | 0.053923 | -0.043298 | 0.029265
2466.5781 | 120.9961 | -0.17853 | 120.8954 | 0.044018 | -0.054257 | -0.002842 | -0.043331 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.1479 | 0.000359 | -0.10179 | 0.057392 | 0.055266 | -0.024328 | 0.015141 | 0.22255 | 0.12427 | 0.17569 | 0.1352 | 0.25599 | 0.22748 | 0.11581 | 0.061642 | 0.16621 | 0.01867 | -0.083475 | 0.075703 | 0.073577 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.057033 | 0.024687
2468.3281 | 121.106 | -0.16479 | 120.8862 | 0.034862 | -0.063415 | 0.001736 | -0.038752 | 0.082044 | 0.039799 | -0.058139 | 0.043331 | 0.15248 | 0.014094 | -0.10179 | 0.052814 | 0.059844 | -0.019749 | 0.019719 | 0.19966 | 0.10138 | 0.16653 | 0.12604 | 0.24684 | 0.20459 | 0.10666 | 0.061642 | 0.17079 | 0.032405 | -0.083475 | 0.071125 | 0.078155 | -0.001438 | 0.03803 | -0.009483 | 0.06308 | -0.03872 | 0.033843
2470.0156 | 121.0556 | -0.19226 | 120.9457 | 0.03944 | -0.063415 | 0.001736 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.06197 | 0.055266 | -0.024328 | 0.019719 | 0.2317 | 0.12885 | 0.194 | 0.14893 | 0.27431 | 0.23206 | 0.12954 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.080281 | 0.073577 | -0.006017 | 0.03803 | -0.018639 | 0.067659 | -0.052455 | 0.033843
2471.7656 | 121.0693 | -0.17853 | 120.9366 | 0.044018 | -0.058836 | -0.002842 | -0.038752 | 0.082044 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 0.22255 | 0.11969 | 0.17569 | 0.13978 | 0.26057 | 0.2229 | 0.11123 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.047877 | 0.029264
2473.5156 | 121.0281 | -0.21973 | 120.9503 | 0.03944 | -0.063415 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.038752 | 0.15248 | 0.000359 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 0.25917 | 0.15631 | 0.22604 | 0.1764 | 0.30177 | 0.25953 | 0.15701 | 0.057063 | 0.17079 | 0.01867 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.057033 | 0.020108
2475.2656 | 121.106 | -0.20142 | 120.9503 | 0.03944 | -0.063415 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.058139 | 0.043331 | 0.15706 | 0.018672 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.015141 | 0.24086 | 0.138 | 0.20315 | 0.15809 | 0.2743 | 0.24579 | 0.14328 | 0.061642 | 0.17537 | 0.036983 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.03872 | 0.043
2477.0156 | 121.0693 | -0.21057 | 120.9686 | 0.034862 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.053561 | 0.038752 | 0.16164 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.015141 | 0.24543 | 0.14716 | 0.21231 | 0.16724 | 0.28804 | 0.25495 | 0.15701 | 0.057063 | 0.17995 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2478.7188 | 121.0785 | -0.19684 | 120.9869 | 0.03944 | -0.063415 | -0.002842 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.034174 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 0.23628 | 0.13342 | 0.194 | 0.15351 | 0.27888 | 0.24122 | 0.13412 | 0.052485 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.023218 | 0.058502 | -0.043298 | 0.038422
2480.4688 | 121.106 | -0.23346 | 121.0098 | 0.034862 | -0.067994 | 0.001736 | -0.038752 | 0.072888 | 0.039799 | -0.058139 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.052814 | 0.059844 | -0.015171 | 0.015141 | 0.26832 | 0.16547 | 0.23519 | 0.19471 | 0.30635 | 0.27326 | 0.17532 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.071125 | 0.078155 | 0.00314 | 0.033452 | -0.014062 | 0.053923 | -0.03872 | 0.029265
2482.1562 | 121.2021 | -0.16479 | 120.9824 | 0.03944 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.071874 | 0.038752 | 0.1479 | 0.009515 | -0.11552 | 0.052814 | 0.064423 | -0.019749 | 0.015141 | 0.20423 | 0.10138 | 0.16195 | 0.12146 | 0.24226 | 0.20917 | 0.092921 | 0.057063 | 0.16621 | 0.027826 | -0.097212 | 0.071125 | 0.082734 | -0.001438 | 0.033452 | -0.014062 | 0.058501 | -0.043299 | 0.029264
2483.9219 | 121.2341 | -0.15106 | 120.9732 | 0.03944 | -0.067994 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.004937 | -0.11094 | 0.057392 | 0.059844 | -0.028906 | 0.019719 | 0.1905 | 0.083068 | 0.1528 | 0.10773 | 0.22853 | 0.19086 | 0.083767 | 0.061642 | 0.17079 | 0.023248 | -0.092633 | 0.075703 | 0.078155 | -0.010595 | 0.03803 | -0.014061 | 0.072237 | -0.052455 | 0.033843
2485.6875 | 121.2296 | -0.16022 | 120.9961 | 0.03944 | -0.058836 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.047909 | 0.15706 | 0.004937 | -0.10637 | 0.052814 | 0.064423 | -0.019749 | 0.019719 | 0.19966 | 0.10138 | 0.15737 | 0.11231 | 0.23311 | 0.20459 | 0.0975 | 0.06622 | 0.17537 | 0.023248 | -0.088054 | 0.071125 | 0.082734 | -0.001438 | 0.03803 | -0.004905 | 0.067658 | -0.047877 | 0.024686
2487.4375 | 121.17 | -0.16937 | 121.0236 | 0.044018 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.010563 | 0.21339 | 0.11054 | 0.17111 | 0.12604 | 0.24226 | 0.21375 | 0.10666 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.028874 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2489.1406 | 121.2616 | -0.15564 | 121.0098 | 0.034862 | -0.063415 | -0.002842 | -0.047909 | 0.072888 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.004937 | -0.11552 | 0.057392 | 0.055266 | -0.024328 | 0.015141 | 0.1905 | 0.092225 | 0.1528 | 0.10773 | 0.22853 | 0.19544 | 0.092923 | 0.061642 | 0.17537 | 0.023248 | -0.097212 | 0.075703 | 0.073577 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.052455 | 0.029265
2490.8438 | 121.257 | -0.16479 | 121.0327 | 0.03944 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.035221 | -0.071874 | 0.029595 | 0.15706 | 0.004937 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 0.20423 | 0.10138 | 0.16195 | 0.11689 | 0.24226 | 0.20002 | 0.092921 | 0.047906 | 0.17537 | 0.023248 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.027797 | 0.053923 | -0.052455 | 0.029265
2492.5938 | 121.2433 | -0.16022 | 121.019 | 0.034862 | -0.063415 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.024328 | 0.015141 | 0.19508 | 0.096802 | 0.16195 | 0.11231 | 0.23768 | 0.20459 | 0.0975 | 0.061642 | 0.17079 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.006017 | 0.033452 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2494.3438 | 121.225 | -0.16479 | 121.0327 | 0.03944 | -0.054257 | 0.001736 | -0.043331 | 0.06831 | 0.044377 | -0.071874 | 0.038752 | 0.15248 | 0.014094 | -0.11094 | 0.048236 | 0.055266 | -0.024328 | 0.015141 | 0.20423 | 0.11054 | 0.16653 | 0.12146 | 0.23311 | 0.20917 | 0.092921 | 0.057063 | 0.17079 | 0.032405 | -0.092633 | 0.066547 | 0.073577 | -0.006017 | 0.033452 | -0.009484 | 0.06308 | -0.034142 | 0.038422
2496.0938 | 121.1563 | -0.21515 | 121.0739 | 0.03944 | -0.063415 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.048983 | 0.034174 | 0.15248 | 0.014094 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.010563 | 0.25459 | 0.15173 | 0.21688 | 0.17182 | 0.29719 | 0.25953 | 0.16617 | 0.052485 | 0.17079 | 0.032405 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.028874 | -0.027796 | 0.053923 | -0.047876 | 0.033843
2497.7969 | 121.17 | -0.21057 | 121.106 | 0.034862 | -0.072572 | -0.002842 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.047909 | 0.15706 | 0.004937 | -0.11552 | 0.057392 | 0.059844 | -0.019749 | 0.005985 | 0.24543 | 0.138 | 0.20773 | 0.17182 | 0.28804 | 0.25495 | 0.14328 | 0.06622 | 0.17537 | 0.023248 | -0.097212 | 0.075703 | 0.078155 | -0.001438 | 0.024296 | -0.009483 | 0.067658 | -0.052455 | 0.024686
2499.5625 | 121.3028 | -0.14191 | 121.0648 | 0.03944 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 0.18135 | 0.078492 | 0.13906 | 0.093998 | 0.21937 | 0.18171 | 0.074612 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2501.25 | 121.1884 | -0.21057 | 121.1151 | 0.034862 | -0.054257 | 0.006315 | -0.052488 | 0.082044 | 0.048956 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.11552 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 0.24543 | 0.15631 | 0.21689 | 0.15808 | 0.29262 | 0.25953 | 0.14785 | 0.061642 | 0.17079 | 0.027826 | -0.097212 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.018639 | 0.067659 | -0.052455 | 0.033843
2502.9375 | 121.2433 | -0.20142 | 121.106 | 0.044018 | -0.063415 | 0.006315 | -0.047909 | 0.072888 | 0.039799 | -0.058139 | 0.043331 | 0.1479 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 0.24543 | 0.138 | 0.20773 | 0.15351 | 0.2743 | 0.24122 | 0.14328 | 0.061642 | 0.16621 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.047877 | 0.033843
2504.6875 | 121.3165 | -0.1831 | 121.1014 | 0.03944 | -0.067994 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11552 | 0.057392 | 0.064423 | -0.024328 | 0.019719 | 0.22254 | 0.11511 | 0.18484 | 0.1352 | 0.26515 | 0.22748 | 0.12039 | 0.057063 | 0.17537 | 0.027826 | -0.097212 | 0.075703 | 0.082734 | -0.006017 | 0.03803 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2506.4375 | 121.2021 | -0.20142 | 121.1426 | 0.030283 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.15248 | 0.009515 | -0.10179 | 0.052814 | 0.064423 | -0.024328 | 0.015141 | 0.2317 | 0.14258 | 0.19857 | 0.15351 | 0.27888 | 0.24122 | 0.13412 | 0.057063 | 0.17079 | 0.027826 | -0.083475 | 0.071125 | 0.082734 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2508.125 | 121.3028 | -0.16022 | 121.0876 | 0.034862 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.15248 | 0.000359 | -0.11094 | 0.048236 | 0.059844 | -0.019749 | 0.015141 | 0.19508 | 0.096802 | 0.16195 | 0.11689 | 0.23768 | 0.20002 | 0.092922 | 0.052485 | 0.17079 | 0.01867 | -0.092633 | 0.066547 | 0.078155 | -0.001438 | 0.033452 | -0.014062 | 0.053923 | -0.047877 | 0.020108
2509.8125 | 121.3852 | -0.16479 | 121.0876 | 0.03944 | -0.058836 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.062717 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 0.20423 | 0.10596 | 0.16653 | 0.11231 | 0.23768 | 0.20459 | 0.10208 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.023218 | 0.058502 | -0.043298 | 0.038422
2511.5625 | 121.2616 | -0.21515 | 121.1517 | 0.03944 | -0.058836 | 0.006315 | -0.047909 | 0.077466 | 0.044377 | -0.071874 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 0.25459 | 0.15631 | 0.22146 | 0.16724 | 0.29262 | 0.25953 | 0.14328 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.043298 | 0.038422
2513.25 | 121.2891 | -0.19226 | 121.1609 | 0.03944 | -0.067994 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.014094 | -0.10179 | 0.048236 | 0.059844 | -0.019749 | 0.010563 | 0.2317 | 0.12427 | 0.194 | 0.14435 | 0.26973 | 0.23664 | 0.12497 | 0.061642 | 0.17079 | 0.032405 | -0.083475 | 0.066547 | 0.078155 | -0.001438 | 0.028874 | -0.004905 | 0.06308 | -0.034142 | 0.033843
2515 | 121.2982 | -0.18768 | 121.1838 | 0.044018 | -0.063415 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.019719 | 0.2317 | 0.12427 | 0.18942 | 0.13977 | 0.26973 | 0.22748 | 0.12497 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.03803 | -0.01864 | 0.053923 | -0.043298 | 0.029265
2516.6875 | 121.3074 | -0.20599 | 121.1655 | 0.03944 | -0.054257 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.058139 | 0.047909 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.055266 | -0.019749 | 0.015141 | 0.24543 | 0.15174 | 0.20773 | 0.15809 | 0.28804 | 0.24579 | 0.14786 | 0.06622 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.073577 | -0.001438 | 0.033452 | -0.009483 | 0.067658 | -0.047877 | 0.029264
2518.4375 | 121.344 | -0.16937 | 121.1517 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.052814 | 0.055266 | -0.024328 | 0.019719 | 0.20881 | 0.11054 | 0.17111 | 0.12146 | 0.24226 | 0.21375 | 0.10208 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.071125 | 0.073577 | -0.006017 | 0.03803 | -0.014062 | 0.06308 | -0.047877 | 0.029265
2520.125 | 121.4081 | -0.16937 | 121.1563 | 0.044018 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.015141 | 0.21339 | 0.11054 | 0.16653 | 0.12604 | 0.24684 | 0.20917 | 0.10208 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.033452 | -0.009483 | 0.067659 | -0.043299 | 0.033843
2521.875 | 121.2845 | -0.20599 | 121.1838 | 0.034862 | -0.054257 | 0.001736 | -0.043331 | 0.082044 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.11094 | 0.057392 | 0.059844 | -0.028906 | 0.015141 | 0.24086 | 0.15174 | 0.20773 | 0.16266 | 0.28804 | 0.25495 | 0.14328 | 0.057063 | 0.17079 | 0.023248 | -0.092633 | 0.075703 | 0.078155 | -0.010595 | 0.033452 | -0.01864 | 0.067658 | -0.052455 | 0.033843
2523.6094 | 121.344 | -0.17853 | 121.1609 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.043331 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.019719 | 0.21797 | 0.11969 | 0.18026 | 0.13062 | 0.25599 | 0.21833 | 0.11123 | 0.061642 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.03803 | -0.009483 | 0.06308 | -0.043299 | 0.029264
2525.3594 | 121.4218 | -0.15564 | 121.17 | 0.044018 | -0.058836 | -0.002842 | -0.057066 | 0.072888 | 0.044377 | -0.062717 | 0.047909 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.059844 | -0.024328 | 0.015141 | 0.19966 | 0.096804 | 0.1528 | 0.098574 | 0.22853 | 0.20002 | 0.092923 | 0.06622 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.072237 | -0.052455 | 0.033843
2527.0469 | 121.4035 | -0.16479 | 121.1792 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.072888 | 0.035221 | -0.062717 | 0.043331 | 0.15248 | -0.004219 | -0.10179 | 0.052814 | 0.055266 | -0.028906 | 0.015141 | 0.19966 | 0.10596 | 0.16195 | 0.11689 | 0.23768 | 0.20002 | 0.10208 | 0.061642 | 0.17079 | 0.014092 | -0.083475 | 0.071125 | 0.073577 | -0.010595 | 0.033452 | -0.009483 | 0.072237 | -0.057033 | 0.024687
2528.7969 | 121.3211 | -0.21973 | 121.225 | 0.03944 | -0.063415 | -0.007421 | -0.047909 | 0.077466 | 0.048956 | -0.053561 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.019719 | 0.25917 | 0.15631 | 0.21231 | 0.17182 | 0.29719 | 0.26868 | 0.16617 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.03803 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2530.5625 | 121.344 | -0.18768 | 121.2021 | 0.030283 | -0.067994 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.062717 | 0.034174 | 0.15706 | 0.009515 | -0.10637 | 0.052814 | 0.059844 | -0.019749 | 0.019719 | 0.21797 | 0.11969 | 0.18942 | 0.13519 | 0.26057 | 0.22748 | 0.12497 | 0.052485 | 0.17537 | 0.027826 | -0.088054 | 0.071125 | 0.078155 | -0.001438 | 0.03803 | -0.01864 | 0.053923 | -0.043299 | 0.029264
2532.3125 | 121.3989 | -0.19684 | 121.2387 | 0.044018 | -0.063415 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.053561 | 0.047909 | 0.15706 | 0.004937 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 0.24086 | 0.13342 | 0.19857 | 0.14893 | 0.27888 | 0.23664 | 0.14328 | 0.06622 | 0.17537 | 0.023248 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.009483 | 0.067658 | -0.052455 | 0.024686
2534 | 121.3898 | -0.19226 | 121.225 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.066548 | 0.059844 | -0.028906 | 0.019719 | 0.22712 | 0.13342 | 0.18942 | 0.14435 | 0.27431 | 0.23664 | 0.13412 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.084859 | 0.078155 | -0.010595 | 0.03803 | -0.027796 | 0.067658 | -0.057033 | 0.038421
2535.6875 | 121.431 | -0.16479 | 121.2067 | 0.034862 | -0.063415 | -0.002842 | -0.057066 | 0.072888 | 0.039799 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.010563 | 0.19966 | 0.10138 | 0.16195 | 0.10773 | 0.23768 | 0.20459 | 0.0975 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.028874 | -0.014062 | 0.058501 | -0.043299 | 0.029264
2537.4375 | 121.4401 | -0.19684 | 121.2021 | 0.034862 | -0.058836 | -0.002842 | -0.052488 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 0.2317 | 0.138 | 0.194 | 0.14435 | 0.2743 | 0.23664 | 0.12954 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.052455 | 0.029264
2539.125 | 121.4447 | -0.17395 | 121.2433 | 0.03944 | -0.063415 | 0.001736 | -0.057066 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.015141 | 0.21339 | 0.11053 | 0.17569 | 0.11688 | 0.25142 | 0.21833 | 0.11123 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2540.8125 | 120.8176 | -0.21515 | 120.7443 | 0.044018 | -0.049678 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.010563 | 0.25917 | 0.16547 | 0.22146 | 0.16724 | 0.28804 | 0.25953 | 0.15243 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.028874 | -0.018639 | 0.067659 | -0.052455 | 0.033843
2542.5625 | 120.9915 | -0.1831 | 120.9045 | 0.03944 | -0.058836 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.048983 | 0.038752 | 0.15248 | 0.009515 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.015141 | 0.22254 | 0.12427 | 0.18942 | 0.13977 | 0.26515 | 0.2229 | 0.13412 | 0.057063 | 0.17079 | 0.027826 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2544.2656 | 121.1884 | -0.14191 | 120.8908 | 0.03944 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.039799 | -0.058139 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.055266 | -0.015171 | 0.015141 | 0.18135 | 0.083071 | 0.13906 | 0.093998 | 0.22395 | 0.18171 | 0.083768 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.073577 | 0.00314 | 0.033452 | -0.014062 | 0.053923 | -0.043299 | 0.024686
2546.0312 | 121.0831 | -0.18768 | 121.0098 | 0.034862 | -0.058836 | -0.002842 | -0.043331 | 0.086622 | 0.039799 | -0.067295 | 0.047909 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.005985 | 0.22254 | 0.12885 | 0.18484 | 0.14435 | 0.27431 | 0.22748 | 0.12039 | 0.06622 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.024296 | -0.009483 | 0.067658 | -0.047877 | 0.029264
2547.7188 | 121.1243 | -0.19226 | 121.0144 | 0.044018 | -0.058836 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.004937 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 0.23628 | 0.13342 | 0.194 | 0.14435 | 0.27431 | 0.23664 | 0.12954 | 0.061642 | 0.17537 | 0.023248 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.052455 | 0.029265
2549.4688 | 121.1517 | -0.20599 | 121.0693 | 0.034862 | -0.058836 | -0.012 | -0.038752 | 0.072888 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.004937 | -0.11094 | 0.06197 | 0.055266 | -0.028906 | 0.010563 | 0.24086 | 0.14716 | 0.19399 | 0.16724 | 0.27888 | 0.25037 | 0.1387 | 0.061642 | 0.17079 | 0.023248 | -0.092633 | 0.080281 | 0.073577 | -0.010595 | 0.028874 | -0.018639 | 0.072237 | -0.057033 | 0.033843
2551.1719 | 121.2433 | -0.16937 | 121.051 | 0.044018 | -0.067994 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 0.21339 | 0.10138 | 0.17111 | 0.12146 | 0.24684 | 0.20917 | 0.10666 | 0.061642 | 0.17995 | 0.032405 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.014061 | 0.067659 | -0.043298 | 0.038422
2552.9219 | 121.2799 | -0.14648 | 121.0556 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11552 | 0.048236 | 0.064423 | -0.028906 | 0.019719 | 0.18135 | 0.087648 | 0.14364 | 0.098575 | 0.22395 | 0.18628 | 0.083767 | 0.057063 | 0.17537 | 0.032405 | -0.097212 | 0.066547 | 0.082734 | -0.010595 | 0.03803 | -0.009484 | 0.067658 | -0.034142 | 0.043
2554.6875 | 120.4056 | -5.2185 | 115.1596 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.004937 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.005985 | 5.2579 | 5.1597 | 5.2202 | 5.1706 | 5.3005 | 5.2583 | 5.1558 | 0.057063 | 0.17537 | 0.023248 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.024296 | -0.01864 | 0.06308 | -0.052455 | 0.029265
2556.375 | 120.6162 | -6.5094 | 115.2878 | 0.034862 | -0.063415 | 0.001736 | -0.043331 | 0.082044 | 0.048956 | -0.058139 | 0.043331 | 0.15706 | 0.009515 | -0.11552 | 0.048236 | 0.055266 | -0.024328 | 0.005985 | 6.5443 | 6.446 | 6.5111 | 6.4661 | 6.5914 | 6.5584 | 6.4513 | 0.061642 | 0.17537 | 0.027826 | -0.097212 | 0.066547 | 0.073577 | -0.006017 | 0.024296 | -0.004905 | 0.067659 | -0.038721 | 0.033843
2558.125 | 120.6802 | -6.6605 | 114.0427 | 0.03944 | -0.054257 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.055266 | -0.028906 | 0.015141 | 6.6999 | 6.6062 | 6.6576 | 6.6126 | 6.7379 | 6.7048 | 6.5977 | 0.061642 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.073577 | -0.010595 | 0.033452 | -0.014061 | 0.072237 | -0.043298 | 0.043
2559.875 | 120.8176 | -7.0312 | 113.6719 | 0.044018 | -0.058836 | 0.001736 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.047909 | 0.15706 | 0.014094 | -0.11552 | 0.048236 | 0.055266 | -0.019749 | 0.010563 | 7.0753 | 6.9724 | 7.033 | 6.9833 | 7.1041 | 7.0756 | 6.9685 | 0.06622 | 0.17537 | 0.032405 | -0.097212 | 0.066547 | 0.073577 | -0.001438 | 0.028874 | -0.000327 | 0.067658 | -0.034142 | 0.033843
2561.5469 | 120.7397 | -6.7337 | 114.1159 | 0.044018 | -0.058836 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 6.7777 | 6.6749 | 6.74 | 6.6904 | 6.8157 | 6.7781 | 6.671 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.03872 | 0.038422
2563.2969 | 120.8359 | -6.0287 | 114.8163 | 0.034862 | -0.058836 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.10179 | 0.052814 | 0.055266 | -0.028906 | 0.015141 | 6.0636 | 5.9699 | 6.0305 | 5.9808 | 6.1108 | 6.0731 | 5.966 | 0.061642 | 0.17079 | 0.027826 | -0.083475 | 0.071125 | 0.073577 | -0.010595 | 0.033452 | -0.009483 | 0.072237 | -0.043299 | 0.038421
2564.9844 | 120.7855 | -6.8436 | 114.0427 | 0.03944 | -0.063415 | 0.001736 | -0.047909 | 0.086622 | 0.044377 | -0.062717 | 0.047909 | 0.1479 | 0.014094 | -0.10637 | 0.06197 | 0.055266 | -0.019749 | 0.015141 | 6.883 | 6.7802 | 6.8453 | 6.7957 | 6.9302 | 6.8879 | 6.7809 | 0.06622 | 0.16621 | 0.032405 | -0.088054 | 0.080281 | 0.073577 | -0.001438 | 0.033452 | -0.014061 | 0.067658 | -0.047876 | 0.033843
2566.7344 | 120.8221 | -7.3517 | 113.5803 | 0.044018 | -0.054257 | 0.006315 | -0.052488 | 0.077466 | 0.039799 | -0.062717 | 0.047909 | 0.15706 | 0.009515 | -0.11552 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 7.3957 | 7.2974 | 7.358 | 7.2992 | 7.4292 | 7.3915 | 7.289 | 0.06622 | 0.17537 | 0.027826 | -0.097212 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.009483 | 0.067658 | -0.047877 | 0.029264
2568.4844 | 120.8588 | -7.4203 | 113.5529 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.048956 | -0.062717 | 0.047909 | 0.16164 | 0.014094 | -0.12468 | 0.048236 | 0.055266 | -0.015171 | 0.010563 | 7.4598 | 7.3615 | 7.4221 | 7.377 | 7.4978 | 7.4693 | 7.3576 | 0.06622 | 0.17995 | 0.032405 | -0.10637 | 0.066547 | 0.073577 | 0.00314 | 0.028874 | -0.000327 | 0.06308 | -0.034142 | 0.029265
2570.1719 | 120.9 | -7.3151 | 113.6581 | 0.044018 | -0.058836 | -0.002842 | -0.038752 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.004937 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.019719 | 7.3591 | 7.2562 | 7.3122 | 7.2763 | 7.3971 | 7.3594 | 7.2523 | 0.061642 | 0.17079 | 0.023248 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.03803 | -0.014061 | 0.067659 | -0.052455 | 0.029265
2571.875 | 121.0144 | -7.1594 | 113.7497 | 0.044018 | -0.049678 | 0.001736 | -0.038752 | 0.072888 | 0.039799 | -0.062717 | 0.038752 | 0.16164 | 0.000359 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.005985 | 7.2034 | 7.1097 | 7.1612 | 7.1207 | 7.2323 | 7.1992 | 7.0967 | 0.057063 | 0.17995 | 0.01867 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.024296 | -0.01864 | 0.058501 | -0.057033 | 0.020108
2573.6406 | 120.9869 | -7.0679 | 113.9099 | 0.048597 | -0.049678 | 0.010893 | -0.047909 | 0.072888 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.048236 | 0.055266 | -0.019749 | 0.010563 | 7.1165 | 7.0182 | 7.0788 | 7.02 | 7.1408 | 7.1077 | 7.0052 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.066547 | 0.073577 | -0.001438 | 0.028874 | -0.004905 | 0.06308 | -0.034142 | 0.033843
2575.3906 | 121.0648 | -5.6122 | 115.416 | 0.044018 | -0.058836 | 0.006315 | -0.043331 | 0.077466 | 0.039799 | -0.058139 | 0.043331 | 0.15706 | 0.018672 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 5.6562 | 5.5533 | 5.6185 | 5.5689 | 5.6896 | 5.652 | 5.554 | 0.061642 | 0.17537 | 0.036983 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.014061 | 0.06308 | -0.03872 | 0.038421
2577.1094 | 120.9595 | -6.4957 | 114.5828 | 0.044018 | -0.058836 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 6.5397 | 6.4368 | 6.502 | 6.4523 | 6.5777 | 6.54 | 6.4329 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2578.8594 | 121.0739 | -6.7383 | 114.2715 | 0.044018 | -0.063415 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 6.7823 | 6.6749 | 6.74 | 6.6949 | 6.8112 | 6.7827 | 6.6756 | 0.061642 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2580.5469 | 121.0693 | -6.8893 | 114.1434 | 0.044018 | -0.058836 | -0.002842 | -0.052488 | 0.072888 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.000359 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 6.9334 | 6.8305 | 6.8865 | 6.8369 | 6.9622 | 6.9383 | 6.8266 | 0.057063 | 0.17537 | 0.01867 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.052455 | 0.024687
2582.2969 | 121.1472 | -12.0575 | 108.9203 | 0.048597 | -0.058836 | -0.002842 | -0.043331 | 0.086622 | 0.044377 | -0.062717 | 0.043331 | 0.16164 | 0.004937 | -0.11094 | 0.052814 | 0.055266 | -0.019749 | 0.010563 | 12.1061 | 11.9987 | 12.0547 | 12.0142 | 12.1441 | 12.1019 | 11.9948 | 0.061642 | 0.17995 | 0.023248 | -0.092633 | 0.071125 | 0.073577 | -0.001438 | 0.028874 | -0.009483 | 0.06308 | -0.047877 | 0.024686
2584.0469 | 121.0693 | -9.7366 | 111.3373 | 0.03944 | -0.054257 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.028906 | 0.010563 | 9.7761 | 9.6824 | 9.7384 | 9.6887 | 9.8187 | 9.781 | 9.6785 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.010595 | 0.028874 | -0.014062 | 0.067658 | -0.03872 | 0.043
2585.8125 | 121.0602 | -7.1091 | 114.0427 | 0.044018 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.055266 | -0.028906 | 0.019719 | 7.1531 | 7.0502 | 7.1062 | 7.0657 | 7.1865 | 7.1534 | 7.0509 | 0.061642 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.073577 | -0.010595 | 0.03803 | -0.014061 | 0.072237 | -0.043298 | 0.043
2587.5625 | 121.1884 | -8.4091 | 112.6785 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.072888 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.009515 | -0.11552 | 0.057392 | 0.064423 | -0.015171 | 0.019719 | 8.4486 | 8.3503 | 8.4109 | 8.3658 | 8.482 | 8.4489 | 8.3464 | 0.061642 | 0.17995 | 0.027826 | -0.097212 | 0.075703 | 0.082734 | 0.00314 | 0.03803 | -0.014061 | 0.058502 | -0.047877 | 0.024686
2589.25 | 121.2112 | -6.5598 | 114.4867 | 0.03944 | -0.054257 | -0.002842 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 6.5992 | 6.5055 | 6.5569 | 6.5164 | 6.6418 | 6.6041 | 6.497 | 0.061642 | 0.17995 | 0.032405 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.043298 | 0.033843
2591.0156 | 121.0693 | -8.2718 | 112.9211 | 0.03944 | -0.058836 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.06197 | 0.059844 | -0.028906 | 0.024297 | 8.3112 | 8.213 | 8.2735 | 8.2193 | 8.3493 | 8.3162 | 8.2137 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.080281 | 0.078155 | -0.010595 | 0.042608 | -0.018639 | 0.072237 | -0.052455 | 0.038421
2592.7656 | 121.1334 | -8.2031 | 112.9898 | 0.044018 | -0.058836 | 0.001736 | -0.047909 | 0.082044 | 0.048956 | -0.058139 | 0.043331 | 0.15248 | 0.004937 | -0.10637 | 0.057392 | 0.050688 | -0.019749 | 0.015141 | 8.2471 | 8.1443 | 8.2049 | 8.1552 | 8.2852 | 8.2521 | 8.145 | 0.061642 | 0.17079 | 0.023248 | -0.088054 | 0.075703 | 0.068999 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.052455 | 0.024686
2594.5156 | 121.1975 | -6.958 | 114.1846 | 0.044018 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.052488 | 0.15706 | 0.009515 | -0.11552 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 7.002 | 6.8946 | 6.9597 | 6.9147 | 7.0355 | 6.9978 | 6.8907 | 0.070799 | 0.17537 | 0.027826 | -0.097212 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.000326 | 0.076816 | -0.043299 | 0.033843
2596.2188 | 121.2067 | -6.8985 | 114.2853 | 0.03944 | -0.054257 | 0.010893 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.1479 | 0.014094 | -0.10637 | 0.052814 | 0.064423 | -0.019749 | 0.019719 | 6.9379 | 6.8442 | 6.9094 | 6.8552 | 6.9805 | 6.9429 | 6.8358 | 0.061642 | 0.16621 | 0.032405 | -0.088054 | 0.071125 | 0.082734 | -0.001438 | 0.03803 | -0.009483 | 0.06308 | -0.03872 | 0.033843
2597.9688 | 121.1426 | -5.5023 | 115.7089 | 0.034862 | -0.054257 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.018672 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 5.5372 | 5.4481 | 5.5041 | 5.4544 | 5.5844 | 5.5467 | 5.435 | 0.057063 | 0.17079 | 0.036983 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.043298 | 0.038421
2599.6719 | 121.2524 | -6.6788 | 114.5004 | 0.044018 | -0.063415 | 0.001736 | -0.038752 | 0.082044 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 6.7228 | 6.6154 | 6.6805 | 6.64 | 6.7608 | 6.7186 | 6.6115 | 0.061642 | 0.17079 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.009483 | 0.06308 | -0.03872 | 0.033843
2601.4219 | 121.1243 | -6.2393 | 115.0452 | 0.03944 | -0.054257 | 0.001736 | -0.043331 | 0.082044 | 0.039799 | -0.058139 | 0.043331 | 0.16164 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 6.2788 | 6.1851 | 6.2411 | 6.196 | 6.3214 | 6.2791 | 6.1812 | 0.061642 | 0.17995 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.009483 | 0.06308 | -0.03872 | 0.033843
2603.1719 | 121.3028 | -6.5048 | 114.6744 | 0.03944 | -0.058836 | 0.006315 | -0.052488 | 0.086622 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.018672 | -0.10637 | 0.052814 | 0.059844 | -0.019749 | 0.015141 | 6.5443 | 6.446 | 6.5111 | 6.4523 | 6.5914 | 6.5492 | 6.4375 | 0.061642 | 0.17537 | 0.036983 | -0.088054 | 0.071125 | 0.078155 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.034142 | 0.038421
2604.9219 | 121.2845 | -6.459 | 114.7385 | 0.044018 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.048956 | -0.071874 | 0.047909 | 0.15706 | 0.009515 | -0.10637 | 0.052814 | 0.064423 | -0.028906 | 0.015141 | 6.5031 | 6.4002 | 6.4608 | 6.4157 | 6.5411 | 6.508 | 6.3872 | 0.06622 | 0.17537 | 0.027826 | -0.088054 | 0.071125 | 0.082734 | -0.010595 | 0.033452 | -0.004905 | 0.076815 | -0.043299 | 0.038421
2606.6094 | 121.2296 | -6.2393 | 114.9811 | 0.044018 | -0.058836 | -0.002842 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.004937 | -0.11094 | 0.043657 | 0.064423 | -0.019749 | 0.019719 | 6.2833 | 6.1805 | 6.2365 | 6.196 | 6.3214 | 6.2837 | 6.1766 | 0.057063 | 0.17537 | 0.023248 | -0.092633 | 0.061968 | 0.082734 | -0.001438 | 0.03803 | -0.004905 | 0.058501 | -0.03872 | 0.024686
2608.3594 | 121.2799 | -5.7861 | 115.4388 | 0.034862 | -0.063415 | -0.002842 | -0.047909 | 0.06831 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 5.821 | 5.7227 | 5.7833 | 5.7382 | 5.8544 | 5.8259 | 5.7188 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.047877 | 0.029264
2610.1094 | 121.225 | -5.8594 | 115.4022 | 0.048597 | -0.063415 | 0.006315 | -0.052488 | 0.072888 | 0.035221 | -0.058139 | 0.043331 | 0.15248 | 0.009515 | -0.11552 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 5.908 | 5.796 | 5.8657 | 5.8069 | 5.9323 | 5.8946 | 5.8012 | 0.061642 | 0.17079 | 0.027826 | -0.097212 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.009483 | 0.06308 | -0.043299 | 0.029264
2611.875 | 121.3211 | -6.8848 | 114.3631 | 0.034862 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.058139 | 0.034174 | 0.15248 | 0.004937 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 6.9196 | 6.8259 | 6.8819 | 6.8414 | 6.9622 | 6.9291 | 6.8266 | 0.052485 | 0.17079 | 0.023248 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.023218 | 0.058502 | -0.052455 | 0.029265
2613.6094 | 121.2112 | -6.1661 | 115.1459 | 0.044018 | -0.054257 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.047909 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 6.2101 | 6.1118 | 6.1632 | 6.1182 | 6.2435 | 6.2059 | 6.0988 | 0.06622 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.009483 | 0.067658 | -0.043298 | 0.033843
2615.3125 | 121.3394 | -6.015 | 115.2374 | 0.034862 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 6.0499 | 5.9516 | 6.0168 | 5.9717 | 6.0925 | 6.0548 | 5.9523 | 0.061642 | 0.17995 | 0.032405 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.018639 | 0.06308 | -0.047876 | 0.033843
2617.0625 | 121.2479 | -6.2576 | 115.0909 | 0.034862 | -0.058836 | 0.006315 | -0.047909 | 0.077466 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 6.2925 | 6.1988 | 6.2639 | 6.2097 | 6.3351 | 6.2974 | 6.1949 | 0.061642 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.043298 | 0.038422
2618.75 | 121.3394 | -6.0974 | 115.1367 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.072888 | 0.039799 | -0.067295 | 0.043331 | 0.15706 | 0.018672 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 6.1323 | 6.0386 | 6.0946 | 6.0495 | 6.1703 | 6.1372 | 6.0301 | 0.061642 | 0.17537 | 0.036983 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.014061 | 0.06308 | -0.03872 | 0.038421
2620.5 | 121.312 | -6.3034 | 115.036 | 0.044018 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.039799 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.057392 | 0.069001 | -0.015171 | 0.010563 | 6.3474 | 6.2446 | 6.3006 | 6.2555 | 6.3854 | 6.3432 | 6.2453 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.075703 | 0.087312 | 0.00314 | 0.028874 | -0.01864 | 0.053923 | -0.043298 | 0.029265
2622.25 | 121.3074 | -6.7062 | 114.6332 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.06197 | 0.059844 | -0.024328 | 0.015141 | 6.7457 | 6.6474 | 6.708 | 6.6583 | 6.7837 | 6.7552 | 6.6435 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.080281 | 0.078155 | -0.006017 | 0.033452 | -0.018639 | 0.067659 | -0.052455 | 0.033843
2623.9375 | 121.3348 | -6.6238 | 114.6835 | 0.03944 | -0.054257 | 0.001736 | -0.047909 | 0.077466 | 0.039799 | -0.062717 | 0.047909 | 0.15248 | 0.009515 | -0.11552 | 0.057392 | 0.055266 | -0.019749 | 0.010563 | 6.6633 | 6.5696 | 6.6256 | 6.5759 | 6.7013 | 6.6636 | 6.5611 | 0.06622 | 0.17079 | 0.027826 | -0.097212 | 0.075703 | 0.073577 | -0.001438 | 0.028874 | -0.009483 | 0.067658 | -0.047877 | 0.029264
2625.7031 | 121.2891 | -6.4362 | 114.9536 | 0.03944 | -0.058836 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.058139 | 0.034174 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 6.4756 | 6.3773 | 6.4425 | 6.3882 | 6.509 | 6.4805 | 6.378 | 0.052485 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.023218 | 0.058502 | -0.047877 | 0.033843
2627.4062 | 121.2753 | -6.4041 | 114.9673 | 0.048597 | -0.054257 | 0.006315 | -0.047909 | 0.072888 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.005985 | 6.4527 | 6.3499 | 6.4104 | 6.3562 | 6.477 | 6.4485 | 6.346 | 0.057063 | 0.17995 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.024296 | -0.01864 | 0.058501 | -0.047877 | 0.029264
2629.1719 | 121.3165 | -6.6376 | 114.7797 | 0.034862 | -0.054257 | 0.006315 | -0.038752 | 0.086622 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 6.6724 | 6.5833 | 6.6439 | 6.5988 | 6.7242 | 6.6819 | 6.5703 | 0.061642 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.043298 | 0.033843
2630.875 | 121.2845 | -10.2402 | 111.1084 | 0.044018 | -0.054257 | -0.002842 | -0.043331 | 0.077466 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.055266 | -0.028906 | 0.015141 | 10.2842 | 10.1859 | 10.2373 | 10.1968 | 10.3176 | 10.2891 | 10.1775 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.073577 | -0.010595 | 0.033452 | -0.01864 | 0.067658 | -0.043298 | 0.043
2632.625 | 121.4355 | -9.6909 | 111.6074 | 0.044018 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.044377 | -0.058139 | 0.043331 | 0.16164 | 0.014094 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 9.7349 | 9.632 | 9.688 | 9.6429 | 9.7729 | 9.7352 | 9.6327 | 0.061642 | 0.17995 | 0.032405 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.018639 | 0.06308 | -0.047876 | 0.033843
2634.3125 | 121.3623 | -8.963 | 112.3856 | 0.030283 | -0.058836 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.047909 | 0.16164 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.028906 | 0.019719 | 8.9933 | 8.9042 | 8.9647 | 8.9151 | 9.0405 | 9.0074 | 8.9003 | 0.06622 | 0.17995 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.010595 | 0.03803 | -0.004905 | 0.076815 | -0.03872 | 0.043
2636.0781 | 121.3623 | -7.4615 | 113.9053 | 0.034862 | -0.058836 | 0.006315 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.16164 | 0.018672 | -0.1201 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 7.4964 | 7.4027 | 7.4679 | 7.4182 | 7.5436 | 7.5059 | 7.3988 | 0.057063 | 0.17995 | 0.036983 | -0.10179 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.03872 | 0.038421
2637.7656 | 121.431 | -6.4911 | 114.8254 | 0.044018 | -0.049678 | 0.001736 | -0.052488 | 0.072888 | 0.039799 | -0.067295 | 0.043331 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.055266 | -0.024328 | 0.005985 | 6.5351 | 6.4414 | 6.4928 | 6.4386 | 6.564 | 6.5309 | 6.4238 | 0.061642 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.073577 | -0.006017 | 0.024296 | -0.014061 | 0.067659 | -0.047877 | 0.033843
2639.5156 | 121.376 | -7.0129 | 114.3951 | 0.044018 | -0.063415 | 0.006315 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.02325 | -0.11552 | 0.057392 | 0.055266 | -0.024328 | 0.019719 | 7.057 | 6.9495 | 7.0193 | 6.9696 | 7.0904 | 7.0573 | 6.9502 | 0.057063 | 0.17537 | 0.041561 | -0.097212 | 0.075703 | 0.073577 | -0.006017 | 0.03803 | -0.01864 | 0.06308 | -0.034142 | 0.047578
2641.2656 | 120.7901 | -120.1538 | 0.56763 | 0.085224 | -0.022205 | 0.038365 | -0.011281 | 0.10951 | 0.085583 | -0.03067 | 0.079959 | 0.19369 | 0.041563 | -0.12468 | 0.039079 | 0.02322 | -0.033484 | -0.00775 | 120.239 | 120.1316 | 120.1922 | 120.1425 | 120.2633 | 120.2394 | 120.1231 | 0.09827 | 0.212 | 0.059874 | -0.10637 | 0.05739 | 0.041531 | -0.015173 | 0.010561 | 0.04088 | 0.11344 | 0.002484 | 0.075047
2642.9531 | 120.932 | -118.7897 | 2.1469 | 0.071489 | -0.031363 | 0.042944 | -0.006703 | 0.11867 | 0.085583 | -0.026092 | 0.079959 | 0.19827 | 0.041563 | -0.12926 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 118.8612 | 118.7583 | 118.8326 | 118.783 | 118.9083 | 118.8753 | 118.7636 | 0.09827 | 0.21658 | 0.059874 | -0.11095 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.01164 | 0.084204
2644.7031 | 121.4447 | -76.5244 | 44.2017 | 0.071489 | -0.031363 | 0.029208 | -0.025017 | 0.10951 | 0.067269 | -0.039826 | 0.070802 | 0.18453 | 0.036985 | -0.12468 | 0.052814 | 0.027798 | -0.033484 | 0.001406 | 76.5958 | 76.493 | 76.5536 | 76.4993 | 76.6339 | 76.5916 | 76.4845 | 0.089113 | 0.20284 | 0.055296 | -0.10637 | 0.071125 | 0.046109 | -0.015173 | 0.019717 | 0.017988 | 0.10429 | -0.015829 | 0.070469
2646.4688 | 95.0912 | -5.9418 | 89.1174 | 0.034862 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.034174 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.055266 | -0.010593 | 0.015141 | 5.9766 | 5.8784 | 5.9389 | 5.8939 | 6.0192 | 5.9861 | 5.8791 | 0.052485 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.073577 | 0.007718 | 0.033452 | -0.023218 | 0.044767 | -0.043298 | 0.024687
2648.1719 | 119.0323 | -79.9393 | 38.887 | 0.053175 | -0.049678 | 0.015472 | -0.01586 | 0.095778 | 0.067269 | -0.044405 | 0.057066 | 0.16622 | 0.027829 | -0.11552 | 0.080283 | 0.027798 | -0.024328 | 0.005985 | 79.9924 | 79.8896 | 79.9547 | 79.9234 | 80.035 | 80.0065 | 79.8949 | 0.075377 | 0.18453 | 0.04614 | -0.097212 | 0.098594 | 0.046109 | -0.006017 | 0.024296 | -0.023217 | 0.081394 | -0.052454 | 0.052157
2649.9219 | 120.7352 | -118.0481 | 2.3895 | 0.085224 | -0.017627 | 0.038365 | -0.006703 | 0.11867 | 0.081005 | -0.021514 | 0.079959 | 0.19827 | 0.046142 | -0.12468 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 118.1333 | 118.0305 | 118.0865 | 118.0414 | 118.1668 | 118.1291 | 118.0266 | 0.09827 | 0.21658 | 0.064453 | -0.10637 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.016219 | 0.093362
2651.6719 | 120.1492 | -4.3396 | 105.9814 | 0.030283 | -0.063415 | -0.007421 | -0.052488 | 0.072888 | 0.035221 | -0.071874 | 0.034174 | 0.14332 | 0.014094 | -0.10637 | 0.066548 | 0.073579 | -0.010593 | 0.010563 | 4.3699 | 4.2762 | 4.3322 | 4.2871 | 4.4125 | 4.3748 | 4.2677 | 0.052485 | 0.16163 | 0.032405 | -0.088054 | 0.084859 | 0.09189 | 0.007718 | 0.028874 | -0.032374 | 0.044767 | -0.052454 | 0.024687
2653.3594 | 120.607 | -3.6484 | 117.1188 | 0.034862 | -0.067994 | -0.002842 | -0.057066 | 0.072888 | 0.035221 | -0.08103 | 0.029595 | 0.1479 | -0.004219 | -0.10637 | 0.066548 | 0.069001 | -0.019749 | 0.024297 | 3.6832 | 3.5804 | 3.6455 | 3.5913 | 3.7213 | 3.6836 | 3.5673 | 0.047906 | 0.16621 | 0.014092 | -0.088054 | 0.084859 | 0.087312 | -0.001438 | 0.042608 | -0.036953 | 0.049344 | -0.070767 | 0.01553
2655.1094 | 96.4096 | -4.2068 | 107.4463 | 0.021127 | -0.063415 | -0.002842 | -0.052488 | 0.072888 | 0.035221 | -0.067295 | 0.034174 | 0.1479 | 0.000359 | -0.11552 | 0.06197 | 0.064423 | -0.024328 | 0.019719 | 4.228 | 4.1434 | 4.204 | 4.1544 | 4.2797 | 4.2421 | 4.1396 | 0.052485 | 0.16621 | 0.01867 | -0.097212 | 0.080281 | 0.082734 | -0.006017 | 0.03803 | -0.027796 | 0.058502 | -0.061611 | 0.024687
2656.8594 | 98.4879 | -5.2643 | 114.8575 | 0.034862 | -0.063415 | 0.001736 | -0.052488 | 0.077466 | 0.026064 | -0.067295 | 0.034174 | 0.13874 | 0.009515 | -0.10637 | 0.057392 | 0.069001 | -0.015171 | 0.019719 | 5.2991 | 5.2009 | 5.266 | 5.2118 | 5.3417 | 5.2903 | 5.197 | 0.052485 | 0.15705 | 0.027826 | -0.088054 | 0.075703 | 0.087312 | 0.00314 | 0.03803 | -0.023218 | 0.049345 | -0.047877 | 0.024686
2658.6094 | 120.4147 | -18.663 | 101.6006 | 0.03944 | -0.054257 | -0.002842 | -0.047909 | 0.082044 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.055266 | -0.019749 | 0.010563 | 18.7025 | 18.6088 | 18.6602 | 18.6151 | 18.7451 | 18.7074 | 18.5957 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.073577 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.047877 | 0.029264
2660.3594 | 120.5521 | -14.8727 | 105.2673 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.004937 | -0.10637 | 0.06197 | 0.069001 | -0.019749 | 0.015141 | 14.9076 | 14.8139 | 14.8699 | 14.8248 | 14.9456 | 14.9171 | 14.81 | 0.057063 | 0.17537 | 0.023248 | -0.088054 | 0.080281 | 0.087312 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.057033 | 0.024686
2662.125 | 91.3559 | -14.4424 | 80.983 | 0.03944 | -0.063415 | 0.001736 | -0.038752 | 0.082044 | 0.044377 | -0.067295 | 0.034174 | 0.15248 | 0.009515 | -0.11094 | 0.06197 | 0.064423 | -0.015171 | 0.019719 | 14.4819 | 14.379 | 14.4442 | 14.4037 | 14.5245 | 14.4868 | 14.3751 | 0.052485 | 0.17079 | 0.027826 | -0.092633 | 0.080281 | 0.082734 | 0.00314 | 0.03803 | -0.027796 | 0.049345 | -0.052455 | 0.024686
2663.8125 | 95.3934 | -14.4516 | 91.2323 | 0.044018 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.035221 | -0.058139 | 0.038752 | 0.15248 | 0.009515 | -0.10637 | 0.052814 | 0.055266 | -0.015171 | 0.019719 | 14.4956 | 14.3882 | 14.4488 | 14.4037 | 14.5291 | 14.4868 | 14.3935 | 0.057063 | 0.17079 | 0.027826 | -0.088054 | 0.071125 | 0.073577 | 0.00314 | 0.03803 | -0.014062 | 0.053923 | -0.043299 | 0.024686
2665.5625 | 120.9686 | -15.7745 | 105.0888 | 0.03944 | -0.063415 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.015171 | 0.015141 | 15.814 | 15.7111 | 15.7763 | 15.722 | 15.852 | 15.8143 | 15.7072 | 0.052485 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | 0.00314 | 0.033452 | -0.01864 | 0.049345 | -0.043299 | 0.024686
2667.3281 | 120.195 | -17.2211 | 103.0701 | 0.034862 | -0.067994 | 0.006315 | -0.047909 | 0.082044 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.018672 | -0.11094 | 0.06197 | 0.055266 | -0.028906 | 0.010563 | 17.2559 | 17.1531 | 17.2274 | 17.1732 | 17.3031 | 17.2609 | 17.1538 | 0.061642 | 0.17079 | 0.036983 | -0.092633 | 0.080281 | 0.073577 | -0.010595 | 0.028874 | -0.018639 | 0.072237 | -0.043298 | 0.047578
2669.0156 | 120.845 | -16.8137 | 104.1046 | 0.034862 | -0.058836 | 0.001736 | -0.052488 | 0.072888 | 0.035221 | -0.062717 | 0.034174 | 0.16164 | 0.000359 | -0.10179 | 0.06197 | 0.064423 | -0.015171 | 0.015141 | 16.8485 | 16.7548 | 16.8154 | 16.7612 | 16.8865 | 16.8489 | 16.7509 | 0.052485 | 0.17995 | 0.01867 | -0.083475 | 0.080281 | 0.082734 | 0.00314 | 0.033452 | -0.027796 | 0.049345 | -0.061611 | 0.01553
2670.7812 | 121.1334 | -18.3975 | 102.5391 | 0.030283 | -0.058836 | 0.006315 | -0.043331 | 0.072888 | 0.035221 | -0.067295 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.052814 | 0.064423 | -0.019749 | 0.019719 | 18.4278 | 18.3387 | 18.4038 | 18.3542 | 18.4704 | 18.4327 | 18.3302 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.071125 | 0.082734 | -0.001438 | 0.03803 | -0.014062 | 0.058501 | -0.03872 | 0.033843
2672.5625 | 120.4926 | -18.8141 | 102.2278 | 0.03944 | -0.058836 | 0.006315 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.038752 | 0.1479 | 0.014094 | -0.11552 | 0.052814 | 0.064423 | -0.024328 | 0.019719 | 18.8535 | 18.7553 | 18.8204 | 18.7708 | 18.8961 | 18.8539 | 18.7514 | 0.057063 | 0.16621 | 0.032405 | -0.097212 | 0.071125 | 0.082734 | -0.006017 | 0.03803 | -0.014062 | 0.06308 | -0.03872 | 0.038422
2674.25 | 104.4937 | -17.2028 | 102.8961 | 0.03944 | -0.063415 | 0.010893 | -0.038752 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.015141 | 17.2422 | 17.1393 | 17.2137 | 17.164 | 17.2802 | 17.2471 | 17.1446 | 0.061642 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.033452 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2676.0156 | 120.7764 | -17.2623 | 103.5004 | 0.03944 | -0.063415 | 0.001736 | -0.047909 | 0.082044 | 0.035221 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.12468 | 0.057392 | 0.059844 | -0.024328 | 0.010563 | 17.3017 | 17.1989 | 17.264 | 17.2144 | 17.3443 | 17.2975 | 17.195 | 0.057063 | 0.17537 | 0.027826 | -0.10637 | 0.075703 | 0.078155 | -0.006017 | 0.028874 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2677.7031 | 121.1792 | -18.924 | 102.0584 | 0.034862 | -0.058836 | 0.001736 | -0.047909 | 0.077466 | 0.035221 | -0.058139 | 0.043331 | 0.15706 | 0.009515 | -0.10179 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 18.9588 | 18.8651 | 18.9257 | 18.876 | 19.0014 | 18.9592 | 18.8658 | 0.061642 | 0.17537 | 0.027826 | -0.083475 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.047877 | 0.033843
2679.4531 | 120.5566 | -19.5648 | 101.0468 | 0.03944 | -0.054257 | 0.006315 | -0.052488 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 19.6043 | 19.5106 | 19.5711 | 19.5123 | 19.6469 | 19.6092 | 19.5021 | 0.061642 | 0.17995 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.043298 | 0.038422
2681.2188 | 121.1655 | -19.7571 | 101.2802 | 0.048597 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.035221 | -0.071874 | 0.038752 | 0.16164 | 0.018672 | -0.11552 | 0.057392 | 0.055266 | -0.028906 | 0.019719 | 19.8057 | 19.6982 | 19.7542 | 19.7092 | 19.8345 | 19.7923 | 19.6852 | 0.057063 | 0.17995 | 0.036983 | -0.097212 | 0.075703 | 0.073577 | -0.010595 | 0.03803 | -0.01864 | 0.067658 | -0.03872 | 0.047578
2682.9688 | 105.1392 | -9.343 | 111.5707 | 0.030283 | -0.063415 | -0.007421 | -0.047909 | 0.072888 | 0.044377 | -0.071874 | 0.034174 | 0.15248 | 0.004937 | -0.10637 | 0.066548 | 0.073579 | -0.024328 | 0.015141 | 9.3732 | 9.2795 | 9.3355 | 9.295 | 9.4158 | 9.3873 | 9.2711 | 0.052485 | 0.17079 | 0.023248 | -0.088054 | 0.084859 | 0.09189 | -0.006017 | 0.033452 | -0.032374 | 0.058502 | -0.061611 | 0.029265
2684.6562 | 121.1197 | -8.5739 | 112.5641 | 0.025705 | -0.063415 | -0.012 | -0.052488 | 0.072888 | 0.030642 | -0.067295 | 0.038752 | 0.15248 | 0.014094 | -0.10179 | 0.066548 | 0.069001 | -0.019749 | 0.019719 | 8.5996 | 8.5105 | 8.5619 | 8.5214 | 8.6468 | 8.6046 | 8.5066 | 0.057063 | 0.17079 | 0.032405 | -0.083475 | 0.084859 | 0.087312 | -0.001438 | 0.03803 | -0.027796 | 0.058501 | -0.052454 | 0.033843
2686.4062 | 121.2524 | -8.1436 | 112.9807 | 0.030283 | -0.063415 | -0.012 | -0.047909 | 0.082044 | 0.044377 | -0.067295 | 0.034174 | 0.1479 | 0.004937 | -0.11094 | 0.066548 | 0.064423 | -0.019749 | 0.028875 | 8.1739 | 8.0802 | 8.1316 | 8.0957 | 8.2257 | 8.188 | 8.0763 | 0.052485 | 0.16621 | 0.023248 | -0.092633 | 0.084859 | 0.082734 | -0.001438 | 0.047186 | -0.032374 | 0.053923 | -0.061611 | 0.024686
2688.1562 | 121.0007 | -7.869 | 113.2507 | 0.030283 | -0.067994 | -0.007421 | -0.052488 | 0.077466 | 0.030642 | -0.071874 | 0.029595 | 0.1479 | 0.009515 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 7.8992 | 7.801 | 7.8615 | 7.8165 | 7.9464 | 7.8996 | 7.7971 | 0.047906 | 0.16621 | 0.027826 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.027797 | 0.049344 | -0.047877 | 0.029264
2689.9062 | 121.0281 | -7.6492 | 113.5574 | 0.034862 | -0.063415 | -0.012 | -0.052488 | 0.06831 | 0.035221 | -0.076452 | 0.034174 | 0.14332 | 0.000359 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.015141 | 7.6841 | 7.5858 | 7.6372 | 7.5967 | 7.7175 | 7.6845 | 7.5728 | 0.052485 | 0.16163 | 0.01867 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.033452 | -0.027796 | 0.049345 | -0.061611 | 0.01553
2691.6562 | 120.7031 | -7.4982 | 113.5712 | 0.025705 | -0.058836 | -0.007421 | -0.047909 | 0.06831 | 0.035221 | -0.071874 | 0.025017 | 0.14332 | 0.000359 | -0.10637 | 0.06197 | 0.069001 | -0.015171 | 0.028875 | 7.5239 | 7.4393 | 7.4907 | 7.4503 | 7.5665 | 7.5334 | 7.4263 | 0.043328 | 0.16163 | 0.01867 | -0.088054 | 0.080281 | 0.087312 | 0.00314 | 0.047186 | -0.036953 | 0.040188 | -0.061611 | 0.01553
2693.3438 | 121.2708 | -7.3517 | 113.768 | 0.025705 | -0.072572 | -0.012 | -0.057066 | 0.077466 | 0.030642 | -0.067295 | 0.034174 | 0.14332 | 0.004937 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.019719 | 7.3774 | 7.2791 | 7.3397 | 7.2946 | 7.4292 | 7.3823 | 7.2844 | 0.052485 | 0.16163 | 0.023248 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.03803 | -0.027796 | 0.053923 | -0.057033 | 0.024686
2695.0938 | 120.5704 | -7.2052 | 113.5803 | 0.030283 | -0.072572 | -0.007421 | -0.047909 | 0.077466 | 0.044377 | -0.071874 | 0.038752 | 0.1479 | 0.004937 | -0.11094 | 0.06197 | 0.069001 | -0.015171 | 0.019719 | 7.2355 | 7.1326 | 7.1978 | 7.1573 | 7.2827 | 7.2496 | 7.1333 | 0.057063 | 0.16621 | 0.023248 | -0.092633 | 0.080281 | 0.087312 | 0.00314 | 0.03803 | -0.023218 | 0.053923 | -0.057033 | 0.020108
2696.7969 | 121.138 | -7.164 | 113.9969 | 0.025705 | -0.067994 | -0.007421 | -0.047909 | 0.06831 | 0.039799 | -0.08103 | 0.038752 | 0.15248 | 0.004937 | -0.11094 | 0.066548 | 0.069001 | -0.019749 | 0.015141 | 7.1897 | 7.096 | 7.1566 | 7.1161 | 7.2323 | 7.2038 | 7.083 | 0.057063 | 0.17079 | 0.023248 | -0.092633 | 0.084859 | 0.087312 | -0.001438 | 0.033452 | -0.027796 | 0.058501 | -0.061611 | 0.024686
2698.5625 | 120.9869 | -7.1777 | 114.0701 | 0.030283 | -0.067994 | -0.007421 | -0.057066 | 0.06831 | 0.026064 | -0.071874 | 0.034174 | 0.14332 | 0.000359 | -0.11094 | 0.06197 | 0.069001 | -0.019749 | 0.015141 | 7.208 | 7.1097 | 7.1703 | 7.1207 | 7.246 | 7.2038 | 7.1059 | 0.052485 | 0.16163 | 0.01867 | -0.092633 | 0.080281 | 0.087312 | -0.001438 | 0.033452 | -0.027796 | 0.053923 | -0.061611 | 0.020108
2700.25 | 121.2158 | -8.6014 | 112.6556 | 0.025705 | -0.072572 | -0.002842 | -0.057066 | 0.06831 | 0.044377 | -0.067295 | 0.038752 | 0.1479 | 0.009515 | -0.11094 | 0.06197 | 0.069001 | -0.019749 | 0.019719 | 8.6271 | 8.5288 | 8.5985 | 8.5443 | 8.6697 | 8.6458 | 8.5341 | 0.057063 | 0.16621 | 0.027826 | -0.092633 | 0.080281 | 0.087312 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.052455 | 0.029264
2702.0156 | 121.2753 | -9.0271 | 112.1429 | 0.030283 | -0.067994 | -0.002842 | -0.057066 | 0.063733 | 0.039799 | -0.067295 | 0.038752 | 0.14332 | 0.004937 | -0.10179 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 9.0574 | 8.9591 | 9.0243 | 8.97 | 9.0908 | 9.0669 | 8.9598 | 0.057063 | 0.16163 | 0.023248 | -0.083475 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.01864 | 0.058501 | -0.052455 | 0.024686
2703.7656 | 121.2067 | -9.6909 | 111.5707 | 0.030283 | -0.067994 | -0.002842 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 0.034174 | 0.14332 | 0.004937 | -0.11094 | 0.066548 | 0.064423 | -0.019749 | 0.019719 | 9.7211 | 9.6229 | 9.688 | 9.6384 | 9.7637 | 9.7307 | 9.619 | 0.052485 | 0.16163 | 0.023248 | -0.092633 | 0.084859 | 0.082734 | -0.001438 | 0.03803 | -0.032374 | 0.053923 | -0.061611 | 0.024686
2705.5156 | 121.2936 | -9.8923 | 111.3007 | 0.025705 | -0.067994 | -0.007421 | -0.057066 | 0.077466 | 0.035221 | -0.071874 | 0.038752 | 0.14332 | 0.004937 | -0.10637 | 0.06197 | 0.069001 | -0.015171 | 0.019719 | 9.918 | 9.8243 | 9.8849 | 9.8352 | 9.9697 | 9.9275 | 9.8204 | 0.057063 | 0.16163 | 0.023248 | -0.088054 | 0.080281 | 0.087312 | 0.00314 | 0.03803 | -0.023218 | 0.053923 | -0.057033 | 0.020108
2707.2344 | 121.2021 | -9.3887 | 111.8774 | 0.030283 | -0.067994 | -0.012 | -0.052488 | 0.072888 | 0.035221 | -0.071874 | 0.034174 | 0.1479 | 0.004937 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.024297 | 9.419 | 9.3207 | 9.3767 | 9.3362 | 9.4616 | 9.424 | 9.3169 | 0.052485 | 0.16621 | 0.023248 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.042608 | -0.027796 | 0.053923 | -0.057033 | 0.024686
2708.9844 | 121.2845 | -9.3887 | 111.8454 | 0.034862 | -0.067994 | -0.002842 | -0.052488 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.06197 | 0.069001 | -0.028906 | 0.019719 | 9.4236 | 9.3207 | 9.3859 | 9.3362 | 9.4662 | 9.4285 | 9.326 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.080281 | 0.087312 | -0.010595 | 0.03803 | -0.023218 | 0.067658 | -0.052455 | 0.038421
2710.7344 | 121.1792 | -9.169 | 112.1338 | 0.030283 | -0.072572 | 0.001736 | -0.052488 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.1479 | 0.004937 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.019719 | 9.1993 | 9.0964 | 9.1707 | 9.1165 | 9.2465 | 9.2088 | 9.1017 | 0.057063 | 0.16621 | 0.023248 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.03803 | -0.01864 | 0.058501 | -0.052455 | 0.024686
2712.5312 | 121.3623 | -8.6197 | 112.5824 | 0.034862 | -0.058836 | -0.007421 | -0.047909 | 0.072888 | 0.035221 | -0.062717 | 0.038752 | 0.1479 | 0.004937 | -0.11094 | 0.066548 | 0.069001 | -0.019749 | 0.019719 | 8.6546 | 8.5609 | 8.6123 | 8.5718 | 8.6926 | 8.6549 | 8.557 | 0.057063 | 0.16621 | 0.023248 | -0.092633 | 0.084859 | 0.087312 | -0.001438 | 0.03803 | -0.027796 | 0.058501 | -0.061611 | 0.024686
2714.2969 | 121.3669 | -7.9788 | 113.2553 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.048956 | -0.076452 | 0.038752 | 0.15706 | 0.004937 | -0.10179 | 0.057392 | 0.069001 | -0.015171 | 0.019719 | 8.0137 | 7.92 | 7.976 | 7.9309 | 8.0563 | 8.0278 | 7.9024 | 0.057063 | 0.17537 | 0.023248 | -0.083475 | 0.075703 | 0.087312 | 0.00314 | 0.03803 | -0.01864 | 0.053923 | -0.052455 | 0.020108
2715.9844 | 121.3577 | -7.901 | 113.3698 | 0.030283 | -0.058836 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.071874 | 0.038752 | 0.15706 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.015141 | 7.9313 | 7.8422 | 7.8982 | 7.8531 | 7.9739 | 7.9454 | 7.8291 | 0.057063 | 0.17537 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.033452 | -0.023218 | 0.053923 | -0.052455 | 0.024686
2717.75 | 121.4081 | -7.3059 | 113.9557 | 0.030283 | -0.063415 | 0.001736 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.073579 | -0.024328 | 0.024297 | 7.3362 | 7.2425 | 7.3076 | 7.2626 | 7.3834 | 7.3457 | 7.2386 | 0.052485 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.09189 | -0.006017 | 0.042608 | -0.023218 | 0.058502 | -0.043298 | 0.038422
2719.5156 | 121.3943 | -7.5897 | 113.6444 | 0.034862 | -0.077151 | -0.007421 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 0.043331 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.019719 | 7.6246 | 7.5126 | 7.5823 | 7.5372 | 7.6626 | 7.6295 | 7.5178 | 0.061642 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.03803 | -0.014061 | 0.058502 | -0.043298 | 0.029265
2721.2188 | 121.4081 | -7.4844 | 113.7817 | 0.025705 | -0.077151 | -0.002842 | -0.057066 | 0.072888 | 0.039799 | -0.071874 | 0.034174 | 0.15706 | 0.009515 | -0.1201 | 0.057392 | 0.059844 | -0.019749 | 0.019719 | 7.5101 | 7.4073 | 7.4816 | 7.4274 | 7.5573 | 7.5242 | 7.4126 | 0.052485 | 0.17537 | 0.027826 | -0.10179 | 0.075703 | 0.078155 | -0.001438 | 0.03803 | -0.023218 | 0.053923 | -0.047877 | 0.029264
2722.9219 | 121.0098 | -8.5098 | 112.8571 | 0.030283 | -0.072572 | -0.002842 | -0.052488 | 0.077466 | 0.039799 | -0.058139 | 0.034174 | 0.15706 | 0.014094 | -0.10179 | 0.066548 | 0.064423 | -0.024328 | 0.019719 | 8.5401 | 8.4373 | 8.507 | 8.4573 | 8.5873 | 8.5496 | 8.4517 | 0.052485 | 0.17537 | 0.032405 | -0.083475 | 0.084859 | 0.082734 | -0.006017 | 0.03803 | -0.032374 | 0.058502 | -0.052454 | 0.038422
2724.6875 | 120.9961 | -8.1482 | 113.1775 | 0.030283 | -0.063415 | -0.007421 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.029595 | 0.15706 | 0.004937 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 8.1785 | 8.0848 | 8.1408 | 8.1003 | 8.2257 | 8.188 | 8.0809 | 0.047906 | 0.17537 | 0.023248 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.027797 | 0.049344 | -0.052455 | 0.024686
2726.375 | 121.106 | -8.8165 | 112.5275 | 0.030283 | -0.063415 | -0.012 | -0.047909 | 0.06831 | 0.035221 | -0.071874 | 0.038752 | 0.1479 | 0.014094 | -0.10637 | 0.06197 | 0.069001 | -0.019749 | 0.024297 | 8.8468 | 8.7531 | 8.8045 | 8.7686 | 8.8848 | 8.8517 | 8.7447 | 0.057063 | 0.16621 | 0.032405 | -0.088054 | 0.080281 | 0.087312 | -0.001438 | 0.042608 | -0.023218 | 0.058501 | -0.047876 | 0.033843
2728.1406 | 119.7098 | -5.0262 | 115.4846 | 0.034862 | -0.058836 | -0.007421 | -0.052488 | 0.077466 | 0.044377 | -0.076452 | 0.038752 | 0.15248 | 0.014094 | -0.10179 | 0.06197 | 0.069001 | -0.019749 | 0.010563 | 5.0611 | 4.9674 | 5.0188 | 4.9738 | 5.1037 | 5.0706 | 4.9498 | 0.057063 | 0.17079 | 0.032405 | -0.083475 | 0.080281 | 0.087312 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.047876 | 0.033843
2729.8906 | 120.9091 | -3.8773 | 117.3248 | 0.030283 | -0.058836 | -0.007421 | -0.052488 | 0.072888 | 0.039799 | -0.067295 | 0.034174 | 0.1479 | 0.014094 | -0.10179 | 0.071126 | 0.059844 | -0.019749 | 0.019719 | 3.9075 | 3.8184 | 3.8698 | 3.8248 | 3.9501 | 3.9171 | 3.81 | 0.052485 | 0.16621 | 0.032405 | -0.083475 | 0.089437 | 0.078155 | -0.001438 | 0.03803 | -0.036952 | 0.053923 | -0.057032 | 0.033843
2731.5781 | 120.7855 | -3.8406 | 116.8396 | 0.034862 | -0.067994 | -0.007421 | -0.038752 | 0.077466 | 0.039799 | -0.062717 | 0.034174 | 0.1479 | 0.009515 | -0.1201 | 0.066548 | 0.069001 | -0.015171 | 0.015141 | 3.8755 | 3.7726 | 3.8332 | 3.8019 | 3.9181 | 3.8804 | 3.7779 | 0.052485 | 0.16621 | 0.027826 | -0.10179 | 0.084859 | 0.087312 | 0.00314 | 0.033452 | -0.032374 | 0.049345 | -0.057033 | 0.024686
2733.3438 | 121.2845 | -3.5248 | 117.7277 | 0.025705 | -0.058836 | -0.007421 | -0.052488 | 0.072888 | 0.035221 | -0.067295 | 0.034174 | 0.1479 | 0.009515 | -0.11094 | 0.057392 | 0.073579 | -0.019749 | 0.015141 | 3.5505 | 3.4659 | 3.5174 | 3.4723 | 3.5977 | 3.56 | 3.4575 | 0.052485 | 0.16621 | 0.027826 | -0.092633 | 0.075703 | 0.09189 | -0.001438 | 0.033452 | -0.023218 | 0.053923 | -0.047877 | 0.029264
2735.1094 | 121.4264 | -3.0579 | 118.2495 | 0.030283 | -0.067994 | -0.012 | -0.052488 | 0.06831 | 0.035221 | -0.071874 | 0.034174 | 0.1479 | 0.009515 | -0.10179 | 0.06197 | 0.064423 | -0.015171 | 0.024297 | 3.0881 | 2.9899 | 3.0459 | 3.0054 | 3.1262 | 3.0931 | 2.986 | 0.052485 | 0.16621 | 0.027826 | -0.083475 | 0.080281 | 0.082734 | 0.00314 | 0.042608 | -0.027796 | 0.049345 | -0.052455 | 0.024686
2736.8125 | 121.4813 | -3.1631 | 118.1671 | 0.021127 | -0.067994 | -0.007421 | -0.047909 | 0.072888 | 0.035221 | -0.062717 | 0.034174 | 0.15248 | 0.000359 | -0.10637 | 0.057392 | 0.069001 | -0.019749 | 0.019719 | 3.1843 | 3.0952 | 3.1557 | 3.1152 | 3.236 | 3.1984 | 3.1004 | 0.052485 | 0.17079 | 0.01867 | -0.088054 | 0.075703 | 0.087312 | -0.001438 | 0.03803 | -0.023218 | 0.053923 | -0.057033 | 0.020108
2738.5625 | 121.3577 | -2.8381 | 118.5379 | 0.034862 | -0.067994 | -0.002842 | -0.052488 | 0.072888 | 0.035221 | -0.067295 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.066548 | 0.069001 | -0.010593 | 0.019719 | 2.873 | 2.7701 | 2.8353 | 2.7856 | 2.911 | 2.8734 | 2.7708 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.084859 | 0.087312 | 0.007718 | 0.03803 | -0.027796 | 0.049345 | -0.057033 | 0.020108
2740.25 | 121.4767 | -3.0304 | 118.4235 | 0.034862 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.035221 | -0.062717 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.06197 | 0.069001 | -0.024328 | 0.010563 | 3.0653 | 2.967 | 3.0276 | 2.9825 | 3.1079 | 3.0656 | 2.9677 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.080281 | 0.087312 | -0.006017 | 0.028874 | -0.023218 | 0.06308 | -0.047876 | 0.038422
2742.0469 | 116.3544 | -81.8665 | 34.3369 | 0.062332 | -0.035942 | 0.029208 | -0.01586 | 0.10951 | 0.067269 | -0.03067 | 0.070802 | 0.18911 | 0.041563 | -0.1201 | 0.039079 | 0.027798 | -0.042641 | 0.001406 | 81.9288 | 81.8305 | 81.8957 | 81.8506 | 81.976 | 81.9337 | 81.8358 | 0.089113 | 0.20742 | 0.059874 | -0.10179 | 0.05739 | 0.046109 | -0.02433 | 0.019717 | 0.031723 | 0.11344 | 0.002484 | 0.084204
2743.7344 | 121.0785 | -120.7214 | 0.1831 | 0.080646 | -0.022205 | 0.033786 | 0.002454 | 0.11867 | 0.090161 | -0.026092 | 0.084537 | 0.20284 | 0.05072 | -0.1201 | 0.025345 | 0.018642 | -0.051798 | -0.012328 | 120.8021 | 120.6992 | 120.7552 | 120.7239 | 120.8401 | 120.8116 | 120.6953 | 0.10285 | 0.22116 | 0.069031 | -0.10179 | 0.043656 | 0.036953 | -0.033487 | 0.005983 | 0.059192 | 0.13633 | 0.025375 | 0.10252
2745.4844 | 121.1563 | -120.8496 | 0.21057 | 0.071489 | -0.008469 | 0.042944 | -0.006703 | 0.12325 | 0.081005 | -0.016936 | 0.093694 | 0.20284 | 0.064455 | -0.12926 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 120.9211 | 120.8411 | 120.8926 | 120.8429 | 120.9729 | 120.9306 | 120.8327 | 0.112 | 0.22116 | 0.082766 | -0.11095 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.063771 | 0.13633 | 0.034532 | 0.1071
2747.25 | 121.1243 | -120.9686 | 0.21973 | 0.076067 | -0.022205 | 0.038365 | 0.002454 | 0.11867 | 0.081005 | -0.016936 | 0.084537 | 0.19827 | 0.055298 | -0.12468 | 0.029923 | 0.014064 | -0.042641 | -0.00775 | 121.0447 | 120.9464 | 121.007 | 120.9711 | 121.0873 | 121.0496 | 120.9517 | 0.10285 | 0.21658 | 0.073609 | -0.10637 | 0.048234 | 0.032375 | -0.02433 | 0.010561 | 0.054614 | 0.12718 | 0.025375 | 0.097939
2748.9375 | 116.6885 | -83.0887 | 33.6136 | 0.06691 | -0.031363 | 0.033786 | -0.002124 | 0.11409 | 0.071848 | -0.026092 | 0.07538 | 0.19369 | 0.05072 | -0.1201 | 0.034501 | 0.032376 | -0.038063 | -0.00775 | 83.1556 | 83.0573 | 83.1225 | 83.0866 | 83.2028 | 83.1605 | 83.0626 | 0.093691 | 0.212 | 0.069031 | -0.10179 | 0.052812 | 0.050687 | -0.019752 | 0.010561 | 0.040879 | 0.11344 | 0.016219 | 0.088783
2750.7031 | 120.8405 | -120.6985 | 0.20599 | 0.080646 | -0.013048 | 0.038365 | -0.002124 | 0.12325 | 0.090161 | -0.016936 | 0.084537 | 0.20742 | 0.055298 | -0.12468 | 0.034501 | 0.018642 | -0.042641 | -0.003172 | 120.7792 | 120.6855 | 120.7369 | 120.6964 | 120.8218 | 120.7887 | 120.6816 | 0.10285 | 0.22573 | 0.073609 | -0.10637 | 0.052812 | 0.036953 | -0.02433 | 0.015139 | 0.050036 | 0.12718 | 0.020797 | 0.097939
2752.4844 | 121.0327 | -120.7443 | 0.1831 | 0.076067 | -0.013048 | 0.033786 | 0.007033 | 0.11867 | 0.081005 | -0.03067 | 0.079959 | 0.20284 | 0.05072 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 120.8204 | 120.7313 | 120.7781 | 120.7514 | 120.863 | 120.8253 | 120.7137 | 0.09827 | 0.22116 | 0.069031 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.050036 | 0.1226 | 0.020797 | 0.093361
2754.1719 | 121.1197 | -120.7947 | 0.17853 | 0.076067 | -0.022205 | 0.038365 | 0.007033 | 0.12325 | 0.085583 | -0.03067 | 0.079959 | 0.20284 | 0.055298 | -0.12468 | 0.029923 | 0.014064 | -0.038063 | -0.00775 | 120.8707 | 120.7725 | 120.833 | 120.8017 | 120.9179 | 120.8803 | 120.764 | 0.09827 | 0.22116 | 0.073609 | -0.10637 | 0.048234 | 0.032375 | -0.019752 | 0.010561 | 0.050036 | 0.11802 | 0.025375 | 0.093361
2755.8594 | 121.0968 | -120.8542 | 0.19684 | 0.076067 | -0.022205 | 0.033786 | -0.006703 | 0.12325 | 0.081005 | -0.021514 | 0.07538 | 0.19827 | 0.055298 | -0.1201 | 0.020767 | 0.014064 | -0.04722 | -0.00775 | 120.9303 | 120.832 | 120.888 | 120.8475 | 120.9774 | 120.9352 | 120.8327 | 0.093691 | 0.21658 | 0.073609 | -0.10179 | 0.039078 | 0.032375 | -0.028909 | 0.010561 | 0.054613 | 0.1226 | 0.034531 | 0.10252
2757.625 | 121.1655 | -120.8633 | 0.17853 | 0.071489 | -0.022205 | 0.038365 | -0.006703 | 0.11867 | 0.085583 | -0.016936 | 0.084537 | 0.20742 | 0.055298 | -0.12468 | 0.029923 | 0.004908 | -0.033484 | -0.012328 | 120.9348 | 120.8411 | 120.9017 | 120.8566 | 120.982 | 120.9489 | 120.8464 | 0.10285 | 0.22573 | 0.073609 | -0.10637 | 0.048234 | 0.023219 | -0.015173 | 0.005983 | 0.054614 | 0.11802 | 0.025375 | 0.088782
2759.3125 | 121.0602 | -120.9274 | 0.21057 | 0.076067 | -0.017627 | 0.042944 | 0.002454 | 0.11867 | 0.090161 | -0.021514 | 0.089116 | 0.20284 | 0.059877 | -0.11552 | 0.029923 | 0.014064 | -0.042641 | -0.012328 | 121.0035 | 120.9098 | 120.9704 | 120.9299 | 121.0461 | 121.0176 | 120.9059 | 0.10743 | 0.22116 | 0.078188 | -0.097212 | 0.048234 | 0.032375 | -0.02433 | 0.005983 | 0.059193 | 0.13176 | 0.029954 | 0.10252
2761.0625 | 121.2112 | -120.9183 | 0.18768 | 0.080646 | -0.013048 | 0.042944 | -0.006703 | 0.12782 | 0.090161 | -0.021514 | 0.089116 | 0.20284 | 0.055298 | -0.1201 | 0.020767 | 0.018642 | -0.042641 | -0.012328 | 120.9989 | 120.9052 | 120.9612 | 120.9116 | 121.0461 | 121.0084 | 120.8968 | 0.10743 | 0.22116 | 0.073609 | -0.10179 | 0.039078 | 0.036953 | -0.02433 | 0.005983 | 0.068349 | 0.13176 | 0.034531 | 0.097939
2762.8281 | 121.106 | -120.9869 | 0.19684 | 0.080646 | -0.017627 | 0.042944 | -0.006703 | 0.12325 | 0.085583 | -0.026092 | 0.084537 | 0.19827 | 0.055298 | -0.12468 | 0.034501 | 0.009486 | -0.038063 | -0.012328 | 121.0676 | 120.9693 | 121.0299 | 120.9802 | 121.1102 | 121.0725 | 120.9608 | 0.10285 | 0.21658 | 0.073609 | -0.10637 | 0.052812 | 0.027797 | -0.019752 | 0.005983 | 0.050036 | 0.1226 | 0.020797 | 0.093361
2764.5938 | 115.7593 | -77.6001 | 38.1454 | 0.062332 | -0.031363 | 0.029208 | -0.01586 | 0.11409 | 0.071848 | -0.026092 | 0.066223 | 0.18453 | 0.041563 | -0.1201 | 0.039079 | 0.032376 | -0.038063 | -0.003172 | 77.6624 | 77.5687 | 77.6293 | 77.5842 | 77.7142 | 77.6719 | 77.574 | 0.084534 | 0.20284 | 0.059874 | -0.10179 | 0.05739 | 0.050687 | -0.019752 | 0.015139 | 0.027144 | 0.10429 | 0.002484 | 0.079626
2766.2812 | 120.7352 | -119.8563 | 0.74158 | 0.076067 | -0.013048 | 0.047522 | -0.002124 | 0.11409 | 0.081005 | -0.021514 | 0.084537 | 0.20742 | 0.059877 | -0.12468 | 0.020767 | 0.018642 | -0.042641 | -0.00775 | 119.9323 | 119.8432 | 119.9038 | 119.8541 | 119.9704 | 119.9373 | 119.8347 | 0.10285 | 0.22573 | 0.078188 | -0.10637 | 0.039078 | 0.036953 | -0.02433 | 0.010561 | 0.06377 | 0.12718 | 0.03911 | 0.10252
2768.0469 | 120.7855 | -120.0943 | 0.70496 | 0.076067 | -0.026784 | 0.033786 | 0.002454 | 0.12325 | 0.081005 | -0.021514 | 0.089116 | 0.212 | 0.055298 | -0.12468 | 0.025345 | 0.014064 | -0.04722 | -0.012328 | 120.1704 | 120.0675 | 120.1281 | 120.0968 | 120.2175 | 120.1753 | 120.0728 | 0.10743 | 0.23031 | 0.073609 | -0.10637 | 0.043656 | 0.032375 | -0.028909 | 0.005983 | 0.063771 | 0.13634 | 0.029953 | 0.10252
2769.7344 | 120.9045 | -118.8812 | 2.0233 | 0.076067 | -0.022205 | 0.042944 | -0.006703 | 0.11867 | 0.085583 | -0.021514 | 0.084537 | 0.19369 | 0.055298 | -0.1201 | 0.034501 | 0.014064 | -0.04722 | -0.012328 | 118.9573 | 118.859 | 118.9242 | 118.8745 | 118.9999 | 118.9668 | 118.8597 | 0.10285 | 0.212 | 0.073609 | -0.10179 | 0.052812 | 0.032375 | -0.028909 | 0.005983 | 0.050036 | 0.13176 | 0.020797 | 0.10252
2771.4844 | 120.9137 | -120.3049 | 0.59052 | 0.076067 | -0.022205 | 0.038365 | 0.007033 | 0.11867 | 0.081005 | -0.026092 | 0.084537 | 0.20742 | 0.064455 | -0.1201 | 0.020767 | 0.014064 | -0.042641 | -0.00775 | 120.3809 | 120.2827 | 120.3432 | 120.3119 | 120.4235 | 120.3859 | 120.2788 | 0.10285 | 0.22573 | 0.082766 | -0.10179 | 0.039078 | 0.032375 | -0.02433 | 0.010561 | 0.06377 | 0.12718 | 0.043688 | 0.1071
2773.2344 | 120.9641 | -120.3918 | 0.55847 | 0.076067 | -0.013048 | 0.052101 | -0.002124 | 0.12325 | 0.090161 | -0.03067 | 0.079959 | 0.19827 | 0.055298 | -0.13384 | 0.025345 | 0.018642 | -0.04722 | -0.012328 | 120.4679 | 120.3788 | 120.4439 | 120.3897 | 120.5151 | 120.482 | 120.3612 | 0.09827 | 0.21658 | 0.073609 | -0.11553 | 0.043656 | 0.036953 | -0.028909 | 0.005983 | 0.054614 | 0.12718 | 0.029953 | 0.10252
2774.9844 | 120.6345 | -120.314 | 0.58136 | 0.085224 | -0.026784 | 0.033786 | 0.002454 | 0.11409 | 0.090161 | -0.021514 | 0.089116 | 0.20284 | 0.059877 | -0.12468 | 0.034501 | 0.014064 | -0.038063 | -0.003172 | 120.3992 | 120.2872 | 120.3478 | 120.3165 | 120.4281 | 120.4042 | 120.2925 | 0.10743 | 0.22116 | 0.078188 | -0.10637 | 0.052812 | 0.032375 | -0.019752 | 0.015139 | 0.054615 | 0.12718 | 0.025376 | 0.09794
2776.7344 | 121.0098 | -120.3918 | 0.60883 | 0.080646 | -0.022205 | 0.038365 | -0.002124 | 0.12782 | 0.081005 | -0.012357 | 0.089116 | 0.19827 | 0.055298 | -0.1201 | 0.025345 | 0.014064 | -0.04722 | -0.00775 | 120.4725 | 120.3696 | 120.4302 | 120.3897 | 120.5197 | 120.4729 | 120.3795 | 0.10743 | 0.21658 | 0.073609 | -0.10179 | 0.043656 | 0.032375 | -0.028909 | 0.010561 | 0.063771 | 0.13634 | 0.029953 | 0.10252
2778.5 | 121.1151 | -120.3552 | 0.59509 | 0.080646 | -0.013048 | 0.042944 | -0.006703 | 0.12325 | 0.081005 | -0.021514 | 0.089116 | 0.20742 | 0.055298 | -0.12468 | 0.020767 | 0.014064 | -0.04722 | -0.00775 | 120.4359 | 120.3422 | 120.3982 | 120.3485 | 120.4785 | 120.4362 | 120.3337 | 0.10743 | 0.22573 | 0.073609 | -0.10637 | 0.039078 | 0.032375 | -0.028909 | 0.010561 | 0.068349 | 0.13634 | 0.034531 | 0.10252
2780.25 | 121.1243 | -120.4834 | 0.49439 | 0.076067 | -0.022205 | 0.033786 | 0.007033 | 0.12325 | 0.085583 | -0.026092 | 0.084537 | 0.20742 | 0.055298 | -0.11552 | 0.020767 | 0.018642 | -0.051798 | -0.012328 | 120.5595 | 120.4612 | 120.5172 | 120.4904 | 120.6066 | 120.569 | 120.4573 | 0.10285 | 0.22573 | 0.073609 | -0.097212 | 0.039078 | 0.036953 | -0.033487 | 0.005983 | 0.06377 | 0.13633 | 0.034531 | 0.1071
2781.9375 | 121.1151 | -120.5475 | 0.48065 | 0.071489 | -0.013048 | 0.042944 | 0.002454 | 0.12325 | 0.081005 | -0.012357 | 0.093694 | 0.20284 | 0.059877 | -0.12926 | 0.025345 | 0.018642 | -0.04722 | -0.00775 | 120.619 | 120.5344 | 120.5904 | 120.5499 | 120.6707 | 120.6285 | 120.5351 | 0.112 | 0.22116 | 0.078188 | -0.11095 | 0.043656 | 0.036953 | -0.028909 | 0.010561 | 0.068349 | 0.14091 | 0.034532 | 0.1071
2783.6875 | 121.1105 | -120.5109 | 0.46234 | 0.076067 | -0.017627 | 0.033786 | -0.002124 | 0.12325 | 0.081005 | -0.021514 | 0.079959 | 0.19827 | 0.05072 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 120.5869 | 120.4932 | 120.5447 | 120.5087 | 120.6341 | 120.5919 | 120.4894 | 0.09827 | 0.21658 | 0.069031 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.020797 | 0.09794
2785.4375 | 120.9412 | -120.52 | 0.49896 | 0.076067 | -0.017627 | 0.038365 | 0.002454 | 0.11867 | 0.085583 | -0.021514 | 0.084537 | 0.20284 | 0.05072 | -0.12468 | 0.029923 | 0.018642 | -0.04722 | -0.016906 | 120.5961 | 120.5024 | 120.5584 | 120.5225 | 120.6387 | 120.6056 | 120.4985 | 0.10285 | 0.22116 | 0.069031 | -0.10637 | 0.048234 | 0.036953 | -0.028909 | 0.001405 | 0.054614 | 0.13176 | 0.020797 | 0.09794
2787.2031 | 118.7668 | -91.5619 | 27.7039 | 0.06691 | -0.026784 | 0.033786 | 0.002454 | 0.11867 | 0.085583 | -0.026092 | 0.079959 | 0.19827 | 0.046142 | -0.1201 | 0.025345 | 0.014064 | -0.04722 | -0.012328 | 91.6288 | 91.5351 | 91.5957 | 91.5643 | 91.6806 | 91.6475 | 91.5358 | 0.09827 | 0.21658 | 0.064453 | -0.10179 | 0.043656 | 0.032375 | -0.028909 | 0.005983 | 0.054614 | 0.12718 | 0.020797 | 0.093362
2788.8906 | 120.7397 | -99.5911 | 20.9335 | 0.06691 | -0.026784 | 0.029208 | -0.01586 | 0.10951 | 0.076426 | -0.026092 | 0.070802 | 0.18911 | 0.041563 | -0.1201 | 0.039079 | 0.032376 | -0.04722 | -0.003172 | 99.658 | 99.5643 | 99.6203 | 99.5752 | 99.7006 | 99.6675 | 99.565 | 0.089113 | 0.20742 | 0.059874 | -0.10179 | 0.05739 | 0.050687 | -0.028909 | 0.015139 | 0.031723 | 0.11802 | 0.002484 | 0.088783
2790.6406 | 120.9549 | -114.8163 | 5.896 | 0.076067 | -0.022205 | 0.038365 | 0.002454 | 0.11867 | 0.081005 | -0.026092 | 0.07538 | 0.19369 | 0.05072 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.012328 | 114.8924 | 114.7941 | 114.8546 | 114.8187 | 114.935 | 114.8973 | 114.7902 | 0.093691 | 0.212 | 0.069031 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.005983 | 0.045457 | 0.1226 | 0.020797 | 0.09794
2792.3281 | 121.051 | -115.4297 | 5.3009 | 0.071489 | -0.017627 | 0.038365 | -0.006703 | 0.11867 | 0.081005 | -0.021514 | 0.07538 | 0.19827 | 0.05072 | -0.12468 | 0.029923 | 0.018642 | -0.042641 | -0.012328 | 115.5012 | 115.4121 | 115.4681 | 115.423 | 115.5484 | 115.5107 | 115.4082 | 0.093691 | 0.21658 | 0.069031 | -0.10637 | 0.048234 | 0.036953 | -0.02433 | 0.005983 | 0.045457 | 0.11802 | 0.020797 | 0.093361
2794.0781 | 120.9595 | -115.2328 | 5.6763 | 0.080646 | -0.017627 | 0.038365 | -0.002124 | 0.1324 | 0.081005 | -0.026092 | 0.07538 | 0.19827 | 0.05072 | -0.1201 | 0.029923 | 0.018642 | -0.038063 | -0.00775 | 115.3135 | 115.2152 | 115.2712 | 115.2307 | 115.3653 | 115.3139 | 115.2068 | 0.093691 | 0.21658 | 0.069031 | -0.10179 | 0.048234 | 0.036953 | -0.019752 | 0.010561 | 0.045457 | 0.11344 | 0.020797 | 0.088783
2795.8281 | 121.0876 | -104.3427 | 16.5253 | 0.071489 | -0.026784 | 0.033786 | -0.006703 | 0.11867 | 0.071848 | -0.026092 | 0.07538 | 0.20284 | 0.055298 | -0.11552 | 0.025345 | 0.02322 | -0.04722 | -0.012328 | 104.4141 | 104.3159 | 104.3764 | 104.3359 | 104.4613 | 104.4145 | 104.3166 | 0.093691 | 0.22116 | 0.073609 | -0.097212 | 0.043656 | 0.041531 | -0.028909 | 0.005983 | 0.050035 | 0.1226 | 0.029953 | 0.10252
2797.5938 | 121.0693 | -12.3505 | 108.5953 | 0.034862 | -0.063415 | -0.002842 | -0.052488 | 0.077466 | 0.035221 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.06197 | 0.069001 | -0.015171 | 0.019719 | 12.3853 | 12.287 | 12.3476 | 12.298 | 12.4279 | 12.3857 | 12.2877 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.080281 | 0.087312 | 0.00314 | 0.03803 | -0.023218 | 0.053923 | -0.057033 | 0.020108
2799.2969 | 120.3506 | -11.2335 | 109.8404 | 0.030283 | -0.058836 | -0.002842 | -0.043331 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.15706 | 0.004937 | -0.10637 | 0.066548 | 0.073579 | -0.024328 | 0.015141 | 11.2638 | 11.1747 | 11.2307 | 11.1902 | 11.3156 | 11.2779 | 11.1754 | 0.057063 | 0.17537 | 0.023248 | -0.088054 | 0.084859 | 0.09189 | -0.006017 | 0.033452 | -0.027796 | 0.06308 | -0.061611 | 0.029265
2801.0469 | 121.0419 | -10.7483 | 110.2753 | 0.03944 | -0.054257 | -0.007421 | -0.043331 | 0.072888 | 0.039799 | -0.062717 | 0.034174 | 0.16164 | 0.009515 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.019719 | 10.7877 | 10.694 | 10.7409 | 10.705 | 10.8212 | 10.7881 | 10.6856 | 0.052485 | 0.17995 | 0.027826 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.03803 | -0.023218 | 0.058502 | -0.047877 | 0.033843
2802.7344 | 120.8359 | -10.6934 | 110.3851 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.086622 | 0.048956 | -0.062717 | 0.038752 | 0.16164 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.015141 | 10.7282 | 10.6345 | 10.6905 | 10.6454 | 10.78 | 10.7423 | 10.6306 | 0.057063 | 0.17995 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.033452 | -0.014062 | 0.058501 | -0.047877 | 0.024686
2804.5 | 121.106 | -10.5698 | 110.4584 | 0.030283 | -0.058836 | -0.007421 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.1479 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.028906 | 0.015141 | 10.6 | 10.5109 | 10.5623 | 10.5264 | 10.6518 | 10.6141 | 10.507 | 0.061642 | 0.16621 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | -0.010595 | 0.033452 | -0.014061 | 0.072237 | -0.047877 | 0.038421
2806.25 | 121.1609 | -10.4187 | 110.5911 | 0.034862 | -0.054257 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.034174 | 0.16164 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 10.4536 | 10.3644 | 10.4159 | 10.3754 | 10.4962 | 10.4585 | 10.356 | 0.052485 | 0.17995 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.023218 | 0.058502 | -0.047877 | 0.033843
2807.9375 | 121.0922 | -10.3958 | 110.701 | 0.030283 | -0.054257 | -0.007421 | -0.047909 | 0.082044 | 0.048956 | -0.062717 | 0.038752 | 0.14332 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 10.4261 | 10.3416 | 10.3884 | 10.3479 | 10.4779 | 10.4448 | 10.3331 | 0.057063 | 0.16163 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.043298 | 0.033843
2809.6875 | 121.1151 | -10.3638 | 110.7468 | 0.03944 | -0.054257 | 0.001736 | -0.052488 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 10.4032 | 10.3095 | 10.3655 | 10.3113 | 10.4412 | 10.4081 | 10.3011 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.043298 | 0.038422
2811.375 | 121.2204 | -10.2127 | 110.8475 | 0.030283 | -0.058836 | -0.007421 | -0.038752 | 0.082044 | 0.044377 | -0.071874 | 0.029595 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.015171 | 0.015141 | 10.243 | 10.1539 | 10.2053 | 10.174 | 10.2948 | 10.2571 | 10.1408 | 0.047906 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | 0.00314 | 0.033452 | -0.027797 | 0.044766 | -0.047877 | 0.024686
2813.1406 | 121.138 | -9.8602 | 111.2915 | 0.030283 | -0.054257 | -0.007421 | -0.043331 | 0.082044 | 0.048956 | -0.067295 | 0.034174 | 0.15706 | 0.004937 | -0.11094 | 0.06197 | 0.059844 | -0.015171 | 0.015141 | 9.8905 | 9.806 | 9.8528 | 9.8169 | 9.9423 | 9.9092 | 9.7929 | 0.052485 | 0.17537 | 0.023248 | -0.092633 | 0.080281 | 0.078155 | 0.00314 | 0.033452 | -0.027796 | 0.049345 | -0.057033 | 0.020108
2814.8438 | 121.225 | -9.8099 | 111.2915 | 0.025705 | -0.054257 | -0.007421 | -0.047909 | 0.082044 | 0.030642 | -0.071874 | 0.038752 | 0.15706 | 0.02325 | -0.11094 | 0.048236 | 0.064423 | -0.019749 | 0.019719 | 9.8356 | 9.7556 | 9.8025 | 9.762 | 9.8919 | 9.8405 | 9.738 | 0.057063 | 0.17537 | 0.041561 | -0.092633 | 0.066547 | 0.082734 | -0.001438 | 0.03803 | -0.009484 | 0.058501 | -0.024986 | 0.042999
2816.5938 | 121.1472 | -9.8465 | 111.319 | 0.030283 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.069001 | -0.015171 | 0.019719 | 9.8768 | 9.7877 | 9.8437 | 9.7986 | 9.9285 | 9.8909 | 9.7838 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.087312 | 0.00314 | 0.03803 | -0.014061 | 0.058502 | -0.047877 | 0.024686
2818.3594 | 121.1975 | -9.6771 | 111.438 | 0.034862 | -0.058836 | -0.007421 | -0.043331 | 0.072888 | 0.035221 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.069001 | -0.019749 | 0.015141 | 9.712 | 9.6183 | 9.6697 | 9.6338 | 9.75 | 9.7123 | 9.6098 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.087312 | -0.001438 | 0.033452 | -0.023218 | 0.053923 | -0.043298 | 0.033843
2820.0625 | 121.2708 | -9.7321 | 111.3739 | 0.034862 | -0.058836 | -0.007421 | -0.043331 | 0.06831 | 0.044377 | -0.058139 | 0.038752 | 0.15706 | 0.009515 | -0.11552 | 0.052814 | 0.064423 | -0.028906 | 0.010563 | 9.7669 | 9.6732 | 9.7246 | 9.6887 | 9.8004 | 9.7764 | 9.6739 | 0.057063 | 0.17537 | 0.027826 | -0.097212 | 0.071125 | 0.082734 | -0.010595 | 0.028874 | -0.014062 | 0.067658 | -0.043299 | 0.038421
2821.75 | 121.2021 | -9.6863 | 111.4929 | 0.030283 | -0.063415 | -0.012 | -0.043331 | 0.072888 | 0.048956 | -0.053561 | 0.038752 | 0.15248 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 9.7166 | 9.6229 | 9.6743 | 9.6429 | 9.7592 | 9.7352 | 9.6327 | 0.057063 | 0.17079 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.047877 | 0.033843
2823.5 | 121.3165 | -9.3933 | 111.7493 | 0.030283 | -0.058836 | -0.007421 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.038752 | 0.1479 | 0.014094 | -0.11094 | 0.06197 | 0.069001 | -0.015171 | 0.024297 | 9.4236 | 9.3345 | 9.3859 | 9.3454 | 9.4708 | 9.4331 | 9.326 | 0.057063 | 0.16621 | 0.032405 | -0.092633 | 0.080281 | 0.087312 | 0.00314 | 0.042608 | -0.023218 | 0.053923 | -0.047876 | 0.029265
2825.25 | 121.2799 | -8.7433 | 112.413 | 0.034862 | -0.054257 | -0.007421 | -0.043331 | 0.072888 | 0.039799 | -0.067295 | 0.025017 | 0.15248 | 0.004937 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.019719 | 8.7781 | 8.689 | 8.7359 | 8.7 | 8.8162 | 8.7831 | 8.676 | 0.043328 | 0.17079 | 0.023248 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.03803 | -0.032375 | 0.044766 | -0.052455 | 0.024686
2826.9375 | 121.2845 | -8.3862 | 112.7975 | 0.030283 | -0.063415 | -0.012 | -0.038752 | 0.072888 | 0.039799 | -0.067295 | 0.038752 | 0.14332 | 0.009515 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 8.4165 | 8.3228 | 8.3742 | 8.3475 | 8.4591 | 8.426 | 8.3189 | 0.057063 | 0.16163 | 0.027826 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.052455 | 0.029264
2828.6875 | 121.3348 | -7.8781 | 113.3057 | 0.034862 | -0.058836 | -0.007421 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.1479 | 0.004937 | -0.11094 | 0.06197 | 0.064423 | -0.024328 | 0.019719 | 7.913 | 7.8193 | 7.8707 | 7.8302 | 7.9556 | 7.9179 | 7.8108 | 0.052485 | 0.16621 | 0.023248 | -0.092633 | 0.080281 | 0.082734 | -0.006017 | 0.03803 | -0.027796 | 0.058502 | -0.057033 | 0.029265
2830.375 | 121.2204 | -7.8552 | 113.4293 | 0.034862 | -0.058836 | -0.002842 | -0.047909 | 0.06831 | 0.048956 | -0.062717 | 0.038752 | 0.1479 | 0.014094 | -0.10637 | 0.066548 | 0.064423 | -0.024328 | 0.019719 | 7.8901 | 7.7964 | 7.8524 | 7.8073 | 7.9235 | 7.9042 | 7.7925 | 0.057063 | 0.16621 | 0.032405 | -0.088054 | 0.084859 | 0.082734 | -0.006017 | 0.03803 | -0.027796 | 0.06308 | -0.052454 | 0.038422
2832.125 | 121.2662 | -6.9351 | 114.3539 | 0.034862 | -0.058836 | -0.002842 | -0.052488 | 0.072888 | 0.030642 | -0.071874 | 0.034174 | 0.15248 | 0.018672 | -0.10179 | 0.06197 | 0.069001 | -0.019749 | 0.015141 | 6.97 | 6.8763 | 6.9323 | 6.8826 | 7.008 | 6.9658 | 6.8632 | 0.052485 | 0.17079 | 0.036983 | -0.083475 | 0.080281 | 0.087312 | -0.001438 | 0.033452 | -0.027796 | 0.053923 | -0.043298 | 0.038421
2833.8906 | 121.2982 | -6.7795 | 114.4959 | 0.034862 | -0.054257 | -0.012 | -0.047909 | 0.072888 | 0.030642 | -0.067295 | 0.043331 | 0.1479 | 0.009515 | -0.11094 | 0.06197 | 0.069001 | -0.019749 | 0.024297 | 6.8143 | 6.7252 | 6.7675 | 6.7316 | 6.8524 | 6.8101 | 6.7122 | 0.061642 | 0.16621 | 0.027826 | -0.092633 | 0.080281 | 0.087312 | -0.001438 | 0.042608 | -0.018639 | 0.06308 | -0.052455 | 0.029264
2835.6406 | 121.2753 | -6.6422 | 114.6423 | 0.034862 | -0.058836 | -0.007421 | -0.047909 | 0.077466 | 0.048956 | -0.062717 | 0.034174 | 0.15248 | 0.014094 | -0.10179 | 0.06197 | 0.064423 | -0.019749 | 0.010563 | 6.677 | 6.5833 | 6.6347 | 6.5942 | 6.7196 | 6.6911 | 6.5794 | 0.052485 | 0.17079 | 0.032405 | -0.083475 | 0.080281 | 0.082734 | -0.001438 | 0.028874 | -0.027796 | 0.053923 | -0.047876 | 0.033843
2837.3281 | 121.2616 | -6.6879 | 114.6744 | 0.030283 | -0.054257 | 0.001736 | -0.043331 | 0.072888 | 0.048956 | -0.067295 | 0.038752 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.064423 | -0.015171 | 0.019719 | 6.7182 | 6.6337 | 6.6897 | 6.6446 | 6.7608 | 6.7369 | 6.6206 | 0.057063 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.082734 | 0.00314 | 0.03803 | -0.01864 | 0.053923 | -0.043298 | 0.029265
2839.0781 | 121.2387 | -6.5186 | 114.798 | 0.025705 | -0.058836 | -0.002842 | -0.043331 | 0.072888 | 0.044377 | -0.067295 | 0.043331 | 0.14332 | 0.009515 | -0.10637 | 0.06197 | 0.069001 | -0.024328 | 0.019719 | 6.5443 | 6.4597 | 6.5157 | 6.4752 | 6.5914 | 6.5629 | 6.4513 | 0.061642 | 0.16163 | 0.027826 | -0.088054 | 0.080281 | 0.087312 | -0.006017 | 0.03803 | -0.018639 | 0.067659 | -0.052455 | 0.033843
2840.7656 | 121.2616 | -6.8848 | 114.4501 | 0.034862 | -0.054257 | -0.007421 | -0.043331 | 0.072888 | 0.048956 | -0.062717 | 0.034174 | 0.15706 | 0.004937 | -0.10637 | 0.06197 | 0.073579 | -0.015171 | 0.010563 | 6.9196 | 6.8305 | 6.8773 | 6.8414 | 6.9577 | 6.9337 | 6.822 | 0.052485 | 0.17537 | 0.023248 | -0.088054 | 0.080281 | 0.09189 | 0.00314 | 0.028874 | -0.027796 | 0.049345 | -0.057033 | 0.020108
2842.5312 | 121.3852 | -6.546 | 114.7385 | 0.030283 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.071874 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.06197 | 0.059844 | -0.010593 | 0.019719 | 6.5763 | 6.4872 | 6.5432 | 6.4981 | 6.6235 | 6.5858 | 6.4741 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.080281 | 0.078155 | 0.007718 | 0.03803 | -0.023218 | 0.049345 | -0.052455 | 0.020108
2844.2344 | 121.3943 | -6.427 | 114.8117 | 0.030283 | -0.063415 | 0.001736 | -0.047909 | 0.072888 | 0.039799 | -0.067295 | 0.029595 | 0.1479 | 0.004937 | -0.10637 | 0.066548 | 0.059844 | -0.019749 | 0.019719 | 6.4573 | 6.3636 | 6.4287 | 6.3791 | 6.4999 | 6.4668 | 6.3597 | 0.047906 | 0.16621 | 0.023248 | -0.088054 | 0.084859 | 0.078155 | -0.001438 | 0.03803 | -0.036953 | 0.049344 | -0.061611 | 0.024686
2845.9688 | 121.2891 | -6.8069 | 114.5874 | 0.034862 | -0.049678 | -0.007421 | -0.047909 | 0.072888 | 0.048956 | -0.067295 | 0.038752 | 0.1479 | 0.014094 | -0.10637 | 0.066548 | 0.064423 | -0.019749 | 0.019719 | 6.8418 | 6.7573 | 6.7995 | 6.759 | 6.8798 | 6.8559 | 6.7397 | 0.057063 | 0.16621 | 0.032405 | -0.088054 | 0.084859 | 0.082734 | -0.001438 | 0.03803 | -0.027796 | 0.058501 | -0.052454 | 0.033843
2847.6719 | 120.5017 | -25.3143 | 95.5032 | 0.03944 | -0.049678 | -0.002842 | -0.038752 | 0.086622 | 0.048956 | -0.058139 | 0.047909 | 0.16164 | 0.018672 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 25.3538 | 25.2647 | 25.3115 | 25.2756 | 25.401 | 25.3633 | 25.2562 | 0.06622 | 0.17995 | 0.036983 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.004905 | 0.072237 | -0.034142 | 0.043
2849.4375 | 120.7443 | -6.7566 | 114.2212 | 0.03944 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.035221 | -0.058139 | 0.034174 | 0.16164 | 0.014094 | -0.11552 | 0.057392 | 0.069001 | -0.019749 | 0.010563 | 6.796 | 6.6978 | 6.7538 | 6.7133 | 6.8341 | 6.7918 | 6.6985 | 0.052485 | 0.17995 | 0.032405 | -0.097212 | 0.075703 | 0.087312 | -0.001438 | 0.028874 | -0.023218 | 0.053923 | -0.043298 | 0.033843
2851.1406 | 121.0922 | -5.809 | 115.2145 | 0.034862 | -0.063415 | -0.007421 | -0.047909 | 0.072888 | 0.039799 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.015141 | 5.8439 | 5.7456 | 5.8016 | 5.7611 | 5.8819 | 5.8488 | 5.7417 | 0.057063 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.033452 | -0.01864 | 0.053923 | -0.047877 | 0.024686
2852.8906 | 120.3186 | -5.7587 | 115.3061 | 0.025705 | -0.058836 | -0.007421 | -0.047909 | 0.077466 | 0.048956 | -0.071874 | 0.043331 | 0.1479 | 0.009515 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.024297 | 5.7844 | 5.6998 | 5.7512 | 5.7108 | 5.8361 | 5.8076 | 5.6868 | 0.061642 | 0.16621 | 0.027826 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.042608 | -0.018639 | 0.06308 | -0.052455 | 0.029264
2854.5938 | 121.1975 | -5.8365 | 115.2832 | 0.030283 | -0.049678 | -0.007421 | -0.047909 | 0.077466 | 0.035221 | -0.062717 | 0.034174 | 0.1479 | 0.004937 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.015141 | 5.8668 | 5.7868 | 5.8291 | 5.7886 | 5.914 | 5.8717 | 5.7738 | 0.052485 | 0.16621 | 0.023248 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.033452 | -0.023218 | 0.049345 | -0.052455 | 0.020108
2856.3438 | 121.1792 | -5.0034 | 116.098 | 0.030283 | -0.054257 | 0.001736 | -0.047909 | 0.072888 | 0.030642 | -0.067295 | 0.034174 | 0.15248 | 0.009515 | -0.11552 | 0.052814 | 0.064423 | -0.028906 | 0.024297 | 5.0336 | 4.9491 | 5.0051 | 4.9554 | 5.0762 | 5.034 | 4.9361 | 0.052485 | 0.17079 | 0.027826 | -0.097212 | 0.071125 | 0.082734 | -0.010595 | 0.042608 | -0.01864 | 0.06308 | -0.043299 | 0.038421
2858.0938 | 121.0785 | -4.7379 | 116.4734 | 0.030283 | -0.058836 | -0.012 | -0.052488 | 0.072888 | 0.039799 | -0.071874 | 0.038752 | 0.1479 | 0.009515 | -0.11552 | 0.057392 | 0.069001 | -0.019749 | 0.015141 | 4.7681 | 4.679 | 4.7259 | 4.6854 | 4.8107 | 4.7777 | 4.666 | 0.057063 | 0.16621 | 0.027826 | -0.097212 | 0.075703 | 0.087312 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.047877 | 0.029264
2859.7812 | 121.2204 | -4.66 | 116.5146 | 0.034862 | -0.054257 | -0.012 | -0.057066 | 0.072888 | 0.044377 | -0.071874 | 0.034174 | 0.15248 | 0.004937 | -0.11094 | 0.06197 | 0.064423 | -0.015171 | 0.019719 | 4.6949 | 4.6058 | 4.648 | 4.603 | 4.7329 | 4.7044 | 4.5882 | 0.052485 | 0.17079 | 0.023248 | -0.092633 | 0.080281 | 0.082734 | 0.00314 | 0.03803 | -0.027796 | 0.049345 | -0.057033 | 0.020108
2861.5156 | 121.1792 | -3.5385 | 117.7231 | 0.030283 | -0.058836 | -0.007421 | -0.052488 | 0.072888 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.066548 | 0.073579 | -0.015171 | 0.028875 | 3.5688 | 3.4797 | 3.5311 | 3.486 | 3.6114 | 3.5829 | 3.4712 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.084859 | 0.09189 | 0.00314 | 0.047186 | -0.023217 | 0.058502 | -0.057033 | 0.024686
2863.2656 | 121.3074 | -3.5477 | 117.659 | 0.030283 | -0.054257 | -0.012 | -0.047909 | 0.063733 | 0.048956 | -0.067295 | 0.038752 | 0.14332 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.019719 | 3.578 | 3.4934 | 3.5357 | 3.4998 | 3.6114 | 3.5966 | 3.4804 | 0.057063 | 0.16163 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.03803 | -0.023218 | 0.053923 | -0.052455 | 0.024686
2865.0312 | 121.2112 | -3.0899 | 118.1488 | 0.034862 | -0.054257 | -0.012 | -0.043331 | 0.072888 | 0.044377 | -0.067295 | 0.034174 | 0.15706 | 0.009515 | -0.10637 | 0.066548 | 0.069001 | -0.019749 | 0.019719 | 3.1248 | 3.0356 | 3.0779 | 3.0466 | 3.1628 | 3.1343 | 3.0226 | 0.052485 | 0.17537 | 0.027826 | -0.088054 | 0.084859 | 0.087312 | -0.001438 | 0.03803 | -0.032374 | 0.053923 | -0.057033 | 0.029264
2866.7344 | 121.2158 | -3.3737 | 117.897 | 0.025705 | -0.054257 | -0.007421 | -0.047909 | 0.06831 | 0.039799 | -0.062717 | 0.034174 | 0.1479 | -0.004219 | -0.10637 | 0.066548 | 0.073579 | -0.019749 | 0.019719 | 3.3994 | 3.3195 | 3.3663 | 3.3258 | 3.442 | 3.4135 | 3.311 | 0.052485 | 0.16621 | 0.014092 | -0.088054 | 0.084859 | 0.09189 | -0.001438 | 0.03803 | -0.032374 | 0.053923 | -0.070767 | 0.01553
2868.4844 | 121.225 | -3.4058 | 117.9062 | 0.034862 | -0.058836 | -0.007421 | -0.047909 | 0.06831 | 0.044377 | -0.071874 | 0.034174 | 0.15248 | 0.000359 | -0.10637 | 0.066548 | 0.078157 | -0.019749 | 0.015141 | 3.4406 | 3.3469 | 3.3983 | 3.3579 | 3.4741 | 3.4501 | 3.3339 | 0.052485 | 0.17079 | 0.01867 | -0.088054 | 0.084859 | 0.096468 | -0.001438 | 0.033452 | -0.032374 | 0.053923 | -0.066189 | 0.020108
2870.2344 | 121.2112 | -3.3646 | 117.984 | 0.025705 | -0.058836 | -0.012 | -0.052488 | 0.072888 | 0.039799 | -0.067295 | 0.034174 | 0.1479 | 0.000359 | -0.11094 | 0.057392 | 0.073579 | -0.015171 | 0.010563 | 3.3903 | 3.3057 | 3.3526 | 3.3121 | 3.4375 | 3.4044 | 3.2973 | 0.052485 | 0.16621 | 0.01867 | -0.092633 | 0.075703 | 0.09189 | 0.00314 | 0.028874 | -0.023218 | 0.049345 | -0.057033 | 0.01553
2871.9219 | 121.2341 | -3.6667 | 117.6544 | 0.030283 | -0.0451 | -0.012 | -0.043331 | 0.06831 | 0.048956 | -0.067295 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 3.697 | 3.6216 | 3.6547 | 3.6234 | 3.735 | 3.7156 | 3.5994 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.047876 | 0.033843
2873.6719 | 121.2845 | -2.7466 | 118.5516 | 0.030283 | -0.054257 | -0.012 | -0.047909 | 0.072888 | 0.035221 | -0.067295 | 0.029595 | 0.14332 | 0.009515 | -0.10637 | 0.06197 | 0.069001 | -0.019749 | 0.015141 | 2.7769 | 2.6923 | 2.7346 | 2.6987 | 2.8195 | 2.7818 | 2.6793 | 0.047906 | 0.16163 | 0.027826 | -0.088054 | 0.080281 | 0.087312 | -0.001438 | 0.033452 | -0.032375 | 0.049344 | -0.052455 | 0.029264
2875.4375 | 121.3623 | -2.2842 | 118.9865 | 0.030283 | -0.058836 | -0.012 | -0.057066 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.14332 | 0.014094 | -0.10637 | 0.057392 | 0.069001 | -0.019749 | 0.019719 | 2.3145 | 2.2254 | 2.2722 | 2.2272 | 2.3617 | 2.324 | 2.2169 | 0.052485 | 0.16163 | 0.032405 | -0.088054 | 0.075703 | 0.087312 | -0.001438 | 0.03803 | -0.023218 | 0.053923 | -0.043298 | 0.033843
2877.125 | 121.3165 | -2.0004 | 119.2841 | 0.030283 | -0.058836 | -0.012 | -0.043331 | 0.077466 | 0.048956 | -0.076452 | 0.034174 | 0.1479 | 0.004937 | -0.10637 | 0.057392 | 0.078157 | -0.028906 | 0.010563 | 2.0307 | 1.9416 | 1.9884 | 1.9571 | 2.0779 | 2.0494 | 1.924 | 0.052485 | 0.16621 | 0.023248 | -0.088054 | 0.075703 | 0.096468 | -0.010595 | 0.028874 | -0.023218 | 0.06308 | -0.052455 | 0.033843
2878.875 | 121.312 | -1.8311 | 119.4672 | 0.034862 | -0.063415 | -0.012 | -0.057066 | 0.06831 | 0.030642 | -0.076452 | 0.034174 | 0.1479 | 0.014094 | -0.11094 | 0.057392 | 0.069001 | -0.015171 | 0.015141 | 1.8659 | 1.7676 | 1.8191 | 1.774 | 1.8994 | 1.8617 | 1.7546 | 0.052485 | 0.16621 | 0.032405 | -0.092633 | 0.075703 | 0.087312 | 0.00314 | 0.033452 | -0.023218 | 0.049345 | -0.043298 | 0.029265
2880.5625 | 121.3715 | -1.5381 | 119.7784 | 0.034862 | -0.054257 | -0.002842 | -0.038752 | 0.077466 | 0.039799 | -0.058139 | 0.038752 | 0.1479 | 0.014094 | -0.10179 | 0.057392 | 0.069001 | -0.028906 | 0.015141 | 1.5729 | 1.4838 | 1.5352 | 1.4993 | 1.6156 | 1.5779 | 1.4799 | 0.057063 | 0.16621 | 0.032405 | -0.083475 | 0.075703 | 0.087312 | -0.010595 | 0.033452 | -0.01864 | 0.067658 | -0.043298 | 0.043
2882.3125 | 121.3348 | -1.6434 | 119.7601 | 0.03944 | -0.058836 | 0.001736 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.059844 | -0.015171 | 0.019719 | 1.6828 | 1.5845 | 1.6451 | 1.5955 | 1.7163 | 1.6877 | 1.5807 | 0.061642 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.078155 | 0.00314 | 0.03803 | -0.018639 | 0.058502 | -0.052455 | 0.024686
2884.0781 | 121.3669 | -1.6022 | 119.8196 | 0.034862 | -0.049678 | -0.002842 | -0.043331 | 0.086622 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.024297 | 1.637 | 1.5525 | 1.5993 | 1.5588 | 1.6888 | 1.6465 | 1.5395 | 0.057063 | 0.17079 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.042608 | -0.01864 | 0.06308 | -0.043298 | 0.038422
2885.7656 | 121.3623 | -1.5884 | 119.8059 | 0.030283 | -0.054257 | 0.001736 | -0.043331 | 0.077466 | 0.048956 | -0.067295 | 0.034174 | 0.1479 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.010563 | 1.6187 | 1.5342 | 1.5902 | 1.5451 | 1.6659 | 1.6374 | 1.5211 | 0.052485 | 0.16621 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.028874 | -0.027796 | 0.058502 | -0.052455 | 0.033843
2887.4531 | 121.4584 | -1.5518 | 119.8196 | 0.030283 | -0.049678 | -0.002842 | -0.038752 | 0.06831 | 0.044377 | -0.058139 | 0.034174 | 0.15248 | 0.009515 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 1.5821 | 1.5021 | 1.549 | 1.5131 | 1.6201 | 1.5962 | 1.4937 | 0.052485 | 0.17079 | 0.027826 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | -0.027796 | 0.053923 | -0.052455 | 0.029264
2889.2188 | 121.3531 | -1.5427 | 119.8654 | 0.030283 | -0.054257 | -0.002842 | -0.043331 | 0.072888 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.052814 | 0.069001 | -0.019749 | 0.015141 | 1.5729 | 1.4884 | 1.5398 | 1.4993 | 1.6156 | 1.5916 | 1.4799 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.071125 | 0.087312 | -0.001438 | 0.033452 | -0.014062 | 0.058501 | -0.047877 | 0.024686
2890.9062 | 121.3394 | -1.5564 | 119.9066 | 0.034862 | -0.058836 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.11094 | 0.066548 | 0.069001 | -0.024328 | 0.019719 | 1.5913 | 1.4976 | 1.5581 | 1.5085 | 1.6384 | 1.6008 | 1.4937 | 0.061642 | 0.17079 | 0.032405 | -0.092633 | 0.084859 | 0.087312 | -0.006017 | 0.03803 | -0.023217 | 0.067659 | -0.052454 | 0.038422
2892.6562 | 121.463 | -1.5198 | 119.8975 | 0.034862 | -0.054257 | -0.007421 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 0.043331 | 0.1479 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 1.5546 | 1.4655 | 1.5124 | 1.4764 | 1.6018 | 1.5642 | 1.4525 | 0.061642 | 0.16621 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.018639 | 0.06308 | -0.043298 | 0.038421
2894.4062 | 121.376 | -1.5335 | 119.9341 | 0.034862 | -0.058836 | -0.007421 | -0.052488 | 0.082044 | 0.044377 | -0.062717 | 0.034174 | 0.15248 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.015171 | 0.015141 | 1.5684 | 1.4747 | 1.5261 | 1.481 | 1.6156 | 1.5779 | 1.4708 | 0.052485 | 0.17079 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | 0.00314 | 0.033452 | -0.023218 | 0.049345 | -0.047877 | 0.024686
2896.0938 | 121.3898 | -1.387 | 120.1263 | 0.034862 | -0.049678 | -0.002842 | -0.047909 | 0.077466 | 0.035221 | -0.071874 | 0.034174 | 0.1479 | 0.014094 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.010563 | 1.4219 | 1.3373 | 1.3842 | 1.3391 | 1.4645 | 1.4222 | 1.3152 | 0.052485 | 0.16621 | 0.032405 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.028874 | -0.027796 | 0.053923 | -0.047876 | 0.033843
2897.8438 | 121.4676 | -1.4282 | 120.0073 | 0.030283 | -0.054257 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.062717 | 0.047909 | 0.1479 | 0.009515 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.019719 | 1.4585 | 1.374 | 1.4254 | 1.3757 | 1.5011 | 1.4726 | 1.3655 | 0.06622 | 0.16621 | 0.027826 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.03803 | -0.009483 | 0.072237 | -0.047877 | 0.033843
2899.6094 | 121.3943 | -1.4694 | 120.0531 | 0.030283 | -0.054257 | -0.007421 | -0.047909 | 0.082044 | 0.039799 | -0.062717 | 0.038752 | 0.15248 | 0.018672 | -0.11552 | 0.06197 | 0.064423 | -0.010593 | 0.015141 | 1.4997 | 1.4152 | 1.462 | 1.4215 | 1.5515 | 1.5092 | 1.4067 | 0.057063 | 0.17079 | 0.036983 | -0.097212 | 0.080281 | 0.082734 | 0.007718 | 0.033452 | -0.023218 | 0.049345 | -0.043298 | 0.029265
2901.2969 | 121.4035 | -1.4603 | 120.0211 | 0.034862 | -0.054257 | -0.007421 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.018672 | -0.10179 | 0.057392 | 0.069001 | -0.024328 | 0.010563 | 1.4951 | 1.406 | 1.4528 | 1.4169 | 1.5423 | 1.5046 | 1.393 | 0.057063 | 0.17079 | 0.036983 | -0.083475 | 0.075703 | 0.087312 | -0.006017 | 0.028874 | -0.01864 | 0.06308 | -0.03872 | 0.043
2903.0469 | 121.0098 | -31.4163 | 89.566 | 0.048597 | -0.040521 | 0.015472 | -0.029595 | 0.095778 | 0.062691 | -0.053561 | 0.061645 | 0.17079 | 0.032407 | -0.11552 | 0.043657 | 0.041532 | -0.033484 | 0.005985 | 31.4649 | 31.3758 | 31.4318 | 31.3867 | 31.5121 | 31.479 | 31.3628 | 0.079956 | 0.1891 | 0.050718 | -0.097212 | 0.061968 | 0.059843 | -0.015173 | 0.024296 | 0.017988 | 0.095129 | -0.01125 | 0.065891
2904.7344 | 120.5566 | -13.2843 | 107.8857 | 0.044018 | -0.049678 | 0.006315 | -0.043331 | 0.082044 | 0.048956 | -0.053561 | 0.038752 | 0.15248 | 0.018672 | -0.10637 | 0.06197 | 0.059844 | -0.024328 | 0.005985 | 13.3283 | 13.2346 | 13.2906 | 13.241 | 13.3663 | 13.3333 | 13.2307 | 0.057063 | 0.17079 | 0.036983 | -0.088054 | 0.080281 | 0.078155 | -0.006017 | 0.024296 | -0.023218 | 0.06308 | -0.043298 | 0.043
2906.4844 | 120.9366 | -11.5311 | 109.6985 | 0.048597 | -0.049678 | 0.006315 | -0.038752 | 0.095778 | 0.048956 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.1201 | 0.052814 | 0.050688 | -0.024328 | 0.005985 | 11.5797 | 11.4814 | 11.5374 | 11.4923 | 11.6268 | 11.58 | 11.4729 | 0.057063 | 0.17995 | 0.032405 | -0.10179 | 0.071125 | 0.068999 | -0.006017 | 0.024296 | -0.014062 | 0.06308 | -0.03872 | 0.038422
2908.1719 | 121.2112 | -10.8582 | 110.376 | 0.030283 | -0.049678 | 0.006315 | -0.038752 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.018672 | -0.11552 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 10.8884 | 10.8085 | 10.8645 | 10.8194 | 10.9402 | 10.9025 | 10.7954 | 0.057063 | 0.17537 | 0.036983 | -0.097212 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.014062 | 0.058501 | -0.034142 | 0.038421
2909.9375 | 121.2021 | -10.2722 | 111.0214 | 0.034862 | -0.0451 | 0.001736 | -0.038752 | 0.086622 | 0.053534 | -0.058139 | 0.047909 | 0.16164 | 0.018672 | -0.11552 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 10.3071 | 10.2271 | 10.274 | 10.2335 | 10.3588 | 10.3258 | 10.2141 | 0.06622 | 0.17995 | 0.036983 | -0.097212 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.004905 | 0.072237 | -0.034142 | 0.043
2911.7031 | 121.1655 | -10.1395 | 111.145 | 0.03944 | -0.054257 | 0.006315 | -0.038752 | 0.086622 | 0.048956 | -0.058139 | 0.043331 | 0.16164 | 0.009515 | -0.11094 | 0.06197 | 0.055266 | -0.024328 | 0.015141 | 10.1789 | 10.0852 | 10.1458 | 10.1007 | 10.2261 | 10.1884 | 10.0813 | 0.061642 | 0.17995 | 0.027826 | -0.092633 | 0.080281 | 0.073577 | -0.006017 | 0.033452 | -0.018639 | 0.067659 | -0.052455 | 0.033843
2913.4531 | 121.344 | -9.0591 | 112.175 | 0.034862 | -0.054257 | 0.001736 | -0.038752 | 0.082044 | 0.053534 | -0.062717 | 0.047909 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.055266 | -0.024328 | 0.015141 | 9.094 | 9.0049 | 9.0609 | 9.0204 | 9.1412 | 9.1127 | 8.9964 | 0.06622 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.073577 | -0.006017 | 0.033452 | -0.009483 | 0.072237 | -0.047877 | 0.033843
2915.1562 | 121.2524 | -6.4499 | 114.9307 | 0.034862 | -0.058836 | 0.001736 | -0.038752 | 0.086622 | 0.048956 | -0.062717 | 0.043331 | 0.15248 | 0.018672 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.010563 | 6.4848 | 6.3911 | 6.4516 | 6.4111 | 6.5365 | 6.4988 | 6.3872 | 0.061642 | 0.17079 | 0.036983 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.028874 | -0.018639 | 0.06308 | -0.043298 | 0.038421
2916.9062 | 121.3623 | -5.5801 | 115.7455 | 0.03944 | -0.049678 | -0.002842 | -0.043331 | 0.082044 | 0.058113 | -0.062717 | 0.038752 | 0.16164 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.024328 | 0.015141 | 5.6196 | 5.5305 | 5.5773 | 5.5368 | 5.6622 | 5.6383 | 5.5174 | 0.057063 | 0.17995 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.03872 | 0.038422
2918.6719 | 121.4355 | -5.2643 | 116.0522 | 0.025705 | -0.0451 | 0.001736 | -0.038752 | 0.082044 | 0.039799 | -0.053561 | 0.043331 | 0.15706 | 0.018672 | -0.11552 | 0.06197 | 0.069001 | -0.015171 | 0.015141 | 5.29 | 5.2192 | 5.266 | 5.2255 | 5.3463 | 5.3041 | 5.2107 | 0.061642 | 0.17537 | 0.036983 | -0.097212 | 0.080281 | 0.087312 | 0.00314 | 0.033452 | -0.018639 | 0.058502 | -0.043298 | 0.033843
2920.375 | 121.4355 | -5.3467 | 115.9882 | 0.034862 | -0.054257 | -0.012 | -0.043331 | 0.082044 | 0.048956 | -0.067295 | 0.043331 | 0.15706 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.019749 | 0.015141 | 5.3815 | 5.2924 | 5.3347 | 5.3033 | 5.4287 | 5.3956 | 5.2794 | 0.061642 | 0.17537 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.043299 | 0.029264
2922.125 | 121.3303 | -5.0674 | 116.3452 | 0.034862 | -0.049678 | -0.007421 | -0.043331 | 0.086622 | 0.044377 | -0.058139 | 0.047909 | 0.15706 | 0.02325 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 5.1023 | 5.0178 | 5.06 | 5.0241 | 5.1541 | 5.1118 | 5.0093 | 0.06622 | 0.17537 | 0.041561 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.009483 | 0.072237 | -0.034142 | 0.047578
2923.875 | 121.4401 | -5.3467 | 116.0889 | 0.034862 | -0.054257 | -0.002842 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.038752 | 0.16164 | 0.009515 | -0.1201 | 0.048236 | 0.064423 | -0.024328 | 0.010563 | 5.3815 | 5.2924 | 5.3438 | 5.3033 | 5.4287 | 5.3865 | 5.284 | 0.057063 | 0.17995 | 0.027826 | -0.10179 | 0.066547 | 0.082734 | -0.006017 | 0.028874 | -0.009484 | 0.06308 | -0.038721 | 0.033843
2925.625 | 121.431 | -5.6763 | 115.7043 | 0.03944 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.053534 | -0.062717 | 0.038752 | 0.15706 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.028906 | 0.015141 | 5.7157 | 5.6174 | 5.6734 | 5.6329 | 5.7537 | 5.7298 | 5.6136 | 0.057063 | 0.17537 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.010595 | 0.033452 | -0.023218 | 0.067658 | -0.043298 | 0.047578
2927.3125 | 121.4905 | -5.9967 | 115.3976 | 0.025705 | -0.058836 | -0.007421 | -0.043331 | 0.086622 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.064423 | -0.028906 | 0.010563 | 6.0224 | 5.9379 | 5.9893 | 5.9534 | 6.0833 | 6.0411 | 5.934 | 0.057063 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.082734 | -0.010595 | 0.028874 | -0.01864 | 0.067658 | -0.043298 | 0.043
2929.0625 | 121.4951 | -5.9326 | 115.4755 | 0.034862 | -0.049678 | 0.001736 | -0.047909 | 0.086622 | 0.048956 | -0.062717 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 5.9675 | 5.8829 | 5.9344 | 5.8847 | 6.0192 | 5.9816 | 5.8699 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.01864 | 0.06308 | -0.043298 | 0.038422
2930.75 | 121.4355 | -5.5344 | 115.947 | 0.034862 | -0.049678 | 0.001736 | -0.038752 | 0.072888 | 0.048956 | -0.062717 | 0.047909 | 0.15706 | 0.02325 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 5.5692 | 5.4847 | 5.5361 | 5.4956 | 5.6073 | 5.5833 | 5.4716 | 0.06622 | 0.17537 | 0.041561 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.014061 | 0.067658 | -0.03872 | 0.042999
2932.5 | 121.4127 | -5.3192 | 116.185 | 0.044018 | -0.054257 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.16164 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.033484 | 0.015141 | 5.3632 | 5.265 | 5.3164 | 5.2805 | 5.3967 | 5.3682 | 5.2565 | 0.061642 | 0.17995 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.015173 | 0.033452 | -0.014061 | 0.076815 | -0.047877 | 0.042999
2934.2656 | 121.4905 | -4.9576 | 116.4642 | 0.034862 | -0.049678 | -0.002842 | -0.038752 | 0.077466 | 0.044377 | -0.062717 | 0.047909 | 0.15706 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 4.9924 | 4.9079 | 4.9547 | 4.9188 | 5.035 | 5.002 | 4.8949 | 0.06622 | 0.17537 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.004905 | 0.072237 | -0.03872 | 0.038422
2935.9688 | 121.4951 | -4.8981 | 116.597 | 0.030283 | -0.058836 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.1479 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 4.9284 | 4.8392 | 4.8952 | 4.8502 | 4.9755 | 4.9424 | 4.8354 | 0.061642 | 0.16621 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2937.6719 | 121.4676 | -4.7562 | 116.748 | 0.044018 | -0.058836 | -0.002842 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 4.8002 | 4.6973 | 4.7533 | 4.7083 | 4.8382 | 4.8005 | 4.6934 | 0.057063 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.01864 | 0.06308 | -0.03872 | 0.043
2939.4375 | 121.5637 | -4.6005 | 116.8671 | 0.03944 | -0.058836 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.053561 | 0.034174 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 4.64 | 4.5417 | 4.6023 | 4.5572 | 4.678 | 4.6449 | 4.547 | 0.052485 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.023218 | 0.058502 | -0.03872 | 0.043
2941.1406 | 121.4447 | -4.4998 | 117.041 | 0.034862 | -0.049678 | -0.007421 | -0.038752 | 0.082044 | 0.044377 | -0.058139 | 0.043331 | 0.15706 | 0.018672 | -0.11552 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 4.5347 | 4.4501 | 4.4924 | 4.4611 | 4.5819 | 4.5442 | 4.4417 | 0.061642 | 0.17537 | 0.036983 | -0.097212 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.03872 | 0.043
2942.8906 | 121.5408 | -4.1519 | 117.3294 | 0.034862 | -0.054257 | 0.010893 | -0.043331 | 0.086622 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.010563 | 4.1868 | 4.0977 | 4.1628 | 4.1086 | 4.2385 | 4.1917 | 4.0892 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.028874 | -0.009483 | 0.067659 | -0.03872 | 0.038422
2944.5781 | 121.4539 | -4.8981 | 116.6382 | 0.034862 | -0.054257 | -0.002842 | -0.038752 | 0.082044 | 0.058113 | -0.062717 | 0.038752 | 0.15248 | 0.018672 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.010563 | 4.9329 | 4.8438 | 4.8952 | 4.8593 | 4.9801 | 4.9562 | 4.8354 | 0.057063 | 0.17079 | 0.036983 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.028874 | -0.01864 | 0.053923 | -0.03872 | 0.033843
2946.3281 | 121.463 | -3.7765 | 117.8009 | 0.034862 | -0.049678 | 0.001736 | -0.034174 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.10179 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 3.8114 | 3.7269 | 3.7783 | 3.7424 | 3.854 | 3.8209 | 3.7138 | 0.061642 | 0.17079 | 0.032405 | -0.083475 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.014061 | 0.06308 | -0.043298 | 0.033843
2948.0156 | 121.5088 | -2.9022 | 118.6707 | 0.03944 | -0.058836 | -0.002842 | -0.038752 | 0.086622 | 0.044377 | -0.058139 | 0.043331 | 0.16164 | 0.014094 | -0.11094 | 0.06197 | 0.059844 | -0.024328 | 0.015141 | 2.9417 | 2.8434 | 2.8994 | 2.8635 | 2.9888 | 2.9466 | 2.8441 | 0.061642 | 0.17995 | 0.032405 | -0.092633 | 0.080281 | 0.078155 | -0.006017 | 0.033452 | -0.018639 | 0.067659 | -0.047876 | 0.038422
2949.7812 | 121.5958 | -2.4445 | 119.0826 | 0.034862 | -0.054257 | -0.002842 | -0.043331 | 0.072888 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 2.4793 | 2.3902 | 2.4416 | 2.4011 | 2.5173 | 2.4888 | 2.3772 | 0.061642 | 0.17537 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.018639 | 0.06308 | -0.052455 | 0.029264
2951.5312 | 121.4859 | -2.3758 | 119.2383 | 0.030283 | -0.049678 | -0.007421 | -0.043331 | 0.082044 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.018672 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.005985 | 2.4061 | 2.3261 | 2.3684 | 2.3325 | 2.4578 | 2.4156 | 2.3131 | 0.061642 | 0.17995 | 0.036983 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.024296 | -0.018639 | 0.058502 | -0.043298 | 0.033843
2953.2812 | 121.5408 | -2.2751 | 119.3161 | 0.03944 | -0.049678 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 2.3145 | 2.2254 | 2.2722 | 2.2318 | 2.3526 | 2.3149 | 2.2124 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.014062 | 0.06308 | -0.043299 | 0.033843
2954.9844 | 121.5683 | -2.2842 | 119.2932 | 0.034862 | -0.058836 | -0.007421 | -0.052488 | 0.082044 | 0.035221 | -0.067295 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.010563 | 2.3191 | 2.2254 | 2.2768 | 2.2318 | 2.3663 | 2.3195 | 2.2169 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.057033 | 0.024686
2956.6719 | 121.6324 | -2.1744 | 119.3481 | 0.030283 | -0.049678 | -0.002842 | -0.038752 | 0.082044 | 0.053534 | -0.067295 | 0.043331 | 0.16164 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 2.2047 | 2.1247 | 2.1715 | 2.1356 | 2.2564 | 2.2279 | 2.1071 | 0.061642 | 0.17995 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.043298 | 0.033843
2958.4219 | 121.5591 | -2.1561 | 119.458 | 0.034862 | -0.054257 | 0.001736 | -0.043331 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.16164 | 0.009515 | -0.11552 | 0.06197 | 0.064423 | -0.028906 | 0.010563 | 2.1909 | 2.1018 | 2.1578 | 2.1127 | 2.2335 | 2.205 | 2.0934 | 0.061642 | 0.17995 | 0.027826 | -0.097212 | 0.080281 | 0.082734 | -0.010595 | 0.028874 | -0.018639 | 0.072237 | -0.052455 | 0.038421
2960.1875 | 121.6553 | -2.1652 | 119.4077 | 0.025705 | -0.054257 | 0.001736 | -0.043331 | 0.086622 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11552 | 0.048236 | 0.059844 | -0.019749 | 0.015141 | 2.1909 | 2.111 | 2.167 | 2.1219 | 2.2518 | 2.205 | 2.1025 | 0.057063 | 0.17537 | 0.032405 | -0.097212 | 0.066547 | 0.078155 | -0.001438 | 0.033452 | -0.009484 | 0.058501 | -0.034142 | 0.033843
2961.9375 | 121.5179 | -2.2064 | 119.4031 | 0.030283 | -0.054257 | -0.007421 | -0.047909 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 2.2367 | 2.1522 | 2.199 | 2.1585 | 2.2885 | 2.2508 | 2.1483 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.01864 | 0.058501 | -0.047877 | 0.029264
2963.6875 | 121.5958 | -2.0828 | 119.4946 | 0.03944 | -0.054257 | -0.002842 | -0.047909 | 0.086622 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.018672 | -0.10637 | 0.057392 | 0.055266 | -0.015171 | 0.010563 | 2.1223 | 2.0286 | 2.08 | 2.0349 | 2.1694 | 2.1272 | 2.0155 | 0.061642 | 0.17537 | 0.036983 | -0.088054 | 0.075703 | 0.073577 | 0.00314 | 0.028874 | -0.014061 | 0.058502 | -0.03872 | 0.033843
2965.3906 | 121.55 | -2.0599 | 119.5724 | 0.03944 | -0.054257 | -0.007421 | -0.034174 | 0.077466 | 0.048956 | -0.058139 | 0.047909 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 2.0994 | 2.0057 | 2.0525 | 2.0258 | 2.1374 | 2.1089 | 2.0018 | 0.06622 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.009483 | 0.072237 | -0.043298 | 0.038422
2967.1562 | 121.5775 | -2.005 | 119.632 | 0.034862 | -0.054257 | 0.006315 | -0.038752 | 0.086622 | 0.048956 | -0.062717 | 0.038752 | 0.16164 | 0.018672 | -0.11552 | 0.06197 | 0.059844 | -0.019749 | 0.019719 | 2.0399 | 1.9507 | 2.0113 | 1.9663 | 2.0916 | 2.054 | 1.9423 | 0.057063 | 0.17995 | 0.036983 | -0.097212 | 0.080281 | 0.078155 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.043298 | 0.038421
2968.8438 | 121.6095 | -1.8814 | 119.751 | 0.034862 | -0.049678 | -0.002842 | -0.038752 | 0.086622 | 0.048956 | -0.062717 | 0.034174 | 0.16164 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.010563 | 1.9163 | 1.8317 | 1.8786 | 1.8427 | 1.968 | 1.9304 | 1.8187 | 0.052485 | 0.17995 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.028874 | -0.01864 | 0.053923 | -0.03872 | 0.033843
2970.5938 | 121.6003 | -1.8631 | 119.7876 | 0.030283 | -0.049678 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.034174 | 0.15248 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 1.8934 | 1.8134 | 1.8603 | 1.8243 | 1.9406 | 1.9121 | 1.8004 | 0.052485 | 0.17079 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.027796 | 0.053923 | -0.043298 | 0.038421
2972.3438 | 121.6003 | -1.7853 | 119.8608 | 0.034862 | -0.054257 | 0.010893 | -0.038752 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11552 | 0.057392 | 0.059844 | -0.019749 | 0.019719 | 1.8201 | 1.731 | 1.7962 | 1.7465 | 1.8673 | 1.8297 | 1.7271 | 0.057063 | 0.17995 | 0.032405 | -0.097212 | 0.075703 | 0.078155 | -0.001438 | 0.03803 | -0.01864 | 0.058501 | -0.043298 | 0.033843
2974.0938 | 121.6049 | -1.6571 | 119.989 | 0.03944 | -0.049678 | 0.001736 | -0.043331 | 0.077466 | 0.053534 | -0.067295 | 0.043331 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.015171 | 0.010563 | 1.6965 | 1.6074 | 1.6588 | 1.6138 | 1.7346 | 1.7106 | 1.5898 | 0.061642 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | 0.00314 | 0.028874 | -0.014061 | 0.058502 | -0.043298 | 0.029265
2975.7812 | 121.6919 | -1.5518 | 120.0485 | 0.034862 | -0.054257 | -0.007421 | -0.043331 | 0.077466 | 0.044377 | -0.058139 | 0.043331 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 1.5867 | 1.4976 | 1.5444 | 1.5085 | 1.6293 | 1.5962 | 1.4937 | 0.061642 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.043298 | 0.038422
2977.5469 | 121.6187 | -1.593 | 120.0806 | 0.034862 | -0.063415 | -0.002842 | -0.034174 | 0.077466 | 0.044377 | -0.067295 | 0.038752 | 0.16164 | 0.018672 | -0.1201 | 0.06197 | 0.059844 | -0.019749 | 0.010563 | 1.6279 | 1.5296 | 1.5902 | 1.5588 | 1.6705 | 1.6374 | 1.5257 | 0.057063 | 0.17995 | 0.036983 | -0.10179 | 0.080281 | 0.078155 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.043298 | 0.038421
2979.2344 | 121.669 | -1.4923 | 120.163 | 0.030283 | -0.054257 | -0.002842 | -0.038752 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.014094 | -0.11094 | 0.057392 | 0.059844 | -0.015171 | 0.005985 | 1.5226 | 1.4381 | 1.4895 | 1.4536 | 1.5744 | 1.5367 | 1.4296 | 0.057063 | 0.17079 | 0.032405 | -0.092633 | 0.075703 | 0.078155 | 0.00314 | 0.024296 | -0.01864 | 0.053923 | -0.043298 | 0.029265
2980.9219 | 121.6919 | -0.20599 | 121.431 | 0.044018 | -0.049678 | -0.002842 | -0.038752 | 0.077466 | 0.039799 | -0.062717 | 0.034174 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 0.25001 | 0.15632 | 0.20315 | 0.16724 | 0.28346 | 0.24579 | 0.14328 | 0.052485 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.027796 | 0.053923 | -0.052455 | 0.029264
2982.6875 | 121.701 | -0.21515 | 121.4218 | 0.030283 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.048956 | -0.058139 | 0.038752 | 0.14332 | 0.018672 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.024297 | 0.24543 | 0.15631 | 0.21688 | 0.17182 | 0.29719 | 0.26411 | 0.15701 | 0.057063 | 0.16163 | 0.036983 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.042608 | -0.023218 | 0.058501 | -0.043298 | 0.038421
2984.3906 | 121.3577 | -0.22888 | 121.4951 | 0.03944 | -0.058836 | -0.002842 | -0.038752 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.018672 | -0.11552 | 0.06197 | 0.059844 | -0.010593 | 0.024297 | 0.26832 | 0.17005 | 0.22604 | 0.19013 | 0.30635 | 0.27326 | 0.16617 | 0.061642 | 0.17079 | 0.036983 | -0.097212 | 0.080281 | 0.078155 | 0.007718 | 0.042608 | -0.018639 | 0.053924 | -0.043298 | 0.029265
2986.1562 | 121.6415 | -0.23804 | 121.4676 | 0.030283 | -0.054257 | -0.002842 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.018672 | -0.11094 | 0.052814 | 0.055266 | -0.024328 | 0.015141 | 0.26832 | 0.18378 | 0.23519 | 0.19928 | 0.3155 | 0.28241 | 0.17074 | 0.061642 | 0.17079 | 0.036983 | -0.092633 | 0.071125 | 0.073577 | -0.006017 | 0.033452 | -0.009483 | 0.067659 | -0.034142 | 0.043
2987.8594 | 121.7331 | -0.23346 | 121.463 | 0.030283 | -0.063415 | -0.002842 | -0.034174 | 0.077466 | 0.039799 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11552 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 0.26374 | 0.17004 | 0.23062 | 0.19928 | 0.31093 | 0.27326 | 0.17532 | 0.057063 | 0.17995 | 0.032405 | -0.097212 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.047876 | 0.033843
2989.625 | 115.4709 | -45.1813 | 70.1202 | 0.053175 | -0.049678 | 0.010893 | -0.029595 | 0.10036 | 0.062691 | -0.044405 | 0.061645 | 0.17537 | 0.027829 | -0.12468 | 0.052814 | 0.04611 | -0.028906 | 0.001406 | 45.2344 | 45.1316 | 45.1922 | 45.1517 | 45.2816 | 45.244 | 45.1369 | 0.079956 | 0.19368 | 0.04614 | -0.10637 | 0.071125 | 0.064421 | -0.010595 | 0.019717 | 0.008831 | 0.090551 | -0.024985 | 0.056735
2991.375 | 120.575 | -0.18768 | 120.5017 | 0.03944 | -0.063415 | -0.007421 | -0.043331 | 0.072888 | 0.048956 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.11552 | 0.057392 | 0.064423 | -0.019749 | 0.005985 | 0.22712 | 0.12427 | 0.18026 | 0.14435 | 0.26057 | 0.23664 | 0.12497 | 0.061642 | 0.17995 | 0.032405 | -0.097212 | 0.075703 | 0.082734 | -0.001438 | 0.024296 | -0.014061 | 0.06308 | -0.043298 | 0.033843
2993.0781 | 120.845 | -0.16022 | 120.6528 | 0.030283 | -0.054257 | -0.007421 | -0.043331 | 0.077466 | 0.048956 | -0.053561 | 0.038752 | 0.16164 | 0.004937 | -0.10637 | 0.057392 | 0.069001 | -0.024328 | 0.005985 | 0.1905 | 0.10596 | 0.1528 | 0.11689 | 0.23768 | 0.20917 | 0.10666 | 0.057063 | 0.17995 | 0.023248 | -0.088054 | 0.075703 | 0.087312 | -0.006017 | 0.024296 | -0.01864 | 0.06308 | -0.052455 | 0.029265
2994.7812 | 120.8038 | -0.76446 | 120.1904 | 0.03944 | -0.058836 | -0.007421 | -0.034174 | 0.086622 | 0.044377 | -0.058139 | 0.043331 | 0.15248 | 0.018672 | -0.11094 | 0.057392 | 0.059844 | -0.028906 | 0.010563 | 0.8039 | 0.70563 | 0.75704 | 0.73029 | 0.85109 | 0.80884 | 0.70633 | 0.061642 | 0.17079 | 0.036983 | -0.092633 | 0.075703 | 0.078155 | -0.010595 | 0.028874 | -0.014061 | 0.072237 | -0.03872 | 0.047578
2996.5312 | 120.9869 | -0.6134 | 120.2911 | 0.030283 | -0.058836 | -0.016578 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.048236 | 0.064423 | -0.019749 | 0.015141 | 0.64369 | 0.55457 | 0.59683 | 0.57465 | 0.69087 | 0.66236 | 0.55069 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.066547 | 0.082734 | -0.001438 | 0.033452 | -0.009484 | 0.058501 | -0.043299 | 0.024686
2998.2344 | 120.9274 | -0.65002 | 120.4056 | 0.034862 | -0.054257 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.053561 | 0.038752 | 0.15706 | 0.004937 | -0.10179 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 0.68489 | 0.59577 | 0.65176 | 0.60669 | 0.72749 | 0.6944 | 0.59646 | 0.057063 | 0.17537 | 0.023248 | -0.083475 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.01864 | 0.06308 | -0.052455 | 0.029265
2999.9844 | 121.1014 | -0.56305 | 120.4651 | 0.034862 | -0.058836 | -0.007421 | -0.034174 | 0.082044 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.064423 | -0.028906 | 0.015141 | 0.59791 | 0.50421 | 0.55563 | 0.52887 | 0.64509 | 0.60743 | 0.49575 | 0.061642 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.082734 | -0.010595 | 0.033452 | -0.014061 | 0.072237 | -0.03872 | 0.047578
3001.6875 | 121.0327 | -0.54932 | 120.5566 | 0.03944 | -0.058836 | -0.002842 | -0.038752 | 0.072888 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.050688 | -0.028906 | 0.019719 | 0.58876 | 0.49048 | 0.54647 | 0.51056 | 0.6222 | 0.59827 | 0.4866 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.068999 | -0.010595 | 0.03803 | -0.023218 | 0.067658 | -0.052455 | 0.038421
3003.4375 | 121.1609 | -0.45776 | 120.6482 | 0.030283 | -0.058836 | -0.002842 | -0.034174 | 0.082044 | 0.044377 | -0.067295 | 0.034174 | 0.16164 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 0.48805 | 0.39893 | 0.45492 | 0.42359 | 0.53981 | 0.50214 | 0.39047 | 0.052485 | 0.17995 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.027796 | 0.058502 | -0.052455 | 0.033843
3005.125 | 121.1609 | -0.42114 | 120.6802 | 0.025705 | -0.058836 | -0.002842 | -0.038752 | 0.082044 | 0.039799 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.064423 | -0.028906 | 0.019719 | 0.44685 | 0.36231 | 0.4183 | 0.38239 | 0.50319 | 0.46094 | 0.35385 | 0.057063 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.082734 | -0.010595 | 0.03803 | -0.023218 | 0.067658 | -0.052455 | 0.038421
3006.8906 | 121.2158 | -0.4303 | 120.7031 | 0.030283 | -0.058836 | -0.007421 | -0.038752 | 0.077466 | 0.053534 | -0.067295 | 0.034174 | 0.16622 | 0.018672 | -0.11094 | 0.052814 | 0.064423 | -0.019749 | 0.010563 | 0.46058 | 0.37146 | 0.42288 | 0.39155 | 0.50776 | 0.48383 | 0.363 | 0.052485 | 0.18453 | 0.036983 | -0.092633 | 0.071125 | 0.082734 | -0.001438 | 0.028874 | -0.01864 | 0.053923 | -0.034142 | 0.038421
3008.6406 | 121.1243 | -0.48981 | 120.7352 | 0.034862 | -0.054257 | -0.002842 | -0.038752 | 0.082044 | 0.039799 | -0.058139 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 0.52467 | 0.43555 | 0.48696 | 0.45105 | 0.57185 | 0.52961 | 0.43167 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.047876 | 0.033843
3010.3906 | 121.2341 | -0.44861 | 120.7352 | 0.044018 | -0.067994 | -0.002842 | -0.043331 | 0.072888 | 0.044377 | -0.058139 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.066548 | 0.064423 | -0.015171 | 0.015141 | 0.49263 | 0.38061 | 0.44577 | 0.40528 | 0.5215 | 0.49299 | 0.39047 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.084859 | 0.082734 | 0.00314 | 0.033452 | -0.027796 | 0.053923 | -0.052454 | 0.029265
3012.0938 | 121.2479 | -0.35706 | 120.7901 | 0.034862 | -0.054257 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.064423 | -0.028906 | 0.015141 | 0.39192 | 0.3028 | 0.35879 | 0.31372 | 0.43452 | 0.40143 | 0.28976 | 0.057063 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.082734 | -0.010595 | 0.033452 | -0.014062 | 0.067658 | -0.03872 | 0.043
3013.8438 | 121.1746 | -0.43945 | 120.8038 | 0.044018 | -0.058836 | -0.002842 | -0.034174 | 0.0912 | 0.044377 | -0.067295 | 0.034174 | 0.15706 | 0.009515 | -0.11552 | 0.06197 | 0.064423 | -0.015171 | 0.019719 | 0.48347 | 0.38062 | 0.43661 | 0.40528 | 0.53065 | 0.48383 | 0.37216 | 0.052485 | 0.17537 | 0.027826 | -0.097212 | 0.080281 | 0.082734 | 0.00314 | 0.03803 | -0.027796 | 0.049345 | -0.052455 | 0.024686
3015.5781 | 121.225 | -0.40741 | 120.8771 | 0.03944 | -0.054257 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 0.44685 | 0.35315 | 0.40457 | 0.36866 | 0.48488 | 0.45637 | 0.34469 | 0.061642 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.067659 | -0.047877 | 0.033843
3017.2812 | 121.2341 | -0.42572 | 120.8496 | 0.03944 | -0.049678 | -0.002842 | -0.034174 | 0.072888 | 0.044377 | -0.062717 | 0.034174 | 0.15248 | 0.014094 | -0.11094 | 0.06197 | 0.069001 | -0.019749 | 0.005985 | 0.46516 | 0.37604 | 0.42288 | 0.39155 | 0.49861 | 0.4701 | 0.363 | 0.052485 | 0.17079 | 0.032405 | -0.092633 | 0.080281 | 0.087312 | -0.001438 | 0.024296 | -0.027796 | 0.053923 | -0.047876 | 0.033843
3019.0312 | 121.2936 | -0.42114 | 120.8725 | 0.030283 | -0.058836 | -0.007421 | -0.043331 | 0.082044 | 0.044377 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.10637 | 0.052814 | 0.059844 | -0.024328 | 0.010563 | 0.45143 | 0.36231 | 0.41372 | 0.37781 | 0.50319 | 0.46552 | 0.35385 | 0.052485 | 0.17537 | 0.032405 | -0.088054 | 0.071125 | 0.078155 | -0.006017 | 0.028874 | -0.01864 | 0.058502 | -0.03872 | 0.038422
3020.7344 | 121.225 | -0.43945 | 120.8862 | 0.034862 | -0.049678 | -0.012 | -0.043331 | 0.086622 | 0.048956 | -0.067295 | 0.038752 | 0.15706 | 0.018672 | -0.10637 | 0.052814 | 0.064423 | -0.015171 | 0.015141 | 0.47431 | 0.38977 | 0.42745 | 0.39612 | 0.52607 | 0.48841 | 0.37216 | 0.057063 | 0.17537 | 0.036983 | -0.088054 | 0.071125 | 0.082734 | 0.00314 | 0.033452 | -0.014062 | 0.053923 | -0.034142 | 0.033843
3022.5 | 121.2845 | -0.54016 | 120.7809 | 0.030283 | -0.054257 | 0.001736 | -0.034174 | 0.082044 | 0.035221 | -0.058139 | 0.047909 | 0.15248 | 0.014094 | -0.10179 | 0.057392 | 0.055266 | -0.019749 | 0.015141 | 0.57044 | 0.4859 | 0.5419 | 0.50599 | 0.62221 | 0.57538 | 0.48202 | 0.06622 | 0.17079 | 0.032405 | -0.083475 | 0.075703 | 0.073577 | -0.001438 | 0.033452 | -0.009483 | 0.067658 | -0.043298 | 0.033843
3024.2656 | 121.3715 | -0.48523 | 120.8176 | 0.030283 | -0.054257 | -0.007421 | -0.047909 | 0.086622 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.066548 | 0.069001 | -0.019749 | 0.015141 | 0.51551 | 0.43097 | 0.47781 | 0.43732 | 0.57185 | 0.52961 | 0.42251 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.084859 | 0.087312 | -0.001438 | 0.033452 | -0.027796 | 0.058501 | -0.057033 | 0.029264
3026.0312 | 121.4127 | -0.43488 | 120.8954 | 0.034862 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.16164 | 0.009515 | -0.10179 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 0.46974 | 0.37604 | 0.43203 | 0.39154 | 0.51234 | 0.47467 | 0.37216 | 0.057063 | 0.17995 | 0.027826 | -0.083475 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.047877 | 0.029264
3027.7188 | 121.4035 | -0.46692 | 120.8496 | 0.044018 | -0.063415 | 0.001736 | -0.038752 | 0.082044 | 0.039799 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.028906 | 0.024297 | 0.51094 | 0.4035 | 0.46865 | 0.42817 | 0.54896 | 0.50672 | 0.4042 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.010595 | 0.042608 | -0.009483 | 0.072237 | -0.03872 | 0.043
3029.4688 | 121.3257 | -0.43488 | 120.9732 | 0.03944 | -0.058836 | 0.006315 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.16164 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 0.47432 | 0.37604 | 0.44119 | 0.39154 | 0.51234 | 0.47925 | 0.37216 | 0.057063 | 0.17995 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.043298 | 0.033843
3031.2344 | 121.4539 | -0.37537 | 120.9457 | 0.030283 | -0.054257 | -0.007421 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.043331 | 0.1479 | 0.018672 | -0.11552 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 0.40565 | 0.32111 | 0.36794 | 0.33661 | 0.45283 | 0.41974 | 0.30807 | 0.061642 | 0.16621 | 0.036983 | -0.097212 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.03872 | 0.038421
3032.9844 | 121.3486 | -0.43488 | 121.0236 | 0.03944 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.034174 | 0.16622 | 0.014094 | -0.11552 | 0.052814 | 0.069001 | -0.024328 | 0.010563 | 0.47432 | 0.37604 | 0.43203 | 0.39154 | 0.51234 | 0.47925 | 0.37216 | 0.052485 | 0.18453 | 0.032405 | -0.097212 | 0.071125 | 0.087312 | -0.006017 | 0.028874 | -0.01864 | 0.058502 | -0.03872 | 0.038422
3034.75 | 121.344 | -0.37079 | 121.0785 | 0.034862 | -0.049678 | -0.007421 | -0.043331 | 0.086622 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.10637 | 0.06197 | 0.055266 | -0.024328 | 0.010563 | 0.40565 | 0.32111 | 0.36337 | 0.32746 | 0.45741 | 0.41517 | 0.30807 | 0.057063 | 0.17537 | 0.027826 | -0.088054 | 0.080281 | 0.073577 | -0.006017 | 0.028874 | -0.023218 | 0.06308 | -0.052455 | 0.033843
3036.4531 | 121.3303 | -0.3891 | 121.0693 | 0.034862 | -0.049678 | 0.001736 | -0.034174 | 0.082044 | 0.053534 | -0.067295 | 0.038752 | 0.16164 | 0.014094 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 0.42396 | 0.33942 | 0.39083 | 0.35492 | 0.47114 | 0.44263 | 0.3218 | 0.057063 | 0.17995 | 0.032405 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.047876 | 0.033843
3038.2031 | 121.4218 | -0.28839 | 121.1334 | 0.03944 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 0.32783 | 0.22956 | 0.28555 | 0.24506 | 0.36586 | 0.33277 | 0.22567 | 0.061642 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.043298 | 0.038422
3039.9531 | 121.4813 | -0.27924 | 121.1151 | 0.030283 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 0.30952 | 0.2204 | 0.28097 | 0.2359 | 0.36128 | 0.32361 | 0.21652 | 0.061642 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.014061 | 0.06308 | -0.03872 | 0.038421
3041.7031 | 121.4493 | -0.37537 | 121.0327 | 0.034862 | -0.054257 | -0.002842 | -0.043331 | 0.082044 | 0.039799 | -0.067295 | 0.034174 | 0.16164 | 0.014094 | -0.11552 | 0.066548 | 0.059844 | -0.019749 | 0.015141 | 0.41023 | 0.32111 | 0.37252 | 0.33203 | 0.45741 | 0.41517 | 0.30807 | 0.052485 | 0.17995 | 0.032405 | -0.097212 | 0.084859 | 0.078155 | -0.001438 | 0.033452 | -0.032374 | 0.053923 | -0.052454 | 0.033843
3043.4531 | 121.4401 | -0.40283 | 121.0236 | 0.034862 | -0.058836 | 0.001736 | -0.038752 | 0.072888 | 0.035221 | -0.062717 | 0.043331 | 0.16164 | 0.018672 | -0.11094 | 0.057392 | 0.069001 | -0.019749 | 0.010563 | 0.43769 | 0.344 | 0.40457 | 0.36408 | 0.47572 | 0.43805 | 0.34012 | 0.061642 | 0.17995 | 0.036983 | -0.092633 | 0.075703 | 0.087312 | -0.001438 | 0.028874 | -0.014061 | 0.06308 | -0.03872 | 0.038421
3045.2031 | 121.3852 | -0.39825 | 121.1014 | 0.034862 | -0.054257 | -0.002842 | -0.038752 | 0.072888 | 0.039799 | -0.058139 | 0.034174 | 0.15706 | 0.014094 | -0.10637 | 0.052814 | 0.069001 | -0.019749 | 0.019719 | 0.43312 | 0.344 | 0.39541 | 0.3595 | 0.47114 | 0.43805 | 0.34012 | 0.052485 | 0.17537 | 0.032405 | -0.088054 | 0.071125 | 0.087312 | -0.001438 | 0.03803 | -0.01864 | 0.053923 | -0.03872 | 0.033843
3046.9062 | 121.5042 | -0.3479 | 121.0968 | 0.030283 | -0.058836 | -0.002842 | -0.052488 | 0.072888 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.010563 | 0.37818 | 0.28906 | 0.34506 | 0.29541 | 0.42079 | 0.39228 | 0.28518 | 0.061642 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.028874 | -0.014061 | 0.06308 | -0.047877 | 0.029264
3048.6562 | 121.4584 | -0.2243 | 121.2845 | 0.034862 | -0.058836 | 0.001736 | -0.034174 | 0.077466 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.024328 | 0.019719 | 0.25917 | 0.16547 | 0.22604 | 0.19013 | 0.30177 | 0.2641 | 0.16159 | 0.061642 | 0.17995 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.006017 | 0.03803 | -0.009483 | 0.067659 | -0.03872 | 0.038422
3050.4219 | 121.5363 | -0.17853 | 121.2616 | 0.034862 | -0.054257 | -0.002842 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.064423 | -0.028906 | 0.010563 | 0.21339 | 0.12427 | 0.17569 | 0.13978 | 0.25599 | 0.2229 | 0.11123 | 0.061642 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.082734 | -0.010595 | 0.028874 | -0.009483 | 0.072237 | -0.03872 | 0.043
3052.1875 | 121.5271 | -0.17395 | 121.2845 | 0.03944 | -0.058836 | -0.002842 | -0.034174 | 0.077466 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.010563 | 0.21339 | 0.11511 | 0.17111 | 0.13978 | 0.25142 | 0.21833 | 0.10665 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.052455 | 0.029264
3053.875 | 121.4218 | -0.22888 | 121.3303 | 0.03944 | -0.058836 | -0.007421 | -0.034174 | 0.082044 | 0.053534 | -0.058139 | 0.043331 | 0.15706 | 0.018672 | -0.11094 | 0.066548 | 0.064423 | -0.019749 | 0.015141 | 0.26832 | 0.17005 | 0.22146 | 0.19471 | 0.31093 | 0.28242 | 0.17074 | 0.061642 | 0.17537 | 0.036983 | -0.092633 | 0.084859 | 0.082734 | -0.001438 | 0.033452 | -0.023217 | 0.06308 | -0.047876 | 0.038421
3055.6094 | 121.55 | -0.16937 | 121.3211 | 0.03944 | -0.054257 | 0.006315 | -0.034174 | 0.082044 | 0.039799 | -0.058139 | 0.038752 | 0.16164 | 0.004937 | -0.11094 | 0.048236 | 0.059844 | -0.024328 | 0.010563 | 0.20881 | 0.11512 | 0.17569 | 0.1352 | 0.25142 | 0.20917 | 0.11123 | 0.057063 | 0.17995 | 0.023248 | -0.092633 | 0.066547 | 0.078155 | -0.006017 | 0.028874 | -0.009484 | 0.06308 | -0.043299 | 0.029265
3057.3125 | 121.4172 | -0.23804 | 121.3486 | 0.03944 | -0.054257 | 0.006315 | -0.038752 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 0.27748 | 0.18378 | 0.24435 | 0.19928 | 0.32008 | 0.28241 | 0.1799 | 0.057063 | 0.17995 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.043298 | 0.038422
3059.0625 | 121.4905 | -0.21973 | 121.3348 | 0.034862 | -0.058836 | -0.002842 | -0.038752 | 0.082044 | 0.044377 | -0.062717 | 0.034174 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.028906 | 0.010563 | 0.25459 | 0.16089 | 0.21688 | 0.18097 | 0.30177 | 0.2641 | 0.15701 | 0.052485 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.010595 | 0.028874 | -0.01864 | 0.06308 | -0.03872 | 0.043
3060.8125 | 121.4127 | -0.23804 | 121.2982 | 0.034862 | -0.063415 | -0.007421 | -0.043331 | 0.072888 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11552 | 0.06197 | 0.059844 | -0.024328 | 0.019719 | 0.2729 | 0.17462 | 0.23062 | 0.19471 | 0.31093 | 0.28241 | 0.1799 | 0.057063 | 0.17995 | 0.032405 | -0.097212 | 0.080281 | 0.078155 | -0.006017 | 0.03803 | -0.023218 | 0.06308 | -0.047876 | 0.038422
3062.5781 | 121.5546 | -0.24719 | 121.2662 | 0.030283 | -0.063415 | -0.002842 | -0.043331 | 0.082044 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.015141 | 0.27747 | 0.18378 | 0.24435 | 0.20386 | 0.32924 | 0.29615 | 0.18448 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.047877 | 0.029264
3064.2656 | 115.9744 | -40.036 | 75.737 | 0.048597 | -0.049678 | 0.010893 | -0.029595 | 0.086622 | 0.053534 | -0.048983 | 0.052488 | 0.16622 | 0.02325 | -0.1201 | 0.052814 | 0.055266 | -0.033484 | 0.010563 | 40.0846 | 39.9863 | 40.0469 | 40.0064 | 40.1226 | 40.0895 | 39.987 | 0.070799 | 0.18453 | 0.041561 | -0.10179 | 0.071125 | 0.073577 | -0.015173 | 0.028874 | -0.000326 | 0.085972 | -0.029564 | 0.056734
3066.0156 | 120.5292 | -0.13275 | 120.4239 | 0.030283 | -0.063415 | 0.001736 | -0.043331 | 0.06831 | 0.044377 | -0.067295 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 0.16303 | 0.069336 | 0.13449 | 0.08942 | 0.20106 | 0.17713 | 0.065456 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.018639 | 0.06308 | -0.052455 | 0.029264
3067.7031 | 120.6848 | -0.20142 | 120.6619 | 0.030283 | -0.058836 | -0.007421 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.018672 | -0.11094 | 0.066548 | 0.064423 | -0.019749 | 0.015141 | 0.2317 | 0.14258 | 0.194 | 0.15809 | 0.27888 | 0.24579 | 0.1387 | 0.057063 | 0.17079 | 0.036983 | -0.092633 | 0.084859 | 0.082734 | -0.001438 | 0.033452 | -0.027796 | 0.058501 | -0.047876 | 0.038421
3069.4531 | 120.9045 | -0.14648 | 120.6848 | 0.030283 | -0.067994 | 0.001736 | -0.038752 | 0.072888 | 0.039799 | -0.067295 | 0.038752 | 0.15706 | 0.004937 | -0.11094 | 0.057392 | 0.073579 | -0.019749 | 0.024297 | 0.17677 | 0.07849 | 0.14822 | 0.10773 | 0.21937 | 0.18628 | 0.079189 | 0.057063 | 0.17537 | 0.023248 | -0.092633 | 0.075703 | 0.09189 | -0.001438 | 0.042608 | -0.01864 | 0.058501 | -0.052455 | 0.024686
3071.1875 | 120.8359 | -0.1831 | 120.813 | 0.034862 | -0.058836 | -0.002842 | -0.038752 | 0.072888 | 0.044377 | -0.062717 | 0.034174 | 0.14332 | 0.009515 | -0.10637 | 0.06197 | 0.069001 | -0.024328 | 0.005985 | 0.21797 | 0.12427 | 0.18026 | 0.14435 | 0.25599 | 0.22748 | 0.12039 | 0.052485 | 0.16163 | 0.027826 | -0.088054 | 0.080281 | 0.087312 | -0.006017 | 0.024296 | -0.027796 | 0.058502 | -0.052455 | 0.033843
3072.9531 | 120.8908 | -0.17853 | 120.8405 | 0.025705 | -0.067994 | -0.007421 | -0.038752 | 0.06831 | 0.044377 | -0.067295 | 0.029595 | 0.15706 | 0.004937 | -0.10637 | 0.06197 | 0.069001 | -0.019749 | 0.024297 | 0.20423 | 0.11053 | 0.17111 | 0.13978 | 0.24684 | 0.2229 | 0.11123 | 0.047906 | 0.17537 | 0.023248 | -0.088054 | 0.080281 | 0.087312 | -0.001438 | 0.042608 | -0.032375 | 0.049344 | -0.057033 | 0.024686
3074.6562 | 121.0464 | -0.1236 | 120.8176 | 0.025705 | -0.067994 | -0.007421 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.004937 | -0.10637 | 0.057392 | 0.069001 | -0.015171 | 0.019719 | 0.1493 | 0.055602 | 0.11618 | 0.080265 | 0.19648 | 0.16797 | 0.060879 | 0.057063 | 0.17079 | 0.023248 | -0.088054 | 0.075703 | 0.087312 | 0.00314 | 0.03803 | -0.01864 | 0.053923 | -0.052455 | 0.020108
3076.4062 | 120.9457 | -0.19226 | 120.9091 | 0.030283 | -0.063415 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.020438 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.010563 | 0.22254 | 0.12885 | 0.18942 | 0.14435 | 0.26515 | 0.23664 | 0.12954 | 0.038749 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.028874 | -0.032376 | 0.044766 | -0.03872 | 0.038422
3078.1562 | 121.0373 | -0.16937 | 120.9274 | 0.030283 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.048956 | -0.062717 | 0.034174 | 0.14332 | 0.004937 | -0.1201 | 0.071126 | 0.059844 | -0.019749 | 0.015141 | 0.19966 | 0.10596 | 0.16653 | 0.12604 | 0.24684 | 0.21833 | 0.10666 | 0.052485 | 0.16163 | 0.023248 | -0.10179 | 0.089437 | 0.078155 | -0.001438 | 0.033452 | -0.036952 | 0.053923 | -0.066189 | 0.024686
3079.9219 | 121.0968 | -0.16937 | 120.9229 | 0.030283 | -0.067994 | 0.001736 | -0.047909 | 0.072888 | 0.035221 | -0.062717 | 0.034174 | 0.16622 | 0.009515 | -0.11094 | 0.057392 | 0.073579 | -0.024328 | 0.010563 | 0.19966 | 0.10138 | 0.17111 | 0.12146 | 0.24226 | 0.20459 | 0.10666 | 0.052485 | 0.18453 | 0.027826 | -0.092633 | 0.075703 | 0.09189 | -0.006017 | 0.028874 | -0.023218 | 0.058502 | -0.047877 | 0.033843
3081.6875 | 121.1655 | -0.12817 | 120.932 | 0.030283 | -0.063415 | -0.002842 | -0.047909 | 0.077466 | 0.039799 | -0.067295 | 0.043331 | 0.15248 | 0.014094 | -0.11094 | 0.06197 | 0.073579 | -0.024328 | 0.010563 | 0.15846 | 0.064759 | 0.12533 | 0.080265 | 0.20564 | 0.16797 | 0.060879 | 0.061642 | 0.17079 | 0.032405 | -0.092633 | 0.080281 | 0.09189 | -0.006017 | 0.028874 | -0.018639 | 0.067659 | -0.047876 | 0.038422
3083.375 | 121.0831 | -0.18768 | 120.9732 | 0.03944 | -0.058836 | -0.007421 | -0.038752 | 0.077466 | 0.039799 | -0.058139 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.066548 | 0.069001 | -0.019749 | 0.015141 | 0.22712 | 0.12885 | 0.18026 | 0.14893 | 0.26515 | 0.22748 | 0.12954 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.084859 | 0.087312 | -0.001438 | 0.033452 | -0.032374 | 0.053923 | -0.052454 | 0.033843
3085.125 | 121.1105 | -0.18768 | 121.0144 | 0.034862 | -0.067994 | -0.007421 | -0.043331 | 0.086622 | 0.039799 | -0.062717 | 0.038752 | 0.15706 | 0.018672 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 0.22254 | 0.11969 | 0.18026 | 0.14435 | 0.27431 | 0.22748 | 0.12497 | 0.057063 | 0.17537 | 0.036983 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.043298 | 0.038421
3086.8906 | 121.1197 | -0.26093 | 120.9732 | 0.034862 | -0.058836 | -0.007421 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.15706 | 0.018672 | -0.11552 | 0.066548 | 0.069001 | -0.019749 | 0.019719 | 0.29579 | 0.20209 | 0.2535 | 0.21759 | 0.33839 | 0.30072 | 0.19363 | 0.052485 | 0.17537 | 0.036983 | -0.097212 | 0.084859 | 0.087312 | -0.001438 | 0.03803 | -0.032374 | 0.053923 | -0.047876 | 0.038421
3088.5781 | 121.1288 | -0.26093 | 120.9869 | 0.034862 | -0.063415 | -0.007421 | -0.043331 | 0.072888 | 0.044377 | -0.071874 | 0.043331 | 0.15248 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.005985 | 0.29579 | 0.19751 | 0.2535 | 0.21759 | 0.33381 | 0.3053 | 0.18905 | 0.061642 | 0.17079 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.024296 | -0.014061 | 0.058502 | -0.047877 | 0.024686
3090.3281 | 121.257 | -0.18768 | 121.0144 | 0.030283 | -0.067994 | -0.002842 | -0.038752 | 0.077466 | 0.039799 | -0.067295 | 0.034174 | 0.1479 | 0.014094 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.019719 | 0.21797 | 0.11969 | 0.18484 | 0.14893 | 0.26515 | 0.22748 | 0.12039 | 0.052485 | 0.16621 | 0.032405 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.03803 | -0.027796 | 0.058502 | -0.047876 | 0.038422
3092.0312 | 121.1243 | -0.23346 | 121.051 | 0.025705 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 0.25916 | 0.17004 | 0.23062 | 0.19013 | 0.31093 | 0.27326 | 0.17074 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.047876 | 0.033843
3093.7812 | 121.3028 | -0.1831 | 121.0144 | 0.034862 | -0.063415 | -0.002842 | -0.043331 | 0.082044 | 0.039799 | -0.067295 | 0.034174 | 0.15706 | 0.009515 | -0.11094 | 0.06197 | 0.069001 | -0.010593 | 0.019719 | 0.21797 | 0.11969 | 0.18026 | 0.13977 | 0.26515 | 0.2229 | 0.11581 | 0.052485 | 0.17537 | 0.027826 | -0.092633 | 0.080281 | 0.087312 | 0.007718 | 0.03803 | -0.027796 | 0.044767 | -0.052455 | 0.020108
3095.5312 | 121.2753 | -0.2243 | 121.0602 | 0.025705 | -0.067994 | -0.007421 | -0.038752 | 0.077466 | 0.044377 | -0.071874 | 0.038752 | 0.15706 | 0.004937 | -0.11552 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 0.25001 | 0.15631 | 0.21688 | 0.18555 | 0.30177 | 0.26868 | 0.15243 | 0.057063 | 0.17537 | 0.023248 | -0.097212 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.052455 | 0.029265
3097.2188 | 121.1563 | -0.25177 | 121.0602 | 0.025705 | -0.063415 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.062717 | 0.043331 | 0.15248 | 0.009515 | -0.10637 | 0.066548 | 0.064423 | -0.015171 | 0.015141 | 0.27747 | 0.18835 | 0.24893 | 0.20386 | 0.32466 | 0.29615 | 0.18905 | 0.061642 | 0.17079 | 0.027826 | -0.088054 | 0.084859 | 0.082734 | 0.00314 | 0.033452 | -0.023217 | 0.058502 | -0.057033 | 0.024686
3098.9688 | 121.2433 | -0.23346 | 121.0785 | 0.034862 | -0.058836 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.062717 | 0.034174 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.015141 | 0.26832 | 0.17462 | 0.23062 | 0.19013 | 0.31093 | 0.27784 | 0.17074 | 0.052485 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.033452 | -0.023218 | 0.049345 | -0.047877 | 0.024686
3100.6562 | 121.1884 | -0.22888 | 121.1472 | 0.034862 | -0.067994 | -0.002842 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.038752 | 0.15706 | 0.009515 | -0.10637 | 0.052814 | 0.069001 | -0.028906 | 0.010563 | 0.26374 | 0.16089 | 0.22604 | 0.19013 | 0.30635 | 0.27326 | 0.16159 | 0.057063 | 0.17537 | 0.027826 | -0.088054 | 0.071125 | 0.087312 | -0.010595 | 0.028874 | -0.014062 | 0.067658 | -0.043299 | 0.038421
3102.4219 | 120.2316 | -82.8644 | 37.1292 | 0.062332 | -0.035942 | 0.024629 | -0.011281 | 0.10493 | 0.071848 | -0.039826 | 0.070802 | 0.18453 | 0.036985 | -0.1201 | 0.048236 | 0.036954 | -0.033484 | -0.00775 | 82.9267 | 82.8284 | 82.889 | 82.8531 | 82.9693 | 82.9362 | 82.8246 | 0.089113 | 0.20284 | 0.055296 | -0.10179 | 0.066547 | 0.055265 | -0.015173 | 0.010561 | 0.022566 | 0.10429 | -0.011251 | 0.070469
3104.1719 | 120.6894 | -8.757 | 112.1979 | 0.03944 | -0.063415 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.1201 | 0.066548 | 0.059844 | -0.033484 | 0.015141 | 8.7965 | 8.6936 | 8.7542 | 8.7183 | 8.8345 | 8.806 | 8.6943 | 0.061642 | 0.17995 | 0.032405 | -0.10179 | 0.084859 | 0.078155 | -0.015173 | 0.033452 | -0.023217 | 0.076815 | -0.052454 | 0.047578
3105.9219 | 121.0693 | -7.8461 | 113.2004 | 0.030283 | -0.063415 | 0.006315 | -0.038752 | 0.082044 | 0.044377 | -0.067295 | 0.038752 | 0.16164 | 0.014094 | -0.10179 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 7.8764 | 7.7827 | 7.8524 | 7.8073 | 7.9281 | 7.8904 | 7.7788 | 0.057063 | 0.17995 | 0.032405 | -0.083475 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.043298 | 0.038422
3107.6875 | 121.019 | -7.3425 | 113.8458 | 0.03944 | -0.063415 | -0.002842 | -0.034174 | 0.077466 | 0.058113 | -0.062717 | 0.038752 | 0.16164 | 0.018672 | -0.11552 | 0.06197 | 0.064423 | -0.015171 | 0.015141 | 7.382 | 7.2791 | 7.3397 | 7.3084 | 7.42 | 7.4006 | 7.2798 | 0.057063 | 0.17995 | 0.036983 | -0.097212 | 0.080281 | 0.082734 | 0.00314 | 0.033452 | -0.023218 | 0.053923 | -0.043298 | 0.033843
3109.4375 | 121.1288 | -6.1478 | 114.9216 | 0.030283 | -0.067994 | -0.007421 | -0.038752 | 0.077466 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.018672 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 6.178 | 6.0798 | 6.1403 | 6.109 | 6.2252 | 6.1921 | 6.085 | 0.057063 | 0.17079 | 0.036983 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.01864 | 0.058501 | -0.03872 | 0.038421
3111.125 | 121.17 | -6.2576 | 114.8804 | 0.025705 | -0.063415 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.067295 | 0.034174 | 0.14332 | 0.009515 | -0.11552 | 0.057392 | 0.059844 | -0.024328 | 0.019719 | 6.2833 | 6.1942 | 6.2548 | 6.2189 | 6.3351 | 6.3066 | 6.1903 | 0.052485 | 0.16163 | 0.027826 | -0.097212 | 0.075703 | 0.078155 | -0.006017 | 0.03803 | -0.023218 | 0.058502 | -0.047877 | 0.033843
3112.8906 | 121.2112 | -6.1386 | 115.036 | 0.034862 | -0.063415 | 0.001736 | -0.038752 | 0.072888 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.010563 | 6.1735 | 6.0752 | 6.1403 | 6.0999 | 6.2115 | 6.1876 | 6.0759 | 0.057063 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.028874 | -0.014062 | 0.06308 | -0.043299 | 0.033843
3114.6562 | 121.257 | -6.0471 | 115.0864 | 0.044018 | -0.067994 | 0.001736 | -0.047909 | 0.077466 | 0.048956 | -0.067295 | 0.038752 | 0.15706 | 0.004937 | -0.11094 | 0.052814 | 0.059844 | -0.028906 | 0.015141 | 6.0911 | 5.9791 | 6.0488 | 5.9991 | 6.1245 | 6.096 | 5.9798 | 0.057063 | 0.17537 | 0.023248 | -0.092633 | 0.071125 | 0.078155 | -0.010595 | 0.033452 | -0.014062 | 0.067658 | -0.047877 | 0.033843
3116.3438 | 121.2708 | -6.0287 | 115.155 | 0.034862 | -0.058836 | -0.002842 | -0.038752 | 0.086622 | 0.044377 | -0.058139 | 0.034174 | 0.15706 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.019749 | 0.015141 | 6.0636 | 5.9699 | 6.0259 | 5.99 | 6.1154 | 6.0731 | 5.9706 | 0.052485 | 0.17537 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | -0.001438 | 0.033452 | -0.01864 | 0.053923 | -0.03872 | 0.033843
3118.0938 | 121.1792 | -6.0562 | 115.2054 | 0.034862 | -0.063415 | 0.001736 | -0.038752 | 0.077466 | 0.048956 | -0.071874 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.066548 | 0.059844 | -0.019749 | 0.005985 | 6.0911 | 5.9928 | 6.0579 | 6.0175 | 6.1337 | 6.1052 | 5.9843 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.084859 | 0.078155 | -0.001438 | 0.024296 | -0.027796 | 0.058501 | -0.052454 | 0.033843
3119.8594 | 121.312 | -5.9692 | 115.242 | 0.034862 | -0.072572 | 0.001736 | -0.047909 | 0.082044 | 0.039799 | -0.062717 | 0.034174 | 0.15706 | 0.009515 | -0.10637 | 0.066548 | 0.069001 | -0.024328 | 0.010563 | 6.0041 | 5.8967 | 5.971 | 5.9213 | 6.0513 | 6.009 | 5.9065 | 0.052485 | 0.17537 | 0.027826 | -0.088054 | 0.084859 | 0.087312 | -0.006017 | 0.028874 | -0.032374 | 0.058502 | -0.057033 | 0.033843
3121.6094 | 121.2936 | -6.0287 | 115.2283 | 0.030283 | -0.067994 | 0.001736 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 6.059 | 5.9608 | 6.0305 | 5.9808 | 6.1108 | 6.0731 | 5.966 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.047876 | 0.033843
3123.3125 | 121.2204 | -6.189 | 115.1688 | 0.030283 | -0.063415 | 0.001736 | -0.038752 | 0.082044 | 0.053534 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.069001 | -0.019749 | 0.010563 | 6.2192 | 6.1255 | 6.1907 | 6.1502 | 6.271 | 6.2425 | 6.1262 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.087312 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.043298 | 0.033843
3125.0781 | 121.2708 | -6.0745 | 115.2237 | 0.030283 | -0.063415 | -0.007421 | -0.038752 | 0.082044 | 0.048956 | -0.062717 | 0.043331 | 0.15248 | 0.014094 | -0.11552 | 0.057392 | 0.059844 | -0.010593 | 0.010563 | 6.1048 | 6.0111 | 6.0671 | 6.0358 | 6.1566 | 6.1235 | 6.0118 | 0.061642 | 0.17079 | 0.032405 | -0.097212 | 0.075703 | 0.078155 | 0.007718 | 0.028874 | -0.014061 | 0.053924 | -0.043298 | 0.024687
3126.7656 | 121.344 | -5.9921 | 115.2649 | 0.034862 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.052814 | 0.064423 | -0.024328 | 0.015141 | 6.027 | 5.9287 | 5.9893 | 5.9488 | 6.0696 | 6.0319 | 5.9294 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.071125 | 0.082734 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.043299 | 0.033843
3128.5312 | 121.3348 | -5.8823 | 115.4205 | 0.034862 | -0.063415 | -0.002842 | -0.043331 | 0.077466 | 0.044377 | -0.071874 | 0.043331 | 0.15248 | 0.014094 | -0.11552 | 0.06197 | 0.069001 | -0.024328 | 0.015141 | 5.9171 | 5.8188 | 5.8794 | 5.8389 | 5.9597 | 5.9266 | 5.8104 | 0.061642 | 0.17079 | 0.032405 | -0.097212 | 0.080281 | 0.087312 | -0.006017 | 0.033452 | -0.018639 | 0.067659 | -0.047876 | 0.038422
3130.2656 | 121.3165 | -5.9418 | 115.4388 | 0.03944 | -0.072572 | 0.001736 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 5.9812 | 5.8692 | 5.9435 | 5.903 | 6.0192 | 5.9907 | 5.8791 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.027796 | 0.058502 | -0.047876 | 0.038422
3131.9531 | 121.2891 | -5.9509 | 115.3885 | 0.030283 | -0.063415 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.058139 | 0.034174 | 0.14332 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.024328 | 0.010563 | 5.9812 | 5.8875 | 5.9481 | 5.9122 | 6.0284 | 5.9999 | 5.8928 | 0.052485 | 0.16163 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.006017 | 0.028874 | -0.027796 | 0.058502 | -0.043298 | 0.043
3133.7188 | 121.2708 | -5.8594 | 115.5029 | 0.034862 | -0.058836 | 0.001736 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.038752 | 0.16164 | 0.018672 | -0.11552 | 0.052814 | 0.069001 | -0.019749 | 0.015141 | 5.8942 | 5.8005 | 5.8611 | 5.8206 | 5.9368 | 5.9083 | 5.7967 | 0.057063 | 0.17995 | 0.036983 | -0.097212 | 0.071125 | 0.087312 | -0.001438 | 0.033452 | -0.014062 | 0.058501 | -0.034142 | 0.038421
3135.4688 | 121.3531 | -5.928 | 115.4388 | 0.03944 | -0.067994 | 0.001736 | -0.047909 | 0.072888 | 0.048956 | -0.062717 | 0.034174 | 0.15248 | 0.009515 | -0.10637 | 0.06197 | 0.059844 | -0.019749 | 0.015141 | 5.9675 | 5.86 | 5.9298 | 5.8801 | 6.0009 | 5.977 | 5.8653 | 0.052485 | 0.17079 | 0.027826 | -0.088054 | 0.080281 | 0.078155 | -0.001438 | 0.033452 | -0.027796 | 0.053923 | -0.052455 | 0.029264
3137.2344 | 121.4447 | -5.8594 | 115.4434 | 0.030283 | -0.063415 | -0.002842 | -0.047909 | 0.082044 | 0.048956 | -0.062717 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.069001 | -0.024328 | 0.024297 | 5.8897 | 5.796 | 5.8565 | 5.8115 | 5.9414 | 5.9083 | 5.7967 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.087312 | -0.006017 | 0.042608 | -0.023218 | 0.058502 | -0.043298 | 0.038422
3138.9375 | 121.4172 | -5.8777 | 115.4892 | 0.034862 | -0.072572 | -0.007421 | -0.047909 | 0.077466 | 0.044377 | -0.058139 | 0.038752 | 0.16622 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.019749 | 0.019719 | 5.9125 | 5.8051 | 5.8703 | 5.8298 | 5.9552 | 5.9221 | 5.8195 | 0.057063 | 0.18453 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.001438 | 0.03803 | -0.014062 | 0.058501 | -0.03872 | 0.033843
3140.6875 | 121.344 | -5.8823 | 115.5716 | 0.030283 | -0.067994 | -0.002842 | -0.038752 | 0.082044 | 0.048956 | -0.062717 | 0.047909 | 0.1479 | 0.018672 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.005985 | 5.9125 | 5.8143 | 5.8794 | 5.8435 | 5.9643 | 5.9312 | 5.8195 | 0.06622 | 0.16621 | 0.036983 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.024296 | -0.004905 | 0.072237 | -0.034142 | 0.043
3142.375 | 121.3577 | -6.0516 | 115.3793 | 0.030283 | -0.063415 | -0.007421 | -0.038752 | 0.072888 | 0.048956 | -0.067295 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.052814 | 0.064423 | -0.015171 | 0.015141 | 6.0819 | 5.9882 | 6.0442 | 6.0129 | 6.1245 | 6.1006 | 5.9843 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.071125 | 0.082734 | 0.00314 | 0.033452 | -0.014062 | 0.053923 | -0.03872 | 0.029265
3144.125 | 121.4859 | -5.8319 | 115.5304 | 0.030283 | -0.058836 | 0.001736 | -0.043331 | 0.082044 | 0.035221 | -0.062717 | 0.034174 | 0.15706 | 0.02325 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 5.8622 | 5.7731 | 5.8336 | 5.7886 | 5.914 | 5.8671 | 5.7692 | 0.052485 | 0.17537 | 0.041561 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.023218 | 0.053923 | -0.034142 | 0.042999
3145.875 | 121.5042 | -5.928 | 115.4388 | 0.03944 | -0.063415 | -0.002842 | -0.038752 | 0.082044 | 0.039799 | -0.067295 | 0.034174 | 0.15248 | 0.018672 | -0.11094 | 0.071126 | 0.069001 | -0.019749 | 0.015141 | 5.9675 | 5.8646 | 5.9252 | 5.8893 | 6.0101 | 5.9678 | 5.8607 | 0.052485 | 0.17079 | 0.036983 | -0.092633 | 0.089437 | 0.087312 | -0.001438 | 0.033452 | -0.036952 | 0.053923 | -0.052454 | 0.038421
3147.6406 | 121.4035 | -6.0379 | 115.4205 | 0.034862 | -0.067994 | 0.006315 | -0.038752 | 0.086622 | 0.044377 | -0.067295 | 0.047909 | 0.15706 | 0.018672 | -0.10179 | 0.06197 | 0.059844 | -0.024328 | 0.015141 | 6.0728 | 5.9699 | 6.0442 | 5.9992 | 6.1245 | 6.0823 | 5.9706 | 0.06622 | 0.17537 | 0.036983 | -0.083475 | 0.080281 | 0.078155 | -0.006017 | 0.033452 | -0.014061 | 0.072237 | -0.043298 | 0.043
3149.3906 | 121.4401 | -5.9921 | 115.4572 | 0.030283 | -0.058836 | 0.006315 | -0.047909 | 0.082044 | 0.044377 | -0.062717 | 0.034174 | 0.16164 | 0.02325 | -0.10637 | 0.06197 | 0.059844 | -0.024328 | 0.010563 | 6.0224 | 5.9333 | 5.9984 | 5.9442 | 6.0742 | 6.0365 | 5.9294 | 0.052485 | 0.17995 | 0.041561 | -0.088054 | 0.080281 | 0.078155 | -0.006017 | 0.028874 | -0.027796 | 0.058502 | -0.03872 | 0.047578
3151.1562 | 121.5454 | -6.0059 | 115.3793 | 0.03944 | -0.067994 | -0.007421 | -0.043331 | 0.077466 | 0.039799 | -0.062717 | 0.034174 | 0.16164 | 0.018672 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.010563 | 6.0453 | 5.9379 | 5.9984 | 5.9625 | 6.0833 | 6.0457 | 5.9431 | 0.052485 | 0.17995 | 0.036983 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.028874 | -0.023218 | 0.058502 | -0.03872 | 0.043
3152.8594 | 121.4767 | -5.9601 | 115.4892 | 0.03944 | -0.067994 | -0.007421 | -0.043331 | 0.086622 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.010563 | 5.9995 | 5.8921 | 5.9527 | 5.9168 | 6.0467 | 6.009 | 5.8974 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.043298 | 0.033843
3154.6094 | 121.4767 | -5.9738 | 115.4526 | 0.030283 | -0.067994 | 0.001736 | -0.038752 | 0.082044 | 0.048956 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.015141 | 6.0041 | 5.9058 | 5.9756 | 5.9351 | 6.0559 | 6.0228 | 5.9111 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.033452 | -0.014061 | 0.058502 | -0.043298 | 0.029265
3156.2969 | 121.4127 | -6.0196 | 115.4755 | 0.034862 | -0.072572 | -0.002842 | -0.038752 | 0.086622 | 0.039799 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.11552 | 0.052814 | 0.064423 | -0.024328 | 0.015141 | 6.0545 | 5.947 | 6.0168 | 5.9808 | 6.1062 | 6.0594 | 5.9523 | 0.052485 | 0.17537 | 0.032405 | -0.097212 | 0.071125 | 0.082734 | -0.006017 | 0.033452 | -0.01864 | 0.058502 | -0.03872 | 0.038422
3158.0625 | 121.431 | -6.0287 | 115.4434 | 0.03944 | -0.067994 | 0.001736 | -0.038752 | 0.082044 | 0.048956 | -0.062717 | 0.034174 | 0.16164 | 0.018672 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 6.0682 | 5.9608 | 6.0305 | 5.99 | 6.1108 | 6.0777 | 5.966 | 0.052485 | 0.17995 | 0.036983 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.027796 | 0.053923 | -0.043298 | 0.038421
3159.8281 | 121.4493 | -6.0745 | 115.4251 | 0.03944 | -0.072572 | 0.001736 | -0.034174 | 0.077466 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.02325 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.019719 | 6.114 | 6.002 | 6.0763 | 6.0404 | 6.152 | 6.1235 | 6.0118 | 0.057063 | 0.17079 | 0.041561 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.03803 | -0.023218 | 0.06308 | -0.03872 | 0.047578
3161.5781 | 121.4401 | -6.0471 | 115.4572 | 0.030283 | -0.072572 | -0.002842 | -0.038752 | 0.077466 | 0.053534 | -0.062717 | 0.038752 | 0.15248 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.019749 | 0.019719 | 6.0773 | 5.9745 | 6.0442 | 6.0083 | 6.1245 | 6.1006 | 5.9843 | 0.057063 | 0.17079 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.001438 | 0.03803 | -0.023218 | 0.058501 | -0.043298 | 0.038421
3163.2812 | 121.2524 | -86.8698 | 33.8425 | 0.06691 | -0.040521 | 0.024629 | -0.002124 | 0.10036 | 0.071848 | -0.035248 | 0.070802 | 0.19369 | 0.046142 | -0.1201 | 0.034501 | 0.027798 | -0.038063 | -0.00775 | 86.9367 | 86.8293 | 86.8944 | 86.8677 | 86.9702 | 86.9417 | 86.8346 | 0.089113 | 0.212 | 0.064453 | -0.10179 | 0.052812 | 0.046109 | -0.019752 | 0.010561 | 0.036301 | 0.10887 | 0.011641 | 0.084205
3165.0469 | 120.9503 | -10.9222 | 110.5179 | 0.03944 | -0.077151 | 0.001736 | -0.043331 | 0.082044 | 0.048956 | -0.058139 | 0.038752 | 0.15706 | 0.018672 | -0.10637 | 0.06197 | 0.064423 | -0.015171 | 0.010563 | 10.9617 | 10.8451 | 10.924 | 10.8789 | 11.0043 | 10.9712 | 10.8641 | 0.057063 | 0.17537 | 0.036983 | -0.088054 | 0.080281 | 0.082734 | 0.00314 | 0.028874 | -0.023218 | 0.053923 | -0.043298 | 0.033843
3166.7344 | 121.3852 | -7.3425 | 114.0106 | 0.030283 | -0.072572 | -0.002842 | -0.034174 | 0.077466 | 0.039799 | -0.062717 | 0.034174 | 0.16164 | 0.009515 | -0.11094 | 0.057392 | 0.064423 | -0.015171 | 0.010563 | 7.3728 | 7.27 | 7.3397 | 7.3084 | 7.42 | 7.3823 | 7.2798 | 0.052485 | 0.17995 | 0.027826 | -0.092633 | 0.075703 | 0.082734 | 0.00314 | 0.028874 | -0.023218 | 0.049345 | -0.047877 | 0.024686
3168.5 | 121.344 | -6.6742 | 114.7659 | 0.030283 | -0.072572 | -0.007421 | -0.043331 | 0.082044 | 0.048956 | -0.062717 | 0.034174 | 0.16164 | 0.014094 | -0.10637 | 0.048236 | 0.059844 | -0.024328 | 0.010563 | 6.7045 | 6.6016 | 6.6668 | 6.6309 | 6.7562 | 6.7232 | 6.6115 | 0.052485 | 0.17995 | 0.032405 | -0.088054 | 0.066547 | 0.078155 | -0.006017 | 0.028874 | -0.014062 | 0.058502 | -0.034142 | 0.038422
3170.25 | 121.3623 | -7.4844 | 113.9465 | 0.03944 | -0.067994 | -0.002842 | -0.038752 | 0.082044 | 0.044377 | -0.062717 | 0.029595 | 0.15706 | 0.014094 | -0.10637 | 0.052814 | 0.064423 | -0.019749 | 0.010563 | 7.5239 | 7.4164 | 7.4816 | 7.4457 | 7.5665 | 7.5288 | 7.4217 | 0.047906 | 0.17537 | 0.032405 | -0.088054 | 0.071125 | 0.082734 | -0.001438 | 0.028874 | -0.023219 | 0.049344 | -0.03872 | 0.033843
3171.9375 | 121.4127 | -7.338 | 114.1296 | 0.03944 | -0.067994 | 0.001736 | -0.043331 | 0.086622 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.019749 | 0.015141 | 7.3774 | 7.27 | 7.3397 | 7.2946 | 7.4246 | 7.3823 | 7.2752 | 0.057063 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.043298 | 0.033843
3173.7031 | 121.4767 | -7.2739 | 114.1571 | 0.03944 | -0.077151 | -0.002842 | -0.038752 | 0.082044 | 0.044377 | -0.058139 | 0.034174 | 0.15248 | 0.009515 | -0.11094 | 0.052814 | 0.064423 | -0.024328 | 0.010563 | 7.3133 | 7.1967 | 7.271 | 7.2351 | 7.3559 | 7.3182 | 7.2157 | 0.052485 | 0.17079 | 0.027826 | -0.092633 | 0.071125 | 0.082734 | -0.006017 | 0.028874 | -0.01864 | 0.058502 | -0.043299 | 0.033843
3175.3906 | 121.4127 | -7.5302 | 113.9877 | 0.034862 | -0.077151 | -0.002842 | -0.047909 | 0.086622 | 0.039799 | -0.067295 | 0.034174 | 0.16164 | 0.018672 | -0.10637 | 0.06197 | 0.059844 | -0.024328 | 0.019719 | 7.5651 | 7.4531 | 7.5274 | 7.4823 | 7.6168 | 7.57 | 7.4629 | 0.052485 | 0.17995 | 0.036983 | -0.088054 | 0.080281 | 0.078155 | -0.006017 | 0.03803 | -0.027796 | 0.058502 | -0.043298 | 0.043
3177.1562 | 121.4722 | -7.0999 | 114.3997 | 0.03944 | -0.072572 | 0.001736 | -0.038752 | 0.082044 | 0.044377 | -0.053561 | 0.034174 | 0.15248 | 0.014094 | -0.11094 | 0.052814 | 0.064423 | -0.019749 | 0.010563 | 7.1394 | 7.0273 | 7.1017 | 7.0612 | 7.182 | 7.1443 | 7.0464 | 0.052485 | 0.17079 | 0.032405 | -0.092633 | 0.071125 | 0.082734 | -0.001438 | 0.028874 | -0.01864 | 0.053923 | -0.03872 | 0.033843
3178.8594 | 121.463 | -7.2189 | 114.4318 | 0.03944 | -0.072572 | -0.002842 | -0.029595 | 0.077466 | 0.039799 | -0.058139 | 0.038752 | 0.15248 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 7.2584 | 7.1464 | 7.2161 | 7.1893 | 7.2964 | 7.2587 | 7.1608 | 0.057063 | 0.17079 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.023218 | 0.06308 | -0.043298 | 0.043
3180.6094 | 120.7031 | -10.8994 | 109.6024 | 0.03944 | -0.067994 | 0.010893 | -0.038752 | 0.082044 | 0.048956 | -0.058139 | 0.043331 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.055266 | -0.024328 | 0.010563 | 10.9388 | 10.8314 | 10.9102 | 10.8606 | 10.9814 | 10.9483 | 10.8412 | 0.061642 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.073577 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.043298 | 0.038422
3182.3594 | 120.9 | -6.0837 | 115.1413 | 0.03944 | -0.077151 | 0.006315 | -0.034174 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.16622 | 0.02325 | -0.10637 | 0.06197 | 0.064423 | -0.019749 | 0.015141 | 6.1231 | 6.0065 | 6.09 | 6.0495 | 6.1657 | 6.1281 | 6.0255 | 0.057063 | 0.18453 | 0.041561 | -0.088054 | 0.080281 | 0.082734 | -0.001438 | 0.033452 | -0.023218 | 0.058501 | -0.03872 | 0.042999
3184.0625 | 121.1792 | -5.69 | 115.5991 | 0.03944 | -0.077151 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.058139 | 0.038752 | 0.15706 | 0.014094 | -0.1201 | 0.057392 | 0.064423 | -0.015171 | 0.015141 | 5.7294 | 5.6129 | 5.6872 | 5.6467 | 5.7675 | 5.7298 | 5.6319 | 0.057063 | 0.17537 | 0.032405 | -0.10179 | 0.075703 | 0.082734 | 0.00314 | 0.033452 | -0.01864 | 0.053923 | -0.043298 | 0.029265
3185.8125 | 121.2204 | -6.0562 | 115.2191 | 0.03944 | -0.077151 | 0.006315 | -0.034174 | 0.086622 | 0.048956 | -0.058139 | 0.043331 | 0.16164 | 0.018672 | -0.10637 | 0.06197 | 0.055266 | -0.028906 | 0.015141 | 6.0957 | 5.9791 | 6.0625 | 6.022 | 6.1428 | 6.1052 | 5.9981 | 0.061642 | 0.17995 | 0.036983 | -0.088054 | 0.080281 | 0.073577 | -0.010595 | 0.033452 | -0.018639 | 0.072237 | -0.043298 | 0.047578
3187.5781 | 121.3257 | -6.5826 | 114.5874 | 0.048597 | -0.086309 | -0.002842 | -0.047909 | 0.0912 | 0.039799 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.11552 | 0.048236 | 0.059844 | -0.019749 | 0.010563 | 6.6312 | 6.4963 | 6.5798 | 6.5347 | 6.6738 | 6.6224 | 6.5153 | 0.052485 | 0.17537 | 0.032405 | -0.097212 | 0.066547 | 0.078155 | -0.001438 | 0.028874 | -0.014062 | 0.053923 | -0.034142 | 0.033843
3189.2812 | 121.3074 | -5.1865 | 116.1301 | 0.034862 | -0.072572 | 0.001736 | -0.029595 | 0.082044 | 0.048956 | -0.058139 | 0.034174 | 0.16164 | 0.014094 | -0.11552 | 0.066548 | 0.064423 | -0.010593 | 0.015141 | 5.2213 | 5.1139 | 5.1882 | 5.1569 | 5.2685 | 5.2354 | 5.1283 | 0.052485 | 0.17995 | 0.032405 | -0.097212 | 0.084859 | 0.082734 | 0.007718 | 0.033452 | -0.032374 | 0.044767 | -0.052454 | 0.024687
3191.0312 | 121.3303 | -7.4341 | 114.2303 | 0.034862 | -0.08173 | -0.002842 | -0.034174 | 0.082044 | 0.048956 | -0.058139 | 0.038752 | 0.15248 | 0.018672 | -0.11552 | 0.06197 | 0.059844 | -0.024328 | 0.019719 | 7.4689 | 7.3524 | 7.4312 | 7.3999 | 7.5161 | 7.483 | 7.3759 | 0.057063 | 0.17079 | 0.036983 | -0.097212 | 0.080281 | 0.078155 | -0.006017 | 0.03803 | -0.023218 | 0.06308 | -0.043298 | 0.043
3192.7188 | 121.431 | -5.864 | 115.4892 | 0.030283 | -0.08173 | 0.001736 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.019719 | 5.8942 | 5.7822 | 5.8657 | 5.8252 | 5.9414 | 5.9083 | 5.7967 | 0.052485 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.03803 | -0.023218 | 0.058502 | -0.043298 | 0.038422
3194.4844 | 121.4264 | -4.921 | 116.4368 | 0.03944 | -0.08173 | 0.001736 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.038752 | 0.15248 | 0.014094 | -0.10637 | 0.057392 | 0.069001 | -0.019749 | 0.015141 | 4.9604 | 4.8392 | 4.9227 | 4.8822 | 4.9984 | 4.9699 | 4.8582 | 0.057063 | 0.17079 | 0.032405 | -0.088054 | 0.075703 | 0.087312 | -0.001438 | 0.033452 | -0.01864 | 0.058501 | -0.043298 | 0.033843
3196.1719 | 121.4722 | -5.0262 | 116.2766 | 0.034862 | -0.077151 | -0.007421 | -0.043331 | 0.082044 | 0.044377 | -0.053561 | 0.038752 | 0.15248 | 0.014094 | -0.11094 | 0.06197 | 0.064423 | -0.024328 | 0.005985 | 5.0611 | 4.9491 | 5.0188 | 4.9829 | 5.1083 | 5.0706 | 4.9727 | 0.057063 | 0.17079 | 0.032405 | -0.092633 | 0.080281 | 0.082734 | -0.006017 | 0.024296 | -0.023218 | 0.06308 | -0.047876 | 0.038422
3197.9219 | 121.376 | -5.5847 | 115.8325 | 0.034862 | -0.077151 | 0.001736 | -0.038752 | 0.086622 | 0.053534 | -0.062717 | 0.043331 | 0.15706 | 0.018672 | -0.11552 | 0.066548 | 0.064423 | -0.024328 | 0.015141 | 5.6196 | 5.5076 | 5.5865 | 5.546 | 5.6713 | 5.6383 | 5.522 | 0.061642 | 0.17537 | 0.036983 | -0.097212 | 0.084859 | 0.082734 | -0.006017 | 0.033452 | -0.023217 | 0.067659 | -0.047876 | 0.043
3199.6875 | 115.8096 | -62.5854 | 53.6957 | 0.057754 | -0.063415 | 0.015472 | -0.020438 | 0.095778 | 0.058113 | -0.044405 | 0.057066 | 0.17079 | 0.041563 | -0.11552 | 0.06197 | 0.050688 | -0.019749 | -0.003172 | 62.6432 | 62.522 | 62.6009 | 62.565 | 62.6812 | 62.6436 | 62.541 | 0.075377 | 0.1891 | 0.059874 | -0.097212 | 0.080281 | 0.068999 | -0.001438 | 0.015139 | -0.004904 | 0.076815 | -0.020407 | 0.061312
3201.375 | 117.0731 | -7.988 | 109.9182 | 0.03944 | -0.072572 | 0.001736 | -0.034174 | 0.082044 | 0.048956 | -0.058139 | 0.047909 | 0.15248 | 0.014094 | -0.11552 | 0.052814 | 0.064423 | -0.019749 | 0.005985 | 8.0274 | 7.9154 | 7.9897 | 7.9538 | 8.07 | 8.0369 | 7.9298 | 0.06622 | 0.17079 | 0.032405 | -0.097212 | 0.071125 | 0.082734 | -0.001438 | 0.024296 | -0.004905 | 0.067658 | -0.03872 | 0.033843
3203.1406 | 120.401 | -4.6051 | 115.6265 | 0.034862 | -0.067994 | -0.007421 | -0.034174 | 0.072888 | 0.044377 | -0.062717 | 0.038752 | 0.16164 | 0.018672 | -0.11094 | 0.06197 | 0.069001 | -0.015171 | 0.010563 | 4.64 | 4.5371 | 4.5977 | 4.5709 | 4.678 | 4.6495 | 4.5424 | 0.057063 | 0.17995 | 0.036983 | -0.092633 | 0.080281 | 0.087312 | 0.00314 | 0.028874 | -0.023218 | 0.053923 | -0.043298 | 0.033843
3204.8906 | 120.5109 | -4.0192 | 116.5375 | 0.044018 | -0.077151 | -0.007421 | -0.038752 | 0.077466 | 0.044377 | -0.053561 | 0.043331 | 0.16164 | 0.018672 | -0.11552 | 0.057392 | 0.064423 | -0.024328 | 0.001406 | 4.0632 | 3.942 | 4.0117 | 3.9804 | 4.0966 | 4.0635 | 3.9656 | 0.061642 | 0.17995 | 0.036983 | -0.097212 | 0.075703 | 0.082734 | -0.006017 | 0.019717 | -0.014061 | 0.067659 | -0.03872 | 0.043
3206.6406 | 106.4804 | -3.5797 | 116.4642 | 0.044018 | -0.072572 | -0.007421 | -0.043331 | 0.077466 | 0.048956 | -0.058139 | 0.043331 | 0.15706 | 0.014094 | -0.11552 | 0.057392 | 0.069001 | -0.019749 | 0.015141 | 3.6237 | 3.5071 | 3.5723 | 3.5364 | 3.6572 | 3.6287 | 3.5216 | 0.061642 | 0.17537 | 0.032405 | -0.097212 | 0.075703 | 0.087312 | -0.001438 | 0.033452 | -0.014061 | 0.06308 | -0.043298 | 0.033843
3208.3438 | 93.5989 | -3.5202 | 99.7284 | 0.03944 | -0.067994 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.15706 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.024328 | 0.010563 | 3.5596 | 3.4522 | 3.5174 | 3.4815 | 3.5977 | 3.5692 | 3.4575 | 0.061642 | 0.17537 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | -0.006017 | 0.028874 | -0.018639 | 0.067659 | -0.043298 | 0.043
3210.0938 | 120.8679 | -3.566 | 117.2791 | 0.030283 | -0.067994 | 0.001736 | -0.047909 | 0.077466 | 0.053534 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.10637 | 0.057392 | 0.059844 | -0.028906 | 0.010563 | 3.5963 | 3.498 | 3.5677 | 3.5181 | 3.6434 | 3.6195 | 3.5033 | 0.061642 | 0.17537 | 0.032405 | -0.088054 | 0.075703 | 0.078155 | -0.010595 | 0.028874 | -0.014061 | 0.072237 | -0.043298 | 0.043
3211.8438 | 120.9045 | -3.6667 | 117.2882 | 0.034862 | -0.072572 | -0.002842 | -0.043331 | 0.077466 | 0.039799 | -0.067295 | 0.043331 | 0.16622 | 0.014094 | -0.11552 | 0.057392 | 0.064423 | -0.015171 | 0.010563 | 3.7015 | 3.5941 | 3.6638 | 3.6234 | 3.7442 | 3.7065 | 3.5994 | 0.061642 | 0.18453 | 0.032405 | -0.097212 | 0.075703 | 0.082734 | 0.00314 | 0.028874 | -0.014061 | 0.058502 | -0.043298 | 0.029265
3213.5938 | 104.6448 | -3.7399 | 116.8167 | 0.03944 | -0.08173 | -0.002842 | -0.038752 | 0.082044 | 0.053534 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.10637 | 0.066548 | 0.064423 | -0.019749 | 0.019719 | 3.7794 | 3.6582 | 3.7371 | 3.7012 | 3.822 | 3.7935 | 3.6726 | 0.052485 | 0.17537 | 0.032405 | -0.088054 | 0.084859 | 0.082734 | -0.001438 | 0.03803 | -0.032374 | 0.053923 | -0.052454 | 0.033843
3215.2812 | 109.8816 | -3.9459 | 116.8671 | 0.044018 | -0.077151 | 0.001736 | -0.038752 | 0.086622 | 0.048956 | -0.062717 | 0.038752 | 0.16164 | 0.02325 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 3.9899 | 3.8688 | 3.9477 | 3.9072 | 4.0325 | 3.9949 | 3.8832 | 0.057063 | 0.17995 | 0.041561 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.01864 | 0.06308 | -0.034142 | 0.047578
3217.0312 | 121.2341 | -4.0604 | 116.8625 | 0.030283 | -0.072572 | 0.001736 | -0.038752 | 0.077466 | 0.048956 | -0.058139 | 0.038752 | 0.15248 | 0.018672 | -0.10637 | 0.066548 | 0.064423 | -0.028906 | 0.019719 | 4.0906 | 3.9878 | 4.0621 | 4.0216 | 4.1378 | 4.1093 | 4.0022 | 0.057063 | 0.17079 | 0.036983 | -0.088054 | 0.084859 | 0.082734 | -0.010595 | 0.03803 | -0.027796 | 0.067658 | -0.047876 | 0.047578
3218.7188 | 121.2479 | -4.0924 | 116.6794 | 0.03944 | -0.077151 | 0.001736 | -0.038752 | 0.082044 | 0.044377 | -0.053561 | 0.043331 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.005985 | 4.1318 | 4.0153 | 4.0941 | 4.0537 | 4.1745 | 4.1368 | 4.0388 | 0.061642 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.024296 | -0.014061 | 0.067659 | -0.043298 | 0.038422
3220.4844 | 121.2524 | -4.0466 | 116.9403 | 0.03944 | -0.072572 | 0.001736 | -0.043331 | 0.086622 | 0.053534 | -0.062717 | 0.038752 | 0.16164 | 0.02325 | -0.10637 | 0.066548 | 0.064423 | -0.024328 | 0.010563 | 4.0861 | 3.9741 | 4.0484 | 4.0033 | 4.1333 | 4.1002 | 3.9839 | 0.057063 | 0.17995 | 0.041561 | -0.088054 | 0.084859 | 0.082734 | -0.006017 | 0.028874 | -0.027796 | 0.06308 | -0.043298 | 0.047578
3222.1719 | 121.0831 | -4.1153 | 116.5878 | 0.034862 | -0.077151 | 0.001736 | -0.047909 | 0.077466 | 0.044377 | -0.058139 | 0.034174 | 0.15706 | 0.009515 | -0.11094 | 0.057392 | 0.059844 | -0.024328 | 0.015141 | 4.1502 | 4.0381 | 4.117 | 4.0674 | 4.1928 | 4.1597 | 4.0572 | 0.052485 | 0.17537 | 0.027826 | -0.092633 | 0.075703 | 0.078155 | -0.006017 | 0.033452 | -0.023218 | 0.058502 | -0.047877 | 0.033843
3223.9375 | 121.257 | -4.097 | 116.9495 | 0.034862 | -0.077151 | 0.001736 | -0.043331 | 0.077466 | 0.044377 | -0.058139 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.055266 | -0.019749 | 0.015141 | 4.1318 | 4.0198 | 4.0987 | 4.0537 | 4.1745 | 4.1414 | 4.0388 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.073577 | -0.001438 | 0.033452 | -0.023218 | 0.053923 | -0.043298 | 0.033843
3225.6875 | 121.257 | -4.1336 | 117.0685 | 0.044018 | -0.077151 | 0.001736 | -0.038752 | 0.082044 | 0.053534 | -0.067295 | 0.038752 | 0.16164 | 0.018672 | -0.11552 | 0.052814 | 0.064423 | -0.033484 | 0.024297 | 4.1776 | 4.0565 | 4.1353 | 4.0949 | 4.2157 | 4.1871 | 4.0663 | 0.057063 | 0.17995 | 0.036983 | -0.097212 | 0.071125 | 0.082734 | -0.015173 | 0.042608 | -0.014062 | 0.072236 | -0.034142 | 0.052156
3227.375 | 121.3577 | -4.1519 | 117.0273 | 0.034862 | -0.077151 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.062717 | 0.043331 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.073579 | -0.033484 | 0.010563 | 4.1868 | 4.0748 | 4.1491 | 4.104 | 4.2294 | 4.1963 | 4.0892 | 0.061642 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.09189 | -0.015173 | 0.028874 | -0.014061 | 0.076815 | -0.03872 | 0.052156
3229.125 | 120.607 | -4.2984 | 116.9724 | 0.034862 | -0.072572 | 0.001736 | -0.043331 | 0.086622 | 0.039799 | -0.062717 | 0.043331 | 0.16164 | 0.014094 | -0.11552 | 0.057392 | 0.059844 | -0.028906 | 0.015141 | 4.3333 | 4.2258 | 4.3001 | 4.2551 | 4.385 | 4.3382 | 4.2357 | 0.061642 | 0.17995 | 0.032405 | -0.097212 | 0.075703 | 0.078155 | -0.010595 | 0.033452 | -0.014061 | 0.072237 | -0.043298 | 0.043
3230.875 | 121.3394 | -4.2938 | 116.9403 | 0.03944 | -0.072572 | -0.002842 | -0.038752 | 0.082044 | 0.048956 | -0.058139 | 0.043331 | 0.16164 | 0.018672 | -0.11094 | 0.052814 | 0.069001 | -0.019749 | 0.015141 | 4.3333 | 4.2213 | 4.291 | 4.2551 | 4.3759 | 4.3428 | 4.2357 | 0.061642 | 0.17995 | 0.036983 | -0.092633 | 0.071125 | 0.087312 | -0.001438 | 0.033452 | -0.009483 | 0.06308 | -0.034142 | 0.038421
3232.5781 | 121.3531 | -4.4449 | 116.8121 | 0.03944 | -0.077151 | 0.001736 | -0.043331 | 0.082044 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.018672 | -0.11094 | 0.052814 | 0.064423 | -0.028906 | 0.010563 | 4.4843 | 4.3677 | 4.4466 | 4.4016 | 4.5269 | 4.4938 | 4.3822 | 0.057063 | 0.17537 | 0.036983 | -0.092633 | 0.071125 | 0.082734 | -0.010595 | 0.028874 | -0.014062 | 0.067658 | -0.034142 | 0.047578
3234.3438 | 121.312 | -4.4678 | 116.8213 | 0.034862 | -0.08173 | -0.002842 | -0.038752 | 0.082044 | 0.048956 | -0.058139 | 0.043331 | 0.16164 | 0.02325 | -0.11552 | 0.06197 | 0.064423 | -0.019749 | 0.005985 | 4.5026 | 4.386 | 4.4649 | 4.429 | 4.5498 | 4.5167 | 4.4096 | 0.061642 | 0.17995 | 0.041561 | -0.097212 | 0.080281 | 0.082734 | -0.001438 | 0.024296 | -0.018639 | 0.06308 | -0.03872 | 0.042999
3236.0312 | 120.8084 | -4.4952 | 116.8762 | 0.044018 | -0.072572 | -0.002842 | -0.038752 | 0.0912 | 0.044377 | -0.053561 | 0.043331 | 0.15248 | 0.02325 | -0.11094 | 0.052814 | 0.064423 | -0.019749 | 0.019719 | 4.5393 | 4.4227 | 4.4924 | 4.4565 | 4.5864 | 4.5396 | 4.4417 | 0.061642 | 0.17079 | 0.041561 | -0.092633 | 0.071125 | 0.082734 | -0.001438 | 0.03803 | -0.009483 | 0.06308 | -0.029564 | 0.042999
3237.7812 | 120.9732 | -4.4724 | 116.922 | 0.034862 | -0.072572 | -0.002842 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.052488 | 0.16164 | 0.014094 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.010563 | 4.5072 | 4.3998 | 4.4695 | 4.429 | 4.5544 | 4.5167 | 4.4096 | 0.070799 | 0.17995 | 0.032405 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.028874 | -0.004904 | 0.076816 | -0.043298 | 0.038422
3239.4844 | 121.3943 | -4.3945 | 116.8671 | 0.034862 | -0.072572 | -0.002842 | -0.047909 | 0.082044 | 0.048956 | -0.067295 | 0.034174 | 0.15706 | 0.014094 | -0.11094 | 0.057392 | 0.069001 | -0.028906 | 0.010563 | 4.4294 | 4.322 | 4.3917 | 4.3466 | 4.4766 | 4.4435 | 4.3272 | 0.052485 | 0.17537 | 0.032405 | -0.092633 | 0.075703 | 0.087312 | -0.010595 | 0.028874 | -0.023218 | 0.06308 | -0.043298 | 0.043
3241.25 | 121.3852 | -4.5364 | 116.8167 | 0.030283 | -0.067994 | 0.006315 | -0.043331 | 0.086622 | 0.053534 | -0.058139 | 0.034174 | 0.15706 | 0.018672 | -0.10637 | 0.057392 | 0.064423 | -0.024328 | 0.015141 | 4.5667 | 4.4684 | 4.5428 | 4.4931 | 4.6231 | 4.59 | 4.4783 | 0.052485 | 0.17537 | 0.036983 | -0.088054 | 0.075703 | 0.082734 | -0.006017 | 0.033452 | -0.023218 | 0.058502 | -0.03872 | 0.043
3243.0625 | 121.4539 | -4.4174 | 116.922 | 0.03944 | -0.077151 | 0.006315 | -0.043331 | 0.082044 | 0.048956 | -0.058139 | 0.038752 | 0.15706 | 0.018672 | -0.11094 | 0.057392 | 0.059844 | -0.019749 | 0.010563 | 4.4569 | 4.3403 | 4.4237 | 4.3741 | 4.4995 | 4.4664 | 4.3593 | 0.057063 | 0.17537 | 0.036983 | -0.092633 | 0.075703 | 0.078155 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.03872 | 0.038421
3244.8125 | 121.3715 | -4.6509 | 116.716 | 0.034862 | -0.067994 | -0.002842 | -0.038752 | 0.086622 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.06197 | 0.059844 | -0.019749 | 0.010563 | 4.6857 | 4.5829 | 4.648 | 4.6121 | 4.7375 | 4.6953 | 4.5927 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.080281 | 0.078155 | -0.001438 | 0.028874 | -0.023218 | 0.058501 | -0.047876 | 0.033843
3246.5625 | 121.3211 | -4.7195 | 116.6702 | 0.034862 | -0.08173 | 0.001736 | -0.034174 | 0.082044 | 0.048956 | -0.053561 | 0.043331 | 0.16164 | 0.018672 | -0.11094 | 0.06197 | 0.064423 | -0.015171 | 0.015141 | 4.7544 | 4.6378 | 4.7213 | 4.6854 | 4.8016 | 4.7685 | 4.666 | 0.061642 | 0.17995 | 0.036983 | -0.092633 | 0.080281 | 0.082734 | 0.00314 | 0.033452 | -0.018639 | 0.058502 | -0.043298 | 0.033843
3248.3125 | 121.3989 | -5.3055 | 116.0797 | 0.034862 | -0.08173 | -0.002842 | -0.043331 | 0.086622 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11552 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 5.3403 | 5.2238 | 5.3026 | 5.2622 | 5.3921 | 5.3544 | 5.2428 | 0.057063 | 0.17537 | 0.032405 | -0.097212 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.023218 | 0.06308 | -0.047876 | 0.038422
3250.0156 | 121.3989 | -2.9892 | 118.4189 | 0.03944 | -0.077151 | -0.002842 | -0.043331 | 0.086622 | 0.039799 | -0.053561 | 0.047909 | 0.15706 | 0.02325 | -0.10637 | 0.071126 | 0.064423 | -0.019749 | 0.010563 | 3.0286 | 2.912 | 2.9864 | 2.9459 | 3.0758 | 3.029 | 2.9356 | 0.06622 | 0.17537 | 0.041561 | -0.088054 | 0.089437 | 0.082734 | -0.001438 | 0.028874 | -0.023217 | 0.067658 | -0.047876 | 0.042999
3251.7031 | 121.3989 | -5.1773 | 116.0889 | 0.044018 | -0.077151 | 0.001736 | -0.043331 | 0.082044 | 0.044377 | -0.062717 | 0.038752 | 0.15248 | 0.014094 | -0.11094 | 0.06197 | 0.069001 | -0.024328 | 0.010563 | 5.2213 | 5.1002 | 5.179 | 5.134 | 5.2594 | 5.2217 | 5.1146 | 0.057063 | 0.17079 | 0.032405 | -0.092633 | 0.080281 | 0.087312 | -0.006017 | 0.028874 | -0.023218 | 0.06308 | -0.047876 | 0.038422
3253.4531 | 121.4081 | -4.9072 | 116.4825 | 0.034862 | -0.077151 | 0.001736 | -0.052488 | 0.082044 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.052814 | 0.059844 | -0.028906 | 0.015141 | 4.9421 | 4.8301 | 4.909 | 4.8547 | 4.9893 | 4.9562 | 4.8445 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.071125 | 0.078155 | -0.010595 | 0.033452 | -0.014062 | 0.067658 | -0.03872 | 0.043
3255.2188 | 121.3531 | -2.3529 | 119.1193 | 0.034862 | -0.077151 | 0.001736 | -0.034174 | 0.077466 | 0.048956 | -0.058139 | 0.043331 | 0.16164 | 0.014094 | -0.10637 | 0.06197 | 0.055266 | -0.019749 | 0.019719 | 2.3878 | 2.2758 | 2.3546 | 2.3187 | 2.4304 | 2.4019 | 2.2948 | 0.061642 | 0.17995 | 0.032405 | -0.088054 | 0.080281 | 0.073577 | -0.001438 | 0.03803 | -0.018639 | 0.06308 | -0.047876 | 0.033843
3256.9062 | 121.3531 | -2.2751 | 119.2245 | 0.03944 | -0.077151 | -0.002842 | -0.047909 | 0.077466 | 0.044377 | -0.058139 | 0.038752 | 0.15706 | 0.014094 | -0.11094 | 0.06197 | 0.059844 | -0.024328 | 0.010563 | 2.3145 | 2.1979 | 2.2722 | 2.2272 | 2.3526 | 2.3195 | 2.2169 | 0.057063 | 0.17537 | 0.032405 | -0.092633 | 0.080281 | 0.078155 | -0.006017 | 0.028874 | -0.023218 | 0.06308 | -0.047876 | 0.038422
3258.6094 | 121.5271 | -2.3209 | 119.101 | 0.030283 | -0.077151 | 0.006315 | -0.038752 | 0.077466 | 0.044377 | -0.067295 | 0.038752 | 0.15248 | 0.02325 | -0.10637 | 0.052814 | 0.059844 | -0.024328 | 0.015141 | 2.3511 | 2.2437 | 2.3272 | 2.2821 | 2.3983 | 2.3652 | 2.2536 | 0.057063 | 0.17079 | 0.041561 | -0.088054 | 0.071125 | 0.078155 | -0.006017 | 0.033452 | -0.014062 | 0.06308 | -0.029564 | 0.047578
3260.375 | 121.5088 | -1.9501 | 119.4626 | 0.03944 | -0.072572 | 0.001736 | -0.052488 | 0.086622 | 0.044377 | -0.058139 | 0.038752 | 0.15706 | 0.018672 | -0.10179 | 0.048236 | 0.064423 | -0.024328 | 0.015141 | 1.9895 | 1.8775 | 1.9518 | 1.8976 | 2.0367 | 1.9945 | 1.8919 | 0.057063 | 0.17537 | 0.036983 | -0.083475 | 0.066547 | 0.082734 | -0.006017 | 0.033452 | -0.009484 | 0.06308 | -0.029564 | 0.043
3262.0625 | 121.4081 | -2.2339 | 119.0002 | 0.030283 | -0.077151 | -0.002842 | -0.038752 | 0.077466 | 0.048956 | -0.062717 | 0.038752 | 0.15706 | 0.009515 | -0.10637 | 0.057392 | 0.059844 | -0.028906 | 0.019719 | 2.2642 | 2.1567 | 2.231 | 2.1951 | 2.3114 | 2.2828 | 2.1712 | 0.057063 | 0.17537 | 0.027826 | -0.088054 | 0.075703 | 0.078155 | -0.010595 | 0.03803 | -0.01864 | 0.067658 | -0.047877 | 0.038421
3263.75 | 121.6827 | -1.6983 | 119.7189 | 0.034862 | -0.08173 | 0.001736 | -0.043331 | 0.072888 | 0.044377 | -0.062717 | 0.038752 | 0.15706 | 0.018672 | -0.11552 | 0.057392 | 0.064423 | -0.019749 | 0.010563 | 1.7332 | 1.6166 | 1.7 | 1.655 | 1.7712 | 1.7427 | 1.6356 | 0.057063 | 0.17537 | 0.036983 | -0.097212 | 0.075703 | 0.082734 | -0.001438 | 0.028874 | -0.01864 | 0.058501 | -0.03872 | 0.038421
3265.5 | 121.5271 | -1.5198 | 119.9478 | 0.030283 | -0.08173 | -0.002842 | -0.052488 | 0.077466 | 0.048956 | -0.062717 | 0.043331 | 0.15706 | 0.014094 | -0.11552 | 0.075705 | 0.059844 | -0.019749 | 0.015141 | 1.5501 | 1.438 | 1.5169 | 1.4673 | 1.5972 | 1.5687 | 1.4571 | 0.061642 | 0.17537 | 0.032405 | -0.097212 | 0.094016 | 0.078155 | -0.001438 | 0.033452 | -0.032374 | 0.06308 | -0.061611 | 0.033843
3267.25 | 121.5317 | -1.7166 | 119.7327 | 0.03944 | -0.08173 | -0.002842 | -0.047909 | 0.072888 | 0.044377 | -0.067295 | 0.043331 | 0.15706 | 0.014094 | -0.11552 | 0.052814 | 0.059844 | -0.015171 | 0.015141 | 1.7561 | 1.6349 | 1.7138 | 1.6687 | 1.7895 | 1.761 | 1.6493 | 0.061642 | 0.17537 | 0.032405 | -0.097212 | 0.071125 | 0.078155 | 0.00314 | 0.033452 | -0.009483 | 0.058502 | -0.03872 | 0.029265
3268.9375 | 121.5408 | -1.5152 | 119.9295 | 0.034862 | -0.086309 | -0.002842 | -0.047909 | 0.077466 | 0.048956 | -0.058139 | 0.038752 | 0.16164 | 0.02325 | -0.10637 | 0.052814 | 0.064423 | -0.019749 | 0.005985 | 1.5501 | 1.4289 | 1.5124 | 1.4673 | 1.5927 | 1.5642 | 1.4571 | 0.057063 | 0.17995 | 0.041561 | -0.088054 | 0.071125 | 0.082734 | -0.001438 | 0.024296 | -0.014062 | 0.058501 | -0.029564 | 0.042999
3270.6875 | 121.5637 | -1.6022 | 119.9158 | 0.025705 | -0.08173 | -0.007421 | -0.043331 | 0.077466 | 0.048956 | -0.053561 | 0.038752 | 0.14332 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.019749 | 0.019719 | 1.6279 | 1.5204 | 1.5948 | 1.5588 | 1.6796 | 1.6511 | 1.5486 | 0.057063 | 0.16163 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | -0.001438 | 0.03803 | -0.01864 | 0.058501 | -0.043298 | 0.033843
3272.3906 | 121.4355 | -1.3596 | 120.195 | 0.034862 | -0.086309 | 0.001736 | -0.038752 | 0.082044 | 0.044377 | -0.058139 | 0.038752 | 0.16164 | 0.014094 | -0.11094 | 0.057392 | 0.064423 | -0.024328 | 0.005985 | 1.3944 | 1.2732 | 1.3613 | 1.3208 | 1.4416 | 1.4039 | 1.3014 | 0.057063 | 0.17995 | 0.032405 | -0.092633 | 0.075703 | 0.082734 | -0.006017 | 0.024296 | -0.01864 | 0.06308 | -0.043298 | 0.038422
3274.1562 | 121.5225 | -1.4145 | 120.0943 | 0.030283 | -0.086309 | 0.001736 | -0.052488 | 0.082044 | 0.048956 | -0.062717 | 0.038752 | 0.1479 | 0.009515 | -0.10637 | 0.06197 | 0.064423 | -0.024328 | 0.015141 | 1.4448 | 1.3282 | 1.4162 | 1.362 | 1.4965 | 1.4634 | 1.3518 | 0.057063 | 0.16621 | 0.027826 | -0.088054 | 0.080281 | 0.082734 | -0.006017 | 0.033452 | -0.023218 | 0.06308 | -0.052455 | 0.033843
3275.8438 | 121.6278 | -1.3504 | 120.1538 | 0.034862 | -0.086309 | -0.002842 | -0.047909 | 0.072888 | 0.039799 | -0.053561 | 0.043331 | 0.15248 | 0.018672 | -0.11552 | 0.057392 | 0.059844 | -0.024328 | 0.010563 | 1.3853 | 1.2641 | 1.3476 | 1.3025 | 1.4233 | 1.3902 | 1.2968 | 0.061642 | 0.17079 | 0.036983 | -0.097212 | 0.075703 | 0.078155 | -0.006017 | 0.028874 | -0.014061 | 0.067659 | -0.03872 | 0.043
3277.5938 | 120.7214 | -120.5795 | 0.19226 | 0.071489 | -0.035942 | 0.033786 | -0.006703 | 0.12325 | 0.085583 | -0.03067 | 0.084537 | 0.19369 | 0.055298 | -0.12468 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 120.651 | 120.5436 | 120.6133 | 120.5728 | 120.7028 | 120.6651 | 120.5489 | 0.10285 | 0.212 | 0.073609 | -0.10637 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.054614 | 0.13176 | 0.025375 | 0.10252
3279.2969 | 121.1105 | -120.7947 | 0.1831 | 0.06691 | -0.040521 | 0.033786 | -0.006703 | 0.11867 | 0.081005 | -0.016936 | 0.079959 | 0.19369 | 0.059877 | -0.12468 | 0.025345 | 0.014064 | -0.042641 | 0.001406 | 120.8616 | 120.7542 | 120.8285 | 120.788 | 120.9133 | 120.8757 | 120.7777 | 0.09827 | 0.212 | 0.078188 | -0.10637 | 0.043656 | 0.032375 | -0.02433 | 0.019717 | 0.054614 | 0.1226 | 0.034532 | 0.10252
3281.0625 | 121.0831 | -120.9366 | 0.18768 | 0.080646 | -0.040521 | 0.033786 | -0.006703 | 0.11409 | 0.085583 | -0.016936 | 0.084537 | 0.16164 | 0.05072 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.012328 | 121.0172 | 120.8961 | 120.9704 | 120.9299 | 121.0507 | 121.0222 | 120.9196 | 0.10285 | 0.17995 | 0.069031 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.005983 | 0.054614 | 0.12718 | 0.020797 | 0.093361
3282.8125 | 121.1243 | -120.9869 | 0.20599 | 0.076067 | -0.0451 | 0.033786 | -0.006703 | 0.10951 | 0.085583 | -0.021514 | 0.079959 | 0.16622 | 0.059877 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.003172 | 121.063 | 120.9418 | 121.0207 | 120.9802 | 121.0964 | 121.0725 | 120.9654 | 0.09827 | 0.18453 | 0.078188 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | 0.029954 | 0.10252
3284.5625 | 121.3074 | -120.9915 | 0.17395 | 0.076067 | -0.0451 | 0.038365 | -0.01586 | 0.11867 | 0.085583 | -0.026092 | 0.07538 | 0.16164 | 0.055298 | -0.1201 | 0.029923 | 0.018642 | -0.042641 | 0.001406 | 121.0676 | 120.9464 | 121.0299 | 120.9757 | 121.1102 | 121.0771 | 120.9654 | 0.093691 | 0.17995 | 0.073609 | -0.10179 | 0.048234 | 0.036953 | -0.02433 | 0.019717 | 0.045457 | 0.11802 | 0.025375 | 0.097939
3286.25 | 121.3211 | -120.9686 | 0.17853 | 0.06691 | -0.0451 | 0.038365 | -0.006703 | 0.11409 | 0.081005 | -0.035248 | 0.084537 | 0.17537 | 0.055298 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.0355 | 120.9235 | 121.007 | 120.9619 | 121.0827 | 121.0496 | 120.9334 | 0.10285 | 0.19368 | 0.073609 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.054614 | 0.12718 | 0.025375 | 0.097939
3288 | 121.1929 | -121.0922 | 0.20142 | 0.076067 | -0.0451 | 0.029208 | -0.006703 | 0.11867 | 0.081005 | -0.021514 | 0.07538 | 0.16164 | 0.055298 | -0.1201 | 0.025345 | 0.02322 | -0.038063 | 0.001406 | 121.1683 | 121.0471 | 121.1214 | 121.0855 | 121.2109 | 121.1732 | 121.0707 | 0.093691 | 0.17995 | 0.073609 | -0.10179 | 0.043656 | 0.041531 | -0.019752 | 0.019717 | 0.050035 | 0.11344 | 0.029953 | 0.093361
3289.7031 | 121.3715 | -121.051 | 0.16937 | 0.071489 | -0.0451 | 0.033786 | -0.006703 | 0.10951 | 0.071848 | -0.035248 | 0.07538 | 0.16622 | 0.05072 | -0.12468 | 0.025345 | 0.027798 | -0.042641 | -0.012328 | 121.1225 | 121.0059 | 121.0848 | 121.0443 | 121.1605 | 121.1229 | 121.0158 | 0.093691 | 0.18453 | 0.069031 | -0.10637 | 0.043656 | 0.046109 | -0.02433 | 0.005983 | 0.050035 | 0.11802 | 0.025375 | 0.093361
3291.4531 | 121.2845 | -121.1105 | 0.21973 | 0.071489 | -0.040521 | 0.038365 | -0.002124 | 0.11867 | 0.081005 | -0.021514 | 0.07538 | 0.16164 | 0.055298 | -0.12468 | 0.039079 | 0.027798 | -0.042641 | -0.00775 | 121.182 | 121.07 | 121.1489 | 121.1084 | 121.2292 | 121.1915 | 121.089 | 0.093691 | 0.17995 | 0.073609 | -0.10637 | 0.05739 | 0.046109 | -0.02433 | 0.010561 | 0.036301 | 0.11802 | 0.016219 | 0.097939
3293.2031 | 121.3257 | -121.1243 | 0.21057 | 0.076067 | -0.058836 | 0.038365 | -0.002124 | 0.11867 | 0.090161 | -0.016936 | 0.089116 | 0.16622 | 0.05072 | -0.12468 | 0.029923 | 0.027798 | -0.038063 | -0.00775 | 121.2003 | 121.0654 | 121.1626 | 121.1221 | 121.2429 | 121.2144 | 121.1073 | 0.10743 | 0.18453 | 0.069031 | -0.10637 | 0.048234 | 0.046109 | -0.019752 | 0.010561 | 0.059193 | 0.12718 | 0.020797 | 0.088783
3294.9844 | 121.4218 | -121.0968 | 0.16937 | 0.076067 | -0.049678 | 0.038365 | -0.002124 | 0.11867 | 0.081005 | -0.026092 | 0.070802 | 0.16164 | 0.055298 | -0.12468 | 0.034501 | 0.027798 | -0.042641 | -0.00775 | 121.1729 | 121.0471 | 121.1352 | 121.0947 | 121.2155 | 121.1778 | 121.0707 | 0.089113 | 0.17995 | 0.073609 | -0.10637 | 0.052812 | 0.046109 | -0.02433 | 0.010561 | 0.036301 | 0.11344 | 0.020797 | 0.097939
3296.6719 | 121.4539 | -121.1563 | 0.19684 | 0.076067 | -0.0451 | 0.038365 | -0.006703 | 0.12782 | 0.085583 | -0.016936 | 0.079959 | 0.16164 | 0.055298 | -0.12468 | 0.034501 | 0.02322 | -0.038063 | -0.003172 | 121.2324 | 121.1112 | 121.1947 | 121.1496 | 121.2841 | 121.2419 | 121.1394 | 0.09827 | 0.17995 | 0.073609 | -0.10637 | 0.052812 | 0.041531 | -0.019752 | 0.015139 | 0.045458 | 0.11802 | 0.020797 | 0.093361
3298.4219 | 121.4355 | -121.1563 | 0.16937 | 0.06691 | -0.054257 | 0.033786 | -0.002124 | 0.11409 | 0.085583 | -0.026092 | 0.07538 | 0.16622 | 0.055298 | -0.1201 | 0.034501 | 0.018642 | -0.04722 | -0.003172 | 121.2232 | 121.1021 | 121.1901 | 121.1542 | 121.2704 | 121.2419 | 121.1302 | 0.093691 | 0.18453 | 0.073609 | -0.10179 | 0.052812 | 0.036953 | -0.028909 | 0.015139 | 0.040879 | 0.1226 | 0.020797 | 0.10252
3300.125 | 121.3394 | -121.2112 | 0.21973 | 0.071489 | -0.054257 | 0.038365 | -0.002124 | 0.11409 | 0.085583 | -0.03067 | 0.079959 | 0.16622 | 0.05072 | -0.12468 | 0.025345 | 0.032376 | -0.042641 | -0.003172 | 121.2827 | 121.157 | 121.2496 | 121.2091 | 121.3253 | 121.2968 | 121.1806 | 0.09827 | 0.18453 | 0.069031 | -0.10637 | 0.043656 | 0.050687 | -0.02433 | 0.015139 | 0.054614 | 0.1226 | 0.025375 | 0.093361
3301.875 | 121.4859 | -121.1884 | 0.16022 | 0.076067 | -0.0451 | 0.033786 | -0.002124 | 0.11867 | 0.081005 | -0.03067 | 0.079959 | 0.16622 | 0.055298 | -0.11552 | 0.034501 | 0.027798 | -0.04722 | -0.003172 | 121.2644 | 121.1433 | 121.2221 | 121.1862 | 121.307 | 121.2694 | 121.1577 | 0.09827 | 0.18453 | 0.073609 | -0.097212 | 0.052812 | 0.046109 | -0.028909 | 0.015139 | 0.045458 | 0.12718 | 0.020797 | 0.10252
3303.625 | 121.4127 | -121.2067 | 0.21057 | 0.076067 | -0.040521 | 0.038365 | -0.011281 | 0.12325 | 0.085583 | -0.021514 | 0.070802 | 0.17537 | 0.05072 | -0.12926 | 0.029923 | 0.018642 | -0.042641 | -0.003172 | 121.2827 | 121.1661 | 121.245 | 121.1954 | 121.3299 | 121.2922 | 121.1852 | 0.089113 | 0.19368 | 0.069031 | -0.11095 | 0.048234 | 0.036953 | -0.02433 | 0.015139 | 0.040879 | 0.11344 | 0.020797 | 0.093361
3305.3281 | 121.4539 | -121.2158 | 0.18768 | 0.071489 | -0.0451 | 0.029208 | -0.002124 | 0.11409 | 0.076426 | -0.026092 | 0.07538 | 0.17079 | 0.055298 | -0.1201 | 0.025345 | 0.018642 | -0.038063 | -0.012328 | 121.2873 | 121.1707 | 121.245 | 121.2137 | 121.3299 | 121.2922 | 121.1897 | 0.093691 | 0.1891 | 0.073609 | -0.10179 | 0.043656 | 0.036953 | -0.019752 | 0.005983 | 0.050035 | 0.11344 | 0.029953 | 0.093361
3307.0938 | 121.4905 | -121.2158 | 0.1831 | 0.076067 | -0.049678 | 0.038365 | -0.002124 | 0.11409 | 0.090161 | -0.026092 | 0.079959 | 0.17537 | 0.055298 | -0.12926 | 0.029923 | 0.018642 | -0.04722 | -0.00775 | 121.2919 | 121.1661 | 121.2542 | 121.2137 | 121.3299 | 121.306 | 121.1897 | 0.09827 | 0.19368 | 0.073609 | -0.11095 | 0.048234 | 0.036953 | -0.028909 | 0.010561 | 0.050036 | 0.12718 | 0.025375 | 0.10252
3308.7969 | 121.5225 | -121.2204 | 0.17395 | 0.076067 | -0.049678 | 0.033786 | -0.002124 | 0.11409 | 0.085583 | -0.03067 | 0.079959 | 0.16622 | 0.055298 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.2965 | 121.1707 | 121.2542 | 121.2183 | 121.3345 | 121.306 | 121.1897 | 0.09827 | 0.18453 | 0.073609 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.025375 | 0.097939
3310.5625 | 121.5546 | -121.2387 | 0.17853 | 0.071489 | -0.0451 | 0.024629 | -0.002124 | 0.11409 | 0.081005 | -0.026092 | 0.079959 | 0.15706 | 0.046142 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.3102 | 121.1936 | 121.2633 | 121.2366 | 121.3528 | 121.3197 | 121.2126 | 0.09827 | 0.17537 | 0.064453 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.016219 | 0.088783
3312.3281 | 121.4401 | -121.2479 | 0.21057 | 0.076067 | -0.035942 | 0.038365 | -0.002124 | 0.11867 | 0.081005 | -0.021514 | 0.079959 | 0.16622 | 0.059877 | -0.12468 | 0.029923 | 0.032376 | -0.04722 | -0.003172 | 121.3239 | 121.2119 | 121.2862 | 121.2457 | 121.3665 | 121.3289 | 121.2264 | 0.09827 | 0.18453 | 0.078188 | -0.10637 | 0.048234 | 0.050687 | -0.028909 | 0.015139 | 0.050036 | 0.12718 | 0.029954 | 0.1071
3314.0156 | 121.4355 | -121.2799 | 0.21973 | 0.076067 | -0.049678 | 0.033786 | -0.006703 | 0.12325 | 0.090161 | -0.035248 | 0.089116 | 0.16164 | 0.055298 | -0.12468 | 0.043657 | 0.02322 | -0.038063 | 0.001406 | 121.356 | 121.2302 | 121.3137 | 121.2732 | 121.4032 | 121.3701 | 121.2447 | 0.10743 | 0.17995 | 0.073609 | -0.10637 | 0.061968 | 0.041531 | -0.019752 | 0.019717 | 0.045459 | 0.12718 | 0.011641 | 0.093361
3315.7656 | 121.4767 | -121.2936 | 0.20599 | 0.071489 | -0.049678 | 0.033786 | -0.011281 | 0.12325 | 0.085583 | -0.026092 | 0.084537 | 0.17079 | 0.05072 | -0.12468 | 0.029923 | 0.027798 | -0.04722 | -0.012328 | 121.3651 | 121.244 | 121.3274 | 121.2824 | 121.4169 | 121.3792 | 121.2675 | 0.10285 | 0.1891 | 0.069031 | -0.10637 | 0.048234 | 0.046109 | -0.028909 | 0.005983 | 0.054614 | 0.13176 | 0.020797 | 0.09794
3317.5312 | 121.5775 | -121.2662 | 0.19226 | 0.071489 | -0.049678 | 0.029208 | -0.011281 | 0.12325 | 0.076426 | -0.021514 | 0.084537 | 0.16622 | 0.05072 | -0.1201 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 121.3377 | 121.2165 | 121.2954 | 121.2549 | 121.3894 | 121.3426 | 121.2447 | 0.10285 | 0.18453 | 0.069031 | -0.10179 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.054614 | 0.1226 | 0.020797 | 0.088783
3319.2344 | 121.5408 | -121.2936 | 0.19226 | 0.080646 | -0.0451 | 0.038365 | -0.006703 | 0.11867 | 0.076426 | -0.021514 | 0.079959 | 0.16164 | 0.059877 | -0.12468 | 0.034501 | 0.027798 | -0.04722 | -0.00775 | 121.3743 | 121.2485 | 121.332 | 121.2869 | 121.4123 | 121.3701 | 121.2721 | 0.09827 | 0.17995 | 0.078188 | -0.10637 | 0.052812 | 0.046109 | -0.028909 | 0.010561 | 0.045458 | 0.12718 | 0.025376 | 0.1071
3321 | 121.5958 | -121.2936 | 0.16022 | 0.076067 | -0.049678 | 0.029208 | -0.006703 | 0.11867 | 0.081005 | -0.03067 | 0.07538 | 0.16164 | 0.059877 | -0.12468 | 0.025345 | 0.02322 | -0.038063 | -0.012328 | 121.3697 | 121.244 | 121.3228 | 121.2869 | 121.4123 | 121.3746 | 121.263 | 0.093691 | 0.17995 | 0.078188 | -0.10637 | 0.043656 | 0.041531 | -0.019752 | 0.005983 | 0.050035 | 0.11344 | 0.034532 | 0.09794
3322.6875 | 121.5546 | -121.3257 | 0.18768 | 0.071489 | -0.049678 | 0.029208 | -0.006703 | 0.11409 | 0.085583 | -0.026092 | 0.079959 | 0.16164 | 0.05072 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.3972 | 121.276 | 121.3549 | 121.319 | 121.4398 | 121.4113 | 121.2996 | 0.09827 | 0.17995 | 0.069031 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | 0.016219 | 0.093361
3324.4375 | 121.669 | -121.3165 | 0.16479 | 0.071489 | -0.0451 | 0.038365 | -0.011281 | 0.11409 | 0.076426 | -0.026092 | 0.084537 | 0.16622 | 0.046142 | -0.12468 | 0.034501 | 0.02322 | -0.038063 | -0.00775 | 121.388 | 121.2714 | 121.3549 | 121.3052 | 121.4306 | 121.393 | 121.2904 | 0.10285 | 0.18453 | 0.064453 | -0.10637 | 0.052812 | 0.041531 | -0.019752 | 0.010561 | 0.050036 | 0.1226 | 0.011641 | 0.084205
3326.1875 | 120.4971 | -120.2316 | 0.15106 | 0.076067 | -0.0451 | 0.038365 | -0.002124 | 0.10951 | 0.071848 | -0.026092 | 0.07538 | 0.16622 | 0.055298 | -0.12468 | 0.039079 | 0.027798 | -0.042641 | -0.00775 | 120.3077 | 120.1865 | 120.27 | 120.2295 | 120.3411 | 120.3035 | 120.2055 | 0.093691 | 0.18453 | 0.073609 | -0.10637 | 0.05739 | 0.046109 | -0.02433 | 0.010561 | 0.036301 | 0.11802 | 0.016219 | 0.097939
3327.9375 | 121.1151 | -120.8817 | 0.16479 | 0.06691 | -0.049678 | 0.033786 | -0.011281 | 0.12782 | 0.081005 | -0.026092 | 0.079959 | 0.16622 | 0.05072 | -0.12926 | 0.034501 | 0.027798 | -0.04722 | -0.00775 | 120.9486 | 120.832 | 120.9154 | 120.8704 | 121.0095 | 120.9627 | 120.8556 | 0.09827 | 0.18453 | 0.069031 | -0.11095 | 0.052812 | 0.046109 | -0.028909 | 0.010561 | 0.045458 | 0.12718 | 0.016219 | 0.09794
3329.7031 | 121.1792 | -121.0098 | 0.18768 | 0.076067 | -0.049678 | 0.038365 | -0.002124 | 0.11867 | 0.090161 | -0.016936 | 0.079959 | 0.16622 | 0.05072 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 121.0859 | 120.9601 | 121.0482 | 121.0077 | 121.1285 | 121.1 | 120.9929 | 0.09827 | 0.18453 | 0.069031 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.045458 | 0.1226 | 0.016219 | 0.093361
3331.4062 | 121.2433 | -121.0602 | 0.19226 | 0.06691 | -0.049678 | 0.042944 | -0.002124 | 0.11867 | 0.085583 | -0.021514 | 0.079959 | 0.15706 | 0.055298 | -0.12468 | 0.039079 | 0.02322 | -0.042641 | -0.00775 | 121.1271 | 121.0105 | 121.1031 | 121.0581 | 121.1788 | 121.1458 | 121.0387 | 0.09827 | 0.17537 | 0.073609 | -0.10637 | 0.05739 | 0.041531 | -0.02433 | 0.010561 | 0.04088 | 0.1226 | 0.016219 | 0.097939
3333.1719 | 121.3623 | -121.0144 | 0.16479 | 0.076067 | -0.0451 | 0.033786 | -0.006703 | 0.11409 | 0.081005 | -0.03067 | 0.07538 | 0.16164 | 0.05072 | -0.1201 | 0.034501 | 0.027798 | -0.042641 | -0.012328 | 121.0905 | 120.9693 | 121.0482 | 121.0077 | 121.1285 | 121.0954 | 120.9837 | 0.093691 | 0.17995 | 0.069031 | -0.10179 | 0.052812 | 0.046109 | -0.02433 | 0.005983 | 0.040879 | 0.11802 | 0.016219 | 0.093361
3334.875 | 121.3394 | -121.0922 | 0.16022 | 0.071489 | -0.0451 | 0.033786 | -0.002124 | 0.11409 | 0.081005 | -0.026092 | 0.079959 | 0.16622 | 0.05072 | -0.1201 | 0.029923 | 0.027798 | -0.042641 | -0.012328 | 121.1637 | 121.0471 | 121.126 | 121.0901 | 121.2063 | 121.1732 | 121.0661 | 0.09827 | 0.18453 | 0.069031 | -0.10179 | 0.048234 | 0.046109 | -0.02433 | 0.005983 | 0.050036 | 0.1226 | 0.020797 | 0.093361
3336.625 | 121.2799 | -121.1563 | 0.19226 | 0.076067 | -0.049678 | 0.029208 | -0.002124 | 0.12782 | 0.085583 | -0.021514 | 0.089116 | 0.17079 | 0.05072 | -0.1201 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.2324 | 121.1066 | 121.1855 | 121.1542 | 121.2841 | 121.2419 | 121.1348 | 0.10743 | 0.1891 | 0.069031 | -0.10179 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.059193 | 0.13176 | 0.020797 | 0.093361
3338.3281 | 121.3257 | -121.1655 | 0.16937 | 0.06691 | -0.049678 | 0.038365 | -0.002124 | 0.11409 | 0.085583 | -0.021514 | 0.079959 | 0.16622 | 0.05072 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.2324 | 121.1158 | 121.2038 | 121.1633 | 121.2796 | 121.251 | 121.144 | 0.09827 | 0.18453 | 0.069031 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | 0.016219 | 0.093361
3340.0938 | 121.4127 | -121.1563 | 0.17395 | 0.071489 | -0.0451 | 0.033786 | -0.006703 | 0.11867 | 0.076426 | -0.021514 | 0.079959 | 0.15706 | 0.05072 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.2278 | 121.1112 | 121.1901 | 121.1496 | 121.275 | 121.2327 | 121.1348 | 0.09827 | 0.17537 | 0.069031 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.020797 | 0.093361
3341.8281 | 121.431 | -121.1609 | 0.19226 | 0.06691 | -0.054257 | 0.038365 | -0.002124 | 0.12325 | 0.085583 | -0.026092 | 0.079959 | 0.16164 | 0.055298 | -0.12926 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.2278 | 121.1066 | 121.1993 | 121.1588 | 121.2841 | 121.2465 | 121.1348 | 0.09827 | 0.17995 | 0.073609 | -0.11095 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.045458 | 0.1226 | 0.020797 | 0.097939
3343.5312 | 121.4035 | -121.1975 | 0.1831 | 0.080646 | -0.049678 | 0.029208 | -0.002124 | 0.12325 | 0.090161 | -0.021514 | 0.07538 | 0.16622 | 0.05072 | -0.12926 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 121.2782 | 121.1478 | 121.2267 | 121.1954 | 121.3208 | 121.2877 | 121.176 | 0.093691 | 0.18453 | 0.069031 | -0.11095 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | 0.020797 | 0.088783
3345.2969 | 121.1746 | -121.0739 | 0.20142 | 0.076067 | -0.049678 | 0.038365 | -0.002124 | 0.11867 | 0.081005 | -0.021514 | 0.07538 | 0.16622 | 0.05072 | -0.12468 | 0.025345 | 0.032376 | -0.042641 | -0.003172 | 121.15 | 121.0242 | 121.1123 | 121.0718 | 121.1926 | 121.1549 | 121.0524 | 0.093691 | 0.18453 | 0.069031 | -0.10637 | 0.043656 | 0.050687 | -0.02433 | 0.015139 | 0.050035 | 0.11802 | 0.025375 | 0.093361
3347 | 121.2387 | -121.1517 | 0.21973 | 0.071489 | -0.049678 | 0.029208 | -0.011281 | 0.11867 | 0.085583 | -0.021514 | 0.07538 | 0.16164 | 0.05072 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.00775 | 121.2232 | 121.1021 | 121.1809 | 121.1405 | 121.2704 | 121.2373 | 121.1302 | 0.093691 | 0.17995 | 0.069031 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.010561 | 0.045457 | 0.11802 | 0.020797 | 0.093361
3348.75 | 121.4218 | -121.1243 | 0.16937 | 0.076067 | -0.054257 | 0.038365 | -0.01586 | 0.11867 | 0.081005 | -0.021514 | 0.079959 | 0.16164 | 0.05072 | -0.11552 | 0.029923 | 0.027798 | -0.033484 | -0.003172 | 121.2003 | 121.07 | 121.1626 | 121.1084 | 121.2429 | 121.2053 | 121.1028 | 0.09827 | 0.17995 | 0.069031 | -0.097212 | 0.048234 | 0.046109 | -0.015173 | 0.015139 | 0.050036 | 0.11344 | 0.020797 | 0.084204
3350.5156 | 121.3165 | -121.1609 | 0.21057 | 0.071489 | -0.049678 | 0.038365 | -0.006703 | 0.12325 | 0.081005 | -0.021514 | 0.07538 | 0.16164 | 0.055298 | -0.12468 | 0.029923 | 0.027798 | -0.042641 | -0.012328 | 121.2324 | 121.1112 | 121.1993 | 121.1542 | 121.2841 | 121.2419 | 121.1394 | 0.093691 | 0.17995 | 0.073609 | -0.10637 | 0.048234 | 0.046109 | -0.02433 | 0.005983 | 0.045457 | 0.11802 | 0.025375 | 0.097939
3352.2188 | 121.4401 | -121.1792 | 0.16937 | 0.071489 | -0.0451 | 0.029208 | -0.011281 | 0.11867 | 0.076426 | -0.021514 | 0.07538 | 0.16622 | 0.055298 | -0.1201 | 0.029923 | 0.02322 | -0.04722 | -0.003172 | 121.2507 | 121.1341 | 121.2084 | 121.1679 | 121.2979 | 121.2556 | 121.1577 | 0.093691 | 0.18453 | 0.073609 | -0.10179 | 0.048234 | 0.041531 | -0.028909 | 0.015139 | 0.045457 | 0.1226 | 0.025375 | 0.10252
3353.9688 | 121.3394 | -121.2067 | 0.19684 | 0.071489 | -0.0451 | 0.038365 | -0.011281 | 0.11409 | 0.076426 | -0.021514 | 0.079959 | 0.16164 | 0.055298 | -0.1201 | 0.034501 | 0.02322 | -0.051798 | -0.00775 | 121.2782 | 121.1616 | 121.245 | 121.1954 | 121.3208 | 121.2831 | 121.1852 | 0.09827 | 0.17995 | 0.073609 | -0.10179 | 0.052812 | 0.041531 | -0.033487 | 0.010561 | 0.045458 | 0.13176 | 0.020797 | 0.1071
3355.6719 | 121.463 | -121.1975 | 0.18768 | 0.06691 | -0.054257 | 0.033786 | -0.006703 | 0.11867 | 0.081005 | -0.016936 | 0.07538 | 0.16622 | 0.046142 | -0.11552 | 0.029923 | 0.02322 | -0.038063 | -0.003172 | 121.2644 | 121.1433 | 121.2313 | 121.1908 | 121.3162 | 121.2785 | 121.1806 | 0.093691 | 0.18453 | 0.064453 | -0.097212 | 0.048234 | 0.041531 | -0.019752 | 0.015139 | 0.045457 | 0.11344 | 0.016219 | 0.084205
3357.4375 | 121.5363 | -121.1792 | 0.1831 | 0.071489 | -0.0451 | 0.038365 | -0.006703 | 0.11867 | 0.076426 | -0.021514 | 0.079959 | 0.16164 | 0.055298 | -0.12468 | 0.029923 | 0.02322 | -0.042641 | -0.003172 | 121.2507 | 121.1341 | 121.2176 | 121.1725 | 121.2979 | 121.2556 | 121.1577 | 0.09827 | 0.17995 | 0.073609 | -0.10637 | 0.048234 | 0.041531 | -0.02433 | 0.015139 | 0.050036 | 0.1226 | 0.025375 | 0.097939
3359.1875 | 121.3898 | -121.2753 | 0.23346 | 0.071489 | -0.049678 | 0.033786 | -0.006703 | 0.12325 | 0.081005 | -0.021514 | 0.079959 | 0.16622 | 0.05072 | -0.12468 | 0.034501 | 0.018642 | -0.04722 | 0.001406 | 121.3468 | 121.2257 | 121.3091 | 121.2686 | 121.3986 | 121.3563 | 121.2538 | 0.09827 | 0.18453 | 0.069031 | -0.10637 | 0.052812 | 0.036953 | -0.028909 | 0.019717 | 0.045458 | 0.12718 | 0.016219 | 0.09794
3360.9531 | 121.4264 | -121.2433 | 0.23346 | 0.071489 | -0.054257 | 0.038365 | -0.006703 | 0.11409 | 0.076426 | -0.016936 | 0.079959 | 0.16164 | 0.055298 | -0.1201 | 0.029923 | 0.02322 | -0.042641 | -0.00775 | 121.3148 | 121.189 | 121.2817 | 121.2366 | 121.3574 | 121.3197 | 121.2263 | 0.09827 | 0.17995 | 0.073609 | -0.10179 | 0.048234 | 0.041531 | -0.02433 | 0.010561 | 0.050036 | 0.1226 | 0.025375 | 0.097939
3362.7031 | 121.4905 | -121.2753 | 0.20599 | 0.076067 | -0.049678 | 0.038365 | -0.002124 | 0.11867 | 0.090161 | -0.016936 | 0.084537 | 0.16622 | 0.05072 | -0.12468 | 0.034501 | 0.02322 | -0.042641 | -0.003172 | 121.3514 | 121.2257 | 121.3137 | 121.2732 | 121.394 | 121.3655 | 121.2584 | 0.10285 | 0.18453 | 0.069031 | -0.10637 | 0.052812 | 0.041531 | -0.02433 | 0.015139 | 0.050036 | 0.12718 | 0.016219 | 0.093361
3364.4688 | 121.5317 | -121.2433 | 0.18768 | 0.071489 | -0.054257 | 0.029208 | -0.006703 | 0.12782 | 0.085583 | -0.026092 | 0.079959 | 0.16622 | 0.055298 | -0.13384 | 0.034501 | 0.032376 | -0.042641 | -0.00775 | 121.3148 | 121.189 | 121.2725 | 121.2366 | 121.3711 | 121.3289 | 121.2172 | 0.09827 | 0.18453 | 0.073609 | -0.11553 | 0.052812 | 0.050687 | -0.02433 | 0.010561 | 0.045458 | 0.1226 | 0.020797 | 0.097939
3366.1719 | 121.5088 | -121.2799 | 0.19684 | 0.071489 | -0.054257 | 0.038365 | -0.011281 | 0.12325 | 0.085583 | -0.026092 | 0.070802 | 0.16164 | 0.05072 | -0.1201 | 0.034501 | 0.02322 | -0.042641 | -0.00775 | 121.3514 | 121.2256 | 121.3183 | 121.2686 | 121.4032 | 121.3655 | 121.2538 | 0.089113 | 0.17995 | 0.069031 | -0.10179 | 0.052812 | 0.041531 | -0.02433 | 0.010561 | 0.036301 | 0.11344 | 0.016219 | 0.093361
3367.9219 | 121.582 | -121.3028 | 0.18768 | 0.062332 | -0.049678 | 0.038365 | -0.002124 | 0.11867 | 0.081005 | -0.021514 | 0.079959 | 0.16164 | 0.055298 | -0.12468 | 0.034501 | 0.018642 | -0.042641 | -0.00775 | 121.3651 | 121.2531 | 121.3412 | 121.3007 | 121.4215 | 121.3838 | 121.2813 | 0.09827 | 0.17995 | 0.073609 | -0.10637 | 0.052812 | 0.036953 | -0.02433 | 0.010561 | 0.045458 | 0.1226 | 0.020797 | 0.097939
3369.6094 | 121.4767 | -121.3257 | 0.20599 | 0.06691 | -0.049678 | 0.038365 | -0.011281 | 0.1324 | 0.085583 | -0.016936 | 0.084537 | 0.15706 | 0.059877 | -0.12468 | 0.034501 | 0.018642 | -0.038063 | -0.00775 | 121.3926 | 121.276 | 121.364 | 121.3144 | 121.4581 | 121.4113 | 121.3087 | 0.10285 | 0.17537 | 0.078188 | -0.10637 | 0.052812 | 0.036953 | -0.019752 | 0.010561 | 0.050036 | 0.1226 | 0.025376 | 0.09794
3371.3594 | 121.55 | -121.3348 | 0.21515 | 0.076067 | -0.0451 | 0.033786 | -0.002124 | 0.12325 | 0.081005 | -0.021514 | 0.070802 | 0.16622 | 0.046142 | -0.1201 | 0.029923 | 0.018642 | -0.04722 | -0.016906 | 121.4109 | 121.2897 | 121.3686 | 121.3327 | 121.4581 | 121.4158 | 121.3133 | 0.089113 | 0.18453 | 0.064453 | -0.10179 | 0.048234 | 0.036953 | -0.028909 | 0.001405 | 0.040879 | 0.11802 | 0.016219 | 0.093362

## Thermal Data
Fire Time | A Position - Middle
-0.9333 | 84.6108
0.0667 | 96.6753
1.0667 | 99.3685
2.0667 | 105.6539
3.0667 | 111.5778
4.0667 | 118.9512
5.0667 | 123.258
6.0667 | 133.328
7.0667 | 138.5202
8.0667 | 147.3482
9.0667 | 154.4281
10.0667 | 162.8701
11.0667 | 167.4889
12.0667 | 171.6021
13.0667 | 177.5693
14.0667 | 181.3498
15.0667 | 185.7165
16.0667 | 191.7332
17.0667 | 193.6549
18.0667 | 198.2119
19.0667 | 201.9307
20.0667 | 210.2672
21.0667 | 211.5144
22.0667 | 216.8494
23.0667 | 217.4239
24.0667 | 221.1363
25.0667 | 229.842
26.0667 | 233.0347
27.0667 | 232.9074
28.0667 | 232.4504
29.0667 | 231.074
30.0667 | 235.1717
31.0667 | 238.0788
32.0667 | 241.9093
33.0667 | 243.353
34.0667 | 249.0651
35.0667 | 248.7255
36.0667 | 247.8415
37.0667 | 247.5532
38.0667 | 251.5994
39.0667 | 257.7093
40.0667 | 258.4181
41.0667 | 260.0256
42.0667 | 263.3768
43.0667 | 264.8913
44.0667 | 271.9528
45.0667 | 274.2797
46.0667 | 279.5788
47.0667 | 279.0551
48.0667 | 281.0047
49.0667 | 278.1157
50.0667 | 280.8461
51.0667 | 279.6977
52.0667 | 277.785
53.0667 | 280.8469
54.0667 | 280.8719
55.0667 | 288.4768
56.0667 | 290.8182
57.0667 | 293.5766
58.0667 | 301.4231
59.0667 | 304.5394
60.0667 | 303.535
61.0667 | 302.5182
62.0667 | 300.0097
63.0667 | 296.8646
64.0667 | 306.9042
65.0667 | 312.6309
66.0667 | 310.7478
67.0667 | 308.6905
68.0667 | 311.1447
69.0667 | 311.3314
70.0667 | 310.6243
71.0667 | 308.6806
72.0667 | 310.1795
73.0667 | 306.762
74.0667 | 306.3167
75.0667 | 305.2017
76.0667 | 301.5781
77.0667 | 297.576
78.0667 | 297.2431
79.0667 | 301.2282
80.0667 | 295.006
81.0667 | 295.1183
82.0667 | 296.2938
83.0667 | 293.39
84.0667 | 293.3883
85.0667 | 292.9071
86.0667 | 292.8877
87.0667 | 290.3328
88.0667 | 289.6539
89.0667 | 293.9559
90.0823 | 296.2372
91.0667 | 296.6056
92.0667 | 299.9011
93.0667 | 303.3369
94.0667 | 304.7821
95.0667 | 300.9838
96.0667 | 301.1522
97.0667 | 300.5176
98.0667 | 303.4541
99.0667 | 307.2865
100.0667 | 310.8143
101.0667 | 316.7622
102.0667 | 316.7831
103.0667 | 321.2158
104.0667 | 328.3971
105.0667 | 329.6432
106.0667 | 327.6177
107.0667 | 332.2389
108.0667 | 331.3112
109.0667 | 333.6576
110.0667 | 332.3301
111.0667 | 329.0191
112.0667 | 330.2967
113.0667 | 330.0352
114.0667 | 329.4604
115.0667 | 331.5425
116.0667 | 332.6526
117.0667 | 334.5793
118.0667 | 332.9898
119.0667 | 331.3709
120.0667 | 332.9154
121.0667 | 334.1193
122.0667 | 333.3014
123.0667 | 335.1713
124.0667 | 338.1441
125.0667 | 339.8467
126.0979 | 343.2752
127.0823 | 339.5531
128.0667 | 336.5799
129.0667 | 338.1803
130.0823 | 340.5755
131.0667 | 340.0061
132.0667 | 337.1794
133.0667 | 336.9078
134.0667 | 333.5559
135.0823 | 330.0366
136.0667 | 333.1222
137.0667 | 337.1217
138.0667 | 334.2605
139.0667 | 329.3516
140.0667 | 327.0314
141.0667 | 327.0873
142.0667 | 328.009
143.0667 | 322.9597
144.0667 | 324.6409
145.0823 | 322.4318
146.0667 | 320.5602
147.0667 | 315.8566
148.0667 | 312.7363
149.0667 | 319.765
150.0667 | 324.2758
151.0667 | 334.1369
152.0667 | 332.632
153.0667 | 333.0358
154.0667 | 336.9894
155.0667 | 337.1748
156.0667 | 337.5556
157.0667 | 342.3021
158.0667 | 351.7828
159.0667 | 360.1005
160.0667 | 352.7876
161.0667 | 352.7428
162.0667 | 355.4191
163.0667 | 359.0671
164.0667 | 357.8799
165.0667 | 358.0207
166.0667 | 355.782
167.0667 | 359.5534
168.0667 | 373.3115
169.0667 | 373.9709
170.0667 | 374.6956
171.0667 | 378.6419
172.0667 | 377.8592
173.0667 | 375.3315
174.0667 | 376.8575
175.0667 | 379.5562
176.0667 | 384.3049
177.0667 | 384.6338
178.0823 | 380.7137
179.0823 | 378.3821
180.0667 | 376.7782
181.0667 | 378.4844
182.0667 | 375.6002
183.0667 | 371.9639
184.0667 | 364.7091
185.0667 | 364.0201
186.0667 | 358.9102
187.0667 | 360.0804
188.0667 | 364.9439
189.0667 | 371.9308
190.0667 | 379.5681
191.0667 | 377.9009
192.0667 | 376.4025
193.0667 | 378.9324
194.0667 | 379.8364
195.0667 | 377.8016
196.0667 | 372.8583
197.0667 | 371.5485
198.0667 | 369.6426
199.0667 | 374.0979
200.0667 | 373.7825
201.0667 | 371.9177
202.0667 | 370.9757
203.0667 | 370.4422
204.0667 | 368.366
205.0667 | 363.0946
206.0667 | 356.8551
207.0667 | 353.2872
208.0667 | 351.6888
209.0667 | 347.6872
210.0667 | 344.5279
211.0667 | 346.5892
212.0667 | 341.7588
213.0667 | 340.1193
214.0667 | 339.3571
215.0667 | 350.7551
216.0667 | 347.4023
217.0667 | 346.5867
218.0667 | 345.5083
219.0667 | 344.817
220.0667 | 345.1332
221.0667 | 344.0305
222.0667 | 346.231
223.0667 | 352.3182
224.0667 | 361.181
225.0667 | 365.1492
226.0667 | 365.4306
227.0667 | 363.0063
228.0667 | 367.3205
229.0667 | 372.3246
230.0667 | 369.7535
231.0667 | 368.244
232.0667 | 365.2612
233.0667 | 362.8313
234.0667 | 356.8445
235.0667 | 355.642
236.0667 | 351.8449
237.0667 | 352.221
238.0667 | 351.0598
239.0667 | 348.891
240.0667 | 345.3876
241.0667 | 344.8609
242.0667 | 341.9305
243.0667 | 341.5765
244.0667 | 337.8789
245.0667 | 336.1517
246.0667 | 335.752
247.0667 | 339.4275
248.0667 | 346.5338
249.0667 | 346.6402
250.0667 | 344.2013
251.0667 | 346.5421
252.0667 | 349.1929
253.0667 | 346.9046
254.0667 | 345.7034
255.0667 | 343.8274
256.0667 | 347.3817
257.0667 | 346.0664
258.0667 | 343.7467
259.0667 | 342.9557
260.0667 | 345.1966
261.0667 | 346.6112
262.0667 | 344.1894
263.0667 | 345.8051
264.0667 | 346.484
265.0667 | 344.7805
266.0667 | 347.9771
267.0667 | 345.1716
268.0667 | 341.3942
269.0667 | 340.4492
270.0667 | 343.847
271.0667 | 344.9084
272.0667 | 345.4999
273.0667 | 350.1784
274.0667 | 352.9128
275.0667 | 356.0911
276.0667 | 358.7085
277.0667 | 364.672
278.0667 | 368.538
279.0667 | 372.7493
280.0667 | 376.6235
281.0667 | 376.1696
282.0667 | 378.5192
283.0667 | 384.6224
284.0667 | 389.5734
285.0667 | 393.1029
286.0667 | 396.9291
287.0667 | 399.5396
288.0667 | 400.3395
289.0667 | 406.6907
290.0667 | 407.9044
291.0667 | 406.626
292.0667 | 406.6581
293.0667 | 406.5832
294.0667 | 406.0848
295.0667 | 405.5507
296.0667 | 403.6474
297.0667 | 402.8307
298.0667 | 400.548
299.0667 | 396.7533
300.0667 | 393.195
301.0667 | 391.3581
302.0667 | 391.4642
303.0823 | 392.1402
304.0823 | 390.2674
305.0667 | 389.9729
306.0667 | 389.902
307.0667 | 387.846
308.0667 | 387.6504
309.0667 | 386.4828
310.0667 | 384.5128
311.0667 | 385.0304
312.0667 | 385.1229
313.0667 | 380.928
314.0667 | 380.3949
315.0667 | 381.9225
316.0667 | 381.4137
317.0667 | 377.099
318.0667 | 376.7115
319.0667 | 374.0692
320.0667 | 378.7903
321.0667 | 380.2903
322.0667 | 381.125
323.0667 | 384.0134
324.0667 | 384.6468
325.0667 | 385.8653
326.0667 | 389.3658
327.0667 | 389.6285
328.0667 | 393.9433
329.0667 | 393.4778
330.0667 | 393.031
331.0667 | 396.4875
332.0667 | 394.383
333.0667 | 393.8664
334.0667 | 394.8748
335.0667 | 393.4528
336.0667 | 389.9751
337.0667 | 393.8875
338.0667 | 393.838
339.0667 | 394.8148
340.0667 | 398.2726
341.0667 | 394.2732
342.0667 | 395.9047
343.0667 | 390.7531
344.0823 | 391.8429
345.0667 | 391.5046
346.0667 | 389.5709
347.0667 | 388.7785
348.0667 | 389.976
349.0667 | 389.6579
350.0667 | 394.2117
351.0667 | 394.4328
352.0667 | 393.4584
353.0667 | 390.4548
354.0667 | 392.1669
355.0667 | 390.5518
356.0667 | 390.3125
357.0667 | 388.1615
358.0667 | 384.0403
359.0667 | 380.7925
360.0667 | 379.1231
361.0667 | 378.9149
362.0667 | 387.6606
363.0667 | 389.9568
364.0667 | 387.7164
365.0667 | 389.7127
366.0667 | 390.68
367.0667 | 393.8541
368.0823 | 394.9183
369.0667 | 398.1651
370.0667 | 401.36
371.0667 | 401.2816
372.0667 | 398.5758
373.0667 | 402.1039
374.0823 | 404.815
375.0667 | 404.0344
376.0667 | 405.7521
377.0667 | 404.0998
378.0667 | 407.1067
379.0667 | 410.9105
380.0667 | 411.3552
381.0667 | 411.5864
382.0667 | 413.9434
383.0667 | 412.8205
384.0667 | 414.763
385.0667 | 415.6793
386.0667 | 413.7213
387.0667 | 410.7844
388.0667 | 408.436
389.0667 | 407.1801
390.0667 | 405.7992
391.0667 | 402.0946
392.0667 | 399.8352
393.0823 | 399.8117
394.0823 | 399.816
395.0667 | 397.4729
396.0667 | 395.8464
397.0667 | 397.3663
398.0667 | 397.4631
399.0667 | 397.8704
400.0667 | 398.7612
401.0667 | 396.0807
402.0667 | 396.7052
403.0667 | 394.1606
404.0823 | 390.6426
405.0667 | 390.7305
406.0667 | 390.7554
407.0667 | 389.8475
408.0667 | 386.2076
409.0667 | 386.4493
410.0667 | 390.431
411.0667 | 393.2533
412.0667 | 394.7459
413.0667 | 398.9449
414.0667 | 395.8217
415.0667 | 398.1155
416.0667 | 397.8023
417.0667 | 396.5632
418.0667 | 395.719
419.0667 | 392.5929
420.0667 | 394.3817
421.0667 | 394.4457
422.0667 | 398.504
423.0667 | 400.3221
424.0667 | 400.5773
425.0667 | 401.1422
426.0667 | 400.0311
427.0667 | 399.351
428.0667 | 400.6384
429.0667 | 403.5896
430.0667 | 401.7603
431.0667 | 400.0229
432.0667 | 401.459
433.0667 | 397.2448
434.0667 | 396.6078
435.0667 | 397.5694
436.0667 | 396.4688
437.0667 | 396.9763
438.0667 | 394.7242
439.0667 | 394.749
440.0667 | 392.3326
441.0667 | 389.2703
442.0667 | 387.9409
443.0667 | 388.5401
444.0667 | 387.6157
445.0667 | 388.358
446.0667 | 386.1737
447.0667 | 386.3279
448.0667 | 389.7211
449.0667 | 393.9657
450.0667 | 387.2641
451.0667 | 394.9078
452.0667 | 397.73
453.0667 | 419.5741
454.0667 | 435.0872
455.0667 | 454.2835
456.0667 | 465.1315
457.0667 | 468.5997
458.0667 | 468.4474
459.0667 | 465.8703
460.0667 | 464.9355
461.0667 | 489.7711
462.0667 | 500.7967
463.0667 | 514.095
464.0667 | 514.5279
465.0667 | 545.4133
466.0667 | 555.8838
467.0667 | 561.0422
468.0667 | 570.801
469.0667 | 576.3308
470.0667 | 585.213
471.0667 | 604.6811
472.0667 | 623.8894
473.0667 | 643.8354
474.0667 | 646.2306
475.0667 | 642.388
476.0667 | 642.7952
477.0667 | 644.0147
478.0667 | 638.75
479.0667 | 625.6663
480.0667 | 621.4641
481.0667 | 619.9921
482.0667 | 618.454
483.0667 | 632.6459
484.0667 | 635.6341
485.0667 | 640.1443
486.0667 | 648.2735
487.0667 | 649.7095
488.0667 | 633.4769
489.0667 | 642.4451
490.0667 | 652.7938
491.0667 | 648.7921
492.0667 | 652.3075
493.0667 | 668.8146
494.0823 | 651.5007
495.0667 | 663.5997
496.0667 | 651.7717
497.0667 | 644.6657
498.0667 | 629.5183
499.0667 | 640.1594
500.0667 | 632.0714
501.0667 | 630.6608
502.0667 | 630.6276
503.0667 | 632.2653
504.0667 | 648.6022
505.0667 | 632.9568
506.0667 | 644.4934
507.0667 | 647.9371
508.0667 | 662.0357
509.0667 | 682.7966
510.0667 | 695.7422
511.0667 | 708.0111
512.0667 | 711.0398
513.0667 | 717.1896
514.0667 | 718.6647
515.0667 | 716.3639
516.0823 | 728.6879
517.0823 | 724.0096
518.0667 | 700.757
519.0667 | 698.8987
520.0667 | 708.0619
521.0823 | 701.8954
522.0667 | 707.7596
523.0823 | 703.7109
524.0823 | 709.5699
525.0667 | 710.725
526.0667 | 717.0074
527.0667 | 720.8149
528.0667 | 722.4773
529.0667 | 712.0589
530.0667 | 709.7959
531.0667 | 717.2488
532.0667 | 714.9878
533.0667 | 697.0241
534.0667 | 693.4659
535.0667 | 702.0089
536.0667 | 702.2816
537.0667 | 706.0453
538.0667 | 689.9112
539.0667 | 673.6926
540.0667 | 681.4913
541.0667 | 680.2147
542.0667 | 671.7656
543.0667 | 691.0796
544.0667 | 693.9324
545.0667 | 696.5377
546.0667 | 692.4091
547.0667 | 698.4328
548.0667 | 705.705
549.0667 | 715.1585
550.0667 | 707.1192
551.0667 | 705.3448
552.0823 | 717.7072
553.0667 | 725.0992
554.0823 | 724.6436
555.0667 | 724.3706
556.0667 | 722.8031
557.0667 | 724.7408
558.0667 | 735.1908
559.0823 | 736.6657
560.0667 | 722.8297
561.0667 | 726.7921
562.0823 | 720.6298
563.0667 | 724.3086
564.0667 | 734.8676
565.0667 | 731.7374
566.0667 | 736.7136
567.0667 | 742.9007
568.0667 | 742.6104
569.0667 | 743.6242
570.0667 | 741.6489
571.0667 | 748.8514
572.0667 | 737.9556
573.0667 | 734.4708
574.0667 | 737.0074
575.0667 | 741.6656
576.0667 | 753.2407
577.0667 | 755.9917
578.0667 | 742.373
579.0667 | 731.1147
580.0667 | 733.0031
581.0667 | 735.4892
582.0667 | 738.3078
583.0667 | 736.7522
584.0823 | 734.2941
585.0667 | 731.3738
586.0667 | 742.7608
587.0667 | 733.7069
588.0667 | 742.8007
589.0667 | 740.5627
590.0667 | 727.7465
591.0667 | 738.4382
592.0667 | 729.4331
593.0667 | 726.9149
594.0667 | 728.499
595.0667 | 731.4159
596.0667 | 734.4553
597.0667 | 737.6597
598.0667 | 743.6593
599.0667 | 735.5874
600.0667 | 742.5458
601.0667 | 739.378
602.0667 | 738.4846
603.0667 | 743.2833
604.0667 | 738.0747
605.0667 | 739.3466
606.0667 | 736.7572
607.0667 | 726.9028
608.0667 | 717.4024
609.0667 | 718.9825
610.0667 | 720.0583
611.0667 | 711.4431
612.0667 | 705.6591
613.0667 | 708.9721
614.0667 | 710.7347
615.0667 | 691.3118
616.0667 | 685.9933
617.0667 | 687.3769
618.0667 | 693.3244
619.0667 | 677.0065
620.0667 | 657.0283
621.0667 | 658.9214
622.0667 | 663.3237
623.0667 | 659.7354
624.0667 | 658.611
625.0667 | 647.3427
626.0667 | 655.9375
627.0667 | 647.3805
628.0667 | 626.7991
629.0667 | 621.2188
630.0667 | 613.1875
631.0667 | 618.2273
632.0667 | 609.1051
633.0667 | 604.4083
634.0667 | 604.4201
635.0667 | 597.2198
636.0667 | 589.1744
637.0667 | 594.5695
638.0667 | 592.9889
639.0667 | 598.8371
640.0667 | 602.7893
641.0667 | 606.5731
642.0667 | 609.2653
643.0667 | 613.9576
644.0667 | 611.1303
645.0667 | 608.5732
646.0667 | 613.2403
647.0667 | 601.4495
648.0667 | 601.8766
649.0667 | 604.3151
650.0667 | 591.925
651.0667 | 590.6019
652.0667 | 589.946
653.0667 | 578.2694
654.0667 | 568.8042
655.0667 | 562.8375
656.0667 | 557.7894
657.0667 | 555.5477
658.0667 | 550.771
659.0667 | 543.3452
660.0667 | 530.9111
661.0667 | 524.3018
662.0667 | 520.6218
663.0667 | 531.5455
664.0667 | 525.0397
665.0667 | 524.1118
666.0667 | 521.1153
667.0667 | 520.7799
668.0667 | 532.7196
669.0667 | 532.775
670.0667 | 526.6894
671.0667 | 523.5803
672.0667 | 523.6122
673.0667 | 529.215
674.0667 | 521.2017
675.0667 | 513.0927
676.0667 | 508.0864
677.0667 | 504.4688
678.0667 | 512.692
679.0667 | 517.2733
680.0667 | 517.5943
681.0667 | 511.7627
682.0667 | 507.0157
683.0667 | 503.5237
684.0667 | 501.9193
685.0667 | 509.0452
686.0667 | 503.6649
687.0667 | 498.3771
688.0667 | 501.8692
689.0667 | 497.6609
690.0667 | 491.2696
691.0667 | 488.9739
692.0667 | 485.7777
693.0667 | 485.5464
694.0667 | 493.3642
695.0667 | 485.8923
696.0667 | 478.5358
697.0667 | 478.7651
698.0667 | 481.3467
699.0667 | 481.6283
700.0667 | 480.5434
701.0667 | 477.7434
702.0667 | 475.2851
703.0667 | 475.0652
704.0667 | 478.2839
705.0667 | 477.1419
706.0667 | 477.7604
707.0667 | 479.2178
708.0667 | 474.9338
709.0667 | 474.7066
710.0667 | 509.9029
711.0667 | 501.263
712.0667 | 500.5335
713.0667 | 504.1349
714.0667 | 500.1567
715.0667 | 495.0133
716.0667 | 492.6584
717.0667 | 500.9886
718.0667 | 501.8261
719.0667 | 504.2784
720.0667 | 506.0715
721.0667 | 508.8216
722.0667 | 508.4098
723.0667 | 514.8099
724.0667 | 539.3171
725.0667 | 529.5778
726.0667 | 522.3205
727.0667 | 518.5941
728.0667 | 521.9132
729.0667 | 527.4891
730.0667 | 529.3863
731.0667 | 532.8465
732.0667 | 529.2874
733.0667 | 539.0519
734.0667 | 543.426
735.0667 | 544.4476
736.0667 | 536.5868
737.0667 | 533.3542
738.0667 | 530.9915
739.0667 | 539.134
740.0667 | 533.7309
741.0667 | 542.4067
742.0667 | 555.7277
743.0667 | 560.4815
744.0667 | 556.3842
745.0667 | 569.0867
746.0667 | 587.9422
747.0667 | 591.2707
748.0823 | 602.1249
749.0667 | 599.6519
750.0823 | 593.6467
751.0667 | 602.9995
752.0667 | 610.5952
753.0667 | 613.9395
754.0823 | 613.9067
755.0667 | 610.3735
756.0667 | 615.749
757.0667 | 611.7561
758.0667 | 614.9586
759.0667 | 597.1564
760.0667 | 587.9955
761.0667 | 586.7455
762.0667 | 585.2372
763.0667 | 595.9283
764.0667 | 606.1921
765.0667 | 625.9747
766.0667 | 634.4659
767.0667 | 632.1016
768.0667 | 636.9512
769.0667 | 633.0934
770.0667 | 631.3259
771.0667 | 634.7733
772.0667 | 632.0868
773.0667 | 628.3259
774.0667 | 633.2663
775.0667 | 642.1016
776.0667 | 641.0282
777.0667 | 643.8966
778.0667 | 638.8751
779.0667 | 637.8958
780.0667 | 639.2728
781.0667 | 640.1467
782.0667 | 644.4464
783.0667 | 650.5624
784.0667 | 668.1094
785.0667 | 673.8452
786.0667 | 679.3337
787.0667 | 665.2207
788.0667 | 667.7958
789.0667 | 670.1689
790.0667 | 691.4757
791.0667 | 676.714
792.0667 | 676.987
793.0667 | 673.026
794.0667 | 668.5231
795.0667 | 661.6825
796.0667 | 657.8058
797.0667 | 664.6605
798.0667 | 665.8507
799.0667 | 667.241
800.0667 | 678.0327
801.0823 | 680.9984
802.0667 | 666.619
803.0667 | 665.4606
804.0667 | 660.8736
805.0823 | 667.3933
806.0667 | 663.3882
807.0667 | 654.5703
808.0667 | 669.2416
809.0667 | 664.7283
810.0667 | 651.8409
811.0667 | 653.7316
812.0667 | 651.7216
813.0667 | 647.2459
814.0667 | 648.032
815.0667 | 656.8465
816.0667 | 655.9435
817.0667 | 649.8148
818.0667 | 643.2114
819.0667 | 642.9642
820.0667 | 632.1613
821.0823 | 635.9895
822.0667 | 634.5378
823.0667 | 633.5718
824.0667 | 634.4294
825.0667 | 621.7438
826.0667 | 608.7909
827.0667 | 605.4359
828.0667 | 602.0145
829.0667 | 600.5936
830.0667 | 598.222
831.0667 | 601.1664
832.0667 | 598.6857
833.0667 | 604.3156
834.0667 | 604.9365
835.0667 | 601.3325
836.0667 | 596.708
837.0667 | 592.776
838.0667 | 583.9842
839.0667 | 577.9757
840.0667 | 572.7343
841.0667 | 570.2352
842.0667 | 566.5811
843.0667 | 570.3661
844.0667 | 567.5581
845.0667 | 563.0886
846.0667 | 562.6932
847.0667 | 568.3635
848.0667 | 567.7431
849.0667 | 567.8757
850.0667 | 568.1839
851.0667 | 574.3762
852.0667 | 584.2154
853.0667 | 593.6183
854.0667 | 585.9802
855.0667 | 578.8815
856.0667 | 576.4518
857.0667 | 572.821
858.0667 | 574.4005
859.0823 | 573.4216
860.0823 | 566.428
861.0667 | 562.8792
862.0667 | 557.4699
863.0667 | 559.5432
864.0667 | 559.767
865.0667 | 557.3579
866.0667 | 556.2097
867.0667 | 548.9033
868.0667 | 544.3718
869.0667 | 544.6792
870.0667 | 537.8294
871.0667 | 529.4611
872.0667 | 521.4984
873.0667 | 517.9017
874.0667 | 514.6043
875.0667 | 511.6234
876.0667 | 506.1998
877.0667 | 505.2144
878.0667 | 508.8604
879.0667 | 507.8903
880.0667 | 510.6764
881.0667 | 512.2684
882.0667 | 510.0267
883.0667 | 507.8777
884.0667 | 507.4187
885.0667 | 503.7152
886.0667 | 505.0702
887.0667 | 502.3528
888.0667 | 500.064
889.0667 | 496.6169
890.0667 | 495.6801
891.0667 | 497.2043
892.0667 | 499.7402
893.0667 | 498.7973
894.0667 | 496.375
895.0667 | 507.4109
896.0667 | 520.9978
897.0667 | 519.2859
898.0667 | 520.6887
899.0667 | 529.1856
900.0667 | 520.6716
901.0667 | 522.8811
902.0667 | 516.8943
903.0667 | 506.9616
904.0667 | 504.6181
905.0667 | 506.2678
906.0667 | 515.0577
907.0667 | 508.848
908.0667 | 506.0609
909.0667 | 502.6999
910.0667 | 503.6697
911.0667 | 497.2279
912.0667 | 494.8141
913.0667 | 495.139
914.0667 | 496.0595
915.0667 | 496.9312
916.0667 | 495.8076
917.0667 | 499.5689
918.0667 | 504.6618
919.0667 | 512.223
920.0667 | 512.6487
921.0667 | 512.5212
922.0667 | 512.7805
923.0667 | 513.9639
924.0667 | 507.4513
925.0667 | 514.2942
926.0667 | 511.1494
927.0667 | 515.8812
928.0667 | 519.2016
929.0667 | 521.6741
930.0667 | 526.3004
931.0667 | 537.0226
932.0667 | 542.9213
933.0667 | 542.2606
934.0667 | 541.7453
935.0667 | 538.8041
936.0667 | 536.2934
937.0667 | 532.6603
938.0667 | 529.6903
939.0667 | 527.722
940.0667 | 536.9216
941.0667 | 534.9115
942.0667 | 532.4346
943.0667 | 533.5138
944.0667 | 535.1142
945.0667 | 535.6282
946.0667 | 536.2941
947.0667 | 533.5536
948.0667 | 553.1321
949.0667 | 545.4265
950.0667 | 544.1024
951.0667 | 540.9419
952.0667 | 533.9863
953.0667 | 534.7505
954.0667 | 534.7393
955.0667 | 533.3623
956.0667 | 531.036
957.0667 | 529.9032
958.0667 | 533.2371
959.0667 | 533.2281
960.0667 | 537.1826
961.0667 | 541.4429
962.0667 | 554.07
963.0667 | 567.5782
964.0667 | 575.284
965.0667 | 571.3556
966.0667 | 571.2485
967.0667 | 567.3286
968.0667 | 565.1369
969.0667 | 561.8568
970.0667 | 572.8603
971.0667 | 575.7803
972.0667 | 572.609
973.0667 | 569.9527
974.0667 | 568.0522
975.0667 | 566.8603
976.0667 | 573.7806
977.0667 | 570.3513
978.0667 | 570.8079
979.0667 | 579.4783
980.0667 | 602.4594
981.0667 | 608.341
982.0667 | 603.5398
983.0667 | 599.5935
984.0667 | 598.9271
985.0667 | 603.4215
986.0667 | 613.8119
987.0667 | 624.4887
988.0667 | 619.106
989.0667 | 625.5948
990.0667 | 618.9327
991.0667 | 616.6952
992.0667 | 619.6049
993.0667 | 616.7574
994.0667 | 629.1217
995.0667 | 639.189
996.0823 | 641.9332
997.0823 | 635.7608
998.0667 | 642.1114
999.0667 | 643.6381
1000.0823 | 641.2566
1001.0667 | 639.1142
1002.0823 | 642.162
1003.0667 | 666.8055
1004.0667 | 682.7529
1005.0667 | 688.9949
1006.0667 | 687.9074
1007.0667 | 705.1496
1008.0667 | 695.0812
1009.0667 | 689.3921
1010.0667 | 693.3342
1011.0667 | 691.9798
1012.0667 | 692.676
1013.0667 | 693.4776
1014.0667 | 693.2448
1015.0667 | 705.6475
1016.0667 | 711.4595
1017.0667 | 709.7281
1018.0667 | 716.4553
1019.0667 | 712.4443
1020.0667 | 715.1699
1021.0667 | 728.5532
1022.0667 | 737.706
1023.0667 | 742.0348
1024.0667 | 738.9257
1025.0667 | 735.4536
1026.0667 | 728.1538
1027.0667 | 711.779
1028.0823 | 711.4872
1029.0667 | 705.7666
1030.0667 | 705.5152
1031.0667 | 705.2914
1032.0667 | 713.5429
1033.0667 | 697.2084
1034.0667 | 705.6297
1035.0667 | 711.0616
1036.0667 | 705.623
1037.0667 | 715.9914
1038.0667 | 709.1034
1039.0667 | 696.566
1040.0667 | 694.2754
1041.0667 | 691.3492
1042.0667 | 696.9385
1043.0667 | 710.1513
1044.0667 | 714.2648
1045.0667 | 707.0102
1046.0667 | 705.657
1047.0667 | 710.4468
1048.0667 | 715.259
1049.0667 | 710.9268
1050.0667 | 713.3746
1051.0667 | 721.9153
1052.0667 | 726.0403
1053.0667 | 732.3237
1054.0667 | 732.8351
1055.0667 | 728.247
1056.0667 | 721.6061
1057.0667 | 724.8505
1058.0667 | 714.0174
1059.0667 | 709.5346
1060.0667 | 714.8087
1061.0667 | 715.0547
1062.0667 | 713.0042
1063.0667 | 710.42
1064.0667 | 728.1426
1065.0667 | 729.5256
1066.0667 | 730.1029
1067.0667 | 731.9314
1068.0667 | 728.3894
1069.0667 | 727.6268
1070.0667 | 732.7277
1071.0667 | 735.8167
1072.0667 | 743.5556
1073.0667 | 746.9084
1074.0667 | 752.3574
1075.0667 | 751.492
1076.0667 | 746.3009
1077.0667 | 751.4939
1078.0667 | 744.1113
1079.0667 | 747.8428
1080.0667 | 755.5957
1081.0667 | 746.3607
1082.0667 | 737.6747
1083.0667 | 731.1529
1084.0667 | 724.518
1085.0667 | 717.8204
1086.0667 | 721.297
1087.0667 | 720.5262
1088.0667 | 718.0355
1089.0667 | 722.2165
1090.0667 | 715.0724
1091.0667 | 712.9919
1092.0667 | 714.0347
1093.0667 | 713.3651
1094.0667 | 716.8567
1095.0667 | 721.3395
1096.0667 | 714.6244
1097.0667 | 712.8849
1098.0667 | 713.6571
1099.0667 | 715.6087
1100.0667 | 720.639
1101.0667 | 716.9007
1102.0667 | 714.0497
1103.0667 | 715.44
1104.0667 | 721.833
1105.0823 | 724.6505
1106.0667 | 715.7423
1107.0667 | 709.6181
1108.0667 | 706.2618
1109.0667 | 710.1427
1110.0667 | 714.1583
1111.0667 | 716.8021
1112.0667 | 731.6585
1113.0667 | 734.1661
1114.0667 | 736.7609
1115.0667 | 731.929
1116.0667 | 725.2444
1117.0667 | 723.7548
1118.0667 | 722.2548
1119.0667 | 725.0763
1120.0667 | 716.8563
1121.0667 | 708.8337
1122.0667 | 704.9388
1123.0667 | 708.5997
1124.0667 | 702.6715
1125.0667 | 706.2322
1126.0667 | 713.4059
1127.0667 | 709.2548
1128.0667 | 702.6214
1129.0667 | 699.9259
1130.0667 | 696.2753
1131.0667 | 694.8868
1132.0667 | 692.9664
1133.0667 | 697.4317
1134.0667 | 693.1548
1135.0667 | 695.1181
1136.0667 | 697.8991
1137.0667 | 688.2692
1138.0667 | 681.1087
1139.0667 | 677.5025
1140.0667 | 674.0985
1141.0667 | 671.0091
1142.0667 | 681.0782
1143.0667 | 681.5828
1144.0667 | 701.1487
1145.0667 | 701.8636
1146.0667 | 701.2178
1147.0667 | 705.4861
1148.0667 | 701.8029
1149.0667 | 703.8042
1150.0667 | 703.1315
1151.0667 | 700.5241
1152.0667 | 711.797
1153.0667 | 706.4765
1154.0667 | 710.9068
1155.0667 | 702.3172
1156.0667 | 719.9962
1157.0667 | 716.0014
1158.0667 | 715.5532
1159.0667 | 714.3229
1160.0667 | 706.2134
1161.0667 | 702.0513
1162.0667 | 699.3869
1163.0667 | 703.352
1164.0667 | 709.4467
1165.0667 | 707.1641
1166.0667 | 707.6578
1167.0667 | 716.4563
1168.0667 | 717.5471
1169.0667 | 715.4382
1170.0667 | 723.2306
1171.0667 | 731.1499
1172.0667 | 733.6237
1173.0667 | 735.8363
1174.0667 | 728.3134
1175.0667 | 724.1365
1176.0667 | 718.5839
1177.0667 | 714.5282
1178.0667 | 712.7399
1179.0667 | 717.0888
1180.0667 | 721.1015
1181.0667 | 722.267
1182.0667 | 718.3666
1183.0667 | 711.3578
1184.0667 | 708.9984
1185.0667 | 703.4368
1186.0667 | 698.6543
1187.0667 | 701.7486
1188.0667 | 705.8224
1189.0667 | 708.3262
1190.0667 | 712.4543
1191.0667 | 709.4865
1192.0667 | 713.0652
1193.0667 | 712.929
1194.0667 | 714.0689
1195.0667 | 718.6754
1196.0667 | 711.3763
1197.0667 | 711.8409
1198.0667 | 707.9364
1199.0667 | 706.8208
1200.0667 | 709.9836
1201.0667 | 709.6192
1202.0667 | 714.0843
1203.0667 | 708.4897
1204.0667 | 708.5117
1205.0667 | 709.7119
1206.0667 | 717.2206
1207.0667 | 714.3904
1208.0667 | 714.3718
1209.0667 | 708.0916
1210.0667 | 702.1332
1211.0667 | 699.2438
1212.0667 | 709.6223
1213.0667 | 715.5046
1214.0667 | 722.9494
1215.0667 | 725.2415
1216.0667 | 726.2867
1217.0667 | 727.1675
1218.0667 | 721.4505
1219.0667 | 729.8051
1220.0667 | 726.8967
1221.0667 | 721.6307
1222.0667 | 713.9943
1223.0667 | 719.8434
1224.0667 | 721.1739
1225.0667 | 717.4329
1226.0667 | 724.193
1227.0667 | 724.9851
1228.0667 | 726.3081
1229.0667 | 724.4947
1230.0667 | 727.7619
1231.0667 | 722.7338
1232.0667 | 725.4367
1233.0667 | 717.6826
1234.0667 | 710.1528
1235.0667 | 709.5988
1236.0667 | 705.4821
1237.0667 | 699.7545
1238.0667 | 701.3398
1239.0667 | 702.2328
1240.0667 | 701.4289
1241.0667 | 699.54
1242.0667 | 697.1285
1243.0667 | 704.1146
1244.0823 | 702.9729
1245.0667 | 707.2604
1246.0667 | 708.5608
1247.0667 | 703.1523
1248.0667 | 708.0782
1249.0667 | 702.7339
1250.0667 | 698.9334
1251.0667 | 698.1627
1252.0667 | 697.273
1253.0667 | 696.0977
1254.0667 | 694.813
1255.0667 | 709.628
1256.0667 | 711.4219
1257.0667 | 709.4056
1258.0667 | 714.1444
1259.0667 | 704.3801
1260.0667 | 715.7306
1261.0667 | 711.5615
1262.0667 | 703.6919
1263.0667 | 706.85
1264.0667 | 715.959
1265.0667 | 714.0955
1266.0667 | 716.0377
1267.0667 | 713.2762
1268.0667 | 710.7208
1269.0667 | 709.1621
1270.0667 | 716.3118
1271.0667 | 708.4071
1272.0667 | 706.7016
1273.0667 | 706.5426
1274.0667 | 704.3427
1275.0667 | 706.5417
1276.0667 | 702.8866
1277.0667 | 704.2425
1278.0667 | 706.791
1279.0667 | 700.8806
1280.0667 | 705.7176
1281.0667 | 705.4867
1282.0667 | 698.2507
1283.0667 | 688.3566
1284.0667 | 678.7991
1285.0667 | 670.7642
1286.0667 | 664.8176
1287.0667 | 659.7103
1288.0667 | 654.4542
1289.0667 | 650.1892
1290.0667 | 646.099
1291.0667 | 642.7097
1292.0667 | 639.7021
1293.0667 | 638.0452
1294.0667 | 636.2088
1295.0667 | 635.1555
1296.0667 | 634.2858
1297.0667 | 633.3169
1298.0667 | 632.3101
1299.0667 | 632.5732
1300.0667 | 632.6056
1301.0667 | 632.3015
1302.0667 | 631.8569
1303.0667 | 633.145
1304.0667 | 634.6828
1305.0667 | 637.0182
1306.0667 | 637.2158
1307.0667 | 639.2068
1308.0667 | 639.7742
1309.0667 | 639.6697
1310.0667 | 640.117
1311.0667 | 640.3248
1312.0667 | 640.0121
1313.0667 | 639.3393
1314.0667 | 638.3447
1315.0667 | 638.2204
1316.0667 | 637.1743
1317.0667 | 635.7421
1318.0667 | 635.5256
1319.0667 | 635.5843
1320.0667 | 635.1919
1321.0667 | 634.5768
1322.0667 | 633.9045
1323.0667 | 633.5316
1324.0667 | 634.3382
1325.0667 | 634.8365
1326.0667 | 634.3798
1327.0667 | 633.4264
1328.0667 | 633.2452
1329.0667 | 632.8109
1330.0667 | 632.6573
1331.0667 | 631.688
1332.0667 | 631.0897
1333.0667 | 630.4156
1334.0667 | 629.0258
1335.0667 | 628.0306
1336.0667 | 627.0111
1337.0667 | 626.5613
1338.0667 | 625.1133
1339.0667 | 624.5713
1340.0667 | 623.8287
1341.0667 | 623.6153
1342.0667 | 622.9506
1343.0667 | 623.3262
1344.0667 | 624.0644
1345.0667 | 624.0836
1346.0667 | 624.4988
1347.0667 | 624.9203
1348.0667 | 624.5045
1349.0667 | 625.2946
1350.0667 | 625.2891
1351.0667 | 627.9902
1352.0667 | 630.6312
1353.0667 | 635.4055
1354.0667 | 638.2069
1355.0667 | 638.8669
1356.0667 | 639.2117
1357.0667 | 643.4406
1358.0667 | 643.3336
1359.0667 | 643.4301
1360.0667 | 641.8576
1361.0667 | 642.1684
1362.0667 | 645.0553
1363.0667 | 646.2203
1364.0667 | 646.5221
1365.0667 | 647.199
1366.0667 | 645.4772
1367.0667 | 645.2634
1368.0667 | 645.6535
1369.0667 | 643.376
1370.0667 | 644.2757
1371.0667 | 647.1889
1372.0667 | 645.4802
1373.0667 | 645.3374
1374.0667 | 645.0261
1375.0667 | 644.0267
1376.0667 | 641.7732
1377.0667 | 646.1799
1378.0667 | 645.9189
1379.0667 | 644.4937
1380.0667 | 640.7607
1381.0667 | 637.2644
1382.0667 | 633.5498
1383.0667 | 633.7931
1384.0667 | 634.452
1385.0667 | 634.1593
1386.0667 | 633.5233
1387.0667 | 631.8277
1388.0667 | 630.8422
1389.0667 | 635.6525
1390.0667 | 636.0787
1391.0667 | 636.0132
1392.0667 | 637.2829
1393.0667 | 638.9389
1394.0667 | 639.9582
1395.0667 | 638.6541
1396.2542 | 637.968
1397.1292 | 642.6093
1398.2385 | 642.4971
1399.1135 | 642.3287
1400.5823 | 639.1475
1401.3479 | 638.7801
1402.0667 | 640.0949
1403.0667 | 643.4198
1404.0667 | 642.9342
1405.0667 | 642.2223
1406.0667 | 644.2149
1407.0667 | 644.9335
1408.0667 | 647.1007
1409.0667 | 649.0783
1410.0667 | 647.6757
1411.0667 | 644.6612
1412.0667 | 643.5152
1413.0667 | 640.0882
1414.0667 | 641.0586
1415.0667 | 638.7614
1416.0667 | 636.3814
1417.0667 | 635.3731
1418.0667 | 635.0167
1419.0667 | 636.6042
1420.0667 | 638.053
1421.0667 | 636.1779
1422.0667 | 635.8568
1423.0667 | 637.0168
1424.0667 | 634.5026
1425.0667 | 632.9778
1426.0667 | 637.1599
1427.0667 | 635.8992
1428.0667 | 637.5542
1429.0667 | 638.7809
1430.0667 | 639.1033
1431.0667 | 641.5066
1432.0667 | 640.7196
1433.0667 | 643.9385
1434.0823 | 642.429
1435.0667 | 643.5281
1436.0823 | 646.497
1437.0667 | 644.3923
1438.0979 | 646.6307
1439.0667 | 646.5727
1440.0667 | 649.1244
1441.0667 | 649.495
1442.0667 | 649.2193
1443.0667 | 647.5201
1444.0667 | 651.1382
1445.0667 | 650.8729
1446.0667 | 647.7607
1447.0667 | 646.64
1448.0667 | 643.4836
1449.0667 | 644.9229
1450.0667 | 647.6009
1451.0667 | 651.4681
1452.0667 | 656.4597
1453.0667 | 655.1666
1454.0667 | 653.308
1455.0823 | 649.1608
1456.0667 | 651.2608
1457.0667 | 659.1062
1458.0667 | 655.5845
1459.0667 | 656.1389
1460.0667 | 655.8963
1461.0667 | 656.0568
1462.0667 | 653.6115
1463.0667 | 657.1329
1464.0667 | 654.4299
1465.0667 | 655.5063
1466.0667 | 651.669
1467.0667 | 648.891
1468.0823 | 652.0967
1469.0979 | 648.28
1470.0823 | 647.5786
1471.0823 | 645.4782
1472.0667 | 646.0982
1473.0823 | 646.0748
1474.0667 | 643.2115
1475.0667 | 639.1513
1476.0667 | 636.0311
1477.0667 | 630.923
1478.0667 | 626.1269
1479.0667 | 623.1825
1480.0667 | 623.7592
1481.0667 | 623.4262
1482.0667 | 624.768
1483.0667 | 628.6836
1484.0667 | 631.0287
1485.0823 | 630.5194
1486.0667 | 630.3062
1487.0667 | 630.9812
1488.0667 | 630.5043
1489.0667 | 629.1587
1490.0667 | 630.9917
1491.0667 | 633.0228
1492.0667 | 634.1171
1493.0667 | 634.6569
1494.0667 | 635.9144
1495.0667 | 633.8464
1496.0667 | 643.5096
1497.0667 | 650.9731
1498.0667 | 645.3214
1499.0667 | 644.5128
1500.0667 | 645.3632
1501.0667 | 645.5779
1502.0667 | 645.7277
1503.0667 | 644.2222
1504.0667 | 646.315
1505.0667 | 642.7507
1506.0667 | 644.0539
1507.0667 | 642.3689
1508.0667 | 645.8831
1509.0667 | 646.7132
1510.0667 | 650.0945
1511.0667 | 648.6052
1512.0667 | 644.5498
1513.0667 | 641.4376
1514.0667 | 639.2508
1515.0667 | 637.2911
1516.0667 | 634.7245
1517.0667 | 637.4248
1518.0667 | 633.9388
1519.0667 | 643.0546
1520.0667 | 641.1658
1521.0667 | 640.2349
1522.0667 | 637.4219
1523.0667 | 637.2165
1524.0667 | 639.8858
1525.0667 | 637.545
1526.0667 | 636.6245
1527.0667 | 646.1403
1528.0667 | 649.9181
1529.0667 | 646.6184
1530.0667 | 644.5231
1531.0667 | 649.9296
1532.0667 | 647.1788
1533.0667 | 645.6275
1534.0667 | 646.3534
1535.0667 | 647.1702
1536.0667 | 652.7981
1537.0667 | 651.012
1538.0667 | 651.1202
1539.0667 | 650.1809
1540.0667 | 651.3225
1541.0667 | 651.4568
1542.0667 | 650.5457
1543.0667 | 649.0716
1544.0667 | 646.9836
1545.0667 | 644.3946
1546.0667 | 642.8249
1547.0667 | 643.9823
1548.0667 | 642.6129
1549.0667 | 642.0051
1550.0667 | 643.7403
1551.0667 | 645.0399
1552.0667 | 642.1922
1553.0667 | 649.3255
1554.0667 | 648.9654
1555.0667 | 652.2966
1556.0667 | 649.0834
1557.0667 | 651.3314
1558.0667 | 652.487
1559.0667 | 647.0739
1560.0667 | 646.6103
1561.0667 | 651.0463
1562.0667 | 656.8667
1563.0667 | 660.6228
1564.0667 | 655.53
1565.0667 | 651.5134
1566.0667 | 652.8362
1567.0667 | 654.5608
1568.0667 | 653.5983
1569.0667 | 652.4635
1570.0667 | 650.103
1571.0667 | 646.1902
1572.0667 | 649.8017
1573.0667 | 650.784
1574.0667 | 652.3917
1575.0823 | 653.7576
1576.0667 | 651.2591
1577.0667 | 650.5707
1578.0667 | 651.8905
1579.0667 | 653.2191
1580.0667 | 655.6131
1581.0667 | 652.8969
1582.0667 | 649.0805
1583.0667 | 648.331
1584.0667 | 647.0493
1585.0667 | 645.1108
1586.0667 | 644.1343
1587.0667 | 642.4358
1588.0667 | 649.6273
1589.0667 | 649.6953
1590.0667 | 646.2771
1591.0667 | 645.7043
1592.0667 | 648.0093
1593.0667 | 643.9366
1594.0667 | 643.817
1595.0667 | 640.6832
1596.0667 | 638.2859
1597.0667 | 638.0194
1598.0667 | 636.7286
1599.0667 | 635.0908
1600.0667 | 637.8412
1601.0667 | 639.6321
1602.0667 | 638.6091
1603.0667 | 640.3371
1604.0667 | 641.131
1605.0667 | 641.2692
1606.0667 | 640.5099
1607.0667 | 640.7285
1608.0667 | 648.7391
1609.0667 | 650.8836
1610.0667 | 644.8792
1611.0667 | 645.8938
1612.0667 | 651.2924
1613.0667 | 651.9343
1614.0667 | 649.1047
1615.0667 | 646.4752
1616.0667 | 643.7587
1617.0667 | 644.4297
1618.0667 | 642.7047
1619.0667 | 642.3363
1620.0667 | 645.3111
1621.0667 | 644.5642
1622.0667 | 642.3126
1623.0667 | 644.0618
1624.0667 | 643.4091
1625.0667 | 642.7712
1626.0667 | 644.8851
1627.0667 | 643.8276
1628.0667 | 643.0086
1629.0667 | 651.1313
1630.0667 | 650.1708
1631.0667 | 651.8957
1632.0667 | 657.1946
1633.0667 | 659.6639
1634.0667 | 659.8227
1635.0667 | 663.6054
1636.0667 | 674.0375
1637.0667 | 675.2609
1638.0667 | 674.5017
1639.0667 | 681.1697
1640.0667 | 682.5699
1641.0667 | 676.1039
1642.0667 | 673.5121
1643.0667 | 667.9922
1644.0667 | 666.6464
1645.0667 | 660.2871
1646.0667 | 655.4574
1647.0667 | 655.6951
1648.0667 | 658.1105
1649.0667 | 656.4518
1650.0667 | 657.0355
1651.0667 | 657.2442
1652.0667 | 656.9267
1653.0667 | 661.7802
1654.0667 | 662.4333
1655.0667 | 660.7435
1656.0667 | 665.3486
1657.0667 | 667.2232
1658.0667 | 679.7821
1659.0667 | 671.4438
1660.0667 | 674.8267
1661.0667 | 681.6585
1662.0667 | 679.8157
1663.0667 | 676.9103
1664.0667 | 675.9907
1665.0667 | 672.7916
1666.0667 | 673.4411
1667.0667 | 669.5151
1668.0667 | 665.9184
1669.0667 | 664.7855
1670.0667 | 666.2675
1671.0667 | 672.6177
1672.0667 | 672.6593
1673.0667 | 670.5528
1674.0667 | 667.9537
1675.0667 | 669.2639
1676.0667 | 672.5666
1677.0667 | 677.2293
1678.0667 | 676.5468
1679.0667 | 674.1314
1680.0667 | 675.4262
1681.0667 | 669.9662
1682.0667 | 665.068
1683.0667 | 664.7023
1684.0667 | 668.3269
1685.0667 | 674.5433
1686.0667 | 678.1396
1687.0667 | 673.853
1688.0667 | 670.1463
1689.0667 | 669.2555
1690.0667 | 663.9398
1691.0667 | 663.687
1692.0667 | 659.9013
1693.0667 | 661.424
1694.0667 | 662.7195
1695.0667 | 664.5362
1696.0667 | 668.6215
1697.0667 | 671.5936
1698.0667 | 672.6792
1699.0667 | 670.537
1700.0667 | 670.8302
1701.0667 | 670.6802
1702.0667 | 679.1793
1703.0667 | 675.9514
1704.0667 | 676.6996
1705.0667 | 679.7079
1706.0667 | 680.092
1707.0667 | 678.4433
1708.0667 | 685.6626
1709.0667 | 691.9016
1710.0667 | 693.6807
1711.0667 | 693.2443
1712.0667 | 703.1489
1713.0667 | 702.5169
1714.0667 | 704.196
1715.0667 | 700.8384
1716.0667 | 703.8154
1717.0667 | 707.6931
1718.0667 | 708.4987
1719.0667 | 705.0411
1720.0667 | 700.5809
1721.0667 | 696.0555
1722.0667 | 695.1184
1723.0667 | 691.8264
1724.0667 | 687.7417
1725.0667 | 683.3124
1726.0667 | 680.14
1727.0667 | 675.1274
1728.0667 | 673.8057
1729.0667 | 669.83
1730.0667 | 668.1546
1731.0667 | 670.1913
1732.0667 | 667.7917
1733.0667 | 667.9433
1734.0667 | 669.238
1735.0667 | 664.833
1736.0667 | 662.7793
1737.0667 | 666.4427
1738.0667 | 675.7481
1739.0667 | 678.4672
1740.0667 | 679.8657
1741.0667 | 681.5614
1742.0667 | 685.377
1743.0667 | 688.6445
1744.0667 | 692.4648
1745.0667 | 689.2011
1746.0667 | 688.0103
1747.0667 | 690.5999
1748.0667 | 695.9372
1749.0667 | 696.0023
1750.0667 | 696.0915
1751.0667 | 695.953
1752.0667 | 693.0944
1753.0667 | 688.0004
1754.0667 | 686.438
1755.0667 | 684.302
1756.0667 | 685.5444
1757.0667 | 684.6078
1758.0667 | 686.5507
1759.0667 | 691.888
1760.0667 | 691.5316
1761.0667 | 689.6674
1762.0667 | 686.5831
1763.0667 | 684.2324
1764.0667 | 683.4337
1765.0667 | 686.6909
1766.0667 | 684.7304
1767.0667 | 690.3996
1768.0667 | 693.5222
1769.0667 | 691.5601
1770.0667 | 690.6933
1771.0667 | 692.0916
1772.0667 | 688.5969
1773.0667 | 690.9268
1774.0667 | 697.2531
1775.0667 | 698.0773
1776.0667 | 694.7459
1777.0667 | 691.6331
1778.0667 | 691.2886
1779.0667 | 691.4341
1780.0667 | 692.4878
1781.0667 | 694.235
1782.0667 | 698.9292
1783.0667 | 698.3525
1784.0667 | 694.2281
1785.0667 | 691.1592
1786.0667 | 693.2642
1787.0667 | 693.9207
1788.0667 | 695.0546
1789.0667 | 697.1183
1790.0667 | 703.162
1791.0667 | 715.3689
1792.0667 | 711.1587
1793.0667 | 707.2626
1794.0667 | 704.2181
1795.0667 | 704.3415
1796.0667 | 701.8627
1797.0667 | 705.8754
1798.0667 | 710.3205
1799.0667 | 706.0962
1800.0667 | 705.4978
1801.0667 | 702.1647
1802.0667 | 705.4123
1803.0667 | 705.869
1804.0667 | 699.3139
1805.0667 | 694.0685
1806.0667 | 696.7277
1807.0667 | 696.7576
1808.0667 | 695.8921
1809.0667 | 691.5797
1810.0667 | 690.5056
1811.0667 | 697.1795
1812.0667 | 694.7918
1813.0667 | 697.9194
1814.0667 | 699.1685
1815.0667 | 697.6682
1816.0667 | 703.0385
1817.0667 | 702.246
1818.0667 | 702.2364
1819.0667 | 702.9493
1820.0667 | 699.581
1821.0667 | 698.0499
1822.0667 | 702.816
1823.0667 | 706.3431
1824.0667 | 709.6068
1825.0667 | 714.4552
1826.0667 | 719.9131
1827.0667 | 718.628
1828.0667 | 719.1016
1829.0667 | 721.6937
1830.0667 | 722.384
1831.0667 | 721.9847
1832.0667 | 714.8506
1833.0667 | 713.9802
1834.0667 | 712.6343
1835.0667 | 716.397
1836.0667 | 715.3801
1837.0667 | 714.8124
1838.0667 | 714.8948
1839.0667 | 716.6968
1840.0667 | 715.8566
1841.0667 | 714.0648
1842.0667 | 713.4645
1843.0667 | 714.4341
1844.0667 | 716.7843
1845.0667 | 714.217
1846.0667 | 719.6002
1847.0667 | 719.204
1848.0667 | 719.6986
1849.0667 | 721.4246
1850.0667 | 721.0187
1851.0667 | 717.4347
1852.0667 | 713.0551
1853.0667 | 717.5138
1854.0667 | 720.979
1855.0667 | 718.813
1856.0667 | 716.8989
1857.0667 | 713.3684
1858.0667 | 713.6121
1859.0667 | 711.5812
1860.0667 | 709.8277
1861.0667 | 707.4539
1862.0667 | 704.2247
1863.0667 | 701.3283
1864.0667 | 697.7848
1865.0667 | 695.3368
1866.0667 | 695.3539
1867.0667 | 694.4608
1868.0667 | 692.9679
1869.0667 | 690.0557
1870.0667 | 687.6722
1871.0667 | 686.9836
1872.0667 | 687.6535
1873.0667 | 687.6365
1874.0667 | 686.8301
1875.0667 | 686.7334
1876.0667 | 689.8966
1877.0667 | 688.6258
1878.0667 | 690.7119
1879.0667 | 690.3841
1880.0667 | 690.7816
1881.0667 | 691.32
1882.0823 | 692.8018
1883.0823 | 695.0947
1884.0667 | 691.876
1885.0667 | 692.729
1886.0667 | 691.2495
1887.0667 | 694.1788
1888.0667 | 697.2856
1889.0667 | 699.821
1890.0823 | 696.1027
1891.0667 | 696.4195
1892.0667 | 697.8686
1893.0667 | 697.872
1894.0667 | 696.1009
1895.0667 | 700.7649
1896.0667 | 702.7941
1897.0667 | 703.2985
1898.0667 | 703.463
1899.0667 | 703.8278
1900.0667 | 704.667
1901.0667 | 702.8822
1902.0667 | 702.9387
1903.0667 | 700.8599
1904.0667 | 699.3236
1905.0667 | 699.5591
1906.0667 | 695.7839
1907.0667 | 695.4346
1908.0667 | 697.8022
1909.0667 | 699.8372
1910.0667 | 699.2989
1911.0667 | 701.447
1912.0667 | 705.4478
1913.0667 | 708.06
1914.0667 | 709.8774
1915.0667 | 712.5644
1916.0667 | 712.0301
1917.0667 | 716.4449
1918.0667 | 716.7159
1919.0667 | 713.2233
1920.0667 | 710.2598
1921.0667 | 709.36
1922.0667 | 708.8757
1923.0667 | 701.6144
1924.0667 | 701.598
1925.0667 | 698.6752
1926.0667 | 696.2524
1927.0667 | 696.0292
1928.0667 | 693.004
1929.0667 | 688.1079
1930.0667 | 687.1359
1931.0667 | 686.314
1932.0667 | 687.6638
1933.0667 | 688.0066
1934.0667 | 689.4444
1935.0667 | 695.4617
1936.0667 | 696.0447
1937.0667 | 697.0164
1938.0667 | 698.8019
1939.0667 | 702.0029
1940.0667 | 701.6011
1941.0667 | 703.3714
1942.0667 | 702.1842
1943.0667 | 701.0919
1944.0667 | 698.1309
1945.0667 | 694.5094
1946.0667 | 693.7626
1947.0667 | 695.1309
1948.0667 | 696.1269
1949.0667 | 696.7245
1950.0667 | 695.2055
1951.0667 | 690.6717
1952.0667 | 693.3417
1953.0667 | 692.0733
1954.0667 | 688.1705
1955.0667 | 690.675
1956.0667 | 691.3511
1957.0667 | 694.797
1958.0667 | 698.0408
1959.0667 | 699.8226
1960.0667 | 700.1372
1961.0667 | 699.3451
1962.0667 | 697.9629
1963.0667 | 699.6765
1964.0667 | 696.8769
1965.0667 | 694.547
1966.0667 | 695.6895
1967.0667 | 697.8243
1968.0667 | 701.0802
1969.0667 | 700.4765
1970.0667 | 700.7209
1971.0667 | 702.8098
1972.0667 | 706.1864
1973.0667 | 709.6481
1974.0667 | 711.6999
1975.0667 | 714.7754
1976.0667 | 710.0871
1977.0667 | 704.2028
1978.0667 | 703.8764
1979.0667 | 698.5149
1980.0667 | 701.5036
1981.0667 | 698.4613
1982.0667 | 696.635
1983.0667 | 695.8978
1984.0667 | 693.4602
1985.0667 | 687.6837
1986.0667 | 686.2323
1987.0667 | 684.3849
1988.0667 | 682.5888
1989.0667 | 680.6926
1990.0667 | 677.8087
1991.0667 | 677.5459
1992.0667 | 677.8245
1993.0667 | 678.1987
1994.0667 | 675.9053
1995.0667 | 678.2796
1996.0667 | 675.4901
1997.0667 | 673.9105
1998.0667 | 675.9623
1999.0667 | 677.7173
2000.0667 | 676.3803
2001.0667 | 675.8073
2002.0667 | 672.4688
2003.0667 | 667.3414
2004.0667 | 668.0035
2005.0667 | 669.9227
2006.0667 | 668.2811
2007.0667 | 670.0095
2008.0667 | 668.9274
2009.0667 | 663.9035
2010.0667 | 667.3388
2011.0667 | 675.6288
2012.0667 | 676.5311
2013.0667 | 679.7005
2014.0667 | 681.4196
2015.0667 | 683.6384
2016.0667 | 686.1338
2017.0667 | 687.9848
2018.0667 | 688.0277
2019.0667 | 686.0106
2020.0667 | 686.6277
2021.0667 | 685.9083
2022.0667 | 678.4475
2023.0667 | 676.9428
2024.0667 | 676.6487
2025.0667 | 677.7808
2026.0667 | 676.942
2027.0667 | 675.3746
2028.0667 | 676.1051
2029.0667 | 673.2597
2030.0667 | 673.7965
2031.0667 | 674.0842
2032.0667 | 674.2479
2033.0667 | 675.8212
2034.0667 | 676.1816
2035.0667 | 676.6552
2036.0667 | 676.6835
2037.0667 | 675.1044
2038.0667 | 672.5361
2039.0667 | 675.894
2040.0667 | 674.789
2041.0667 | 672.0743
2042.0667 | 670.068
2043.0667 | 671.6856
2044.0667 | 673.9152
2045.0667 | 669.6873
2046.0667 | 670.5484
2047.0667 | 674.0535
2048.0667 | 677.528
2049.0667 | 678.1833
2050.0667 | 678.2847
2051.0667 | 678.228
2052.0667 | 678.3966
2053.0667 | 676.1576
2054.0667 | 676.0845
2055.0667 | 676.3371
2056.0667 | 675.9771
2057.0667 | 670.5714
2058.0667 | 667.7249
2059.0667 | 667.8479
2060.0667 | 668.5739
2061.0667 | 670.381
2062.0667 | 672.364
2063.0667 | 677.5183
2064.0667 | 671.0021
2065.0667 | 676.2972
2066.0667 | 673.0392
2067.0667 | 669.8056
2068.0667 | 671.5123
2069.0667 | 667.4572
2070.0667 | 668.3891
2071.0667 | 664.8884
2072.0667 | 668.7795
2073.0667 | 671.365
2074.0667 | 675.5388
2075.0667 | 679.7658
2076.0667 | 679.4353
2077.0667 | 679.5449
2078.0667 | 682.2116
2079.0667 | 682.1765
2080.0667 | 680.9798
2081.0667 | 684.6533
2082.0667 | 686.0738
2083.0667 | 688.8391
2084.0667 | 690.7448
2085.0667 | 687.9422
2086.0667 | 683.2566
2087.0667 | 682.6069
2088.0667 | 679.7518
2089.0667 | 679.1942
2090.0823 | 676.863
2091.0667 | 676.4259
2092.0667 | 678.7042
2093.0667 | 680.1819
2094.0667 | 680.5535
2095.0667 | 683.9469
2096.0667 | 688.3897
2097.0667 | 690.0478
2098.0667 | 693.693
2099.0667 | 695.8019
2100.0667 | 696.1919
2101.0667 | 693.6317
2102.0667 | 686.5354
2103.0667 | 689.4869
2104.0667 | 694.0451
2105.0667 | 694.1464
2106.0667 | 692.1703
2107.0667 | 690.0692
2108.0667 | 692.6259
2109.0667 | 694.0835
2110.0667 | 690.34
2111.0667 | 685.0757
2112.0667 | 682.7176
2113.0667 | 680.4076
2114.0667 | 682.7703
2115.0667 | 684.843
2116.0667 | 687.8233
2117.0667 | 692.0915
2118.0667 | 693.2059
2119.0667 | 694.1885
2120.0667 | 694.9883
2121.0667 | 693.7217
2122.0667 | 684.6901
2123.0667 | 677.8652
2124.0667 | 673.9326
2125.0667 | 674.3597
2126.0667 | 673.9129
2127.0667 | 669.247
2128.0667 | 667.149
2129.0667 | 668.9091
2130.0667 | 671.522
2131.0667 | 669.5148
2132.0667 | 670.1668
2133.0667 | 672.1749
2134.0667 | 671.8305
2135.0667 | 674.9283
2136.0667 | 676.2029
2137.0667 | 676.7825
2138.0667 | 679.1699
2139.0667 | 681.2133
2140.0667 | 678.5144
2141.0667 | 675.1176
2142.0667 | 679.6457
2143.0667 | 677.198
2144.0667 | 671.5925
2145.0667 | 670.6276
2146.0667 | 670.7805
2147.0667 | 671.063
2148.0667 | 667.1912
2149.0667 | 662.9165
2150.0667 | 666.6905
2151.0667 | 660.636
2152.0667 | 659.7593
2153.0667 | 659.3775
2154.0667 | 661.6373
2155.0667 | 657.0656
2156.0667 | 659.4446
2157.0667 | 664.25
2158.0667 | 664.8006
2159.0667 | 662.7371
2160.0667 | 661.7541
2161.0667 | 661.0524
2162.0667 | 658.4803
2163.0667 | 653.8871
2164.0667 | 649.4776
2165.0667 | 652.5148
2166.0667 | 651.3036
2167.0667 | 650.3264
2168.0667 | 652.2453
2169.0667 | 659.5695
2170.0667 | 657.7206
2171.0667 | 654.5215
2172.0667 | 658.2286
2173.0667 | 658.969
2174.0667 | 661.6548
2175.0667 | 665.1466
2176.0667 | 672.1072
2177.0667 | 679.3962
2178.0667 | 688.3246
2179.0667 | 691.2872
2180.0667 | 688.7054
2181.0667 | 687.7149
2182.0667 | 682.2908
2183.0667 | 678.6813
2184.0667 | 672.6707
2185.0667 | 672.832
2186.0667 | 676.1733
2187.0667 | 679.9701
2188.0667 | 676.4889
2189.0667 | 679.9444
2190.0667 | 681.6122
2191.0667 | 687.2685
2192.0667 | 692.5783
2193.0667 | 695.0494
2194.0667 | 696.9264
2195.0667 | 694.6603
2196.0667 | 693.0395
2197.0667 | 692.5222
2198.0667 | 693.0785
2199.0667 | 691.1218
2200.0667 | 690.1368
2201.0667 | 686.8158
2202.0667 | 683.1794
2203.0667 | 686.7361
2204.0667 | 691.6036
2205.0667 | 689.0443
2206.0667 | 684.98
2207.0667 | 678.4551
2208.0667 | 677.3356
2209.0667 | 675.4123
2210.0667 | 674.5381
2211.0667 | 677.9693
2212.0667 | 677.353
2213.0667 | 678.4177
2214.0667 | 680.3659
2215.0667 | 680.6765
2216.0667 | 683.9724
2217.0667 | 684.7285
2218.0667 | 682.5665
2219.0667 | 678.9337
2220.0823 | 673.9925
2221.0667 | 676.457
2222.0667 | 676.6033
2223.0667 | 675.0211
2224.0667 | 677.917
2225.0667 | 675.3294
2226.0667 | 674.6263
2227.0667 | 672.581
2228.0667 | 671.1914
2229.0667 | 668.2643
2230.0667 | 663.8296
2231.0667 | 660.358
2232.0667 | 658.1808
2233.0667 | 654.9382
2234.0667 | 654.3844
2235.0667 | 651.1068
2236.0667 | 651.1395
2237.0667 | 645.1441
2238.0667 | 647.5157
2239.0667 | 651.3381
2240.0667 | 655.9328
2241.0667 | 659.8526
2242.0667 | 661.7322
2243.0667 | 662.483
2244.0667 | 663.3756
2245.0667 | 663.0897
2246.0667 | 663.4406
2247.0667 | 663.9632
2248.0823 | 661.9492
2249.0667 | 658.4713
2250.0667 | 657.5622
2251.0667 | 660.3949
2252.0667 | 657.4785
2253.0667 | 657.0834
2254.0667 | 657.2449
2255.0667 | 661.8494
2256.0667 | 660.3961
2257.0667 | 658.5855
2258.0667 | 659.486
2259.0667 | 662.506
2260.0667 | 671.883
2261.0667 | 677.877
2262.0667 | 678.3556
2263.0667 | 676.3628
2264.0667 | 672.5932
2265.0667 | 672.0943
2266.0667 | 668.389
2267.0667 | 667.7632
2268.0667 | 666.5229
2269.0667 | 664.8392
2270.0667 | 667.018
2271.0667 | 668.8282
2272.0667 | 671.6463
2273.0667 | 666.9882
2274.0667 | 660.7295
2275.0667 | 655.8044
2276.0667 | 657.8616
2277.0667 | 657.7074
2278.0667 | 645.7966
2279.0667 | 646.8855
2280.0667 | 653.1049
2281.0667 | 654.4225
2282.0667 | 655.0141
2283.0667 | 658.2373
2284.0667 | 656.5428
2285.0667 | 661.6355
2286.0667 | 669.0827
2287.0667 | 673.5605
2288.0667 | 677.0092
2289.0667 | 677.1916
2290.0667 | 678.3902
2291.0667 | 677.276
2292.0667 | 678.5181
2293.0667 | 681.6295
2294.0667 | 680.6808
2295.0667 | 685.2846
2296.0667 | 683.6131
2297.0667 | 682.8176
2298.0667 | 679.4441
2299.0667 | 675.8719
2300.0667 | 671.8176
2301.0667 | 670.6647
2302.0667 | 671.6529
2303.0667 | 671.6949
2304.0667 | 670.0075
2305.0667 | 667.7123
2306.0667 | 667.3404
2307.0667 | 666.8891
2308.0667 | 666.4991
2309.0667 | 668.3528
2310.0667 | 671.9648
2311.0667 | 671.5222
2312.0667 | 675.7715
2313.0667 | 671.0017
2314.0667 | 668.5285
2315.0667 | 675.9006
2316.0667 | 671.374
2317.0667 | 670.1305
2318.0667 | 671.2364
2319.0667 | 672.6066
2320.0667 | 672.0802
2321.0667 | 674.2713
2322.0667 | 681.6361
2323.0667 | 679.5636
2324.0667 | 678.1052
2325.0667 | 683.5507
2326.0667 | 689.1982
2327.0667 | 693.1449
2328.0667 | 690.7246
2329.0667 | 689.4469
2330.0667 | 693.3023
2331.0667 | 699.1529
2332.0667 | 700.8877
2333.0667 | 699.5039
2334.0667 | 700.52
2335.0667 | 699.9891
2336.0667 | 697.462
2337.0667 | 700.617
2338.0667 | 694.7543
2339.0667 | 697.0751
2340.0667 | 699.2448
2341.0667 | 699.5595
2342.0667 | 700.2975
2343.0667 | 697.8611
2344.0667 | 697.9457
2345.0667 | 699.9307
2346.0667 | 701.441
2347.0667 | 706.757
2348.0667 | 714.4116
2349.0667 | 711.9033
2350.0667 | 703.869
2351.0667 | 702.9528
2352.0667 | 697.7866
2353.0667 | 692.356
2354.0667 | 690.1111
2355.0667 | 694.305
2356.0667 | 692.8441
2357.0667 | 692.0806
2358.0667 | 686.1081
2359.0667 | 685.1991
2360.0667 | 681.6328
2361.0667 | 680.6445
2362.0667 | 679.4943
2363.0667 | 675.7738
2364.0667 | 673.2296
2365.0667 | 674.136
2366.0667 | 671.4569
2367.0667 | 674.12
2368.0667 | 670.783
2369.0667 | 672.3131
2370.0667 | 670.7076
2371.0667 | 668.8648
2372.0667 | 669.492
2373.0667 | 671.9132
2374.0667 | 669.5696
2375.0667 | 670.7586
2376.0667 | 676.8177
2377.0667 | 678.0627
2378.0667 | 676.2847
2379.0667 | 682.1765
2380.0667 | 677.5386
2381.0667 | 678.9472
2382.0667 | 683.3439
2383.0667 | 688.3615
2384.0667 | 690.6749
2385.0667 | 697.1124
2386.0667 | 692.2268
2387.0667 | 687.8927
2388.0667 | 686.1396
2389.0667 | 683.3296
2390.0667 | 686.2809
2391.0667 | 684.4177
2392.0667 | 682.2982
2393.0667 | 682.744
2394.0667 | 676.2932
2395.0667 | 672.6714
2396.0667 | 672.9381
2397.0667 | 673.0351
2398.0667 | 672.6103
2399.0667 | 680.6598
2400.0667 | 687.1834
2401.0667 | 684.9464
2402.0667 | 682.7399
2403.0667 | 683.9921
2404.0667 | 683.35
2405.0667 | 681.5393
2406.0667 | 681.3827
2407.0667 | 687.3334
2408.0667 | 697.0627
2409.0667 | 701.7752
2410.0667 | 701.7819
2411.0667 | 699.0459
2412.0667 | 697.4389
2413.0667 | 695.1768
2414.0667 | 694.7998
2415.0667 | 688.6767
2416.0667 | 685.3447
2417.0667 | 684.2899
2418.0667 | 686.6863
2419.0667 | 687.5767
2420.0667 | 689.9117
2421.0667 | 688.3432
2422.0667 | 687.2593
2423.0667 | 681.5357
2424.0667 | 674.4765
2425.0667 | 673.4678
2426.0667 | 670.9674
2427.0667 | 667.3195
2428.0667 | 668.4001
2429.0667 | 668.2378
2430.0667 | 664.8598
2431.0667 | 665.9336
2432.0667 | 661.2815
2433.0667 | 656.4371
2434.0667 | 655.9797
2435.0823 | 654.2202
2436.0667 | 646.5986
2437.0667 | 647.0255
2438.0667 | 646.9852
2439.0667 | 649.6968
2440.0667 | 656.3717
2441.0667 | 662.5321
2442.0667 | 666.3287
2443.0667 | 670.3804
2444.0667 | 668.6047
2445.0667 | 672.8944
2446.0823 | 669.7856
2447.0667 | 665.8953
2448.0667 | 667.6479
2449.0667 | 667.5524
2450.0667 | 669.8334
2451.0667 | 667.8267
2452.0667 | 664.6732
2453.0667 | 661.3482
2454.0667 | 654.9928
2455.0667 | 653.7066
2456.0667 | 654.3909
2457.0667 | 655.7975
2458.0667 | 650.6032
2459.0667 | 646.0676
2460.0667 | 646.5519
2461.0667 | 650.3244
2462.0667 | 651.7674
2463.0667 | 653.0661
2464.0667 | 651.7849
2465.0667 | 654.1511
2466.0667 | 659.2952
2467.0667 | 660.9793
2468.0667 | 665.0678
2469.0667 | 665.6594
2470.0667 | 674.7575
2471.0667 | 678.768
2472.0667 | 677.3916
2473.0667 | 682.3046
2474.0667 | 687.5986
2475.0667 | 689.7372
2476.0823 | 689.9866
2477.0667 | 687.4271
2478.0667 | 688.5343
2479.0667 | 691.0074
2480.0667 | 692.9917
2481.0667 | 694.9122
2482.0667 | 689.2182
2483.0667 | 680.9613
2484.0667 | 683.4514
2485.0667 | 686.3474
2486.0667 | 688.3843
2487.0667 | 687.3906
2488.0667 | 682.9716
2489.0667 | 677.9186
2490.0667 | 673.7284
2491.0667 | 667.2044
2492.0667 | 663.4683
2493.0667 | 668.3049
2494.0667 | 669.3961
2495.0667 | 667.8379
2496.0667 | 668.356
2497.0667 | 673.642
2498.0667 | 673.844
2499.0667 | 671.9192
2500.0667 | 671.1987
2501.0667 | 671.4499
2502.0667 | 678.8855
2503.0667 | 675.4873
2504.0667 | 666.3636
2505.0667 | 665.7731
2506.0667 | 668.0837
2507.0667 | 669.5184
2508.0667 | 671.3248
2509.0667 | 673.6258
2510.0667 | 676.3677
2511.0823 | 684.3796
2512.0667 | 677.442
2513.0667 | 675.1793
2514.0667 | 676.0596
2515.0667 | 669.5567
2516.0667 | 676.0002
2517.0667 | 682.4773
2518.0667 | 685.3
2519.0823 | 685.3934
2520.0667 | 682.5851
2521.0667 | 677.5606
2522.0667 | 676.0066
2523.0667 | 673.4478
2524.0667 | 671.9916
2525.0667 | 677.6603
2526.0667 | 677.745
2527.0667 | 670.0997
2528.0667 | 669.8716
2529.0667 | 673.6699
2530.0667 | 676.6259
2531.0667 | 671.5604
2532.0667 | 668.5057
2533.0667 | 672.203
2534.0667 | 677.7737
2535.0667 | 677.9523
2536.0823 | 673.3206
2537.0667 | 670.2533
2538.0667 | 670.9035
2539.0667 | 668.5345
2540.0667 | 668.6391
2541.0667 | 665.7184
2542.0667 | 659.7046
2543.0667 | 657.4717
2544.0667 | 654.7135
2545.0667 | 653.2071
2546.0667 | 652.1902
2547.0667 | 654.195
2548.0823 | 657.3572
2549.0667 | 662.0432
2550.0667 | 662.9725
2551.0667 | 663.8986
2552.0667 | 661.7656
2553.0667 | 663.9021
2554.0667 | 663.4855
2555.0667 | 666.3146
2556.0667 | 659.203
2557.0667 | 652.9291
2558.0667 | 644.5127
2559.0667 | 650.9887
2560.0667 | 658.2897
2561.0667 | 668.1969
2562.0667 | 673.1823
2563.0667 | 674.5416
2564.0667 | 678.6023
2565.0667 | 679.5191
2566.0823 | 682.6321
2567.0667 | 688.4261
2568.0667 | 685.8362
2569.0667 | 683.4018
2570.0667 | 682.9778
2571.0667 | 681.2219
2572.0667 | 675.0476
2573.0667 | 673.6489
2574.0667 | 674.4174
2575.0667 | 676.8488
2576.0667 | 678.977
2577.0667 | 675.5163
2578.0667 | 673.6422
2579.0667 | 668.7567
2580.0667 | 663.2248
2581.0667 | 660.3589
2582.0667 | 660.286
2583.0667 | 658.7703
2584.0667 | 664.5143
2585.0667 | 661.3
2586.0667 | 660.804
2587.0667 | 656.8325
2588.0667 | 654.7538
2589.0667 | 655.6682
2590.0667 | 651.1542
2591.0667 | 647.9404
2592.0667 | 648.8826
2593.0667 | 655.9113
2594.0667 | 658.2221
2595.0667 | 660.2595
2596.0823 | 666.0857
2597.0667 | 665.4453
2598.0667 | 657.7949
2599.0667 | 658.6673
2600.0667 | 657.4978
2601.0667 | 660.6703
2602.0667 | 660.1698
2603.0667 | 659.2655
2604.0667 | 660.8141
2605.0667 | 655.9048
2606.0667 | 657.4739
2607.0667 | 655.6155
2608.0667 | 652.9238
2609.0667 | 645.3323
2610.0667 | 646.9323
2611.0667 | 648.947
2612.0667 | 657.6086
2613.0667 | 657.8185
2614.0667 | 650.6042
2615.0667 | 644.7995
2616.0667 | 646.8531
2617.0667 | 645.6077
2618.0667 | 649.6907
2619.0667 | 646.8596
2620.0667 | 647.4374
2621.0667 | 657.7904
2622.0667 | 661.9829
2623.0667 | 660.767
2624.0667 | 659.4237
2625.0667 | 660.4097
2626.0823 | 660.1307
2627.0667 | 662.6926
2628.0667 | 666.8319
2629.0667 | 667.2051
2630.0667 | 669.4199
2631.0667 | 671.497
2632.0667 | 672.3558
2633.0667 | 670.0188
2634.0667 | 669.12
2635.0667 | 669.3187
2636.0667 | 667.0451
2637.0667 | 667.5559
2638.0667 | 666.9622
2639.0667 | 663.7525
2640.0667 | 666.4831
2641.0667 | 669.0106
2642.0667 | 667.4487
2643.0667 | 665.9884
2644.0667 | 668.9944
2645.0667 | 672.1417
2646.0667 | 673.0544
2647.0667 | 669.7209
2648.0667 | 674.0888
2649.0667 | 673.5563
2650.0667 | 676.0788
2651.0667 | 682.2265
2652.0667 | 685.4785
2653.0667 | 685.5055
2654.0667 | 686.0687
2655.0667 | 685.8178
2656.0823 | 686.0359
2657.0667 | 687.4669
2658.0667 | 691.7351
2659.0667 | 689.88
2660.0667 | 679.3355
2661.0667 | 677.5794
2662.0667 | 669.8227
2663.0667 | 665.4071
2664.0667 | 660.0557
2665.0667 | 656.3991
2666.0667 | 652.6628
2667.0667 | 653.1952
2668.0667 | 651.8994
2669.0667 | 654.3108
2670.0823 | 652.8882
2671.0667 | 647.175
2672.0667 | 646.4672
2673.0667 | 645.4195
2674.0667 | 646.9887
2675.0667 | 649.9913
2676.0667 | 653.9803
2677.0667 | 654.8693
2678.0667 | 655.5539
2679.0667 | 659.044
2680.0667 | 662.7017
2681.0667 | 660.5706
2682.0667 | 664.6736
2683.0667 | 673.0431
2684.0667 | 677.236
2685.0667 | 680.0661
2686.0667 | 682.0064
2687.0667 | 683.8484
2688.0667 | 685.5747
2689.0667 | 690.784
2690.0667 | 696.0144
2691.0667 | 701.3145
2692.0667 | 701.5914
2693.0667 | 704.6426
2694.0667 | 711.5291
2695.0667 | 706.0009
2696.0667 | 708.6062
2697.0667 | 709.7656
2698.0667 | 698.2531
2699.0667 | 696.7051
2700.0667 | 691.6382
2701.0667 | 686.7596
2702.0667 | 686.9845
2703.0667 | 687.6568
2704.0667 | 689.4601
2705.0667 | 689.0776
2706.0667 | 693.2662
2707.0667 | 696.5817
2708.0667 | 699.3152
2709.0667 | 698.8931
2710.0667 | 696.8897
2711.0667 | 699.8472
2712.0667 | 701.8989
2713.0667 | 699.0586
2714.0667 | 692.0604
2715.0667 | 689.9272
2716.0667 | 683.4357
2717.0667 | 684.8373
2718.0667 | 684.3036
2719.0667 | 688.2736
2720.0667 | 680.3076
2721.0667 | 675.3246
2722.0667 | 674.4377
2723.0667 | 676.2929
2724.0667 | 683.0099
2725.0667 | 687.8558
2726.0667 | 690.0799
2727.0667 | 686.4588
2728.0823 | 684.2302
2729.0667 | 684.2319
2730.0667 | 682.9109
2731.0667 | 686.2262
2732.0667 | 690.2483
2733.0667 | 688.3292
2734.0667 | 690.9527
2735.0667 | 682.9202
2736.0667 | 675.4325
2737.0667 | 670.513
2738.0667 | 669.659
2739.0667 | 670.6028
2740.0667 | 670.2697
2741.0667 | 675.151
2742.0667 | 675.5706
2743.0667 | 676.0923
2744.0667 | 671.5092
2745.0667 | 666.3345
2746.0667 | 662.9875
2747.0667 | 659.5723
2748.0667 | 655.3878
2749.0667 | 648.7382
2750.0667 | 644.9144
2751.0667 | 648.7561
2752.0667 | 644.3536
2753.0667 | 644.1525
2754.0667 | 640.4273
2755.0667 | 645.1095
2756.0667 | 641.81
2757.0667 | 646.5074
2758.0667 | 648.508
2759.0667 | 650.4222
2760.0667 | 653.1668
2761.0667 | 648.0936
2762.0667 | 646.309
2763.0667 | 646.9844
2764.0667 | 648.821
2765.0667 | 654.8596
2766.0667 | 660.4701
2767.0667 | 662.5696
2768.0667 | 660.3412
2769.0667 | 656.0744
2770.0667 | 656.8846
2771.0667 | 651.4645
2772.0667 | 649.6409
2773.0667 | 654.5897
2774.0667 | 654.3982
2775.0667 | 652.5136
2776.0667 | 654.8927
2777.0667 | 657.8805
2778.0667 | 660.9646
2779.0667 | 663.4935
2780.0667 | 664.6472
2781.0667 | 660.7427
2782.0667 | 663.1761
2783.0667 | 664.7715
2784.0667 | 665.1124
2785.0667 | 660.417
2786.0667 | 653.4201
2787.0667 | 653.0347
2788.0667 | 653.3069
2789.0667 | 648.6153
2790.0667 | 649.995
2791.0667 | 650.4216
2792.0667 | 646.6538
2793.0667 | 642.9886
2794.0667 | 637.5558
2795.0667 | 641.2371
2796.0667 | 649.5548
2797.0667 | 643.8489
2798.0667 | 641.34
2799.0667 | 636.6384
2800.0667 | 637.3396
2801.0667 | 628.7312
2802.0667 | 625.4984
2803.0667 | 625.5021
2804.0667 | 620.9934
2805.0667 | 620.9852
2806.0667 | 625.2264
2807.0667 | 632.3156
2808.0667 | 632.9218
2809.0667 | 641.4912
2810.0667 | 647.8835
2811.0667 | 651.8357
2812.0667 | 651.7081
2813.0667 | 646.0212
2814.0667 | 647.5318
2815.0667 | 650.8754
2816.0667 | 652.6316
2817.0667 | 653.6469
2818.0667 | 657.5025
2819.0667 | 657.4326
2820.0667 | 663.5962
2821.0667 | 667.5133
2822.0667 | 671.1646
2823.0667 | 667.9824
2824.0667 | 668.3608
2825.0667 | 673.5873
2826.0667 | 672.3691
2827.0667 | 674.7652
2828.0667 | 669.5957
2829.0667 | 659.9004
2830.0667 | 656.8627
2831.0667 | 655.5018
2832.0667 | 663.6655
2833.0667 | 658.6627
2834.0667 | 660.1406
2835.0667 | 658.8759
2836.0667 | 659.037
2837.0667 | 652.454
2838.0667 | 653.8103
2839.0667 | 655.2377
2840.0667 | 655.3344
2841.0667 | 654.5574
2842.0667 | 655.9162
2843.0667 | 657.6256
2844.0667 | 650.7376
2845.0667 | 645.9976
2846.0667 | 641.227
2847.0667 | 640.3563
2848.0823 | 643.0427
2849.0667 | 642.6109
2850.0667 | 639.1859
2851.0667 | 637.4523
2852.0667 | 637.3606
2853.0667 | 636.9842
2854.0667 | 636.7791
2855.0667 | 633.4378
2856.0667 | 636.2228
2857.0667 | 638.0275
2858.0667 | 636.8059
2859.0667 | 635.7556
2860.0667 | 628.0842
2861.0667 | 625.4807
2862.0667 | 625.233
2863.0667 | 624.331
2864.0667 | 628.8565
2865.0667 | 632.6079
2866.0667 | 635.3708
2867.0667 | 637.8151
2868.0667 | 635.3457
2869.0667 | 635.1462
2870.0667 | 639.1085
2871.0667 | 636.6709
2872.0667 | 632.4589
2873.0667 | 634.6387
2874.0667 | 634.6397
2875.0667 | 630.0955
2876.0667 | 626.409
2877.0667 | 623.5617
2878.0667 | 621.5042
2879.0667 | 621.1613
2880.0667 | 626.0538
2881.0667 | 624.2267
2882.0667 | 623.5809
2883.0667 | 628.4157
2884.0667 | 631.479
2885.0667 | 632.9946
2886.0667 | 631.6809
2887.0667 | 637.5243
2888.0667 | 639.899
2889.0667 | 639.3336
2890.0667 | 638.1877
2891.0667 | 637.8073
2892.0667 | 643.7471
2893.0667 | 646.5792
2894.0667 | 650.8766
2895.0667 | 656.8377
2896.0667 | 654.8067
2897.0667 | 649.0126
2898.0667 | 646.7852
2899.0667 | 654.377
2900.0667 | 658.6596
2901.0667 | 657.0491
2902.0667 | 653.6412
2903.0667 | 653.0001
2904.0667 | 650.4261
2905.0667 | 651.6624
2906.0667 | 655.1022
2907.0667 | 661.8321
2908.0667 | 663.986
2909.0667 | 667.8554
2910.0667 | 663.5755
2911.0667 | 660.0513
2912.0667 | 664.4184
2913.0667 | 661.5419
2914.0667 | 657.1935
2915.0667 | 649.3811
2916.0667 | 649.1607
2917.0667 | 655.3703
2918.0667 | 662.5774
2919.0667 | 664.9512
2920.0667 | 662.7648
2921.0667 | 667.8835
2922.0667 | 674.475
2923.0667 | 676.7494
2924.0667 | 674.5793
2925.0667 | 675.1576
2926.0667 | 674.9845
2927.0667 | 679.2894
2928.0667 | 683.3105
2929.0667 | 684.6876
2930.0667 | 680.8535
2931.0667 | 678.2544
2932.0667 | 674.6905
2933.0667 | 670.8942
2934.0667 | 668.8043
2935.0667 | 665.664
2936.0667 | 669.3919
2937.0667 | 671.5102
2938.0667 | 671.9132
2939.0667 | 665.9715
2940.0667 | 667.3757
2941.0667 | 676.5171
2942.0667 | 679.3169
2943.0667 | 678.0846
2944.0667 | 676.1075
2945.0667 | 676.736
2946.0667 | 674.6957
2947.0667 | 675.0504
2948.0667 | 673.1766
2949.0667 | 668.5018
2950.0667 | 664.9649
2951.0667 | 658.537
2952.0667 | 660.0879
2953.0667 | 664.3603
2954.0667 | 665.6317
2955.0667 | 660.3123
2956.0667 | 655.7638
2957.0667 | 656.0831
2958.0667 | 659.1017
2959.0667 | 651.099
2960.0667 | 650.9765
2961.0667 | 652.4024
2962.0667 | 655.9635
2963.0667 | 655.8049
2964.0667 | 655.2618
2965.0667 | 655.7009
2966.0667 | 655.2295
2967.0667 | 651.7751
2968.0667 | 646.9284
2969.0667 | 649.1042
2970.0667 | 646.0143
2971.0667 | 643.4384
2972.0667 | 642.1402
2973.0667 | 641.0487
2974.0667 | 639.4566
2975.0667 | 638.3595
2976.0667 | 638.5492
2977.0667 | 644.7093
2978.0667 | 649.2807
2979.0667 | 654.4103
2980.0667 | 655.0111
2981.0667 | 657.5236
2982.0667 | 662.553
2983.0667 | 666.9696
2984.0667 | 667.1704
2985.0667 | 666.1664
2986.0667 | 665.5555
2987.0667 | 657.2535
2988.0667 | 642.8005
2989.0667 | 631.1185
2990.0667 | 632.1606
2991.0667 | 631.2467
2992.0667 | 628.8841
2993.0667 | 624.4777
2994.0667 | 616.6353
2995.0667 | 610.4478
2996.0667 | 604.0288
2997.0667 | 597.6849
2998.0667 | 598.1487
2999.0667 | 604.4907
3000.0667 | 603.9751
3001.0667 | 608.5418
3002.0667 | 616.693
3003.0667 | 622.3897
3004.0667 | 632.8877
3005.0667 | 644.5787
3006.0667 | 653.4174
3007.0667 | 657.4242
3008.0667 | 653.6644
3009.0667 | 646.2006
3010.0667 | 638.9358
3011.0667 | 644.9631
3012.0667 | 643.8692
3013.0667 | 636.0644
3014.0667 | 635.6797
3015.0667 | 632.6936
3016.0667 | 633.2767
3017.0667 | 630.4722
3018.0667 | 627.8872
3019.0667 | 627.3318
3020.0667 | 632.0993
3021.0667 | 641.1189
3022.0667 | 645.4327
3023.0667 | 651.6058
3024.0667 | 651.6887
3025.0667 | 643.0826
3026.0667 | 645.4275
3027.0667 | 645.8258
3028.0667 | 643.8742
3029.0667 | 643.3833
3030.0667 | 644.6261
3031.0667 | 645.5084
3032.0667 | 650.1655
3033.0667 | 654.8576
3034.0667 | 662.1403
3035.0667 | 667.0499
3036.0667 | 670.9249
3037.0667 | 674.1026
3038.0667 | 678.7794
3039.0667 | 685.8019
3040.0667 | 679.8562
3041.0667 | 673.5208
3042.0667 | 671.8654
3043.0667 | 669.9372
3044.0667 | 670.8906
3045.0667 | 672.516
3046.0667 | 678.2889
3047.0667 | 679.8981
3048.0667 | 675.7813
3049.0667 | 674.2527
3050.0667 | 672.4621
3051.0667 | 672.7183
3052.0667 | 673.1725
3053.0667 | 672.5357
3054.0667 | 670.5169
3055.0667 | 670.8114
3056.0667 | 673.9958
3057.0667 | 673.6601
3058.0667 | 675.0026
3059.0667 | 678.0653
3060.0667 | 678.6268
3061.0667 | 674.6742
3062.0667 | 668.9234
3063.0667 | 666.4117
3064.0667 | 664.7653
3065.0667 | 660.3195
3066.0823 | 653.156
3067.0823 | 650.618
3068.0667 | 643.0307
3069.0667 | 639.5204
3070.0667 | 643.1156
3071.0667 | 636.1143
3072.0667 | 626.0704
3073.0667 | 625.4057
3074.0667 | 622.94
3075.0667 | 619.2891
3076.0667 | 620.9505
3077.0667 | 626.5069
3078.0667 | 629.8063
3079.0667 | 632.1775
3080.0667 | 630.2838
3081.0667 | 635.6836
3082.0667 | 641.5531
3083.0667 | 646.8691
3084.0667 | 648.0894
3085.0667 | 647.8275
3086.0667 | 648.9337
3087.0667 | 647.9841
3088.0667 | 644.5531
3089.0667 | 643.0722
3090.0667 | 644.4531
3091.0667 | 655.4364
3092.0667 | 663.5886
3093.0667 | 671.1375
3094.0667 | 677.695
3095.0667 | 675.2435
3096.0667 | 670.056
3097.0667 | 667.115
3098.0667 | 667.4638
3099.0667 | 668.614
3100.0667 | 674.7803
3101.0667 | 679.5682
3102.0667 | 680.0736
3103.0667 | 682.4951
3104.0667 | 680.1737
3105.0667 | 678.5487
3106.0667 | 682.2745
3107.0667 | 682.3965
3108.0667 | 680.0753
3109.0667 | 684.732
3110.0667 | 683.2067
3111.0667 | 679.687
3112.0667 | 683.4475
3113.0667 | 687.8972
3114.0667 | 689.5392
3115.0667 | 692.9019
3116.0667 | 697.0718
3117.0667 | 695.1006
3118.0667 | 691.1634
3119.0667 | 689.5181
3120.0667 | 684.7336
3121.0667 | 684.5135
3122.0667 | 685.3241
3123.0667 | 683.7532
3124.0667 | 674.6106
3125.0667 | 662.3232
3126.0667 | 650.9081
3127.0667 | 644.876
3128.0667 | 643.146
3129.0667 | 645.812
3130.0667 | 648.9996
3131.0667 | 652.5941
3132.0667 | 657.857
3133.0667 | 658.1246
3134.0667 | 654.0508
3135.0667 | 644.8071
3136.0667 | 640.4614
3137.0667 | 637.6071
3138.0667 | 642.6741
3139.0667 | 646.5382
3140.0667 | 650.6503
3141.0667 | 652.3049
3142.0667 | 655.3119
3143.0667 | 654.2436
3144.0667 | 656.8297
3145.0667 | 658.989
3146.0667 | 663.8751
3147.0667 | 660.8407
3148.0667 | 655.5916
3149.0667 | 658.3774
3150.0667 | 662.6744
3151.0667 | 657.669
3152.0667 | 656.1644
3153.0667 | 660.2184
3154.0667 | 657.117
3155.0667 | 659.7578
3156.0667 | 656.1493
3157.0667 | 654.2582
3158.0667 | 663.0699
3159.0667 | 667.5153
3160.0667 | 666.7552
3161.0667 | 675.8382
3162.0667 | 679.1239
3163.0667 | 682.1767
3164.0667 | 686.7818
3165.0667 | 690.638
3166.0667 | 685.702
3167.0667 | 688.72
3168.0667 | 690.7984
3169.0667 | 689.5006
3170.0667 | 693.4883
3171.0667 | 691.1979
3172.0667 | 698.5338
3173.0667 | 695.4976
3174.0667 | 695.9835
3175.0667 | 697.1006
3176.0667 | 703.0075
3177.0667 | 714.4862
3178.0667 | 717.6364
3179.0667 | 715.8054
3180.0667 | 710.8478
3181.0667 | 707.557
3182.0667 | 705.4266
3183.0667 | 699.1095
3184.0667 | 693.9942
3185.0667 | 692.0519
3186.0667 | 700.5624
3187.0667 | 706.6517
3188.0667 | 714.063
3189.0667 | 716.2072
3190.0667 | 720.0851
3191.0667 | 720.3284
3192.0667 | 725.1704
3193.0667 | 728.6303
3194.0667 | 725.3892
3195.0667 | 722.9274
3196.0667 | 713.6354
3197.0667 | 709.0713
3198.0667 | 707.7137
3199.0667 | 698.4925
3200.0667 | 702.0966
3201.0667 | 706.0658
3202.0667 | 710.9063
3203.0667 | 715.2531
3204.0667 | 717.9838
3205.0667 | 716.7583
3206.0667 | 711.6227
3207.0667 | 708.2097
3208.0667 | 703.4706
3209.0667 | 697.2033
3210.0667 | 694.3221
3211.0667 | 690.1782
3212.0667 | 684.0385
3213.0667 | 681.757
3214.0667 | 678.0876
3215.0667 | 678.6747
3216.0667 | 675.9858
3217.0667 | 673.5895
3218.0667 | 667.6555
3219.0667 | 659.7419
3220.0667 | 655.5598
3221.0667 | 643.3258
3222.0667 | 641.6307
3223.0667 | 644.7909
3224.0667 | 652.6365
3225.0667 | 657.237
3226.0667 | 658.0108
3227.0667 | 654.5491
3228.0667 | 660.4803
3229.0667 | 657.1617
3230.0667 | 655.6469
3231.0667 | 652.796
3232.0667 | 655.1452
3233.0667 | 647.7086
3234.0667 | 653.7276
3235.0667 | 660.554
3236.0667 | 669.2338
3237.0667 | 675.833
3238.0667 | 674.7924
3239.0667 | 673.0249
3240.0667 | 668.1803
3241.0667 | 673.3352
3242.0667 | 675.8993
3243.0667 | 691.1921
3244.0667 | 711.2321
3245.0667 | 718.667
3246.0667 | 718.425
3247.0667 | 717.5752
3248.0667 | 719.6201
3249.0667 | 724.5496
3250.0667 | 732.2135
3251.0667 | 730.9647
3252.0667 | 728.085
3253.0667 | 736.9308
3254.0667 | 736.6297
3255.0667 | 734.302
3256.0667 | 726.3752
3257.0667 | 721.4978
3258.0667 | 723.009
3259.0667 | 723.8487
3260.0667 | 720.5385
3261.0667 | 719.875
3262.0667 | 722.3573
3263.0667 | 725.6291
3264.0667 | 739.9317
3265.0667 | 730.3732
3266.0667 | 726.458
3267.0667 | 733.5286
3268.0667 | 727.5295
3269.0667 | 722.6784
3270.0667 | 721.1378
3271.0667 | 719.5933
3272.0667 | 719.8598
3273.0667 | 712.0472
3274.0667 | 703.3869
3275.0667 | 695.7544
3276.0667 | 687.7221
3277.0667 | 698.2834
3278.0667 | 712.1477
3279.0667 | 713.1173
3280.0667 | 713.3241
3281.0667 | 710.7298
3282.0667 | 711.2969
3283.0667 | 709.7786
3284.0667 | 707.6934
3285.0667 | 705.7031
3286.0667 | 703.8412
3287.0667 | 703.8807
3288.0667 | 700.1607
3289.0667 | 710.3327
3290.0667 | 710.8126
3291.0667 | 717.3283
3292.0667 | 715.3623
3293.0667 | 715.7749
3294.0667 | 718.2384
3295.0667 | 714.7437
3296.0667 | 708.9573
3297.0667 | 704.6709
3298.0667 | 700.7335
3299.0667 | 699.9296
3300.0667 | 697.6483
3301.0667 | 695.9616
3302.0667 | 695.6758
3303.0667 | 698.5773
3304.0667 | 699.1247
3305.0667 | 696.141
3306.0667 | 694.9315
3307.0667 | 695.9394
3308.0667 | 701.9685
3309.0667 | 700.965
3310.0667 | 699.3795
3311.0667 | 695.4256
3312.0667 | 691.1409
3313.0667 | 690.0802
3314.0667 | 683.5043
3315.0667 | 680.8116
3316.0667 | 678.4409
3317.0667 | 676.6376
3318.0667 | 673.8308
3319.0667 | 670.4161
3320.0667 | 667.6104
3321.0667 | 667.6234
3322.0667 | 671.3051
3323.0667 | 680.2294
3324.0667 | 693.798
3325.0667 | 701.4388
3326.0667 | 701.9222
3327.0667 | 698.6412
3328.0667 | 697.0279
3329.0667 | 695.2291
3330.0667 | 696.4684
3331.0667 | 698.794
3332.0667 | 691.929
3333.0667 | 691.0781
3334.0667 | 687.045
3335.0667 | 684.9787
3336.0667 | 685.7084
3337.0667 | 690.1096
3338.0667 | 696.2412
3339.0667 | 697.4251
3340.0667 | 712.6254
3341.0667 | 713.9193
3342.0667 | 716.4962
3343.0667 | 713.4278
3344.0667 | 716.7892
3345.0667 | 723.9741
3346.0667 | 718.2911
3347.0667 | 710.1512
3348.0667 | 705.7362
3349.0667 | 700.4035
3350.0667 | 700.6401
3351.0667 | 704.882
3352.0667 | 701.7319
3353.0667 | 704.9498
3354.0667 | 704.7598
3355.0667 | 705.0455
3356.0667 | 703.1829
3357.0667 | 703.1273
3358.0667 | 696.1339
3359.0667 | 688.9561
3360.0667 | 691.0168
3361.0667 | 695.7885
3362.0667 | 697.6628
3363.0667 | 702.675
3364.0667 | 709.7508
3365.0667 | 711.0744
3366.0667 | 708.1682
3367.0667 | 705.1313
3368.0667 | 702.7132
3369.0667 | 697.6445
3370.0667 | 698.5437