## Test Conditions
DESIREE-FIRE Intermediate Scale Test 3 - Circuit Data Only
Test Date: | 2010-02-17
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 13:27
Fire Time | 14:05
Offset | 0:40 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2390 | seconds
Heat Source Offset | 0:38 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2266 | seconds
Heat Source Stop Time | 15:01
Test Duration | 0:56 | hours:minutes:seconds
| 3370 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
Large Coil | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-1.4844 | 121.5912 | -60.7132 | 60.7452 | -0.0086212 | 0.002619 | 0.072062 | 0.0051248 | 0.064924 | 0.001363 | -0.00038024 | 0.0069425 | 0.0016962 | 0.063602 | 0.065728 | -0.0081305 | -0.0046741 | 60.6674 | -60.5026 | 0.064087 | -60.7407 | 60.7269 | -60.7636 | -60.7224 | -61.0565 | 0.050354 | -61.0062 | 60.6262 | 60.672 | -60.6674 | -60.8459 | -0.050354 | -0.009155 | -0.01831 | 0.21057 | -0.027466 | -0.018311 | -0.07782 | 0.045777 | -0.13275 | -0.11902 | -0.34332 | -0.29297 | -0.16022 | -0.073242 | 121.4401 | 121.3806 | 60.7773 | -121.4676 | 121.3394 | 121.3852 | 60.7636 | -121.5912
0.25 | 121.637 | -60.7315 | 60.6857 | 0.0066373 | 0.0056098 | 0.071634 | 0.00897 | 0.065779 | -0.0050458 | -0.0014484 | 0.0069425 | -0.002149 | 0.064884 | 0.064873 | -0.012403 | -0.0033923 | 60.6445 | -60.434 | 0.086975 | -60.7178 | 60.64 | -60.759 | -60.7178 | -61.0519 | 0.16937 | -60.9329 | 60.5576 | 60.5759 | -60.672 | -60.878 | -0.027466 | 0.013733 | -0.045776 | 0.29755 | 0.013733 | 0 | -0.041199 | 0.059509 | -0.14648 | -0.12817 | -0.32043 | -0.20142 | -0.054931 | -0.10986 | 121.3715 | 121.376 | 60.8185 | -121.4035 | 121.2891 | 121.3074 | 60.9009 | -121.5637
1.9062 | 121.5363 | -60.7956 | 60.704 | 0.0066373 | 0.0081732 | 0.074625 | 0.001066 | 0.063215 | -0.0033368 | -0.0031574 | -0.008316 | -0.003858 | 0.06232 | 0.065087 | -0.0085577 | -0.0036059 | 60.6354 | -60.4752 | 0.054932 | -60.7636 | 60.6583 | -60.7544 | -60.7178 | -61.0565 | 0.036621 | -60.9787 | 60.5576 | 60.5713 | -60.6903 | -60.8826 | 0.041198 | 0.07782 | -0.045777 | 0.32043 | 0.032043 | -0.045777 | -0.068665 | 0.10528 | -0.086975 | -0.14648 | -0.26093 | -0.18311 | -0.096131 | -0.13275 | 121.4539 | 121.431 | 60.8505 | -121.4218 | 121.3531 | 121.3669 | 60.8322 | -121.5866
3.625 | 121.5775 | -60.759 | 60.6995 | -0.00099167 | 0.0079596 | 0.070353 | 0.0036294 | 0.064497 | 0.00029476 | 0.00047416 | 0.0069425 | -0.00044004 | 0.062107 | 0.065728 | -0.0079169 | -0.0055285 | 60.6537 | -60.5118 | 0.045776 | -60.7315 | 60.6628 | -60.7773 | -60.7132 | -61.0382 | 0.064087 | -60.9741 | 60.5713 | 60.5804 | -60.6995 | -60.8597 | -0.018311 | 0.045776 | -0.036621 | 0.24719 | 0.027466 | -0.01831 | -0.045776 | 0.059509 | -0.10071 | -0.12817 | -0.27924 | -0.21515 | -0.11444 | -0.11902 | 121.4218 | 121.4127 | 60.8047 | -121.4127 | 121.3303 | 121.3394 | 60.8231 | -121.5591
5.2812 | 121.6187 | -60.7407 | 60.7086 | 0.021896 | 0.001551 | 0.071848 | 0.0044838 | 0.064497 | -0.0035504 | -0.0020892 | -0.00068649 | -0.0027898 | 0.062534 | 0.064019 | -0.01048 | -0.0040331 | 60.6354 | -60.4797 | 0.11902 | -60.7315 | 60.6812 | -60.7636 | -60.7269 | -61.0611 | 0.13275 | -60.9787 | 60.585 | 60.6125 | -60.6628 | -60.8734 | -0.022888 | 0.013733 | -0.027466 | 0.26093 | 0.009156 | -0.004577 | -0.073242 | 0.07782 | -0.13275 | -0.1236 | -0.32043 | -0.23804 | -0.10529 | -0.09613 | 121.4218 | 121.376 | 60.8597 | -121.4355 | 121.3257 | 121.3531 | 60.8734 | -121.582
7.0156 | 121.582 | -60.7452 | 60.7315 | 0.0066373 | 0.0083868 | 0.068857 | 0.003843 | 0.064924 | 0.001363 | -0.0023028 | 0.0069425 | 0.002337 | 0.064884 | 0.0653 | -0.0077033 | -0.0059557 | 60.5896 | -60.6171 | -0.032043 | -60.8047 | 60.7452 | -60.7681 | -60.7361 | -61.1114 | -0.050354 | -61.0703 | 60.64 | 60.6354 | -60.6949 | -60.8688 | -0.022888 | 0.009155 | 0.013733 | 0.12817 | -0.05951 | -0.068665 | -0.14191 | 0.050354 | -0.1236 | -0.091552 | -0.36621 | -0.32501 | -0.20142 | -0.09613 | 121.4905 | 121.3348 | 60.7132 | -121.4676 | 121.3852 | 121.3806 | 60.6949 | -121.6003
8.6875 | 121.6141 | -60.6949 | 60.7224 | -0.00099167 | 0.0036872 | 0.069284 | 0.0068338 | 0.065138 | -0.00077324 | -0.0012346 | 0.0069425 | 0.001269 | 0.063816 | 0.066582 | -0.011549 | -0.0055285 | 60.6125 | -60.5392 | 0.059509 | -60.7498 | 60.6995 | -60.7498 | -60.7132 | -61.1252 | 0.073242 | -61.0336 | 60.64 | 60.6628 | -60.6812 | -60.8734 | -0.054932 | -0.018311 | -0.022888 | 0.15564 | -0.054932 | -0.036621 | -0.10986 | 0.013733 | -0.17853 | -0.082397 | -0.4303 | -0.33875 | -0.16022 | -0.059509 | 121.3943 | 121.3074 | 60.7544 | -121.4355 | 121.3348 | 121.3577 | 60.7681 | -121.5958
10.4219 | 121.5546 | -60.7544 | 60.7269 | 0.0066373 | 0.0056098 | 0.069712 | 0.0029886 | 0.065351 | 0.0017902 | -0.00080744 | 0.0069425 | 0.0021234 | 0.065311 | 0.065514 | -0.0074897 | -0.0046741 | 60.5759 | -60.6125 | -0.036621 | -60.8002 | 60.7452 | -60.7864 | -60.6995 | -61.1206 | -0.050354 | -61.0748 | 60.6445 | 60.6674 | -60.7086 | -60.8688 | -0.032043 | 0.054932 | 0.01831 | 0.14191 | -0.045776 | -0.10071 | -0.15106 | 0.045777 | -0.11444 | -0.082398 | -0.36621 | -0.32043 | -0.20599 | -0.05951 | 121.4996 | 121.3303 | 60.7178 | -121.4264 | 121.3989 | 121.4218 | 60.704 | -121.5958
12.1406 | 121.6553 | -60.7361 | 60.6995 | -0.00099167 | 0.0073188 | 0.072275 | 0.0051248 | 0.065992 | -0.0052594 | -0.0018756 | 0.014572 | -0.00022644 | 0.062107 | 0.065941 | -0.011549 | -0.0018969 | 60.6354 | -60.4706 | 0.086975 | -60.7407 | 60.6491 | -60.7681 | -60.7224 | -61.0291 | 0.16022 | -60.9421 | 60.5713 | 60.5942 | -60.6583 | -60.8505 | -0.032043 | 0.013733 | -0.050354 | 0.2655 | -0.004578 | -0.018311 | -0.064087 | 0.07782 | -0.11444 | -0.12817 | -0.29297 | -0.20599 | -0.091553 | -0.10529 | 121.3852 | 121.3715 | 60.8231 | -121.4218 | 121.3074 | 121.3303 | 60.8963 | -121.55
13.8125 | 121.6232 | -60.7269 | 60.7452 | -0.00099167 | 0.0036872 | 0.070353 | 0.0034158 | 0.064497 | 0.0037128 | 4.696e-05 | -0.00068649 | 0.0025508 | 0.063602 | 0.065941 | -0.0074897 | -0.0055285 | 60.6583 | -60.5164 | 0.068665 | -60.7407 | 60.7498 | -60.759 | -60.6583 | -61.0245 | 0.09613 | -60.997 | 60.672 | 60.6766 | -60.6628 | -60.8414 | -0.032043 | 0.068665 | 0.004578 | 0.21057 | -0.013733 | -0.082398 | -0.086975 | 0.064087 | -0.11444 | -0.073242 | -0.29755 | -0.27008 | -0.15564 | -0.068664 | 121.4767 | 121.3852 | 60.7956 | -121.4035 | 121.3989 | 121.4035 | 60.8231 | -121.5866
15.5312 | 121.5454 | -60.7864 | 60.7819 | 0.014267 | 0.0058234 | 0.068644 | 0.002775 | 0.063643 | 0.00093576 | -0.0023028 | 0.014572 | 0.0019098 | 0.065097 | 0.067009 | -0.0074897 | -0.0029651 | 60.5713 | -60.6262 | -0.032043 | -60.8047 | 60.7361 | -60.7681 | -60.7224 | -61.1114 | -0.041199 | -61.0748 | 60.6674 | 60.6812 | -60.6674 | -60.8871 | 0.018311 | 0.064087 | -0.045776 | 0.16022 | -0.018311 | -0.082398 | -0.21057 | 0.11902 | -0.10071 | -0.11444 | -0.32501 | -0.28839 | -0.18768 | -0.10071 | 121.5225 | 121.3577 | 60.7544 | -121.5042 | 121.4539 | 121.4676 | 60.7452 | -121.669
17.2656 | 121.637 | -60.7498 | 60.6812 | -0.00099167 | 0.0086006 | 0.069498 | 0.0046976 | 0.064711 | -0.0078228 | -0.0040118 | 0.0069425 | -0.0032172 | 0.063816 | 0.065087 | -0.014112 | -0.0042467 | 60.5713 | -60.553 | 0.027466 | -60.7681 | 60.6674 | -60.7956 | -60.7086 | -61.0886 | 0.073242 | -60.9741 | 60.5759 | 60.6171 | -60.6857 | -60.8826 | -0.045776 | 0.041199 | -0.013733 | 0.19684 | -0.01831 | -0.059509 | -0.10986 | 0.064087 | -0.13275 | -0.10528 | -0.33875 | -0.2243 | -0.091553 | -0.064087 | 121.4172 | 121.3211 | 60.7773 | -121.3898 | 121.3257 | 121.3669 | 60.8231 | -121.5637
18.9375 | 121.6965 | -60.6995 | 60.7315 | 0.0066373 | 0.0028326 | 0.070353 | 0.007261 | 0.064497 | 0.0011494 | -0.001662 | -0.00068649 | 0.0019098 | 0.063816 | 0.064873 | -0.0094123 | -0.0048877 | 60.585 | -60.585 | -0.004578 | -60.7773 | 60.7361 | -60.7773 | -60.7407 | -61.1069 | 0.036621 | -61.0428 | 60.6537 | 60.6857 | -60.704 | -60.8597 | -0.07782 | -0.041199 | 0.004578 | 0.11444 | -0.07782 | -0.036621 | -0.14648 | -0.004578 | -0.16022 | -0.077819 | -0.40741 | -0.34332 | -0.18311 | -0.045776 | 121.4355 | 121.2845 | 60.6949 | -121.4722 | 121.3531 | 121.3852 | 60.7361 | -121.5912
20.6719 | 121.6187 | -60.7132 | 60.7086 | 0.014267 | 0.0039008 | 0.069498 | 0.0053384 | 0.065779 | -0.0041912 | -0.001662 | 0.0069425 | 0.0010554 | 0.065738 | 0.064232 | -0.010053 | -0.0059557 | 60.6354 | -60.466 | 0.11444 | -60.7452 | 60.6537 | -60.7498 | -60.7132 | -61.0336 | 0.15106 | -60.9512 | 60.6033 | 60.6171 | -60.672 | -60.8734 | -0.036621 | 0 | -0.054931 | 0.24719 | -0.032043 | -0.032043 | -0.073242 | 0.041199 | -0.16022 | -0.10529 | -0.32043 | -0.23804 | -0.07782 | -0.091553 | 121.3669 | 121.3486 | 60.8276 | -121.4218 | 121.3165 | 121.3303 | 60.8643 | -121.582
22.3438 | 121.6553 | -60.7269 | 60.6766 | 0.021896 | 0.0073188 | 0.073343 | 0.0044838 | 0.06407 | -0.0029094 | -0.0029436 | -0.008316 | -0.0027898 | 0.065097 | 0.065087 | -0.011335 | -0.0046741 | 60.585 | -60.5347 | 0.022888 | -60.7727 | 60.6857 | -60.7636 | -60.7315 | -61.084 | 0.091553 | -60.9741 | 60.5621 | 60.6033 | -60.6995 | -60.8734 | -0.036621 | -0.004577 | 0.009155 | 0.19226 | -0.045776 | -0.041199 | -0.091553 | 0.027466 | -0.14648 | -0.11444 | -0.35706 | -0.24719 | -0.10071 | -0.073242 | 121.4127 | 121.312 | 60.7498 | -121.4081 | 121.2891 | 121.3303 | 60.8185 | -121.55
24.0625 | 121.6736 | -60.7086 | 60.7132 | 0.0066373 | 0.0019782 | 0.065653 | 0.0036294 | 0.066847 | 0.004781 | -0.0020892 | 0.014572 | 0.0036188 | 0.064457 | 0.066368 | -0.0066351 | -0.0059557 | 60.6354 | -60.5484 | 0.045776 | -60.759 | 60.759 | -60.7498 | -60.7132 | -61.0428 | 0.082397 | -61.0153 | 60.6628 | 60.6628 | -60.6766 | -60.878 | -0.041199 | -0.004578 | 0.045776 | 0.16022 | -0.050354 | -0.045776 | -0.07782 | 0.032043 | -0.16937 | -0.050354 | -0.33417 | -0.3067 | -0.13733 | -0.050354 | 121.4676 | 121.344 | 60.7544 | -121.4264 | 121.3715 | 121.3715 | 60.791 | -121.5912
25.7188 | 121.5271 | -60.7956 | 60.6995 | 0.0066373 | 0.0086006 | 0.071848 | 0.00063865 | 0.065992 | -0.003764 | -0.00038024 | -0.008316 | -0.0010808 | 0.063388 | 0.065728 | -0.0068487 | -0.0038195 | 60.6033 | -60.5072 | 0.018311 | -60.7956 | 60.6262 | -60.7864 | -60.7178 | -61.0794 | 0.032043 | -60.9879 | 60.553 | 60.5667 | -60.6766 | -60.8963 | 0.009155 | 0.07782 | -0.073242 | 0.28839 | 0 | -0.07782 | -0.09613 | 0.11902 | -0.10071 | -0.14648 | -0.28381 | -0.19226 | -0.091553 | -0.13275 | 121.4218 | 121.3989 | 60.8139 | -121.4172 | 121.3486 | 121.3623 | 60.8276 | -121.5958
27.4375 | 121.6003 | -60.7681 | 60.6857 | 0.0066373 | 0.007746 | 0.074625 | 0.0042702 | 0.062788 | -0.0050458 | -0.004439 | 0.0069425 | -0.0012946 | 0.061252 | 0.063164 | -0.0081305 | -0.0048877 | 60.5759 | -60.5667 | -0.013733 | -60.7956 | 60.6628 | -60.7681 | -60.7452 | -61.1069 | 0.045776 | -61.0153 | 60.5896 | 60.5667 | -60.7178 | -60.8826 | 0 | 0.022888 | -0.022888 | 0.20142 | -0.027466 | -0.050354 | -0.10986 | 0.050354 | -0.11444 | -0.09613 | -0.33875 | -0.24719 | -0.13275 | -0.11902 | 121.431 | 121.344 | 60.7544 | -121.431 | 121.3577 | 121.3348 | 60.8139 | -121.5683
29.1719 | 121.6919 | -60.6949 | 60.7086 | 0.0066373 | 0.00326 | 0.070139 | 0.0057656 | 0.06706 | 0.0054218 | -0.001662 | -0.00068649 | 0.0016962 | 0.065525 | 0.064232 | -0.0057807 | -0.0074511 | 60.6079 | -60.5759 | 0.013733 | -60.7636 | 60.7452 | -60.7727 | -60.7224 | -61.0611 | 0.068665 | -61.0153 | 60.6766 | 60.6628 | -60.6766 | -60.8688 | -0.07782 | -0.027466 | 0.036621 | 0.11902 | -0.068665 | -0.041199 | -0.10071 | 0.01831 | -0.17395 | -0.032043 | -0.36621 | -0.32044 | -0.14649 | -0.045776 | 121.4401 | 121.3028 | 60.7086 | -121.431 | 121.3715 | 121.3577 | 60.7636 | -121.5775
30.8906 | 121.6507 | -60.7086 | 60.6766 | -0.0086212 | 0.0096686 | 0.076334 | 0.0042702 | 0.063856 | -0.0048322 | -0.0031574 | 0.0069425 | -0.0025762 | 0.062107 | 0.064232 | -0.01048 | -0.0029651 | 60.585 | -60.5072 | 0.041199 | -60.7773 | 60.6766 | -60.7819 | -60.7315 | -61.0794 | 0.11444 | -60.9558 | 60.553 | 60.5896 | -60.6674 | -60.878 | -0.073242 | -0.022888 | 0 | 0.20142 | -0.068665 | -0.045777 | -0.091553 | 0.041199 | -0.16937 | -0.1236 | -0.37079 | -0.24719 | -0.07782 | -0.086975 | 121.3852 | 121.2936 | 60.7498 | -121.4081 | 121.2616 | 121.2982 | 60.8231 | -121.5546
32.5625 | 121.5454 | -60.8047 | 60.704 | 0.0066373 | 0.0079596 | 0.070566 | 0.0059792 | 0.064497 | -0.0029094 | -0.0029436 | 0.014572 | -0.0017218 | 0.063602 | 0.063378 | -0.0094123 | -0.0048877 | 60.5896 | -60.5438 | 0.013733 | -60.8002 | 60.6445 | -60.7819 | -60.7269 | -61.1114 | 0.018311 | -61.0291 | 60.585 | 60.5804 | -60.7086 | -60.91 | 0.022889 | 0.07782 | -0.05951 | 0.26093 | 0.004578 | -0.073242 | -0.11444 | 0.096131 | -0.10529 | -0.11902 | -0.3067 | -0.2243 | -0.11902 | -0.1236 | 121.4493 | 121.3943 | 60.8185 | -121.431 | 121.3898 | 121.3852 | 60.8231 | -121.6141
34.2812 | 121.5363 | -60.7956 | 60.7178 | 0.0066373 | 0.0081732 | 0.071634 | 0.00085245 | 0.066206 | -0.0014142 | -0.0029436 | 0.022202 | 0.0010554 | 0.063388 | 0.063378 | -0.0070623 | -0.0046741 | 60.6628 | -60.466 | 0.054932 | -60.7407 | 60.6491 | -60.7636 | -60.7224 | -61.0428 | 0.064087 | -60.9604 | 60.553 | 60.5667 | -60.6857 | -60.8917 | 0.032043 | 0.073242 | -0.068664 | 0.32959 | 0.054931 | -0.018311 | -0.054931 | 0.10986 | -0.096131 | -0.16479 | -0.24719 | -0.1648 | -0.068664 | -0.15106 | 121.4447 | 121.4584 | 60.8505 | -121.4401 | 121.3486 | 121.3623 | 60.8597 | -121.6095
36 | 121.5408 | -60.791 | 60.6766 | 0.0066373 | 0.0083868 | 0.07078 | 0.002775 | 0.065351 | -0.00034604 | -0.00080744 | 0.014572 | 0.00084176 | 0.061252 | 0.0653 | -0.0064215 | -0.0057421 | 60.6674 | -60.4889 | 0.059509 | -60.7315 | 60.64 | -60.759 | -60.7178 | -61.0153 | 0.073242 | -60.9421 | 60.5576 | 60.5713 | -60.6903 | -60.8368 | 0.032044 | 0.073243 | -0.036621 | 0.30212 | 0.05951 | -0.013733 | -0.009156 | 0.10071 | -0.045776 | -0.11902 | -0.2243 | -0.15106 | -0.10529 | -0.10529 | 121.431 | 121.4584 | 60.8505 | -121.3943 | 121.3486 | 121.3623 | 60.8643 | -121.5134
37.7188 | 121.6324 | -60.7544 | 60.6674 | 0.014267 | 0.0064642 | 0.073343 | 0.0051248 | 0.067274 | -0.0031232 | -0.0031574 | 0.022202 | -0.0010808 | 0.064029 | 0.064659 | -0.0094123 | -0.0044605 | 60.5804 | -60.5438 | 0.018311 | -60.7819 | 60.6857 | -60.7636 | -60.7315 | -61.0703 | 0.073242 | -60.9787 | 60.585 | 60.553 | -60.6995 | -60.8597 | -0.009155 | 0.022889 | 0.018311 | 0.21057 | -0.027465 | -0.050354 | -0.086975 | 0.054932 | -0.10528 | -0.082397 | -0.31586 | -0.2243 | -0.11902 | -0.11444 | 121.4401 | 121.3348 | 60.7727 | -121.3989 | 121.3394 | 121.3074 | 60.8276 | -121.5271
39.4375 | 121.6415 | -60.6995 | 60.6857 | 0.0066373 | 0.007746 | 0.073984 | 0.0053384 | 0.065565 | -0.0022686 | -0.0029436 | 0.014572 | -0.0017218 | 0.064243 | 0.064446 | -0.011121 | -0.0053149 | 60.6537 | -60.4752 | 0.091553 | -60.7269 | 60.672 | -60.7681 | -60.7224 | -61.0245 | 0.14648 | -60.9146 | 60.5667 | 60.5942 | -60.6674 | -60.8643 | -0.068664 | -0.022888 | -0.013733 | 0.2243 | -0.027466 | -0.004578 | -0.032043 | 0.032044 | -0.16479 | -0.11902 | -0.32501 | -0.21515 | -0.050354 | -0.091553 | 121.3715 | 121.3531 | 60.791 | -121.4081 | 121.2662 | 121.2936 | 60.8459 | -121.55
41.1094 | 121.5591 | -60.7269 | 60.7544 | 0.0066373 | 0.0036872 | 0.069498 | 0.0025612 | 0.064924 | 0.0054218 | -0.00059384 | 0.0069425 | 0.0038324 | 0.063388 | 0.065728 | -0.0047125 | -0.0080921 | 60.6583 | -60.5255 | 0.059509 | -60.7544 | 60.7361 | -60.7544 | -60.7086 | -61.0428 | 0.045776 | -61.0291 | 60.64 | 60.6674 | -60.6628 | -60.8322 | -0.027466 | 0.018311 | -0.018311 | 0.20142 | -0.027466 | -0.045777 | -0.096131 | 0.064087 | -0.10529 | -0.11444 | -0.31586 | -0.30212 | -0.19684 | -0.086976 | 121.463 | 121.3852 | 60.7864 | -121.463 | 121.3669 | 121.3943 | 60.7727 | -121.5866
42.8125 | 121.6324 | -60.7315 | 60.704 | 0.0066373 | 0.004328 | 0.07078 | 0.0064066 | 0.068769 | -0.0052594 | -0.003371 | 0.014572 | -0.0012946 | 0.064457 | 0.063378 | -0.012403 | -0.0053149 | 60.6674 | -60.434 | 0.10529 | -60.7224 | 60.6491 | -60.7773 | -60.7086 | -61.0199 | 0.16022 | -60.9329 | 60.5576 | 60.5896 | -60.6674 | -60.878 | -0.045777 | 0.022888 | -0.054932 | 0.29755 | 0.009155 | -0.013733 | -0.036622 | 0.064087 | -0.14648 | -0.14648 | -0.28839 | -0.20142 | -0.054931 | -0.11444 | 121.3806 | 121.3989 | 60.8368 | -121.4127 | 121.2891 | 121.3211 | 60.8917 | -121.582
44.5 | 121.5271 | -60.7498 | 60.7636 | -0.0086212 | 0.007746 | 0.068857 | 0.001066 | 0.063215 | 0.0039264 | -0.0025164 | -0.00068649 | 0.002337 | 0.065525 | 0.064232 | -0.0057807 | -0.0055285 | 60.5942 | -60.5759 | 0 | -60.7681 | 60.7681 | -60.759 | -60.6949 | -61.0977 | -0.032043 | -61.0886 | 60.6583 | 60.6903 | -60.6903 | -60.8551 | -0.009155 | 0.054932 | 0.004577 | 0.17395 | -0.01831 | -0.073242 | -0.16937 | 0.059509 | -0.10529 | -0.10529 | -0.3479 | -0.33875 | -0.23346 | -0.073242 | 121.5179 | 121.344 | 60.7498 | -121.4584 | 121.4081 | 121.4401 | 60.7178 | -121.6187
46.2188 | 121.637 | -60.7224 | 60.6674 | 0.0066373 | 0.0053962 | 0.072062 | 0.0079018 | 0.065565 | -0.0044048 | -0.001662 | 0.014572 | -0.0019354 | 0.065097 | 0.063805 | -0.010908 | -0.0046741 | 60.6628 | -60.4294 | 0.10071 | -60.7086 | 60.6583 | -60.7498 | -60.7315 | -61.0153 | 0.16937 | -60.9375 | 60.585 | 60.6125 | -60.6766 | -60.8734 | -0.027466 | -0.009155 | -0.009155 | 0.29297 | 0.013733 | 0.022888 | -0.004577 | 0.045776 | -0.15106 | -0.082397 | -0.29297 | -0.21515 | -0.064087 | -0.054931 | 121.3806 | 121.3852 | 60.8231 | -121.3989 | 121.3074 | 121.3348 | 60.8917 | -121.5408
47.9531 | 121.5408 | -60.7864 | 60.6995 | 0.0066373 | 0.011378 | 0.075693 | 0.0014932 | 0.064497 | -0.0024822 | -0.00038024 | 0.0069425 | 0.0019098 | 0.061679 | 0.0653 | -0.0072759 | -0.0046741 | 60.5942 | -60.5164 | 0.032043 | -60.7819 | 60.6354 | -60.759 | -60.7224 | -61.0703 | 0.036621 | -61.0016 | 60.5392 | 60.585 | -60.6857 | -60.8597 | 0.027466 | 0.064087 | -0.064087 | 0.27008 | 0.004578 | -0.059509 | -0.10529 | 0.10071 | -0.073242 | -0.16022 | -0.28381 | -0.21515 | -0.14191 | -0.11444 | 121.4218 | 121.3806 | 60.8185 | -121.4218 | 121.3257 | 121.3715 | 60.8231 | -121.5591
49.6094 | 121.5271 | -60.7269 | 60.7407 | 0.014267 | 0.0013374 | 0.066721 | 0.0046976 | 0.063002 | 0.0045674 | 4.696e-05 | 0.0069425 | 0.0042596 | 0.06467 | 0.065514 | -0.0085577 | -0.0059557 | 60.64 | -60.5621 | 0.032043 | -60.7407 | 60.7498 | -60.7681 | -60.6949 | -61.0611 | 0.013733 | -61.0336 | 60.6766 | 60.6628 | -60.6583 | -60.8688 | -0.041198 | 0.032044 | 0.009155 | 0.16479 | -0.013733 | -0.045777 | -0.10071 | 0.068665 | -0.14191 | -0.064087 | -0.33417 | -0.3067 | -0.1648 | -0.07782 | 121.4767 | 121.3669 | 60.759 | -121.4355 | 121.4035 | 121.3898 | 60.7407 | -121.6095
51.3281 | 121.669 | -60.6812 | 60.7224 | 0.0066373 | 0.001551 | 0.067362 | 0.003843 | 0.064283 | 0.002431 | -0.00059384 | -0.00068649 | 0.0019098 | 0.06467 | 0.068505 | -0.0062079 | -0.0057421 | 60.6354 | -60.5392 | 0.059509 | -60.7269 | 60.7315 | -60.7681 | -60.7086 | -61.0245 | 0.082397 | -60.997 | 60.6537 | 60.6857 | -60.6674 | -60.8551 | -0.086975 | -0.027466 | 0.009155 | 0.14191 | -0.045777 | -0.018311 | -0.086975 | 0.013733 | -0.17395 | -0.068664 | -0.34332 | -0.31586 | -0.14191 | -0.036621 | 121.4127 | 121.3165 | 60.7407 | -121.431 | 121.3348 | 121.3669 | 60.7635 | -121.5775
53.0625 | 121.5729 | -60.759 | 60.7224 | -0.00099167 | 0.0083868 | 0.072062 | 0.0053384 | 0.065138 | -0.0063274 | -0.00059384 | -0.00068649 | -0.0023626 | 0.065097 | 0.065514 | -0.011549 | -0.0061695 | 60.553 | -60.5576 | -0.022888 | -60.7864 | 60.672 | -60.7681 | -60.7224 | -61.0931 | 0.041199 | -61.0245 | 60.5759 | 60.6171 | -60.7132 | -60.9055 | -0.009155 | 0.036621 | -0.050354 | 0.20142 | -0.027466 | -0.064087 | -0.16937 | 0.045776 | -0.14648 | -0.14648 | -0.33417 | -0.2655 | -0.11902 | -0.10529 | 121.431 | 121.312 | 60.7361 | -121.4447 | 121.3348 | 121.376 | 60.8002 | -121.6278
54.7344 | 121.669 | -60.6903 | 60.6949 | -0.0086212 | 0.0034736 | 0.069925 | 0.0023476 | 0.068342 | 0.00093576 | -0.0040118 | 0.014572 | 0.0044734 | 0.064457 | 0.066796 | -0.0083441 | -0.0044605 | 60.585 | -60.5667 | 0 | -60.7864 | 60.7452 | -60.7864 | -60.7178 | -61.084 | 0.032043 | -61.0519 | 60.6812 | 60.6857 | -60.6995 | -60.8917 | -0.09613 | -0.027465 | 0.050354 | 0.1236 | -0.09613 | -0.068665 | -0.10986 | -0.009155 | -0.20142 | -0.013733 | -0.39368 | -0.36163 | -0.16022 | -0.009155 | 121.4355 | 121.2753 | 60.6903 | -121.4127 | 121.3715 | 121.376 | 60.7224 | -121.5866
56.4531 | 121.6278 | -60.7269 | 60.7132 | -0.00099167 | 0.004969 | 0.073771 | 0.0029886 | 0.064924 | -0.0029094 | -0.003371 | -0.00068649 | 0.00020076 | 0.063602 | 0.064446 | -0.0098395 | -0.0046741 | 60.64 | -60.4477 | 0.11444 | -60.7452 | 60.6491 | -60.759 | -60.7361 | -61.0291 | 0.16479 | -60.9238 | 60.5759 | 60.5942 | -60.6628 | -60.8734 | -0.032043 | -0.009155 | -0.064087 | 0.27924 | -0.01831 | -0.009155 | -0.073242 | 0.064087 | -0.14648 | -0.13733 | -0.30212 | -0.19684 | -0.050354 | -0.11902 | 121.376 | 121.3669 | 60.8414 | -121.4493 | 121.3028 | 121.3211 | 60.8917 | -121.5866
58.1875 | 121.5363 | -60.7498 | 60.7773 | 0.0066373 | 0.0021918 | 0.069712 | 0.001066 | 0.065351 | 0.0026446 | -0.00080744 | 0.0069425 | 0.0034052 | 0.063388 | 0.068291 | -0.0049261 | -0.0063831 | 60.5713 | -60.6033 | -0.036621 | -60.7819 | 60.7498 | -60.7727 | -60.7178 | -61.1114 | -0.027466 | -61.0611 | 60.6674 | 60.6812 | -60.6583 | -60.8826 | -0.022888 | 0.032044 | -0.027466 | 0.14648 | -0.032043 | -0.064087 | -0.20599 | 0.091553 | -0.13275 | -0.10986 | -0.36163 | -0.31128 | -0.17853 | -0.096131 | 121.4996 | 121.3211 | 60.7132 | -121.4951 | 121.4172 | 121.431 | 60.7224 | -121.6599
59.9219 | 121.6141 | -60.704 | 60.7224 | 0.0066373 | 0.0036872 | 0.075266 | 0.0034158 | 0.065992 | -0.00055964 | -0.0035846 | 0.0069425 | 0.001269 | 0.065525 | 0.064873 | -0.010267 | -0.0010425 | 60.5621 | -60.5392 | 0.018311 | -60.7819 | 60.7224 | -60.7681 | -60.7086 | -61.1206 | 0.064087 | -61.0291 | 60.6445 | 60.672 | -60.6949 | -60.878 | -0.064086 | -0.004577 | 0 | 0.16479 | -0.077819 | -0.073242 | -0.16022 | 0.009156 | -0.17395 | -0.07782 | -0.41656 | -0.32501 | -0.15106 | -0.050354 | 121.4264 | 121.2662 | 60.7224 | -121.431 | 121.3486 | 121.376 | 60.7681 | -121.6003
61.5938 | 121.5591 | -60.7452 | 60.7452 | -0.00099167 | 0.0058234 | 0.068857 | 0.001066 | 0.065138 | 0.0039264 | -0.0014484 | -0.008316 | 0.00084176 | 0.06467 | 0.067437 | -0.0079169 | -0.0057421 | 60.5713 | -60.6033 | -0.022888 | -60.7773 | 60.7544 | -60.7544 | -60.704 | -61.1069 | -0.050354 | -61.0748 | 60.6445 | 60.6674 | -60.6766 | -60.878 | -0.009156 | 0.041198 | 0.009156 | 0.14191 | -0.032044 | -0.073242 | -0.17395 | 0.068664 | -0.13275 | -0.10071 | -0.36163 | -0.32959 | -0.19684 | -0.07782 | 121.4996 | 121.3165 | 60.7224 | -121.4493 | 121.3898 | 121.4127 | 60.6949 | -121.6232
63.3281 | 121.5225 | -60.8002 | 60.6766 | 0.0066373 | 0.0081732 | 0.070566 | 0.0057656 | 0.062361 | -0.0029094 | -0.0018756 | -0.00068649 | -0.00065364 | 0.063388 | 0.064873 | -0.012403 | -0.0042467 | 60.5896 | -60.5301 | 0.022888 | -60.7681 | 60.6445 | -60.791 | -60.7269 | -61.084 | 0.041199 | -60.9833 | 60.5667 | 60.6125 | -60.6903 | -60.8871 | 0.009155 | 0.073242 | -0.032044 | 0.27008 | 0.032044 | -0.041198 | -0.086975 | 0.10986 | -0.086975 | -0.10986 | -0.28381 | -0.1831 | -0.09613 | -0.064087 | 121.4447 | 121.3898 | 60.8231 | -121.4035 | 121.3669 | 121.4127 | 60.8414 | -121.5637
65 | 121.5866 | -60.6995 | 60.7773 | 0.0066373 | 0.0028326 | 0.066507 | 0.0064066 | 0.067915 | 0.0037128 | -0.0020892 | 0.014572 | 0.0027644 | 0.065952 | 0.065087 | -0.0096259 | -0.0076647 | 60.6583 | -60.5026 | 0.073242 | -60.7361 | 60.7315 | -60.7361 | -60.6995 | -61.0519 | 0.064087 | -61.0016 | 60.6491 | 60.6949 | -60.6674 | -60.8505 | -0.036621 | 0 | -0.045777 | 0.19684 | -0.036621 | -0.036621 | -0.11902 | 0.032044 | -0.15106 | -0.12817 | -0.35248 | -0.30212 | -0.15106 | -0.082398 | 121.431 | 121.3577 | 60.7727 | -121.4767 | 121.3486 | 121.3943 | 60.7636 | -121.6278
66.6562 | 121.6187 | -60.7315 | 60.7178 | -0.00099167 | 0.0053962 | 0.070993 | 0.0068338 | 0.06706 | -0.0031232 | -0.0042254 | 0.0069425 | -0.002149 | 0.063602 | 0.064232 | -0.0094123 | -0.0036059 | 60.6171 | -60.4385 | 0.10986 | -60.7315 | 60.6537 | -60.7636 | -60.704 | -61.0245 | 0.17395 | -60.9329 | 60.5804 | 60.6033 | -60.6628 | -60.8597 | -0.032044 | 0.027465 | -0.064086 | 0.29297 | 0 | -0.027465 | -0.10071 | 0.068664 | -0.12817 | -0.13733 | -0.29297 | -0.20142 | -0.073242 | -0.11444 | 121.3852 | 121.3486 | 60.8414 | -121.4218 | 121.3119 | 121.3348 | 60.9055 | -121.5775
68.3906 | 121.5866 | -60.7315 | 60.7132 | 0.021896 | 0.0028326 | 0.069284 | 0.0044838 | 0.065992 | 0.0017902 | 0.00047416 | -0.00068649 | 0.0025508 | 0.065097 | 0.065941 | -0.0057807 | -0.0038195 | 60.6491 | -60.498 | 0.068665 | -60.7178 | 60.7498 | -60.7452 | -60.7086 | -61.0291 | 0.068665 | -61.0016 | 60.6491 | 60.6354 | -60.672 | -60.8551 | -0.013733 | 0.022888 | 0.036621 | 0.23346 | 0.013733 | -0.009155 | -0.064087 | 0.059509 | -0.1236 | -0.064087 | -0.29755 | -0.27008 | -0.14648 | -0.07782 | 121.4813 | 121.3806 | 60.8002 | -121.4218 | 121.3806 | 121.3669 | 60.8002 | -121.5683
70.0625 | 121.5363 | -60.7956 | 60.6995 | 0.014267 | 0.0068916 | 0.071421 | 0.0040566 | 0.066633 | -0.00077324 | -0.0012346 | 0.0069425 | -0.0012946 | 0.06232 | 0.065941 | -0.0079169 | -0.0042467 | 60.6079 | -60.4797 | 0.050354 | -60.7361 | 60.6491 | -60.7498 | -60.7315 | -61.0245 | 0.082397 | -60.9558 | 60.5667 | 60.5576 | -60.6995 | -60.8826 | 0.045776 | 0.064087 | -0.050354 | 0.31586 | 0.059509 | -0.004578 | -0.091553 | 0.09613 | -0.086975 | -0.13275 | -0.22888 | -0.16022 | -0.073243 | -0.14191 | 121.4447 | 121.4035 | 60.8459 | -121.431 | 121.3623 | 121.3531 | 60.878 | -121.582
71.7344 | 121.6232 | -60.7086 | 60.7452 | -0.00099167 | 0.004969 | 0.070993 | 0.0051248 | 0.062361 | -0.00098684 | -0.0012346 | -0.00068649 | 0.00084176 | 0.06467 | 0.063378 | -0.010694 | -0.0033923 | 60.5667 | -60.5621 | 0.032043 | -60.7819 | 60.7178 | -60.7681 | -60.7178 | -61.116 | 0.050354 | -61.0245 | 60.64 | 60.6812 | -60.7086 | -60.9009 | -0.059509 | -0.009155 | -0.027466 | 0.14648 | -0.073242 | -0.064087 | -0.17853 | 0 | -0.19226 | -0.10528 | -0.40741 | -0.31586 | -0.1236 | -0.064087 | 121.4264 | 121.2753 | 60.7407 | -121.463 | 121.3486 | 121.3898 | 60.759 | -121.6461
73.4688 | 121.6415 | -60.7315 | 60.6674 | 0.0066373 | 0.0086006 | 0.070993 | 0.0051248 | 0.064283 | -0.0039776 | -0.0046526 | 0.0069425 | -0.0015082 | 0.062534 | 0.064446 | -0.010908 | -0.0044605 | 60.6216 | -60.466 | 0.07782 | -60.7315 | 60.6445 | -60.7681 | -60.6995 | -61.0519 | 0.14648 | -60.9238 | 60.553 | 60.5804 | -60.6857 | -60.8734 | -0.036621 | 0.032043 | -0.022888 | 0.2655 | 0 | -0.032043 | -0.045776 | 0.045776 | -0.14191 | -0.11444 | -0.32043 | -0.19226 | -0.050354 | -0.086975 | 121.376 | 121.3531 | 60.8093 | -121.3669 | 121.2845 | 121.3119 | 60.878 | -121.5408
75.2031 | 121.5363 | -60.7407 | 60.759 | 0.0066373 | 0.0024054 | 0.068857 | 0.003843 | 0.066633 | 0.0028584 | -0.0037982 | -0.00068649 | 0.0016962 | 0.062748 | 0.065941 | -0.0057807 | -0.0051013 | 60.6308 | -60.5484 | 0.041199 | -60.7498 | 60.7636 | -60.7452 | -60.7086 | -61.0565 | 0.004578 | -61.0382 | 60.6537 | 60.6354 | -60.6857 | -60.8734 | -0.004577 | 0.032044 | 0.004578 | 0.19226 | -0.009155 | -0.041199 | -0.12817 | 0.054932 | -0.13275 | -0.10529 | -0.31586 | -0.29755 | -0.16479 | -0.1236 | 121.5042 | 121.3715 | 60.7819 | -121.4676 | 121.3943 | 121.376 | 60.7452 | -121.6324
76.875 | 121.6827 | -60.6949 | 60.7269 | 0.0066373 | 0.0021918 | 0.068644 | 0.0053384 | 0.065138 | 0.0026446 | -0.00080744 | 0.0069425 | 0.00084176 | 0.065311 | 0.063591 | -0.010267 | -0.0031787 | 60.585 | -60.5484 | 0.041199 | -60.7498 | 60.7498 | -60.7498 | -60.7178 | -61.0657 | 0.073242 | -61.0062 | 60.6766 | 60.6766 | -60.672 | -60.8643 | -0.054932 | -0.022888 | 0.022888 | 0.14648 | -0.054932 | -0.032044 | -0.14191 | 0.022888 | -0.16937 | -0.050354 | -0.37079 | -0.31128 | -0.14191 | -0.050354 | 121.4447 | 121.2799 | 60.7361 | -121.4447 | 121.3715 | 121.3715 | 60.7681 | -121.5912
78.6094 | 121.5408 | -60.7727 | 60.6857 | 0.014267 | 0.0098822 | 0.070993 | 0.007261 | 0.066206 | -0.0059002 | -0.0031574 | 0.0069425 | -0.0012946 | 0.065311 | 0.065728 | -0.011121 | -0.0057421 | 60.5621 | -60.5576 | 0.009155 | -60.7819 | 60.6354 | -60.7727 | -60.7178 | -61.116 | 0.022888 | -61.0107 | 60.553 | 60.5896 | -60.6903 | -60.8871 | 0 | 0.054932 | -0.050354 | 0.21515 | -0.009155 | -0.064087 | -0.1236 | 0.082397 | -0.11444 | -0.13275 | -0.34332 | -0.23804 | -0.1236 | -0.09613 | 121.4081 | 121.3348 | 60.7819 | -121.4035 | 121.3257 | 121.3623 | 60.7956 | -121.5729
80.3438 | 121.6324 | -60.6812 | 60.7269 | -0.0086212 | 0.0017646 | 0.066935 | 0.0053384 | 0.063429 | -0.00055964 | -0.0025164 | -0.00068649 | 0.0034052 | 0.064243 | 0.065728 | -0.0085577 | -0.0046741 | 60.5667 | -60.5942 | 0.022888 | -60.7819 | 60.7269 | -60.7681 | -60.7224 | -61.116 | 0.022888 | -61.0382 | 60.6857 | 60.6949 | -60.6491 | -60.8597 | -0.086975 | -0.041199 | 0 | 0.086975 | -0.10071 | -0.059509 | -0.16022 | 0.032043 | -0.17853 | -0.041199 | -0.43488 | -0.35706 | -0.17853 | -0.032044 | 121.4081 | 121.2479 | 60.704 | -121.4493 | 121.3669 | 121.376 | 60.704 | -121.5866
82 | 121.6095 | -60.7178 | 60.6903 | 0.0066373 | 0.0021918 | 0.07313 | 0.0053384 | 0.064283 | -0.0024822 | -0.0031574 | 0.0069425 | -0.0040716 | 0.06467 | 0.064659 | -0.010694 | -0.0053149 | 60.6216 | -60.4385 | 0.10071 | -60.7315 | 60.6628 | -60.7544 | -60.6766 | -61.0428 | 0.16937 | -60.9238 | 60.5713 | 60.6171 | -60.6674 | -60.8551 | -0.036622 | 0.041198 | -0.027466 | 0.27923 | -0.013733 | -0.054931 | -0.068665 | 0.050354 | -0.13733 | -0.11902 | -0.32501 | -0.20599 | -0.068664 | -0.073243 | 121.3806 | 121.3394 | 60.8185 | -121.3669 | 121.2891 | 121.3348 | 60.8871 | -121.5454
83.6875 | 121.6415 | -60.6857 | 60.7269 | 0.0066373 | 0.0024054 | 0.067148 | 0.0029886 | 0.067274 | 0.004781 | -0.00059384 | -0.00068649 | 0.0016962 | 0.066379 | 0.0653 | -0.0072759 | -0.0055285 | 60.6354 | -60.5072 | 0.064087 | -60.7269 | 60.7681 | -60.7361 | -60.7086 | -61.0245 | 0.07782 | -60.9787 | 60.6491 | 60.6812 | -60.64 | -60.8322 | -0.050354 | -0.022888 | 0.041198 | 0.17853 | -0.041199 | -0.018311 | -0.091553 | 0.045776 | -0.14648 | -0.07782 | -0.33875 | -0.29297 | -0.14648 | -0.045777 | 121.4539 | 121.3211 | 60.7498 | -121.4355 | 121.3348 | 121.3669 | 60.7636 | -121.5591
85.4062 | 121.6232 | -60.7178 | 60.7132 | 0.0066373 | 0.001551 | 0.069925 | 0.0051248 | 0.064924 | -0.0026958 | -0.0025164 | 0.0069425 | 0.00084176 | 0.066806 | 0.0653 | -0.014112 | -0.0027515 | 60.5621 | -60.553 | 0.009155 | -60.7773 | 60.7269 | -60.7498 | -60.7224 | -61.1023 | 0.054932 | -61.0428 | 60.6628 | 60.6674 | -60.6903 | -60.8551 | -0.032044 | -0.004578 | 0.013733 | 0.16479 | -0.05951 | -0.054932 | -0.15106 | 0.027465 | -0.13733 | -0.050354 | -0.38452 | -0.32501 | -0.18768 | -0.045777 | 121.4447 | 121.2799 | 60.7269 | -121.4355 | 121.3806 | 121.3852 | 60.7727 | -121.5683
87.125 | 121.6232 | -60.6949 | 60.7132 | -0.00099167 | 0.00026917 | 0.070139 | 0.0064066 | 0.063215 | -0.0024822 | -0.001662 | 0.014572 | 0.00062796 | 0.066166 | 0.067437 | -0.0094123 | -0.0042467 | 60.553 | -60.5667 | 0.022888 | -60.8047 | 60.7452 | -60.7636 | -60.7086 | -61.1069 | 0.050354 | -61.0245 | 60.64 | 60.6949 | -60.6995 | -60.8597 | -0.068665 | -0.013733 | 0.032043 | 0.12817 | -0.10986 | -0.096131 | -0.16022 | -0.004578 | -0.16479 | -0.073242 | -0.41199 | -0.32959 | -0.1648 | -0.018311 | 121.4401 | 121.2479 | 60.7178 | -121.4218 | 121.3348 | 121.3898 | 60.7452 | -121.5729
88.8438 | 121.5271 | -60.7452 | 60.7452 | 0.0066373 | 0.0021918 | 0.071207 | 0.0025612 | 0.065565 | 0.0020038 | -0.0014484 | 0.0069425 | 0.0042596 | 0.064243 | 0.0653 | -0.0044989 | -0.0040331 | 60.64 | -60.5164 | 0.054932 | -60.7498 | 60.7315 | -60.7269 | -60.7224 | -61.0519 | 0.027466 | -61.0153 | 60.6354 | 60.6857 | -60.6674 | -60.8688 | 0.01831 | 0.022888 | -0.013733 | 0.22888 | -0.004578 | -0.027466 | -0.10528 | 0.07782 | -0.1236 | -0.10986 | -0.3067 | -0.27008 | -0.14649 | -0.059509 | 121.4767 | 121.3852 | 60.8002 | -121.4676 | 121.3806 | 121.431 | 60.7727 | -121.6141
90.5625 | 121.5546 | -60.7361 | 60.7132 | 0.0066373 | 0.0058234 | 0.07078 | 0.00063865 | 0.066847 | -0.00055964 | -0.0012346 | -0.008316 | 0.0031916 | 0.064243 | 0.06765 | -0.0081305 | -0.0044605 | 60.5576 | -60.5942 | -0.036621 | -60.7773 | 60.7407 | -60.7407 | -60.7132 | -61.1206 | -0.032043 | -61.0519 | 60.6445 | 60.6674 | -60.6903 | -60.8688 | -0.004578 | 0.022888 | 0.027466 | 0.14191 | -0.041199 | -0.064087 | -0.15564 | 0.045776 | -0.13275 | -0.068665 | -0.38452 | -0.31586 | -0.18311 | -0.045777 | 121.4767 | 121.2936 | 60.6995 | -121.4264 | 121.3806 | 121.4035 | 60.704 | -121.582
92.2969 | 121.6415 | -60.6766 | 60.6995 | -0.00099167 | 0.00326 | 0.068644 | 0.0051248 | 0.065138 | -0.00034604 | -0.0023028 | -0.00068649 | 0.00084176 | 0.066593 | 0.065087 | -0.012617 | -0.0025379 | 60.553 | -60.5667 | 0.022888 | -60.7864 | 60.7224 | -60.7727 | -60.7178 | -61.1298 | 0.036621 | -61.0382 | 60.6445 | 60.6674 | -60.6995 | -60.8871 | -0.09613 | -0.041198 | 0.022888 | 0.10986 | -0.10986 | -0.068665 | -0.14648 | -0.022888 | -0.21057 | -0.054932 | -0.45319 | -0.36163 | -0.15106 | -0.032044 | 121.3989 | 121.2296 | 60.6995 | -121.4172 | 121.3211 | 121.344 | 60.7132 | -121.5866
93.9688 | 121.6553 | -60.6949 | 60.7132 | -0.00099167 | 0.0045416 | 0.068857 | 0.003843 | 0.064924 | 0.00072196 | 0.00090156 | 0.029831 | 0.002337 | 0.063388 | 0.065728 | -0.0083441 | -0.0063831 | 60.5988 | -60.5118 | 0.050354 | -60.7269 | 60.7544 | -60.7407 | -60.6857 | -61.0428 | 0.086975 | -60.9833 | 60.6445 | 60.6674 | -60.6628 | -60.8597 | -0.045777 | 0.009155 | 0.041199 | 0.1831 | -0.032044 | -0.041199 | -0.11444 | 0.032043 | -0.16479 | -0.068665 | -0.3479 | -0.28839 | -0.1236 | -0.045777 | 121.4493 | 121.2936 | 60.7452 | -121.3989 | 121.3394 | 121.3623 | 60.7819 | -121.5729
95.7031 | 121.6644 | -60.6949 | 60.6949 | -0.00099167 | 0.0030464 | 0.070566 | 0.0049112 | 0.064711 | -0.00055964 | -0.00080744 | -0.00068649 | 0.0014826 | 0.066166 | 0.0653 | -0.0098395 | -0.0044605 | 60.5667 | -60.5713 | 0.018311 | -60.759 | 60.7452 | -60.7636 | -60.7224 | -61.0611 | 0.082397 | -60.997 | 60.6674 | 60.6949 | -60.6537 | -60.8459 | -0.068665 | -0.027466 | 0.050354 | 0.1236 | -0.064087 | -0.036621 | -0.12817 | 0.041198 | -0.15106 | -0.027466 | -0.36621 | -0.30212 | -0.15106 | 0 | 121.4401 | 121.2616 | 60.7132 | -121.4172 | 121.3623 | 121.3898 | 60.7773 | -121.5408
97.4375 | 121.6461 | -60.6857 | 60.7178 | -0.00099167 | 0.0024054 | 0.071848 | 0.003843 | 0.065351 | 0.00093576 | -0.001021 | -0.00068649 | 0.00020076 | 0.064243 | 0.067223 | -0.0072759 | -0.0029651 | 60.6079 | -60.5164 | 0.064087 | -60.7498 | 60.7361 | -60.7452 | -60.7132 | -61.0336 | 0.09613 | -60.9695 | 60.6445 | 60.6537 | -60.6674 | -60.8505 | -0.059509 | -0.027466 | 0.018311 | 0.16937 | -0.064087 | -0.036621 | -0.10986 | 0.018311 | -0.16479 | -0.073242 | -0.3479 | -0.28381 | -0.11902 | -0.064086 | 121.4218 | 121.2936 | 60.7498 | -121.431 | 121.3303 | 121.3394 | 60.7819 | -121.5683
99.1094 | 121.5225 | -60.7864 | 60.6903 | 0.0066373 | 0.0068916 | 0.073984 | 0.0051248 | 0.064497 | -0.0046184 | -0.004439 | 0.022202 | -0.0027898 | 0.066806 | 0.063591 | -0.010053 | -0.0036059 | 60.5621 | -60.5118 | 0.009155 | -60.7773 | 60.6537 | -60.7681 | -60.7224 | -61.1023 | 0.041199 | -60.9787 | 60.5713 | 60.5804 | -60.6949 | -60.8826 | 0.018311 | 0.064087 | -0.036621 | 0.27466 | 0.009155 | -0.054932 | -0.12817 | 0.091553 | -0.09613 | -0.11902 | -0.31586 | -0.19226 | -0.096131 | -0.10986 | 121.4401 | 121.3486 | 60.7956 | -121.4127 | 121.3577 | 121.3669 | 60.8276 | -121.5729
100.8438 | 121.5225 | -60.7452 | 60.7315 | 0.014267 | 0.0056098 | 0.070566 | 0.0044838 | 0.064497 | 0.00050836 | -0.0031574 | 0.0069425 | 0.0031916 | 0.063602 | 0.065087 | -0.0057807 | -0.0044605 | 60.5347 | -60.6262 | -0.045776 | -60.7956 | 60.7498 | -60.7636 | -60.7178 | -61.116 | -0.032043 | -61.0611 | 60.6628 | 60.6628 | -60.6766 | -60.8734 | -0.018311 | 0.027466 | 0.018311 | 0.11902 | -0.050354 | -0.07782 | -0.19684 | 0.068664 | -0.12817 | -0.068664 | -0.37079 | -0.31586 | -0.18768 | -0.068664 | 121.4951 | 121.2799 | 60.6995 | -121.4493 | 121.4081 | 121.4081 | 60.7132 | -121.6049
102.5781 | 121.582 | -60.7498 | 60.6812 | -0.00099167 | 0.0088142 | 0.072489 | 0.0070474 | 0.064283 | -0.0044048 | -0.003371 | -0.00068649 | -0.0023626 | 0.065952 | 0.063164 | -0.011762 | -0.0055285 | 60.5255 | -60.5621 | -0.004578 | -60.7864 | 60.6491 | -60.7636 | -60.7132 | -61.1069 | 0.054932 | -60.997 | 60.5621 | 60.5759 | -60.6949 | -60.8917 | -0.013733 | 0.036621 | -0.032043 | 0.18768 | -0.036621 | -0.073242 | -0.15564 | 0.054932 | -0.14191 | -0.11902 | -0.35706 | -0.24719 | -0.10528 | -0.10528 | 121.3989 | 121.2753 | 60.7452 | -121.3943 | 121.312 | 121.3257 | 60.8047 | -121.5729
104.25 | 121.6507 | -60.6995 | 60.7315 | -0.00099167 | 0.002619 | 0.071421 | 0.0036294 | 0.063429 | 0.0026446 | -0.0012346 | -0.00068649 | 0.002337 | 0.064029 | 0.066796 | -0.0059943 | -0.0072375 | 60.6125 | -60.5209 | 0.050354 | -60.7361 | 60.7544 | -60.7315 | -60.704 | -61.0519 | 0.073242 | -60.9924 | 60.6537 | 60.6583 | -60.6537 | -60.8643 | -0.032043 | -0.004578 | 0.022889 | 0.17853 | -0.036621 | -0.032043 | -0.11902 | 0.045776 | -0.16479 | -0.077819 | -0.35248 | -0.29297 | -0.12817 | -0.073242 | 121.4539 | 121.312 | 60.7498 | -121.4355 | 121.3531 | 121.3577 | 60.7727 | -121.5958
105.9844 | 121.6232 | -60.6857 | 60.7315 | 0.0066373 | 5.5572e-05 | 0.070353 | 0.0036294 | 0.064497 | -0.002055 | -0.00273 | -0.00068649 | 0.0019098 | 0.063388 | 0.067437 | -0.011549 | -0.0051013 | 60.5713 | -60.5667 | 0.018311 | -60.791 | 60.7269 | -60.7636 | -60.704 | -61.1252 | 0.032043 | -61.0519 | 60.6857 | 60.6903 | -60.6812 | -60.8459 | -0.07782 | -0.018311 | -0.004577 | 0.11902 | -0.10529 | -0.086975 | -0.16022 | 0.004578 | -0.16022 | -0.045776 | -0.43945 | -0.36621 | -0.20599 | -0.041198 | 121.4127 | 121.257 | 60.704 | -121.4355 | 121.3715 | 121.376 | 60.7178 | -121.5775
107.7188 | 121.6415 | -60.7086 | 60.7224 | 0.0066373 | 0.0034736 | 0.067148 | 0.0046976 | 0.065779 | 0.003072 | -0.0029436 | 0.0069425 | 0.0014826 | 0.066166 | 0.067009 | -0.0081305 | -0.0053149 | 60.6171 | -60.5164 | 0.059509 | -60.7224 | 60.7727 | -60.7315 | -60.7178 | -61.0382 | 0.086975 | -60.9787 | 60.6216 | 60.672 | -60.6354 | -60.8597 | -0.022888 | -0.009155 | 0.050354 | 0.19226 | -0.013733 | -0.004578 | -0.10529 | 0.073242 | -0.15106 | -0.10071 | -0.32959 | -0.27008 | -0.11902 | -0.050354 | 121.4813 | 121.3257 | 60.7681 | -121.4401 | 121.3303 | 121.3806 | 60.7956 | -121.582
109.4531 | 121.6232 | -60.6903 | 60.7178 | 0.0066373 | 0.0019782 | 0.069712 | 0.0029886 | 0.06642 | 0.00072196 | -0.0029436 | -0.00068649 | 0.0016962 | 0.062534 | 0.066155 | -0.0074897 | -0.0044605 | 60.6171 | -60.5026 | 0.082397 | -60.7315 | 60.7407 | -60.7361 | -60.7086 | -61.0428 | 0.09613 | -60.9879 | 60.6445 | 60.672 | -60.6766 | -60.8368 | -0.045776 | -0.01831 | 0.022889 | 0.18768 | -0.041198 | -0.022888 | -0.10071 | 0.013733 | -0.14648 | -0.073242 | -0.35248 | -0.29755 | -0.15106 | -0.045776 | 121.431 | 121.3074 | 60.7727 | -121.4264 | 121.3348 | 121.3623 | 60.7864 | -121.5546
111.125 | 121.5179 | -60.7819 | 60.6995 | 0.0066373 | 0.009455 | 0.07078 | 0.0019204 | 0.065565 | -0.0044048 | -0.001662 | 0.022202 | -0.0036444 | 0.065097 | 0.065087 | -0.010053 | -0.0059557 | 60.6216 | -60.466 | 0.07782 | -60.7498 | 60.64 | -60.7498 | -60.704 | -61.0382 | 0.09613 | -60.9329 | 60.553 | 60.5896 | -60.6812 | -60.8688 | 0.032043 | 0.077819 | -0.059509 | 0.31586 | 0.032043 | -0.045776 | -0.07782 | 0.10071 | -0.086975 | -0.14648 | -0.25635 | -0.15106 | -0.064087 | -0.10986 | 121.4218 | 121.4035 | 60.8597 | -121.4035 | 121.3348 | 121.3715 | 60.878 | -121.5683
112.8594 | 121.6415 | -60.7315 | 60.6903 | 0.014267 | 0.0030464 | 0.071634 | 0.0051248 | 0.06407 | -0.005473 | -0.0052936 | 0.014572 | -0.00044004 | 0.063388 | 0.065514 | -0.013685 | -0.0025379 | 60.6262 | -60.4294 | 0.11444 | -60.7269 | 60.6628 | -60.7269 | -60.7178 | -61.0336 | 0.16022 | -60.9283 | 60.5576 | 60.5942 | -60.6674 | -60.8459 | 0.004577 | 0.013733 | -0.027466 | 0.30212 | 0.004577 | -0.009156 | -0.064087 | 0.064087 | -0.11444 | -0.13275 | -0.30212 | -0.19684 | -0.082398 | -0.096131 | 121.3943 | 121.3577 | 60.8459 | -121.4081 | 121.2891 | 121.3257 | 60.8917 | -121.5363
114.5781 | 121.6507 | -60.6857 | 60.6995 | 0.0066373 | 0.0017646 | 0.068003 | 0.005552 | 0.063429 | 0.0028584 | -0.0025164 | 0.0069425 | 0.002978 | 0.064029 | 0.067223 | -0.0098395 | -0.0080921 | 60.64 | -60.5301 | 0.059509 | -60.7132 | 60.7498 | -60.7407 | -60.6995 | -61.0428 | 0.073242 | -60.9787 | 60.6445 | 60.6674 | -60.6628 | -60.8643 | -0.054932 | -0.013733 | 0.050354 | 0.15564 | -0.027466 | -0.013733 | -0.059509 | 0.022888 | -0.17853 | -0.054932 | -0.35706 | -0.29297 | -0.11444 | -0.032044 | 121.4355 | 121.3257 | 60.7452 | -121.3989 | 121.3303 | 121.3531 | 60.759 | -121.5637
116.2969 | 121.55 | -60.7727 | 60.704 | 0.014267 | 0.0086006 | 0.070993 | 0.001066 | 0.065992 | -0.0029094 | 0.00026056 | 0.014572 | -0.0019354 | 0.060825 | 0.065941 | -0.0083441 | -0.0055285 | 60.6354 | -60.4797 | 0.050354 | -60.7361 | 60.6445 | -60.7498 | -60.704 | -61.0291 | 0.059509 | -60.9558 | 60.553 | 60.5759 | -60.672 | -60.8459 | 0.022888 | 0.068664 | -0.05951 | 0.29297 | 0.036621 | -0.032043 | -0.068665 | 0.10071 | -0.073242 | -0.15106 | -0.25635 | -0.18311 | -0.10986 | -0.12817 | 121.4172 | 121.4081 | 60.8231 | -121.4081 | 121.3257 | 121.3486 | 60.8322 | -121.55
118.0312 | 121.6003 | -60.7315 | 60.7132 | 0.0066373 | -0.00015803 | 0.071848 | 0.0074746 | 0.066206 | -0.0016278 | -0.0042254 | 0.022202 | 0.00062796 | 0.064243 | 0.064019 | -0.010267 | -0.0048877 | 60.5484 | -60.5713 | 0.032043 | -60.7773 | 60.7361 | -60.759 | -60.7178 | -61.116 | 0.032043 | -61.0382 | 60.6537 | 60.6995 | -60.6857 | -60.8826 | -0.027466 | 0.013733 | 0.022888 | 0.16022 | -0.045777 | -0.05951 | -0.1648 | 0.045776 | -0.15106 | -0.059509 | -0.38452 | -0.3067 | -0.15564 | -0.013733 | 121.4676 | 121.2799 | 60.7635 | -121.431 | 121.3852 | 121.431 | 60.7635 | -121.5958
119.7031 | 121.5591 | -60.759 | 60.672 | -0.00099167 | 0.0068916 | 0.070353 | 0.0017068 | 0.06642 | -0.0012006 | -0.0020892 | 0.0069425 | -0.00065364 | 0.063816 | 0.065728 | -0.0094123 | -0.0046741 | 60.5988 | -60.5164 | 0.013733 | -60.7452 | 60.6857 | -60.7407 | -60.7086 | -61.0153 | 0.045776 | -60.9695 | 60.5438 | 60.6125 | -60.6674 | -60.8459 | 0.01831 | 0.050354 | 0.013733 | 0.24262 | 0.013733 | -0.036621 | -0.073242 | 0.091553 | -0.086975 | -0.12817 | -0.25635 | -0.21057 | -0.1236 | -0.059509 | 121.4447 | 121.3577 | 60.7727 | -121.3806 | 121.3028 | 121.3715 | 60.8047 | -121.5179
121.4219 | 121.5454 | -60.759 | 60.6857 | 0.014267 | 0.0062506 | 0.069925 | 0.0019204 | 0.06407 | 0.00072196 | -0.00016664 | 0.0069425 | 0.0027644 | 0.064029 | 0.064446 | -0.0055671 | -0.0027515 | 60.5804 | -60.5942 | -0.036621 | -60.7956 | 60.7269 | -60.7407 | -60.7132 | -61.1023 | -0.054932 | -61.0565 | 60.6354 | 60.6628 | -60.6903 | -60.8597 | 0.01831 | 0.045776 | 0.041199 | 0.16479 | -0.036621 | -0.082397 | -0.10529 | 0.068664 | -0.10071 | -0.050354 | -0.34332 | -0.29755 | -0.19684 | -0.022888 | 121.4859 | 121.3394 | 60.7224 | -121.3989 | 121.3943 | 121.4218 | 60.704 | -121.5454
123.0938 | 121.5088 | -60.759 | 60.7407 | -0.00099167 | 0.0051826 | 0.067148 | 0.00085245 | 0.065351 | 0.002431 | -0.001021 | 0.0069425 | 0.002337 | 0.06702 | 0.066155 | -0.0074897 | -0.0040331 | 60.5942 | -60.5438 | 0.041199 | -60.7407 | 60.7224 | -60.7361 | -60.704 | -61.0886 | 0 | -61.0519 | 60.6216 | 60.6949 | -60.6354 | -60.878 | 0.022888 | 0.054931 | -0.018311 | 0.21515 | 0.01831 | -0.036621 | -0.14648 | 0.1236 | -0.11902 | -0.11902 | -0.32959 | -0.29297 | -0.17395 | -0.045777 | 121.4813 | 121.3531 | 60.8002 | -121.4447 | 121.3806 | 121.4539 | 60.759 | -121.6187
124.8125 | 121.5134 | -60.7498 | 60.7086 | -0.00099167 | 0.0062506 | 0.070993 | 0.0014932 | 0.064283 | 0.0020038 | -0.001021 | 0.0069425 | 0.0034052 | 0.065952 | 0.065728 | -0.0068487 | -0.0036059 | 60.5347 | -60.5988 | -0.036621 | -60.8047 | 60.7361 | -60.7544 | -60.7315 | -61.1069 | -0.032043 | -61.0565 | 60.6491 | 60.6537 | -60.6903 | -60.8871 | -0.004578 | 0.018311 | 0.027466 | 0.15106 | -0.054932 | -0.073243 | -0.17395 | 0.059509 | -0.13733 | -0.059509 | -0.35706 | -0.3067 | -0.16937 | -0.054931 | 121.4859 | 121.2845 | 60.7132 | -121.4401 | 121.3989 | 121.4035 | 60.7178 | -121.5958
126.5312 | 121.5729 | -60.7773 | 60.704 | -0.0086212 | 0.0062506 | 0.070353 | 0.0044838 | 0.064924 | -0.0018414 | -0.0014484 | -0.00068649 | 0.0027644 | 0.064457 | 0.066155 | -0.0087713 | -0.0057421 | 60.5988 | -60.5072 | 0.022888 | -60.7498 | 60.6583 | -60.7544 | -60.704 | -61.0428 | 0.054932 | -60.9467 | 60.5667 | 60.6125 | -60.672 | -60.8322 | 0.022888 | 0.073242 | -0.045777 | 0.27008 | 0.027466 | -0.045776 | -0.10529 | 0.10529 | -0.054931 | -0.13733 | -0.2655 | -0.16937 | -0.11444 | -0.091553 | 121.4355 | 121.376 | 60.8002 | -121.4081 | 121.344 | 121.3898 | 60.8322 | -121.5363
128.2031 | 121.5546 | -60.7498 | 60.6995 | 0.0066373 | 0.0075324 | 0.070353 | -0.00021575 | 0.065779 | -0.0022686 | -0.0023028 | -0.00068649 | 0.0016962 | 0.064457 | 0.066582 | -0.01048 | -0.0044605 | 60.6216 | -60.4935 | 0.064087 | -60.7269 | 60.6583 | -60.7498 | -60.7086 | -61.0153 | 0.059509 | -60.9604 | 60.5667 | 60.6216 | -60.6674 | -60.8597 | 0 | 0.041199 | -0.041199 | 0.25635 | 0.022888 | -0.018311 | -0.07782 | 0.082398 | -0.10986 | -0.13275 | -0.2655 | -0.21057 | -0.10071 | -0.07782 | 121.4081 | 121.3715 | 60.8139 | -121.4081 | 121.3165 | 121.3715 | 60.8093 | -121.5591
129.9219 | 121.5591 | -60.7315 | 60.6949 | 0.0066373 | 0.0073188 | 0.070566 | 0.002775 | 0.065138 | 8.1158e-05 | -0.0031574 | 0.0069425 | 0.0031916 | 0.062748 | 0.066155 | -0.0091985 | -0.0061695 | 60.5667 | -60.5942 | -0.036621 | -60.791 | 60.7178 | -60.7452 | -60.7132 | -61.0931 | -0.032043 | -61.0382 | 60.5988 | 60.6354 | -60.6674 | -60.8688 | -0.013733 | 0.01831 | 0.022888 | 0.13733 | -0.05951 | -0.07782 | -0.12817 | 0.064087 | -0.13733 | -0.09613 | -0.36163 | -0.3067 | -0.16937 | -0.059509 | 121.4493 | 121.2982 | 60.6949 | -121.4081 | 121.3303 | 121.3669 | 60.6995 | -121.5637
131.5938 | 121.5591 | -60.7498 | 60.672 | 0.014267 | 0.0098822 | 0.069071 | 0.003843 | 0.064711 | -0.0029094 | -0.0012346 | -0.00068649 | 0.00041436 | 0.064884 | 0.0653 | -0.0096259 | -0.0048877 | 60.6308 | -60.466 | 0.045776 | -60.7315 | 60.6491 | -60.7269 | -60.672 | -61.0199 | 0.068665 | -60.9604 | 60.5347 | 60.5804 | -60.672 | -60.8688 | 0.022888 | 0.07782 | -0.022888 | 0.28381 | 0.018311 | -0.059509 | -0.041199 | 0.07782 | -0.11902 | -0.13733 | -0.27008 | -0.21057 | -0.091553 | -0.091553 | 121.3989 | 121.3806 | 60.7956 | -121.344 | 121.2845 | 121.3303 | 60.8185 | -121.5408
133.3281 | 121.6187 | -60.7178 | 60.6857 | 0.0066373 | 0.0071052 | 0.070353 | 0.0070474 | 0.066206 | -0.0044048 | -0.004439 | -0.00068649 | -0.002149 | 0.06467 | 0.063805 | -0.012189 | -0.0046741 | 60.6216 | -60.4614 | 0.10986 | -60.7269 | 60.6537 | -60.7452 | -60.6949 | -61.0474 | 0.17395 | -60.9238 | 60.5759 | 60.6171 | -60.672 | -60.8734 | -0.027466 | 0.022888 | -0.032043 | 0.25635 | -0.009156 | -0.032044 | -0.064087 | 0.045776 | -0.15564 | -0.10986 | -0.32959 | -0.20599 | -0.050354 | -0.068665 | 121.3715 | 121.3394 | 60.8276 | -121.3806 | 121.2936 | 121.3348 | 60.8917 | -121.5591
135.0625 | 121.6232 | -60.7544 | 60.6812 | 0.0066373 | 0.0086006 | 0.072062 | 0.0059792 | 0.065992 | -0.0056866 | -0.0055072 | 0.0069425 | -0.0027898 | 0.062534 | 0.065087 | -0.012617 | -0.0059557 | 60.5576 | -60.5484 | 0.004578 | -60.7819 | 60.6674 | -60.759 | -60.7224 | -61.084 | 0.07782 | -60.9695 | 60.5942 | 60.6033 | -60.6766 | -60.8917 | -0.004577 | 0.032044 | -0.013733 | 0.20599 | -0.027465 | -0.059509 | -0.1236 | 0.07782 | -0.13733 | -0.086975 | -0.32959 | -0.21515 | -0.077819 | -0.077819 | 121.4218 | 121.312 | 60.759 | -121.4035 | 121.3486 | 121.3577 | 60.8322 | -121.5729
136.7812 | 121.5134 | -60.7773 | 60.7178 | -0.00099167 | 0.0079596 | 0.072489 | 0.002775 | 0.065992 | -0.0026958 | -0.0035846 | -0.00068649 | 0.00084176 | 0.062107 | 0.064873 | -0.0094123 | -0.0055285 | 60.5942 | -60.5209 | 0.004578 | -60.7773 | 60.672 | -60.7407 | -60.7224 | -61.0886 | 0.027466 | -61.0062 | 60.5667 | 60.585 | -60.672 | -60.8826 | 0.036621 | 0.054932 | -0.045776 | 0.25635 | 0 | -0.054932 | -0.1236 | 0.10529 | -0.10529 | -0.15106 | -0.31128 | -0.22888 | -0.1236 | -0.13275 | 121.4493 | 121.3715 | 60.7819 | -121.4401 | 121.344 | 121.3623 | 60.8047 | -121.6003
138.5156 | 121.6599 | -60.7086 | 60.6903 | -0.00099167 | 0.002619 | 0.071421 | 0.0057656 | 0.064924 | 0.0017902 | -0.0025164 | -0.00068649 | 0.0038324 | 0.065097 | 0.066796 | -0.0087713 | -0.0065967 | 60.5896 | -60.5621 | 0.013733 | -60.7727 | 60.7269 | -60.7681 | -60.7178 | -61.0794 | 0.036621 | -61.0382 | 60.6628 | 60.6812 | -60.6857 | -60.8551 | -0.059509 | -0.009155 | 0.036621 | 0.14648 | -0.064087 | -0.054932 | -0.10071 | 0.022888 | -0.14648 | -0.027466 | -0.37079 | -0.32959 | -0.1831 | -0.009156 | 121.4355 | 121.2982 | 60.7224 | -121.4081 | 121.3715 | 121.3898 | 60.7452 | -121.5454
140.1875 | 121.5042 | -60.7819 | 60.7315 | 0.0066373 | 0.0083868 | 0.072489 | 0.0034158 | 0.064924 | -0.0022686 | -0.0020892 | 0.022202 | -0.002149 | 0.062961 | 0.064232 | -0.0083441 | -0.0048877 | 60.6354 | -60.4706 | 0.059509 | -60.7544 | 60.6354 | -60.7407 | -60.7086 | -61.0245 | 0.059509 | -60.9695 | 60.5576 | 60.5621 | -60.6903 | -60.878 | 0.041198 | 0.073242 | -0.09613 | 0.31128 | 0.027465 | -0.045777 | -0.09613 | 0.091552 | -0.096131 | -0.17395 | -0.24262 | -0.18768 | -0.091552 | -0.16937 | 121.4172 | 121.4172 | 60.8414 | -121.4401 | 121.3394 | 121.344 | 60.8414 | -121.6095
141.9219 | 121.5134 | -60.7727 | 60.6766 | 0.0066373 | 0.007746 | 0.073557 | 0.0034158 | 0.06172 | -0.0029094 | -0.0037982 | -0.008316 | -1.2844e-05 | 0.062961 | 0.063378 | -0.0098395 | -0.0040331 | 60.6033 | -60.5072 | 0.032043 | -60.7773 | 60.6445 | -60.7681 | -60.7178 | -61.0794 | 0.027466 | -60.9833 | 60.5576 | 60.5804 | -60.6903 | -60.878 | 0.004578 | 0.054932 | -0.032044 | 0.2655 | -0.004578 | -0.05951 | -0.073242 | 0.082397 | -0.10529 | -0.11902 | -0.3067 | -0.21057 | -0.10528 | -0.096131 | 121.4172 | 121.376 | 60.8047 | -121.3943 | 121.3303 | 121.3531 | 60.8002 | -121.5546
143.6719 | 121.6141 | -60.6949 | 60.6995 | 0.014267 | 0.0058234 | 0.071848 | 0.0076882 | 0.063643 | -0.00098684 | -0.00080744 | 0.014572 | 0.00020076 | 0.063816 | 0.0653 | -0.010053 | -0.0057421 | 60.64 | -60.466 | 0.1236 | -60.7086 | 60.64 | -60.7407 | -60.7132 | -61.0291 | 0.13733 | -60.9512 | 60.5759 | 60.6171 | -60.6537 | -60.8551 | -0.045777 | -0.018311 | -0.059509 | 0.22888 | -0.013733 | 0.004578 | -0.059509 | 0.041198 | -0.16022 | -0.1236 | -0.33417 | -0.25635 | -0.09613 | -0.082398 | 121.3348 | 121.3348 | 60.8185 | -121.4127 | 121.2708 | 121.3119 | 60.8322 | -121.5546
145.3594 | 121.637 | -60.6674 | 60.7315 | 0.021896 | 0.0036872 | 0.068003 | 0.0034158 | 0.063215 | 0.0045674 | -0.0018756 | 0.0069425 | 0.002978 | 0.06467 | 0.0653 | -0.0085577 | -0.0057421 | 60.6445 | -60.5164 | 0.073242 | -60.7315 | 60.759 | -60.7315 | -60.7269 | -61.0153 | 0.082397 | -60.9741 | 60.6445 | 60.6628 | -60.6766 | -60.8276 | -0.064087 | -0.05951 | 0.027466 | 0.15106 | -0.064087 | -0.004577 | -0.086975 | -0.009156 | -0.16022 | -0.086975 | -0.3479 | -0.3067 | -0.14648 | -0.068664 | 121.4264 | 121.3119 | 60.7407 | -121.4584 | 121.3119 | 121.3303 | 60.7498 | -121.5591
147.0156 | 121.5088 | -60.791 | 60.7086 | 0.0066373 | 0.011805 | 0.072489 | 0.002775 | 0.06407 | -0.0026958 | -0.0020892 | 0.0069425 | -0.00044004 | 0.064029 | 0.065087 | -0.0085577 | -0.0033923 | 60.6262 | -60.4614 | 0.064087 | -60.7361 | 60.6308 | -60.7498 | -60.704 | -61.0382 | 0.068665 | -60.9787 | 60.5392 | 60.5576 | -60.6995 | -60.8917 | 0.041199 | 0.086975 | -0.07782 | 0.32959 | 0.054932 | -0.032043 | -0.082397 | 0.091553 | -0.10071 | -0.16937 | -0.24719 | -0.18768 | -0.086975 | -0.15106 | 121.4218 | 121.4172 | 60.8551 | -121.4127 | 121.3303 | 121.3486 | 60.8597 | -121.6003
148.7031 | 121.5408 | -60.7315 | 60.7178 | -0.00099167 | 0.00069637 | 0.070993 | 0.0053384 | 0.064711 | 0.0052082 | -0.0025164 | 0.0069425 | 0.004046 | 0.063388 | 0.065941 | -0.0072759 | -0.0074511 | 60.6537 | -60.5072 | 0.050354 | -60.7315 | 60.7132 | -60.7727 | -60.6857 | -61.0336 | 0.041199 | -61.0062 | 60.6262 | 60.6491 | -60.6628 | -60.8597 | -0.041199 | 0.045776 | -0.004577 | 0.2243 | 0 | -0.045776 | -0.064086 | 0.068664 | -0.12817 | -0.091552 | -0.30212 | -0.27466 | -0.14649 | -0.068664 | 121.4447 | 121.3852 | 60.7819 | -121.4035 | 121.3577 | 121.3806 | 60.7727 | -121.5775
150.4219 | 121.5912 | -60.7636 | 60.6903 | 0.0066373 | 0.0096686 | 0.069498 | 0.002775 | 0.065992 | 8.1158e-05 | -0.00080744 | 0.0069425 | 0.00084176 | 0.063175 | 0.064873 | -0.0077033 | -0.0031787 | 60.64 | -60.4752 | 0.059509 | -60.7086 | 60.6491 | -60.7498 | -60.7086 | -61.0107 | 0.07782 | -60.9467 | 60.5392 | 60.5667 | -60.704 | -60.8734 | 0.013733 | 0.054932 | -0.041199 | 0.28839 | 0.054932 | 0 | -0.050354 | 0.059509 | -0.10986 | -0.15106 | -0.24719 | -0.1831 | -0.073242 | -0.1236 | 121.4127 | 121.4035 | 60.8231 | -121.3989 | 121.3028 | 121.3303 | 60.8414 | -121.5637
152.0781 | 121.637 | -60.7361 | 60.6628 | 0.0066373 | 0.0086006 | 0.072275 | 0.0064066 | 0.065351 | -0.0067548 | -0.00016664 | 0.0069425 | -0.0032172 | 0.064243 | 0.060814 | -0.01048 | -0.0046741 | 60.5667 | -60.5072 | 0.045776 | -60.7544 | 60.6674 | -60.7452 | -60.7224 | -61.0748 | 0.11902 | -60.9421 | 60.5621 | 60.5804 | -60.704 | -60.8643 | -0.009155 | 0.013733 | 0.004577 | 0.22888 | -0.018311 | -0.032044 | -0.096131 | 0.032043 | -0.12817 | -0.10071 | -0.33875 | -0.20599 | -0.07782 | -0.082398 | 121.4035 | 121.3028 | 60.7819 | -121.3852 | 121.2982 | 121.3165 | 60.8551 | -121.5271
153.75 | 121.5729 | -60.7498 | 60.7086 | 0.0066373 | 0.0053962 | 0.070993 | 0.00021145 | 0.065351 | 0.0011494 | -0.00059384 | 0.0069425 | 0.0036188 | 0.063816 | 0.065941 | -0.0066351 | -0.0044605 | 60.585 | -60.6033 | -0.041199 | -60.7864 | 60.7315 | -60.7727 | -60.704 | -61.1023 | -0.041199 | -61.0611 | 60.64 | 60.6903 | -60.6812 | -60.8734 | -0.022888 | 0.045776 | 0.022888 | 0.14648 | -0.036621 | -0.082397 | -0.1236 | 0.068665 | -0.1236 | -0.068664 | -0.35248 | -0.31128 | -0.18768 | -0.01831 | 121.4813 | 121.3348 | 60.7086 | -121.4127 | 121.3898 | 121.4401 | 60.7086 | -121.582
155.4688 | 121.6187 | -60.7132 | 60.7269 | 0.0066373 | 0.0021918 | 0.067575 | 0.0044838 | 0.066206 | 0.0017902 | -0.0014484 | 0.014572 | 0.0027644 | 0.065097 | 0.065941 | -0.0085577 | -0.0051013 | 60.6354 | -60.4889 | 0.086975 | -60.7361 | 60.759 | -60.7498 | -60.6995 | -61.0153 | 0.091553 | -60.9741 | 60.6491 | 60.6583 | -60.64 | -60.8597 | -0.036621 | 0.013733 | 0.032043 | 0.2243 | -0.022888 | -0.036621 | -0.091553 | 0.073242 | -0.14648 | -0.07782 | -0.30212 | -0.26092 | -0.11444 | -0.068665 | 121.4722 | 121.3486 | 60.8002 | -121.4264 | 121.3623 | 121.3715 | 60.8047 | -121.5866
157.125 | 121.5591 | -60.7498 | 60.6903 | 0.014267 | 0.0062506 | 0.070353 | 0.0012796 | 0.06407 | -0.00055964 | -0.00016664 | -0.00068649 | 0.00062796 | 0.064029 | 0.0653 | -0.0070623 | -0.0033923 | 60.5576 | -60.5759 | -0.050354 | -60.7956 | 60.7315 | -60.7773 | -60.7407 | -61.0931 | -0.022888 | -61.0199 | 60.6079 | 60.6079 | -60.6903 | -60.8551 | -0.027466 | 0.009155 | 0.041198 | 0.17395 | -0.045776 | -0.054931 | -0.13275 | 0.059509 | -0.10529 | -0.082398 | -0.34332 | -0.27008 | -0.16479 | -0.082398 | 121.4813 | 121.3074 | 60.6995 | -121.431 | 121.3577 | 121.3577 | 60.7269 | -121.5454
159.2812 | 121.6553 | -60.7224 | 60.6537 | 0.014267 | 0.0068916 | 0.074198 | 0.0059792 | 0.064924 | -0.005473 | -0.0025164 | -0.00068649 | -0.0019354 | 0.063602 | 0.066368 | -0.011762 | -0.0046741 | 60.5988 | -60.4614 | 0.068665 | -60.7452 | 60.6583 | -60.7727 | -60.6812 | -61.0474 | 0.13733 | -60.91 | 60.5438 | 60.5942 | -60.672 | -60.8505 | -0.050354 | 0.041199 | 0.004577 | 0.26093 | -0.022888 | -0.064087 | -0.054932 | 0.050354 | -0.12817 | -0.10986 | -0.32501 | -0.18768 | -0.059509 | -0.05951 | 121.3806 | 121.3211 | 60.791 | -121.3348 | 121.2662 | 121.3165 | 60.8597 | -121.5042
161.1719 | 121.6095 | -60.704 | 60.7178 | 0.014267 | 0.002619 | 0.069712 | 0.0042702 | 0.069197 | 0.002431 | -0.00038024 | 0.0069425 | 0.0034052 | 0.064457 | 0.066796 | -0.0070623 | -0.0063831 | 60.6537 | -60.4797 | 0.091553 | -60.7269 | 60.759 | -60.7224 | -60.6857 | -61.0199 | 0.07782 | -60.9879 | 60.6445 | 60.6537 | -60.6445 | -60.8459 | -0.01831 | 0.018311 | 0.041199 | 0.2243 | -0.022888 | -0.041199 | -0.064086 | 0.05951 | -0.14191 | -0.073242 | -0.31586 | -0.28381 | -0.14191 | -0.064086 | 121.463 | 121.3577 | 60.7956 | -121.4035 | 121.3486 | 121.3577 | 60.7819 | -121.5637
162.8906 | 121.5729 | -60.7498 | 60.6903 | 0.0066373 | 0.006037 | 0.070353 | 0.0051248 | 0.065992 | -0.0073956 | -0.001662 | -0.00068649 | -0.0027898 | 0.064884 | 0.063378 | -0.012403 | -0.0038195 | 60.5347 | -60.5484 | -0.004578 | -60.7819 | 60.6583 | -60.7864 | -60.7086 | -61.1023 | 0.054932 | -60.9787 | 60.5759 | 60.585 | -60.6766 | -60.878 | -0.036621 | 0.041199 | -0.032044 | 0.20142 | -0.032043 | -0.073242 | -0.15564 | 0.073242 | -0.12817 | -0.11444 | -0.35248 | -0.22888 | -0.10071 | -0.10529 | 121.4081 | 121.2845 | 60.7452 | -121.3989 | 121.3257 | 121.3348 | 60.8047 | -121.5683
164.5469 | 121.6415 | -60.6812 | 60.6903 | -0.00099167 | 0.00048277 | 0.068216 | 0.005552 | 0.06407 | -0.00077324 | -0.00273 | 0.0069425 | 0.004687 | 0.065311 | 0.066368 | -0.011121 | -0.0053149 | 60.5759 | -60.5576 | 0.013733 | -60.7727 | 60.7178 | -60.7727 | -60.7361 | -61.0748 | 0.068665 | -61.0245 | 60.6537 | 60.672 | -60.6537 | -60.8505 | -0.091553 | -0.054932 | 0.027465 | 0.1236 | -0.091553 | -0.036621 | -0.11444 | 0.027465 | -0.16937 | -0.036621 | -0.39368 | -0.34332 | -0.17395 | -0.018311 | 121.3989 | 121.257 | 60.6949 | -121.4264 | 121.3348 | 121.3531 | 60.7498 | -121.5408
166.2344 | 121.5225 | -60.7727 | 60.6949 | -0.00099167 | 0.0068916 | 0.069712 | 0.0040566 | 0.065351 | -0.003764 | -0.0052936 | 0.0069425 | -0.0023626 | 0.064029 | 0.063378 | -0.011335 | -0.0036059 | 60.553 | -60.5347 | 0.013733 | -60.7773 | 60.6537 | -60.7544 | -60.6995 | -61.1023 | 0.036621 | -61.0062 | 60.5438 | 60.5988 | -60.6903 | -60.8597 | 0.01831 | 0.073242 | -0.041198 | 0.23804 | -0.004578 | -0.07782 | -0.14191 | 0.082397 | -0.086975 | -0.15106 | -0.32959 | -0.23346 | -0.14649 | -0.09613 | 121.4264 | 121.3257 | 60.7864 | -121.3943 | 121.3165 | 121.3715 | 60.8093 | -121.5546
167.9062 | 121.6187 | -60.6949 | 60.7086 | 0.021896 | 0.0045416 | 0.070993 | 0.005552 | 0.065565 | -0.0026958 | -0.001662 | -0.008316 | 0.002337 | 0.06467 | 0.064232 | -0.0083441 | -0.0038195 | 60.5804 | -60.5484 | 0.022888 | -60.7773 | 60.7132 | -60.7773 | -60.7086 | -61.0931 | 0.050354 | -61.0291 | 60.6491 | 60.6903 | -60.672 | -60.8551 | -0.082398 | -0.013733 | 0.004578 | 0.14648 | -0.082398 | -0.068665 | -0.12817 | 0.022888 | -0.16022 | -0.059509 | -0.39825 | -0.33417 | -0.17395 | -0.01831 | 121.4081 | 121.2753 | 60.7178 | -121.4172 | 121.344 | 121.3852 | 60.7452 | -121.5637
169.5781 | 121.6553 | -60.6766 | 60.7178 | 0.0066373 | 0.0056098 | 0.069498 | 0.0044838 | 0.06642 | 0.0011494 | -0.0018756 | 0.0069425 | 0.0025508 | 0.063388 | 0.064446 | -0.0066351 | -0.0051013 | 60.5804 | -60.553 | 0.022888 | -60.759 | 60.7407 | -60.791 | -60.704 | -61.0703 | 0.068665 | -61.0016 | 60.6583 | 60.6812 | -60.6445 | -60.8688 | -0.11444 | -0.027466 | 0.022889 | 0.1236 | -0.082397 | -0.054931 | -0.13733 | 0.032044 | -0.19226 | -0.059509 | -0.39368 | -0.32501 | -0.13275 | -0.036621 | 121.4172 | 121.257 | 60.6995 | -121.4218 | 121.3348 | 121.3577 | 60.7452 | -121.5866
171.25 | 121.5363 | -60.7636 | 60.7498 | 0.0066373 | 0.0056098 | 0.069284 | 0.00021145 | 0.066633 | 0.0032856 | -0.0018756 | -0.00068649 | 0.0034052 | 0.063602 | 0.066155 | -0.0051397 | -0.0023241 | 60.5621 | -60.5942 | -0.013733 | -60.7773 | 60.7315 | -60.759 | -60.7132 | -61.0886 | -0.050354 | -61.0565 | 60.6583 | 60.672 | -60.6628 | -60.878 | 0.004578 | 0.050354 | -0.018311 | 0.16937 | -0.013733 | -0.064087 | -0.18768 | 0.10071 | -0.11444 | -0.091553 | -0.32501 | -0.29297 | -0.17853 | -0.07782 | 121.4951 | 121.3257 | 60.7498 | -121.463 | 121.4218 | 121.4355 | 60.7132 | -121.6278
172.9219 | 121.6141 | -60.7269 | 60.6491 | 0.0066373 | 0.0071052 | 0.06843 | 0.0046976 | 0.065351 | -0.006541 | -0.0012346 | 0.014572 | -0.0017218 | 0.065097 | 0.065728 | -0.010694 | -0.0031787 | 60.553 | -60.5209 | 0.032043 | -60.7498 | 60.6537 | -60.759 | -60.704 | -61.0703 | 0.091553 | -60.9558 | 60.5576 | 60.6125 | -60.6674 | -60.8643 | -0.032043 | 0.022888 | 0.004578 | 0.20599 | -0.022888 | -0.045776 | -0.09613 | 0.05951 | -0.13733 | -0.091553 | -0.34332 | -0.22888 | -0.091553 | -0.036621 | 121.3806 | 121.2799 | 60.759 | -121.3531 | 121.2845 | 121.3394 | 60.8185 | -121.5134
174.625 | 121.5729 | -60.759 | 60.6903 | -0.00099167 | 0.0081732 | 0.070139 | 0.0025612 | 0.067274 | -0.00013244 | -0.0014484 | 0.0069425 | 0.0014826 | 0.062748 | 0.063164 | -0.0051397 | -0.0065967 | 60.5942 | -60.5438 | -0.004578 | -60.7773 | 60.6949 | -60.7361 | -60.6995 | -61.0291 | 0.027466 | -60.9558 | 60.6033 | 60.5988 | -60.672 | -60.8414 | 0.022888 | 0.059509 | 0.004577 | 0.21515 | -0.018311 | -0.07782 | -0.096131 | 0.086975 | -0.082398 | -0.086975 | -0.27008 | -0.19684 | -0.11444 | -0.091553 | 121.4539 | 121.3531 | 60.7544 | -121.3898 | 121.3623 | 121.3577 | 60.7864 | -121.5317
176.2812 | 121.582 | -60.672 | 60.6995 | -0.00099167 | 0.0024054 | 0.069712 | 0.005552 | 0.068556 | -0.003764 | -0.0042254 | -0.00068649 | 0.001269 | 0.06467 | 0.068505 | -0.010694 | -0.0051013 | 60.6125 | -60.4843 | 0.091553 | -60.7224 | 60.6949 | -60.7361 | -60.6949 | -61.0748 | 0.09613 | -60.9787 | 60.6308 | 60.6262 | -60.672 | -60.8643 | -0.064087 | -0.022888 | -0.004578 | 0.18768 | -0.050354 | -0.027466 | -0.086975 | 0 | -0.19226 | -0.068665 | -0.40283 | -0.3067 | -0.11444 | -0.073242 | 121.3669 | 121.2845 | 60.7635 | -121.3943 | 121.3028 | 121.2982 | 60.7681 | -121.5637
177.9375 | 121.5591 | -60.7636 | 60.7315 | 0.0066373 | 0.0047552 | 0.068644 | 0.003843 | 0.064283 | 0.002431 | -0.001021 | 0.0069425 | 0.002337 | 0.064457 | 0.069145 | -0.0074897 | -0.0044605 | 60.5667 | -60.5896 | -0.032043 | -60.7727 | 60.7544 | -60.7407 | -60.6995 | -61.0931 | -0.054932 | -61.0565 | 60.6583 | 60.6674 | -60.6674 | -60.8688 | 0.022888 | 0.064087 | 0.022889 | 0.17395 | -0.009155 | -0.073242 | -0.1648 | 0.096131 | -0.10528 | -0.073242 | -0.32959 | -0.29297 | -0.18768 | -0.064087 | 121.5179 | 121.3303 | 60.7315 | -121.431 | 121.4218 | 121.431 | 60.7086 | -121.6003
179.5938 | 121.6324 | -60.6949 | 60.7178 | 0.0066373 | 0.00026917 | 0.07078 | 0.0057656 | 0.064283 | -0.00055964 | -0.0031574 | -0.00068649 | 0.0014826 | 0.064457 | 0.065087 | -0.01048 | -0.0033923 | 60.5484 | -60.5576 | 0.013733 | -60.7773 | 60.7132 | -60.7636 | -60.6949 | -61.1069 | 0.036621 | -61.0291 | 60.64 | 60.6949 | -60.672 | -60.9055 | -0.068665 | 0 | -0.004577 | 0.13733 | -0.082398 | -0.082398 | -0.16937 | 0.022888 | -0.21057 | -0.077819 | -0.41199 | -0.33417 | -0.1236 | -0.022888 | 121.4081 | 121.2433 | 60.7086 | -121.4127 | 121.3348 | 121.3898 | 60.7315 | -121.6232
181.25 | 121.6553 | -60.6949 | 60.7132 | 0.0066373 | 0.0013374 | 0.069284 | 0.0057656 | 0.06706 | -0.00034604 | -0.001662 | -0.008316 | 0.002337 | 0.065738 | 0.065087 | -0.0081305 | -0.0059557 | 60.5759 | -60.5576 | 0.027466 | -60.7544 | 60.7361 | -60.7315 | -60.6949 | -61.0474 | 0.073242 | -60.9833 | 60.672 | 60.6583 | -60.6491 | -60.8551 | -0.036621 | 0 | 0.022888 | 0.13733 | -0.05951 | -0.05951 | -0.13733 | 0.045776 | -0.16022 | -0.041199 | -0.35248 | -0.28839 | -0.12817 | -0.054932 | 121.431 | 121.2708 | 60.7224 | -121.4081 | 121.3669 | 121.3531 | 60.7681 | -121.5683
182.9062 | 121.5637 | -60.7361 | 60.6857 | 0.014267 | 0.0090278 | 0.070993 | 0.0034158 | 0.064924 | 0.00072196 | -0.00038024 | -0.00068649 | -0.00086724 | 0.062961 | 0.0653 | -0.0064215 | -0.0040331 | 60.5713 | -60.5164 | -0.013733 | -60.759 | 60.6583 | -60.7452 | -60.7224 | -61.0382 | 0.045776 | -60.965 | 60.5484 | 60.5804 | -60.672 | -60.8597 | -0.009155 | 0.013733 | -0.027466 | 0.21973 | -0.022888 | -0.036621 | -0.11444 | 0.064087 | -0.1236 | -0.13733 | -0.30212 | -0.22888 | -0.10529 | -0.10529 | 121.3943 | 121.3074 | 60.7224 | -121.4081 | 121.2845 | 121.3165 | 60.7819 | -121.5454
184.5625 | 121.582 | -60.6995 | 60.7086 | -0.00099167 | 0.0024054 | 0.070566 | 0.0076882 | 0.064283 | -0.00077324 | -0.00080744 | 0.0069425 | 0.001269 | 0.066166 | 0.066796 | -0.011549 | -0.0057421 | 60.5484 | -60.5347 | 0.027466 | -60.7864 | 60.7086 | -60.7544 | -60.7269 | -61.1069 | 0.054932 | -60.997 | 60.6583 | 60.6674 | -60.6857 | -60.8414 | -0.054932 | -0.027466 | 0 | 0.16479 | -0.086975 | -0.059509 | -0.16022 | 0.013733 | -0.14191 | -0.050354 | -0.40741 | -0.29755 | -0.15564 | -0.041199 | 121.4081 | 121.2479 | 60.7269 | -121.4355 | 121.3577 | 121.3669 | 60.7544 | -121.55
186.2656 | 121.5546 | -60.7544 | 60.7224 | -0.0086212 | 0.0083868 | 0.070139 | -0.00021575 | 0.065351 | -0.00098684 | -0.0023028 | 0.0069425 | 0.001269 | 0.063816 | 0.066796 | -0.0081305 | -0.0048877 | 60.5896 | -60.5026 | 0.022888 | -60.7498 | 60.6903 | -60.7452 | -60.7086 | -61.0245 | 0.059509 | -60.9467 | 60.5621 | 60.5896 | -60.6674 | -60.8505 | 0.009156 | 0.045777 | -0.032043 | 0.25177 | 0.004578 | -0.041199 | -0.13275 | 0.086976 | -0.09613 | -0.16022 | -0.27008 | -0.19226 | -0.09613 | -0.13275 | 121.4447 | 121.344 | 60.7773 | -121.431 | 121.3165 | 121.344 | 60.8139 | -121.5729
187.9531 | 121.6415 | -60.7178 | 60.672 | -0.00099167 | 0.0073188 | 0.072062 | 0.0081154 | 0.063002 | -0.0078228 | -0.001021 | -0.008316 | -0.00044004 | 0.064884 | 0.063805 | -0.01283 | -0.0051013 | 60.5942 | -60.4568 | 0.082397 | -60.7315 | 60.64 | -60.7544 | -60.7086 | -61.0245 | 0.13275 | -60.8826 | 60.5164 | 60.5896 | -60.6674 | -60.8688 | -0.036622 | 0.009155 | -0.032043 | 0.26093 | -0.013733 | -0.022888 | -0.07782 | 0.050354 | -0.15106 | -0.15564 | -0.3067 | -0.16479 | -0.013733 | -0.082397 | 121.3577 | 121.3119 | 60.8002 | -121.3806 | 121.2341 | 121.3074 | 60.8505 | -121.5408
189.6094 | 121.5134 | -60.7361 | 60.7407 | -0.016251 | 0.0030464 | 0.065866 | 0.0053384 | 0.065992 | 0.0011494 | -0.004439 | -0.00068649 | 0.0055414 | 0.06702 | 0.068718 | -0.0091985 | -0.0057421 | 60.5576 | -60.6262 | -0.022888 | -60.7819 | 60.7407 | -60.7544 | -60.6766 | -61.0886 | -0.045776 | -61.0519 | 60.6491 | 60.6674 | -60.6674 | -60.8414 | -0.018311 | 0.059509 | 0 | 0.10986 | -0.045776 | -0.10529 | -0.18311 | 0.068665 | -0.10529 | -0.091553 | -0.35248 | -0.31586 | -0.21057 | -0.073243 | 121.4767 | 121.2936 | 60.7132 | -121.4172 | 121.3852 | 121.4035 | 60.6903 | -121.582
191.3125 | 121.6003 | -60.7407 | 60.6445 | -0.00099167 | 0.0036872 | 0.071848 | 0.0053384 | 0.063429 | -0.0039776 | -0.0037982 | 0.0069425 | -0.0012946 | 0.061893 | 0.066796 | -0.011121 | -0.0051013 | 60.6033 | -60.4202 | 0.10529 | -60.7178 | 60.6674 | -60.7315 | -60.7178 | -61.0107 | 0.17395 | -60.9146 | 60.5621 | 60.585 | -60.6674 | -60.8734 | 0.009156 | 0.022889 | 0.022888 | 0.32044 | 0.022889 | 0 | -0.041198 | 0.073243 | -0.13275 | -0.082397 | -0.27008 | -0.17395 | -0.041199 | -0.059509 | 121.4081 | 121.344 | 60.8459 | -121.3623 | 121.3028 | 121.3257 | 60.9146 | -121.5179
192.9688 | 121.5225 | -60.759 | 60.7132 | 0.014267 | 0.00326 | 0.069712 | 0.0023476 | 0.064283 | 0.0034992 | -0.0014484 | 0.0069425 | 0.0021234 | 0.062961 | 0.067864 | -0.0055671 | -0.0055285 | 60.5484 | -60.5896 | -0.032043 | -60.791 | 60.7636 | -60.7544 | -60.704 | -61.0886 | -0.027466 | -61.0474 | 60.64 | 60.6308 | -60.6628 | -60.8551 | 0.004577 | 0.054931 | 0.050354 | 0.16937 | -0.032044 | -0.086975 | -0.1648 | 0.09613 | -0.096131 | -0.073242 | -0.32959 | -0.28839 | -0.19226 | -0.082398 | 121.5225 | 121.3074 | 60.7269 | -121.4172 | 121.3989 | 121.3898 | 60.7315 | -121.5683
194.625 | 121.5179 | -60.7727 | 60.6812 | 0.0066373 | 0.01095 | 0.073771 | 0.0034158 | 0.064283 | -0.0059002 | -0.0023028 | 0.0069425 | 0.00041436 | 0.062107 | 0.06295 | -0.011335 | -0.0029651 | 60.5759 | -60.4935 | 0.022888 | -60.7773 | 60.6491 | -60.7452 | -60.6995 | -61.0886 | 0.068665 | -60.965 | 60.5759 | 60.5988 | -60.6766 | -60.8734 | 0.027466 | 0.073242 | -0.032043 | 0.27924 | -0.004578 | -0.07782 | -0.10528 | 0.09613 | -0.10071 | -0.10528 | -0.31586 | -0.19226 | -0.091553 | -0.082397 | 121.4218 | 121.3486 | 60.7956 | -121.3806 | 121.3486 | 121.3715 | 60.8414 | -121.5546
196.2812 | 121.669 | -60.6949 | 60.7178 | 0.0066373 | 0.00069637 | 0.067575 | 0.0076882 | 0.064924 | 0.00072196 | -0.0046526 | 0.014572 | 0.002978 | 0.06467 | 0.064659 | -0.0079169 | -0.0080921 | 60.5804 | -60.5484 | 0.027466 | -60.759 | 60.7498 | -60.7498 | -60.704 | -61.0474 | 0.073242 | -60.9879 | 60.6537 | 60.6766 | -60.6491 | -60.8276 | -0.054932 | -0.009156 | 0.032044 | 0.14648 | -0.064087 | -0.054931 | -0.13733 | 0.045776 | -0.13275 | -0.064086 | -0.35248 | -0.29297 | -0.16022 | -0.041198 | 121.4447 | 121.2753 | 60.7224 | -121.4218 | 121.3486 | 121.3715 | 60.7681 | -121.5454
197.9375 | 121.637 | -60.7132 | 60.6857 | -0.0086212 | 0.0073188 | 0.072275 | 0.0044838 | 0.064497 | -0.0061138 | -0.0012346 | -0.00068649 | -0.0034308 | 0.063388 | 0.065087 | -0.011121 | -0.0046741 | 60.6033 | -60.434 | 0.082397 | -60.7452 | 60.6537 | -60.7727 | -60.7315 | -61.0291 | 0.14648 | -60.8963 | 60.5484 | 60.5576 | -60.6766 | -60.8597 | -0.059509 | -0.01831 | -0.032043 | 0.27924 | -0.032043 | -0.013733 | -0.082397 | 0.036621 | -0.14648 | -0.13733 | -0.31586 | -0.1831 | -0.036621 | -0.12817 | 121.3669 | 121.3165 | 60.7956 | -121.4172 | 121.2616 | 121.2708 | 60.8597 | -121.5454
199.625 | 121.5317 | -60.7636 | 60.704 | 0.0066373 | 0.0092414 | 0.070139 | 0.0012796 | 0.066847 | 0.00029476 | -0.0046526 | 0.0069425 | 0.00062796 | 0.06467 | 0.066155 | -0.0053533 | -0.0076647 | 60.6308 | -60.4706 | 0.032043 | -60.7269 | 60.6491 | -60.7407 | -60.6949 | -61.0153 | 0.064087 | -60.9375 | 60.5667 | 60.5621 | -60.6812 | -60.8505 | 0.022888 | 0.068665 | -0.054932 | 0.29297 | 0.036621 | -0.032044 | -0.073243 | 0.082398 | -0.086975 | -0.13733 | -0.25177 | -0.17395 | -0.086975 | -0.14191 | 121.4127 | 121.3943 | 60.7956 | -121.3989 | 121.3303 | 121.3257 | 60.8276 | -121.5546
201.3125 | 121.6415 | -60.6354 | 60.704 | 0.0066373 | 0.0017646 | 0.067362 | 0.0061928 | 0.064497 | 0.0026446 | -0.001662 | -0.00068649 | 0.002337 | 0.064457 | 0.066582 | -0.0091985 | -0.0053149 | 60.6216 | -60.5209 | 0.045776 | -60.7361 | 60.7727 | -60.7224 | -60.6903 | -61.0336 | 0.07782 | -61.0016 | 60.6537 | 60.6674 | -60.6537 | -60.8459 | -0.086975 | -0.054932 | 0.068664 | 0.11444 | -0.10071 | -0.045776 | -0.082398 | -0.018311 | -0.21057 | -0.050354 | -0.39825 | -0.36621 | -0.15564 | -0.036622 | 121.4081 | 121.257 | 60.6812 | -121.3943 | 121.2891 | 121.3028 | 60.7132 | -121.55
202.9844 | 121.4996 | -60.7636 | 60.7086 | 0.014267 | 0.011378 | 0.071848 | -0.00085655 | 0.063856 | -0.0012006 | -0.0014484 | -0.00068649 | 0.00062796 | 0.061466 | 0.063378 | -0.0089849 | -0.0044605 | 60.6171 | -60.4706 | 0.059509 | -60.7269 | 60.6491 | -60.759 | -60.6949 | -61.0199 | 0.082397 | -60.9329 | 60.5621 | 60.5759 | -60.6857 | -60.8643 | 0.004578 | 0.068665 | -0.059509 | 0.29297 | 0.036621 | -0.032044 | -0.091553 | 0.07782 | -0.10071 | -0.14648 | -0.25635 | -0.16937 | -0.068664 | -0.13275 | 121.4127 | 121.3806 | 60.8231 | -121.4035 | 121.3257 | 121.3394 | 60.8459 | -121.5729
204.6562 | 121.6553 | -60.6812 | 60.6995 | 0.014267 | 0.0030464 | 0.070993 | 0.0040566 | 0.065138 | 0.0020038 | -0.00080744 | 0.0069425 | 0.0034052 | 0.065738 | 0.066582 | -0.010908 | -0.0048877 | 60.5988 | -60.5301 | 0.032043 | -60.7361 | 60.759 | -60.7269 | -60.6857 | -61.0474 | 0.064087 | -61.0016 | 60.6583 | 60.6583 | -60.672 | -60.8322 | -0.045777 | -0.004578 | 0.059509 | 0.15106 | -0.054932 | -0.050354 | -0.10071 | 0.009155 | -0.15106 | -0.041199 | -0.36621 | -0.32044 | -0.16937 | -0.041199 | 121.4401 | 121.2799 | 60.7132 | -121.3852 | 121.3394 | 121.3394 | 60.7452 | -121.5317
206.3438 | 121.582 | -60.6995 | 60.7132 | -0.00099167 | 0.0034736 | 0.07078 | 0.0012796 | 0.065779 | 0.0022174 | -0.001021 | 0.0069425 | 0.004687 | 0.063388 | 0.066796 | -0.0051397 | -0.0048877 | 60.6308 | -60.4752 | 0.082397 | -60.7269 | 60.7315 | -60.7361 | -60.6857 | -61.0245 | 0.068665 | -60.9833 | 60.6537 | 60.6674 | -60.6445 | -60.8597 | -0.036621 | 0.013733 | 0.01831 | 0.2243 | -0.027466 | -0.041199 | -0.082398 | 0.054932 | -0.16022 | -0.059509 | -0.32501 | -0.28381 | -0.1236 | -0.045777 | 121.431 | 121.3303 | 60.7819 | -121.3989 | 121.3531 | 121.3669 | 60.7681 | -121.5729
208.0156 | 121.6461 | -60.6949 | 60.6766 | 0.0066373 | 0.009455 | 0.07078 | 0.0057656 | 0.064711 | -0.0044048 | -0.0020892 | 0.014572 | -0.0025762 | 0.063388 | 0.064873 | -0.013258 | -0.0031787 | 60.6125 | -60.4202 | 0.086975 | -60.7224 | 60.6491 | -60.7086 | -60.6949 | -61.0245 | 0.16022 | -60.8963 | 60.5576 | 60.5988 | -60.672 | -60.8551 | -0.013733 | 0 | -0.027466 | 0.27466 | -0.027466 | -0.027466 | -0.064087 | 0.022888 | -0.16022 | -0.11902 | -0.32959 | -0.20142 | -0.041198 | -0.07782 | 121.344 | 121.3074 | 60.7819 | -121.3715 | 121.2524 | 121.2936 | 60.8551 | -121.5317
209.7031 | 121.637 | -60.6583 | 60.7224 | 0.0066373 | 0.0030464 | 0.068644 | 0.0034158 | 0.063429 | 0.0034992 | 4.696e-05 | -0.00068649 | 0.0021234 | 0.063816 | 0.067009 | -0.0085577 | -0.0063831 | 60.6216 | -60.498 | 0.064087 | -60.7269 | 60.7498 | -60.7315 | -60.6995 | -61.0153 | 0.09613 | -60.9558 | 60.64 | 60.6674 | -60.6491 | -60.8093 | -0.073242 | -0.041199 | 0.027466 | 0.16022 | -0.068665 | -0.027466 | -0.10071 | 0.009155 | -0.15106 | -0.082397 | -0.35706 | -0.29755 | -0.14648 | -0.054932 | 121.4081 | 121.2799 | 60.7224 | -121.4218 | 121.2982 | 121.3257 | 60.7544 | -121.5317
211.375 | 121.6187 | -60.6583 | 60.7269 | -0.00099167 | 0.0017646 | 0.071634 | 0.002775 | 0.065992 | 0.0017902 | -0.00080744 | -0.00068649 | 0.002337 | 0.064029 | 0.066155 | -0.0087713 | -0.0048877 | 60.6262 | -60.4752 | 0.073242 | -60.704 | 60.7407 | -60.7452 | -60.6949 | -61.0153 | 0.091553 | -60.9833 | 60.6491 | 60.6674 | -60.6491 | -60.8551 | -0.086975 | -0.036621 | 0.013733 | 0.18311 | -0.045777 | -0.009156 | -0.10071 | 0.009155 | -0.19684 | -0.07782 | -0.35706 | -0.32501 | -0.12817 | -0.05951 | 121.3989 | 121.2845 | 60.7315 | -121.4218 | 121.3074 | 121.3257 | 60.7498 | -121.582
213.0625 | 121.6507 | -60.6628 | 60.6995 | -0.0086212 | 0.0017646 | 0.068216 | 0.0042702 | 0.065565 | 0.0017902 | -0.00038024 | 0.014572 | 0.0014826 | 0.065097 | 0.065087 | -0.0079169 | -0.0025379 | 60.5759 | -60.5209 | 0.050354 | -60.7224 | 60.7773 | -60.7315 | -60.6857 | -61.0428 | 0.073242 | -60.9741 | 60.6308 | 60.6766 | -60.6628 | -60.8414 | -0.068664 | -0.022888 | 0.07782 | 0.14191 | -0.059509 | -0.036621 | -0.1236 | 0 | -0.17853 | -0.068665 | -0.37994 | -0.31128 | -0.13275 | -0.022888 | 121.4401 | 121.2387 | 60.7132 | -121.3852 | 121.2936 | 121.3394 | 60.7361 | -121.5408
214.7188 | 121.5042 | -60.7727 | 60.6903 | 0.0066373 | 0.0088142 | 0.071848 | 0.0064066 | 0.062147 | -0.0050458 | -0.0025164 | 0.0069425 | -0.0027898 | 0.062748 | 0.064873 | -0.0098395 | -0.0027515 | 60.5438 | -60.498 | 0.018311 | -60.7681 | 60.6262 | -60.7452 | -60.7132 | -61.0748 | 0.050354 | -60.9879 | 60.553 | 60.5759 | -60.6674 | -60.8597 | 0.027466 | 0.059509 | -0.064087 | 0.27466 | 0.004578 | -0.054931 | -0.14648 | 0.10529 | -0.086975 | -0.13733 | -0.30212 | -0.21515 | -0.12817 | -0.11444 | 121.3989 | 121.3165 | 60.791 | -121.4035 | 121.3257 | 121.3486 | 60.8231 | -121.55
216.4062 | 121.4905 | -60.7636 | 60.6857 | 0.0066373 | 0.0098822 | 0.075693 | 0.0023476 | 0.065565 | -0.0031232 | -0.0029436 | 0.0069425 | -1.2844e-05 | 0.06232 | 0.063591 | -0.01048 | -0.0051013 | 60.5621 | -60.5072 | 0.013733 | -60.7773 | 60.6583 | -60.7407 | -60.7086 | -61.0794 | 0.032043 | -60.9695 | 60.5621 | 60.5759 | -60.6949 | -60.8643 | 0.022888 | 0.054932 | -0.027466 | 0.25635 | -0.013733 | -0.068665 | -0.1236 | 0.068665 | -0.10071 | -0.1236 | -0.31586 | -0.20599 | -0.10529 | -0.10986 | 121.4218 | 121.3257 | 60.7773 | -121.3943 | 121.3257 | 121.3394 | 60.7956 | -121.55
218.0625 | 121.5454 | -60.7361 | 60.7315 | -0.00099167 | 0.0053962 | 0.068003 | 0.0034158 | 0.063856 | 0.001363 | -0.0014484 | 0.0069425 | 0.004687 | 0.065097 | 0.068932 | -0.0081305 | -0.0036059 | 60.5759 | -60.5713 | -0.027466 | -60.7727 | 60.7407 | -60.7498 | -60.6766 | -61.1023 | -0.050354 | -61.0565 | 60.6491 | 60.6537 | -60.6812 | -60.8368 | -0.013733 | 0.059509 | 0.009156 | 0.16479 | -0.036621 | -0.09613 | -0.15564 | 0.054932 | -0.10071 | -0.082397 | -0.36621 | -0.32044 | -0.21973 | -0.077819 | 121.4767 | 121.312 | 60.7086 | -121.4081 | 121.3852 | 121.3898 | 60.6857 | -121.5683
219.75 | 121.5546 | -60.7407 | 60.6857 | -0.00099167 | 0.0075324 | 0.068857 | 0.0023476 | 0.065351 | 0.00050836 | -0.00059384 | -0.008316 | 0.00084176 | 0.064029 | 0.067009 | -0.0070623 | -0.0046741 | 60.585 | -60.5118 | 0.009155 | -60.7407 | 60.6812 | -60.7452 | -60.6857 | -61.0199 | 0.045776 | -60.9375 | 60.5713 | 60.6125 | -60.6812 | -60.8276 | -0.004577 | 0.054932 | -0.004578 | 0.22888 | 0 | -0.054932 | -0.10071 | 0.05951 | -0.086975 | -0.11444 | -0.27923 | -0.19684 | -0.10986 | -0.073242 | 121.4218 | 121.3257 | 60.7498 | -121.3715 | 121.312 | 121.3531 | 60.7864 | -121.5134
221.4688 | 121.5775 | -60.6995 | 60.7086 | -0.0086212 | 0.0045416 | 0.071421 | 0.0070474 | 0.068983 | -0.0035504 | -0.00508 | -0.00068649 | 0.00084176 | 0.064457 | 0.068077 | -0.011121 | -0.0046741 | 60.6079 | -60.4385 | 0.1236 | -60.7132 | 60.6903 | -60.7452 | -60.6857 | -61.0291 | 0.15106 | -60.9375 | 60.5667 | 60.6125 | -60.672 | -60.8643 | -0.045776 | 0.013733 | -0.01831 | 0.26093 | -0.013733 | -0.027466 | -0.10071 | 0.027466 | -0.16479 | -0.14191 | -0.32959 | -0.23804 | -0.073242 | -0.09613 | 121.3898 | 121.3074 | 60.8231 | -121.3943 | 121.2662 | 121.312 | 60.8505 | -121.5729
223.1406 | 121.6324 | -60.6674 | 60.7224 | -0.00099167 | 0.0017646 | 0.071421 | 0.0068338 | 0.063643 | 0.00050836 | -0.00273 | -0.00068649 | 0.0025508 | 0.064457 | 0.066368 | -0.0094123 | -0.0061695 | 60.5576 | -60.553 | 0.013733 | -60.7636 | 60.7452 | -60.7498 | -60.7132 | -61.084 | 0.036621 | -61.0245 | 60.672 | 60.6537 | -60.6583 | -60.8643 | -0.082398 | -0.045777 | 0.022888 | 0.11444 | -0.096131 | -0.050354 | -0.1648 | 0.009155 | -0.19684 | -0.050354 | -0.41656 | -0.35706 | -0.16022 | -0.068664 | 121.4127 | 121.225 | 60.6812 | -121.4355 | 121.3394 | 121.3211 | 60.704 | -121.5866
224.875 | 121.5912 | -60.6949 | 60.7178 | -0.0086212 | 0.0024054 | 0.070566 | 0.0059792 | 0.06706 | -0.0018414 | -0.0025164 | 0.0069425 | 0.0010554 | 0.066379 | 0.0653 | -0.012189 | -0.0065967 | 60.5667 | -60.5255 | 0.018311 | -60.759 | 60.7224 | -60.7452 | -60.7132 | -61.0886 | 0.054932 | -60.9924 | 60.6491 | 60.6628 | -60.6903 | -60.8505 | -0.050354 | -0.018311 | 0.004578 | 0.16937 | -0.064087 | -0.045776 | -0.15106 | 0.004577 | -0.15564 | -0.068664 | -0.39368 | -0.29755 | -0.14191 | -0.054931 | 121.4172 | 121.2616 | 60.7132 | -121.431 | 121.344 | 121.3577 | 60.7498 | -121.5683
226.5781 | 121.637 | -60.6903 | 60.6766 | -0.00099167 | 0.0064642 | 0.073343 | 0.0044838 | 0.06407 | -0.0039776 | -0.0042254 | 0.0069425 | -0.00065364 | 0.064884 | 0.065514 | -0.012189 | -0.0053149 | 60.6445 | -60.434 | 0.10529 | -60.6995 | 60.6491 | -60.759 | -60.672 | -61.0062 | 0.16022 | -60.9009 | 60.5667 | 60.5988 | -60.6537 | -60.8688 | -0.068664 | 0.018311 | -0.027466 | 0.25635 | -0.009155 | -0.027466 | -0.032044 | 0.036621 | -0.17853 | -0.10986 | -0.31586 | -0.21057 | -0.032044 | -0.07782 | 121.3394 | 121.3348 | 60.7956 | -121.3486 | 121.257 | 121.2891 | 60.8505 | -121.5454
228.25 | 121.6507 | -60.6674 | 60.7269 | 0.0066373 | 0.0036872 | 0.069284 | 0.0012796 | 0.066206 | 0.0015766 | -0.004439 | 0.0069425 | 0.0036188 | 0.064029 | 0.065941 | -0.0085577 | -0.0068103 | 60.6079 | -60.5392 | 0.022888 | -60.7361 | 60.7544 | -60.7269 | -60.7086 | -61.0382 | 0.07782 | -60.9879 | 60.6903 | 60.6949 | -60.6445 | -60.8185 | -0.05951 | -0.041199 | 0.027466 | 0.12817 | -0.068665 | -0.027466 | -0.11902 | 0.022888 | -0.15106 | -0.036621 | -0.37079 | -0.32043 | -0.16937 | -0.032044 | 121.4218 | 121.2753 | 60.6903 | -121.4355 | 121.3577 | 121.3623 | 60.7452 | -121.5454
229.9531 | 121.6232 | -60.704 | 60.6903 | -0.00099167 | 0.010309 | 0.071634 | 0.0032022 | 0.065779 | -0.0052594 | -0.006148 | 0.0069425 | -0.0036444 | 0.065738 | 0.066155 | -0.011762 | -0.0029651 | 60.553 | -60.5118 | 0.009155 | -60.7636 | 60.6674 | -60.7681 | -60.6995 | -61.0703 | 0.073242 | -60.9558 | 60.5759 | 60.585 | -60.6674 | -60.8551 | -0.064086 | 0.004578 | -0.022889 | 0.19226 | -0.059509 | -0.064087 | -0.13733 | 0.036622 | -0.15106 | -0.11444 | -0.36621 | -0.25177 | -0.10071 | -0.10529 | 121.3715 | 121.257 | 60.7132 | -121.3898 | 121.2799 | 121.2891 | 60.7773 | -121.5454
231.6406 | 121.5134 | -60.7178 | 60.7407 | 0.014267 | 0.0024054 | 0.069925 | 0.0032022 | 0.061506 | 0.0037128 | -0.0020892 | 0.022202 | 0.004046 | 0.065738 | 0.068077 | -0.0066351 | -0.0076647 | 60.6216 | -60.5164 | 0.041199 | -60.7269 | 60.7498 | -60.7407 | -60.6995 | -61.0336 | 0.036621 | -60.997 | 60.6491 | 60.672 | -60.6583 | -60.8643 | -0.022889 | 0.01831 | 0.009155 | 0.20142 | -0.009156 | -0.027466 | -0.11902 | 0.059509 | -0.14648 | -0.091553 | -0.31586 | -0.27924 | -0.13275 | -0.068665 | 121.4676 | 121.3394 | 60.759 | -121.4401 | 121.3669 | 121.3898 | 60.7544 | -121.6049
233.3125 | 121.5454 | -60.7361 | 60.6949 | -0.00099167 | 0.0083868 | 0.07078 | 0.0012796 | 0.064497 | -0.00077324 | 4.696e-05 | -0.00068649 | 0.00041436 | 0.062748 | 0.064019 | -0.0057807 | -0.0044605 | 60.6171 | -60.466 | 0.054932 | -60.7178 | 60.6583 | -60.7315 | -60.6674 | -60.9879 | 0.07782 | -60.9329 | 60.553 | 60.5621 | -60.6674 | -60.8459 | 0.004578 | 0.068665 | -0.036621 | 0.27008 | 0.018311 | -0.050354 | -0.07782 | 0.068665 | -0.10986 | -0.14191 | -0.25177 | -0.19684 | -0.086975 | -0.13275 | 121.3943 | 121.3531 | 60.791 | -121.3623 | 121.2891 | 121.2982 | 60.8139 | -121.5408
234.9844 | 121.5912 | -60.7178 | 60.6995 | -0.00099167 | 0.0047552 | 0.071848 | 0.0049112 | 0.06407 | -0.0029094 | -0.0029436 | 0.0069425 | 0.00084176 | 0.06467 | 0.066155 | -0.010267 | -0.0042467 | 60.5667 | -60.5392 | 0.027466 | -60.7819 | 60.7407 | -60.759 | -60.704 | -61.0931 | 0.050354 | -61.0107 | 60.6766 | 60.704 | -60.6583 | -60.8414 | -0.041199 | 0.013732 | 0.041199 | 0.17853 | -0.064087 | -0.077819 | -0.13275 | 0.059509 | -0.1236 | -0.022888 | -0.37537 | -0.29297 | -0.16937 | 0.004578 | 121.4584 | 121.2845 | 60.7452 | -121.4035 | 121.3943 | 121.4218 | 60.7681 | -121.5408
236.6562 | 121.5179 | -60.7407 | 60.7178 | -0.00099167 | 0.0081732 | 0.071207 | 0.0032022 | 0.065779 | 0.00072196 | -0.0012346 | -0.00068649 | 0.00020076 | 0.063602 | 0.066796 | -0.0070623 | -0.0051013 | 60.6262 | -60.4706 | 0.032043 | -60.7086 | 60.6903 | -60.6995 | -60.6628 | -60.9924 | 0.07782 | -60.9283 | 60.5759 | 60.5896 | -60.6583 | -60.8368 | 0.041199 | 0.07782 | -0.027465 | 0.27008 | 0.032044 | -0.045776 | -0.091552 | 0.082398 | -0.09613 | -0.14191 | -0.25177 | -0.18768 | -0.091553 | -0.12817 | 121.431 | 121.3669 | 60.7727 | -121.3806 | 121.3165 | 121.3303 | 60.8185 | -121.5546
238.3281 | 121.5042 | -60.7315 | 60.7681 | 0.014267 | 0.0028326 | 0.068644 | 0.0032022 | 0.063429 | 0.002431 | -0.00080744 | 0.014572 | 0.0044734 | 0.064243 | 0.066582 | -0.0081305 | -0.0053149 | 60.6308 | -60.5026 | 0.032043 | -60.7361 | 60.7407 | -60.7224 | -60.6903 | -61.0291 | 0.022888 | -61.0153 | 60.6628 | 60.672 | -60.64 | -60.8368 | 0.009155 | 0.041198 | -0.027465 | 0.22888 | -0.004578 | -0.045776 | -0.13733 | 0.091552 | -0.10529 | -0.10529 | -0.29755 | -0.28381 | -0.17853 | -0.09613 | 121.4722 | 121.3623 | 60.7635 | -121.4584 | 121.3943 | 121.4035 | 60.7544 | -121.6049
239.9844 | 121.6232 | -60.6995 | 60.6903 | -0.00099167 | 0.009455 | 0.073771 | 0.0059792 | 0.062361 | -0.0067548 | -0.0031574 | 0.022202 | -0.0023626 | 0.063388 | 0.063378 | -0.0096259 | -0.0029651 | 60.5896 | -60.4706 | 0.059509 | -60.7269 | 60.6537 | -60.7315 | -60.6995 | -61.0336 | 0.12817 | -60.8963 | 60.5667 | 60.585 | -60.6583 | -60.8505 | -0.032043 | 0 | -0.036621 | 0.22888 | -0.027466 | -0.027466 | -0.10071 | 0.041199 | -0.15106 | -0.1236 | -0.33417 | -0.19684 | -0.045776 | -0.10529 | 121.3531 | 121.2891 | 60.759 | -121.3898 | 121.2662 | 121.2845 | 60.8276 | -121.5408
241.6562 | 121.5866 | -60.6949 | 60.6995 | -0.00099167 | 0.0051826 | 0.072916 | 0.0064066 | 0.065779 | -0.0039776 | -0.0025164 | -0.00068649 | 0.00041436 | 0.065738 | 0.063591 | -0.011335 | -0.0044605 | 60.6308 | -60.4202 | 0.13275 | -60.704 | 60.672 | -60.7315 | -60.6812 | -61.0153 | 0.16479 | -60.9192 | 60.5988 | 60.585 | -60.6491 | -60.8414 | -0.036621 | 0.013733 | -0.027466 | 0.27466 | -0.009156 | -0.022889 | -0.068665 | 0.045776 | -0.14648 | -0.10071 | -0.32044 | -0.2243 | -0.077819 | -0.11444 | 121.3669 | 121.3257 | 60.8276 | -121.3806 | 121.2936 | 121.2799 | 60.8597 | -121.5408
243.3438 | 121.5591 | -60.7315 | 60.7132 | -0.0086212 | 0.004969 | 0.072489 | -0.00021575 | 0.064924 | 0.0020038 | -0.0025164 | 0.014572 | 0.0031916 | 0.063388 | 0.065728 | -0.0079169 | -0.0063831 | 60.6033 | -60.5209 | -0.009155 | -60.7361 | 60.7269 | -60.6949 | -60.6812 | -61.0107 | 0.054932 | -60.9375 | 60.6033 | 60.6171 | -60.64 | -60.8459 | 0.036621 | 0.050354 | 0.013733 | 0.21057 | -0.004578 | -0.054932 | -0.10986 | 0.091552 | -0.11444 | -0.10986 | -0.27924 | -0.20599 | -0.091553 | -0.096131 | 121.4584 | 121.3348 | 60.7224 | -121.3943 | 121.3348 | 121.3486 | 60.7864 | -121.5591
245.0312 | 121.4767 | -60.759 | 60.7361 | 0.014267 | 0.011164 | 0.071848 | 0.003843 | 0.06407 | -0.003764 | -0.00273 | 0.0069425 | -0.00044004 | 0.064029 | 0.06295 | -0.0083441 | -0.0048877 | 60.6262 | -60.4477 | 0.032043 | -60.7361 | 60.6491 | -60.7407 | -60.6857 | -61.0474 | 0.050354 | -60.9512 | 60.5484 | 60.6079 | -60.672 | -60.8551 | 0.01831 | 0.073242 | -0.086975 | 0.31128 | 0.022888 | -0.050354 | -0.10986 | 0.086975 | -0.096131 | -0.18768 | -0.28839 | -0.19226 | -0.09613 | -0.12817 | 121.4081 | 121.3852 | 60.791 | -121.4218 | 121.3074 | 121.3669 | 60.8093 | -121.5912
246.7031 | 121.5546 | -60.7224 | 60.7269 | 0.014267 | 0.007746 | 0.072275 | 0.002134 | 0.061934 | 0.0020038 | -0.0012346 | 0.0069425 | 0.00041436 | 0.061039 | 0.065514 | -0.0064215 | -0.0055285 | 60.5896 | -60.5347 | -0.013733 | -60.759 | 60.7636 | -60.7315 | -60.6949 | -61.0245 | -0.009155 | -60.9879 | 60.6216 | 60.6308 | -60.6445 | -60.8505 | -0.009155 | 0.027466 | 0.036621 | 0.18768 | -0.036621 | -0.064087 | -0.13733 | 0.07782 | -0.12817 | -0.10529 | -0.30212 | -0.2655 | -0.13733 | -0.096131 | 121.4859 | 121.312 | 60.7086 | -121.4218 | 121.344 | 121.3531 | 60.7132 | -121.5775
248.3906 | 121.5866 | -60.6903 | 60.7452 | 0.0066373 | 0.00326 | 0.071421 | 0.0066202 | 0.067274 | 0.00072196 | -0.00273 | 0.014572 | 0.0016962 | 0.064457 | 0.066582 | -0.0098395 | -0.0029651 | 60.585 | -60.5026 | 0.045776 | -60.7452 | 60.7498 | -60.7361 | -60.672 | -61.0748 | 0.050354 | -60.997 | 60.672 | 60.704 | -60.6628 | -60.8459 | -0.045776 | 0.018311 | 0.004578 | 0.18768 | -0.054931 | -0.073242 | -0.16022 | 0.027466 | -0.15564 | -0.073242 | -0.38452 | -0.3067 | -0.15106 | -0.041198 | 121.4401 | 121.2753 | 60.7361 | -121.4172 | 121.3623 | 121.3943 | 60.7407 | -121.5912
250.0938 | 121.55 | -60.7407 | 60.7361 | 0.0066373 | 0.0039008 | 0.068857 | 0.0032022 | 0.064497 | 0.00029476 | -0.00016664 | 0.0069425 | 0.001269 | 0.062961 | 0.066155 | -0.0079169 | -0.0053149 | 60.6079 | -60.5255 | -0.013733 | -60.7544 | 60.7315 | -60.7269 | -60.6903 | -61.0291 | 0.009155 | -60.9604 | 60.6262 | 60.6628 | -60.64 | -60.8459 | 0.013733 | 0.050354 | -0.004578 | 0.21515 | -0.013733 | -0.064087 | -0.12817 | 0.10071 | -0.10529 | -0.10986 | -0.28839 | -0.21973 | -0.11444 | -0.073242 | 121.4722 | 121.3486 | 60.7269 | -121.4264 | 121.3669 | 121.4035 | 60.7498 | -121.582
251.7969 | 121.6187 | -60.7407 | 60.6903 | 0.0066373 | 0.010737 | 0.074839 | 0.0023476 | 0.063215 | -0.0041912 | -0.0031574 | 0.0069425 | -0.00086724 | 0.064243 | 0.062737 | -0.011762 | -0.0038195 | 60.5576 | -60.5026 | 0 | -60.7224 | 60.6766 | -60.7452 | -60.672 | -61.0565 | 0.068665 | -60.9421 | 60.6125 | 60.6354 | -60.6308 | -60.8276 | -0.004577 | 0.068665 | -0.013733 | 0.23804 | 0.018311 | -0.050354 | -0.13275 | 0.10986 | -0.086975 | -0.07782 | -0.31586 | -0.20142 | -0.11444 | -0.054932 | 121.4172 | 121.2982 | 60.7407 | -121.3623 | 121.3531 | 121.376 | 60.8093 | -121.5179
253.5156 | 121.6187 | -60.6537 | 60.6949 | -0.00099167 | 0.0058234 | 0.073984 | 0.0061928 | 0.06642 | -0.0041912 | -0.00273 | -0.008316 | 0.00084176 | 0.064457 | 0.064446 | -0.010694 | -0.0048877 | 60.6583 | -60.4111 | 0.10529 | -60.6949 | 60.6674 | -60.7269 | -60.6766 | -60.9695 | 0.16937 | -60.8917 | 60.5759 | 60.6033 | -60.64 | -60.8185 | -0.073242 | -0.022888 | -0.027466 | 0.24262 | -0.041198 | -0.01831 | -0.036621 | 0.013733 | -0.16479 | -0.11902 | -0.31586 | -0.23804 | -0.073243 | -0.091552 | 121.3211 | 121.312 | 60.759 | -121.3715 | 121.2296 | 121.257 | 60.8231 | -121.5134
255.1875 | 121.5958 | -60.6812 | 60.7178 | 0.014267 | 0.0053962 | 0.07313 | 0.0066202 | 0.065565 | 0.001363 | -0.0020892 | 0.014572 | 0.0019098 | 0.065525 | 0.062096 | -0.010053 | -0.0063831 | 60.5988 | -60.5026 | 0.041199 | -60.7315 | 60.7636 | -60.7132 | -60.6537 | -61.0611 | 0.045776 | -60.9787 | 60.6583 | 60.6903 | -60.6628 | -60.8322 | -0.032044 | 0.027465 | 0.045777 | 0.17853 | -0.050354 | -0.077819 | -0.11902 | 0.01831 | -0.15106 | -0.059509 | -0.37994 | -0.29755 | -0.14648 | -0.027465 | 121.4447 | 121.2799 | 60.7224 | -121.3715 | 121.3394 | 121.3715 | 60.7269 | -121.55
256.875 | 121.582 | -60.6674 | 60.759 | 0.0066373 | 0.0017646 | 0.071634 | 0.003843 | 0.066847 | -0.00098684 | -0.0023028 | 0.014572 | 0.00062796 | 0.06467 | 0.063164 | -0.0081305 | -0.0051013 | 60.6445 | -60.4385 | 0.073242 | -60.7132 | 60.7315 | -60.7269 | -60.7086 | -61.0474 | 0.086975 | -60.9741 | 60.6628 | 60.6857 | -60.6674 | -60.8368 | -0.05951 | -0.041199 | -0.027466 | 0.22888 | -0.045777 | -0.004578 | -0.11444 | 0 | -0.16937 | -0.09613 | -0.37994 | -0.3067 | -0.13733 | -0.073242 | 121.3989 | 121.3119 | 60.7407 | -121.4676 | 121.3303 | 121.3531 | 60.7544 | -121.5958
258.5312 | 121.4951 | -60.7361 | 60.7498 | -0.00099167 | 0.011591 | 0.073984 | 0.002134 | 0.063643 | -0.0026958 | -0.0035846 | 0.0069425 | -0.002149 | 0.061679 | 0.065514 | -0.0064215 | -0.0029651 | 60.6079 | -60.4477 | 0.018311 | -60.7315 | 60.672 | -60.7361 | -60.6628 | -61.0474 | 0.041199 | -60.9329 | 60.5942 | 60.6262 | -60.6537 | -60.8643 | 0 | 0.073242 | -0.07782 | 0.28839 | 0.004578 | -0.068664 | -0.14191 | 0.082397 | -0.12817 | -0.15564 | -0.31128 | -0.19684 | -0.068664 | -0.1236 | 121.4081 | 121.344 | 60.7544 | -121.4127 | 121.3303 | 121.3623 | 60.7773 | -121.6141
260.2188 | 121.5866 | -60.6445 | 60.7315 | 0.0066373 | 0.0036872 | 0.071848 | 0.0053384 | 0.06642 | -0.0016278 | -0.00273 | 0.014572 | -0.0015082 | 0.064029 | 0.065087 | -0.01048 | -0.0057421 | 60.6583 | -60.3973 | 0.10986 | -60.672 | 60.7132 | -60.6995 | -60.6812 | -60.9787 | 0.17395 | -60.9055 | 60.6308 | 60.6125 | -60.64 | -60.8276 | -0.054932 | -0.036621 | -0.01831 | 0.24719 | -0.027466 | 0.009155 | -0.073242 | 0.004577 | -0.18311 | -0.10071 | -0.33417 | -0.26093 | -0.07782 | -0.11902 | 121.3577 | 121.3028 | 60.7544 | -121.4127 | 121.2753 | 121.257 | 60.8185 | -121.5591
261.9062 | 121.5958 | -60.672 | 60.7224 | -0.00099167 | 0.0056098 | 0.073557 | 0.0079018 | 0.065351 | -0.0016278 | -0.0031574 | 0.0069425 | -0.00086724 | 0.06467 | 0.064659 | -0.011762 | -0.0068103 | 60.672 | -60.3836 | 0.10986 | -60.6857 | 60.6949 | -60.7224 | -60.6674 | -60.9604 | 0.16022 | -60.8826 | 60.6308 | 60.6125 | -60.6308 | -60.8002 | -0.050354 | 0.004578 | -0.027466 | 0.28839 | -0.013733 | -0.018311 | -0.050354 | 0.041199 | -0.12817 | -0.091553 | -0.28839 | -0.21057 | -0.082397 | -0.10986 | 121.3669 | 121.344 | 60.7819 | -121.3898 | 121.3028 | 121.2845 | 60.8322 | -121.5225
263.5625 | 121.5042 | -60.6812 | 60.7864 | 0.0066373 | 0.004969 | 0.067789 | 0.0017068 | 0.064711 | 0.004781 | -0.00059384 | 0.0069425 | 0.0049006 | 0.063816 | 0.066155 | -0.0064215 | -0.0068103 | 60.6445 | -60.5072 | 0.009155 | -60.7132 | 60.8093 | -60.704 | -60.6354 | -61.0199 | -0.009155 | -61.0016 | 60.7132 | 60.7132 | -60.6216 | -60.8047 | -0.022889 | 0.045776 | 0.022888 | 0.17395 | -0.032044 | -0.07782 | -0.14191 | 0.059509 | -0.1236 | -0.073242 | -0.33875 | -0.32044 | -0.19684 | -0.073242 | 121.4905 | 121.3257 | 60.6903 | -121.4218 | 121.3943 | 121.3943 | 60.672 | -121.5912
265.2344 | 121.5088 | -60.6812 | 60.8002 | 0.0066373 | 0.0019782 | 0.070353 | -0.00042935 | 0.06706 | 0.003072 | -0.0025164 | 0.0069425 | 0.0049006 | 0.064457 | 0.065941 | -0.0057807 | -0.0044605 | 60.6537 | -60.466 | 0.050354 | -60.704 | 60.7681 | -60.6903 | -60.6491 | -60.9924 | 0.032043 | -60.965 | 60.6812 | 60.6995 | -60.6171 | -60.7864 | -0.009156 | 0.032043 | -0.032044 | 0.21515 | -0.022889 | -0.054932 | -0.14648 | 0.064087 | -0.10529 | -0.11902 | -0.31128 | -0.28381 | -0.17853 | -0.10071 | 121.4493 | 121.3348 | 60.7315 | -121.4493 | 121.3623 | 121.3806 | 60.7132 | -121.5866
266.9531 | 121.5317 | -60.704 | 60.759 | 0.014267 | 0.0064642 | 0.070139 | -2.152e-06 | 0.064283 | -0.00077324 | -0.00059384 | -0.008316 | 0.002337 | 0.063175 | 0.065514 | -0.0081305 | -0.0029651 | 60.5988 | -60.5164 | -0.041199 | -60.7315 | 60.7956 | -60.7086 | -60.6628 | -61.0474 | -0.032043 | -60.9924 | 60.7132 | 60.7086 | -60.6171 | -60.8047 | -0.004577 | 0.041199 | 0.036621 | 0.18768 | -0.027465 | -0.068664 | -0.16022 | 0.086976 | -0.10071 | -0.045776 | -0.34332 | -0.28839 | -0.18768 | -0.050354 | 121.4996 | 121.3028 | 60.6628 | -121.4218 | 121.4172 | 121.4127 | 60.672 | -121.5637
268.6875 | 121.6324 | -60.6628 | 60.7224 | -0.00099167 | 0.0073188 | 0.074198 | 0.0070474 | 0.064711 | -0.0061138 | -0.001662 | -0.00068649 | -0.0012946 | 0.063388 | 0.06295 | -0.010053 | -0.0033923 | 60.6537 | -60.3653 | 0.09613 | -60.672 | 60.6857 | -60.704 | -60.6583 | -60.965 | 0.16937 | -60.8459 | 60.6171 | 60.64 | -60.6125 | -60.8139 | -0.041199 | 0.004578 | -0.036621 | 0.29755 | -0.009155 | -0.013733 | -0.068664 | 0.050354 | -0.15106 | -0.10529 | -0.30212 | -0.18311 | -0.032043 | -0.082397 | 121.3486 | 121.3165 | 60.759 | -121.3806 | 121.2799 | 121.3028 | 60.8322 | -121.5363
270.3594 | 121.5454 | -60.704 | 60.7452 | 0.014267 | 0.0064642 | 0.068644 | 0.001066 | 0.063215 | 0.0037128 | -0.0018756 | 0.0069425 | 0.0019098 | 0.061466 | 0.06765 | -0.0068487 | -0.0051013 | 60.6216 | -60.5164 | -0.036621 | -60.7178 | 60.791 | -60.704 | -60.6812 | -61.0107 | -0.009155 | -60.9421 | 60.6628 | 60.6674 | -60.6445 | -60.8093 | 0 | 0.022889 | 0.045777 | 0.18768 | -0.013732 | -0.036621 | -0.1236 | 0.05951 | -0.10529 | -0.082397 | -0.3067 | -0.23804 | -0.13275 | -0.07782 | 121.4951 | 121.3257 | 60.6674 | -121.4264 | 121.3669 | 121.3715 | 60.6949 | -121.5546
272.0312 | 121.5408 | -60.6583 | 60.7864 | 0.014267 | 0.0011236 | 0.069284 | 0.0034158 | 0.065779 | 0.0034992 | -0.0029436 | -0.00068649 | 0.0019098 | 0.06232 | 0.064232 | -0.0068487 | -0.0046741 | 60.7132 | -60.4111 | 0.073242 | -60.6628 | 60.7956 | -60.6766 | -60.6308 | -60.9695 | 0.050354 | -60.9283 | 60.7132 | 60.7132 | -60.5942 | -60.8047 | -0.018311 | 0.027466 | 0.009155 | 0.24719 | -0.004578 | -0.032044 | -0.073242 | 0.064087 | -0.14648 | -0.073242 | -0.31128 | -0.27008 | -0.1236 | -0.073242 | 121.4539 | 121.3715 | 60.7315 | -121.4172 | 121.3715 | 121.3715 | 60.7086 | -121.5912
273.7188 | 121.5912 | -60.6308 | 60.7773 | -0.00099167 | 0.0036872 | 0.068857 | 0.0044838 | 0.065565 | 0.0032856 | 4.696e-05 | 0.014572 | 0.0016962 | 0.062534 | 0.066155 | -0.0091985 | -0.0046741 | 60.6812 | -60.3928 | 0.073242 | -60.6445 | 60.8185 | -60.6445 | -60.6354 | -60.9512 | 0.09613 | -60.8963 | 60.6949 | 60.6995 | -60.5759 | -60.7681 | -0.013733 | -0.004578 | 0.041198 | 0.23804 | -0.013733 | -0.009155 | -0.096131 | 0.054931 | -0.13733 | -0.082398 | -0.32044 | -0.2655 | -0.12817 | -0.07782 | 121.4493 | 121.3119 | 60.704 | -121.4127 | 121.3257 | 121.3303 | 60.7269 | -121.5454
275.3906 | 121.5683 | -60.6079 | 60.7681 | 0.0066373 | 0.0039008 | 0.069071 | 0.0083292 | 0.064283 | -0.0012006 | -0.00273 | 0.0069425 | 0.00062796 | 0.06467 | 0.064659 | -0.013258 | -0.0053149 | 60.6354 | -60.4065 | 0.068665 | -60.6537 | 60.7864 | -60.672 | -60.6216 | -61.0245 | 0.07782 | -60.9146 | 60.7086 | 60.7224 | -60.585 | -60.7819 | -0.064087 | -0.013733 | 0.018311 | 0.20142 | -0.045777 | -0.032044 | -0.13275 | 0.022888 | -0.17395 | -0.059509 | -0.41657 | -0.3067 | -0.13275 | -0.045776 | 121.3943 | 121.2433 | 60.6766 | -121.3898 | 121.3165 | 121.3303 | 60.6857 | -121.55
277.0781 | 121.5683 | -60.64 | 60.7773 | -0.00099167 | 0.0079596 | 0.073771 | 0.0057656 | 0.06407 | -0.0059002 | -0.00273 | -0.008316 | -0.0023626 | 0.063388 | 0.063591 | -0.012617 | -0.0031787 | 60.5942 | -60.4431 | 0.004578 | -60.6857 | 60.7452 | -60.6583 | -60.6308 | -61.0107 | 0.059509 | -60.8963 | 60.6537 | 60.6583 | -60.6033 | -60.791 | -0.01831 | 0.009156 | -0.032044 | 0.19684 | -0.045776 | -0.054932 | -0.18311 | 0.036621 | -0.15106 | -0.1236 | -0.37079 | -0.25635 | -0.10529 | -0.11902 | 121.3852 | 121.2341 | 60.6445 | -121.4081 | 121.2936 | 121.2982 | 60.6995 | -121.5683
278.7656 | 121.5408 | -60.6766 | 60.7681 | -0.00099167 | 0.009455 | 0.073771 | -0.00021575 | 0.064924 | -0.0026958 | -0.00273 | 0.014572 | 0.00084176 | 0.062534 | 0.063591 | -0.0070623 | -0.0068103 | 60.7224 | -60.3882 | 0.054932 | -60.6262 | 60.7727 | -60.6445 | -60.6171 | -60.9146 | 0.073242 | -60.8368 | 60.6628 | 60.6628 | -60.5804 | -60.7636 | 0.032044 | 0.05951 | 0.004578 | 0.28839 | 0.050354 | -0.009156 | -0.045776 | 0.096131 | -0.086975 | -0.10529 | -0.23804 | -0.16022 | -0.073242 | -0.10529 | 121.4493 | 121.3989 | 60.7315 | -121.3852 | 121.3394 | 121.3394 | 60.7498 | -121.5317
280.4844 | 121.5958 | -60.5896 | 60.791 | -0.00099167 | 0.0034736 | 0.072062 | 0.0066202 | 0.065138 | -0.0039776 | -0.0012346 | 0.0069425 | 0.0014826 | 0.063388 | 0.0653 | -0.011121 | -0.0057421 | 60.7224 | -60.347 | 0.12817 | -60.6308 | 60.7681 | -60.6491 | -60.5942 | -60.9009 | 0.16937 | -60.8231 | 60.6628 | 60.7224 | -60.553 | -60.7361 | -0.059509 | -0.004577 | -0.022889 | 0.24262 | -0.041198 | -0.036621 | -0.068665 | 0.036621 | -0.14648 | -0.12817 | -0.31128 | -0.23346 | -0.086975 | -0.068665 | 121.3577 | 121.312 | 60.7178 | -121.3852 | 121.2524 | 121.312 | 60.759 | -121.5271
282.1562 | 121.6415 | -60.5804 | 60.7727 | -0.016251 | 0.0086006 | 0.073557 | 0.0040566 | 0.066206 | -0.0033368 | -0.0055072 | 0.014572 | -0.0010808 | 0.065097 | 0.063805 | -0.011549 | -0.0065967 | 60.7269 | -60.3516 | 0.073242 | -60.6079 | 60.7498 | -60.64 | -60.5942 | -60.91 | 0.14191 | -60.7956 | 60.6491 | 60.6949 | -60.5576 | -60.7407 | -0.05951 | -0.013733 | -0.022888 | 0.22888 | -0.027466 | -0.013733 | -0.045776 | 0.022888 | -0.16022 | -0.1236 | -0.32959 | -0.21515 | -0.054931 | -0.07782 | 121.3303 | 121.3074 | 60.6537 | -121.3669 | 121.2296 | 121.2753 | 60.7224 | -121.5134
283.8594 | 121.5317 | -60.6033 | 60.8505 | -0.00099167 | 0.0058234 | 0.070566 | 0.0012796 | 0.065992 | 0.0037128 | -0.0020892 | 0.0069425 | 0.004046 | 0.066593 | 0.066796 | -0.0053533 | -0.0078783 | 60.704 | -60.4523 | -0.027466 | -60.672 | 60.9146 | -60.6308 | -60.5759 | -60.9695 | -0.068665 | -60.9283 | 60.7681 | 60.759 | -60.5621 | -60.7452 | -0.027465 | 0.027466 | 0.064087 | 0.15106 | -0.068664 | -0.09613 | -0.14648 | 0.041199 | -0.14191 | -0.082398 | -0.36621 | -0.32501 | -0.18311 | -0.091553 | 121.5179 | 121.3074 | 60.5759 | -121.4264 | 121.3715 | 121.3623 | 60.5347 | -121.5958
285.5469 | 121.5088 | -60.5988 | 60.8688 | -0.00099167 | 0.0017646 | 0.069071 | 0.0029886 | 0.065351 | 0.0032856 | -0.0014484 | -0.008316 | 0.0038324 | 0.064457 | 0.066582 | -0.0070623 | -0.0051013 | 60.7864 | -60.3653 | 0.054932 | -60.6125 | 60.8597 | -60.6125 | -60.5576 | -60.8917 | 0.036621 | -60.878 | 60.7819 | 60.8139 | -60.5392 | -60.6995 | -0.013733 | 0.041199 | -0.009155 | 0.23346 | -0.013733 | -0.054932 | -0.082397 | 0.059509 | -0.10071 | -0.086975 | -0.29297 | -0.27924 | -0.17853 | -0.054931 | 121.4584 | 121.3852 | 60.6537 | -121.4264 | 121.3806 | 121.4127 | 60.6354 | -121.5683
287.2188 | 121.6049 | -60.5576 | 60.8368 | 0.014267 | 0.0036872 | 0.069284 | 0.003843 | 0.065779 | -0.00034604 | -0.0014484 | 0.0069425 | 0.0025508 | 0.063175 | 0.063805 | -0.0072759 | -0.0044605 | 60.7636 | -60.347 | 0.086975 | -60.5896 | 60.8871 | -60.5942 | -60.5621 | -60.8688 | 0.091553 | -60.8231 | 60.7727 | 60.8185 | -60.498 | -60.7132 | -0.036621 | -0.004578 | 0.050354 | 0.21057 | -0.032044 | -0.027466 | -0.073242 | 0.059509 | -0.15564 | -0.064087 | -0.31128 | -0.2655 | -0.10986 | -0.018311 | 121.4447 | 121.3211 | 60.6445 | -121.3989 | 121.3303 | 121.376 | 60.6491 | -121.55
288.9062 | 121.6278 | -60.5667 | 60.8276 | 0.021896 | 0.0064642 | 0.070993 | 0.0085428 | 0.064497 | -0.0067548 | -0.0018756 | -0.00068649 | -0.0010808 | 0.063388 | 0.065728 | -0.012403 | -0.0046741 | 60.7636 | -60.2692 | 0.11444 | -60.5576 | 60.7956 | -60.5896 | -60.5484 | -60.8734 | 0.15564 | -60.7544 | 60.6995 | 60.7407 | -60.5347 | -60.6903 | -0.022889 | 0.01831 | -0.032044 | 0.29755 | 0.009155 | -0.009155 | -0.064087 | 0.032043 | -0.1236 | -0.12817 | -0.3067 | -0.18768 | -0.064087 | -0.086975 | 121.3623 | 121.3303 | 60.6812 | -121.376 | 121.2662 | 121.3074 | 60.7224 | -121.5179
290.6094 | 121.5317 | -60.5484 | 60.878 | -0.00099167 | 0.0030464 | 0.068216 | 0.0040566 | 0.062147 | 0.0026446 | -0.001662 | 0.0069425 | 0.0036188 | 0.064029 | 0.066582 | -0.0074897 | -0.0063831 | 60.7956 | -60.3195 | 0.068665 | -60.5667 | 60.8734 | -60.5713 | -60.5255 | -60.8597 | 0.054932 | -60.8322 | 60.8139 | 60.8231 | -60.4706 | -60.6812 | -0.022888 | 0.022888 | -0.004578 | 0.22888 | -0.01831 | -0.041198 | -0.082398 | 0.07782 | -0.13275 | -0.064087 | -0.31128 | -0.28381 | -0.15106 | -0.054932 | 121.4218 | 121.344 | 60.6171 | -121.4035 | 121.3623 | 121.3715 | 60.6033 | -121.5591
292.2812 | 121.6278 | -60.5072 | 60.8963 | 0.0066373 | 0.0039008 | 0.072489 | 0.0040566 | 0.063002 | -0.002055 | -0.0023028 | 0.0069425 | 0.0016962 | 0.062748 | 0.064873 | -0.012403 | -0.0029651 | 60.7178 | -60.3607 | 0.013733 | -60.5896 | 60.9009 | -60.5667 | -60.5301 | -60.9329 | 0.050354 | -60.8414 | 60.8276 | 60.8231 | -60.5255 | -60.6903 | -0.059509 | -0.022888 | 0.004578 | 0.14648 | -0.082398 | -0.05951 | -0.17853 | -0.018311 | -0.18311 | -0.068664 | -0.42572 | -0.33417 | -0.15106 | -0.073242 | 121.4081 | 121.225 | 60.5209 | -121.4264 | 121.3348 | 121.3303 | 60.5576 | -121.5866
293.9531 | 121.5042 | -60.5255 | 60.9375 | 0.0066373 | 0.0041144 | 0.069712 | 0.0029886 | 0.06706 | 0.002431 | -0.00038024 | 0.0069425 | 0.00041436 | 0.065738 | 0.065941 | -0.0091985 | -0.0038195 | 60.7773 | -60.3424 | 0.032043 | -60.553 | 60.9238 | -60.553 | -60.5072 | -60.8917 | 0 | -60.8459 | 60.8368 | 60.8414 | -60.4706 | -60.6766 | -0.027466 | 0.018311 | -0.013733 | 0.18311 | -0.027466 | -0.045777 | -0.16022 | 0.054932 | -0.15106 | -0.10071 | -0.36621 | -0.32043 | -0.16937 | -0.09613 | 121.4493 | 121.3028 | 60.5576 | -121.4447 | 121.3623 | 121.3669 | 60.5255 | -121.6141
295.6406 | 121.5958 | -60.5072 | 60.9009 | -0.00099167 | 0.0047552 | 0.07313 | 0.0074746 | 0.066633 | -0.007182 | -0.0012346 | 0.014572 | -0.0012946 | 0.063816 | 0.063591 | -0.013471 | -0.0031787 | 60.8185 | -60.2097 | 0.11444 | -60.5118 | 60.8551 | -60.5301 | -60.4889 | -60.8231 | 0.17853 | -60.7086 | 60.7773 | 60.7956 | -60.4568 | -60.6354 | -0.022888 | 0.01831 | -0.045776 | 0.29755 | -0.004578 | -0.022888 | -0.082398 | 0.050354 | -0.12817 | -0.1236 | -0.31586 | -0.20142 | -0.073242 | -0.10529 | 121.3623 | 121.3257 | 60.6216 | -121.3898 | 121.2845 | 121.3028 | 60.6857 | -121.5363
297.3125 | 121.6415 | -60.4889 | 60.9009 | 0.0066373 | 0.0071052 | 0.074198 | 0.0036294 | 0.062361 | -0.005473 | -0.0046526 | 0.0069425 | 0.00041436 | 0.060825 | 0.064873 | -0.010908 | -0.0051013 | 60.8276 | -60.2142 | 0.07782 | -60.5072 | 60.8917 | -60.5301 | -60.4797 | -60.7864 | 0.15564 | -60.6628 | 60.759 | 60.8231 | -60.434 | -60.6079 | -0.041198 | 0.009156 | -0.009155 | 0.27466 | -0.01831 | -0.027466 | -0.073242 | 0.054932 | -0.11902 | -0.14191 | -0.29755 | -0.17395 | -0.054932 | -0.07782 | 121.3806 | 121.3165 | 60.5667 | -121.3806 | 121.2479 | 121.312 | 60.6445 | -121.5088
298.9844 | 121.6232 | -60.4706 | 60.91 | 0.0066373 | 0.007746 | 0.071848 | 0.0064066 | 0.06407 | -0.0026958 | -0.0037982 | 0.0069425 | -0.00086724 | 0.064884 | 0.064232 | -0.010053 | -0.0053149 | 60.8276 | -60.2509 | 0.041199 | -60.498 | 60.9146 | -60.5255 | -60.466 | -60.7956 | 0.1236 | -60.6766 | 60.8322 | 60.8368 | -60.4248 | -60.5896 | -0.054932 | 0.004578 | 0.004578 | 0.21973 | -0.027466 | -0.032044 | -0.082397 | 0.045776 | -0.11902 | -0.07782 | -0.32501 | -0.20599 | -0.086975 | -0.073242 | 121.3852 | 121.2982 | 60.5118 | -121.376 | 121.3028 | 121.3074 | 60.5942 | -121.4996
300.6562 | 121.5591 | -60.4843 | 60.9421 | 0.0066373 | 0.007746 | 0.070353 | -0.0010702 | 0.064497 | 0.001363 | -0.0046526 | 0.0069425 | -0.00044004 | 0.063816 | 0.065941 | -0.0066351 | -0.0053149 | 60.8597 | -60.2829 | -0.018311 | -60.5118 | 60.965 | -60.4889 | -60.4248 | -60.7681 | 0.018311 | -60.6903 | 60.8643 | 60.8597 | -60.4065 | -60.585 | -0.004578 | 0.059509 | 0.022888 | 0.20142 | -0.027466 | -0.086975 | -0.082398 | 0.07782 | -0.10071 | -0.07782 | -0.28381 | -0.20599 | -0.10529 | -0.082398 | 121.4493 | 121.344 | 60.466 | -121.3669 | 121.3486 | 121.344 | 60.5026 | -121.5271
302.3281 | 121.5546 | -60.4431 | 60.965 | 0.0066373 | 0.0083868 | 0.070139 | 0.002134 | 0.064711 | 0.0037128 | -0.00080744 | -0.00068649 | 0.0025508 | 0.062961 | 0.064446 | -0.0064215 | -0.0057421 | 60.8688 | -60.2875 | -0.045776 | -60.498 | 60.997 | -60.4706 | -60.4385 | -60.7773 | -0.032043 | -60.7498 | 60.9238 | 60.9512 | -60.3973 | -60.5621 | -0.027466 | 0.004577 | 0.032043 | 0.15564 | -0.054932 | -0.059509 | -0.096131 | 0.045776 | -0.11902 | -0.041199 | -0.33417 | -0.3067 | -0.18768 | -0.013733 | 121.4401 | 121.3119 | 60.3973 | -121.4035 | 121.3669 | 121.3943 | 60.4111 | -121.5271
304 | 121.5683 | -60.4019 | 61.0565 | 0.0066373 | 0.0053962 | 0.068003 | 0.0029886 | 0.064924 | 0.0028584 | -0.00080744 | 0.014572 | 0.0027644 | 0.06467 | 0.066155 | -0.0079169 | -0.0055285 | 60.9604 | -60.1685 | 0.07782 | -60.4202 | 61.0474 | -60.4065 | -60.379 | -60.7224 | 0.064087 | -60.6857 | 60.9604 | 60.9558 | -60.3378 | -60.5438 | -0.004577 | 0.022889 | -0.009156 | 0.23346 | -0.01831 | -0.041199 | -0.096131 | 0.064087 | -0.14191 | -0.096131 | -0.32043 | -0.28381 | -0.14191 | -0.10071 | 121.4493 | 121.3623 | 60.4797 | -121.4355 | 121.3623 | 121.3577 | 60.466 | -121.6003
305.6719 | 121.637 | -60.3241 | 61.0519 | 0.014267 | 0.004328 | 0.068003 | 0.0068338 | 0.065351 | 0.001363 | -0.00080744 | -0.00068649 | 0.00084176 | 0.065311 | 0.067009 | -0.0098395 | -0.0063831 | 60.91 | -60.2097 | 0.045776 | -60.3882 | 61.0886 | -60.379 | -60.3653 | -60.6949 | 0.07782 | -60.6491 | 60.9741 | 61.0245 | -60.3195 | -60.5118 | -0.054931 | -0.041198 | 0.036621 | 0.11444 | -0.064087 | -0.022889 | -0.14191 | 0.004578 | -0.18768 | -0.07782 | -0.37079 | -0.32501 | -0.13733 | -0.027466 | 121.4127 | 121.2341 | 60.3699 | -121.4172 | 121.2982 | 121.3486 | 60.4019 | -121.5637
307.3438 | 121.5775 | -60.3424 | 61.0474 | 0.0066373 | 0.0041144 | 0.073557 | 0.007261 | 0.063643 | -0.0048322 | -0.0029436 | -0.00068649 | -0.0023626 | 0.064029 | 0.066368 | -0.013471 | -0.0031787 | 60.9695 | -60.0723 | 0.1236 | -60.3516 | 61.0291 | -60.3745 | -60.3195 | -60.6583 | 0.16937 | -60.553 | 60.9375 | 60.965 | -60.2966 | -60.5026 | -0.032044 | 0.022888 | -0.01831 | 0.27008 | -0.009155 | -0.032043 | -0.07782 | 0.045776 | -0.16022 | -0.10986 | -0.31586 | -0.21057 | -0.050354 | -0.082397 | 121.3715 | 121.3119 | 60.466 | -121.3669 | 121.2799 | 121.3074 | 60.5118 | -121.55
309.0156 | 121.6141 | -60.3378 | 61.0565 | -0.00099167 | 0.006037 | 0.07313 | 0.0074746 | 0.065138 | -0.0039776 | -0.0025164 | -0.00068649 | -0.003858 | 0.064884 | 0.064019 | -0.011762 | -0.0068103 | 60.997 | -60.0357 | 0.11902 | -60.3195 | 61.0519 | -60.347 | -60.2966 | -60.6171 | 0.17853 | -60.5255 | 60.9512 | 60.965 | -60.2646 | -60.4614 | -0.009155 | 0.041199 | -0.004578 | 0.30212 | 0.018311 | -0.022888 | -0.05951 | 0.073243 | -0.1236 | -0.10529 | -0.27923 | -0.18768 | -0.064087 | -0.091553 | 121.3898 | 121.3348 | 60.4568 | -121.3531 | 121.2891 | 121.3028 | 60.5164 | -121.5179
310.6875 | 121.55 | -60.3149 | 61.116 | 0.021896 | 0.0081732 | 0.070566 | 0.0068338 | 0.065779 | -0.0033368 | -0.0040118 | 0.014572 | -0.0019354 | 0.063388 | 0.064659 | -0.011549 | -0.0063831 | 60.9695 | -60.0998 | 0.018311 | -60.347 | 61.084 | -60.3378 | -60.2921 | -60.6491 | 0.036621 | -60.5484 | 61.0016 | 61.0016 | -60.2371 | -60.466 | -0.022889 | 0.022888 | -0.032044 | 0.21515 | -0.032044 | -0.054932 | -0.14648 | 0.077819 | -0.15106 | -0.11444 | -0.33417 | -0.23346 | -0.082398 | -0.11444 | 121.3989 | 121.2845 | 60.3333 | -121.4081 | 121.3165 | 121.3165 | 60.3516 | -121.582
312.375 | 121.5088 | -60.2737 | 61.2167 | 0.0066373 | 0.006037 | 0.066721 | 0.0025612 | 0.063856 | 0.0056354 | 0.00026056 | -0.015945 | 0.006396 | 0.063602 | 0.065087 | -0.0064215 | -0.0068103 | 61.0382 | -60.1181 | -0.027466 | -60.3058 | 61.203 | -60.2692 | -60.2554 | -60.6262 | -0.045776 | -60.5988 | 61.1252 | 61.1435 | -60.1822 | -60.4019 | 0.004578 | 0.018311 | -0.013733 | 0.15564 | -0.032043 | -0.050354 | -0.17853 | 0.091553 | -0.12817 | -0.091553 | -0.35248 | -0.32501 | -0.19684 | -0.073242 | 121.4767 | 121.312 | 60.2463 | -121.4722 | 121.3989 | 121.4172 | 60.228 | -121.6187
314.0469 | 121.6507 | -60.1776 | 61.1984 | 0.0066373 | 0.0045416 | 0.068644 | 0.0066202 | 0.065138 | 0.0032856 | -0.0014484 | 0.014572 | 0.004046 | 0.065738 | 0.068505 | -0.0087713 | -0.0040331 | 61.0748 | -60.0174 | 0.045776 | -60.2371 | 61.2442 | -60.2325 | -60.1959 | -60.5438 | 0.068665 | -60.4752 | 61.1526 | 61.171 | -60.1273 | -60.3241 | -0.054932 | -0.018311 | 0.045777 | 0.16022 | -0.05951 | -0.041199 | -0.1236 | 0.050354 | -0.14648 | -0.045776 | -0.36621 | -0.29755 | -0.15106 | -0.027466 | 121.4218 | 121.2524 | 60.2234 | -121.3943 | 121.3303 | 121.3486 | 60.2463 | -121.5225
315.75 | 121.5088 | -60.1685 | 61.2854 | -0.00099167 | 0.0058234 | 0.069712 | 0.0032022 | 0.063643 | 0.0032856 | -0.00080744 | -0.00068649 | 0.0021234 | 0.065525 | 0.066368 | -0.0070623 | -0.0046741 | 61.116 | -59.9762 | 0.032043 | -60.1868 | 61.2717 | -60.1868 | -60.1456 | -60.5255 | 0.009155 | -60.498 | 61.1893 | 61.2076 | -60.1181 | -60.3241 | -0.018311 | 0.022888 | -0.013733 | 0.19226 | -0.018311 | -0.041199 | -0.16937 | 0.050354 | -0.15564 | -0.09613 | -0.35706 | -0.32959 | -0.17395 | -0.077819 | 121.4401 | 121.2845 | 60.2005 | -121.431 | 121.3577 | 121.376 | 60.1776 | -121.6095
317.4844 | 121.5271 | -60.1501 | 61.3083 | -0.00099167 | 0.0053962 | 0.069498 | 0.0029886 | 0.065565 | -0.00013244 | -0.001021 | 0.0069425 | 0.0031916 | 0.062748 | 0.064873 | -0.0062079 | -0.0031787 | 61.1252 | -59.9762 | -0.036621 | -60.1822 | 61.322 | -60.173 | -60.1181 | -60.4843 | -0.027466 | -60.4568 | 61.2122 | 61.2625 | -60.0861 | -60.2692 | -0.022889 | 0.032043 | 0.013732 | 0.17395 | -0.032044 | -0.064087 | -0.18311 | 0.064086 | -0.11902 | -0.096131 | -0.33417 | -0.3067 | -0.18768 | -0.045777 | 121.4722 | 121.2753 | 60.1135 | -121.4264 | 121.3623 | 121.4127 | 60.1227 | -121.5775
319.1562 | 121.5363 | -60.0998 | 61.3541 | 0.0066373 | 0.0071052 | 0.070139 | 0.001066 | 0.064497 | -0.00055964 | -0.0014484 | -0.00068649 | 0.002978 | 0.063175 | 0.065728 | -0.0072759 | -0.0029651 | 61.1847 | -59.9396 | -0.032043 | -60.141 | 61.3861 | -60.1044 | -60.0815 | -60.4614 | -0.036621 | -60.3836 | 61.2625 | 61.2854 | -60.0494 | -60.2325 | -0.004578 | 0.01831 | 0.032043 | 0.16022 | -0.041199 | -0.059509 | -0.16937 | 0.050354 | -0.13275 | -0.091553 | -0.36163 | -0.28381 | -0.15106 | -0.068665 | 121.4859 | 121.2845 | 60.0677 | -121.4355 | 121.3623 | 121.3852 | 60.0632 | -121.5866
320.8281 | 121.5683 | -60.0311 | 61.3907 | 0.014267 | 0.0047552 | 0.072489 | 0.010465 | 0.064924 | -0.0044048 | -0.0018756 | 0.0069425 | -0.0023626 | 0.064457 | 0.063805 | -0.013898 | -0.0044605 | 61.2808 | -59.7427 | 0.11444 | -60.0082 | 61.3449 | -60.0586 | -59.9945 | -60.3745 | 0.15564 | -60.2417 | 61.2762 | 61.3129 | -59.9991 | -60.1685 | -0.027466 | 0.036621 | -0.045776 | 0.28839 | 0.022888 | -0.013733 | -0.10986 | 0.032044 | -0.13733 | -0.11444 | -0.34332 | -0.21057 | -0.073242 | -0.07782 | 121.376 | 121.312 | 60.1456 | -121.3852 | 121.3074 | 121.344 | 60.1868 | -121.5591
322.5469 | 121.6324 | -59.9121 | 61.4731 | 0.0066373 | 0.0034736 | 0.071848 | 0.0032022 | 0.063856 | 0.00072196 | -0.0042254 | 0.014572 | 0.0021234 | 0.062748 | 0.065087 | -0.0079169 | -0.0063831 | 61.3312 | -59.7702 | 0.041199 | -59.967 | 61.5005 | -59.9854 | -59.9579 | -60.3195 | 0.073242 | -60.2463 | 61.3724 | 61.4044 | -59.9213 | -60.1044 | -0.073243 | -0.045777 | 0.027466 | 0.14191 | -0.054932 | -0.009155 | -0.14191 | -0.009156 | -0.19226 | -0.10071 | -0.40741 | -0.33417 | -0.14191 | -0.068664 | 121.4127 | 121.2433 | 59.9533 | -121.431 | 121.2845 | 121.3165 | 59.9854 | -121.5775
324.2188 | 121.6415 | -59.8938 | 61.5097 | 0.0066373 | 0.0047552 | 0.068857 | 0.0076882 | 0.064283 | 8.1158e-05 | -0.0020892 | 0.014572 | 0.0038324 | 0.065952 | 0.067864 | -0.0094123 | -0.0046741 | 61.3312 | -59.761 | 0.022888 | -59.967 | 61.5326 | -59.9487 | -59.8938 | -60.2921 | 0.041199 | -60.2188 | 61.4548 | 61.4685 | -59.8801 | -60.0449 | -0.054931 | 0 | 0.022888 | 0.13275 | -0.073242 | -0.073242 | -0.17853 | 0.013733 | -0.15106 | -0.054932 | -0.39825 | -0.32501 | -0.17395 | -0.041199 | 121.4264 | 121.225 | 59.9167 | -121.4035 | 121.3486 | 121.3623 | 59.935 | -121.5546
325.8906 | 121.5637 | -59.8251 | 61.5601 | 0.014267 | 0.0047552 | 0.070566 | 0.0081154 | 0.063215 | -0.0026958 | -0.0035846 | 0.0069425 | -0.0010808 | 0.065525 | 0.065087 | -0.010694 | -0.0025379 | 61.4044 | -59.6558 | 0.041199 | -59.903 | 61.5646 | -59.8892 | -59.8251 | -60.26 | 0.073242 | -60.1456 | 61.5097 | 61.5326 | -59.8206 | -60.0082 | -0.064087 | 0 | 0.004577 | 0.16937 | -0.07782 | -0.07782 | -0.15564 | 0.004577 | -0.18311 | -0.050354 | -0.43488 | -0.32044 | -0.13733 | -0.027466 | 121.3898 | 121.2296 | 59.8663 | -121.3852 | 121.3348 | 121.3577 | 59.8984 | -121.5683
327.5625 | 121.5134 | -59.8343 | 61.615 | 0.0066373 | 0.010096 | 0.070993 | 0.0044838 | 0.063856 | -0.007182 | -0.0048662 | 0.022202 | -0.0025762 | 0.062961 | 0.066582 | -0.011121 | -0.0038195 | 61.4502 | -59.6146 | -0.004578 | -59.8709 | 61.5646 | -59.8526 | -59.7794 | -60.1822 | 0.027466 | -60.0677 | 61.4914 | 61.5051 | -59.7565 | -59.9716 | -0.01831 | 0.054932 | -0.050354 | 0.21973 | -0.036621 | -0.091553 | -0.16479 | 0.07782 | -0.13733 | -0.1236 | -0.3479 | -0.23346 | -0.09613 | -0.10986 | 121.3989 | 121.2845 | 59.8297 | -121.3943 | 121.3257 | 121.3394 | 59.8618 | -121.5866
329.2344 | 121.5683 | -59.7519 | 61.6379 | 0.014267 | 0.0079596 | 0.072275 | 0.0032022 | 0.061293 | -0.0044048 | -0.0055072 | 0.0069425 | -0.0015082 | 0.063816 | 0.065514 | -0.011549 | -0.0059557 | 61.5097 | -59.5825 | 0 | -59.8022 | 61.6379 | -59.7702 | -59.7473 | -60.1135 | 0.050354 | -59.9991 | 61.5646 | 61.5738 | -59.697 | -59.8663 | -0.018311 | 0.004578 | 0 | 0.16937 | -0.050354 | -0.054932 | -0.12817 | 0.054932 | -0.11444 | -0.073242 | -0.36163 | -0.24719 | -0.13275 | -0.064086 | 121.3898 | 121.2616 | 59.7519 | -121.3852 | 121.3165 | 121.3257 | 59.8022 | -121.5042
330.9219 | 121.55 | -59.6878 | 61.7615 | -0.00099167 | 0.0098822 | 0.067362 | 0.0023476 | 0.065138 | 0.003072 | -0.0014484 | 0.0069425 | 0.0027644 | 0.06232 | 0.066155 | -0.0053533 | -0.0059557 | 61.6196 | -59.5688 | -0.032043 | -59.7473 | 61.7706 | -59.7015 | -59.6512 | -60.0494 | -0.041199 | -60.0037 | 61.6928 | 61.702 | -59.642 | -59.8434 | -0.013733 | 0.036621 | 0.009155 | 0.11902 | -0.059509 | -0.09613 | -0.14191 | 0.045776 | -0.15564 | -0.068665 | -0.36163 | -0.31586 | -0.16022 | -0.05951 | 121.4584 | 121.3074 | 59.6558 | -121.4127 | 121.3806 | 121.3898 | 59.6466 | -121.6049
332.5938 | 121.5134 | -59.61 | 61.8942 | 0.014267 | 0.0041144 | 0.071634 | 0.003843 | 0.063856 | 0.0015766 | 0.00047416 | 0.0069425 | 0.002337 | 0.064884 | 0.066796 | -0.0070623 | -0.0044605 | 61.702 | -59.4406 | 0 | -59.6512 | 61.8713 | -59.6146 | -59.5642 | -59.9442 | -0.022888 | -59.9304 | 61.7935 | 61.7889 | -59.5413 | -59.729 | -0.004578 | 0.045776 | -0.022888 | 0.16937 | -0.041199 | -0.086975 | -0.19226 | 0.068664 | -0.11902 | -0.10071 | -0.33417 | -0.32043 | -0.20142 | -0.10529 | 121.4813 | 121.3119 | 59.61 | -121.4584 | 121.4035 | 121.3989 | 59.5871 | -121.6232
334.3125 | 121.5408 | -59.5413 | 61.8759 | 0.0066373 | 0.010309 | 0.074625 | 0.0061928 | 0.062574 | -0.0067548 | -0.0014484 | 0.0069425 | -0.0036444 | 0.062961 | 0.062523 | -0.010908 | -0.0042467 | 61.7294 | -59.3536 | 0.004578 | -59.5734 | 61.8576 | -59.5734 | -59.523 | -59.903 | 0.041199 | -59.7794 | 61.7752 | 61.7935 | -59.5047 | -59.6741 | -0.032043 | 0.018311 | -0.018311 | 0.18768 | -0.032043 | -0.050354 | -0.14648 | 0.036621 | -0.13275 | -0.10071 | -0.36163 | -0.23804 | -0.10529 | -0.082398 | 121.3989 | 121.2708 | 59.5459 | -121.3989 | 121.3165 | 121.3348 | 59.5825 | -121.55
336.0156 | 121.5042 | -59.5001 | 62.0087 | 0.0066373 | 0.0056098 | 0.07078 | 0.0014932 | 0.06407 | 0.0011494 | -0.0014484 | 0.0069425 | 0.0031916 | 0.062748 | 0.065941 | -0.0083441 | -0.0072375 | 61.8073 | -59.3719 | -0.027466 | -59.5367 | 62.0041 | -59.4772 | -59.4589 | -59.848 | -0.041199 | -59.7839 | 61.908 | 61.9354 | -59.4315 | -59.61 | 0.022888 | 0.041199 | -0.004578 | 0.12817 | -0.036621 | -0.07782 | -0.20142 | 0.068664 | -0.10986 | -0.10071 | -0.3479 | -0.28381 | -0.17395 | -0.073242 | 121.5042 | 121.3074 | 59.4727 | -121.4676 | 121.4081 | 121.4355 | 59.4589 | -121.6187
337.6875 | 121.5408 | -59.4269 | 62.0682 | 0.0066373 | 0.0064642 | 0.070139 | 0.0044838 | 0.06407 | 0.00050836 | -0.001021 | -0.00068649 | 0.002978 | 0.064029 | 0.066155 | -0.0068487 | -0.0044605 | 61.8896 | -59.2667 | -0.013733 | -59.4406 | 62.0636 | -59.3903 | -59.3811 | -59.7565 | -0.045776 | -59.7153 | 61.9904 | 61.9904 | -59.3491 | -59.5276 | 0.036621 | 0.045776 | -0.004577 | 0.16022 | -0.013733 | -0.059509 | -0.17853 | 0.07782 | -0.10071 | -0.07782 | -0.32959 | -0.28839 | -0.18768 | -0.07782 | 121.4905 | 121.3165 | 59.4131 | -121.4493 | 121.4172 | 121.4172 | 59.3811 | -121.5958
339.375 | 121.5363 | -59.3216 | 62.1185 | 0.0066373 | 0.0079596 | 0.071848 | 0.002134 | 0.065138 | -0.00013244 | -0.0018756 | 0.0069425 | 0.00062796 | 0.060184 | 0.064019 | -0.0098395 | -0.0029651 | 62.0407 | -59.0652 | 0.054932 | -59.3079 | 62.0773 | -59.3124 | -59.2712 | -59.5963 | 0.064087 | -59.5413 | 61.9675 | 61.9904 | -59.2438 | -59.436 | 0.009155 | 0.050354 | -0.041198 | 0.25635 | 0.013733 | -0.036621 | -0.07782 | 0.07782 | -0.11444 | -0.15106 | -0.27466 | -0.21973 | -0.10529 | -0.12817 | 121.3989 | 121.3623 | 59.3765 | -121.3898 | 121.2891 | 121.3119 | 59.3857 | -121.5546
341.0469 | 121.6003 | -59.1797 | 62.1826 | -0.016251 | 0.0053962 | 0.070353 | 0.0059792 | 0.064497 | -0.0041912 | -0.00508 | 0.014572 | -0.0034308 | 0.063388 | 0.066582 | -0.010267 | -0.0055285 | 62.1094 | -58.9645 | 0.11444 | -59.2392 | 62.1277 | -59.2484 | -59.1934 | -59.5139 | 0.16022 | -59.4315 | 62.0407 | 62.1048 | -59.1568 | -59.3491 | -0.068665 | -0.013733 | -0.054931 | 0.21515 | -0.05951 | -0.045777 | -0.073242 | 0.022888 | -0.16937 | -0.14191 | -0.33417 | -0.25177 | -0.082398 | -0.07782 | 121.3074 | 121.2891 | 59.2941 | -121.376 | 121.2204 | 121.2845 | 59.3399 | -121.5317
342.7188 | 121.5729 | -59.1476 | 62.265 | 0.0066373 | 0.0096686 | 0.072916 | 0.0057656 | 0.065138 | -0.0044048 | -0.0035846 | 0.0069425 | -0.002149 | 0.064884 | 0.064446 | -0.012403 | -0.0055285 | 62.1094 | -58.9828 | -0.004578 | -59.2026 | 62.2421 | -59.1934 | -59.1293 | -59.5184 | 0.068665 | -59.3948 | 62.146 | 62.1872 | -59.0927 | -59.2896 | -0.045776 | 0.018311 | -0.022889 | 0.16479 | -0.054932 | -0.073243 | -0.15564 | 0.054932 | -0.14191 | -0.11902 | -0.37079 | -0.24719 | -0.10528 | -0.07782 | 121.3898 | 121.257 | 59.1431 | -121.3943 | 121.2936 | 121.3348 | 59.2163 | -121.5546
344.4531 | 121.5134 | -59.0469 | 62.4161 | -0.00099167 | 0.0036872 | 0.068644 | 0.0029886 | 0.06706 | 0.0045674 | -0.0020892 | 0.0069425 | 0.0036188 | 0.063816 | 0.065514 | -0.0064215 | -0.0080921 | 62.2925 | -58.8684 | 0.041199 | -59.0881 | 62.4161 | -59.0378 | -59.0378 | -59.3719 | -0.013733 | -59.3582 | 62.3154 | 62.3428 | -59.0286 | -59.1705 | 0.009155 | 0.009155 | 0 | 0.17853 | -0.041199 | -0.050354 | -0.1236 | 0.018311 | -0.1236 | -0.10071 | -0.32501 | -0.31128 | -0.18768 | -0.073243 | 121.463 | 121.3394 | 59.0881 | -121.4539 | 121.3623 | 121.3898 | 59.0332 | -121.5866
346.125 | 121.5363 | -58.9828 | 62.4619 | 0.014267 | 0.0096686 | 0.070139 | 0.00063865 | 0.062574 | 0.00029476 | -0.00059384 | -0.00068649 | -0.00065364 | 0.061679 | 0.064659 | -0.0062079 | -0.0059557 | 62.4069 | -58.7036 | 0.054932 | -58.96 | 62.439 | -58.9508 | -58.9188 | -59.2209 | 0.07782 | -59.166 | 62.3199 | 62.3657 | -58.9096 | -59.0698 | 0.032043 | 0.064087 | -0.022888 | 0.27924 | 0.022888 | -0.041199 | -0.054932 | 0.073242 | -0.086975 | -0.14191 | -0.23804 | -0.18311 | -0.096131 | -0.09613 | 121.4218 | 121.3898 | 59.0378 | -121.3806 | 121.3028 | 121.3486 | 59.0607 | -121.5317
347.7969 | 121.5088 | -58.8593 | 62.6083 | 0.014267 | 0.0034736 | 0.067789 | 0.00085245 | 0.064497 | 0.0026446 | -0.00059384 | -0.00068649 | 0.0034052 | 0.063816 | 0.065941 | -0.0072759 | -0.0044605 | 62.4344 | -58.699 | 0 | -58.905 | 62.6038 | -58.8547 | -58.8409 | -59.2026 | -0.022888 | -59.1843 | 62.5122 | 62.5534 | -58.7814 | -58.9966 | 0.004578 | 0.018311 | -0.004577 | 0.16022 | -0.045776 | -0.064087 | -0.17395 | 0.07782 | -0.13733 | -0.09613 | -0.34332 | -0.32501 | -0.18768 | -0.054931 | 121.463 | 121.2936 | 58.8593 | -121.4493 | 121.3715 | 121.4127 | 58.8364 | -121.6049
349.5312 | 121.5408 | -58.7769 | 62.6862 | 0.0066373 | 0.0064642 | 0.07078 | 0.0042702 | 0.065351 | -0.0016278 | -0.0023028 | 0.014572 | 0.0027644 | 0.063388 | 0.066796 | -0.0070623 | -0.0038195 | 62.5076 | -58.6258 | -0.041199 | -58.8181 | 62.709 | -58.7906 | -58.7402 | -59.1339 | -0.054932 | -59.0973 | 62.59 | 62.6312 | -58.7036 | -58.905 | -0.013733 | 0.036621 | 0.022888 | 0.15106 | -0.041199 | -0.07782 | -0.17853 | 0.073242 | -0.12817 | -0.09613 | -0.35706 | -0.32044 | -0.19226 | -0.054931 | 121.4859 | 121.2845 | 58.7357 | -121.4264 | 121.3669 | 121.4081 | 58.7219 | -121.5912
351.2031 | 121.5088 | -58.6716 | 62.7823 | -0.00099167 | 0.0041144 | 0.069712 | 0.0034158 | 0.06407 | 0.00029476 | -0.00038024 | -0.00068649 | 0.002337 | 0.065952 | 0.063591 | -0.0062079 | -0.0029651 | 62.6083 | -58.5251 | -0.027466 | -58.7082 | 62.796 | -58.6761 | -58.6441 | -59.0469 | -0.032043 | -58.9828 | 62.7319 | 62.7228 | -58.5938 | -58.7997 | -0.004577 | 0.027466 | 0.013733 | 0.14649 | -0.036621 | -0.064087 | -0.17395 | 0.07782 | -0.12817 | -0.050354 | -0.37537 | -0.31128 | -0.18311 | -0.05951 | 121.4676 | 121.2799 | 58.6441 | -121.4264 | 121.4035 | 121.3943 | 58.6395 | -121.582
352.8906 | 121.5042 | -58.5938 | 62.8693 | 0.0066373 | 0.0083868 | 0.071634 | 0.0032022 | 0.065565 | -0.0041912 | -0.0020892 | 0.0069425 | 0.00020076 | 0.061679 | 0.063805 | -0.0087713 | -0.0031787 | 62.7914 | -58.3054 | 0.064087 | -58.5434 | 62.8143 | -58.548 | -58.5068 | -58.8272 | 0.09613 | -58.7494 | 62.7365 | 62.7777 | -58.4702 | -58.6441 | 0.045776 | 0.086975 | -0.054932 | 0.28839 | 0.050354 | -0.036621 | -0.07782 | 0.1236 | -0.050354 | -0.13275 | -0.23346 | -0.15564 | -0.10529 | -0.091553 | 121.4081 | 121.3852 | 58.6578 | -121.376 | 121.3303 | 121.3715 | 58.6899 | -121.5134
354.5938 | 121.4951 | -58.4473 | 63.0066 | 0.0066373 | 0.004328 | 0.073343 | 0.0040566 | 0.065565 | 0.0032856 | 4.696e-05 | 0.0069425 | 0.00084176 | 0.06467 | 0.0653 | -0.0079169 | -0.0038195 | 62.8555 | -58.3237 | -0.018311 | -58.493 | 63.0249 | -58.4381 | -58.4106 | -58.8226 | -0.041199 | -58.786 | 62.9654 | 62.9745 | -58.3694 | -58.5617 | 0.009156 | 0.036621 | 0.01831 | 0.1236 | -0.045776 | -0.082397 | -0.15106 | 0.07782 | -0.11444 | -0.041199 | -0.37537 | -0.33875 | -0.2243 | -0.032044 | 121.4722 | 121.3028 | 58.429 | -121.4172 | 121.4127 | 121.4218 | 58.4061 | -121.5683
356.2812 | 121.5225 | -58.3191 | 63.1348 | 0.0066373 | 0.00326 | 0.068857 | 0.0029886 | 0.070478 | 0.0011494 | -0.0012346 | -0.00068649 | 0.0034052 | 0.062748 | 0.06765 | -0.0087713 | -0.0038195 | 62.9974 | -58.1039 | 0.068665 | -58.3649 | 63.1165 | -58.3328 | -58.3237 | -58.6487 | 0.041199 | -58.6258 | 63.0386 | 63.0661 | -58.287 | -58.4518 | -0.013733 | -0.004577 | -0.018311 | 0.21515 | -0.045776 | -0.041199 | -0.13733 | 0.032044 | -0.13275 | -0.096131 | -0.32959 | -0.3067 | -0.17395 | -0.068665 | 121.4355 | 121.3165 | 58.3878 | -121.4584 | 121.3577 | 121.3852 | 58.3603 | -121.5866
357.9844 | 121.6278 | -58.1909 | 63.1714 | 0.014267 | 0.0083868 | 0.072062 | 0.0064066 | 0.064924 | -0.005473 | -0.0042254 | -0.00068649 | -0.0023626 | 0.061252 | 0.06295 | -0.013044 | -0.0033923 | 63.0707 | -57.9987 | 0.045776 | -58.2321 | 63.1622 | -58.223 | -58.2047 | -58.5434 | 0.12817 | -58.4106 | 63.0707 | 63.1119 | -58.1635 | -58.3191 | -0.032043 | -0.013733 | -0.009156 | 0.19226 | -0.041199 | -0.027466 | -0.10071 | 0.027466 | -0.12817 | -0.10071 | -0.35248 | -0.21973 | -0.091553 | -0.05951 | 121.3531 | 121.2616 | 58.2367 | -121.376 | 121.2616 | 121.3028 | 58.3191 | -121.4905
359.6875 | 121.669 | -58.0399 | 63.3408 | -0.0086212 | 0.0034736 | 0.066294 | 0.0049112 | 0.06642 | 0.00072196 | -0.0029436 | -0.00068649 | 0.002978 | 0.066806 | 0.063378 | -0.01048 | -0.0065967 | 63.2126 | -57.9254 | 0.059509 | -58.1223 | 63.3957 | -58.1131 | -58.0261 | -58.4152 | 0.068665 | -58.3603 | 63.2904 | 63.327 | -58.0353 | -58.2275 | -0.073242 | 0.013733 | 0.054932 | 0.11444 | -0.082397 | -0.09613 | -0.12817 | 0.004578 | -0.18768 | -0.050354 | -0.37537 | -0.32043 | -0.13275 | -0.013733 | 121.4355 | 121.2524 | 58.0994 | -121.3669 | 121.3303 | 121.3669 | 58.1085 | -121.5683
361.3906 | 121.5546 | -57.9529 | 63.4827 | 0.0066373 | 0.0083868 | 0.070139 | 0.0049112 | 0.067701 | 8.1158e-05 | -0.00080744 | 0.0069425 | 0.0016962 | 0.065952 | 0.065941 | -0.0089849 | -0.0048877 | 63.3224 | -57.8156 | -0.045776 | -58.0124 | 63.5193 | -57.9712 | -57.9117 | -58.3054 | -0.050354 | -58.2458 | 63.414 | 63.4003 | -57.8888 | -58.049 | -0.01831 | 0.041199 | 0.036621 | 0.13733 | -0.059509 | -0.10071 | -0.16022 | 0.064087 | -0.09613 | -0.068665 | -0.35248 | -0.29297 | -0.19684 | -0.082397 | 121.4722 | 121.2753 | 57.9071 | -121.3943 | 121.3669 | 121.3531 | 57.9025 | -121.5317
363.0625 | 121.5363 | -57.811 | 63.6383 | 0.014267 | 0.004969 | 0.070993 | 0.0019204 | 0.064924 | 0.001363 | -0.0014484 | -0.00068649 | 0.00041436 | 0.064029 | 0.065728 | -0.0077033 | -0.0048877 | 63.4598 | -57.6874 | -0.054932 | -57.8751 | 63.6658 | -57.8339 | -57.7744 | -58.1818 | -0.050354 | -58.1406 | 63.5605 | 63.5788 | -57.756 | -57.9208 | -0.022888 | 0.036621 | 0.027465 | 0.1236 | -0.064087 | -0.10071 | -0.17853 | 0.054932 | -0.10986 | -0.07782 | -0.37079 | -0.32959 | -0.21973 | -0.05951 | 121.4767 | 121.2708 | 57.756 | -121.4127 | 121.3715 | 121.3898 | 57.7606 | -121.5591
364.7344 | 121.5088 | -57.6736 | 63.7894 | -0.00099167 | 0.0058234 | 0.06843 | 0.0019204 | 0.06706 | 0.00050836 | -0.0020892 | 0.0069425 | 0.0031916 | 0.064457 | 0.065514 | -0.0085577 | -0.0042467 | 63.6017 | -57.55 | -0.022888 | -57.7515 | 63.8168 | -57.6828 | -57.6279 | -58.0215 | -0.045776 | -57.9849 | 63.6978 | 63.7619 | -57.6279 | -57.8018 | -0.009155 | 0.045776 | 0.027465 | 0.1236 | -0.07782 | -0.1236 | -0.18768 | 0.045776 | -0.12817 | -0.091553 | -0.3479 | -0.31128 | -0.1831 | -0.027466 | 121.4905 | 121.2753 | 57.6508 | -121.4172 | 121.3715 | 121.4355 | 57.6279 | -121.5912
366.4531 | 121.5134 | -57.5455 | 63.913 | -0.00099167 | 0.009455 | 0.071634 | 0.0019204 | 0.064711 | -0.0012006 | -0.0035846 | 0.0069425 | 0.001269 | 0.064243 | 0.064659 | -0.0094123 | -0.0059557 | 63.8397 | -57.2571 | 0.07782 | -57.5134 | 63.858 | -57.486 | -57.4493 | -57.7835 | 0.091553 | -57.7103 | 63.7711 | 63.826 | -57.4402 | -57.6141 | 0.059509 | 0.09613 | -0.054932 | 0.28839 | 0.032043 | -0.064087 | -0.073242 | 0.10529 | -0.068665 | -0.14191 | -0.23804 | -0.16479 | -0.09613 | -0.086975 | 121.4035 | 121.3852 | 57.6233 | -121.3623 | 121.3165 | 121.3715 | 57.637 | -121.5271
368.125 | 121.5042 | -57.4081 | 64.0411 | 0.0066373 | 0.009455 | 0.070993 | 0.00085245 | 0.065138 | -0.003764 | -0.0025164 | 0.0069425 | -1.2844e-05 | 0.062961 | 0.064659 | -0.0077033 | -0.0053149 | 63.9725 | -57.1198 | 0.07782 | -57.3807 | 64.0182 | -57.3715 | -57.3212 | -57.6553 | 0.086975 | -57.5729 | 63.9221 | 63.9587 | -57.3029 | -57.4905 | 0.036621 | 0.086975 | -0.022888 | 0.28839 | 0.027466 | -0.059509 | -0.068665 | 0.10529 | -0.082398 | -0.11902 | -0.24719 | -0.1648 | -0.082397 | -0.082398 | 121.4264 | 121.3806 | 57.486 | -121.3623 | 121.3303 | 121.3669 | 57.4951 | -121.5317
369.7969 | 121.5408 | -57.2342 | 64.2334 | 0.014267 | 0.0064642 | 0.069071 | 0.0017068 | 0.063429 | 0.0020038 | -0.0025164 | -0.008316 | 0.0031916 | 0.062748 | 0.065087 | -0.0087713 | -0.0059557 | 64.064 | -57.106 | -0.045776 | -57.2937 | 64.2609 | -57.2388 | -57.1976 | -57.5958 | -0.036621 | -57.5363 | 64.1739 | 64.1739 | -57.1747 | -57.3395 | -0.004578 | 0.036621 | 0.027466 | 0.12817 | -0.059509 | -0.09613 | -0.16937 | 0.059509 | -0.10529 | -0.059509 | -0.36163 | -0.30212 | -0.19684 | -0.059509 | 121.4951 | 121.2982 | 57.1884 | -121.431 | 121.4081 | 121.4081 | 57.1976 | -121.5729
371.5469 | 121.5912 | -56.955 | 64.4714 | -0.0086212 | 0.0021918 | 0.065653 | 0.0066202 | 0.06706 | 0.0011494 | -0.0012346 | 0.014572 | -0.00022644 | 0.065738 | 0.065514 | -0.0085577 | -0.0068103 | 64.357 | -56.7856 | 0.10071 | -57.0007 | 64.4531 | -56.9916 | -56.9366 | -57.2891 | 0.082397 | -57.2617 | 64.3616 | 64.3845 | -56.9412 | -57.1243 | -0.036621 | 0.01831 | -0.018311 | 0.16937 | -0.045776 | -0.064086 | -0.11444 | 0.013733 | -0.16937 | -0.10986 | -0.33417 | -0.3067 | -0.13733 | -0.086976 | 121.4081 | 121.312 | 57.0557 | -121.4081 | 121.3165 | 121.3394 | 57.0374 | -121.5958
373.2188 | 121.6187 | -56.8039 | 64.6179 | -0.00099167 | 0.0036872 | 0.068216 | 0.0064066 | 0.061506 | 0.0011494 | -0.0012346 | 0.0069425 | 0.0010554 | 0.066379 | 0.066582 | -0.0087713 | -0.0061695 | 64.4852 | -56.6391 | 0.07782 | -56.8451 | 64.6362 | -56.8268 | -56.8085 | -57.1381 | 0.09613 | -57.0831 | 64.5126 | 64.5584 | -56.7627 | -56.955 | -0.022888 | -0.004578 | 0.01831 | 0.16479 | -0.041199 | -0.036621 | -0.13275 | 0.041199 | -0.15106 | -0.10529 | -0.33417 | -0.27924 | -0.12817 | -0.059509 | 121.4401 | 121.2891 | 56.8817 | -121.4264 | 121.3165 | 121.3623 | 56.9 | -121.5729
374.9062 | 121.6232 | -56.6254 | 64.7415 | 0.0066373 | 0.006037 | 0.071207 | 0.0074746 | 0.064924 | -0.007182 | -0.0025164 | 0.014572 | -0.003858 | 0.065525 | 0.064659 | -0.013044 | -0.0042467 | 64.6683 | -56.369 | 0.11902 | -56.662 | 64.7141 | -56.6803 | -56.6345 | -56.955 | 0.1831 | -56.8405 | 64.6408 | 64.682 | -56.5979 | -56.781 | -0.054932 | -0.009155 | -0.027466 | 0.25635 | -0.036621 | -0.027466 | -0.073242 | 0.027466 | -0.15564 | -0.10071 | -0.32959 | -0.21515 | -0.059509 | -0.059509 | 121.3394 | 121.2936 | 56.7444 | -121.376 | 121.2662 | 121.3074 | 56.8085 | -121.5225
376.6094 | 121.5088 | -56.4835 | 65.0024 | -0.00099167 | 0.010737 | 0.073557 | 0.0036294 | 0.065779 | -0.0046184 | -0.0031574 | 0.014572 | -0.0032172 | 0.061252 | 0.0653 | -0.011549 | -0.0055285 | 64.8331 | -56.2683 | 0.022888 | -56.5018 | 64.9475 | -56.4697 | -56.4056 | -56.8039 | 0.032043 | -56.7032 | 64.8468 | 64.888 | -56.4102 | -56.5887 | 0.013732 | 0.077819 | -0.054931 | 0.21515 | -0.018311 | -0.09613 | -0.16937 | 0.073242 | -0.10529 | -0.15564 | -0.32043 | -0.21973 | -0.11444 | -0.11444 | 121.431 | 121.3165 | 56.5063 | -121.4081 | 121.3303 | 121.3715 | 56.5155 | -121.5912
378.2812 | 121.4951 | -56.2683 | 65.1947 | 0.0066373 | 0.0083868 | 0.070139 | 0.0012796 | 0.064924 | -0.0012006 | -0.0031574 | -0.00068649 | -0.00022644 | 0.060611 | 0.063591 | -0.0079169 | -0.0055285 | 65.0894 | -56.0165 | 0.054932 | -56.2637 | 65.126 | -56.25 | -56.2363 | -56.5292 | 0.082397 | -56.4743 | 65.0436 | 65.0894 | -56.1813 | -56.369 | 0.018311 | 0.032044 | -0.068664 | 0.25177 | 0.004578 | -0.027466 | -0.10529 | 0.086976 | -0.10071 | -0.15106 | -0.26093 | -0.20599 | -0.10528 | -0.10529 | 121.3943 | 121.3577 | 56.3232 | -121.431 | 121.312 | 121.3577 | 56.3507 | -121.5637
379.9688 | 121.55 | -56.0577 | 65.3641 | 0.0066373 | 0.0062506 | 0.071634 | 0.0032022 | 0.064924 | 0.00029476 | -0.0042254 | -0.00068649 | 0.00062796 | 0.061252 | 0.064232 | -0.0079169 | -0.0063831 | 65.2771 | -55.8517 | 0.045776 | -56.0761 | 65.3641 | -56.0761 | -56.0349 | -56.3141 | 0.064087 | -56.2866 | 65.2359 | 65.2542 | -56.0028 | -56.1539 | -0.018311 | 0.022888 | 0 | 0.20599 | -0.018311 | -0.041199 | -0.086975 | 0.054931 | -0.096131 | -0.12817 | -0.25635 | -0.22888 | -0.13275 | -0.10986 | 121.4218 | 121.3348 | 56.1035 | -121.3989 | 121.2936 | 121.3119 | 56.1218 | -121.5179
381.6562 | 121.5958 | -55.8014 | 65.6021 | 0.0066373 | 0.0056098 | 0.070566 | 0.0023476 | 0.066633 | 0.00029476 | -0.0046526 | 0.0069425 | 0.0016962 | 0.067661 | 0.066368 | -0.011121 | -0.0051013 | 65.4282 | -55.7098 | 0.036621 | -55.9296 | 65.593 | -55.8929 | -55.8472 | -56.2271 | 0.045776 | -56.1539 | 65.5197 | 65.5426 | -55.8105 | -55.9662 | -0.091552 | -0.045776 | -0.009155 | 0.091553 | -0.12817 | -0.082397 | -0.17395 | -0.009155 | -0.16479 | -0.082398 | -0.42572 | -0.35248 | -0.18768 | -0.059509 | 121.3943 | 121.2296 | 55.838 | -121.4493 | 121.3211 | 121.344 | 55.8472 | -121.5683
383.3281 | 121.5912 | -55.5542 | 65.831 | -0.00099167 | 0.0058234 | 0.069071 | 0.0064066 | 0.065992 | -0.0018414 | -0.0042254 | -0.00068649 | -0.0012946 | 0.065525 | 0.066368 | -0.010267 | -0.0055285 | 65.6525 | -55.4718 | 0.018311 | -55.6824 | 65.8768 | -55.6458 | -55.5862 | -55.9891 | 0.050354 | -55.9296 | 65.7852 | 65.7852 | -55.5588 | -55.7465 | -0.091553 | -0.032044 | 0.045776 | 0.082397 | -0.12817 | -0.09613 | -0.17853 | -0.004578 | -0.19226 | -0.045777 | -0.43488 | -0.37537 | -0.1831 | -0.045777 | 121.431 | 121.2067 | 55.5725 | -121.4172 | 121.3394 | 121.3394 | 55.6046 | -121.5775
385.0625 | 121.4996 | -55.4169 | 66.0461 | 0.014267 | 0.002619 | 0.071634 | 0.00063865 | 0.064283 | 0.0049946 | -0.0029436 | -0.008316 | 0.0053278 | 0.061679 | 0.065514 | -0.0055671 | -0.0051013 | 65.9042 | -55.2704 | 0.032043 | -55.4581 | 66.0416 | -55.4214 | -55.3802 | -55.7465 | 0.018311 | -55.7465 | 65.9729 | 65.9958 | -55.3757 | -55.5542 | -0.004578 | 0.036621 | -0.004578 | 0.14648 | -0.041199 | -0.07782 | -0.14191 | 0.041199 | -0.13733 | -0.073243 | -0.32959 | -0.32959 | -0.19226 | -0.050354 | 121.4584 | 121.3211 | 55.4489 | -121.4264 | 121.3898 | 121.4127 | 55.4352 | -121.6003
386.7344 | 121.4996 | -55.22 | 66.2613 | 0.014267 | 0.0039008 | 0.070566 | 0.002134 | 0.067488 | 0.0045674 | -0.00080744 | 0.0069425 | 0.0036188 | 0.064243 | 0.065514 | -0.0049261 | -0.0048877 | 66.0873 | -55.0735 | 0.036621 | -55.275 | 66.275 | -55.2109 | -55.1788 | -55.5405 | 0.009155 | -55.545 | 66.1652 | 66.1835 | -55.1651 | -55.3482 | 0.009156 | 0.041199 | 0.013732 | 0.14649 | -0.054931 | -0.09613 | -0.17395 | 0.054932 | -0.12817 | -0.096131 | -0.32043 | -0.32501 | -0.19684 | -0.07782 | 121.4951 | 121.3074 | 55.2567 | -121.4401 | 121.3852 | 121.4035 | 55.2292 | -121.6095
388.4062 | 121.55 | -54.95 | 66.4764 | 0.0066373 | 0.0068916 | 0.071421 | -2.152e-06 | 0.064497 | -0.0014142 | -0.001021 | 0.0069425 | -0.0010808 | 0.063388 | 0.064873 | -0.0072759 | -0.0044605 | 66.3483 | -54.8035 | 0.009155 | -55.0095 | 66.4581 | -54.9728 | -54.9179 | -55.2429 | 0.054932 | -55.188 | 66.362 | 66.4078 | -54.8859 | -55.069 | -0.022888 | 0.032043 | -0.01831 | 0.14648 | -0.059509 | -0.091552 | -0.12817 | 0.064087 | -0.11902 | -0.11444 | -0.29297 | -0.23804 | -0.11902 | -0.068664 | 121.4081 | 121.2982 | 54.9591 | -121.3943 | 121.312 | 121.3577 | 55.0049 | -121.5454
390.1094 | 121.6187 | -54.5975 | 66.8152 | 0.0066373 | 0.0079596 | 0.073771 | 0.0046976 | 0.062788 | -0.006541 | -0.0035846 | 0.014572 | -0.00065364 | 0.061252 | 0.062737 | -0.012189 | -0.0029651 | 66.655 | -54.4327 | 0.036621 | -54.6753 | 66.7786 | -54.6433 | -54.5837 | -54.9545 | 0.10529 | -54.863 | 66.6779 | 66.7374 | -54.57 | -54.7394 | -0.045777 | 0.013733 | -0.036622 | 0.16479 | -0.07782 | -0.091553 | -0.16022 | 0.027466 | -0.14191 | -0.13733 | -0.35706 | -0.2655 | -0.1236 | -0.07782 | 121.376 | 121.2524 | 54.6341 | -121.3989 | 121.2753 | 121.3348 | 54.7028 | -121.5546
391.7812 | 121.5546 | -54.3549 | 67.1036 | -0.00099167 | 0.0081732 | 0.072275 | 0.0044838 | 0.062788 | -0.003764 | -0.003371 | 0.0069425 | -0.0012946 | 0.061466 | 0.066155 | -0.011121 | -0.0042467 | 66.9388 | -54.2038 | -0.009155 | -54.3915 | 67.0349 | -54.3594 | -54.3228 | -54.689 | 0.041199 | -54.5975 | 66.9525 | 67.0029 | -54.2725 | -54.4556 | -0.004578 | 0.032043 | -0.068665 | 0.15106 | -0.036621 | -0.068664 | -0.16479 | 0.082397 | -0.10071 | -0.15106 | -0.33417 | -0.24262 | -0.14191 | -0.10071 | 121.3898 | 121.2936 | 54.3457 | -121.4264 | 121.3074 | 121.3577 | 54.3961 | -121.5591
393.5 | 121.6232 | -53.9749 | 67.4286 | -0.00099167 | 0.002619 | 0.066935 | 0.005552 | 0.067915 | 0.0034992 | -0.0029436 | 0.0069425 | 0.0025508 | 0.064243 | 0.063378 | -0.0098395 | -0.0070239 | 67.3325 | -53.8605 | 0.068665 | -54.0436 | 67.4606 | -54.0253 | -53.9932 | -54.2908 | 0.10986 | -54.2816 | 67.392 | 67.392 | -53.9429 | -54.1214 | -0.050354 | -0.01831 | 0.032043 | 0.11444 | -0.068664 | -0.050354 | -0.096131 | 0.032044 | -0.14648 | -0.036621 | -0.31586 | -0.3067 | -0.16022 | -0.036621 | 121.4355 | 121.3074 | 54.0436 | -121.4218 | 121.3669 | 121.3669 | 54.0848 | -121.55
395.1719 | 121.5958 | -53.6728 | 67.749 | -0.0086212 | 0.00326 | 0.069071 | 0.0076882 | 0.066206 | -0.0024822 | -0.0023028 | -0.00068649 | -0.0015082 | 0.066166 | 0.066582 | -0.010694 | -0.0053149 | 67.5797 | -53.5812 | 0.022888 | -53.7643 | 67.7582 | -53.7231 | -53.6911 | -54.0482 | 0.064087 | -54.0024 | 67.6895 | 67.6987 | -53.6682 | -53.801 | -0.050354 | -0.01831 | 0.009156 | 0.091553 | -0.091552 | -0.073242 | -0.16937 | 0.004578 | -0.12817 | -0.059509 | -0.37537 | -0.32959 | -0.20142 | -0.050354 | 121.431 | 121.2524 | 53.6957 | -121.4401 | 121.3623 | 121.3715 | 53.7369 | -121.55
396.8594 | 121.5775 | -53.3615 | 68.0374 | 0.0066373 | 0.0053962 | 0.070353 | 0.0068338 | 0.064924 | -0.0016278 | -0.001662 | 0.0069425 | 0.0010554 | 0.062961 | 0.063591 | -0.010694 | -0.0053149 | 67.8452 | -53.2883 | 0.041199 | -53.4897 | 68.0466 | -53.4439 | -53.4027 | -53.7872 | 0.054932 | -53.7369 | 67.9962 | 67.9779 | -53.3615 | -53.5355 | -0.082398 | -0.041199 | 0.009155 | 0.073242 | -0.12817 | -0.086975 | -0.19226 | 0 | -0.17395 | -0.041199 | -0.42572 | -0.37537 | -0.20142 | -0.05951 | 121.4081 | 121.2067 | 53.4027 | -121.4401 | 121.3577 | 121.3394 | 53.4164 | -121.5729
398.5625 | 121.55 | -52.9495 | 68.5043 | 0.0066373 | 0.0068916 | 0.073984 | 0.002775 | 0.064924 | 0.0011494 | -0.0020892 | -0.008316 | 0.00041436 | 0.062961 | 0.066582 | -0.0064215 | -0.0051013 | 68.367 | -52.7939 | 0 | -52.9953 | 68.5043 | -52.9312 | -52.8946 | -53.2196 | 0.036621 | -53.2059 | 68.3716 | 68.4036 | -52.8671 | -53.0457 | 0.018311 | 0.054932 | 0 | 0.15564 | -0.045776 | -0.10071 | -0.13733 | 0.082398 | -0.09613 | -0.13275 | -0.27008 | -0.25635 | -0.16022 | -0.10071 | 121.4539 | 121.3165 | 52.9495 | -121.3989 | 121.3211 | 121.3531 | 52.9861 | -121.55
400.2344 | 121.5088 | -52.6108 | 68.8751 | 0.0066373 | 0.00326 | 0.06843 | 0.0032022 | 0.064283 | 0.0032856 | -0.0020892 | 0.0069425 | 0.002978 | 0.063175 | 0.064873 | -0.0053533 | -0.0057421 | 68.6966 | -52.4689 | 0.041199 | -52.652 | 68.866 | -52.597 | -52.5833 | -52.9541 | -0.004578 | -52.9449 | 68.7927 | 68.7836 | -52.533 | -52.7435 | 0.013733 | 0.027466 | -0.009155 | 0.14191 | -0.041199 | -0.068665 | -0.17853 | 0.07782 | -0.13275 | -0.082397 | -0.34332 | -0.33417 | -0.20142 | -0.091553 | 121.4767 | 121.3074 | 52.652 | -121.4584 | 121.4035 | 121.3943 | 52.6062 | -121.6187
401.9219 | 121.6278 | -52.1347 | 69.2459 | 0.014267 | 0.0086006 | 0.071207 | 0.0070474 | 0.06172 | -0.0056866 | -0.0037982 | -0.00068649 | -0.0042852 | 0.064243 | 0.065728 | -0.012617 | -0.0070239 | 69.1544 | -51.9424 | 0.10529 | -52.1896 | 69.223 | -52.1851 | -52.1393 | -52.4506 | 0.1831 | -52.3544 | 69.1177 | 69.1452 | -52.121 | -52.2675 | -0.050354 | -0.004577 | -0.022889 | 0.19226 | -0.054931 | -0.050354 | -0.091553 | 0.013733 | -0.13275 | -0.12817 | -0.31586 | -0.21973 | -0.086975 | -0.10071 | 121.3577 | 121.2891 | 52.24 | -121.3852 | 121.2524 | 121.2799 | 52.3178 | -121.5134
403.5938 | 121.5866 | -51.5945 | 69.8364 | 0.0066373 | 0.0064642 | 0.072702 | 0.002775 | 0.063002 | -0.00077324 | -0.0035846 | -0.00068649 | -0.0015082 | 0.06232 | 0.064446 | -0.0094123 | -0.0051013 | 69.7083 | -51.4297 | 0.1236 | -51.6541 | 69.7723 | -51.6129 | -51.622 | -51.9287 | 0.14191 | -51.8784 | 69.7266 | 69.7632 | -51.5579 | -51.709 | -0.018311 | -0.027466 | -0.064087 | 0.16479 | -0.05951 | -0.032044 | -0.12817 | 0.036621 | -0.11444 | -0.10986 | -0.33417 | -0.28381 | -0.16937 | -0.073242 | 121.3669 | 121.3028 | 51.7181 | -121.4584 | 121.3211 | 121.3577 | 51.7365 | -121.5454
405.2656 | 121.4767 | -51.1459 | 70.34 | 0.0066373 | 0.010096 | 0.069498 | 0.002134 | 0.066847 | -0.0033368 | -0.0023028 | -0.008316 | -1.2844e-05 | 0.062748 | 0.06295 | -0.0094123 | -0.0055285 | 70.2118 | -50.9308 | 0.059509 | -51.1734 | 70.2713 | -51.123 | -51.0818 | -51.4389 | 0.082397 | -51.384 | 70.1752 | 70.2072 | -51.0635 | -51.2192 | 0.022888 | 0.064087 | -0.068665 | 0.21515 | -0.027466 | -0.091553 | -0.12817 | 0.082397 | -0.073242 | -0.16479 | -0.29297 | -0.23804 | -0.16479 | -0.13275 | 121.4172 | 121.3577 | 51.2054 | -121.4218 | 121.3211 | 121.3531 | 51.2283 | -121.5591
406.9375 | 121.4951 | -50.7614 | 70.7245 | 0.0066373 | 0.010523 | 0.073557 | 0.00063865 | 0.063856 | -0.00055964 | -0.0018756 | 0.0069425 | 0.00041436 | 0.06232 | 0.064232 | -0.0079169 | -0.0057421 | 70.6375 | -50.5371 | 0.068665 | -50.7385 | 70.7016 | -50.7156 | -50.6744 | -50.9628 | 0.10071 | -50.9537 | 70.5963 | 70.6192 | -50.6607 | -50.8026 | 0.045777 | 0.086976 | -0.022888 | 0.22431 | 0.022889 | -0.064087 | -0.086975 | 0.10071 | -0.041198 | -0.12817 | -0.20142 | -0.19226 | -0.15106 | -0.10528 | 121.463 | 121.3989 | 50.8301 | -121.3989 | 121.3577 | 121.3806 | 50.8621 | -121.5271
408.6094 | 121.5408 | -50.1251 | 71.315 | 0.0066373 | 0.007746 | 0.07078 | 0.0019204 | 0.062788 | -0.002055 | -0.0025164 | 0.022202 | -0.00065364 | 0.062534 | 0.063805 | -0.010694 | -0.0038195 | 71.1456 | -50.029 | -0.004578 | -50.2121 | 71.2601 | -50.1297 | -50.1205 | -50.473 | 0.054932 | -50.4044 | 71.1777 | 71.2234 | -50.0656 | -50.267 | -0.004578 | 0.004578 | -0.054931 | 0.09613 | -0.086975 | -0.091553 | -0.16937 | 0.059509 | -0.14191 | -0.13733 | -0.3479 | -0.27924 | -0.13733 | -0.091552 | 121.3852 | 121.2708 | 50.1205 | -121.4355 | 121.3028 | 121.3486 | 50.1801 | -121.582
410.2812 | 121.6278 | -49.5392 | 71.8323 | -0.0086212 | 0.0090278 | 0.073771 | 0.0053384 | 0.064711 | -0.0035504 | -0.0035846 | 0.022202 | -1.2844e-05 | 0.061893 | 0.062523 | -0.0098395 | -0.0074511 | 71.7865 | -49.3973 | 0.068665 | -49.5987 | 71.8552 | -49.5438 | -49.5438 | -49.8596 | 0.14648 | -49.7955 | 71.759 | 71.7773 | -49.5163 | -49.6674 | -0.004577 | -0.004577 | 0.022889 | 0.14191 | -0.059509 | -0.054932 | -0.045776 | 0.022889 | -0.12817 | -0.073242 | -0.32043 | -0.25635 | -0.12817 | -0.054931 | 121.3943 | 121.3257 | 49.6079 | -121.376 | 121.2982 | 121.3165 | 49.6857 | -121.4996
411.9531 | 121.5271 | -48.9899 | 72.4319 | -0.00099167 | 0.0079596 | 0.071848 | 0.0025612 | 0.06407 | 0.0017902 | -0.0037982 | 0.0069425 | 0.0025508 | 0.063175 | 0.065087 | -0.0053533 | -0.0068103 | 72.3541 | -48.8297 | 0.054932 | -49.0128 | 72.4182 | -48.9578 | -48.9441 | -49.2508 | 0.07782 | -49.2416 | 72.3267 | 72.3221 | -48.9532 | -49.0906 | 0.032043 | 0.045776 | -0.013733 | 0.16022 | -0.022888 | -0.068664 | -0.07782 | 0.036621 | -0.10071 | -0.10529 | -0.26093 | -0.25177 | -0.15106 | -0.10986 | 121.4081 | 121.344 | 49.0448 | -121.376 | 121.3165 | 121.312 | 49.0677 | -121.5225
413.6406 | 121.5088 | -48.175 | 73.2925 | 0.0066373 | 0.0092414 | 0.073343 | 0.00085245 | 0.064283 | -0.0031232 | -0.0055072 | -0.00068649 | -0.002149 | 0.062107 | 0.063805 | -0.0094123 | -0.0051013 | 73.1323 | -48.0515 | 0.009155 | -48.2346 | 73.2651 | -48.1476 | -48.1613 | -48.4955 | 0.045776 | -48.4451 | 73.1369 | 73.1918 | -48.0789 | -48.2529 | 0.027466 | 0.013733 | -0.027466 | 0.1236 | -0.059509 | -0.073242 | -0.16022 | 0.096131 | -0.07782 | -0.15564 | -0.32043 | -0.27008 | -0.19226 | -0.10071 | 121.4401 | 121.3074 | 48.1842 | -121.4539 | 121.312 | 121.3669 | 48.2208 | -121.5454
415.3125 | 121.5317 | -47.2687 | 74.2081 | -0.00099167 | 0.0088142 | 0.070993 | 0.0025612 | 0.061934 | 0.0032856 | -0.0025164 | 0.0069425 | 0.0031916 | 0.063602 | 0.066155 | -0.0053533 | -0.0057421 | 74.025 | -47.2275 | -0.032043 | -47.3923 | 74.2172 | -47.287 | -47.2595 | -47.6028 | -0.027466 | -47.6074 | 74.1348 | 74.1165 | -47.2092 | -47.3785 | -0.01831 | 0.009156 | 0.009155 | 0.041199 | -0.1236 | -0.13275 | -0.18311 | 0.05951 | -0.10986 | -0.073242 | -0.33417 | -0.33875 | -0.22888 | -0.091553 | 121.4859 | 121.2936 | 47.2366 | -121.4676 | 121.4035 | 121.3852 | 47.2412 | -121.5866
417 | 121.5225 | -46.6965 | 74.7986 | -0.00099167 | 0.004969 | 0.072275 | 0.0012796 | 0.065138 | 0.0049946 | -0.0023028 | 0.014572 | 0.0053278 | 0.065097 | 0.064232 | -0.0049261 | -0.0042467 | 74.5834 | -46.669 | -0.013733 | -46.8063 | 74.7711 | -46.7148 | -46.6827 | -47.0444 | -0.004578 | -47.0718 | 74.6658 | 74.7253 | -46.6415 | -46.788 | -0.018311 | 0.013733 | -0.027466 | 0.027466 | -0.10986 | -0.1236 | -0.21515 | 0.054931 | -0.091553 | -0.13275 | -0.3479 | -0.37537 | -0.28381 | -0.073242 | 121.4676 | 121.2799 | 46.6827 | -121.4813 | 121.3623 | 121.4218 | 46.6919 | -121.5866
418.7031 | 121.4859 | -46.1746 | 75.325 | -0.00099167 | 0.0075324 | 0.07313 | 0.0064066 | 0.065138 | -0.0035504 | -0.0035846 | 0.014572 | -0.0017218 | 0.063175 | 0.063591 | -0.010908 | -0.0036059 | 75.1328 | -46.0419 | 0.013733 | -46.2341 | 75.2792 | -46.1334 | -46.1105 | -46.4767 | 0.050354 | -46.4539 | 75.174 | 75.2014 | -46.106 | -46.2524 | 0.041199 | 0.064087 | -0.045776 | 0.13275 | -0.059509 | -0.1236 | -0.19226 | 0.068665 | -0.077819 | -0.15106 | -0.30212 | -0.27923 | -0.20142 | -0.1236 | 121.4539 | 121.3074 | 46.1884 | -121.4355 | 121.3486 | 121.376 | 46.225 | -121.5775
420.4219 | 121.6324 | -45.5017 | 75.9476 | 0.014267 | 0.0073188 | 0.072489 | 0.0081154 | 0.064497 | -0.0044048 | -0.0023028 | -0.008316 | -0.0032172 | 0.065097 | 0.065728 | -0.011121 | -0.0068103 | 75.8286 | -45.3598 | 0.091553 | -45.5566 | 75.8743 | -45.5154 | -45.4788 | -45.7809 | 0.17853 | -45.7397 | 75.7874 | 75.824 | -45.4651 | -45.6161 | -0.013733 | 0.022888 | -0.073242 | 0.14191 | -0.054932 | -0.07782 | -0.11902 | 0.036621 | -0.11444 | -0.16022 | -0.27924 | -0.23804 | -0.1236 | -0.1236 | 121.376 | 121.3303 | 45.5933 | -121.4264 | 121.2891 | 121.3257 | 45.6802 | -121.5637
422.1094 | 121.6415 | -44.6594 | 76.7349 | -0.00099167 | 0.0039008 | 0.069925 | 0.0068338 | 0.066206 | 0.0045674 | -0.00080744 | 0.014572 | 0.0019098 | 0.063816 | 0.068291 | -0.0089849 | -0.0076647 | 76.5701 | -44.6686 | 0.018311 | -44.7922 | 76.7899 | -44.7052 | -44.696 | -45.0348 | 0.07782 | -45.0439 | 76.7349 | 76.712 | -44.6457 | -44.7876 | -0.045776 | -0.036621 | 0.054932 | -0.009155 | -0.13275 | -0.09613 | -0.1648 | 0.013733 | -0.12817 | 0 | -0.37537 | -0.38452 | -0.25635 | -0.022888 | 121.4493 | 121.2296 | 44.6777 | -121.431 | 121.3943 | 121.3715 | 44.7372 | -121.5225
423.8281 | 121.5363 | -43.8446 | 77.6321 | 0.014267 | 0.0086006 | 0.069498 | 0.003843 | 0.063215 | 0.0037128 | -0.00080744 | 0.0069425 | 0.0025508 | 0.064457 | 0.064873 | -0.0057807 | -0.0061695 | 77.4902 | -43.7302 | 0.086975 | -43.9178 | 77.6367 | -43.8309 | -43.8492 | -44.133 | 0.086975 | -44.1788 | 77.5131 | 77.5177 | -43.7988 | -43.9636 | 0.013732 | -0.004578 | 0.004578 | 0.11444 | -0.073243 | -0.068665 | -0.14191 | 0.045776 | -0.11902 | -0.11902 | -0.28839 | -0.33417 | -0.21515 | -0.11444 | 121.4813 | 121.3348 | 43.9316 | -121.4813 | 121.3577 | 121.3623 | 43.9316 | -121.5958
425.5625 | 121.5271 | -43.0847 | 78.3875 | -0.00099167 | 0.0068916 | 0.067789 | 0.0051248 | 0.065351 | 0.001363 | -0.001662 | 0.0069425 | 0.0016962 | 0.065952 | 0.066796 | -0.0091985 | -0.0040331 | 78.1815 | -43.0664 | -0.018311 | -43.222 | 78.4103 | -43.0618 | -43.0801 | -43.4418 | -0.022888 | -43.4555 | 78.2822 | 78.2867 | -43.0801 | -43.1992 | 0.022888 | 0.004578 | 0.022888 | 0.018311 | -0.13733 | -0.14191 | -0.20599 | 0.004578 | -0.11444 | -0.10528 | -0.35706 | -0.37079 | -0.25635 | -0.10071 | 121.4951 | 121.2662 | 43.0664 | -121.4676 | 121.3669 | 121.3715 | 43.0618 | -121.5866
427.3281 | 121.5134 | -42.3431 | 79.1565 | 0.0066373 | 0.0090278 | 0.06843 | 0.0049112 | 0.063856 | 0.0011494 | -0.00059384 | -0.00068649 | 0.004046 | 0.065525 | 0.065514 | -0.0074897 | -0.0051013 | 78.9505 | -42.2424 | 0.073242 | -42.4164 | 79.1199 | -42.3431 | -42.3203 | -42.6361 | 0.073242 | -42.6773 | 79.0558 | 79.0833 | -42.2653 | -42.4164 | 0 | 0.022889 | -0.036621 | 0.10071 | -0.073242 | -0.096131 | -0.20599 | 0.07782 | -0.073242 | -0.10071 | -0.29297 | -0.33417 | -0.26093 | -0.073242 | 121.463 | 121.2936 | 42.4164 | -121.4767 | 121.3989 | 121.4264 | 42.4164 | -121.5729
429.0312 | 121.5546 | -41.3773 | 80.04 | 0.021896 | 0.004969 | 0.069284 | 0.0085428 | 0.066633 | -0.0039776 | -0.0018756 | -0.00068649 | -0.00044004 | 0.065738 | 0.065514 | -0.011549 | -0.0055285 | 79.8798 | -41.2811 | 0.12817 | -41.4734 | 79.9759 | -41.4047 | -41.3773 | -41.7114 | 0.1831 | -41.6794 | 79.8798 | 79.9301 | -41.3635 | -41.5009 | -0.027466 | 0 | -0.064087 | 0.09613 | -0.096131 | -0.096131 | -0.16022 | 0.013733 | -0.1236 | -0.16022 | -0.33417 | -0.30212 | -0.17853 | -0.10986 | 121.3531 | 121.257 | 41.5054 | -121.4172 | 121.257 | 121.3074 | 41.5604 | -121.5408
430.7031 | 121.6049 | -40.6815 | 80.7083 | 0.0066373 | 0.0086006 | 0.071207 | 0.0091836 | 0.064924 | -0.0044048 | -0.0012346 | -0.00068649 | -0.0017218 | 0.064457 | 0.063591 | -0.011762 | -0.0051013 | 80.5527 | -40.5945 | 0.10986 | -40.8096 | 80.6534 | -40.7455 | -40.7455 | -41.0202 | 0.20599 | -41.0019 | 80.5481 | 80.5801 | -40.6952 | -40.8554 | -0.064086 | -0.064086 | -0.054932 | 0.086976 | -0.12817 | -0.064087 | -0.15564 | -0.013732 | -0.17395 | -0.16022 | -0.33875 | -0.32043 | -0.14648 | -0.12817 | 121.3348 | 121.2341 | 40.7913 | -121.4539 | 121.2296 | 121.2616 | 40.8875 | -121.5637
432.4531 | 121.6049 | -39.592 | 81.8253 | 0.014267 | 0.0068916 | 0.071848 | 0.0070474 | 0.067488 | -0.0026958 | -0.0055072 | 0.014572 | -0.0019354 | 0.062534 | 0.065728 | -0.011121 | -0.0061695 | 81.6742 | -39.4775 | 0.11902 | -39.679 | 81.8024 | -39.5966 | -39.6011 | -39.8712 | 0.19226 | -39.8666 | 81.6742 | 81.7062 | -39.5462 | -39.7018 | -0.004578 | -0.009155 | -0.022888 | 0.11444 | -0.086975 | -0.07782 | -0.15106 | 0.045776 | -0.10986 | -0.15106 | -0.27924 | -0.27466 | -0.1648 | -0.11902 | 121.3943 | 121.2662 | 39.711 | -121.4264 | 121.2662 | 121.2982 | 39.7842 | -121.5271
434.125 | 121.5729 | -38.3423 | 83.0795 | -0.00099167 | 0.0056098 | 0.070993 | 0.0053384 | 0.06407 | -0.0026958 | -0.0042254 | 0.022202 | -0.0010808 | 0.063602 | 0.063805 | -0.0089849 | -0.0046741 | 83.0246 | -38.1729 | 0.16937 | -38.3698 | 83.1299 | -38.269 | -38.2736 | -38.562 | 0.23804 | -38.5574 | 83.0109 | 83.0383 | -38.2599 | -38.4155 | 0.073242 | 0.068664 | 0.050354 | 0.16937 | -0.027466 | -0.09613 | -0.054932 | 0.082397 | -0.073242 | -0.068665 | -0.21973 | -0.21515 | -0.14191 | -0.041199 | 121.4722 | 121.3669 | 38.5117 | -121.3531 | 121.3531 | 121.3806 | 38.5803 | -121.4951
435.8125 | 121.5729 | -37.3856 | 84.0408 | 0.0066373 | 0.0056098 | 0.069925 | 0.0042702 | 0.065351 | -0.0018414 | -0.0029436 | 0.0069425 | 0.0010554 | 0.063816 | 0.064659 | -0.010908 | -0.0078783 | 83.931 | -37.2528 | 0.16479 | -37.4359 | 84.0454 | -37.3581 | -37.3581 | -37.6511 | 0.17395 | -37.6877 | 83.9172 | 83.9539 | -37.3581 | -37.5 | 0.027466 | 0.027466 | 0.004577 | 0.13275 | -0.050354 | -0.07782 | -0.10986 | 0.027466 | -0.11444 | -0.1236 | -0.2655 | -0.30212 | -0.18768 | -0.086976 | 121.431 | 121.3165 | 37.5504 | -121.3989 | 121.3028 | 121.3394 | 37.5595 | -121.5408
437.5469 | 121.5637 | -36.9507 | 84.4986 | 0.014267 | 0.004969 | 0.070993 | 0.0076882 | 0.065565 | -0.0014142 | -0.0029436 | 0.0069425 | 0.00084176 | 0.066806 | 0.063378 | -0.010053 | -0.0085193 | 84.3246 | -36.8912 | 0.13733 | -37.0377 | 84.4849 | -36.9278 | -36.9553 | -37.2482 | 0.15106 | -37.2665 | 84.4116 | 84.4116 | -36.9049 | -37.0377 | 0.022889 | -0.004577 | -0.013733 | 0.05951 | -0.086975 | -0.082398 | -0.17395 | 0.045777 | -0.086975 | -0.086975 | -0.29755 | -0.31586 | -0.22888 | -0.086975 | 121.4355 | 121.2753 | 37.088 | -121.4539 | 121.3623 | 121.3623 | 37.1017 | -121.5363
439.2188 | 121.5912 | -36.3007 | 85.1212 | 0.014267 | 0.0092414 | 0.072702 | 0.0066202 | 0.063856 | -0.0035504 | -0.0048662 | 0.0069425 | -0.0023626 | 0.06467 | 0.065087 | -0.011121 | -0.0059557 | 85.0296 | -36.2 | 0.073242 | -36.3785 | 85.1028 | -36.3281 | -36.2961 | -36.6165 | 0.064087 | -36.6257 | 84.9609 | 84.9838 | -36.3052 | -36.4517 | -0.027466 | 0.004577 | -0.018311 | 0.10071 | -0.07782 | -0.082397 | -0.091553 | -0.004578 | -0.15106 | -0.16022 | -0.31586 | -0.32501 | -0.17395 | -0.13733 | 121.4035 | 121.3303 | 36.3739 | -121.4172 | 121.2616 | 121.2845 | 36.3647 | -121.5729
440.9688 | 121.582 | -36.0168 | 85.3592 | 0.0066373 | 0.007746 | 0.073984 | 0.0046976 | 0.063856 | -0.00098684 | -0.0020892 | -0.00068649 | 0.001269 | 0.063388 | 0.064019 | -0.0089849 | -0.0059557 | 85.2356 | -35.9619 | 0.13733 | -36.1359 | 85.3546 | -36.0535 | -36.0535 | -36.3968 | 0.11902 | -36.3968 | 85.2264 | 85.2356 | -36.0626 | -36.1954 | -0.036621 | -0.036621 | -0.004578 | 0.054932 | -0.11902 | -0.082397 | -0.1236 | -0.045776 | -0.17853 | -0.13275 | -0.37994 | -0.37994 | -0.20142 | -0.1236 | 121.3715 | 121.2524 | 36.1542 | -121.4127 | 121.2433 | 121.2524 | 36.1359 | -121.5546
442.6562 | 121.5134 | -36.7538 | 84.7366 | -0.00099167 | 0.0024054 | 0.069925 | 0.00085245 | 0.063215 | 0.0062762 | -0.0012346 | -0.008316 | 0.0036188 | 0.06232 | 0.064873 | -0.0055671 | -0.0065967 | 84.5123 | -36.7584 | 0.091553 | -36.9003 | 84.6771 | -36.7905 | -36.795 | -37.0697 | 0.10071 | -37.1429 | 84.5947 | 84.6222 | -36.731 | -36.8683 | -0.036621 | -0.041199 | -0.059509 | -0.004578 | -0.14648 | -0.10529 | -0.2243 | 0.022888 | -0.11444 | -0.14191 | -0.31586 | -0.3891 | -0.27466 | -0.11444 | 121.431 | 121.2662 | 36.8454 | -121.5317 | 121.3486 | 121.376 | 36.8546 | -121.6049
444.3906 | 121.6095 | -36.676 | 84.6954 | -0.00099167 | 0.001551 | 0.069284 | 0.0046976 | 0.062361 | 0.00050836 | -0.0025164 | 0.014572 | 0.002337 | 0.063602 | 0.063805 | -0.0070623 | -0.0038195 | 84.549 | -36.6989 | 0.064087 | -36.8683 | 84.7824 | -36.7218 | -36.7447 | -37.0972 | 0.064087 | -37.1201 | 84.6634 | 84.6634 | -36.7035 | -36.8408 | -0.045777 | -0.068665 | 0.086975 | -0.022889 | -0.19226 | -0.1236 | -0.14648 | -0.027466 | -0.16479 | -0.032044 | -0.42114 | -0.44403 | -0.27924 | -0.032044 | 121.4584 | 121.225 | 36.7401 | -121.4401 | 121.3394 | 121.3394 | 36.7401 | -121.5363
446.0625 | 121.5088 | -37.0377 | 84.4391 | -0.00099167 | 0.0034736 | 0.070566 | 0.0019204 | 0.064497 | 0.0022174 | -0.001662 | 0.014572 | 0.0038324 | 0.064884 | 0.066796 | -0.0062079 | -0.0044605 | 84.2972 | -36.9965 | 0.1236 | -37.1338 | 84.4528 | -37.0102 | -37.0285 | -37.3123 | 0.10529 | -37.3718 | 84.3658 | 84.3887 | -36.9324 | -37.088 | 0.027466 | 0.009156 | 0.013733 | 0.041199 | -0.09613 | -0.10529 | -0.14191 | 0.10529 | -0.050354 | -0.073242 | -0.27466 | -0.33417 | -0.28381 | -0.050354 | 121.4905 | 121.3348 | 37.1613 | -121.4676 | 121.4035 | 121.4264 | 37.1429 | -121.5271
447.7344 | 121.4905 | -37.381 | 84.1187 | -0.0086212 | 0.011805 | 0.074198 | 0.002134 | 0.06172 | -0.0050458 | -0.0031574 | 0.014572 | 0.00062796 | 0.061252 | 0.065087 | -0.0089849 | -0.0053149 | 83.8852 | -37.2894 | 0.10986 | -37.4634 | 84.0454 | -37.3306 | -37.3444 | -37.6648 | 0.10529 | -37.6602 | 83.9722 | 83.9767 | -37.294 | -37.4359 | 0.050354 | 0.036621 | -0.073242 | 0.091552 | -0.082398 | -0.11902 | -0.23346 | 0.086975 | -0.054932 | -0.14648 | -0.28381 | -0.27924 | -0.2243 | -0.14191 | 121.4264 | 121.2662 | 37.4908 | -121.463 | 121.3531 | 121.3577 | 37.4863 | -121.5546
449.4688 | 121.5775 | -37.2528 | 84.1644 | -0.0086212 | 0.0098822 | 0.073343 | 0.0036294 | 0.063856 | -0.003764 | -0.0037982 | -0.00068649 | -0.0019354 | 0.063175 | 0.063591 | -0.011121 | -0.0059557 | 83.9722 | -37.2574 | -0.004578 | -37.3856 | 84.1782 | -37.2803 | -37.2894 | -37.6007 | 0.050354 | -37.5641 | 84.0637 | 84.0912 | -37.2391 | -37.3718 | -0.027465 | -0.036621 | 0.013733 | -0.004577 | -0.13275 | -0.09613 | -0.19226 | 0.013733 | -0.11902 | -0.10071 | -0.3479 | -0.31128 | -0.19226 | -0.073242 | 121.431 | 121.225 | 37.2482 | -121.4539 | 121.3165 | 121.344 | 37.3032 | -121.5363
451.1406 | 121.6415 | -35.6598 | 85.7071 | -0.00099167 | 0.00326 | 0.069284 | 0.0074746 | 0.065565 | -0.00034604 | -0.0018756 | 0.0069425 | -0.0010808 | 0.063816 | 0.065728 | -0.0079169 | -0.0053149 | 85.4965 | -35.7697 | 0.10071 | -35.8521 | 85.7437 | -35.7513 | -35.7651 | -36.0764 | 0.09613 | -36.1176 | 85.6522 | 85.6659 | -35.7285 | -35.8704 | -0.091553 | -0.10529 | 0.036621 | -0.10986 | -0.19226 | -0.086975 | -0.21057 | -0.068665 | -0.21057 | -0.054931 | -0.41656 | -0.45776 | -0.24719 | -0.041198 | 121.4035 | 121.1563 | 35.7605 | -121.4722 | 121.312 | 121.3257 | 35.7559 | -121.5775
452.875 | 121.5729 | -36.1633 | 85.2676 | 0.0066373 | 0.0041144 | 0.067789 | 0.0085428 | 0.064924 | -0.00077324 | -0.00016664 | 0.014572 | 0.00041436 | 0.066593 | 0.0653 | -0.010694 | -0.0051013 | 85.0937 | -36.1221 | 0.14191 | -36.2686 | 85.2676 | -36.1633 | -36.1679 | -36.5204 | 0.1236 | -36.5341 | 85.199 | 85.2036 | -36.1221 | -36.2686 | 0 | -0.004578 | 0 | 0.041199 | -0.10529 | -0.10071 | -0.17395 | 0.041199 | -0.10529 | -0.068664 | -0.35706 | -0.37079 | -0.2655 | -0.064087 | 121.431 | 121.257 | 36.3052 | -121.4355 | 121.3623 | 121.3669 | 36.2869 | -121.5363
454.6094 | 121.4813 | -36.3876 | 85.1028 | -0.00099167 | 0.0096686 | 0.070353 | 0.002134 | 0.063215 | -0.0024822 | -0.0014484 | -0.00068649 | -1.2844e-05 | 0.062961 | 0.065728 | -0.0087713 | -0.0038195 | 84.906 | -36.3052 | 0.10529 | -36.4609 | 85.0388 | -36.351 | -36.3464 | -36.6714 | 0.10529 | -36.6852 | 84.9197 | 84.9655 | -36.319 | -36.4563 | 0.036621 | 0.041198 | -0.064087 | 0.082397 | -0.073242 | -0.11444 | -0.19684 | 0.068664 | -0.068665 | -0.1831 | -0.28381 | -0.29755 | -0.22888 | -0.13733 | 121.4264 | 121.2936 | 36.4929 | -121.4493 | 121.3074 | 121.3531 | 36.4929 | -121.5591
456.3594 | 121.5317 | -35.7513 | 85.7162 | 0.0066373 | 0.0075324 | 0.068857 | 0.00042505 | 0.062574 | 0.0011494 | -0.0035846 | -0.00068649 | 0.0031916 | 0.061252 | 0.065728 | -0.0062079 | -0.0059557 | 85.4782 | -35.8109 | 0.036621 | -35.9116 | 85.7437 | -35.7742 | -35.7605 | -36.0992 | 0.027466 | -36.1404 | 85.6201 | 85.6567 | -35.7193 | -35.8429 | -0.022888 | -0.009155 | 0.027465 | -0.059509 | -0.16022 | -0.15106 | -0.23804 | 0.032044 | -0.091553 | -0.096131 | -0.3479 | -0.3891 | -0.29755 | -0.05951 | 121.4951 | 121.2296 | 35.788 | -121.4767 | 121.3715 | 121.4081 | 35.7788 | -121.5591
458.0469 | 121.637 | -35.0281 | 86.3754 | -0.00099167 | 0.0083868 | 0.072702 | 0.0068338 | 0.063215 | -0.0059002 | -0.0048662 | -0.00068649 | -0.0025762 | 0.064029 | 0.06295 | -0.011121 | -0.0051013 | 86.2701 | -34.9777 | 0.054932 | -35.1425 | 86.38 | -35.0189 | -35.0281 | -35.3485 | 0.086975 | -35.3165 | 86.2701 | 86.2885 | -35.0052 | -35.1288 | 0.009155 | 0 | 0.004578 | 0.050354 | -0.11444 | -0.11444 | -0.10528 | 0.022888 | -0.10071 | -0.10528 | -0.32044 | -0.28839 | -0.18768 | -0.086975 | 121.4081 | 121.2982 | 35.083 | -121.4035 | 121.2982 | 121.3165 | 35.1151 | -121.5042
459.7344 | 121.6187 | -35.0555 | 86.3617 | -0.00099167 | 0.0047552 | 0.070566 | 0.0019204 | 0.064283 | 0.00414 | -0.001662 | -0.00068649 | 0.0014826 | 0.063388 | 0.067223 | -0.0072759 | -0.0042467 | 86.2061 | -35.1059 | 0.1236 | -35.1791 | 86.4166 | -35.0967 | -35.1196 | -35.3577 | 0.14648 | -35.4401 | 86.3159 | 86.3113 | -35.0601 | -35.2295 | -0.041199 | -0.064087 | 0.054932 | -0.050354 | -0.1236 | -0.059509 | -0.15564 | -0.004578 | -0.17395 | -0.045776 | -0.30212 | -0.38452 | -0.21057 | -0.050354 | 121.4722 | 121.2616 | 35.1791 | -121.4813 | 121.3715 | 121.3669 | 35.202 | -121.5912
461.4688 | 121.6187 | -33.4534 | 87.9684 | 0.0066373 | 0.010523 | 0.068216 | 0.0034158 | 0.065992 | 0.0020038 | -0.00016664 | -0.00068649 | 0.0016962 | 0.066379 | 0.066796 | -0.0098395 | -0.0051013 | 87.7808 | -33.5083 | 0.11902 | -33.6044 | 87.9639 | -33.5083 | -33.5083 | -33.7784 | 0.10529 | -33.8333 | 87.8815 | 87.9364 | -33.4488 | -33.5815 | -0.054932 | -0.054932 | -0.004578 | -0.054932 | -0.15106 | -0.09613 | -0.18768 | 0.004577 | -0.12817 | -0.086975 | -0.32501 | -0.37994 | -0.25177 | -0.032044 | 121.4172 | 121.2341 | 33.5724 | -121.4767 | 121.3348 | 121.3898 | 33.5587 | -121.55
463.2188 | 121.4767 | -31.7963 | 89.7171 | -0.00099167 | 0.010737 | 0.070566 | 0.002775 | 0.061934 | -0.0033368 | -0.0012346 | -0.008316 | -0.0025762 | 0.061039 | 0.064232 | -0.0068487 | -0.0036059 | 89.5477 | -31.6818 | 0.13733 | -31.8146 | 89.6667 | -31.7184 | -31.7276 | -31.9977 | 0.12817 | -32.0251 | 89.566 | 89.6118 | -31.6772 | -31.8192 | 0.07782 | 0.068665 | -0.050354 | 0.11444 | -0.01831 | -0.086975 | -0.16937 | 0.11902 | -0.022888 | -0.15106 | -0.20142 | -0.22888 | -0.20599 | -0.10529 | 121.463 | 121.344 | 31.9336 | -121.4447 | 121.3623 | 121.4081 | 31.9244 | -121.5363
464.8906 | 121.4951 | -29.9652 | 91.5619 | 0.0066373 | 0.0086006 | 0.071421 | 0.0014932 | 0.063643 | -0.0026958 | -0.001021 | -0.008316 | 0.00041436 | 0.062534 | 0.062737 | -0.0074897 | -0.0044605 | 91.3651 | -29.892 | 0.20142 | -29.9927 | 91.507 | -29.8965 | -29.8965 | -30.1483 | 0.1831 | -30.1849 | 91.4108 | 91.4612 | -29.837 | -29.9698 | 0.068665 | 0.068665 | -0.054932 | 0.073242 | -0.027466 | -0.096131 | -0.19684 | 0.12817 | -0.004578 | -0.15106 | -0.18311 | -0.21973 | -0.21515 | -0.10071 | 121.4722 | 121.3303 | 30.1666 | -121.4584 | 121.376 | 121.4264 | 30.1483 | -121.5317
466.6406 | 121.5912 | -28.4866 | 92.9443 | -0.00099167 | 5.5572e-05 | 0.071848 | 0.0042702 | 0.063643 | 0.00029476 | -0.0029436 | 0.0069425 | 0.002337 | 0.062961 | 0.065514 | -0.0098395 | -0.0068103 | 92.6697 | -28.6057 | 0.12817 | -28.6789 | 92.9581 | -28.5049 | -28.5507 | -28.8345 | 0.1236 | -28.894 | 92.9306 | 92.9398 | -28.4409 | -28.5599 | -0.018311 | -0.064087 | 0.013733 | -0.11902 | -0.19226 | -0.12817 | -0.27466 | 0.045776 | -0.073242 | -0.013733 | -0.3479 | -0.40741 | -0.33417 | -0.004578 | 121.4447 | 121.1563 | 28.6148 | -121.4951 | 121.4172 | 121.4264 | 28.6102 | -121.5042
468.375 | 121.4905 | -26.6876 | 94.7479 | 0.0066373 | 0.0083868 | 0.07313 | 0.0064066 | 0.064711 | -0.0039776 | -0.0031574 | 0.0069425 | -0.0036444 | 0.063816 | 0.063378 | -0.01283 | -0.0061695 | 94.4366 | -26.8112 | 0.25635 | -26.7654 | 94.7342 | -26.651 | -26.683 | -27.1225 | 0.091553 | -27.0859 | 94.5877 | 94.6609 | -26.683 | -26.7792 | 0.036621 | 0.004578 | -0.013733 | -0.1236 | -0.07782 | -0.082398 | -0.31128 | 0.004578 | -0.091553 | -0.16022 | -0.43488 | -0.39825 | -0.3067 | -0.086975 | 121.4218 | 121.1243 | 26.944 | -121.431 | 121.2753 | 121.3486 | 26.7792 | -121.5271
470.125 | 121.5042 | -26.1612 | 95.3751 | 0.014267 | 0.0081732 | 0.07078 | 0.0019204 | 0.064283 | 0.002431 | -0.0029436 | 0.0069425 | 0.0019098 | 0.062107 | 0.065514 | -0.0079169 | -0.0051013 | 95.0363 | -26.3077 | 0.10071 | -26.3443 | 95.343 | -26.1383 | -26.1887 | -26.4816 | 0.009155 | -26.5732 | 95.2606 | 95.2606 | -26.1383 | -26.2436 | 0.022888 | -0.027466 | -0.032043 | -0.14648 | -0.18311 | -0.15564 | -0.33875 | 0.022888 | -0.082397 | -0.11444 | -0.32043 | -0.41199 | -0.32959 | -0.11444 | 121.5042 | 121.1975 | 26.2619 | -121.5637 | 121.4218 | 121.4218 | 26.1703 | -121.6187
471.8125 | 121.4951 | -23.7808 | 97.7142 | 0.014267 | 0.01095 | 0.07078 | 0.0051248 | 0.065351 | -0.0035504 | -0.0031574 | 0.0069425 | -0.0025762 | 0.063816 | 0.064232 | -0.012403 | -0.0057421 | 97.4213 | -23.8266 | 0.18768 | -23.8998 | 97.641 | -23.735 | -23.8129 | -24.0601 | 0.11444 | -24.0875 | 97.5906 | 97.6135 | -23.7122 | -23.8266 | 0.045777 | -0.032043 | -0.073242 | -0.045776 | -0.11902 | -0.086975 | -0.29297 | 0.068665 | -0.045776 | -0.1236 | -0.27924 | -0.3067 | -0.26092 | -0.10071 | 121.4218 | 121.2021 | 23.9685 | -121.5271 | 121.3715 | 121.3943 | 23.8953 | -121.5408
473.5469 | 121.5317 | -23.8266 | 97.673 | 0.014267 | 0.010309 | 0.070993 | 0.002134 | 0.063215 | 0.0028584 | -0.0025164 | -0.015945 | 0.001269 | 0.061893 | 0.065087 | -0.0074897 | -0.0059557 | 97.3709 | -23.9044 | 0.23346 | -23.9685 | 97.5952 | -23.8495 | -23.8953 | -24.0372 | 0.11902 | -24.1287 | 97.5037 | 97.522 | -23.7534 | -23.8724 | -0.022888 | -0.068665 | -0.07782 | -0.07782 | -0.14191 | -0.073242 | -0.30212 | 0.073242 | -0.045776 | -0.16937 | -0.21057 | -0.30212 | -0.25635 | -0.15106 | 121.4218 | 121.1975 | 24.0601 | -121.5683 | 121.3303 | 121.3486 | 23.9456 | -121.5454
475.2812 | 121.4676 | -21.8628 | 99.6918 | 0.0066373 | 0.0045416 | 0.068216 | 0.0014932 | 0.064711 | 0.0037128 | -0.0023028 | -0.008316 | 0.00062796 | 0.063816 | 0.064873 | -0.0079169 | -0.0068103 | 99.4217 | -21.9498 | 0.2243 | -21.9498 | 99.7009 | -21.785 | -21.8628 | -22.1191 | 0.059509 | -22.2107 | 99.6185 | 99.6414 | -21.7667 | -21.8857 | 0.07782 | 0 | 0.009156 | -0.086975 | -0.086975 | -0.086975 | -0.27008 | 0.09613 | -0.022888 | -0.073242 | -0.25635 | -0.3479 | -0.32501 | -0.050354 | 121.5637 | 121.2845 | 22.0871 | -121.5546 | 121.4813 | 121.5042 | 21.9223 | -121.5775
476.9531 | 121.55 | -21.2769 | 100.1862 | -0.00099167 | 0.0030464 | 0.070993 | 0.005552 | 0.063002 | -0.0035504 | -0.0023028 | 0.014572 | -0.00044004 | 0.064457 | 0.05996 | -0.0098395 | -0.0042467 | 99.9481 | -21.2997 | 0.35248 | -21.3821 | 100.1175 | -21.2952 | -21.3364 | -21.5012 | 0.26093 | -21.5469 | 100.0626 | 100.1221 | -21.2311 | -21.3455 | -0.018311 | -0.05951 | -0.068664 | -0.022889 | -0.10529 | -0.045776 | -0.23804 | 0.045776 | -0.068665 | -0.1236 | -0.2243 | -0.27008 | -0.20142 | -0.064087 | 121.3943 | 121.225 | 21.6293 | -121.5225 | 121.3394 | 121.3989 | 21.5378 | -121.5317
478.625 | 121.6095 | -19.6747 | 101.7792 | -0.00099167 | 0.0036872 | 0.069712 | 0.0051248 | 0.061506 | 0.0022174 | -0.0020892 | 0.014572 | 0.0034052 | 0.065738 | 0.0653 | -0.0091985 | -0.0061695 | 101.5274 | -19.7937 | 0.32501 | -19.7983 | 101.7654 | -19.7159 | -19.7433 | -19.9219 | 0.15106 | -20.0363 | 101.6785 | 101.7197 | -19.6609 | -19.7571 | -0.041198 | -0.068664 | -0.013733 | -0.11902 | -0.1236 | -0.054932 | -0.25177 | 0.013733 | -0.082397 | -0.10071 | -0.24719 | -0.36163 | -0.27924 | -0.059509 | 121.4401 | 121.2021 | 19.9997 | -121.5225 | 121.3531 | 121.3943 | 19.8257 | -121.5363
480.3594 | 121.5683 | -18.3884 | 103.0884 | 0.0066373 | 0.0036872 | 0.070993 | 0.0066202 | 0.061506 | -0.0026958 | -0.0031574 | 0.014572 | -0.00065364 | 0.065952 | 0.065728 | -0.012403 | -0.0040331 | 102.8046 | -18.4525 | 0.32959 | -18.5074 | 103.0975 | -18.3746 | -18.4387 | -18.6722 | 0.09613 | -18.75 | 103.0334 | 103.0243 | -18.3701 | -18.4662 | 0.013733 | -0.050354 | 0.009155 | -0.064087 | -0.11902 | -0.068664 | -0.28381 | 0.018311 | -0.07782 | -0.054932 | -0.28381 | -0.36163 | -0.28381 | -0.064087 | 121.4859 | 121.1929 | 18.718 | -121.5271 | 121.4218 | 121.4127 | 18.4845 | -121.5546
482.0938 | 121.6187 | -17.482 | 103.9764 | 0.0066373 | 0.0024054 | 0.069284 | 0.0079018 | 0.064924 | 0.00072196 | -0.0046526 | -0.008316 | 0.001269 | 0.065952 | 0.064873 | -0.0079169 | -0.0083057 | 103.688 | -17.601 | 0.37079 | -17.5919 | 104.0085 | -17.5323 | -17.5735 | -17.7429 | 0.12817 | -17.8574 | 103.8895 | 103.9169 | -17.514 | -17.6056 | -0.050354 | -0.091552 | 0.032044 | -0.11902 | -0.10986 | -0.018311 | -0.28839 | -0.032043 | -0.1236 | -0.086975 | -0.26093 | -0.37537 | -0.25177 | -0.059509 | 121.4905 | 121.17 | 17.8528 | -121.55 | 121.3715 | 121.3989 | 17.6102 | -121.582
483.7656 | 121.4996 | -17.8116 | 103.6789 | 0.0066373 | 0.0047552 | 0.069284 | 0.003843 | 0.064497 | 0.0022174 | -0.00059384 | 0.0069425 | 0.0016962 | 0.065525 | 0.0653 | -0.0068487 | -0.0059557 | 103.4225 | -17.8574 | 0.37994 | -17.8986 | 103.6606 | -17.8024 | -17.8574 | -18.0267 | 0.091553 | -18.1503 | 103.5873 | 103.6057 | -17.7887 | -17.894 | 0.009155 | -0.045777 | -0.018311 | -0.045777 | -0.086976 | -0.041199 | -0.25635 | 0.022888 | -0.082398 | -0.091553 | -0.21515 | -0.33875 | -0.25635 | -0.073242 | 121.4722 | 121.2341 | 18.1915 | -121.5363 | 121.3989 | 121.4172 | 17.9031 | -121.5729
485.4844 | 121.6141 | -17.5507 | 103.8895 | -0.00099167 | 0.010309 | 0.073771 | 0.0066202 | 0.061079 | -0.0073956 | -0.0020892 | 0.0069425 | -0.0036444 | 0.063388 | 0.06231 | -0.011762 | -0.0061695 | 103.6469 | -17.5552 | 0.35248 | -17.6147 | 103.8803 | -17.5415 | -17.5873 | -17.7475 | 0.15564 | -17.8024 | 103.7704 | 103.8162 | -17.5369 | -17.6193 | 0.009155 | -0.036621 | -0.009155 | -0.004578 | -0.064087 | -0.027466 | -0.24261 | 0.013733 | -0.068665 | -0.11902 | -0.19684 | -0.25177 | -0.18311 | -0.073242 | 121.431 | 121.1975 | 17.9031 | -121.4767 | 121.3211 | 121.3669 | 17.7063 | -121.5088
487.2344 | 121.6187 | -16.7038 | 104.7226 | 0.021896 | 0.01095 | 0.070993 | 0.0066202 | 0.063856 | -0.0050458 | -0.0025164 | -0.00068649 | -0.0040716 | 0.06467 | 0.0653 | -0.011762 | -0.0061695 | 104.5303 | -16.6901 | 0.46692 | -16.7496 | 104.7272 | -16.6901 | -16.7358 | -16.8686 | 0.21973 | -16.9464 | 104.6219 | 104.6722 | -16.658 | -16.7679 | 0.013733 | -0.032044 | 0.004578 | 0.013733 | -0.045777 | -0.013733 | -0.19226 | 0.045776 | -0.064087 | -0.10071 | -0.16479 | -0.24262 | -0.17853 | -0.050354 | 121.431 | 121.2341 | 17.1707 | -121.4584 | 121.3257 | 121.376 | 16.9235 | -121.4905
488.9219 | 121.6095 | -16.9235 | 104.5349 | 0.0066373 | 0.0062506 | 0.071848 | 0.0012796 | 0.06642 | 0.0028584 | -0.0020892 | 0.0069425 | 0.004046 | 0.063602 | 0.0653 | -0.0087713 | -0.0061695 | 104.2831 | -17.0334 | 0.42572 | -17.0334 | 104.5441 | -16.9327 | -17.0059 | -17.1432 | 0.10071 | -17.2668 | 104.4525 | 104.4846 | -16.9144 | -17.0242 | -0.009155 | -0.082397 | 0.009155 | -0.10986 | -0.10986 | -0.027466 | -0.25177 | 0.009155 | -0.10071 | -0.082397 | -0.21973 | -0.34332 | -0.24262 | -0.050354 | 121.4676 | 121.2067 | 17.3492 | -121.5408 | 121.376 | 121.4081 | 17.0242 | -121.5591
490.6562 | 121.6278 | -16.8594 | 104.5944 | -0.00099167 | 0.010737 | 0.07313 | 0.0042702 | 0.064497 | -0.006541 | -0.0042254 | 0.0069425 | -0.0019354 | 0.062534 | 0.064659 | -0.014112 | -0.0057421 | 104.3701 | -16.8594 | 0.45319 | -16.9189 | 104.5807 | -16.864 | -16.8961 | -17.0242 | 0.17395 | -17.0929 | 104.4891 | 104.5166 | -16.832 | -16.9281 | -0.004578 | -0.036621 | -0.013733 | 0 | -0.059509 | -0.022888 | -0.2243 | 0.027466 | -0.068665 | -0.10528 | -0.1648 | -0.23346 | -0.16479 | -0.077819 | 121.4401 | 121.2296 | 17.3126 | -121.4905 | 121.3486 | 121.376 | 17.0334 | -121.5225
492.3906 | 121.4996 | -16.745 | 104.805 | -0.00099167 | 0.0051826 | 0.067362 | 0.0046976 | 0.06407 | 0.0043536 | -0.0014484 | 0.014572 | 0.004046 | 0.065311 | 0.065514 | -0.0055671 | -0.010015 | 104.5029 | -16.7953 | 0.44403 | -16.7999 | 104.7867 | -16.6992 | -16.7587 | -16.9418 | 0.041199 | -17.0929 | 104.686 | 104.7363 | -16.6901 | -16.7816 | 0.045776 | -0.013733 | -0.018311 | -0.050354 | -0.054932 | -0.041199 | -0.30212 | 0.054932 | -0.036621 | -0.11902 | -0.19684 | -0.3479 | -0.31128 | -0.068665 | 121.5317 | 121.2479 | 17.189 | -121.5637 | 121.431 | 121.4813 | 16.7862 | -121.5866
494.0781 | 121.5637 | -16.0629 | 105.423 | 0.0066373 | 0.0047552 | 0.071634 | 0.0053384 | 0.064497 | -0.00055964 | -0.0025164 | -0.00068649 | -0.0023626 | 0.065097 | 0.065728 | -0.010267 | -0.0053149 | 105.098 | -16.1407 | 0.45319 | -16.1774 | 105.423 | -16.0721 | -16.1499 | -16.3284 | 0.11902 | -16.4017 | 105.3406 | 105.3635 | -16.0629 | -16.1407 | -0.009156 | -0.086975 | 0 | -0.07782 | -0.11444 | -0.027466 | -0.32501 | 0 | -0.07782 | -0.082398 | -0.2655 | -0.33875 | -0.26093 | -0.05951 | 121.4859 | 121.1609 | 16.5161 | -121.5729 | 121.4035 | 121.4264 | 16.1819 | -121.5637
495.75 | 121.5683 | -15.7242 | 105.7388 | -0.00099167 | 0.0073188 | 0.071207 | 0.0064066 | 0.06407 | -0.0046184 | -0.0046526 | 0.0069425 | -0.0019354 | 0.063175 | 0.064019 | -0.0087713 | -0.0059557 | 105.5374 | -15.6601 | 0.5722 | -15.7288 | 105.7251 | -15.7013 | -15.7562 | -15.8615 | 0.21515 | -15.9531 | 105.6198 | 105.6519 | -15.6738 | -15.77 | 0.022888 | -0.032044 | -0.013733 | 0.064087 | -0.004578 | 0.027466 | -0.20142 | 0.050354 | -0.045776 | -0.11902 | -0.13733 | -0.22888 | -0.18311 | -0.086976 | 121.4493 | 121.2616 | 16.2964 | -121.4951 | 121.344 | 121.376 | 15.9393 | -121.5088
497.4844 | 121.4859 | -15.2481 | 106.2515 | 0.014267 | 0.011378 | 0.07313 | 0.0017068 | 0.063215 | -0.005473 | -0.00508 | 0.0069425 | -0.0025762 | 0.063816 | 0.062523 | -0.0089849 | -0.0044605 | 106.0638 | -15.1428 | 0.52185 | -15.184 | 106.3385 | -15.1154 | -15.1703 | -15.3534 | 0.10529 | -15.4175 | 106.2286 | 106.2286 | -15.1016 | -15.2161 | 0.13275 | 0.07782 | 0.086975 | 0.10529 | 0.064087 | -0.013733 | -0.18768 | 0.14648 | 0.032044 | -0.022888 | -0.10529 | -0.16937 | -0.20142 | -0.022888 | 121.5866 | 121.312 | 15.77 | -121.4218 | 121.4767 | 121.4767 | 15.3534 | -121.4676
499.2188 | 121.6507 | -29.3198 | 92.0334 | -0.00099167 | 0.0034736 | 0.070566 | 0.0044838 | 0.063002 | 0.0037128 | -0.0031574 | 0.0069425 | 0.0036188 | 0.063388 | 0.065087 | -0.0072759 | -0.0072375 | 91.8777 | -29.4159 | 0.2655 | -29.5074 | 92.1021 | -29.4113 | -29.4342 | -29.6768 | 0.050354 | -29.7546 | 91.9876 | 91.9922 | -29.3655 | -29.4891 | -0.091553 | -0.11444 | 0.068665 | -0.096131 | -0.18768 | -0.073242 | -0.15564 | -0.045777 | -0.16937 | -0.045776 | -0.35706 | -0.43488 | -0.2655 | -0.041199 | 121.4218 | 121.1975 | 29.5853 | -121.4676 | 121.3074 | 121.3119 | 29.3701 | -121.5225
500.9531 | 121.6187 | -36.3876 | 84.9518 | 0.0066373 | 0.0073188 | 0.073771 | 0.0036294 | 0.065565 | -0.0048322 | -0.0029436 | -0.00068649 | -0.00022644 | 0.062107 | 0.063591 | -0.010053 | -0.0057421 | 84.8557 | -36.3327 | 0.21515 | -36.5021 | 84.9747 | -36.4334 | -36.4426 | -36.6989 | 0.17395 | -36.6852 | 84.874 | 84.9472 | -36.3831 | -36.5067 | -0.045777 | -0.054932 | 0.022888 | 0.054931 | -0.11444 | -0.059509 | -0.09613 | 0.004577 | -0.11902 | -0.07782 | -0.31128 | -0.29755 | -0.17853 | -0.004577 | 121.3623 | 121.2433 | 36.6028 | -121.3943 | 121.2616 | 121.3348 | 36.5616 | -121.4584
502.6875 | 121.2112 | -62.0636 | 59.3079 | -0.00099167 | 0.0034736 | 0.070993 | 0.0066202 | 0.067274 | -0.0018414 | -0.0035846 | -0.00068649 | 0.001269 | 0.062748 | 0.063591 | -0.011335 | -0.0051013 | 59.0652 | -61.972 | -0.11902 | -62.1643 | 59.2575 | -62.265 | -62.2421 | -62.5259 | -0.07782 | -62.4023 | 59.2209 | 59.2392 | -62.1277 | -62.3016 | -0.20142 | -0.17853 | -0.050354 | 0.091553 | -0.10071 | 0.077819 | -0.24261 | -0.064087 | -0.23804 | -0.086975 | -0.46234 | -0.33874 | -0.10071 | -0.068664 | 121.3211 | 121.1288 | 61.9446 | -121.55 | 121.2845 | 121.3028 | 61.9858 | -121.6095
504.4219 | 121.582 | -60.2005 | 61.1572 | 0.0066373 | 0.0051826 | 0.071421 | 0.007261 | 0.06407 | 0.00093576 | -0.00273 | -0.00068649 | -0.00044004 | 0.06467 | 0.066368 | -0.0098395 | -0.0070239 | 61.0703 | -59.9442 | 0.086975 | -60.2051 | 61.1572 | -60.2783 | -60.2463 | -60.5072 | 0.16479 | -60.3973 | 61.1481 | 61.1481 | -60.1181 | -60.3287 | -0.07782 | -0.045777 | 0 | 0.25635 | -0.004578 | 0.041199 | -0.086976 | 0.082397 | -0.12817 | -0.009156 | -0.3067 | -0.19684 | -0.068665 | -0.009156 | 121.3577 | 121.2708 | 60.2875 | -121.4035 | 121.3486 | 121.3486 | 60.3653 | -121.4859
506.0938 | 121.4859 | -57.9941 | 63.4415 | 0.014267 | 0.0041144 | 0.069498 | 0.0049112 | 0.065351 | 0.0043536 | -0.001021 | 0.0069425 | 0.0034052 | 0.063175 | 0.066582 | -0.0085577 | -0.0063831 | 63.2812 | -57.8293 | -0.027466 | -58.0261 | 63.5101 | -57.9987 | -57.962 | -58.3374 | -0.064087 | -58.3099 | 63.4048 | 63.4048 | -57.9254 | -58.1131 | -0.004577 | 0.032044 | 0.068665 | 0.16479 | -0.032043 | -0.064087 | -0.16022 | 0.068665 | -0.11902 | -0.036621 | -0.34332 | -0.31586 | -0.19684 | -0.036621 | 121.5042 | 121.2753 | 57.9666 | -121.4035 | 121.3989 | 121.3989 | 57.93 | -121.5546
507.8281 | 121.5225 | -56.012 | 65.4236 | 0.0066373 | 0.0075324 | 0.069498 | 0.0023476 | 0.068129 | 0.0020038 | -0.0037982 | 0.0069425 | 0.00041436 | 0.064457 | 0.065514 | -0.0087713 | -0.0042467 | 65.2588 | -55.8701 | -0.073242 | -56.0761 | 65.4739 | -56.0257 | -55.9982 | -56.3507 | -0.086975 | -56.3141 | 65.3641 | 65.3778 | -55.9387 | -56.131 | -0.013733 | 0.013733 | 0.050354 | 0.14191 | -0.064087 | -0.07782 | -0.1648 | 0.073242 | -0.11902 | -0.059509 | -0.33874 | -0.30212 | -0.18311 | -0.045776 | 121.4859 | 121.2708 | 55.9387 | -121.4218 | 121.376 | 121.3898 | 55.925 | -121.5546
509.5625 | 121.5271 | -55.0552 | 66.3666 | -0.00099167 | 0.0079596 | 0.069284 | 0.0042702 | 0.06407 | 0.00050836 | -0.0020892 | -0.00068649 | 0.0021234 | 0.062748 | 0.064232 | -0.0074897 | -0.0031787 | 66.1606 | -54.9225 | -0.032043 | -55.1422 | 66.362 | -55.0598 | -55.069 | -55.3986 | -0.004578 | -55.3436 | 66.2888 | 66.2979 | -54.9957 | -55.1468 | -0.004577 | -0.013733 | -0.004577 | 0.13275 | -0.086975 | -0.073242 | -0.20599 | 0.059509 | -0.091553 | -0.07782 | -0.34332 | -0.28839 | -0.19684 | -0.068664 | 121.4172 | 121.2158 | 55.0232 | -121.4355 | 121.344 | 121.3531 | 55.0507 | -121.5134
511.25 | 121.5775 | -52.7618 | 68.6783 | -0.0086212 | 0.011164 | 0.072916 | 0.005552 | 0.064283 | -0.0086774 | -0.0035846 | 0.029831 | -0.0030034 | 0.061039 | 0.061882 | -0.011976 | -0.0046741 | 68.3899 | -52.652 | 0.050354 | -52.8717 | 68.5455 | -52.8442 | -52.8305 | -53.1464 | 0.13733 | -52.9953 | 68.4677 | 68.541 | -52.7161 | -52.8946 | -0.082397 | -0.068664 | -0.13275 | 0.10986 | -0.10986 | -0.041199 | -0.28839 | 0.045777 | -0.13275 | -0.21057 | -0.38452 | -0.23346 | -0.10071 | -0.13733 | 121.3074 | 121.1517 | 52.8122 | -121.5088 | 121.2296 | 121.3028 | 52.8992 | -121.5729
512.9844 | 121.4584 | -48.967 | 72.5143 | 0.0066373 | 0.011805 | 0.072275 | 0.00085245 | 0.064711 | -0.0031232 | -0.00273 | 0.0069425 | -0.00022644 | 0.062748 | 0.064232 | -0.0087713 | -0.0042467 | 72.2672 | -48.8388 | 0.39368 | -49.0723 | 72.3084 | -49.0219 | -48.9944 | -49.3195 | 0.39825 | -49.2737 | 72.2488 | 72.2992 | -48.9578 | -49.1455 | -0.054932 | -0.027466 | -0.20599 | 0.12817 | -0.10529 | -0.07782 | -0.24719 | 0.009155 | -0.17853 | -0.2655 | -0.35248 | -0.3067 | -0.12817 | -0.21515 | 121.2753 | 121.2341 | 49.3607 | -121.5088 | 121.2158 | 121.2662 | 49.3652 | -121.6599
514.7188 | 121.4127 | -9.7229 | 111.8866 | 0.0066373 | 0.0083868 | 0.072062 | 0.0017068 | 0.062574 | 0.0015766 | -0.003371 | 0.014572 | 0.0014826 | 0.06467 | 0.063591 | -0.0062079 | -0.0070239 | 111.5341 | -9.6725 | 0.68207 | -9.6405 | 111.8637 | -9.5947 | -9.6863 | -9.7412 | 0.091553 | -9.8785 | 111.7355 | 111.763 | -9.6176 | -9.6863 | 0.12817 | 0.036621 | -0.022889 | 0.050354 | 0.082397 | 0.045776 | -0.35248 | 0.10528 | 0.036621 | -0.15106 | -0.018311 | -0.15564 | -0.19226 | -0.1236 | 121.5866 | 121.257 | 10.405 | -121.5729 | 121.4584 | 121.4859 | 9.8145 | -121.5729
516.4531 | 121.3715 | -8.8623 | 112.6923 | -0.00099167 | 0.012446 | 0.075479 | 0.0025612 | 0.061079 | -0.0031232 | -0.003371 | -0.00068649 | -0.0019354 | 0.062107 | 0.061455 | -0.010053 | -0.0031787 | 112.3581 | -8.7341 | 0.75531 | -8.7387 | 112.6419 | -8.7387 | -8.844 | -8.8577 | 0.14648 | -8.9584 | 112.5092 | 112.5549 | -8.7616 | -8.844 | 0.1236 | 0.018311 | -0.050354 | 0.12817 | 0.1236 | 0.10529 | -0.33417 | 0.10071 | 0.018311 | -0.18311 | 0.004578 | -0.09613 | -0.11444 | -0.13733 | 121.5042 | 121.2204 | 9.6176 | -121.5363 | 121.3715 | 121.4172 | 9.0088 | -121.5363
518.125 | 121.4676 | -8.2397 | 113.1958 | 0.0066373 | 0.0024054 | 0.070993 | 0.007261 | 0.063429 | 0.0011494 | -0.003371 | 0.0069425 | 0.002337 | 0.065097 | 0.064446 | -0.01048 | -0.0070239 | 112.8891 | -8.2397 | 0.81024 | -8.1848 | 113.237 | -8.2077 | -8.2809 | -8.2993 | 0.086975 | -8.4366 | 113.1409 | 113.1638 | -8.1985 | -8.2489 | 0.032043 | -0.041199 | 0.041199 | 0 | 0.054932 | 0.096131 | -0.3067 | 0.041199 | -0.009155 | -0.054932 | -0.059509 | -0.19684 | -0.18768 | -0.032044 | 121.4767 | 121.1288 | 9.05 | -121.4767 | 121.3806 | 121.4035 | 8.3267 | -121.4447
519.8594 | 121.4081 | -7.3334 | 114.093 | 0.014267 | 0.0071052 | 0.072916 | 0.0066202 | 0.062361 | -0.0033368 | -0.0025164 | 0.014572 | -0.0012946 | 0.063175 | 0.063591 | -0.0094123 | -0.0074511 | 113.8184 | -7.1777 | 0.97504 | -7.1777 | 114.0289 | -7.2784 | -7.3471 | -7.3196 | 0.23804 | -7.4295 | 113.9328 | 113.9877 | -7.2922 | -7.3334 | 0.054932 | -0.013733 | -0.064087 | 0.15564 | 0.15564 | 0.16937 | -0.27466 | 0.041199 | 0 | -0.16022 | 0.013733 | -0.09613 | -0.09613 | -0.10529 | 121.3623 | 121.1517 | 8.3084 | -121.4401 | 121.2662 | 121.3211 | 7.5714 | -121.4264
521.5312 | 121.4905 | -38.9008 | 83.2672 | 0.014267 | 0.0071052 | 0.070139 | 0.0074746 | 0.06407 | -0.00034604 | -0.0020892 | -0.00068649 | 0.0010554 | 0.064243 | 0.067437 | -0.010267 | -0.0072375 | 73.8739 | -44.1376 | 1.973 | -42.1875 | 79.1336 | -43.0664 | -42.4713 | -37.5 | 5.8502 | -37.1521 | 83.7662 | 83.8852 | -36.9461 | -36.9095 | -4.1656 | -3.5706 | -4.1336 | -5.2368 | -3.2867 | 0.28381 | -9.3933 | 1.9547 | 1.9913 | 0.49896 | 1.4008 | 1.7487 | -0.24262 | 0.61798 | 118.0344 | 112.7747 | 40.8737 | -125.7385 | 122.6669 | 122.7859 | 44.751 | -120.1767
523.2812 | 121.3303 | -4.4174 | 116.9952 | 0.0066373 | 0.004328 | 0.071634 | 0.0066202 | 0.062147 | -0.00077324 | -0.0042254 | 0.014572 | -0.002149 | 0.063602 | 0.064019 | -0.01048 | -0.0059557 | 116.6153 | -4.3304 | 1.0849 | -4.2801 | 116.9861 | -4.3854 | -4.4815 | -4.4083 | 0.14191 | -4.5456 | 116.8625 | 116.9128 | -4.3854 | -4.4449 | 0.032043 | -0.064087 | -0.009155 | 0.086975 | 0.13733 | 0.20142 | -0.37994 | 0.032043 | -0.027466 | -0.13275 | 0.009155 | -0.12817 | -0.10071 | -0.082397 | 121.4035 | 121.0327 | 5.5023 | -121.4767 | 121.2799 | 121.3303 | 4.5593 | -121.4401
525.0156 | 121.3211 | -6.0287 | 115.2969 | -0.00099167 | 0.0075324 | 0.070993 | 0.0070474 | 0.06172 | -0.0018414 | -0.0025164 | 0.0069425 | -0.0023626 | 0.064029 | 0.062523 | -0.011549 | -0.0055285 | 115.0452 | -5.8136 | 1.1581 | -5.8548 | 115.2832 | -5.9555 | -6.0287 | -5.9372 | 0.24719 | -6.0471 | 115.1733 | 115.1916 | -5.9692 | -6.0242 | 0.073243 | 0 | -0.013733 | 0.21515 | 0.17395 | 0.17395 | -0.25177 | 0.05951 | 0.004578 | -0.1236 | 0.091553 | -0.01831 | -0.022888 | -0.10529 | 121.312 | 121.0739 | 7.1869 | -121.3257 | 121.2021 | 121.2204 | 6.2759 | -121.3211
526.75 | 121.1563 | -4.6555 | 116.6382 | -0.00099167 | 0.012018 | 0.075052 | 0.0059792 | 0.061934 | -0.0031232 | -0.0052936 | 0.0069425 | -0.0027898 | 0.062534 | 0.064232 | -0.0091985 | -0.0053149 | 116.3361 | -4.4907 | 1.1398 | -4.4724 | 116.6199 | -4.5593 | -4.6463 | -4.6234 | 0.059509 | -4.7012 | 116.4825 | 116.5283 | -4.5959 | -4.6463 | 0.096131 | 0.009156 | -0.018311 | 0.16479 | 0.18311 | 0.17395 | -0.30212 | 0.05951 | 0.009156 | -0.15564 | 0.032044 | -0.045776 | -0.054932 | -0.10986 | 121.2753 | 120.9915 | 5.7953 | -121.2845 | 121.138 | 121.1838 | 4.715 | -121.2845
528.4844 | 121.2891 | -2.7374 | 118.5837 | 0.014267 | 0.006037 | 0.074625 | 0.0053384 | 0.064497 | 0.00029476 | -0.00508 | 0.0069425 | 0.0016962 | 0.063175 | 0.063805 | -0.0085577 | -0.0053149 | 118.2495 | -2.6276 | 1.2909 | -2.6093 | 118.5654 | -2.7237 | -2.8015 | -2.6825 | 0.1831 | -2.7512 | 118.5287 | 118.5425 | -2.7145 | -2.742 | 0.013733 | -0.064087 | -0.01831 | 0.10986 | 0.12817 | 0.19226 | -0.33417 | 0.022888 | -0.004577 | -0.054931 | 0.054932 | -0.013733 | -0.009156 | -0.041199 | 121.3028 | 120.9869 | 4.0283 | -121.3852 | 121.2662 | 121.2799 | 2.9205 | -121.3257
530.1562 | 121.2616 | -5.1132 | 116.1209 | -0.00099167 | 0.0028326 | 0.067789 | 0.0053384 | 0.065779 | 0.0037128 | -0.00273 | -0.00068649 | 0.0036188 | 0.065738 | 0.066582 | -0.0068487 | -0.0087329 | 115.6998 | -5.1407 | 1.1902 | -5.1178 | 115.9973 | -5.2185 | -5.3192 | -5.1636 | 0.073242 | -5.3696 | 115.892 | 115.9424 | -5.2231 | -5.278 | -0.10529 | -0.20599 | -0.1236 | -0.027466 | -0.004578 | 0.20142 | -0.42114 | -0.10986 | -0.16479 | -0.22888 | -0.050354 | -0.25635 | -0.091553 | -0.17853 | 121.1105 | 120.813 | 6.3034 | -121.4401 | 121.0052 | 121.0556 | 5.1865 | -121.3989
531.8906 | 121.2296 | -3.4012 | 118.0344 | 0.0066373 | 0.002619 | 0.073557 | 0.005552 | 0.064283 | -0.0012006 | -0.0020892 | 0.0069425 | -0.00086724 | 0.065738 | 0.065087 | -0.0079169 | -0.0053149 | 116.9128 | -3.9139 | 0.62714 | -3.8956 | 117.2882 | -3.978 | -4.0649 | -3.9505 | -0.50354 | -4.0421 | 117.2333 | 117.2653 | -3.9551 | -3.9917 | -0.57678 | -0.66376 | -0.74616 | -0.51269 | -0.49438 | 0.16937 | -1.1215 | -0.55389 | -0.59051 | -0.80109 | -0.54932 | -0.64087 | -0.050354 | -0.76904 | 120.6894 | 120.314 | 4.0283 | -122.0993 | 120.6345 | 120.6665 | 2.8976 | -122.0261
533.6406 | 121.1792 | -5.3192 | 115.9012 | -0.0086212 | 0.0092414 | 0.067789 | 0.0032022 | 0.062788 | 0.00029476 | -0.0020892 | 0.0069425 | 0.00062796 | 0.062961 | 0.066155 | -0.0083441 | -0.0072375 | 115.5762 | -5.2231 | 1.2039 | -5.1773 | 115.9241 | -5.2551 | -5.3558 | -5.2002 | 0.068665 | -5.3787 | 115.8234 | 115.86 | -5.2231 | -5.278 | 0.064087 | -0.036621 | 0.022888 | 0.096131 | 0.14191 | 0.17853 | -0.32501 | 0.096131 | 0.041199 | -0.07782 | 0.11902 | -0.059509 | -0.10071 | -0.041199 | 121.2433 | 120.8954 | 6.5231 | -121.257 | 121.1426 | 121.1792 | 5.3879 | -121.1792
535.375 | 121.1975 | -5.1819 | 115.8691 | 0.0066373 | 0.0096686 | 0.072702 | 0.0053384 | 0.063643 | -0.0039776 | -0.001662 | 0.0069425 | -0.0034308 | 0.063175 | 0.06231 | -0.012403 | -0.0061695 | 115.6128 | -5.0308 | 1.3458 | -5.0217 | 115.892 | -5.1407 | -5.2322 | -5.159 | 0.16022 | -5.191 | 115.773 | 115.8417 | -5.1453 | -5.2094 | 0.041199 | -0.050354 | 0.022888 | 0.15106 | 0.16022 | 0.21057 | -0.25635 | 0.036621 | -0.027466 | -0.096131 | 0.022888 | -0.009155 | 0.018311 | -0.027466 | 121.0739 | 120.7947 | 6.5277 | -121.1014 | 120.9549 | 121.0236 | 5.3421 | -121.0785
537.0469 | 121.0281 | -5.658 | 115.3244 | -0.00099167 | 0.0066778 | 0.071848 | 0.007261 | 0.063643 | -0.00055964 | -0.0029436 | -0.00068649 | -0.00086724 | 0.064884 | 0.06295 | -0.010053 | -0.0068103 | 115.0269 | -5.5252 | 1.3962 | -5.5389 | 115.2603 | -5.6488 | -5.7404 | -5.658 | 0.21515 | -5.7312 | 115.1871 | 115.1916 | -5.6854 | -5.7587 | 0.009155 | -0.082397 | -0.064087 | 0.13275 | 0.11902 | 0.20142 | -0.29755 | -0.027466 | -0.10071 | -0.13733 | 0 | -0.073242 | 0.027466 | -0.13275 | 120.9183 | 120.6848 | 7.0541 | -121.0648 | 120.845 | 120.8496 | 5.8731 | -121.0831
538.7969 | 120.9274 | -17.244 | 103.6926 | 0.0066373 | 0.007746 | 0.068644 | 0.00085245 | 0.063429 | 0.0037128 | -0.0025164 | -0.00068649 | 0.0031916 | 0.063175 | 0.064446 | -0.0072759 | -0.0072375 | 103.2303 | -17.569 | 0.68665 | -17.4088 | 103.4775 | -17.3813 | -17.4866 | -17.5232 | -0.09613 | -17.6743 | 103.4317 | 103.3768 | -17.363 | -17.4408 | -0.13733 | -0.24261 | -0.21515 | -0.32501 | -0.16479 | 0.07782 | -0.46234 | -0.11902 | -0.19684 | -0.26093 | -0.27923 | -0.4303 | -0.23346 | -0.31586 | 120.7214 | 120.4742 | 17.9306 | -121.1792 | 120.6757 | 120.6207 | 17.1478 | -121.1334
540.5469 | 120.8267 | -7.7042 | 113.118 | 0.014267 | 0.007746 | 0.07078 | 0.0079018 | 0.061934 | -0.0018414 | -0.0031574 | 0.0069425 | 0.00062796 | 0.065311 | 0.063378 | -0.0091985 | -0.0042467 | 112.6053 | -7.8186 | 1.1948 | -7.7591 | 112.9669 | -7.8003 | -7.9056 | -7.9056 | 0.12817 | -7.988 | 112.9074 | 112.9532 | -7.7957 | -7.869 | -0.09613 | -0.20142 | -0.15106 | -0.11444 | -0.054931 | 0.14649 | -0.51269 | -0.091552 | -0.16479 | -0.21057 | -0.20142 | -0.28381 | -0.11902 | -0.16479 | 120.6711 | 120.3094 | 8.8989 | -121.0236 | 120.6116 | 120.6573 | 7.8323 | -120.9869
542.2188 | 120.7809 | -5.4382 | 115.2603 | 0.014267 | 0.0028326 | 0.067362 | 0.005552 | 0.06407 | 0.002431 | -0.00273 | 0.0069425 | 0.001269 | 0.063175 | 0.064873 | -0.0079169 | -0.0055285 | 115.1871 | -5.1956 | 1.7944 | -5.2094 | 115.4526 | -5.3101 | -5.4291 | -5.278 | 0.59052 | -5.4703 | 115.3427 | 115.3564 | -5.3101 | -5.3787 | 0.12817 | 0.009155 | 0.19226 | 0.24261 | 0.22888 | 0.21973 | -0.073242 | 0.12817 | 0.059509 | 0.082397 | 0.16022 | -0.032044 | -0.091553 | 0.09613 | 120.8908 | 120.6253 | 7.2327 | -120.6894 | 120.7809 | 120.7947 | 6.0287 | -120.639
543.9688 | 120.5841 | -8.1345 | 112.4588 | -0.00099167 | 0.0098822 | 0.069071 | 0.002134 | 0.064283 | -0.0039776 | -0.0029436 | -0.008316 | -0.0010808 | 0.062961 | 0.066368 | -0.0081305 | -0.0051013 | 112.2803 | -7.933 | 1.3779 | -7.933 | 112.5137 | -7.9834 | -8.0658 | -7.9971 | 0.27924 | -8.0612 | 112.4542 | 112.4908 | -7.933 | -8.0017 | 0.15106 | 0.068664 | 0.054932 | 0.20142 | 0.20142 | 0.13275 | -0.17853 | 0.20142 | 0.13275 | -0.004577 | 0.13733 | 0.073242 | -0.059509 | 0.032044 | 120.6482 | 120.4147 | 9.5123 | -120.5246 | 120.5887 | 120.6253 | 8.4137 | -120.4605
545.7031 | 120.9457 | -0.16937 | 120.9412 | -0.00099167 | 0.0036872 | 0.068003 | 0.003843 | 0.063856 | 0.00093576 | -0.0031574 | -0.00068649 | 0.0019098 | 0.065097 | 0.063591 | -0.0062079 | -0.0068103 | 120.607 | -0.009155 | 1.6617 | 0.041199 | 120.9137 | -0.09613 | -0.2243 | -0.036621 | 0.11902 | -0.19226 | 120.845 | 120.8725 | -0.1236 | -0.15106 | 0.073243 | -0.054931 | -0.027466 | 0.16022 | 0.21057 | 0.2655 | -0.33417 | 0.045777 | 0.018311 | -0.09613 | 0.13275 | -0.022888 | -0.041199 | -0.068664 | 121.0831 | 120.7764 | 1.8311 | -121.1655 | 121.0144 | 121.0419 | 0.28839 | -121.0922
547.375 | 121.2067 | -0.16479 | 121.0052 | -0.00099167 | 0.0030464 | 0.070353 | 0.0064066 | 0.066847 | 0.00050836 | -0.0029436 | 0.014572 | 0.002978 | 0.062748 | 0.065087 | -0.0074897 | -0.0068103 | 120.6573 | -0.068665 | 1.6754 | 0.022888 | 121.0556 | -0.11902 | -0.21973 | -0.082397 | 0.12817 | -0.17853 | 120.9457 | 120.9595 | -0.12817 | -0.17395 | 0.045776 | -0.054932 | 0.050354 | 0.09613 | 0.18768 | 0.24261 | -0.3479 | 0.036621 | -0.009155 | -0.059509 | 0.082398 | -0.013733 | -0.004578 | -0.045776 | 121.2204 | 120.8221 | 1.8402 | -121.225 | 121.1105 | 121.1243 | 0.29297 | -121.1792
549.1406 | 121.2112 | -0.15564 | 121.0419 | 0.0066373 | 0.004969 | 0.071634 | 0.0087564 | 0.064711 | -0.0022686 | -0.0037982 | -0.00068649 | -0.00065364 | 0.064884 | 0.065514 | -0.01283 | -0.0048877 | 120.6619 | -0.073242 | 1.6891 | -0.032043 | 121.0785 | -0.15106 | -0.24261 | -0.11444 | 0.10986 | -0.21057 | 120.9869 | 121.0281 | -0.14648 | -0.16937 | 0.004578 | -0.086975 | 0.036621 | 0.082398 | 0.1236 | 0.21057 | -0.37994 | 0.009156 | -0.013733 | -0.054932 | 0.041199 | -0.054931 | -0.041198 | -0.013733 | 121.2341 | 120.8176 | 1.8448 | -121.2845 | 121.1426 | 121.1838 | 0.2655 | -121.2112
550.8906 | 121.2662 | -0.12817 | 121.0648 | 0.0066373 | 0.0092414 | 0.072916 | 0.0076882 | 0.067274 | -0.0067548 | -0.0055072 | 0.0069425 | -0.0036444 | 0.063388 | 0.062737 | -0.012189 | -0.0038195 | 120.7809 | 0.064087 | 1.8036 | 0.064087 | 121.0968 | -0.082397 | -0.19684 | 0 | 0.22888 | -0.054932 | 120.9595 | 121.0281 | -0.11444 | -0.15564 | 0.045777 | -0.068664 | 0.032044 | 0.19226 | 0.19226 | 0.26093 | -0.28381 | 0.013733 | -0.027466 | -0.10528 | 0.12817 | 0.073242 | 0.10071 | -0.036621 | 121.225 | 120.9091 | 1.9318 | -121.2616 | 121.0876 | 121.1563 | 0.35706 | -121.2204
552.5781 | 121.3348 | -0.15106 | 121.0831 | 0.014267 | 0.004328 | 0.072062 | 0.0076882 | 0.063856 | 0.0015766 | -0.004439 | 0.014572 | 0.002337 | 0.066379 | 0.062737 | -0.0072759 | -0.0068103 | 120.7352 | -0.082397 | 1.7715 | 0.004578 | 121.138 | -0.13275 | -0.23346 | -0.10986 | 0.10529 | -0.20142 | 121.0373 | 121.0556 | -0.13733 | -0.1831 | 0.018311 | -0.082397 | 0.054931 | 0.068665 | 0.15564 | 0.23804 | -0.3479 | 0.013733 | -0.032043 | -0.045777 | 0.041199 | -0.050354 | -0.018311 | -0.027466 | 121.2891 | 120.8862 | 1.9226 | -121.3165 | 121.1884 | 121.2067 | 0.25635 | -121.2662
554.3125 | 121.3074 | -0.16022 | 121.1334 | 0.0066373 | 0.011378 | 0.072702 | 0.0042702 | 0.063002 | -0.0061138 | -0.0057208 | 0.0069425 | -0.0027898 | 0.06232 | 0.063805 | -0.011335 | -0.0080921 | 120.7672 | -0.018311 | 1.8082 | 0.027466 | 121.138 | -0.086975 | -0.21973 | -0.050354 | 0.15106 | -0.10071 | 121.0007 | 121.0602 | -0.11444 | -0.16479 | 0.073242 | -0.05951 | 0.004577 | 0.14191 | 0.18768 | 0.24719 | -0.36621 | 0.045776 | -0.004578 | -0.13275 | 0.10986 | 0.059509 | 0.064087 | -0.073242 | 121.2982 | 120.9274 | 1.9684 | -121.3531 | 121.1609 | 121.2204 | 0.31128 | -121.2982
556.0469 | 121.1975 | -0.21515 | 121.1426 | 0.0066373 | 0.0058234 | 0.071848 | 0.003843 | 0.064497 | 0.004781 | -0.003371 | 0.0069425 | 0.0025508 | 0.064457 | 0.065728 | -0.0053533 | -0.0061695 | 120.8176 | -0.064087 | 1.8585 | 0.004578 | 121.17 | -0.12817 | -0.24261 | -0.086975 | 0.064087 | -0.21973 | 121.0648 | 121.0968 | -0.13733 | -0.18768 | 0.086975 | -0.027466 | 0.027466 | 0.15106 | 0.21973 | 0.24719 | -0.32501 | 0.07782 | 0.027466 | -0.07782 | 0.12817 | -0.004578 | -0.032044 | -0.045776 | 121.3852 | 121.0327 | 2.0737 | -121.3852 | 121.2799 | 121.312 | 0.27924 | -121.3303
557.7969 | 121.2158 | -0.20142 | 121.1655 | 0.0066373 | 0.0083868 | 0.069498 | 0.003843 | 0.063215 | 0.00093576 | -0.0042254 | -0.00068649 | 0.0031916 | 0.062748 | 0.064659 | -0.0070623 | -0.0051013 | 120.7535 | -0.13733 | 1.8173 | -0.027466 | 121.1838 | -0.1236 | -0.25635 | -0.1236 | 0.018311 | -0.24719 | 121.0876 | 121.1288 | -0.15106 | -0.19226 | 0.07782 | -0.054932 | 0.018311 | 0.064087 | 0.17395 | 0.22888 | -0.41199 | 0.050354 | 0.009155 | -0.07782 | 0.07782 | -0.045776 | -0.054931 | -0.036621 | 121.3852 | 120.9549 | 2.0187 | -121.4218 | 121.2891 | 121.3303 | 0.21973 | -121.3577
559.5312 | 121.2067 | -0.20599 | 121.1655 | 0.014267 | 0.00326 | 0.068857 | 0.002134 | 0.065138 | 0.0015766 | -0.0012346 | 0.0069425 | 0.00084176 | 0.063602 | 0.062737 | -0.0068487 | -0.0070239 | 120.8038 | -0.073242 | 1.8906 | -0.004578 | 121.1746 | -0.11902 | -0.23804 | -0.091553 | 0.059509 | -0.25177 | 121.0876 | 121.1288 | -0.15106 | -0.19684 | 0.086975 | -0.032043 | 0.009156 | 0.13275 | 0.20142 | 0.23346 | -0.36163 | 0.054932 | 0.009156 | -0.07782 | 0.11444 | -0.045776 | -0.054932 | -0.036621 | 121.3806 | 121.0098 | 2.0966 | -121.4035 | 121.2936 | 121.3348 | 0.2655 | -121.3623
561.2188 | 121.2204 | -0.20599 | 121.1838 | 0.0066373 | 0.010309 | 0.072916 | 0.0057656 | 0.062574 | -0.0061138 | -0.0042254 | -0.008316 | -0.0030034 | 0.065097 | 0.062096 | -0.010694 | -0.0038195 | 120.8359 | 0.018311 | 1.9547 | 0.022888 | 121.1197 | -0.086975 | -0.19226 | -0.054932 | 0.12817 | -0.13275 | 121.0236 | 121.1243 | -0.11444 | -0.15106 | 0.11902 | 0.013733 | -0.064087 | 0.22431 | 0.22888 | 0.21515 | -0.3479 | 0.091553 | 0.054932 | -0.16022 | 0.15106 | 0.073243 | 0.018311 | -0.059509 | 121.3257 | 121.0419 | 2.1606 | -121.376 | 121.2296 | 121.3303 | 0.33417 | -121.3348
562.9688 | 121.3623 | -0.14648 | 121.138 | 0.0066373 | 0.0079596 | 0.071207 | 0.0070474 | 0.065565 | -0.0063274 | -0.0042254 | 0.0069425 | -0.0027898 | 0.063388 | 0.062523 | -0.012403 | -0.0051013 | 120.8862 | 0.082397 | 2.0325 | 0.073242 | 121.1655 | -0.10529 | -0.20599 | 0 | 0.25177 | -0.059509 | 121.0281 | 121.106 | -0.11444 | -0.16022 | 0.041198 | -0.05951 | 0.027466 | 0.22888 | 0.21973 | 0.27924 | -0.25177 | 0.032043 | -0.013733 | -0.10986 | 0.14648 | 0.086975 | 0.10071 | -0.032043 | 121.3119 | 121.0327 | 2.179 | -121.344 | 121.1746 | 121.2524 | 0.39825 | -121.2982
564.6562 | 121.3348 | -0.18768 | 121.1426 | -0.00099167 | 0.004328 | 0.072489 | 0.0079018 | 0.063002 | -0.0014142 | -0.0042254 | 0.0069425 | 0.0010554 | 0.066806 | 0.064019 | -0.010908 | -0.0070239 | 120.8176 | -0.068665 | 1.9455 | -0.022888 | 121.1838 | -0.13275 | -0.25177 | -0.13733 | 0.09613 | -0.21515 | 121.1151 | 121.138 | -0.16022 | -0.19684 | 0.054932 | -0.064087 | 0.041199 | 0.11902 | 0.16479 | 0.22888 | -0.32501 | 0.027466 | -0.009155 | -0.027466 | 0.050354 | -0.027466 | -0.018311 | -0.004578 | 121.3715 | 121.0052 | 2.1332 | -121.3943 | 121.3028 | 121.3257 | 0.28381 | -121.3394
566.4062 | 121.3852 | -0.15564 | 121.1609 | -0.00099167 | 0.0045416 | 0.069712 | 0.0042702 | 0.064711 | 0.0015766 | -0.003371 | 0.014572 | 0.00062796 | 0.065738 | 0.0653 | -0.0091985 | -0.0085193 | 120.813 | -0.091553 | 1.9638 | -0.013733 | 121.2067 | -0.15106 | -0.24719 | -0.10529 | 0.09613 | -0.22888 | 121.1288 | 121.1838 | -0.15106 | -0.18768 | 0.004578 | -0.091552 | 0.045776 | 0.064087 | 0.14191 | 0.23346 | -0.3479 | 0.004578 | -0.032043 | -0.032044 | 0.050354 | -0.073242 | -0.041199 | 0.022888 | 121.3623 | 120.9686 | 2.1194 | -121.4081 | 121.2845 | 121.3394 | 0.25177 | -121.3486
568.1562 | 121.3348 | -0.16937 | 121.1655 | 0.0066373 | 0.0068916 | 0.074198 | 0.0064066 | 0.064283 | -0.0016278 | -0.0037982 | 0.014572 | 0.0016962 | 0.063816 | 0.064019 | -0.0081305 | -0.0053149 | 120.8588 | -0.027466 | 2.0325 | 0.009155 | 121.2021 | -0.13275 | -0.23346 | -0.11444 | 0.10529 | -0.21057 | 121.1105 | 121.1884 | -0.16937 | -0.19684 | 0.036622 | -0.064086 | 0.036621 | 0.14191 | 0.17853 | 0.24261 | -0.3067 | 0 | -0.027465 | -0.054931 | 0.054932 | -0.041198 | -0.013733 | 0.022888 | 121.3715 | 121.0281 | 2.2018 | -121.3989 | 121.2799 | 121.3577 | 0.27466 | -121.3623
569.8906 | 121.3394 | -0.1831 | 121.1792 | 0.0066373 | 0.0058234 | 0.071848 | 0.0040566 | 0.063856 | -0.0022686 | -0.004439 | 0.022202 | 0.00041436 | 0.063816 | 0.063378 | -0.0079169 | -0.0063831 | 120.9045 | 0.059509 | 2.1194 | 0.059509 | 121.1929 | -0.09613 | -0.21973 | -0.022888 | 0.2243 | -0.10529 | 121.0922 | 121.138 | -0.11444 | -0.16022 | 0.086975 | -0.036622 | 0.013733 | 0.24261 | 0.24261 | 0.27924 | -0.27466 | 0.068664 | 0.022888 | -0.086975 | 0.16022 | 0.077819 | 0.054931 | -0.041199 | 121.376 | 121.0876 | 2.3026 | -121.3989 | 121.2753 | 121.3211 | 0.40741 | -121.3394
571.625 | 121.3394 | -0.17853 | 121.1838 | 0.0066373 | 0.007746 | 0.071421 | 0.0053384 | 0.064711 | -0.0044048 | -0.0057208 | 0.014572 | -0.00086724 | 0.064884 | 0.062737 | -0.01048 | -0.0072375 | 120.9366 | 0.059509 | 2.1332 | 0.064087 | 121.1746 | -0.07782 | -0.19226 | -0.013733 | 0.2243 | -0.10986 | 121.1105 | 121.1517 | -0.10986 | -0.16479 | 0.10071 | -0.013733 | -0.009155 | 0.23804 | 0.24261 | 0.25635 | -0.24719 | 0.068665 | 0.013733 | -0.073242 | 0.16479 | 0.068665 | 0.054932 | -0.032044 | 121.3531 | 121.1151 | 2.3117 | -121.376 | 121.2891 | 121.3303 | 0.40283 | -121.3486
573.2969 | 121.2799 | -0.19684 | 121.2387 | 0.0066373 | 0.0028326 | 0.069498 | 0.0032022 | 0.064497 | 0.0039264 | -0.0046526 | 0.0069425 | 0.002337 | 0.065525 | 0.065514 | -0.0068487 | -0.0076647 | 120.9183 | -0.050354 | 2.0737 | 0.009155 | 121.225 | -0.11902 | -0.21057 | -0.07782 | 0.064087 | -0.2243 | 121.1472 | 121.1884 | -0.14648 | -0.17395 | 0.077819 | -0.013733 | -0.013732 | 0.14648 | 0.20599 | 0.21973 | -0.32043 | 0.050354 | 0.022888 | -0.091552 | 0.11902 | -0.027466 | -0.050354 | -0.050354 | 121.4218 | 121.1151 | 2.2705 | -121.4493 | 121.344 | 121.3852 | 0.26093 | -121.4127
575.0312 | 121.3486 | -0.15564 | 121.2112 | 0.014267 | 0.00090997 | 0.069498 | 0.0049112 | 0.065351 | 0.002431 | -0.001021 | 0.0069425 | 0.0014826 | 0.065525 | 0.064446 | -0.0079169 | -0.0072375 | 120.9137 | -0.013733 | 2.1286 | 0.018311 | 121.2662 | -0.1236 | -0.21515 | -0.041199 | 0.12817 | -0.18768 | 121.1517 | 121.1792 | -0.1236 | -0.1831 | 0.032044 | -0.059509 | 0.054931 | 0.14191 | 0.17395 | 0.23346 | -0.29755 | 0.032044 | -0.027465 | -0.05951 | 0.11444 | -0.032043 | -0.004578 | -0.032044 | 121.4218 | 121.0693 | 2.2842 | -121.4264 | 121.3074 | 121.3348 | 0.28381 | -121.3943
576.7656 | 121.3943 | -0.15564 | 121.1884 | -0.00099167 | 0.0066778 | 0.072489 | 0.0036294 | 0.063002 | -0.002055 | -0.0031574 | 0.022202 | 0.0014826 | 0.064029 | 0.062737 | -0.0083441 | -0.0057421 | 120.8313 | -0.082397 | 2.0691 | -0.027466 | 121.2296 | -0.14648 | -0.23346 | -0.13275 | 0.086975 | -0.2243 | 121.1609 | 121.2067 | -0.13733 | -0.1831 | 0.009156 | -0.077819 | 0.041199 | 0.073243 | 0.12817 | 0.20599 | -0.35706 | 0.018311 | -0.027465 | -0.027465 | 0.022889 | -0.068664 | -0.041199 | 0.018311 | 121.3852 | 120.9869 | 2.2247 | -121.4218 | 121.3165 | 121.3623 | 0.24261 | -121.3715
578.4531 | 121.2936 | -0.19226 | 121.2204 | 0.014267 | 0.0068916 | 0.067789 | 0.0029886 | 0.06407 | 0.001363 | -0.003371 | 0.0069425 | -0.00022644 | 0.064884 | 0.065514 | -0.0068487 | -0.0053149 | 120.8084 | -0.11444 | 2.0737 | -0.004578 | 121.2753 | -0.13275 | -0.24261 | -0.11444 | 0.009155 | -0.2243 | 121.138 | 121.2067 | -0.12817 | -0.20142 | 0.05951 | -0.050354 | 0.054932 | 0.07782 | 0.18768 | 0.23804 | -0.41199 | 0.064087 | -0.009155 | -0.082398 | 0.07782 | -0.032043 | -0.022888 | -0.013733 | 121.4676 | 121.0007 | 2.2659 | -121.463 | 121.3303 | 121.3989 | 0.20142 | -121.4218
580.1875 | 121.4218 | -0.15564 | 121.1884 | 0.014267 | 0.002619 | 0.070566 | 0.0076882 | 0.063429 | -0.00013244 | -0.0029436 | -0.008316 | 0.0010554 | 0.063388 | 0.064659 | -0.0096259 | -0.0044605 | 120.8405 | -0.091553 | 2.1149 | -0.013733 | 121.2433 | -0.1236 | -0.23804 | -0.11902 | 0.086975 | -0.21515 | 121.1884 | 121.225 | -0.13275 | -0.17853 | 0.032044 | -0.082397 | 0.054932 | 0.064087 | 0.14191 | 0.2243 | -0.3479 | 0.022889 | -0.022888 | 0 | 0.036621 | -0.059509 | -0.036621 | 0.036622 | 121.3989 | 120.9961 | 2.2705 | -121.4264 | 121.344 | 121.3806 | 0.24261 | -121.3669
581.9219 | 121.4127 | -0.13733 | 121.225 | 0.0066373 | 0.0047552 | 0.07078 | 0.0036294 | 0.061293 | -0.00013244 | -0.0037982 | 0.022202 | -0.00022644 | 0.065311 | 0.064232 | -0.0096259 | -0.0055285 | 120.8359 | -0.07782 | 2.1332 | -0.022888 | 121.257 | -0.14191 | -0.23346 | -0.10529 | 0.073242 | -0.20599 | 121.1838 | 121.2112 | -0.13275 | -0.17853 | -0.004578 | -0.09613 | 0.032043 | 0.059509 | 0.11444 | 0.21057 | -0.3891 | 0.004578 | -0.041199 | -0.041199 | 0.032043 | -0.068665 | -0.027466 | -0.013733 | 121.3943 | 120.9732 | 2.2705 | -121.4584 | 121.3211 | 121.3486 | 0.21057 | -121.4035
583.6719 | 121.2936 | -0.20142 | 121.2387 | 0.0066373 | 0.010309 | 0.072062 | 0.0068338 | 0.065565 | -0.0044048 | -0.003371 | -0.00068649 | -0.0036444 | 0.066166 | 0.063591 | -0.010694 | -0.0059557 | 120.9091 | 0.032043 | 2.2202 | 0.032043 | 121.2296 | -0.086975 | -0.19226 | -0.036621 | 0.11902 | -0.11902 | 121.1014 | 121.1792 | -0.11902 | -0.16479 | 0.11444 | 0.009155 | -0.009155 | 0.23346 | 0.23346 | 0.2243 | -0.32959 | 0.082397 | 0.036621 | -0.13733 | 0.1648 | 0.082397 | 0.045776 | -0.059509 | 121.431 | 121.1105 | 2.4216 | -121.431 | 121.3028 | 121.3806 | 0.32044 | -121.4035
585.3438 | 121.2662 | -0.19684 | 121.2524 | 0.014267 | 0.0133 | 0.071848 | 0.00085245 | 0.063002 | -0.0026958 | -0.0048662 | -0.008316 | 0.00062796 | 0.05997 | 0.063805 | -0.0085577 | -0.0048877 | 120.9641 | 0.041199 | 2.2522 | 0.036621 | 121.2204 | -0.086975 | -0.16937 | -0.018311 | 0.13275 | -0.10071 | 121.1288 | 121.1792 | -0.09613 | -0.13733 | 0.10986 | 0.027465 | -0.032043 | 0.23804 | 0.23346 | 0.20599 | -0.28839 | 0.10071 | 0.059509 | -0.1236 | 0.17853 | 0.09613 | 0.036621 | -0.073242 | 121.4172 | 121.1609 | 2.449 | -121.4218 | 121.3257 | 121.376 | 0.32959 | -121.3898
587.0781 | 121.4401 | -0.15106 | 121.1929 | 0.014267 | 0.0056098 | 0.071848 | 0.0066202 | 0.062574 | 0.0034992 | -0.0035846 | -0.00068649 | 0.0025508 | 0.062748 | 0.064446 | -0.0072759 | -0.0044605 | 120.8771 | -0.082397 | 2.2018 | -0.004578 | 121.2891 | -0.1236 | -0.23804 | -0.086975 | 0.10986 | -0.20142 | 121.2021 | 121.2204 | -0.14191 | -0.17853 | 0.027466 | -0.086975 | 0.09613 | 0.068665 | 0.14648 | 0.23346 | -0.31586 | 0.009155 | -0.027466 | 0.009155 | 0.064087 | -0.050354 | -0.022888 | 0.027466 | 121.4401 | 121.0281 | 2.3529 | -121.431 | 121.3531 | 121.3715 | 0.26093 | -121.3715
588.8281 | 121.2708 | -0.1831 | 121.2479 | -0.00099167 | 0.013514 | 0.073771 | 0.0046976 | 0.062788 | -0.0044048 | -0.0035846 | -0.00068649 | -0.0015082 | 0.062107 | 0.065087 | -0.0094123 | -0.0051013 | 120.9412 | 0.045776 | 2.298 | 0.064087 | 121.2112 | -0.10986 | -0.16937 | -0.013733 | 0.12817 | -0.10986 | 121.1151 | 121.1838 | -0.09613 | -0.14191 | 0.073242 | 0.013732 | -0.036621 | 0.22888 | 0.24719 | 0.23346 | -0.3067 | 0.086975 | 0.041198 | -0.13275 | 0.16937 | 0.073242 | 0.032044 | -0.064087 | 121.3943 | 121.1243 | 2.4811 | -121.4172 | 121.2982 | 121.3669 | 0.31128 | -121.3898
590.5625 | 121.3074 | -0.19226 | 121.225 | -0.0086212 | 0.012018 | 0.073343 | 0.0014932 | 0.063002 | -0.0046184 | -0.0063616 | -0.008316 | -0.0012946 | 0.06232 | 0.06295 | -0.010267 | -0.0059557 | 120.932 | 0.009155 | 2.2751 | 0.036621 | 121.2479 | -0.091553 | -0.17853 | -0.059509 | 0.11902 | -0.1236 | 121.1334 | 121.2067 | -0.09613 | -0.15564 | 0.10071 | 0.013733 | 0.022888 | 0.20142 | 0.22888 | 0.21515 | -0.29297 | 0.096131 | 0.036621 | -0.091553 | 0.13275 | 0.068665 | 0.032044 | -0.018311 | 121.4401 | 121.1243 | 2.4673 | -121.4035 | 121.3257 | 121.3989 | 0.31128 | -121.3806
592.2344 | 121.3348 | -0.19684 | 121.2708 | 0.0066373 | 0.0092414 | 0.072489 | 0.00021145 | 0.063643 | 0.0022174 | -0.00508 | 0.0069425 | 0.00084176 | 0.060611 | 0.064659 | -0.0068487 | -0.0061695 | 121.0007 | 0.050354 | 2.3529 | 0.073242 | 121.2662 | -0.082397 | -0.17853 | 0.032043 | 0.16479 | -0.091553 | 121.1517 | 121.2112 | -0.09613 | -0.12817 | 0.11444 | 0.01831 | -0.004578 | 0.24719 | 0.27008 | 0.25177 | -0.27008 | 0.10071 | 0.068664 | -0.11902 | 0.22888 | 0.10529 | 0.036621 | -0.059509 | 121.463 | 121.1975 | 2.5497 | -121.4493 | 121.3486 | 121.4081 | 0.36163 | -121.3989
593.9844 | 121.3852 | -0.16937 | 121.2387 | 0.0066373 | 0.0058234 | 0.072275 | 0.0042702 | 0.062361 | -0.0033368 | -0.0042254 | 0.0069425 | -0.00065364 | 0.062107 | 0.062737 | -0.010053 | -0.0059557 | 120.9869 | 0.050354 | 2.3804 | 0.07782 | 121.2204 | -0.10071 | -0.19226 | -0.004578 | 0.21057 | -0.09613 | 121.138 | 121.2204 | -0.091553 | -0.14191 | 0.068665 | -0.022888 | -0.01831 | 0.21973 | 0.24719 | 0.27008 | -0.25177 | 0.07782 | 0.027466 | -0.10071 | 0.16479 | 0.073243 | 0.045777 | -0.01831 | 121.3898 | 121.1563 | 2.5497 | -121.431 | 121.3074 | 121.3898 | 0.37994 | -121.3806
595.7188 | 121.4172 | -0.15564 | 121.2433 | -0.00099167 | 0.0053962 | 0.072489 | 0.0040566 | 0.061293 | -0.0031232 | -0.0052936 | -0.00068649 | -0.0010808 | 0.062748 | 0.061455 | -0.01048 | -0.0076647 | 120.9869 | 0.059509 | 2.417 | 0.09613 | 121.2433 | -0.091553 | -0.19226 | 0.013733 | 0.22888 | -0.073242 | 121.1426 | 121.2204 | -0.11444 | -0.15106 | 0.064087 | -0.036621 | 0 | 0.21515 | 0.25177 | 0.28839 | -0.25635 | 0.041199 | 0.004578 | -0.10071 | 0.16937 | 0.082398 | 0.07782 | -0.022888 | 121.3989 | 121.1426 | 2.5726 | -121.4355 | 121.2982 | 121.376 | 0.38452 | -121.3943
597.4531 | 121.3577 | -0.16022 | 121.2662 | 0.0066373 | 0.0092414 | 0.067575 | 0.002134 | 0.060438 | -0.0014142 | -0.0035846 | 0.014572 | -1.2844e-05 | 0.061893 | 0.065728 | -0.0085577 | -0.010015 | 121.0098 | 0.041199 | 2.3895 | 0.086975 | 121.2387 | -0.07782 | -0.1831 | 0.036621 | 0.15106 | -0.09613 | 121.138 | 121.2204 | -0.082397 | -0.13275 | 0.082397 | -0.022888 | -0.027466 | 0.20142 | 0.24719 | 0.27008 | -0.25635 | 0.07782 | 0.027466 | -0.12817 | 0.19684 | 0.064087 | 0.036621 | -0.045776 | 121.3989 | 121.17 | 2.5497 | -121.4493 | 121.2982 | 121.3806 | 0.31128 | -121.3989
599.1562 | 121.3623 | -0.1831 | 121.2799 | 0.0066373 | 0.009455 | 0.070993 | 0.0029886 | 0.064711 | 0.0020038 | -0.00080744 | 0.0069425 | 0.0016962 | 0.063602 | 0.063378 | -0.0059943 | -0.0063831 | 120.9961 | 0.045776 | 2.4033 | 0.068665 | 121.2433 | -0.086975 | -0.19226 | 0.050354 | 0.15106 | -0.091553 | 121.1517 | 121.2021 | -0.086975 | -0.13733 | 0.09613 | -0.009156 | -0.036621 | 0.22888 | 0.25177 | 0.26093 | -0.28381 | 0.09613 | 0.045776 | -0.12817 | 0.23346 | 0.091552 | 0.045776 | -0.07782 | 121.4264 | 121.1792 | 2.5864 | -121.4722 | 121.3348 | 121.3852 | 0.33417 | -121.4172
600.8906 | 121.312 | -0.19226 | 121.2708 | 0.014267 | 0.0053962 | 0.068644 | 0.0019204 | 0.063643 | 0.0022174 | -0.0023028 | 0.014572 | 0.004046 | 0.064884 | 0.064019 | -0.0055671 | -0.0065967 | 120.9229 | -0.068665 | 2.3438 | 0 | 121.3028 | -0.11444 | -0.23346 | -0.068665 | 0.050354 | -0.23346 | 121.1838 | 121.2524 | -0.14191 | -0.16937 | 0.07782 | -0.041198 | 0.032043 | 0.1236 | 0.19226 | 0.23346 | -0.3479 | 0.050354 | 0.022888 | -0.086975 | 0.1236 | -0.041198 | -0.064086 | -0.018311 | 121.4951 | 121.1151 | 2.536 | -121.5042 | 121.376 | 121.4447 | 0.24261 | -121.4401
602.625 | 121.4172 | -0.14191 | 121.2479 | -0.00099167 | 0.0086006 | 0.070993 | 0.0070474 | 0.063429 | -0.0050458 | -0.0025164 | 0.0069425 | -0.0015082 | 0.065525 | 0.063591 | -0.011335 | -0.0065967 | 120.9732 | 0.086975 | 2.4765 | 0.082397 | 121.2479 | -0.073242 | -0.19226 | 0.004578 | 0.21973 | -0.07782 | 121.1288 | 121.2112 | -0.10986 | -0.14191 | 0.068665 | -0.050354 | 0 | 0.22888 | 0.2243 | 0.27466 | -0.27466 | 0.032044 | 0 | -0.11902 | 0.14649 | 0.064087 | 0.064087 | -0.036621 | 121.3898 | 121.1151 | 2.6184 | -121.4401 | 121.2708 | 121.3531 | 0.36163 | -121.3898
604.3125 | 121.3577 | -0.17395 | 121.2662 | 0.014267 | 0.012659 | 0.071421 | 0.002134 | 0.062574 | 0.00072196 | -0.0029436 | 0.0069425 | 0.001269 | 0.061252 | 0.063164 | -0.0068487 | -0.0053149 | 120.9915 | 0.041199 | 2.4536 | 0.082397 | 121.2753 | -0.082397 | -0.1831 | 0.027466 | 0.16022 | -0.10071 | 121.1517 | 121.2204 | -0.09613 | -0.1236 | 0.091553 | -0.009155 | 0.009156 | 0.21515 | 0.25635 | 0.2655 | -0.27466 | 0.07782 | 0.050354 | -0.11444 | 0.20142 | 0.073242 | 0.022888 | -0.045776 | 121.4493 | 121.1655 | 2.6276 | -121.4493 | 121.3257 | 121.3943 | 0.33417 | -121.3898
606.0469 | 121.344 | -0.19684 | 121.2708 | 0.0066373 | 0.0047552 | 0.070139 | 0.00021145 | 0.06172 | 0.003072 | -0.00016664 | -0.00068649 | 0.0038324 | 0.061893 | 0.065728 | -0.0055671 | -0.0070239 | 120.9732 | -0.022888 | 2.4399 | 0.022888 | 121.3074 | -0.10529 | -0.21973 | -0.050354 | 0.10071 | -0.19684 | 121.2067 | 121.2524 | -0.12817 | -0.17395 | 0.091552 | -0.022889 | 0.036621 | 0.17395 | 0.21973 | 0.24261 | -0.29755 | 0.068664 | 0.022888 | -0.064087 | 0.14648 | 0 | -0.022888 | -0.018311 | 121.5042 | 121.17 | 2.6367 | -121.4905 | 121.4035 | 121.4493 | 0.29755 | -121.4447
607.7344 | 121.4127 | -0.15564 | 121.2296 | 0.0066373 | 0.004969 | 0.069071 | 0.0044838 | 0.06172 | -0.00013244 | -0.0020892 | 0.0069425 | 0.0021234 | 0.06467 | 0.065728 | -0.0081305 | -0.0059557 | 120.9641 | -0.004578 | 2.4673 | 0.041199 | 121.3211 | -0.1236 | -0.21515 | -0.022888 | 0.13275 | -0.15564 | 121.1838 | 121.2524 | -0.1236 | -0.16022 | 0.032044 | -0.059509 | 0.091553 | 0.15106 | 0.19684 | 0.25635 | -0.2655 | 0.032044 | -0.004577 | -0.045776 | 0.13275 | 0 | 0.004577 | 0.022888 | 121.4767 | 121.1197 | 2.623 | -121.4447 | 121.3394 | 121.4081 | 0.28839 | -121.3898
609.4844 | 121.3806 | -0.18768 | 121.2524 | 0.0066373 | 0.0079596 | 0.068857 | 0.0029886 | 0.062574 | -0.00098684 | -0.0014484 | 0.0069425 | 0.00084176 | 0.063388 | 0.062737 | -0.0074897 | -0.0053149 | 120.9824 | 0.032043 | 2.4719 | 0.068665 | 121.2616 | -0.086975 | -0.17395 | 0.009155 | 0.16022 | -0.09613 | 121.1655 | 121.2112 | -0.091553 | -0.13275 | 0.10071 | 0.013733 | 0.009156 | 0.21973 | 0.25635 | 0.24261 | -0.27008 | 0.09613 | 0.054932 | -0.086975 | 0.19684 | 0.091553 | 0.036621 | -0.041198 | 121.4493 | 121.17 | 2.6596 | -121.4264 | 121.3531 | 121.3989 | 0.3479 | -121.3852
611.1719 | 121.4767 | -0.15564 | 121.2479 | -0.00099167 | 0.0066778 | 0.06843 | 0.0040566 | 0.060652 | 0.00050836 | -0.0023028 | 0.014572 | 0.0027644 | 0.064884 | 0.065514 | -0.0089849 | -0.0059557 | 120.9549 | -0.036621 | 2.4811 | 0.032043 | 121.3257 | -0.10986 | -0.22888 | -0.050354 | 0.15106 | -0.16479 | 121.2067 | 121.2845 | -0.11444 | -0.17853 | 0.045777 | -0.073242 | 0.07782 | 0.11902 | 0.18768 | 0.26093 | -0.29297 | 0.041199 | -0.022888 | -0.041199 | 0.10529 | -0.009155 | 0.013733 | 0.036621 | 121.4813 | 121.1105 | 2.6367 | -121.4767 | 121.3623 | 121.4401 | 0.3067 | -121.4264
612.9219 | 121.4081 | -0.16022 | 121.2433 | 0.0066373 | 0.0073188 | 0.070353 | 0.0083292 | 0.063643 | -0.0035504 | -0.0046526 | 0.0069425 | -1.2844e-05 | 0.064884 | 0.064446 | -0.011121 | -0.0065967 | 120.9457 | 0.027466 | 2.5223 | 0.059509 | 121.2753 | -0.09613 | -0.20599 | -0.07782 | 0.16479 | -0.14191 | 121.2112 | 121.2433 | -0.12817 | -0.16022 | 0.064087 | -0.045777 | 0.032044 | 0.18768 | 0.21973 | 0.2655 | -0.29755 | 0.032043 | 0 | -0.032043 | 0.082397 | 0.01831 | 0.01831 | 0 | 121.4355 | 121.106 | 2.6825 | -121.4493 | 121.3715 | 121.4035 | 0.32501 | -121.4035
614.6562 | 121.4172 | -0.15106 | 121.2753 | 0.0066373 | 0.0064642 | 0.070353 | 0.005552 | 0.063643 | 0.0020038 | -0.004439 | 0.0069425 | 0.00084176 | 0.064243 | 0.066368 | -0.0083441 | -0.0065967 | 120.9686 | 0.004578 | 2.5085 | 0.045776 | 121.3211 | -0.10986 | -0.22888 | -0.032043 | 0.13275 | -0.15106 | 121.2067 | 121.2296 | -0.12817 | -0.15106 | 0.041199 | -0.07782 | 0.045776 | 0.15564 | 0.19684 | 0.27466 | -0.3067 | 0.022888 | 0 | -0.068665 | 0.11902 | 0 | 0 | -0.045777 | 121.4722 | 121.1197 | 2.6596 | -121.5042 | 121.3577 | 121.3806 | 0.28381 | -121.4264
616.3281 | 121.3257 | -0.17853 | 121.312 | 0.0066373 | 0.014368 | 0.071421 | 0.002775 | 0.064924 | -0.0026958 | -0.0025164 | -0.00068649 | -0.0017218 | 0.062107 | 0.065087 | -0.0089849 | -0.0048877 | 120.9869 | 0.082397 | 2.5452 | 0.068665 | 121.2753 | -0.059509 | -0.17853 | 0.018311 | 0.16022 | -0.073242 | 121.1563 | 121.2296 | -0.091553 | -0.13275 | 0.11902 | 0 | -0.036621 | 0.26092 | 0.24719 | 0.24719 | -0.32501 | 0.086975 | 0.045777 | -0.15564 | 0.19684 | 0.10529 | 0.059509 | -0.082398 | 121.4539 | 121.1655 | 2.7237 | -121.4905 | 121.3348 | 121.4081 | 0.33874 | -121.4447
618.0625 | 121.344 | -0.17853 | 121.2616 | -0.00099167 | 0.013514 | 0.073557 | 0.0066202 | 0.062788 | -0.0048322 | -0.0048662 | -0.00068649 | -0.0012946 | 0.061039 | 0.063591 | -0.0091985 | -0.0044605 | 120.9503 | 0.027466 | 2.5223 | 0.045776 | 121.2753 | -0.07782 | -0.18768 | -0.036621 | 0.1236 | -0.11902 | 121.1884 | 121.2296 | -0.082397 | -0.13275 | 0.10071 | -0.009155 | 0.013733 | 0.20599 | 0.2243 | 0.23346 | -0.31128 | 0.096131 | 0.045777 | -0.073243 | 0.14191 | 0.059509 | 0.013732 | -0.032044 | 121.4539 | 121.1288 | 2.7008 | -121.4493 | 121.3669 | 121.4081 | 0.30212 | -121.3943
619.75 | 121.4676 | -0.15106 | 121.2524 | 0.0066373 | 0.0058234 | 0.069284 | 0.0066202 | 0.065351 | 0.0017902 | -0.0025164 | 0.0069425 | 0.002337 | 0.062107 | 0.065087 | -0.0077033 | -0.0085193 | 120.9686 | -0.032043 | 2.5452 | 0.036621 | 121.3303 | -0.10986 | -0.21515 | -0.041199 | 0.14648 | -0.16479 | 121.2341 | 121.2524 | -0.13733 | -0.16022 | 0.041199 | -0.064087 | 0.07782 | 0.11902 | 0.18768 | 0.25177 | -0.28381 | 0.013733 | -0.009155 | -0.01831 | 0.10986 | -0.013733 | -0.004578 | 0 | 121.4813 | 121.1197 | 2.6962 | -121.4676 | 121.3852 | 121.4035 | 0.29755 | -121.4127
621.4844 | 121.4172 | -0.16479 | 121.2891 | -0.00099167 | 0.004969 | 0.070139 | 0.0066202 | 0.061079 | -0.0026958 | -0.00508 | 0.0069425 | 0.0019098 | 0.066166 | 0.064659 | -0.0096259 | -0.0048877 | 120.9183 | -0.032043 | 2.5223 | 0.018311 | 121.2891 | -0.12817 | -0.21057 | -0.09613 | 0.10071 | -0.18768 | 121.2296 | 121.2845 | -0.14191 | -0.17395 | 0.036621 | -0.045776 | 0 | 0.13275 | 0.18311 | 0.22888 | -0.37079 | 0.022888 | -0.009155 | -0.059509 | 0.068665 | -0.022888 | -0.013733 | -0.004577 | 121.4539 | 121.0831 | 2.6871 | -121.4996 | 121.3943 | 121.4493 | 0.2655 | -121.463
623.2188 | 121.4447 | -0.16479 | 121.2799 | 0.014267 | 0.0036872 | 0.069925 | 0.0074746 | 0.064497 | -0.0012006 | -0.0057208 | -0.00068649 | 0.0021234 | 0.063388 | 0.06295 | -0.01048 | -0.0076647 | 120.9091 | -0.064087 | 2.5177 | -0.013733 | 121.344 | -0.13733 | -0.21515 | -0.11902 | 0.091553 | -0.21057 | 121.2433 | 121.257 | -0.13275 | -0.16022 | 0.027466 | -0.050354 | 0.064087 | 0.10071 | 0.15106 | 0.20142 | -0.37079 | 0.032044 | 0.004578 | -0.036621 | 0.045776 | -0.045776 | -0.050354 | -0.022888 | 121.5088 | 121.0739 | 2.6825 | -121.4951 | 121.4081 | 121.4218 | 0.25635 | -121.4401
624.9688 | 121.3577 | -0.19226 | 121.3028 | -0.00099167 | 0.0071052 | 0.069925 | 0.0014932 | 0.063002 | 0.0039264 | -0.0014484 | 0.0069425 | 0.002337 | 0.06232 | 0.066368 | -0.0059943 | -0.0065967 | 120.9091 | -0.10529 | 2.5085 | 0.004578 | 121.312 | -0.10071 | -0.21973 | -0.10071 | 0.027466 | -0.21515 | 121.2296 | 121.2799 | -0.13275 | -0.16022 | 0.091553 | -0.027466 | 0.009156 | 0.086975 | 0.19684 | 0.22431 | -0.39368 | 0.05951 | 0.032044 | -0.073242 | 0.091553 | -0.022888 | -0.054932 | -0.022888 | 121.5042 | 121.1014 | 2.7008 | -121.5225 | 121.4218 | 121.4722 | 0.21973 | -121.463
626.6562 | 121.3348 | -0.17853 | 121.3074 | 0.0066373 | 0.0090278 | 0.071207 | 0.0025612 | 0.062788 | -0.0035504 | -0.0025164 | 0.014572 | -0.00086724 | 0.061252 | 0.063805 | -0.010053 | -0.0055285 | 121.019 | 0.068665 | 2.6367 | 0.082397 | 121.2616 | -0.07782 | -0.17853 | 0.009155 | 0.17853 | -0.068665 | 121.1929 | 121.2341 | -0.082397 | -0.12817 | 0.10071 | 0 | -0.045776 | 0.24719 | 0.26092 | 0.26092 | -0.28839 | 0.096131 | 0.050354 | -0.11444 | 0.18768 | 0.10986 | 0.059509 | -0.073242 | 121.4401 | 121.1975 | 2.8152 | -121.4859 | 121.3715 | 121.4127 | 0.35706 | -121.4355
628.3906 | 121.4996 | -0.13733 | 121.2708 | -0.0086212 | 0.0058234 | 0.068216 | 0.0070474 | 0.061506 | 0.0011494 | -0.00508 | 0.0069425 | 0.0014826 | 0.066166 | 0.064659 | -0.0085577 | -0.0076647 | 120.9183 | -0.073242 | 2.5681 | 0.018311 | 121.3303 | -0.11444 | -0.21973 | -0.050354 | 0.11444 | -0.18768 | 121.2433 | 121.2753 | -0.13733 | -0.16937 | 0.022888 | -0.082398 | 0.059509 | 0.064087 | 0.15564 | 0.23804 | -0.35248 | 0 | -0.032044 | -0.027466 | 0.086975 | -0.050354 | -0.01831 | 0.004578 | 121.4676 | 121.0556 | 2.7054 | -121.4905 | 121.3806 | 121.4127 | 0.25177 | -121.4401
630.1406 | 121.3943 | -0.17395 | 121.3165 | 0.0066373 | 0.0090278 | 0.068216 | 0.0044838 | 0.062361 | 0.00050836 | -0.0037982 | -0.015945 | 0.00084176 | 0.063602 | 0.064446 | -0.0081305 | -0.0070239 | 120.9457 | -0.073242 | 2.5818 | 0.027466 | 121.3165 | -0.091553 | -0.19226 | -0.041199 | 0.09613 | -0.13733 | 121.1929 | 121.2845 | -0.09613 | -0.13733 | 0.082397 | -0.018311 | 0 | 0.10071 | 0.20142 | 0.21973 | -0.37079 | 0.07782 | 0.036621 | -0.1236 | 0.13275 | 0.036621 | 0 | -0.032043 | 121.4905 | 121.1197 | 2.7557 | -121.5088 | 121.3669 | 121.4584 | 0.27008 | -121.4539
631.8125 | 121.344 | -0.18768 | 121.2982 | -0.00099167 | 0.010523 | 0.07313 | 0.0029886 | 0.061079 | -0.0035504 | -0.0037982 | 0.014572 | 0.00020076 | 0.06232 | 0.061241 | -0.0068487 | -0.0053149 | 121.0052 | 0.07782 | 2.6779 | 0.086975 | 121.2845 | -0.059509 | -0.16022 | 0.009155 | 0.16479 | -0.07782 | 121.17 | 121.2662 | -0.082397 | -0.14191 | 0.12817 | 0.027466 | -0.013733 | 0.2655 | 0.27466 | 0.24719 | -0.29297 | 0.10529 | 0.045776 | -0.12817 | 0.19684 | 0.10986 | 0.064087 | -0.032044 | 121.4722 | 121.1929 | 2.8656 | -121.4584 | 121.3577 | 121.4539 | 0.35248 | -121.4401
633.5469 | 121.4584 | -0.15106 | 121.2662 | 0.014267 | 0.0088142 | 0.075052 | 0.0070474 | 0.062574 | -0.0018414 | -0.0048662 | 0.0069425 | 0.0010554 | 0.062534 | 0.061241 | -0.0087713 | -0.0072375 | 120.9137 | -0.059509 | 2.6093 | -0.018311 | 121.3394 | -0.11444 | -0.22888 | -0.1236 | 0.091553 | -0.20599 | 121.257 | 121.2891 | -0.15106 | -0.16479 | 0.036621 | -0.07782 | 0.073243 | 0.091553 | 0.13275 | 0.21057 | -0.35248 | 0 | -0.013733 | -0.009155 | 0.027466 | -0.054932 | -0.041199 | 0.022888 | 121.4905 | 121.0648 | 2.7603 | -121.4951 | 121.4081 | 121.4401 | 0.24261 | -121.431
635.2188 | 121.4813 | -0.14648 | 121.2387 | -0.00099167 | 0.0056098 | 0.069284 | 0.0074746 | 0.062147 | 0.0049946 | -0.0029436 | 0.0069425 | 0.002978 | 0.065525 | 0.063164 | -0.0094123 | -0.0063831 | 120.9641 | -0.041199 | 2.6596 | 0.041199 | 121.3486 | -0.10529 | -0.22888 | -0.022888 | 0.13275 | -0.16937 | 121.2387 | 121.2799 | -0.11444 | -0.15564 | 0.041198 | -0.082398 | 0.10986 | 0.10529 | 0.18768 | 0.27008 | -0.27466 | 0.032043 | -0.009156 | 0 | 0.1236 | -0.022889 | -0.013733 | 0.041199 | 121.4951 | 121.1105 | 2.8061 | -121.4676 | 121.3852 | 121.4264 | 0.27924 | -121.3943
636.9531 | 121.4584 | -0.13275 | 121.2799 | 0.0066373 | 0.0096686 | 0.072916 | 0.0076882 | 0.062788 | -0.0039776 | -0.0042254 | -0.00068649 | -0.002149 | 0.064457 | 0.063164 | -0.012189 | -0.0063831 | 121.0373 | 0.086975 | 2.7374 | 0.091553 | 121.2753 | -0.068665 | -0.17395 | 0.013733 | 0.24261 | -0.041199 | 121.1746 | 121.2479 | -0.086975 | -0.1236 | 0.064086 | -0.041199 | -0.004577 | 0.21973 | 0.2243 | 0.2655 | -0.24262 | 0.045776 | 0.009155 | -0.10528 | 0.14648 | 0.091552 | 0.082397 | -0.032043 | 121.4081 | 121.17 | 2.8702 | -121.4539 | 121.3074 | 121.3806 | 0.37537 | -121.4035
638.6406 | 121.3348 | -0.1831 | 121.3394 | 0.0066373 | 0.011378 | 0.071848 | 0.005552 | 0.061934 | -0.0041912 | -0.0042254 | -0.00068649 | -0.00065364 | 0.062748 | 0.063378 | -0.0089849 | -0.0072375 | 121.0007 | 0.041199 | 2.7145 | 0.068665 | 121.3028 | -0.059509 | -0.16937 | 0 | 0.13733 | -0.091553 | 121.1838 | 121.2479 | -0.09613 | -0.13733 | 0.1236 | 0.013732 | -0.036622 | 0.2243 | 0.25177 | 0.23804 | -0.33875 | 0.086975 | 0.045776 | -0.15564 | 0.1831 | 0.091552 | 0.045776 | -0.091553 | 121.4859 | 121.1838 | 2.8976 | -121.5088 | 121.3669 | 121.431 | 0.32043 | -121.4767
640.375 | 121.3531 | -0.1831 | 121.3165 | 0.021896 | 0.0073188 | 0.068003 | 0.00042505 | 0.061079 | 0.0067036 | -0.0023028 | 0.0069425 | 0.0038324 | 0.063175 | 0.065728 | -0.0072759 | -0.0074511 | 120.9366 | -0.10529 | 2.6184 | 0 | 121.3669 | -0.10071 | -0.20142 | -0.073242 | 0.022888 | -0.23346 | 121.2433 | 121.2936 | -0.1236 | -0.16022 | 0.082397 | -0.018311 | 0.050354 | 0.077819 | 0.1831 | 0.20142 | -0.37994 | 0.059509 | 0.022888 | -0.073242 | 0.10986 | -0.050354 | -0.073242 | -0.022888 | 121.55 | 121.1197 | 2.8015 | -121.5179 | 121.4264 | 121.4767 | 0.20599 | -121.4767
642.1094 | 121.4539 | -0.15564 | 121.2845 | 0.014267 | 0.0066778 | 0.072489 | 0.003843 | 0.060438 | -0.0033368 | -0.003371 | 0.014572 | -0.0017218 | 0.063388 | 0.064232 | -0.010908 | -0.0042467 | 121.0144 | 0.091553 | 2.7557 | 0.10071 | 121.2891 | -0.059509 | -0.18768 | 0.009155 | 0.23346 | -0.07782 | 121.2158 | 121.257 | -0.082397 | -0.12817 | 0.096131 | -0.032043 | 0.004577 | 0.24719 | 0.25635 | 0.28839 | -0.27008 | 0.073243 | 0.027466 | -0.068665 | 0.16479 | 0.07782 | 0.050354 | -0.027466 | 121.4447 | 121.17 | 2.9114 | -121.4722 | 121.3715 | 121.4127 | 0.3891 | -121.4127
643.8594 | 121.3669 | -0.17853 | 121.3486 | 0.0066373 | 0.0083868 | 0.070353 | 0.0017068 | 0.061506 | 0.0011494 | -0.0029436 | 0.022202 | 0.002337 | 0.062961 | 0.063378 | -0.0055671 | -0.0046741 | 120.9366 | -0.11444 | 2.6505 | -0.018311 | 121.3623 | -0.10986 | -0.21515 | -0.086975 | 0.013733 | -0.22888 | 121.2616 | 121.3165 | -0.13275 | -0.16022 | 0.068665 | -0.036621 | 0.013733 | 0.064087 | 0.16022 | 0.19684 | -0.41199 | 0.045777 | 0.018311 | -0.086975 | 0.091553 | -0.050354 | -0.068665 | -0.032044 | 121.5408 | 121.1151 | 2.829 | -121.5637 | 121.4401 | 121.4951 | 0.19226 | -121.5088
645.5938 | 121.4401 | -0.14648 | 121.3028 | -0.00099167 | 0.0045416 | 0.071634 | 0.0083292 | 0.064283 | -0.00034604 | -0.003371 | 0.0069425 | 0.0010554 | 0.065952 | 0.063164 | -0.010267 | -0.0048877 | 120.9595 | -0.018311 | 2.71 | 0.041199 | 121.3211 | -0.10986 | -0.21515 | -0.09613 | 0.10986 | -0.16479 | 121.2708 | 121.2982 | -0.10071 | -0.17395 | 0.036621 | -0.068665 | 0.018311 | 0.12817 | 0.18768 | 0.25635 | -0.34332 | 0.045776 | -0.027466 | -0.032043 | 0.050354 | -0.018311 | 0.009155 | -0.004577 | 121.4676 | 121.106 | 2.8564 | -121.5179 | 121.4172 | 121.4447 | 0.25635 | -121.4767
647.2812 | 121.4447 | -0.13275 | 121.2891 | 0.0066373 | 0.0073188 | 0.071848 | 0.0074746 | 0.064711 | -0.0024822 | -0.0059344 | -0.00068649 | -0.00044004 | 0.063816 | 0.063164 | -0.0096259 | -0.0057421 | 121.0052 | 0.054932 | 2.774 | 0.068665 | 121.3303 | -0.086975 | -0.19226 | -0.054932 | 0.15106 | -0.12817 | 121.2433 | 121.2708 | -0.11902 | -0.15564 | 0.045776 | -0.05951 | 0.041199 | 0.18768 | 0.20142 | 0.26093 | -0.28381 | 0.013732 | -0.022889 | -0.045776 | 0.077819 | 0.004577 | 0.027466 | -0.01831 | 121.463 | 121.138 | 2.9068 | -121.4813 | 121.376 | 121.4035 | 0.28381 | -121.4447
649.0312 | 121.5042 | -0.13275 | 121.2891 | -0.00099167 | 0.0086006 | 0.072916 | 0.0098244 | 0.063215 | -0.0041912 | -0.0046526 | 0.014572 | -0.0012946 | 0.062961 | 0.0653 | -0.011762 | -0.0063831 | 121.0281 | 0.09613 | 2.8015 | 0.091553 | 121.3303 | -0.064087 | -0.18768 | 0.045776 | 0.22888 | -0.022888 | 121.1929 | 121.2204 | -0.086975 | -0.12817 | 0.068664 | -0.054932 | 0.041199 | 0.22888 | 0.2243 | 0.27924 | -0.26093 | 0.045776 | 0.004577 | -0.09613 | 0.17853 | 0.10986 | 0.10529 | -0.068664 | 121.463 | 121.1609 | 2.9343 | -121.4767 | 121.3257 | 121.3531 | 0.36163 | -121.4172
650.7031 | 121.5179 | -0.12817 | 121.2936 | 0.014267 | 0.0068916 | 0.069071 | 0.0051248 | 0.063856 | 0.002431 | -0.00273 | -0.008316 | 0.0034052 | 0.065097 | 0.063164 | -0.0077033 | -0.0068103 | 120.9503 | -0.073242 | 2.7145 | 0.027466 | 121.376 | -0.10986 | -0.2243 | -0.073242 | 0.091553 | -0.19226 | 121.2753 | 121.3074 | -0.13275 | -0.16937 | 0.018311 | -0.09613 | 0.082398 | 0.054932 | 0.15564 | 0.25177 | -0.34332 | -0.004577 | -0.041199 | -0.01831 | 0.054932 | -0.064087 | -0.022888 | 0.013733 | 121.5042 | 121.0785 | 2.8427 | -121.5179 | 121.4035 | 121.4355 | 0.21973 | -121.463
652.4375 | 121.3806 | -0.16022 | 121.3394 | 0.0066373 | 0.010309 | 0.072062 | 0.0017068 | 0.062361 | 0.0011494 | -0.001662 | 0.0069425 | -1.2844e-05 | 0.062748 | 0.066796 | -0.0094123 | -0.0076647 | 121.0556 | 0.059509 | 2.829 | 0.091553 | 121.3074 | -0.073242 | -0.16479 | 0.045776 | 0.16022 | -0.068665 | 121.2021 | 121.2616 | -0.091553 | -0.1236 | 0.086975 | -0.004578 | -0.032044 | 0.21973 | 0.25177 | 0.25635 | -0.28381 | 0.068664 | 0.036621 | -0.13733 | 0.20599 | 0.091552 | 0.054931 | -0.07782 | 121.4676 | 121.2158 | 2.9892 | -121.5042 | 121.3623 | 121.4218 | 0.32043 | -121.463
654.1875 | 121.4951 | -0.15564 | 121.2845 | -0.00099167 | 0.0090278 | 0.070993 | 0.0064066 | 0.06407 | -0.0026958 | -0.0048662 | 0.0069425 | 0.001269 | 0.063602 | 0.064232 | -0.0070623 | -0.0053149 | 120.9366 | -0.059509 | 2.742 | -0.009155 | 121.344 | -0.10529 | -0.2243 | -0.10071 | 0.082397 | -0.19684 | 121.257 | 121.312 | -0.1236 | -0.16022 | 0.050354 | -0.068664 | 0.059509 | 0.096131 | 0.14649 | 0.21515 | -0.3479 | 0.032044 | -0.004577 | -0.027466 | 0.054932 | -0.041198 | -0.036621 | 0.027466 | 121.4996 | 121.0922 | 2.8976 | -121.5088 | 121.4127 | 121.4676 | 0.23804 | -121.4447
655.8594 | 121.4355 | -0.16479 | 121.312 | 0.014267 | 0.0088142 | 0.064798 | 0.0049112 | 0.060225 | 0.0017902 | -0.0025164 | -0.00068649 | 0.0021234 | 0.065311 | 0.066155 | -0.0068487 | -0.0068103 | 121.0236 | 0 | 2.829 | 0.041199 | 121.3715 | -0.09613 | -0.20142 | -0.027466 | 0.13733 | -0.15564 | 121.2433 | 121.3303 | -0.12817 | -0.15106 | 0.068665 | -0.036621 | 0.059509 | 0.16479 | 0.20599 | 0.24262 | -0.28839 | 0.036621 | 0.013733 | -0.068665 | 0.13733 | 0.009155 | -0.004578 | 0.01831 | 121.5363 | 121.1884 | 2.9938 | -121.5134 | 121.4081 | 121.4951 | 0.30212 | -121.463
657.5938 | 121.431 | -0.16022 | 121.3165 | -0.016251 | 0.01095 | 0.069712 | 0.0049112 | 0.063429 | -0.0056866 | -0.00273 | 0.0069425 | -0.0042852 | 0.062534 | 0.063378 | -0.011335 | -0.0046741 | 120.9549 | 0.004578 | 2.7786 | 0.050354 | 121.3394 | -0.086975 | -0.20142 | -0.041199 | 0.13733 | -0.091553 | 121.2341 | 121.2845 | -0.086975 | -0.12817 | 0.073242 | -0.041199 | 0.022889 | 0.16479 | 0.21057 | 0.25177 | -0.36163 | 0.073242 | 0.032043 | -0.082397 | 0.11902 | 0.068664 | 0.036621 | -0.032043 | 121.4996 | 121.1151 | 2.9388 | -121.5179 | 121.3943 | 121.4447 | 0.29755 | -121.4447
659.2812 | 121.3623 | -0.17853 | 121.344 | 0.0066373 | 0.010096 | 0.07078 | 0.0017068 | 0.061079 | -0.0039776 | -0.004439 | -0.00068649 | -0.00044004 | 0.061679 | 0.062737 | -0.0070623 | -0.0076647 | 121.0464 | 0.059509 | 2.8473 | 0.086975 | 121.3028 | -0.073242 | -0.16022 | 0.022888 | 0.18768 | -0.07782 | 121.2112 | 121.2662 | -0.091553 | -0.12817 | 0.10529 | 0.018311 | -0.041199 | 0.23804 | 0.2655 | 0.24719 | -0.29755 | 0.086975 | 0.050354 | -0.13275 | 0.20142 | 0.10071 | 0.050354 | -0.07782 | 121.4813 | 121.225 | 3.0258 | -121.5042 | 121.3898 | 121.4447 | 0.36621 | -121.4722
661.0156 | 121.5271 | -0.13275 | 121.2891 | 0.0066373 | 0.0045416 | 0.068644 | 0.005552 | 0.062788 | 0.0022174 | -0.0018756 | 0.0069425 | 0.0031916 | 0.064884 | 0.065728 | -0.0066351 | -0.0072375 | 120.9686 | -0.045776 | 2.8244 | 0.045776 | 121.3943 | -0.10529 | -0.21057 | -0.032043 | 0.13275 | -0.17395 | 121.2753 | 121.2845 | -0.12817 | -0.16479 | 0.027465 | -0.07782 | 0.10529 | 0.086975 | 0.17853 | 0.25635 | -0.32043 | 0.004577 | -0.032044 | -0.013732 | 0.10071 | -0.041199 | -0.009155 | -0.004577 | 121.5271 | 121.1014 | 2.9572 | -121.4996 | 121.4081 | 121.4172 | 0.2655 | -121.4539
662.75 | 121.4493 | -0.14648 | 121.2891 | 0.0066373 | 0.009455 | 0.074411 | 0.0034158 | 0.063429 | -0.0052594 | -0.0046526 | 0.0069425 | -0.0036444 | 0.061893 | 0.061669 | -0.011335 | -0.0038195 | 120.9732 | 0.009155 | 2.8061 | 0.045776 | 121.3531 | -0.10529 | -0.18768 | -0.032043 | 0.15106 | -0.086975 | 121.2112 | 121.2982 | -0.091553 | -0.11444 | 0.041198 | -0.041199 | 0.064087 | 0.15564 | 0.19226 | 0.23346 | -0.31586 | 0.054931 | 0.032043 | -0.077819 | 0.11444 | 0.059509 | 0.027466 | 0.009156 | 121.4996 | 121.1197 | 2.9526 | -121.4767 | 121.3577 | 121.4447 | 0.29755 | -121.4035
664.4844 | 121.4996 | -0.14191 | 121.2936 | -0.00099167 | 0.0045416 | 0.069925 | 0.0051248 | 0.066847 | 0.0017902 | -0.0059344 | 0.014572 | 0.0031916 | 0.06467 | 0.064232 | -0.0098395 | -0.0080921 | 120.9503 | -0.07782 | 2.7924 | -0.013733 | 121.3531 | -0.13275 | -0.22888 | -0.086975 | 0.086975 | -0.19684 | 121.2891 | 121.3211 | -0.11444 | -0.17395 | 0.009156 | -0.086975 | 0.059509 | 0.064087 | 0.12817 | 0.21515 | -0.34332 | 0.027466 | -0.032043 | -0.004578 | 0.054932 | -0.054931 | -0.022888 | 0.027466 | 121.4951 | 121.0922 | 2.9343 | -121.5225 | 121.431 | 121.463 | 0.22888 | -121.4676
666.1719 | 121.4127 | -0.18768 | 121.3623 | 0.0066373 | 0.0064642 | 0.070139 | 0.002775 | 0.062574 | 0.00414 | -0.00273 | 0.014572 | 0.002978 | 0.064457 | 0.065941 | -0.0074897 | -0.0063831 | 120.9549 | -0.091553 | 2.774 | -0.004578 | 121.3715 | -0.10071 | -0.22888 | -0.082397 | 0.027466 | -0.21057 | 121.2708 | 121.2982 | -0.11902 | -0.15564 | 0.086975 | -0.041199 | 0.009155 | 0.09613 | 0.1831 | 0.2243 | -0.40741 | 0.068664 | 0.032043 | -0.091553 | 0.10529 | -0.022888 | -0.054931 | -0.064087 | 121.5591 | 121.1426 | 2.9617 | -121.5912 | 121.4584 | 121.4859 | 0.21515 | -121.5179
667.9062 | 121.4584 | -0.14191 | 121.3211 | 0.0066373 | 0.0071052 | 0.072275 | 0.0059792 | 0.061934 | -0.0024822 | -0.003371 | -0.00068649 | -0.00044004 | 0.06467 | 0.063591 | -0.0085577 | -0.0068103 | 120.9595 | -0.027466 | 2.8336 | -0.004578 | 121.3623 | -0.09613 | -0.21515 | -0.091553 | 0.10529 | -0.1831 | 121.2708 | 121.3211 | -0.10071 | -0.17395 | 0.045777 | -0.073242 | 0.041199 | 0.11444 | 0.13733 | 0.21057 | -0.36163 | 0.041199 | -0.032043 | -0.050354 | 0.050354 | -0.041198 | -0.009155 | 0 | 121.5042 | 121.1014 | 2.9755 | -121.5363 | 121.4127 | 121.463 | 0.24719 | -121.4951
669.6406 | 121.4859 | -0.13733 | 121.3211 | 0.0066373 | 0.0028326 | 0.067575 | 0.0053384 | 0.063002 | 0.001363 | -0.00080744 | -0.00068649 | 0.0016962 | 0.065097 | 0.064446 | -0.0055671 | -0.0080921 | 121.0052 | 0.009155 | 2.9022 | 0.041199 | 121.3806 | -0.10071 | -0.19684 | -0.018311 | 0.14191 | -0.15106 | 121.2662 | 121.2891 | -0.10529 | -0.16022 | 0.036621 | -0.059509 | 0.059509 | 0.14648 | 0.17853 | 0.23804 | -0.31586 | 0.032043 | -0.022888 | -0.054932 | 0.11902 | -0.013733 | 0.009155 | -0.032044 | 121.5179 | 121.1426 | 3.0396 | -121.5179 | 121.4035 | 121.4264 | 0.27924 | -121.4813
671.3125 | 121.4127 | -0.17853 | 121.3303 | 0.014267 | 0.009455 | 0.071207 | 0.0070474 | 0.063215 | 0.001363 | -0.0023028 | 0.0069425 | 0.00020076 | 0.06232 | 0.064659 | -0.0070623 | -0.0053149 | 120.9457 | -0.045776 | 2.8427 | 0.009155 | 121.3669 | -0.10529 | -0.21057 | -0.032043 | 0.07782 | -0.16022 | 121.257 | 121.2799 | -0.10071 | -0.14648 | 0.073242 | -0.032043 | 0.036621 | 0.13275 | 0.18768 | 0.21973 | -0.38452 | 0.07782 | 0.032044 | -0.073242 | 0.14648 | 0.018311 | -0.013733 | -0.050354 | 121.5454 | 121.1243 | 3.0212 | -121.5408 | 121.4355 | 121.4584 | 0.25635 | -121.4767
673.0469 | 121.5179 | -0.13275 | 121.2982 | 0.0066373 | 0.0079596 | 0.07078 | 0.0096108 | 0.063643 | -0.00055964 | -0.00273 | -0.00068649 | 0.00041436 | 0.065097 | 0.0653 | -0.0083441 | -0.0055285 | 120.9274 | -0.059509 | 2.8427 | 0.004578 | 121.376 | -0.11444 | -0.2243 | -0.10071 | 0.10071 | -0.19684 | 121.2753 | 121.3211 | -0.1236 | -0.17395 | 0.01831 | -0.091553 | 0.07782 | 0.073242 | 0.13733 | 0.22888 | -0.37079 | 0.009155 | -0.041199 | -0.022888 | 0.032043 | -0.064087 | -0.022888 | 0.022888 | 121.5088 | 121.0602 | 2.9755 | -121.5225 | 121.4081 | 121.4539 | 0.23346 | -121.4722
674.7969 | 121.3806 | -0.18768 | 121.3348 | 0.0066373 | 0.013087 | 0.07313 | 0.0046976 | 0.064924 | -0.00077324 | -0.0042254 | 0.014572 | 0.00020076 | 0.06232 | 0.064019 | -0.0096259 | -0.0063831 | 121.0464 | 0.07782 | 2.9663 | 0.086975 | 121.312 | -0.07782 | -0.17395 | 0.018311 | 0.17853 | -0.054932 | 121.225 | 121.2708 | -0.082397 | -0.14648 | 0.10986 | 0.013733 | -0.022888 | 0.2655 | 0.27466 | 0.26092 | -0.28839 | 0.10529 | 0.041199 | -0.10986 | 0.20599 | 0.13275 | 0.091552 | -0.064087 | 121.4996 | 121.2341 | 3.154 | -121.5088 | 121.4127 | 121.4584 | 0.36621 | -121.4813
676.5469 | 121.3989 | -0.16937 | 121.3531 | 0.0066373 | 0.0071052 | 0.068216 | 0.0053384 | 0.064497 | 0.00050836 | -0.0025164 | 0.029831 | 0.0021234 | 0.063602 | 0.066582 | -0.0070623 | -0.0080921 | 120.9229 | -0.10529 | 2.8519 | -0.004578 | 121.3943 | -0.1236 | -0.20599 | -0.086975 | 0.027466 | -0.2243 | 121.2982 | 121.3303 | -0.1236 | -0.16022 | 0.045777 | -0.036621 | 0.041199 | 0.064087 | 0.16479 | 0.20142 | -0.4303 | 0.045777 | 0.009156 | -0.054931 | 0.082398 | -0.054931 | -0.064087 | -0.022888 | 121.5637 | 121.0922 | 3.0212 | -121.5591 | 121.4676 | 121.4996 | 0.19684 | -121.5134
678.2188 | 121.5042 | -0.12817 | 121.2982 | 0.014267 | 0.0088142 | 0.073984 | 0.0053384 | 0.060011 | -0.0059002 | -0.0052936 | 0.014572 | -0.0027898 | 0.06467 | 0.064446 | -0.011549 | -0.0033923 | 120.9869 | 0.041199 | 2.9526 | 0.07782 | 121.3303 | -0.073242 | -0.19226 | -0.004578 | 0.20142 | -0.050354 | 121.2158 | 121.2982 | -0.07782 | -0.10986 | 0.054932 | -0.064087 | 0.032043 | 0.16937 | 0.20599 | 0.27008 | -0.31128 | 0.050354 | 0.018311 | -0.082398 | 0.1236 | 0.07782 | 0.059509 | 0 | 121.4584 | 121.1151 | 3.0808 | -121.4905 | 121.344 | 121.4264 | 0.32959 | -121.4081
679.9531 | 121.4996 | -0.14648 | 121.2936 | 0.0066373 | 0.0028326 | 0.06608 | 0.0061928 | 0.062147 | 0.0015766 | -0.0040118 | -0.008316 | 0.00062796 | 0.064457 | 0.064446 | -0.0089849 | -0.0083057 | 121.0052 | -0.032043 | 2.948 | 0.059509 | 121.3715 | -0.09613 | -0.21515 | -0.045776 | 0.13275 | -0.16479 | 121.2524 | 121.3074 | -0.09613 | -0.15106 | 0.050354 | -0.068665 | 0.07782 | 0.11444 | 0.20599 | 0.27466 | -0.28839 | 0.050354 | -0.004578 | -0.041199 | 0.10071 | -0.018311 | -0.013733 | 0.013733 | 121.5179 | 121.1517 | 3.0945 | -121.5088 | 121.3989 | 121.4539 | 0.27924 | -121.4447
681.6875 | 121.4172 | -0.16022 | 121.3348 | 0.0066373 | 0.0053962 | 0.06843 | 0.0023476 | 0.064497 | 0.0026446 | -0.0014484 | -0.00068649 | 0.002978 | 0.066806 | 0.064659 | -0.0059943 | -0.0055285 | 121.0236 | -0.013733 | 2.9617 | 0.045776 | 121.3623 | -0.10529 | -0.21973 | -0.022888 | 0.10986 | -0.17853 | 121.2891 | 121.3348 | -0.10529 | -0.15564 | 0.054931 | -0.05951 | 0.027466 | 0.14648 | 0.20599 | 0.2655 | -0.31128 | 0.054931 | 0.004577 | -0.045777 | 0.13733 | -0.018311 | -0.022888 | 0 | 121.5225 | 121.1838 | 3.1219 | -121.5546 | 121.4493 | 121.4951 | 0.27008 | -121.4905
683.4219 | 121.4767 | -0.14191 | 121.3074 | 0.0066373 | 0.004969 | 0.069925 | 0.0068338 | 0.065351 | -0.0031232 | -0.004439 | -0.00068649 | -0.00086724 | 0.065311 | 0.063378 | -0.010267 | -0.0055285 | 120.9274 | -0.054932 | 2.9251 | 0.009155 | 121.3531 | -0.11902 | -0.21973 | -0.11444 | 0.091553 | -0.1831 | 121.2982 | 121.3303 | -0.12817 | -0.16479 | 0.022888 | -0.07782 | 0.045776 | 0.086975 | 0.15106 | 0.22888 | -0.37994 | 0.013733 | -0.022888 | -0.009155 | 0.027466 | -0.041198 | -0.01831 | 0.022888 | 121.4951 | 121.0693 | 3.067 | -121.5271 | 121.4401 | 121.4722 | 0.23346 | -121.4722
685.1094 | 121.3898 | -0.16937 | 121.376 | 0.0066373 | 0.0081732 | 0.072489 | 0.003843 | 0.062788 | -0.0063274 | -0.0014484 | -0.00068649 | -0.0034308 | 0.064029 | 0.06231 | -0.0098395 | -0.0033923 | 121.0052 | 0.022888 | 2.9709 | 0.045776 | 121.3486 | -0.059509 | -0.17395 | -0.036621 | 0.11444 | -0.10071 | 121.2296 | 121.3074 | -0.09613 | -0.12817 | 0.10986 | -0.004577 | -0.027466 | 0.19226 | 0.21515 | 0.21973 | -0.37079 | 0.073243 | 0.041199 | -0.14648 | 0.13275 | 0.068665 | 0.027466 | -0.068665 | 121.5179 | 121.1746 | 3.1403 | -121.55 | 121.3989 | 121.4767 | 0.28381 | -121.5042
686.8438 | 121.4218 | -0.17853 | 121.3486 | 0.0066373 | 0.0086006 | 0.070353 | 0.002134 | 0.065351 | 0.00414 | -0.0040118 | -0.00068649 | 0.0025508 | 0.063388 | 0.062737 | -0.0051397 | -0.0076647 | 120.9732 | -0.064087 | 2.8976 | -0.004578 | 121.3806 | -0.091553 | -0.21515 | -0.068665 | 0.036621 | -0.17395 | 121.2982 | 121.3257 | -0.13733 | -0.13733 | 0.086975 | -0.036621 | 0.032043 | 0.11444 | 0.17395 | 0.21057 | -0.37537 | 0.041199 | 0.041199 | -0.050354 | 0.10986 | 0.004578 | -0.036621 | -0.022888 | 121.5591 | 121.1517 | 3.0762 | -121.5637 | 121.4767 | 121.5042 | 0.21515 | -121.4859
688.5781 | 121.4172 | -0.15564 | 121.3531 | 0.021896 | 0.0068916 | 0.069712 | 0.0023476 | 0.065138 | 0.00093576 | -0.00016664 | 0.0069425 | 0.0031916 | 0.061679 | 0.065514 | -0.0053533 | -0.0053149 | 120.9549 | -0.07782 | 2.9022 | 0.009155 | 121.3989 | -0.09613 | -0.21057 | -0.086975 | 0.036621 | -0.19226 | 121.3028 | 121.344 | -0.11444 | -0.15564 | 0.05951 | -0.054931 | 0.045777 | 0.07782 | 0.16479 | 0.21973 | -0.39825 | 0.041199 | 0 | -0.050354 | 0.068665 | -0.036621 | -0.036621 | -0.009155 | 121.5546 | 121.1105 | 3.0579 | -121.5637 | 121.4584 | 121.4996 | 0.19226 | -121.5088
690.2656 | 121.3943 | -0.1831 | 121.3623 | 0.0066373 | 0.0075324 | 0.070566 | 0.0046976 | 0.062788 | 0.00050836 | -0.0012346 | 0.014572 | 0.002978 | 0.065097 | 0.06295 | -0.0047125 | -0.0076647 | 121.0098 | -0.009155 | 2.9846 | 0.032043 | 121.3715 | -0.10529 | -0.20599 | -0.059509 | 0.082397 | -0.18768 | 121.3028 | 121.3303 | -0.10986 | -0.16022 | 0.077819 | -0.022889 | 0.009155 | 0.17395 | 0.21515 | 0.23804 | -0.35248 | 0.073242 | 0.022888 | -0.05951 | 0.1236 | -0.004578 | -0.027466 | -0.032044 | 121.5546 | 121.1929 | 3.1677 | -121.5683 | 121.4859 | 121.5134 | 0.2655 | -121.5225
692.0156 | 121.4905 | -0.13275 | 121.3303 | 0.0066373 | 0.011591 | 0.075052 | 0.007261 | 0.060011 | -0.008891 | -0.0055072 | 0.0069425 | -0.0040716 | 0.063602 | 0.064446 | -0.01283 | -0.0053149 | 121.0007 | 0.027466 | 3.0029 | 0.068665 | 121.344 | -0.07782 | -0.17395 | -0.004578 | 0.18768 | -0.059509 | 121.2616 | 121.3303 | -0.091553 | -0.13275 | 0.054931 | -0.041199 | 0.013733 | 0.16022 | 0.20142 | 0.24261 | -0.32959 | 0.041198 | 0 | -0.068664 | 0.12817 | 0.073242 | 0.073242 | 0 | 121.4767 | 121.1334 | 3.1357 | -121.5042 | 121.3943 | 121.463 | 0.32043 | -121.463
693.6875 | 121.4722 | -0.13275 | 121.3211 | -0.00099167 | 0.007746 | 0.072062 | 0.0085428 | 0.062574 | -0.0035504 | -0.0052936 | 0.0069425 | -0.0023626 | 0.064029 | 0.063164 | -0.011335 | -0.0072375 | 121.0556 | 0.07782 | 3.0624 | 0.10529 | 121.3348 | -0.086975 | -0.16937 | 0.027466 | 0.2243 | -0.054932 | 121.2433 | 121.3074 | -0.073242 | -0.11444 | 0.045776 | -0.036622 | 0.013733 | 0.21057 | 0.23804 | 0.27466 | -0.2655 | 0.059509 | 0.01831 | -0.07782 | 0.16022 | 0.077819 | 0.059509 | -0.013733 | 121.4676 | 121.1884 | 3.1952 | -121.4905 | 121.376 | 121.4401 | 0.35706 | -121.4355
695.4219 | 121.3989 | -0.17853 | 121.3486 | 0.0066373 | 0.0096686 | 0.072489 | 0.0064066 | 0.060865 | -0.0041912 | -0.0035846 | -0.008316 | -0.0019354 | 0.061252 | 0.065941 | -0.011549 | -0.0085193 | 121.0098 | -0.004578 | 2.9892 | 0.032043 | 121.3715 | -0.068665 | -0.1831 | -0.032043 | 0.10529 | -0.11902 | 121.2662 | 121.2891 | -0.10529 | -0.12817 | 0.10986 | -0.004577 | 0.022888 | 0.17395 | 0.21057 | 0.21515 | -0.33875 | 0.073242 | 0.050354 | -0.082398 | 0.14648 | 0.059509 | 0.009155 | -0.05951 | 121.55 | 121.1884 | 3.1677 | -121.5317 | 121.4447 | 121.4676 | 0.28381 | -121.4767
697.1719 | 121.3852 | -0.20142 | 121.3531 | -0.0086212 | 0.0053962 | 0.069712 | 0.0019204 | 0.06407 | 0.0026446 | -0.0012346 | 0.0069425 | 0.0053278 | 0.062107 | 0.064232 | -0.0064215 | -0.0091601 | 120.9824 | -0.09613 | 2.98 | 0.004578 | 121.3989 | -0.10986 | -0.20142 | -0.086975 | 0.036621 | -0.2243 | 121.3074 | 121.3577 | -0.12817 | -0.16937 | 0.091553 | 0 | 0.045777 | 0.10529 | 0.20599 | 0.20599 | -0.37079 | 0.073242 | 0.032043 | -0.045776 | 0.11444 | -0.022888 | -0.054931 | 0.004578 | 121.6003 | 121.1838 | 3.1815 | -121.5546 | 121.5088 | 121.5591 | 0.23804 | -121.5225
698.8594 | 121.3806 | -0.17853 | 121.3394 | -0.00099167 | 0.0096686 | 0.075479 | 0.005552 | 0.061506 | -0.0039776 | -0.00273 | -0.00068649 | -0.00086724 | 0.063816 | 0.061882 | -0.0074897 | -0.0048877 | 121.0419 | 0.054932 | 3.0441 | 0.068665 | 121.3486 | -0.073242 | -0.17395 | -0.022888 | 0.12817 | -0.091553 | 121.2616 | 121.3211 | -0.07782 | -0.12817 | 0.10529 | 0.004578 | 0.009155 | 0.23346 | 0.24719 | 0.24261 | -0.29755 | 0.10071 | 0.050354 | -0.07782 | 0.15564 | 0.086975 | 0.036621 | -0.018311 | 121.5271 | 121.2204 | 3.2227 | -121.5134 | 121.4401 | 121.4996 | 0.3067 | -121.4676
700.6094 | 121.5271 | -0.13275 | 121.3394 | 0.0066373 | 0.010523 | 0.072275 | 0.0064066 | 0.062361 | -0.0046184 | -0.0046526 | 0.0069425 | -0.00086724 | 0.061893 | 0.063378 | -0.011762 | -0.0057421 | 121.0419 | 0.036621 | 3.067 | 0.086975 | 121.3669 | -0.082397 | -0.19684 | 0.018311 | 0.18768 | -0.045776 | 121.2753 | 121.2982 | -0.064087 | -0.1236 | 0.050354 | -0.064087 | 0.027465 | 0.16937 | 0.21973 | 0.28381 | -0.29755 | 0.068664 | 0.009155 | -0.064087 | 0.15106 | 0.086975 | 0.07782 | -0.041199 | 121.4996 | 121.1746 | 3.1998 | -121.5363 | 121.4081 | 121.431 | 0.32043 | -121.463
702.3438 | 121.4401 | -0.16022 | 121.3623 | 0.0066373 | 0.010309 | 0.071421 | 0.003843 | 0.063643 | 0.00093576 | -0.00059384 | 0.0069425 | -0.00022644 | 0.062107 | 0.0653 | -0.0062079 | -0.0085193 | 121.0831 | 0.009155 | 3.0762 | 0.07782 | 121.3806 | -0.050354 | -0.16479 | 0.045776 | 0.15564 | -0.07782 | 121.2753 | 121.3165 | -0.073242 | -0.1236 | 0.10986 | -0.004578 | 0.01831 | 0.16937 | 0.23804 | 0.24261 | -0.27924 | 0.086975 | 0.036621 | -0.086975 | 0.20599 | 0.082397 | 0.045776 | -0.045777 | 121.5408 | 121.2433 | 3.2364 | -121.5271 | 121.4355 | 121.4767 | 0.31586 | -121.4859
704.0312 | 121.4767 | -0.1236 | 121.3623 | 0.0066373 | 0.0079596 | 0.072489 | 0.0042702 | 0.062574 | -0.00077324 | -0.003371 | 0.0069425 | -0.00086724 | 0.064884 | 0.05996 | -0.0089849 | -0.0072375 | 121.0785 | 0.082397 | 3.1403 | 0.091553 | 121.344 | -0.068665 | -0.17853 | 0.013733 | 0.21515 | -0.09613 | 121.2799 | 121.3394 | -0.086975 | -0.13733 | 0.054931 | -0.054932 | -0.018311 | 0.20599 | 0.21515 | 0.27008 | -0.28381 | 0.036621 | -0.013733 | -0.082398 | 0.13733 | 0.027466 | 0.041199 | -0.022888 | 121.4676 | 121.2021 | 3.2639 | -121.5408 | 121.4035 | 121.463 | 0.33875 | -121.4996
705.7188 | 121.4264 | -0.16022 | 121.3669 | -0.00099167 | 0.0047552 | 0.069712 | 0.0032022 | 0.064283 | 0.0039264 | -0.0014484 | 0.0069425 | 0.0027644 | 0.06467 | 0.065514 | -0.0051397 | -0.0070239 | 121.0693 | 0.004578 | 3.0853 | 0.041199 | 121.3943 | -0.10071 | -0.19226 | -0.013733 | 0.11902 | -0.1831 | 121.2891 | 121.3211 | -0.10071 | -0.12817 | 0.059509 | -0.032044 | 0.027466 | 0.16479 | 0.20142 | 0.23346 | -0.29755 | 0.059509 | 0.032043 | -0.07782 | 0.14648 | -0.022888 | -0.054931 | -0.045776 | 121.5546 | 121.2296 | 3.2455 | -121.5591 | 121.4493 | 121.4813 | 0.27924 | -121.4951
707.4531 | 121.5271 | -0.1236 | 121.3165 | 0.014267 | 0.010737 | 0.071421 | 0.0070474 | 0.064497 | -0.0035504 | -0.0055072 | -0.00068649 | -0.00065364 | 0.065097 | 0.063805 | -0.011762 | -0.0042467 | 121.0922 | 0.10071 | 3.1586 | 0.10529 | 121.3486 | -0.032043 | -0.16937 | 0.045776 | 0.2243 | -0.050354 | 121.2753 | 121.3303 | -0.086975 | -0.10986 | 0.091553 | -0.045777 | 0.032044 | 0.2243 | 0.22888 | 0.27466 | -0.2243 | 0.036621 | 0.013733 | -0.041198 | 0.16937 | 0.073242 | 0.059509 | 0.013733 | 121.4722 | 121.2158 | 3.2822 | -121.4859 | 121.3989 | 121.4539 | 0.3479 | -121.4264
709.2031 | 121.5271 | -0.11902 | 121.3348 | 0.0066373 | 0.0064642 | 0.072916 | 0.0068338 | 0.063215 | 0.0011494 | -0.001662 | 0.0069425 | 0.00041436 | 0.063816 | 0.066582 | -0.0096259 | -0.0093737 | 120.9869 | -0.059509 | 3.0396 | -0.004578 | 121.4447 | -0.10986 | -0.21057 | -0.09613 | 0.086975 | -0.20142 | 121.3303 | 121.3531 | -0.13275 | -0.15564 | 0.009156 | -0.091552 | 0.10986 | 0.05951 | 0.11444 | 0.20599 | -0.3479 | -0.013732 | -0.036621 | -0.004578 | 0.022889 | -0.082397 | -0.045776 | 0.01831 | 121.5637 | 121.106 | 3.1586 | -121.5454 | 121.4493 | 121.4722 | 0.20599 | -121.4905
710.875 | 121.4355 | -0.16479 | 121.3623 | -0.00099167 | 0.007746 | 0.069498 | 0.0029886 | 0.063429 | 0.0015766 | -0.0031574 | 0.0069425 | 0.002337 | 0.06232 | 0.062737 | -0.0047125 | -0.0053149 | 120.9915 | -0.068665 | 3.0304 | 0.009155 | 121.431 | -0.10071 | -0.20599 | -0.054932 | 0.036621 | -0.21515 | 121.3211 | 121.3348 | -0.10529 | -0.15106 | 0.064087 | -0.041199 | 0.068664 | 0.09613 | 0.17395 | 0.21515 | -0.37079 | 0.059509 | 0.013733 | -0.041199 | 0.10986 | -0.050354 | -0.064087 | -0.027466 | 121.5958 | 121.1563 | 3.1952 | -121.5683 | 121.4859 | 121.4996 | 0.20142 | -121.5134
712.6094 | 121.5408 | -0.13275 | 121.344 | -0.0086212 | 0.010309 | 0.070139 | 0.0057656 | 0.064711 | -0.0024822 | -0.001021 | -0.00068649 | 0.00062796 | 0.065097 | 0.063591 | -0.0098395 | -0.0044605 | 120.9686 | -0.050354 | 3.067 | 0.018311 | 121.3989 | -0.11444 | -0.21057 | -0.082397 | 0.09613 | -0.1831 | 121.2982 | 121.3623 | -0.10986 | -0.15106 | 0.01831 | -0.07782 | 0.054932 | 0.082397 | 0.15106 | 0.22888 | -0.37537 | 0.022888 | -0.018311 | -0.045776 | 0.050354 | -0.050354 | -0.032043 | 0.018311 | 121.5317 | 121.1014 | 3.1998 | -121.5546 | 121.431 | 121.4951 | 0.22888 | -121.4951
714.2969 | 121.4767 | -0.1236 | 121.3165 | 0.0066373 | 0.0083868 | 0.070993 | 0.0076882 | 0.061506 | -0.0041912 | -0.0023028 | -0.00068649 | -0.0032172 | 0.063175 | 0.065087 | -0.011335 | -0.0063831 | 121.0648 | 0.11444 | 3.1998 | 0.10529 | 121.3577 | -0.059509 | -0.17853 | 0.018311 | 0.24719 | -0.045776 | 121.2662 | 121.2936 | -0.07782 | -0.11444 | 0.064087 | -0.054932 | 0.041199 | 0.23804 | 0.22888 | 0.28381 | -0.25177 | 0.045776 | 0.009155 | -0.050354 | 0.14191 | 0.07782 | 0.068665 | -0.022888 | 121.4813 | 121.1884 | 3.3234 | -121.4951 | 121.3898 | 121.4172 | 0.37079 | -121.431
716.0469 | 121.4035 | -0.17853 | 121.3669 | -0.0086212 | 0.0045416 | 0.069712 | 0.002134 | 0.062574 | 0.0043536 | -0.001662 | -0.00068649 | 0.0016962 | 0.064884 | 0.065514 | -0.0059943 | -0.0063831 | 121.0281 | 0.004578 | 3.1494 | 0.050354 | 121.431 | -0.09613 | -0.17853 | -0.027466 | 0.09613 | -0.16479 | 121.3211 | 121.3211 | -0.10071 | -0.14648 | 0.082398 | 0 | 0.064087 | 0.18311 | 0.22888 | 0.22888 | -0.33875 | 0.07782 | 0.032044 | -0.045776 | 0.15106 | 0.013733 | -0.018311 | -0.045776 | 121.6095 | 121.2067 | 3.3279 | -121.5454 | 121.4996 | 121.4996 | 0.27466 | -121.5134
717.7188 | 121.4447 | -0.15564 | 121.3577 | -0.00099167 | 0.0081732 | 0.069925 | 0.0051248 | 0.063002 | 8.1158e-05 | -0.001662 | 0.0069425 | 0.0021234 | 0.06467 | 0.063805 | -0.0087713 | -0.0061695 | 120.9641 | -0.059509 | 3.067 | 0 | 121.4127 | -0.10071 | -0.21057 | -0.07782 | 0.022888 | -0.20142 | 121.3348 | 121.344 | -0.11902 | -0.13733 | 0.054932 | -0.054931 | 0.054932 | 0.096131 | 0.15564 | 0.21057 | -0.39368 | 0.036621 | 0.018311 | -0.022888 | 0.07782 | -0.045776 | -0.064087 | -0.013733 | 121.5683 | 121.1197 | 3.2227 | -121.5683 | 121.4905 | 121.4996 | 0.17853 | -121.4951
719.4531 | 121.4859 | -0.14648 | 121.3165 | 0.0066373 | 0.0058234 | 0.071634 | 0.0083292 | 0.06172 | -0.0048322 | -0.0037982 | 0.0069425 | -0.00065364 | 0.062534 | 0.062737 | -0.012189 | -0.0059557 | 121.0327 | 0.068665 | 3.1998 | 0.09613 | 121.3715 | -0.045776 | -0.16937 | -0.022888 | 0.19684 | -0.09613 | 121.2936 | 121.3577 | -0.09613 | -0.1236 | 0.10071 | -0.022889 | 0.054932 | 0.21515 | 0.24261 | 0.2655 | -0.28381 | 0.050354 | 0.022888 | -0.022888 | 0.1236 | 0.050354 | 0.027466 | 0.041199 | 121.5179 | 121.1792 | 3.3463 | -121.4859 | 121.4401 | 121.5042 | 0.34332 | -121.4401
721.2031 | 121.4081 | -0.16937 | 121.3715 | 0.0066373 | 0.004969 | 0.067362 | 0.0025612 | 0.063429 | 0.00414 | -0.00059384 | -0.008316 | 0.002978 | 0.065097 | 0.0653 | -0.0057807 | -0.0076647 | 121.0098 | -0.027466 | 3.1082 | 0.022888 | 121.4172 | -0.091553 | -0.21057 | -0.059509 | 0.068665 | -0.20599 | 121.3165 | 121.3486 | -0.10529 | -0.15106 | 0.07782 | -0.041198 | 0.045776 | 0.14191 | 0.19226 | 0.23346 | -0.36163 | 0.064087 | 0.018311 | -0.054932 | 0.10986 | -0.036621 | -0.054932 | -0.022888 | 121.5866 | 121.1792 | 3.2776 | -121.582 | 121.4859 | 121.5179 | 0.23804 | -121.5225
722.9375 | 121.5363 | -0.10986 | 121.3715 | -0.00099167 | 0.010737 | 0.07313 | 0.007261 | 0.060438 | -0.006541 | -0.0029436 | -0.00068649 | -0.0023626 | 0.063602 | 0.064019 | -0.013471 | -0.0048877 | 121.0602 | 0.11902 | 3.1952 | 0.091553 | 121.3531 | -0.073242 | -0.1831 | 0.041199 | 0.24719 | -0.018311 | 121.2753 | 121.3165 | -0.068665 | -0.1236 | 0.036621 | -0.073242 | -0.018311 | 0.22888 | 0.20142 | 0.27466 | -0.31128 | 0.041198 | -0.013733 | -0.09613 | 0.15106 | 0.091552 | 0.10528 | -0.054932 | 121.463 | 121.17 | 3.3051 | -121.5546 | 121.3852 | 121.4264 | 0.35706 | -121.4951
724.6719 | 121.5042 | -0.1236 | 121.3669 | 0.021896 | 0.0039008 | 0.068216 | 0.0036294 | 0.062574 | 0.0020038 | -0.00273 | 0.0069425 | 0.0034052 | 0.062961 | 0.06231 | -0.0066351 | -0.0095873 | 121.0556 | 0.013733 | 3.186 | 0.054932 | 121.431 | -0.073242 | -0.20142 | -0.004578 | 0.14191 | -0.14191 | 121.3211 | 121.3715 | -0.086975 | -0.14191 | 0.050354 | -0.07782 | 0.064087 | 0.13733 | 0.17853 | 0.25635 | -0.31128 | 0.036621 | -0.018311 | -0.045776 | 0.11902 | -0.018311 | 0 | 0.004578 | 121.5546 | 121.1792 | 3.3096 | -121.5683 | 121.4447 | 121.4951 | 0.2655 | -121.5088
726.4219 | 121.5225 | -0.13733 | 121.3577 | 0.021896 | 0.004969 | 0.073557 | 0.0032022 | 0.064924 | 0.0026446 | -0.001021 | 0.014572 | 0.0021234 | 0.063816 | 0.06295 | -0.0077033 | -0.0063831 | 121.0419 | 0.027466 | 3.1952 | 0.050354 | 121.4172 | -0.09613 | -0.17853 | -0.009155 | 0.14648 | -0.14191 | 121.312 | 121.3806 | -0.091553 | -0.14648 | 0.041199 | -0.041199 | 0.059509 | 0.16479 | 0.18768 | 0.22888 | -0.31586 | 0.045776 | -0.009155 | -0.045776 | 0.12817 | -0.004578 | 0.004577 | 0.022888 | 121.5546 | 121.1792 | 3.3325 | -121.5363 | 121.4493 | 121.5179 | 0.28381 | -121.5042
728.0938 | 121.4584 | -0.14648 | 121.3989 | -0.00099167 | 0.0086006 | 0.068644 | 0.0044838 | 0.063429 | -0.00013244 | -0.0029436 | 0.014572 | 0.001269 | 0.06467 | 0.066582 | -0.0081305 | -0.0046741 | 120.9778 | -0.045776 | 3.1082 | 0.018311 | 121.4035 | -0.086975 | -0.19684 | -0.045776 | 0.041199 | -0.16479 | 121.3303 | 121.3394 | -0.11902 | -0.1236 | 0.059509 | -0.050354 | 0.004577 | 0.10071 | 0.16479 | 0.21515 | -0.42114 | 0.027465 | 0.022888 | -0.068665 | 0.10071 | -0.018311 | -0.041199 | -0.059509 | 121.55 | 121.1243 | 3.2547 | -121.5958 | 121.4767 | 121.4859 | 0.18768 | -121.5225
729.8438 | 121.5317 | -0.11902 | 121.3165 | 0.014267 | 0.0083868 | 0.073343 | 0.0076882 | 0.061506 | -0.0078228 | -0.0042254 | 0.014572 | -0.0034308 | 0.063175 | 0.063591 | -0.013471 | -0.0033923 | 121.051 | 0.1236 | 3.2318 | 0.10529 | 121.3852 | -0.045776 | -0.15106 | 0.045776 | 0.24261 | -0.013733 | 121.2799 | 121.3211 | -0.073242 | -0.10071 | 0.073243 | -0.032043 | 0.068665 | 0.24261 | 0.22431 | 0.25635 | -0.2655 | 0.045777 | 0.018311 | -0.036621 | 0.16479 | 0.10529 | 0.086975 | 0.004578 | 121.5042 | 121.17 | 3.3508 | -121.4676 | 121.3989 | 121.4401 | 0.36163 | -121.4172
731.5938 | 121.3989 | -0.1831 | 121.3898 | 0.0066373 | 0.0064642 | 0.068216 | 0.0083292 | 0.063856 | 0.001363 | -0.0029436 | -0.00068649 | 0.002337 | 0.064457 | 0.0653 | -0.0077033 | -0.0065967 | 120.9869 | -0.09613 | 3.1174 | 0.009155 | 121.4539 | -0.086975 | -0.21057 | -0.09613 | 0.036621 | -0.23346 | 121.3257 | 121.3806 | -0.10986 | -0.16022 | 0.09613 | -0.027466 | 0.064086 | 0.086975 | 0.19226 | 0.21973 | -0.40283 | 0.073242 | 0.022888 | -0.064087 | 0.086975 | -0.050354 | -0.073242 | -0.009156 | 121.637 | 121.17 | 3.3005 | -121.6003 | 121.5088 | 121.5637 | 0.21973 | -121.55
733.2656 | 121.4035 | -0.17853 | 121.4081 | 0.0066373 | 0.0058234 | 0.071634 | 0.003843 | 0.064283 | 0.0037128 | -0.00273 | 0.0069425 | 0.002337 | 0.063175 | 0.065728 | -0.0081305 | -0.0042467 | 120.9824 | -0.091553 | 3.1219 | 0.004578 | 121.3989 | -0.086975 | -0.21057 | -0.091553 | 0.032043 | -0.23346 | 121.3348 | 121.3898 | -0.09613 | -0.14648 | 0.091553 | -0.032043 | -0.009155 | 0.086975 | 0.18311 | 0.21515 | -0.42572 | 0.082398 | 0.032044 | -0.073242 | 0.086975 | -0.054931 | -0.086975 | -0.01831 | 121.5775 | 121.1609 | 3.3005 | -121.6187 | 121.5134 | 121.5683 | 0.21057 | -121.5546
735 | 121.4584 | -0.16937 | 121.3898 | -0.0086212 | 0.012873 | 0.07313 | 0.002775 | 0.06407 | -0.0080364 | -0.0031574 | -0.00068649 | -0.0040716 | 0.060184 | 0.062737 | -0.010053 | -0.0048877 | 121.0098 | 0.013733 | 3.1769 | 0.054932 | 121.376 | -0.082397 | -0.17853 | -0.036621 | 0.11444 | -0.10529 | 121.2845 | 121.3577 | -0.086975 | -0.12817 | 0.086976 | -0.009155 | -0.013733 | 0.18311 | 0.22431 | 0.23346 | -0.37994 | 0.082398 | 0.041199 | -0.10529 | 0.13275 | 0.064087 | 0.022888 | -0.032044 | 121.5454 | 121.1792 | 3.3463 | -121.5683 | 121.4539 | 121.5271 | 0.28381 | -121.5179
736.6719 | 121.5042 | -0.1236 | 121.3531 | 0.0066373 | 0.0039008 | 0.070353 | 0.0096108 | 0.06407 | -0.0014142 | -0.00508 | 0.0069425 | 0.00041436 | 0.065097 | 0.0653 | -0.012189 | -0.0063831 | 120.9778 | -0.050354 | 3.1631 | 0.013733 | 121.4264 | -0.10986 | -0.19684 | -0.086975 | 0.086975 | -0.17853 | 121.3348 | 121.3898 | -0.10986 | -0.16479 | 0.013733 | -0.073242 | 0.073243 | 0.073242 | 0.13733 | 0.21057 | -0.37537 | 0.013733 | -0.041199 | -0.01831 | 0.036621 | -0.054932 | -0.013733 | 0.036622 | 121.55 | 121.1014 | 3.2867 | -121.55 | 121.4584 | 121.5134 | 0.21057 | -121.5179
738.4062 | 121.5454 | -0.10986 | 121.3348 | -0.00099167 | 0.0053962 | 0.069925 | 0.0057656 | 0.06407 | 0.0011494 | -0.00508 | 0.014572 | 0.0019098 | 0.067447 | 0.065087 | -0.0081305 | -0.0080921 | 120.9915 | -0.054932 | 3.1769 | 0.027466 | 121.431 | -0.09613 | -0.21515 | -0.07782 | 0.10529 | -0.17853 | 121.3303 | 121.3806 | -0.10529 | -0.15106 | 0.013733 | -0.10529 | 0.09613 | 0.054931 | 0.13733 | 0.24261 | -0.34332 | 0.004577 | -0.041199 | -0.004578 | 0.032043 | -0.068665 | -0.027466 | 0.045776 | 121.5408 | 121.1014 | 3.2867 | -121.55 | 121.4401 | 121.4905 | 0.21515 | -121.4859
740.1562 | 121.4951 | -0.13733 | 121.3486 | 0.0066373 | 0.007746 | 0.073343 | 0.0057656 | 0.061934 | -0.0044048 | -0.0052936 | -0.00068649 | -0.0030034 | 0.064029 | 0.066796 | -0.010267 | -0.0051013 | 121.0739 | 0.10071 | 3.3005 | 0.10529 | 121.3898 | -0.059509 | -0.15564 | 0.027466 | 0.24261 | -0.032043 | 121.2845 | 121.3394 | -0.064087 | -0.11444 | 0.07782 | -0.018311 | 0.041199 | 0.23804 | 0.24262 | 0.26093 | -0.27466 | 0.073242 | 0.022888 | -0.064087 | 0.16479 | 0.10529 | 0.082398 | -0.009155 | 121.5271 | 121.2112 | 3.4378 | -121.5042 | 121.4218 | 121.4767 | 0.37994 | -121.463
741.8906 | 121.4172 | -0.16479 | 121.4127 | -0.0086212 | 0.0053962 | 0.068003 | 0.0049112 | 0.063643 | 0.0037128 | -0.00273 | 0.0069425 | 0.0034052 | 0.064457 | 0.065087 | -0.0057807 | -0.0059557 | 120.9961 | -0.091553 | 3.1631 | 0.009155 | 121.4447 | -0.09613 | -0.19684 | -0.054932 | 0.027466 | -0.19684 | 121.3486 | 121.3852 | -0.10986 | -0.15106 | 0.068665 | -0.032043 | 0.032043 | 0.073242 | 0.17395 | 0.20599 | -0.41657 | 0.054932 | 0.013733 | -0.064087 | 0.10986 | -0.032043 | -0.045776 | -0.027466 | 121.6095 | 121.1609 | 3.3279 | -121.6095 | 121.5134 | 121.55 | 0.19226 | -121.5637
743.5625 | 121.4172 | -0.16022 | 121.3898 | 0.0066373 | 0.0075324 | 0.069712 | 0.002134 | 0.062788 | 0.0015766 | -0.00080744 | 0.014572 | 0.0031916 | 0.065097 | 0.0653 | -0.0055671 | -0.0063831 | 120.9778 | -0.073242 | 3.1769 | 0.013733 | 121.4447 | -0.091553 | -0.20599 | -0.073242 | 0.032043 | -0.20599 | 121.3394 | 121.3852 | -0.10986 | -0.13275 | 0.068664 | -0.045777 | 0.054931 | 0.086975 | 0.17395 | 0.21973 | -0.41199 | 0.050354 | 0.027466 | -0.050354 | 0.086975 | -0.045777 | -0.073243 | -0.004578 | 121.6049 | 121.138 | 3.3371 | -121.5958 | 121.4996 | 121.5454 | 0.19226 | -121.5225
745.3125 | 121.4859 | -0.13275 | 121.3623 | 0.0066373 | 0.0068916 | 0.072702 | 0.0068338 | 0.062788 | -0.0018414 | -0.0023028 | -0.00068649 | 0.00062796 | 0.065097 | 0.066155 | -0.010053 | -0.0059557 | 121.0144 | 0.004578 | 3.2593 | 0.041199 | 121.3989 | -0.10529 | -0.20599 | -0.082397 | 0.11902 | -0.15106 | 121.3074 | 121.4081 | -0.09613 | -0.14191 | 0.027465 | -0.073243 | 0.036621 | 0.13733 | 0.17395 | 0.24719 | -0.3479 | 0.036621 | -0.009156 | -0.054932 | 0.050354 | -0.018311 | -0.009155 | 0.045776 | 121.5317 | 121.1472 | 3.392 | -121.5683 | 121.4401 | 121.5408 | 0.25177 | -121.5042
747.0625 | 121.4081 | -0.15106 | 121.376 | 0.014267 | 0.0096686 | 0.071421 | 0.0034158 | 0.061506 | -0.0041912 | -0.004439 | 0.0069425 | -0.0032172 | 0.06467 | 0.062523 | -0.0094123 | -0.0065967 | 121.0785 | 0.073242 | 3.3188 | 0.07782 | 121.376 | -0.059509 | -0.16022 | 0.027466 | 0.14648 | -0.059509 | 121.2662 | 121.3486 | -0.07782 | -0.12817 | 0.091553 | -0.009155 | 0 | 0.2243 | 0.22888 | 0.23804 | -0.29755 | 0.073242 | 0.022888 | -0.10986 | 0.17853 | 0.091553 | 0.068665 | -0.027466 | 121.5271 | 121.2296 | 3.4698 | -121.5363 | 121.4172 | 121.4996 | 0.29755 | -121.5042
748.8125 | 121.4539 | -0.16937 | 121.3623 | 0.0066373 | 0.0092414 | 0.071421 | 0.0019204 | 0.063215 | 0.0015766 | -0.0020892 | 0.0069425 | 0.0010554 | 0.060184 | 0.064232 | -0.0066351 | -0.0070239 | 121.0144 | -0.07782 | 3.2089 | 0.013733 | 121.4447 | -0.091553 | -0.19226 | -0.073242 | 0.027466 | -0.18768 | 121.3486 | 121.4081 | -0.11444 | -0.12817 | 0.07782 | -0.022888 | 0.082397 | 0.091553 | 0.18311 | 0.20599 | -0.3479 | 0.054932 | 0.041199 | -0.013733 | 0.096131 | -0.01831 | -0.059509 | 0.045776 | 121.6141 | 121.1838 | 3.3783 | -121.5546 | 121.5179 | 121.5775 | 0.19684 | -121.4905
750.5469 | 121.4584 | -0.16479 | 121.3989 | 0.0066373 | 0.0090278 | 0.069071 | 0.0023476 | 0.063643 | 0.00072196 | -0.004439 | -0.00068649 | 0.002337 | 0.064457 | 0.066368 | -0.0081305 | -0.0072375 | 121.0007 | -0.064087 | 3.2181 | 0.013733 | 121.4264 | -0.091553 | -0.21515 | -0.064087 | 0.036621 | -0.17395 | 121.344 | 121.3806 | -0.09613 | -0.13275 | 0.073242 | -0.050354 | 0.027466 | 0.10071 | 0.17853 | 0.22888 | -0.39826 | 0.068665 | 0.032044 | -0.054932 | 0.10071 | -0.009155 | -0.041199 | -0.018311 | 121.5912 | 121.1655 | 3.3829 | -121.6141 | 121.5088 | 121.5454 | 0.20142 | -121.5317
752.3594 | 121.3852 | -0.17395 | 121.4172 | 0.0066373 | 0.0096686 | 0.072062 | 0.005552 | 0.064497 | -0.0048322 | -0.0029436 | 0.0069425 | -0.00044004 | 0.06232 | 0.063378 | -0.013044 | -0.0068103 | 121.0739 | 0.050354 | 3.3325 | 0.07782 | 121.3898 | -0.045776 | -0.15564 | 0.004578 | 0.14191 | -0.068665 | 121.3074 | 121.3669 | -0.059509 | -0.10986 | 0.12817 | 0.01831 | -0.027465 | 0.2243 | 0.25177 | 0.23346 | -0.34332 | 0.11444 | 0.064087 | -0.10986 | 0.17853 | 0.10528 | 0.041198 | -0.050354 | 121.5637 | 121.2479 | 3.5065 | -121.5729 | 121.4813 | 121.5408 | 0.31586 | -121.5271
754.1094 | 121.4218 | -0.16022 | 121.3989 | 0.0066373 | 0.0071052 | 0.067148 | 0.0025612 | 0.063856 | 0.0017902 | -0.003371 | -0.00068649 | 0.0016962 | 0.064029 | 0.064232 | -0.0083441 | -0.0076647 | 120.9915 | -0.09613 | 3.2272 | 0.009155 | 121.463 | -0.10071 | -0.19684 | -0.050354 | 0.022888 | -0.21057 | 121.3669 | 121.3898 | -0.11902 | -0.15106 | 0.059509 | -0.036621 | 0.064087 | 0.064087 | 0.16937 | 0.20599 | -0.40741 | 0.041198 | 0.009155 | -0.032044 | 0.10986 | -0.050354 | -0.059509 | -0.009155 | 121.6232 | 121.1517 | 3.3875 | -121.5958 | 121.5271 | 121.55 | 0.1831 | -121.55
755.8281 | 121.5317 | -0.10071 | 121.344 | 0.014267 | 0.010309 | 0.072062 | 0.0061928 | 0.059156 | -0.0050458 | -0.0048662 | 0.0069425 | -0.0023626 | 0.063388 | 0.064019 | -0.013044 | -0.0051013 | 121.0373 | 0.054932 | 3.3371 | 0.07782 | 121.4264 | -0.050354 | -0.16022 | 0.013733 | 0.19226 | -0.032043 | 121.2982 | 121.3806 | -0.050354 | -0.10986 | 0.050354 | -0.059509 | 0.082398 | 0.15564 | 0.17853 | 0.23804 | -0.3067 | 0.050354 | -0.009155 | -0.045776 | 0.11444 | 0.068665 | 0.07782 | 0.036621 | 121.5271 | 121.138 | 3.4378 | -121.5042 | 121.3989 | 121.4813 | 0.29297 | -121.4539
757.5312 | 121.4401 | -0.15106 | 121.4035 | 0.0066373 | 0.0098822 | 0.069925 | 0.001066 | 0.063856 | -0.00034604 | -0.0055072 | 0.0069425 | 0.0010554 | 0.060825 | 0.063164 | -0.0066351 | -0.0076647 | 121.1105 | 0.064087 | 3.3554 | 0.10529 | 121.3852 | -0.054932 | -0.16479 | 0.054932 | 0.16022 | -0.045776 | 121.2936 | 121.3394 | -0.068665 | -0.10529 | 0.09613 | -0.013733 | -0.01831 | 0.21515 | 0.25635 | 0.27008 | -0.29297 | 0.082397 | 0.045776 | -0.10986 | 0.20599 | 0.10529 | 0.05951 | -0.064086 | 121.5363 | 121.2616 | 3.5065 | -121.5683 | 121.4447 | 121.4905 | 0.31128 | -121.5088
759.2344 | 121.5637 | -0.11902 | 121.3486 | 0.0066373 | 0.0034736 | 0.07078 | 0.0074746 | 0.063215 | 0.0011494 | -0.00508 | -0.00068649 | 0.00041436 | 0.064457 | 0.062737 | -0.0087713 | -0.0083057 | 121.0098 | -0.059509 | 3.273 | 0.018311 | 121.4539 | -0.082397 | -0.20599 | -0.068665 | 0.091553 | -0.19226 | 121.3577 | 121.4264 | -0.11444 | -0.14648 | 0.036622 | -0.086975 | 0.10528 | 0.05951 | 0.13733 | 0.22431 | -0.33875 | 0.004578 | -0.027465 | 0.009155 | 0.050354 | -0.073242 | -0.045777 | 0.07782 | 121.5729 | 121.1288 | 3.392 | -121.5546 | 121.4767 | 121.5454 | 0.21057 | -121.4951
760.9688 | 121.5454 | -0.13733 | 121.3348 | -0.00099167 | 0.004328 | 0.069071 | 0.0093972 | 0.065138 | 0.00050836 | -0.0037982 | -0.00068649 | -0.0025762 | 0.065525 | 0.064446 | -0.010908 | -0.0065967 | 120.9869 | -0.041199 | 3.2639 | 0.018311 | 121.4767 | -0.10986 | -0.21057 | -0.091553 | 0.086975 | -0.19684 | 121.3303 | 121.3852 | -0.10986 | -0.16479 | 0.027466 | -0.073242 | 0.14191 | 0.09613 | 0.15564 | 0.22888 | -0.3479 | 0.027466 | -0.027466 | -0.004578 | 0.045776 | -0.059509 | -0.032043 | 0.050354 | 121.6141 | 121.1243 | 3.4012 | -121.5454 | 121.4676 | 121.5225 | 0.2243 | -121.4996
762.6562 | 121.5546 | -0.10986 | 121.3715 | 0.0066373 | 0.0039008 | 0.070139 | 0.0066202 | 0.063856 | 0.0020038 | -0.00059384 | -0.00068649 | -0.00044004 | 0.064243 | 0.065514 | -0.0079169 | -0.0065967 | 121.0419 | -0.004578 | 3.3325 | 0.064087 | 121.4401 | -0.091553 | -0.20599 | 0.004578 | 0.14191 | -0.13733 | 121.344 | 121.3852 | -0.09613 | -0.14191 | 0.01831 | -0.096131 | 0.068665 | 0.10529 | 0.17395 | 0.27008 | -0.32959 | 0.013733 | -0.032044 | -0.027466 | 0.11444 | -0.027466 | 0.004578 | 0.013733 | 121.55 | 121.1517 | 3.4424 | -121.5775 | 121.4539 | 121.4951 | 0.25177 | -121.5134
764.3438 | 121.4996 | -0.14648 | 121.3669 | -0.00099167 | 0.0096686 | 0.072489 | 0.0061928 | 0.063002 | -0.0059002 | -0.0072162 | -0.00068649 | -0.0015082 | 0.062534 | 0.062737 | -0.01048 | -0.0051013 | 121.0098 | 0.027466 | 3.3234 | 0.064087 | 121.4081 | -0.07782 | -0.17853 | -0.022888 | 0.13275 | -0.10529 | 121.3211 | 121.3715 | -0.09613 | -0.12817 | 0.068664 | -0.032044 | 0.041199 | 0.17395 | 0.21057 | 0.24261 | -0.35706 | 0.050354 | 0.01831 | -0.045776 | 0.1236 | 0.041198 | 0.022888 | 0.004578 | 121.5546 | 121.1563 | 3.4698 | -121.5454 | 121.4676 | 121.5179 | 0.27924 | -121.4951
766.0625 | 121.4264 | -0.16937 | 121.3898 | 0.0066373 | 0.011378 | 0.072916 | 0.0042702 | 0.063215 | -0.0026958 | -0.0031574 | 0.0069425 | -0.0012946 | 0.061466 | 0.064019 | -0.0091985 | -0.0074511 | 121.051 | 0.032043 | 3.3417 | 0.059509 | 121.4035 | -0.073242 | -0.16937 | -0.018311 | 0.10986 | -0.11444 | 121.3211 | 121.3715 | -0.064087 | -0.1236 | 0.096131 | 0 | 0.013732 | 0.20142 | 0.22888 | 0.22888 | -0.33875 | 0.10529 | 0.045777 | -0.068665 | 0.15106 | 0.054932 | 0.009155 | -0.018311 | 121.5729 | 121.2204 | 3.511 | -121.5591 | 121.4905 | 121.5408 | 0.27924 | -121.5134
767.7344 | 121.5637 | -0.1236 | 121.3623 | 0.0066373 | 0.011591 | 0.074839 | 0.0081154 | 0.063002 | -0.0033368 | -0.0046526 | 0.0069425 | -0.0036444 | 0.061466 | 0.061882 | -0.010694 | -0.0055285 | 121.1105 | 0.091553 | 3.392 | 0.09613 | 121.3989 | -0.064087 | -0.15564 | 0.041199 | 0.22888 | -0.032043 | 121.3074 | 121.376 | -0.068665 | -0.10071 | 0.059509 | -0.032044 | 0.036621 | 0.21515 | 0.21973 | 0.25177 | -0.25177 | 0.054931 | 0.022888 | -0.054932 | 0.16479 | 0.091553 | 0.068665 | 0.013733 | 121.5225 | 121.2341 | 3.5156 | -121.5179 | 121.431 | 121.4996 | 0.35248 | -121.463
769.5 | 121.5271 | -0.13275 | 121.3852 | 0.0066373 | 0.004969 | 0.070353 | 0.0017068 | 0.06407 | 0.0045674 | -0.003371 | -0.00068649 | 0.0038324 | 0.065097 | 0.063378 | -0.0066351 | -0.0089465 | 121.0785 | -0.004578 | 3.3646 | 0.045776 | 121.4539 | -0.082397 | -0.2243 | 0.009155 | 0.15106 | -0.15106 | 121.3394 | 121.4127 | -0.10529 | -0.13275 | 0.050354 | -0.091553 | 0.068664 | 0.12817 | 0.17853 | 0.27008 | -0.3067 | 0.027465 | 0 | -0.045776 | 0.14191 | -0.018311 | -0.018311 | 0.027466 | 121.5866 | 121.2112 | 3.4973 | -121.6095 | 121.4722 | 121.5454 | 0.28381 | -121.5179
771.2031 | 121.55 | -0.13733 | 121.344 | 0.0066373 | 0.0051826 | 0.068644 | 0.0057656 | 0.062147 | 0.0020038 | -0.0014484 | -0.00068649 | -0.00022644 | 0.065311 | 0.063591 | -0.0072759 | -0.0059557 | 121.0648 | 0.013733 | 3.3646 | 0.054932 | 121.4447 | -0.11444 | -0.20599 | -0.004578 | 0.15564 | -0.12817 | 121.3394 | 121.3806 | -0.082397 | -0.13275 | 0.022888 | -0.068665 | 0.10071 | 0.15106 | 0.19226 | 0.26093 | -0.27924 | 0.054932 | 0.004578 | -0.004577 | 0.13275 | 0.009155 | 0.004577 | 0.036621 | 121.582 | 121.2021 | 3.5019 | -121.55 | 121.4767 | 121.5179 | 0.29297 | -121.4767
772.9062 | 121.4676 | -0.14648 | 121.4081 | 0.0066373 | 0.0079596 | 0.071634 | 0.0014932 | 0.064283 | -0.0031232 | -0.0025164 | 0.022202 | 0.001269 | 0.064457 | 0.063164 | -0.0081305 | -0.0048877 | 121.0968 | 0.041199 | 3.4012 | 0.10529 | 121.4172 | -0.064087 | -0.14648 | 0.036621 | 0.17395 | -0.050354 | 121.3028 | 121.376 | -0.064087 | -0.10529 | 0.082397 | 0 | 0.009155 | 0.18768 | 0.25177 | 0.25177 | -0.31128 | 0.082397 | 0.041198 | -0.10529 | 0.18311 | 0.09613 | 0.054932 | -0.032043 | 121.5637 | 121.2433 | 3.5477 | -121.5546 | 121.4493 | 121.5225 | 0.32043 | -121.5134
774.5938 | 121.3989 | -0.16022 | 121.3989 | 0.0066373 | 0.010737 | 0.070993 | 0.0029886 | 0.05937 | -0.00055964 | -0.0042254 | 0.022202 | -0.00065364 | 0.061252 | 0.063805 | -0.010267 | -0.0048877 | 121.1288 | 0.086975 | 3.4378 | 0.10529 | 121.3806 | -0.064087 | -0.16937 | 0.041199 | 0.17853 | -0.045776 | 121.2936 | 121.3943 | -0.064087 | -0.10986 | 0.09613 | -0.009156 | -0.018311 | 0.24719 | 0.2655 | 0.27466 | -0.27008 | 0.09613 | 0.050354 | -0.10529 | 0.20142 | 0.11444 | 0.064087 | -0.004578 | 121.5408 | 121.2891 | 3.598 | -121.5683 | 121.4539 | 121.5546 | 0.33874 | -121.5088
776.2969 | 121.5088 | -0.14191 | 121.3715 | 0.0066373 | 0.012659 | 0.075479 | 0.0061928 | 0.063429 | -0.005473 | -0.0072162 | 0.014572 | -0.0015082 | 0.062534 | 0.063591 | -0.012403 | -0.0038195 | 121.0419 | 0.018311 | 3.3691 | 0.054932 | 121.4264 | -0.068665 | -0.1831 | -0.013733 | 0.15106 | -0.082397 | 121.3028 | 121.3715 | -0.073242 | -0.10986 | 0.073242 | -0.041198 | 0.054932 | 0.16022 | 0.19684 | 0.23804 | -0.32959 | 0.068665 | 0.032044 | -0.068665 | 0.12817 | 0.05951 | 0.027466 | 0 | 121.5683 | 121.1838 | 3.511 | -121.5546 | 121.4447 | 121.5134 | 0.29297 | -121.4813
778 | 121.4722 | -0.14191 | 121.3989 | -0.0086212 | 0.010737 | 0.073984 | 0.0034158 | 0.065351 | -0.0029094 | -0.0042254 | -0.00068649 | -0.0012946 | 0.06232 | 0.063805 | -0.0091985 | -0.0061695 | 121.0556 | 0.018311 | 3.3646 | 0.059509 | 121.4218 | -0.064087 | -0.17853 | -0.022888 | 0.13275 | -0.091553 | 121.3211 | 121.3898 | -0.082397 | -0.11444 | 0.07782 | -0.036621 | 0.022888 | 0.16022 | 0.20142 | 0.23804 | -0.34332 | 0.05951 | 0.027466 | -0.07782 | 0.11902 | 0.050354 | 0.022888 | -0.009155 | 121.5637 | 121.1975 | 3.5065 | -121.5775 | 121.463 | 121.5317 | 0.27466 | -121.5134
779.6875 | 121.5042 | -0.14648 | 121.376 | -0.00099167 | 0.0096686 | 0.074198 | 0.0049112 | 0.061934 | -0.0014142 | -0.00273 | -0.00068649 | -0.00086724 | 0.061679 | 0.06231 | -0.0083441 | -0.0055285 | 121.0373 | -0.004578 | 3.3737 | 0.054932 | 121.4264 | -0.059509 | -0.17853 | -0.013733 | 0.1236 | -0.068665 | 121.3211 | 121.3715 | -0.073242 | -0.1236 | 0.086975 | -0.032044 | 0.050354 | 0.14191 | 0.20142 | 0.23346 | -0.33875 | 0.073242 | 0.022888 | -0.054932 | 0.13275 | 0.077819 | 0.054931 | -0.004578 | 121.5729 | 121.1838 | 3.5202 | -121.5546 | 121.4676 | 121.5179 | 0.27008 | -121.4996
781.3594 | 121.5134 | -0.15106 | 121.3989 | -0.0086212 | 0.0058234 | 0.071421 | 0.0070474 | 0.063215 | -0.00013244 | -0.0042254 | 0.0069425 | 0.0021234 | 0.063388 | 0.063164 | -0.0091985 | -0.0089465 | 121.0739 | 0.018311 | 3.4378 | 0.059509 | 121.431 | -0.07782 | -0.18768 | -0.050354 | 0.1236 | -0.15106 | 121.3531 | 121.4127 | -0.11444 | -0.13275 | 0.073242 | -0.036621 | 0.032043 | 0.16937 | 0.21057 | 0.24719 | -0.32501 | 0.036621 | 0.018311 | -0.045777 | 0.10071 | 0 | -0.018311 | 0.013733 | 121.582 | 121.225 | 3.5889 | -121.5866 | 121.5042 | 121.5637 | 0.27466 | -121.5317
783.0312 | 121.5225 | -0.14648 | 121.3715 | 0.0066373 | 0.0045416 | 0.073984 | 0.0081154 | 0.065351 | -0.00013244 | -0.00508 | -0.00068649 | 0.00020076 | 0.064884 | 0.064873 | -0.010694 | -0.0087329 | 121.0327 | -0.027466 | 3.3783 | 0.009155 | 121.4539 | -0.086975 | -0.21057 | -0.068665 | 0.11902 | -0.16937 | 121.3715 | 121.3989 | -0.10529 | -0.13733 | 0.059509 | -0.064087 | 0.082397 | 0.11902 | 0.15564 | 0.21973 | -0.33875 | 0.041198 | 0.009155 | 0 | 0.077819 | -0.022889 | -0.032044 | 0.027466 | 121.6003 | 121.1792 | 3.5248 | -121.582 | 121.5179 | 121.5454 | 0.2655 | -121.5088
784.7188 | 121.5637 | -0.12817 | 121.3669 | 0.0066373 | 0.0028326 | 0.067362 | 0.0053384 | 0.064497 | 0.0032856 | -0.0018756 | 0.0069425 | 0.0010554 | 0.06467 | 0.064019 | -0.0066351 | -0.0078783 | 121.0648 | -0.018311 | 3.4058 | 0.059509 | 121.4676 | -0.09613 | -0.20599 | -0.004578 | 0.15564 | -0.16022 | 121.3577 | 121.3852 | -0.10071 | -0.12817 | 0.032044 | -0.07782 | 0.10071 | 0.10986 | 0.18768 | 0.2655 | -0.30212 | 0.027466 | 0 | -0.009155 | 0.1236 | -0.032043 | -0.032043 | 0.018311 | 121.5958 | 121.1929 | 3.5339 | -121.5729 | 121.4859 | 121.5134 | 0.28381 | -121.4951
786.4688 | 121.5271 | -0.13275 | 121.3715 | 0.0066373 | 0.0068916 | 0.069925 | 0.0053384 | 0.063643 | 8.1158e-05 | -0.0042254 | 0.0069425 | -0.00044004 | 0.064884 | 0.064232 | -0.0089849 | -0.0061695 | 121.0052 | -0.022888 | 3.3783 | 0.004578 | 121.4539 | -0.09613 | -0.20142 | -0.091553 | 0.10071 | -0.17853 | 121.3669 | 121.4172 | -0.11444 | -0.15564 | 0.036621 | -0.068665 | 0.082397 | 0.10986 | 0.13733 | 0.20599 | -0.36621 | 0.01831 | -0.022889 | -0.004578 | 0.041198 | -0.045777 | -0.022888 | 0.045776 | 121.5866 | 121.138 | 3.511 | -121.5729 | 121.4996 | 121.55 | 0.23346 | -121.5271
788.1406 | 121.5179 | -0.13733 | 121.3852 | 0.0066373 | 0.0051826 | 0.068003 | 0.0070474 | 0.060652 | 0.00029476 | -0.0014484 | 0.0069425 | 0.00062796 | 0.064457 | 0.065514 | -0.0085577 | -0.0078783 | 121.0739 | 0.027466 | 3.4561 | 0.068665 | 121.4493 | -0.09613 | -0.19226 | 0.013733 | 0.16022 | -0.14191 | 121.3577 | 121.3898 | -0.09613 | -0.1236 | 0.041199 | -0.054932 | 0.064087 | 0.16479 | 0.20599 | 0.26093 | -0.31128 | 0.041199 | 0.013733 | -0.027466 | 0.15106 | -0.004578 | -0.018311 | 0.004578 | 121.5866 | 121.2112 | 3.5934 | -121.5775 | 121.4951 | 121.5271 | 0.29755 | -121.5088
789.8125 | 121.463 | -0.16937 | 121.4172 | 0.0066373 | 0.0073188 | 0.071848 | 0.0025612 | 0.063856 | 0.00029476 | -0.0023028 | 0.014572 | 0.0021234 | 0.063602 | 0.0653 | -0.0068487 | -0.0048877 | 121.0007 | -0.059509 | 3.3417 | 0.013733 | 121.4859 | -0.082397 | -0.20142 | -0.068665 | 0.054932 | -0.20142 | 121.3715 | 121.3806 | -0.09613 | -0.14648 | 0.086976 | -0.032043 | 0.068665 | 0.10986 | 0.18311 | 0.21515 | -0.41657 | 0.073243 | 0.022889 | -0.045776 | 0.10071 | -0.032043 | -0.054932 | -0.036621 | 121.6553 | 121.17 | 3.511 | -121.6187 | 121.5408 | 121.55 | 0.22431 | -121.5637
791.5312 | 121.4767 | -0.15106 | 121.3943 | -0.00099167 | 0.0088142 | 0.074198 | 0.0019204 | 0.062361 | -0.00034604 | -0.0012346 | -0.00068649 | -0.00065364 | 0.061252 | 0.062096 | -0.0081305 | -0.0040331 | 121.0098 | -0.013733 | 3.3875 | 0.032043 | 121.463 | -0.059509 | -0.18768 | -0.004578 | 0.1236 | -0.10071 | 121.3348 | 121.3669 | -0.082397 | -0.1236 | 0.091553 | -0.036621 | 0.068665 | 0.13733 | 0.18311 | 0.21973 | -0.38452 | 0.068665 | 0.027466 | -0.059509 | 0.14648 | 0.050354 | 0.022888 | -0.027466 | 121.6141 | 121.1609 | 3.5385 | -121.582 | 121.4859 | 121.5179 | 0.27466 | -121.5179
793.2031 | 121.4539 | -0.17853 | 121.3943 | 0.0066373 | 0.0053962 | 0.071421 | 0.002775 | 0.063215 | 0.0026446 | -0.0029436 | 0.014572 | 0.0031916 | 0.06232 | 0.064019 | -0.0089849 | -0.0053149 | 121.0739 | 0.009155 | 3.447 | 0.059509 | 121.4493 | -0.086975 | -0.21057 | -0.027466 | 0.11902 | -0.16479 | 121.3577 | 121.3989 | -0.10986 | -0.14648 | 0.091553 | -0.032043 | 0.054932 | 0.18768 | 0.23804 | 0.27008 | -0.32043 | 0.068665 | 0.032044 | -0.036621 | 0.15106 | 0.013733 | -0.018311 | 0.004578 | 121.6278 | 121.2524 | 3.6255 | -121.6049 | 121.5363 | 121.5775 | 0.29755 | -121.5408
794.9062 | 121.5088 | -0.11444 | 121.3577 | -0.00099167 | 0.0066778 | 0.07313 | 0.0070474 | 0.06407 | -0.0050458 | -0.0057208 | 0.0069425 | -0.0027898 | 0.063816 | 0.063591 | -0.011762 | -0.0072375 | 121.106 | 0.11444 | 3.5156 | 0.10986 | 121.4218 | -0.054932 | -0.16937 | 0.027466 | 0.25177 | -0.022888 | 121.3165 | 121.376 | -0.082397 | -0.11902 | 0.059509 | -0.054932 | 0.064087 | 0.22888 | 0.2243 | 0.27924 | -0.25177 | 0.032044 | -0.004578 | -0.041199 | 0.14191 | 0.091553 | 0.096131 | 0.018311 | 121.5363 | 121.2204 | 3.6301 | -121.5271 | 121.431 | 121.4905 | 0.36621 | -121.4767
796.5781 | 121.4813 | -0.13733 | 121.3898 | 0.0066373 | 0.011164 | 0.069712 | 0.0044838 | 0.062147 | -0.0018414 | -0.0020892 | -0.00068649 | -0.00044004 | 0.061466 | 0.062737 | -0.0066351 | -0.0078783 | 121.1014 | 0.050354 | 3.4607 | 0.09613 | 121.4264 | -0.064087 | -0.15564 | 0.041199 | 0.16937 | -0.059509 | 121.3257 | 121.3669 | -0.059509 | -0.09613 | 0.073242 | -0.018311 | 0.036621 | 0.18768 | 0.23346 | 0.25177 | -0.28839 | 0.07782 | 0.041199 | -0.064087 | 0.17853 | 0.07782 | 0.036621 | -0.022889 | 121.5637 | 121.2387 | 3.598 | -121.5454 | 121.463 | 121.5042 | 0.3067 | -121.4859
798.2812 | 121.5637 | -0.10986 | 121.3806 | -0.0086212 | 0.011591 | 0.072702 | 0.0087564 | 0.062361 | -0.007182 | -0.004439 | 0.014572 | -0.0036444 | 0.063602 | 0.062096 | -0.011976 | -0.0061695 | 121.0922 | 0.045776 | 3.4836 | 0.10071 | 121.4447 | -0.045776 | -0.17395 | 0.018311 | 0.20599 | -0.032043 | 121.3211 | 121.3898 | -0.068665 | -0.09613 | 0.064087 | -0.064087 | 0.064087 | 0.15564 | 0.21057 | 0.27466 | -0.28839 | 0.041198 | 0.013733 | -0.059509 | 0.12817 | 0.07782 | 0.064087 | 0.009156 | 121.5546 | 121.2021 | 3.5934 | -121.5546 | 121.431 | 121.4996 | 0.31586 | -121.4767
799.9531 | 121.5729 | -0.1236 | 121.3715 | 0.0066373 | 0.0039008 | 0.070566 | 0.0070474 | 0.061079 | 0.0020038 | -0.0042254 | 0.014572 | 0.001269 | 0.062748 | 0.063378 | -0.011121 | -0.0087329 | 121.0464 | -0.068665 | 3.4287 | 0.036621 | 121.4767 | -0.082397 | -0.1831 | -0.050354 | 0.10986 | -0.16479 | 121.3989 | 121.4081 | -0.10529 | -0.14191 | 0.041199 | -0.059509 | 0.10529 | 0.054931 | 0.16022 | 0.21973 | -0.32501 | 0.01831 | -0.018311 | 0.027466 | 0.073242 | -0.041199 | -0.022888 | 0.036621 | 121.6003 | 121.17 | 3.5522 | -121.5546 | 121.5225 | 121.5317 | 0.23346 | -121.5134
801.625 | 121.463 | -0.17395 | 121.4172 | -0.00099167 | 0.0051826 | 0.06608 | 0.0046976 | 0.063643 | 0.002431 | -0.0035846 | 0.0069425 | 0.001269 | 0.064243 | 0.0653 | -0.0091985 | -0.0083057 | 121.0098 | -0.086975 | 3.4103 | 0.013733 | 121.4951 | -0.082397 | -0.20599 | -0.059509 | 0.013733 | -0.19226 | 121.3806 | 121.4081 | -0.091553 | -0.14191 | 0.091553 | -0.032044 | 0.07782 | 0.086975 | 0.18768 | 0.21973 | -0.40741 | 0.082397 | 0.032043 | -0.036621 | 0.11444 | -0.018311 | -0.050354 | -0.009155 | 121.669 | 121.1838 | 3.5843 | -121.6232 | 121.5546 | 121.582 | 0.18768 | -121.5591
803.2969 | 121.4401 | -0.16479 | 121.4035 | 0.0066373 | 0.0081732 | 0.072062 | 0.0012796 | 0.06407 | 0.003072 | -0.0014484 | 0.022202 | 0.0021234 | 0.065311 | 0.063591 | -0.0062079 | -0.0051013 | 121.019 | -0.07782 | 3.4058 | 0.009155 | 121.4767 | -0.082397 | -0.20142 | -0.068665 | 0.036621 | -0.2243 | 121.3669 | 121.4035 | -0.10071 | -0.13733 | 0.082398 | -0.036621 | 0.073243 | 0.086975 | 0.17395 | 0.21057 | -0.38452 | 0.064087 | 0.027466 | -0.036621 | 0.09613 | -0.059509 | -0.086975 | 0 | 121.6415 | 121.1838 | 3.5706 | -121.6049 | 121.5317 | 121.5683 | 0.20142 | -121.5408
804.9844 | 121.5683 | -0.12817 | 121.3623 | 0.0066373 | 0.004328 | 0.070139 | 0.0034158 | 0.063002 | -0.00013244 | -0.0023028 | 0.0069425 | 0.0019098 | 0.062961 | 0.063164 | -0.0077033 | -0.0053149 | 121.0373 | -0.027466 | 3.479 | 0.059509 | 121.4905 | -0.073242 | -0.21057 | -0.022888 | 0.13733 | -0.14191 | 121.3486 | 121.4264 | -0.09613 | -0.14191 | 0.054932 | -0.082397 | 0.12817 | 0.10071 | 0.18768 | 0.27008 | -0.32501 | 0.032044 | -0.013733 | -0.013733 | 0.10529 | -0.013733 | 0 | 0.064087 | 121.6187 | 121.1655 | 3.6072 | -121.5729 | 121.4767 | 121.5546 | 0.2655 | -121.5042
806.6562 | 121.431 | -0.14648 | 121.4172 | 0.0066373 | 0.0071052 | 0.069712 | 0.0053384 | 0.063429 | -0.00034604 | -0.0018756 | 0.014572 | 0.0019098 | 0.064029 | 0.064446 | -0.0064215 | -0.0036059 | 120.9915 | -0.07782 | 3.4103 | 0.013733 | 121.4813 | -0.09613 | -0.21057 | -0.086975 | 0.032043 | -0.19684 | 121.3898 | 121.4355 | -0.09613 | -0.13733 | 0.050354 | -0.064087 | 0.064087 | 0.068664 | 0.16022 | 0.2243 | -0.42572 | 0.050354 | 0.009155 | -0.027465 | 0.059509 | -0.050354 | -0.059509 | 0.018311 | 121.6278 | 121.138 | 3.5568 | -121.6278 | 121.5363 | 121.582 | 0.17853 | -121.5546
808.3438 | 121.5546 | -0.10986 | 121.3806 | 0.0066373 | 0.0036872 | 0.069712 | 0.00897 | 0.061934 | 0.00050836 | -0.0023028 | 0.0069425 | 0.0025508 | 0.064457 | 0.065728 | -0.0083441 | -0.0048877 | 121.0556 | 0.013733 | 3.511 | 0.068665 | 121.4584 | -0.086975 | -0.18768 | -0.018311 | 0.16022 | -0.13733 | 121.3531 | 121.4035 | -0.10071 | -0.13733 | 0.022888 | -0.07782 | 0.07782 | 0.1236 | 0.17853 | 0.25635 | -0.32501 | 0.009155 | -0.027466 | -0.027466 | 0.091552 | -0.027466 | 0 | 0.022888 | 121.5683 | 121.1655 | 3.6209 | -121.5683 | 121.463 | 121.5134 | 0.27008 | -121.5179
810.0312 | 121.5134 | -0.14648 | 121.3806 | 0.0066373 | 0.0064642 | 0.071634 | 0.0085428 | 0.060865 | -0.0044048 | -0.0035846 | 0.0069425 | 0.00041436 | 0.064243 | 0.065087 | -0.012403 | -0.0068103 | 121.0052 | -0.004578 | 3.4927 | 0.036621 | 121.4539 | -0.082397 | -0.19226 | -0.09613 | 0.11444 | -0.16937 | 121.3669 | 121.431 | -0.10071 | -0.14191 | 0.064087 | -0.045777 | 0.073242 | 0.14191 | 0.18311 | 0.22888 | -0.37537 | 0.045776 | 0.004577 | -0.013733 | 0.050354 | -0.022889 | -0.027466 | 0.050354 | 121.6003 | 121.1517 | 3.6392 | -121.5729 | 121.5134 | 121.5775 | 0.26093 | -121.5225
811.7188 | 121.4447 | -0.17853 | 121.4401 | 0.014267 | 0.002619 | 0.064157 | 0.0070474 | 0.061934 | -0.00013244 | -0.001662 | 0.0069425 | 0.00062796 | 0.065952 | 0.066368 | -0.0089849 | -0.0061695 | 121.019 | -0.07782 | 3.4653 | 0.022888 | 121.4722 | -0.082397 | -0.19684 | -0.068665 | 0.050354 | -0.21057 | 121.3852 | 121.4355 | -0.11444 | -0.16022 | 0.096131 | -0.01831 | 0.032043 | 0.10071 | 0.20142 | 0.21973 | -0.42114 | 0.064087 | 0.018311 | -0.054932 | 0.10986 | -0.032043 | -0.050354 | -0.004578 | 121.6507 | 121.1975 | 3.6438 | -121.637 | 121.5637 | 121.6141 | 0.22888 | -121.6003
813.4688 | 121.4401 | -0.16022 | 121.4218 | -0.00099167 | 0.006037 | 0.069498 | 0.002775 | 0.063215 | 0.0020038 | -0.003371 | 0.014572 | 0.0025508 | 0.063175 | 0.065514 | -0.0077033 | -0.0057421 | 121.0236 | -0.045776 | 3.4744 | 0.027466 | 121.4676 | -0.07782 | -0.18768 | -0.068665 | 0.059509 | -0.20599 | 121.3852 | 121.4218 | -0.10529 | -0.1236 | 0.082397 | -0.027466 | 0.045776 | 0.11444 | 0.18768 | 0.21515 | -0.39825 | 0.054931 | 0.036621 | -0.036621 | 0.091552 | -0.045777 | -0.082398 | 0 | 121.6278 | 121.1838 | 3.6346 | -121.6095 | 121.5454 | 121.582 | 0.21973 | -121.5454
815.2188 | 121.5729 | -0.11902 | 121.3898 | 0.014267 | 0.0034736 | 0.070353 | 0.0049112 | 0.063215 | 8.1158e-05 | -0.0012346 | 0.014572 | 0.001269 | 0.063816 | 0.062737 | -0.0070623 | -0.0044605 | 121.051 | 0.018311 | 3.5248 | 0.054932 | 121.4722 | -0.086975 | -0.19226 | -0.022888 | 0.16479 | -0.13733 | 121.376 | 121.3989 | -0.10529 | -0.13733 | 0.032044 | -0.073242 | 0.082397 | 0.13733 | 0.17395 | 0.24719 | -0.33875 | 0.013733 | -0.01831 | -0.013733 | 0.096131 | -0.01831 | 0 | 0.009155 | 121.5912 | 121.17 | 3.6438 | -121.582 | 121.4951 | 121.5179 | 0.28381 | -121.5271
816.9219 | 121.5042 | -0.14191 | 121.4081 | -0.00099167 | 0.0086006 | 0.071421 | 0.0049112 | 0.063215 | -0.00098684 | -0.004439 | -0.00068649 | 0.0021234 | 0.063602 | 0.064446 | -0.0089849 | -0.0036059 | 121.0098 | -0.041199 | 3.4561 | 0.018311 | 121.4493 | -0.086975 | -0.20599 | -0.041199 | 0.082397 | -0.12817 | 121.3852 | 121.4081 | -0.082397 | -0.11902 | 0.054932 | -0.064087 | 0.041199 | 0.10071 | 0.16022 | 0.22431 | -0.39825 | 0.05951 | 0.022888 | -0.022888 | 0.10071 | 0.013733 | -0.009155 | 0 | 121.5912 | 121.1517 | 3.598 | -121.6141 | 121.5271 | 121.55 | 0.2243 | -121.5271
818.6719 | 121.5179 | -0.14191 | 121.3715 | -0.00099167 | 0.0062506 | 0.070353 | 0.0083292 | 0.065565 | -0.0069684 | -0.0037982 | -0.00068649 | -0.0025762 | 0.065525 | 0.06295 | -0.014753 | -0.0063831 | 121.0739 | 0.091553 | 3.598 | 0.10986 | 121.4401 | -0.068665 | -0.16479 | -0.013733 | 0.19684 | -0.086975 | 121.3669 | 121.3989 | -0.086975 | -0.11902 | 0.073242 | -0.022888 | 0.068665 | 0.23346 | 0.25177 | 0.27466 | -0.29755 | 0.054932 | 0.022888 | -0.004578 | 0.12817 | 0.054932 | 0.032044 | 0.027466 | 121.582 | 121.2158 | 3.7399 | -121.5363 | 121.5088 | 121.5408 | 0.33875 | -121.4905
820.3594 | 121.4813 | -0.15106 | 121.4264 | 0.0066373 | 0.0092414 | 0.069712 | 0.0044838 | 0.062361 | -0.00055964 | -0.0031574 | 0.0069425 | -0.0015082 | 0.06467 | 0.061455 | -0.0077033 | -0.0068103 | 121.0876 | 0.059509 | 3.566 | 0.10986 | 121.4447 | -0.041199 | -0.16022 | 0.032043 | 0.15106 | -0.059509 | 121.3165 | 121.3806 | -0.064087 | -0.10986 | 0.10986 | -0.009155 | 0.01831 | 0.21057 | 0.26093 | 0.27008 | -0.33875 | 0.086975 | 0.041199 | -0.10986 | 0.18311 | 0.091553 | 0.050354 | -0.045777 | 121.5958 | 121.2387 | 3.717 | -121.5866 | 121.4676 | 121.5317 | 0.30212 | -121.5363
822.1094 | 121.5591 | -0.14191 | 121.4127 | -0.0086212 | 0.0028326 | 0.068857 | 0.0061928 | 0.060225 | -0.0018414 | -0.00508 | 0.014572 | -0.0019354 | 0.06467 | 0.065941 | -0.010053 | -0.0065967 | 121.0236 | -0.041199 | 3.4973 | 0.032043 | 121.4996 | -0.091553 | -0.20599 | -0.10529 | 0.082397 | -0.18768 | 121.3943 | 121.4447 | -0.10986 | -0.14191 | 0.050354 | -0.064087 | 0.086975 | 0.10071 | 0.17395 | 0.23804 | -0.3891 | 0.032044 | 0 | -0.018311 | 0.036621 | -0.045776 | -0.045776 | 0.032043 | 121.6415 | 121.1655 | 3.6392 | -121.6187 | 121.5363 | 121.5866 | 0.2243 | -121.5546
823.7812 | 121.5179 | -0.11444 | 121.4035 | 0.0066373 | 0.0075324 | 0.070139 | 0.0070474 | 0.061506 | -0.00034604 | -0.00508 | 0.0069425 | -0.00022644 | 0.065311 | 0.064019 | -0.0098395 | -0.0074511 | 121.0098 | -0.032043 | 3.5065 | 0.032043 | 121.4813 | -0.07782 | -0.19684 | -0.091553 | 0.10986 | -0.16937 | 121.4035 | 121.4218 | -0.10986 | -0.16022 | 0.036621 | -0.082397 | 0.07782 | 0.082398 | 0.14648 | 0.22888 | -0.39368 | 0.004578 | -0.045776 | 0 | 0.022888 | -0.054932 | -0.009156 | 0.018311 | 121.5958 | 121.1243 | 3.6209 | -121.6003 | 121.5179 | 121.5363 | 0.2243 | -121.5637
825.5312 | 121.5225 | -0.13733 | 121.3806 | 0.0066373 | 0.0088142 | 0.070566 | 0.0068338 | 0.062574 | -0.0022686 | -0.00508 | 0.0069425 | -0.0030034 | 0.06467 | 0.063591 | -0.011335 | -0.0074511 | 121.1014 | 0.091553 | 3.6072 | 0.09613 | 121.4401 | -0.036621 | -0.14648 | 0.018311 | 0.2243 | -0.068665 | 121.3348 | 121.3898 | -0.064087 | -0.11902 | 0.10071 | -0.009155 | 0.05951 | 0.22888 | 0.23346 | 0.24261 | -0.27924 | 0.073242 | 0.01831 | -0.045776 | 0.15564 | 0.068664 | 0.050354 | 0.009156 | 121.5775 | 121.2387 | 3.7445 | -121.5271 | 121.4722 | 121.5271 | 0.36163 | -121.4996
827.2188 | 121.582 | -0.11902 | 121.3898 | 0.0066373 | 0.0064642 | 0.071421 | 0.0057656 | 0.061079 | -0.0056866 | -0.0040118 | 0.022202 | -0.0010808 | 0.06232 | 0.063591 | -0.010053 | -0.0048877 | 121.1243 | 0.10529 | 3.598 | 0.10071 | 121.4722 | -0.036621 | -0.15564 | 0.041199 | 0.22888 | -0.022888 | 121.312 | 121.3806 | -0.068665 | -0.09613 | 0.082398 | -0.036621 | 0.082397 | 0.22431 | 0.21973 | 0.25635 | -0.2655 | 0.050354 | 0.022889 | -0.07782 | 0.16022 | 0.096131 | 0.073242 | -0.009156 | 121.5912 | 121.2433 | 3.717 | -121.5454 | 121.431 | 121.4996 | 0.3479 | -121.4859
828.8906 | 121.5179 | -0.12817 | 121.4172 | 0.0066373 | 0.0062506 | 0.07078 | 0.0049112 | 0.063429 | -0.00013244 | -0.006148 | 0.0069425 | -0.0017218 | 0.063388 | 0.065087 | -0.010908 | -0.0080921 | 121.0464 | -0.009155 | 3.5248 | 0.022888 | 121.4905 | -0.10071 | -0.21057 | -0.059509 | 0.10986 | -0.16479 | 121.4127 | 121.4172 | -0.10986 | -0.15106 | 0.027466 | -0.082397 | 0.073243 | 0.11902 | 0.15106 | 0.23346 | -0.37079 | 0.018311 | -0.022888 | -0.004577 | 0.068665 | -0.036621 | -0.013733 | 0 | 121.6187 | 121.1746 | 3.653 | -121.6278 | 121.5408 | 121.5454 | 0.23804 | -121.5683
830.625 | 121.5317 | -0.13275 | 121.4081 | 0.021896 | 0.0079596 | 0.071207 | 0.0064066 | 0.062147 | -0.00077324 | -0.0055072 | 0.014572 | -0.0019354 | 0.064457 | 0.064873 | -0.010053 | -0.0078783 | 121.1105 | 0.068665 | 3.6163 | 0.11444 | 121.4767 | -0.073242 | -0.16022 | -0.013733 | 0.18768 | -0.10529 | 121.3531 | 121.3989 | -0.10529 | -0.10529 | 0.059509 | -0.027466 | 0.068665 | 0.20142 | 0.24719 | 0.27466 | -0.29755 | 0.027465 | 0.027465 | -0.054932 | 0.11902 | 0.027465 | 0 | -0.009155 | 121.6095 | 121.2433 | 3.7491 | -121.5683 | 121.4859 | 121.5317 | 0.32043 | -121.5134
832.2969 | 121.4401 | -0.15106 | 121.431 | -0.00099167 | 0.013727 | 0.072062 | -2.152e-06 | 0.06172 | -0.00098684 | -0.0042254 | 0.0069425 | -0.0010808 | 0.060184 | 0.064659 | -0.0070623 | -0.0070239 | 121.1472 | 0.082397 | 3.6072 | 0.082397 | 121.4355 | -0.059509 | -0.16022 | 0.045776 | 0.14648 | -0.064087 | 121.3348 | 121.3806 | -0.064087 | -0.10071 | 0.091553 | -0.009155 | 0.004578 | 0.23346 | 0.23346 | 0.24261 | -0.28381 | 0.086975 | 0.050354 | -0.09613 | 0.19684 | 0.086975 | 0.036621 | -0.050354 | 121.5866 | 121.2982 | 3.7582 | -121.5912 | 121.4859 | 121.5317 | 0.29755 | -121.5317
834.0312 | 121.4676 | -0.16022 | 121.4035 | 0.0066373 | 0.013087 | 0.073343 | 0.0029886 | 0.061934 | -0.0031232 | -0.0063616 | -0.00068649 | -0.0019354 | 0.060398 | 0.06231 | -0.0087713 | -0.0068103 | 121.0648 | 0.027466 | 3.5706 | 0.064087 | 121.463 | -0.054932 | -0.17395 | -0.018311 | 0.11902 | -0.09613 | 121.3623 | 121.4218 | -0.068665 | -0.10529 | 0.10528 | -0.013733 | 0.05951 | 0.18768 | 0.2243 | 0.23804 | -0.33875 | 0.091552 | 0.054931 | -0.041198 | 0.14191 | 0.064087 | 0.009156 | 0.018311 | 121.6232 | 121.225 | 3.7308 | -121.5775 | 121.5225 | 121.582 | 0.27924 | -121.5088
835.7031 | 121.5408 | -0.11902 | 121.4127 | 0.0066373 | 0.0071052 | 0.073557 | 0.0053384 | 0.062574 | -0.0014142 | -0.0031574 | 0.014572 | 0.00020076 | 0.063816 | 0.062523 | -0.0091985 | -0.0072375 | 121.1517 | 0.10071 | 3.6713 | 0.11902 | 121.4447 | -0.050354 | -0.15564 | 0.041199 | 0.21973 | -0.045776 | 121.3394 | 121.4127 | -0.059509 | -0.11902 | 0.068665 | -0.036621 | 0.032043 | 0.21973 | 0.23804 | 0.27466 | -0.26093 | 0.05951 | 0 | -0.073242 | 0.16022 | 0.073243 | 0.073243 | 0 | 121.5637 | 121.2708 | 3.7903 | -121.5683 | 121.4584 | 121.5317 | 0.33875 | -121.5317
837.4375 | 121.5225 | -0.1236 | 121.3989 | 0.0066373 | 0.0064642 | 0.072489 | 0.0070474 | 0.06407 | -0.00055964 | -0.0042254 | 0.0069425 | 0.00084176 | 0.063175 | 0.064232 | -0.0085577 | -0.0065967 | 121.0785 | -0.004578 | 3.5843 | 0.032043 | 121.4767 | -0.091553 | -0.20142 | -0.050354 | 0.12817 | -0.15106 | 121.3989 | 121.4264 | -0.10529 | -0.13733 | 0.032043 | -0.07782 | 0.07782 | 0.11902 | 0.15564 | 0.23346 | -0.32044 | 0.01831 | -0.013733 | 0 | 0.073242 | -0.027466 | -0.013733 | 0.027466 | 121.6003 | 121.2021 | 3.7079 | -121.6003 | 121.5225 | 121.55 | 0.25177 | -121.5363
839.1094 | 121.4996 | -0.16479 | 121.4081 | 0.014267 | 0.0045416 | 0.069712 | 0.002775 | 0.064711 | 0.00649 | -0.0020892 | 0.022202 | 0.0019098 | 0.065097 | 0.066368 | -0.0074897 | -0.0074511 | 121.1243 | 0.027466 | 3.6255 | 0.054932 | 121.4722 | -0.068665 | -0.19226 | 0 | 0.12817 | -0.16022 | 121.376 | 121.4355 | -0.10071 | -0.13275 | 0.09613 | -0.027466 | 0.064087 | 0.19226 | 0.21973 | 0.24719 | -0.28381 | 0.064087 | 0.032044 | -0.032043 | 0.16479 | 0.004578 | -0.027466 | 0.027466 | 121.637 | 121.2891 | 3.7903 | -121.6003 | 121.5408 | 121.6003 | 0.29297 | -121.5408
840.8438 | 121.4905 | -0.16022 | 121.4081 | 0.0066373 | 0.007746 | 0.070139 | 0.0059792 | 0.062574 | 0.00029476 | -0.0012346 | -0.00068649 | 0.00062796 | 0.062961 | 0.064873 | -0.0049261 | -0.0057421 | 121.0464 | -0.027466 | 3.5294 | 0.032043 | 121.4767 | -0.09613 | -0.21057 | -0.022888 | 0.059509 | -0.14648 | 121.3806 | 121.4127 | -0.073242 | -0.13275 | 0.064087 | -0.050354 | 0.068665 | 0.13275 | 0.19226 | 0.24261 | -0.36163 | 0.086975 | 0.027466 | -0.027466 | 0.13733 | 0.013733 | -0.013733 | 0.004578 | 121.637 | 121.2067 | 3.6896 | -121.6187 | 121.5408 | 121.5729 | 0.21973 | -121.5408
842.5938 | 121.4264 | -0.13275 | 121.4539 | 0.014267 | 0.0092414 | 0.070993 | 0.0046976 | 0.06407 | -0.0022686 | -0.0031574 | 0.014572 | -0.0015082 | 0.062748 | 0.063805 | -0.011549 | -0.0029651 | 121.1151 | 0.10529 | 3.6484 | 0.11902 | 121.463 | -0.036621 | -0.14648 | 0.041199 | 0.16479 | -0.059509 | 121.3303 | 121.3852 | -0.073242 | -0.10529 | 0.09613 | -0.013733 | 0.009156 | 0.23804 | 0.25177 | 0.2655 | -0.33875 | 0.059509 | 0.027465 | -0.1236 | 0.17395 | 0.073242 | 0.045777 | -0.068664 | 121.5958 | 121.2479 | 3.7811 | -121.6003 | 121.463 | 121.5179 | 0.29755 | -121.5591
844.2812 | 121.5683 | -0.10986 | 121.3898 | 0.0066373 | 0.010309 | 0.07313 | 0.0051248 | 0.062147 | -0.0056866 | -0.00273 | 0.014572 | 0.001269 | 0.06467 | 0.063591 | -0.013471 | -0.0065967 | 121.138 | 0.091553 | 3.653 | 0.10071 | 121.4264 | -0.064087 | -0.15564 | 0.050354 | 0.2243 | -0.022888 | 121.3577 | 121.3898 | -0.059509 | -0.10529 | 0.045776 | -0.045777 | 0.036621 | 0.20142 | 0.21057 | 0.25635 | -0.25177 | 0.050354 | 0.004577 | -0.032044 | 0.16022 | 0.086975 | 0.082398 | 0 | 121.5363 | 121.2479 | 3.7628 | -121.5454 | 121.4676 | 121.4996 | 0.33417 | -121.4951
846.0312 | 121.5729 | -0.10529 | 121.3806 | 0.0066373 | 0.010309 | 0.072916 | 0.0061928 | 0.063643 | -0.0056866 | -0.0040118 | 0.014572 | -0.00086724 | 0.062534 | 0.063805 | -0.011121 | -0.0053149 | 121.0968 | 0.068665 | 3.6209 | 0.09613 | 121.4676 | -0.059509 | -0.15106 | 0.022888 | 0.21057 | -0.041199 | 121.3577 | 121.4172 | -0.064087 | -0.10986 | 0.045777 | -0.045776 | 0.086975 | 0.17395 | 0.20142 | 0.24719 | -0.28381 | 0.041199 | -0.004577 | -0.022888 | 0.12817 | 0.064087 | 0.068664 | 0.036621 | 121.5729 | 121.2021 | 3.7262 | -121.5317 | 121.463 | 121.5225 | 0.31586 | -121.4905
847.7812 | 121.5729 | -0.10986 | 121.3715 | -0.0086212 | 0.010737 | 0.072275 | 0.005552 | 0.060652 | -0.0018414 | -0.0042254 | 0.014572 | -0.00086724 | 0.061893 | 0.063164 | -0.010908 | -0.0065967 | 121.1426 | 0.10071 | 3.6667 | 0.10529 | 121.4676 | -0.045776 | -0.16937 | 0.073242 | 0.24261 | -0.013733 | 121.3531 | 121.3806 | -0.054932 | -0.091553 | 0.064087 | -0.05951 | 0.09613 | 0.21057 | 0.21515 | 0.27466 | -0.22888 | 0.054931 | 0.01831 | -0.018311 | 0.18311 | 0.09613 | 0.07782 | 0.009155 | 121.5775 | 121.2524 | 3.7765 | -121.5408 | 121.463 | 121.4905 | 0.35248 | -121.463
849.5312 | 121.5958 | -0.09613 | 121.4081 | -0.00099167 | 0.011378 | 0.070993 | 0.0068338 | 0.063215 | -0.0029094 | -0.0037982 | 0.0069425 | 0.0019098 | 0.062961 | 0.063164 | -0.010908 | -0.0076647 | 121.1472 | 0.086975 | 3.6484 | 0.09613 | 121.4676 | -0.054932 | -0.17395 | 0.050354 | 0.21057 | -0.027466 | 121.3623 | 121.3898 | -0.059509 | -0.10071 | 0.041198 | -0.07782 | 0.059509 | 0.1831 | 0.19226 | 0.27008 | -0.26093 | 0.036621 | -0.004578 | -0.045776 | 0.14648 | 0.068664 | 0.073242 | -0.01831 | 121.5637 | 121.2433 | 3.7445 | -121.582 | 121.4584 | 121.4859 | 0.3067 | -121.5088
851.2188 | 121.4813 | -0.15564 | 121.4218 | 0.0066373 | 0.0079596 | 0.068644 | 0.0025612 | 0.062574 | 0.0049946 | -0.0059344 | 0.014572 | 0.0038324 | 0.064029 | 0.064446 | -0.0025763 | -0.0085193 | 121.138 | 0.018311 | 3.6346 | 0.054932 | 121.4951 | -0.09613 | -0.18768 | 0.004578 | 0.1236 | -0.16022 | 121.4081 | 121.4401 | -0.09613 | -0.1236 | 0.05951 | -0.032043 | 0.073242 | 0.17395 | 0.21057 | 0.24261 | -0.28381 | 0.05951 | 0.032044 | -0.013733 | 0.16022 | -0.004577 | -0.036621 | 0.018311 | 121.6507 | 121.2936 | 3.7903 | -121.6095 | 121.5637 | 121.5958 | 0.27924 | -121.5454
852.9062 | 121.5042 | -0.13275 | 121.4401 | 0.014267 | 0.010737 | 0.068857 | -0.00042935 | 0.063643 | -0.00034604 | -0.0014484 | 0.0069425 | 0.0010554 | 0.062107 | 0.063164 | -0.0053533 | -0.0059557 | 121.1472 | 0.082397 | 3.6438 | 0.10529 | 121.4676 | -0.036621 | -0.13275 | 0.059509 | 0.17853 | -0.064087 | 121.3531 | 121.4264 | -0.07782 | -0.091553 | 0.09613 | 0 | 0.027465 | 0.21515 | 0.23804 | 0.23804 | -0.29297 | 0.054931 | 0.041198 | -0.086976 | 0.19226 | 0.068664 | 0.027466 | -0.013733 | 121.6003 | 121.2799 | 3.7765 | -121.5729 | 121.4859 | 121.5591 | 0.31128 | -121.5317
854.6562 | 121.6003 | -0.13275 | 121.3943 | 0.0066373 | 0.0047552 | 0.071207 | 0.0040566 | 0.062147 | 0.0028584 | -0.004439 | -0.008316 | 0.0016962 | 0.062107 | 0.06295 | -0.0040717 | -0.0080921 | 121.0693 | -0.027466 | 3.5843 | 0.054932 | 121.4905 | -0.091553 | -0.20142 | -0.022888 | 0.14191 | -0.14648 | 121.3898 | 121.431 | -0.091553 | -0.13275 | 0.041198 | -0.068665 | 0.096131 | 0.10529 | 0.18768 | 0.25635 | -0.32501 | 0.041198 | 0 | -0.004577 | 0.10986 | -0.013733 | -0.013733 | 0.036621 | 121.6232 | 121.2021 | 3.717 | -121.5958 | 121.5225 | 121.5637 | 0.27466 | -121.5271
856.3281 | 121.5088 | -0.16022 | 121.4264 | 0.0066373 | 0.0083868 | 0.069071 | 0.0046976 | 0.063215 | 0.0020038 | -0.0029436 | 0.0069425 | 0.0019098 | 0.06467 | 0.064446 | -0.0083441 | -0.0053149 | 121.0464 | -0.045776 | 3.5522 | 0.027466 | 121.5042 | -0.07782 | -0.19684 | -0.045776 | 0.045776 | -0.17853 | 121.3898 | 121.4172 | -0.086975 | -0.11902 | 0.082397 | -0.036621 | 0.077819 | 0.11444 | 0.18768 | 0.2243 | -0.37994 | 0.073242 | 0.041198 | -0.036621 | 0.11444 | -0.018311 | -0.059509 | -0.009156 | 121.6644 | 121.2067 | 3.7125 | -121.6232 | 121.55 | 121.5775 | 0.20599 | -121.5454
858.0625 | 121.4951 | -0.14648 | 121.4035 | 0.014267 | 0.0096686 | 0.072702 | 0.003843 | 0.061079 | 0.0011494 | -0.0029436 | 0.0069425 | -0.0012946 | 0.063816 | 0.063164 | -0.0068487 | -0.0068103 | 121.1243 | 0.091553 | 3.6758 | 0.10071 | 121.4447 | -0.027466 | -0.14191 | 0.059509 | 0.18768 | -0.059509 | 121.3623 | 121.3943 | -0.059509 | -0.10529 | 0.11902 | 0.004577 | 0.041199 | 0.23804 | 0.24719 | 0.24262 | -0.27923 | 0.086975 | 0.041198 | -0.041198 | 0.20599 | 0.086975 | 0.045777 | -0.009155 | 121.5912 | 121.2708 | 3.8223 | -121.5454 | 121.5088 | 121.5408 | 0.33417 | -121.5088
859.7344 | 121.5866 | -0.10986 | 121.3898 | -0.00099167 | 0.011805 | 0.073557 | 0.0044838 | 0.065351 | -0.006541 | -0.00273 | 0.0069425 | -0.0036444 | 0.062107 | 0.063591 | -0.010694 | -0.0057421 | 121.1243 | 0.10071 | 3.6987 | 0.10071 | 121.4401 | -0.045776 | -0.16479 | 0.032043 | 0.2243 | -0.013733 | 121.344 | 121.3898 | -0.054932 | -0.086975 | 0.064087 | -0.054932 | 0.050354 | 0.21057 | 0.21057 | 0.2655 | -0.2655 | 0.054931 | 0.022888 | -0.045777 | 0.14191 | 0.09613 | 0.073242 | 0 | 121.55 | 121.2341 | 3.8086 | -121.5546 | 121.4539 | 121.4996 | 0.33417 | -121.4767
861.5 | 121.5637 | -0.10986 | 121.431 | 0.0066373 | 0.0039008 | 0.071421 | 0.002775 | 0.063429 | 0.0020038 | -0.0029436 | -0.00068649 | 0.0036188 | 0.061893 | 0.063164 | -0.0068487 | -0.0074511 | 121.1014 | 0.018311 | 3.6713 | 0.054932 | 121.4813 | -0.07782 | -0.21057 | 0.004578 | 0.16022 | -0.14191 | 121.4127 | 121.4584 | -0.091553 | -0.14191 | 0.032043 | -0.10071 | 0.050354 | 0.12817 | 0.16479 | 0.2655 | -0.32959 | 0.01831 | -0.032044 | -0.01831 | 0.11444 | -0.032044 | 0 | 0.027466 | 121.5912 | 121.2112 | 3.7811 | -121.6415 | 121.5225 | 121.5683 | 0.27008 | -121.5729
863.25 | 121.5637 | -0.11444 | 121.4127 | -0.00099167 | 0.007746 | 0.072916 | 0.0081154 | 0.061934 | -0.0041912 | -0.0031574 | 0.022202 | -0.0030034 | 0.063602 | 0.061028 | -0.0087713 | -0.0048877 | 121.1609 | 0.13733 | 3.7262 | 0.10529 | 121.4447 | -0.050354 | -0.14648 | 0.045776 | 0.23804 | -0.022888 | 121.3577 | 121.4218 | -0.054932 | -0.09613 | 0.064087 | -0.032043 | 0.032043 | 0.25177 | 0.21973 | 0.25177 | -0.25177 | 0.059509 | 0.018311 | -0.054932 | 0.16022 | 0.091553 | 0.073242 | 0.009155 | 121.5591 | 121.2753 | 3.8406 | -121.5591 | 121.4722 | 121.5363 | 0.35248 | -121.5088
864.9219 | 121.5958 | -0.11902 | 121.4218 | -0.00099167 | 0.0013374 | 0.069284 | 0.0061928 | 0.063429 | 0.0034992 | -0.0035846 | -0.00068649 | 0.0014826 | 0.066379 | 0.066368 | -0.0094123 | -0.0078783 | 121.0831 | -0.032043 | 3.6301 | 0.054932 | 121.5179 | -0.086975 | -0.20599 | -0.041199 | 0.13275 | -0.14191 | 121.4035 | 121.463 | -0.1236 | -0.14191 | 0.032044 | -0.086975 | 0.09613 | 0.086976 | 0.17395 | 0.26093 | -0.33875 | -0.004577 | -0.022888 | -0.018311 | 0.07782 | -0.022888 | 0 | 0.041199 | 121.637 | 121.2021 | 3.7491 | -121.6278 | 121.5225 | 121.582 | 0.25177 | -121.5637
866.6719 | 121.4584 | -0.12817 | 121.431 | 0.0066373 | 0.012018 | 0.070566 | 0.0029886 | 0.062574 | 0.00029476 | -0.0020892 | 0.0069425 | -0.0017218 | 0.062748 | 0.063378 | -0.0072759 | -0.0070239 | 121.1334 | 0.07782 | 3.717 | 0.1236 | 121.4493 | -0.036621 | -0.16022 | 0.068665 | 0.1831 | -0.041199 | 121.3531 | 121.3531 | -0.050354 | -0.082397 | 0.091553 | -0.032043 | 0.018311 | 0.20599 | 0.25177 | 0.28381 | -0.29755 | 0.07782 | 0.045777 | -0.07782 | 0.19684 | 0.086975 | 0.041198 | -0.07782 | 121.5775 | 121.2616 | 3.8452 | -121.5912 | 121.4813 | 121.4813 | 0.31128 | -121.5134
868.3594 | 121.5454 | -0.13733 | 121.3898 | 0.0066373 | 0.006037 | 0.072916 | 0.0061928 | 0.062788 | -0.0056866 | -0.0055072 | 0.014572 | -0.0012946 | 0.063388 | 0.063591 | -0.010694 | -0.0074511 | 121.138 | 0.10529 | 3.7491 | 0.10529 | 121.4493 | -0.050354 | -0.15106 | 0.041199 | 0.23346 | -0.045776 | 121.3531 | 121.4264 | -0.059509 | -0.11444 | 0.086975 | -0.013733 | 0.059509 | 0.24262 | 0.24262 | 0.25635 | -0.25177 | 0.07782 | 0.022888 | -0.036622 | 0.17853 | 0.091553 | 0.068665 | 0.036621 | 121.5866 | 121.2753 | 3.8864 | -121.5408 | 121.4905 | 121.5637 | 0.37079 | -121.5042
870.0938 | 121.5775 | -0.13733 | 121.4035 | 0.0066373 | 0.011164 | 0.072702 | 0.005552 | 0.064283 | -0.0039776 | -0.0057208 | 0.0069425 | -0.0017218 | 0.062748 | 0.064232 | -0.011121 | -0.0074511 | 121.1563 | 0.12817 | 3.7491 | 0.11902 | 121.4859 | -0.054932 | -0.15564 | 0.036621 | 0.24261 | -0.022888 | 121.3486 | 121.4081 | -0.050354 | -0.09613 | 0.082397 | -0.018311 | 0.082398 | 0.2655 | 0.25635 | 0.27466 | -0.24719 | 0.086975 | 0.041199 | -0.054931 | 0.17395 | 0.11444 | 0.073242 | 0.004578 | 121.6232 | 121.2936 | 3.8864 | -121.5591 | 121.4859 | 121.5454 | 0.37994 | -121.4996
871.8438 | 121.5088 | -0.14191 | 121.4584 | -0.0086212 | 0.0047552 | 0.068003 | 0.0032022 | 0.064283 | 0.0043536 | -0.0031574 | 0.014572 | 0.0034052 | 0.06232 | 0.0653 | -0.0064215 | -0.0095873 | 121.1609 | 0.013733 | 3.7079 | 0.054932 | 121.4905 | -0.073242 | -0.18768 | 0.004578 | 0.13275 | -0.15106 | 121.431 | 121.4493 | -0.082397 | -0.14191 | 0.068665 | -0.045776 | 0.032044 | 0.15564 | 0.19684 | 0.24261 | -0.29755 | 0.05951 | 0 | -0.027466 | 0.14649 | -0.009155 | -0.009155 | -0.009155 | 121.6324 | 121.3028 | 3.8498 | -121.6461 | 121.5729 | 121.5912 | 0.27466 | -121.6003
873.5938 | 121.463 | -0.17853 | 121.4218 | -0.0086212 | 0.010309 | 0.072275 | 0.005552 | 0.061506 | -0.0046184 | -0.00273 | -0.00068649 | -0.0025762 | 0.063388 | 0.064019 | -0.010694 | -0.0046741 | 121.1014 | 0.050354 | 3.7125 | 0.068665 | 121.4905 | -0.054932 | -0.15564 | -0.018311 | 0.13733 | -0.07782 | 121.3577 | 121.4035 | -0.07782 | -0.13275 | 0.1236 | 0.022888 | 0.068665 | 0.22888 | 0.24719 | 0.22431 | -0.32044 | 0.10071 | 0.045777 | -0.064087 | 0.16022 | 0.10071 | 0.054931 | -0.018311 | 121.669 | 121.2799 | 3.891 | -121.5775 | 121.5363 | 121.582 | 0.31586 | -121.5546
875.3281 | 121.463 | -0.15106 | 121.4447 | 0.014267 | 0.0079596 | 0.069712 | 0.002775 | 0.064924 | 0.0045674 | -0.0025164 | 0.0069425 | 0.0025508 | 0.062534 | 0.064446 | -0.0057807 | -0.0065967 | 121.0602 | -0.064087 | 3.6392 | 0.022888 | 121.4996 | -0.082397 | -0.20142 | -0.050354 | 0.036621 | -0.21057 | 121.4401 | 121.4767 | -0.086975 | -0.14191 | 0.068665 | -0.050354 | 0.054932 | 0.086975 | 0.17395 | 0.2243 | -0.38452 | 0.064087 | 0.009155 | -0.004577 | 0.10071 | -0.059509 | -0.068664 | 0.032044 | 121.6507 | 121.2112 | 3.7903 | -121.6461 | 121.5912 | 121.6278 | 0.18768 | -121.5866
877 | 121.6003 | -0.11444 | 121.3943 | 0.014267 | 0.010309 | 0.071634 | 0.0032022 | 0.065138 | -0.0069684 | -0.0055072 | -0.00068649 | -0.0032172 | 0.064243 | 0.06295 | -0.01283 | -0.0061695 | 121.138 | 0.10071 | 3.7262 | 0.10071 | 121.4722 | -0.041199 | -0.15564 | 0.032043 | 0.22888 | -0.013733 | 121.3486 | 121.431 | -0.059509 | -0.086975 | 0.073242 | -0.041199 | 0.07782 | 0.21515 | 0.21515 | 0.25635 | -0.25635 | 0.054932 | 0.027466 | -0.045776 | 0.14648 | 0.10071 | 0.073242 | 0.036621 | 121.5866 | 121.2524 | 3.8406 | -121.55 | 121.463 | 121.5454 | 0.34332 | -121.4813
878.75 | 121.5317 | -0.13733 | 121.4081 | -0.00099167 | 0.0062506 | 0.073771 | 0.0059792 | 0.065992 | 8.1158e-05 | -0.0046526 | -0.00068649 | -0.0012946 | 0.061679 | 0.062096 | -0.0098395 | -0.0065967 | 121.0876 | 0.054932 | 3.7033 | 0.068665 | 121.463 | -0.082397 | -0.19226 | -0.050354 | 0.14191 | -0.15564 | 121.4081 | 121.4493 | -0.09613 | -0.13275 | 0.054932 | -0.054932 | 0.054932 | 0.19226 | 0.20599 | 0.26093 | -0.32043 | 0.041199 | 0.004578 | 0 | 0.086975 | -0.018311 | -0.022889 | 0.041199 | 121.6003 | 121.225 | 3.8406 | -121.6003 | 121.5454 | 121.5866 | 0.27924 | -121.5408
880.4375 | 121.5866 | -0.09613 | 121.4081 | -0.00099167 | 0.0053962 | 0.072275 | 0.0057656 | 0.061934 | 0.0015766 | -0.001662 | 0.014572 | -0.00022644 | 0.062961 | 0.063805 | -0.0081305 | -0.0068103 | 121.0693 | -0.013733 | 3.6621 | 0.045776 | 121.5454 | -0.091553 | -0.1831 | -0.045776 | 0.14191 | -0.15106 | 121.4127 | 121.4127 | -0.09613 | -0.14191 | 0.004577 | -0.086975 | 0.13733 | 0.082397 | 0.14191 | 0.22888 | -0.33874 | 0 | -0.045777 | 0.004578 | 0.050354 | -0.054932 | -0.009155 | 0.004578 | 121.6415 | 121.1655 | 3.7582 | -121.5912 | 121.5088 | 121.5088 | 0.23804 | -121.55
882.1875 | 121.4813 | -0.14648 | 121.4493 | 0.014267 | 0.013727 | 0.073984 | 0.007261 | 0.062788 | -0.0041912 | -0.0052936 | 0.014572 | -0.0010808 | 0.062961 | 0.062096 | -0.011335 | -0.0070239 | 121.0968 | 0.032043 | 3.6758 | 0.059509 | 121.463 | -0.045776 | -0.14648 | -0.022888 | 0.13733 | -0.091553 | 121.376 | 121.4264 | -0.082397 | -0.10986 | 0.10071 | 0 | 0.013733 | 0.17853 | 0.20599 | 0.20599 | -0.35248 | 0.064087 | 0.036621 | -0.073242 | 0.1236 | 0.054931 | 0.01831 | -0.022888 | 121.6095 | 121.2433 | 3.8223 | -121.5958 | 121.5225 | 121.5729 | 0.28381 | -121.5591
883.9219 | 121.5179 | -0.13733 | 121.4172 | 0.014267 | 0.010096 | 0.074198 | 0.0044838 | 0.061506 | -0.0050458 | -0.0037982 | 0.0069425 | -0.0015082 | 0.062748 | 0.063805 | -0.010267 | -0.0065967 | 121.0785 | 0.027466 | 3.6804 | 0.073242 | 121.4905 | -0.045776 | -0.16022 | -0.013733 | 0.15106 | -0.082397 | 121.3715 | 121.4172 | -0.068665 | -0.11444 | 0.091553 | -0.022888 | 0.073243 | 0.16479 | 0.21057 | 0.23346 | -0.33875 | 0.068664 | 0.022888 | -0.045776 | 0.1236 | 0.054932 | 0.032044 | 0 | 121.6278 | 121.2158 | 3.8177 | -121.5775 | 121.5088 | 121.5546 | 0.28839 | -121.5317
885.6562 | 121.5134 | -0.14191 | 121.4264 | 0.0066373 | 0.0090278 | 0.073343 | 0.0040566 | 0.062361 | 0.00093576 | -0.0063616 | -0.00068649 | 0.001269 | 0.064029 | 0.064232 | -0.0051397 | -0.0072375 | 121.1105 | 0 | 3.6942 | 0.045776 | 121.4859 | -0.045776 | -0.17395 | 0.036621 | 0.13733 | -0.082397 | 121.3898 | 121.3989 | -0.050354 | -0.10986 | 0.096131 | -0.032043 | 0.059509 | 0.14191 | 0.18768 | 0.21973 | -0.31586 | 0.091553 | 0.032044 | -0.036621 | 0.17853 | 0.05951 | 0.027466 | -0.027466 | 121.6278 | 121.2524 | 3.8361 | -121.6003 | 121.5317 | 121.5408 | 0.27924 | -121.5363
887.3438 | 121.5729 | -0.082397 | 121.3943 | 0.0066373 | 0.010737 | 0.073343 | 0.0046976 | 0.064283 | -0.0033368 | -0.0020892 | 0.0069425 | -0.0010808 | 0.063602 | 0.05996 | -0.011335 | -0.0068103 | 121.1838 | 0.14191 | 3.7949 | 0.11902 | 121.4584 | -0.045776 | -0.17395 | 0.054932 | 0.24261 | -0.032043 | 121.3852 | 121.4172 | -0.068665 | -0.10529 | 0.036621 | -0.091553 | 0.064087 | 0.2243 | 0.20142 | 0.29297 | -0.21057 | 0.013732 | -0.022889 | -0.009155 | 0.13733 | 0.050354 | 0.073243 | 0.022888 | 121.5408 | 121.2662 | 3.8773 | -121.5683 | 121.4676 | 121.4996 | 0.32501 | -121.4996
889.0938 | 121.6232 | -0.11902 | 121.4264 | -0.00099167 | 0.002619 | 0.06843 | 0.0068338 | 0.065565 | 0.0037128 | -0.00273 | -0.00068649 | 0.002337 | 0.065097 | 0.064659 | -0.0070623 | -0.0085193 | 121.0922 | -0.036621 | 3.6942 | 0.050354 | 121.4996 | -0.091553 | -0.20599 | -0.018311 | 0.13275 | -0.16022 | 121.4035 | 121.431 | -0.10986 | -0.15106 | 0.027466 | -0.086975 | 0.073242 | 0.082398 | 0.16937 | 0.25635 | -0.33417 | 0.009156 | -0.032043 | -0.022889 | 0.10071 | -0.041198 | -0.009155 | 0.004577 | 121.6187 | 121.2112 | 3.8132 | -121.6324 | 121.5225 | 121.55 | 0.25177 | -121.5775
890.8281 | 121.4813 | -0.16022 | 121.4493 | -0.00099167 | 0.012873 | 0.070139 | 0.0042702 | 0.061934 | 0.00029476 | -0.0020892 | -0.008316 | -0.0017218 | 0.061252 | 0.064232 | -0.010053 | -0.0085193 | 121.1655 | 0.09613 | 3.7765 | 0.09613 | 121.463 | -0.032043 | -0.14648 | 0.059509 | 0.19684 | -0.041199 | 121.3669 | 121.431 | -0.064087 | -0.10986 | 0.12817 | 0.013733 | 0.013733 | 0.25635 | 0.25635 | 0.24261 | -0.28381 | 0.09613 | 0.050354 | -0.082398 | 0.21973 | 0.11902 | 0.068664 | -0.018311 | 121.6232 | 121.3257 | 3.9368 | -121.5958 | 121.5271 | 121.5912 | 0.35706 | -121.5591
892.5781 | 121.6049 | -0.11902 | 121.431 | 0.0066373 | 0.0034736 | 0.071421 | 0.0044838 | 0.060652 | 0.0022174 | -0.00273 | 0.0069425 | 0.0049006 | 0.06467 | 0.066155 | -0.0087713 | -0.0078783 | 121.106 | 0.013733 | 3.7445 | 0.068665 | 121.5271 | -0.068665 | -0.19684 | 0.013733 | 0.15106 | -0.12817 | 121.4127 | 121.4584 | -0.082397 | -0.11902 | 0.050354 | -0.077819 | 0.096131 | 0.13275 | 0.18768 | 0.2655 | -0.32501 | 0.036622 | 0 | -0.01831 | 0.13275 | -0.009155 | -0.009155 | 0.027466 | 121.6461 | 121.225 | 3.8635 | -121.6278 | 121.5317 | 121.5775 | 0.27008 | -121.55
894.3125 | 121.5775 | -0.11902 | 121.3943 | 0.0066373 | 0.004969 | 0.069925 | 0.0068338 | 0.065779 | 0.0026446 | -0.0029436 | 0.0069425 | 0.0016962 | 0.063175 | 0.064659 | -0.0083441 | -0.0065967 | 121.1197 | 0.009155 | 3.7537 | 0.059509 | 121.5225 | -0.07782 | -0.19226 | -0.004578 | 0.16479 | -0.12817 | 121.3943 | 121.4584 | -0.07782 | -0.1236 | 0.041199 | -0.073242 | 0.12817 | 0.12817 | 0.17853 | 0.25177 | -0.27466 | 0.041199 | -0.004577 | 0 | 0.11444 | -0.009155 | -0.004578 | 0.064087 | 121.6415 | 121.2387 | 3.8727 | -121.5866 | 121.5134 | 121.5775 | 0.28381 | -121.5179
895.9844 | 121.5179 | -0.13275 | 121.4218 | 0.0066373 | 0.010737 | 0.070139 | 0.0023476 | 0.064497 | -0.00077324 | -0.00273 | 0.0069425 | 0.00020076 | 0.062534 | 0.065087 | -0.0089849 | -0.0055285 | 121.106 | 0.032043 | 3.7308 | 0.073242 | 121.4767 | -0.059509 | -0.17395 | 0.045776 | 0.17395 | -0.073242 | 121.3852 | 121.4035 | -0.054932 | -0.10071 | 0.073242 | -0.041199 | 0.054932 | 0.16479 | 0.20599 | 0.24719 | -0.31586 | 0.077819 | 0.032043 | -0.036621 | 0.17853 | 0.059509 | 0.027466 | -0.018311 | 121.6095 | 121.2387 | 3.8635 | -121.5958 | 121.5179 | 121.5363 | 0.3067 | -121.5225
897.7188 | 121.5729 | -0.1236 | 121.4127 | 0.021896 | 0.010523 | 0.073557 | 0.0081154 | 0.062361 | -0.0035504 | -0.0031574 | 0.0069425 | -0.0017218 | 0.062961 | 0.06295 | -0.010053 | -0.0072375 | 121.1609 | 0.14648 | 3.8132 | 0.11444 | 121.463 | -0.054932 | -0.15564 | 0.045776 | 0.25635 | -0.022888 | 121.3531 | 121.4127 | -0.050354 | -0.10071 | 0.068664 | -0.032044 | 0.050354 | 0.27008 | 0.23804 | 0.27008 | -0.25177 | 0.073242 | 0.022888 | -0.05951 | 0.16937 | 0.10071 | 0.07782 | 0 | 121.5866 | 121.2845 | 3.9368 | -121.5683 | 121.4767 | 121.5363 | 0.37994 | -121.5134
899.4531 | 121.5591 | -0.10986 | 121.4127 | -0.00099167 | 0.0092414 | 0.073984 | 0.007261 | 0.065992 | -0.0046184 | -0.0046526 | -0.00068649 | -0.00086724 | 0.063816 | 0.061241 | -0.0098395 | -0.0091601 | 121.1563 | 0.11902 | 3.8361 | 0.11902 | 121.463 | -0.041199 | -0.15106 | 0.059509 | 0.25635 | -0.027466 | 121.376 | 121.4493 | -0.059509 | -0.09613 | 0.068664 | -0.041199 | 0.050354 | 0.22888 | 0.22888 | 0.27008 | -0.25635 | 0.050354 | 0.013733 | -0.036621 | 0.16937 | 0.082397 | 0.068664 | 0.036621 | 121.5729 | 121.2662 | 3.9459 | -121.5637 | 121.4859 | 121.5591 | 0.36621 | -121.5088
901.1406 | 121.4767 | -0.16022 | 121.4676 | 0.0066373 | 0.0075324 | 0.069071 | 0.0017068 | 0.062147 | 0.0032856 | -0.0023028 | 0.014572 | 0.0021234 | 0.068088 | 0.0653 | -0.0079169 | -0.0063831 | 121.0648 | -0.082397 | 3.7125 | 0.018311 | 121.5271 | -0.086975 | -0.19226 | -0.054932 | 0.045776 | -0.21515 | 121.4264 | 121.4722 | -0.09613 | -0.13275 | 0.073242 | -0.032044 | 0.05951 | 0.07782 | 0.17853 | 0.21057 | -0.40283 | 0.064087 | 0.027466 | -0.041198 | 0.10528 | -0.054932 | -0.082398 | 0.004578 | 121.6873 | 121.225 | 3.8727 | -121.6599 | 121.5866 | 121.6324 | 0.20599 | -121.6003
902.8906 | 121.5546 | -0.12817 | 121.4355 | 0.0066373 | 0.0073188 | 0.071848 | 0.0059792 | 0.058729 | -0.0029094 | -0.0048662 | 0.0069425 | 0.00062796 | 0.063816 | 0.064446 | -0.011121 | -0.0055285 | 121.1288 | 0.086975 | 3.8177 | 0.10529 | 121.4584 | -0.073242 | -0.14191 | 0 | 0.17853 | -0.082397 | 121.3898 | 121.4447 | -0.07782 | -0.12817 | 0.054932 | -0.013733 | 0.022888 | 0.21515 | 0.23346 | 0.24719 | -0.3067 | 0.050354 | 0 | -0.045776 | 0.12817 | 0.045777 | 0.045777 | 0.009155 | 121.5866 | 121.257 | 3.9459 | -121.5775 | 121.5179 | 121.5729 | 0.3067 | -121.5637
904.625 | 121.5225 | -0.1236 | 121.431 | 0.014267 | 0.0064642 | 0.072062 | 0.0046976 | 0.064711 | -0.00034604 | -0.0023028 | -0.00068649 | -0.0010808 | 0.063602 | 0.065087 | -0.012617 | -0.0074511 | 121.106 | 0.036621 | 3.7811 | 0.086975 | 121.4905 | -0.07782 | -0.18768 | -0.050354 | 0.13275 | -0.13733 | 121.4127 | 121.4767 | -0.11444 | -0.13275 | 0.045776 | -0.064087 | 0.05951 | 0.16022 | 0.21057 | 0.27466 | -0.32501 | 0.009155 | -0.009155 | -0.01831 | 0.073242 | -0.013733 | -0.004578 | 0.045777 | 121.6141 | 121.2296 | 3.9047 | -121.6187 | 121.5363 | 121.6003 | 0.25635 | -121.5637
906.2969 | 121.5088 | -0.16479 | 121.4539 | 0.014267 | 0.0068916 | 0.070566 | 0.00085245 | 0.063002 | 0.0028584 | -0.0018756 | 0.0069425 | 0.0025508 | 0.064243 | 0.066368 | -0.0070623 | -0.0080921 | 121.0648 | -0.059509 | 3.7033 | 0.027466 | 121.5179 | -0.068665 | -0.1831 | -0.054932 | 0.050354 | -0.17395 | 121.4172 | 121.4401 | -0.10529 | -0.14191 | 0.09613 | -0.01831 | 0.064087 | 0.10529 | 0.19226 | 0.21057 | -0.3891 | 0.059509 | 0.022888 | -0.036621 | 0.10986 | -0.009155 | -0.032043 | -0.013732 | 121.6827 | 121.2296 | 3.8681 | -121.637 | 121.582 | 121.6049 | 0.21515 | -121.5958
908.0469 | 121.5546 | -0.10529 | 121.4539 | 0.0066373 | 0.004328 | 0.066507 | 0.005552 | 0.061934 | 0.0015766 | -0.0025164 | 0.0069425 | 0.0016962 | 0.067447 | 0.064019 | -0.0096259 | -0.0065967 | 121.1334 | 0.022888 | 3.8269 | 0.073242 | 121.5179 | -0.086975 | -0.19684 | 0 | 0.16479 | -0.13733 | 121.4035 | 121.4722 | -0.082397 | -0.11902 | 0.018311 | -0.091552 | 0.064087 | 0.12817 | 0.17853 | 0.27008 | -0.32043 | 0.022889 | -0.013733 | -0.050354 | 0.10529 | -0.032043 | -0.01831 | 0.018311 | 121.6232 | 121.2387 | 3.9322 | -121.6507 | 121.5088 | 121.5775 | 0.27008 | -121.5729
909.7188 | 121.5088 | -0.15564 | 121.431 | -0.0086212 | 0.0064642 | 0.069498 | 0.0044838 | 0.057875 | 0.0017902 | -0.0029436 | 0.014572 | 0.0016962 | 0.064029 | 0.063378 | -0.0074897 | -0.0068103 | 121.1197 | 0.027466 | 3.8132 | 0.064087 | 121.5317 | -0.07782 | -0.20599 | -0.009155 | 0.13275 | -0.15564 | 121.431 | 121.4676 | -0.082397 | -0.13275 | 0.07782 | -0.050354 | 0.10071 | 0.18311 | 0.21973 | 0.27008 | -0.31128 | 0.073243 | 0.022889 | 0 | 0.14649 | 0 | -0.022889 | 0.036621 | 121.6873 | 121.2753 | 3.9688 | -121.637 | 121.5866 | 121.6232 | 0.28839 | -121.5637
911.4844 | 121.5683 | -0.11902 | 121.4127 | -0.00099167 | 0.0098822 | 0.074411 | 0.0083292 | 0.062361 | -0.005473 | -0.003371 | 0.0069425 | -0.0019354 | 0.063816 | 0.06295 | -0.01048 | -0.0051013 | 121.1288 | 0.13275 | 3.8544 | 0.11902 | 121.4676 | -0.050354 | -0.16022 | 0.041199 | 0.25635 | -0.032043 | 121.3806 | 121.4264 | -0.073242 | -0.10986 | 0.068665 | -0.041198 | 0.054931 | 0.25177 | 0.23804 | 0.27924 | -0.28381 | 0.045777 | 0.009156 | -0.032044 | 0.16022 | 0.086976 | 0.07782 | 0.013733 | 121.5866 | 121.2479 | 3.9734 | -121.5729 | 121.4996 | 121.5454 | 0.37537 | -121.5225
913.1719 | 121.5546 | -0.12817 | 121.4172 | 0.0066373 | 0.0083868 | 0.073771 | 0.0051248 | 0.064283 | -0.0048322 | -0.00508 | 0.0069425 | -0.0019354 | 0.061679 | 0.064446 | -0.011762 | -0.0055285 | 121.138 | 0.09613 | 3.8544 | 0.10986 | 121.4767 | -0.068665 | -0.1831 | 0.018311 | 0.22888 | -0.059509 | 121.3806 | 121.4401 | -0.073242 | -0.10529 | 0.059509 | -0.054931 | 0.05951 | 0.2243 | 0.23804 | 0.29297 | -0.27924 | 0.054932 | 0.022888 | -0.036621 | 0.14649 | 0.068665 | 0.045777 | 0.022889 | 121.6049 | 121.2662 | 3.9825 | -121.6003 | 121.5088 | 121.5683 | 0.35706 | -121.5225
914.8438 | 121.4996 | -0.15564 | 121.4539 | -0.00099167 | 0.0036872 | 0.068857 | 0.0044838 | 0.063002 | 0.00414 | -0.00273 | 0.022202 | 0.0021234 | 0.065952 | 0.065087 | -0.0051397 | -0.0085193 | 121.1334 | 0.009155 | 3.8132 | 0.054932 | 121.5134 | -0.073242 | -0.16479 | -0.018311 | 0.13275 | -0.15106 | 121.431 | 121.4813 | -0.07782 | -0.13733 | 0.082398 | -0.009155 | 0.05951 | 0.16479 | 0.21057 | 0.21973 | -0.32043 | 0.07782 | 0.018311 | -0.022888 | 0.13733 | 0.004578 | -0.013733 | 0.027466 | 121.669 | 121.2891 | 3.9688 | -121.6187 | 121.5866 | 121.637 | 0.28839 | -121.5912
916.5938 | 121.5408 | -0.1236 | 121.4447 | 0.0066373 | 0.011805 | 0.07313 | 0.0051248 | 0.059584 | -0.006541 | -0.0052936 | -0.00068649 | -0.0034308 | 0.064029 | 0.063591 | -0.011976 | -0.0040331 | 121.0556 | 0.018311 | 3.7811 | 0.068665 | 121.4996 | -0.068665 | -0.1831 | -0.027466 | 0.13733 | -0.068665 | 121.3898 | 121.4447 | -0.073242 | -0.10071 | 0.054931 | -0.059509 | 0.054932 | 0.14191 | 0.19226 | 0.25177 | -0.3891 | 0.050354 | 0.022888 | -0.054931 | 0.09613 | 0.054931 | 0.032043 | 0 | 121.6232 | 121.1792 | 3.9047 | -121.6278 | 121.5134 | 121.5683 | 0.26093 | -121.5454
918.3438 | 121.4996 | -0.15564 | 121.4584 | 0.0066373 | 0.0064642 | 0.06843 | 0.0032022 | 0.064283 | 0.0028584 | -0.00273 | 0.0069425 | 0.002978 | 0.064457 | 0.065514 | -0.0074897 | -0.0059557 | 121.0419 | -0.068665 | 3.7308 | 0.013733 | 121.5363 | -0.10529 | -0.1831 | -0.064087 | 0.022888 | -0.19226 | 121.431 | 121.463 | -0.10986 | -0.14191 | 0.050354 | -0.027465 | 0.07782 | 0.086975 | 0.16937 | 0.19684 | -0.41656 | 0.045777 | 0.013733 | -0.027466 | 0.091553 | -0.036621 | -0.050354 | 0.004578 | 121.6919 | 121.1975 | 3.8864 | -121.6415 | 121.5866 | 121.6187 | 0.17853 | -121.6003
920.0781 | 121.4676 | -0.15106 | 121.4676 | 0.0066373 | 0.0062506 | 0.069712 | 0.0036294 | 0.062147 | 0.001363 | -0.00038024 | 0.0069425 | 0.001269 | 0.065097 | 0.063591 | -0.0053533 | -0.0040331 | 121.0419 | -0.059509 | 3.7354 | 0.018311 | 121.5134 | -0.09613 | -0.20142 | -0.059509 | 0.050354 | -0.19684 | 121.431 | 121.4722 | -0.082397 | -0.12817 | 0.054932 | -0.050354 | 0.045777 | 0.091553 | 0.16937 | 0.21973 | -0.42572 | 0.068665 | 0.022888 | -0.036621 | 0.091553 | -0.045776 | -0.068664 | 0.004578 | 121.6644 | 121.1929 | 3.8864 | -121.669 | 121.582 | 121.6232 | 0.20142 | -121.5958
921.75 | 121.4767 | -0.15106 | 121.4355 | 0.014267 | 0.013514 | 0.069925 | 0.0042702 | 0.060652 | -0.00077324 | -0.0037982 | 0.0069425 | -0.0030034 | 0.062107 | 0.062523 | -0.0087713 | -0.0063831 | 121.1472 | 0.10071 | 3.8498 | 0.11902 | 121.4722 | -0.045776 | -0.14191 | 0.050354 | 0.17853 | -0.041199 | 121.376 | 121.4172 | -0.045776 | -0.10071 | 0.10529 | 0.009155 | 0.036621 | 0.25177 | 0.27008 | 0.26093 | -0.28839 | 0.10529 | 0.050354 | -0.059509 | 0.20142 | 0.10986 | 0.059509 | -0.018311 | 121.6232 | 121.2982 | 4.0009 | -121.5775 | 121.5271 | 121.5683 | 0.32959 | -121.5363
923.4844 | 121.4722 | -0.15106 | 121.4493 | 0.014267 | 0.011378 | 0.076334 | 0.0046976 | 0.060438 | -0.0052594 | -0.0035846 | 0.014572 | -0.00086724 | 0.061039 | 0.063378 | -0.0087713 | -0.0051013 | 121.0922 | 0.054932 | 3.8177 | 0.050354 | 121.4859 | -0.054932 | -0.15564 | -0.009155 | 0.13733 | -0.082397 | 121.3623 | 121.4447 | -0.086975 | -0.11902 | 0.09613 | -0.004578 | 0.036621 | 0.20599 | 0.20142 | 0.20599 | -0.35706 | 0.064087 | 0.032043 | -0.086975 | 0.14191 | 0.068665 | 0.036622 | -0.004578 | 121.637 | 121.2433 | 3.9688 | -121.6049 | 121.5134 | 121.5958 | 0.28839 | -121.5683
925.1562 | 121.5958 | -0.13275 | 121.4355 | -0.0086212 | 0.0036872 | 0.072062 | 0.0076882 | 0.063643 | 0.0032856 | -0.0042254 | 0.022202 | 0.00084176 | 0.063388 | 0.06231 | -0.010053 | -0.0074511 | 121.0556 | -0.054932 | 3.7674 | 0.013733 | 121.5271 | -0.09613 | -0.19226 | -0.07782 | 0.09613 | -0.17853 | 121.4447 | 121.4767 | -0.10071 | -0.14648 | 0.036621 | -0.05951 | 0.091553 | 0.077819 | 0.14648 | 0.20599 | -0.37994 | 0.032043 | -0.013733 | 0.009155 | 0.054931 | -0.045777 | -0.032044 | 0.041199 | 121.6599 | 121.1884 | 3.9001 | -121.6278 | 121.5775 | 121.6095 | 0.22888 | -121.582
926.8281 | 121.4996 | -0.14648 | 121.463 | 0.014267 | 0.0034736 | 0.070993 | 0.0025612 | 0.063215 | 0.0037128 | -0.001662 | 0.0069425 | 0.0016962 | 0.065097 | 0.065728 | -0.0079169 | -0.0080921 | 121.1243 | 0.022888 | 3.8315 | 0.059509 | 121.5271 | -0.073242 | -0.20142 | -0.018311 | 0.10986 | -0.15106 | 121.4493 | 121.463 | -0.10071 | -0.13275 | 0.073242 | -0.054932 | 0.064087 | 0.16937 | 0.20599 | 0.26093 | -0.33875 | 0.045776 | 0.013733 | -0.013733 | 0.12817 | -0.004578 | -0.018311 | 0 | 121.6736 | 121.2708 | 3.978 | -121.6644 | 121.5958 | 121.6095 | 0.25635 | -121.5958
928.5781 | 121.6095 | -0.12817 | 121.4035 | 0.0066373 | 0.0056098 | 0.069712 | 0.0049112 | 0.061293 | 0.00072196 | -0.0035846 | 0.0069425 | 0.0021234 | 0.061466 | 0.064019 | -0.0077033 | -0.0065967 | 121.0464 | -0.036621 | 3.7857 | 0.045776 | 121.5271 | -0.086975 | -0.2243 | -0.064087 | 0.10986 | -0.16479 | 121.431 | 121.4859 | -0.09613 | -0.12817 | 0.041199 | -0.09613 | 0.1236 | 0.091553 | 0.17395 | 0.27008 | -0.35706 | 0.032044 | 0 | 0.027466 | 0.064087 | -0.036621 | -0.036621 | 0.082398 | 121.6553 | 121.1746 | 3.9139 | -121.6278 | 121.5591 | 121.6141 | 0.23804 | -121.5317
930.375 | 121.4813 | -0.16937 | 121.4401 | 0.014267 | 0.004969 | 0.069712 | 0.0012796 | 0.062147 | 0.0015766 | -0.0012346 | 0.014572 | 0.002337 | 0.063175 | 0.065514 | -0.0053533 | -0.0074511 | 121.051 | -0.050354 | 3.772 | 0.018311 | 121.5363 | -0.082397 | -0.20599 | -0.073242 | 0.059509 | -0.21515 | 121.4264 | 121.4859 | -0.09613 | -0.12817 | 0.086976 | -0.036621 | 0.09613 | 0.11902 | 0.18768 | 0.22431 | -0.3891 | 0.073243 | 0.041199 | -0.013733 | 0.096131 | -0.045776 | -0.086975 | 0.045776 | 121.7056 | 121.2204 | 3.9413 | -121.6461 | 121.5958 | 121.6553 | 0.22888 | -121.5683
932.0469 | 121.4813 | -0.15106 | 121.4264 | 0.014267 | 0.012873 | 0.071634 | 0.0034158 | 0.063643 | -0.0026958 | -0.00080744 | -0.00068649 | -0.0023626 | 0.062107 | 0.061455 | -0.0057807 | -0.0068103 | 121.1472 | 0.09613 | 3.8773 | 0.10529 | 121.4859 | -0.059509 | -0.16022 | 0.045776 | 0.19226 | -0.054932 | 121.3577 | 121.4355 | -0.054932 | -0.10071 | 0.091553 | -0.009155 | 0.059509 | 0.24719 | 0.25635 | 0.2655 | -0.27924 | 0.09613 | 0.050354 | -0.068665 | 0.19684 | 0.09613 | 0.045776 | 0.009155 | 121.637 | 121.2982 | 4.0283 | -121.5866 | 121.5088 | 121.5866 | 0.34332 | -121.5271
933.7188 | 121.582 | -0.1236 | 121.4401 | -0.00099167 | 0.0056098 | 0.068003 | 0.0068338 | 0.063215 | 0.0028584 | -0.00273 | 0.0069425 | 0.00041436 | 0.06702 | 0.0653 | -0.0094123 | -0.0068103 | 121.1197 | 0.018311 | 3.8727 | 0.059509 | 121.5225 | -0.07782 | -0.17395 | 0.009155 | 0.15564 | -0.11902 | 121.4264 | 121.463 | -0.073242 | -0.12817 | 0.045776 | -0.050354 | 0.082397 | 0.14191 | 0.1831 | 0.23346 | -0.32043 | 0.050354 | -0.004578 | -0.013733 | 0.13275 | 0.004577 | 0.009155 | 0.022888 | 121.6461 | 121.2433 | 3.9963 | -121.6141 | 121.55 | 121.5866 | 0.27924 | -121.5683
935.4688 | 121.4859 | -0.1831 | 121.4539 | 0.0066373 | 0.004328 | 0.070566 | 0.0036294 | 0.062147 | 0.001363 | -0.0020892 | 0.0069425 | 0.00084176 | 0.062748 | 0.065728 | -0.0079169 | -0.0078783 | 121.0464 | -0.086975 | 3.7765 | 0.022888 | 121.5225 | -0.07782 | -0.19226 | -0.073242 | 0.050354 | -0.21973 | 121.4127 | 121.4767 | -0.091553 | -0.14191 | 0.10528 | -0.009156 | 0.068665 | 0.09613 | 0.20599 | 0.21515 | -0.40741 | 0.091552 | 0.041198 | -0.041198 | 0.10986 | -0.036622 | -0.07782 | 0.022889 | 121.7056 | 121.2296 | 3.9597 | -121.6461 | 121.5958 | 121.6599 | 0.23346 | -121.5958
937.2031 | 121.4996 | -0.13733 | 121.4447 | -0.00099167 | 0.0066778 | 0.069498 | 0.0040566 | 0.06407 | -0.00013244 | -0.00080744 | 0.0069425 | 0.0014826 | 0.06232 | 0.064659 | -0.0074897 | -0.0063831 | 121.1151 | 0.013733 | 3.8452 | 0.059509 | 121.5225 | -0.073242 | -0.18768 | -0.027466 | 0.12817 | -0.15106 | 121.4035 | 121.4996 | -0.082397 | -0.11444 | 0.064087 | -0.050354 | 0.07782 | 0.15106 | 0.19684 | 0.24719 | -0.32959 | 0.054932 | 0.022888 | -0.041199 | 0.10986 | -0.013733 | -0.036621 | 0.054932 | 121.6599 | 121.2524 | 3.9825 | -121.6324 | 121.5408 | 121.637 | 0.2655 | -121.5591
938.8906 | 121.6049 | -0.10529 | 121.431 | 0.0066373 | 0.0096686 | 0.070353 | 0.007261 | 0.05937 | -0.0080364 | -0.0042254 | 0.0069425 | -0.003858 | 0.063175 | 0.063805 | -0.013044 | -0.0053149 | 121.0831 | 0.041199 | 3.8544 | 0.068665 | 121.5042 | -0.054932 | -0.16937 | 0 | 0.18768 | -0.032043 | 121.3989 | 121.4676 | -0.068665 | -0.11444 | 0.050354 | -0.064087 | 0.073242 | 0.14649 | 0.17395 | 0.23804 | -0.3479 | 0.036621 | -0.009155 | -0.032043 | 0.10529 | 0.073243 | 0.082398 | 0.036621 | 121.6095 | 121.1884 | 3.9597 | -121.6003 | 121.5042 | 121.5729 | 0.29297 | -121.5454
940.6406 | 121.5775 | -0.13733 | 121.4447 | -0.00099167 | 0.0068916 | 0.072489 | 0.0085428 | 0.062147 | -0.0031232 | -0.0065752 | 0.014572 | -0.00065364 | 0.063388 | 0.065087 | -0.011121 | -0.0076647 | 121.1426 | 0.073242 | 3.8864 | 0.082397 | 121.5042 | -0.068665 | -0.19226 | -0.032043 | 0.1831 | -0.10529 | 121.4081 | 121.4951 | -0.086975 | -0.1236 | 0.068664 | -0.054932 | 0.059509 | 0.21057 | 0.21973 | 0.27466 | -0.30212 | 0.050354 | 0.013733 | -0.036621 | 0.10529 | 0.032043 | 0.01831 | 0.050354 | 121.6415 | 121.2799 | 4.0237 | -121.637 | 121.5454 | 121.6324 | 0.32043 | -121.5683
942.3281 | 121.6003 | -0.10529 | 121.4172 | 0.0066373 | 0.0071052 | 0.071634 | 0.002775 | 0.063215 | 0.0022174 | -0.001662 | 0.014572 | 0.0016962 | 0.062961 | 0.064873 | -0.0072759 | -0.0068103 | 121.1105 | 0.009155 | 3.8681 | 0.068665 | 121.5225 | -0.07782 | -0.19226 | -0.009155 | 0.15106 | -0.11902 | 121.431 | 121.4905 | -0.086975 | -0.1236 | 0.027466 | -0.086975 | 0.10529 | 0.11444 | 0.17395 | 0.26093 | -0.3067 | 0.018311 | -0.01831 | 0.013733 | 0.096131 | -0.013733 | 0.004577 | 0.073243 | 121.6278 | 121.2158 | 3.9734 | -121.6095 | 121.5363 | 121.5958 | 0.25635 | -121.5408
944.0156 | 121.5729 | -0.11444 | 121.4401 | -0.00099167 | 0.0058234 | 0.071421 | 0.0085428 | 0.063429 | -0.0035504 | -0.0037982 | -0.00068649 | -0.0030034 | 0.063175 | 0.063378 | -0.011121 | -0.0063831 | 121.1105 | 0.032043 | 3.8864 | 0.07782 | 121.5088 | -0.082397 | -0.1831 | -0.068665 | 0.13275 | -0.14648 | 121.4218 | 121.4996 | -0.10071 | -0.13733 | 0.032044 | -0.068664 | 0.068664 | 0.14648 | 0.19226 | 0.26092 | -0.32959 | 0.013733 | -0.022888 | -0.018311 | 0.045776 | -0.032043 | -0.009155 | 0.059509 | 121.6232 | 121.225 | 4.0009 | -121.6232 | 121.5363 | 121.6141 | 0.24719 | -121.5775
945.6875 | 121.5179 | -0.15564 | 121.4676 | 0.014267 | 0.010737 | 0.069712 | 0.0036294 | 0.06172 | 8.1158e-05 | -0.0070026 | 0.022202 | 0.00084176 | 0.062107 | 0.065941 | -0.0089849 | -0.0070239 | 121.0739 | -0.059509 | 3.7949 | 0.009155 | 121.5271 | -0.086975 | -0.19684 | -0.059509 | 0.050354 | -0.18768 | 121.4218 | 121.4813 | -0.10071 | -0.13733 | 0.068665 | -0.041198 | 0.05951 | 0.096131 | 0.16479 | 0.20599 | -0.39368 | 0.054932 | 0.018311 | -0.045776 | 0.096131 | -0.032043 | -0.050354 | 0.013733 | 121.6827 | 121.2296 | 3.9505 | -121.6644 | 121.5775 | 121.637 | 0.20599 | -121.6049
947.4219 | 121.6187 | -0.10986 | 121.4264 | 0.014267 | 0.011378 | 0.072702 | 0.0081154 | 0.063215 | -0.006541 | -0.0035846 | 0.0069425 | -0.0027898 | 0.062534 | 0.062096 | -0.013471 | -0.0051013 | 121.1334 | 0.086975 | 3.8864 | 0.10529 | 121.4951 | -0.032043 | -0.17395 | 0.032043 | 0.21515 | -0.022888 | 121.3898 | 121.4584 | -0.045776 | -0.091553 | 0.07782 | -0.064087 | 0.068664 | 0.19684 | 0.21515 | 0.27924 | -0.29297 | 0.064087 | 0.01831 | -0.036621 | 0.14191 | 0.086975 | 0.068665 | 0.032043 | 121.6049 | 121.2433 | 3.9963 | -121.6003 | 121.4996 | 121.5683 | 0.32501 | -121.5179
949.1875 | 121.6232 | -0.10071 | 121.4539 | 0.014267 | 0.0051826 | 0.069925 | 0.0053384 | 0.062788 | 0.002431 | -0.004439 | -0.00068649 | 0.0010554 | 0.063816 | 0.0653 | -0.0066351 | -0.0074511 | 121.1105 | -0.013733 | 3.8406 | 0.068665 | 121.5546 | -0.068665 | -0.19684 | -0.009155 | 0.14648 | -0.14648 | 121.4218 | 121.4767 | -0.086975 | -0.13275 | 0.032043 | -0.09613 | 0.10071 | 0.086975 | 0.16937 | 0.2655 | -0.34332 | 0.013733 | -0.032043 | -0.032043 | 0.091553 | -0.045776 | -0.013733 | 0.022889 | 121.6553 | 121.2112 | 3.9413 | -121.6507 | 121.5225 | 121.5775 | 0.24719 | -121.5866
950.8594 | 121.6599 | -0.1236 | 121.4264 | 0.0066373 | 0.0058234 | 0.071421 | 0.0051248 | 0.05937 | 0.0020038 | -0.0052936 | 0.014572 | 0.00020076 | 0.063388 | 0.0653 | -0.0074897 | -0.0076647 | 121.0739 | -0.027466 | 3.8361 | 0.036621 | 121.5683 | -0.10529 | -0.20142 | -0.027466 | 0.14648 | -0.15106 | 121.431 | 121.4676 | -0.09613 | -0.14648 | 0.01831 | -0.07782 | 0.14191 | 0.09613 | 0.16022 | 0.23804 | -0.35248 | 0.027466 | -0.022888 | 0.004577 | 0.09613 | -0.027466 | -0.004578 | 0.041198 | 121.6919 | 121.1975 | 3.9597 | -121.6278 | 121.5546 | 121.5912 | 0.27008 | -121.5729
952.6094 | 121.55 | -0.12817 | 121.4584 | 0.0066373 | 0.0066778 | 0.069925 | 0.0074746 | 0.063215 | -0.0031232 | -0.006148 | -0.00068649 | -0.0010808 | 0.063388 | 0.064659 | -0.01283 | -0.0061695 | 121.0876 | 0.032043 | 3.891 | 0.064087 | 121.5271 | -0.091553 | -0.21057 | -0.073242 | 0.12817 | -0.14191 | 121.4264 | 121.4859 | -0.10071 | -0.15106 | 0.036621 | -0.082397 | 0.068665 | 0.16022 | 0.19226 | 0.27466 | -0.37079 | 0.027466 | -0.022888 | -0.032043 | 0.054932 | -0.013733 | 0.009155 | 0.027466 | 121.6553 | 121.2158 | 4.0192 | -121.669 | 121.5546 | 121.6141 | 0.25635 | -121.6095
954.3594 | 121.5683 | -0.13275 | 121.4401 | 0.0066373 | 0.0088142 | 0.072489 | 0.0079018 | 0.063856 | -0.0024822 | -0.003371 | 0.0069425 | -0.0012946 | 0.065738 | 0.061241 | -0.0089849 | -0.0055285 | 121.1151 | 0.068665 | 3.891 | 0.082397 | 121.5317 | -0.082397 | -0.16937 | -0.041199 | 0.15564 | -0.11902 | 121.4172 | 121.4859 | -0.10071 | -0.13275 | 0.050354 | -0.036622 | 0.091552 | 0.20142 | 0.21515 | 0.25177 | -0.32501 | 0.032043 | 0 | -0.022889 | 0.091552 | 0.013732 | 0.013732 | 0.045776 | 121.6644 | 121.2479 | 4.0237 | -121.6095 | 121.55 | 121.6187 | 0.28839 | -121.5729
956.0469 | 121.6003 | -0.11902 | 121.4401 | -0.00099167 | 0.0053962 | 0.069925 | 0.0049112 | 0.062574 | 0.0022174 | -0.0025164 | 0.0069425 | 0.004046 | 0.063388 | 0.065087 | -0.0059943 | -0.0076647 | 121.1197 | 0.018311 | 3.8956 | 0.068665 | 121.5317 | -0.091553 | -0.20142 | -0.013733 | 0.16022 | -0.14191 | 121.4584 | 121.4813 | -0.09613 | -0.12817 | 0.027466 | -0.082397 | 0.091552 | 0.13733 | 0.18768 | 0.27008 | -0.32043 | 0.022889 | -0.009155 | 0.01831 | 0.10529 | -0.022888 | -0.013733 | 0.041198 | 121.6507 | 121.2387 | 4.0146 | -121.6415 | 121.5775 | 121.6003 | 0.27924 | -121.5683
957.7344 | 121.6095 | -0.12817 | 121.4401 | 0.014267 | 0.012446 | 0.074198 | 0.0057656 | 0.061293 | -0.0048322 | -0.003371 | 0.014572 | -0.0030034 | 0.063175 | 0.063378 | -0.01048 | -0.0074511 | 121.0922 | 0.059509 | 3.8864 | 0.086975 | 121.5134 | -0.073242 | -0.16479 | 0.013733 | 0.20599 | -0.050354 | 121.3852 | 121.4218 | -0.068665 | -0.11444 | 0.054932 | -0.036621 | 0.073242 | 0.18768 | 0.21515 | 0.25177 | -0.3479 | 0.059509 | 0.013733 | -0.054932 | 0.14191 | 0.07782 | 0.064087 | -0.018311 | 121.6415 | 121.2204 | 4.0146 | -121.6049 | 121.5134 | 121.55 | 0.33417 | -121.5546
959.4531 | 121.5088 | -0.16937 | 121.4447 | 0.0066373 | 0.0073188 | 0.069498 | 0.0044838 | 0.063429 | 0.003072 | -0.004439 | 0.0069425 | 0.00084176 | 0.064884 | 0.065087 | -0.0053533 | -0.0080921 | 121.051 | -0.068665 | 3.8086 | 0.013733 | 121.5683 | -0.091553 | -0.19684 | -0.07782 | 0.036621 | -0.20142 | 121.4493 | 121.4951 | -0.09613 | -0.14648 | 0.07782 | -0.027465 | 0.1236 | 0.10071 | 0.18311 | 0.21057 | -0.39368 | 0.073243 | 0.022889 | 0.004578 | 0.091553 | -0.032043 | -0.054932 | 0.050354 | 121.7377 | 121.2204 | 3.978 | -121.6415 | 121.6187 | 121.6644 | 0.20599 | -121.5912
961.2031 | 121.5225 | -0.15564 | 121.463 | -0.00099167 | 0.007746 | 0.070353 | 0.0019204 | 0.06172 | -0.00013244 | -0.0018756 | -0.00068649 | 0.004687 | 0.061893 | 0.064659 | -0.0072759 | -0.0055285 | 121.0739 | -0.059509 | 3.7949 | 0.022888 | 121.5454 | -0.073242 | -0.20599 | -0.064087 | 0.064087 | -0.17395 | 121.4447 | 121.4951 | -0.10529 | -0.12817 | 0.082398 | -0.050354 | 0.082397 | 0.096131 | 0.17853 | 0.22888 | -0.3891 | 0.050354 | 0.027466 | -0.018311 | 0.091553 | -0.01831 | -0.045776 | 0.032043 | 121.7011 | 121.2296 | 3.9505 | -121.669 | 121.6003 | 121.6507 | 0.21973 | -121.5912
962.8906 | 121.6095 | -0.09613 | 121.4081 | 0.014267 | 0.010309 | 0.075052 | 0.0061928 | 0.062147 | -0.0076092 | -0.0048662 | 0.0069425 | -0.0010808 | 0.062534 | 0.06295 | -0.011121 | -0.0051013 | 121.1472 | 0.07782 | 3.9139 | 0.09613 | 121.5134 | -0.064087 | -0.16479 | 0.013733 | 0.21057 | -0.032043 | 121.4127 | 121.463 | -0.073242 | -0.10529 | 0.032043 | -0.068665 | 0.10529 | 0.17395 | 0.19226 | 0.26092 | -0.26093 | 0.022888 | -0.009156 | 0.004578 | 0.10986 | 0.064087 | 0.073243 | 0.054932 | 121.6095 | 121.2433 | 4.01 | -121.5729 | 121.5088 | 121.5591 | 0.3067 | -121.5134
964.6406 | 121.4813 | -0.17853 | 121.4859 | -0.00099167 | 0.011378 | 0.069925 | 0.0046976 | 0.060865 | -0.0022686 | -0.0057208 | 0.0069425 | -0.00044004 | 0.061466 | 0.063164 | -0.010267 | -0.0063831 | 121.1884 | 0.073242 | 3.9459 | 0.10071 | 121.4859 | -0.036621 | -0.15564 | 0.018311 | 0.16937 | -0.050354 | 121.3852 | 121.4539 | -0.07782 | -0.10529 | 0.14191 | 0.022888 | 0 | 0.25177 | 0.27924 | 0.25635 | -0.29755 | 0.10071 | 0.073242 | -0.10071 | 0.19684 | 0.12817 | 0.054932 | -0.032044 | 121.6644 | 121.3669 | 4.1245 | -121.6415 | 121.5637 | 121.6324 | 0.3479 | -121.5912
966.3906 | 121.6141 | -0.10529 | 121.4401 | 0.0066373 | 0.0034736 | 0.069925 | 0.0044838 | 0.060652 | 0.0015766 | -0.0029436 | -0.00068649 | 0.001269 | 0.06467 | 0.065087 | -0.0066351 | -0.0093737 | 121.1288 | -0.022888 | 3.8727 | 0.059509 | 121.5637 | -0.091553 | -0.17853 | -0.013733 | 0.14191 | -0.13275 | 121.4447 | 121.4859 | -0.091553 | -0.1236 | 0.013733 | -0.073242 | 0.1236 | 0.082398 | 0.16479 | 0.23804 | -0.31128 | 0.013733 | -0.01831 | 0.004577 | 0.091553 | -0.027465 | -0.009155 | 0.045776 | 121.669 | 121.2341 | 3.978 | -121.6187 | 121.55 | 121.5912 | 0.24719 | -121.5637
968.125 | 121.4859 | -0.16022 | 121.4539 | -0.00099167 | 0.012018 | 0.072916 | 0.0051248 | 0.061506 | -0.0026958 | -0.0031574 | -0.00068649 | -0.0032172 | 0.063602 | 0.064873 | -0.0083441 | -0.0048877 | 121.1197 | 0.054932 | 3.8956 | 0.068665 | 121.4767 | -0.064087 | -0.14648 | 0 | 0.13733 | -0.082397 | 121.4035 | 121.4401 | -0.073242 | -0.10529 | 0.09613 | 0.013733 | 0.022889 | 0.21515 | 0.22888 | 0.21515 | -0.33417 | 0.086975 | 0.054931 | -0.050354 | 0.16022 | 0.07782 | 0.022889 | -0.013732 | 121.637 | 121.2799 | 4.0558 | -121.6003 | 121.5637 | 121.6003 | 0.29755 | -121.5591
969.8125 | 121.5637 | -0.11902 | 121.4722 | 0.021896 | 0.009455 | 0.072702 | 0.0061928 | 0.065992 | -0.0018414 | -0.0046526 | 0.0069425 | -0.0019354 | 0.062961 | 0.064659 | -0.011335 | -0.0087329 | 121.1609 | 0.091553 | 3.9825 | 0.1236 | 121.4951 | -0.050354 | -0.16937 | 0.041199 | 0.24719 | -0.045776 | 121.3943 | 121.4905 | -0.07782 | -0.09613 | 0.068665 | -0.050354 | 0.022888 | 0.21057 | 0.24261 | 0.29297 | -0.31128 | 0.041199 | 0.022889 | -0.07782 | 0.16022 | 0.073243 | 0.050354 | 0.018311 | 121.6141 | 121.2799 | 4.1016 | -121.6415 | 121.5134 | 121.6095 | 0.36621 | -121.5683
971.5469 | 121.5363 | -0.16022 | 121.4355 | -0.00099167 | 0.010523 | 0.071634 | 0.00042505 | 0.062574 | 0.001363 | -0.00273 | -0.00068649 | -1.2844e-05 | 0.060611 | 0.061882 | -0.0055671 | -0.0074511 | 121.1746 | 0.073242 | 3.9322 | 0.10529 | 121.5042 | -0.050354 | -0.16022 | 0.050354 | 0.19226 | -0.059509 | 121.3898 | 121.4401 | -0.073242 | -0.10529 | 0.10986 | 0 | 0.068664 | 0.23346 | 0.2655 | 0.2655 | -0.26093 | 0.086975 | 0.054931 | -0.045776 | 0.21057 | 0.10071 | 0.045777 | 0.004578 | 121.6644 | 121.3348 | 4.0924 | -121.5958 | 121.55 | 121.6003 | 0.35248 | -121.5408
973.2969 | 121.5546 | -0.16479 | 121.4447 | -0.0086212 | 0.0075324 | 0.073984 | 0.0070474 | 0.065138 | -0.0016278 | -0.0029436 | -0.00068649 | 0.001269 | 0.062961 | 0.0653 | -0.0087713 | -0.0074511 | 121.1426 | 0.054932 | 3.9459 | 0.086975 | 121.5179 | -0.082397 | -0.17395 | -0.027466 | 0.16022 | -0.14191 | 121.4401 | 121.5088 | -0.09613 | -0.13275 | 0.082398 | -0.009155 | 0.073242 | 0.21973 | 0.25177 | 0.26092 | -0.30212 | 0.068665 | 0.032044 | -0.004577 | 0.13733 | 0.022888 | -0.009156 | 0.064087 | 121.6827 | 121.3074 | 4.1107 | -121.6187 | 121.6049 | 121.6736 | 0.32501 | -121.5775
974.9688 | 121.5088 | -0.16937 | 121.4813 | -0.00099167 | 0.004328 | 0.067789 | 0.0068338 | 0.063429 | 0.0049946 | -0.00273 | 0.0069425 | 0.0016962 | 0.064029 | 0.064232 | -0.0064215 | -0.0074511 | 121.1334 | 0.013733 | 3.9093 | 0.050354 | 121.5363 | -0.07782 | -0.19226 | -0.022888 | 0.10071 | -0.17853 | 121.4401 | 121.463 | -0.10529 | -0.15106 | 0.091553 | -0.022888 | 0.054932 | 0.18311 | 0.21973 | 0.24261 | -0.3479 | 0.064087 | 0.018311 | -0.041198 | 0.14649 | -0.009155 | -0.027466 | -0.01831 | 121.7056 | 121.3028 | 4.0787 | -121.6736 | 121.6095 | 121.6324 | 0.27008 | -121.6324
976.6406 | 121.4859 | -0.15106 | 121.4676 | -0.00099167 | 0.014582 | 0.070353 | 0.0049112 | 0.061293 | -0.0033368 | -0.0025164 | 0.0069425 | -0.0012946 | 0.063175 | 0.064019 | -0.0083441 | -0.0057421 | 121.1746 | 0.086975 | 3.978 | 0.091553 | 121.4905 | -0.045776 | -0.16022 | 0.041199 | 0.18768 | -0.059509 | 121.3852 | 121.4539 | -0.068665 | -0.09613 | 0.10529 | -0.009155 | 0.022889 | 0.23804 | 0.24261 | 0.25177 | -0.29297 | 0.082397 | 0.054932 | -0.082397 | 0.19226 | 0.091553 | 0.036621 | -0.013733 | 121.6415 | 121.3257 | 4.129 | -121.6278 | 121.5363 | 121.6049 | 0.33874 | -121.5637
978.3906 | 121.4951 | -0.16479 | 121.4813 | 0.0066373 | 0.01095 | 0.070139 | 0.0044838 | 0.065565 | -0.0016278 | -0.0035846 | 0.014572 | 0.00020076 | 0.061893 | 0.062523 | -0.0091985 | -0.0074511 | 121.1746 | 0.082397 | 3.9871 | 0.11444 | 121.4813 | -0.027466 | -0.15106 | 0.059509 | 0.1831 | -0.050354 | 121.3989 | 121.4584 | -0.064087 | -0.09613 | 0.13733 | 0.013733 | 0 | 0.24719 | 0.27924 | 0.2655 | -0.3067 | 0.10071 | 0.068665 | -0.082397 | 0.2243 | 0.11444 | 0.045776 | -0.022888 | 121.6461 | 121.3394 | 4.1519 | -121.6324 | 121.5637 | 121.6232 | 0.3479 | -121.5775
980.125 | 121.5317 | -0.16022 | 121.4447 | -0.00099167 | 0.0098822 | 0.069284 | 0.0029886 | 0.063643 | 0.00093576 | -0.0035846 | 0.014572 | -0.00086724 | 0.060611 | 0.063591 | -0.0096259 | -0.0078783 | 121.1929 | 0.073242 | 3.9642 | 0.10529 | 121.5088 | -0.041199 | -0.16479 | 0.054932 | 0.17853 | -0.050354 | 121.4035 | 121.4447 | -0.045776 | -0.10986 | 0.11902 | -0.004578 | 0.064087 | 0.23346 | 0.2655 | 0.27008 | -0.25177 | 0.11444 | 0.050354 | -0.041199 | 0.21515 | 0.10986 | 0.059509 | 0 | 121.669 | 121.3531 | 4.1245 | -121.6095 | 121.5637 | 121.6049 | 0.33874 | -121.5546
981.7969 | 121.5271 | -0.13733 | 121.4722 | 0.0066373 | 0.013514 | 0.074198 | 0.0023476 | 0.063856 | -0.0056866 | -0.0025164 | 0.0069425 | -0.0027898 | 0.062107 | 0.061669 | -0.0096259 | -0.0055285 | 121.1151 | 0.009155 | 3.9322 | 0.068665 | 121.5179 | -0.054932 | -0.19684 | -0.013733 | 0.13733 | -0.10071 | 121.4081 | 121.463 | -0.050354 | -0.1236 | 0.082397 | -0.059509 | 0.045776 | 0.14648 | 0.20599 | 0.2655 | -0.35706 | 0.086975 | 0.013733 | -0.064087 | 0.1236 | 0.036621 | 0.022888 | -0.009155 | 121.6553 | 121.2524 | 4.0695 | -121.669 | 121.5454 | 121.6003 | 0.27466 | -121.5958
983.5469 | 121.5271 | -0.16479 | 121.4584 | 0.0066373 | 0.012232 | 0.070993 | 0.003843 | 0.062574 | 0.001363 | -0.004439 | -0.00068649 | 0.00041436 | 0.064029 | 0.065514 | -0.0074897 | -0.0053149 | 121.1975 | 0.07782 | 3.9871 | 0.10071 | 121.4905 | -0.041199 | -0.16022 | 0.073242 | 0.17853 | -0.059509 | 121.3989 | 121.463 | -0.073242 | -0.11902 | 0.1236 | 0.004578 | 0.032044 | 0.24261 | 0.2655 | 0.26093 | -0.26093 | 0.091553 | 0.045776 | -0.059509 | 0.23804 | 0.10529 | 0.05951 | 0.004578 | 121.6553 | 121.3623 | 4.1519 | -121.6187 | 121.5637 | 121.6278 | 0.34332 | -121.5775
985.2812 | 121.5591 | -0.14191 | 121.4676 | 0.0066373 | 0.013087 | 0.072702 | 0.0059792 | 0.060652 | -0.0022686 | -0.0057208 | 0.0069425 | -0.00086724 | 0.062534 | 0.063378 | -0.011762 | -0.0068103 | 121.1151 | 0.004578 | 3.9322 | 0.064087 | 121.5363 | -0.068665 | -0.17395 | 0 | 0.14648 | -0.10071 | 121.4218 | 121.4905 | -0.073242 | -0.11902 | 0.073242 | -0.032043 | 0.068665 | 0.14649 | 0.20599 | 0.23804 | -0.35248 | 0.068665 | 0.022888 | -0.045776 | 0.14191 | 0.041199 | 0.018311 | 0.022889 | 121.6782 | 121.257 | 4.0741 | -121.6415 | 121.5637 | 121.6324 | 0.28839 | -121.5866
986.9531 | 121.6324 | -0.10529 | 121.4539 | -0.00099167 | 0.0034736 | 0.068003 | 0.005552 | 0.063429 | 0.0049946 | -0.0023028 | -0.008316 | 0.0027644 | 0.063816 | 0.0653 | -0.0074897 | -0.0095873 | 121.138 | -0.027466 | 3.9368 | 0.059509 | 121.5363 | -0.086975 | -0.19684 | 0 | 0.16022 | -0.14648 | 121.4264 | 121.4813 | -0.091553 | -0.12817 | 0.018311 | -0.091552 | 0.082398 | 0.07782 | 0.16479 | 0.25635 | -0.31586 | 0.013733 | -0.022888 | -0.027465 | 0.10529 | -0.041198 | -0.01831 | 0.027466 | 121.6415 | 121.2433 | 4.0421 | -121.6507 | 121.5317 | 121.5866 | 0.2655 | -121.582
988.625 | 121.4951 | -0.1831 | 121.463 | 0.0066373 | 0.012232 | 0.075693 | 0.0032022 | 0.065138 | -0.00077324 | -0.0042254 | 0.0069425 | -0.0010808 | 0.059757 | 0.061882 | -0.010267 | -0.0074511 | 121.1334 | 0.068665 | 3.9871 | 0.07782 | 121.5088 | -0.041199 | -0.15564 | 0.009155 | 0.16022 | -0.091553 | 121.3989 | 121.4493 | -0.086975 | -0.10529 | 0.14191 | 0.027465 | 0.045776 | 0.25177 | 0.26092 | 0.23346 | -0.32959 | 0.09613 | 0.077819 | -0.064087 | 0.19226 | 0.091552 | 0.013733 | -0.013733 | 121.6919 | 121.3165 | 4.1702 | -121.6187 | 121.582 | 121.6324 | 0.34332 | -121.5683
990.375 | 121.5225 | -0.14191 | 121.4722 | 0.0066373 | 0.0041144 | 0.068857 | 0.0042702 | 0.064497 | 0.002431 | -0.0029436 | 0.0069425 | 0.0031916 | 0.062748 | 0.063378 | -0.0049261 | -0.0089465 | 121.1517 | 0 | 3.9597 | 0.041199 | 121.5225 | -0.086975 | -0.18768 | -0.004578 | 0.12817 | -0.16479 | 121.4493 | 121.4722 | -0.091553 | -0.12817 | 0.054932 | -0.045776 | 0.050354 | 0.14191 | 0.18311 | 0.22888 | -0.32044 | 0.050354 | 0.013733 | -0.022888 | 0.13733 | -0.022888 | -0.036621 | 0 | 121.6644 | 121.2936 | 4.1016 | -121.6599 | 121.5912 | 121.6141 | 0.27008 | -121.6003
992.1094 | 121.5729 | -0.15564 | 121.4493 | -0.00099167 | 0.0096686 | 0.071421 | 0.005552 | 0.065779 | -0.00077324 | -0.0023028 | 0.0069425 | -0.00022644 | 0.064243 | 0.063805 | -0.010908 | -0.0080921 | 121.0602 | -0.022888 | 3.9322 | 0.013733 | 121.5363 | -0.10071 | -0.20599 | -0.073242 | 0.13275 | -0.1831 | 121.463 | 121.4493 | -0.10986 | -0.14648 | 0.054932 | -0.050354 | 0.086975 | 0.13275 | 0.16937 | 0.21973 | -0.3891 | 0.045777 | 0.009156 | 0.013733 | 0.082398 | -0.027465 | -0.036621 | 0 | 121.6919 | 121.2158 | 4.0878 | -121.6553 | 121.6187 | 121.6049 | 0.28839 | -121.5958
993.8125 | 121.6003 | -0.12817 | 121.4401 | 0.0066373 | 0.0090278 | 0.071634 | 0.0070474 | 0.065565 | -0.0024822 | -0.0031574 | -0.008316 | -0.0051398 | 0.06467 | 0.064659 | -0.010908 | -0.0065967 | 121.1517 | 0.13275 | 4.0329 | 0.10071 | 121.4951 | -0.064087 | -0.15564 | 0.050354 | 0.26093 | -0.022888 | 121.4172 | 121.4172 | -0.059509 | -0.11902 | 0.064087 | -0.027466 | 0.054931 | 0.26093 | 0.22888 | 0.25635 | -0.28839 | 0.068665 | 0.009155 | -0.022889 | 0.17853 | 0.10529 | 0.096131 | -0.022889 | 121.6232 | 121.2799 | 4.1611 | -121.5958 | 121.5454 | 121.5454 | 0.3891 | -121.5591
995.5469 | 121.5042 | -0.17853 | 121.4493 | 0.014267 | 0.0036872 | 0.07078 | 0.003843 | 0.063002 | 0.0026446 | -0.0012346 | 0.0069425 | 0.0016962 | 0.062107 | 0.066368 | -0.0049261 | -0.0083057 | 121.0785 | -0.07782 | 3.8956 | 0.013733 | 121.5408 | -0.091553 | -0.20142 | -0.068665 | 0.054932 | -0.20599 | 121.4951 | 121.4722 | -0.09613 | -0.13733 | 0.086975 | -0.022888 | 0.091553 | 0.10071 | 0.19226 | 0.21515 | -0.37079 | 0.082398 | 0.041199 | 0.045776 | 0.10986 | -0.027466 | -0.068665 | 0.022888 | 121.7194 | 121.257 | 4.0741 | -121.6507 | 121.6736 | 121.6507 | 0.23346 | -121.5866
997.2344 | 121.4676 | -0.16022 | 121.4951 | 0.0066373 | 0.010523 | 0.074411 | 0.005552 | 0.063643 | -0.0018414 | -0.001021 | 0.0069425 | -0.0036444 | 0.062534 | 0.062737 | -0.0089849 | -0.0053149 | 121.1655 | 0.07782 | 4.0054 | 0.086975 | 121.4951 | -0.068665 | -0.14648 | 0.013733 | 0.1831 | -0.059509 | 121.3852 | 121.463 | -0.059509 | -0.11444 | 0.091552 | 0.013733 | 0 | 0.23804 | 0.24719 | 0.23346 | -0.32959 | 0.10071 | 0.045776 | -0.10986 | 0.17395 | 0.10071 | 0.054932 | -0.032043 | 121.6553 | 121.3257 | 4.1656 | -121.6415 | 121.5454 | 121.6232 | 0.34332 | -121.6095
998.9844 | 121.6278 | -0.11902 | 121.431 | 0.0066373 | 0.011805 | 0.074411 | 0.005552 | 0.063002 | -0.005473 | -0.0052936 | -0.00068649 | -0.00022644 | 0.060825 | 0.062737 | -0.011549 | -0.0074511 | 121.1792 | 0.10986 | 4.0146 | 0.091553 | 121.5317 | -0.054932 | -0.16937 | 0.059509 | 0.2655 | -0.009155 | 121.3943 | 121.4401 | -0.054932 | -0.11444 | 0.064087 | -0.050354 | 0.10071 | 0.22888 | 0.21057 | 0.26093 | -0.25177 | 0.064087 | 0.004578 | -0.036621 | 0.17853 | 0.10986 | 0.10529 | 0.009156 | 121.6507 | 121.2982 | 4.1336 | -121.6003 | 121.5134 | 121.5591 | 0.38452 | -121.5454
1000.7188 | 121.5408 | -0.15564 | 121.4813 | -0.00099167 | 0.0096686 | 0.069498 | 0.0046976 | 0.06172 | 0.003072 | -0.0020892 | -0.008316 | 0.00041436 | 0.062961 | 0.064019 | -0.0059943 | -0.0085193 | 121.138 | 0.013733 | 3.9551 | 0.045776 | 121.5271 | -0.054932 | -0.17395 | 0.036621 | 0.16022 | -0.082397 | 121.431 | 121.4539 | -0.068665 | -0.091553 | 0.10071 | -0.01831 | 0.045777 | 0.16937 | 0.20142 | 0.21973 | -0.34332 | 0.086975 | 0.064087 | -0.050354 | 0.19226 | 0.073243 | 0.009156 | -0.027466 | 121.6827 | 121.2936 | 4.1107 | -121.6553 | 121.5866 | 121.6095 | 0.31586 | -121.5729
1002.4688 | 121.5866 | -0.12817 | 121.4355 | 0.014267 | 0.009455 | 0.071848 | 0.0079018 | 0.064497 | -0.0033368 | -0.0048662 | -0.00068649 | -0.0019354 | 0.063816 | 0.063805 | -0.011335 | -0.0085193 | 121.2204 | 0.11902 | 4.0649 | 0.10986 | 121.5042 | -0.059509 | -0.15564 | 0.064087 | 0.26093 | -0.032043 | 121.3989 | 121.4676 | -0.064087 | -0.10986 | 0.068665 | -0.027466 | 0.068664 | 0.24719 | 0.23804 | 0.2655 | -0.21515 | 0.064087 | 0.018311 | -0.036621 | 0.19226 | 0.096131 | 0.07782 | 0.032043 | 121.6324 | 121.3486 | 4.1931 | -121.5912 | 121.5271 | 121.5958 | 0.3891 | -121.5454
1004.2188 | 121.5179 | -0.16937 | 121.4676 | -0.0086212 | 0.0092414 | 0.070353 | 0.002775 | 0.060652 | -0.00055964 | -0.0046526 | 0.022202 | -0.00065364 | 0.062961 | 0.06231 | -0.0062079 | -0.0087329 | 121.1975 | 0.07782 | 4.0192 | 0.11444 | 121.4951 | -0.059509 | -0.14648 | 0.050354 | 0.20142 | -0.064087 | 121.3898 | 121.4447 | -0.073242 | -0.09613 | 0.10986 | 0.022889 | 0.027466 | 0.24719 | 0.28381 | 0.26093 | -0.27008 | 0.096131 | 0.073243 | -0.077819 | 0.21973 | 0.10529 | 0.032043 | -0.022888 | 121.6644 | 121.3669 | 4.1885 | -121.6141 | 121.5591 | 121.6141 | 0.37079 | -121.5637
1005.9062 | 121.5271 | -0.16479 | 121.4813 | -0.016251 | 0.014582 | 0.074411 | 0.005552 | 0.059156 | -0.0039776 | -0.0037982 | 0.022202 | -0.0023626 | 0.060825 | 0.061455 | -0.0087713 | -0.0042467 | 121.1197 | 0.022888 | 3.978 | 0.059509 | 121.5134 | -0.059509 | -0.17395 | -0.022888 | 0.13275 | -0.07782 | 121.4081 | 121.4493 | -0.068665 | -0.1236 | 0.10529 | -0.009155 | 0.032044 | 0.18768 | 0.2243 | 0.23346 | -0.36163 | 0.09613 | 0.041199 | -0.073242 | 0.14191 | 0.086975 | 0.045776 | -0.032043 | 121.6782 | 121.2845 | 4.1428 | -121.6553 | 121.5729 | 121.6141 | 0.29755 | -121.6049
1007.6406 | 121.5225 | -0.15564 | 121.4813 | -0.00099167 | 0.0075324 | 0.071848 | 0.0053384 | 0.062361 | 0.0032856 | -0.0037982 | 0.014572 | 0.0010554 | 0.06467 | 0.064232 | -0.0059943 | -0.0068103 | 121.0739 | -0.064087 | 3.9185 | 0.022888 | 121.582 | -0.086975 | -0.20599 | -0.054932 | 0.045776 | -0.20142 | 121.4584 | 121.4767 | -0.10071 | -0.15106 | 0.068665 | -0.050354 | 0.10071 | 0.091553 | 0.17853 | 0.22888 | -0.40741 | 0.054932 | 0.004578 | -0.022888 | 0.10071 | -0.045776 | -0.050354 | -0.004577 | 121.7377 | 121.2296 | 4.0741 | -121.6873 | 121.6141 | 121.6324 | 0.20142 | -121.6324
1009.3906 | 121.5729 | -0.14191 | 121.4813 | -0.00099167 | 0.009455 | 0.069925 | 0.0068338 | 0.063215 | -0.005473 | -0.0035846 | 0.014572 | -0.0027898 | 0.063388 | 0.063591 | -0.010694 | -0.0051013 | 121.1151 | 0.027466 | 3.9688 | 0.068665 | 121.5225 | -0.059509 | -0.17395 | -0.009155 | 0.16022 | -0.082397 | 121.4081 | 121.4676 | -0.068665 | -0.10986 | 0.082398 | -0.032043 | 0.041199 | 0.16937 | 0.21057 | 0.24261 | -0.36621 | 0.073242 | 0.032044 | -0.073242 | 0.13275 | 0.05951 | 0.027466 | -0.013733 | 121.6644 | 121.257 | 4.1107 | -121.6553 | 121.55 | 121.6095 | 0.30212 | -121.5912
1011.0625 | 121.5775 | -0.11902 | 121.463 | 0.0066373 | 0.0083868 | 0.07313 | 0.0044838 | 0.065565 | 0.00072196 | -0.0046526 | -0.008316 | 0.00062796 | 0.064029 | 0.065728 | -0.010053 | -0.0059557 | 121.1105 | -0.013733 | 3.9734 | 0.032043 | 121.5363 | -0.091553 | -0.19226 | -0.059509 | 0.12817 | -0.16022 | 121.4539 | 121.4767 | -0.10986 | -0.14191 | 0.027466 | -0.073242 | 0.073242 | 0.10529 | 0.15106 | 0.2243 | -0.35248 | 0.009156 | -0.022888 | -0.009156 | 0.05951 | -0.041198 | -0.01831 | 0.013733 | 121.6553 | 121.2296 | 4.0924 | -121.6553 | 121.5729 | 121.5958 | 0.24719 | -121.6049
1012.7969 | 121.6278 | -0.10986 | 121.4355 | 0.021896 | 0.013087 | 0.073771 | 0.0034158 | 0.062361 | -0.0035504 | -0.0052936 | 0.0069425 | -0.0017218 | 0.059757 | 0.064232 | -0.012617 | -0.0095873 | 121.17 | 0.059509 | 4.0283 | 0.10986 | 121.5317 | -0.045776 | -0.15564 | 0.050354 | 0.23346 | -0.041199 | 121.4081 | 121.4493 | -0.059509 | -0.10529 | 0.064087 | -0.045777 | 0.09613 | 0.16937 | 0.21973 | 0.2655 | -0.2655 | 0.050354 | 0.004577 | -0.027466 | 0.16022 | 0.068664 | 0.064087 | 0.013733 | 121.6415 | 121.2799 | 4.1382 | -121.5912 | 121.5179 | 121.5591 | 0.34332 | -121.5408
1014.5469 | 121.5363 | -0.17853 | 121.4813 | 0.014267 | 0.0088142 | 0.073343 | 0.00085245 | 0.062147 | 0.0052082 | -0.0018756 | 0.0069425 | 0.0025508 | 0.06232 | 0.066582 | -0.0053533 | -0.0068103 | 121.0968 | -0.068665 | 3.9139 | 0.013733 | 121.5683 | -0.068665 | -0.21057 | -0.050354 | 0.054932 | -0.18768 | 121.4767 | 121.4951 | -0.10071 | -0.16022 | 0.10986 | -0.032043 | 0.086975 | 0.10986 | 0.19226 | 0.2243 | -0.38452 | 0.07782 | 0.018311 | -0.004577 | 0.12817 | -0.009155 | -0.027466 | 0.013733 | 121.7468 | 121.2753 | 4.0924 | -121.6919 | 121.6553 | 121.6736 | 0.23346 | -121.6415
1016.2344 | 121.5958 | -0.12817 | 121.4172 | 0.014267 | 0.0047552 | 0.071207 | 0.0076882 | 0.06407 | -0.0014142 | -0.004439 | -0.00068649 | -0.00065364 | 0.063388 | 0.063591 | -0.0096259 | -0.0076647 | 121.0693 | -0.018311 | 3.9642 | 0.018311 | 121.5408 | -0.09613 | -0.20142 | -0.073242 | 0.1236 | -0.17395 | 121.4722 | 121.4813 | -0.11444 | -0.14191 | 0.032044 | -0.073242 | 0.1236 | 0.10986 | 0.14649 | 0.21973 | -0.3479 | 0.013733 | -0.013733 | 0.054932 | 0.054932 | -0.045776 | -0.032043 | 0.064087 | 121.669 | 121.1975 | 4.0924 | -121.6187 | 121.6003 | 121.6095 | 0.25177 | -121.5591
1017.9688 | 121.4996 | -0.16479 | 121.4722 | -0.00099167 | 0.011805 | 0.072275 | 0.0032022 | 0.060652 | -0.0029094 | -0.0040118 | -0.00068649 | -0.0017218 | 0.062107 | 0.061882 | -0.0091985 | -0.0074511 | 121.1334 | 0.059509 | 4.0146 | 0.050354 | 121.5546 | -0.050354 | -0.16937 | -0.004578 | 0.15106 | -0.091553 | 121.4218 | 121.431 | -0.073242 | -0.1236 | 0.11444 | -0.004578 | 0.082397 | 0.2243 | 0.21515 | 0.21973 | -0.33875 | 0.091553 | 0.041199 | -0.050354 | 0.16022 | 0.073242 | 0.032043 | -0.041199 | 121.7194 | 121.2982 | 4.1794 | -121.6415 | 121.5866 | 121.5958 | 0.31586 | -121.5958
1019.7188 | 121.4722 | -0.15564 | 121.4813 | 0.014267 | 0.011591 | 0.072489 | 0.0036294 | 0.064283 | -0.00055964 | -0.0020892 | 0.0069425 | -0.00022644 | 0.062748 | 0.061669 | -0.0053533 | -0.0068103 | 121.1884 | 0.10986 | 4.0604 | 0.091553 | 121.5134 | -0.036621 | -0.16479 | 0.073242 | 0.18768 | -0.050354 | 121.4218 | 121.4264 | -0.064087 | -0.11444 | 0.11902 | -0.009155 | 0.032044 | 0.2655 | 0.24719 | 0.25635 | -0.29297 | 0.091553 | 0.041199 | -0.059509 | 0.22888 | 0.10529 | 0.064087 | -0.054931 | 121.669 | 121.344 | 4.216 | -121.6461 | 121.5775 | 121.582 | 0.34332 | -121.5958
1021.4688 | 121.6232 | -0.11444 | 121.4355 | 0.0066373 | 0.0041144 | 0.070353 | 0.0046976 | 0.062574 | 0.0049946 | -0.0035846 | -0.008316 | 0.0021234 | 0.063816 | 0.064232 | -0.0068487 | -0.0078783 | 121.1472 | 0 | 4.0283 | 0.068665 | 121.5591 | -0.09613 | -0.19226 | -0.013733 | 0.16937 | -0.12817 | 121.4813 | 121.4722 | -0.10529 | -0.11902 | 0.018311 | -0.07782 | 0.1236 | 0.11444 | 0.18311 | 0.26093 | -0.28839 | 0.009155 | -0.004578 | 0.045776 | 0.10071 | -0.013733 | -0.009155 | 0.036621 | 121.6736 | 121.2616 | 4.1428 | -121.6278 | 121.5958 | 121.5866 | 0.28381 | -121.5546
1023.1406 | 121.5042 | -0.17395 | 121.4539 | 0.014267 | 0.0066778 | 0.072489 | 0.0025612 | 0.061934 | 0.003072 | -0.0018756 | 0.0069425 | 0.001269 | 0.062107 | 0.064019 | -0.0057807 | -0.0061695 | 121.0831 | -0.07782 | 3.9413 | 0.009155 | 121.5683 | -0.068665 | -0.20599 | -0.054932 | 0.073242 | -0.21057 | 121.463 | 121.4722 | -0.09613 | -0.13275 | 0.10528 | -0.032044 | 0.11444 | 0.09613 | 0.1831 | 0.21515 | -0.37079 | 0.07782 | 0.041199 | 0.009156 | 0.11902 | -0.036621 | -0.07782 | 0.018311 | 121.7422 | 121.257 | 4.1153 | -121.6599 | 121.637 | 121.6461 | 0.24719 | -121.5866
1024.875 | 121.4951 | -0.16022 | 121.4722 | 0.014267 | 0.012873 | 0.072062 | 0.0019204 | 0.061079 | -0.0012006 | -0.00273 | 0.022202 | -0.0025762 | 0.061252 | 0.064873 | -0.0085577 | -0.0057421 | 121.1746 | 0.091553 | 4.0695 | 0.10529 | 121.5042 | -0.041199 | -0.14648 | 0.050354 | 0.20142 | -0.027466 | 121.3989 | 121.4401 | -0.059509 | -0.11444 | 0.11902 | 0.013733 | 0.032043 | 0.25177 | 0.2655 | 0.25177 | -0.29755 | 0.10071 | 0.045776 | -0.073242 | 0.21057 | 0.13275 | 0.086975 | -0.032043 | 121.6644 | 121.3348 | 4.2297 | -121.6187 | 121.5591 | 121.6003 | 0.36163 | -121.5866
1026.6094 | 121.5775 | -0.1236 | 121.4493 | -0.00099167 | 0.0071052 | 0.072702 | 0.010465 | 0.061079 | -0.0041912 | -0.0040118 | 0.0069425 | -0.0015082 | 0.065311 | 0.0653 | -0.012189 | -0.0048877 | 121.1426 | 0.068665 | 4.0466 | 0.082397 | 121.5225 | -0.073242 | -0.18768 | -0.041199 | 0.17395 | -0.1236 | 121.4447 | 121.4767 | -0.086975 | -0.14191 | 0.050354 | -0.064087 | 0.073242 | 0.19226 | 0.20599 | 0.27008 | -0.3067 | 0.036621 | -0.018311 | -0.004578 | 0.082397 | 0 | 0.018311 | 0.027466 | 121.6461 | 121.2662 | 4.1702 | -121.637 | 121.5683 | 121.6003 | 0.29755 | -121.5912
1028.2969 | 121.5134 | -0.16479 | 121.4905 | -0.00099167 | 0.006037 | 0.07078 | 0.0051248 | 0.065565 | 0.0020038 | -0.0012346 | -0.00068649 | 0.0014826 | 0.063602 | 0.065087 | -0.0059943 | -0.0089465 | 121.1151 | -0.027466 | 3.9825 | 0.022888 | 121.5866 | -0.086975 | -0.19684 | -0.045776 | 0.091553 | -0.20142 | 121.4722 | 121.4859 | -0.10529 | -0.15106 | 0.07782 | -0.032043 | 0.09613 | 0.13733 | 0.18768 | 0.21973 | -0.37537 | 0.059509 | 0.013733 | -0.018311 | 0.11902 | -0.036621 | -0.050354 | -0.004578 | 121.7514 | 121.2799 | 4.1473 | -121.6873 | 121.637 | 121.6507 | 0.25635 | -121.6415
1030.0469 | 121.5088 | -0.1831 | 121.4905 | 0.014267 | 0.0056098 | 0.070353 | 0.0032022 | 0.061934 | 0.002431 | -0.0012346 | -0.00068649 | 0.0021234 | 0.065525 | 0.064659 | -0.0081305 | -0.0070239 | 121.0602 | -0.068665 | 3.9322 | 0 | 121.5637 | -0.10071 | -0.19684 | -0.068665 | 0.059509 | -0.19684 | 121.4584 | 121.4859 | -0.10986 | -0.15564 | 0.082397 | -0.013733 | 0.073242 | 0.11444 | 0.1831 | 0.19684 | -0.4303 | 0.073242 | 0.027465 | -0.032044 | 0.11444 | -0.013733 | -0.041198 | -0.004578 | 121.7468 | 121.2433 | 4.1153 | -121.6873 | 121.6415 | 121.669 | 0.24261 | -121.6461
1031.7969 | 121.5637 | -0.13275 | 121.4584 | -0.00099167 | 0.0028326 | 0.069925 | 0.0036294 | 0.065779 | 0.0022174 | -0.0014484 | 0.014572 | 0.0014826 | 0.061893 | 0.063805 | -0.0062079 | -0.0051013 | 121.138 | 0.036621 | 4.0283 | 0.059509 | 121.5546 | -0.091553 | -0.19684 | -0.018311 | 0.15564 | -0.14191 | 121.4447 | 121.4767 | -0.091553 | -0.13733 | 0.041198 | -0.064087 | 0.09613 | 0.16937 | 0.19226 | 0.25635 | -0.32043 | 0.041198 | -0.004578 | -0.013733 | 0.11444 | -0.009156 | -0.004578 | 0.018311 | 121.6873 | 121.2708 | 4.1611 | -121.6553 | 121.5775 | 121.6095 | 0.28839 | -121.5958
1033.5469 | 121.4996 | -0.16022 | 121.4813 | 0.014267 | 0.006037 | 0.072702 | 0.0034158 | 0.062147 | 0.00050836 | -0.0048662 | -0.00068649 | 0.002337 | 0.063816 | 0.063805 | -0.0083441 | -0.0061695 | 121.0831 | -0.004578 | 4.0054 | 0.041199 | 121.5591 | -0.091553 | -0.19226 | -0.064087 | 0.086975 | -0.19226 | 121.4584 | 121.4951 | -0.10529 | -0.15106 | 0.068664 | -0.032044 | 0.07782 | 0.15564 | 0.20142 | 0.23346 | -0.39825 | 0.054931 | 0.009155 | -0.022888 | 0.09613 | -0.032044 | -0.041199 | 0.013733 | 121.7194 | 121.2433 | 4.1656 | -121.6736 | 121.6187 | 121.6553 | 0.24719 | -121.6324
1035.2344 | 121.6278 | -0.10986 | 121.4218 | -0.00099167 | 0.012659 | 0.071634 | 0.0087564 | 0.061079 | -0.0067548 | -0.0040118 | -0.00068649 | -0.0044988 | 0.062107 | 0.063805 | -0.012617 | -0.0042467 | 121.1197 | 0.091553 | 4.0741 | 0.10071 | 121.5317 | -0.041199 | -0.16022 | 0.022888 | 0.23346 | -0.022888 | 121.431 | 121.4676 | -0.050354 | -0.09613 | 0.068664 | -0.050354 | 0.10986 | 0.20142 | 0.21057 | 0.26093 | -0.30212 | 0.059509 | 0.013733 | 0.009155 | 0.13275 | 0.086975 | 0.073242 | 0.045776 | 121.6415 | 121.2296 | 4.184 | -121.582 | 121.5408 | 121.5775 | 0.34332 | -121.5179
1036.9688 | 121.5454 | -0.15564 | 121.4722 | 0.0066373 | 0.009455 | 0.069712 | 0.003843 | 0.060865 | 0.00072196 | -0.0040118 | 0.0069425 | 0.002337 | 0.063175 | 0.062523 | -0.0077033 | -0.0072375 | 121.0831 | -0.041199 | 3.9734 | 0.013733 | 121.5591 | -0.086975 | -0.20599 | -0.068665 | 0.068665 | -0.16937 | 121.4539 | 121.4951 | -0.09613 | -0.13733 | 0.068665 | -0.050354 | 0.086975 | 0.11444 | 0.16937 | 0.21973 | -0.3891 | 0.05951 | 0.018311 | -0.018311 | 0.086975 | -0.013733 | -0.032044 | 0.022888 | 121.7148 | 121.2387 | 4.129 | -121.6782 | 121.6095 | 121.6507 | 0.22431 | -121.6095
1038.6562 | 121.6141 | -0.14191 | 121.4264 | 0.014267 | 0.0086006 | 0.069925 | 0.0074746 | 0.061293 | -0.0046184 | -0.003371 | 0.014572 | -0.0034308 | 0.065097 | 0.063591 | -0.014112 | -0.0055285 | 121.1929 | 0.10986 | 4.1061 | 0.09613 | 121.5088 | -0.059509 | -0.16022 | 0.027466 | 0.29755 | -0.018311 | 121.4218 | 121.4722 | -0.07782 | -0.10986 | 0.082398 | -0.01831 | 0.082397 | 0.25177 | 0.23804 | 0.25635 | -0.23346 | 0.064087 | 0.032044 | -0.004578 | 0.16937 | 0.1236 | 0.091552 | 0.045776 | 121.6507 | 121.3348 | 4.248 | -121.5866 | 121.5637 | 121.6141 | 0.43945 | -121.5363
1040.4062 | 121.6095 | -0.11444 | 121.4447 | -0.00099167 | 0.010737 | 0.071848 | 0.0076882 | 0.062788 | -0.0033368 | -0.0035846 | -0.00068649 | -0.0017218 | 0.062107 | 0.063378 | -0.01048 | -0.0074511 | 121.1884 | 0.10986 | 4.0924 | 0.10986 | 121.5179 | -0.059509 | -0.17395 | 0.027466 | 0.25635 | -0.032043 | 121.4035 | 121.4447 | -0.059509 | -0.10529 | 0.054932 | -0.059509 | 0.073242 | 0.2243 | 0.2243 | 0.28381 | -0.25635 | 0.054932 | 0.009155 | -0.041199 | 0.14191 | 0.082398 | 0.073243 | 0 | 121.6324 | 121.3028 | 4.2068 | -121.6187 | 121.5179 | 121.5591 | 0.37079 | -121.55
1042.1406 | 121.5912 | -0.14191 | 121.4722 | 0.014267 | 0.007746 | 0.072489 | 0.0061928 | 0.062788 | -0.0031232 | -0.003371 | 0.0069425 | -0.00065364 | 0.062107 | 0.063591 | -0.0077033 | -0.0072375 | 121.1655 | 0.086975 | 4.1107 | 0.1236 | 121.5271 | -0.068665 | -0.16479 | 0.041199 | 0.25177 | -0.054932 | 121.431 | 121.4722 | -0.073242 | -0.10986 | 0.073242 | -0.022888 | 0.054932 | 0.22888 | 0.2655 | 0.28839 | -0.3067 | 0.068665 | 0.032044 | -0.041199 | 0.18311 | 0.086975 | 0.054931 | 0 | 121.669 | 121.3074 | 4.2526 | -121.637 | 121.5729 | 121.6141 | 0.39368 | -121.582
1043.8906 | 121.5408 | -0.13733 | 121.4676 | -0.00099167 | 0.012232 | 0.070566 | 0.00063865 | 0.062574 | 0.0011494 | -0.0031574 | 0.0069425 | 0.00041436 | 0.059543 | 0.064873 | -0.0072759 | -0.010442 | 121.1838 | 0.045776 | 4.0833 | 0.09613 | 121.55 | -0.036621 | -0.16479 | 0.068665 | 0.18768 | -0.064087 | 121.4035 | 121.4722 | -0.082397 | -0.086975 | 0.10071 | -0.027466 | 0.082398 | 0.18311 | 0.23346 | 0.26092 | -0.28381 | 0.054932 | 0.050354 | -0.064087 | 0.20599 | 0.073242 | 0.022888 | 0.004578 | 121.6873 | 121.3211 | 4.2206 | -121.6324 | 121.5408 | 121.6095 | 0.32501 | -121.5546
1045.6094 | 121.5179 | -0.16937 | 121.5042 | -0.00099167 | 0.0039008 | 0.068644 | 0.0042702 | 0.064497 | 0.0028584 | -0.0031574 | 0.0069425 | 0.0044734 | 0.063816 | 0.0653 | -0.0068487 | -0.0095873 | 121.0968 | -0.059509 | 4.01 | 0.018311 | 121.5637 | -0.091553 | -0.20599 | -0.064087 | 0.073242 | -0.21515 | 121.4539 | 121.5134 | -0.11902 | -0.14191 | 0.07782 | -0.036621 | 0.05951 | 0.10986 | 0.18768 | 0.22431 | -0.40741 | 0.050354 | 0.027466 | -0.050354 | 0.10529 | -0.045776 | -0.073242 | 0.009156 | 121.7331 | 121.2662 | 4.1794 | -121.7102 | 121.6232 | 121.6827 | 0.24261 | -121.6461
1047.2969 | 121.5134 | -0.15564 | 121.4767 | 0.0066373 | 0.010737 | 0.071848 | 0.002134 | 0.062574 | -0.0035504 | -0.0037982 | 0.0069425 | -0.0042852 | 0.062961 | 0.061455 | -0.0066351 | -0.0078783 | 121.17 | 0.082397 | 4.0878 | 0.11444 | 121.5088 | -0.036621 | -0.16022 | 0.059509 | 0.19226 | -0.050354 | 121.4127 | 121.463 | -0.073242 | -0.11902 | 0.11902 | -0.004577 | 0.032043 | 0.23804 | 0.27008 | 0.27466 | -0.3067 | 0.082398 | 0.036621 | -0.064087 | 0.21515 | 0.10529 | 0.068665 | -0.013733 | 121.6644 | 121.3257 | 4.2435 | -121.637 | 121.5683 | 121.6187 | 0.3479 | -121.5958
1049.0469 | 121.6278 | -0.12817 | 121.4035 | -0.00099167 | 0.012659 | 0.075907 | 0.0044838 | 0.05937 | -0.0039776 | -0.00508 | -0.00068649 | -0.0040716 | 0.061039 | 0.061882 | -0.011335 | -0.0053149 | 121.1472 | 0.073242 | 4.0741 | 0.086975 | 121.5271 | -0.059509 | -0.16479 | 0.027466 | 0.23346 | -0.036621 | 121.4081 | 121.463 | -0.068665 | -0.10071 | 0.068665 | -0.036621 | 0.1236 | 0.20142 | 0.21515 | 0.25177 | -0.25635 | 0.059509 | 0.027466 | 0.004578 | 0.15564 | 0.091553 | 0.064087 | 0.05951 | 121.6553 | 121.2753 | 4.2023 | -121.5683 | 121.5363 | 121.5912 | 0.36163 | -121.5042
1050.7344 | 121.5958 | -0.11902 | 121.4355 | -0.016251 | 0.0083868 | 0.073343 | 0.010038 | 0.063215 | -0.002055 | -0.0037982 | -0.00068649 | -0.0023626 | 0.063388 | 0.063164 | -0.011121 | -0.0055285 | 121.1746 | 0.11444 | 4.1336 | 0.10986 | 121.5042 | -0.050354 | -0.15564 | 0.054932 | 0.2655 | -0.027466 | 121.4172 | 121.4584 | -0.073242 | -0.11444 | 0.068665 | -0.036621 | 0.068664 | 0.23346 | 0.22888 | 0.2655 | -0.26093 | 0.045777 | 0.004578 | -0.018311 | 0.17395 | 0.091553 | 0.086975 | 0.022888 | 121.6232 | 121.2936 | 4.2526 | -121.5912 | 121.5363 | 121.5775 | 0.38452 | -121.55
1052.4844 | 121.6141 | -0.1236 | 121.4493 | 0.0066373 | 0.012018 | 0.071634 | 0.0051248 | 0.060011 | -0.0052594 | -0.003371 | -0.00068649 | -0.0032172 | 0.062748 | 0.062523 | -0.010694 | -0.0085193 | 121.1426 | 0.045776 | 4.0878 | 0.082397 | 121.5454 | -0.068665 | -0.16479 | 0.022888 | 0.20599 | -0.041199 | 121.4264 | 121.4722 | -0.050354 | -0.091553 | 0.054931 | -0.041199 | 0.09613 | 0.16937 | 0.20599 | 0.24719 | -0.3067 | 0.073242 | 0.032043 | -0.022888 | 0.14648 | 0.082397 | 0.050354 | 0.022888 | 121.669 | 121.2662 | 4.2114 | -121.6141 | 121.55 | 121.5958 | 0.32959 | -121.5408
1054.2344 | 121.5546 | -0.15564 | 121.4905 | 0.014267 | 0.009455 | 0.070139 | 0.0017068 | 0.062361 | 0.0026446 | -0.00273 | -0.008316 | 0.0021234 | 0.062961 | 0.065514 | -0.0081305 | -0.010228 | 121.1105 | -0.068665 | 4.0009 | 0.018311 | 121.5775 | -0.09613 | -0.20142 | -0.036621 | 0.07782 | -0.17853 | 121.4539 | 121.5042 | -0.10529 | -0.14648 | 0.05951 | -0.045776 | 0.086975 | 0.086975 | 0.17395 | 0.21973 | -0.37994 | 0.050354 | 0.009156 | -0.036622 | 0.11902 | -0.022888 | -0.032044 | 0.013732 | 121.7331 | 121.2662 | 4.1565 | -121.6919 | 121.6095 | 121.6599 | 0.23346 | -121.637
1055.9062 | 121.5866 | -0.13733 | 121.4584 | 0.014267 | 0.0098822 | 0.073771 | 0.0044838 | 0.063215 | -0.0039776 | -0.004439 | 0.014572 | -0.0030034 | 0.063816 | 0.062096 | -0.010053 | -0.0070239 | 121.1105 | 0.027466 | 4.0558 | 0.054932 | 121.5408 | -0.07782 | -0.17853 | 0 | 0.16937 | -0.073242 | 121.4264 | 121.4584 | -0.073242 | -0.10071 | 0.059509 | -0.041199 | 0.082398 | 0.16479 | 0.19226 | 0.23346 | -0.3479 | 0.064087 | 0.036621 | -0.032043 | 0.13733 | 0.064087 | 0.027466 | 0 | 121.6782 | 121.2479 | 4.1931 | -121.637 | 121.5637 | 121.5958 | 0.3067 | -121.5591
1057.6406 | 121.5912 | -0.11444 | 121.4264 | 0.0066373 | 0.0068916 | 0.075479 | 0.0070474 | 0.062147 | -0.00055964 | -0.0055072 | 0.014572 | -0.00044004 | 0.061893 | 0.061455 | -0.0081305 | -0.0085193 | 121.1838 | 0.11902 | 4.1519 | 0.10986 | 121.5225 | -0.059509 | -0.16022 | 0.059509 | 0.26093 | -0.045776 | 121.4081 | 121.4401 | -0.073242 | -0.09613 | 0.054932 | -0.045776 | 0.09613 | 0.23346 | 0.2243 | 0.27008 | -0.24262 | 0.041199 | 0.018311 | -0.018311 | 0.17395 | 0.068665 | 0.050354 | 0.013733 | 121.637 | 121.2982 | 4.2664 | -121.5866 | 121.5225 | 121.5546 | 0.37537 | -121.5225
1059.3281 | 121.5408 | -0.16479 | 121.4722 | 0.0066373 | 0.010523 | 0.068644 | 0.0032022 | 0.061293 | 0.0028584 | -0.0020892 | -0.00068649 | 0.0027644 | 0.062534 | 0.065087 | -0.0070623 | -0.0080921 | 121.1105 | -0.064087 | 4.0192 | 0.013733 | 121.5866 | -0.082397 | -0.21057 | -0.036621 | 0.07782 | -0.1831 | 121.4584 | 121.5225 | -0.10071 | -0.1236 | 0.082398 | -0.045776 | 0.11444 | 0.10071 | 0.17853 | 0.2243 | -0.36163 | 0.064087 | 0.041199 | -0.013733 | 0.12817 | -0.01831 | -0.059509 | 0.050354 | 121.7514 | 121.2753 | 4.184 | -121.6827 | 121.6232 | 121.6873 | 0.24261 | -121.5958
1061.0781 | 121.5637 | -0.14648 | 121.4493 | 0.0066373 | 0.0096686 | 0.072275 | 0.0046976 | 0.062361 | -0.0031232 | -0.0037982 | 0.0069425 | -0.0019354 | 0.063602 | 0.061241 | -0.0083441 | -0.0061695 | 121.1105 | 0.032043 | 4.0466 | 0.059509 | 121.5546 | -0.07782 | -0.17395 | -0.027466 | 0.13733 | -0.09613 | 121.4172 | 121.4401 | -0.07782 | -0.11902 | 0.068664 | -0.027466 | 0.10528 | 0.17853 | 0.20599 | 0.23346 | -0.33875 | 0.068664 | 0.027465 | -0.032044 | 0.11902 | 0.050354 | 0.022889 | -0.009155 | 121.701 | 121.257 | 4.1931 | -121.6232 | 121.5637 | 121.5866 | 0.28381 | -121.5683
1062.7656 | 121.6187 | -0.13275 | 121.4676 | 0.014267 | 0.0133 | 0.069712 | 0.010038 | 0.061506 | -0.0026958 | -0.0042254 | -0.00068649 | -0.0025762 | 0.060611 | 0.0653 | -0.01283 | -0.0072375 | 121.1243 | 0.045776 | 4.0833 | 0.073242 | 121.5454 | -0.064087 | -0.1831 | 0.013733 | 0.19684 | -0.068665 | 121.4081 | 121.4493 | -0.064087 | -0.1236 | 0.068664 | -0.050354 | 0.07782 | 0.17853 | 0.20599 | 0.25635 | -0.34332 | 0.068664 | 0.009155 | -0.059509 | 0.14648 | 0.064086 | 0.054931 | -0.01831 | 121.6782 | 121.257 | 4.216 | -121.6507 | 121.5408 | 121.582 | 0.32959 | -121.5912
1064.5156 | 121.5271 | -0.15106 | 121.4722 | 0.014267 | 0.012018 | 0.072489 | 0.0061928 | 0.061506 | -0.0031232 | -0.0042254 | 0.022202 | -0.0015082 | 0.061039 | 0.061669 | -0.0087713 | -0.0076647 | 121.1288 | 0.018311 | 4.0512 | 0.050354 | 121.5088 | -0.054932 | -0.1831 | 0 | 0.14648 | -0.10529 | 121.4127 | 121.4539 | -0.07782 | -0.13275 | 0.09613 | -0.032043 | 0.036621 | 0.16937 | 0.20142 | 0.23346 | -0.34332 | 0.073242 | 0.018311 | -0.059509 | 0.15106 | 0.045776 | 0.027465 | -0.018311 | 121.6599 | 121.2799 | 4.2023 | -121.6553 | 121.5637 | 121.6049 | 0.29755 | -121.6049
1066.2656 | 121.4951 | -0.16937 | 121.4584 | 0.0066373 | 0.00326 | 0.069712 | 0.0044838 | 0.062361 | 0.0056354 | -0.0012346 | 0.014572 | 0.002337 | 0.063816 | 0.064873 | -0.0062079 | -0.0098009 | 121.1288 | -0.013733 | 4.0878 | 0.045776 | 121.5591 | -0.082397 | -0.21057 | -0.027466 | 0.10986 | -0.20599 | 121.463 | 121.4859 | -0.10529 | -0.15564 | 0.086976 | -0.041198 | 0.10071 | 0.15564 | 0.21515 | 0.25635 | -0.32959 | 0.064087 | 0.013733 | 0.004578 | 0.14191 | -0.036621 | -0.050354 | 0.027466 | 121.7285 | 121.2982 | 4.2572 | -121.669 | 121.6324 | 121.6553 | 0.27924 | -121.6141
1067.9375 | 121.4859 | -0.17853 | 121.4401 | -0.00099167 | 0.012232 | 0.073984 | 0.0040566 | 0.060225 | -0.0041912 | -0.0042254 | -0.00068649 | -0.0027898 | 0.061893 | 0.061241 | -0.0081305 | -0.0063831 | 121.1243 | 0.045776 | 4.1016 | 0.059509 | 121.4951 | -0.068665 | -0.16937 | -0.018311 | 0.16937 | -0.09613 | 121.431 | 121.463 | -0.091553 | -0.12817 | 0.10986 | 0.009155 | 0.054931 | 0.2243 | 0.23804 | 0.22888 | -0.31586 | 0.086975 | 0.050354 | -0.009156 | 0.16022 | 0.082398 | 0.032044 | 0.022888 | 121.6736 | 121.3028 | 4.2801 | -121.6095 | 121.6095 | 121.6415 | 0.3479 | -121.5683
1069.6875 | 121.6095 | -0.14648 | 121.4539 | 0.0066373 | 0.0039008 | 0.071848 | 0.0046976 | 0.062788 | 0.0026446 | -0.0023028 | 0.0069425 | 0.002337 | 0.063388 | 0.062737 | -0.0047125 | -0.0089465 | 121.1243 | 0.004578 | 4.1153 | 0.050354 | 121.5271 | -0.10986 | -0.21515 | -0.004578 | 0.1831 | -0.14191 | 121.4264 | 121.4767 | -0.10986 | -0.14191 | 0.036621 | -0.068665 | 0.073243 | 0.15106 | 0.19684 | 0.2655 | -0.32959 | 0.036621 | 0.004577 | -0.027465 | 0.14191 | 0.004577 | 0 | 0.022889 | 121.6736 | 121.2708 | 4.2618 | -121.669 | 121.5729 | 121.6232 | 0.32959 | -121.5958
1071.4375 | 121.6187 | -0.1236 | 121.4493 | 0.0066373 | 0.004328 | 0.068216 | 0.0036294 | 0.06407 | 0.00414 | -0.001021 | -0.00068649 | 0.001269 | 0.062961 | 0.063805 | -0.0072759 | -0.0078783 | 121.1197 | 0.018311 | 4.1153 | 0.059509 | 121.5546 | -0.082397 | -0.21057 | -0.004578 | 0.18768 | -0.14191 | 121.4539 | 121.4447 | -0.10071 | -0.15564 | 0.041199 | -0.086975 | 0.10528 | 0.14191 | 0.1831 | 0.27008 | -0.32959 | 0.022888 | -0.032044 | 0.004577 | 0.11902 | -0.018311 | 0.013733 | -0.004578 | 121.6782 | 121.2433 | 4.2389 | -121.6599 | 121.5775 | 121.5683 | 0.31128 | -121.6049
1073.1875 | 121.6278 | -0.14648 | 121.4355 | -0.0086212 | 0.004328 | 0.06843 | 0.0061928 | 0.064497 | 0.0022174 | -0.0025164 | 0.0069425 | 0.001269 | 0.063602 | 0.064019 | -0.0064215 | -0.0068103 | 121.106 | 0.018311 | 4.1199 | 0.036621 | 121.5363 | -0.10986 | -0.23346 | -0.022888 | 0.19226 | -0.15564 | 121.4035 | 121.4584 | -0.12817 | -0.14648 | 0.036621 | -0.086975 | 0.10071 | 0.16479 | 0.18311 | 0.27008 | -0.32959 | 0.01831 | 0 | -0.032044 | 0.1236 | -0.009156 | -0.009156 | 0.022888 | 121.6827 | 121.2524 | 4.2664 | -121.669 | 121.55 | 121.6049 | 0.33874 | -121.582
1074.875 | 121.5179 | -0.20142 | 121.431 | 0.0066373 | 0.011805 | 0.071848 | 0.0081154 | 0.059156 | -0.0059002 | -0.0042254 | -0.00068649 | -0.0025762 | 0.064243 | 0.064232 | -0.011976 | -0.0078783 | 121.0419 | -0.004578 | 4.0878 | 0.032043 | 121.4767 | -0.07782 | -0.21515 | -0.068665 | 0.16022 | -0.13275 | 121.3669 | 121.4401 | -0.10986 | -0.14648 | 0.1236 | -0.013733 | 0.045777 | 0.19684 | 0.23346 | 0.24719 | -0.3891 | 0.091553 | 0.054932 | -0.064087 | 0.13275 | 0.068665 | 0.013733 | 0.009156 | 121.6782 | 121.2433 | 4.2892 | -121.6461 | 121.5683 | 121.6415 | 0.36163 | -121.5775
1076.625 | 121.582 | -0.15564 | 121.376 | -0.0086212 | 0.0058234 | 0.072275 | 0.0087564 | 0.063429 | -0.00098684 | -0.0037982 | 0.0069425 | 0.0016962 | 0.062748 | 0.065728 | -0.010053 | -0.0078783 | 121.0144 | -0.068665 | 4.0695 | 0.050354 | 121.4905 | -0.10986 | -0.24719 | -0.12817 | 0.14648 | -0.2243 | 121.431 | 121.4493 | -0.13275 | -0.19226 | 0.045777 | -0.091552 | 0.11444 | 0.086975 | 0.20599 | 0.29755 | -0.36163 | 0.022889 | -0.036621 | 0.054931 | 0.027466 | -0.068664 | -0.032043 | 0.073242 | 121.6461 | 121.17 | 4.2252 | -121.6232 | 121.5866 | 121.6049 | 0.30212 | -121.5683
1078.3594 | 121.5775 | -0.16022 | 121.3806 | -0.00099167 | 0.0051826 | 0.070353 | 0.00897 | 0.061506 | 0.001363 | -0.0055072 | 0.0069425 | 0.00020076 | 0.064884 | 0.064019 | -0.01048 | -0.0055285 | 120.9961 | -0.059509 | 4.0833 | 0 | 121.4905 | -0.11902 | -0.24261 | -0.11444 | 0.14191 | -0.21057 | 121.4035 | 121.4355 | -0.13275 | -0.17853 | 0.041198 | -0.082398 | 0.10986 | 0.10071 | 0.16022 | 0.24261 | -0.38452 | 0.027466 | -0.018311 | 0.022888 | 0.045776 | -0.050354 | -0.032043 | 0.054932 | 121.6507 | 121.1563 | 4.2435 | -121.6232 | 121.5637 | 121.5958 | 0.30212 | -121.5591
1080.1094 | 121.55 | -0.16022 | 121.3715 | 0.014267 | 0.0047552 | 0.070139 | 0.0091836 | 0.065565 | -0.0022686 | -0.00508 | 0.0069425 | 0.0014826 | 0.06467 | 0.064019 | -0.01048 | -0.0065967 | 120.9961 | -0.064087 | 4.0787 | -0.018311 | 121.5134 | -0.12817 | -0.23346 | -0.11444 | 0.13733 | -0.20142 | 121.3898 | 121.4447 | -0.14191 | -0.17395 | 0.032043 | -0.073242 | 0.14191 | 0.09613 | 0.14191 | 0.21515 | -0.37537 | 0.01831 | -0.013733 | 0.018311 | 0.045776 | -0.041199 | -0.027466 | 0.073242 | 121.6736 | 121.1563 | 4.2389 | -121.6049 | 121.55 | 121.6049 | 0.29755 | -121.5454
1081.7812 | 121.4584 | -0.21057 | 121.3898 | 0.0066373 | 0.012659 | 0.072275 | 0.0032022 | 0.061506 | -0.0024822 | -0.0029436 | 0.0069425 | -0.002149 | 0.060184 | 0.063164 | -0.0079169 | -0.0059557 | 121.051 | 0.036621 | 4.1336 | 0.032043 | 121.431 | -0.10071 | -0.18768 | -0.027466 | 0.17853 | -0.11444 | 121.344 | 121.3989 | -0.11902 | -0.14648 | 0.10986 | 0.022888 | 0.041198 | 0.24719 | 0.24261 | 0.21973 | -0.33875 | 0.091552 | 0.064087 | -0.045777 | 0.18311 | 0.09613 | 0.032043 | 0.009155 | 121.6415 | 121.2616 | 4.3442 | -121.5775 | 121.5546 | 121.6095 | 0.3891 | -121.5363
1083.5156 | 121.4996 | -0.20142 | 121.3806 | 0.014267 | 0.0092414 | 0.071207 | 0.0025612 | 0.064711 | 0.0015766 | -0.0052936 | 0.0069425 | 0.0014826 | 0.065311 | 0.064446 | -0.0062079 | -0.0059557 | 121.0052 | -0.09613 | 4.0558 | -0.027466 | 121.4996 | -0.14648 | -0.24261 | -0.086975 | 0.086975 | -0.20599 | 121.3898 | 121.3989 | -0.15106 | -0.17853 | 0.054932 | -0.041199 | 0.11902 | 0.10529 | 0.17395 | 0.21515 | -0.37537 | 0.050354 | 0.022888 | 0.009156 | 0.11444 | -0.004578 | -0.027466 | 0.018311 | 121.701 | 121.2067 | 4.2572 | -121.6232 | 121.5912 | 121.6003 | 0.28839 | -121.5591
1085.25 | 121.582 | -0.16479 | 121.3623 | 0.0066373 | 0.012232 | 0.075266 | 0.0046976 | 0.061506 | -0.0048322 | -0.003371 | 0.014572 | -0.0032172 | 0.061893 | 0.061669 | -0.011549 | -0.0057421 | 121.019 | 0 | 4.129 | 0.027466 | 121.4355 | -0.11444 | -0.21973 | -0.045776 | 0.19684 | -0.10529 | 121.3165 | 121.3806 | -0.11902 | -0.16022 | 0.050354 | -0.054932 | 0.073242 | 0.16479 | 0.19226 | 0.24719 | -0.34332 | 0.045776 | 0.004578 | -0.045777 | 0.11902 | 0.059509 | 0.054931 | 0.01831 | 121.6003 | 121.1838 | 4.2938 | -121.582 | 121.4813 | 121.5454 | 0.36163 | -121.5225
1087 | 121.5408 | -0.2243 | 121.3165 | -0.0086212 | 0.0062506 | 0.075479 | 0.0061928 | 0.062361 | -0.0018414 | -0.0037982 | -0.00068649 | -0.002149 | 0.061466 | 0.061882 | -0.0079169 | -0.0061695 | 121.0144 | 0 | 4.1931 | 0.022888 | 121.4035 | -0.14648 | -0.25635 | -0.064087 | 0.25177 | -0.14648 | 121.3074 | 121.3211 | -0.17395 | -0.19684 | 0.07782 | -0.032044 | 0.086975 | 0.2243 | 0.24719 | 0.27924 | -0.30212 | 0.050354 | 0.027466 | -0.009155 | 0.16022 | 0.07782 | 0.050354 | 0.004578 | 121.6278 | 121.2387 | 4.4174 | -121.5729 | 121.5317 | 121.5454 | 0.47607 | -121.5134
1088.6875 | 121.5591 | -0.15564 | 121.344 | -0.00099167 | 0.0036872 | 0.070993 | 0.005552 | 0.059797 | 0.0032856 | -0.003371 | 0.014572 | 0.0021234 | 0.062961 | 0.065728 | -0.0055671 | -0.0085193 | 121.0648 | -0.004578 | 4.1336 | 0.036621 | 121.5042 | -0.10986 | -0.22888 | -0.032043 | 0.1831 | -0.16022 | 121.376 | 121.4035 | -0.10986 | -0.16937 | 0.045777 | -0.073242 | 0.16022 | 0.15106 | 0.19226 | 0.2655 | -0.27924 | 0.045777 | -0.013733 | 0.032044 | 0.1236 | -0.004577 | 0.009156 | 0.059509 | 121.6599 | 121.2204 | 4.2892 | -121.5729 | 121.5317 | 121.5591 | 0.33874 | -121.5134
1090.4375 | 121.4905 | -0.16479 | 121.3806 | -0.00099167 | 0.0019782 | 0.069284 | 0.0017068 | 0.065138 | 0.0032856 | -0.0035846 | 0.014572 | 0.0016962 | 0.063602 | 0.061455 | -0.0068487 | -0.0076647 | 121.0648 | -0.009155 | 4.1199 | 0.022888 | 121.4951 | -0.09613 | -0.20599 | -0.027466 | 0.16022 | -0.16479 | 121.3898 | 121.4264 | -0.1236 | -0.15564 | 0.068665 | -0.041199 | 0.11444 | 0.15564 | 0.18768 | 0.22888 | -0.31586 | 0.041199 | 0.009155 | 0.009156 | 0.13733 | 0 | -0.009155 | 0.045777 | 121.6599 | 121.2296 | 4.2847 | -121.5866 | 121.5546 | 121.5912 | 0.32501 | -121.5363
1092.1719 | 121.5683 | -0.19226 | 121.3211 | -0.00099167 | 0.0034736 | 0.07078 | 0.0081154 | 0.063002 | 0.00072196 | -0.0048662 | -0.008316 | 0.0014826 | 0.064243 | 0.064659 | -0.0087713 | -0.0078783 | 120.9503 | -0.11444 | 4.0924 | -0.027466 | 121.4264 | -0.15106 | -0.28839 | -0.13275 | 0.13275 | -0.24719 | 121.3348 | 121.4081 | -0.16937 | -0.21515 | 0.041199 | -0.09613 | 0.10529 | 0.07782 | 0.16479 | 0.26093 | -0.37079 | 0.022888 | -0.022888 | 0.013733 | 0.05951 | -0.054931 | -0.032043 | 0.086975 | 121.6187 | 121.1426 | 4.2847 | -121.6095 | 121.5271 | 121.6003 | 0.32501 | -121.5363
1093.9062 | 121.3623 | -1.886 | 119.3573 | -0.00099167 | 0.0045416 | 0.069498 | 0.0076882 | 0.061934 | 0.00029476 | -0.001021 | 0.0069425 | -1.2844e-05 | 0.06232 | 0.063805 | -0.011549 | -0.0085193 | 119.0506 | -1.799 | 3.8864 | -1.7029 | 119.5404 | -1.8539 | -1.9547 | -1.8173 | 0.11902 | -1.9913 | 119.4397 | 119.458 | -1.8814 | -1.918 | 0.032043 | -0.068665 | 0.18311 | 0.086975 | 0.1831 | 0.25177 | -0.3067 | 0.004577 | -0.032044 | 0.082397 | 0.068664 | -0.10529 | -0.073242 | 0.10071 | 121.4264 | 120.9366 | 5.7724 | -121.312 | 121.3257 | 121.344 | 2.005 | -121.2753
1095.6562 | 121.3577 | -0.18768 | 121.3394 | -0.00099167 | 0.0051826 | 0.070353 | 0.0034158 | 0.062788 | 0.002431 | -0.0048662 | 0.014572 | 0.00020076 | 0.061893 | 0.066582 | -0.0066351 | -0.0065967 | 120.9732 | -0.032043 | 4.1016 | 0.027466 | 121.4172 | -0.11902 | -0.21057 | -0.07782 | 0.11902 | -0.21057 | 121.344 | 121.3623 | -0.12817 | -0.16022 | 0.068664 | -0.022888 | 0.077819 | 0.15564 | 0.21515 | 0.23804 | -0.36621 | 0.059509 | 0.027466 | 0.004577 | 0.10986 | -0.022888 | -0.050354 | 0.022888 | 121.6049 | 121.1609 | 4.2892 | -121.55 | 121.5317 | 121.55 | 0.3067 | -121.4996
1097.3906 | 121.3715 | -1.1444 | 120.1859 | 0.014267 | 0.0021918 | 0.073771 | 0.0051248 | 0.060865 | 8.1158e-05 | -0.0012346 | -0.00068649 | 0.0016962 | 0.064884 | 0.064446 | -0.0053533 | -0.0057421 | 120.2454 | -0.70496 | 4.0237 | -0.68207 | 120.6436 | -0.81482 | -0.92468 | -0.69122 | 0.15106 | -0.75531 | 120.607 | 120.6848 | -0.70038 | -0.70953 | 0.32959 | 0.21973 | 0.45776 | 0.43945 | 0.46234 | 0.24262 | 0.059509 | 0.44403 | 0.43488 | 0.42114 | 0.45319 | 0.3891 | -0.045776 | 0.49896 | 121.788 | 121.3898 | 5.1682 | -121.1105 | 121.7514 | 121.8292 | 1.2955 | -120.8954
1099.0625 | 121.1975 | -1.9958 | 119.2566 | 0.014267 | 0.011378 | 0.072702 | 0.0029886 | 0.060438 | -0.0041912 | -0.0042254 | 0.0069425 | -0.0032172 | 0.059543 | 0.061882 | -0.0077033 | -0.0044605 | 119.0231 | -1.7441 | 3.7628 | -1.6983 | 119.3848 | -1.8311 | -1.9226 | -1.7258 | 0.07782 | -1.9455 | 119.252 | 119.3344 | -1.8585 | -1.8997 | 0.16479 | 0.073243 | 0.12817 | 0.25177 | 0.29755 | 0.2243 | -0.23346 | 0.13733 | 0.096131 | -0.004578 | 0.27008 | 0.050354 | -0.045777 | 0.07782 | 121.3806 | 121.019 | 5.7587 | -121.1792 | 121.2479 | 121.3303 | 2.0737 | -121.1563
1100.7969 | 121.0876 | -43.4326 | 77.8061 | -0.00099167 | 0.015223 | 0.073343 | 0.001066 | 0.061293 | -0.0061138 | -0.0052936 | 0.0069425 | -0.0015082 | 0.060398 | 0.062096 | -0.0098395 | -0.0053149 | 77.4353 | -43.4692 | 1.3641 | -43.4464 | 77.4399 | -43.634 | -43.5837 | -43.8126 | 0.7782 | -43.5516 | 77.623 | 77.7145 | -43.3136 | -43.5562 | -0.20142 | -0.15106 | -0.36621 | -0.036621 | -0.013733 | 0.13733 | -0.37079 | 0.11902 | -0.1236 | -0.1831 | -0.37994 | -0.11902 | 0.004577 | -0.091552 | 120.8725 | 120.8679 | 44.7968 | -121.3898 | 121.0556 | 121.1472 | 44.2108 | -121.3623
1102.5469 | 121.2204 | -70.8801 | 50.1984 | 0.0066373 | 0.0079596 | 0.072916 | 0.0091836 | 0.061293 | -0.0026958 | -0.0042254 | 0.0069425 | 0.00041436 | 0.062961 | 0.064232 | -0.01048 | -0.0040331 | 50.5463 | -70.0424 | -0.74616 | -70.3308 | 50.766 | -70.4681 | -70.3949 | -70.8664 | -0.11902 | -70.7199 | 50.6149 | 50.6241 | -70.3995 | -70.5597 | 0.41199 | 0.48523 | 0.56763 | 0.83771 | 0.54932 | 0.064086 | 0.3479 | 0.48065 | 0.32044 | 0.41656 | 0.013733 | 0.16022 | -0.16022 | 0.42572 | 121.6461 | 121.4264 | 70.134 | -120.5933 | 121.4951 | 121.5042 | 70.7611 | -120.7581
1104.3125 | 121.0556 | -67.4377 | 53.5629 | 0.0066373 | 0.012659 | 0.071848 | 0.0085428 | 0.062788 | -0.0033368 | -0.0037982 | 0.014572 | -0.0032172 | 0.064457 | 0.065941 | -0.010267 | -0.0061695 | 52.8214 | -67.5797 | -0.95673 | -67.8589 | 53.1006 | -67.9184 | -67.8406 | -68.1244 | 0 | -67.749 | 53.2425 | 53.215 | -67.6895 | -67.9138 | -0.48065 | -0.40283 | -0.46234 | -0.14191 | -0.42114 | -0.018311 | -0.74158 | -0.25177 | -0.47607 | -0.32043 | -0.68665 | -0.31128 | 0.1648 | -0.3479 | 120.5383 | 120.2591 | 66.481 | -121.4035 | 120.6802 | 120.6528 | 67.4377 | -121.4767
1106 | 121.0098 | -51.7868 | 69.1269 | -0.00099167 | 0.010096 | 0.069284 | 0.0025612 | 0.063002 | 0.0022174 | -0.00273 | -0.008316 | -0.00044004 | 0.061252 | 0.063378 | -0.0047125 | -0.0083057 | 68.9529 | -51.622 | 0.16937 | -51.86 | 69.1772 | -51.796 | -51.7914 | -52.0615 | 0.15564 | -52.0294 | 69.0445 | 69.0491 | -51.7502 | -51.9241 | -0.009155 | -0.004578 | 0.050354 | 0.16479 | -0.073242 | -0.068664 | -0.17395 | 0.036621 | -0.13733 | -0.082397 | -0.27466 | -0.24262 | -0.10529 | -0.07782 | 120.964 | 120.7397 | 51.9562 | -120.9183 | 120.8313 | 120.8359 | 51.9424 | -121.051
1107.6719 | 121.051 | -57.7057 | 63.0569 | -0.00099167 | 0.014368 | 0.072062 | 0.0064066 | 0.063002 | -0.0026958 | -0.0063616 | -0.00068649 | -0.0023626 | 0.060184 | 0.062737 | -0.010267 | -0.0087329 | 62.6633 | -57.6324 | -0.85602 | -58.2184 | 62.7045 | -58.3328 | -58.4015 | -58.9783 | -0.97961 | -58.7357 | 62.3245 | 62.3337 | -58.4335 | -58.5709 | -0.62714 | -0.6958 | -0.35248 | 0.073242 | -0.5127 | 0.1831 | -0.39368 | -0.72784 | -0.86517 | -0.73242 | -1.2726 | -1.03 | -0.1648 | -0.72327 | 120.4102 | 120.369 | 56.8497 | -121.4584 | 120.0302 | 120.0394 | 56.7261 | -121.6278
1109.4062 | 121.0648 | -34.7168 | 86.142 | -0.00099167 | 0.004328 | 0.072916 | 0.0087564 | 0.060865 | 0.0015766 | -0.00508 | -0.00068649 | 0.00062796 | 0.064884 | 0.062737 | -0.0077033 | -0.0057421 | 86.0413 | -34.6619 | 0.42114 | -35.2753 | 86.1511 | -34.877 | -34.9274 | -35.0967 | -0.16937 | -35.0647 | 86.0138 | 85.8398 | -35.0601 | -35.2295 | -0.16022 | -0.21057 | 0.009155 | 0.054932 | -0.55847 | -0.3479 | -0.10071 | -0.34332 | -0.5127 | -0.12817 | -0.37994 | -0.3479 | 0.16479 | -0.30212 | 120.8679 | 120.7581 | 35.1379 | -121.0693 | 120.7306 | 120.5566 | 34.5474 | -121.3715
1111.1406 | 120.9045 | -46.8109 | 73.938 | -0.00099167 | 0.004969 | 0.068644 | 0.003843 | 0.06172 | 0.0034992 | -0.0042254 | -0.00068649 | 0.0021234 | 0.062961 | 0.064873 | -0.0064215 | -0.0070239 | 74.263 | -46.9254 | -0.37079 | -47.8409 | 73.5214 | -47.2412 | -47.2183 | -47.5937 | -0.66376 | -47.5662 | 73.439 | 73.3749 | -47.1359 | -47.1222 | -0.4303 | -0.40741 | -0.41657 | -0.11444 | -1.03 | -0.62256 | 0.32501 | -0.32501 | -0.31128 | -0.49896 | -0.78278 | -0.75531 | -0.44403 | -0.56305 | 120.3323 | 121.0739 | 46.4401 | -121.1563 | 120.2499 | 120.1859 | 46.1472 | -121.0602
1112.8125 | 120.8496 | -36.9736 | 82.8644 | 0.0066373 | 0.012232 | 0.072702 | 0.0029886 | 0.060865 | -0.00055964 | -0.00273 | 0.0069425 | -0.0032172 | 0.061679 | 0.064019 | -0.0087713 | -0.0057421 | 88.7192 | -26.5869 | 1.9821 | -27.4841 | 91.5161 | -29.0817 | -28.9032 | -33.371 | -6.8207 | -36.5524 | 87.7625 | 86.6547 | -34.3414 | -34.6344 | 7.8918 | 8.0704 | 8.6517 | 10.3867 | 9.4894 | 1.4191 | 5.8548 | 2.6321 | 2.3392 | 4.8981 | 3.6026 | 0.42114 | -1.918 | 3.7903 | 128.4897 | 125.6927 | 38.9557 | -111.7676 | 124.736 | 123.6282 | 30.1529 | -117.4988
1114.5469 | 120.845 | -60.6995 | 59.9899 | -0.00099167 | 0.0021918 | 0.071207 | 0.0049112 | 0.063429 | 0.002431 | -0.00080744 | 0.014572 | 0.0016962 | 0.064029 | 0.064232 | -0.0055671 | -0.0070239 | 59.5779 | -60.7636 | 0.20599 | -61.1618 | 59.7198 | -61.1847 | -61.1847 | -61.5967 | 0 | -61.6379 | 59.4223 | 59.3994 | -61.3541 | -61.5601 | -0.48523 | -0.48523 | -0.27008 | -0.064087 | -0.46234 | 0.022888 | -0.41199 | -0.6546 | -0.8606 | -0.56763 | -0.89722 | -0.93841 | -0.077819 | -0.59051 | 120.4193 | 120.2774 | 60.9055 | -121.1746 | 120.1218 | 120.0989 | 60.6995 | -121.55
1116.2969 | 120.9686 | -43.721 | 77.2339 | -0.00099167 | 0.0062506 | 0.074839 | 0.0057656 | 0.062574 | -0.0039776 | -0.0042254 | 0.014572 | -0.0032172 | 0.061679 | 0.064019 | -0.010908 | -0.0055285 | 78.6804 | -41.835 | 1.2085 | -41.922 | 79.1428 | -41.7389 | -41.6519 | -44.5862 | -1.6891 | -44.6091 | 76.9135 | 76.799 | -44.1559 | -44.371 | 1.9821 | 2.0691 | 1.9089 | 1.886 | 1.799 | -0.27008 | 1.4465 | -0.43488 | -0.65002 | -0.32043 | -0.86517 | -0.88806 | -0.23804 | -0.43488 | 122.8638 | 122.4014 | 44.9295 | -118.8858 | 120.6345 | 120.52 | 42.0319 | -121.6049
1117.9844 | 121.0098 | -59.6695 | 61.116 | 0.0066373 | 0.0039008 | 0.066507 | 0.0064066 | 0.063856 | -0.00013244 | -0.0042254 | 0.0069425 | 0.0034052 | 0.064029 | 0.065728 | -0.0079169 | -0.0059557 | 60.5301 | -59.9487 | -0.25177 | -60.054 | 60.704 | -60.0998 | -60.0357 | -60.7864 | -0.16022 | -60.759 | 60.2966 | 60.0357 | -60.9055 | -61.3174 | -0.4303 | -0.36621 | -0.41199 | -0.27923 | -0.38452 | -0.01831 | -0.58594 | -1.236 | -1.6479 | -0.8194 | -1.1169 | -1.0895 | 0.55847 | -1.0803 | 120.3735 | 120.1996 | 59.4177 | -121.1517 | 119.9661 | 119.7052 | 59.5093 | -122.4335
1119.7344 | 120.9732 | -33.11 | 87.9822 | 0.014267 | 0.014368 | 0.071634 | 0.0046976 | 0.061506 | -0.0061138 | -0.0020892 | 0.0069425 | -0.0019354 | 0.061039 | 0.062737 | -0.011121 | -0.0055285 | 86.4441 | -34.2957 | -0.045776 | -34.2545 | 86.9247 | -34.0347 | -34.0714 | -34.108 | -0.66376 | -34.0027 | 87.1216 | 87.2955 | -33.4534 | -33.4808 | -0.92468 | -0.9613 | -1.0574 | -1.1856 | -1.1444 | -0.18311 | -1.5381 | -0.34332 | -0.37079 | -0.8606 | -0.99793 | -0.89264 | -0.52185 | -0.68665 | 120.0348 | 119.5541 | 33.0643 | -122.0535 | 120.2316 | 120.4056 | 32.4463 | -121.463
1121.4844 | 121.0144 | -35.9894 | 84.8053 | 0.0066373 | 0.0073188 | 0.071848 | 0.0066202 | 0.061293 | 0.00093576 | -0.0042254 | 0.0069425 | 0.0014826 | 0.062534 | 0.064659 | -0.0091985 | -0.0072375 | 84.7137 | -35.6049 | 0.62714 | -35.6003 | 85.437 | -35.5316 | -35.6094 | -35.8292 | -0.15564 | -35.7056 | 85.4004 | 85.4782 | -35.3439 | -35.4218 | 0.45776 | 0.37994 | 0.63171 | 0.38452 | 0.3891 | 0.009155 | -0.091553 | 0.64545 | 0.56763 | 0.59509 | 0.16022 | 0.28381 | -0.28381 | 0.67291 | 121.4264 | 120.7031 | 36.6165 | -120.4147 | 121.3898 | 121.4676 | 35.8337 | -120.2271
1123.1719 | 120.7855 | -25.0717 | 95.7825 | 0.0066373 | 0.0039008 | 0.072275 | 0.002775 | 0.063429 | 0.0034992 | -0.0035846 | 0.0069425 | 0.0019098 | 0.061252 | 0.065087 | -0.0066351 | -0.0076647 | 95.6451 | -24.971 | 1.7853 | -25.1633 | 95.9793 | -24.9069 | -24.9756 | -25.676 | -0.42572 | -25.9277 | 95.43 | 95.4758 | -25.3235 | -25.415 | 0.16479 | 0.09613 | 0.19684 | 0.10071 | -0.091553 | -0.18768 | -0.13733 | -0.25177 | -0.34332 | -0.35248 | -0.60425 | -0.85602 | -0.5127 | -0.3067 | 121.051 | 120.7169 | 26.857 | -120.7581 | 120.5017 | 120.5475 | 24.646 | -121.1975
1124.8594 | 120.8725 | -26.4313 | 94.2856 | -0.0086212 | 0.0024054 | 0.071207 | 0.0074746 | 0.062361 | 0.0011494 | -0.004439 | 0.0069425 | -0.00022644 | 0.064029 | 0.06231 | -0.0070623 | -0.0072375 | 94.3085 | -26.4359 | 1.1536 | -26.5549 | 94.6518 | -26.239 | -26.2619 | -26.2482 | 0.52643 | -26.2985 | 94.812 | 94.812 | -25.8957 | -26.0559 | 0.19226 | 0.16937 | 0.36621 | -0.004578 | -0.1236 | -0.29297 | 0.022889 | 0.53558 | 0.37537 | 0.52643 | 0.1831 | 0.13275 | -0.24262 | 0.52643 | 121.0831 | 120.7397 | 27.5848 | -120.5475 | 121.2433 | 121.2433 | 26.9577 | -120.3415
1126.5938 | 120.845 | -41.3315 | 79.1428 | 0.0066373 | 0.0039008 | 0.07078 | 0.0074746 | 0.061079 | 0.00072196 | -0.003371 | -0.00068649 | -0.0017218 | 0.063602 | 0.064446 | -0.010053 | -0.0046741 | 77.5818 | -42.6682 | -0.44861 | -42.4759 | 78.3142 | -42.3614 | -42.247 | -42.4255 | -0.70038 | -43.1992 | 78.4973 | 78.3554 | -42.4072 | -42.7917 | -1.03 | -0.91553 | -0.82855 | -1.3367 | -1.1444 | -0.22888 | -1.561 | -1.0757 | -1.4603 | -0.64545 | -1.0941 | -1.8677 | -0.40741 | -0.78735 | 119.6457 | 118.9133 | 40.8829 | -121.3898 | 119.8288 | 119.6869 | 40.6311 | -121.9345
1128.3438 | 120.0714 | -81.6879 | 38.0173 | -0.00099167 | 0.0024054 | 0.070139 | 0.0053384 | 0.061506 | -0.0026958 | -0.0031574 | -0.00068649 | -0.002149 | 0.063388 | 0.064019 | -0.01048 | -0.0059557 | 37.999 | -81.2347 | -1.9226 | -81.7612 | 38.2095 | -81.8802 | -81.8207 | -82.2922 | -0.18768 | -81.9809 | 38.0356 | 38.0402 | -81.7612 | -81.9855 | -0.19226 | -0.13275 | 0.19226 | 0.45319 | -0.073242 | 0.05951 | -0.018311 | -0.073242 | -0.29755 | 0.01831 | -0.60425 | -0.29297 | 0.004578 | 0.022888 | 119.8975 | 119.6869 | 79.7653 | -119.838 | 119.7235 | 119.7281 | 81.5002 | -120.0027
1130.0469 | 120.9229 | -0.32044 | 120.6848 | 0.0066373 | 0.00326 | 0.072489 | 0.005552 | 0.062361 | 0.0020038 | -0.0042254 | -0.00068649 | 0.00084176 | 0.066166 | 0.064446 | -0.0081305 | -0.0089465 | 120.3278 | -0.17853 | 4.1702 | -0.11444 | 120.7855 | -0.26093 | -0.38452 | -0.18768 | 0.23346 | -0.32501 | 120.6757 | 120.694 | -0.27924 | -0.31586 | 0.05951 | -0.064086 | 0.10071 | 0.14191 | 0.20599 | 0.27008 | -0.35706 | 0.041199 | 0.004578 | -0.009155 | 0.13275 | -0.004577 | -0.009155 | 0.009156 | 121.106 | 120.6482 | 4.4907 | -121.0693 | 120.9961 | 121.0144 | 0.55389 | -121.0007
1131.8125 | 121.0785 | -0.33875 | 120.726 | -0.00099167 | 0.006037 | 0.071634 | 0.0042702 | 0.063429 | -0.0039776 | -0.0042254 | 0.014572 | -0.0010808 | 0.063816 | 0.065941 | -0.0098395 | -0.0063831 | 120.314 | -0.2243 | 4.1199 | -0.18768 | 120.845 | -0.30212 | -0.40741 | -0.31128 | 0.19226 | -0.39825 | 120.7306 | 120.813 | -0.32501 | -0.35706 | 0.036621 | -0.068665 | 0.11902 | 0.11444 | 0.15106 | 0.21973 | -0.41199 | 0.013733 | -0.018311 | 0.004578 | 0.027466 | -0.059509 | -0.041198 | 0.086975 | 121.1838 | 120.6528 | 4.4586 | -121.1334 | 121.0693 | 121.1517 | 0.53101 | -121.0831
1133.5469 | 120.9 | -3.7491 | 117.2195 | 0.0066373 | 0.012446 | 0.071848 | 0.0029886 | 0.062574 | -0.0026958 | -0.003371 | 0.0069425 | -0.0049262 | 0.061466 | 0.063378 | -0.0087713 | -0.0040331 | 117.0914 | -3.3554 | 3.8498 | -3.36 | 117.4988 | -3.479 | -3.5843 | -3.479 | 0.16937 | -3.5614 | 117.3569 | 117.4347 | -3.5294 | -3.5706 | 0.27008 | 0.16479 | 0.27924 | 0.39368 | 0.3891 | 0.22431 | -0.12817 | 0.21973 | 0.17853 | 0.13733 | 0.27008 | 0.18768 | 0.009156 | 0.21515 | 121.2479 | 120.8405 | 7.5989 | -120.8038 | 121.106 | 121.1838 | 3.9185 | -120.7901
1135.2344 | 121.0281 | -0.5127 | 120.6757 | 0.0066373 | 0.0053962 | 0.068644 | 0.002775 | 0.060438 | 0.00093576 | -0.001662 | 0.0069425 | 0.00020076 | 0.062107 | 0.064659 | -0.0077033 | -0.0085193 | 120.2087 | -0.43945 | 4.0833 | -0.34332 | 120.7214 | -0.44403 | -0.56763 | -0.44861 | 0.10986 | -0.56763 | 120.6162 | 120.6848 | -0.45776 | -0.5127 | 0.068664 | -0.054932 | 0.045777 | 0.073242 | 0.16937 | 0.2243 | -0.46692 | 0.054931 | 0 | -0.059509 | 0.064087 | -0.054932 | -0.054932 | 0.009155 | 121.2341 | 120.7214 | 4.5959 | -121.2433 | 121.1288 | 121.1975 | 0.62256 | -121.1884
1136.9844 | 121.0693 | -0.64545 | 120.5338 | 0.021896 | 0.0079596 | 0.06843 | 0.0032022 | 0.062361 | 0.0017902 | -0.003371 | 0.0069425 | 0.001269 | 0.061679 | 0.064873 | -0.0081305 | -0.0068103 | 120.1263 | -0.56305 | 4.0924 | -0.46234 | 120.5933 | -0.58594 | -0.70038 | -0.59509 | 0.10529 | -0.70038 | 120.52 | 120.5704 | -0.58594 | -0.65002 | 0.05951 | -0.054931 | 0.05951 | 0.082398 | 0.18311 | 0.23804 | -0.40741 | 0.05951 | -0.004577 | -0.013732 | 0.050354 | -0.054931 | -0.050354 | 0.036622 | 121.2387 | 120.7718 | 4.7379 | -121.2341 | 121.1655 | 121.2158 | 0.75073 | -121.1838
1138.6719 | 121.1746 | -0.74616 | 120.3644 | 0.0066373 | 0.014155 | 0.07313 | 0.0059792 | 0.062361 | -0.0063274 | -0.0037982 | -0.008316 | -0.0040716 | 0.063602 | 0.06295 | -0.011335 | -0.0078783 | 120.0256 | -0.60425 | 4.1748 | -0.56763 | 120.433 | -0.71411 | -0.81024 | -0.6546 | 0.27466 | -0.68207 | 120.3232 | 120.3964 | -0.71869 | -0.76904 | 0.032044 | -0.064087 | 0.068664 | 0.14191 | 0.17853 | 0.24262 | -0.33875 | 0.027466 | -0.022888 | -0.041199 | 0.091553 | 0.064087 | 0.086975 | 0.032043 | 121.1792 | 120.7718 | 4.921 | -121.1746 | 121.0693 | 121.1426 | 1.0208 | -121.1334
1140.4219 | 121.138 | -4.097 | 116.9174 | 0.014267 | 0.0064642 | 0.070566 | 0.0042702 | 0.063643 | 0.00050836 | -0.0037982 | 0.014572 | 0.00084176 | 0.062748 | 0.066368 | -0.0077033 | -0.0093737 | 116.6016 | -4.0512 | 3.8589 | -3.9597 | 117.0685 | -4.0649 | -4.1794 | -4.0375 | 0.25635 | -4.1977 | 116.9769 | 117.009 | -4.0695 | -4.1245 | 0.032044 | -0.082397 | 0.15106 | 0.045777 | 0.13733 | 0.21973 | -0.31586 | 0.027466 | -0.027466 | 0.05951 | 0.059509 | -0.10071 | -0.073242 | 0.091553 | 121.1655 | 120.6985 | 7.9559 | -121.0968 | 121.0739 | 121.106 | 4.3533 | -121.0419
1142.1562 | 121.0785 | -2.243 | 118.8492 | 0.0066373 | 0.0092414 | 0.072489 | 0.0064066 | 0.063002 | -0.0046184 | -0.00508 | 0.0069425 | -0.002149 | 0.063602 | 0.063378 | -0.011549 | -0.0080921 | 118.5837 | -1.9867 | 4.0146 | -1.9638 | 118.9316 | -2.1103 | -2.2202 | -2.1149 | 0.19226 | -2.2247 | 118.8263 | 118.8904 | -2.1927 | -2.2293 | 0.13275 | 0.022888 | 0.082398 | 0.25635 | 0.27924 | 0.25635 | -0.2655 | 0.050354 | 0.013733 | -0.022888 | 0.12817 | 0.018311 | 0.004578 | 0.041199 | 121.1746 | 120.8267 | 6.2576 | -121.0693 | 121.0693 | 121.1334 | 2.4353 | -121.0785
1143.9062 | 121.0785 | -1.2177 | 119.9341 | -0.00099167 | 0.0133 | 0.073771 | 0.0053384 | 0.059797 | -0.0067548 | -0.006148 | 0.0069425 | -0.0025762 | 0.06232 | 0.061669 | -0.011121 | -0.0080921 | 119.5816 | -1.0666 | 4.0741 | -1.0071 | 120.0027 | -1.1261 | -1.2268 | -1.1032 | 0.1831 | -1.1948 | 119.8837 | 119.9478 | -1.1581 | -1.181 | 0.091552 | -0.009156 | 0.068665 | 0.15106 | 0.21057 | 0.21973 | -0.35248 | 0.059509 | 0.036621 | -0.050354 | 0.11444 | 0.022888 | -0.013733 | 0.013733 | 121.2204 | 120.7993 | 5.2917 | -121.1609 | 121.1014 | 121.1655 | 1.4008 | -121.1151
1145.6562 | 121.0007 | -5.9875 | 114.6973 | 0.0066373 | 0.0066778 | 0.069284 | 0.0098244 | 0.061934 | 0.00029476 | -0.0042254 | 0.0069425 | 0.0010554 | 0.064884 | 0.064446 | -0.011121 | -0.0061695 | 113.9511 | -6.5002 | 3.6667 | -6.4133 | 114.5233 | -6.5048 | -6.5826 | -6.3171 | 0.32044 | -6.6101 | 114.5645 | 114.6103 | -6.3904 | -6.4087 | -0.51727 | -0.59509 | -0.17395 | -0.5127 | -0.42572 | 0.16937 | -0.74616 | -0.40283 | -0.42114 | -0.13275 | -0.32959 | -0.62256 | -0.20142 | -0.086975 | 120.5109 | 119.9387 | 9.6542 | -121.2799 | 120.5521 | 120.5978 | 6.308 | -121.106
1147.3438 | 121.0785 | -1.5152 | 119.6365 | 0.0066373 | 0.002619 | 0.07078 | 0.002775 | 0.061293 | 0.0034992 | -0.0031574 | 0.022202 | 0.0021234 | 0.06467 | 0.064873 | -0.0066351 | -0.0074511 | 119.3115 | -1.3367 | 4.0787 | -1.3046 | 119.7235 | -1.4694 | -1.5701 | -1.3779 | 0.19226 | -1.5381 | 119.6182 | 119.6732 | -1.4648 | -1.5015 | 0.045777 | -0.054931 | 0.086975 | 0.17853 | 0.21057 | 0.2655 | -0.32501 | 0.050354 | 0.013733 | -0.018311 | 0.13733 | -0.022888 | -0.036621 | 0.036621 | 121.2387 | 120.8267 | 5.5939 | -121.2067 | 121.1334 | 121.1884 | 1.7075 | -121.138
1149.0781 | 121.106 | -2.536 | 118.5562 | 0.0066373 | 0.0079596 | 0.072062 | 0.0066202 | 0.059156 | -0.0033368 | -0.0046526 | -0.00068649 | -0.0017218 | 0.065525 | 0.063378 | -0.0098395 | -0.0076647 | 118.2312 | -2.3483 | 4.097 | -2.2934 | 118.6798 | -2.4582 | -2.5406 | -2.4582 | 0.27466 | -2.5497 | 118.6111 | 118.634 | -2.4673 | -2.5177 | 0.07782 | -0.004577 | 0.1236 | 0.18768 | 0.24261 | 0.24719 | -0.32501 | 0.068665 | 0.018311 | 0.054932 | 0.07782 | -0.013733 | -0.032044 | 0.07782 | 121.2158 | 120.7672 | 6.633 | -121.0968 | 121.1472 | 121.17 | 2.8107 | -121.0739
1150.8281 | 121.0876 | -1.4191 | 119.751 | 0.014267 | 0.002619 | 0.069712 | 0.0042702 | 0.062788 | 0.0026446 | -0.003371 | 0.014572 | 0.001269 | 0.061893 | 0.062523 | -0.0057807 | -0.0072375 | 119.426 | -1.2314 | 4.0924 | -1.1856 | 119.8929 | -1.3367 | -1.4465 | -1.2909 | 0.18768 | -1.4557 | 119.7739 | 119.7968 | -1.355 | -1.4099 | 0.082397 | -0.027466 | 0.14191 | 0.18768 | 0.23346 | 0.26093 | -0.32501 | 0.064087 | 0.009155 | 0.022888 | 0.12817 | -0.036621 | -0.045776 | 0.045776 | 121.3119 | 120.845 | 5.5115 | -121.1975 | 121.1929 | 121.2158 | 1.6068 | -121.1609
1152.5781 | 120.9549 | -5.1407 | 115.9195 | -0.00099167 | 0.015009 | 0.073557 | 0.0040566 | 0.061079 | -0.0041912 | -0.0072162 | -0.00068649 | -0.0025762 | 0.060825 | 0.060387 | -0.0098395 | -0.0036059 | 115.4343 | -5.1041 | 3.6346 | -5.1132 | 115.8005 | -5.1956 | -5.2826 | -5.1865 | 0.16022 | -5.3238 | 115.6906 | 115.773 | -5.2094 | -5.2734 | -0.054932 | -0.14191 | -0.11902 | 0.036621 | 0.027466 | 0.16937 | -0.48523 | -0.068665 | -0.13275 | -0.22888 | -0.045776 | -0.18311 | -0.050355 | -0.14648 | 120.9412 | 120.575 | 8.7753 | -121.2021 | 120.8313 | 120.9137 | 5.3009 | -121.1929
1154.25 | 121.0968 | -3.36 | 117.6086 | -0.00099167 | 0.0021918 | 0.069284 | 0.0061928 | 0.060225 | 0.0015766 | -0.0048662 | -0.00068649 | -0.00022644 | 0.064457 | 0.065514 | -0.0096259 | -0.0076647 | 117.2562 | -3.3737 | 3.8406 | -3.2684 | 117.7368 | -3.3646 | -3.4607 | -3.3737 | 0.17395 | -3.511 | 117.6636 | 117.691 | -3.3737 | -3.4424 | -0.004578 | -0.10071 | 0.12817 | -0.013733 | 0.091552 | 0.19226 | -0.35248 | -0.013733 | -0.082398 | 0.054931 | -0.013733 | -0.15106 | -0.068664 | 0.082397 | 121.0968 | 120.6161 | 7.2006 | -121.0693 | 121.0236 | 121.051 | 3.5339 | -121.051
1156 | 120.9778 | -5.2505 | 115.8966 | -0.00099167 | 0.011591 | 0.07078 | 0.0036294 | 0.062147 | 8.1158e-05 | -0.003371 | -0.00068649 | -1.2844e-05 | 0.063816 | 0.0653 | -0.0094123 | -0.0061695 | 115.0726 | -5.5115 | 3.653 | -5.3696 | 115.4526 | -5.4749 | -5.6168 | -5.1544 | 0.3479 | -5.3696 | 115.5533 | 115.567 | -5.3284 | -5.4199 | -0.2243 | -0.36621 | -0.44403 | -0.26093 | -0.11902 | 0.24719 | -0.82397 | -0.07782 | -0.16937 | -0.34332 | 0.09613 | -0.11902 | 0.050354 | -0.32959 | 120.7031 | 120.3232 | 8.9035 | -121.5134 | 120.8038 | 120.8176 | 5.5984 | -121.3165
1157.6875 | 121.0281 | -6.1066 | 114.8071 | -0.00099167 | 0.0051826 | 0.065866 | 0.0059792 | 0.062788 | 0.0011494 | -0.0023028 | -0.00068649 | 0.002978 | 0.063175 | 0.065087 | -0.0083441 | -0.0087329 | 114.6194 | -5.928 | 3.5568 | -5.864 | 115.036 | -5.9555 | -6.0654 | -5.9875 | 0.17853 | -6.1707 | 114.9033 | 114.9765 | -5.9967 | -6.0379 | 0.15106 | 0.041198 | 0.22888 | 0.17853 | 0.24261 | 0.20142 | -0.18768 | 0.10986 | 0.068664 | 0.09613 | 0.11902 | -0.064087 | -0.13275 | 0.16937 | 121.1426 | 120.726 | 9.6634 | -120.8725 | 121.0098 | 121.0831 | 6.2851 | -120.845
1159.4219 | 120.7718 | -11.0092 | 109.6207 | 0.014267 | 0.0034736 | 0.068003 | 0.0051248 | 0.060865 | 0.00072196 | -0.0023028 | 0.014572 | 0.0027644 | 0.06232 | 0.064232 | -0.0077033 | -0.0078783 | 110.0922 | -10.4141 | 3.566 | -10.5331 | 110.2661 | -10.5011 | -10.5927 | -10.7986 | 0.4715 | -11.0275 | 109.9457 | 109.9915 | -10.7117 | -10.8307 | 0.50812 | 0.41657 | 0.64545 | 0.59509 | 0.47607 | 0.059509 | 0.4715 | 0.29755 | 0.17853 | 0.32501 | 0.21057 | -0.018311 | -0.19684 | 0.37079 | 121.2753 | 121.1014 | 14.5752 | -120.2133 | 120.9549 | 121.0007 | 11.4807 | -120.4514
1161.1562 | 120.6253 | -12.7808 | 107.9315 | -0.00099167 | 0.00326 | 0.065012 | 0.0053384 | 0.061506 | 0.0015766 | -0.0023028 | -0.00068649 | 0.002337 | 0.063602 | 0.064446 | -0.0096259 | -0.0080921 | 107.666 | -12.6022 | 2.6505 | -12.6068 | 108.2108 | -12.5702 | -12.6434 | -12.7579 | -0.39368 | -12.8769 | 108.0505 | 108.1284 | -12.5381 | -12.6114 | 0.21057 | 0.13733 | 0.27923 | 0.17853 | 0.17395 | 0.036621 | -0.2655 | 0.24261 | 0.16937 | 0.11902 | 0.022888 | -0.09613 | -0.2655 | 0.19684 | 120.9915 | 120.4468 | 15.4312 | -120.575 | 120.8313 | 120.9091 | 12.3871 | -120.5429
1162.8906 | 120.5292 | -8.3588 | 111.9095 | 0.014267 | 0.0053962 | 0.071207 | 0.005552 | 0.061293 | -0.003764 | -0.0031574 | 0.0069425 | -0.0030034 | 0.063816 | 0.06295 | -0.0098395 | -0.0065967 | 111.2183 | -8.7021 | 3.186 | -8.7479 | 111.85 | -8.7387 | -8.8394 | -8.8806 | -0.12817 | -8.9081 | 111.7264 | 111.8271 | -8.725 | -8.7891 | -0.37994 | -0.48065 | -0.059509 | -0.34332 | -0.3891 | 0.091553 | -0.69122 | -0.36621 | -0.4303 | -0.18311 | -0.52185 | -0.54932 | -0.11902 | -0.082398 | 120.2087 | 119.577 | 11.5448 | -120.7489 | 120.0851 | 120.1859 | 8.2306 | -120.6985
1164.5781 | 120.7947 | -2.9755 | 117.6361 | 0.0066373 | 0.013087 | 0.07313 | 0.0070474 | 0.061506 | -0.0059002 | -0.0065752 | -0.00068649 | -0.0044988 | 0.062534 | 0.060387 | -0.011762 | -0.0051013 | 117.5171 | -2.6596 | 4.01 | -2.5772 | 117.9703 | -2.8107 | -2.8931 | -2.7191 | 0.39825 | -2.6962 | 117.9016 | 117.9291 | -2.774 | -2.7969 | 0.1648 | 0.082398 | 0.33417 | 0.31586 | 0.39826 | 0.31586 | -0.11902 | 0.20142 | 0.17853 | 0.2655 | 0.25635 | 0.27924 | 0.10071 | 0.29297 | 120.9457 | 120.4926 | 6.9855 | -120.5292 | 120.8771 | 120.9045 | 3.3737 | -120.433
1166.3281 | 120.1538 | -25.2869 | 94.8807 | -0.00099167 | 0.00326 | 0.071634 | 0.0046976 | 0.063643 | 0.0026446 | -0.0046526 | -0.00068649 | 0.0025508 | 0.064029 | 0.063805 | -0.0051397 | -0.0061695 | 94.0659 | -25.6531 | 2.7878 | -25.2365 | 94.8761 | -25.3967 | -25.3464 | -25.4471 | 0.91553 | -25.5844 | 94.8395 | 94.8898 | -25.1633 | -25.2914 | -0.10986 | -0.05951 | -0.004577 | -0.36621 | 0.050354 | 0.10986 | -0.81482 | 0.1236 | -0.004578 | -0.041198 | -0.16022 | -0.29755 | -0.29297 | 0.009156 | 120.163 | 119.3527 | 28.0746 | -120.2271 | 120.1263 | 120.1767 | 26.2024 | -120.1721
1168.0781 | 120.8038 | -0.14648 | 120.6757 | 0.014267 | 0.010523 | 0.073771 | 0.0049112 | 0.062147 | -0.005473 | -0.0055072 | 0.014572 | -0.0027898 | 0.062534 | 0.062096 | -0.011762 | -0.0070239 | 120.3873 | 0.07782 | 4.2389 | 0.10071 | 120.7397 | -0.091553 | -0.21057 | 0.018311 | 0.32959 | -0.041199 | 120.6253 | 120.6985 | -0.09613 | -0.1236 | 0.054931 | -0.064087 | 0.064087 | 0.2243 | 0.24719 | 0.31128 | -0.28839 | 0.050354 | 0.022888 | -0.050354 | 0.16479 | 0.10529 | 0.082397 | 0.022888 | 120.8862 | 120.5338 | 4.3854 | -120.8862 | 120.7718 | 120.845 | 0.47607 | -120.7993
1169.8281 | 120.9549 | -0.14191 | 120.7397 | 0.0066373 | 0.0062506 | 0.069071 | 0.0051248 | 0.061079 | 0.00029476 | -0.0042254 | 0.0069425 | 0.0016962 | 0.061039 | 0.06295 | -0.0094123 | -0.0068103 | 120.3781 | -0.068665 | 4.1473 | 0.004578 | 120.8817 | -0.11444 | -0.2243 | -0.086975 | 0.17853 | -0.17853 | 120.7993 | 120.8313 | -0.1236 | -0.16022 | 0.027466 | -0.082397 | 0.14191 | 0.073242 | 0.14649 | 0.22888 | -0.36163 | 0.018311 | -0.01831 | 0.059509 | 0.054932 | -0.036621 | -0.018311 | 0.091553 | 121.0236 | 120.52 | 4.2892 | -120.9641 | 120.9412 | 120.9732 | 0.32044 | -120.9
1171.5781 | 120.8633 | -0.20599 | 120.8679 | 0.014267 | 0.012232 | 0.072702 | 0.0025612 | 0.061506 | -0.0035504 | -0.00273 | -0.00068649 | -0.0012946 | 0.060825 | 0.062523 | -0.0081305 | -0.0087329 | 120.52 | 0.073242 | 4.248 | 0.064087 | 120.8633 | -0.068665 | -0.17853 | 0.013733 | 0.25177 | -0.086975 | 120.7809 | 120.8405 | -0.11444 | -0.11902 | 0.13733 | 0.027466 | -0.004578 | 0.27924 | 0.27008 | 0.24261 | -0.3479 | 0.091553 | 0.086975 | -0.086975 | 0.21973 | 0.11902 | 0.032044 | -0.027466 | 121.0693 | 120.726 | 4.454 | -121.0464 | 120.9869 | 121.0464 | 0.45776 | -120.9869
1173.25 | 121.0236 | -0.13275 | 120.8359 | -0.00099167 | 0.013087 | 0.073771 | 0.0079018 | 0.063215 | -0.0026958 | -0.004439 | 0.0069425 | -0.002149 | 0.062107 | 0.063378 | -0.011762 | -0.0080921 | 120.5704 | 0.091553 | 4.2984 | 0.082397 | 120.9274 | -0.082397 | -0.19226 | 0.018311 | 0.31128 | -0.050354 | 120.845 | 120.8679 | -0.11444 | -0.13733 | 0.050354 | -0.05951 | 0.091553 | 0.2243 | 0.21515 | 0.27466 | -0.2655 | 0.01831 | -0.004578 | 0.009156 | 0.15106 | 0.082397 | 0.086975 | 0.032044 | 121.0602 | 120.7031 | 4.4312 | -121.0281 | 120.9778 | 121.0007 | 0.44403 | -120.9732
1174.9844 | 121.0373 | -0.15106 | 120.8633 | 0.0066373 | 0.0073188 | 0.07313 | 0.0076882 | 0.064283 | -0.0052594 | -0.0055072 | -0.00068649 | -0.0019354 | 0.061252 | 0.06231 | -0.0089849 | -0.0087329 | 120.5887 | 0.082397 | 4.2847 | 0.07782 | 120.9824 | -0.091553 | -0.21057 | 0 | 0.3067 | -0.082397 | 120.8542 | 120.9091 | -0.10071 | -0.12817 | 0.059509 | -0.059509 | 0.11902 | 0.23346 | 0.22888 | 0.28839 | -0.27466 | 0.050354 | 0.022888 | -0.009155 | 0.15106 | 0.068665 | 0.045777 | 0.045777 | 121.1334 | 120.7397 | 4.4357 | -121.0739 | 121.0052 | 121.0602 | 0.45776 | -120.9915
1176.6719 | 121.0007 | -0.1831 | 120.9183 | 0.0066373 | 0.015436 | 0.073984 | 0.0049112 | 0.062147 | -0.0044048 | -0.0063616 | 0.0069425 | -0.0049262 | 0.061039 | 0.062737 | -0.0094123 | -0.0087329 | 120.5566 | 0.004578 | 4.216 | 0.027466 | 120.9869 | -0.09613 | -0.19684 | -0.059509 | 0.19226 | -0.10986 | 120.8908 | 120.9366 | -0.11902 | -0.13275 | 0.086975 | -0.013733 | 0.068664 | 0.18768 | 0.21057 | 0.2243 | -0.36163 | 0.064086 | 0.050354 | -0.027466 | 0.1236 | 0.073242 | 0.022888 | 0.01831 | 121.17 | 120.7397 | 4.3991 | -121.1151 | 121.0739 | 121.1197 | 0.37537 | -121.051
1178.4219 | 121.0373 | -0.16479 | 120.9595 | -0.00099167 | 0.014368 | 0.071634 | 0.0051248 | 0.062361 | 0.003072 | -0.0023028 | 0.0069425 | -0.00022644 | 0.061679 | 0.064019 | -0.0059943 | -0.0085193 | 120.6436 | 0.032043 | 4.2618 | 0.082397 | 120.9961 | -0.082397 | -0.19684 | 0.032043 | 0.23346 | -0.082397 | 120.9091 | 120.932 | -0.082397 | -0.11902 | 0.082398 | -0.032043 | 0.036621 | 0.19684 | 0.24719 | 0.27924 | -0.31586 | 0.082398 | 0.045776 | -0.050354 | 0.19684 | 0.082398 | 0.036622 | -0.027466 | 121.1609 | 120.8084 | 4.4266 | -121.1563 | 121.0739 | 121.0968 | 0.39825 | -121.0785
1180.1562 | 121.0007 | -0.1831 | 120.9641 | -0.00099167 | 0.013941 | 0.073984 | 0.0019204 | 0.059584 | 8.1158e-05 | -0.0025164 | -0.00068649 | -0.0032172 | 0.061252 | 0.062523 | -0.0066351 | -0.0072375 | 120.6436 | 0.068665 | 4.2847 | 0.064087 | 121.0098 | -0.086975 | -0.19226 | 0.022888 | 0.24719 | -0.086975 | 120.8908 | 120.9412 | -0.10529 | -0.14191 | 0.09613 | -0.009156 | 0.045777 | 0.25177 | 0.24719 | 0.25635 | -0.32043 | 0.077819 | 0.041198 | -0.073242 | 0.20599 | 0.09613 | 0.054932 | -0.022888 | 121.1929 | 120.8267 | 4.4678 | -121.1563 | 121.0739 | 121.1243 | 0.4303 | -121.106
1181.9219 | 121.0052 | -0.19226 | 120.9824 | -0.00099167 | 0.012659 | 0.073343 | 0.0053384 | 0.061079 | -0.0035504 | -0.0037982 | 0.014572 | -0.0010808 | 0.061039 | 0.06295 | -0.0091985 | -0.0053149 | 120.6253 | 0.027466 | 4.2526 | 0.032043 | 121.051 | -0.073242 | -0.19684 | -0.027466 | 0.21057 | -0.1236 | 120.932 | 120.9824 | -0.10986 | -0.13733 | 0.11902 | -0.004577 | 0.068664 | 0.21973 | 0.2243 | 0.22888 | -0.35706 | 0.082398 | 0.054932 | -0.050354 | 0.16479 | 0.068665 | 0.013733 | 0 | 121.2433 | 120.8176 | 4.4449 | -121.1792 | 121.1243 | 121.1746 | 0.40283 | -121.1197
1183.6562 | 121.0876 | -0.1831 | 120.9915 | -0.00099167 | 0.012018 | 0.070993 | 0.002775 | 0.066633 | 0.0043536 | -0.0059344 | -0.00068649 | -0.00065364 | 0.061679 | 0.062737 | -0.0053533 | -0.0076647 | 120.6711 | 0.027466 | 4.2938 | 0.068665 | 121.0739 | -0.086975 | -0.18768 | 0.027466 | 0.25635 | -0.09613 | 120.9549 | 120.9824 | -0.082397 | -0.12817 | 0.09613 | -0.004578 | 0.082398 | 0.21057 | 0.25177 | 0.25635 | -0.32043 | 0.10071 | 0.054931 | -0.036621 | 0.21057 | 0.086975 | 0.032044 | -0.009155 | 121.257 | 120.8542 | 4.4769 | -121.1792 | 121.138 | 121.1655 | 0.43945 | -121.1197
1185.3438 | 121.17 | -0.14191 | 120.9824 | 0.014267 | 0.013514 | 0.071421 | 0.0051248 | 0.060438 | -0.003764 | -0.0046526 | -0.00068649 | -0.0012946 | 0.062534 | 0.062737 | -0.011549 | -0.0070239 | 120.6528 | 0.004578 | 4.2755 | 0.054932 | 121.0785 | -0.086975 | -0.21057 | -0.032043 | 0.2655 | -0.07782 | 120.9549 | 121.0236 | -0.11444 | -0.15564 | 0.054932 | -0.068664 | 0.09613 | 0.14649 | 0.19684 | 0.2655 | -0.32959 | 0.027466 | -0.013733 | -0.027466 | 0.10986 | 0.064087 | 0.07782 | 0.041199 | 121.2204 | 120.7947 | 4.4174 | -121.1929 | 121.0968 | 121.1655 | 0.40741 | -121.138
1187.0938 | 121.1746 | -0.15564 | 120.9915 | -0.0086212 | 0.0028326 | 0.07078 | 0.0051248 | 0.060865 | 0.0054218 | -0.0031574 | 0.014572 | 0.0036188 | 0.062961 | 0.064019 | -0.0066351 | -0.0070239 | 120.6665 | -0.018311 | 4.2801 | 0.041199 | 121.106 | -0.11902 | -0.2243 | -0.018311 | 0.21515 | -0.16937 | 120.9961 | 121.0236 | -0.11444 | -0.16937 | 0.036621 | -0.068664 | 0.11444 | 0.13733 | 0.19684 | 0.2655 | -0.32501 | 0.041199 | -0.013733 | 0.004578 | 0.13733 | -0.013733 | 0 | 0.032044 | 121.2616 | 120.8221 | 4.4357 | -121.2158 | 121.1517 | 121.1792 | 0.37079 | -121.1609
1188.7812 | 121.1288 | -0.17853 | 121.0144 | 0.021896 | 0.013087 | 0.074411 | 0.0070474 | 0.060011 | -0.0048322 | -0.0055072 | -0.00068649 | -0.003858 | 0.06467 | 0.06295 | -0.010908 | -0.0070239 | 120.6162 | 0.004578 | 4.248 | 0.036621 | 121.0922 | -0.10071 | -0.20599 | -0.032043 | 0.20599 | -0.10529 | 120.9457 | 121.0144 | -0.10529 | -0.14191 | 0.07782 | -0.027466 | 0.07782 | 0.18311 | 0.21515 | 0.24262 | -0.39825 | 0.073242 | 0.036621 | -0.068664 | 0.14648 | 0.073242 | 0.036621 | 0 | 121.2708 | 120.7947 | 4.4266 | -121.2204 | 121.1243 | 121.1929 | 0.38452 | -121.1563
1190.5156 | 121.0876 | -0.19226 | 121.0556 | 0.0066373 | 0.0071052 | 0.068644 | 0.002775 | 0.062361 | 0.0034992 | -0.0031574 | 0.014572 | 0.0031916 | 0.063602 | 0.060173 | -0.0040717 | -0.0074511 | 120.6162 | -0.11902 | 4.1885 | -0.013733 | 121.1288 | -0.11902 | -0.2243 | -0.068665 | 0.10071 | -0.24261 | 121.0281 | 121.051 | -0.14191 | -0.17395 | 0.073242 | -0.032043 | 0.073242 | 0.073242 | 0.17853 | 0.21057 | -0.43945 | 0.050354 | 0.018311 | -0.027466 | 0.1236 | -0.050354 | -0.068665 | -0.004578 | 121.3211 | 120.8084 | 4.3808 | -121.2799 | 121.2204 | 121.2433 | 0.29297 | -121.2296
1192.2656 | 121.2204 | -0.13733 | 120.9869 | 0.0066373 | 0.0039008 | 0.070566 | 0.0042702 | 0.062574 | 0.0022174 | -0.0025164 | -0.00068649 | 0.002337 | 0.064457 | 0.064446 | -0.0079169 | -0.0085193 | 120.6894 | -0.013733 | 4.2755 | 0.041199 | 121.138 | -0.11444 | -0.22888 | -0.022888 | 0.23804 | -0.17853 | 121.0281 | 121.0648 | -0.11444 | -0.15564 | 0.022888 | -0.091553 | 0.15106 | 0.1236 | 0.17853 | 0.27008 | -0.29755 | 0.022888 | -0.018311 | 0.041199 | 0.11444 | -0.041199 | -0.022888 | 0.07782 | 121.2753 | 120.8267 | 4.4128 | -121.2158 | 121.1655 | 121.2021 | 0.37537 | -121.1426
1194.0156 | 121.2158 | -0.14648 | 121.0098 | 0.0066373 | 0.00326 | 0.072275 | 0.003843 | 0.064283 | 0.0017902 | -0.0031574 | 0.0069425 | -0.00065364 | 0.06232 | 0.061882 | -0.0070623 | -0.0070239 | 120.6711 | -0.022888 | 4.2755 | 0.036621 | 121.138 | -0.10986 | -0.22888 | -0.032043 | 0.23346 | -0.16479 | 121.0098 | 121.0556 | -0.11444 | -0.16022 | 0.036621 | -0.082398 | 0.12817 | 0.1236 | 0.18311 | 0.2655 | -0.33875 | 0.032043 | -0.013733 | 0 | 0.11444 | -0.018311 | -0.004578 | 0.045776 | 121.2845 | 120.8176 | 4.422 | -121.2387 | 121.1563 | 121.2021 | 0.37994 | -121.17
1195.7031 | 121.1838 | -0.16479 | 121.0236 | 0.0066373 | 0.0066778 | 0.072916 | 0.0070474 | 0.061506 | -0.0041912 | -0.0012346 | 0.0069425 | -0.0010808 | 0.06467 | 0.061882 | -0.010694 | -0.0055285 | 120.694 | 0.064087 | 4.3259 | 0.07782 | 121.0922 | -0.091553 | -0.21973 | -0.068665 | 0.27466 | -0.14191 | 121.0281 | 121.0602 | -0.12817 | -0.15564 | 0.073242 | -0.054932 | 0.068664 | 0.22888 | 0.24261 | 0.29755 | -0.32959 | 0.036621 | 0.009155 | 0.004577 | 0.09613 | 0.022888 | 0.013733 | 0.036621 | 121.257 | 120.8588 | 4.4907 | -121.2433 | 121.1929 | 121.225 | 0.43945 | -121.1792
1197.4219 | 121.1472 | -0.18768 | 121.0373 | 0.021896 | 0.013514 | 0.070566 | 0.0057656 | 0.061506 | -0.0012006 | -0.0055072 | 0.0069425 | -0.00086724 | 0.061252 | 0.063378 | -0.0062079 | -0.0068103 | 120.7169 | 0.050354 | 4.3121 | 0.068665 | 121.106 | -0.082397 | -0.18768 | 0 | 0.25177 | -0.082397 | 120.9824 | 121.051 | -0.10071 | -0.11902 | 0.10529 | 0 | 0.068665 | 0.23804 | 0.25635 | 0.25635 | -0.32043 | 0.086975 | 0.068664 | -0.054931 | 0.18768 | 0.10529 | 0.036622 | 0.013733 | 121.2936 | 120.9045 | 4.4998 | -121.225 | 121.17 | 121.2387 | 0.43945 | -121.1563
1199.1562 | 121.1151 | -0.1831 | 121.0922 | -0.00099167 | 0.012873 | 0.073343 | 0.002134 | 0.060438 | -0.0031232 | -0.0046526 | 0.0069425 | 0.00020076 | 0.060398 | 0.064232 | -0.0085577 | -0.0053149 | 120.7306 | 0.073242 | 4.3304 | 0.068665 | 121.1105 | -0.07782 | -0.17853 | -0.004578 | 0.23346 | -0.082397 | 121.0144 | 121.0739 | -0.09613 | -0.14648 | 0.10528 | 0.004577 | 0.018311 | 0.25635 | 0.25177 | 0.24719 | -0.36163 | 0.086975 | 0.036621 | -0.07782 | 0.17853 | 0.10071 | 0.064087 | -0.01831 | 121.2936 | 120.9137 | 4.5135 | -121.2708 | 121.1975 | 121.257 | 0.41656 | -121.2387
1200.8438 | 121.2524 | -0.15106 | 121.0419 | 0.014267 | 0.0053962 | 0.068216 | 0.0051248 | 0.060011 | 0.0034992 | -0.001662 | 0.0069425 | 0.0019098 | 0.063175 | 0.063164 | -0.0070623 | -0.0093737 | 120.7123 | -0.022888 | 4.2892 | 0.032043 | 121.1426 | -0.11902 | -0.23804 | -0.045776 | 0.23804 | -0.17395 | 121.0648 | 121.1014 | -0.13275 | -0.16937 | 0.032043 | -0.086975 | 0.10071 | 0.12817 | 0.18311 | 0.27008 | -0.32959 | 0.018311 | -0.018311 | 0.022888 | 0.10529 | -0.022888 | -0.004577 | 0.059509 | 121.2936 | 120.8633 | 4.4403 | -121.2799 | 121.2158 | 121.2524 | 0.3891 | -121.2112
1202.5938 | 121.2296 | -0.15106 | 121.0556 | 0.0066373 | 0.0071052 | 0.072275 | 0.0074746 | 0.060225 | 0.00029476 | -0.0023028 | -0.00068649 | 0.00062796 | 0.062961 | 0.064659 | -0.0098395 | -0.0083057 | 120.6619 | -0.07782 | 4.248 | 0.004578 | 121.17 | -0.14191 | -0.26093 | -0.1236 | 0.19684 | -0.21057 | 121.0602 | 121.1288 | -0.14191 | -0.20142 | 0.009155 | -0.10986 | 0.11444 | 0.073242 | 0.15564 | 0.2655 | -0.39368 | 0.009155 | -0.050354 | 0.004578 | 0.027466 | -0.059509 | -0.009155 | 0.073242 | 121.3211 | 120.813 | 4.3991 | -121.3165 | 121.2112 | 121.2799 | 0.3479 | -121.257
1204.2969 | 121.257 | -0.15106 | 121.0739 | -0.0086212 | 0.0039008 | 0.07313 | 0.0057656 | 0.060438 | -0.0014142 | -0.0046526 | 0.014572 | -0.0010808 | 0.062107 | 0.064873 | -0.0085577 | -0.0065967 | 120.639 | -0.086975 | 4.2435 | -0.018311 | 121.1746 | -0.12817 | -0.23804 | -0.11444 | 0.19684 | -0.21057 | 121.0693 | 121.106 | -0.14191 | -0.16937 | 0.022888 | -0.086975 | 0.10071 | 0.064087 | 0.13275 | 0.21973 | -0.43488 | 0.009155 | -0.018311 | -0.004578 | 0.036621 | -0.059509 | -0.041198 | 0.032043 | 121.3257 | 120.7901 | 4.3945 | -121.312 | 121.2204 | 121.257 | 0.3479 | -121.2433
1206.0469 | 121.1884 | -0.1831 | 121.0739 | -0.00099167 | 0.0073188 | 0.070566 | 0.003843 | 0.063002 | -0.0014142 | -0.00508 | 0.0069425 | 0.00020076 | 0.062748 | 0.063378 | -0.0070623 | -0.0072375 | 120.6619 | -0.07782 | 4.2389 | -0.004578 | 121.1792 | -0.1236 | -0.23346 | -0.059509 | 0.16937 | -0.17395 | 121.051 | 121.106 | -0.1236 | -0.14191 | 0.059509 | -0.050354 | 0.10528 | 0.10528 | 0.17853 | 0.22888 | -0.41199 | 0.059509 | 0.041198 | -0.022889 | 0.1236 | 0.009155 | -0.032043 | 0.032043 | 121.3623 | 120.845 | 4.422 | -121.3074 | 121.2341 | 121.2891 | 0.35248 | -121.2158
1207.7344 | 121.1792 | -0.21057 | 121.0693 | 0.0066373 | 0.011591 | 0.072489 | 0.0061928 | 0.060865 | -0.0050458 | -0.0055072 | 0.0069425 | -0.0017218 | 0.064243 | 0.062096 | -0.0077033 | -0.0070239 | 120.6802 | -0.004578 | 4.2892 | 0.032043 | 121.1517 | -0.091553 | -0.21515 | -0.054932 | 0.20599 | -0.1236 | 121.0419 | 121.1105 | -0.13275 | -0.16022 | 0.11902 | -0.004578 | 0.082397 | 0.20599 | 0.24261 | 0.24719 | -0.3891 | 0.07782 | 0.050354 | -0.027466 | 0.15564 | 0.086975 | 0.036621 | 0.041199 | 121.3623 | 120.8908 | 4.4998 | -121.2845 | 121.2524 | 121.3211 | 0.41657 | -121.2296
1209.4844 | 121.2845 | -0.16937 | 121.0419 | 0.014267 | 0.0051826 | 0.070353 | 0.0085428 | 0.065138 | 0.001363 | -0.0037982 | -0.00068649 | 0.002337 | 0.063602 | 0.063805 | -0.0068487 | -0.0089465 | 120.7306 | -0.054932 | 4.3076 | 0.018311 | 121.1884 | -0.13275 | -0.25635 | -0.050354 | 0.23346 | -0.16937 | 121.0648 | 121.1197 | -0.13733 | -0.1831 | 0.036622 | -0.086975 | 0.14648 | 0.11444 | 0.18768 | 0.27466 | -0.31128 | 0.032044 | -0.013732 | 0.022888 | 0.11902 | 0 | 0.013732 | 0.07782 | 121.3577 | 120.9 | 4.4769 | -121.2982 | 121.2341 | 121.2891 | 0.40283 | -121.225
1211.1719 | 121.2799 | -0.15106 | 121.0556 | 0.0066373 | 0.013941 | 0.075266 | 0.0053384 | 0.06172 | -0.0052594 | -0.0014484 | 0.014572 | -0.0034308 | 0.061466 | 0.063164 | -0.011121 | -0.0076647 | 120.7031 | 0.004578 | 4.3259 | 0.045776 | 121.1472 | -0.09613 | -0.21973 | -0.036621 | 0.29297 | -0.10071 | 121.0373 | 121.0785 | -0.12817 | -0.16937 | 0.054932 | -0.068665 | 0.091553 | 0.15564 | 0.19684 | 0.2655 | -0.35248 | 0.022888 | -0.018311 | -0.018311 | 0.11444 | 0.050354 | 0.068665 | 0.022888 | 121.2982 | 120.8542 | 4.4769 | -121.2753 | 121.1884 | 121.2296 | 0.44403 | -121.225
1212.8594 | 121.2753 | -0.16022 | 121.051 | 0.0066373 | 0.012232 | 0.074625 | 0.0061928 | 0.063643 | -0.0061138 | -0.0057208 | 0.0069425 | -0.0034308 | 0.061679 | 0.063164 | -0.0091985 | -0.0072375 | 120.7535 | 0.036621 | 4.3442 | 0.059509 | 121.1426 | -0.10529 | -0.26093 | -0.013733 | 0.31586 | -0.068665 | 121.019 | 121.0739 | -0.1236 | -0.15564 | 0.054931 | -0.10071 | 0.091553 | 0.19684 | 0.21973 | 0.32043 | -0.29755 | 0.036621 | 0.004577 | -0.032043 | 0.14648 | 0.091552 | 0.086975 | 0.022889 | 121.3028 | 120.9137 | 4.5044 | -121.3119 | 121.1792 | 121.2341 | 0.47607 | -121.2067
1214.6094 | 121.2936 | -0.16479 | 121.0648 | -0.00099167 | 0.004969 | 0.072275 | 0.0081154 | 0.061934 | 0.0017902 | -0.00508 | -0.008316 | 0.00084176 | 0.064884 | 0.065941 | -0.0094123 | -0.0098009 | 120.694 | -0.09613 | 4.2618 | -0.022888 | 121.1884 | -0.16022 | -0.28381 | -0.10529 | 0.1831 | -0.23346 | 121.1105 | 121.1105 | -0.1831 | -0.20599 | 0.004578 | -0.11902 | 0.1236 | 0.068665 | 0.14191 | 0.26092 | -0.37079 | -0.01831 | -0.041199 | 0.045777 | 0.059509 | -0.068664 | -0.027465 | 0.045777 | 121.3531 | 120.8588 | 4.4266 | -121.3486 | 121.2753 | 121.2753 | 0.3479 | -121.2708
1216.2969 | 121.2845 | -0.16022 | 121.0648 | 0.0066373 | 0.015009 | 0.075266 | 0.0044838 | 0.060865 | -0.0044048 | -0.006148 | -0.00068649 | -0.0015082 | 0.063175 | 0.062523 | -0.0096259 | -0.0074511 | 120.7352 | 0.036621 | 4.3579 | 0.050354 | 121.1426 | -0.10529 | -0.21057 | -0.013733 | 0.29755 | -0.073242 | 121.0373 | 121.106 | -0.1236 | -0.16937 | 0.054931 | -0.050354 | 0.07782 | 0.19684 | 0.21057 | 0.26093 | -0.32959 | 0.036621 | -0.009156 | -0.027466 | 0.14648 | 0.086975 | 0.096131 | 0.041199 | 121.3028 | 120.8954 | 4.5181 | -121.2753 | 121.1975 | 121.2662 | 0.45776 | -121.2341
1218.0312 | 121.2662 | -0.15564 | 121.0648 | 0.0066373 | 0.014368 | 0.074625 | 0.0044838 | 0.062574 | -0.0046184 | -0.0055072 | 0.0069425 | -0.0010808 | 0.060825 | 0.061455 | -0.011335 | -0.0085193 | 120.7169 | -0.009155 | 4.3076 | 0.032043 | 121.1746 | -0.11444 | -0.20599 | -0.050354 | 0.24261 | -0.1236 | 121.0419 | 121.1151 | -0.12817 | -0.17395 | 0.041199 | -0.050354 | 0.10986 | 0.14649 | 0.18768 | 0.23804 | -0.3479 | 0.027466 | -0.01831 | -0.022888 | 0.10529 | 0.032044 | 0.050354 | 0.050354 | 121.3303 | 120.8725 | 4.4632 | -121.2708 | 121.1975 | 121.2708 | 0.39826 | -121.2387
1219.7031 | 121.3303 | -0.16479 | 121.0693 | 0.0066373 | 0.004328 | 0.067362 | 0.003843 | 0.061079 | 0.0049946 | -0.0020892 | 0.014572 | 0.0016962 | 0.062748 | 0.064873 | -0.0087713 | -0.0093737 | 120.7581 | -0.045776 | 4.3304 | 0.032043 | 121.2158 | -0.13733 | -0.25635 | -0.050354 | 0.23346 | -0.19684 | 121.0922 | 121.1472 | -0.15106 | -0.17853 | 0.027466 | -0.091553 | 0.14648 | 0.11902 | 0.19684 | 0.28839 | -0.31128 | 0.013733 | -0.013733 | 0.022888 | 0.11444 | -0.032043 | -0.01831 | 0.07782 | 121.3806 | 120.9229 | 4.4952 | -121.3257 | 121.257 | 121.312 | 0.39825 | -121.2479
1221.4531 | 121.1929 | -0.21973 | 121.1197 | 0.014267 | 0.01565 | 0.068216 | -2.152e-06 | 0.063215 | -0.00077324 | -0.001662 | 0.0069425 | -0.0025762 | 0.063816 | 0.063591 | -0.0083441 | -0.010015 | 120.7947 | 0.050354 | 4.3854 | 0.068665 | 121.138 | -0.11444 | -0.21973 | 0.022888 | 0.29297 | -0.10071 | 121.0327 | 121.0876 | -0.13275 | -0.15106 | 0.10529 | 0 | 0.01831 | 0.27008 | 0.28839 | 0.28839 | -0.32501 | 0.086976 | 0.068665 | -0.086975 | 0.24261 | 0.11902 | 0.050354 | -0.032044 | 121.3577 | 121.0144 | 4.6051 | -121.3394 | 121.2524 | 121.3074 | 0.5127 | -121.2708
1223.2031 | 121.2204 | -0.21515 | 121.0876 | 0.0066373 | 0.015009 | 0.069498 | 0.0012796 | 0.063643 | 0.002431 | -0.0042254 | 0.0069425 | -0.0010808 | 0.062961 | 0.062523 | -0.0077033 | -0.0083057 | 120.7901 | 0.018311 | 4.3716 | 0.054932 | 121.1517 | -0.09613 | -0.22888 | 0.004578 | 0.27924 | -0.1236 | 121.019 | 121.1014 | -0.12817 | -0.17395 | 0.11902 | -0.013733 | 0.064087 | 0.23346 | 0.27008 | 0.28381 | -0.29755 | 0.086975 | 0.041199 | -0.068664 | 0.21973 | 0.091553 | 0.050354 | 0.013733 | 121.3669 | 121.0052 | 4.5868 | -121.3165 | 121.2341 | 121.3165 | 0.49438 | -121.2616
1224.8906 | 121.1929 | -0.20142 | 121.0968 | -0.0086212 | 0.013941 | 0.072062 | 0.003843 | 0.060652 | -0.0052594 | -0.0020892 | -0.00068649 | -0.0015082 | 0.062748 | 0.060814 | -0.0098395 | -0.0068103 | 120.7489 | -0.022888 | 4.3259 | 0.009155 | 121.1746 | -0.10529 | -0.2243 | -0.068665 | 0.23346 | -0.16479 | 121.0327 | 121.1151 | -0.14191 | -0.18768 | 0.09613 | -0.022888 | 0.07782 | 0.17853 | 0.21057 | 0.23346 | -0.3479 | 0.059509 | 0.013733 | -0.064087 | 0.13275 | 0.036621 | 0.022888 | 0.01831 | 121.376 | 120.9503 | 4.5273 | -121.3211 | 121.2341 | 121.3165 | 0.43488 | -121.2845
1226.6562 | 121.1884 | -0.2243 | 121.1243 | 0.0066373 | 0.013941 | 0.071421 | 0.0079018 | 0.06407 | 0.00072196 | -0.00273 | 0.0069425 | 0.00020076 | 0.060398 | 0.062096 | -0.0066351 | -0.0068103 | 120.8038 | 0.018311 | 4.3762 | 0.032043 | 121.1792 | -0.1236 | -0.21973 | -0.009155 | 0.25635 | -0.11444 | 121.0602 | 121.1105 | -0.14191 | -0.16022 | 0.10071 | 0.004577 | 0.054931 | 0.24261 | 0.25635 | 0.25177 | -0.32044 | 0.082397 | 0.064087 | -0.064087 | 0.21515 | 0.10986 | 0.045776 | -0.013733 | 121.4035 | 121.0281 | 4.6005 | -121.344 | 121.2845 | 121.3348 | 0.48065 | -121.2845
1228.3438 | 121.2799 | -0.19684 | 121.0922 | 0.014267 | 0.0075324 | 0.073343 | 0.0076882 | 0.060438 | -0.0012006 | -0.0029436 | -0.00068649 | -0.0010808 | 0.062748 | 0.063591 | -0.0096259 | -0.0085193 | 120.7672 | 0.022888 | 4.3854 | 0.027466 | 121.1609 | -0.14191 | -0.26093 | -0.086975 | 0.27008 | -0.17853 | 121.0693 | 121.1334 | -0.16479 | -0.20142 | 0.054931 | -0.064087 | 0.068665 | 0.21973 | 0.2243 | 0.28839 | -0.32501 | 0.032043 | -0.004578 | -0.022888 | 0.10986 | 0.01831 | 0.022888 | 0.041199 | 121.3577 | 120.9641 | 4.5822 | -121.3531 | 121.2662 | 121.3303 | 0.46692 | -121.2936
1230.0938 | 121.1975 | -0.23804 | 121.106 | 0.0066373 | 0.0073188 | 0.068644 | 0.0014932 | 0.062361 | 0.0039264 | -0.0042254 | -0.00068649 | -0.00022644 | 0.063388 | 0.06295 | -0.0030035 | -0.0095873 | 120.7031 | -0.14648 | 4.2709 | -0.059509 | 121.2204 | -0.16937 | -0.27466 | -0.1236 | 0.12817 | -0.29755 | 121.1151 | 121.1517 | -0.1831 | -0.20599 | 0.068664 | -0.036621 | 0.11444 | 0.091553 | 0.17853 | 0.21515 | -0.40283 | 0.054932 | 0.032043 | 0.009155 | 0.11444 | -0.059509 | -0.091552 | 0.045776 | 121.4584 | 120.9412 | 4.509 | -121.3806 | 121.3531 | 121.3898 | 0.36621 | -121.312
1231.7656 | 121.2936 | -0.26093 | 121.0327 | -0.0086212 | 0.009455 | 0.07313 | 0.007261 | 0.063215 | -0.0022686 | -0.003371 | -0.00068649 | -0.0010808 | 0.064457 | 0.061669 | -0.0096259 | -0.0083057 | 120.7169 | -0.032043 | 4.3991 | -0.013733 | 121.1105 | -0.17395 | -0.28381 | -0.10529 | 0.33417 | -0.17853 | 121.0007 | 121.0327 | -0.20599 | -0.2655 | 0.086975 | -0.022888 | 0.07782 | 0.22888 | 0.24719 | 0.27008 | -0.31586 | 0.054931 | -0.004578 | -0.032044 | 0.15564 | 0.082397 | 0.086975 | 0 | 121.3715 | 120.9778 | 4.66 | -121.3165 | 121.2616 | 121.2936 | 0.59509 | -121.2982
1233.5 | 121.312 | -0.2655 | 121.0052 | 0.0066373 | 0.012873 | 0.073557 | 0.0066202 | 0.062574 | -0.0033368 | -0.004439 | -0.00068649 | -0.0015082 | 0.061679 | 0.062096 | -0.0089849 | -0.0072375 | 120.7489 | -0.013733 | 4.4083 | -0.027466 | 121.0922 | -0.19684 | -0.31586 | -0.091553 | 0.36621 | -0.16937 | 120.9824 | 121.0327 | -0.21515 | -0.25177 | 0.068665 | -0.050354 | 0.086975 | 0.25177 | 0.23804 | 0.28839 | -0.25635 | 0.050354 | 0.013733 | -0.022888 | 0.17395 | 0.09613 | 0.082397 | 0.027466 | 121.3577 | 121.0144 | 4.6738 | -121.3211 | 121.2479 | 121.2982 | 0.63171 | -121.257
1235.1719 | 121.2845 | -0.27008 | 121.0281 | -0.00099167 | 0.004328 | 0.065866 | 0.0057656 | 0.061293 | 0.0054218 | -0.0035846 | 0.0069425 | 0.0031916 | 0.064243 | 0.066155 | -0.0055671 | -0.0074511 | 120.7077 | -0.082397 | 4.3808 | -0.059509 | 121.1426 | -0.23346 | -0.34332 | -0.14191 | 0.24719 | -0.29297 | 121.0464 | 121.0785 | -0.22888 | -0.27924 | 0.036622 | -0.073242 | 0.11444 | 0.18768 | 0.21057 | 0.28381 | -0.32043 | 0.041199 | -0.009155 | 0.018311 | 0.12817 | -0.022888 | -0.013733 | 0.050354 | 121.4127 | 120.9778 | 4.6509 | -121.3715 | 121.3165 | 121.3486 | 0.51727 | -121.3074
1236.9219 | 121.2341 | -0.27466 | 121.051 | 0.014267 | 0.014155 | 0.070353 | 0.0032022 | 0.062574 | -0.0029094 | -0.00508 | -0.00068649 | -0.00022644 | 0.061039 | 0.062737 | -0.0074897 | -0.0085193 | 120.7169 | -0.050354 | 4.4128 | -0.018311 | 121.0831 | -0.19684 | -0.29755 | -0.07782 | 0.29755 | -0.1831 | 120.9915 | 121.0602 | -0.21515 | -0.23804 | 0.07782 | -0.022888 | 0.032044 | 0.2243 | 0.25635 | 0.27923 | -0.33417 | 0.059509 | 0.036621 | -0.059509 | 0.19684 | 0.091553 | 0.054932 | 0.009156 | 121.3577 | 120.9915 | 4.6875 | -121.3486 | 121.2662 | 121.3348 | 0.5722 | -121.2891
1238.6719 | 121.257 | -0.29755 | 121.0373 | 0.0066373 | 0.0081732 | 0.071207 | 0.0023476 | 0.060225 | 0.0015766 | -0.00080744 | 0.0069425 | 0.0019098 | 0.064029 | 0.061669 | -0.0066351 | -0.0055285 | 120.6345 | -0.1831 | 4.2847 | -0.11902 | 121.1609 | -0.23346 | -0.3479 | -0.20142 | 0.14648 | -0.32044 | 121.051 | 121.0785 | -0.2655 | -0.29755 | 0.064087 | -0.050354 | 0.1236 | 0.11444 | 0.17853 | 0.22888 | -0.40283 | 0.032043 | 0 | 0.013733 | 0.09613 | -0.022889 | -0.022889 | 0.041199 | 121.4584 | 120.932 | 4.5822 | -121.3852 | 121.3486 | 121.376 | 0.44403 | -121.3348
1240.3594 | 121.2708 | -0.3067 | 121.0281 | 0.0066373 | 0.012873 | 0.073557 | 0.0057656 | 0.060438 | -0.0031232 | -0.0035846 | 0.014572 | -0.0042852 | 0.062534 | 0.063164 | -0.010908 | -0.0070239 | 120.639 | -0.1236 | 4.3396 | -0.059509 | 121.0922 | -0.21515 | -0.31586 | -0.16479 | 0.23804 | -0.22888 | 120.9732 | 121.0739 | -0.2243 | -0.24261 | 0.091553 | -0.009155 | 0.064087 | 0.18311 | 0.24719 | 0.25635 | -0.3891 | 0.082398 | 0.064087 | -0.054931 | 0.14191 | 0.07782 | 0.013733 | 0.045777 | 121.3989 | 120.9457 | 4.6463 | -121.344 | 121.2799 | 121.3806 | 0.54474 | -121.2708
1242.1094 | 121.3531 | -0.27466 | 121.0052 | -0.00099167 | 0.006037 | 0.068857 | 0.0074746 | 0.063643 | 0.0011494 | -0.0035846 | 0.0069425 | 0.0025508 | 0.063816 | 0.064019 | -0.0085577 | -0.010442 | 120.6848 | -0.15106 | 4.3533 | -0.086975 | 121.1472 | -0.23804 | -0.36621 | -0.16022 | 0.27008 | -0.28839 | 121.051 | 121.0556 | -0.24719 | -0.28839 | 0.036621 | -0.091553 | 0.14191 | 0.1236 | 0.18768 | 0.27924 | -0.32044 | 0.027466 | -0.013733 | 0.045776 | 0.11444 | -0.013733 | 0 | 0.050354 | 121.4218 | 120.9595 | 4.628 | -121.3715 | 121.3257 | 121.3303 | 0.54474 | -121.2936
1243.8438 | 121.3074 | -0.28839 | 121.0327 | 0.0066373 | 0.0088142 | 0.071207 | 0.0085428 | 0.061506 | -0.0052594 | -0.0042254 | 0.029831 | -0.0010808 | 0.064457 | 0.063378 | -0.010694 | -0.0072375 | 120.694 | -0.068665 | 4.4037 | -0.041199 | 121.106 | -0.21973 | -0.33417 | -0.16022 | 0.29297 | -0.2655 | 121.051 | 121.0831 | -0.24261 | -0.27008 | 0.068664 | -0.045776 | 0.073242 | 0.21973 | 0.24719 | 0.29297 | -0.33875 | 0.045776 | 0.01831 | 0.01831 | 0.12817 | 0.022888 | 0.004578 | 0.050354 | 121.3943 | 120.9824 | 4.6921 | -121.3669 | 121.3394 | 121.3715 | 0.58136 | -121.3028
1245.5781 | 121.2021 | -0.30212 | 121.0602 | 0.014267 | 0.013941 | 0.073557 | 0.0034158 | 0.060011 | -0.0044048 | -0.0040118 | 0.014572 | -0.0030034 | 0.061252 | 0.064446 | -0.010053 | -0.0061695 | 120.7169 | -0.054932 | 4.3854 | -0.032043 | 121.1197 | -0.1831 | -0.29755 | -0.11902 | 0.25635 | -0.21057 | 120.9961 | 121.0602 | -0.21515 | -0.25635 | 0.11902 | 0.004578 | 0.059509 | 0.24719 | 0.27008 | 0.2655 | -0.34332 | 0.086975 | 0.045776 | -0.064087 | 0.18311 | 0.091553 | 0.045777 | 0 | 121.4218 | 121.019 | 4.6875 | -121.3577 | 121.2982 | 121.3623 | 0.55847 | -121.3165
1247.3281 | 121.2387 | -0.26093 | 121.1014 | -0.00099167 | 0.004969 | 0.069925 | 0.0046976 | 0.062147 | 0.00414 | -0.00273 | 0.014572 | 0.0034052 | 0.063602 | 0.06295 | -0.0053533 | -0.0072375 | 120.7214 | -0.13733 | 4.3396 | -0.059509 | 121.2204 | -0.19684 | -0.28839 | -0.14648 | 0.18768 | -0.32044 | 121.1014 | 121.1197 | -0.2243 | -0.24719 | 0.064087 | -0.027466 | 0.11902 | 0.1236 | 0.20142 | 0.22888 | -0.37994 | 0.036621 | 0.013733 | 0 | 0.11444 | -0.05951 | -0.073243 | 0.018311 | 121.4813 | 120.9824 | 4.6005 | -121.3898 | 121.3623 | 121.3806 | 0.44861 | -121.3486
1249 | 121.2158 | -0.30212 | 121.0602 | -0.00099167 | 0.0133 | 0.072489 | 0.0032022 | 0.058943 | -0.0044048 | -0.0035846 | 0.0069425 | -0.0027898 | 0.060611 | 0.063378 | -0.0077033 | -0.0042467 | 120.7214 | -0.032043 | 4.4174 | -0.041199 | 121.106 | -0.19226 | -0.31586 | -0.10529 | 0.29297 | -0.20142 | 121.0007 | 121.0602 | -0.22888 | -0.2655 | 0.10986 | -0.013733 | 0.045776 | 0.27008 | 0.26093 | 0.27466 | -0.33875 | 0.073242 | 0.036621 | -0.05951 | 0.19684 | 0.10071 | 0.064087 | 0 | 121.4081 | 121.0236 | 4.7195 | -121.376 | 121.3028 | 121.3623 | 0.59509 | -121.3257
1250.7344 | 121.2387 | -0.29297 | 121.051 | 0.0066373 | 0.0045416 | 0.070993 | 0.003843 | 0.062788 | 0.0028584 | -0.00273 | 0.0069425 | -0.00086724 | 0.061893 | 0.063805 | -0.0042853 | -0.0068103 | 120.7031 | -0.10986 | 4.3533 | -0.073242 | 121.1426 | -0.19226 | -0.32959 | -0.1831 | 0.21973 | -0.31128 | 121.0556 | 121.1151 | -0.24719 | -0.27008 | 0.10071 | -0.036621 | 0.091553 | 0.18311 | 0.21973 | 0.25635 | -0.3479 | 0.045777 | 0.022888 | 0.004578 | 0.10986 | -0.01831 | -0.041198 | 0.064087 | 121.4355 | 120.9961 | 4.6463 | -121.3806 | 121.3486 | 121.4081 | 0.5127 | -121.3211
1252.4844 | 121.3028 | -0.27924 | 121.0052 | -0.00099167 | 0.0081732 | 0.07313 | 0.0070474 | 0.06172 | -0.003764 | -0.0035846 | 0.0069425 | -0.0034308 | 0.063175 | 0.061882 | -0.011976 | -0.0059557 | 120.694 | -0.059509 | 4.4449 | -0.041199 | 121.1151 | -0.19684 | -0.32959 | -0.16937 | 0.32959 | -0.22888 | 121.019 | 121.0831 | -0.23804 | -0.2655 | 0.082398 | -0.050354 | 0.10986 | 0.21973 | 0.23804 | 0.28839 | -0.31128 | 0.041199 | 0.013733 | 0.013733 | 0.10986 | 0.050354 | 0.036621 | 0.07782 | 121.3943 | 120.9732 | 4.7241 | -121.3348 | 121.2982 | 121.3623 | 0.60883 | -121.2708
1254.1719 | 121.2845 | -0.37537 | 120.9366 | 0.0066373 | 0.0098822 | 0.069071 | 0.0036294 | 0.061934 | 0.00029476 | -0.0029436 | -0.00068649 | -0.0015082 | 0.062534 | 0.064232 | -0.0081305 | -0.0083057 | 120.6207 | -0.16937 | 4.4083 | -0.1236 | 121.0327 | -0.27924 | -0.39825 | -0.1831 | 0.29755 | -0.30212 | 120.9 | 120.9641 | -0.3067 | -0.33875 | 0.09613 | -0.022888 | 0.096131 | 0.20599 | 0.25177 | 0.27466 | -0.31586 | 0.068664 | 0.036621 | -0.036621 | 0.19226 | 0.073242 | 0.036621 | 0.027466 | 121.4081 | 120.9961 | 4.7836 | -121.3348 | 121.2753 | 121.3394 | 0.67291 | -121.2753
1255.9219 | 121.2158 | -0.2243 | 121.0968 | 0.014267 | 0.014155 | 0.070993 | 0.007261 | 0.063002 | -0.0016278 | -0.0018756 | 0.014572 | 0.00041436 | 0.062107 | 0.064232 | -0.0068487 | -0.0076647 | 120.7901 | 0 | 4.4312 | 0.050354 | 121.138 | -0.13733 | -0.24261 | -0.013733 | 0.3067 | -0.1236 | 121.051 | 121.0968 | -0.14191 | -0.19226 | 0.086975 | -0.018311 | 0.041198 | 0.2243 | 0.27466 | 0.29297 | -0.3067 | 0.082397 | 0.032043 | -0.045777 | 0.21057 | 0.10071 | 0.068665 | 0 | 121.3623 | 121.0144 | 4.6555 | -121.3394 | 121.2753 | 121.3211 | 0.53101 | -121.2891
1257.6094 | 121.225 | -0.25635 | 121.1243 | -0.0086212 | 0.0036872 | 0.067789 | 0.0066202 | 0.062361 | 0.0028584 | -0.0040118 | 0.0069425 | 0.0027644 | 0.065952 | 0.064659 | -0.0081305 | -0.0070239 | 120.7306 | -0.086975 | 4.4037 | -0.027466 | 121.2067 | -0.17853 | -0.29297 | -0.10529 | 0.22888 | -0.25635 | 121.0968 | 121.1746 | -0.1831 | -0.21515 | 0.07782 | -0.036621 | 0.082397 | 0.16937 | 0.22888 | 0.2655 | -0.39368 | 0.073243 | 0.041199 | -0.027466 | 0.15106 | 0 | -0.041199 | 0.050354 | 121.463 | 120.9869 | 4.66 | -121.4172 | 121.3531 | 121.431 | 0.48523 | -121.3394
1259.3438 | 121.3257 | -0.22888 | 121.0739 | 0.014267 | 0.011805 | 0.07313 | 0.0070474 | 0.060652 | -0.0041912 | -0.0040118 | -0.00068649 | -0.0023626 | 0.062534 | 0.064019 | -0.011976 | -0.0089465 | 120.7397 | 0 | 4.4678 | 0.009155 | 121.1563 | -0.16479 | -0.28839 | -0.059509 | 0.37994 | -0.13275 | 121.0281 | 121.106 | -0.1831 | -0.21515 | 0.064087 | -0.059509 | 0.082397 | 0.22888 | 0.23804 | 0.29755 | -0.33417 | 0.045777 | 0.013733 | -0.045777 | 0.16937 | 0.096131 | 0.082398 | 0.032043 | 121.3852 | 120.9686 | 4.6967 | -121.3623 | 121.257 | 121.3348 | 0.60883 | -121.2891
1261.0938 | 121.225 | -0.30212 | 121.0556 | 0.0066373 | 0.014155 | 0.070139 | 0.0036294 | 0.065565 | -0.00034604 | -0.0018756 | 0.0069425 | -0.0010808 | 0.061466 | 0.063378 | -0.0079169 | -0.0076647 | 120.7169 | -0.045776 | 4.4266 | -0.022888 | 121.0785 | -0.18768 | -0.31128 | -0.07782 | 0.27924 | -0.17853 | 120.9961 | 121.0785 | -0.19684 | -0.23346 | 0.11444 | -0.009155 | 0.022888 | 0.25635 | 0.27924 | 0.28839 | -0.33875 | 0.10529 | 0.068665 | -0.059509 | 0.2243 | 0.1236 | 0.054931 | 0.022888 | 121.3806 | 121.019 | 4.7287 | -121.3669 | 121.2982 | 121.3806 | 0.58136 | -121.2891
1262.8438 | 121.2387 | -0.20599 | 121.1197 | 0.014267 | 0.0096686 | 0.072489 | 0.003843 | 0.060438 | -0.0035504 | -0.0063616 | 0.014572 | -0.00086724 | 0.062961 | 0.062737 | -0.0077033 | -0.0078783 | 120.7581 | 0.018311 | 4.454 | 0.050354 | 121.1655 | -0.12817 | -0.23346 | -0.064087 | 0.29755 | -0.17395 | 121.1151 | 121.1472 | -0.16479 | -0.19226 | 0.07782 | -0.027465 | 0.045776 | 0.22431 | 0.25635 | 0.28381 | -0.36163 | 0.041199 | 0.013733 | -0.004578 | 0.14191 | 0.032044 | 0.018311 | 0.027466 | 121.3715 | 120.9641 | 4.66 | -121.3531 | 121.3211 | 121.3531 | 0.50354 | -121.312
1264.5938 | 121.2479 | -0.21973 | 121.1838 | 0.0066373 | 0.0083868 | 0.071421 | -0.00064295 | 0.06172 | 0.0028584 | -0.0057208 | 0.014572 | 0.004046 | 0.061466 | 0.064019 | -0.0066351 | -0.0072375 | 120.7123 | -0.11444 | 4.3304 | -0.013733 | 121.2753 | -0.13733 | -0.24261 | -0.10071 | 0.16479 | -0.23804 | 121.1838 | 121.2158 | -0.16479 | -0.18768 | 0.082398 | -0.022888 | 0.091553 | 0.10529 | 0.20599 | 0.22888 | -0.4715 | 0.054932 | 0.032044 | 0 | 0.11902 | -0.01831 | -0.050354 | 0.032043 | 121.4951 | 120.932 | 4.5502 | -121.4264 | 121.4035 | 121.4355 | 0.38452 | -121.3715
1266.2656 | 121.3531 | -0.16022 | 121.1288 | 0.0066373 | 0.012659 | 0.072062 | 0.0096108 | 0.062147 | -0.0052594 | -0.003371 | -0.00068649 | -0.0015082 | 0.06232 | 0.063378 | -0.011549 | -0.0059557 | 120.8267 | 0.068665 | 4.454 | 0.064087 | 121.2296 | -0.09613 | -0.21973 | 0.009155 | 0.36163 | -0.064087 | 121.1197 | 121.1609 | -0.12817 | -0.14648 | 0.064087 | -0.05951 | 0.10071 | 0.22888 | 0.2243 | 0.28381 | -0.30212 | 0.032043 | 0.013733 | -0.009155 | 0.16937 | 0.09613 | 0.082397 | 0.032044 | 121.3898 | 120.9869 | 4.6143 | -121.3486 | 121.2799 | 121.3211 | 0.52185 | -121.2753
1268 | 121.312 | -0.17853 | 121.17 | 0.0066373 | 0.0083868 | 0.072489 | 0.0074746 | 0.063856 | -0.0026958 | -0.0042254 | 0.0069425 | -0.0012946 | 0.062748 | 0.062096 | -0.0081305 | -0.0093737 | 120.8176 | 0.009155 | 4.4495 | 0.059509 | 121.2433 | -0.13275 | -0.24261 | -0.073242 | 0.29755 | -0.17395 | 121.17 | 121.2204 | -0.13733 | -0.17395 | 0.045777 | -0.064087 | 0.073242 | 0.18768 | 0.23804 | 0.30212 | -0.35248 | 0.041199 | 0.004578 | 0 | 0.10529 | 0.004578 | 0 | 0.050354 | 121.4218 | 120.9961 | 4.628 | -121.4127 | 121.3486 | 121.3989 | 0.47607 | -121.344
1269.7344 | 121.3165 | -0.17395 | 121.1746 | 0.0066373 | 0.0083868 | 0.072062 | 0.0053384 | 0.06172 | -0.0026958 | -0.0057208 | 0.014572 | -0.002149 | 0.063816 | 0.062096 | -0.01048 | -0.0076647 | 120.8405 | 0.050354 | 4.4998 | 0.073242 | 121.2708 | -0.091553 | -0.19684 | -0.022888 | 0.36163 | -0.11902 | 121.1517 | 121.1929 | -0.11444 | -0.16937 | 0.082397 | -0.022888 | 0.09613 | 0.2243 | 0.24719 | 0.27008 | -0.33417 | 0.059509 | 0.004577 | -0.022889 | 0.15106 | 0.054931 | 0.050354 | 0.01831 | 121.4447 | 121.0144 | 4.6738 | -121.3715 | 121.3257 | 121.3669 | 0.53558 | -121.344
1271.5 | 121.4081 | -0.1831 | 121.1517 | 0.0066373 | 0.0045416 | 0.069498 | 0.0051248 | 0.061506 | 0.002431 | -0.003371 | 0.0069425 | 0.0019098 | 0.06232 | 0.067009 | -0.0059943 | -0.0080921 | 120.7855 | -0.07782 | 4.3991 | -0.009155 | 121.3074 | -0.15106 | -0.24261 | -0.068665 | 0.27008 | -0.19684 | 121.2158 | 121.2387 | -0.15106 | -0.17395 | 0.032043 | -0.05951 | 0.15564 | 0.10528 | 0.17395 | 0.23346 | -0.36621 | 0.032043 | 0.009155 | 0.064087 | 0.11444 | -0.013733 | -0.022888 | 0.086975 | 121.4905 | 120.9686 | 4.5822 | -121.3943 | 121.3989 | 121.4218 | 0.45319 | -121.3257
1273.1875 | 121.3715 | -0.15106 | 121.17 | -0.00099167 | 0.01095 | 0.072489 | 0.0046976 | 0.05937 | -0.0059002 | -0.0042254 | -0.00068649 | -0.0012946 | 0.063602 | 0.061241 | -0.011762 | -0.0070239 | 120.8084 | 0.032043 | 4.4357 | 0.041199 | 121.2845 | -0.12817 | -0.21057 | -0.018311 | 0.35248 | -0.082397 | 121.1517 | 121.2296 | -0.11902 | -0.16479 | 0.022888 | -0.059509 | 0.11444 | 0.18311 | 0.19226 | 0.25177 | -0.36163 | 0.032043 | -0.013733 | -0.018311 | 0.13275 | 0.068665 | 0.082398 | 0.059509 | 121.4355 | 120.9595 | 4.5868 | -121.3806 | 121.3028 | 121.3806 | 0.50354 | -121.3348
1274.9219 | 121.3623 | -0.16937 | 121.1517 | 0.0066373 | 0.011378 | 0.070566 | 0.0081154 | 0.065565 | -0.0029094 | -0.0059344 | 0.0069425 | -0.0015082 | 0.064029 | 0.065087 | -0.010267 | -0.0083057 | 120.8817 | 0.091553 | 4.4998 | 0.073242 | 121.2524 | -0.10071 | -0.21515 | 0.018311 | 0.39825 | -0.07782 | 121.1609 | 121.2158 | -0.10986 | -0.13275 | 0.068665 | -0.045776 | 0.10071 | 0.26093 | 0.24261 | 0.28839 | -0.27008 | 0.05951 | 0.036622 | 0.009156 | 0.18768 | 0.091553 | 0.054931 | 0.064087 | 121.4218 | 121.051 | 4.6692 | -121.3669 | 121.3303 | 121.3852 | 0.56763 | -121.2845
1276.6719 | 121.2753 | -0.21057 | 121.2341 | 0.014267 | 0.010096 | 0.069498 | 0.005552 | 0.062361 | -0.0012006 | -0.0070026 | 0.014572 | -1.2844e-05 | 0.06467 | 0.064446 | -0.0083441 | -0.0089465 | 120.8359 | 0.018311 | 4.454 | 0.041199 | 121.2708 | -0.11444 | -0.21515 | -0.036621 | 0.28839 | -0.11902 | 121.1563 | 121.2204 | -0.10071 | -0.14648 | 0.09613 | -0.004578 | 0.036621 | 0.22888 | 0.25177 | 0.25635 | -0.39826 | 0.10986 | 0.064087 | -0.07782 | 0.17395 | 0.091552 | 0.027465 | -0.013733 | 121.4813 | 121.0464 | 4.6646 | -121.4493 | 121.3669 | 121.431 | 0.49896 | -121.3806
1278.3594 | 121.4264 | -0.15106 | 121.1746 | -0.00099167 | 0.0079596 | 0.068857 | 0.005552 | 0.062147 | 0.0043536 | -0.0023028 | 0.014572 | 0.004046 | 0.064243 | 0.065087 | -0.0059943 | -0.0091601 | 120.8176 | -0.068665 | 4.422 | 0.009155 | 121.3577 | -0.11902 | -0.23804 | -0.054932 | 0.27008 | -0.20142 | 121.2341 | 121.2662 | -0.16022 | -0.19226 | 0.032043 | -0.086975 | 0.1831 | 0.082397 | 0.16022 | 0.24719 | -0.35706 | -0.009155 | -0.041199 | 0.059509 | 0.09613 | -0.050354 | -0.009155 | 0.091552 | 121.5088 | 120.9686 | 4.5731 | -121.4127 | 121.3852 | 121.4172 | 0.42114 | -121.3669
1280.0938 | 121.3943 | -0.16022 | 121.1792 | -0.00099167 | 0.013941 | 0.073343 | 0.0034158 | 0.060652 | -0.0022686 | -0.00273 | 0.0069425 | -0.0023626 | 0.063816 | 0.061882 | -0.010908 | -0.0053149 | 120.8038 | -0.004578 | 4.4403 | 0.041199 | 121.2799 | -0.10071 | -0.21515 | -0.036621 | 0.30212 | -0.09613 | 121.1746 | 121.2524 | -0.10986 | -0.16937 | 0.059509 | -0.054932 | 0.10071 | 0.15564 | 0.20142 | 0.25635 | -0.37537 | 0.050354 | -0.009156 | -0.004577 | 0.1236 | 0.064087 | 0.073243 | 0.073242 | 121.4401 | 120.9641 | 4.6005 | -121.3943 | 121.3348 | 121.4127 | 0.46234 | -121.3486
1281.8438 | 121.2845 | -0.20599 | 121.225 | -0.00099167 | 0.006037 | 0.070139 | 0.0040566 | 0.062147 | 0.00414 | -0.0046526 | 0.0069425 | 0.0059686 | 0.061252 | 0.06295 | -0.0027899 | -0.0080921 | 120.7809 | -0.09613 | 4.3945 | -0.013733 | 121.3394 | -0.13733 | -0.25177 | -0.10529 | 0.18768 | -0.25635 | 121.2158 | 121.2479 | -0.15106 | -0.18768 | 0.068665 | -0.045776 | 0.11444 | 0.10986 | 0.19226 | 0.23804 | -0.44403 | 0.054932 | 0.018311 | -0.009156 | 0.10071 | -0.050354 | -0.068665 | 0.022888 | 121.5454 | 120.9869 | 4.6005 | -121.4767 | 121.4218 | 121.4539 | 0.39368 | -121.4127
1283.5781 | 121.3715 | -0.17853 | 121.1929 | 0.014267 | 0.0066778 | 0.070993 | 0.0061928 | 0.06172 | -0.00013244 | -0.0035846 | 0.0069425 | -0.0015082 | 0.061893 | 0.0653 | -0.010053 | -0.0076647 | 120.7581 | -0.064087 | 4.4128 | -0.013733 | 121.3074 | -0.13275 | -0.26093 | -0.11902 | 0.27466 | -0.21057 | 121.2341 | 121.2524 | -0.15106 | -0.1831 | 0.045777 | -0.082397 | 0.11444 | 0.11444 | 0.16479 | 0.24719 | -0.43488 | 0.027466 | -0.004577 | 0.041199 | 0.059509 | -0.032043 | -0.027466 | 0.059509 | 121.4859 | 120.9366 | 4.5914 | -121.4539 | 121.4127 | 121.431 | 0.45319 | -121.376
1285.2656 | 121.3577 | -0.17395 | 121.2158 | -0.00099167 | 0.0066778 | 0.072916 | 0.0032022 | 0.063429 | 0.004781 | -0.0031574 | 0.0069425 | 0.0014826 | 0.061039 | 0.063164 | -0.0057807 | -0.0068103 | 120.8542 | 0.004578 | 4.4769 | 0.032043 | 121.3257 | -0.11444 | -0.2243 | -0.045776 | 0.30212 | -0.20142 | 121.2296 | 121.2616 | -0.13733 | -0.16937 | 0.059509 | -0.050354 | 0.10986 | 0.17853 | 0.20599 | 0.25635 | -0.36163 | 0.036621 | 0.004577 | 0.013733 | 0.12817 | -0.027466 | -0.032043 | 0.045777 | 121.4996 | 121.0281 | 4.6509 | -121.4401 | 121.4035 | 121.4355 | 0.47607 | -121.3852
1287.0156 | 121.3028 | -0.1831 | 121.2341 | -0.00099167 | 0.012232 | 0.074625 | 0.0057656 | 0.062574 | -0.0052594 | -0.003371 | -0.008316 | -0.002149 | 0.06232 | 0.063805 | -0.010053 | -0.0059557 | 120.8038 | 0.027466 | 4.4449 | 0.022888 | 121.3074 | -0.1236 | -0.23804 | -0.064087 | 0.27466 | -0.13733 | 121.1655 | 121.2616 | -0.11444 | -0.16022 | 0.059509 | -0.054932 | 0.073242 | 0.21057 | 0.20599 | 0.26093 | -0.4303 | 0.068664 | 0.022888 | -0.068665 | 0.11902 | 0.045776 | 0.022888 | 0.027466 | 121.4905 | 120.9869 | 4.628 | -121.4722 | 121.3486 | 121.4447 | 0.45776 | -121.3943
1288.75 | 121.2708 | -0.20142 | 121.225 | 0.0066373 | 0.014368 | 0.073771 | 0.0040566 | 0.061934 | -0.00034604 | -0.0055072 | -0.00068649 | -0.0030034 | 0.060825 | 0.060387 | -0.0070623 | -0.0061695 | 120.8771 | 0.073242 | 4.5136 | 0.050354 | 121.2753 | -0.09613 | -0.20599 | -0.013733 | 0.31586 | -0.086975 | 121.1609 | 121.1975 | -0.11444 | -0.16479 | 0.10529 | -0.004578 | 0.050354 | 0.27466 | 0.25177 | 0.25635 | -0.3479 | 0.086975 | 0.036621 | -0.064087 | 0.18768 | 0.11444 | 0.07782 | -0.027466 | 121.4767 | 121.0785 | 4.715 | -121.431 | 121.3623 | 121.3989 | 0.51727 | -121.3898
1290.5 | 121.312 | -0.20599 | 121.2479 | -0.00099167 | 0.0088142 | 0.07078 | 0.0034158 | 0.062788 | 0.00414 | -0.0025164 | 0.022202 | 0.0019098 | 0.060825 | 0.063805 | -0.0051397 | -0.0074511 | 120.7581 | -0.10986 | 4.3991 | -0.013733 | 121.3577 | -0.11902 | -0.25177 | -0.10986 | 0.18768 | -0.24719 | 121.2524 | 121.2387 | -0.13733 | -0.18768 | 0.086975 | -0.045776 | 0.10986 | 0.096131 | 0.19226 | 0.23804 | -0.48981 | 0.068665 | 0.018311 | 0.004577 | 0.096131 | -0.041198 | -0.059509 | -0.009156 | 121.5637 | 120.9641 | 4.6051 | -121.4996 | 121.4584 | 121.4447 | 0.39368 | -121.4355
1292.1875 | 121.3623 | -0.18768 | 121.2021 | 0.0066373 | 0.0073188 | 0.073557 | 0.0076882 | 0.06172 | -0.0033368 | -0.0031574 | -0.00068649 | -0.00086724 | 0.063175 | 0.061241 | -0.0089849 | -0.0059557 | 120.8221 | 0.022888 | 4.4861 | 0.032043 | 121.3211 | -0.13733 | -0.25177 | -0.11902 | 0.30212 | -0.17853 | 121.2341 | 121.2708 | -0.14191 | -0.19684 | 0.050354 | -0.064087 | 0.11902 | 0.21057 | 0.21973 | 0.28381 | -0.37994 | 0.045776 | -0.009155 | 0.032044 | 0.068664 | 0.009155 | 0.01831 | 0.068665 | 121.5088 | 121.0098 | 4.6738 | -121.4539 | 121.4218 | 121.4584 | 0.48981 | -121.3989
1293.9219 | 121.4264 | -0.16937 | 121.1975 | 0.0066373 | 0.004969 | 0.072489 | 0.00897 | 0.061506 | 0.00072196 | -0.0029436 | 0.0069425 | 0.0016962 | 0.065525 | 0.0653 | -0.011121 | -0.0080921 | 120.7809 | -0.07782 | 4.4312 | -0.009155 | 121.3394 | -0.13275 | -0.25635 | -0.13275 | 0.24261 | -0.23804 | 121.2524 | 121.2753 | -0.14648 | -0.1831 | 0.036622 | -0.086975 | 0.14191 | 0.091553 | 0.16022 | 0.24719 | -0.41656 | 0.022889 | -0.013732 | 0.054931 | 0.036622 | -0.068664 | -0.054932 | 0.07782 | 121.5088 | 120.9503 | 4.6005 | -121.4539 | 121.4218 | 121.4447 | 0.41199 | -121.3806
1295.6562 | 121.3943 | -0.17853 | 121.2296 | -0.00099167 | 0.0079596 | 0.072916 | 0.0098244 | 0.06172 | -0.0029094 | -0.0037982 | 0.014572 | -0.00065364 | 0.063388 | 0.060387 | -0.0089849 | -0.0080921 | 120.845 | 0.027466 | 4.4907 | 0.041199 | 121.312 | -0.10071 | -0.24719 | -0.09613 | 0.3067 | -0.17395 | 121.2204 | 121.2708 | -0.13733 | -0.18768 | 0.07782 | -0.068664 | 0.082398 | 0.20599 | 0.21973 | 0.28839 | -0.38452 | 0.041199 | -0.009155 | -0.009155 | 0.082398 | 0.004578 | 0.013733 | 0.041199 | 121.4905 | 121.0236 | 4.6692 | -121.4767 | 121.3989 | 121.4493 | 0.48523 | -121.4172
1297.3438 | 121.3623 | -0.19684 | 121.2296 | 0.0066373 | 0.012018 | 0.075052 | 0.007261 | 0.060225 | -0.0026958 | -0.0042254 | 0.014572 | -0.0019354 | 0.062961 | 0.061882 | -0.010908 | -0.0070239 | 120.7993 | 0 | 4.4495 | 0.022888 | 121.3257 | -0.091553 | -0.21973 | -0.068665 | 0.28381 | -0.12817 | 121.1929 | 121.2662 | -0.14191 | -0.16479 | 0.10529 | -0.022889 | 0.096131 | 0.19684 | 0.21973 | 0.24261 | -0.4303 | 0.054931 | 0.032043 | -0.036621 | 0.12817 | 0.068664 | 0.036621 | 0.036621 | 121.5225 | 120.9961 | 4.6463 | -121.4493 | 121.3898 | 121.463 | 0.48065 | -121.3943
1299.0938 | 121.4081 | -0.16022 | 121.2112 | -0.00099167 | 0.0098822 | 0.072916 | 0.007261 | 0.062788 | -0.0016278 | -0.0057208 | -0.008316 | -0.0025762 | 0.062534 | 0.063591 | -0.010694 | -0.0083057 | 120.8908 | 0.073242 | 4.541 | 0.082397 | 121.312 | -0.10529 | -0.20599 | 0.009155 | 0.41199 | -0.09613 | 121.1975 | 121.2708 | -0.10529 | -0.14191 | 0.054931 | -0.045777 | 0.10071 | 0.23346 | 0.24261 | 0.28839 | -0.32043 | 0.054931 | 0.01831 | -0.013733 | 0.16937 | 0.064087 | 0.045777 | 0.059509 | 121.4722 | 121.051 | 4.7012 | -121.4172 | 121.3577 | 121.431 | 0.5722 | -121.3531
1300.7812 | 121.4264 | -0.17853 | 121.2204 | 0.0066373 | 0.0088142 | 0.072062 | 0.0066202 | 0.062361 | -0.0018414 | -0.00273 | 0.0069425 | 0.00084176 | 0.06232 | 0.063164 | -0.0079169 | -0.0068103 | 120.8084 | -0.07782 | 4.422 | -0.018311 | 121.3531 | -0.14191 | -0.26093 | -0.11902 | 0.25635 | -0.21057 | 121.2479 | 121.2936 | -0.14648 | -0.19684 | 0.036621 | -0.082397 | 0.13275 | 0.10071 | 0.16022 | 0.24261 | -0.41199 | 0.032044 | -0.01831 | 0.027466 | 0.059509 | -0.032043 | -0.013733 | 0.073242 | 121.5317 | 120.9869 | 4.6005 | -121.4813 | 121.4264 | 121.4722 | 0.43488 | -121.4172
1302.5469 | 121.3623 | -0.19226 | 121.2479 | -0.00099167 | 0.01095 | 0.070993 | 0.003843 | 0.063643 | 0.003072 | -0.0029436 | 0.0069425 | 0.00062796 | 0.061679 | 0.0653 | -0.0059943 | -0.0057421 | 120.8359 | -0.07782 | 4.4174 | -0.013733 | 121.3577 | -0.13275 | -0.23346 | -0.082397 | 0.2243 | -0.19684 | 121.2158 | 121.2799 | -0.13275 | -0.17853 | 0.05951 | -0.041198 | 0.10986 | 0.11444 | 0.17853 | 0.21973 | -0.41199 | 0.05951 | 0.013733 | -0.032044 | 0.10986 | -0.004577 | -0.01831 | 0.032043 | 121.55 | 121.0281 | 4.6097 | -121.4813 | 121.4081 | 121.4722 | 0.41656 | -121.4264
1304.2188 | 121.4447 | -0.14191 | 121.2067 | -0.00099167 | 0.011378 | 0.073984 | 0.0066202 | 0.061506 | -0.0046184 | -0.0057208 | 0.0069425 | -0.0034308 | 0.062534 | 0.062737 | -0.010267 | -0.0078783 | 120.9091 | 0.10071 | 4.5731 | 0.086975 | 121.3211 | -0.10986 | -0.20142 | -0.004578 | 0.39825 | -0.073242 | 121.1884 | 121.2616 | -0.10986 | -0.16479 | 0.032044 | -0.059509 | 0.11444 | 0.24262 | 0.22888 | 0.28839 | -0.29755 | 0.032044 | -0.022888 | -0.018311 | 0.13733 | 0.068665 | 0.091553 | 0.054932 | 121.463 | 121.051 | 4.715 | -121.4081 | 121.3303 | 121.4035 | 0.54016 | -121.3715
1305.9531 | 121.4539 | -0.14191 | 121.1975 | -0.0086212 | 0.011378 | 0.07313 | 0.007261 | 0.065138 | -0.0024822 | -0.0052936 | 0.0069425 | -0.0032172 | 0.061893 | 0.062096 | -0.010053 | -0.0051013 | 120.8908 | 0.054932 | 4.5136 | 0.07782 | 121.344 | -0.091553 | -0.22888 | -0.013733 | 0.3891 | -0.068665 | 121.2158 | 121.2799 | -0.10986 | -0.14191 | 0.050354 | -0.086975 | 0.14648 | 0.19684 | 0.21973 | 0.3067 | -0.3067 | 0.032044 | 0 | 0.01831 | 0.12817 | 0.073242 | 0.073242 | 0.082397 | 121.4859 | 121.0327 | 4.6555 | -121.4264 | 121.3577 | 121.4218 | 0.53101 | -121.3394
1307.7031 | 121.3257 | -0.20599 | 121.2616 | -0.00099167 | 0.011591 | 0.071848 | 0.0019204 | 0.060865 | 0.004781 | -0.0023028 | -0.008316 | 0.001269 | 0.062961 | 0.065087 | -0.0064215 | -0.0070239 | 120.8496 | -0.082397 | 4.4495 | -0.013733 | 121.3806 | -0.13275 | -0.22888 | -0.07782 | 0.22888 | -0.24261 | 121.2616 | 121.3394 | -0.16479 | -0.1831 | 0.073243 | -0.022888 | 0.11902 | 0.1236 | 0.19226 | 0.21515 | -0.41199 | 0.041199 | 0.022889 | 0 | 0.12817 | -0.036621 | -0.05951 | 0.07782 | 121.5866 | 121.0556 | 4.6555 | -121.4905 | 121.4676 | 121.5454 | 0.43488 | -121.4447
1309.4531 | 121.4081 | -0.14648 | 121.2479 | 0.0066373 | 0.0066778 | 0.072062 | 0.003843 | 0.063215 | 0.0032856 | -0.001662 | 0.0069425 | 0.00062796 | 0.06467 | 0.063591 | -0.0049261 | -0.0080921 | 120.8954 | 0.018311 | 4.509 | 0.036621 | 121.3715 | -0.13275 | -0.2243 | -0.027466 | 0.32501 | -0.17395 | 121.2524 | 121.2799 | -0.13275 | -0.16022 | 0.013733 | -0.07782 | 0.1236 | 0.16479 | 0.18311 | 0.26093 | -0.35248 | 0.013733 | -0.013733 | 0.004577 | 0.11902 | -0.027466 | -0.013733 | 0.032043 | 121.5179 | 121.0419 | 4.6555 | -121.4722 | 121.3989 | 121.4264 | 0.4715 | -121.4081
1311.2031 | 121.3989 | -0.17853 | 121.2479 | 0.0066373 | 0.006037 | 0.069925 | 0.0034158 | 0.06172 | 0.0032856 | -0.001662 | 0.0069425 | 0.0031916 | 0.06467 | 0.065728 | -0.0059943 | -0.0055285 | 120.9045 | 0 | 4.5273 | 0.045776 | 121.3531 | -0.13275 | -0.24261 | -0.036621 | 0.31128 | -0.19226 | 121.2616 | 121.3303 | -0.13733 | -0.15564 | 0.045777 | -0.064087 | 0.10528 | 0.17853 | 0.2243 | 0.28839 | -0.34332 | 0.041199 | 0.022888 | 0.013733 | 0.14191 | -0.013733 | -0.036621 | 0.082397 | 121.5317 | 121.0831 | 4.7058 | -121.4905 | 121.4401 | 121.5088 | 0.48981 | -121.4035
1312.8906 | 121.4081 | -0.16937 | 121.2524 | -0.016251 | 0.0058234 | 0.071634 | 0.0087564 | 0.063215 | -0.0033368 | -0.00273 | 0.014572 | -0.0030034 | 0.065097 | 0.065087 | -0.011549 | -0.0063831 | 120.8221 | -0.022888 | 4.4815 | 0.013733 | 121.3577 | -0.12817 | -0.22888 | -0.10071 | 0.30212 | -0.19226 | 121.2753 | 121.344 | -0.14191 | -0.17853 | 0.041199 | -0.059509 | 0.10529 | 0.14649 | 0.18311 | 0.24261 | -0.4303 | 0.027466 | -0.009155 | 0.022889 | 0.068665 | -0.022888 | -0.013733 | 0.091553 | 121.5271 | 120.9915 | 4.6509 | -121.4813 | 121.4447 | 121.5134 | 0.4715 | -121.431
1314.625 | 121.4081 | -0.17853 | 121.2662 | 0.0066373 | 0.0062506 | 0.068857 | 0.0064066 | 0.065138 | 0.0020038 | -0.0025164 | -0.00068649 | 0.0016962 | 0.06467 | 0.064659 | -0.0077033 | -0.0072375 | 120.9137 | 0.004578 | 4.5273 | 0.027466 | 121.376 | -0.10986 | -0.23346 | -0.054932 | 0.31586 | -0.18768 | 121.2982 | 121.3623 | -0.1236 | -0.16022 | 0.068665 | -0.054931 | 0.10986 | 0.18311 | 0.20599 | 0.26093 | -0.35248 | 0.054932 | 0.018311 | 0.032044 | 0.1236 | -0.009155 | -0.027466 | 0.096131 | 121.5546 | 121.0922 | 4.7058 | -121.4996 | 121.4767 | 121.5408 | 0.49438 | -121.4264
1316.3594 | 121.344 | -0.19684 | 121.2799 | -0.00099167 | 0.0075324 | 0.070353 | 0.002775 | 0.062147 | 0.0020038 | -0.0042254 | 0.0069425 | 0.00084176 | 0.063602 | 0.063805 | -0.0066351 | -0.0063831 | 120.8313 | -0.10529 | 4.4266 | -0.018311 | 121.3852 | -0.11902 | -0.23346 | -0.10529 | 0.2243 | -0.23346 | 121.2891 | 121.3577 | -0.12817 | -0.18768 | 0.077819 | -0.036621 | 0.10529 | 0.091552 | 0.17853 | 0.21515 | -0.44861 | 0.068664 | 0.009155 | 0.009155 | 0.091552 | -0.036621 | -0.045776 | 0.07782 | 121.582 | 121.0281 | 4.6234 | -121.5134 | 121.4859 | 121.5546 | 0.42114 | -121.4676
1318.0469 | 121.4035 | -0.16937 | 121.2524 | -0.00099167 | 0.0075324 | 0.072489 | 0.0059792 | 0.062574 | -0.0029094 | -0.0046526 | -0.00068649 | -0.0017218 | 0.06232 | 0.062523 | -0.011762 | -0.0080921 | 120.8862 | 0.032043 | 4.5502 | 0.054932 | 121.3303 | -0.10986 | -0.21057 | -0.07782 | 0.34332 | -0.15106 | 121.2524 | 121.344 | -0.13275 | -0.18768 | 0.05951 | -0.041198 | 0.07782 | 0.20142 | 0.22431 | 0.2655 | -0.36621 | 0.036622 | -0.01831 | 0 | 0.091553 | 0.018311 | 0.036621 | 0.091553 | 121.4996 | 121.0556 | 4.7195 | -121.463 | 121.4218 | 121.5134 | 0.5127 | -121.4401
1319.7969 | 121.4401 | -0.16022 | 121.2524 | -0.00099167 | 0.007746 | 0.073343 | 0.0064066 | 0.064924 | -0.0067548 | -0.0042254 | 0.0069425 | -0.0042852 | 0.06232 | 0.061028 | -0.0094123 | -0.0068103 | 120.9549 | 0.073242 | 4.5959 | 0.054932 | 121.3394 | -0.091553 | -0.20599 | 0 | 0.43945 | -0.050354 | 121.2021 | 121.3028 | -0.10529 | -0.13733 | 0.068664 | -0.045777 | 0.086976 | 0.23346 | 0.21515 | 0.26093 | -0.29755 | 0.054931 | 0.022888 | -0.050354 | 0.16022 | 0.10986 | 0.086975 | 0.050354 | 121.4996 | 121.1151 | 4.7562 | -121.4584 | 121.3623 | 121.463 | 0.59967 | -121.3898
1321.5469 | 121.3898 | -0.19684 | 121.2936 | 0.014267 | 0.011378 | 0.070566 | 0.002775 | 0.061079 | 0.0020038 | -0.0023028 | 0.014572 | 0.001269 | 0.063388 | 0.065728 | -0.0059943 | -0.0087329 | 120.8633 | -0.082397 | 4.4449 | -0.004578 | 121.3898 | -0.11444 | -0.25177 | -0.091553 | 0.22888 | -0.20599 | 121.2936 | 121.344 | -0.1236 | -0.17395 | 0.082397 | -0.054932 | 0.096131 | 0.11444 | 0.19226 | 0.24719 | -0.4303 | 0.073242 | 0.022888 | 0 | 0.10529 | -0.009156 | -0.032044 | 0.050354 | 121.5866 | 121.0602 | 4.6417 | -121.5454 | 121.4905 | 121.5408 | 0.42572 | -121.4676
1323.2344 | 121.4218 | -0.14648 | 121.2662 | -0.00099167 | 0.010096 | 0.073771 | 0.0051248 | 0.060438 | -0.0016278 | -0.006148 | 0.0069425 | -0.003858 | 0.063175 | 0.065728 | -0.012189 | -0.010869 | 120.9274 | 0.064087 | 4.6005 | 0.082397 | 121.3074 | -0.086975 | -0.21515 | 0 | 0.41199 | -0.07782 | 121.2341 | 121.3257 | -0.10986 | -0.14648 | 0.059509 | -0.068665 | 0.041199 | 0.21057 | 0.22888 | 0.29755 | -0.33875 | 0.036621 | 0 | -0.032043 | 0.14648 | 0.068664 | 0.068664 | 0.05951 | 121.4539 | 121.0739 | 4.747 | -121.4813 | 121.3806 | 121.4722 | 0.55847 | -121.4127
1324.9688 | 121.3257 | -0.19226 | 121.3028 | -0.00099167 | 0.013941 | 0.073557 | 0.0032022 | 0.061079 | -0.0026958 | -0.0035846 | 0.014572 | -0.0036444 | 0.059543 | 0.065728 | -0.0083441 | -0.010015 | 120.9641 | 0.068665 | 4.5547 | 0.07782 | 121.344 | -0.07782 | -0.19684 | 0.022888 | 0.35706 | -0.059509 | 121.2479 | 121.3165 | -0.10071 | -0.13733 | 0.11444 | -0.004577 | 0.041199 | 0.26093 | 0.27008 | 0.27466 | -0.33875 | 0.091553 | 0.054932 | -0.054931 | 0.21515 | 0.13275 | 0.07782 | 0.013733 | 121.5363 | 121.1563 | 4.747 | -121.4996 | 121.4401 | 121.5088 | 0.54932 | -121.4401
1326.7031 | 121.3531 | -0.17853 | 121.2936 | -0.0086212 | 0.010309 | 0.077829 | 0.0029886 | 0.061506 | -0.0048322 | -0.0055072 | 0.0069425 | -0.0034308 | 0.061679 | 0.061882 | -0.010053 | -0.0072375 | 120.9 | 0.013733 | 4.5319 | 0.032043 | 121.3669 | -0.086975 | -0.20599 | -0.032043 | 0.29755 | -0.11902 | 121.2799 | 121.3257 | -0.10529 | -0.16479 | 0.091553 | -0.027466 | 0.073242 | 0.19226 | 0.21057 | 0.23804 | -0.39368 | 0.073242 | 0.013733 | -0.013733 | 0.14648 | 0.059509 | 0.045776 | 0.032044 | 121.5454 | 121.0785 | 4.7104 | -121.4996 | 121.4584 | 121.5042 | 0.47607 | -121.4584
1328.4531 | 121.3806 | -0.1831 | 121.2936 | -0.00099167 | 0.0073188 | 0.071634 | 0.0023476 | 0.063643 | 0.0043536 | -0.004439 | -0.00068649 | 0.0014826 | 0.063388 | 0.063378 | -0.0059943 | -0.0091601 | 120.9412 | -0.009155 | 4.5181 | 0.032043 | 121.4172 | -0.10071 | -0.22888 | -0.050354 | 0.27008 | -0.21057 | 121.2753 | 121.3486 | -0.14191 | -0.16937 | 0.082397 | -0.045777 | 0.1236 | 0.17395 | 0.21515 | 0.26093 | -0.35248 | 0.041198 | 0.013732 | -0.01831 | 0.13275 | -0.027466 | -0.041198 | 0.054932 | 121.6003 | 121.1243 | 4.7012 | -121.5225 | 121.4584 | 121.5317 | 0.45319 | -121.463
1330.1406 | 121.3989 | -0.16479 | 121.3028 | 0.0066373 | 0.010309 | 0.071848 | 0.0034158 | 0.060011 | -0.00034604 | -0.00273 | -0.00068649 | -0.0025762 | 0.062961 | 0.064659 | -0.0049261 | -0.0055285 | 120.9229 | 0.004578 | 4.5273 | 0.045776 | 121.3943 | -0.086975 | -0.20142 | 0.022888 | 0.33875 | -0.10071 | 121.2799 | 121.2982 | -0.091553 | -0.14648 | 0.07782 | -0.036621 | 0.091553 | 0.16937 | 0.21057 | 0.24719 | -0.37994 | 0.073242 | 0.018311 | -0.022888 | 0.18768 | 0.064087 | 0.045776 | -0.004577 | 121.5591 | 121.0876 | 4.6921 | -121.5042 | 121.4447 | 121.463 | 0.50354 | -121.4493
1331.8906 | 121.4493 | -0.14191 | 121.2845 | 0.014267 | 0.0090278 | 0.073771 | 0.0087564 | 0.061934 | -0.0041912 | -0.0055072 | -0.00068649 | -0.002149 | 0.064029 | 0.061455 | -0.010694 | -0.0068103 | 120.9229 | 0.064087 | 4.6051 | 0.07782 | 121.3806 | -0.082397 | -0.19684 | -0.032043 | 0.38452 | -0.11902 | 121.2891 | 121.3257 | -0.12817 | -0.14648 | 0.05951 | -0.054931 | 0.09613 | 0.20599 | 0.21973 | 0.27466 | -0.36163 | 0.013733 | -0.004577 | 0.004577 | 0.10986 | 0.022888 | 0.027465 | 0.041199 | 121.5225 | 121.0648 | 4.747 | -121.4813 | 121.431 | 121.4676 | 0.52643 | -121.431
1333.625 | 121.3669 | -0.19684 | 121.3257 | 0.014267 | 0.0066778 | 0.06608 | 0.0087564 | 0.060865 | 0.0039264 | -0.0025164 | -0.00068649 | 0.00084176 | 0.063388 | 0.064659 | -0.0077033 | -0.0074511 | 120.8725 | -0.10529 | 4.454 | -0.009155 | 121.4264 | -0.1236 | -0.2243 | -0.086975 | 0.21515 | -0.2243 | 121.312 | 121.3989 | -0.13733 | -0.1831 | 0.073242 | -0.027466 | 0.10071 | 0.091552 | 0.18768 | 0.21515 | -0.45319 | 0.059509 | 0.013733 | -0.013733 | 0.10986 | -0.027466 | -0.041199 | 0.073242 | 121.6232 | 121.0693 | 4.6509 | -121.55 | 121.5088 | 121.5958 | 0.41199 | -121.5088
1335.3594 | 121.4859 | -0.14191 | 121.2616 | 0.0066373 | 0.0066778 | 0.069925 | 0.0057656 | 0.06172 | 0.0020038 | -0.0035846 | -0.00068649 | 0.00062796 | 0.063388 | 0.065941 | -0.0074897 | -0.0074511 | 120.9091 | -0.032043 | 4.5456 | 0.032043 | 121.3898 | -0.10986 | -0.24719 | -0.041199 | 0.32959 | -0.17853 | 121.2982 | 121.3623 | -0.14191 | -0.16479 | 0.032044 | -0.10528 | 0.12817 | 0.10986 | 0.17395 | 0.27924 | -0.35248 | 0 | -0.022888 | 0.036621 | 0.10071 | -0.036621 | -0.013733 | 0.10071 | 121.5317 | 121.051 | 4.6875 | -121.5088 | 121.4401 | 121.5042 | 0.4715 | -121.4264
1337.0469 | 121.3806 | -0.19684 | 121.3211 | -0.00099167 | 0.010737 | 0.072702 | 0.0070474 | 0.060011 | -0.0063274 | -0.00508 | 0.0069425 | -0.0034308 | 0.063816 | 0.065087 | -0.011762 | -0.0074511 | 120.8908 | -0.004578 | 4.5181 | 0.050354 | 121.3943 | -0.09613 | -0.21515 | -0.050354 | 0.32044 | -0.13275 | 121.2708 | 121.3486 | -0.10529 | -0.16022 | 0.10071 | -0.018311 | 0.073242 | 0.19226 | 0.24719 | 0.2655 | -0.4303 | 0.091552 | 0.036621 | -0.050354 | 0.14648 | 0.064087 | 0.027466 | 0.027466 | 121.5912 | 121.0876 | 4.715 | -121.5363 | 121.4676 | 121.5454 | 0.51727 | -121.4813
1338.7969 | 121.4539 | -0.16479 | 121.2662 | -0.00099167 | 0.011378 | 0.072062 | 0.0070474 | 0.061079 | -0.00034604 | -0.0063616 | 0.0069425 | -0.0030034 | 0.064243 | 0.063164 | -0.01048 | -0.0076647 | 120.9503 | 0.064087 | 4.5959 | 0.07782 | 121.3669 | -0.091553 | -0.20142 | -0.032043 | 0.40741 | -0.10529 | 121.2936 | 121.344 | -0.12817 | -0.16937 | 0.073242 | -0.036621 | 0.10071 | 0.22888 | 0.24261 | 0.27924 | -0.31586 | 0.036621 | -0.004578 | 0.027466 | 0.13275 | 0.059509 | 0.064087 | 0.07782 | 121.5317 | 121.1151 | 4.7607 | -121.4676 | 121.4584 | 121.5088 | 0.5722 | -121.4355
1340.5469 | 121.4035 | -0.18768 | 121.2936 | 0.0066373 | 0.013514 | 0.07313 | 0.00042505 | 0.062147 | -0.00077324 | -0.0025164 | 0.014572 | -0.0010808 | 0.061039 | 0.062523 | -0.0064215 | -0.0080921 | 120.9641 | 0.059509 | 4.5776 | 0.082397 | 121.3898 | -0.091553 | -0.19684 | 0.018311 | 0.36621 | -0.086975 | 121.257 | 121.2982 | -0.11444 | -0.15564 | 0.09613 | -0.009155 | 0.096131 | 0.24719 | 0.27008 | 0.27924 | -0.32959 | 0.073242 | 0.032043 | -0.036621 | 0.20599 | 0.10071 | 0.068665 | 0.004578 | 121.5775 | 121.1517 | 4.7653 | -121.4905 | 121.4447 | 121.4859 | 0.55389 | -121.4493
1342.2188 | 121.4905 | -0.16022 | 121.3074 | -0.00099167 | 0.0064642 | 0.071207 | 0.0085428 | 0.062361 | -0.0014142 | -0.0055072 | 0.0069425 | 0.0010554 | 0.065097 | 0.063591 | -0.0091985 | -0.0053149 | 120.8679 | -0.082397 | 4.4998 | -0.018311 | 121.4218 | -0.13733 | -0.24261 | -0.10986 | 0.30212 | -0.2243 | 121.3394 | 121.3531 | -0.17395 | -0.19684 | 0.022888 | -0.082398 | 0.11444 | 0.07782 | 0.14191 | 0.2243 | -0.43945 | -0.013733 | -0.036621 | 0.032044 | 0.050354 | -0.064087 | -0.027466 | 0.045776 | 121.582 | 121.0281 | 4.66 | -121.55 | 121.4996 | 121.5134 | 0.46234 | -121.5042
1343.9688 | 121.4127 | -0.20599 | 121.312 | 0.0066373 | 0.010096 | 0.06843 | 0.0049112 | 0.062147 | 0.002431 | -0.00273 | -0.00068649 | 0.0025508 | 0.062748 | 0.064019 | -0.0062079 | -0.0068103 | 120.8679 | -0.091553 | 4.4678 | -0.018311 | 121.4447 | -0.13275 | -0.23804 | -0.091553 | 0.24261 | -0.2243 | 121.3348 | 121.3715 | -0.14648 | -0.19226 | 0.073243 | -0.032043 | 0.13275 | 0.11444 | 0.18768 | 0.21973 | -0.44403 | 0.05951 | 0.013733 | 0.022888 | 0.11444 | -0.01831 | -0.032043 | 0.059509 | 121.6507 | 121.0739 | 4.6738 | -121.55 | 121.5408 | 121.5775 | 0.44861 | -121.5042
1345.6562 | 121.3669 | -0.20599 | 121.2982 | -0.00099167 | 0.012873 | 0.073557 | 0.0046976 | 0.063643 | -0.0026958 | -0.0035846 | 0.0069425 | -0.003858 | 0.061252 | 0.06295 | -0.0081305 | -0.0059557 | 120.9457 | 0.041199 | 4.5822 | 0.045776 | 121.376 | -0.086975 | -0.19684 | -0.022888 | 0.35248 | -0.10986 | 121.2524 | 121.2982 | -0.10986 | -0.16479 | 0.11902 | 0.009156 | 0.07782 | 0.24719 | 0.25177 | 0.24261 | -0.35248 | 0.096131 | 0.041199 | -0.045777 | 0.18311 | 0.096131 | 0.054932 | 0 | 121.582 | 121.1517 | 4.7882 | -121.4951 | 121.4584 | 121.5042 | 0.55847 | -121.463
1347.3906 | 121.431 | -0.19684 | 121.3211 | 0.014267 | 0.01095 | 0.069284 | 0.0042702 | 0.06407 | 0.003072 | -0.003371 | 0.0069425 | 0.0014826 | 0.063175 | 0.063591 | -0.0074897 | -0.0059557 | 120.8817 | -0.086975 | 4.4724 | -0.013733 | 121.4539 | -0.13275 | -0.24261 | -0.086975 | 0.26093 | -0.2243 | 121.3257 | 121.3394 | -0.11902 | -0.16022 | 0.064087 | -0.045777 | 0.13275 | 0.10986 | 0.18311 | 0.22888 | -0.43945 | 0.077819 | 0.036621 | 0.004578 | 0.10986 | -0.027466 | -0.064087 | 0.018311 | 121.6507 | 121.0785 | 4.6692 | -121.5637 | 121.5225 | 121.5363 | 0.45776 | -121.4813
1349.1406 | 121.4401 | -0.17853 | 121.2936 | 0.014267 | 0.012873 | 0.072275 | 0.0076882 | 0.05937 | -0.0041912 | -0.0046526 | -0.00068649 | -0.0047124 | 0.061466 | 0.061882 | -0.0094123 | -0.0068103 | 120.9091 | 0 | 4.5319 | 0.054932 | 121.3989 | -0.086975 | -0.19226 | -0.045776 | 0.33417 | -0.12817 | 121.2982 | 121.3623 | -0.09613 | -0.14648 | 0.091553 | -0.013733 | 0.10529 | 0.17853 | 0.23346 | 0.24719 | -0.38452 | 0.082398 | 0.032044 | 0.004578 | 0.13275 | 0.050354 | 0.01831 | 0.068665 | 121.5775 | 121.0876 | 4.7104 | -121.4859 | 121.4767 | 121.5408 | 0.5127 | -121.4401
1350.8906 | 121.4859 | -0.15564 | 121.3165 | -0.00099167 | 0.010309 | 0.069925 | 0.005552 | 0.060865 | -0.0039776 | -0.0048662 | -0.00068649 | -0.0010808 | 0.062748 | 0.064019 | -0.012617 | -0.0089465 | 120.9778 | 0.07782 | 4.6188 | 0.086975 | 121.4081 | -0.091553 | -0.18768 | 0.004578 | 0.45776 | -0.068665 | 121.2891 | 121.3715 | -0.10529 | -0.13733 | 0.064087 | -0.032043 | 0.091553 | 0.23346 | 0.24261 | 0.27466 | -0.33875 | 0.050354 | 0.018311 | -0.027466 | 0.16022 | 0.086975 | 0.068664 | 0.054932 | 121.5637 | 121.1334 | 4.7745 | -121.5042 | 121.4447 | 121.5271 | 0.6134 | -121.4539
1352.6406 | 121.4401 | -0.16937 | 121.3211 | 0.0066373 | 0.0066778 | 0.068644 | 0.0032022 | 0.061079 | 0.0043536 | -0.0037982 | -0.00068649 | 0.0038324 | 0.065097 | 0.065514 | -0.0074897 | -0.0085193 | 120.9915 | 0 | 4.5731 | 0.050354 | 121.4355 | -0.12817 | -0.22888 | -0.027466 | 0.34332 | -0.17395 | 121.3348 | 121.3989 | -0.12817 | -0.17395 | 0.041199 | -0.059509 | 0.11444 | 0.16937 | 0.21973 | 0.27924 | -0.32959 | 0.041199 | -0.004577 | 0.013733 | 0.14191 | -0.004577 | 0 | 0.07782 | 121.6049 | 121.1609 | 4.7424 | -121.55 | 121.5042 | 121.5683 | 0.5127 | -121.4951
1354.3125 | 121.3943 | -0.17853 | 121.3211 | -0.00099167 | 0.013727 | 0.074411 | 0.0029886 | 0.061293 | -0.0031232 | -0.003371 | -0.008316 | -0.0017218 | 0.06232 | 0.064659 | -0.0089849 | -0.0070239 | 120.9503 | 0.018311 | 4.5502 | 0.036621 | 121.3989 | -0.073242 | -0.19226 | -0.032043 | 0.35706 | -0.11902 | 121.2753 | 121.3806 | -0.10986 | -0.15564 | 0.10529 | -0.013733 | 0.07782 | 0.19684 | 0.21515 | 0.22888 | -0.37079 | 0.068665 | 0.022888 | -0.045776 | 0.14648 | 0.059509 | 0.036621 | 0.059509 | 121.5775 | 121.1288 | 4.7287 | -121.5134 | 121.4539 | 121.5591 | 0.53558 | -121.4767
1356.0469 | 121.4355 | -0.25177 | 121.2296 | -0.016251 | 0.012659 | 0.071207 | 0.0025612 | 0.059797 | -0.00077324 | -0.00508 | 0.014572 | 0.00062796 | 0.061893 | 0.062523 | -0.0085577 | -0.0059557 | 120.9137 | -0.032043 | 4.5731 | -0.004578 | 121.3165 | -0.15564 | -0.25177 | -0.041199 | 0.38452 | -0.15106 | 121.2204 | 121.2524 | -0.16937 | -0.21057 | 0.09613 | 0 | 0.086975 | 0.21973 | 0.24719 | 0.24719 | -0.31586 | 0.082397 | 0.041199 | -0.009155 | 0.21057 | 0.10071 | 0.059509 | 0.022888 | 121.5683 | 121.1655 | 4.8248 | -121.4813 | 121.4722 | 121.5042 | 0.63629 | -121.4401
1357.7969 | 121.5271 | -0.16479 | 121.2753 | -0.00099167 | 0.0081732 | 0.072062 | 0.0046976 | 0.060652 | 0.003072 | -0.0020892 | 0.0069425 | 0.002337 | 0.063388 | 0.063591 | -0.0070623 | -0.0078783 | 120.932 | -0.059509 | 4.5547 | 0.032043 | 121.4127 | -0.13275 | -0.27466 | -0.064087 | 0.36621 | -0.20599 | 121.3165 | 121.3577 | -0.15106 | -0.21057 | 0.032044 | -0.10986 | 0.13733 | 0.10529 | 0.19684 | 0.3067 | -0.34332 | 0.013733 | -0.045776 | 0.041198 | 0.10071 | -0.041199 | 0.004577 | 0.082397 | 121.5775 | 121.0968 | 4.7195 | -121.55 | 121.4813 | 121.5225 | 0.53101 | -121.4859
1359.4844 | 121.3623 | -0.37079 | 121.1014 | -0.00099167 | 0.0086006 | 0.069925 | 0.002775 | 0.062788 | 0.002431 | -0.0029436 | 0.0069425 | 0.00062796 | 0.064243 | 0.0653 | -0.0064215 | -0.0053149 | 120.6619 | -0.29297 | 4.5364 | -0.1831 | 121.2158 | -0.3067 | -0.42114 | -0.3067 | 0.32044 | -0.3891 | 121.106 | 121.1197 | -0.32959 | -0.37079 | 0.064087 | -0.050354 | 0.11444 | 0.07782 | 0.18768 | 0.23804 | -0.43945 | 0.041199 | 0 | 0.004578 | 0.064087 | -0.01831 | -0.01831 | 0.018311 | 121.5866 | 121.0327 | 4.9072 | -121.5225 | 121.4767 | 121.4905 | 0.69122 | -121.4722
1361.2188 | 118.2678 | -92.2668 | 25.8408 | -0.00099167 | 0.002619 | 0.068003 | 0.0091836 | 0.063215 | 0.001363 | -0.0014484 | 0.014572 | 0.0019098 | 0.063602 | 0.065087 | -0.0087713 | -0.0080921 | 26.3168 | -90.9714 | -3.1219 | -91.5024 | 26.564 | -91.777 | -91.6031 | -91.9556 | -0.3479 | -91.7404 | 26.5549 | 26.5457 | -91.6077 | -91.8228 | 0.48981 | 0.66376 | 0.72327 | 1.2955 | 0.76447 | 0.10071 | 0.47607 | 0.65918 | 0.44403 | 0.71411 | 0.31128 | 0.52643 | 0.082398 | 0.70496 | 118.8309 | 118.5837 | 89.1449 | -117.4438 | 118.8217 | 118.8126 | 91.9189 | -117.6636
1362.9375 | 119.751 | -118.9819 | 0.81482 | 0.014267 | 0.0068916 | 0.068857 | 0.0057656 | 0.063856 | 0.0022174 | -0.0029436 | 0.014572 | 0.00041436 | 0.063175 | 0.066796 | -0.0094123 | -0.0068103 | 0.40741 | -118.3685 | -6.2942 | -118.8629 | 0.82855 | -119.1834 | -119.0002 | -119.4443 | -0.56305 | -119.1284 | 0.72327 | 0.71411 | -118.9957 | -119.2108 | -0.20142 | -0.01831 | 0.013733 | 0.6134 | 0.11902 | 0.13733 | -0.40741 | -0.013733 | -0.22888 | -0.091552 | -0.46234 | -0.14648 | 0.082397 | -0.10071 | 119.8105 | 119.3893 | 112.6877 | -119.8151 | 119.7052 | 119.696 | 118.4189 | -120.0256
1364.7031 | 120.1859 | -33.4808 | 86.7142 | 0.014267 | 0.0071052 | 0.071207 | 0.0040566 | 0.061293 | 0.00050836 | -0.0029436 | 0.0069425 | 0.0025508 | 0.059757 | 0.06295 | -0.0079169 | -0.0057421 | 86.3388 | -33.5587 | 1.7899 | -33.5587 | 86.8195 | -33.3572 | -33.3984 | -33.7234 | 0.71411 | -33.7738 | 86.7599 | 86.8378 | -33.3023 | -33.4488 | 0.1236 | 0.082398 | 0.10529 | -0.07782 | -0.07782 | -0.16022 | -0.37537 | 0.17853 | 0.032043 | 0.045777 | -0.24262 | -0.29297 | -0.32501 | 0.1236 | 120.3003 | 119.8196 | 35.2707 | -120.1126 | 120.2408 | 120.3186 | 34.1949 | -120.163
1366.3906 | 120.4788 | -20.7047 | 99.765 | -0.0086212 | 0.0051826 | 0.072275 | 0.0066202 | 0.061506 | -0.00013244 | -0.0012346 | 0.0069425 | 0.0019098 | 0.064457 | 0.061882 | -0.0087713 | -0.0076647 | 99.6048 | -20.5124 | 2.7924 | -20.5627 | 100.0259 | -20.4758 | -20.5673 | -20.8557 | 0.55389 | -21.0114 | 99.7833 | 99.8154 | -20.6268 | -20.7275 | 0.22888 | 0.13733 | 0.26093 | 0.19226 | 0.14191 | 0.004578 | -0.16022 | 0.07782 | -0.022888 | 0.01831 | -0.15106 | -0.3067 | -0.28381 | 0.050354 | 120.7306 | 120.3094 | 23.497 | -120.3323 | 120.488 | 120.52 | 21.2585 | -120.4926
1368.1406 | 120.4559 | -24.6002 | 95.8237 | 0.0066373 | 0.0092414 | 0.071421 | 0.007261 | 0.060865 | -0.0080364 | -0.0025164 | -0.00068649 | -0.0040716 | 0.062107 | 0.06231 | -0.013258 | -0.0053149 | 95.9335 | -24.3713 | 2.536 | -24.2523 | 96.3043 | -24.1562 | -24.1608 | -24.2294 | 0.98877 | -24.4583 | 96.405 | 96.3821 | -24.0921 | -24.2981 | 0.44403 | 0.43945 | 0.48065 | 0.22888 | 0.3479 | -0.091552 | 0.10986 | 0.50812 | 0.30212 | 0.58136 | 0.37079 | 0.14191 | -0.16022 | 0.55847 | 120.9045 | 120.5338 | 27.1362 | -119.9844 | 121.0052 | 120.9824 | 25.589 | -120.1218
1369.875 | 120.6207 | -8.0429 | 112.3581 | 0.014267 | 0.014155 | 0.074198 | 0.0032022 | 0.062361 | -0.0044048 | -0.006148 | -0.00068649 | -0.002149 | 0.060184 | 0.061455 | -0.0094123 | -0.0074511 | 112.0697 | -7.9971 | 3.5248 | -8.3771 | 112.326 | -8.1711 | -8.2626 | -7.8827 | 0.29755 | -8.1116 | 112.4496 | 112.4771 | -8.0475 | -8.0795 | -0.12817 | -0.21973 | -0.032043 | 0.045777 | -0.33417 | -0.11444 | -0.28839 | -0.004577 | -0.036621 | 0.091553 | 0.16022 | -0.068664 | -0.032043 | 0.11902 | 120.369 | 120.1126 | 11.5677 | -120.6207 | 120.4926 | 120.52 | 8.3405 | -120.4376
1371.5625 | 120.6162 | -11.8195 | 108.7326 | 0.0066373 | 0.0079596 | 0.070139 | 0.0044838 | 0.062574 | 0.004781 | -0.0037982 | -0.00068649 | 0.00020076 | 0.061679 | 0.065514 | -0.0081305 | -0.0076647 | 108.078 | -12.0026 | 3.8956 | -11.6272 | 108.6639 | -12.1307 | -12.0483 | -11.6135 | 0.71869 | -12.1994 | 108.8196 | 108.8287 | -11.7004 | -11.7783 | -0.31128 | -0.22888 | -0.068665 | -0.18311 | 0.19226 | 0.42114 | -0.6546 | 0.11902 | 0.041199 | 0.086975 | 0.20599 | -0.37994 | -0.42114 | 0.09613 | 120.4834 | 119.8975 | 15.715 | -120.7809 | 120.639 | 120.6482 | 12.5381 | -120.5109
1373.3125 | 119.7327 | -40.5579 | 79.2984 | 0.0066373 | 0.0083868 | 0.072275 | 0.0074746 | 0.060011 | -0.0056866 | -0.003371 | -0.00068649 | -0.0049262 | 0.058048 | 0.062737 | -0.010267 | -0.0080921 | 77.7145 | -41.6565 | 5.4108 | -41.6565 | 77.8336 | -41.6611 | -41.629 | -41.8076 | 6.0562 | -41.6519 | 77.9114 | 77.9526 | -41.4505 | -41.5695 | -1.1032 | -1.0712 | -1.4648 | -1.0986 | -1.0986 | -0.027466 | -1.5839 | -0.89264 | -1.0117 | -1.387 | -1.2497 | -1.0941 | -0.082398 | -1.3458 | 118.3914 | 118.2724 | 45.9686 | -120.9274 | 118.4692 | 118.5104 | 46.6141 | -120.8679
1375.0625 | 120.4376 | -117.5903 | 2.5269 | 0.0066373 | 0.0039008 | 0.071634 | 0.0023476 | 0.064497 | 0.0039264 | -0.0018756 | 0.0069425 | 0.00020076 | 0.060184 | 0.064873 | -0.0044989 | -0.0051013 | 2.2888 | -117.0639 | -6.3538 | -117.5583 | 2.6367 | -117.9245 | -117.7277 | -118.1717 | -0.33875 | -117.865 | 2.4902 | 2.5131 | -117.7505 | -117.952 | -0.33417 | -0.13733 | 0.10986 | 0.52643 | 0.032043 | 0.16937 | -0.23804 | -0.16022 | -0.36163 | -0.036621 | -0.58136 | -0.27466 | 0.086975 | -0.013732 | 120.2271 | 119.8792 | 111.2366 | -120.2545 | 120.0806 | 120.1035 | 117.2516 | -120.4788
1376.75 | 120.607 | -117.7231 | 2.4994 | -0.00099167 | 0.012446 | 0.071634 | 0.0064066 | 0.06172 | -0.006541 | -0.0048662 | 0.0069425 | -0.0042852 | 0.059757 | 0.062737 | -0.012617 | -0.0063831 | 2.3026 | -117.0959 | -6.4774 | -117.6865 | 2.6138 | -117.9565 | -117.8238 | -118.2495 | -0.21973 | -117.8879 | 2.4902 | 2.504 | -117.8101 | -118.0801 | -0.23346 | -0.10071 | 0.11444 | 0.62714 | 0.036621 | 0.13733 | -0.19684 | -0.086976 | -0.35706 | -0.009156 | -0.52643 | -0.16479 | 0.19226 | 0.004577 | 120.3369 | 120.0256 | 111.2457 | -120.3232 | 120.2133 | 120.2271 | 117.5034 | -120.5795
1378.5 | 120.607 | -118.959 | 1.4923 | 0.0066373 | 0.0041144 | 0.07078 | 0.0044838 | 0.064924 | 0.003072 | -0.001021 | 0.0069425 | 0.0034052 | 0.062107 | 0.0653 | -0.0055671 | -0.0074511 | 1.1902 | -118.3044 | -6.8481 | -118.8721 | 1.561 | -119.1193 | -118.9819 | -119.4534 | -0.39368 | -119.1513 | 1.4008 | 1.4191 | -118.959 | -119.2291 | -0.16022 | -0.022889 | 0.068664 | 0.6546 | 0.086975 | 0.10986 | -0.30212 | 0 | -0.27008 | -0.091553 | -0.49438 | -0.19226 | 0.07782 | -0.073243 | 120.52 | 120.1492 | 112.1109 | -120.4742 | 120.3598 | 120.3781 | 118.5654 | -120.7214
1380.1875 | 120.575 | -118.9636 | 1.506 | 0.0066373 | 0.0086006 | 0.069498 | 0.0057656 | 0.063643 | -0.00034604 | -0.00038024 | -0.00068649 | -0.00022644 | 0.06232 | 0.064446 | -0.0068487 | -0.0061695 | 1.2039 | -118.3594 | -6.926 | -118.8858 | 1.6067 | -119.0826 | -118.9819 | -119.4626 | -0.35706 | -119.1238 | 1.5106 | 1.506 | -118.9499 | -119.1971 | -0.11902 | -0.018311 | 0.10071 | 0.60425 | 0.07782 | 0.096131 | -0.30212 | 0.013733 | -0.23346 | 0.004578 | -0.49896 | -0.16022 | 0.073243 | 0 | 120.5704 | 120.1675 | 112.0377 | -120.488 | 120.4742 | 120.4697 | 118.6066 | -120.7031
1381.9219 | 120.6162 | -119.4077 | 1.1856 | 0.0066373 | 0.0083868 | 0.07078 | 0.0040566 | 0.062147 | 0.0022174 | -0.0012346 | -0.00068649 | -0.00065364 | 0.061466 | 0.065514 | -0.0068487 | -0.0059557 | 0.8194 | -118.7622 | -7.0312 | -119.2886 | 1.2268 | -119.4809 | -119.3527 | -119.8791 | -0.35706 | -119.5633 | 1.1261 | 1.1536 | -119.3207 | -119.5999 | -0.073242 | 0.054932 | 0.041199 | 0.64545 | 0.11902 | 0.064087 | -0.36621 | 0.086975 | -0.19226 | -0.059509 | -0.4715 | -0.15564 | 0.036622 | -0.032044 | 120.6345 | 120.2271 | 112.3764 | -120.5383 | 120.5338 | 120.5612 | 119.0506 | -120.7855
1383.6562 | 120.575 | -119.3756 | 1.2222 | 0.0066373 | 0.0024054 | 0.070139 | 0.0068338 | 0.063643 | 0.0022174 | -0.0012346 | -0.00068649 | 0.0016962 | 0.064243 | 0.065087 | -0.0057807 | -0.0076647 | 0.86975 | -118.7073 | -7.0633 | -119.2566 | 1.2726 | -119.4489 | -119.3161 | -119.8471 | -0.33875 | -119.5587 | 1.1856 | 1.1902 | -119.3069 | -119.5679 | -0.073243 | 0.059509 | 0.050354 | 0.66833 | 0.11902 | 0.059509 | -0.35248 | 0.068664 | -0.19226 | -0.036621 | -0.4715 | -0.18311 | 0.009155 | -0.032043 | 120.6482 | 120.2454 | 112.3123 | -120.5383 | 120.5612 | 120.5658 | 119.0369 | -120.7901
1385.3281 | 120.5841 | -118.6203 | 1.9821 | -0.00099167 | 0.0073188 | 0.070566 | 0.0042702 | 0.063856 | 0.0022174 | -0.0020892 | -0.008316 | -0.00044004 | 0.061893 | 0.066582 | -0.0083441 | -0.0046741 | 1.5564 | -118.0069 | -7.1777 | -118.5013 | 1.9363 | -118.7027 | -118.6203 | -119.0872 | -0.48065 | -118.7439 | 1.9135 | 1.918 | -118.5104 | -118.7531 | -0.082398 | 0 | -0.045777 | 0.6134 | 0.11902 | 0.11902 | -0.42572 | 0.10986 | -0.13275 | -0.068665 | -0.46692 | -0.1236 | 0.009156 | -0.064087 | 120.5566 | 120.1767 | 111.4426 | -120.6024 | 120.5338 | 120.5383 | 118.1396 | -120.7352
1387.0781 | 120.4285 | -115.2145 | 4.9255 | -0.00099167 | 0.004328 | 0.071848 | 0.0087564 | 0.063429 | -0.0026958 | -0.003371 | 0.014572 | -0.0017218 | 0.062107 | 0.063378 | -0.010267 | -0.0046741 | 4.66 | -114.6469 | -6.6376 | -115.1459 | 5.0629 | -115.3107 | -115.1825 | -115.7959 | -0.3067 | -115.4434 | 4.9438 | 4.9622 | -115.2466 | -115.4755 | -0.09613 | 0.032044 | 0.13733 | 0.56763 | 0.068665 | 0.036621 | -0.2655 | -0.032043 | -0.26093 | 0.018311 | -0.58136 | -0.22888 | 0.032044 | 0.036621 | 120.2774 | 119.8746 | 108.577 | -120.108 | 120.1584 | 120.1767 | 114.9078 | -120.401
1388.7656 | 120.5795 | -117.0456 | 3.3142 | 0.014267 | 0.0096686 | 0.071421 | 0.0061928 | 0.063643 | -0.0059002 | -0.0018756 | -0.00068649 | -0.0040716 | 0.061679 | 0.063378 | -0.010694 | -0.0065967 | 3.1219 | -116.3361 | -6.7612 | -116.9357 | 3.3829 | -117.1463 | -117.0319 | -117.485 | -0.13275 | -117.1326 | 3.2547 | 3.2959 | -117.0135 | -117.2836 | -0.10071 | 0.013733 | 0.068665 | 0.70953 | 0.10986 | 0.09613 | -0.19226 | 0.032043 | -0.23804 | -0.059509 | -0.43945 | -0.086975 | 0.15106 | -0.018311 | 120.4285 | 120.1675 | 110.2844 | -120.3461 | 120.3003 | 120.3415 | 116.9128 | -120.5978
1390.5156 | 120.6848 | -116.7801 | 3.6484 | -0.00099167 | 0.0030464 | 0.071421 | 0.0064066 | 0.062788 | 0.00093576 | -0.0025164 | -0.00068649 | 0.00062796 | 0.064029 | 0.065728 | -0.0083441 | -0.0063831 | 3.2913 | -116.2445 | -6.8436 | -116.7572 | 3.6758 | -116.9678 | -116.8671 | -117.3386 | -0.20142 | -117.0227 | 3.5934 | 3.598 | -116.8213 | -117.0776 | -0.18768 | -0.086975 | 0.027466 | 0.53558 | 0.022888 | 0.10986 | -0.35705 | -0.041199 | -0.29755 | -0.054931 | -0.55847 | -0.24262 | 0.054932 | -0.050354 | 120.4559 | 120.0714 | 109.9365 | -120.5154 | 120.3735 | 120.3781 | 116.5787 | -120.726
1392.2031 | 120.5978 | -117.6773 | 2.8473 | 0.014267 | 0.0090278 | 0.072489 | 0.003843 | 0.062788 | 0.001363 | -0.0023028 | 0.014572 | -0.0010808 | 0.061679 | 0.064446 | -0.0064215 | -0.0068103 | 2.6779 | -116.835 | -6.9672 | -117.3477 | 3.0167 | -117.6041 | -117.5034 | -118.2495 | -0.6134 | -118.0115 | 2.6825 | 2.6688 | -117.8192 | -118.0389 | 0.073242 | 0.17395 | 0.16937 | 0.84229 | 0.32959 | 0.15564 | -0.16937 | -0.14191 | -0.36163 | -0.1648 | -0.5722 | -0.33417 | 0.027465 | -0.17853 | 120.694 | 120.3552 | 110.7101 | -120.3506 | 120.3598 | 120.3461 | 117.0639 | -120.8862
1393.9531 | 120.6985 | -118.0847 | 2.4307 | 0.0066373 | 0.012446 | 0.073343 | 0.007261 | 0.062361 | -0.006541 | -0.006148 | 0.0069425 | -0.0047124 | 0.062534 | 0.061455 | -0.010908 | -0.0059557 | 2.1927 | -117.3477 | -6.9763 | -117.952 | 2.4719 | -118.1625 | -118.0344 | -118.5196 | -0.13733 | -118.1305 | 2.3621 | 2.3529 | -118.0527 | -118.2816 | -0.07782 | 0.050354 | 0.041199 | 0.737 | 0.13275 | 0.082398 | -0.23804 | 0.032044 | -0.19684 | -0.068664 | -0.43488 | -0.045776 | 0.15106 | -0.07782 | 120.5566 | 120.2774 | 111.1084 | -120.4651 | 120.4468 | 120.4376 | 117.9474 | -120.7123
1395.7031 | 120.694 | -117.8604 | 2.6917 | 0.0066373 | 0.0056098 | 0.072275 | 0.00897 | 0.061934 | 8.1158e-05 | -0.0037982 | -0.00068649 | 0.0014826 | 0.061039 | 0.063164 | -0.0089849 | -0.0076647 | 2.3895 | -117.215 | -7.0724 | -117.7597 | 2.7969 | -117.9474 | -117.8146 | -118.3456 | -0.25177 | -118.0252 | 2.7145 | 2.7054 | -117.8101 | -118.0435 | -0.086975 | 0.045777 | 0.10529 | 0.64545 | 0.10071 | 0.054931 | -0.30212 | 0.050354 | -0.18311 | 0.022889 | -0.48523 | -0.1648 | 0.01831 | 0.013733 | 120.6573 | 120.2499 | 110.788 | -120.5063 | 120.575 | 120.5658 | 117.6086 | -120.7352
1397.4375 | 120.726 | -117.4118 | 3.1448 | -0.00099167 | 0.006037 | 0.069925 | 0.0076882 | 0.062574 | 0.0011494 | -0.0040118 | 0.014572 | -0.0010808 | 0.062534 | 0.065087 | -0.010267 | -0.0095873 | 2.8427 | -116.8121 | -7.0312 | -117.2928 | 3.2364 | -117.5262 | -117.366 | -117.897 | -0.26093 | -117.5858 | 3.1631 | 3.1815 | -117.3981 | -117.6315 | -0.11444 | 0.045776 | 0.091553 | 0.59967 | 0.11902 | 0.073242 | -0.30212 | 0.013733 | -0.21973 | 0.018311 | -0.48523 | -0.17395 | 0.045777 | 0.036622 | 120.6482 | 120.2545 | 110.3806 | -120.5109 | 120.575 | 120.5933 | 117.1509 | -120.7764
1399.1719 | 120.5475 | -112.0377 | 8.5052 | 0.014267 | 0.011164 | 0.069284 | 0.0034158 | 0.060652 | 0.00093576 | -0.0025164 | 0.0069425 | 0.00062796 | 0.061893 | 0.064232 | -0.0089849 | -0.0070239 | 8.313 | -111.3144 | -6.3034 | -111.8729 | 8.5922 | -112.0239 | -111.9049 | -112.4542 | -0.26093 | -112.175 | 8.4 | 8.432 | -111.9598 | -112.2208 | 0.013733 | 0.13275 | 0.086975 | 0.72327 | 0.16479 | 0.032043 | -0.19226 | 0.07782 | -0.1831 | -0.10529 | -0.41656 | -0.13733 | 0.045776 | -0.073242 | 120.6299 | 120.3506 | 105.7343 | -120.4102 | 120.4376 | 120.4697 | 111.7767 | -120.726
1400.8594 | 120.6802 | -113.5025 | 6.9397 | -0.00099167 | 0.012232 | 0.072489 | 0.0051248 | 0.064711 | -0.0041912 | -0.0042254 | 0.014572 | -0.0034308 | 0.06232 | 0.063164 | -0.010908 | -0.0048877 | 6.8344 | -112.6694 | -6.3492 | -113.2233 | 7.1503 | -113.4201 | -113.3194 | -113.7543 | -0.21973 | -113.649 | 6.9763 | 6.9946 | -113.4018 | -113.6948 | 0.082397 | 0.18311 | 0.21057 | 0.83313 | 0.27923 | 0.09613 | -0.10528 | 0.10071 | -0.19226 | 0.036621 | -0.25177 | -0.14648 | 0.045776 | 0.054932 | 120.6528 | 120.3369 | 107.1533 | -120.2591 | 120.4788 | 120.4971 | 113.2828 | -120.6345
1402.5938 | 120.4788 | -115.8691 | 4.6463 | 0.0066373 | 0.012446 | 0.070566 | 0.0025612 | 0.063215 | -0.002055 | -0.0048662 | 0.0069425 | -0.0019354 | 0.060398 | 0.063378 | -0.0074897 | -0.0074511 | 4.2801 | -115.2878 | -6.6925 | -115.8279 | 4.5136 | -116.0294 | -115.9012 | -116.304 | -0.11444 | -116.0385 | 4.4632 | 4.4724 | -115.8829 | -116.0568 | -0.16022 | -0.032043 | -0.13275 | 0.58136 | 0.041199 | 0.073242 | -0.36621 | -0.013733 | -0.18768 | -0.18311 | -0.43488 | -0.16937 | 0.018311 | -0.17395 | 120.3827 | 120.1492 | 109.1766 | -120.5475 | 120.3323 | 120.3415 | 115.7547 | -120.7031
1404.2812 | 120.4788 | -113.0951 | 7.4203 | -0.00099167 | 0.006037 | 0.069284 | 0.0019204 | 0.064924 | 0.0020038 | -0.0018756 | 0.014572 | 0.001269 | 0.059543 | 0.064019 | -0.0053533 | -0.0076647 | 7.0541 | -112.5916 | -6.5552 | -113.0814 | 7.3883 | -113.2553 | -113.118 | -113.6444 | -0.3891 | -113.3972 | 7.2601 | 7.2876 | -113.1226 | -113.3926 | -0.16022 | -0.022888 | -0.032043 | 0.50354 | 0.013733 | 0.036621 | -0.36621 | -0.027466 | -0.29755 | -0.16022 | -0.54932 | -0.30212 | -0.004578 | -0.13275 | 120.4834 | 120.1492 | 106.5399 | -120.5383 | 120.3552 | 120.3827 | 112.706 | -120.813
1406.0312 | 120.0165 | -114.1022 | 5.7037 | -0.00099167 | 0.0083868 | 0.069284 | 0.002775 | 0.060438 | -0.00034604 | -0.0029436 | 0.0069425 | -0.00086724 | 0.061039 | 0.063164 | -0.0074897 | -0.0070239 | 5.4428 | -113.6032 | -6.6742 | -114.0244 | 5.8136 | -114.1937 | -114.0884 | -114.6011 | -0.42114 | -114.2487 | 5.7312 | 5.7632 | -114.0656 | -114.2715 | -0.091553 | 0.013733 | 0.10986 | 0.49896 | 0.07782 | 0.064087 | -0.26093 | 0.036621 | -0.16937 | 0.027466 | -0.49896 | -0.14648 | 0.022888 | 0.05951 | 119.9158 | 119.545 | 107.428 | -119.7922 | 119.8334 | 119.8654 | 113.681 | -119.9753
1407.7188 | 120.1538 | -4.7104 | 115.2328 | 0.0066373 | 0.012446 | 0.070353 | 0.0034158 | 0.059584 | -0.0031232 | -0.0029436 | 0.0069425 | -0.0044988 | 0.062748 | 0.061028 | -0.0087713 | -0.0065967 | 114.8758 | -4.7745 | 4.5181 | -4.7699 | 115.21 | -4.8706 | -4.9622 | -4.8752 | 0.5722 | -4.9988 | 115.123 | 115.1825 | -4.9026 | -4.9438 | -0.16022 | -0.25177 | -0.022888 | -0.064087 | -0.059509 | 0.19226 | -0.35706 | -0.19226 | -0.23346 | -0.10986 | -0.16479 | -0.28839 | -0.054931 | -0.050354 | 119.9203 | 119.5862 | 9.2285 | -120.195 | 119.8334 | 119.8929 | 5.2826 | -120.1767
1409.4688 | 119.751 | -4.5364 | 115.8188 | 0.014267 | 0.00326 | 0.069498 | 0.003843 | 0.060438 | 0.0022174 | -0.0029436 | -0.00068649 | 0.0016962 | 0.062534 | 0.064659 | -0.0057807 | -0.0087329 | 115.4388 | -4.4312 | 4.4861 | -4.3671 | 115.8875 | -4.4815 | -4.5639 | -4.4907 | 0.42572 | -4.66 | 115.7822 | 115.8188 | -4.5136 | -4.541 | 0.054932 | -0.027466 | 0.068664 | 0.10529 | 0.16937 | 0.19684 | -0.37994 | 0.022888 | -0.004578 | -0.036621 | 0.045776 | -0.1236 | -0.11902 | 0 | 120.4239 | 119.9753 | 9.0225 | -120.3827 | 120.3186 | 120.3552 | 4.9622 | -120.3598
1411.2031 | 120.4056 | -4.3259 | 116.011 | 0.0066373 | 0.0030464 | 0.071848 | 0.0049112 | 0.062574 | 0.0017902 | -0.0023028 | 0.014572 | -0.002149 | 0.061466 | 0.063164 | -0.0085577 | -0.0087329 | 115.6769 | -4.2068 | 4.5227 | -4.1794 | 116.1163 | -4.3076 | -4.3854 | -4.2755 | 0.47607 | -4.4266 | 115.9973 | 116.0614 | -4.3167 | -4.3808 | 0.018311 | -0.059509 | 0.10529 | 0.11902 | 0.14648 | 0.20599 | -0.33417 | 0.009156 | -0.054931 | -0.013733 | 0.050354 | -0.10071 | -0.045777 | 0.050354 | 120.4422 | 120.0027 | 8.8486 | -120.3964 | 120.3232 | 120.3873 | 4.8019 | -120.3918
1412.9375 | 120.4147 | -3.8681 | 116.5695 | 0.0066373 | 0.0036872 | 0.069712 | 0.0044838 | 0.063215 | 0.0015766 | -0.001662 | 0.0069425 | -0.0019354 | 0.062748 | 0.061669 | -0.0072759 | -0.0093737 | 116.1987 | -3.7216 | 4.5639 | -3.6987 | 116.6382 | -3.8269 | -3.9185 | -3.7994 | 0.45776 | -3.9551 | 116.5237 | 116.5833 | -3.8406 | -3.8727 | 0.041199 | -0.050354 | 0.068665 | 0.14648 | 0.16937 | 0.21973 | -0.37079 | 0.027466 | -0.004578 | -0.045776 | 0.068665 | -0.086975 | -0.082397 | 0.013733 | 120.5063 | 120.0668 | 8.432 | -120.488 | 120.3918 | 120.4514 | 4.3259 | -120.4422
1414.625 | 119.5724 | -3.7033 | 116.6931 | 0.014267 | 0.014582 | 0.074198 | 0.0040566 | 0.061934 | -0.0059002 | -0.0055072 | 0.0069425 | -0.0042852 | 0.060825 | 0.060814 | -0.010908 | -0.0051013 | 116.2949 | -3.6118 | 4.5914 | -3.598 | 116.7068 | -3.6896 | -3.7857 | -3.6942 | 0.45319 | -3.7949 | 116.629 | 116.7023 | -3.7079 | -3.7949 | 0.013733 | -0.082398 | 0.013733 | 0.091553 | 0.10529 | 0.18768 | -0.39825 | -0.004578 | -0.091553 | -0.064087 | 0.009155 | -0.091553 | 0 | 0.009156 | 120.4102 | 119.9982 | 8.2947 | -120.4788 | 120.3323 | 120.4056 | 4.1565 | -120.488
1416.3594 | 120.488 | -3.3737 | 117.0822 | -0.00099167 | 0.014582 | 0.074411 | 0.0083292 | 0.060865 | -0.0046184 | -0.0055072 | 0.0069425 | -0.0057806 | 0.061252 | 0.063805 | -0.011976 | -0.0065967 | 116.7664 | -3.1906 | 4.6829 | -3.186 | 117.128 | -3.3188 | -3.4378 | -3.2547 | 0.53101 | -3.3371 | 117.0319 | 117.0914 | -3.3371 | -3.392 | 0.054931 | -0.064087 | 0.045777 | 0.18311 | 0.18768 | 0.25177 | -0.31586 | 0.036621 | -0.018311 | -0.050354 | 0.11902 | 0.036621 | 0.054932 | 0.009156 | 120.5017 | 120.1401 | 8.0566 | -120.52 | 120.4056 | 120.4651 | 3.9047 | -120.4742
1418.0938 | 120.5841 | -3.3737 | 117.1051 | -0.00099167 | 0.013941 | 0.071634 | 0.0076882 | 0.061934 | -0.0046184 | -0.0065752 | 0.014572 | -0.0044988 | 0.059116 | 0.061241 | -0.011335 | -0.0085193 | 116.835 | -3.154 | 4.6738 | -3.1631 | 117.1783 | -3.3188 | -3.4058 | -3.241 | 0.54474 | -3.3279 | 117.0959 | 117.1051 | -3.3371 | -3.3875 | 0.054931 | -0.032044 | 0.073242 | 0.21973 | 0.21057 | 0.24262 | -0.27008 | 0.036621 | -0.013733 | -0.009156 | 0.13275 | 0.045776 | 0.059509 | 0 | 120.5521 | 120.2087 | 8.0475 | -120.5109 | 120.4697 | 120.4788 | 3.9185 | -120.4926
1419.8438 | 119.957 | -119.7876 | 0.21057 | -0.0086212 | 0.0071052 | 0.070139 | 0.0025612 | 0.063643 | 0.002431 | -0.0046526 | -0.00068649 | -0.0012946 | 0.060398 | 0.06231 | -0.0051397 | -0.0065967 | -0.10071 | -119.0918 | -7.1823 | -119.6548 | 0.28381 | -119.838 | -119.7235 | -120.195 | -0.48981 | -119.9066 | 0.17395 | 0.18768 | -119.7647 | -119.989 | -0.050354 | 0.064087 | 0.073242 | 0.6958 | 0.13275 | 0.068665 | -0.31128 | 0.022889 | -0.20142 | -0.036621 | -0.40741 | -0.11902 | 0.082398 | -0.022888 | 120.0714 | 119.6869 | 112.6053 | -119.9341 | 119.9615 | 119.9753 | 119.2978 | -120.1996
1421.5781 | 120.108 | -119.8425 | 0.1831 | 0.0066373 | 0.011164 | 0.070993 | 0.0023476 | 0.062574 | -0.00013244 | -0.0035846 | -0.00068649 | -0.0042852 | 0.058689 | 0.064873 | -0.0070623 | -0.0076647 | -0.032043 | -119.1147 | -7.2464 | -119.6732 | 0.20599 | -119.9158 | -119.8105 | -120.2362 | -0.32044 | -119.9158 | 0.10986 | 0.11902 | -119.8242 | -120.0439 | -0.073242 | 0.032043 | 0.022889 | 0.72784 | 0.16937 | 0.13733 | -0.21515 | 0.01831 | -0.20142 | -0.073242 | -0.39368 | -0.073242 | 0.12817 | -0.064086 | 120.0485 | 119.8105 | 112.5961 | -119.9936 | 119.9524 | 119.9615 | 119.5221 | -120.227
1423.2656 | 115.6769 | -83.606 | 31.8695 | -0.00099167 | 0.0073188 | 0.066507 | 0.0051248 | 0.060438 | 0.0028584 | -0.0029436 | 0.0069425 | 0.0010554 | 0.057621 | 0.062096 | -0.0077033 | -0.0087329 | 31.0455 | -83.4503 | -2.9846 | -84.3063 | 31.2607 | -84.201 | -84.3475 | -83.9951 | -0.20142 | -84.8419 | 30.8166 | 30.8395 | -84.6725 | -84.787 | -0.59509 | -0.74158 | -0.60883 | 0.15564 | -0.70038 | 0.041199 | -0.82397 | -1.0666 | -1.181 | -1.0529 | -0.3891 | -1.236 | -0.054932 | -1.03 | 114.8666 | 114.6515 | 80.6213 | -116.217 | 114.4226 | 114.4455 | 83.4045 | -116.6565
1425.0156 | 119.8517 | -119.5999 | 0.16022 | 0.0066373 | 0.012446 | 0.072275 | 0.0083292 | 0.060225 | -0.0048322 | -0.003371 | 0.0069425 | -0.0051398 | 0.061893 | 0.06295 | -0.0094123 | -0.0040331 | -0.1236 | -118.895 | -7.3608 | -119.4626 | 0.19684 | -119.7006 | -119.5404 | -120.0348 | -0.28839 | -119.6732 | 0.09613 | 0.11444 | -119.5587 | -119.8059 | -0.10071 | 0.05951 | 0.036621 | 0.70496 | 0.13733 | 0.07782 | -0.28381 | 0.041199 | -0.20599 | -0.064087 | -0.43488 | -0.073242 | 0.13275 | -0.045776 | 119.7968 | 119.4763 | 112.2391 | -119.7006 | 119.696 | 119.7144 | 119.3115 | -119.9661
1426.6875 | 119.9112 | -119.7784 | 0.19684 | 0.014267 | 0.0013374 | 0.069071 | 0.0053384 | 0.063429 | 0.0054218 | -0.001021 | 0.0069425 | 0.001269 | 0.064029 | 0.065728 | -0.0072759 | -0.0087329 | -0.09613 | -119.0689 | -7.4066 | -119.6136 | 0.23346 | -119.8288 | -119.7464 | -120.2133 | -0.37079 | -119.9341 | 0.13275 | 0.14648 | -119.7189 | -119.9478 | -0.050354 | 0.032043 | 0.036621 | 0.70953 | 0.16479 | 0.13275 | -0.29297 | 0.059509 | -0.16937 | -0.064087 | -0.43488 | -0.15564 | 0.013733 | -0.050354 | 120.0119 | 119.6823 | 112.3718 | -119.9432 | 119.9112 | 119.9249 | 119.4077 | -120.1447
1428.4219 | 120.1218 | -119.8196 | 0.16937 | 0.0066373 | 0.0021918 | 0.068857 | 0.0064066 | 0.063002 | 0.0026446 | -0.001021 | -0.00068649 | -0.00022644 | 0.062534 | 0.064232 | -0.0062079 | -0.0061695 | -0.091553 | -119.1376 | -7.4249 | -119.6869 | 0.23804 | -119.9203 | -119.8059 | -120.2774 | -0.2655 | -119.9661 | 0.1236 | 0.13275 | -119.7739 | -120.0394 | -0.10071 | 0.013733 | 0.068664 | 0.68207 | 0.13275 | 0.11902 | -0.26093 | 0.045776 | -0.21973 | -0.045777 | -0.45776 | -0.14648 | 0.073243 | -0.036622 | 120.0577 | 119.7281 | 112.3947 | -119.9753 | 119.9432 | 119.9524 | 119.5541 | -120.2087
1430.1094 | 120.1904 | -119.8517 | 0.13733 | -0.0086212 | 0.0092414 | 0.073984 | 0.0081154 | 0.062361 | -0.0056866 | -0.0042254 | -0.00068649 | -0.0062078 | 0.061039 | 0.061241 | -0.011121 | -0.0044605 | -0.045776 | -119.0964 | -7.3929 | -119.7006 | 0.19684 | -119.9387 | -119.8242 | -120.2866 | -0.16937 | -119.9112 | 0.073242 | 0.11444 | -119.8334 | -120.0531 | -0.086975 | 0.027466 | 0.059509 | 0.75531 | 0.15106 | 0.1236 | -0.18311 | 0.018311 | -0.20142 | -0.064087 | -0.43487 | -0.059509 | 0.14191 | -0.022888 | 120.0485 | 119.8059 | 112.4588 | -119.9615 | 119.9249 | 119.9661 | 119.6823 | -120.1904
1431.8594 | 120.1447 | -119.7418 | 0.31586 | 0.0066373 | 0.0071052 | 0.071634 | 0.0074746 | 0.061506 | -0.0039776 | -0.0023028 | -0.00068649 | -0.003858 | 0.061252 | 0.063805 | -0.0089849 | -0.0078783 | 0.073242 | -118.9819 | -7.4295 | -119.577 | 0.37994 | -119.8059 | -119.6869 | -120.1996 | -0.24261 | -119.8471 | 0.27924 | 0.29297 | -119.7052 | -119.9615 | -0.064087 | 0.054931 | 0.064087 | 0.75989 | 0.16479 | 0.10986 | -0.24261 | 0.036621 | -0.21973 | -0.036621 | -0.45776 | -0.10529 | 0.11444 | -0.022888 | 120.1218 | 119.8151 | 112.3123 | -120.0027 | 120.0211 | 120.0348 | 119.4992 | -120.2774
1433.5938 | 120.1309 | -119.87 | 0.21973 | -0.00099167 | 0.0073188 | 0.070993 | 0.0083292 | 0.062788 | 0.001363 | -0.0046526 | 0.0069425 | 0.00084176 | 0.06232 | 0.062523 | -0.0085577 | -0.0061695 | 0.009155 | -119.0964 | -7.5577 | -119.6503 | 0.35248 | -119.8608 | -119.7372 | -120.2774 | -0.33417 | -119.9249 | 0.23804 | 0.24719 | -119.8151 | -120.0302 | 0.009155 | 0.13275 | 0.13275 | 0.77362 | 0.21973 | 0.086975 | -0.21057 | 0.054932 | -0.16022 | 0.01831 | -0.40741 | -0.054932 | 0.10529 | 0.027465 | 120.2225 | 119.8792 | 112.3123 | -119.957 | 120.108 | 120.1172 | 119.5358 | -120.2499
1435.3438 | 120.2225 | -120.0302 | 0.19226 | 0.0066373 | 0.010096 | 0.071421 | 0.0040566 | 0.064497 | -0.00034604 | -0.00273 | 0.014572 | -0.0012946 | 0.061466 | 0.064659 | -0.0051397 | -0.0053149 | -0.07782 | -119.2795 | -7.5531 | -119.8517 | 0.21973 | -120.0485 | -119.9524 | -120.4056 | -0.25635 | -120.0714 | 0.091553 | 0.11902 | -119.9844 | -120.1904 | -0.018311 | 0.077819 | 0.027466 | 0.75073 | 0.17853 | 0.10071 | -0.27008 | 0.045776 | -0.16022 | -0.10071 | -0.37537 | -0.041199 | 0.11902 | -0.073242 | 120.2499 | 119.9524 | 112.4771 | -120.1447 | 120.1218 | 120.1492 | 119.7739 | -120.3827
1437.0469 | 120.3094 | -120.0394 | 0.17853 | 0.0066373 | 0.0021918 | 0.071634 | 0.0053384 | 0.061934 | 0.002431 | -0.001021 | -0.00068649 | 0.0010554 | 0.060398 | 0.063378 | -0.0074897 | -0.0055285 | -0.07782 | -119.339 | -7.5714 | -119.9066 | 0.23346 | -120.1126 | -119.9844 | -120.4971 | -0.25177 | -120.1721 | 0.1236 | 0.14648 | -119.9936 | -120.2637 | -0.073242 | 0.054932 | 0.054931 | 0.70038 | 0.13275 | 0.07782 | -0.25635 | 0.045777 | -0.2243 | -0.054932 | -0.45776 | -0.13275 | 0.091553 | -0.032044 | 120.2728 | 119.9615 | 112.468 | -120.163 | 120.163 | 120.1859 | 119.7876 | -120.4422
1438.7969 | 120.1904 | -119.9615 | 0.30212 | -0.00099167 | 0.0090278 | 0.069498 | 0.003843 | 0.061079 | -0.0026958 | -0.0020892 | 0.014572 | -0.003858 | 0.062748 | 0.063591 | -0.0062079 | -0.0076647 | 0.068665 | -119.1559 | -7.5256 | -119.7556 | 0.29755 | -119.9753 | -119.8608 | -120.3461 | -0.23804 | -119.9661 | 0.21057 | 0.23804 | -119.8654 | -120.1126 | -0.013733 | 0.10071 | -0.004578 | 0.80566 | 0.20599 | 0.10529 | -0.23346 | 0.096131 | -0.15106 | -0.091553 | -0.38452 | -0.004577 | 0.14648 | -0.064087 | 120.2591 | 120.0302 | 112.4359 | -120.163 | 120.1721 | 120.1996 | 119.7235 | -120.4147
1440.5469 | 120.2499 | -120.1218 | 0.19226 | 0.014267 | 0.0045416 | 0.068216 | 0.0029886 | 0.063643 | 0.0045674 | -0.0020892 | 0.014572 | 0.0016962 | 0.062961 | 0.063805 | -0.0047125 | -0.0068103 | -0.11444 | -119.4351 | -7.6309 | -119.9844 | 0.23346 | -120.1767 | -120.0485 | -120.5978 | -0.32501 | -120.2957 | 0.11444 | 0.14648 | -120.0806 | -120.3003 | -0.054932 | 0.073242 | 0.041198 | 0.68664 | 0.13733 | 0.064087 | -0.3067 | 0.041199 | -0.17853 | -0.07782 | -0.47607 | -0.17395 | 0.004578 | -0.045777 | 120.3552 | 120.0073 | 112.4908 | -120.2408 | 120.2362 | 120.2682 | 119.7968 | -120.4926
1442.2188 | 120.2682 | -120.1538 | 0.19226 | 0.0066373 | 0.0030464 | 0.06843 | 0.0046976 | 0.06172 | 0.0026446 | -0.001021 | -0.00068649 | -0.0012946 | 0.059543 | 0.065087 | -0.0074897 | -0.0070239 | -0.13275 | -119.4626 | -7.6447 | -120.0073 | 0.23346 | -120.1767 | -120.0577 | -120.6345 | -0.35248 | -120.3049 | 0.14648 | 0.14191 | -120.1035 | -120.3461 | -0.022888 | 0.096131 | 0.041198 | 0.69122 | 0.14648 | 0.050354 | -0.32501 | 0.050354 | -0.19226 | -0.045777 | -0.48065 | -0.15106 | 0.041198 | -0.050354 | 120.3873 | 120.0211 | 112.5092 | -120.2499 | 120.3003 | 120.2957 | 119.8013 | -120.5383
1443.9688 | 120.2957 | -120.1675 | 0.1831 | -0.00099167 | 0.012446 | 0.071634 | 0.0057656 | 0.060225 | -0.0056866 | -0.0052936 | 0.0069425 | -0.0032172 | 0.061252 | 0.064659 | -0.013471 | -0.0038195 | -0.10986 | -119.3939 | -7.5989 | -119.9982 | 0.18768 | -120.163 | -120.0485 | -120.6162 | -0.27466 | -120.2271 | 0.10529 | 0.11444 | -120.0577 | -120.3186 | 0.004578 | 0.11902 | 0.004578 | 0.77362 | 0.16937 | 0.050354 | -0.29297 | 0.10986 | -0.15106 | -0.077819 | -0.44861 | -0.059509 | 0.091553 | -0.068664 | 120.3552 | 120.0577 | 112.5687 | -120.2316 | 120.2728 | 120.282 | 119.8929 | -120.5017
1445.7188 | 120.2591 | -119.7784 | 0.50812 | 0.0066373 | 0.012018 | 0.071207 | 0.0034158 | 0.064283 | 0.0032856 | -0.0025164 | 0.0069425 | 0.0016962 | 0.060825 | 0.065941 | -0.0062079 | -0.0093737 | 0.16022 | -119.1376 | -7.6675 | -119.6823 | 0.57678 | -119.8151 | -119.7281 | -120.2866 | -0.37537 | -119.9753 | 0.44403 | 0.45776 | -119.7784 | -119.9753 | -0.036621 | 0.050354 | 0.068664 | 0.64087 | 0.09613 | 0.045776 | -0.3479 | 0 | -0.19684 | -0.064087 | -0.50812 | -0.19684 | 0 | -0.050354 | 120.3552 | 119.9387 | 112.1109 | -120.2362 | 120.2225 | 120.2362 | 119.4031 | -120.4834
1447.4688 | 120.369 | -120.2133 | 0.1831 | 0.0066373 | 0.010309 | 0.072489 | 0.003843 | 0.062574 | -0.00034604 | -0.0025164 | 0.0069425 | -0.00065364 | 0.06232 | 0.064446 | -0.0053533 | -0.0033923 | -0.14648 | -119.5175 | -7.7271 | -120.0714 | 0.24719 | -120.2454 | -120.1126 | -120.6573 | -0.32959 | -120.314 | 0.11902 | 0.1236 | -120.163 | -120.3827 | -0.032043 | 0.10071 | 0.064087 | 0.6958 | 0.14191 | 0.041199 | -0.32959 | 0.050354 | -0.16937 | -0.064086 | -0.44403 | -0.10071 | 0.068664 | -0.059509 | 120.4605 | 120.0668 | 112.4863 | -120.2957 | 120.3323 | 120.3369 | 119.8837 | -120.5658
1449.1562 | 120.3552 | -120.2408 | 0.19684 | 0.0066373 | 0.0047552 | 0.068857 | 0.0064066 | 0.062574 | 0.003072 | -0.00273 | 0.014572 | 0.00020076 | 0.06232 | 0.065087 | -0.0070623 | -0.0070239 | -0.14191 | -119.5358 | -7.6904 | -120.0714 | 0.22888 | -120.2637 | -120.1355 | -120.694 | -0.33417 | -120.3873 | 0.13275 | 0.15564 | -120.1447 | -120.3873 | -0.022888 | 0.10529 | 0.032044 | 0.70496 | 0.16937 | 0.064087 | -0.33875 | 0.096131 | -0.14648 | -0.064087 | -0.45319 | -0.14648 | 0 | -0.041198 | 120.4697 | 120.0989 | 112.5504 | -120.3323 | 120.3735 | 120.3964 | 119.9066 | -120.5841
1450.8906 | 120.4056 | -120.0439 | 0.28381 | 0.0066373 | 0.0086006 | 0.070993 | 0.0081154 | 0.063215 | -0.0031232 | -0.0046526 | 0.0069425 | -0.0017218 | 0.060398 | 0.064019 | -0.011762 | -0.0070239 | -0.013733 | -119.3253 | -7.6584 | -119.902 | 0.35706 | -120.1172 | -119.989 | -120.5612 | -0.27924 | -120.1767 | 0.25177 | 0.28381 | -120.0485 | -120.2454 | -0.073242 | 0.054931 | 0.073243 | 0.71869 | 0.14191 | 0.086975 | -0.29755 | -0.004578 | -0.20142 | -0.032043 | -0.51727 | -0.13275 | 0.068664 | 0 | 120.401 | 120.0302 | 112.3856 | -120.2728 | 120.2957 | 120.3278 | 119.7647 | -120.5292
1452.6406 | 120.4376 | -120.1996 | 0.16937 | 0.0066373 | 0.007746 | 0.071207 | 0.007261 | 0.061506 | -0.0029094 | -0.0057208 | 0.014572 | -0.0027898 | 0.061679 | 0.064446 | -0.010908 | -0.0063831 | -0.10529 | -119.4901 | -7.6859 | -120.0531 | 0.20599 | -120.2682 | -120.1218 | -120.7077 | -0.27466 | -120.3552 | 0.1236 | 0.15106 | -120.1813 | -120.4193 | -0.068665 | 0.07782 | 0.036621 | 0.70953 | 0.14648 | 0.068664 | -0.27466 | 0.018311 | -0.21973 | -0.045777 | -0.50812 | -0.15564 | 0.064087 | -0.018311 | 120.4056 | 120.0943 | 112.5137 | -120.2911 | 120.3232 | 120.3506 | 119.9249 | -120.5887
1454.3438 | 120.4742 | -120.2271 | 0.15106 | 0.014267 | 0.007746 | 0.071848 | 0.007261 | 0.061506 | -0.0052594 | -0.0018756 | 0.0069425 | -0.0040716 | 0.06232 | 0.060173 | -0.0087713 | -0.0063831 | -0.064087 | -119.4351 | -7.6492 | -120.0531 | 0.19226 | -120.2866 | -120.1263 | -120.6528 | -0.1831 | -120.2728 | 0.082397 | 0.11444 | -120.2087 | -120.4102 | -0.059509 | 0.10071 | 0.041199 | 0.79193 | 0.17395 | 0.073242 | -0.21515 | 0.018311 | -0.1831 | -0.068665 | -0.42572 | -0.045776 | 0.13733 | -0.036621 | 120.4193 | 120.163 | 112.5778 | -120.2774 | 120.3094 | 120.3415 | 120.0439 | -120.5612
1456.0938 | 120.5109 | -120.2133 | 0.14191 | -0.00099167 | 0.0098822 | 0.072489 | 0.005552 | 0.064283 | -0.0033368 | -0.0037982 | 0.022202 | -0.0027898 | 0.06232 | 0.065087 | -0.010053 | -0.0089465 | -0.054932 | -119.4397 | -7.6401 | -120.0623 | 0.19226 | -120.3094 | -120.1721 | -120.6619 | -0.16479 | -120.2866 | 0.086975 | 0.10071 | -120.2133 | -120.4147 | -0.09613 | 0.041199 | 0.050354 | 0.77362 | 0.15106 | 0.10986 | -0.19684 | 0 | -0.20142 | -0.054932 | -0.44861 | -0.073242 | 0.12817 | -0.041199 | 120.4056 | 120.1584 | 112.5732 | -120.314 | 120.3003 | 120.314 | 120.0485 | -120.5566
1457.7969 | 120.4971 | -120.2408 | 0.19684 | -0.00099167 | 0.006037 | 0.06843 | 0.0023476 | 0.061293 | 0.0034992 | -0.0042254 | 0.014572 | -0.0017218 | 0.062107 | 0.067864 | -0.0051397 | -0.0068103 | -0.1236 | -119.6732 | -7.8049 | -120.1859 | 0.26093 | -120.314 | -120.2087 | -120.7397 | -0.39368 | -120.4514 | 0.15564 | 0.15106 | -120.2271 | -120.4788 | -0.073242 | 0.032044 | 0.064087 | 0.56763 | 0.054932 | 0.022888 | -0.32043 | 0.013733 | -0.23804 | -0.041198 | -0.49896 | -0.21057 | 0.027466 | -0.045776 | 120.5017 | 120.1172 | 112.4359 | -120.4056 | 120.3964 | 120.3918 | 119.8471 | -120.6757
1459.5156 | 120.1813 | -119.8471 | 0.15564 | 0.014267 | 0.0053962 | 0.075052 | 0.0085428 | 0.061934 | -0.0014142 | -0.0014484 | 0.0069425 | -0.00044004 | 0.062534 | 0.06295 | -0.0085577 | -0.0068103 | -0.13275 | -119.1055 | -7.6859 | -119.7418 | 0.23804 | -119.9524 | -119.8425 | -120.4788 | -0.3479 | -120.0897 | 0.11902 | 0.14191 | -119.838 | -120.0439 | -0.10529 | 0.004578 | 0.082397 | 0.74158 | 0.10529 | 0.10071 | -0.28839 | 0.009155 | -0.19684 | -0.036621 | -0.63171 | -0.24262 | -0.045777 | -0.013733 | 120.0851 | 119.7144 | 112.1613 | -119.9982 | 119.9661 | 119.989 | 119.4992 | -120.1996
1461.2656 | 120.4422 | -120.1904 | 0.2243 | -0.00099167 | 0.009455 | 0.070353 | 0.0046976 | 0.063215 | 0.0020038 | -0.0018756 | 0.0069425 | 0.00084176 | 0.05997 | 0.064873 | -0.0055671 | -0.0070239 | -0.050354 | -119.4946 | -7.782 | -120.0623 | 0.30212 | -120.2499 | -120.108 | -120.6848 | -0.35248 | -120.3323 | 0.20599 | 0.21057 | -120.1584 | -120.3323 | -0.059509 | 0.082398 | 0.07782 | 0.6958 | 0.12817 | 0.045776 | -0.27466 | 0.032044 | -0.14191 | -0.01831 | -0.49438 | -0.14191 | 0 | -0.013733 | 120.4926 | 120.1401 | 112.4084 | -120.3323 | 120.3964 | 120.401 | 119.838 | -120.5566
1463.0156 | 120.3552 | -119.8929 | 0.51727 | 0.014267 | 0.0034736 | 0.069712 | 0.0053384 | 0.063002 | 0.003072 | -0.0023028 | 0.0069425 | 0.00041436 | 0.060611 | 0.064232 | -0.0064215 | -0.0046741 | 0.16479 | -119.2383 | -7.7683 | -119.7693 | 0.5722 | -119.9249 | -119.8242 | -120.3964 | -0.37537 | -120.0623 | 0.47607 | 0.48065 | -119.8334 | -120.076 | -0.032044 | 0.068664 | 0.054932 | 0.6546 | 0.1236 | 0.054932 | -0.35248 | 0.059509 | -0.18311 | -0.041199 | -0.50354 | -0.16937 | 0.013733 | -0.036621 | 120.4651 | 120.0577 | 112.1246 | -120.3415 | 120.369 | 120.3735 | 119.5175 | -120.5933
1464.7031 | 120.4742 | -120.2911 | 0.19226 | -0.00099167 | 0.0039008 | 0.067789 | 0.0049112 | 0.060011 | 0.00050836 | -0.0042254 | 0.0069425 | -0.0012946 | 0.061252 | 0.0653 | -0.0074897 | -0.0053149 | -0.15106 | -119.6548 | -7.8186 | -120.163 | 0.25177 | -120.3369 | -120.2408 | -120.7535 | -0.37537 | -120.4422 | 0.14191 | 0.15106 | -120.2454 | -120.4742 | -0.045776 | 0.050354 | 0.059509 | 0.63629 | 0.12817 | 0.07782 | -0.34332 | 0.045777 | -0.1831 | -0.050354 | -0.46234 | -0.15106 | 0.032043 | -0.041199 | 120.5429 | 120.1401 | 112.4725 | -120.433 | 120.433 | 120.4422 | 119.9158 | -120.6665
1466.4375 | 120.607 | -120.2728 | 0.15106 | 0.0066373 | 0.0030464 | 0.070353 | 0.0098244 | 0.062361 | -0.00077324 | -0.0012346 | 0.014572 | -0.0012946 | 0.060398 | 0.064873 | -0.010053 | -0.0074511 | -0.15106 | -119.6457 | -7.8049 | -120.1767 | 0.2243 | -120.3735 | -120.2545 | -120.7993 | -0.28839 | -120.4468 | 0.13275 | 0.14191 | -120.2911 | -120.488 | -0.10071 | 0.01831 | 0.073242 | 0.62714 | 0.09613 | 0.07782 | -0.30212 | -0.018311 | -0.21515 | -0.018311 | -0.52643 | -0.17395 | 0.041199 | -0.009155 | 120.4971 | 120.1218 | 112.468 | -120.4056 | 120.4056 | 120.4147 | 119.9844 | -120.639
1468.1719 | 120.3003 | -119.2337 | 0.97961 | 0.014267 | 0.011164 | 0.07078 | 0.002775 | 0.063215 | -0.00098684 | -0.0020892 | 0.0069425 | -0.0053534 | 0.060611 | 0.063805 | -0.0091985 | -0.0057421 | 0.75989 | -118.5104 | -7.6035 | -119.0414 | 1.0391 | -119.3161 | -119.1513 | -119.6457 | -0.25635 | -119.3527 | 0.89722 | 0.92926 | -119.2245 | -119.3848 | -0.082397 | 0.082398 | 0.05951 | 0.72327 | 0.19226 | 0.10986 | -0.21973 | 0.009156 | -0.15106 | -0.082397 | -0.41199 | -0.11902 | 0.032044 | -0.050354 | 120.2728 | 119.9936 | 111.6302 | -120.1309 | 120.1309 | 120.163 | 118.9774 | -120.3644
1469.9219 | 120.3735 | -119.7327 | 0.53101 | -0.00099167 | 0.006037 | 0.067575 | 0.0064066 | 0.06407 | 0.0022174 | -0.0014484 | -0.008316 | 0.00084176 | 0.063175 | 0.065514 | -0.0083441 | -0.0070239 | 0.27008 | -119.0277 | -7.6721 | -119.5908 | 0.59052 | -119.783 | -119.6732 | -120.1859 | -0.26093 | -119.8608 | 0.49896 | 0.5127 | -119.6823 | -119.9341 | -0.050354 | 0.059509 | 0.059509 | 0.70496 | 0.14191 | 0.082398 | -0.26092 | 0.050354 | -0.20142 | -0.032044 | -0.45319 | -0.12817 | 0.073242 | -0.018311 | 120.3232 | 120.0027 | 112.0605 | -120.2042 | 120.2316 | 120.2454 | 119.4717 | -120.4651
1471.5938 | 120.5429 | -120.2866 | 0.15106 | 0.0066373 | 0.013514 | 0.07313 | 0.0046976 | 0.06407 | -0.0076092 | -0.0040118 | 0.014572 | -0.0062078 | 0.061679 | 0.063164 | -0.0098395 | -0.0053149 | -0.15106 | -119.5633 | -7.8049 | -120.1355 | 0.19684 | -120.3369 | -120.1996 | -120.7581 | -0.29297 | -120.3644 | 0.082397 | 0.11444 | -120.2682 | -120.4651 | -0.050354 | 0.086975 | 0.045776 | 0.72327 | 0.15106 | 0.064087 | -0.30212 | 0.01831 | -0.17853 | -0.068665 | -0.4715 | -0.07782 | 0.10071 | -0.036621 | 120.4834 | 120.1355 | 112.4817 | -120.3506 | 120.369 | 120.401 | 119.9936 | -120.6161
1473.3281 | 120.4605 | -120.369 | 0.18768 | 0.014267 | 0.0133 | 0.072062 | 0.0046976 | 0.063643 | -0.0014142 | -0.0059344 | -0.00068649 | -0.0025762 | 0.05997 | 0.064019 | -0.01048 | -0.0068103 | -0.050354 | -119.5312 | -7.7454 | -120.1538 | 0.18768 | -120.3506 | -120.2271 | -120.7672 | -0.27466 | -120.3827 | 0.091553 | 0.10071 | -120.2728 | -120.4971 | 0.018311 | 0.14191 | 0 | 0.83771 | 0.21515 | 0.073242 | -0.23804 | 0.096131 | -0.12817 | -0.09613 | -0.39825 | -0.013732 | 0.11444 | -0.086975 | 120.5566 | 120.3186 | 112.6236 | -120.4147 | 120.4605 | 120.4697 | 120.0943 | -120.6848
1475.0781 | 120.5292 | -120.3827 | 0.18768 | 0.0066373 | 0.0051826 | 0.069498 | 0.0051248 | 0.063856 | 0.0026446 | -0.0042254 | 0.0069425 | 0.00041436 | 0.063388 | 0.064446 | -0.0051397 | -0.0070239 | -0.073242 | -119.6365 | -7.782 | -120.2179 | 0.22888 | -120.3827 | -120.2866 | -120.8221 | -0.32044 | -120.5154 | 0.11902 | 0.15106 | -120.3278 | -120.5475 | 0 | 0.09613 | 0.041199 | 0.74615 | 0.16479 | 0.068664 | -0.26092 | 0.054931 | -0.16479 | -0.068664 | -0.43945 | -0.13275 | 0.032043 | -0.036621 | 120.6116 | 120.3094 | 112.6007 | -120.4742 | 120.5017 | 120.5338 | 120.0623 | -120.7352
1476.7656 | 120.5795 | -120.3232 | 0.16022 | 0.014267 | 0.0096686 | 0.073343 | 0.0059792 | 0.060438 | -0.0048322 | -0.0052936 | 0.0069425 | -0.005567 | 0.060825 | 0.062096 | -0.011121 | -0.0061695 | -0.068665 | -119.5175 | -7.7316 | -120.1584 | 0.19226 | -120.4239 | -120.2728 | -120.7718 | -0.17395 | -120.3918 | 0.064087 | 0.10529 | -120.3094 | -120.5338 | -0.10071 | 0.050354 | 0.032044 | 0.80566 | 0.1648 | 0.11444 | -0.22888 | 0.013733 | -0.21057 | -0.09613 | -0.44861 | -0.068665 | 0.14191 | -0.054931 | 120.5154 | 120.2545 | 112.5916 | -120.433 | 120.3873 | 120.4285 | 120.1492 | -120.694
1478.5 | 120.639 | -120.3461 | 0.13733 | 0.014267 | 0.0056098 | 0.071848 | 0.0081154 | 0.06172 | 0.0020038 | -0.0057208 | -0.00068649 | -0.0027898 | 0.064243 | 0.064019 | -0.011335 | -0.0083057 | -0.15564 | -119.7189 | -7.8644 | -120.282 | 0.23804 | -120.4788 | -120.3232 | -120.9 | -0.3479 | -120.5475 | 0.1236 | 0.17395 | -120.3644 | -120.575 | -0.13275 | 0.022888 | 0.10071 | 0.62714 | 0.064087 | 0.041199 | -0.29297 | -0.018311 | -0.22888 | -0.013733 | -0.55389 | -0.20142 | 0.027466 | 0.036621 | 120.5841 | 120.1904 | 112.4817 | -120.4605 | 120.4697 | 120.52 | 119.9982 | -120.7123
1480.25 | 120.5612 | -120.4193 | 0.16937 | -0.00099167 | 0.013941 | 0.070139 | 0.0076882 | 0.064497 | -0.003764 | -0.0040118 | 0.0069425 | -0.0053534 | 0.062107 | 0.064019 | -0.011549 | -0.0051013 | -0.10986 | -119.6777 | -7.8232 | -120.2454 | 0.20142 | -120.4056 | -120.3049 | -120.8496 | -0.31586 | -120.4742 | 0.10071 | 0.11444 | -120.3461 | -120.5612 | 0.013733 | 0.11444 | 0.032043 | 0.74158 | 0.17395 | 0.05951 | -0.27924 | 0.073243 | -0.14191 | -0.068665 | -0.4303 | -0.054931 | 0.086975 | -0.054932 | 120.6207 | 120.3094 | 112.5961 | -120.4742 | 120.52 | 120.5338 | 120.1035 | -120.7306
1481.9375 | 120.5887 | -120.3964 | 0.18768 | -0.00099167 | 0.0098822 | 0.072062 | 0.0034158 | 0.062147 | 0.0032856 | -0.003371 | -0.00068649 | 0.00041436 | 0.060611 | 0.067009 | -0.0074897 | -0.0083057 | -0.10071 | -119.7464 | -7.869 | -120.2911 | 0.23804 | -120.433 | -120.3415 | -120.845 | -0.35706 | -120.5246 | 0.11902 | 0.11444 | -120.3781 | -120.5841 | -0.036621 | 0.054931 | 0.050354 | 0.65002 | 0.10528 | 0.050354 | -0.28839 | 0.01831 | -0.18768 | -0.068664 | -0.44861 | -0.12817 | 0.059509 | -0.073242 | 120.6345 | 120.2957 | 112.5275 | -120.5292 | 120.5154 | 120.5109 | 120.0394 | -120.7718
1483.6094 | 120.5246 | -119.8059 | 0.6134 | -0.00099167 | 0.0092414 | 0.074411 | 0.0061928 | 0.06407 | -0.0041912 | -0.0046526 | 0.0069425 | -0.0047124 | 0.061679 | 0.064659 | -0.0079169 | -0.0070239 | 0.43945 | -118.959 | -7.7042 | -119.6457 | 0.64545 | -119.8563 | -119.7235 | -120.2042 | -0.21057 | -119.8517 | 0.54932 | 0.5722 | -119.7693 | -119.9982 | -0.050354 | 0.082397 | 0.032044 | 0.84686 | 0.16022 | 0.07782 | -0.17395 | 0.036621 | -0.19226 | -0.064087 | -0.39825 | -0.045777 | 0.14648 | -0.041198 | 120.4514 | 120.2454 | 112.1017 | -120.3369 | 120.3552 | 120.3781 | 119.5953 | -120.6116
1485.3594 | 120.6665 | -120.076 | 0.46692 | -0.0086212 | 0.0019782 | 0.07078 | 0.0040566 | 0.062361 | 0.0045674 | -0.00059384 | -0.00068649 | 0.001269 | 0.060611 | 0.063378 | -0.0057807 | -0.0093737 | 0.24261 | -119.2612 | -7.7591 | -119.8334 | 0.54932 | -120.1538 | -119.9982 | -120.401 | -0.27924 | -120.108 | 0.43945 | 0.45319 | -119.9753 | -120.195 | -0.07782 | 0.07782 | 0.082397 | 0.81482 | 0.24262 | 0.16479 | -0.2243 | 0.10071 | -0.11902 | -0.027466 | -0.32501 | -0.032043 | 0.086975 | -0.013733 | 120.6253 | 120.3186 | 112.3169 | -120.4651 | 120.5154 | 120.5292 | 119.7968 | -120.6619
1487.1094 | 120.5612 | -120.2271 | 0.31586 | -0.0086212 | 0.012446 | 0.074411 | 0.0057656 | 0.063429 | -0.003764 | -0.0037982 | -0.00068649 | -0.0051398 | 0.061893 | 0.062096 | -0.0091985 | -0.0051013 | 0.036621 | -119.4763 | -7.8232 | -120.0714 | 0.35248 | -120.2499 | -120.1401 | -120.6665 | -0.32044 | -120.2911 | 0.27466 | 0.28839 | -120.1996 | -120.401 | -0.022888 | 0.086975 | 0.036621 | 0.75073 | 0.15564 | 0.068665 | -0.27924 | 0.027466 | -0.17395 | -0.041199 | -0.43945 | -0.064087 | 0.10986 | -0.027466 | 120.5795 | 120.2637 | 112.4039 | -120.4559 | 120.5017 | 120.5154 | 119.9066 | -120.7169
1488.7969 | 120.5795 | -120.0439 | 0.44403 | 0.014267 | 0.0041144 | 0.070566 | 0.0066202 | 0.063429 | 0.0037128 | 0.0013288 | -0.008316 | 0.0010554 | 0.061039 | 0.064446 | -0.0051397 | -0.0068103 | 0.18768 | -119.3161 | -7.782 | -119.9661 | 0.49439 | -120.1218 | -120.0027 | -120.4742 | -0.35706 | -120.1584 | 0.36621 | 0.40741 | -120.0165 | -120.2911 | -0.07782 | 0.041198 | 0.050354 | 0.72784 | 0.07782 | 0.036622 | -0.25635 | 0.027466 | -0.24719 | -0.07782 | -0.4303 | -0.11444 | 0.13275 | -0.036621 | 120.5383 | 120.2316 | 112.262 | -120.4468 | 120.4102 | 120.4514 | 119.6869 | -120.7352
1490.5469 | 120.3278 | -120.0623 | 0.17395 | 0.014267 | 0.01095 | 0.071848 | 0.0023476 | 0.06172 | -0.00013244 | -0.0035846 | 0.0069425 | 0.00062796 | 0.060398 | 0.062737 | -0.0074897 | -0.0063831 | -0.10529 | -119.4168 | -7.8323 | -119.9753 | 0.2243 | -120.1401 | -120.0485 | -120.5246 | -0.32959 | -120.1859 | 0.09613 | 0.12817 | -120.0577 | -120.2728 | -0.07782 | 0.013733 | 0.050354 | 0.64545 | 0.086975 | 0.073242 | -0.27924 | 0.004578 | -0.21057 | -0.07782 | -0.46234 | -0.1236 | 0.086975 | -0.045776 | 120.2866 | 119.957 | 112.2299 | -120.2225 | 120.1584 | 120.1904 | 119.7327 | -120.4468
1492.2344 | 120.52 | -120.1996 | 0.15564 | 0.014267 | 0.010309 | 0.071421 | 0.0083292 | 0.061934 | -0.0059002 | -0.0018756 | -0.00068649 | -0.003858 | 0.060611 | 0.0653 | -0.011762 | -0.0042467 | -0.022888 | -119.3939 | -7.7683 | -120.0348 | 0.21515 | -120.2454 | -120.1355 | -120.6345 | -0.20142 | -120.2545 | 0.10071 | 0.11444 | -120.195 | -120.4147 | -0.045776 | 0.064087 | 0.059509 | 0.80566 | 0.16479 | 0.10071 | -0.17853 | 0.004578 | -0.21515 | -0.054932 | -0.43488 | -0.054932 | 0.16022 | -0.041199 | 120.4147 | 120.1767 | 112.4313 | -120.2911 | 120.3003 | 120.314 | 119.9982 | -120.5704
1493.9844 | 120.5841 | -120.2362 | 0.15106 | -0.00099167 | 0.013087 | 0.071421 | 0.0070474 | 0.063002 | -0.0039776 | -0.004439 | 0.014572 | -0.0032172 | 0.059757 | 0.0653 | -0.01283 | -0.0083057 | -0.064087 | -119.5221 | -7.8369 | -120.1172 | 0.18768 | -120.314 | -120.2133 | -120.6848 | -0.25635 | -120.314 | 0.09613 | 0.10529 | -120.2591 | -120.4605 | -0.07782 | 0.022888 | 0.036621 | 0.71411 | 0.11902 | 0.096131 | -0.21515 | -0.022888 | -0.2243 | -0.054932 | -0.44861 | -0.07782 | 0.14648 | -0.045776 | 120.4239 | 120.1721 | 112.3993 | -120.3644 | 120.3323 | 120.3415 | 119.9799 | -120.6116
1495.6719 | 120.4697 | -120.3598 | 0.18768 | 0.0066373 | 0.013087 | 0.069071 | 0.0012796 | 0.062147 | -0.0016278 | -0.0042254 | -0.00068649 | -0.0017218 | 0.058475 | 0.063164 | -0.0083441 | -0.0065967 | -0.032043 | -119.5175 | -7.8506 | -120.1401 | 0.19226 | -120.3415 | -120.2179 | -120.7352 | -0.31586 | -120.3506 | 0.10071 | 0.1236 | -120.2957 | -120.5063 | 0.01831 | 0.14191 | 0.004578 | 0.84229 | 0.21973 | 0.07782 | -0.21973 | 0.064087 | -0.14648 | -0.086975 | -0.37537 | 0.009155 | 0.15564 | -0.064087 | 120.5521 | 120.3278 | 112.5092 | -120.4056 | 120.4605 | 120.4834 | 120.0439 | -120.694
1497.4062 | 120.5429 | -119.902 | 0.53101 | 0.0066373 | 0.0079596 | 0.071634 | 0.0059792 | 0.062361 | -0.00098684 | -0.0042254 | 0.0069425 | -0.0025762 | 0.060184 | 0.061241 | -0.0098395 | -0.0065967 | 0.26093 | -119.1696 | -7.8094 | -119.7601 | 0.58594 | -119.9799 | -119.8517 | -120.3827 | -0.28381 | -120.0211 | 0.47607 | 0.50812 | -119.9295 | -120.1172 | -0.077819 | 0.050354 | 0.054931 | 0.73242 | 0.14191 | 0.091553 | -0.27008 | -0.027465 | -0.21515 | -0.054932 | -0.48065 | -0.11902 | 0.09613 | -0.022888 | 120.488 | 120.163 | 112.0926 | -120.3827 | 120.3781 | 120.4102 | 119.6182 | -120.6482
1499.1562 | 120.5841 | -119.9799 | 0.45776 | -0.00099167 | 0.0036872 | 0.071634 | 0.0079018 | 0.062788 | 0.0011494 | -0.0035846 | 0.014572 | -0.00044004 | 0.060398 | 0.065087 | -0.0083441 | -0.0068103 | 0.086975 | -119.3527 | -7.8369 | -119.9799 | 0.50812 | -120.1035 | -120.0027 | -120.5338 | -0.37537 | -120.1996 | 0.36621 | 0.41199 | -120.0623 | -120.2591 | -0.1236 | -0.022889 | 0.050354 | 0.62714 | 0 | 0.022889 | -0.37079 | -0.082398 | -0.27924 | -0.091553 | -0.55389 | -0.21973 | 0.059509 | -0.045777 | 120.488 | 120.0668 | 112.1429 | -120.4605 | 120.3461 | 120.3918 | 119.6045 | -120.7169
1500.9062 | 120.5612 | -120.401 | 0.20142 | -0.0086212 | 0.0056098 | 0.069712 | 0.0032022 | 0.062574 | 0.00414 | -0.0023028 | 0.0069425 | 0.0021234 | 0.061252 | 0.063591 | -0.0038581 | -0.0080921 | -0.14191 | -119.7601 | -8.02 | -120.2866 | 0.23346 | -120.4468 | -120.3598 | -120.8954 | -0.44861 | -120.575 | 0.14191 | 0.16022 | -120.3781 | -120.607 | -0.045776 | 0.041199 | 0.032043 | 0.64087 | 0.11444 | 0.073242 | -0.34332 | 0.022888 | -0.20599 | -0.059509 | -0.49439 | -0.17395 | 0.032044 | -0.041199 | 120.6345 | 120.2591 | 112.381 | -120.5612 | 120.5429 | 120.5612 | 119.9524 | -120.8084
1502.6406 | 120.6665 | -120.4147 | 0.17853 | 0.0066373 | 0.006037 | 0.072702 | 0.0081154 | 0.061293 | -0.00077324 | -0.0025164 | -0.00068649 | -1.2844e-05 | 0.064457 | 0.064873 | -0.0091985 | -0.0083057 | -0.15106 | -119.7098 | -8.0017 | -120.314 | 0.23346 | -120.4697 | -120.369 | -120.9 | -0.38452 | -120.5612 | 0.14648 | 0.14648 | -120.4239 | -120.6162 | -0.054932 | 0.045776 | 0.054931 | 0.70496 | 0.10071 | 0.054932 | -0.32959 | -0.009155 | -0.20142 | -0.032044 | -0.48523 | -0.14648 | 0.054932 | -0.032044 | 120.6482 | 120.2637 | 112.413 | -120.5475 | 120.5612 | 120.5612 | 120.0302 | -120.7947
1504.3281 | 120.5887 | -120.4193 | 0.18768 | -0.00099167 | 0.0019782 | 0.069071 | 0.0053384 | 0.064283 | 0.003072 | -0.001662 | 0.0069425 | 0.0021234 | 0.062107 | 0.064873 | -0.0051397 | -0.0065967 | -0.068665 | -119.6823 | -7.9742 | -120.2591 | 0.22888 | -120.4742 | -120.3461 | -120.8588 | -0.35706 | -120.5795 | 0.12817 | 0.14648 | -120.4239 | -120.6207 | -0.054931 | 0.073243 | 0.041199 | 0.737 | 0.16022 | 0.086975 | -0.25635 | -0.004577 | -0.20142 | -0.059509 | -0.43945 | -0.16022 | 0.041199 | -0.041199 | 120.6482 | 120.3506 | 112.4451 | -120.5338 | 120.5475 | 120.5658 | 120.0623 | -120.8084
1506.0781 | 120.5978 | -120.4102 | 0.24261 | 0.0066373 | 0.00048277 | 0.068216 | 0.0046976 | 0.063429 | 0.0011494 | -0.0012346 | 0.0069425 | -0.00022644 | 0.061466 | 0.064019 | -0.0072759 | -0.0061695 | -0.082397 | -119.696 | -8.0063 | -120.2728 | 0.25635 | -120.4468 | -120.314 | -120.8817 | -0.41657 | -120.5612 | 0.17395 | 0.17853 | -120.3873 | -120.5841 | -0.036621 | 0.09613 | 0.013733 | 0.71411 | 0.13733 | 0.041199 | -0.32501 | 0.022888 | -0.17395 | -0.068665 | -0.4715 | -0.15106 | 0.022888 | -0.064087 | 120.6665 | 120.3278 | 112.4039 | -120.5566 | 120.5841 | 120.5887 | 119.9936 | -120.8267
1507.8281 | 120.7123 | -120.3918 | 0.1831 | 0.0066373 | 0.0039008 | 0.069071 | 0.0076882 | 0.062788 | 0.0017902 | -0.0020892 | 0.0069425 | -1.2844e-05 | 0.063602 | 0.068077 | -0.0081305 | -0.0063831 | -0.054932 | -119.6594 | -7.9971 | -120.2362 | 0.27008 | -120.4376 | -120.3598 | -120.8633 | -0.34332 | -120.52 | 0.14648 | 0.16937 | -120.3964 | -120.5978 | -0.045776 | 0.032044 | 0.086976 | 0.73242 | 0.15564 | 0.1236 | -0.23804 | -0.004577 | -0.20599 | -0.036621 | -0.4715 | -0.12817 | 0.077819 | -0.013732 | 120.6619 | 120.3369 | 112.3947 | -120.5429 | 120.5383 | 120.5612 | 120.0485 | -120.7809
1509.5781 | 120.6757 | -120.1126 | 0.42114 | 0.0066373 | 0.0019782 | 0.067362 | 0.007261 | 0.063002 | -0.00055964 | -0.001021 | 0.0069425 | 0.00041436 | 0.062748 | 0.065087 | -0.0074897 | -0.0065967 | 0.15106 | -119.4168 | -7.9697 | -119.9661 | 0.4715 | -120.1813 | -120.076 | -120.5841 | -0.36163 | -120.2499 | 0.39825 | 0.39825 | -120.0714 | -120.3323 | -0.068664 | 0.036621 | 0.050354 | 0.6958 | 0.14648 | 0.10986 | -0.27008 | 0.041199 | -0.21973 | -0.022889 | -0.4715 | -0.13733 | 0.082397 | -0.022889 | 120.5841 | 120.2637 | 112.1429 | -120.4971 | 120.5109 | 120.5109 | 119.751 | -120.7535
1511.3125 | 120.5566 | -119.6503 | 0.81482 | -0.00099167 | 0.0034736 | 0.06843 | 0.0064066 | 0.064283 | 0.00029476 | -0.0012346 | 0.0069425 | -0.0017218 | 0.062107 | 0.067223 | -0.0089849 | -0.0074511 | 0.63629 | -118.8904 | -7.9834 | -119.5175 | 0.90179 | -119.7098 | -119.632 | -120.0302 | -0.40283 | -119.6869 | 0.8194 | 0.81482 | -119.6045 | -119.8151 | -0.059509 | 0.018311 | 0.086975 | 0.75989 | 0.13275 | 0.11444 | -0.17853 | 0.045777 | -0.16479 | 0.004578 | -0.37994 | -0.036621 | 0.12817 | 0 | 120.5521 | 120.2866 | 111.6669 | -120.4468 | 120.4697 | 120.4651 | 119.2474 | -120.6299
1513 | 120.6162 | -119.8013 | 0.60425 | -0.0086212 | 0.0034736 | 0.069712 | 0.0074746 | 0.062788 | -0.00098684 | -0.001662 | -0.00068649 | -0.00022644 | 0.063388 | 0.066796 | -0.010053 | -0.0063831 | 0.32044 | -119.1925 | -8.0063 | -119.7464 | 0.6958 | -119.9203 | -119.8196 | -120.3415 | -0.39825 | -119.9753 | 0.6134 | 0.62714 | -119.8334 | -120.0439 | -0.11902 | -0.01831 | 0.091553 | 0.60883 | 0.054932 | 0.073242 | -0.28381 | -0.032043 | -0.24261 | 0.009155 | -0.54016 | -0.17395 | 0.068664 | 0.022888 | 120.4971 | 120.1218 | 111.795 | -120.4239 | 120.4147 | 120.4285 | 119.4031 | -120.6482
1514.7344 | 120.5978 | -120.3918 | 0.24261 | 0.0066373 | 0.0088142 | 0.069284 | 0.003843 | 0.064924 | 0.0015766 | -0.0031574 | -0.00068649 | 0.00020076 | 0.063175 | 0.066582 | -0.0057807 | -0.0057421 | -0.11902 | -119.7235 | -8.1161 | -120.3049 | 0.2655 | -120.4422 | -120.3598 | -120.8817 | -0.43945 | -120.5292 | 0.1831 | 0.18768 | -120.4056 | -120.5841 | -0.050354 | 0.032044 | 0.022888 | 0.66833 | 0.086975 | 0.054931 | -0.36163 | -0.013733 | -0.19226 | -0.05951 | -0.48981 | -0.13733 | 0.054931 | -0.054932 | 120.6573 | 120.2728 | 112.2757 | -120.6024 | 120.575 | 120.5795 | 119.9524 | -120.8267
1516.4844 | 120.6482 | -120.3461 | 0.24719 | -0.00099167 | 0.0079596 | 0.072489 | 0.00897 | 0.062361 | -0.0063274 | -0.0042254 | 0.0069425 | -0.003858 | 0.058689 | 0.064019 | -0.011121 | -0.0070239 | 0.032043 | -119.5496 | -8.02 | -120.1675 | 0.27466 | -120.3644 | -120.2637 | -120.7901 | -0.32044 | -120.3918 | 0.16022 | 0.1831 | -120.3415 | -120.5475 | -0.018311 | 0.082397 | 0.027466 | 0.79651 | 0.17853 | 0.09613 | -0.21515 | 0.004577 | -0.20142 | -0.086975 | -0.44403 | -0.045777 | 0.15564 | -0.064087 | 120.6207 | 120.3781 | 112.326 | -120.5109 | 120.5063 | 120.5292 | 120.0256 | -120.7947
1518.1719 | 120.52 | -120.0211 | 0.55389 | -0.00099167 | 0.0053962 | 0.069071 | 0.0025612 | 0.061079 | 0.0026446 | -0.003371 | 0.0069425 | -0.0015082 | 0.060611 | 0.066368 | -0.0053533 | -0.0068103 | 0.22888 | -119.3756 | -8.0978 | -119.902 | 0.59052 | -120.0439 | -119.9387 | -120.5154 | -0.53558 | -120.195 | 0.50354 | 0.51727 | -119.9936 | -120.2179 | -0.022888 | 0.082397 | 0.036621 | 0.64545 | 0.11902 | 0.036621 | -0.32501 | 0.027466 | -0.19684 | -0.050354 | -0.49438 | -0.17395 | 0.022889 | -0.036621 | 120.6116 | 120.2499 | 111.9232 | -120.4926 | 120.5246 | 120.5383 | 119.4855 | -120.7718
1519.9062 | 120.6482 | -120.4651 | 0.1831 | 0.0066373 | 0.010309 | 0.069498 | 0.0019204 | 0.061079 | 0.00029476 | -0.0029436 | -0.00068649 | -0.00022644 | 0.060611 | 0.065728 | -0.0064215 | -0.0078783 | -0.1236 | -119.8059 | -8.1665 | -120.369 | 0.22888 | -120.52 | -120.4193 | -120.9366 | -0.51727 | -120.5795 | 0.11902 | 0.15564 | -120.4468 | -120.6482 | -0.054932 | 0.045776 | 0.045777 | 0.65918 | 0.09613 | 0.050354 | -0.3067 | 0.018311 | -0.18311 | -0.064086 | -0.4715 | -0.11444 | 0.068664 | -0.027465 | 120.694 | 120.3415 | 112.2986 | -120.6024 | 120.5841 | 120.6207 | 119.9478 | -120.8313
1521.6406 | 119.9615 | -119.6045 | 0.21057 | -0.00099167 | 0.013941 | 0.073557 | 0.0044838 | 0.061506 | -0.0067548 | -0.0055072 | -0.00068649 | -0.0042852 | 0.060184 | 0.063164 | -0.011121 | -0.0061695 | -0.10529 | -118.9545 | -8.0429 | -119.5358 | 0.22888 | -119.7006 | -119.5908 | -120.1675 | -0.5127 | -119.7372 | 0.11444 | 0.16022 | -119.6594 | -119.87 | -0.096131 | 0.013733 | 0.018311 | 0.65002 | 0.068664 | 0.054931 | -0.31586 | -0.054932 | -0.2655 | -0.09613 | -0.56305 | -0.13275 | 0.13275 | -0.050354 | 119.8334 | 119.4992 | 111.5616 | -119.8013 | 119.7189 | 119.7647 | 119.0918 | -120.0806
1523.3125 | 120.488 | -120.1859 | 0.15106 | -0.0086212 | 0.006037 | 0.071634 | 0.0081154 | 0.063429 | -0.0031232 | -0.004439 | 0.014572 | -0.0027898 | 0.062748 | 0.062523 | -0.010694 | -0.0070239 | -0.045776 | -119.4168 | -8.0566 | -120.0256 | 0.18768 | -120.2408 | -120.1538 | -120.6345 | -0.37079 | -120.2728 | 0.086975 | 0.11902 | -120.2042 | -120.4193 | -0.054932 | 0.032043 | 0.036621 | 0.76904 | 0.16022 | 0.12817 | -0.19684 | -0.018311 | -0.23346 | -0.064087 | -0.44861 | -0.086975 | 0.14648 | -0.032043 | 120.3735 | 120.1401 | 112.1292 | -120.3049 | 120.2728 | 120.3049 | 119.8151 | -120.5704
1525.0469 | 120.401 | -119.9478 | 0.43488 | 0.0066373 | 0.0017646 | 0.067575 | 0.0051248 | 0.061934 | 0.0039264 | -0.003371 | -0.00068649 | 0.00084176 | 0.060611 | 0.0653 | -0.0042853 | -0.010015 | 0.21973 | -119.2017 | -8.1436 | -119.7784 | 0.51727 | -119.957 | -119.8471 | -120.3735 | -0.55847 | -120.076 | 0.39825 | 0.44403 | -119.8746 | -120.1035 | -0.009155 | 0.10071 | 0.082398 | 0.74616 | 0.16937 | 0.068665 | -0.21515 | 0.073242 | -0.15564 | -0.036621 | -0.42572 | -0.12817 | 0.027466 | 0.009156 | 120.4651 | 120.1675 | 111.8042 | -120.282 | 120.3461 | 120.3918 | 119.3893 | -120.5383
1526.7969 | 120.5063 | -120.3186 | 0.17853 | -0.00099167 | 0.010309 | 0.069498 | 0.00085245 | 0.062361 | -0.00013244 | -0.00059384 | 0.0069425 | -0.0025762 | 0.060825 | 0.0653 | -0.0074897 | -0.0087329 | -0.041199 | -119.5267 | -8.1528 | -120.1263 | 0.17853 | -120.3461 | -120.2454 | -120.7077 | -0.45776 | -120.3552 | 0.09613 | 0.10986 | -120.2911 | -120.4651 | -0.027465 | 0.073243 | 0 | 0.79193 | 0.19226 | 0.11902 | -0.21973 | 0.027466 | -0.14648 | -0.082398 | -0.3891 | -0.036621 | 0.10986 | -0.068665 | 120.4971 | 120.2774 | 112.1658 | -120.4239 | 120.4147 | 120.4285 | 119.8608 | -120.6436
1528.5469 | 120.5658 | -120.1904 | 0.14191 | 0.0066373 | 0.012873 | 0.072702 | 0.0059792 | 0.061079 | -0.0035504 | -0.0048662 | -0.00068649 | -0.0036444 | 0.058902 | 0.06295 | -0.010694 | -0.0063831 | -0.11444 | -119.5221 | -8.1985 | -120.0943 | 0.17853 | -120.2682 | -120.1675 | -120.694 | -0.46692 | -120.3049 | 0.064087 | 0.09613 | -120.2271 | -120.4697 | -0.07782 | 0.022888 | 0.036621 | 0.66834 | 0.096131 | 0.073243 | -0.25635 | -0.036621 | -0.27924 | -0.07782 | -0.50354 | -0.11444 | 0.16479 | -0.045777 | 120.369 | 120.076 | 111.9919 | -120.3094 | 120.2545 | 120.2866 | 119.7235 | -120.6116
1530.2344 | 120.5246 | -120.3827 | 0.14191 | 0.014267 | 0.013087 | 0.073771 | 0.005552 | 0.062147 | -0.003764 | -0.0052936 | 0.0069425 | -0.0023626 | 0.060398 | 0.066796 | -0.0085577 | -0.0089465 | -0.11444 | -119.5953 | -8.2581 | -120.2133 | 0.16479 | -120.3781 | -120.314 | -120.7993 | -0.53101 | -120.4285 | 0.068665 | 0.10071 | -120.3461 | -120.5612 | 0.004577 | 0.068664 | 0.022888 | 0.78735 | 0.16937 | 0.10071 | -0.25635 | 0.036621 | -0.17853 | -0.073242 | -0.41657 | -0.045777 | 0.13275 | -0.041199 | 120.5475 | 120.2682 | 112.1246 | -120.4559 | 120.4514 | 120.4834 | 119.8517 | -120.7031
1531.9844 | 120.6482 | -120.3964 | 0.13733 | -0.00099167 | 0.010096 | 0.072702 | 0.0081154 | 0.063215 | -0.0016278 | -0.0042254 | 0.0069425 | -0.0036444 | 0.063388 | 0.061882 | -0.0079169 | -0.0085193 | -0.064087 | -119.5862 | -8.194 | -120.2042 | 0.1831 | -120.4285 | -120.3186 | -120.8176 | -0.43945 | -120.4514 | 0.064087 | 0.09613 | -120.4193 | -120.5841 | -0.032044 | 0.077819 | 0.045776 | 0.81024 | 0.19226 | 0.11444 | -0.20142 | -0.022889 | -0.18768 | -0.073242 | -0.42114 | -0.054932 | 0.13275 | -0.041199 | 120.5795 | 120.3323 | 112.2025 | -120.4559 | 120.4605 | 120.4926 | 119.957 | -120.7214
1533.7344 | 120.575 | -120.4742 | 0.15564 | -0.00099167 | 0.0058234 | 0.071207 | 0.002134 | 0.064497 | 0.0062762 | -0.00273 | 0.0069425 | 0.002337 | 0.060398 | 0.065728 | -0.0057807 | -0.0098009 | -0.15564 | -119.8013 | -8.3862 | -120.2957 | 0.20599 | -120.488 | -120.3918 | -120.9274 | -0.63171 | -120.639 | 0.12817 | 0.11902 | -120.4376 | -120.6436 | -0.013733 | 0.082397 | 0.050354 | 0.67291 | 0.17853 | 0.096131 | -0.31128 | 0.036621 | -0.16937 | -0.027466 | -0.45319 | -0.16479 | 0.004578 | -0.036621 | 120.6802 | 120.3186 | 112.088 | -120.5475 | 120.6024 | 120.5933 | 119.8425 | -120.7993
1535.4688 | 120.726 | -120.4056 | 0.1236 | -0.0086212 | 0.012446 | 0.073557 | 0.0064066 | 0.062788 | -0.0018414 | -0.0048662 | 0.0069425 | -0.0070624 | 0.062107 | 0.062523 | -0.011549 | -0.0059557 | -0.068665 | -119.6182 | -8.2764 | -120.2637 | 0.19684 | -120.4834 | -120.3827 | -120.8359 | -0.46692 | -120.4742 | 0.09613 | 0.10071 | -120.4422 | -120.639 | -0.077819 | 0.022889 | 0.073242 | 0.78735 | 0.14191 | 0.11902 | -0.19226 | -0.036621 | -0.23346 | -0.027466 | -0.4303 | -0.068664 | 0.16479 | -0.022888 | 120.6024 | 120.3369 | 112.1292 | -120.5063 | 120.5017 | 120.5063 | 119.9387 | -120.7626
1537.1562 | 120.6207 | -120.4834 | 0.17853 | 0.0066373 | 0.013087 | 0.07612 | 0.0044838 | 0.06172 | -0.0039776 | -0.0025164 | 0.014572 | -0.0044988 | 0.059757 | 0.063164 | -0.0074897 | -0.0053149 | -0.10529 | -119.7006 | -8.3862 | -120.3323 | 0.18768 | -120.5109 | -120.3873 | -120.9137 | -0.58136 | -120.5429 | 0.07782 | 0.09613 | -120.4514 | -120.6299 | -0.027466 | 0.09613 | 0.009155 | 0.78278 | 0.15106 | 0.054932 | -0.28381 | 0.032043 | -0.14649 | -0.10071 | -0.4303 | -0.05951 | 0.086975 | -0.082398 | 120.6711 | 120.3781 | 112.0972 | -120.5658 | 120.5612 | 120.5795 | 119.902 | -120.8084
1538.8906 | 120.6573 | -120.3964 | 0.25635 | 0.0066373 | 0.01095 | 0.071848 | 0.0025612 | 0.063002 | 0.0060626 | -0.0012346 | -0.008316 | 0.00084176 | 0.061252 | 0.063591 | -0.0047125 | -0.0087329 | -0.059509 | -119.7144 | -8.5052 | -120.2225 | 0.28839 | -120.4605 | -120.3415 | -120.8771 | -0.6958 | -120.5475 | 0.19226 | 0.21515 | -120.3598 | -120.5566 | -0.064087 | 0.054931 | 0.032043 | 0.68207 | 0.17395 | 0.11902 | -0.31586 | 0.036621 | -0.16022 | -0.064087 | -0.48065 | -0.15106 | 0.009156 | -0.041199 | 120.6848 | 120.3369 | 111.8912 | -120.5978 | 120.5887 | 120.6116 | 119.7006 | -120.813
1540.6406 | 120.6207 | -120.0668 | 0.48065 | 0.021896 | 0.0086006 | 0.067362 | 0.005552 | 0.06172 | 0.0015766 | -0.0031574 | 0.0069425 | 0.0010554 | 0.061252 | 0.064232 | -0.0055671 | -0.0072375 | 0.23346 | -119.3207 | -8.3817 | -119.9203 | 0.52643 | -120.1263 | -120.0302 | -120.4926 | -0.5722 | -120.1859 | 0.41199 | 0.45776 | -120.0577 | -120.2774 | -0.05951 | 0.036621 | 0.045776 | 0.74615 | 0.14648 | 0.10986 | -0.24719 | 0.009155 | -0.21057 | -0.068665 | -0.42572 | -0.11902 | 0.091553 | -0.022888 | 120.5933 | 120.3003 | 111.6852 | -120.5109 | 120.4788 | 120.5246 | 119.4946 | -120.7581
1542.3281 | 120.607 | -120.52 | 0.17395 | 0.0066373 | 0.012446 | 0.073343 | 0.0044838 | 0.061293 | -0.002055 | -0.0020892 | 0.0069425 | -0.0053534 | 0.062107 | 0.065087 | -0.010694 | -0.0063831 | -0.068665 | -119.696 | -8.4457 | -120.3461 | 0.16022 | -120.4834 | -120.3918 | -120.9274 | -0.60883 | -120.5521 | 0.082397 | 0.10529 | -120.4742 | -120.6802 | 0.036622 | 0.12817 | -0.013733 | 0.82398 | 0.17395 | 0.045777 | -0.24261 | 0.045777 | -0.16022 | -0.091553 | -0.40741 | -0.032043 | 0.12817 | -0.068664 | 120.6802 | 120.4514 | 112.0743 | -120.5658 | 120.6024 | 120.6253 | 119.9112 | -120.8542
1544.0781 | 120.7535 | -120.5109 | 0.10986 | -0.00099167 | 0.0088142 | 0.071421 | 0.010252 | 0.062574 | -0.0044048 | -0.003371 | -0.008316 | -0.0036444 | 0.060398 | 0.061028 | -0.0094123 | -0.0053149 | -0.073242 | -119.6457 | -8.4412 | -120.314 | 0.1831 | -120.5429 | -120.4285 | -120.9091 | -0.52185 | -120.5338 | 0.068665 | 0.086975 | -120.4926 | -120.6848 | -0.032044 | 0.082397 | 0.073242 | 0.86517 | 0.19684 | 0.11444 | -0.18311 | 0.01831 | -0.17395 | -0.041198 | -0.39826 | -0.022888 | 0.15106 | -0.022888 | 120.694 | 120.4376 | 112.0697 | -120.5383 | 120.5795 | 120.5978 | 119.989 | -120.7947
1545.8281 | 120.6757 | -120.5841 | 0.16022 | -0.00099167 | 0.0090278 | 0.069071 | 0.0046976 | 0.059797 | 0.0022174 | -0.00038024 | 0.0069425 | -0.00086724 | 0.060825 | 0.065087 | -0.0057807 | -0.0098009 | -0.15564 | -119.8791 | -8.5831 | -120.4376 | 0.21515 | -120.5795 | -120.5154 | -121.0419 | -0.75989 | -120.7443 | 0.10529 | 0.1236 | -120.5292 | -120.7581 | 0.004577 | 0.068664 | 0.054932 | 0.70496 | 0.14648 | 0.07782 | -0.31586 | 0.054931 | -0.17395 | -0.054931 | -0.45776 | -0.16022 | 0.013733 | -0.036621 | 120.7993 | 120.4285 | 112.001 | -120.6757 | 120.6894 | 120.7077 | 119.8242 | -120.9183
1547.5781 | 120.4834 | -119.7144 | 0.83771 | -0.00099167 | 0.014368 | 0.07078 | 0.0040566 | 0.062147 | -0.002055 | -0.0014484 | -0.00068649 | -0.0030034 | 0.060184 | 0.062523 | -0.0083441 | -0.0059557 | 0.59509 | -118.8766 | -8.4091 | -119.5221 | 0.81482 | -119.7189 | -119.6091 | -120.0714 | -0.59052 | -119.7052 | 0.72327 | 0.74616 | -119.6823 | -119.8746 | -0.004578 | 0.10528 | -0.022889 | 0.83771 | 0.19226 | 0.086975 | -0.24262 | 0.032043 | -0.16022 | -0.11444 | -0.35706 | 0.009155 | 0.16937 | -0.091553 | 120.5292 | 120.3094 | 111.3052 | -120.4468 | 120.4376 | 120.4605 | 119.1238 | -120.7123
1549.3281 | 120.726 | -120.2499 | 0.28839 | 0.014267 | 0.019495 | 0.069284 | 0.0074746 | 0.062361 | 0.00050836 | -0.001021 | -0.00068649 | 0.0014826 | 0.063602 | 0.066368 | -0.0087713 | -0.0053149 | 0.018311 | -119.5724 | -8.6472 | -120.1401 | 0.37994 | -120.3369 | -120.2225 | -120.7214 | -0.737 | -120.4147 | 0.27924 | 0.29755 | -120.3094 | -120.4926 | -0.086975 | 0.027466 | 0.091553 | 0.67749 | 0.10986 | 0.082397 | -0.27008 | -0.059509 | -0.24262 | -0.009155 | -0.4715 | -0.16479 | 0.07782 | 0.009155 | 120.6299 | 120.2682 | 111.6028 | -120.5109 | 120.5292 | 120.5475 | 119.5129 | -120.7809
1551 | 120.7901 | -120.4926 | 0.13733 | -0.00099167 | 0.0064642 | 0.071634 | 0.0096108 | 0.059797 | -0.0046184 | -0.0029436 | -0.008316 | -0.0047124 | 0.060184 | 0.064019 | -0.010908 | -0.0055285 | -0.045776 | -119.6915 | -8.6334 | -120.3461 | 0.16022 | -120.5429 | -120.4514 | -120.8954 | -0.6546 | -120.5292 | 0.064087 | 0.09613 | -120.5063 | -120.6985 | -0.050354 | 0.041199 | 0.022888 | 0.80109 | 0.14648 | 0.10529 | -0.18311 | -0.013733 | -0.20599 | -0.073242 | -0.40283 | -0.036621 | 0.16937 | -0.041199 | 120.6528 | 120.4468 | 111.8591 | -120.5887 | 120.5566 | 120.5887 | 119.838 | -120.8359
1552.75 | 120.6619 | -120.488 | 0.21973 | -0.00099167 | 0.015864 | 0.070139 | 0.0029886 | 0.060865 | 0.002431 | -0.00059384 | 0.014572 | 0.00041436 | 0.059116 | 0.063378 | -0.0047125 | -0.0089465 | -0.054932 | -119.7418 | -8.7021 | -120.3232 | 0.25635 | -120.5338 | -120.4147 | -120.9 | -0.77362 | -120.6299 | 0.15106 | 0.17395 | -120.4834 | -120.694 | -0.045776 | 0.073242 | 0.036621 | 0.74616 | 0.16479 | 0.091553 | -0.27466 | 0.004578 | -0.20599 | -0.068665 | -0.41199 | -0.14191 | 0.064087 | -0.045777 | 120.7443 | 120.433 | 111.7859 | -120.6345 | 120.639 | 120.6619 | 119.7144 | -120.9137
1554.5 | 120.694 | -120.5887 | 0.15564 | 0.0066373 | -0.001867 | 0.072062 | 0.0017068 | 0.063002 | -0.003764 | -0.0031574 | 0.0069425 | -0.0023626 | 0.058475 | 0.062096 | -0.0079169 | -0.0053149 | -0.10986 | -119.7784 | -8.7891 | -120.4239 | 0.17853 | -120.5887 | -120.5109 | -121.0098 | -0.82398 | -120.639 | 0.059509 | 0.10071 | -120.5475 | -120.7626 | 0 | 0.07782 | 0.022888 | 0.81024 | 0.16479 | 0.086975 | -0.2655 | 0.041199 | -0.17395 | -0.096131 | -0.42114 | -0.050354 | 0.1236 | -0.054932 | 120.7672 | 120.4788 | 111.7996 | -120.6665 | 120.6482 | 120.6894 | 119.7647 | -120.9183
1556.1875 | 120.8084 | -120.5978 | 0.13275 | -0.00099167 | -0.00058523 | 0.073984 | 0.0057656 | 0.06172 | -0.006541 | -0.0042254 | -0.00068649 | -0.005567 | 0.05933 | 0.061882 | -0.0089849 | -0.0068103 | -0.14648 | -119.8242 | -8.8257 | -120.4376 | 0.18768 | -120.6024 | -120.4971 | -121.0052 | -0.8606 | -120.6299 | 0.082397 | 0.10529 | -120.5887 | -120.7809 | -0.004578 | 0.10071 | 0.054932 | 0.77362 | 0.16022 | 0.059509 | -0.27924 | 0.009155 | -0.18311 | -0.050354 | -0.40741 | -0.032044 | 0.15106 | -0.027465 | 120.7855 | 120.4514 | 111.7722 | -120.6299 | 120.6802 | 120.7031 | 119.7372 | -120.9137
1557.9219 | 120.7993 | -120.5841 | 0.14191 | -0.00099167 | 0.012873 | 0.074198 | 0.007261 | 0.064711 | -0.0024822 | -0.0052936 | 0.014572 | -0.00086724 | 0.060611 | 0.061669 | -0.0079169 | -0.0080921 | -0.086975 | -119.7876 | -8.8715 | -120.4239 | 0.16022 | -120.6299 | -120.5429 | -121.0464 | -0.79651 | -120.6985 | 0.091553 | 0.10529 | -120.6162 | -120.8176 | -0.045777 | 0.041198 | 0.01831 | 0.79651 | 0.16022 | 0.11902 | -0.22888 | -0.032044 | -0.23346 | -0.050354 | -0.46234 | -0.11444 | 0.11902 | -0.036621 | 120.7443 | 120.4971 | 111.7126 | -120.6848 | 120.6757 | 120.6894 | 119.7876 | -120.9595
1559.6562 | 120.8176 | -120.575 | 0.14648 | -0.00099167 | 0.013941 | 0.072062 | 0.0087564 | 0.06407 | -0.00034604 | -0.0055072 | -0.00068649 | -0.002149 | 0.063388 | 0.060601 | -0.010267 | -0.0074511 | -0.09613 | -119.8471 | -8.9676 | -120.4605 | 0.19226 | -120.6482 | -120.5612 | -121.0739 | -0.88806 | -120.726 | 0.12817 | 0.14191 | -120.6162 | -120.7993 | -0.073242 | 0.013733 | 0.045777 | 0.72784 | 0.11444 | 0.10071 | -0.24261 | -0.041199 | -0.2243 | -0.01831 | -0.49896 | -0.15106 | 0.073242 | -0.004577 | 120.7672 | 120.4788 | 111.6074 | -120.7077 | 120.7031 | 120.7169 | 119.6869 | -120.9457
1561.3438 | 120.726 | -120.6436 | 0.17853 | -0.00099167 | 0.0051826 | 0.071848 | 0.002134 | 0.060865 | -0.0026958 | -0.004439 | -0.008316 | -0.0036444 | 0.057621 | 0.061028 | -0.0074897 | -0.0072375 | -0.059509 | -119.8059 | -8.9813 | -120.433 | 0.16022 | -120.6299 | -120.5429 | -121.0281 | -0.89722 | -120.6757 | 0.064087 | 0.082397 | -120.6024 | -120.8084 | 0.013733 | 0.10071 | -0.018311 | 0.83771 | 0.21057 | 0.10986 | -0.23804 | 0.041199 | -0.1648 | -0.11444 | -0.38452 | -0.032043 | 0.13275 | -0.096131 | 120.8038 | 120.5841 | 111.6623 | -120.7214 | 120.7077 | 120.726 | 119.7464 | -120.9869
1563.0938 | 120.7352 | -120.639 | 0.16479 | -0.00099167 | 0.0092414 | 0.074198 | 0.0032022 | 0.060438 | -0.0031232 | -0.0025164 | -0.00068649 | -0.003858 | 0.061679 | 0.063805 | -0.0064215 | -0.0068103 | -0.036621 | -119.7876 | -9.0546 | -120.433 | 0.14648 | -120.6482 | -120.5429 | -121.0098 | -0.90179 | -120.694 | 0.064087 | 0.07782 | -120.5933 | -120.8038 | -0.009155 | 0.09613 | -0.018311 | 0.85144 | 0.20599 | 0.10986 | -0.20142 | 0.045776 | -0.16479 | -0.10071 | -0.37079 | -0.054932 | 0.10986 | -0.086975 | 120.7855 | 120.6024 | 111.5845 | -120.7077 | 120.7031 | 120.7169 | 119.7372 | -120.9686
1564.8281 | 120.7809 | -120.6573 | 0.16022 | -0.00099167 | 0.013727 | 0.070993 | 0.0046976 | 0.061506 | 0.0028584 | -0.001662 | -0.008316 | 0.00084176 | 0.061679 | 0.063805 | -0.0059943 | -0.0085193 | -0.14648 | -119.9844 | -9.2331 | -120.5383 | 0.20142 | -120.6894 | -120.5933 | -121.0968 | -1.0986 | -120.8267 | 0.10529 | 0.09613 | -120.6573 | -120.8359 | -0.032043 | 0.064087 | 0.041199 | 0.67291 | 0.11902 | 0.054932 | -0.3067 | 0 | -0.17853 | -0.054931 | -0.43945 | -0.16937 | 0.009155 | -0.064087 | 120.8588 | 120.5109 | 111.4243 | -120.7535 | 120.7626 | 120.7535 | 119.5587 | -120.9961
1566.5781 | 120.8313 | -120.5887 | 0.13275 | -0.00099167 | 0.013087 | 0.068644 | 0.0079018 | 0.063429 | -0.0022686 | -0.0037982 | 0.0069425 | -0.0019354 | 0.06232 | 0.063378 | -0.012189 | -0.0089465 | -0.068665 | -119.7968 | -9.1599 | -120.4559 | 0.16022 | -120.6665 | -120.5429 | -121.051 | -0.97504 | -120.7031 | 0.082397 | 0.11444 | -120.6482 | -120.8313 | -0.07782 | 0.045776 | 0.027466 | 0.79193 | 0.13275 | 0.086975 | -0.20142 | -0.059509 | -0.24262 | -0.050354 | -0.46234 | -0.11444 | 0.12817 | -0.01831 | 120.7489 | 120.52 | 111.4288 | -120.6757 | 120.6711 | 120.7031 | 119.6136 | -120.9641
1568.2656 | 120.8817 | -120.639 | 0.11444 | -0.0086212 | 0.0096686 | 0.07313 | 0.0087564 | 0.064924 | -0.0014142 | -0.0046526 | 0.0069425 | -0.0010808 | 0.061466 | 0.065514 | -0.0098395 | -0.0080921 | -0.16479 | -119.9249 | -9.3018 | -120.5429 | 0.21057 | -120.7123 | -120.6162 | -121.138 | -1.0895 | -120.7993 | 0.10529 | 0.12817 | -120.7031 | -120.8725 | -0.073242 | 0.022888 | 0.09613 | 0.71411 | 0.09613 | 0.073242 | -0.27924 | -0.064087 | -0.23346 | -0.009155 | -0.49896 | -0.16022 | 0.073243 | 0.013733 | 120.8496 | 120.4742 | 111.3373 | -120.7306 | 120.7443 | 120.7672 | 119.5496 | -120.9869
1570.0156 | 120.9091 | -120.6619 | 0.1236 | 0.0066373 | 0.010523 | 0.072062 | 0.0070474 | 0.061934 | 0.0015766 | -0.003371 | -0.00068649 | -0.0012946 | 0.061679 | 0.064873 | -0.0079169 | -0.0065967 | -0.16022 | -119.9661 | -9.375 | -120.5566 | 0.21973 | -120.726 | -120.607 | -121.1609 | -1.1307 | -120.8313 | 0.10529 | 0.12817 | -120.6848 | -120.8771 | -0.064087 | 0.054931 | 0.096131 | 0.6958 | 0.10528 | 0.050354 | -0.28381 | -0.022888 | -0.21515 | -0.01831 | -0.49896 | -0.16937 | 0.045776 | 0.004578 | 120.8817 | 120.5017 | 111.2869 | -120.7306 | 120.7672 | 120.7901 | 119.5312 | -121.0007
1571.7656 | 120.8084 | -120.6711 | 0.16022 | 0.0066373 | 0.00326 | 0.072916 | 0.0057656 | 0.063002 | -0.0031232 | -0.0035846 | -0.00068649 | -0.0042852 | 0.060398 | 0.062737 | -0.0085577 | -0.0059557 | -0.11902 | -119.8975 | -9.3933 | -120.5338 | 0.16937 | -120.6802 | -120.5933 | -121.106 | -1.1215 | -120.7489 | 0.068665 | 0.10071 | -120.6985 | -120.8588 | -0.009155 | 0.07782 | 0.009156 | 0.77362 | 0.13733 | 0.05951 | -0.27924 | -0.027465 | -0.18768 | -0.091552 | -0.43488 | -0.077819 | 0.10986 | -0.059509 | 120.8405 | 120.5521 | 111.2778 | -120.7535 | 120.7397 | 120.7718 | 119.5496 | -121.019
1573.5 | 120.9412 | -120.6619 | 0.11902 | 0.014267 | 0.0064642 | 0.072702 | 0.0053384 | 0.062361 | -0.0033368 | -0.003371 | -0.008316 | -0.0059942 | 0.060398 | 0.06231 | -0.011121 | -0.0078783 | -0.082397 | -119.8746 | -9.4162 | -120.5154 | 0.16937 | -120.6848 | -120.6116 | -121.0693 | -1.0712 | -120.7214 | 0.064087 | 0.082397 | -120.6894 | -120.8542 | -0.022888 | 0.050354 | 0.050354 | 0.78735 | 0.14648 | 0.09613 | -0.20142 | -0.027466 | -0.19226 | -0.054932 | -0.40741 | -0.05951 | 0.13275 | -0.036622 | 120.8313 | 120.5795 | 111.2457 | -120.7306 | 120.726 | 120.7443 | 119.5908 | -120.9732
1575.1875 | 120.8542 | -120.7077 | 0.16022 | -0.00099167 | 0.014155 | 0.069071 | 0.0044838 | 0.060438 | 0.0045674 | -0.001021 | 0.0069425 | 0.00062796 | 0.061039 | 0.064659 | -0.0036443 | -0.0068103 | -0.14648 | -120.0027 | -9.5581 | -120.5978 | 0.20599 | -120.7535 | -120.6573 | -121.1609 | -1.2772 | -120.8725 | 0.10529 | 0.13275 | -120.7489 | -120.9091 | -0.045776 | 0.050354 | 0.045777 | 0.70496 | 0.10986 | 0.05951 | -0.3067 | -0.041198 | -0.20142 | -0.054931 | -0.45319 | -0.16479 | 0.036621 | -0.027466 | 120.9137 | 120.5612 | 111.1496 | -120.8176 | 120.813 | 120.8405 | 119.4305 | -121.0693
1576.9531 | 120.9412 | -120.7123 | 0.15564 | 0.0066373 | 0.013087 | 0.070566 | 0.0085428 | 0.061506 | -0.0018414 | -0.00273 | -0.00068649 | -0.0010808 | 0.060825 | 0.063591 | -0.0087713 | -0.0078783 | -0.17395 | -119.9753 | -9.5535 | -120.6162 | 0.21057 | -120.8084 | -120.6665 | -121.2112 | -1.2268 | -120.8542 | 0.10529 | 0.11444 | -120.7535 | -120.932 | -0.096131 | 0.045776 | 0.054931 | 0.737 | 0.09613 | 0.050354 | -0.32959 | -0.041199 | -0.21973 | -0.050354 | -0.49896 | -0.14191 | 0.07782 | -0.041199 | 120.9229 | 120.5383 | 111.1588 | -120.8221 | 120.8176 | 120.8267 | 119.4855 | -121.0876
1578.6406 | 120.8405 | -120.7397 | 0.16022 | 0.014267 | 0.01565 | 0.067575 | 0.0046976 | 0.064283 | 0.0045674 | 0.00047416 | -0.008316 | -1.2844e-05 | 0.061252 | 0.064873 | -0.0047125 | -0.0085193 | -0.17853 | -120.0211 | -9.6359 | -120.5978 | 0.2243 | -120.726 | -120.6802 | -121.1884 | -1.3504 | -120.9045 | 0.09613 | 0.11444 | -120.7672 | -120.9503 | 0.013733 | 0.059509 | 0.064087 | 0.71869 | 0.14191 | 0.082398 | -0.33874 | -0.027466 | -0.21057 | -0.064087 | -0.44861 | -0.16479 | 0.045776 | -0.045776 | 120.9641 | 120.5612 | 111.1038 | -120.8405 | 120.8359 | 120.8542 | 119.3893 | -121.1105
1580.375 | 120.845 | -120.7443 | 0.16022 | -0.00099167 | 0.021204 | 0.06843 | 0.0053384 | 0.063002 | 0.0032856 | 0.00047416 | 0.014572 | -1.2844e-05 | 0.062534 | 0.066368 | -0.0055671 | -0.0070239 | -0.1236 | -119.9753 | -9.6588 | -120.5933 | 0.18768 | -120.7993 | -120.6482 | -121.1655 | -1.3641 | -120.9 | 0.082397 | 0.12817 | -120.7489 | -120.9503 | -0.054931 | 0.096131 | 0.027466 | 0.76904 | 0.15106 | 0.054931 | -0.28381 | -0.004577 | -0.20599 | -0.07782 | -0.42114 | -0.15564 | 0.050354 | -0.032043 | 120.932 | 120.6207 | 111.0855 | -120.8084 | 120.8267 | 120.8725 | 119.3802 | -121.1105
1582.125 | 120.9915 | -120.7306 | 0.14191 | 0.0066373 | 0.021418 | 0.068644 | 0.007261 | 0.063429 | 0.003072 | -0.0020892 | 0.0069425 | -0.0015082 | 0.061679 | 0.062096 | -0.0074897 | -0.0057421 | -0.15106 | -119.9524 | -9.7046 | -120.5978 | 0.21515 | -120.7901 | -120.6802 | -121.1746 | -1.3229 | -120.8405 | 0.09613 | 0.1236 | -120.7901 | -120.9595 | -0.059509 | 0.050354 | 0.073242 | 0.7782 | 0.13275 | 0.082398 | -0.29297 | -0.059509 | -0.22888 | -0.045777 | -0.44403 | -0.10986 | 0.11902 | -0.018311 | 120.9457 | 120.5795 | 111.026 | -120.8221 | 120.8267 | 120.8542 | 119.4077 | -121.1014
1583.8594 | 120.9045 | -120.7397 | 0.14648 | 0.0066373 | 0.023127 | 0.071848 | 0.0064066 | 0.061506 | 0.00029476 | -0.0020892 | -0.00068649 | -0.0027898 | 0.064029 | 0.063805 | -0.0072759 | -0.0065967 | -0.18768 | -120.0256 | -9.8145 | -120.6482 | 0.20142 | -120.8084 | -120.7031 | -121.2296 | -1.4923 | -120.8908 | 0.10986 | 0.10071 | -120.7764 | -120.9641 | -0.068665 | 0.036621 | 0.054932 | 0.71411 | 0.091553 | 0.054932 | -0.33417 | -0.036621 | -0.2243 | -0.036621 | -0.48981 | -0.15106 | 0.073242 | -0.045776 | 120.9412 | 120.5521 | 110.9253 | -120.8496 | 120.8496 | 120.8405 | 119.2474 | -121.1105
1585.5469 | 120.9641 | -120.7626 | 0.13733 | 0.0066373 | 0.004328 | 0.071207 | 0.0064066 | 0.063856 | -0.0035504 | -0.0029436 | 0.0069425 | -0.003858 | 0.05997 | 0.06295 | -0.0091985 | -0.0042467 | -0.1236 | -119.9112 | -9.7824 | -120.5841 | 0.16937 | -120.7855 | -120.6711 | -121.2158 | -1.3916 | -120.8588 | 0.091553 | 0.11444 | -120.7901 | -120.9595 | -0.022888 | 0.091552 | 0.032044 | 0.85144 | 0.17853 | 0.086976 | -0.26093 | -0.027466 | -0.19684 | -0.045776 | -0.45319 | -0.096131 | 0.10071 | -0.022888 | 120.932 | 120.639 | 110.9802 | -120.8084 | 120.8542 | 120.8771 | 119.371 | -121.0968
1587.3125 | 121.0052 | -120.726 | 0.13275 | -0.00099167 | 0.0098822 | 0.072275 | 0.00897 | 0.060438 | -0.005473 | -0.0046526 | -0.008316 | -0.0062078 | 0.060825 | 0.06295 | -0.012189 | -0.0076647 | -0.082397 | -119.8608 | -9.7824 | -120.5521 | 0.16937 | -120.7764 | -120.6573 | -121.1472 | -1.3504 | -120.7535 | 0.045776 | 0.073242 | -120.7443 | -120.9366 | -0.050354 | 0.068664 | 0.036622 | 0.86517 | 0.17395 | 0.10529 | -0.21515 | -0.018311 | -0.21057 | -0.086975 | -0.42114 | -0.027466 | 0.1831 | -0.059509 | 120.8954 | 120.6436 | 110.9436 | -120.7901 | 120.7718 | 120.7993 | 119.3756 | -121.0693
1589 | 120.9 | -120.7809 | 0.15564 | 0.0066373 | 0.011805 | 0.07078 | 0.0042702 | 0.063429 | 0.0032856 | -0.0018756 | 0.0069425 | 0.0016962 | 0.060184 | 0.064446 | -0.0055671 | -0.0074511 | -0.16937 | -120.0806 | -10.0479 | -120.6848 | 0.21515 | -120.845 | -120.7214 | -121.257 | -1.6159 | -120.9412 | 0.09613 | 0.12817 | -120.8038 | -120.9869 | -0.064087 | 0.059509 | 0.059509 | 0.70038 | 0.096131 | 0.036622 | -0.32501 | -0.022888 | -0.20599 | -0.05951 | -0.47607 | -0.16022 | 0.045776 | -0.027466 | 120.9961 | 120.6116 | 110.733 | -120.8771 | 120.8771 | 120.9091 | 119.165 | -121.1426
1590.75 | 120.9824 | -120.7718 | 0.13733 | -0.00099167 | 0.010737 | 0.072702 | 0.0070474 | 0.063215 | -0.002055 | -0.0031574 | 0.0069425 | -0.0040716 | 0.061679 | 0.062096 | -0.010908 | -0.0063831 | -0.091553 | -119.9249 | -9.9609 | -120.5978 | 0.17395 | -120.7855 | -120.6985 | -121.2158 | -1.506 | -120.8588 | 0.082397 | 0.09613 | -120.8038 | -120.9915 | -0.013732 | 0.073243 | 0.036621 | 0.84686 | 0.17395 | 0.10071 | -0.22888 | -0.032043 | -0.21973 | -0.054932 | -0.44403 | -0.086975 | 0.13275 | -0.041199 | 120.9457 | 120.6802 | 110.8109 | -120.8359 | 120.8542 | 120.8679 | 119.2657 | -121.1288
1592.5 | 121.0419 | -120.7443 | 0.11902 | 0.0066373 | 0.0088142 | 0.070566 | 0.005552 | 0.063002 | 0.0037128 | -0.00273 | 0.0069425 | -0.0010808 | 0.061679 | 0.065514 | -0.0085577 | -0.0078783 | -0.14191 | -120.0256 | -10.1212 | -120.6345 | 0.20142 | -120.8313 | -120.7397 | -121.2204 | -1.6113 | -120.9091 | 0.086975 | 0.1236 | -120.8221 | -120.9961 | -0.086975 | 0.004578 | 0.082397 | 0.71869 | 0.10986 | 0.10529 | -0.26093 | -0.07782 | -0.25177 | -0.032044 | -0.47607 | -0.16479 | 0.086975 | 0.004577 | 120.9457 | 120.6024 | 110.6232 | -120.8588 | 120.8313 | 120.8679 | 119.133 | -121.1151
1594.1875 | 121.0052 | -120.7764 | 0.13733 | -0.00099167 | 0.0092414 | 0.072916 | 0.0096108 | 0.063856 | -0.003764 | -0.0040118 | 0.0069425 | -0.0042852 | 0.061252 | 0.065087 | -0.010267 | -0.0061695 | -0.10071 | -119.9203 | -10.1074 | -120.6024 | 0.15106 | -120.8084 | -120.6894 | -121.2021 | -1.5976 | -120.8633 | 0.07782 | 0.091553 | -120.7993 | -120.9961 | -0.032044 | 0.086975 | 0.013733 | 0.85602 | 0.17395 | 0.086975 | -0.23804 | -0.022888 | -0.21973 | -0.059509 | -0.42572 | -0.086975 | 0.13275 | -0.045776 | 120.9274 | 120.6757 | 110.6689 | -120.8267 | 120.8542 | 120.8679 | 119.1788 | -121.1334
1595.9375 | 121.0602 | -120.7764 | 0.13733 | 0.0066373 | 0.0088142 | 0.069925 | 0.0076882 | 0.063643 | 0.00072196 | -0.0048662 | 0.0069425 | -0.00022644 | 0.060825 | 0.064659 | -0.0083441 | -0.0063831 | -0.13275 | -120.0485 | -10.2951 | -120.6528 | 0.21057 | -120.8725 | -120.7397 | -121.257 | -1.7029 | -120.9274 | 0.091553 | 0.10529 | -120.8221 | -121.0144 | -0.096131 | 0.036621 | 0.073242 | 0.72784 | 0.1236 | 0.086975 | -0.27008 | -0.045777 | -0.23804 | -0.045776 | -0.48065 | -0.15106 | 0.086975 | -0.032043 | 120.9869 | 120.6436 | 110.4813 | -120.8771 | 120.8679 | 120.8817 | 119.0735 | -121.1517
1597.6875 | 120.932 | -120.8267 | 0.15106 | 0.0066373 | 0.0096686 | 0.069712 | 0.0036294 | 0.062574 | 0.003072 | -0.0020892 | -0.00068649 | 0.001269 | 0.060611 | 0.063378 | -0.0044989 | -0.0080921 | -0.14648 | -120.1126 | -10.4004 | -120.7077 | 0.20599 | -120.8771 | -120.7489 | -121.2936 | -1.8173 | -120.9915 | 0.09613 | 0.10986 | -120.8313 | -121.019 | -0.050354 | 0.07782 | 0.054932 | 0.71411 | 0.11902 | 0.041198 | -0.29755 | -0.004578 | -0.19226 | -0.054932 | -0.46692 | -0.16479 | 0.027466 | -0.041199 | 121.0327 | 120.6802 | 110.4263 | -120.9 | 120.9229 | 120.9366 | 119.0094 | -121.17
1599.3906 | 121.0236 | -120.7993 | 0.12817 | -0.00099167 | 0.0092414 | 0.072702 | 0.010252 | 0.060438 | -0.0050458 | -0.0035846 | -0.00068649 | -0.0068488 | 0.05997 | 0.061455 | -0.01048 | -0.0055285 | -0.068665 | -119.9341 | -10.318 | -120.6253 | 0.14191 | -120.845 | -120.7306 | -121.2021 | -1.7258 | -120.8267 | 0.050354 | 0.086975 | -120.8176 | -120.9869 | -0.045777 | 0.068664 | 0.013733 | 0.86517 | 0.17395 | 0.10529 | -0.19684 | -0.018311 | -0.18768 | -0.07782 | -0.40283 | -0.027466 | 0.16022 | -0.041199 | 120.9412 | 120.7306 | 110.4813 | -120.8588 | 120.8496 | 120.8862 | 119.0735 | -121.1151
1601.125 | 120.9641 | -120.8359 | 0.17853 | 0.0066373 | 0.0079596 | 0.070139 | 0.0070474 | 0.062788 | 0.0017902 | -0.00273 | 0.0069425 | 0.0034052 | 0.061679 | 0.0653 | -0.0070623 | -0.0095873 | -0.091553 | -120.0531 | -10.4828 | -120.6802 | 0.20599 | -120.8633 | -120.7672 | -121.2662 | -1.8768 | -120.9732 | 0.10071 | 0.12817 | -120.8633 | -121.0373 | -0.027466 | 0.068664 | 0.027466 | 0.78278 | 0.15564 | 0.086975 | -0.27008 | -0.027466 | -0.20142 | -0.07782 | -0.4303 | -0.13733 | 0.064086 | -0.050354 | 121.0419 | 120.7443 | 110.3531 | -120.9457 | 120.9366 | 120.9641 | 118.959 | -121.2158
1602.9219 | 120.9412 | -120.8542 | 0.16479 | 0.0066373 | 0.011164 | 0.069925 | 0.0053384 | 0.061506 | -0.0050458 | -0.006148 | 0.0069425 | -0.0025762 | 0.058475 | 0.06295 | -0.010053 | -0.0048877 | -0.086975 | -119.9982 | -10.5377 | -120.6802 | 0.15564 | -120.845 | -120.726 | -121.2479 | -1.918 | -120.8908 | 0.068665 | 0.10529 | -120.8359 | -121.0281 | 0.009155 | 0.12817 | -0.009155 | 0.85602 | 0.17395 | 0.045776 | -0.25177 | 0.018311 | -0.17395 | -0.09613 | -0.39368 | -0.036621 | 0.13733 | -0.059509 | 121.0098 | 120.7672 | 110.3165 | -120.8908 | 120.9229 | 120.9595 | 118.9362 | -121.1929
1604.6562 | 121.051 | -120.8313 | 0.1236 | 0.0066373 | 0.0068916 | 0.07078 | 0.0064066 | 0.063856 | -0.0041912 | -0.0040118 | 0.0069425 | -0.0051398 | 0.060398 | 0.063164 | -0.010694 | -0.0080921 | -0.073242 | -119.9844 | -10.5194 | -120.6482 | 0.15564 | -120.8542 | -120.7443 | -121.2296 | -1.8814 | -120.8633 | 0.059509 | 0.10071 | -120.8176 | -121.0464 | -0.022888 | 0.086975 | 0.032044 | 0.84686 | 0.18311 | 0.096131 | -0.19684 | 0.013733 | -0.21515 | -0.064087 | -0.39825 | -0.032043 | 0.18311 | -0.022888 | 120.9869 | 120.7581 | 110.3119 | -120.8679 | 120.8908 | 120.932 | 118.9499 | -121.17
1606.3594 | 120.9641 | -120.8954 | 0.16022 | -0.0086212 | 0.0081732 | 0.069071 | 0.0023476 | 0.060438 | 0.0039264 | -0.001662 | 0.014572 | 0.00020076 | 0.060611 | 0.064659 | -0.0032171 | -0.0078783 | -0.16022 | -120.1492 | -10.8032 | -120.7489 | 0.21515 | -120.8817 | -120.7809 | -121.3211 | -2.1606 | -121.051 | 0.082397 | 0.11902 | -120.8954 | -121.0785 | 0.013733 | 0.11444 | 0.054932 | 0.74616 | 0.14648 | 0.032044 | -0.32043 | 0 | -0.1831 | -0.07782 | -0.42572 | -0.15564 | 0.027466 | -0.041198 | 121.1105 | 120.7352 | 110.0922 | -120.9412 | 120.9778 | 121.0144 | 118.7347 | -121.2387
1608.0625 | 121.0098 | -120.8771 | 0.14648 | -0.00099167 | 0.010096 | 0.073771 | 0.0049112 | 0.063643 | -0.0046184 | -0.0031574 | 0.014572 | -0.0062078 | 0.060825 | 0.063591 | -0.0096259 | -0.0051013 | -0.12817 | -120.0439 | -10.7666 | -120.7123 | 0.16937 | -120.9045 | -120.7672 | -121.2845 | -2.1423 | -120.9274 | 0.068665 | 0.10071 | -120.8771 | -121.0831 | -0.027466 | 0.10986 | 0.022889 | 0.83313 | 0.16479 | 0.054932 | -0.27466 | 0 | -0.20599 | -0.077819 | -0.40741 | -0.050354 | 0.15564 | -0.045776 | 121.0464 | 120.7489 | 110.1105 | -120.9137 | 120.9457 | 120.9778 | 118.7347 | -121.2296
1609.7656 | 120.9778 | -120.8862 | 0.15106 | 0.014267 | 0.012232 | 0.074839 | 0.0053384 | 0.062147 | -0.002055 | -0.0037982 | 0.014572 | -0.0051398 | 0.060611 | 0.062523 | -0.0064215 | -0.0068103 | -0.068665 | -119.9982 | -10.8215 | -120.6894 | 0.14648 | -120.8908 | -120.7764 | -121.2479 | -2.1332 | -120.9183 | 0.068665 | 0.068665 | -120.8542 | -121.0602 | -0.004578 | 0.10986 | -0.004578 | 0.88806 | 0.19684 | 0.086975 | -0.21973 | 0.032043 | -0.17395 | -0.082397 | -0.36163 | -0.032044 | 0.14191 | -0.082397 | 121.0327 | 120.8176 | 110.0647 | -120.9274 | 120.9549 | 120.9549 | 118.7531 | -121.2112
1611.5156 | 121.0968 | -120.845 | 0.1236 | 0.014267 | 0.006037 | 0.068857 | 0.0068338 | 0.063856 | 0.0032856 | -0.0040118 | 0.022202 | -0.00086724 | 0.061679 | 0.063164 | -0.0059943 | -0.0089465 | -0.07782 | -120.0714 | -10.9909 | -120.7077 | 0.20599 | -120.9183 | -120.8313 | -121.2753 | -2.1881 | -120.9961 | 0.11444 | 0.10529 | -120.9045 | -121.0876 | -0.073242 | 0.013733 | 0.082398 | 0.77362 | 0.13733 | 0.1236 | -0.20142 | -0.059509 | -0.24261 | -0.009155 | -0.4303 | -0.15106 | 0.091552 | -0.01831 | 121.051 | 120.7672 | 109.8541 | -120.9549 | 120.9595 | 120.9503 | 118.6569 | -121.2112
1613.2031 | 121.0281 | -120.8908 | 0.14648 | 0.0066373 | 0.012659 | 0.072702 | 0.0019204 | 0.062147 | -0.00055964 | -0.0029436 | 0.0069425 | -0.0042852 | 0.061466 | 0.063805 | -0.0072759 | -0.0078783 | -0.064087 | -119.9936 | -11.0733 | -120.6757 | 0.14648 | -120.8862 | -120.7809 | -121.2296 | -2.2522 | -120.9091 | 0.064087 | 0.068665 | -120.8862 | -121.0419 | 0.004578 | 0.10986 | 0 | 0.89722 | 0.21515 | 0.10529 | -0.21057 | 0.004578 | -0.15106 | -0.082397 | -0.33874 | -0.018311 | 0.13275 | -0.077819 | 121.0373 | 120.8267 | 109.8175 | -120.9274 | 120.9549 | 120.9595 | 118.6386 | -121.1884
1614.9062 | 121.138 | -120.8633 | 0.13733 | 0.0066373 | 0.0086006 | 0.069712 | 0.0083292 | 0.063643 | 0.0028584 | -0.001662 | 0.0069425 | -0.00022644 | 0.062534 | 0.064019 | -0.0072759 | -0.0063831 | -0.10529 | -120.0989 | -11.2106 | -120.7352 | 0.20142 | -120.9503 | -120.8267 | -121.3028 | -2.3575 | -121.0007 | 0.10071 | 0.10986 | -120.9091 | -121.1105 | -0.086975 | 0.036621 | 0.064087 | 0.76447 | 0.12817 | 0.091553 | -0.24262 | -0.045777 | -0.24719 | -0.036621 | -0.43945 | -0.13733 | 0.10986 | -0.027466 | 121.0648 | 120.7581 | 109.6527 | -120.9641 | 120.9641 | 120.9732 | 118.5059 | -121.2479
1616.625 | 121.0007 | -120.9183 | 0.15106 | -0.00099167 | 0.010523 | 0.074839 | 0.0046976 | 0.063856 | -0.0033368 | -0.0025164 | 0.0069425 | -0.0025762 | 0.058689 | 0.064659 | -0.0074897 | -0.0070239 | -0.07782 | -120.0165 | -11.1923 | -120.7123 | 0.14648 | -120.9 | -120.7764 | -121.2662 | -2.3849 | -120.9457 | 0.059509 | 0.10529 | -120.9137 | -121.0876 | 0.018311 | 0.14191 | -0.004578 | 0.90179 | 0.20599 | 0.064087 | -0.22888 | 0.004578 | -0.16937 | -0.091553 | -0.3479 | -0.027466 | 0.14191 | -0.045776 | 121.0648 | 120.8405 | 109.726 | -120.9274 | 120.9778 | 121.0236 | 118.5333 | -121.2387
1618.3281 | 121.0464 | -120.9091 | 0.15564 | 0.014267 | 0.012659 | 0.072062 | 0.002775 | 0.063643 | -0.002055 | -0.0012346 | 0.0069425 | -0.0047124 | 0.059543 | 0.06295 | -0.0057807 | -0.0085193 | -0.059509 | -120.0485 | -11.2381 | -120.6985 | 0.17395 | -120.9045 | -120.8221 | -121.2662 | -2.4307 | -120.9366 | 0.054932 | 0.068665 | -120.9183 | -121.0785 | 0.004578 | 0.086975 | 0.01831 | 0.8606 | 0.21057 | 0.1236 | -0.21515 | -0.009155 | -0.16937 | -0.10071 | -0.35706 | -0.027465 | 0.14191 | -0.086975 | 121.0831 | 120.8496 | 109.671 | -120.9778 | 120.9641 | 120.9778 | 118.4784 | -121.2341
1620.0312 | 121.1014 | -120.9 | 0.16937 | 0.0066373 | 0.0064642 | 0.070139 | 0.003843 | 0.066206 | 0.0020038 | -0.0012346 | 0.014572 | 0.00084176 | 0.061039 | 0.067009 | -0.0051397 | -0.0065967 | -0.07782 | -120.0897 | -11.3754 | -120.7626 | 0.21057 | -120.9366 | -120.8405 | -121.3394 | -2.536 | -121.0281 | 0.082397 | 0.12817 | -120.932 | -121.1197 | -0.036621 | 0.059509 | 0.041198 | 0.81024 | 0.13733 | 0.07782 | -0.24719 | -0.032044 | -0.21973 | -0.086976 | -0.43945 | -0.12817 | 0.091553 | -0.041199 | 121.1105 | 120.8221 | 109.5245 | -121.0098 | 120.9824 | 121.0281 | 118.364 | -121.2891
1621.75 | 121.1563 | -120.932 | 0.13275 | -0.00099167 | 0.0064642 | 0.072702 | 0.0066202 | 0.061506 | -0.00098684 | -0.003371 | -0.00068649 | -0.0023626 | 0.062748 | 0.063378 | -0.01048 | -0.0068103 | -0.1831 | -120.163 | -11.4716 | -120.8084 | 0.20599 | -120.9595 | -120.8679 | -121.4081 | -2.6367 | -121.0739 | 0.09613 | 0.1236 | -120.9595 | -121.1334 | -0.027466 | 0.064087 | 0.073243 | 0.76904 | 0.1236 | 0.059509 | -0.31586 | -0.027466 | -0.20142 | -0.036621 | -0.47607 | -0.14191 | 0.059509 | -0.009155 | 121.138 | 120.7489 | 109.4604 | -121.0007 | 121.0281 | 121.0556 | 118.2953 | -121.2662
1623.4844 | 121.1563 | -120.9366 | 0.10986 | -0.0086212 | 0.013087 | 0.075266 | 0.0076882 | 0.063215 | -0.007182 | -0.00508 | -0.00068649 | -0.0036444 | 0.059543 | 0.061669 | -0.012617 | -0.0053149 | -0.12817 | -120.0806 | -11.5448 | -120.7489 | 0.16937 | -120.9457 | -120.8496 | -121.3211 | -2.6779 | -120.9503 | 0.054932 | 0.091553 | -120.9457 | -121.1288 | -0.009156 | 0.086975 | 0.05951 | 0.85602 | 0.18768 | 0.10071 | -0.23804 | -0.009156 | -0.19226 | -0.054931 | -0.38452 | -0.013733 | 0.17853 | -0.01831 | 121.106 | 120.8084 | 109.3918 | -120.9595 | 120.9915 | 121.0281 | 118.2587 | -121.2387
1625.1562 | 121.0785 | -120.9549 | 0.13733 | -0.00099167 | 0.0086006 | 0.069284 | 0.0044838 | 0.063002 | 0.0052082 | -0.0020892 | 0.0069425 | -0.00022644 | 0.060825 | 0.065941 | -0.0066351 | -0.0080921 | -0.091553 | -120.1447 | -11.7233 | -120.7855 | 0.19684 | -120.9457 | -120.8817 | -121.3577 | -2.8839 | -121.0876 | 0.07782 | 0.10986 | -120.9732 | -121.1472 | 0.009155 | 0.073242 | 0.059509 | 0.81024 | 0.16937 | 0.096131 | -0.22888 | -0.018311 | -0.19226 | -0.059509 | -0.40283 | -0.13275 | 0.05951 | -0.027466 | 121.1517 | 120.8633 | 109.2316 | -121.019 | 121.0327 | 121.0648 | 118.071 | -121.2845
1626.8438 | 121.1517 | -120.932 | 0.1236 | 0.0066373 | 0.0079596 | 0.072062 | 0.0087564 | 0.058943 | 8.1158e-05 | -0.0031574 | 0.0069425 | -0.0019354 | 0.063175 | 0.063378 | -0.011121 | -0.0083057 | -0.18768 | -120.1584 | -11.9156 | -120.8176 | 0.20599 | -120.9961 | -120.8954 | -121.4081 | -2.9709 | -121.0785 | 0.10071 | 0.1236 | -121.0098 | -121.1563 | -0.064087 | 0.036621 | 0.082398 | 0.77362 | 0.11444 | 0.07782 | -0.31128 | -0.07782 | -0.2243 | -0.022888 | -0.47607 | -0.14648 | 0.07782 | 0 | 121.138 | 120.7443 | 109.0164 | -121.019 | 121.0327 | 121.0556 | 117.9611 | -121.2799
1628.5625 | 121.0785 | -120.9732 | 0.16022 | 0.0066373 | 0.0088142 | 0.070353 | 0.0057656 | 0.063429 | 0.0043536 | -0.0020892 | 0.0069425 | 0.00084176 | 0.061893 | 0.066796 | -0.0062079 | -0.0087329 | -0.10986 | -120.1401 | -11.9202 | -120.8084 | 0.18768 | -120.9824 | -120.8771 | -121.3852 | -3.0167 | -121.1014 | 0.091553 | 0.10529 | -120.9915 | -121.1655 | -0.009155 | 0.096131 | 0.027466 | 0.83313 | 0.16479 | 0.068664 | -0.27008 | -0.01831 | -0.19226 | -0.068664 | -0.41199 | -0.12817 | 0.064087 | -0.054931 | 121.1609 | 120.8633 | 109.053 | -121.0373 | 121.0648 | 121.0785 | 117.9565 | -121.3257
1630.25 | 121.0739 | -120.9915 | 0.17395 | 0.0066373 | 0.0090278 | 0.069925 | 0.0046976 | 0.062574 | 0.0026446 | -0.0020892 | 0.0069425 | -0.00086724 | 0.061039 | 0.0653 | -0.0053533 | -0.0078783 | -0.16479 | -120.195 | -11.998 | -120.8359 | 0.19684 | -120.9869 | -120.9 | -121.4264 | -3.1586 | -121.138 | 0.09613 | 0.11902 | -121.0007 | -121.1975 | 0.004578 | 0.091553 | 0.022888 | 0.79651 | 0.15564 | 0.064087 | -0.33874 | -0.009155 | -0.20599 | -0.07782 | -0.43488 | -0.14648 | 0.05951 | -0.054931 | 121.1884 | 120.8267 | 108.9935 | -121.0739 | 121.0876 | 121.1105 | 117.8329 | -121.3715
1631.9531 | 121.1838 | -120.9091 | 0.1236 | -0.00099167 | 0.010309 | 0.071421 | 0.0081154 | 0.063643 | -0.0050458 | -0.0046526 | 0.022202 | -0.0049262 | 0.061466 | 0.061669 | -0.0096259 | -0.0059557 | -0.09613 | -120.0256 | -11.9339 | -120.7672 | 0.16022 | -120.9778 | -120.8725 | -121.3486 | -2.98 | -120.9869 | 0.041199 | 0.082397 | -120.9686 | -121.1517 | -0.068664 | 0.036621 | 0.036621 | 0.88348 | 0.14191 | 0.10529 | -0.21973 | -0.059509 | -0.24261 | -0.082397 | -0.43945 | -0.077819 | 0.16479 | -0.041199 | 121.0693 | 120.813 | 108.9752 | -120.9961 | 120.9503 | 120.9915 | 117.9291 | -121.2753
1633.6875 | 121.257 | -120.9549 | 0.1236 | -0.00099167 | 0.0088142 | 0.070353 | 0.00897 | 0.06407 | 0.0034992 | -0.0023028 | 0.029831 | -1.2844e-05 | 0.062961 | 0.061882 | -0.0079169 | -0.010015 | -0.11902 | -120.1447 | -12.117 | -120.7993 | 0.19684 | -121.0144 | -120.9045 | -121.3715 | -3.2181 | -121.0693 | 0.10529 | 0.10986 | -121.0373 | -121.1929 | -0.059509 | 0.050354 | 0.073242 | 0.81024 | 0.15564 | 0.10529 | -0.24261 | -0.082397 | -0.23804 | -0.01831 | -0.41657 | -0.11444 | 0.1236 | -0.013733 | 121.1517 | 120.8359 | 108.8379 | -121.0281 | 121.0602 | 121.0648 | 117.7368 | -121.3165
1635.4688 | 121.225 | -120.9549 | 0.1236 | -0.00099167 | 0.010096 | 0.073771 | 0.010679 | 0.060865 | -0.0059002 | -0.00508 | 0.0069425 | -0.0064214 | 0.061466 | 0.061882 | -0.012403 | -0.0042467 | -0.086975 | -120.0439 | -12.1124 | -120.7672 | 0.16022 | -120.9869 | -120.8862 | -121.3257 | -3.1677 | -120.9686 | 0.050354 | 0.086975 | -120.9824 | -121.1838 | -0.032043 | 0.068665 | 0.036621 | 0.91095 | 0.18768 | 0.11902 | -0.21057 | -0.027466 | -0.22888 | -0.073242 | -0.37079 | -0.013733 | 0.21515 | -0.036621 | 121.1151 | 120.8679 | 108.8425 | -121.0098 | 121.0052 | 121.0419 | 117.7872 | -121.3074
1637.1719 | 121.0968 | -120.9778 | 0.15564 | -0.0086212 | 0.011378 | 0.068216 | 0.0070474 | 0.063643 | -0.0012006 | -0.00038024 | 0.0069425 | -0.0032172 | 0.060825 | 0.064232 | -0.0062079 | -0.0089465 | -0.064087 | -120.0851 | -12.2772 | -120.7626 | 0.15106 | -120.9824 | -120.8725 | -121.3257 | -3.3463 | -121.0098 | 0.050354 | 0.082397 | -120.9869 | -121.1792 | -0.004578 | 0.10529 | -0.004578 | 0.89264 | 0.21515 | 0.10986 | -0.21973 | -0.009155 | -0.20142 | -0.10529 | -0.3479 | -0.032044 | 0.16937 | -0.073243 | 121.1288 | 120.9137 | 108.7006 | -121.0281 | 121.0281 | 121.0602 | 117.6315 | -121.3348
1638.8594 | 121.1197 | -121.0236 | 0.17853 | 0.0066373 | 0.0083868 | 0.07078 | 0.005552 | 0.063856 | 0.0054218 | -0.0025164 | -0.00068649 | 0.00062796 | 0.062534 | 0.064446 | -0.0077033 | -0.0070239 | -0.12817 | -120.2087 | -12.5153 | -120.8496 | 0.19226 | -121.0327 | -120.9274 | -121.431 | -3.5385 | -121.1655 | 0.10986 | 0.11902 | -121.0052 | -121.2112 | -0.009155 | 0.096131 | 0.013733 | 0.81482 | 0.17395 | 0.07782 | -0.3067 | 0.018311 | -0.18768 | -0.068665 | -0.40741 | -0.14191 | 0.045777 | -0.059509 | 121.2158 | 120.8954 | 108.5083 | -121.106 | 121.1334 | 121.1426 | 117.485 | -121.3898
1640.5938 | 121.1288 | -121.0236 | 0.16479 | 0.0066373 | 0.0083868 | 0.070566 | 0.0044838 | 0.061506 | 0.0026446 | -0.00038024 | -0.008316 | -0.0017218 | 0.060398 | 0.0653 | -0.0077033 | -0.0068103 | -0.16479 | -120.2728 | -12.5977 | -120.8908 | 0.20599 | -121.0419 | -120.9137 | -121.4493 | -3.5706 | -121.1792 | 0.07782 | 0.11902 | -121.0464 | -121.225 | -0.01831 | 0.10986 | 0.041199 | 0.75073 | 0.13275 | 0.022888 | -0.32959 | -0.022888 | -0.20142 | -0.086975 | -0.42572 | -0.15564 | 0.045777 | -0.045776 | 121.2296 | 120.8588 | 108.4259 | -121.0785 | 121.1014 | 121.1426 | 117.453 | -121.3898
1642.3438 | 121.1929 | -120.9869 | 0.14191 | 0.0066373 | 0.011164 | 0.072275 | 0.0079018 | 0.061506 | -0.0052594 | -0.0025164 | 0.0069425 | -0.0032172 | 0.060611 | 0.062096 | -0.0094123 | -0.0072375 | -0.10529 | -120.1263 | -12.529 | -120.8267 | 0.15564 | -121.0327 | -120.9045 | -121.431 | -3.5431 | -121.0876 | 0.07782 | 0.10986 | -121.019 | -121.2204 | -0.045777 | 0.082397 | 0.013733 | 0.86059 | 0.16022 | 0.07782 | -0.24719 | -0.032044 | -0.23346 | -0.064087 | -0.44403 | -0.10071 | 0.13275 | -0.032044 | 121.1426 | 120.8817 | 108.4579 | -121.0464 | 121.0648 | 121.0968 | 117.4438 | -121.3623
1644.0938 | 121.1746 | -121.0327 | 0.16022 | 0.0066373 | 0.0090278 | 0.069925 | 0.0051248 | 0.064283 | 0.002431 | -0.0025164 | 0.0069425 | 0.00020076 | 0.060611 | 0.063805 | -0.0042853 | -0.0057421 | -0.16022 | -120.2591 | -12.7533 | -120.8817 | 0.19226 | -121.0648 | -120.9412 | -121.4584 | -3.7079 | -121.1609 | 0.10071 | 0.11902 | -121.0464 | -121.2112 | -0.032043 | 0.091553 | 0.032044 | 0.77362 | 0.15106 | 0.059509 | -0.32043 | -0.013733 | -0.17853 | -0.059509 | -0.42572 | -0.12817 | 0.050354 | -0.041198 | 121.225 | 120.8725 | 108.2794 | -121.1014 | 121.1334 | 121.1517 | 117.3248 | -121.3715
1645.7656 | 121.2479 | -120.9686 | 0.12817 | -0.0086212 | 0.012446 | 0.072916 | 0.0061928 | 0.062574 | -0.0076092 | -0.00508 | 0.0069425 | -0.0059942 | 0.060398 | 0.060173 | -0.011335 | -0.0053149 | -0.11902 | -120.1401 | -12.7396 | -120.8359 | 0.15564 | -121.019 | -120.9045 | -121.3898 | -3.6987 | -121.0144 | 0.050354 | 0.10986 | -121.0144 | -121.2112 | -0.050354 | 0.064087 | 0.027466 | 0.82855 | 0.13275 | 0.068665 | -0.24719 | -0.045776 | -0.24262 | -0.07782 | -0.42114 | -0.045776 | 0.19684 | -0.018311 | 121.1243 | 120.8496 | 108.2291 | -121.0327 | 121.019 | 121.0785 | 117.2699 | -121.3394
1647.5 | 121.2708 | -120.9686 | 0.10986 | 0.0066373 | 0.0062506 | 0.068003 | 0.0096108 | 0.065992 | 0.0028584 | -0.0042254 | -0.00068649 | -0.00022644 | 0.061466 | 0.064659 | -0.0083441 | -0.010869 | -0.11444 | -120.1904 | -12.8128 | -120.8633 | 0.19684 | -121.0739 | -120.9641 | -121.4127 | -3.6987 | -121.1151 | 0.082397 | 0.10529 | -121.0693 | -121.2433 | -0.10529 | 0.004578 | 0.086975 | 0.7782 | 0.10529 | 0.10071 | -0.2243 | -0.10071 | -0.27466 | -0.027466 | -0.44403 | -0.14648 | 0.12817 | -0.004577 | 121.1655 | 120.8542 | 108.1558 | -121.0739 | 121.051 | 121.0739 | 117.2699 | -121.3531
1649.1875 | 121.2662 | -120.9961 | 0.12817 | 0.014267 | 0.0098822 | 0.075693 | 0.011747 | 0.061506 | -0.0052594 | -0.0042254 | 0.0069425 | -0.0034308 | 0.062107 | 0.061669 | -0.011762 | -0.0057421 | -0.068665 | -120.0714 | -12.7808 | -120.813 | 0.17853 | -121.0464 | -120.9229 | -121.3623 | -3.6896 | -121.019 | 0.050354 | 0.091553 | -121.0648 | -121.2158 | -0.050354 | 0.073242 | 0.050354 | 0.92468 | 0.18311 | 0.10986 | -0.19684 | -0.068664 | -0.21973 | -0.07782 | -0.36621 | -0.022888 | 0.19684 | -0.036621 | 121.1746 | 120.9274 | 108.2153 | -121.051 | 121.0464 | 121.0876 | 117.3065 | -121.344
1650.9375 | 121.1884 | -121.0464 | 0.15106 | 0.014267 | 0.011805 | 0.072062 | 0.0068338 | 0.061293 | 0.0028584 | -0.0037982 | 0.014572 | -1.2844e-05 | 0.060611 | 0.062737 | -0.0070623 | -0.0065967 | -0.15564 | -120.2682 | -13.06 | -120.9137 | 0.21057 | -121.0556 | -121.0007 | -121.4859 | -3.9642 | -121.1746 | 0.091553 | 0.11902 | -121.0739 | -121.2616 | -0.009155 | 0.045777 | 0.059509 | 0.7782 | 0.13275 | 0.086975 | -0.3067 | -0.027466 | -0.21515 | -0.059509 | -0.43945 | -0.12817 | 0.086975 | -0.032043 | 121.257 | 120.8908 | 107.9864 | -121.1517 | 121.138 | 121.1655 | 117.0822 | -121.4127
1652.625 | 121.2021 | -121.0556 | 0.15564 | -0.0086212 | 0.009455 | 0.070566 | 0.0049112 | 0.061934 | 0.0015766 | -0.0014484 | -0.00068649 | -0.0025762 | 0.062107 | 0.064659 | -0.0059943 | -0.0065967 | -0.16022 | -120.2591 | -13.0783 | -120.9229 | 0.20142 | -121.0648 | -120.9778 | -121.463 | -4.0649 | -121.17 | 0.10986 | 0.11444 | -121.0876 | -121.2479 | -0.009155 | 0.07782 | 0.045776 | 0.79651 | 0.13275 | 0.054931 | -0.31586 | -0.032043 | -0.19226 | -0.045777 | -0.40741 | -0.11444 | 0.07782 | -0.041199 | 121.257 | 120.8954 | 107.9773 | -121.1334 | 121.1655 | 121.17 | 116.9907 | -121.4035
1654.3594 | 121.1609 | -121.0693 | 0.16479 | -0.0086212 | 0.010309 | 0.067789 | 0.0076882 | 0.06407 | 0.0022174 | -0.0014484 | -0.008316 | -1.2844e-05 | 0.05997 | 0.064019 | -0.0038581 | -0.0055285 | -0.16937 | -120.2591 | -13.1607 | -120.9274 | 0.20599 | -121.0922 | -120.9824 | -121.5088 | -4.1245 | -121.2341 | 0.091553 | 0.11444 | -121.0922 | -121.2799 | -0.022888 | 0.086975 | 0.041199 | 0.81024 | 0.14191 | 0.054932 | -0.33417 | -0.022888 | -0.21057 | -0.073242 | -0.43945 | -0.16479 | 0.045776 | -0.050354 | 121.2753 | 120.9 | 107.9086 | -121.1472 | 121.1609 | 121.1838 | 116.9449 | -121.4447
1656.0938 | 121.2708 | -121.0281 | 0.1236 | 0.014267 | 0.012232 | 0.073771 | 0.010038 | 0.060865 | -0.006541 | -0.0023028 | 0.0069425 | -0.0064214 | 0.061039 | 0.063591 | -0.01048 | -0.0038195 | -0.15106 | -120.1859 | -13.1882 | -120.8771 | 0.17395 | -121.0693 | -120.9869 | -121.4401 | -4.1199 | -121.0739 | 0.059509 | 0.082397 | -121.0648 | -121.2479 | -0.041199 | 0.041199 | 0.050354 | 0.84229 | 0.15106 | 0.10986 | -0.27466 | -0.036621 | -0.21973 | -0.064087 | -0.41199 | -0.045777 | 0.17395 | -0.041199 | 121.2021 | 120.8771 | 107.84 | -121.1105 | 121.0876 | 121.1105 | 116.9083 | -121.3715
1657.7812 | 121.1975 | -121.0648 | 0.16022 | 0.0066373 | 0.010523 | 0.07078 | 0.0061928 | 0.064283 | 0.0037128 | -0.0025164 | 0.014572 | -1.2844e-05 | 0.061679 | 0.065941 | -0.0066351 | -0.0087329 | -0.16022 | -120.3278 | -13.3026 | -120.9686 | 0.19684 | -121.0876 | -120.9961 | -121.4951 | -4.2801 | -121.225 | 0.10529 | 0.12817 | -121.0464 | -121.2891 | -0.022888 | 0.068664 | 0.036621 | 0.737 | 0.09613 | 0.027466 | -0.32043 | 0.01831 | -0.2243 | -0.054931 | -0.4303 | -0.16022 | 0.064086 | -0.032043 | 121.2616 | 120.9045 | 107.7621 | -121.1563 | 121.17 | 121.1929 | 116.7847 | -121.4493
1659.5312 | 121.1975 | -121.106 | 0.17395 | -0.00099167 | 0.0092414 | 0.071207 | 0.0059792 | 0.064283 | 0.0032856 | -0.0025164 | -0.008316 | 0.0014826 | 0.062107 | 0.066155 | -0.0049261 | -0.0076647 | -0.1236 | -120.2545 | -13.3484 | -120.9183 | 0.20142 | -121.1151 | -121.019 | -121.4996 | -4.2755 | -121.225 | 0.10071 | 0.13275 | -121.0968 | -121.3074 | -0.009155 | 0.086975 | 0.027466 | 0.85144 | 0.18768 | 0.10071 | -0.29755 | 0.009155 | -0.20142 | -0.073242 | -0.39368 | -0.11902 | 0.082397 | -0.041199 | 121.3074 | 120.9824 | 107.7576 | -121.1929 | 121.2067 | 121.2387 | 116.8304 | -121.4813
1661.2188 | 121.1884 | -121.0876 | 0.16937 | 0.014267 | 0.01095 | 0.071421 | 0.0036294 | 0.063215 | -0.0031232 | -0.0029436 | 0.014572 | -0.0036444 | 0.05997 | 0.06295 | -0.0085577 | -0.0065967 | -0.07782 | -120.1401 | -13.3713 | -120.8633 | 0.15106 | -121.0693 | -120.9824 | -121.4035 | -4.2892 | -121.106 | 0.050354 | 0.064087 | -121.0648 | -121.2433 | 0.01831 | 0.10529 | -0.018311 | 0.94757 | 0.2243 | 0.11902 | -0.24719 | 0.022888 | -0.15564 | -0.11902 | -0.31586 | -0.018311 | 0.13733 | -0.10529 | 121.2387 | 121.0098 | 107.7164 | -121.1517 | 121.138 | 121.1517 | 116.7984 | -121.4127
1662.9688 | 121.2524 | -121.0739 | 0.13275 | -0.00099167 | 0.0047552 | 0.069071 | 0.0066202 | 0.061934 | 0.0015766 | -0.0029436 | -0.00068649 | -0.00086724 | 0.061252 | 0.0653 | -0.0070623 | -0.0085193 | -0.086975 | -120.2271 | -13.4262 | -120.9 | 0.1831 | -121.1014 | -121.0144 | -121.4767 | -4.3213 | -121.1975 | 0.086975 | 0.11444 | -121.1243 | -121.2616 | -0.027465 | 0.05951 | 0.050354 | 0.84686 | 0.17395 | 0.11444 | -0.21973 | -0.050354 | -0.18768 | -0.045776 | -0.40283 | -0.1236 | 0.064087 | -0.01831 | 121.257 | 120.9869 | 107.6477 | -121.1472 | 121.1609 | 121.1884 | 116.7526 | -121.3943
1664.6562 | 121.3165 | -121.0602 | 0.11902 | 0.0066373 | 0.009455 | 0.068216 | 0.0096108 | 0.064283 | 0.00029476 | -0.0031574 | 0.0069425 | -1.2844e-05 | 0.063388 | 0.064019 | -0.010267 | -0.0080921 | -0.13733 | -120.2728 | -13.5315 | -120.9091 | 0.20599 | -121.1197 | -121.0373 | -121.4951 | -4.4266 | -121.1884 | 0.09613 | 0.091553 | -121.1105 | -121.2982 | -0.059509 | 0.022889 | 0.086975 | 0.78735 | 0.15106 | 0.12817 | -0.25635 | -0.050354 | -0.23804 | -0.022889 | -0.43488 | -0.12817 | 0.10986 | -0.027466 | 121.2662 | 120.9229 | 107.5287 | -121.1563 | 121.1563 | 121.1517 | 116.6336 | -121.4172
1666.3906 | 121.1975 | -121.1288 | 0.16022 | 0.014267 | 0.0083868 | 0.068003 | 0.0034158 | 0.061506 | 0.00072196 | -0.00080744 | -0.00068649 | -0.00022644 | 0.062961 | 0.067009 | -0.0079169 | -0.0070239 | -0.1236 | -120.2637 | -13.6963 | -120.9457 | 0.20142 | -121.1288 | -121.0373 | -121.5042 | -4.5959 | -121.2524 | 0.086975 | 0.13275 | -121.1334 | -121.3028 | 0 | 0.091553 | 0.041199 | 0.86517 | 0.1831 | 0.091552 | -0.28381 | -0.004578 | -0.17395 | -0.073242 | -0.37537 | -0.1236 | 0.050354 | -0.027466 | 121.3303 | 121.0052 | 107.4326 | -121.1975 | 121.2158 | 121.2616 | 116.5329 | -121.463
1668.1406 | 121.3028 | -121.0648 | 0.1236 | 0.014267 | 0.010737 | 0.074839 | 0.0087564 | 0.062574 | -0.0059002 | -0.00508 | 0.0069425 | -0.0077032 | 0.060825 | 0.063164 | -0.011335 | -0.0048877 | -0.17395 | -120.2179 | -13.7833 | -120.9183 | 0.17853 | -121.1105 | -121.0144 | -121.4905 | -4.5914 | -121.1243 | 0.064087 | 0.082397 | -121.1197 | -121.2891 | -0.045777 | 0.050354 | 0.054932 | 0.84686 | 0.14648 | 0.09613 | -0.29755 | -0.054932 | -0.2243 | -0.059509 | -0.42572 | -0.05951 | 0.16479 | -0.041199 | 121.2433 | 120.8908 | 107.2815 | -121.138 | 121.1288 | 121.1472 | 116.4734 | -121.4127
1669.8906 | 121.2616 | -121.1014 | 0.13733 | -0.00099167 | -0.0033624 | 0.073771 | 0.0046976 | 0.06407 | -0.0029094 | -0.0052936 | 0.0069425 | -0.0044988 | 0.056766 | 0.066582 | -0.011121 | -0.0076647 | -0.14191 | -120.2408 | -13.884 | -120.9274 | 0.16479 | -121.1197 | -121.0327 | -121.4859 | -4.7699 | -121.1288 | 0.07782 | 0.10071 | -121.1243 | -121.312 | -0.018311 | 0.068664 | 0.027466 | 0.86059 | 0.17395 | 0.10529 | -0.27924 | -0.022889 | -0.21057 | -0.059509 | -0.38452 | -0.027466 | 0.18311 | -0.036621 | 121.2662 | 120.9595 | 107.2174 | -121.17 | 121.1792 | 121.2021 | 116.3315 | -121.4493
1671.5781 | 121.2479 | -121.1151 | 0.15564 | 0.0066373 | 0.01095 | 0.070566 | 0.0034158 | 0.061506 | 0.0034992 | -0.00273 | 0.0069425 | -0.00065364 | 0.060398 | 0.066155 | -0.0062079 | -0.0068103 | -0.14648 | -120.3369 | -14.0396 | -120.9824 | 0.21515 | -121.1517 | -121.0693 | -121.5363 | -4.9713 | -121.257 | 0.10071 | 0.13733 | -121.1243 | -121.3074 | -0.036621 | 0.045776 | 0.059509 | 0.7782 | 0.13275 | 0.086975 | -0.30212 | -0.009156 | -0.19226 | -0.054932 | -0.42114 | -0.14191 | 0.050354 | -0.018311 | 121.3303 | 120.9686 | 107.0755 | -121.225 | 121.2158 | 121.2524 | 116.1438 | -121.463
1673.3125 | 121.3486 | -121.0831 | 0.11444 | -0.016251 | 0.0019782 | 0.07313 | 0.0070474 | 0.062361 | -0.0046184 | -0.0059344 | 0.0069425 | -0.0047124 | 0.061039 | 0.063591 | -0.010908 | -0.0070239 | -0.10986 | -120.2042 | -14.0533 | -120.9274 | 0.17395 | -121.1197 | -121.0144 | -121.463 | -4.9255 | -121.106 | 0.054932 | 0.082397 | -121.1517 | -121.2982 | -0.036621 | 0.068665 | 0.059509 | 0.87891 | 0.15564 | 0.086975 | -0.2243 | -0.068664 | -0.21515 | -0.059509 | -0.37994 | -0.022888 | 0.19226 | -0.032044 | 121.257 | 120.9732 | 107.0297 | -121.1288 | 121.138 | 121.1655 | 116.1575 | -121.4127
1675.0625 | 121.3074 | -121.1197 | 0.13733 | 0.0066373 | 0.0092414 | 0.072702 | 0.0085428 | 0.062361 | -0.00055964 | -0.0037982 | 0.0069425 | -0.0030034 | 0.06232 | 0.063164 | -0.0077033 | -0.0057421 | -0.13275 | -120.2499 | -14.1403 | -120.9549 | 0.16937 | -121.138 | -121.0464 | -121.5408 | -5.1315 | -121.2387 | 0.10986 | 0.11902 | -121.1929 | -121.3348 | -0.01831 | 0.073242 | 0.032044 | 0.86975 | 0.1648 | 0.091553 | -0.27008 | -0.073242 | -0.21515 | -0.027466 | -0.42114 | -0.11902 | 0.096131 | -0.01831 | 121.2891 | 120.9869 | 106.9794 | -121.1838 | 121.2296 | 121.2387 | 115.9882 | -121.4722
1676.75 | 120.9961 | -119.7601 | 1.1902 | 0.0066373 | 0.009455 | 0.071421 | 0.005552 | 0.063643 | 0.0017902 | -0.0012346 | 0.0069425 | -0.00022644 | 0.061466 | 0.064659 | -0.0049261 | -0.0070239 | 0.91553 | -118.9728 | -14.0533 | -119.6594 | 1.2497 | -119.8013 | -119.696 | -120.1767 | -5.2826 | -119.9203 | 1.1398 | 1.1627 | -119.8196 | -119.9799 | -0.041199 | 0.064087 | 0.059509 | 0.78735 | 0.10071 | 0.036621 | -0.27466 | -0.059509 | -0.21973 | -0.050354 | -0.41657 | -0.16022 | 0.059509 | -0.027466 | 121.0098 | 120.6757 | 105.7068 | -120.8862 | 120.9 | 120.9229 | 114.4775 | -121.17
1678.5 | 120.4651 | -5.2414 | 115.4022 | 0.0066373 | 0.013087 | 0.073343 | 0.0068338 | 0.060438 | -0.0039776 | -0.0031574 | -0.00068649 | -0.006635 | 0.061252 | 0.061669 | -0.013044 | -0.0076647 | 114.5004 | -5.5069 | 9.7412 | -5.4382 | 114.7339 | -6.0791 | -5.7037 | -5.2963 | 3.772 | -5.6534 | 114.6927 | 114.7247 | -5.8228 | -5.6488 | -0.83771 | -0.46234 | -0.66833 | -0.2655 | -0.19684 | 0.2655 | -0.90179 | -0.58136 | -0.40741 | -0.70953 | -0.054932 | -0.41199 | -0.004577 | -0.67749 | 119.9753 | 119.7418 | 14.9826 | -121.106 | 119.9341 | 119.9661 | 9.0134 | -121.051
1680.2344 | 120.8038 | -3.8315 | 116.9449 | -0.00099167 | 0.009455 | 0.070139 | 0.0042702 | 0.061934 | 0.003072 | -0.0042254 | -0.00068649 | 0.00062796 | 0.062961 | 0.064659 | -0.0074897 | -0.010228 | 116.7206 | -3.5156 | 11.1603 | -3.6392 | 116.9952 | -3.8498 | -3.9322 | -3.5751 | 4.6188 | -3.7537 | 116.9907 | 117.0456 | -3.7354 | -3.7765 | -0.01831 | -0.10071 | 0.050354 | 0.31586 | 0.19226 | 0.29297 | -0.2243 | 0.09613 | 0.054932 | 0.045777 | 0.25635 | 0.07782 | 0.022888 | 0.10071 | 120.8267 | 120.5521 | 14.9918 | -120.8771 | 120.8221 | 120.8771 | 8.4503 | -120.7214
1681.9844 | 120.7718 | -2.7512 | 118.158 | 0.0066373 | 0.015223 | 0.072702 | 0.0017068 | 0.061934 | 0.0017902 | -0.0035846 | -0.00068649 | -0.0030034 | 0.05997 | 0.062523 | -0.0059943 | -0.0070239 | 117.1921 | -2.5131 | 12.7762 | -2.5497 | 117.8284 | -3.0624 | -3.0991 | -2.4902 | 5.7861 | -2.6871 | 118.1763 | 118.2495 | -2.5589 | -2.6276 | -0.31128 | -0.3479 | -0.32959 | 0.23804 | 0.20142 | 0.54932 | -0.96588 | 0.19226 | 0.1236 | 0.018311 | 0.26093 | 0.064087 | -0.05951 | 0.091553 | 120.5795 | 119.9432 | 15.5273 | -121.257 | 120.9274 | 121.0007 | 8.5373 | -120.7855
1683.6719 | 120.9732 | -4.1153 | 116.748 | -0.00099167 | 0.0071052 | 0.073984 | 0.005552 | 0.063429 | -0.00098684 | -0.0025164 | 0.0069425 | -0.003858 | 0.060611 | 0.062737 | -0.010053 | -0.0070239 | 116.4185 | -3.9551 | 11.1923 | -3.9551 | 116.8991 | -4.0146 | -4.1199 | -3.9185 | 4.7974 | -4.0878 | 116.922 | 116.9266 | -3.9871 | -4.0237 | 0.10071 | -0.004578 | 0.15106 | 0.16022 | 0.16022 | 0.1648 | -0.32959 | 0.12817 | 0.091552 | 0.17395 | 0.19684 | 0.027465 | -0.064087 | 0.17853 | 121.0144 | 120.5338 | 15.3076 | -120.8679 | 121.0373 | 121.0419 | 8.9127 | -120.7718
1685.4062 | 120.9686 | -114.9628 | 5.8548 | -0.00099167 | 0.013727 | 0.072916 | 0.0057656 | 0.064497 | -0.0041912 | -0.003371 | -0.008316 | -0.0017218 | 0.061039 | 0.063591 | -0.010267 | -0.0063831 | 5.5984 | -114.2395 | -13.0829 | -114.9445 | 5.7907 | -115.2191 | -115.0864 | -115.4434 | -5.2826 | -115.1505 | 5.69 | 5.722 | -115.2054 | -115.3015 | -0.25635 | -0.1236 | -0.064087 | 0.72327 | 0.018311 | 0.14191 | -0.25635 | -0.24261 | -0.33875 | -0.16479 | -0.48065 | -0.18768 | 0.15106 | -0.13275 | 120.7535 | 120.5612 | 101.8799 | -120.9412 | 120.6528 | 120.6848 | 109.6802 | -121.1563
1687.1562 | 121.1563 | -118.0344 | 2.7969 | -0.00099167 | 0.007746 | 0.070353 | 0.005552 | 0.062788 | 0.0011494 | -0.0023028 | -0.00068649 | 0.00041436 | 0.06232 | 0.064873 | -0.0066351 | -0.0087329 | 2.5589 | -117.3248 | -14.0442 | -117.9703 | 2.8976 | -118.2541 | -118.1305 | -118.4921 | -5.6122 | -118.2404 | 2.8015 | 2.8015 | -118.2358 | -118.3731 | -0.21973 | -0.09613 | 0.10071 | 0.70953 | 0.064087 | 0.16022 | -0.23804 | -0.20142 | -0.33875 | 0.004578 | -0.45776 | -0.20599 | 0.13275 | 0.004578 | 120.932 | 120.5933 | 103.9902 | -120.9274 | 120.8359 | 120.8359 | 112.4222 | -121.17
1688.8906 | 121.0556 | -119.101 | 1.8997 | 0.0066373 | 0.0081732 | 0.070993 | 0.0040566 | 0.062788 | 0.0026446 | -0.001662 | -0.008316 | 0.001269 | 0.063175 | 0.066368 | -0.0066351 | -0.0089465 | 1.6525 | -118.2449 | -14.2914 | -118.9499 | 1.9089 | -119.1742 | -119.0826 | -119.4763 | -5.6442 | -119.2383 | 1.8173 | 1.8631 | -119.1696 | -119.3481 | -0.073242 | 0.01831 | 0.009156 | 0.85602 | 0.15106 | 0.13275 | -0.24719 | -0.068665 | -0.24719 | -0.082397 | -0.37537 | -0.13733 | 0.10986 | -0.036621 | 121.0098 | 120.7535 | 104.8096 | -120.9824 | 120.9183 | 120.9641 | 113.4567 | -121.2479
1690.625 | 121.0739 | -119.8746 | 1.1124 | -0.00099167 | 0.011805 | 0.069925 | 0.0046976 | 0.062574 | -0.0014142 | -0.0012346 | 0.0069425 | -0.00022644 | 0.062534 | 0.066368 | -0.0062079 | -0.0061695 | 0.83313 | -119.0598 | -14.7446 | -119.7464 | 1.1673 | -119.9203 | -119.8563 | -120.2591 | -5.9189 | -119.9661 | 1.0529 | 1.0757 | -119.9524 | -120.0668 | -0.045776 | 0.018311 | 0.054931 | 0.81482 | 0.12817 | 0.10986 | -0.27924 | -0.07782 | -0.19226 | -0.05951 | -0.38452 | -0.091552 | 0.10071 | -0.036621 | 121.0419 | 120.7077 | 105.13 | -120.9686 | 120.9274 | 120.9503 | 113.9557 | -121.1792
1692.3125 | 121.0373 | -120.0211 | 1.0162 | 0.0066373 | 0.01565 | 0.071207 | 0.0044838 | 0.060865 | -0.0026958 | -0.004439 | 0.0069425 | -0.0047124 | 0.062534 | 0.064232 | -0.01048 | -0.0046741 | 0.77362 | -119.0781 | -14.7949 | -119.838 | 1.0162 | -120.0485 | -119.9478 | -120.3644 | -6.0333 | -120.0577 | 0.92926 | 0.94757 | -120.0348 | -120.2179 | -0.027466 | 0.073242 | 0 | 0.94299 | 0.1831 | 0.10986 | -0.24261 | -0.013733 | -0.19684 | -0.086975 | -0.34332 | -0.036621 | 0.16022 | -0.068664 | 121.0373 | 120.7947 | 105.2261 | -120.9641 | 120.9503 | 120.9686 | 113.9877 | -121.2341
1694.0625 | 121.1975 | -119.4168 | 1.5884 | -0.016251 | 0.0075324 | 0.073984 | 0.0081154 | 0.063643 | -0.00013244 | -0.003371 | -0.00068649 | -0.00065364 | 0.062961 | 0.063805 | -0.0098395 | -0.0068103 | 1.3275 | -118.6111 | -15.0009 | -119.3069 | 1.6754 | -119.4855 | -119.4077 | -119.8563 | -6.1707 | -119.5816 | 1.5839 | 1.5793 | -119.4717 | -119.6732 | -0.068665 | 0.009155 | 0.086975 | 0.80566 | 0.10986 | 0.10071 | -0.26093 | -0.054932 | -0.25635 | -0.004578 | -0.43945 | -0.16479 | 0.091553 | -0.009155 | 121.0922 | 120.7443 | 104.4159 | -120.9961 | 121.0007 | 120.9961 | 113.2462 | -121.2616
1695.75 | 121.1334 | -120.2591 | 0.79193 | -0.00099167 | 0.010096 | 0.071634 | 0.0029886 | 0.06172 | 0.0011494 | -0.0018756 | 0.0069425 | 0.00020076 | 0.061466 | 0.066368 | -0.0059943 | -0.0063831 | 0.52643 | -119.4489 | -15.3763 | -120.1401 | 0.85144 | -120.3186 | -120.2179 | -120.6482 | -6.395 | -120.3918 | 0.75073 | 0.77362 | -120.3186 | -120.4788 | -0.05951 | 0.041198 | 0.059509 | 0.81024 | 0.11902 | 0.07782 | -0.2655 | -0.05951 | -0.21973 | -0.041199 | -0.3891 | -0.13275 | 0.086975 | -0.01831 | 121.1105 | 120.7855 | 104.8828 | -121.0098 | 121.0098 | 121.0327 | 113.8641 | -121.2708
1697.5 | 121.2524 | -117.572 | 3.3829 | -0.00099167 | 0.012232 | 0.073771 | 0.0051248 | 0.062147 | -0.0059002 | -0.0055072 | 0.0069425 | -0.0062078 | 0.060398 | 0.063164 | -0.011121 | -0.0070239 | 3.2181 | -116.684 | -14.7079 | -117.4347 | 3.4378 | -117.659 | -117.5217 | -117.952 | -6.0059 | -117.6315 | 3.3279 | 3.3508 | -117.6315 | -117.8467 | -0.086976 | 0.050354 | 0.054931 | 0.88806 | 0.13733 | 0.086975 | -0.1648 | -0.05951 | -0.27466 | -0.054932 | -0.37994 | -0.05951 | 0.21515 | -0.032044 | 121.0098 | 120.7901 | 102.8641 | -120.9045 | 120.9 | 120.9229 | 111.5662 | -121.2296
1699.25 | 121.2341 | -118.4052 | 2.5909 | 0.0066373 | 0.0036872 | 0.071207 | 0.0053384 | 0.062361 | 0.0017902 | -0.003371 | -0.00068649 | 0.0031916 | 0.060825 | 0.064873 | -0.0070623 | -0.0083057 | 2.3621 | -117.627 | -15.1154 | -118.3182 | 2.6596 | -118.5104 | -118.4372 | -118.84 | -6.3217 | -118.5654 | 2.5543 | 2.5681 | -118.5104 | -118.6935 | -0.10529 | -0.032044 | 0.068665 | 0.7782 | 0.086975 | 0.11902 | -0.22888 | -0.10529 | -0.28839 | -0.036621 | -0.43488 | -0.16022 | 0.12817 | -0.022888 | 121.0648 | 120.7672 | 103.2898 | -121.0281 | 120.9595 | 120.9732 | 112.0834 | -121.2845
1701 | 121.257 | -118.6844 | 2.3346 | -0.00099167 | 0.0051826 | 0.069071 | 0.0040566 | 0.063856 | 0.0020038 | -0.0025164 | 0.0069425 | -0.0012946 | 0.061252 | 0.064659 | -0.0068487 | -0.0061695 | 2.1103 | -117.8604 | -15.3076 | -118.5608 | 2.4307 | -118.7714 | -118.6752 | -119.1055 | -6.4178 | -118.8675 | 2.2705 | 2.3117 | -118.8126 | -118.9636 | -0.086975 | 0.009155 | 0.09613 | 0.82397 | 0.1236 | 0.11444 | -0.2243 | -0.12817 | -0.27924 | -0.064087 | -0.42114 | -0.18311 | 0.09613 | -0.022888 | 121.1151 | 120.7947 | 103.3768 | -121.0098 | 120.9549 | 120.9961 | 112.2665 | -121.2982
1702.75 | 121.1746 | -118.2999 | 2.8015 | -0.00099167 | 0.013727 | 0.073984 | 0.0059792 | 0.060438 | -0.005473 | -0.0025164 | 0.0069425 | -0.0047124 | 0.060825 | 0.063378 | -0.013258 | -0.0083057 | 2.5269 | -117.4026 | -15.2939 | -118.1488 | 2.8336 | -118.3319 | -118.2129 | -118.6752 | -6.4774 | -118.3502 | 2.7054 | 2.7283 | -118.3365 | -118.5104 | -0.032043 | 0.086975 | 0.032043 | 0.89722 | 0.15106 | 0.064087 | -0.27466 | -0.036621 | -0.21057 | -0.096131 | -0.37537 | -0.050354 | 0.16022 | -0.073243 | 121.1334 | 120.8267 | 103.006 | -121.0144 | 121.0052 | 121.0281 | 111.8225 | -121.312
1704.5156 | 121.1197 | -118.7164 | 2.4765 | -0.0086212 | 0.0066778 | 0.069925 | 0.0049112 | 0.064711 | 0.004781 | -0.00059384 | 0.0069425 | 0.00084176 | 0.061679 | 0.064446 | -0.0049261 | -0.0087329 | 2.1469 | -117.8879 | -15.6372 | -118.5654 | 2.4994 | -118.7256 | -118.6203 | -119.0781 | -6.7612 | -118.8583 | 2.3849 | 2.4261 | -118.7576 | -118.895 | -0.009155 | 0.096131 | 0.022889 | 0.82855 | 0.15106 | 0.054931 | -0.32959 | -0.041198 | -0.17853 | -0.091552 | -0.36163 | -0.14191 | 0.036621 | -0.050354 | 121.2158 | 120.8633 | 103.0792 | -121.0968 | 121.1014 | 121.1426 | 111.9553 | -121.3715
1706.2656 | 121.1243 | -118.9911 | 2.1973 | 0.0066373 | 0.012018 | 0.072489 | 0.0061928 | 0.062361 | -0.0039776 | -0.0029436 | -0.00068649 | -0.0036444 | 0.061679 | 0.061455 | -0.0098395 | -0.0059557 | 1.9821 | -117.9794 | -15.6692 | -118.7485 | 2.1973 | -118.9362 | -118.7988 | -119.2291 | -6.7017 | -118.9636 | 2.1103 | 2.1286 | -118.9545 | -119.1284 | 0.054932 | 0.19226 | 0 | 1.0117 | 0.24262 | 0.050354 | -0.21515 | 0.036621 | -0.13733 | -0.086975 | -0.23804 | 0.027466 | 0.16479 | -0.068665 | 121.1884 | 120.9732 | 103.3218 | -120.9961 | 121.1014 | 121.1197 | 112.2894 | -121.3257
1708.0156 | 121.257 | -118.8675 | 2.2614 | -0.00099167 | 0.0075324 | 0.071848 | 0.0059792 | 0.064711 | 0.0020038 | -0.00016664 | -0.00068649 | 0.00062796 | 0.062107 | 0.067223 | -0.0064215 | -0.0078783 | 2.0096 | -117.9977 | -15.8524 | -118.7164 | 2.2705 | -118.9316 | -118.8492 | -119.2154 | -6.8436 | -118.9957 | 2.1927 | 2.2202 | -118.9133 | -119.1055 | -0.064087 | 0.018311 | 0.009155 | 0.86975 | 0.15106 | 0.13275 | -0.25177 | -0.045776 | -0.23804 | -0.068665 | -0.3479 | -0.12817 | 0.10986 | -0.041199 | 121.138 | 120.8771 | 103.0151 | -121.1105 | 121.0602 | 121.0876 | 112.0239 | -121.3669
1709.7031 | 121.2662 | -118.3044 | 2.8015 | -0.00099167 | 0.0068916 | 0.069071 | 0.0057656 | 0.060865 | 0.002431 | -0.00273 | 0.0069425 | -0.0019354 | 0.061252 | 0.064446 | -0.0083441 | -0.0070239 | 2.5269 | -117.4805 | -15.8066 | -118.1854 | 2.861 | -118.3731 | -118.3228 | -118.6844 | -6.9626 | -118.4326 | 2.774 | 2.7786 | -118.364 | -118.5379 | -0.068665 | -0.018311 | 0.059509 | 0.82397 | 0.11902 | 0.13733 | -0.27466 | -0.05951 | -0.23346 | -0.027466 | -0.37994 | -0.12817 | 0.10529 | -0.022889 | 121.1655 | 120.8313 | 102.4979 | -121.1243 | 121.0785 | 121.0831 | 111.3419 | -121.3394
1711.4531 | 121.1838 | -118.9911 | 2.1469 | 0.0066373 | 0.009455 | 0.069712 | 0.007261 | 0.065138 | 0.00093576 | -0.001021 | 0.0069425 | -0.0023626 | 0.061893 | 0.063805 | -0.0070623 | -0.0038195 | 1.8585 | -118.1534 | -16.1636 | -118.8675 | 2.2018 | -119.0186 | -118.9316 | -119.371 | -7.196 | -119.1055 | 2.0966 | 2.1149 | -119.0506 | -119.2062 | -0.027466 | 0.059509 | 0.054931 | 0.83771 | 0.1236 | 0.064087 | -0.28839 | -0.059509 | -0.21515 | -0.050354 | -0.37994 | -0.11444 | 0.10071 | -0.032044 | 121.1929 | 120.8496 | 102.8275 | -121.0785 | 121.0876 | 121.106 | 111.795 | -121.3531
1713.2031 | 121.2982 | -119.1513 | 2.0187 | -0.00099167 | 0.0047552 | 0.071207 | 0.0074746 | 0.06407 | -0.0012006 | -0.0035846 | 0.014572 | 0.00062796 | 0.064243 | 0.064873 | -0.0079169 | -0.0061695 | 1.6983 | -118.2953 | -16.3605 | -119.0506 | 2.092 | -119.2062 | -119.1376 | -119.5724 | -7.3471 | -119.2749 | 1.9501 | 1.9547 | -119.2337 | -119.371 | -0.054932 | 0.013733 | 0.073242 | 0.85602 | 0.10071 | 0.086975 | -0.32044 | -0.082398 | -0.21973 | -0.068665 | -0.42114 | -0.1236 | 0.096131 | -0.064087 | 121.2433 | 120.8496 | 102.7908 | -121.1563 | 121.1014 | 121.106 | 111.8042 | -121.3898
1714.9375 | 121.2524 | -119.4351 | 1.7441 | 0.0066373 | 0.0083868 | 0.068644 | 0.0061928 | 0.065138 | 0.0020038 | -0.0031574 | 0.0069425 | -0.00022644 | 0.061893 | 0.063805 | -0.0068487 | -0.0065967 | 1.5289 | -118.5104 | -16.4291 | -119.2703 | 1.8265 | -119.4443 | -119.3573 | -119.7784 | -7.4615 | -119.5267 | 1.7029 | 1.7258 | -119.458 | -119.632 | -0.009155 | 0.07782 | 0.082397 | 0.92468 | 0.16479 | 0.086975 | -0.21515 | -0.022888 | -0.19684 | -0.041199 | -0.34332 | -0.091552 | 0.10529 | -0.018311 | 121.2616 | 120.9641 | 103.006 | -121.1014 | 121.138 | 121.1609 | 111.9736 | -121.376
1716.625 | 121.2936 | -119.371 | 1.7624 | -0.00099167 | 0.0086006 | 0.071421 | 0.0074746 | 0.064283 | 0.002431 | -0.001662 | 0.0069425 | -0.00086724 | 0.065097 | 0.065728 | -0.0081305 | -0.0083057 | 1.5335 | -118.4738 | -16.5253 | -119.2291 | 1.8402 | -119.426 | -119.3481 | -119.7418 | -7.6904 | -119.4855 | 1.7441 | 1.7303 | -119.4443 | -119.5999 | -0.054931 | 0.022888 | 0.07782 | 0.89722 | 0.14191 | 0.11902 | -0.22888 | -0.073242 | -0.22888 | -0.01831 | -0.37079 | -0.11444 | 0.11444 | -0.032043 | 121.2112 | 120.9045 | 102.8458 | -121.1105 | 121.1151 | 121.1014 | 111.6806 | -121.3623
1718.375 | 121.1975 | -119.5541 | 1.68 | 0.0066373 | 0.0096686 | 0.072489 | 0.0044838 | 0.062574 | 0.0017902 | -0.0023028 | 0.014572 | -1.2844e-05 | 0.061893 | 0.066368 | -0.0079169 | -0.0068103 | 1.3412 | -118.7027 | -16.8182 | -119.4168 | 1.7303 | -119.5816 | -119.4672 | -119.9387 | -7.9468 | -119.6823 | 1.6205 | 1.6388 | -119.5816 | -119.7327 | -0.027466 | 0.086975 | 0.050354 | 0.85144 | 0.13733 | 0.050354 | -0.33875 | -0.027466 | -0.17853 | -0.05951 | -0.38452 | -0.12817 | 0.050354 | -0.041199 | 121.2845 | 120.8954 | 102.7359 | -121.1472 | 121.1746 | 121.1929 | 111.6074 | -121.4127
1720.0625 | 121.2708 | -119.6182 | 1.5472 | -0.00099167 | 0.010523 | 0.071634 | 0.0093972 | 0.065138 | -0.0056866 | -0.0018756 | 0.014572 | -0.0047124 | 0.061252 | 0.062737 | -0.0089849 | -0.0059557 | 1.3138 | -118.6569 | -16.7908 | -119.4397 | 1.5701 | -119.6732 | -119.5816 | -119.9753 | -7.8644 | -119.6869 | 1.4832 | 1.506 | -119.6823 | -119.8334 | -0.054932 | 0.036621 | 0.022888 | 0.9613 | 0.17853 | 0.14191 | -0.23346 | -0.064087 | -0.21515 | -0.064087 | -0.35706 | -0.068665 | 0.14648 | -0.041199 | 121.1884 | 120.932 | 102.8275 | -121.1288 | 121.1014 | 121.1243 | 111.7538 | -121.3806
1721.7969 | 121.3257 | -119.7556 | 1.3733 | -0.00099167 | 0.010309 | 0.074625 | 0.0096108 | 0.061079 | -0.005473 | -0.0070026 | 0.014572 | -0.0057806 | 0.060398 | 0.063591 | -0.011976 | -0.0089465 | 1.1765 | -118.8171 | -17.0471 | -119.6136 | 1.4236 | -119.8242 | -119.7189 | -120.1263 | -8.1024 | -119.8105 | 1.3321 | 1.3412 | -119.8196 | -119.9936 | -0.068665 | 0.036621 | 0.050354 | 0.93842 | 0.14191 | 0.10529 | -0.19684 | -0.064087 | -0.23804 | -0.041199 | -0.37079 | -0.054932 | 0.1831 | -0.032043 | 121.1792 | 120.932 | 102.7084 | -121.0922 | 121.0876 | 121.0968 | 111.6531 | -121.3669
1723.5469 | 121.2662 | -119.5129 | 1.7075 | 0.014267 | 0.009455 | 0.071207 | 0.0061928 | 0.062361 | 0.0015766 | -0.003371 | -0.00068649 | -0.0015082 | 0.059543 | 0.06295 | -0.0051397 | -0.010869 | 1.5381 | -118.5287 | -17.0471 | -119.2978 | 1.7899 | -119.4992 | -119.4305 | -119.8013 | -8.2077 | -119.5724 | 1.6937 | 1.7075 | -119.5084 | -119.6732 | 0.013732 | 0.082397 | 0.082398 | 0.98419 | 0.21515 | 0.13275 | -0.16937 | 0.004577 | -0.16022 | -0.013732 | -0.28839 | -0.05951 | 0.10071 | 0 | 121.3028 | 121.051 | 102.4658 | -121.138 | 121.2067 | 121.2204 | 111.3052 | -121.3806
1725.2969 | 121.2708 | -119.6732 | 1.5472 | 0.0066373 | 0.01095 | 0.072062 | 0.0070474 | 0.063856 | -0.0022686 | -0.0025164 | 0.014572 | -0.0025762 | 0.062961 | 0.064019 | -0.010694 | -0.0072375 | 1.268 | -118.7531 | -17.2806 | -119.5129 | 1.5976 | -119.696 | -119.6045 | -120.0668 | -8.5098 | -119.8013 | 1.5106 | 1.5335 | -119.7327 | -119.8791 | -0.022888 | 0.068665 | 0.050354 | 0.92011 | 0.16022 | 0.091553 | -0.27924 | -0.059509 | -0.20599 | -0.036621 | -0.39368 | -0.12817 | 0.077819 | -0.013733 | 121.2708 | 120.9412 | 102.3926 | -121.1517 | 121.1838 | 121.2067 | 111.1633 | -121.4264
1727.0469 | 121.225 | -119.7235 | 1.5472 | 0.014267 | 0.010523 | 0.06843 | 0.0053384 | 0.065565 | 0.0026446 | -0.0020892 | 0.0069425 | -0.0012946 | 0.063388 | 0.062523 | -0.0081305 | -0.0063831 | 1.1993 | -118.8858 | -17.3859 | -119.5724 | 1.5701 | -119.7418 | -119.6548 | -120.0943 | -8.6334 | -119.87 | 1.4832 | 1.4969 | -119.7556 | -119.9295 | -0.01831 | 0.068665 | 0.022888 | 0.83771 | 0.15106 | 0.082397 | -0.3479 | -0.032043 | -0.20599 | -0.064087 | -0.37079 | -0.14648 | 0.059509 | -0.050354 | 121.2936 | 120.9229 | 102.3376 | -121.2021 | 121.2067 | 121.2204 | 111.0901 | -121.4767
1728.7344 | 121.344 | -119.8608 | 1.3184 | -0.0086212 | 0.0075324 | 0.067789 | 0.0070474 | 0.064924 | 0.001363 | -0.0020892 | 0.0069425 | 0.0014826 | 0.063816 | 0.066796 | -0.0096259 | -0.0087329 | 1.0849 | -118.9865 | -17.4728 | -119.7189 | 1.3779 | -119.9341 | -119.8608 | -120.2454 | -8.6884 | -120.0073 | 1.2863 | 1.3092 | -119.957 | -120.1126 | -0.073242 | 0 | 0.05951 | 0.87433 | 0.14191 | 0.14191 | -0.23346 | -0.09613 | -0.25177 | -0.032043 | -0.38452 | -0.14648 | 0.10529 | -0.009155 | 121.2387 | 120.9457 | 102.388 | -121.1792 | 121.1472 | 121.17 | 111.1725 | -121.431
1730.4844 | 121.2799 | -119.9295 | 1.3092 | 0.0066373 | 0.0092414 | 0.072275 | 0.0036294 | 0.061293 | -0.00055964 | -0.0018756 | 0.0069425 | -0.002149 | 0.061679 | 0.064446 | -0.010267 | -0.0053149 | 1.0345 | -119.0414 | -17.6971 | -119.783 | 1.3367 | -119.9615 | -119.87 | -120.2408 | -8.876 | -120.0073 | 1.2222 | 1.236 | -119.9387 | -120.1401 | -0.032044 | 0.059509 | 0.027466 | 0.88806 | 0.14648 | 0.086975 | -0.27466 | -0.009156 | -0.21057 | -0.086975 | -0.31128 | -0.07782 | 0.13275 | -0.073242 | 121.2662 | 120.9641 | 102.2324 | -121.1792 | 121.1517 | 121.1655 | 111.0535 | -121.4493
1732.2344 | 121.2341 | -120.0119 | 1.2863 | -0.00099167 | 0.010096 | 0.07078 | 0.0074746 | 0.062788 | -0.0046184 | -0.0042254 | 0.014572 | -0.0044988 | 0.060611 | 0.063805 | -0.012617 | -0.0063831 | 1.0071 | -119.0506 | -17.7612 | -119.8151 | 1.2817 | -119.9982 | -119.8975 | -120.3323 | -9.0271 | -120.0394 | 1.1902 | 1.1993 | -120.0073 | -120.1904 | 0.013733 | 0.11444 | -0.004578 | 0.9613 | 0.19684 | 0.082398 | -0.27924 | 0.004578 | -0.17853 | -0.09613 | -0.32043 | -0.027466 | 0.15106 | -0.086975 | 121.2936 | 121.019 | 102.2507 | -121.1838 | 121.2021 | 121.2112 | 110.9848 | -121.4767
1734 | 121.2341 | -119.9982 | 1.2726 | 0.014267 | 0.011164 | 0.071848 | 0.0025612 | 0.062361 | -0.0022686 | -0.0029436 | -0.008316 | -0.0025762 | 0.058689 | 0.063591 | -0.0077033 | -0.0080921 | 1.0666 | -118.9957 | -17.9031 | -119.7876 | 1.2589 | -119.989 | -119.9066 | -120.2866 | -9.1736 | -120.0165 | 1.1765 | 1.1948 | -120.0119 | -120.1859 | 0.009155 | 0.091553 | -0.013733 | 1.0025 | 0.21057 | 0.11902 | -0.20599 | -0.013733 | -0.18768 | -0.09613 | -0.28839 | -0.01831 | 0.16937 | -0.07782 | 121.257 | 121.0648 | 102.095 | -121.1792 | 121.1746 | 121.1929 | 110.8246 | -121.4584
1735.6875 | 121.3943 | -119.8883 | 1.3458 | 0.0066373 | 0.0051826 | 0.070353 | 0.0083292 | 0.063429 | 0.0011494 | -0.003371 | 0.0069425 | -1.2844e-05 | 0.06467 | 0.065941 | -0.0077033 | -0.010015 | 1.0986 | -119.0414 | -18.2098 | -119.7601 | 1.442 | -119.9661 | -119.838 | -120.2499 | -9.4391 | -120.0302 | 1.3275 | 1.3458 | -119.9615 | -120.108 | -0.077819 | 0.050354 | 0.096131 | 0.84686 | 0.12817 | 0.07782 | -0.24719 | -0.073242 | -0.21973 | -0.01831 | -0.36163 | -0.14191 | 0.07782 | 0 | 121.3303 | 120.9869 | 101.6785 | -121.1838 | 121.2158 | 121.2341 | 110.4492 | -121.4539
1737.4219 | 121.2616 | -119.9799 | 1.3458 | 0.014267 | 0.0075324 | 0.070993 | 0.0042702 | 0.061934 | 0.002431 | -0.00273 | -0.00068649 | 0.00020076 | 0.061679 | 0.067437 | -0.0036443 | -0.0074511 | 1.0941 | -119.0048 | -18.3655 | -119.783 | 1.3687 | -119.957 | -119.8563 | -120.282 | -9.613 | -120.0851 | 1.2726 | 1.2863 | -119.989 | -120.163 | 0.022888 | 0.1236 | 0.022888 | 0.97504 | 0.19684 | 0.073242 | -0.25177 | -0.009156 | -0.18311 | -0.073242 | -0.30212 | -0.10529 | 0.07782 | -0.059509 | 121.3486 | 121.0739 | 101.6144 | -121.2021 | 121.2524 | 121.2662 | 110.3668 | -121.5088
1739.1094 | 121.3852 | -119.8883 | 1.3367 | 0.014267 | 0.006037 | 0.070139 | 0.007261 | 0.060652 | 0.00093576 | -0.0023028 | -0.00068649 | -0.0032172 | 0.063175 | 0.063378 | -0.0089849 | -0.0055285 | 1.062 | -119.0323 | -18.4845 | -119.7693 | 1.4099 | -119.9753 | -119.8471 | -120.2728 | -9.668 | -120.0394 | 1.3229 | 1.355 | -119.9615 | -120.1126 | -0.086975 | 0.041199 | 0.073242 | 0.85602 | 0.11902 | 0.07782 | -0.27466 | -0.073242 | -0.2243 | -0.013733 | -0.38452 | -0.15106 | 0.073242 | 0.01831 | 121.2982 | 120.9503 | 101.4038 | -121.1838 | 121.2112 | 121.2433 | 110.2203 | -121.4493
1740.7969 | 121.2753 | -119.902 | 1.4053 | -0.00099167 | 0.010309 | 0.070566 | 0.0070474 | 0.063429 | 0.0026446 | -0.0025164 | -0.00068649 | -0.0012946 | 0.061893 | 0.067009 | -0.0068487 | -0.0065967 | 1.0757 | -119.0552 | -18.7225 | -119.7784 | 1.4465 | -119.9387 | -119.8471 | -120.2774 | -9.8969 | -120.0485 | 1.3367 | 1.3504 | -119.9661 | -120.1309 | -0.036621 | 0.054932 | 0.041199 | 0.84686 | 0.1236 | 0.068665 | -0.32959 | -0.064086 | -0.22888 | -0.068664 | -0.37537 | -0.14648 | 0.082397 | -0.054931 | 121.3486 | 120.9778 | 101.1795 | -121.2524 | 121.2387 | 121.2524 | 110.0052 | -121.5363
1742.5469 | 121.3486 | -120.0394 | 1.2085 | 0.0066373 | 0.0053962 | 0.071421 | 0.010679 | 0.060865 | -0.0035504 | -0.0040118 | 0.014572 | -0.00065364 | 0.063175 | 0.064659 | -0.010908 | -0.0061695 | 0.92468 | -119.1422 | -18.8644 | -119.9203 | 1.2955 | -120.0897 | -120.0073 | -120.4422 | -10.0571 | -120.1767 | 1.1948 | 1.2314 | -120.1447 | -120.282 | -0.050354 | 0.032044 | 0.086975 | 0.89722 | 0.11902 | 0.086975 | -0.28381 | -0.10529 | -0.24261 | -0.013733 | -0.40283 | -0.13733 | 0.10528 | 0.022888 | 121.3348 | 120.9641 | 101.1749 | -121.2158 | 121.2341 | 121.2708 | 109.9823 | -121.4905
1744.2969 | 121.2936 | -120.0714 | 1.2268 | 0.0066373 | 0.012446 | 0.069712 | 0.0042702 | 0.063856 | -0.00098684 | -0.00273 | -0.00068649 | -0.0036444 | 0.061039 | 0.06765 | -0.0089849 | -0.0080921 | 1.0254 | -119.0689 | -18.9011 | -119.8608 | 1.2131 | -120.0714 | -119.9478 | -120.3232 | -10.1486 | -120.0623 | 1.1215 | 1.1627 | -120.0897 | -120.2637 | 0 | 0.1236 | -0.013733 | 1.0025 | 0.21057 | 0.086975 | -0.20142 | -0.018311 | -0.19226 | -0.10529 | -0.25177 | 0.009155 | 0.20142 | -0.064087 | 121.2845 | 121.0968 | 101.1703 | -121.1746 | 121.1929 | 121.2341 | 109.9228 | -121.4905
1745.9844 | 121.3943 | -120.0989 | 1.1581 | 0.0066373 | 0.0086006 | 0.072702 | 0.007261 | 0.063643 | -0.0063274 | -0.0035846 | -0.008316 | -0.0034308 | 0.061039 | 0.060387 | -0.0087713 | -0.0059557 | 0.97046 | -119.0598 | -19.0155 | -119.8929 | 1.2039 | -120.1126 | -119.9982 | -120.3873 | -10.1257 | -120.1126 | 1.1215 | 1.1215 | -120.1584 | -120.3094 | -0.013733 | 0.10071 | 0.045776 | 1.0391 | 0.20599 | 0.10529 | -0.18768 | -0.059509 | -0.21057 | -0.036621 | -0.28839 | -0.013733 | 0.19684 | -0.036621 | 121.3028 | 121.0693 | 101.0834 | -121.1563 | 121.2204 | 121.2204 | 109.9731 | -121.4676
1747.7344 | 121.344 | -120.1721 | 1.1353 | 0.014267 | 0.012446 | 0.073557 | 0.0079018 | 0.062788 | -0.0029094 | -0.0048662 | 0.0069425 | -0.0064214 | 0.060611 | 0.063591 | -0.01048 | -0.0065967 | 0.8606 | -119.2245 | -19.2719 | -120.0027 | 1.1536 | -120.1813 | -120.0668 | -120.4788 | -10.5606 | -120.2225 | 1.0666 | 1.0803 | -120.1996 | -120.3598 | -0.009155 | 0.10529 | 0.01831 | 0.94757 | 0.16937 | 0.064086 | -0.27466 | -0.027466 | -0.18768 | -0.068665 | -0.3067 | -0.050354 | 0.13733 | -0.054932 | 121.3257 | 121.0327 | 100.9003 | -121.2021 | 121.2387 | 121.2524 | 109.6115 | -121.4951
1749.5 | 121.3715 | -120.1584 | 1.1261 | -0.00099167 | 0.0051826 | 0.069071 | 0.0098244 | 0.064283 | 0.00093576 | -0.0059344 | 0.014572 | -0.00086724 | 0.062961 | 0.064659 | -0.0091985 | -0.0091601 | 0.85144 | -119.2566 | -19.4229 | -120.0302 | 1.1948 | -120.2133 | -120.1309 | -120.5383 | -10.73 | -120.2866 | 1.1124 | 1.1032 | -120.2499 | -120.401 | -0.054932 | 0.027466 | 0.068664 | 0.90179 | 0.12817 | 0.10071 | -0.27466 | -0.091553 | -0.24262 | -0.013733 | -0.37994 | -0.12817 | 0.11444 | -0.022889 | 121.3531 | 121.0098 | 100.7355 | -121.257 | 121.2708 | 121.2616 | 109.4284 | -121.5271
1751.1875 | 121.431 | -120.1538 | 1.1032 | -0.00099167 | 0.012873 | 0.072916 | 0.0091836 | 0.063002 | -0.0029094 | -0.0063616 | -0.00068649 | -0.0057806 | 0.061252 | 0.065514 | -0.0091985 | -0.0076647 | 0.89264 | -119.1742 | -19.5923 | -119.9982 | 1.149 | -120.1904 | -120.1035 | -120.4559 | -10.7986 | -120.1904 | 1.0437 | 1.0529 | -120.2087 | -120.3918 | -0.036621 | 0.050354 | 0.045777 | 0.97961 | 0.15564 | 0.10529 | -0.21057 | -0.054931 | -0.23804 | -0.059509 | -0.30212 | -0.036621 | 0.20142 | -0.050354 | 121.3028 | 121.0464 | 100.5615 | -121.2067 | 121.1975 | 121.2067 | 109.3552 | -121.4951
1752.9375 | 121.376 | -120.1813 | 1.1444 | -0.00099167 | 0.0071052 | 0.068857 | 0.0046976 | 0.063643 | 0.0071308 | -0.0020892 | 0.0069425 | 0.0010554 | 0.064243 | 0.063805 | -0.0068487 | -0.0093737 | 0.94299 | -119.2017 | -19.6198 | -119.9982 | 1.1948 | -120.195 | -120.1172 | -120.4651 | -10.8948 | -120.2866 | 1.0986 | 1.1215 | -120.1996 | -120.3827 | -0.013733 | 0.064087 | 0.050354 | 0.97961 | 0.1831 | 0.11902 | -0.20142 | -0.018311 | -0.20142 | -0.045776 | -0.28381 | -0.10529 | 0.09613 | -0.022888 | 121.376 | 121.1243 | 100.5615 | -121.2616 | 121.2799 | 121.3028 | 109.2865 | -121.5271
1754.6094 | 121.3348 | -120.3827 | 0.95673 | 0.014267 | 0.011591 | 0.074839 | 0.0064066 | 0.062788 | -0.0041912 | -0.0059344 | 0.014572 | -0.0053534 | 0.060184 | 0.064019 | -0.0081305 | -0.0059557 | 0.67749 | -119.4214 | -19.693 | -120.2271 | 0.97046 | -120.3918 | -120.3049 | -120.6985 | -11.0321 | -120.4239 | 0.86517 | 0.89722 | -120.4147 | -120.5795 | -0.009156 | 0.077819 | 0.013733 | 0.9613 | 0.15564 | 0.07782 | -0.27924 | -0.032044 | -0.19684 | -0.091553 | -0.31586 | -0.041199 | 0.15564 | -0.059509 | 121.3531 | 121.0602 | 100.6897 | -121.2616 | 121.2479 | 121.2799 | 109.3506 | -121.5363
1756.3594 | 121.4264 | -120.3918 | 0.91095 | 0.014267 | 0.0081732 | 0.073343 | 0.005552 | 0.064497 | 0.0032856 | -0.0037982 | -0.00068649 | -0.00086724 | 0.061252 | 0.064659 | -0.0068487 | -0.0080921 | 0.63629 | -119.4992 | -19.9493 | -120.3003 | 0.99335 | -120.4651 | -120.369 | -120.7672 | -11.3113 | -120.5566 | 0.91095 | 0.89722 | -120.4742 | -120.6345 | -0.073242 | 0.022888 | 0.082397 | 0.89264 | 0.091553 | 0.068665 | -0.27466 | -0.082397 | -0.24261 | 0 | -0.37537 | -0.16479 | 0.077819 | -0.013733 | 121.3852 | 121.0281 | 100.4425 | -121.2799 | 121.3028 | 121.2891 | 109.0805 | -121.5454
1758.1094 | 121.4401 | -120.401 | 0.88348 | 0.0066373 | 0.010737 | 0.074839 | 0.0061928 | 0.063215 | -0.003764 | -0.0046526 | 0.014572 | -0.0042852 | 0.062107 | 0.062737 | -0.01048 | -0.0080921 | 0.72327 | -119.3619 | -19.9905 | -120.2179 | 0.94299 | -120.4056 | -120.3461 | -120.6573 | -11.4075 | -120.3964 | 0.83313 | 0.85144 | -120.4239 | -120.6253 | -0.004578 | 0.054932 | 0.059509 | 1.0391 | 0.1831 | 0.12817 | -0.16022 | -0.022888 | -0.2243 | -0.050354 | -0.25635 | 0.004578 | 0.22888 | -0.032044 | 121.344 | 121.1243 | 100.4105 | -121.2296 | 121.2341 | 121.2524 | 108.9935 | -121.5088
1759.7969 | 121.3211 | -120.4514 | 0.92468 | -0.0086212 | 0.0075324 | 0.069498 | 0.0036294 | 0.062574 | 0.0028584 | -0.0014484 | 0.0069425 | -1.2844e-05 | 0.061679 | 0.066368 | -0.0038581 | -0.0078783 | 0.62256 | -119.5358 | -20.3156 | -120.3232 | 0.94757 | -120.4651 | -120.3735 | -120.7718 | -11.8698 | -120.6253 | 0.84686 | 0.88348 | -120.4926 | -120.6665 | -0.013733 | 0.07782 | 0.022888 | 0.91553 | 0.12817 | 0.050354 | -0.30212 | -0.041199 | -0.21515 | -0.07782 | -0.32043 | -0.17395 | 0.041199 | -0.041199 | 121.3989 | 121.0739 | 100.1358 | -121.2982 | 121.2982 | 121.3348 | 108.5815 | -121.5912
1761.5625 | 121.3806 | -120.4742 | 0.86975 | 0.0066373 | 0.012018 | 0.070353 | 0.0044838 | 0.062361 | 0.00093576 | -0.0025164 | 0.0069425 | -0.0010808 | 0.060184 | 0.066796 | -0.0070623 | -0.0076647 | 0.60883 | -119.5496 | -20.4849 | -120.3369 | 0.92926 | -120.5017 | -120.4056 | -120.7672 | -11.9797 | -120.5521 | 0.82398 | 0.83313 | -120.5063 | -120.6665 | -0.027466 | 0.068664 | 0.059509 | 0.92468 | 0.13733 | 0.068665 | -0.26093 | -0.032044 | -0.19226 | -0.045776 | -0.29297 | -0.07782 | 0.11444 | -0.036621 | 121.4035 | 121.0831 | 99.9893 | -121.2753 | 121.2982 | 121.3074 | 108.4946 | -121.5363
1763.3281 | 121.4584 | -120.4971 | 0.82855 | 0.0066373 | 0.0066778 | 0.071421 | 0.0057656 | 0.063002 | 0.00093576 | -0.003371 | 0.0069425 | -0.00022644 | 0.06232 | 0.066796 | -0.0091985 | -0.0072375 | 0.55389 | -119.5724 | -20.7275 | -120.369 | 0.90179 | -120.5704 | -120.4742 | -120.845 | -12.2955 | -120.639 | 0.79651 | 0.82855 | -120.5566 | -120.7123 | -0.073243 | 0.022888 | 0.073242 | 0.92468 | 0.12817 | 0.10528 | -0.27466 | -0.05951 | -0.21515 | -0.032043 | -0.3479 | -0.14191 | 0.073242 | 0 | 121.3989 | 121.051 | 99.7696 | -121.3028 | 121.2936 | 121.3257 | 108.2016 | -121.5408
1765.0156 | 121.463 | -120.4971 | 0.81024 | -0.016251 | 0.012232 | 0.074839 | 0.0081154 | 0.063643 | -0.005473 | -0.0035846 | 0.0069425 | -0.0051398 | 0.061039 | 0.064446 | -0.0091985 | -0.0072375 | 0.59967 | -119.4855 | -20.8282 | -120.3232 | 0.82855 | -120.5521 | -120.4239 | -120.7901 | -12.4191 | -120.5154 | 0.72327 | 0.75989 | -120.5704 | -120.7397 | -0.054932 | 0.073242 | 0.01831 | 1.0117 | 0.17395 | 0.10071 | -0.21057 | -0.073243 | -0.24262 | -0.086975 | -0.29297 | -0.018311 | 0.2243 | -0.050354 | 121.3257 | 121.0968 | 99.6689 | -121.2341 | 121.2204 | 121.257 | 108.078 | -121.55
1766.75 | 121.344 | -120.5795 | 0.81024 | -0.00099167 | 0.004969 | 0.066935 | 0.0046976 | 0.062147 | 0.0067036 | -0.00273 | 0.014572 | -0.0017218 | 0.060611 | 0.066155 | -0.0062079 | -0.0072375 | 0.54016 | -119.6136 | -21.1304 | -120.4285 | 0.82855 | -120.607 | -120.5063 | -120.8954 | -12.8082 | -120.7169 | 0.74158 | 0.75531 | -120.6436 | -120.8038 | -0.027466 | 0.073242 | 0.01831 | 0.96588 | 0.15106 | 0.07782 | -0.27008 | -0.064087 | -0.2243 | -0.068665 | -0.31586 | -0.13733 | 0.086975 | -0.054932 | 121.4081 | 121.1197 | 99.4492 | -121.3165 | 121.3211 | 121.3348 | 107.7713 | -121.6141
1768.5 | 121.4676 | -120.5383 | 0.77362 | 0.014267 | 0.0096686 | 0.076334 | 0.00897 | 0.063643 | -0.0078228 | -0.0037982 | 0.014572 | -0.0047124 | 0.060184 | 0.064232 | -0.010053 | -0.0057421 | 0.58594 | -119.4855 | -21.1533 | -120.3506 | 0.80109 | -120.5841 | -120.4788 | -120.7993 | -12.8036 | -120.5292 | 0.71869 | 0.74158 | -120.6024 | -120.7581 | -0.045776 | 0.059509 | 0.027465 | 1.0529 | 0.18768 | 0.12817 | -0.18768 | -0.064087 | -0.21973 | -0.054932 | -0.26093 | 0.009155 | 0.22888 | -0.032044 | 121.3394 | 121.1243 | 99.3851 | -121.2524 | 121.257 | 121.2799 | 107.7347 | -121.5317
1770.1875 | 121.3577 | -120.5978 | 0.80566 | -0.00099167 | 0.011591 | 0.072702 | 0.0085428 | 0.060438 | -0.0033368 | -0.0046526 | 0.022202 | -0.0023626 | 0.061679 | 0.065514 | -0.011335 | -0.0059557 | 0.54474 | -119.5724 | -21.4233 | -120.401 | 0.81024 | -120.5704 | -120.4834 | -120.8679 | -13.1607 | -120.6253 | 0.72784 | 0.73242 | -120.5933 | -120.7535 | 0.027465 | 0.11444 | 0.004578 | 1.0254 | 0.19684 | 0.082397 | -0.26093 | 0.004577 | -0.15564 | -0.07782 | -0.27008 | -0.027466 | 0.12817 | -0.073242 | 121.4081 | 121.1426 | 99.1745 | -121.2891 | 121.3257 | 121.3303 | 107.4371 | -121.5591
1771.9375 | 121.4447 | -117.8787 | 3.392 | 0.0066373 | 0.012659 | 0.073557 | 0.0061928 | 0.062574 | -0.0029094 | -0.0037982 | 0.0069425 | -0.0036444 | 0.05997 | 0.062096 | -0.01048 | -0.0068103 | 3.1494 | -116.9998 | -20.7275 | -117.7872 | 3.4058 | -117.9932 | -117.8787 | -118.2495 | -12.8494 | -118.0252 | 3.3005 | 3.3417 | -118.0023 | -118.1534 | -0.11444 | 0 | 0.013733 | 0.87891 | 0.091553 | 0.091553 | -0.24261 | -0.1236 | -0.27466 | -0.091553 | -0.37079 | -0.14649 | 0.12817 | -0.050354 | 121.2845 | 121.0281 | 97.1512 | -121.2708 | 121.1792 | 121.2204 | 105.0293 | -121.5454
1773.6875 | 121.5363 | -117.7185 | 3.5751 | 0.014267 | 0.006037 | 0.072275 | 0.0076882 | 0.063429 | 0.00093576 | -0.0031574 | 0.0069425 | 0.00062796 | 0.062961 | 0.064232 | -0.0062079 | -0.0074511 | 3.2593 | -116.9128 | -20.6635 | -117.691 | 3.6026 | -117.8696 | -117.8009 | -118.1396 | -12.9181 | -117.9794 | 3.4973 | 3.511 | -117.8879 | -118.0664 | -0.15106 | -0.082397 | 0.027466 | 0.80566 | 0.027466 | 0.10986 | -0.31586 | -0.16937 | -0.3479 | -0.07782 | -0.42114 | -0.26093 | 0.086975 | -0.064087 | 121.3211 | 120.9778 | 97.0551 | -121.376 | 121.2158 | 121.2296 | 104.8004 | -121.6415
1775.4219 | 121.4081 | -117.8696 | 3.4836 | 0.014267 | 0.011378 | 0.072275 | 0.0066202 | 0.064283 | -0.003764 | -0.0048662 | 0.014572 | -0.0047124 | 0.063175 | 0.065087 | -0.0079169 | -0.0083057 | 3.2501 | -116.89 | -20.961 | -117.7048 | 3.511 | -117.897 | -117.8101 | -118.1534 | -13.2248 | -117.9337 | 3.4012 | 3.4149 | -117.9153 | -118.1076 | -0.027466 | 0.059509 | 0.027465 | 0.97961 | 0.16479 | 0.10529 | -0.23346 | -0.045776 | -0.23804 | -0.082398 | -0.28381 | -0.064087 | 0.17395 | -0.068665 | 121.3806 | 121.1197 | 96.9086 | -121.2936 | 121.2708 | 121.2845 | 104.6448 | -121.5912
1777.1719 | 121.431 | -118.3456 | 3.0716 | 0.014267 | 0.011805 | 0.073557 | 0.0061928 | 0.06642 | -0.0039776 | -0.0037982 | 0.014572 | -0.0036444 | 0.062961 | 0.065941 | -0.0091985 | -0.0083057 | 2.8198 | -117.334 | -21.2952 | -118.1305 | 3.0716 | -118.3182 | -118.2495 | -118.5928 | -13.5269 | -118.3731 | 2.98 | 3.0075 | -118.3319 | -118.5196 | 0.027466 | 0.09613 | 0 | 1.0117 | 0.21515 | 0.11902 | -0.25177 | 0.013733 | -0.17395 | -0.091552 | -0.24719 | -0.027466 | 0.14648 | -0.064087 | 121.4172 | 121.1655 | 97.0505 | -121.3211 | 121.3257 | 121.3531 | 104.8187 | -121.5912
1778.8594 | 121.4355 | -119.0369 | 2.3621 | -0.00099167 | 0.011378 | 0.069498 | 0.0042702 | 0.062147 | 0.0034992 | -0.00273 | 0.0069425 | 0.001269 | 0.062534 | 0.067009 | -0.0044989 | -0.0087329 | 2.0828 | -118.1168 | -21.7392 | -118.8995 | 2.417 | -119.0781 | -118.9728 | -119.3573 | -13.916 | -119.2291 | 2.3026 | 2.2934 | -119.1422 | -119.3207 | -0.041199 | 0.064087 | 0.054931 | 0.92011 | 0.13733 | 0.073242 | -0.27924 | -0.10529 | -0.28381 | -0.05951 | -0.32043 | -0.19226 | 0.091553 | -0.068665 | 121.4539 | 121.1197 | 97.2977 | -121.3348 | 121.3394 | 121.3303 | 105.1208 | -121.6827
1780.5938 | 121.2204 | -45.4971 | 75.8423 | 0.014267 | 0.016291 | 0.071207 | 0.0066202 | 0.062574 | 0.0022174 | -0.0042254 | 0.0069425 | -0.0049262 | 0.058048 | 0.060814 | -0.0070623 | -0.0080921 | 75.2151 | -45.5658 | 1.9638 | -45.9229 | 75.3937 | -45.8221 | -45.8771 | -46.0373 | 1.9592 | -45.9915 | 75.3845 | 75.4395 | -45.6711 | -45.7169 | -0.32501 | -0.37994 | -0.44861 | -0.068665 | -0.42572 | -0.045777 | -0.62714 | -0.17395 | -0.21973 | -0.45776 | -0.54016 | -0.49438 | -0.27466 | -0.40283 | 120.8908 | 120.7123 | 47.4609 | -121.7194 | 120.8817 | 120.9366 | 47.4564 | -121.5591
1782.3281 | 121.5729 | -118.6569 | 2.5955 | -0.00099167 | 0.012446 | 0.074839 | 0.0070474 | 0.063002 | -0.003764 | -0.0048662 | -0.008316 | -0.003858 | 0.061679 | 0.064019 | -0.011762 | -0.0063831 | 2.3941 | -117.7185 | -21.8033 | -118.5654 | 2.6413 | -118.8126 | -118.6707 | -118.9774 | -14.0121 | -118.7668 | 2.536 | 2.5681 | -118.808 | -118.9774 | -0.15564 | -0.013733 | 0.045776 | 0.93841 | 0.091552 | 0.10528 | -0.20142 | -0.15106 | -0.32044 | -0.059509 | -0.32044 | -0.10986 | 0.21057 | -0.027466 | 121.2982 | 121.051 | 96.8536 | -121.2662 | 121.1929 | 121.225 | 104.6448 | -121.5729
1784.0312 | 121.4996 | -118.2312 | 3.1082 | -0.016251 | 0.0092414 | 0.072062 | 0.0068338 | 0.063002 | 8.1158e-05 | -0.003371 | -0.00068649 | -0.0015082 | 0.061252 | 0.0653 | -0.0087713 | -0.0072375 | 2.8748 | -117.2653 | -21.7941 | -118.0939 | 3.1631 | -118.3044 | -118.2312 | -118.5745 | -14.1769 | -118.3868 | 3.0808 | 3.1036 | -118.3594 | -118.5059 | -0.073242 | 0 | 0.054932 | 0.96588 | 0.13733 | 0.13733 | -0.23346 | -0.12817 | -0.27466 | -0.027465 | -0.34332 | -0.15564 | 0.11902 | -0.004577 | 121.3943 | 121.106 | 96.4371 | -121.3394 | 121.312 | 121.3348 | 104.0543 | -121.6141
1785.7188 | 121.5454 | -118.4052 | 2.916 | 0.0066373 | 0.012659 | 0.072489 | 0.005552 | 0.062361 | -0.0044048 | -0.003371 | 0.014572 | -0.0027898 | 0.060184 | 0.06295 | -0.0091985 | -0.0059557 | 2.71 | -117.421 | -21.9131 | -118.2816 | 2.9709 | -118.4784 | -118.3777 | -118.6661 | -14.2273 | -118.4418 | 2.8748 | 2.8885 | -118.4555 | -118.6386 | -0.073243 | 0.027465 | 0.054931 | 0.98419 | 0.1236 | 0.096131 | -0.20599 | -0.050354 | -0.23346 | -0.041199 | -0.26093 | -0.036621 | 0.19684 | -0.027466 | 121.376 | 121.1151 | 96.492 | -121.2936 | 121.2799 | 121.2936 | 104.1779 | -121.5546
1787.4688 | 121.4493 | -118.6615 | 2.7832 | 0.0066373 | 0.007746 | 0.072702 | 0.0019204 | 0.064711 | 0.0052082 | -0.0018756 | -0.00068649 | 0.0021234 | 0.059757 | 0.0653 | -0.0027899 | -0.0080921 | 2.5772 | -117.6086 | -22.1146 | -118.3685 | 2.9205 | -118.5562 | -118.4692 | -118.9316 | -14.6805 | -118.8263 | 2.7237 | 2.7191 | -118.6661 | -118.8446 | 0.10529 | 0.19226 | 0.13733 | 1.0529 | 0.29297 | 0.10071 | -0.20599 | -0.004578 | -0.1831 | -0.059509 | -0.27008 | -0.16479 | 0.01831 | -0.064087 | 121.582 | 121.2387 | 96.5469 | -121.2524 | 121.3852 | 121.3806 | 103.981 | -121.6278
1789.1719 | 121.4127 | -118.9957 | 2.449 | -0.00099167 | 0.0062506 | 0.068644 | 0.0029886 | 0.063002 | 0.0043536 | -0.00080744 | 0.0069425 | 0.00084176 | 0.061466 | 0.065941 | -0.0057807 | -0.0085193 | 2.1561 | -118.0389 | -22.5037 | -118.8309 | 2.4719 | -119.0048 | -118.9316 | -119.2657 | -14.9323 | -119.1422 | 2.3987 | 2.4033 | -119.0506 | -119.22 | -0.009155 | 0.064087 | 0.022888 | 0.95673 | 0.16479 | 0.10071 | -0.29297 | -0.054931 | -0.2243 | -0.050354 | -0.27008 | -0.14648 | 0.07782 | -0.045777 | 121.4676 | 121.1517 | 96.492 | -121.3806 | 121.3943 | 121.3989 | 104.0634 | -121.669
1790.9219 | 121.4127 | -119.989 | 1.4465 | 0.0066373 | 0.011378 | 0.072702 | 0.003843 | 0.064711 | -0.0041912 | -0.0020892 | 0.0069425 | -0.0019354 | 0.061466 | 0.064019 | -0.0072759 | -0.0072375 | 1.2314 | -118.8446 | -22.9248 | -119.7601 | 1.4374 | -119.9982 | -119.8654 | -120.1813 | -15.1932 | -120.0027 | 1.3687 | 1.3687 | -120.0256 | -120.1859 | -0.009155 | 0.1236 | -0.009155 | 1.1444 | 0.22888 | 0.10528 | -0.21515 | -0.036621 | -0.19684 | -0.07782 | -0.19226 | -0.013733 | 0.1831 | -0.07782 | 121.4264 | 121.2204 | 97.0642 | -121.3119 | 121.3577 | 121.3577 | 104.7958 | -121.6324
1792.6719 | 121.4493 | -120.2637 | 1.1444 | 0.0066373 | 0.014796 | 0.072489 | 0.0051248 | 0.061293 | 0.0020038 | -0.0025164 | 0.0069425 | -0.002149 | 0.059116 | 0.063378 | -0.0044989 | -0.0065967 | 0.97961 | -119.1788 | -23.1628 | -120.0394 | 1.1627 | -120.2728 | -120.1996 | -120.4605 | -15.4175 | -120.2866 | 1.0666 | 1.0757 | -120.3094 | -120.4468 | -0.009155 | 0.064087 | 0.018311 | 1.0849 | 0.2243 | 0.16022 | -0.1648 | -0.045776 | -0.1831 | -0.07782 | -0.19684 | -0.022888 | 0.16022 | -0.068664 | 121.4264 | 121.2433 | 97.1008 | -121.344 | 121.3303 | 121.3394 | 104.8462 | -121.5912
1794.3594 | 121.4127 | -120.6985 | 0.7782 | -0.00099167 | 0.013727 | 0.075479 | 0.0042702 | 0.060011 | -0.0016278 | -0.0025164 | -0.00068649 | -0.0015082 | 0.060611 | 0.064232 | -0.0081305 | -0.0044605 | 0.55847 | -119.5679 | -23.4421 | -120.4697 | 0.76904 | -120.6711 | -120.575 | -120.8954 | -15.6738 | -120.7077 | 0.68207 | 0.70496 | -120.694 | -120.8679 | 0.027465 | 0.1236 | -0.009155 | 1.1307 | 0.22888 | 0.10528 | -0.21973 | 0.004577 | -0.16937 | -0.09613 | -0.19684 | -0.009156 | 0.16022 | -0.073242 | 121.4676 | 121.257 | 97.2565 | -121.3531 | 121.3806 | 121.4035 | 105.0247 | -121.6461
1796.1094 | 121.4218 | -120.8176 | 0.69122 | 0.0066373 | 0.0062506 | 0.068644 | 0.0066202 | 0.063215 | 0.0039264 | 0.00026056 | -0.00068649 | 0.00041436 | 0.063175 | 0.065941 | -0.0049261 | -0.0072375 | 0.42114 | -119.7922 | -23.6298 | -120.6024 | 0.72327 | -120.813 | -120.7031 | -121.0464 | -16.0492 | -120.9045 | 0.63171 | 0.63171 | -120.8221 | -121.019 | 0.004578 | 0.11444 | 0.032044 | 1.0254 | 0.21515 | 0.10071 | -0.27008 | -0.004578 | -0.20142 | -0.059509 | -0.22888 | -0.086975 | 0.11444 | -0.059509 | 121.5408 | 121.2387 | 97.1878 | -121.3943 | 121.4493 | 121.4493 | 104.7684 | -121.7102
1797.8281 | 121.4767 | -120.8313 | 0.64087 | 0.014267 | 0.0036872 | 0.072489 | 0.007261 | 0.063215 | 0.0052082 | -0.0020892 | -0.015945 | -0.00065364 | 0.063175 | 0.065514 | -0.0068487 | -0.0083057 | 0.40741 | -119.7556 | -23.9731 | -120.6253 | 0.66376 | -120.8267 | -120.7535 | -121.051 | -16.2231 | -120.9229 | 0.58594 | 0.60883 | -120.8771 | -121.051 | 0.004578 | 0.07782 | 0.022888 | 1.0757 | 0.20599 | 0.12817 | -0.23346 | -0.045776 | -0.21973 | -0.054932 | -0.21973 | -0.091553 | 0.12817 | -0.032043 | 121.4951 | 121.2387 | 96.8582 | -121.3943 | 121.4172 | 121.4401 | 104.6082 | -121.6919
1799.5312 | 121.4539 | -120.8771 | 0.60425 | 0.0066373 | 0.0064642 | 0.071207 | 0.0061928 | 0.063002 | 0.0022174 | -0.0029436 | 0.022202 | -0.0012946 | 0.062107 | 0.065941 | -0.0042853 | -0.0061695 | 0.3479 | -119.8151 | -23.996 | -120.6757 | 0.63171 | -120.8862 | -120.813 | -121.1151 | -16.4337 | -120.9686 | 0.54474 | 0.54932 | -120.9045 | -121.0739 | -0.009155 | 0.064087 | 0.027466 | 1.062 | 0.20142 | 0.13733 | -0.25635 | -0.027466 | -0.19684 | -0.059509 | -0.23804 | -0.091553 | 0.10529 | -0.054932 | 121.5088 | 121.225 | 96.8811 | -121.4172 | 121.4218 | 121.4264 | 104.4434 | -121.6782
1801.2812 | 121.4081 | -120.9091 | 0.59967 | -0.00099167 | 0.012232 | 0.074198 | 0.0057656 | 0.064924 | -0.0044048 | -0.0025164 | 0.022202 | -0.0051398 | 0.058475 | 0.0653 | -0.0091985 | -0.0055285 | 0.3479 | -119.7372 | -24.0509 | -120.6573 | 0.59052 | -120.8817 | -120.7901 | -121.0876 | -16.5298 | -120.8862 | 0.49439 | 0.52643 | -120.9 | -121.0693 | 0.027466 | 0.11902 | -0.009155 | 1.1719 | 0.25177 | 0.13275 | -0.25177 | 0.009156 | -0.16022 | -0.10529 | -0.17853 | 0.022889 | 0.18311 | -0.073242 | 121.4996 | 121.257 | 96.8582 | -121.3898 | 121.4035 | 121.4355 | 104.3793 | -121.669
1802.9531 | 121.5683 | -120.8771 | 0.55389 | 0.0066373 | 0.0030464 | 0.069498 | 0.0057656 | 0.063429 | 0.0034992 | -0.0040118 | 0.0069425 | -0.00022644 | 0.061893 | 0.064873 | -0.0074897 | -0.0093737 | 0.3067 | -119.8517 | -24.2432 | -120.7077 | 0.61798 | -120.9457 | -120.8359 | -121.1288 | -16.7175 | -120.9869 | 0.50354 | 0.54016 | -120.9366 | -121.1151 | -0.068665 | 0.041199 | 0.064087 | 1.0254 | 0.16937 | 0.12817 | -0.24719 | -0.059509 | -0.23804 | -0.050354 | -0.25177 | -0.10986 | 0.12817 | -0.013733 | 121.4951 | 121.1838 | 96.6339 | -121.3898 | 121.3806 | 121.4172 | 104.1595 | -121.669
1804.6875 | 121.4264 | -120.3415 | 0.99792 | 0.0066373 | 0.010737 | 0.073771 | 0.0066202 | 0.062788 | -0.0063274 | -0.0023028 | 0.014572 | -0.0044988 | 0.062107 | 0.067009 | -0.011976 | -0.0042467 | 0.73242 | -119.3573 | -24.1974 | -120.2316 | 1.0117 | -120.3873 | -120.314 | -120.6436 | -16.7404 | -120.4285 | 0.90179 | 0.94299 | -120.433 | -120.5933 | -0.045776 | 0.027466 | 0.013733 | 0.98419 | 0.10986 | 0.082398 | -0.2655 | -0.091552 | -0.25177 | -0.096131 | -0.30212 | -0.086975 | 0.16479 | -0.054932 | 121.3531 | 121.0739 | 96.1441 | -121.312 | 121.2433 | 121.2845 | 103.6011 | -121.5912
1806.4375 | 121.5775 | -120.2866 | 1.0803 | 0.0066373 | 0.0058234 | 0.070353 | 0.007261 | 0.062361 | 0.0015766 | -0.0031574 | 0.014572 | -0.0015082 | 0.061679 | 0.065941 | -0.0070623 | -0.0093737 | 0.79651 | -119.3298 | -24.6277 | -120.1767 | 1.1536 | -120.3781 | -120.2637 | -120.5795 | -16.9693 | -120.4422 | 1.062 | 1.0666 | -120.4102 | -120.5658 | -0.091553 | 0.022888 | 0.073242 | 0.95673 | 0.10986 | 0.086975 | -0.28381 | -0.1236 | -0.27924 | -0.01831 | -0.29297 | -0.15564 | 0.1236 | -0.013733 | 121.4401 | 121.0831 | 95.6589 | -121.344 | 121.3486 | 121.3531 | 103.3173 | -121.6461
1808.1562 | 121.5958 | -120.6162 | 0.75989 | 0.021896 | 0.006037 | 0.070993 | 0.0053384 | 0.064283 | 0.0028584 | -0.0046526 | -0.00068649 | -0.0025762 | 0.062534 | 0.063805 | -0.0064215 | -0.0078783 | 0.48523 | -119.6182 | -24.7925 | -120.5017 | 0.81482 | -120.7077 | -120.6253 | -120.8862 | -17.2989 | -120.7581 | 0.74616 | 0.75073 | -120.7352 | -120.9045 | -0.091553 | -0.009155 | 0.054931 | 0.99793 | 0.11444 | 0.1236 | -0.27466 | -0.11902 | -0.28839 | -0.013733 | -0.27008 | -0.14191 | 0.14648 | -0.009156 | 121.431 | 121.1014 | 95.8237 | -121.3852 | 121.3623 | 121.3669 | 103.3173 | -121.6644
1809.8281 | 121.4767 | -120.7809 | 0.66834 | 0.0066373 | 0.010737 | 0.075693 | 0.0070474 | 0.061293 | -0.006541 | -0.0040118 | -0.00068649 | -0.005567 | 0.058902 | 0.061669 | -0.010053 | -0.0025379 | 0.38452 | -119.7098 | -25.1129 | -120.5978 | 0.68665 | -120.7947 | -120.694 | -121.0098 | -17.5186 | -120.8084 | 0.58136 | 0.59509 | -120.8313 | -120.9869 | -0.013733 | 0.086975 | 0.018311 | 1.0712 | 0.18311 | 0.096131 | -0.28381 | -0.050354 | -0.20599 | -0.086975 | -0.22888 | -0.027466 | 0.17853 | -0.073242 | 121.4676 | 121.1655 | 95.668 | -121.3623 | 121.3623 | 121.376 | 103.2623 | -121.6553
1811.5469 | 121.5775 | -120.813 | 0.59052 | -0.00099167 | 0.011591 | 0.074198 | 0.0093972 | 0.065351 | -0.0044048 | -0.003371 | -0.00068649 | -0.005567 | 0.060825 | 0.063805 | -0.010694 | -0.0072375 | 0.4303 | -119.6548 | -25.5249 | -120.6116 | 0.62714 | -120.8359 | -120.7352 | -121.0052 | -17.7521 | -120.8084 | 0.53101 | 0.57678 | -120.8588 | -120.9915 | -0.022888 | 0.07782 | 0.036621 | 1.1581 | 0.20142 | 0.1236 | -0.16022 | -0.045777 | -0.17853 | -0.059509 | -0.19226 | 0.004577 | 0.1831 | -0.013733 | 121.4401 | 121.2433 | 95.2881 | -121.3257 | 121.344 | 121.3898 | 103.0609 | -121.582
1813.2344 | 121.5591 | -120.7901 | 0.65002 | -0.00099167 | 0.006037 | 0.069925 | 0.0076882 | 0.061934 | 0.0022174 | -0.0018756 | 0.014572 | -1.2844e-05 | 0.062748 | 0.064446 | -0.0047125 | -0.010442 | 0.42114 | -119.7235 | -25.7309 | -120.6116 | 0.70038 | -120.8267 | -120.7352 | -121.0052 | -18.0496 | -120.8954 | 0.60883 | 0.61798 | -120.8313 | -121.0281 | -0.036621 | 0.054932 | 0.050354 | 1.0666 | 0.17853 | 0.1236 | -0.22888 | -0.041199 | -0.23804 | -0.041198 | -0.21515 | -0.10529 | 0.13275 | -0.032043 | 121.4905 | 121.2112 | 95.0592 | -121.3852 | 121.3989 | 121.4081 | 102.7405 | -121.6782
1814.9531 | 121.4996 | -120.8359 | 0.66376 | 0.0066373 | 0.0096686 | 0.071634 | 0.0032022 | 0.062788 | 0.001363 | -0.0046526 | 0.0069425 | -0.00065364 | 0.063175 | 0.066155 | -0.0053533 | -0.0055285 | 0.32959 | -119.8196 | -25.9964 | -120.6848 | 0.70496 | -120.8542 | -120.7626 | -121.0739 | -18.3289 | -120.9457 | 0.59967 | 0.61798 | -120.8817 | -121.0373 | -0.018311 | 0.073242 | 0.041199 | 1.0162 | 0.15106 | 0.07782 | -0.33417 | -0.045777 | -0.20142 | -0.064087 | -0.23804 | -0.10986 | 0.091552 | -0.045776 | 121.5408 | 121.1655 | 94.8395 | -121.4264 | 121.4355 | 121.4539 | 102.507 | -121.701
1816.6406 | 121.4493 | -120.9045 | 0.61798 | -0.00099167 | 0.0058234 | 0.069712 | 0.0036294 | 0.063856 | 0.0022174 | -0.0012346 | -0.00068649 | 0.00062796 | 0.059543 | 0.065728 | -0.0064215 | -0.0059557 | 0.28839 | -119.8883 | -26.2894 | -120.7581 | 0.62714 | -120.9183 | -120.8496 | -121.1517 | -18.6356 | -121.0464 | 0.54932 | 0.58136 | -120.9366 | -121.138 | -0.013733 | 0.054932 | 0.009155 | 1.0162 | 0.14648 | 0.091552 | -0.32959 | -0.032043 | -0.23346 | -0.068665 | -0.24719 | -0.14191 | 0.091552 | -0.036621 | 121.5317 | 121.1929 | 94.6152 | -121.4676 | 121.4539 | 121.4859 | 102.269 | -121.756
1818.3281 | 121.4767 | -120.9412 | 0.6134 | 0.0066373 | 0.0064642 | 0.069498 | 0.0053384 | 0.064711 | 0.0039264 | -0.00016664 | 0.014572 | 0.002978 | 0.059757 | 0.0653 | -0.0053533 | -0.0072375 | 0.32959 | -119.8334 | -26.3489 | -120.7214 | 0.61798 | -120.9366 | -120.8359 | -121.138 | -18.8141 | -121.0327 | 0.5127 | 0.55389 | -120.9595 | -121.1105 | 0.004578 | 0.10529 | 0.004578 | 1.1078 | 0.21973 | 0.11444 | -0.28381 | -0.018311 | -0.16937 | -0.10071 | -0.19684 | -0.091553 | 0.07782 | -0.059509 | 121.5591 | 121.2708 | 94.5923 | -121.4493 | 121.4539 | 121.4951 | 102.1271 | -121.7239
1820.0938 | 121.4493 | -120.9412 | 0.54932 | 0.014267 | 0.012873 | 0.071207 | 0.0042702 | 0.065565 | -0.0033368 | -0.00038024 | 0.014572 | -0.0036444 | 0.057621 | 0.063591 | -0.0079169 | -0.0055285 | 0.33875 | -119.783 | -26.5366 | -120.7077 | 0.55389 | -120.9503 | -120.8405 | -121.0876 | -18.8553 | -120.932 | 0.45319 | 0.49439 | -120.9549 | -121.1334 | -0.009155 | 0.10071 | 0.004578 | 1.1581 | 0.23346 | 0.13275 | -0.21057 | -0.013733 | -0.19226 | -0.09613 | -0.14648 | 0.009155 | 0.20142 | -0.054931 | 121.4951 | 121.2799 | 94.4046 | -121.3898 | 121.3943 | 121.4355 | 102.0859 | -121.6827
1821.7812 | 121.5912 | -120.9457 | 0.49896 | -0.00099167 | 0.0071052 | 0.069925 | 0.0083292 | 0.061506 | 0.0011494 | -0.0042254 | -0.00068649 | -0.0017218 | 0.061893 | 0.065941 | -0.0091985 | -0.0053149 | 0.25177 | -119.9203 | -26.7471 | -120.7809 | 0.55847 | -121.0007 | -120.9137 | -121.1746 | -19.0704 | -121.0693 | 0.4715 | 0.50812 | -121.0236 | -121.1929 | -0.054931 | 0.032044 | 0.05951 | 1.0254 | 0.16479 | 0.13275 | -0.24719 | -0.07782 | -0.24719 | -0.027465 | -0.22888 | -0.1236 | 0.1236 | 0.009156 | 121.5042 | 121.1975 | 94.1986 | -121.4127 | 121.4172 | 121.4539 | 101.8753 | -121.6919
1823.5156 | 121.5546 | -120.9824 | 0.4715 | 0.014267 | 0.0090278 | 0.072489 | 0.011106 | 0.061506 | -0.0024822 | -0.0048662 | 0.0069425 | -0.0044988 | 0.06467 | 0.064659 | -0.011549 | -0.0070239 | 0.27008 | -119.8471 | -26.8295 | -120.7855 | 0.51727 | -121.0052 | -120.9183 | -121.1563 | -19.1528 | -120.9915 | 0.40741 | 0.45776 | -121.0785 | -121.225 | -0.022888 | 0.064087 | 0.045776 | 1.1353 | 0.19684 | 0.13275 | -0.20142 | -0.09613 | -0.24262 | -0.064087 | -0.17395 | -0.009155 | 0.23346 | -0.013733 | 121.4996 | 121.2524 | 94.1528 | -121.3898 | 121.3898 | 121.4401 | 101.8295 | -121.6965
1825.1875 | 121.4539 | -121.0556 | 0.44861 | 0.014267 | 0.012873 | 0.073771 | 0.0059792 | 0.065138 | -0.0022686 | -0.0025164 | -0.00068649 | -0.0042852 | 0.061252 | 0.062523 | -0.0068487 | -0.0076647 | 0.24719 | -119.8791 | -26.9531 | -120.8267 | 0.45776 | -121.0373 | -120.9503 | -121.1884 | -19.2764 | -121.0739 | 0.37079 | 0.39368 | -121.1014 | -121.2524 | 0.018311 | 0.10529 | 0.009156 | 1.1765 | 0.22888 | 0.1236 | -0.20142 | -0.045776 | -0.19684 | -0.077819 | -0.13275 | -0.018311 | 0.17853 | -0.054931 | 121.5134 | 121.3028 | 94.1025 | -121.3989 | 121.4264 | 121.4493 | 101.7792 | -121.701
1826.875 | 121.5408 | -121.0602 | 0.44403 | -0.0086212 | 0.007746 | 0.070353 | 0.0040566 | 0.06407 | 0.0022174 | -0.0055072 | 0.0069425 | -0.00065364 | 0.060825 | 0.0653 | -0.0021491 | -0.0063831 | 0.21515 | -119.9478 | -27.1545 | -120.8633 | 0.48065 | -121.0648 | -120.9961 | -121.2387 | -19.5877 | -121.1609 | 0.37994 | 0.41657 | -121.1014 | -121.2753 | -0.004577 | 0.064087 | 0.036621 | 1.1124 | 0.19684 | 0.13275 | -0.22888 | -0.041198 | -0.21515 | -0.064087 | -0.17853 | -0.10071 | 0.11444 | -0.027466 | 121.5408 | 121.2753 | 93.9056 | -121.4401 | 121.4401 | 121.4767 | 101.4725 | -121.7194
1828.5781 | 121.4767 | -121.0602 | 0.44403 | -0.0086212 | 0.010737 | 0.069284 | 0.0036294 | 0.061934 | -0.0026958 | -0.00080744 | -0.008316 | -0.002149 | 0.058689 | 0.063805 | -0.0068487 | -0.0078783 | 0.24719 | -119.8837 | -27.3926 | -120.8267 | 0.44403 | -121.0922 | -120.9686 | -121.1838 | -19.9081 | -121.0556 | 0.35706 | 0.37994 | -121.0785 | -121.2433 | -0.032043 | 0.091553 | 0 | 1.1765 | 0.23346 | 0.14191 | -0.19684 | -0.01831 | -0.1831 | -0.086975 | -0.1236 | 0.004578 | 0.18768 | -0.064087 | 121.5042 | 121.3074 | 93.6676 | -121.4127 | 121.4172 | 121.4401 | 101.152 | -121.6873
1830.2812 | 121.5179 | -121.0739 | 0.4303 | 0.021896 | 0.012873 | 0.072489 | 0.0053384 | 0.063002 | 0.001363 | -0.001662 | 0.014572 | -0.003858 | 0.062107 | 0.065087 | -0.0077033 | -0.0098009 | 0.21973 | -119.9249 | -27.5299 | -120.8542 | 0.44861 | -121.0785 | -120.9824 | -121.2112 | -20.0775 | -121.0831 | 0.34332 | 0.36621 | -121.1197 | -121.2662 | -0.004577 | 0.091553 | 0.01831 | 1.149 | 0.21973 | 0.12817 | -0.21057 | -0.045776 | -0.19226 | -0.086975 | -0.13733 | -0.009155 | 0.18311 | -0.064087 | 121.5225 | 121.2936 | 93.544 | -121.4127 | 121.4172 | 121.4401 | 100.9964 | -121.6965
1831.9688 | 121.6095 | -121.051 | 0.41199 | 0.0066373 | 0.0068916 | 0.068857 | 0.0076882 | 0.06172 | -0.00034604 | -0.00273 | 0.014572 | -0.00044004 | 0.064243 | 0.064659 | -0.0096259 | -0.0080921 | 0.1236 | -120.0577 | -27.8091 | -120.9549 | 0.48065 | -121.1472 | -121.0556 | -121.3211 | -20.3842 | -121.2204 | 0.40283 | 0.39825 | -121.1792 | -121.3211 | -0.096131 | -0.004578 | 0.068665 | 0.99335 | 0.09613 | 0.10071 | -0.28839 | -0.12817 | -0.27008 | -0.009155 | -0.27008 | -0.16937 | 0.10071 | -0.013733 | 121.5317 | 121.1746 | 93.2419 | -121.4676 | 121.4539 | 121.4493 | 100.6668 | -121.7331
1833.6406 | 121.4951 | -121.0968 | 0.41657 | 0.0066373 | 0.013514 | 0.074625 | 0.0042702 | 0.063002 | -0.002055 | -0.001662 | 0.0069425 | -0.0040716 | 0.059757 | 0.065941 | -0.0085577 | -0.0076647 | 0.22888 | -119.9203 | -27.832 | -120.8679 | 0.41657 | -121.0922 | -121.0098 | -121.2112 | -20.5444 | -121.106 | 0.32044 | 0.3479 | -121.1197 | -121.2936 | 0.004578 | 0.086975 | 0 | 1.1765 | 0.22888 | 0.14191 | -0.18768 | -0.022888 | -0.19684 | -0.09613 | -0.11444 | -0.009155 | 0.18768 | -0.068665 | 121.5134 | 121.3257 | 93.2648 | -121.4264 | 121.4172 | 121.4447 | 100.5524 | -121.7102
1835.3594 | 121.4996 | -121.1426 | 0.42572 | 0.0066373 | 0.0075324 | 0.072275 | 0.003843 | 0.062574 | 0.002431 | -0.0029436 | 0.014572 | 0.00041436 | 0.061679 | 0.065941 | -0.0059943 | -0.0072375 | 0.17395 | -120.0119 | -28.0838 | -120.9457 | 0.46234 | -121.1334 | -121.0419 | -121.3028 | -20.8191 | -121.2433 | 0.35706 | 0.37994 | -121.1792 | -121.344 | 0.009155 | 0.10071 | 0.036621 | 1.1307 | 0.19684 | 0.09613 | -0.25177 | -0.036621 | -0.20142 | -0.068664 | -0.16022 | -0.10071 | 0.10071 | -0.045776 | 121.6049 | 121.3165 | 93.0588 | -121.4676 | 121.4996 | 121.5225 | 100.3235 | -121.7697
1837.0469 | 121.6049 | -121.1014 | 0.40283 | 0.0066373 | 0.011805 | 0.073557 | 0.0074746 | 0.064924 | -0.0061138 | -0.004439 | 0.0069425 | -0.0044988 | 0.061252 | 0.0653 | -0.011335 | -0.0085193 | 0.20599 | -119.902 | -28.1799 | -120.8679 | 0.41657 | -121.1197 | -121.0419 | -121.2341 | -20.9518 | -121.106 | 0.31586 | 0.33417 | -121.1517 | -121.3211 | -0.018311 | 0.059509 | 0.013733 | 1.1993 | 0.23346 | 0.17395 | -0.19684 | -0.050354 | -0.21973 | -0.086975 | -0.13275 | -0.004578 | 0.21515 | -0.068665 | 121.5179 | 121.3074 | 92.9214 | -121.4447 | 121.4172 | 121.4355 | 100.1495 | -121.7239
1838.7188 | 121.5546 | -121.1014 | 0.4303 | -0.00099167 | 0.012018 | 0.072702 | 0.0042702 | 0.061293 | 0.0015766 | -0.0023028 | 0.014572 | -0.00086724 | 0.05997 | 0.067223 | -0.0049261 | -0.0072375 | 0.12817 | -120.076 | -28.4683 | -120.9869 | 0.4715 | -121.17 | -121.0602 | -121.3165 | -21.1945 | -121.2341 | 0.36163 | 0.35248 | -121.1929 | -121.3257 | -0.068665 | 0.041198 | 0.041199 | 1.0254 | 0.11444 | 0.073243 | -0.30212 | -0.091553 | -0.22431 | -0.068665 | -0.21515 | -0.13275 | 0.091553 | -0.07782 | 121.5729 | 121.2296 | 92.6331 | -121.4905 | 121.463 | 121.4539 | 99.9069 | -121.756
1840.4688 | 121.5225 | -121.1105 | 0.42114 | 0.0066373 | 0.0098822 | 0.071421 | 0.0059792 | 0.062574 | -0.00077324 | -0.0031574 | 0.0069425 | -0.002149 | 0.061679 | 0.064446 | -0.0066351 | -0.0063831 | 0.20599 | -119.9478 | -28.6377 | -120.8954 | 0.41657 | -121.1426 | -121.0281 | -121.2204 | -21.3501 | -121.1288 | 0.30212 | 0.33875 | -121.1609 | -121.2982 | -0.032043 | 0.082398 | -0.004578 | 1.1627 | 0.21515 | 0.13275 | -0.21515 | -0.050354 | -0.18768 | -0.11902 | -0.10986 | -0.01831 | 0.16937 | -0.082398 | 121.5271 | 121.3165 | 92.4728 | -121.4493 | 121.4127 | 121.4493 | 99.7604 | -121.7194
1842.2031 | 121.5134 | -121.1655 | 0.40741 | 0.0066373 | 0.016291 | 0.067789 | 0.0051248 | 0.064497 | 0.004781 | -0.0025164 | 0.0069425 | 0.00062796 | 0.063602 | 0.066368 | -0.0059943 | -0.0098009 | 0.10529 | -120.0851 | -28.9719 | -120.9915 | 0.4303 | -121.1426 | -121.0876 | -121.3303 | -21.5515 | -121.3028 | 0.3479 | 0.36163 | -121.2158 | -121.3852 | 0.022888 | 0.07782 | 0.022888 | 1.0803 | 0.17395 | 0.09613 | -0.30212 | -0.050354 | -0.21973 | -0.05951 | -0.16479 | -0.13733 | 0.082398 | -0.045777 | 121.5958 | 121.2708 | 92.1936 | -121.4951 | 121.5134 | 121.5271 | 99.614 | -121.7926
1843.875 | 121.5591 | -121.1517 | 0.38452 | -0.00099167 | 0.011378 | 0.075266 | 0.0066202 | 0.059797 | -0.0039776 | -0.0057208 | 0.0069425 | -0.0068488 | 0.058902 | 0.063378 | -0.011121 | -0.0080921 | 0.11902 | -120.0256 | -29.1504 | -120.9457 | 0.41199 | -121.1609 | -121.0419 | -121.2982 | -21.817 | -121.1655 | 0.32044 | 0.33875 | -121.1792 | -121.3943 | -0.009156 | 0.10986 | 0.027466 | 1.1261 | 0.20599 | 0.09613 | -0.2655 | -0.027466 | -0.24262 | -0.064086 | -0.14649 | -0.013733 | 0.22888 | -0.045776 | 121.5637 | 121.2708 | 92.0013 | -121.4264 | 121.4722 | 121.4905 | 99.3347 | -121.7789
1845.5625 | 121.6003 | -121.1288 | 0.37537 | 0.014267 | 0.0083868 | 0.073343 | 0.0079018 | 0.063643 | -0.0022686 | -0.0057208 | -0.00068649 | -0.0012946 | 0.062107 | 0.064659 | -0.0083441 | -0.0091601 | 0.17395 | -119.9295 | -29.1092 | -120.9274 | 0.38452 | -121.1517 | -121.0602 | -121.2662 | -21.9315 | -121.1472 | 0.31128 | 0.34332 | -121.1838 | -121.3394 | -0.022888 | 0.068664 | 0.009155 | 1.1993 | 0.20142 | 0.13275 | -0.20142 | -0.054932 | -0.21057 | -0.064087 | -0.13733 | -0.018311 | 0.19226 | -0.032043 | 121.5134 | 121.3028 | 92.0197 | -121.4355 | 121.4401 | 121.4722 | 99.1974 | -121.7148
1847.2344 | 121.5683 | -121.138 | 0.39825 | -0.00099167 | 0.012873 | 0.071421 | 0.0029886 | 0.062574 | 0.004781 | -0.0018756 | 0.0069425 | 0.00084176 | 0.060825 | 0.064232 | -0.0057807 | -0.0080921 | 0.10071 | -120.0943 | -29.5532 | -121.0098 | 0.45776 | -121.1609 | -121.106 | -121.344 | -22.403 | -121.2982 | 0.34332 | 0.37994 | -121.2296 | -121.3943 | -0.022889 | 0.032043 | 0.05951 | 1.0437 | 0.12817 | 0.09613 | -0.29755 | -0.091553 | -0.25635 | -0.054931 | -0.20599 | -0.16022 | 0.09613 | -0.01831 | 121.5958 | 121.2387 | 91.5848 | -121.5042 | 121.4813 | 121.5179 | 98.735 | -121.7926
1848.9219 | 121.5454 | -121.1929 | 0.3891 | 0.0066373 | 0.0051826 | 0.069925 | 0.0029886 | 0.065779 | 0.0022174 | -0.0020892 | 0.0069425 | 0.002337 | 0.062961 | 0.066368 | -0.0051397 | -0.0089465 | 0.13275 | -120.0531 | -29.6173 | -120.9915 | 0.4303 | -121.1838 | -121.0739 | -121.3394 | -22.5952 | -121.2891 | 0.34332 | 0.37079 | -121.2433 | -121.376 | 0.009155 | 0.11902 | 0.041199 | 1.1398 | 0.20142 | 0.082398 | -0.25635 | -0.050354 | -0.18311 | -0.045776 | -0.14648 | -0.09613 | 0.086976 | -0.01831 | 121.6232 | 121.3257 | 91.5756 | -121.463 | 121.5363 | 121.5637 | 98.5977 | -121.7651
1850.5938 | 121.6049 | -121.1426 | 0.36163 | -0.00099167 | 0.0088142 | 0.071634 | 0.0076882 | 0.065565 | -0.0041912 | -0.004439 | 0.014572 | -0.0047124 | 0.062748 | 0.065941 | -0.010267 | -0.0068103 | 0.17395 | -119.9341 | -29.686 | -120.932 | 0.40741 | -121.1746 | -121.0648 | -121.2936 | -22.7234 | -121.1838 | 0.32501 | 0.33417 | -121.2341 | -121.3898 | -0.032044 | 0.07782 | 0.045777 | 1.2085 | 0.21057 | 0.13275 | -0.18768 | -0.091553 | -0.24719 | -0.036621 | -0.15106 | -0.041199 | 0.20599 | -0.027466 | 121.55 | 121.3165 | 91.4566 | -121.4264 | 121.4676 | 121.4767 | 98.4192 | -121.7514
1852.2969 | 121.6553 | -121.1151 | 0.36163 | -0.00099167 | 0.012232 | 0.072916 | 0.0083292 | 0.062147 | -0.0044048 | -0.0025164 | 0.014572 | -0.0047124 | 0.060825 | 0.061669 | -0.011762 | -0.0068103 | 0.15106 | -119.9707 | -29.8553 | -120.9457 | 0.40741 | -121.1792 | -121.0876 | -121.2479 | -22.7966 | -121.1517 | 0.31586 | 0.32501 | -121.1884 | -121.3669 | -0.064087 | 0.027466 | 0.045777 | 1.1444 | 0.16937 | 0.14191 | -0.21057 | -0.073242 | -0.25177 | -0.045776 | -0.13275 | -0.036621 | 0.21515 | -0.036621 | 121.5225 | 121.2662 | 91.2598 | -121.4493 | 121.431 | 121.4401 | 98.3185 | -121.7285
1854.0156 | 121.6644 | -121.1472 | 0.37079 | -0.0086212 | 0.0068916 | 0.068216 | 0.0064066 | 0.063215 | 0.002431 | -0.0057208 | 0.014572 | 0.001269 | 0.061679 | 0.067009 | -0.0089849 | -0.0089465 | 0.10071 | -120.0989 | -30.2353 | -121.019 | 0.44861 | -121.2021 | -121.1151 | -121.3486 | -23.3688 | -121.2936 | 0.36163 | 0.36621 | -121.2524 | -121.3898 | -0.054931 | 0.032044 | 0.077819 | 1.0483 | 0.12817 | 0.09613 | -0.27008 | -0.10529 | -0.24262 | -0.009156 | -0.20142 | -0.14648 | 0.096131 | -0.004578 | 121.5958 | 121.2479 | 90.9119 | -121.4859 | 121.5088 | 121.5134 | 97.7783 | -121.7606
1855.7031 | 121.5775 | -121.1792 | 0.3891 | -0.0086212 | 0.011805 | 0.070993 | 0.00042505 | 0.063429 | 0.00029476 | -0.0018756 | -0.00068649 | -0.002149 | 0.061466 | 0.065087 | -0.0055671 | -0.0085193 | 0.19226 | -119.9753 | -30.336 | -120.9457 | 0.40283 | -121.1609 | -121.0693 | -121.225 | -23.3871 | -121.1792 | 0.3067 | 0.32501 | -121.2296 | -121.3486 | 0.01831 | 0.10986 | 0.013733 | 1.2039 | 0.23346 | 0.1236 | -0.19684 | -0.050354 | -0.16937 | -0.082397 | -0.045777 | 0 | 0.16937 | -0.064087 | 121.582 | 121.3715 | 90.8432 | -121.4584 | 121.4859 | 121.5042 | 97.7921 | -121.7377
1857.3906 | 121.5866 | -121.1884 | 0.37537 | -0.0086212 | 0.0090278 | 0.071848 | 0.0040566 | 0.064497 | 0.0020038 | -0.00273 | -0.00068649 | -0.00044004 | 0.059757 | 0.064873 | -0.0051397 | -0.0072375 | 0.12817 | -120.0394 | -30.5466 | -121.0052 | 0.42572 | -121.1975 | -121.1105 | -121.257 | -23.5016 | -121.2341 | 0.31128 | 0.34332 | -121.2387 | -121.3852 | -0.009156 | 0.077819 | 0.050354 | 1.149 | 0.1831 | 0.10529 | -0.24719 | -0.050354 | -0.19684 | -0.064087 | -0.068665 | -0.045777 | 0.15106 | -0.032043 | 121.6141 | 121.3165 | 90.6418 | -121.4859 | 121.4996 | 121.5317 | 97.6868 | -121.7606
1859.125 | 121.6782 | -121.1426 | 0.37079 | 0.0066373 | 0.010523 | 0.071421 | 0.0076882 | 0.061293 | -0.006541 | -0.0048662 | 0.0069425 | -0.0049262 | 0.062107 | 0.064873 | -0.012617 | -0.0078783 | 0.15106 | -119.9661 | -30.6702 | -120.9641 | 0.41199 | -121.2158 | -121.0922 | -121.257 | -23.6298 | -121.1655 | 0.28839 | 0.32044 | -121.2112 | -121.3806 | -0.073242 | 0.050354 | 0.041198 | 1.1765 | 0.17853 | 0.12817 | -0.21973 | -0.068665 | -0.23804 | -0.082398 | -0.11444 | -0.022888 | 0.21515 | -0.050354 | 121.5546 | 121.2936 | 90.4724 | -121.463 | 121.431 | 121.463 | 97.5128 | -121.7514
1860.8281 | 121.5912 | -121.1975 | 0.41657 | -0.00099167 | 0.010737 | 0.071207 | 0.0049112 | 0.062361 | 0.003072 | -0.0037982 | -0.00068649 | -0.0025762 | 0.061679 | 0.068932 | -0.0059943 | -0.0089465 | 0.1236 | -120.076 | -30.9082 | -121.0052 | 0.47607 | -121.1975 | -121.1105 | -121.3028 | -24.0051 | -121.2936 | 0.37537 | 0.37079 | -121.2479 | -121.3898 | 0 | 0.086975 | 0.059509 | 1.1215 | 0.19226 | 0.10529 | -0.29297 | -0.050354 | -0.19226 | -0.041199 | -0.10529 | -0.09613 | 0.096131 | -0.045776 | 121.6736 | 121.3211 | 90.2893 | -121.5271 | 121.5729 | 121.5683 | 97.1924 | -121.8063
1862.5156 | 121.55 | -121.2021 | 0.41657 | -0.0086212 | 0.01095 | 0.068644 | 0.0040566 | 0.063002 | 0.001363 | -0.0020892 | 0.0069425 | 0.00041436 | 0.059757 | 0.065941 | -0.0038581 | -0.0074511 | 0.086975 | -120.108 | -31.0822 | -121.0464 | 0.43945 | -121.2204 | -121.1426 | -121.3669 | -24.2615 | -121.3348 | 0.35248 | 0.35706 | -121.257 | -121.431 | -0.018311 | 0.059509 | 0.022888 | 1.0941 | 0.15564 | 0.09613 | -0.32959 | -0.054932 | -0.22888 | -0.064087 | -0.16479 | -0.13275 | 0.09613 | -0.059509 | 121.6415 | 121.2891 | 90.1199 | -121.5591 | 121.5546 | 121.5591 | 96.9406 | -121.8475
1864.2188 | 121.5546 | -121.2204 | 0.37079 | 0.014267 | 0.011591 | 0.075693 | 0.0053384 | 0.058302 | -0.0039776 | -0.0055072 | 0.0069425 | -0.0062078 | 0.060398 | 0.063805 | -0.011549 | -0.0057421 | 0.10986 | -120.0256 | -31.1966 | -121.0236 | 0.37537 | -121.2112 | -121.1288 | -121.312 | -24.2523 | -121.2387 | 0.2655 | 0.29755 | -121.2845 | -121.4127 | 0.009155 | 0.091553 | 0.004577 | 1.1948 | 0.19684 | 0.10528 | -0.26093 | -0.064087 | -0.19226 | -0.10529 | -0.091553 | -0.01831 | 0.17395 | -0.073243 | 121.5958 | 121.3303 | 90.0238 | -121.4996 | 121.4859 | 121.5179 | 96.9681 | -121.7834
1865.9219 | 121.5408 | -121.2341 | 0.36163 | 0.0066373 | 0.0133 | 0.069712 | 0.0085428 | 0.062147 | -0.0026958 | -0.0048662 | 0.0069425 | -0.0036444 | 0.062107 | 0.065087 | -0.0089849 | -0.0070239 | 0.16022 | -120.0073 | -31.3202 | -121.0144 | 0.35706 | -121.1975 | -121.1288 | -121.3028 | -24.4629 | -121.2433 | 0.27466 | 0.29755 | -121.2799 | -121.431 | 0.036621 | 0.10529 | -0.004577 | 1.2268 | 0.21973 | 0.11444 | -0.20142 | -0.045776 | -0.19684 | -0.086975 | -0.068664 | -0.009155 | 0.18768 | -0.064087 | 121.5912 | 121.3943 | 89.9139 | -121.4905 | 121.5088 | 121.5317 | 96.7712 | -121.7926
1867.5938 | 121.7102 | -121.1792 | 0.34332 | 0.0066373 | 0.0075324 | 0.069925 | 0.007261 | 0.062574 | 0.0037128 | -0.003371 | -0.015945 | 0.0027644 | 0.065525 | 0.066155 | -0.0087713 | -0.0085193 | 0.082397 | -120.0989 | -31.6086 | -121.0602 | 0.41199 | -121.2616 | -121.1655 | -121.3531 | -24.7696 | -121.3303 | 0.33417 | 0.34332 | -121.3165 | -121.431 | -0.082398 | 0.013733 | 0.068664 | 1.0803 | 0.11902 | 0.10528 | -0.26093 | -0.13733 | -0.25177 | -0.009156 | -0.17395 | -0.15106 | 0.10071 | 0 | 121.5912 | 121.2616 | 89.5706 | -121.5088 | 121.5134 | 121.5225 | 96.4096 | -121.7743
1869.2812 | 121.6095 | -121.2524 | 0.37079 | -0.00099167 | 0.010737 | 0.074411 | 0.0049112 | 0.06407 | 0.0037128 | -0.0029436 | 0.0069425 | -0.0027898 | 0.060398 | 0.065087 | -0.0055671 | -0.0070239 | 0.16479 | -120.0119 | -31.7917 | -121.0098 | 0.38452 | -121.2387 | -121.1517 | -121.2662 | -24.9573 | -121.2341 | 0.25635 | 0.29297 | -121.2891 | -121.4264 | 0.013733 | 0.10071 | 0.013732 | 1.2405 | 0.24261 | 0.14191 | -0.20599 | -0.036621 | -0.17395 | -0.11444 | -0.013733 | 0.01831 | 0.19226 | -0.07782 | 121.637 | 121.4172 | 89.4608 | -121.5225 | 121.5088 | 121.5454 | 96.2952 | -121.7972
1871 | 121.6599 | -121.2158 | 0.33875 | 0.014267 | 0.0096686 | 0.070139 | 0.0046976 | 0.065992 | 0.0026446 | -0.0025164 | 0.022202 | -0.0010808 | 0.061039 | 0.065087 | -0.0036443 | -0.0051013 | 0.14191 | -120.0439 | -32.0389 | -121.0556 | 0.41199 | -121.257 | -121.1655 | -121.3165 | -25.058 | -121.344 | 0.28381 | 0.32501 | -121.312 | -121.4722 | -0.041199 | 0.050354 | 0.073242 | 1.1719 | 0.16022 | 0.10986 | -0.19684 | -0.096131 | -0.25635 | -0.054932 | -0.10071 | -0.12817 | 0.12817 | -0.013733 | 121.6278 | 121.3577 | 89.1769 | -121.5042 | 121.4996 | 121.5408 | 96.1578 | -121.8109
1872.7031 | 121.5775 | -121.2387 | 0.37079 | 0.0066373 | 0.011805 | 0.072702 | 0.0029886 | 0.065138 | -0.0012006 | -0.001662 | -0.00068649 | -0.0036444 | 0.05997 | 0.063164 | -0.0079169 | -0.0051013 | 0.17395 | -119.957 | -32.2083 | -121.0052 | 0.36163 | -121.2158 | -121.1151 | -121.2753 | -25.3601 | -121.2158 | 0.2655 | 0.29755 | -121.2936 | -121.4264 | 0.022888 | 0.1236 | -0.009156 | 1.2817 | 0.23346 | 0.10986 | -0.19684 | -0.054932 | -0.18768 | -0.10529 | -0.036622 | 0.022888 | 0.21057 | -0.073243 | 121.6003 | 121.4127 | 89.0305 | -121.4859 | 121.5042 | 121.5363 | 95.8786 | -121.7972
1874.4531 | 121.582 | -121.2708 | 0.37994 | 0.0066373 | 0.0096686 | 0.07078 | 0.003843 | 0.064711 | 0.0017902 | -0.0037982 | -0.00068649 | -1.2844e-05 | 0.062961 | 0.0653 | -0.0049261 | -0.0085193 | 0.11444 | -120.0577 | -32.4692 | -121.0693 | 0.39368 | -121.2845 | -121.1838 | -121.3531 | -25.7309 | -121.376 | 0.3067 | 0.33417 | -121.2891 | -121.4447 | -0.013733 | 0.086975 | 0.013733 | 1.2131 | 0.20142 | 0.11444 | -0.2655 | -0.01831 | -0.17395 | -0.073242 | -0.082397 | -0.10529 | 0.068664 | -0.045777 | 121.6644 | 121.3852 | 88.8016 | -121.5637 | 121.5775 | 121.6049 | 95.5399 | -121.8246
1876.1406 | 121.7102 | -121.2158 | 0.32959 | -0.00099167 | 0.0075324 | 0.073984 | 0.010038 | 0.065138 | -0.0056866 | -0.0046526 | -0.008316 | -0.003858 | 0.062534 | 0.062737 | -0.010694 | -0.0061695 | 0.14648 | -119.9432 | -32.579 | -121.0144 | 0.34332 | -121.2662 | -121.1563 | -121.2753 | -25.6256 | -121.2341 | 0.24719 | 0.27466 | -121.3028 | -121.4676 | -0.050354 | 0.059509 | 0.013733 | 1.2726 | 0.20142 | 0.14191 | -0.18311 | -0.086975 | -0.25177 | -0.082398 | -0.05951 | -0.018311 | 0.23346 | -0.054932 | 121.5591 | 121.3623 | 88.6368 | -121.4859 | 121.463 | 121.4905 | 95.5902 | -121.7972
1877.8281 | 121.5729 | -121.2708 | 0.35248 | 0.0066373 | 0.015009 | 0.075693 | 0.0040566 | 0.063002 | -0.00098684 | -0.0031574 | 0.014572 | -0.0019354 | 0.05933 | 0.065087 | -0.0085577 | -0.0087329 | 0.15106 | -119.9753 | -32.7438 | -121.0464 | 0.36163 | -121.257 | -121.1472 | -121.2891 | -26.0239 | -121.257 | 0.25177 | 0.27924 | -121.3028 | -121.4447 | 0.013733 | 0.1236 | 0.009155 | 1.2955 | 0.2243 | 0.10071 | -0.20142 | -0.032043 | -0.17395 | -0.10071 | -0.01831 | 0.013733 | 0.18768 | -0.073242 | 121.6324 | 121.4218 | 88.5269 | -121.4996 | 121.5225 | 121.55 | 95.2469 | -121.7972
1879.5469 | 121.6187 | -121.2753 | 0.34332 | 0.0066373 | 0.011164 | 0.070139 | 0.0034158 | 0.064283 | 0.00072196 | -0.0035846 | 0.0069425 | -0.0034308 | 0.058902 | 0.064873 | -0.0053533 | -0.0087329 | 0.15106 | -119.9936 | -32.9864 | -121.051 | 0.35248 | -121.2616 | -121.1746 | -121.2662 | -26.2482 | -121.2799 | 0.24261 | 0.2655 | -121.344 | -121.4722 | 0.013733 | 0.10071 | 0.009155 | 1.2817 | 0.22431 | 0.1236 | -0.19226 | -0.068664 | -0.19684 | -0.10071 | 0.009156 | -0.004577 | 0.19226 | -0.07782 | 121.6278 | 121.4264 | 88.2889 | -121.5179 | 121.5179 | 121.5408 | 95.0272 | -121.8155
1881.2344 | 121.7056 | -121.2479 | 0.32044 | 0.0066373 | 0.006037 | 0.06843 | 0.007261 | 0.061506 | 0.004781 | -0.0020892 | 0.0069425 | 0.001269 | 0.060825 | 0.0653 | -0.0064215 | -0.0089465 | 0.10986 | -120.0623 | -33.0734 | -121.0831 | 0.38452 | -121.312 | -121.1975 | -121.3348 | -26.445 | -121.3715 | 0.27924 | 0.3067 | -121.344 | -121.4996 | -0.064087 | 0.050354 | 0.064086 | 1.1856 | 0.1648 | 0.11444 | -0.21057 | -0.09613 | -0.25177 | -0.041199 | -0.086975 | -0.1236 | 0.12817 | -0.013733 | 121.6324 | 121.3577 | 88.1744 | -121.5179 | 121.5271 | 121.5546 | 94.8029 | -121.8201
1882.9062 | 121.5958 | -121.2982 | 0.33417 | 0.0066373 | 0.012232 | 0.074839 | 0.007261 | 0.062788 | -0.0046184 | -0.0037982 | 0.0069425 | -0.0044988 | 0.062107 | 0.064659 | -0.011335 | -0.0059557 | 0.073242 | -120.0485 | -33.2336 | -121.0968 | 0.3479 | -121.2799 | -121.1929 | -121.3531 | -26.4771 | -121.3074 | 0.25177 | 0.28839 | -121.3623 | -121.4722 | 0.018311 | 0.10529 | 0.013733 | 1.2497 | 0.20142 | 0.09613 | -0.26092 | -0.064087 | -0.17395 | -0.082397 | -0.054931 | -0.009155 | 0.16479 | -0.045776 | 121.6461 | 121.3715 | 88.0646 | -121.5271 | 121.55 | 121.5866 | 94.8212 | -121.8063
1884.6094 | 121.5912 | -121.3074 | 0.34332 | -0.0086212 | 0.0064642 | 0.068216 | 0.0070474 | 0.063002 | 0.004781 | -0.0031574 | 0.014572 | 0.00084176 | 0.064243 | 0.064659 | -0.0055671 | -0.0080921 | 0.09613 | -120.0851 | -33.49 | -121.1151 | 0.37079 | -121.2982 | -121.2662 | -121.3898 | -26.9119 | -121.4264 | 0.28839 | 0.29755 | -121.376 | -121.5134 | 0.009155 | 0.041199 | 0.027466 | 1.2222 | 0.19226 | 0.15106 | -0.24719 | -0.068665 | -0.20599 | -0.054932 | -0.082398 | -0.11902 | 0.086975 | -0.045777 | 121.6782 | 121.4035 | 87.8174 | -121.6095 | 121.5958 | 121.6049 | 94.3954 | -121.8567
1886.2969 | 121.6187 | -121.2753 | 0.34332 | -0.00099167 | 0.013941 | 0.073343 | 0.0068338 | 0.062361 | -0.0061138 | -0.0018756 | -0.00068649 | -0.0053534 | 0.062534 | 0.063164 | -0.0085577 | -0.0074511 | 0.059509 | -120.0348 | -33.6365 | -121.0968 | 0.35706 | -121.2936 | -121.2112 | -121.3577 | -26.9119 | -121.312 | 0.25635 | 0.27466 | -121.3577 | -121.4996 | -0.01831 | 0.064087 | 0.013733 | 1.2405 | 0.17853 | 0.11444 | -0.28381 | -0.082397 | -0.2243 | -0.086975 | -0.082397 | -0.036621 | 0.18768 | -0.068665 | 121.6324 | 121.3348 | 87.6389 | -121.5546 | 121.5317 | 121.55 | 94.3634 | -121.843
1887.9688 | 121.637 | -121.2936 | 0.33417 | 0.0066373 | 0.004328 | 0.068644 | 0.005552 | 0.064711 | 0.003072 | -0.0014484 | 0.0069425 | 0.00084176 | 0.061466 | 0.066796 | -0.0074897 | -0.010442 | 0.11902 | -120.0485 | -33.7326 | -121.1014 | 0.37994 | -121.312 | -121.2341 | -121.3348 | -27.1042 | -121.3989 | 0.27924 | 0.29297 | -121.344 | -121.5271 | -0.018311 | 0.059509 | 0.045777 | 1.2451 | 0.19226 | 0.13275 | -0.21515 | -0.050354 | -0.23346 | -0.054931 | -0.041199 | -0.10529 | 0.12817 | -0.041198 | 121.6736 | 121.4127 | 87.561 | -121.5683 | 121.5729 | 121.5866 | 94.1895 | -121.8613
1889.6562 | 121.6141 | -121.2891 | 0.37537 | 0.014267 | 0.0073188 | 0.068644 | 0.0036294 | 0.062361 | 0.00414 | -0.00016664 | -0.00068649 | 0.00084176 | 0.062534 | 0.066796 | -0.0042853 | -0.0068103 | 0.050354 | -120.1126 | -34.0027 | -121.1334 | 0.39368 | -121.3074 | -121.2204 | -121.3806 | -27.3331 | -121.4401 | 0.28839 | 0.32959 | -121.3715 | -121.5408 | -0.018311 | 0.068664 | 0.018311 | 1.1765 | 0.15564 | 0.086975 | -0.32501 | -0.082398 | -0.25177 | -0.086975 | -0.091553 | -0.15106 | 0.10071 | -0.045776 | 121.6827 | 121.3394 | 87.2864 | -121.5958 | 121.5775 | 121.6187 | 93.956 | -121.9162
1891.3281 | 121.6187 | -121.2845 | 0.35706 | -0.0086212 | 0.013941 | 0.072489 | 0.0049112 | 0.064283 | -0.0041912 | -0.001021 | 0.022202 | -0.0059942 | 0.060398 | 0.062737 | -0.01048 | -0.0055285 | 0.073242 | -120.0119 | -33.9935 | -121.0922 | 0.36621 | -121.2753 | -121.1884 | -121.3165 | -27.2232 | -121.3028 | 0.27924 | 0.28381 | -121.3303 | -121.5042 | 0.009155 | 0.096131 | 0.009155 | 1.2726 | 0.19226 | 0.09613 | -0.28381 | -0.045776 | -0.21973 | -0.07782 | -0.032043 | -0.01831 | 0.20142 | -0.073243 | 121.6507 | 121.3577 | 87.291 | -121.5454 | 121.5637 | 121.5683 | 94.0613 | -121.8613
1893 | 121.7148 | -121.257 | 0.32044 | -0.00099167 | 0.0058234 | 0.069284 | 0.0046976 | 0.062574 | 0.0034992 | -0.0040118 | 0.0069425 | -0.0019354 | 0.062961 | 0.066155 | -0.0049261 | -0.0072375 | 0.11444 | -120.0394 | -34.2407 | -121.0785 | 0.37994 | -121.2982 | -121.2387 | -121.3165 | -27.4887 | -121.3806 | 0.29755 | 0.32501 | -121.376 | -121.5042 | -0.041199 | 0.018311 | 0.059509 | 1.2177 | 0.17853 | 0.16022 | -0.20599 | -0.11902 | -0.24719 | -0.022889 | -0.059509 | -0.1236 | 0.1236 | 0.004577 | 121.637 | 121.3715 | 87.0163 | -121.5591 | 121.5546 | 121.582 | 93.7683 | -121.8246
1894.6875 | 121.701 | -121.2799 | 0.33875 | -0.0086212 | 0.009455 | 0.070353 | 0.0093972 | 0.061293 | -0.005473 | -0.0048662 | -0.00068649 | -0.0036444 | 0.060611 | 0.065087 | -0.0091985 | -0.0072375 | 0.11902 | -119.9478 | -34.4055 | -121.0785 | 0.36621 | -121.3028 | -121.2067 | -121.2891 | -27.6718 | -121.2891 | 0.27008 | 0.27924 | -121.3577 | -121.4905 | -0.022888 | 0.073242 | 0.027466 | 1.3321 | 0.20142 | 0.12817 | -0.21973 | -0.07782 | -0.21057 | -0.068664 | -0.009155 | -0.009155 | 0.20142 | -0.059509 | 121.6461 | 121.3989 | 86.8744 | -121.5454 | 121.55 | 121.5591 | 93.6081 | -121.8292
1896.375 | 121.7331 | -121.2708 | 0.31586 | 0.0066373 | 0.0133 | 0.074198 | 0.0070474 | 0.060011 | -0.0046184 | -0.003371 | -0.00068649 | -0.0049262 | 0.059543 | 0.065514 | -0.011976 | -0.0074511 | 0.13733 | -119.9432 | -34.6298 | -121.0648 | 0.35248 | -121.2845 | -121.2341 | -121.2616 | -27.9694 | -121.2524 | 0.23346 | 0.28381 | -121.3531 | -121.4767 | -0.013733 | 0.036621 | 0.036621 | 1.3275 | 0.20599 | 0.16937 | -0.17853 | -0.082397 | -0.20599 | -0.082398 | 0.009155 | 0.018311 | 0.22431 | -0.032044 | 121.6232 | 121.4081 | 86.6409 | -121.55 | 121.5042 | 121.5546 | 93.3014 | -121.7926
1898.0625 | 121.7148 | -121.2891 | 0.33417 | 0.0066373 | 0.0062506 | 0.070993 | 0.0046976 | 0.064924 | 0.004781 | -0.00273 | 0.0069425 | -0.00065364 | 0.062961 | 0.066796 | -0.0051397 | -0.0083057 | 0.11902 | -120.0302 | -34.8541 | -121.1243 | 0.39825 | -121.3303 | -121.2387 | -121.312 | -28.244 | -121.3943 | 0.27924 | 0.3067 | -121.3852 | -121.5363 | -0.041199 | 0.050354 | 0.064087 | 1.2588 | 0.16479 | 0.11444 | -0.21515 | -0.096131 | -0.24719 | -0.054931 | -0.022889 | -0.10529 | 0.14191 | -0.027465 | 121.6873 | 121.4081 | 86.4349 | -121.5729 | 121.5683 | 121.5958 | 93.045 | -121.8704
1899.75 | 121.6187 | -121.3486 | 0.3479 | 0.0066373 | 0.01095 | 0.073984 | 0.0061928 | 0.063215 | -0.0035504 | -0.0042254 | 0.022202 | -0.0049262 | 0.060611 | 0.0653 | -0.0074897 | -0.0065967 | 0.07782 | -120.0211 | -34.9686 | -121.1288 | 0.34332 | -121.3303 | -121.2433 | -121.3303 | -28.4821 | -121.344 | 0.25635 | 0.26093 | -121.3898 | -121.55 | 0.018311 | 0.10529 | -0.004577 | 1.3275 | 0.21973 | 0.11444 | -0.27008 | -0.041199 | -0.20142 | -0.091552 | 0.018311 | 0.004578 | 0.20599 | -0.086975 | 121.6919 | 121.4264 | 86.38 | -121.5912 | 121.6049 | 121.6095 | 92.8665 | -121.8979
1901.5 | 121.6553 | -121.3486 | 0.31128 | 0.0066373 | 0.009455 | 0.069712 | 0.0051248 | 0.06172 | 0.0032856 | -0.001662 | 0.0069425 | -0.00044004 | 0.060184 | 0.066582 | -0.0055671 | -0.0083057 | 0.041199 | -120.1355 | -35.2615 | -121.1838 | 0.36163 | -121.3486 | -121.257 | -121.3715 | -28.7292 | -121.4584 | 0.28381 | 0.29755 | -121.4172 | -121.5683 | 0 | 0.091553 | 0.050354 | 1.2131 | 0.16479 | 0.073242 | -0.27008 | -0.068664 | -0.21973 | -0.027466 | -0.022888 | -0.10986 | 0.10986 | -0.013733 | 121.7102 | 121.3898 | 86.087 | -121.5683 | 121.6324 | 121.6461 | 92.6193 | -121.8796
1903.1875 | 121.7834 | -121.3074 | 0.30212 | 0.0066373 | 0.0073188 | 0.070993 | 0.005552 | 0.066206 | 0.00050836 | 0.00026056 | 0.014572 | -0.0019354 | 0.060825 | 0.065941 | -0.0083441 | -0.0074511 | 0.027466 | -120.1035 | -35.4355 | -121.1838 | 0.35706 | -121.376 | -121.2936 | -121.3577 | -28.8483 | -121.4493 | 0.27466 | 0.29297 | -121.4172 | -121.5546 | -0.068665 | 0.013733 | 0.054932 | 1.2039 | 0.1236 | 0.10986 | -0.27466 | -0.10986 | -0.24719 | -0.027466 | -0.050354 | -0.14191 | 0.10528 | -0.009155 | 121.6644 | 121.3348 | 85.8719 | -121.5958 | 121.582 | 121.6003 | 92.4591 | -121.8567
1904.8906 | 121.637 | -121.3531 | 0.32044 | 0.0066373 | 0.0068916 | 0.070353 | 0.0014932 | 0.065138 | 0.0020038 | -0.00080744 | 0.0069425 | 0.00084176 | 0.061466 | 0.068291 | -0.0051397 | -0.0061695 | 0.022888 | -120.1447 | -35.6918 | -121.1975 | 0.35248 | -121.3943 | -121.2891 | -121.4035 | -29.2557 | -121.5134 | 0.27466 | 0.29297 | -121.4218 | -121.5775 | -0.041199 | 0.064087 | 0.032043 | 1.2085 | 0.15564 | 0.091552 | -0.29755 | -0.068665 | -0.22431 | -0.045777 | -0.050354 | -0.16022 | 0.064087 | -0.027466 | 121.7056 | 121.376 | 85.6613 | -121.6095 | 121.6278 | 121.6461 | 92.0975 | -121.8979
1906.5938 | 121.6095 | -121.3577 | 0.32959 | 0.0066373 | 0.012018 | 0.072702 | 0.0042702 | 0.06172 | -0.0063274 | -0.00273 | 0.0069425 | -0.0042852 | 0.061679 | 0.066368 | -0.0077033 | -0.0068103 | 0.082397 | -119.9707 | -35.7101 | -121.1426 | 0.31586 | -121.344 | -121.2341 | -121.3303 | -29.4342 | -121.3715 | 0.21057 | 0.25177 | -121.4035 | -121.5591 | 0.013733 | 0.1236 | -0.013733 | 1.387 | 0.21515 | 0.091553 | -0.24719 | -0.045776 | -0.20142 | -0.11902 | 0.027466 | -0.013733 | 0.18768 | -0.07782 | 121.6736 | 121.4401 | 85.6476 | -121.5637 | 121.5683 | 121.6095 | 91.9235 | -121.8887
1908.2969 | 121.7789 | -121.3577 | 0.27924 | 0.0066373 | 0.004969 | 0.073343 | 0.0081154 | 0.063856 | -0.00055964 | -0.0035846 | 0.014572 | -0.00022644 | 0.061252 | 0.064659 | -0.0081305 | -0.0074511 | 0.013733 | -120.1035 | -35.9985 | -121.1975 | 0.37994 | -121.4172 | -121.3165 | -121.4035 | -29.7684 | -121.4767 | 0.26093 | 0.27924 | -121.4676 | -121.6095 | -0.059509 | 0.041199 | 0.10071 | 1.2543 | 0.16022 | 0.11902 | -0.2655 | -0.10986 | -0.25177 | -0.018311 | -0.045776 | -0.11902 | 0.13275 | 0 | 121.7377 | 121.3715 | 85.3592 | -121.5958 | 121.6187 | 121.637 | 91.5894 | -121.8887
1909.9844 | 121.637 | -121.4035 | 0.3067 | -0.0086212 | 0.006037 | 0.070353 | 0.0034158 | 0.06407 | 0.00414 | -0.001021 | 0.0069425 | -0.00044004 | 0.061039 | 0.066796 | -0.0053533 | -0.0074511 | -0.018311 | -120.1675 | -36.1862 | -121.225 | 0.33875 | -121.4218 | -121.3165 | -121.4218 | -30.162 | -121.5363 | 0.23346 | 0.25635 | -121.4767 | -121.6049 | -0.018311 | 0.086975 | 0.032043 | 1.236 | 0.17853 | 0.091552 | -0.32501 | -0.073243 | -0.20142 | -0.073243 | -0.018311 | -0.13275 | 0.068664 | -0.050354 | 121.7422 | 121.3852 | 85.2173 | -121.6232 | 121.637 | 121.6599 | 91.2415 | -121.9116
1911.6719 | 121.6599 | -121.4035 | 0.27466 | -0.00099167 | 0.013941 | 0.075266 | 0.0061928 | 0.063002 | -0.0052594 | -0.0025164 | 0.0069425 | -0.0044988 | 0.061466 | 0.063805 | -0.0091985 | -0.0070239 | 0.004578 | -120.0531 | -36.2045 | -121.2021 | 0.28839 | -121.376 | -121.2982 | -121.3806 | -30.1392 | -121.4081 | 0.17853 | 0.21515 | -121.4493 | -121.6461 | 0.027465 | 0.10528 | 0.013733 | 1.3504 | 0.20142 | 0.096131 | -0.27008 | -0.045777 | -0.24262 | -0.09613 | 0.022888 | -0.004578 | 0.23804 | -0.059509 | 121.6919 | 121.4081 | 85.199 | -121.5729 | 121.582 | 121.6187 | 91.2643 | -121.9208
1913.4062 | 121.7331 | -121.3715 | 0.27466 | 0.0066373 | 0.0092414 | 0.072916 | 0.0091836 | 0.063429 | -0.0014142 | -0.003371 | 0.0069425 | -0.0032172 | 0.06232 | 0.0653 | -0.010908 | -0.0085193 | 0.036621 | -120.0439 | -36.4426 | -121.1929 | 0.31586 | -121.4401 | -121.3165 | -121.4264 | -30.2902 | -121.5042 | 0.23346 | 0.24719 | -121.4996 | -121.6187 | -0.068665 | 0.054932 | 0.041199 | 1.3275 | 0.17853 | 0.1236 | -0.23804 | -0.12817 | -0.24719 | -0.041199 | -0.054932 | -0.13275 | 0.11444 | -0.027466 | 121.6873 | 121.4081 | 84.9289 | -121.5912 | 121.6049 | 121.6187 | 91.0812 | -121.8933
1915.1406 | 121.7468 | -121.3806 | 0.26093 | -0.0086212 | 0.013514 | 0.075052 | 0.0074746 | 0.063429 | -0.0052594 | -0.00273 | -0.00068649 | -0.0042852 | 0.062748 | 0.0653 | -0.0089849 | -0.0059557 | 0.009155 | -120.0531 | -36.6806 | -121.1975 | 0.29755 | -121.4035 | -121.3303 | -121.3715 | -30.5695 | -121.4035 | 0.18768 | 0.21515 | -121.463 | -121.6278 | -0.022888 | 0.050354 | 0.036621 | 1.3275 | 0.18311 | 0.13275 | -0.25177 | -0.082398 | -0.24719 | -0.073242 | 0.009155 | -0.022888 | 0.22431 | -0.045776 | 121.6782 | 121.3898 | 84.7 | -121.5912 | 121.5683 | 121.5958 | 90.8112 | -121.8887
1916.8281 | 121.5958 | -121.138 | 0.27008 | -0.0086212 | 0.0051826 | 0.071421 | 0.0064066 | 0.063643 | 0.00414 | -0.0029436 | 0.0069425 | 0.00041436 | 0.060825 | 0.0653 | -0.0047125 | -0.0074511 | 0.050354 | -119.8837 | -36.9415 | -121.0052 | 0.31128 | -121.2067 | -121.1334 | -121.1838 | -30.9952 | -121.2982 | 0.21515 | 0.21515 | -121.2662 | -121.4355 | -0.068665 | 0.004577 | 0.041198 | 1.2543 | 0.13275 | 0.12817 | -0.21973 | -0.12817 | -0.29755 | -0.054932 | -0.045777 | -0.16022 | 0.13733 | -0.054932 | 121.4493 | 121.1884 | 84.1965 | -121.4035 | 121.3531 | 121.3531 | 90.1428 | -121.7056
1918.5469 | 121.6049 | -121.257 | 0.29755 | -0.00099167 | 0.011591 | 0.070139 | 0.0061928 | 0.064711 | 0.00050836 | -0.0031574 | 0.0069425 | -0.00065364 | 0.061893 | 0.066796 | -0.0053533 | -0.0061695 | 0.004578 | -120.0119 | -37.1338 | -121.1197 | 0.32959 | -121.312 | -121.2158 | -121.2662 | -31.2607 | -121.3943 | 0.22888 | 0.2655 | -121.3531 | -121.5088 | -0.054932 | 0.041199 | 0.032044 | 1.2451 | 0.13733 | 0.09613 | -0.29297 | -0.09613 | -0.25177 | -0.068664 | -0.009155 | -0.13733 | 0.11444 | -0.032043 | 121.5866 | 121.2616 | 84.1232 | -121.5134 | 121.4859 | 121.5225 | 89.9963 | -121.8063
1920.2344 | 121.6507 | -121.2341 | 0.25177 | -0.00099167 | 0.0090278 | 0.073771 | 0.012174 | 0.064924 | -0.0039776 | -0.0046526 | -0.00068649 | -0.0059942 | 0.062534 | 0.062737 | -0.011762 | -0.0076647 | 0.068665 | -119.8425 | -37.1841 | -121.0556 | 0.28839 | -121.2753 | -121.2112 | -121.2204 | -31.2561 | -121.2891 | 0.19684 | 0.23804 | -121.3577 | -121.4859 | -0.041199 | 0.022888 | 0.036621 | 1.3916 | 0.17853 | 0.15564 | -0.1831 | -0.1236 | -0.25177 | -0.054932 | 0.013733 | -0.054931 | 0.19684 | -0.013733 | 121.5225 | 121.3028 | 84.05 | -121.463 | 121.431 | 121.4722 | 89.978 | -121.7377
1921.9219 | 121.5683 | -121.3257 | 0.31128 | 0.014267 | 0.013087 | 0.07078 | 0.0079018 | 0.062574 | -0.002055 | -0.006148 | -0.00068649 | -0.0042852 | 0.060825 | 0.064659 | -0.0072759 | -0.0065967 | 0.064087 | -119.8975 | -37.5137 | -121.1151 | 0.28381 | -121.3028 | -121.2387 | -121.257 | -31.8192 | -121.3486 | 0.21973 | 0.23346 | -121.3669 | -121.5317 | 0.022889 | 0.086976 | -0.027466 | 1.4282 | 0.21057 | 0.1236 | -0.24719 | -0.041198 | -0.20599 | -0.091552 | 0.068665 | -0.022888 | 0.1831 | -0.07782 | 121.6095 | 121.3898 | 83.812 | -121.55 | 121.5454 | 121.5591 | 89.5065 | -121.843
1923.6094 | 121.5958 | -121.3394 | 0.29297 | -0.00099167 | 0.0083868 | 0.068216 | 0.0044838 | 0.061934 | 0.0049946 | -0.00273 | 0.0069425 | 0.0010554 | 0.061466 | 0.065087 | -0.0085577 | -0.0089465 | 0 | -120.0531 | -37.8479 | -121.1746 | 0.34332 | -121.3623 | -121.2753 | -121.3165 | -32.2037 | -121.4905 | 0.24261 | 0.27924 | -121.3852 | -121.5591 | -0.022888 | 0.064087 | 0.050354 | 1.2863 | 0.16479 | 0.10071 | -0.29297 | -0.045776 | -0.21973 | -0.050354 | 0.022889 | -0.15106 | 0.068664 | -0.013733 | 121.6827 | 121.3394 | 83.4915 | -121.5683 | 121.582 | 121.6187 | 89.1357 | -121.8521
1925.2812 | 121.7102 | -121.2982 | 0.27466 | 0.0066373 | 0.011805 | 0.075479 | 0.0074746 | 0.060652 | -0.0041912 | -0.0035846 | -0.00068649 | -0.0057806 | 0.061679 | 0.063591 | -0.010267 | -0.0061695 | 0.027466 | -119.9295 | -38.0081 | -121.1014 | 0.3067 | -121.3211 | -121.2387 | -121.2433 | -32.1671 | -121.3165 | 0.20599 | 0.23804 | -121.3989 | -121.5546 | -0.022888 | 0.05951 | 0.032044 | 1.3687 | 0.19684 | 0.13733 | -0.24719 | -0.10071 | -0.25635 | -0.068664 | 0.054932 | -0.01831 | 0.23804 | -0.036621 | 121.6049 | 121.3257 | 83.2901 | -121.5134 | 121.5042 | 121.5363 | 89.1312 | -121.8292
1926.9688 | 121.6599 | -121.3257 | 0.29297 | -0.0086212 | 0.012232 | 0.072489 | 0.0040566 | 0.064497 | 0.0028584 | -0.00273 | 0.0069425 | -0.0017218 | 0.061466 | 0.065514 | -0.0059943 | -0.0083057 | 0.09613 | -119.8975 | -38.0676 | -121.0876 | 0.3067 | -121.3348 | -121.2341 | -121.2112 | -32.5241 | -121.3486 | 0.20142 | 0.22888 | -121.376 | -121.5271 | -0.009155 | 0.091553 | 0.013733 | 1.4282 | 0.23804 | 0.14648 | -0.19684 | -0.050354 | -0.20142 | -0.091553 | 0.11444 | -0.022888 | 0.17853 | -0.064087 | 121.6324 | 121.4218 | 83.2581 | -121.5271 | 121.5271 | 121.5546 | 88.8016 | -121.8201
1928.6562 | 121.7331 | -121.312 | 0.26093 | 0.014267 | 0.0058234 | 0.069071 | 0.0059792 | 0.06407 | 0.0062762 | -0.001662 | 0.014572 | 0.00084176 | 0.060184 | 0.065087 | -0.0070623 | -0.0085193 | 0.050354 | -119.957 | -38.4155 | -121.1334 | 0.33417 | -121.3669 | -121.2982 | -121.2616 | -32.7896 | -121.431 | 0.23804 | 0.2655 | -121.3943 | -121.5591 | -0.054931 | 0.013733 | 0.073242 | 1.355 | 0.17853 | 0.1648 | -0.21057 | -0.082397 | -0.24719 | -0.022888 | 0.050354 | -0.11902 | 0.12817 | 0.004578 | 121.6461 | 121.3623 | 82.8964 | -121.5591 | 121.55 | 121.5775 | 88.5223 | -121.8201
1930.375 | 121.6232 | -121.344 | 0.32044 | 0.014267 | 0.0036872 | 0.070139 | 0.0044838 | 0.061506 | 0.003072 | -0.00080744 | 0.0069425 | -0.0017218 | 0.063175 | 0.065941 | -0.0055671 | -0.0070239 | 0.022888 | -120.0119 | -38.736 | -121.1884 | 0.33417 | -121.3989 | -121.2891 | -121.3028 | -33.11 | -121.4951 | 0.25177 | 0.2655 | -121.4218 | -121.6003 | -0.054932 | 0.054932 | 0.013732 | 1.3321 | 0.15564 | 0.10071 | -0.29755 | -0.07782 | -0.25635 | -0.068665 | 0.041199 | -0.15106 | 0.10529 | -0.054932 | 121.6782 | 121.3669 | 82.608 | -121.6095 | 121.5958 | 121.6095 | 88.2339 | -121.9208
1932.0469 | 121.7056 | -121.3348 | 0.28839 | 0.0066373 | 0.013727 | 0.07313 | 0.0057656 | 0.065138 | -0.0056866 | -0.0035846 | -0.008316 | -0.0040716 | 0.061252 | 0.06295 | -0.0085577 | -0.0053149 | -0.009155 | -119.9478 | -38.9191 | -121.1655 | 0.30212 | -121.3623 | -121.2616 | -121.2616 | -33.5999 | -121.3577 | 0.2243 | 0.25177 | -121.4172 | -121.5591 | -0.027466 | 0.073242 | 0.013733 | 1.387 | 0.16937 | 0.096131 | -0.29755 | -0.082397 | -0.2243 | -0.064087 | 0.073242 | -0.022888 | 0.20142 | -0.036621 | 121.637 | 121.3257 | 82.4158 | -121.55 | 121.5591 | 121.5866 | 87.735 | -121.8475
1933.7188 | 121.7468 | -121.3394 | 0.29297 | 0.0066373 | 0.0068916 | 0.06843 | 0.0046976 | 0.065565 | 0.0032856 | -0.0029436 | -0.00068649 | 0.00062796 | 0.061039 | 0.066155 | -0.0072759 | -0.0083057 | 0.041199 | -119.9615 | -39.2807 | -121.1746 | 0.35248 | -121.3898 | -121.2799 | -121.2616 | -34.5016 | -121.4355 | 0.23346 | 0.27008 | -121.4127 | -121.6003 | -0.050354 | 0.05951 | 0.059509 | 1.3779 | 0.16479 | 0.10528 | -0.25177 | -0.073242 | -0.26093 | -0.05951 | 0.07782 | -0.09613 | 0.16479 | -0.022888 | 121.6919 | 121.3806 | 82.0587 | -121.5729 | 121.5729 | 121.6095 | 86.8378 | -121.8933
1935.4062 | 121.6232 | -121.3806 | 0.31586 | 0.014267 | 0.009455 | 0.070353 | 0.0049112 | 0.061506 | 0.0039264 | -0.0020892 | 0.0069425 | -0.0015082 | 0.061039 | 0.067223 | -0.0068487 | -0.0080921 | -0.013733 | -120.0623 | -39.5966 | -121.2067 | 0.35706 | -121.4127 | -121.312 | -121.3211 | -34.8679 | -121.5134 | 0.25635 | 0.27008 | -121.431 | -121.5729 | -0.032044 | 0.068664 | 0.041199 | 1.3184 | 0.17395 | 0.10529 | -0.32959 | -0.050354 | -0.19226 | -0.059509 | 0.059509 | -0.13275 | 0.059509 | -0.045776 | 121.7377 | 121.3669 | 81.7841 | -121.6278 | 121.637 | 121.6507 | 86.5128 | -121.8887
1937.0938 | 121.7102 | -121.3669 | 0.29755 | 0.0066373 | 0.009455 | 0.072702 | 0.00897 | 0.065138 | -0.0018414 | -0.0018756 | 0.0069425 | -0.0032172 | 0.060825 | 0.063805 | -0.010694 | -0.0074511 | 0.036621 | -119.9295 | -39.7339 | -121.1472 | 0.32501 | -121.3898 | -121.2936 | -121.2982 | -34.964 | -121.431 | 0.24719 | 0.27008 | -121.4447 | -121.5683 | -0.022889 | 0.073242 | 0.027466 | 1.4374 | 0.21973 | 0.14648 | -0.26092 | -0.07782 | -0.20142 | -0.050354 | 0.068664 | -0.064087 | 0.13733 | -0.027465 | 121.6919 | 121.4035 | 81.633 | -121.5912 | 121.6141 | 121.637 | 86.4029 | -121.8658
1938.7812 | 121.7606 | -121.2982 | 0.28381 | -0.0086212 | 0.010737 | 0.073343 | 0.0066202 | 0.060865 | -0.003764 | -0.00273 | -0.00068649 | -0.0053534 | 0.060611 | 0.063378 | -0.0096259 | -0.0074511 | 0.027466 | -119.9203 | -39.7842 | -121.1563 | 0.32501 | -121.376 | -121.2524 | -121.2479 | -35.0372 | -121.3531 | 0.21515 | 0.25177 | -121.4127 | -121.6003 | -0.07782 | 0.045777 | 0.041199 | 1.3779 | 0.14191 | 0.09613 | -0.25635 | -0.11444 | -0.30212 | -0.068664 | 0.050354 | -0.054931 | 0.24719 | -0.032043 | 121.6232 | 121.3257 | 81.514 | -121.5363 | 121.5134 | 121.55 | 86.261 | -121.8842
1940.5156 | 121.788 | -121.3486 | 0.27466 | -0.0086212 | 0.0051826 | 0.069925 | 0.010038 | 0.064283 | 0.0032856 | -0.003371 | -0.00068649 | -0.00065364 | 0.06467 | 0.066796 | -0.0059943 | -0.0085193 | -0.009155 | -120.0119 | -40.0955 | -121.2067 | 0.33417 | -121.431 | -121.3348 | -121.2753 | -35.0876 | -121.463 | 0.25177 | 0.28839 | -121.4584 | -121.5866 | -0.082397 | 0.013733 | 0.059509 | 1.3367 | 0.14191 | 0.12817 | -0.28381 | -0.10986 | -0.23804 | -0.022888 | 0.073242 | -0.11444 | 0.1236 | 0.013733 | 121.6827 | 121.3394 | 81.2531 | -121.6095 | 121.6003 | 121.637 | 86.261 | -121.8613
1942.2031 | 121.7285 | -121.2845 | 0.25635 | 0.0066373 | 0.011805 | 0.072702 | 0.007261 | 0.062361 | -0.005473 | -0.0063616 | 0.0069425 | -0.0040716 | 0.062748 | 0.064232 | -0.0094123 | -0.0055285 | 0.032043 | -119.8196 | -40.1138 | -121.0739 | 0.29297 | -121.3303 | -121.2387 | -121.1472 | -34.964 | -121.2753 | 0.20599 | 0.21515 | -121.3943 | -121.5271 | -0.045776 | 0.045777 | 0.036621 | 1.4648 | 0.21057 | 0.16479 | -0.22431 | -0.10986 | -0.24262 | -0.050354 | 0.13733 | 0.009155 | 0.25177 | -0.041199 | 121.5775 | 121.3165 | 81.1707 | -121.4951 | 121.4905 | 121.4996 | 86.3205 | -121.7834
1943.9062 | 121.6599 | -121.3211 | 0.28381 | -0.00099167 | 0.010737 | 0.070566 | 0.0036294 | 0.063215 | 0.0028584 | -0.0025164 | -0.00068649 | -0.002149 | 0.060825 | 0.065087 | -0.0057807 | -0.0048877 | -0.013733 | -119.9707 | -40.4709 | -121.1884 | 0.33417 | -121.3943 | -121.2891 | -121.2204 | -35.4172 | -121.4584 | 0.21515 | 0.24719 | -121.431 | -121.5866 | -0.073242 | 0.032044 | 0.050354 | 1.3504 | 0.13275 | 0.10071 | -0.29755 | -0.10986 | -0.2655 | -0.068664 | 0.10071 | -0.13733 | 0.12817 | -0.036621 | 121.6553 | 121.3074 | 80.8502 | -121.5729 | 121.5363 | 121.5683 | 85.9039 | -121.8704
1945.6094 | 121.637 | -121.3486 | 0.28381 | 0.0066373 | 0.014368 | 0.07078 | 0.0025612 | 0.063429 | 8.1158e-05 | -0.0042254 | 0.0069425 | -0.0034308 | 0.05933 | 0.0653 | -0.0068487 | -0.0072375 | 0.064087 | -119.8471 | -40.4755 | -121.1243 | 0.28381 | -121.3623 | -121.2341 | -121.1563 | -35.6369 | -121.344 | 0.19226 | 0.2243 | -121.4035 | -121.5683 | -0.013733 | 0.11444 | 0 | 1.5015 | 0.2243 | 0.10986 | -0.21973 | -0.054931 | -0.21973 | -0.091552 | 0.19226 | 0.004578 | 0.2243 | -0.059509 | 121.6324 | 121.4127 | 80.8731 | -121.5179 | 121.5408 | 121.5729 | 85.7117 | -121.8521
1947.2812 | 121.7606 | -121.3211 | 0.2655 | 0.0066373 | 0.0062506 | 0.070139 | 0.0070474 | 0.061934 | 0.00093576 | -0.00038024 | 0.0069425 | -0.00086724 | 0.063388 | 0.066582 | -0.0066351 | -0.0076647 | 0.022888 | -119.9295 | -40.7913 | -121.1746 | 0.33875 | -121.4035 | -121.3211 | -121.2296 | -36.026 | -121.4447 | 0.22888 | 0.24261 | -121.4493 | -121.5866 | -0.082397 | 0 | 0.073242 | 1.3916 | 0.14648 | 0.14648 | -0.24261 | -0.12817 | -0.2655 | -0.036621 | 0.091553 | -0.1236 | 0.14191 | -0.022888 | 121.6599 | 121.344 | 80.5298 | -121.5866 | 121.55 | 121.5637 | 85.2951 | -121.8521
1948.9688 | 121.6461 | -121.3943 | 0.29297 | 0.014267 | 0.007746 | 0.066935 | 0.0046976 | 0.063429 | 0.002431 | -0.0025164 | 0.0069425 | -0.0010808 | 0.063388 | 0.067437 | -0.0081305 | -0.0080921 | -0.036621 | -119.9936 | -40.9744 | -121.2067 | 0.32959 | -121.4035 | -121.3074 | -121.2616 | -36.0992 | -121.5134 | 0.22888 | 0.25635 | -121.431 | -121.6141 | -0.009155 | 0.086975 | 0.036621 | 1.4008 | 0.18768 | 0.10071 | -0.32959 | -0.036621 | -0.21973 | -0.064087 | 0.13275 | -0.11902 | 0.10071 | -0.036621 | 121.7239 | 121.3577 | 80.4199 | -121.6003 | 121.6232 | 121.6507 | 85.2951 | -121.907
1950.6562 | 121.582 | -121.2479 | 0.21515 | 0.014267 | 0.012018 | 0.072275 | 0.0023476 | 0.062147 | 0.00072196 | -0.0012346 | 0.0069425 | -0.002149 | 0.059543 | 0.06765 | -0.0053533 | -0.0057421 | -0.09613 | -119.8746 | -40.9332 | -121.138 | 0.2655 | -121.3257 | -121.2296 | -121.138 | -36.3373 | -121.376 | 0.14191 | 0.1831 | -121.3669 | -121.5134 | -0.07782 | 0.018311 | 0.050354 | 1.3733 | 0.10986 | 0.091553 | -0.31128 | -0.11902 | -0.2655 | -0.073242 | 0.10986 | -0.12817 | 0.13733 | -0.032044 | 121.5134 | 121.1517 | 80.3146 | -121.4447 | 121.3898 | 121.431 | 84.9106 | -121.7285
1952.3281 | 121.7194 | -121.3028 | 0.21515 | 0.0066373 | 0.0056098 | 0.074411 | 0.010038 | 0.064283 | -0.0014142 | -0.0025164 | 0.0069425 | -0.0017218 | 0.065311 | 0.064446 | -0.0094123 | -0.0065967 | -0.11444 | -119.9341 | -41.2033 | -121.1792 | 0.29755 | -121.3943 | -121.3074 | -121.2387 | -36.6074 | -121.463 | 0.19684 | 0.2243 | -121.4355 | -121.5408 | -0.091553 | -0.004578 | 0.082397 | 1.3687 | 0.1236 | 0.12817 | -0.32959 | -0.13275 | -0.23804 | -0.018311 | 0.064087 | -0.16022 | 0.07782 | 0.009155 | 121.6003 | 121.1884 | 80.0995 | -121.5225 | 121.4996 | 121.5271 | 84.6954 | -121.756
1954.0156 | 121.6507 | -121.3486 | 0.23346 | 0.0066373 | 0.013514 | 0.072916 | 0.002775 | 0.062574 | -0.0022686 | -0.0029436 | -0.00068649 | -0.0027898 | 0.061466 | 0.065728 | -0.0057807 | -0.0070239 | -0.018311 | -119.8471 | -41.4642 | -121.1334 | 0.25177 | -121.3394 | -121.2753 | -121.1426 | -36.7401 | -121.3852 | 0.15106 | 0.17395 | -121.4401 | -121.5729 | 0.009155 | 0.073242 | 0.018311 | 1.5015 | 0.21515 | 0.14191 | -0.25177 | -0.091553 | -0.2243 | -0.082397 | 0.20599 | -0.036621 | 0.18768 | -0.059509 | 121.6003 | 121.3303 | 79.8843 | -121.5088 | 121.4996 | 121.5225 | 84.6085 | -121.8063
1955.7031 | 121.7194 | -121.3531 | 0.20142 | -0.00099167 | 0.012873 | 0.075907 | 0.0059792 | 0.064283 | -0.0052594 | -0.003371 | 0.0069425 | -0.0053534 | 0.063175 | 0.064659 | -0.01048 | -0.0044605 | -0.059509 | -119.8837 | -41.597 | -121.17 | 0.26093 | -121.4081 | -121.3074 | -121.2021 | -36.937 | -121.3669 | 0.15564 | 0.1831 | -121.4218 | -121.6049 | -0.054932 | 0.045776 | 0.059509 | 1.4694 | 0.1831 | 0.13733 | -0.26093 | -0.068665 | -0.25177 | -0.045776 | 0.15106 | -0.013733 | 0.23804 | -0.018311 | 121.6141 | 121.2936 | 79.7562 | -121.5088 | 121.5088 | 121.5363 | 84.4162 | -121.8063
1957.3906 | 121.7468 | -121.3486 | 0.19684 | -0.00099167 | 0.011378 | 0.072062 | 0.0079018 | 0.064924 | -0.0050458 | -0.003371 | 0.014572 | -0.0034308 | 0.060825 | 0.065941 | -0.010908 | -0.0063831 | 0.027466 | -119.8059 | -41.684 | -121.1334 | 0.22888 | -121.3852 | -121.2799 | -121.1426 | -37.0056 | -121.3348 | 0.15106 | 0.1831 | -121.4355 | -121.582 | -0.036621 | 0.068665 | 0.032044 | 1.5427 | 0.21515 | 0.14648 | -0.16937 | -0.086975 | -0.23346 | -0.045776 | 0.20599 | 0.013733 | 0.24719 | -0.013733 | 121.5775 | 121.376 | 79.6646 | -121.4767 | 121.4996 | 121.5317 | 84.343 | -121.7789
1959.0781 | 121.6187 | -121.4081 | 0.29297 | -0.0086212 | 0.0039008 | 0.071207 | 0.0036294 | 0.063643 | 0.0060626 | -0.003371 | -0.00068649 | -0.00065364 | 0.061252 | 0.066155 | -0.0036443 | -0.0085193 | 0.1236 | -119.902 | -42.3248 | -121.1838 | 0.32959 | -121.3715 | -121.3074 | -121.2433 | -37.3672 | -121.5179 | 0.20599 | 0.22888 | -121.4813 | -121.6324 | 0.036621 | 0.10071 | 0.036621 | 1.506 | 0.2243 | 0.1236 | -0.16937 | -0.073242 | -0.2243 | -0.086975 | 0.16479 | -0.10986 | 0.11444 | -0.064087 | 121.7377 | 121.5317 | 79.0833 | -121.6003 | 121.6141 | 121.637 | 84.0408 | -121.9254
1960.7656 | 121.7468 | -121.3531 | 0.23804 | 0.0066373 | 0.0092414 | 0.072489 | 0.0064066 | 0.064711 | -0.0044048 | -0.0042254 | -0.00068649 | -0.0051398 | 0.062107 | 0.064019 | -0.011762 | -0.0059557 | 0.041199 | -119.7418 | -42.5674 | -121.0876 | 0.27924 | -121.3806 | -121.2616 | -121.1151 | -37.3169 | -121.3348 | 0.1831 | 0.24261 | -121.4172 | -121.5546 | -0.027466 | 0.091552 | 0.041199 | 1.6113 | 0.2655 | 0.17395 | -0.19684 | -0.064087 | -0.20142 | -0.054932 | 0.23804 | 0.01831 | 0.21973 | 0.004578 | 121.6324 | 121.3943 | 78.7857 | -121.4996 | 121.5363 | 121.5958 | 84.0363 | -121.7926
1962.5 | 121.7056 | -121.3943 | 0.23346 | -0.00099167 | 0.0088142 | 0.072702 | 0.007261 | 0.063429 | -0.0014142 | -0.0025164 | 0.0069425 | -0.0032172 | 0.062961 | 0.066368 | -0.010053 | -0.0085193 | 0.013733 | -119.8334 | -42.8192 | -121.1746 | 0.28381 | -121.3989 | -121.312 | -121.1884 | -37.6465 | -121.4401 | 0.17853 | 0.20599 | -121.4584 | -121.6095 | -0.004578 | 0.082397 | 0.050354 | 1.561 | 0.21973 | 0.13733 | -0.21973 | -0.064087 | -0.21515 | -0.054931 | 0.20599 | -0.045777 | 0.16937 | -0.027465 | 121.6782 | 121.4081 | 78.5751 | -121.5454 | 121.5729 | 121.6003 | 83.7479 | -121.843
1964.1719 | 121.6782 | -121.4218 | 0.23804 | -0.0086212 | 0.011805 | 0.070139 | 0.0044838 | 0.065138 | 0.002431 | -0.0023028 | -0.00068649 | -0.00044004 | 0.061679 | 0.067223 | -0.0072759 | -0.0070239 | -0.073242 | -119.9707 | -43.1213 | -121.2799 | 0.30212 | -121.4401 | -121.3898 | -121.225 | -37.9532 | -121.5317 | 0.20599 | 0.20142 | -121.5088 | -121.6507 | -0.018311 | 0.032043 | 0.064087 | 1.4511 | 0.14191 | 0.10986 | -0.31128 | -0.086975 | -0.22888 | -0.032043 | 0.19684 | -0.10986 | 0.11902 | -0.036621 | 121.7239 | 121.3486 | 78.3005 | -121.6278 | 121.6278 | 121.6232 | 83.4686 | -121.8887
1965.8594 | 121.7743 | -121.3806 | 0.2243 | 0.0066373 | 0.010309 | 0.072702 | 0.0091836 | 0.063215 | -0.0048322 | -0.0014484 | 0.0069425 | -0.0042852 | 0.062534 | 0.064019 | -0.010267 | -0.0091601 | 0.013733 | -119.783 | -43.3136 | -121.1746 | 0.25177 | -121.4355 | -121.3394 | -121.1197 | -37.9211 | -121.3806 | 0.15564 | 0.19226 | -121.4584 | -121.637 | -0.054932 | 0.041198 | 0.027466 | 1.5976 | 0.20599 | 0.16479 | -0.21057 | -0.07782 | -0.25635 | -0.068664 | 0.26093 | 0 | 0.25635 | -0.032043 | 121.6324 | 121.3943 | 78.067 | -121.5637 | 121.5363 | 121.5729 | 83.4595 | -121.8613
1967.5781 | 121.7194 | -121.431 | 0.2243 | 0.0066373 | 0.009455 | 0.072062 | 0.0098244 | 0.066206 | -0.0018414 | -0.0040118 | 0.014572 | -0.0010808 | 0.061679 | 0.0653 | -0.0081305 | -0.0083057 | -0.032043 | -119.8471 | -43.1534 | -121.2112 | 0.27008 | -121.463 | -121.344 | -121.1792 | -38.205 | -121.4996 | 0.17395 | 0.17853 | -121.5134 | -121.6461 | -0.032044 | 0.086975 | 0.045777 | 1.5839 | 0.21973 | 0.13275 | -0.25635 | -0.082398 | -0.21515 | -0.050354 | 0.25177 | -0.068665 | 0.14648 | -0.045776 | 121.7011 | 121.3989 | 78.2776 | -121.5683 | 121.6049 | 121.6095 | 83.226 | -121.8704
1969.2656 | 121.701 | -121.4264 | 0.2655 | 0.0066373 | 0.011164 | 0.070566 | 0.0051248 | 0.063643 | 0.0043536 | -0.0020892 | -0.00068649 | -0.0030034 | 0.061252 | 0.066796 | -0.0047125 | -0.0063831 | -0.07782 | -119.9432 | -43.2632 | -121.2524 | 0.30212 | -121.4539 | -121.3806 | -121.2204 | -38.4567 | -121.5546 | 0.20599 | 0.21057 | -121.5088 | -121.6599 | -0.027465 | 0.045777 | 0.036621 | 1.4832 | 0.17395 | 0.12817 | -0.34332 | -0.082397 | -0.23346 | -0.059509 | 0.20599 | -0.12817 | 0.10529 | -0.054932 | 121.7285 | 121.3486 | 78.1631 | -121.6461 | 121.6324 | 121.637 | 82.9697 | -121.9254
1970.9531 | 121.6553 | -121.3806 | 0.31586 | -0.0086212 | 0.013514 | 0.073343 | 0.0068338 | 0.062574 | -0.0016278 | -0.0040118 | 0.022202 | -0.0032172 | 0.061679 | 0.065514 | -0.010267 | -0.0061695 | 0.036621 | -119.783 | -43.2678 | -121.1563 | 0.36621 | -121.344 | -121.257 | -121.138 | -38.6215 | -121.4127 | 0.25177 | 0.25177 | -121.4355 | -121.5958 | 0.036621 | 0.1236 | 0.050354 | 1.5976 | 0.2243 | 0.10071 | -0.27924 | -0.054932 | -0.21515 | -0.064087 | 0.24262 | -0.032044 | 0.1831 | -0.064087 | 121.7468 | 121.4172 | 78.1128 | -121.5729 | 121.6324 | 121.6324 | 82.7591 | -121.9116
1972.6562 | 121.7606 | -121.3943 | 0.23346 | 0.014267 | 0.0058234 | 0.06843 | 0.0079018 | 0.067274 | 0.0039264 | -0.0029436 | -0.00068649 | -1.2844e-05 | 0.063602 | 0.0653 | -0.0049261 | -0.0072375 | 0.009155 | -119.8517 | -43.6111 | -121.1884 | 0.31128 | -121.4493 | -121.3257 | -121.1472 | -38.649 | -121.5179 | 0.21057 | 0.2243 | -121.5042 | -121.6599 | -0.054932 | 0.068664 | 0.07782 | 1.5427 | 0.20599 | 0.13733 | -0.2243 | -0.10986 | -0.2655 | -0.022888 | 0.24719 | -0.1236 | 0.14191 | -0.009155 | 121.7056 | 121.4035 | 77.7832 | -121.5591 | 121.6049 | 121.6187 | 82.7454 | -121.8933
1974.3281 | 121.7834 | -121.3348 | 0.27008 | -0.00099167 | 0.014796 | 0.073557 | 0.010465 | 0.062788 | -0.0050458 | -0.00273 | -0.00068649 | -0.0032172 | 0.060825 | 0.064873 | -0.01048 | -0.0065967 | 0.045776 | -119.751 | -43.7714 | -121.1334 | 0.29755 | -121.4401 | -121.312 | -121.0281 | -38.6398 | -121.3394 | 0.21057 | 0.21973 | -121.4401 | -121.6049 | -0.10529 | 0.022888 | 0.027465 | 1.5839 | 0.20142 | 0.17853 | -0.22431 | -0.10529 | -0.27008 | -0.05951 | 0.3067 | -0.004578 | 0.2655 | -0.050354 | 121.6324 | 121.3806 | 77.5635 | -121.582 | 121.5454 | 121.5546 | 82.695 | -121.875
1976.0156 | 120.9778 | -119.1422 | 1.7212 | 0.0066373 | 0.0066778 | 0.069498 | 0.003843 | 0.063429 | 0.0056354 | -0.0025164 | -0.00068649 | 0.00020076 | 0.061252 | 0.064446 | -0.0049261 | -0.0091601 | 1.6571 | -117.4667 | -42.897 | -118.7439 | 1.9455 | -119.0231 | -118.9636 | -118.8446 | -38.031 | -119.1193 | 1.7715 | 1.7899 | -119.1193 | -119.2886 | 0.11902 | 0.17853 | 0.2243 | 1.6754 | 0.39825 | 0.21973 | -0.064087 | 0.022888 | -0.14648 | 0.050354 | 0.29755 | 0.022888 | 0.16937 | 0.068665 | 121.0876 | 120.7993 | 76.2451 | -120.6848 | 120.9137 | 120.932 | 81.1111 | -121.0098
1977.7031 | 121.344 | -120.3415 | 0.97504 | -0.0086212 | 0.012659 | 0.072275 | 0.0057656 | 0.064711 | -0.0048322 | -0.0023028 | 0.0069425 | -0.0059942 | 0.061252 | 0.063805 | -0.0087713 | -0.0068103 | 0.60883 | -118.8309 | -43.7439 | -120.2362 | 0.89264 | -120.4651 | -120.3369 | -120.1172 | -38.649 | -120.4285 | 0.83771 | 0.85602 | -120.4697 | -120.607 | -0.1236 | 0.004578 | -0.082398 | 1.5106 | 0.10529 | 0.10071 | -0.36621 | -0.12817 | -0.2655 | -0.13733 | 0.22431 | -0.086975 | 0.17853 | -0.11902 | 121.2341 | 120.9503 | 76.5976 | -121.312 | 121.1792 | 121.1975 | 81.6925 | -121.582
1979.4062 | 121.4493 | -120.6848 | 0.71411 | 0.021896 | 0.0079596 | 0.07078 | 0.0061928 | 0.062788 | 0.0045674 | -0.0029436 | -0.00068649 | -1.2844e-05 | 0.06232 | 0.064659 | -0.0036443 | -0.0093737 | 0.48523 | -119.0781 | -43.9407 | -120.4651 | 0.74616 | -120.6894 | -120.6162 | -120.3598 | -38.9969 | -120.7809 | 0.6546 | 0.67749 | -120.7535 | -120.9045 | -0.004578 | 0.068664 | 0.032044 | 1.6068 | 0.21973 | 0.15106 | -0.22888 | -0.068665 | -0.21973 | -0.059509 | 0.32501 | -0.096131 | 0.1236 | -0.036621 | 121.431 | 121.17 | 76.7441 | -121.3303 | 121.3394 | 121.3623 | 81.6879 | -121.6187
1981.1094 | 121.3989 | -120.5933 | 0.87433 | -0.00099167 | 0.014582 | 0.074411 | 0.005552 | 0.062788 | -0.0022686 | -0.0031574 | 0.0069425 | -0.0042852 | 0.061252 | 0.063591 | -0.0081305 | -0.0029651 | 0.59967 | -118.9178 | -44.1101 | -120.3506 | 0.8606 | -120.5658 | -120.4468 | -120.2728 | -39.0381 | -120.5704 | 0.79651 | 0.82398 | -120.6528 | -120.7901 | 0.027466 | 0.14648 | -0.013733 | 1.6754 | 0.24262 | 0.09613 | -0.27466 | -0.059509 | -0.19684 | -0.07782 | 0.32043 | 0.022888 | 0.21973 | -0.050354 | 121.4539 | 121.1929 | 76.4832 | -121.3211 | 121.3898 | 121.4172 | 81.5552 | -121.6644
1982.7969 | 121.5775 | -120.6573 | 0.74616 | -0.00099167 | 0.0086006 | 0.07313 | 0.0057656 | 0.063643 | 0.001363 | -0.0025164 | 0.0069425 | -0.00086724 | 0.05997 | 0.066796 | -0.0081305 | -0.0095873 | 0.45319 | -119.1284 | -44.5084 | -120.5154 | 0.8194 | -120.7306 | -120.6573 | -120.2866 | -39.1388 | -120.694 | 0.81482 | 0.86517 | -120.7077 | -120.8817 | -0.073242 | 0 | 0.073242 | 1.5289 | 0.14191 | 0.14191 | -0.29297 | -0.050354 | -0.2243 | 0.068664 | 0.37079 | -0.036621 | 0.18768 | 0.11902 | 121.4767 | 121.1105 | 76.149 | -121.4035 | 121.4722 | 121.5225 | 81.5186 | -121.6278
1984.4844 | 121.6049 | -120.6894 | 0.71869 | -0.0086212 | 0.0079596 | 0.074625 | 0.010252 | 0.062147 | -0.0029094 | -0.0042254 | 0.014572 | -0.0036444 | 0.061466 | 0.063591 | -0.011121 | -0.0072375 | 0.44403 | -119.0369 | -44.6457 | -120.5612 | 0.69122 | -120.8038 | -120.7169 | -120.4056 | -39.3036 | -120.7901 | 0.60883 | 0.62714 | -120.845 | -121.0144 | -0.11444 | -0.027466 | -0.027466 | 1.6525 | 0.12817 | 0.15564 | -0.27466 | -0.15564 | -0.32501 | -0.10986 | 0.28381 | -0.10071 | 0.2243 | -0.091553 | 121.3806 | 121.1334 | 76.0437 | -121.4355 | 121.2982 | 121.3165 | 81.3858 | -121.7331
1986.1719 | 121.6278 | -120.8176 | 0.54016 | 0.0066373 | 0.007746 | 0.067362 | 0.010893 | 0.063643 | 0.003072 | -0.0035846 | 0.0069425 | -0.00065364 | 0.062107 | 0.065728 | -0.0066351 | -0.0076647 | 0.33417 | -119.2429 | -44.7784 | -120.6985 | 0.64545 | -120.932 | -120.845 | -120.5383 | -39.7842 | -120.9869 | 0.56305 | 0.59509 | -120.7077 | -120.7489 | -0.11444 | -0.027466 | 0.10529 | 1.5747 | 0.11902 | 0.14648 | -0.20599 | 0.10986 | 0.068665 | 0.022888 | 0.27924 | -0.16937 | -0.23804 | 0.054932 | 121.463 | 121.1517 | 76.0391 | -121.3852 | 121.3806 | 121.4127 | 81.0333 | -121.2891
1987.8438 | 121.6003 | -120.8313 | 0.59509 | -0.0086212 | 0.009455 | 0.074625 | 0.0070474 | 0.062788 | -0.0056866 | -0.003371 | -0.00068649 | -0.0051398 | 0.060398 | 0.061669 | -0.0089849 | -0.0070239 | 0.45319 | -119.0277 | -45.0439 | -120.607 | 0.66376 | -120.8588 | -120.813 | -120.6024 | -39.9353 | -121.0098 | 0.41657 | 0.43488 | -121.0327 | -121.1563 | -0.027466 | 0.018311 | 0.068664 | 1.8036 | 0.2243 | 0.20599 | -0.14191 | -0.20142 | -0.32501 | -0.17853 | 0.22888 | -0.17853 | 0.14648 | -0.16022 | 121.4951 | 121.2845 | 75.7874 | -121.4081 | 121.2479 | 121.2662 | 80.896 | -121.7514
1989.5156 | 121.6553 | -121.019 | 0.45319 | -0.00099167 | 0.0096686 | 0.070353 | 0.0042702 | 0.06407 | 0.003072 | -0.0029436 | -0.00068649 | 0.00084176 | 0.063816 | 0.065087 | -0.0079169 | -0.0089465 | 0.19226 | -119.371 | -45.8633 | -120.845 | 0.5127 | -121.1014 | -121.019 | -120.6482 | -40.0589 | -121.1197 | 0.42572 | 0.44403 | -121.1151 | -121.2799 | -0.082397 | 0 | 0.059509 | 1.6479 | 0.17395 | 0.17395 | -0.26092 | -0.09613 | -0.26093 | -0.027466 | 0.37079 | -0.10071 | 0.16022 | -0.009155 | 121.5317 | 121.2112 | 75.1556 | -121.4722 | 121.4447 | 121.463 | 80.9601 | -121.7331
1991.2344 | 121.5225 | -121.1014 | 0.49439 | 0.0066373 | 0.0062506 | 0.071848 | 0.0019204 | 0.063002 | 0.00414 | -0.0025164 | 0.014572 | -0.00044004 | 0.06232 | 0.066155 | -0.0047125 | -0.0051013 | 0.16937 | -119.4077 | -46.1014 | -120.8862 | 0.51727 | -121.1151 | -120.9915 | -120.7031 | -40.6174 | -121.2067 | 0.41199 | 0.4303 | -121.1472 | -121.3486 | -0.013733 | 0.10986 | 0.022888 | 1.6937 | 0.21515 | 0.10529 | -0.32501 | -0.045777 | -0.24719 | -0.082398 | 0.39825 | -0.10529 | 0.14191 | -0.064087 | 121.6187 | 121.2708 | 75 | -121.4859 | 121.5134 | 121.5317 | 80.484 | -121.843
1992.9219 | 121.6049 | -121.1151 | 0.40741 | -0.00099167 | 0.0088142 | 0.070566 | 0.007261 | 0.062147 | -0.0035504 | -0.004439 | -0.00068649 | -0.0044988 | 0.061893 | 0.060814 | -0.0087713 | -0.0063831 | 0.17395 | -119.3253 | -45.8084 | -120.8725 | 0.4303 | -121.138 | -121.0327 | -120.6619 | -40.6677 | -121.1105 | 0.32501 | 0.36163 | -121.2021 | -121.3348 | -0.022888 | 0.082397 | 0.022888 | 1.7899 | 0.24261 | 0.16022 | -0.23346 | -0.086975 | -0.21973 | -0.082398 | 0.45319 | 0.004577 | 0.2243 | -0.045777 | 121.5454 | 121.2891 | 75.3067 | -121.4401 | 121.4401 | 121.4767 | 80.4474 | -121.7422
1994.625 | 121.6461 | -121.106 | 0.39368 | -0.00099167 | 0.011164 | 0.073984 | 0.0066202 | 0.06642 | -0.0052594 | -0.0029436 | 0.0069425 | -0.0057806 | 0.060398 | 0.063378 | -0.0096259 | -0.0068103 | 0.20599 | -119.2429 | -45.7993 | -120.8679 | 0.44403 | -121.0968 | -121.0144 | -120.6116 | -40.7684 | -121.0739 | 0.35706 | 0.37537 | -121.1884 | -121.3394 | 0.009155 | 0.091553 | 0.050354 | 1.8631 | 0.23804 | 0.14648 | -0.18768 | -0.082397 | -0.23346 | -0.036621 | 0.49439 | 0.032043 | 0.2655 | -0.018311 | 121.55 | 121.312 | 75.3067 | -121.4081 | 121.463 | 121.4813 | 80.3375 | -121.7331
1996.3438 | 121.7056 | -121.0739 | 0.44861 | -0.00099167 | 0.010096 | 0.07313 | 0.0068338 | 0.063856 | 0.0032856 | -0.001021 | -0.008316 | -0.00086724 | 0.059757 | 0.0653 | -0.0055671 | -0.0083057 | 0.13733 | -119.4031 | -45.9183 | -120.9091 | 0.48981 | -121.1609 | -121.0327 | -120.6665 | -40.6815 | -121.1884 | 0.39825 | 0.43488 | -121.2112 | -121.3486 | -0.086975 | 0.041199 | 0.041199 | 1.6708 | 0.16479 | 0.1236 | -0.31128 | -0.13733 | -0.27466 | -0.050354 | 0.40741 | -0.11444 | 0.16022 | -0.013733 | 121.5637 | 121.2112 | 75.1556 | -121.4813 | 121.4722 | 121.5088 | 80.3925 | -121.7972
1998.0312 | 121.6187 | -120.4514 | 0.93842 | 0.0066373 | 0.01095 | 0.076334 | 0.007261 | 0.061934 | -0.0024822 | -0.003371 | 0.014572 | -0.005567 | 0.062748 | 0.0653 | -0.010053 | -0.0061695 | 0.1831 | -119.2841 | -46.106 | -120.9 | 0.42114 | -121.1426 | -121.0556 | -120.6253 | -40.6586 | -121.1243 | 0.32959 | 0.36163 | -121.225 | -121.3669 | -0.69122 | -0.60425 | -0.51727 | 1.1673 | -0.44861 | 0.15564 | -0.75531 | -0.77362 | -0.91553 | -0.60883 | -0.17395 | -0.67291 | 0.24261 | -0.57678 | 120.8725 | 120.6345 | 74.3454 | -121.994 | 120.7809 | 120.813 | 79.7928 | -122.3053
1999.7188 | 121.6049 | -121.0556 | 0.54474 | 0.0066373 | 0.015864 | 0.07313 | 0.005552 | 0.06407 | -0.0022686 | -0.0048662 | -0.00068649 | -0.0034308 | 0.061252 | 0.066155 | -0.0079169 | -0.0072375 | 0.35248 | -119.1742 | -45.9366 | -120.7764 | 0.62714 | -121.0007 | -120.9091 | -120.4468 | -40.86 | -120.9503 | 0.6134 | 0.62714 | -121.0602 | -121.2616 | 0.054932 | 0.14648 | 0.082397 | 1.8814 | 0.27924 | 0.13275 | -0.19226 | -0.004578 | -0.20599 | 0.068664 | 0.60883 | 0.10529 | 0.31128 | 0.082397 | 121.6827 | 121.4081 | 75.119 | -121.4539 | 121.669 | 121.6827 | 80.1956 | -121.8063
2001.4531 | 121.6095 | -121.0602 | 0.50354 | 0.0066373 | 0.012873 | 0.073557 | 0.0025612 | 0.065351 | 0.0039264 | -0.0012346 | 0.0069425 | 0.00020076 | 0.060398 | 0.066582 | -0.0066351 | -0.010228 | 0.30212 | -119.2245 | -45.8496 | -120.7993 | 0.50812 | -121.0602 | -120.9824 | -120.4697 | -41.3269 | -121.0922 | 0.43488 | 0.45776 | -121.1105 | -121.2708 | 0 | 0.07782 | 0.004578 | 1.8356 | 0.26093 | 0.18311 | -0.20142 | -0.050354 | -0.21057 | -0.068665 | 0.59051 | -0.032043 | 0.17853 | -0.045776 | 121.5683 | 121.3623 | 75.2106 | -121.4859 | 121.4951 | 121.5179 | 79.7333 | -121.7743
2003.1406 | 121.701 | -120.7718 | 0.80566 | -0.00099167 | 0.0066778 | 0.069498 | 0.0064066 | 0.061934 | 0.0045674 | -0.0031574 | 0.0069425 | 0.00020076 | 0.060611 | 0.06765 | -0.0055671 | -0.0087329 | 0.97961 | -118.515 | -45.5109 | -119.902 | 1.474 | -120.1492 | -120.0256 | -119.5358 | -40.7043 | -119.9936 | 1.506 | 1.5656 | -120.0439 | -120.1904 | 0.62256 | 0.74616 | 0.66834 | 2.2568 | 0.86975 | 0.1236 | 0.17395 | 0.72785 | 0.58136 | 0.70038 | 1.236 | 0.7782 | 0.19684 | 0.75989 | 122.2458 | 121.7514 | 75.2609 | -120.8313 | 122.2778 | 122.3373 | 80.0674 | -120.9961
2004.9688 | 121.6965 | -121.138 | 0.39825 | -0.00099167 | 0.0086006 | 0.069925 | 0.002134 | 0.06407 | 0.00414 | -0.00038024 | -0.00068649 | -0.00044004 | 0.061466 | 0.064873 | -0.0059943 | -0.0053149 | 0.17853 | -119.3115 | -45.8542 | -120.9686 | 0.4715 | -121.1975 | -121.1243 | -120.6528 | -41.0431 | -121.2616 | 0.35248 | 0.37994 | -121.2433 | -121.4172 | -0.05951 | 0.013732 | 0.073243 | 1.8265 | 0.16937 | 0.15564 | -0.21973 | -0.10529 | -0.27924 | -0.045776 | 0.48523 | -0.1236 | 0.15564 | -0.01831 | 121.6095 | 121.3165 | 75.2838 | -121.5225 | 121.4905 | 121.5179 | 80.0949 | -121.8155
2006.8125 | 121.637 | -121.1151 | 0.43945 | 0.0066373 | 0.013514 | 0.071421 | 0.0051248 | 0.061506 | 0.0045674 | -0.00080744 | 0.0069425 | -0.00044004 | 0.065097 | 0.067437 | -0.0064215 | -0.0051013 | 0.12817 | -119.3939 | -45.7855 | -120.9961 | 0.48523 | -121.2204 | -121.1197 | -120.6711 | -40.6998 | -121.2616 | 0.43488 | 0.43488 | -121.2204 | -121.3806 | -0.10529 | -0.004578 | 0.045776 | 1.7212 | 0.11902 | 0.1236 | -0.31128 | -0.10529 | -0.2655 | -0.004578 | 0.44403 | -0.14648 | 0.11902 | -0.004578 | 121.6003 | 121.2433 | 75.3296 | -121.5591 | 121.55 | 121.55 | 80.4153 | -121.8201
2008.6719 | 121.6782 | -121.0693 | 0.48981 | 0.014267 | 0.011164 | 0.072275 | 0.0064066 | 0.061934 | -0.0039776 | -0.0020892 | -0.00068649 | -0.0040716 | 0.060184 | 0.064019 | -0.010908 | -0.0053149 | 0.21515 | -119.1925 | -45.9457 | -120.5658 | 0.50354 | -120.9229 | -120.8771 | -120.5795 | -40.6036 | -121.1517 | 0.4303 | 0.45776 | -121.1975 | -121.3577 | 0.14648 | 0.19226 | 0.013733 | 1.8768 | 0.50354 | 0.31128 | -0.27466 | -0.12817 | -0.28839 | -0.059509 | 0.48981 | -0.082397 | 0.20599 | -0.032043 | 121.5729 | 121.2845 | 75.1236 | -121.3669 | 121.4996 | 121.5271 | 80.4657 | -121.8475
2010.7188 | 121.7331 | -121.1472 | 0.38452 | -0.00099167 | 0.013514 | 0.074198 | 0.0081154 | 0.060225 | -0.0050458 | -0.0037982 | 0.0069425 | -0.0034308 | 0.05997 | 0.062737 | -0.0091985 | -0.0063831 | 0.15106 | -119.2566 | -46.2799 | -120.9457 | 0.42572 | -121.2021 | -121.0968 | -120.5887 | -40.8646 | -121.1334 | 0.32044 | 0.3479 | -121.2341 | -121.3852 | -0.054931 | 0.050354 | 0.041199 | 1.8906 | 0.20142 | 0.15106 | -0.23346 | -0.086975 | -0.23804 | -0.064086 | 0.55847 | 0.013733 | 0.25177 | -0.036621 | 121.5729 | 121.2982 | 74.8672 | -121.4813 | 121.4676 | 121.4951 | 80.2826 | -121.7697
2012.6875 | 121.5912 | -121.2936 | 0.38452 | 0.0066373 | 0.010523 | 0.071848 | 0.005552 | 0.062361 | 0.0073444 | -0.0023028 | -0.008316 | 0.0019098 | 0.061466 | 0.066796 | -0.0047125 | -0.0087329 | 0.045776 | -119.426 | -46.8658 | -121.0876 | 0.41657 | -121.2936 | -121.2112 | -120.7352 | -40.8371 | -121.3852 | 0.34332 | 0.34332 | -121.3211 | -121.4539 | 0 | 0.082397 | 0.032044 | 1.8677 | 0.20599 | 0.1236 | -0.33875 | -0.027466 | -0.16022 | -0.041198 | 0.55847 | -0.091553 | 0.068664 | -0.041198 | 121.7102 | 121.3394 | 74.4278 | -121.5958 | 121.637 | 121.637 | 80.4565 | -121.8384
2016.1875 | 121.5912 | -121.1746 | 0.48065 | 0.0066373 | 0.012873 | 0.068003 | 0.0087564 | 0.063215 | 8.1158e-05 | -0.0031574 | -0.008316 | -0.0032172 | 0.064029 | 0.066796 | -0.012189 | -0.0083057 | 0.26093 | -119.0872 | -46.7972 | -120.8908 | 0.5127 | -121.1288 | -121.0281 | -120.4193 | -40.3839 | -121.0831 | 0.41657 | 0.44403 | -121.1792 | -121.3028 | 0.045777 | 0.14648 | 0.032043 | 2.0874 | 0.28381 | 0.13733 | -0.21973 | -0.004577 | -0.12817 | -0.064087 | 0.75531 | 0.091553 | 0.21973 | -0.036621 | 121.6873 | 121.4355 | 74.3774 | -121.5088 | 121.5912 | 121.6187 | 80.7907 | -121.7834
2017.9844 | 121.0281 | -119.989 | 0.83771 | -0.00099167 | 0.013727 | 0.073771 | 0.0079018 | 0.063002 | -0.0056866 | -0.0059344 | 0.0069425 | -0.0036444 | 0.060611 | 0.065728 | -0.0091985 | -0.0083057 | 0.54932 | -118.103 | -46.4493 | -119.8334 | 0.84686 | -120.0577 | -119.9936 | -119.4397 | -40.3336 | -120.0714 | 0.75989 | 0.79193 | -120.0989 | -120.2911 | -0.068664 | -0.004577 | 0.009155 | 1.886 | 0.15564 | 0.16022 | -0.28839 | -0.10986 | -0.30212 | -0.07782 | 0.54932 | -0.082397 | 0.21973 | -0.045777 | 120.8359 | 120.5383 | 73.5397 | -120.8313 | 120.7489 | 120.7809 | 79.6555 | -121.1288
2019.6719 | 121.3715 | -120.7947 | 0.39825 | 0.014267 | 0.0071052 | 0.07078 | 0.0098244 | 0.063215 | 0.00072196 | -0.003371 | 0.0069425 | -0.0012946 | 0.061252 | 0.067223 | -0.0085577 | -0.0089465 | 0.10529 | -118.9453 | -47.3236 | -120.6665 | 0.46234 | -120.9 | -120.8084 | -120.282 | -40.5579 | -120.9778 | 0.39368 | 0.40741 | -120.9412 | -121.1014 | -0.10528 | -0.013733 | 0.064087 | 1.8494 | 0.12817 | 0.14191 | -0.29297 | -0.14648 | -0.3067 | -0.004577 | 0.5127 | -0.1831 | 0.1236 | 0.009156 | 121.257 | 120.9 | 73.4711 | -121.2067 | 121.1884 | 121.2021 | 80.2368 | -121.4996
2021.3594 | 121.3715 | -120.8267 | 0.48065 | 0.0066373 | 0.01095 | 0.071848 | 0.0057656 | 0.063215 | 0.001363 | -0.0020892 | 0.014572 | -0.00022644 | 0.05997 | 0.066368 | -0.0042853 | -0.0072375 | 0.13733 | -119.0186 | -47.3831 | -120.7352 | 0.45776 | -120.9686 | -120.8862 | -120.314 | -39.7522 | -120.8908 | 0.32501 | 0.33875 | -120.9824 | -121.1197 | -0.14191 | -0.059509 | -0.022888 | 1.8082 | 0.091553 | 0.15106 | -0.34332 | -0.15564 | -0.29297 | -0.15564 | 0.5127 | -0.064087 | 0.22888 | -0.14191 | 121.2845 | 120.9641 | 73.4436 | -121.3669 | 121.1517 | 121.1655 | 81.0745 | -121.6003
2023.0312 | 121.4584 | -121.0373 | 0.27466 | 0.0066373 | 0.0056098 | 0.07078 | 0.0079018 | 0.065351 | 8.1158e-05 | -0.00273 | 0.0069425 | -0.00065364 | 0.062748 | 0.066582 | -0.0077033 | -0.0072375 | 0.041199 | -119.1284 | -47.4197 | -120.813 | 0.40283 | -121.0648 | -121.0007 | -120.4193 | -39.83 | -121.1426 | 0.3067 | 0.3067 | -121.1334 | -121.2845 | -0.027466 | 0.036621 | 0.12817 | 1.9089 | 0.2243 | 0.18768 | -0.23346 | -0.096131 | -0.24719 | 0.032044 | 0.61798 | -0.10529 | 0.14191 | 0.032044 | 121.4401 | 121.0785 | 73.6176 | -121.2753 | 121.344 | 121.344 | 81.2073 | -121.5591
2024.7188 | 121.5088 | -121.0144 | 0.3067 | -0.00099167 | 0.012232 | 0.072062 | 0.0091836 | 0.063429 | -0.0033368 | -0.0029436 | -0.008316 | -0.0040716 | 0.062748 | 0.062096 | -0.010908 | -0.0068103 | 0.21515 | -118.8858 | -47.5479 | -120.6345 | 0.47607 | -120.9183 | -120.8359 | -120.1492 | -39.5645 | -120.8267 | 0.45319 | 0.46692 | -120.8588 | -121.0236 | 0.09613 | 0.17853 | 0.16937 | 2.1286 | 0.37994 | 0.20142 | -0.091553 | 0.15564 | -0.009156 | 0.14648 | 0.86517 | 0.18768 | 0.19684 | 0.16022 | 121.4905 | 121.2296 | 73.4665 | -121.1426 | 121.4676 | 121.4813 | 81.4499 | -121.3303
2026.4531 | 120.9686 | -120.7855 | 0.17853 | -0.00099167 | 0.014796 | 0.072702 | 0.0019204 | 0.063215 | -0.00055964 | -0.00273 | -0.00068649 | -0.0057806 | 0.061893 | 0.0653 | -0.0087713 | -0.0065967 | -0.073242 | -118.7485 | -48.1888 | -120.5658 | 0.16479 | -120.7809 | -120.694 | -120.0485 | -40.0909 | -120.8176 | 0.086975 | 0.091553 | -120.8496 | -121.0098 | 0.004577 | 0.091552 | -0.013733 | 2.037 | 0.21973 | 0.12817 | -0.25177 | -0.064087 | -0.22431 | -0.091553 | 0.737 | -0.032044 | 0.19226 | -0.086975 | 120.9503 | 120.7123 | 72.5967 | -120.8725 | 120.8725 | 120.8771 | 80.6946 | -121.1884
2028.1406 | 120.8725 | -120.7901 | 0.13733 | -0.00099167 | 0.014796 | 0.070566 | 0.0051248 | 0.063429 | 0.0015766 | -0.0023028 | 0.0069425 | -0.0019354 | 0.060825 | 0.065941 | -0.0040717 | -0.0083057 | -0.068665 | -118.6844 | -48.3673 | -120.4971 | 0.14191 | -120.7397 | -120.6665 | -119.9295 | -39.949 | -120.7489 | 0.050354 | 0.064087 | -120.7901 | -120.9229 | 0.050354 | 0.1236 | 0.004578 | 2.1057 | 0.29297 | 0.16937 | -0.20599 | 0 | -0.13275 | -0.086975 | 0.8606 | 0.041199 | 0.17395 | -0.073242 | 120.932 | 120.7214 | 72.4228 | -120.8038 | 120.8405 | 120.8542 | 80.8411 | -121.0602
2029.8125 | 120.7443 | -120.5887 | 0.11902 | 0.014267 | 0.0064642 | 0.071207 | 0.0081154 | 0.063429 | -0.0012006 | -0.0029436 | -0.00068649 | -0.00086724 | 0.06232 | 0.066368 | -0.0083441 | -0.0087329 | -0.16937 | -118.5516 | -48.6191 | -120.3552 | 0.19226 | -120.6207 | -120.5383 | -119.8837 | -40.3702 | -120.6619 | 0.09613 | 0.11444 | -120.6757 | -120.8267 | -0.032044 | 0.050354 | 0.073242 | 2.037 | 0.23346 | 0.1831 | -0.28839 | -0.086975 | -0.23804 | -0.022889 | 0.70496 | -0.073242 | 0.1648 | -0.004578 | 120.7809 | 120.4193 | 71.9696 | -120.6573 | 120.6848 | 120.7031 | 80.2185 | -120.9457
2031.5312 | 121.0236 | -120.9595 | 0.13275 | -0.00099167 | 0.007746 | 0.068857 | 0.0034158 | 0.065992 | 0.0045674 | 0.00047416 | 0.0069425 | -0.0015082 | 0.061679 | 0.06765 | -0.0034307 | -0.0085193 | -0.009155 | -118.808 | -48.8708 | -120.6116 | 0.27008 | -120.8359 | -120.7764 | -120.0211 | -40.7089 | -120.9457 | 0.1831 | 0.20599 | -120.8771 | -121.0556 | 0.1236 | 0.18311 | 0.13733 | 2.1515 | 0.3479 | 0.16479 | -0.14191 | 0.082398 | -0.09613 | 0.050354 | 0.93842 | 0.013733 | 0.10986 | 0.073243 | 121.2296 | 120.9503 | 72.0886 | -120.9091 | 121.1426 | 121.1655 | 80.2506 | -121.1884
2033.2188 | 121.138 | -120.9869 | 0.11444 | 0.014267 | 0.012232 | 0.073557 | 0.0093972 | 0.064283 | -0.0029094 | -0.00273 | 0.0069425 | -0.003858 | 0.061252 | 0.063805 | -0.0091985 | -0.0053149 | -0.1831 | -118.895 | -48.999 | -120.7489 | 0.15564 | -121.0007 | -120.932 | -120.2042 | -40.242 | -120.9961 | 0.064087 | 0.082397 | -121.0419 | -121.2158 | -0.013733 | 0.054931 | 0.041199 | 2.092 | 0.23804 | 0.18311 | -0.29755 | -0.054932 | -0.22888 | -0.050354 | 0.78278 | -0.009156 | 0.21973 | -0.032044 | 121.1426 | 120.8038 | 71.9879 | -121.0464 | 121.051 | 121.0693 | 80.7449 | -121.3303
2034.9219 | 121.2753 | -121.0052 | 0.11902 | -0.0086212 | 0.010309 | 0.070139 | 0.0057656 | 0.064283 | 0.0037128 | 4.696e-05 | -0.00068649 | 0.00020076 | 0.060184 | 0.064659 | -0.0055671 | -0.0093737 | -0.15564 | -118.9362 | -49.0952 | -120.8221 | 0.17853 | -121.0739 | -121.0007 | -120.2316 | -40.1779 | -121.1288 | 0.09613 | 0.11444 | -121.1472 | -121.2845 | -0.068665 | 0.004578 | 0.059509 | 2.0691 | 0.18311 | 0.17853 | -0.27466 | -0.14191 | -0.27924 | -0.022889 | 0.77362 | -0.1236 | 0.15564 | -0.004578 | 121.1838 | 120.8496 | 71.9101 | -121.1197 | 121.1014 | 121.1197 | 80.8273 | -121.4035
2036.6094 | 121.2891 | -121.0464 | 0.11902 | -0.016251 | 0.011164 | 0.072916 | 0.0085428 | 0.062147 | -0.0029094 | -0.0031574 | -0.00068649 | -0.0047124 | 0.063602 | 0.063591 | -0.01048 | -0.0051013 | -0.10071 | -118.808 | -49.2645 | -120.7764 | 0.15106 | -121.0922 | -121.0052 | -120.1767 | -40.4297 | -121.0281 | 0.054932 | 0.068665 | -121.1472 | -121.2708 | -0.045776 | 0.041199 | 0.032043 | 2.2385 | 0.27008 | 0.22888 | -0.21973 | -0.10071 | -0.2243 | -0.064087 | 0.86975 | 0.018311 | 0.24262 | -0.050354 | 121.1975 | 120.9457 | 71.7819 | -121.1243 | 121.1014 | 121.1151 | 80.6168 | -121.3898
2038.2969 | 121.2021 | -121.1105 | 0.15564 | -0.00099167 | 0.010309 | 0.072489 | 0.00063865 | 0.06172 | 0.0060626 | -0.001021 | -0.00068649 | 0.00020076 | 0.060611 | 0.066155 | -0.0049261 | -0.0098009 | -0.15564 | -118.9728 | -49.585 | -120.9 | 0.18768 | -121.1105 | -121.0556 | -120.2591 | -41.1392 | -121.2433 | 0.091553 | 0.11444 | -121.1975 | -121.3348 | 0 | 0.054932 | 0.032043 | 2.1378 | 0.21057 | 0.15564 | -0.31128 | -0.086975 | -0.2243 | -0.064087 | 0.85144 | -0.13275 | 0.091553 | -0.041199 | 121.2982 | 120.9549 | 71.5256 | -121.2112 | 121.2021 | 121.225 | 79.9713 | -121.4905
2040 | 121.3394 | -121.0968 | 0.11902 | 0.0066373 | 0.0062506 | 0.069925 | 0.00897 | 0.062788 | 0.00093576 | -0.0023028 | 0.0069425 | 0.001269 | 0.062961 | 0.068291 | -0.0072759 | -0.0070239 | -0.19684 | -118.9499 | -49.6262 | -120.9137 | 0.17853 | -121.1838 | -121.1105 | -120.2637 | -41.4505 | -121.2341 | 0.10986 | 0.1236 | -121.2204 | -121.3623 | -0.086975 | -0.013733 | 0.059509 | 2.1469 | 0.18311 | 0.19684 | -0.31586 | -0.1236 | -0.2655 | -0.009156 | 0.83313 | -0.13733 | 0.12817 | 0.004577 | 121.2753 | 120.9 | 71.4706 | -121.2296 | 121.2067 | 121.2204 | 79.6463 | -121.4813
2041.6875 | 121.2479 | -121.17 | 0.14191 | -0.00099167 | 0.0088142 | 0.069925 | 0.0042702 | 0.06407 | 0.00414 | -0.00059384 | -0.00068649 | 0.00020076 | 0.063602 | 0.067009 | -0.0047125 | -0.0059557 | -0.18768 | -118.9499 | -49.5071 | -120.9274 | 0.16937 | -121.1655 | -121.0739 | -120.2408 | -41.4688 | -121.2708 | 0.10071 | 0.11902 | -121.2524 | -121.376 | 0.004578 | 0.09613 | 0.027466 | 2.2202 | 0.24262 | 0.14648 | -0.32959 | -0.082397 | -0.20599 | -0.041199 | 0.92926 | -0.10071 | 0.10529 | -0.022888 | 121.3394 | 120.9824 | 71.6629 | -121.2158 | 121.2708 | 121.2891 | 79.7012 | -121.5179
2043.3594 | 121.3577 | -121.1105 | 0.10986 | -0.0086212 | 0.010523 | 0.075479 | 0.0093972 | 0.065565 | -0.0048322 | -0.0035846 | 0.0069425 | -0.006635 | 0.062107 | 0.064873 | -0.0089849 | -0.0063831 | -0.11902 | -118.7256 | -49.4934 | -120.845 | 0.15564 | -121.1517 | -121.0785 | -120.1309 | -41.5329 | -121.1151 | 0.041199 | 0.073242 | -121.2067 | -121.3623 | -0.041198 | 0.032044 | 0.045777 | 2.3849 | 0.2655 | 0.23346 | -0.22888 | -0.09613 | -0.25177 | -0.068664 | 0.97961 | -0.004577 | 0.24719 | -0.036621 | 121.2662 | 120.9915 | 71.6171 | -121.1884 | 121.1517 | 121.1838 | 79.5776 | -121.4722
2045.0469 | 121.3211 | -121.1746 | 0.13733 | 0.0066373 | 0.010737 | 0.072275 | 0.0053384 | 0.062361 | 0.001363 | -0.0040118 | 0.014572 | -0.002149 | 0.060398 | 0.0653 | -0.0049261 | -0.0087329 | -0.1236 | -118.7943 | -49.5758 | -120.9 | 0.17853 | -121.1655 | -121.0831 | -120.0943 | -41.6428 | -121.1517 | 0.045776 | 0.082397 | -121.225 | -121.376 | 0.009156 | 0.091553 | 0.041199 | 2.3804 | 0.27466 | 0.18311 | -0.26093 | -0.050354 | -0.20142 | -0.091553 | 1.0803 | 0.022889 | 0.22431 | -0.054932 | 121.3531 | 121.051 | 71.5988 | -121.2204 | 121.2204 | 121.257 | 79.5319 | -121.5134
2046.75 | 121.3486 | -121.17 | 0.13275 | -0.00099167 | 0.012232 | 0.071848 | 0.002775 | 0.064711 | 0.00050836 | -0.0018756 | -0.00068649 | 0.00020076 | 0.060611 | 0.065514 | -0.0042853 | -0.0061695 | -0.12817 | -118.8263 | -49.8505 | -120.9503 | 0.16937 | -121.1929 | -121.1197 | -120.0943 | -41.8167 | -121.1884 | 0.050354 | 0.086975 | -121.2341 | -121.3989 | -0.022888 | 0.050354 | 0.036622 | 2.3438 | 0.21973 | 0.16937 | -0.26093 | -0.064087 | -0.22888 | -0.082397 | 1.0757 | -0.01831 | 0.21057 | -0.045776 | 121.3394 | 121.0419 | 71.3196 | -121.2524 | 121.2204 | 121.257 | 79.3533 | -121.5317
2048.5 | 121.3074 | -121.1975 | 0.14191 | 0.014267 | 0.0133 | 0.07078 | 0.0042702 | 0.063643 | -0.0012006 | -0.00059384 | 0.0069425 | -0.0042852 | 0.06232 | 0.065941 | -0.0072759 | -0.0048877 | -0.082397 | -118.7073 | -50.0427 | -120.9091 | 0.13733 | -121.1838 | -121.1105 | -120.0485 | -41.4368 | -121.17 | 0.050354 | 0.082397 | -121.225 | -121.4218 | 0.013733 | 0.086975 | -0.004578 | 2.4902 | 0.28839 | 0.20142 | -0.2243 | -0.027466 | -0.2243 | -0.091553 | 1.149 | 0.027466 | 0.25177 | -0.05951 | 121.3348 | 121.1151 | 71.1548 | -121.2524 | 121.2479 | 121.2799 | 79.7607 | -121.5637
2050.1875 | 121.4355 | -121.1975 | 0.10071 | 0.0066373 | 0.010096 | 0.072489 | 0.0059792 | 0.066206 | 0.001363 | -0.0055072 | 0.014572 | -0.0019354 | 0.06232 | 0.067864 | -0.0072759 | -0.0091601 | -0.17853 | -118.8126 | -50.4181 | -120.9915 | 0.19684 | -121.2524 | -121.17 | -120.1035 | -41.716 | -121.3028 | 0.091553 | 0.10986 | -121.2936 | -121.4401 | -0.054931 | 0.027466 | 0.09613 | 2.3849 | 0.20599 | 0.17853 | -0.27924 | -0.09613 | -0.24262 | -0.009155 | 1.0941 | -0.10529 | 0.13733 | 0.009155 | 121.3943 | 121.019 | 70.7794 | -121.2708 | 121.2891 | 121.3074 | 79.4815 | -121.5408
2051.9062 | 121.4127 | -121.1792 | 0.10986 | -0.00099167 | 0.010309 | 0.073557 | 0.007261 | 0.062574 | -0.0044048 | -0.0037982 | 0.0069425 | -0.0025762 | 0.061252 | 0.065941 | -0.010053 | -0.0072375 | -0.073242 | -118.634 | -50.3082 | -120.9137 | 0.13733 | -121.225 | -121.1197 | -119.9753 | -41.4047 | -121.1929 | 0.041199 | 0.07782 | -121.2387 | -121.4172 | -0.045777 | 0.059509 | 0.027466 | 2.5452 | 0.2655 | 0.20599 | -0.18311 | -0.059509 | -0.23804 | -0.068664 | 1.2039 | -0.013733 | 0.2243 | -0.032043 | 121.3165 | 121.106 | 70.871 | -121.2296 | 121.2204 | 121.257 | 79.7745 | -121.5271
2053.5938 | 121.431 | -121.2067 | 0.14191 | -0.00099167 | 0.0079596 | 0.070353 | 0.0049112 | 0.064711 | 0.003072 | -0.0029436 | -0.00068649 | 0.00084176 | 0.060825 | 0.067864 | -0.0055671 | -0.0080921 | -0.10071 | -118.6661 | -50.3632 | -120.9641 | 0.17395 | -121.2616 | -121.1609 | -119.9753 | -41.2125 | -121.2936 | 0.082397 | 0.10071 | -121.3074 | -121.463 | -0.054932 | 0.045776 | 0.032043 | 2.5406 | 0.24262 | 0.19684 | -0.24262 | -0.10071 | -0.25635 | -0.05951 | 1.2314 | -0.086975 | 0.16937 | -0.041199 | 121.3806 | 121.106 | 70.8435 | -121.3028 | 121.2891 | 121.3074 | 79.9942 | -121.6049
2055.2812 | 121.3348 | -121.2479 | 0.15106 | 0.0066373 | 0.010737 | 0.074198 | 0.0064066 | 0.064711 | -0.0031232 | -0.0012346 | -0.00068649 | -0.003858 | 0.060611 | 0.064232 | -0.0064215 | -0.0074511 | -0.086975 | -118.5654 | -50.1434 | -120.9503 | 0.14648 | -121.2479 | -121.1426 | -119.9112 | -41.5009 | -121.2204 | 0.032043 | 0.082397 | -121.2936 | -121.4401 | 0 | 0.10529 | -0.004578 | 2.6825 | 0.29755 | 0.19226 | -0.23804 | -0.045776 | -0.19226 | -0.11902 | 1.3367 | 0.027466 | 0.21973 | -0.068665 | 121.3943 | 121.1609 | 71.1044 | -121.2936 | 121.2799 | 121.3303 | 79.747 | -121.5912
2056.9844 | 121.4722 | -121.1929 | 0.10529 | 0.0066373 | 0.013941 | 0.072916 | 0.010252 | 0.064924 | -0.0026958 | -0.003371 | -0.00068649 | -0.0059942 | 0.063602 | 0.064446 | -0.011121 | -0.0057421 | -0.11444 | -118.5242 | -50.0381 | -120.9595 | 0.16479 | -121.2524 | -121.1472 | -119.8746 | -41.5924 | -121.2021 | 0.07782 | 0.064087 | -121.3348 | -121.4722 | -0.059509 | 0.045776 | 0.059509 | 2.6688 | 0.23346 | 0.18768 | -0.21973 | -0.14191 | -0.27924 | -0.027466 | 1.3184 | -0.009155 | 0.27008 | -0.041199 | 121.3577 | 121.0785 | 71.1548 | -121.2524 | 121.2708 | 121.257 | 79.6005 | -121.5775
2058.6719 | 121.3577 | -121.2845 | 0.15564 | -0.0086212 | 0.015223 | 0.079111 | 0.0051248 | 0.062788 | 8.1158e-05 | -0.004439 | 0.0069425 | -0.0042852 | 0.058475 | 0.0653 | -0.0053533 | -0.0074511 | -0.10529 | -118.5333 | -50.2808 | -121.0052 | 0.15106 | -121.2662 | -121.1655 | -119.902 | -42.1738 | -121.2662 | 0.068665 | 0.07782 | -121.2936 | -121.463 | 0.018311 | 0.11902 | -0.004578 | 2.7512 | 0.27924 | 0.16022 | -0.26093 | -0.009155 | -0.17853 | -0.086975 | 1.3824 | 0.018311 | 0.19684 | -0.07782 | 121.4355 | 121.1792 | 71.0037 | -121.3211 | 121.3531 | 121.3623 | 79.1107 | -121.6187
2060.375 | 121.5042 | -121.2341 | 0.10986 | -0.0086212 | 0.01095 | 0.072489 | 0.0076882 | 0.06407 | -0.0035504 | -0.0037982 | 0.0069425 | -0.0025762 | 0.062107 | 0.065728 | -0.011335 | -0.0068103 | -0.073242 | -118.4463 | -50.8026 | -120.9686 | 0.12817 | -121.2479 | -121.1929 | -119.7968 | -42.3111 | -121.1975 | 0.032043 | 0.073242 | -121.3165 | -121.4722 | -0.013733 | 0.041199 | 0.018311 | 2.7878 | 0.2655 | 0.2243 | -0.18311 | -0.082397 | -0.23804 | -0.07782 | 1.4374 | 0.036621 | 0.27466 | -0.036621 | 121.3623 | 121.1609 | 70.4315 | -121.3028 | 121.2662 | 121.3074 | 78.923 | -121.582
2062.0781 | 121.5134 | -121.2753 | 0.10986 | 0.014267 | 0.0075324 | 0.070353 | 0.0053384 | 0.066206 | 0.0054218 | -0.0020892 | -0.00068649 | 0.0027644 | 0.061466 | 0.068291 | -0.0040717 | -0.0076647 | -0.11444 | -118.5242 | -51.4069 | -121.0144 | 0.1831 | -121.312 | -121.2204 | -119.8105 | -43.0252 | -121.3394 | 0.082397 | 0.082397 | -121.3165 | -121.5088 | -0.036621 | 0.054932 | 0.073242 | 2.7512 | 0.26093 | 0.20599 | -0.2243 | -0.041198 | -0.23346 | -0.027466 | 1.4648 | -0.064087 | 0.16937 | -0.027466 | 121.4584 | 121.1609 | 69.8685 | -121.3303 | 121.3577 | 121.3577 | 78.2501 | -121.6187
2063.7812 | 121.5088 | -121.2799 | 0.10529 | -0.00099167 | 0.0075324 | 0.072062 | 0.0076882 | 0.064711 | 0.0017902 | -0.001662 | 0.0069425 | 0.0010554 | 0.061679 | 0.066582 | -0.0066351 | -0.0074511 | -0.16479 | -118.5608 | -51.5167 | -121.019 | 0.1831 | -121.3577 | -121.2616 | -119.7739 | -43.4738 | -121.376 | 0.086975 | 0.11444 | -121.3348 | -121.4996 | -0.07782 | 0.01831 | 0.077819 | 2.7191 | 0.26093 | 0.24262 | -0.27008 | -0.054932 | -0.21973 | -0.018311 | 1.506 | -0.096131 | 0.1236 | 0.009155 | 121.463 | 121.1151 | 69.7632 | -121.3669 | 121.3669 | 121.3943 | 77.8061 | -121.6049
2065.5156 | 121.4813 | -121.2891 | 0.12817 | -0.00099167 | 0.0088142 | 0.072275 | 0.0074746 | 0.063215 | -0.0014142 | -0.003371 | -0.00068649 | -0.0032172 | 0.064457 | 0.068291 | -0.0087713 | -0.0063831 | -0.17395 | -118.4784 | -51.7914 | -121.0602 | 0.16022 | -121.3211 | -121.2433 | -119.8196 | -43.6203 | -121.3806 | 0.091553 | 0.12817 | -121.3852 | -121.5454 | -0.032044 | 0.045776 | 0.032043 | 2.8107 | 0.22888 | 0.1831 | -0.30212 | -0.096131 | -0.25635 | -0.036621 | 1.4694 | -0.091553 | 0.16479 | 0 | 121.4493 | 121.1151 | 69.4977 | -121.3715 | 121.3806 | 121.4172 | 77.6688 | -121.6736
2067.2031 | 121.3943 | -121.2891 | 0.13733 | 0.0066373 | 0.012232 | 0.075052 | 0.0068338 | 0.064283 | -0.0031232 | -0.003371 | 0.0069425 | -0.0047124 | 0.063175 | 0.064446 | -0.0083441 | -0.0063831 | -0.13275 | -118.3594 | -51.5854 | -121.0052 | 0.14191 | -121.312 | -121.1884 | -119.6915 | -43.8034 | -121.3028 | 0.050354 | 0.09613 | -121.344 | -121.5225 | -0.022889 | 0.10071 | 0.004578 | 2.9297 | 0.28381 | 0.1831 | -0.27008 | -0.054932 | -0.23346 | -0.086975 | 1.5976 | -0.013733 | 0.21973 | -0.041199 | 121.431 | 121.1563 | 69.7037 | -121.3257 | 121.3394 | 121.3852 | 77.4857 | -121.6599
2068.9062 | 121.4493 | -121.3028 | 0.14191 | -0.0086212 | 0.014368 | 0.077402 | 0.0074746 | 0.062788 | -0.0022686 | -0.0025164 | -0.00068649 | -0.0040716 | 0.061466 | 0.066155 | -0.0074897 | -0.0048877 | -0.16937 | -118.309 | -51.297 | -121.0281 | 0.15106 | -121.3028 | -121.2296 | -119.6457 | -43.9957 | -121.3074 | 0.050354 | 0.082397 | -121.3852 | -121.5317 | 0 | 0.073242 | 0.009155 | 2.9938 | 0.27466 | 0.20142 | -0.31128 | -0.082398 | -0.22888 | -0.091553 | 1.6571 | -0.004578 | 0.2243 | -0.05951 | 121.4539 | 121.1334 | 70.0058 | -121.3715 | 121.3531 | 121.3852 | 77.3071 | -121.6736
2070.6094 | 121.4172 | -121.3165 | 0.16022 | 0.0066373 | 0.0083868 | 0.072489 | 0.0057656 | 0.066633 | 0.004781 | -0.0012346 | 0.0069425 | 0.002337 | 0.061252 | 0.06765 | -0.0034307 | -0.0057421 | -0.10071 | -118.2953 | -51.5167 | -121.0281 | 0.16937 | -121.344 | -121.2387 | -119.6457 | -44.5816 | -121.3989 | 0.086975 | 0.10071 | -121.376 | -121.5454 | -0.027466 | 0.07782 | 0.009156 | 3.0212 | 0.28839 | 0.21057 | -0.26093 | -0.05951 | -0.22888 | -0.073242 | 1.6708 | -0.082398 | 0.14648 | -0.059509 | 121.4859 | 121.2158 | 69.7998 | -121.3989 | 121.4035 | 121.4172 | 76.7349 | -121.7056
2072.2969 | 121.463 | -121.3074 | 0.12817 | 0.0066373 | 0.015223 | 0.075479 | 0.0076882 | 0.064711 | -0.0029094 | -0.0018756 | -0.00068649 | -0.0044988 | 0.062961 | 0.064873 | -0.0091985 | -0.0061695 | -0.17395 | -118.19 | -51.4755 | -121.0236 | 0.16022 | -121.3486 | -121.2433 | -119.6136 | -44.4946 | -121.3074 | 0.050354 | 0.086975 | -121.3806 | -121.5454 | -0.041199 | 0.064087 | 0.032043 | 3.1174 | 0.28381 | 0.21973 | -0.30212 | -0.073242 | -0.23804 | -0.07782 | 1.6937 | 0 | 0.23804 | -0.041199 | 121.4676 | 121.1334 | 69.8318 | -121.3715 | 121.3577 | 121.3943 | 76.8127 | -121.6736
2074 | 121.4813 | -121.3303 | 0.14191 | -0.00099167 | 0.011591 | 0.071848 | 0.0051248 | 0.061506 | 0.0020038 | -0.0018756 | 0.0069425 | -0.0012946 | 0.060611 | 0.065728 | -0.0055671 | -0.0074511 | -0.13733 | -118.1259 | -51.8188 | -121.0327 | 0.15106 | -121.344 | -121.2433 | -119.4443 | -44.9066 | -121.3348 | 0.050354 | 0.082397 | -121.3989 | -121.5225 | -0.013733 | 0.086975 | 0.009155 | 3.2043 | 0.29755 | 0.21057 | -0.27924 | -0.068665 | -0.19226 | -0.091553 | 1.886 | -0.004578 | 0.18768 | -0.05951 | 121.4813 | 121.1929 | 69.5114 | -121.3852 | 121.3806 | 121.4127 | 76.4236 | -121.6644
2075.6875 | 121.5271 | -121.3028 | 0.10986 | -0.00099167 | 0.011164 | 0.072275 | 0.00897 | 0.062361 | -0.0029094 | -0.0035846 | 0.022202 | -0.0030034 | 0.063175 | 0.066368 | -0.01048 | -0.0061695 | -0.091553 | -117.9474 | -51.9928 | -120.9686 | 0.13733 | -121.3303 | -121.2433 | -119.4214 | -45.1401 | -121.2708 | 0.045776 | 0.073242 | -121.3715 | -121.5454 | -0.027466 | 0.059509 | 0.027466 | 3.3554 | 0.33417 | 0.27466 | -0.20142 | -0.068665 | -0.24262 | -0.064087 | 1.8814 | 0.032043 | 0.27466 | -0.036621 | 121.4401 | 121.2112 | 69.31 | -121.3531 | 121.3486 | 121.376 | 76.1627 | -121.6553
2077.375 | 121.4401 | -121.3577 | 0.13733 | -0.00099167 | 0.0066778 | 0.070993 | 0.0017068 | 0.065565 | 0.0045674 | -0.0025164 | -0.008316 | 0.001269 | 0.060611 | 0.06765 | -0.0051397 | -0.0053149 | -0.13275 | -118.0115 | -52.1988 | -121.0419 | 0.19226 | -121.376 | -121.2891 | -119.4351 | -45.6253 | -121.4584 | 0.091553 | 0.10986 | -121.4035 | -121.5866 | -0.018311 | 0.068665 | 0.054932 | 3.3463 | 0.31586 | 0.24719 | -0.27008 | -0.045776 | -0.22888 | -0.045776 | 1.9226 | -0.10071 | 0.12817 | -0.027466 | 121.55 | 121.225 | 69.1589 | -121.4264 | 121.4493 | 121.4676 | 75.7324 | -121.7239
2079.0625 | 121.5408 | -121.3348 | 0.10986 | -0.0086212 | 0.0088142 | 0.072062 | 0.0083292 | 0.065992 | -0.00034604 | -0.0012346 | 0.0069425 | -0.0019354 | 0.064884 | 0.068718 | -0.0094123 | -0.0055285 | -0.1831 | -117.8879 | -52.3224 | -121.0831 | 0.18768 | -121.3806 | -121.2936 | -119.4077 | -45.4788 | -121.431 | 0.10529 | 0.10529 | -121.431 | -121.6003 | -0.045776 | 0.041199 | 0.07782 | 3.447 | 0.25177 | 0.21057 | -0.29297 | -0.09613 | -0.2655 | -0.004577 | 1.9272 | -0.09613 | 0.16937 | -0.004577 | 121.5225 | 121.1517 | 69.0125 | -121.4035 | 121.4401 | 121.4401 | 75.856 | -121.7102
2080.7656 | 121.4539 | -121.3531 | 0.15106 | 0.0066373 | 0.012446 | 0.071848 | 0.0046976 | 0.064283 | 0.0011494 | -0.00080744 | 0.0069425 | -0.0025762 | 0.061893 | 0.066582 | -0.0074897 | -0.0048877 | -0.082397 | -117.7185 | -52.8168 | -121.0052 | 0.13733 | -121.3486 | -121.2524 | -119.2245 | -46.2662 | -121.3165 | 0.041199 | 0.073242 | -121.3943 | -121.5454 | 0.004577 | 0.10071 | -0.013733 | 3.6346 | 0.3479 | 0.24719 | -0.23346 | -0.041199 | -0.19226 | -0.10986 | 2.1286 | 0.036621 | 0.22888 | -0.07782 | 121.4905 | 121.2708 | 68.5364 | -121.4035 | 121.3943 | 121.4264 | 75.087 | -121.6965
2082.5156 | 121.4493 | -121.3852 | 0.14648 | -0.00099167 | 0.015223 | 0.071207 | 0.005552 | 0.064924 | -0.0012006 | -0.0012346 | -0.00068649 | -0.0047124 | 0.062107 | 0.066368 | -0.0077033 | -0.0055285 | -0.091553 | -117.6819 | -53.1784 | -121.0327 | 0.12817 | -121.3394 | -121.257 | -119.1376 | -46.6049 | -121.3623 | 0.045776 | 0.086975 | -121.4035 | -121.5454 | 0.045776 | 0.12817 | -0.01831 | 3.7033 | 0.35248 | 0.2243 | -0.23804 | -0.01831 | -0.16022 | -0.10071 | 2.2476 | 0.022888 | 0.1831 | -0.059509 | 121.5134 | 121.2936 | 68.2068 | -121.4035 | 121.431 | 121.4722 | 74.7803 | -121.6919
2084.2031 | 121.6232 | -121.3348 | 0.11444 | 0.0066373 | 0.010737 | 0.069284 | 0.0059792 | 0.06706 | 0.0037128 | -0.00038024 | 0.0069425 | 0.00020076 | 0.063175 | 0.069145 | -0.0044989 | -0.0078783 | -0.14191 | -117.659 | -53.5446 | -121.0464 | 0.19684 | -121.3898 | -121.3074 | -119.1193 | -46.106 | -121.4127 | 0.082397 | 0.10986 | -121.4264 | -121.6049 | -0.054932 | 0.027466 | 0.082397 | 3.6758 | 0.28839 | 0.26093 | -0.25635 | -0.091553 | -0.27008 | -0.032044 | 2.2156 | -0.07782 | 0.19226 | -0.004578 | 121.5317 | 121.1929 | 67.7902 | -121.4218 | 121.4172 | 121.4447 | 75.2289 | -121.7194
2085.9062 | 121.6049 | -121.3348 | 0.1236 | -0.00099167 | 0.012018 | 0.073343 | 0.0064066 | 0.064283 | 0.00072196 | -0.001662 | 0.0069425 | 0.00041436 | 0.062534 | 0.069573 | -0.0064215 | -0.0053149 | -0.19684 | -117.5629 | -53.3386 | -121.0876 | 0.1831 | -121.3898 | -121.3303 | -119.0781 | -46.875 | -121.4539 | 0.10071 | 0.1236 | -121.4539 | -121.6003 | -0.054932 | 0.004578 | 0.059509 | 3.772 | 0.24719 | 0.24261 | -0.32043 | -0.11902 | -0.2655 | -0.022888 | 2.2568 | -0.11902 | 0.14648 | 0 | 121.5179 | 121.138 | 67.9962 | -121.4539 | 121.4355 | 121.4584 | 74.4598 | -121.7239
2087.5938 | 121.5454 | -121.3715 | 0.12817 | 0.0066373 | 0.0079596 | 0.068216 | 0.0076882 | 0.065565 | 0.0032856 | -0.001021 | 0.0069425 | 0.00084176 | 0.066379 | 0.069573 | -0.0068487 | -0.0051013 | -0.10986 | -117.4347 | -54.1489 | -121.0052 | 0.17853 | -121.3806 | -121.3257 | -118.9911 | -47.1085 | -121.431 | 0.082397 | 0.10986 | -121.4676 | -121.6141 | -0.009155 | 0.045776 | 0.050354 | 3.9368 | 0.36621 | 0.32043 | -0.23804 | -0.09613 | -0.24262 | -0.045777 | 2.3804 | -0.059509 | 0.18311 | -0.018311 | 121.55 | 121.2616 | 67.2226 | -121.4539 | 121.4539 | 121.4813 | 74.263 | -121.7422
2089.2812 | 121.4859 | -121.3806 | 0.15564 | 0.0066373 | 0.014368 | 0.073984 | 0.0044838 | 0.065565 | -0.00098684 | -0.001021 | -0.00068649 | -0.0040716 | 0.063816 | 0.065514 | -0.0074897 | -0.0051013 | -0.09613 | -117.3203 | -54.483 | -121.0098 | 0.1236 | -121.3623 | -121.2708 | -118.8309 | -47.0398 | -121.3211 | 0.041199 | 0.082397 | -121.4676 | -121.5866 | 0.01831 | 0.10986 | -0.032044 | 4.0604 | 0.37079 | 0.26093 | -0.25177 | -0.086975 | -0.20599 | -0.11444 | 2.5497 | 0.059509 | 0.2655 | -0.073243 | 121.5042 | 121.2845 | 66.8976 | -121.4264 | 121.4218 | 121.463 | 74.3408 | -121.7422
2090.9688 | 121.4813 | -121.4035 | 0.15564 | 0.0066373 | 0.01565 | 0.075266 | 0.0036294 | 0.064924 | -0.0029094 | -0.0012346 | 0.0069425 | -0.0025762 | 0.059757 | 0.065087 | -0.0064215 | -0.0061695 | -0.11444 | -117.2241 | -54.7028 | -121.0098 | 0.1236 | -121.376 | -121.2936 | -118.7759 | -46.4951 | -121.3486 | 0.050354 | 0.064087 | -121.4355 | -121.6003 | 0.027465 | 0.10986 | -0.032044 | 4.1794 | 0.39368 | 0.28381 | -0.27008 | -0.032044 | -0.19684 | -0.10529 | 2.6276 | 0.054931 | 0.25177 | -0.091553 | 121.5271 | 121.2891 | 66.7007 | -121.4493 | 121.4539 | 121.4676 | 74.9084 | -121.756
2092.6562 | 121.6278 | -121.3577 | 0.10071 | 0.0066373 | 0.0079596 | 0.073984 | 0.003843 | 0.06642 | 0.0043536 | -0.003371 | 0.0069425 | 0.0025508 | 0.05933 | 0.069786 | -0.0034307 | -0.0061695 | -0.14191 | -117.1783 | -54.5883 | -121.051 | 0.19226 | -121.4081 | -121.3257 | -118.7164 | -46.8567 | -121.4355 | 0.07782 | 0.1236 | -121.4767 | -121.6232 | -0.050354 | 0.032043 | 0.091553 | 4.1794 | 0.3067 | 0.27466 | -0.24262 | -0.11902 | -0.2655 | -0.022888 | 2.6413 | -0.07782 | 0.18768 | 0.022888 | 121.55 | 121.2158 | 66.7694 | -121.4264 | 121.4355 | 121.4813 | 74.501 | -121.7239
2094.3438 | 121.5088 | -121.4081 | 0.12817 | 0.0066373 | 0.014582 | 0.075266 | 0.0079018 | 0.065992 | -0.0048322 | -0.0037982 | 0.0069425 | -0.0053534 | 0.063388 | 0.066155 | -0.011121 | -0.0033923 | -0.15106 | -117.0135 | -54.4235 | -121.0556 | 0.15106 | -121.3806 | -121.3211 | -118.6432 | -47.4518 | -121.3852 | 0.073242 | 0.086975 | -121.4767 | -121.6095 | 0.027466 | 0.086975 | 0.022888 | 4.3945 | 0.35248 | 0.2655 | -0.27924 | -0.068665 | -0.20142 | -0.054932 | 2.7649 | 0.022888 | 0.2243 | -0.041199 | 121.5591 | 121.257 | 66.9846 | -121.4493 | 121.4813 | 121.4951 | 73.9563 | -121.7377
2096.0312 | 121.5088 | -121.4264 | 0.14191 | 0.0066373 | 0.012018 | 0.070353 | 0.0053384 | 0.064497 | 0.0054218 | 4.696e-05 | 0.014572 | 0.0014826 | 0.062748 | 0.070427 | -0.0055671 | -0.0085193 | -0.18768 | -117.0593 | -55.4077 | -121.1014 | 0.20599 | -121.431 | -121.344 | -118.5699 | -48.024 | -121.5134 | 0.082397 | 0.10986 | -121.4859 | -121.6324 | -0.004577 | 0.082398 | 0.064087 | 4.3671 | 0.32501 | 0.24262 | -0.32959 | -0.059509 | -0.20599 | -0.05951 | 2.8564 | -0.086975 | 0.11902 | -0.032044 | 121.6324 | 121.2387 | 66.0187 | -121.4859 | 121.5088 | 121.5363 | 73.4024 | -121.7743
2097.7188 | 121.6324 | -121.3989 | 0.11444 | 0.0066373 | 0.011805 | 0.075266 | 0.0081154 | 0.065992 | -0.0029094 | -0.0031574 | -0.00068649 | -0.0040716 | 0.062534 | 0.067009 | -0.010053 | -0.0074511 | -0.10071 | -116.684 | -54.8721 | -121.0007 | 0.14648 | -121.3898 | -121.3303 | -118.3456 | -47.5021 | -121.3348 | 0.036621 | 0.073242 | -121.463 | -121.6003 | 0.009155 | 0.068665 | 0.032043 | 4.715 | 0.39826 | 0.32959 | -0.21515 | -0.064087 | -0.20142 | -0.07782 | 3.0533 | 0.064087 | 0.2655 | -0.041199 | 121.5454 | 121.2982 | 66.5268 | -121.4447 | 121.4355 | 121.4722 | 73.8968 | -121.7148
2099.4531 | 121.5637 | -121.4035 | 0.12817 | 0.0066373 | 0.013087 | 0.075907 | 0.0057656 | 0.066633 | -0.0026958 | -0.0040118 | -0.00068649 | -0.0047124 | 0.063175 | 0.067223 | -0.0077033 | -0.0046741 | -0.15106 | -116.7755 | -55.8792 | -121.0556 | 0.17395 | -121.3989 | -121.3394 | -118.2907 | -47.4884 | -121.3989 | 0.068665 | 0.082397 | -121.463 | -121.6187 | 0.004577 | 0.064086 | 0.045776 | 4.628 | 0.3479 | 0.28381 | -0.27924 | -0.05951 | -0.21515 | -0.059509 | 3.1128 | 0.004577 | 0.21973 | -0.045777 | 121.5775 | 121.2524 | 65.5243 | -121.4676 | 121.4722 | 121.4859 | 73.9151 | -121.7468
2101.1406 | 121.6553 | -121.3989 | 0.11902 | -0.0086212 | 0.0081732 | 0.07313 | 0.002775 | 0.066633 | 0.004781 | -0.0018756 | -0.00068649 | 0.00062796 | 0.061679 | 0.067009 | -0.0034307 | -0.0080921 | -0.10986 | -116.8488 | -57.6187 | -121.0464 | 0.18768 | -121.4493 | -121.3348 | -118.19 | -47.6349 | -121.4676 | 0.082397 | 0.10071 | -121.5088 | -121.637 | -0.050354 | 0.064087 | 0.068664 | 4.5502 | 0.35248 | 0.28839 | -0.22888 | -0.10986 | -0.23804 | -0.036622 | 3.2089 | -0.068664 | 0.16937 | -0.018311 | 121.5866 | 121.2891 | 63.7802 | -121.4539 | 121.4813 | 121.4996 | 73.764 | -121.756
2102.8281 | 121.6461 | -121.3806 | 0.11902 | 0.014267 | 0.0068916 | 0.072062 | 0.0087564 | 0.06706 | 0.0028584 | -0.0018756 | 0.0069425 | 0.00084176 | 0.067234 | 0.067009 | -0.0083441 | -0.0068103 | -0.17853 | -116.8259 | -57.312 | -121.0739 | 0.17853 | -121.4813 | -121.3669 | -118.1625 | -47.5891 | -121.4767 | 0.091553 | 0.13275 | -121.5271 | -121.6736 | -0.10071 | 0.013733 | 0.059509 | 4.5547 | 0.3067 | 0.29297 | -0.29755 | -0.14648 | -0.29297 | -0.027466 | 3.2181 | -0.096131 | 0.19684 | 0.013732 | 121.5591 | 121.2021 | 64.0686 | -121.4859 | 121.4722 | 121.5134 | 73.7915 | -121.7926
2104.5469 | 121.5591 | -121.4264 | 0.14648 | -0.0086212 | 0.012018 | 0.070353 | 0.0042702 | 0.064924 | 0.005849 | -0.00016664 | 0.0069425 | -0.00065364 | 0.063816 | 0.069786 | -0.0057807 | -0.0076647 | -0.16479 | -116.6702 | -57.0786 | -121.0876 | 0.17853 | -121.4401 | -121.3806 | -117.9794 | -48.1293 | -121.5179 | 0.07782 | 0.09613 | -121.5225 | -121.6873 | -0.013733 | 0.045777 | 0.032044 | 4.7562 | 0.33875 | 0.29297 | -0.31128 | -0.09613 | -0.26092 | -0.068664 | 3.447 | -0.091552 | 0.16937 | -0.050354 | 121.6049 | 121.2616 | 64.3478 | -121.5271 | 121.5042 | 121.5225 | 73.2971 | -121.8338
2106.2344 | 121.6644 | -121.376 | 0.11444 | 0.0066373 | 0.013941 | 0.076334 | 0.0087564 | 0.06407 | -0.0056866 | -0.001021 | 0.0069425 | -0.0064214 | 0.062534 | 0.06765 | -0.0085577 | -0.0029651 | -0.1236 | -116.4185 | -57.1106 | -120.9595 | 0.14191 | -121.4264 | -121.3165 | -117.8146 | -48.1522 | -121.3623 | 0.050354 | 0.086975 | -121.4951 | -121.6644 | -0.050354 | 0.05951 | 0.027466 | 4.9576 | 0.41656 | 0.35706 | -0.23804 | -0.11902 | -0.28839 | -0.064087 | 3.5614 | 0.013733 | 0.30212 | -0.027466 | 121.5179 | 121.2524 | 64.2654 | -121.431 | 121.4264 | 121.463 | 73.2239 | -121.7789
2107.9375 | 121.6141 | -121.4081 | 0.11444 | -0.00099167 | 0.010096 | 0.074625 | 0.00897 | 0.06642 | -0.00098684 | -0.0018756 | 0.014572 | -0.0044988 | 0.062748 | 0.066155 | -0.0089849 | -0.0065967 | -0.11444 | -116.2491 | -56.8726 | -121.0052 | 0.15106 | -121.4447 | -121.3577 | -117.6544 | -48.1888 | -121.4355 | 0.064087 | 0.09613 | -121.5179 | -121.6599 | -0.036621 | 0.050354 | 0.036621 | 5.159 | 0.40283 | 0.35248 | -0.22888 | -0.10986 | -0.25177 | -0.050354 | 3.7537 | -0.027466 | 0.2243 | -0.018311 | 121.5591 | 121.2936 | 64.5355 | -121.4722 | 121.4722 | 121.5042 | 73.2193 | -121.7743
2109.6562 | 121.5454 | -121.4539 | 0.12817 | -0.0086212 | 0.015009 | 0.07612 | 0.0074746 | 0.064283 | -0.0018414 | -0.0014484 | -0.00068649 | -0.0047124 | 0.061466 | 0.069573 | -0.0081305 | -0.0046741 | -0.13733 | -116.1072 | -56.6437 | -121.0236 | 0.16479 | -121.431 | -121.3531 | -117.5537 | -47.7768 | -121.3898 | 0.054932 | 0.091553 | -121.4996 | -121.6782 | 0.022888 | 0.10071 | 0.036621 | 5.3467 | 0.4303 | 0.32959 | -0.2655 | -0.045777 | -0.22431 | -0.073242 | 3.9001 | 0.064086 | 0.28839 | -0.036621 | 121.6187 | 121.3165 | 64.8102 | -121.4813 | 121.5088 | 121.5454 | 73.6771 | -121.8063
2111.375 | 121.5958 | -121.4401 | 0.16479 | -0.0086212 | 0.013087 | 0.073771 | 0.002134 | 0.066206 | 0.00414 | -0.00080744 | 0.014572 | 0.0025508 | 0.060611 | 0.067864 | -0.0032171 | -0.0070239 | -0.16937 | -116.0934 | -57.4997 | -121.0739 | 0.19226 | -121.4676 | -121.3989 | -117.3889 | -48.4726 | -121.5363 | 0.091553 | 0.1236 | -121.5317 | -121.6827 | -0.027465 | 0.041199 | 0.027466 | 5.3467 | 0.36621 | 0.32501 | -0.33417 | -0.091552 | -0.24261 | -0.073242 | 4.0512 | -0.09613 | 0.14648 | -0.041199 | 121.6324 | 121.2708 | 63.9404 | -121.5637 | 121.5317 | 121.5637 | 72.9675 | -121.8475
2113.0938 | 121.5958 | -121.4539 | 0.14191 | -0.016251 | 0.011378 | 0.071848 | 0.0025612 | 0.063002 | 0.0032856 | 0.00047416 | -0.008316 | 0.0014826 | 0.062534 | 0.069573 | -0.0040717 | -0.0080921 | -0.17395 | -116.0248 | -57.3166 | -121.0648 | 0.17395 | -121.4447 | -121.3943 | -117.2928 | -48.4039 | -121.5317 | 0.11444 | 0.10071 | -121.5454 | -121.7148 | 0.009155 | 0.059509 | 0.032043 | 5.4291 | 0.3891 | 0.32959 | -0.31586 | -0.091553 | -0.26093 | -0.027466 | 4.1611 | -0.07782 | 0.18311 | -0.041199 | 121.6278 | 121.2799 | 64.1373 | -121.5363 | 121.5683 | 121.5546 | 73.0499 | -121.8567
2114.7969 | 121.5454 | -121.4722 | 0.15106 | 0.0066373 | 0.011805 | 0.07313 | 0.005552 | 0.06706 | 0.0045674 | 0.0019696 | 0.0069425 | 0.0014826 | 0.065952 | 0.068505 | -0.0023627 | -0.0053149 | -0.17395 | -115.7455 | -57.1747 | -121.0281 | 0.19226 | -121.4859 | -121.3806 | -117.1143 | -48.4406 | -121.5591 | 0.073242 | 0.13733 | -121.5225 | -121.7102 | -0.013733 | 0.091553 | 0.041199 | 5.7266 | 0.44403 | 0.35248 | -0.32501 | -0.050354 | -0.23804 | -0.07782 | 4.3579 | -0.086975 | 0.15106 | -0.013733 | 121.6644 | 121.2982 | 64.2975 | -121.5317 | 121.5454 | 121.6095 | 73.0316 | -121.8613
2116.5312 | 121.5912 | -121.4539 | 0.13733 | -0.00099167 | 0.012232 | 0.073984 | 0.005552 | 0.065138 | 0.00029476 | -0.00080744 | 0.014572 | 0.001269 | 0.062534 | 0.069573 | -0.0044989 | -0.0033923 | -0.16937 | -115.5716 | -57.5546 | -121.0648 | 0.16937 | -121.4905 | -121.4035 | -116.9678 | -48.9258 | -121.4859 | 0.082397 | 0.091553 | -121.5454 | -121.6827 | -0.036622 | 0.050354 | 0.032044 | 5.8823 | 0.3891 | 0.33875 | -0.3067 | -0.091553 | -0.22888 | -0.054932 | 4.4861 | -0.032044 | 0.19684 | -0.045776 | 121.6232 | 121.2845 | 63.8992 | -121.5408 | 121.5363 | 121.5454 | 72.5281 | -121.8201
2118.2188 | 121.6461 | -121.431 | 0.11444 | -0.0086212 | 0.0133 | 0.075479 | 0.010252 | 0.065779 | -0.0016278 | -0.0025164 | -0.00068649 | -0.0047124 | 0.064457 | 0.067223 | -0.0096259 | -0.0036059 | -0.1236 | -115.4114 | -57.3349 | -120.9641 | 0.13733 | -121.4859 | -121.3486 | -116.7618 | -48.7473 | -121.4355 | 0.054932 | 0.10071 | -121.5408 | -121.6965 | -0.054932 | 0.082397 | 0.022888 | 6.0196 | 0.46692 | 0.38452 | -0.23804 | -0.10986 | -0.2655 | -0.059509 | 4.6692 | -0.004578 | 0.26093 | -0.013733 | 121.5683 | 121.3074 | 64.0961 | -121.463 | 121.4859 | 121.5317 | 72.6837 | -121.8109
2119.9219 | 121.5683 | -121.4813 | 0.14648 | -0.00099167 | 0.0090278 | 0.073343 | 0.0036294 | 0.067915 | 0.0060626 | -0.00059384 | 0.0069425 | 0.0025508 | 0.065525 | 0.071068 | -0.0040717 | -0.0044605 | -0.13275 | -115.3427 | -57.3944 | -121.0236 | 0.18768 | -121.4584 | -121.3852 | -116.5375 | -48.8342 | -121.5363 | 0.086975 | 0.10071 | -121.5683 | -121.6919 | 0.022888 | 0.09613 | 0.041199 | 6.1386 | 0.45776 | 0.36163 | -0.27924 | -0.086975 | -0.21057 | -0.059509 | 4.9438 | -0.054932 | 0.15564 | -0.045776 | 121.669 | 121.3486 | 64.0869 | -121.5317 | 121.5683 | 121.582 | 72.6471 | -121.8384
2121.6094 | 121.6782 | -121.463 | 0.10529 | 0.0066373 | 0.014155 | 0.081034 | 0.0076882 | 0.06706 | -0.0061138 | -0.001021 | -0.008316 | -0.005567 | 0.061679 | 0.068077 | -0.0074897 | -0.0036059 | -0.11444 | -115.0452 | -57.193 | -120.9457 | 0.14648 | -121.4905 | -121.3715 | -116.2216 | -48.3353 | -121.3806 | 0.045776 | 0.082397 | -121.5317 | -121.6736 | -0.027466 | 0.091553 | 0.041198 | 6.4178 | 0.51727 | 0.42572 | -0.21973 | -0.068664 | -0.21057 | -0.05951 | 5.2414 | 0.082398 | 0.29297 | -0.022889 | 121.6095 | 121.3486 | 64.27 | -121.4767 | 121.5088 | 121.5454 | 73.1277 | -121.7789
2123.2812 | 121.582 | -121.463 | 0.16479 | 0.014267 | 0.012659 | 0.073343 | 0.0029886 | 0.06642 | 0.00414 | -0.0018756 | -0.00068649 | -0.00086724 | 0.063175 | 0.070854 | -0.0053533 | -0.0046741 | -0.18768 | -115.0635 | -57.1335 | -121.0327 | 0.19226 | -121.4996 | -121.431 | -116.1438 | -48.8846 | -121.5363 | 0.10071 | 0.11902 | -121.5546 | -121.7285 | -0.036621 | 0.032044 | 0.027466 | 6.3995 | 0.4303 | 0.39825 | -0.35248 | -0.091552 | -0.2655 | -0.064087 | 5.3192 | -0.073242 | 0.19226 | -0.045776 | 121.6553 | 121.2753 | 64.3295 | -121.5958 | 121.5637 | 121.582 | 72.5784 | -121.8933
2124.9844 | 121.7056 | -121.431 | 0.11902 | -0.00099167 | 0.010309 | 0.076548 | 0.0079018 | 0.068129 | 0.0015766 | -0.00038024 | -0.015945 | -1.2844e-05 | 0.067874 | 0.070641 | -0.0064215 | -0.0051013 | -0.19226 | -114.8346 | -56.6666 | -121.0098 | 0.18768 | -121.5134 | -121.4493 | -115.8966 | -47.9736 | -121.5317 | 0.10529 | 0.13275 | -121.5729 | -121.7239 | -0.082398 | -0.018311 | 0.068664 | 6.5964 | 0.42114 | 0.43945 | -0.31128 | -0.14191 | -0.29297 | -0.013733 | 5.5344 | -0.10071 | 0.19226 | 0.013732 | 121.6187 | 121.2387 | 64.7644 | -121.5683 | 121.5363 | 121.5637 | 73.4573 | -121.843
2126.7188 | 121.6507 | -121.4722 | 0.12817 | -0.00099167 | 0.0066778 | 0.074411 | 0.0040566 | 0.066847 | 0.0026446 | -0.001021 | -0.00068649 | 0.0014826 | 0.063175 | 0.071282 | -0.0044989 | -0.0048877 | -0.11902 | -114.6103 | -56.7856 | -120.9595 | 0.16937 | -121.5179 | -121.4127 | -115.5487 | -47.9736 | -121.4951 | 0.064087 | 0.09613 | -121.5271 | -121.7056 | -0.045776 | 0.059509 | 0.041199 | 6.8619 | 0.51269 | 0.45319 | -0.24719 | -0.054932 | -0.23346 | -0.064087 | 5.9235 | -0.022888 | 0.21057 | -0.032044 | 121.6415 | 121.3531 | 64.6866 | -121.5408 | 121.5363 | 121.5683 | 73.4985 | -121.8338
2128.4688 | 121.5591 | -121.4767 | 0.14648 | 0.0066373 | 0.018854 | 0.076761 | 0.0059792 | 0.067488 | -0.0026958 | -0.0023028 | -0.00068649 | -0.0025762 | 0.066593 | 0.071068 | -0.0070623 | -0.0014697 | -0.11444 | -114.3265 | -56.1035 | -120.9412 | 0.15106 | -121.4813 | -121.376 | -115.155 | -47.9507 | -121.4493 | 0.064087 | 0.091553 | -121.5408 | -121.7194 | -0.004577 | 0.10071 | 0.004578 | 7.1503 | 0.53558 | 0.43488 | -0.26093 | -0.064087 | -0.24261 | -0.082397 | 6.3217 | 0.027466 | 0.27008 | -0.054931 | 121.6278 | 121.3623 | 65.3732 | -121.5225 | 121.5408 | 121.5683 | 73.526 | -121.8658
2130.1719 | 121.6095 | -121.4996 | 0.13275 | -0.00099167 | 0.018427 | 0.079325 | 0.0051248 | 0.065351 | -0.0026958 | -0.0020892 | 0.0069425 | -0.002149 | 0.063816 | 0.069145 | -0.0091985 | -0.0031787 | -0.13275 | -114.0747 | -56.4514 | -120.9549 | 0.13733 | -121.4676 | -121.3715 | -114.9994 | -47.8317 | -121.4401 | 0.054932 | 0.09613 | -121.5454 | -121.7056 | 0.032044 | 0.12817 | 0.004578 | 7.4249 | 0.54474 | 0.41657 | -0.2655 | -0.045776 | -0.20599 | -0.077819 | 6.5002 | 0.059509 | 0.2655 | -0.036621 | 121.637 | 121.3669 | 65.0482 | -121.5042 | 121.5546 | 121.5958 | 73.6679 | -121.8384
2131.875 | 121.7194 | -121.4584 | 0.10986 | 0.0066373 | 0.014368 | 0.078897 | 0.0061928 | 0.068556 | 8.1158e-05 | -0.001021 | 0.014572 | -0.0036444 | 0.06232 | 0.068932 | -0.0079169 | -0.0053149 | -0.082397 | -113.8092 | -56.4743 | -120.8954 | 0.16022 | -121.4813 | -121.3943 | -114.6652 | -47.7585 | -121.3715 | 0.059509 | 0.064087 | -121.5363 | -121.6782 | -0.022888 | 0.064087 | 0.050354 | 7.6492 | 0.56305 | 0.49896 | -0.19226 | -0.07782 | -0.21973 | -0.050354 | 6.7932 | 0.086975 | 0.3067 | -0.045776 | 121.6187 | 121.376 | 64.9841 | -121.5042 | 121.5179 | 121.5225 | 73.7 | -121.788
2133.5938 | 121.7331 | -121.4493 | 0.11444 | -0.00099167 | 0.014796 | 0.075693 | 0.0083292 | 0.066633 | -0.0012006 | -0.0035846 | -0.008316 | -0.0040716 | 0.064029 | 0.068932 | -0.0074897 | -0.0063831 | -0.07782 | -113.5391 | -56.1218 | -120.845 | 0.15106 | -121.4859 | -121.3989 | -114.4272 | -47.7951 | -121.3806 | 0.041199 | 0.059509 | -121.5683 | -121.7056 | -0.036621 | 0.050354 | 0.036621 | 7.9102 | 0.60425 | 0.55389 | -0.19226 | -0.11902 | -0.25635 | -0.073242 | 7.0221 | 0.068665 | 0.32501 | -0.054932 | 121.6003 | 121.3715 | 65.3275 | -121.5134 | 121.4905 | 121.5088 | 73.6542 | -121.8201
2135.3125 | 121.6827 | -121.4722 | 0.10986 | -0.016251 | 0.016505 | 0.076975 | 0.00897 | 0.070906 | 0.0011494 | -0.0018756 | 0.0069425 | -0.0012946 | 0.063602 | 0.071282 | -0.0074897 | -0.0046741 | -0.059509 | -113.269 | -56.0257 | -120.8633 | 0.14191 | -121.4676 | -121.4035 | -114.061 | -47.3007 | -121.4035 | 0.064087 | 0.073242 | -121.5271 | -121.7148 | 0.004578 | 0.068665 | 0.032044 | 8.2031 | 0.60883 | 0.54016 | -0.16937 | -0.054932 | -0.24262 | -0.045776 | 7.4112 | 0.068665 | 0.31128 | -0.036621 | 121.6141 | 121.4127 | 65.4465 | -121.5134 | 121.5363 | 121.5454 | 74.1714 | -121.8246
2137 | 121.6415 | -121.4951 | 0.1236 | -0.00099167 | 0.012018 | 0.078684 | 0.0040566 | 0.067488 | 0.001363 | 0.00068796 | 0.0069425 | -0.0027898 | 0.06702 | 0.070854 | -0.0044989 | -0.0053149 | -0.14191 | -113.0585 | -55.7007 | -120.8862 | 0.15106 | -121.5088 | -121.4127 | -113.7451 | -46.9986 | -121.4218 | 0.050354 | 0.086975 | -121.5683 | -121.7194 | -0.013733 | 0.082397 | 0.027466 | 8.4366 | 0.60883 | 0.52643 | -0.2655 | -0.073242 | -0.2243 | -0.073242 | 7.7499 | 0.073242 | 0.29755 | -0.036621 | 121.6461 | 121.3531 | 65.7944 | -121.5363 | 121.5454 | 121.582 | 74.4965 | -121.843
2138.6875 | 121.7056 | -121.4493 | 0.11902 | -0.00099167 | 0.016718 | 0.075693 | 0.002775 | 0.067701 | 0.0088398 | -0.001021 | -0.00068649 | 0.0025508 | 0.065952 | 0.070641 | -0.0019355 | -0.0059557 | -0.10529 | -112.825 | -55.3665 | -120.8542 | 0.17853 | -121.5271 | -121.4218 | -113.53 | -47.0032 | -121.4905 | 0.086975 | 0.11444 | -121.5729 | -121.7331 | -0.07782 | 0.027466 | 0.059509 | 8.6243 | 0.59509 | 0.56763 | -0.22431 | -0.1236 | -0.28381 | -0.032044 | 7.9193 | -0.041199 | 0.24261 | -0.004578 | 121.6278 | 121.344 | 66.0828 | -121.5408 | 121.5363 | 121.5637 | 74.4461 | -121.8521
2140.375 | 121.7422 | -121.4447 | 0.10986 | 0.0066373 | 0.01565 | 0.077188 | 0.0087564 | 0.070906 | -0.00077324 | -0.0018756 | -0.00068649 | -0.0027898 | 0.066593 | 0.070427 | -0.0074897 | -0.0053149 | -0.11902 | -112.3856 | -54.7073 | -120.813 | 0.15564 | -121.5179 | -121.4218 | -113.0447 | -47.0398 | -121.3806 | 0.059509 | 0.082397 | -121.5683 | -121.7148 | -0.073242 | 0.022888 | 0.045777 | 9.0591 | 0.63171 | 0.60883 | -0.22888 | -0.1236 | -0.27008 | -0.050354 | 8.4 | 0.064087 | 0.33417 | -0.027466 | 121.6003 | 121.3257 | 66.7374 | -121.5317 | 121.5042 | 121.5271 | 74.4049 | -121.8246
2142.0625 | 121.6278 | -121.5088 | 0.14191 | -0.00099167 | 0.020991 | 0.076334 | 0.0049112 | 0.068129 | 0.010549 | 4.696e-05 | 0.0069425 | 0.0034052 | 0.066166 | 0.075127 | -0.0042853 | -0.0036059 | -0.10071 | -112.0789 | -54.7256 | -120.8176 | 0.16022 | -121.5134 | -121.4447 | -112.7151 | -46.5134 | -121.5317 | 0.07782 | 0.11902 | -121.5866 | -121.756 | -0.004578 | 0.064087 | 0.01831 | 9.4299 | 0.69122 | 0.62714 | -0.24262 | -0.07782 | -0.24719 | -0.064087 | 8.7936 | -0.022888 | 0.2243 | -0.022888 | 121.669 | 121.4081 | 66.7831 | -121.5866 | 121.5866 | 121.6278 | 74.9954 | -121.8979
2143.75 | 121.6873 | -121.5042 | 0.13733 | -0.00099167 | 0.014796 | 0.075266 | 0.0076882 | 0.070051 | 0.0034992 | -0.001662 | 0.014572 | -0.00065364 | 0.066593 | 0.071068 | -0.0070623 | -0.0029651 | -0.14191 | -111.7538 | -54.8721 | -120.8267 | 0.16479 | -121.5408 | -121.4584 | -112.2391 | -46.3852 | -121.4905 | 0.082397 | 0.10071 | -121.6095 | -121.7239 | -0.036622 | 0.045776 | 0.027466 | 9.7504 | 0.67749 | 0.63171 | -0.27924 | -0.10529 | -0.21973 | -0.054932 | 9.2651 | 0.013732 | 0.23346 | -0.036621 | 121.669 | 121.3623 | 66.6321 | -121.5958 | 121.5866 | 121.6049 | 75.119 | -121.8613
2145.4844 | 121.7056 | -121.4767 | 0.14648 | -0.00099167 | 0.017786 | 0.076975 | 0.0036294 | 0.070478 | 0.00649 | 0.00047416 | -0.00068649 | 0.0036188 | 0.067874 | 0.073845 | -0.0032171 | -0.0033923 | -0.11444 | -111.4197 | -54.8035 | -120.7993 | 0.17853 | -121.5317 | -121.4447 | -111.9644 | -46.2433 | -121.4905 | 0.07782 | 0.09613 | -121.5912 | -121.7514 | -0.054931 | 0.032044 | 0.032044 | 10.0571 | 0.67749 | 0.64545 | -0.26093 | -0.11444 | -0.27466 | -0.068664 | 9.5123 | -0.013733 | 0.26093 | -0.050354 | 121.6553 | 121.3623 | 66.6733 | -121.5912 | 121.5546 | 121.5729 | 75.2335 | -121.8979
2147.1719 | 121.7148 | -121.4996 | 0.11902 | 0.0066373 | 0.019068 | 0.076548 | 0.0091836 | 0.068129 | 0.0032856 | 0.00047416 | 0.014572 | -0.00086724 | 0.068302 | 0.075341 | -0.0074897 | -0.0012561 | -0.21515 | -111.1359 | -54.6112 | -120.8679 | 0.20142 | -121.5683 | -121.4905 | -111.5112 | -45.9183 | -121.5134 | 0.09613 | 0.13733 | -121.6278 | -121.7514 | -0.068664 | 0.009155 | 0.082397 | 10.3638 | 0.63171 | 0.62256 | -0.33417 | -0.12817 | -0.25177 | -0.022889 | 9.9884 | -0.013733 | 0.23804 | 0.01831 | 121.701 | 121.2845 | 66.8884 | -121.6095 | 121.5958 | 121.637 | 75.5814 | -121.8704
2148.8594 | 121.6507 | -121.5271 | 0.1236 | -0.0086212 | 0.017359 | 0.077402 | 0.0059792 | 0.07176 | 0.00050836 | -0.001021 | 0.0069425 | -0.0023626 | 0.066379 | 0.073632 | -0.0070623 | -0.0021105 | -0.17853 | -110.8475 | -54.3823 | -120.7535 | 0.14648 | -121.4996 | -121.4355 | -111.2732 | -45.7672 | -121.431 | 0.045776 | 0.086975 | -121.5958 | -121.7468 | 0.027466 | 0.091553 | 0.022888 | 10.6796 | 0.77362 | 0.68207 | -0.30212 | -0.068664 | -0.21973 | -0.07782 | 10.2539 | 0.096131 | 0.31586 | -0.036621 | 121.6736 | 121.3486 | 67.1448 | -121.5591 | 121.5729 | 121.6141 | 75.7599 | -121.8704
2150.5625 | 121.6827 | -121.5088 | 0.15106 | 0.0066373 | 0.019068 | 0.075052 | 0.0049112 | 0.071119 | 0.0045674 | 0.0021832 | -0.00068649 | 0.0034052 | 0.064884 | 0.073204 | -0.0010809 | -0.0029651 | -0.19684 | -110.6506 | -54.3549 | -120.7718 | 0.19684 | -121.5454 | -121.463 | -110.6369 | -45.2316 | -121.5363 | 0.073242 | 0.11444 | -121.6141 | -121.7514 | -0.036621 | 0.045776 | 0.045776 | 10.8582 | 0.737 | 0.69122 | -0.3479 | -0.10529 | -0.24262 | -0.07782 | 10.8719 | -0.027466 | 0.21515 | -0.036621 | 121.7056 | 121.312 | 67.1539 | -121.6141 | 121.582 | 121.6232 | 76.2772 | -121.9025
2152.2344 | 121.7743 | -121.463 | 0.11902 | -0.00099167 | 0.020563 | 0.076334 | 0.010465 | 0.071119 | 0.0049946 | 0.0038922 | 0.0069425 | 0.004046 | 0.069583 | 0.073632 | -0.0044989 | -0.00061532 | -0.20142 | -110.2386 | -53.6316 | -120.7672 | 0.19226 | -121.5637 | -121.4905 | -110.3851 | -44.9066 | -121.4905 | 0.09613 | 0.10986 | -121.6049 | -121.7651 | -0.10071 | -0.027466 | 0.073242 | 11.2244 | 0.6958 | 0.72327 | -0.32044 | -0.14191 | -0.30212 | -0.022889 | 11.0779 | -0.027466 | 0.27466 | -0.009156 | 121.6553 | 121.2616 | 67.8314 | -121.6095 | 121.5591 | 121.5729 | 76.5564 | -121.8842
2153.9219 | 121.7468 | -121.4859 | 0.10529 | -0.00099167 | 0.018641 | 0.075052 | 0.0066202 | 0.069624 | -0.00098684 | 0.003465 | 0.0069425 | -0.0017218 | 0.068302 | 0.078331 | -0.0079169 | -0.0014697 | -0.10986 | -108.9203 | -51.3886 | -120.5704 | 0.16022 | -121.4951 | -121.3989 | -98.6664 | -44.4305 | -121.3394 | 0.059509 | 0.10071 | -121.5866 | -121.7468 | -0.009155 | 0.086975 | 0.054931 | 12.5656 | 0.91553 | 0.82855 | -0.21515 | -0.10071 | -0.26093 | -0.045777 | 22.8195 | 0.14648 | 0.40741 | -0.004578 | 121.6461 | 121.376 | 70.0974 | -121.5042 | 121.5454 | 121.5866 | 77.0554 | -121.8521
2155.6094 | 121.7331 | -121.4722 | 0.13275 | -0.00099167 | 0.014582 | 0.078684 | 0.0036294 | 0.071974 | 0.0015766 | 0.0021832 | -0.00068649 | 0.00041436 | 0.062534 | 0.12789 | -0.0017217 | -0.0010425 | -0.10071 | -108.1512 | -50.3357 | -120.5063 | 0.16479 | -121.5042 | -121.4172 | -7.6492 | -40.1962 | -121.2708 | 0.059509 | 0.11444 | -121.5637 | -121.701 | -0.032043 | 0.054932 | 0.032044 | 13.3209 | 0.96588 | 0.91095 | -0.23346 | -0.091553 | -0.22888 | -0.073242 | 113.8229 | 0.20142 | 0.4303 | -0.01831 | 121.637 | 121.3715 | 71.1365 | -121.55 | 121.5317 | 121.5866 | 81.2759 | -121.8338
2157.2969 | 121.6827 | -121.5179 | 0.15564 | 0.014267 | 0.02035 | 0.076761 | 0.0040566 | 0.075392 | 0.0081988 | 0.003465 | 0.014572 | 0.0044734 | 0.06232 | 0.13067 | 0.0012689 | -0.0021105 | -0.11444 | -107.8079 | -50.5783 | -120.5658 | 0.18768 | -121.5271 | -121.4539 | -7.4799 | -40.1093 | -121.3989 | 0.09613 | 0.11444 | -121.5591 | -121.7514 | -0.009156 | 0.064087 | 0.032043 | 13.71 | 0.95215 | 0.88806 | -0.27008 | -0.041199 | -0.23346 | -0.05951 | 114.0381 | 0.11902 | 0.35248 | -0.041199 | 121.7056 | 121.4035 | 70.9396 | -121.6095 | 121.6141 | 121.6324 | 81.4087 | -121.907
2158.9844 | 121.637 | -121.4859 | 0.16937 | 0.0066373 | 0.016505 | 0.076334 | 0.003843 | 0.073683 | 0.0032856 | 0.0019696 | -0.00068649 | -0.0012946 | 0.063388 | 0.13024 | -0.0034307 | 0.00066648 | -0.09613 | -107.4005 | -50.4501 | -120.488 | 0.16022 | -121.5134 | -121.3989 | -6.5552 | -39.2395 | -121.3028 | 0.068665 | 0.07782 | -121.5637 | -121.7285 | -0.027466 | 0.086975 | -0.009156 | 14.0854 | 0.99792 | 0.91095 | -0.2655 | -0.07782 | -0.24262 | -0.10071 | 114.9307 | 0.18311 | 0.42572 | -0.091553 | 121.6461 | 121.3898 | 71.0358 | -121.5683 | 121.5546 | 121.5637 | 82.2464 | -121.8979
2160.6719 | 121.6827 | -121.5225 | 0.17853 | 0.014267 | 0.020136 | 0.076548 | 0.005552 | 0.073896 | 0.0071308 | 0.003465 | 0.0069425 | 0.002978 | 0.062961 | 0.13174 | 0.00020087 | 2.5678e-05 | -0.17853 | -107.0023 | -50.6744 | -120.4834 | 0.21973 | -121.5317 | -121.463 | -6.5277 | -39.8026 | -121.3943 | 0.10529 | 0.14191 | -121.5775 | -121.7331 | -0.009155 | 0.059509 | 0.041199 | 14.5203 | 1.0391 | 0.97962 | -0.35706 | -0.054932 | -0.21057 | -0.073242 | 114.9948 | 0.12817 | 0.33875 | -0.036621 | 121.7422 | 121.344 | 70.8481 | -121.6415 | 121.6278 | 121.6644 | 81.72 | -121.9116
2162.3906 | 121.6736 | -121.5042 | 0.16022 | -0.00099167 | 0.019923 | 0.075266 | 0.0040566 | 0.07411 | 0.0077716 | 0.0019696 | 0.0069425 | 0.0016962 | 0.064029 | 0.13216 | -0.00065373 | 0.0047253 | -0.15564 | -106.4896 | -50.6424 | -120.4559 | 0.17395 | -121.5317 | -121.4355 | -6.308 | -39.6011 | -121.3028 | 0.10071 | 0.10986 | -121.5591 | -121.7194 | -0.027466 | 0.068664 | 0.013733 | 15.0146 | 1.0483 | 0.97961 | -0.31586 | -0.054932 | -0.21515 | -0.059509 | 115.1962 | 0.20142 | 0.41656 | -0.050354 | 121.6782 | 121.3486 | 70.8618 | -121.5958 | 121.6049 | 121.6141 | 81.9031 | -121.8796
2164.0938 | 121.7285 | -121.4767 | 0.13733 | 0.0066373 | 0.019709 | 0.077402 | 0.00897 | 0.074751 | 0.0045674 | 0.0028242 | 0.0069425 | 0.0010554 | 0.064457 | 0.13067 | -0.0059943 | 0.015406 | -0.10529 | -105.8853 | -50.5005 | -120.2682 | 0.1831 | -121.5088 | -121.4218 | -6.2988 | -44.9158 | -121.2982 | 0.082397 | 0.11444 | -121.5912 | -121.7285 | -0.032043 | 0.054932 | 0.045776 | 15.5914 | 1.2085 | 1.1536 | -0.24262 | -0.11444 | -0.25177 | -0.054932 | 115.1779 | 0.17853 | 0.4303 | -0.022888 | 121.6599 | 121.3715 | 70.9763 | -121.5591 | 121.5591 | 121.5912 | 76.561 | -121.8658
2165.7812 | 121.6644 | -121.5088 | 0.16022 | 0.014267 | 0.018 | 0.079966 | 0.003843 | 0.074965 | 0.0079852 | 0.0019696 | 0.0069425 | 0.001269 | 0.062961 | 0.13174 | 0.00084167 | 0.017543 | -0.07782 | -106.4896 | -52.9816 | -120.0668 | 0.17395 | -121.4767 | -121.3989 | -6.1752 | -45.9366 | -121.2799 | 0.073242 | 0.07782 | -121.5683 | -121.701 | 0.032043 | 0.10986 | 0.013733 | 15.0192 | 1.442 | 1.3321 | -0.23804 | -0.059509 | -0.19226 | -0.086975 | 115.3336 | 0.22888 | 0.42114 | -0.082397 | 121.6827 | 121.431 | 68.5272 | -121.5591 | 121.582 | 121.5866 | 75.5722 | -121.8613
2167.4844 | 121.7972 | -121.4767 | 0.14648 | 0.0066373 | 0.024409 | 0.077402 | 0.0070474 | 0.074751 | 0.0081988 | 0.0026106 | 0.0069425 | 0.004687 | 0.06702 | 0.13281 | -0.0019355 | 0.019038 | -0.14648 | -106.2012 | -53.4073 | -120.1996 | 0.21973 | -121.5408 | -121.4493 | -6.2668 | -45.9641 | -121.3211 | 0.12817 | 0.12817 | -121.5637 | -121.7148 | -0.064087 | 0.027466 | 0.073243 | 15.2756 | 1.2772 | 1.2497 | -0.29297 | -0.086975 | -0.23804 | -0.01831 | 115.21 | 0.15564 | 0.39368 | -0.01831 | 121.6965 | 121.3303 | 68.0695 | -121.5958 | 121.6049 | 121.6049 | 75.5127 | -121.8613
2169.1875 | 121.7468 | -121.4081 | 0.10986 | 0.0066373 | 0.019068 | 0.075907 | 0.0093972 | 0.073683 | 0.0020038 | 0.0026106 | 0.014572 | -0.0057806 | -0.0053982 | -0.0024182 | -0.01518 | 0.022242 | -0.10986 | -103.6285 | -51.5945 | -120.0211 | 0.14191 | -121.4859 | -121.3623 | -0.018311 | -1.6891 | -0.041199 | 0.11444 | 0.11444 | -0.14648 | -0.20599 | -0.07782 | 0.045776 | 0.032044 | 17.7795 | 1.387 | 1.3412 | -0.21973 | 121.2616 | 121.2021 | 0.004578 | 121.3898 | 121.3669 | 0.1648 | 0.004578 | 121.55 | 121.2982 | 69.8135 | -121.4722 | 121.5225 | 121.5225 | 119.7189 | -0.31586
2170.8906 | 121.6278 | -121.4859 | 0.13733 | 0.0066373 | 0.01565 | 0.080606 | 0.0032022 | 0.074751 | 0.0049946 | 0.0013288 | 0.0069425 | -0.0059942 | -0.006039 | -0.0015638 | -0.011121 | 0.022456 | -0.13275 | -104.5761 | -51.7181 | -119.902 | 0.14191 | -121.4767 | -121.4218 | -0.059509 | -1.886 | -0.09613 | 0.09613 | 0.082397 | -0.16937 | -0.19226 | 0.009155 | 0.064087 | 0.004578 | 16.9098 | 1.5839 | 1.5198 | -0.27008 | 121.3165 | 121.2936 | -0.041199 | 121.4264 | 121.3898 | 0.096131 | -0.054932 | 121.6278 | 121.3531 | 69.7678 | -121.5591 | 121.582 | 121.5683 | 119.5999 | -0.32959
2172.5938 | 121.6965 | -121.5088 | 0.12817 | -0.0086212 | 0.021632 | 0.077402 | 0.0034158 | 0.079451 | 0.013967 | 0.0038922 | -0.008316 | -0.0017218 | -0.0039028 | -0.0011364 | -0.0091985 | 0.020961 | -0.086975 | -104.2191 | -52.2675 | -119.5221 | 0.14648 | -121.5271 | -121.4264 | -0.022888 | -1.8036 | -0.073242 | 0.073242 | 0.09613 | -0.11444 | -0.16937 | -0.018311 | 0.082397 | 0.01831 | 17.2897 | 1.9867 | 1.9043 | -0.21515 | 121.3943 | 121.3394 | -0.054932 | 121.4859 | 121.4355 | 0.096131 | -0.032044 | 121.6553 | 121.4218 | 69.2413 | -121.5546 | 121.582 | 121.6049 | 119.7052 | -0.29755
2174.2656 | 121.7606 | -121.4813 | 0.11902 | 0.0066373 | 0.019923 | 0.075693 | 0.0081154 | 0.076887 | 0.018026 | 0.001756 | 0.014572 | -0.0059942 | -0.0017666 | -0.0043408 | -0.014753 | 0.025019 | -0.10986 | -103.8757 | -52.0065 | -117.5583 | 0.14191 | -121.4905 | -121.4447 | -0.027466 | -1.6891 | -0.036621 | 0.10529 | 0.086975 | -0.13275 | -0.17395 | -0.009156 | 0.036621 | 0.022888 | 17.6056 | 3.923 | 3.8864 | -0.22888 | 121.3486 | 121.3074 | -0.013733 | 121.4539 | 121.4447 | 0.13733 | -0.032044 | 121.6232 | 121.3715 | 69.4748 | -121.5637 | 121.5866 | 121.5683 | 119.7922 | -0.29297
2175.9531 | 121.6324 | -121.5546 | 0.15564 | -0.00099167 | 0.018427 | 0.080393 | 0.0036294 | 0.077314 | 0.02593 | 0.0023968 | 0.0069425 | -0.0062078 | -0.0017666 | -0.001991 | -0.010908 | 0.023524 | -0.10986 | -103.7613 | -52.6062 | -116.9861 | 0.14648 | -121.5271 | -121.4539 | -0.027466 | -1.712 | -0.041199 | 0.10071 | 0.086975 | -0.1236 | -0.17853 | 0.027465 | 0.10071 | -0.009156 | 17.7933 | 4.5685 | 4.4678 | -0.2655 | 121.431 | 121.376 | -0.054932 | 121.5271 | 121.5134 | 0.13733 | -0.068665 | 121.701 | 121.4447 | 68.9484 | -121.6095 | 121.6553 | 121.6415 | 119.8425 | -0.33417
2177.6562 | 120.9824 | -98.877 | 21.7987 | -0.00099167 | 0.020136 | 0.080606 | 0.0059792 | 0.073896 | 0.024434 | 0.0038922 | 0.0069425 | -0.00022644 | 0.013187 | 0.010826 | -0.0081305 | 0.0081433 | 21.5881 | -82.3746 | -34.6298 | -95.2744 | 21.8353 | -99.0372 | -98.9868 | 0.050354 | 4.3991 | 0.17395 | 21.7484 | 21.7484 | 0.1831 | 0.14648 | -0.16022 | -0.10986 | 0.036621 | 16.5024 | 3.6026 | 3.7125 | -0.21057 | 99.0601 | 99.0234 | -0.050354 | 98.9273 | 99.0509 | 0.027466 | -0.050354 | 120.7123 | 120.4651 | 64.2471 | -120.7855 | 120.6253 | 120.6253 | 103.2761 | -21.6522
2179.3281 | 121.2387 | -10.0067 | 111.1267 | -0.0086212 | 0.018854 | 0.084452 | 0.0083292 | 0.071974 | 0.00050836 | 0.00090156 | -0.00068649 | 0.004046 | 0.068088 | 0.05761 | -0.011121 | -0.040136 | 110.82 | 2.3071 | 38.6215 | -9.1232 | 111.1496 | -10.5515 | -10.0891 | 0.86975 | 24.4446 | 1.7761 | 111.0306 | 111.1038 | 1.5198 | 1.4877 | -0.54474 | -0.082397 | 0.022888 | 12.3138 | 0.88348 | 0.96588 | -0.3067 | 11.5265 | 11.4944 | -0.09613 | 10.8765 | 11.7828 | 0.28839 | -0.022888 | 121.1563 | 120.8267 | 48.6282 | -121.2158 | 121.0373 | 121.1105 | 34.4513 | -109.639
2181.0156 | 121.2662 | -70.2255 | 50.8392 | 0.014267 | 0.023981 | 0.079111 | 0.0023476 | 0.076887 | 0.021871 | 0.0038922 | 0.014572 | 0.001269 | 0.0095554 | 0.010399 | -0.0070623 | 0.010493 | 23.9319 | -68.0511 | -16.2552 | -81.4728 | 37.5641 | -81.015 | -83.8943 | 0.068665 | 5.3833 | -0.045776 | 19.5648 | 19.606 | 0.19226 | 0.16937 | -10.7895 | -13.6688 | -13.2751 | 2.1744 | -11.2473 | 2.4216 | -26.9073 | 70.4178 | 70.3949 | -31.2744 | 70.2942 | 70.1797 | -0.21515 | -31.2332 | 107.7896 | 94.1574 | 53.9703 | -134.7336 | 89.7903 | 89.8315 | 75.6088 | -50.6699
2182.7031 | 121.4951 | -118.8538 | 2.3621 | 0.0066373 | 0.023768 | 0.080179 | 0.0081154 | 0.079237 | 0.033193 | 0.005174 | 0.0069425 | -0.00086724 | -0.00027123 | 0.00078621 | -0.013258 | 0.02032 | 2.0187 | -99.6368 | -51.741 | -113.4613 | 2.4353 | -119.0826 | -118.9362 | -0.13275 | -0.72784 | -0.14648 | 2.3849 | 2.3712 | -0.13275 | -0.19684 | -0.22888 | -0.082397 | 0.073242 | 19.2169 | 5.3925 | 5.4749 | -0.34332 | 118.721 | 118.6569 | 0.022888 | 118.721 | 118.7073 | 0.050354 | 0.009155 | 121.2891 | 120.8725 | 67.1127 | -121.2982 | 121.2387 | 121.225 | 118.1259 | -2.5589
2184.375 | 121.3989 | -96.1349 | 25.0854 | 0.0066373 | 0.016291 | 0.080393 | 0.0034158 | 0.076033 | 0.024434 | 0.0028242 | 0.0069425 | -0.0036444 | 0.01575 | 0.009972 | -0.010908 | 0.0070753 | 24.6735 | -79.0054 | -33.6136 | -92.4133 | 24.2844 | -97.4213 | -97.8836 | 0.16937 | 7.1915 | 0.36621 | 24.9939 | 25.0259 | 0.2243 | 0.19684 | -1.2863 | -1.7487 | -0.80109 | 17.1295 | 3.7216 | 5.4703 | -0.41199 | 96.3593 | 96.3318 | -0.091553 | 96.3043 | 96.5012 | 0.16937 | -0.059509 | 120.4193 | 120.8084 | 62.5214 | -122.9691 | 121.1288 | 121.1609 | 103.3264 | -24.8886
2186.0625 | 121.4493 | -114.9399 | 6.3492 | 0.0066373 | 0.015864 | 0.081034 | 0.0051248 | 0.085005 | 0.4677 | 0.0045332 | 0.014572 | -0.003858 | -0.001553 | -0.00070919 | -0.011762 | 0.018824 | 6.2668 | -90.8981 | -45.9778 | -36.5707 | 6.395 | -115.036 | -114.9124 | -0.022888 | 1.1215 | 0.027466 | 6.2897 | 6.2897 | -0.041199 | -0.086975 | -0.096131 | 0.027465 | 0.045776 | 24.0417 | 78.3691 | 78.3417 | -0.082397 | 114.8987 | 114.8529 | -0.059509 | 114.917 | 114.9673 | 0.11444 | -0.059509 | 121.3348 | 121.2067 | 68.9621 | -121.2616 | 121.2296 | 121.2296 | 116.0614 | -6.4362
2187.7656 | 121.4264 | -116.7526 | 4.6051 | -0.00099167 | 0.021845 | 0.080606 | 0.0051248 | 0.088209 | 0.70162 | 0.0049604 | 0.014572 | 0.00062796 | 0.0010104 | 0.0018542 | -0.0083441 | 0.018824 | 4.4769 | -90.1428 | -46.4584 | -5.4794 | 4.6646 | -116.7618 | -116.6702 | -0.086975 | 0.5127 | -0.10986 | 4.5868 | 4.5685 | -0.086975 | -0.15106 | -0.009155 | 0.082398 | 0.059509 | 26.6098 | 111.2732 | 111.1908 | -0.12817 | 116.6656 | 116.6016 | -0.018311 | 116.6656 | 116.6428 | 0.041199 | -0.036622 | 121.4172 | 121.2296 | 70.2942 | -121.2753 | 121.3394 | 121.3211 | 117.2653 | -4.7562
2189.5156 | 121.3943 | -117.2104 | 4.1656 | 0.014267 | 0.021845 | 0.078043 | 0.0044838 | 0.088636 | 0.70952 | 0.008592 | 0.0069425 | 0.00084176 | -0.0017666 | 0.0022814 | -0.0066351 | 0.018397 | 4.0375 | -89.5248 | -46.7697 | -4.4495 | 4.2389 | -117.1967 | -117.1097 | -0.10529 | 0.34332 | -0.15564 | 4.1428 | 4.1382 | -0.09613 | -0.16479 | 0.013733 | 0.10071 | 0.073243 | 27.6855 | 112.7609 | 112.6602 | -0.12817 | 117.1143 | 117.0456 | -0.022888 | 117.1051 | 117.0547 | 0.009155 | -0.027465 | 121.4493 | 121.2479 | 70.4407 | -121.2753 | 121.3531 | 121.3486 | 117.5537 | -4.3304
2191.2031 | 121.5271 | -117.3706 | 3.9368 | 0.014267 | 0.024622 | 0.078257 | 0.0087564 | 0.089491 | 0.71123 | 0.0077374 | -0.00068649 | 0.00041436 | -0.001553 | 0.0018542 | -0.012189 | 0.019893 | 3.8681 | -88.1104 | -47.3831 | -4.01 | 4.0421 | -117.3706 | -117.2882 | -0.064087 | 0.29755 | -0.068665 | 3.9597 | 3.9505 | -0.086975 | -0.16022 | 0 | 0.082397 | 0.10529 | 29.2603 | 113.3606 | 113.2782 | -0.068665 | 117.2836 | 117.2104 | 0.022888 | 117.3065 | 117.3019 | 0.091552 | 0.013732 | 121.4127 | 121.2387 | 69.9875 | -121.225 | 121.3303 | 121.3211 | 117.6682 | -4.097
2192.9688 | 121.3943 | -117.4667 | 3.9368 | 0.0066373 | 0.022272 | 0.075479 | 0.0044838 | 0.0912 | 0.71465 | 0.0090192 | 0.0069425 | 0.00084176 | -0.00069863 | 0.0018542 | -0.010267 | 0.021388 | 3.7857 | -87.8906 | -47.9599 | -3.7857 | 4.0054 | -117.4118 | -117.3752 | -0.11902 | 0.24719 | -0.15106 | 3.9322 | 3.9139 | -0.09613 | -0.16937 | 0.054932 | 0.091553 | 0.068664 | 29.5761 | 113.681 | 113.5895 | -0.15106 | 117.3706 | 117.2974 | -0.004578 | 117.3477 | 117.3157 | 0.018311 | -0.022889 | 121.4722 | 121.2524 | 69.5068 | -121.312 | 121.3989 | 121.3806 | 117.7139 | -4.1061
2194.7812 | 121.4447 | -117.5903 | 3.7674 | -0.00099167 | 0.017573 | 0.081675 | 0.0034158 | 0.090345 | 0.70803 | 0.006883 | 0.0069425 | -0.0032172 | -0.0041164 | 0.00035881 | -0.01048 | 0.022029 | 3.6713 | -87.529 | -48.1888 | -3.6026 | 3.8223 | -117.5766 | -117.4759 | -0.091553 | 0.2655 | -0.068665 | 3.7537 | 3.7445 | -0.091553 | -0.15564 | 0.013733 | 0.11444 | 0.054932 | 30.0613 | 113.9877 | 113.8733 | -0.09613 | 117.4988 | 117.4347 | -0.013733 | 117.4988 | 117.5217 | 0.086975 | -0.022888 | 121.4127 | 121.2616 | 69.4016 | -121.2433 | 121.344 | 121.3348 | 117.8558 | -3.923
2196.5625 | 121.4996 | -117.5674 | 3.7628 | -0.00099167 | 0.021204 | 0.078043 | 0.010038 | 0.091627 | 0.71102 | 0.006883 | 0.0069425 | -0.00086724 | 0.0014378 | -0.00028199 | -0.014326 | 0.020747 | 3.6255 | -86.9431 | -47.9507 | -3.5797 | 3.8544 | -117.572 | -117.5034 | -0.13275 | 0.26093 | -0.12817 | 3.7811 | 3.7674 | -0.10529 | -0.16479 | -0.004577 | 0.064087 | 0.091553 | 30.6244 | 113.9877 | 113.9236 | -0.13733 | 117.4622 | 117.4026 | 0.018311 | 117.4347 | 117.4393 | 0.036621 | 0.004578 | 121.4218 | 121.1929 | 69.6167 | -121.2662 | 121.3486 | 121.3348 | 117.8284 | -3.9276
2198.3125 | 121.5225 | -117.6865 | 3.6255 | 0.0066373 | 0.0227 | 0.080179 | 0.0064066 | 0.091627 | 0.71294 | 0.0088056 | 0.0069425 | -0.0030034 | -0.0011258 | -0.0026318 | -0.013044 | 0.019893 | 3.5339 | -86.2747 | -47.8043 | -3.4332 | 3.7674 | -117.6498 | -117.6041 | -0.09613 | 0.22888 | -0.09613 | 3.6575 | 3.6575 | -0.10986 | -0.16937 | 0.036621 | 0.082397 | 0.14191 | 31.4117 | 114.2532 | 114.1708 | -0.091552 | 117.5766 | 117.5171 | 0.032044 | 117.5903 | 117.5903 | 0.073243 | 0.032044 | 121.4539 | 121.2204 | 69.8822 | -121.2296 | 121.344 | 121.344 | 117.9153 | -3.7949
2200.0781 | 121.5317 | -117.8741 | 3.4195 | 0.0066373 | 0.019709 | 0.079752 | 0.0085428 | 0.093336 | 0.71508 | 0.0088056 | 0.014572 | -0.002149 | -0.0028348 | 0.00057261 | -0.012189 | 0.019679 | 3.3234 | -85.7849 | -47.3923 | -3.3691 | 3.5431 | -117.865 | -117.7872 | -0.10529 | 0.086975 | -0.11902 | 3.4744 | 3.4378 | -0.10071 | -0.16937 | 0.009156 | 0.086976 | 0.1236 | 32.0892 | 114.505 | 114.418 | -0.096131 | 117.7734 | 117.7048 | 0.054931 | 117.7689 | 117.7551 | 0.050354 | 0.01831 | 121.4172 | 121.1975 | 70.4819 | -121.2067 | 121.3486 | 121.312 | 117.9611 | -3.5889
2201.7812 | 121.5408 | -117.7551 | 3.5522 | -0.00099167 | 0.023127 | 0.080179 | 0.0044838 | 0.093122 | 0.71508 | 0.010087 | 0.0069425 | -0.00086724 | -0.0011258 | 0.001427 | -0.010267 | 0.02032 | 3.479 | -85.1669 | -46.4355 | -3.2547 | 3.6575 | -117.7643 | -117.6819 | -0.07782 | 0.17853 | -0.086975 | 3.5751 | 3.5568 | -0.10529 | -0.14191 | -0.009155 | 0.073242 | 0.10529 | 32.5882 | 114.5004 | 114.4272 | -0.073242 | 117.6498 | 117.6132 | 0.022888 | 117.6773 | 117.6682 | 0.054932 | 0.004578 | 121.4127 | 121.2341 | 71.3196 | -121.2341 | 121.3303 | 121.312 | 117.9337 | -3.6942
2203.5312 | 121.5179 | -117.7597 | 3.5614 | 0.0066373 | 0.019923 | 0.08317 | 0.010893 | 0.094831 | 0.70995 | 0.0075238 | -0.00068649 | -0.0064214 | 0.00058317 | 0.00035881 | -0.015607 | 0.02032 | 3.5156 | -84.4666 | -45.5521 | -3.1631 | 3.6163 | -117.7414 | -117.6453 | 0.009155 | 0.21973 | 0.032043 | 3.5156 | 3.5385 | -0.082397 | -0.11902 | 0.018311 | 0.11444 | 0.054932 | 33.2932 | 114.5966 | 114.4821 | -0.045776 | 117.6773 | 117.6407 | -0.045776 | 117.7689 | 117.7917 | 0.15106 | -0.022888 | 121.376 | 121.2753 | 72.2076 | -121.2067 | 121.2753 | 121.2982 | 117.9794 | -3.6804
2205.2812 | 121.4081 | -117.8009 | 3.598 | 0.0066373 | 0.016932 | 0.080606 | 0.0079018 | 0.092909 | 0.70846 | 0.0066694 | 0.0069425 | -0.0057806 | -0.0011258 | -0.00092279 | -0.013898 | 0.021601 | 3.4698 | -83.7067 | -45.9595 | -3.1723 | 3.6346 | -117.7322 | -117.6544 | -0.054932 | 0.16022 | -0.027466 | 3.5385 | 3.5339 | -0.09613 | -0.1236 | 0.068664 | 0.14648 | 0.036622 | 34.0942 | 114.6286 | 114.4821 | -0.12817 | 117.7048 | 117.6773 | -0.059509 | 117.746 | 117.7734 | 0.09613 | -0.064086 | 121.4355 | 121.2708 | 71.8414 | -121.2524 | 121.3394 | 121.3348 | 117.9611 | -3.7216
2207.0312 | 121.4767 | -117.8284 | 3.5294 | -0.00099167 | 0.021418 | 0.081461 | 0.007261 | 0.096113 | 0.71294 | 0.0083784 | -0.00068649 | -0.0042852 | -0.0013394 | -0.0013502 | -0.013471 | 0.019465 | 3.4836 | -83.2397 | -45.7809 | -3.0716 | 3.5751 | -117.778 | -117.6773 | -0.013733 | 0.18768 | 0.013733 | 3.4744 | 3.4698 | -0.064087 | -0.13733 | 0.050354 | 0.15106 | 0.045776 | 34.5886 | 114.7568 | 114.6057 | -0.045776 | 117.7643 | 117.691 | -0.054932 | 117.8146 | 117.8421 | 0.15106 | -0.059509 | 121.4035 | 121.312 | 72.0474 | -121.2067 | 121.3028 | 121.2982 | 118.0161 | -3.6667
2208.7188 | 121.4081 | -117.7917 | 3.598 | -0.00099167 | 0.023554 | 0.081888 | 0.0051248 | 0.096113 | 0.71636 | 0.0098738 | 0.0069425 | -0.0025762 | -0.00091223 | -6.8386e-05 | -0.010053 | 0.018184 | 3.5431 | -82.933 | -45.7901 | -2.9892 | 3.6392 | -117.7048 | -117.6544 | -0.009155 | 0.21057 | -0.009155 | 3.5339 | 3.5294 | -0.054932 | -0.091553 | 0.086975 | 0.13733 | 0.041199 | 34.8587 | 114.8026 | 114.6652 | -0.054931 | 117.7368 | 117.7002 | -0.064086 | 117.7826 | 117.7826 | 0.082398 | -0.068664 | 121.431 | 121.3348 | 72.0016 | -121.2524 | 121.3257 | 121.3211 | 118.0023 | -3.6896
2210.4844 | 121.4355 | -117.8787 | 3.5248 | -0.00099167 | 0.021418 | 0.079538 | 0.0070474 | 0.096968 | 0.71914 | 0.013505 | -0.00068649 | 0.00062796 | -0.001553 | 0.00057261 | -0.010053 | 0.019679 | 3.4058 | -82.2968 | -45.7535 | -3.0441 | 3.6209 | -117.8238 | -117.7322 | -0.10529 | 0.064087 | -0.14648 | 3.4882 | 3.5065 | -0.10986 | -0.16479 | 0.054931 | 0.14648 | 0.096131 | 35.582 | 114.8346 | 114.6881 | -0.11902 | 117.7689 | 117.7139 | -0.036621 | 117.7734 | 117.7322 | 0.018311 | -0.01831 | 121.4996 | 121.2845 | 72.1252 | -121.257 | 121.3669 | 121.3852 | 117.9428 | -3.6896
2212.2344 | 121.5088 | -117.6086 | 3.7354 | 0.0066373 | 0.022486 | 0.079325 | 0.007261 | 0.099531 | 0.71785 | 0.010515 | -0.00068649 | 0.00062796 | 0.00058317 | -0.0011364 | -0.010053 | 0.020747 | 3.6621 | -80.777 | -45.2271 | -2.948 | 3.8406 | -117.5812 | -117.5034 | -0.068665 | 0.2243 | -0.10529 | 3.7354 | 3.7308 | -0.09613 | -0.17395 | 0.027466 | 0.10529 | 0.10529 | 36.8317 | 114.6606 | 114.5554 | -0.073243 | 117.5125 | 117.4347 | 0 | 117.54 | 117.5034 | 0.068664 | -0.004578 | 121.4493 | 121.2708 | 72.3816 | -121.2387 | 121.344 | 121.3394 | 117.8329 | -3.9093
2213.9219 | 121.5317 | -117.7551 | 3.5797 | 0.0066373 | 0.019282 | 0.083384 | 0.0085428 | 0.10615 | 0.71038 | 0.010087 | -0.00068649 | -0.0042852 | -5.7632e-05 | -0.0022046 | -0.015394 | 0.022456 | 3.511 | -66.9479 | -44.696 | -2.8931 | 3.6484 | -117.7094 | -117.659 | -0.004578 | 0.15564 | 0.013733 | 3.5385 | 3.5522 | -0.091553 | -0.13733 | 0.045776 | 0.09613 | 0.068664 | 50.8072 | 114.8621 | 114.7659 | -0.068665 | 117.6636 | 117.6178 | -0.041199 | 117.7505 | 117.7689 | 0.15106 | -0.027466 | 121.4035 | 121.2662 | 73.0591 | -121.2387 | 121.2936 | 121.3074 | 117.9108 | -3.717
2215.6719 | 121.4264 | -117.897 | 3.5156 | 0.0066373 | 0.020136 | 0.078897 | 0.0025612 | 0.10957 | 0.717 | 0.012651 | -0.00068649 | -0.0023626 | 0.0022922 | -0.00049559 | -0.010267 | 0.019679 | 3.4241 | -61.9217 | -44.6182 | -2.8473 | 3.5614 | -117.8192 | -117.7505 | -0.009155 | 0.07782 | -0.022888 | 3.4424 | 3.4378 | -0.086975 | -0.14191 | 0.07782 | 0.14648 | 0.045776 | 55.9753 | 115.0497 | 114.9033 | -0.091553 | 117.8101 | 117.7551 | -0.073242 | 117.8879 | 117.8741 | 0.11902 | -0.07782 | 121.4584 | 121.3211 | 73.2788 | -121.2662 | 121.3394 | 121.3348 | 117.9749 | -3.6575
2217.4062 | 121.4218 | -117.9337 | 3.4103 | -0.00099167 | 0.02035 | 0.079966 | 0.0042702 | 0.11064 | 0.71572 | 0.01436 | -0.00068649 | -0.002149 | -0.0017666 | 0.00057261 | -0.011121 | 0.020747 | 3.3783 | -62.9562 | -44.8837 | -2.742 | 3.4515 | -117.897 | -117.7963 | -0.022888 | 0.082397 | -0.041199 | 3.3737 | 3.3554 | -0.073242 | -0.14648 | 0.036621 | 0.13733 | 0.041199 | 54.9774 | 115.1917 | 115.0543 | -0.032043 | 117.8604 | 117.7872 | -0.036621 | 117.9108 | 117.8925 | 0.10529 | -0.054931 | 121.3852 | 121.312 | 73.0499 | -121.2067 | 121.3074 | 121.2891 | 118.0161 | -3.5568
2219.0938 | 121.5088 | -118.4738 | 2.8473 | 0.014267 | 0.024409 | 0.079966 | 0.0049112 | 0.10872 | 0.72255 | 0.013933 | 0.014572 | 0.0014826 | -0.0021938 | 0.00035881 | -0.0085577 | 0.02032 | 2.7695 | -64.682 | -45.1172 | -2.7237 | 2.9114 | -118.4921 | -118.4143 | -0.13733 | 0.036621 | -0.15106 | 2.8427 | 2.8381 | -0.1236 | -0.20142 | -0.01831 | 0.059509 | 0.064087 | 53.7918 | 115.7501 | 115.6906 | -0.07782 | 118.3502 | 118.2724 | -0.004578 | 118.3365 | 118.3228 | 0.050354 | -0.009155 | 121.3852 | 121.2433 | 73.3566 | -121.2616 | 121.3165 | 121.312 | 118.5104 | -3.0487
2220.7969 | 121.4081 | -118.5013 | 2.8839 | 0.0066373 | 0.025904 | 0.082315 | 0.002775 | 0.11192 | 0.72213 | 0.014573 | -0.00068649 | -0.00044004 | 0.00036957 | 0.00014521 | -0.010267 | 0.020533 | 2.7924 | -61.6104 | -45.3369 | -2.6367 | 2.9526 | -118.4601 | -118.3777 | -0.18768 | -0.009155 | -0.15106 | 2.8748 | 2.8427 | -0.14648 | -0.20142 | 0.041199 | 0.1236 | 0.068665 | 56.8909 | 115.8646 | 115.741 | -0.091553 | 118.3548 | 118.2999 | -0.009155 | 118.3136 | 118.3502 | 0.050354 | -0.041199 | 121.4539 | 121.2936 | 73.1644 | -121.2616 | 121.376 | 121.344 | 118.4921 | -3.0853
2222.4844 | 121.0373 | -32.4142 | 88.266 | -0.0086212 | 0.031031 | 0.095987 | 0.012388 | 0.084578 | 0.19747 | 0.006883 | -0.00068649 | 0.0083186 | 0.060611 | 0.049065 | -0.0091985 | -0.029027 | 88.1241 | -7.5485 | 24.6918 | -0.71869 | 88.3392 | -32.4463 | -32.5333 | 1.442 | 1.9913 | 1.7395 | 88.2568 | 88.2706 | 1.593 | 1.5793 | -0.032043 | -0.11902 | 0.073242 | 24.8657 | 31.6956 | 31.8146 | -0.14191 | 34.0073 | 33.9935 | -0.009155 | 33.8562 | 34.1537 | 0.16022 | 0.004578 | 120.7535 | 120.5383 | 57.106 | -120.7993 | 120.6711 | 120.6848 | 34.4055 | -86.6867
2224.2188 | 120.282 | -33.3618 | 87.085 | -0.00099167 | 0.032954 | 0.10047 | 0.0079018 | 0.085432 | 0.21029 | 0.0094464 | 0.0069425 | 0.010882 | 0.059757 | 0.046929 | -0.0087713 | -0.029241 | 86.998 | -8.1665 | 23.4695 | -0.74158 | 87.0758 | -34.0256 | -34.0347 | 1.5152 | 1.9409 | 1.7258 | 86.4349 | 86.5814 | 1.5793 | 1.5472 | -0.66376 | -0.67291 | -0.009155 | 25.1953 | 32.6202 | 33.2932 | -0.086975 | 34.9411 | 34.9091 | -0.65002 | 34.877 | 35.0876 | 0.17853 | -0.50354 | 120.4376 | 120.3598 | 56.8314 | -121.1197 | 119.7968 | 119.9432 | 35.3027 | -85.5377
2225.9688 | 121.3943 | -116.011 | 4.9576 | -0.00099167 | 0.023768 | 0.080393 | 0.0087564 | 0.11278 | 0.70589 | 0.012224 | -0.008316 | -0.0025762 | 0.0010104 | -6.8386e-05 | -0.011335 | 0.020106 | 4.8477 | -62.9379 | -44.252 | -2.4536 | 5.0949 | -116.2125 | -116.0751 | -0.16022 | 0.004578 | -0.11902 | 5.0034 | 5.0034 | -0.1236 | -0.16937 | -0.20142 | -0.064087 | 0.13733 | 53.0731 | 113.5574 | 113.6215 | -0.10986 | 115.8875 | 115.8417 | 0.045776 | 115.8508 | 115.892 | 0.050354 | 0.045776 | 121.106 | 120.8588 | 71.759 | -121.0327 | 121.0144 | 121.0144 | 116.0156 | -5.127
2227.6562 | 121.3394 | -116.684 | 4.3762 | -0.00099167 | 0.023554 | 0.081247 | 0.00897 | 0.14332 | 0.70461 | 0.012864 | 0.0069425 | -0.0042852 | 0.001865 | -0.0013502 | -0.015394 | 0.022029 | 4.3076 | -59.8206 | -44.9249 | -2.3621 | 4.4495 | -116.7526 | -116.6519 | -0.10529 | 0.10529 | -0.045776 | 4.3579 | 4.3579 | -0.09613 | -0.1831 | -0.068665 | 0.032043 | 0.073242 | 56.8634 | 114.3219 | 114.2899 | -0.068665 | 116.5878 | 116.5009 | -0.018311 | 116.5787 | 116.6382 | 0.13733 | -0.018311 | 121.1334 | 120.9915 | 71.759 | -121.0281 | 121.0419 | 121.0419 | 116.7892 | -4.5593
2229.4219 | 121.2936 | -117.16 | 3.9688 | 0.0066373 | 0.02804 | 0.078684 | 0.0057656 | 0.13905 | 0.71166 | 0.011796 | 0.014572 | -1.2844e-05 | 0.0020786 | 0.00099981 | -0.010694 | 0.02267 | 3.8315 | -61.7523 | -46.7377 | -2.4765 | 4.0741 | -117.1829 | -117.1188 | -0.16479 | -0.059509 | -0.16479 | 3.9825 | 3.9734 | -0.13733 | -0.20142 | -0.022888 | 0.041199 | 0.10529 | 55.4077 | 114.6835 | 114.6423 | -0.13733 | 117.0227 | 116.9586 | 0.013733 | 116.9952 | 116.9952 | 0.036621 | 0.004578 | 121.2341 | 120.9915 | 70.4224 | -121.0876 | 121.1426 | 121.1334 | 117.1005 | -4.1702
2231.1094 | 121.2524 | -118.1213 | 3.0304 | 0.0066373 | 0.010523 | 0.0079745 | 0.00085245 | 0.0038281 | -0.0018414 | -0.0052936 | -0.00068649 | -0.0042852 | -0.0047574 | -0.00049559 | -0.011335 | 0.019679 | 3.067 | 0.60425 | 1.3641 | 0.17395 | 3.154 | 0.20599 | 0.050354 | 0.13275 | 0.17853 | 0.064087 | 3.0167 | 2.9984 | -0.009155 | -0.059509 | 118.3273 | 118.1717 | 0.1236 | 118.7256 | 118.2953 | 0.1236 | 0.036621 | 118.1122 | 118.0618 | -0.013733 | 118.2541 | 118.1854 | 0.1236 | -0.032044 | 121.2753 | 121.1884 | 119.4855 | -2.98 | 121.138 | 121.1197 | 118.2999 | -3.0899
2232.8594 | 121.3806 | -118.3228 | 2.8564 | -0.0086212 | 0.012659 | 0.0058383 | 0.0093972 | 0.0053235 | -0.0018414 | -0.0072162 | 0.014572 | -0.0059942 | -0.0024074 | 0.00035881 | -0.014539 | 0.018397 | 2.7695 | 0.59967 | 1.1993 | 0.17395 | 2.8473 | 0.14191 | 0.004578 | 0.1236 | 0.21973 | 0.091553 | 2.7237 | 2.7374 | -0.009155 | -0.073242 | 118.4647 | 118.3273 | -0.009155 | 118.9224 | 118.4967 | 0.16937 | -0.086975 | 118.3136 | 118.2495 | -0.13275 | 118.4464 | 118.4143 | 0.16479 | -0.11902 | 121.17 | 121.0922 | 119.5221 | -2.8519 | 121.0464 | 121.0602 | 118.5425 | -2.9297
2234.625 | 121.3943 | -119.632 | 1.6937 | 0.014267 | 0.012659 | 0.0066927 | 0.0068338 | 0.0042555 | -0.0024822 | -0.00508 | -0.00068649 | -0.0047124 | -0.003262 | -0.0017774 | -0.016035 | 0.020747 | 1.6067 | 0.28839 | 0.6546 | 0.12817 | 1.7899 | 0.027466 | -0.1236 | 0.050354 | 0.10071 | 0.022888 | 1.6983 | 1.6891 | -0.036621 | -0.11444 | 119.6594 | 119.5084 | 0.09613 | 119.9203 | 119.7601 | 0.25177 | -0.086976 | 119.5953 | 119.5175 | 0.004577 | 119.6823 | 119.6548 | 0.13733 | -0.004578 | 121.4218 | 121.2387 | 120.2866 | -1.8173 | 121.3303 | 121.3211 | 119.7327 | -1.8082
2236.3125 | 121.4767 | -120.0485 | 1.2909 | -0.00099167 | 0.013514 | 0.0051975 | 0.0085428 | 0.0016919 | 0.003072 | -0.0063616 | 0.0069425 | -0.0012946 | -0.00048483 | -0.00070919 | -0.012403 | 0.017543 | 1.1581 | 0.15564 | 0.38452 | 0.073242 | 1.3733 | -0.059509 | -0.1831 | -0.009155 | 0.022888 | -0.09613 | 1.2863 | 1.2634 | -0.082397 | -0.14648 | 119.989 | 119.8654 | 0.082397 | 120.2042 | 120.1218 | 0.25635 | -0.13275 | 119.9661 | 119.902 | -0.004578 | 120.0394 | 119.9524 | 0.050354 | -0.027466 | 121.4218 | 121.2067 | 120.433 | -1.474 | 121.3348 | 121.312 | 120.0714 | -1.4374
2238.0625 | 121.3531 | -120.076 | 1.3229 | 0.0066373 | 0.0073188 | 0.0066927 | 0.0046976 | 0.00041006 | -0.0033368 | -0.00508 | -0.00068649 | -0.006635 | -0.0047574 | -0.0017774 | -0.01048 | 0.019038 | 1.2177 | 0.23804 | 0.48523 | 0.11444 | 1.355 | 0.018311 | -0.13275 | 0.059509 | 0.091553 | -0.004578 | 1.2726 | 1.268 | -0.050354 | -0.11444 | 120.0943 | 119.9432 | 0.032043 | 120.314 | 120.1904 | 0.24719 | -0.10529 | 120.0256 | 119.9615 | -0.050354 | 120.1355 | 120.0714 | 0.10986 | -0.054932 | 121.431 | 121.2936 | 120.5612 | -1.4557 | 121.3486 | 121.344 | 120.1675 | -1.4374
2239.75 | 121.3806 | -120.6802 | 0.75073 | -0.00099167 | 0.012659 | 0.0034885 | 0.0014932 | 0.0048963 | 0.0049946 | -0.0029436 | 0.0069425 | -0.00086724 | -0.0058254 | -0.00049559 | -0.0066351 | 0.019465 | 0.62256 | 0.064087 | 0.16022 | 0.091553 | 0.8194 | -0.032043 | -0.20142 | 0 | 0.004578 | -0.14648 | 0.72784 | 0.71869 | -0.091553 | -0.16022 | 120.6482 | 120.4788 | 0.068665 | 120.7443 | 120.7718 | 0.29297 | -0.12817 | 120.5887 | 120.52 | -0.022888 | 120.6802 | 120.5338 | 0.013733 | -0.032043 | 121.4996 | 121.3028 | 120.8405 | -0.95215 | 121.4081 | 121.3989 | 120.6848 | -0.91095
2241.5156 | 121.4264 | -120.8817 | 0.53101 | 0.014267 | 0.011805 | 0.0069063 | 0.0044838 | 0.0029737 | 0.0026446 | -0.0048662 | 0.0069425 | -0.00065364 | -0.0068936 | 0.00099981 | -0.01048 | 0.02032 | 0.38452 | 0 | 0.059509 | 0.059509 | 0.60425 | -0.045776 | -0.20599 | 0 | -0.004578 | -0.10071 | 0.50354 | 0.48065 | -0.09613 | -0.13275 | 120.8359 | 120.6757 | 0.073242 | 120.8817 | 120.9412 | 0.2655 | -0.14648 | 120.7855 | 120.7489 | -0.027466 | 120.8817 | 120.7809 | 0.032043 | -0.050354 | 121.4859 | 121.2662 | 120.9412 | -0.737 | 121.3852 | 121.3623 | 120.8771 | -0.66376
2243.2031 | 121.431 | -120.9 | 0.54016 | -0.00099167 | 0.015436 | 0.0045565 | 0.0053384 | 0.0027601 | 0.0026446 | -0.0042254 | -0.00068649 | -0.00022644 | -0.0041164 | 0.00035881 | -0.0096259 | 0.021815 | 0.40283 | -0.013733 | 0.050354 | 0.086975 | 0.60883 | -0.050354 | -0.21973 | -0.018311 | -0.027466 | -0.10986 | 0.52185 | 0.5127 | -0.09613 | -0.14191 | 120.8496 | 120.6802 | 0.068665 | 120.8862 | 120.9869 | 0.3067 | -0.13733 | 120.8038 | 120.7581 | -0.01831 | 120.8817 | 120.7901 | 0.032044 | -0.027466 | 121.5088 | 121.3028 | 120.9503 | -0.75989 | 121.4218 | 121.4127 | 120.8725 | -0.68207
2244.8906 | 121.0327 | -113.8412 | 6.8939 | 0.014267 | 0.012018 | 0.0094699 | 0.0042702 | 0.0046827 | -0.002055 | -0.0040118 | 0.0069425 | -0.0015082 | 0.00015597 | 0.00057261 | -0.0081305 | 0.017756 | 6.8802 | 1.5564 | 2.9388 | 0.14648 | 6.9534 | 0.3479 | 0.18768 | 0.39368 | 0.28839 | 0.17853 | 6.8573 | 6.8527 | 0.11444 | 0.036621 | 114.1891 | 114.0289 | 0.059509 | 115.3976 | 113.9877 | -0.041199 | -0.013733 | 113.9557 | 113.8779 | -0.036621 | 114.2349 | 114.0198 | 0.14191 | -0.041199 | 120.7947 | 120.7214 | 116.7801 | -6.7062 | 120.6985 | 120.694 | 114.1296 | -6.8573
2246.6406 | 121.1975 | -116.8625 | 4.216 | 0.0066373 | 0.009455 | 0.010538 | 0.0036294 | 0.0048963 | -0.0044048 | -0.00508 | -0.00068649 | -0.0040716 | -0.00433 | -0.0011364 | -0.013044 | 0.020106 | 4.129 | 0.98877 | 1.7303 | 0.11902 | 4.2252 | 0.18768 | 0.036621 | 0.22888 | 0.19684 | 0.086975 | 4.1245 | 4.1245 | 0.027466 | -0.013733 | 117.0502 | 116.8991 | 0.009156 | 117.8513 | 116.9815 | 0.082398 | -0.086975 | 116.89 | 116.8488 | -0.091552 | 117.0914 | 116.9495 | 0.10071 | -0.091552 | 121.0876 | 120.9915 | 118.5928 | -4.1794 | 120.9869 | 120.9869 | 117.0593 | -4.2297
2248.3906 | 121.2662 | -117.0273 | 4.1153 | -0.00099167 | 0.014155 | 0.0077609 | 0.003843 | 0.0057507 | 0.0037128 | -0.0023028 | 0.014572 | 0.0010554 | -0.0028348 | 0.0027088 | -0.0087713 | 0.018611 | 4.0833 | 1.4557 | 1.6983 | 0.13275 | 4.1748 | 0.15564 | 0 | 0.21057 | 0.13275 | 0 | 4.1107 | 4.1153 | 0.009155 | -0.054932 | 117.1829 | 117.0273 | 0.05951 | 118.483 | 117.16 | 0.13275 | -0.032043 | 117.0364 | 116.9724 | -0.004577 | 117.2379 | 117.0273 | 0.054932 | 0 | 121.2021 | 121.1105 | 118.7256 | -4.1153 | 121.138 | 121.1426 | 117.16 | -4.1702
2250.0781 | 121.376 | -117.4667 | 3.7399 | 0.0066373 | 0.013087 | 0.0092563 | 0.010252 | 0.0023327 | -0.00055964 | -0.00508 | 0.0069425 | -0.0027898 | 0.0022922 | -6.8386e-05 | -0.014539 | 0.018824 | 3.6209 | 1.5564 | 1.5244 | 0.091553 | 3.8406 | 0.086975 | -0.064087 | 0.13275 | 0.10529 | -0.013733 | 3.7354 | 3.7125 | -0.022888 | -0.059509 | 117.5537 | 117.4026 | 0.10071 | 119.0231 | 117.5583 | 0.15564 | -0.11902 | 117.4438 | 117.4072 | -0.004577 | 117.5995 | 117.453 | 0.045776 | -0.027466 | 121.3074 | 121.0876 | 118.9911 | -3.804 | 121.2021 | 121.1792 | 117.572 | -3.7994
2251.7812 | 121.3486 | -117.8055 | 3.4378 | 0.014267 | 0.0098822 | 0.0090427 | 0.0091836 | 0.0034009 | -0.0052594 | -0.004439 | -0.00068649 | -0.0062078 | -0.0024074 | 0.00035881 | -0.013044 | 0.019038 | 3.3508 | 1.5472 | 1.506 | 0.14191 | 3.4882 | 0.11902 | -0.027466 | 0.20142 | 0.15564 | 0.086975 | 3.4287 | 3.4241 | 0.018311 | -0.054932 | 117.9245 | 117.778 | 0.050354 | 119.3527 | 117.9474 | 0.16937 | -0.086975 | 117.8238 | 117.7505 | -0.009155 | 118.0069 | 117.8925 | 0.14191 | -0.013733 | 121.2936 | 121.1563 | 119.3115 | -3.4653 | 121.2341 | 121.2296 | 117.9611 | -3.4927
2253.5156 | 121.3486 | -118.0893 | 3.2043 | 0.014267 | 0.012232 | 0.0075473 | 0.0061928 | 0.0048963 | 0.002431 | -0.0046526 | 0.0069425 | 0.002337 | -0.0024074 | 0.00099981 | -0.0098395 | 0.017329 | 3.1494 | 0.93384 | 1.3412 | 0.1236 | 3.273 | 0.059509 | -0.10529 | 0.19226 | 0.10071 | -0.018311 | 3.1631 | 3.1906 | -0.018311 | -0.068665 | 118.1488 | 117.984 | 0.068664 | 119.0231 | 118.2129 | 0.22888 | -0.054932 | 118.071 | 118.0206 | -0.041199 | 118.2816 | 118.071 | 0.050354 | -0.013733 | 121.3623 | 121.2387 | 119.4305 | -3.3096 | 121.2524 | 121.2799 | 118.19 | -3.273
2255.2656 | 121.4584 | -118.1854 | 3.0624 | 0.0066373 | 0.012232 | 0.012033 | 0.0083292 | 0.0048963 | -0.0050458 | -0.0059344 | -0.00068649 | -0.0030034 | -0.0026212 | 0.00014521 | -0.014539 | 0.020961 | 3.0441 | 1.0345 | 1.3962 | 0.1831 | 3.1265 | 0.068665 | -0.064087 | 0.25635 | 0.23804 | 0.11902 | 3.0304 | 3.0396 | 0.004578 | -0.064087 | 118.2541 | 118.1213 | 0.064087 | 119.22 | 118.3685 | 0.24719 | -0.018311 | 118.19 | 118.1213 | -0.032043 | 118.4418 | 118.3044 | 0.18311 | -0.022888 | 121.312 | 121.2296 | 119.5816 | -3.1265 | 121.2158 | 121.225 | 118.4235 | -3.1265
2256.9688 | 121.3348 | -118.483 | 2.8564 | 0.014267 | 0.010737 | 0.0077609 | 0.0074746 | 0.0014783 | -0.00077324 | -0.00508 | -0.00068649 | -0.0027898 | -0.0024074 | 0.00057261 | -0.013471 | 0.019038 | 2.8244 | 0.90179 | 1.2909 | 0.16937 | 2.8931 | 0.064087 | -0.091553 | 0.25177 | 0.18768 | 0.07782 | 2.7924 | 2.7924 | 0.004578 | -0.064087 | 118.5471 | 118.3914 | 0.036621 | 119.3848 | 118.6523 | 0.26093 | -0.032043 | 118.4875 | 118.4189 | -0.064087 | 118.7347 | 118.5608 | 0.14191 | -0.064087 | 121.376 | 121.3074 | 119.7739 | -2.948 | 121.2753 | 121.2753 | 118.6707 | -2.9205
2258.6562 | 121.3623 | -118.7439 | 2.623 | 0.014267 | 0.0081732 | 0.0092563 | 0.002775 | 0.0038281 | 0.002431 | -0.0035846 | -0.008316 | -0.0034308 | -0.0047574 | -0.00070919 | -0.0083441 | 0.019893 | 2.5589 | 0.85602 | 1.1719 | 0.16479 | 2.6276 | 0.064087 | -0.07782 | 0.23804 | 0.17853 | 0.073242 | 2.5177 | 2.5314 | 0 | -0.045776 | 118.808 | 118.6661 | 0.004577 | 119.5999 | 118.9087 | 0.24261 | -0.064087 | 118.7439 | 118.6981 | -0.10529 | 118.9819 | 118.8171 | 0.11902 | -0.091553 | 121.3715 | 121.3028 | 119.9158 | -2.7008 | 121.2616 | 121.2753 | 118.9224 | -2.6688
2260.4062 | 121.0876 | -118.1946 | 2.5223 | 0.0066373 | 0.011164 | 0.0092563 | 0.0068338 | 0.0038281 | 0.0052082 | -0.0035846 | -0.00068649 | -0.0017218 | -0.0021938 | 0.00057261 | -0.0083441 | 0.018824 | 2.4765 | 1.1124 | 1.0483 | 0.1236 | 2.6184 | 0.018311 | -0.12817 | 0.20142 | 0.1236 | -0.022888 | 2.5223 | 2.5223 | -0.018311 | -0.10071 | 118.2129 | 118.0664 | 0.09613 | 119.3069 | 118.3182 | 0.25177 | -0.045777 | 118.1763 | 118.0939 | 0 | 118.396 | 118.1717 | 0.07782 | 0 | 120.813 | 120.6711 | 119.2429 | -2.6505 | 120.7169 | 120.7169 | 118.3182 | -2.623
2262.1562 | 121.2479 | -120.4971 | 0.45319 | -0.00099167 | 0.01095 | 0.0077609 | 0.005552 | 0.0031873 | -0.0041912 | -0.004439 | 0.0069425 | -0.0051398 | -0.0034756 | -0.003059 | -0.01283 | 0.022242 | 0.43488 | 0.21057 | 0.20142 | 0.15106 | 0.54016 | -0.027466 | -0.16479 | 0.091553 | 0.15564 | 0.050354 | 0.43945 | 0.43488 | -0.059509 | -0.12817 | 120.4697 | 120.3323 | 0.086975 | 120.7077 | 120.6482 | 0.31586 | -0.018311 | 120.4376 | 120.369 | -0.013733 | 120.5887 | 120.5475 | 0.17853 | -0.018311 | 121.0373 | 120.932 | 120.6985 | -0.61798 | 120.9366 | 120.932 | 120.6528 | -0.58136
2263.9062 | 121.2204 | -119.7327 | 1.3733 | 0.0066373 | 0.013087 | 0.0039157 | 0.0046976 | 0.00062386 | 0.0043536 | -0.0057208 | -0.00068649 | 0.00062796 | -0.004971 | 0.00035881 | -0.0070623 | 0.017756 | 1.3367 | 0.44403 | 0.53558 | 0.11444 | 1.4191 | -0.009155 | -0.16479 | 0.10071 | 0.07782 | -0.064087 | 1.3733 | 1.3687 | -0.050354 | -0.10986 | 119.7235 | 119.5679 | 0.045776 | 120.1767 | 119.8471 | 0.27924 | -0.036621 | 119.6823 | 119.6228 | 0 | 119.8334 | 119.6686 | 0.045776 | -0.004578 | 121.1517 | 121.0693 | 120.2682 | -1.5381 | 121.106 | 121.1014 | 119.8105 | -1.4832
2265.6094 | 121.1975 | -120.6162 | 0.60883 | 0.0066373 | 0.016505 | 0.0041293 | 0.0053384 | 0.0025465 | 0.0052082 | -0.001021 | -0.015945 | -0.002149 | -0.0017666 | 0.0018542 | -0.0083441 | 0.023097 | 0.48523 | 0.11902 | 0.14648 | 0.091553 | 0.64087 | -0.054932 | -0.19684 | -0.013733 | 0.004578 | -0.12817 | 0.58136 | 0.59052 | -0.086975 | -0.14191 | 120.5612 | 120.4193 | 0.032043 | 120.7352 | 120.7077 | 0.28839 | -0.1236 | 120.5292 | 120.4742 | -0.027466 | 120.6024 | 120.488 | 0.013733 | -0.018311 | 121.257 | 121.1014 | 120.7626 | -0.80566 | 121.1975 | 121.2067 | 120.6207 | -0.75073
2267.3594 | 121.3074 | -120.6985 | 0.48065 | -0.0086212 | 0.0086006 | 0.0054111 | 0.0091836 | 0.0036145 | -0.0052594 | -0.001021 | 0.0069425 | -0.003858 | -0.001553 | -0.0011364 | -0.013471 | 0.020747 | 0.41657 | 0.18768 | 0.23804 | 0.16022 | 0.54016 | -0.018311 | -0.16479 | 0.059509 | 0.14191 | 0.013733 | 0.43945 | 0.45319 | -0.050354 | -0.11902 | 120.6802 | 120.5338 | 0.059509 | 120.8862 | 120.8588 | 0.32501 | -0.064087 | 120.6482 | 120.5795 | -0.041199 | 120.7581 | 120.7123 | 0.13275 | -0.027466 | 121.2387 | 121.1151 | 120.9366 | -0.64545 | 121.138 | 121.1517 | 120.8405 | -0.59967
2269.1094 | 121.3486 | -120.7993 | 0.4303 | 0.0066373 | 0.013087 | 0.0045565 | 0.0042702 | 0.0048963 | 0.0032856 | -0.0029436 | 0.0069425 | 0.00020076 | -0.0039028 | 0.0018542 | -0.0094123 | 0.020747 | 0.35706 | 0.14191 | 0.1236 | 0.11444 | 0.53101 | -0.045776 | -0.20599 | 0.036621 | 0.064087 | -0.09613 | 0.42572 | 0.41657 | -0.068665 | -0.14191 | 120.7535 | 120.5933 | 0.10071 | 120.9412 | 120.9137 | 0.32044 | -0.073242 | 120.7306 | 120.6573 | -0.004578 | 120.8359 | 120.7031 | 0.045777 | -0.013733 | 121.3303 | 121.1563 | 120.9229 | -0.63629 | 121.225 | 121.2158 | 120.8633 | -0.57221
2270.8594 | 121.2708 | -120.9091 | 0.42572 | 0.0066373 | 0.015223 | 0.0037021 | 0.0081154 | 0.0025465 | 0.0049946 | -0.0012346 | 0.0069425 | -0.0017218 | -0.0013394 | 0.0018542 | -0.0096259 | 0.02032 | 0.32044 | 0.09613 | 0.10071 | 0.11444 | 0.48981 | -0.059509 | -0.20142 | 0 | 0.022888 | -0.12817 | 0.3891 | 0.3891 | -0.086975 | -0.15106 | 120.8496 | 120.7077 | 0.064087 | 121.0052 | 121.0236 | 0.31586 | -0.10528 | 120.8221 | 120.7581 | -0.036621 | 120.9091 | 120.7809 | 0.022888 | -0.036621 | 121.3989 | 121.2296 | 121.0098 | -0.62714 | 121.2982 | 121.2982 | 120.932 | -0.57678
2272.5469 | 121.2799 | -120.8954 | 0.42572 | 0.0066373 | 0.012659 | 0.0022067 | 0.0046976 | 0.0038281 | 0.002431 | -0.0023028 | 0.0069425 | -0.00065364 | -5.7632e-05 | 0.00035881 | -0.010267 | 0.020961 | 0.28381 | 0.059509 | 0.073242 | 0.086975 | 0.50354 | -0.059509 | -0.21515 | -0.013733 | -0.004578 | -0.13733 | 0.40741 | 0.3891 | -0.064087 | -0.15564 | 120.8359 | 120.6802 | 0.07782 | 120.9549 | 120.9824 | 0.30212 | -0.14191 | 120.8313 | 120.7397 | -0.01831 | 120.8817 | 120.7581 | 0.018311 | -0.036621 | 121.3989 | 121.1792 | 120.9686 | -0.64087 | 121.3028 | 121.2845 | 120.8908 | -0.58136
2274.2969 | 121.2936 | -120.8817 | 0.45776 | 0.0066373 | 0.012018 | 0.0037021 | 0.0057656 | 0.0025465 | 0.0028584 | -0.0018756 | 0.0069425 | -0.0027898 | -0.0021938 | 0.001427 | -0.010053 | 0.021174 | 0.26093 | 0.013733 | 0.050354 | 0.073242 | 0.53558 | -0.059509 | -0.22888 | -0.013733 | -0.004578 | -0.13733 | 0.41657 | 0.42114 | -0.10071 | -0.16479 | 120.8221 | 120.6528 | 0.077819 | 120.8954 | 120.9549 | 0.30212 | -0.19684 | 120.7809 | 120.7169 | -0.041199 | 120.8679 | 120.7443 | 0.027466 | -0.036621 | 121.4172 | 121.1426 | 120.932 | -0.68665 | 121.2982 | 121.3028 | 120.8771 | -0.62256
2275.9844 | 121.3028 | -120.9 | 0.42114 | -0.016251 | 0.0066778 | 0.0030611 | 0.0070474 | 0.0034009 | -0.0022686 | -0.0040118 | -0.008316 | -0.005567 | -0.0036892 | 0.00099981 | -0.011335 | 0.020961 | 0.34332 | 0.17853 | 0.20142 | 0.15564 | 0.44861 | -0.013733 | -0.16937 | 0.073242 | 0.14191 | 0.018311 | 0.36621 | 0.36621 | -0.054932 | -0.11444 | 120.8862 | 120.7306 | 0.027465 | 121.0785 | 121.0556 | 0.32501 | -0.07782 | 120.845 | 120.7855 | -0.054932 | 120.9732 | 120.9183 | 0.13275 | -0.054932 | 121.3486 | 121.2433 | 121.1014 | -0.59052 | 121.2662 | 121.2662 | 121.0419 | -0.53558
2277.6719 | 121.3577 | -120.8817 | 0.46234 | 0.021896 | 0.011591 | 0.0030611 | 0.0042702 | 0.0027601 | 0.0017902 | -0.004439 | 0.0069425 | -0.0027898 | -0.0028348 | -0.00092279 | -0.01048 | 0.022456 | 0.32959 | 0.07782 | 0.11444 | 0.091553 | 0.52643 | -0.022888 | -0.16937 | 0.064087 | 0.07782 | -0.022888 | 0.43488 | 0.41657 | -0.064087 | -0.11444 | 120.8588 | 120.7123 | 0.064087 | 120.9595 | 120.9732 | 0.26093 | -0.13275 | 120.8176 | 120.7672 | -0.027466 | 120.9457 | 120.8588 | 0.091553 | -0.045776 | 121.4081 | 121.2112 | 120.9961 | -0.63171 | 121.3165 | 121.2982 | 120.9595 | -0.57678
2279.4062 | 121.3715 | -120.8908 | 0.45776 | -0.00099167 | 0.0056098 | 0.0066927 | 0.0046976 | 0.0029737 | -0.0033368 | -0.0063616 | -0.008316 | -0.0062078 | -0.0041164 | -0.0041272 | -0.013258 | 0.023097 | 0.3479 | 0.10529 | 0.17853 | 0.11444 | 0.53558 | -0.022888 | -0.15564 | 0.045776 | 0.07782 | -0.009155 | 0.42114 | 0.40741 | -0.054932 | -0.10986 | 120.8679 | 120.7352 | 0.077819 | 120.9961 | 121.0052 | 0.27008 | -0.10986 | 120.8359 | 120.7809 | -0.036621 | 120.9366 | 120.8817 | 0.10071 | -0.050354 | 121.4264 | 121.2387 | 121.0693 | -0.6134 | 121.312 | 121.2982 | 120.9686 | -0.56763
2281.1562 | 121.2021 | -119.2474 | 1.593 | 0.0066373 | 0.012232 | 0.0064791 | 0.0068338 | 0.0053235 | 0.0073444 | -0.0082842 | 0.0069425 | -0.0023626 | -0.0021938 | -0.00070919 | -0.010267 | 0.018824 | 1.268 | 0.16022 | 0.54474 | 0.11444 | 1.4145 | -0.022888 | -0.17853 | 0.16022 | 0.10986 | -0.045776 | 1.2955 | 1.3046 | -0.022888 | -0.10529 | 119.2245 | 119.0689 | -0.17853 | 119.4077 | 119.3619 | 0.29297 | -0.32501 | 119.2245 | 119.1422 | -0.29755 | 119.4077 | 119.2017 | 0.05951 | -0.28839 | 120.6619 | 120.5154 | 119.7922 | -1.7715 | 120.5429 | 120.5521 | 119.3573 | -1.6983
2282.8438 | 121.3394 | -120.6162 | 0.45776 | 0.014267 | 0.015436 | 0.0049837 | 0.0083292 | 0.0034009 | 0.0039264 | -0.0040118 | -0.00068649 | -0.0019354 | -0.0026212 | 0.00057261 | -0.0083441 | 0.019679 | 0.39825 | 0.064087 | 0.17395 | 0.12817 | 0.53558 | -0.032043 | -0.17853 | 0.018311 | 0.073242 | -0.073242 | 0.44861 | 0.43945 | -0.073242 | -0.13733 | 120.5841 | 120.4376 | 0.077819 | 120.6802 | 120.7443 | 0.3067 | -0.05951 | 120.5429 | 120.4788 | -0.009156 | 120.6345 | 120.5429 | 0.064087 | -0.018311 | 121.1517 | 121.0144 | 120.7901 | -0.63629 | 121.0648 | 121.0556 | 120.6894 | -0.59509
2284.5938 | 121.3486 | -120.6665 | 0.48523 | -0.00099167 | 0.013941 | 0.0049837 | 0.0085428 | 0.0016919 | 0.002431 | -0.0040118 | -0.00068649 | -0.0030034 | -0.00027123 | -0.0011364 | -0.010053 | 0.019679 | 0.41199 | 0.073242 | 0.26093 | 0.11444 | 0.5722 | -0.032043 | -0.21515 | 0.045776 | 0.07782 | -0.064087 | 0.48065 | 0.46234 | -0.068665 | -0.1236 | 120.6345 | 120.4514 | 0.086976 | 120.7397 | 120.7809 | 0.32959 | -0.073242 | 120.5978 | 120.5429 | -0.004577 | 120.7123 | 120.6024 | 0.059509 | -0.022888 | 121.2387 | 121.0785 | 120.9274 | -0.70038 | 121.1472 | 121.1288 | 120.7443 | -0.60883
2286.2812 | 121.0648 | -2.092 | 118.5379 | 0.0066373 | 0.045557 | 0.28312 | 0.0068338 | 0.0055371 | -0.017222 | 0.01671 | 0.0069425 | 0.030108 | 0.44855 | 0.069573 | 0.00084167 | -0.057866 | 118.7439 | 18.869 | 38.2919 | 0.59509 | 119.0186 | 3.5248 | 3.4058 | 5.2734 | 4.6646 | 4.4586 | 118.895 | 118.9362 | 4.3716 | 4.3442 | 5.6168 | 5.4977 | 0.48065 | 20.961 | 2.6871 | -2.8107 | 0.20599 | 6.4636 | 6.4362 | 0.35706 | 7.3654 | 6.5506 | 0.11444 | 0.39825 | 121.1105 | 120.8359 | 40.3839 | -115.1321 | 120.9869 | 121.0281 | 6.7566 | -114.1937
2288.0312 | 121.2158 | -0.1831 | 120.4605 | -0.0086212 | 0.015436 | 0.054331 | 0.010893 | -1.714e-05 | 0.00072196 | -0.0059344 | 0.0069425 | -0.0036444 | 0.0093418 | -0.0032728 | -0.013685 | 0.022883 | -0.054932 | -0.027466 | -0.018311 | 0.045776 | 0.20142 | -0.10529 | -0.25635 | -0.091553 | -0.013733 | -0.15106 | 0.1236 | 0.09613 | -0.13733 | -0.19684 | 0.077819 | -0.073243 | -120.2591 | 0.15564 | 0.22888 | 0.30212 | -120.5154 | 0.045776 | -0.013733 | -120.3369 | 0.091552 | 0.032043 | 0.045776 | -120.3644 | 0.38452 | 0.12817 | 0.16479 | -120.7169 | 0.3067 | 0.27924 | 0.16937 | -120.6573
2289.7031 | 121.2662 | -0.14191 | 120.8679 | 0.0066373 | 0.009455 | 0.054544 | 0.0081154 | 0.0040417 | -0.005473 | -0.0072162 | 0.0069425 | -0.0068488 | 0.005283 | -0.0037 | -0.013044 | 0.021815 | 0.027466 | 0.091553 | 0.1236 | 0.1236 | 0.16937 | -0.045776 | -0.20599 | 0.013733 | 0.13275 | 0.018311 | 0.064087 | 0.059509 | -0.07782 | -0.14191 | 0.096131 | -0.064087 | -120.6985 | 0.23346 | 0.2655 | 0.32959 | -120.8405 | 0.064087 | 0 | -120.8038 | 0.15564 | 0.16022 | 0.16022 | -120.8084 | 0.31128 | 0.16937 | 0.2655 | -121.0739 | 0.20599 | 0.20142 | 0.27466 | -121.0098
2291.4688 | 116.7435 | -51.6174 | 64.4852 | 0.0066373 | 0.014368 | 0.053904 | 0.0049112 | 0.0029737 | -0.0050458 | -0.0074298 | 0.0069425 | -0.0044988 | 0.0050694 | -0.005409 | -0.011335 | 0.022029 | 0.018311 | 0.054932 | 0.068665 | 0.11902 | 0.16479 | -0.045776 | -0.16937 | 0.009155 | 0.11444 | 0.004578 | 0.086975 | 0.073242 | -0.07782 | -0.13733 | 51.5717 | 51.4481 | -64.3204 | 51.6724 | 51.7365 | 0.28839 | -64.4669 | 51.5396 | 51.4801 | -64.3982 | 51.6266 | 51.622 | 0.14191 | -64.4119 | 51.7822 | 51.6357 | 51.6861 | -64.6545 | 51.7044 | 51.6907 | 51.7319 | -64.6225
2293.1562 | 120.7443 | -0.89264 | 119.8746 | -0.00099167 | 0.011378 | 0.05369 | 0.0042702 | 0.0029737 | -0.0016278 | -0.0076434 | -0.008316 | -0.0036444 | 0.004642 | -0.0041272 | -0.0096259 | 0.02032 | 0.022888 | 0.073242 | 0.10071 | 0.09613 | 0.13733 | -0.050354 | -0.21515 | -0.009155 | 0.041199 | -0.045776 | 0.073242 | 0.073242 | -0.082397 | -0.14648 | 0.84228 | 0.67749 | -119.7372 | 0.96588 | 0.98877 | 0.31128 | -119.8517 | 0.81024 | 0.74615 | -119.8013 | 0.88348 | 0.84686 | 0.10071 | -119.8013 | 1.03 | 0.91553 | 0.99335 | -120.0897 | 0.96588 | 0.96588 | 0.93384 | -120.0211
2294.9062 | 120.9778 | -0.78735 | 120.0302 | 0.0066373 | 0.011164 | 0.05369 | 0.003843 | 0.0044691 | 0.0028584 | -0.0070026 | -0.00068649 | 0.0010554 | 0.006992 | -0.0045544 | -0.011121 | 0.019679 | -0.027466 | -0.045776 | -0.032043 | 0.036621 | 0.21973 | -0.091553 | -0.26093 | -0.082397 | -0.036621 | -0.14648 | 0.1236 | 0.10071 | -0.1236 | -0.18768 | 0.6958 | 0.52643 | -119.8105 | 0.74158 | 0.82398 | 0.29755 | -120.0577 | 0.66376 | 0.59967 | -119.9066 | 0.70496 | 0.64087 | 0.041199 | -119.9295 | 1.0071 | 0.75989 | 0.75531 | -120.2911 | 0.91095 | 0.88806 | 0.75073 | -120.2179
2296.6562 | 121.019 | -0.70496 | 120.2271 | -0.00099167 | 0.012446 | 0.05369 | 0.007261 | 0.0042555 | 0.001363 | -0.0048662 | -0.008316 | -0.0019354 | 0.0067782 | -0.003059 | -0.011976 | 0.020961 | -0.022888 | -0.036621 | 0.009155 | 0.045776 | 0.17853 | -0.09613 | -0.24719 | -0.091553 | -0.027466 | -0.14648 | 0.11902 | 0.10071 | -0.12817 | -0.19226 | 0.60883 | 0.45776 | -120.0485 | 0.66834 | 0.75073 | 0.29297 | -120.2499 | 0.57678 | 0.5127 | -120.108 | 0.6134 | 0.55847 | 0.045777 | -120.1263 | 0.88348 | 0.68207 | 0.71411 | -120.4742 | 0.82398 | 0.80566 | 0.67749 | -120.4193
2298.4062 | 120.5566 | -0.71411 | 120.3461 | 0.0066373 | 0.0075324 | 0.054972 | 0.0059792 | 0.0038281 | -0.0029094 | -0.0067888 | -0.00068649 | -0.0064214 | 0.0059238 | -0.0045544 | -0.013044 | 0.020533 | 0.018311 | 0.050354 | 0.091553 | 0.091553 | 0.16479 | -0.050354 | -0.20142 | -0.009155 | 0.036621 | -0.054932 | 0.073242 | 0.050354 | -0.091553 | -0.16479 | 0.66376 | 0.5127 | -120.1813 | 0.76447 | 0.80566 | 0.29297 | -120.3278 | 0.62256 | 0.54932 | -120.2728 | 0.70496 | 0.65918 | 0.10986 | -120.2957 | 0.87891 | 0.73242 | 0.80566 | -120.5475 | 0.78735 | 0.76447 | 0.75073 | -120.5109
2300.1562 | 120.726 | -0.737 | 120.314 | 0.0066373 | 0.012018 | 0.054544 | 0.0036294 | 0.0025465 | 0.0022174 | -0.0046526 | 0.0069425 | -0.0010808 | 0.0040012 | -0.0017774 | -0.0079169 | 0.019893 | 0.068665 | 0.054932 | 0.086975 | 0.1236 | 0.15564 | -0.041199 | -0.20142 | 0.050354 | 0.064087 | -0.032043 | 0.041199 | 0.036621 | -0.091553 | -0.13733 | 0.6958 | 0.53558 | -120.1584 | 0.79193 | 0.8606 | 0.32501 | -120.2454 | 0.64545 | 0.59967 | -120.2728 | 0.78735 | 0.70496 | 0.10529 | -120.2774 | 0.89264 | 0.80566 | 0.82398 | -120.5154 | 0.7782 | 0.77362 | 0.80109 | -120.4514
2301.9219 | 121.106 | -0.71411 | 120.3323 | -0.00099167 | 0.012659 | 0.051126 | 0.0057656 | 0.0040417 | -0.0014142 | -0.00508 | -0.008316 | -0.0023626 | 0.0074192 | -0.0034864 | -0.011335 | 0.021174 | 0.059509 | 0.09613 | 0.10529 | 0.12817 | 0.15106 | -0.064087 | -0.21057 | 0.009155 | 0.10529 | -0.032043 | 0.059509 | 0.054932 | -0.086975 | -0.15106 | 0.65002 | 0.50354 | -120.1813 | 0.81024 | 0.84229 | 0.33875 | -120.2728 | 0.62714 | 0.56305 | -120.2728 | 0.72327 | 0.68207 | 0.11902 | -120.2774 | 0.86517 | 0.77362 | 0.8194 | -120.5429 | 0.77362 | 0.76904 | 0.8194 | -120.4834
2303.6094 | 120.7718 | -0.67291 | 120.3461 | -0.00099167 | 0.0073188 | 0.055399 | 0.0051248 | 0.0044691 | -0.0033368 | -0.00508 | 0.0069425 | -0.0047124 | 0.0059238 | -0.0049816 | -0.011549 | 0.022456 | 0.004578 | 0.027466 | 0.068665 | 0.10529 | 0.17395 | -0.068665 | -0.21515 | 0.004578 | 0.073242 | -0.027466 | 0.064087 | 0.045776 | -0.07782 | -0.14648 | 0.60425 | 0.45776 | -120.1721 | 0.70038 | 0.7782 | 0.32044 | -120.3415 | 0.59509 | 0.52643 | -120.282 | 0.67749 | 0.64545 | 0.11902 | -120.3003 | 0.84686 | 0.67749 | 0.74158 | -120.5612 | 0.737 | 0.71869 | 0.74616 | -120.4926
2305.3594 | 121.0098 | -0.69122 | 120.3003 | 0.0066373 | 0.016077 | 0.052835 | 0.0074746 | 0.0034009 | 0.0037128 | -0.0037982 | -0.00068649 | -1.2844e-05 | 0.0089146 | -0.0043408 | -0.010694 | 0.018824 | 0.041199 | 0.013733 | 0.022888 | 0.09613 | 0.19226 | -0.068665 | -0.25177 | -0.013733 | 0.027466 | -0.11902 | 0.09613 | 0.073242 | -0.11444 | -0.17395 | 0.62256 | 0.43945 | -120.108 | 0.70496 | 0.78735 | 0.3479 | -120.2591 | 0.57678 | 0.51727 | -120.2042 | 0.67749 | 0.5722 | 0.054931 | -120.2271 | 0.88348 | 0.73242 | 0.71411 | -120.5521 | 0.78735 | 0.76447 | 0.71869 | -120.4742
2307.1094 | 120.3232 | -0.70496 | 120.0623 | 0.0066373 | 0.010737 | 0.054117 | 0.0019204 | 0.0025465 | 0.003072 | -0.0037982 | -0.00068649 | -0.00044004 | 0.0050694 | -0.0011364 | -0.0081305 | 0.021601 | -0.013733 | -0.059509 | -0.027466 | 0.027466 | 0.19684 | -0.07782 | -0.25177 | -0.064087 | -0.064087 | -0.14648 | 0.068665 | 0.07782 | -0.10986 | -0.17853 | 0.62714 | 0.45319 | -119.8654 | 0.64545 | 0.73242 | 0.27924 | -120.076 | 0.59509 | 0.52643 | -119.9936 | 0.64087 | 0.55847 | 0.032044 | -119.9844 | 0.90179 | 0.69122 | 0.67749 | -120.314 | 0.77362 | 0.78278 | 0.64087 | -120.2408
2308.7969 | 117.2974 | -0.72784 | 120.0897 | -0.00099167 | 0.011591 | 0.055399 | 0.0042702 | 0.0019055 | 0.0034992 | -0.0035846 | 0.0069425 | -0.0025762 | 0.0050694 | -0.001991 | -0.0091985 | 0.021601 | 0 | -0.022888 | 0 | 0.07782 | 0.1831 | -0.082397 | -0.2243 | 0.004578 | 0.027466 | -0.086975 | 0.068665 | 0.054932 | -0.10071 | -0.15564 | 0.64545 | 0.50354 | -119.9066 | 0.70496 | 0.80566 | 0.30212 | -120.0897 | 0.62714 | 0.5722 | -120.0211 | 0.73242 | 0.64087 | 0.068665 | -120.0348 | 0.91095 | 0.72784 | 0.72784 | -120.314 | 0.79651 | 0.78278 | 0.75531 | -120.2454
2310.5469 | 121.1929 | -0.70953 | 120.4514 | -0.00099167 | 0.010096 | 0.055826 | 0.0083292 | 0.0036145 | -0.0022686 | -0.0070026 | -0.00068649 | -0.0042852 | 0.0061374 | 0.00057261 | -0.014112 | 0.022029 | 0.041199 | 0.082397 | 0.086975 | 0.11444 | 0.15564 | -0.045776 | -0.21057 | -0.018311 | 0.068665 | -0.082397 | 0.064087 | 0.073242 | -0.09613 | -0.16022 | 0.66376 | 0.49896 | -120.2957 | 0.79193 | 0.82398 | 0.32501 | -120.4102 | 0.6134 | 0.54932 | -120.3873 | 0.69122 | 0.62714 | 0.07782 | -120.3781 | 0.86517 | 0.75073 | 0.79651 | -120.6619 | 0.77362 | 0.78278 | 0.7782 | -120.6116
2312.25 | 121.2204 | -0.71411 | 120.4376 | 0.0066373 | 0.013087 | 0.054972 | 0.0093972 | 0.00019646 | -0.00055964 | -0.0070026 | 0.0069425 | -0.0034308 | 0.0065646 | -0.0013502 | -0.014539 | 0.022029 | 0.036621 | 0.059509 | 0.07782 | 0.10986 | 0.15564 | -0.082397 | -0.21057 | -0.036621 | 0.041199 | -0.091553 | 0.059509 | 0.073242 | -0.10529 | -0.17395 | 0.63171 | 0.50354 | -120.282 | 0.77362 | 0.82397 | 0.32043 | -120.401 | 0.60883 | 0.54016 | -120.3781 | 0.67749 | 0.62256 | 0.082397 | -120.3644 | 0.86975 | 0.75073 | 0.79193 | -120.6482 | 0.77362 | 0.78735 | 0.75531 | -120.6116
2314 | 120.7993 | -0.74616 | 120.1447 | 0.0066373 | 0.013514 | 0.051767 | 0.0064066 | 0.0036145 | 0.004781 | -0.0035846 | 0.0069425 | -0.00086724 | 0.0074192 | -0.00092279 | -0.0083441 | 0.018184 | 0.018311 | 0.013733 | 0.009155 | 0.073242 | 0.16937 | -0.082397 | -0.21057 | -0.045776 | -0.027466 | -0.16479 | 0.086975 | 0.064087 | -0.11902 | -0.16479 | 0.66376 | 0.53558 | -119.9753 | 0.75989 | 0.8194 | 0.28381 | -120.1263 | 0.62714 | 0.58136 | -120.0577 | 0.70038 | 0.58136 | 0 | -120.0806 | 0.91553 | 0.76447 | 0.75531 | -120.3552 | 0.83313 | 0.81024 | 0.71869 | -120.3094
2315.75 | 120.6024 | -0.75531 | 120.3552 | -0.0086212 | 0.0073188 | 0.054972 | 0.0044838 | 0.0038281 | -0.0035504 | -0.0037982 | 0.0069425 | -0.006635 | 0.004642 | -0.0037 | -0.011762 | 0.022242 | -0.013733 | 0.045776 | 0.059509 | 0.086975 | 0.14648 | -0.054932 | -0.19226 | -0.013733 | 0.027466 | -0.054932 | 0.036621 | 0.041199 | -0.09613 | -0.15564 | 0.70038 | 0.56305 | -120.2087 | 0.80109 | 0.84229 | 0.27924 | -120.369 | 0.65918 | 0.59967 | -120.3186 | 0.74158 | 0.70038 | 0.10071 | -120.314 | 0.90179 | 0.74158 | 0.81482 | -120.5475 | 0.79193 | 0.79651 | 0.78278 | -120.5109
2317.5 | 120.4468 | -0.74158 | 120.3369 | -0.00099167 | 0.0062506 | 0.055185 | -0.00021575 | 0.0048963 | -0.0016278 | -0.0057208 | 0.0069425 | -0.005567 | 0.005283 | -0.004768 | -0.01048 | 0.021174 | 0.045776 | 0.07782 | 0.091553 | 0.10071 | 0.15106 | -0.045776 | -0.19226 | 0.004578 | 0.054932 | -0.032043 | 0.068665 | 0.054932 | -0.082397 | -0.14648 | 0.6958 | 0.54932 | -120.1859 | 0.8194 | 0.84229 | 0.29297 | -120.2911 | 0.65918 | 0.59509 | -120.2682 | 0.74616 | 0.70953 | 0.11444 | -120.282 | 0.89264 | 0.78735 | 0.83313 | -120.5292 | 0.81024 | 0.79651 | 0.79651 | -120.4834
2319.25 | 120.5658 | -0.72784 | 120.5475 | 0.0066373 | 0.015436 | 0.051767 | 0.0040566 | 0.0036145 | 0.00414 | -0.0063616 | -0.008316 | -0.0010808 | 0.005283 | 0.00014521 | -0.0087713 | 0.018824 | -0.018311 | -0.064087 | -0.050354 | 0.032043 | 0.19226 | -0.082397 | -0.24719 | -0.068665 | -0.059509 | -0.16022 | 0.086975 | 0.07782 | -0.11444 | -0.16937 | 0.64545 | 0.48065 | -120.3552 | 0.66376 | 0.75989 | 0.27924 | -120.5658 | 0.6134 | 0.55847 | -120.4605 | 0.65918 | 0.56763 | 0.009156 | -120.4697 | 0.92011 | 0.70953 | 0.67749 | -120.7947 | 0.81482 | 0.80566 | 0.66834 | -120.7169
2320.9531 | 121.2524 | -0.70038 | 120.5521 | 0.014267 | 0.0133 | 0.051767 | 0.0051248 | 0.0061781 | 0.0060626 | -0.0042254 | 0.014572 | 0.0010554 | 0.006992 | -0.0017774 | -0.0079169 | 0.019252 | 0.041199 | 0.022888 | 0.027466 | 0.09613 | 0.19684 | -0.086975 | -0.21973 | -0.032043 | 0.027466 | -0.14191 | 0.086975 | 0.082397 | -0.1236 | -0.16937 | 0.6134 | 0.48065 | -120.3552 | 0.72327 | 0.79651 | 0.31586 | -120.5109 | 0.57678 | 0.531 | -120.4651 | 0.66833 | 0.55847 | 0.027466 | -120.4697 | 0.89722 | 0.74158 | 0.72784 | -120.7718 | 0.78735 | 0.78277 | 0.72784 | -120.7214
2322.6406 | 120.8633 | -0.737 | 120.575 | -0.00099167 | 0.0133 | 0.054117 | 0.0044838 | 0.0046827 | 0.00414 | -0.0020892 | 0.0069425 | -0.0017218 | 0.0078464 | -0.0034864 | -0.0091985 | 0.021174 | -0.050354 | -0.082397 | -0.041199 | 0.050354 | 0.19684 | -0.082397 | -0.23804 | -0.073242 | -0.064087 | -0.15106 | 0.09613 | 0.086975 | -0.10986 | -0.16937 | 0.6546 | 0.49896 | -120.3781 | 0.6546 | 0.78735 | 0.28839 | -120.6253 | 0.62714 | 0.56763 | -120.4788 | 0.66376 | 0.58594 | 0.018311 | -120.488 | 0.93384 | 0.68665 | 0.6958 | -120.813 | 0.83313 | 0.82398 | 0.67291 | -120.7443
2324.3906 | 120.9549 | -0.75073 | 120.5795 | -0.0086212 | 0.012446 | 0.053904 | 0.0057656 | 0.0055371 | 0.0022174 | -0.0025164 | 0.014572 | -0.0017218 | 0.0059238 | -0.0011364 | -0.010053 | 0.022029 | -0.027466 | -0.073242 | -0.059509 | 0.032043 | 0.16479 | -0.086975 | -0.23804 | -0.082397 | -0.064087 | -0.16022 | 0.082397 | 0.073242 | -0.10986 | -0.1831 | 0.66376 | 0.51269 | -120.4147 | 0.67749 | 0.78277 | 0.27008 | -120.607 | 0.64087 | 0.56763 | -120.4971 | 0.66833 | 0.59051 | 0.022888 | -120.5063 | 0.91553 | 0.72327 | 0.69122 | -120.8176 | 0.83313 | 0.82397 | 0.68664 | -120.7626
2326.1406 | 121.3577 | -0.70038 | 120.5292 | -0.00099167 | 0.01565 | 0.050699 | 0.01132 | 0.0023327 | 0.0011494 | -0.0052936 | 0.014572 | -0.0019354 | 0.010624 | -0.00049559 | -0.01283 | 0.020747 | -0.054932 | -0.041199 | -0.045776 | 0.064087 | 0.18768 | -0.09613 | -0.24261 | -0.07782 | -0.018311 | -0.13275 | 0.09613 | 0.068665 | -0.11902 | -0.17395 | 0.60425 | 0.45776 | -120.3415 | 0.65918 | 0.76446 | 0.3067 | -120.5841 | 0.58136 | 0.52643 | -120.433 | 0.62256 | 0.56763 | 0.041199 | -120.4605 | 0.88806 | 0.64545 | 0.6546 | -120.7718 | 0.79651 | 0.76904 | 0.68207 | -120.7031
2327.8281 | 120.9503 | -0.737 | 120.4376 | 0.0066373 | 0.009455 | 0.051767 | 0.0059792 | 0.0021191 | -0.00077324 | -0.0020892 | 0.0069425 | -0.0059942 | 0.0054966 | -0.003059 | -0.0094123 | 0.019038 | 0.013733 | 0.032043 | 0.041199 | 0.11444 | 0.14648 | -0.045776 | -0.21057 | 0.027466 | 0.082397 | -0.036621 | 0.032043 | 0.054932 | -0.082397 | -0.14648 | 0.69122 | 0.52643 | -120.2911 | 0.76904 | 0.85144 | 0.32501 | -120.4239 | 0.6546 | 0.59052 | -120.4056 | 0.76447 | 0.70038 | 0.10986 | -120.3827 | 0.88348 | 0.75073 | 0.7782 | -120.6482 | 0.76904 | 0.79193 | 0.8194 | -120.5841
2329.5156 | 121.3531 | -0.70496 | 120.5612 | 0.0066373 | 0.013087 | 0.051554 | 0.0091836 | 0.0042555 | 8.1158e-05 | -0.0055072 | 0.014572 | -0.0012946 | 0.0084872 | -0.0017774 | -0.010694 | 0.022029 | -0.045776 | -0.059509 | -0.059509 | 0.050354 | 0.19226 | -0.082397 | -0.25635 | -0.07782 | -0.027466 | -0.15564 | 0.11444 | 0.082397 | -0.13275 | -0.20142 | 0.62256 | 0.44861 | -120.369 | 0.64545 | 0.75531 | 0.3067 | -120.607 | 0.57221 | 0.50354 | -120.4468 | 0.62714 | 0.54932 | 0.045776 | -120.4788 | 0.89722 | 0.65918 | 0.64545 | -120.8176 | 0.8194 | 0.78735 | 0.67749 | -120.7626
2331.2656 | 121.2479 | -0.75989 | 120.6024 | 0.014267 | 0.012446 | 0.052195 | 0.0053384 | 0.0034009 | 0.0020038 | -0.0057208 | 0.014572 | -0.00086724 | 0.0059238 | -0.00092279 | -0.0070623 | 0.021601 | -0.064087 | -0.091553 | -0.073242 | 0.036621 | 0.19226 | -0.068665 | -0.22888 | -0.086975 | -0.068665 | -0.1831 | 0.086975 | 0.10071 | -0.10529 | -0.19226 | 0.69122 | 0.53101 | -120.4102 | 0.66834 | 0.79651 | 0.2655 | -120.6665 | 0.6546 | 0.56763 | -120.5154 | 0.67291 | 0.57678 | 0.009156 | -120.5017 | 0.95215 | 0.6958 | 0.68665 | -120.8313 | 0.84686 | 0.8606 | 0.69122 | -120.7947
2333.0312 | 121.2891 | -0.72327 | 120.639 | -0.00099167 | 0.013727 | 0.051767 | 0.0044838 | 0.0040417 | 0.0032856 | -0.0029436 | 0.014572 | -0.0012946 | 0.0065646 | -0.0045544 | -0.010267 | 0.02032 | 0.036621 | 0.004578 | 0.013733 | 0.082397 | 0.1831 | -0.064087 | -0.21973 | -0.041199 | 0.004578 | -0.14191 | 0.09613 | 0.082397 | -0.086975 | -0.16479 | 0.65918 | 0.50354 | -120.4559 | 0.72784 | 0.80566 | 0.30212 | -120.6024 | 0.63629 | 0.55847 | -120.5429 | 0.68207 | 0.58136 | 0.022888 | -120.5566 | 0.90637 | 0.75989 | 0.737 | -120.8588 | 0.8194 | 0.80566 | 0.72784 | -120.8038
2334.7188 | 121.3623 | -0.71411 | 120.5566 | -0.00099167 | 0.013514 | 0.049417 | 0.0083292 | 0.0038281 | 0.0017902 | -0.0042254 | 0.022202 | -0.002149 | 0.0074192 | -0.003059 | -0.010053 | 0.020747 | 0.022888 | 0.013733 | 0.022888 | 0.082397 | 0.17395 | -0.091553 | -0.23346 | -0.032043 | 0.018311 | -0.11902 | 0.07782 | 0.091553 | -0.10529 | -0.17395 | 0.62256 | 0.48065 | -120.3827 | 0.72784 | 0.79651 | 0.31586 | -120.5338 | 0.60883 | 0.54016 | -120.4788 | 0.68207 | 0.59509 | 0.054931 | -120.4651 | 0.88806 | 0.737 | 0.737 | -120.7901 | 0.79193 | 0.80566 | 0.73242 | -120.7306
2336.4688 | 121.3989 | -0.72327 | 120.5521 | -0.00099167 | 0.0075324 | 0.055185 | 0.0085428 | 0.0014783 | -0.006541 | -0.0082842 | 0.0069425 | -0.0059942 | 0.008701 | -0.0013502 | -0.016248 | 0.022456 | 0.036621 | 0.10529 | 0.10529 | 0.13733 | 0.14191 | -0.045776 | -0.20599 | 0.009155 | 0.13733 | 0.027466 | 0.054932 | 0.045776 | -0.07782 | -0.14648 | 0.67749 | 0.51727 | -120.4102 | 0.82855 | 0.8606 | 0.34332 | -120.5154 | 0.64545 | 0.57678 | -120.4971 | 0.73242 | 0.75073 | 0.17395 | -120.5063 | 0.86517 | 0.75989 | 0.82855 | -120.7581 | 0.7782 | 0.76904 | 0.8606 | -120.6985
2338.2188 | 121.3348 | -0.78278 | 120.6162 | 0.0066373 | 0.011805 | 0.053263 | 0.0029886 | 0.0048963 | 0.00029476 | -0.0048662 | 0.014572 | -0.00086724 | 0.0044284 | -0.0049816 | -0.0094123 | 0.020533 | -0.032043 | -0.004578 | 0.004578 | 0.064087 | 0.19226 | -0.073242 | -0.20599 | -0.004578 | 0.013733 | -0.073242 | 0.054932 | 0.054932 | -0.082397 | -0.16937 | 0.70953 | 0.57678 | -120.4239 | 0.7782 | 0.84686 | 0.27008 | -120.6482 | 0.70038 | 0.6134 | -120.5612 | 0.7782 | 0.70953 | 0.096131 | -120.5612 | 0.97504 | 0.75073 | 0.78735 | -120.8221 | 0.83771 | 0.83771 | 0.79651 | -120.7855
2339.9688 | 121.3943 | -0.75989 | 120.5658 | -0.0086212 | 0.015864 | 0.052622 | 0.0061928 | 0.0023327 | 0.0052082 | -0.003371 | 0.014572 | -0.0010808 | 0.010837 | -0.0015638 | -0.0096259 | 0.018824 | 0.013733 | 0.027466 | 0.004578 | 0.086975 | 0.17853 | -0.068665 | -0.22888 | -0.027466 | 0.032043 | -0.11902 | 0.068665 | 0.068665 | -0.10071 | -0.16022 | 0.69122 | 0.53101 | -120.3873 | 0.78735 | 0.84686 | 0.31586 | -120.5521 | 0.65918 | 0.59967 | -120.4971 | 0.73242 | 0.64087 | 0.041198 | -120.4971 | 0.93842 | 0.77362 | 0.76447 | -120.7947 | 0.82855 | 0.82855 | 0.79193 | -120.726
2341.6562 | 121.4172 | -0.75531 | 120.5658 | -0.00099167 | 0.0098822 | 0.056894 | 0.0085428 | 0.0031873 | -0.0059002 | -0.0052936 | 0.0069425 | -0.0091986 | 0.0054966 | -0.0043408 | -0.013471 | 0.020747 | 0.013733 | 0.10071 | 0.09613 | 0.13275 | 0.16479 | -0.050354 | -0.19226 | 0.018311 | 0.10986 | 0.013733 | 0.045776 | 0.036621 | -0.082397 | -0.14191 | 0.70496 | 0.56305 | -120.401 | 0.85602 | 0.88806 | 0.32501 | -120.5521 | 0.67291 | 0.6134 | -120.52 | 0.77362 | 0.76904 | 0.15564 | -120.5292 | 0.92011 | 0.76904 | 0.85144 | -120.7581 | 0.80109 | 0.79193 | 0.86517 | -120.7077
2343.4219 | 121.2753 | -0.80109 | 120.5933 | -0.00099167 | 0.0092414 | 0.052835 | 0.0076882 | 0.00062386 | 0.00050836 | -0.00508 | 0.0069425 | -0.0049262 | 0.0065646 | -0.0034864 | -0.010908 | 0.021388 | 0.018311 | 0.073242 | 0.10071 | 0.10071 | 0.13733 | -0.036621 | -0.18768 | 0.009155 | 0.045776 | -0.032043 | 0.050354 | 0.045776 | -0.10071 | -0.14648 | 0.76446 | 0.6134 | -120.4559 | 0.87433 | 0.90179 | 0.28839 | -120.575 | 0.70038 | 0.6546 | -120.5429 | 0.81024 | 0.76904 | 0.11444 | -120.5475 | 0.93841 | 0.8194 | 0.90179 | -120.7809 | 0.85144 | 0.84686 | 0.84686 | -120.7397
2345.1719 | 121.3211 | -0.81024 | 120.6116 | 0.0066373 | 0.013514 | 0.050699 | 0.0044838 | 0.0027601 | 0.0054218 | -0.0029436 | 0.014572 | -0.0010808 | 0.0048556 | -0.0017774 | -0.0083441 | 0.019465 | -0.004578 | -0.018311 | -0.036621 | 0.045776 | 0.17395 | -0.086975 | -0.23346 | -0.059509 | -0.059509 | -0.16937 | 0.086975 | 0.07782 | -0.11902 | -0.17395 | 0.72327 | 0.57678 | -120.4376 | 0.79193 | 0.85602 | 0.27924 | -120.6161 | 0.69122 | 0.63629 | -120.5246 | 0.75073 | 0.64087 | 0.004577 | -120.5338 | 0.98419 | 0.80566 | 0.77362 | -120.845 | 0.89722 | 0.88806 | 0.75073 | -120.7855
2346.8594 | 121.376 | -0.80566 | 120.6253 | 0.014267 | 0.010523 | 0.050699 | 0.003843 | 0.0016919 | 0.001363 | -0.0040118 | -0.00068649 | -0.0040716 | 0.006992 | -0.001991 | -0.010053 | 0.020747 | -0.009155 | 0.009155 | 0.009155 | 0.082397 | 0.20142 | -0.050354 | -0.21057 | 0.013733 | 0.027466 | -0.059509 | 0.036621 | 0.059509 | -0.07782 | -0.12817 | 0.75531 | 0.59509 | -120.4239 | 0.81482 | 0.88806 | 0.29297 | -120.6345 | 0.72784 | 0.67749 | -120.5887 | 0.8194 | 0.74616 | 0.068665 | -120.5658 | 1.0071 | 0.79651 | 0.81482 | -120.8359 | 0.84229 | 0.86517 | 0.83313 | -120.7535
2348.6094 | 121.4127 | -0.76904 | 120.6024 | 0.014267 | 0.013087 | 0.05369 | 0.010038 | 0.0048963 | -0.0031232 | -0.0063616 | 0.014572 | -0.0053534 | 0.0067782 | -0.0037 | -0.013044 | 0.020961 | 0.018311 | 0.10986 | 0.10529 | 0.12817 | 0.15564 | -0.045776 | -0.19226 | 0.041199 | 0.10986 | -0.022888 | 0.054932 | 0.045776 | -0.10529 | -0.14191 | 0.72327 | 0.57678 | -120.4468 | 0.87891 | 0.89722 | 0.32044 | -120.5841 | 0.66376 | 0.62714 | -120.5475 | 0.81024 | 0.74616 | 0.11902 | -120.5566 | 0.92468 | 0.78735 | 0.87433 | -120.7947 | 0.82398 | 0.81482 | 0.87891 | -120.7443
2350.375 | 121.4584 | -0.75531 | 120.5475 | 0.0066373 | 0.011591 | 0.052408 | 0.0083292 | 0.0042555 | -0.0018414 | -0.0070026 | 0.0069425 | -0.0051398 | 0.006992 | -0.0039136 | -0.014326 | 0.019679 | 0.059509 | 0.13733 | 0.10986 | 0.13733 | 0.15564 | -0.036621 | -0.20142 | 0.013733 | 0.1236 | 0 | 0.050354 | 0.050354 | -0.073242 | -0.14191 | 0.71869 | 0.55389 | -120.3918 | 0.89264 | 0.89264 | 0.33875 | -120.488 | 0.68207 | 0.6134 | -120.4971 | 0.76904 | 0.75531 | 0.14191 | -120.4971 | 0.91095 | 0.81482 | 0.86517 | -120.7489 | 0.80566 | 0.80566 | 0.87891 | -120.6894
2352.0938 | 121.4584 | -0.76904 | 120.5658 | 0.0066373 | 0.010309 | 0.055185 | 0.0066202 | 0.0038281 | -0.0041912 | -0.0072162 | -0.00068649 | -0.0053534 | 0.0057102 | -0.0039136 | -0.013044 | 0.02032 | 0.073242 | 0.13275 | 0.10986 | 0.13275 | 0.14191 | -0.045776 | -0.20142 | 0.027466 | 0.11902 | -0.004578 | 0.050354 | 0.045776 | -0.073242 | -0.14191 | 0.72327 | 0.56763 | -120.4239 | 0.90179 | 0.90179 | 0.33417 | -120.4926 | 0.6958 | 0.62714 | -120.5154 | 0.79651 | 0.76447 | 0.13733 | -120.52 | 0.91095 | 0.84229 | 0.87891 | -120.7672 | 0.8194 | 0.81482 | 0.88806 | -120.7077
2353.8438 | 121.4813 | -0.78735 | 120.5887 | -0.00099167 | 0.013727 | 0.051126 | 0.005552 | 0.0021191 | 0.0054218 | -0.0052936 | -0.00068649 | 0.00084176 | 0.0072056 | -0.0011364 | -0.011121 | 0.016475 | 0.009155 | -0.004578 | -0.013733 | 0.086975 | 0.1831 | -0.07782 | -0.22888 | -0.009155 | 0.018311 | -0.13733 | 0.07782 | 0.050354 | -0.10071 | -0.1831 | 0.70953 | 0.55847 | -120.4056 | 0.78278 | 0.87433 | 0.31586 | -120.5795 | 0.68665 | 0.60425 | -120.5109 | 0.7782 | 0.65002 | 0.045776 | -120.5383 | 0.97046 | 0.79651 | 0.77362 | -120.8176 | 0.86517 | 0.83771 | 0.80566 | -120.7718
2355.5781 | 121.3943 | -0.8194 | 120.639 | 0.0066373 | 0.011591 | 0.054331 | 0.00021145 | 0.0029737 | 0.0026446 | -0.0018756 | 0.014572 | -0.0023626 | 0.0074192 | -0.0013502 | -0.0081305 | 0.019893 | -0.009155 | 0.009155 | -0.004578 | 0.068665 | 0.1831 | -0.059509 | -0.2243 | 0.018311 | 0.022888 | -0.059509 | 0.054932 | 0.045776 | -0.082397 | -0.15106 | 0.75989 | 0.59509 | -120.4559 | 0.82855 | 0.88806 | 0.29297 | -120.6482 | 0.737 | 0.66834 | -120.5841 | 0.83771 | 0.75989 | 0.091553 | -120.5933 | 1.0025 | 0.81024 | 0.81482 | -120.8633 | 0.87433 | 0.86517 | 0.84229 | -120.7901
2357.3281 | 121.3898 | -0.84228 | 120.639 | 0.0066373 | 0.01565 | 0.052835 | 0.0057656 | 0.0053235 | 0.00414 | -0.0020892 | 0.0069425 | 0.002978 | 0.0067782 | -0.0024182 | -0.0064215 | 0.020747 | 0.004578 | -0.004578 | 0 | 0.073242 | 0.16937 | -0.064087 | -0.2243 | -0.064087 | -0.022888 | -0.1831 | 0.09613 | 0.082397 | -0.10529 | -0.17853 | 0.7782 | 0.61798 | -120.4697 | 0.83771 | 0.91553 | 0.29755 | -120.6345 | 0.737 | 0.66376 | -120.5429 | 0.7782 | 0.65918 | -0.004577 | -120.5566 | 1.0117 | 0.84686 | 0.84228 | -120.8633 | 0.93841 | 0.92468 | 0.8194 | -120.8176
2359.0156 | 121.4722 | -0.80566 | 120.6207 | 0.0066373 | 0.012232 | 0.050699 | 0.0034158 | 0.0016919 | 0.0037128 | -0.0048662 | -0.00068649 | -0.0019354 | 0.008701 | -0.0028454 | -0.0098395 | 0.018611 | 0.013733 | 0.027466 | 0 | 0.07782 | 0.1831 | -0.068665 | -0.21973 | -0.018311 | 0.022888 | -0.11444 | 0.086975 | 0.059509 | -0.11902 | -0.15564 | 0.737 | 0.58594 | -120.4376 | 0.83313 | 0.88348 | 0.29755 | -120.607 | 0.68665 | 0.65002 | -120.5338 | 0.78735 | 0.69122 | 0.041199 | -120.5612 | 0.98877 | 0.8194 | 0.80566 | -120.8405 | 0.89264 | 0.86517 | 0.82855 | -120.7764
2360.7656 | 121.4172 | -0.85602 | 120.607 | 0.0066373 | 0.015009 | 0.052408 | 0.0051248 | 0.0036145 | 0.0020038 | -0.0031574 | 0.014572 | -0.0025762 | 0.0054966 | -0.0024182 | -0.0085577 | 0.023951 | -0.059509 | -0.059509 | -0.068665 | 0.050354 | 0.18768 | -0.082397 | -0.21973 | -0.068665 | -0.054932 | -0.15564 | 0.09613 | 0.07782 | -0.10986 | -0.17395 | 0.77362 | 0.63629 | -120.4193 | 0.79651 | 0.90637 | 0.27008 | -120.6665 | 0.74615 | 0.68207 | -120.5109 | 0.78735 | 0.70038 | 0.01831 | -120.5292 | 1.0437 | 0.79651 | 0.78735 | -120.8267 | 0.95215 | 0.93384 | 0.80109 | -120.7809
2362.5156 | 121.3806 | -0.85602 | 120.6207 | 0.0066373 | 0.0090278 | 0.051767 | 0.0044838 | 0.0012647 | -0.0014142 | -0.00508 | -0.00068649 | -0.0030034 | 0.003574 | -0.0017774 | -0.011762 | 0.021174 | 0.059509 | 0.059509 | 0.082397 | 0.12817 | 0.14191 | -0.032043 | -0.18768 | 0.041199 | 0.07782 | -0.018311 | 0.027466 | 0.036621 | -0.068665 | -0.13733 | 0.82397 | 0.66833 | -120.4788 | 0.91553 | 0.98419 | 0.31586 | -120.5612 | 0.78735 | 0.71869 | -120.5933 | 0.89722 | 0.83771 | 0.11902 | -120.5841 | 0.99792 | 0.91553 | 0.93841 | -120.8084 | 0.88348 | 0.89264 | 0.93384 | -120.7581
2364.2031 | 121.4813 | -0.8606 | 120.5795 | 0.0066373 | 0.012232 | 0.051981 | 0.005552 | 0.0034009 | 0.0022174 | -0.0055072 | 0.0069425 | -0.0025762 | 0.01041 | -0.00092279 | -0.010908 | 0.020961 | -0.022888 | -0.059509 | -0.009155 | 0.059509 | 0.1831 | -0.07782 | -0.23346 | -0.022888 | -0.004578 | -0.09613 | 0.073242 | 0.07782 | -0.09613 | -0.14191 | 0.78278 | 0.62714 | -120.3964 | 0.80109 | 0.92011 | 0.29297 | -120.6024 | 0.76447 | 0.71869 | -120.5063 | 0.83771 | 0.76447 | 0.045777 | -120.5017 | 1.0437 | 0.83771 | 0.85144 | -120.813 | 0.93384 | 0.93842 | 0.85602 | -120.7214
2365.9688 | 121.5729 | -0.83313 | 120.5612 | -0.0086212 | 0.014155 | 0.052835 | 0.010252 | 0.0025465 | 0.0022174 | -0.0048662 | 0.0069425 | -0.0019354 | 0.0084872 | -0.00070919 | -0.011335 | 0.018824 | -0.041199 | -0.036621 | -0.036621 | 0.073242 | 0.16937 | -0.091553 | -0.25177 | -0.050354 | 0.004578 | -0.1236 | 0.086975 | 0.068665 | -0.10986 | -0.1831 | 0.74158 | 0.58136 | -120.3918 | 0.79651 | 0.90637 | 0.32501 | -120.6024 | 0.72327 | 0.65003 | -120.4742 | 0.78278 | 0.70953 | 0.059509 | -120.4926 | 1.0025 | 0.79193 | 0.79651 | -120.813 | 0.92011 | 0.9018 | 0.83771 | -120.7443
2367.6719 | 121.4355 | -0.91095 | 120.5795 | -0.00099167 | 0.014582 | 0.052622 | 0.0049112 | 0.0036145 | 0.0045674 | -0.0029436 | 0.0069425 | -0.0030034 | 0.0089146 | -0.0017774 | -0.0096259 | 0.021174 | -0.073242 | -0.073242 | -0.054932 | 0.036621 | 0.1831 | -0.07782 | -0.21973 | -0.07782 | -0.082397 | -0.17853 | 0.091553 | 0.073242 | -0.1236 | -0.1831 | 0.83313 | 0.69122 | -120.3964 | 0.83771 | 0.94757 | 0.25635 | -120.6528 | 0.78735 | 0.72785 | -120.488 | 0.83313 | 0.73242 | 0.004577 | -120.5063 | 1.0941 | 0.83771 | 0.85602 | -120.7993 | 1.0025 | 0.98419 | 0.82855 | -120.7626
2369.4219 | 121.5225 | -0.90637 | 120.4971 | 0.0066373 | 0.012659 | 0.053263 | 0.007261 | 0.0029737 | -0.0050458 | -0.0059344 | 0.0069425 | -0.0062078 | 0.0076328 | -0.0041272 | -0.013044 | 0.021601 | 0 | 0.07782 | 0.086975 | 0.13275 | 0.16937 | -0.073242 | -0.21515 | -0.041199 | 0.082397 | -0.059509 | 0.073242 | 0.045776 | -0.10529 | -0.16937 | 0.83313 | 0.69122 | -120.3278 | 0.98419 | 1.0391 | 0.3479 | -120.4971 | 0.80109 | 0.737 | -120.4239 | 0.86517 | 0.84686 | 0.10986 | -120.4514 | 1.0757 | 0.90637 | 0.99335 | -120.7123 | 0.97961 | 0.95215 | 0.98877 | -120.6665
2371.1719 | 121.5225 | -0.90637 | 120.5475 | 0.014267 | 0.012873 | 0.05369 | 0.010465 | 0.0029737 | -0.0031232 | -0.0070026 | 0.0069425 | -0.0036444 | 0.0072056 | -0.0041272 | -0.011976 | 0.02032 | 0.018311 | 0.09613 | 0.082397 | 0.13275 | 0.14648 | -0.054932 | -0.21515 | -0.027466 | 0.082397 | -0.073242 | 0.068665 | 0.041199 | -0.10529 | -0.15564 | 0.85144 | 0.69122 | -120.401 | 1.0025 | 1.0391 | 0.3479 | -120.5292 | 0.80109 | 0.75073 | -120.4788 | 0.87891 | 0.83313 | 0.082398 | -120.5063 | 1.0529 | 0.92468 | 0.98877 | -120.7626 | 0.97504 | 0.94757 | 0.98877 | -120.7031
2372.8594 | 121.5088 | -0.90637 | 120.5475 | 0.0066373 | 0.010523 | 0.051981 | 0.0091836 | 0.00062386 | -0.00013244 | -0.00508 | 0.014572 | -0.0032172 | 0.0065646 | -0.0024182 | -0.011335 | 0.019679 | -0.036621 | -0.009155 | -0.022888 | 0.059509 | 0.18768 | -0.086975 | -0.24261 | -0.086975 | -0.022888 | -0.15564 | 0.086975 | 0.091553 | -0.13275 | -0.19226 | 0.8194 | 0.66376 | -120.3598 | 0.89722 | 0.96588 | 0.30212 | -120.5841 | 0.77362 | 0.71411 | -120.4605 | 0.8194 | 0.75073 | 0.036621 | -120.4559 | 1.0941 | 0.86975 | 0.88348 | -120.7901 | 0.99335 | 0.99792 | 0.88348 | -120.7397
2374.6094 | 121.4264 | -0.98419 | 120.5429 | 0.014267 | 0.0062506 | 0.053263 | 0.0049112 | 0.0027601 | -0.00055964 | -0.0072162 | -0.00068649 | -0.0034308 | 0.004642 | -0.0026318 | -0.011335 | 0.021174 | 0.036621 | 0.068665 | 0.07782 | 0.091553 | 0.13275 | -0.045776 | -0.17853 | -0.018311 | 0.032043 | -0.054932 | 0.059509 | 0.059509 | -0.073242 | -0.14191 | 0.93842 | 0.80566 | -120.4102 | 1.0529 | 1.0757 | 0.27008 | -120.5063 | 0.91095 | 0.84228 | -120.4834 | 0.96588 | 0.92926 | 0.086975 | -120.4834 | 1.1169 | 1.0208 | 1.062 | -120.7214 | 1.0437 | 1.0437 | 1.0162 | -120.6848
2376.2969 | 121.4264 | -0.99335 | 120.5383 | -0.00099167 | 0.010096 | 0.053049 | 0.0023476 | 0.0014783 | -0.00077324 | -0.0035846 | -0.00068649 | -0.0034308 | 0.002933 | -0.0041272 | -0.011335 | 0.019038 | 0.068665 | 0.082397 | 0.086975 | 0.14191 | 0.13733 | -0.022888 | -0.1831 | 0.050354 | 0.086975 | -0.022888 | 0.064087 | 0.054932 | -0.07782 | -0.15106 | 0.97046 | 0.81024 | -120.401 | 1.0757 | 1.1353 | 0.32501 | -120.4697 | 0.91553 | 0.84228 | -120.4742 | 1.0437 | 0.97046 | 0.12817 | -120.4834 | 1.1307 | 1.062 | 1.0803 | -120.7214 | 1.0574 | 1.0483 | 1.0803 | -120.6894
2378.0469 | 121.4676 | -1.2222 | 120.2042 | -0.00099167 | 0.013941 | 0.053263 | 0.0034158 | 0.0021191 | 0.0052082 | -0.0031574 | 0.014572 | -0.00022644 | 0.0074192 | -0.00092279 | -0.0081305 | 0.019465 | 0.032043 | 0 | -0.022888 | 0.073242 | 0.17853 | -0.07782 | -0.2243 | -0.036621 | -0.027466 | -0.16022 | 0.082397 | 0.07782 | -0.10071 | -0.16937 | 1.1444 | 0.99792 | -120.0256 | 1.2222 | 1.2955 | 0.29755 | -120.1721 | 1.1215 | 1.0529 | -120.1218 | 1.1856 | 1.062 | 0.009156 | -120.1263 | 1.4008 | 1.2543 | 1.1993 | -120.4285 | 1.3046 | 1.3 | 1.1948 | -120.3735
2379.7969 | 121.431 | -1.1536 | 120.3781 | -0.00099167 | 0.0064642 | 0.054544 | 0.0034158 | 0.0012647 | -0.0029094 | -0.0057208 | 0.0069425 | -0.0053534 | 0.0061374 | -0.00028199 | -0.011335 | 0.021601 | 0.027466 | 0.054932 | 0.054932 | 0.086975 | 0.14191 | -0.068665 | -0.20142 | -0.018311 | 0.041199 | -0.059509 | 0.073242 | 0.050354 | -0.086975 | -0.16022 | 1.0849 | 0.95215 | -120.2362 | 1.2085 | 1.2405 | 0.28839 | -120.3506 | 1.0666 | 0.99335 | -120.3049 | 1.1353 | 1.0941 | 0.10071 | -120.3278 | 1.2955 | 1.181 | 1.2085 | -120.5795 | 1.2268 | 1.2039 | 1.1948 | -120.5383
2381.5469 | 121.5179 | -1.268 | 120.2454 | -0.00099167 | 0.012232 | 0.05369 | 0.010679 | 0.0016919 | -0.00034604 | -0.0048662 | 0.0069425 | -0.0030034 | 0.0048556 | -0.0051954 | -0.01283 | 0.020106 | 0.064087 | 0.082397 | 0.082397 | 0.13275 | 0.15564 | -0.050354 | -0.17395 | 0.018311 | 0.082397 | -0.045776 | 0.07782 | 0.054932 | -0.086975 | -0.14191 | 1.2177 | 1.0941 | -120.0897 | 1.3504 | 1.4008 | 0.3067 | -120.1813 | 1.181 | 1.1261 | -120.1675 | 1.2863 | 1.2222 | 0.096131 | -120.1904 | 1.4236 | 1.3321 | 1.3504 | -120.4193 | 1.3458 | 1.3229 | 1.3504 | -120.3873
2383.3594 | 121.4676 | -1.2772 | 120.2728 | 0.0066373 | 0.015223 | 0.053049 | 0.0036294 | 0.0059643 | 0.0022174 | -0.00508 | 0.0069425 | -0.00086724 | 0.0057102 | -0.001991 | -0.0072759 | 0.019679 | 0.027466 | -0.032043 | -0.027466 | 0.064087 | 0.17395 | -0.07782 | -0.21515 | -0.050354 | -0.045776 | -0.17853 | 0.09613 | 0.068665 | -0.11444 | -0.16937 | 1.1993 | 1.062 | -120.0989 | 1.2451 | 1.3412 | 0.27924 | -120.2454 | 1.1627 | 1.1078 | -120.1767 | 1.2268 | 1.0986 | -0.009155 | -120.2042 | 1.4511 | 1.3046 | 1.2497 | -120.488 | 1.3733 | 1.3458 | 1.2314 | -120.4422
2385.0625 | 121.6095 | -1.2589 | 120.2271 | -0.00099167 | 0.015864 | 0.05134 | 0.0057656 | 0.0034009 | 0.0039264 | -0.00508 | -0.00068649 | -0.00086724 | 0.0091282 | -0.003059 | -0.0098395 | 0.018611 | -0.022888 | -0.036621 | -0.032043 | 0.064087 | 0.18768 | -0.082397 | -0.23804 | -0.073242 | 0 | -0.15106 | 0.082397 | 0.10071 | -0.10529 | -0.17395 | 1.1765 | 1.0208 | -120.0394 | 1.2222 | 1.3229 | 0.30212 | -120.2499 | 1.1536 | 1.0849 | -120.1447 | 1.1856 | 1.1078 | 0.022888 | -120.1263 | 1.4465 | 1.236 | 1.2268 | -120.4651 | 1.3412 | 1.3596 | 1.2589 | -120.401
2386.8438 | 121.5912 | -1.1032 | 120.3506 | -0.00099167 | 0.010737 | 0.055613 | 0.0081154 | 0.0014783 | -0.0063274 | -0.0065752 | 0.014572 | -0.0062078 | 0.006351 | -0.0024182 | -0.013471 | 0.022242 | 0 | 0.050354 | 0.073242 | 0.10529 | 0.15106 | -0.050354 | -0.21057 | 0.027466 | 0.086975 | -0.022888 | 0.045776 | 0.054932 | -0.068665 | -0.15106 | 1.0529 | 0.89264 | -120.1996 | 1.1536 | 1.2085 | 0.31586 | -120.3506 | 1.0345 | 0.95215 | -120.3049 | 1.1307 | 1.0803 | 0.12817 | -120.2957 | 1.2543 | 1.1032 | 1.1765 | -120.5612 | 1.149 | 1.1581 | 1.1902 | -120.5017
2388.625 | 117.1051 | -59.3079 | 57.5592 | -0.00099167 | 0.015436 | 0.054331 | 0.0068338 | 0.0038281 | 0.0062762 | -0.0052936 | 0.0069425 | -0.00065364 | 0.0082736 | -0.00028199 | -0.0091985 | 0.01797 | 0.050354 | 0.022888 | 0.032043 | 0.09613 | 0.20142 | -0.045776 | -0.19684 | 0.004578 | 0.036621 | -0.10071 | 0.086975 | 0.073242 | -0.091553 | -0.16022 | 59.2621 | 59.111 | -57.3578 | 59.3307 | 59.404 | 0.29297 | -57.5089 | 59.2163 | 59.1476 | -57.4722 | 59.3124 | 59.2072 | 0.059509 | -57.486 | 59.5093 | 59.3582 | 59.3399 | -57.756 | 59.3948 | 59.3811 | 59.3445 | -57.7194
2390.3281 | 120.2637 | -0.16937 | 120.0714 | 0.0066373 | 0.012659 | 0.052195 | 0.0085428 | 0.0040417 | -0.00055964 | -0.0040118 | -0.00068649 | -0.0034308 | 0.010837 | -0.0024182 | -0.012189 | 0.019679 | -0.004578 | 0.022888 | 0.032043 | 0.086975 | 0.17853 | -0.07782 | -0.21973 | -0.068665 | 0.018311 | -0.1236 | 0.09613 | 0.068665 | -0.1236 | -0.16479 | 0.091553 | -0.050354 | -119.8929 | 0.19226 | 0.25635 | 0.3067 | -120.076 | 0.045777 | 0.004578 | -119.9753 | 0.10071 | 0.045777 | 0.041199 | -120.0027 | 0.3479 | 0.16479 | 0.20142 | -120.2911 | 0.2655 | 0.23804 | 0.18768 | -120.2362
2392.0781 | 120.7031 | -0.14191 | 120.4468 | 0.014267 | 0.014582 | 0.055399 | 0.0074746 | 0.0029737 | -0.0048322 | -0.0055072 | 0.0069425 | -0.0074896 | 0.0057102 | -0.003059 | -0.011976 | 0.021388 | 0.045776 | 0.13275 | 0.1236 | 0.14648 | 0.14191 | -0.032043 | -0.18768 | 0.018311 | 0.12817 | 0 | 0.054932 | 0.054932 | -0.059509 | -0.15106 | 0.10986 | -0.045776 | -120.3049 | 0.27466 | 0.28839 | 0.33417 | -120.401 | 0.082398 | -0.009155 | -120.3918 | 0.16022 | 0.14191 | 0.15106 | -120.3918 | 0.28381 | 0.18768 | 0.2655 | -120.6345 | 0.19684 | 0.19684 | 0.27008 | -120.5978
2393.7812 | 120.8221 | -0.16022 | 120.52 | -0.00099167 | 0.013087 | 0.054972 | 0.0081154 | 0.0061781 | 0.0039264 | -0.0031574 | 0.0069425 | -0.0010808 | 0.0089146 | -0.0022046 | -0.0098395 | 0.01797 | -0.022888 | -0.018311 | -0.009155 | 0.07782 | 0.18768 | -0.086975 | -0.22888 | -0.027466 | 0.013733 | -0.12817 | 0.07782 | 0.091553 | -0.09613 | -0.17395 | 0.073242 | -0.068665 | -120.3323 | 0.14191 | 0.23804 | 0.3067 | -120.5429 | 0.064087 | -0.013733 | -120.4422 | 0.13275 | 0.032043 | 0.045776 | -120.4285 | 0.3479 | 0.13733 | 0.15106 | -120.7489 | 0.23804 | 0.25177 | 0.17395 | -120.694
2395.5625 | 120.8817 | -0.15106 | 120.5795 | -0.016251 | 0.009455 | 0.05369 | 0.007261 | 0.0029737 | -0.0041912 | -0.0042254 | 0.0069425 | -0.0064214 | 0.0050694 | -0.0015638 | -0.012189 | 0.020747 | 0.022888 | 0.10529 | 0.10529 | 0.1236 | 0.15106 | -0.054932 | -0.19226 | 0.041199 | 0.13733 | 0.004578 | 0.059509 | 0.032043 | -0.068665 | -0.13733 | 0.09613 | -0.041199 | -120.4285 | 0.25635 | 0.27466 | 0.31586 | -120.5566 | 0.082397 | 0.013733 | -120.52 | 0.19226 | 0.15564 | 0.14191 | -120.5475 | 0.30212 | 0.17395 | 0.25635 | -120.7718 | 0.21057 | 0.18311 | 0.28839 | -120.7169
2397.2656 | 120.7947 | -0.19226 | 120.6573 | 0.0066373 | 0.0083868 | 0.056253 | 0.0051248 | 0.0029737 | -0.0022686 | -0.006148 | 0.014572 | -0.0059942 | 0.0059238 | -0.0034864 | -0.0091985 | 0.021601 | 0.032043 | 0.086975 | 0.086975 | 0.091553 | 0.14191 | -0.032043 | -0.17853 | 0 | 0.036621 | -0.050354 | 0.054932 | 0.022888 | -0.086975 | -0.15106 | 0.16022 | 0.013733 | -120.5154 | 0.27924 | 0.28381 | 0.27008 | -120.6253 | 0.10529 | 0.041199 | -120.6024 | 0.19226 | 0.14191 | 0.10071 | -120.6345 | 0.33417 | 0.2243 | 0.27924 | -120.8359 | 0.24719 | 0.21515 | 0.22888 | -120.8084
2399.0312 | 120.9229 | -0.16022 | 120.6573 | -0.00099167 | 0.012446 | 0.055826 | 0.0070474 | 0.0038281 | -0.0012006 | -0.0057208 | -0.00068649 | -0.005567 | 0.0054966 | -0.0034864 | -0.01283 | 0.019893 | 0.054932 | 0.12817 | 0.10529 | 0.13733 | 0.13733 | -0.041199 | -0.17853 | 0.036621 | 0.13275 | -0.018311 | 0.059509 | 0.032043 | -0.07782 | -0.14648 | 0.11902 | -0.018311 | -120.52 | 0.28839 | 0.29755 | 0.31586 | -120.6024 | 0.082397 | 0.013733 | -120.5978 | 0.19684 | 0.14191 | 0.12817 | -120.6253 | 0.29755 | 0.21515 | 0.2655 | -120.8359 | 0.21973 | 0.19226 | 0.29297 | -120.8038
2400.7188 | 120.9824 | -0.14191 | 120.694 | -0.0086212 | 0.0088142 | 0.05369 | 0.0044838 | 0.0027601 | -0.0031232 | -0.0046526 | 0.014572 | -0.005567 | 0.008701 | -0.0034864 | -0.01283 | 0.020533 | 0.036621 | 0.091553 | 0.082397 | 0.11902 | 0.14191 | -0.054932 | -0.18768 | 0.036621 | 0.091553 | 0.009155 | 0.054932 | 0.036621 | -0.10071 | -0.15106 | 0.086975 | -0.045776 | -120.5521 | 0.23346 | 0.26093 | 0.3067 | -120.6573 | 0.041199 | -0.009155 | -120.639 | 0.17853 | 0.15106 | 0.16022 | -120.6573 | 0.28381 | 0.17853 | 0.2243 | -120.8817 | 0.19684 | 0.17853 | 0.23346 | -120.845
2402.4688 | 121.0007 | -0.18768 | 120.7169 | 0.014267 | 0.012446 | 0.055826 | 0.010465 | 0.0040417 | 0.0032856 | -0.0059344 | 0.0069425 | -0.00044004 | 0.00806 | -0.001991 | -0.011762 | 0.019893 | -0.054932 | -0.018311 | -0.045776 | 0.041199 | 0.19226 | -0.082397 | -0.23804 | -0.064087 | -0.027466 | -0.15564 | 0.10529 | 0.082397 | -0.11444 | -0.18768 | 0.10529 | -0.050354 | -120.5246 | 0.16937 | 0.22888 | 0.27924 | -120.7718 | 0.073242 | 0 | -120.6116 | 0.1236 | 0.032043 | 0.032043 | -120.6345 | 0.37994 | 0.13275 | 0.14191 | -120.9549 | 0.29297 | 0.27008 | 0.16022 | -120.9045
2404.2188 | 121.0648 | -0.15564 | 120.7443 | -0.00099167 | 0.013087 | 0.053904 | 0.00897 | 0.0036145 | 0.0043536 | -0.003371 | 0.0069425 | -0.0015082 | 0.0078464 | -0.0011364 | -0.0098395 | 0.019038 | -0.059509 | -0.045776 | -0.045776 | 0.064087 | 0.16479 | -0.082397 | -0.23346 | -0.045776 | -0.009155 | -0.15106 | 0.10529 | 0.086975 | -0.13275 | -0.1831 | 0.073243 | -0.077819 | -120.5795 | 0.10986 | 0.21973 | 0.29755 | -120.8038 | 0.022889 | -0.027465 | -120.639 | 0.10986 | 0.004578 | 0.032043 | -120.6573 | 0.32044 | 0.096131 | 0.10986 | -120.9778 | 0.26093 | 0.24261 | 0.14649 | -120.9274
2405.9062 | 120.9274 | -0.21515 | 120.813 | -0.00099167 | 0.0133 | 0.053476 | 0.0044838 | 0.0051099 | -0.0018414 | -0.0052936 | 0.014572 | -0.0053534 | 0.005283 | -0.0039136 | -0.0094123 | 0.020747 | 0.032043 | 0.09613 | 0.086975 | 0.11444 | 0.13275 | -0.050354 | -0.19684 | 0.022888 | 0.07782 | -0.032043 | 0.050354 | 0.032043 | -0.082397 | -0.16022 | 0.16479 | 0.018311 | -120.6802 | 0.31128 | 0.32959 | 0.31128 | -120.7809 | 0.13275 | 0.054932 | -120.7626 | 0.23804 | 0.18311 | 0.12817 | -120.7809 | 0.3479 | 0.24719 | 0.30212 | -121.0098 | 0.2655 | 0.24719 | 0.29297 | -120.9732
2407.6562 | 120.9732 | -0.20599 | 120.8771 | 0.0066373 | 0.013514 | 0.050486 | 0.003843 | 0.0059643 | 0.0043536 | -0.0035846 | 0.0069425 | -0.00065364 | 0.0099826 | -0.001991 | -0.0081305 | 0.020533 | -0.07782 | -0.07782 | -0.068665 | 0.022888 | 0.20599 | -0.064087 | -0.23346 | -0.050354 | -0.073242 | -0.17853 | 0.082397 | 0.068665 | -0.10529 | -0.17395 | 0.14191 | -0.027465 | -120.6711 | 0.12817 | 0.22888 | 0.25635 | -120.9549 | 0.10071 | 0.032044 | -120.7947 | 0.15564 | 0.027466 | -0.004578 | -120.8084 | 0.41199 | 0.12817 | 0.13733 | -121.1105 | 0.28839 | 0.27466 | 0.13275 | -121.051
2409.4062 | 120.9778 | -0.20142 | 120.8633 | -0.00099167 | 0.011164 | 0.051554 | 0.0046976 | 0.0051099 | -0.002055 | -0.0037982 | -0.00068649 | -0.0044988 | 0.0072056 | -0.00049559 | -0.010908 | 0.020106 | 0.032043 | 0.12817 | 0.11444 | 0.11444 | 0.12817 | -0.045776 | -0.17395 | 0.022888 | 0.07782 | -0.041199 | 0.059509 | 0.032043 | -0.068665 | -0.14191 | 0.15564 | 0.027466 | -120.7352 | 0.32959 | 0.31586 | 0.28839 | -120.8313 | 0.13275 | 0.059509 | -120.8038 | 0.2243 | 0.16022 | 0.10071 | -120.8313 | 0.32959 | 0.23346 | 0.31586 | -121.0373 | 0.26093 | 0.23346 | 0.27924 | -121.0052
2411.1562 | 121.0602 | -0.19226 | 120.8771 | -0.0086212 | 0.010737 | 0.051767 | 0.0036294 | 0.0059643 | 0.0028584 | -0.0042254 | 0.0069425 | -0.00044004 | 0.0074192 | -0.0011364 | -0.0085577 | 0.019465 | -0.018311 | -0.027466 | -0.018311 | 0.068665 | 0.1831 | -0.059509 | -0.21057 | 0.009155 | 0.022888 | -0.10071 | 0.068665 | 0.050354 | -0.10986 | -0.14648 | 0.13275 | -0.01831 | -120.694 | 0.16479 | 0.26093 | 0.27924 | -120.8954 | 0.082398 | 0.045777 | -120.8084 | 0.20142 | 0.091553 | 0.045776 | -120.8267 | 0.37537 | 0.17395 | 0.17395 | -121.0876 | 0.26093 | 0.24261 | 0.21515 | -121.0236
2412.8594 | 121.1472 | -0.15564 | 120.8496 | 0.014267 | 0.011164 | 0.053049 | 0.0046976 | 0.0044691 | 0.0032856 | -0.0037982 | -0.00068649 | -0.0027898 | 0.0065646 | -0.0017774 | -0.0085577 | 0.019679 | -0.041199 | -0.036621 | -0.032043 | 0.054932 | 0.17395 | -0.091553 | -0.22888 | -0.050354 | -0.004578 | -0.14191 | 0.082397 | 0.07782 | -0.12817 | -0.16937 | 0.064087 | -0.073242 | -120.6757 | 0.11902 | 0.21057 | 0.28381 | -120.8908 | 0.027466 | -0.013733 | -120.7672 | 0.10529 | 0.013733 | 0.027466 | -120.7718 | 0.32959 | 0.11444 | 0.1236 | -121.0785 | 0.23804 | 0.23346 | 0.15106 | -121.019
2414.625 | 121.1426 | -0.25177 | 120.7764 | 0.0066373 | 0.010096 | 0.053904 | 0.0087564 | 0.0027601 | -0.0044048 | -0.0048662 | 0.0069425 | -0.0053534 | 0.006351 | -0.0013502 | -0.01283 | 0.019679 | -0.018311 | 0.036621 | 0.054932 | 0.10529 | 0.16022 | -0.041199 | -0.20599 | 0.009155 | 0.073242 | -0.018311 | 0.050354 | 0.059509 | -0.086975 | -0.14648 | 0.21057 | 0.045776 | -120.6161 | 0.28839 | 0.35706 | 0.31128 | -120.7947 | 0.16479 | 0.10529 | -120.726 | 0.26093 | 0.23346 | 0.12817 | -120.7169 | 0.41199 | 0.23346 | 0.3067 | -120.9824 | 0.30212 | 0.31128 | 0.32501 | -120.9229
2416.375 | 121.0602 | -0.29755 | 120.8405 | 0.0066373 | 0.014155 | 0.051554 | 0.0040566 | 0.0036145 | 0.0069172 | -0.0057208 | 0.014572 | -0.00086724 | 0.0074192 | -0.0013502 | -0.0070623 | 0.020533 | -0.036621 | -0.068665 | -0.064087 | 0.041199 | 0.19226 | -0.082397 | -0.22888 | -0.07782 | -0.082397 | -0.19684 | 0.091553 | 0.073242 | -0.10071 | -0.16022 | 0.21515 | 0.068664 | -120.6482 | 0.22888 | 0.33874 | 0.27008 | -120.8771 | 0.19684 | 0.13733 | -120.7489 | 0.21973 | 0.10071 | -0.036621 | -120.7672 | 0.48981 | 0.26092 | 0.23346 | -121.0693 | 0.3891 | 0.37079 | 0.21515 | -121.0007
2418.125 | 121.0693 | -0.31586 | 120.845 | 0.014267 | 0.011805 | 0.053263 | 0.0046976 | 0.0036145 | 0.0039264 | -0.00273 | 0.0069425 | -0.00022644 | 0.0074192 | -0.0022046 | -0.0083441 | 0.019252 | -0.050354 | -0.054932 | -0.064087 | 0.059509 | 0.17395 | -0.068665 | -0.22888 | -0.082397 | -0.059509 | -0.19684 | 0.09613 | 0.073242 | -0.11902 | -0.15106 | 0.24719 | 0.086975 | -120.6711 | 0.26093 | 0.37537 | 0.28839 | -120.8954 | 0.19684 | 0.16479 | -120.7489 | 0.23346 | 0.11902 | -0.045776 | -120.7718 | 0.48981 | 0.2655 | 0.25177 | -121.0739 | 0.41199 | 0.3891 | 0.25635 | -120.9961
2419.8125 | 121.1884 | -0.24261 | 120.845 | -0.00099167 | 0.013727 | 0.052195 | 0.007261 | 0.0053235 | 0.0026446 | -0.0046526 | -0.00068649 | -0.0012946 | 0.00806 | -0.00070919 | -0.010053 | 0.021601 | -0.004578 | 0.018311 | 0.004578 | 0.07782 | 0.17395 | -0.07782 | -0.22888 | -0.022888 | 0.036621 | -0.11444 | 0.068665 | 0.059509 | -0.09613 | -0.16022 | 0.16479 | 0.013733 | -120.6711 | 0.26093 | 0.32044 | 0.3067 | -120.8496 | 0.14649 | 0.082398 | -120.7764 | 0.21973 | 0.12817 | 0.045776 | -120.7855 | 0.41656 | 0.23804 | 0.24719 | -121.0739 | 0.31128 | 0.30212 | 0.27924 | -121.0052
2421.5625 | 120.3644 | -0.17395 | 120.1492 | -0.00099167 | 0.0075324 | 0.05839 | 0.0079018 | 0.0023327 | -0.0076092 | -0.0048662 | -0.00068649 | -0.0068488 | 0.0054966 | -0.0017774 | -0.013898 | 0.020747 | -0.050354 | 0.018311 | 0.045776 | 0.086975 | 0.16022 | -0.050354 | -0.21057 | -0.027466 | 0.041199 | -0.050354 | 0.059509 | 0.045776 | -0.082397 | -0.14648 | 0.1236 | -0.036621 | -119.989 | 0.19226 | 0.26092 | 0.29755 | -120.1996 | 0.091553 | 0.027466 | -120.0897 | 0.14648 | 0.1236 | 0.09613 | -120.1035 | 0.33417 | 0.1236 | 0.21973 | -120.3598 | 0.23346 | 0.21973 | 0.21515 | -120.2957
2423.3125 | 120.5795 | -0.1831 | 120.4376 | 0.0066373 | 0.0081732 | 0.056894 | 0.0057656 | 0.0034009 | -0.0041912 | -0.0057208 | -0.00068649 | -0.0049262 | 0.0042148 | -0.0022046 | -0.011976 | 0.021601 | -0.036621 | 0.018311 | 0.032043 | 0.082397 | 0.13275 | -0.036621 | -0.19226 | -0.013733 | 0.032043 | -0.050354 | 0.07782 | 0.041199 | -0.09613 | -0.14191 | 0.14648 | -0.009156 | -120.3049 | 0.20142 | 0.2655 | 0.27466 | -120.4742 | 0.086975 | 0.041198 | -120.3598 | 0.16937 | 0.13275 | 0.091553 | -120.3964 | 0.31586 | 0.14648 | 0.21515 | -120.6299 | 0.26092 | 0.2243 | 0.21515 | -120.5795
2425.0625 | 120.6757 | -0.19684 | 120.5063 | -0.0086212 | 0.012659 | 0.053263 | 0.0036294 | 0.0021191 | 0.0037128 | -0.00273 | -0.00068649 | 0.00062796 | 0.0076328 | -0.0011364 | -0.0059943 | 0.019893 | 0.045776 | 0.032043 | 0.009155 | 0.09613 | 0.17395 | -0.07782 | -0.2243 | -0.027466 | 0.013733 | -0.1236 | 0.086975 | 0.068665 | -0.11444 | -0.15106 | 0.11902 | -0.027466 | -120.3323 | 0.22888 | 0.29297 | 0.32043 | -120.4605 | 0.082397 | 0.045776 | -120.4193 | 0.16937 | 0.073242 | 0.027466 | -120.4376 | 0.37079 | 0.24261 | 0.20599 | -120.7306 | 0.28381 | 0.2655 | 0.21057 | -120.6573
2426.7656 | 120.6894 | -0.21057 | 120.6024 | 0.0066373 | 0.012232 | 0.053049 | 0.005552 | 0.0036145 | 0.0045674 | -0.0042254 | 0.0069425 | -0.0017218 | 0.006351 | 0.0012134 | -0.0098395 | 0.019038 | 0.013733 | -0.009155 | -0.027466 | 0.073242 | 0.17395 | -0.07782 | -0.22888 | -0.050354 | -0.027466 | -0.17853 | 0.07782 | 0.07782 | -0.11444 | -0.17395 | 0.13275 | -0.018311 | -120.4285 | 0.20142 | 0.28381 | 0.30212 | -120.5887 | 0.09613 | 0.036621 | -120.5246 | 0.16022 | 0.032043 | -0.004578 | -120.5246 | 0.38452 | 0.2243 | 0.18311 | -120.8313 | 0.28839 | 0.28839 | 0.18311 | -120.7764
2428.5312 | 120.7855 | -0.17853 | 120.6162 | 0.0066373 | 0.0081732 | 0.054758 | 0.0059792 | 0.0036145 | -0.0041912 | -0.004439 | 0.0069425 | -0.0070624 | 0.0067782 | -0.0032728 | -0.011549 | 0.022242 | -0.032043 | 0.013733 | 0.032043 | 0.091553 | 0.16022 | -0.050354 | -0.21515 | -0.018311 | 0.050354 | -0.054932 | 0.064087 | 0.068665 | -0.086975 | -0.16479 | 0.12817 | -0.036621 | -120.4559 | 0.19226 | 0.27008 | 0.3067 | -120.6482 | 0.091553 | 0.013733 | -120.5521 | 0.16022 | 0.1236 | 0.10986 | -120.5475 | 0.33874 | 0.14648 | 0.21057 | -120.8313 | 0.24261 | 0.24719 | 0.22888 | -120.7809
2430.2812 | 120.9 | -0.16022 | 120.6619 | 0.0066373 | 0.012232 | 0.053476 | 0.00897 | 0.0036145 | -0.00013244 | -0.00508 | -0.008316 | 0.00020076 | 0.0076328 | -0.0022046 | -0.010053 | 0.019893 | -0.027466 | -0.059509 | -0.064087 | 0.050354 | 0.19684 | -0.07782 | -0.23804 | -0.073242 | -0.027466 | -0.15564 | 0.10071 | 0.09613 | -0.11902 | -0.17853 | 0.082397 | -0.07782 | -120.4651 | 0.10071 | 0.21057 | 0.28839 | -120.6894 | 0.041198 | -0.018311 | -120.5612 | 0.086975 | 0.004577 | 0.022888 | -120.5658 | 0.35706 | 0.13275 | 0.09613 | -120.9 | 0.26093 | 0.25635 | 0.13275 | -120.8405
2431.9844 | 120.3049 | -0.20142 | 120.1675 | -0.0086212 | 0.01095 | 0.052195 | 0.005552 | 0.0027601 | 0.0049946 | -0.0035846 | -0.00068649 | -0.00065364 | 0.0084872 | -0.00049559 | -0.0074897 | 0.019679 | -0.059509 | -0.091553 | -0.07782 | 0.036621 | 0.20142 | -0.064087 | -0.2243 | -0.082397 | -0.068665 | -0.17853 | 0.082397 | 0.086975 | -0.11444 | -0.1831 | 0.13733 | -0.022888 | -119.9661 | 0.10986 | 0.23804 | 0.26093 | -120.2271 | 0.086975 | 0.018311 | -120.0851 | 0.11902 | 0.022888 | 0.004577 | -120.0806 | 0.40283 | 0.14191 | 0.1236 | -120.3918 | 0.28381 | 0.28839 | 0.13275 | -120.3506
2433.6875 | 120.6619 | -0.15106 | 120.3964 | -0.0086212 | 0.011378 | 0.054117 | 0.0085428 | 0.0051099 | -0.005473 | -0.00508 | 0.0069425 | -0.0068488 | 0.006351 | -0.003059 | -0.01518 | 0.019893 | 0.022888 | 0.09613 | 0.09613 | 0.12817 | 0.15106 | -0.045776 | -0.20599 | 0.041199 | 0.12817 | 0.004578 | 0.050354 | 0.032043 | -0.068665 | -0.1236 | 0.10529 | -0.054932 | -120.2454 | 0.24719 | 0.27924 | 0.33417 | -120.3735 | 0.082397 | 0.027466 | -120.3461 | 0.19226 | 0.15564 | 0.12817 | -120.3644 | 0.30212 | 0.17395 | 0.24719 | -120.6024 | 0.20142 | 0.18311 | 0.27924 | -120.52
2435.4375 | 120.7443 | -0.15106 | 120.4834 | -0.00099167 | 0.016077 | 0.055185 | 0.005552 | -1.714e-05 | 0.0032856 | -0.0048662 | -0.00068649 | -0.00022644 | 0.0076328 | -0.0013502 | -0.0085577 | 0.018611 | 0.009155 | -0.032043 | -0.013733 | 0.07782 | 0.1831 | -0.07782 | -0.21973 | -0.027466 | 0.009155 | -0.12817 | 0.10071 | 0.07782 | -0.10071 | -0.16022 | 0.073242 | -0.068665 | -120.3003 | 0.11902 | 0.22888 | 0.29755 | -120.4742 | 0.050354 | -0.009155 | -120.3827 | 0.1236 | 0.022888 | 0.032043 | -120.4056 | 0.33417 | 0.16022 | 0.13733 | -120.7031 | 0.25177 | 0.22888 | 0.16022 | -120.6436
2437.1406 | 120.7443 | -0.16937 | 120.5338 | -0.0086212 | 0.011591 | 0.053476 | 0.0070474 | 0.0031873 | -0.0024822 | -0.0046526 | 0.0069425 | -0.0034308 | 0.0078464 | -0.0022046 | -0.013685 | 0.020533 | 0 | 0.041199 | 0.036621 | 0.09613 | 0.16479 | -0.064087 | -0.20599 | -0.068665 | 0.022888 | -0.11444 | 0.09613 | 0.073242 | -0.11902 | -0.17395 | 0.10529 | -0.036621 | -120.369 | 0.21057 | 0.2655 | 0.30212 | -120.5338 | 0.050354 | -0.004577 | -120.4376 | 0.10071 | 0.054932 | 0.059509 | -120.4605 | 0.33417 | 0.16937 | 0.20599 | -120.7397 | 0.2655 | 0.24261 | 0.19226 | -120.7077
2438.9062 | 120.7123 | -0.1831 | 120.6116 | -0.016251 | 0.010523 | 0.053476 | 0.0025612 | 0.0016919 | -0.00013244 | -0.0046526 | 0.014572 | -0.0053534 | 0.0044284 | -0.0032728 | -0.0094123 | 0.020961 | 0.073242 | 0.064087 | 0.082397 | 0.11444 | 0.14648 | -0.032043 | -0.1831 | 0.045776 | 0.091553 | -0.036621 | 0.041199 | 0.027466 | -0.059509 | -0.13275 | 0.15106 | 0 | -120.4651 | 0.24719 | 0.29755 | 0.29755 | -120.5383 | 0.1236 | 0.050354 | -120.5704 | 0.22888 | 0.14648 | 0.09613 | -120.5841 | 0.32959 | 0.25635 | 0.2655 | -120.7947 | 0.2243 | 0.21057 | 0.27466 | -120.7443
2440.6562 | 120.7443 | -0.20142 | 120.6116 | 0.0066373 | 0.013087 | 0.053904 | 0.0044838 | 0.0051099 | -0.00034604 | -0.0052936 | -0.00068649 | -0.0030034 | 0.0054966 | -0.005409 | -0.010908 | 0.021388 | 0.054932 | 0.086975 | 0.082397 | 0.13275 | 0.1236 | -0.032043 | -0.1831 | 0.032043 | 0.086975 | -0.018311 | 0.050354 | 0.027466 | -0.10529 | -0.13733 | 0.16937 | 0.018311 | -120.488 | 0.28839 | 0.33417 | 0.31586 | -120.5566 | 0.09613 | 0.064087 | -120.5612 | 0.23346 | 0.18311 | 0.11902 | -120.5841 | 0.32501 | 0.25635 | 0.28381 | -120.7947 | 0.25177 | 0.22888 | 0.28839 | -120.7489
2442.4062 | 120.8038 | -0.20599 | 120.6436 | -0.00099167 | 0.012873 | 0.053904 | 0.0034158 | 0.0042555 | 0.002431 | -0.006148 | 0.0069425 | -0.00065364 | 0.0042148 | -0.003059 | -0.0074897 | 0.02267 | -0.027466 | -0.059509 | -0.064087 | 0.045776 | 0.17853 | -0.082397 | -0.21973 | -0.054932 | -0.073242 | -0.14191 | 0.07782 | 0.082397 | -0.10071 | -0.16479 | 0.1236 | -0.013733 | -120.4651 | 0.14649 | 0.25177 | 0.2655 | -120.6711 | 0.10529 | 0.041199 | -120.5658 | 0.15106 | 0.064087 | 0.022888 | -120.5612 | 0.38452 | 0.17853 | 0.14191 | -120.8633 | 0.28381 | 0.28839 | 0.13275 | -120.8084
2444.1719 | 120.9091 | -0.15564 | 120.694 | 0.0066373 | 0.0088142 | 0.054972 | 0.00897 | 0.0040417 | -0.0052594 | -0.007857 | -0.00068649 | -0.0062078 | 0.0059238 | -0.00092279 | -0.014967 | 0.019679 | 0.041199 | 0.091553 | 0.09613 | 0.13275 | 0.14191 | -0.036621 | -0.20142 | 0.045776 | 0.10986 | -0.004578 | 0.059509 | 0.036621 | -0.073242 | -0.1236 | 0.11902 | -0.045776 | -120.5521 | 0.24719 | 0.28839 | 0.33417 | -120.6528 | 0.082398 | 0.032044 | -120.6345 | 0.20142 | 0.15106 | 0.11902 | -120.6573 | 0.29755 | 0.19684 | 0.25177 | -120.8954 | 0.21515 | 0.19226 | 0.2655 | -120.8176
2445.8594 | 120.8267 | -0.21515 | 120.7352 | 0.0066373 | 0.007746 | 0.053904 | 0.0034158 | 0.0029737 | -0.0039776 | -0.0070026 | 0.014572 | -0.0047124 | 0.0033604 | -0.0032728 | -0.012403 | 0.022883 | 0.004578 | 0.032043 | 0.027466 | 0.082397 | 0.15564 | -0.050354 | -0.18768 | 0 | 0.027466 | -0.068665 | 0.054932 | 0.041199 | -0.082397 | -0.14648 | 0.16479 | 0.027466 | -120.5795 | 0.24719 | 0.29755 | 0.27008 | -120.7306 | 0.13275 | 0.068665 | -120.6802 | 0.21515 | 0.14648 | 0.077819 | -120.694 | 0.37079 | 0.21973 | 0.24261 | -120.9229 | 0.27008 | 0.25635 | 0.24261 | -120.8817
2447.5469 | 120.9595 | -0.16937 | 120.694 | -0.00099167 | 0.012659 | 0.052835 | 0.0029886 | 0.0061781 | 0.0049946 | -0.0042254 | -0.00068649 | -0.00086724 | 0.0057102 | -0.00070919 | -0.0089849 | 0.01797 | -0.004578 | -0.041199 | -0.022888 | 0.068665 | 0.18768 | -0.073242 | -0.23346 | -0.032043 | 0.004578 | -0.12817 | 0.07782 | 0.073242 | -0.091553 | -0.16937 | 0.096131 | -0.064086 | -120.5063 | 0.12817 | 0.23804 | 0.30212 | -120.6985 | 0.07782 | 0 | -120.6161 | 0.13733 | 0.041199 | 0.041199 | -120.6207 | 0.35706 | 0.16479 | 0.14649 | -120.9274 | 0.24719 | 0.24261 | 0.17395 | -120.8633
2449.25 | 120.9183 | -0.18768 | 120.7581 | -0.00099167 | 0.01095 | 0.05369 | 0.0046976 | 0.0038281 | 0.0039264 | -0.0059344 | 0.022202 | -0.003858 | 0.0061374 | -0.00092279 | -0.0098395 | 0.019679 | -0.009155 | -0.059509 | -0.050354 | 0.054932 | 0.19684 | -0.07782 | -0.21973 | -0.045776 | -0.045776 | -0.13733 | 0.068665 | 0.064087 | -0.10071 | -0.16022 | 0.10986 | -0.032044 | -120.5612 | 0.12817 | 0.24261 | 0.27466 | -120.7672 | 0.086975 | 0.027466 | -120.6894 | 0.14191 | 0.050354 | 0.022888 | -120.694 | 0.38452 | 0.17853 | 0.13733 | -120.9778 | 0.25635 | 0.25177 | 0.14191 | -120.9183
2451 | 120.9641 | -0.16022 | 120.726 | 0.0066373 | 0.016932 | 0.054331 | 0.0098244 | 0.0016919 | -0.00077324 | -0.00508 | -0.008316 | -0.0040716 | 0.0076328 | -0.0037 | -0.012617 | 0.019038 | -0.050354 | -0.050354 | -0.018311 | 0.027466 | 0.19684 | -0.073242 | -0.2243 | -0.09613 | -0.022888 | -0.15106 | 0.09613 | 0.086975 | -0.13275 | -0.1831 | 0.086975 | -0.064087 | -120.5292 | 0.10986 | 0.18768 | 0.25177 | -120.7764 | 0.027466 | -0.022888 | -120.6299 | 0.064087 | 0.009155 | 0.032043 | -120.639 | 0.35706 | 0.10986 | 0.14191 | -120.9503 | 0.25635 | 0.24719 | 0.13733 | -120.9091
2452.75 | 120.932 | -0.21515 | 120.7993 | -0.00099167 | 0.013514 | 0.05369 | 0.0032022 | 0.0034009 | 0.002431 | -0.0055072 | -0.00068649 | -0.00065364 | 0.0065646 | -0.001991 | -0.0091985 | 0.021174 | -0.009155 | -0.045776 | -0.013733 | 0.054932 | 0.19226 | -0.059509 | -0.2243 | -0.009155 | -0.004578 | -0.10986 | 0.064087 | 0.054932 | -0.082397 | -0.14648 | 0.15564 | -0.009155 | -120.607 | 0.16937 | 0.27008 | 0.27924 | -120.8084 | 0.13275 | 0.068665 | -120.7352 | 0.20599 | 0.10529 | 0.036621 | -120.7443 | 0.40741 | 0.20599 | 0.20142 | -121.0236 | 0.27924 | 0.27008 | 0.21057 | -120.9457
2454.5156 | 120.8908 | -0.19684 | 120.813 | -0.00099167 | 0.0098822 | 0.053476 | 0.0087564 | 0.0025465 | -0.003764 | -0.004439 | -0.00068649 | -0.0059942 | 0.004642 | -0.0022046 | -0.0087713 | 0.022242 | 0.045776 | 0.10071 | 0.091553 | 0.11444 | 0.13733 | -0.032043 | -0.19226 | 0.032043 | 0.073242 | -0.041199 | 0.041199 | 0.045776 | -0.07782 | -0.13733 | 0.1648 | 0.004577 | -120.6757 | 0.29755 | 0.31128 | 0.3067 | -120.7672 | 0.11902 | 0.059509 | -120.7718 | 0.22888 | 0.15564 | 0.09613 | -120.7672 | 0.33417 | 0.24261 | 0.28839 | -121.0052 | 0.23804 | 0.24261 | 0.27008 | -120.9503
2456.2812 | 120.9091 | -0.20599 | 120.8267 | -0.00099167 | 0.015223 | 0.052835 | 0.0051248 | 0.0029737 | 0.0054218 | -0.0042254 | 0.022202 | -0.00065364 | 0.00806 | -0.0034864 | -0.0079169 | 0.020533 | -0.041199 | -0.068665 | -0.068665 | 0.041199 | 0.1831 | -0.086975 | -0.24261 | -0.091553 | -0.073242 | -0.18768 | 0.091553 | 0.082397 | -0.10071 | -0.1831 | 0.11902 | -0.036621 | -120.6436 | 0.13733 | 0.24719 | 0.28381 | -120.8679 | 0.10529 | 0.022889 | -120.7352 | 0.11444 | 0.018311 | -0.004578 | -120.7443 | 0.3891 | 0.1648 | 0.13733 | -121.0693 | 0.29755 | 0.28839 | 0.13275 | -121.0098
2457.9688 | 121.0327 | -0.16937 | 120.813 | 0.0066373 | 0.015009 | 0.051981 | 0.010252 | 0.0027601 | 0.0034992 | -0.0046526 | 0.0069425 | -0.00022644 | 0.008701 | -0.0017774 | -0.010267 | 0.018184 | 0.018311 | 0.032043 | 0.009155 | 0.091553 | 0.17853 | -0.073242 | -0.22888 | -0.036621 | 0.013733 | -0.12817 | 0.07782 | 0.082397 | -0.10986 | -0.16937 | 0.096131 | -0.059509 | -120.6345 | 0.20142 | 0.26093 | 0.32044 | -120.7947 | 0.05951 | 0 | -120.7352 | 0.13275 | 0.041199 | 0.041199 | -120.7306 | 0.3479 | 0.18768 | 0.17853 | -121.0419 | 0.24719 | 0.25177 | 0.18311 | -120.9824
2459.6719 | 121.0327 | -0.16479 | 120.8313 | 0.0066373 | 0.012232 | 0.054544 | 0.0076882 | 0.0051099 | -0.0035504 | -0.006148 | 0.0069425 | -0.005567 | 0.0074192 | -0.004768 | -0.014753 | 0.021388 | 0.027466 | 0.10071 | 0.10529 | 0.13733 | 0.14648 | -0.045776 | -0.19226 | 0.018311 | 0.12817 | -0.018311 | 0.059509 | 0.045776 | -0.068665 | -0.1236 | 0.11902 | -0.027466 | -120.6848 | 0.2655 | 0.30212 | 0.32959 | -120.8038 | 0.09613 | 0.041199 | -120.7718 | 0.18311 | 0.14648 | 0.10528 | -120.7855 | 0.31128 | 0.19226 | 0.27008 | -121.0236 | 0.2243 | 0.21057 | 0.29297 | -120.9549
2461.4219 | 120.9641 | -0.20142 | 120.8496 | 0.014267 | 0.0133 | 0.053049 | 0.0049112 | 0.0048963 | 0.0054218 | -0.0052936 | 0.0069425 | -0.00086724 | 0.0042148 | 0.00014521 | -0.0077033 | 0.018184 | -0.041199 | -0.086975 | -0.068665 | 0.041199 | 0.17395 | -0.068665 | -0.23346 | -0.059509 | -0.068665 | -0.17853 | 0.073242 | 0.082397 | -0.09613 | -0.17395 | 0.13275 | -0.032043 | -120.6757 | 0.11444 | 0.24262 | 0.27466 | -120.8908 | 0.10529 | 0.027466 | -120.7764 | 0.14191 | 0.022888 | -0.004578 | -120.7672 | 0.37537 | 0.16022 | 0.13275 | -121.0831 | 0.27466 | 0.28381 | 0.13275 | -121.0236
2463.1094 | 121.0968 | -0.16022 | 120.8679 | 0.014267 | 0.014155 | 0.052195 | 0.0049112 | 0.0044691 | 0.00414 | -0.001021 | 0.0069425 | -0.002149 | 0.0067782 | -0.0028454 | -0.0094123 | 0.02032 | 0.022888 | 0.022888 | -0.009155 | 0.086975 | 0.17395 | -0.064087 | -0.2243 | -0.027466 | 0.032043 | -0.11902 | 0.091553 | 0.068665 | -0.10071 | -0.16937 | 0.09613 | -0.064087 | -120.694 | 0.1831 | 0.24719 | 0.31128 | -120.845 | 0.059509 | -0.009156 | -120.7764 | 0.13275 | 0.041198 | 0.050354 | -120.7993 | 0.33417 | 0.1831 | 0.15106 | -121.0922 | 0.25177 | 0.22888 | 0.19226 | -121.0373
2464.8125 | 120.9915 | -0.18768 | 120.8954 | 0.014267 | 0.0096686 | 0.053476 | 0.0057656 | 0.0046827 | -0.00098684 | -0.0042254 | -0.00068649 | -0.003858 | 0.0057102 | -0.0028454 | -0.0091985 | 0.021388 | 0.050354 | 0.07782 | 0.07782 | 0.13733 | 0.14191 | -0.041199 | -0.16937 | 0.041199 | 0.091553 | -0.022888 | 0.036621 | 0.036621 | -0.068665 | -0.12817 | 0.14648 | 0.01831 | -120.7535 | 0.2655 | 0.32501 | 0.3067 | -120.845 | 0.11902 | 0.059509 | -120.8588 | 0.22888 | 0.16479 | 0.10529 | -120.8588 | 0.32959 | 0.23804 | 0.2655 | -121.0648 | 0.2243 | 0.2243 | 0.27924 | -121.0236
2466.5781 | 120.9961 | -0.17853 | 120.8954 | 0.014267 | 0.010523 | 0.052835 | 0.0036294 | 0.0027601 | 0.0015766 | -0.0055072 | 0.0069425 | -0.0027898 | 0.0048556 | -0.0032728 | -0.010053 | 0.020533 | 0.036621 | 0.050354 | 0.068665 | 0.11444 | 0.15564 | -0.036621 | -0.17853 | 0.041199 | 0.073242 | -0.036621 | 0.050354 | 0.041199 | -0.064087 | -0.10986 | 0.14191 | 0 | -120.7397 | 0.22888 | 0.29297 | 0.29297 | -120.8588 | 0.11444 | 0.068665 | -120.845 | 0.21973 | 0.14191 | 0.073242 | -120.8542 | 0.33417 | 0.21515 | 0.24719 | -121.0739 | 0.22888 | 0.21973 | 0.25177 | -121.0052
2468.3281 | 121.106 | -0.16479 | 120.8862 | 0.0066373 | 0.014368 | 0.050913 | 0.0068338 | 0.0053235 | 0.0015766 | -0.0035846 | 0.0069425 | -0.0036444 | 0.0078464 | -0.0028454 | -0.01048 | 0.019465 | 0.036621 | 0.009155 | 0 | 0.091553 | 0.16937 | -0.064087 | -0.22888 | -0.018311 | 0.036621 | -0.12817 | 0.091553 | 0.07782 | -0.10529 | -0.15106 | 0.10071 | -0.064087 | -120.7169 | 0.17395 | 0.25635 | 0.32044 | -120.8496 | 0.059509 | 0.013733 | -120.7947 | 0.14648 | 0.036621 | 0.022888 | -120.8084 | 0.33417 | 0.20142 | 0.16479 | -121.1151 | 0.25635 | 0.24261 | 0.20142 | -121.0373
2470.0156 | 121.0556 | -0.19226 | 120.9457 | -0.00099167 | 0.011164 | 0.054331 | 0.0036294 | 0.0034009 | 8.1158e-05 | -0.0042254 | 0.0069425 | -0.0047124 | 0.0054966 | -0.0011364 | -0.011549 | 0.020106 | 0.027466 | 0.022888 | 0.036621 | 0.091553 | 0.14648 | -0.036621 | -0.19226 | 0.022888 | 0.059509 | -0.036621 | 0.050354 | 0.041199 | -0.068665 | -0.13275 | 0.15564 | 0 | -120.7993 | 0.21515 | 0.28381 | 0.28381 | -120.9183 | 0.1236 | 0.05951 | -120.8954 | 0.21515 | 0.15564 | 0.09613 | -120.9045 | 0.33874 | 0.21973 | 0.22888 | -121.138 | 0.24261 | 0.23346 | 0.25177 | -121.0785
2471.7656 | 121.0693 | -0.17853 | 120.9366 | 0.0066373 | 0.013941 | 0.052195 | 0.0051248 | 0.0025465 | 0.0028584 | -0.0025164 | -0.00068649 | -0.0010808 | 0.0057102 | -0.00092279 | -0.0072759 | 0.019893 | 0.036621 | 0 | 0.004578 | 0.086975 | 0.16479 | -0.064087 | -0.22888 | -0.036621 | -0.009155 | -0.13733 | 0.068665 | 0.082397 | -0.10986 | -0.16479 | 0.11444 | -0.050354 | -120.7718 | 0.17853 | 0.2655 | 0.31586 | -120.9 | 0.068665 | 0.013733 | -120.8679 | 0.14191 | 0.041199 | 0.027466 | -120.8542 | 0.34332 | 0.21515 | 0.18311 | -121.1655 | 0.24719 | 0.26092 | 0.16937 | -121.1014
2473.5156 | 121.0281 | -0.21973 | 120.9503 | 0.0066373 | 0.014582 | 0.050272 | 0.0044838 | 0.0036145 | 0.0039264 | -0.0035846 | -0.00068649 | -0.0012946 | 0.009769 | -0.003059 | -0.010267 | 0.019893 | -0.032043 | -0.041199 | -0.045776 | 0.050354 | 0.1831 | -0.068665 | -0.21057 | -0.073242 | -0.050354 | -0.18768 | 0.091553 | 0.086975 | -0.10529 | -0.1831 | 0.15106 | 0.009156 | -120.7672 | 0.17853 | 0.27008 | 0.26093 | -120.9824 | 0.11444 | 0.036622 | -120.8588 | 0.14649 | 0.032044 | -0.004578 | -120.8633 | 0.40283 | 0.18768 | 0.17395 | -121.1609 | 0.31128 | 0.3067 | 0.16937 | -121.1334
2475.2656 | 121.106 | -0.20142 | 120.9503 | -0.0086212 | 0.012873 | 0.053049 | 0.007261 | 0.0040417 | 0.0015766 | -0.0040118 | -0.00068649 | -0.0010808 | 0.0057102 | -0.00070919 | -0.010267 | 0.021388 | -0.068665 | -0.059509 | -0.054932 | 0.032043 | 0.1831 | -0.082397 | -0.2243 | -0.073242 | -0.059509 | -0.15106 | 0.09613 | 0.091553 | -0.10071 | -0.16022 | 0.11902 | -0.022888 | -120.7672 | 0.14191 | 0.23346 | 0.25635 | -121.019 | 0.10071 | 0.041199 | -120.8542 | 0.12817 | 0.050354 | 0.009155 | -120.8588 | 0.38452 | 0.13275 | 0.14648 | -121.1746 | 0.29755 | 0.29297 | 0.14191 | -121.1105
2477.0156 | 121.0693 | -0.21057 | 120.9686 | 0.0066373 | 0.014155 | 0.05134 | 0.0051248 | 0.0042555 | 0.002431 | -0.003371 | 0.0069425 | -0.002149 | 0.006992 | -0.0015638 | -0.0085577 | 0.02032 | -0.032043 | -0.064087 | -0.064087 | 0.045776 | 0.17395 | -0.09613 | -0.2243 | -0.10071 | -0.054932 | -0.18768 | 0.09613 | 0.082397 | -0.11444 | -0.1831 | 0.11444 | -0.013733 | -120.7947 | 0.14648 | 0.25635 | 0.27008 | -121.0007 | 0.09613 | 0.027466 | -120.8725 | 0.10986 | 0.022888 | -0.004578 | -120.8862 | 0.38452 | 0.17853 | 0.14648 | -121.1929 | 0.3067 | 0.29297 | 0.15564 | -121.1517
2478.7188 | 121.0785 | -0.19684 | 120.9869 | -0.00099167 | 0.010096 | 0.054544 | 0.0064066 | 0.0023327 | -0.0067548 | -0.0048662 | 0.014572 | -0.0062078 | 0.0074192 | -0.0039136 | -0.014112 | 0.02331 | -0.013733 | 0.036621 | 0.045776 | 0.086975 | 0.13733 | -0.027466 | -0.19226 | -0.036621 | 0.036621 | -0.064087 | 0.059509 | 0.054932 | -0.068665 | -0.15106 | 0.16937 | 0.004577 | -120.8496 | 0.23346 | 0.28381 | 0.27924 | -121.0007 | 0.12817 | 0.045776 | -120.9274 | 0.16022 | 0.13275 | 0.086975 | -120.932 | 0.33417 | 0.18311 | 0.24261 | -121.1792 | 0.25635 | 0.25177 | 0.23346 | -121.138
2480.4688 | 121.106 | -0.23346 | 121.0098 | -0.00099167 | 0.014155 | 0.052622 | 0.0066202 | 0.0031873 | 0.0043536 | -0.004439 | 0.0069425 | -0.0019354 | 0.0082736 | -0.003059 | -0.0098395 | 0.019679 | -0.004578 | -0.032043 | -0.027466 | 0.073242 | 0.1831 | -0.054932 | -0.23346 | -0.068665 | -0.050354 | -0.16022 | 0.091553 | 0.068665 | -0.10986 | -0.16022 | 0.17853 | 0 | -120.8267 | 0.20142 | 0.3067 | 0.3067 | -121.0144 | 0.1236 | 0.073242 | -120.9183 | 0.16479 | 0.073242 | 0 | -120.9412 | 0.41656 | 0.22888 | 0.20599 | -121.2433 | 0.32501 | 0.30212 | 0.1831 | -121.17
2482.1562 | 121.2021 | -0.16479 | 120.9824 | -0.00099167 | 0.015009 | 0.052622 | 0.0059792 | 0.0025465 | 0.0054218 | -0.0037982 | -0.00068649 | -0.0025762 | 0.0072056 | -0.00092279 | -0.010053 | 0.02032 | 0 | 0.022888 | 0 | 0.091553 | 0.17853 | -0.07782 | -0.20599 | -0.036621 | 0.036621 | -0.11444 | 0.07782 | 0.086975 | -0.09613 | -0.16479 | 0.086975 | -0.041199 | -120.8038 | 0.18768 | 0.25635 | 0.29755 | -120.9824 | 0.068665 | 0 | -120.9045 | 0.12817 | 0.050354 | 0.050354 | -120.8954 | 0.34332 | 0.16479 | 0.16479 | -121.1884 | 0.24261 | 0.25177 | 0.20142 | -121.1472
2483.9219 | 121.2341 | -0.15106 | 120.9732 | 0.0066373 | 0.010523 | 0.054758 | 0.010679 | 0.0029737 | -0.0046184 | -0.0067888 | -0.00068649 | -0.006635 | 0.0059238 | -0.0043408 | -0.016676 | 0.022029 | -0.013733 | 0.036621 | 0.050354 | 0.10529 | 0.1831 | -0.027466 | -0.18768 | -0.009155 | 0.07782 | -0.013733 | 0.059509 | 0.059509 | -0.086975 | -0.14648 | 0.1236 | -0.036621 | -120.7901 | 0.18768 | 0.25635 | 0.29297 | -120.9869 | 0.064087 | 0.004578 | -120.9137 | 0.14191 | 0.13733 | 0.13275 | -120.9137 | 0.33417 | 0.13733 | 0.20142 | -121.1609 | 0.21057 | 0.21057 | 0.22888 | -121.1197
2485.6875 | 121.2296 | -0.16022 | 120.9961 | 0.0066373 | 0.0133 | 0.051981 | 0.0064066 | 0.0031873 | 0.003072 | -0.00508 | -0.00068649 | -0.0010808 | 0.0072056 | -0.0011364 | -0.011549 | 0.019038 | -0.064087 | -0.045776 | -0.064087 | 0.041199 | 0.19684 | -0.09613 | -0.22888 | -0.091553 | -0.032043 | -0.16479 | 0.082397 | 0.082397 | -0.11902 | -0.15106 | 0.064087 | -0.068665 | -120.7993 | 0.11444 | 0.20142 | 0.27008 | -121.0602 | 0.041198 | 0.009155 | -120.9137 | 0.068664 | -0.004578 | -0.013733 | -120.9137 | 0.35706 | 0.09613 | 0.09613 | -121.225 | 0.24261 | 0.24261 | 0.12817 | -121.1472
2487.4375 | 121.17 | -0.16937 | 121.0236 | -0.00099167 | 0.012873 | 0.05369 | 0.0040566 | 0.0021191 | 0.0028584 | -0.0037982 | 0.0069425 | -0.0025762 | 0.0074192 | -6.8386e-05 | -0.011121 | 0.019679 | -0.041199 | -0.050354 | -0.045776 | 0.050354 | 0.17395 | -0.073242 | -0.21973 | -0.018311 | -0.022888 | -0.1236 | 0.073242 | 0.054932 | -0.10071 | -0.14648 | 0.096131 | -0.050354 | -120.8496 | 0.11902 | 0.21973 | 0.27008 | -121.0648 | 0.068665 | 0.022889 | -120.9503 | 0.15106 | 0.045777 | 0.022888 | -120.9686 | 0.34332 | 0.12817 | 0.1236 | -121.2433 | 0.24261 | 0.22431 | 0.14649 | -121.17
2489.1406 | 121.2616 | -0.15564 | 121.0098 | 0.014267 | 0.011591 | 0.053904 | 0.0046976 | 0.0027601 | 0.0017902 | -0.0065752 | -0.00068649 | -0.0032172 | 0.006992 | -0.0028454 | -0.010053 | 0.019252 | -0.032043 | -0.059509 | -0.045776 | 0.054932 | 0.19684 | -0.086975 | -0.23804 | -0.082397 | -0.032043 | -0.15106 | 0.09613 | 0.07782 | -0.10529 | -0.16479 | 0.068665 | -0.082397 | -120.813 | 0.096131 | 0.21057 | 0.29297 | -121.0419 | 0.050354 | -0.009155 | -120.9137 | 0.073243 | 0.004578 | 0.013733 | -120.932 | 0.35248 | 0.1236 | 0.10986 | -121.2479 | 0.25177 | 0.23346 | 0.1236 | -121.1746
2490.8438 | 121.257 | -0.16479 | 121.0327 | -0.00099167 | 0.013514 | 0.051554 | 0.0064066 | 0.0048963 | 0.00414 | -0.0048662 | -0.00068649 | -0.0023626 | 0.0084872 | 0.00014521 | -0.010267 | 0.018824 | 0 | 0.013733 | -0.004578 | 0.082397 | 0.1831 | -0.073242 | -0.2243 | -0.027466 | 0.009155 | -0.1236 | 0.082397 | 0.064087 | -0.10071 | -0.16022 | 0.091553 | -0.059509 | -120.8496 | 0.17853 | 0.24719 | 0.3067 | -121.0327 | 0.064087 | 0.004578 | -120.9503 | 0.13733 | 0.041199 | 0.036621 | -120.9686 | 0.3479 | 0.16479 | 0.16022 | -121.257 | 0.24719 | 0.22888 | 0.17395 | -121.1929
2492.5938 | 121.2433 | -0.16022 | 121.019 | 0.0066373 | 0.012446 | 0.054758 | 0.0093972 | 0.0042555 | -0.0044048 | -0.0074298 | -0.00068649 | -0.0051398 | 0.008701 | -0.0032728 | -0.01518 | 0.020533 | 0.018311 | 0.11902 | 0.11902 | 0.14191 | 0.14191 | -0.041199 | -0.16479 | 0.027466 | 0.12817 | -0.009155 | 0.022888 | 0.041199 | -0.07782 | -0.13275 | 0.11902 | -0.004578 | -120.8771 | 0.27924 | 0.30212 | 0.3067 | -121.0007 | 0.082397 | 0.027466 | -120.9961 | 0.18768 | 0.15106 | 0.1236 | -120.9778 | 0.30212 | 0.17853 | 0.27924 | -121.1838 | 0.1831 | 0.20142 | 0.28839 | -121.1517
2494.3438 | 121.225 | -0.16479 | 121.0327 | 0.0066373 | 0.014155 | 0.051981 | 0.010038 | 0.0021191 | 0.00072196 | -0.007857 | -0.00068649 | -0.0051398 | 0.0065646 | -0.0028454 | -0.01283 | 0.02032 | -0.009155 | 0.027466 | 0.018311 | 0.086975 | 0.16937 | -0.073242 | -0.20599 | -0.068665 | 0.004578 | -0.14648 | 0.091553 | 0.073242 | -0.10529 | -0.16022 | 0.091553 | -0.041199 | -120.8633 | 0.19226 | 0.25177 | 0.29297 | -121.0419 | 0.059509 | 0.004578 | -120.9412 | 0.09613 | 0.018311 | 0.013733 | -120.9595 | 0.33417 | 0.15564 | 0.18311 | -121.2387 | 0.25635 | 0.23804 | 0.16937 | -121.1929
2496.0938 | 121.1563 | -0.21515 | 121.0739 | 0.0066373 | 0.012232 | 0.052835 | 0.0051248 | 0.0040417 | 0.00414 | -0.004439 | 0.014572 | -0.0012946 | 0.0061374 | -0.0015638 | -0.0072759 | 0.02032 | -0.050354 | -0.073242 | -0.054932 | 0.050354 | 0.17853 | -0.068665 | -0.24261 | -0.07782 | -0.086975 | -0.20142 | 0.09613 | 0.082397 | -0.11444 | -0.1831 | 0.14648 | -0.027466 | -120.8954 | 0.14191 | 0.2655 | 0.29297 | -121.1243 | 0.10071 | 0.032044 | -120.9778 | 0.13733 | 0.013733 | -0.018311 | -120.9915 | 0.39368 | 0.16479 | 0.16022 | -121.3165 | 0.31128 | 0.29755 | 0.12817 | -121.257
2497.7969 | 121.17 | -0.21057 | 121.106 | 0.014267 | 0.013727 | 0.05134 | 0.0042702 | 0.0044691 | 0.0028584 | -0.0042254 | -0.00068649 | -0.0027898 | 0.0078464 | -0.0022046 | -0.0091985 | 0.020533 | -0.045776 | -0.068665 | -0.054932 | 0.036621 | 0.17853 | -0.068665 | -0.22888 | -0.086975 | -0.064087 | -0.21515 | 0.086975 | 0.07782 | -0.10529 | -0.17853 | 0.14191 | -0.018311 | -120.9274 | 0.14191 | 0.24719 | 0.2655 | -121.1517 | 0.10529 | 0.032043 | -121.019 | 0.1236 | -0.004578 | -0.036621 | -121.0281 | 0.3891 | 0.1648 | 0.15564 | -121.3348 | 0.29755 | 0.28839 | 0.14648 | -121.2845
2499.5625 | 121.3028 | -0.14191 | 121.0648 | -0.0086212 | 0.017786 | 0.053904 | 0.007261 | 0.0046827 | 0.0011494 | -0.003371 | 0.0069425 | -0.0019354 | 0.0089146 | -0.0017774 | -0.011121 | 0.022029 | -0.013733 | -0.022888 | 0 | 0.07782 | 0.17853 | -0.082397 | -0.22888 | -0.032043 | 0.022888 | -0.11902 | 0.10071 | 0.091553 | -0.10529 | -0.15564 | 0.05951 | -0.086975 | -120.8862 | 0.11902 | 0.21973 | 0.3067 | -121.0785 | 0.036621 | -0.013733 | -120.9641 | 0.10986 | 0.022888 | 0.036621 | -120.9732 | 0.32044 | 0.12817 | 0.14191 | -121.2936 | 0.24262 | 0.23346 | 0.16479 | -121.2204
2501.25 | 121.1884 | -0.21057 | 121.1151 | 0.0066373 | 0.012446 | 0.051767 | 0.0061928 | 0.0027601 | 0.0026446 | -0.003371 | 0.014572 | -0.0015082 | 0.0067782 | -0.00092279 | -0.0079169 | 0.019679 | -0.059509 | -0.036621 | -0.050354 | 0.054932 | 0.1831 | -0.054932 | -0.21515 | -0.091553 | -0.059509 | -0.1831 | 0.07782 | 0.086975 | -0.10986 | -0.16479 | 0.15564 | -0.004578 | -120.932 | 0.17395 | 0.2655 | 0.27008 | -121.1746 | 0.10071 | 0.045776 | -121.0373 | 0.11902 | 0.027466 | -0.01831 | -121.0281 | 0.39368 | 0.15106 | 0.16022 | -121.3303 | 0.28839 | 0.29755 | 0.15106 | -121.2799
2502.9375 | 121.2433 | -0.20142 | 121.106 | -0.00099167 | 0.015009 | 0.051554 | 0.0057656 | 0.0036145 | 0.0022174 | -0.0046526 | 0.0069425 | -0.0025762 | 0.0057102 | -0.0022046 | -0.0087713 | 0.020961 | -0.059509 | -0.073242 | -0.064087 | 0.050354 | 0.18768 | -0.07782 | -0.21515 | -0.086975 | -0.064087 | -0.16479 | 0.091553 | 0.091553 | -0.10529 | -0.17395 | 0.1236 | -0.013733 | -120.9183 | 0.12817 | 0.25177 | 0.2655 | -121.1655 | 0.09613 | 0.027466 | -121.0144 | 0.11444 | 0.036621 | 0.009155 | -121.0144 | 0.3891 | 0.14191 | 0.13733 | -121.3211 | 0.29297 | 0.29297 | 0.13733 | -121.2799
2504.6875 | 121.3165 | -0.1831 | 121.1014 | 0.0066373 | 0.012018 | 0.052622 | 0.0091836 | 0.0051099 | -0.00077324 | -0.00508 | -0.00068649 | -0.0034308 | 0.0091282 | -0.0011364 | -0.012617 | 0.021388 | -0.073242 | -0.045776 | -0.045776 | 0.045776 | 0.19226 | -0.073242 | -0.23346 | -0.10071 | -0.018311 | -0.15564 | 0.10071 | 0.09613 | -0.11444 | -0.17395 | 0.10986 | -0.050354 | -120.9091 | 0.13733 | 0.22888 | 0.27924 | -121.1746 | 0.068664 | 0.009155 | -121.0007 | 0.082397 | 0.027465 | 0.01831 | -121.0052 | 0.37537 | 0.10986 | 0.13733 | -121.3348 | 0.28381 | 0.27924 | 0.16479 | -121.2753
2506.4375 | 121.2021 | -0.20142 | 121.1426 | 0.0066373 | 0.0092414 | 0.053904 | 0.0076882 | 0.0048963 | -0.0026958 | -0.0046526 | -0.00068649 | -0.0077032 | 0.0065646 | -0.0015638 | -0.011976 | 0.02267 | 0.013733 | 0.064087 | 0.073242 | 0.10529 | 0.13275 | -0.054932 | -0.17395 | 0.004578 | 0.068665 | -0.032043 | 0.032043 | 0.045776 | -0.082397 | -0.14191 | 0.14648 | 0.027466 | -121.0098 | 0.2655 | 0.3067 | 0.27924 | -121.1288 | 0.11902 | 0.059509 | -121.1105 | 0.20599 | 0.16937 | 0.10986 | -121.0968 | 0.33417 | 0.21515 | 0.27466 | -121.3165 | 0.23346 | 0.24719 | 0.27008 | -121.2845
2508.125 | 121.3028 | -0.16022 | 121.0876 | 0.0066373 | 0.012018 | 0.054972 | 0.0079018 | 0.0044691 | -0.0022686 | -0.0065752 | 0.0069425 | -0.0030034 | 0.0072056 | -0.0017774 | -0.011976 | 0.020106 | -0.041199 | -0.036621 | -0.032043 | 0.036621 | 0.17853 | -0.068665 | -0.23804 | -0.10071 | -0.027466 | -0.15106 | 0.091553 | 0.091553 | -0.14191 | -0.16479 | 0.091552 | -0.07782 | -120.9091 | 0.1236 | 0.19684 | 0.27466 | -121.1288 | 0.01831 | -0.004578 | -120.9961 | 0.059509 | 0.009155 | 0.013733 | -120.9961 | 0.33874 | 0.11902 | 0.12817 | -121.3257 | 0.25177 | 0.25177 | 0.13275 | -121.2524
2509.8125 | 121.3852 | -0.16479 | 121.0876 | -0.00099167 | 0.016718 | 0.05134 | 0.00897 | 0.0057507 | -0.00013244 | -0.0067888 | 0.0069425 | -0.0025762 | 0.0091282 | -0.00049559 | -0.010694 | 0.017329 | -0.050354 | -0.045776 | -0.041199 | 0.054932 | 0.1831 | -0.064087 | -0.2243 | -0.059509 | -0.013733 | -0.14648 | 0.10071 | 0.082397 | -0.10529 | -0.16937 | 0.10071 | -0.059509 | -120.9045 | 0.11902 | 0.21973 | 0.27924 | -121.138 | 0.059509 | -0.004578 | -120.9869 | 0.10529 | 0.018311 | 0.022889 | -121.0052 | 0.3479 | 0.11444 | 0.1236 | -121.312 | 0.2655 | 0.24719 | 0.15106 | -121.257
2511.5625 | 121.2616 | -0.21515 | 121.1517 | 0.0066373 | 0.014796 | 0.054117 | 0.0023476 | 0.0053235 | 0.0037128 | -0.0055072 | 0.014572 | -0.003858 | 0.005283 | -0.0028454 | -0.0085577 | 0.020106 | -0.059509 | -0.054932 | -0.059509 | 0.045776 | 0.18768 | -0.068665 | -0.21973 | -0.068665 | -0.064087 | -0.16937 | 0.086975 | 0.082397 | -0.09613 | -0.16022 | 0.14648 | -0.004578 | -120.964 | 0.16022 | 0.26093 | 0.2655 | -121.2112 | 0.11902 | 0.054932 | -121.0648 | 0.14648 | 0.045776 | -0.009156 | -121.0693 | 0.40283 | 0.15564 | 0.15564 | -121.3715 | 0.30212 | 0.29755 | 0.15106 | -121.3119
2513.25 | 121.2891 | -0.19226 | 121.1609 | -0.0086212 | 0.012232 | 0.052408 | 0.0040566 | 0.0042555 | -0.00013244 | -0.0065752 | -0.00068649 | -0.0034308 | 0.0057102 | -0.0051954 | -0.010053 | 0.021174 | 0.032043 | 0.050354 | 0.045776 | 0.10529 | 0.14648 | -0.036621 | -0.20599 | 0.027466 | 0.073242 | -0.054932 | 0.064087 | 0.045776 | -0.068665 | -0.11444 | 0.15564 | -0.013733 | -121.0144 | 0.24261 | 0.29755 | 0.31128 | -121.1288 | 0.1236 | 0.07782 | -121.0968 | 0.21973 | 0.13733 | 0.059509 | -121.1151 | 0.33874 | 0.2243 | 0.23804 | -121.3669 | 0.25635 | 0.23804 | 0.2655 | -121.2753
2515 | 121.2982 | -0.18768 | 121.1838 | -0.00099167 | 0.012659 | 0.05369 | 0.0049112 | 0.0019055 | -0.00013244 | -0.0040118 | 0.0069425 | -0.0019354 | 0.0050694 | -0.0028454 | -0.010267 | 0.02032 | 0.018311 | 0.013733 | 0.027466 | 0.091553 | 0.15106 | -0.027466 | -0.18768 | 0.041199 | 0.059509 | -0.050354 | 0.054932 | 0.045776 | -0.064087 | -0.13733 | 0.16022 | 0 | -121.0327 | 0.20142 | 0.27924 | 0.27924 | -121.1655 | 0.1236 | 0.050354 | -121.1288 | 0.22888 | 0.13733 | 0.086975 | -121.138 | 0.33874 | 0.20599 | 0.21515 | -121.3715 | 0.24261 | 0.23346 | 0.24719 | -121.3211
2516.6875 | 121.3074 | -0.20599 | 121.1655 | 0.014267 | 0.015864 | 0.05604 | 0.0074746 | 0.0021191 | 0.00072196 | -0.0035846 | 0.0069425 | -0.002149 | 0.003574 | -0.0017774 | -0.010694 | 0.019893 | -0.004578 | -0.045776 | -0.013733 | 0.050354 | 0.19226 | -0.045776 | -0.21973 | 0 | 0 | -0.091553 | 0.059509 | 0.036621 | -0.073242 | -0.14191 | 0.16022 | -0.013733 | -120.9732 | 0.16022 | 0.25635 | 0.27008 | -121.17 | 0.13275 | 0.064087 | -121.106 | 0.20599 | 0.11444 | 0.050354 | -121.1288 | 0.39826 | 0.20142 | 0.19226 | -121.3852 | 0.2655 | 0.24262 | 0.20599 | -121.3074
2518.4375 | 121.344 | -0.16937 | 121.1517 | -0.00099167 | 0.012232 | 0.053263 | 0.0083292 | 0.0025465 | -0.0048322 | -0.00508 | -0.00068649 | -0.003858 | 0.0067782 | -0.0034864 | -0.01283 | 0.021815 | 0.050354 | 0.068665 | 0.07782 | 0.13275 | 0.16937 | -0.032043 | -0.17853 | -0.009155 | 0.09613 | -0.054932 | 0.064087 | 0.045776 | -0.073242 | -0.15106 | 0.13733 | -0.009155 | -120.9824 | 0.23804 | 0.30212 | 0.31128 | -121.1014 | 0.096131 | 0.018311 | -121.0876 | 0.16022 | 0.11444 | 0.09613 | -121.106 | 0.33875 | 0.21973 | 0.24719 | -121.3303 | 0.23346 | 0.21515 | 0.2655 | -121.3028
2520.125 | 121.4081 | -0.16937 | 121.1563 | -0.00099167 | 0.015009 | 0.052195 | 0.0085428 | 0.0040417 | 0.003072 | -0.0065752 | 0.0069425 | -0.0025762 | 0.0084872 | -0.0022046 | -0.013044 | 0.016902 | -0.032043 | -0.064087 | -0.050354 | 0.054932 | 0.19684 | -0.059509 | -0.21973 | -0.07782 | -0.018311 | -0.15564 | 0.09613 | 0.073242 | -0.11902 | -0.17853 | 0.10986 | -0.050354 | -120.9595 | 0.10529 | 0.22431 | 0.27466 | -121.1884 | 0.050354 | -0.009155 | -121.0602 | 0.091553 | 0.013733 | 0.022888 | -121.0831 | 0.36621 | 0.13733 | 0.11902 | -121.376 | 0.2655 | 0.24261 | 0.15106 | -121.3348
2521.875 | 121.2845 | -0.20599 | 121.1838 | 0.014267 | 0.0075324 | 0.054972 | 0.0053384 | 0.0016919 | -0.0052594 | -0.0059344 | 0.0069425 | -0.003858 | 0.0061374 | -0.00070919 | -0.010908 | 0.022456 | 0 | 0.027466 | 0.054932 | 0.07782 | 0.15564 | -0.032043 | -0.1831 | -0.032043 | 0.032043 | -0.059509 | 0.054932 | 0.059509 | -0.073242 | -0.13733 | 0.17395 | 0.022889 | -121.0281 | 0.23346 | 0.28381 | 0.26092 | -121.1838 | 0.13275 | 0.068665 | -121.1288 | 0.17395 | 0.14649 | 0.07782 | -121.1243 | 0.36163 | 0.20599 | 0.26093 | -121.3669 | 0.26093 | 0.2655 | 0.23804 | -121.3211
2523.6094 | 121.344 | -0.17853 | 121.1609 | -0.00099167 | 0.010096 | 0.053904 | 0.0053384 | 0.0014783 | -0.00077324 | -0.0042254 | 0.0069425 | -0.0044988 | 0.0074192 | -0.0039136 | -0.011335 | 0.018397 | 0.032043 | 0.068665 | 0.045776 | 0.1236 | 0.14648 | -0.054932 | -0.19684 | -0.036621 | 0.054932 | -0.07782 | 0.082397 | 0.068665 | -0.10529 | -0.15564 | 0.1236 | -0.01831 | -121.0144 | 0.24719 | 0.30212 | 0.32043 | -121.1288 | 0.073242 | 0.022888 | -121.0785 | 0.14191 | 0.10071 | 0.07782 | -121.0922 | 0.32501 | 0.21057 | 0.2243 | -121.3577 | 0.26092 | 0.24719 | 0.23346 | -121.3165
2525.3594 | 121.4218 | -0.15564 | 121.17 | -0.00099167 | 0.010523 | 0.054972 | 0.0081154 | -1.714e-05 | -0.0014142 | -0.0076434 | -0.008316 | -0.006635 | 0.0050694 | -0.0043408 | -0.012617 | 0.02032 | 0.054932 | 0.10529 | 0.11444 | 0.14191 | 0.15564 | -0.036621 | -0.17853 | 0.041199 | 0.11902 | -0.013733 | 0.027466 | 0.027466 | -0.059509 | -0.12817 | 0.11902 | -0.022888 | -121.0144 | 0.26093 | 0.29755 | 0.32044 | -121.1151 | 0.096131 | 0.027466 | -121.1426 | 0.19684 | 0.14191 | 0.11444 | -121.1426 | 0.31128 | 0.21057 | 0.27008 | -121.3486 | 0.18311 | 0.18311 | 0.27466 | -121.2982
2527.0469 | 121.4035 | -0.16479 | 121.1792 | 0.0066373 | 0.011164 | 0.051554 | 0.0064066 | 0.0021191 | -0.0031232 | -0.0084978 | 0.0069425 | -0.0047124 | 0.00806 | -0.0026318 | -0.0096259 | 0.018611 | 0.064087 | 0.13275 | 0.10529 | 0.14648 | 0.14648 | -0.027466 | -0.17395 | 0.032043 | 0.11444 | -0.013733 | 0.064087 | 0.041199 | -0.064087 | -0.13275 | 0.13733 | -0.009155 | -121.0327 | 0.29755 | 0.31128 | 0.32043 | -121.1151 | 0.10071 | 0.032044 | -121.1151 | 0.19684 | 0.15106 | 0.11902 | -121.138 | 0.31128 | 0.22888 | 0.27008 | -121.3531 | 0.22888 | 0.20599 | 0.27924 | -121.3119
2528.7969 | 121.3211 | -0.21973 | 121.225 | -0.0086212 | 0.013941 | 0.049204 | 0.003843 | 0.0021191 | 0.005849 | -0.0042254 | -0.00068649 | -1.2844e-05 | 0.0076328 | -0.0026318 | -0.0081305 | 0.018824 | -0.036621 | -0.07782 | -0.064087 | 0.041199 | 0.19684 | -0.059509 | -0.2243 | -0.041199 | -0.07782 | -0.17395 | 0.10986 | 0.086975 | -0.091553 | -0.17395 | 0.16022 | -0.004577 | -121.0281 | 0.14191 | 0.26093 | 0.2655 | -121.2616 | 0.12817 | 0.045777 | -121.1151 | 0.17853 | 0.045777 | 0 | -121.138 | 0.41657 | 0.18311 | 0.15564 | -121.4493 | 0.32959 | 0.3067 | 0.14191 | -121.3989
2530.5625 | 121.344 | -0.18768 | 121.2021 | -0.00099167 | 0.01095 | 0.055613 | 0.007261 | 0.0044691 | -0.0024822 | -0.0059344 | 0.0069425 | -0.0070624 | 0.005283 | -0.0039136 | -0.013898 | 0.020747 | 0 | 0.041199 | 0.045776 | 0.086975 | 0.15564 | -0.041199 | -0.17853 | -0.018311 | 0.027466 | -0.082397 | 0.064087 | 0.064087 | -0.073242 | -0.12817 | 0.14648 | 0.009155 | -121.0464 | 0.22888 | 0.27466 | 0.2655 | -121.2021 | 0.11444 | 0.059509 | -121.138 | 0.16937 | 0.10529 | 0.045777 | -121.138 | 0.34332 | 0.18768 | 0.23346 | -121.3806 | 0.25177 | 0.25177 | 0.21515 | -121.3303
2532.3125 | 121.3989 | -0.19684 | 121.2387 | 0.0066373 | 0.011378 | 0.052408 | 0.0029886 | 0.0051099 | 0.004781 | -0.003371 | -0.00068649 | 0.00062796 | 0.0065646 | 0.00035881 | -0.01048 | 0.018611 | -0.004578 | -0.050354 | -0.041199 | 0.059509 | 0.18768 | -0.064087 | -0.21515 | -0.022888 | -0.036621 | -0.14648 | 0.086975 | 0.068665 | -0.091553 | -0.16022 | 0.13275 | -0.018311 | -121.051 | 0.14648 | 0.25635 | 0.27466 | -121.2433 | 0.10529 | 0.036621 | -121.1517 | 0.17395 | 0.050354 | 0.013733 | -121.17 | 0.38452 | 0.19226 | 0.15564 | -121.4539 | 0.28381 | 0.2655 | 0.16022 | -121.3989
2534 | 121.3898 | -0.19226 | 121.225 | -0.00099167 | 0.011805 | 0.049204 | 0.0046976 | 0.0042555 | 0.0020038 | -0.00273 | 0.0069425 | -0.0023626 | 0.006992 | -0.0037 | -0.0096259 | 0.019252 | 0.009155 | -0.009155 | 0 | 0.068665 | 0.16022 | -0.036621 | -0.19226 | 0.036621 | 0.050354 | -0.073242 | 0.059509 | 0.045776 | -0.082397 | -0.1236 | 0.15564 | 0 | -121.0648 | 0.18311 | 0.26093 | 0.26093 | -121.2158 | 0.10986 | 0.068665 | -121.1655 | 0.22888 | 0.11902 | 0.050354 | -121.1792 | 0.35248 | 0.20142 | 0.19226 | -121.4172 | 0.25177 | 0.23804 | 0.24261 | -121.3486
2535.6875 | 121.431 | -0.16479 | 121.2067 | 0.0066373 | 0.0090278 | 0.055185 | 0.007261 | 0.0036145 | -0.0048322 | -0.0065752 | 0.0069425 | -0.005567 | 0.006351 | -0.0028454 | -0.014112 | 0.021601 | 0.050354 | 0.086975 | 0.091553 | 0.1236 | 0.15106 | -0.036621 | -0.19226 | 0.041199 | 0.10986 | 0.004578 | 0.054932 | 0.036621 | -0.064087 | -0.1236 | 0.12817 | -0.027466 | -121.0556 | 0.25177 | 0.28839 | 0.31586 | -121.1563 | 0.10071 | 0.041199 | -121.1517 | 0.20599 | 0.16937 | 0.12817 | -121.17 | 0.31586 | 0.21515 | 0.25635 | -121.3989 | 0.21973 | 0.20142 | 0.27466 | -121.3303
2537.4375 | 121.4401 | -0.19684 | 121.2021 | -0.00099167 | 0.012446 | 0.05604 | 0.010038 | 0.0021191 | -0.00034604 | -0.0057208 | 0.0069425 | -0.0027898 | 0.0061374 | -0.0024182 | -0.012189 | 0.019038 | 0.036621 | 0.059509 | 0.036621 | 0.10071 | 0.15564 | -0.059509 | -0.21057 | -0.045776 | 0.027466 | -0.10986 | 0.073242 | 0.068665 | -0.086975 | -0.15564 | 0.13733 | -0.013733 | -121.0464 | 0.25635 | 0.29755 | 0.31128 | -121.1655 | 0.10986 | 0.041198 | -121.1288 | 0.15106 | 0.086975 | 0.045777 | -121.1334 | 0.35248 | 0.23346 | 0.23346 | -121.4127 | 0.27008 | 0.2655 | 0.2243 | -121.3577
2539.125 | 121.4447 | -0.17395 | 121.2433 | 0.014267 | 0.014796 | 0.049631 | 0.0061928 | 0.0046827 | 0.0060626 | -0.003371 | 0.014572 | -0.00022644 | 0.0078464 | -0.0024182 | -0.0091985 | 0.018611 | 0.041199 | 0.032043 | 0.013733 | 0.091553 | 0.16479 | -0.054932 | -0.21973 | -0.018311 | 0.018311 | -0.13733 | 0.059509 | 0.068665 | -0.086975 | -0.16937 | 0.11902 | -0.045777 | -121.0785 | 0.20599 | 0.2655 | 0.31128 | -121.2021 | 0.086975 | 0.004577 | -121.1838 | 0.15564 | 0.036621 | 0.032044 | -121.1746 | 0.33874 | 0.21515 | 0.18768 | -121.463 | 0.23346 | 0.24261 | 0.19226 | -121.4127
2540.8125 | 120.8176 | -0.21515 | 120.7443 | -0.00099167 | 0.012873 | 0.052622 | 0.0053384 | 0.0036145 | 0.00414 | -0.00273 | -0.00068649 | -0.0010808 | 0.0074192 | -0.0017774 | -0.0079169 | 0.019679 | -0.054932 | -0.09613 | -0.086975 | 0.032043 | 0.19226 | -0.064087 | -0.22888 | -0.041199 | -0.07782 | -0.17395 | 0.086975 | 0.073242 | -0.1236 | -0.16937 | 0.15106 | -0.013733 | -120.5521 | 0.11902 | 0.24719 | 0.26093 | -120.7993 | 0.091553 | 0.045776 | -120.6573 | 0.17395 | 0.041199 | -0.004577 | -120.6711 | 0.40741 | 0.16022 | 0.12817 | -120.9732 | 0.30212 | 0.28839 | 0.13733 | -120.9137
2542.5625 | 120.9915 | -0.1831 | 120.9045 | -0.00099167 | 0.012659 | 0.051554 | 0.0079018 | 0.0029737 | -0.00055964 | -0.0037982 | 0.014572 | -0.0040716 | 0.0067782 | -0.0037 | -0.010908 | 0.020961 | 0.054932 | 0.091553 | 0.10071 | 0.12817 | 0.11444 | -0.027466 | -0.16479 | 0.032043 | 0.091553 | -0.013733 | 0.050354 | 0.045776 | -0.059509 | -0.13275 | 0.15564 | 0.01831 | -120.7901 | 0.27466 | 0.31128 | 0.29297 | -120.8496 | 0.1236 | 0.050354 | -120.8542 | 0.21515 | 0.16937 | 0.11902 | -120.8588 | 0.29755 | 0.23804 | 0.28381 | -121.0693 | 0.23346 | 0.22888 | 0.27466 | -121.0373
2544.2656 | 121.1884 | -0.14191 | 120.8908 | -0.00099167 | 0.012018 | 0.054117 | 0.0074746 | 0.0023327 | -0.0044048 | -0.0040118 | -0.008316 | -0.0049262 | 0.0054966 | -0.0028454 | -0.013685 | 0.021388 | 0.064087 | 0.11444 | 0.10071 | 0.14191 | 0.13733 | -0.045776 | -0.1831 | 0.045776 | 0.14191 | 0.013733 | 0.022888 | 0.059509 | -0.068665 | -0.12817 | 0.096131 | -0.041198 | -120.7535 | 0.25635 | 0.28381 | 0.32501 | -120.8267 | 0.073242 | 0.013733 | -120.8679 | 0.18768 | 0.15564 | 0.14191 | -120.8313 | 0.27924 | 0.20599 | 0.24262 | -121.0739 | 0.16479 | 0.20142 | 0.28381 | -121.019
2546.0312 | 121.0831 | -0.18768 | 121.0098 | 0.0066373 | 0.010096 | 0.054117 | 0.0040566 | 0.0023327 | 0.00093576 | -0.0046526 | -0.00068649 | -0.0030034 | 0.0061374 | -0.0028454 | -0.0091985 | 0.019893 | 0.073242 | 0.082397 | 0.082397 | 0.13275 | 0.11902 | -0.032043 | -0.1831 | 0.041199 | 0.07782 | -0.032043 | 0.032043 | 0.041199 | -0.064087 | -0.13733 | 0.15564 | 0.004578 | -120.8908 | 0.27008 | 0.32043 | 0.31586 | -120.9366 | 0.1236 | 0.050354 | -120.9778 | 0.22888 | 0.15564 | 0.10529 | -120.9686 | 0.3067 | 0.26092 | 0.27008 | -121.1929 | 0.21973 | 0.22888 | 0.2655 | -121.1472
2547.7188 | 121.1243 | -0.19226 | 121.0144 | 0.0066373 | 0.013727 | 0.051554 | 0.0051248 | 0.0029737 | 0.0071308 | -0.0046526 | 0.0069425 | -1.2844e-05 | 0.006351 | -0.00028199 | -0.0085577 | 0.017543 | 0.018311 | -0.004578 | -0.022888 | 0.050354 | 0.17853 | -0.054932 | -0.21515 | -0.041199 | -0.032043 | -0.17853 | 0.091553 | 0.082397 | -0.11444 | -0.16022 | 0.13733 | -0.022888 | -120.8359 | 0.18768 | 0.24261 | 0.2655 | -120.9961 | 0.07782 | 0.032044 | -120.9229 | 0.15106 | 0.013733 | -0.018311 | -120.932 | 0.37079 | 0.21057 | 0.16937 | -121.2296 | 0.28381 | 0.27466 | 0.16022 | -121.1746
2549.4688 | 121.1517 | -0.20599 | 121.0693 | 0.0066373 | 0.0064642 | 0.053049 | 0.0066202 | 0.0027601 | -0.0022686 | -0.0029436 | -0.00068649 | -0.0040716 | 0.0065646 | -0.003059 | -0.013258 | 0.024165 | 0.009155 | 0.045776 | 0.059509 | 0.086975 | 0.16022 | -0.045776 | -0.17853 | -0.004578 | 0.041199 | -0.050354 | 0.050354 | 0.050354 | -0.073242 | -0.13275 | 0.16022 | 0.027466 | -120.9091 | 0.25177 | 0.29297 | 0.2655 | -121.0602 | 0.13275 | 0.073243 | -121.019 | 0.20142 | 0.15564 | 0.082397 | -121.019 | 0.36621 | 0.21515 | 0.2655 | -121.2479 | 0.25635 | 0.25635 | 0.24719 | -121.2021
2551.1719 | 121.2433 | -0.16937 | 121.051 | 0.0066373 | 0.013727 | 0.053476 | 0.0049112 | 0.0010511 | -0.002055 | -0.0065752 | 0.014572 | -0.0025762 | 0.006351 | -0.0056226 | -0.011335 | 0.019893 | 0.050354 | 0.10986 | 0.10071 | 0.1236 | 0.14191 | -0.036621 | -0.19684 | 0.013733 | 0.11902 | -0.027466 | 0.068665 | 0.036621 | -0.073242 | -0.13275 | 0.13275 | -0.027465 | -120.9091 | 0.27924 | 0.29297 | 0.32043 | -121.0007 | 0.096131 | 0.036622 | -120.9824 | 0.18311 | 0.14191 | 0.10529 | -121.0144 | 0.31128 | 0.21973 | 0.27008 | -121.2479 | 0.23804 | 0.20599 | 0.28839 | -121.1838
2552.9219 | 121.2799 | -0.14648 | 121.0556 | 0.014267 | 0.011805 | 0.050058 | 0.0046976 | 0.0051099 | 0.0054218 | -0.0035846 | -0.00068649 | -0.00022644 | 0.0095554 | 0.00014521 | -0.0072759 | 0.017543 | 0.027466 | 0.009155 | 0 | 0.09613 | 0.17853 | -0.054932 | -0.21973 | -0.013733 | 0.022888 | -0.13275 | 0.07782 | 0.073242 | -0.10071 | -0.14648 | 0.091552 | -0.073243 | -120.8771 | 0.15564 | 0.24261 | 0.31586 | -121.0281 | 0.045776 | 0 | -120.9778 | 0.13275 | 0.013733 | 0.013733 | -120.9824 | 0.32501 | 0.17395 | 0.14648 | -121.2753 | 0.2243 | 0.21973 | 0.16937 | -121.2021
2554.6875 | 120.4056 | -5.2185 | 115.1596 | -0.00099167 | 0.012232 | 0.056894 | 0.0074746 | 0.0021191 | -0.0041912 | -0.0070026 | 0.0069425 | -0.003858 | 0.005283 | -0.0058362 | -0.011762 | 0.020533 | 0.054932 | 0.11902 | 0.10071 | 0.13275 | 0.16022 | -0.022888 | -0.17853 | 0.027466 | 0.14191 | -0.013733 | 0.059509 | 0.050354 | -0.059509 | -0.13733 | 5.1956 | 5.04 | -114.9994 | 5.3375 | 5.3513 | 0.31128 | -115.1047 | 5.159 | 5.0812 | -115.1001 | 5.246 | 5.2048 | 0.1236 | -115.1093 | 5.3787 | 5.2734 | 5.3192 | -115.3381 | 5.278 | 5.2689 | 5.3604 | -115.2969
2556.375 | 120.6162 | -6.5094 | 115.2878 | -0.00099167 | 0.0083868 | 0.054758 | 0.0046976 | 0.00083746 | -0.00098684 | -0.0070026 | 0.014572 | -0.0059942 | 0.0059238 | -0.0037 | -0.010908 | 0.021388 | 0.027466 | 0.059509 | 0.073242 | 0.10071 | 0.13275 | -0.032043 | -0.1831 | -0.004578 | 0.045776 | -0.059509 | 0.045776 | 0.045776 | -0.07782 | -0.12817 | 6.4774 | 6.3263 | -115.155 | 6.5689 | 6.6101 | 0.28381 | -115.2603 | 6.4316 | 6.3812 | -115.242 | 6.5048 | 6.4499 | 0.068665 | -115.242 | 6.6421 | 6.5369 | 6.5826 | -115.4709 | 6.5552 | 6.5552 | 6.5552 | -115.416
2558.125 | 120.6802 | -6.6605 | 114.0427 | 0.0066373 | 0.014368 | 0.051981 | 0.0079018 | 0.0025465 | 0.0073444 | -0.0048662 | 0.014572 | -1.2844e-05 | 0.0076328 | -0.0015638 | -0.0074897 | 0.017329 | 0.054932 | 0.022888 | 0.004578 | 0.086975 | 0.19226 | -0.064087 | -0.21515 | -0.022888 | 0.022888 | -0.13275 | 0.086975 | 0.059509 | -0.086975 | -0.16022 | 6.5964 | 6.4453 | -113.8504 | 6.6833 | 6.7474 | 0.30212 | -113.9877 | 6.5735 | 6.5002 | -113.9557 | 6.6376 | 6.5277 | 0.027466 | -113.9832 | 6.8527 | 6.7154 | 6.665 | -114.2578 | 6.7474 | 6.72 | 6.6833 | -114.2029
2559.875 | 120.8176 | -7.0312 | 113.6719 | 0.014267 | 0.012446 | 0.053263 | 0.0096108 | 0.0031873 | -0.0033368 | -0.0046526 | 0.022202 | -0.0053534 | 0.0059238 | -0.003059 | -0.014112 | 0.020106 | 0.036621 | 0.13275 | 0.091553 | 0.14191 | 0.15106 | -0.027466 | -0.1831 | 0.032043 | 0.11902 | 0.004578 | 0.054932 | 0.032043 | -0.082397 | -0.12817 | 7.0038 | 6.8481 | -113.5208 | 7.164 | 7.1732 | 0.32501 | -113.6353 | 6.9489 | 6.9031 | -113.6169 | 7.0633 | 7.0358 | 0.13275 | -113.6398 | 7.1823 | 7.0679 | 7.1228 | -113.855 | 7.0862 | 7.0633 | 7.1503 | -113.8
2561.5469 | 120.7397 | -6.7337 | 114.1159 | 0.0066373 | 0.015223 | 0.053904 | 0.0053384 | 0.0038281 | 0.0037128 | -0.003371 | 0.014572 | 0.00062796 | 0.0057102 | -0.00070919 | -0.0055671 | 0.019038 | -0.036621 | -0.045776 | -0.068665 | 0.054932 | 0.20142 | -0.07782 | -0.20599 | -0.068665 | -0.054932 | -0.19684 | 0.091553 | 0.07782 | -0.10986 | -0.15564 | 6.6559 | 6.5277 | -113.9145 | 6.6879 | 6.7886 | 0.26093 | -114.1525 | 6.6238 | 6.5781 | -114.0244 | 6.665 | 6.5369 | -0.041198 | -114.0381 | 6.9351 | 6.6971 | 6.665 | -114.3219 | 6.8253 | 6.8115 | 6.6788 | -114.2715
2563.2969 | 120.8359 | -6.0287 | 114.8163 | 0.0066373 | 0.014155 | 0.05369 | 0.010252 | 0.0051099 | 8.1158e-05 | -0.0048662 | 0.014572 | -0.0034308 | 0.0078464 | -0.00070919 | -0.011976 | 0.02032 | -0.041199 | -0.004578 | -0.009155 | 0.050354 | 0.1831 | -0.064087 | -0.21515 | -0.07782 | 0.009155 | -0.13733 | 0.091553 | 0.082397 | -0.10986 | -0.1831 | 5.9647 | 5.8136 | -114.6332 | 6.0242 | 6.0791 | 0.2655 | -114.8575 | 5.9189 | 5.8456 | -114.7247 | 5.9509 | 5.8914 | 0.045776 | -114.7339 | 6.2119 | 5.9875 | 6.0196 | -115.0314 | 6.1203 | 6.1111 | 6.0379 | -114.9994
2564.9844 | 120.7855 | -6.8436 | 114.0427 | 0.0066373 | 0.015009 | 0.050486 | 0.0053384 | 0.0036145 | 0.0039264 | -0.0046526 | 0.014572 | 0.00020076 | 0.0095554 | -0.00070919 | -0.0085577 | 0.019252 | -0.041199 | -0.059509 | -0.054932 | 0.036621 | 0.19684 | -0.073242 | -0.21515 | -0.07782 | -0.07782 | -0.20142 | 0.073242 | 0.091553 | -0.10071 | -0.16022 | 6.7703 | 6.6284 | -113.8458 | 6.7841 | 6.8802 | 0.25177 | -114.0839 | 6.7429 | 6.6833 | -113.9694 | 6.7657 | 6.6422 | -0.041199 | -113.9511 | 7.0404 | 6.8024 | 6.7886 | -114.2578 | 6.9168 | 6.9351 | 6.7657 | -114.2029
2566.7344 | 120.8221 | -7.3517 | 113.5803 | -0.00099167 | 0.011164 | 0.054117 | 0.0064066 | 0.0025465 | -0.00098684 | -0.0042254 | -0.00068649 | -0.003858 | 0.0059238 | -0.0034864 | -0.012403 | 0.022242 | 0.032043 | 0.09613 | 0.082397 | 0.10529 | 0.12817 | -0.041199 | -0.15564 | 0.018311 | 0.068665 | -0.027466 | 0.041199 | 0.045776 | -0.082397 | -0.13733 | 7.3105 | 7.196 | -113.4521 | 7.4478 | 7.457 | 0.26093 | -113.5483 | 7.2693 | 7.2144 | -113.5391 | 7.37 | 7.3242 | 0.10986 | -113.5345 | 7.4799 | 7.3837 | 7.4341 | -113.736 | 7.3929 | 7.3975 | 7.4204 | -113.7177
2568.4844 | 120.8588 | -7.4203 | 113.5529 | 0.0066373 | 0.013727 | 0.052622 | 0.0040566 | 0.0029737 | 0.0062762 | -0.0037982 | 0.0069425 | 0.00084176 | 0.0057102 | -0.0015638 | -0.0074897 | 0.02032 | -0.054932 | -0.07782 | -0.082397 | 0.036621 | 0.18768 | -0.07782 | -0.21973 | -0.050354 | -0.064087 | -0.16479 | 0.082397 | 0.091553 | -0.10071 | -0.16937 | 7.3425 | 7.2006 | -113.3652 | 7.3425 | 7.457 | 0.25635 | -113.6078 | 7.3196 | 7.251 | -113.4705 | 7.37 | 7.2556 | 0.004578 | -113.4613 | 7.608 | 7.3654 | 7.338 | -113.7726 | 7.5027 | 7.5119 | 7.3563 | -113.7222
2570.1719 | 120.9 | -7.3151 | 113.6581 | -0.0086212 | 0.0083868 | 0.055185 | 0.0046976 | 0.0010511 | -0.0052594 | -0.00508 | -0.00068649 | -0.007276 | 0.0050694 | -0.0051954 | -0.010694 | 0.023097 | -0.022888 | 0.036621 | 0.041199 | 0.086975 | 0.13733 | -0.022888 | -0.18768 | -0.009155 | 0.022888 | -0.041199 | 0.068665 | 0.054932 | -0.073242 | -0.14648 | 7.2922 | 7.1274 | -113.5208 | 7.3517 | 7.402 | 0.27466 | -113.681 | 7.2418 | 7.1686 | -113.5895 | 7.3059 | 7.2739 | 0.10529 | -113.6032 | 7.4524 | 7.2922 | 7.3563 | -113.8458 | 7.3837 | 7.37 | 7.338 | -113.8046
2571.875 | 121.0144 | -7.1594 | 113.7497 | -0.00099167 | 0.012446 | 0.05369 | 0.0059792 | 0.0036145 | 0.0020038 | -0.006148 | 0.0069425 | -0.0025762 | 0.006992 | -0.0017774 | -0.0096259 | 0.018611 | -0.045776 | -0.045776 | -0.041199 | 0.041199 | 0.20142 | -0.07782 | -0.2243 | -0.07782 | -0.022888 | -0.15106 | 0.09613 | 0.082397 | -0.10071 | -0.19684 | 7.0816 | 6.9351 | -113.5483 | 7.1136 | 7.2006 | 0.2655 | -113.7955 | 7.0587 | 6.9626 | -113.6536 | 7.0816 | 7.0084 | 0.045776 | -113.6673 | 7.3608 | 7.1136 | 7.1182 | -113.974 | 7.2556 | 7.2418 | 7.1365 | -113.9465
2573.6406 | 120.9869 | -7.0679 | 113.9099 | 0.0066373 | 0.010523 | 0.050913 | 0.0074746 | 0.0040417 | 0.0011494 | -0.00508 | -0.00068649 | -0.003858 | 0.0065646 | -0.0022046 | -0.0094123 | 0.020961 | 0.064087 | 0.082397 | 0.068665 | 0.12817 | 0.16022 | 0.004578 | -0.17853 | 0.045776 | 0.07782 | -0.045776 | 0.036621 | 0.018311 | -0.068665 | -0.09613 | 7.0724 | 6.8893 | -113.7497 | 7.1503 | 7.196 | 0.3067 | -113.8458 | 6.9992 | 6.9717 | -113.8733 | 7.1136 | 7.0221 | 0.050354 | -113.8916 | 7.2281 | 7.132 | 7.1365 | -114.0884 | 7.1045 | 7.0862 | 7.1457 | -114.006
2575.3906 | 121.0648 | -5.6122 | 115.416 | 0.0066373 | 0.011378 | 0.051554 | 0.0034158 | 0.0055371 | 0.0028584 | -0.0029436 | 0.022202 | -0.0012946 | 0.006351 | -0.0013502 | -0.0096259 | 0.019893 | 0.013733 | 0.018311 | -0.004578 | 0.09613 | 0.18768 | -0.054932 | -0.20599 | -0.018311 | 0.045776 | -0.10529 | 0.064087 | 0.086975 | -0.086975 | -0.15106 | 5.5573 | 5.4062 | -115.2283 | 5.6305 | 5.7083 | 0.30212 | -115.4022 | 5.5252 | 5.4611 | -115.3519 | 5.5939 | 5.5069 | 0.045776 | -115.329 | 5.7999 | 5.6259 | 5.6076 | -115.6219 | 5.6763 | 5.6992 | 5.658 | -115.567
2577.1094 | 120.9595 | -6.4957 | 114.5828 | 0.0066373 | 0.013727 | 0.053263 | 0.007261 | 0.0057507 | 0.0011494 | -0.0048662 | 0.0069425 | -0.00044004 | 0.0050694 | -0.0015638 | -0.0083441 | 0.018184 | 0.018311 | -0.004578 | -0.013733 | 0.086975 | 0.18768 | -0.054932 | -0.2243 | -0.045776 | -0.004578 | -0.14648 | 0.10529 | 0.086975 | -0.09613 | -0.16022 | 6.4407 | 6.2714 | -114.3951 | 6.4911 | 6.5826 | 0.31128 | -114.5645 | 6.3995 | 6.3354 | -114.4775 | 6.4499 | 6.3492 | 0.013733 | -114.4959 | 6.6833 | 6.514 | 6.4819 | -114.8071 | 6.601 | 6.5826 | 6.4911 | -114.743
2578.8594 | 121.0739 | -6.7383 | 114.2715 | 0.0066373 | 0.0075324 | 0.052408 | 0.007261 | 0.0025465 | -0.0035504 | -0.0048662 | -0.00068649 | -0.0053534 | 0.0059238 | -0.0039136 | -0.014753 | 0.021601 | 0.041199 | 0.11444 | 0.09613 | 0.12817 | 0.13733 | -0.032043 | -0.18768 | 0.018311 | 0.12817 | -0.022888 | 0.041199 | 0.045776 | -0.068665 | -0.13275 | 6.7062 | 6.5506 | -114.1342 | 6.8527 | 6.8665 | 0.31586 | -114.2303 | 6.6696 | 6.6055 | -114.2303 | 6.7566 | 6.7154 | 0.10986 | -114.2258 | 6.8756 | 6.7795 | 6.8344 | -114.4592 | 6.7795 | 6.7841 | 6.8665 | -114.4043
2580.5469 | 121.0693 | -6.8893 | 114.1434 | 0.0066373 | 0.012446 | 0.051554 | 0.0098244 | 0.0038281 | -0.0035504 | -0.004439 | 0.0069425 | -0.0049262 | 0.0074192 | -0.0015638 | -0.014112 | 0.020747 | 0.018311 | 0.068665 | 0.082397 | 0.13275 | 0.14191 | -0.022888 | -0.18768 | -0.013733 | 0.073242 | -0.068665 | 0.073242 | 0.064087 | -0.07782 | -0.15106 | 6.8665 | 6.7017 | -114.0015 | 6.958 | 7.0221 | 0.32043 | -114.1251 | 6.8115 | 6.7383 | -114.0701 | 6.8756 | 6.8207 | 0.082397 | -114.0793 | 7.0312 | 6.9077 | 6.9717 | -114.3311 | 6.9626 | 6.9534 | 6.9626 | -114.2944
2582.2969 | 121.1472 | -12.0575 | 108.9203 | -0.0086212 | 0.013514 | 0.050272 | 0.0091836 | 0.0014783 | 0.0043536 | -0.0048662 | 0.0069425 | 0.00020076 | 0.00806 | -0.00028199 | -0.011121 | 0.01797 | -0.041199 | -0.027466 | -0.032043 | 0.073242 | 0.17853 | -0.059509 | -0.21973 | -0.022888 | 0.018311 | -0.12817 | 0.07782 | 0.082397 | -0.091553 | -0.16937 | 11.998 | 11.8378 | -108.7418 | 12.03 | 12.1307 | 0.29297 | -108.9615 | 11.9659 | 11.8881 | -108.8425 | 12.0346 | 11.9293 | 0.041199 | -108.8379 | 12.236 | 12.0163 | 12.0255 | -109.14 | 12.1353 | 12.1399 | 12.0758 | -109.0897
2584.0469 | 121.0693 | -9.7366 | 111.3373 | 0.0066373 | 0.010737 | 0.054544 | 0.007261 | 0.0040417 | -0.0052594 | -0.0065752 | -0.015945 | -0.0059942 | 0.006992 | -0.0043408 | -0.013685 | 0.019252 | -0.036621 | 0.022888 | 0.045776 | 0.091553 | 0.15564 | -0.045776 | -0.18768 | 0 | 0.050354 | -0.032043 | 0.073242 | 0.054932 | -0.07782 | -0.15564 | 9.6909 | 9.5489 | -111.1816 | 9.7595 | 9.8282 | 0.27924 | -111.3739 | 9.6588 | 9.581 | -111.264 | 9.7366 | 9.7046 | 0.1236 | -111.2823 | 9.8923 | 9.7 | 9.7824 | -111.525 | 9.8099 | 9.7916 | 9.787 | -111.4929
2585.8125 | 121.0602 | -7.1091 | 114.0427 | 0.014267 | 0.011805 | 0.054331 | 0.0044838 | 0.0040417 | 0.0017902 | -0.0031574 | -0.00068649 | -0.0042852 | 0.0054966 | -0.0026318 | -0.0066351 | 0.017543 | 0.086975 | 0.068665 | 0.07782 | 0.1236 | 0.14191 | -0.022888 | -0.1831 | 0.032043 | 0.068665 | -0.032043 | 0.032043 | 0.045776 | -0.073242 | -0.11902 | 7.0862 | 6.926 | -113.9008 | 7.1777 | 7.2327 | 0.3067 | -113.9557 | 7.0358 | 6.9901 | -114.0106 | 7.1411 | 7.077 | 0.086976 | -113.9969 | 7.251 | 7.196 | 7.1869 | -114.2258 | 7.1411 | 7.1548 | 7.1777 | -114.1617
2587.5625 | 121.1884 | -8.4091 | 112.6785 | -0.00099167 | 0.016077 | 0.052622 | 0.0064066 | 0.0048963 | 0.002431 | -0.0065752 | 0.0069425 | -0.003858 | 0.0099826 | -0.0013502 | -0.010908 | 0.017756 | -0.041199 | -0.054932 | -0.045776 | 0.054932 | 0.20142 | -0.082397 | -0.23804 | -0.073242 | -0.018311 | -0.14648 | 0.09613 | 0.086975 | -0.10071 | -0.17395 | 8.3267 | 8.1711 | -112.4771 | 8.3542 | 8.4641 | 0.29297 | -112.7197 | 8.3084 | 8.2352 | -112.5824 | 8.3359 | 8.2626 | 0.027466 | -112.5916 | 8.6105 | 8.3679 | 8.3633 | -112.9166 | 8.5052 | 8.4961 | 8.3908 | -112.8525
2589.25 | 121.2112 | -6.5598 | 114.4867 | 0.0066373 | 0.012659 | 0.055185 | 0.0083292 | 0.0042555 | -0.0046184 | -0.004439 | 0.0069425 | -0.0040716 | 0.006992 | -0.0026318 | -0.014112 | 0.018397 | 0.041199 | 0.12817 | 0.10529 | 0.14191 | 0.15106 | -0.027466 | -0.1831 | 0.027466 | 0.1236 | 0 | 0.032043 | 0.036621 | -0.07782 | -0.12817 | 6.5323 | 6.3766 | -114.3356 | 6.6879 | 6.7017 | 0.32501 | -114.4455 | 6.4819 | 6.4316 | -114.4547 | 6.5872 | 6.5598 | 0.12817 | -114.4501 | 6.7108 | 6.601 | 6.665 | -114.6698 | 6.5918 | 6.5964 | 6.6833 | -114.6149
2591.0156 | 121.0693 | -8.2718 | 112.9211 | 0.0066373 | 0.01095 | 0.053049 | 0.0083292 | 0.0038281 | -0.00098684 | -0.0055072 | 0.0069425 | -0.0044988 | 0.0078464 | -0.003059 | -0.012403 | 0.018611 | 0 | 0.045776 | 0.036621 | 0.091553 | 0.16022 | 0 | -0.18768 | 0.013733 | 0.032043 | -0.054932 | 0.073242 | 0.054932 | -0.073242 | -0.14191 | 8.2718 | 8.0841 | -112.7609 | 8.3176 | 8.3633 | 0.27924 | -112.9211 | 8.1985 | 8.1299 | -112.8479 | 8.2855 | 8.2169 | 0.086975 | -112.8662 | 8.432 | 8.2718 | 8.3084 | -113.1088 | 8.345 | 8.3267 | 8.3038 | -113.0631
2592.7656 | 121.1334 | -8.2031 | 112.9898 | 0.0066373 | 0.015223 | 0.050913 | 0.005552 | 0.0021191 | 0.0054218 | -0.0035846 | 0.0069425 | -0.00086724 | 0.0084872 | 0.00035881 | -0.0083441 | 0.017543 | 0.018311 | 0.041199 | 0.009155 | 0.07782 | 0.16937 | -0.041199 | -0.21515 | -0.027466 | 0.009155 | -0.14648 | 0.086975 | 0.059509 | -0.09613 | -0.16937 | 8.1619 | 7.988 | -112.8204 | 8.2443 | 8.2809 | 0.29297 | -112.9715 | 8.107 | 8.0338 | -112.9028 | 8.1757 | 8.0566 | 0.022889 | -112.9303 | 8.3725 | 8.2214 | 8.2123 | -113.205 | 8.2901 | 8.2626 | 8.2123 | -113.1592
2594.5156 | 121.1975 | -6.958 | 114.1846 | -0.0086212 | 0.012659 | 0.052195 | 0.0083292 | 0.0029737 | -0.0031232 | -0.0040118 | 0.014572 | -0.003858 | 0.0065646 | -0.0022046 | -0.013471 | 0.02032 | 0.022888 | 0.09613 | 0.054932 | 0.10986 | 0.14648 | -0.050354 | -0.18768 | -0.027466 | 0.050354 | -0.091553 | 0.064087 | 0.064087 | -0.086975 | -0.15106 | 6.9077 | 6.7703 | -114.0381 | 7.0541 | 7.0679 | 0.29755 | -114.1617 | 6.871 | 6.8069 | -114.1205 | 6.9305 | 6.8665 | 0.059509 | -114.1205 | 7.1045 | 6.9809 | 7.0129 | -114.3723 | 7.0221 | 7.0221 | 7.0084 | -114.3356
2596.2188 | 121.2067 | -6.8985 | 114.2853 | 0.0066373 | 0.012873 | 0.053049 | 0.0098244 | 0.0038281 | 0.00050836 | -0.0063616 | -0.00068649 | -0.0036444 | 0.006992 | -0.001991 | -0.010908 | 0.019679 | -0.054932 | 0 | -0.036621 | 0.036621 | 0.18768 | -0.068665 | -0.2243 | -0.091553 | -0.022888 | -0.15564 | 0.11902 | 0.073242 | -0.1236 | -0.17395 | 6.8298 | 6.6742 | -114.0976 | 6.8985 | 6.9351 | 0.26093 | -114.3402 | 6.7749 | 6.7245 | -114.1663 | 6.8069 | 6.7429 | 0.01831 | -114.212 | 7.0862 | 6.8436 | 6.8619 | -114.5096 | 7.0175 | 6.9717 | 6.8756 | -114.4592
2597.9688 | 121.1426 | -5.5023 | 115.7089 | 0.0066373 | 0.011805 | 0.051554 | 0.0040566 | 0.0036145 | 0.0011494 | -0.0057208 | -0.00068649 | -0.0051398 | 0.0072056 | -0.0015638 | -0.0079169 | 0.019679 | 0.050354 | 0.091553 | 0.073242 | 0.13733 | 0.15106 | -0.022888 | -0.16937 | 0.054932 | 0.09613 | -0.036621 | 0.041199 | 0.027466 | -0.07782 | -0.11444 | 5.4794 | 5.3329 | -115.5579 | 5.5939 | 5.6396 | 0.3067 | -115.6586 | 5.4245 | 5.3879 | -115.6677 | 5.5573 | 5.4657 | 0.07782 | -115.6815 | 5.6534 | 5.5527 | 5.5756 | -115.8783 | 5.5435 | 5.5298 | 5.5984 | -115.8234
2599.6719 | 121.2524 | -6.6788 | 114.5004 | 0.014267 | 0.0133 | 0.054331 | 0.0079018 | 0.0027601 | 0.0032856 | -0.001662 | -0.00068649 | 0.00084176 | 0.0089146 | -0.0013502 | -0.0098395 | 0.018611 | -0.018311 | -0.013733 | -0.032043 | 0.073242 | 0.19226 | -0.059509 | -0.21973 | -0.018311 | 0.013733 | -0.1236 | 0.10071 | 0.082397 | -0.09613 | -0.15564 | 6.6193 | 6.459 | -114.3082 | 6.665 | 6.752 | 0.29297 | -114.5187 | 6.5826 | 6.5231 | -114.3997 | 6.6605 | 6.5552 | 0.032044 | -114.418 | 6.871 | 6.6605 | 6.6467 | -114.7202 | 6.7795 | 6.7612 | 6.6925 | -114.6561
2601.4219 | 121.1243 | -6.2393 | 115.0452 | -0.00099167 | 0.0081732 | 0.053049 | 0.0023476 | 0.0021191 | -0.0024822 | -0.0042254 | 0.0069425 | -0.0040716 | 0.006992 | -0.0022046 | -0.010908 | 0.020106 | 0.036621 | 0.10529 | 0.091553 | 0.12817 | 0.13275 | -0.027466 | -0.16937 | 0.027466 | 0.068665 | -0.022888 | 0.045776 | 0.036621 | -0.073242 | -0.12817 | 6.2119 | 6.0699 | -114.9124 | 6.3446 | 6.3675 | 0.29755 | -115.0085 | 6.1661 | 6.1111 | -114.9994 | 6.2668 | 6.2164 | 0.10529 | -115.0085 | 6.3721 | 6.2759 | 6.3309 | -115.2145 | 6.2851 | 6.2759 | 6.308 | -115.1733
2603.1719 | 121.3028 | -6.5048 | 114.6744 | 0.014267 | 0.014368 | 0.053049 | 0.0053384 | 0.0044691 | 0.0039264 | -0.00508 | -0.00068649 | -0.0025762 | 0.0072056 | -0.00070919 | -0.0055671 | 0.020961 | -0.032043 | 0 | -0.032043 | 0.064087 | 0.1831 | -0.07782 | -0.2243 | -0.036621 | 0.009155 | -0.13275 | 0.10529 | 0.073242 | -0.10071 | -0.15106 | 6.427 | 6.2805 | -114.4913 | 6.5048 | 6.5689 | 0.28839 | -114.7064 | 6.4041 | 6.3538 | -114.5691 | 6.4682 | 6.3721 | 0.018311 | -114.6011 | 6.6879 | 6.4728 | 6.4728 | -114.8987 | 6.6101 | 6.5781 | 6.514 | -114.8254
2604.9219 | 121.2845 | -6.459 | 114.7385 | -0.00099167 | 0.0079596 | 0.053904 | 0.0093972 | 0.0025465 | -0.0046184 | -0.0087114 | 0.0069425 | -0.0064214 | 0.0065646 | -0.0026318 | -0.013471 | 0.020747 | -0.004578 | 0.045776 | 0.068665 | 0.10986 | 0.16022 | -0.032043 | -0.18768 | 0.009155 | 0.086975 | -0.013733 | 0.059509 | 0.032043 | -0.07782 | -0.14191 | 6.427 | 6.2714 | -114.5782 | 6.5048 | 6.5689 | 0.29755 | -114.743 | 6.3812 | 6.3171 | -114.679 | 6.4682 | 6.4453 | 0.12817 | -114.7064 | 6.6193 | 6.4545 | 6.5277 | -114.9261 | 6.5186 | 6.4911 | 6.546 | -114.8804
2606.6094 | 121.2296 | -6.2393 | 114.9811 | 0.014267 | 0.014582 | 0.048136 | 0.0061928 | 0.0057507 | 0.005849 | -0.00508 | 0.014572 | -0.0023626 | 0.00806 | -0.00028199 | -0.0081305 | 0.017543 | 0.041199 | 0.036621 | -0.013733 | 0.07782 | 0.17395 | -0.050354 | -0.20599 | -0.022888 | 0.004578 | -0.13733 | 0.07782 | 0.068665 | -0.073242 | -0.16022 | 6.189 | 6.0333 | -114.8071 | 6.2759 | 6.3171 | 0.28381 | -114.9399 | 6.1661 | 6.0791 | -114.9033 | 6.2164 | 6.102 | 0.022888 | -114.9124 | 6.4133 | 6.2805 | 6.2256 | -115.1871 | 6.3171 | 6.308 | 6.2439 | -115.1413
2608.3594 | 121.2799 | -5.7861 | 115.4388 | -0.00099167 | 0.012873 | 0.053904 | 0.0087564 | 0.0029737 | -0.0026958 | -0.004439 | 0.014572 | -0.0036444 | 0.0072056 | -0.0024182 | -0.014326 | 0.019465 | 0.022888 | 0.10986 | 0.091553 | 0.11902 | 0.16022 | -0.041199 | -0.17395 | 0.018311 | 0.11902 | -0.032043 | 0.054932 | 0.054932 | -0.064087 | -0.15106 | 5.7449 | 5.6122 | -115.2786 | 5.896 | 5.9052 | 0.29297 | -115.416 | 5.722 | 5.6351 | -115.3839 | 5.8044 | 5.7541 | 0.11902 | -115.3839 | 5.9464 | 5.809 | 5.8777 | -115.6128 | 5.8411 | 5.8411 | 5.9052 | -115.5899
2610.1094 | 121.225 | -5.8594 | 115.4022 | -0.00099167 | 0.013087 | 0.051126 | 0.0034158 | 0.0027601 | 0.0022174 | -0.004439 | -0.00068649 | -0.00086724 | 0.0042148 | -0.0022046 | -0.0074897 | 0.018611 | 0.054932 | 0.073242 | 0.068665 | 0.13733 | 0.15106 | -0.027466 | -0.16479 | 0.050354 | 0.082397 | -0.027466 | 0.054932 | 0.045776 | -0.07782 | -0.10529 | 5.8319 | 5.6946 | -115.2512 | 5.9326 | 5.9967 | 0.30212 | -115.3473 | 5.7816 | 5.7541 | -115.3473 | 5.9097 | 5.8319 | 0.07782 | -115.3564 | 6.0104 | 5.9143 | 5.928 | -115.567 | 5.9143 | 5.9052 | 5.9418 | -115.5075
2611.875 | 121.3211 | -6.8848 | 114.3631 | 0.0066373 | 0.015009 | 0.054331 | 0.003843 | 0.0038281 | -0.00013244 | -0.0072162 | 0.0069425 | -0.002149 | 0.0059238 | -0.0028454 | -0.013044 | 0.022029 | -0.036621 | -0.004578 | -0.022888 | 0.041199 | 0.18768 | -0.068665 | -0.2243 | -0.064087 | -0.009155 | -0.15564 | 0.091553 | 0.086975 | -0.11444 | -0.16022 | 6.8161 | 6.6605 | -114.1754 | 6.8802 | 6.926 | 0.2655 | -114.3997 | 6.7703 | 6.7245 | -114.2715 | 6.8207 | 6.7291 | 0.004577 | -114.2761 | 7.0724 | 6.8481 | 6.8619 | -114.5874 | 6.9763 | 6.9717 | 6.8756 | -114.5233
2613.6094 | 121.2112 | -6.1661 | 115.1459 | -0.0086212 | 0.010523 | 0.053476 | 0.0025612 | 0.00083746 | -0.00055964 | -0.0040118 | 0.0069425 | -0.003858 | 0.0027194 | -0.0015638 | -0.01048 | 0.018397 | 0.054932 | 0.09613 | 0.09613 | 0.1236 | 0.13733 | -0.022888 | -0.16479 | 0.036621 | 0.086975 | -0.027466 | 0.068665 | 0.036621 | -0.054932 | -0.13275 | 6.1432 | 6.0013 | -115.0085 | 6.2622 | 6.2897 | 0.28839 | -115.0909 | 6.1111 | 6.0333 | -115.0772 | 6.2027 | 6.1386 | 0.10529 | -115.1093 | 6.3034 | 6.221 | 6.2622 | -115.3107 | 6.2347 | 6.2027 | 6.2531 | -115.2786
2615.3125 | 121.3394 | -6.015 | 115.2374 | 0.0066373 | 0.010309 | 0.055613 | 0.0053384 | 0.0029737 | -0.0050458 | -0.0055072 | 0.0069425 | -0.0044988 | 0.005283 | -0.0045544 | -0.011976 | 0.022029 | 0.009155 | 0.032043 | 0.027466 | 0.10071 | 0.14648 | -0.036621 | -0.17853 | 0.004578 | 0.07782 | -0.027466 | 0.059509 | 0.059509 | -0.059509 | -0.13733 | 5.9784 | 5.8365 | -115.0909 | 6.0471 | 6.1157 | 0.27924 | -115.2283 | 5.9555 | 5.8777 | -115.1779 | 6.0196 | 5.9875 | 0.10986 | -115.1779 | 6.1615 | 6.0242 | 6.0425 | -115.416 | 6.0745 | 6.0745 | 6.0928 | -115.3748
2617.0625 | 121.2479 | -6.2576 | 115.0909 | 0.0066373 | 0.016505 | 0.052195 | 0.005552 | 0.0034009 | 0.007558 | -0.00508 | 0.0069425 | -0.002149 | 0.0082736 | 0.0012134 | -0.0089849 | 0.018397 | 0.045776 | -0.009155 | -0.013733 | 0.064087 | 0.16022 | -0.054932 | -0.20599 | -0.022888 | -0.036621 | -0.16022 | 0.086975 | 0.07782 | -0.10071 | -0.15564 | 6.2027 | 6.0516 | -114.9307 | 6.2485 | 6.3217 | 0.27008 | -115.0452 | 6.1569 | 6.102 | -115.004 | 6.2347 | 6.0974 | -0.004577 | -115.0131 | 6.4178 | 6.3034 | 6.2439 | -115.2969 | 6.3446 | 6.3354 | 6.221 | -115.2466
2618.75 | 121.3394 | -6.0974 | 115.1367 | 0.0066373 | 0.012873 | 0.053263 | 0.0087564 | 0.00083746 | -0.00098684 | -0.0074298 | -0.00068649 | -0.0040716 | 0.0084872 | -0.0028454 | -0.01283 | 0.019038 | 0.022888 | 0.054932 | 0.036621 | 0.10529 | 0.16479 | -0.059509 | -0.21515 | -0.041199 | 0.032043 | -0.1236 | 0.082397 | 0.07782 | -0.10529 | -0.15106 | 6.0379 | 5.8823 | -114.9719 | 6.1523 | 6.2027 | 0.32044 | -115.1138 | 5.9921 | 5.9464 | -115.0543 | 6.0562 | 5.9738 | 0.027466 | -115.0589 | 6.2622 | 6.1203 | 6.134 | -115.3519 | 6.1798 | 6.1752 | 6.1295 | -115.2878
2620.5 | 121.312 | -6.3034 | 115.036 | 0.0066373 | 0.010737 | 0.053904 | 0.0034158 | 0.0036145 | 0.0022174 | -0.0031574 | 0.0069425 | -0.00086724 | 0.0061374 | -0.0013502 | -0.0079169 | 0.017756 | 0.041199 | 0.032043 | 0.032043 | 0.09613 | 0.15564 | -0.022888 | -0.17395 | 0.054932 | 0.054932 | -0.050354 | 0.050354 | 0.036621 | -0.064087 | -0.11902 | 6.2805 | 6.1295 | -114.8804 | 6.3354 | 6.3995 | 0.27008 | -114.9948 | 6.2393 | 6.1844 | -114.9857 | 6.3583 | 6.2531 | 0.068665 | -114.9994 | 6.459 | 6.3446 | 6.3354 | -115.21 | 6.3538 | 6.34 | 6.3583 | -115.155
2622.25 | 121.3074 | -6.7062 | 114.6332 | 0.0066373 | 0.014368 | 0.054544 | 0.0042702 | 0.0029737 | 0.0020038 | -0.0040118 | 0.022202 | -0.0017218 | 0.0061374 | -0.001991 | -0.0087713 | 0.021174 | -0.018311 | -0.045776 | -0.050354 | 0.050354 | 0.19684 | -0.064087 | -0.21515 | -0.036621 | -0.054932 | -0.13275 | 0.07782 | 0.07782 | -0.10071 | -0.16022 | 6.6422 | 6.4911 | -114.4363 | 6.6605 | 6.7566 | 0.2655 | -114.6515 | 6.6055 | 6.546 | -114.5554 | 6.6696 | 6.5735 | 0.027466 | -114.5554 | 6.9031 | 6.6879 | 6.6559 | -114.8483 | 6.7841 | 6.7841 | 6.6513 | -114.7934
2623.9375 | 121.3348 | -6.6238 | 114.6835 | 0.0066373 | 0.012232 | 0.052408 | 0.0070474 | 0.0036145 | 0.0032856 | -0.0037982 | -0.00068649 | -0.0019354 | 0.0074192 | -0.00028199 | -0.010908 | 0.021388 | -0.050354 | -0.054932 | -0.054932 | 0.045776 | 0.17853 | -0.073242 | -0.19684 | -0.050354 | -0.041199 | -0.15106 | 0.091553 | 0.086975 | -0.09613 | -0.15564 | 6.5506 | 6.427 | -114.505 | 6.5689 | 6.6696 | 0.24261 | -114.7339 | 6.5277 | 6.4682 | -114.592 | 6.5735 | 6.4728 | 0.004578 | -114.5966 | 6.8024 | 6.5735 | 6.5689 | -114.8804 | 6.7154 | 6.7108 | 6.5826 | -114.8392
2625.7031 | 121.2891 | -6.4362 | 114.9536 | 0.0066373 | 0.015009 | 0.053904 | 0.0051248 | 0.0036145 | 0.0043536 | -0.0055072 | 0.0069425 | 0.00062796 | 0.0089146 | -0.00070919 | -0.0079169 | 0.020106 | -0.041199 | -0.050354 | -0.041199 | 0.045776 | 0.16937 | -0.054932 | -0.21057 | -0.07782 | -0.054932 | -0.1831 | 0.11444 | 0.07782 | -0.10529 | -0.1831 | 6.3812 | 6.2256 | -114.7842 | 6.3858 | 6.4819 | 0.25635 | -114.9948 | 6.3309 | 6.2531 | -114.8392 | 6.3583 | 6.2531 | 0 | -114.8758 | 6.6055 | 6.395 | 6.395 | -115.1642 | 6.5506 | 6.514 | 6.3812 | -115.1367
2627.4062 | 121.2753 | -6.4041 | 114.9673 | -0.00099167 | 0.012232 | 0.051981 | 0.0034158 | 0.0040417 | -0.0014142 | -0.0035846 | -0.00068649 | -0.0059942 | 0.0059238 | -0.004768 | -0.01048 | 0.022456 | 0.054932 | 0.091553 | 0.086975 | 0.13275 | 0.12817 | -0.018311 | -0.16022 | 0.036621 | 0.09613 | -0.013733 | 0.041199 | 0.032043 | -0.068665 | -0.10986 | 6.3858 | 6.2439 | -114.8392 | 6.4957 | 6.5369 | 0.29297 | -114.9124 | 6.3354 | 6.2943 | -114.9261 | 6.4407 | 6.3904 | 0.09613 | -114.9353 | 6.5323 | 6.459 | 6.4911 | -115.1276 | 6.4453 | 6.4362 | 6.5002 | -115.0772
2629.1719 | 121.3165 | -6.6376 | 114.7797 | -0.00099167 | 0.0133 | 0.052195 | 0.0044838 | 0.0031873 | 0.001363 | -0.004439 | -0.00068649 | -0.0049262 | 0.006351 | -0.003059 | -0.01048 | 0.019893 | -0.022888 | 0.027466 | 0.022888 | 0.086975 | 0.16937 | -0.041199 | -0.19684 | 0.036621 | 0.059509 | -0.064087 | 0.054932 | 0.032043 | -0.059509 | -0.11902 | 6.5964 | 6.4407 | -114.6103 | 6.665 | 6.7245 | 0.28381 | -114.8026 | 6.5781 | 6.5186 | -114.7247 | 6.6742 | 6.5735 | 0.054932 | -114.7476 | 6.8069 | 6.6147 | 6.6605 | -114.9765 | 6.6925 | 6.6696 | 6.6971 | -114.8987
2630.875 | 121.2845 | -10.2402 | 111.1084 | -0.00099167 | 0.011378 | 0.054972 | 0.0068338 | 0.00041006 | -0.0033368 | -0.0063616 | 0.0069425 | -0.0042852 | 0.0057102 | -0.004768 | -0.01283 | 0.022029 | 0.013733 | 0.068665 | 0.068665 | 0.09613 | 0.13733 | -0.022888 | -0.1831 | -0.004578 | 0.041199 | -0.045776 | 0.050354 | 0.036621 | -0.064087 | -0.13275 | 10.2173 | 10.0571 | -110.9711 | 10.3088 | 10.3363 | 0.27924 | -111.0947 | 10.1761 | 10.1074 | -111.058 | 10.2356 | 10.1944 | 0.086975 | -111.0718 | 10.3775 | 10.2539 | 10.3088 | -111.2915 | 10.2905 | 10.2768 | 10.2814 | -111.2411
2632.625 | 121.4355 | -9.6909 | 111.6074 | 0.0066373 | 0.016077 | 0.053049 | 0.0051248 | 0.0036145 | 0.0037128 | -0.0031574 | -0.00068649 | -0.00022644 | 0.00806 | -0.0015638 | -0.0091985 | 0.016902 | 0 | -0.004578 | -0.022888 | 0.082397 | 0.18768 | -0.064087 | -0.20599 | -0.018311 | 0.027466 | -0.11444 | 0.086975 | 0.064087 | -0.10071 | -0.16937 | 9.6268 | 9.4849 | -111.4197 | 9.6863 | 9.7733 | 0.28839 | -111.6074 | 9.5901 | 9.5215 | -111.5204 | 9.6725 | 9.5764 | 0.054932 | -111.5433 | 9.8785 | 9.6909 | 9.668 | -111.8134 | 9.7778 | 9.7549 | 9.7183 | -111.7767
2634.3125 | 121.3623 | -8.963 | 112.3856 | -0.00099167 | 0.012659 | 0.052622 | 0.0081154 | 0.0055371 | 0.00029476 | -0.0055072 | -0.008316 | -0.0036444 | 0.006992 | -0.001991 | -0.011121 | 0.020106 | -0.064087 | -0.018311 | -0.036621 | 0.032043 | 0.17853 | -0.068665 | -0.21973 | -0.07782 | -0.036621 | -0.14648 | 0.10986 | 0.10529 | -0.11444 | -0.16479 | 8.8943 | 8.7433 | -112.207 | 8.9447 | 8.9951 | 0.25177 | -112.4496 | 8.8486 | 8.7982 | -112.2757 | 8.8852 | 8.8165 | 0.018311 | -112.2803 | 9.1415 | 8.8989 | 8.9264 | -112.6053 | 9.0729 | 9.0683 | 8.9264 | -112.5504
2636.0781 | 121.3623 | -7.4615 | 113.9053 | 0.014267 | 0.011591 | 0.05369 | 0.0061928 | 0.0031873 | -0.0012006 | -0.00508 | -0.00068649 | -0.0059942 | 0.0072056 | -0.00028199 | -0.012617 | 0.021601 | 0.045776 | 0.10529 | 0.086975 | 0.13275 | 0.14191 | -0.032043 | -0.17853 | 0.027466 | 0.12817 | -0.018311 | 0.064087 | 0.045776 | -0.064087 | -0.14648 | 7.4295 | 7.283 | -113.7634 | 7.5668 | 7.5943 | 0.31128 | -113.8596 | 7.3975 | 7.3151 | -113.8412 | 7.489 | 7.4432 | 0.12817 | -113.8596 | 7.6035 | 7.5073 | 7.5485 | -114.0839 | 7.5256 | 7.5073 | 7.5897 | -114.0518
2637.7656 | 121.431 | -6.4911 | 114.8254 | 0.014267 | 0.009455 | 0.054758 | 0.007261 | 0.0023327 | -0.0035504 | -0.0055072 | -0.008316 | -0.005567 | 0.0048556 | -0.0037 | -0.013258 | 0.019893 | 0.041199 | 0.11444 | 0.086975 | 0.13275 | 0.15106 | -0.036621 | -0.16937 | 0.041199 | 0.11444 | 0.022888 | 0.045776 | 0.045776 | -0.064087 | -0.12817 | 6.4545 | 6.3217 | -114.6744 | 6.6055 | 6.6238 | 0.30212 | -114.7842 | 6.427 | 6.3629 | -114.7797 | 6.5323 | 6.514 | 0.15106 | -114.7797 | 6.6422 | 6.5323 | 6.5781 | -114.9948 | 6.5369 | 6.5369 | 6.6055 | -114.9536
2639.5156 | 121.376 | -7.0129 | 114.3951 | -0.00099167 | 0.007746 | 0.05604 | 0.0064066 | 0.0029737 | -0.0026958 | -0.004439 | -0.008316 | -0.0051398 | 0.0031468 | -0.0026318 | -0.010267 | 0.019465 | -0.018311 | 0.027466 | 0.032043 | 0.086975 | 0.16022 | -0.041199 | -0.18768 | 0.004578 | 0.041199 | -0.054932 | 0.073242 | 0.059509 | -0.064087 | -0.13275 | 6.9717 | 6.8253 | -114.2349 | 7.0404 | 7.0999 | 0.27466 | -114.4135 | 6.9489 | 6.8802 | -114.3219 | 7.0175 | 6.958 | 0.077819 | -114.3356 | 7.1732 | 6.9946 | 7.045 | -114.5828 | 7.0862 | 7.0724 | 7.0541 | -114.5279
2641.2656 | 120.7901 | -120.1538 | 0.56763 | -0.0086212 | 0.010523 | 0.053476 | 0.0040566 | 0.0016919 | 0.0011494 | -0.0042254 | -0.00068649 | -0.0030034 | 0.005283 | -0.0013502 | -0.0098395 | 0.018397 | 0.10529 | 0.10986 | 0.11444 | 0.16479 | 0.14648 | 0.009155 | -0.14191 | 0.09613 | 0.10071 | 0.004578 | 0.07782 | 0.073242 | -0.032043 | -0.09613 | 120.163 | 120.0119 | -0.42114 | 120.2637 | 120.3186 | 0.3067 | -0.46234 | 120.1218 | 120.0577 | -0.48981 | 120.2499 | 120.1584 | 0.10071 | -0.49438 | 120.3003 | 120.2591 | 120.2682 | -0.70953 | 120.2316 | 120.2271 | 120.2545 | -0.66376
2642.9531 | 120.932 | -118.7897 | 2.1469 | 0.014267 | 0.014155 | 0.05369 | 0.001066 | 0.0036145 | 0.0043536 | -0.0035846 | -0.008316 | -0.00065364 | 0.006351 | -0.0022046 | -0.0079169 | 0.02032 | 0.013733 | -0.027466 | -0.018311 | 0.064087 | 0.21057 | -0.027466 | -0.19684 | -0.009155 | -0.022888 | -0.12817 | 0.1236 | 0.10986 | -0.073242 | -0.12817 | 118.7622 | 118.5928 | -1.9363 | 118.7622 | 118.8538 | 0.26093 | -2.1332 | 118.7164 | 118.6615 | -2.0233 | 118.7805 | 118.6615 | 0 | -2.037 | 119.0002 | 118.8034 | 118.7714 | -2.3438 | 118.9133 | 118.8995 | 118.7668 | -2.2751
2644.7031 | 121.4447 | -76.5244 | 44.2017 | 0.0066373 | 0.016077 | 0.051126 | 0.010679 | 0.0034009 | 0.0028584 | -0.0037982 | 0.014572 | -0.0032172 | 0.0093418 | -0.0028454 | -0.011121 | 0.01797 | -0.009155 | -0.013733 | -0.032043 | 0.073242 | 0.19684 | -0.050354 | -0.21515 | -0.018311 | -0.009155 | -0.11902 | 0.1236 | 0.073242 | -0.091553 | -0.13733 | 76.474 | 76.3092 | -44.0048 | 76.5106 | 76.5976 | 0.28839 | -44.2108 | 76.4328 | 76.387 | -44.0781 | 76.506 | 76.4053 | 0.01831 | -44.1284 | 76.7212 | 76.5152 | 76.4923 | -44.4168 | 76.6479 | 76.5976 | 76.5152 | -44.339
2646.4688 | 95.0912 | -5.9418 | 89.1174 | 0.0066373 | 0.01565 | 0.052622 | 0.0036294 | 0.0034009 | 0.0032856 | -0.0057208 | -0.00068649 | -0.0019354 | 0.0061374 | -0.0015638 | -0.0077033 | 0.021388 | -0.036621 | -0.054932 | -0.073242 | 0.054932 | 0.1831 | -0.059509 | -0.21515 | -0.059509 | -0.064087 | -0.17853 | 0.07782 | 0.086975 | -0.09613 | -0.16937 | 5.8823 | 5.7266 | -88.9343 | 5.8868 | 5.9967 | 0.27008 | -89.1541 | 5.8456 | 5.7724 | -89.0396 | 5.8823 | 5.7632 | -0.009155 | -89.0305 | 6.1249 | 5.9052 | 5.8685 | -89.3326 | 6.0196 | 6.0287 | 5.8777 | -89.2868
2648.1719 | 119.0323 | -79.9393 | 38.887 | 0.0066373 | 0.013941 | 0.051554 | 0.0057656 | 0.0025465 | 0.003072 | -0.0029436 | 0.014572 | -0.0019354 | 0.008701 | 0.00014521 | -0.0096259 | 0.021388 | -0.054932 | -0.050354 | -0.032043 | 0.045776 | 0.20142 | -0.050354 | -0.19226 | -0.045776 | -0.054932 | -0.16937 | 0.10986 | 0.10071 | -0.07782 | -0.13275 | 79.8889 | 79.747 | -38.6856 | 79.8889 | 79.985 | 0.23804 | -38.942 | 79.8614 | 79.8065 | -38.7772 | 79.8935 | 79.7699 | -0.036622 | -38.7863 | 80.1407 | 79.8843 | 79.9072 | -39.0793 | 80.0491 | 80.04 | 79.8843 | -39.0198
2649.9219 | 120.7352 | -118.0481 | 2.3895 | -0.00099167 | 0.014582 | 0.055185 | 0.00897 | 0.0057507 | 0.00072196 | -0.0023028 | -0.00068649 | -0.0019354 | 0.0095554 | -0.0024182 | -0.01048 | 0.019893 | -0.013733 | 0 | 0.004578 | 0.10529 | 0.21515 | -0.036621 | -0.17853 | -0.018311 | 0.036621 | -0.091553 | 0.12817 | 0.11444 | -0.059509 | -0.12817 | 118.0115 | 117.8696 | -2.1744 | 118.0481 | 118.1534 | 0.28381 | -2.4033 | 117.9886 | 117.9199 | -2.2614 | 118.0298 | 117.9565 | 0.036621 | -2.2751 | 118.2632 | 118.0344 | 118.0527 | -2.5681 | 118.1763 | 118.1625 | 118.0847 | -2.5177
2651.6719 | 120.1492 | -4.3396 | 105.9814 | 0.0066373 | 0.016505 | 0.051767 | 0.0081154 | 0.0027601 | 0.0022174 | -0.0029436 | 0.014572 | -0.0015082 | 0.00806 | -0.0015638 | -0.0098395 | 0.018397 | 0 | 0.022888 | 0 | 0.07782 | 0.14648 | -0.068665 | -0.22888 | -0.036621 | 0.013733 | -0.13733 | 0.073242 | 0.059509 | -0.09613 | -0.16022 | 4.2709 | 4.1107 | -105.835 | 4.3625 | 4.4174 | 0.3067 | -105.9814 | 4.2435 | 4.1794 | -105.9082 | 4.303 | 4.2023 | 0.022888 | -105.9219 | 4.4861 | 4.3396 | 4.3396 | -106.2103 | 4.4128 | 4.3991 | 4.3533 | -106.1417
2653.3594 | 120.607 | -3.6484 | 117.1188 | 0.0066373 | 0.011591 | 0.052195 | 0.0096108 | -0.0017261 | -0.0059002 | -0.0067888 | 0.022202 | -0.007276 | 0.0059238 | -0.003059 | -0.015394 | 0.020106 | 0.009155 | 0.12817 | 0.082397 | 0.13275 | 0.13733 | -0.032043 | -0.16022 | 0.013733 | 0.13733 | -0.009155 | 0.054932 | 0.041199 | -0.073242 | -0.12817 | 3.6163 | 3.4882 | -116.9815 | 3.7765 | 3.7811 | 0.29297 | -117.1097 | 3.5751 | 3.5202 | -117.0639 | 3.6621 | 3.6392 | 0.11902 | -117.0776 | 3.7857 | 3.6575 | 3.7308 | -117.2791 | 3.7033 | 3.6896 | 3.7857 | -117.247
2655.1094 | 96.4096 | -4.2068 | 107.4463 | 0.021896 | 0.0133 | 0.05134 | 0.002775 | 0.0031873 | 0.00072196 | -0.004439 | -0.00068649 | -0.0025762 | 0.0042148 | -0.0032728 | -0.0074897 | 0.018184 | 0.009155 | 0.032043 | 0.018311 | 0.086975 | 0.15106 | -0.050354 | -0.20142 | 0.013733 | 0.050354 | -0.050354 | 0.050354 | 0.036621 | -0.073242 | -0.1236 | 4.1565 | 4.0054 | -107.2952 | 4.2389 | 4.2938 | 0.28839 | -107.4371 | 4.1336 | 4.0833 | -107.3959 | 4.2206 | 4.1565 | 0.073242 | -107.4097 | 4.3579 | 4.216 | 4.2252 | -107.6477 | 4.2572 | 4.2435 | 4.2572 | -107.5699
2656.8594 | 98.4879 | -5.2643 | 114.8575 | 0.0066373 | 0.013941 | 0.054544 | 0.0034158 | 0.0051099 | -0.00034604 | -0.0040118 | 0.0069425 | -0.0034308 | 0.0044284 | -0.0028454 | -0.0081305 | 0.020961 | 0.050354 | 0.073242 | 0.068665 | 0.1236 | 0.13275 | -0.027466 | -0.18768 | 0.041199 | 0.07782 | -0.041199 | 0.022888 | 0.036621 | -0.07782 | -0.12817 | 5.2368 | 5.0766 | -114.7247 | 5.3375 | 5.3879 | 0.31128 | -114.8071 | 5.1865 | 5.1361 | -114.8346 | 5.3055 | 5.2231 | 0.086975 | -114.8209 | 5.397 | 5.3146 | 5.3329 | -115.0452 | 5.2872 | 5.3009 | 5.3421 | -114.9857
2658.6094 | 120.4147 | -18.663 | 101.6006 | 0.014267 | 0.016505 | 0.05134 | 0.0085428 | 0.0046827 | 0.00093576 | -0.0048662 | 0.0069425 | -0.0015082 | 0.0084872 | -0.0013502 | -0.011549 | 0.016047 | -0.004578 | -0.009155 | -0.018311 | 0.086975 | 0.20142 | -0.068665 | -0.23804 | -0.041199 | 0.013733 | -0.10986 | 0.07782 | 0.073242 | -0.07782 | -0.16479 | 18.5944 | 18.425 | -101.3992 | 18.6539 | 18.75 | 0.32501 | -101.6052 | 18.5852 | 18.4982 | -101.5228 | 18.6218 | 18.5532 | 0.054932 | -101.5274 | 18.8644 | 18.6584 | 18.6447 | -101.8387 | 18.7408 | 18.7363 | 18.6768 | -101.7654
2660.3594 | 120.5521 | -14.8727 | 105.2673 | -0.00099167 | 0.013941 | 0.051981 | 0.0087564 | 0.0038281 | -0.0033368 | -0.0052936 | 0.0069425 | -0.0062078 | 0.0076328 | -0.001991 | -0.016035 | 0.020747 | 0.009155 | 0.10529 | 0.10529 | 0.13275 | 0.15106 | -0.064087 | -0.17853 | 0.022888 | 0.10529 | -0.022888 | 0.050354 | 0.050354 | -0.054932 | -0.13733 | 14.8087 | 14.6942 | -105.1163 | 14.978 | 15.0055 | 0.31128 | -105.2582 | 14.8178 | 14.7354 | -105.217 | 14.8956 | 14.8499 | 0.11444 | -105.217 | 15.0238 | 14.8819 | 14.978 | -105.4459 | 14.9231 | 14.9231 | 14.978 | -105.4047
2662.125 | 91.3559 | -14.4424 | 80.983 | 0.0066373 | 0.012873 | 0.051126 | 0.0040566 | 0.0031873 | 0.0026446 | -0.0035846 | -0.008316 | -0.0015082 | 0.0065646 | -0.00070919 | -0.0091985 | 0.018397 | 0.009155 | 0.027466 | 0.022888 | 0.091553 | 0.16022 | -0.032043 | -0.16937 | 0.036621 | 0.064087 | -0.050354 | 0.050354 | 0.050354 | -0.059509 | -0.13733 | 14.4104 | 14.2731 | -80.8228 | 14.4699 | 14.534 | 0.26093 | -80.9738 | 14.3829 | 14.3051 | -80.9326 | 14.4791 | 14.3921 | 0.086975 | -80.9326 | 14.6027 | 14.4516 | 14.4653 | -81.1523 | 14.4928 | 14.4928 | 14.5065 | -81.1203
2663.8125 | 95.3934 | -14.4516 | 91.2323 | -0.00099167 | 0.011164 | 0.053476 | 0.0066202 | 0.0016919 | 0.002431 | -0.00508 | 0.0069425 | -0.0010808 | 0.0061374 | -0.0026318 | -0.0091985 | 0.019679 | -0.036621 | -0.036621 | -0.059509 | 0.032043 | 0.16479 | -0.059509 | -0.2243 | -0.041199 | -0.027466 | -0.11444 | 0.086975 | 0.059509 | -0.09613 | -0.14648 | 14.3921 | 14.2273 | -91.0675 | 14.415 | 14.4836 | 0.25635 | -91.2689 | 14.3555 | 14.3051 | -91.1453 | 14.4104 | 14.3372 | 0.032043 | -91.1728 | 14.6164 | 14.415 | 14.3921 | -91.4566 | 14.5386 | 14.5111 | 14.4241 | -91.3788
2665.5625 | 120.9686 | -15.7745 | 105.0888 | -0.00099167 | 0.013941 | 0.053263 | 0.0081154 | 0.0031873 | -0.0012006 | -0.0055072 | -0.00068649 | -0.0053534 | 0.0093418 | -0.003059 | -0.013044 | 0.018824 | 0.018311 | 0.086975 | 0.068665 | 0.11902 | 0.13733 | -0.036621 | -0.18768 | -0.013733 | 0.10071 | -0.07782 | 0.073242 | 0.064087 | -0.10071 | -0.13275 | 15.7379 | 15.5869 | -104.9515 | 15.8615 | 15.8936 | 0.3067 | -105.0705 | 15.6738 | 15.6418 | -105.0156 | 15.7608 | 15.6967 | 0.054931 | -105.0247 | 15.9119 | 15.7928 | 15.8432 | -105.2765 | 15.8478 | 15.8386 | 15.8752 | -105.2216
2667.3281 | 120.195 | -17.2211 | 103.0701 | 0.0066373 | 0.012018 | 0.052622 | 0.003843 | 0.0027601 | 0.002431 | -0.00508 | 0.014572 | -0.00086724 | 0.0065646 | 0.00014521 | -0.0089849 | 0.020961 | -0.041199 | -0.073242 | -0.059509 | 0.045776 | 0.17395 | -0.07782 | -0.21973 | -0.07782 | -0.068665 | -0.16479 | 0.07782 | 0.07782 | -0.10071 | -0.15106 | 17.1432 | 17.0013 | -102.8961 | 17.1478 | 17.2668 | 0.2655 | -103.1113 | 17.1204 | 17.07 | -102.9922 | 17.1432 | 17.0563 | -0.013733 | -102.9922 | 17.395 | 17.1799 | 17.1616 | -103.2898 | 17.2989 | 17.2989 | 17.1524 | -103.2211
2669.0156 | 120.845 | -16.8137 | 104.1046 | -0.00099167 | 0.01565 | 0.053904 | 0.0049112 | 0.0016919 | 0.0026446 | -0.0070026 | -0.00068649 | -0.00044004 | 0.0059238 | -0.0024182 | -0.0085577 | 0.020533 | 0.004578 | 0.013733 | -0.018311 | 0.082397 | 0.16937 | -0.07782 | -0.2243 | -0.027466 | 0.022888 | -0.12817 | 0.073242 | 0.073242 | -0.09613 | -0.15106 | 16.7358 | 16.5894 | -103.9352 | 16.8274 | 16.8961 | 0.3067 | -104.1 | 16.7175 | 16.6626 | -104.0314 | 16.7862 | 16.6855 | 0.022888 | -104.0314 | 16.983 | 16.8182 | 16.7953 | -104.3289 | 16.8869 | 16.8869 | 16.8365 | -104.2557
2670.7812 | 121.1334 | -18.3975 | 102.5391 | -0.00099167 | 0.016077 | 0.054544 | 0.010893 | 0.0027601 | -0.00013244 | -0.004439 | -0.008316 | -0.0019354 | 0.008701 | -0.0015638 | -0.011121 | 0.02032 | -0.050354 | -0.054932 | -0.036621 | 0.059509 | 0.19226 | -0.068665 | -0.21515 | -0.059509 | 0.013733 | -0.13733 | 0.07782 | 0.091553 | -0.10071 | -0.16479 | 18.3289 | 18.1824 | -102.3468 | 18.3426 | 18.457 | 0.27466 | -102.5894 | 18.2968 | 18.2327 | -102.4612 | 18.338 | 18.2602 | 0.027466 | -102.4475 | 18.5898 | 18.3472 | 18.3609 | -102.7542 | 18.4753 | 18.4891 | 18.4113 | -102.7039
2672.5625 | 120.4926 | -18.8141 | 102.2278 | -0.00099167 | 0.009455 | 0.056253 | 0.0068338 | 0.0027601 | -0.0059002 | -0.0055072 | -0.00068649 | -0.0068488 | 0.0065646 | -0.0026318 | -0.012189 | 0.022029 | 0 | 0.054932 | 0.07782 | 0.09613 | 0.13733 | -0.032043 | -0.17853 | -0.022888 | 0.041199 | -0.054932 | 0.059509 | 0.064087 | -0.07782 | -0.13733 | 18.782 | 18.6356 | -102.0905 | 18.869 | 18.9102 | 0.27466 | -102.2278 | 18.7363 | 18.6768 | -102.1683 | 18.7912 | 18.7592 | 0.082397 | -102.1637 | 18.9514 | 18.8141 | 18.8919 | -102.4063 | 18.8736 | 18.8782 | 18.8553 | -102.3651
2674.25 | 104.4937 | -17.2028 | 102.8961 | 0.0066373 | 0.010309 | 0.053263 | 0.0059792 | 0.0044691 | 0.0017902 | -0.0048662 | -0.00068649 | -0.0034308 | 0.0048556 | -0.0026318 | -0.0096259 | 0.020747 | 0.068665 | 0.086975 | 0.082397 | 0.12817 | 0.11902 | -0.013733 | -0.16479 | 0.050354 | 0.07782 | -0.013733 | 0.032043 | 0.027466 | -0.050354 | -0.1236 | 17.189 | 17.038 | -102.7771 | 17.2897 | 17.3309 | 0.29297 | -102.8275 | 17.1524 | 17.0792 | -102.8641 | 17.2531 | 17.189 | 0.10986 | -102.8687 | 17.3218 | 17.2714 | 17.2852 | -103.0609 | 17.2348 | 17.2302 | 17.2806 | -103.0197
2676.0156 | 120.7764 | -17.2623 | 103.5004 | 0.0066373 | 0.012873 | 0.055826 | 0.007261 | 0.0012647 | -0.0056866 | -0.0052936 | 0.014572 | -0.0070624 | 0.0054966 | -0.0041272 | -0.012189 | 0.020106 | 0.054932 | 0.11444 | 0.09613 | 0.14191 | 0.15564 | -0.027466 | -0.1831 | 0.036621 | 0.12817 | 0.013733 | 0.054932 | 0.032043 | -0.059509 | -0.1236 | 17.2348 | 17.0792 | -103.3447 | 17.3767 | 17.4042 | 0.32501 | -103.4454 | 17.2028 | 17.1387 | -103.4454 | 17.2989 | 17.276 | 0.13733 | -103.4683 | 17.4179 | 17.3172 | 17.3584 | -103.6835 | 17.3172 | 17.2943 | 17.3904 | -103.624
2677.7031 | 121.1792 | -18.924 | 102.0584 | -0.00099167 | 0.011164 | 0.05369 | 0.0059792 | 0.0044691 | -0.0031232 | -0.0031574 | 0.0069425 | -0.0053534 | 0.004642 | -0.0034864 | -0.013044 | 0.017329 | 0.073242 | 0.10986 | 0.10071 | 0.12817 | 0.16479 | -0.032043 | -0.16479 | 0.018311 | 0.10529 | -0.013733 | 0.041199 | 0.054932 | -0.064087 | -0.11902 | 18.8919 | 18.7592 | -101.8936 | 19.0338 | 19.0521 | 0.29297 | -101.9852 | 18.8599 | 18.8049 | -102.0172 | 18.9423 | 18.9102 | 0.10529 | -102.0035 | 19.0887 | 18.9972 | 19.0247 | -102.2232 | 18.9651 | 18.9789 | 19.0292 | -102.1774
2679.4531 | 120.5566 | -19.5648 | 101.0468 | -0.00099167 | 0.012446 | 0.052622 | 0.0046976 | 0.0025465 | 0.0039264 | -0.0059344 | -0.00068649 | -0.00022644 | 0.0067782 | 0.00035881 | -0.0068487 | 0.018397 | -0.045776 | -0.10529 | -0.082397 | 0.036621 | 0.20142 | -0.086975 | -0.20142 | -0.050354 | -0.073242 | -0.17853 | 0.082397 | 0.07782 | -0.10071 | -0.16937 | 19.4778 | 19.3634 | -100.8453 | 19.4595 | 19.6014 | 0.23804 | -101.0925 | 19.4641 | 19.3954 | -100.9644 | 19.5145 | 19.3863 | -0.009155 | -100.9689 | 19.7662 | 19.519 | 19.4824 | -101.2482 | 19.6472 | 19.6426 | 19.4916 | -101.2161
2681.2188 | 121.1655 | -19.7571 | 101.2802 | 0.0066373 | 0.010096 | 0.052622 | 0.005552 | 0.00083746 | -0.00077324 | -0.0042254 | 0.0069425 | -0.0047124 | 0.005283 | -0.0013502 | -0.010053 | 0.021601 | -0.018311 | 0.018311 | -0.004578 | 0.082397 | 0.18768 | -0.068665 | -0.21057 | -0.068665 | -0.009155 | -0.13733 | 0.10529 | 0.068665 | -0.10071 | -0.17853 | 19.6884 | 19.5465 | -101.0925 | 19.7754 | 19.8395 | 0.29297 | -101.2985 | 19.6564 | 19.5786 | -101.1749 | 19.6884 | 19.6198 | 0.041199 | -101.2115 | 19.9448 | 19.7388 | 19.7525 | -101.4908 | 19.8624 | 19.8257 | 19.7479 | -101.4587
2682.9688 | 105.1392 | -9.343 | 111.5707 | -0.0086212 | 0.0092414 | 0.054117 | 0.003843 | 0.0021191 | -0.00098684 | -0.0037982 | -0.00068649 | -0.0051398 | 0.0040012 | -0.0037 | -0.0094123 | 0.021388 | 0.045776 | 0.09613 | 0.068665 | 0.09613 | 0.14191 | -0.027466 | -0.19226 | 0.018311 | 0.068665 | -0.032043 | 0.045776 | 0.041199 | -0.073242 | -0.1236 | 9.3155 | 9.1507 | -111.4288 | 9.4391 | 9.4391 | 0.28839 | -111.525 | 9.2697 | 9.2194 | -111.525 | 9.3613 | 9.3109 | 0.091553 | -111.5295 | 9.4849 | 9.3887 | 9.4116 | -111.763 | 9.3887 | 9.3842 | 9.4116 | -111.6943
2684.6562 | 121.1197 | -8.5739 | 112.5641 | -0.00099167 | 0.014796 | 0.053263 | 0.011961 | 0.0023327 | 0.0022174 | -0.0052936 | -0.00068649 | -0.0040716 | 0.008701 | -0.0013502 | -0.011976 | 0.020961 | -0.018311 | -0.045776 | -0.050354 | 0.036621 | 0.19226 | -0.07782 | -0.2243 | -0.091553 | -0.018311 | -0.16022 | 0.09613 | 0.07782 | -0.1236 | -0.17395 | 8.4961 | 8.3496 | -112.3718 | 8.5281 | 8.6105 | 0.26093 | -112.5824 | 8.4503 | 8.4 | -112.468 | 8.4824 | 8.4137 | 0.013733 | -112.4863 | 8.7662 | 8.5556 | 8.5236 | -112.7884 | 8.67 | 8.6517 | 8.5556 | -112.738
2686.4062 | 121.2524 | -8.1436 | 112.9807 | -0.00099167 | 0.0133 | 0.053476 | 0.010893 | 0.0027601 | 0.0011494 | -0.0065752 | -0.00068649 | -0.00086724 | 0.0067782 | -0.0022046 | -0.0094123 | 0.019679 | -0.032043 | -0.068665 | -0.064087 | 0.036621 | 0.16937 | -0.073242 | -0.21973 | -0.082397 | -0.036621 | -0.16479 | 0.082397 | 0.086975 | -0.11444 | -0.16479 | 8.0704 | 7.9239 | -112.8113 | 8.075 | 8.1802 | 0.25635 | -113.0127 | 8.0292 | 7.9788 | -112.8983 | 8.0612 | 7.9788 | 0 | -112.8937 | 8.313 | 8.1116 | 8.0795 | -113.2004 | 8.226 | 8.2306 | 8.107 | -113.1454
2688.1562 | 121.0007 | -7.869 | 113.2507 | -0.00099167 | 0.013514 | 0.053476 | 0.0032022 | 0.0042555 | 0.0052082 | -0.0035846 | 0.0069425 | 0.00020076 | 0.006992 | -0.0011364 | -0.0077033 | 0.020961 | -0.045776 | -0.082397 | -0.068665 | 0.032043 | 0.17395 | -0.073242 | -0.21973 | -0.073242 | -0.073242 | -0.21057 | 0.068665 | 0.068665 | -0.11444 | -0.16022 | 7.7957 | 7.6492 | -113.0768 | 7.7866 | 7.901 | 0.25177 | -113.2965 | 7.7545 | 7.7087 | -113.1821 | 7.7957 | 7.6584 | -0.050354 | -113.1821 | 8.0429 | 7.8232 | 7.8003 | -113.4705 | 7.9376 | 7.9376 | 7.7957 | -113.4109
2689.9062 | 121.0281 | -7.6492 | 113.5574 | -0.00099167 | 0.0086006 | 0.056681 | 0.007261 | 0.0012647 | -0.0048322 | -0.004439 | 0.0069425 | -0.0047124 | 0.004642 | -0.0032728 | -0.011549 | 0.021601 | -0.027466 | 0.009155 | 0.027466 | 0.07782 | 0.13733 | -0.041199 | -0.20142 | -0.013733 | 0.027466 | -0.07782 | 0.054932 | 0.050354 | -0.07782 | -0.13733 | 7.608 | 7.4478 | -113.4201 | 7.6584 | 7.7271 | 0.27924 | -113.5849 | 7.5714 | 7.5119 | -113.5025 | 7.6355 | 7.5714 | 0.059509 | -113.5071 | 7.7866 | 7.6218 | 7.6767 | -113.7588 | 7.7042 | 7.6996 | 7.6767 | -113.6948
2691.6562 | 120.7031 | -7.4982 | 113.5712 | 0.0066373 | 0.014155 | 0.051981 | 0.0057656 | 0.0029737 | 0.0034992 | -0.0076434 | -0.00068649 | 0.0014826 | 0.0076328 | -0.0011364 | -0.010267 | 0.019038 | -0.050354 | -0.059509 | -0.07782 | 0.032043 | 0.18768 | -0.064087 | -0.21973 | -0.064087 | -0.073242 | -0.16937 | 0.086975 | 0.068665 | -0.09613 | -0.15564 | 7.4341 | 7.2784 | -113.3835 | 7.4387 | 7.5302 | 0.25177 | -113.6215 | 7.402 | 7.3425 | -113.4842 | 7.4341 | 7.3288 | -0.013733 | -113.5025 | 7.6859 | 7.4478 | 7.4203 | -113.7909 | 7.5851 | 7.5668 | 7.4249 | -113.7268
2693.3438 | 121.2708 | -7.3517 | 113.768 | -0.00099167 | 0.016291 | 0.053263 | 0.010252 | 0.0034009 | 0.00093576 | -0.0055072 | 0.0069425 | -0.0042852 | 0.008701 | -0.0017774 | -0.011762 | 0.018184 | -0.059509 | -0.045776 | -0.064087 | 0.041199 | 0.19684 | -0.07782 | -0.22888 | -0.07782 | -0.041199 | -0.17853 | 0.082397 | 0.082397 | -0.11444 | -0.1831 | 7.2739 | 7.1228 | -113.5712 | 7.3059 | 7.3929 | 0.27008 | -113.8275 | 7.2372 | 7.1686 | -113.6856 | 7.2739 | 7.1732 | 0.004577 | -113.6856 | 7.5485 | 7.2922 | 7.2876 | -113.9969 | 7.4341 | 7.4341 | 7.3105 | -113.9511
2695.0938 | 120.5704 | -7.2052 | 113.5803 | 0.0066373 | 0.011805 | 0.052622 | 0.0076882 | 0.0036145 | 0.0015766 | -0.00273 | -0.00068649 | -0.0027898 | 0.0082736 | -0.00028199 | -0.0091985 | 0.019252 | -0.045776 | -0.036621 | -0.032043 | 0.050354 | 0.17853 | -0.068665 | -0.2243 | -0.022888 | 0 | -0.10071 | 0.064087 | 0.032043 | -0.07782 | -0.14191 | 7.1365 | 6.9809 | -113.4018 | 7.1686 | 7.2556 | 0.27466 | -113.6261 | 7.1274 | 7.0633 | -113.5162 | 7.1823 | 7.1045 | 0.041199 | -113.5483 | 7.3837 | 7.1594 | 7.1732 | -113.8046 | 7.2693 | 7.2372 | 7.2052 | -113.7222
2696.7969 | 121.138 | -7.164 | 113.9969 | -0.0086212 | 0.007746 | 0.055185 | 0.005552 | 0.0031873 | -0.0046184 | -0.0065752 | -0.00068649 | -0.006635 | 0.004642 | -0.0034864 | -0.012617 | 0.021388 | -0.045776 | 0.032043 | 0.018311 | 0.068665 | 0.15564 | -0.045776 | -0.18768 | -0.027466 | 0.036621 | -0.064087 | 0.054932 | 0.045776 | -0.050354 | -0.13275 | 7.1182 | 6.9763 | -113.8412 | 7.196 | 7.2327 | 0.25635 | -114.0427 | 7.1136 | 7.0312 | -113.942 | 7.1365 | 7.0999 | 0.068664 | -113.9511 | 7.3196 | 7.1182 | 7.1823 | -114.1846 | 7.2189 | 7.2098 | 7.2006 | -114.1296
2698.5625 | 120.9869 | -7.1777 | 114.0701 | 0.014267 | 0.011378 | 0.055185 | 0.0085428 | 0.0034009 | -0.0029094 | -0.0042254 | -0.00068649 | -0.005567 | 0.0054966 | -0.0045544 | -0.013685 | 0.020106 | -0.018311 | 0.036621 | 0.036621 | 0.073242 | 0.14191 | -0.036621 | -0.17395 | -0.022888 | 0.009155 | -0.073242 | 0.068665 | 0.041199 | -0.068665 | -0.13275 | 7.1411 | 7.0038 | -113.9282 | 7.2144 | 7.251 | 0.24719 | -114.0884 | 7.1091 | 7.045 | -114.0015 | 7.1548 | 7.1045 | 0.059509 | -114.0289 | 7.3196 | 7.1594 | 7.2144 | -114.2441 | 7.2464 | 7.2189 | 7.1869 | -114.2029
2700.25 | 121.2158 | -8.6014 | 112.6556 | 0.0066373 | 0.012232 | 0.051981 | 0.0034158 | 0.0025465 | 0.00649 | -0.0046526 | 0.0069425 | -0.00044004 | 0.0061374 | -0.00028199 | -0.0079169 | 0.018184 | -0.027466 | -0.082397 | -0.064087 | 0.036621 | 0.18768 | -0.07782 | -0.21515 | -0.064087 | -0.07782 | -0.16937 | 0.07782 | 0.064087 | -0.09613 | -0.16022 | 8.5236 | 8.3862 | -112.468 | 8.519 | 8.638 | 0.25177 | -112.6831 | 8.5052 | 8.4412 | -112.5778 | 8.5373 | 8.432 | -0.009156 | -112.5916 | 8.7891 | 8.5739 | 8.5373 | -112.8708 | 8.6792 | 8.6655 | 8.5236 | -112.8159
2702.0156 | 121.2753 | -9.0271 | 112.1429 | -0.00099167 | 0.010737 | 0.054758 | 0.0057656 | 0.0031873 | -0.0031232 | -0.0055072 | 0.0069425 | -0.005567 | 0.006351 | -0.006477 | -0.01283 | 0.019465 | 0.036621 | 0.11902 | 0.10071 | 0.1236 | 0.15106 | -0.027466 | -0.19226 | 0.041199 | 0.1236 | -0.013733 | 0.036621 | 0.045776 | -0.07782 | -0.10986 | 8.9996 | 8.8348 | -111.9919 | 9.1461 | 9.1507 | 0.31586 | -112.1063 | 8.9493 | 8.9172 | -112.1063 | 9.0683 | 9.0134 | 0.09613 | -112.0972 | 9.1782 | 9.0637 | 9.1278 | -112.3352 | 9.0637 | 9.0729 | 9.1507 | -112.2528
2703.7656 | 121.2067 | -9.6909 | 111.5707 | 0.0066373 | 0.011591 | 0.051981 | 0.0057656 | 0.0038281 | 0.0032856 | -0.00508 | 0.0069425 | -0.00022644 | 0.0099826 | -0.00070919 | -0.0064215 | 0.018184 | -0.027466 | -0.068665 | -0.07782 | 0.054932 | 0.16937 | -0.059509 | -0.21973 | -0.054932 | -0.068665 | -0.19684 | 0.07782 | 0.064087 | -0.086975 | -0.15564 | 9.6313 | 9.4711 | -111.4014 | 9.6222 | 9.7458 | 0.27466 | -111.5982 | 9.6039 | 9.5352 | -111.4929 | 9.6359 | 9.494 | -0.041198 | -111.5067 | 9.8602 | 9.6634 | 9.613 | -111.7905 | 9.7687 | 9.7549 | 9.6222 | -111.7264
2705.5156 | 121.2936 | -9.8923 | 111.3007 | 0.0066373 | 0.013941 | 0.053263 | 0.0093972 | 0.0048963 | -0.002055 | -0.003371 | -0.00068649 | -0.0042852 | 0.0095554 | -0.0024182 | -0.013258 | 0.020106 | -0.004578 | 0.045776 | 0.013733 | 0.10071 | 0.15106 | -0.050354 | -0.21057 | -0.050354 | 0.022888 | -0.1236 | 0.07782 | 0.073242 | -0.09613 | -0.13733 | 9.8419 | 9.6817 | -111.1496 | 9.938 | 9.993 | 0.31128 | -111.3052 | 9.7961 | 9.7549 | -111.2228 | 9.8419 | 9.7687 | 0.013733 | -111.2274 | 10.0433 | 9.8877 | 9.906 | -111.5112 | 9.9701 | 9.9655 | 9.9152 | -111.438
2707.2344 | 121.2021 | -9.3887 | 111.8774 | 0.0066373 | 0.016077 | 0.054117 | 0.0029886 | 0.0025465 | 0.004781 | -0.004439 | -0.00068649 | -0.0010808 | 0.006351 | -0.0039136 | -0.0089849 | 0.019038 | -0.045776 | -0.068665 | -0.059509 | 0.050354 | 0.16937 | -0.073242 | -0.22888 | -0.091553 | -0.07782 | -0.18768 | 0.082397 | 0.082397 | -0.10529 | -0.14648 | 9.3155 | 9.1599 | -111.7081 | 9.3201 | 9.4391 | 0.27924 | -111.9232 | 9.2834 | 9.2422 | -111.795 | 9.2972 | 9.2011 | -0.041199 | -111.795 | 9.5581 | 9.343 | 9.3292 | -112.1063 | 9.4711 | 9.4711 | 9.3109 | -112.0239
2708.9844 | 121.2845 | -9.3887 | 111.8454 | -0.0086212 | 0.014582 | 0.053263 | 0.0083292 | 0.0040417 | -0.0014142 | -0.0059344 | -0.00068649 | -0.0044988 | 0.0093418 | -0.00049559 | -0.012617 | 0.020106 | -0.018311 | 0.045776 | 0.022888 | 0.091553 | 0.16937 | -0.068665 | -0.20599 | -0.068665 | 0.013733 | -0.1236 | 0.10529 | 0.07782 | -0.10529 | -0.16022 | 9.3201 | 9.1827 | -111.676 | 9.4345 | 9.4803 | 0.29755 | -111.8637 | 9.2834 | 9.2285 | -111.7401 | 9.3201 | 9.2651 | 0.036621 | -111.7676 | 9.5581 | 9.3704 | 9.4116 | -112.0514 | 9.494 | 9.4666 | 9.4025 | -112.0056
2710.7344 | 121.1792 | -9.169 | 112.1338 | -0.00099167 | 0.0092414 | 0.051126 | 0.0034158 | 0.00083746 | -0.0014142 | -0.004439 | 0.0069425 | -0.0032172 | 0.0044284 | -0.0041272 | -0.0079169 | 0.021601 | 0.064087 | 0.086975 | 0.073242 | 0.12817 | 0.15106 | -0.013733 | -0.15106 | 0.054932 | 0.086975 | -0.027466 | 0.041199 | 0.032043 | -0.068665 | -0.12817 | 9.1553 | 9.0179 | -111.9827 | 9.256 | 9.2972 | 0.27924 | -112.0697 | 9.1003 | 9.0408 | -112.0926 | 9.2239 | 9.1415 | 0.10071 | -112.1017 | 9.3201 | 9.2331 | 9.2422 | -112.2849 | 9.2102 | 9.201 | 9.256 | -112.262
2712.5312 | 121.3623 | -8.6197 | 112.5824 | 0.0066373 | 0.0090278 | 0.056894 | 0.0061928 | 0.0027601 | -0.0048322 | -0.0067888 | -0.00068649 | -0.0053534 | 0.0065646 | -0.0034864 | -0.015394 | 0.019252 | 0.013733 | 0.086975 | 0.073242 | 0.10986 | 0.14191 | -0.032043 | -0.19684 | 0.036621 | 0.10071 | 0.009155 | 0.041199 | 0.036621 | -0.086975 | -0.1236 | 8.5876 | 8.4229 | -112.4405 | 8.7067 | 8.7296 | 0.3067 | -112.5687 | 8.5327 | 8.4961 | -112.5412 | 8.6563 | 8.6288 | 0.13275 | -112.5458 | 8.7616 | 8.6334 | 8.6929 | -112.7792 | 8.6609 | 8.6563 | 8.7204 | -112.706
2714.2969 | 121.3669 | -7.9788 | 113.2553 | -0.0086212 | 0.011164 | 0.05369 | 0.0085428 | 0.0038281 | -0.00013244 | -0.00508 | -0.00068649 | -0.0077032 | 0.0057102 | -0.001991 | -0.01283 | 0.021601 | 0.054932 | 0.07782 | 0.091553 | 0.11902 | 0.13733 | -0.045776 | -0.17853 | 0.045776 | 0.11902 | 0 | 0.041199 | 0.041199 | -0.054932 | -0.11902 | 7.933 | 7.8003 | -113.118 | 8.0566 | 8.0978 | 0.29755 | -113.2004 | 7.9239 | 7.8598 | -113.2141 | 8.0246 | 7.9788 | 0.11902 | -113.2141 | 8.1161 | 8.0338 | 8.0704 | -113.4338 | 8.02 | 8.02 | 8.0978 | -113.3743
2715.9844 | 121.3577 | -7.901 | 113.3698 | -0.0086212 | 0.01095 | 0.053263 | 0.0061928 | 0.0021191 | -0.00013244 | -0.0048662 | -0.00068649 | -0.0042852 | 0.0061374 | -0.003059 | -0.012617 | 0.017756 | 0.082397 | 0.10986 | 0.082397 | 0.1236 | 0.14648 | -0.050354 | -0.17395 | 0.018311 | 0.12817 | -0.013733 | 0.036621 | 0.041199 | -0.054932 | -0.11902 | 7.8506 | 7.7271 | -113.2233 | 8.0109 | 8.0246 | 0.29755 | -113.2874 | 7.8461 | 7.782 | -113.3331 | 7.9193 | 7.8873 | 0.10529 | -113.3286 | 8.0475 | 7.9834 | 7.9834 | -113.5437 | 7.9376 | 7.9422 | 8.0292 | -113.4888
2717.75 | 121.4081 | -7.3059 | 113.9557 | -0.00099167 | 0.012659 | 0.052408 | 0.0051248 | 0.0031873 | 0.0037128 | -0.00508 | -0.00068649 | -0.0010808 | 0.00806 | -0.0011364 | -0.0094123 | 0.017115 | 0.004578 | -0.027466 | -0.022888 | 0.059509 | 0.16937 | -0.054932 | -0.23804 | -0.022888 | -0.004578 | -0.13733 | 0.082397 | 0.064087 | -0.10071 | -0.14648 | 7.251 | 7.0679 | -113.7863 | 7.2784 | 7.3654 | 0.29755 | -113.9511 | 7.2052 | 7.1594 | -113.8733 | 7.283 | 7.1686 | 0.009155 | -113.8916 | 7.4753 | 7.3105 | 7.283 | -114.1937 | 7.3883 | 7.37 | 7.3013 | -114.1022
2719.5156 | 121.3943 | -7.5897 | 113.6444 | 0.0066373 | 0.014155 | 0.05369 | 0.0064066 | 0.0046827 | 0.0039264 | -0.004439 | -0.008316 | -0.00065364 | 0.008701 | -0.0017774 | -0.01048 | 0.016688 | -0.022888 | 0 | -0.032043 | 0.082397 | 0.15106 | -0.064087 | -0.20142 | -0.013733 | 0.018311 | -0.13733 | 0.082397 | 0.07782 | -0.091553 | -0.16479 | 7.5256 | 7.3883 | -113.4933 | 7.5897 | 7.6721 | 0.28381 | -113.6673 | 7.4982 | 7.4249 | -113.562 | 7.576 | 7.4524 | 0.027466 | -113.5666 | 7.7408 | 7.5668 | 7.5577 | -113.8458 | 7.6721 | 7.6675 | 7.608 | -113.8092
2721.2188 | 121.4081 | -7.4844 | 113.7817 | 0.0066373 | 0.011591 | 0.051767 | 0.00897 | 0.0021191 | 0.0028584 | -0.0052936 | 0.0069425 | -0.0053534 | 0.0084872 | -0.0043408 | -0.0094123 | 0.020961 | -0.050354 | -0.041199 | -0.050354 | 0.050354 | 0.19684 | -0.086975 | -0.21973 | -0.059509 | -0.013733 | -0.16022 | 0.10071 | 0.07782 | -0.091553 | -0.15106 | 7.3975 | 7.2647 | -113.5849 | 7.4432 | 7.5348 | 0.27008 | -113.8321 | 7.3929 | 7.3334 | -113.681 | 7.4249 | 7.3242 | -0.009155 | -113.7039 | 7.6813 | 7.4341 | 7.4341 | -114.0015 | 7.5851 | 7.5623 | 7.4707 | -113.9328
2722.9219 | 121.0098 | -8.5098 | 112.8571 | -0.00099167 | 0.011591 | 0.052195 | 0.00085245 | 0.0040417 | 0.0032856 | -0.0046526 | -0.00068649 | -0.0023626 | 0.006992 | -0.0011364 | -0.0094123 | 0.022883 | -0.059509 | -0.059509 | -0.068665 | 0.022888 | 0.17853 | -0.054932 | -0.21515 | -0.068665 | -0.07782 | -0.16022 | 0.086975 | 0.091553 | -0.09613 | -0.14648 | 8.4549 | 8.2947 | -112.6785 | 8.4503 | 8.5327 | 0.23804 | -112.9166 | 8.4137 | 8.3633 | -112.7701 | 8.4412 | 8.3496 | -0.013733 | -112.7655 | 8.6884 | 8.4503 | 8.4412 | -113.0722 | 8.5968 | 8.6014 | 8.432 | -113.0035
2724.6875 | 120.9961 | -8.1482 | 113.1775 | 0.0066373 | 0.014155 | 0.050913 | 0.0051248 | 0.0048963 | 0.0034992 | -0.0029436 | 0.014572 | 0.00062796 | 0.0061374 | 0.00014521 | -0.0087713 | 0.019893 | 0.036621 | 0.013733 | -0.013733 | 0.082397 | 0.18768 | -0.050354 | -0.21057 | -0.045776 | 0.022888 | -0.13275 | 0.086975 | 0.073242 | -0.10071 | -0.14191 | 8.0978 | 7.9376 | -112.9898 | 8.1619 | 8.2306 | 0.29297 | -113.1409 | 8.0475 | 8.0063 | -113.0905 | 8.1024 | 8.0154 | 0.009156 | -113.1042 | 8.3359 | 8.1848 | 8.1345 | -113.3881 | 8.2352 | 8.2214 | 8.1711 | -113.3194
2726.375 | 121.106 | -8.8165 | 112.5275 | -0.00099167 | 0.012659 | 0.054544 | 0.007261 | 0.0051099 | 0.00072196 | -0.0052936 | -0.008316 | -0.0015082 | 0.008701 | -0.0022046 | -0.0089849 | 0.021388 | -0.059509 | -0.082397 | -0.073242 | 0.054932 | 0.19226 | -0.064087 | -0.22888 | -0.073242 | -0.059509 | -0.1831 | 0.086975 | 0.082397 | -0.086975 | -0.15564 | 8.7524 | 8.5876 | -112.3352 | 8.7341 | 8.8715 | 0.28381 | -112.587 | 8.7296 | 8.6609 | -112.4405 | 8.7433 | 8.6334 | -0.027465 | -112.4451 | 9.0088 | 8.757 | 8.7433 | -112.7563 | 8.9035 | 8.8989 | 8.757 | -112.6831
2728.1406 | 119.7098 | -5.0262 | 115.4846 | 0.0066373 | 0.010737 | 0.053476 | 0.0051248 | 0.0016919 | -0.00098684 | -0.0025164 | 0.014572 | -0.0044988 | 0.0057102 | -0.0037 | -0.011762 | 0.022883 | 0.050354 | 0.073242 | 0.073242 | 0.13733 | 0.12817 | -0.027466 | -0.1831 | 0.050354 | 0.082397 | -0.032043 | 0.036621 | 0.045776 | -0.068665 | -0.12817 | 4.9988 | 4.8431 | -115.3564 | 5.0995 | 5.1636 | 0.32043 | -115.4343 | 4.9576 | 4.8981 | -115.448 | 5.0766 | 4.9942 | 0.096131 | -115.4388 | 5.1544 | 5.0766 | 5.0995 | -115.6677 | 5.0629 | 5.072 | 5.1086 | -115.6128
2729.8906 | 120.9091 | -3.8773 | 117.3248 | 0.014267 | 0.019068 | 0.053904 | 0.0066202 | 0.0034009 | 0.0039264 | -0.0048662 | 0.014572 | 0.00020076 | 0.0057102 | -0.0034864 | -0.010267 | 0.02032 | 0.027466 | 0.009155 | 0.004578 | 0.091553 | 0.17395 | -0.045776 | -0.20142 | -0.054932 | 0.009155 | -0.13733 | 0.064087 | 0.07782 | -0.10071 | -0.14648 | 3.8315 | 3.6758 | -117.1509 | 3.8864 | 3.9688 | 0.29297 | -117.2974 | 3.7765 | 3.7308 | -117.2607 | 3.8223 | 3.7399 | 0.009155 | -117.247 | 4.0512 | 3.9047 | 3.8818 | -117.5262 | 3.9413 | 3.9551 | 3.8864 | -117.4713
2731.5781 | 120.7855 | -3.8406 | 116.8396 | 0.0066373 | 0.010309 | 0.056467 | 0.0029886 | 0.0025465 | -0.0026958 | -0.003371 | -0.00068649 | -0.0044988 | 0.0057102 | -0.0022046 | -0.010267 | 0.021815 | 0.022888 | 0.07782 | 0.086975 | 0.1236 | 0.12817 | -0.018311 | -0.16022 | 0.018311 | 0.091553 | -0.041199 | 0.022888 | 0.036621 | -0.064087 | -0.13275 | 3.8223 | 3.6804 | -116.7114 | 3.9185 | 3.9642 | 0.28381 | -116.8167 | 3.7766 | 3.7079 | -116.8167 | 3.8589 | 3.7994 | 0.091552 | -116.803 | 3.9688 | 3.8635 | 3.9276 | -116.9998 | 3.8635 | 3.8773 | 3.9322 | -116.9724
2733.3438 | 121.2845 | -3.5248 | 117.7277 | 0.0066373 | 0.01095 | 0.053904 | 0.010252 | 0.0021191 | -0.0046184 | -0.0067888 | 0.0069425 | -0.0074896 | 0.005283 | -0.0045544 | -0.015394 | 0.022029 | -0.041199 | 0.018311 | 0.045776 | 0.086975 | 0.14648 | -0.036621 | -0.1831 | -0.032043 | 0.027466 | -0.059509 | 0.050354 | 0.036621 | -0.086975 | -0.12817 | 3.4882 | 3.3417 | -117.5812 | 3.5431 | 3.6118 | 0.27008 | -117.7689 | 3.4378 | 3.3966 | -117.6773 | 3.4927 | 3.4653 | 0.068665 | -117.691 | 3.6713 | 3.4836 | 3.5706 | -117.9108 | 3.5751 | 3.5614 | 3.5522 | -117.8558
2735.1094 | 121.4264 | -3.0579 | 118.2495 | -0.00099167 | 0.013087 | 0.053476 | 0.0096108 | 0.0025465 | -0.0026958 | -0.0070026 | 0.014572 | -0.0079168 | 0.0065646 | -0.003059 | -0.014112 | 0.01797 | 0 | 0.064087 | 0.059509 | 0.10071 | 0.13733 | -0.036621 | -0.18768 | 0.018311 | 0.086975 | 0 | 0.045776 | 0.036621 | -0.050354 | -0.13733 | 3.0212 | 2.8702 | -118.1122 | 3.1219 | 3.1586 | 0.28839 | -118.2495 | 3.0075 | 2.9205 | -118.2037 | 3.0762 | 3.0579 | 0.13733 | -118.2129 | 3.1952 | 3.0579 | 3.1174 | -118.4372 | 3.1036 | 3.0945 | 3.1448 | -118.3868
2736.8125 | 121.4813 | -3.1631 | 118.1671 | 0.0066373 | 0.0098822 | 0.054331 | 0.0064066 | 0.0038281 | -0.0024822 | -0.007857 | 0.014572 | -0.0053534 | 0.0050694 | -0.0017774 | -0.012617 | 0.019465 | -0.013733 | 0.027466 | 0.045776 | 0.091553 | 0.15106 | -0.041199 | -0.18768 | 0.018311 | 0.07782 | -0.018311 | 0.064087 | 0.054932 | -0.064087 | -0.11444 | 3.1219 | 2.9755 | -118.0161 | 3.1906 | 3.2547 | 0.27924 | -118.1808 | 3.0991 | 3.0487 | -118.103 | 3.1815 | 3.1448 | 0.09613 | -118.1122 | 3.3142 | 3.1494 | 3.2089 | -118.3548 | 3.2272 | 3.2181 | 3.241 | -118.2816
2738.5625 | 121.3577 | -2.8381 | 118.5379 | 0.0066373 | 0.013087 | 0.052408 | 0.002775 | 0.0038281 | 0.0032856 | -0.0052936 | 0.0069425 | -0.0023626 | 0.0037876 | -0.0022046 | -0.0059943 | 0.017756 | 0.07782 | 0.073242 | 0.064087 | 0.13275 | 0.14191 | -0.032043 | -0.18768 | 0.059509 | 0.073242 | -0.036621 | 0.054932 | 0.032043 | -0.050354 | -0.13275 | 2.8061 | 2.6505 | -118.396 | 2.9114 | 2.9709 | 0.32043 | -118.4601 | 2.7878 | 2.7054 | -118.483 | 2.8976 | 2.8015 | 0.09613 | -118.5059 | 2.98 | 2.916 | 2.9022 | -118.7256 | 2.8931 | 2.8702 | 2.9114 | -118.6707
2740.25 | 121.4767 | -3.0304 | 118.4235 | -0.00099167 | 0.013514 | 0.05369 | 0.005552 | 0.0042555 | 0.0067036 | -0.004439 | 0.0069425 | -0.0012946 | 0.006351 | -0.001991 | -0.0091985 | 0.018824 | -0.022888 | -0.059509 | -0.064087 | 0.064087 | 0.17853 | -0.073242 | -0.22888 | -0.068665 | -0.022888 | -0.16022 | 0.10071 | 0.082397 | -0.091553 | -0.16479 | 2.9572 | 2.8015 | -118.2449 | 2.9709 | 3.0945 | 0.29297 | -118.4463 | 2.9388 | 2.8656 | -118.3228 | 2.9617 | 2.8702 | 0.004578 | -118.3411 | 3.2089 | 3.0075 | 2.9663 | -118.6523 | 3.1311 | 3.1128 | 3.0075 | -118.5883
2742.0469 | 116.3544 | -81.8665 | 34.3369 | 0.0066373 | 0.011164 | 0.053049 | 0.0085428 | 0.0048963 | -0.002055 | -0.0055072 | 0.014572 | -0.0051398 | 0.0065646 | -0.0015638 | -0.012189 | 0.020961 | 0.082397 | 0.15106 | 0.10986 | 0.15106 | 0.16479 | -0.018311 | -0.16937 | 0.059509 | 0.14191 | 0.013733 | 0.068665 | 0.073242 | -0.032043 | -0.09613 | 81.8481 | 81.6971 | -34.1721 | 82.0175 | 82.0175 | 0.32044 | -34.2545 | 81.8344 | 81.7703 | -34.2682 | 81.926 | 81.8802 | 0.10986 | -34.2636 | 82.0312 | 81.9489 | 81.9763 | -34.5062 | 81.9351 | 81.9397 | 82.0084 | -34.433
2743.7344 | 121.0785 | -120.7214 | 0.1831 | -0.0086212 | 0.0090278 | 0.05604 | 0.0049112 | 0.0042555 | -0.0033368 | -0.0080706 | 0.014572 | -0.0042852 | 0.004642 | -0.0022046 | -0.010694 | 0.020533 | 0.045776 | 0.07782 | 0.073242 | 0.13275 | 0.19226 | -0.004578 | -0.14648 | 0.041199 | 0.10071 | 0 | 0.10986 | 0.086975 | -0.027466 | -0.09613 | 120.7169 | 120.575 | 0.009156 | 120.7993 | 120.8542 | 0.27924 | -0.13733 | 120.694 | 120.6253 | -0.073242 | 120.7626 | 120.7214 | 0.09613 | -0.09613 | 120.9137 | 120.7672 | 120.7947 | -0.32959 | 120.8313 | 120.8084 | 120.8221 | -0.27924
2745.4844 | 121.1563 | -120.8496 | 0.21057 | -0.00099167 | 0.014155 | 0.054544 | 0.0032022 | 0.0019055 | 0.0071308 | -0.0031574 | -0.00068649 | 0.00062796 | 0.0059238 | -0.0034864 | -0.0062079 | 0.017543 | 0.086975 | 0.059509 | 0.036621 | 0.10529 | 0.21057 | -0.018311 | -0.16937 | 0.004578 | 0.050354 | -0.10071 | 0.11444 | 0.09613 | -0.059509 | -0.11902 | 120.8313 | 120.6802 | 0 | 120.9091 | 120.9549 | 0.27466 | -0.1236 | 120.7901 | 120.7306 | -0.09613 | 120.8542 | 120.7489 | 0.018311 | -0.11444 | 121.0602 | 120.9366 | 120.8862 | -0.37994 | 120.9641 | 120.9457 | 120.9 | -0.32959
2747.25 | 121.1243 | -120.9686 | 0.21973 | -0.0086212 | 0.0073188 | 0.053904 | 0.0074746 | 0.0010511 | -0.00098684 | -0.0029436 | 0.0069425 | -0.0044988 | 0.0050694 | -0.001991 | -0.011762 | 0.021815 | 0.064087 | 0.10071 | 0.10071 | 0.12817 | 0.17395 | 0.013733 | -0.13275 | 0.036621 | 0.086975 | -0.018311 | 0.09613 | 0.086975 | -0.036621 | -0.09613 | 120.9824 | 120.8359 | -0.045777 | 121.0693 | 121.0968 | 0.26093 | -0.15564 | 120.932 | 120.8725 | -0.1236 | 121.0052 | 120.9503 | 0.077819 | -0.13275 | 121.1426 | 121.0327 | 121.0693 | -0.35248 | 121.0648 | 121.0556 | 121.0556 | -0.31586
2748.9375 | 116.6885 | -83.0887 | 33.6136 | -0.00099167 | 0.010096 | 0.054758 | 0.0059792 | 0.0029737 | 0.0037128 | -0.0042254 | 0.0069425 | -0.0030034 | 0.006351 | -0.0022046 | -0.0083441 | 0.019679 | 0.082397 | 0.086975 | 0.091553 | 0.16479 | 0.16479 | 0.022888 | -0.14648 | 0.086975 | 0.09613 | -0.009155 | 0.068665 | 0.054932 | -0.045776 | -0.082397 | 83.1116 | 82.9422 | -33.4488 | 83.1757 | 83.2535 | 0.31128 | -33.5312 | 83.0429 | 83.0063 | -33.5449 | 83.1757 | 83.0795 | 0.073242 | -33.5587 | 83.2535 | 83.1711 | 83.1802 | -33.7601 | 83.1573 | 83.1436 | 83.1848 | -33.696
2750.7031 | 120.8405 | -120.6985 | 0.20599 | -0.00099167 | 0.012659 | 0.051554 | 0.0044838 | 0.0036145 | 0.0037128 | -0.0040118 | -0.015945 | 0.0019098 | 0.0040012 | -0.003059 | -0.0072759 | 0.019679 | 0.004578 | -0.036621 | -0.036621 | 0.064087 | 0.23346 | -0.022888 | -0.17395 | -0.013733 | -0.018311 | -0.14648 | 0.13275 | 0.12817 | -0.068665 | -0.13733 | 120.6757 | 120.5246 | 0.027465 | 120.6619 | 120.7626 | 0.23804 | -0.20142 | 120.6299 | 120.5612 | -0.073243 | 120.6848 | 120.5521 | -0.009155 | -0.07782 | 120.932 | 120.7031 | 120.6619 | -0.37994 | 120.8313 | 120.8267 | 120.6802 | -0.34332
2752.4844 | 121.0327 | -120.7443 | 0.1831 | 0.0066373 | 0.012018 | 0.056467 | 0.01132 | 0.0029737 | -0.0035504 | -0.00508 | -0.00068649 | -0.0068488 | 0.0065646 | -0.0051954 | -0.013685 | 0.02267 | 0.10071 | 0.14648 | 0.15564 | 0.16022 | 0.16479 | 0.009155 | -0.15564 | 0.068665 | 0.15564 | 0.018311 | 0.07782 | 0.091553 | -0.018311 | -0.086975 | 120.7535 | 120.5887 | -0.01831 | 120.8908 | 120.9045 | 0.31586 | -0.082397 | 120.726 | 120.6573 | -0.10528 | 120.813 | 120.7626 | 0.10529 | -0.091552 | 120.9091 | 120.845 | 120.9 | -0.33874 | 120.8221 | 120.8359 | 120.9 | -0.27008
2754.1719 | 121.1197 | -120.7947 | 0.17853 | -0.00099167 | 0.01565 | 0.049845 | 0.0057656 | 0.0036145 | 0.0034992 | -0.003371 | 0.0069425 | 0.0010554 | 0.0067782 | -0.0034864 | -0.011549 | 0.019465 | 0.064087 | 0.032043 | 0.032043 | 0.13275 | 0.21515 | -0.027466 | -0.16937 | 0.032043 | 0.054932 | -0.082397 | 0.10986 | 0.13275 | -0.059509 | -0.1236 | 120.7672 | 120.6253 | 0.036621 | 120.8267 | 120.9274 | 0.30212 | -0.11444 | 120.7352 | 120.6711 | -0.068665 | 120.8267 | 120.7123 | 0.041199 | -0.045777 | 121.0098 | 120.8588 | 120.8267 | -0.3479 | 120.9045 | 120.9274 | 120.8496 | -0.30212
2755.8594 | 121.0968 | -120.8542 | 0.19684 | 0.0066373 | 0.011591 | 0.053476 | 0.0083292 | 0.0016919 | -0.0016278 | -0.0046526 | 0.014572 | -0.0070624 | 0.0065646 | -0.0017774 | -0.013471 | 0.022242 | 0.041199 | 0.07782 | 0.050354 | 0.13733 | 0.20599 | -0.004578 | -0.17853 | -0.036621 | 0.032043 | -0.09613 | 0.10071 | 0.1236 | -0.068665 | -0.11902 | 120.8496 | 120.6757 | 0.009156 | 120.932 | 120.9915 | 0.31586 | -0.15564 | 120.7855 | 120.7352 | -0.09613 | 120.8176 | 120.7581 | 0.022889 | -0.073242 | 121.0602 | 120.8954 | 120.9045 | -0.37537 | 120.9549 | 120.9778 | 120.8862 | -0.31586
2757.625 | 121.1655 | -120.8633 | 0.17853 | 0.0066373 | 0.0066778 | 0.055613 | 0.0040566 | 0.0025465 | -0.003764 | -0.004439 | -0.00068649 | -0.0047124 | 0.0054966 | -0.0011364 | -0.011976 | 0.019893 | 0.032043 | 0.073242 | 0.082397 | 0.14191 | 0.1831 | 0 | -0.15106 | 0.045776 | 0.10071 | 0.004578 | 0.09613 | 0.086975 | -0.036621 | -0.086975 | 120.8633 | 120.7123 | 0.004577 | 120.9366 | 121.0052 | 0.29297 | -0.14648 | 120.8267 | 120.7764 | -0.082398 | 120.9091 | 120.8679 | 0.091553 | -0.091553 | 121.0464 | 120.8954 | 120.9457 | -0.32959 | 120.9595 | 120.9503 | 120.9641 | -0.2655
2759.3125 | 121.0602 | -120.9274 | 0.21057 | 0.014267 | 0.009455 | 0.055185 | 0.0029886 | 0.0012647 | -0.00098684 | -0.0040118 | -0.00068649 | -0.0042852 | 0.0048556 | -0.0051954 | -0.01048 | 0.020106 | 0.10071 | 0.11444 | 0.11444 | 0.14648 | 0.18768 | 0.013733 | -0.11444 | 0.068665 | 0.091553 | 0.004578 | 0.082397 | 0.09613 | -0.022888 | -0.10071 | 120.9412 | 120.813 | -0.022888 | 121.0419 | 121.0739 | 0.26093 | -0.10986 | 120.9045 | 120.8267 | -0.12817 | 120.9961 | 120.932 | 0.10529 | -0.11444 | 121.1151 | 121.0281 | 121.0419 | -0.32501 | 121.0098 | 121.0236 | 121.019 | -0.31128
2761.0625 | 121.2112 | -120.9183 | 0.18768 | 0.014267 | 0.013727 | 0.053904 | 0.0079018 | 0.0034009 | 0.002431 | -0.0065752 | -0.00068649 | -0.0027898 | 0.0065646 | -0.0032728 | -0.012403 | 0.019679 | 0.013733 | 0.004578 | -0.009155 | 0.07782 | 0.21515 | -0.036621 | -0.16937 | -0.022888 | 0.018311 | -0.10986 | 0.13275 | 0.10986 | -0.086975 | -0.12817 | 120.8817 | 120.7489 | 0.027466 | 120.9229 | 120.9961 | 0.24719 | -0.17395 | 120.8313 | 120.7901 | -0.054932 | 120.8954 | 120.8084 | 0.018311 | -0.07782 | 121.1334 | 120.932 | 120.9091 | -0.35706 | 121.051 | 121.0281 | 120.9366 | -0.31586
2762.8281 | 121.106 | -120.9869 | 0.19684 | -0.00099167 | 0.010096 | 0.053263 | 0.0040566 | 0.0016919 | -0.0026958 | -0.0067888 | -0.00068649 | -0.0053534 | 0.004642 | -0.0051954 | -0.011976 | 0.02032 | 0.091553 | 0.10529 | 0.10071 | 0.14191 | 0.20142 | 0.018311 | -0.14648 | 0.059509 | 0.082397 | -0.018311 | 0.09613 | 0.07782 | -0.018311 | -0.10071 | 121.0052 | 120.8405 | 0.004578 | 121.0922 | 121.1288 | 0.28839 | -0.10529 | 120.9686 | 120.8862 | -0.10071 | 121.0464 | 120.9686 | 0.082397 | -0.11902 | 121.1884 | 121.0785 | 121.0876 | -0.34332 | 121.0831 | 121.0648 | 121.0693 | -0.29755
2764.5938 | 115.7593 | -77.6001 | 38.1454 | 0.0066373 | 0.016077 | 0.05369 | 0.0044838 | 0.0014783 | 0.00649 | -0.0046526 | -0.00068649 | -0.0015082 | 0.0050694 | -0.00070919 | -0.0077033 | 0.019893 | 0.004578 | -0.022888 | -0.027466 | 0.059509 | 0.21057 | -0.045776 | -0.19226 | -0.022888 | -0.041199 | -0.12817 | 0.1236 | 0.091553 | -0.068665 | -0.13275 | 77.5543 | 77.4078 | -37.9349 | 77.5772 | 77.6596 | 0.25177 | -38.1409 | 77.5314 | 77.4673 | -38.0219 | 77.5772 | 77.4719 | 0.004577 | -38.0539 | 77.8107 | 77.6047 | 77.5726 | -38.3377 | 77.7237 | 77.6917 | 77.5589 | -38.2782
2766.2812 | 120.7352 | -119.8563 | 0.74158 | 0.014267 | 0.014368 | 0.053904 | 0.0057656 | 0.0031873 | 0.0039264 | -0.0046526 | -0.00068649 | 0.00041436 | 0.0059238 | -0.00092279 | -0.0068487 | 0.019252 | 0.086975 | 0.068665 | 0.032043 | 0.11444 | 0.20142 | -0.036621 | -0.16022 | 0.022888 | 0.041199 | -0.10986 | 0.11444 | 0.10529 | -0.059509 | -0.10986 | 119.8196 | 119.696 | -0.54016 | 119.9249 | 119.9707 | 0.27466 | -0.6546 | 119.7968 | 119.7464 | -0.62714 | 119.8791 | 119.7464 | 0 | -0.63629 | 120.0577 | 119.9432 | 119.8883 | -0.90179 | 119.9707 | 119.9615 | 119.8975 | -0.85144
2768.0469 | 120.7855 | -120.0943 | 0.70496 | 0.014267 | 0.0088142 | 0.054758 | 0.0057656 | 0.00041006 | -0.003764 | -0.0042254 | 0.014572 | -0.0040716 | 0.0033604 | -0.0034864 | -0.01048 | 0.02032 | 0.07782 | 0.13733 | 0.11444 | 0.14191 | 0.16937 | 0 | -0.12817 | 0.064087 | 0.10986 | -0.004578 | 0.073242 | 0.091553 | -0.032043 | -0.082397 | 120.0943 | 119.9661 | -0.53558 | 120.2316 | 120.2362 | 0.27008 | -0.62714 | 120.0623 | 120.0119 | -0.63171 | 120.1584 | 120.0897 | 0.077819 | -0.6134 | 120.2637 | 120.1721 | 120.2087 | -0.83313 | 120.1675 | 120.1859 | 120.2042 | -0.78735
2769.7344 | 120.9045 | -118.8812 | 2.0233 | -0.00099167 | 0.0098822 | 0.055826 | 0.0091836 | 0.0036145 | -0.002055 | -0.0076434 | 0.014572 | -0.0070624 | 0.004642 | -0.003059 | -0.013685 | 0.02331 | 0.10986 | 0.14191 | 0.14191 | 0.16479 | 0.19684 | 0.009155 | -0.14191 | 0.086975 | 0.16479 | 0.054932 | 0.07782 | 0.082397 | -0.013733 | -0.07782 | 118.8904 | 118.7393 | -1.8265 | 119.0231 | 119.046 | 0.3067 | -1.9135 | 118.8675 | 118.8034 | -1.9455 | 118.9682 | 118.9362 | 0.13275 | -1.9409 | 119.0781 | 118.9911 | 119.0231 | -2.1652 | 118.959 | 118.9636 | 119.046 | -2.1011
2771.4844 | 120.9137 | -120.3049 | 0.59052 | -0.00099167 | 0.012873 | 0.051981 | 0.0076882 | 0.0021191 | 0.0054218 | -0.0031574 | -0.00068649 | -0.00065364 | 0.0074192 | -0.00049559 | -0.0074897 | 0.018397 | 0.082397 | 0.059509 | 0.027466 | 0.1236 | 0.21973 | -0.013733 | -0.16022 | 0.022888 | 0.041199 | -0.10071 | 0.11902 | 0.11902 | -0.050354 | -0.10529 | 120.2911 | 120.1447 | -0.37079 | 120.3644 | 120.4285 | 0.28381 | -0.50812 | 120.2545 | 120.1996 | -0.4715 | 120.3278 | 120.2042 | 0.004578 | -0.4715 | 120.5246 | 120.3873 | 120.3323 | -0.75073 | 120.4239 | 120.4239 | 120.3461 | -0.6958
2773.2344 | 120.9641 | -120.3918 | 0.55847 | -0.00099167 | 0.015436 | 0.052408 | 0.0053384 | 0.0031873 | 0.004781 | -0.0025164 | 0.0069425 | -0.0015082 | 0.006992 | -0.0022046 | -0.0096259 | 0.02032 | 0.082397 | 0.068665 | 0.032043 | 0.12817 | 0.20142 | -0.022888 | -0.1831 | 0.009155 | 0.059509 | -0.09613 | 0.11902 | 0.10071 | -0.041199 | -0.10529 | 120.369 | 120.2087 | -0.35706 | 120.4605 | 120.52 | 0.31128 | -0.47607 | 120.3506 | 120.2866 | -0.43945 | 120.401 | 120.2957 | 0.009156 | -0.45776 | 120.5933 | 120.4742 | 120.4239 | -0.74158 | 120.5109 | 120.4926 | 120.4514 | -0.66376
2774.9844 | 120.6345 | -120.314 | 0.58136 | 0.029526 | 0.016077 | 0.052622 | 0.010252 | 0.0031873 | 0.001363 | -0.0037982 | 0.014572 | -0.0034308 | 0.008701 | -0.0015638 | -0.01283 | 0.020533 | -0.027466 | 0 | 0 | 0.091553 | 0.23804 | -0.041199 | -0.19226 | -0.045776 | 0.009155 | -0.11902 | 0.14191 | 0.1236 | -0.07782 | -0.1236 | 120.2728 | 120.1218 | -0.34332 | 120.314 | 120.4056 | 0.28381 | -0.60883 | 120.2362 | 120.1904 | -0.43945 | 120.2682 | 120.195 | 0.004577 | -0.45776 | 120.5521 | 120.2866 | 120.314 | -0.77362 | 120.4559 | 120.4376 | 120.3232 | -0.70496
2776.7344 | 121.0098 | -120.3918 | 0.60883 | -0.00099167 | 0.011805 | 0.051767 | 0.0053384 | 0.0038281 | 0.0020038 | -0.003371 | 0.0069425 | -0.0034308 | 0.006351 | -0.0011364 | -0.0074897 | 0.020747 | 0.027466 | 0.045776 | 0.022888 | 0.091553 | 0.21057 | 0 | -0.15106 | 0.045776 | 0.068665 | -0.036621 | 0.086975 | 0.082397 | -0.009155 | -0.091553 | 120.3918 | 120.2408 | -0.39825 | 120.4376 | 120.4834 | 0.24261 | -0.58136 | 120.3827 | 120.3003 | -0.52185 | 120.4376 | 120.3552 | 0.054932 | -0.52643 | 120.6024 | 120.4193 | 120.4147 | -0.75989 | 120.4788 | 120.4742 | 120.4605 | -0.70038
2778.5 | 121.1151 | -120.3552 | 0.59509 | -0.0086212 | 0.014368 | 0.053263 | 0.011961 | 0.0040417 | 0.00029476 | -0.00508 | 0.014572 | -0.0025762 | 0.0091282 | -0.00028199 | -0.011549 | 0.019679 | -0.018311 | -0.013733 | -0.022888 | 0.086975 | 0.21057 | -0.027466 | -0.19684 | -0.050354 | 0.004578 | -0.11902 | 0.11902 | 0.12817 | -0.059509 | -0.11902 | 120.3278 | 120.1584 | -0.38452 | 120.3415 | 120.4422 | 0.28381 | -0.6134 | 120.2957 | 120.2362 | -0.47607 | 120.3049 | 120.2362 | 0 | -0.46692 | 120.5658 | 120.3369 | 120.3323 | -0.79193 | 120.4742 | 120.4834 | 120.3598 | -0.71411
2780.25 | 121.1243 | -120.4834 | 0.49439 | -0.00099167 | 0.015864 | 0.052408 | 0.00897 | 0.0029737 | 0.0032856 | -0.0040118 | -0.008316 | -0.00086724 | 0.0082736 | -0.0013502 | -0.010053 | 0.019679 | 0.032043 | 0.059509 | 0.059509 | 0.11444 | 0.21057 | -0.013733 | -0.16937 | 0.009155 | 0.082397 | -0.082397 | 0.11444 | 0.11902 | -0.059509 | -0.12817 | 120.4697 | 120.314 | -0.28381 | 120.5429 | 120.5978 | 0.28381 | -0.46234 | 120.4239 | 120.3552 | -0.37994 | 120.4926 | 120.401 | 0.045777 | -0.37537 | 120.694 | 120.5154 | 120.5429 | -0.66376 | 120.5978 | 120.6024 | 120.5658 | -0.62256
2781.9375 | 121.1151 | -120.5475 | 0.48065 | 0.0066373 | 0.012873 | 0.049631 | 0.0081154 | 0.0031873 | 0.0039264 | -0.004439 | 0.0069425 | -0.0012946 | 0.0072056 | -0.00070919 | -0.0085577 | 0.02032 | 0.041199 | 0.064087 | 0.050354 | 0.11444 | 0.2243 | -0.018311 | -0.1831 | 0.013733 | 0.07782 | -0.07782 | 0.1236 | 0.10071 | -0.036621 | -0.12817 | 120.5292 | 120.3644 | -0.25635 | 120.6116 | 120.6619 | 0.29755 | -0.43945 | 120.5109 | 120.4193 | -0.35706 | 120.5612 | 120.4697 | 0.050354 | -0.37994 | 120.7718 | 120.5887 | 120.5978 | -0.66376 | 120.6711 | 120.6482 | 120.6253 | -0.60883
2783.6875 | 121.1105 | -120.5109 | 0.46234 | 0.014267 | 0.013514 | 0.05369 | 0.012174 | 0.0055371 | -0.0033368 | -0.0046526 | -0.00068649 | -0.0017218 | 0.00806 | -0.0011364 | -0.01283 | 0.02032 | -0.054932 | 0.009155 | 0.022888 | 0.073242 | 0.2243 | -0.027466 | -0.17395 | -0.064087 | 0.018311 | -0.11444 | 0.14648 | 0.10529 | -0.068665 | -0.13275 | 120.4834 | 120.3369 | -0.23804 | 120.52 | 120.5841 | 0.24719 | -0.51727 | 120.4422 | 120.3781 | -0.31586 | 120.4468 | 120.3964 | 0.01831 | -0.35706 | 120.7352 | 120.4559 | 120.5338 | -0.63629 | 120.6573 | 120.6162 | 120.5292 | -0.59509
2785.4375 | 120.9412 | -120.52 | 0.49896 | -0.00099167 | 0.0088142 | 0.05604 | 0.010252 | 0.0036145 | -0.0056866 | -0.00508 | 0.014572 | -0.008985 | 0.0065646 | -0.0043408 | -0.015607 | 0.022029 | -0.004578 | 0.07782 | 0.07782 | 0.11902 | 0.19226 | 0.018311 | -0.12817 | 0.018311 | 0.068665 | -0.036621 | 0.09613 | 0.086975 | -0.045776 | -0.09613 | 120.5383 | 120.3918 | -0.3067 | 120.5978 | 120.639 | 0.24719 | -0.50354 | 120.4742 | 120.4239 | -0.40283 | 120.5383 | 120.4834 | 0.059509 | -0.41199 | 120.7123 | 120.5154 | 120.5978 | -0.62714 | 120.6162 | 120.607 | 120.5887 | -0.59509
2787.2031 | 118.7668 | -91.5619 | 27.7039 | -0.00099167 | 0.014368 | 0.051767 | 0.0093972 | 0.0012647 | -0.00055964 | -0.007857 | 0.0069425 | -0.0030034 | 0.0084872 | -0.00092279 | -0.011335 | 0.018611 | -0.032043 | 0 | -0.022888 | 0.068665 | 0.22888 | -0.045776 | -0.20599 | -0.045776 | 0 | -0.1236 | 0.12817 | 0.10529 | -0.086975 | -0.14191 | 91.5161 | 91.3559 | -27.475 | 91.5619 | 91.6306 | 0.27466 | -27.7359 | 91.4749 | 91.42 | -27.5757 | 91.5161 | 91.4383 | 0.018311 | -27.5986 | 91.7908 | 91.5298 | 91.539 | -27.9099 | 91.6901 | 91.6672 | 91.5619 | -27.8458
2788.8906 | 120.7397 | -99.5911 | 20.9335 | 0.014267 | 0.0092414 | 0.054758 | 0.0019204 | 0.0055371 | -0.0014142 | -0.0059344 | 0.014572 | -0.0036444 | 0.0033604 | -0.0022046 | -0.010267 | 0.021388 | 0.059509 | 0.10529 | 0.10071 | 0.14648 | 0.17395 | -0.004578 | -0.15106 | 0.032043 | 0.082397 | -0.009155 | 0.086975 | 0.07782 | -0.032043 | -0.10529 | 99.5865 | 99.44 | -20.7596 | 99.6964 | 99.7375 | 0.29755 | -20.874 | 99.559 | 99.4858 | -20.8466 | 99.6231 | 99.5819 | 0.096131 | -20.8557 | 99.765 | 99.6506 | 99.6918 | -21.0846 | 99.678 | 99.6689 | 99.6735 | -21.0388
2790.6406 | 120.9549 | -114.8163 | 5.896 | -0.00099167 | 0.012873 | 0.052835 | 0.003843 | 0.0023327 | 0.00414 | -0.0037982 | -0.00068649 | -0.0023626 | 0.0044284 | -0.0015638 | -0.0077033 | 0.019252 | 0.004578 | -0.004578 | -0.013733 | 0.086975 | 0.22888 | -0.018311 | -0.17853 | 0 | -0.004578 | -0.091553 | 0.10529 | 0.10071 | -0.032043 | -0.10071 | 114.798 | 114.6378 | -5.6671 | 114.8117 | 114.9033 | 0.2655 | -5.8914 | 114.7842 | 114.7156 | -5.7907 | 114.8163 | 114.7247 | 0.009155 | -5.7953 | 115.0452 | 114.8209 | 114.8026 | -6.0745 | 114.9216 | 114.917 | 114.8117 | -5.9967
2792.3281 | 121.051 | -115.4297 | 5.3009 | 0.0066373 | 0.009455 | 0.05604 | 0.0053384 | 0.0046827 | -0.0031232 | -0.0070026 | -0.00068649 | -0.0059942 | 0.0078464 | -0.0034864 | -0.012189 | 0.020106 | 0.086975 | 0.16022 | 0.13275 | 0.16937 | 0.19226 | 0.004578 | -0.14191 | 0.073242 | 0.16022 | 0.054932 | 0.09613 | 0.07782 | -0.027466 | -0.082397 | 115.4343 | 115.2878 | -5.1086 | 115.5899 | 115.5991 | 0.31128 | -5.2139 | 115.4022 | 115.3473 | -5.2048 | 115.5029 | 115.4846 | 0.13733 | -5.2231 | 115.6219 | 115.5167 | 115.5624 | -5.4428 | 115.5258 | 115.5075 | 115.5899 | -5.3833
2794.0781 | 120.9595 | -115.2328 | 5.6763 | -0.00099167 | 0.0066778 | 0.052622 | 0.0036294 | 0.0036145 | 0.00093576 | -0.0029436 | 0.0069425 | -0.0036444 | 0.004642 | -0.0034864 | -0.011335 | 0.021388 | 0.10071 | 0.12817 | 0.11444 | 0.16022 | 0.16479 | 0.032043 | -0.10986 | 0.064087 | 0.11444 | 0.009155 | 0.091553 | 0.068665 | -0.027466 | -0.10071 | 115.2649 | 115.123 | -5.5115 | 115.361 | 115.3931 | 0.27008 | -5.5756 | 115.2054 | 115.1321 | -5.5847 | 115.2969 | 115.242 | 0.10986 | -5.6076 | 115.3976 | 115.3336 | 115.3473 | -5.7861 | 115.3244 | 115.3015 | 115.3473 | -5.777
2795.8281 | 121.0876 | -104.3427 | 16.5253 | -0.0086212 | 0.012446 | 0.053049 | 0.0091836 | 0.0048963 | 0.004781 | -0.0055072 | 0.0069425 | -0.00086724 | 0.0089146 | -0.0017774 | -0.010694 | 0.019038 | 0.009155 | 0 | -0.013733 | 0.086975 | 0.21973 | -0.032043 | -0.19226 | -0.032043 | 0.027466 | -0.11902 | 0.14191 | 0.11444 | -0.07782 | -0.1236 | 104.3106 | 104.1504 | -16.3055 | 104.3427 | 104.4296 | 0.27924 | -16.5161 | 104.2648 | 104.2191 | -16.3834 | 104.3106 | 104.2236 | 0.004577 | -16.4108 | 104.5624 | 104.3518 | 104.3289 | -16.7175 | 104.4846 | 104.4571 | 104.3701 | -16.6489
2797.5938 | 121.0693 | -12.3505 | 108.5953 | -0.00099167 | 0.012873 | 0.053049 | 0.0074746 | 0.0025465 | 0.0026446 | -0.00508 | -0.00068649 | -0.002149 | 0.0076328 | -0.0017774 | -0.010267 | 0.02032 | -0.022888 | -0.045776 | -0.036621 | 0.054932 | 0.1831 | -0.073242 | -0.2243 | -0.054932 | -0.013733 | -0.1236 | 0.10529 | 0.07782 | -0.10986 | -0.15106 | 12.2772 | 12.1262 | -108.4122 | 12.3047 | 12.4054 | 0.27924 | -108.6182 | 12.2406 | 12.1994 | -108.49 | 12.2955 | 12.2269 | 0.027466 | -108.5175 | 12.5336 | 12.3276 | 12.3138 | -108.8196 | 12.4558 | 12.4283 | 12.3367 | -108.7463
2799.2969 | 120.3506 | -11.2335 | 109.8404 | 0.014267 | 0.013727 | 0.052408 | 0.0053384 | 0.0019055 | 0.0045674 | -0.0040118 | -0.00068649 | -0.0023626 | 0.0082736 | 0.00078621 | -0.01048 | 0.020747 | -0.036621 | -0.07782 | -0.045776 | 0.036621 | 0.18768 | -0.068665 | -0.21515 | -0.059509 | -0.073242 | -0.16479 | 0.10071 | 0.09613 | -0.09613 | -0.15564 | 11.1649 | 11.0184 | -109.6527 | 11.1557 | 11.2701 | 0.25177 | -109.877 | 11.1374 | 11.0779 | -109.7397 | 11.174 | 11.0687 | -0.009155 | -109.7443 | 11.4212 | 11.1969 | 11.1877 | -110.0555 | 11.3342 | 11.3297 | 11.1603 | -109.996
2801.0469 | 121.0419 | -10.7483 | 110.2753 | -0.00099167 | 0.013727 | 0.05369 | 0.0091836 | 0.0038281 | -0.0018414 | -0.0067888 | -0.00068649 | -0.0044988 | 0.00806 | -0.0024182 | -0.011121 | 0.020533 | -0.022888 | 0.022888 | 0.004578 | 0.091553 | 0.16937 | -0.050354 | -0.19684 | -0.07782 | 0 | -0.1236 | 0.07782 | 0.086975 | -0.091553 | -0.16022 | 10.6979 | 10.5515 | -110.1059 | 10.7712 | 10.8398 | 0.28839 | -110.2982 | 10.6567 | 10.5881 | -110.1974 | 10.6705 | 10.6247 | 0.036621 | -110.1883 | 10.9177 | 10.7254 | 10.7529 | -110.4721 | 10.8261 | 10.8353 | 10.7483 | -110.4355
2802.7344 | 120.8359 | -10.6934 | 110.3851 | 0.0066373 | 0.0086006 | 0.051767 | 0.0044838 | 0.0038281 | -0.00055964 | -0.0042254 | 0.014572 | -0.0059942 | 0.006992 | -0.001991 | -0.011762 | 0.020961 | 0.036621 | 0.09613 | 0.086975 | 0.10986 | 0.14648 | -0.027466 | -0.17395 | 0.032043 | 0.054932 | -0.032043 | 0.036621 | 0.050354 | -0.064087 | -0.1236 | 10.6659 | 10.5194 | -110.2386 | 10.7895 | 10.8032 | 0.28381 | -110.3485 | 10.6293 | 10.5698 | -110.3485 | 10.7254 | 10.6613 | 0.091553 | -110.3348 | 10.8398 | 10.73 | 10.7803 | -110.5591 | 10.73 | 10.7437 | 10.7483 | -110.5087
2804.5 | 121.106 | -10.5698 | 110.4584 | -0.00099167 | 0.0133 | 0.049417 | 0.005552 | 0.0042555 | 0.0071308 | -0.0048662 | -0.008316 | -0.002149 | 0.0074192 | -0.0011364 | -0.0087713 | 0.01797 | 0.022888 | 0.032043 | 0.004578 | 0.082397 | 0.17395 | -0.059509 | -0.20599 | -0.018311 | 0.009155 | -0.13275 | 0.059509 | 0.073242 | -0.073242 | -0.15106 | 10.5103 | 10.3638 | -110.2844 | 10.6018 | 10.6522 | 0.28839 | -110.4355 | 10.4965 | 10.4187 | -110.3989 | 10.5515 | 10.437 | 0.018311 | -110.3851 | 10.7437 | 10.5927 | 10.5743 | -110.6644 | 10.6293 | 10.643 | 10.5789 | -110.6094
2806.25 | 121.1609 | -10.4187 | 110.5911 | -0.00099167 | 0.01095 | 0.055185 | 0.0093972 | 0.0016919 | -0.0044048 | -0.0072162 | -0.00068649 | -0.005567 | 0.0057102 | -0.001991 | -0.014753 | 0.020533 | 0.013733 | 0.13733 | 0.11444 | 0.13733 | 0.13733 | -0.036621 | -0.16479 | 0.059509 | 0.15106 | 0 | 0.054932 | 0.050354 | -0.059509 | -0.1236 | 10.3821 | 10.2539 | -110.4538 | 10.556 | 10.556 | 0.30212 | -110.5774 | 10.3592 | 10.2951 | -110.5362 | 10.4782 | 10.4187 | 0.1236 | -110.5408 | 10.556 | 10.4324 | 10.5331 | -110.7559 | 10.4736 | 10.4691 | 10.5698 | -110.7147
2807.9375 | 121.0922 | -10.3958 | 110.701 | 0.014267 | 0.012446 | 0.052835 | 0.0023476 | 0.00062386 | 0.0045674 | -0.0037982 | 0.014572 | -0.0010808 | 0.0072056 | 0.00057261 | -0.0077033 | 0.019893 | -0.050354 | -0.068665 | -0.068665 | 0.032043 | 0.18768 | -0.064087 | -0.21973 | -0.059509 | -0.073242 | -0.14648 | 0.09613 | 0.086975 | -0.091553 | -0.16479 | 10.3317 | 10.1761 | -110.5133 | 10.3271 | 10.4279 | 0.25177 | -110.7513 | 10.3043 | 10.231 | -110.6049 | 10.3363 | 10.2493 | 0.018311 | -110.614 | 10.5835 | 10.3455 | 10.3271 | -110.9207 | 10.4919 | 10.4828 | 10.3226 | -110.8658
2809.6875 | 121.1151 | -10.3638 | 110.7468 | 0.0066373 | 0.014582 | 0.050913 | 0.0081154 | 0.0016919 | 0.004781 | -0.0040118 | 0.022202 | -0.0030034 | 0.0095554 | -0.00028199 | -0.0079169 | 0.016902 | 0.018311 | 0.027466 | 0.009155 | 0.082397 | 0.17395 | -0.054932 | -0.2243 | -0.009155 | 0.013733 | -0.14191 | 0.086975 | 0.073242 | -0.082397 | -0.16022 | 10.3088 | 10.1395 | -110.5728 | 10.3912 | 10.4462 | 0.3067 | -110.7285 | 10.2814 | 10.2036 | -110.6598 | 10.3546 | 10.2219 | 0.01831 | -110.6735 | 10.5377 | 10.3821 | 10.3729 | -110.9711 | 10.4507 | 10.437 | 10.3775 | -110.907
2811.375 | 121.2204 | -10.2127 | 110.8475 | -0.0086212 | 0.010523 | 0.053263 | 0.00897 | 0.0031873 | -0.0056866 | -0.0042254 | 0.0069425 | -0.0074896 | 0.0061374 | -0.0015638 | -0.015821 | 0.018824 | -0.009155 | 0.07782 | 0.082397 | 0.10986 | 0.14648 | -0.041199 | -0.1831 | 0.018311 | 0.09613 | 0.009155 | 0.059509 | 0.036621 | -0.07782 | -0.1236 | 10.1715 | 10.0296 | -110.701 | 10.2905 | 10.3226 | 0.29297 | -110.8566 | 10.1349 | 10.0891 | -110.788 | 10.231 | 10.2219 | 0.13275 | -110.8109 | 10.3592 | 10.2036 | 10.2951 | -111.0306 | 10.2722 | 10.2493 | 10.3088 | -110.9711
2813.1406 | 121.138 | -9.8602 | 111.2915 | 0.014267 | 0.013727 | 0.052408 | 0.0081154 | 0.0029737 | -0.0035504 | -0.0074298 | 0.014572 | -0.0047124 | 0.0067782 | -0.001991 | -0.014112 | 0.019893 | -0.045776 | 0.027466 | 0.027466 | 0.091553 | 0.16022 | -0.041199 | -0.19226 | -0.009155 | 0.036621 | -0.045776 | 0.07782 | 0.073242 | -0.068665 | -0.13275 | 9.819 | 9.668 | -111.1313 | 9.8877 | 9.9518 | 0.28381 | -111.3373 | 9.7916 | 9.7275 | -111.2137 | 9.8511 | 9.8145 | 0.086975 | -111.2183 | 10.0204 | 9.8145 | 9.8877 | -111.4838 | 9.938 | 9.9335 | 9.8969 | -111.4243
2814.8438 | 121.225 | -9.8099 | 111.2915 | -0.00099167 | 0.011805 | 0.055613 | 0.0076882 | 0.0034009 | -0.0024822 | -0.0063616 | -0.008316 | -0.0062078 | 0.0050694 | -0.0022046 | -0.013685 | 0.020961 | 0.041199 | 0.11902 | 0.09613 | 0.11902 | 0.16022 | -0.022888 | -0.1831 | 0.054932 | 0.12817 | 0.022888 | 0.041199 | 0.050354 | -0.054932 | -0.11444 | 9.787 | 9.6268 | -111.1313 | 9.9289 | 9.9289 | 0.30212 | -111.2503 | 9.7549 | 9.6954 | -111.2503 | 9.8648 | 9.8328 | 0.13733 | -111.2412 | 9.9701 | 9.8511 | 9.906 | -111.4746 | 9.8511 | 9.8602 | 9.938 | -111.4059
2816.5938 | 121.1472 | -9.8465 | 111.319 | 0.0066373 | 0.012232 | 0.053904 | 0.00063865 | 0.0031873 | 0.0039264 | -0.0063616 | -0.00068649 | -0.0017218 | 0.0054966 | -0.0013502 | -0.0070623 | 0.01797 | -0.032043 | -0.045776 | -0.041199 | 0.036621 | 0.18768 | -0.07782 | -0.21515 | -0.022888 | -0.059509 | -0.13733 | 0.082397 | 0.07782 | -0.07782 | -0.13733 | 9.7687 | 9.6313 | -111.1313 | 9.8007 | 9.8831 | 0.25177 | -111.351 | 9.7687 | 9.7092 | -111.2366 | 9.8236 | 9.7092 | 0 | -111.2411 | 10.0342 | 9.8145 | 9.8053 | -111.5341 | 9.9289 | 9.9243 | 9.787 | -111.4563
2818.3594 | 121.1975 | -9.6771 | 111.438 | 0.0066373 | 0.0133 | 0.055613 | 0.0081154 | 0.0044691 | -0.0016278 | -0.0048662 | -0.00068649 | -0.003858 | 0.005283 | -0.0034864 | -0.012403 | 0.019465 | 0.054932 | 0.10529 | 0.10071 | 0.12817 | 0.14648 | -0.013733 | -0.19226 | 0.022888 | 0.12817 | -0.013733 | 0.045776 | 0.045776 | -0.036621 | -0.12817 | 9.6634 | 9.4849 | -111.2915 | 9.7824 | 9.8053 | 0.32044 | -111.3831 | 9.6405 | 9.5489 | -111.3922 | 9.7 | 9.6634 | 0.11444 | -111.3922 | 9.8236 | 9.7321 | 9.7778 | -111.6302 | 9.7229 | 9.7229 | 9.8053 | -111.5662
2820.0625 | 121.2708 | -9.7321 | 111.3739 | 0.0066373 | 0.011805 | 0.054117 | 0.0085428 | 0.0023327 | -0.0031232 | -0.0065752 | 0.0069425 | -0.0057806 | 0.0054966 | -0.0028454 | -0.011976 | 0.020533 | 0.059509 | 0.10071 | 0.10071 | 0.1236 | 0.14648 | -0.045776 | -0.16937 | 0.059509 | 0.1236 | 0.013733 | 0.064087 | 0.054932 | -0.064087 | -0.10986 | 9.6863 | 9.5627 | -111.2274 | 9.8328 | 9.8557 | 0.29297 | -111.3144 | 9.668 | 9.6222 | -111.3098 | 9.7916 | 9.7458 | 0.1236 | -111.319 | 9.8785 | 9.7916 | 9.8328 | -111.5433 | 9.7961 | 9.787 | 9.8557 | -111.4838
2821.75 | 121.2021 | -9.6863 | 111.4929 | -0.00099167 | 0.012659 | 0.052622 | 0.002775 | 0.0040417 | 0.003072 | -0.0035846 | -0.008316 | -0.0023626 | 0.0033604 | -0.0032728 | -0.0077033 | 0.01797 | 0.073242 | 0.054932 | 0.054932 | 0.11444 | 0.14648 | -0.022888 | -0.17853 | 0.045776 | 0.068665 | -0.032043 | 0.050354 | 0.054932 | -0.054932 | -0.10529 | 9.6634 | 9.5078 | -111.3464 | 9.7412 | 9.8007 | 0.29297 | -111.4197 | 9.6313 | 9.581 | -111.4426 | 9.7321 | 9.6542 | 0.073243 | -111.438 | 9.8328 | 9.7595 | 9.7412 | -111.6714 | 9.7366 | 9.7412 | 9.7549 | -111.5982
2823.5 | 121.3165 | -9.3933 | 111.7493 | -0.00099167 | 0.017786 | 0.051981 | 0.0053384 | 0.0042555 | 0.0020038 | -0.0046526 | -0.008316 | -0.0015082 | 0.0040012 | -0.0022046 | -0.0089849 | 0.017115 | -0.022888 | -0.036621 | -0.045776 | 0.073242 | 0.18768 | -0.086975 | -0.21973 | -0.018311 | 0 | -0.1236 | 0.091553 | 0.068665 | -0.091553 | -0.14648 | 9.3063 | 9.1736 | -111.5616 | 9.3567 | 9.4666 | 0.29297 | -111.7722 | 9.3018 | 9.2468 | -111.6577 | 9.375 | 9.2697 | 0.022888 | -111.6806 | 9.581 | 9.3704 | 9.3475 | -111.969 | 9.4849 | 9.462 | 9.3933 | -111.8958
2825.25 | 121.2799 | -8.7433 | 112.413 | 0.0066373 | 0.012018 | 0.053263 | 0.0093972 | 0.0010511 | -0.00055964 | -0.0042254 | -0.00068649 | -0.0077032 | 0.0065646 | -0.0034864 | -0.014112 | 0.019679 | 0.054932 | 0.1236 | 0.086975 | 0.13275 | 0.14191 | -0.036621 | -0.18768 | 0.032043 | 0.13275 | 0.004578 | 0.054932 | 0.032043 | -0.068665 | -0.10986 | 8.7067 | 8.5556 | -112.2711 | 8.8669 | 8.876 | 0.32043 | -112.3581 | 8.6746 | 8.6334 | -112.3581 | 8.7753 | 8.7479 | 0.11444 | -112.381 | 8.8852 | 8.7982 | 8.8303 | -112.6007 | 8.7982 | 8.7753 | 8.876 | -112.5229
2826.9375 | 121.2845 | -8.3862 | 112.7975 | 0.0066373 | 0.014796 | 0.049204 | 0.0074746 | 0.00083746 | 0.00414 | -0.0048662 | 0.0069425 | -0.0025762 | 0.010196 | 0.00057261 | -0.0083441 | 0.020747 | 0.009155 | 0.036621 | 0.009155 | 0.086975 | 0.16479 | -0.07782 | -0.21973 | 0 | 0.032043 | -0.11902 | 0.086975 | 0.073242 | -0.086975 | -0.13733 | 8.3084 | 8.1665 | -112.6328 | 8.4229 | 8.4732 | 0.3067 | -112.7884 | 8.2993 | 8.2489 | -112.7106 | 8.3862 | 8.2672 | 0.01831 | -112.7243 | 8.551 | 8.3954 | 8.3954 | -113.0173 | 8.4732 | 8.4595 | 8.4183 | -112.9349
2828.6875 | 121.3348 | -7.8781 | 113.3057 | -0.00099167 | 0.016077 | 0.054331 | 0.0068338 | 0.0051099 | 0.0039264 | -0.0059344 | -0.00068649 | -0.00044004 | 0.006992 | -0.0017774 | -0.010267 | 0.02032 | -0.041199 | -0.022888 | -0.050354 | 0.050354 | 0.17853 | -0.059509 | -0.21057 | -0.045776 | 0.004578 | -0.13733 | 0.10071 | 0.086975 | -0.10529 | -0.16022 | 7.8186 | 7.6675 | -113.1271 | 7.8552 | 7.9285 | 0.26093 | -113.3469 | 7.7728 | 7.7179 | -113.205 | 7.8323 | 7.7408 | 0.022888 | -113.2187 | 8.0566 | 7.8369 | 7.8278 | -113.5162 | 7.9788 | 7.9651 | 7.8827 | -113.4659
2830.375 | 121.2204 | -7.8552 | 113.4293 | -0.00099167 | 0.016077 | 0.051767 | 0.0068338 | 0.0023327 | 0.00414 | -0.0037982 | 0.0069425 | -0.0015082 | 0.0091282 | -0.0013502 | -0.0087713 | 0.020106 | 0 | 0.009155 | -0.018311 | 0.086975 | 0.16022 | -0.045776 | -0.2243 | -0.027466 | -0.004578 | -0.16022 | 0.082397 | 0.073242 | -0.082397 | -0.14648 | 7.8094 | 7.6309 | -113.269 | 7.8644 | 7.9422 | 0.31128 | -113.4293 | 7.7728 | 7.7087 | -113.3469 | 7.8278 | 7.695 | -0.013733 | -113.356 | 8.0154 | 7.8552 | 7.8369 | -113.6536 | 7.9376 | 7.9285 | 7.8506 | -113.5757
2832.125 | 121.2662 | -6.9351 | 114.3539 | 0.0066373 | 0.01095 | 0.054758 | 0.0074746 | 0.0016919 | -0.0050458 | -0.0042254 | 0.0069425 | -0.007276 | 0.0065646 | -0.0051954 | -0.011762 | 0.023097 | -0.036621 | 0.022888 | 0.036621 | 0.09613 | 0.15564 | -0.036621 | -0.16937 | -0.009155 | 0.050354 | -0.041199 | 0.050354 | 0.068665 | -0.068665 | -0.13733 | 6.8985 | 6.7657 | -114.1983 | 6.958 | 7.0312 | 0.2655 | -114.3906 | 6.8665 | 6.7978 | -114.3036 | 6.926 | 6.8939 | 0.09613 | -114.2853 | 7.0908 | 6.8985 | 6.9717 | -114.5233 | 6.9855 | 7.0038 | 6.9855 | -114.4913
2833.8906 | 121.2982 | -6.7795 | 114.4959 | -0.00099167 | 0.0088142 | 0.054758 | 0.0083292 | 0.0036145 | -0.0022686 | -0.0042254 | 0.0069425 | -0.0059942 | 0.005283 | -0.0041272 | -0.010908 | 0.020533 | -0.036621 | 0.009155 | 0.032043 | 0.086975 | 0.14648 | -0.022888 | -0.17395 | -0.013733 | 0.059509 | -0.050354 | 0.054932 | 0.054932 | -0.068665 | -0.14648 | 6.7566 | 6.6055 | -114.3494 | 6.7886 | 6.8665 | 0.26092 | -114.5325 | 6.7108 | 6.633 | -114.4409 | 6.7657 | 6.7291 | 0.09613 | -114.4409 | 6.926 | 6.7429 | 6.8115 | -114.6698 | 6.8344 | 6.8344 | 6.839 | -114.6423
2835.6406 | 121.2753 | -6.6422 | 114.6423 | 0.0066373 | 0.012659 | 0.05369 | 0.0032022 | 0.00041006 | 0.002431 | -0.0059344 | -0.00068649 | -0.0025762 | 0.0057102 | -0.0013502 | -0.0077033 | 0.01797 | 0.027466 | 0.022888 | 0.013733 | 0.07782 | 0.17395 | -0.045776 | -0.18768 | 0.045776 | 0.045776 | -0.041199 | 0.041199 | 0.045776 | -0.064087 | -0.11902 | 6.5964 | 6.4545 | -114.4684 | 6.665 | 6.72 | 0.2655 | -114.6149 | 6.5781 | 6.5231 | -114.6011 | 6.6879 | 6.601 | 0.07782 | -114.5966 | 6.8161 | 6.6696 | 6.6559 | -114.83 | 6.6833 | 6.6879 | 6.6879 | -114.7614
2837.3281 | 121.2616 | -6.6879 | 114.6744 | -0.00099167 | 0.011805 | 0.050058 | 0.0032022 | 0.0029737 | 0.0045674 | -0.0046526 | 0.022202 | -0.0010808 | 0.0059238 | -0.00028199 | -0.0066351 | 0.018397 | -0.050354 | -0.073242 | -0.064087 | 0.041199 | 0.18768 | -0.064087 | -0.22888 | -0.068665 | -0.068665 | -0.19226 | 0.086975 | 0.068665 | -0.11444 | -0.16022 | 6.6238 | 6.459 | -114.4867 | 6.6147 | 6.7291 | 0.27008 | -114.7247 | 6.5735 | 6.5277 | -114.5874 | 6.6193 | 6.4957 | -0.032044 | -114.6057 | 6.8756 | 6.6376 | 6.6238 | -114.9033 | 6.7749 | 6.7566 | 6.6193 | -114.8346
2839.0781 | 121.2387 | -6.5186 | 114.798 | 0.0066373 | 0.011164 | 0.054758 | 0.005552 | 0.0048963 | -0.00055964 | -0.0037982 | 0.014572 | -0.0049262 | 0.0027194 | -0.0026318 | -0.010908 | 0.018611 | 0.059509 | 0.09613 | 0.086975 | 0.1236 | 0.13733 | -0.018311 | -0.17395 | 0.050354 | 0.10071 | -0.018311 | 0.027466 | 0.032043 | -0.064087 | -0.10529 | 6.5002 | 6.3446 | -114.6606 | 6.6147 | 6.6422 | 0.29755 | -114.7385 | 6.4545 | 6.4133 | -114.7705 | 6.5689 | 6.5002 | 0.086975 | -114.7659 | 6.6559 | 6.5781 | 6.6055 | -114.9719 | 6.546 | 6.5506 | 6.6193 | -114.9033
2840.7656 | 121.2616 | -6.8848 | 114.4501 | -0.00099167 | 0.0081732 | 0.054972 | 0.0040566 | 0.00062386 | -0.0022686 | -0.0087114 | 0.0069425 | -0.0040716 | 0.0040012 | -0.0015638 | -0.011549 | 0.021388 | 0.013733 | 0.059509 | 0.050354 | 0.091553 | 0.15106 | -0.032043 | -0.1831 | 0 | 0.036621 | -0.045776 | 0.045776 | 0.059509 | -0.050354 | -0.13275 | 6.8527 | 6.7017 | -114.299 | 6.9443 | 6.9763 | 0.27466 | -114.4363 | 6.8344 | 6.752 | -114.4043 | 6.8848 | 6.839 | 0.086975 | -114.3906 | 7.0358 | 6.8985 | 6.9351 | -114.6332 | 6.9305 | 6.9443 | 6.9214 | -114.5828
2842.5312 | 121.3852 | -6.546 | 114.7385 | -0.00099167 | 0.011164 | 0.053476 | 0.0066202 | 0.0036145 | -0.00055964 | -0.0059344 | 0.0069425 | -0.0017218 | 0.0067782 | -0.0041272 | -0.011335 | 0.018397 | -0.032043 | -0.050354 | -0.045776 | 0.022888 | 0.19226 | -0.073242 | -0.23346 | -0.07782 | -0.036621 | -0.16479 | 0.11444 | 0.091553 | -0.10529 | -0.15106 | 6.4728 | 6.3126 | -114.5462 | 6.4957 | 6.5689 | 0.25635 | -114.7705 | 6.4407 | 6.395 | -114.624 | 6.4682 | 6.3812 | -0.013733 | -114.6469 | 6.7383 | 6.514 | 6.5002 | -114.9719 | 6.6605 | 6.6376 | 6.5094 | -114.8895
2844.2344 | 121.3943 | -6.427 | 114.8117 | 0.0066373 | 0.0086006 | 0.058176 | 0.0068338 | 0.00083746 | -0.0033368 | -0.0059344 | -0.00068649 | -0.0059942 | 0.0054966 | -0.0045544 | -0.011762 | 0.019679 | 0.027466 | 0.068665 | 0.07782 | 0.1236 | 0.14191 | -0.036621 | -0.18768 | 0.050354 | 0.10071 | 0.004578 | 0.059509 | 0.041199 | -0.059509 | -0.1236 | 6.3904 | 6.2393 | -114.6698 | 6.4957 | 6.5506 | 0.31128 | -114.7842 | 6.3675 | 6.3034 | -114.7522 | 6.4774 | 6.4316 | 0.12817 | -114.7705 | 6.5689 | 6.4545 | 6.5048 | -114.9994 | 6.4865 | 6.4682 | 6.5277 | -114.9353
2845.9688 | 121.2891 | -6.8069 | 114.5874 | -0.00099167 | 0.014582 | 0.050486 | 0.0053384 | 0.0021191 | 0.0049946 | -0.003371 | 0.0069425 | -0.00022644 | 0.008701 | -0.00092279 | -0.0072759 | 0.01797 | -0.018311 | -0.050354 | -0.050354 | 0.041199 | 0.18768 | -0.054932 | -0.21515 | -0.064087 | -0.036621 | -0.18768 | 0.09613 | 0.09613 | -0.10986 | -0.16479 | 6.752 | 6.5918 | -114.3997 | 6.7566 | 6.8481 | 0.25635 | -114.6057 | 6.6971 | 6.6422 | -114.4913 | 6.7429 | 6.6193 | -0.022888 | -114.4913 | 6.9946 | 6.7886 | 6.7566 | -114.8026 | 6.9031 | 6.9031 | 6.7703 | -114.7522
2847.6719 | 120.5017 | -25.3143 | 95.5032 | 0.0066373 | 0.011591 | 0.052195 | 0.0042702 | 0.0053235 | 8.1158e-05 | -0.0040118 | 0.0069425 | -0.0030034 | 0.0054966 | -0.00070919 | -0.0096259 | 0.018824 | 0.054932 | 0.036621 | 0.041199 | 0.11444 | 0.17395 | -0.018311 | -0.19226 | 0.050354 | 0.07782 | -0.032043 | 0.041199 | 0.068665 | -0.054932 | -0.10986 | 25.296 | 25.1221 | -95.3293 | 25.351 | 25.4288 | 0.3067 | -95.4483 | 25.2594 | 25.2045 | -95.462 | 25.3647 | 25.2823 | 0.07782 | -95.4346 | 25.4883 | 25.3693 | 25.3555 | -95.6955 | 25.3555 | 25.383 | 25.3922 | -95.6131
2849.4375 | 120.7443 | -6.7566 | 114.2212 | -0.00099167 | 0.011378 | 0.052622 | 0.0087564 | 0.0046827 | -0.0024822 | -0.0059344 | 0.0069425 | -0.0081304 | 0.0078464 | -0.0017774 | -0.015394 | 0.022456 | -0.009155 | 0.032043 | 0.064087 | 0.082397 | 0.16479 | -0.032043 | -0.17395 | 0 | 0.059509 | -0.036621 | 0.054932 | 0.059509 | -0.068665 | -0.13275 | 6.7245 | 6.5826 | -114.0564 | 6.7886 | 6.839 | 0.25635 | -114.2303 | 6.6879 | 6.6238 | -114.1663 | 6.7566 | 6.72 | 0.09613 | -114.1617 | 6.9214 | 6.7474 | 6.8207 | -114.3951 | 6.8115 | 6.8161 | 6.8161 | -114.3539
2851.1406 | 121.0922 | -5.809 | 115.2145 | -0.00099167 | 0.01095 | 0.05369 | 0.007261 | 0.0016919 | -0.0041912 | -0.0072162 | -0.00068649 | -0.0057806 | 0.0040012 | -0.0041272 | -0.011762 | 0.02032 | -0.013733 | 0.027466 | 0.050354 | 0.07782 | 0.15106 | -0.036621 | -0.17395 | 0.027466 | 0.064087 | -0.032043 | 0.050354 | 0.059509 | -0.07782 | -0.12817 | 5.7724 | 5.6351 | -115.0635 | 5.8365 | 5.8868 | 0.25177 | -115.2283 | 5.7312 | 5.6808 | -115.1642 | 5.8365 | 5.777 | 0.096131 | -115.155 | 5.9601 | 5.7953 | 5.8594 | -115.3885 | 5.8594 | 5.8685 | 5.8731 | -115.3427
2852.8906 | 120.3186 | -5.7587 | 115.3061 | -0.0086212 | 0.011591 | 0.050913 | 0.007261 | 0.0034009 | 0.0039264 | -0.00508 | 0.0069425 | -0.0023626 | 0.0065646 | -0.00049559 | -0.0096259 | 0.016902 | -0.009155 | -0.022888 | -0.036621 | 0.045776 | 0.16479 | -0.068665 | -0.20142 | 0 | 0 | -0.086975 | 0.068665 | 0.059509 | -0.073242 | -0.12817 | 5.69 | 5.5573 | -115.1413 | 5.7358 | 5.8044 | 0.24719 | -115.3152 | 5.6854 | 5.6305 | -115.2374 | 5.7587 | 5.6717 | 0.041199 | -115.2466 | 5.9235 | 5.7495 | 5.722 | -115.5075 | 5.8273 | 5.8182 | 5.7587 | -115.4343
2854.5938 | 121.1975 | -5.8365 | 115.2832 | -0.0086212 | 0.011591 | 0.05134 | 0.007261 | 0.0034009 | 0.002431 | -0.0037982 | -0.008316 | -0.00022644 | 0.0065646 | -0.0017774 | -0.0074897 | 0.016688 | -0.032043 | -0.013733 | -0.036621 | 0.059509 | 0.16479 | -0.07782 | -0.2243 | -0.041199 | 0.009155 | -0.13275 | 0.091553 | 0.07782 | -0.09613 | -0.14648 | 5.7587 | 5.6122 | -115.1184 | 5.8228 | 5.896 | 0.28381 | -115.3152 | 5.7404 | 5.69 | -115.1916 | 5.7953 | 5.7037 | 0.013733 | -115.2054 | 6.0013 | 5.8044 | 5.7999 | -115.5075 | 5.928 | 5.9143 | 5.8456 | -115.4297
2856.3438 | 121.1792 | -5.0034 | 116.098 | 0.0066373 | 0.011805 | 0.052622 | 0.0093972 | 0.0034009 | -0.0035504 | -0.0037982 | 0.0069425 | -0.0053534 | 0.0050694 | -0.0024182 | -0.013044 | 0.019465 | 0.041199 | 0.11444 | 0.09613 | 0.11902 | 0.15106 | -0.036621 | -0.16937 | 0.032043 | 0.13275 | -0.009155 | 0.041199 | 0.036621 | -0.059509 | -0.11902 | 4.9667 | 4.834 | -115.947 | 5.1178 | 5.1224 | 0.28839 | -116.0568 | 4.9438 | 4.8843 | -116.0568 | 5.0354 | 4.9942 | 0.10986 | -116.0614 | 5.1544 | 5.0446 | 5.0995 | -116.2674 | 5.0446 | 5.04 | 5.1361 | -116.217
2858.0938 | 121.0785 | -4.7379 | 116.4734 | 0.0066373 | 0.0090278 | 0.053049 | 0.0044838 | 0.0029737 | 0.0015766 | -0.0059344 | -0.00068649 | -0.0062078 | 0.0048556 | -0.003059 | -0.011762 | 0.019679 | 0.041199 | 0.086975 | 0.07782 | 0.10986 | 0.12817 | -0.027466 | -0.16479 | 0.013733 | 0.054932 | -0.036621 | 0.054932 | 0.054932 | -0.068665 | -0.1236 | 4.7104 | 4.5731 | -116.3452 | 4.8248 | 4.8477 | 0.27466 | -116.4322 | 4.6692 | 4.6143 | -116.4185 | 4.7516 | 4.7012 | 0.086975 | -116.4185 | 4.866 | 4.7791 | 4.8157 | -116.6382 | 4.7928 | 4.7928 | 4.7928 | -116.597
2859.7812 | 121.2204 | -4.66 | 116.5146 | -0.0086212 | 0.011805 | 0.055613 | 0.0085428 | 0.0021191 | -0.0031232 | -0.0065752 | 0.0069425 | -0.003858 | 0.0084872 | -0.0024182 | -0.011976 | 0.018824 | 0.054932 | 0.11444 | 0.09613 | 0.12817 | 0.15564 | -0.050354 | -0.17395 | 0.041199 | 0.12817 | -0.009155 | 0.041199 | 0.050354 | -0.045776 | -0.10071 | 4.6097 | 4.4861 | -116.3589 | 4.7745 | 4.7882 | 0.30212 | -116.4597 | 4.6143 | 4.5593 | -116.4734 | 4.7012 | 4.6509 | 0.091553 | -116.4642 | 4.8157 | 4.715 | 4.7562 | -116.6885 | 4.7012 | 4.7104 | 4.7882 | -116.6153
2861.5156 | 121.1792 | -3.5385 | 117.7231 | 0.0066373 | 0.016291 | 0.052622 | 0.0096108 | 0.0053235 | 0.0052082 | -0.0057208 | -0.00068649 | 0.00084176 | 0.0082736 | -0.00092279 | -0.0083441 | 0.01797 | 0.050354 | 0.013733 | 0.004578 | 0.07782 | 0.18768 | -0.054932 | -0.2243 | 0 | 0.004578 | -0.13733 | 0.10071 | 0.07782 | -0.073242 | -0.16022 | 3.4836 | 3.3142 | -117.5354 | 3.5522 | 3.6163 | 0.30212 | -117.6727 | 3.4653 | 3.3783 | -117.6224 | 3.5385 | 3.4012 | 0.022888 | -117.6453 | 3.7262 | 3.5889 | 3.5431 | -117.9474 | 3.6392 | 3.6163 | 3.5431 | -117.8833
2863.2656 | 121.3074 | -3.5477 | 117.659 | 0.0066373 | 0.016718 | 0.054331 | 0.0083292 | 0.0042555 | 0.003072 | -0.0029436 | 0.014572 | -0.0019354 | 0.008701 | -0.001991 | -0.011762 | 0.018184 | -0.036621 | -0.041199 | -0.032043 | 0.059509 | 0.17853 | -0.054932 | -0.22888 | -0.032043 | 0.004578 | -0.1236 | 0.10986 | 0.10529 | -0.09613 | -0.14648 | 3.4927 | 3.3188 | -117.4805 | 3.5065 | 3.6072 | 0.28839 | -117.6956 | 3.4515 | 3.4012 | -117.5491 | 3.5156 | 3.4241 | 0.022888 | -117.5537 | 3.7262 | 3.511 | 3.5156 | -117.8879 | 3.6575 | 3.653 | 3.5522 | -117.8055
2865.0312 | 121.2112 | -3.0899 | 118.1488 | 0.014267 | 0.013941 | 0.050486 | 0.0057656 | 0.0021191 | 0.003072 | -0.0057208 | 0.0069425 | -0.0017218 | 0.0061374 | -6.8386e-05 | -0.0089849 | 0.021174 | -0.027466 | -0.054932 | -0.041199 | 0.050354 | 0.18768 | -0.059509 | -0.2243 | -0.027466 | -0.022888 | -0.10986 | 0.09613 | 0.064087 | -0.073242 | -0.14191 | 3.0304 | 2.8656 | -117.9611 | 3.035 | 3.1403 | 0.27466 | -118.1763 | 3.0167 | 2.948 | -118.0527 | 3.0624 | 2.98 | 0.032044 | -118.0847 | 3.2776 | 3.0624 | 3.0487 | -118.3731 | 3.186 | 3.154 | 3.067 | -118.2907
2866.7344 | 121.2158 | -3.3737 | 117.897 | -0.00099167 | 0.014368 | 0.053263 | 0.0040566 | 0.0044691 | 0.002431 | -0.0020892 | 0.0069425 | -0.003858 | 0.0061374 | -0.001991 | -0.0091985 | 0.021174 | -0.041199 | -0.036621 | -0.054932 | 0.045776 | 0.16022 | -0.068665 | -0.21057 | -0.018311 | 0 | -0.10071 | 0.086975 | 0.068665 | -0.068665 | -0.14191 | 3.3051 | 3.1631 | -117.7368 | 3.3371 | 3.4195 | 0.25635 | -117.9382 | 3.3051 | 3.2318 | -117.8101 | 3.3554 | 3.273 | 0.041199 | -117.8284 | 3.5339 | 3.3325 | 3.3188 | -118.1076 | 3.4607 | 3.4424 | 3.3737 | -118.0389
2868.4844 | 121.225 | -3.4058 | 117.9062 | 0.021896 | 0.0133 | 0.051767 | 0.0059792 | 0.0048963 | 0.0032856 | -0.004439 | 0.0069425 | -0.0015082 | 0.0065646 | -0.00028199 | -0.0072759 | 0.019679 | -0.050354 | -0.091553 | -0.073242 | 0.027466 | 0.18768 | -0.059509 | -0.21515 | -0.059509 | -0.064087 | -0.14191 | 0.09613 | 0.086975 | -0.086975 | -0.15106 | 3.3463 | 3.1906 | -117.7185 | 3.3142 | 3.4332 | 0.24261 | -117.9565 | 3.3188 | 3.2547 | -117.8101 | 3.3463 | 3.2639 | 0.009155 | -117.8192 | 3.5934 | 3.3554 | 3.3325 | -118.1213 | 3.5019 | 3.4927 | 3.3417 | -118.0573
2870.2344 | 121.2112 | -3.3646 | 117.984 | 0.0066373 | 0.015009 | 0.053049 | 0.0066202 | 0.0021191 | 0.0032856 | -0.0052936 | -0.00068649 | -0.00065364 | 0.0067782 | -0.00092279 | -0.0077033 | 0.021174 | 0.013733 | -0.022888 | -0.018311 | 0.068665 | 0.17395 | -0.045776 | -0.21973 | -0.050354 | -0.022888 | -0.16022 | 0.07782 | 0.07782 | -0.07782 | -0.14191 | 3.3188 | 3.1448 | -117.8101 | 3.3417 | 3.4332 | 0.28839 | -117.9703 | 3.2867 | 3.2227 | -117.9062 | 3.3142 | 3.2043 | -0.01831 | -117.9062 | 3.5385 | 3.3783 | 3.3463 | -118.2037 | 3.4424 | 3.4424 | 3.3417 | -118.1259
2871.9219 | 121.2341 | -3.6667 | 117.6544 | 0.0066373 | 0.012873 | 0.053476 | 0.0076882 | 0.0025465 | 0.0026446 | -0.0046526 | -0.00068649 | -0.0034308 | 0.0078464 | -0.00070919 | -0.0094123 | 0.019465 | -0.068665 | -0.07782 | -0.059509 | 0.041199 | 0.1831 | -0.073242 | -0.20599 | -0.068665 | -0.064087 | -0.15564 | 0.09613 | 0.091553 | -0.09613 | -0.15106 | 3.5934 | 3.4607 | -117.4713 | 3.5889 | 3.7079 | 0.24719 | -117.7231 | 3.5706 | 3.5156 | -117.5583 | 3.598 | 3.511 | -0.004578 | -117.5629 | 3.8498 | 3.598 | 3.6072 | -117.8604 | 3.7628 | 3.7582 | 3.6026 | -117.8055
2873.6719 | 121.2845 | -2.7466 | 118.5516 | -0.0086212 | 0.014582 | 0.054117 | 0.010893 | 0.0046827 | -0.0029094 | -0.004439 | 0.014572 | -0.0070624 | 0.009769 | -0.0013502 | -0.012617 | 0.019038 | -0.027466 | 0.009155 | 0.004578 | 0.086975 | 0.16479 | -0.064087 | -0.21515 | -0.082397 | 0.018311 | -0.1236 | 0.091553 | 0.082397 | -0.10071 | -0.15564 | 2.6825 | 2.5314 | -118.3868 | 2.7557 | 2.8336 | 0.30212 | -118.5791 | 2.6459 | 2.5909 | -118.4601 | 2.6642 | 2.623 | 0.032044 | -118.4692 | 2.9114 | 2.7191 | 2.7512 | -118.7668 | 2.8381 | 2.829 | 2.7649 | -118.7073
2875.4375 | 121.3623 | -2.2842 | 118.9865 | 0.021896 | 0.0092414 | 0.056253 | 0.010465 | 0.0027601 | -0.0048322 | -0.006148 | 0.014572 | -0.0079168 | 0.0059238 | -0.0024182 | -0.014967 | 0.018611 | 0.032043 | 0.10986 | 0.10529 | 0.13733 | 0.14648 | -0.032043 | -0.1831 | 0.041199 | 0.14191 | 0.022888 | 0.050354 | 0.059509 | -0.054932 | -0.11902 | 2.2522 | 2.1011 | -118.84 | 2.3941 | 2.4216 | 0.32043 | -118.9545 | 2.2293 | 2.1652 | -118.9362 | 2.3254 | 2.3071 | 0.14191 | -118.927 | 2.4307 | 2.3163 | 2.3895 | -119.1696 | 2.3346 | 2.3438 | 2.4261 | -119.1055
2877.125 | 121.3165 | -2.0004 | 119.2841 | 0.0066373 | 0.012873 | 0.053263 | 0.0093972 | 0.0021191 | -0.00098684 | -0.0063616 | 0.0069425 | -0.0057806 | 0.008701 | -0.0028454 | -0.015394 | 0.017115 | 0.027466 | 0.091553 | 0.086975 | 0.1236 | 0.1236 | -0.022888 | -0.17395 | 0.009155 | 0.11444 | -0.036621 | 0.064087 | 0.068665 | -0.068665 | -0.14191 | 1.9775 | 1.8265 | -119.1605 | 2.092 | 2.124 | 0.29755 | -119.2566 | 1.9318 | 1.8585 | -119.22 | 2.0096 | 1.9638 | 0.10529 | -119.2154 | 2.124 | 2.0279 | 2.0874 | -119.458 | 2.0645 | 2.0691 | 2.1149 | -119.426
2878.875 | 121.312 | -1.8311 | 119.4672 | 0.0066373 | 0.012659 | 0.052622 | 0.0087564 | 0.0040417 | -0.0014142 | -0.0067888 | -0.00068649 | -0.0036444 | 0.009769 | -0.0013502 | -0.011549 | 0.01797 | -0.027466 | 0.013733 | 0.009155 | 0.07782 | 0.17853 | -0.064087 | -0.2243 | -0.064087 | 0.004578 | -0.13733 | 0.11444 | 0.10071 | -0.10071 | -0.15106 | 1.767 | 1.6068 | -119.2886 | 1.8448 | 1.9089 | 0.30212 | -119.4946 | 1.7303 | 1.68 | -119.3527 | 1.767 | 1.6937 | 0.013733 | -119.3665 | 2.0096 | 1.8036 | 1.8402 | -119.6915 | 1.9455 | 1.9318 | 1.8356 | -119.6182
2880.5625 | 121.3715 | -1.5381 | 119.7784 | -0.00099167 | 0.0133 | 0.055185 | 0.005552 | 0.0044691 | -0.0024822 | -0.0052936 | -0.00068649 | -0.0047124 | 0.0061374 | -0.0039136 | -0.011549 | 0.017329 | 0.032043 | 0.10529 | 0.07782 | 0.12817 | 0.14191 | -0.045776 | -0.1831 | 0.036621 | 0.10986 | -0.032043 | 0.041199 | 0.041199 | -0.054932 | -0.11902 | 1.4923 | 1.355 | -119.6365 | 1.6434 | 1.6663 | 0.31128 | -119.7464 | 1.4832 | 1.4191 | -119.7372 | 1.5747 | 1.506 | 0.086976 | -119.7372 | 1.68 | 1.5701 | 1.6159 | -119.9615 | 1.5793 | 1.5793 | 1.6479 | -119.8975
2882.3125 | 121.3348 | -1.6434 | 119.7601 | 0.014267 | 0.015436 | 0.052195 | 0.00042505 | 0.0012647 | 0.004781 | -0.0059344 | 0.0069425 | -0.0027898 | 0.0057102 | -6.8386e-05 | -0.0074897 | 0.01797 | -0.054932 | -0.064087 | -0.064087 | 0.036621 | 0.19226 | -0.068665 | -0.21057 | -0.059509 | -0.07782 | -0.16937 | 0.068665 | 0.07782 | -0.10986 | -0.16022 | 1.5747 | 1.4328 | -119.5679 | 1.5793 | 1.68 | 0.24719 | -119.8151 | 1.5335 | 1.4832 | -119.6915 | 1.5839 | 1.474 | -0.009156 | -119.6823 | 1.8356 | 1.5884 | 1.5793 | -119.9707 | 1.712 | 1.7212 | 1.5656 | -119.9203
2884.0781 | 121.3669 | -1.6022 | 119.8196 | -0.016251 | 0.012446 | 0.053049 | 0.0049112 | 0.0040417 | 0.00414 | -0.0072162 | 0.0069425 | -0.0017218 | 0.0054966 | -0.0028454 | -0.0072759 | 0.020106 | -0.027466 | -0.018311 | -0.013733 | 0.064087 | 0.16479 | -0.054932 | -0.19684 | 0.004578 | 0.032043 | -0.086975 | 0.064087 | 0.045776 | -0.068665 | -0.13275 | 1.5472 | 1.4053 | -119.6548 | 1.5839 | 1.6663 | 0.26093 | -119.8471 | 1.5335 | 1.4694 | -119.7556 | 1.6068 | 1.5152 | 0.045776 | -119.7739 | 1.767 | 1.5747 | 1.5884 | -120.0165 | 1.6663 | 1.6479 | 1.6342 | -119.9524
2885.7656 | 121.3623 | -1.5884 | 119.8059 | -0.00099167 | 0.013727 | 0.051126 | 0.005552 | 0.0025465 | 0.0022174 | -0.0048662 | -0.00068649 | -0.00086724 | 0.0059238 | -0.0013502 | -0.0087713 | 0.018824 | -0.032043 | -0.032043 | -0.064087 | 0.036621 | 0.17853 | -0.054932 | -0.21057 | -0.027466 | -0.022888 | -0.13275 | 0.07782 | 0.054932 | -0.082397 | -0.14648 | 1.5335 | 1.3779 | -119.6274 | 1.5564 | 1.6251 | 0.24719 | -119.838 | 1.506 | 1.442 | -119.7281 | 1.561 | 1.4557 | 0.013733 | -119.751 | 1.767 | 1.5564 | 1.5244 | -120.0165 | 1.6663 | 1.6434 | 1.5656 | -119.9524
2887.4531 | 121.4584 | -1.5518 | 119.8196 | -0.00099167 | 0.010523 | 0.052835 | 0.0074746 | 0.0031873 | 0.00072196 | -0.0067888 | 0.0069425 | -0.0019354 | 0.0089146 | -0.0037 | -0.011762 | 0.021174 | -0.054932 | -0.050354 | -0.054932 | 0.036621 | 0.18768 | -0.07782 | -0.22888 | -0.068665 | -0.032043 | -0.17395 | 0.082397 | 0.07782 | -0.10529 | -0.16479 | 1.474 | 1.3229 | -119.632 | 1.5015 | 1.5884 | 0.2655 | -119.8746 | 1.4465 | 1.387 | -119.7372 | 1.4832 | 1.3779 | -0.009155 | -119.7418 | 1.7395 | 1.4969 | 1.4969 | -120.0485 | 1.6342 | 1.6296 | 1.5198 | -119.9844
2889.2188 | 121.3531 | -1.5427 | 119.8654 | -0.00099167 | 0.009455 | 0.052622 | 0.0059792 | 0.0019055 | 0.00050836 | -0.003371 | -0.008316 | -0.0044988 | 0.0065646 | -0.0017774 | -0.010908 | 0.021174 | 0.036621 | 0.091553 | 0.082397 | 0.13275 | 0.15106 | -0.022888 | -0.16479 | 0.045776 | 0.082397 | -0.036621 | 0.041199 | 0.036621 | -0.064087 | -0.14648 | 1.5198 | 1.3779 | -119.7144 | 1.6342 | 1.6754 | 0.29755 | -119.8288 | 1.4786 | 1.3962 | -119.8242 | 1.5884 | 1.506 | 0.10986 | -119.8288 | 1.6937 | 1.5793 | 1.6251 | -120.0302 | 1.5839 | 1.5793 | 1.6251 | -120.0119
2890.9062 | 121.3394 | -1.5564 | 119.9066 | -0.00099167 | 0.007746 | 0.054972 | 0.0064066 | -0.00023074 | -0.0031232 | -0.0046526 | 0.0069425 | -0.0040716 | 0.0057102 | -0.0041272 | -0.011121 | 0.020533 | 0.022888 | 0.064087 | 0.054932 | 0.091553 | 0.14191 | -0.004578 | -0.17395 | 0.004578 | 0.032043 | -0.059509 | 0.032043 | 0.032043 | -0.064087 | -0.13275 | 1.5518 | 1.3824 | -119.7647 | 1.6205 | 1.6479 | 0.2655 | -119.8837 | 1.4923 | 1.4236 | -119.8746 | 1.561 | 1.4969 | 0.073242 | -119.8746 | 1.6983 | 1.5793 | 1.6113 | -120.0806 | 1.5884 | 1.5884 | 1.5884 | -120.0394
2892.6562 | 121.463 | -1.5198 | 119.8975 | 0.014267 | 0.012659 | 0.052835 | 0.011961 | 0.0042555 | -0.002055 | -0.0063616 | -0.008316 | -0.0032172 | 0.0061374 | -0.0041272 | -0.012617 | 0.018397 | 0.054932 | 0.11444 | 0.09613 | 0.13275 | 0.14191 | -0.054932 | -0.1831 | 0.027466 | 0.11444 | 0 | 0.045776 | 0.032043 | -0.059509 | -0.1236 | 1.4648 | 1.3367 | -119.7556 | 1.6342 | 1.6525 | 0.31586 | -119.8425 | 1.4603 | 1.3962 | -119.8517 | 1.5472 | 1.5198 | 0.1236 | -119.8654 | 1.6617 | 1.5747 | 1.6159 | -120.0806 | 1.5656 | 1.5518 | 1.6342 | -120.0211
2894.4062 | 121.376 | -1.5335 | 119.9341 | 0.0066373 | 0.0081732 | 0.056253 | 0.0066202 | 0.0031873 | -0.0056866 | -0.0057208 | 0.0069425 | -0.0051398 | 0.0057102 | -0.0024182 | -0.010908 | 0.019252 | 0.009155 | 0.027466 | 0.036621 | 0.082397 | 0.12817 | -0.032043 | -0.17395 | -0.004578 | 0.018311 | -0.054932 | 0.054932 | 0.054932 | -0.082397 | -0.13275 | 1.5015 | 1.3596 | -119.8059 | 1.561 | 1.6159 | 0.25635 | -119.9249 | 1.4511 | 1.4008 | -119.8792 | 1.5289 | 1.4786 | 0.077819 | -119.8792 | 1.6617 | 1.5427 | 1.5701 | -120.108 | 1.5884 | 1.5884 | 1.5518 | -120.0668
2896.0938 | 121.3898 | -1.387 | 120.1263 | 0.0066373 | 0.013514 | 0.050699 | 0.0029886 | 0.0044691 | 0.005849 | -0.0040118 | -0.00068649 | -0.00022644 | 0.006351 | -0.00092279 | -0.0079169 | 0.017543 | -0.041199 | -0.086975 | -0.064087 | 0.027466 | 0.17853 | -0.07782 | -0.21057 | -0.054932 | -0.09613 | -0.18768 | 0.09613 | 0.082397 | -0.086975 | -0.15564 | 1.3092 | 1.1765 | -119.9478 | 1.3 | 1.4145 | 0.23804 | -120.1675 | 1.3 | 1.2314 | -120.0302 | 1.3321 | 1.1993 | -0.032043 | -120.0439 | 1.5656 | 1.3458 | 1.3229 | -120.3369 | 1.4832 | 1.4694 | 1.2909 | -120.282
2897.8438 | 121.4676 | -1.4282 | 120.0073 | -0.00099167 | 0.015864 | 0.054331 | 0.010679 | 0.0025465 | 0.00029476 | -0.0063616 | 0.0069425 | -0.0036444 | 0.00806 | -0.0026318 | -0.010053 | 0.020106 | -0.013733 | 0.013733 | 0.004578 | 0.068665 | 0.16937 | -0.059509 | -0.20599 | -0.073242 | -0.013733 | -0.14191 | 0.082397 | 0.07782 | -0.11444 | -0.16022 | 1.3687 | 1.2222 | -119.838 | 1.442 | 1.4969 | 0.27466 | -120.0211 | 1.3138 | 1.268 | -119.9249 | 1.355 | 1.2863 | 0.01831 | -119.9295 | 1.5976 | 1.4145 | 1.4328 | -120.2133 | 1.5106 | 1.506 | 1.4145 | -120.1675
2899.6094 | 121.3943 | -1.4694 | 120.0531 | -0.00099167 | 0.016077 | 0.052622 | 0.003843 | 0.0053235 | 0.005849 | -0.0035846 | 0.0069425 | 0.00041436 | 0.0067782 | -0.00092279 | -0.0079169 | 0.018184 | -0.009155 | -0.041199 | -0.050354 | 0.036621 | 0.19226 | -0.059509 | -0.19684 | -0.064087 | -0.059509 | -0.19226 | 0.10529 | 0.068665 | -0.10529 | -0.15106 | 1.4099 | 1.2726 | -119.8608 | 1.4282 | 1.506 | 0.23346 | -120.0623 | 1.3641 | 1.3184 | -119.9478 | 1.4053 | 1.2772 | -0.041199 | -119.9844 | 1.6617 | 1.4603 | 1.4191 | -120.2499 | 1.5747 | 1.5381 | 1.4099 | -120.2042
2901.2969 | 121.4035 | -1.4603 | 120.0211 | 0.014267 | 0.015864 | 0.051981 | 0.0057656 | 0.0025465 | 0.0049946 | -0.0035846 | 0.0069425 | -0.00022644 | 0.0084872 | -0.00070919 | -0.0087713 | 0.019252 | -0.004578 | -0.018311 | -0.032043 | 0.073242 | 0.16022 | -0.068665 | -0.21057 | -0.059509 | -0.041199 | -0.16479 | 0.07782 | 0.07782 | -0.086975 | -0.14648 | 1.3916 | 1.2497 | -119.8608 | 1.442 | 1.5335 | 0.28381 | -120.0256 | 1.3733 | 1.3138 | -119.9432 | 1.4008 | 1.2955 | -0.018311 | -119.9432 | 1.6205 | 1.4557 | 1.4282 | -120.2316 | 1.5381 | 1.5381 | 1.4191 | -120.1675
2903.0469 | 121.0098 | -31.4163 | 89.566 | -0.00099167 | 0.013514 | 0.052622 | 0.0091836 | 0.0040417 | -0.00098684 | -0.0048662 | -0.008316 | -0.003858 | 0.0095554 | -0.0024182 | -0.013471 | 0.020747 | -0.068665 | -0.018311 | -0.041199 | 0.054932 | 0.19684 | -0.064087 | -0.20142 | -0.073242 | -0.004578 | -0.12817 | 0.086975 | 0.086975 | -0.10071 | -0.15564 | 31.3522 | 31.2149 | -89.3692 | 31.398 | 31.4713 | 0.25635 | -89.6347 | 31.3156 | 31.2607 | -89.4791 | 31.3431 | 31.2881 | 0.027466 | -89.4791 | 31.6132 | 31.3477 | 31.3751 | -89.7675 | 31.5033 | 31.5033 | 31.4117 | -89.7217
2904.7344 | 120.5566 | -13.2843 | 107.8857 | 0.0066373 | 0.009455 | 0.051554 | 0.0034158 | 0.0023327 | 0.0020038 | -0.0037982 | 0.0069425 | -0.0051398 | 0.0082736 | -0.0013502 | -0.01048 | 0.019252 | 0.022888 | 0.041199 | 0.045776 | 0.10529 | 0.15564 | -0.036621 | -0.19226 | 0.027466 | 0.068665 | -0.032043 | 0.050354 | 0.054932 | -0.059509 | -0.1236 | 13.2477 | 13.092 | -107.7301 | 13.3255 | 13.3896 | 0.29755 | -107.8629 | 13.2248 | 13.1607 | -107.8354 | 13.3118 | 13.2523 | 0.091553 | -107.8308 | 13.4399 | 13.3072 | 13.3301 | -108.078 | 13.3347 | 13.3392 | 13.353 | -108.0093
2906.4844 | 120.9366 | -11.5311 | 109.6985 | 0.0066373 | 0.012018 | 0.055613 | 0.0046976 | 0.0023327 | 0.00414 | -0.0037982 | 0.0069425 | -0.0015082 | 0.002933 | -0.001991 | -0.0085577 | 0.019893 | -0.036621 | -0.041199 | -0.059509 | 0.059509 | 0.19226 | -0.073242 | -0.19684 | -0.064087 | -0.045776 | -0.13733 | 0.086975 | 0.07782 | -0.086975 | -0.14648 | 11.4578 | 11.3342 | -109.5062 | 11.4899 | 11.5906 | 0.25635 | -109.7351 | 11.4441 | 11.3846 | -109.6115 | 11.467 | 11.3937 | 0.009155 | -109.6207 | 11.7233 | 11.4944 | 11.4716 | -109.8953 | 11.618 | 11.6089 | 11.4853 | -109.845
2908.1719 | 121.2112 | -10.8582 | 110.376 | -0.00099167 | 0.015864 | 0.053904 | 0.0079018 | 0.0029737 | 0.0022174 | -0.0025164 | 0.0069425 | -0.0015082 | 0.0074192 | -0.00070919 | -0.0091985 | 0.019465 | 0.027466 | 0.027466 | 0 | 0.10071 | 0.16937 | -0.050354 | -0.20599 | -0.027466 | 0 | -0.14648 | 0.068665 | 0.073242 | -0.086975 | -0.14648 | 10.8078 | 10.6522 | -110.2066 | 10.8856 | 10.9589 | 0.3067 | -110.3485 | 10.7712 | 10.7117 | -110.3073 | 10.8307 | 10.7117 | 0 | -110.3027 | 11.0275 | 10.8856 | 10.8582 | -110.582 | 10.9268 | 10.9314 | 10.8582 | -110.5225
2909.9375 | 121.2021 | -10.2722 | 111.0214 | -0.00099167 | 0.015223 | 0.050058 | 0.0068338 | 0.0014783 | 0.0039264 | -0.001662 | 0.022202 | -0.0019354 | 0.0067782 | -0.0013502 | -0.0098395 | 0.020533 | -0.050354 | -0.036621 | -0.041199 | 0.050354 | 0.1831 | -0.059509 | -0.21057 | -0.086975 | -0.054932 | -0.17853 | 0.07782 | 0.086975 | -0.082397 | -0.16937 | 10.2127 | 10.0616 | -110.8383 | 10.2356 | 10.3226 | 0.26093 | -111.0718 | 10.1898 | 10.1028 | -110.9436 | 10.1852 | 10.0937 | -0.009155 | -110.9344 | 10.4553 | 10.2219 | 10.231 | -111.232 | 10.35 | 10.3592 | 10.2173 | -111.1908
2911.7031 | 121.1655 | -10.1395 | 111.145 | -0.00099167 | 0.013941 | 0.052835 | 0.0066202 | 0.0025465 | 0.0011494 | -0.0052936 | 0.014572 | -0.00044004 | 0.0057102 | 0.00035881 | -0.011121 | 0.021601 | -0.054932 | -0.050354 | -0.059509 | 0.050354 | 0.18768 | -0.064087 | -0.20599 | -0.064087 | -0.050354 | -0.14191 | 0.07782 | 0.086975 | -0.082397 | -0.14648 | 10.0754 | 9.9335 | -110.9573 | 10.0891 | 10.1898 | 0.25635 | -111.2 | 10.0571 | 9.993 | -111.0672 | 10.0754 | 9.9976 | 0.004577 | -111.058 | 10.3271 | 10.0845 | 10.08 | -111.351 | 10.2173 | 10.2264 | 10.0891 | -111.2915
2913.4531 | 121.344 | -9.0591 | 112.175 | 0.0066373 | 0.011164 | 0.055826 | 0.010679 | 0.0048963 | -0.008891 | -0.0048662 | 0.0069425 | -0.0062078 | 0.0065646 | -0.0024182 | -0.012617 | 0.020106 | 0.045776 | 0.10986 | 0.10986 | 0.13275 | 0.14648 | -0.036621 | -0.15564 | 0.018311 | 0.1236 | 0 | 0.054932 | 0.041199 | -0.045776 | -0.13275 | 9.0225 | 8.9035 | -112.0285 | 9.169 | 9.1919 | 0.28839 | -112.1292 | 9.0134 | 8.9264 | -112.1201 | 9.0775 | 9.0591 | 0.13275 | -112.1338 | 9.2056 | 9.1049 | 9.169 | -112.3306 | 9.1141 | 9.1003 | 9.1827 | -112.3077
2915.1562 | 121.2524 | -6.4499 | 114.9307 | -0.00099167 | 0.0133 | 0.05134 | 0.0046976 | 0.0031873 | 0.0056354 | -0.0040118 | -0.00068649 | -0.00065364 | 0.0044284 | -6.8386e-05 | -0.0083441 | 0.019679 | -0.041199 | -0.073242 | -0.068665 | 0.045776 | 0.18768 | -0.050354 | -0.20599 | -0.086975 | -0.07782 | -0.18768 | 0.086975 | 0.086975 | -0.086975 | -0.16479 | 6.3995 | 6.2439 | -114.743 | 6.3766 | 6.4957 | 0.25177 | -114.9719 | 6.3629 | 6.2851 | -114.8438 | 6.3629 | 6.2622 | -0.022888 | -114.8438 | 6.6376 | 6.4087 | 6.3812 | -115.1367 | 6.5369 | 6.5369 | 6.3721 | -115.0955
2916.9062 | 121.3623 | -5.5801 | 115.7455 | -0.0086212 | 0.015009 | 0.054117 | 0.010038 | 0.0034009 | -0.00098684 | -0.0046526 | -0.00068649 | -0.0040716 | 0.0076328 | -0.0017774 | -0.013044 | 0.020533 | -0.073242 | -0.032043 | -0.036621 | 0.045776 | 0.18768 | -0.064087 | -0.23346 | -0.10986 | -0.022888 | -0.13733 | 0.091553 | 0.086975 | -0.10986 | -0.16022 | 5.5161 | 5.3467 | -115.5579 | 5.5481 | 5.6259 | 0.27924 | -115.8188 | 5.4703 | 5.4199 | -115.654 | 5.4703 | 5.4428 | 0.022888 | -115.6586 | 5.7678 | 5.5069 | 5.5435 | -115.979 | 5.6717 | 5.6671 | 5.5573 | -115.9058
2918.6719 | 121.4355 | -5.2643 | 116.0522 | -0.00099167 | 0.012873 | 0.050913 | 0.0081154 | 0.0023327 | 0.0020038 | -0.0042254 | 0.0069425 | -0.0023626 | 0.0078464 | -0.001991 | -0.0098395 | 0.018184 | -0.013733 | -0.004578 | -0.013733 | 0.091553 | 0.16937 | -0.059509 | -0.20142 | -0.032043 | 0.004578 | -0.12817 | 0.091553 | 0.073242 | -0.11444 | -0.15564 | 5.2048 | 5.0629 | -115.8829 | 5.2597 | 5.3558 | 0.29297 | -116.066 | 5.1498 | 5.1086 | -115.9607 | 5.2322 | 5.1361 | 0.027466 | -115.979 | 5.4337 | 5.2505 | 5.2505 | -116.2537 | 5.3558 | 5.3375 | 5.2689 | -116.2079
2920.375 | 121.4355 | -5.3467 | 115.9882 | -0.00099167 | 0.01095 | 0.053904 | 0.0081154 | 0.0023327 | -0.0050458 | -0.0070026 | 0.0069425 | -0.0057806 | 0.006351 | -0.0015638 | -0.01518 | 0.02032 | -0.004578 | 0.073242 | 0.07782 | 0.10986 | 0.14648 | -0.018311 | -0.18768 | 0.018311 | 0.10529 | -0.013733 | 0.054932 | 0.036621 | -0.054932 | -0.1236 | 5.3284 | 5.159 | -115.8417 | 5.4199 | 5.4565 | 0.29755 | -115.9927 | 5.2917 | 5.2231 | -115.9332 | 5.365 | 5.3329 | 0.10986 | -115.9515 | 5.4932 | 5.3421 | 5.4245 | -116.1758 | 5.4016 | 5.3833 | 5.452 | -116.1118
2922.125 | 121.3303 | -5.0674 | 116.3452 | -0.0086212 | 0.012232 | 0.052622 | 0.005552 | 0.0029737 | -0.00055964 | -0.0040118 | 0.0069425 | -0.0019354 | 0.003574 | -0.0041272 | -0.011121 | 0.019252 | 0.064087 | 0.07782 | 0.09613 | 0.12817 | 0.13275 | -0.009155 | -0.15106 | 0.004578 | 0.068665 | -0.032043 | 0.041199 | 0.045776 | -0.050354 | -0.11444 | 5.0583 | 4.9164 | -116.2125 | 5.1453 | 5.1956 | 0.27924 | -116.2811 | 5.0171 | 4.953 | -116.304 | 5.072 | 5.0354 | 0.082398 | -116.2994 | 5.2002 | 5.1315 | 5.1636 | -116.4963 | 5.1086 | 5.1132 | 5.1361 | -116.4597
2923.875 | 121.4401 | -5.3467 | 116.0889 | 0.0066373 | 0.013941 | 0.051126 | 0.0079018 | 0.0042555 | 0.001363 | -0.0063616 | 0.0069425 | -0.0034308 | 0.0067782 | -0.001991 | -0.011762 | 0.018611 | -0.050354 | -0.018311 | -0.022888 | 0.045776 | 0.19226 | -0.07782 | -0.2243 | -0.086975 | -0.027466 | -0.15106 | 0.10071 | 0.10529 | -0.11444 | -0.16937 | 5.2689 | 5.1224 | -115.8966 | 5.3284 | 5.3925 | 0.27008 | -116.1392 | 5.2322 | 5.1773 | -115.9882 | 5.2597 | 5.1956 | 0.018311 | -115.9836 | 5.5389 | 5.2963 | 5.3238 | -116.3132 | 5.4474 | 5.452 | 5.3192 | -116.2582
2925.625 | 121.431 | -5.6763 | 115.7043 | -0.00099167 | 0.01095 | 0.05369 | 0.0059792 | 0.0019055 | -0.00098684 | -0.0076434 | 0.014572 | -0.0036444 | 0.0067782 | -0.0043408 | -0.011549 | 0.01797 | 0.018311 | 0.07782 | 0.050354 | 0.11444 | 0.13275 | -0.041199 | -0.19684 | -0.041199 | 0.027466 | -0.10529 | 0.068665 | 0.082397 | -0.07782 | -0.14648 | 5.6351 | 5.4794 | -115.5716 | 5.7541 | 5.7907 | 0.31128 | -115.686 | 5.5984 | 5.5298 | -115.6357 | 5.6351 | 5.571 | 0.041198 | -115.6219 | 5.809 | 5.6946 | 5.7266 | -115.9012 | 5.7449 | 5.7587 | 5.7037 | -115.8508
2927.3125 | 121.4905 | -5.9967 | 115.3976 | -0.00099167 | 0.015864 | 0.05369 | 0.0061928 | 0.0010511 | 0.0028584 | -0.0076434 | -0.00068649 | -0.0036444 | 0.0089146 | -0.0013502 | -0.011121 | 0.018397 | -0.036621 | -0.041199 | -0.059509 | 0.050354 | 0.19226 | -0.068665 | -0.19684 | -0.082397 | -0.050354 | -0.16479 | 0.09613 | 0.10529 | -0.09613 | -0.17853 | 5.928 | 5.7999 | -115.2054 | 5.9555 | 6.0471 | 0.24719 | -115.4343 | 5.9006 | 5.8182 | -115.3015 | 5.9143 | 5.8319 | 0.013733 | -115.2924 | 6.189 | 5.9601 | 5.9372 | -115.5945 | 6.0928 | 6.102 | 5.9464 | -115.5762
2929.0625 | 121.4951 | -5.9326 | 115.4755 | -0.0086212 | 0.016291 | 0.05134 | 0.01132 | 0.0012647 | -0.00013244 | -0.0052936 | 0.0069425 | -0.0030034 | 0.0078464 | -0.0017774 | -0.011976 | 0.019679 | -0.054932 | -0.036621 | -0.064087 | 0.054932 | 0.19684 | -0.07782 | -0.23804 | -0.091553 | -0.045776 | -0.15564 | 0.09613 | 0.09613 | -0.10529 | -0.16479 | 5.8548 | 5.6946 | -115.2786 | 5.896 | 5.9875 | 0.29297 | -115.5304 | 5.8273 | 5.7678 | -115.3793 | 5.8411 | 5.777 | 0.009155 | -115.3793 | 6.1295 | 5.8777 | 5.8685 | -115.7135 | 6.0287 | 6.0287 | 5.8868 | -115.6403
2930.75 | 121.4355 | -5.5344 | 115.947 | 0.0066373 | 0.012232 | 0.054117 | 0.002775 | 0.0038281 | 0.00414 | -0.0040118 | -0.00068649 | -0.0019354 | 0.004642 | 0.0012134 | -0.0087713 | 0.019465 | -0.045776 | -0.054932 | -0.059509 | 0.054932 | 0.21057 | -0.07782 | -0.21057 | -0.064087 | -0.073242 | -0.16479 | 0.086975 | 0.09613 | -0.091553 | -0.15564 | 5.4565 | 5.3238 | -115.7364 | 5.4794 | 5.5893 | 0.2655 | -115.9927 | 5.4428 | 5.3787 | -115.86 | 5.4703 | 5.3696 | -0.009155 | -115.8508 | 5.7449 | 5.4886 | 5.4749 | -116.1575 | 5.6213 | 5.6305 | 5.4611 | -116.1026
2932.5 | 121.4127 | -5.3192 | 116.185 | -0.00099167 | 0.010309 | 0.05369 | 0.0042702 | 0.0025465 | -0.00055964 | -0.0042254 | 0.022202 | -0.003858 | 0.0076328 | -0.0037 | -0.0098395 | 0.021174 | 0.050354 | 0.10529 | 0.091553 | 0.11902 | 0.14191 | -0.022888 | -0.15564 | 0.036621 | 0.082397 | -0.018311 | 0.041199 | 0.032043 | -0.068665 | -0.12817 | 5.2963 | 5.1636 | -116.0431 | 5.4245 | 5.4382 | 0.27466 | -116.1346 | 5.2505 | 5.191 | -116.1438 | 5.3558 | 5.3009 | 0.10986 | -116.153 | 5.4611 | 5.3696 | 5.4108 | -116.3406 | 5.3604 | 5.3513 | 5.4016 | -116.3132
2934.2656 | 121.4905 | -4.9576 | 116.4642 | 0.0066373 | 0.013727 | 0.054544 | 0.0068338 | 0.0044691 | -0.0018414 | -0.0052936 | 0.0069425 | -0.005567 | 0.0050694 | -0.0028454 | -0.010267 | 0.020106 | 0.045776 | 0.091553 | 0.086975 | 0.12817 | 0.14648 | -0.027466 | -0.18768 | -0.004578 | 0.10071 | -0.036621 | 0.032043 | 0.050354 | -0.059509 | -0.13733 | 4.9301 | 4.7699 | -116.3177 | 5.0491 | 5.0858 | 0.31586 | -116.4185 | 4.8981 | 4.8203 | -116.4322 | 4.953 | 4.921 | 0.10071 | -116.4139 | 5.1041 | 5.0034 | 5.0446 | -116.6519 | 4.9896 | 5.0079 | 5.0583 | -116.6016
2935.9688 | 121.4951 | -4.8981 | 116.597 | -0.00099167 | 0.012446 | 0.05134 | 0.0093972 | 0.0021191 | 0.00093576 | -0.0055072 | 0.0069425 | -0.0032172 | 0.0074192 | -0.0026318 | -0.011549 | 0.020961 | 0.013733 | 0.036621 | 0.041199 | 0.10986 | 0.16937 | -0.045776 | -0.18768 | -0.054932 | 0.004578 | -0.1236 | 0.086975 | 0.073242 | -0.082397 | -0.15564 | 4.8523 | 4.7104 | -116.4276 | 4.9347 | 5.0079 | 0.29755 | -116.5833 | 4.8157 | 4.7424 | -116.51 | 4.8431 | 4.7745 | 0.032044 | -116.5237 | 5.0674 | 4.9118 | 4.9393 | -116.7847 | 4.985 | 4.9713 | 4.9026 | -116.7526
2937.6719 | 121.4676 | -4.7562 | 116.748 | 0.014267 | 0.010523 | 0.053049 | 0.007261 | 0.0023327 | 0.0043536 | -0.004439 | 0.0069425 | -0.0017218 | 0.0076328 | -0.0011364 | -0.0091985 | 0.017756 | -0.022888 | -0.027466 | -0.032043 | 0.036621 | 0.18768 | -0.059509 | -0.18768 | -0.009155 | -0.036621 | -0.10986 | 0.073242 | 0.064087 | -0.082397 | -0.13733 | 4.6967 | 4.5685 | -116.5604 | 4.7287 | 4.7928 | 0.2243 | -116.7709 | 4.6738 | 4.6188 | -116.6748 | 4.747 | 4.6463 | 0.027466 | -116.684 | 4.9438 | 4.7333 | 4.7241 | -116.9357 | 4.8294 | 4.8203 | 4.7195 | -116.8854
2939.4375 | 121.5637 | -4.6005 | 116.8671 | 0.021896 | 0.012659 | 0.053263 | 0.005552 | 0.0051099 | 0.00414 | -0.0031574 | -0.00068649 | -0.00022644 | 0.0044284 | -0.003059 | -0.0087713 | 0.017543 | -0.018311 | 0 | -0.022888 | 0.091553 | 0.1831 | -0.064087 | -0.19684 | -0.032043 | 0.018311 | -0.14648 | 0.07782 | 0.082397 | -0.082397 | -0.16479 | 4.5364 | 4.4037 | -116.684 | 4.6005 | 4.6921 | 0.28839 | -116.8854 | 4.5181 | 4.4357 | -116.7892 | 4.5685 | 4.454 | 0.018311 | -116.7847 | 4.7836 | 4.5822 | 4.5776 | -117.0639 | 4.6783 | 4.6829 | 4.6188 | -117.0319
2941.1406 | 121.4447 | -4.4998 | 117.041 | 0.014267 | 0.015223 | 0.051767 | 0.0051248 | 0.0040417 | 0.0052082 | -0.0042254 | 0.0069425 | -0.00086724 | 0.0061374 | -0.001991 | -0.0070623 | 0.019038 | -0.050354 | -0.064087 | -0.064087 | 0.041199 | 0.17395 | -0.054932 | -0.21973 | -0.082397 | -0.086975 | -0.19684 | 0.07782 | 0.073242 | -0.10529 | -0.17395 | 4.4449 | 4.2801 | -116.8671 | 4.4357 | 4.541 | 0.26093 | -117.0914 | 4.3945 | 4.3259 | -116.9632 | 4.4174 | 4.303 | -0.022888 | -116.9678 | 4.6738 | 4.4495 | 4.4357 | -117.2607 | 4.5776 | 4.5731 | 4.4128 | -117.215
2942.8906 | 121.5408 | -4.1519 | 117.3294 | -0.00099167 | 0.012446 | 0.05369 | 0.0093972 | 0.0042555 | -0.0018414 | -0.0055072 | 0.0069425 | -0.005567 | 0.0082736 | -0.0024182 | -0.013471 | 0.020961 | -0.059509 | -0.027466 | -0.036621 | 0.036621 | 0.17395 | -0.07782 | -0.21057 | -0.091553 | -0.018311 | -0.14648 | 0.086975 | 0.086975 | -0.10986 | -0.15564 | 4.0741 | 3.9413 | -117.1555 | 4.1245 | 4.1885 | 0.24719 | -117.3889 | 4.0421 | 3.9963 | -117.2424 | 4.0604 | 4.0054 | 0.009156 | -117.2424 | 4.3259 | 4.0924 | 4.1153 | -117.54 | 4.2389 | 4.2389 | 4.1336 | -117.485
2944.5781 | 121.4539 | -4.8981 | 116.6382 | 0.021896 | 0.016718 | 0.050913 | 0.005552 | 0.0034009 | 0.0028584 | -0.0052936 | 0.0069425 | -0.0010808 | 0.008701 | -0.0026318 | -0.0098395 | 0.019038 | -0.013733 | -0.013733 | -0.022888 | 0.050354 | 0.17853 | -0.036621 | -0.19684 | -0.064087 | -0.045776 | -0.17853 | 0.086975 | 0.064087 | -0.10529 | -0.14648 | 4.8614 | 4.7012 | -116.4597 | 4.8843 | 4.9484 | 0.24719 | -116.6519 | 4.7928 | 4.7516 | -116.5512 | 4.834 | 4.7195 | -0.032044 | -116.5741 | 5.0766 | 4.8843 | 4.8752 | -116.835 | 4.985 | 4.9622 | 4.8523 | -116.7847
2946.3281 | 121.463 | -3.7765 | 117.8009 | -0.00099167 | 0.013727 | 0.053049 | 0.0044838 | 0.0019055 | 0.002431 | -0.0023028 | 0.0069425 | -0.00022644 | 0.0089146 | -0.0011364 | -0.0068487 | 0.02032 | -0.013733 | -0.009155 | -0.027466 | 0.050354 | 0.18768 | -0.045776 | -0.20142 | -0.059509 | -0.041199 | -0.17395 | 0.091553 | 0.09613 | -0.09613 | -0.16022 | 3.7308 | 3.5751 | -117.6132 | 3.7674 | 3.8269 | 0.25177 | -117.8146 | 3.6804 | 3.6163 | -117.7094 | 3.717 | 3.6026 | -0.013733 | -117.7048 | 3.9642 | 3.7628 | 3.7491 | -118.0023 | 3.8681 | 3.8727 | 3.7354 | -117.9611
2948.0156 | 121.5088 | -2.9022 | 118.6707 | -0.00099167 | 0.013514 | 0.052408 | 0.0057656 | 0.0031873 | 8.1158e-05 | -0.0035846 | -0.008316 | -0.0059942 | 0.005283 | -0.0041272 | -0.0091985 | 0.018397 | 0.004578 | 0.050354 | 0.059509 | 0.10529 | 0.15106 | -0.036621 | -0.17853 | 0.022888 | 0.073242 | -0.027466 | 0.041199 | 0.036621 | -0.041199 | -0.086975 | 2.8656 | 2.7237 | -118.5196 | 2.9526 | 3.0075 | 0.28381 | -118.6661 | 2.861 | 2.8152 | -118.6295 | 2.9251 | 2.8748 | 0.059509 | -118.634 | 3.0533 | 2.9068 | 2.9617 | -118.8492 | 2.9434 | 2.9388 | 2.9755 | -118.7576
2949.7812 | 121.5958 | -2.4445 | 119.0826 | 0.014267 | 0.014582 | 0.050272 | 0.007261 | 0.0040417 | -0.0022686 | -0.0057208 | -0.00068649 | -0.003858 | 0.0059238 | -0.0015638 | -0.01283 | 0.020533 | -0.064087 | -0.041199 | -0.059509 | 0.036621 | 0.18768 | -0.082397 | -0.20599 | -0.10529 | -0.032043 | -0.14191 | 0.11902 | 0.068665 | -0.10529 | -0.16022 | 2.3621 | 2.2385 | -118.895 | 2.4033 | 2.4811 | 0.24262 | -119.1467 | 2.3392 | 2.2842 | -118.9636 | 2.3392 | 2.3026 | 0.01831 | -119.014 | 2.6321 | 2.3804 | 2.3849 | -119.2886 | 2.5635 | 2.5131 | 2.4124 | -119.2429
2951.5312 | 121.4859 | -2.3758 | 119.2383 | -0.00099167 | 0.0088142 | 0.054331 | 0.0057656 | 0.0021191 | -0.006541 | -0.0063616 | 0.0069425 | -0.0053534 | 0.006351 | -0.0028454 | -0.011762 | 0.02267 | -0.032043 | 0.036621 | 0.032043 | 0.091553 | 0.14191 | -0.036621 | -0.1831 | -0.032043 | 0.018311 | -0.064087 | 0.059509 | 0.045776 | -0.07782 | -0.10529 | 2.3392 | 2.1927 | -119.0964 | 2.4124 | 2.4673 | 0.27466 | -119.2703 | 2.298 | 2.2705 | -119.1788 | 2.3438 | 2.3117 | 0.041199 | -119.1925 | 2.5177 | 2.3438 | 2.4078 | -119.4214 | 2.4353 | 2.4216 | 2.3941 | -119.3436
2953.2812 | 121.5408 | -2.2751 | 119.3161 | 0.0066373 | 0.012659 | 0.053049 | 0.003843 | 0.0012647 | 0.003072 | -0.0059344 | -0.008316 | -0.0019354 | 0.0044284 | -0.0017774 | -0.0072759 | 0.019038 | -0.022888 | -0.045776 | -0.054932 | 0.045776 | 0.19226 | -0.054932 | -0.2243 | -0.041199 | -0.054932 | -0.1236 | 0.086975 | 0.064087 | -0.09613 | -0.14648 | 2.2202 | 2.0508 | -119.1238 | 2.2293 | 2.3209 | 0.27008 | -119.339 | 2.179 | 2.1286 | -119.2291 | 2.2339 | 2.1515 | 0.022888 | -119.252 | 2.4673 | 2.2522 | 2.2202 | -119.5404 | 2.3621 | 2.3392 | 2.2202 | -119.4626
2954.9844 | 121.5683 | -2.2842 | 119.2932 | -0.00099167 | 0.012232 | 0.054331 | 0.0079018 | 0.0025465 | -0.00055964 | -0.00508 | -0.00068649 | -0.0042852 | 0.0061374 | -0.0034864 | -0.012617 | 0.020747 | 0.004578 | 0.041199 | 0.027466 | 0.10071 | 0.17853 | -0.054932 | -0.20142 | -0.07782 | 0 | -0.11444 | 0.086975 | 0.091553 | -0.11902 | -0.14191 | 2.2293 | 2.0828 | -119.1147 | 2.3254 | 2.3849 | 0.30212 | -119.2886 | 2.1652 | 2.1423 | -119.2062 | 2.2064 | 2.1698 | 0.027466 | -119.2017 | 2.4628 | 2.2888 | 2.3117 | -119.4946 | 2.3712 | 2.3758 | 2.2842 | -119.4351
2956.6719 | 121.6324 | -2.1744 | 119.3481 | -0.00099167 | 0.015009 | 0.053263 | 0.013242 | 0.0042555 | 8.1158e-05 | -0.0065752 | -0.00068649 | -0.0034308 | 0.0067782 | -0.0011364 | -0.011549 | 0.01797 | -0.050354 | -0.050354 | -0.064087 | 0.032043 | 0.21057 | -0.059509 | -0.21515 | -0.082397 | -0.036621 | -0.15106 | 0.09613 | 0.086975 | -0.10529 | -0.15564 | 2.1149 | 1.9592 | -119.1376 | 2.124 | 2.2064 | 0.24719 | -119.3985 | 2.0691 | 2.0187 | -119.252 | 2.092 | 2.0233 | 0.004578 | -119.2612 | 2.3849 | 2.124 | 2.1103 | -119.5633 | 2.2705 | 2.2614 | 2.1378 | -119.5038
2958.4219 | 121.5591 | -2.1561 | 119.458 | 0.0066373 | 0.012232 | 0.049845 | 0.005552 | 0.00062386 | 0.0020038 | -0.0042254 | 0.0069425 | -0.002149 | 0.0067782 | -0.0017774 | -0.0094123 | 0.018184 | -0.036621 | -0.050354 | -0.064087 | 0.027466 | 0.19226 | -0.059509 | -0.20599 | -0.045776 | -0.059509 | -0.14191 | 0.091553 | 0.07782 | -0.091553 | -0.14648 | 2.0966 | 1.9501 | -119.2657 | 2.1057 | 2.1835 | 0.23346 | -119.4946 | 2.0645 | 2.0096 | -119.3665 | 2.1103 | 2.0142 | 0.004577 | -119.3802 | 2.3483 | 2.1194 | 2.092 | -119.664 | 2.2476 | 2.2339 | 2.0966 | -119.6045
2960.1875 | 121.6553 | -2.1652 | 119.4077 | 0.0066373 | 0.013727 | 0.053049 | 0.0076882 | 0.0034009 | 0.00072196 | -0.00508 | 0.0069425 | -0.0012946 | 0.006992 | 0.00057261 | -0.0083441 | 0.019252 | -0.009155 | -0.013733 | -0.041199 | 0.07782 | 0.19226 | -0.059509 | -0.21057 | -0.045776 | 0.009155 | -0.12817 | 0.068665 | 0.054932 | -0.082397 | -0.16479 | 2.1057 | 1.9547 | -119.2154 | 2.1515 | 2.243 | 0.28839 | -119.4168 | 2.0828 | 2.0004 | -119.339 | 2.1194 | 2.037 | 0.036621 | -119.3527 | 2.3575 | 2.1561 | 2.124 | -119.6182 | 2.2339 | 2.2202 | 2.1744 | -119.5724
2961.9375 | 121.5179 | -2.2064 | 119.4031 | -0.00099167 | 0.012232 | 0.053263 | 0.0051248 | 0.0057507 | 0.00050836 | -0.0057208 | -0.00068649 | -0.0027898 | 0.0050694 | -0.003059 | -0.011335 | 0.020106 | 0.036621 | 0.086975 | 0.082397 | 0.13275 | 0.12817 | -0.013733 | -0.16479 | 0.045776 | 0.086975 | -0.022888 | 0.041199 | 0.045776 | -0.068665 | -0.1236 | 2.1927 | 2.0416 | -119.2749 | 2.2934 | 2.3392 | 0.29755 | -119.3665 | 2.1378 | 2.0828 | -119.3619 | 2.2522 | 2.1835 | 0.10071 | -119.3573 | 2.3346 | 2.243 | 2.2888 | -119.5679 | 2.2476 | 2.2522 | 2.2934 | -119.5267
2963.6875 | 121.5958 | -2.0828 | 119.4946 | -0.00099167 | 0.013727 | 0.055826 | 0.01132 | 0.0027601 | -0.00013244 | -0.00508 | -0.008316 | -0.0032172 | 0.00806 | -0.0022046 | -0.013685 | 0.019893 | -0.059509 | -0.041199 | -0.022888 | 0.050354 | 0.19226 | -0.064087 | -0.21973 | -0.091553 | -0.027466 | -0.15106 | 0.10529 | 0.082397 | -0.11444 | -0.15106 | 2.0187 | 1.8631 | -119.3024 | 2.0416 | 2.1332 | 0.27008 | -119.5541 | 1.9684 | 1.9318 | -119.3893 | 1.9913 | 1.9318 | 0 | -119.4122 | 2.2751 | 2.0233 | 2.0599 | -119.7144 | 2.1881 | 2.1652 | 2.0554 | -119.6457
2965.3906 | 121.55 | -2.0599 | 119.5724 | 0.0066373 | 0.010523 | 0.050486 | 0.0076882 | 0.0031873 | 0.00029476 | -0.0035846 | 0.0069425 | -0.0034308 | 0.0076328 | -0.0017774 | -0.0096259 | 0.020533 | 0.050354 | 0.09613 | 0.091553 | 0.12817 | 0.15106 | -0.018311 | -0.15564 | 0.045776 | 0.07782 | -0.027466 | 0.045776 | 0.018311 | -0.068665 | -0.12817 | 2.0416 | 1.9043 | -119.4214 | 2.1561 | 2.1881 | 0.28381 | -119.5221 | 1.9913 | 1.9318 | -119.5267 | 2.1057 | 2.0325 | 0.10071 | -119.5541 | 2.211 | 2.1103 | 2.1515 | -119.7281 | 2.1057 | 2.0782 | 2.1378 | -119.7006
2967.1562 | 121.5775 | -2.005 | 119.632 | -0.00099167 | 0.011164 | 0.05369 | 0.0051248 | 0.0040417 | 0.00029476 | -0.0042254 | 0.014572 | -0.0034308 | 0.0042148 | -0.0024182 | -0.0079169 | 0.019038 | 0.050354 | 0.068665 | 0.054932 | 0.11902 | 0.14191 | -0.041199 | -0.16937 | 0.054932 | 0.054932 | -0.050354 | 0.041199 | 0.032043 | -0.064087 | -0.10529 | 1.9638 | 1.8356 | -119.4901 | 2.0737 | 2.124 | 0.28839 | -119.5816 | 1.9409 | 1.8997 | -119.5908 | 2.0599 | 1.9547 | 0.054932 | -119.5999 | 2.1469 | 2.0554 | 2.0599 | -119.8013 | 2.0462 | 2.037 | 2.0599 | -119.7372
2968.8438 | 121.6095 | -1.8814 | 119.751 | -0.00099167 | 0.010737 | 0.053476 | 0.0059792 | 0.0055371 | 8.1158e-05 | -0.0048662 | 0.014572 | -0.002149 | 0.0054966 | -0.0032728 | -0.0083441 | 0.018397 | 0.022888 | 0.009155 | 0.004578 | 0.082397 | 0.15106 | -0.032043 | -0.1831 | 0.036621 | 0.041199 | -0.064087 | 0.073242 | 0.036621 | -0.050354 | -0.12817 | 1.8494 | 1.6983 | -119.5999 | 1.8906 | 1.9638 | 0.2655 | -119.7281 | 1.8311 | 1.7532 | -119.6777 | 1.918 | 1.8173 | 0.064087 | -119.7144 | 2.0325 | 1.9043 | 1.886 | -119.9341 | 1.9547 | 1.918 | 1.9226 | -119.8792
2970.5938 | 121.6003 | -1.8631 | 119.7876 | 0.0066373 | 0.013514 | 0.051981 | 0.0081154 | 0.0036145 | 0.0028584 | -0.0046526 | -0.00068649 | -0.0010808 | 0.006992 | -0.001991 | -0.0098395 | 0.02032 | -0.041199 | -0.045776 | -0.064087 | 0.041199 | 0.1831 | -0.07782 | -0.20599 | -0.054932 | -0.059509 | -0.16022 | 0.073242 | 0.07782 | -0.091553 | -0.16022 | 1.7853 | 1.6571 | -119.6045 | 1.8173 | 1.9043 | 0.24719 | -119.8288 | 1.7715 | 1.7029 | -119.7144 | 1.8082 | 1.7029 | 0 | -119.7098 | 2.0462 | 1.8219 | 1.799 | -119.9936 | 1.9363 | 1.9409 | 1.8036 | -119.9478
2972.3438 | 121.6003 | -1.7853 | 119.8608 | 0.021896 | 0.0133 | 0.053263 | 0.007261 | 0.0051099 | 0.0022174 | -0.0048662 | -0.00068649 | -0.002149 | 0.004642 | -0.0043408 | -0.0074897 | 0.020961 | -0.027466 | -0.013733 | -0.027466 | 0.050354 | 0.16479 | -0.050354 | -0.20142 | -0.004578 | 0.009155 | -0.09613 | 0.07782 | 0.064087 | -0.073242 | -0.13733 | 1.7349 | 1.5839 | -119.696 | 1.7715 | 1.8356 | 0.25177 | -119.8883 | 1.712 | 1.6479 | -119.783 | 1.7807 | 1.6891 | 0.041199 | -119.7968 | 1.9501 | 1.7578 | 1.7578 | -120.0623 | 1.8631 | 1.8494 | 1.7944 | -119.9982
2974.0938 | 121.6049 | -1.6571 | 119.989 | -0.00099167 | 0.015009 | 0.05369 | 0.0076882 | 0.0016919 | 0.0015766 | -0.00508 | 0.0069425 | -0.0034308 | 0.0074192 | -0.00028199 | -0.010694 | 0.018611 | -0.036621 | -0.059509 | -0.036621 | 0.045776 | 0.19684 | -0.054932 | -0.20599 | -0.018311 | -0.027466 | -0.10986 | 0.068665 | 0.041199 | -0.073242 | -0.14648 | 1.6022 | 1.4511 | -119.7922 | 1.5976 | 1.7029 | 0.25177 | -120.0256 | 1.5839 | 1.5106 | -119.9203 | 1.6388 | 1.5472 | 0.036621 | -119.9478 | 1.8539 | 1.6205 | 1.6205 | -120.195 | 1.7258 | 1.6983 | 1.6296 | -120.1355
2975.7812 | 121.6919 | -1.5518 | 120.0485 | -0.0086212 | 0.01095 | 0.057535 | 0.0070474 | -0.0023669 | -0.0056866 | -0.0063616 | -0.00068649 | -0.0062078 | 0.0059238 | -0.0041272 | -0.01283 | 0.019679 | 0.032043 | 0.1236 | 0.09613 | 0.13733 | 0.14191 | -0.032043 | -0.17395 | 0.032043 | 0.10986 | 0 | 0.054932 | 0.027466 | -0.059509 | -0.1236 | 1.5198 | 1.3779 | -119.9066 | 1.6754 | 1.6891 | 0.31128 | -120.0165 | 1.4923 | 1.4282 | -119.9936 | 1.5839 | 1.5518 | 0.1236 | -120.0211 | 1.6937 | 1.5839 | 1.6479 | -120.2225 | 1.6068 | 1.5793 | 1.6617 | -120.1721
2977.5469 | 121.6187 | -1.593 | 120.0806 | 0.0066373 | 0.011805 | 0.054117 | 0.0096108 | 0.0014783 | -0.0035504 | -0.0080706 | 0.0069425 | -0.007276 | 0.0061374 | -0.0041272 | -0.011976 | 0.019038 | -0.009155 | 0.009155 | 0.027466 | 0.07782 | 0.16022 | -0.045776 | -0.15564 | -0.009155 | 0.022888 | -0.059509 | 0.059509 | 0.068665 | -0.068665 | -0.13733 | 1.5472 | 1.4374 | -119.9203 | 1.6022 | 1.6708 | 0.23346 | -120.0897 | 1.5244 | 1.4557 | -120.0211 | 1.5839 | 1.5335 | 0.07782 | -120.0119 | 1.7532 | 1.5839 | 1.6205 | -120.2362 | 1.6525 | 1.6617 | 1.6159 | -120.2179
2979.2344 | 121.669 | -1.4923 | 120.163 | 0.0066373 | 0.010737 | 0.05369 | 0.0029886 | 0.0019055 | -0.0039776 | -0.0080706 | 0.0069425 | -0.0047124 | 0.0044284 | -0.003059 | -0.013258 | 0.018824 | -0.018311 | 0.036621 | 0.032043 | 0.091553 | 0.14648 | -0.027466 | -0.20142 | 0.004578 | 0.041199 | -0.050354 | 0.059509 | 0.050354 | -0.082397 | -0.13733 | 1.4648 | 1.2909 | -120.0165 | 1.5289 | 1.5839 | 0.29297 | -120.1813 | 1.4099 | 1.355 | -120.1035 | 1.4969 | 1.442 | 0.086975 | -120.1126 | 1.6388 | 1.474 | 1.5244 | -120.3644 | 1.5518 | 1.5427 | 1.5335 | -120.3003
2980.9219 | 121.6919 | -0.20599 | 121.431 | -0.0086212 | 0.015223 | 0.053476 | 0.0074746 | 0.0025465 | 0.0043536 | -0.0059344 | -0.00068649 | 0.00020076 | 0.0065646 | -0.003059 | -0.0085577 | 0.017756 | 0.027466 | 0.036621 | -0.004578 | 0.086975 | 0.1831 | -0.054932 | -0.19684 | 0 | 0.018311 | -0.13275 | 0.086975 | 0.059509 | -0.10071 | -0.13275 | 0.15106 | 0.009156 | -121.2479 | 0.24262 | 0.29297 | 0.28381 | -121.4035 | 0.10529 | 0.073243 | -121.344 | 0.20599 | 0.073243 | 0 | -121.3715 | 0.3891 | 0.23346 | 0.20142 | -121.6278 | 0.29297 | 0.2655 | 0.22431 | -121.5637
2982.6875 | 121.701 | -0.21515 | 121.4218 | 0.014267 | 0.015009 | 0.052622 | 0.0064066 | 0.0014783 | 0.004781 | -0.0063616 | 0.0069425 | -0.0030034 | 0.0076328 | -0.0028454 | -0.0081305 | 0.01797 | 0.027466 | 0.013733 | 0.004578 | 0.082397 | 0.16937 | -0.050354 | -0.20599 | -0.013733 | 0.027466 | -0.13275 | 0.064087 | 0.082397 | -0.10071 | -0.12817 | 0.16479 | 0.009155 | -121.2524 | 0.22888 | 0.29755 | 0.28839 | -121.3943 | 0.11444 | 0.086975 | -121.3577 | 0.20142 | 0.082398 | -0.004577 | -121.3394 | 0.38452 | 0.24261 | 0.21973 | -121.6278 | 0.27924 | 0.29755 | 0.24261 | -121.55
2984.3906 | 121.3577 | -0.22888 | 121.4951 | -0.00099167 | 0.012873 | 0.054331 | 0.0042702 | 0.00062386 | -0.0016278 | -0.0048662 | -0.00068649 | -0.0064214 | 0.006351 | -0.00049559 | -0.0087713 | 0.019679 | 0.059509 | 0.10071 | 0.086975 | 0.11902 | 0.12817 | -0.013733 | -0.16937 | 0.054932 | 0.082397 | -0.032043 | 0.022888 | 0.032043 | -0.059509 | -0.11444 | 0.21515 | 0.059509 | -121.3669 | 0.32959 | 0.3479 | 0.28839 | -121.4355 | 0.16937 | 0.11444 | -121.4722 | 0.28381 | 0.19684 | 0.082398 | -121.463 | 0.35706 | 0.28839 | 0.31586 | -121.6644 | 0.25177 | 0.26093 | 0.31128 | -121.6095
2986.1562 | 121.6415 | -0.23804 | 121.4676 | -0.00099167 | 0.010309 | 0.054758 | 0.0074746 | 0.0019055 | -0.005473 | -0.0093524 | 0.0069425 | -0.0053534 | 0.0061374 | -0.0032728 | -0.013898 | 0.021174 | -0.022888 | 0.009155 | 0.045776 | 0.09613 | 0.14648 | -0.045776 | -0.17395 | -0.004578 | 0.041199 | -0.050354 | 0.068665 | 0.041199 | -0.073242 | -0.13733 | 0.19226 | 0.064087 | -121.3211 | 0.24719 | 0.33417 | 0.27008 | -121.4905 | 0.16479 | 0.10071 | -121.3989 | 0.23346 | 0.18768 | 0.086975 | -121.4264 | 0.38452 | 0.21515 | 0.28381 | -121.6415 | 0.3067 | 0.27924 | 0.27924 | -121.6049
2987.8594 | 121.7331 | -0.23346 | 121.463 | -0.00099167 | 0.013514 | 0.053904 | 0.0059792 | 0.00083746 | -0.0018414 | -0.0046526 | 0.0069425 | -0.0053534 | 0.0048556 | -0.003059 | -0.013898 | 0.020106 | 0.086975 | 0.12817 | 0.11902 | 0.13275 | 0.14648 | -0.027466 | -0.1831 | 0.032043 | 0.1236 | -0.004578 | 0.022888 | 0.054932 | -0.064087 | -0.11444 | 0.20599 | 0.050354 | -121.3165 | 0.36163 | 0.36621 | 0.31586 | -121.376 | 0.16937 | 0.11902 | -121.4401 | 0.2655 | 0.22888 | 0.10986 | -121.4081 | 0.37994 | 0.32043 | 0.35248 | -121.6461 | 0.25635 | 0.28839 | 0.35706 | -121.5775
2989.625 | 115.4709 | -45.1813 | 70.1202 | -0.00099167 | 0.012232 | 0.054758 | 0.00897 | 0.0027601 | 0.001363 | -0.0063616 | -0.00068649 | -0.0036444 | 0.0072056 | -0.00049559 | -0.010694 | 0.016902 | 0 | -0.013733 | -0.018311 | 0.050354 | 0.19226 | -0.054932 | -0.20142 | -0.073242 | -0.013733 | -0.13733 | 0.09613 | 0.091553 | -0.10071 | -0.15564 | 45.1263 | 44.9799 | -69.928 | 45.1675 | 45.2316 | 0.25177 | -70.1202 | 45.0806 | 45.0256 | -70.0241 | 45.108 | 45.0439 | 0.018311 | -70.0287 | 45.3735 | 45.1813 | 45.163 | -70.3217 | 45.2774 | 45.2728 | 45.1675 | -70.2759
2991.375 | 120.575 | -0.18768 | 120.5017 | 0.0066373 | 0.014155 | 0.05369 | 0.0034158 | 0.0036145 | 0.0062762 | -0.0029436 | -0.008316 | 0.00020076 | 0.0054966 | -0.0011364 | -0.0074897 | 0.019252 | -0.032043 | -0.07782 | -0.091553 | 0.022888 | 0.20142 | -0.036621 | -0.20599 | -0.041199 | -0.073242 | -0.1831 | 0.086975 | 0.07782 | -0.09613 | -0.16022 | 0.15106 | -0.018311 | -120.3003 | 0.10986 | 0.21057 | 0.22888 | -120.5338 | 0.091553 | 0.027466 | -120.4147 | 0.14648 | 0.004578 | -0.022888 | -120.4239 | 0.3891 | 0.15564 | 0.09613 | -120.7077 | 0.27466 | 0.2655 | 0.11444 | -120.6619
2993.0781 | 120.845 | -0.16022 | 120.6528 | -0.0086212 | 0.013087 | 0.052835 | 0.0083292 | 0.0040417 | -0.0022686 | -0.0025164 | 0.014572 | -0.0047124 | 0.0076328 | -0.00049559 | -0.013044 | 0.019038 | -0.032043 | -0.022888 | -0.032043 | 0.050354 | 0.17395 | -0.07782 | -0.20599 | -0.068665 | -0.004578 | -0.13733 | 0.09613 | 0.073242 | -0.09613 | -0.16937 | 0.082397 | -0.045777 | -120.4788 | 0.13733 | 0.21057 | 0.25635 | -120.6848 | 0.064087 | -0.009156 | -120.5566 | 0.091552 | 0.022888 | 0.032044 | -120.5795 | 0.33417 | 0.12817 | 0.12817 | -120.8588 | 0.25635 | 0.23346 | 0.15564 | -120.8221
2994.7812 | 120.8038 | -0.76446 | 120.1904 | 0.0066373 | 0.0081732 | 0.056681 | 0.0012796 | 0.0048963 | -0.00013244 | -0.0040118 | 0.014572 | -0.0049262 | 0.005283 | -0.003059 | -0.010908 | 0.018824 | 0.050354 | 0.10529 | 0.09613 | 0.11444 | 0.13733 | -0.022888 | -0.16937 | 0.032043 | 0.082397 | -0.036621 | 0.045776 | 0.036621 | -0.054932 | -0.11444 | 0.74158 | 0.59509 | -120.0531 | 0.86975 | 0.87891 | 0.28381 | -120.1401 | 0.70953 | 0.65002 | -120.1447 | 0.79651 | 0.72784 | 0.07782 | -120.1538 | 0.90179 | 0.81482 | 0.86059 | -120.3598 | 0.81024 | 0.80109 | 0.84686 | -120.3049
2996.5312 | 120.9869 | -0.6134 | 120.2911 | 0.0066373 | 0.010737 | 0.056467 | 0.0051248 | 0.0029737 | -0.0026958 | -0.0067888 | 0.0069425 | -0.0051398 | 0.0044284 | -0.0039136 | -0.011335 | 0.020533 | -0.022888 | 0.032043 | 0.032043 | 0.10071 | 0.15106 | -0.041199 | -0.18768 | 0 | 0.054932 | -0.036621 | 0.050354 | 0.032043 | -0.07782 | -0.13733 | 0.5722 | 0.42572 | -120.1401 | 0.64545 | 0.71411 | 0.28839 | -120.314 | 0.53558 | 0.47607 | -120.2408 | 0.6134 | 0.57678 | 0.10071 | -120.2591 | 0.76447 | 0.59052 | 0.64545 | -120.4788 | 0.66376 | 0.64545 | 0.66834 | -120.4285
2998.2344 | 120.9274 | -0.65002 | 120.4056 | 0.0066373 | 0.0088142 | 0.054758 | 0.005552 | 0.0040417 | -0.0012006 | -0.0057208 | -0.008316 | -0.0040716 | 0.0061374 | -0.0032728 | -0.011976 | 0.021601 | 0.009155 | 0.045776 | 0.032043 | 0.073242 | 0.16022 | -0.045776 | -0.17395 | 0 | 0.027466 | -0.054932 | 0.041199 | 0.059509 | -0.073242 | -0.13275 | 0.60425 | 0.47607 | -120.2454 | 0.6958 | 0.72327 | 0.24719 | -120.3964 | 0.57678 | 0.51727 | -120.3644 | 0.65002 | 0.59509 | 0.077819 | -120.3461 | 0.81024 | 0.65918 | 0.68207 | -120.5795 | 0.69122 | 0.70953 | 0.67749 | -120.5383
2999.9844 | 121.1014 | -0.56305 | 120.4651 | -0.00099167 | 0.011591 | 0.05369 | 0.0079018 | 0.0016919 | 0.00414 | -0.0070026 | -0.00068649 | -0.0017218 | 0.0061374 | -0.001991 | -0.0083441 | 0.017543 | -0.013733 | -0.050354 | -0.054932 | 0.041199 | 0.21515 | -0.059509 | -0.21973 | -0.059509 | -0.022888 | -0.16022 | 0.10071 | 0.07782 | -0.09613 | -0.16022 | 0.50354 | 0.34332 | -120.2499 | 0.5127 | 0.60425 | 0.26093 | -120.4788 | 0.46692 | 0.40283 | -120.3644 | 0.50354 | 0.40283 | 0 | -120.3873 | 0.7782 | 0.54932 | 0.50812 | -120.6848 | 0.66376 | 0.64087 | 0.54016 | -120.6253
3001.6875 | 121.0327 | -0.54932 | 120.5566 | 0.0066373 | 0.012446 | 0.053049 | 0.0064066 | 0.0019055 | 0.0043536 | -0.0035846 | 0.0069425 | -0.0012946 | 0.0054966 | -0.0022046 | -0.0081305 | 0.018824 | 0.032043 | 0.022888 | 0.013733 | 0.086975 | 0.16937 | -0.027466 | -0.19226 | 0.045776 | 0.064087 | -0.068665 | 0.050354 | 0.041199 | -0.064087 | -0.10529 | 0.52185 | 0.35706 | -120.3873 | 0.5722 | 0.63629 | 0.27924 | -120.5246 | 0.48523 | 0.44403 | -120.5063 | 0.59509 | 0.48065 | 0.036621 | -120.5154 | 0.71869 | 0.58136 | 0.56305 | -120.7489 | 0.59967 | 0.59052 | 0.6134 | -120.6619
3003.4375 | 121.1609 | -0.45776 | 120.6482 | 0.0066373 | 0.014368 | 0.053904 | 0.0085428 | 0.0053235 | -0.00013244 | -0.006148 | -0.00068649 | -0.0010808 | 0.0078464 | -0.0028454 | -0.01048 | 0.018824 | -0.036621 | -0.045776 | -0.059509 | 0.045776 | 0.1831 | -0.073242 | -0.2243 | -0.07782 | -0.032043 | -0.16479 | 0.09613 | 0.09613 | -0.082397 | -0.15106 | 0.38452 | 0.23346 | -120.4651 | 0.41199 | 0.50354 | 0.27008 | -120.6848 | 0.37537 | 0.3067 | -120.5521 | 0.37994 | 0.29297 | -0.013733 | -120.5521 | 0.64087 | 0.42114 | 0.39826 | -120.8725 | 0.55389 | 0.55389 | 0.42572 | -120.7993
3005.125 | 121.1609 | -0.42114 | 120.6802 | -0.00099167 | 0.013514 | 0.054544 | 0.007261 | 0.0021191 | -0.0029094 | -0.004439 | 0.0069425 | -0.006635 | 0.0076328 | -0.0026318 | -0.013471 | 0.019893 | 0.054932 | 0.10986 | 0.10071 | 0.11444 | 0.14648 | -0.022888 | -0.17395 | 0.036621 | 0.13733 | 0.004578 | 0.041199 | 0.027466 | -0.059509 | -0.13275 | 0.39825 | 0.24719 | -120.5338 | 0.53101 | 0.53558 | 0.28839 | -120.6253 | 0.36163 | 0.28839 | -120.639 | 0.45776 | 0.42572 | 0.13733 | -120.6528 | 0.56763 | 0.47607 | 0.52185 | -120.8542 | 0.46234 | 0.44861 | 0.55847 | -120.813
3006.8906 | 121.2158 | -0.4303 | 120.7031 | -0.00099167 | 0.011591 | 0.054117 | 0.0061928 | 0.00083746 | -0.0052594 | -0.0070026 | 0.0069425 | -0.005567 | 0.0067782 | -0.0011364 | -0.013685 | 0.018824 | 0.041199 | 0.10071 | 0.10071 | 0.11902 | 0.15564 | -0.018311 | -0.16022 | 0.059509 | 0.11902 | 0 | 0.050354 | 0.018311 | -0.059509 | -0.1236 | 0.41199 | 0.27008 | -120.5475 | 0.53101 | 0.54932 | 0.27924 | -120.6619 | 0.37079 | 0.3067 | -120.6528 | 0.48981 | 0.4303 | 0.1236 | -120.6848 | 0.58594 | 0.4715 | 0.53101 | -120.8633 | 0.48065 | 0.44861 | 0.54932 | -120.8267
3008.6406 | 121.1243 | -0.48981 | 120.7352 | -0.016251 | 0.012018 | 0.051981 | 0.0053384 | 0.0038281 | 0.0052082 | -0.006148 | 0.0069425 | -1.2844e-05 | 0.0067782 | -0.0017774 | -0.0068487 | 0.018184 | -0.027466 | -0.073242 | -0.068665 | 0.050354 | 0.17853 | -0.064087 | -0.20599 | -0.068665 | -0.07782 | -0.19684 | 0.09613 | 0.07782 | -0.086975 | -0.16479 | 0.42572 | 0.28381 | -120.5566 | 0.41656 | 0.54016 | 0.25635 | -120.7626 | 0.40283 | 0.32501 | -120.639 | 0.42114 | 0.29297 | -0.032043 | -120.6573 | 0.66834 | 0.46234 | 0.42114 | -120.9412 | 0.58594 | 0.56763 | 0.41199 | -120.9
3010.3906 | 121.2341 | -0.44861 | 120.7352 | -0.00099167 | 0.015436 | 0.054544 | 0.0064066 | -0.00065794 | 0.00050836 | -0.0065752 | 0.0069425 | -0.0023626 | 0.0061374 | -0.0015638 | -0.010053 | 0.018397 | -0.050354 | -0.013733 | -0.050354 | 0.027466 | 0.1831 | -0.059509 | -0.23346 | -0.07782 | -0.022888 | -0.16937 | 0.10071 | 0.082397 | -0.10071 | -0.16479 | 0.3891 | 0.21515 | -120.5521 | 0.43488 | 0.47607 | 0.26093 | -120.7855 | 0.3479 | 0.28381 | -120.6345 | 0.37079 | 0.27924 | -0.004578 | -120.6528 | 0.63171 | 0.39825 | 0.39825 | -120.9686 | 0.54932 | 0.531 | 0.42572 | -120.9
3012.0938 | 121.2479 | -0.35706 | 120.7901 | -0.00099167 | 0.013087 | 0.054544 | 0.007261 | 0.0038281 | -0.0029094 | -0.0029436 | 0.0069425 | -0.008344 | 0.006351 | -0.0034864 | -0.012403 | 0.017756 | 0.059509 | 0.13275 | 0.086975 | 0.11444 | 0.14648 | -0.027466 | -0.1831 | 0.050354 | 0.14648 | -0.009155 | 0.073242 | 0.041199 | -0.054932 | -0.12817 | 0.32959 | 0.17395 | -120.6436 | 0.48981 | 0.4715 | 0.29755 | -120.7306 | 0.30212 | 0.22888 | -120.7169 | 0.40741 | 0.3479 | 0.11902 | -120.7489 | 0.50354 | 0.41656 | 0.44403 | -120.9732 | 0.4303 | 0.39825 | 0.50354 | -120.9183
3013.8438 | 121.1746 | -0.43945 | 120.8038 | -0.00099167 | 0.011378 | 0.05369 | 0.0029886 | 0.00083746 | 0.0017902 | -0.0029436 | 0.014572 | -0.0025762 | 0.0048556 | -0.0028454 | -0.0077033 | 0.019465 | 0.059509 | 0.064087 | 0.045776 | 0.11444 | 0.14648 | -0.032043 | -0.16479 | 0.050354 | 0.068665 | -0.032043 | 0.022888 | 0.036621 | -0.041199 | -0.10986 | 0.40741 | 0.27466 | -120.6573 | 0.50354 | 0.55389 | 0.27924 | -120.7443 | 0.39825 | 0.32959 | -120.7809 | 0.48981 | 0.40741 | 0.07782 | -120.7672 | 0.58594 | 0.49896 | 0.48523 | -120.9686 | 0.46234 | 0.47607 | 0.50812 | -120.9137
3015.5781 | 121.225 | -0.40741 | 120.8771 | -0.0086212 | 0.009455 | 0.054331 | 0.0066202 | 0.0038281 | -0.002055 | -0.006148 | -0.00068649 | -0.0064214 | 0.0057102 | -0.0028454 | -0.011121 | 0.020533 | -0.022888 | 0.036621 | 0.027466 | 0.082397 | 0.12817 | -0.027466 | -0.17853 | 0 | 0.032043 | -0.068665 | 0.068665 | 0.064087 | -0.054932 | -0.13733 | 0.37994 | 0.22888 | -120.7489 | 0.44403 | 0.48981 | 0.26092 | -120.9 | 0.35248 | 0.27008 | -120.8084 | 0.40741 | 0.33874 | 0.068664 | -120.813 | 0.53558 | 0.38452 | 0.43488 | -121.0556 | 0.47608 | 0.4715 | 0.43945 | -121.0144
3017.2812 | 121.2341 | -0.42572 | 120.8496 | 0.014267 | 0.011378 | 0.053049 | 0.0029886 | 0.0014783 | 0.0028584 | -0.0042254 | 0.0069425 | -0.0017218 | 0.0050694 | -0.0028454 | -0.0066351 | 0.020961 | 0.091553 | 0.09613 | 0.082397 | 0.13275 | 0.14191 | -0.018311 | -0.13733 | 0.054932 | 0.073242 | -0.027466 | 0.041199 | 0.050354 | -0.059509 | -0.1236 | 0.40741 | 0.28839 | -120.7077 | 0.52185 | 0.55847 | 0.27008 | -120.7581 | 0.36621 | 0.30212 | -120.8084 | 0.48065 | 0.39825 | 0.09613 | -120.7993 | 0.56763 | 0.51727 | 0.50812 | -120.9869 | 0.46692 | 0.47607 | 0.49896 | -120.9732
3019.0312 | 121.2936 | -0.42114 | 120.8725 | 0.014267 | 0.0133 | 0.052195 | 0.010893 | 0.0036145 | 8.1158e-05 | -0.00508 | -0.008316 | -0.007276 | 0.0072056 | -0.0034864 | -0.011121 | 0.018397 | 0.041199 | 0.086975 | 0.064087 | 0.13275 | 0.15564 | -0.036621 | -0.20142 | -0.004578 | 0.086975 | -0.082397 | 0.064087 | 0.054932 | -0.07782 | -0.13733 | 0.38452 | 0.21973 | -120.7169 | 0.50812 | 0.55389 | 0.33417 | -120.8313 | 0.34332 | 0.28381 | -120.8084 | 0.41656 | 0.33875 | 0.054932 | -120.8176 | 0.57678 | 0.46234 | 0.48523 | -121.0739 | 0.48523 | 0.47607 | 0.50812 | -121.0098
3020.7344 | 121.225 | -0.43945 | 120.8862 | 0.0066373 | 0.016077 | 0.054117 | 0.005552 | 0.0031873 | 0.0017902 | -0.0057208 | 0.0069425 | -0.003858 | 0.0074192 | -0.0039136 | -0.0083441 | 0.019252 | 0.050354 | 0.086975 | 0.082397 | 0.12817 | 0.13733 | -0.009155 | -0.16022 | 0.054932 | 0.086975 | -0.032043 | 0.032043 | 0.032043 | -0.050354 | -0.11444 | 0.4303 | 0.27924 | -120.7489 | 0.52643 | 0.56763 | 0.28839 | -120.8359 | 0.3891 | 0.32501 | -120.8542 | 0.49438 | 0.40741 | 0.082398 | -120.8542 | 0.57678 | 0.48981 | 0.52185 | -121.0464 | 0.4715 | 0.4715 | 0.52643 | -121.0007
3022.5 | 121.2845 | -0.54016 | 120.7809 | 0.0066373 | 0.013087 | 0.051767 | 0.0061928 | 0.0031873 | 0.0028584 | -0.0035846 | 0.014572 | -0.002149 | 0.0076328 | -0.0017774 | -0.0085577 | 0.01797 | -0.018311 | -0.036621 | -0.050354 | 0.050354 | 0.20599 | -0.059509 | -0.20599 | -0.032043 | -0.032043 | -0.13733 | 0.07782 | 0.059509 | -0.07782 | -0.14648 | 0.48065 | 0.33417 | -120.575 | 0.50354 | 0.59052 | 0.25635 | -120.7993 | 0.46234 | 0.39368 | -120.7031 | 0.50812 | 0.40283 | 0.009155 | -120.7214 | 0.74616 | 0.52185 | 0.48981 | -120.9869 | 0.61798 | 0.59967 | 0.50812 | -120.9274
3024.2656 | 121.3715 | -0.48523 | 120.8176 | -0.0086212 | 0.016291 | 0.05369 | 0.0093972 | 0.0044691 | 0.001363 | -0.0029436 | 0.014572 | -0.0027898 | 0.0074192 | -0.00092279 | -0.0083441 | 0.019893 | -0.054932 | -0.027466 | -0.054932 | 0.054932 | 0.19226 | -0.086975 | -0.2243 | -0.050354 | -0.013733 | -0.15106 | 0.091553 | 0.059509 | -0.10986 | -0.16937 | 0.39825 | 0.26093 | -120.6253 | 0.45776 | 0.54016 | 0.27924 | -120.8725 | 0.37537 | 0.31586 | -120.726 | 0.43488 | 0.33417 | 0.018311 | -120.7581 | 0.67749 | 0.4303 | 0.4303 | -121.0419 | 0.57678 | 0.54474 | 0.4715 | -120.9869
3026.0312 | 121.4127 | -0.43488 | 120.8954 | -0.00099167 | 0.015009 | 0.050913 | 0.0064066 | 0.0021191 | 0.0026446 | -0.0042254 | -0.00068649 | -0.00086724 | 0.0059238 | -0.0013502 | -0.0094123 | 0.018184 | -0.041199 | -0.022888 | -0.045776 | 0.064087 | 0.17395 | -0.041199 | -0.19684 | -0.045776 | 0 | -0.1236 | 0.082397 | 0.086975 | -0.082397 | -0.16022 | 0.39368 | 0.23804 | -120.7214 | 0.41199 | 0.49896 | 0.26093 | -120.9366 | 0.35248 | 0.27466 | -120.813 | 0.3891 | 0.31128 | 0.036621 | -120.8084 | 0.60882 | 0.39368 | 0.3891 | -121.0922 | 0.51727 | 0.52185 | 0.43488 | -121.0556
3027.7188 | 121.4035 | -0.46692 | 120.8496 | -0.00099167 | 0.01565 | 0.052622 | 0.0081154 | 0.0010511 | 0.00072196 | -0.0012346 | -0.00068649 | -0.0025762 | 0.0074192 | -0.0022046 | -0.011976 | 0.016047 | -0.022888 | 0.009155 | -0.004578 | 0.086975 | 0.16022 | -0.073242 | -0.20599 | -0.027466 | 0.041199 | -0.1236 | 0.091553 | 0.064087 | -0.10071 | -0.13733 | 0.39368 | 0.26092 | -120.6894 | 0.47607 | 0.55389 | 0.29297 | -120.8725 | 0.36621 | 0.32959 | -120.7581 | 0.43945 | 0.34332 | 0.013733 | -120.7855 | 0.62714 | 0.44403 | 0.46234 | -121.0556 | 0.55847 | 0.53101 | 0.50812 | -120.9869
3029.4688 | 121.3257 | -0.43488 | 120.9732 | -0.0086212 | 0.012873 | 0.051554 | 0.005552 | 0.0029737 | -0.00034604 | -0.0042254 | 0.0069425 | -0.005567 | 0.0050694 | -0.0039136 | -0.0094123 | 0.021388 | 0.032043 | 0.086975 | 0.059509 | 0.13275 | 0.12817 | -0.009155 | -0.16937 | 0.045776 | 0.07782 | -0.032043 | 0.050354 | 0.022888 | -0.059509 | -0.13275 | 0.42572 | 0.2655 | -120.845 | 0.52185 | 0.56763 | 0.30212 | -120.9412 | 0.37537 | 0.30212 | -120.9229 | 0.48065 | 0.40283 | 0.10071 | -120.9503 | 0.56305 | 0.46692 | 0.49438 | -121.1426 | 0.48523 | 0.45776 | 0.5127 | -121.106
3031.2344 | 121.4539 | -0.37537 | 120.9457 | -0.016251 | 0.016718 | 0.052195 | 0.0093972 | 0.0012647 | 0.00050836 | -0.0048662 | -0.008316 | -0.002149 | 0.006992 | 0.00014521 | -0.010053 | 0.017115 | -0.050354 | -0.013733 | -0.036621 | 0.059509 | 0.17395 | -0.068665 | -0.21057 | -0.050354 | -0.004578 | -0.13733 | 0.091553 | 0.068665 | -0.086975 | -0.15564 | 0.3067 | 0.16479 | -120.7718 | 0.36163 | 0.43487 | 0.27008 | -120.9961 | 0.28839 | 0.21973 | -120.8542 | 0.32501 | 0.23804 | 0.018311 | -120.8771 | 0.54932 | 0.32501 | 0.33874 | -121.1563 | 0.46692 | 0.44403 | 0.37079 | -121.1014
3032.9844 | 121.3486 | -0.43488 | 121.0236 | -0.0086212 | 0.0133 | 0.05369 | 0.0053384 | 0.0046827 | 0.0026446 | -0.0035846 | 0.0069425 | -0.0023626 | 0.0054966 | -0.0011364 | -0.0087713 | 0.022029 | -0.050354 | -0.050354 | -0.064087 | 0.045776 | 0.1831 | -0.059509 | -0.21973 | -0.064087 | -0.054932 | -0.15564 | 0.07782 | 0.086975 | -0.068665 | -0.15564 | 0.37537 | 0.21515 | -120.8405 | 0.38452 | 0.48065 | 0.2655 | -121.0739 | 0.36621 | 0.27924 | -120.9457 | 0.37079 | 0.27924 | 0 | -120.9366 | 0.61798 | 0.38452 | 0.37079 | -121.2433 | 0.5127 | 0.52185 | 0.37994 | -121.1792
3034.75 | 121.344 | -0.37079 | 121.0785 | 0.0066373 | 0.016932 | 0.053904 | 0.0042702 | 0.0046827 | 0.0011494 | -0.0031574 | -0.00068649 | -0.00065364 | 0.0061374 | -0.0034864 | -0.0081305 | 0.022883 | -0.073242 | -0.07782 | -0.059509 | 0.032043 | 0.17853 | -0.059509 | -0.20599 | -0.082397 | -0.068665 | -0.17853 | 0.091553 | 0.073242 | -0.086975 | -0.16937 | 0.31128 | 0.16479 | -120.9 | 0.29297 | 0.40283 | 0.23804 | -121.1517 | 0.28381 | 0.20142 | -120.9869 | 0.28839 | 0.19226 | -0.009155 | -121.0052 | 0.54932 | 0.29755 | 0.31128 | -121.2845 | 0.46234 | 0.44403 | 0.30212 | -121.2479
3036.4531 | 121.3303 | -0.3891 | 121.0693 | -0.00099167 | 0.010737 | 0.052622 | 0.0044838 | 0.0034009 | -0.0044048 | -0.006148 | -0.00068649 | -0.005567 | 0.0025058 | -0.0051954 | -0.010694 | 0.02331 | 0.036621 | 0.07782 | 0.07782 | 0.1236 | 0.13733 | -0.022888 | -0.16479 | 0.009155 | 0.07782 | -0.027466 | 0.032043 | 0.045776 | -0.050354 | -0.1236 | 0.36621 | 0.2243 | -120.932 | 0.46692 | 0.5127 | 0.28839 | -121.0327 | 0.33874 | 0.2655 | -121.0373 | 0.39825 | 0.36163 | 0.09613 | -121.0236 | 0.52643 | 0.42572 | 0.46692 | -121.2341 | 0.42114 | 0.43487 | 0.46692 | -121.1929
3038.2031 | 121.4218 | -0.28839 | 121.1334 | 0.0066373 | 0.017145 | 0.053476 | 0.0068338 | 0.0051099 | 0.00414 | -0.0059344 | 0.0069425 | -0.0040716 | 0.0076328 | -0.0013502 | -0.0087713 | 0.016902 | 0.018311 | 0.027466 | 0.004578 | 0.068665 | 0.16937 | -0.045776 | -0.21057 | -0.036621 | 0.022888 | -0.1236 | 0.073242 | 0.068665 | -0.07782 | -0.13733 | 0.24262 | 0.07782 | -120.9641 | 0.31586 | 0.35706 | 0.27924 | -121.1151 | 0.21057 | 0.15106 | -121.0602 | 0.25177 | 0.1648 | 0.013733 | -121.0648 | 0.45776 | 0.3067 | 0.29297 | -121.344 | 0.36163 | 0.35706 | 0.31128 | -121.2708
3039.9531 | 121.4813 | -0.27924 | 121.1151 | -0.0086212 | 0.015223 | 0.052195 | 0.012602 | 0.0051099 | -0.00077324 | -0.006148 | 0.0069425 | -0.0012946 | 0.0084872 | -0.0013502 | -0.012189 | 0.019465 | -0.059509 | -0.054932 | -0.041199 | 0.041199 | 0.1831 | -0.07782 | -0.2243 | -0.07782 | -0.022888 | -0.14648 | 0.09613 | 0.064087 | -0.10071 | -0.16022 | 0.20142 | 0.054932 | -120.932 | 0.2243 | 0.32043 | 0.2655 | -121.1746 | 0.17853 | 0.11902 | -121.019 | 0.20142 | 0.13275 | 0.013733 | -121.051 | 0.46234 | 0.21973 | 0.23804 | -121.3394 | 0.37537 | 0.34332 | 0.25635 | -121.2753
3041.7031 | 121.4493 | -0.37537 | 121.0327 | -0.00099167 | 0.014582 | 0.050913 | 0.0081154 | 0.0038281 | 0.0032856 | -0.0046526 | 0.0069425 | -0.0023626 | 0.0074192 | -0.00049559 | -0.011762 | 0.019038 | 0.013733 | 0.013733 | -0.004578 | 0.091553 | 0.18768 | -0.054932 | -0.21515 | -0.022888 | 0.032043 | -0.10986 | 0.086975 | 0.059509 | -0.09613 | -0.14191 | 0.32043 | 0.16022 | -120.845 | 0.3891 | 0.46692 | 0.3067 | -121.019 | 0.27924 | 0.23346 | -120.9457 | 0.35248 | 0.2655 | 0.032044 | -120.9732 | 0.56305 | 0.3891 | 0.37079 | -121.2479 | 0.46234 | 0.43487 | 0.40741 | -121.1746
3043.4531 | 121.4401 | -0.40283 | 121.0236 | 0.0066373 | 0.014155 | 0.051981 | 0.010252 | 0.0029737 | -0.0061138 | -0.0067888 | 0.0069425 | -0.0057806 | 0.0076328 | -0.0013502 | -0.013258 | 0.020106 | 0.013733 | 0.09613 | 0.086975 | 0.12817 | 0.15106 | -0.032043 | -0.17395 | 0 | 0.10071 | -0.041199 | 0.054932 | 0.07782 | -0.059509 | -0.13275 | 0.37079 | 0.22888 | -120.8725 | 0.49896 | 0.53101 | 0.30212 | -121.0098 | 0.34332 | 0.27008 | -120.9686 | 0.40283 | 0.36163 | 0.091552 | -120.9457 | 0.55389 | 0.41657 | 0.48981 | -121.1975 | 0.45776 | 0.48065 | 0.50354 | -121.1563
3045.2031 | 121.3852 | -0.39825 | 121.1014 | -0.00099167 | 0.010096 | 0.055826 | 0.0085428 | 0.0023327 | -0.0033368 | -0.0052936 | 0.0069425 | -0.0070624 | 0.0061374 | -0.0032728 | -0.011762 | 0.020961 | -0.032043 | 0.022888 | 0.027466 | 0.07782 | 0.16479 | -0.032043 | -0.17853 | -0.036621 | 0.032043 | -0.073242 | 0.059509 | 0.032043 | -0.059509 | -0.14191 | 0.36621 | 0.21973 | -120.9366 | 0.42114 | 0.47607 | 0.25635 | -121.1334 | 0.33875 | 0.25635 | -121.0419 | 0.36163 | 0.32501 | 0.068665 | -121.0693 | 0.56305 | 0.36621 | 0.42572 | -121.2799 | 0.45776 | 0.4303 | 0.4303 | -121.2433
3046.9062 | 121.5042 | -0.3479 | 121.0968 | -0.00099167 | 0.016291 | 0.053476 | 0.0066202 | 0.0021191 | 0.00414 | -0.0080706 | 0.0069425 | -0.00065364 | 0.0078464 | -0.0039136 | -0.0064215 | 0.017543 | 0 | 0.027466 | 0 | 0.082397 | 0.19226 | -0.068665 | -0.20142 | -0.027466 | 0.018311 | -0.11444 | 0.073242 | 0.064087 | -0.09613 | -0.16937 | 0.27924 | 0.14648 | -120.9045 | 0.37537 | 0.4303 | 0.28381 | -121.0968 | 0.25177 | 0.17853 | -121.0236 | 0.32043 | 0.23346 | 0.054932 | -121.0327 | 0.54016 | 0.3479 | 0.3479 | -121.2982 | 0.42114 | 0.41199 | 0.36621 | -121.2662
3048.6562 | 121.4584 | -0.2243 | 121.2845 | 0.0066373 | 0.012873 | 0.053904 | 0.0083292 | 0.0025465 | -0.0061138 | -0.0055072 | -0.008316 | -0.0068488 | 0.0067782 | -0.0039136 | -0.013258 | 0.019679 | -0.11902 | -0.036621 | -0.036621 | 0.018311 | 0.086975 | -0.10529 | -0.24261 | -0.022888 | 0.027466 | -0.045776 | 0.059509 | 0.032043 | -0.073242 | -0.13733 | 0.11902 | -0.018311 | -121.1975 | 0.18768 | 0.24261 | 0.26093 | -121.4035 | 0.15106 | 0.086975 | -121.225 | 0.20142 | 0.17853 | 0.091553 | -121.2524 | 0.31128 | 0.10529 | 0.18768 | -121.5271 | 0.28381 | 0.25635 | 0.25177 | -121.4218
3050.4219 | 121.5363 | -0.17853 | 121.2616 | -0.00099167 | 0.013514 | 0.053904 | 0.0093972 | 0.0021191 | -0.0029094 | -0.0055072 | 0.0069425 | -0.006635 | 0.0076328 | -0.0024182 | -0.01283 | 0.020106 | -0.027466 | 0.064087 | 0.036621 | 0.082397 | 0.09613 | -0.086975 | -0.24261 | 0.022888 | 0.11444 | -0.004578 | 0.041199 | 0.045776 | -0.068665 | -0.13275 | 0.091553 | -0.064087 | -121.1655 | 0.24261 | 0.26092 | 0.32501 | -121.2891 | 0.10986 | 0.045777 | -121.2204 | 0.20142 | 0.17395 | 0.12817 | -121.2158 | 0.27466 | 0.15106 | 0.21515 | -121.5042 | 0.21973 | 0.2243 | 0.29297 | -121.3943
3052.1875 | 121.5271 | -0.17395 | 121.2845 | 0.0066373 | 0.015009 | 0.050913 | 0.0068338 | -1.714e-05 | 0.0052082 | -0.0052936 | 0.0069425 | 0.00062796 | 0.006992 | -0.00049559 | -0.0079169 | 0.017756 | -0.032043 | -0.013733 | -0.045776 | 0.045776 | 0.1236 | -0.10071 | -0.24719 | -0.013733 | 0.018311 | -0.11902 | 0.073242 | 0.059509 | -0.09613 | -0.14648 | 0.073242 | -0.073242 | -121.1609 | 0.16022 | 0.21973 | 0.29297 | -121.3165 | 0.07782 | 0.027466 | -121.2112 | 0.16022 | 0.054931 | 0.027465 | -121.225 | 0.29755 | 0.14191 | 0.12817 | -121.5317 | 0.24719 | 0.23346 | 0.19226 | -121.431
3053.875 | 121.4218 | -0.22888 | 121.3303 | -0.00099167 | 0.0133 | 0.053476 | 0.0029886 | 0.0034009 | 0.0032856 | -0.0055072 | -0.00068649 | -0.0015082 | 0.0095554 | -0.0022046 | -0.0074897 | 0.019679 | -0.11902 | -0.10529 | -0.11444 | -0.004578 | 0.12817 | -0.10529 | -0.26093 | -0.073242 | -0.059509 | -0.1831 | 0.086975 | 0.082397 | -0.086975 | -0.16479 | 0.1236 | -0.032043 | -121.2021 | 0.1236 | 0.2243 | 0.25635 | -121.4493 | 0.14191 | 0.064087 | -121.2433 | 0.15564 | 0.045777 | -0.01831 | -121.2479 | 0.35706 | 0.10986 | 0.11444 | -121.5912 | 0.31586 | 0.31128 | 0.16937 | -121.4951
3055.6094 | 121.55 | -0.16937 | 121.3211 | 0.014267 | 0.006037 | 0.057962 | 0.0061928 | 0.0025465 | -0.005473 | -0.0072162 | 0.014572 | -0.0047124 | 0.0040012 | -0.0034864 | -0.011335 | 0.02267 | -0.07782 | 0.022888 | -0.018311 | 0.018311 | 0.073242 | -0.1236 | -0.24719 | 0.027466 | 0.10529 | -0.004578 | 0.050354 | 0.054932 | -0.059509 | -0.12817 | 0.045777 | -0.077819 | -121.2479 | 0.19226 | 0.18768 | 0.2655 | -121.3989 | 0.10986 | 0.041199 | -121.2708 | 0.19684 | 0.16479 | 0.1236 | -121.2662 | 0.24261 | 0.091553 | 0.15106 | -121.5683 | 0.21973 | 0.22431 | 0.27466 | -121.4493
3057.3125 | 121.4172 | -0.23804 | 121.3486 | 0.014267 | 0.014368 | 0.051981 | 0.0079018 | 0.0016919 | 0.004781 | -0.0031574 | -0.00068649 | 0.00062796 | 0.0067782 | -0.00028199 | -0.0077033 | 0.018611 | -0.050354 | -0.068665 | -0.07782 | 0.009155 | 0.10986 | -0.10529 | -0.27008 | -0.050354 | -0.032043 | -0.15564 | 0.064087 | 0.082397 | -0.091553 | -0.16937 | 0.13275 | -0.032044 | -121.2387 | 0.16937 | 0.24719 | 0.27924 | -121.3989 | 0.14648 | 0.068664 | -121.2845 | 0.18768 | 0.082397 | 0.013733 | -121.2662 | 0.3479 | 0.18768 | 0.16022 | -121.6187 | 0.30212 | 0.32043 | 0.20599 | -121.5179
3059.0625 | 121.4905 | -0.21973 | 121.3348 | -0.00099167 | 0.0073188 | 0.054972 | 0.0070474 | -0.00044434 | -0.0031232 | -0.007857 | -0.00068649 | -0.005567 | 0.0042148 | -0.001991 | -0.014326 | 0.018611 | -0.10529 | -0.036621 | -0.036621 | 0.022888 | 0.091553 | -0.091553 | -0.23346 | -0.013733 | 0.041199 | -0.059509 | 0.050354 | 0.041199 | -0.07782 | -0.13275 | 0.12817 | -0.013732 | -121.2433 | 0.18311 | 0.24261 | 0.25635 | -121.4401 | 0.14191 | 0.086976 | -121.2845 | 0.20599 | 0.16022 | 0.073242 | -121.2936 | 0.31128 | 0.11444 | 0.18311 | -121.5683 | 0.27008 | 0.26093 | 0.26093 | -121.4676
3060.8125 | 121.4127 | -0.23804 | 121.2982 | 0.0066373 | 0.01565 | 0.052835 | 0.003843 | 0.0034009 | 0.0049946 | -0.003371 | -0.008316 | -0.0012946 | 0.0059238 | -0.0024182 | -0.0057807 | 0.019038 | -0.11902 | -0.13275 | -0.1236 | -0.032043 | 0.12817 | -0.1236 | -0.27466 | -0.068665 | -0.091553 | -0.1831 | 0.091553 | 0.07782 | -0.10071 | -0.15106 | 0.11444 | -0.036621 | -121.17 | 0.10529 | 0.20599 | 0.24262 | -121.4172 | 0.13733 | 0.086975 | -121.2067 | 0.16937 | 0.054932 | -0.032043 | -121.2204 | 0.36621 | 0.11902 | 0.11444 | -121.5729 | 0.32959 | 0.31586 | 0.14648 | -121.4493
3062.5781 | 121.5546 | -0.24719 | 121.2662 | -0.0086212 | 0.0096686 | 0.054972 | 0.0064066 | 0.00062386 | -0.0059002 | -0.0072162 | -0.00068649 | -0.005567 | 0.002933 | -0.0051954 | -0.01283 | 0.021174 | -0.036621 | 0.027466 | 0.022888 | 0.068665 | 0.10986 | -0.091553 | -0.21973 | 0.018311 | 0.086975 | -0.022888 | 0.045776 | 0.050354 | -0.07782 | -0.1236 | 0.15564 | 0.027465 | -121.1563 | 0.27466 | 0.31586 | 0.28839 | -121.3028 | 0.16937 | 0.1236 | -121.2204 | 0.2655 | 0.2243 | 0.10071 | -121.2158 | 0.35706 | 0.21057 | 0.27008 | -121.4859 | 0.29297 | 0.29755 | 0.33417 | -121.3898
3064.2656 | 115.9744 | -40.036 | 75.737 | 0.0066373 | 0.013087 | 0.053904 | 0.0061928 | 0.0025465 | 0.0039264 | -0.0076434 | -0.00068649 | -0.0034308 | 0.0044284 | -0.0026318 | -0.0087713 | 0.018397 | 0.045776 | 0.004578 | 0.027466 | 0.082397 | 0.20599 | -0.022888 | -0.17395 | 0.036621 | 0.064087 | -0.054932 | 0.064087 | 0.082397 | -0.036621 | -0.086975 | 40.0131 | 39.8621 | -75.531 | 40.0406 | 40.1184 | 0.25635 | -75.6912 | 39.9994 | 39.949 | -75.6729 | 40.0726 | 39.9811 | 0.032043 | -75.6546 | 40.242 | 40.0818 | 40.0635 | -75.9109 | 40.1001 | 40.1184 | 40.1001 | -75.824
3066.0156 | 120.5292 | -0.13275 | 120.4239 | -0.0086212 | 0.012232 | 0.05604 | 0.0081154 | 0.0053235 | -0.0031232 | -0.0067888 | -0.008316 | -0.0057806 | 0.0065646 | -0.0045544 | -0.010694 | 0.018397 | 0.050354 | 0.068665 | 0.073242 | 0.13275 | 0.14191 | -0.027466 | -0.19226 | -0.004578 | 0.086975 | -0.045776 | 0.050354 | 0.041199 | -0.07782 | -0.13275 | 0.10529 | -0.05951 | -120.282 | 0.20142 | 0.2655 | 0.32501 | -120.3735 | 0.054931 | 0 | -120.3735 | 0.12817 | 0.086975 | 0.086975 | -120.3827 | 0.27466 | 0.18311 | 0.20599 | -120.6162 | 0.18311 | 0.17395 | 0.21973 | -120.5566
3067.7031 | 120.6848 | -0.20142 | 120.6619 | 0.014267 | 0.014796 | 0.051554 | 0.0066202 | 0.0014783 | 0.00649 | -0.0040118 | 0.0069425 | -0.0012946 | 0.0061374 | -0.00070919 | -0.0072759 | 0.017543 | -0.032043 | -0.064087 | -0.064087 | 0.045776 | 0.1831 | -0.082397 | -0.21057 | -0.073242 | -0.091553 | -0.20142 | 0.082397 | 0.082397 | -0.09613 | -0.15106 | 0.11902 | -0.009155 | -120.4788 | 0.13733 | 0.24719 | 0.25635 | -120.694 | 0.10529 | 0.050354 | -120.5795 | 0.12817 | 0 | -0.050354 | -120.5795 | 0.38452 | 0.16937 | 0.13733 | -120.8725 | 0.28381 | 0.28381 | 0.10986 | -120.813
3069.4531 | 120.9045 | -0.14648 | 120.6848 | -0.00099167 | 0.016077 | 0.054758 | 0.0074746 | 0.0021191 | 0.0011494 | -0.0046526 | 0.0069425 | -0.00065364 | 0.0074192 | -0.003059 | -0.011335 | 0.018184 | -0.054932 | -0.041199 | -0.059509 | 0.041199 | 0.17395 | -0.068665 | -0.24261 | -0.073242 | -0.032043 | -0.15106 | 0.068665 | 0.073242 | -0.10071 | -0.17395 | 0.077819 | -0.096131 | -120.5109 | 0.10529 | 0.18768 | 0.28381 | -120.7397 | 0.045776 | -0.027466 | -120.6161 | 0.073242 | -0.004578 | 0.022888 | -120.6116 | 0.32043 | 0.091552 | 0.086975 | -120.9274 | 0.21515 | 0.21973 | 0.11444 | -120.8588
3071.1875 | 120.8359 | -0.1831 | 120.813 | -0.00099167 | 0.007746 | 0.056681 | 0.0023476 | 0.0025465 | -0.0035504 | -0.0042254 | 0.0069425 | -0.0062078 | 0.0054966 | -0.003059 | -0.011121 | 0.022456 | 0.009155 | 0.050354 | 0.036621 | 0.073242 | 0.14191 | -0.027466 | -0.16937 | -0.027466 | 0.032043 | -0.073242 | 0.045776 | 0.050354 | -0.073242 | -0.15106 | 0.15564 | 0.013732 | -120.6711 | 0.23346 | 0.25635 | 0.24261 | -120.8038 | 0.10986 | 0.032043 | -120.7672 | 0.15564 | 0.10986 | 0.07782 | -120.7626 | 0.32501 | 0.19226 | 0.21973 | -120.9824 | 0.22888 | 0.23346 | 0.21515 | -120.9641
3072.9531 | 120.8908 | -0.17853 | 120.8405 | -0.00099167 | 0.011378 | 0.055613 | 0.0085428 | 0.0025465 | -0.0035504 | -0.0052936 | -0.00068649 | -0.0059942 | 0.005283 | -0.001991 | -0.013471 | 0.019252 | 0 | 0.032043 | 0.036621 | 0.086975 | 0.1236 | -0.032043 | -0.19226 | -0.018311 | 0.027466 | -0.07782 | 0.050354 | 0.050354 | -0.073242 | -0.15106 | 0.14648 | -0.013733 | -120.7169 | 0.21057 | 0.2655 | 0.27924 | -120.8405 | 0.10529 | 0.027466 | -120.7901 | 0.16022 | 0.10071 | 0.073242 | -120.7901 | 0.30212 | 0.17853 | 0.21515 | -121.0327 | 0.22888 | 0.22888 | 0.20599 | -120.9915
3074.6562 | 121.0464 | -0.1236 | 120.8176 | 0.014267 | 0.012659 | 0.054972 | 0.0091836 | 0.0010511 | -0.002055 | -0.004439 | -0.00068649 | -0.007276 | 0.0057102 | -0.0017774 | -0.013258 | 0.017756 | 0.054932 | 0.11444 | 0.10986 | 0.12817 | 0.15106 | -0.032043 | -0.16479 | 0.059509 | 0.1236 | 0 | 0.041199 | 0.036621 | -0.07782 | -0.11444 | 0.091553 | -0.041199 | -120.6665 | 0.23804 | 0.25177 | 0.29297 | -120.7626 | 0.045776 | 0.009155 | -120.7764 | 0.1831 | 0.1236 | 0.11444 | -120.7809 | 0.27466 | 0.17853 | 0.23346 | -120.9824 | 0.16479 | 0.16022 | 0.24719 | -120.932
3076.4062 | 120.9457 | -0.19226 | 120.9091 | -0.0086212 | 0.009455 | 0.053904 | 0.003843 | 0.0014783 | -0.00013244 | -0.0057208 | -0.008316 | -0.0025762 | 0.0048556 | -0.0032728 | -0.0094123 | 0.018611 | 0.032043 | 0.045776 | 0.073242 | 0.091553 | 0.12817 | -0.013733 | -0.1831 | -0.004578 | 0.018311 | -0.073242 | 0.036621 | 0.050354 | -0.082397 | -0.14191 | 0.17853 | 0.009156 | -120.7809 | 0.23804 | 0.28381 | 0.27466 | -120.8771 | 0.10986 | 0.050354 | -120.8725 | 0.18768 | 0.11902 | 0.068665 | -120.8588 | 0.32044 | 0.2243 | 0.2655 | -121.0922 | 0.22888 | 0.24261 | 0.21057 | -121.051
3078.1562 | 121.0373 | -0.16937 | 120.9274 | 0.0066373 | 0.013941 | 0.053904 | 0.0059792 | 0.0029737 | 0.004781 | -0.0052936 | 0.0069425 | -0.00086724 | 0.006351 | -0.00049559 | -0.0081305 | 0.017756 | 0.009155 | -0.036621 | -0.027466 | 0.050354 | 0.16937 | -0.054932 | -0.19684 | -0.009155 | -0.013733 | -0.10529 | 0.059509 | 0.054932 | -0.091553 | -0.13275 | 0.11444 | -0.027465 | -120.7581 | 0.13275 | 0.21973 | 0.24719 | -120.9183 | 0.07782 | 0.036622 | -120.8679 | 0.16022 | 0.064087 | 0.027465 | -120.8725 | 0.33875 | 0.17853 | 0.14191 | -121.1243 | 0.22888 | 0.22431 | 0.15564 | -121.0602
3079.9219 | 121.0968 | -0.16937 | 120.9229 | -0.0086212 | 0.012446 | 0.053476 | 0.007261 | 0.0040417 | -0.00077324 | -0.0031574 | -0.00068649 | -0.0044988 | 0.0074192 | -0.0022046 | -0.014112 | 0.019679 | 0.045776 | 0.086975 | 0.073242 | 0.10529 | 0.15564 | -0.041199 | -0.1831 | -0.013733 | 0.068665 | -0.082397 | 0.054932 | 0.054932 | -0.086975 | -0.14648 | 0.12817 | -0.013732 | -120.7672 | 0.25635 | 0.27466 | 0.28839 | -120.8771 | 0.082398 | 0.022889 | -120.8679 | 0.15564 | 0.086976 | 0.064087 | -120.8679 | 0.32501 | 0.21515 | 0.24261 | -121.106 | 0.22431 | 0.22431 | 0.23804 | -121.0693
3081.6875 | 121.1655 | -0.12817 | 120.932 | -0.0086212 | 0.011805 | 0.055613 | 0.0074746 | 0.0036145 | -0.00055964 | -0.0052936 | -0.00068649 | -0.007276 | 0.0074192 | -0.0041272 | -0.012617 | 0.020106 | 0.073242 | 0.11902 | 0.10071 | 0.13733 | 0.12817 | -0.041199 | -0.16937 | 0.027466 | 0.10071 | -0.013733 | 0.041199 | 0.050354 | -0.068665 | -0.1236 | 0.086975 | -0.041199 | -120.8038 | 0.24719 | 0.2655 | 0.3067 | -120.8588 | 0.059509 | 0.004578 | -120.8908 | 0.15564 | 0.11444 | 0.10986 | -120.8817 | 0.25635 | 0.20142 | 0.22888 | -121.1014 | 0.16937 | 0.17853 | 0.22888 | -121.0556
3083.375 | 121.0831 | -0.18768 | 120.9732 | 0.0066373 | 0.014155 | 0.051767 | 0.0040566 | 0.0014783 | 0.0022174 | -0.0052936 | -0.008316 | -0.00065364 | 0.003574 | -0.0026318 | -0.0057807 | 0.020106 | 0.004578 | 0 | -0.009155 | 0.068665 | 0.16937 | -0.045776 | -0.19226 | 0.018311 | 0.018311 | -0.07782 | 0.064087 | 0.045776 | -0.059509 | -0.13733 | 0.14191 | -0.004578 | -120.8038 | 0.18768 | 0.25635 | 0.26093 | -120.9686 | 0.12817 | 0.050354 | -120.9091 | 0.20599 | 0.10986 | 0.059509 | -120.9274 | 0.35706 | 0.19226 | 0.17853 | -121.1655 | 0.25177 | 0.23346 | 0.20599 | -121.1105
3085.125 | 121.1105 | -0.18768 | 121.0144 | -0.00099167 | 0.015223 | 0.054331 | 0.0064066 | 0.0027601 | 0.0060626 | -0.0042254 | 0.0069425 | 0.00020076 | 0.0059238 | -0.0017774 | -0.0068487 | 0.018184 | 0.059509 | 0.009155 | -0.022888 | 0.068665 | 0.16022 | -0.064087 | -0.19684 | -0.022888 | -0.022888 | -0.16479 | 0.073242 | 0.086975 | -0.091553 | -0.15106 | 0.1236 | -0.009155 | -120.8542 | 0.19684 | 0.25635 | 0.2655 | -120.9549 | 0.09613 | 0.036621 | -120.9412 | 0.16479 | 0.022888 | -0.013733 | -120.9274 | 0.3479 | 0.24719 | 0.16479 | -121.2112 | 0.26092 | 0.27466 | 0.16479 | -121.1655
3086.8906 | 121.1197 | -0.26093 | 120.9732 | -0.00099167 | 0.016505 | 0.053049 | 0.0064066 | 0.0012647 | 0.0039264 | -0.0012346 | 0.014572 | -0.0010808 | 0.0076328 | -0.003059 | -0.010053 | 0.019465 | -0.054932 | -0.086975 | -0.059509 | 0.041199 | 0.19226 | -0.050354 | -0.21515 | -0.068665 | -0.086975 | -0.18768 | 0.091553 | 0.068665 | -0.10071 | -0.15564 | 0.21057 | 0.045776 | -120.7809 | 0.17395 | 0.30212 | 0.25635 | -121.0281 | 0.16022 | 0.10529 | -120.8817 | 0.19226 | 0.073242 | -0.032043 | -120.9045 | 0.45319 | 0.20599 | 0.20142 | -121.1884 | 0.35248 | 0.32959 | 0.17395 | -121.1288
3088.5781 | 121.1288 | -0.26093 | 120.9869 | 0.014267 | 0.014155 | 0.053263 | 0.0057656 | 0.0023327 | 0.0034992 | -0.0025164 | -0.00068649 | -1.2844e-05 | 0.0078464 | -0.0013502 | -0.0083441 | 0.020533 | 0.018311 | 0.009155 | -0.009155 | 0.07782 | 0.17395 | -0.059509 | -0.21515 | -0.054932 | -0.004578 | -0.16479 | 0.068665 | 0.059509 | -0.091553 | -0.15564 | 0.20142 | 0.045776 | -120.813 | 0.27008 | 0.33875 | 0.29297 | -120.9686 | 0.16937 | 0.10529 | -120.9183 | 0.20599 | 0.09613 | -0.009155 | -120.9274 | 0.43488 | 0.27924 | 0.25177 | -121.2021 | 0.32959 | 0.32043 | 0.25635 | -121.1426
3090.3281 | 121.257 | -0.18768 | 121.0144 | 0.0066373 | 0.010309 | 0.055826 | 0.011106 | 0.0025465 | -0.0046184 | -0.0059344 | -0.008316 | -0.0070624 | 0.0057102 | -0.0032728 | -0.014539 | 0.020747 | 0.022888 | 0.12817 | 0.11444 | 0.12817 | 0.14191 | -0.004578 | -0.17395 | 0.027466 | 0.12817 | -0.022888 | 0.050354 | 0.050354 | -0.050354 | -0.12817 | 0.1831 | 0.013733 | -120.8725 | 0.31586 | 0.31586 | 0.30212 | -120.9915 | 0.13733 | 0.059509 | -120.9641 | 0.21515 | 0.16479 | 0.10529 | -120.9641 | 0.32959 | 0.21057 | 0.30212 | -121.1884 | 0.23804 | 0.23804 | 0.31586 | -121.1426
3092.0312 | 121.1243 | -0.23346 | 121.051 | -0.00099167 | 0.012018 | 0.052835 | 0.0061928 | 0.0036145 | 0.00050836 | -0.0048662 | 0.0069425 | -0.0062078 | 0.0072056 | -0.0015638 | -0.013044 | 0.01797 | 0.041199 | 0.082397 | 0.09613 | 0.11444 | 0.13275 | -0.027466 | -0.17395 | 0.027466 | 0.07782 | -0.036621 | 0.027466 | 0.041199 | -0.064087 | -0.13733 | 0.20599 | 0.059509 | -120.9183 | 0.31586 | 0.3479 | 0.28839 | -121.0098 | 0.16937 | 0.09613 | -121.0236 | 0.26093 | 0.19684 | 0.10071 | -121.0098 | 0.36621 | 0.27466 | 0.32959 | -121.225 | 0.26093 | 0.27466 | 0.31128 | -121.1884
3093.7812 | 121.3028 | -0.1831 | 121.0144 | -0.00099167 | 0.016505 | 0.053263 | 0.0093972 | 0.0012647 | 0.00414 | -0.0048662 | 0.014572 | -0.0012946 | 0.0078464 | -0.0017774 | -0.0094123 | 0.018184 | -0.050354 | -0.036621 | -0.045776 | 0.050354 | 0.19684 | -0.068665 | -0.23804 | -0.068665 | -0.009155 | -0.16937 | 0.09613 | 0.07782 | -0.10986 | -0.15564 | 0.11444 | -0.054932 | -120.8176 | 0.14648 | 0.23346 | 0.28839 | -121.0648 | 0.073242 | 0.027465 | -120.9183 | 0.11444 | 0.013732 | -0.013733 | -120.9366 | 0.37994 | 0.13275 | 0.13733 | -121.2524 | 0.27924 | 0.26092 | 0.17395 | -121.17
3095.5312 | 121.2753 | -0.2243 | 121.0602 | -0.00099167 | 0.014582 | 0.054758 | 0.01132 | 0.0016919 | 0.00093576 | -0.0057208 | 0.0069425 | -0.0047124 | 0.0065646 | -0.00070919 | -0.013044 | 0.019465 | -0.064087 | -0.036621 | -0.032043 | 0.032043 | 0.17853 | -0.073242 | -0.22888 | -0.086975 | -0.018311 | -0.15564 | 0.11902 | 0.086975 | -0.10529 | -0.16022 | 0.15106 | -0.004578 | -120.8817 | 0.18768 | 0.25635 | 0.26093 | -121.1243 | 0.11902 | 0.064087 | -120.9412 | 0.13733 | 0.068664 | 0.004577 | -120.9732 | 0.40283 | 0.16022 | 0.19226 | -121.2891 | 0.34332 | 0.31128 | 0.20599 | -121.2204
3097.2188 | 121.1563 | -0.25177 | 121.0602 | 0.0066373 | 0.007746 | 0.051767 | 0.0044838 | 0.0012647 | -0.002055 | -0.0055072 | 0.0069425 | -0.003858 | 0.0072056 | -0.0022046 | -0.010267 | 0.020106 | 0.013733 | 0.082397 | 0.068665 | 0.10071 | 0.13733 | -0.027466 | -0.16479 | 0.013733 | 0.041199 | -0.054932 | 0.036621 | 0.041199 | -0.073242 | -0.12817 | 0.2243 | 0.086975 | -120.9229 | 0.33417 | 0.35248 | 0.2655 | -121.0464 | 0.17853 | 0.1236 | -121.0236 | 0.2655 | 0.19684 | 0.073242 | -121.019 | 0.3891 | 0.2655 | 0.32044 | -121.225 | 0.28839 | 0.29297 | 0.29297 | -121.1884
3098.9688 | 121.2433 | -0.23346 | 121.0785 | 0.0066373 | 0.014368 | 0.052835 | 0.0046976 | 0.0034009 | 0.0039264 | -0.00508 | 0.0069425 | 0.00062796 | 0.0050694 | -0.0024182 | -0.0077033 | 0.01797 | -0.045776 | -0.07782 | -0.073242 | 0.032043 | 0.19226 | -0.059509 | -0.21515 | -0.054932 | -0.086975 | -0.17853 | 0.086975 | 0.082397 | -0.09613 | -0.16937 | 0.17395 | 0.01831 | -120.8862 | 0.15564 | 0.2655 | 0.24719 | -121.1243 | 0.13733 | 0.064086 | -120.9915 | 0.17853 | 0.054931 | -0.009155 | -120.9961 | 0.42572 | 0.18768 | 0.16022 | -121.2936 | 0.32043 | 0.31586 | 0.14648 | -121.2479
3100.6562 | 121.1884 | -0.22888 | 121.1472 | 0.0066373 | 0.011164 | 0.054117 | 0.0040566 | 0.0031873 | -0.0035504 | -0.0057208 | -0.008316 | -0.0040716 | 0.0042148 | -0.0026318 | -0.0085577 | 0.019893 | 0.041199 | 0.10529 | 0.07782 | 0.11902 | 0.1236 | -0.032043 | -0.18768 | 0.018311 | 0.07782 | -0.041199 | 0.041199 | 0.041199 | -0.064087 | -0.1236 | 0.19684 | 0.041199 | -121.0236 | 0.33417 | 0.3479 | 0.3067 | -121.106 | 0.16479 | 0.10529 | -121.106 | 0.24719 | 0.18768 | 0.082397 | -121.106 | 0.35248 | 0.27008 | 0.3067 | -121.3348 | 0.27008 | 0.27008 | 0.3067 | -121.2708
3102.4219 | 120.2316 | -82.8644 | 37.1292 | 0.0066373 | 0.0133 | 0.054331 | 0.0098244 | 0.0012647 | -0.00034604 | -0.006148 | -0.00068649 | -0.007276 | 0.0061374 | -0.0028454 | -0.011335 | 0.019893 | 0.050354 | 0.15564 | 0.13275 | 0.15564 | 0.16022 | 0.004578 | -0.14191 | 0.068665 | 0.14648 | 0.004578 | 0.086975 | 0.07782 | -0.022888 | -0.10529 | 82.869 | 82.7225 | -36.969 | 83.02 | 83.02 | 0.29755 | -37.0789 | 82.8415 | 82.7591 | -37.0422 | 82.933 | 82.869 | 0.10986 | -37.0514 | 83.0246 | 82.9147 | 82.9971 | -37.2711 | 82.9514 | 82.9422 | 83.0109 | -37.2345
3104.1719 | 120.6894 | -8.757 | 112.1979 | -0.0086212 | 0.011805 | 0.053476 | 0.0025612 | 0.0044691 | 0.0022174 | -0.00508 | 0.0069425 | -0.0032172 | 0.0031468 | -0.003059 | -0.0070623 | 0.016902 | 0.07782 | 0.082397 | 0.059509 | 0.12817 | 0.1236 | -0.027466 | -0.17853 | 0.064087 | 0.07782 | -0.027466 | 0.036621 | 0.045776 | -0.036621 | -0.10986 | 8.7296 | 8.5785 | -112.0743 | 8.8394 | 8.8852 | 0.3067 | -112.1201 | 8.7204 | 8.6472 | -112.1613 | 8.8211 | 8.7296 | 0.082397 | -112.1521 | 8.8806 | 8.8348 | 8.8165 | -112.3764 | 8.7936 | 8.8028 | 8.8348 | -112.3077
3105.9219 | 121.0693 | -7.8461 | 113.2004 | -0.00099167 | 0.014155 | 0.052622 | 0.010252 | 0.0029737 | -0.00034604 | -0.0065752 | -0.00068649 | -0.0027898 | 0.0057102 | -0.0051954 | -0.011762 | 0.022242 | 0.064087 | 0.11444 | 0.086975 | 0.12817 | 0.13733 | -0.013733 | -0.16937 | 0.041199 | 0.12817 | -0.018311 | 0.050354 | 0.045776 | -0.059509 | -0.11444 | 7.8323 | 7.6767 | -113.063 | 7.9605 | 7.9742 | 0.29755 | -113.1363 | 7.7866 | 7.7316 | -113.15 | 7.8873 | 7.8278 | 0.09613 | -113.1546 | 7.9834 | 7.9102 | 7.933 | -113.3698 | 7.8964 | 7.8918 | 7.9742 | -113.3148
3107.6875 | 121.019 | -7.3425 | 113.8458 | -0.00099167 | 0.014155 | 0.049845 | 0.0042702 | 0.0019055 | 0.004781 | -0.0048662 | -0.008316 | -1.2844e-05 | 0.006992 | 0.00014521 | -0.0091985 | 0.018184 | -0.041199 | -0.073242 | -0.07782 | 0.041199 | 0.20142 | -0.045776 | -0.21515 | -0.064087 | -0.09613 | -0.17853 | 0.086975 | 0.050354 | -0.091553 | -0.14191 | 7.2968 | 7.1274 | -113.6444 | 7.2693 | 7.3837 | 0.25635 | -113.887 | 7.251 | 7.2006 | -113.7589 | 7.2784 | 7.164 | -0.036621 | -113.7955 | 7.5439 | 7.3013 | 7.2647 | -114.061 | 7.4295 | 7.3929 | 7.2464 | -113.9877
3109.4375 | 121.1288 | -6.1478 | 114.9216 | 0.0066373 | 0.0133 | 0.055399 | 0.0079018 | 0.0031873 | -0.00077324 | -0.0059344 | -0.00068649 | -0.0017218 | 0.0076328 | -0.0026318 | -0.011976 | 0.019252 | -0.013733 | 0.022888 | 0.009155 | 0.086975 | 0.17395 | -0.045776 | -0.20599 | -0.059509 | -0.004578 | -0.12817 | 0.07782 | 0.07782 | -0.10986 | -0.16937 | 6.102 | 5.9418 | -114.7476 | 6.1707 | 6.2347 | 0.29297 | -114.9353 | 6.0379 | 5.9784 | -114.8438 | 6.0883 | 6.0196 | 0.041199 | -114.8438 | 6.3217 | 6.134 | 6.1569 | -115.1276 | 6.2256 | 6.2256 | 6.1432 | -115.0909
3111.125 | 121.17 | -6.2576 | 114.8804 | -0.00099167 | 0.013727 | 0.05369 | 0.010038 | 0.0025465 | -0.0018414 | -0.0059344 | -0.00068649 | -0.0059942 | 0.0091282 | -0.0024182 | -0.013471 | 0.020533 | 0.018311 | 0.09613 | 0.068665 | 0.11444 | 0.14648 | -0.041199 | -0.19226 | -0.022888 | 0.041199 | -0.082397 | 0.054932 | 0.054932 | -0.064087 | -0.14191 | 6.2164 | 6.0654 | -114.7339 | 6.3538 | 6.3721 | 0.3067 | -114.8621 | 6.1935 | 6.1157 | -114.8254 | 6.2347 | 6.1752 | 0.05951 | -114.8254 | 6.4041 | 6.2759 | 6.3263 | -115.0726 | 6.3126 | 6.3126 | 6.2988 | -115.0223
3112.8906 | 121.2112 | -6.1386 | 115.036 | -0.00099167 | 0.014368 | 0.053476 | 0.0057656 | 0.0034009 | 0.003072 | -0.0052936 | 0.014572 | -0.0019354 | 0.005283 | -0.00092279 | -0.0062079 | 0.01797 | 0.013733 | 0.036621 | -0.004578 | 0.073242 | 0.16479 | -0.045776 | -0.19684 | -0.022888 | 0.022888 | -0.12817 | 0.086975 | 0.059509 | -0.091553 | -0.15106 | 6.0928 | 5.9418 | -114.8712 | 6.1752 | 6.2119 | 0.27008 | -115.0223 | 6.0471 | 5.9875 | -114.949 | 6.1157 | 6.0104 | 0.022888 | -114.9765 | 6.3034 | 6.1523 | 6.134 | -115.2328 | 6.2256 | 6.1981 | 6.1615 | -115.1871
3114.6562 | 121.257 | -6.0471 | 115.0864 | 0.014267 | 0.0133 | 0.054758 | 0.0068338 | 0.0031873 | -0.0061138 | -0.0035846 | 0.0069425 | -0.0070624 | 0.0059238 | -0.005409 | -0.011121 | 0.019465 | 0.054932 | 0.13733 | 0.11902 | 0.12817 | 0.16022 | -0.027466 | -0.16937 | 0.032043 | 0.13275 | -0.009155 | 0.054932 | 0.050354 | -0.050354 | -0.10986 | 6.0196 | 5.8777 | -114.9261 | 6.1844 | 6.1752 | 0.29755 | -115.0314 | 5.9967 | 5.9372 | -115.0314 | 6.0791 | 6.0379 | 0.10071 | -115.036 | 6.2073 | 6.102 | 6.1661 | -115.2557 | 6.102 | 6.0974 | 6.1798 | -115.1962
3116.3438 | 121.2708 | -6.0287 | 115.155 | -0.00099167 | 0.010096 | 0.055826 | 0.0087564 | 0.0019055 | -0.0016278 | -0.0074298 | 0.0069425 | -0.0040716 | 0.004642 | -0.004768 | -0.013471 | 0.019679 | -0.004578 | 0.054932 | 0.036621 | 0.09613 | 0.15564 | -0.050354 | -0.17395 | 0.009155 | 0.086975 | -0.027466 | 0.054932 | 0.054932 | -0.064087 | -0.1236 | 5.9784 | 5.8548 | -114.9994 | 6.0837 | 6.1249 | 0.27008 | -115.1596 | 5.9647 | 5.9052 | -115.1001 | 6.0379 | 6.0013 | 0.09613 | -115.1001 | 6.1844 | 6.0242 | 6.0654 | -115.329 | 6.0837 | 6.0837 | 6.1157 | -115.2786
3118.0938 | 121.1792 | -6.0562 | 115.2054 | 0.021896 | 0.014155 | 0.053263 | 0.0049112 | 0.0031873 | 0.0037128 | -0.003371 | 0.014572 | -0.00065364 | 0.00806 | -0.0024182 | -0.0077033 | 0.017756 | -0.041199 | -0.082397 | -0.082397 | 0.032043 | 0.18768 | -0.041199 | -0.21057 | -0.059509 | -0.091553 | -0.1831 | 0.091553 | 0.073242 | -0.082397 | -0.15564 | 6.015 | 5.8456 | -115.0177 | 5.9738 | 6.0883 | 0.24261 | -115.2466 | 5.9738 | 5.9006 | -115.1138 | 5.9967 | 5.8731 | -0.027465 | -115.1321 | 6.2439 | 6.015 | 5.9738 | -115.416 | 6.1478 | 6.1295 | 5.9647 | -115.361
3119.8594 | 121.312 | -5.9692 | 115.242 | -0.016251 | 0.01095 | 0.051126 | 0.0076882 | 0.0034009 | -0.0050458 | -0.004439 | 0.0069425 | -0.0068488 | 0.006992 | -0.0043408 | -0.013471 | 0.021174 | -0.022888 | 0.045776 | 0.045776 | 0.10071 | 0.15106 | -0.027466 | -0.16479 | 0.004578 | 0.068665 | -0.022888 | 0.059509 | 0.054932 | -0.091553 | -0.12817 | 5.9418 | 5.8044 | -115.0909 | 6.015 | 6.0699 | 0.2655 | -115.2649 | 5.8777 | 5.8411 | -115.1825 | 5.9738 | 5.9463 | 0.10529 | -115.1871 | 6.1203 | 5.9463 | 6.015 | -115.4068 | 6.0287 | 6.0242 | 6.0379 | -115.3702
3121.6094 | 121.2936 | -6.0287 | 115.2283 | -0.00099167 | 0.017145 | 0.052195 | 0.0081154 | 0.0019055 | 0.0054218 | -0.0040118 | -0.00068649 | -0.00086724 | 0.0078464 | -0.003059 | -0.0070623 | 0.016688 | 0.032043 | 0.027466 | 0.009155 | 0.091553 | 0.19226 | -0.059509 | -0.20142 | -0.013733 | 0.022888 | -0.14191 | 0.073242 | 0.054932 | -0.082397 | -0.14648 | 5.9692 | 5.8273 | -115.036 | 6.0562 | 6.1203 | 0.29297 | -115.1962 | 5.9464 | 5.8823 | -115.155 | 6.015 | 5.8868 | 0.004577 | -115.1733 | 6.221 | 6.0608 | 6.0379 | -115.4297 | 6.102 | 6.0837 | 6.0516 | -115.3748
3123.3125 | 121.2204 | -6.189 | 115.1688 | -0.00099167 | 0.013727 | 0.053476 | 0.0064066 | 0.0034009 | 0.0037128 | -0.0037982 | 0.0069425 | 0.0014826 | 0.0054966 | -0.0015638 | -0.0068487 | 0.019465 | -0.022888 | -0.041199 | -0.073242 | 0.045776 | 0.17395 | -0.059509 | -0.19684 | -0.082397 | -0.068665 | -0.19684 | 0.082397 | 0.082397 | -0.10071 | -0.16479 | 6.1295 | 5.9921 | -114.9948 | 6.1478 | 6.2347 | 0.24261 | -115.1916 | 6.0883 | 6.0242 | -115.0864 | 6.1066 | 5.9921 | -0.032043 | -115.0864 | 6.3629 | 6.1661 | 6.1157 | -115.3656 | 6.2714 | 6.2714 | 6.1203 | -115.3336
3125.0781 | 121.2708 | -6.0745 | 115.2237 | 0.0066373 | 0.014582 | 0.052622 | 0.0061928 | 0.0019055 | 0.0034992 | -0.003371 | 0.0069425 | -0.00044004 | 0.006351 | -0.0032728 | -0.0062079 | 0.020106 | 0.009155 | 0.018311 | -0.009155 | 0.07782 | 0.17395 | -0.054932 | -0.20599 | -0.036621 | -0.004578 | -0.14191 | 0.064087 | 0.07782 | -0.091553 | -0.14191 | 6.0196 | 5.8685 | -115.0497 | 6.0928 | 6.1523 | 0.28381 | -115.2145 | 5.983 | 5.9326 | -115.1596 | 6.0379 | 5.9326 | 0 | -115.1459 | 6.2485 | 6.0837 | 6.0654 | -115.4297 | 6.1386 | 6.1523 | 6.0699 | -115.3656
3126.7656 | 121.344 | -5.9921 | 115.2649 | 0.0066373 | 0.0133 | 0.052622 | 0.0091836 | 0.0019055 | 0.0043536 | -0.0046526 | -0.00068649 | -1.2844e-05 | 0.0084872 | -0.0017774 | -0.010267 | 0.018824 | 0.009155 | 0.036621 | -0.009155 | 0.09613 | 0.16937 | -0.036621 | -0.21515 | -0.036621 | 0.027466 | -0.1236 | 0.082397 | 0.073242 | -0.07782 | -0.14648 | 5.9555 | 5.777 | -115.0955 | 6.0287 | 6.0883 | 0.31128 | -115.2557 | 5.9143 | 5.8456 | -115.1825 | 5.9555 | 5.8685 | 0.022888 | -115.1917 | 6.1615 | 6.0013 | 5.983 | -115.48 | 6.0745 | 6.0654 | 6.0196 | -115.4114
3128.5312 | 121.3348 | -5.8823 | 115.4205 | -0.0086212 | 0.015009 | 0.053476 | 0.012388 | 0.0029737 | -0.0039776 | -0.00508 | 0.0069425 | -0.005567 | 0.005283 | -0.0028454 | -0.015821 | 0.022242 | 0.004578 | 0.068665 | 0.050354 | 0.10071 | 0.15564 | -0.041199 | -0.19226 | -0.041199 | 0.032043 | -0.09613 | 0.082397 | 0.073242 | -0.09613 | -0.14648 | 5.8411 | 5.69 | -115.2649 | 5.9509 | 5.983 | 0.29297 | -115.416 | 5.7861 | 5.7358 | -115.3381 | 5.8411 | 5.7861 | 0.050354 | -115.3473 | 6.0379 | 5.8868 | 5.9326 | -115.6128 | 5.9647 | 5.9555 | 5.9143 | -115.567
3130.2656 | 121.3165 | -5.9418 | 115.4388 | -0.00099167 | 0.012659 | 0.051981 | 0.0036294 | 0.0019055 | 0.0034992 | -0.0059344 | 0.014572 | -0.0012946 | 0.0044284 | -0.00092279 | -0.010053 | 0.021388 | -0.041199 | -0.073242 | -0.054932 | 0.041199 | 0.19226 | -0.064087 | -0.20142 | -0.059509 | -0.059509 | -0.15106 | 0.091553 | 0.10071 | -0.086975 | -0.16479 | 5.8777 | 5.7404 | -115.2466 | 5.8685 | 5.983 | 0.24262 | -115.48 | 5.8548 | 5.777 | -115.3473 | 5.8823 | 5.7907 | 0.013733 | -115.3381 | 6.134 | 5.9006 | 5.8868 | -115.6403 | 6.0333 | 6.0425 | 5.8823 | -115.6036
3131.9531 | 121.2891 | -5.9509 | 115.3885 | 0.014267 | 0.0075324 | 0.054972 | 0.005552 | 0.0055371 | -0.0063274 | -0.0046526 | -0.00068649 | -0.0057806 | 0.0044284 | -0.0043408 | -0.012189 | 0.020533 | -0.018311 | 0.036621 | 0.036621 | 0.07782 | 0.15564 | -0.032043 | -0.17853 | -0.027466 | 0.036621 | -0.050354 | 0.054932 | 0.036621 | -0.082397 | -0.1236 | 5.9189 | 5.7724 | -115.2328 | 5.9875 | 6.0287 | 0.25635 | -115.4068 | 5.8685 | 5.8273 | -115.3336 | 5.9235 | 5.9006 | 0.073242 | -115.3519 | 6.1066 | 5.9326 | 5.9875 | -115.567 | 6.0059 | 5.9875 | 5.9875 | -115.5121
3133.7188 | 121.2708 | -5.8594 | 115.5029 | 0.014267 | 0.0133 | 0.053049 | 0.0059792 | 0.0021191 | -0.002055 | -0.00508 | -0.00068649 | -0.0032172 | 0.0050694 | -0.0041272 | -0.010908 | 0.021174 | 0.050354 | 0.07782 | 0.082397 | 0.11444 | 0.15564 | -0.013733 | -0.17395 | 0.013733 | 0.050354 | -0.036621 | 0.045776 | 0.045776 | -0.059509 | -0.13733 | 5.8456 | 5.6854 | -115.3473 | 5.9372 | 5.9738 | 0.28839 | -115.4526 | 5.7999 | 5.722 | -115.4572 | 5.8731 | 5.8228 | 0.10071 | -115.4572 | 6.015 | 5.9097 | 5.9418 | -115.6769 | 5.9052 | 5.9052 | 5.9097 | -115.6403
3135.4688 | 121.3531 | -5.928 | 115.4388 | -0.00099167 | 0.0133 | 0.054331 | 0.0049112 | 0.0031873 | 0.0017902 | -0.00508 | -0.008316 | -0.0019354 | 0.004642 | -0.0026318 | -0.0083441 | 0.018611 | 0.009155 | 0.013733 | 0.013733 | 0.073242 | 0.16022 | -0.032043 | -0.17395 | 0.027466 | 0.027466 | -0.059509 | 0.054932 | 0.041199 | -0.059509 | -0.10986 | 5.896 | 5.7541 | -115.2786 | 5.9418 | 6.0013 | 0.24719 | -115.4297 | 5.8685 | 5.8182 | -115.3839 | 5.9555 | 5.8685 | 0.050354 | -115.3976 | 6.0883 | 5.9372 | 5.9418 | -115.6128 | 5.983 | 5.9692 | 5.9555 | -115.5487
3137.2344 | 121.4447 | -5.8594 | 115.4434 | -0.00099167 | 0.012232 | 0.055399 | 0.00897 | -0.00023074 | -0.0035504 | -0.0082842 | -0.00068649 | -0.0049262 | 0.0061374 | -0.0022046 | -0.015394 | 0.01797 | 0.064087 | 0.1236 | 0.09613 | 0.1236 | 0.14648 | -0.027466 | -0.17853 | 0.027466 | 0.12817 | -0.013733 | 0.050354 | 0.050354 | -0.045776 | -0.11902 | 5.8319 | 5.6808 | -115.2969 | 5.983 | 5.983 | 0.30212 | -115.3793 | 5.8136 | 5.7404 | -115.3931 | 5.8868 | 5.8456 | 0.10529 | -115.3931 | 6.0059 | 5.9235 | 5.9555 | -115.6219 | 5.9097 | 5.9097 | 5.9875 | -115.5624
3138.9375 | 121.4172 | -5.8777 | 115.4892 | -0.016251 | 0.011591 | 0.052408 | 0.010679 | 0.0019055 | -0.0014142 | -0.007857 | 0.0069425 | -0.0040716 | 0.008701 | -0.003059 | -0.011976 | 0.017543 | 0.032043 | 0.073242 | 0.073242 | 0.13275 | 0.13733 | -0.036621 | -0.18768 | -0.036621 | 0.059509 | -0.07782 | 0.07782 | 0.045776 | -0.10071 | -0.14191 | 5.8411 | 5.69 | -115.3519 | 5.9509 | 6.0104 | 0.32043 | -115.4572 | 5.777 | 5.7358 | -115.4114 | 5.8411 | 5.7999 | 0.064087 | -115.4434 | 6.015 | 5.9097 | 5.9509 | -115.6769 | 5.9555 | 5.9235 | 5.9372 | -115.6311
3140.6875 | 121.344 | -5.8823 | 115.5716 | -0.0086212 | 0.014155 | 0.052835 | 0.0059792 | 0.0040417 | 0.0039264 | -0.0040118 | -0.00068649 | -0.00044004 | 0.0074192 | -0.0017774 | -0.0062079 | 0.014552 | -0.027466 | -0.086975 | -0.091553 | 0.041199 | 0.1831 | -0.059509 | -0.20142 | -0.073242 | -0.082397 | -0.17853 | 0.082397 | 0.082397 | -0.07782 | -0.15564 | 5.8228 | 5.6808 | -115.3885 | 5.7953 | 5.9235 | 0.24262 | -115.5991 | 5.8044 | 5.7266 | -115.4892 | 5.809 | 5.7037 | -0.022888 | -115.4892 | 6.0654 | 5.8548 | 5.7907 | -115.773 | 5.9647 | 5.9647 | 5.7999 | -115.7272
3142.375 | 121.3577 | -6.0516 | 115.3793 | -0.00099167 | 0.0090278 | 0.05604 | 0.0053384 | 0.00062386 | -0.0033368 | -0.00508 | 0.0069425 | -0.0044988 | 0.0054966 | -0.0039136 | -0.012403 | 0.021174 | 0.004578 | 0.045776 | 0.041199 | 0.091553 | 0.15106 | -0.022888 | -0.17395 | -0.013733 | 0.027466 | -0.064087 | 0.073242 | 0.064087 | -0.07782 | -0.11444 | 6.0287 | 5.8777 | -115.2283 | 6.0974 | 6.1432 | 0.2655 | -115.3748 | 5.9738 | 5.9372 | -115.3061 | 6.0379 | 5.9875 | 0.050354 | -115.3152 | 6.2027 | 6.0562 | 6.0928 | -115.5533 | 6.1249 | 6.1157 | 6.0791 | -115.4938
3144.125 | 121.4859 | -5.8319 | 115.5304 | 0.014267 | 0.0133 | 0.053049 | 0.0081154 | 0.0059643 | 0.0028584 | -0.0048662 | 0.0069425 | -0.002149 | 0.008701 | -0.0039136 | -0.010267 | 0.018184 | -0.045776 | -0.041199 | -0.054932 | 0.064087 | 0.19684 | -0.091553 | -0.23346 | -0.064087 | -0.018311 | -0.14648 | 0.091553 | 0.086975 | -0.10071 | -0.17395 | 5.7404 | 5.5984 | -115.3336 | 5.7907 | 5.896 | 0.29755 | -115.5762 | 5.7312 | 5.658 | -115.4388 | 5.7678 | 5.6854 | 0.027466 | -115.4434 | 6.0287 | 5.7861 | 5.777 | -115.7639 | 5.9235 | 5.9189 | 5.8136 | -115.7043
3145.875 | 121.5042 | -5.928 | 115.4388 | -0.0086212 | 0.014155 | 0.053476 | 0.007261 | 0.0046827 | -0.003764 | -0.0042254 | -0.00068649 | -0.0068488 | 0.0067782 | -0.0032728 | -0.010908 | 0.018824 | 0.059509 | 0.13733 | 0.10529 | 0.13733 | 0.14191 | -0.018311 | -0.16937 | 0.032043 | 0.11902 | -0.013733 | 0.054932 | 0.041199 | -0.068665 | -0.10986 | 5.9097 | 5.7587 | -115.2969 | 6.0654 | 6.0654 | 0.3067 | -115.3793 | 5.8594 | 5.8182 | -115.3839 | 5.9601 | 5.9143 | 0.09613 | -115.3976 | 6.0699 | 5.9875 | 6.0333 | -115.6082 | 5.983 | 5.9692 | 6.0471 | -115.5487
3147.6406 | 121.4035 | -6.0379 | 115.4205 | 0.0066373 | 0.0081732 | 0.052195 | 0.0053384 | 0.0027601 | -0.0024822 | -0.0070026 | -0.00068649 | -0.0068488 | 0.0054966 | -0.0022046 | -0.010694 | 0.018611 | 0 | 0.022888 | 0.032043 | 0.082397 | 0.15106 | -0.032043 | -0.19684 | -0.004578 | 0.018311 | -0.068665 | 0.050354 | 0.054932 | -0.082397 | -0.12817 | 6.0059 | 5.8411 | -115.2695 | 6.0608 | 6.1203 | 0.27924 | -115.4205 | 5.9555 | 5.9097 | -115.3702 | 6.0333 | 5.9692 | 0.059509 | -115.3656 | 6.189 | 6.0379 | 6.0699 | -115.6174 | 6.0883 | 6.0928 | 6.0562 | -115.5487
3149.3906 | 121.4401 | -5.9921 | 115.4572 | -0.0086212 | 0.013514 | 0.05134 | 0.0044838 | 0.0014783 | 0.004781 | -0.0055072 | -0.00068649 | -0.002149 | 0.0061374 | -0.00092279 | -0.0072759 | 0.019679 | -0.004578 | -0.064087 | -0.064087 | 0.036621 | 0.20599 | -0.050354 | -0.19684 | -0.041199 | -0.059509 | -0.14648 | 0.091553 | 0.082397 | -0.091553 | -0.13733 | 5.9418 | 5.7953 | -115.2512 | 5.928 | 6.0287 | 0.23346 | -115.4617 | 5.9006 | 5.8548 | -115.3656 | 5.9509 | 5.8456 | -0.009155 | -115.3748 | 6.1981 | 5.9875 | 5.928 | -115.654 | 6.0837 | 6.0745 | 5.9326 | -115.5945
3151.1562 | 121.5454 | -6.0059 | 115.3793 | 0.0066373 | 0.012873 | 0.053904 | 0.0070474 | 0.0044691 | 0.0015766 | -0.0065752 | -0.00068649 | -0.0025762 | 0.0050694 | -0.0026318 | -0.0068487 | 0.015834 | -0.027466 | -0.045776 | -0.045776 | 0.054932 | 0.1831 | -0.073242 | -0.23346 | -0.059509 | -0.018311 | -0.14648 | 0.10986 | 0.09613 | -0.091553 | -0.16022 | 5.9326 | 5.7724 | -115.1962 | 5.9601 | 6.0608 | 0.28839 | -115.4068 | 5.9143 | 5.8456 | -115.2695 | 5.9463 | 5.8594 | 0.013733 | -115.2832 | 6.189 | 5.9784 | 5.9601 | -115.6128 | 6.1157 | 6.102 | 5.9875 | -115.5396
3152.8594 | 121.4767 | -5.9601 | 115.4892 | -0.0086212 | 0.0068916 | 0.05604 | 0.0057656 | 0.00083746 | -0.0031232 | -0.0059344 | 0.014572 | -0.0085576 | 0.0067782 | -0.0037 | -0.012617 | 0.020106 | -0.027466 | 0.027466 | 0.032043 | 0.082397 | 0.15106 | -0.027466 | -0.17395 | 0 | 0.036621 | -0.054932 | 0.068665 | 0.050354 | -0.068665 | -0.11444 | 5.9326 | 5.7861 | -115.3381 | 5.9875 | 6.0425 | 0.25635 | -115.5167 | 5.8914 | 5.8456 | -115.4205 | 5.9601 | 5.9052 | 0.059509 | -115.4388 | 6.1111 | 5.9326 | 5.9921 | -115.6631 | 6.0287 | 6.0104 | 5.9967 | -115.6036
3154.6094 | 121.4767 | -5.9738 | 115.4526 | 0.0066373 | 0.0098822 | 0.054544 | 0.0064066 | 0.0010511 | -0.0016278 | -0.007857 | -0.015945 | -0.0057806 | 0.0048556 | -0.0026318 | -0.01283 | 0.019038 | -0.013733 | 0.004578 | 0.032043 | 0.086975 | 0.15564 | -0.027466 | -0.19684 | -0.009155 | 0.041199 | -0.064087 | 0.059509 | 0.054932 | -0.064087 | -0.11444 | 5.9463 | 5.777 | -115.2969 | 5.9784 | 6.0608 | 0.28381 | -115.4663 | 5.9097 | 5.8594 | -115.3931 | 5.9647 | 5.9097 | 0.050354 | -115.3976 | 6.1295 | 5.9601 | 6.0059 | -115.6494 | 6.0333 | 6.0287 | 6.015 | -115.567
3156.2969 | 121.4127 | -6.0196 | 115.4755 | -0.00099167 | 0.011591 | 0.054117 | 0.0042702 | 0.0019055 | 0.002431 | -0.0029436 | 0.014572 | -0.0036444 | 0.004642 | -0.0034864 | -0.0081305 | 0.019465 | 0.073242 | 0.086975 | 0.091553 | 0.14648 | 0.13275 | 0 | -0.17853 | 0.041199 | 0.082397 | -0.032043 | 0.050354 | 0.022888 | -0.054932 | -0.11444 | 6.0196 | 5.8411 | -115.3427 | 6.1066 | 6.1661 | 0.32501 | -115.4022 | 5.9647 | 5.9052 | -115.4251 | 6.0608 | 5.9875 | 0.082398 | -115.4526 | 6.1523 | 6.0928 | 6.1111 | -115.654 | 6.0699 | 6.0425 | 6.102 | -115.5899
3158.0625 | 121.431 | -6.0287 | 115.4434 | -0.00099167 | 0.009455 | 0.054972 | 0.0076882 | 0.00041006 | 0.00050836 | -0.0055072 | 0.0069425 | -0.0062078 | 0.0061374 | -0.005409 | -0.012189 | 0.021601 | 0 | 0.018311 | 0.036621 | 0.07782 | 0.17853 | -0.036621 | -0.16937 | 0.009155 | 0.032043 | -0.059509 | 0.050354 | 0.054932 | -0.068665 | -0.13275 | 5.9921 | 5.8594 | -115.2649 | 6.0471 | 6.1066 | 0.24719 | -115.4434 | 5.9601 | 5.896 | -115.3931 | 6.0379 | 5.9692 | 0.073242 | -115.3885 | 6.2073 | 6.0287 | 6.0654 | -115.6128 | 6.0791 | 6.0837 | 6.0608 | -115.5762
3159.8281 | 121.4493 | -6.0745 | 115.4251 | -0.00099167 | 0.011805 | 0.052622 | 0.0057656 | 0.0029737 | 0.0028584 | -0.0046526 | -0.00068649 | -0.0019354 | 0.0057102 | -0.0022046 | -0.0070623 | 0.018824 | 0.09613 | 0.082397 | 0.086975 | 0.1236 | 0.14191 | -0.004578 | -0.16937 | 0.059509 | 0.068665 | -0.032043 | 0.050354 | 0.036621 | -0.050354 | -0.1236 | 6.0699 | 5.9052 | -115.2832 | 6.1569 | 6.1981 | 0.29297 | -115.329 | 6.0242 | 5.9509 | -115.3748 | 6.134 | 6.0425 | 0.091553 | -115.3885 | 6.2164 | 6.1707 | 6.1615 | -115.5945 | 6.1249 | 6.1111 | 6.1432 | -115.5487
3161.5781 | 121.4401 | -6.0471 | 115.4572 | 0.0066373 | 0.015436 | 0.049204 | 0.0068338 | 0.0029737 | 0.0079852 | -0.0042254 | -0.00068649 | -0.00044004 | 0.006351 | -0.0024182 | -0.0085577 | 0.015193 | 0.032043 | 0.013733 | -0.009155 | 0.07782 | 0.17853 | -0.041199 | -0.20142 | -0.018311 | -0.009155 | -0.16479 | 0.091553 | 0.064087 | -0.10529 | -0.14191 | 6.0059 | 5.8456 | -115.2786 | 6.0608 | 6.1249 | 0.27924 | -115.4251 | 5.9418 | 5.9052 | -115.3656 | 6.0287 | 5.8823 | -0.022888 | -115.3931 | 6.2256 | 6.0791 | 6.0379 | -115.6586 | 6.1386 | 6.1111 | 6.0379 | -115.5991
3163.2812 | 121.2524 | -86.8698 | 33.8425 | -0.00099167 | 0.010309 | 0.054331 | 0.010252 | 0.0029737 | -0.0048322 | -0.00508 | -0.00068649 | -0.0064214 | 0.0082736 | -0.0049816 | -0.01283 | 0.020533 | 0.050354 | 0.13275 | 0.10986 | 0.15564 | 0.17395 | -0.009155 | -0.15564 | 0.073242 | 0.14191 | 0.032043 | 0.073242 | 0.073242 | -0.036621 | -0.082397 | 86.8607 | 86.7142 | -33.6685 | 87.0026 | 87.0255 | 0.31128 | -33.7921 | 86.8332 | 86.7874 | -33.7692 | 86.9431 | 86.9019 | 0.11444 | -33.7692 | 87.0438 | 86.9202 | 86.9797 | -33.9981 | 86.9431 | 86.9431 | 87.0117 | -33.9249
3165.0469 | 120.9503 | -10.9222 | 110.5179 | -0.00099167 | 0.014796 | 0.052408 | 0.0046976 | 0.0023327 | 0.0052082 | -0.0029436 | 0.0069425 | -0.00065364 | 0.00806 | -0.00049559 | -0.0068487 | 0.016688 | -0.009155 | -0.013733 | -0.036621 | 0.054932 | 0.17853 | -0.050354 | -0.21515 | -0.059509 | -0.045776 | -0.1831 | 0.09613 | 0.073242 | -0.10071 | -0.15106 | 10.8719 | 10.7071 | -110.3394 | 10.9085 | 10.9772 | 0.27008 | -110.527 | 10.8215 | 10.7712 | -110.4218 | 10.8627 | 10.7391 | -0.032043 | -110.4446 | 11.1008 | 10.9131 | 10.8856 | -110.733 | 11.0184 | 10.9955 | 10.8765 | -110.6689
3166.7344 | 121.3852 | -7.3425 | 114.0106 | 0.014267 | 0.014155 | 0.05134 | 0.005552 | 0.0025465 | 0.004781 | -0.0031574 | 0.0069425 | -0.0015082 | 0.0084872 | -0.0011364 | -0.0094123 | 0.017543 | 0.009155 | 0.041199 | 0.004578 | 0.086975 | 0.1831 | -0.068665 | -0.20142 | -0.022888 | 0.032043 | -0.12817 | 0.086975 | 0.054932 | -0.091553 | -0.13733 | 7.2739 | 7.1411 | -113.8275 | 7.3837 | 7.4295 | 0.28839 | -114.0015 | 7.251 | 7.2052 | -113.9236 | 7.3196 | 7.2144 | 0.009155 | -113.9557 | 7.5256 | 7.3517 | 7.3471 | -114.212 | 7.4295 | 7.3975 | 7.3746 | -114.1479
3168.5 | 121.344 | -6.6742 | 114.7659 | -0.00099167 | 0.0090278 | 0.056681 | 0.0068338 | 0.0027601 | -0.005473 | -0.0042254 | -0.00068649 | -0.0059942 | 0.0044284 | -0.0037 | -0.012403 | 0.022242 | -0.027466 | 0.054932 | 0.032043 | 0.082397 | 0.15106 | -0.036621 | -0.17853 | -0.004578 | 0.032043 | -0.064087 | 0.068665 | 0.041199 | -0.091553 | -0.11902 | 6.6376 | 6.4957 | -114.6149 | 6.7291 | 6.7566 | 0.26092 | -114.7934 | 6.5826 | 6.5552 | -114.6973 | 6.6696 | 6.6101 | 0.054932 | -114.7247 | 6.8253 | 6.6467 | 6.7062 | -114.9445 | 6.7429 | 6.7154 | 6.7062 | -114.8849
3170.25 | 121.3623 | -7.4844 | 113.9465 | 0.0066373 | 0.011805 | 0.050699 | 0.0057656 | 0.0034009 | 0.00093576 | -0.0023028 | 0.014572 | -0.0025762 | 0.0061374 | -0.0041272 | -0.011121 | 0.018184 | 0.064087 | 0.091553 | 0.073242 | 0.12817 | 0.13733 | -0.022888 | -0.17395 | 0.064087 | 0.082397 | -0.022888 | 0.054932 | 0.027466 | -0.054932 | -0.11902 | 7.4615 | 7.3105 | -113.8092 | 7.576 | 7.6126 | 0.30212 | -113.8824 | 7.4295 | 7.3654 | -113.8916 | 7.5485 | 7.4615 | 0.096131 | -113.9191 | 7.6218 | 7.5485 | 7.5577 | -114.1205 | 7.5394 | 7.5119 | 7.5668 | -114.0656
3171.9375 | 121.4127 | -7.338 | 114.1296 | 0.0066373 | 0.012018 | 0.052835 | 0.0059792 | 0.0036145 | 0.0032856 | -0.0029436 | -0.00068649 | -0.0023626 | 0.0082736 | -0.0015638 | -0.0089849 | 0.019038 | -0.009155 | -0.022888 | -0.009155 | 0.059509 | 0.16937 | -0.050354 | -0.20599 | 0.013733 | 0.009155 | -0.07782 | 0.054932 | 0.059509 | -0.064087 | -0.14191 | 7.2876 | 7.132 | -113.9603 | 7.3151 | 7.3975 | 0.2655 | -114.1388 | 7.2739 | 7.196 | -114.0747 | 7.3517 | 7.2601 | 0.064087 | -114.0701 | 7.5073 | 7.3288 | 7.3288 | -114.3356 | 7.3929 | 7.3975 | 7.3471 | -114.2715
3173.7031 | 121.4767 | -7.2739 | 114.1571 | -0.00099167 | 0.0083868 | 0.054972 | 0.0076882 | 0.00019646 | -0.0031232 | -0.0065752 | 0.0069425 | -0.0064214 | 0.0042148 | -0.0032728 | -0.01283 | 0.019679 | 0.004578 | 0.027466 | 0.027466 | 0.086975 | 0.14648 | -0.041199 | -0.1831 | -0.004578 | 0.064087 | -0.032043 | 0.064087 | 0.045776 | -0.068665 | -0.15106 | 7.2327 | 7.0908 | -114.0106 | 7.3013 | 7.3608 | 0.27008 | -114.1525 | 7.2052 | 7.1228 | -114.093 | 7.2693 | 7.2418 | 0.11902 | -114.1113 | 7.4203 | 7.2784 | 7.3013 | -114.3402 | 7.338 | 7.3196 | 7.338 | -114.3082
3175.3906 | 121.4127 | -7.5302 | 113.9877 | 0.0066373 | 0.015009 | 0.05369 | 0.0040566 | 0.0038281 | 0.0054218 | -0.0029436 | 0.0069425 | -0.0023626 | 0.005283 | -0.0022046 | -0.0077033 | 0.018611 | -0.013733 | -0.064087 | -0.07782 | 0.045776 | 0.17395 | -0.054932 | -0.20142 | -0.082397 | -0.054932 | -0.20142 | 0.086975 | 0.07782 | -0.11444 | -0.15564 | 7.4753 | 7.3288 | -113.8138 | 7.4661 | 7.576 | 0.24719 | -114.0015 | 7.4158 | 7.3746 | -113.9008 | 7.4478 | 7.3288 | -0.045776 | -113.9099 | 7.7042 | 7.5165 | 7.4524 | -114.1891 | 7.6172 | 7.608 | 7.4753 | -114.1434
3177.1562 | 121.4722 | -7.0999 | 114.3997 | 0.0066373 | 0.018 | 0.050058 | 0.0053384 | 0.0057507 | 0.0037128 | -0.0035846 | -0.00068649 | -0.00044004 | 0.0031468 | -0.001991 | -0.0079169 | 0.019038 | 0.022888 | 0.009155 | 0 | 0.068665 | 0.16479 | -0.032043 | -0.20142 | -0.054932 | -0.018311 | -0.16937 | 0.082397 | 0.082397 | -0.10071 | -0.14648 | 7.0679 | 6.8985 | -114.2349 | 7.1091 | 7.1686 | 0.27008 | -114.3768 | 6.9992 | 6.9534 | -114.3173 | 7.045 | 6.9305 | -0.022889 | -114.3173 | 7.2647 | 7.1228 | 7.0999 | -114.6011 | 7.1823 | 7.1823 | 7.0816 | -114.5462
3178.8594 | 121.463 | -7.2189 | 114.4318 | -0.0086212 | 0.01565 | 0.052622 | 0.0061928 | 0.0010511 | 0.0020038 | -0.0037982 | -0.00068649 | -0.0034308 | 0.006351 | -0.0022046 | -0.0094123 | 0.019893 | -0.032043 | -0.059509 | -0.064087 | 0.041199 | 0.17853 | -0.059509 | -0.19226 | -0.059509 | -0.050354 | -0.15106 | 0.09613 | 0.07782 | -0.091553 | -0.16022 | 7.1594 | 7.0267 | -114.2532 | 7.1594 | 7.2601 | 0.23346 | -114.4638 | 7.1274 | 7.0587 | -114.3356 | 7.1594 | 7.0679 | 0.009155 | -114.3539 | 7.3975 | 7.1869 | 7.1548 | -114.624 | 7.3151 | 7.2968 | 7.1686 | -114.592
3180.6094 | 120.7031 | -10.8994 | 109.6024 | 0.014267 | 0.015436 | 0.051767 | 0.007261 | 0.0021191 | 0.0037128 | -0.004439 | 0.0069425 | -0.0010808 | 0.0061374 | -0.001991 | -0.0070623 | 0.019465 | -0.004578 | -0.018311 | -0.027466 | 0.064087 | 0.17853 | -0.054932 | -0.21057 | -0.064087 | -0.041199 | -0.17395 | 0.10071 | 0.07782 | -0.09613 | -0.16022 | 10.8444 | 10.6888 | -109.4238 | 10.881 | 10.9634 | 0.27466 | -109.6069 | 10.8032 | 10.7391 | -109.5016 | 10.8353 | 10.7254 | -0.013733 | -109.5245 | 11.0779 | 10.8948 | 10.8719 | -109.8129 | 11.0001 | 10.9772 | 10.8582 | -109.7626
3182.3594 | 120.9 | -6.0837 | 115.1413 | 0.0066373 | 0.011591 | 0.054544 | 0.005552 | 0.0029737 | -0.0033368 | -0.0042254 | 0.014572 | -0.006635 | 0.0072056 | -0.003059 | -0.012403 | 0.020961 | 0.032043 | 0.086975 | 0.082397 | 0.10986 | 0.15106 | -0.013733 | -0.16479 | -0.009155 | 0.050354 | -0.036621 | 0.064087 | 0.045776 | -0.054932 | -0.1236 | 6.0699 | 5.9189 | -114.9902 | 6.1707 | 6.1935 | 0.27466 | -115.1093 | 6.0287 | 5.9601 | -115.0772 | 6.0745 | 6.0471 | 0.086975 | -115.0955 | 6.2347 | 6.1157 | 6.1661 | -115.3061 | 6.1478 | 6.1295 | 6.134 | -115.2649
3184.0625 | 121.1792 | -5.69 | 115.5991 | -0.00099167 | 0.012873 | 0.052408 | 0.0066202 | 0.0038281 | -0.0056866 | -0.0057208 | 0.0069425 | -0.0062078 | 0.0044284 | -0.001991 | -0.014753 | 0.019465 | -0.022888 | 0.018311 | 0.041199 | 0.082397 | 0.14648 | -0.041199 | -0.17853 | -0.018311 | 0.027466 | -0.045776 | 0.068665 | 0.045776 | -0.073242 | -0.14191 | 5.6488 | 5.5115 | -115.4526 | 5.7083 | 5.7724 | 0.26092 | -115.6219 | 5.6168 | 5.5481 | -115.5304 | 5.6717 | 5.6442 | 0.096131 | -115.5533 | 5.8365 | 5.6671 | 5.7312 | -115.7776 | 5.7587 | 5.7358 | 5.7175 | -115.741
3185.8125 | 121.2204 | -6.0562 | 115.2191 | 0.0066373 | 0.013727 | 0.053263 | 0.0070474 | 0.0023327 | 0.0026446 | -0.0048662 | 0.014572 | -0.0030034 | 0.0067782 | -0.0011364 | -0.0083441 | 0.019038 | 0 | -0.009155 | -0.022888 | 0.064087 | 0.1831 | -0.041199 | -0.19226 | -0.009155 | 0 | -0.073242 | 0.059509 | 0.054932 | -0.064087 | -0.1236 | 6.015 | 5.864 | -115.036 | 6.0471 | 6.1203 | 0.25635 | -115.2191 | 5.9921 | 5.9326 | -115.1596 | 6.0471 | 5.983 | 0.050354 | -115.1642 | 6.2393 | 6.0562 | 6.0333 | -115.4114 | 6.1157 | 6.1111 | 6.0562 | -115.3427
3187.5781 | 121.3257 | -6.5826 | 114.5874 | -0.00099167 | 0.011164 | 0.052408 | 0.010679 | 0.0040417 | -0.0022686 | -0.0072162 | -0.008316 | -0.0070624 | 0.0084872 | -0.0032728 | -0.01518 | 0.019038 | 0.054932 | 0.10986 | 0.10071 | 0.13733 | 0.13733 | -0.018311 | -0.17395 | 0.032043 | 0.10529 | 0.009155 | 0.054932 | 0.050354 | -0.054932 | -0.13275 | 6.5643 | 6.4087 | -114.4501 | 6.6925 | 6.72 | 0.31128 | -114.5325 | 6.5277 | 6.4499 | -114.5325 | 6.6147 | 6.5918 | 0.14191 | -114.537 | 6.72 | 6.6376 | 6.6833 | -114.7614 | 6.6376 | 6.633 | 6.6879 | -114.7202
3189.2812 | 121.3074 | -5.1865 | 116.1301 | -0.00099167 | 0.016718 | 0.050272 | 0.007261 | 0.0036145 | 0.0049946 | -0.006148 | 0.014572 | 0.00041436 | 0.0095554 | -0.0011364 | -0.0085577 | 0.017756 | 0.041199 | 0.022888 | 0 | 0.10071 | 0.16022 | -0.045776 | -0.21515 | -0.013733 | 0.018311 | -0.12817 | 0.041199 | 0.054932 | -0.091553 | -0.14648 | 5.1407 | 4.9713 | -115.9698 | 5.2093 | 5.2872 | 0.31586 | -116.0889 | 5.0949 | 5.04 | -116.0889 | 5.1727 | 5.0583 | 0.01831 | -116.0751 | 5.3467 | 5.2277 | 5.1865 | -116.3452 | 5.2277 | 5.2414 | 5.2048 | -116.2766
3191.0312 | 121.3303 | -7.4341 | 114.2303 | 0.014267 | 0.016077 | 0.053476 | 0.0053384 | 0.0038281 | 0.0015766 | -0.004439 | 0.0069425 | -0.002149 | 0.0065646 | -0.001991 | -0.0079169 | 0.017756 | 0.022888 | 0.027466 | -0.018311 | 0.10071 | 0.1831 | -0.064087 | -0.19684 | -0.009155 | 0.027466 | -0.12817 | 0.068665 | 0.073242 | -0.082397 | -0.16022 | 7.37 | 7.2372 | -114.0472 | 7.4615 | 7.5348 | 0.29755 | -114.2075 | 7.3517 | 7.2739 | -114.1617 | 7.4249 | 7.3059 | 0.032043 | -114.1571 | 7.6172 | 7.457 | 7.4158 | -114.4272 | 7.5027 | 7.5073 | 7.4615 | -114.3906
3192.7188 | 121.431 | -5.864 | 115.4892 | 0.014267 | 0.015436 | 0.05134 | 0.0074746 | 0.0046827 | -0.00055964 | -0.0057208 | 0.0069425 | -0.0010808 | 0.0076328 | -0.0011364 | -0.011335 | 0.020533 | -0.059509 | -0.032043 | -0.054932 | 0.045776 | 0.17853 | -0.068665 | -0.23804 | -0.073242 | -0.045776 | -0.16022 | 0.091553 | 0.073242 | -0.09613 | -0.16022 | 5.7953 | 5.6259 | -115.3107 | 5.8319 | 5.9097 | 0.28381 | -115.5487 | 5.7678 | 5.7037 | -115.3976 | 5.7907 | 5.7037 | 0 | -115.416 | 6.0425 | 5.8044 | 5.809 | -115.7272 | 5.9555 | 5.9372 | 5.8182 | -115.6494
3194.4844 | 121.4264 | -4.921 | 116.4368 | -0.00099167 | 0.0088142 | 0.053476 | 0.0057656 | 0.0036145 | -0.0052594 | -0.0042254 | -0.008316 | -0.0062078 | 0.006351 | -0.0032728 | -0.012403 | 0.020961 | -0.004578 | 0.054932 | 0.064087 | 0.10529 | 0.15564 | -0.013733 | -0.1831 | 0.018311 | 0.082397 | -0.018311 | 0.054932 | 0.036621 | -0.068665 | -0.1236 | 4.9072 | 4.7379 | -116.2811 | 4.9759 | 5.0262 | 0.28839 | -116.4413 | 4.8523 | 4.7974 | -116.3818 | 4.9393 | 4.9026 | 0.10528 | -116.4001 | 5.0766 | 4.9164 | 4.985 | -116.6199 | 4.9759 | 4.9576 | 5.0034 | -116.5604
3196.1719 | 121.4722 | -5.0262 | 116.2766 | 0.0066373 | 0.015009 | 0.051554 | 0.010252 | 0.0053235 | 0.001363 | -0.0063616 | 0.0069425 | -0.00044004 | 0.008701 | -0.003059 | -0.012617 | 0.017756 | -0.027466 | -0.036621 | -0.054932 | 0.054932 | 0.19684 | -0.059509 | -0.21515 | -0.064087 | -0.022888 | -0.14648 | 0.082397 | 0.07782 | -0.10071 | -0.16022 | 4.9667 | 4.8111 | -116.0797 | 4.9896 | 5.0812 | 0.27008 | -116.304 | 4.9255 | 4.866 | -116.1942 | 4.9622 | 4.8798 | 0.013733 | -116.1987 | 5.2231 | 4.9988 | 4.9713 | -116.4917 | 5.1086 | 5.1041 | 5.0034 | -116.4368
3197.9219 | 121.376 | -5.5847 | 115.8325 | -0.00099167 | 0.012873 | 0.052408 | 0.0057656 | 0.0027601 | 0.003072 | -0.0048662 | -0.00068649 | -0.00086724 | 0.0074192 | -0.0032728 | -0.0087713 | 0.019252 | -0.041199 | -0.068665 | -0.073242 | 0.050354 | 0.1831 | -0.045776 | -0.21057 | -0.073242 | -0.064087 | -0.16937 | 0.10071 | 0.086975 | -0.086975 | -0.15564 | 5.5389 | 5.3741 | -115.6494 | 5.5161 | 5.6351 | 0.26093 | -115.8737 | 5.4977 | 5.4291 | -115.7318 | 5.5115 | 5.4153 | -0.013733 | -115.7455 | 5.7678 | 5.5435 | 5.5115 | -116.0431 | 5.6854 | 5.6717 | 5.5206 | -115.9882
3199.6875 | 115.8096 | -62.5854 | 53.6957 | -0.00099167 | 0.0092414 | 0.052622 | 0.0059792 | 0.0021191 | -0.0026958 | -0.0059344 | 0.0069425 | -0.0062078 | 0.006992 | -0.0037 | -0.014753 | 0.022029 | 0.013733 | 0.086975 | 0.064087 | 0.1236 | 0.13275 | 0 | -0.15106 | 0.004578 | 0.050354 | -0.036621 | 0.07782 | 0.068665 | -0.054932 | -0.1236 | 62.5854 | 62.4344 | -53.5629 | 62.6724 | 62.709 | 0.27466 | -53.6819 | 62.5305 | 62.4619 | -53.6179 | 62.59 | 62.5488 | 0.086975 | -53.627 | 62.7182 | 62.5992 | 62.6495 | -53.8467 | 62.6633 | 62.6541 | 62.6358 | -53.8193
3201.375 | 117.0731 | -7.988 | 109.9182 | -0.00099167 | 0.013941 | 0.053263 | 0.0070474 | 0.00083746 | -0.0016278 | -0.0055072 | 0.0069425 | -0.0040716 | 0.0054966 | -0.0026318 | -0.0098395 | 0.019465 | 0.054932 | 0.082397 | 0.082397 | 0.11902 | 0.12817 | -0.004578 | -0.15564 | 0.032043 | 0.086975 | -0.018311 | 0.050354 | 0.041199 | -0.054932 | -0.10529 | 7.9834 | 7.8323 | -109.79 | 8.0704 | 8.107 | 0.27466 | -109.8633 | 7.933 | 7.8827 | -109.8679 | 8.02 | 7.9697 | 0.086975 | -109.877 | 8.1161 | 8.0429 | 8.0704 | -110.0739 | 8.0383 | 8.0292 | 8.075 | -110.0235
3203.1406 | 120.401 | -4.6051 | 115.6265 | -0.00099167 | 0.013941 | 0.056253 | 0.0076882 | 0.00062386 | -0.0014142 | -0.0037982 | -0.00068649 | -0.0053534 | 0.0059238 | -0.0041272 | -0.011549 | 0.019465 | 0.054932 | 0.1236 | 0.091553 | 0.15564 | 0.16022 | -0.036621 | -0.17853 | 0.018311 | 0.10986 | -0.032043 | 0.041199 | 0.050354 | -0.059509 | -0.11902 | 4.5685 | 4.4266 | -115.4663 | 4.7287 | 4.7607 | 0.33417 | -115.5716 | 4.5456 | 4.4861 | -115.5853 | 4.6234 | 4.5731 | 0.086976 | -115.5762 | 4.7653 | 4.66 | 4.6967 | -115.8051 | 4.6463 | 4.6555 | 4.715 | -115.7455
3204.8906 | 120.5109 | -4.0192 | 116.5375 | -0.00099167 | 0.012659 | 0.055399 | 0.0061928 | 0.0027601 | -0.00013244 | -0.0057208 | -0.008316 | -0.0044988 | 0.0059238 | -0.0034864 | -0.010694 | 0.02032 | 0.068665 | 0.10986 | 0.091553 | 0.13733 | 0.15564 | -0.032043 | -0.1831 | 0.032043 | 0.11444 | -0.022888 | 0.045776 | 0.050354 | -0.059509 | -0.11444 | 3.9871 | 3.8361 | -116.3818 | 4.129 | 4.1565 | 0.32043 | -116.4688 | 3.9597 | 3.9047 | -116.4917 | 4.0512 | 3.9963 | 0.091553 | -116.4871 | 4.1748 | 4.0878 | 4.1107 | -116.7206 | 4.0649 | 4.0695 | 4.1336 | -116.6519
3206.6406 | 106.4804 | -3.5797 | 116.4642 | -0.00099167 | 0.017145 | 0.050272 | 0.003843 | 0.0036145 | 0.0062762 | -0.0035846 | 0.0069425 | 0.001269 | 0.0050694 | -0.0011364 | -0.0083441 | 0.020961 | -0.027466 | -0.091553 | -0.073242 | 0.027466 | 0.19684 | -0.045776 | -0.21515 | -0.073242 | -0.068665 | -0.19226 | 0.09613 | 0.068665 | -0.073242 | -0.1236 | 3.5339 | 3.3646 | -116.2674 | 3.4882 | 3.6072 | 0.24261 | -116.4917 | 3.5065 | 3.4561 | -116.3681 | 3.5065 | 3.3875 | -0.068665 | -116.3956 | 3.7765 | 3.5522 | 3.5065 | -116.6794 | 3.6758 | 3.6484 | 3.511 | -116.5878
3208.3438 | 93.5989 | -3.5202 | 99.7284 | -0.00099167 | 0.012873 | 0.053049 | 0.0081154 | 0.0027601 | 0.002431 | -0.00273 | -0.00068649 | -0.00065364 | 0.0091282 | -0.0043408 | -0.0070623 | 0.018611 | -0.018311 | -0.054932 | -0.050354 | 0.022888 | 0.20142 | -0.050354 | -0.19684 | -0.032043 | -0.045776 | -0.14648 | 0.082397 | 0.064087 | -0.068665 | -0.14648 | 3.4698 | 3.3234 | -99.527 | 3.4653 | 3.5431 | 0.21973 | -99.7467 | 3.4515 | 3.3737 | -99.646 | 3.4882 | 3.3737 | 0 | -99.6643 | 3.7216 | 3.5019 | 3.4698 | -99.9252 | 3.6026 | 3.5843 | 3.4744 | -99.8749
3210.0938 | 120.8679 | -3.566 | 117.2791 | 0.0066373 | 0.015436 | 0.052835 | 0.0091836 | 0.0019055 | 8.1158e-05 | -0.006148 | -0.008316 | -0.0017218 | 0.0076328 | -0.0022046 | -0.013258 | 0.020106 | -0.054932 | -0.027466 | -0.041199 | 0.032043 | 0.18768 | -0.068665 | -0.21515 | -0.07782 | -0.027466 | -0.15106 | 0.09613 | 0.09613 | -0.10529 | -0.15106 | 3.4973 | 3.3508 | -117.0914 | 3.5385 | 3.598 | 0.24719 | -117.334 | 3.4607 | 3.4149 | -117.1829 | 3.4882 | 3.4149 | 0 | -117.1829 | 3.7537 | 3.511 | 3.5248 | -117.4942 | 3.6621 | 3.6621 | 3.5385 | -117.4301
3211.8438 | 120.9045 | -3.6667 | 117.2882 | -0.00099167 | 0.013941 | 0.05369 | 0.0087564 | 0.0038281 | -0.0016278 | -0.0052936 | 0.0069425 | -0.0047124 | 0.0044284 | -0.0041272 | -0.011976 | 0.019038 | 0.018311 | 0.082397 | 0.045776 | 0.10071 | 0.16479 | -0.018311 | -0.18768 | -0.036621 | 0.054932 | -0.082397 | 0.068665 | 0.073242 | -0.09613 | -0.14648 | 3.6484 | 3.479 | -117.1234 | 3.7491 | 3.7674 | 0.28839 | -117.2699 | 3.5706 | 3.5202 | -117.2195 | 3.6301 | 3.5843 | 0.064087 | -117.215 | 3.8315 | 3.685 | 3.7125 | -117.4759 | 3.7354 | 3.7399 | 3.7216 | -117.4347
3213.5938 | 104.6448 | -3.7399 | 116.8167 | -0.00099167 | 0.015009 | 0.053049 | 0.0076882 | 0.0040417 | 0.0056354 | -0.004439 | 0.0069425 | -0.00086724 | 0.0065646 | 0.00057261 | -0.010694 | 0.018184 | -0.022888 | -0.059509 | -0.054932 | 0.045776 | 0.20599 | -0.064087 | -0.21057 | -0.050354 | -0.054932 | -0.15564 | 0.091553 | 0.068665 | -0.068665 | -0.14191 | 3.6758 | 3.5294 | -116.6107 | 3.6804 | 3.7857 | 0.25635 | -116.8396 | 3.6713 | 3.598 | -116.7252 | 3.6896 | 3.5843 | -0.013733 | -116.748 | 3.9459 | 3.717 | 3.685 | -117.0273 | 3.8315 | 3.8086 | 3.685 | -116.9586
3215.2812 | 109.8816 | -3.9459 | 116.8671 | -0.00099167 | 0.012659 | 0.053904 | 0.0036294 | 0.0023327 | 0.0045674 | -0.00273 | 0.014572 | -0.0023626 | 0.005283 | -0.00049559 | -0.0087713 | 0.021601 | -0.045776 | -0.064087 | -0.073242 | 0.041199 | 0.20142 | -0.064087 | -0.19684 | -0.045776 | -0.07782 | -0.17395 | 0.10071 | 0.07782 | -0.091553 | -0.15564 | 3.8818 | 3.7491 | -116.6656 | 3.8818 | 3.9871 | 0.23804 | -116.9128 | 3.8544 | 3.7903 | -116.7664 | 3.9001 | 3.772 | -0.01831 | -116.7892 | 4.1473 | 3.9001 | 3.8727 | -117.0639 | 4.0466 | 4.0237 | 3.8681 | -117.0227
3217.0312 | 121.2341 | -4.0604 | 116.8625 | -0.00099167 | 0.014582 | 0.051981 | 0.010893 | 0.0053235 | 0.0015766 | -0.003371 | -0.00068649 | -0.0027898 | 0.0084872 | -0.00092279 | -0.010267 | 0.018824 | -0.032043 | -0.018311 | -0.013733 | 0.091553 | 0.17853 | -0.050354 | -0.20599 | -0.036621 | 0.013733 | -0.11444 | 0.09613 | 0.068665 | -0.07782 | -0.13733 | 4.01 | 3.8544 | -116.684 | 4.0421 | 4.1519 | 0.29755 | -116.8945 | 3.9825 | 3.923 | -116.7664 | 4.0237 | 3.9459 | 0.022888 | -116.7938 | 4.2389 | 4.0283 | 4.0466 | -117.0685 | 4.1565 | 4.129 | 4.0741 | -116.9998
3218.7188 | 121.2479 | -4.0924 | 116.6794 | 0.0066373 | 0.012018 | 0.050486 | 0.0079018 | 0.0044691 | 0.0011494 | -0.0035846 | -0.00068649 | -0.0030034 | 0.00806 | -0.00092279 | -0.013044 | 0.019465 | -0.050354 | -0.013733 | -0.045776 | 0.059509 | 0.17395 | -0.054932 | -0.21973 | -0.045776 | 0.022888 | -0.12817 | 0.10071 | 0.073242 | -0.07782 | -0.16022 | 4.0375 | 3.8727 | -116.5054 | 4.0787 | 4.1519 | 0.27924 | -116.7297 | 4.0146 | 3.9322 | -116.5787 | 4.0466 | 3.9642 | 0.032043 | -116.6061 | 4.2664 | 4.0421 | 4.0466 | -116.8991 | 4.1931 | 4.1656 | 4.1153 | -116.8396
3220.4844 | 121.2524 | -4.0466 | 116.9403 | 0.0066373 | 0.012873 | 0.052622 | 0.0068338 | 0.0021191 | -0.0014142 | -0.0052936 | -0.008316 | -0.0017218 | 0.0054966 | -0.001991 | -0.0079169 | 0.020533 | -0.050354 | -0.036621 | -0.059509 | 0.045776 | 0.17853 | -0.068665 | -0.21515 | -0.050354 | -0.054932 | -0.13275 | 0.09613 | 0.059509 | -0.073242 | -0.14191 | 3.978 | 3.8315 | -116.7618 | 4.01 | 4.0924 | 0.26093 | -116.9907 | 3.9734 | 3.9047 | -116.8442 | 3.9963 | 3.9139 | 0.009156 | -116.8808 | 4.2252 | 3.9963 | 3.9871 | -117.1555 | 4.1428 | 4.1061 | 3.9917 | -117.0822
3222.1719 | 121.0831 | -4.1153 | 116.5878 | -0.00099167 | 0.0090278 | 0.054117 | 0.0064066 | 0.00083746 | -0.0061138 | -0.0040118 | 0.0069425 | -0.006635 | 0.0048556 | -0.0056226 | -0.011762 | 0.021174 | 0.027466 | 0.11902 | 0.10071 | 0.1236 | 0.15106 | -0.032043 | -0.17395 | 0.018311 | 0.11902 | 0.018311 | 0.027466 | 0.036621 | -0.068665 | -0.11444 | 4.0833 | 3.9413 | -116.4368 | 4.2343 | 4.2389 | 0.29755 | -116.5604 | 4.0466 | 4.0009 | -116.5604 | 4.1336 | 4.1336 | 0.13275 | -116.5512 | 4.2664 | 4.1428 | 4.216 | -116.7618 | 4.1428 | 4.1519 | 4.2343 | -116.7023
3223.9375 | 121.257 | -4.097 | 116.9495 | 0.014267 | 0.0133 | 0.055399 | 0.0085428 | 0.0040417 | -0.0029094 | -0.0067888 | -0.008316 | -0.0025762 | 0.0067782 | -0.0015638 | -0.012189 | 0.019465 | -0.068665 | -0.018311 | -0.045776 | 0.036621 | 0.1831 | -0.054932 | -0.21057 | -0.10071 | -0.018311 | -0.14648 | 0.091553 | 0.082397 | -0.10071 | -0.16479 | 4.0421 | 3.8864 | -116.7664 | 4.0787 | 4.1336 | 0.24719 | -117.0181 | 3.9963 | 3.9322 | -116.8579 | 3.9963 | 3.9505 | 0.018311 | -116.8671 | 4.2801 | 4.0283 | 4.0512 | -117.16 | 4.1885 | 4.1794 | 4.0787 | -117.1143
3225.6875 | 121.257 | -4.1336 | 117.0685 | -0.0086212 | 0.012018 | 0.055185 | 0.0074746 | 0.0010511 | -0.0029094 | -0.0070026 | -0.008316 | -0.0047124 | 0.0061374 | -0.0041272 | -0.010267 | 0.020961 | 0.054932 | 0.12817 | 0.10071 | 0.1236 | 0.14648 | -0.041199 | -0.16937 | 0.022888 | 0.1236 | -0.018311 | 0.059509 | 0.036621 | -0.050354 | -0.13275 | 4.0924 | 3.9642 | -116.922 | 4.2618 | 4.2572 | 0.29297 | -117.0135 | 4.0833 | 4.0009 | -117.009 | 4.1565 | 4.1153 | 0.11444 | -117.0319 | 4.2801 | 4.1885 | 4.2343 | -117.2379 | 4.1931 | 4.1702 | 4.2572 | -117.2012
3227.375 | 121.3577 | -4.1519 | 117.0273 | -0.00099167 | 0.016505 | 0.053049 | 0.0096108 | 0.0021191 | -0.00013244 | -0.006148 | -0.00068649 | 0.00020076 | 0.0078464 | -0.00092279 | -0.011549 | 0.018824 | -0.036621 | -0.050354 | -0.054932 | 0.064087 | 0.18768 | -0.07782 | -0.21057 | -0.059509 | -0.018311 | -0.14648 | 0.091553 | 0.09613 | -0.11444 | -0.15564 | 4.0741 | 3.9413 | -116.8396 | 4.1016 | 4.216 | 0.27466 | -117.0639 | 4.0375 | 3.9963 | -116.9357 | 4.0924 | 4.0054 | 0.009156 | -116.9312 | 4.3396 | 4.1153 | 4.097 | -117.2379 | 4.2435 | 4.248 | 4.1336 | -117.1829
3229.125 | 120.607 | -4.2984 | 116.9724 | 0.014267 | 0.012446 | 0.052195 | 0.0068338 | 0.0038281 | -0.00055964 | -0.0052936 | -0.00068649 | -0.0064214 | 0.0059238 | -0.0013502 | -0.014112 | 0.020961 | 0.041199 | 0.07782 | 0.082397 | 0.10529 | 0.14191 | -0.032043 | -0.17853 | 0 | 0.050354 | -0.054932 | 0.050354 | 0.054932 | -0.059509 | -0.11444 | 4.2664 | 4.1199 | -116.8304 | 4.3762 | 4.4037 | 0.28381 | -116.9312 | 4.2389 | 4.184 | -116.922 | 4.2984 | 4.2435 | 0.059509 | -116.9174 | 4.4403 | 4.3396 | 4.3808 | -117.1509 | 4.3488 | 4.3533 | 4.3488 | -117.0868
3230.875 | 121.3394 | -4.2938 | 116.9403 | 0.014267 | 0.016932 | 0.053904 | 0.0051248 | 0.0057507 | 0.00414 | -0.0020892 | 0.0069425 | -0.00086724 | 0.0065646 | 0.00057261 | -0.0085577 | 0.016902 | -0.022888 | -0.013733 | -0.022888 | 0.082397 | 0.17853 | -0.041199 | -0.20142 | -0.041199 | 0.018311 | -0.11444 | 0.10986 | 0.073242 | -0.091553 | -0.15564 | 4.2526 | 4.0924 | -116.7618 | 4.2801 | 4.3762 | 0.28381 | -116.9632 | 4.2023 | 4.1382 | -116.8304 | 4.2526 | 4.1794 | 0.041199 | -116.8671 | 4.4724 | 4.2709 | 4.2709 | -117.1417 | 4.4037 | 4.3671 | 4.3121 | -117.0959
3232.5781 | 121.3531 | -4.4449 | 116.8121 | -0.00099167 | 0.012873 | 0.053049 | 0.010252 | 0.00062386 | -0.003764 | -0.0063616 | -0.008316 | -0.0057806 | 0.006992 | -0.0032728 | -0.013258 | 0.019252 | 0.009155 | 0.07782 | 0.09613 | 0.11444 | 0.14648 | -0.045776 | -0.16937 | 0.041199 | 0.10071 | -0.009155 | 0.064087 | 0.045776 | -0.054932 | -0.10986 | 4.3991 | 4.2755 | -116.6656 | 4.5227 | 4.5593 | 0.28381 | -116.803 | 4.39 | 4.335 | -116.748 | 4.4861 | 4.4357 | 0.10071 | -116.7664 | 4.5914 | 4.454 | 4.541 | -116.9815 | 4.509 | 4.4907 | 4.5456 | -116.922
3234.3438 | 121.312 | -4.4678 | 116.8213 | -0.0086212 | 0.014155 | 0.052195 | 0.0061928 | 0.0036145 | -0.00098684 | -0.0055072 | -0.00068649 | -0.0044988 | 0.0074192 | -0.0034864 | -0.011762 | 0.018824 | 0.027466 | 0.082397 | 0.073242 | 0.13275 | 0.16022 | -0.032043 | -0.19684 | -0.027466 | 0.032043 | -0.082397 | 0.054932 | 0.064087 | -0.086975 | -0.14648 | 4.4357 | 4.2709 | -116.6611 | 4.5502 | 4.6005 | 0.32959 | -116.7938 | 4.3808 | 4.3213 | -116.7664 | 4.4403 | 4.3854 | 0.064087 | -116.7572 | 4.628 | 4.4952 | 4.541 | -117.0181 | 4.5227 | 4.5319 | 4.4998 | -116.9678
3236.0312 | 120.8084 | -4.4952 | 116.8762 | 0.014267 | 0.010523 | 0.051981 | 0.0036294 | 0.0046827 | -0.00098684 | -0.0052936 | -0.008316 | -0.0049262 | 0.006992 | -0.0017774 | -0.0079169 | 0.018611 | 0.064087 | 0.10071 | 0.059509 | 0.14191 | 0.15106 | -0.027466 | -0.15106 | 0.045776 | 0.07782 | -0.041199 | 0.054932 | 0.041199 | -0.064087 | -0.09613 | 4.4678 | 4.3442 | -116.7252 | 4.5959 | 4.6371 | 0.29297 | -116.8121 | 4.4312 | 4.3991 | -116.8213 | 4.541 | 4.454 | 0.054931 | -116.835 | 4.6463 | 4.5593 | 4.5547 | -117.0273 | 4.5502 | 4.5364 | 4.5731 | -116.9724
3237.7812 | 120.9732 | -4.4724 | 116.922 | 0.014267 | 0.011164 | 0.054758 | 0.0044838 | 0.0025465 | -0.00077324 | -0.0059344 | 0.0069425 | -0.005567 | 0.0040012 | -0.0024182 | -0.0074897 | 0.019038 | 0.059509 | 0.10071 | 0.073242 | 0.12817 | 0.14191 | -0.018311 | -0.16022 | 0.032043 | 0.068665 | -0.013733 | 0.059509 | 0.054932 | -0.050354 | -0.12817 | 4.454 | 4.3121 | -116.7801 | 4.5731 | 4.6005 | 0.28839 | -116.8625 | 4.422 | 4.3442 | -116.8625 | 4.5044 | 4.4586 | 0.11444 | -116.8671 | 4.6143 | 4.5319 | 4.5456 | -117.0822 | 4.5319 | 4.5273 | 4.541 | -117.0502
3239.4844 | 121.3943 | -4.3945 | 116.8671 | 0.0066373 | 0.013727 | 0.052622 | 0.007261 | 0.0016919 | -0.0026958 | -0.007857 | -0.00068649 | -0.0036444 | 0.006351 | -0.0026318 | -0.013685 | 0.020747 | 0.050354 | 0.11902 | 0.09613 | 0.12817 | 0.15564 | -0.027466 | -0.17853 | 0.036621 | 0.1236 | -0.004578 | 0.050354 | 0.050354 | -0.059509 | -0.1236 | 4.3671 | 4.216 | -116.7114 | 4.5135 | 4.5227 | 0.3067 | -116.8167 | 4.335 | 4.2709 | -116.8167 | 4.4312 | 4.39 | 0.11902 | -116.8167 | 4.5502 | 4.4449 | 4.4907 | -117.0456 | 4.4449 | 4.4449 | 4.5181 | -116.9907
3241.25 | 121.3852 | -4.5364 | 116.8167 | 0.0066373 | 0.014582 | 0.054331 | 0.0093972 | 0.0034009 | 0.00072196 | -0.0067888 | 0.0069425 | -0.0030034 | 0.0074192 | -0.0011364 | -0.012189 | 0.01797 | -0.027466 | -0.009155 | -0.018311 | 0.036621 | 0.19226 | -0.059509 | -0.20599 | -0.07782 | -0.013733 | -0.16022 | 0.09613 | 0.09613 | -0.086975 | -0.16022 | 4.4769 | 4.3304 | -116.6244 | 4.5273 | 4.5731 | 0.24262 | -116.8442 | 4.4495 | 4.3762 | -116.7206 | 4.4586 | 4.3762 | 0 | -116.7206 | 4.7287 | 4.509 | 4.5181 | -117.0227 | 4.6326 | 4.6326 | 4.5227 | -116.9769
3243.0625 | 121.4539 | -4.4174 | 116.922 | 0.0066373 | 0.016932 | 0.050913 | 0.0074746 | 0.0048963 | 0.0017902 | -0.0037982 | -0.00068649 | -0.0032172 | 0.00806 | 0.00035881 | -0.0081305 | 0.017329 | -0.004578 | -0.018311 | -0.027466 | 0.068665 | 0.1831 | -0.068665 | -0.20142 | -0.032043 | -0.004578 | -0.13275 | 0.091553 | 0.068665 | -0.091553 | -0.15564 | 4.3488 | 4.216 | -116.7389 | 4.3991 | 4.4861 | 0.27008 | -116.9266 | 4.3259 | 4.2618 | -116.8304 | 4.3854 | 4.2847 | 0.022889 | -116.8533 | 4.6005 | 4.4128 | 4.39 | -117.1234 | 4.509 | 4.4861 | 4.4128 | -117.0776
3244.8125 | 121.3715 | -4.6509 | 116.716 | 0.0066373 | 0.012232 | 0.052835 | 0.0025612 | 0.0027601 | 0.0022174 | -0.0040118 | 0.0069425 | -0.0042852 | 0.0072056 | -0.0028454 | -0.0087713 | 0.017329 | -0.018311 | 0.022888 | 0.004578 | 0.068665 | 0.16479 | -0.036621 | -0.1831 | 0.013733 | 0.027466 | -0.07782 | 0.041199 | 0.064087 | -0.059509 | -0.11902 | 4.6143 | 4.4678 | -116.5512 | 4.6738 | 4.7195 | 0.25177 | -116.7343 | 4.5914 | 4.5319 | -116.6748 | 4.6646 | 4.5731 | 0.041199 | -116.6519 | 4.8157 | 4.6326 | 4.6555 | -116.8991 | 4.6921 | 4.715 | 4.6783 | -116.835
3246.5625 | 121.3211 | -4.7195 | 116.6702 | 0.0066373 | 0.014582 | 0.05369 | 0.0036294 | 0.0029737 | 0.0037128 | -0.0031574 | 0.0069425 | 0.001269 | 0.0061374 | -0.0039136 | -0.0055671 | 0.020106 | -0.054932 | -0.054932 | -0.073242 | 0.032043 | 0.19226 | -0.054932 | -0.20142 | -0.064087 | -0.064087 | -0.17395 | 0.082397 | 0.073242 | -0.10071 | -0.15106 | 4.6646 | 4.5181 | -116.478 | 4.6646 | 4.7516 | 0.23346 | -116.7252 | 4.6188 | 4.5685 | -116.5878 | 4.6555 | 4.5456 | -0.022888 | -116.597 | 4.9118 | 4.6646 | 4.6463 | -116.8716 | 4.8019 | 4.7928 | 4.6555 | -116.8213
3248.3125 | 121.3989 | -5.3055 | 116.0797 | 0.0066373 | 0.014368 | 0.050486 | 0.005552 | 0.0029737 | 0.003072 | -0.001662 | 0.0069425 | -0.0025762 | 0.0057102 | -0.0026318 | -0.0072759 | 0.019252 | 0.013733 | 0.054932 | -0.004578 | 0.07782 | 0.17395 | -0.027466 | -0.21057 | -0.027466 | 0.009155 | -0.13275 | 0.082397 | 0.082397 | -0.086975 | -0.15564 | 5.278 | 5.0949 | -115.9058 | 5.3604 | 5.3833 | 0.28839 | -116.066 | 5.2185 | 5.1498 | -115.9973 | 5.278 | 5.1727 | 0.022889 | -115.9973 | 5.4794 | 5.3192 | 5.3009 | -116.2903 | 5.3879 | 5.3879 | 5.3146 | -116.2354
3250.0156 | 121.3989 | -2.9892 | 118.4189 | 0.0066373 | 0.014368 | 0.051981 | 0.0079018 | 0.0012647 | 0.0028584 | -0.00508 | -0.00068649 | -0.0027898 | 0.006351 | -0.0028454 | -0.0072759 | 0.023738 | -0.059509 | -0.036621 | -0.050354 | 0.041199 | 0.19226 | -0.064087 | -0.22888 | -0.064087 | -0.054932 | -0.14191 | 0.082397 | 0.064087 | -0.091553 | -0.14191 | 2.9251 | 2.7603 | -118.2266 | 2.9526 | 3.0304 | 0.27008 | -118.4784 | 2.8976 | 2.8473 | -118.3365 | 2.9251 | 2.8473 | 0 | -118.3548 | 3.1815 | 2.9297 | 2.9388 | -118.6478 | 3.0716 | 3.0533 | 2.9343 | -118.5608
3251.7031 | 121.3989 | -5.1773 | 116.0889 | -0.00099167 | 0.015223 | 0.054544 | 0.005552 | 0.0029737 | 0.0039264 | -0.0046526 | -0.00068649 | -0.0023626 | 0.0076328 | -0.0028454 | -0.0077033 | 0.02032 | -0.059509 | -0.045776 | -0.073242 | 0.050354 | 0.18768 | -0.054932 | -0.20599 | -0.07782 | -0.050354 | -0.14648 | 0.082397 | 0.068665 | -0.082397 | -0.15106 | 5.1224 | 4.9713 | -115.9012 | 5.1315 | 5.2277 | 0.25635 | -116.1484 | 5.0949 | 5.0262 | -116.0065 | 5.0995 | 5.0308 | 0.004578 | -116.0202 | 5.365 | 5.1178 | 5.1041 | -116.2949 | 5.2597 | 5.246 | 5.127 | -116.2399
3253.4531 | 121.4081 | -4.9072 | 116.4825 | 0.0066373 | 0.0092414 | 0.053049 | 0.0074746 | 0.0012647 | -0.0059002 | -0.0067888 | 0.014572 | -0.0059942 | 0.0054966 | -0.0026318 | -0.013258 | 0.021388 | -0.027466 | 0.036621 | 0.045776 | 0.091553 | 0.15106 | -0.032043 | -0.15564 | -0.041199 | 0.018311 | -0.050354 | 0.064087 | 0.045776 | -0.054932 | -0.1236 | 4.8752 | 4.7516 | -116.3315 | 4.9438 | 4.9988 | 0.24719 | -116.51 | 4.8523 | 4.7836 | -116.4185 | 4.866 | 4.8569 | 0.073242 | -116.4368 | 5.0583 | 4.8798 | 4.953 | -116.6382 | 4.9713 | 4.953 | 4.9255 | -116.6061
3255.2188 | 121.3531 | -2.3529 | 119.1193 | 0.0066373 | 0.009455 | 0.053263 | 0.0083292 | 0.0025465 | -0.0026958 | -0.0059344 | -0.015945 | -0.0057806 | 0.0050694 | -0.0026318 | -0.013471 | 0.019465 | 0.009155 | 0.059509 | 0.054932 | 0.086975 | 0.13733 | -0.027466 | -0.15106 | -0.004578 | 0.027466 | -0.050354 | 0.054932 | 0.041199 | -0.073242 | -0.13733 | 2.3254 | 2.2018 | -118.9819 | 2.4124 | 2.4399 | 0.23804 | -119.1101 | 2.2797 | 2.2156 | -119.0643 | 2.3483 | 2.3026 | 0.086975 | -119.0781 | 2.4902 | 2.3621 | 2.4078 | -119.2703 | 2.4078 | 2.3941 | 2.3804 | -119.2566
3256.9062 | 121.3531 | -2.2751 | 119.2245 | -0.00099167 | 0.011378 | 0.055399 | 0.005552 | 0.00083746 | -0.0024822 | -0.006148 | 0.014572 | -0.0068488 | 0.0061374 | -0.005409 | -0.012617 | 0.021388 | 0.018311 | 0.059509 | 0.059509 | 0.10986 | 0.14191 | -0.027466 | -0.16479 | 0 | 0.027466 | -0.064087 | 0.054932 | 0.054932 | -0.073242 | -0.1236 | 2.2476 | 2.1103 | -119.0826 | 2.3346 | 2.3849 | 0.27466 | -119.2062 | 2.2018 | 2.1515 | -119.1696 | 2.2751 | 2.211 | 0.059509 | -119.1696 | 2.417 | 2.2934 | 2.3346 | -119.3893 | 2.33 | 2.33 | 2.3026 | -119.3481
3258.6094 | 121.5271 | -2.3209 | 119.101 | 0.0066373 | 0.012018 | 0.053904 | 0.0083292 | 0.0016919 | -0.0031232 | -0.0091388 | -0.00068649 | -0.005567 | 0.0061374 | -0.0022046 | -0.013685 | 0.016902 | 0.054932 | 0.11444 | 0.10529 | 0.13733 | 0.14648 | -0.018311 | -0.16022 | 0.050354 | 0.10071 | 0 | 0.050354 | 0.036621 | -0.068665 | -0.1236 | 2.3026 | 2.1606 | -118.9545 | 2.4353 | 2.4582 | 0.29755 | -119.046 | 2.2522 | 2.1973 | -119.0506 | 2.3712 | 2.3209 | 0.1236 | -119.0643 | 2.4673 | 2.3758 | 2.4261 | -119.2612 | 2.3712 | 2.3575 | 2.4216 | -119.2245
3260.375 | 121.5088 | -1.9501 | 119.4626 | -0.00099167 | 0.016505 | 0.053263 | 0.0044838 | 0.0051099 | 0.0067036 | -0.004439 | -0.008316 | -0.0010808 | 0.0061374 | -0.0028454 | -0.0079169 | 0.016261 | 0.041199 | 0.013733 | -0.013733 | 0.091553 | 0.19684 | -0.054932 | -0.21057 | -0.009155 | 0.022888 | -0.11902 | 0.09613 | 0.059509 | -0.09613 | -0.16022 | 1.8951 | 1.7395 | -119.2657 | 1.9638 | 2.0416 | 0.30212 | -119.4214 | 1.8539 | 1.7899 | -119.3665 | 1.9409 | 1.8311 | 0.041198 | -119.4031 | 2.1469 | 1.9913 | 1.9363 | -119.6732 | 2.0462 | 2.0096 | 1.973 | -119.6228
3262.0625 | 121.4081 | -2.2339 | 119.0002 | 0.0066373 | 0.0096686 | 0.054544 | 0.0068338 | 0.00019646 | -0.0014142 | -0.0040118 | 0.0069425 | -0.0062078 | 0.005283 | -0.003059 | -0.0087713 | 0.019038 | 0.032043 | 0.091553 | 0.07782 | 0.10529 | 0.13275 | -0.018311 | -0.17853 | 0.018311 | 0.064087 | -0.045776 | 0.059509 | 0.041199 | -0.054932 | -0.11902 | 2.2156 | 2.0554 | -118.8675 | 2.3254 | 2.3392 | 0.28381 | -118.9682 | 2.179 | 2.1149 | -118.9407 | 2.2522 | 2.1881 | 0.073243 | -118.959 | 2.3666 | 2.2659 | 2.3117 | -119.1788 | 2.2934 | 2.2751 | 2.298 | -119.1193
3263.75 | 121.6827 | -1.6983 | 119.7189 | 0.014267 | 0.012018 | 0.055185 | 0.010038 | 0.0027601 | -0.00055964 | -0.0065752 | -0.00068649 | -0.003858 | 0.004642 | -0.0032728 | -0.011762 | 0.019038 | 0.068665 | 0.12817 | 0.091553 | 0.12817 | 0.15106 | -0.032043 | -0.17395 | 0.045776 | 0.12817 | 0.009155 | 0.059509 | 0.041199 | -0.045776 | -0.11444 | 1.6663 | 1.5244 | -119.5679 | 1.8265 | 1.8265 | 0.30212 | -119.6503 | 1.6525 | 1.5839 | -119.6594 | 1.7441 | 1.7075 | 0.1236 | -119.6777 | 1.8494 | 1.767 | 1.7899 | -119.8929 | 1.7578 | 1.7395 | 1.8265 | -119.8334
3265.5 | 121.5271 | -1.5198 | 119.9478 | -0.00099167 | 0.015436 | 0.054117 | 0.0096108 | 0.0014783 | 0.00029476 | -0.0057208 | 0.0069425 | -0.0036444 | 0.006992 | -0.0034864 | -0.010053 | 0.019252 | 0.059509 | 0.09613 | 0.09613 | 0.13275 | 0.15106 | -0.045776 | -0.1831 | 0.018311 | 0.09613 | -0.054932 | 0.054932 | 0.045776 | -0.050354 | -0.11902 | 1.474 | 1.3367 | -119.7968 | 1.6159 | 1.6525 | 0.31586 | -119.8883 | 1.4694 | 1.4008 | -119.8929 | 1.5381 | 1.4648 | 0.064087 | -119.902 | 1.6708 | 1.5793 | 1.6159 | -120.1309 | 1.5747 | 1.5656 | 1.6159 | -120.0668
3267.25 | 121.5317 | -1.7166 | 119.7327 | 0.0066373 | 0.010523 | 0.052408 | 0.0053384 | 0.0014783 | -0.0024822 | -0.0046526 | 0.0069425 | -0.0044988 | 0.003574 | -0.0034864 | -0.011762 | 0.01797 | 0.004578 | 0.036621 | 0.041199 | 0.09613 | 0.16937 | -0.036621 | -0.17853 | 0.004578 | 0.032043 | -0.041199 | 0.054932 | 0.068665 | -0.059509 | -0.13275 | 1.68 | 1.5381 | -119.5633 | 1.7532 | 1.8127 | 0.27466 | -119.7281 | 1.6571 | 1.5839 | -119.6777 | 1.7212 | 1.6754 | 0.091552 | -119.664 | 1.886 | 1.7212 | 1.7578 | -119.9112 | 1.7715 | 1.7853 | 1.7487 | -119.8654
3268.9375 | 121.5408 | -1.5152 | 119.9295 | 0.0066373 | 0.02035 | 0.051767 | 0.0085428 | 0.0029737 | 0.0054218 | -0.0037982 | 0.0069425 | 0.00020076 | 0.006351 | -0.00092279 | -0.0089849 | 0.017329 | 0.032043 | -0.009155 | -0.022888 | 0.086975 | 0.1831 | -0.054932 | -0.21973 | -0.004578 | 0.027466 | -0.1236 | 0.073242 | 0.068665 | -0.10071 | -0.13733 | 1.4603 | 1.2955 | -119.7464 | 1.506 | 1.6022 | 0.3067 | -119.8975 | 1.4145 | 1.3779 | -119.8563 | 1.5106 | 1.3916 | 0.013733 | -119.8608 | 1.6983 | 1.5472 | 1.4923 | -120.1492 | 1.5884 | 1.5839 | 1.5427 | -120.0668
3270.6875 | 121.5637 | -1.6022 | 119.9158 | -0.00099167 | 0.0098822 | 0.053476 | 0.0044838 | 0.0034009 | -0.0018414 | -0.0063616 | -0.00068649 | -0.007276 | 0.004642 | -0.001991 | -0.011762 | 0.019679 | 0.013733 | 0.073242 | 0.064087 | 0.11902 | 0.16479 | -0.054932 | -0.17395 | 0.036621 | 0.10071 | -0.004578 | 0.045776 | 0.032043 | -0.045776 | -0.1236 | 1.5472 | 1.4282 | -119.751 | 1.6754 | 1.7212 | 0.29297 | -119.902 | 1.5564 | 1.4786 | -119.87 | 1.6388 | 1.5976 | 0.11902 | -119.8837 | 1.767 | 1.6159 | 1.6663 | -120.0897 | 1.6479 | 1.6342 | 1.7029 | -120.0394
3272.3906 | 121.4355 | -1.3596 | 120.195 | -0.0086212 | 0.0090278 | 0.055613 | 0.0034158 | 0.0029737 | 0.00093576 | -0.0046526 | 0.0069425 | -0.0047124 | 0.0044284 | -0.0032728 | -0.0081305 | 0.018824 | 0.045776 | 0.11444 | 0.086975 | 0.11444 | 0.14191 | -0.018311 | -0.16022 | 0.045776 | 0.068665 | -0.041199 | 0.050354 | 0.032043 | -0.073242 | -0.11444 | 1.3412 | 1.1993 | -120.0531 | 1.474 | 1.474 | 0.27466 | -120.1492 | 1.2863 | 1.2451 | -120.1447 | 1.4053 | 1.3184 | 0.073242 | -120.163 | 1.5015 | 1.4053 | 1.4465 | -120.3552 | 1.4099 | 1.3916 | 1.4282 | -120.3094
3274.1562 | 121.5225 | -1.4145 | 120.0943 | -0.00099167 | 0.013727 | 0.053904 | 0.0070474 | 0.0027601 | -0.00034604 | -0.0070026 | 0.0069425 | -0.0027898 | 0.004642 | -0.003059 | -0.01048 | 0.019252 | 0 | 0.032043 | 0.013733 | 0.07782 | 0.17853 | -0.045776 | -0.21057 | -0.064087 | 0 | -0.13275 | 0.073242 | 0.07782 | -0.091553 | -0.17395 | 1.3687 | 1.2039 | -119.9158 | 1.4465 | 1.4923 | 0.28839 | -120.0943 | 1.3229 | 1.2405 | -120.0211 | 1.3504 | 1.2817 | 0.041199 | -120.0165 | 1.593 | 1.4145 | 1.4282 | -120.3049 | 1.4877 | 1.4923 | 1.4145 | -120.2682
3275.8438 | 121.6278 | -1.3504 | 120.1538 | -0.00099167 | 0.014582 | 0.053476 | 0.0083292 | 0.0014783 | 0.0034992 | -0.0065752 | -0.00068649 | -0.0023626 | 0.0084872 | -0.00049559 | -0.010053 | 0.015834 | -0.018311 | -0.027466 | -0.036621 | 0.059509 | 0.19226 | -0.064087 | -0.21057 | -0.041199 | -0.013733 | -0.14191 | 0.091553 | 0.09613 | -0.09613 | -0.16022 | 1.2863 | 1.1398 | -119.9615 | 1.3229 | 1.4099 | 0.27008 | -120.1721 | 1.2543 | 1.1902 | -120.0623 | 1.3092 | 1.2085 | 0.01831 | -120.0577 | 1.5427 | 1.3321 | 1.3138 | -120.3644 | 1.442 | 1.4465 | 1.3367 | -120.314
3277.5938 | 120.7214 | -120.5795 | 0.19226 | 0.0066373 | 0.010096 | 0.054331 | 0.0034158 | 0.0023327 | 0.0034992 | -0.0040118 | 0.0069425 | -0.0064214 | 0.0042148 | -0.0024182 | -0.010694 | 0.021388 | 0.10986 | 0.14191 | 0.12817 | 0.16022 | 0.17853 | 0.036621 | -0.13275 | 0.086975 | 0.1236 | 0.022888 | 0.082397 | 0.082397 | -0.018311 | -0.068665 | 120.6161 | 120.4468 | -0.013733 | 120.7214 | 120.7397 | 0.29297 | -0.082398 | 120.5612 | 120.5109 | -0.10986 | 120.6665 | 120.6024 | 0.091553 | -0.10986 | 120.7581 | 120.6894 | 120.7077 | -0.32501 | 120.6619 | 120.6619 | 120.7031 | -0.26093
3279.2969 | 121.1105 | -120.7947 | 0.1831 | 0.0066373 | 0.010737 | 0.054758 | 0.0070474 | 0.0016919 | -0.0044048 | -0.0084978 | -0.008316 | -0.0057806 | 0.0050694 | -0.0017774 | -0.013258 | 0.020747 | 0.09613 | 0.15106 | 0.11902 | 0.1831 | 0.21973 | 0.013733 | -0.1236 | 0.082397 | 0.16479 | 0.036621 | 0.086975 | 0.086975 | -0.009155 | -0.086975 | 120.8084 | 120.6711 | 0.036622 | 120.9457 | 120.9778 | 0.3067 | -0.086975 | 120.7855 | 120.7077 | -0.09613 | 120.8771 | 120.8313 | 0.1236 | -0.09613 | 121.0144 | 120.8908 | 120.9137 | -0.3067 | 120.8817 | 120.8817 | 120.9595 | -0.27008
3281.0625 | 121.0831 | -120.9366 | 0.18768 | 0.0066373 | 0.0133 | 0.05134 | 0.0042702 | 0.0036145 | 0.0017902 | -0.00508 | -0.00068649 | -0.0047124 | 0.0031468 | -0.0024182 | -0.010694 | 0.019465 | 0.12817 | 0.13275 | 0.13733 | 0.16022 | 0.16937 | 0.018311 | -0.12817 | 0.091553 | 0.12817 | 0.013733 | 0.09613 | 0.064087 | -0.022888 | -0.073242 | 120.9549 | 120.8084 | -0.01831 | 121.0693 | 121.0968 | 0.28839 | -0.059509 | 120.9137 | 120.8633 | -0.091553 | 121.0281 | 120.9503 | 0.086975 | -0.1236 | 121.106 | 121.0648 | 121.0739 | -0.31586 | 121.0327 | 121.0007 | 121.0648 | -0.26092
3282.8125 | 121.1243 | -120.9869 | 0.20599 | 0.0066373 | 0.014796 | 0.053049 | 0.0053384 | 0.0025465 | 0.0039264 | -0.0037982 | 0.0069425 | 0.00084176 | 0.0057102 | -0.0049816 | -0.0087713 | 0.019038 | 0.009155 | -0.054932 | -0.041199 | 0.07782 | 0.23346 | -0.027466 | -0.17853 | -0.009155 | -0.032043 | -0.14191 | 0.14191 | 0.11902 | -0.041199 | -0.11902 | 120.9595 | 120.8084 | 0.027465 | 120.932 | 121.0648 | 0.25635 | -0.19684 | 120.9457 | 120.8679 | -0.064087 | 120.9778 | 120.845 | -0.022888 | -0.086975 | 121.2204 | 120.9961 | 120.9457 | -0.38452 | 121.1288 | 121.106 | 120.9549 | -0.32501
3284.5625 | 121.3074 | -120.9915 | 0.17395 | 0.0066373 | 0.017786 | 0.051126 | 0.0087564 | 0.0040417 | 0.0032856 | -0.0031574 | 0.022202 | -1.2844e-05 | 0.0072056 | -0.0011364 | -0.01048 | 0.019465 | 0.027466 | 0.027466 | 0.018311 | 0.1236 | 0.22888 | -0.022888 | -0.16937 | 0.004578 | 0.059509 | -0.082397 | 0.13733 | 0.11444 | -0.059509 | -0.10529 | 120.9686 | 120.8221 | 0.054932 | 121.019 | 121.1151 | 0.29297 | -0.14648 | 120.932 | 120.8862 | -0.036621 | 120.9961 | 120.9091 | 0.022889 | -0.059509 | 121.2204 | 121.019 | 121.0098 | -0.34332 | 121.1288 | 121.106 | 121.051 | -0.27924
3286.25 | 121.3211 | -120.9686 | 0.17853 | 0.014267 | 0.012232 | 0.054331 | 0.0081154 | 0.0031873 | -0.0039776 | -0.0042254 | 0.0069425 | -0.005567 | 0.0044284 | -0.0026318 | -0.014753 | 0.021174 | 0.07782 | 0.16937 | 0.14191 | 0.16937 | 0.18768 | 0.022888 | -0.12817 | 0.086975 | 0.16022 | 0.041199 | 0.082397 | 0.082397 | -0.018311 | -0.073242 | 120.9915 | 120.8405 | 0.009155 | 121.138 | 121.138 | 0.29755 | -0.10071 | 120.9503 | 120.8954 | -0.096131 | 121.0556 | 121.0098 | 0.11444 | -0.096131 | 121.1563 | 121.0464 | 121.1105 | -0.3067 | 121.051 | 121.051 | 121.1288 | -0.25177
3288 | 121.1929 | -121.0922 | 0.20142 | 0.0066373 | 0.0075324 | 0.052195 | 0.0036294 | 0.0025465 | -0.0012006 | -0.0052936 | -0.008316 | -0.0059942 | 0.0040012 | -0.0034864 | -0.0074897 | 0.020961 | 0.082397 | 0.14191 | 0.10529 | 0.15106 | 0.17853 | 0.018311 | -0.1236 | 0.054932 | 0.091553 | -0.009155 | 0.10529 | 0.10071 | -0.018311 | -0.07782 | 121.1105 | 120.9686 | -0.022888 | 121.2341 | 121.2433 | 0.27466 | -0.11902 | 121.0739 | 121.0144 | -0.09613 | 121.1472 | 121.0831 | 0.068665 | -0.10071 | 121.2708 | 121.1746 | 121.1975 | -0.32501 | 121.1975 | 121.1929 | 121.1838 | -0.27924
3289.7031 | 121.3715 | -121.051 | 0.16937 | -0.00099167 | 0.01565 | 0.054117 | 0.0046976 | 0.0034009 | 0.0052082 | -0.0042254 | 0.0069425 | -0.00065364 | 0.006351 | -0.0015638 | -0.0068487 | 0.018611 | 0.032043 | 0.050354 | 0.013733 | 0.12817 | 0.23346 | -0.027466 | -0.16479 | 0.018311 | 0.073242 | -0.082397 | 0.14191 | 0.10529 | -0.050354 | -0.10529 | 121.0236 | 120.8862 | 0.064086 | 121.1014 | 121.1792 | 0.29297 | -0.13733 | 121.0007 | 120.9457 | -0.027466 | 121.0693 | 120.9686 | 0.022889 | -0.064087 | 121.2845 | 121.0831 | 121.0648 | -0.33417 | 121.1929 | 121.1563 | 121.1243 | -0.27466
3291.4531 | 121.2845 | -121.1105 | 0.21973 | -0.00099167 | 0.010523 | 0.051767 | 0.0053384 | -0.0017261 | 0.001363 | -0.004439 | 0.0069425 | -0.0044988 | 0.0037876 | -0.0026318 | -0.0079169 | 0.019252 | 0.10529 | 0.12817 | 0.1236 | 0.1831 | 0.1831 | 0.027466 | -0.1236 | 0.07782 | 0.12817 | 0.009155 | 0.082397 | 0.082397 | -0.009155 | -0.068665 | 121.138 | 120.9869 | -0.036622 | 121.2387 | 121.2936 | 0.3067 | -0.11444 | 121.1014 | 121.0419 | -0.13733 | 121.1884 | 121.1197 | 0.07782 | -0.13733 | 121.2936 | 121.2158 | 121.2341 | -0.34332 | 121.1929 | 121.1929 | 121.2387 | -0.28839
3293.2031 | 121.3257 | -121.1243 | 0.21057 | 0.0066373 | 0.015223 | 0.051126 | 0.0053384 | 0.0034009 | 0.00414 | -0.0023028 | -0.00068649 | -0.0019354 | 0.0061374 | -0.0051954 | -0.0087713 | 0.01797 | 0.013733 | -0.036621 | -0.018311 | 0.091553 | 0.2243 | -0.018311 | -0.17395 | -0.022888 | -0.041199 | -0.1236 | 0.13733 | 0.13275 | -0.054932 | -0.10986 | 121.106 | 120.9503 | 0.013733 | 121.0876 | 121.2158 | 0.2655 | -0.19684 | 121.0693 | 121.0144 | -0.073242 | 121.1014 | 121.0007 | -0.013733 | -0.07782 | 121.3486 | 121.138 | 121.106 | -0.38452 | 121.2616 | 121.257 | 121.0831 | -0.32043
3294.9844 | 121.4218 | -121.0968 | 0.16937 | 0.0066373 | 0.011591 | 0.052835 | 0.0085428 | 0.0036145 | 0.0028584 | -0.0046526 | -0.00068649 | -0.00044004 | 0.0048556 | -0.0013502 | -0.0091985 | 0.019679 | 0.018311 | 0.009155 | 0 | 0.10986 | 0.21515 | -0.018311 | -0.16937 | -0.018311 | 0.050354 | -0.086975 | 0.14191 | 0.11444 | -0.073242 | -0.10071 | 121.0785 | 120.9274 | 0.045776 | 121.106 | 121.2067 | 0.27924 | -0.15106 | 121.0236 | 120.9961 | -0.027466 | 121.0785 | 121.0098 | 0.013733 | -0.054932 | 121.312 | 121.1151 | 121.0968 | -0.33875 | 121.2387 | 121.2112 | 121.1472 | -0.27008
3296.6719 | 121.4539 | -121.1563 | 0.19684 | -0.00099167 | 0.015009 | 0.053263 | 0.0076882 | 0.0036145 | 0.0043536 | -0.0040118 | 0.014572 | -0.003858 | 0.0095554 | -6.8386e-05 | -0.010053 | 0.01797 | 0.045776 | 0.050354 | 0.036621 | 0.11902 | 0.21515 | -0.022888 | -0.16479 | 0.013733 | 0.07782 | -0.07782 | 0.13275 | 0.1236 | -0.045776 | -0.10529 | 121.1334 | 120.9915 | 0.018311 | 121.2067 | 121.2753 | 0.28381 | -0.15106 | 121.1105 | 121.051 | -0.064087 | 121.17 | 121.0785 | 0.027466 | -0.073242 | 121.3715 | 121.2021 | 121.1929 | -0.36163 | 121.2891 | 121.2799 | 121.2341 | -0.30212
3298.4219 | 121.4355 | -121.1563 | 0.16937 | -0.00099167 | 0.016077 | 0.053476 | 0.010679 | 0.0029737 | -0.00034604 | -0.0048662 | 0.014572 | -0.0023626 | 0.00806 | -0.0032728 | -0.01283 | 0.020747 | -0.032043 | 0.022888 | 0 | 0.073242 | 0.22888 | -0.032043 | -0.19226 | -0.041199 | 0.013733 | -0.11444 | 0.1236 | 0.12817 | -0.059509 | -0.1236 | 121.1243 | 120.9641 | 0.059509 | 121.1792 | 121.2296 | 0.2655 | -0.20142 | 121.0968 | 121.0327 | -0.045777 | 121.1151 | 121.0419 | 0.009155 | -0.041199 | 121.3852 | 121.1243 | 121.1563 | -0.36163 | 121.2799 | 121.2845 | 121.17 | -0.29297
3300.125 | 121.3394 | -121.2112 | 0.21973 | 0.0066373 | 0.015436 | 0.050272 | 0.0085428 | 0.0012647 | 0.0020038 | -0.0042254 | 0.0069425 | -0.0015082 | 0.00806 | -0.0024182 | -0.0087713 | 0.020961 | 0.018311 | 0.009155 | 0 | 0.10071 | 0.21515 | -0.009155 | -0.17853 | -0.032043 | 0 | -0.13733 | 0.12817 | 0.11902 | -0.050354 | -0.12817 | 121.2021 | 121.0327 | -0.004578 | 121.2204 | 121.312 | 0.27924 | -0.20142 | 121.1609 | 121.0831 | -0.091553 | 121.1792 | 121.0739 | -0.009155 | -0.10071 | 121.4264 | 121.2296 | 121.2112 | -0.39826 | 121.3394 | 121.3303 | 121.2112 | -0.3479
3301.875 | 121.4859 | -121.1884 | 0.16022 | -0.016251 | 0.015436 | 0.052622 | 0.010252 | 0.0038281 | -0.00013244 | -0.006148 | 0.0069425 | -0.0036444 | 0.0057102 | -0.00028199 | -0.011976 | 0.019038 | -0.032043 | 0 | -0.009155 | 0.082397 | 0.25177 | -0.027466 | -0.17395 | -0.041199 | 0 | -0.10529 | 0.13733 | 0.11444 | -0.059509 | -0.1236 | 121.1609 | 121.0144 | 0.091553 | 121.1884 | 121.2708 | 0.25635 | -0.19226 | 121.1288 | 121.0648 | -0.022888 | 121.1472 | 121.0831 | 0.01831 | -0.045776 | 121.4401 | 121.1563 | 121.1792 | -0.33417 | 121.3257 | 121.3028 | 121.1884 | -0.28381
3303.625 | 121.4127 | -121.2067 | 0.21057 | -0.00099167 | 0.0066778 | 0.054972 | 0.0034158 | 0.00041006 | -0.0063274 | -0.0070026 | -0.008316 | -0.0059942 | 0.0040012 | -0.0037 | -0.013685 | 0.021815 | 0.004578 | 0.054932 | 0.07782 | 0.11902 | 0.20599 | 0.004578 | -0.12817 | 0.013733 | 0.064087 | -0.018311 | 0.10071 | 0.091553 | -0.018311 | -0.1236 | 121.2112 | 121.0785 | -0.004577 | 121.2616 | 121.3257 | 0.24719 | -0.20599 | 121.1884 | 121.0831 | -0.10986 | 121.2204 | 121.1884 | 0.10528 | -0.11902 | 121.4127 | 121.2112 | 121.2845 | -0.33875 | 121.3074 | 121.2982 | 121.2708 | -0.33417
3305.3281 | 121.4539 | -121.2158 | 0.18768 | 0.0066373 | 0.013727 | 0.058176 | 0.0074746 | 0.0019055 | -0.00098684 | -0.0059344 | -0.00068649 | -0.0057806 | 0.0061374 | -0.0039136 | -0.013044 | 0.018611 | 0.064087 | 0.11902 | 0.10071 | 0.16022 | 0.19684 | 0.004578 | -0.15564 | 0 | 0.086975 | -0.041199 | 0.091553 | 0.09613 | -0.032043 | -0.10529 | 121.2204 | 121.0602 | 0.009155 | 121.3348 | 121.376 | 0.31586 | -0.1236 | 121.1838 | 121.1105 | -0.09613 | 121.2158 | 121.1746 | 0.064087 | -0.091553 | 121.4127 | 121.2799 | 121.3165 | -0.34332 | 121.3074 | 121.3119 | 121.3028 | -0.29297
3307.0938 | 121.4905 | -121.2158 | 0.1831 | 0.0066373 | 0.011805 | 0.054117 | 0.0091836 | 0.0034009 | -0.0048322 | -0.0046526 | 0.0069425 | -0.006635 | 0.006992 | -0.0032728 | -0.013685 | 0.020533 | 0.018311 | 0.068665 | 0.073242 | 0.13275 | 0.21057 | 0.018311 | -0.14191 | 0.027466 | 0.082397 | -0.009155 | 0.10071 | 0.10529 | -0.018311 | -0.073242 | 121.2341 | 121.0739 | 0.027466 | 121.2845 | 121.3486 | 0.27466 | -0.16479 | 121.1975 | 121.1426 | -0.082397 | 121.2433 | 121.2067 | 0.064087 | -0.077819 | 121.4264 | 121.2341 | 121.2891 | -0.32501 | 121.3165 | 121.3211 | 121.2982 | -0.25635
3308.7969 | 121.5225 | -121.2204 | 0.17395 | 0.0066373 | 0.011591 | 0.055826 | 0.0098244 | 0.0021191 | -0.0016278 | -0.0063616 | 0.0069425 | -0.0064214 | 0.0061374 | -0.0028454 | -0.012403 | 0.01797 | 0.10529 | 0.16022 | 0.14191 | 0.17395 | 0.20142 | 0.027466 | -0.13275 | 0.07782 | 0.16022 | 0.041199 | 0.10071 | 0.082397 | -0.013733 | -0.07782 | 121.2479 | 121.0876 | 0.027466 | 121.3806 | 121.3943 | 0.3067 | -0.068664 | 121.2067 | 121.1426 | -0.073242 | 121.2982 | 121.2616 | 0.11902 | -0.091553 | 121.4218 | 121.3257 | 121.3623 | -0.3067 | 121.3211 | 121.3028 | 121.3806 | -0.25177
3310.5625 | 121.5546 | -121.2387 | 0.17853 | 0.0066373 | 0.0133 | 0.054331 | 0.0079018 | 0.0029737 | 0.00029476 | -0.0048662 | 0.0069425 | -0.0012946 | 0.0078464 | -6.8386e-05 | -0.011976 | 0.016047 | 0.018311 | 0.004578 | -0.018311 | 0.07782 | 0.22888 | -0.032043 | -0.17853 | -0.032043 | 0.018311 | -0.11444 | 0.13275 | 0.13275 | -0.050354 | -0.11902 | 121.2067 | 121.0602 | 0.050354 | 121.2433 | 121.3165 | 0.25635 | -0.16022 | 121.1884 | 121.1197 | -0.045777 | 121.2067 | 121.1243 | 0.004578 | -0.045777 | 121.4676 | 121.257 | 121.2204 | -0.35706 | 121.3715 | 121.3715 | 121.257 | -0.29755
3312.3281 | 121.4401 | -121.2479 | 0.21057 | -0.0086212 | 0.0096686 | 0.05369 | 0.0042702 | 0.0048963 | 0.00072196 | -0.00508 | 0.0069425 | -0.0032172 | 0.0037876 | -0.0017774 | -0.0087713 | 0.020106 | 0.09613 | 0.13275 | 0.13275 | 0.17853 | 0.19226 | 0.018311 | -0.11444 | 0.091553 | 0.11902 | 0.004578 | 0.082397 | 0.091553 | -0.032043 | -0.07782 | 121.2662 | 121.1334 | -0.01831 | 121.3806 | 121.4264 | 0.29297 | -0.11444 | 121.2158 | 121.17 | -0.12817 | 121.3394 | 121.2524 | 0.082398 | -0.11902 | 121.4401 | 121.344 | 121.3806 | -0.32501 | 121.3303 | 121.3394 | 121.3669 | -0.28839
3314.0156 | 121.4355 | -121.2799 | 0.21973 | 0.0066373 | 0.010737 | 0.052835 | 0.002775 | 0.0034009 | 0.0011494 | -0.006148 | -0.00068649 | -0.003858 | 0.003574 | -0.0039136 | -0.0094123 | 0.02032 | 0.086975 | 0.16937 | 0.12817 | 0.16022 | 0.16937 | 0.009155 | -0.1236 | 0.07782 | 0.10529 | 0.009155 | 0.10529 | 0.082397 | -0.018311 | -0.068665 | 121.2891 | 121.1563 | -0.050354 | 121.4493 | 121.4401 | 0.28381 | -0.13275 | 121.2616 | 121.2112 | -0.11444 | 121.3577 | 121.2891 | 0.07782 | -0.13733 | 121.4493 | 121.3669 | 121.4081 | -0.34332 | 121.3852 | 121.3623 | 121.3852 | -0.28839
3315.7656 | 121.4767 | -121.2936 | 0.20599 | 0.0066373 | 0.012659 | 0.053904 | 0.0051248 | -0.00044434 | 0.0045674 | -0.0037982 | -0.00068649 | -0.0015082 | 0.006351 | -0.0022046 | -0.0066351 | 0.020747 | -0.009155 | -0.032043 | -0.045776 | 0.082397 | 0.2243 | -0.009155 | -0.17853 | -0.013733 | -0.041199 | -0.14648 | 0.13275 | 0.12817 | -0.059509 | -0.11902 | 121.2845 | 121.1151 | 0.01831 | 121.2616 | 121.376 | 0.26092 | -0.21515 | 121.2341 | 121.1746 | -0.073243 | 121.2799 | 121.1472 | -0.027465 | -0.07782 | 121.5179 | 121.2845 | 121.2479 | -0.38452 | 121.4264 | 121.4218 | 121.2524 | -0.32501
3317.5312 | 121.5775 | -121.2662 | 0.19226 | 0.0066373 | 0.011591 | 0.053476 | 0.0074746 | 0.0025465 | 0.002431 | -0.0042254 | -0.00068649 | -0.00086724 | 0.008701 | -0.0034864 | -0.0094123 | 0.018397 | 0.045776 | 0.07782 | 0.032043 | 0.12817 | 0.21057 | -0.013733 | -0.16479 | 0.018311 | 0.064087 | -0.086975 | 0.11444 | 0.10071 | -0.036621 | -0.10986 | 121.2524 | 121.1014 | 0.01831 | 121.344 | 121.3943 | 0.29297 | -0.14648 | 121.2296 | 121.1563 | -0.07782 | 121.2845 | 121.1792 | 0.022888 | -0.091553 | 121.4767 | 121.312 | 121.2982 | -0.35706 | 121.3806 | 121.3669 | 121.3303 | -0.30212
3319.2344 | 121.5408 | -121.2936 | 0.19226 | 0.014267 | 0.016077 | 0.054544 | 0.0081154 | 0.0014783 | 0.0045674 | -0.0025164 | -0.008316 | -0.0027898 | 0.0059238 | -0.0015638 | -0.0074897 | 0.020533 | 0.054932 | 0.086975 | 0.045776 | 0.1236 | 0.21973 | 0 | -0.16479 | 0.009155 | 0.073242 | -0.064087 | 0.14191 | 0.11444 | -0.045776 | -0.10986 | 121.2936 | 121.1288 | 0.027466 | 121.3806 | 121.4172 | 0.28839 | -0.13733 | 121.2479 | 121.1838 | -0.050354 | 121.3028 | 121.2296 | 0.045776 | -0.07782 | 121.5134 | 121.3486 | 121.3394 | -0.35706 | 121.4355 | 121.4081 | 121.3669 | -0.30212
3321 | 121.5958 | -121.2936 | 0.16022 | -0.0086212 | 0.0098822 | 0.054544 | 0.0085428 | 0.0016919 | -0.0056866 | -0.006148 | -0.015945 | -0.0085576 | 0.0048556 | -0.0034864 | -0.014753 | 0.022883 | 0.045776 | 0.11902 | 0.13733 | 0.14191 | 0.19226 | 0.022888 | -0.13733 | 0.064087 | 0.14191 | 0.027466 | 0.082397 | 0.09613 | -0.013733 | -0.068665 | 121.3165 | 121.1563 | 0.032044 | 121.4127 | 121.4355 | 0.27924 | -0.11444 | 121.2799 | 121.225 | -0.07782 | 121.3577 | 121.3211 | 0.096131 | -0.064087 | 121.4859 | 121.3394 | 121.431 | -0.29755 | 121.376 | 121.3898 | 121.4355 | -0.22888
3322.6875 | 121.5546 | -121.3257 | 0.18768 | 0.0066373 | 0.016718 | 0.050913 | 0.0083292 | -0.00087154 | 0.0045674 | -0.0046526 | -0.00068649 | -0.00044004 | 0.0076328 | -0.00028199 | -0.0096259 | 0.017756 | 0.07782 | 0.082397 | 0.036621 | 0.13275 | 0.21057 | -0.009155 | -0.16479 | 0.009155 | 0.041199 | -0.09613 | 0.11444 | 0.09613 | -0.027466 | -0.11902 | 121.3165 | 121.1609 | 0.022888 | 121.4081 | 121.4584 | 0.29755 | -0.10986 | 121.2982 | 121.2067 | -0.073242 | 121.3348 | 121.2296 | 0.022889 | -0.091553 | 121.5363 | 121.4035 | 121.3623 | -0.35248 | 121.4401 | 121.4218 | 121.3669 | -0.3067
3324.4375 | 121.669 | -121.3165 | 0.16479 | -0.00099167 | 0.012659 | 0.053476 | 0.011533 | 0.0031873 | -0.0044048 | -0.0055072 | -0.00068649 | -0.007276 | 0.004642 | -0.00049559 | -0.013898 | 0.020961 | 0.07782 | 0.15106 | 0.15564 | 0.19684 | 0.18768 | 0.032043 | -0.1236 | 0.07782 | 0.16937 | 0.059509 | 0.10986 | 0.068665 | -0.013733 | -0.07782 | 121.3486 | 121.1929 | 0.022888 | 121.4676 | 121.5134 | 0.32043 | -0.086975 | 121.3028 | 121.2387 | -0.054932 | 121.3943 | 121.376 | 0.13733 | -0.09613 | 121.5042 | 121.3943 | 121.4722 | -0.28839 | 121.4264 | 121.3852 | 121.4859 | -0.24261
3326.1875 | 120.4971 | -120.2316 | 0.15106 | -0.00099167 | 0.016505 | 0.05369 | 0.00897 | 0.0036145 | -0.00055964 | -0.0074298 | 0.0069425 | -0.0023626 | 0.00806 | -0.00092279 | -0.011976 | 0.018824 | -0.013733 | 0.018311 | -0.009155 | 0.082397 | 0.23804 | -0.032043 | -0.19684 | -0.045776 | 0.009155 | -0.11902 | 0.15564 | 0.1236 | -0.064087 | -0.10071 | 120.1996 | 120.0348 | 0.086975 | 120.2499 | 120.314 | 0.27924 | -0.16479 | 120.1675 | 120.1309 | 0.004578 | 120.1859 | 120.1126 | -0.018311 | -0.027466 | 120.4697 | 120.2179 | 120.2225 | -0.3479 | 120.3873 | 120.3552 | 120.2408 | -0.25177
3327.9375 | 121.1151 | -120.8817 | 0.16479 | -0.00099167 | 0.014368 | 0.055826 | 0.0068338 | -0.00087154 | -0.00098684 | -0.00508 | -0.00068649 | -0.0032172 | 0.006351 | -0.0041272 | -0.011976 | 0.018824 | 0.068665 | 0.13275 | 0.1236 | 0.17395 | 0.19684 | -0.009155 | -0.12817 | 0.036621 | 0.14191 | -0.018311 | 0.11444 | 0.10071 | -0.018311 | -0.091553 | 120.8725 | 120.7535 | 0.032043 | 121.0144 | 121.0556 | 0.30212 | -0.09613 | 120.8633 | 120.7901 | -0.050354 | 120.9183 | 120.8633 | 0.073242 | -0.064087 | 121.0785 | 120.9503 | 121.0052 | -0.29297 | 120.9961 | 120.9824 | 121.0236 | -0.25635
3329.7031 | 121.1792 | -121.0098 | 0.18768 | 0.0066373 | 0.013514 | 0.05369 | 0.0051248 | 0.0036145 | 0.00414 | -0.0037982 | 0.0069425 | -0.00086724 | 0.0076328 | -0.0026318 | -0.0074897 | 0.018184 | 0.009155 | -0.018311 | -0.027466 | 0.07782 | 0.22888 | -0.027466 | -0.15564 | -0.022888 | -0.022888 | -0.13275 | 0.15106 | 0.11444 | -0.050354 | -0.11902 | 120.9824 | 120.8542 | 0.041199 | 120.9915 | 121.0876 | 0.23346 | -0.17853 | 120.9595 | 120.8908 | -0.036621 | 120.9869 | 120.8771 | -0.013732 | -0.073242 | 121.2387 | 121.019 | 120.9824 | -0.34332 | 121.1609 | 121.1243 | 120.9869 | -0.3067
3331.4062 | 121.2433 | -121.0602 | 0.19226 | -0.00099167 | 0.015223 | 0.053904 | 0.0032022 | 0.0029737 | 0.0032856 | -0.0035846 | 0.0069425 | -0.00086724 | 0.005283 | -0.00092279 | -0.0066351 | 0.018184 | 0.068665 | 0.068665 | 0.032043 | 0.13275 | 0.19684 | -0.009155 | -0.16479 | 0.004578 | 0.059509 | -0.11902 | 0.11902 | 0.11902 | -0.045776 | -0.10529 | 121.051 | 120.8954 | 0.004577 | 121.1288 | 121.1929 | 0.29755 | -0.1236 | 121.0144 | 120.9549 | -0.073242 | 121.0648 | 120.9412 | -0.013733 | -0.073242 | 121.257 | 121.1288 | 121.0922 | -0.35706 | 121.1792 | 121.1792 | 121.1197 | -0.29755
3333.1719 | 121.3623 | -121.0144 | 0.16479 | 0.0066373 | 0.014796 | 0.054117 | 0.0051248 | 0.0044691 | -0.0016278 | -0.0025164 | -0.00068649 | -0.0019354 | 0.006351 | -0.0022046 | -0.0094123 | 0.019038 | 0.036621 | 0.036621 | 0.013733 | 0.11444 | 0.21515 | -0.013733 | -0.16479 | 0.018311 | 0.073242 | -0.073242 | 0.13733 | 0.12817 | -0.054932 | -0.11902 | 121.0007 | 120.8496 | 0.050354 | 121.051 | 121.1288 | 0.27924 | -0.12817 | 120.9595 | 120.8954 | -0.027466 | 121.0327 | 120.9412 | 0.045777 | -0.036621 | 121.2296 | 121.051 | 121.0281 | -0.32959 | 121.1517 | 121.1426 | 121.0876 | -0.28381
3334.875 | 121.3394 | -121.0922 | 0.16022 | -0.016251 | 0.014582 | 0.053904 | 0.0096108 | 0.0040417 | -0.003764 | -0.0046526 | 0.0069425 | -0.0049262 | 0.0061374 | -0.001991 | -0.01283 | 0.022456 | 0.018311 | 0.064087 | 0.045776 | 0.1236 | 0.21057 | 0 | -0.16479 | -0.036621 | 0.041199 | -0.082397 | 0.12817 | 0.12817 | -0.068665 | -0.11902 | 121.0922 | 120.9274 | 0.050354 | 121.1563 | 121.2158 | 0.28839 | -0.14191 | 121.0236 | 120.9732 | -0.032043 | 121.0556 | 121.0098 | 0.036622 | -0.032043 | 121.3028 | 121.1105 | 121.138 | -0.32501 | 121.2204 | 121.2204 | 121.1334 | -0.27924
3336.625 | 121.2799 | -121.1563 | 0.19226 | -0.00099167 | 0.0133 | 0.051767 | 0.0042702 | 0.0025465 | -0.0012006 | -0.0035846 | 0.0069425 | -0.0057806 | 0.0054966 | -0.001991 | -0.010053 | 0.019038 | 0.073242 | 0.13733 | 0.12817 | 0.15564 | 0.17853 | 0.013733 | -0.12817 | 0.064087 | 0.10529 | 0.018311 | 0.086975 | 0.086975 | -0.013733 | -0.086975 | 121.17 | 121.0281 | -0.013733 | 121.2936 | 121.312 | 0.28381 | -0.11902 | 121.1426 | 121.0693 | -0.10529 | 121.2204 | 121.1746 | 0.10529 | -0.10529 | 121.3348 | 121.2296 | 121.2845 | -0.32044 | 121.2433 | 121.2433 | 121.2616 | -0.27924
3338.3281 | 121.3257 | -121.1655 | 0.16937 | 0.0066373 | 0.012873 | 0.052835 | 0.0074746 | 0.0036145 | 0.0020038 | -0.0055072 | 0.0069425 | -0.0040716 | 0.005283 | -0.0037 | -0.0085577 | 0.019252 | 0.10986 | 0.1236 | 0.12817 | 0.17395 | 0.18768 | 0.018311 | -0.14191 | 0.082397 | 0.1236 | 0.022888 | 0.082397 | 0.07782 | -0.013733 | -0.064087 | 121.1838 | 121.0236 | 0.01831 | 121.2891 | 121.3394 | 0.31586 | -0.05951 | 121.1517 | 121.1014 | -0.086976 | 121.2479 | 121.1884 | 0.086975 | -0.091553 | 121.3531 | 121.2753 | 121.2936 | -0.31128 | 121.2479 | 121.2433 | 121.2891 | -0.23346
3340.0938 | 121.4127 | -121.1563 | 0.17395 | -0.00099167 | 0.010523 | 0.054544 | 0.00897 | 0.0023327 | -0.003764 | -0.0052936 | -0.008316 | -0.0064214 | 0.0057102 | -0.0017774 | -0.014539 | 0.020961 | 0.082397 | 0.15106 | 0.13275 | 0.19226 | 0.17853 | 0.004578 | -0.16022 | 0.068665 | 0.14191 | 0.022888 | 0.091553 | 0.086975 | -0.018311 | -0.07782 | 121.1609 | 120.9961 | 0.004578 | 121.3074 | 121.3486 | 0.35248 | -0.091553 | 121.138 | 121.0785 | -0.082397 | 121.225 | 121.1792 | 0.10071 | -0.086975 | 121.3348 | 121.2387 | 121.2891 | -0.33417 | 121.2479 | 121.2433 | 121.2982 | -0.25177
3341.8281 | 121.431 | -121.1609 | 0.19226 | -0.00099167 | 0.019923 | 0.051981 | 0.0081154 | 0.0021191 | 0.004781 | -0.006148 | 0.0069425 | -0.0010808 | 0.0076328 | -0.0017774 | -0.0070623 | 0.014979 | 0.086975 | 0.054932 | 0.041199 | 0.1236 | 0.22888 | 0 | -0.14648 | 0.022888 | 0.059509 | -0.086975 | 0.11902 | 0.11444 | -0.045776 | -0.091553 | 121.1609 | 121.0144 | 0.036621 | 121.2158 | 121.2845 | 0.27008 | -0.10529 | 121.1151 | 121.0693 | -0.073242 | 121.1838 | 121.0739 | 0.004578 | -0.07782 | 121.3898 | 121.2479 | 121.2021 | -0.33874 | 121.2799 | 121.2753 | 121.2204 | -0.28381
3343.5312 | 121.4035 | -121.1975 | 0.1831 | 0.0066373 | 0.015223 | 0.053049 | 0.0042702 | 0.00083746 | 0.0017902 | -0.0065752 | -0.00068649 | -0.003858 | 0.0050694 | -0.0056226 | -0.0070623 | 0.020106 | 0.004578 | 0.004578 | 0 | 0.086975 | 0.23346 | -0.013733 | -0.16479 | 0.018311 | 0.018311 | -0.082397 | 0.10986 | 0.11444 | -0.045776 | -0.09613 | 121.1838 | 121.0327 | 0.050354 | 121.2021 | 121.2845 | 0.25177 | -0.17853 | 121.1517 | 121.1014 | -0.073242 | 121.2158 | 121.1151 | 0.013733 | -0.068664 | 121.431 | 121.2021 | 121.1975 | -0.3479 | 121.3074 | 121.312 | 121.2158 | -0.27924
3345.2969 | 121.1746 | -121.0739 | 0.20142 | -0.00099167 | 0.012446 | 0.054117 | 0.007261 | 0.00041006 | -0.0039776 | -0.0080706 | -0.00068649 | -0.0059942 | 0.0065646 | -0.0041272 | -0.011976 | 0.019252 | 0.032043 | 0.09613 | 0.091553 | 0.12817 | 0.1831 | 0.004578 | -0.13275 | 0.036621 | 0.07782 | -0.018311 | 0.09613 | 0.091553 | -0.013733 | -0.09613 | 121.0785 | 120.9412 | -0.018311 | 121.17 | 121.2021 | 0.26093 | -0.16937 | 121.0602 | 120.9778 | -0.10529 | 121.1105 | 121.0556 | 0.077819 | -0.10986 | 121.257 | 121.106 | 121.1655 | -0.33417 | 121.17 | 121.1655 | 121.1517 | -0.29755
3347 | 121.2387 | -121.1517 | 0.21973 | 0.0066373 | 0.012659 | 0.05369 | 0.007261 | 0.0012647 | -0.002055 | -0.0080706 | -0.00068649 | -0.0044988 | 0.004642 | -0.001991 | -0.011121 | 0.02032 | 0.050354 | 0.073242 | 0.073242 | 0.12817 | 0.20142 | 0.009155 | -0.13275 | 0.045776 | 0.068665 | -0.027466 | 0.091553 | 0.091553 | -0.032043 | -0.086975 | 121.1609 | 121.019 | -0.018311 | 121.225 | 121.2799 | 0.26093 | -0.16937 | 121.1197 | 121.0648 | -0.12817 | 121.1975 | 121.1243 | 0.059509 | -0.12817 | 121.3531 | 121.2021 | 121.225 | -0.35248 | 121.2433 | 121.2433 | 121.2204 | -0.3067
3348.75 | 121.4218 | -121.1243 | 0.16937 | 0.014267 | 0.014582 | 0.05369 | 0.0061928 | 0.0053235 | 0.0034992 | -0.0063616 | -0.00068649 | -0.00065364 | 0.0082736 | -0.0013502 | -0.0081305 | 0.018184 | 0.050354 | 0.045776 | 0.032043 | 0.13275 | 0.2243 | -0.032043 | -0.16479 | 0.013733 | 0.064087 | -0.091553 | 0.13275 | 0.10071 | -0.059509 | -0.10071 | 121.0922 | 120.9595 | 0.054931 | 121.17 | 121.257 | 0.29755 | -0.11902 | 121.0648 | 121.0236 | -0.036622 | 121.138 | 121.0327 | 0.009155 | -0.068665 | 121.3486 | 121.1746 | 121.1563 | -0.33417 | 121.257 | 121.225 | 121.1884 | -0.27008
3350.5156 | 121.3165 | -121.1609 | 0.21057 | -0.00099167 | 0.012873 | 0.053904 | 0.0057656 | 0.0019055 | -0.00055964 | -0.004439 | 0.0069425 | -0.0053534 | 0.0059238 | -0.0039136 | -0.0091985 | 0.018824 | 0.086975 | 0.1236 | 0.1236 | 0.17395 | 0.16937 | 0.036621 | -0.11902 | 0.082397 | 0.12817 | 0.004578 | 0.082397 | 0.073242 | -0.022888 | -0.068665 | 121.1975 | 121.0419 | -0.041198 | 121.2845 | 121.3348 | 0.29297 | -0.1236 | 121.138 | 121.0922 | -0.12817 | 121.2433 | 121.1655 | 0.073243 | -0.13733 | 121.3303 | 121.2479 | 121.2845 | -0.32959 | 121.2433 | 121.2341 | 121.2891 | -0.27924
3352.2188 | 121.4401 | -121.1792 | 0.16937 | -0.00099167 | 0.013727 | 0.055185 | 0.0057656 | 0.00062386 | -0.0039776 | -0.0072162 | 0.014572 | -0.0047124 | 0.0061374 | -0.0037 | -0.011762 | 0.019465 | 0.09613 | 0.15564 | 0.15106 | 0.16937 | 0.18768 | 0.004578 | -0.13275 | 0.059509 | 0.15106 | 0.032043 | 0.082397 | 0.064087 | -0.009155 | -0.091553 | 121.1838 | 121.0464 | 0.01831 | 121.3348 | 121.3486 | 0.30212 | -0.073243 | 121.17 | 121.0876 | -0.086976 | 121.2387 | 121.2112 | 0.1236 | -0.10529 | 121.3669 | 121.2753 | 121.3303 | -0.30212 | 121.2616 | 121.2433 | 121.3303 | -0.26093
3353.9688 | 121.3394 | -121.2067 | 0.19684 | -0.00099167 | 0.010523 | 0.051981 | 0.0049112 | 0.0027601 | 0.0011494 | -0.003371 | -0.00068649 | -0.0070624 | 0.0040012 | -0.0034864 | -0.0081305 | 0.020747 | 0.09613 | 0.12817 | 0.11902 | 0.14648 | 0.17853 | 0.027466 | -0.15106 | 0.059509 | 0.09613 | 0 | 0.10529 | 0.07782 | -0.027466 | -0.09613 | 121.2341 | 121.0556 | -0.01831 | 121.3348 | 121.3531 | 0.29755 | -0.10071 | 121.1792 | 121.1105 | -0.091552 | 121.2662 | 121.2067 | 0.09613 | -0.11902 | 121.3852 | 121.3028 | 121.3257 | -0.3479 | 121.312 | 121.2845 | 121.3028 | -0.29297
3355.6719 | 121.463 | -121.1975 | 0.18768 | 0.0066373 | 0.013941 | 0.054544 | 0.0091836 | 0.0034009 | -0.00098684 | -0.006148 | 0.0069425 | -0.0030034 | 0.0040012 | -0.005409 | -0.011121 | 0.017115 | 0.10529 | 0.11902 | 0.11902 | 0.17853 | 0.18768 | 0.022888 | -0.15106 | 0.050354 | 0.11902 | -0.036621 | 0.09613 | 0.10529 | -0.022888 | -0.091553 | 121.2204 | 121.0464 | 0 | 121.3165 | 121.376 | 0.32959 | -0.082397 | 121.1746 | 121.106 | -0.091553 | 121.2479 | 121.1609 | 0.054932 | -0.082397 | 121.3852 | 121.3028 | 121.3165 | -0.33874 | 121.2936 | 121.3028 | 121.3165 | -0.27924
3357.4375 | 121.5363 | -121.1792 | 0.1831 | -0.0086212 | 0.011591 | 0.053049 | 0.0079018 | 0.0034009 | -0.0022686 | -0.0076434 | -0.008316 | -0.0044988 | 0.0084872 | -0.004768 | -0.011762 | 0.01797 | 0.10986 | 0.13733 | 0.1236 | 0.16022 | 0.19684 | 0.041199 | -0.11902 | 0.09613 | 0.16022 | 0.041199 | 0.091553 | 0.10071 | -0.027466 | -0.068665 | 121.2204 | 121.0602 | 0.013733 | 121.3165 | 121.3394 | 0.27924 | -0.073242 | 121.1517 | 121.1105 | -0.091552 | 121.2753 | 121.2204 | 0.10986 | -0.082397 | 121.376 | 121.2891 | 121.3028 | -0.30212 | 121.2708 | 121.2799 | 121.3394 | -0.25177
3359.1875 | 121.3898 | -121.2753 | 0.23346 | -0.0086212 | 0.0086006 | 0.054544 | 0.0025612 | 0.0051099 | 0.00029476 | -0.006148 | 0.0069425 | -0.0025762 | 0.0033604 | -0.003059 | -0.0089849 | 0.019038 | 0.11902 | 0.12817 | 0.11902 | 0.15564 | 0.18768 | 0.022888 | -0.12817 | 0.068665 | 0.10071 | -0.009155 | 0.086975 | 0.068665 | -0.027466 | -0.091553 | 121.2982 | 121.1472 | -0.045776 | 121.4035 | 121.431 | 0.28381 | -0.11444 | 121.2479 | 121.1838 | -0.14648 | 121.344 | 121.2662 | 0.082398 | -0.16479 | 121.463 | 121.3943 | 121.3943 | -0.36163 | 121.3623 | 121.344 | 121.376 | -0.32501
3360.9531 | 121.4264 | -121.2433 | 0.23346 | 0.0066373 | 0.011378 | 0.051767 | 0.0044838 | 0.0038281 | 8.1158e-05 | -0.0076434 | 0.0069425 | -0.0059942 | 0.0044284 | -0.0024182 | -0.0087713 | 0.018184 | 0.064087 | 0.10529 | 0.10529 | 0.1236 | 0.19226 | 0.018311 | -0.12817 | 0.045776 | 0.068665 | -0.022888 | 0.086975 | 0.073242 | -0.018311 | -0.082397 | 121.2616 | 121.1151 | -0.041198 | 121.3486 | 121.3669 | 0.25177 | -0.16937 | 121.225 | 121.1609 | -0.14648 | 121.2891 | 121.2204 | 0.059509 | -0.16022 | 121.4355 | 121.3074 | 121.3486 | -0.36163 | 121.3303 | 121.3165 | 121.312 | -0.31586
3362.7031 | 121.4905 | -121.2753 | 0.20599 | 0.0066373 | 0.016932 | 0.054758 | 0.0046976 | 0.0044691 | 0.00414 | -0.0059344 | -0.00068649 | -0.0017218 | 0.003574 | -0.0017774 | -0.0068487 | 0.017756 | 0.054932 | 0.004578 | 0 | 0.073242 | 0.24261 | -0.018311 | -0.16479 | 0.036621 | -0.004578 | -0.086975 | 0.10986 | 0.09613 | -0.041199 | -0.10071 | 121.257 | 121.1105 | 0.036621 | 121.2799 | 121.3486 | 0.23804 | -0.15106 | 121.2341 | 121.1746 | -0.096131 | 121.312 | 121.1884 | 0.013733 | -0.10986 | 121.5179 | 121.3303 | 121.2753 | -0.37079 | 121.3852 | 121.3715 | 121.2708 | -0.3067
3364.4688 | 121.5317 | -121.2433 | 0.18768 | -0.0086212 | 0.012232 | 0.054758 | 0.0091836 | 0.0010511 | -0.0012006 | -0.006148 | 0.014572 | -0.006635 | 0.006992 | -0.0032728 | -0.013471 | 0.019465 | 0.032043 | 0.059509 | 0.07782 | 0.12817 | 0.21057 | 0 | -0.14648 | 0.045776 | 0.07782 | -0.004578 | 0.10529 | 0.09613 | -0.022888 | -0.086975 | 121.2433 | 121.0968 | 0.022888 | 121.3028 | 121.3715 | 0.27466 | -0.15564 | 121.2204 | 121.1563 | -0.082397 | 121.2891 | 121.2387 | 0.082397 | -0.091553 | 121.4539 | 121.2753 | 121.3211 | -0.33417 | 121.3486 | 121.3394 | 121.3211 | -0.27466
3366.1719 | 121.5088 | -121.2799 | 0.19684 | 0.0066373 | 0.012446 | 0.052408 | 0.0059792 | 0.0044691 | 0.0052082 | -0.0046526 | -0.008316 | -0.0030034 | 0.004642 | -0.0011364 | -0.0079169 | 0.017756 | 0.041199 | 0.041199 | 0.036621 | 0.10529 | 0.22888 | -0.004578 | -0.15106 | 0.059509 | 0.068665 | -0.036621 | 0.09613 | 0.10529 | -0.022888 | -0.07782 | 121.2753 | 121.1288 | 0.032044 | 121.3211 | 121.3852 | 0.25635 | -0.15564 | 121.257 | 121.2021 | -0.10071 | 121.3394 | 121.2433 | 0.041199 | -0.091552 | 121.5088 | 121.3211 | 121.3165 | -0.3479 | 121.376 | 121.3852 | 121.3486 | -0.27466
3367.9219 | 121.582 | -121.3028 | 0.18768 | 0.0066373 | 0.017145 | 0.051981 | 0.0070474 | 0.0034009 | 0.00414 | -0.004439 | -0.00068649 | -0.00065364 | 0.005283 | -0.0037 | -0.0077033 | 0.018397 | 0.073242 | 0.07782 | 0.045776 | 0.1236 | 0.21515 | -0.027466 | -0.15106 | 0.032043 | 0.073242 | -0.082397 | 0.12817 | 0.11444 | -0.050354 | -0.10071 | 121.2753 | 121.1517 | 0.027466 | 121.3806 | 121.4264 | 0.27466 | -0.11444 | 121.2524 | 121.2021 | -0.059509 | 121.3348 | 121.2204 | 0.018311 | -0.073242 | 121.5179 | 121.376 | 121.3486 | -0.33874 | 121.431 | 121.4172 | 121.376 | -0.28839
3369.6094 | 121.4767 | -121.3257 | 0.20599 | 0.0066373 | 0.0066778 | 0.052835 | 0.0070474 | 0.00019646 | -0.0039776 | -0.0048662 | 0.014572 | -0.007276 | 0.0044284 | -0.0037 | -0.011335 | 0.022029 | 0.036621 | 0.09613 | 0.082397 | 0.10529 | 0.19226 | 0.013733 | -0.13733 | 0.041199 | 0.059509 | -0.027466 | 0.10986 | 0.086975 | -0.022888 | -0.10071 | 121.3394 | 121.1884 | -0.013733 | 121.4218 | 121.431 | 0.24262 | -0.16937 | 121.3028 | 121.225 | -0.096131 | 121.3669 | 121.2982 | 0.073242 | -0.11902 | 121.5179 | 121.3623 | 121.4081 | -0.34332 | 121.4355 | 121.4127 | 121.3852 | -0.3067
3371.3594 | 121.55 | -121.3348 | 0.21515 | -0.00099167 | 0.013514 | 0.054117 | 0.0049112 | 0.00083746 | 0.0032856 | -0.007857 | 0.0069425 | -0.0027898 | 0.005283 | -0.0034864 | -0.0089849 | 0.019038 | 0.027466 | 0.041199 | 0.032043 | 0.10529 | 0.21515 | 0.013733 | -0.15564 | 0.073242 | 0.064087 | -0.041199 | 0.10529 | 0.10529 | -0.018311 | -0.073242 | 121.3486 | 121.1792 | 0 | 121.376 | 121.4401 | 0.26093 | -0.18768 | 121.3165 | 121.2616 | -0.10986 | 121.4081 | 121.2936 | 0.032043 | -0.10986 | 121.55 | 121.3623 | 121.3669 | -0.37079 | 121.4401 | 121.4401 | 121.3989 | -0.28839

## Thermal Data
Fire Time | D Position - 3' | D Position - Middle | D Position - 7'
-0.9333 | 29.8408 | 39.0888 | 20.0061
0.0667 | 32.0066 | 42.3466 | 21.6258
1.0667 | 33.9033 | 46.2088 | 23.3999
2.0667 | 37.2101 | 50.2079 | 25.4017
3.0667 | 39.0939 | 54.1077 | 28.1734
4.0667 | 41.4162 | 57.5962 | 30.1215
5.0667 | 43.2746 | 61.2584 | 31.463
6.0667 | 45.4654 | 65.6862 | 33.8015
7.0667 | 47.8089 | 70.3938 | 35.5289
8.0667 | 50.4464 | 74.0309 | 37.3262
9.0667 | 53.0042 | 77.6917 | 39.2287
10.0667 | 54.8772 | 81.7783 | 42.127
11.0667 | 57.3767 | 85.4402 | 45.367
12.0667 | 59.9009 | 88.73 | 47.7212
13.0667 | 62.5485 | 93.1873 | 49.9095
14.0667 | 64.4155 | 96.0448 | 51.3737
15.0667 | 65.9682 | 98.39 | 52.0381
16.0667 | 67.4539 | 99.8424 | 53.3625
17.0667 | 69.718 | 102.5641 | 54.3371
18.0667 | 71.0703 | 103.8459 | 54.8776
19.0667 | 73.0866 | 106.7377 | 56.8632
20.0667 | 75.1274 | 109.6107 | 58.8067
21.0667 | 77.4333 | 110.793 | 60.4186
22.0667 | 79.7639 | 112.5564 | 62.204
23.0667 | 82.1442 | 113.7876 | 63.6373
24.0667 | 83.9821 | 115.4767 | 64.9257
25.0667 | 86.8868 | 117.0343 | 66.7037
26.0667 | 89.4059 | 117.8886 | 68.0656
27.0667 | 90.2617 | 119.3335 | 69.3511
28.0667 | 92.3184 | 120.5438 | 71.1555
29.0667 | 94.0489 | 121.6253 | 72.5791
30.0667 | 97.494 | 123.5 | 73.9462
31.0667 | 100.5085 | 125.3832 | 75.3184
32.0667 | 102.0465 | 126.6632 | 76.3994
33.0667 | 102.9079 | 129.09 | 77.9187
34.0667 | 103.9244 | 130.9514 | 79.1308
35.0667 | 105.474 | 133.1963 | 80.643
36.0667 | 107.2189 | 133.1506 | 81.3808
37.0667 | 107.5014 | 133.6263 | 81.4772
38.0667 | 108.0497 | 133.8395 | 81.3605
39.0667 | 108.3908 | 134.7158 | 82.5679
40.0667 | 109.1859 | 136.6345 | 82.9252
41.0667 | 109.6351 | 136.6561 | 83.5279
42.0667 | 110.713 | 137.1757 | 84.032
43.0667 | 112.001 | 138.1195 | 84.6314
44.0667 | 113.7529 | 140.4937 | 87.504
45.0667 | 114.7348 | 141.3175 | 88.37
46.0667 | 115.4069 | 141.5938 | 88.1566
47.0667 | 116.4483 | 142.6145 | 88.4321
48.0667 | 117.7042 | 144.1324 | 88.2036
49.0667 | 118.3989 | 144.7833 | 89.5392
50.0667 | 118.4928 | 145.4761 | 90.189
51.0667 | 119.7073 | 146.6232 | 90.8278
52.0667 | 119.797 | 146.0432 | 90.7298
53.0667 | 120.2009 | 146.3275 | 90.6006
54.0667 | 120.961 | 146.9322 | 90.8956
55.0667 | 121.7487 | 148.4362 | 91.5331
56.0667 | 122.3061 | 150.3459 | 93.2831
57.0667 | 123.2454 | 151.3383 | 94.5467
58.0667 | 124.2097 | 152.6512 | 94.1615
59.0667 | 125.6663 | 154.2074 | 97.1541
60.0667 | 125.9957 | 155.5789 | 99.2179
61.0667 | 125.8923 | 156.2959 | 100.0809
62.0667 | 125.8201 | 156.5133 | 102.6878
63.0667 | 126.0406 | 157.7295 | 103.674
64.0667 | 126.7697 | 158.977 | 104.7242
65.0667 | 126.8124 | 158.7958 | 106.226
66.0667 | 127.4312 | 159.0706 | 106.9575
67.0667 | 127.36 | 159.4326 | 106.7636
68.0667 | 127.9291 | 160.395 | 107.249
69.0667 | 128.7053 | 160.7018 | 109.6434
70.0667 | 129.0183 | 160.5983 | 109.6505
71.0667 | 129.647 | 161.687 | 112.1623
72.0667 | 129.8296 | 161.6641 | 112.8299
73.0667 | 130.0447 | 161.9689 | 113.0737
74.0667 | 130.1603 | 161.971 | 113.7714
75.0667 | 130.3636 | 162.061 | 114.0134
76.0667 | 130.6844 | 161.947 | 114.7204
77.0667 | 130.4081 | 161.6294 | 114.8477
78.0667 | 130.1037 | 159.9408 | 114.2555
79.0667 | 130.3636 | 160.2381 | 114.9545
80.0667 | 130.7101 | 161.2517 | 115.5899
81.0667 | 130.4213 | 160.6786 | 116.1092
82.0667 | 130.6282 | 161.1106 | 115.4392
83.0667 | 131.2559 | 162.6723 | 116.1658
84.0667 | 131.6273 | 162.8845 | 117.5102
85.0667 | 132.1012 | 163.1881 | 118.0192
86.0667 | 132.4757 | 163.6095 | 119.6377
87.0667 | 132.8682 | 164.2432 | 119.3805
88.0667 | 132.8743 | 164.8976 | 119.8775
89.0667 | 133.0047 | 164.4807 | 120.7374
90.0823 | 133.3906 | 165.863 | 122.2067
91.0667 | 134.3808 | 166.7357 | 123.0964
92.0667 | 134.4334 | 166.7343 | 124.8505
93.0667 | 134.6479 | 167.8628 | 125.6699
94.0667 | 134.7729 | 168.8926 | 126.3715
95.0667 | 134.7631 | 170.4674 | 126.5389
96.0667 | 135.7034 | 170.8718 | 128.0803
97.0667 | 135.5975 | 172.7445 | 129.5645
98.0667 | 136.9475 | 173.3791 | 130.229
99.0667 | 137.5046 | 174.7251 | 130.7899
100.0667 | 138.4248 | 175.8151 | 131.7246
101.0667 | 139.0486 | 176.9373 | 132.4712
102.0667 | 139.5325 | 177.9723 | 134.3668
103.0667 | 139.872 | 178.4296 | 134.6968
104.0667 | 140.3642 | 179.9645 | 134.0412
105.0667 | 140.6852 | 181.1204 | 133.5802
106.0667 | 141.5545 | 182.4406 | 134.2988
107.0667 | 141.9533 | 182.2618 | 135.9555
108.0667 | 142.2248 | 182.0916 | 137.9024
109.0667 | 142.5487 | 183.1919 | 138.184
110.0667 | 143.4938 | 183.0842 | 139.1357
111.0667 | 143.333 | 183.6174 | 139.333
112.0667 | 143.285 | 183.9482 | 138.1925
113.0667 | 142.8714 | 182.3009 | 138.1278
114.0667 | 142.4478 | 182.3049 | 137.7937
115.0667 | 142.0987 | 182.3382 | 137.1335
116.0667 | 142.4657 | 182.8648 | 137.3127
117.0667 | 142.7103 | 183.2105 | 137.3614
118.0667 | 142.5493 | 184.7117 | 137.0479
119.0667 | 142.7638 | 185.0832 | 136.4449
120.0667 | 142.8738 | 184.563 | 136.248
121.0667 | 142.8618 | 185.9212 | 135.0852
122.0667 | 142.8771 | 185.9103 | 134.8205
123.0667 | 142.9453 | 185.7058 | 134.9739
124.0667 | 143.0258 | 185.8907 | 135.1074
125.0667 | 142.675 | 187.312 | 135.7192
126.0979 | 142.7084 | 186.1934 | 136.4397
127.0823 | 142.7692 | 187.8237 | 137.7409
128.0667 | 142.9056 | 187.9764 | 137.5667
129.0667 | 142.6789 | 188.2344 | 138.7957
130.0823 | 142.8079 | 188.4202 | 138.911
131.0667 | 143.0407 | 188.1728 | 139.2234
132.0667 | 142.7084 | 186.7875 | 139.0942
133.0667 | 142.6612 | 186.0557 | 139.6614
134.0667 | 142.626 | 186.9424 | 140.556
135.0823 | 142.6791 | 186.5268 | 141.2052
136.0667 | 142.6334 | 186.5646 | 140.9408
137.0667 | 143.2309 | 187.3286 | 140.7956
138.0667 | 143.1963 | 187.2833 | 140.8082
139.0667 | 143.4183 | 187.6597 | 140.0271
140.0667 | 143.5453 | 187.6294 | 139.8885
141.0667 | 143.7175 | 186.4557 | 141.5391
142.0667 | 143.5212 | 185.8648 | 142.5168
143.0667 | 143.4544 | 185.5282 | 141.5313
144.0667 | 143.4069 | 184.0101 | 141.2377
145.0823 | 144.1377 | 184.9508 | 141.2867
146.0667 | 144.6806 | 185.098 | 141.8491
147.0667 | 145.9777 | 185.2448 | 142.9942
148.0667 | 146.4428 | 185.0911 | 143.8041
149.0667 | 146.7515 | 186.1376 | 145.0578
150.0667 | 147.4193 | 186.2894 | 145.6513
151.0667 | 148.2902 | 187.071 | 145.5592
152.0667 | 148.8212 | 188.8373 | 146.6345
153.0667 | 150.2311 | 189.6998 | 148.1802
154.0667 | 150.1704 | 190.1771 | 148.7912
155.0667 | 150.481 | 190.873 | 149.8501
156.0667 | 150.5219 | 191.0327 | 151.7635
157.0667 | 150.2218 | 191.1565 | 151.1875
158.0667 | 150.234 | 190.7044 | 151.9359
159.0667 | 149.6497 | 191.7887 | 151.6826
160.0667 | 149.7676 | 192.5136 | 152.53
161.0667 | 150.3131 | 191.9652 | 153.6458
162.0667 | 150.3817 | 192.0149 | 154.4141
163.0667 | 149.8946 | 192.2241 | 155.2954
164.0667 | 150.0063 | 193.6645 | 154.8576
165.0667 | 150.4397 | 193.6912 | 154.9591
166.0667 | 150.9062 | 193.692 | 155.1649
167.0667 | 151.4448 | 194.4091 | 155.1796
168.0667 | 151.2816 | 194.2855 | 154.8917
169.0667 | 150.908 | 194.32 | 154.9265
170.0667 | 150.872 | 195.2658 | 155.386
171.0667 | 150.766 | 195.4147 | 155.2239
172.0667 | 150.6703 | 194.5733 | 155.6719
173.0667 | 150.6155 | 195.382 | 155.5346
174.0667 | 150.9669 | 195.9981 | 156.0665
175.0667 | 151.3683 | 196.2901 | 157.8401
176.0667 | 151.2428 | 197.0672 | 158.0206
177.0667 | 151.3947 | 197.8165 | 159.3193
178.0823 | 151.2023 | 197.6447 | 159.0635
179.0823 | 151.5574 | 197.7155 | 158.5454
180.0667 | 151.7356 | 197.0034 | 159.1698
181.0667 | 152.1964 | 197.4706 | 157.8714
182.0667 | 152.134 | 197.2004 | 157.989
183.0667 | 152.7935 | 198.8676 | 157.6483
184.0667 | 154.0769 | 199.2402 | 156.6843
185.0667 | 154.4566 | 199.1533 | 156.7711
186.0667 | 156.9763 | 199.7812 | 156.8681
187.0667 | 157.0649 | 198.9532 | 157.5147
188.0667 | 157.0066 | 199.4751 | 157.8197
189.0667 | 157.0743 | 199.816 | 158.0757
190.0667 | 157.6751 | 202.4049 | 157.9238
191.0667 | 157.5028 | 204.2405 | 157.9164
192.0667 | 157.9076 | 203.078 | 158.1576
193.0667 | 158.3499 | 202.6118 | 157.5742
194.0667 | 157.9786 | 202.1561 | 157.6998
195.0667 | 157.424 | 201.2432 | 159.0302
196.0667 | 157.0032 | 202.2865 | 159.6904
197.0667 | 156.8608 | 201.6155 | 159.4109
198.0667 | 156.7133 | 201.7209 | 160.3784
199.0667 | 156.5956 | 201.0132 | 159.8382
200.0667 | 156.1172 | 199.6635 | 159.3378
201.0667 | 155.6974 | 199.1185 | 158.4623
202.0667 | 155.8533 | 199.1882 | 158.9304
203.0667 | 155.8513 | 198.6878 | 158.8182
204.0667 | 155.411 | 197.8779 | 159.1252
205.0667 | 155.2075 | 198.1316 | 159.6255
206.0667 | 155.517 | 199.4243 | 161.585
207.0667 | 157.0215 | 199.3744 | 162.4425
208.0667 | 158.0986 | 198.9 | 161.5367
209.0667 | 157.8209 | 198.8739 | 162.1293
210.0667 | 158.2844 | 199.2631 | 162.3662
211.0667 | 159.2855 | 198.4357 | 162.5452
212.0667 | 159.0718 | 197.0436 | 161.8554
213.0667 | 159.129 | 196.7577 | 161.3756
214.0667 | 159.0633 | 196.9317 | 161.1524
215.0667 | 158.9913 | 198.094 | 160.8782
216.0667 | 159.558 | 199.4234 | 161.4655
217.0667 | 159.2278 | 200.1793 | 162.9563
218.0667 | 160.7113 | 200.7839 | 164.1706
219.0667 | 160.9322 | 200.4951 | 164.4693
220.0667 | 161.0604 | 199.8955 | 164.3936
221.0667 | 161.0124 | 199.5703 | 164.2448
222.0667 | 160.7363 | 199.6939 | 163.5638
223.0667 | 160.9203 | 200.6792 | 163.5068
224.0667 | 161.8524 | 201.6866 | 164.5482
225.0667 | 163.0093 | 202.8931 | 164.7273
226.0667 | 162.8945 | 203.8919 | 164.9776
227.0667 | 164.5175 | 204.5013 | 165.5345
228.0667 | 164.4867 | 205.1859 | 165.708
229.0667 | 167.322 | 205.8853 | 165.238
230.0667 | 167.1136 | 206.2922 | 165.6379
231.0667 | 166.3044 | 205.0491 | 165.838
232.0667 | 167.2682 | 205.6148 | 166.5208
233.0667 | 166.8998 | 205.9965 | 167.3281
234.0667 | 166.0587 | 205.4716 | 167.5028
235.0667 | 165.7046 | 205.3178 | 167.1377
236.0667 | 165.3957 | 204.8017 | 167.778
237.0667 | 166.4603 | 204.7155 | 169.5616
238.0667 | 166.4835 | 204.7632 | 170.7907
239.0667 | 166.7686 | 204.6226 | 170.9558
240.0667 | 167.0488 | 204.422 | 171.347
241.0667 | 167.1778 | 204.1653 | 171.0458
242.0667 | 166.9042 | 204.3107 | 171.2998
243.0667 | 166.2857 | 203.9342 | 171.5243
244.0667 | 165.93 | 204.4512 | 171.5202
245.0667 | 165.4007 | 203.6058 | 171.2222
246.0667 | 164.7446 | 202.1194 | 170.1285
247.0667 | 164.132 | 201.7221 | 169.1373
248.0667 | 164.3149 | 202.6148 | 168.5197
249.0667 | 163.8511 | 202.1695 | 168.1275
250.0667 | 163.5672 | 200.8076 | 167.4512
251.0667 | 162.9913 | 200.0348 | 167.8772
252.0667 | 162.7815 | 200.7118 | 168.5668
253.0667 | 163.0504 | 200.5585 | 167.8211
254.0667 | 163.5794 | 200.5966 | 169.4229
255.0667 | 163.6204 | 201.5939 | 169.0067
256.0667 | 163.7408 | 202.4874 | 169.7391
257.0667 | 164.1918 | 203.4403 | 171.1689
258.0667 | 164.3974 | 204.0202 | 171.4653
259.0667 | 164.2618 | 203.2063 | 170.5204
260.0667 | 165.0597 | 202.9257 | 171.3264
261.0667 | 164.6861 | 202.8535 | 170.4503
262.0667 | 165.2418 | 203.2164 | 170.5448
263.0667 | 165.0808 | 203.1329 | 171.3601
264.0667 | 164.5702 | 203.6889 | 170.8684
265.0667 | 166.0408 | 203.8508 | 171.1066
266.0667 | 166.1001 | 203.4831 | 170.8015
267.0667 | 165.762 | 202.6966 | 169.5801
268.0667 | 165.6152 | 201.8337 | 169.5659
269.0667 | 165.3504 | 201.0967 | 169.1647
270.0667 | 165.0447 | 201.2325 | 169.3786
271.0667 | 165.031 | 201.7749 | 170.4089
272.0667 | 164.6605 | 202.7552 | 171.3325
273.0667 | 166.0323 | 202.7645 | 171.25
274.0667 | 167.9242 | 203.9368 | 171.0337
275.0667 | 168.384 | 204.9947 | 170.9811
276.0667 | 168.7123 | 205.3293 | 171.114
277.0667 | 168.3099 | 205.1837 | 171.7296
278.0667 | 168.5928 | 206.3169 | 171.4004
279.0667 | 168.838 | 207.5221 | 171.6363
280.0667 | 168.8276 | 208.3528 | 171.2097
281.0667 | 169.4743 | 208.2388 | 172.4579
282.0667 | 169.1965 | 208.9262 | 173.5418
283.0667 | 169.2713 | 208.3515 | 173.4707
284.0667 | 168.8073 | 208.4604 | 174.0629
285.0667 | 168.6436 | 208.4183 | 174.1879
286.0667 | 168.655 | 208.5189 | 174.9204
287.0667 | 168.9333 | 209.48 | 175.2776
288.0667 | 168.7289 | 209.5498 | 174.8799
289.0667 | 169.5926 | 210.2595 | 174.8554
290.0667 | 169.7667 | 210.5002 | 175.4299
291.0667 | 169.5957 | 210.138 | 174.0217
292.0667 | 169.5369 | 209.2354 | 174.6388
293.0667 | 169.869 | 208.9426 | 175.5155
294.0667 | 170.3319 | 209.3005 | 174.8833
295.0667 | 170.5101 | 208.8424 | 174.8997
296.0667 | 170.3744 | 207.8528 | 174.5147
297.0667 | 169.8368 | 208.6294 | 175.0451
298.0667 | 169.2565 | 208.273 | 174.6115
299.0667 | 168.8265 | 208.0686 | 173.4034
300.0667 | 168.6417 | 207.955 | 172.9069
301.0667 | 168.3867 | 206.5704 | 172.7102
302.0667 | 168.3862 | 206.8314 | 172.193
303.0823 | 168.3541 | 207.5274 | 172.8287
304.0823 | 168.431 | 207.116 | 173.1625
305.0667 | 169.3377 | 208.4775 | 173.1977
306.0667 | 168.8704 | 209.0031 | 173.7762
307.0667 | 169.2479 | 208.9694 | 172.5811
308.0667 | 170.6501 | 209.5676 | 173.5787
309.0667 | 171.9023 | 209.8152 | 175.4709
310.0667 | 171.9938 | 209.8858 | 175.0802
311.0667 | 173.6033 | 210.6891 | 174.7024
312.0667 | 174.5751 | 211.724 | 175.2286
313.0667 | 174.9093 | 212.2926 | 176.2286
314.0667 | 174.5019 | 212.0083 | 175.7729
315.0667 | 174.2364 | 212.1349 | 175.5891
316.0667 | 173.7861 | 212.8051 | 174.8023
317.0667 | 173.248 | 211.5142 | 174.6822
318.0667 | 172.5934 | 210.6465 | 173.8696
319.0667 | 171.9441 | 209.6323 | 173.6254
320.0667 | 171.7958 | 209.1922 | 173.5186
321.0667 | 171.5637 | 208.7045 | 176.022
322.0667 | 171.2205 | 208.1738 | 177.5171
323.0667 | 171.4276 | 208.6286 | 177.4008
324.0667 | 171.123 | 208.5866 | 178.1172
325.0667 | 171.3792 | 207.6999 | 178.1521
326.0667 | 171.1552 | 207.5641 | 177.7691
327.0667 | 171.1357 | 208.3746 | 178.8035
328.0667 | 172.4174 | 208.3313 | 178.6926
329.0667 | 173.2447 | 208.2683 | 177.8426
330.0667 | 173.3005 | 208.8875 | 177.6276
331.0667 | 172.7203 | 209.3406 | 177.4484
332.0667 | 172.3208 | 209.5012 | 178.2106
333.0667 | 171.8245 | 209.921 | 179.6062
334.0667 | 171.8794 | 210.6549 | 180.2517
335.0667 | 172.502 | 210.7157 | 182.7829
336.0667 | 171.9576 | 209.729 | 182.2257
337.0667 | 171.8479 | 210.1033 | 183.0827
338.0667 | 172.7674 | 212.1111 | 184.3756
339.0667 | 173.3821 | 211.4203 | 183.8167
340.0667 | 173.1082 | 211.5542 | 183.6997
341.0667 | 172.5589 | 210.9066 | 182.5398
342.0667 | 171.9894 | 210.2853 | 183.8565
343.0667 | 171.6505 | 210.6294 | 183.114
344.0823 | 171.6916 | 210.947 | 183.8017
345.0667 | 171.3609 | 211.2772 | 182.6249
346.0667 | 171.1111 | 210.9982 | 182.431
347.0667 | 171.1439 | 211.3526 | 181.7729
348.0667 | 171.8493 | 212.5431 | 180.7091
349.0667 | 172.6556 | 213.1857 | 180.2568
350.0667 | 173.3113 | 214.4749 | 180.6045
351.0667 | 173.4646 | 215.2985 | 179.7842
352.0667 | 174.5838 | 215.849 | 180.2067
353.0667 | 175.8746 | 217.6494 | 180.5553
354.0667 | 176.2767 | 218.2461 | 179.8602
355.0667 | 175.7979 | 219.0636 | 179.6634
356.0667 | 175.3948 | 217.8506 | 180.5174
357.0667 | 175.2947 | 217.1502 | 181.2862
358.0667 | 174.8668 | 215.9048 | 181.8447
359.0667 | 174.7855 | 215.1241 | 181.1749
360.0667 | 174.313 | 216.2495 | 180.7014
361.0667 | 174.5914 | 216.1987 | 180.8939
362.0667 | 174.1902 | 215.9227 | 180.605
363.0667 | 174.4756 | 216.6357 | 180.7399
364.0667 | 174.8886 | 217.0426 | 182.5276
365.0667 | 174.4786 | 216.2063 | 181.1176
366.0667 | 174.7178 | 216.4979 | 181.4098
367.0667 | 174.7654 | 216.4142 | 182.416
368.0823 | 174.0531 | 215.6388 | 181.7787
369.0667 | 173.3212 | 215.1395 | 181.2718
370.0667 | 174.0868 | 215.7341 | 181.0421
371.0667 | 174.3513 | 216.8609 | 181.5446
372.0667 | 174.093 | 216.0588 | 181.4235
373.0667 | 174.1353 | 215.4135 | 180.5065
374.0823 | 174.971 | 216.1502 | 180.9582
375.0667 | 175.4114 | 217.9236 | 180.7457
376.0667 | 175.7225 | 217.7545 | 180.9752
377.0667 | 175.198 | 217.7467 | 181.7598
378.0667 | 175.2911 | 218.2053 | 182.0427
379.0667 | 176.0181 | 218.5029 | 183.0685
380.0667 | 176.3941 | 218.2124 | 183.9946
381.0667 | 176.1086 | 217.4297 | 183.469
382.0667 | 176.352 | 217.3337 | 184.4134
383.0667 | 175.8749 | 217.4047 | 184.1611
384.0667 | 176.5123 | 218.3885 | 183.7891
385.0667 | 176.485 | 217.3362 | 184.2894
386.0667 | 176.4995 | 217.2558 | 184.0203
387.0667 | 177.3323 | 217.2933 | 183.8621
388.0667 | 177.3964 | 217.5969 | 184.1369
389.0667 | 179.7561 | 218.4152 | 183.7505
390.0667 | 180.5007 | 219.8605 | 183.8265
391.0667 | 180.7575 | 220.606 | 184.4004
392.0667 | 180.7156 | 220.1875 | 184.0041
393.0823 | 180.6632 | 220.0195 | 183.3942
394.0823 | 180.3174 | 219.31 | 182.5807
395.0667 | 179.8745 | 218.9562 | 183.2011
396.0667 | 179.5963 | 217.3318 | 182.5674
397.0667 | 179.0648 | 218.1146 | 182.6716
398.0667 | 180.1355 | 218.7998 | 182.2876
399.0667 | 180.4163 | 219.1479 | 182.0019
400.0667 | 180.4941 | 220.5366 | 181.3109
401.0667 | 180.1387 | 221.1044 | 181.7257
402.0667 | 180.4516 | 221.169 | 181.0658
403.0667 | 182.1043 | 221.4001 | 180.6806
404.0823 | 182.2605 | 221.1826 | 180.2605
405.0667 | 181.234 | 220.1241 | 180.5176
406.0667 | 180.9958 | 221.025 | 181.5657
407.0667 | 181.2595 | 221.6034 | 182.1278
408.0667 | 181.5464 | 221.4499 | 182.79
409.0667 | 180.9274 | 221.5771 | 182.2562
410.0667 | 180.4523 | 222.4784 | 184.3375
411.0667 | 180.5554 | 222.2923 | 185.6822
412.0667 | 180.7999 | 222.5761 | 185.0934
413.0667 | 181.2276 | 223.3064 | 184.816
414.0667 | 181.1288 | 222.853 | 185.6659
415.0667 | 180.5819 | 221.0055 | 184.0763
416.0667 | 180.1845 | 221.171 | 184.4536
417.0667 | 179.4413 | 221.3671 | 185.1993
418.0667 | 179.1031 | 221.2326 | 185.6996
419.0667 | 178.6418 | 220.7849 | 184.6071
420.0667 | 178.1296 | 219.9435 | 184.2882
421.0667 | 177.8182 | 219.0871 | 183.9294
422.0667 | 177.63 | 219.203 | 184.7679
423.0667 | 177.7272 | 218.6699 | 185.3679
424.0667 | 177.5317 | 217.6822 | 186.0866
425.0667 | 177.2301 | 217.164 | 185.6179
426.0667 | 177.0857 | 215.9124 | 185.2737
427.0667 | 176.7771 | 215.4552 | 184.9754
428.0667 | 176.8939 | 216.0241 | 186.2569
429.0667 | 177.9786 | 216.2398 | 186.9129
430.0667 | 178.9483 | 216.3457 | 185.9481
431.0667 | 179.0268 | 217.7931 | 185.7711
432.0667 | 179.272 | 218.578 | 185.362
433.0667 | 179.7141 | 219.2 | 185.641
434.0667 | 180.3841 | 219.1624 | 185.0383
435.0667 | 181.7506 | 220.3181 | 184.4779
436.0667 | 182.8484 | 220.5381 | 183.8364
437.0667 | 182.7948 | 220.6054 | 183.3623
438.0667 | 182.1295 | 220.4771 | 182.6536
439.0667 | 181.6868 | 219.3567 | 182.0011
440.0667 | 181.6414 | 218.8773 | 181.0527
441.0667 | 181.6898 | 217.3215 | 179.5584
442.0667 | 181.544 | 217.3565 | 178.9629
443.0667 | 181.3051 | 218.0555 | 179.1038
444.0667 | 182.03 | 219.3958 | 178.7185
445.0667 | 182.8373 | 219.8124 | 178.3616
446.0667 | 183.9242 | 220.2233 | 177.2824
447.0667 | 184.9308 | 220.5668 | 176.6402
448.0667 | 185.4393 | 221.4361 | 176.0962
449.0667 | 186.3485 | 222.61 | 176.0791
450.0667 | 187.2774 | 223.7512 | 175.1959
451.0667 | 189.1996 | 224.8158 | 175.0203
452.0667 | 190.0465 | 225.7407 | 174.9825
453.0667 | 190.293 | 226.9544 | 175.0853
454.0667 | 190.1324 | 227.1531 | 175.205
455.0667 | 190.2714 | 227.4286 | 175.5537
456.0667 | 190.6729 | 227.1929 | 175.8864
457.0667 | 190.7356 | 228.2628 | 176.9495
458.0667 | 190.4413 | 227.4637 | 175.9351
459.0667 | 190.7514 | 227.7931 | 176.2595
460.0667 | 191.556 | 228.5577 | 176.5344
461.0667 | 192.331 | 229.6718 | 175.8814
462.0667 | 192.0728 | 231.1384 | 175.7419
463.0667 | 191.8017 | 230.7577 | 175.1915
464.0667 | 191.3962 | 229.2423 | 175.8082
465.0667 | 190.9932 | 229.1923 | 178.2135
466.0667 | 191.1745 | 230.0578 | 178.478
467.0667 | 191.5816 | 232.0182 | 180.4664
468.0667 | 192.3504 | 232.4207 | 181.8692
469.0667 | 192.5615 | 232.8923 | 182.1971
470.0667 | 192.4157 | 233.4101 | 182.1445
471.0667 | 192.0053 | 233.043 | 182.873
472.0667 | 191.5159 | 233.5789 | 183.1742
473.0667 | 191.0119 | 233.9569 | 183.7853
474.0667 | 190.7991 | 233.6392 | 184.9726
475.0667 | 190.3155 | 232.9409 | 186.0116
476.0667 | 189.6456 | 231.5542 | 186.0966
477.0667 | 189.6074 | 231.8366 | 186.1784
478.0667 | 189.7754 | 233.5575 | 185.5568
479.0667 | 190.6873 | 234.8153 | 185.052
480.0667 | 190.894 | 235.3289 | 184.9613
481.0667 | 191.4648 | 235.7513 | 183.9109
482.0667 | 193.0863 | 236.6491 | 182.8319
483.0667 | 194.4247 | 238.4151 | 182.763
484.0667 | 196.0554 | 240.0531 | 182.2859
485.0667 | 197.4365 | 239.5907 | 181.0254
486.0667 | 198.4616 | 239.7337 | 180.886
487.0667 | 200.0852 | 240.9491 | 180.3445
488.0667 | 201.2539 | 241.5495 | 180.2358
489.0667 | 201.2759 | 241.6849 | 179.6784
490.0667 | 201.8415 | 241.8803 | 180.0249
491.0667 | 201.8848 | 242.8153 | 179.9503
492.0667 | 202.3626 | 243.8556 | 179.7072
493.0667 | 202.2886 | 244.1641 | 179.244
494.0823 | 203.027 | 245.1791 | 178.7502
495.0667 | 204.5937 | 246.2465 | 179.1354
496.0667 | 206.4683 | 244.9998 | 178.8115
497.0667 | 206.8004 | 246.2025 | 179.4821
498.0667 | 207.2104 | 246.9838 | 179.835
499.0667 | 207.6336 | 247.958 | 179.4803
500.0667 | 208.4769 | 247.3929 | 180.1173
501.0667 | 208.5883 | 248.0979 | 180.8823
502.0667 | 208.3811 | 247.8732 | 180.7858
503.0667 | 208.2684 | 248.927 | 180.0458
504.0667 | 208.7612 | 250.9396 | 179.7264
505.0667 | 209.7659 | 250.872 | 179.3715
506.0667 | 209.2136 | 252.0769 | 178.4835
507.0667 | 208.7981 | 252.922 | 177.9459
508.0667 | 208.1428 | 251.9537 | 177.3245
509.0667 | 207.5506 | 251.868 | 176.545
510.0667 | 207.3459 | 250.7173 | 176.8423
511.0667 | 207.8828 | 251.5949 | 178.0723
512.0667 | 209.8765 | 252.6647 | 179.209
513.0667 | 211.4185 | 253.5595 | 181.8043
514.0667 | 211.7899 | 253.6278 | 183.2065
515.0667 | 210.9388 | 252.6676 | 184.7618
516.0823 | 210.6431 | 253.3625 | 185.8187
517.0823 | 210.1779 | 252.6896 | 185.8116
518.0667 | 210.871 | 252.5053 | 185.5995
519.0667 | 211.7093 | 252.4559 | 186.1913
520.0667 | 212.2595 | 252.1154 | 188.5165
521.0823 | 212.4579 | 251.5452 | 188.8306
522.0667 | 212.3801 | 253.0656 | 188.9291
523.0823 | 212.2041 | 252.8476 | 187.9786
524.0823 | 212.891 | 253.1298 | 186.9833
525.0667 | 212.5222 | 254.4387 | 187.1064
526.0667 | 212.6027 | 256.2863 | 188.5253
527.0667 | 211.7793 | 256.1471 | 188.2351
528.0667 | 211.8515 | 256.6445 | 188.2359
529.0667 | 211.412 | 256.3589 | 188.5089
530.0667 | 211.968 | 256.0644 | 188.5843
531.0667 | 213.5568 | 255.8072 | 188.6201
532.0667 | 214.7189 | 256.296 | 187.8715
533.0667 | 214.3223 | 256.5867 | 186.6428
534.0667 | 213.8576 | 256.1733 | 185.7902
535.0667 | 215.2464 | 256.9684 | 184.96
536.0667 | 214.5396 | 257.0744 | 183.7299
537.0667 | 214.196 | 257.4185 | 182.7373
538.0667 | 215.2015 | 257.5235 | 183.2777
539.0667 | 215.4686 | 257.5567 | 183.7247
540.0667 | 217.8114 | 258.2844 | 185.5352
541.0667 | 219.4875 | 258.3093 | 186.0962
542.0667 | 219.5051 | 258.4666 | 188.4493
543.0667 | 219.6229 | 259.5542 | 188.5813
544.0667 | 220.8646 | 259.8928 | 188.2458
545.0667 | 221.4959 | 260.7978 | 188.5374
546.0667 | 221.2252 | 261.1171 | 189.98
547.0667 | 220.8218 | 261.57 | 189.6216
548.0667 | 220.328 | 262.4103 | 189.7231
549.0667 | 219.5789 | 261.7058 | 190.813
550.0667 | 219.2877 | 260.5897 | 191.822
551.0667 | 218.2157 | 259.8531 | 192.8661
552.0823 | 217.2541 | 259.6688 | 192.1767
553.0667 | 216.8662 | 258.9725 | 191.6798
554.0823 | 216.219 | 258.7179 | 192.7513
555.0667 | 215.6178 | 259.3603 | 192.2118
556.0667 | 214.9352 | 258.6907 | 192.3155
557.0667 | 214.0776 | 258.9807 | 192.3212
558.0667 | 213.9546 | 258.2308 | 193.3107
559.0823 | 213.4011 | 257.9574 | 193.3077
560.0667 | 213.9952 | 258.3891 | 195.5763
561.0667 | 213.6127 | 258.4851 | 195.9154
562.0823 | 213.3542 | 258.8756 | 195.8317
563.0667 | 213.4823 | 259.8746 | 195.36
564.0667 | 213.3339 | 260.6191 | 195.5948
565.0667 | 213.109 | 260.6633 | 196.2752
566.0667 | 213.029 | 261.0472 | 196.7471
567.0667 | 212.5726 | 261.1031 | 197.7913
568.0667 | 212.1592 | 260.9347 | 199.4442
569.0667 | 211.4228 | 260.9428 | 199.91
570.0667 | 211.4918 | 260.9018 | 200.0276
571.0667 | 211.3222 | 260.9394 | 199.7442
572.0667 | 211.1925 | 261.0841 | 199.6246
573.0667 | 210.357 | 260.7621 | 199.2777
574.0667 | 209.8319 | 260.2836 | 199.2834
575.0667 | 210.2282 | 260.497 | 199.4469
576.0667 | 209.9181 | 260.3565 | 199.4164
577.0667 | 209.2964 | 259.9617 | 199.9515
578.0667 | 209.1222 | 259.6099 | 199.6343
579.0667 | 209.6583 | 260.9258 | 200.02
580.0667 | 210.2694 | 262.2081 | 200.6992
581.0667 | 210.0999 | 262.2708 | 199.9001
582.0667 | 210.4878 | 263.095 | 199.789
583.0667 | 211.3975 | 263.0643 | 199.7328
584.0823 | 211.1791 | 262.5176 | 199.7052
585.0667 | 210.649 | 263.3514 | 199.0933
586.0667 | 210.1376 | 262.6197 | 199.7283
587.0667 | 210.2704 | 263.2784 | 200.1115
588.0667 | 210.0956 | 263.2662 | 199.3856
589.0667 | 210.0127 | 262.4645 | 199.7184
590.0667 | 210.3216 | 262.7487 | 199.6122
591.0667 | 210.5175 | 263.0389 | 199.4066
592.0667 | 210.6712 | 264.3257 | 199.9359
593.0667 | 211.6066 | 262.511 | 199.6083
594.0667 | 212.4468 | 263.059 | 199.0057
595.0667 | 212.735 | 262.4666 | 198.7392
596.0667 | 212.6585 | 263.1658 | 197.8715
597.0667 | 211.9499 | 264.1764 | 197.3533
598.0667 | 211.2476 | 264.9667 | 196.631
599.0667 | 210.8841 | 264.4965 | 195.5988
600.0667 | 210.7481 | 264.9509 | 194.988
601.0667 | 210.9588 | 264.8678 | 194.2476
602.0667 | 211.6628 | 265.9865 | 194.0599
603.0667 | 211.299 | 266.2968 | 194.2276
604.0667 | 211.267 | 265.8134 | 194.1621
605.0667 | 212.421 | 266.2038 | 194.9058
606.0667 | 213.5185 | 266.8378 | 195.3615
607.0667 | 215.2201 | 266.7447 | 196.2041
608.0667 | 215.3585 | 266.4991 | 196.2259
609.0667 | 215.1464 | 266.6672 | 197.1443
610.0667 | 214.8703 | 266.607 | 196.6689
611.0667 | 215.5871 | 267.1148 | 197.0005
612.0667 | 217.8216 | 266.9373 | 196.8414
613.0667 | 220.141 | 267.4175 | 197.5807
614.0667 | 221.0531 | 268.5103 | 197.7757
615.0667 | 221.552 | 268.5916 | 196.9316
616.0667 | 222.0814 | 267.6738 | 196.3359
617.0667 | 221.8026 | 267.2646 | 196.0757
618.0667 | 221.5315 | 267.0679 | 195.7621
619.0667 | 222.0494 | 267.3159 | 195.6213
620.0667 | 222.5088 | 268.4059 | 195.0805
621.0667 | 222.7509 | 269.42 | 194.6558
622.0667 | 221.5994 | 269.4926 | 194.6027
623.0667 | 221.2813 | 269.8611 | 195.3642
624.0667 | 221.335 | 269.7745 | 196.0067
625.0667 | 221.2245 | 271.6475 | 195.524
626.0667 | 221.6099 | 271.8439 | 196.0728
627.0667 | 221.2681 | 272.5057 | 195.3944
628.0667 | 222.4133 | 271.7827 | 194.7792
629.0667 | 223.6343 | 272.1253 | 194.9143
630.0667 | 223.8627 | 272.3894 | 195.129
631.0667 | 224.2048 | 272.6971 | 194.9771
632.0667 | 223.8186 | 272.4553 | 195.3261
633.0667 | 223.008 | 272.2457 | 195.2345
634.0667 | 222.2773 | 272.407 | 195.1246
635.0667 | 221.9876 | 272.2505 | 195.531
636.0667 | 222.7141 | 271.5297 | 197.2643
637.0667 | 222.2115 | 271.0444 | 197.4082
638.0667 | 221.5846 | 270.7023 | 197.1841
639.0667 | 222.0739 | 270.9932 | 198.1403
640.0667 | 221.1908 | 270.896 | 199.2698
641.0667 | 220.7539 | 270.4707 | 200.7179
642.0667 | 220.3676 | 270.2508 | 200.3799
643.0667 | 220.0066 | 270.2508 | 200.0609
644.0667 | 219.3443 | 269.3401 | 199.416
645.0667 | 219.0389 | 269.5729 | 199.3235
646.0667 | 218.6311 | 269.9863 | 199.1908
647.0667 | 219.6447 | 270.1552 | 200.0802
648.0667 | 220.2787 | 270.4858 | 199.5141
649.0667 | 220.166 | 269.9366 | 199.4884
650.0667 | 220.1248 | 269.1368 | 199.3607
651.0667 | 220.1224 | 268.7722 | 199.3947
652.0667 | 219.8854 | 268.4719 | 199.0811
653.0667 | 219.2408 | 268.5759 | 199.3805
654.0667 | 219.6996 | 267.8275 | 199.1911
655.0667 | 219.5436 | 266.9414 | 199.0468
656.0667 | 219.0151 | 266.6387 | 198.7779
657.0667 | 218.1189 | 266.5242 | 197.9581
658.0667 | 218.7077 | 266.3682 | 197.5529
659.0667 | 219.8911 | 265.2195 | 197.3462
660.0667 | 220.4197 | 266.2215 | 197.3519
661.0667 | 221.7415 | 266.5903 | 196.4858
662.0667 | 221.9949 | 266.2517 | 195.6984
663.0667 | 221.3419 | 265.7771 | 195.3775
664.0667 | 221.5867 | 266.508 | 196.5253
665.0667 | 220.5571 | 266.5774 | 197.4214
666.0667 | 220.0513 | 266.9246 | 197.2813
667.0667 | 219.6844 | 267.5375 | 197.1812
668.0667 | 220.6336 | 268.1855 | 197.9609
669.0667 | 219.9841 | 268.2762 | 198.1706
670.0667 | 220.0425 | 268.4958 | 198.6292
671.0667 | 220.6645 | 268.3452 | 198.1727
672.0667 | 220.2939 | 268.4814 | 198.449
673.0667 | 219.8595 | 269.2329 | 197.8874
674.0667 | 219.0209 | 268.6465 | 197.2221
675.0667 | 219.1899 | 268.9988 | 196.1361
676.0667 | 220.5566 | 268.3734 | 196.0074
677.0667 | 220.6137 | 268.182 | 196.7138
678.0667 | 221.0014 | 267.2769 | 195.892
679.0667 | 220.9063 | 266.4639 | 195.0625
680.0667 | 220.2928 | 266.7468 | 194.4846
681.0667 | 221.0663 | 268.7327 | 194.1383
682.0667 | 220.8128 | 267.7607 | 193.6242
683.0667 | 220.8118 | 267.2581 | 192.9807
684.0667 | 221.488 | 267.6794 | 193.5746
685.0667 | 221.3876 | 268.457 | 193.3975
686.0667 | 222.0242 | 268.5234 | 194.846
687.0667 | 221.6477 | 268.4964 | 194.7861
688.0667 | 223.3953 | 269.0108 | 194.7773
689.0667 | 224.2594 | 269.4861 | 195.0238
690.0667 | 225.6049 | 270.871 | 195.2954
691.0667 | 224.8516 | 270.1986 | 194.8404
692.0667 | 225.6581 | 270.3122 | 194.2284
693.0667 | 225.3255 | 271.1053 | 193.9183
694.0667 | 225.0769 | 270.499 | 193.6747
695.0667 | 225.6446 | 270.3181 | 193.9457
696.0667 | 227.2547 | 270.4731 | 193.9313
697.0667 | 229.7042 | 271.4183 | 194.8866
698.0667 | 230.0437 | 270.7446 | 196.3881
699.0667 | 230.253 | 270.9449 | 197.9349
700.0667 | 229.4001 | 270.3947 | 197.6446
701.0667 | 229.0112 | 270.7617 | 197.8074
702.0667 | 228.6916 | 271.0898 | 198.3529
703.0667 | 229.3241 | 270.8585 | 198.856
704.0667 | 228.8651 | 270.4052 | 198.5325
705.0667 | 229.8147 | 270.0083 | 198.9043
706.0667 | 228.7359 | 269.0454 | 198.968
707.0667 | 228.557 | 269.6327 | 198.9107
708.0667 | 228.6292 | 271.1569 | 199.1581
709.0667 | 227.9731 | 271.1513 | 197.9541
710.0667 | 227.0746 | 270.7543 | 197.0726
711.0667 | 225.9191 | 271.7592 | 196.875
712.0667 | 225.0884 | 271.8415 | 197.3654
713.0667 | 225.3873 | 271.0599 | 197.5846
714.0667 | 226.0438 | 270.7372 | 197.7797
715.0667 | 227.5885 | 272.2855 | 198.2415
716.0667 | 228.1319 | 272.5207 | 198.4584
717.0667 | 227.9609 | 271.6044 | 198.2236
718.0667 | 228.1624 | 272.2639 | 197.9034
719.0667 | 227.9497 | 273.023 | 198.6523
720.0667 | 229.3288 | 273.2253 | 197.8292
721.0667 | 228.3164 | 273.9048 | 197.6089
722.0667 | 227.3525 | 273.8594 | 196.9003
723.0667 | 226.9724 | 274.3724 | 197.7794
724.0667 | 227.3512 | 275.0036 | 198.9127
725.0667 | 228.2695 | 275.4815 | 199.4185
726.0667 | 229.9831 | 275.974 | 199.5622
727.0667 | 229.4254 | 275.9085 | 199.0876
728.0667 | 228.3554 | 276.595 | 198.6928
729.0667 | 228.7629 | 276.7107 | 199.3047
730.0667 | 229.8445 | 276.7708 | 199.8279
731.0667 | 229.8941 | 276.3182 | 200.5556
732.0667 | 229.4013 | 275.2609 | 200.3441
733.0667 | 229.1582 | 275.8319 | 200.0212
734.0667 | 231.1006 | 276.9835 | 200.2911
735.0667 | 231.9432 | 277.849 | 201.3375
736.0667 | 232.4778 | 278.4009 | 200.647
737.0667 | 232.9136 | 277.4793 | 199.7792
738.0667 | 233.2363 | 276.9547 | 199.7268
739.0667 | 234.2395 | 278.3807 | 201.1132
740.0667 | 234.1296 | 279.3456 | 200.9695
741.0667 | 234.7686 | 279.6509 | 200.9036
742.0667 | 235.0382 | 279.4602 | 199.9808
743.0667 | 236.2336 | 279.7782 | 199.6672
744.0667 | 236.101 | 279.8769 | 199.6276
745.0667 | 236.645 | 279.5207 | 200.0099
746.0667 | 236.4121 | 279.6182 | 200.438
747.0667 | 236.9975 | 280.1501 | 201.5177
748.0823 | 237.9622 | 281.1357 | 202.5576
749.0667 | 236.938 | 280.7554 | 203.6999
750.0823 | 235.3115 | 280.3017 | 203.9691
751.0667 | 234.237 | 280.7087 | 204.0608
752.0667 | 233.7846 | 280.5997 | 203.2839
753.0667 | 232.3518 | 280.1101 | 203.1853
754.0823 | 232.1199 | 280.5482 | 203.4116
755.0667 | 232.4311 | 281.2634 | 204.7102
756.0667 | 232.0615 | 281.2697 | 204.7662
757.0667 | 231.1915 | 281.0868 | 204.8148
758.0667 | 231.9667 | 280.918 | 205.876
759.0667 | 232.282 | 280.8723 | 205.3169
760.0667 | 233.4265 | 280.7586 | 205.4602
761.0667 | 233.8853 | 280.5944 | 206.0831
762.0667 | 234.3289 | 281.1562 | 206.0264
763.0667 | 235.9649 | 281.8292 | 206.6573
764.0667 | 235.3945 | 281.0333 | 207.3386
765.0667 | 235.5957 | 280.3501 | 207.1467
766.0667 | 235.1153 | 279.9024 | 208.2931
767.0667 | 234.2517 | 279.3122 | 207.8008
768.0667 | 234.0562 | 279.2479 | 207.706
769.0667 | 234.1988 | 279.7345 | 207.548
770.0667 | 235.1133 | 279.7635 | 208.0042
771.0667 | 234.8431 | 280.2621 | 208.9581
772.0667 | 235.1553 | 281.166 | 208.2968
773.0667 | 234.2186 | 279.7436 | 208.2841
774.0667 | 233.2909 | 279.7641 | 209.4809
775.0667 | 232.4184 | 280.0102 | 208.4431
776.0667 | 232.0794 | 279.5065 | 208.6335
777.0667 | 232.8999 | 279.2197 | 209.0202
778.0667 | 232.838 | 278.6809 | 209.5823
779.0667 | 234.62 | 278.8344 | 210.9245
780.0667 | 235.6492 | 278.6897 | 211.652
781.0667 | 235.7516 | 279.5569 | 211.8187
782.0667 | 235.3308 | 279.976 | 211.1292
783.0667 | 235.4883 | 280.0067 | 212.5185
784.0667 | 234.4874 | 280.4482 | 211.662
785.0667 | 233.84 | 279.2703 | 211.2961
786.0667 | 233.4267 | 279.8523 | 212.3056
787.0667 | 233.4888 | 281.9087 | 212.7712
788.0667 | 233.4665 | 282.0743 | 212.7344
789.0667 | 233.8775 | 282.6854 | 212.5081
790.0667 | 232.9766 | 282.2229 | 213.831
791.0667 | 232.1241 | 281.3486 | 214.2543
792.0667 | 232.3362 | 281.1984 | 214.1808
793.0667 | 232.3644 | 281.411 | 215.1636
794.0667 | 233.0163 | 282.0253 | 216.188
795.0667 | 233.417 | 281.735 | 217.6847
796.0667 | 233.5587 | 281.3371 | 216.9386
797.0667 | 234.4884 | 281.2901 | 217.718
798.0667 | 236.2705 | 281.6294 | 218.8311
799.0667 | 235.9702 | 281.1524 | 218.0165
800.0667 | 236.0619 | 280.346 | 217.6384
801.0823 | 235.1338 | 279.2286 | 217.1096
802.0667 | 234.4459 | 277.9584 | 217.074
803.0667 | 234.3858 | 278.4961 | 216.3968
804.0667 | 234.1076 | 278.8569 | 216.1714
805.0823 | 234.9278 | 279.4339 | 215.5756
806.0667 | 235.2174 | 279.6204 | 215.2063
807.0667 | 236.5237 | 280.912 | 214.4485
808.0667 | 237.994 | 282.4939 | 214.342
809.0667 | 238.6129 | 283.3608 | 214.128
810.0667 | 239.9708 | 283.8534 | 213.1792
811.0667 | 240.8008 | 284.396 | 212.1354
812.0667 | 241.0808 | 283.963 | 211.3531
813.0667 | 241.3626 | 284.0102 | 210.574
814.0667 | 242.4853 | 285.2566 | 210.6993
815.0667 | 244.4474 | 286.6935 | 211.6031
816.0667 | 245.7375 | 287.3092 | 211.4853
817.0667 | 245.2005 | 287.2551 | 210.7084
818.0667 | 244.9221 | 287.8043 | 210.5249
819.0667 | 244.9119 | 288.1465 | 210.1737
820.0667 | 245.1527 | 288.7194 | 209.2716
821.0823 | 245.9558 | 289.1001 | 209.9177
822.0667 | 247.2086 | 289.5246 | 209.2987
823.0667 | 248.8358 | 289.2949 | 208.7165
824.0667 | 249.7756 | 289.7704 | 208.1134
825.0667 | 250.7505 | 290.1682 | 207.2005
826.0667 | 251.1423 | 289.94 | 206.5211
827.0667 | 252.0184 | 289.2651 | 206.1242
828.0667 | 252.781 | 289.8119 | 206.1421
829.0667 | 253.799 | 291.1686 | 206.1318
830.0667 | 253.5086 | 291.9937 | 206.4026
831.0667 | 254.1069 | 292.5103 | 205.3335
832.0667 | 253.9868 | 291.6191 | 205.0581
833.0667 | 255.0409 | 292.3273 | 204.8004
834.0667 | 255.1211 | 292.318 | 204.0933
835.0667 | 254.9954 | 291.9987 | 204.1036
836.0667 | 256.1262 | 291.9984 | 204.3151
837.0667 | 258.8102 | 291.4204 | 204.0546
838.0667 | 261.7879 | 290.9758 | 203.5292
839.0667 | 262.0256 | 291.3676 | 203.3491
840.0667 | 261.7705 | 290.7346 | 202.7403
841.0667 | 261.4961 | 291.093 | 202.4697
842.0667 | 262.3332 | 290.9662 | 202.6972
843.0667 | 263.2676 | 292.6163 | 203.0378
844.0667 | 264.0972 | 293.769 | 202.9564
845.0667 | 264.8304 | 294.8901 | 203.1296
846.0667 | 265.4445 | 295.6011 | 204.2898
847.0667 | 264.0443 | 295.3639 | 204.364
848.0667 | 264.6007 | 297.6745 | 204.3123
849.0667 | 264.7179 | 298.0694 | 203.8957
850.0667 | 265.338 | 297.8213 | 203.615
851.0667 | 265.7357 | 297.5671 | 203.58
852.0667 | 266.1606 | 298.2413 | 203.3222
853.0667 | 268.3294 | 298.7783 | 203.6849
854.0667 | 268.2859 | 300.1849 | 203.4536
855.0667 | 267.0193 | 300.4753 | 203.1926
856.0667 | 265.6182 | 300.0989 | 202.7197
857.0667 | 265.2853 | 299.1062 | 202.2373
858.0667 | 264.6249 | 298.3208 | 202.0564
859.0823 | 263.3791 | 298.2492 | 201.649
860.0823 | 262.5311 | 297.9488 | 201.3348
861.0667 | 262.201 | 297.5225 | 201.1237
862.0667 | 261.3715 | 297.3546 | 201.0635
863.0667 | 260.2087 | 296.3618 | 200.973
864.0667 | 259.472 | 294.8428 | 200.8974
865.0667 | 258.9716 | 294.6566 | 201.1657
866.0667 | 258.3788 | 294.3587 | 201.185
867.0667 | 258.3406 | 293.7033 | 200.7022
868.0667 | 258.852 | 293.1601 | 200.5924
869.0667 | 259.0826 | 292.6404 | 200.8262
870.0667 | 258.9121 | 292.8524 | 201.0018
871.0667 | 260.0633 | 291.5241 | 202.4726
872.0667 | 260.8101 | 291.6152 | 202.8341
873.0667 | 261.8687 | 291.2077 | 202.3585
874.0667 | 262.661 | 291.4826 | 201.949
875.0667 | 264.0014 | 292.402 | 201.6138
876.0667 | 263.9316 | 291.8204 | 202.0035
877.0667 | 264.8499 | 291.9929 | 202.2666
878.0667 | 265.7979 | 292.5854 | 202.235
879.0667 | 265.8775 | 292.7776 | 202.0397
880.0667 | 265.1504 | 292.5584 | 202.2144
881.0667 | 264.3198 | 292.5155 | 202.5922
882.0667 | 264.3268 | 292.1936 | 203.004
883.0667 | 263.707 | 292.6251 | 203.1411
884.0667 | 263.434 | 292.36 | 203.0434
885.0667 | 264.5197 | 290.9602 | 203.1104
886.0667 | 265.6478 | 291.7017 | 203.2601
887.0667 | 265.4889 | 291.6116 | 202.9943
888.0667 | 265.3286 | 290.237 | 203.0517
889.0667 | 264.3515 | 290.2802 | 203.2705
890.0667 | 264.832 | 290.3904 | 203.0447
891.0667 | 265.2047 | 290.7332 | 203.0461
892.0667 | 264.6294 | 291.4138 | 203.0428
893.0667 | 263.663 | 290.6551 | 203.1608
894.0667 | 263.539 | 290.8318 | 202.9268
895.0667 | 263.7302 | 289.8045 | 202.8474
896.0667 | 264.1867 | 289.0842 | 202.238
897.0667 | 263.7646 | 289.508 | 202.1405
898.0667 | 263.0117 | 291.2397 | 202.0886
899.0667 | 262.4787 | 289.9101 | 202.4277
900.0667 | 263.5116 | 288.9728 | 202.7992
901.0667 | 262.4336 | 289.7106 | 202.9659
902.0667 | 262.7883 | 288.6017 | 203.3892
903.0667 | 263.2957 | 287.2959 | 202.8594
904.0667 | 264.857 | 286.8167 | 202.3897
905.0667 | 267.1997 | 286.831 | 201.9616
906.0667 | 269.9883 | 287.1178 | 201.3544
907.0667 | 271.9889 | 288.2284 | 201.4851
908.0667 | 272.3898 | 288.4487 | 201.7277
909.0667 | 272.2182 | 288.8455 | 201.4876
910.0667 | 272.3348 | 288.5432 | 201.6782
911.0667 | 272.4441 | 288.6841 | 201.7291
912.0667 | 273.041 | 288.5273 | 202.1199
913.0667 | 273.1156 | 289.2802 | 201.9879
914.0667 | 273.7541 | 289.4375 | 201.9688
915.0667 | 274.0588 | 290.1439 | 201.5695
916.0667 | 274.8892 | 290.2598 | 201.3578
917.0667 | 276.6955 | 291.1114 | 201.0572
918.0667 | 276.8025 | 290.7082 | 200.834
919.0667 | 275.9439 | 290.38 | 201.2105
920.0667 | 275.9125 | 291.39 | 201.2116
921.0667 | 277.4969 | 291.9925 | 201.5418
922.0667 | 279.9486 | 293.7627 | 202.0796
923.0667 | 281.3747 | 294.6858 | 202.7599
924.0667 | 283.0712 | 295.7364 | 203.4577
925.0667 | 284.3661 | 295.3569 | 203.768
926.0667 | 285.0132 | 297.0838 | 204.3411
927.0667 | 285.6387 | 298.1934 | 204.2414
928.0667 | 286.8746 | 300.0453 | 204.6456
929.0667 | 288.0206 | 300.9477 | 205.285
930.0667 | 288.7424 | 302.8568 | 205.7617
931.0667 | 288.9489 | 303.8077 | 205.942
932.0667 | 289.6084 | 305.0704 | 207.6496
933.0667 | 288.9898 | 306.1123 | 209.4266
934.0667 | 290.5697 | 308.1816 | 209.8862
935.0667 | 291.3379 | 308.7626 | 210.2012
936.0667 | 292.1153 | 308.2647 | 209.9738
937.0667 | 293.384 | 307.1796 | 209.7844
938.0667 | 295.0226 | 306.6452 | 209.5851
939.0667 | 296.1126 | 308.224 | 209.2657
940.0667 | 296.4164 | 309.1674 | 209.5884
941.0667 | 297.1996 | 310.1397 | 210.4524
942.0667 | 297.1407 | 311.5447 | 211.357
943.0667 | 297.3645 | 312.6444 | 212.2272
944.0667 | 297.1333 | 313.046 | 212.4966
945.0667 | 297.6128 | 313.7409 | 212.3623
946.0667 | 298.896 | 314.3793 | 212.5701
947.0667 | 298.8573 | 314.8143 | 213.4455
948.0667 | 299.5894 | 314.8109 | 213.1939
949.0667 | 299.9984 | 315.6727 | 213.8984
950.0667 | 300.7523 | 315.1683 | 214.4097
951.0667 | 302.1176 | 316.0669 | 215.0618
952.0667 | 302.5924 | 315.6841 | 214.6382
953.0667 | 301.9981 | 315.7122 | 215.1388
954.0667 | 302.4805 | 317.4046 | 215.1262
955.0667 | 303.1286 | 317.0412 | 214.9991
956.0667 | 303.0588 | 317.262 | 214.9473
957.0667 | 303.9692 | 317.3503 | 215.0216
958.0667 | 304.0654 | 316.8622 | 215.9598
959.0667 | 303.973 | 317.3266 | 215.8384
960.0667 | 303.7222 | 317.7274 | 215.6081
961.0667 | 303.4209 | 317.7628 | 216.714
962.0667 | 303.8724 | 318.1708 | 216.7996
963.0667 | 305.052 | 319.1736 | 219.1173
964.0667 | 306.57 | 320.0175 | 222.479
965.0667 | 306.0313 | 320.9138 | 226.613
966.0667 | 307.2303 | 322.3924 | 228.2051
967.0667 | 307.1805 | 323.3251 | 229.3406
968.0667 | 307.2072 | 324.3309 | 231.086
969.0667 | 307.1421 | 324.7696 | 231.2425
970.0667 | 306.7975 | 325.4074 | 231.2262
971.0667 | 306.2289 | 326.2316 | 230.6575
972.0667 | 305.1082 | 326.2874 | 230.3489
973.0667 | 304.0457 | 326.2738 | 229.9394
974.0667 | 302.8443 | 325.8909 | 229.429
975.0667 | 301.6892 | 326.2237 | 229.3958
976.0667 | 300.2393 | 325.8576 | 229.309
977.0667 | 300.3045 | 326.2349 | 230.1881
978.0667 | 299.1633 | 325.9315 | 229.8147
979.0667 | 298.6739 | 326.7803 | 229.5571
980.0667 | 299.5262 | 327.0039 | 229.7051
981.0667 | 299.3964 | 327.1182 | 229.969
982.0667 | 298.8643 | 328.0707 | 231.5925
983.0667 | 299.0876 | 328.5249 | 233.2582
984.0667 | 298.0359 | 328.9231 | 233.2446
985.0667 | 298.5366 | 328.2175 | 233.5058
986.0667 | 297.396 | 328.1682 | 233.9023
987.0667 | 297.0768 | 328.413 | 233.7025
988.0667 | 296.6057 | 328.6983 | 234.1525
989.0667 | 295.9665 | 329.07 | 233.2376
990.0667 | 296.787 | 328.7195 | 233.5277
991.0667 | 297.1943 | 327.9194 | 233.941
992.0667 | 296.1002 | 327.1602 | 233.9711
993.0667 | 295.0872 | 327.3482 | 234.34
994.0667 | 296.7423 | 327.8987 | 235.1912
995.0667 | 295.4928 | 328.011 | 235.1988
996.0823 | 295.6483 | 328.5117 | 234.7081
997.0823 | 295.1894 | 328.1018 | 234.8983
998.0667 | 294.9149 | 327.8879 | 235.0337
999.0667 | 294.2759 | 327.7069 | 235.3921
1000.0823 | 294.4695 | 327.4313 | 235.0118
1001.0667 | 293.7767 | 327.5245 | 234.8096
1002.0823 | 292.2263 | 327.5597 | 235.2242
1003.0667 | 290.4829 | 327.1485 | 235.5891
1004.0667 | 289.4468 | 328.1563 | 235.1981
1005.0667 | 289.1668 | 328.2871 | 235.362
1006.0667 | 288.0188 | 329.4238 | 235.0858
1007.0667 | 287.7109 | 329.5869 | 236.1228
1008.0667 | 289.5746 | 329.7407 | 237.4701
1009.0667 | 289.786 | 329.5196 | 239.3105
1010.0667 | 289.9492 | 329.3336 | 240.9818
1011.0667 | 289.6721 | 328.8194 | 242.0647
1012.0667 | 289.3597 | 328.5857 | 241.9627
1013.0667 | 288.8493 | 329.9631 | 241.7114
1014.0667 | 289.399 | 329.8776 | 242.1601
1015.0667 | 290.1483 | 330.131 | 242.5642
1016.0667 | 289.7441 | 329.4479 | 242.6767
1017.0667 | 288.6246 | 329.7361 | 242.6407
1018.0667 | 287.8307 | 329.8739 | 242.4069
1019.0667 | 287.1578 | 330.1083 | 242.8262
1020.0667 | 286.4964 | 330.2128 | 243.6641
1021.0667 | 286.1402 | 330.3527 | 243.349
1022.0667 | 286.2657 | 330.3906 | 243.2038
1023.0667 | 286.4171 | 330.2931 | 242.2798
1024.0667 | 286.7403 | 329.0396 | 242.1493
1025.0667 | 286.9592 | 329.2557 | 242.5777
1026.0667 | 286.9497 | 329.0085 | 243.1661
1027.0667 | 287.3844 | 329.3806 | 243.8615
1028.0823 | 287.8354 | 329.1607 | 243.1014
1029.0667 | 288.4055 | 328.6282 | 242.5316
1030.0667 | 290.5984 | 329.2517 | 242.1802
1031.0667 | 291.1697 | 329.7536 | 242.4079
1032.0667 | 290.5116 | 329.7327 | 242.4604
1033.0667 | 291.5279 | 330.3349 | 243.0728
1034.0667 | 292.2904 | 331.7658 | 242.1042
1035.0667 | 292.7066 | 332.7088 | 241.3892
1036.0667 | 293.0212 | 333.3086 | 240.6327
1037.0667 | 292.6775 | 333.3283 | 240.3757
1038.0667 | 292.9999 | 333.4281 | 241.0913
1039.0667 | 292.6274 | 333.8601 | 242.4734
1040.0667 | 292.8403 | 333.2311 | 243.1142
1041.0667 | 294.2848 | 333.5163 | 242.9705
1042.0667 | 295.2239 | 334.3726 | 243.0669
1043.0667 | 295.1323 | 334.7797 | 243.7319
1044.0667 | 294.6415 | 335.4433 | 243.2739
1045.0667 | 295.0514 | 336.2875 | 243.5633
1046.0667 | 295.9495 | 336.394 | 243.3193
1047.0667 | 296.3943 | 336.8498 | 245.0402
1048.0667 | 295.4282 | 337.8926 | 245.8897
1049.0667 | 294.7325 | 338.4935 | 245.7595
1050.0667 | 294.5583 | 337.2208 | 245.0027
1051.0667 | 293.525 | 336.7456 | 244.7932
1052.0667 | 294.5083 | 336.4172 | 245.4743
1053.0667 | 294.0514 | 335.6537 | 244.8774
1054.0667 | 294.9307 | 335.4341 | 245.243
1055.0667 | 294.1313 | 335.0656 | 245.8546
1056.0667 | 295.0338 | 335.1075 | 247.1318
1057.0667 | 294.9392 | 335.4498 | 246.9614
1058.0667 | 295.1085 | 334.7949 | 247.2478
1059.0667 | 295.1961 | 334.4241 | 246.6901
1060.0667 | 295.2401 | 334.7502 | 246.3599
1061.0667 | 295.5141 | 334.0574 | 245.5749
1062.0667 | 296.2442 | 334.9198 | 245.3036
1063.0667 | 296.3884 | 335.2827 | 245.342
1064.0667 | 296.3998 | 335.5318 | 244.7399
1065.0667 | 296.0119 | 335.9924 | 244.7417
1066.0667 | 294.2806 | 336.4506 | 246.1802
1067.0667 | 294.6235 | 337.552 | 247.186
1068.0667 | 294.0579 | 337.932 | 246.5821
1069.0667 | 293.1044 | 337.8156 | 246.822
1070.0667 | 293.7556 | 337.7075 | 247.6159
1071.0667 | 292.5812 | 337.5518 | 247.542
1072.0667 | 293.0108 | 337.6749 | 248.4307
1073.0667 | 294.1996 | 339.0126 | 249.0542
1074.0667 | 294.4956 | 339.0714 | 249.0065
1075.0667 | 294.2163 | 338.9123 | 248.9372
1076.0667 | 294.9668 | 339.8948 | 250.0472
1077.0667 | 294.947 | 340.1661 | 249.8692
1078.0667 | 294.3179 | 340.1915 | 251.0973
1079.0667 | 294.8616 | 339.8663 | 251.203
1080.0667 | 295.4261 | 339.2936 | 251.5444
1081.0667 | 295.977 | 339.121 | 250.7971
1082.0667 | 295.2027 | 338.9544 | 249.855
1083.0667 | 295.6458 | 340.1479 | 248.9795
1084.0667 | 296.4399 | 341.248 | 249.2493
1085.0667 | 296.9345 | 341.6189 | 249.8372
1086.0667 | 297.0767 | 342.3196 | 250.8551
1087.0667 | 296.5191 | 342.856 | 251.7945
1088.0667 | 296.6576 | 343.47 | 252.8198
1089.0667 | 297.2782 | 343.3115 | 254.1075
1090.0667 | 297.6332 | 342.7779 | 254.9004
1091.0667 | 297.8198 | 344.1457 | 254.4675
1092.0667 | 298.6317 | 344.5777 | 254.4887
1093.0667 | 298.7539 | 344.8254 | 254.275
1094.0667 | 298.5258 | 344.8167 | 254.8487
1095.0667 | 298.8277 | 344.7774 | 255.8957
1096.0667 | 299.2059 | 345.6187 | 255.9221
1097.0667 | 298.1095 | 345.9424 | 256.39
1098.0667 | 298.4127 | 346.8367 | 256.4877
1099.0667 | 296.7918 | 347.0148 | 256.5396
1100.0667 | 296.549 | 345.8084 | 257.7877
1101.0667 | 297.7467 | 345.2381 | 258.7919
1102.0667 | 298.1406 | 345.5813 | 258.4806
1103.0667 | 297.0917 | 345.6126 | 259.0917
1104.0667 | 296.9718 | 346.3244 | 259.6514
1105.0823 | 296.2201 | 346.6414 | 261.4549
1106.0667 | 296.0424 | 346.3627 | 261.7546
1107.0667 | 297.916 | 345.6026 | 261.3966
1108.0667 | 298.32 | 346.8154 | 261.5907
1109.0667 | 298.5765 | 346.2955 | 261.7072
1110.0667 | 298.8025 | 345.8497 | 260.969
1111.0667 | 299.3237 | 345.8102 | 260.165
1112.0667 | 299.3108 | 345.774 | 260.3618
1113.0667 | 298.7873 | 345.4912 | 260.1105
1114.0667 | 298.2211 | 344.9708 | 260.3528
1115.0667 | 298.651 | 344.9064 | 260.8244
1116.0667 | 299.645 | 344.8797 | 261.2613
1117.0667 | 299.476 | 345.5434 | 261.1646
1118.0667 | 299.1316 | 346.1376 | 262.2347
1119.0667 | 299.107 | 347.5633 | 263.1633
1120.0667 | 299.2565 | 349.4005 | 262.7897
1121.0667 | 298.7485 | 349.0763 | 262.3344
1122.0667 | 298.0038 | 349.0857 | 261.1079
1123.0667 | 297.1065 | 347.8502 | 260.8686
1124.0667 | 296.7786 | 348.6415 | 261.1518
1125.0667 | 296.1305 | 348.2618 | 260.679
1126.0667 | 296.5202 | 347.7822 | 260.5965
1127.0667 | 296.9504 | 347.8613 | 260.5695
1128.0667 | 297.0539 | 348.3271 | 260.0132
1129.0667 | 297.435 | 348.6399 | 260.2066
1130.0667 | 297.8122 | 348.8687 | 259.6513
1131.0667 | 298.2851 | 347.8107 | 259.5487
1132.0667 | 299.7048 | 347.368 | 259.2801
1133.0667 | 300.6336 | 347.0068 | 258.521
1134.0667 | 300.112 | 346.6093 | 257.7359
1135.0667 | 299.3734 | 346.6237 | 257.3944
1136.0667 | 299.3375 | 347.6389 | 258.2153
1137.0667 | 299.4472 | 346.9022 | 257.76
1138.0667 | 300.6867 | 346.6831 | 256.9319
1139.0667 | 302.0128 | 344.9385 | 256.1701
1140.0667 | 303.6205 | 343.7494 | 255.0046
1141.0667 | 303.7364 | 342.0149 | 254.1649
1142.0667 | 304.0504 | 341.2801 | 253.4433
1143.0667 | 304.6008 | 341.563 | 253.2587
1144.0667 | 303.9086 | 341.3597 | 254.2876
1145.0667 | 303.0225 | 341.2061 | 254.2394
1146.0667 | 302.1113 | 341.5694 | 254.378
1147.0667 | 301.4391 | 341.3399 | 254.7621
1148.0667 | 301.6872 | 340.7223 | 254.4449
1149.0667 | 301.112 | 340.719 | 253.5716
1150.0667 | 300.7369 | 341.0906 | 254.2427
1151.0667 | 300.1725 | 341.6476 | 254.6961
1152.0667 | 299.8359 | 341.7046 | 255.3486
1153.0667 | 299.2556 | 342.2523 | 255.3419
1154.0667 | 299.1374 | 342.9409 | 256.0453
1155.0667 | 298.4926 | 343.0427 | 255.9573
1156.0667 | 299.3432 | 344.264 | 256.8091
1157.0667 | 298.6483 | 344.583 | 257.6225
1158.0667 | 298.4534 | 344.8992 | 258.786
1159.0667 | 297.5665 | 344.4346 | 257.9478
1160.0667 | 297.0939 | 344.2869 | 257.5027
1161.0667 | 296.8298 | 344.479 | 257.4848
1162.0667 | 297.0571 | 344.6699 | 257.2369
1163.0667 | 296.696 | 345.6991 | 257.0969
1164.0667 | 297.3705 | 345.4282 | 257.5499
1165.0667 | 298.164 | 346.7272 | 257.5588
1166.0667 | 298.5114 | 347.8842 | 257.7283
1167.0667 | 298.7222 | 348.5329 | 257.5162
1168.0667 | 299.7245 | 348.6175 | 257.5506
1169.0667 | 299.9994 | 347.6655 | 257.8696
1170.0667 | 299.9249 | 348.2632 | 258.637
1171.0667 | 299.4425 | 348.0589 | 259.8769
1172.0667 | 299.7528 | 348.8121 | 259.3055
1173.0667 | 300.0728 | 348.599 | 258.9179
1174.0667 | 299.9846 | 347.5647 | 258.9909
1175.0667 | 300.2699 | 347.5392 | 259.7577
1176.0667 | 300.3833 | 347.3201 | 260.9122
1177.0667 | 300.7362 | 347.4133 | 260.3677
1178.0667 | 300.9861 | 347.4696 | 260.1585
1179.0667 | 301.3957 | 348.0075 | 259.7238
1180.0667 | 302.2478 | 348.3794 | 259.7117
1181.0667 | 301.3543 | 348.9976 | 259.7204
1182.0667 | 300.5531 | 350.1428 | 259.5975
1183.0667 | 301.497 | 349.5784 | 261.3937
1184.0667 | 300.3249 | 349.9059 | 262.0139
1185.0667 | 299.6692 | 350.6044 | 262.0688
1186.0667 | 299.2155 | 350.642 | 262.5553
1187.0667 | 299.6313 | 350.86 | 262.0292
1188.0667 | 299.7136 | 350.2122 | 261.6782
1189.0667 | 299.3643 | 349.6306 | 262.1472
1190.0667 | 299.3786 | 348.9107 | 262.2183
1191.0667 | 299.392 | 348.4197 | 263.2849
1192.0667 | 299.2448 | 348.0409 | 264.9619
1193.0667 | 298.2753 | 347.5781 | 266.2179
1194.0667 | 298.2805 | 348.9056 | 266.2881
1195.0667 | 299.5581 | 349.6627 | 266.7901
1196.0667 | 299.0509 | 349.6479 | 267.6314
1197.0667 | 299.285 | 349.4073 | 267.6857
1198.0667 | 299.7156 | 349.5476 | 267.4788
1199.0667 | 300.0181 | 350.1493 | 267.1456
1200.0667 | 301.4018 | 349.929 | 268.4278
1201.0667 | 302.2135 | 350.583 | 268.7029
1202.0667 | 302.3252 | 350.8782 | 267.7126
1203.0667 | 302.7316 | 350.8332 | 267.6785
1204.0667 | 302.7711 | 350.5286 | 267.635
1205.0667 | 303.2941 | 350.1156 | 266.9362
1206.0667 | 303.975 | 350.4534 | 266.6508
1207.0667 | 303.3042 | 351.4411 | 268.2859
1208.0667 | 302.7133 | 350.646 | 269.5365
1209.0667 | 301.3332 | 350.3507 | 269.7148
1210.0667 | 301.0389 | 350.6315 | 270.5732
1211.0667 | 300.3042 | 350.6047 | 270.947
1212.0667 | 300.5421 | 350.5781 | 270.198
1213.0667 | 301.4816 | 351.2347 | 269.5939
1214.0667 | 302.5726 | 351.4472 | 269.1041
1215.0667 | 303.3965 | 351.9717 | 269.5984
1216.0667 | 303.8349 | 351.8036 | 269.2581
1217.0667 | 304.8733 | 353.4648 | 268.5539
1218.0667 | 304.9969 | 354.2454 | 268.9331
1219.0667 | 305.422 | 354.856 | 269.4858
1220.0667 | 305.0103 | 354.7703 | 268.634
1221.0667 | 305.1235 | 355.4746 | 268.7395
1222.0667 | 304.4227 | 355.8832 | 269.4195
1223.0667 | 304.0247 | 356.3303 | 270.215
1224.0667 | 303.8536 | 357.2672 | 269.8781
1225.0667 | 303.7423 | 357.4448 | 269.9443
1226.0667 | 303.5657 | 357.3008 | 271.0458
1227.0667 | 303.371 | 357.0724 | 271.2958
1228.0667 | 302.6886 | 357.8257 | 270.8181
1229.0667 | 302.6437 | 357.0589 | 269.5775
1230.0667 | 302.5802 | 357.0146 | 268.3964
1231.0667 | 302.7201 | 356.6475 | 267.7489
1232.0667 | 302.8088 | 357.3654 | 266.972
1233.0667 | 303.0586 | 357.0047 | 266.3178
1234.0667 | 304.2351 | 357.0225 | 267.9225
1235.0667 | 304.3381 | 356.9978 | 268.4234
1236.0667 | 303.6049 | 356.1758 | 268.7969
1237.0667 | 303.4977 | 356.1457 | 268.4625
1238.0667 | 303.2675 | 354.9772 | 268.2169
1239.0667 | 303.1708 | 353.8517 | 267.8428
1240.0667 | 303.065 | 353.8687 | 267.5294
1241.0667 | 302.4928 | 354.3637 | 267.7229
1242.0667 | 301.7873 | 354.7132 | 267.9703
1243.0667 | 301.52 | 355.1375 | 267.4202
1244.0823 | 301.5781 | 354.1315 | 267.3186
1245.0667 | 301.8528 | 353.2198 | 266.7765
1246.0667 | 301.6264 | 352.7162 | 265.9846
1247.0667 | 300.932 | 352.91 | 265.9224
1248.0667 | 300.5295 | 353.3727 | 266.4782
1249.0667 | 300.4147 | 353.4491 | 266.4679
1250.0667 | 300.8811 | 353.5621 | 267.0795
1251.0667 | 300.1774 | 352.6727 | 268.3257
1252.0667 | 300.4764 | 352.2223 | 269.6728
1253.0667 | 300.6327 | 352.0988 | 271.2564
1254.0667 | 300.8529 | 351.9293 | 271.7521
1255.0667 | 300.7665 | 352.8196 | 271.6841
1256.0667 | 301.7939 | 353.4992 | 270.8121
1257.0667 | 302.3797 | 353.8728 | 271.4594
1258.0667 | 302.497 | 353.752 | 270.6192
1259.0667 | 303.7984 | 354.4037 | 270.6477
1260.0667 | 305.3655 | 354.639 | 270.5868
1261.0667 | 305.4531 | 355.9377 | 270.5177
1262.0667 | 306.5685 | 356.4537 | 270.0982
1263.0667 | 307.4156 | 357.4492 | 269.1793
1264.0667 | 308.1767 | 357.0944 | 269.6048
1265.0667 | 308.8187 | 357.378 | 270.502
1266.0667 | 309.744 | 357.869 | 270.0386
1267.0667 | 310.7094 | 357.954 | 269.7723
1268.0667 | 311.0657 | 357.9179 | 269.3726
1269.0667 | 311.0751 | 357.1854 | 270.2627
1270.0667 | 311.7914 | 357.5137 | 269.7463
1271.0667 | 312.2154 | 358.6965 | 270.5837
1272.0667 | 312.0099 | 358.7858 | 270.759
1273.0667 | 311.4986 | 360.1215 | 270.608
1274.0667 | 310.8407 | 360.4543 | 271.0788
1275.0667 | 310.0542 | 360.7609 | 271.7423
1276.0667 | 310.93 | 360.2057 | 271.358
1277.0667 | 311.5226 | 360.3224 | 270.9687
1278.0667 | 311.9945 | 359.8793 | 270.8952
1279.0667 | 313.2106 | 360.6407 | 270.2537
1280.0667 | 313.7666 | 360.9691 | 269.6493
1281.0667 | 313.6381 | 360.4835 | 270.464
1282.0667 | 313.9017 | 360.5319 | 270.4299
1283.0667 | 312.7951 | 359.9716 | 270.7637
1284.0667 | 312.9553 | 360.4243 | 270.2403
1285.0667 | 313.159 | 359.9125 | 269.9074
1286.0667 | 312.8852 | 362.3127 | 269.0847
1287.0667 | 312.994 | 362.896 | 269.0783
1288.0667 | 312.7396 | 362.7293 | 268.8256
1289.0667 | 312.6381 | 363.6769 | 268.7783
1290.0667 | 311.9503 | 364.0743 | 268.4877
1291.0667 | 312.6433 | 366.1632 | 268.4291
1292.0667 | 313.4669 | 366.9518 | 268.392
1293.0667 | 312.9478 | 366.8811 | 267.9099
1294.0667 | 312.7407 | 366.2513 | 267.4207
1295.0667 | 313.0028 | 365.4234 | 267.0281
1296.0667 | 312.4312 | 365.2245 | 266.9127
1297.0667 | 311.9696 | 364.7137 | 266.5791
1298.0667 | 311.8727 | 366.2854 | 266.4774
1299.0667 | 311.352 | 369.3516 | 266.951
1300.0667 | 312.0253 | 369.941 | 267.0683
1301.0667 | 311.9649 | 370.5711 | 267.1981
1302.0667 | 310.8061 | 370.5298 | 267.2568
1303.0667 | 309.4446 | 370.6939 | 266.9369
1304.0667 | 308.1255 | 370.5971 | 267.0644
1305.0667 | 308.6794 | 370.0833 | 267.6411
1306.0667 | 308.9266 | 368.9898 | 268.4195
1307.0667 | 308.7455 | 368.8158 | 269.48
1308.0667 | 308.7771 | 367.5704 | 269.771
1309.0667 | 308.745 | 367.111 | 270.08
1310.0667 | 308.3993 | 366.7349 | 269.7702
1311.0667 | 310.5844 | 367.1128 | 269.4923
1312.0667 | 311.2085 | 367.6781 | 269.6216
1313.0667 | 311.7856 | 367.3754 | 269.2166
1314.0667 | 313.3818 | 367.3723 | 268.9948
1315.0667 | 314.2071 | 367.8524 | 269.1235
1316.0667 | 314.7437 | 367.5446 | 268.4269
1317.0667 | 316.2141 | 369.689 | 267.9457
1318.0667 | 316.6627 | 369.6131 | 267.8144
1319.0667 | 316.6477 | 371.0215 | 267.6412
1320.0667 | 316.9942 | 372.5971 | 267.9437
1321.0667 | 318.3349 | 370.9161 | 267.3986
1322.0667 | 318.9414 | 369.6034 | 267.2516
1323.0667 | 319.7177 | 369.6704 | 267.0135
1324.0667 | 319.8274 | 370.7526 | 267.0456
1325.0667 | 320.2967 | 370.4767 | 266.9309
1326.0667 | 321.6294 | 370.6348 | 266.3842
1327.0667 | 322.5385 | 369.5571 | 266.1376
1328.0667 | 322.0128 | 369.2772 | 265.6022
1329.0667 | 322.0272 | 368.5567 | 264.9454
1330.0667 | 325.2092 | 367.8323 | 264.5834
1331.0667 | 326.6726 | 367.3759 | 263.989
1332.0667 | 327.497 | 367.367 | 263.8936
1333.0667 | 328.324 | 367.8176 | 263.2817
1334.0667 | 327.9212 | 367.9985 | 262.9045
1335.0667 | 328.1008 | 366.9705 | 262.7703
1336.0667 | 328.4456 | 367.5677 | 263.0087
1337.0667 | 328.4642 | 367.9538 | 263.0454
1338.0667 | 330.5094 | 366.8159 | 263.1247
1339.0667 | 332.0587 | 364.7405 | 262.5231
1340.0667 | 332.8081 | 363.3206 | 262.0522
1341.0667 | 332.9323 | 364.2017 | 261.6551
1342.0667 | 332.5143 | 365.6221 | 261.8958
1343.0667 | 333.0267 | 368.6855 | 261.8778
1344.0667 | 334.1279 | 367.9543 | 262.1675
1345.0667 | 335.0394 | 367.2481 | 262.3606
1346.0667 | 336.1317 | 367.9922 | 262.1023
1347.0667 | 335.7522 | 369.2107 | 262.15
1348.0667 | 334.8217 | 368.5487 | 262.2216
1349.0667 | 336.0564 | 366.9152 | 261.8373
1350.0667 | 336.9252 | 366.3646 | 261.612
1351.0667 | 336.4083 | 368.1141 | 261.7486
1352.0667 | 335.193 | 368.6824 | 261.7584
1353.0667 | 335.9907 | 368.3683 | 261.8717
1354.0667 | 337.5713 | 368.4921 | 261.6601
1355.0667 | 338.9229 | 368.1696 | 261.9371
1356.0667 | 338.3017 | 368.1902 | 261.7611
1357.0667 | 337.3005 | 367.6767 | 262.0003
1358.0667 | 336.0016 | 367.7494 | 261.9712
1359.0667 | 334.8693 | 367.2328 | 261.9061
1360.0667 | 335.2726 | 366.606 | 262.1515
1361.0667 | 335.133 | 366.5534 | 261.96
1362.0667 | 334.5168 | 366.0894 | 261.9488
1363.0667 | 333.914 | 367.2019 | 262.1018
1364.0667 | 333.113 | 368.0953 | 262.5178
1365.0667 | 332.2086 | 368.8629 | 262.3679
1366.0667 | 331.432 | 367.4296 | 261.9759
1367.0667 | 330.1859 | 367.3016 | 261.5726
1368.0667 | 329.6326 | 366.9832 | 261.7959
1369.0667 | 330.2092 | 367.444 | 262.2365
1370.0667 | 331.9612 | 367.9371 | 262.1468
1371.0667 | 332.394 | 368.0655 | 262.2019
1372.0667 | 331.535 | 368.3138 | 262.2548
1373.0667 | 332.0366 | 369.4824 | 262.4639
1374.0667 | 331.1475 | 371.8554 | 262.4396
1375.0667 | 331.0847 | 370.5569 | 262.7843
1376.0667 | 332.0703 | 371.0245 | 263.0367
1377.0667 | 331.999 | 369.9334 | 263.2803
1378.0667 | 331.5154 | 369.1992 | 263.9975
1379.0667 | 333.8404 | 368.6064 | 263.9709
1380.0667 | 334.7831 | 367.3866 | 263.9672
1381.0667 | 334.4413 | 367.8277 | 263.9258
1382.0667 | 334.8118 | 366.6217 | 264.1345
1383.0667 | 335.0041 | 365.2386 | 263.7422
1384.0667 | 334.9741 | 362.8781 | 263.4987
1385.0667 | 334.722 | 361.4043 | 263.8588
1386.0667 | 336.419 | 361.352 | 263.6331
1387.0667 | 337.0899 | 361.0836 | 263.8332
1388.0667 | 337.7114 | 361.056 | 263.9929
1389.0667 | 338.2401 | 359.6043 | 263.9196
1390.0667 | 337.938 | 359.6259 | 263.436
1391.0667 | 337.7312 | 358.5898 | 263.1655
1392.0667 | 338.0217 | 358.2676 | 262.9448
1393.0667 | 337.2244 | 358.6328 | 263.0778
1394.0667 | 336.2788 | 358.9729 | 263.6934
1395.0667 | 333.9224 | 357.9035 | 264.0164
1396.2542 | 331.6638 | 357.5718 | 263.9691
1397.1292 | 330.1743 | 357.1767 | 263.911
1398.2385 | 328.6738 | 356.7292 | 263.9418
1399.1135 | 327.0999 | 356.8325 | 264.3838
1400.5823 | 326.8723 | 357.3999 | 264.4278
1401.3479 | 327.1973 | 356.6338 | 264.8884
1402.0667 | 327.3804 | 356.2508 | 264.7229
1403.0667 | 326.5499 | 355.7133 | 264.4681
1404.0667 | 325.7856 | 356.0385 | 265.0826
1405.0667 | 325.5909 | 356.7713 | 265.7737
1406.0667 | 325.8036 | 357.4732 | 266.3067
1407.0667 | 325.6075 | 357.1131 | 266.0266
1408.0667 | 326.0029 | 357.5343 | 265.9718
1409.0667 | 325.7534 | 356.9152 | 265.8389
1410.0667 | 325.9861 | 356.801 | 265.7103
1411.0667 | 326.6551 | 356.4614 | 266.5261
1412.0667 | 327.6308 | 355.8229 | 266.8468
1413.0667 | 327.3529 | 356.8577 | 266.8206
1414.0667 | 328.3723 | 356.6909 | 266.4525
1415.0667 | 328.9018 | 355.906 | 265.9037
1416.0667 | 328.4158 | 355.9043 | 265.3415
1417.0667 | 327.7219 | 355.2815 | 264.9178
1418.0667 | 327.8313 | 354.3806 | 264.6441
1419.0667 | 328.315 | 355.4762 | 264.4497
1420.0667 | 328.0178 | 355.9131 | 264.6624
1421.0667 | 329.4447 | 355.7054 | 264.6248
1422.0667 | 329.2055 | 354.5482 | 264.3668
1423.0667 | 328.7211 | 353.7309 | 263.9626
1424.0667 | 329.2104 | 353.3774 | 263.7074
1425.0667 | 331.43 | 352.4756 | 263.4933
1426.0667 | 333.1273 | 352.3161 | 263.7253
1427.0667 | 336.3481 | 353.2087 | 264.0256
1428.0667 | 338.5328 | 353.7221 | 264.2699
1429.0667 | 339.0481 | 354.3832 | 264.7798
1430.0667 | 339.3901 | 354.1294 | 264.5136
1431.0667 | 340.6382 | 353.7157 | 264.5604
1432.0667 | 341.6035 | 353.1371 | 264.634
1433.0667 | 341.5835 | 354.6042 | 264.704
1434.0823 | 340.6694 | 354.4954 | 264.7277
1435.0667 | 339.7936 | 354.4844 | 265.0807
1436.0823 | 338.563 | 353.6788 | 265.0322
1437.0667 | 337.43 | 354.3736 | 265.0907
1438.0979 | 336.6908 | 354.8856 | 265.6568
1439.0667 | 335.9198 | 354.8972 | 265.2713
1440.0667 | 335.2707 | 354.7833 | 265.8464
1441.0667 | 334.5108 | 354.2891 | 265.7089
1442.0667 | 332.9511 | 354.6046 | 265.6907
1443.0667 | 332.7576 | 354.5804 | 265.4134
1444.0667 | 332.1014 | 353.7978 | 265.1636
1445.0667 | 332.2984 | 353.9808 | 264.9482
1446.0667 | 331.1438 | 355.0374 | 265.0672
1447.0667 | 329.9513 | 355.0588 | 265.3011
1448.0667 | 328.6222 | 354.5815 | 265.1114
1449.0667 | 326.861 | 353.6477 | 265.1404
1450.0667 | 326.4667 | 353.3718 | 265.3481
1451.0667 | 326.5943 | 353.0287 | 265.9184
1452.0667 | 326.0286 | 353.3926 | 267.119
1453.0667 | 325.5717 | 353.8919 | 268.6238
1454.0667 | 325.2013 | 354.493 | 268.7643
1455.0823 | 324.342 | 353.661 | 268.8206
1456.0667 | 324.6923 | 353.6464 | 268.3517
1457.0667 | 324.298 | 353.2264 | 268.0641
1458.0667 | 323.3927 | 353.4753 | 267.7392
1459.0667 | 322.5099 | 353.4 | 268.1262
1460.0667 | 321.1307 | 354.6401 | 268.7919
1461.0667 | 320.004 | 354.8547 | 270.2535
1462.0667 | 320.0122 | 355.5198 | 271.6007
1463.0667 | 319.9546 | 355.5244 | 271.572
1464.0667 | 320.3006 | 355.8737 | 271.1538
1465.0667 | 319.751 | 356.4117 | 270.933
1466.0667 | 319.2376 | 357.3124 | 271.8357
1467.0667 | 318.207 | 357.112 | 272.836
1468.0823 | 317.109 | 356.1239 | 273.3713
1469.0979 | 317.0331 | 356.1809 | 273.5484
1470.0823 | 315.8347 | 355.4552 | 274.4298
1471.0823 | 314.7559 | 355.4683 | 275.128
1472.0667 | 313.4286 | 354.5025 | 276.3423
1473.0823 | 311.9417 | 353.3407 | 277.3847
1474.0667 | 311.2419 | 353.4561 | 278.2301
1475.0667 | 311.1435 | 353.6021 | 278.1267
1476.0667 | 310.7392 | 353.9862 | 278.1938
1477.0667 | 311.1888 | 353.2221 | 277.6313
1478.0667 | 312.3087 | 353.6252 | 277.52
1479.0667 | 312.2829 | 353.103 | 277.2243
1480.0667 | 313.2113 | 352.3181 | 277.1823
1481.0667 | 312.5547 | 352.0342 | 276.7267
1482.0667 | 312.4708 | 352.2934 | 276.4357
1483.0667 | 311.385 | 351.7522 | 276.0946
1484.0667 | 309.9881 | 350.3619 | 276.1864
1485.0823 | 308.6187 | 349.573 | 277.1403
1486.0667 | 307.9484 | 349.8225 | 278.0675
1487.0667 | 308.8679 | 350.8631 | 278.3795
1488.0667 | 309.066 | 351.0402 | 278.0587
1489.0667 | 309.7199 | 351.252 | 277.9976
1490.0667 | 309.1731 | 351.2734 | 277.5125
1491.0667 | 308.7257 | 351.0689 | 276.9924
1492.0667 | 309.0591 | 351.595 | 276.8582
1493.0667 | 309.9366 | 352.0087 | 276.5713
1494.0667 | 310.78 | 351.9252 | 275.8022
1495.0667 | 312.2043 | 351.9386 | 275.0948
1496.0667 | 312.5361 | 351.3175 | 274.4551
1497.0667 | 313.0361 | 351.6185 | 273.8895
1498.0667 | 313.1176 | 351.565 | 273.3642
1499.0667 | 313.0066 | 352.0995 | 273.0707
1500.0667 | 312.391 | 353.3959 | 273.0282
1501.0667 | 311.7053 | 352.394 | 272.5265
1502.0667 | 311.389 | 352.1855 | 272.1627
1503.0667 | 311.4171 | 352.5402 | 272.1085
1504.0667 | 311.0624 | 352.6296 | 272.9154
1505.0667 | 311.2601 | 353.2334 | 272.9035
1506.0667 | 311.1624 | 354.1314 | 273.4186
1507.0667 | 310.8847 | 354.3948 | 273.6224
1508.0667 | 311.0706 | 354.7802 | 274.3198
1509.0667 | 311.1664 | 354.4671 | 274.3156
1510.0667 | 310.7546 | 355.5735 | 274.6484
1511.0667 | 311.6239 | 357.5992 | 274.7971
1512.0667 | 312.8707 | 357.9116 | 275.004
1513.0667 | 314.2085 | 357.9461 | 274.4577
1514.0667 | 315.8377 | 357.9369 | 274.1404
1515.0667 | 316.2489 | 357.2715 | 273.6933
1516.0667 | 316.6256 | 356.497 | 273.3387
1517.0667 | 317.5341 | 354.8683 | 272.791
1518.0667 | 318.1036 | 354.0832 | 272.2043
1519.0667 | 318.904 | 354.4551 | 271.7793
1520.0667 | 320.762 | 353.9351 | 271.3504
1521.0667 | 322.6337 | 353.5252 | 271.1943
1522.0667 | 322.6917 | 351.9265 | 271.4137
1523.0667 | 321.6393 | 350.5708 | 271.6673
1524.0667 | 320.209 | 350.0219 | 271.4339
1525.0667 | 318.9103 | 349.9101 | 272.2011
1526.0667 | 318.7269 | 350.1081 | 272.8037
1527.0667 | 318.907 | 349.7309 | 272.4401
1528.0667 | 319.6872 | 349.2264 | 271.8723
1529.0667 | 319.5801 | 349.7586 | 272.201
1530.0667 | 318.8328 | 348.6694 | 272.1663
1531.0667 | 317.7911 | 348.9263 | 272.3634
1532.0667 | 316.6709 | 349.5588 | 273.3333
1533.0667 | 316.2638 | 349.9241 | 273.8585
1534.0667 | 315.9955 | 349.5104 | 273.7521
1535.0667 | 315.4912 | 350.0108 | 273.3737
1536.0667 | 314.9259 | 350.2013 | 273.1494
1537.0667 | 314.2805 | 350.9309 | 273.1933
1538.0667 | 313.5401 | 351.5627 | 273.2867
1539.0667 | 312.6613 | 351.9327 | 273.8317
1540.0667 | 314.157 | 353.0575 | 273.8943
1541.0667 | 315.3613 | 351.9579 | 273.6839
1542.0667 | 315.2731 | 350.4013 | 273.0807
1543.0667 | 314.3635 | 349.5972 | 272.8888
1544.0667 | 314.9344 | 348.7005 | 272.7952
1545.0667 | 314.9715 | 348.2301 | 273.0208
1546.0667 | 315.8081 | 348.7599 | 272.6712
1547.0667 | 315.6637 | 349.1494 | 272.8133
1548.0667 | 316.1064 | 349.4866 | 272.7615
1549.0667 | 316.657 | 350.0642 | 272.5061
1550.0667 | 316.7528 | 348.9235 | 272.2553
1551.0667 | 316.8016 | 348.6786 | 271.862
1552.0667 | 317.2851 | 348.9089 | 271.5616
1553.0667 | 317.8069 | 348.7664 | 271.2468
1554.0667 | 317.6927 | 348.7986 | 270.9243
1555.0667 | 318.7449 | 348.1741 | 270.4747
1556.0667 | 319.5688 | 348.4484 | 270.2947
1557.0667 | 319.5138 | 348.4133 | 270.0468
1558.0667 | 318.8118 | 348.4029 | 269.9097
1559.0667 | 319.0007 | 348.8774 | 269.6716
1560.0667 | 319.1951 | 348.0485 | 269.6931
1561.0667 | 319.1583 | 346.2807 | 269.494
1562.0667 | 318.9533 | 345.931 | 269.2074
1563.0667 | 319.5445 | 346.6885 | 269.0481
1564.0667 | 319.1894 | 346.9819 | 269.0439
1565.0667 | 317.9754 | 346.608 | 269.5443
1566.0667 | 316.2417 | 345.9181 | 269.9089
1567.0667 | 314.5409 | 344.905 | 270.5508
1568.0667 | 313.0924 | 344.9107 | 272.557
1569.0667 | 312.6641 | 347.1717 | 273.8714
1570.0667 | 312.4219 | 348.4343 | 274.9954
1571.0667 | 313.539 | 347.9327 | 274.5979
1572.0667 | 314.4182 | 346.5319 | 273.9334
1573.0667 | 314.6423 | 345.0755 | 273.3732
1574.0667 | 314.5728 | 345.3779 | 273.4456
1575.0823 | 313.787 | 345.0763 | 273.8588
1576.0667 | 312.4644 | 345.5813 | 274.7864
1577.0667 | 311.091 | 345.3503 | 275.673
1578.0667 | 310.5451 | 346.1888 | 276.0273
1579.0667 | 310.1646 | 346.3309 | 275.6249
1580.0667 | 309.9336 | 345.9961 | 275.159
1581.0667 | 309.1895 | 346.5772 | 275.6035
1582.0667 | 309.8019 | 347.7864 | 275.6835
1583.0667 | 309.61 | 347.5572 | 275.153
1584.0667 | 309.1887 | 347.0002 | 275.3039
1585.0667 | 308.5543 | 346.8673 | 275.9716
1586.0667 | 307.6484 | 346.2377 | 276.1689
1587.0667 | 307.4472 | 346.4795 | 276.6137
1588.0667 | 307.2107 | 347.0851 | 276.6527
1589.0667 | 306.9929 | 346.5352 | 276.2362
1590.0667 | 307.2662 | 346.1 | 275.6317
1591.0667 | 307.2152 | 345.2914 | 275.2858
1592.0667 | 306.6616 | 345.9013 | 275.92
1593.0667 | 307.3945 | 347.4459 | 276.2745
1594.0667 | 308.181 | 347.8701 | 276.0738
1595.0667 | 308.2383 | 347.4011 | 275.5872
1596.0667 | 308.7738 | 346.6133 | 274.9277
1597.0667 | 310.2472 | 346.7993 | 274.3165
1598.0667 | 312.879 | 346.715 | 273.969
1599.0667 | 314.89 | 346.5346 | 273.5415
1600.0667 | 316.3332 | 347.5943 | 273.4856
1601.0667 | 316.9904 | 347.2951 | 273.0516
1602.0667 | 316.8589 | 346.293 | 272.4521
1603.0667 | 316.7197 | 345.4572 | 272.1239
1604.0667 | 316.5135 | 344.8991 | 271.9645
1605.0667 | 316.3176 | 344.1655 | 271.876
1606.0667 | 316.2745 | 343.8895 | 271.9684
1607.0667 | 316.2625 | 344.0097 | 271.6527
1608.0667 | 318.978 | 344.338 | 271.5756
1609.0667 | 320.8871 | 344.8287 | 271.2221
1610.0667 | 322.4381 | 343.9776 | 270.7996
1611.0667 | 323.0525 | 342.7485 | 270.4524
1612.0667 | 324.4883 | 342.8917 | 270.1452
1613.0667 | 325.7681 | 343.3424 | 270.2254
1614.0667 | 326.8388 | 343.735 | 269.9426
1615.0667 | 326.3412 | 344.4304 | 269.8273
1616.0667 | 325.0091 | 344.6289 | 269.8532
1617.0667 | 323.3463 | 343.9398 | 269.8394
1618.0667 | 321.6075 | 343.394 | 269.8495
1619.0667 | 320.46 | 343.4918 | 270.1934
1620.0667 | 319.8775 | 343.3628 | 270.5517
1621.0667 | 319.4539 | 344.6054 | 270.964
1622.0667 | 318.6311 | 345.9731 | 271.3701
1623.0667 | 317.9279 | 346.2125 | 271.3035
1624.0667 | 317.7401 | 347.6069 | 271.4003
1625.0667 | 318.4768 | 349.0126 | 271.4961
1626.0667 | 317.9573 | 348.8194 | 271.3948
1627.0667 | 317.1493 | 348.5684 | 271.5436
1628.0667 | 316.1641 | 348.9827 | 271.8085
1629.0667 | 316.348 | 348.5906 | 272.0812
1630.0667 | 316.4255 | 348.868 | 272.2012
1631.0667 | 316.3551 | 349.6088 | 272.3113
1632.0667 | 315.7744 | 349.9316 | 272.6412
1633.0667 | 316.4375 | 351.6347 | 273.1913
1634.0667 | 317.3488 | 352.4945 | 273.307
1635.0667 | 317.6534 | 353.053 | 273.5963
1636.0667 | 319.5116 | 353.6361 | 273.8901
1637.0667 | 320.2467 | 355.1271 | 274.0678
1638.0667 | 320.5411 | 355.0773 | 274.5241
1639.0667 | 320.9883 | 354.2698 | 274.4806
1640.0667 | 319.908 | 353.37 | 275.0341
1641.0667 | 319.9808 | 352.9598 | 275.7251
1642.0667 | 319.7904 | 352.2754 | 275.9805
1643.0667 | 319.3728 | 351.6577 | 275.9406
1644.0667 | 318.8262 | 350.9092 | 275.7233
1645.0667 | 318.0086 | 351.5344 | 275.5281
1646.0667 | 317.8203 | 352.191 | 275.363
1647.0667 | 317.872 | 350.9584 | 275.1502
1648.0667 | 317.3637 | 350.7676 | 275.1655
1649.0667 | 317.0367 | 350.9949 | 275.5944
1650.0667 | 317.1796 | 352.5651 | 275.5723
1651.0667 | 317.4711 | 352.022 | 275.4102
1652.0667 | 316.7581 | 351.9363 | 274.9455
1653.0667 | 318.1755 | 351.1242 | 274.582
1654.0667 | 318.2045 | 351.6182 | 274.3126
1655.0667 | 318.4195 | 351.5438 | 273.9744
1656.0667 | 320.315 | 351.1185 | 273.6982
1657.0667 | 321.7742 | 349.7955 | 273.3029
1658.0667 | 322.832 | 349.1167 | 272.9697
1659.0667 | 323.0994 | 348.5082 | 272.7437
1660.0667 | 322.4169 | 347.9113 | 272.5755
1661.0667 | 322.4705 | 347.5434 | 273.0259
1662.0667 | 322.5612 | 347.6181 | 273.0747
1663.0667 | 321.3872 | 349.3988 | 273.218
1664.0667 | 320.8373 | 350.878 | 273.4438
1665.0667 | 320.2664 | 351.2575 | 273.5874
1666.0667 | 320.4468 | 351.7936 | 273.5801
1667.0667 | 319.7379 | 353.0221 | 273.6583
1668.0667 | 318.7659 | 354.0453 | 273.9673
1669.0667 | 317.8927 | 353.7458 | 274.7588
1670.0667 | 317.2235 | 353.462 | 275.2281
1671.0667 | 317.2176 | 353.7821 | 275.832
1672.0667 | 318.0568 | 353.595 | 276.1337
1673.0667 | 318.5134 | 354.0106 | 276.3269
1674.0667 | 318.694 | 354.8713 | 276.8301
1675.0667 | 319.0234 | 355.0946 | 277.2346
1676.0667 | 318.9686 | 355.1314 | 277.2622
1677.0667 | 319.0554 | 354.8454 | 277.21
1678.0667 | 319.5045 | 354.6428 | 276.9864
1679.0667 | 320.6853 | 355.5029 | 276.8963
1680.0667 | 322.2745 | 354.5555 | 276.7284
1681.0667 | 322.0411 | 354.1019 | 276.4109
1682.0667 | 322.9108 | 353.1644 | 276.1967
1683.0667 | 322.4779 | 352.1933 | 275.7668
1684.0667 | 323.4129 | 351.8706 | 275.502
1685.0667 | 323.4324 | 351.1787 | 275.1191
1686.0667 | 324.9372 | 351.5219 | 275.0123
1687.0667 | 325.2034 | 351.1808 | 274.7768
1688.0667 | 324.7206 | 350.7935 | 274.6368
1689.0667 | 323.8485 | 350.7964 | 274.9463
1690.0667 | 322.463 | 351.3516 | 275.3385
1691.0667 | 322.4328 | 352.79 | 275.4
1692.0667 | 322.3278 | 355.5534 | 275.457
1693.0667 | 321.797 | 356.6788 | 275.4362
1694.0667 | 322.0185 | 358.1072 | 275.52
1695.0667 | 321.5481 | 359.4482 | 275.5026
1696.0667 | 321.6805 | 359.7886 | 276.034
1697.0667 | 321.798 | 360.1345 | 276.3155
1698.0667 | 321.8603 | 360.1583 | 276.9151
1699.0667 | 321.7089 | 360.2501 | 277.4196
1700.0667 | 321.6449 | 359.4812 | 277.8416
1701.0667 | 321.698 | 358.6134 | 277.8043
1702.0667 | 321.5214 | 358.2638 | 277.4977
1703.0667 | 321.7908 | 358.0585 | 277.1959
1704.0667 | 322.225 | 357.3936 | 277.2591
1705.0667 | 322.1868 | 357.5813 | 277.7235
1706.0667 | 322.3696 | 358.232 | 278.5539
1707.0667 | 322.5338 | 359.6135 | 279.4616
1708.0667 | 321.9782 | 360.1324 | 280.5663
1709.0667 | 321.5263 | 360.6102 | 281.2511
1710.0667 | 322.9882 | 361.5701 | 281.9154
1711.0667 | 324.2735 | 362.8932 | 282.6221
1712.0667 | 325.1614 | 364.095 | 283.2791
1713.0667 | 326.373 | 365.6057 | 284.639
1714.0667 | 327.9788 | 368.457 | 285.0939
1715.0667 | 329.7979 | 370.6096 | 285.9646
1716.0667 | 331.4507 | 371.8099 | 287.1007
1717.0667 | 331.9962 | 372.9089 | 287.7328
1718.0667 | 332.2931 | 373.2046 | 288.1457
1719.0667 | 331.583 | 373.0887 | 288.8564
1720.0667 | 330.9259 | 373.6459 | 289.9144
1721.0667 | 330.1866 | 373.6147 | 291.2384
1722.0667 | 329.8709 | 373.8243 | 292.8221
1723.0667 | 329.1719 | 373.9403 | 293.3756
1724.0667 | 328.5574 | 373.7851 | 293.7388
1725.0667 | 328.1345 | 373.3711 | 294.0039
1726.0667 | 328.1839 | 374.5057 | 294.7604
1727.0667 | 328.7019 | 374.2291 | 294.4364
1728.0667 | 330.0623 | 373.9659 | 293.8079
1729.0667 | 330.6821 | 372.9675 | 293.0986
1730.0667 | 330.3848 | 372.594 | 292.6569
1731.0667 | 331.4907 | 374.2127 | 292.4566
1732.0667 | 332.462 | 375.4279 | 292.2556
1733.0667 | 334.3879 | 378.7869 | 292.1667
1734.0667 | 334.9496 | 378.2783 | 291.8552
1735.0667 | 336.5389 | 377.1224 | 291.3889
1736.0667 | 339.9283 | 376.9196 | 290.7678
1737.0667 | 344.2605 | 375.8719 | 290.2511
1738.0667 | 348.154 | 375.2274 | 289.9014
1739.0667 | 348.7375 | 373.8991 | 289.5565
1740.0667 | 350.0876 | 373.4537 | 289.1336
1741.0667 | 350.1262 | 373.1382 | 288.7526
1742.0667 | 352.0275 | 371.8356 | 288.7315
1743.0667 | 353.5227 | 372.239 | 289.2937
1744.0667 | 354.4982 | 374.5141 | 289.5634
1745.0667 | 355.9168 | 375.8766 | 290.3355
1746.0667 | 356.7119 | 376.007 | 289.8927
1747.0667 | 357.9874 | 374.447 | 289.5529
1748.0667 | 359.0374 | 373.4698 | 289.3566
1749.0667 | 361.3885 | 373.0889 | 289.3349
1750.0667 | 363.2442 | 372.2266 | 289.0904
1751.0667 | 364.9664 | 372.786 | 288.6879
1752.0667 | 364.6172 | 373.7978 | 288.5825
1753.0667 | 363.4613 | 373.8663 | 288.3389
1754.0667 | 361.5022 | 373.8032 | 288.2636
1755.0667 | 359.2341 | 374.2807 | 288.7165
1756.0667 | 356.9096 | 375.802 | 289.2887
1757.0667 | 355.5494 | 378.1827 | 289.7139
1758.0667 | 357.8268 | 378.8053 | 289.7471
1759.0667 | 358.9036 | 380.8196 | 289.6517
1760.0667 | 360.5676 | 381.8403 | 289.7027
1761.0667 | 361.3246 | 381.326 | 289.821
1762.0667 | 360.9019 | 381.621 | 290.1281
1763.0667 | 359.0214 | 381.6955 | 290.5678
1764.0667 | 357.1655 | 380.9325 | 291.1759
1765.0667 | 355.6254 | 381.3367 | 292.0692
1766.0667 | 355.7762 | 382.1388 | 292.5434
1767.0667 | 355.8305 | 381.8595 | 292.7868
1768.0667 | 357.3294 | 382.5785 | 292.9316
1769.0667 | 356.8723 | 382.0191 | 292.8023
1770.0667 | 355.5133 | 381.8597 | 292.8165
1771.0667 | 353.7821 | 380.9974 | 292.8564
1772.0667 | 352.8277 | 381.3797 | 294.5111
1773.0667 | 351.6547 | 381.4828 | 295.5915
1774.0667 | 352.6008 | 381.1461 | 295.8891
1775.0667 | 353.5401 | 380.8179 | 295.5584
1776.0667 | 353.2434 | 380.5884 | 295.6796
1777.0667 | 352.5822 | 381.5466 | 297.1147
1778.0667 | 353.4435 | 382.6814 | 297.5168
1779.0667 | 353.9924 | 382.9146 | 297.75
1780.0667 | 356.061 | 381.5273 | 297.3457
1781.0667 | 355.869 | 380.0685 | 296.8448
1782.0667 | 356.1004 | 379.9003 | 297.3352
1783.0667 | 355.3821 | 380.549 | 297.8625
1784.0667 | 355.4057 | 381.2085 | 298.2282
1785.0667 | 355.7108 | 382.0195 | 298.1237
1786.0667 | 355.4486 | 381.2369 | 297.547
1787.0667 | 355.8095 | 381.2635 | 297.1394
1788.0667 | 356.2777 | 381.2281 | 296.6391
1789.0667 | 356.0423 | 381.0401 | 296.3463
1790.0667 | 356.2859 | 381.9066 | 296.4597
1791.0667 | 356.3001 | 382.3726 | 296.8879
1792.0667 | 356.43 | 382.3893 | 296.8236
1793.0667 | 355.1941 | 382.0911 | 296.9845
1794.0667 | 353.1337 | 382.3635 | 297.6528
1795.0667 | 351.3631 | 384.5281 | 299.1655
1796.0667 | 349.8767 | 384.6436 | 300.6785
1797.0667 | 349.7714 | 384.1319 | 301.6472
1798.0667 | 351.8105 | 384.0649 | 301.5367
1799.0667 | 352.4613 | 385.2496 | 301.7657
1800.0667 | 352.3836 | 384.2991 | 301.9934
1801.0667 | 352.1379 | 382.876 | 301.6565
1802.0667 | 354.4242 | 383.663 | 302.4527
1803.0667 | 356.1928 | 383.1145 | 301.9507
1804.0667 | 357.0723 | 382.4984 | 301.8665
1805.0667 | 357.6034 | 383.8018 | 302.2655
1806.0667 | 356.8824 | 384.4405 | 302.2509
1807.0667 | 357.2098 | 384.3554 | 302.0301
1808.0667 | 358.1439 | 384.5753 | 301.7616
1809.0667 | 359.0599 | 388.5167 | 301.69
1810.0667 | 358.9748 | 388.9666 | 301.6816
1811.0667 | 359.3574 | 388.8169 | 302.2813
1812.0667 | 358.862 | 389.0394 | 302.4283
1813.0667 | 358.6736 | 388.821 | 301.9976
1814.0667 | 358.0263 | 388.5204 | 303.1842
1815.0667 | 358.0758 | 388.5966 | 303.3289
1816.0667 | 358.0829 | 387.8727 | 303.1589
1817.0667 | 358.4352 | 388.2202 | 303.2025
1818.0667 | 358.5898 | 388.0608 | 302.5756
1819.0667 | 358.1122 | 387.9557 | 302.7436
1820.0667 | 357.3728 | 387.8237 | 302.6349
1821.0667 | 355.4239 | 385.901 | 302.9653
1822.0667 | 353.577 | 384.904 | 303.624
1823.0667 | 353.4413 | 385.098 | 303.9895
1824.0667 | 354.499 | 385.0049 | 303.8275
1825.0667 | 355.7931 | 383.9717 | 303.5676
1826.0667 | 357.4277 | 383.9385 | 303.7104
1827.0667 | 358.5446 | 385.7317 | 304.4135
1828.0667 | 359.94 | 387.2159 | 304.8048
1829.0667 | 359.8508 | 388.3218 | 304.9041
1830.0667 | 360.1179 | 388.9596 | 304.975
1831.0667 | 359.6846 | 389.7511 | 304.9651
1832.0667 | 358.5893 | 390.6644 | 305.3021
1833.0667 | 357.7663 | 390.3017 | 305.2724
1834.0667 | 357.4666 | 390.6371 | 305.3461
1835.0667 | 358.2529 | 391.0122 | 305.2183
1836.0667 | 358.7837 | 391.5314 | 305.3739
1837.0667 | 358.9347 | 391.9803 | 305.2056
1838.0667 | 358.5165 | 392.5163 | 305.8922
1839.0667 | 359.6292 | 393.6589 | 305.8554
1840.0667 | 361.2548 | 393.8667 | 305.598
1841.0667 | 361.1126 | 392.7471 | 304.995
1842.0667 | 360.7125 | 391.9608 | 304.5913
1843.0667 | 360.6556 | 391.5753 | 304.4456
1844.0667 | 361.1626 | 391.7588 | 304.842
1845.0667 | 360.5634 | 391.3718 | 305.0406
1846.0667 | 359.9516 | 391.9006 | 305.6145
1847.0667 | 359.4122 | 392.8911 | 306.5887
1848.0667 | 359.6715 | 393.7265 | 307.0618
1849.0667 | 359.5158 | 392.8272 | 307.5368
1850.0667 | 359.3033 | 393.12 | 307.5124
1851.0667 | 358.8089 | 392.9347 | 307.3439
1852.0667 | 358.1423 | 392.5603 | 307.3414
1853.0667 | 357.8764 | 391.795 | 307.1192
1854.0667 | 357.4484 | 391.9391 | 308.4751
1855.0667 | 356.2301 | 391.9649 | 309.3751
1856.0667 | 356.6724 | 392.161 | 310.1625
1857.0667 | 358.162 | 393.144 | 310.7422
1858.0667 | 358.1394 | 392.2803 | 310.1468
1859.0667 | 357.2598 | 390.8293 | 309.4772
1860.0667 | 355.6131 | 389.8632 | 309.811
1861.0667 | 354.1997 | 389.3173 | 310.7658
1862.0667 | 353.8436 | 390.448 | 311.2968
1863.0667 | 353.9097 | 390.1863 | 310.7278
1864.0667 | 353.6439 | 389.8301 | 309.8921
1865.0667 | 354.5288 | 390.4923 | 309.2646
1866.0667 | 355.6223 | 391.231 | 309.0315
1867.0667 | 355.0491 | 390.7277 | 308.3452
1868.0667 | 355.9439 | 390.948 | 307.9943
1869.0667 | 356.171 | 392.7495 | 307.7529
1870.0667 | 357.4011 | 392.4005 | 307.5506
1871.0667 | 359.302 | 391.7548 | 307.0954
1872.0667 | 359.8264 | 391.0431 | 306.5266
1873.0667 | 360.3014 | 390.0983 | 305.9115
1874.0667 | 359.5759 | 389.4605 | 305.387
1875.0667 | 360.3425 | 389.1096 | 304.9123
1876.0667 | 360.3573 | 389.4074 | 304.4426
1877.0667 | 360.3356 | 390.3042 | 304.0674
1878.0667 | 359.3801 | 389.1908 | 303.6761
1879.0667 | 358.2146 | 388.6159 | 303.476
1880.0667 | 357.5072 | 388.3492 | 303.4412
1881.0667 | 357.2053 | 388.7012 | 303.2352
1882.0823 | 358.0415 | 388.8782 | 303.0909
1883.0823 | 358.1649 | 387.9887 | 302.9182
1884.0667 | 358.1306 | 388.5737 | 303.0504
1885.0667 | 359.2266 | 388.5482 | 302.9254
1886.0667 | 360.9605 | 389.2023 | 302.8947
1887.0667 | 363.2233 | 390.3247 | 302.7882
1888.0667 | 364.6289 | 389.8459 | 302.5184
1889.0667 | 365.239 | 389.5543 | 302.2841
1890.0823 | 365.5335 | 390.2947 | 302.064
1891.0667 | 366.1526 | 390.5416 | 301.9079
1892.0667 | 366.4534 | 389.5983 | 301.7942
1893.0667 | 366.9005 | 391.5024 | 302.0125
1894.0667 | 366.1302 | 391.564 | 302.3985
1895.0667 | 364.6989 | 391.5419 | 302.6241
1896.0667 | 365.3943 | 392.0871 | 302.8453
1897.0667 | 367.1871 | 392.7688 | 302.9771
1898.0667 | 369.6056 | 392.8652 | 303.0549
1899.0667 | 371.3475 | 392.2296 | 303.0248
1900.0667 | 372.7362 | 391.1942 | 302.9514
1901.0667 | 372.9214 | 391.0611 | 303.1472
1902.0667 | 372.5192 | 390.1778 | 303.0727
1903.0667 | 371.9799 | 390.7803 | 303.1982
1904.0667 | 373.7297 | 391.5129 | 303.1445
1905.0667 | 374.5697 | 392.9747 | 303.23
1906.0667 | 374.7794 | 393.6145 | 303.2972
1907.0667 | 376.401 | 393.4385 | 303.4457
1908.0667 | 377.7143 | 393.4493 | 303.5081
1909.0667 | 379.3077 | 396.2187 | 303.8111
1910.0667 | 379.5719 | 396.4236 | 304.6106
1911.0667 | 379.1103 | 395.4116 | 304.2728
1912.0667 | 378.9045 | 395.6946 | 304.592
1913.0667 | 378.4342 | 395.8346 | 305.1915
1914.0667 | 377.7655 | 395.6353 | 305.3461
1915.0667 | 377.1046 | 396.1803 | 305.5846
1916.0667 | 376.138 | 396.315 | 306.4989
1917.0667 | 374.8221 | 396.4311 | 307.7604
1918.0667 | 373.7526 | 396.4359 | 308.874
1919.0667 | 372.6774 | 396.7638 | 309.6163
1920.0667 | 372.6941 | 397.4096 | 310.0621
1921.0667 | 372.9067 | 396.6587 | 309.9466
1922.0667 | 372.6417 | 396.8438 | 310.4002
1923.0667 | 371.8721 | 398.3738 | 310.9548
1924.0667 | 371.4491 | 398.7671 | 310.9133
1925.0667 | 370.6005 | 400.0898 | 310.8349
1926.0667 | 369.2307 | 402.9686 | 311.1859
1927.0667 | 368.0986 | 403.7166 | 311.6396
1928.0667 | 366.7515 | 403.4064 | 311.6496
1929.0667 | 367.3548 | 403.9728 | 312.1872
1930.0667 | 367.7562 | 406.0068 | 312.4134
1931.0667 | 367.3744 | 407.0434 | 312.5136
1932.0667 | 367.3911 | 406.8726 | 312.6787
1933.0667 | 366.603 | 405.6251 | 312.9491
1934.0667 | 365.2713 | 405.3388 | 313.5121
1935.0667 | 364.3721 | 408.8442 | 314.3507
1936.0667 | 364.133 | 407.3735 | 315.6862
1937.0667 | 364.4525 | 406.7931 | 316.0013
1938.0667 | 363.7405 | 406.3952 | 316.7993
1939.0667 | 362.5754 | 405.2896 | 317.7393
1940.0667 | 361.6629 | 405.1959 | 318.619
1941.0667 | 361.2061 | 405.2155 | 319.3151
1942.0667 | 361.1742 | 406.1365 | 319.3743
1943.0667 | 361.6438 | 406.945 | 320.0579
1944.0667 | 362.2965 | 407.572 | 320.3922
1945.0667 | 364.5014 | 408.4213 | 320.3338
1946.0667 | 365.6612 | 410.2998 | 320.1444
1947.0667 | 367.1613 | 409.7294 | 320.3012
1948.0667 | 367.9 | 408.5132 | 319.8651
1949.0667 | 368.3185 | 408.5669 | 319.6467
1950.0667 | 368.2599 | 408.0226 | 320.4093
1951.0667 | 369.4 | 407.3365 | 320.2615
1952.0667 | 370.4579 | 406.1905 | 319.7743
1953.0667 | 370.6805 | 407.5304 | 319.5228
1954.0667 | 371.0052 | 407.1676 | 319.5432
1955.0667 | 371.3128 | 407.1091 | 319.3356
1956.0667 | 371.728 | 405.9466 | 319.1312
1957.0667 | 370.3993 | 404.3977 | 318.9984
1958.0667 | 369.292 | 403.4494 | 318.9381
1959.0667 | 367.5589 | 402.1507 | 319.6088
1960.0667 | 366.3217 | 401.5907 | 321.5111
1961.0667 | 364.8031 | 400.9401 | 322.4434
1962.0667 | 364.1468 | 400.9493 | 322.6643
1963.0667 | 362.5089 | 401.3362 | 323.14
1964.0667 | 361.3459 | 401.7699 | 323.6731
1965.0667 | 362.0841 | 402.212 | 323.6346
1966.0667 | 363.0277 | 401.8663 | 323.3242
1967.0667 | 365.0096 | 403.1454 | 322.8001
1968.0667 | 365.5194 | 402.9141 | 322.2409
1969.0667 | 365.5155 | 405.5706 | 322.6142
1970.0667 | 365.5854 | 405.5592 | 322.6238
1971.0667 | 365.4199 | 405.4264 | 322.2958
1972.0667 | 366.0733 | 405.0202 | 322.0648
1973.0667 | 365.4893 | 404.548 | 321.935
1974.0667 | 365.9376 | 406.0932 | 322.346
1975.0667 | 366.812 | 407.4971 | 322.3293
1976.0667 | 366.8283 | 408.9712 | 323.347
1977.0667 | 367.7744 | 410.3628 | 323.4277
1978.0667 | 369.3136 | 409.9644 | 323.0057
1979.0667 | 372.0052 | 413.0093 | 322.6726
1980.0667 | 372.28 | 414.2348 | 322.3548
1981.0667 | 373.511 | 417.4827 | 322.233
1982.0667 | 374.7177 | 417.609 | 322.1324
1983.0667 | 374.7197 | 417.1472 | 321.6507
1984.0667 | 374.4659 | 418.4723 | 321.4718
1985.0667 | 375.1895 | 422.7187 | 321.4917
1986.0667 | 376.0444 | 426.6114 | 322.1581
1987.0667 | 375.8231 | 432.0216 | 323.3995
1988.0667 | 376.7376 | 437.7135 | 323.8514
1989.0667 | 376.9486 | 445.6182 | 324.6577
1990.0667 | 377.1416 | 463.5583 | 325.0734
1991.0667 | 377.8412 | 472.6534 | 325.3045
1992.0667 | 379.2967 | 477.4433 | 325.2776
1993.0667 | 380.5549 | 487.4102 | 325.1489
1994.0667 | 385.0061 | 491.5992 | 325.1166
1995.0667 | 386.6203 | 489.5489 | 325.3118
1996.0667 | 388.0314 | 487.8041 | 325.7002
1997.0667 | 390.053 | 486.8977 | 326.0744
1998.0667 | 390.8909 | 485.9395 | 326.848
1999.0667 | 390.976 | 481.7762 | 327.4099
2000.0667 | 390.2305 | 476.3776 | 327.3018
2001.0667 | 389.3868 | 479.5032 | 327.6981
2002.0667 | 391.4929 | 485.0374 | 328.0455
2003.0667 | 395.6599 | 484.9455 | 327.8196
2004.0667 | 398.5757 | 479.506 | 327.2879
2005.0667 | 400.0914 | 474.9347 | 326.7872
2006.0667 | 400.8641 | 476.7705 | 326.3614
2007.0667 | 401.9252 | 472.5933 | 325.8723
2008.0667 | 402.0813 | 468.463 | 325.5308
2009.0667 | 403.3011 | 464.6833 | 325.2307
2010.0667 | 404.0438 | 462.6632 | 324.978
2011.0667 | 404.7257 | 466.5345 | 325.2046
2012.0667 | 404.5446 | 467.6675 | 325.4775
2013.0667 | 402.0459 | 462.0335 | 325.4404
2014.0667 | 401.046 | 464.7133 | 325.9295
2015.0667 | 400.5738 | 464.2169 | 326.1362
2016.0667 | 400.1813 | 462.3702 | 326.1368
2017.0667 | 398.8778 | 458.8217 | 326.2322
2018.0667 | 397.7918 | 456.0819 | 326.5109
2019.0667 | 396.1639 | 454.3958 | 327.0908
2020.0667 | 396.1931 | 453.4831 | 327.0785
2021.0667 | 398.4143 | 458.5621 | 327.022
2022.0667 | 400.324 | 459.0358 | 326.7614
2023.0667 | 402.352 | 458.753 | 326.5544
2024.0667 | 404.7814 | 457.7666 | 326.37
2025.0667 | 406.2184 | 460.605 | 326.3385
2026.0667 | 406.6778 | 464.2271 | 326.7175
2027.0667 | 406.9805 | 472.6991 | 327.0987
2028.0667 | 407.5016 | 479.208 | 327.6359
2029.0667 | 408.677 | 483.7416 | 328.0133
2030.0667 | 409.1999 | 483.8658 | 328.0774
2031.0667 | 409.016 | 485.3331 | 328.1849
2032.0667 | 411.8053 | 487.338 | 328.1266
2033.0667 | 412.708 | 486.8925 | 328.0555
2034.0667 | 414.3988 | 489.1501 | 328.1845
2035.0667 | 414.6412 | 487.1929 | 328.3962
2036.0667 | 415.4443 | 486.2311 | 328.6959
2037.0667 | 415.8244 | 489.9181 | 328.7205
2038.0667 | 418.038 | 491.6026 | 328.6416
2039.0667 | 419.6795 | 491.7272 | 328.7607
2040.0667 | 420.8132 | 496.6004 | 328.7666
2041.0667 | 423.8026 | 497.1985 | 328.7216
2042.0667 | 428.3377 | 496.6983 | 328.7755
2043.0667 | 431.0326 | 496.3463 | 329.0453
2044.0667 | 431.1274 | 500.9607 | 329.4697
2045.0667 | 432.5424 | 508.4552 | 330.1587
2046.0667 | 434.6784 | 510.0522 | 330.5588
2047.0667 | 435.8284 | 512.0356 | 330.8914
2048.0667 | 435.028 | 514.8056 | 331.3383
2049.0667 | 437.2421 | 520.5963 | 331.7684
2050.0667 | 437.3964 | 523.8854 | 331.9401
2051.0667 | 438.4225 | 528.5922 | 332.5345
2052.0667 | 437.7524 | 529.3545 | 332.8835
2053.0667 | 438.297 | 528.4178 | 332.9974
2054.0667 | 438.375 | 533.4789 | 333.2865
2055.0667 | 440.0214 | 537.538 | 333.6685
2056.0667 | 440.0776 | 540.8319 | 334.1192
2057.0667 | 439.401 | 544.6008 | 334.401
2058.0667 | 439.9142 | 546.7266 | 334.8272
2059.0667 | 442.0811 | 549.666 | 335.1411
2060.0667 | 443.9106 | 553.7225 | 335.4004
2061.0667 | 443.5007 | 555.4383 | 335.8119
2062.0667 | 444.5274 | 562.3552 | 336.1352
2063.0667 | 444.06 | 563.14 | 336.8158
2064.0667 | 442.6479 | 562.807 | 337.2792
2065.0667 | 442.0455 | 567.4951 | 337.5395
2066.0667 | 443.3769 | 571.2656 | 337.8824
2067.0667 | 443.2351 | 573.0644 | 338.156
2068.0667 | 442.1723 | 573.5257 | 338.2264
2069.0667 | 443.1856 | 575.8164 | 338.23
2070.0667 | 442.7692 | 572.2128 | 338.2415
2071.0667 | 441.876 | 569.8211 | 338.1175
2072.0667 | 441.1827 | 565.2061 | 337.8908
2073.0667 | 443.7692 | 565.2056 | 338.0725
2074.0667 | 442.7275 | 563.047 | 338.471
2075.0667 | 442.2188 | 560.0126 | 339.0855
2076.0667 | 441.5536 | 562.474 | 339.96
2077.0667 | 439.785 | 560.9361 | 340.4262
2078.0667 | 438.7675 | 557.4179 | 340.74
2079.0667 | 441.0798 | 556.7924 | 341.1042
2080.0667 | 441.7127 | 554.6415 | 341.556
2081.0667 | 442.2877 | 553.4567 | 342.114
2082.0667 | 443.9256 | 552.7196 | 342.764
2083.0667 | 446.3924 | 551.3018 | 343.5423
2084.0667 | 448.1335 | 551.9005 | 344.5094
2085.0667 | 448.5822 | 549.5448 | 345.369
2086.0667 | 448.734 | 546.1915 | 345.5414
2087.0667 | 448.9294 | 543.529 | 345.9489
2088.0667 | 450.904 | 543.8513 | 346.1903
2089.0667 | 453.1999 | 543.1706 | 346.6542
2090.0823 | 455.2443 | 542.7584 | 347.0636
2091.0667 | 457.7961 | 542.6772 | 347.6732
2092.0667 | 457.8046 | 539.9519 | 347.826
2093.0667 | 458.5627 | 538.904 | 348.0936
2094.0667 | 457.674 | 535.7454 | 348.3899
2095.0667 | 457.9235 | 532.0677 | 348.4958
2096.0667 | 456.5727 | 528.2746 | 348.2559
2097.0667 | 459.4043 | 527.6433 | 348.0857
2098.0667 | 459.191 | 524.596 | 348.1507
2099.0667 | 461.7866 | 525.2792 | 348.7613
2100.0667 | 462.9941 | 524.7792 | 348.8781
2101.0667 | 464.1853 | 525.0995 | 348.7791
2102.0667 | 465.9703 | 524.28 | 348.8368
2103.0667 | 468.1573 | 523.4419 | 348.6642
2104.0667 | 470.1642 | 522.5251 | 348.3505
2105.0667 | 470.0739 | 521.9787 | 348.6723
2106.0667 | 470.9164 | 520.3794 | 348.8646
2107.0667 | 470.3077 | 516.8897 | 349.0983
2108.0667 | 469.5163 | 514.2034 | 348.9239
2109.0667 | 471.1059 | 518.0321 | 349.1177
2110.0667 | 471.9524 | 518.8493 | 349.1358
2111.0667 | 471.8879 | 518.78 | 348.8214
2112.0667 | 472.4172 | 517.7525 | 348.4064
2113.0667 | 474.2955 | 517.9535 | 347.8871
2114.0667 | 477.0013 | 516.116 | 347.3254
2115.0667 | 479.3779 | 516.9764 | 347.2703
2116.0667 | 481.4007 | 517.42 | 347.3632
2117.0667 | 481.3026 | 520.632 | 347.998
2118.0667 | 481.409 | 525.1125 | 348.1353
2119.0667 | 485.0833 | 527.0897 | 348.1965
2120.0667 | 486.7737 | 526.146 | 348.23
2121.0667 | 490.5632 | 531.9681 | 348.8781
2122.0667 | 492.9532 | 533.034 | 349.1735
2123.0667 | 498.1416 | 530.8002 | 349.0954
2124.0667 | 502.7782 | 530.0702 | 348.828
2125.0667 | 504.9138 | 531.7936 | 348.636
2126.0667 | 506.8403 | 533.9742 | 348.587
2127.0667 | 509.3719 | 535.6796 | 348.5677
2128.0667 | 510.555 | 533.3006 | 348.604
2129.0667 | 512.3314 | 534.4362 | 348.5979
2130.0667 | 512.6955 | 535.6299 | 348.6968
2131.0667 | 515.8444 | 537.3009 | 349.2885
2132.0667 | 518.0483 | 538.51 | 349.4651
2133.0667 | 519.3997 | 537.3724 | 350.0612
2134.0667 | 521.034 | 539.4476 | 350.0491
2135.0667 | 522.4635 | 541.4499 | 350.372
2136.0667 | 523.2159 | 544.468 | 351.336
2137.0667 | 524.8211 | 545.8281 | 352.0492
2138.0667 | 524.0537 | 546.3931 | 352.5726
2139.0667 | 524.5759 | 547.6264 | 353.2217
2140.0667 | 525.5177 | 548.8282 | 354.0437
2141.0667 | 526.5267 | 550.386 | 354.7781
2142.0667 | 526.3008 | 544.6864 | 355.1353
2143.0667 | 529.1529 | 546.0863 | 355.4444
2144.0667 | 531.2584 | 548.6852 | 355.886
2145.0667 | 533.8709 | 548.3973 | 356.3055
2146.0667 | 538.0096 | 551.551 | 356.8656
2147.0667 | 538.1874 | 551.4834 | 357.4268
2148.0667 | 538.6295 | 549.6644 | 358.0432
2149.0667 | 539.351 | 550.6992 | 358.2105
2150.0667 | 539.5541 | 555.7577 | 358.6175
2151.0667 | 542.1635 | 556.4076 | 359.0565
2152.0667 | 543.3147 | 556.7272 | 359.6799
2153.0667 | 545.0542 | 558.0931 | 360.1614
2154.0667 | 548.4615 | 559.0102 | 360.8211
2155.0667 | 551.0978 | 557.9912 | 361.558
2156.0667 | 551.2941 | 556.3677 | 361.9684
2157.0667 | 550.5652 | 560.5765 | 362.1401
2158.0667 | 550.4019 | 562.6613 | 362.961
2159.0667 | 549.3702 | 560.4312 | 363.3135
2160.0667 | 549.0729 | 563.0178 | 363.6867
2161.0667 | 547.9197 | 560.3399 | 363.8964
2162.0667 | 545.2767 | 559.5074 | 363.655
2163.0667 | 543.4577 | 557.8756 | 363.9004
2164.0667 | 541.5888 | 559.1814 | 364.5864
2165.0667 | 536.77 | 559.9295 | 365.7263
2166.0667 | 532.7632 | 560.4128 | 366.7052
2167.0667 | 531.6026 | 557.0117 | 367.0748
2168.0667 | 531.0159 | 557.4539 | 367.0258
2169.0667 | 529.2355 | 559.7359 | 367.0358
2170.0667 | 528.2511 | 559.6953 | 367.5795
2171.0667 | 526.4646 | 556.9049 | 367.6394
2172.0667 | 523.7386 | 550.8835 | 367.6362
2173.0667 | 524.5035 | 552.4438 | 367.8184
2174.0667 | 525.5923 | 556.4611 | 368.1717
2175.0667 | 524.4325 | 553.8686 | 368.774
2176.0667 | 522.1417 | 551.727 | 369.1733
2177.0667 | 518.9602 | 552.2481 | 370.3433
2178.0667 | 515.4527 | 550.3561 | 370.9319
2179.0667 | 513.0721 | 552.4557 | 371.6323
2180.0667 | 514.3946 | 551.7816 | 372.2359
2181.0667 | 514.2327 | 551.2368 | 372.8549
2182.0667 | 516.7152 | 548.2136 | 372.922
2183.0667 | 517.5671 | 548.2981 | 372.7145
2184.0667 | 518.3181 | 548.7437 | 372.6063
2185.0667 | 517.4655 | 553.7095 | 372.6691
2186.0667 | 516.4972 | 556.6869 | 373.0844
2187.0667 | 514.5243 | 556.547 | 373.5785
2188.0667 | 512.791 | 555.561 | 374.3035
2189.0667 | 511.0678 | 555.5226 | 375.3431
2190.0667 | 514.0971 | 556.1406 | 375.9813
2191.0667 | 520.0046 | 561.3431 | 377.239
2192.0667 | 519.1944 | 560.8102 | 378.1444
2193.0667 | 519.9854 | 559.7337 | 378.1344
2194.0667 | 524.2701 | 560.6466 | 379.1903
2195.0667 | 524.301 | 561.2107 | 380.4063
2196.0667 | 524.1745 | 561.289 | 380.8677
2197.0667 | 521.6106 | 560.4379 | 381.3532
2198.0667 | 518.9206 | 558.5426 | 381.5266
2199.0667 | 517.7581 | 557.0919 | 382.1113
2200.0667 | 518.1363 | 563.7284 | 382.1456
2201.0667 | 518.3866 | 563.4008 | 382.2253
2202.0667 | 519.2473 | 560.4322 | 381.9361
2203.0667 | 521.5118 | 555.8334 | 381.9566
2204.0667 | 526.73 | 556.9999 | 382.8399
2205.0667 | 526.1298 | 558.0751 | 383.6612
2206.0667 | 523.9096 | 563.2484 | 384.066
2207.0667 | 522.5774 | 564.2849 | 383.8807
2208.0667 | 523.1595 | 561.4308 | 383.3083
2209.0667 | 524.328 | 558.7707 | 382.5525
2210.0667 | 526.3055 | 559.2239 | 382.1631
2211.0667 | 528.9096 | 558.1942 | 382.4726
2212.0667 | 531.9467 | 560.3948 | 382.381
2213.0667 | 532.4315 | 559.6527 | 382.6306
2214.0667 | 532.396 | 554.42 | 382.101
2215.0667 | 536.4917 | 550.7515 | 381.9657
2216.0667 | 541.5416 | 548.5835 | 382.0253
2217.0667 | 542.0599 | 547.1645 | 382.6553
2218.0667 | 542.2991 | 545.9872 | 382.568
2219.0667 | 544.8214 | 545.9516 | 381.8661
2220.0823 | 547.7796 | 547.7074 | 381.5264
2221.0667 | 550.008 | 544.2608 | 381.0701
2222.0667 | 553.6105 | 545.6651 | 380.3232
2223.0667 | 555.686 | 545.6133 | 380.0898
2224.0667 | 558.6709 | 548.2174 | 380.313
2225.0667 | 560.6796 | 549.2451 | 380.1587
2226.0667 | 561.0737 | 548.5845 | 379.8601
2227.0667 | 565.0286 | 550.5024 | 380.1347
2228.0667 | 566.5456 | 554.1311 | 380.3719
2229.0667 | 569.0183 | 557.4261 | 380.8964
2230.0667 | 570.7055 | 556.9088 | 380.9026
2231.0667 | 571.4475 | 556.5143 | 380.8282
2232.0667 | 572.0322 | 557.7161 | 380.959
2233.0667 | 574.429 | 555.0661 | 380.85
2234.0667 | 575.6415 | 552.6269 | 380.645
2235.0667 | 576.9595 | 554.378 | 380.4826
2236.0667 | 577.4626 | 555.6225 | 380.7478
2237.0667 | 577.9139 | 555.5749 | 380.7918
2238.0667 | 578.1731 | 556.6008 | 381.0151
2239.0667 | 576.4506 | 557.9314 | 381.0067
2240.0667 | 574.2941 | 557.8111 | 381.0897
2241.0667 | 571.363 | 555.5592 | 382.2158
2242.0667 | 569.805 | 555.7866 | 382.6762
2243.0667 | 567.0588 | 554.4051 | 382.6299
2244.0667 | 564.6897 | 552.5795 | 382.1665
2245.0667 | 563.6287 | 552.0974 | 381.8226
2246.0667 | 562.8296 | 549.6811 | 381.6783
2247.0667 | 565.3179 | 550.7606 | 381.8686
2248.0823 | 566.8689 | 551.9305 | 381.7006
2249.0667 | 567.8955 | 551.6556 | 381.6726
2250.0667 | 567.594 | 551.298 | 381.6306
2251.0667 | 568.3339 | 551.8824 | 381.8294
2252.0667 | 570.1612 | 555.545 | 382.2937
2253.0667 | 570.5046 | 557.9552 | 382.4795
2254.0667 | 569.5241 | 560.0719 | 383.0014
2255.0667 | 569.449 | 561.316 | 383.2222
2256.0667 | 568.3839 | 560.9699 | 383.3505
2257.0667 | 568.0071 | 561.3488 | 383.7039
2258.0667 | 566.4747 | 558.9874 | 383.6873
2259.0667 | 566.2344 | 555.8387 | 383.6485
2260.0667 | 571.6788 | 556.5368 | 383.9539
2261.0667 | 572.2272 | 557.5895 | 384.4869
2262.0667 | 571.1805 | 560.8225 | 384.527
2263.0667 | 570.483 | 563.0057 | 384.4427
2264.0667 | 568.89 | 563.0565 | 384.4409
2265.0667 | 568.0788 | 560.905 | 384.2682
2266.0667 | 568.1527 | 564.0799 | 384.2857
2267.0667 | 569.1038 | 562.9618 | 384.3315
2268.0667 | 567.3432 | 563.049 | 384.0916
2269.0667 | 567.2005 | 562.5649 | 384.0937
2270.0667 | 568.0402 | 561.9296 | 384.5494
2271.0667 | 566.9062 | 561.2929 | 385.0471
2272.0667 | 564.7434 | 559.2019 | 384.9633
2273.0667 | 564.6569 | 556.2976 | 384.2829
2274.0667 | 563.4974 | 558.3223 | 384.2279
2275.0667 | 562.5561 | 558.8633 | 384.1805
2276.0667 | 562.2545 | 558.0168 | 384.0774
2277.0667 | 563.2955 | 558.0046 | 384.2689
2278.0667 | 563.6573 | 558.9869 | 384.5256
2279.0667 | 562.874 | 558.4559 | 384.8408
2280.0667 | 561.8135 | 560.9175 | 385.0703
2281.0667 | 557.377 | 562.3161 | 385.4674
2282.0667 | 556.8797 | 562.3769 | 386.2411
2283.0667 | 557.5524 | 563.4635 | 386.749
2284.0667 | 556.7854 | 560.0046 | 386.8226
2285.0667 | 554.8984 | 558.2264 | 386.5187
2286.0667 | 556.0657 | 561.5381 | 386.5084
2287.0667 | 555.3388 | 561.0532 | 386.5704
2288.0667 | 551.7261 | 559.5886 | 386.7317
2289.0667 | 549.1355 | 559.571 | 386.5237
2290.0667 | 549.1312 | 561.2055 | 386.2972
2291.0667 | 547.2326 | 562.3364 | 385.9839
2292.0667 | 545.6757 | 565.5725 | 385.8771
2293.0667 | 543.055 | 564.7323 | 385.8684
2294.0667 | 540.1302 | 565.3387 | 385.9437
2295.0667 | 539.3526 | 565.0445 | 385.7699
2296.0667 | 541.1168 | 565.9958 | 385.6854
2297.0667 | 544.1596 | 567.5556 | 385.7398
2298.0667 | 546.2865 | 566.7483 | 385.7942
2299.0667 | 546.7272 | 567.0326 | 385.8627
2300.0667 | 547.6062 | 567.6727 | 385.7241
2301.0667 | 547.0806 | 567.313 | 385.5963
2302.0667 | 546.9658 | 568.1162 | 385.6349
2303.0667 | 546.6859 | 569.3924 | 385.841
2304.0667 | 547.2966 | 565.5576 | 385.7886
2305.0667 | 547.5967 | 564.76 | 385.5744
2306.0667 | 548.1955 | 560.6949 | 385.1614
2307.0667 | 548.5568 | 562.1859 | 384.5928
2308.0667 | 549.8732 | 561.9502 | 384.3223
2309.0667 | 549.6871 | 560.3478 | 384.3863
2310.0667 | 551.0176 | 559.9324 | 384.4786
2311.0667 | 550.1028 | 557.8847 | 384.6726
2312.0667 | 546.0193 | 556.5365 | 384.9417
2313.0667 | 545.2386 | 554.3082 | 385.0966
2314.0667 | 544.9136 | 550.2162 | 385.0783
2315.0667 | 545.2484 | 550.3316 | 385.053
2316.0667 | 546.6224 | 550.373 | 385.1679
2317.0667 | 544.5743 | 547.1547 | 385.0534
2318.0667 | 543.785 | 545.8018 | 384.9581
2319.0667 | 540.6664 | 543.4474 | 384.8853
2320.0667 | 538.3573 | 542.1264 | 385.0288
2321.0667 | 534.9965 | 540.3904 | 385.4313
2322.0667 | 531.8558 | 537.9492 | 385.6465
2323.0667 | 532.3792 | 538.0527 | 385.7546
2324.0667 | 529.4023 | 535.5267 | 385.7531
2325.0667 | 527.5876 | 533.0624 | 385.5204
2326.0667 | 528.3439 | 531.6405 | 385.204
2327.0667 | 528.3783 | 531.8376 | 385.0297
2328.0667 | 530.4481 | 531.0715 | 384.6776
2329.0667 | 529.7172 | 527.7164 | 384.1948
2330.0667 | 527.1403 | 523.1506 | 383.7636
2331.0667 | 529.3856 | 524.2822 | 383.814
2332.0667 | 529.0545 | 525.1471 | 383.9209
2333.0667 | 526.353 | 524.2095 | 384.121
2334.0667 | 524.7611 | 521.0454 | 384.0953
2335.0667 | 525.2119 | 529.1555 | 384.1087
2336.0667 | 524.8797 | 530.9837 | 384.1135
2337.0667 | 525.96 | 530.1339 | 384.1297
2338.0667 | 524.1855 | 530.9009 | 384.1046
2339.0667 | 523.6608 | 529.9657 | 383.9222
2340.0667 | 524.0841 | 528.5376 | 383.9458
2341.0667 | 523.7571 | 527.7962 | 383.8979
2342.0667 | 522.8024 | 528.1939 | 383.9397
2343.0667 | 520.1105 | 530.9229 | 384.0333
2344.0667 | 519.1165 | 531.4968 | 384.2215
2345.0667 | 515.9821 | 533.8387 | 384.6424
2346.0667 | 513.9451 | 536.27 | 384.9245
2347.0667 | 513.7228 | 538.5839 | 385.115
2348.0667 | 514.3988 | 539.3931 | 385.3288
2349.0667 | 515.3188 | 538.7346 | 385.597
2350.0667 | 514.1131 | 541.1599 | 385.6873
2351.0667 | 513.1866 | 540.1079 | 385.7414
2352.0667 | 513.1417 | 544.3917 | 385.7624
2353.0667 | 513.9287 | 543.4435 | 385.8248
2354.0667 | 515.9677 | 540.2171 | 385.782
2355.0667 | 516.8428 | 541.537 | 385.85
2356.0667 | 516.7505 | 543.0012 | 386.2081
2357.0667 | 516.6101 | 545.0893 | 386.6745
2358.0667 | 516.4612 | 548.2582 | 387.0931
2359.0667 | 517.0667 | 549.5465 | 387.4078
2360.0667 | 516.4217 | 548.5542 | 387.626
2361.0667 | 515.6615 | 548.7041 | 387.7299
2362.0667 | 514.9579 | 549.8216 | 387.8557
2363.0667 | 517.0834 | 549.6665 | 388.0082
2364.0667 | 518.7508 | 552.2146 | 388.3193
2365.0667 | 519.9963 | 553.4278 | 388.5664
2366.0667 | 519.8425 | 558.1008 | 388.8891
2367.0667 | 517.8388 | 555.2677 | 388.958
2368.0667 | 516.1079 | 552.2786 | 389.0656
2369.0667 | 516.2266 | 554.1538 | 389.2432
2370.0667 | 515.9974 | 555.7269 | 389.5527
2371.0667 | 516.917 | 559.0621 | 389.739
2372.0667 | 518.5567 | 556.7274 | 389.802
2373.0667 | 520.1462 | 558.1231 | 389.7621
2374.0667 | 521.3317 | 557.1876 | 389.6028
2375.0667 | 522.2485 | 556.8728 | 389.4717
2376.0667 | 522.7054 | 556.9932 | 389.6693
2377.0667 | 525.6686 | 556.977 | 389.9192
2378.0667 | 527.036 | 566.3587 | 390.1062
2379.0667 | 527.3624 | 567.7074 | 390.3443
2380.0667 | 526.4535 | 566.7345 | 390.5863
2381.0667 | 526.8046 | 564.0277 | 390.7982
2382.0667 | 525.3134 | 567.3581 | 391.1617
2383.0667 | 524.2809 | 571.1117 | 391.8776
2384.0667 | 524.7068 | 572.2228 | 392.6067
2385.0667 | 524.2361 | 570.9622 | 393.5029
2386.0667 | 525.663 | 570.571 | 394.3529
2387.0667 | 526.2658 | 571.78 | 395.3086
2388.0667 | 525.2908 | 570.9107 | 395.9588
2389.0667 | 524.5489 | 570.5991 | 396.2162
2390.0667 | 525.9951 | 571.7105 | 396.3845
2391.0667 | 524.4351 | 568.278 | 396.6298
2392.0667 | 524.1554 | 566.2046 | 396.7976
2393.0667 | 523.1608 | 563.8963 | 396.8502
2394.0667 | 523.3892 | 564.8113 | 397.0015
2395.0667 | 523.345 | 561.0122 | 397.1
2396.0667 | 518.9637 | 556.0555 | 396.9491
2397.0667 | 517.876 | 555.1312 | 397.0553
2398.0667 | 515.3201 | 552.5625 | 396.9869
2399.0667 | 513.0697 | 553.5318 | 397.0487
2400.0667 | 512.5801 | 553.3577 | 397.4128
2401.0667 | 511.7646 | 552.6741 | 397.3976
2402.0667 | 511.1632 | 551.2302 | 397.1062
2403.0667 | 510.8083 | 553.1925 | 396.7543
2404.0667 | 511.5527 | 552.0736 | 396.3788
2405.0667 | 511.0202 | 553.646 | 396.0166
2406.0667 | 507.8266 | 547.7381 | 395.7071
2407.0667 | 505.2812 | 546.3104 | 395.6295
2408.0667 | 503.4813 | 547.0854 | 395.4192
2409.0667 | 501.0852 | 544.8984 | 395.2701
2410.0667 | 498.7882 | 545.6027 | 395.0686
2411.0667 | 497.5453 | 543.1183 | 394.8243
2412.0667 | 498.2904 | 544.3004 | 394.594
2413.0667 | 496.6291 | 541.174 | 394.2958
2414.0667 | 495.7769 | 538.9109 | 394.0059
2415.0667 | 498.3185 | 541.9424 | 393.7988
2416.0667 | 497.4958 | 536.012 | 393.5544
2417.0667 | 497.6785 | 534.0002 | 393.3479
2418.0667 | 496.8737 | 534.8226 | 393.3369
2419.0667 | 494.0526 | 533.0435 | 393.2865
2420.0667 | 492.7376 | 531.3397 | 393.0772
2421.0667 | 491.0726 | 529.3612 | 392.909
2422.0667 | 488.7776 | 527.9711 | 392.6532
2423.0667 | 487.4615 | 526.1602 | 392.328
2424.0667 | 485.6844 | 529.3466 | 391.9269
2425.0667 | 485.8685 | 535.0998 | 391.5161
2426.0667 | 486.776 | 534.5547 | 390.8797
2427.0667 | 488.0816 | 531.7692 | 390.5912
2428.0667 | 487.8895 | 533.0605 | 390.964
2429.0667 | 486.4273 | 530.4047 | 391.1895
2430.0667 | 485.168 | 531.6154 | 391.2569
2431.0667 | 485.2322 | 532.1085 | 391.1601
2432.0667 | 487.2298 | 531.742 | 391.0373
2433.0667 | 491.6754 | 530.6709 | 390.8973
2434.0667 | 493.3804 | 530.9734 | 390.627
2435.0823 | 495.8548 | 531.2775 | 390.3913
2436.0667 | 496.9389 | 532.7694 | 390.0821
2437.0667 | 497.319 | 532.2021 | 389.7967
2438.0667 | 498.4701 | 530.6881 | 389.5712
2439.0667 | 499.5749 | 534.0287 | 389.6954
2440.0667 | 500.0443 | 538.7076 | 390.0937
2441.0667 | 500.5586 | 538.5085 | 390.5687
2442.0667 | 499.0337 | 540.7506 | 390.9369
2443.0667 | 497.6601 | 540.9731 | 391.1887
2444.0667 | 496.5719 | 540.3241 | 391.3903
2445.0667 | 495.2163 | 535.5758 | 391.4258
2446.0823 | 494.5474 | 533.7688 | 391.4124
2447.0667 | 495.5754 | 531.1119 | 391.5595
2448.0667 | 494.9344 | 528.3629 | 391.5532
2449.0667 | 495.2645 | 530.4725 | 391.608
2450.0667 | 497.0267 | 526.7325 | 391.4117
2451.0667 | 498.9864 | 527.3631 | 391.1486
2452.0667 | 501.2438 | 533.3364 | 390.9488
2453.0667 | 503.3909 | 531.1424 | 390.8544
2454.0667 | 505.4213 | 533.8015 | 390.8544
2455.0667 | 507.2698 | 533.4847 | 390.8105
2456.0667 | 508.2413 | 536.4693 | 390.8468
2457.0667 | 511.1833 | 535.3451 | 390.8043
2458.0667 | 513.3779 | 535.1797 | 390.8848
2459.0667 | 516.1367 | 535.5928 | 390.9945
2460.0667 | 517.7838 | 537.9459 | 391.2923
2461.0667 | 517.6404 | 542.1563 | 391.7023
2462.0667 | 518.8264 | 543.0256 | 392.161
2463.0667 | 521.4378 | 543.062 | 392.5503
2464.0667 | 527.3477 | 542.6819 | 392.9166
2465.0667 | 527.8903 | 543.4644 | 393.4017
2466.0667 | 525.5158 | 544.1947 | 393.8667
2467.0667 | 524.3375 | 541.0641 | 394.1013
2468.0667 | 523.7438 | 540.5577 | 394.2476
2469.0667 | 524.0244 | 538.4819 | 394.4207
2470.0667 | 524.3325 | 540.4916 | 394.5714
2471.0667 | 525.4684 | 539.0215 | 394.8881
2472.0667 | 526.0388 | 540.5274 | 395.252
2473.0667 | 526.505 | 538.5915 | 395.4558
2474.0667 | 525.6871 | 536.9767 | 395.4652
2475.0667 | 525.2893 | 537.4093 | 395.6364
2476.0823 | 523.5345 | 537.4084 | 395.817
2477.0667 | 521.0108 | 536.9361 | 395.851
2478.0667 | 520.9446 | 536.6188 | 395.8457
2479.0667 | 519.7151 | 535.8757 | 395.9446
2480.0667 | 522.5304 | 533.4528 | 396.083
2481.0667 | 522.3568 | 531.7491 | 396.466
2482.0667 | 520.5975 | 533.8735 | 396.7046
2483.0667 | 520.178 | 533.796 | 396.8167
2484.0667 | 517.8844 | 534.2371 | 396.7476
2485.0667 | 517.4467 | 531.4333 | 396.5863
2486.0667 | 517.6887 | 533.0681 | 396.651
2487.0667 | 517.6325 | 531.1463 | 396.9274
2488.0667 | 516.0014 | 534.0642 | 397.2139
2489.0667 | 514.7791 | 538.5207 | 397.3403
2490.0667 | 518.2344 | 539.6337 | 397.3289
2491.0667 | 519.3678 | 537.7045 | 397.0497
2492.0667 | 519.2578 | 534.2198 | 396.6431
2493.0667 | 518.37 | 534.781 | 396.4683
2494.0667 | 514.9315 | 533.4116 | 396.5768
2495.0667 | 513.8403 | 533.2234 | 396.8217
2496.0667 | 511.7266 | 531.6457 | 397.0488
2497.0667 | 510.8369 | 534.8625 | 397.1295
2498.0667 | 509.7105 | 535.1188 | 397.2095
2499.0667 | 511.6598 | 537.8615 | 397.3623
2500.0667 | 511.8484 | 538.8943 | 397.5266
2501.0667 | 512.9043 | 536.1238 | 397.5966
2502.0667 | 513.5173 | 537.1093 | 397.7187
2503.0667 | 511.2878 | 538.0131 | 397.9057
2504.0667 | 512.7346 | 537.0038 | 398.177
2505.0667 | 512.0053 | 537.0423 | 398.2898
2506.0667 | 509.6175 | 536.6734 | 398.5828
2507.0667 | 510.6931 | 535.1942 | 398.7778
2508.0667 | 510.5882 | 534.8339 | 399.0127
2509.0667 | 509.6329 | 535.6543 | 399.3653
2510.0667 | 507.6833 | 533.9279 | 399.7794
2511.0823 | 507.2606 | 531.3719 | 400.0296
2512.0667 | 509.0004 | 530.9766 | 400.0832
2513.0667 | 511.6548 | 530.2261 | 399.9355
2514.0667 | 515.0794 | 528.1527 | 399.6606
2515.0667 | 516.6799 | 529.5087 | 399.6182
2516.0667 | 516.7302 | 527.5914 | 399.6477
2517.0667 | 518.491 | 529.9266 | 399.8247
2518.0667 | 519.1934 | 528.1282 | 399.9917
2519.0823 | 518.0549 | 530.3426 | 400.1948
2520.0667 | 518.085 | 528.6327 | 400.2514
2521.0667 | 519.5437 | 527.2149 | 400.1494
2522.0667 | 522.13 | 527.6922 | 400.1875
2523.0667 | 524.2049 | 532.3061 | 400.3636
2524.0667 | 524.4308 | 531.0996 | 400.4891
2525.0667 | 525.1043 | 527.1763 | 400.5117
2526.0667 | 524.2316 | 525.6008 | 400.3424
2527.0667 | 523.4309 | 523.9118 | 400.0145
2528.0667 | 523.822 | 521.5073 | 399.5542
2529.0667 | 530.4993 | 520.4434 | 399.1083
2530.0667 | 532.5508 | 519.7441 | 398.8971
2531.0667 | 536.1008 | 519.9509 | 398.7555
2532.0667 | 536.6926 | 521.0369 | 398.5502
2533.0667 | 539.6413 | 532.4168 | 398.3551
2534.0667 | 538.8934 | 530.7096 | 398.2742
2535.0667 | 540.3188 | 529.7301 | 398.5231
2536.0823 | 538.5646 | 530.456 | 398.6761
2537.0667 | 539.0951 | 533.2502 | 398.7642
2538.0667 | 539.9652 | 534.6386 | 398.8446
2539.0667 | 542.9885 | 534.3663 | 398.8676
2540.0667 | 546.2499 | 531.8163 | 398.9016
2541.0667 | 550.5278 | 532.7396 | 399.0196
2542.0667 | 551.6601 | 536.086 | 399.3248
2543.0667 | 552.5702 | 538.9034 | 399.4762
2544.0667 | 553.0673 | 534.7077 | 399.6789
2545.0667 | 552.4723 | 534.9522 | 399.7684
2546.0667 | 553.0485 | 535.9451 | 399.9813
2547.0667 | 554.3704 | 533.3695 | 400.333
2548.0823 | 553.7189 | 532.4699 | 400.8021
2549.0667 | 551.5308 | 530.5506 | 401.291
2550.0667 | 550.5551 | 531.7113 | 401.957
2551.0667 | 549.558 | 531.45 | 402.4891
2552.0667 | 546.6758 | 529.7879 | 402.8754
2553.0667 | 545.082 | 529.0922 | 403.2154
2554.0667 | 543.9961 | 528.7619 | 403.4425
2555.0667 | 546.1403 | 529.0692 | 403.6382
2556.0667 | 549.0307 | 528.8781 | 404.0317
2557.0667 | 550.3901 | 529.7738 | 404.5118
2558.0667 | 555.451 | 528.9083 | 404.9664
2559.0667 | 555.793 | 527.3776 | 405.3561
2560.0667 | 553.2674 | 527.3643 | 405.7129
2561.0667 | 554.2854 | 525.8948 | 406.2427
2562.0667 | 553.0284 | 524.6962 | 406.7591
2563.0667 | 550.6029 | 525.5729 | 407.2345
2564.0667 | 552.2133 | 525.8238 | 407.5483
2565.0667 | 552.631 | 526.127 | 407.6479
2566.0823 | 552.3362 | 526.537 | 407.6774
2567.0667 | 551.3397 | 525.4233 | 407.7515
2568.0667 | 553.976 | 526.3901 | 407.9597
2569.0667 | 553.2853 | 530.7532 | 408.3402
2570.0667 | 549.2297 | 532.5151 | 408.8056
2571.0667 | 545.3411 | 532.1433 | 409.1799
2572.0667 | 545.3167 | 529.7528 | 409.3488
2573.0667 | 545.4603 | 530.1376 | 409.3871
2574.0667 | 545.6273 | 529.9504 | 409.4633
2575.0667 | 545.7239 | 531.0941 | 409.6631
2576.0667 | 545.6452 | 533.2964 | 410.0503
2577.0667 | 546.1555 | 533.802 | 410.2971
2578.0667 | 545.5542 | 531.8727 | 410.5124
2579.0667 | 544.7186 | 529.9552 | 410.6354
2580.0667 | 544.4076 | 528.7439 | 410.72
2581.0667 | 545.1422 | 529.9511 | 410.6722
2582.0667 | 549.33 | 531.6746 | 410.7039
2583.0667 | 551.7519 | 534.9182 | 410.8929
2584.0667 | 553.2006 | 531.8458 | 411.0672
2585.0667 | 553.687 | 531.0631 | 411.1505
2586.0667 | 553.4676 | 531.5731 | 411.0307
2587.0667 | 554.8651 | 530.4111 | 410.897
2588.0667 | 557.8879 | 531.8232 | 410.8372
2589.0667 | 561.3057 | 532.2302 | 410.7977
2590.0667 | 562.5622 | 532.0718 | 410.8306
2591.0667 | 563.5809 | 531.9697 | 411.0481
2592.0667 | 565.0323 | 530.0606 | 411.2757
2593.0667 | 565.4016 | 529.6464 | 411.3366
2594.0667 | 565.1236 | 530.4548 | 411.4674
2595.0667 | 566.6737 | 528.0509 | 411.4118
2596.0823 | 564.1251 | 526.2629 | 411.2907
2597.0667 | 561.4231 | 526.5252 | 411.1688
2598.0667 | 563.0862 | 528.5003 | 411.1
2599.0667 | 565.0193 | 530.0391 | 410.9859
2600.0667 | 565.9905 | 528.7436 | 410.8072
2601.0667 | 565.9844 | 527.7176 | 410.7288
2602.0667 | 565.9449 | 525.6649 | 410.8699
2603.0667 | 569.1096 | 527.8699 | 411.25
2604.0667 | 570.409 | 531.5648 | 411.6797
2605.0667 | 568.6248 | 530.7208 | 412.0661
2606.0667 | 570.1196 | 531.2155 | 412.3527
2607.0667 | 568.8435 | 533.9251 | 412.5024
2608.0667 | 567.4702 | 533.4015 | 412.5057
2609.0667 | 572.8 | 533.5113 | 412.4102
2610.0667 | 573.3633 | 532.4296 | 412.2588
2611.0667 | 574.2075 | 530.6103 | 412.1639
2612.0667 | 573.8985 | 528.7956 | 412.2381
2613.0667 | 573.168 | 527.3229 | 412.4239
2614.0667 | 580.1306 | 532.5567 | 412.7729
2615.0667 | 579.6881 | 533.2716 | 412.9187
2616.0667 | 580.9944 | 534.8052 | 412.9838
2617.0667 | 582.7681 | 534.6287 | 412.9731
2618.0667 | 589.6231 | 535.4497 | 413.0151
2619.0667 | 593.6009 | 534.1997 | 413.1519
2620.0667 | 594.4257 | 531.1452 | 413.2332
2621.0667 | 592.2382 | 528.2868 | 413.1914
2622.0667 | 588.4534 | 526.3984 | 413.3973
2623.0667 | 592.3422 | 532.4147 | 413.6925
2624.0667 | 593.9197 | 533.4633 | 413.9859
2625.0667 | 594.4665 | 533.617 | 414.0721
2626.0823 | 599.2679 | 531.9417 | 414.1313
2627.0667 | 597.4013 | 532.7984 | 414.3546
2628.0667 | 594.0083 | 532.3241 | 414.6797
2629.0667 | 592.9443 | 532.5235 | 415.0184
2630.0667 | 594.8328 | 532.1597 | 415.2081
2631.0667 | 597.2566 | 533.6337 | 415.3725
2632.0667 | 597.4804 | 533.1084 | 415.5086
2633.0667 | 599.4502 | 532.1596 | 415.7052
2634.0667 | 601.7143 | 531.059 | 415.8524
2635.0667 | 606.0607 | 537.933 | 416.0551
2636.0667 | 607.2368 | 539.7106 | 416.3411
2637.0667 | 607.2795 | 539.8118 | 416.9288
2638.0667 | 604.7829 | 539.3406 | 417.6326
2639.0667 | 607.3824 | 542.1901 | 418.9753
2640.0667 | 614.0757 | 548.2506 | 419.9824
2641.0667 | 611.9145 | 550.3489 | 420.5869
2642.0667 | 606.4161 | 554.3247 | 421.2003
2643.0667 | 610.4423 | 554.9045 | 421.6039
2644.0667 | 604.7818 | 551.6959 | 421.6916
2645.0667 | 596.6396 | 549.0694 | 421.9933
2646.0667 | 595.0317 | 546.3824 | 422.4672
2647.0667 | 606.4558 | 550.571 | 423.0422
2648.0667 | 610.6184 | 547.9784 | 423.4766
2649.0667 | 605.4015 | 545.8658 | 423.7738
2650.0667 | 619.6657 | 542.9299 | 423.8776
2651.0667 | 617.3077 | 539.3735 | 424.0446
2652.0667 | 615.4427 | 538.0179 | 424.1657
2653.0667 | 614.1321 | 539.7509 | 424.7562
2654.0667 | 614.7271 | 539.1703 | 425.1025
2655.0667 | 614.2298 | 537.9639 | 425.2791
2656.0823 | 618.8051 | 537.2362 | 425.4886
2657.0667 | 617.8714 | 540.3234 | 425.7423
2658.0667 | 611.8172 | 539.3111 | 425.7284
2659.0667 | 608.6423 | 538.1589 | 425.8523
2660.0667 | 613.9524 | 538.0378 | 425.8646
2661.0667 | 613.8459 | 537.9841 | 425.8611
2662.0667 | 612.3651 | 540.0192 | 425.7848
2663.0667 | 608.9123 | 541.8742 | 425.8519
2664.0667 | 622.8818 | 552.7071 | 426.0333
2665.0667 | 626.7244 | 551.3675 | 426.2297
2666.0667 | 621.2793 | 549.3272 | 426.2034
2667.0667 | 619.5927 | 550.7876 | 426.2066
2668.0667 | 620.1709 | 550.2772 | 426.2482
2669.0667 | 621.1775 | 546.7338 | 426.4375
2670.0823 | 618.3348 | 543.3293 | 426.7866
2671.0667 | 628.8207 | 541.7778 | 427.0108
2672.0667 | 628.0066 | 540.3405 | 426.9172
2673.0667 | 632.4163 | 536.0156 | 426.6788
2674.0667 | 629.4814 | 534.8808 | 426.6187
2675.0667 | 631.7423 | 532.4819 | 426.5169
2676.0667 | 650.4989 | 532.3066 | 426.7458
2677.0667 | 648.1691 | 532.02 | 427.0863
2678.0667 | 644.8879 | 530.6894 | 427.2547
2679.0667 | 639.8489 | 529.4354 | 427.1801
2680.0667 | 638.206 | 528.2962 | 427.0012
2681.0667 | 637.9135 | 529.0047 | 426.8793
2682.0667 | 631.3069 | 527.0122 | 426.7904
2683.0667 | 644.0454 | 526.1222 | 426.6722
2684.0667 | 653.4504 | 528.9359 | 426.9195
2685.0667 | 653.6927 | 532.9692 | 427.3818
2686.0667 | 649.2541 | 534.6622 | 427.7555
2687.0667 | 641.0718 | 533.6548 | 428.0239
2688.0667 | 649.0574 | 534.1501 | 428.2779
2689.0667 | 651.4771 | 534.5266 | 428.5523
2690.0667 | 645.0573 | 533.5383 | 429.0483
2691.0667 | 639.1093 | 533.9772 | 429.4691
2692.0667 | 655.8754 | 534.9101 | 429.8668
2693.0667 | 663.8012 | 537.2067 | 430.2485
2694.0667 | 660.1503 | 538.1389 | 430.5529
2695.0667 | 661.7826 | 538.8998 | 431.0112
2696.0667 | 662.398 | 538.5558 | 431.4985
2697.0667 | 667.7622 | 536.6381 | 432.0578
2698.0667 | 671.7102 | 538.695 | 432.704
2699.0667 | 670.1968 | 538.7276 | 433.2629
2700.0667 | 664.3255 | 538.073 | 433.6179
2701.0667 | 669.1206 | 537.3642 | 433.9024
2702.0667 | 664.7289 | 534.9367 | 434.1225
2703.0667 | 669.0445 | 535.1039 | 434.3485
2704.0667 | 672.3738 | 534.5508 | 434.4599
2705.0667 | 676.9849 | 535.8695 | 434.6516
2706.0667 | 673.3894 | 535.2327 | 434.7902
2707.0667 | 666.436 | 533.5186 | 434.9192
2708.0667 | 658.5418 | 533.6895 | 435.3924
2709.0667 | 664.0886 | 535.9398 | 435.7299
2710.0667 | 660.7633 | 535.3642 | 435.9748
2711.0667 | 655.8894 | 536.2433 | 436.0285
2712.0667 | 654.8751 | 535.3202 | 436.0856
2713.0667 | 650.7673 | 537.1178 | 436.4918
2714.0667 | 651.5145 | 537.2494 | 437.0065
2715.0667 | 648.315 | 537.7291 | 437.4075
2716.0667 | 651.5914 | 539.1973 | 437.7979
2717.0667 | 645.8572 | 539.6618 | 438.0033
2718.0667 | 639.9511 | 541.4739 | 438.3142
2719.0667 | 639.5128 | 539.9012 | 438.7538
2720.0667 | 646.6674 | 539.665 | 439.0044
2721.0667 | 643.4601 | 540.0348 | 439.1149
2722.0667 | 639.1349 | 538.0323 | 439.0425
2723.0667 | 644.5717 | 538.0514 | 438.9676
2724.0667 | 648.9328 | 539.7353 | 438.9969
2725.0667 | 651.2294 | 539.3935 | 439.2756
2726.0667 | 658.0658 | 539.964 | 440.1614
2727.0667 | 658.9664 | 541.6176 | 440.7524
2728.0823 | 652.8038 | 538.6613 | 441.0302
2729.0667 | 657.8216 | 540.3718 | 440.8881
2730.0667 | 652.4 | 540.7007 | 441.0925
2731.0667 | 654.1797 | 539.7802 | 441.0868
2732.0667 | 666.0497 | 537.2727 | 441.1888
2733.0667 | 669.2006 | 535.598 | 441.5175
2734.0667 | 681.7094 | 534.7309 | 441.6411
2735.0667 | 686.104 | 535.8072 | 441.7923
2736.0667 | 677.5885 | 538.9461 | 441.848
2737.0667 | 667.818 | 539.2975 | 441.7739
2738.0667 | 672.7478 | 536.004 | 441.555
2739.0667 | 664.5694 | 536.5399 | 441.3604
2740.0667 | 666.6569 | 540.2617 | 441.3843
2741.0667 | 660.1475 | 539.2803 | 441.4348
2742.0667 | 660.6434 | 539.4541 | 441.5639
2743.0667 | 652.1565 | 538.7034 | 441.683
2744.0667 | 651.7383 | 542.6037 | 442.0843
2745.0667 | 648.1854 | 544.0516 | 442.3545
2746.0667 | 644.6176 | 543.5981 | 442.3015
2747.0667 | 640.724 | 547.165 | 442.4944
2748.0667 | 639.0046 | 547.2844 | 442.4927
2749.0667 | 638.1859 | 544.3245 | 442.4926
2750.0667 | 633.5024 | 544.7456 | 442.4371
2751.0667 | 631.9227 | 543.9381 | 442.3098
2752.0667 | 631.4566 | 541.4464 | 442.2832
2753.0667 | 636.2778 | 542.9887 | 442.5593
2754.0667 | 633.9677 | 544.0542 | 442.7287
2755.0667 | 627.6109 | 543.0209 | 442.912
2756.0667 | 630.5771 | 545.8614 | 443.115
2757.0667 | 633.7832 | 545.9509 | 443.148
2758.0667 | 633.9278 | 544.5507 | 443.2361
2759.0667 | 636.9699 | 544.2376 | 443.3461
2760.0667 | 639.2592 | 545.379 | 443.3812
2761.0667 | 641.0727 | 547.5178 | 443.394
2762.0667 | 637.2042 | 550.4041 | 443.544
2763.0667 | 633.643 | 551.1242 | 443.5837
2764.0667 | 635.2402 | 550.0299 | 443.4915
2765.0667 | 637.1503 | 551.2247 | 443.4049
2766.0667 | 647.3884 | 552.5478 | 443.4142
2767.0667 | 660.7123 | 552.7295 | 443.7298
2768.0667 | 659.4789 | 551.857 | 444.189
2769.0667 | 649.7145 | 551.2685 | 444.481
2770.0667 | 642.747 | 551.6631 | 444.5305
2771.0667 | 642.8524 | 552.9153 | 444.5396
2772.0667 | 652.9168 | 551.0491 | 444.5399
2773.0667 | 662.0352 | 549.0636 | 445.0124
2774.0667 | 666.3604 | 546.8336 | 445.5078
2775.0667 | 661.8386 | 544.6406 | 446.0901
2776.0667 | 665.2653 | 545.8198 | 446.5649
2777.0667 | 655.4932 | 544.8068 | 446.8987
2778.0667 | 645.4155 | 545.806 | 447.8681
2779.0667 | 637.2831 | 544.6146 | 448.8641
2780.0667 | 634.2284 | 543.1964 | 449.5741
2781.0667 | 641.9788 | 544.7221 | 450.1156
2782.0667 | 643.7362 | 544.9931 | 450.3621
2783.0667 | 650.2923 | 545.7788 | 450.9945
2784.0667 | 653.2809 | 546.4731 | 451.8447
2785.0667 | 654.2607 | 548.7345 | 453.1809
2786.0667 | 649.4829 | 548.1847 | 454.0095
2787.0667 | 647.2603 | 548.375 | 454.442
2788.0667 | 644.2178 | 547.345 | 454.9166
2789.0667 | 639.6238 | 545.8443 | 455.3758
2790.0667 | 631.9939 | 544.0281 | 455.776
2791.0667 | 639.0897 | 545.4495 | 456.2786
2792.0667 | 642.9077 | 550.4819 | 456.8404
2793.0667 | 644.1246 | 554.2516 | 457.547
2794.0667 | 644.0256 | 565.121 | 458.7854
2795.0667 | 638.168 | 563.8144 | 460.0999
2796.0667 | 636.4525 | 562.7974 | 461.3538
2797.0667 | 634.042 | 563.7405 | 462.9307
2798.0667 | 632.5501 | 560.829 | 464.2279
2799.0667 | 626.1023 | 560.4411 | 464.9251
2800.0667 | 624.416 | 557.3807 | 465.2188
2801.0667 | 628.2659 | 554.3484 | 466.0751
2802.0667 | 626.229 | 567.2322 | 467.7951
2803.0667 | 630.5373 | 570.6182 | 469.4178
2804.0667 | 630.7578 | 566.5607 | 471.0205
2805.0667 | 629.6637 | 560.0876 | 472.0059
2806.0667 | 629.8561 | 560.199 | 473.4243
2807.0667 | 623.5557 | 565.3556 | 474.6739
2808.0667 | 626.5413 | 562.3531 | 475.9172
2809.0667 | 628.0739 | 561.1445 | 476.7175
2810.0667 | 631.0322 | 559.3776 | 478.2953
2811.0667 | 631.672 | 557.3 | 479.6396
2812.0667 | 635.9215 | 555.7304 | 480.6036
2813.0667 | 630.5118 | 551.4248 | 481.2767
2814.0667 | 636.5747 | 549.3505 | 481.6201
2815.0667 | 641.5463 | 547.5412 | 482.0405
2816.0667 | 640.0149 | 553.8729 | 482.4161
2817.0667 | 635.5321 | 561.2019 | 483.3405
2818.0667 | 639.7078 | 560.3731 | 484.4259
2819.0667 | 640.2595 | 558.8423 | 485.9075
2820.0667 | 635.0856 | 557.3046 | 486.9875
2821.0667 | 638.0493 | 555.8043 | 487.6118
2822.0667 | 635.6309 | 554.1414 | 488.2753
2823.0667 | 631.9774 | 553.3905 | 488.5803
2824.0667 | 632.5361 | 553.0871 | 488.4366
2825.0667 | 638.5261 | 554.7168 | 488.9325
2826.0667 | 636.1177 | 555.6774 | 489.9805
2827.0667 | 633.2182 | 553.9091 | 490.6387
2828.0667 | 634.5104 | 550.9431 | 490.8726
2829.0667 | 629.6488 | 546.9473 | 491.235
2830.0667 | 622.5238 | 542.2672 | 491.4571
2831.0667 | 620.3274 | 542.6345 | 491.9106
2832.0667 | 615.8574 | 551.9112 | 492.387
2833.0667 | 619.1335 | 550.4042 | 492.7204
2834.0667 | 624.2645 | 555.1733 | 493.2119
2835.0667 | 625.6264 | 552.2181 | 493.2116
2836.0667 | 634.9991 | 551.2774 | 493.2823
2837.0667 | 629.0034 | 552.5804 | 493.5077
2838.0667 | 617.6378 | 554.0941 | 493.4881
2839.0667 | 627.3392 | 564.4004 | 493.7221
2840.0667 | 633.0252 | 564.9333 | 493.7562
2841.0667 | 629.4205 | 563.273 | 493.8275
2842.0667 | 617.8511 | 557.5738 | 493.9653
2843.0667 | 609.2413 | 553.0337 | 493.8736
2844.0667 | 610.4825 | 552.321 | 493.914
2845.0667 | 607.0205 | 552.1946 | 494.2944
2846.0667 | 602.9653 | 558.1041 | 494.3426
2847.0667 | 601.5419 | 556.1656 | 494.9591
2848.0823 | 595.3867 | 563.6274 | 495.9064
2849.0667 | 593.333 | 568.8111 | 496.6699
2850.0667 | 593.1938 | 569.9953 | 497.3896
2851.0667 | 600.4335 | 568.1161 | 497.8202
2852.0667 | 598.7494 | 567.5411 | 498.5379
2853.0667 | 595.9429 | 565.6961 | 498.9298
2854.0667 | 593.1224 | 564.1147 | 499.0313
2855.0667 | 588.3324 | 567.346 | 499.5438
2856.0667 | 586.0456 | 574.3521 | 499.6277
2857.0667 | 592.9056 | 573.3928 | 499.6655
2858.0667 | 593.4679 | 576.695 | 500.2668
2859.0667 | 595.1652 | 574.5811 | 500.4783
2860.0667 | 595.7547 | 574.7756 | 500.3535
2861.0667 | 593.8074 | 577.0431 | 500.2782
2862.0667 | 591.6961 | 582.1736 | 500.4782
2863.0667 | 597.2638 | 575.0143 | 500.5154
2864.0667 | 601.6179 | 570.1613 | 500.0621
2865.0667 | 594.9138 | 566.5672 | 499.5593
2866.0667 | 591.8079 | 565.6155 | 500.0314
2867.0667 | 586.4654 | 562.4361 | 500.3865
2868.0667 | 583.8903 | 561.0737 | 500.5251
2869.0667 | 586.9677 | 558.7972 | 500.4349
2870.0667 | 591.1674 | 555.4532 | 500.2197
2871.0667 | 590.8952 | 560.0435 | 499.9239
2872.0667 | 588.5579 | 557.9198 | 500.0692
2873.0667 | 586.1141 | 564.9746 | 500.3686
2874.0667 | 584.5682 | 565.3248 | 500.3824
2875.0667 | 583.7236 | 573.9053 | 500.3287
2876.0667 | 583.1489 | 570.4094 | 500.4182
2877.0667 | 587.567 | 574.8605 | 500.6282
2878.0667 | 593.94 | 576.9358 | 501.1882
2879.0667 | 588.9283 | 575.5772 | 501.602
2880.0667 | 593.4017 | 572.1488 | 502.4293
2881.0667 | 592.3339 | 570.5014 | 503.6331
2882.0667 | 598.6578 | 569.4657 | 504.653
2883.0667 | 594.4568 | 569.8876 | 505.1855
2884.0667 | 593.2502 | 571.0789 | 505.2398
2885.0667 | 591.1269 | 572.6151 | 505.3819
2886.0667 | 587.6206 | 577.6591 | 505.6024
2887.0667 | 589.5267 | 576.3509 | 506.0643
2888.0667 | 588.7519 | 579.367 | 506.9185
2889.0667 | 595.3426 | 575.9439 | 507.2384
2890.0667 | 596.4915 | 581.3293 | 507.1053
2891.0667 | 593.2616 | 577.231 | 506.779
2892.0667 | 590.917 | 580.3546 | 506.6797
2893.0667 | 594.3782 | 576.8542 | 506.8571
2894.0667 | 596.7022 | 575.8334 | 506.553
2895.0667 | 601.0693 | 573.4326 | 506.022
2896.0667 | 604.5555 | 577.8459 | 505.3435
2897.0667 | 604.9794 | 576.0435 | 504.7994
2898.0667 | 601.647 | 577.4535 | 504.7786
2899.0667 | 596.6184 | 574.2611 | 505.3709
2900.0667 | 595.1783 | 572.651 | 506.0336
2901.0667 | 597.0573 | 570.9327 | 506.5042
2902.0667 | 593.7635 | 572.14 | 506.7825
2903.0667 | 589.723 | 568.8185 | 506.9624
2904.0667 | 593.8737 | 566.3751 | 507.0551
2905.0667 | 588.0573 | 571.0108 | 507.3168
2906.0667 | 585.2657 | 571.9013 | 507.3553
2907.0667 | 579.5761 | 581.4067 | 507.4563
2908.0667 | 583.997 | 580.6152 | 507.1386
2909.0667 | 578.0115 | 576.0424 | 506.6572
2910.0667 | 582.8451 | 571.0479 | 506.1403
2911.0667 | 590.661 | 566.7407 | 506.0323
2912.0667 | 586.2861 | 571.047 | 506.365
2913.0667 | 580.9996 | 570.3012 | 506.7084
2914.0667 | 579.5694 | 571.4976 | 506.8155
2915.0667 | 578.1565 | 569.0575 | 506.7004
2916.0667 | 574.0406 | 565.3093 | 506.5238
2917.0667 | 568.7431 | 572.876 | 506.7787
2918.0667 | 563.8042 | 570.8095 | 507.0873
2919.0667 | 559.5936 | 571.3146 | 506.8792
2920.0667 | 559.5987 | 568.8192 | 506.1515
2921.0667 | 564.9957 | 563.7093 | 505.4488
2922.0667 | 561.1278 | 559.8428 | 504.7038
2923.0667 | 571.5861 | 558.0325 | 504.0408
2924.0667 | 566.7039 | 555.32 | 503.397
2925.0667 | 561.5983 | 553.3825 | 503.0766
2926.0667 | 556.6933 | 549.5483 | 502.4766
2927.0667 | 554.1314 | 548.2061 | 502.0628
2928.0667 | 550.9567 | 546.321 | 502.196
2929.0667 | 560.0232 | 545.3691 | 502.4458
2930.0667 | 562.5688 | 546.6357 | 503.2827
2931.0667 | 564.7869 | 545.7893 | 504.0602
2932.0667 | 561.0195 | 543.9792 | 504.5175
2933.0667 | 558.3341 | 542.9714 | 505.1548
2934.0667 | 556.1483 | 542.1354 | 506.1311
2935.0667 | 554.4357 | 542.4191 | 507.0506
2936.0667 | 552.6401 | 540.8499 | 507.8399
2937.0667 | 550.2691 | 539.6277 | 509.119
2938.0667 | 547.5045 | 539.8397 | 510.175
2939.0667 | 546.428 | 540.4313 | 510.8086
2940.0667 | 545.7826 | 539.8545 | 511.0844
2941.0667 | 543.3413 | 539.0215 | 511.1904
2942.0667 | 540.3341 | 539.072 | 511.2374
2943.0667 | 537.0025 | 538.0487 | 511.3897
2944.0667 | 532.9432 | 534.9389 | 511.4561
2945.0667 | 529.4417 | 533.6762 | 511.1643
2946.0667 | 545.5514 | 535.256 | 510.8508
2947.0667 | 550.9819 | 537.6993 | 510.5856
2948.0667 | 551.8287 | 540.5886 | 510.7214
2949.0667 | 560.3074 | 542.0475 | 511.2093
2950.0667 | 569.332 | 549.4171 | 511.5686
2951.0667 | 566.5554 | 555.1615 | 511.7583
2952.0667 | 561.1322 | 554.8868 | 512.4704
2953.0667 | 573.5028 | 554.9131 | 513.5612
2954.0667 | 576.1575 | 552.9734 | 514.4172
2955.0667 | 573.8775 | 550.9138 | 514.9743
2956.0667 | 570.8498 | 549.0923 | 515.302
2957.0667 | 565.9694 | 549.4542 | 515.5811
2958.0667 | 571.3559 | 551.8375 | 515.8899
2959.0667 | 567.1435 | 552.1282 | 516.1972
2960.0667 | 563.5754 | 554.4622 | 516.6204
2961.0667 | 560.8283 | 558.3227 | 516.9937
2962.0667 | 560.6188 | 558.9215 | 517.2891
2963.0667 | 557.5155 | 557.0114 | 517.1798
2964.0667 | 555.1172 | 560.6754 | 516.874
2965.0667 | 553.391 | 558.531 | 516.3518
2966.0667 | 554.741 | 558.0843 | 515.8896
2967.0667 | 554.7292 | 560.8757 | 515.8328
2968.0667 | 555.822 | 558.6958 | 516.1027
2969.0667 | 553.3978 | 558.7318 | 516.7142
2970.0667 | 549.3422 | 568.9784 | 517.1398
2971.0667 | 546.1946 | 570.9713 | 517.4014
2972.0667 | 544.4241 | 570.3403 | 517.805
2973.0667 | 544.4022 | 569.6575 | 517.8575
2974.0667 | 547.5667 | 571.9109 | 517.829
2975.0667 | 547.9755 | 572.3748 | 517.7672
2976.0667 | 545.4862 | 569.8021 | 517.9238
2977.0667 | 543.8964 | 566.8188 | 518.5768
2978.0667 | 546.7253 | 568.5935 | 519.0651
2979.0667 | 542.6319 | 569.8267 | 519.4717
2980.0667 | 544.6542 | 568.6469 | 519.5247
2981.0667 | 546.387 | 564.5205 | 519.4022
2982.0667 | 545.4594 | 564.818 | 519.7204
2983.0667 | 541.1136 | 561.2281 | 520.0509
2984.0667 | 540.6099 | 559.8934 | 520.0827
2985.0667 | 540.3302 | 558.683 | 520.3463
2986.0667 | 537.7055 | 557.645 | 521.1385
2987.0667 | 534.9699 | 557.8598 | 521.982
2988.0667 | 535.1314 | 558.5018 | 522.4016
2989.0667 | 536.6768 | 557.2083 | 522.4715
2990.0667 | 536.2275 | 561.7635 | 522.3375
2991.0667 | 535.853 | 564.8241 | 522.3394
2992.0667 | 538.6147 | 566.8422 | 522.5998
2993.0667 | 542.8929 | 568.2418 | 522.9092
2994.0667 | 543.4843 | 570.0515 | 523.3773
2995.0667 | 543.7659 | 584.9378 | 523.6512
2996.0667 | 544.9469 | 582.2959 | 523.5064
2997.0667 | 544.8484 | 573.6978 | 523.1998
2998.0667 | 544.1743 | 575.0845 | 522.7921
2999.0667 | 541.6809 | 569.786 | 522.2416
3000.0667 | 538.6294 | 563.4429 | 521.7534
3001.0667 | 536.3915 | 557.8425 | 521.3678
3002.0667 | 535.7369 | 559.7295 | 521.2944
3003.0667 | 534.9273 | 558.569 | 521.5842
3004.0667 | 530.7683 | 561.4127 | 522.1378
3005.0667 | 537.5042 | 559.1536 | 522.5617
3006.0667 | 536.6867 | 558.6354 | 522.9998
3007.0667 | 536.6932 | 557.3104 | 523.4837
3008.0667 | 536.3245 | 560.1172 | 523.5412
3009.0667 | 536.8739 | 562.5711 | 523.304
3010.0667 | 537.3315 | 560.3608 | 523.1573
3011.0667 | 534.3449 | 558.055 | 523.2522
3012.0667 | 533.6476 | 556.6554 | 523.3986
3013.0667 | 533.2855 | 556.0177 | 523.3683
3014.0667 | 534.0177 | 557.2101 | 523.1485
3015.0667 | 533.4601 | 558.324 | 522.8758
3016.0667 | 533.4073 | 554.0079 | 522.6873
3017.0667 | 535.3574 | 551.4485 | 522.6741
3018.0667 | 535.9931 | 551.9567 | 522.9729
3019.0667 | 535.3394 | 549.6745 | 523.0043
3020.0667 | 534.5884 | 552.3029 | 522.8951
3021.0667 | 532.5628 | 551.0624 | 522.8316
3022.0667 | 530.8495 | 550.5099 | 522.9176
3023.0667 | 529.3649 | 550.2707 | 522.7932
3024.0667 | 531.1374 | 549.9458 | 522.4646
3025.0667 | 537.5166 | 553.332 | 521.7883
3026.0667 | 534.9075 | 552.3297 | 520.9614
3027.0667 | 532.7569 | 550.0407 | 520.1232
3028.0667 | 530.7766 | 548.2855 | 519.1694
3029.0667 | 528.8787 | 549.7992 | 517.9655
3030.0667 | 527.6826 | 548.0291 | 516.4182
3031.0667 | 527.5878 | 546.6389 | 515.0805
3032.0667 | 526.3183 | 543.9476 | 514.2509
3033.0667 | 524.19 | 541.7129 | 513.5438
3034.0667 | 521.7791 | 540.6993 | 512.9943
3035.0667 | 518.5971 | 539.7294 | 512.497
3036.0667 | 516.3924 | 539.2369 | 512.2229
3037.0667 | 515.3541 | 541.3595 | 512.1226
3038.0667 | 513.8959 | 541.6162 | 512.1748
3039.0667 | 512.5895 | 540.0136 | 512.3146
3040.0667 | 511.5716 | 540.6982 | 512.5399
3041.0667 | 512.5952 | 539.7669 | 512.5944
3042.0667 | 513.3024 | 541.3254 | 512.6295
3043.0667 | 512.0073 | 545.004 | 512.4562
3044.0667 | 510.7233 | 543.0173 | 512.2534
3045.0667 | 510.6792 | 543.8749 | 512.1947
3046.0667 | 511.6345 | 546.9944 | 511.9739
3047.0667 | 519.8302 | 550.2017 | 511.8313
3048.0667 | 523.2812 | 559.2282 | 511.6522
3049.0667 | 525.3959 | 566.6482 | 511.378
3050.0667 | 524.6351 | 568.2162 | 510.877
3051.0667 | 530.9088 | 565.0992 | 510.409
3052.0667 | 529.4721 | 562.8302 | 509.4743
3053.0667 | 526.77 | 562.1835 | 509.0706
3054.0667 | 525.0015 | 559.8773 | 507.842
3055.0667 | 524.4659 | 554.4971 | 507.637
3056.0667 | 526.4457 | 550.0414 | 506.1396
3057.0667 | 525.1744 | 546.6894 | 505.8674
3058.0667 | 525.7228 | 549.4334 | 505.0164
3059.0667 | 525.3028 | 548.6499 | 503.4371
3060.0667 | 527.3422 | 546.7787 | 503.3636
3061.0667 | 527.9213 | 546.5912 | 502.0153
3062.0667 | 526.0121 | 545.0461 | 501.7813
3063.0667 | 523.1517 | 547.3238 | 501.7141
3064.0667 | 520.5281 | 553.525 | 501.4609
3065.0667 | 517.8802 | 560.6154 | 501.0751
3066.0823 | 515.5194 | 557.9061 | 500.7874
3067.0823 | 514.595 | 551.9366 | 501.0455
3068.0667 | 515.3744 | 558.0005 | 500.7344
3069.0667 | 520.042 | 558.2641 | 500.3496
3070.0667 | 518.6811 | 556.0961 | 500.8755
3071.0667 | 518.2862 | 553.5061 | 501.092
3072.0667 | 520.5602 | 550.9639 | 501.6495
3073.0667 | 520.7287 | 548.0438 | 501.5372
3074.0667 | 519.7679 | 544.5232 | 501.5125
3075.0667 | 520.4542 | 541.2936 | 501.1218
3076.0667 | 519.8174 | 540.7668 | 501.6019
3077.0667 | 519.2553 | 544.7602 | 501.6374
3078.0667 | 517.8341 | 543.5536 | 502.3379
3079.0667 | 525.7167 | 543.4008 | 501.6911
3080.0667 | 526.8804 | 543.5025 | 502.7927
3081.0667 | 524.1042 | 540.8101 | 503.8386
3082.0667 | 522.2106 | 538.1302 | 504.0518
3083.0667 | 521.2964 | 537.7594 | 504.8586
3084.0667 | 519.3392 | 537.7019 | 505.1892
3085.0667 | 518.8731 | 536.8881 | 505.281
3086.0667 | 517.2933 | 534.7007 | 505.7463
3087.0667 | 518.244 | 533.6736 | 505.9695
3088.0667 | 521.8268 | 533.2289 | 506.1076
3089.0667 | 521.2436 | 540.2615 | 506.1414
3090.0667 | 517.7384 | 542.3849 | 506.8306
3091.0667 | 515.7025 | 541.6145 | 507.4705
3092.0667 | 514.1004 | 543.4621 | 507.4308
3093.0667 | 512.4544 | 544.4318 | 507.5671
3094.0667 | 510.6033 | 543.725 | 507.7641
3095.0667 | 512.6205 | 544.2401 | 507.5883
3096.0667 | 513.3339 | 546.0186 | 507.3721
3097.0667 | 513.1365 | 547.0351 | 506.8905
3098.0667 | 513.5554 | 544.2203 | 507.0478
3099.0667 | 513.5259 | 543.3195 | 506.5055
3100.0667 | 511.7377 | 541.5733 | 506.9907
3101.0667 | 509.2179 | 540.8875 | 506.6639
3102.0667 | 508.2499 | 540.5005 | 507.6231
3103.0667 | 506.9224 | 538.8801 | 508.4809
3104.0667 | 507.4304 | 536.1536 | 509.1734
3105.0667 | 506.7406 | 533.5086 | 509.7954
3106.0667 | 506.2664 | 532.8662 | 510.5115
3107.0667 | 506.0969 | 532.5639 | 511.2307
3108.0667 | 506.6937 | 531.8312 | 511.9911
3109.0667 | 506.2627 | 531.8743 | 512.4563
3110.0667 | 505.7225 | 534.1131 | 512.9432
3111.0667 | 506.7783 | 536.022 | 513.3891
3112.0667 | 505.7774 | 536.0504 | 513.7054
3113.0667 | 505.3663 | 536.1727 | 512.9723
3114.0667 | 507.8939 | 537.8061 | 513.5146
3115.0667 | 507.8546 | 539.5154 | 514.0411
3116.0667 | 506.3664 | 539.1074 | 513.911
3117.0667 | 506.6021 | 541.2766 | 514.6375
3118.0667 | 506.911 | 542.0786 | 514.1629
3119.0667 | 506.2365 | 543.1732 | 514.6313
3120.0667 | 506.4761 | 544.87 | 514.4798
3121.0667 | 506.3953 | 546.7616 | 514.3046
3122.0667 | 507.2967 | 555.8843 | 514.8665
3123.0667 | 508.1755 | 557.0866 | 515.6186
3124.0667 | 511.5556 | 559.5322 | 515.8287
3125.0667 | 515.4001 | 558.455 | 515.7088
3126.0667 | 518.5438 | 555.9615 | 516.0779
3127.0667 | 519.3299 | 553.7747 | 515.3056
3128.0667 | 520.4627 | 552.3958 | 514.8513
3129.0667 | 520.6036 | 552.6341 | 515.174
3130.0667 | 523.0043 | 552.2036 | 515.1677
3131.0667 | 523.535 | 551.1001 | 515.2091
3132.0667 | 523.2523 | 549.748 | 515.5782
3133.0667 | 522.6387 | 550.7408 | 516.2533
3134.0667 | 527.4286 | 554.0131 | 516.5464
3135.0667 | 529.928 | 553.4172 | 517.3023
3136.0667 | 530.823 | 553.7599 | 517.8758
3137.0667 | 530.5514 | 551.0923 | 518.2756
3138.0667 | 531.5933 | 549.6303 | 518.5699
3139.0667 | 531.0559 | 548.4163 | 518.7302
3140.0667 | 531.0704 | 550.097 | 518.914
3141.0667 | 531.1446 | 550.9793 | 519.446
3142.0667 | 529.8415 | 549.0173 | 520.0082
3143.0667 | 530.589 | 549.0007 | 520.6011
3144.0667 | 529.3942 | 548.8588 | 521.2117
3145.0667 | 527.672 | 548.6562 | 521.8237
3146.0667 | 527.5922 | 547.3456 | 522.3479
3147.0667 | 530.6661 | 547.2253 | 522.9178
3148.0667 | 532.6393 | 546.7175 | 523.5287
3149.0667 | 530.5835 | 544.8774 | 524.0107
3150.0667 | 529.3979 | 543.6415 | 524.401
3151.0667 | 529.0904 | 544.1542 | 524.794
3152.0667 | 531.0947 | 544.9948 | 525.2649
3153.0667 | 530.1906 | 546.5923 | 525.7577
3154.0667 | 532.1612 | 546.9355 | 526.3118
3155.0667 | 532.2071 | 546.8908 | 526.9291
3156.0667 | 535.133 | 547.5794 | 527.5358
3157.0667 | 536.7797 | 547.8614 | 528.1108
3158.0667 | 536.1037 | 548.5809 | 528.568
3159.0667 | 534.1181 | 546.5916 | 528.9621
3160.0667 | 533.372 | 544.8239 | 529.4618
3161.0667 | 531.9162 | 542.837 | 530.043
3162.0667 | 530.5606 | 541.72 | 530.5809
3163.0667 | 530.6304 | 541.7499 | 531.134
3164.0667 | 531.0762 | 541.8548 | 531.739
3165.0667 | 529.938 | 542.5851 | 532.3745
3166.0667 | 530.8171 | 543.619 | 533.1587
3167.0667 | 530.1493 | 544.8034 | 534.0392
3168.0667 | 528.7688 | 542.8908 | 534.8703
3169.0667 | 528.0816 | 542.742 | 535.6146
3170.0667 | 527.0339 | 541.6901 | 536.1795
3171.0667 | 525.5252 | 541.4118 | 536.6021
3172.0667 | 524.648 | 541.2335 | 536.9982
3173.0667 | 523.0697 | 540.5827 | 537.3646
3174.0667 | 523.3312 | 539.6835 | 537.6278
3175.0667 | 522.7656 | 538.9815 | 537.8872
3176.0667 | 521.6698 | 538.415 | 538.3013
3177.0667 | 520.4238 | 538.2506 | 538.7729
3178.0667 | 519.549 | 540.7801 | 539.0572
3179.0667 | 519.0576 | 540.9326 | 539.2396
3180.0667 | 520.3256 | 541.1403 | 539.6722
3181.0667 | 520.2199 | 540.5283 | 540.2151
3182.0667 | 519.2904 | 540.4145 | 540.8012
3183.0667 | 519.2398 | 541.6981 | 541.294
3184.0667 | 520.7441 | 542.7283 | 541.6591
3185.0667 | 519.4019 | 540.356 | 542.0597
3186.0667 | 518.234 | 538.6779 | 542.4193
3187.0667 | 516.9467 | 538.2732 | 542.7463
3188.0667 | 514.207 | 538.1025 | 543.0997
3189.0667 | 512.9791 | 537.5027 | 543.3257
3190.0667 | 512.7355 | 537.9756 | 543.5993
3191.0667 | 512.0577 | 538.5062 | 543.9239
3192.0667 | 510.3692 | 539.2104 | 544.0735
3193.0667 | 508.2984 | 541.5768 | 544.0249
3194.0667 | 509.0858 | 543.8168 | 544.0848
3195.0667 | 509.2753 | 544.2708 | 544.136
3196.0667 | 511.9705 | 545.1667 | 544.0035
3197.0667 | 513.5682 | 543.7175 | 543.8199
3198.0667 | 513.3692 | 543.3559 | 543.8134
3199.0667 | 514.5356 | 543.3901 | 543.8975
3200.0667 | 515.101 | 542.4106 | 543.9509
3201.0667 | 514.2665 | 541.3925 | 544.2731
3202.0667 | 512.4705 | 540.5084 | 544.6654
3203.0667 | 511.8892 | 538.5313 | 545.0429
3204.0667 | 510.7718 | 537.9013 | 545.3874
3205.0667 | 509.3096 | 538.9511 | 545.9044
3206.0667 | 508.5581 | 538.8043 | 546.5069
3207.0667 | 509.3374 | 539.8231 | 546.9134
3208.0667 | 510.5423 | 541.7307 | 547.0967
3209.0667 | 511.0855 | 542.3697 | 547.1358
3210.0667 | 512.1894 | 543.5467 | 546.9648
3211.0667 | 513.4551 | 544.8568 | 546.8628
3212.0667 | 513.0176 | 544.0206 | 546.7937
3213.0667 | 513.218 | 543.0631 | 546.8594
3214.0667 | 514.8058 | 541.796 | 546.8776
3215.0667 | 515.2114 | 541.5872 | 546.9159
3216.0667 | 516.3667 | 542.857 | 546.8543
3217.0667 | 517.8415 | 543.3005 | 546.7152
3218.0667 | 518.988 | 544.2856 | 546.4928
3219.0667 | 521.0761 | 543.5047 | 546.228
3220.0667 | 521.6663 | 543.5346 | 545.9829
3221.0667 | 524.2794 | 542.5515 | 545.7074
3222.0667 | 525.6645 | 540.1365 | 545.2666
3223.0667 | 527.7399 | 540.4146 | 544.7007
3224.0667 | 526.9993 | 540.569 | 544.1188
3225.0667 | 526.6185 | 539.9024 | 543.5698
3226.0667 | 526.3291 | 542.7365 | 543.1717
3227.0667 | 525.6744 | 544.602 | 543.0297
3228.0667 | 524.866 | 545.9285 | 543.0647
3229.0667 | 525.3816 | 545.9848 | 543.0429
3230.0667 | 528.4352 | 545.9479 | 543.0136
3231.0667 | 530.9323 | 546.5988 | 542.9149
3232.0667 | 531.4431 | 546.2214 | 542.8662
3233.0667 | 533.1599 | 544.392 | 542.6512
3234.0667 | 532.3545 | 542.8501 | 542.1986
3235.0667 | 530.5279 | 540.6732 | 541.6602
3236.0667 | 529.9276 | 544.5339 | 541.3421
3237.0667 | 528.9761 | 547.3718 | 541.2059
3238.0667 | 527.4441 | 550.0286 | 541.1645
3239.0667 | 526.8018 | 549.3661 | 540.9889
3240.0667 | 526.1497 | 549.9145 | 540.6497
3241.0667 | 524.3891 | 548.3732 | 540.4468
3242.0667 | 523.4074 | 547.1448 | 540.4688
3243.0667 | 522.2895 | 546.4104 | 540.5813
3244.0667 | 521.902 | 546.2116 | 540.9418
3245.0667 | 520.9107 | 547.3561 | 541.363
3246.0667 | 519.9829 | 546.699 | 541.6711
3247.0667 | 521.5078 | 545.7144 | 541.6488
3248.0667 | 520.7389 | 546.7096 | 541.2876
3249.0667 | 518.9406 | 546.6982 | 540.5978
3250.0667 | 517.3038 | 545.9237 | 539.7747
3251.0667 | 516.1538 | 545.8225 | 538.928
3252.0667 | 514.6949 | 545.928 | 538.1863
3253.0667 | 514.1659 | 545.4189 | 537.5657
3254.0667 | 513.2508 | 544.6304 | 536.9774
3255.0667 | 511.7148 | 544.9671 | 536.3595
3256.0667 | 512.5085 | 544.6516 | 535.6934
3257.0667 | 512.8976 | 543.0332 | 535.0365
3258.0667 | 511.9108 | 540.9504 | 534.368
3259.0667 | 511.4984 | 541.4668 | 533.7858
3260.0667 | 511.3034 | 543.5562 | 533.377
3261.0667 | 510.319 | 542.4148 | 532.9211
3262.0667 | 510.4349 | 542.4051 | 532.3776
3263.0667 | 511.4083 | 542.969 | 531.775
3264.0667 | 511.5268 | 542.6484 | 531.2572
3265.0667 | 511.4399 | 541.7953 | 530.8548
3266.0667 | 510.4773 | 540.6817 | 530.6158
3267.0667 | 509.9318 | 540.4452 | 530.4052
3268.0667 | 509.639 | 540.9562 | 530.3915
3269.0667 | 509.2597 | 541.705 | 530.4997
3270.0667 | 508.6212 | 540.4711 | 530.6567
3271.0667 | 508.3235 | 541.1189 | 530.9135
3272.0667 | 507.8255 | 543.4726 | 531.1534
3273.0667 | 508.4 | 546.8836 | 531.3545
3274.0667 | 508.5509 | 546.7578 | 531.6275
3275.0667 | 509.2951 | 544.8649 | 531.771
3276.0667 | 512.9626 | 542.7615 | 531.6957
3277.0667 | 514.0577 | 541.0982 | 531.5356
3278.0667 | 514.1783 | 540.231 | 531.5582
3279.0667 | 514.1103 | 540.4249 | 531.8596
3280.0667 | 513.2341 | 541.2485 | 532.2543
3281.0667 | 512.5753 | 539.6341 | 532.2801
3282.0667 | 512.3174 | 539.0157 | 532.0506
3283.0667 | 513.2102 | 538.2441 | 531.6478
3284.0667 | 514.4751 | 539.4844 | 531.1328
3285.0667 | 515.8407 | 539.1377 | 530.5891
3286.0667 | 515.4937 | 538.2677 | 530.0573
3287.0667 | 515.5323 | 537.6051 | 529.4668
3288.0667 | 516.0659 | 538.3564 | 528.9571
3289.0667 | 514.241 | 536.8756 | 528.4175
3290.0667 | 514.0273 | 536.0972 | 527.9369
3291.0667 | 515.0114 | 536.1565 | 527.6992
3292.0667 | 514.4054 | 537.0831 | 527.4402
3293.0667 | 512.5162 | 536.6215 | 527.1714
3294.0667 | 512.3388 | 535.1337 | 526.8592
3295.0667 | 515.074 | 535.8786 | 526.3911
3296.0667 | 517.0885 | 535.5147 | 525.8613
3297.0667 | 517.6741 | 534.4021 | 525.4011
3298.0667 | 516.5505 | 533.3427 | 525.0243
3299.0667 | 515.2472 | 533.1295 | 524.6756
3300.0667 | 515.4839 | 534.7558 | 524.3318
3301.0667 | 516.1082 | 534.6714 | 523.9461
3302.0667 | 517.2907 | 533.6756 | 523.5045
3303.0667 | 517.9878 | 533.7935 | 523.0071
3304.0667 | 516.9434 | 535.3283 | 522.5439
3305.0667 | 515.8095 | 533.7334 | 522.2283
3306.0667 | 515.7182 | 532.8149 | 522.1117
3307.0667 | 515.0289 | 532.2021 | 522.0133
3308.0667 | 513.4577 | 530.6317 | 521.944
3309.0667 | 512.6432 | 531.325 | 521.9281
3310.0667 | 512.8778 | 531.2786 | 521.8512
3311.0667 | 512.3138 | 530.5057 | 521.6096
3312.0667 | 512.0141 | 530.9876 | 521.3034
3313.0667 | 511.4722 | 529.6577 | 520.9639
3314.0667 | 514.1175 | 529.7141 | 520.6575
3315.0667 | 516.0437 | 529.6962 | 520.3107
3316.0667 | 516.542 | 530.4179 | 519.8889
3317.0667 | 515.2038 | 531.3858 | 519.5883
3318.0667 | 516.11 | 529.3596 | 519.6726
3319.0667 | 516.3417 | 528.028 | 519.7978
3320.0667 | 516.8301 | 528.1357 | 519.9969
3321.0667 | 517.5739 | 528.3532 | 520.3242
3322.0667 | 517.2112 | 527.1288 | 520.7197
3323.0667 | 515.6349 | 526.0211 | 520.9976
3324.0667 | 513.81 | 527.4114 | 521.4249
3325.0667 | 512.2688 | 528.9988 | 522.1839
3326.0667 | 511.5133 | 529.6358 | 522.8803
3327.0667 | 511.1676 | 529.8704 | 523.512
3328.0667 | 510.9827 | 530.6301 | 523.8803
3329.0667 | 511.4148 | 531.1004 | 524.1234
3330.0667 | 510.7027 | 531.2385 | 524.3098
3331.0667 | 510.6505 | 532.8451 | 524.808
3332.0667 | 511.7481 | 534.6897 | 525.3734
3333.0667 | 513.5623 | 534.9224 | 525.7314
3334.0667 | 514.0947 | 534.4393 | 525.8542
3335.0667 | 514.0191 | 533.4083 | 525.9778
3336.0667 | 513.5879 | 533.3147 | 526.1032
3337.0667 | 513.4035 | 534.6484 | 526.4223
3338.0667 | 513.5524 | 533.506 | 526.6931
3339.0667 | 512.6881 | 533.7215 | 526.7975
3340.0667 | 511.3938 | 533.5194 | 526.6979
3341.0667 | 511.2618 | 535.9208 | 526.4353
3342.0667 | 510.9848 | 535.3716 | 526.2463
3343.0667 | 511.9009 | 534.47 | 526.0645
3344.0667 | 512.7823 | 533.7119 | 525.835
3345.0667 | 512.5531 | 534.1106 | 525.4575
3346.0667 | 512.1139 | 533.8568 | 525.0156
3347.0667 | 513.0929 | 533.159 | 524.5524
3348.0667 | 513.3269 | 531.8261 | 524.1469
3349.0667 | 513.2525 | 531.3584 | 523.696
3350.0667 | 512.7986 | 530.96 | 523.1712
3351.0667 | 512.0762 | 530.1917 | 522.6478
3352.0667 | 512.4615 | 530.4069 | 522.1144
3353.0667 | 511.2616 | 529.9266 | 521.658
3354.0667 | 509.9831 | 530.0159 | 521.3331
3355.0667 | 509.7025 | 530.4179 | 521.0919
3356.0667 | 510.8556 | 529.5415 | 520.8324
3357.0667 | 510.1244 | 529.5315 | 520.5066
3358.0667 | 510.5045 | 529.0262 | 520.1278
3359.0667 | 510.4842 | 528.0469 | 519.6417
3360.0667 | 509.9612 | 527.8452 | 519.1821
3361.0667 | 509.4393 | 527.0188 | 518.6998
3362.0667 | 508.5835 | 527.1894 | 518.1855
3363.0667 | 507.5323 | 527.2538 | 517.8884
3364.0667 | 506.779 | 527.6458 | 517.7367
3365.0667 | 506.8512 | 527.7752 | 517.5186
3366.0667 | 506.4351 | 529.0534 | 517.243
3367.0667 | 506.2664 | 529.2901 | 517.0714
3368.0667 | 506.4269 | 528.9048 | 516.974
3369.0667 | 507.8644 | 527.6047 | 516.8857
3370.0667 | 507.9754 | 527.4298 | 516.777