## Test Conditions
DESIREE-FIRE Intermediate Scale Test 3 - Circuit Simulator Data Only
Test Date: | 2010-02-17
DCSim DAQ Start Time | 13:25
DCSim Time for Synchronization | 13:28
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:27
Fire Time | 14:05
Offset | 0:40 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2390 | seconds
Heat Source Offset | 0:38 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2266 | seconds
Heat Source Stop Time | 15:01
Test Duration | 0:56 | hour:minutes:seconds
| 3370 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
SOV 2 | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 5, 6, and 7 represents the air temperature 3', 5', and 7' down the cable tray located in D-Position. These are labeled as "D-Position - 3'", "D-Position - Middle", " D-Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-1.4844 | 121.5912 | -60.7132 | 60.7452 | 1.4211e-13 | -0.0084743 | 0.002421 | 0.06734 | -0.008006 | 0.059967 | 0.0079357 | -0.0014485 | -0.0010684 | 0.060766 | 0.021893 | 0.056368 | -60.6168 | 0.019721 | -60.7347 | 60.6837 | 60.6162 | 60.6757 | -60.7796 | -60.6806 | 0.009516 | -60.7288 | 60.5069 | 60.7489 | 60.6284 | -60.9479 | -0.066401 | -0.061521 | 0.096388 | -0.021526 | 0.044875 | -0.12908 | -0.069569 | -0.23475 | -0.23833 | 0.032602 | -0.015639 | 0.21911 | 0.00363 | -0.11679 | 121.3969 | 121.3294 | 121.3889 | 60.7329 | -121.5248 | 121.2201 | 121.4621 | 121.3416 | 60.7227 | -121.6932
0.25 | 121.637 | -60.7315 | 60.6857 | 1.4211e-13 | -0.0084743 | 0.0026346 | 0.06734 | -0.008006 | 0.059967 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060979 | 0.021679 | 0.056368 | -60.6168 | 0.0243 | -60.7301 | 60.6791 | 60.6162 | 60.6711 | -60.775 | -60.676 | 0.023253 | -60.7288 | 60.5069 | 60.7443 | 60.6193 | -60.9479 | -0.043512 | -0.00659 | 0.1147 | 0.001362 | 0.044874 | -0.069568 | -0.014639 | -0.21644 | -0.17882 | 0.055491 | 0.002671 | 0.21911 | 0.05856 | -0.066439 | 121.4106 | 121.3477 | 121.4026 | 60.7558 | -121.4607 | 121.2384 | 121.4758 | 121.3508 | 60.7548 | -121.6337
1.9062 | 121.5363 | -60.7956 | 60.704 | 1.4211e-13 | -0.0084743 | 0.002421 | 0.067126 | -0.008006 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.021252 | 0.056582 | -60.6168 | 0.015142 | -60.7301 | 60.6791 | 60.6253 | 60.6802 | -60.7704 | -60.6806 | 0.004938 | -60.738 | 60.5069 | 60.7534 | 60.6239 | -60.9434 | 0.025154 | -0.024901 | 0.17878 | 0.065449 | 0.040295 | -0.078721 | -0.023793 | -0.14778 | -0.19713 | 0.115 | 0.0576 | 0.20537 | 0.049407 | -0.080172 | 121.4747 | 121.4209 | 121.4758 | 60.8107 | -121.4745 | 121.3025 | 121.549 | 121.4195 | 60.8005 | -121.6474
3.625 | 121.5775 | -60.759 | 60.6995 | 1.4211e-13 | -0.0086879 | 0.002421 | 0.067554 | -0.0077924 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060979 | 0.021466 | 0.057009 | -60.6214 | 0.0243 | -60.7301 | 60.6837 | 60.6162 | 60.6711 | -60.7796 | -60.6852 | 0.004938 | -60.7334 | 60.5023 | 60.7489 | 60.633 | -60.9434 | -0.020625 | -0.015745 | 0.13759 | 0.028828 | 0.049453 | -0.083301 | -0.028372 | -0.1844 | -0.19713 | 0.073799 | 0.025558 | 0.20995 | 0.049406 | -0.066436 | 121.4427 | 121.3751 | 121.4301 | 60.7833 | -121.4791 | 121.2613 | 121.5078 | 121.392 | 60.7639 | -121.6428
5.2812 | 121.6187 | -60.7407 | 60.7086 | 1.4211e-13 | -0.0086879 | 0.0022072 | 0.067554 | -0.008006 | 0.059967 | 0.015566 | -0.0014485 | -0.00064099 | 0.060979 | 0.021893 | 0.056795 | -60.6168 | 0.015142 | -60.7256 | 60.6837 | 60.6253 | 60.6757 | -60.7842 | -60.6806 | 0.014095 | -60.7471 | 60.5069 | 60.7489 | 60.6284 | -60.9434 | -0.043514 | -0.0249 | 0.12385 | 0.015096 | 0.05861 | -0.083298 | -0.032948 | -0.20271 | -0.20171 | 0.060068 | -0.006488 | 0.19622 | 0.040251 | -0.08017 | 121.4244 | 121.366 | 121.4163 | 60.7558 | -121.4928 | 121.2476 | 121.4895 | 121.3691 | 60.7548 | -121.652
7.0156 | 121.582 | -60.7452 | 60.7315 | 1.4211e-13 | -0.0084743 | 0.0028484 | 0.067554 | -0.008006 | 0.06018 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060979 | 0.021466 | 0.056582 | -60.6214 | 0.019721 | -60.7347 | 60.6791 | 60.6299 | 60.6711 | -60.7796 | -60.676 | 0.014095 | -60.7426 | 60.5115 | 60.7534 | 60.6193 | -60.9525 | -0.034358 | -0.052366 | 0.12385 | 0.010517 | 0.044875 | -0.10161 | -0.060415 | -0.20729 | -0.22002 | 0.069224 | 0.002667 | 0.20995 | 0.021942 | -0.11222 | 121.4244 | 121.3751 | 121.4163 | 60.765 | -121.5111 | 121.2567 | 121.4987 | 121.3645 | 60.7593 | -121.684
8.6875 | 121.6141 | -60.6949 | 60.7224 | 1.4211e-13 | -0.0084743 | 0.0026346 | 0.067554 | -0.008006 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.021679 | 0.056795 | -60.6168 | 0.010564 | -60.7393 | 60.6837 | 60.6207 | 60.6757 | -60.7842 | -60.676 | 0.014095 | -60.738 | 60.5161 | 60.7534 | 60.6239 | -60.9479 | -0.089291 | -0.038633 | 0.078077 | -0.044416 | 0.044875 | -0.10161 | -0.046681 | -0.25306 | -0.20629 | 0.01887 | -0.043108 | 0.20995 | 0.031097 | -0.098482 | 121.3786 | 121.3156 | 121.3706 | 60.7054 | -121.5065 | 121.211 | 121.4483 | 121.3188 | 60.709 | -121.6703
10.4219 | 121.5546 | -60.7544 | 60.7269 | 1.4211e-13 | -0.0084743 | 0.0026346 | 0.06734 | -0.0082196 | 0.06018 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060979 | 0.021679 | 0.056582 | -60.6214 | 0.019721 | -60.7301 | 60.6791 | 60.6253 | 60.6802 | -60.7888 | -60.6806 | 0.014095 | -60.7426 | 60.5023 | 60.7489 | 60.6193 | -60.9479 | -0.03436 | -0.047789 | 0.13301 | 0.024251 | 0.058611 | -0.10161 | -0.046681 | -0.19355 | -0.2246 | 0.073801 | 0.011823 | 0.20537 | 0.02194 | -0.10764 | 121.4335 | 121.3797 | 121.4346 | 60.7741 | -121.5157 | 121.2567 | 121.5033 | 121.3737 | 60.7685 | -121.6749
12.1406 | 121.6553 | -60.7361 | 60.6995 | 1.4211e-13 | -0.0089017 | 0.0028484 | 0.067767 | -0.007365 | 0.060608 | 0.00030522 | -0.0012349 | -0.00085459 | 0.060766 | 0.021466 | 0.056582 | -60.6214 | 0.015142 | -60.7301 | 60.6791 | 60.6299 | 60.6757 | -60.775 | -60.6806 | 0.014095 | -60.7334 | 60.5069 | 60.7489 | 60.6284 | -60.9388 | -0.038934 | -0.020323 | 0.1147 | 0.00594 | 0.044874 | -0.069564 | -0.023793 | -0.20271 | -0.19255 | 0.05549 | 0.00267 | 0.20537 | 0.049406 | -0.071015 | 121.4152 | 121.366 | 121.4118 | 60.7512 | -121.4745 | 121.243 | 121.485 | 121.3645 | 60.7502 | -121.6383
13.8125 | 121.6232 | -60.7269 | 60.7452 | 1.4211e-13 | -0.0084743 | 0.002421 | 0.06734 | -0.0075786 | 0.059753 | 0.0079357 | -0.0014485 | -0.00085459 | 0.061193 | 0.021679 | 0.057009 | -60.6168 | 0.019721 | -60.7393 | 60.6791 | 60.6162 | 60.6848 | -60.775 | -60.6852 | 0.014095 | -60.738 | 60.5069 | 60.7443 | 60.6284 | -60.9434 | -0.048089 | -0.066099 | 0.11012 | -0.012372 | 0.035717 | -0.12908 | -0.060412 | -0.21644 | -0.23833 | 0.041756 | -0.011064 | 0.20537 | -0.000949 | -0.11679 | 121.4061 | 121.3431 | 121.4118 | 60.7466 | -121.5203 | 121.2338 | 121.4712 | 121.3554 | 60.741 | -121.6886
15.5312 | 121.5454 | -60.7864 | 60.7819 | 1.4211e-13 | -0.0086879 | 0.0026346 | 0.067554 | -0.0077924 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060979 | 0.021679 | 0.056582 | -60.6214 | 0.019721 | -60.7301 | 60.6791 | 60.6253 | 60.6757 | -60.7888 | -60.6806 | 0.004938 | -60.738 | 60.5115 | 60.7534 | 60.633 | -60.9479 | -0.002317 | -0.10272 | 0.16505 | 0.056294 | 0.058611 | -0.15654 | -0.10619 | -0.16151 | -0.27037 | 0.10584 | 0.048445 | 0.20995 | -0.028412 | -0.14883 | 121.4656 | 121.4118 | 121.4621 | 60.8062 | -121.5706 | 121.2979 | 121.5399 | 121.4195 | 60.7914 | -121.7298
17.2656 | 121.637 | -60.7498 | 60.6812 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.06734 | -0.0082196 | 0.06018 | 0.015566 | -0.0012349 | -0.00042739 | 0.060766 | 0.021893 | 0.057009 | -60.626 | 0.019721 | -60.7347 | 60.6883 | 60.607 | 60.6711 | -60.775 | -60.676 | 0.009516 | -60.7334 | 60.5023 | 60.7489 | 60.6239 | -60.9434 | -0.025201 | 0.007145 | 0.12385 | 0.015095 | 0.040296 | -0.074148 | -0.010061 | -0.19355 | -0.17882 | 0.073802 | 0.016403 | 0.20995 | 0.067717 | -0.057283 | 121.4381 | 121.3568 | 121.4209 | 60.7695 | -121.4562 | 121.2521 | 121.4987 | 121.3737 | 60.7593 | -121.6245
18.9375 | 121.6965 | -60.6995 | 60.7315 | 1.4211e-13 | -0.0086879 | 0.0026346 | 0.06734 | -0.0082196 | 0.059967 | 0.00030522 | -0.0018757 | -0.00042739 | 0.060979 | 0.021466 | 0.056582 | -60.6168 | 0.015142 | -60.7393 | 60.6791 | 60.6207 | 60.6711 | -60.775 | -60.6806 | 0.014095 | -60.738 | 60.5115 | 60.7443 | 60.6284 | -60.9388 | -0.075555 | -0.052366 | 0.082655 | -0.039838 | 0.035717 | -0.11077 | -0.060415 | -0.23933 | -0.22002 | 0.018869 | -0.03853 | 0.2008 | 0.012784 | -0.10306 | 121.3786 | 121.3202 | 121.3706 | 60.7146 | -121.5065 | 121.211 | 121.4438 | 121.3279 | 60.7136 | -121.6703
20.6719 | 121.6187 | -60.7132 | 60.7086 | 1.4211e-13 | -0.0086879 | 0.0026346 | 0.067554 | -0.0077924 | 0.06018 | 0.0079357 | -0.0016621 | -0.00042739 | 0.061193 | 0.021679 | 0.057223 | -60.6122 | 0.019721 | -60.7347 | 60.6929 | 60.6299 | 60.6757 | -60.7704 | -60.676 | 0.000359 | -60.738 | 60.5023 | 60.7489 | 60.6284 | -60.9388 | -0.057243 | -0.015743 | 0.10097 | -0.021526 | 0.035717 | -0.078719 | -0.032948 | -0.22559 | -0.20629 | 0.037181 | -0.024797 | 0.2008 | 0.040251 | -0.08017 | 121.4061 | 121.3431 | 121.3889 | 60.7329 | -121.4791 | 121.2155 | 121.4621 | 121.3416 | 60.7136 | -121.6474
22.3438 | 121.6553 | -60.7269 | 60.6766 | 1.4211e-13 | -0.0086879 | 0.0022072 | 0.067554 | -0.0082196 | 0.06018 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060979 | 0.021679 | 0.056582 | -60.6122 | 0.019721 | -60.7347 | 60.6791 | 60.6253 | 60.6711 | -60.775 | -60.6806 | 0.014095 | -60.7334 | 60.5023 | 60.7351 | 60.6284 | -60.9434 | -0.048089 | 0.002565 | 0.1147 | -0.007793 | 0.040296 | -0.051255 | -0.005484 | -0.21644 | -0.17424 | 0.046335 | -0.006485 | 0.20995 | 0.058558 | -0.048127 | 121.4061 | 121.3522 | 121.398 | 60.7466 | -121.4516 | 121.2293 | 121.4621 | 121.3554 | 60.741 | -121.6199
24.0625 | 121.6736 | -60.7086 | 60.7132 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.067554 | -0.008006 | 0.059967 | -0.0073253 | -0.0014485 | -0.00042739 | 0.060766 | 0.022107 | 0.057009 | -60.6214 | 0.019721 | -60.7393 | 60.6883 | 60.6299 | 60.6711 | -60.7796 | -60.6714 | 0.014095 | -60.7288 | 60.5023 | 60.7443 | 60.6239 | -60.9525 | -0.070979 | -0.024899 | 0.087232 | -0.030683 | 0.040296 | -0.083297 | -0.042105 | -0.24391 | -0.21087 | 0.037181 | -0.020217 | 0.22369 | 0.031094 | -0.089327 | 121.3969 | 121.3385 | 121.3797 | 60.7283 | -121.4928 | 121.2109 | 121.4529 | 121.3325 | 60.7227 | -121.6657
25.7188 | 121.5271 | -60.7956 | 60.6995 | 1.4211e-13 | -0.0089017 | 0.0022072 | 0.067554 | -0.0077924 | 0.059967 | 0.00030522 | -0.0010211 | -0.00064099 | 0.060979 | 0.021893 | 0.056795 | -60.6168 | 0.015142 | -60.7256 | 60.6791 | 60.6253 | 60.6757 | -60.775 | -60.6714 | 0.014095 | -60.7334 | 60.5023 | 60.7489 | 60.6239 | -60.9434 | 0.020575 | -0.020323 | 0.17878 | 0.070027 | 0.049452 | -0.074143 | -0.023793 | -0.14778 | -0.19713 | 0.12416 | 0.062179 | 0.20995 | 0.049406 | -0.075594 | 121.4747 | 121.4209 | 121.4713 | 60.8107 | -121.4745 | 121.2979 | 121.5445 | 121.4195 | 60.8097 | -121.6428
27.4375 | 121.6003 | -60.7681 | 60.6857 | 1.4211e-13 | -0.0086879 | 0.002421 | 0.06734 | -0.0077924 | 0.060394 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060766 | 0.021893 | 0.056368 | -60.6214 | 0.019721 | -60.7347 | 60.6837 | 60.6253 | 60.6665 | -60.7796 | -60.6669 | 0.009516 | -60.7288 | 60.5115 | 60.7443 | 60.6284 | -60.9342 | -0.01147 | -0.002012 | 0.14674 | 0.033405 | 0.044875 | -0.06041 | -0.019217 | -0.16608 | -0.17424 | 0.10127 | 0.039292 | 0.20538 | 0.05856 | -0.057282 | 121.4518 | 121.3934 | 121.4346 | 60.7878 | -121.4653 | 121.2796 | 121.5124 | 121.3966 | 60.7776 | -121.6199
29.1719 | 121.6919 | -60.6949 | 60.7086 | 1.4211e-13 | -0.0089017 | 0.0022072 | 0.067767 | -0.008006 | 0.06018 | 0.00030522 | -0.0010211 | -0.00042739 | 0.060979 | 0.021893 | 0.056795 | -60.6168 | 0.010564 | -60.7301 | 60.6837 | 60.6253 | 60.6757 | -60.7796 | -60.6669 | 0.014095 | -60.738 | 60.5069 | 60.7351 | 60.633 | -60.9479 | -0.084712 | -0.0249 | 0.078077 | -0.035259 | 0.049453 | -0.083298 | -0.032948 | -0.25306 | -0.20171 | 0.028027 | -0.043108 | 0.20995 | 0.026515 | -0.075591 | 121.3786 | 121.3202 | 121.3706 | 60.7054 | -121.4882 | 121.2018 | 121.43 | 121.3279 | 60.709 | -121.6566
30.8906 | 121.6507 | -60.7086 | 60.6766 | 1.4211e-13 | -0.0086879 | 0.0026346 | 0.067554 | -0.008006 | 0.06018 | 0.00030522 | -0.0014485 | -0.00085459 | 0.060979 | 0.022107 | 0.056582 | -60.6168 | 0.019721 | -60.7347 | 60.6746 | 60.6207 | 60.6802 | -60.7796 | -60.676 | 0.009516 | -60.7334 | 60.5069 | 60.7443 | 60.6239 | -60.9434 | -0.070979 | -0.002014 | 0.09181 | -0.026104 | 0.044875 | -0.055834 | 0.003673 | -0.23475 | -0.16967 | 0.032603 | -0.024796 | 0.20995 | 0.067715 | -0.052706 | 121.3832 | 121.3294 | 121.3889 | 60.7283 | -121.4562 | 121.2155 | 121.4529 | 121.3325 | 60.7181 | -121.6199
32.5625 | 121.5454 | -60.8047 | 60.704 | 1.4211e-13 | -0.0089017 | 0.0026346 | 0.067767 | -0.008006 | 0.059967 | 0.00030522 | -0.0014485 | -0.0010684 | 0.060979 | 0.022107 | 0.056368 | -60.6168 | 0.010564 | -60.7347 | 60.6837 | 60.6207 | 60.6711 | -60.7704 | -60.6714 | 0.004938 | -60.7334 | 60.5069 | 60.7489 | 60.6239 | -60.9479 | 0.03431 | -0.020323 | 0.18794 | 0.070027 | 0.035717 | -0.0833 | -0.03295 | -0.1432 | -0.19713 | 0.13331 | 0.071335 | 0.21453 | 0.044828 | -0.080172 | 121.4885 | 121.4255 | 121.4758 | 60.8153 | -121.4745 | 121.3117 | 121.5536 | 121.4286 | 60.8097 | -121.652
34.2812 | 121.5363 | -60.7956 | 60.7178 | 1.4211e-13 | -0.0091153 | 0.002421 | 0.067554 | -0.008006 | 0.060394 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060979 | 0.022107 | 0.056795 | -60.6122 | 0.015142 | -60.7347 | 60.6883 | 60.6162 | 60.6757 | -60.7796 | -60.6852 | 0.009516 | -60.7334 | 60.5069 | 60.7443 | 60.6239 | -60.9479 | 0.015996 | -0.029476 | 0.18336 | 0.060871 | 0.044875 | -0.10161 | -0.042103 | -0.15235 | -0.21086 | 0.11042 | 0.062179 | 0.21453 | 0.026517 | -0.093904 | 121.4839 | 121.4118 | 121.4713 | 60.8107 | -121.4974 | 121.3025 | 121.5399 | 121.4195 | 60.8051 | -121.6657
36 | 121.5408 | -60.791 | 60.6766 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.067554 | -0.0077924 | 0.06018 | 0.0079357 | -0.0012349 | -0.00064099 | 0.060552 | 0.022107 | 0.056155 | -60.6168 | 0.019721 | -60.7347 | 60.6791 | 60.6253 | 60.6802 | -60.7704 | -60.676 | 0.009516 | -60.7288 | 60.5115 | 60.7351 | 60.633 | -60.9434 | 0.020577 | 0.002565 | 0.17421 | 0.056294 | 0.035717 | -0.051255 | 0.003673 | -0.15235 | -0.16509 | 0.115 | 0.062181 | 0.21453 | 0.058558 | -0.043548 | 121.4702 | 121.4163 | 121.4713 | 60.8107 | -121.447 | 121.3025 | 121.5261 | 121.424 | 60.8005 | -121.6199
37.7188 | 121.6324 | -60.7544 | 60.6674 | 1.4211e-13 | -0.0089017 | 0.0026346 | 0.067981 | -0.0077924 | 0.059967 | 0.00030522 | -0.0012349 | -0.00042739 | 0.060979 | 0.022107 | 0.056795 | -60.6168 | 0.015142 | -60.7301 | 60.6837 | 60.6253 | 60.6711 | -60.7796 | -60.676 | 0.009516 | -60.7288 | 60.5069 | 60.7443 | 60.6239 | -60.9434 | -0.025202 | 0.016299 | 0.13759 | 0.024251 | 0.049453 | -0.042099 | 0.003672 | -0.18897 | -0.16051 | 0.07838 | 0.02556 | 0.21453 | 0.076871 | -0.04355 | 121.4381 | 121.3797 | 121.4255 | 60.7695 | -121.447 | 121.2613 | 121.4987 | 121.3783 | 60.7639 | -121.6108
39.4375 | 121.6415 | -60.6995 | 60.6857 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.067981 | -0.0077924 | 0.059967 | 0.015566 | -0.0014485 | -0.00042739 | 0.060979 | 0.02232 | 0.056368 | -60.6122 | 0.015142 | -60.7301 | 60.6837 | 60.6299 | 60.6711 | -60.7796 | -60.6714 | 0.009516 | -60.7288 | 60.5023 | 60.7489 | 60.6284 | -60.9434 | -0.080134 | -0.002012 | 0.087234 | -0.030681 | 0.049453 | -0.055831 | -0.014639 | -0.2439 | -0.1834 | 0.028026 | -0.029372 | 0.21453 | 0.063139 | -0.057282 | 121.3832 | 121.3294 | 121.3706 | 60.7146 | -121.4653 | 121.2018 | 121.4483 | 121.3279 | 60.709 | -121.6291
41.1094 | 121.5591 | -60.7269 | 60.7544 | 1.4211e-13 | -0.0086879 | 0.0022072 | 0.067554 | -0.0077924 | 0.060394 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.02232 | 0.056795 | -60.6168 | 0.028878 | -60.7347 | 60.6883 | 60.6162 | 60.6757 | -60.7842 | -60.6669 | 0.014095 | -60.7288 | 60.5023 | 60.7489 | 60.633 | -60.9479 | -0.057247 | -0.066098 | 0.11012 | -0.007793 | 0.049454 | -0.13823 | -0.078725 | -0.22102 | -0.25206 | 0.060071 | -0.001906 | 0.21911 | -0.005526 | -0.12137 | 121.4152 | 121.3431 | 121.4026 | 60.7558 | -121.5386 | 121.2293 | 121.4758 | 121.36 | 60.741 | -121.7023
42.8125 | 121.6324 | -60.7315 | 60.704 | 1.4211e-13 | -0.0089017 | 0.0028484 | 0.067981 | -0.0077924 | 0.060394 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.022107 | 0.056582 | -60.6168 | 0.015142 | -60.7301 | 60.6791 | 60.6253 | 60.6757 | -60.7796 | -60.676 | 0.014095 | -60.7288 | 60.5069 | 60.7534 | 60.6239 | -60.9479 | -0.048091 | -0.024901 | 0.1147 | 0.001362 | 0.049453 | -0.078721 | -0.028371 | -0.21644 | -0.19713 | 0.055491 | 0.002671 | 0.21911 | 0.049407 | -0.080172 | 121.4106 | 121.3568 | 121.4072 | 60.7466 | -121.4836 | 121.2384 | 121.485 | 121.3554 | 60.7456 | -121.652
44.5 | 121.5271 | -60.7498 | 60.7636 | 1.4211e-13 | -0.0091153 | 0.002421 | 0.06734 | -0.008006 | 0.059967 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060979 | 0.02232 | 0.056795 | -60.6168 | 0.015142 | -60.7347 | 60.6883 | 60.6299 | 60.6757 | -60.7888 | -60.6623 | 0.014095 | -60.738 | 60.5069 | 60.7489 | 60.633 | -60.9434 | -0.038938 | -0.075253 | 0.13301 | 0.015095 | 0.054033 | -0.13365 | -0.08788 | -0.19355 | -0.25664 | 0.087538 | 0.011824 | 0.20537 | -0.014681 | -0.13052 | 121.4381 | 121.3797 | 121.4255 | 60.765 | -121.5523 | 121.2567 | 121.4987 | 121.3828 | 60.7639 | -121.7069
46.2188 | 121.637 | -60.7224 | 60.6674 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.068195 | -0.008006 | 0.06018 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060979 | 0.022534 | 0.057009 | -60.6168 | 0.019721 | -60.7347 | 60.6837 | 60.6299 | 60.6757 | -60.7796 | -60.6714 | 0.004938 | -60.7288 | 60.5069 | 60.7443 | 60.6239 | -60.9479 | -0.057246 | 0.016299 | 0.10554 | -0.012371 | 0.044875 | -0.03752 | 0.008251 | -0.2256 | -0.16051 | 0.050914 | -0.006484 | 0.21911 | 0.076871 | -0.04355 | 121.4061 | 121.3522 | 121.398 | 60.7421 | -121.447 | 121.2293 | 121.4666 | 121.3462 | 60.7273 | -121.6154
47.9531 | 121.5408 | -60.7864 | 60.6995 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.0077924 | 0.060394 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060766 | 0.02232 | 0.057009 | -60.6122 | 0.0243 | -60.7256 | 60.6746 | 60.6253 | 60.6711 | -60.775 | -60.676 | 0.018674 | -60.7243 | 60.5023 | 60.7397 | 60.6284 | -60.9434 | 0.01142 | -0.024902 | 0.17421 | 0.060872 | 0.049452 | -0.074143 | -0.028372 | -0.15693 | -0.19713 | 0.11042 | 0.062181 | 0.21911 | 0.040249 | -0.071015 | 121.461 | 121.4118 | 121.4575 | 60.8107 | -121.4745 | 121.2888 | 121.5262 | 121.4149 | 60.8051 | -121.6428
49.6094 | 121.5271 | -60.7269 | 60.7407 | 1.4211e-13 | -0.0091153 | 0.002421 | 0.06734 | -0.008006 | 0.059967 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060552 | 0.02232 | 0.056582 | -60.6214 | 0.0243 | -60.7256 | 60.6837 | 60.6207 | 60.6711 | -60.7796 | -60.676 | 0.009516 | -60.7288 | 60.5069 | 60.7443 | 60.6284 | -60.9479 | -0.052668 | -0.056944 | 0.10554 | 0.001363 | 0.054031 | -0.11992 | -0.069571 | -0.22102 | -0.23375 | 0.050914 | -0.001906 | 0.21911 | 0.003628 | -0.11221 | 121.4106 | 121.3477 | 121.398 | 60.7512 | -121.5203 | 121.2338 | 121.4712 | 121.3554 | 60.7364 | -121.6886
51.3281 | 121.669 | -60.6812 | 60.7224 | 1.4211e-13 | -0.0091153 | 0.0019936 | 0.067767 | -0.0077924 | 0.060394 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060552 | 0.022107 | 0.056368 | -60.6168 | 0.0243 | -60.7301 | 60.6837 | 60.6253 | 60.6711 | -60.7704 | -60.6714 | 0.009516 | -60.7334 | 60.5069 | 60.7443 | 60.6284 | -60.9434 | -0.089287 | -0.038633 | 0.064344 | -0.048992 | 0.040295 | -0.097031 | -0.05126 | -0.26222 | -0.21544 | 0.009715 | -0.052262 | 0.20995 | 0.021939 | -0.093903 | 121.3649 | 121.3065 | 121.3522 | 60.7055 | -121.4928 | 121.1881 | 121.4254 | 121.3096 | 60.6907 | -121.6657
53.0625 | 121.5729 | -60.759 | 60.7224 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.0075786 | 0.060394 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060766 | 0.022107 | 0.056368 | -60.6168 | 0.019721 | -60.7256 | 60.6837 | 60.6207 | 60.6665 | -60.775 | -60.6806 | 0.009516 | -60.7288 | 60.5023 | 60.7443 | 60.6239 | -60.9434 | -0.016046 | -0.038633 | 0.14216 | 0.033406 | 0.049452 | -0.10161 | -0.055838 | -0.1844 | -0.22002 | 0.078378 | 0.030137 | 0.21453 | 0.021939 | -0.098482 | 121.4427 | 121.3797 | 121.4255 | 60.7787 | -121.4974 | 121.2613 | 121.5033 | 121.3828 | 60.7685 | -121.6657
54.7344 | 121.669 | -60.6903 | 60.6949 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067767 | -0.0082196 | 0.06018 | 0.015566 | -0.0014485 | -0.00042739 | 0.060552 | 0.022107 | 0.056795 | -60.6077 | 0.019721 | -60.7301 | 60.6791 | 60.6207 | 60.6711 | -60.7796 | -60.6714 | 0.014095 | -60.7334 | 60.5023 | 60.7443 | 60.6193 | -60.9434 | -0.089289 | -0.015745 | 0.082657 | -0.039836 | 0.049453 | -0.074144 | -0.023794 | -0.25306 | -0.19255 | 0.018871 | -0.043106 | 0.20995 | 0.049405 | -0.075594 | 121.3694 | 121.311 | 121.3614 | 60.71 | -121.4745 | 121.1926 | 121.4346 | 121.3096 | 60.7044 | -121.6383
56.4531 | 121.6278 | -60.7269 | 60.7132 | 1.4211e-13 | -0.0093289 | 0.0026346 | 0.067126 | -0.0077924 | 0.06018 | 0.00030522 | -0.0012349 | -0.00064099 | 0.060979 | 0.02232 | 0.056795 | -60.6168 | 0.019721 | -60.7256 | 60.6837 | 60.6253 | 60.6711 | -60.775 | -60.6714 | 0.014095 | -60.7288 | 60.5115 | 60.7489 | 60.6239 | -60.9388 | -0.048089 | -0.029478 | 0.11012 | 0.001363 | 0.049452 | -0.087876 | -0.042105 | -0.21186 | -0.20171 | 0.055492 | -0.001906 | 0.20995 | 0.035673 | -0.089327 | 121.4106 | 121.3522 | 121.398 | 60.7466 | -121.4882 | 121.2384 | 121.4758 | 121.3508 | 60.741 | -121.652
58.1875 | 121.5363 | -60.7498 | 60.7773 | 1.4211e-13 | -0.0093289 | 0.0026346 | 0.06734 | -0.008006 | 0.059967 | 0.015566 | -0.0014485 | -0.00064099 | 0.060766 | 0.02232 | 0.056155 | -60.6122 | 0.019721 | -60.7301 | 60.6837 | 60.6345 | 60.6802 | -60.775 | -60.6714 | 0.023253 | -60.7334 | 60.5069 | 60.7351 | 60.6284 | -60.9388 | -0.025201 | -0.093565 | 0.13759 | 0.019673 | 0.044874 | -0.1428 | -0.097035 | -0.18897 | -0.27037 | 0.07838 | 0.016403 | 0.20537 | -0.04215 | -0.14883 | 121.4335 | 121.3843 | 121.4301 | 60.7695 | -121.5523 | 121.2567 | 121.4849 | 121.3783 | 60.7731 | -121.7161
59.9219 | 121.6141 | -60.704 | 60.7224 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.067554 | -0.0077924 | 0.06018 | 0.015566 | -0.0014485 | -0.00021359 | 0.060766 | 0.022107 | 0.056795 | -60.6077 | 0.019721 | -60.7347 | 60.6791 | 60.6299 | 60.6711 | -60.775 | -60.6714 | 0.009516 | -60.7288 | 60.5023 | 60.7351 | 60.6193 | -60.9479 | -0.070977 | -0.043211 | 0.09639 | -0.030681 | 0.040296 | -0.092452 | -0.05126 | -0.24391 | -0.22002 | 0.032604 | -0.024794 | 0.21911 | 0.012782 | -0.10306 | 121.3832 | 121.3339 | 121.3751 | 60.7238 | -121.4974 | 121.2064 | 121.4392 | 121.3233 | 60.7136 | -121.6703
61.5938 | 121.5591 | -60.7452 | 60.7452 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.0075786 | 0.059967 | 0.015566 | -0.0014485 | -0.00064099 | 0.060552 | 0.022107 | 0.056155 | -60.6168 | 0.0243 | -60.7301 | 60.6746 | 60.6299 | 60.6711 | -60.7659 | -60.6714 | 0.014095 | -60.7288 | 60.5069 | 60.7306 | 60.6284 | -60.9479 | -0.020621 | -0.070678 | 0.12843 | 0.015095 | 0.035716 | -0.11534 | -0.074148 | -0.20271 | -0.23833 | 0.073802 | 0.016404 | 0.21911 | -0.014685 | -0.11679 | 121.4198 | 121.3751 | 121.4163 | 60.7695 | -121.5111 | 121.2521 | 121.4758 | 121.3737 | 60.7593 | -121.6932
63.3281 | 121.5225 | -60.8002 | 60.6766 | 1.4211e-13 | -0.0093289 | 0.0026346 | 0.06734 | -0.0082196 | 0.060394 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060552 | 0.02232 | 0.056368 | -60.6077 | 0.015142 | -60.7301 | 60.6837 | 60.6253 | 60.6711 | -60.7704 | -60.6806 | 0.018674 | -60.7288 | 60.5023 | 60.7397 | 60.6193 | -60.9434 | 0.029732 | 0.007143 | 0.19252 | 0.070027 | 0.040295 | -0.051255 | -0.005484 | -0.1432 | -0.17424 | 0.11958 | 0.071336 | 0.21453 | 0.063137 | -0.057284 | 121.4839 | 121.4255 | 121.4713 | 60.8153 | -121.447 | 121.3025 | 121.5399 | 121.4195 | 60.8188 | -121.6199
65 | 121.5866 | -60.6995 | 60.7773 | 1.4211e-13 | -0.0093289 | 0.0022072 | 0.067981 | -0.0082196 | 0.06018 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.022534 | 0.056582 | -60.6122 | 0.015142 | -60.7393 | 60.6791 | 60.6253 | 60.6711 | -60.7796 | -60.6714 | 0.014095 | -60.7197 | 60.5023 | 60.7443 | 60.633 | -60.9479 | -0.080134 | -0.098143 | 0.087234 | -0.039838 | 0.040296 | -0.15196 | -0.10619 | -0.24848 | -0.27495 | 0.028026 | -0.020215 | 0.22827 | -0.032993 | -0.14426 | 121.3786 | 121.3248 | 121.3706 | 60.7146 | -121.5569 | 121.2018 | 121.4438 | 121.3325 | 60.7136 | -121.7252
66.6562 | 121.6187 | -60.7315 | 60.7178 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.008006 | 0.060394 | -0.0073253 | -0.0014485 | -0.00042739 | 0.060766 | 0.02232 | 0.056155 | -60.6122 | 0.015142 | -60.7347 | 60.6791 | 60.6207 | 60.6711 | -60.775 | -60.6669 | 0.014095 | -60.7288 | 60.4978 | 60.7443 | 60.6239 | -60.9434 | -0.043512 | -0.038633 | 0.11928 | -0.003216 | 0.040296 | -0.097032 | -0.046682 | -0.21186 | -0.22002 | 0.064648 | 0.002671 | 0.21453 | 0.026517 | -0.093904 | 121.4106 | 121.3522 | 121.4026 | 60.7466 | -121.4928 | 121.2293 | 121.4758 | 121.3554 | 60.7456 | -121.6611
68.3906 | 121.5866 | -60.7315 | 60.7132 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.008006 | 0.060394 | 0.015566 | -0.0018757 | -0.00064099 | 0.060979 | 0.022534 | 0.056368 | -60.6077 | 0.019721 | -60.7301 | 60.6837 | 60.6299 | 60.6757 | -60.7796 | -60.676 | 0.009516 | -60.7334 | 60.5069 | 60.7351 | 60.6239 | -60.9434 | -0.048091 | -0.029478 | 0.12386 | 0.001362 | 0.049453 | -0.083297 | -0.037526 | -0.21186 | -0.20629 | 0.055491 | -0.001908 | 0.20995 | 0.021937 | -0.089327 | 121.4152 | 121.3614 | 121.4072 | 60.7512 | -121.4928 | 121.2384 | 121.4666 | 121.3554 | 60.741 | -121.6566
70.0625 | 121.5363 | -60.7956 | 60.6995 | 1.4211e-13 | -0.0095427 | 0.0026346 | 0.067554 | -0.0082196 | 0.059967 | 0.00030522 | -0.0010211 | -0.00042739 | 0.060766 | 0.022748 | 0.056368 | -60.6077 | 0.028878 | -60.721 | 60.6746 | 60.6299 | 60.6802 | -60.7796 | -60.6623 | 0.014095 | -60.7334 | 60.5115 | 60.7443 | 60.6239 | -60.9434 | 0.015996 | -0.024902 | 0.18794 | 0.074605 | 0.058609 | -0.069564 | -0.019215 | -0.14778 | -0.18798 | 0.13331 | 0.062179 | 0.20995 | 0.044827 | -0.075594 | 121.4702 | 121.4255 | 121.4758 | 60.8245 | -121.4791 | 121.3071 | 121.5399 | 121.4195 | 60.8097 | -121.6428
71.7344 | 121.6232 | -60.7086 | 60.7452 | 1.4211e-13 | -0.0089017 | 0.002421 | 0.067767 | -0.0077924 | 0.060394 | 0.015566 | -0.0012349 | -0.00064099 | 0.060552 | 0.022534 | 0.056368 | -60.6214 | 0.015142 | -60.7256 | 60.6837 | 60.6253 | 60.6711 | -60.775 | -60.6669 | 0.023253 | -60.7243 | 60.5069 | 60.7443 | 60.6284 | -60.9479 | -0.0664 | -0.061521 | 0.087232 | -0.016948 | 0.049452 | -0.11992 | -0.074148 | -0.23933 | -0.23833 | 0.04176 | -0.015639 | 0.22369 | -0.000949 | -0.11679 | 121.3923 | 121.3339 | 121.3797 | 60.7238 | -121.5203 | 121.2155 | 121.4529 | 121.3371 | 60.7319 | -121.6932
73.4688 | 121.6415 | -60.7315 | 60.6674 | 1.4211e-13 | -0.0091153 | 0.0026346 | 0.067767 | -0.008006 | 0.060394 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.022534 | 0.056582 | -60.6077 | 0.019721 | -60.721 | 60.6791 | 60.6253 | 60.6757 | -60.775 | -60.6714 | 0.014095 | -60.7288 | 60.5069 | 60.7443 | 60.6284 | -60.9434 | -0.043512 | 0.011721 | 0.12386 | 0.010518 | 0.05403 | -0.042099 | 0.008251 | -0.21186 | -0.16051 | 0.060069 | 0.002671 | 0.21453 | 0.076871 | -0.038971 | 121.4106 | 121.3568 | 121.4072 | 60.7512 | -121.4424 | 121.2384 | 121.4758 | 121.36 | 60.7456 | -121.6108
75.2031 | 121.5363 | -60.7407 | 60.759 | 1.4211e-13 | -0.0093289 | 0.0022072 | 0.067554 | -0.008006 | 0.060394 | 0.0079357 | -0.0016621 | -0.00042739 | 0.061193 | 0.022534 | 0.056795 | -60.6031 | 0.015142 | -60.721 | 60.6791 | 60.6253 | 60.6757 | -60.7796 | -60.676 | 0.018674 | -60.7288 | 60.5069 | 60.7489 | 60.6284 | -60.9525 | -0.038935 | -0.079832 | 0.13759 | 0.019674 | 0.058609 | -0.13365 | -0.083302 | -0.21186 | -0.25206 | 0.064647 | 0.011827 | 0.22369 | -0.010103 | -0.13052 | 121.4198 | 121.366 | 121.4163 | 60.7558 | -121.5386 | 121.2476 | 121.4895 | 121.3691 | 60.7593 | -121.7115
76.875 | 121.6827 | -60.6949 | 60.7269 | 1.4211e-13 | -0.0093289 | 0.0022072 | 0.067767 | -0.008006 | 0.06018 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060766 | 0.022748 | 0.056368 | -60.6122 | 0.015142 | -60.7256 | 60.6883 | 60.6253 | 60.6757 | -60.7796 | -60.6806 | 0.014095 | -60.7288 | 60.5069 | 60.7489 | 60.6239 | -60.9479 | -0.084712 | -0.038632 | 0.082656 | -0.030681 | 0.054031 | -0.10161 | -0.051259 | -0.25306 | -0.22002 | 0.014291 | -0.03395 | 0.21911 | 0.02194 | -0.10306 | 121.3832 | 121.3202 | 121.3706 | 60.71 | -121.5065 | 121.2018 | 121.4438 | 121.3188 | 60.709 | -121.6749
78.6094 | 121.5408 | -60.7727 | 60.6857 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067981 | -0.008006 | 0.059967 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060979 | 0.02232 | 0.056368 | -60.6122 | 0.019721 | -60.721 | 60.6746 | 60.6207 | 60.6757 | -60.775 | -60.676 | 0.014095 | -60.7288 | 60.5069 | 60.7489 | 60.6239 | -60.9479 | -0.002313 | -0.011169 | 0.16048 | 0.051717 | 0.05403 | -0.064989 | -0.01006 | -0.17524 | -0.17882 | 0.09669 | 0.04387 | 0.21911 | 0.063139 | -0.061861 | 121.4473 | 121.3934 | 121.4484 | 60.7924 | -121.4607 | 121.2796 | 121.5216 | 121.3966 | 60.7868 | -121.6337
80.3438 | 121.6324 | -60.6812 | 60.7269 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.067554 | -0.0082196 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.022748 | 0.056155 | -60.6122 | 0.019721 | -60.721 | 60.6746 | 60.6253 | 60.6665 | -60.7704 | -60.676 | 0.018674 | -60.7334 | 60.4978 | 60.7397 | 60.6193 | -60.9434 | -0.089287 | -0.052368 | 0.068923 | -0.039836 | 0.049451 | -0.10161 | -0.060416 | -0.26222 | -0.22918 | 0.005137 | -0.052262 | 0.20995 | 0.012783 | -0.10764 | 121.3557 | 121.3065 | 121.3477 | 60.7009 | -121.4974 | 121.1789 | 121.4209 | 121.3004 | 60.6998 | -121.6703
82 | 121.6095 | -60.7178 | 60.6903 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.068195 | -0.0082196 | 0.059967 | 0.00030522 | -0.0012349 | -0.00042739 | 0.060979 | 0.022534 | 0.056368 | -60.6122 | 0.019721 | -60.721 | 60.6791 | 60.6162 | 60.6711 | -60.7796 | -60.6714 | 0.018674 | -60.738 | 60.5023 | 60.7443 | 60.6193 | -60.9479 | -0.061824 | -0.011168 | 0.10554 | -0.003215 | 0.058609 | -0.074146 | -0.019217 | -0.23017 | -0.18798 | 0.046336 | -0.02022 | 0.20995 | 0.053982 | -0.071017 | 121.3969 | 121.3339 | 121.3889 | 60.7375 | -121.4699 | 121.2201 | 121.4621 | 121.3371 | 60.7364 | -121.6383
83.6875 | 121.6415 | -60.6857 | 60.7269 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.0082196 | 0.06018 | 0.015566 | -0.0012349 | -0.00064099 | 0.060766 | 0.022534 | 0.056582 | -60.6077 | 0.015142 | -60.721 | 60.6791 | 60.6299 | 60.6802 | -60.7842 | -60.6669 | 0.014095 | -60.7243 | 60.5023 | 60.7489 | 60.6284 | -60.9479 | -0.098446 | -0.047789 | 0.078079 | -0.035258 | 0.063188 | -0.09703 | -0.046681 | -0.26222 | -0.2246 | 0.018872 | -0.038527 | 0.22369 | 0.02194 | -0.098481 | 121.3649 | 121.3156 | 121.366 | 60.7009 | -121.5111 | 121.1881 | 121.4346 | 121.3142 | 60.6998 | -121.6749
85.4062 | 121.6232 | -60.7178 | 60.7132 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.067767 | -0.0082196 | 0.06018 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060766 | 0.022748 | 0.056582 | -60.6077 | 0.0243 | -60.721 | 60.6746 | 60.6299 | 60.6711 | -60.7704 | -60.6669 | 0.009516 | -60.7288 | 60.5023 | 60.7443 | 60.6284 | -60.9479 | -0.052666 | -0.038635 | 0.11012 | -0.003215 | 0.049451 | -0.083297 | -0.042105 | -0.23017 | -0.21087 | 0.050915 | -0.011062 | 0.21911 | 0.031094 | -0.084748 | 121.3923 | 121.3477 | 121.3889 | 60.7421 | -121.4836 | 121.2201 | 121.4621 | 121.3462 | 60.7273 | -121.6611
87.125 | 121.6232 | -60.6949 | 60.7132 | 1.4211e-13 | -0.0093289 | 0.0028484 | 0.06734 | -0.0084334 | 0.060394 | 0.015566 | -0.0016621 | -0.00064099 | 0.060979 | 0.022748 | 0.056155 | -60.6122 | 0.019721 | -60.7301 | 60.6837 | 60.6253 | 60.6665 | -60.775 | -60.6714 | 0.014095 | -60.7288 | 60.5069 | 60.7397 | 60.6284 | -60.9434 | -0.080133 | -0.029478 | 0.082656 | -0.035259 | 0.044874 | -0.087876 | -0.046683 | -0.24848 | -0.20629 | 0.023448 | -0.03395 | 0.21453 | 0.026516 | -0.084748 | 121.3786 | 121.3202 | 121.3614 | 60.7146 | -121.4882 | 121.2018 | 121.4346 | 121.3233 | 60.709 | -121.6566
88.8438 | 121.5271 | -60.7452 | 60.7452 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.06734 | -0.0084334 | 0.06018 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.022534 | 0.056368 | -60.6077 | 0.015142 | -60.721 | 60.6791 | 60.6253 | 60.6711 | -60.775 | -60.6714 | 0.018674 | -60.7243 | 60.5023 | 60.7306 | 60.6284 | -60.9434 | -0.029779 | -0.066099 | 0.13759 | 0.024251 | 0.05403 | -0.11992 | -0.074148 | -0.19813 | -0.24291 | 0.073802 | 0.020982 | 0.21911 | -0.014685 | -0.11679 | 121.4244 | 121.3706 | 121.4163 | 60.7604 | -121.5203 | 121.2476 | 121.4758 | 121.3737 | 60.7639 | -121.6886
90.5625 | 121.5546 | -60.7361 | 60.7132 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067767 | -0.008006 | 0.06018 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060766 | 0.022748 | 0.056368 | -60.6122 | 0.015142 | -60.721 | 60.6837 | 60.6253 | 60.6665 | -60.775 | -60.6714 | 0.014095 | -60.7288 | 60.5023 | 60.7351 | 60.6239 | -60.9434 | -0.038934 | -0.029478 | 0.12385 | 0.015096 | 0.05403 | -0.087876 | -0.046683 | -0.20728 | -0.21087 | 0.064647 | 0.007249 | 0.21453 | 0.021937 | -0.089327 | 121.4198 | 121.3614 | 121.4026 | 60.7512 | -121.4882 | 121.2384 | 121.4712 | 121.36 | 60.7502 | -121.6566
92.2969 | 121.6415 | -60.6766 | 60.6995 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067981 | -0.0082196 | 0.06018 | -0.0073253 | -0.0016621 | -0.00021359 | 0.060552 | 0.022961 | 0.056582 | -60.6077 | 0.019721 | -60.7164 | 60.6883 | 60.6207 | 60.6665 | -60.7796 | -60.676 | 0.018674 | -60.7288 | 60.5023 | 60.7397 | 60.6239 | -60.9525 | -0.10302 | -0.011166 | 0.068924 | -0.039834 | 0.063188 | -0.078722 | -0.03295 | -0.27595 | -0.19713 | 0.00056 | -0.05226 | 0.22369 | 0.040249 | -0.075594 | 121.3649 | 121.2973 | 121.3431 | 60.6963 | -121.4791 | 121.1789 | 121.4163 | 121.3004 | 60.6952 | -121.652
93.9688 | 121.6553 | -60.6949 | 60.7132 | 1.4211e-13 | -0.0093289 | 0.0019936 | 0.067767 | -0.008006 | 0.060394 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.022748 | 0.056368 | -60.6122 | 0.0243 | -60.7301 | 60.6746 | 60.6299 | 60.6665 | -60.7796 | -60.6669 | 0.014095 | -60.7243 | 60.5023 | 60.7351 | 60.6239 | -60.9479 | -0.084712 | -0.038635 | 0.082656 | -0.035259 | 0.049453 | -0.083297 | -0.046683 | -0.25306 | -0.21087 | 0.028027 | -0.029372 | 0.22369 | 0.021937 | -0.089327 | 121.3694 | 121.3248 | 121.3614 | 60.7192 | -121.4928 | 121.1972 | 121.43 | 121.3188 | 60.709 | -121.6611
95.7031 | 121.6644 | -60.6949 | 60.6949 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067767 | -0.0084334 | 0.059753 | 0.015566 | -0.0016621 | -0.00064099 | 0.060979 | 0.022748 | 0.056368 | -60.6077 | 0.015142 | -60.721 | 60.6746 | 60.6207 | 60.6665 | -60.7659 | -60.6669 | 0.014095 | -60.7334 | 60.5069 | 60.7306 | 60.6239 | -60.9434 | -0.070975 | -0.020324 | 0.087234 | -0.026103 | 0.044872 | -0.074144 | -0.028372 | -0.24848 | -0.18798 | 0.028027 | -0.038529 | 0.20995 | 0.035669 | -0.071016 | 121.3694 | 121.3156 | 121.3614 | 60.71 | -121.4607 | 121.2018 | 121.4254 | 121.3188 | 60.709 | -121.6383
97.4375 | 121.6461 | -60.6857 | 60.7178 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067981 | -0.0084334 | 0.060394 | 0.0079357 | -0.0018757 | -0.00042739 | 0.060979 | 0.023175 | 0.056368 | -60.6122 | 0.019721 | -60.7256 | 60.6791 | 60.6253 | 60.6711 | -60.7704 | -60.6714 | 0.018674 | -60.7334 | 60.5023 | 60.7351 | 60.6239 | -60.9434 | -0.084709 | -0.038633 | 0.073501 | -0.039836 | 0.044873 | -0.092453 | -0.046682 | -0.25764 | -0.21544 | 0.014293 | -0.047684 | 0.20995 | 0.01736 | -0.093904 | 121.3649 | 121.311 | 121.3568 | 60.7055 | -121.4882 | 121.1881 | 121.4209 | 121.3096 | 60.7044 | -121.6611
99.1094 | 121.5225 | -60.7864 | 60.6903 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.067767 | -0.0082196 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060552 | 0.022961 | 0.056368 | -60.6031 | 0.019721 | -60.7256 | 60.6837 | 60.6207 | 60.6711 | -60.775 | -60.6669 | 0.009516 | -60.738 | 60.5023 | 60.7306 | 60.6239 | -60.9434 | 0.01142 | -0.00659 | 0.18336 | 0.060872 | 0.049452 | -0.069567 | -0.019217 | -0.15693 | -0.18798 | 0.11958 | 0.048445 | 0.20537 | 0.040246 | -0.066439 | 121.4702 | 121.4072 | 121.4575 | 60.8062 | -121.4653 | 121.2888 | 121.517 | 121.4103 | 60.796 | -121.6337
100.8438 | 121.5225 | -60.7452 | 60.7315 | 1.4211e-13 | -0.0093289 | 0.0022072 | 0.067554 | -0.0084334 | 0.059967 | 0.015566 | -0.0016621 | -0.00064099 | 0.060766 | 0.022748 | 0.056368 | -60.6168 | 0.019721 | -60.721 | 60.67 | 60.6207 | 60.6665 | -60.7704 | -60.6669 | 0.014095 | -60.7288 | 60.4978 | 60.7306 | 60.6239 | -60.9479 | -0.0252 | -0.061523 | 0.12843 | 0.024251 | 0.049451 | -0.11077 | -0.064993 | -0.20271 | -0.23375 | 0.078381 | 0.016404 | 0.21911 | -0.000952 | -0.10764 | 121.4152 | 121.366 | 121.4118 | 60.765 | -121.5019 | 121.243 | 121.4758 | 121.3691 | 60.7593 | -121.6795
102.5781 | 121.582 | -60.7498 | 60.6812 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.067554 | -0.008006 | 0.06018 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.022534 | 0.056368 | -60.6031 | 0.019721 | -60.7301 | 60.6791 | 60.6207 | 60.6665 | -60.775 | -60.6669 | 0.014095 | -60.7288 | 60.4978 | 60.7397 | 60.633 | -60.9388 | -0.025201 | -0.002012 | 0.14674 | 0.019673 | 0.044874 | -0.060411 | -0.014639 | -0.18897 | -0.1834 | 0.082959 | 0.020982 | 0.20995 | 0.05856 | -0.048125 | 121.429 | 121.3706 | 121.4163 | 60.7695 | -121.4562 | 121.2476 | 121.4895 | 121.3828 | 60.7639 | -121.6199
104.25 | 121.6507 | -60.6995 | 60.7315 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.067981 | -0.0082196 | 0.059967 | 0.015566 | -0.0012349 | -0.00064099 | 0.060979 | 0.022961 | 0.056368 | -60.6031 | 0.019721 | -60.7256 | 60.6746 | 60.6299 | 60.6711 | -60.7704 | -60.6669 | 0.009516 | -60.7243 | 60.5115 | 60.7397 | 60.633 | -60.9525 | -0.070976 | -0.056945 | 0.09639 | -0.026103 | 0.044873 | -0.10161 | -0.060415 | -0.25306 | -0.22002 | 0.032605 | -0.024794 | 0.22827 | 0.008206 | -0.098479 | 121.374 | 121.3294 | 121.3706 | 60.7192 | -121.5019 | 121.211 | 121.4392 | 121.3325 | 60.709 | -121.684
105.9844 | 121.6232 | -60.6857 | 60.7315 | 1.4211e-13 | -0.0095427 | 0.0022072 | 0.067554 | -0.0082196 | 0.060394 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060766 | 0.022961 | 0.056368 | -60.6122 | 0.028878 | -60.721 | 60.6746 | 60.6207 | 60.6711 | -60.7704 | -60.6669 | 0.018674 | -60.7288 | 60.5023 | 60.7306 | 60.6284 | -60.9525 | -0.084709 | -0.056945 | 0.073501 | -0.035258 | 0.049451 | -0.11077 | -0.060415 | -0.2668 | -0.22918 | 0.018872 | -0.043105 | 0.22369 | -0.000952 | -0.10306 | 121.3603 | 121.3065 | 121.3568 | 60.7146 | -121.5019 | 121.1881 | 121.4163 | 121.3142 | 60.7044 | -121.684
107.7188 | 121.6415 | -60.7086 | 60.7224 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067767 | -0.008006 | 0.06018 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.023175 | 0.056368 | -60.6077 | 0.028878 | -60.7301 | 60.6837 | 60.6207 | 60.6665 | -60.7796 | -60.6623 | 0.018674 | -60.7334 | 60.5023 | 60.7351 | 60.6239 | -60.9479 | -0.070979 | -0.038633 | 0.10097 | -0.021526 | 0.049453 | -0.10161 | -0.055838 | -0.23933 | -0.22002 | 0.046339 | -0.024796 | 0.21453 | 0.012782 | -0.098482 | 121.3923 | 121.3294 | 121.3751 | 60.7375 | -121.5019 | 121.2109 | 121.4438 | 121.3325 | 60.7273 | -121.6703
109.4531 | 121.6232 | -60.6903 | 60.7178 | 1.4211e-13 | -0.0095427 | 0.0026346 | 0.067981 | -0.008006 | 0.060394 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060979 | 0.022534 | 0.056368 | -60.6077 | 0.0243 | -60.721 | 60.6837 | 60.6253 | 60.6711 | -60.775 | -60.6714 | 0.018674 | -60.7288 | 60.4978 | 60.7397 | 60.6284 | -60.9479 | -0.08471 | -0.034055 | 0.082657 | -0.03068 | 0.05403 | -0.092453 | -0.046682 | -0.25764 | -0.22002 | 0.018871 | -0.038527 | 0.21911 | 0.021939 | -0.089325 | 121.374 | 121.3156 | 121.3614 | 60.7146 | -121.4928 | 121.1881 | 121.43 | 121.3188 | 60.709 | -121.6657
111.125 | 121.5179 | -60.7819 | 60.6995 | 1.4211e-13 | -0.0093289 | 0.0022072 | 0.067767 | -0.0082196 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.022748 | 0.056582 | -60.6077 | 0.015142 | -60.7256 | 60.6791 | 60.6253 | 60.6757 | -60.7659 | -60.6669 | 0.009516 | -60.7334 | 60.5023 | 60.7489 | 60.6239 | -60.9479 | 0.016 | -0.020323 | 0.17421 | 0.056294 | 0.040294 | -0.074143 | -0.023793 | -0.16609 | -0.19713 | 0.115 | 0.048446 | 0.21453 | 0.049406 | -0.075594 | 121.461 | 121.4072 | 121.4575 | 60.797 | -121.4653 | 121.2842 | 121.5307 | 121.4057 | 60.7914 | -121.6474
112.8594 | 121.6415 | -60.7315 | 60.6903 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067554 | -0.008006 | 0.059967 | 0.015566 | -0.0010211 | -0.00064099 | 0.060766 | 0.023175 | 0.056368 | -60.6122 | 0.019721 | -60.721 | 60.6791 | 60.6299 | 60.6711 | -60.7659 | -60.6669 | 0.014095 | -60.7288 | 60.5023 | 60.7397 | 60.633 | -60.9434 | -0.034354 | -0.011168 | 0.11928 | 0.010518 | 0.044872 | -0.060409 | -0.019217 | -0.21186 | -0.18798 | 0.064648 | 0.002671 | 0.21453 | 0.049404 | -0.057281 | 121.4106 | 121.3614 | 121.4026 | 60.7512 | -121.4562 | 121.2338 | 121.4712 | 121.3645 | 60.7456 | -121.6337
114.5781 | 121.6507 | -60.6857 | 60.6995 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.06734 | -0.0082196 | 0.06018 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060979 | 0.022961 | 0.056582 | -60.6031 | 0.019721 | -60.721 | 60.6883 | 60.6207 | 60.6757 | -60.775 | -60.6714 | 0.018674 | -60.7334 | 60.4932 | 60.7489 | 60.6284 | -60.9479 | -0.089288 | -0.011166 | 0.082657 | -0.035258 | 0.05403 | -0.078722 | -0.023793 | -0.26222 | -0.20629 | 0.014293 | -0.047684 | 0.21453 | 0.049406 | -0.071015 | 121.374 | 121.3065 | 121.3614 | 60.7055 | -121.4745 | 121.1789 | 121.4346 | 121.3142 | 60.7044 | -121.6474
116.2969 | 121.55 | -60.7727 | 60.704 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.06734 | -0.0084334 | 0.059967 | 0.00030522 | -0.0012349 | -0.00085459 | 0.060766 | 0.022961 | 0.056368 | -60.6077 | 0.019721 | -60.7164 | 60.6746 | 60.6253 | 60.6711 | -60.7659 | -60.6623 | 0.014095 | -60.7288 | 60.4978 | 60.7397 | 60.6239 | -60.9388 | 0.006845 | -0.02948 | 0.16505 | 0.056296 | 0.049451 | -0.078721 | -0.03295 | -0.16608 | -0.20629 | 0.11043 | 0.04387 | 0.20995 | 0.035671 | -0.080172 | 121.4473 | 121.398 | 121.4438 | 60.7924 | -121.4699 | 121.2705 | 121.5124 | 121.3966 | 60.7868 | -121.6428
118.0312 | 121.6003 | -60.7315 | 60.7132 | 1.4211e-13 | -0.0093289 | 0.002421 | 0.067554 | -0.008006 | 0.060394 | 0.015566 | -0.0016621 | -0.00064099 | 0.060979 | 0.022961 | 0.056368 | -60.6031 | 0.0243 | -60.721 | 60.6746 | 60.6253 | 60.6802 | -60.775 | -60.6714 | 0.014095 | -60.7243 | 60.5023 | 60.7351 | 60.6284 | -60.9525 | -0.043512 | -0.038635 | 0.12843 | 0.010518 | 0.05403 | -0.087876 | -0.032948 | -0.22102 | -0.21087 | 0.060069 | 0.007249 | 0.22827 | 0.021937 | -0.084748 | 121.4061 | 121.3568 | 121.4118 | 60.7558 | -121.4882 | 121.2338 | 121.4666 | 121.36 | 60.7456 | -121.6657
119.7031 | 121.5591 | -60.759 | 60.672 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067767 | -0.0084334 | 0.06018 | 0.015566 | -0.0016621 | -0.00064099 | 0.060979 | 0.022961 | 0.056368 | -60.6122 | 0.015142 | -60.7256 | 60.6791 | 60.6345 | 60.6619 | -60.775 | -60.6623 | 0.023253 | -60.7288 | 60.4978 | 60.7443 | 60.6239 | -60.9434 | -0.016046 | 0.007143 | 0.14674 | 0.033406 | 0.049452 | -0.037519 | -0.010063 | -0.1844 | -0.17424 | 0.096693 | 0.030137 | 0.21453 | 0.072293 | -0.048128 | 121.4381 | 121.3935 | 121.4209 | 60.7741 | -121.447 | 121.2567 | 121.5033 | 121.3828 | 60.7822 | -121.6154
121.4219 | 121.5454 | -60.759 | 60.6857 | 1.4211e-13 | -0.0095427 | 0.0022072 | 0.067767 | -0.008006 | 0.060394 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060979 | 0.023389 | 0.056795 | -60.6077 | 0.028878 | -60.721 | 60.6746 | 60.6253 | 60.6757 | -60.7659 | -60.6669 | 0.014095 | -60.7243 | 60.5069 | 60.7397 | 60.6284 | -60.9434 | -0.006888 | -0.011169 | 0.15132 | 0.037984 | 0.044872 | -0.06041 | -0.01006 | -0.1844 | -0.17882 | 0.092114 | 0.034715 | 0.21911 | 0.053982 | -0.057282 | 121.4335 | 121.3843 | 121.4346 | 60.7878 | -121.4516 | 121.2659 | 121.4987 | 121.3874 | 60.7731 | -121.6291
123.0938 | 121.5088 | -60.759 | 60.7407 | 1.4211e-13 | -0.0095427 | 0.0019936 | 0.067554 | -0.0082196 | 0.06018 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060979 | 0.022961 | 0.056582 | -60.6122 | 0.0243 | -60.7164 | 60.6837 | 60.6253 | 60.6757 | -60.775 | -60.6714 | 0.018674 | -60.7334 | 60.4978 | 60.7443 | 60.6284 | -60.9388 | -0.016046 | -0.056944 | 0.14674 | 0.042563 | 0.058609 | -0.11534 | -0.064992 | -0.17982 | -0.24291 | 0.087535 | 0.025558 | 0.20537 | 0.003628 | -0.11221 | 121.4427 | 121.3843 | 121.4346 | 60.7833 | -121.5157 | 121.2567 | 121.5033 | 121.3874 | 60.7776 | -121.6795
124.8125 | 121.5134 | -60.7498 | 60.7086 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067767 | -0.008006 | 0.06018 | -0.0073253 | -0.0012349 | -0.00042739 | 0.060766 | 0.022961 | 0.056368 | -60.6077 | 0.0243 | -60.7256 | 60.6837 | 60.6253 | 60.6802 | -60.775 | -60.676 | 0.014095 | -60.7288 | 60.5023 | 60.7397 | 60.6239 | -60.9525 | -0.025201 | -0.0249 | 0.14217 | 0.024251 | 0.049452 | -0.083298 | -0.02837 | -0.20271 | -0.20629 | 0.073802 | 0.020982 | 0.22369 | 0.031094 | -0.084749 | 121.4335 | 121.3751 | 121.4301 | 60.7741 | -121.4836 | 121.2521 | 121.4895 | 121.3737 | 60.7639 | -121.6611
126.5312 | 121.5729 | -60.7773 | 60.704 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067554 | -0.0082196 | 0.06018 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.023175 | 0.056368 | -60.6031 | 0.019721 | -60.721 | 60.6791 | 60.6162 | 60.6665 | -60.7659 | -60.6623 | 0.023253 | -60.7288 | 60.5023 | 60.7351 | 60.6239 | -60.9434 | 0.011423 | -0.024901 | 0.17421 | 0.056295 | 0.044872 | -0.087879 | -0.037528 | -0.16609 | -0.20171 | 0.115 | 0.048448 | 0.21453 | 0.031092 | -0.080172 | 121.4564 | 121.3934 | 121.4438 | 60.797 | -121.4699 | 121.2796 | 121.5124 | 121.4012 | 60.8005 | -121.6474
128.2031 | 121.5546 | -60.7498 | 60.6995 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067981 | -0.008006 | 0.06018 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060766 | 0.023175 | 0.056155 | -60.6031 | 0.019721 | -60.7164 | 60.6791 | 60.6299 | 60.6711 | -60.7704 | -60.6669 | 0.014095 | -60.7288 | 60.4978 | 60.7397 | 60.6147 | -60.9434 | -0.020622 | -0.020323 | 0.14674 | 0.033408 | 0.05403 | -0.069564 | -0.028372 | -0.19355 | -0.20171 | 0.082959 | 0.020982 | 0.21453 | 0.040249 | -0.084751 | 121.429 | 121.3797 | 121.4209 | 60.7695 | -121.4699 | 121.2476 | 121.4895 | 121.3645 | 60.7639 | -121.6428
129.9219 | 121.5591 | -60.7315 | 60.6949 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067554 | -0.008647 | 0.059967 | 0.00030522 | -0.0012349 | -0.0010684 | 0.060979 | 0.022961 | 0.056795 | -60.6077 | 0.0243 | -60.721 | 60.6791 | 60.6253 | 60.6711 | -60.7704 | -60.6669 | 0.014095 | -60.7243 | 60.5023 | 60.7351 | 60.6193 | -60.9342 | -0.038933 | -0.015745 | 0.12386 | 0.010518 | 0.049451 | -0.069565 | -0.023794 | -0.2027 | -0.19255 | 0.064648 | 0.007249 | 0.20995 | 0.040248 | -0.075594 | 121.4106 | 121.3568 | 121.4026 | 60.7558 | -121.4653 | 121.2338 | 121.4666 | 121.3508 | 60.7456 | -121.6291
131.5938 | 121.5591 | -60.7498 | 60.672 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.067554 | -0.0084334 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060552 | 0.022961 | 0.056155 | -60.6031 | 0.019721 | -60.721 | 60.67 | 60.6299 | 60.6711 | -60.7704 | -60.6669 | 0.014095 | -60.7334 | 60.4978 | 60.7351 | 60.6239 | -60.9434 | -0.020622 | -0.002014 | 0.14674 | 0.028829 | 0.049451 | -0.042098 | -0.000906 | -0.19355 | -0.17424 | 0.082959 | 0.016403 | 0.20995 | 0.063136 | -0.048128 | 121.4198 | 121.3797 | 121.4209 | 60.7695 | -121.4424 | 121.2476 | 121.4849 | 121.3737 | 60.7639 | -121.6154
133.3281 | 121.6187 | -60.7178 | 60.6857 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067767 | -0.008006 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060979 | 0.023175 | 0.056582 | -60.6122 | 0.0243 | -60.721 | 60.67 | 60.6207 | 60.6711 | -60.775 | -60.6669 | 0.018674 | -60.7334 | 60.4978 | 60.7443 | 60.6284 | -60.9388 | -0.057245 | -0.015747 | 0.10554 | -0.003215 | 0.05403 | -0.064989 | -0.014639 | -0.22102 | -0.18798 | 0.050915 | -0.015641 | 0.20537 | 0.05856 | -0.057282 | 121.3878 | 121.3385 | 121.3889 | 60.7421 | -121.4607 | 121.2155 | 121.4621 | 121.3462 | 60.7364 | -121.6245
135.0625 | 121.6232 | -60.7544 | 60.6812 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067767 | -0.008006 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060979 | 0.023175 | 0.056582 | -60.6077 | 0.010564 | -60.7256 | 60.6791 | 60.6207 | 60.6711 | -60.7704 | -60.6669 | 0.023253 | -60.7288 | 60.4978 | 60.7397 | 60.6284 | -60.9434 | -0.016044 | -0.002012 | 0.14674 | 0.028829 | 0.044873 | -0.060411 | -0.010061 | -0.18897 | -0.1834 | 0.087537 | 0.02556 | 0.21453 | 0.05856 | -0.052704 | 121.4335 | 121.3751 | 121.4255 | 60.765 | -121.4516 | 121.2521 | 121.4941 | 121.3828 | 60.7776 | -121.6245
136.7812 | 121.5134 | -60.7773 | 60.7178 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.067554 | -0.0084334 | 0.059539 | 0.00030522 | -0.0012349 | -0.00064099 | 0.060552 | 0.023175 | 0.055941 | -60.5985 | 0.019721 | -60.7164 | 60.6791 | 60.6299 | 60.6711 | -60.7704 | -60.6623 | 0.018674 | -60.7243 | 60.5023 | 60.7397 | 60.6193 | -60.9388 | 0.006844 | -0.038633 | 0.17879 | 0.060874 | 0.05403 | -0.087874 | -0.046682 | -0.16151 | -0.21544 | 0.115 | 0.053026 | 0.21453 | 0.021939 | -0.098482 | 121.4564 | 121.4072 | 121.4484 | 60.797 | -121.4882 | 121.2796 | 121.517 | 121.3966 | 60.796 | -121.6566
138.5156 | 121.6599 | -60.7086 | 60.6903 | 1.4211e-13 | -0.0099699 | 0.0026346 | 0.067767 | -0.008006 | 0.06018 | 0.015566 | -0.0016621 | -0.00064099 | 0.060979 | 0.023175 | 0.056582 | -60.6077 | 0.019721 | -60.7164 | 60.6746 | 60.6253 | 60.6802 | -60.7796 | -60.6623 | 0.018674 | -60.7243 | 60.4886 | 60.7397 | 60.6284 | -60.9434 | -0.070979 | -0.015747 | 0.10097 | -0.007791 | 0.063188 | -0.064988 | -0.01006 | -0.23475 | -0.20171 | 0.046339 | -0.015639 | 0.21911 | 0.049404 | -0.06186 | 121.3832 | 121.3339 | 121.3889 | 60.7283 | -121.4699 | 121.1972 | 121.4483 | 121.3371 | 60.7273 | -121.6337
140.1875 | 121.5042 | -60.7819 | 60.7315 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067767 | -0.0082196 | 0.06018 | 0.015566 | -0.0016621 | -0.00064099 | 0.060338 | 0.023175 | 0.056368 | -60.6077 | 0.019721 | -60.721 | 60.6791 | 60.6207 | 60.6757 | -60.7704 | -60.6669 | 0.018674 | -60.7197 | 60.5023 | 60.7351 | 60.6193 | -60.9479 | 0.011421 | -0.052366 | 0.17421 | 0.060872 | 0.049451 | -0.11077 | -0.055836 | -0.16609 | -0.22918 | 0.115 | 0.062182 | 0.22827 | 0.003627 | -0.11222 | 121.461 | 121.4026 | 121.4575 | 60.8016 | -121.5019 | 121.2842 | 121.517 | 121.4012 | 60.8005 | -121.6795
141.9219 | 121.5134 | -60.7727 | 60.6766 | 1.4211e-13 | -0.0095427 | 0.002421 | 0.06734 | -0.008006 | 0.06018 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.023175 | 0.056155 | -60.6031 | 0.019721 | -60.721 | 60.6746 | 60.6207 | 60.6665 | -60.775 | -60.6669 | 0.014095 | -60.7197 | 60.4932 | 60.7397 | 60.6239 | -60.9342 | -0.002313 | -0.002014 | 0.16963 | 0.051717 | 0.05403 | -0.055834 | -0.010062 | -0.16151 | -0.1834 | 0.10585 | 0.053027 | 0.21453 | 0.063137 | -0.052706 | 121.4473 | 121.3934 | 121.4392 | 60.7924 | -121.4516 | 121.2659 | 121.5124 | 121.3966 | 60.7868 | -121.6108
143.6719 | 121.6141 | -60.6949 | 60.6995 | 1.4211e-13 | -0.0095427 | 0.0022072 | 0.067554 | -0.0082196 | 0.059967 | 0.0079357 | -0.0012349 | -0.00064099 | 0.060766 | 0.023175 | 0.056368 | -60.6031 | 0.019721 | -60.721 | 60.6883 | 60.6253 | 60.6757 | -60.7704 | -60.6623 | 0.014095 | -60.7243 | 60.5115 | 60.7397 | 60.6284 | -60.9388 | -0.075554 | -0.011166 | 0.091812 | -0.026103 | 0.049451 | -0.074143 | -0.023793 | -0.2439 | -0.18798 | 0.032606 | -0.029372 | 0.21453 | 0.040249 | -0.071015 | 121.3832 | 121.3202 | 121.3706 | 60.7146 | -121.4699 | 121.2064 | 121.4346 | 121.3233 | 60.709 | -121.6383
145.3594 | 121.637 | -60.6674 | 60.7315 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067981 | -0.008006 | 0.060394 | 0.015566 | -0.0016621 | -0.00064099 | 0.060766 | 0.023175 | 0.056368 | -60.6031 | 0.0243 | -60.721 | 60.6883 | 60.6253 | 60.6802 | -60.775 | -60.6623 | 0.018674 | -60.7288 | 60.5069 | 60.7351 | 60.6239 | -60.9434 | -0.1076 | -0.043209 | 0.064346 | -0.053569 | 0.05403 | -0.10619 | -0.051258 | -0.27595 | -0.2246 | 0.00514 | -0.061416 | 0.21453 | 0.003627 | -0.10764 | 121.3557 | 121.2927 | 121.3477 | 60.6917 | -121.5065 | 121.1743 | 121.4026 | 121.2913 | 60.6861 | -121.6749
147.0156 | 121.5088 | -60.791 | 60.7086 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.067126 | -0.008006 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060979 | 0.023389 | 0.056368 | -60.5985 | 0.015142 | -60.721 | 60.6791 | 60.6253 | 60.6711 | -60.775 | -60.6623 | 0.014095 | -60.7288 | 60.5023 | 60.7397 | 60.6284 | -60.9434 | 0.015998 | -0.029478 | 0.19252 | 0.070028 | 0.05403 | -0.083298 | -0.037527 | -0.15235 | -0.20629 | 0.12874 | 0.062181 | 0.21453 | 0.031094 | -0.08017 | 121.4702 | 121.4163 | 121.4621 | 60.8062 | -121.4836 | 121.2933 | 121.5307 | 121.4195 | 60.8051 | -121.652
148.7031 | 121.5408 | -60.7315 | 60.7178 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067767 | -0.0084334 | 0.059753 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060766 | 0.022961 | 0.056368 | -60.6031 | 0.019721 | -60.7256 | 60.6837 | 60.6345 | 60.6711 | -60.775 | -60.6669 | 0.018674 | -60.7243 | 60.5069 | 60.7351 | 60.6239 | -60.9479 | -0.043512 | -0.034055 | 0.12843 | 0.00594 | 0.049452 | -0.083295 | -0.046682 | -0.21644 | -0.21086 | 0.064648 | 0.007249 | 0.22369 | 0.01736 | -0.093904 | 121.4152 | 121.366 | 121.4026 | 60.7512 | -121.4928 | 121.2384 | 121.4666 | 121.3554 | 60.7502 | -121.6657
150.4219 | 121.5912 | -60.7636 | 60.6903 | 1.4211e-13 | -0.0095427 | 0.0022072 | 0.067767 | -0.008006 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.022961 | 0.056582 | -60.6031 | 0.019721 | -60.7164 | 60.6791 | 60.6162 | 60.6711 | -60.775 | -60.6669 | 0.018674 | -60.7243 | 60.4978 | 60.7397 | 60.6239 | -60.9434 | -0.011468 | -0.011168 | 0.16048 | 0.047141 | 0.058609 | -0.074146 | -0.019217 | -0.17982 | -0.19256 | 0.096692 | 0.039293 | 0.21911 | 0.049404 | -0.066439 | 121.4427 | 121.3797 | 121.4346 | 60.7833 | -121.4653 | 121.2613 | 121.5033 | 121.3874 | 60.7822 | -121.6337
152.0781 | 121.637 | -60.7361 | 60.6628 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067767 | -0.008006 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060552 | 0.023175 | 0.056155 | -60.6031 | 0.0243 | -60.7164 | 60.6791 | 60.6299 | 60.6757 | -60.775 | -60.6714 | 0.014095 | -60.7243 | 60.4932 | 60.7351 | 60.6284 | -60.9434 | -0.038934 | 0.016298 | 0.13301 | 0.019675 | 0.058609 | -0.032943 | 0.012828 | -0.20728 | -0.16967 | 0.064647 | 0.011827 | 0.21911 | 0.072291 | -0.034394 | 121.4152 | 121.366 | 121.4118 | 60.7604 | -121.4379 | 121.2293 | 121.4712 | 121.3645 | 60.7502 | -121.6062
153.75 | 121.5729 | -60.7498 | 60.7086 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067554 | -0.008006 | 0.059753 | 0.0079357 | -0.0016621 | -0.00085459 | 0.060766 | 0.023389 | 0.056582 | -60.6031 | 0.0243 | -60.721 | 60.6883 | 60.6207 | 60.6802 | -60.7659 | -60.6669 | 0.009516 | -60.7288 | 60.5069 | 60.7397 | 60.6147 | -60.9434 | -0.016043 | -0.020321 | 0.14674 | 0.028829 | 0.044872 | -0.087877 | -0.02837 | -0.19355 | -0.20171 | 0.082959 | 0.020982 | 0.21453 | 0.031094 | -0.093906 | 121.4381 | 121.3706 | 121.4301 | 60.7741 | -121.4745 | 121.2567 | 121.4895 | 121.3645 | 60.7593 | -121.652
155.4688 | 121.6187 | -60.7132 | 60.7269 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067554 | -0.0082196 | 0.060608 | 0.00030522 | -0.0012349 | -0.00042739 | 0.060766 | 0.023602 | 0.056368 | -60.6077 | 0.0243 | -60.7164 | 60.6837 | 60.6299 | 60.6757 | -60.7796 | -60.6669 | 0.018674 | -60.7334 | 60.5069 | 60.7397 | 60.633 | -60.9388 | -0.066401 | -0.043211 | 0.10555 | -0.003213 | 0.063188 | -0.09703 | -0.051259 | -0.22559 | -0.22002 | 0.046338 | -0.020218 | 0.20537 | 0.012783 | -0.093902 | 121.3969 | 121.3431 | 121.3889 | 60.7375 | -121.5065 | 121.2201 | 121.4529 | 121.3462 | 60.7319 | -121.6657
157.125 | 121.5591 | -60.7498 | 60.6903 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.067981 | -0.0082196 | 0.06018 | 0.00030522 | -0.0014485 | -0.00085459 | 0.060552 | 0.023389 | 0.056368 | -60.5985 | 0.015142 | -60.7118 | 60.6837 | 60.6253 | 60.6665 | -60.7796 | -60.6669 | 0.018674 | -60.7243 | 60.4932 | 60.7351 | 60.6239 | -60.9434 | -0.02978 | -0.00659 | 0.15132 | 0.037986 | 0.067766 | -0.064988 | -0.023795 | -0.19355 | -0.19713 | 0.082959 | 0.02556 | 0.21911 | 0.044825 | -0.066439 | 121.4335 | 121.3751 | 121.4163 | 60.765 | -121.4699 | 121.243 | 121.4849 | 121.3737 | 60.7685 | -121.6337
159.2812 | 121.6553 | -60.7224 | 60.6537 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.06734 | -0.0077924 | 0.060394 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.023389 | 0.056368 | -60.6031 | 0.015142 | -60.7164 | 60.6837 | 60.6253 | 60.6757 | -60.7659 | -60.6623 | 0.023253 | -60.7243 | 60.4978 | 60.7214 | 60.6193 | -60.9434 | -0.043509 | 0.030031 | 0.11928 | 0.005942 | 0.049451 | -0.028367 | 0.021983 | -0.22102 | -0.15593 | 0.060072 | -0.001906 | 0.21911 | 0.06771 | -0.034396 | 121.4061 | 121.3477 | 121.398 | 60.7375 | -121.4195 | 121.2201 | 121.4437 | 121.3416 | 60.7456 | -121.5971
161.1719 | 121.6095 | -60.704 | 60.7178 | 1.4211e-13 | -0.0095427 | 0.0022072 | 0.067767 | -0.008006 | 0.059967 | 0.0079357 | -0.0018757 | -0.00064099 | 0.060979 | 0.023389 | 0.056368 | -60.6031 | 0.015142 | -60.7164 | 60.6791 | 60.6253 | 60.6757 | -60.775 | -60.6669 | 0.023253 | -60.7243 | 60.5023 | 60.7306 | 60.6193 | -60.9571 | -0.070977 | -0.038633 | 0.10097 | -0.012368 | 0.058609 | -0.092453 | -0.042103 | -0.25306 | -0.21544 | 0.037183 | -0.020216 | 0.23285 | 0.012781 | -0.098482 | 121.3832 | 121.3294 | 121.3797 | 60.7192 | -121.4928 | 121.2064 | 121.4346 | 121.3233 | 60.7273 | -121.6749
162.8906 | 121.5729 | -60.7498 | 60.6903 | 1.4211e-13 | -0.0099699 | 0.0022072 | 0.067554 | -0.0077924 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060552 | 0.023389 | 0.056368 | -60.5985 | 0.028878 | -60.721 | 60.6654 | 60.6253 | 60.6757 | -60.7704 | -60.6669 | 0.018674 | -60.7288 | 60.4932 | 60.7306 | 60.6239 | -60.9388 | -0.020622 | -0.024903 | 0.15132 | 0.028829 | 0.049451 | -0.064988 | -0.014638 | -0.18897 | -0.19713 | 0.082959 | 0.020982 | 0.20995 | 0.040246 | -0.066439 | 121.4152 | 121.3751 | 121.4255 | 60.7787 | -121.4607 | 121.243 | 121.4804 | 121.3737 | 60.7685 | -121.6291
164.5469 | 121.6415 | -60.6812 | 60.6903 | 1.4211e-13 | -0.0099699 | 0.0026346 | 0.06734 | -0.008006 | 0.06018 | 0.015566 | -0.0014485 | -0.00064099 | 0.060552 | 0.023175 | 0.056368 | -60.6077 | 0.0243 | -60.7164 | 60.6791 | 60.6162 | 60.6757 | -60.7704 | -60.6623 | 0.027831 | -60.7288 | 60.5069 | 60.7351 | 60.6147 | -60.9388 | -0.089287 | -0.011168 | 0.073501 | -0.035257 | 0.05403 | -0.074146 | -0.014638 | -0.25764 | -0.1834 | 0.018873 | -0.047683 | 0.20995 | 0.044825 | -0.075596 | 121.3603 | 121.2973 | 121.3568 | 60.7055 | -121.4607 | 121.1881 | 121.4163 | 121.2959 | 60.709 | -121.6291
166.2344 | 121.5225 | -60.7727 | 60.6949 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.067767 | -0.0077924 | 0.059967 | -0.0073253 | -0.0014485 | -0.00064099 | 0.060766 | 0.023389 | 0.056795 | -60.5985 | 0.010564 | -60.721 | 60.6746 | 60.6207 | 60.6711 | -60.7704 | -60.6623 | 0.023253 | -60.7334 | 60.4978 | 60.7351 | 60.6239 | -60.9434 | 0.002266 | -0.020324 | 0.17421 | 0.051717 | 0.049451 | -0.074144 | -0.023794 | -0.17066 | -0.19713 | 0.11043 | 0.039291 | 0.20995 | 0.040248 | -0.071016 | 121.4473 | 121.3934 | 121.4438 | 60.7833 | -121.4653 | 121.2705 | 121.5078 | 121.3966 | 60.796 | -121.6383
167.9062 | 121.6187 | -60.6949 | 60.7086 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067554 | -0.0075786 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.023602 | 0.056582 | -60.6077 | 0.0243 | -60.7118 | 60.6746 | 60.6253 | 60.6711 | -60.7704 | -60.6714 | 0.018674 | -60.7288 | 60.5069 | 60.7306 | 60.6193 | -60.9434 | -0.075554 | -0.034057 | 0.087234 | -0.016946 | 0.058608 | -0.083298 | -0.037527 | -0.24848 | -0.20171 | 0.023448 | -0.03395 | 0.21453 | 0.021936 | -0.089327 | 121.3694 | 121.3202 | 121.366 | 60.7192 | -121.4791 | 121.2018 | 121.4254 | 121.3142 | 60.7136 | -121.652
169.5781 | 121.6553 | -60.6766 | 60.7178 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067554 | -0.0077924 | 0.059967 | 0.0079357 | -0.0018757 | -0.00021359 | 0.060766 | 0.023602 | 0.056582 | -60.5985 | 0.015142 | -60.7164 | 60.6746 | 60.6299 | 60.6757 | -60.7704 | -60.6623 | 0.018674 | -60.7243 | 60.5069 | 60.7351 | 60.6284 | -60.9388 | -0.093864 | -0.043212 | 0.078081 | -0.039834 | 0.05403 | -0.087874 | -0.042103 | -0.26221 | -0.21086 | 0.014296 | -0.047682 | 0.21453 | 0.01736 | -0.089325 | 121.3511 | 121.3065 | 121.3522 | 60.6917 | -121.4882 | 121.1835 | 121.4117 | 121.305 | 60.6952 | -121.6566
171.25 | 121.5363 | -60.7636 | 60.7498 | 1.4211e-13 | -0.0099699 | 0.0022072 | 0.06734 | -0.0077924 | 0.059967 | 0.00030522 | -0.0016621 | -0.00085459 | 0.060552 | 0.023602 | 0.056582 | -60.6031 | 0.015142 | -60.7256 | 60.6883 | 60.6253 | 60.6757 | -60.775 | -60.6577 | 0.014095 | -60.7288 | 60.5069 | 60.7351 | 60.6193 | -60.9479 | -0.011468 | -0.06152 | 0.16048 | 0.037984 | 0.049452 | -0.1245 | -0.074147 | -0.1844 | -0.24291 | 0.10585 | 0.034715 | 0.21911 | -0.014684 | -0.13053 | 121.4518 | 121.3889 | 121.4392 | 60.7787 | -121.5248 | 121.2705 | 121.4987 | 121.3828 | 60.7776 | -121.6978
172.9219 | 121.6141 | -60.7269 | 60.6491 | 1.4211e-13 | -0.0099699 | 0.0022072 | 0.067554 | -0.0077924 | 0.06018 | 0.00030522 | -0.0014485 | -0.00064099 | 0.061193 | 0.023389 | 0.056155 | -60.5939 | 0.0243 | -60.7164 | 60.6791 | 60.6253 | 60.6802 | -60.7613 | -60.6623 | 0.018674 | -60.7243 | 60.5069 | 60.7397 | 60.6239 | -60.9388 | -0.034352 | 0.030031 | 0.13301 | 0.01052 | 0.044872 | -0.023789 | 0.031139 | -0.21186 | -0.1422 | 0.06465 | 0.002672 | 0.21453 | 0.090603 | -0.02524 | 121.4061 | 121.3522 | 121.4072 | 60.7512 | -121.4104 | 121.2338 | 121.4666 | 121.3508 | 60.7456 | -121.5879
174.625 | 121.5729 | -60.759 | 60.6903 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.06734 | -0.0082196 | 0.060394 | -0.0073253 | -0.0012349 | -0.00085459 | 0.060979 | 0.023175 | 0.055941 | -60.6031 | 0.0243 | -60.7118 | 60.6791 | 60.6299 | 60.6848 | -60.7704 | -60.6669 | 0.018674 | -60.7243 | 60.4978 | 60.7397 | 60.6239 | -60.9434 | -0.011467 | -0.011168 | 0.1559 | 0.047141 | 0.058608 | -0.060409 | -0.005481 | -0.1844 | -0.19256 | 0.092114 | 0.034715 | 0.21911 | 0.049404 | -0.066439 | 121.4381 | 121.3889 | 121.4438 | 60.7833 | -121.4607 | 121.2567 | 121.4987 | 121.3828 | 60.7776 | -121.6337
176.2812 | 121.582 | -60.672 | 60.6995 | 1.4211e-13 | -0.0097563 | 0.0019936 | 0.067767 | -0.0075786 | 0.060394 | 0.023196 | -0.0014485 | -0.00064099 | 0.060766 | 0.023602 | 0.056368 | -60.6031 | 0.019721 | -60.7164 | 60.6791 | 60.6253 | 60.6757 | -60.7704 | -60.6669 | 0.014095 | -60.7197 | 60.4978 | 60.7397 | 60.6147 | -60.9479 | -0.098442 | -0.020323 | 0.068924 | -0.044412 | 0.05403 | -0.074143 | -0.023793 | -0.27595 | -0.20171 | 0.005139 | -0.047681 | 0.22827 | 0.040249 | -0.084751 | 121.3511 | 121.2973 | 121.3477 | 60.6917 | -121.4699 | 121.1697 | 121.4117 | 121.2867 | 60.6861 | -121.6474
177.9375 | 121.5591 | -60.7636 | 60.7315 | 1.4211e-13 | -0.0099699 | 0.0019936 | 0.06734 | -0.0082196 | 0.059753 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060979 | 0.023389 | 0.056368 | -60.6031 | 0.028878 | -60.7164 | 60.6791 | 60.6253 | 60.6802 | -60.775 | -60.6669 | 0.018674 | -60.7243 | 60.4978 | 60.7306 | 60.6239 | -60.9434 | -0.011468 | -0.052366 | 0.16048 | 0.047141 | 0.058609 | -0.10619 | -0.051258 | -0.17982 | -0.23375 | 0.096692 | 0.039293 | 0.21911 | -0.000952 | -0.10764 | 121.4427 | 121.3889 | 121.4438 | 60.7924 | -121.5065 | 121.2613 | 121.4941 | 121.3874 | 60.7822 | -121.6749
179.5938 | 121.6324 | -60.6949 | 60.7178 | 1.4211e-13 | -0.0097563 | 0.0026346 | 0.06734 | -0.0077924 | 0.059967 | 0.00030522 | -0.0014485 | -0.00085459 | 0.060552 | 0.023602 | 0.056368 | -60.6031 | 0.028878 | -60.721 | 60.6791 | 60.6253 | 60.6757 | -60.7704 | -60.6669 | 0.018674 | -60.7197 | 60.5069 | 60.7351 | 60.6239 | -60.9479 | -0.075554 | -0.038633 | 0.091812 | -0.026103 | 0.049451 | -0.092453 | -0.042103 | -0.25306 | -0.21086 | 0.028027 | -0.024793 | 0.22827 | 0.01736 | -0.093904 | 121.374 | 121.3202 | 121.3706 | 60.7238 | -121.4882 | 121.2018 | 121.43 | 121.3188 | 60.7136 | -121.6657
181.25 | 121.6553 | -60.6949 | 60.7132 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067767 | -0.008006 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060552 | 0.023816 | 0.056368 | -60.5985 | 0.010564 | -60.721 | 60.6837 | 60.6299 | 60.6802 | -60.7659 | -60.6623 | 0.018674 | -60.7197 | 60.5023 | 60.7397 | 60.6284 | -60.9434 | -0.070975 | -0.029478 | 0.096391 | -0.026103 | 0.044872 | -0.083297 | -0.032948 | -0.24848 | -0.21087 | 0.032606 | -0.024793 | 0.22369 | 0.026516 | -0.084748 | 121.3786 | 121.3248 | 121.3751 | 60.7054 | -121.4791 | 121.1972 | 121.4346 | 121.3233 | 60.7136 | -121.6566
182.9062 | 121.5637 | -60.7361 | 60.6857 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067554 | -0.0077924 | 0.060394 | 0.015566 | -0.0018757 | -0.00042739 | 0.060766 | 0.023602 | 0.056155 | -60.6031 | 0.0243 | -60.7256 | 60.6746 | 60.6207 | 60.6711 | -60.7704 | -60.6669 | 0.018674 | -60.7197 | 60.4978 | 60.7397 | 60.6239 | -60.9434 | -0.034355 | -0.011169 | 0.13301 | 0.010518 | 0.044873 | -0.064989 | -0.014639 | -0.20728 | -0.18798 | 0.069226 | 0.016406 | 0.22369 | 0.053982 | -0.061861 | 121.4106 | 121.3568 | 121.4072 | 60.7604 | -121.4562 | 121.2338 | 121.4758 | 121.36 | 60.7548 | -121.6291
184.5625 | 121.582 | -60.6995 | 60.7086 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067767 | -0.008006 | 0.06018 | 0.00030522 | -0.0016621 | -0.00085459 | 0.060979 | 0.023602 | 0.056582 | -60.5985 | 0.010564 | -60.7164 | 60.6746 | 60.6253 | 60.6757 | -60.7659 | -60.6669 | 0.009516 | -60.7197 | 60.4932 | 60.7351 | 60.6193 | -60.9388 | -0.066397 | -0.034057 | 0.10097 | -0.016946 | 0.049451 | -0.083298 | -0.032948 | -0.23933 | -0.21544 | 0.032605 | -0.020215 | 0.21911 | 0.026515 | -0.089327 | 121.374 | 121.3248 | 121.3751 | 60.71 | -121.4745 | 121.1926 | 121.4346 | 121.3188 | 60.709 | -121.6474
186.2656 | 121.5546 | -60.7544 | 60.7224 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067767 | -0.008006 | 0.060394 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.023816 | 0.056582 | -60.6031 | 0.0243 | -60.721 | 60.6837 | 60.6299 | 60.6665 | -60.7613 | -60.6623 | 0.014095 | -60.7197 | 60.5069 | 60.7397 | 60.6284 | -60.9388 | -0.006886 | -0.038633 | 0.15132 | 0.033407 | 0.040293 | -0.092452 | -0.055838 | -0.18439 | -0.21544 | 0.092116 | 0.034717 | 0.21911 | 0.017361 | -0.093903 | 121.4381 | 121.3843 | 121.4209 | 60.7787 | -121.4836 | 121.2613 | 121.4941 | 121.3828 | 60.7685 | -121.6611
187.9531 | 121.6415 | -60.7178 | 60.672 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067767 | -0.0075786 | 0.06018 | 0.015566 | -0.0014485 | -0.00042739 | 0.060766 | 0.023602 | 0.056368 | -60.6031 | 0.0243 | -60.721 | 60.6746 | 60.6253 | 60.6802 | -60.775 | -60.6623 | 0.018674 | -60.7334 | 60.5023 | 60.7397 | 60.6284 | -60.9388 | -0.057245 | 0.002564 | 0.1147 | -0.003215 | 0.05403 | -0.046677 | 0.008251 | -0.22102 | -0.16967 | 0.055494 | -0.015641 | 0.20537 | 0.067715 | -0.043549 | 121.3923 | 121.3431 | 121.398 | 60.7421 | -121.447 | 121.2201 | 121.4575 | 121.3462 | 60.7364 | -121.6108
189.6094 | 121.5134 | -60.7361 | 60.7407 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067554 | -0.0075786 | 0.059967 | 0.0079357 | -0.0016621 | -0.00042739 | 0.061193 | 0.023602 | 0.056582 | -60.5939 | 0.0243 | -60.7164 | 60.6791 | 60.6253 | 60.6848 | -60.775 | -60.6577 | 0.018674 | -60.7288 | 60.5023 | 60.7397 | 60.6193 | -60.9388 | -0.038934 | -0.061522 | 0.14217 | 0.019675 | 0.058609 | -0.11534 | -0.055835 | -0.20271 | -0.23833 | 0.078383 | 0.007249 | 0.20995 | -0.00095 | -0.12137 | 121.4152 | 121.3614 | 121.4209 | 60.7604 | -121.5157 | 121.2384 | 121.4758 | 121.3554 | 60.7548 | -121.6795
191.3125 | 121.6003 | -60.7407 | 60.6445 | 1.4211e-13 | -0.0097563 | 0.002421 | 0.067767 | -0.0077924 | 0.059967 | -0.0073253 | -0.0016621 | -0.00085459 | 0.060766 | 0.023816 | 0.056582 | -60.5985 | 0.019721 | -60.721 | 60.6746 | 60.6253 | 60.6848 | -60.775 | -60.6669 | 0.014095 | -60.7151 | 60.5023 | 60.7351 | 60.6193 | -60.9479 | -0.034356 | 0.03003 | 0.14217 | 0.019674 | 0.05403 | -0.019211 | 0.040296 | -0.20728 | -0.1422 | 0.073804 | 0.025563 | 0.23285 | 0.090602 | -0.02524 | 121.4152 | 121.366 | 121.4255 | 60.7604 | -121.4195 | 121.243 | 121.4758 | 121.36 | 60.7548 | -121.5925
192.9688 | 121.5225 | -60.759 | 60.7132 | 1.4211e-13 | -0.010184 | 0.0019936 | 0.067554 | -0.0077924 | 0.06018 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.023816 | 0.056368 | -60.5939 | 0.0243 | -60.7164 | 60.6791 | 60.6299 | 60.6802 | -60.7704 | -60.6577 | 0.014095 | -60.7197 | 60.5069 | 60.7397 | 60.6193 | -60.9434 | -0.011467 | -0.034056 | 0.16506 | 0.042563 | 0.05403 | -0.083297 | -0.032948 | -0.1844 | -0.20629 | 0.10127 | 0.039294 | 0.22369 | 0.026516 | -0.093905 | 121.4381 | 121.3889 | 121.4392 | 60.7833 | -121.4836 | 121.2659 | 121.4987 | 121.3783 | 60.7731 | -121.6566
194.625 | 121.5179 | -60.7727 | 60.6812 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067554 | -0.0077924 | 0.059753 | 0.0079357 | -0.0014485 | -0.00085459 | 0.060979 | 0.023175 | 0.056368 | -60.5985 | 0.0243 | -60.7256 | 60.6746 | 60.6253 | 60.6802 | -60.7704 | -60.6623 | 0.018674 | -60.7288 | 60.5069 | 60.7397 | 60.6193 | -60.9434 | 0.002266 | -0.006591 | 0.17421 | 0.047139 | 0.044873 | -0.055832 | -0.000904 | -0.17066 | -0.17424 | 0.11043 | 0.04387 | 0.21453 | 0.05856 | -0.061861 | 121.4473 | 121.398 | 121.453 | 60.797 | -121.4516 | 121.2796 | 121.5124 | 121.392 | 60.7914 | -121.6245
196.2812 | 121.669 | -60.6949 | 60.7178 | 1.4211e-13 | -0.0099699 | 0.0019936 | 0.067981 | -0.0077924 | 0.059967 | 0.015566 | -0.0012349 | -0.00085459 | 0.060979 | 0.023602 | 0.056368 | -60.5985 | 0.0243 | -60.721 | 60.6746 | 60.6299 | 60.6848 | -60.7613 | -60.6623 | 0.009516 | -60.7197 | 60.5023 | 60.7351 | 60.6147 | -60.9434 | -0.066396 | -0.043212 | 0.096391 | -0.026103 | 0.040293 | -0.087874 | -0.032946 | -0.24848 | -0.21544 | 0.032606 | -0.024793 | 0.22369 | 0.01736 | -0.10306 | 121.3694 | 121.3248 | 121.3797 | 60.7192 | -121.4791 | 121.1972 | 121.43 | 121.3096 | 60.7044 | -121.6611
197.9375 | 121.637 | -60.7132 | 60.6857 | 1.4211e-13 | -0.0095427 | 0.0022072 | 0.067554 | -0.0077924 | 0.059967 | 0.015566 | -0.0016621 | -0.00085459 | 0.060766 | 0.023816 | 0.056582 | -60.6031 | 0.019721 | -60.721 | 60.6791 | 60.6345 | 60.6802 | -60.7659 | -60.6531 | 0.014095 | -60.7243 | 60.5069 | 60.7397 | 60.6284 | -60.9388 | -0.052664 | -0.00659 | 0.11012 | -0.007792 | 0.044872 | -0.051252 | -0.005482 | -0.22559 | -0.17882 | 0.060074 | -0.011061 | 0.21453 | 0.053982 | -0.057282 | 121.3923 | 121.3477 | 121.3934 | 60.7329 | -121.4516 | 121.2201 | 121.4529 | 121.3416 | 60.7273 | -121.6245
199.625 | 121.5317 | -60.7636 | 60.704 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.06734 | -0.008006 | 0.06018 | 0.015566 | -0.0016621 | -0.00064099 | 0.060552 | 0.023816 | 0.056582 | -60.5939 | 0.0243 | -60.7164 | 60.6746 | 60.6299 | 60.6802 | -60.7704 | -60.6531 | 0.023253 | -60.7243 | 60.5023 | 60.7351 | 60.6193 | -60.9434 | -0.006889 | -0.02948 | 0.16963 | 0.047141 | 0.05403 | -0.074142 | -0.023793 | -0.17982 | -0.20171 | 0.11043 | 0.039293 | 0.21911 | 0.031092 | -0.08475 | 121.4381 | 121.3934 | 121.4438 | 60.7878 | -121.4745 | 121.2659 | 121.4987 | 121.3828 | 60.7868 | -121.6474
201.3125 | 121.6415 | -60.6354 | 60.704 | 1.4211e-13 | -0.0097563 | 0.0022072 | 0.067554 | -0.008006 | 0.060394 | 0.0079357 | -0.0014485 | -0.00085459 | 0.060766 | 0.023389 | 0.056368 | -60.5985 | 0.0243 | -60.7256 | 60.6791 | 60.6253 | 60.6894 | -60.7659 | -60.6577 | 0.014095 | -60.7243 | 60.5023 | 60.7351 | 60.6284 | -60.9388 | -0.13048 | -0.024901 | 0.036882 | -0.09019 | 0.040294 | -0.078721 | -0.014635 | -0.30341 | -0.20171 | -0.022325 | -0.088881 | 0.21453 | 0.031092 | -0.075593 | 121.3145 | 121.2607 | 121.3248 | 60.6597 | -121.4699 | 121.1377 | 121.3705 | 121.2638 | 60.6495 | -121.6428
202.9844 | 121.4996 | -60.7636 | 60.7086 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067554 | -0.0077924 | 0.059967 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060552 | 0.023389 | 0.056368 | -60.5939 | 0.015142 | -60.7118 | 60.6791 | 60.6253 | 60.6757 | -60.7659 | -60.6669 | 0.018674 | -60.7151 | 60.4932 | 60.7351 | 60.6239 | -60.9342 | -0.00231 | -0.029478 | 0.16963 | 0.051719 | 0.054029 | -0.083298 | -0.032948 | -0.17066 | -0.21544 | 0.096692 | 0.048451 | 0.21911 | 0.026515 | -0.084749 | 121.4427 | 121.3889 | 121.4392 | 60.7787 | -121.4745 | 121.2567 | 121.4987 | 121.3874 | 60.7822 | -121.6428
204.6562 | 121.6553 | -60.6812 | 60.6995 | 1.4211e-13 | -0.0099699 | 0.002421 | 0.067767 | -0.008006 | 0.060394 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.023602 | 0.056582 | -60.5939 | 0.019721 | -60.7164 | 60.6791 | 60.6253 | 60.6802 | -60.7613 | -60.6577 | 0.027831 | -60.7197 | 60.5069 | 60.7397 | 60.6284 | -60.9434 | -0.080129 | -0.020323 | 0.087236 | -0.035257 | 0.044872 | -0.074143 | -0.019215 | -0.26222 | -0.19255 | 0.023451 | -0.038526 | 0.22369 | 0.040249 | -0.071015 | 121.3603 | 121.3065 | 121.3614 | 60.7009 | -121.4607 | 121.1881 | 121.4209 | 121.3096 | 60.709 | -121.6428
206.3438 | 121.582 | -60.6995 | 60.7132 | 1.4211e-13 | -0.010397 | 0.002421 | 0.067554 | -0.0075786 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.023602 | 0.056795 | -60.5985 | 0.015142 | -60.721 | 60.6791 | 60.6253 | 60.6848 | -60.7704 | -60.6623 | 0.023253 | -60.7197 | 60.4978 | 60.7351 | 60.6193 | -60.9434 | -0.070976 | -0.034056 | 0.10097 | -0.021525 | 0.049451 | -0.087876 | -0.028369 | -0.2439 | -0.21544 | 0.037184 | -0.020215 | 0.22369 | 0.021937 | -0.093905 | 121.3786 | 121.3248 | 121.3843 | 60.7146 | -121.4836 | 121.1972 | 121.4346 | 121.3188 | 60.7227 | -121.6566
208.0156 | 121.6461 | -60.6949 | 60.6766 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067554 | -0.0075786 | 0.06018 | -0.0073253 | -0.0014485 | -0.0010684 | 0.060552 | 0.023816 | 0.056368 | -60.5985 | 0.015142 | -60.7118 | 60.6791 | 60.6253 | 60.6848 | -60.7659 | -60.6623 | 0.018674 | -60.7243 | 60.4978 | 60.7351 | 60.6239 | -60.9388 | -0.070975 | 0.002565 | 0.096391 | -0.016946 | 0.054029 | -0.051255 | 0.008252 | -0.2439 | -0.17882 | 0.032606 | -0.029372 | 0.21453 | 0.058558 | -0.052706 | 121.374 | 121.3202 | 121.3797 | 60.71 | -121.4424 | 121.1926 | 121.43 | 121.3188 | 60.7136 | -121.6154
209.7031 | 121.637 | -60.6583 | 60.7224 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067767 | -0.0077924 | 0.059753 | -0.014956 | -0.0014485 | -0.00064099 | 0.060979 | 0.023602 | 0.056368 | -60.5893 | 0.019721 | -60.7118 | 60.6791 | 60.6345 | 60.6848 | -60.7704 | -60.6577 | 0.018674 | -60.7197 | 60.4932 | 60.7397 | 60.633 | -60.9434 | -0.11218 | -0.043211 | 0.068927 | -0.053567 | 0.058608 | -0.087873 | -0.037524 | -0.2851 | -0.22918 | 0.000563 | -0.061414 | 0.22369 | 0.017361 | -0.089324 | 121.3374 | 121.2927 | 121.3431 | 60.678 | -121.4928 | 121.1514 | 121.398 | 121.2913 | 60.6769 | -121.6657
211.375 | 121.6187 | -60.6583 | 60.7269 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067554 | -0.008006 | 0.06018 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.02403 | 0.056582 | -60.5893 | 0.010564 | -60.7164 | 60.6837 | 60.6299 | 60.6848 | -60.7659 | -60.6577 | 0.014095 | -60.7151 | 60.5023 | 60.7397 | 60.6239 | -60.9388 | -0.1076 | -0.043211 | 0.068927 | -0.058145 | 0.049451 | -0.09703 | -0.042102 | -0.28052 | -0.2246 | 0.000563 | -0.056835 | 0.22369 | 0.012783 | -0.10306 | 121.342 | 121.2882 | 121.3431 | 60.6688 | -121.4928 | 121.1606 | 121.398 | 121.2821 | 60.6724 | -121.6657
213.0625 | 121.6507 | -60.6628 | 60.6995 | 1.4211e-13 | -0.0099699 | 0.0019936 | 0.06734 | -0.0082196 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.023602 | 0.056582 | -60.5985 | 0.019721 | -60.7118 | 60.6837 | 60.6345 | 60.6802 | -60.7659 | -60.6577 | 0.018674 | -60.7197 | 60.5115 | 60.7397 | 60.6239 | -60.9342 | -0.10302 | -0.015745 | 0.064348 | -0.048989 | 0.054029 | -0.064985 | -0.019215 | -0.27137 | -0.18798 | 0.005141 | -0.056836 | 0.21453 | 0.040249 | -0.075594 | 121.3466 | 121.2973 | 121.3431 | 60.6826 | -121.4653 | 121.1743 | 121.4026 | 121.2867 | 60.6815 | -121.6337
214.7188 | 121.5042 | -60.7727 | 60.6903 | 1.4211e-13 | -0.010397 | 0.002421 | 0.067554 | -0.0075786 | 0.060394 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060979 | 0.023602 | 0.056368 | -60.5848 | 0.019721 | -60.721 | 60.6837 | 60.6299 | 60.6802 | -60.7613 | -60.6531 | 0.018674 | -60.7243 | 60.5023 | 60.7306 | 60.6239 | -60.9342 | 0.011424 | -0.00659 | 0.18795 | 0.051717 | 0.040293 | -0.060409 | -0.01006 | -0.16151 | -0.18798 | 0.11958 | 0.048448 | 0.20995 | 0.040246 | -0.066439 | 121.4564 | 121.4026 | 121.453 | 60.7924 | -121.4516 | 121.275 | 121.5033 | 121.3966 | 60.7914 | -121.6245
216.4062 | 121.4905 | -60.7636 | 60.6857 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067767 | -0.0084334 | 0.059967 | -0.0073253 | -0.0014485 | -0.00064099 | 0.060766 | 0.023816 | 0.056368 | -60.5939 | 0.015142 | -60.7118 | 60.6837 | 60.6299 | 60.6802 | -60.7613 | -60.6623 | 0.009516 | -60.7197 | 60.5069 | 60.7443 | 60.6284 | -60.9434 | 0.002269 | -0.002012 | 0.16963 | 0.051719 | 0.04945 | -0.055831 | -0.005482 | -0.17982 | -0.17882 | 0.10127 | 0.043872 | 0.22369 | 0.05856 | -0.057282 | 121.4473 | 121.3934 | 121.4438 | 60.7787 | -121.447 | 121.2705 | 121.5078 | 121.392 | 60.7731 | -121.6291
218.0625 | 121.5454 | -60.7361 | 60.7315 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.06734 | -0.008006 | 0.06018 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060552 | 0.023602 | 0.056582 | -60.5893 | 0.0243 | -60.721 | 60.6791 | 60.6391 | 60.6894 | -60.7567 | -60.6577 | 0.018674 | -60.7197 | 60.5115 | 60.7397 | 60.6239 | -60.9434 | -0.020618 | -0.052366 | 0.14675 | 0.015096 | 0.035714 | -0.092449 | -0.0421 | -0.20728 | -0.22002 | 0.078383 | 0.016406 | 0.22369 | 0.008206 | -0.10764 | 121.4152 | 121.3751 | 121.4255 | 60.7604 | -121.4882 | 121.2476 | 121.4758 | 121.36 | 60.7548 | -121.6749
219.75 | 121.5546 | -60.7407 | 60.6857 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067554 | -0.0077924 | 0.059967 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060552 | 0.023816 | 0.056368 | -60.5939 | 0.0243 | -60.7118 | 60.6883 | 60.6345 | 60.6848 | -60.7613 | -60.6577 | 0.014095 | -60.7197 | 60.5115 | 60.7443 | 60.6284 | -60.9388 | -0.020619 | 0.002567 | 0.14675 | 0.028831 | 0.04945 | -0.051252 | -0.000903 | -0.19813 | -0.17424 | 0.082961 | 0.020984 | 0.21911 | 0.05856 | -0.057282 | 121.429 | 121.3751 | 121.4255 | 60.765 | -121.447 | 121.2522 | 121.485 | 121.3691 | 60.7548 | -121.6245
221.4688 | 121.5775 | -60.6995 | 60.7086 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067767 | -0.008006 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.023602 | 0.056368 | -60.5893 | 0.019721 | -60.7118 | 60.6837 | 60.6345 | 60.6894 | -60.7567 | -60.6531 | 0.009516 | -60.7151 | 60.5115 | 60.7443 | 60.6284 | -60.9434 | -0.057239 | -0.0249 | 0.11013 | -0.012368 | 0.044871 | -0.07414 | -0.019212 | -0.2439 | -0.19713 | 0.046341 | -0.015636 | 0.22827 | 0.035672 | -0.08017 | 121.3832 | 121.3339 | 121.3889 | 60.7192 | -121.4653 | 121.211 | 121.4438 | 121.3279 | 60.709 | -121.652
223.1406 | 121.6324 | -60.6674 | 60.7224 | 1.4211e-13 | -0.010184 | 0.0019936 | 0.067554 | -0.008006 | 0.06018 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060552 | 0.023602 | 0.056582 | -60.5848 | 0.010564 | -60.7118 | 60.6883 | 60.6391 | 60.6848 | -60.7659 | -60.6577 | 0.009516 | -60.7151 | 60.5069 | 60.7397 | 60.6284 | -60.9388 | -0.098441 | -0.034054 | 0.08266 | -0.044412 | 0.054029 | -0.083294 | -0.037524 | -0.27137 | -0.21544 | 0.009718 | -0.04768 | 0.22369 | 0.017361 | -0.093903 | 121.3557 | 121.3065 | 121.3522 | 60.678 | -121.4882 | 121.1743 | 121.4071 | 121.2959 | 60.6769 | -121.6611
224.875 | 121.5912 | -60.6949 | 60.7178 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067554 | -0.0082196 | 0.059753 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060979 | 0.023389 | 0.056368 | -60.5893 | 0.015142 | -60.7118 | 60.6837 | 60.6345 | 60.6894 | -60.7659 | -60.6577 | 0.014095 | -60.7105 | 60.5069 | 60.7443 | 60.6284 | -60.9388 | -0.070975 | -0.034055 | 0.10555 | -0.016946 | 0.054029 | -0.083295 | -0.028367 | -0.2439 | -0.21086 | 0.037184 | -0.015636 | 0.22827 | 0.026517 | -0.089325 | 121.3786 | 121.3294 | 121.3843 | 60.71 | -121.4836 | 121.2018 | 121.4392 | 121.3233 | 60.709 | -121.6566
226.5781 | 121.637 | -60.6903 | 60.6766 | 1.4211e-13 | -0.010184 | 0.0026346 | 0.067767 | -0.0082196 | 0.06018 | 0.00030522 | -0.0016621 | -0.0010684 | 0.060766 | 0.023602 | 0.056155 | -60.5848 | 0.019721 | -60.7164 | 60.6883 | 60.6345 | 60.694 | -60.7475 | -60.6531 | 0.009516 | -60.7151 | 60.5069 | 60.7489 | 60.6284 | -60.9342 | -0.057236 | 0.011722 | 0.10555 | -0.026101 | 0.031135 | -0.042097 | 0.017409 | -0.2439 | -0.16967 | 0.037186 | -0.024791 | 0.21911 | 0.072294 | -0.048127 | 121.3786 | 121.3248 | 121.3843 | 60.71 | -121.4241 | 121.1972 | 121.4392 | 121.3188 | 60.6998 | -121.6108
228.25 | 121.6507 | -60.6674 | 60.7269 | 1.4211e-13 | -0.010184 | 0.002421 | 0.06734 | -0.0082196 | 0.059967 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.02403 | 0.056155 | -60.5893 | 0.0243 | -60.7164 | 60.6837 | 60.6299 | 60.6894 | -60.7521 | -60.6531 | 0.023253 | -60.7105 | 60.5206 | 60.7489 | 60.6284 | -60.9342 | -0.084704 | -0.043211 | 0.078082 | -0.04899 | 0.035714 | -0.09703 | -0.037523 | -0.26679 | -0.20629 | 0.014297 | -0.043102 | 0.22369 | 0.02194 | -0.098481 | 121.3511 | 121.2973 | 121.3568 | 60.6917 | -121.4791 | 121.1881 | 121.4163 | 121.2959 | 60.6907 | -121.6611
229.9531 | 121.6232 | -60.704 | 60.6903 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067767 | -0.0082196 | 0.060394 | -0.0073253 | -0.0014485 | -0.00042739 | 0.060552 | 0.023602 | 0.056368 | -60.5848 | 0.0243 | -60.7164 | 60.6837 | 60.6436 | 60.6894 | -60.7567 | -60.6531 | 0.009516 | -60.7105 | 60.5161 | 60.7443 | 60.6284 | -60.9342 | -0.052661 | -0.00659 | 0.11928 | -0.012368 | 0.040293 | -0.046672 | -0.000902 | -0.23017 | -0.17424 | 0.050919 | -0.00648 | 0.22369 | 0.053982 | -0.06186 | 121.3878 | 121.3477 | 121.3934 | 60.7283 | -121.447 | 121.2201 | 121.4483 | 121.3325 | 60.7136 | -121.6245
231.6406 | 121.5134 | -60.7178 | 60.7407 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067554 | -0.0084334 | 0.060394 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060766 | 0.023816 | 0.055941 | -60.5939 | 0.019721 | -60.7073 | 60.6975 | 60.6345 | 60.694 | -60.7567 | -60.6577 | 0.014095 | -60.7105 | 60.5115 | 60.7489 | 60.633 | -60.9342 | -0.038929 | -0.043209 | 0.12386 | 0.01052 | 0.049449 | -0.10618 | -0.046678 | -0.21644 | -0.22917 | 0.060072 | 0.007252 | 0.22369 | 0.008207 | -0.10764 | 121.4152 | 121.3523 | 121.4118 | 60.7375 | -121.4974 | 121.2293 | 121.4666 | 121.3508 | 60.7319 | -121.6749
233.3125 | 121.5454 | -60.7361 | 60.6949 | 1.4211e-13 | -0.010184 | 0.002421 | 0.06734 | -0.0082196 | 0.06018 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.023816 | 0.056368 | -60.5802 | 0.019721 | -60.7164 | 60.6883 | 60.6299 | 60.6894 | -60.7613 | -60.644 | 0.018674 | -60.7105 | 60.5115 | 60.7443 | 60.6284 | -60.9296 | -0.025197 | -0.006588 | 0.1559 | 0.019675 | 0.044872 | -0.064986 | -0.005479 | -0.19355 | -0.1834 | 0.09212 | 0.025563 | 0.21911 | 0.049405 | -0.066437 | 121.4244 | 121.366 | 121.4255 | 60.7558 | -121.4562 | 121.2476 | 121.4804 | 121.3645 | 60.7548 | -121.6245
234.9844 | 121.5912 | -60.7178 | 60.6995 | 1.4211e-13 | -0.010397 | 0.0019936 | 0.067981 | -0.0077924 | 0.06018 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060766 | 0.023816 | 0.056368 | -60.5848 | 0.019721 | -60.7118 | 60.6929 | 60.6391 | 60.694 | -60.7567 | -60.6394 | 0.018674 | -60.7059 | 60.5161 | 60.758 | 60.6284 | -60.9296 | -0.038929 | -0.006588 | 0.13301 | 0.005942 | 0.044871 | -0.060406 | -0.005479 | -0.21186 | -0.1834 | 0.078387 | 0.011831 | 0.22369 | 0.058563 | -0.071015 | 121.4106 | 121.3568 | 121.4118 | 60.7375 | -121.4562 | 121.2338 | 121.4758 | 121.3462 | 60.7364 | -121.6291
236.6562 | 121.5179 | -60.7407 | 60.7178 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0014485 | -0.00021359 | 0.061193 | 0.023389 | 0.055941 | -60.5848 | 0.015142 | -60.7118 | 60.6929 | 60.6436 | 60.694 | -60.7567 | -60.6531 | 0.009516 | -60.7105 | 60.5161 | 60.7489 | 60.633 | -60.9296 | -0.01604 | -0.024898 | 0.1559 | 0.028831 | 0.044871 | -0.074137 | -0.023789 | -0.18897 | -0.20171 | 0.08754 | 0.030141 | 0.21911 | 0.031096 | -0.084746 | 121.4335 | 121.3843 | 121.4346 | 60.7558 | -121.4745 | 121.2567 | 121.4895 | 121.3737 | 60.7502 | -121.6474
238.3281 | 121.5042 | -60.7315 | 60.7681 | 1.4211e-13 | -0.010397 | 0.002421 | 0.067767 | -0.0082196 | 0.06018 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.023816 | 0.056368 | -60.5893 | 0.019721 | -60.7118 | 60.6975 | 60.6436 | 60.7031 | -60.7567 | -60.644 | 0.018674 | -60.7105 | 60.5115 | 60.7489 | 60.6422 | -60.9296 | -0.025196 | -0.070674 | 0.14217 | 0.019675 | 0.044871 | -0.12449 | -0.064986 | -0.19813 | -0.25664 | 0.087542 | 0.020985 | 0.21911 | -0.019258 | -0.12594 | 121.429 | 121.3751 | 121.4346 | 60.7512 | -121.5248 | 121.243 | 121.4804 | 121.3737 | 60.7502 | -121.6978
239.9844 | 121.6232 | -60.6995 | 60.6903 | 1.4211e-13 | -0.010184 | 0.002421 | 0.067767 | -0.008006 | 0.059967 | -0.014956 | -0.0014485 | -0.00021359 | 0.060766 | 0.02403 | 0.056155 | -60.5848 | 0.010564 | -60.7118 | 60.6883 | 60.6482 | 60.6894 | -60.7521 | -60.644 | 0.018674 | -60.7059 | 60.5115 | 60.7489 | 60.6376 | -60.9296 | -0.05266 | -0.002011 | 0.1147 | -0.012368 | 0.040292 | -0.042093 | -0.000902 | -0.23017 | -0.17882 | 0.055499 | -0.006479 | 0.22369 | 0.058561 | -0.052703 | 121.3878 | 121.3477 | 121.3889 | 60.71 | -121.4424 | 121.211 | 121.4483 | 121.3371 | 60.7181 | -121.6199
241.6562 | 121.5866 | -60.6949 | 60.6995 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067767 | -0.0084334 | 0.06018 | 0.015566 | -0.0012349 | -0.00064099 | 0.060766 | 0.02403 | 0.056155 | -60.5893 | 0.019721 | -60.7073 | 60.6975 | 60.6436 | 60.6986 | -60.7521 | -60.6485 | 0.018674 | -60.7014 | 60.5161 | 60.7534 | 60.6376 | -60.9296 | -0.057238 | -0.00201 | 0.10555 | -0.012368 | 0.04487 | -0.055827 | -0.0009 | -0.23475 | -0.1834 | 0.046342 | -0.006478 | 0.22827 | 0.053985 | -0.061858 | 121.3923 | 121.3385 | 121.3934 | 60.7146 | -121.4516 | 121.211 | 121.4483 | 121.3325 | 60.7136 | -121.6291
243.3438 | 121.5591 | -60.7315 | 60.7132 | 1.4211e-13 | -0.010184 | 0.0026346 | 0.067554 | -0.008006 | 0.059967 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060979 | 0.02403 | 0.056155 | -60.5848 | 0.019721 | -60.7118 | 60.6929 | 60.6528 | 60.6986 | -60.7567 | -60.6394 | 0.014095 | -60.7105 | 60.5115 | 60.7626 | 60.6422 | -60.9251 | -0.025196 | -0.020321 | 0.14675 | 0.019675 | 0.044871 | -0.060403 | -0.014633 | -0.19355 | -0.20171 | 0.09212 | 0.020985 | 0.21453 | 0.049409 | -0.071012 | 121.4244 | 121.3843 | 121.4301 | 60.7512 | -121.4699 | 121.243 | 121.4941 | 121.3737 | 60.7456 | -121.6382
245.0312 | 121.4767 | -60.759 | 60.7361 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067554 | -0.0082196 | 0.059753 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060338 | 0.023816 | 0.056368 | -60.5802 | 0.0243 | -60.7073 | 60.6975 | 60.6436 | 60.6986 | -60.7521 | -60.6394 | 0.014095 | -60.7059 | 60.5161 | 60.758 | 60.6422 | -60.9251 | 0.006849 | -0.038631 | 0.17879 | 0.051719 | 0.04487 | -0.092448 | -0.037521 | -0.16608 | -0.22002 | 0.11959 | 0.05303 | 0.21911 | 0.021942 | -0.0939 | 121.4564 | 121.4026 | 121.4575 | 60.7833 | -121.4882 | 121.275 | 121.517 | 121.4012 | 60.7731 | -121.6611
246.7031 | 121.5546 | -60.7224 | 60.7269 | 1.4211e-13 | -0.010825 | 0.002421 | 0.067767 | -0.0084334 | 0.059967 | 0.0079357 | -0.0010211 | -0.00042739 | 0.060766 | 0.023816 | 0.056155 | -60.571 | 0.028878 | -60.7027 | 60.6975 | 60.6574 | 60.694 | -60.7475 | -60.6394 | 0.018674 | -60.6968 | 60.5206 | 60.7534 | 60.6422 | -60.9205 | -0.025193 | -0.029476 | 0.15133 | 0.019677 | 0.04487 | -0.069557 | -0.032945 | -0.19812 | -0.20629 | 0.082965 | 0.025567 | 0.22369 | 0.026519 | -0.084745 | 121.4198 | 121.3797 | 121.4163 | 60.7512 | -121.4745 | 121.243 | 121.4758 | 121.3645 | 60.741 | -121.6474
248.3906 | 121.5866 | -60.6903 | 60.7452 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067767 | -0.008006 | 0.059967 | 0.015566 | -0.0014485 | -0.00042739 | 0.060766 | 0.023602 | 0.056368 | -60.5756 | 0.0243 | -60.7027 | 60.6975 | 60.6528 | 60.7031 | -60.7475 | -60.6394 | 0.018674 | -60.6876 | 60.5206 | 60.7626 | 60.6605 | -60.9159 | -0.057236 | -0.047786 | 0.11471 | -0.012366 | 0.04487 | -0.092446 | -0.042098 | -0.22559 | -0.2246 | 0.050922 | 0.002681 | 0.22827 | 0.017366 | -0.084741 | 121.3878 | 121.3431 | 121.3934 | 60.7146 | -121.4928 | 121.211 | 121.4529 | 121.3508 | 60.709 | -121.6611
250.0938 | 121.55 | -60.7407 | 60.7361 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.06734 | -0.0082196 | 0.06018 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060979 | 0.02403 | 0.056155 | -60.5619 | 0.015142 | -60.6981 | 60.6975 | 60.6528 | 60.7031 | -60.743 | -60.6302 | 0.009516 | -60.6968 | 60.5206 | 60.7626 | 60.6376 | -60.9205 | -0.002303 | -0.038631 | 0.1788 | 0.042566 | 0.044869 | -0.083291 | -0.032943 | -0.17981 | -0.21544 | 0.11043 | 0.043878 | 0.22369 | 0.026521 | -0.098479 | 121.4381 | 121.3935 | 121.4438 | 60.7558 | -121.479 | 121.2613 | 121.5033 | 121.3783 | 60.7502 | -121.6566
251.7969 | 121.6187 | -60.7407 | 60.6903 | 1.4211e-13 | -0.010397 | 0.0026346 | 0.06734 | -0.0082196 | 0.059967 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060979 | 0.023816 | 0.056155 | -60.571 | 0.019721 | -60.6935 | 60.7066 | 60.6528 | 60.7123 | -60.7384 | -60.6302 | 0.023253 | -60.6968 | 60.5252 | 60.7626 | 60.6468 | -60.9113 | 0.002276 | 0.016302 | 0.16964 | 0.047144 | 0.044868 | -0.037515 | 0.021991 | -0.17065 | -0.16509 | 0.11043 | 0.043878 | 0.21453 | 0.072297 | -0.043546 | 121.4473 | 121.3935 | 121.453 | 60.7604 | -121.4287 | 121.2659 | 121.5033 | 121.3874 | 60.7639 | -121.6016
253.5156 | 121.6187 | -60.6537 | 60.6949 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067767 | -0.0084334 | 0.059967 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.02403 | 0.056155 | -60.5756 | 0.019721 | -60.7027 | 60.7112 | 60.6574 | 60.7077 | -60.743 | -60.6348 | 0.023253 | -60.6876 | 60.5252 | 60.7626 | 60.6559 | -60.9113 | -0.089278 | 0.016303 | 0.078085 | -0.048987 | 0.040291 | -0.037513 | 0.012835 | -0.25763 | -0.16966 | 0.01888 | -0.03394 | 0.22369 | 0.06772 | -0.038965 | 121.3649 | 121.3111 | 121.3614 | 60.6734 | -121.4378 | 121.1789 | 121.4163 | 121.3096 | 60.6769 | -121.6062
255.1875 | 121.5958 | -60.6812 | 60.7178 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.06734 | -0.0082196 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.02403 | 0.056368 | -60.5664 | 0.0243 | -60.6935 | 60.7112 | 60.6574 | 60.7123 | -60.7338 | -60.6257 | 0.009516 | -60.6876 | 60.5344 | 60.7672 | 60.6559 | -60.9159 | -0.052655 | -0.006585 | 0.11471 | -0.012366 | 0.040289 | -0.060401 | -0.005474 | -0.23474 | -0.18339 | 0.055502 | -0.006475 | 0.22827 | 0.04941 | -0.061853 | 121.3923 | 121.3385 | 121.3935 | 60.7055 | -121.4516 | 121.2155 | 121.4483 | 121.3371 | 60.6907 | -121.6337
256.875 | 121.582 | -60.6674 | 60.759 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067767 | -0.0082196 | 0.059967 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060979 | 0.02403 | 0.056155 | -60.5756 | 0.019721 | -60.6844 | 60.7112 | 60.6574 | 60.7169 | -60.7338 | -60.6257 | 0.014095 | -60.6922 | 60.5344 | 60.7672 | 60.6559 | -60.9067 | -0.066388 | -0.047784 | 0.091817 | -0.016942 | 0.049446 | -0.1016 | -0.042095 | -0.23932 | -0.22459 | 0.041769 | -0.024787 | 0.21453 | 0.008211 | -0.10305 | 121.3786 | 121.3248 | 121.3843 | 60.6871 | -121.4928 | 121.2018 | 121.4346 | 121.3233 | 60.6815 | -121.6657
258.5312 | 121.4951 | -60.7361 | 60.7498 | 1.4211e-13 | -0.010611 | 0.002421 | 0.067767 | -0.008006 | 0.059753 | 0.015566 | -0.0012349 | -0.00042739 | 0.060766 | 0.023602 | 0.056368 | -60.5619 | 0.019721 | -60.6935 | 60.7203 | 60.6665 | 60.7169 | -60.743 | -60.6257 | 0.014095 | -60.6922 | 60.539 | 60.7718 | 60.6651 | -60.9113 | -0.006881 | -0.029472 | 0.17422 | 0.042566 | 0.049447 | -0.083287 | -0.03294 | -0.17523 | -0.21086 | 0.11043 | 0.043878 | 0.21911 | 0.021945 | -0.08474 | 121.4564 | 121.4026 | 121.453 | 60.7558 | -121.4928 | 121.275 | 121.5078 | 121.4012 | 60.7502 | -121.6611
260.2188 | 121.5866 | -60.6445 | 60.7315 | 1.4211e-13 | -0.010611 | 0.0022072 | 0.067554 | -0.0082196 | 0.059967 | 0.00030522 | -0.0018757 | -0.00064099 | 0.060552 | 0.023816 | 0.056155 | -60.5664 | 0.028878 | -60.6889 | 60.7158 | 60.6665 | 60.7123 | -60.7384 | -60.6211 | 0.014095 | -60.683 | 60.5344 | 60.7626 | 60.6605 | -60.9113 | -0.093855 | -0.015739 | 0.078086 | -0.044409 | 0.049446 | -0.064976 | -0.019207 | -0.26678 | -0.19713 | 0.02346 | -0.038517 | 0.22827 | 0.031099 | -0.071008 | 121.3603 | 121.3111 | 121.3568 | 60.6734 | -121.4699 | 121.1789 | 121.4071 | 121.305 | 60.6586 | -121.6428
261.9062 | 121.5958 | -60.672 | 60.7224 | 1.4211e-13 | -0.010611 | 0.0022072 | 0.067767 | -0.0084334 | 0.059967 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060125 | 0.024243 | 0.055727 | -60.5527 | 0.0243 | -60.6844 | 60.7203 | 60.6665 | 60.726 | -60.7246 | -60.6211 | 0.009516 | -60.6785 | 60.5527 | 60.7809 | 60.6605 | -60.8976 | -0.052653 | -0.002006 | 0.11929 | -0.012364 | 0.040289 | -0.055821 | 0.003683 | -0.22558 | -0.16966 | 0.050926 | -0.006473 | 0.21911 | 0.058568 | -0.061853 | 121.3923 | 121.3385 | 121.398 | 60.6963 | -121.447 | 121.2247 | 121.4529 | 121.3325 | 60.6815 | -121.6199
263.5625 | 121.5042 | -60.6812 | 60.7864 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067554 | -0.0084334 | 0.06018 | 0.015566 | -0.0014485 | -0.00085459 | 0.060552 | 0.024243 | 0.055941 | -60.5573 | 0.0243 | -60.6798 | 60.7203 | 60.6711 | 60.726 | -60.7292 | -60.6211 | 0.018674 | -60.6785 | 60.539 | 60.7763 | 60.6559 | -60.9022 | -0.048077 | -0.066093 | 0.12386 | 0.001369 | 0.049446 | -0.11533 | -0.060404 | -0.22101 | -0.24748 | 0.060081 | 0.002682 | 0.22369 | -0.010097 | -0.13052 | 121.4015 | 121.3523 | 121.4072 | 60.7055 | -121.5157 | 121.2201 | 121.4575 | 121.3371 | 60.6998 | -121.6886
265.2344 | 121.5088 | -60.6812 | 60.8002 | 1.4211e-13 | -0.010611 | 0.0019936 | 0.06734 | -0.0084334 | 0.059967 | 0.015566 | -0.0016621 | -0.00021359 | 0.060338 | 0.02403 | 0.055941 | -60.5527 | 0.0243 | -60.6798 | 60.7295 | 60.6757 | 60.7352 | -60.7292 | -60.6165 | 0.014095 | -60.683 | 60.5435 | 60.7901 | 60.6697 | -60.9022 | -0.048077 | -0.070669 | 0.12844 | 0.001369 | 0.049446 | -0.12448 | -0.064979 | -0.22101 | -0.25663 | 0.06466 | -0.001896 | 0.21911 | -0.010095 | -0.13052 | 121.4107 | 121.3568 | 121.4163 | 60.7055 | -121.5294 | 121.2247 | 121.4712 | 121.3508 | 60.6952 | -121.7023
266.9531 | 121.5317 | -60.704 | 60.759 | 1.4211e-13 | -0.010184 | 0.0022072 | 0.067554 | -0.0082196 | 0.06018 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060979 | 0.024457 | 0.055941 | -60.5527 | 0.0243 | -60.6798 | 60.7295 | 60.6848 | 60.7352 | -60.7201 | -60.6073 | 0.018674 | -60.6647 | 60.5435 | 60.7901 | 60.6742 | -60.8884 | -0.01603 | -0.02947 | 0.15133 | 0.024258 | 0.040288 | -0.074126 | -0.02378 | -0.18438 | -0.21543 | 0.096706 | 0.039308 | 0.22369 | 0.031104 | -0.084738 | 121.4335 | 121.3889 | 121.4392 | 60.7283 | -121.479 | 121.2476 | 121.4941 | 121.3783 | 60.7227 | -121.6474
268.6875 | 121.6324 | -60.6628 | 60.7224 | 1.4211e-13 | -0.010611 | 0.0022072 | 0.067554 | -0.0082196 | 0.06018 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060338 | 0.024243 | 0.055941 | -60.5436 | 0.015142 | -60.6752 | 60.7341 | 60.6848 | 60.7398 | -60.7155 | -60.6073 | 0.009516 | -60.6647 | 60.5481 | 60.7947 | 60.6742 | -60.8884 | -0.05265 | 0.011729 | 0.11929 | -0.012363 | 0.040287 | -0.037505 | 0.017419 | -0.22558 | -0.17424 | 0.055507 | -0.001891 | 0.22369 | 0.072304 | -0.048117 | 121.3969 | 121.3477 | 121.4026 | 60.678 | -121.4378 | 121.211 | 121.4575 | 121.3371 | 60.6724 | -121.6108
270.3594 | 121.5454 | -60.704 | 60.7452 | 1.4211e-13 | -0.010825 | 0.0022072 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060552 | 0.023816 | 0.056155 | -60.539 | 0.0243 | -60.6706 | 60.7341 | 60.6848 | 60.7443 | -60.7155 | -60.5936 | 0.018674 | -60.6556 | 60.5527 | 60.7901 | 60.6788 | -60.8838 | -0.011451 | -0.011159 | 0.16507 | 0.033414 | 0.044865 | -0.060393 | -0.00089 | -0.1798 | -0.19254 | 0.11044 | 0.048465 | 0.22827 | 0.044837 | -0.066426 | 121.4381 | 121.3889 | 121.4484 | 60.7283 | -121.4607 | 121.2567 | 121.4941 | 121.3829 | 60.7227 | -121.6291
272.0312 | 121.5408 | -60.6583 | 60.7864 | 1.4211e-13 | -0.010611 | 0.0019936 | 0.067767 | -0.0084334 | 0.059967 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060766 | 0.02403 | 0.056368 | -60.5298 | 0.0243 | -60.6615 | 60.7478 | 60.694 | 60.7443 | -60.7109 | -60.5936 | 0.018674 | -60.651 | 60.5664 | 60.8038 | 60.688 | -60.8884 | -0.052649 | -0.038622 | 0.12845 | -0.003206 | 0.049443 | -0.092434 | -0.042089 | -0.23016 | -0.22001 | 0.064665 | 0.007267 | 0.23743 | 0.017374 | -0.098468 | 121.4061 | 121.3523 | 121.4026 | 60.6826 | -121.4974 | 121.2247 | 121.4621 | 121.3462 | 60.6769 | -121.6749
273.7188 | 121.5912 | -60.6308 | 60.7773 | 1.4211e-13 | -0.010611 | 0.002421 | 0.067767 | -0.0084334 | 0.059967 | 0.0079357 | -0.0020893 | -0.00085459 | 0.060766 | 0.02403 | 0.055941 | -60.5252 | 0.015142 | -60.6523 | 60.7478 | 60.6986 | 60.7535 | -60.6972 | -60.589 | 0.014095 | -60.6464 | 60.5756 | 60.8084 | 60.688 | -60.8793 | -0.066378 | -0.029467 | 0.10556 | -0.021515 | 0.044863 | -0.0787 | -0.023777 | -0.24847 | -0.2017 | 0.041778 | -0.015621 | 0.23285 | 0.031108 | -0.089313 | 121.3786 | 121.3294 | 121.3843 | 60.6459 | -121.4745 | 121.2064 | 121.4392 | 121.3188 | 60.6449 | -121.6565
275.3906 | 121.5683 | -60.6079 | 60.7681 | 1.4211e-13 | -0.011038 | 0.0026346 | 0.067554 | -0.0082196 | 0.059967 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.023816 | 0.056155 | -60.5161 | 0.0243 | -60.6523 | 60.7616 | 60.7123 | 60.7627 | -60.6926 | -60.5799 | 0.018674 | -60.6464 | 60.5802 | 60.8175 | 60.6971 | -60.8655 | -0.084687 | -0.006576 | 0.091827 | -0.044403 | 0.040284 | -0.055808 | -0.005464 | -0.25762 | -0.18796 | 0.028048 | -0.038509 | 0.21911 | 0.049421 | -0.071 | 121.3695 | 121.3202 | 121.3706 | 60.6322 | -121.4607 | 121.1881 | 121.4255 | 121.305 | 60.6266 | -121.6337
277.0781 | 121.5683 | -60.64 | 60.7773 | 1.4211e-13 | -0.010397 | 0.0026346 | 0.067554 | -0.0084334 | 0.059753 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060552 | 0.02403 | 0.055941 | -60.5069 | 0.019721 | -60.6432 | 60.7661 | 60.7077 | 60.7627 | -60.6834 | -60.5753 | 0.018674 | -60.6373 | 60.5802 | 60.8267 | 60.7154 | -60.8564 | -0.043485 | -0.011154 | 0.13303 | -0.003203 | 0.040282 | -0.069542 | -0.01462 | -0.21642 | -0.19712 | 0.06467 | 0.002693 | 0.21911 | 0.049422 | -0.061842 | 121.4061 | 121.3477 | 121.4026 | 60.6597 | -121.4607 | 121.2201 | 121.4667 | 121.3554 | 60.6586 | -121.6337
278.7656 | 121.5408 | -60.6766 | 60.7681 | 1.4211e-13 | -0.010397 | 0.002421 | 0.067554 | -0.0082196 | 0.059967 | 0.00030522 | -0.0012349 | -0.00064099 | 0.060338 | 0.02403 | 0.056155 | -60.5069 | 0.0243 | -60.6294 | 60.7661 | 60.7169 | 60.7672 | -60.6743 | -60.5661 | 0.018674 | -60.6418 | 60.5893 | 60.8313 | 60.7109 | -60.8564 | 0.002294 | -0.001998 | 0.16965 | 0.047153 | 0.044859 | -0.051229 | -0.000885 | -0.1798 | -0.1788 | 0.11045 | 0.034735 | 0.21453 | 0.063157 | -0.057264 | 121.4427 | 121.3935 | 121.4438 | 60.7009 | -121.4424 | 121.2659 | 121.5079 | 121.3874 | 60.6952 | -121.6245
280.4844 | 121.5958 | -60.5896 | 60.791 | 1.4211e-13 | -0.010611 | 0.002421 | 0.067554 | -0.0082196 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060552 | 0.02403 | 0.055941 | -60.4886 | 0.015142 | -60.6203 | 60.7844 | 60.7352 | 60.7856 | -60.6651 | -60.5524 | 0.009516 | -60.6281 | 60.5985 | 60.8359 | 60.7246 | -60.8381 | -0.075524 | -0.006573 | 0.10099 | -0.030665 | 0.044859 | -0.055802 | -0.00546 | -0.24845 | -0.19254 | 0.03721 | -0.038504 | 0.20995 | 0.044846 | -0.066417 | 121.374 | 121.3248 | 121.3752 | 60.6047 | -121.4561 | 121.1881 | 121.4255 | 121.3142 | 60.5991 | -121.6291
282.1562 | 121.6415 | -60.5804 | 60.7727 | 1.4211e-13 | -0.010611 | 0.002421 | 0.067767 | -0.0082196 | 0.059967 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060766 | 0.024243 | 0.056155 | -60.4932 | 0.0243 | -60.6157 | 60.789 | 60.7352 | 60.7993 | -60.6514 | -60.5524 | 0.018674 | -60.6098 | 60.6122 | 60.8588 | 60.7292 | -60.8335 | -0.070943 | 0.016316 | 0.087253 | -0.035243 | 0.0357 | -0.037491 | 0.026587 | -0.25303 | -0.16049 | 0.028054 | -0.029345 | 0.22369 | 0.08605 | -0.043528 | 121.3695 | 121.3157 | 121.3797 | 60.6047 | -121.4241 | 121.1927 | 121.4392 | 121.3096 | 60.5991 | -121.6062
283.8594 | 121.5317 | -60.6033 | 60.8505 | 1.4211e-13 | -0.011038 | 0.0022072 | 0.067981 | -0.008647 | 0.06018 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060338 | 0.02403 | 0.056155 | -60.4749 | 0.019721 | -60.5974 | 60.7982 | 60.7535 | 60.8039 | -60.6468 | -60.5387 | 0.014095 | -60.5961 | 60.6305 | 60.8633 | 60.7429 | -60.8197 | -0.043475 | -0.052347 | 0.12846 | 0.005959 | 0.049434 | -0.096995 | -0.046654 | -0.21641 | -0.22 | 0.064679 | 0.00728 | 0.22369 | 0.012809 | -0.10761 | 121.4015 | 121.3569 | 121.4072 | 60.6231 | -121.4973 | 121.2339 | 121.4667 | 121.3462 | 60.6174 | -121.6703
285.5469 | 121.5088 | -60.5988 | 60.8688 | 1.4211e-13 | -0.011038 | 0.002421 | 0.067554 | -0.0082196 | 0.059753 | 0.00030522 | -0.0014485 | -0.00085459 | 0.060125 | 0.02403 | 0.056155 | -60.4703 | 0.0243 | -60.5882 | 60.8165 | 60.7627 | 60.8084 | -60.6422 | -60.5341 | 0.018674 | -60.5869 | 60.6351 | 60.8725 | 60.7566 | -60.8152 | -0.043474 | -0.052344 | 0.12846 | 0.010538 | 0.054012 | -0.10615 | -0.060386 | -0.21641 | -0.23373 | 0.06468 | 0.01186 | 0.22827 | 0.003656 | -0.11219 | 121.4152 | 121.3614 | 121.4072 | 60.6231 | -121.5111 | 121.2339 | 121.4712 | 121.3554 | 60.6174 | -121.684
287.2188 | 121.6049 | -60.5576 | 60.8368 | 1.4211e-13 | -0.010611 | 0.0022072 | 0.067554 | -0.0082196 | 0.059967 | 0.015566 | -0.0018757 | -0.00042739 | 0.060552 | 0.02403 | 0.056368 | -60.452 | 0.028878 | -60.5745 | 60.8211 | 60.7718 | 60.8313 | -60.6331 | -60.5158 | 0.014095 | -60.5777 | 60.6443 | 60.8862 | 60.7658 | -60.8014 | -0.075515 | -0.015722 | 0.10557 | -0.016927 | 0.058588 | -0.064947 | -0.00545 | -0.24387 | -0.19253 | 0.041795 | -0.020182 | 0.22369 | 0.049435 | -0.070986 | 121.3786 | 121.3294 | 121.3889 | 60.5864 | -121.4699 | 121.2018 | 121.4438 | 121.3234 | 60.5717 | -121.6382
288.9062 | 121.6278 | -60.5667 | 60.8276 | 1.4211e-13 | -0.010825 | 0.0022072 | 0.067981 | -0.0084334 | 0.06018 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.024457 | 0.055941 | -60.4428 | 0.0243 | -60.5745 | 60.8302 | 60.781 | 60.8359 | -60.601 | -60.502 | 0.018674 | -60.5732 | 60.6534 | 60.9 | 60.7795 | -60.7877 | -0.034308 | 0.00259 | 0.12388 | -0.007772 | 0.026536 | -0.046634 | 0.008284 | -0.22098 | -0.17422 | 0.064687 | -0.006448 | 0.21453 | 0.072326 | -0.048095 | 121.3969 | 121.3477 | 121.4026 | 60.591 | -121.4287 | 121.2201 | 121.4667 | 121.3463 | 60.5854 | -121.6153
290.6094 | 121.5317 | -60.5484 | 60.878 | 1.4211e-13 | -0.010397 | 0.0022072 | 0.067767 | -0.0084334 | 0.059967 | 0.015566 | -0.0014485 | -0.00085459 | 0.060552 | 0.02403 | 0.056582 | -60.4291 | 0.0243 | -60.5516 | 60.8531 | 60.7947 | 60.8451 | -60.6056 | -60.4929 | 0.018674 | -60.5594 | 60.6717 | 60.9045 | 60.7933 | -60.7831 | -0.057197 | -0.024873 | 0.11931 | -0.00319 | 0.054007 | -0.083251 | -0.032913 | -0.23471 | -0.20626 | 0.055534 | -0.011022 | 0.22369 | 0.02655 | -0.084713 | 121.4015 | 121.3431 | 121.3935 | 60.5727 | -121.4836 | 121.2201 | 121.4529 | 121.3417 | 60.5671 | -121.6611
292.2812 | 121.6278 | -60.5072 | 60.8963 | 1.4211e-13 | -0.010825 | 0.0022072 | 0.067554 | -0.0082196 | 0.059753 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.024243 | 0.056155 | -60.4154 | 0.019721 | -60.5516 | 60.8577 | 60.8039 | 60.8725 | -60.5873 | -60.4746 | 0.018674 | -60.5411 | 60.6809 | 60.9229 | 60.807 | -60.7602 | -0.08008 | -0.038604 | 0.091843 | -0.044389 | 0.035691 | -0.092403 | -0.023751 | -0.25301 | -0.21541 | 0.03265 | -0.033906 | 0.21911 | 0.026555 | -0.089288 | 121.3649 | 121.3111 | 121.3798 | 60.5269 | -121.4836 | 121.1881 | 121.4301 | 121.3142 | 60.5259 | -121.6565
293.9531 | 121.5042 | -60.5255 | 60.9375 | 1.4211e-13 | -0.010611 | 0.00178 | 0.06734 | -0.008647 | 0.059967 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060338 | 0.02403 | 0.056368 | -60.4016 | 0.0243 | -60.5287 | 60.8669 | 60.8314 | 60.8863 | -60.5735 | -60.4654 | 0.014095 | -60.5274 | 60.7038 | 60.9274 | 60.8207 | -60.7465 | -0.048032 | -0.070646 | 0.12389 | -0.003187 | 0.044845 | -0.10613 | -0.051214 | -0.22097 | -0.23372 | 0.060118 | -0.001859 | 0.21911 | -0.010066 | -0.11675 | 121.3924 | 121.3569 | 121.4118 | 60.5498 | -121.511 | 121.2293 | 121.4529 | 121.3463 | 60.5396 | -121.684
295.6406 | 121.5958 | -60.5072 | 60.9009 | 1.4211e-13 | -0.010825 | 0.00178 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0012349 | -0.00042739 | 0.060552 | 0.023816 | 0.056155 | -60.3833 | 0.019721 | -60.5195 | 60.8897 | 60.8359 | 60.8954 | -60.5598 | -60.4425 | 0.009516 | -60.5136 | 60.7221 | 60.9503 | 60.8299 | -60.7373 | -0.052606 | -0.011133 | 0.12389 | -0.012341 | 0.040265 | -0.064929 | -0.005436 | -0.23012 | -0.17878 | 0.064701 | -0.006434 | 0.22369 | 0.049448 | -0.070972 | 121.3969 | 121.3432 | 121.4026 | 60.5269 | -121.4607 | 121.2293 | 121.4575 | 121.3371 | 60.5167 | -121.6382
297.3125 | 121.6415 | -60.4889 | 60.9009 | 1.4211e-13 | -0.011038 | 0.0022072 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060338 | 0.024243 | 0.056155 | -60.365 | 0.0243 | -60.4967 | 60.9035 | 60.8497 | 60.9138 | -60.5369 | -60.4288 | 0.018674 | -60.4907 | 60.7358 | 60.9686 | 60.8482 | -60.7144 | -0.048022 | 0.002602 | 0.1239 | -0.00776 | 0.040262 | -0.051192 | 0.012878 | -0.22554 | -0.16505 | 0.060127 | -0.00185 | 0.22369 | 0.067763 | -0.052658 | 121.3924 | 121.3386 | 121.4026 | 60.5132 | -121.4378 | 121.2247 | 121.4575 | 121.3371 | 60.5076 | -121.6153
298.9844 | 121.6232 | -60.4706 | 60.91 | 1.4211e-13 | -0.010611 | 0.0019936 | 0.06734 | -0.0084334 | 0.059967 | 0.0079357 | -0.0012349 | -0.00085459 | 0.060552 | 0.02403 | 0.056155 | -60.3513 | 0.0243 | -60.4783 | 60.9264 | 60.8726 | 60.9275 | -60.5232 | -60.4059 | 0.018674 | -60.4678 | 60.745 | 60.987 | 60.862 | -60.7007 | -0.052596 | 0.016339 | 0.11932 | -0.007758 | 0.044838 | -0.037452 | 0.017459 | -0.23011 | -0.16504 | 0.06471 | 0.002732 | 0.23284 | 0.076922 | -0.048077 | 121.397 | 121.3432 | 121.3981 | 60.4949 | -121.4332 | 121.2156 | 121.4575 | 121.3325 | 60.4893 | -121.6107
300.6562 | 121.5591 | -60.4843 | 60.9421 | 1.4211e-13 | -0.010825 | 0.0022072 | 0.067554 | -0.0084334 | 0.059753 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060766 | 0.024243 | 0.056155 | -60.3329 | 0.0243 | -60.4646 | 60.9493 | 60.8909 | 60.9504 | -60.5049 | -60.3876 | 0.014095 | -60.4495 | 60.7725 | 61.0007 | 60.8757 | -60.6778 | -0.020547 | 0.007187 | 0.15137 | 0.01971 | 0.040257 | -0.05118 | 0.008308 | -0.19348 | -0.16962 | 0.096757 | 0.03478 | 0.22826 | 0.058614 | -0.066385 | 121.4336 | 121.3752 | 121.4347 | 60.5086 | -121.4469 | 121.2568 | 121.485 | 121.36 | 60.4984 | -121.6199
302.3281 | 121.5546 | -60.4431 | 60.965 | 1.4211e-13 | -0.010825 | 0.002421 | 0.06734 | -0.008006 | 0.059539 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060552 | 0.02403 | 0.055941 | -60.3192 | 0.019721 | -60.4371 | 60.9676 | 60.923 | 60.9733 | -60.4865 | -60.3692 | 0.014095 | -60.4358 | 60.7908 | 61.0236 | 60.9077 | -60.6595 | -0.043431 | 0.002612 | 0.1239 | 0.005981 | 0.049412 | -0.042016 | 0.008313 | -0.21637 | -0.17419 | 0.073873 | 0.007317 | 0.22368 | 0.058619 | -0.057223 | 121.4107 | 121.3661 | 121.4164 | 60.4628 | -121.4515 | 121.2339 | 121.4667 | 121.3509 | 60.4572 | -121.6244
304 | 121.5683 | -60.4019 | 61.0565 | 1.4211e-13 | -0.010825 | 0.00178 | 0.067554 | -0.0084334 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060552 | 0.02403 | 0.056368 | -60.2917 | 0.019721 | -60.4097 | 60.9813 | 60.9413 | 60.9916 | -60.4545 | -60.3509 | 0.018674 | -60.4129 | 60.8137 | 61.0511 | 60.9306 | -60.6366 | -0.052576 | -0.075206 | 0.11017 | -0.007748 | 0.044828 | -0.11525 | -0.064926 | -0.23467 | -0.24285 | 0.05099 | -0.010987 | 0.22368 | -0.005462 | -0.12588 | 121.3832 | 121.3432 | 121.3935 | 60.4216 | -121.511 | 121.2156 | 121.453 | 121.3326 | 60.4206 | -121.6931
305.6719 | 121.637 | -60.3241 | 61.0519 | 1.4211e-13 | -0.011038 | 0.0019936 | 0.067554 | -0.0084334 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.02403 | 0.056155 | -60.2643 | 0.019721 | -60.3868 | 61.0088 | 60.9687 | 61.0236 | -60.4362 | -60.3235 | 0.023253 | -60.3763 | 60.8411 | 61.074 | 60.9627 | -60.6091 | -0.11208 | -0.043157 | 0.059825 | -0.062676 | 0.049404 | -0.083202 | -0.028297 | -0.28502 | -0.2108 | 0.000642 | -0.052178 | 0.23284 | 0.022009 | -0.089255 | 121.3329 | 121.2928 | 121.3477 | 60.3438 | -121.4881 | 121.1652 | 121.398 | 121.2868 | 60.3473 | -121.6611
307.3438 | 121.5775 | -60.3424 | 61.0474 | 1.4211e-13 | -0.010825 | 0.0022072 | 0.067767 | -0.0084334 | 0.059753 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.024457 | 0.056155 | -60.2322 | 0.028878 | -60.3593 | 61.0454 | 60.9962 | 61.0511 | -60.4041 | -60.2868 | 0.014095 | -60.358 | 60.8732 | 61.106 | 60.9947 | -60.5771 | -0.061718 | -0.001952 | 0.11018 | -0.016896 | 0.044822 | -0.05115 | 0.003752 | -0.23466 | -0.17417 | 0.055582 | -0.015553 | 0.2191 | 0.058637 | -0.052627 | 121.3878 | 121.3386 | 121.3935 | 60.3713 | -121.4515 | 121.2156 | 121.4484 | 121.3371 | 60.3565 | -121.6244
309.0156 | 121.6141 | -60.3378 | 61.0565 | 1.4211e-13 | -0.011038 | 0.002421 | 0.067554 | -0.0084334 | 0.059967 | 0.015566 | -0.0014485 | -0.00085459 | 0.060552 | 0.024243 | 0.056368 | -60.2048 | 0.0243 | -60.3181 | 61.0729 | 61.0283 | 61.0877 | -60.3721 | -60.2594 | 0.018674 | -60.3259 | 60.9007 | 61.1426 | 61.0131 | -60.5404 | -0.034242 | 0.016362 | 0.13308 | 0.019731 | 0.053973 | -0.028254 | 0.031225 | -0.2026 | -0.15586 | 0.078477 | 0.011921 | 0.21452 | 0.08611 | -0.043468 | 121.4107 | 121.3661 | 121.4256 | 60.3621 | -121.4286 | 121.2385 | 121.4805 | 121.3509 | 60.3565 | -121.597
310.6875 | 121.55 | -60.3149 | 61.116 | 1.4211e-13 | -0.011038 | 0.0022072 | 0.06734 | -0.0084334 | 0.059753 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060338 | 0.024457 | 0.056368 | -60.1681 | 0.010564 | -60.2906 | 61.1095 | 61.0649 | 61.1244 | -60.3354 | -60.2319 | 0.014095 | -60.2939 | 60.9327 | 61.1564 | 61.0543 | -60.5038 | -0.0205 | -0.00652 | 0.14681 | 0.024312 | 0.044812 | -0.051131 | 0.008345 | -0.18886 | -0.18332 | 0.08306 | 0.021083 | 0.20994 | 0.040337 | -0.06177 | 121.4244 | 121.3798 | 121.4393 | 60.3255 | -121.4515 | 121.2476 | 121.4713 | 121.3692 | 60.329 | -121.6198
312.375 | 121.5088 | -60.2737 | 61.2167 | 1.4211e-13 | -0.011038 | 0.0019936 | 0.067554 | -0.0082196 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060552 | 0.024457 | 0.056155 | -60.1269 | 0.019721 | -60.254 | 61.1553 | 61.0924 | 61.1473 | -60.3034 | -60.1907 | 0.018674 | -60.2572 | 60.9648 | 61.2022 | 61.0726 | -60.4763 | -0.029646 | -0.061444 | 0.14682 | 0.01974 | 0.049386 | -0.12437 | -0.06947 | -0.20259 | -0.25198 | 0.083071 | 0.016515 | 0.2191 | -0.014585 | -0.14416 | 121.429 | 121.3661 | 121.421 | 60.2935 | -121.5201 | 121.2385 | 121.4759 | 121.3463 | 60.2924 | -121.6931
314.0469 | 121.6507 | -60.1776 | 61.1984 | 1.4211e-13 | -0.010825 | 0.0019936 | 0.067767 | -0.0084334 | 0.06018 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060766 | 0.024243 | 0.056368 | -60.0949 | 0.019721 | -60.222 | 61.1873 | 61.1427 | 61.1931 | -60.2713 | -60.1586 | 0.018674 | -60.2206 | 61.0014 | 61.2434 | 61.1321 | -60.4443 | -0.093724 | -0.011084 | 0.08274 | -0.044343 | 0.049381 | -0.055687 | -0.005373 | -0.26666 | -0.19704 | 0.018991 | -0.042987 | 0.22368 | 0.044933 | -0.066331 | 121.365 | 121.3204 | 121.3707 | 60.1973 | -121.4698 | 121.179 | 121.421 | 121.3097 | 60.1963 | -121.6427
315.75 | 121.5088 | -60.1685 | 61.2854 | 1.4211e-13 | -0.011038 | 0.0019936 | 0.06734 | -0.0084334 | 0.059753 | -0.0073253 | -0.0014485 | -0.00064099 | 0.060552 | 0.02403 | 0.056155 | -60.0491 | 0.0243 | -60.1762 | 61.224 | 61.1794 | 61.2388 | -60.2255 | -60.1083 | 0.018674 | -60.1748 | 61.0426 | 61.2891 | 61.1779 | -60.4031 | -0.05709 | -0.061432 | 0.11937 | -0.007715 | 0.049375 | -0.10603 | -0.046562 | -0.23461 | -0.24281 | 0.060202 | -0.006354 | 0.22826 | 0.003744 | -0.10752 | 121.3924 | 121.3478 | 121.4073 | 60.1928 | -121.5109 | 121.2111 | 121.4576 | 121.3463 | 60.1871 | -121.6885
317.4844 | 121.5271 | -60.1501 | 61.3083 | 1.4211e-13 | -0.011252 | 0.0022072 | 0.067554 | -0.008647 | 0.059967 | 0.0079357 | -0.0020893 | -0.00042739 | 0.060552 | 0.02403 | 0.056155 | -60.0033 | 0.0243 | -60.1304 | 61.2652 | 61.216 | 61.28 | -60.1752 | -60.0625 | 0.018674 | -60.129 | 61.093 | 61.3304 | 61.2145 | -60.3481 | -0.025033 | -0.043116 | 0.14684 | 0.019757 | 0.04479 | -0.092288 | -0.028244 | -0.19798 | -0.21533 | 0.087678 | 0.021122 | 0.2191 | 0.022062 | -0.09378 | 121.4153 | 121.3661 | 121.4302 | 60.1744 | -121.4835 | 121.2431 | 121.4805 | 121.3647 | 60.1688 | -121.6564
319.1562 | 121.5363 | -60.0998 | 61.3541 | 1.4211e-13 | -0.011038 | 0.002421 | 0.067981 | -0.008006 | 0.059967 | 0.00030522 | -0.0018757 | -0.00064099 | 0.060552 | 0.024243 | 0.056155 | -59.9575 | 0.019721 | -60.0892 | 61.3201 | 61.2664 | 61.3258 | -60.1385 | -60.0258 | 0.018674 | -60.0878 | 61.1387 | 61.3853 | 61.2649 | -60.3023 | -0.038755 | -0.033951 | 0.14227 | 0.010607 | 0.049362 | -0.087696 | -0.028234 | -0.20254 | -0.21532 | 0.073953 | 0.011976 | 0.21452 | 0.03123 | -0.089191 | 121.4199 | 121.3662 | 121.4256 | 60.1195 | -121.4926 | 121.2385 | 121.4851 | 121.3647 | 60.1185 | -121.6564
320.8281 | 121.5683 | -60.0311 | 61.3907 | 1.4211e-13 | -0.011252 | 0.0022072 | 0.067554 | -0.0084334 | 0.06018 | 0.015566 | -0.0016621 | -0.00064099 | 0.060552 | 0.024243 | 0.055941 | -59.9163 | 0.0243 | -60.0388 | 61.3705 | 61.3213 | 61.3808 | -60.079 | -59.9663 | 0.018674 | -60.0329 | 61.1845 | 61.4265 | 61.3107 | -60.2611 | -0.047893 | -0.02021 | 0.11481 | -0.007696 | 0.040197 | -0.06937 | -0.009911 | -0.23 | -0.20616 | 0.064813 | -0.001743 | 0.22825 | 0.035816 | -0.080026 | 121.4016 | 121.3524 | 121.4119 | 60.0554 | -121.4697 | 121.2157 | 121.4576 | 121.3418 | 60.0498 | -121.6518
322.5469 | 121.6324 | -59.9121 | 61.4731 | 1.4211e-13 | -0.011252 | 0.0022072 | 0.067767 | -0.0082196 | 0.059753 | 0.00030522 | -0.0016621 | -0.00021359 | 0.060552 | 0.024457 | 0.055941 | -59.8476 | 0.015142 | -59.9793 | 61.43 | 61.3854 | 61.4403 | -60.0241 | -59.916 | 0.023253 | -59.9779 | 61.244 | 61.486 | 61.3702 | -60.197 | -0.11196 | -0.043088 | 0.06447 | -0.067197 | 0.044768 | -0.087662 | -0.032787 | -0.28491 | -0.22904 | -0.003841 | -0.065818 | 0.21909 | 0.012941 | -0.1029 | 121.3421 | 121.2975 | 121.3524 | 59.9273 | -121.4972 | 121.1562 | 121.3981 | 121.2823 | 59.9354 | -121.6701
324.2188 | 121.6415 | -59.8938 | 61.5097 | 1.4211e-13 | -0.011252 | 0.0019936 | 0.067981 | -0.0084334 | 0.059967 | 0.0079357 | -0.0012349 | -0.00085459 | 0.060552 | 0.024671 | 0.056368 | -59.7973 | 0.015142 | -59.9198 | 61.4849 | 61.4404 | 61.4952 | -59.9737 | -59.861 | 0.023253 | -59.923 | 61.3036 | 61.541 | 61.4251 | -60.1467 | -0.079907 | -0.024769 | 0.096523 | -0.02599 | 0.053917 | -0.069337 | -0.014465 | -0.25285 | -0.20614 | 0.032794 | -0.029183 | 0.22367 | 0.031262 | -0.08458 | 121.3787 | 121.3342 | 121.389 | 59.9089 | -121.4834 | 121.1974 | 121.4348 | 121.3189 | 59.9171 | -121.6564
325.8906 | 121.5637 | -59.8251 | 61.5601 | 1.4211e-13 | -0.011252 | 0.00178 | 0.067554 | -0.008647 | 0.059967 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060552 | 0.024457 | 0.056582 | -59.7378 | 0.028878 | -59.874 | 61.5445 | 61.4907 | 61.5502 | -59.9096 | -59.8015 | 0.023253 | -59.868 | 61.3585 | 61.6051 | 61.4755 | -60.0871 | -0.084467 | -0.015604 | 0.087377 | -0.048872 | 0.035595 | -0.069322 | -0.009876 | -0.26199 | -0.20155 | 0.023652 | -0.042904 | 0.21909 | 0.045009 | -0.08457 | 121.3696 | 121.3159 | 121.3753 | 59.854 | -121.4697 | 121.1836 | 121.4302 | 121.3006 | 59.8484 | -121.6472
327.5625 | 121.5134 | -59.8343 | 61.615 | 1.4211e-13 | -0.011466 | 0.0022072 | 0.06734 | -0.0084334 | 0.059967 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060552 | 0.024457 | 0.056368 | -59.6828 | 0.019721 | -59.8053 | 61.5948 | 61.5503 | 61.6005 | -59.8501 | -59.7511 | 0.023253 | -59.8039 | 61.418 | 61.66 | 61.535 | -60.0322 | -0.015785 | -0.020173 | 0.15147 | 0.028958 | 0.044743 | -0.064727 | -0.014442 | -0.19789 | -0.19696 | 0.083174 | 0.030354 | 0.22825 | 0.045021 | -0.079979 | 121.4291 | 121.3846 | 121.4348 | 59.854 | -121.4651 | 121.2523 | 121.4943 | 121.3693 | 59.8575 | -121.6472
329.2344 | 121.5683 | -59.7519 | 61.6379 | 1.4211e-13 | -0.011252 | 0.00178 | 0.06734 | -0.008647 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060766 | 0.024243 | 0.056155 | -59.6325 | 0.019721 | -59.7504 | 61.6543 | 61.6052 | 61.6601 | -59.7905 | -59.687 | 0.014095 | -59.749 | 61.4776 | 61.7104 | 61.5991 | -59.9681 | -0.038657 | 0.016458 | 0.11944 | 0.0015 | 0.040157 | -0.032668 | 0.022191 | -0.21619 | -0.16033 | 0.064878 | 0.002901 | 0.21909 | 0.072497 | -0.038766 | 121.4062 | 121.3571 | 121.412 | 59.7716 | -121.4284 | 121.2294 | 121.4623 | 121.351 | 59.766 | -121.606
330.9219 | 121.55 | -59.6878 | 61.7615 | 1.4211e-13 | -0.011038 | 0.002421 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060338 | 0.024243 | 0.056368 | -59.5684 | 0.019721 | -59.6863 | 61.723 | 61.6739 | 61.7242 | -59.7356 | -59.6229 | 0.023253 | -59.6895 | 61.5416 | 61.7791 | 61.6678 | -59.904 | -0.047797 | -0.038463 | 0.11945 | 0.001509 | 0.049306 | -0.087581 | -0.037305 | -0.21617 | -0.21983 | 0.064893 | -0.001663 | 0.21451 | 0.017579 | -0.093684 | 121.4108 | 121.3617 | 121.412 | 59.7075 | -121.4971 | 121.2295 | 121.4669 | 121.3556 | 59.7111 | -121.6655
332.5938 | 121.5134 | -59.61 | 61.8942 | 1.4211e-13 | -0.011466 | 0.002421 | 0.06734 | -0.0084334 | 0.06018 | 0.0079357 | -0.0016621 | -0.00085459 | 0.060552 | 0.024243 | 0.056368 | -59.4814 | 0.019721 | -59.6039 | 61.8008 | 61.7563 | 61.8157 | -59.644 | -59.5451 | 0.018674 | -59.5933 | 61.6241 | 61.8569 | 61.7456 | -59.8261 | -0.034038 | -0.093381 | 0.12862 | 0.006098 | 0.040136 | -0.13791 | -0.078484 | -0.21615 | -0.27016 | 0.064911 | 0.01667 | 0.23282 | -0.037335 | -0.1486 | 121.4108 | 121.3663 | 121.4257 | 59.6297 | -121.5382 | 121.234 | 121.4669 | 121.3556 | 59.6287 | -121.7204
334.3125 | 121.5408 | -59.5413 | 61.8759 | 1.4211e-13 | -0.011466 | 0.0022072 | 0.067126 | -0.0084334 | 0.059967 | 0.00030522 | -0.0018757 | -0.00042739 | 0.060766 | 0.024243 | 0.056368 | -59.4081 | 0.019721 | -59.5215 | 61.8833 | 61.825 | 61.8844 | -59.5753 | -59.4672 | 0.027831 | -59.5429 | 61.6973 | 61.9485 | 61.8189 | -59.7483 | -0.034019 | 0.00734 | 0.13321 | 0.019843 | 0.053862 | -0.050918 | 0.008505 | -0.20698 | -0.1786 | 0.074085 | -0.001629 | 0.20535 | 0.072547 | -0.057031 | 121.4246 | 121.3663 | 121.4257 | 59.561 | -121.4513 | 121.2386 | 121.4898 | 121.3602 | 59.5692 | -121.6242
336.0156 | 121.5042 | -59.5001 | 62.0087 | 1.4211e-13 | -0.011466 | 0.002421 | 0.067554 | -0.0084334 | 0.059967 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060552 | 0.024243 | 0.056368 | -59.3486 | 0.033457 | -59.4665 | 61.9382 | 61.8891 | 61.9394 | -59.5158 | -59.4077 | 0.023253 | -59.4651 | 61.7568 | 61.9897 | 61.883 | -59.6979 | -0.015692 | -0.070471 | 0.15153 | 0.033583 | 0.049275 | -0.11956 | -0.069303 | -0.19781 | -0.25183 | 0.092409 | 0.035011 | 0.23282 | -0.018997 | -0.12568 | 121.4383 | 121.3892 | 121.4395 | 59.5336 | -121.5245 | 121.257 | 121.4898 | 121.3831 | 59.5234 | -121.7066
337.6875 | 121.5408 | -59.4269 | 62.0682 | 1.4211e-13 | -0.011252 | 0.00178 | 0.067554 | -0.0084334 | 0.06018 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060766 | 0.024457 | 0.056368 | -59.2753 | 0.0243 | -59.3979 | 62.0115 | 61.9715 | 62.0218 | -59.4426 | -59.3299 | 0.023253 | -59.3873 | 61.8301 | 62.0721 | 61.9517 | -59.6064 | -0.015671 | -0.056725 | 0.15154 | 0.029015 | 0.044686 | -0.096652 | -0.046397 | -0.17947 | -0.23808 | 0.097005 | 0.039607 | 0.21908 | 0.003909 | -0.11651 | 121.4383 | 121.3984 | 121.4487 | 59.4512 | -121.5107 | 121.257 | 121.499 | 121.3785 | 59.4501 | -121.6745
339.375 | 121.5363 | -59.3216 | 62.1185 | 1.4211e-13 | -0.011466 | 0.002421 | 0.067554 | -0.0082196 | 0.059753 | 0.0079357 | -0.0018757 | -0.00064099 | 0.060552 | 0.024884 | 0.056155 | -59.1975 | 0.0243 | -59.32 | 62.0893 | 62.0402 | 62.0905 | -59.3556 | -59.252 | 0.018674 | -59.3186 | 61.9079 | 62.1408 | 62.0295 | -59.5285 | -0.033957 | -0.029247 | 0.12409 | 0.00156 | 0.035517 | -0.078322 | -0.028072 | -0.20692 | -0.2106 | 0.069557 | 0.003001 | 0.20992 | 0.022234 | -0.08903 | 121.4109 | 121.3618 | 121.4121 | 59.3459 | -121.4741 | 121.2295 | 121.4624 | 121.3511 | 59.3403 | -121.647
341.0469 | 121.6003 | -59.1797 | 62.1826 | 1.4211e-13 | -0.011038 | 0.002421 | 0.067767 | -0.0084334 | 0.059967 | 0.015566 | -0.0018757 | -0.00042739 | 0.060552 | 0.024457 | 0.056368 | -59.1197 | 0.028878 | -59.2422 | 62.1763 | 62.1272 | 62.1729 | -59.2777 | -59.1742 | 0.027831 | -59.2362 | 61.9858 | 62.2278 | 62.1028 | -59.4553 | -0.098022 | -0.006344 | 0.060012 | -0.062516 | 0.035506 | -0.05541 | -0.009744 | -0.27557 | -0.19685 | 0.005488 | -0.056489 | 0.21908 | 0.045141 | -0.079859 | 121.356 | 121.3069 | 121.3526 | 59.2086 | -121.4603 | 121.1654 | 121.4074 | 121.2824 | 59.2075 | -121.6379
342.7188 | 121.5729 | -59.1476 | 62.265 | 1.4211e-13 | -0.011466 | 0.00178 | 0.067554 | -0.0082196 | 0.059967 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060552 | 0.024243 | 0.056368 | -59.0327 | 0.0243 | -59.1552 | 62.2541 | 62.205 | 62.2553 | -59.1953 | -59.0964 | 0.023253 | -59.1492 | 62.0773 | 62.3239 | 62.1943 | -59.3637 | -0.047645 | -0.01091 | 0.11496 | -0.007572 | 0.040073 | -0.059966 | -0.009727 | -0.21603 | -0.18768 | 0.051284 | -0.001536 | 0.2145 | 0.058893 | -0.070685 | 121.4017 | 121.3527 | 121.4029 | 59.1719 | -121.4603 | 121.225 | 121.4716 | 121.342 | 59.1709 | -121.6287
344.4531 | 121.5134 | -59.0469 | 62.4161 | 1.4211e-13 | -0.011679 | 0.0022072 | 0.067554 | -0.008647 | 0.059967 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060552 | 0.024457 | 0.056368 | -58.932 | 0.028878 | -59.0499 | 62.3594 | 62.3149 | 62.3698 | -59.0854 | -58.9865 | 0.023253 | -59.053 | 62.1781 | 62.4201 | 62.3042 | -59.2675 | -0.038459 | -0.056669 | 0.11498 | -0.002979 | 0.03548 | -0.10113 | -0.046324 | -0.22058 | -0.23802 | 0.060465 | -0.006092 | 0.21449 | 0.003982 | -0.11186 | 121.4063 | 121.3619 | 121.4167 | 59.0758 | -121.5015 | 121.225 | 121.467 | 121.3512 | 59.0702 | -121.6836
346.125 | 121.5363 | -58.9828 | 62.4619 | 1.4211e-13 | -0.011466 | 0.0022072 | 0.067554 | -0.0084334 | 0.059967 | 0.0079357 | -0.0016621 | 1.2e-08 | 0.060552 | 0.024243 | 0.055941 | -58.8312 | 0.0243 | -58.9629 | 62.451 | 62.4065 | 62.4522 | -58.9984 | -58.8857 | 0.018674 | -58.9569 | 62.2742 | 62.5025 | 62.3958 | -59.1714 | -0.015546 | -0.010877 | 0.15161 | 0.019921 | 0.035467 | -0.055331 | -0.009685 | -0.18852 | -0.18764 | 0.097109 | 0.025974 | 0.21449 | 0.040621 | -0.066064 | 121.4338 | 121.3894 | 121.435 | 59.0071 | -121.4602 | 121.2571 | 121.4853 | 121.3786 | 59.0015 | -121.6332
347.7969 | 121.5088 | -58.8593 | 62.6083 | 1.4211e-13 | -0.011679 | 0.0022072 | 0.067554 | -0.0090744 | 0.059753 | 0.0079357 | -0.0018757 | -0.00064099 | 0.060338 | 0.024884 | 0.056155 | -58.7397 | 0.0243 | -58.8622 | 62.5425 | 62.5027 | 62.5575 | -58.9114 | -58.7987 | 0.023253 | -58.8653 | 62.3704 | 62.6032 | 62.4828 | -59.0752 | -0.052142 | -0.065793 | 0.11958 | -0.002953 | 0.049189 | -0.10566 | -0.050861 | -0.21596 | -0.23798 | 0.060509 | -0.006047 | 0.20991 | -0.005134 | -0.12555 | 121.4018 | 121.3619 | 121.4167 | 58.8836 | -121.5197 | 121.2296 | 121.4625 | 121.342 | 58.8825 | -121.6835
349.5312 | 121.5408 | -58.7769 | 62.6862 | 1.4211e-13 | -0.011252 | 0.002421 | 0.067767 | -0.0088606 | 0.06018 | 0.00030522 | -0.0016621 | -0.00021359 | 0.060766 | 0.024243 | 0.056155 | -58.6435 | 0.028878 | -58.7661 | 62.6524 | 62.6034 | 62.6582 | -58.8015 | -58.7026 | 0.018674 | -58.7646 | 62.4665 | 62.7085 | 62.5881 | -58.9745 | -0.024646 | -0.033732 | 0.13333 | 0.010793 | 0.035439 | -0.082742 | -0.027952 | -0.19762 | -0.21965 | 0.074264 | 0.012286 | 0.20991 | 0.022354 | -0.098067 | 121.4293 | 121.3803 | 121.4351 | 58.8057 | -121.4877 | 121.2434 | 121.4854 | 121.3649 | 58.7955 | -121.6606
351.2031 | 121.5088 | -58.6716 | 62.7823 | 1.4211e-13 | -0.011466 | 0.0019936 | 0.067767 | -0.0088606 | 0.06018 | 0.00030522 | -0.0018757 | 1.2e-08 | 0.060552 | 0.024671 | 0.056368 | -58.5428 | 0.033457 | -58.6699 | 62.7486 | 62.6996 | 62.7589 | -58.7008 | -58.5973 | 0.03241 | -58.6593 | 62.5672 | 62.8092 | 62.6934 | -58.8783 | -0.029195 | -0.033717 | 0.12877 | 0.001652 | 0.030847 | -0.082715 | -0.023354 | -0.20675 | -0.21506 | 0.074289 | 0.012311 | 0.21906 | 0.026952 | -0.08889 | 121.4201 | 121.3711 | 121.4305 | 58.705 | -121.4831 | 121.2388 | 121.4808 | 121.365 | 58.704 | -121.6606
352.8906 | 121.5042 | -58.5938 | 62.8693 | 1.4211e-13 | -0.011252 | 0.002421 | 0.067981 | -0.0082196 | 0.059967 | 0.0079357 | -0.0014485 | -0.00064099 | 0.060552 | 0.024457 | 0.055941 | -58.4283 | 0.028878 | -58.5646 | 62.8539 | 62.8049 | 62.8597 | -58.5954 | -58.4965 | 0.027831 | -58.5631 | 62.6725 | 62.91 | 62.7987 | -58.773 | -0.0017 | -0.015389 | 0.16541 | 0.029133 | 0.030833 | -0.064375 | -0.0096 | -0.17926 | -0.19673 | 0.097201 | 0.030644 | 0.2099 | 0.040706 | -0.070557 | 121.4476 | 121.3986 | 121.4534 | 58.6226 | -121.4647 | 121.2663 | 121.5037 | 121.3925 | 58.6216 | -121.6423
354.5938 | 121.4951 | -58.4473 | 63.0066 | 1.4211e-13 | -0.011252 | 0.002421 | 0.067554 | -0.008647 | 0.059967 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060338 | 0.024457 | 0.056155 | -58.3185 | 0.0243 | -58.441 | 62.9729 | 62.9285 | 62.9787 | -58.481 | -58.3775 | 0.018674 | -58.4441 | 62.7916 | 63.0382 | 62.9223 | -58.6585 | -0.033711 | -0.03368 | 0.12881 | 0.006262 | 0.039973 | -0.078073 | -0.027885 | -0.21127 | -0.21501 | 0.069763 | 0.003207 | 0.21448 | 0.031578 | -0.084264 | 121.4202 | 121.3758 | 121.426 | 58.4716 | -121.4876 | 121.2388 | 121.4854 | 121.3696 | 58.4659 | -121.6651
356.2812 | 121.5225 | -58.3191 | 63.1348 | 1.4211e-13 | -0.011466 | 0.0022072 | 0.067554 | -0.0084334 | 0.06018 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.024671 | 0.055727 | -58.2177 | 0.028878 | -58.3449 | 63.0736 | 63.0293 | 63.0794 | -58.3802 | -58.2676 | 0.023253 | -58.3387 | 62.9015 | 63.1297 | 63.0231 | -58.5486 | -0.061148 | -0.061129 | 0.10136 | -0.025768 | 0.03538 | -0.10551 | -0.05533 | -0.22956 | -0.2333 | 0.051478 | -0.019657 | 0.2099 | -0.005024 | -0.11171 | 121.3927 | 121.3483 | 121.3985 | 58.348 | -121.515 | 121.2206 | 121.4488 | 121.3421 | 58.3423 | -121.6834
357.9844 | 121.6278 | -58.1909 | 63.1714 | 1.4211e-13 | -0.011252 | 0.0022072 | 0.067554 | -0.0088606 | 0.059967 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060552 | 0.024884 | 0.055941 | -58.0987 | 0.033457 | -58.2167 | 63.2018 | 63.1391 | 63.1985 | -58.2612 | -58.1577 | 0.023253 | -58.2105 | 63.0113 | 63.2579 | 63.1375 | -58.425 | -0.07027 | 0.030444 | 0.092224 | -0.02575 | 0.04452 | -0.032238 | 0.027093 | -0.2341 | -0.16004 | 0.033193 | -0.019627 | 0.21447 | 0.086556 | -0.033865 | 121.3927 | 121.3301 | 121.3894 | 58.2244 | -121.4326 | 121.2023 | 121.4489 | 121.3284 | 58.2142 | -121.5964
359.6875 | 121.669 | -58.0399 | 63.3408 | 1.4211e-13 | -0.011679 | 0.002421 | 0.067554 | -0.008647 | 0.06018 | 0.015566 | -0.0016621 | -0.00042739 | 0.060766 | 0.024884 | 0.056155 | -57.9842 | 0.028878 | -58.1022 | 63.3163 | 63.2674 | 63.3221 | -58.1421 | -58.0433 | 0.018674 | -58.1007 | 63.1258 | 63.3724 | 63.2474 | -58.3151 | -0.10228 | -0.024468 | 0.055621 | -0.062355 | 0.039925 | -0.0734 | -0.018657 | -0.27527 | -0.21495 | -0.003401 | -0.0608 | 0.21447 | 0.031649 | -0.09335 | 121.3561 | 121.3072 | 121.362 | 58.0687 | -121.4829 | 121.1657 | 121.4123 | 121.2873 | 58.0585 | -121.6559
361.3906 | 121.5546 | -57.9529 | 63.4827 | 1.4211e-13 | -0.011466 | 0.0019936 | 0.068195 | -0.0088606 | 0.06018 | 0.015566 | -0.0014485 | -0.00064099 | 0.060552 | 0.024671 | 0.055941 | -57.8377 | 0.033457 | -57.9603 | 63.4628 | 63.4093 | 63.4732 | -57.991 | -57.8922 | 0.018674 | -57.9541 | 63.2815 | 63.5189 | 63.3985 | -58.1549 | -0.038151 | -0.019866 | 0.11515 | -0.007403 | 0.030748 | -0.07336 | -0.00947 | -0.20199 | -0.20119 | 0.060721 | -0.001256 | 0.20073 | 0.036257 | -0.084163 | 121.4157 | 121.3622 | 121.4261 | 57.9863 | -121.4737 | 121.2344 | 121.4718 | 121.3514 | 57.9716 | -121.6375
363.0625 | 121.5363 | -57.811 | 63.6383 | 1.4211e-13 | -0.011466 | 0.0022072 | 0.067767 | -0.0082196 | 0.059753 | 0.015566 | -0.0014485 | 1.2e-08 | 0.060552 | 0.024243 | 0.056155 | -57.7004 | 0.0243 | -57.8229 | 63.5864 | 63.5421 | 63.5968 | -57.8628 | -57.7594 | 0.027831 | -57.8305 | 63.4143 | 63.6563 | 63.5313 | -58.0404 | -0.051848 | -0.05189 | 0.1106 | -0.011962 | 0.039886 | -0.096211 | -0.041488 | -0.22942 | -0.22405 | 0.051597 | -0.019538 | 0.20989 | 0.017976 | -0.10702 | 121.3974 | 121.3531 | 121.4078 | 57.8353 | -121.5011 | 121.2252 | 121.4673 | 121.3423 | 57.8388 | -121.6787
364.7344 | 121.5088 | -57.6736 | 63.7894 | 1.4211e-13 | -0.011466 | 0.0019936 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060979 | 0.024457 | 0.056155 | -57.5676 | 0.028878 | -57.681 | 63.7329 | 63.6886 | 63.7388 | -57.7209 | -57.622 | 0.023253 | -57.6932 | 63.5562 | 63.7891 | 63.6686 | -57.8985 | -0.04723 | -0.056444 | 0.10604 | -0.007364 | 0.039866 | -0.10075 | -0.050613 | -0.22481 | -0.23318 | 0.051629 | -0.019506 | 0.2053 | -0.000307 | -0.12073 | 121.4066 | 121.3623 | 121.4124 | 57.7025 | -121.5102 | 121.2298 | 121.4627 | 121.3423 | 57.6969 | -121.6878
366.4531 | 121.5134 | -57.5455 | 63.913 | 1.4211e-13 | -0.011252 | 0.0022072 | 0.067767 | -0.008647 | 0.059967 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060766 | 0.024457 | 0.056368 | -57.4028 | 0.028878 | -57.5116 | 63.8932 | 63.8489 | 63.9036 | -57.556 | -57.4526 | 0.027831 | -57.5192 | 63.7119 | 63.9493 | 63.8289 | -57.7245 | -0.010563 | -0.019796 | 0.14269 | 0.033858 | 0.044421 | -0.064081 | -0.009379 | -0.17899 | -0.20111 | 0.092867 | 0.026311 | 0.2053 | 0.036348 | -0.084073 | 121.4386 | 121.3944 | 121.4491 | 57.5743 | -121.469 | 121.2573 | 121.4948 | 121.3744 | 57.5733 | -121.6374
368.125 | 121.5042 | -57.4081 | 64.0411 | 1.4211e-13 | -0.011679 | 0.0022072 | 0.067554 | -0.0084334 | 0.059967 | 0.00030522 | -0.0018757 | -0.00021359 | 0.060552 | 0.024457 | 0.056155 | -57.2608 | 0.033457 | -57.3743 | 64.0443 | 64.0046 | 64.0501 | -57.4095 | -57.3107 | 0.023253 | -57.3818 | 63.8629 | 64.1096 | 63.9937 | -57.5688 | -0.001366 | 0.003117 | 0.14729 | 0.033877 | 0.035243 | -0.036572 | 0.008962 | -0.16064 | -0.17819 | 0.097478 | 0.026344 | 0.18698 | 0.068425 | -0.047417 | 121.4524 | 121.4127 | 121.4582 | 57.4416 | -121.4506 | 121.2711 | 121.5177 | 121.4019 | 57.4314 | -121.6099
369.7969 | 121.5408 | -57.2342 | 64.2334 | 1.4211e-13 | -0.011679 | 0.002421 | 0.067981 | -0.008647 | 0.059753 | 0.00030522 | -0.0018757 | -0.00064099 | 0.060766 | 0.024884 | 0.056155 | -57.1098 | 0.028878 | -57.2278 | 64.1908 | 64.1511 | 64.1966 | -57.2584 | -57.1596 | 0.03241 | -57.2307 | 64.0095 | 64.2515 | 64.1357 | -57.4314 | -0.024212 | -0.042635 | 0.12443 | 0.006432 | 0.030644 | -0.082306 | -0.036783 | -0.19722 | -0.22394 | 0.074626 | 0.003491 | 0.20071 | 0.018102 | -0.09774 | 121.425 | 121.3853 | 121.4308 | 57.2631 | -121.4918 | 121.2437 | 121.4857 | 121.3699 | 57.2666 | -121.6648
371.5469 | 121.5912 | -56.955 | 64.4714 | 1.4211e-13 | -0.011466 | 0.0019936 | 0.06734 | -0.0084334 | 0.059967 | 0.00030522 | -0.0016621 | -0.00021359 | 0.060125 | 0.024457 | 0.056155 | -56.8946 | 0.028878 | -57.0126 | 64.4105 | 64.3526 | 64.4118 | -57.0478 | -56.9581 | 0.027831 | -57.0201 | 64.2246 | 64.4667 | 64.3509 | -57.2116 | -0.092817 | -0.06091 | 0.060378 | -0.057624 | 0.035193 | -0.11887 | -0.059626 | -0.25668 | -0.24679 | -0.003147 | -0.065124 | 0.19155 | -0.004742 | -0.12058 | 121.3655 | 121.3075 | 121.3668 | 56.9838 | -121.5192 | 121.1796 | 121.4216 | 121.3058 | 56.9828 | -121.6831
373.2188 | 121.6187 | -56.8039 | 64.6179 | 1.4211e-13 | -0.011679 | 0.0022072 | 0.067554 | -0.008647 | 0.059326 | 0.00030522 | -0.0016621 | -0.00085459 | 0.060338 | 0.024671 | 0.055941 | -56.7389 | 0.028878 | -56.8615 | 64.5753 | 64.5266 | 64.5766 | -56.8875 | -56.7841 | 0.023253 | -56.8598 | 64.3803 | 64.6224 | 64.5111 | -57.056 | -0.083617 | -0.042572 | 0.064981 | -0.057603 | 0.026014 | -0.091356 | -0.041281 | -0.25206 | -0.2376 | 0.019782 | -0.055932 | 0.19613 | 0.004447 | -0.10682 | 121.3792 | 121.3305 | 121.3805 | 56.8328 | -121.5054 | 121.1842 | 121.4263 | 121.315 | 56.8271 | -121.6739
374.9062 | 121.6232 | -56.6254 | 64.7415 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067554 | -0.0088606 | 0.059753 | 0.00030522 | -0.0014485 | -0.00064099 | 0.060552 | 0.024671 | 0.056155 | -56.5695 | 0.033457 | -56.6875 | 64.7402 | 64.696 | 64.7369 | -56.7044 | -56.6147 | 0.023253 | -56.6858 | 64.5589 | 64.7964 | 64.6851 | -56.882 | -0.078988 | -0.001346 | 0.055853 | -0.062156 | 0.016832 | -0.045532 | -0.004626 | -0.25659 | -0.18264 | 0.010666 | -0.060469 | 0.19612 | 0.054838 | -0.056426 | 121.3655 | 121.3213 | 121.3623 | 56.6588 | -121.4459 | 121.1842 | 121.4217 | 121.3105 | 56.6486 | -121.6235
376.6094 | 121.5088 | -56.4835 | 65.0024 | 1.4211e-13 | -0.011679 | 0.002421 | 0.067767 | -0.0088606 | 0.059967 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060552 | 0.024671 | 0.056155 | -56.3635 | 0.028878 | -56.4815 | 64.9416 | 64.8929 | 64.9383 | -56.5075 | -56.4178 | 0.027831 | -56.489 | 64.7558 | 64.9932 | 64.882 | -56.6805 | -0.024001 | -0.060822 | 0.11997 | 0.001959 | 0.02596 | -0.10956 | -0.064092 | -0.19703 | -0.24669 | 0.065644 | -0.005491 | 0.19154 | -0.009208 | -0.12047 | 121.4251 | 121.3763 | 121.4218 | 56.5123 | -121.5099 | 121.2392 | 121.4767 | 121.3654 | 56.5113 | -121.6829
378.2812 | 121.4951 | -56.2683 | 65.1947 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067554 | -0.0084334 | 0.059753 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060552 | 0.024884 | 0.055727 | -56.162 | 0.0243 | -56.2801 | 65.1476 | 65.0989 | 65.1535 | -56.3106 | -56.2118 | 0.027831 | -56.2829 | 64.9709 | 65.1993 | 65.088 | -56.4744 | -0.042255 | -0.047056 | 0.10627 | -0.011744 | 0.030511 | -0.095773 | -0.041159 | -0.20613 | -0.22376 | 0.056538 | -0.014597 | 0.19154 | 0.004569 | -0.1067 | 121.416 | 121.3672 | 121.4219 | 56.2926 | -121.5053 | 121.2393 | 121.4676 | 121.3563 | 56.2961 | -121.6691
379.9688 | 121.55 | -56.0577 | 65.3641 | 1.4211e-13 | -0.011893 | 0.0019936 | 0.067767 | -0.0088606 | 0.059753 | 0.0079357 | -0.0016621 | -0.00042739 | 0.060766 | 0.024671 | 0.056155 | -55.9652 | 0.033457 | -56.0878 | 65.3491 | 65.2958 | 65.3458 | -56.1183 | -56.0195 | 0.018674 | -56.0952 | 65.1541 | 65.4007 | 65.2849 | -56.2821 | -0.060513 | -0.01498 | 0.092573 | -0.030029 | 0.030484 | -0.068252 | -0.018231 | -0.22439 | -0.20999 | 0.038272 | -0.037442 | 0.18695 | 0.036654 | -0.079188 | 121.4068 | 121.3536 | 121.4036 | 56.0912 | -121.4823 | 121.2118 | 121.4585 | 121.3426 | 56.0764 | -121.6462
381.6562 | 121.5958 | -55.8014 | 65.6021 | 1.4211e-13 | -0.011679 | 0.002421 | 0.06734 | -0.008647 | 0.059539 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.024457 | 0.056155 | -55.782 | 0.038035 | -55.8909 | 65.546 | 65.4927 | 65.5427 | -55.9168 | -55.8272 | 0.03241 | -55.8937 | 65.3555 | 65.5885 | 65.4772 | -56.0852 | -0.11539 | -0.056146 | 0.019362 | -0.08951 | 0.025877 | -0.1094 | -0.059388 | -0.28385 | -0.24658 | -0.02577 | -0.092326 | 0.19152 | -0.01366 | -0.12492 | 121.3474 | 121.2941 | 121.3441 | 55.8394 | -121.5189 | 121.1569 | 121.3898 | 121.2786 | 55.8338 | -121.6874
383.3281 | 121.5912 | -55.5542 | 65.831 | 1.4211e-13 | -0.011679 | 0.0022072 | 0.067767 | -0.008647 | 0.06018 | 0.00030522 | -0.0020893 | -0.00042739 | 0.060979 | 0.025312 | 0.055941 | -55.5256 | 0.033457 | -55.6391 | 65.7886 | 65.7446 | 65.7991 | -55.6649 | -55.5799 | 0.027831 | -55.6419 | 65.6074 | 65.8449 | 65.729 | -55.8334 | -0.11074 | -0.042373 | 0.028559 | -0.084897 | 0.025842 | -0.086436 | -0.031868 | -0.27921 | -0.22364 | -0.025712 | -0.08769 | 0.19152 | 0.01386 | -0.10198 | 121.3428 | 121.2988 | 121.3533 | 55.5877 | -121.4959 | 121.1616 | 121.3991 | 121.2832 | 55.582 | -121.6644
385.0625 | 121.4996 | -55.4169 | 66.0461 | 1.4211e-13 | -0.011466 | 0.0019936 | 0.067767 | -0.0088606 | 0.06018 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060552 | 0.024243 | 0.056155 | -55.3425 | 0.028878 | -55.456 | 65.9809 | 65.9277 | 65.9777 | -55.4864 | -55.4013 | 0.027831 | -55.4587 | 65.7905 | 66.0372 | 65.9122 | -55.6503 | -0.06949 | -0.06523 | 0.074365 | -0.039095 | 0.030395 | -0.11843 | -0.068451 | -0.23339 | -0.25565 | 0.015528 | -0.04187 | 0.19152 | -0.008988 | -0.13399 | 121.3978 | 121.3446 | 121.3946 | 55.4457 | -121.5325 | 121.2074 | 121.454 | 121.329 | 55.4447 | -121.6964
386.7344 | 121.4996 | -55.22 | 66.2613 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067767 | -0.0090744 | 0.059753 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060766 | 0.024884 | 0.056582 | -55.1319 | 0.033457 | -55.2454 | 66.2007 | 66.1475 | 66.1929 | -55.2757 | -55.1816 | 0.03241 | -55.2573 | 66.0011 | 66.2523 | 66.1411 | -55.4351 | -0.055697 | -0.060616 | 0.088133 | -0.025332 | 0.030365 | -0.11379 | -0.068406 | -0.21502 | -0.26019 | 0.038468 | -0.037245 | 0.17777 | -0.008943 | -0.12021 | 121.4207 | 121.3675 | 121.4129 | 55.2535 | -121.537 | 121.2211 | 121.4724 | 121.3611 | 55.2524 | -121.6963
388.4062 | 121.55 | -54.95 | 66.4764 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067767 | -0.0088606 | 0.059753 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060552 | 0.024457 | 0.056155 | -54.8755 | 0.033457 | -54.9844 | 66.4616 | 66.4131 | 66.463 | -55.001 | -54.916 | 0.03241 | -54.9871 | 66.2758 | 66.5179 | 66.4021 | -55.1695 | -0.051043 | -0.014796 | 0.074442 | -0.034451 | 0.016592 | -0.063359 | -0.013417 | -0.21953 | -0.20063 | 0.033953 | -0.037182 | 0.18235 | 0.041468 | -0.074374 | 121.4116 | 121.363 | 121.413 | 54.9834 | -121.4774 | 121.2258 | 121.4679 | 121.352 | 54.9824 | -121.6459
390.1094 | 121.6187 | -54.5975 | 66.8152 | 1.4211e-13 | -0.011679 | 0.0026346 | 0.067554 | -0.0088606 | 0.059753 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060766 | 0.025098 | 0.056368 | -54.555 | 0.028878 | -54.6548 | 66.773 | 66.729 | 66.7789 | -54.6805 | -54.6046 | 0.036989 | -54.6712 | 66.5963 | 66.8384 | 66.718 | -54.8444 | -0.082996 | -0.042212 | 0.042451 | -0.057293 | 0.025703 | -0.08616 | -0.036239 | -0.24691 | -0.21888 | -0.007173 | -0.073729 | 0.17318 | 0.023224 | -0.097197 | 121.3704 | 121.3265 | 121.3764 | 54.6264 | -121.4957 | 121.1938 | 121.4359 | 121.3155 | 54.6345 | -121.6596
391.7812 | 121.5546 | -54.3549 | 67.1036 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067554 | -0.0088606 | 0.06018 | 0.0079357 | -0.0016621 | -0.00064099 | 0.060979 | 0.024671 | 0.055941 | -54.2712 | 0.047193 | -54.3846 | 67.0568 | 67.0038 | 67.0537 | -54.4057 | -54.3208 | 0.03241 | -54.3919 | 66.8664 | 67.1131 | 66.9881 | -54.5651 | -0.050876 | -0.046743 | 0.083696 | -0.029789 | 0.021087 | -0.099815 | -0.049914 | -0.21022 | -0.23714 | 0.034092 | -0.037043 | 0.17318 | 0.009549 | -0.11545 | 121.4117 | 121.3586 | 121.4085 | 54.4021 | -121.5093 | 121.2213 | 121.468 | 121.343 | 54.3873 | -121.6687
393.5 | 121.6232 | -53.9749 | 67.4286 | 1.4211e-13 | -0.011679 | 0.0019936 | 0.067554 | -0.0084334 | 0.059967 | 0.015566 | -0.0014485 | -0.00064099 | 0.060552 | 0.025098 | 0.056155 | -53.9232 | 0.042614 | -54.0367 | 67.4048 | 67.3563 | 67.4016 | -54.0669 | -53.9728 | 0.027831 | -54.0485 | 67.2236 | 67.4611 | 67.3453 | -54.2308 | -0.091978 | -0.023797 | 0.05171 | -0.061783 | 0.030195 | -0.07225 | -0.026952 | -0.25591 | -0.20503 | 0.002131 | -0.073583 | 0.18232 | 0.032511 | -0.083331 | 121.3797 | 121.3313 | 121.3766 | 54.0175 | -121.4955 | 121.1985 | 121.436 | 121.3202 | 54.0027 | -121.6594
395.1719 | 121.5958 | -53.6728 | 67.749 | 1.4211e-13 | -0.011893 | 0.002421 | 0.067767 | -0.0090744 | 0.059967 | 0.0079357 | -0.0018757 | -0.00064099 | 0.060552 | 0.024884 | 0.056155 | -53.6119 | 0.038035 | -53.7254 | 67.7299 | 67.6723 | 67.7221 | -53.7372 | -53.6614 | 0.036989 | -53.728 | 67.5257 | 67.777 | 67.6612 | -53.9057 | -0.06442 | -0.019166 | 0.060917 | -0.052584 | 0.011836 | -0.076738 | -0.026884 | -0.23294 | -0.22328 | 0.011359 | -0.055197 | 0.17774 | 0.028001 | -0.087842 | 121.4026 | 121.3451 | 121.3949 | 53.7108 | -121.4862 | 121.1985 | 121.4498 | 121.334 | 53.7098 | -121.6547
396.8594 | 121.5775 | -53.3615 | 68.0374 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067554 | -0.0090744 | 0.059539 | -0.0073253 | -0.0016621 | -0.00042739 | 0.060766 | 0.024884 | 0.055941 | -53.3234 | 0.038035 | -53.4324 | 68.0137 | 67.9699 | 68.0106 | -53.4487 | -53.3776 | 0.027831 | -53.4487 | 67.8142 | 68.0746 | 67.9451 | -53.6127 | -0.087228 | -0.023698 | 0.038075 | -0.070854 | 0.016374 | -0.0675 | -0.026824 | -0.25117 | -0.22323 | -0.016041 | -0.087176 | 0.16399 | 0.037218 | -0.09236 | 121.3752 | 121.3314 | 121.3721 | 53.3995 | -121.4862 | 121.1757 | 121.4361 | 121.3066 | 53.3893 | -121.6501
398.5625 | 121.55 | -52.9495 | 68.5043 | 1.4211e-13 | -0.011893 | 0.002421 | 0.067554 | -0.0090744 | 0.059967 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060552 | 0.024671 | 0.056368 | -52.8519 | 0.042614 | -52.9745 | 68.4853 | 68.4324 | 68.4776 | -52.9771 | -52.9014 | 0.041567 | -52.9771 | 68.2812 | 68.5371 | 68.4212 | -53.1456 | -0.027585 | -0.019042 | 0.097662 | -0.025013 | 0.002572 | -0.071947 | -0.026724 | -0.19612 | -0.22314 | 0.048158 | -0.027556 | 0.16856 | 0.032739 | -0.083104 | 121.4348 | 121.3819 | 121.4271 | 52.9921 | -121.4814 | 121.2307 | 121.4866 | 121.3708 | 52.9911 | -121.65
400.2344 | 121.5088 | -52.6108 | 68.8751 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067126 | -0.008647 | 0.059753 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060552 | 0.025098 | 0.055941 | -52.5497 | 0.042614 | -52.6586 | 68.7966 | 68.7483 | 68.7844 | -52.6795 | -52.5946 | 0.041567 | -52.6657 | 68.6017 | 68.8484 | 68.7326 | -52.8297 | -0.0687 | -0.078501 | 0.061091 | -0.047857 | 0.020843 | -0.12679 | -0.090747 | -0.21892 | -0.27343 | 0.016187 | -0.054948 | 0.16398 | -0.026705 | -0.14255 | 121.4074 | 121.3591 | 121.3952 | 52.6534 | -121.5546 | 121.2125 | 121.4592 | 121.3434 | 52.6523 | -121.7048
401.9219 | 121.6278 | -52.1347 | 69.2459 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067767 | -0.0088606 | 0.059753 | -0.0073253 | -0.0016621 | -0.00021359 | 0.060552 | 0.024671 | 0.056155 | -52.1147 | 0.042614 | -52.21 | 69.2453 | 69.1971 | 69.2422 | -52.217 | -52.1596 | 0.03241 | -52.2262 | 69.0458 | 69.2971 | 69.1767 | -52.3718 | -0.082303 | -0.000608 | 0.019964 | -0.075259 | 0.007044 | -0.048844 | -0.003676 | -0.23712 | -0.20011 | -0.02491 | -0.091466 | 0.14565 | 0.051209 | -0.069212 | 121.38 | 121.3318 | 121.3769 | 52.1773 | -121.4629 | 121.1805 | 121.4318 | 121.3114 | 52.1671 | -121.6177
403.5938 | 121.5866 | -51.5945 | 69.8364 | 1.4211e-13 | -0.012107 | 0.0019936 | 0.067767 | -0.0088606 | 0.059753 | 0.015566 | -0.0018757 | -0.00042739 | 0.060338 | 0.025098 | 0.056155 | -51.5836 | 0.042614 | -51.688 | 69.7672 | 69.7191 | 69.755 | -51.6904 | -51.6331 | 0.041567 | -51.7088 | 69.5723 | 69.8145 | 69.6987 | -51.8636 | -0.095888 | -0.069186 | 0.010895 | -0.093497 | 0.002391 | -0.11736 | -0.081387 | -0.26903 | -0.2641 | -0.03852 | -0.11423 | 0.1548 | -0.021924 | -0.13777 | 121.3618 | 121.3136 | 121.3496 | 51.6372 | -121.5269 | 121.1669 | 121.409 | 121.2932 | 51.6361 | -121.7
405.2656 | 121.4767 | -51.1459 | 70.34 | 1.4211e-13 | -0.011893 | 0.002421 | 0.067554 | -0.0084334 | 0.059539 | 0.00030522 | -0.0012349 | -0.00042739 | 0.060552 | 0.024884 | 0.055941 | -51.0526 | 0.042614 | -51.1615 | 70.3029 | 70.2548 | 70.2999 | -51.1547 | -51.0928 | 0.041567 | -51.1731 | 70.108 | 70.3594 | 70.2389 | -51.3233 | -0.008762 | -0.037055 | 0.09338 | -0.015603 | -0.006841 | -0.085168 | -0.040074 | -0.17734 | -0.23195 | 0.053159 | -0.027133 | 0.1502 | 0.01939 | -0.10103 | 121.4488 | 121.4007 | 121.4458 | 51.1885 | -121.4947 | 121.2539 | 121.5053 | 121.3849 | 51.1875 | -121.6632
406.9375 | 121.4951 | -50.7614 | 70.7245 | 1.4211e-13 | -0.011679 | 0.0022072 | 0.06734 | -0.0088606 | 0.059753 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060125 | 0.024884 | 0.056368 | -50.6268 | 0.038035 | -50.7266 | 70.7379 | 70.6898 | 70.7211 | -50.7243 | -50.667 | 0.046146 | -50.7472 | 70.5338 | 70.7897 | 70.6693 | -50.8837 | 0.037136 | 0.013371 | 0.13465 | 0.034813 | -0.002323 | -0.034691 | -0.003363 | -0.12229 | -0.19067 | 0.094458 | 0.014166 | 0.13646 | 0.065257 | -0.055164 | 121.4993 | 121.4512 | 121.4825 | 50.7994 | -121.4488 | 121.2952 | 121.5512 | 121.4307 | 50.8076 | -121.6082
408.6094 | 121.5408 | -50.1251 | 71.315 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067767 | -0.0088606 | 0.059753 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060338 | 0.024671 | 0.056155 | -50.059 | 0.047193 | -50.1681 | 71.3056 | 71.253 | 71.2889 | -50.1656 | -50.1038 | 0.055303 | -50.1749 | 71.1107 | 71.3575 | 71.2325 | -50.3159 | -0.040528 | -0.009424 | 0.066077 | -0.042929 | -0.002401 | -0.061998 | -0.026131 | -0.19081 | -0.2043 | 0.021348 | -0.049787 | 0.14102 | 0.042489 | -0.082511 | 121.4307 | 121.3781 | 121.414 | 50.1723 | -121.4807 | 121.2358 | 121.4826 | 121.3576 | 50.1804 | -121.6309
410.2812 | 121.6278 | -49.5392 | 71.8323 | 1.4211e-13 | -0.011466 | 0.0019936 | 0.067126 | -0.0090744 | 0.059539 | 0.00030522 | -0.0016621 | -0.00064099 | 0.060766 | 0.025098 | 0.056155 | -49.5417 | 0.042614 | -49.6507 | 71.8184 | 71.775 | 71.8108 | -49.6482 | -49.591 | 0.041567 | -49.6621 | 71.6189 | 71.8703 | 71.7499 | -49.7985 | -0.10905 | -0.013918 | -0.002503 | -0.11152 | -0.002474 | -0.057274 | -0.021444 | -0.25934 | -0.21336 | -0.051774 | -0.12291 | 0.13643 | 0.038019 | -0.082401 | 121.3575 | 121.3142 | 121.35 | 49.5818 | -121.4805 | 121.1581 | 121.4095 | 121.2891 | 49.5808 | -121.6308
411.9531 | 121.5271 | -48.9899 | 72.4319 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067554 | -0.0088606 | 0.059539 | 0.015566 | -0.0012349 | -0.00042739 | 0.060552 | 0.024671 | 0.055941 | -48.9511 | 0.047193 | -49.0555 | 72.4227 | 72.3703 | 72.4015 | -49.0484 | -48.9911 | 0.050725 | -49.076 | 72.2233 | 72.4747 | 72.3497 | -49.1987 | -0.058524 | -0.009241 | 0.038793 | -0.065661 | -0.007137 | -0.061685 | -0.030475 | -0.20883 | -0.20867 | -0.00128 | -0.086151 | 0.12268 | 0.042724 | -0.082276 | 121.4126 | 121.3601 | 121.3913 | 49.0371 | -121.4803 | 121.2131 | 121.4645 | 121.3395 | 49.0406 | -121.6306
413.6406 | 121.5088 | -48.175 | 73.2925 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067554 | -0.009288 | 0.059967 | -0.0073253 | -0.0016621 | -0.00042739 | 0.060552 | 0.024884 | 0.056155 | -48.1087 | 0.05635 | -48.1994 | 73.2789 | 73.2265 | 73.2622 | -48.1876 | -48.1395 | 0.055303 | -48.2198 | 73.0703 | 73.3217 | 73.2059 | -48.3379 | -0.012505 | -0.013679 | 0.066397 | -0.024341 | -0.011836 | -0.066022 | -0.030294 | -0.16284 | -0.22224 | 0.035541 | -0.044751 | 0.11808 | 0.029169 | -0.086673 | 121.4539 | 121.4016 | 121.4373 | 48.2314 | -121.4801 | 121.2453 | 121.4968 | 121.3809 | 48.2304 | -121.6304
415.3125 | 121.5317 | -47.2687 | 74.2081 | 1.4211e-13 | -0.01232 | 0.002421 | 0.067767 | -0.0088606 | 0.059753 | 0.015566 | -0.0014485 | -0.00042739 | 0.060766 | 0.024884 | 0.055941 | -47.1976 | 0.051771 | -47.2883 | 74.1991 | 74.1423 | 74.1825 | -47.2718 | -47.2421 | 0.050725 | -47.3086 | 73.9952 | 74.2512 | 74.1307 | -47.4313 | -0.003092 | -0.00895 | 0.071124 | -0.019636 | -0.016544 | -0.065764 | -0.025522 | -0.1626 | -0.21291 | 0.026596 | -0.03996 | 0.12264 | 0.043099 | -0.077322 | 121.4678 | 121.411 | 121.4512 | 47.3204 | -121.4798 | 121.2638 | 121.5198 | 121.3994 | 47.3194 | -121.6393
417 | 121.5225 | -46.6965 | 74.7986 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067981 | -0.0090744 | 0.059539 | -0.0073253 | -0.0016621 | -0.00064099 | 0.060766 | 0.024884 | 0.055941 | -46.7214 | 0.05635 | -46.8259 | 74.6799 | 74.6185 | 74.6541 | -46.7818 | -46.7522 | 0.055303 | -46.837 | 74.4622 | 74.7182 | 74.6069 | -46.9459 | -0.085352 | -0.11873 | -0.024929 | -0.12943 | -0.044082 | -0.18007 | -0.14444 | -0.24945 | -0.33642 | -0.055687 | -0.14056 | 0.10889 | -0.080399 | -0.19166 | 121.3763 | 121.315 | 121.3506 | 46.7528 | -121.5804 | 121.1586 | 121.4147 | 121.3034 | 46.7518 | -121.7445
418.7031 | 121.4859 | -46.1746 | 75.325 | 1.4211e-13 | -0.012107 | 0.0028484 | 0.067767 | -0.0088606 | 0.059539 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060552 | 0.024671 | 0.055727 | -46.0621 | 0.060928 | -46.1529 | 75.3437 | 75.2779 | 75.3135 | -46.127 | -46.102 | 0.064461 | -46.1777 | 75.1306 | 75.3867 | 75.2662 | -46.282 | 0.047584 | 0.018704 | 0.11251 | 0.021723 | -0.025861 | -0.047134 | -0.01155 | -0.10737 | -0.19439 | 0.07264 | -0.003073 | 0.1043 | 0.061649 | -0.058772 | 121.5183 | 121.4525 | 121.4881 | 46.2355 | -121.452 | 121.3052 | 121.5613 | 121.4409 | 46.2391 | -121.607
420.4219 | 121.6324 | -45.5017 | 75.9476 | 1.4211e-13 | -0.011679 | 0.002421 | 0.067554 | -0.009288 | 0.059753 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060552 | 0.024884 | 0.055727 | -45.499 | 0.05635 | -45.5943 | 75.9114 | 75.8502 | 75.8812 | -45.5684 | -45.5342 | 0.055303 | -45.6237 | 75.7075 | 75.9498 | 75.834 | -45.7096 | -0.0667 | -0.036135 | 0.002738 | -0.09264 | -0.02594 | -0.097327 | -0.066362 | -0.20793 | -0.24006 | -0.032513 | -0.12196 | 0.085971 | 0.002258 | -0.11358 | 121.4131 | 121.352 | 121.3829 | 45.5581 | -121.516 | 121.2092 | 121.4515 | 121.3357 | 45.557 | -121.6572
422.1094 | 121.6415 | -44.6594 | 76.7349 | 1.4211e-13 | -0.012107 | 0.0019936 | 0.067554 | -0.009288 | 0.059539 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060552 | 0.024884 | 0.056155 | -44.7115 | 0.060928 | -44.7977 | 76.7035 | 76.6516 | 76.6779 | -44.7671 | -44.7421 | 0.064461 | -44.8361 | 76.4996 | 76.7511 | 76.6261 | -44.9221 | -0.10767 | -0.031427 | -0.052064 | -0.1383 | -0.03063 | -0.083368 | -0.057038 | -0.26266 | -0.23533 | -0.082681 | -0.17671 | 0.085954 | 0.016161 | -0.10884 | 121.3629 | 121.311 | 121.3373 | 44.7204 | -121.502 | 121.159 | 121.4105 | 121.2855 | 44.7239 | -121.657
423.8281 | 121.5363 | -43.8446 | 77.6321 | 1.4211e-13 | -0.012107 | 0.0019936 | 0.067767 | -0.009288 | 0.059539 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060552 | 0.024884 | 0.055941 | -43.8233 | 0.060928 | -43.9187 | 77.6009 | 77.549 | 77.5753 | -43.8742 | -43.8584 | 0.055303 | -43.9387 | 77.3878 | 77.6439 | 77.5372 | -44.0246 | -0.029603 | -0.03128 | 0.021323 | -0.074094 | -0.044491 | -0.083116 | -0.056849 | -0.18004 | -0.24432 | -0.01381 | -0.094102 | 0.085933 | 0.011771 | -0.094914 | 121.4455 | 121.3936 | 121.4199 | 43.9055 | -121.5063 | 121.2324 | 121.4885 | 121.3818 | 43.8999 | -121.6568
425.5625 | 121.5271 | -43.0847 | 78.3875 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067767 | -0.0090744 | 0.059539 | 0.015566 | -0.0018757 | -0.00064099 | 0.060338 | 0.025098 | 0.055941 | -43.164 | 0.060928 | -43.2503 | 78.2647 | 78.2084 | 78.2346 | -43.2103 | -43.1899 | 0.064461 | -43.2794 | 78.0471 | 78.3032 | 78.1782 | -43.3561 | -0.12555 | -0.12272 | -0.079276 | -0.16555 | -0.040006 | -0.17906 | -0.15284 | -0.27141 | -0.34033 | -0.10521 | -0.19466 | 0.076759 | -0.08422 | -0.20922 | 121.3494 | 121.2931 | 121.3193 | 43.1456 | -121.5977 | 121.1318 | 121.3879 | 121.2629 | 43.1492 | -121.7436
427.3281 | 121.5134 | -42.3431 | 79.1565 | 1.4211e-13 | -0.01232 | 0.0019936 | 0.067554 | -0.0090744 | 0.059326 | 0.00030522 | -0.0016621 | -0.00021359 | 0.060552 | 0.025098 | 0.055941 | -42.4406 | 0.070086 | -42.5315 | 78.9973 | 78.9502 | 78.9672 | -42.4822 | -42.4573 | 0.06904 | -42.5514 | 78.7843 | 79.0404 | 78.9245 | -42.6281 | -0.13907 | -0.15922 | -0.097468 | -0.18834 | -0.049265 | -0.20632 | -0.18931 | -0.28496 | -0.37223 | -0.11419 | -0.20822 | 0.076742 | -0.11611 | -0.23195 | 121.3404 | 121.2933 | 121.3103 | 42.4132 | -121.6387 | 121.1274 | 121.3835 | 121.2677 | 42.4122 | -121.7846
429.0312 | 121.5546 | -41.3773 | 80.04 | 1.4211e-13 | -0.01232 | 0.002421 | 0.06734 | -0.009288 | 0.059753 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060552 | 0.025098 | 0.055727 | -41.4013 | 0.060928 | -41.5014 | 80.0366 | 79.9667 | 80.002 | -41.4474 | -41.4454 | 0.064461 | -41.5303 | 79.8144 | 80.0797 | 79.9502 | -41.5887 | -0.070119 | -0.003414 | -0.024056 | -0.12411 | -0.053989 | -0.073281 | -0.038027 | -0.21145 | -0.22555 | -0.068176 | -0.15305 | 0.058403 | 0.039751 | -0.089827 | 121.4138 | 121.344 | 121.3792 | 41.4382 | -121.4874 | 121.1917 | 121.457 | 121.3274 | 41.4417 | -121.6287
430.7031 | 121.6049 | -40.6815 | 80.7083 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067981 | -0.0090744 | 0.059539 | 0.0079357 | -0.0010211 | -0.00042739 | 0.060552 | 0.025098 | 0.055941 | -40.7878 | 0.065507 | -40.8741 | 80.6638 | 80.6077 | 80.6292 | -40.8017 | -40.8136 | 0.078197 | -40.903 | 80.4417 | 80.7024 | 80.5728 | -40.9614 | -0.12029 | -0.04451 | -0.10635 | -0.19268 | -0.072392 | -0.10057 | -0.079093 | -0.27995 | -0.26664 | -0.13211 | -0.22156 | 0.058388 | -0.005894 | -0.13547 | 121.3453 | 121.2892 | 121.3107 | 40.747 | -121.5101 | 121.1231 | 121.3839 | 121.2543 | 40.7597 | -121.6697
432.4531 | 121.6049 | -39.592 | 81.8253 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067981 | -0.0090744 | 0.059753 | 0.0079357 | -0.0018757 | -0.00042739 | 0.060552 | 0.025098 | 0.056155 | -39.5333 | 0.060928 | -39.6197 | 81.9274 | 81.8578 | 81.8883 | -39.5517 | -39.559 | 0.064461 | -39.6622 | 81.7099 | 81.9707 | 81.8365 | -39.7022 | 0.040277 | 0.10218 | 0.058648 | -0.027713 | -0.06799 | 0.032537 | 0.063079 | -0.11026 | -0.11534 | 0.032974 | -0.070211 | 0.040044 | 0.14544 | 0.011279 | 121.5194 | 121.4498 | 121.4803 | 39.6529 | -121.377 | 121.3019 | 121.5627 | 121.4285 | 39.6564 | -121.5275
434.125 | 121.5729 | -38.3423 | 83.0795 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.06734 | -0.0090744 | 0.059539 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060766 | 0.025098 | 0.055727 | -38.5124 | 0.083821 | -38.5942 | 82.9576 | 82.8972 | 82.9185 | -38.5169 | -38.5334 | 0.078197 | -38.6274 | 82.7309 | 82.9963 | 82.8392 | -38.6674 | -0.17458 | -0.12195 | -0.17007 | -0.25187 | -0.077292 | -0.18232 | -0.16101 | -0.32514 | -0.3486 | -0.19109 | -0.28512 | 0.04002 | -0.08323 | -0.24028 | 121.2999 | 121.2395 | 121.2608 | 38.4261 | -121.5964 | 121.0732 | 121.3386 | 121.1815 | 38.4205 | -121.747
435.8125 | 121.5729 | -37.3856 | 84.0408 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.068195 | -0.009288 | 0.059539 | 0.0079357 | -0.0014485 | -0.00085459 | 0.060766 | 0.025312 | 0.055941 | -37.4639 | 0.074664 | -37.5457 | 84.006 | 83.9549 | 83.9624 | -37.4683 | -37.4849 | 0.082776 | -37.588 | 83.7748 | 84.054 | 83.9152 | -37.6097 | -0.082733 | -0.034807 | -0.078341 | -0.16017 | -0.07744 | -0.085893 | -0.078391 | -0.22416 | -0.26601 | -0.099291 | -0.20248 | 0.02168 | 0.013123 | -0.12561 | 121.3916 | 121.3405 | 121.348 | 37.4602 | -121.5091 | 121.1604 | 121.4395 | 121.3008 | 37.4683 | -121.6505
437.5469 | 121.5637 | -36.9507 | 84.4986 | 1.4211e-13 | -0.011893 | 0.0026346 | 0.067767 | -0.009288 | 0.059539 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060766 | 0.024884 | 0.055941 | -37.0427 | 0.079243 | -37.1337 | 84.4364 | 84.3716 | 84.3883 | -37.0516 | -37.0682 | 0.082776 | -37.1714 | 84.2098 | 84.4752 | 84.2311 | -37.193 | -0.10093 | -0.062202 | -0.092005 | -0.183 | -0.082076 | -0.12697 | -0.11034 | -0.24236 | -0.28882 | -0.1175 | -0.22069 | 0.02167 | -0.023409 | -0.26745 | 121.3871 | 121.3223 | 121.3389 | 37.0299 | -121.5502 | 121.1605 | 121.4259 | 121.1818 | 37.0335 | -121.6916
439.2188 | 121.5912 | -36.3007 | 85.1212 | 1.4211e-13 | -0.011679 | 0.002421 | 0.067554 | -0.0095016 | 0.059967 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060338 | 0.025312 | 0.055727 | -36.3056 | 0.0884 | -36.3874 | 85.1873 | 85.1226 | 85.1437 | -36.3144 | -36.3173 | 0.078197 | -36.4296 | 84.9607 | 85.2215 | 85.0919 | -36.4421 | -0.013744 | 0.066095 | -0.004909 | -0.086768 | -0.073024 | 0.001411 | 0.022567 | -0.14146 | -0.1605 | -0.01662 | -0.12896 | 0.012495 | 0.10034 | -0.029234 | 121.4879 | 121.4232 | 121.4444 | 36.3891 | -121.4356 | 121.2613 | 121.5222 | 121.3926 | 36.3789 | -121.5633
440.9688 | 121.582 | -36.0168 | 85.3592 | 1.4211e-13 | -0.012107 | 0.0026346 | 0.067981 | -0.009288 | 0.059539 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060766 | 0.025098 | 0.055941 | -36.0263 | 0.079243 | -36.1127 | 85.4665 | 85.4019 | 85.423 | -36.0305 | -36.0471 | 0.073618 | -36.1549 | 85.2354 | 85.5008 | 85.3621 | -36.172 | -0.013664 | 0.10734 | -0.009441 | -0.095884 | -0.08222 | 0.042689 | 0.063824 | -0.15512 | -0.12383 | -0.030289 | -0.13805 | 0.017067 | 0.1416 | 0.002867 | 121.4834 | 121.4187 | 121.4399 | 36.0961 | -121.3897 | 121.2522 | 121.5176 | 121.3789 | 36.0905 | -121.5312
442.6562 | 121.5134 | -36.7538 | 84.7366 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067981 | -0.009288 | 0.059539 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060552 | 0.025098 | 0.055727 | -36.7497 | 0.074664 | -36.8361 | 84.7431 | 84.6738 | 84.6996 | -36.754 | -36.7706 | 0.073618 | -36.8738 | 84.512 | 84.7774 | 84.6432 | -36.9046 | -0.000135 | 0.006513 | 0.004173 | -0.082253 | -0.082118 | -0.062801 | -0.037036 | -0.15073 | -0.22467 | -0.016726 | -0.11991 | 0.030821 | 0.040742 | -0.093415 | 121.497 | 121.4277 | 121.4534 | 36.8285 | -121.4906 | 121.2658 | 121.5312 | 121.3971 | 36.8275 | -121.6412
444.3906 | 121.6095 | -36.676 | 84.6954 | 1.4211e-13 | -0.011893 | 0.0019936 | 0.067554 | -0.0095016 | 0.059753 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060338 | 0.024884 | 0.055514 | -36.8412 | 0.083821 | -36.9368 | 84.6424 | 84.5685 | 84.5897 | -36.8547 | -36.8667 | 0.078197 | -36.9745 | 84.4021 | 84.6812 | 84.5333 | -36.9962 | -0.17869 | -0.053013 | -0.16521 | -0.26079 | -0.082104 | -0.12692 | -0.10572 | -0.32013 | -0.29336 | -0.1907 | -0.29846 | 0.021665 | -0.014211 | -0.1621 | 121.3184 | 121.2445 | 121.2657 | 36.7598 | -121.5502 | 121.0781 | 121.3572 | 121.2094 | 36.7542 | -121.6916
446.0625 | 121.5088 | -37.0377 | 84.4391 | 1.4211e-13 | -0.01232 | 0.002421 | 0.067554 | -0.0095016 | 0.059753 | 0.00030522 | -0.0016621 | 1.2e-08 | 0.060766 | 0.025098 | 0.055941 | -37.1984 | 0.074664 | -37.2802 | 84.2899 | 84.2297 | 84.2463 | -37.2119 | -37.2147 | 0.082776 | -37.3225 | 84.0633 | 84.3287 | 84.2037 | -37.335 | -0.17421 | -0.1492 | -0.1607 | -0.24253 | -0.068319 | -0.20941 | -0.19277 | -0.29733 | -0.37582 | -0.17705 | -0.28481 | 0.012516 | -0.11042 | -0.23542 | 121.3275 | 121.2673 | 121.284 | 37.1123 | -121.651 | 121.1009 | 121.3663 | 121.2413 | 37.1204 | -121.7741
447.7344 | 121.4905 | -37.381 | 84.1187 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067554 | -0.009288 | 0.059753 | 0.015566 | -0.0014485 | -0.00021359 | 0.060552 | 0.024884 | 0.055727 | -37.3998 | 0.065507 | -37.4771 | 84.0884 | 84.0282 | 84.054 | -37.4088 | -37.4116 | 0.073618 | -37.5194 | 83.8618 | 84.1272 | 83.9885 | -37.541 | -0.027785 | -0.030215 | -0.018822 | -0.096076 | -0.068291 | -0.090449 | -0.064638 | -0.16005 | -0.25684 | -0.03061 | -0.13837 | 0.021679 | 0.008561 | -0.13017 | 121.4694 | 121.4092 | 121.435 | 37.4465 | -121.5274 | 121.2428 | 121.5082 | 121.3695 | 37.4546 | -121.6597
449.4688 | 121.5775 | -37.2528 | 84.1644 | 1.4211e-13 | -0.012107 | 0.002421 | 0.068195 | -0.009288 | 0.059539 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060552 | 0.025098 | 0.055941 | -37.1388 | 0.060928 | -37.239 | 84.3402 | 84.2709 | 84.2921 | -37.1478 | -37.1735 | 0.073618 | -37.2767 | 84.1091 | 84.379 | 84.2403 | -37.3625 | 0.10504 | 0.17582 | 0.11397 | 0.013821 | -0.09122 | 0.10646 | 0.12767 | -0.10965 | -0.055377 | 0.07931 | -0.023876 | 0.085776 | 0.21461 | 0.075872 | 121.5931 | 121.5237 | 121.5449 | 37.3137 | -121.3122 | 121.3619 | 121.6318 | 121.4931 | 37.3264 | -121.5269
451.1406 | 121.6415 | -35.6598 | 85.7071 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067981 | -0.009288 | 0.059539 | -0.0073253 | -0.0010211 | -0.00021359 | 0.060979 | 0.024884 | 0.055727 | -35.6921 | 0.074664 | -35.7785 | 85.7962 | 85.7316 | 85.7481 | -35.7008 | -35.7129 | 0.06904 | -35.8252 | 85.565 | 85.835 | 85.7009 | -35.911 | -0.041037 | 0.089084 | -0.032274 | -0.11872 | -0.077688 | 0.024471 | 0.041005 | -0.25118 | -0.14208 | -0.053099 | -0.16544 | 0.085743 | 0.12794 | -0.006217 | 121.456 | 121.3914 | 121.4079 | 35.7345 | -121.4079 | 121.2248 | 121.4948 | 121.3607 | 35.7288 | -121.6181
452.875 | 121.5729 | -36.1633 | 85.2676 | 1.4211e-13 | -0.011893 | 0.0022072 | 0.067981 | -0.009288 | 0.059539 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060552 | 0.025098 | 0.055727 | -35.9713 | 0.05635 | -36.0578 | 85.5215 | 85.4522 | 85.478 | -35.9801 | -36.0013 | 0.064461 | -36.1091 | 85.2811 | 85.5603 | 85.4216 | -36.1811 | 0.18319 | 0.25383 | 0.19198 | 0.10554 | -0.077649 | 0.18461 | 0.21032 | -0.017795 | 0.013507 | 0.16198 | 0.054218 | 0.072013 | 0.29268 | 0.15394 | 121.6848 | 121.6156 | 121.6413 | 36.2197 | -121.2478 | 121.4445 | 121.7236 | 121.5849 | 36.2278 | -121.4488
454.6094 | 121.4813 | -36.3876 | 85.1028 | 1.4211e-13 | -0.01232 | 0.0022072 | 0.067767 | -0.009288 | 0.059539 | 0.015566 | -0.0012349 | 0.00021361 | 0.060552 | 0.024884 | 0.055727 | -36.388 | 0.070086 | -36.4653 | 85.1003 | 85.0264 | 85.0567 | -36.3922 | -36.4089 | 0.064461 | -36.5258 | 84.8691 | 85.1391 | 85.0003 | -36.5978 | -0.004611 | -0.002583 | -0.000345 | -0.077623 | -0.073012 | -0.076435 | -0.046116 | -0.21016 | -0.23376 | -0.021219 | -0.13814 | 0.072022 | 0.036241 | -0.1025 | 121.4879 | 121.414 | 121.4444 | 36.4577 | -121.4951 | 121.2567 | 121.5267 | 121.388 | 36.4521 | -121.7006
456.3594 | 121.5317 | -35.7513 | 85.7162 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067554 | -0.0095016 | 0.059539 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060338 | 0.024884 | 0.055514 | -35.8203 | 0.079243 | -35.893 | 85.6771 | 85.6079 | 85.6336 | -35.8153 | -35.8365 | 0.073618 | -35.9443 | 85.4506 | 85.7206 | 85.591 | -36.0163 | -0.063957 | -0.039111 | -0.068916 | -0.14163 | -0.077672 | -0.10832 | -0.082616 | -0.26494 | -0.2657 | -0.085171 | -0.19294 | 0.072008 | 0.004319 | -0.12526 | 121.4285 | 121.3593 | 121.385 | 35.8306 | -121.5315 | 121.2019 | 121.4719 | 121.3423 | 35.825 | -121.7325
458.0469 | 121.637 | -35.0281 | 86.3754 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067767 | -0.009288 | 0.059326 | 0.015566 | -0.0012349 | -0.00021359 | 0.060338 | 0.024884 | 0.055941 | -35.2068 | 0.083821 | -35.2886 | 86.2906 | 86.2169 | 86.2426 | -35.2063 | -35.2275 | 0.082776 | -35.3353 | 86.0549 | 86.3295 | 86.1908 | -35.4119 | -0.17823 | -0.084786 | -0.17868 | -0.26056 | -0.082336 | -0.1585 | -0.13284 | -0.38381 | -0.32052 | -0.19947 | -0.30723 | 0.076573 | -0.045906 | -0.18464 | 121.3187 | 121.245 | 121.2707 | 35.1119 | -121.5817 | 121.083 | 121.3576 | 121.2189 | 35.1109 | -121.7873
459.7344 | 121.6187 | -35.0555 | 86.3617 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067767 | -0.0088606 | 0.059753 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060766 | 0.025312 | 0.055514 | -34.9549 | 0.074664 | -35.0368 | 86.547 | 86.4825 | 86.4898 | -34.959 | -34.9803 | 0.073618 | -35.0835 | 86.3067 | 86.5722 | 86.4472 | -35.1555 | 0.096501 | 0.18534 | 0.1006 | 0.018708 | -0.077793 | 0.12081 | 0.12814 | -0.099928 | -0.054965 | 0.075246 | -0.027939 | 0.071989 | 0.21049 | 0.085494 | 121.6026 | 121.538 | 121.5454 | 35.1302 | -121.3207 | 121.3623 | 121.6277 | 121.5027 | 35.1292 | -121.5172
461.4688 | 121.6187 | -33.4534 | 87.9684 | 1.4211e-13 | -0.01232 | 0.0022072 | 0.067981 | -0.0088606 | 0.059753 | -0.014956 | -0.0014485 | -0.00042739 | 0.060338 | 0.025525 | 0.055727 | -33.5356 | 0.079243 | -33.6176 | 87.9618 | 87.902 | 87.9138 | -33.5304 | -33.5563 | 0.087354 | -33.6641 | 87.7306 | 88.0007 | 87.862 | -33.7223 | -0.077048 | -0.006692 | -0.082275 | -0.1642 | -0.08715 | -0.066472 | -0.054669 | -0.26893 | -0.2378 | -0.10295 | -0.21071 | 0.058219 | 0.032266 | -0.10647 | 121.4151 | 121.3553 | 121.3671 | 33.5326 | -121.4989 | 121.184 | 121.4541 | 121.3153 | 33.5407 | -121.6907
463.2188 | 121.4767 | -31.7963 | 89.7171 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067767 | -0.0090744 | 0.059539 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060338 | 0.025525 | 0.055514 | -31.6997 | 0.083821 | -31.7817 | 89.816 | 89.7381 | 89.759 | -31.6851 | -31.7157 | 0.091933 | -31.828 | 89.5758 | 89.8596 | 89.7117 | -31.8816 | 0.11115 | 0.098898 | 0.096555 | 0.014589 | -0.096566 | 0.02102 | 0.041851 | -0.08535 | -0.14133 | 0.080589 | -0.031754 | 0.053596 | 0.14252 | -0.005371 | 121.6123 | 121.5344 | 121.5552 | 31.8801 | -121.4022 | 121.372 | 121.6559 | 121.508 | 31.8882 | -121.5987
464.8906 | 121.4951 | -29.9652 | 91.5619 | 1.4211e-13 | -0.012534 | 0.0022072 | 0.067767 | -0.0090744 | 0.059539 | 0.015566 | -0.0016621 | -0.00021359 | 0.060552 | 0.025525 | 0.055727 | -29.9782 | 0.092979 | -30.0694 | 91.5421 | 91.4781 | 91.4805 | -29.9543 | -29.9895 | 0.087354 | -30.1202 | 91.2973 | 91.572 | 91.447 | -30.1554 | 0.010933 | -0.019838 | -0.013026 | -0.10419 | -0.11512 | -0.083777 | -0.081382 | -0.19019 | -0.2646 | -0.024292 | -0.15495 | 0.035241 | 0.010131 | -0.11487 | 121.5073 | 121.4433 | 121.4457 | 30.0582 | -121.5162 | 121.2625 | 121.5372 | 121.4122 | 30.0526 | -121.7173
466.6406 | 121.5912 | -28.4866 | 92.9443 | 1.4211e-13 | -0.01232 | 0.002421 | 0.067767 | -0.0088606 | 0.059539 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060766 | 0.025525 | 0.055727 | -28.8428 | 0.10214 | -28.9294 | 92.6821 | 92.6137 | 92.6297 | -28.8187 | -28.8631 | 0.096512 | -28.9755 | 92.4465 | 92.7212 | 92.4681 | -29.0153 | -0.33207 | -0.26227 | -0.35616 | -0.44277 | -0.1107 | -0.33065 | -0.3146 | -0.52864 | -0.49785 | -0.37651 | -0.48885 | 0.039793 | -0.22309 | -0.47629 | 121.1687 | 121.1003 | 121.1164 | 28.5888 | -121.763 | 120.9331 | 121.2079 | 120.9547 | 28.5831 | -121.9596
468.375 | 121.4905 | -26.6876 | 94.7479 | 1.4211e-13 | -0.012107 | 0.0026346 | 0.067767 | -0.0097152 | 0.059539 | -0.0073253 | -0.0014485 | -0.00021359 | 0.060552 | 0.025525 | 0.055514 | -26.5857 | 0.097557 | -26.6769 | 94.9484 | 94.8757 | 94.8778 | -26.5476 | -26.5967 | 0.087354 | -26.7182 | 94.6991 | 94.9785 | 94.8443 | -26.7396 | 0.14006 | 0.20045 | 0.10197 | 0.010728 | -0.12934 | 0.12775 | 0.12991 | -0.051982 | -0.048814 | 0.090944 | -0.030557 | 0.021425 | 0.23058 | 0.09642 | 121.636 | 121.5633 | 121.5655 | 26.7852 | -121.2955 | 121.3867 | 121.6661 | 121.532 | 26.775 | -121.4875
470.125 | 121.5042 | -26.1612 | 95.3751 | 1.4211e-13 | -0.012534 | 0.0022072 | 0.068195 | -0.009288 | 0.059967 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060552 | 0.025525 | 0.0553 | -26.4483 | 0.10671 | -26.5258 | 95.0995 | 95.0222 | 95.0289 | -26.4148 | -26.4456 | 0.11025 | -26.5762 | 94.8502 | 95.1342 | 94.9863 | -26.6022 | -0.25357 | -0.2756 | -0.28711 | -0.36462 | -0.11104 | -0.35286 | -0.34614 | -0.44105 | -0.52486 | -0.28439 | -0.41505 | 0.026 | -0.24089 | -0.38878 | 121.2607 | 121.1834 | 121.1901 | 26.2679 | -121.7898 | 121.0114 | 121.2954 | 121.1475 | 26.2714 | -121.9773
471.8125 | 121.4951 | -23.7808 | 97.7142 | 1.4211e-13 | -0.012107 | 0.002421 | 0.068195 | -0.0095016 | 0.059326 | 0.00030522 | -0.0010211 | -0.00021359 | 0.060552 | 0.025525 | 0.055514 | -24.1499 | 0.12961 | -24.2504 | 97.3887 | 97.3117 | 97.3091 | -24.1207 | -24.1516 | 0.1194 | -24.2869 | 97.1349 | 97.4235 | 97.2847 | -24.3037 | -0.3399 | -0.32558 | -0.36912 | -0.46958 | -0.12968 | -0.40257 | -0.40516 | -0.52285 | -0.57936 | -0.37082 | -0.50606 | 0.016789 | -0.29076 | -0.42949 | 121.1695 | 121.0925 | 121.0899 | 23.9104 | -121.835 | 120.9157 | 121.2043 | 121.0656 | 23.9002 | -122.0179
473.5469 | 121.5317 | -23.8266 | 97.673 | 1.4211e-13 | -0.012107 | 0.0022072 | 0.067981 | -0.009288 | 0.059326 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060979 | 0.025312 | 0.055514 | -23.7699 | 0.10671 | -23.875 | 97.7687 | 97.7009 | 97.7028 | -23.7453 | -23.7899 | 0.11483 | -23.916 | 97.5195 | 97.8127 | 97.5732 | -23.9236 | 0.081344 | 0.095625 | 0.056657 | -0.048387 | -0.12973 | 0.027837 | 0.029793 | -0.097032 | -0.15357 | 0.03667 | -0.089409 | 0.007623 | 0.13962 | -0.099843 | 121.5953 | 121.5275 | 121.5294 | 23.9333 | -121.4183 | 121.3461 | 121.6393 | 121.3998 | 23.9414 | -121.5967
475.2812 | 121.4676 | -21.8628 | 99.6918 | 1.4211e-13 | -0.012107 | 0.0026346 | 0.067767 | -0.009288 | 0.059539 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060766 | 0.025525 | 0.0553 | -22.2041 | 0.12045 | -22.3001 | 99.339 | 99.276 | 99.2596 | -22.1655 | -22.2057 | 0.12856 | -22.3409 | 99.0899 | 99.3785 | 99.2169 | -22.3531 | -0.30273 | -0.35273 | -0.34134 | -0.43726 | -0.13453 | -0.41575 | -0.43222 | -0.4903 | -0.60188 | -0.3429 | -0.47814 | 0.012165 | -0.31323 | -0.47486 | 121.2018 | 121.1388 | 121.1223 | 21.9832 | -121.8573 | 120.9527 | 121.2413 | 121.0797 | 21.9914 | -122.0449
476.9531 | 121.55 | -21.2769 | 100.1862 | 1.4211e-13 | -0.01232 | 0.002421 | 0.067981 | -0.009288 | 0.059326 | 0.00030522 | -0.0014485 | -0.00042739 | 0.060979 | 0.025312 | 0.055727 | -21.5952 | 0.12503 | -21.7003 | 99.9434 | 99.8667 | 99.8731 | -21.5703 | -21.6013 | 0.12856 | -21.7457 | 99.6942 | 99.9921 | 99.716 | -21.7533 | -0.29341 | -0.24276 | -0.31835 | -0.42345 | -0.13004 | -0.31945 | -0.31307 | -0.47642 | -0.49191 | -0.32445 | -0.46884 | 0.007572 | -0.19409 | -0.47018 | 121.2202 | 121.1436 | 121.1499 | 21.4019 | -121.7564 | 120.9711 | 121.2689 | 120.9928 | 21.4054 | -121.9394
478.625 | 121.6095 | -19.6747 | 101.7792 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067981 | -0.0095016 | 0.059539 | 0.015566 | -0.0018757 | -0.00021359 | 0.060979 | 0.025739 | 0.055514 | -19.8051 | 0.11587 | -19.8965 | 101.7473 | 101.6616 | 101.6633 | -19.7891 | -19.8019 | 0.11483 | -19.9463 | 101.4753 | 101.7777 | 101.6069 | -19.9584 | -0.11438 | -0.031896 | -0.13037 | -0.22178 | -0.1074 | -0.11753 | -0.11585 | -0.28369 | -0.30389 | -0.12719 | -0.27158 | 0.012108 | -0.001449 | -0.17223 | 121.422 | 121.3363 | 121.338 | 19.7906 | -121.5682 | 121.15 | 121.4524 | 121.2816 | 19.7895 | -121.7375
480.3594 | 121.5683 | -18.3884 | 103.0884 | 1.4211e-13 | -0.012107 | 0.002421 | 0.067981 | -0.0095016 | 0.059753 | 0.00030522 | -0.0018757 | -0.00042739 | 0.060552 | 0.025525 | 0.055727 | -18.4911 | 0.11587 | -18.5917 | 103.0567 | 102.9758 | 102.9728 | -18.4749 | -18.4924 | 0.1194 | -18.6413 | 102.7847 | 103.0918 | 102.8844 | -18.658 | -0.086546 | -0.031681 | -0.10269 | -0.20328 | -0.11674 | -0.11259 | -0.11558 | -0.26962 | -0.30365 | -0.10399 | -0.25297 | 0.016657 | 0.003406 | -0.20401 | 121.4451 | 121.3642 | 121.3612 | 18.5042 | -121.5633 | 121.1731 | 121.4802 | 121.2727 | 18.5078 | -121.7464
482.0938 | 121.6187 | -17.482 | 103.9764 | 1.4211e-13 | -0.011893 | 0.002421 | 0.067981 | -0.009288 | 0.059326 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060766 | 0.025312 | 0.055514 | -17.7036 | 0.12503 | -17.8225 | 103.8396 | 103.7496 | 103.7512 | -17.6919 | -17.7048 | 0.12398 | -17.8492 | 103.5722 | 103.8701 | 103.6948 | -17.8613 | -0.20992 | -0.13684 | -0.22158 | -0.3405 | -0.13058 | -0.22681 | -0.22528 | -0.37928 | -0.4042 | -0.22283 | -0.36722 | 0.012059 | -0.10629 | -0.28166 | 121.3216 | 121.2316 | 121.2332 | 17.607 | -121.6684 | 121.0542 | 121.3521 | 121.1768 | 17.606 | -121.8377
483.7656 | 121.4996 | -17.8116 | 103.6789 | 1.4211e-13 | -0.01232 | 0.0022072 | 0.067981 | -0.0097152 | 0.059753 | 0.015566 | -0.0014485 | -0.00021359 | 0.060552 | 0.025525 | 0.055514 | -17.8409 | 0.12045 | -17.9553 | 103.6931 | 103.6077 | 103.6092 | -17.843 | -17.8559 | 0.1194 | -18.0003 | 103.4349 | 103.7282 | 103.5666 | -18.017 | -0.031437 | 0.0142 | -0.029346 | -0.14369 | -0.11225 | -0.071209 | -0.069668 | -0.20537 | -0.24401 | -0.044337 | -0.18873 | 0.016642 | 0.049317 | -0.11231 | 121.5047 | 121.4193 | 121.4208 | 17.932 | -121.5219 | 121.2465 | 121.5398 | 121.3782 | 17.931 | -121.6959
485.4844 | 121.6141 | -17.5507 | 103.8895 | 1.4211e-13 | -0.01232 | 0.0026346 | 0.068195 | -0.0095016 | 0.059112 | 0.00030522 | -0.0016621 | -0.00021359 | 0.060979 | 0.025312 | 0.0553 | -17.4655 | 0.11129 | -17.5753 | 104.0731 | 103.9877 | 103.9892 | -17.463 | -17.4759 | 0.1194 | -17.6157 | 103.7966 | 104.1128 | 103.9146 | -17.6415 | 0.087688 | 0.18363 | 0.085157 | -0.024613 | -0.1123 | 0.09827 | 0.099785 | -0.090835 | -0.092884 | 0.074771 | -0.065044 | 0.025791 | 0.22335 | 0.025091 | 121.6238 | 121.5384 | 121.5399 | 17.662 | -121.3524 | 121.3472 | 121.6635 | 121.4652 | 17.6701 | -121.531
487.2344 | 121.6187 | -16.7038 | 104.7226 | 1.4211e-13 | -0.01232 | 0.002421 | 0.068409 | -0.009288 | 0.059112 | 0.00030522 | -0.0012349 | -0.00042739 | 0.060552 | 0.025525 | 0.055514 | -16.7696 | 0.11587 | -16.8931 | 104.7553 | 104.6792 | 104.6715 | -16.7807 | -16.7845 | 0.12398 | -16.9335 | 104.4971 | 104.795 | 104.5372 | -16.9455 | -0.076915 | 0.032685 | -0.065791 | -0.18931 | -0.1124 | -0.043442 | -0.051134 | -0.24172 | -0.2255 | -0.080707 | -0.22968 | 0.012038 | 0.07243 | -0.18535 | 121.4591 | 121.3829 | 121.3753 | 16.8197 | -121.5033 | 121.2009 | 121.4988 | 121.241 | 16.8278 | -121.6681
488.9219 | 121.6095 | -16.9235 | 104.5349 | 1.4211e-13 | -0.012534 | 0.0022072 | 0.068195 | -0.009288 | 0.059539 | -0.0073253 | -0.0014485 | -0.00021359 | 0.060766 | 0.025098 | 0.055086 | -16.9665 | 0.12045 | -17.0808 | 104.5676 | 104.4823 | 104.4746 | -16.9684 | -16.9768 | 0.1194 | -17.1212 | 104.3002 | 104.5981 | 104.3221 | -17.1378 | -0.044924 | 0.032654 | -0.042935 | -0.1573 | -0.11237 | -0.052653 | -0.06033 | -0.2143 | -0.2347 | -0.053286 | -0.19768 | 0.016621 | 0.063233 | -0.21286 | 121.4911 | 121.4058 | 121.3981 | 17.044 | -121.5034 | 121.2237 | 121.5217 | 121.2456 | 17.0429 | -121.6727
490.6562 | 121.6278 | -16.8594 | 104.5944 | 1.4211e-13 | -0.01232 | 0.0022072 | 0.067767 | -0.0090744 | 0.059112 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025312 | 0.0553 | -16.8657 | 0.11587 | -16.9847 | 104.6683 | 104.5876 | 104.5799 | -16.8631 | -16.8669 | 0.11483 | -17.0205 | 104.4009 | 104.7126 | 104.4594 | -17.0371 | -0.003695 | 0.073869 | -0.006297 | -0.12524 | -0.12154 | -0.006847 | -0.014532 | -0.17765 | -0.19348 | -0.007483 | -0.16104 | 0.016619 | 0.11819 | -0.13501 | 121.5277 | 121.447 | 121.4393 | 16.9753 | -121.4576 | 121.2604 | 121.572 | 121.3188 | 16.9743 | -121.6315
492.3906 | 121.4996 | -16.745 | 104.805 | 1.4211e-13 | -0.01232 | 0.0022072 | 0.067767 | -0.0095016 | 0.059326 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060979 | 0.025312 | 0.0553 | -16.8016 | 0.12045 | -16.916 | 104.7324 | 104.6517 | 104.6531 | -16.8082 | -16.8028 | 0.1194 | -16.9564 | 104.465 | 104.7676 | 104.5372 | -16.9684 | -0.063189 | -0.072605 | -0.056641 | -0.171 | -0.10781 | -0.15331 | -0.15185 | -0.22341 | -0.33995 | -0.057823 | -0.21137 | 0.012039 | -0.037439 | -0.26775 | 121.4774 | 121.3967 | 121.3981 | 16.8654 | -121.6132 | 121.21 | 121.5125 | 121.2822 | 16.8644 | -121.7734
494.0781 | 121.5637 | -16.0629 | 105.423 | 1.4211e-13 | -0.012107 | 0.0026346 | 0.068195 | -0.009288 | 0.059539 | 0.0079357 | -0.0012349 | -0.00042739 | 0.060552 | 0.025312 | 0.055727 | -16.0783 | 0.12045 | -16.1972 | 105.4558 | 105.3523 | 105.372 | -16.103 | -16.0885 | 0.11483 | -16.2329 | 105.1793 | 105.4864 | 105.2332 | -16.2633 | -0.040103 | 0.032799 | -0.015324 | -0.13428 | -0.094179 | -0.070719 | -0.050986 | -0.20034 | -0.24369 | -0.025612 | -0.17001 | 0.030337 | 0.06342 | -0.18978 | 121.5187 | 121.4152 | 121.4349 | 16.1834 | -121.526 | 121.2422 | 121.5493 | 121.2961 | 16.1778 | -121.6862
495.75 | 121.5683 | -15.7242 | 105.7388 | 1.4211e-13 | -0.01232 | 0.002421 | 0.068409 | -0.0095016 | 0.059539 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.025525 | 0.055086 | -15.7578 | 0.12503 | -15.8767 | 105.7625 | 105.6819 | 105.6742 | -15.7779 | -15.7726 | 0.12398 | -15.9216 | 105.4952 | 105.7977 | 105.6315 | -15.9428 | -0.053744 | 0.023694 | -0.033581 | -0.15255 | -0.098804 | -0.056894 | -0.064656 | -0.21857 | -0.24363 | -0.048426 | -0.1974 | 0.021172 | 0.058908 | -0.1073 | 121.4867 | 121.4061 | 121.3984 | 15.8492 | -121.5168 | 121.2194 | 121.5219 | 121.3557 | 15.8482 | -121.6816
497.4844 | 121.4859 | -15.2481 | 106.2515 | 1.4211e-13 | -0.01232 | 0.0026346 | 0.068409 | -0.0095016 | 0.059539 | 0.015566 | -0.00080746 | 0.00021361 | 0.060979 | 0.025312 | 0.0553 | -15.1946 | 0.11587 | -15.309 | 106.3348 | 106.2451 | 106.2465 | -15.2193 | -15.2003 | 0.1194 | -15.3538 | 106.0629 | 106.3655 | 106.1855 | -15.3704 | 0.02881 | 0.083297 | 0.053486 | -0.060915 | -0.089725 | -0.006381 | -0.005025 | -0.12229 | -0.18859 | 0.047839 | -0.10571 | 0.01658 | 0.11396 | -0.065983 | 121.5829 | 121.4933 | 121.4946 | 15.364 | -121.4708 | 121.311 | 121.6136 | 121.4337 | 15.3675 | -121.6219
499.2188 | 121.6507 | -29.3198 | 92.0334 | 1.4211e-13 | -0.012534 | 0.002421 | 0.068195 | -0.009288 | 0.059753 | -0.0073253 | -0.0014485 | -0.00021359 | 0.060338 | 0.025739 | 0.0553 | -29.0488 | 0.038035 | -29.1217 | 92.4944 | 92.4214 | 92.4557 | -29.0293 | -29.0692 | 0.046146 | -29.1861 | 92.3137 | 92.5335 | 92.3536 | -29.2076 | 0.29043 | 0.46097 | 0.27094 | 0.19807 | -0.092361 | 0.38799 | 0.42236 | 0.11218 | 0.28033 | 0.25058 | 0.13366 | 0.021483 | 0.50014 | 0.3202 | 121.8141 | 121.7411 | 121.7755 | 29.3578 | -121.0627 | 121.6335 | 121.8533 | 121.6733 | 29.3659 | -121.241
500.9531 | 121.6187 | -36.3876 | 84.9518 | 1.4211e-13 | -0.012748 | 0.002421 | 0.067981 | -0.0095016 | 0.059326 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060979 | 0.025312 | 0.055514 | -36.4246 | 0.038035 | -36.511 | 85.0591 | 84.9852 | 85.0247 | -36.4197 | -36.4501 | 0.041567 | -36.5441 | 84.8966 | 85.0887 | 84.9546 | -36.6253 | -0.032084 | 0.10727 | -0.036972 | -0.12341 | -0.091322 | 0.033416 | 0.072896 | -0.23764 | -0.055229 | -0.062428 | -0.15646 | 0.08118 | 0.13694 | 0.002781 | 121.4467 | 121.3728 | 121.4123 | 36.4257 | -121.3715 | 121.2842 | 121.4764 | 121.3422 | 36.4292 | -121.5771
502.6875 | 121.2112 | -62.0636 | 59.3079 | 1.4211e-13 | -0.012748 | 0.0022072 | 0.067554 | -0.0095016 | 0.059753 | 0.0079357 | -0.0014485 | -0.00042739 | 0.060338 | 0.025739 | 0.055941 | -61.8667 | -0.053537 | -62.0121 | 59.4521 | 59.4211 | 59.4944 | -62.1212 | -61.9352 | -0.054586 | -61.9971 | 59.289 | 59.4623 | 59.4197 | -62.2941 | -0.057623 | 0.14427 | 0.19689 | 0.051536 | 0.10916 | 0.1132 | 0.18653 | -0.23052 | -0.018832 | 0.12844 | 0.066461 | 0.29698 | 0.15442 | 0.11184 | 121.5157 | 121.4847 | 121.558 | 62.0101 | -121.4291 | 121.3526 | 121.5259 | 121.4833 | 62.009 | -121.602
504.4219 | 121.582 | -60.2005 | 61.1572 | 1.4211e-13 | -0.012748 | 0.00178 | 0.067554 | -0.009288 | 0.059539 | 0.00030522 | -0.0016621 | -0.00042739 | 0.060125 | 0.025525 | 0.055514 | -60.3558 | -0.007751 | -60.5012 | 60.8989 | 60.8634 | 60.9275 | -60.5323 | -60.4196 | -0.00422 | -60.4816 | 60.7816 | 60.9549 | 60.8482 | -60.774 | -0.33184 | -0.25832 | -0.15534 | -0.30073 | 0.031105 | -0.2938 | -0.22973 | -0.57345 | -0.37561 | -0.21911 | -0.28109 | 0.29237 | -0.20232 | -0.30901 | 121.0994 | 121.0639 | 121.128 | 60.1927 | -121.6896 | 120.9821 | 121.1554 | 121.0487 | 60.1963 | -121.9312
506.0938 | 121.4859 | -57.9941 | 63.4415 | 1.4211e-13 | -0.012961 | 0.0019936 | 0.067767 | -0.009288 | 0.059753 | 0.015566 | -0.0012349 | -0.00021359 | 0.060125 | 0.025525 | 0.055941 | -57.9064 | 0.010564 | -58.0427 | 63.3758 | 63.3452 | 63.4045 | -58.0643 | -57.97 | 0.009516 | -58.0274 | 63.254 | 63.4319 | 63.3252 | -58.306 | -0.070214 | -0.065657 | 0.087678 | -0.048614 | 0.0216 | -0.096266 | -0.03695 | -0.31189 | -0.18746 | 0.024082 | -0.033317 | 0.27857 | -0.009537 | -0.11622 | 121.3699 | 121.3393 | 121.3986 | 58.0046 | -121.5058 | 121.2481 | 121.426 | 121.3193 | 58.0036 | -121.7474
507.8281 | 121.5225 | -56.012 | 65.4236 | 1.4211e-13 | -0.012961 | 0.00178 | 0.067767 | -0.0095016 | 0.059753 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060125 | 0.025739 | 0.055514 | -56.0247 | 0.019721 | -56.1381 | 65.2758 | 65.2363 | 65.3001 | -56.164 | -56.0698 | 0.023253 | -56.141 | 65.1495 | 65.3275 | 65.2162 | -56.3966 | -0.15208 | -0.14774 | -0.012722 | -0.12617 | 0.025912 | -0.18729 | -0.12353 | -0.38464 | -0.27408 | -0.05787 | -0.129 | 0.25563 | -0.096113 | -0.20738 | 121.2878 | 121.2483 | 121.312 | 56.0317 | -121.5876 | 121.1615 | 121.3394 | 121.2282 | 56.0352 | -121.8202
509.5625 | 121.5271 | -55.0552 | 66.3666 | 1.4211e-13 | -0.012961 | 0.0019936 | 0.067981 | -0.0095016 | 0.059753 | -0.0073253 | -0.0014485 | -0.00042739 | 0.060338 | 0.025312 | 0.055727 | -54.9579 | 0.019721 | -55.0851 | 66.3426 | 66.3032 | 66.3623 | -55.0972 | -55.0076 | 0.018674 | -55.0833 | 66.2163 | 66.3989 | 66.2784 | -55.3297 | -0.041914 | -0.023971 | 0.097317 | -0.029887 | 0.012027 | -0.063391 | -0.004283 | -0.2745 | -0.15028 | 0.047664 | -0.028049 | 0.24645 | 0.032287 | -0.088134 | 121.3978 | 121.3584 | 121.4175 | 55.075 | -121.4637 | 121.2715 | 121.4541 | 121.3337 | 55.0739 | -121.6963
511.25 | 121.5775 | -52.7618 | 68.6783 | 1.4211e-13 | -0.012748 | 0.0022072 | 0.067554 | -0.0097152 | 0.059753 | 0.015566 | -0.0014485 | -0.00021359 | 0.060552 | 0.025525 | 0.055941 | -53.1128 | 0.051771 | -53.2309 | 68.1923 | 68.1668 | 68.2075 | -53.2289 | -53.1624 | 0.046146 | -53.2381 | 68.066 | 68.2532 | 68.1374 | -53.4616 | -0.46711 | -0.48601 | -0.35099 | -0.46908 | -0.001971 | -0.51148 | -0.47081 | -0.69974 | -0.61228 | -0.40051 | -0.47623 | 0.22351 | -0.42509 | -0.54093 | 120.9541 | 120.9287 | 120.9693 | 52.8136 | -121.9072 | 120.8278 | 121.015 | 120.8992 | 52.808 | -122.1399
512.9844 | 121.4584 | -48.967 | 72.5143 | 1.4211e-13 | -0.012748 | 0.0022072 | 0.067981 | -0.0095016 | 0.059753 | 0.0079357 | -0.0018757 | -0.00042739 | 0.060552 | 0.025739 | 0.055514 | -51.2677 | 0.11129 | -51.3813 | 70.0511 | 70.0304 | 70.0481 | -51.3562 | -51.2805 | 0.11025 | -51.3654 | 69.9386 | 70.1304 | 70.0237 | -51.5705 | -2.3892 | -2.4632 | -2.3008 | -2.4143 | -0.025125 | -2.4839 | -2.4663 | -2.6035 | -2.5757 | -2.3135 | -2.3984 | 0.20515 | -2.3839 | -2.4906 | 119.0181 | 118.9974 | 119.015 | 49.0783 | -123.8705 | 118.9056 | 119.0974 | 118.9907 | 49.0772 | -124.0849
514.7188 | 121.4127 | -9.7229 | 111.8866 | 1.4211e-13 | -0.012534 | 0.002421 | 0.067981 | -0.0095016 | 0.059326 | 0.015566 | -0.0014485 | 0.00021361 | 0.060979 | 0.025739 | 0.055086 | -9.7555 | 0.18913 | -9.8838 | 111.6961 | 111.6071 | 111.5897 | -9.8116 | -9.7562 | 0.19724 | -9.8823 | 111.4106 | 111.7225 | 111.4326 | -9.9766 | -0.088688 | -0.19048 | -0.032597 | -0.16086 | -0.072173 | -0.27953 | -0.29687 | -0.25365 | -0.47598 | -0.033283 | -0.15936 | 0.094292 | -0.16415 | -0.45397 | 121.419 | 121.33 | 121.3126 | 9.912 | -121.6982 | 121.1335 | 121.4454 | 121.1555 | 9.9201 | -121.8632
516.4531 | 121.3715 | -8.8623 | 112.6923 | 1.4211e-13 | -0.012534 | 0.002421 | 0.068409 | -0.0095016 | 0.059326 | 0.015566 | -0.0012349 | 0.00042721 | 0.060979 | 0.025312 | 0.054873 | -8.8398 | 0.16624 | -8.9269 | 112.5752 | 112.4862 | 112.478 | -8.9095 | -8.8496 | 0.17435 | -8.9574 | 112.2988 | 112.6061 | 112.1515 | -9.0699 | -0.047234 | -0.1171 | 0.022486 | -0.064595 | -0.017361 | -0.20604 | -0.21428 | -0.20764 | -0.39341 | 0.012706 | -0.095058 | 0.11258 | -0.08614 | -0.5408 | 121.4375 | 121.3485 | 121.3403 | 9.0285 | -121.6018 | 121.1612 | 121.4684 | 121.0138 | 9.0367 | -121.7622
518.125 | 121.4676 | -8.2397 | 113.1958 | 1.4211e-13 | -0.012534 | 0.002421 | 0.068195 | -0.0095016 | 0.059326 | 0.00030522 | -0.0016621 | 1.2e-08 | 0.060766 | 0.026167 | 0.054873 | -7.7959 | 0.1525 | -7.8739 | 113.5916 | 113.4936 | 113.4899 | -7.8839 | -7.7553 | 0.16061 | -7.9134 | 113.3061 | 113.6134 | 113.4289 | -8.0397 | 0.35589 | 0.39577 | 0.4438 | 0.36585 | 0.009965 | 0.29778 | 0.29405 | 0.20003 | 0.11031 | 0.48446 | 0.32633 | 0.1263 | 0.41761 | 0.23309 | 121.8313 | 121.7333 | 121.7296 | 8.3922 | -121.0797 | 121.5459 | 121.8532 | 121.6686 | 8.4004 | -121.2355
519.8594 | 121.4081 | -7.3334 | 114.093 | 1.4211e-13 | -0.012748 | 0.002421 | 0.068409 | -0.0097152 | 0.059326 | 0.00030522 | -0.0010211 | 0.00021361 | 0.060766 | 0.025525 | 0.054873 | -7.3015 | 0.15708 | -7.3886 | 114.0494 | 113.9606 | 113.9431 | -7.4077 | -7.2699 | 0.15604 | -7.4189 | 113.764 | 114.0804 | 113.7677 | -7.5544 | -0.074278 | -0.043611 | 0.031893 | -0.055224 | 0.019054 | -0.13238 | -0.14989 | -0.22099 | -0.32905 | 0.06343 | -0.085543 | 0.13544 | -0.012587 | -0.32531 | 121.3828 | 121.294 | 121.2765 | 7.4905 | -121.5007 | 121.0973 | 121.4138 | 121.1011 | 7.4894 | -121.6474
521.5312 | 121.4905 | -38.9008 | 83.2672 | 1.4211e-13 | -0.012961 | 0.00178 | 0.068195 | -0.009288 | 0.059967 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060552 | 0.025739 | 0.056155 | -45.4715 | -0.071851 | -45.6081 | 75.8473 | 75.8411 | 75.84 | -45.573 | -45.493 | -0.068322 | -45.5504 | 75.6846 | 75.8537 | 75.8386 | -45.7096 | -6.6722 | -7.4199 | -6.5707 | -6.7073 | -0.035096 | -7.4261 | -7.4272 | -6.8089 | -7.5826 | -6.5923 | -6.6497 | 0.15923 | -7.4135 | -7.4286 | 114.7481 | 114.7418 | 114.7408 | 38.8289 | -128.8402 | 114.5854 | 114.7544 | 114.7393 | 38.8324 | -128.9769
523.2812 | 121.3303 | -4.4174 | 116.9952 | 1.4211e-13 | -0.012534 | 0.002421 | 0.068195 | -0.0095016 | 0.059112 | 0.0079357 | -0.0016621 | 0.00021361 | 0.060766 | 0.025739 | 0.055086 | -4.5407 | 0.18913 | -4.6371 | 116.7507 | 116.653 | 116.6491 | -4.6649 | -4.5365 | 0.19724 | -4.6396 | 116.4653 | 116.7818 | 116.5652 | -4.8162 | -0.24746 | -0.24458 | -0.12329 | -0.21963 | 0.027825 | -0.3422 | -0.34615 | -0.39881 | -0.52996 | -0.11904 | -0.22222 | 0.17659 | -0.21343 | -0.43 | 121.1681 | 121.0705 | 121.0665 | 4.6065 | -121.6601 | 120.8827 | 121.1992 | 120.9827 | 4.6147 | -121.8115
525.0156 | 121.3211 | -6.0287 | 115.2969 | 1.4211e-13 | -0.01232 | 0.0026346 | 0.067981 | -0.0097152 | 0.059112 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.025739 | 0.054873 | -5.7219 | 0.15708 | -5.832 | 115.542 | 115.4442 | 115.4358 | -5.8508 | -5.7315 | 0.16977 | -5.8347 | 115.2474 | 115.5685 | 115.2558 | -5.993 | 0.17793 | 0.24502 | 0.30681 | 0.19677 | 0.018836 | 0.14727 | 0.13882 | 0.035765 | -0.049539 | 0.29725 | 0.19407 | 0.1583 | 0.27154 | -0.041181 | 121.5707 | 121.473 | 121.4645 | 6.1858 | -121.1478 | 121.2761 | 121.5972 | 121.2845 | 6.1985 | -121.2899
526.75 | 121.1563 | -4.6555 | 116.6382 | 1.4211e-13 | -0.01232 | 0.0026346 | 0.067981 | -0.0090744 | 0.059112 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025739 | 0.055086 | -4.4949 | 0.19371 | -4.5638 | 116.6637 | 116.566 | 116.5529 | -4.6649 | -4.4952 | 0.16977 | -4.5984 | 116.3737 | 116.6857 | 116.4462 | -4.7659 | -0.009419 | 0.025482 | 0.16053 | 0.091658 | 0.10108 | -0.072143 | -0.085249 | -0.1104 | -0.26448 | 0.16021 | 0.057026 | 0.16743 | 0.047472 | -0.19199 | 121.3191 | 121.2215 | 121.2084 | 4.8492 | -121.3031 | 121.0292 | 121.3411 | 121.1016 | 4.8252 | -121.404
528.4844 | 121.2891 | -2.7374 | 118.5837 | 1.4211e-13 | -0.01232 | 0.002421 | 0.068409 | -0.009288 | 0.059112 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025525 | 0.054659 | -2.778 | 0.19371 | -2.8378 | 118.4309 | 118.3335 | 118.3157 | -2.9524 | -2.7782 | 0.16519 | -2.8723 | 118.1364 | 118.4576 | 118.0808 | -3.0625 | -0.21493 | -0.15275 | -0.040607 | -0.10036 | 0.11457 | -0.25017 | -0.26798 | -0.32511 | -0.44725 | -0.040802 | -0.13483 | 0.19028 | -0.1261 | -0.50293 | 121.1684 | 121.0709 | 121.0531 | 2.9311 | -121.536 | 120.8739 | 121.195 | 120.8182 | 2.9026 | -121.6462
530.1562 | 121.2616 | -5.1132 | 116.1209 | 1.4211e-13 | -0.012961 | 0.002421 | 0.068195 | -0.0095016 | 0.059326 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.025739 | 0.054659 | -4.3164 | 0.14334 | -4.3807 | 116.8651 | 116.7629 | 116.7681 | -4.4588 | -4.3213 | 0.12398 | -4.4199 | 116.5614 | 116.8825 | 116.4096 | -4.601 | 0.6544 | 0.7442 | 0.79685 | 0.73255 | 0.078158 | 0.64202 | 0.64722 | 0.5122 | 0.44051 | 0.79197 | 0.69336 | 0.18116 | 0.76162 | 0.28865 | 121.9783 | 121.8762 | 121.8813 | 5.2566 | -120.5797 | 121.6746 | 121.9958 | 121.5228 | 5.2372 | -120.7219
531.8906 | 121.2296 | -3.4012 | 118.0344 | 1.4211e-13 | -0.01232 | 0.0026346 | 0.068195 | -0.009288 | 0.059112 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060125 | 0.025739 | 0.054873 | -2.8467 | 0.17539 | -2.8881 | 118.3439 | 118.2511 | 118.2379 | -3.0027 | -2.8286 | 0.15604 | -2.9272 | 118.0586 | 118.366 | 118.1174 | -3.1175 | 0.39846 | 0.30957 | 0.55447 | 0.51304 | 0.11458 | 0.21672 | 0.2035 | 0.2837 | 0.024231 | 0.57259 | 0.47398 | 0.19028 | 0.33164 | 0.083018 | 121.7451 | 121.6523 | 121.639 | 3.5766 | -121.0371 | 121.4598 | 121.7672 | 121.5186 | 3.5572 | -121.1518
533.6406 | 121.1792 | -5.3192 | 115.9012 | 1.4211e-13 | -0.012748 | 0.0026346 | 0.068409 | -0.009929 | 0.059112 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060552 | 0.025525 | 0.054873 | -4.7696 | 0.12503 | -4.8385 | 116.3569 | 116.2547 | 116.2553 | -4.9167 | -4.7745 | 0.13314 | -4.8823 | 116.0624 | 116.3789 | 116.1074 | -5.0543 | 0.4025 | 0.45573 | 0.54958 | 0.48072 | 0.078222 | 0.35349 | 0.35414 | 0.26489 | 0.16119 | 0.54467 | 0.4369 | 0.17202 | 0.47771 | 0.20619 | 121.6761 | 121.5739 | 121.5745 | 5.4442 | -120.8179 | 121.3816 | 121.6981 | 121.4266 | 5.4524 | -120.9555
535.375 | 121.1975 | -5.1819 | 115.8691 | 1.4211e-13 | -0.012748 | 0.002421 | 0.067981 | -0.0095016 | 0.058898 | 0.023196 | -0.0010211 | 0.00021361 | 0.060338 | 0.025739 | 0.054659 | -4.8978 | 0.12961 | -4.953 | 116.1738 | 116.0715 | 116.0676 | -5.0358 | -4.8524 | 0.13772 | -4.9876 | 115.8655 | 116.1912 | 115.8784 | -5.1551 | 0.14612 | 0.30464 | 0.28406 | 0.22893 | 0.082817 | 0.20238 | 0.19846 | 0.026825 | -0.003647 | 0.3295 | 0.19426 | 0.16744 | 0.32203 | 0.009304 | 121.3557 | 121.2534 | 121.2495 | 5.3115 | -120.9049 | 121.0474 | 121.3731 | 121.0603 | 5.3196 | -121.0242
537.0469 | 121.0281 | -5.658 | 115.3244 | 1.4211e-13 | -0.012961 | 0.0022072 | 0.068195 | -0.009929 | 0.059112 | 0.00030522 | -0.0010211 | 0.00021361 | 0.060338 | 0.025739 | 0.055086 | -5.6166 | 0.13876 | -5.6901 | 115.3405 | 115.2565 | 115.2435 | -5.7455 | -5.5758 | 0.1423 | -5.7248 | 115.0551 | 115.3716 | 115.1596 | -5.8785 | -0.087544 | 0.01611 | 0.041325 | -0.032097 | 0.055447 | -0.067933 | -0.080947 | -0.22055 | -0.2693 | 0.082138 | -0.066835 | 0.15372 | 0.047195 | -0.1648 | 120.9985 | 120.9144 | 120.9014 | 5.7967 | -121.0699 | 120.7131 | 121.0296 | 120.8176 | 5.8003 | -121.2029
538.7969 | 120.9274 | -17.244 | 103.6926 | 1.4211e-13 | -0.012961 | 0.0022072 | 0.067981 | -0.010143 | 0.059112 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060338 | 0.025953 | 0.054873 | -16.4583 | 0.074664 | -16.568 | 104.4531 | 104.3678 | 104.3922 | -16.5334 | -16.4686 | 0.073618 | -16.6267 | 104.2453 | 104.4791 | 104.2259 | -16.6433 | 0.71051 | 0.76048 | 0.7857 | 0.67591 | -0.034601 | 0.67516 | 0.69954 | 0.60065 | 0.55265 | 0.77539 | 0.61726 | 0.01661 | 0.78647 | 0.53327 | 121.6971 | 121.6117 | 121.6361 | 17.3186 | -120.2261 | 121.4892 | 121.7231 | 121.4699 | 17.3176 | -120.3359
540.5469 | 120.8267 | -7.7042 | 113.118 | 1.4211e-13 | -0.012534 | 0.0026346 | 0.067767 | -0.009288 | 0.058898 | 0.0079357 | -0.0016621 | -0.00021359 | 0.060125 | 0.025953 | 0.055086 | -9.5815 | 0.22576 | -9.7144 | 111.1284 | 111.0668 | 111.0174 | -9.6559 | -9.5593 | 0.23845 | -9.6808 | 110.8795 | 111.1684 | 111.0114 | -9.7705 | -1.9517 | -1.9896 | -1.8774 | -2.0102 | -0.05846 | -2.0512 | -2.1006 | -2.0663 | -2.2385 | -1.8551 | -1.9766 | 0.089708 | -1.9495 | -2.1066 | 118.8326 | 118.7709 | 118.7216 | 7.9299 | -122.7739 | 118.5837 | 118.8726 | 118.7156 | 7.9426 | -122.8885
542.2188 | 120.7809 | -5.4382 | 115.2603 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.067554 | -0.009288 | 0.058898 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025953 | 0.054445 | -9.5128 | 0.26697 | -9.6091 | 111.1879 | 111.0988 | 111.1227 | -9.6513 | -9.4998 | 0.27508 | -9.6396 | 110.9161 | 111.2051 | 110.7779 | -9.743 | -4.2131 | -4.0724 | -4.0746 | -4.1708 | 0.042261 | -4.1615 | -4.1376 | -4.3048 | -4.3442 | -4.0615 | -4.2014 | 0.10344 | -4.0552 | -4.4824 | 116.6261 | 116.537 | 116.5609 | 5.7052 | -124.9116 | 116.3544 | 116.6433 | 116.2161 | 5.7133 | -125.0033
543.9688 | 120.5841 | -8.1345 | 112.4588 | 1.4211e-13 | -0.012748 | 0.0026346 | 0.067981 | -0.0097152 | 0.058685 | -0.0073253 | -0.0010211 | 0.00042721 | 0.059698 | 0.025739 | 0.054873 | -8.5331 | 0.17997 | -8.6659 | 111.9891 | 111.9184 | 111.9011 | -8.6256 | -8.5337 | 0.17435 | -8.6552 | 111.7174 | 112.0201 | 111.8035 | -8.7586 | -0.49119 | -0.46967 | -0.39861 | -0.53148 | -0.040292 | -0.54037 | -0.55773 | -0.62413 | -0.74142 | -0.39921 | -0.52071 | 0.10342 | -0.43874 | -0.65531 | 120.1236 | 120.0529 | 120.0355 | 8.3144 | -121.0844 | 119.8518 | 120.1545 | 119.9379 | 8.3088 | -121.2174
545.7031 | 120.9457 | -0.16937 | 120.9412 | 1.4211e-13 | -0.012961 | 0.0028484 | 0.067767 | -0.0095016 | 0.058685 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060552 | 0.025953 | 0.054659 | -0.003531 | 0.18455 | -0.077084 | 120.9536 | 120.8519 | 120.8477 | -0.17295 | 0.010205 | 0.20182 | -0.079245 | 120.6546 | 120.9804 | 120.773 | -0.28778 | -0.003578 | 0.012454 | 0.16584 | 0.092289 | 0.095867 | -0.089248 | -0.093498 | -0.1184 | -0.28656 | 0.17958 | 0.090128 | 0.20853 | 0.039223 | -0.16819 | 121.123 | 121.0213 | 121.017 | 0.35392 | -121.1141 | 120.824 | 121.1498 | 120.9423 | 0.37119 | -121.2289
547.375 | 121.2067 | -0.16479 | 121.0052 | 1.4211e-13 | -0.012534 | 0.0026346 | 0.067981 | -0.0095016 | 0.058898 | 0.015566 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025953 | 0.054659 | -0.008109 | 0.17997 | -0.077084 | 121.0772 | 120.9664 | 120.9576 | -0.16837 | 0.010205 | 0.19724 | -0.065509 | 120.7691 | 121.0903 | 120.8783 | -0.29693 | -0.003578 | 0.071983 | 0.15669 | 0.087711 | 0.091289 | -0.038861 | -0.047698 | -0.13214 | -0.23619 | 0.175 | 0.099286 | 0.23142 | 0.085022 | -0.12697 | 121.242 | 121.1312 | 121.1223 | 0.34477 | -121.1736 | 120.9339 | 121.2551 | 121.0431 | 0.36204 | -121.3022
549.1406 | 121.2112 | -0.15564 | 121.0419 | 1.4211e-13 | -0.012748 | 0.0026346 | 0.068195 | -0.0095016 | 0.058898 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.025953 | 0.054445 | -0.003531 | 0.18455 | -0.077084 | 121.123 | 121.0168 | 121.0033 | -0.17295 | 0.005626 | 0.16977 | -0.083823 | 120.8194 | 121.1498 | 120.9561 | -0.29236 | -0.017311 | 0.081146 | 0.15211 | 0.078556 | 0.095867 | -0.025114 | -0.038533 | -0.13672 | -0.22244 | 0.16127 | 0.071817 | 0.20853 | 0.10792 | -0.085755 | 121.2787 | 121.1724 | 121.159 | 0.34019 | -121.2148 | 120.9751 | 121.3054 | 121.1118 | 0.32541 | -121.3342
550.8906 | 121.2662 | -0.12817 | 121.0648 | 1.4211e-13 | -0.01232 | 0.002421 | 0.068195 | -0.0095016 | 0.059112 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060766 | 0.025953 | 0.054659 | -0.012688 | 0.17997 | -0.077084 | 121.1505 | 121.0488 | 121.0354 | -0.17295 | 0.010205 | 0.16977 | -0.083823 | 120.8515 | 121.1773 | 120.8096 | -0.28778 | -0.044777 | 0.085729 | 0.11549 | 0.05109 | 0.095867 | -0.01595 | -0.029371 | -0.1596 | -0.21328 | 0.13838 | 0.044351 | 0.20395 | 0.11251 | -0.25516 | 121.2787 | 121.177 | 121.1636 | 0.30815 | -121.2377 | 120.9797 | 121.3054 | 120.9378 | 0.29795 | -121.3525
552.5781 | 121.3348 | -0.15106 | 121.0831 | 1.4211e-13 | -0.012748 | 0.0026346 | 0.067981 | -0.009288 | 0.058898 | 0.0079357 | -0.0012349 | 0.00042721 | 0.060338 | 0.025953 | 0.054445 | -0.012688 | 0.17081 | -0.081662 | 121.178 | 121.0763 | 121.0583 | -0.17753 | 0.005626 | 0.17435 | -0.079245 | 120.8698 | 121.1956 | 120.8691 | -0.29236 | -0.026468 | 0.094888 | 0.13837 | 0.0694 | 0.095868 | -0.006787 | -0.024789 | -0.14129 | -0.21328 | 0.15669 | 0.071817 | 0.21311 | 0.11251 | -0.21395 | 121.329 | 121.2273 | 121.2093 | 0.32188 | -121.2606 | 121.0209 | 121.3466 | 121.0202 | 0.32541 | -121.3754
554.3125 | 121.3074 | -0.16022 | 121.1334 | 1.4211e-13 | -0.012534 | 0.002421 | 0.068409 | -0.009288 | 0.058898 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.025953 | 0.054445 | -0.021844 | 0.17539 | -0.081662 | 121.1917 | 121.09 | 121.072 | -0.16837 | -0.003531 | 0.16519 | -0.074666 | 120.8835 | 121.2139 | 120.9241 | -0.28778 | -0.008156 | 0.058269 | 0.13837 | 0.078555 | 0.086711 | -0.043405 | -0.061407 | -0.12756 | -0.2499 | 0.15669 | 0.085551 | 0.21311 | 0.080471 | -0.20936 | 121.3519 | 121.2502 | 121.2322 | 0.33561 | -121.3018 | 121.0437 | 121.3741 | 121.0843 | 0.32541 | -121.4212
556.0469 | 121.1975 | -0.21515 | 121.1426 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068195 | -0.0097152 | 0.059112 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.025953 | 0.054659 | -0.021844 | 0.1525 | -0.08624 | 121.2054 | 121.1038 | 121.0858 | -0.18211 | -0.00811 | 0.16061 | -0.088402 | 120.8973 | 121.2185 | 120.9699 | -0.29693 | 0.03304 | 0.062849 | 0.19331 | 0.12891 | 0.095869 | -0.038823 | -0.056827 | -0.081785 | -0.24532 | 0.20704 | 0.12675 | 0.20853 | 0.075894 | -0.17273 | 121.4206 | 121.3189 | 121.3009 | 0.36765 | -121.3247 | 121.1124 | 121.4336 | 121.185 | 0.37576 | -121.4395
557.7969 | 121.2158 | -0.20142 | 121.1655 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068195 | -0.0097152 | 0.059112 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060766 | 0.026167 | 0.054659 | -0.021844 | 0.15708 | -0.08624 | 121.21 | 121.1175 | 121.0949 | -0.17753 | -0.00811 | 0.16061 | -0.083823 | 120.9156 | 121.2231 | 120.9744 | -0.29236 | 0.023886 | 0.04454 | 0.17957 | 0.11518 | 0.09129 | -0.047974 | -0.070557 | -0.09094 | -0.24989 | 0.19331 | 0.11759 | 0.20853 | 0.057585 | -0.19104 | 121.4114 | 121.3189 | 121.2963 | 0.3585 | -121.343 | 121.117 | 121.4245 | 121.1758 | 0.36203 | -121.4578
559.5312 | 121.2067 | -0.20599 | 121.1655 | 1.4211e-13 | -0.012748 | 0.002421 | 0.068195 | -0.0095016 | 0.058898 | 0.015566 | -0.0012349 | 0.00021361 | 0.060766 | 0.026167 | 0.054659 | -0.026423 | 0.1525 | -0.081662 | 121.2146 | 121.1266 | 121.1132 | -0.18211 | 0.001048 | 0.16519 | -0.088402 | 120.9156 | 121.2414 | 120.9561 | -0.29236 | 0.023885 | 0.049118 | 0.17957 | 0.12433 | 0.10045 | -0.038816 | -0.052243 | -0.086362 | -0.24989 | 0.20704 | 0.11759 | 0.20395 | 0.075899 | -0.20935 | 121.4206 | 121.3326 | 121.3192 | 0.35849 | -121.3476 | 121.1216 | 121.4474 | 121.1621 | 0.37119 | -121.4578
561.2188 | 121.2204 | -0.20599 | 121.1838 | 1.4211e-13 | -0.012534 | 0.0026346 | 0.068409 | -0.0095016 | 0.059112 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025953 | 0.055086 | -0.026423 | 0.14792 | -0.08624 | 121.2192 | 121.1404 | 121.1086 | -0.18669 | -0.003531 | 0.16061 | -0.088402 | 120.9247 | 121.2505 | 120.9424 | -0.29236 | 0.019306 | 0.035385 | 0.17957 | 0.11975 | 0.10045 | -0.04339 | -0.075133 | -0.086362 | -0.25905 | 0.20246 | 0.11759 | 0.20395 | 0.066746 | -0.2414 | 121.4252 | 121.3464 | 121.3146 | 0.35392 | -121.3705 | 121.1307 | 121.4565 | 121.1484 | 0.36661 | -121.4761
562.9688 | 121.3623 | -0.14648 | 121.138 | 1.4211e-13 | -0.012748 | 0.0028484 | 0.068195 | -0.009288 | 0.058898 | 0.015566 | -0.0010211 | -0.00021359 | 0.060552 | 0.025739 | 0.054659 | -0.021844 | 0.14792 | -0.077084 | 121.2283 | 121.1404 | 121.1224 | -0.17753 | -0.012689 | 0.15146 | -0.097559 | 120.9385 | 121.2597 | 120.979 | -0.29236 | -0.031046 | 0.090319 | 0.12464 | 0.0694 | 0.10045 | 0.002387 | -0.01562 | -0.14587 | -0.19953 | 0.13379 | 0.048925 | 0.1948 | 0.12168 | -0.15899 | 121.3748 | 121.2869 | 121.2689 | 0.29441 | -121.3155 | 121.085 | 121.4062 | 121.1255 | 0.29794 | -121.4304
564.6562 | 121.3348 | -0.18768 | 121.1426 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068409 | -0.009288 | 0.058471 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060552 | 0.025739 | 0.054659 | -0.021844 | 0.14334 | -0.090818 | 121.2329 | 121.145 | 121.1224 | -0.17753 | -0.003531 | 0.15604 | -0.083823 | 120.9385 | 121.2643 | 120.9149 | -0.29693 | 0.010153 | 0.09032 | 0.16584 | 0.096865 | 0.086712 | 0.002388 | -0.020198 | -0.10925 | -0.20411 | 0.18415 | 0.10386 | 0.21311 | 0.12168 | -0.22767 | 121.4206 | 121.3326 | 121.3101 | 0.33103 | -121.3201 | 121.1262 | 121.4519 | 121.1026 | 0.34372 | -121.4395
566.4062 | 121.3852 | -0.15564 | 121.1609 | 1.4211e-13 | -0.012748 | 0.002421 | 0.068195 | -0.009288 | 0.059112 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.025953 | 0.055086 | -0.026423 | 0.1525 | -0.08624 | 121.2466 | 121.145 | 121.1407 | -0.17753 | -0.012689 | 0.15146 | -0.088402 | 120.9522 | 121.2688 | 120.979 | -0.28778 | -0.02189 | 0.085744 | 0.12922 | 0.0694 | 0.09129 | -0.015923 | -0.020194 | -0.13214 | -0.20869 | 0.14295 | 0.067238 | 0.19938 | 0.10795 | -0.18188 | 121.4023 | 121.3006 | 121.2963 | 0.30814 | -121.3384 | 121.1078 | 121.4245 | 121.1346 | 0.3071 | -121.4487
568.1562 | 121.3348 | -0.16937 | 121.1655 | 1.4211e-13 | -0.012961 | 0.0028484 | 0.068409 | -0.0095016 | 0.059112 | 0.015566 | -0.0014485 | 1.2e-08 | 0.060338 | 0.025739 | 0.054659 | -0.021844 | 0.14792 | -0.090818 | 121.2512 | 121.1541 | 121.1407 | -0.17753 | -0.003531 | 0.15146 | -0.083823 | 120.9568 | 121.2734 | 120.947 | -0.28778 | -0.008157 | 0.085745 | 0.14753 | 0.078555 | 0.086712 | -0.011343 | -0.024771 | -0.1184 | -0.20868 | 0.16584 | 0.08555 | 0.20395 | 0.10795 | -0.21851 | 121.4206 | 121.3235 | 121.3101 | 0.31729 | -121.343 | 121.1262 | 121.4428 | 121.1163 | 0.32083 | -121.4532
569.8906 | 121.3394 | -0.1831 | 121.1792 | 1.4211e-13 | -0.013175 | 0.003062 | 0.067981 | -0.0095016 | 0.058898 | 0.00030522 | -0.0010211 | -0.00021359 | 0.060338 | 0.025953 | 0.054873 | -0.021844 | 0.14792 | -0.081662 | 121.2649 | 121.1679 | 121.1453 | -0.17295 | -0.012689 | 0.15146 | -0.088402 | 120.9522 | 121.2917 | 120.9607 | -0.29693 | 0.010154 | 0.085747 | 0.16126 | 0.10144 | 0.091289 | -0.011339 | -0.033926 | -0.11383 | -0.227 | 0.17042 | 0.094703 | 0.20853 | 0.11253 | -0.21851 | 121.4481 | 121.351 | 121.3284 | 0.33103 | -121.3521 | 121.1353 | 121.4748 | 121.1438 | 0.33456 | -121.4761
571.625 | 121.3394 | -0.17853 | 121.1838 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068195 | -0.0095016 | 0.058898 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025953 | 0.054873 | -0.021844 | 0.1525 | -0.077084 | 121.2649 | 121.177 | 121.159 | -0.17295 | -0.003531 | 0.16061 | -0.083823 | 120.9659 | 121.2917 | 121.0385 | -0.29236 | 0.005577 | 0.081169 | 0.15668 | 0.10144 | 0.095867 | -0.006759 | -0.024768 | -0.11383 | -0.21784 | 0.175 | 0.094705 | 0.20853 | 0.10795 | -0.14525 | 121.4435 | 121.3555 | 121.3375 | 0.33103 | -121.3567 | 121.1445 | 121.4703 | 121.2171 | 0.33914 | -121.4761
573.2969 | 121.2799 | -0.19684 | 121.2387 | 1.4211e-13 | -0.012961 | 0.0022072 | 0.068195 | -0.0097152 | 0.059112 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060338 | 0.026167 | 0.054659 | -0.021844 | 0.14334 | -0.077084 | 121.2741 | 121.1816 | 121.1682 | -0.17295 | 0.001048 | 0.16061 | -0.088402 | 120.9797 | 121.2917 | 120.8737 | -0.29236 | 0.023887 | 0.035395 | 0.17499 | 0.11975 | 0.095867 | -0.057111 | -0.070542 | -0.095518 | -0.25903 | 0.19789 | 0.10844 | 0.20395 | 0.053022 | -0.36501 | 121.4709 | 121.3784 | 121.365 | 0.34018 | -121.4117 | 121.1765 | 121.4886 | 121.0705 | 0.35745 | -121.5311
575.0312 | 121.3486 | -0.15564 | 121.2112 | 1.4211e-13 | -0.013175 | 0.0028484 | 0.068409 | -0.009288 | 0.059112 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.025953 | 0.055086 | -0.012688 | 0.1525 | -0.077084 | 121.2833 | 121.177 | 121.1727 | -0.16837 | 0.005626 | 0.16061 | -0.079245 | 120.9797 | 121.3055 | 121.1118 | -0.2832 | -0.012733 | 0.072017 | 0.14295 | 0.078556 | 0.091289 | -0.034225 | -0.038498 | -0.12756 | -0.23157 | 0.16127 | 0.076395 | 0.20395 | 0.094223 | -0.099456 | 121.4389 | 121.3327 | 121.3284 | 0.30814 | -121.3796 | 121.1353 | 121.4611 | 121.2674 | 0.31625 | -121.4944
576.7656 | 121.3943 | -0.15564 | 121.1884 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068195 | -0.009929 | 0.059539 | -0.0073253 | -0.0010211 | 0.00021361 | 0.060552 | 0.025953 | 0.054659 | -0.017266 | 0.1525 | -0.077084 | 121.2924 | 121.1953 | 121.1727 | -0.17295 | 0.001048 | 0.15604 | -0.079245 | 120.9797 | 121.3055 | 120.9973 | -0.2832 | -0.017311 | 0.10406 | 0.13837 | 0.078556 | 0.095867 | 0.00698 | -0.015609 | -0.12756 | -0.20868 | 0.15669 | 0.076395 | 0.20395 | 0.11711 | -0.19103 | 121.4481 | 121.351 | 121.3284 | 0.30814 | -121.3613 | 121.1353 | 121.4611 | 121.153 | 0.31168 | -121.4716
578.4531 | 121.2936 | -0.19226 | 121.2204 | 1.4211e-13 | -0.012748 | 0.002421 | 0.068195 | -0.0097152 | 0.059112 | 0.0079357 | -0.0010211 | -0.00021359 | 0.060766 | 0.02638 | 0.054659 | -0.017266 | 0.15708 | -0.081662 | 121.2924 | 121.1999 | 121.1865 | -0.17753 | -0.003531 | 0.15604 | -0.079245 | 120.9888 | 121.3238 | 121.0294 | -0.2832 | 0.014731 | 0.072019 | 0.17499 | 0.1106 | 0.095868 | -0.020485 | -0.033917 | -0.090937 | -0.23157 | 0.18873 | 0.11302 | 0.20395 | 0.10338 | -0.19103 | 121.4847 | 121.3922 | 121.3787 | 0.34934 | -121.3979 | 121.1811 | 121.516 | 121.2216 | 0.3483 | -121.5036
580.1875 | 121.4218 | -0.15564 | 121.1884 | 1.4211e-13 | -0.012748 | 0.0028484 | 0.068195 | -0.0097152 | 0.059112 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060552 | 0.026167 | 0.054873 | -0.017266 | 0.1525 | -0.077084 | 121.2924 | 121.2091 | 121.1865 | -0.17295 | 0.005626 | 0.15604 | -0.079245 | 120.9934 | 121.3238 | 120.8966 | -0.28778 | -0.017311 | 0.10406 | 0.13837 | 0.078556 | 0.095867 | 0.020717 | -0.001873 | -0.13214 | -0.19495 | 0.16127 | 0.076395 | 0.20853 | 0.13543 | -0.29176 | 121.4481 | 121.3647 | 121.3421 | 0.30814 | -121.3613 | 121.149 | 121.4794 | 121.0522 | 0.31168 | -121.4761
581.9219 | 121.4127 | -0.13733 | 121.225 | 1.4211e-13 | -0.013389 | 0.0026346 | 0.068409 | -0.0097152 | 0.058898 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060552 | 0.026167 | 0.054873 | -0.012688 | 0.1525 | -0.077084 | 121.297 | 121.1999 | 121.1911 | -0.16837 | 0.005626 | 0.15146 | -0.083823 | 120.998 | 121.3284 | 121.0294 | -0.27862 | -0.031044 | 0.072019 | 0.12464 | 0.060245 | 0.091289 | -0.025063 | -0.033917 | -0.14129 | -0.22699 | 0.14295 | 0.053506 | 0.1948 | 0.10338 | -0.1956 | 121.4343 | 121.3372 | 121.3284 | 0.28983 | -121.3933 | 121.1353 | 121.4657 | 121.1667 | 0.28879 | -121.5036
583.6719 | 121.2936 | -0.20142 | 121.2387 | 1.4211e-13 | -0.013175 | 0.002421 | 0.068195 | -0.0095016 | 0.059112 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060552 | 0.025739 | 0.054445 | -0.017266 | 0.14792 | -0.072505 | 121.297 | 121.2091 | 121.2002 | -0.16837 | 0.001048 | 0.16061 | -0.074666 | 121.0026 | 121.3284 | 120.8966 | -0.27404 | 0.033043 | 0.058287 | 0.18415 | 0.12891 | 0.095868 | -0.029637 | -0.038491 | -0.072624 | -0.23614 | 0.20246 | 0.12675 | 0.19937 | 0.089651 | -0.34212 | 121.4984 | 121.4105 | 121.4016 | 0.34934 | -121.4071 | 121.204 | 121.5298 | 121.098 | 0.36203 | -121.5127
585.3438 | 121.2662 | -0.19684 | 121.2524 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068195 | -0.0095016 | 0.059112 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060766 | 0.025953 | 0.055086 | -0.021844 | 0.14792 | -0.081662 | 121.3062 | 121.2136 | 121.2002 | -0.16379 | 0.005626 | 0.16061 | -0.074666 | 121.0117 | 121.3375 | 121.0843 | -0.2832 | 0.033044 | 0.053711 | 0.17499 | 0.11518 | 0.082132 | -0.038792 | -0.052224 | -0.08636 | -0.24072 | 0.20246 | 0.12217 | 0.20853 | 0.085075 | -0.16813 | 121.503 | 121.4105 | 121.3971 | 0.34476 | -121.4162 | 121.2086 | 121.5344 | 121.2812 | 0.35745 | -121.5356
587.0781 | 121.4401 | -0.15106 | 121.1929 | 1.4211e-13 | -0.012961 | 0.002421 | 0.068195 | -0.009929 | 0.059539 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060766 | 0.026167 | 0.054445 | -0.012688 | 0.14334 | -0.072505 | 121.3107 | 121.2136 | 121.214 | -0.16837 | -0.003531 | 0.16061 | -0.079245 | 121.0026 | 121.3375 | 121.1393 | -0.2832 | -0.017311 | 0.1178 | 0.13837 | 0.078557 | 0.095868 | 0.020717 | 0.02102 | -0.13214 | -0.19037 | 0.14753 | 0.071817 | 0.20395 | 0.14458 | -0.053673 | 121.4618 | 121.3647 | 121.365 | 0.29441 | -121.3613 | 121.1536 | 121.4886 | 121.2903 | 0.31168 | -121.4761
588.8281 | 121.2708 | -0.1831 | 121.2479 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068195 | -0.0095016 | 0.058898 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060338 | 0.025739 | 0.054445 | -0.012688 | 0.1525 | -0.072505 | 121.3062 | 121.2182 | 121.2185 | -0.17295 | -0.012689 | 0.15604 | -0.074666 | 121.0117 | 121.3329 | 121.1393 | -0.27404 | 0.010154 | 0.058288 | 0.17042 | 0.1106 | 0.10045 | -0.029636 | -0.029333 | -0.090935 | -0.23614 | 0.17042 | 0.10844 | 0.19937 | 0.085073 | -0.10861 | 121.4893 | 121.4013 | 121.4016 | 0.3356 | -121.4208 | 121.1948 | 121.516 | 121.3224 | 0.33914 | -121.5219
590.5625 | 121.3074 | -0.19226 | 121.225 | 1.4211e-13 | -0.012961 | 0.002421 | 0.067981 | -0.0095016 | 0.059112 | 0.00030522 | -0.0012349 | -0.00021359 | 0.060766 | 0.026167 | 0.054659 | -0.012688 | 0.1525 | -0.072505 | 121.3153 | 121.2274 | 121.214 | -0.16379 | 0.010205 | 0.16977 | -0.074666 | 121.0163 | 121.3329 | 121.0294 | -0.2832 | 0.028467 | 0.090333 | 0.17957 | 0.11976 | 0.091289 | 0.00241 | -0.011024 | -0.090937 | -0.20867 | 0.20247 | 0.11759 | 0.20853 | 0.10796 | -0.1956 | 121.5076 | 121.4196 | 121.4062 | 0.34476 | -121.3888 | 121.2086 | 121.5252 | 121.2216 | 0.36203 | -121.5082
592.2344 | 121.3348 | -0.19684 | 121.2708 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068409 | -0.0095016 | 0.059112 | 0.015566 | -0.0010211 | 1.2e-08 | 0.060552 | 0.026167 | 0.054659 | -0.012688 | 0.14792 | -0.077084 | 121.3199 | 121.2228 | 121.2231 | -0.16379 | 0.001048 | 0.15604 | -0.074666 | 121.0163 | 121.3375 | 121.1347 | -0.28778 | 0.033044 | 0.049135 | 0.18415 | 0.11975 | 0.08671 | -0.047945 | -0.047642 | -0.090939 | -0.25445 | 0.19789 | 0.12217 | 0.21311 | 0.066764 | -0.13607 | 121.5167 | 121.4196 | 121.4199 | 0.34476 | -121.4345 | 121.2131 | 121.5344 | 121.3315 | 0.35287 | -121.5585
593.9844 | 121.3852 | -0.16937 | 121.2387 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068409 | -0.0095016 | 0.059326 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060766 | 0.026167 | 0.055086 | -0.017266 | 0.14792 | -0.077084 | 121.3199 | 121.2274 | 121.2185 | -0.16379 | 0.005626 | 0.16061 | -0.074666 | 121.0209 | 121.3467 | 121.1484 | -0.27862 | 0.005579 | 0.081179 | 0.15211 | 0.092289 | 0.08671 | -0.011322 | -0.020177 | -0.10925 | -0.21783 | 0.175 | 0.094707 | 0.20395 | 0.10796 | -0.090292 | 121.4893 | 121.3968 | 121.3879 | 0.31729 | -121.4025 | 121.1903 | 121.516 | 121.3178 | 0.32999 | -121.5173
595.7188 | 121.4172 | -0.15564 | 121.2433 | 1.4211e-13 | -0.012961 | 0.0026346 | 0.068622 | -0.0095016 | 0.059326 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.02638 | 0.054873 | -0.017266 | 0.1525 | -0.067927 | 121.329 | 121.2274 | 121.2277 | -0.16379 | 0.010205 | 0.15604 | -0.079245 | 121.03 | 121.3558 | 121.1393 | -0.27404 | -0.008154 | 0.085758 | 0.13837 | 0.087713 | 0.095867 | -0.0159 | -0.015598 | -0.1184 | -0.21325 | 0.16584 | 0.076395 | 0.19479 | 0.11254 | -0.10403 | 121.4847 | 121.383 | 121.3833 | 0.30814 | -121.4071 | 121.1857 | 121.5115 | 121.2949 | 0.31168 | -121.5173
597.4531 | 121.3577 | -0.16022 | 121.2662 | 1.4211e-13 | -0.012961 | 0.0028484 | 0.068409 | -0.0097152 | 0.058898 | 0.0079357 | -0.0010211 | -0.00021359 | 0.060338 | 0.025953 | 0.054873 | -0.012688 | 0.14334 | -0.081662 | 121.3245 | 121.232 | 121.2231 | -0.16379 | -0.003531 | 0.16061 | -0.070087 | 121.0255 | 121.3513 | 121.1622 | -0.27404 | -0.003577 | 0.058291 | 0.14753 | 0.078555 | 0.082132 | -0.034209 | -0.043064 | -0.11382 | -0.24072 | 0.15669 | 0.09013 | 0.20395 | 0.085078 | -0.10402 | 121.4847 | 121.3922 | 121.3833 | 0.30356 | -121.43 | 121.1857 | 121.5115 | 121.3224 | 0.32083 | -121.5402
599.1562 | 121.3623 | -0.1831 | 121.2799 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068409 | -0.009929 | 0.058898 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060552 | 0.02638 | 0.054445 | -0.012688 | 0.15708 | -0.077084 | 121.3245 | 121.232 | 121.2277 | -0.16379 | 0.010205 | 0.16061 | -0.079245 | 121.0255 | 121.365 | 120.9424 | -0.26946 | 0.019311 | 0.044558 | 0.17042 | 0.10602 | 0.08671 | -0.047942 | -0.052219 | -0.086357 | -0.25445 | 0.19331 | 0.10386 | 0.19022 | 0.085081 | -0.33753 | 121.5076 | 121.4151 | 121.4108 | 0.34018 | -121.4437 | 121.2086 | 121.5481 | 121.1255 | 0.34372 | -121.5494
600.8906 | 121.312 | -0.19226 | 121.2708 | 1.4211e-13 | -0.013389 | 0.002421 | 0.068195 | -0.009288 | 0.058471 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060766 | 0.02638 | 0.054445 | -0.008109 | 0.14792 | -0.072505 | 121.3336 | 121.2411 | 121.2277 | -0.16379 | 0.005626 | 0.16061 | -0.070087 | 121.0255 | 121.3558 | 121.0706 | -0.27404 | 0.028467 | 0.06287 | 0.18415 | 0.11976 | 0.091289 | -0.029629 | -0.043064 | -0.081779 | -0.24529 | 0.19789 | 0.12217 | 0.20395 | 0.085078 | -0.20017 | 121.5259 | 121.4334 | 121.4199 | 0.34018 | -121.4345 | 121.2177 | 121.5481 | 121.2628 | 0.35287 | -121.5448
602.625 | 121.4172 | -0.14191 | 121.2479 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068409 | -0.0095016 | 0.059112 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060552 | 0.026167 | 0.054873 | -0.017266 | 0.14792 | -0.072505 | 121.329 | 121.2365 | 121.2368 | -0.16379 | -0.003531 | 0.16061 | -0.070087 | 121.0392 | 121.3604 | 121.1484 | -0.27862 | -0.021887 | 0.08118 | 0.12464 | 0.069402 | 0.091289 | -0.01132 | -0.011019 | -0.13671 | -0.20867 | 0.13838 | 0.07182 | 0.20853 | 0.11254 | -0.099448 | 121.471 | 121.3785 | 121.3788 | 0.28983 | -121.4117 | 121.1811 | 121.5023 | 121.2903 | 0.30252 | -121.5265
604.3125 | 121.3577 | -0.17395 | 121.2662 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.068195 | -0.0097152 | 0.058898 | -0.0073253 | -0.0012349 | -0.00021359 | 0.060125 | 0.025953 | 0.054445 | -0.012688 | 0.1525 | -0.072505 | 121.3336 | 121.2503 | 121.2368 | -0.16379 | 0.001048 | 0.15604 | -0.074666 | 121.0346 | 121.3513 | 121.1255 | -0.27404 | 0.010156 | 0.067448 | 0.16126 | 0.10144 | 0.091289 | -0.015893 | -0.029329 | -0.10009 | -0.23156 | 0.175 | 0.099284 | 0.19937 | 0.085078 | -0.14065 | 121.5076 | 121.4242 | 121.4108 | 0.32645 | -121.43 | 121.2086 | 121.5252 | 121.2995 | 0.32998 | -121.5402
606.0469 | 121.344 | -0.19684 | 121.2708 | 1.4211e-13 | -0.013389 | 0.003062 | 0.067981 | -0.0097152 | 0.058898 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.02638 | 0.054659 | -0.012688 | 0.14792 | -0.077084 | 121.3382 | 121.2503 | 121.246 | -0.16379 | 0.010205 | 0.15604 | -0.074666 | 121.0392 | 121.3741 | 121.1026 | -0.27862 | 0.033044 | 0.067449 | 0.18415 | 0.11975 | 0.08671 | -0.020471 | -0.024749 | -0.081781 | -0.23156 | 0.20704 | 0.12217 | 0.20395 | 0.10339 | -0.16812 | 121.535 | 121.4471 | 121.4428 | 0.34476 | -121.4345 | 121.236 | 121.571 | 121.2995 | 0.35287 | -121.5494
607.7344 | 121.4127 | -0.15564 | 121.2296 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068195 | -0.009929 | 0.059112 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.025953 | 0.054659 | -0.012688 | 0.1525 | -0.077084 | 121.3428 | 121.2549 | 121.2506 | -0.15921 | 0.001048 | 0.16519 | -0.074666 | 121.0392 | 121.3696 | 121.1667 | -0.27404 | -0.003575 | 0.11323 | 0.14295 | 0.078556 | 0.082131 | 0.025307 | 0.021028 | -0.1184 | -0.19036 | 0.15669 | 0.080974 | 0.19937 | 0.14001 | -0.062823 | 121.4984 | 121.4105 | 121.4062 | 0.30814 | -121.3888 | 121.1948 | 121.5252 | 121.3224 | 0.32083 | -121.5036
609.4844 | 121.3806 | -0.18768 | 121.2524 | 1.4211e-13 | -0.013389 | 0.002421 | 0.068409 | -0.0095016 | 0.058898 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060766 | 0.025953 | 0.054873 | -0.012688 | 0.1525 | -0.067927 | 121.3382 | 121.2457 | 121.2506 | -0.15921 | 0.010205 | 0.16061 | -0.074666 | 121.0484 | 121.3696 | 121.0797 | -0.26946 | 0.028468 | 0.08576 | 0.17499 | 0.11976 | 0.091288 | -0.006739 | -0.00186 | -0.081779 | -0.20409 | 0.19789 | 0.11302 | 0.1948 | 0.11713 | -0.1727 | 121.5259 | 121.4334 | 121.4383 | 0.34018 | -121.4117 | 121.236 | 121.5572 | 121.2674 | 0.3483 | -121.5219
611.1719 | 121.4767 | -0.15564 | 121.2479 | 1.4211e-13 | -0.013389 | 0.002421 | 0.067981 | -0.0097152 | 0.059326 | 0.015566 | -0.0012349 | 1.2e-08 | 0.060338 | 0.025739 | 0.054659 | -0.008109 | 0.1525 | -0.072505 | 121.3474 | 121.2549 | 121.2506 | -0.15921 | 0.005626 | 0.15604 | -0.070087 | 121.0392 | 121.3741 | 121.1393 | -0.27404 | -0.003575 | 0.099493 | 0.14753 | 0.083135 | 0.08671 | 0.006996 | 0.002717 | -0.1184 | -0.20867 | 0.16127 | 0.085553 | 0.20395 | 0.12628 | -0.10861 | 121.503 | 121.4105 | 121.4062 | 0.30814 | -121.4071 | 121.1948 | 121.5298 | 121.2949 | 0.31168 | -121.5219
612.9219 | 121.4081 | -0.16022 | 121.2433 | 1.4211e-13 | -0.013389 | 0.0026346 | 0.068195 | -0.009929 | 0.059112 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060338 | 0.02638 | 0.054445 | -0.008109 | 0.14334 | -0.063349 | 121.3474 | 121.2594 | 121.2552 | -0.16379 | 0.005626 | 0.15604 | -0.079245 | 121.0392 | 121.3696 | 121.0111 | -0.26946 | -0.003577 | 0.10407 | 0.15211 | 0.096868 | 0.10044 | 0.016153 | 0.011874 | -0.10924 | -0.20409 | 0.16584 | 0.080972 | 0.19022 | 0.12628 | -0.23223 | 121.5076 | 121.4197 | 121.4154 | 0.30356 | -121.4071 | 121.1994 | 121.5298 | 121.1713 | 0.31625 | -121.5127
614.6562 | 121.4172 | -0.15106 | 121.2753 | 1.4211e-13 | -0.012961 | 0.002421 | 0.068409 | -0.009929 | 0.059112 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060766 | 0.026594 | 0.054659 | -0.017266 | 0.14792 | -0.067927 | 121.3519 | 121.2549 | 121.2506 | -0.16379 | 0.010205 | 0.16519 | -0.074666 | 121.0484 | 121.3741 | 121.1713 | -0.27862 | -0.012732 | 0.076606 | 0.1338 | 0.083135 | 0.095867 | -0.02047 | -0.024749 | -0.12756 | -0.22698 | 0.16127 | 0.076396 | 0.20395 | 0.098815 | -0.10402 | 121.503 | 121.4059 | 121.4016 | 0.29898 | -121.4391 | 121.1994 | 121.5252 | 121.3224 | 0.31626 | -121.5539
616.3281 | 121.3257 | -0.17853 | 121.312 | 1.4211e-13 | -0.013816 | 0.0028484 | 0.068409 | -0.0095016 | 0.059112 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.026167 | 0.054873 | -0.012688 | 0.1525 | -0.067927 | 121.3474 | 121.264 | 121.2552 | -0.16837 | 0.010205 | 0.15604 | -0.065509 | 121.0529 | 121.3833 | 121.1713 | -0.26488 | 0.010155 | 0.035406 | 0.16584 | 0.1106 | 0.10045 | -0.047933 | -0.056791 | -0.086355 | -0.25902 | 0.18873 | 0.11302 | 0.19937 | 0.071351 | -0.14064 | 121.5259 | 121.4425 | 121.4337 | 0.33103 | -121.4803 | 121.2315 | 121.5618 | 121.3498 | 0.33456 | -121.5768
618.0625 | 121.344 | -0.17853 | 121.2616 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.068409 | -0.009288 | 0.058898 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060766 | 0.02638 | 0.054232 | -0.008109 | 0.15708 | -0.067927 | 121.3474 | 121.2594 | 121.2643 | -0.15464 | 0.005626 | 0.16061 | -0.070087 | 121.0529 | 121.3879 | 121.066 | -0.27862 | 0.023892 | 0.08576 | 0.17042 | 0.1106 | 0.086709 | -0.002158 | 0.00272 | -0.10009 | -0.20867 | 0.18415 | 0.10844 | 0.20853 | 0.12628 | -0.1956 | 121.5259 | 121.438 | 121.4428 | 0.33561 | -121.4162 | 121.2315 | 121.5664 | 121.2445 | 0.33914 | -121.5402
619.75 | 121.4676 | -0.15106 | 121.2524 | 1.4211e-13 | -0.013389 | 0.0026346 | 0.068195 | -0.0095016 | 0.058898 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060338 | 0.02638 | 0.054659 | -0.012688 | 0.14792 | -0.067927 | 121.3565 | 121.2732 | 121.2597 | -0.16379 | 0.005626 | 0.16519 | -0.070087 | 121.0575 | 121.3879 | 121.1301 | -0.26488 | -0.012732 | 0.10407 | 0.13837 | 0.083135 | 0.095867 | 0.020734 | 0.007297 | -0.11382 | -0.19493 | 0.15669 | 0.080975 | 0.1948 | 0.13544 | -0.12234 | 121.5076 | 121.4242 | 121.4108 | 0.29898 | -121.4162 | 121.2086 | 121.5389 | 121.2812 | 0.31626 | -121.5173
621.4844 | 121.4172 | -0.16479 | 121.2891 | 1.4211e-13 | -0.013389 | 0.0026346 | 0.068195 | -0.0097152 | 0.058898 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060552 | 0.02638 | 0.054659 | -0.008109 | 0.1525 | -0.072505 | 121.3565 | 121.264 | 121.2643 | -0.15464 | 0.010205 | 0.16519 | -0.065509 | 121.0575 | 121.3833 | 121.185 | -0.26946 | 0.010159 | 0.067452 | 0.15669 | 0.09229 | 0.082131 | -0.025044 | -0.024745 | -0.10467 | -0.23155 | 0.175 | 0.099286 | 0.20395 | 0.09424 | -0.10402 | 121.5213 | 121.4288 | 121.4291 | 0.31729 | -121.4437 | 121.2223 | 121.5481 | 121.3498 | 0.32999 | -121.5585
623.2188 | 121.4447 | -0.16479 | 121.2799 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.068195 | -0.0097152 | 0.059112 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060338 | 0.02638 | 0.054873 | -0.008109 | 0.1525 | -0.072505 | 121.3611 | 121.2778 | 121.2735 | -0.15921 | 0.014784 | 0.16061 | -0.070087 | 121.0575 | 121.3879 | 121.1209 | -0.26946 | 0.00558 | 0.081185 | 0.15669 | 0.09229 | 0.08671 | -0.002153 | -0.006433 | -0.10467 | -0.2224 | 0.17958 | 0.094708 | 0.19937 | 0.10797 | -0.15896 | 121.5259 | 121.4425 | 121.4383 | 0.31729 | -121.4391 | 121.2223 | 121.5527 | 121.2857 | 0.32541 | -121.5494
624.9688 | 121.3577 | -0.19226 | 121.3028 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.068195 | -0.0097152 | 0.058898 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060552 | 0.02638 | 0.054018 | -0.012688 | 0.15708 | -0.063349 | 121.3565 | 121.2732 | 121.2735 | -0.15921 | 0.014784 | 0.16519 | -0.06093 | 121.0529 | 121.4016 | 121.1896 | -0.26946 | 0.033046 | 0.053719 | 0.17957 | 0.12891 | 0.095866 | -0.02962 | -0.029321 | -0.077201 | -0.24987 | 0.20704 | 0.13133 | 0.20853 | 0.098821 | -0.11317 | 121.5488 | 121.4654 | 121.4657 | 0.34934 | -121.462 | 121.2452 | 121.5939 | 121.3819 | 0.35745 | -121.5723
626.6562 | 121.3348 | -0.17853 | 121.3074 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068409 | -0.009288 | 0.058898 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060125 | 0.026594 | 0.054232 | -0.017266 | 0.15708 | -0.072505 | 121.3657 | 121.2732 | 121.2781 | -0.15464 | 0.001048 | 0.16519 | -0.074666 | 121.0575 | 121.3925 | 121.1759 | -0.27404 | 0.023892 | 0.058298 | 0.16126 | 0.10602 | 0.082131 | -0.034198 | -0.02932 | -0.095512 | -0.24986 | 0.17958 | 0.10386 | 0.19937 | 0.085086 | -0.13148 | 121.5442 | 121.4517 | 121.4566 | 0.33561 | -121.462 | 121.236 | 121.571 | 121.3544 | 0.34372 | -121.5814
628.3906 | 121.4996 | -0.13733 | 121.2708 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068409 | -0.009929 | 0.058898 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060552 | 0.026594 | 0.054659 | -0.008109 | 0.1525 | -0.063349 | 121.3702 | 121.2869 | 121.2781 | -0.16379 | 0.014784 | 0.16977 | -0.065509 | 121.0667 | 121.4016 | 121.0614 | -0.26946 | -0.026465 | 0.099497 | 0.12922 | 0.07398 | 0.10044 | 0.01616 | 0.007301 | -0.13213 | -0.20409 | 0.15211 | 0.07182 | 0.20395 | 0.13086 | -0.20933 | 121.5076 | 121.4242 | 121.4154 | 0.28983 | -121.4345 | 121.204 | 121.5389 | 121.1988 | 0.3071 | -121.5402
630.1406 | 121.3943 | -0.17395 | 121.3165 | 1.4211e-13 | -0.013389 | 0.0028484 | 0.068195 | -0.009929 | 0.059112 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.02638 | 0.054445 | -0.017266 | 0.14792 | -0.072505 | 121.3702 | 121.2778 | 121.2826 | -0.15921 | 0.010205 | 0.16061 | -0.070087 | 121.0712 | 121.397 | 121.1942 | -0.27404 | 0.014735 | 0.053721 | 0.15668 | 0.10144 | 0.08671 | -0.038774 | -0.033897 | -0.10009 | -0.24529 | 0.18415 | 0.10386 | 0.20395 | 0.08051 | -0.12233 | 121.5442 | 121.4517 | 121.4566 | 0.32187 | -121.4757 | 121.2452 | 121.571 | 121.3682 | 0.33456 | -121.5906
631.8125 | 121.344 | -0.18768 | 121.2982 | 1.4211e-13 | -0.013816 | 0.0026346 | 0.068409 | -0.009929 | 0.058898 | 0.0079357 | -0.0012349 | 0.00042721 | 0.060766 | 0.026594 | 0.054659 | -0.012688 | 0.1525 | -0.072505 | 121.3702 | 121.2869 | 121.2781 | -0.15006 | 0.014784 | 0.16977 | -0.065509 | 121.0712 | 121.4062 | 121.0752 | -0.26946 | 0.037626 | 0.072031 | 0.17499 | 0.11518 | 0.077552 | -0.011306 | -0.020165 | -0.081779 | -0.22698 | 0.20247 | 0.12217 | 0.20395 | 0.10798 | -0.22306 | 121.5579 | 121.4746 | 121.4657 | 0.34018 | -121.4483 | 121.2589 | 121.5939 | 121.2628 | 0.35745 | -121.5677
633.5469 | 121.4584 | -0.15106 | 121.2662 | 1.4211e-13 | -0.013175 | 0.0026346 | 0.068195 | -0.0097152 | 0.059112 | -0.0073253 | -0.0014485 | 0.00021361 | 0.060338 | 0.02638 | 0.054659 | -0.008109 | 0.1525 | -0.072505 | 121.3657 | 121.2823 | 121.2826 | -0.16379 | 0.010205 | 0.16977 | -0.070087 | 121.0758 | 121.4016 | 121.1438 | -0.26946 | -0.012732 | 0.099497 | 0.14295 | 0.078557 | 0.091289 | 0.016159 | 0.016457 | -0.1184 | -0.19035 | 0.16127 | 0.080975 | 0.19937 | 0.13544 | -0.12234 | 121.5167 | 121.4334 | 121.4337 | 0.30356 | -121.43 | 121.2269 | 121.5527 | 121.2949 | 0.32083 | -121.5356
635.2188 | 121.4813 | -0.14648 | 121.2387 | 1.4211e-13 | -0.013602 | 0.0028484 | 0.067767 | -0.0095016 | 0.058898 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060552 | 0.026167 | 0.054232 | -0.008109 | 0.1525 | -0.067927 | 121.3702 | 121.2869 | 121.2826 | -0.1409 | 0.014784 | 0.16977 | -0.070087 | 121.0712 | 121.4016 | 121.153 | -0.2832 | 0.005585 | 0.13154 | 0.13837 | 0.078557 | 0.072972 | 0.048204 | 0.043923 | -0.13671 | -0.16747 | 0.16127 | 0.076397 | 0.21311 | 0.16291 | -0.085713 | 121.5167 | 121.4334 | 121.4291 | 0.29898 | -121.3796 | 121.2177 | 121.5481 | 121.2995 | 0.31626 | -121.5219
636.9531 | 121.4584 | -0.13275 | 121.2799 | 1.4211e-13 | -0.013602 | 0.002421 | 0.068409 | -0.009929 | 0.058898 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060979 | 0.02638 | 0.054232 | -0.012688 | 0.1525 | -0.067927 | 121.3794 | 121.2869 | 121.2872 | -0.15464 | 0.010205 | 0.16519 | -0.070087 | 121.0712 | 121.4062 | 121.1484 | -0.26488 | -0.021885 | 0.099499 | 0.12006 | 0.064824 | 0.086709 | 0.007005 | 0.007303 | -0.13213 | -0.20866 | 0.14296 | 0.062664 | 0.1948 | 0.12629 | -0.13149 | 121.5122 | 121.4197 | 121.42 | 0.28525 | -121.4345 | 121.204 | 121.5389 | 121.2812 | 0.29794 | -121.5448
638.6406 | 121.3348 | -0.1831 | 121.3394 | 1.4211e-13 | -0.013389 | 0.0026346 | 0.067981 | -0.0095016 | 0.058685 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060338 | 0.026594 | 0.054445 | -0.003531 | 0.15708 | -0.067927 | 121.3702 | 121.2915 | 121.2872 | -0.15006 | 0.010205 | 0.16977 | -0.065509 | 121.085 | 121.4108 | 121.0889 | -0.26946 | 0.033048 | 0.030832 | 0.17957 | 0.11518 | 0.08213 | -0.047926 | -0.052207 | -0.086357 | -0.25444 | 0.19331 | 0.1176 | 0.20395 | 0.071357 | -0.25052 | 121.5534 | 121.4746 | 121.4703 | 0.34018 | -121.4895 | 121.2681 | 121.5939 | 121.272 | 0.35288 | -121.6089
640.375 | 121.3531 | -0.1831 | 121.3165 | 1.4211e-13 | -0.013389 | 0.002421 | 0.068195 | -0.0097152 | 0.058898 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.02638 | 0.054873 | -0.008109 | 0.15708 | -0.067927 | 121.3794 | 121.2961 | 121.2964 | -0.15464 | 0.014784 | 0.17435 | -0.065509 | 121.085 | 121.4108 | 121.1484 | -0.26488 | 0.028469 | 0.062878 | 0.175 | 0.11518 | 0.086709 | -0.020458 | -0.020161 | -0.081778 | -0.23155 | 0.19789 | 0.1176 | 0.19937 | 0.094246 | -0.16811 | 121.5625 | 121.4792 | 121.4795 | 0.34018 | -121.4712 | 121.2681 | 121.5939 | 121.3315 | 0.35745 | -121.5814
642.1094 | 121.4539 | -0.15564 | 121.2845 | 1.4211e-13 | -0.013602 | 0.0028484 | 0.068622 | -0.009929 | 0.058898 | 0.00030522 | -0.0016621 | 0.00021361 | 0.060552 | 0.02638 | 0.054445 | -0.008109 | 0.15708 | -0.067927 | 121.384 | 121.2915 | 121.2918 | -0.15464 | 0.014784 | 0.17435 | -0.065509 | 121.0804 | 121.4108 | 120.9973 | -0.26946 | 0.001004 | 0.099499 | 0.14753 | 0.087713 | 0.086709 | 0.007006 | 0.007304 | -0.11382 | -0.20409 | 0.17042 | 0.090131 | 0.20395 | 0.12629 | -0.28716 | 121.5396 | 121.4471 | 121.4474 | 0.31272 | -121.4391 | 121.236 | 121.5664 | 121.153 | 0.32999 | -121.5539
643.8594 | 121.3669 | -0.17853 | 121.3486 | 1.4211e-13 | -0.013389 | 0.0022072 | 0.067981 | -0.0097152 | 0.058685 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060552 | 0.026594 | 0.054445 | -0.008109 | 0.15708 | -0.067927 | 121.384 | 121.3052 | 121.2918 | -0.14548 | 0.019362 | 0.16519 | -0.065509 | 121.085 | 121.4108 | 121.0614 | -0.2603 | 0.03305 | 0.035412 | 0.17042 | 0.1106 | 0.077551 | -0.043344 | -0.056783 | -0.081776 | -0.26359 | 0.19789 | 0.11302 | 0.19479 | 0.062202 | -0.28715 | 121.5625 | 121.4838 | 121.4703 | 0.33561 | -121.4941 | 121.2635 | 121.5893 | 121.24 | 0.34372 | -121.6089
645.5938 | 121.4401 | -0.14648 | 121.3028 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.067981 | -0.009929 | 0.058471 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060338 | 0.02638 | 0.054232 | -0.003531 | 0.1525 | -0.067927 | 121.384 | 121.3006 | 121.2918 | -0.15006 | 0.005626 | 0.16977 | -0.06093 | 121.085 | 121.4154 | 121.0797 | -0.26946 | -0.003573 | 0.081189 | 0.14295 | 0.078557 | 0.08213 | -0.002146 | -0.011006 | -0.12298 | -0.21782 | 0.15211 | 0.085554 | 0.20853 | 0.11256 | -0.22306 | 121.5305 | 121.4471 | 121.4383 | 0.29898 | -121.4529 | 121.2315 | 121.5618 | 121.2262 | 0.31626 | -121.5723
647.2812 | 121.4447 | -0.13275 | 121.2891 | 1.4211e-13 | -0.013602 | 0.002421 | 0.067981 | -0.0097152 | 0.058471 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060552 | 0.026808 | 0.054659 | -0.008109 | 0.1525 | -0.072505 | 121.3886 | 121.3006 | 121.2964 | -0.118 | 0.010205 | 0.16977 | -0.065509 | 121.0804 | 121.4108 | 121.0477 | -0.26488 | 0.014747 | 0.099501 | 0.12464 | 0.060246 | 0.045499 | 0.011587 | 0.007305 | -0.13213 | -0.20866 | 0.14296 | 0.067242 | 0.19937 | 0.12171 | -0.24138 | 121.5213 | 121.4334 | 121.4291 | 0.28525 | -121.4071 | 121.2132 | 121.5435 | 121.1804 | 0.30252 | -121.5539
649.0312 | 121.5042 | -0.13275 | 121.2891 | 1.4211e-13 | -0.013602 | 0.002421 | 0.068622 | -0.0097152 | 0.058898 | 0.00030522 | -0.0012349 | -0.00042739 | 0.059911 | 0.02638 | 0.054232 | -0.008109 | 0.15708 | -0.067927 | 121.3886 | 121.3006 | 121.2964 | -0.15006 | 0.014784 | 0.17435 | -0.065509 | 121.0896 | 121.4108 | 121.1026 | -0.26488 | -0.017306 | 0.099501 | 0.12464 | 0.064824 | 0.08213 | 0.011587 | 0.007305 | -0.13213 | -0.19951 | 0.14753 | 0.067242 | 0.19937 | 0.12171 | -0.18643 | 121.5213 | 121.4334 | 121.4291 | 0.28983 | -121.4391 | 121.2223 | 121.5435 | 121.2354 | 0.3071 | -121.5539
650.7031 | 121.5179 | -0.12817 | 121.2936 | 1.4211e-13 | -0.013816 | 0.002421 | 0.068195 | -0.0095016 | 0.058898 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.02638 | 0.054659 | -0.012688 | 0.1525 | -0.067927 | 121.3794 | 121.3098 | 121.3009 | -0.118 | 0.014784 | 0.17435 | -0.065509 | 121.085 | 121.4154 | 121.0752 | -0.2603 | 0.01017 | 0.085766 | 0.11549 | 0.060247 | 0.050077 | 0.016167 | 0.007306 | -0.13213 | -0.20866 | 0.14296 | 0.062665 | 0.19479 | 0.12171 | -0.21848 | 121.5076 | 121.438 | 121.4291 | 0.28067 | -121.4116 | 121.2132 | 121.5435 | 121.2033 | 0.30252 | -121.5539
652.4375 | 121.3806 | -0.16022 | 121.3394 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.068409 | -0.0097152 | 0.058471 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.026594 | 0.054659 | 0.001048 | 0.16166 | -0.067927 | 121.3931 | 121.3098 | 121.3055 | -0.11342 | 0.010205 | 0.17435 | -0.070087 | 121.0896 | 121.4154 | 120.9378 | -0.26946 | 0.046792 | 0.053724 | 0.16126 | 0.09229 | 0.045498 | -0.02961 | -0.033893 | -0.10924 | -0.24986 | 0.17042 | 0.09013 | 0.19937 | 0.075935 | -0.40162 | 121.5534 | 121.47 | 121.4657 | 0.32188 | -121.4528 | 121.2498 | 121.5756 | 121.098 | 0.33457 | -121.6089
654.1875 | 121.4951 | -0.15564 | 121.2845 | 1.4211e-13 | -0.013602 | 0.0026346 | 0.068409 | -0.009929 | 0.058898 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.026808 | 0.054232 | -0.003531 | 0.14792 | -0.072505 | 121.3886 | 121.3144 | 121.3055 | -0.12716 | 0.014784 | 0.17435 | -0.070087 | 121.0941 | 121.4245 | 121.185 | -0.26946 | 0.028478 | 0.10408 | 0.15211 | 0.083135 | 0.054657 | 0.029901 | 0.021039 | -0.11382 | -0.19035 | 0.17042 | 0.085553 | 0.19937 | 0.14002 | -0.09944 | 121.5442 | 121.47 | 121.4612 | 0.30356 | -121.4116 | 121.2498 | 121.5801 | 121.3407 | 0.32999 | -121.5539
655.8594 | 121.4355 | -0.16479 | 121.312 | 1.4211e-13 | -0.01403 | 0.0026346 | 0.068409 | -0.009929 | 0.058257 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.026167 | 0.054445 | 0.001048 | 0.15708 | -0.063349 | 121.3886 | 121.3098 | 121.3101 | -0.14548 | 0.014784 | 0.17435 | -0.06093 | 121.0987 | 121.4245 | 121.2125 | -0.26946 | 0.019317 | 0.076612 | 0.16584 | 0.10145 | 0.082129 | -0.002144 | -0.001848 | -0.10467 | -0.21324 | 0.17958 | 0.10386 | 0.20853 | 0.11256 | -0.099434 | 121.5534 | 121.4746 | 121.4749 | 0.32187 | -121.4574 | 121.2635 | 121.5893 | 121.3773 | 0.33915 | -121.5814
657.5938 | 121.431 | -0.16022 | 121.3165 | 1.4211e-13 | -0.013816 | 0.0026346 | 0.068409 | -0.009929 | 0.058685 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.02638 | 0.054232 | -0.008109 | 0.1525 | -0.05877 | 121.3931 | 121.3052 | 121.3055 | -0.15006 | 0.014784 | 0.16977 | -0.070087 | 121.0896 | 121.4199 | 121.0202 | -0.26488 | 0.01016 | 0.076613 | 0.15211 | 0.10145 | 0.091287 | -0.0113 | -0.011004 | -0.10467 | -0.22697 | 0.175 | 0.09013 | 0.1948 | 0.1034 | -0.29631 | 121.5534 | 121.4654 | 121.4657 | 0.31272 | -121.4666 | 121.2498 | 121.5801 | 121.1804 | 0.32999 | -121.5814
659.2812 | 121.3623 | -0.17853 | 121.344 | 1.4211e-13 | -0.013816 | 0.0026346 | 0.067981 | -0.0097152 | 0.058685 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060766 | 0.026594 | 0.054659 | -0.003531 | 0.15708 | -0.063349 | 121.3886 | 121.3144 | 121.3009 | -0.15006 | 0.010205 | 0.17435 | -0.065509 | 121.0987 | 121.4199 | 120.9927 | -0.27404 | 0.028471 | 0.044569 | 0.175 | 0.11518 | 0.086708 | -0.029608 | -0.043048 | -0.095512 | -0.24528 | 0.18873 | 0.11302 | 0.20853 | 0.075937 | -0.35125 | 121.5671 | 121.4929 | 121.4795 | 0.33561 | -121.4941 | 121.2772 | 121.5985 | 121.1713 | 0.35288 | -121.618
661.0156 | 121.5271 | -0.13275 | 121.2891 | 1.4211e-13 | -0.013816 | 0.0026346 | 0.068195 | -0.0097152 | 0.058471 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.026594 | 0.054445 | -0.012688 | 0.15708 | -0.05877 | 121.3886 | 121.3144 | 121.3101 | -0.15006 | 0.014784 | 0.17435 | -0.070087 | 121.0987 | 121.4245 | 121.1072 | -0.26488 | -0.017306 | 0.099501 | 0.12006 | 0.073981 | 0.091287 | 0.025324 | 0.021041 | -0.13213 | -0.19035 | 0.14753 | 0.062664 | 0.1948 | 0.13545 | -0.18185 | 121.5213 | 121.4471 | 121.4429 | 0.28983 | -121.4391 | 121.2315 | 121.5573 | 121.24 | 0.3071 | -121.5539
662.75 | 121.4493 | -0.14648 | 121.2891 | 1.4211e-13 | -0.013816 | 0.0026346 | 0.068195 | -0.0097152 | 0.058471 | 0.00030522 | -0.00080746 | 1.2e-08 | 0.060766 | 0.026594 | 0.054232 | -0.012688 | 0.14792 | -0.063349 | 121.3931 | 121.3098 | 121.3147 | -0.14548 | 0.019362 | 0.17435 | -0.070087 | 121.0896 | 121.4245 | 121.0065 | -0.26946 | 0.001006 | 0.10408 | 0.1338 | 0.083135 | 0.082129 | 0.020745 | 0.02562 | -0.12298 | -0.19951 | 0.16585 | 0.076397 | 0.19937 | 0.13545 | -0.28258 | 121.5396 | 121.4563 | 121.4612 | 0.29441 | -121.4345 | 121.236 | 121.571 | 121.153 | 0.32083 | -121.5585
664.4844 | 121.4996 | -0.14191 | 121.2936 | 1.4211e-13 | -0.013816 | 0.0028484 | 0.068409 | -0.0095016 | 0.058898 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060552 | 0.026808 | 0.054445 | 0.001048 | 0.1525 | -0.063349 | 121.3931 | 121.3144 | 121.3101 | -0.14548 | 0.014784 | 0.18351 | -0.070087 | 121.0987 | 121.4291 | 121.1438 | -0.26488 | -0.003571 | 0.099501 | 0.14295 | 0.078558 | 0.082129 | 0.020746 | 0.016463 | -0.12298 | -0.19493 | 0.15669 | 0.07182 | 0.1948 | 0.13545 | -0.1498 | 121.535 | 121.4563 | 121.452 | 0.29441 | -121.4391 | 121.2406 | 121.571 | 121.2857 | 0.32541 | -121.5585
666.1719 | 121.4127 | -0.18768 | 121.3623 | 1.4211e-13 | -0.013816 | 0.002421 | 0.068409 | -0.0097152 | 0.058685 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060552 | 0.02638 | 0.054232 | -0.003531 | 0.15708 | -0.067927 | 121.3977 | 121.3144 | 121.3193 | -0.15006 | 0.010205 | 0.17435 | -0.065509 | 121.1033 | 121.4291 | 121.1393 | -0.26488 | 0.037626 | 0.035415 | 0.18415 | 0.11976 | 0.08213 | -0.047919 | -0.043045 | -0.0772 | -0.25901 | 0.19789 | 0.12217 | 0.19937 | 0.066783 | -0.22305 | 121.5854 | 121.5021 | 121.5069 | 0.34476 | -121.5124 | 121.291 | 121.6168 | 121.3269 | 0.36203 | -121.6272
667.9062 | 121.4584 | -0.14191 | 121.3211 | 1.4211e-13 | -0.013602 | 0.002421 | 0.068409 | -0.009929 | 0.058471 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060766 | 0.02638 | 0.054232 | -0.012688 | 0.15708 | -0.063349 | 121.3931 | 121.3144 | 121.3147 | -0.15006 | 0.014784 | 0.17893 | -0.065509 | 121.0941 | 121.4337 | 121.0935 | -0.26946 | -0.00815 | 0.072035 | 0.12922 | 0.078558 | 0.086708 | -0.00672 | -0.006424 | -0.12755 | -0.22697 | 0.15669 | 0.076398 | 0.20395 | 0.11256 | -0.22763 | 121.535 | 121.4563 | 121.4566 | 0.29899 | -121.4712 | 121.236 | 121.5756 | 121.2354 | 0.32084 | -121.5906
669.6406 | 121.4859 | -0.13733 | 121.3211 | 1.4211e-13 | -0.013602 | 0.002421 | 0.068622 | -0.009929 | 0.058685 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060766 | 0.026594 | 0.054232 | -0.003531 | 0.16166 | -0.067927 | 121.4023 | 121.3235 | 121.3238 | -0.14548 | 0.014784 | 0.17893 | -0.065509 | 121.1079 | 121.4291 | 121.0294 | -0.26488 | -0.008149 | 0.081192 | 0.1338 | 0.069402 | 0.077551 | 0.002438 | 0.002733 | -0.12755 | -0.21323 | 0.15211 | 0.07182 | 0.19937 | 0.10798 | -0.29173 | 121.5396 | 121.4609 | 121.4612 | 0.29899 | -121.4666 | 121.2452 | 121.5664 | 121.1667 | 0.31626 | -121.586
671.3125 | 121.4127 | -0.17853 | 121.3303 | 1.4211e-13 | -0.01403 | 0.0026346 | 0.068195 | -0.0097152 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.026808 | 0.054445 | 0.005626 | 0.14792 | -0.067927 | 121.4023 | 121.319 | 121.3284 | -0.15006 | 0.010205 | 0.17435 | -0.070087 | 121.1079 | 121.4291 | 121.0935 | -0.26488 | 0.028471 | 0.072037 | 0.18415 | 0.1106 | 0.08213 | -0.011296 | -0.001844 | -0.086355 | -0.22239 | 0.18873 | 0.10844 | 0.1948 | 0.098827 | -0.23679 | 121.5808 | 121.4975 | 121.5069 | 0.32645 | -121.4803 | 121.2864 | 121.6076 | 121.272 | 0.35288 | -121.5951
673.0469 | 121.5179 | -0.13275 | 121.2982 | 1.4211e-13 | -0.013816 | 0.0026346 | 0.068409 | -0.010143 | 0.058898 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060979 | 0.026808 | 0.054232 | -0.003531 | 0.16166 | -0.067927 | 121.4069 | 121.3281 | 121.3147 | -0.14548 | 0.014784 | 0.18351 | -0.056351 | 121.1079 | 121.4291 | 121.1026 | -0.26488 | -0.012727 | 0.10866 | 0.12922 | 0.064824 | 0.077551 | 0.029905 | 0.016464 | -0.13213 | -0.19035 | 0.14753 | 0.0764 | 0.20853 | 0.13087 | -0.19559 | 121.5396 | 121.4609 | 121.4474 | 0.29441 | -121.4437 | 121.2406 | 121.5618 | 121.2354 | 0.31626 | -121.5631
674.7969 | 121.3806 | -0.18768 | 121.3348 | 1.4211e-13 | -0.013816 | 0.0028484 | 0.068622 | -0.0097152 | 0.058898 | -0.0073253 | -0.0014485 | 0.00021361 | 0.060552 | 0.026808 | 0.054232 | -0.008109 | 0.1525 | -0.067927 | 121.4069 | 121.3281 | 121.3238 | -0.13174 | 0.005626 | 0.17893 | -0.070087 | 121.1079 | 121.4382 | 121.0019 | -0.26488 | 0.055942 | 0.072037 | 0.17957 | 0.11976 | 0.063814 | -0.006716 | -0.011 | -0.0772 | -0.22697 | 0.19331 | 0.1176 | 0.1948 | 0.10341 | -0.33294 | 121.5946 | 121.5158 | 121.5115 | 0.34018 | -121.4666 | 121.2956 | 121.6259 | 121.1896 | 0.36661 | -121.5997
676.5469 | 121.3989 | -0.16937 | 121.3531 | 1.4211e-13 | -0.01403 | 0.003062 | 0.068409 | -0.0097152 | 0.058685 | 0.00030522 | -0.0014485 | 0.00042721 | 0.060552 | 0.026808 | 0.054232 | 0.001048 | 0.16166 | -0.067927 | 121.4115 | 121.3235 | 121.3284 | -0.14548 | 0.014784 | 0.18351 | -0.06093 | 121.1079 | 121.4337 | 121.1576 | -0.26946 | 0.023895 | 0.058306 | 0.17042 | 0.10145 | 0.077551 | -0.029605 | -0.024732 | -0.10009 | -0.24528 | 0.18416 | 0.10844 | 0.20853 | 0.080518 | -0.19558 | 121.5808 | 121.4929 | 121.4978 | 0.33103 | -121.4986 | 121.2772 | 121.603 | 121.3269 | 0.35288 | -121.6226
678.2188 | 121.5042 | -0.12817 | 121.2982 | 1.4211e-13 | -0.01403 | 0.0028484 | 0.067767 | -0.009929 | 0.058685 | 0.015566 | -0.0012349 | 0.00021361 | 0.060338 | 0.027021 | 0.054232 | -0.003531 | 0.16166 | -0.063349 | 121.4023 | 121.319 | 121.3284 | -0.1409 | 0.014784 | 0.18351 | -0.06093 | 121.1033 | 121.4474 | 120.8966 | -0.26488 | -0.012725 | 0.10408 | 0.12464 | 0.064825 | 0.07755 | 0.020747 | 0.030199 | -0.13671 | -0.19493 | 0.14296 | 0.067244 | 0.20395 | 0.14918 | -0.40163 | 121.5305 | 121.4471 | 121.4566 | 0.28983 | -121.4391 | 121.2315 | 121.5756 | 121.0248 | 0.31168 | -121.5631
679.9531 | 121.4996 | -0.14648 | 121.2936 | 1.4211e-13 | -0.013816 | 0.002421 | 0.067767 | -0.009929 | 0.058898 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.026808 | 0.054232 | 0.001048 | 0.1525 | -0.067927 | 121.4069 | 121.3281 | 121.3284 | -0.13632 | 0.019362 | 0.18351 | -0.06093 | 121.117 | 121.4428 | 120.9836 | -0.26946 | 0.010164 | 0.11324 | 0.14753 | 0.078557 | 0.068393 | 0.034483 | 0.034777 | -0.12298 | -0.17661 | 0.16585 | 0.085554 | 0.20853 | 0.14918 | -0.31005 | 121.5534 | 121.4746 | 121.4749 | 0.29898 | -121.43 | 121.2635 | 121.5893 | 121.1301 | 0.32999 | -121.5631
681.6875 | 121.4172 | -0.16022 | 121.3348 | 1.4211e-13 | -0.013816 | 0.0028484 | 0.068622 | -0.010143 | 0.058898 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060766 | 0.026808 | 0.054445 | 0.001048 | 0.15708 | -0.05877 | 121.4115 | 121.3327 | 121.333 | -0.11342 | 0.014784 | 0.18351 | -0.065509 | 121.1079 | 121.4382 | 121.0019 | -0.2603 | 0.046792 | 0.076616 | 0.16126 | 0.10145 | 0.054655 | -0.002138 | -0.001843 | -0.10009 | -0.22697 | 0.175 | 0.094708 | 0.19479 | 0.10341 | -0.33294 | 121.5717 | 121.4929 | 121.4932 | 0.3173 | -121.4483 | 121.2681 | 121.5985 | 121.1621 | 0.34372 | -121.5951
683.4219 | 121.4767 | -0.14191 | 121.3074 | 1.4211e-13 | -0.01403 | 0.002421 | 0.068195 | -0.009929 | 0.058898 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060766 | 0.026808 | 0.054018 | -0.003531 | 0.1525 | -0.063349 | 121.4206 | 121.3373 | 121.3376 | -0.12716 | 0.010205 | 0.19267 | -0.06093 | 121.117 | 121.452 | 121.1301 | -0.26946 | 0.014745 | 0.11324 | 0.13838 | 0.078558 | 0.063813 | 0.029907 | 0.030202 | -0.12755 | -0.19034 | 0.15211 | 0.080977 | 0.20853 | 0.14461 | -0.17727 | 121.5625 | 121.4792 | 121.4795 | 0.29441 | -121.4345 | 121.2589 | 121.5939 | 121.272 | 0.33457 | -121.5768
685.1094 | 121.3898 | -0.16937 | 121.376 | 1.4211e-13 | -0.013816 | 0.0028484 | 0.068195 | -0.009929 | 0.058898 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060125 | 0.026808 | 0.054018 | -0.003531 | 0.15708 | -0.067927 | 121.4115 | 121.3373 | 121.3422 | -0.13174 | 0.014784 | 0.19267 | -0.06093 | 121.117 | 121.4474 | 121.0385 | -0.25572 | 0.037632 | 0.035417 | 0.16584 | 0.10145 | 0.063814 | -0.038758 | -0.033885 | -0.086352 | -0.25901 | 0.18416 | 0.10844 | 0.19479 | 0.071364 | -0.33751 | 121.5808 | 121.5067 | 121.5115 | 0.32645 | -121.5078 | 121.2864 | 121.6168 | 121.2079 | 0.36204 | -121.6318
686.8438 | 121.4218 | -0.17853 | 121.3486 | 1.4211e-13 | -0.013816 | 0.0022072 | 0.067767 | -0.010143 | 0.058898 | -0.0073253 | -0.0014485 | -0.00021359 | 0.060766 | 0.027021 | 0.054659 | 0.001048 | 0.15708 | -0.067927 | 121.4069 | 121.3373 | 121.3376 | -0.10885 | 0.019362 | 0.18809 | -0.070087 | 121.1262 | 121.4566 | 121.1438 | -0.2603 | 0.069681 | 0.058304 | 0.17958 | 0.1106 | 0.04092 | -0.011292 | -0.010997 | -0.081776 | -0.22239 | 0.19789 | 0.10844 | 0.19022 | 0.10799 | -0.20473 | 121.5854 | 121.5158 | 121.5161 | 0.33561 | -121.4574 | 121.3047 | 121.6351 | 121.3224 | 0.36661 | -121.6089
688.5781 | 121.4172 | -0.15564 | 121.3531 | 1.4211e-13 | -0.013816 | 0.002421 | 0.067981 | -0.0097152 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.027021 | 0.054232 | 0.001048 | 0.15708 | -0.063349 | 121.4115 | 121.3419 | 121.3422 | -0.13174 | 0.014784 | 0.18809 | -0.06093 | 121.117 | 121.452 | 120.9607 | -0.2603 | 0.023899 | 0.058306 | 0.15669 | 0.092291 | 0.068392 | -0.01129 | -0.010996 | -0.10466 | -0.23612 | 0.17042 | 0.09471 | 0.19937 | 0.098832 | -0.39246 | 121.5671 | 121.4975 | 121.4978 | 0.31272 | -121.4849 | 121.2727 | 121.6076 | 121.1163 | 0.34373 | -121.6135
690.2656 | 121.3943 | -0.1831 | 121.3623 | 1.4211e-13 | -0.014243 | 0.002421 | 0.068622 | -0.0095016 | 0.058685 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.026594 | 0.054445 | 0.001048 | 0.16166 | -0.067927 | 121.4115 | 121.3373 | 121.3422 | -0.10885 | 0.019362 | 0.18351 | -0.06093 | 121.1216 | 121.452 | 120.947 | -0.26488 | 0.074258 | 0.04915 | 0.18415 | 0.11518 | 0.04092 | -0.025025 | -0.020152 | -0.081778 | -0.2407 | 0.20247 | 0.12217 | 0.20395 | 0.089676 | -0.41535 | 121.5946 | 121.5204 | 121.5253 | 0.34476 | -121.4712 | 121.3047 | 121.6351 | 121.1301 | 0.36661 | -121.6272
692.0156 | 121.4905 | -0.13275 | 121.3303 | 1.4211e-13 | -0.014243 | 0.0026346 | 0.068195 | -0.009929 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.027021 | 0.054232 | 0.001048 | 0.15708 | -0.067927 | 121.4206 | 121.3464 | 121.3467 | -0.10885 | 0.014784 | 0.17893 | -0.06093 | 121.1079 | 121.452 | 121.0843 | -0.26488 | 0.023904 | 0.09035 | 0.1338 | 0.064824 | 0.04092 | 0.016177 | 0.016471 | -0.13213 | -0.22239 | 0.14753 | 0.071821 | 0.20395 | 0.12172 | -0.24594 | 121.5534 | 121.4792 | 121.4795 | 0.28983 | -121.4391 | 121.2406 | 121.5847 | 121.2171 | 0.31168 | -121.5951
693.6875 | 121.4722 | -0.13275 | 121.3211 | 1.4211e-13 | -0.014243 | 0.0026346 | 0.068195 | -0.010143 | 0.058471 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.027021 | 0.054232 | 0.001048 | 0.15708 | -0.05877 | 121.4115 | 121.3464 | 121.3467 | -0.12716 | 0.019362 | 0.18809 | -0.056351 | 121.1216 | 121.4474 | 120.8371 | -0.2603 | 0.005589 | 0.090349 | 0.1338 | 0.073981 | 0.068392 | 0.025332 | 0.025626 | -0.12755 | -0.1995 | 0.15211 | 0.0764 | 0.20395 | 0.1263 | -0.48404 | 121.5442 | 121.4792 | 121.4795 | 0.28983 | -121.4483 | 121.2544 | 121.5802 | 120.9698 | 0.32084 | -121.5814
695.4219 | 121.3989 | -0.17853 | 121.3486 | 1.4211e-13 | -0.014243 | 0.002421 | 0.068622 | -0.0097152 | 0.058685 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060125 | 0.026808 | 0.054445 | -0.003531 | 0.15708 | -0.063349 | 121.4206 | 121.3464 | 121.3467 | -0.10885 | 0.019362 | 0.18351 | -0.065509 | 121.1216 | 121.452 | 120.9012 | -0.26488 | 0.069681 | 0.072039 | 0.175 | 0.11518 | 0.045498 | -0.002134 | -0.00184 | -0.086355 | -0.22697 | 0.19789 | 0.11302 | 0.19937 | 0.10341 | -0.4474 | 121.5991 | 121.525 | 121.5253 | 0.33561 | -121.4574 | 121.3001 | 121.6305 | 121.0797 | 0.36203 | -121.6135
697.1719 | 121.3852 | -0.20142 | 121.3531 | 1.4211e-13 | -0.01403 | 0.002421 | 0.068195 | -0.0097152 | 0.058685 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060338 | 0.027021 | 0.054445 | -0.003531 | 0.15708 | -0.067927 | 121.4206 | 121.3464 | 121.3605 | -0.099689 | 0.019362 | 0.19267 | -0.06093 | 121.1308 | 121.452 | 120.9057 | -0.26946 | 0.10173 | 0.067462 | 0.19789 | 0.13349 | 0.031762 | -0.006711 | 0.007319 | -0.068046 | -0.22239 | 0.22078 | 0.14049 | 0.20853 | 0.098832 | -0.4474 | 121.622 | 121.5479 | 121.5619 | 0.3585 | -121.4528 | 121.3322 | 121.6534 | 121.1072 | 0.39408 | -121.6226
698.8594 | 121.3806 | -0.17853 | 121.3394 | 1.4211e-13 | -0.014243 | 0.0026346 | 0.068622 | -0.010143 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060125 | 0.026594 | 0.054445 | -0.008109 | 0.15708 | -0.063349 | 121.4252 | 121.3419 | 121.3467 | -0.10427 | 0.014784 | 0.19267 | -0.06093 | 121.1262 | 121.452 | 120.9836 | -0.26488 | 0.07426 | 0.085773 | 0.17042 | 0.11518 | 0.040919 | 0.002442 | 0.007315 | -0.086355 | -0.21323 | 0.19331 | 0.1176 | 0.20395 | 0.11256 | -0.35583 | 121.6037 | 121.5204 | 121.5253 | 0.33561 | -121.4437 | 121.3047 | 121.6305 | 121.1621 | 0.37119 | -121.6043
700.6094 | 121.5271 | -0.13275 | 121.3394 | 1.4211e-13 | -0.014243 | 0.0026346 | 0.067981 | -0.0097152 | 0.058685 | 0.023196 | -0.0012349 | -0.00021359 | 0.060766 | 0.026808 | 0.054232 | 0.001048 | 0.1525 | -0.067927 | 121.4206 | 121.351 | 121.3513 | -0.053899 | 0.019362 | 0.19267 | -0.06093 | 121.1262 | 121.4566 | 120.9515 | -0.2603 | 0.078852 | 0.081194 | 0.1338 | 0.064824 | -0.014028 | 0.0116 | 0.011893 | -0.12755 | -0.21323 | 0.15211 | 0.071821 | 0.19937 | 0.11714 | -0.38788 | 121.5534 | 121.4838 | 121.4841 | 0.28525 | -121.3933 | 121.2589 | 121.5893 | 121.0843 | 0.32542 | -121.5997
702.3438 | 121.4401 | -0.16022 | 121.3623 | 1.4211e-13 | -0.014457 | 0.002421 | 0.067981 | -0.009929 | 0.058685 | 0.015566 | -0.0014485 | 1.2e-08 | 0.060766 | 0.027021 | 0.054445 | -0.003531 | 0.1525 | -0.067927 | 121.4252 | 121.3419 | 121.3559 | -0.072215 | 0.014784 | 0.19267 | -0.065509 | 121.1308 | 121.4611 | 121.0752 | -0.2603 | 0.088002 | 0.062885 | 0.15669 | 0.09229 | 0.004288 | -0.020446 | -0.006416 | -0.10009 | -0.23154 | 0.175 | 0.094708 | 0.19479 | 0.098833 | -0.28715 | 121.5854 | 121.5021 | 121.5161 | 0.31272 | -121.4345 | 121.291 | 121.6214 | 121.2354 | 0.35288 | -121.6226
704.0312 | 121.4767 | -0.1236 | 121.3623 | 1.4211e-13 | -0.014457 | 0.0019936 | 0.068195 | -0.010143 | 0.058685 | -0.0073253 | -0.0014485 | 1.2e-08 | 0.060552 | 0.027449 | 0.054232 | 0.005626 | 0.15708 | -0.054192 | 121.4298 | 121.3556 | 121.3513 | -0.049321 | 0.014784 | 0.18809 | -0.06093 | 121.1262 | 121.4611 | 121.0111 | -0.2603 | 0.074275 | 0.067463 | 0.12922 | 0.069404 | -0.004871 | -0.006709 | -0.010995 | -0.13671 | -0.23612 | 0.13838 | 0.062666 | 0.19937 | 0.098833 | -0.35125 | 121.5534 | 121.4792 | 121.4749 | 0.28068 | -121.4116 | 121.2498 | 121.5847 | 121.1347 | 0.31168 | -121.6226
705.7188 | 121.4264 | -0.16022 | 121.3669 | 1.4211e-13 | -0.014457 | 0.002421 | 0.068195 | -0.010143 | 0.058898 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060338 | 0.027235 | 0.054232 | 0.010204 | 0.15708 | -0.063349 | 121.4298 | 121.351 | 121.3467 | -0.076794 | 0.02852 | 0.20182 | -0.051772 | 121.1353 | 121.4657 | 121.1164 | -0.2603 | 0.083423 | 0.062886 | 0.17042 | 0.096868 | 0.013445 | -0.015865 | -0.02015 | -0.10009 | -0.23154 | 0.18874 | 0.10844 | 0.20853 | 0.098835 | -0.25052 | 121.59 | 121.5112 | 121.5069 | 0.3173 | -121.4437 | 121.2956 | 121.6259 | 121.2766 | 0.36204 | -121.6272
707.4531 | 121.5271 | -0.1236 | 121.3165 | 1.4211e-13 | -0.014457 | 0.002421 | 0.068409 | -0.0097152 | 0.058471 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060338 | 0.027021 | 0.054232 | 0.005626 | 0.1525 | -0.067927 | 121.4298 | 121.3602 | 121.3605 | -0.072215 | 0.019362 | 0.19267 | -0.06093 | 121.1262 | 121.4657 | 121.0156 | -0.25572 | 0.051381 | 0.11324 | 0.12922 | 0.055669 | 0.004288 | 0.043647 | 0.04394 | -0.13213 | -0.19034 | 0.14296 | 0.062666 | 0.19479 | 0.14919 | -0.30089 | 121.5534 | 121.4838 | 121.4841 | 0.2761 | -121.3887 | 121.2498 | 121.5893 | 121.1392 | 0.31626 | -121.5723
709.2031 | 121.5271 | -0.11902 | 121.3348 | 1.4211e-13 | -0.014457 | 0.0026346 | 0.068195 | -0.0097152 | 0.058685 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.026808 | 0.054659 | 0.001048 | 0.1525 | -0.067927 | 121.4435 | 121.351 | 121.365 | -0.090531 | 0.019362 | 0.19724 | -0.06093 | 121.1399 | 121.4703 | 121.0202 | -0.25572 | 0.028488 | 0.10866 | 0.12007 | 0.051092 | 0.022604 | 0.016178 | 0.030207 | -0.13671 | -0.19492 | 0.13838 | 0.058089 | 0.19479 | 0.13546 | -0.31462 | 121.5625 | 121.47 | 121.4841 | 0.27152 | -121.4254 | 121.2589 | 121.5893 | 121.1392 | 0.31626 | -121.5906
710.875 | 121.4355 | -0.16479 | 121.3623 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068195 | -0.009929 | 0.058898 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060552 | 0.027449 | 0.054018 | 0.001048 | 0.16166 | -0.05877 | 121.4343 | 121.3602 | 121.3605 | -0.063057 | 0.02852 | 0.2064 | -0.056351 | 121.1353 | 121.4657 | 121.1438 | -0.26488 | 0.10174 | 0.072042 | 0.16584 | 0.10602 | 0.004287 | -0.00213 | -0.001837 | -0.10009 | -0.22696 | 0.19331 | 0.10844 | 0.20853 | 0.10341 | -0.21847 | 121.5991 | 121.525 | 121.5253 | 0.32645 | -121.4254 | 121.3001 | 121.6305 | 121.3086 | 0.3712 | -121.6272
712.6094 | 121.5408 | -0.13275 | 121.344 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068622 | -0.009929 | 0.059112 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060552 | 0.027021 | 0.054018 | 0.001048 | 0.15708 | -0.05877 | 121.4343 | 121.3602 | 121.365 | -0.021847 | 0.014784 | 0.2064 | -0.056351 | 121.1399 | 121.4703 | 120.8829 | -0.2603 | 0.1109 | 0.090353 | 0.1338 | 0.073981 | -0.036923 | 0.016181 | 0.021052 | -0.12755 | -0.20407 | 0.14753 | 0.0764 | 0.20395 | 0.1263 | -0.46114 | 121.5671 | 121.4929 | 121.4978 | 0.28983 | -121.3658 | 121.2727 | 121.603 | 121.0156 | 0.33915 | -121.6043
714.2969 | 121.4767 | -0.1236 | 121.3165 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068195 | -0.010356 | 0.058471 | 0.015566 | -0.0014485 | 1.2e-08 | 0.060766 | 0.026808 | 0.054232 | 0.001048 | 0.15708 | -0.063349 | 121.4389 | 121.3602 | 121.365 | -0.035584 | 0.02852 | 0.19267 | -0.06093 | 121.1353 | 121.4749 | 120.9973 | -0.25115 | 0.088012 | 0.1224 | 0.12464 | 0.060247 | -0.027765 | 0.043647 | 0.048518 | -0.12755 | -0.18119 | 0.15212 | 0.062666 | 0.19022 | 0.15835 | -0.31921 | 121.5625 | 121.4838 | 121.4886 | 0.28068 | -121.3521 | 121.2589 | 121.5985 | 121.1209 | 0.31626 | -121.5677
716.0469 | 121.4035 | -0.17853 | 121.3669 | 1.4211e-13 | -0.01403 | 0.002421 | 0.068409 | -0.010143 | 0.058471 | 0.00030522 | -0.0016621 | 1.2e-08 | 0.060552 | 0.027021 | 0.053804 | 0.010204 | 0.16624 | -0.05877 | 121.4435 | 121.3739 | 121.365 | -0.035584 | 0.023941 | 0.2064 | -0.047194 | 121.1491 | 121.4703 | 121.0614 | -0.25572 | 0.14294 | 0.076621 | 0.18873 | 0.11976 | -0.023186 | 0.00703 | -0.001836 | -0.077197 | -0.2178 | 0.20247 | 0.13133 | 0.20853 | 0.10341 | -0.30546 | 121.622 | 121.5524 | 121.5436 | 0.34476 | -121.4025 | 121.3276 | 121.6488 | 121.24 | 0.38493 | -121.6226
717.7188 | 121.4447 | -0.15564 | 121.3577 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068409 | -0.009929 | 0.058898 | 0.00030522 | -0.0010211 | 0.00021361 | 0.060125 | 0.027235 | 0.054232 | 0.010204 | 0.16166 | -0.067927 | 121.4343 | 121.3648 | 121.365 | -0.076794 | 0.023941 | 0.19724 | -0.051772 | 121.1262 | 121.4795 | 120.9699 | -0.25115 | 0.078846 | 0.07662 | 0.16584 | 0.087713 | 0.008867 | 0.007027 | 0.007319 | -0.095506 | -0.23154 | 0.17958 | 0.10387 | 0.19937 | 0.12173 | -0.38788 | 121.59 | 121.5204 | 121.5207 | 0.3173 | -121.4345 | 121.2818 | 121.6351 | 121.1255 | 0.35288 | -121.6089
719.4531 | 121.4859 | -0.14648 | 121.3165 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068409 | -0.010143 | 0.058685 | 0.015566 | -0.0014485 | 0.00021361 | 0.060552 | 0.027235 | 0.054445 | 0.005626 | 0.15708 | -0.072505 | 121.4389 | 121.3648 | 121.3696 | -0.044742 | 0.023941 | 0.19724 | -0.06093 | 121.1445 | 121.4749 | 121.0248 | -0.25572 | 0.10174 | 0.1224 | 0.15211 | 0.073979 | -0.027763 | 0.048226 | 0.053097 | -0.10924 | -0.17203 | 0.17042 | 0.085554 | 0.19479 | 0.15835 | -0.29173 | 121.5854 | 121.5112 | 121.5161 | 0.30356 | -121.3613 | 121.291 | 121.6214 | 121.1713 | 0.34373 | -121.5723
721.2031 | 121.4081 | -0.16937 | 121.3715 | 1.4211e-13 | -0.014457 | 0.0026346 | 0.068622 | -0.010143 | 0.058685 | 0.015566 | -0.0012349 | 0.00042721 | 0.060338 | 0.027021 | 0.054232 | 0.001048 | 0.15708 | -0.063349 | 121.4481 | 121.3693 | 121.3788 | -0.021847 | 0.033099 | 0.19724 | -0.056351 | 121.1491 | 121.4795 | 120.9103 | -0.25115 | 0.14753 | 0.076622 | 0.17042 | 0.10602 | -0.041502 | -0.002127 | 0.007322 | -0.081773 | -0.22238 | 0.20247 | 0.11302 | 0.19479 | 0.10799 | -0.46113 | 121.6175 | 121.5387 | 121.5482 | 0.32645 | -121.3933 | 121.3185 | 121.6488 | 121.0797 | 0.36662 | -121.6226
722.9375 | 121.5363 | -0.10986 | 121.3715 | 1.4211e-13 | -0.014457 | 0.0028484 | 0.068622 | -0.010143 | 0.058898 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060338 | 0.027021 | 0.054445 | 0.005626 | 0.16166 | -0.05877 | 121.4389 | 121.3648 | 121.3696 | -0.012689 | 0.019362 | 0.20182 | -0.051772 | 121.1537 | 121.4749 | 121.153 | -0.25572 | 0.097174 | 0.067465 | 0.11549 | 0.051093 | -0.046081 | -0.006706 | -0.001835 | -0.14586 | -0.2178 | 0.12923 | 0.058091 | 0.20395 | 0.10341 | -0.21846 | 121.5488 | 121.4746 | 121.4795 | 0.27152 | -121.3841 | 121.2635 | 121.5847 | 121.2629 | 0.31168 | -121.6272
724.6719 | 121.5042 | -0.1236 | 121.3669 | 1.4211e-13 | -0.014671 | 0.0026346 | 0.068195 | -0.009929 | 0.058685 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.027235 | 0.054018 | 0.005626 | 0.16166 | -0.063349 | 121.4435 | 121.3739 | 121.3742 | -0.026426 | 0.023941 | 0.2064 | -0.056351 | 121.1537 | 121.4795 | 121.0111 | -0.25572 | 0.09717 | 0.076621 | 0.12922 | 0.060247 | -0.036923 | 0.00703 | 0.007321 | -0.13213 | -0.21323 | 0.14754 | 0.067245 | 0.19937 | 0.11257 | -0.35582 | 121.5671 | 121.4975 | 121.4978 | 0.28525 | -121.3933 | 121.2773 | 121.603 | 121.1347 | 0.33 | -121.6226
726.4219 | 121.5225 | -0.13733 | 121.3577 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068409 | -0.010143 | 0.058471 | -0.0073253 | -0.0012349 | 0.00042721 | 0.060552 | 0.027662 | 0.054232 | 0.001048 | 0.1525 | -0.054192 | 121.4481 | 121.3648 | 121.3879 | -0.058478 | 0.023941 | 0.21556 | -0.06093 | 121.1491 | 121.4749 | 121.0889 | -0.25115 | 0.078851 | 0.090355 | 0.13838 | 0.083137 | 0.004286 | 0.007027 | 0.030212 | -0.11382 | -0.20865 | 0.16127 | 0.076399 | 0.19022 | 0.11715 | -0.26883 | 121.5854 | 121.5021 | 121.5253 | 0.28983 | -121.4162 | 121.2864 | 121.6122 | 121.2262 | 0.35289 | -121.6089
728.0938 | 121.4584 | -0.14648 | 121.3989 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068409 | -0.0097152 | 0.058257 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.027449 | 0.054018 | 0.001048 | 0.16166 | -0.05877 | 121.4481 | 121.3739 | 121.3788 | -0.072215 | 0.023941 | 0.20182 | -0.056351 | 121.1537 | 121.4886 | 121.0706 | -0.2603 | 0.074269 | 0.049156 | 0.14753 | 0.087714 | 0.013445 | -0.025014 | -0.020144 | -0.11382 | -0.24527 | 0.17042 | 0.090133 | 0.20395 | 0.089684 | -0.32835 | 121.5946 | 121.5204 | 121.5253 | 0.30814 | -121.4711 | 121.3001 | 121.6351 | 121.2171 | 0.34831 | -121.6592
729.8438 | 121.5317 | -0.11902 | 121.3165 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068409 | -0.010356 | 0.058471 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060766 | 0.027449 | 0.054659 | 0.001048 | 0.16166 | -0.063349 | 121.4481 | 121.3693 | 121.3742 | -0.031005 | 0.033099 | 0.2064 | -0.056351 | 121.1537 | 121.4886 | 121.0935 | -0.25115 | 0.088014 | 0.13155 | 0.12007 | 0.05567 | -0.032344 | 0.052805 | 0.057675 | -0.13213 | -0.16287 | 0.15212 | 0.062668 | 0.19479 | 0.17208 | -0.22306 | 121.5671 | 121.4884 | 121.4932 | 0.28068 | -121.3475 | 121.2727 | 121.6076 | 121.2125 | 0.32542 | -121.5677
731.5938 | 121.3989 | -0.1831 | 121.3898 | 1.4211e-13 | -0.014671 | 0.0026346 | 0.068409 | -0.010356 | 0.058685 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060552 | 0.027235 | 0.054445 | 0.005626 | 0.16624 | -0.05877 | 121.4481 | 121.3785 | 121.3879 | -0.072215 | 0.023941 | 0.21098 | -0.051772 | 121.1537 | 121.4795 | 121.1347 | -0.2603 | 0.11089 | 0.058311 | 0.18873 | 0.12433 | 0.013445 | -0.01128 | -0.001832 | -0.077199 | -0.23611 | 0.20705 | 0.13133 | 0.20853 | 0.089682 | -0.25509 | 121.6312 | 121.5616 | 121.571 | 0.34934 | -121.462 | 121.3368 | 121.6626 | 121.3178 | 0.39409 | -121.6501
733.2656 | 121.4035 | -0.17853 | 121.4081 | 1.4211e-13 | -0.014457 | 0.002421 | 0.068409 | -0.010143 | 0.058471 | -0.0073253 | -0.0010211 | 0.00042721 | 0.060552 | 0.027449 | 0.054232 | 0.010204 | 0.16166 | -0.063349 | 121.4435 | 121.3739 | 121.3834 | -0.072215 | 0.023941 | 0.21098 | -0.051772 | 121.1582 | 121.484 | 121.1805 | -0.25572 | 0.10631 | 0.035422 | 0.18873 | 0.11518 | 0.008866 | -0.034169 | -0.02472 | -0.077197 | -0.24985 | 0.20247 | 0.12676 | 0.20395 | 0.07595 | -0.22762 | 121.622 | 121.5524 | 121.5619 | 0.34019 | -121.4803 | 121.3368 | 121.6626 | 121.359 | 0.38951 | -121.6638
735 | 121.4584 | -0.16937 | 121.3898 | 1.4211e-13 | -0.014243 | 0.0028484 | 0.068195 | -0.010143 | 0.058898 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060338 | 0.026808 | 0.054018 | 0.005626 | 0.16166 | -0.063349 | 121.4481 | 121.3693 | 121.3742 | -0.058478 | 0.033099 | 0.2064 | -0.051772 | 121.1445 | 121.4795 | 121.0568 | -0.25115 | 0.11089 | 0.058311 | 0.175 | 0.10602 | -0.004871 | -0.020438 | -0.015568 | -0.081773 | -0.24527 | 0.20247 | 0.1176 | 0.19937 | 0.089682 | -0.33293 | 121.6175 | 121.5387 | 121.5436 | 0.33103 | -121.4482 | 121.3139 | 121.6488 | 121.2262 | 0.37577 | -121.6409
736.6719 | 121.5042 | -0.1236 | 121.3531 | 1.4211e-13 | -0.014884 | 0.0026346 | 0.068409 | -0.010143 | 0.058471 | 0.015566 | -0.0014485 | 0.00021361 | 0.060338 | 0.027449 | 0.054232 | 0.005626 | 0.15708 | -0.063349 | 121.4527 | 121.3739 | 121.3834 | -0.099689 | 0.019362 | 0.21556 | -0.06093 | 121.1491 | 121.4795 | 121.1118 | -0.25572 | 0.023907 | 0.099511 | 0.12922 | 0.060247 | 0.03634 | 0.020763 | 0.030212 | -0.13213 | -0.20407 | 0.14296 | 0.062666 | 0.19479 | 0.1263 | -0.24136 | 121.5763 | 121.4975 | 121.507 | 0.28068 | -121.4528 | 121.2727 | 121.603 | 121.2354 | 0.33915 | -121.6089
738.4062 | 121.5454 | -0.10986 | 121.3348 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068195 | -0.010143 | 0.058685 | 0.0079357 | -0.0016621 | 0.00042721 | 0.060552 | 0.027449 | 0.054232 | 0.014783 | 0.16166 | -0.054192 | 121.4527 | 121.3785 | 121.3834 | -0.035584 | 0.019362 | 0.21556 | -0.051772 | 121.1582 | 121.4886 | 120.9195 | -0.25572 | 0.074279 | 0.11782 | 0.12465 | 0.055671 | -0.018608 | 0.043652 | 0.048522 | -0.14586 | -0.1766 | 0.12923 | 0.058091 | 0.20395 | 0.15377 | -0.41535 | 121.5625 | 121.4884 | 121.4932 | 0.27152 | -121.3704 | 121.2681 | 121.5985 | 121.0293 | 0.32542 | -121.5906
740.1562 | 121.4951 | -0.13733 | 121.3486 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068409 | -0.010143 | 0.058471 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.027021 | 0.054018 | 0.010204 | 0.1525 | -0.05877 | 121.4527 | 121.3785 | 121.3925 | -0.053899 | 0.02852 | 0.22472 | -0.051772 | 121.1628 | 121.484 | 121.153 | -0.2603 | 0.08343 | 0.10409 | 0.14753 | 0.078559 | -0.004871 | 0.029919 | 0.043946 | -0.12297 | -0.18576 | 0.16585 | 0.085557 | 0.20853 | 0.13546 | -0.19558 | 121.59 | 121.5158 | 121.5298 | 0.28983 | -121.4025 | 121.3001 | 121.6214 | 121.2903 | 0.36205 | -121.6089
741.8906 | 121.4172 | -0.16479 | 121.4127 | 1.4211e-13 | -0.014884 | 0.0026346 | 0.068195 | -0.010356 | 0.058685 | 0.0079357 | -0.0014485 | 0.00042721 | 0.060552 | 0.027449 | 0.054232 | 0.001048 | 0.16166 | -0.05877 | 121.4572 | 121.3831 | 121.3788 | -0.026426 | 0.023941 | 0.22014 | -0.06093 | 121.1537 | 121.4978 | 120.9332 | -0.25115 | 0.13837 | 0.04458 | 0.16584 | 0.10602 | -0.032344 | -0.029589 | -0.033877 | -0.086351 | -0.259 | 0.18874 | 0.10386 | 0.19022 | 0.085108 | -0.47944 | 121.622 | 121.5479 | 121.5436 | 0.32645 | -121.4391 | 121.3185 | 121.6626 | 121.098 | 0.38493 | -121.6638
743.5625 | 121.4172 | -0.16022 | 121.3898 | 1.4211e-13 | -0.014884 | 0.0026346 | 0.068409 | -0.01057 | 0.058898 | 0.015566 | -0.0014485 | 1.2e-08 | 0.060766 | 0.027235 | 0.054232 | 0.005626 | 0.16166 | -0.054192 | 121.4527 | 121.3831 | 121.3834 | -0.035584 | 0.023941 | 0.21556 | -0.051772 | 121.1674 | 121.484 | 121.066 | -0.25115 | 0.12463 | 0.062889 | 0.16584 | 0.10603 | -0.018608 | -0.006701 | -0.00641 | -0.090929 | -0.22238 | 0.18416 | 0.10844 | 0.19937 | 0.09426 | -0.32377 | 121.6129 | 121.5433 | 121.5436 | 0.32188 | -121.4254 | 121.3276 | 121.6442 | 121.2262 | 0.37577 | -121.6409
745.3125 | 121.4859 | -0.13275 | 121.3623 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068195 | -0.010143 | 0.058257 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060766 | 0.027449 | 0.054232 | 0.005626 | 0.15708 | -0.05877 | 121.4527 | 121.3831 | 121.3925 | -0.063057 | 0.023941 | 0.22472 | -0.056351 | 121.1582 | 121.4886 | 121.0156 | -0.25115 | 0.069694 | 0.090355 | 0.13838 | 0.073981 | 0.004287 | 0.020765 | 0.030213 | -0.11839 | -0.20407 | 0.15669 | 0.0764 | 0.19479 | 0.1263 | -0.34667 | 121.5854 | 121.5158 | 121.5253 | 0.28983 | -121.4254 | 121.291 | 121.6214 | 121.1484 | 0.35747 | -121.6135
747.0625 | 121.4081 | -0.15106 | 121.376 | 1.4211e-13 | -0.014671 | 0.002421 | 0.068409 | -0.010143 | 0.058471 | -0.0073253 | -0.0014485 | 1.2e-08 | 0.060766 | 0.027662 | 0.054018 | 0.005626 | 0.16624 | -0.067927 | 121.4572 | 121.3831 | 121.3925 | -0.012689 | 0.023941 | 0.22014 | -0.051772 | 121.1537 | 121.4932 | 121.0019 | -0.24657 | 0.13837 | 0.081201 | 0.15669 | 0.083135 | -0.055238 | 0.007032 | 0.01648 | -0.095505 | -0.22238 | 0.175 | 0.09929 | 0.19479 | 0.11715 | -0.37414 | 121.6083 | 121.5341 | 121.5436 | 0.3173 | -121.3887 | 121.3047 | 121.6443 | 121.153 | 0.3712 | -121.6226
748.8125 | 121.4539 | -0.16937 | 121.3623 | 1.4211e-13 | -0.014884 | 0.0026346 | 0.068409 | -0.010784 | 0.058257 | 0.0079357 | -0.0016621 | 0.00021361 | 0.060552 | 0.027235 | 0.054232 | 0.010204 | 0.16624 | -0.063349 | 121.4572 | 121.3831 | 121.3925 | -0.053899 | 0.02852 | 0.22929 | -0.051772 | 121.1582 | 121.4932 | 121.0202 | -0.2603 | 0.11547 | 0.094934 | 0.17958 | 0.10602 | -0.00945 | 0.020765 | 0.030213 | -0.090931 | -0.20407 | 0.19789 | 0.1176 | 0.20853 | 0.13088 | -0.34209 | 121.6266 | 121.5524 | 121.5619 | 0.33561 | -121.4162 | 121.3276 | 121.6626 | 121.1896 | 0.39867 | -121.6226
750.5469 | 121.4584 | -0.16479 | 121.3989 | 1.4211e-13 | -0.015098 | 0.002421 | 0.068195 | -0.010356 | 0.058685 | 0.015566 | -0.0014485 | -0.00021359 | 0.060552 | 0.027876 | 0.054232 | 0.005626 | 0.16166 | -0.063349 | 121.4481 | 121.3922 | 121.3971 | -0.081373 | 0.02852 | 0.22014 | -0.056351 | 121.1628 | 121.4978 | 121.0568 | -0.25572 | 0.083422 | 0.049156 | 0.17042 | 0.10145 | 0.018024 | -0.006698 | -0.00183 | -0.09093 | -0.23611 | 0.19331 | 0.10844 | 0.19937 | 0.098841 | -0.34208 | 121.6129 | 121.557 | 121.5619 | 0.32645 | -121.4803 | 121.3276 | 121.6626 | 121.2216 | 0.38493 | -121.6547
752.3594 | 121.3852 | -0.17395 | 121.4172 | 1.4211e-13 | -0.015098 | 0.0026346 | 0.068195 | -0.010143 | 0.058685 | -0.0073253 | -0.0012349 | 1.2e-08 | 0.060552 | 0.027662 | 0.054232 | 0.001048 | 0.16166 | -0.05877 | 121.4664 | 121.3876 | 121.3971 | -0.081373 | 0.02852 | 0.22472 | -0.056351 | 121.172 | 121.5023 | 121.1622 | -0.25115 | 0.092577 | 0.049159 | 0.175 | 0.11518 | 0.022603 | -0.029587 | -0.02014 | -0.077196 | -0.24527 | 0.20247 | 0.1176 | 0.19479 | 0.08511 | -0.25508 | 121.6403 | 121.5616 | 121.571 | 0.33561 | -121.4986 | 121.3459 | 121.6763 | 121.3361 | 0.39867 | -121.6684
754.1094 | 121.4218 | -0.16022 | 121.3989 | 1.4211e-13 | -0.015098 | 0.0028484 | 0.067981 | -0.010143 | 0.058471 | 0.015566 | -0.0012349 | 1.2e-08 | 0.060338 | 0.027235 | 0.054018 | 0.010204 | 0.15708 | -0.049614 | 121.4664 | 121.3876 | 121.4017 | -0.072215 | 0.023941 | 0.22472 | -0.06093 | 121.1674 | 121.5023 | 121.1713 | -0.25572 | 0.088002 | 0.067469 | 0.17042 | 0.1106 | 0.022601 | -0.011277 | 0.002749 | -0.095508 | -0.23153 | 0.18416 | 0.099287 | 0.19479 | 0.10342 | -0.22762 | 121.6266 | 121.5479 | 121.5619 | 0.3173 | -121.4711 | 121.3276 | 121.6626 | 121.3315 | 0.38493 | -121.6547
755.8281 | 121.5317 | -0.10071 | 121.344 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068409 | -0.01057 | 0.058685 | -0.0073253 | -0.0010211 | 0.00021361 | 0.060338 | 0.027449 | 0.054232 | -0.003531 | 0.1525 | -0.049614 | 121.4618 | 121.3876 | 121.4017 | -0.053899 | 0.033099 | 0.22014 | -0.056351 | 121.1628 | 121.4978 | 121.1484 | -0.25572 | 0.046809 | 0.11782 | 0.097177 | 0.051094 | 0.004285 | 0.043655 | 0.057681 | -0.15502 | -0.18118 | 0.13381 | 0.044357 | 0.19937 | 0.15377 | -0.19558 | 121.5625 | 121.4884 | 121.5024 | 0.25321 | -121.3979 | 121.2635 | 121.5985 | 121.2491 | 0.32084 | -121.5997
757.5312 | 121.4401 | -0.15106 | 121.4035 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068195 | -0.010143 | 0.058685 | 0.015566 | -0.0012349 | 1.2e-08 | 0.060125 | 0.027662 | 0.054018 | 0.010204 | 0.16624 | -0.067927 | 121.4572 | 121.3922 | 121.4063 | -0.035584 | 0.023941 | 0.22472 | -0.051772 | 121.1628 | 121.5069 | 120.9882 | -0.25115 | 0.11548 | 0.053736 | 0.16127 | 0.083135 | -0.032343 | -0.011275 | 0.002751 | -0.10008 | -0.24069 | 0.175 | 0.09929 | 0.19937 | 0.10342 | -0.41534 | 121.6083 | 121.5433 | 121.5573 | 0.3173 | -121.4391 | 121.3139 | 121.658 | 121.1392 | 0.37578 | -121.6546
759.2344 | 121.5637 | -0.11902 | 121.3486 | 1.4211e-13 | -0.014884 | 0.0022072 | 0.068195 | -0.010143 | 0.058257 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060338 | 0.027449 | 0.054018 | 0.010204 | 0.15708 | -0.054192 | 121.4664 | 121.3922 | 121.3925 | -0.040163 | 0.02852 | 0.22014 | -0.051772 | 121.1674 | 121.5069 | 121.0019 | -0.24657 | 0.078856 | 0.11782 | 0.12922 | 0.064827 | -0.014029 | 0.043656 | 0.043946 | -0.12755 | -0.18118 | 0.14754 | 0.067247 | 0.19479 | 0.15835 | -0.34667 | 121.5854 | 121.5112 | 121.5115 | 0.2761 | -121.3887 | 121.2864 | 121.6259 | 121.1209 | 0.33916 | -121.5951
760.9688 | 121.5454 | -0.13733 | 121.3348 | 1.4211e-13 | -0.014884 | 0.002421 | 0.068195 | -0.010356 | 0.058257 | 0.015566 | -0.0014485 | 0.00021361 | 0.060766 | 0.027235 | 0.054232 | 0.010204 | 0.15708 | -0.067927 | 121.4618 | 121.3968 | 121.4017 | -0.049321 | 0.042256 | 0.22472 | -0.051772 | 121.1674 | 121.5069 | 120.9332 | -0.25115 | 0.088008 | 0.12698 | 0.14753 | 0.069402 | -0.018606 | 0.061967 | 0.066836 | -0.11382 | -0.16745 | 0.17958 | 0.085557 | 0.19937 | 0.17208 | -0.40162 | 121.5991 | 121.5341 | 121.539 | 0.29441 | -121.3842 | 121.3047 | 121.6443 | 121.0706 | 0.36205 | -121.586
762.6562 | 121.5546 | -0.10986 | 121.3715 | 1.4211e-13 | -0.015098 | 0.0026346 | 0.068195 | -0.010143 | 0.058471 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.027876 | 0.054018 | -0.003531 | 0.16166 | -0.063349 | 121.4756 | 121.3968 | 121.4063 | -0.017268 | 0.033099 | 0.22929 | -0.051772 | 121.1765 | 121.5161 | 120.9607 | -0.25115 | 0.092595 | 0.10409 | 0.10633 | 0.046514 | -0.046081 | 0.025346 | 0.034794 | -0.14128 | -0.19491 | 0.14296 | 0.058091 | 0.19937 | 0.14462 | -0.41077 | 121.5854 | 121.5067 | 121.5161 | 0.27152 | -121.3887 | 121.2864 | 121.6259 | 121.0706 | 0.33916 | -121.6226
764.3438 | 121.4996 | -0.14648 | 121.3669 | 1.4211e-13 | -0.014671 | 0.0019936 | 0.068409 | -0.010356 | 0.058471 | 0.0079357 | -0.0018757 | 1.2e-08 | 0.060338 | 0.027449 | 0.054018 | 0.005626 | 0.16624 | -0.05877 | 121.4664 | 121.3922 | 121.4063 | -0.063057 | 0.02852 | 0.22929 | -0.056351 | 121.1628 | 121.5069 | 121.1667 | -0.2603 | 0.083427 | 0.099513 | 0.15211 | 0.087714 | 0.004287 | 0.025346 | 0.039372 | -0.11382 | -0.20407 | 0.175 | 0.090133 | 0.20395 | 0.14004 | -0.20015 | 121.6129 | 121.5387 | 121.5527 | 0.31272 | -121.4299 | 121.3093 | 121.6534 | 121.3132 | 0.37578 | -121.6272
766.0625 | 121.4264 | -0.16937 | 121.3898 | 1.4211e-13 | -0.014884 | 0.0022072 | 0.068195 | -0.009929 | 0.058257 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060552 | 0.027449 | 0.054018 | 0.014783 | 0.15708 | -0.063349 | 121.4664 | 121.3968 | 121.4063 | -0.026426 | 0.033099 | 0.23387 | -0.051772 | 121.1674 | 121.5023 | 120.9973 | -0.25115 | 0.14295 | 0.076624 | 0.18416 | 0.10602 | -0.036923 | 0.007035 | 0.016483 | -0.081773 | -0.22238 | 0.20247 | 0.1176 | 0.19937 | 0.11258 | -0.39245 | 121.6358 | 121.5662 | 121.5756 | 0.32645 | -121.4162 | 121.3368 | 121.6717 | 121.1667 | 0.40325 | -121.6409
767.7344 | 121.5637 | -0.1236 | 121.3623 | 1.4211e-13 | -0.015525 | 0.0022072 | 0.068409 | -0.010356 | 0.058257 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.027662 | 0.054232 | 0.005626 | 0.16166 | -0.054192 | 121.471 | 121.4014 | 121.4063 | -0.021847 | 0.023941 | 0.23387 | -0.056351 | 121.1765 | 121.5069 | 120.9332 | -0.24199 | 0.10175 | 0.10867 | 0.12922 | 0.069404 | -0.032345 | 0.03908 | 0.043949 | -0.11839 | -0.18576 | 0.14754 | 0.067245 | 0.18564 | 0.14462 | -0.42908 | 121.5946 | 121.525 | 121.5299 | 0.28525 | -121.3842 | 121.3001 | 121.6305 | 121.0568 | 0.35747 | -121.6043
769.5 | 121.5271 | -0.13275 | 121.3852 | 1.4211e-13 | -0.015098 | 0.0026346 | 0.068409 | -0.010143 | 0.058685 | 0.0079357 | -0.0018757 | 1.2e-08 | 0.060338 | 0.027662 | 0.054018 | 0.005626 | 0.16166 | -0.05877 | 121.4664 | 121.3968 | 121.4108 | -0.058478 | 0.02852 | 0.22929 | -0.051772 | 121.1811 | 121.5161 | 121.0797 | -0.25572 | 0.074273 | 0.081202 | 0.13838 | 0.073981 | -0.000292 | 0.011613 | 0.025639 | -0.12297 | -0.20407 | 0.16127 | 0.080979 | 0.20395 | 0.13089 | -0.30546 | 121.5991 | 121.5296 | 121.5436 | 0.29441 | -121.4437 | 121.3139 | 121.6488 | 121.2125 | 0.36205 | -121.6409
771.2031 | 121.55 | -0.13733 | 121.344 | 1.4211e-13 | -0.014671 | 0.0026346 | 0.068195 | -0.010356 | 0.058471 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060552 | 0.027662 | 0.053804 | 0.014783 | 0.16166 | -0.05877 | 121.471 | 121.3968 | 121.4108 | -0.044742 | 0.02852 | 0.23845 | -0.051772 | 121.1811 | 121.5115 | 121.1393 | -0.25115 | 0.092587 | 0.12698 | 0.15211 | 0.078559 | -0.014028 | 0.052812 | 0.066838 | -0.11382 | -0.16287 | 0.16585 | 0.085557 | 0.19937 | 0.16751 | -0.20473 | 121.6083 | 121.5341 | 121.5482 | 0.29899 | -121.3887 | 121.3185 | 121.6488 | 121.2766 | 0.37578 | -121.5951
772.9062 | 121.4676 | -0.14648 | 121.4081 | 1.4211e-13 | -0.015098 | 0.0019936 | 0.068195 | -0.010143 | 0.058257 | 0.00030522 | -0.0010211 | -0.00021359 | 0.060552 | 0.027449 | 0.054232 | 0.005626 | 0.16166 | -0.054192 | 121.471 | 121.4014 | 121.4154 | -0.049321 | 0.02852 | 0.23387 | -0.047194 | 121.172 | 121.5115 | 121.2308 | -0.25115 | 0.097163 | 0.062893 | 0.15211 | 0.092292 | -0.004871 | -0.006696 | 0.00733 | -0.10466 | -0.23611 | 0.175 | 0.09929 | 0.20395 | 0.10342 | -0.17725 | 121.6175 | 121.5479 | 121.5619 | 0.30814 | -121.4574 | 121.3185 | 121.658 | 121.3773 | 0.38036 | -121.6592
774.5938 | 121.3989 | -0.16022 | 121.3989 | 1.4211e-13 | -0.015312 | 0.0019936 | 0.068409 | -0.010143 | 0.058685 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060338 | 0.027876 | 0.053591 | 0.010204 | 0.16166 | -0.054192 | 121.4664 | 121.406 | 121.4154 | -0.058478 | 0.023941 | 0.22929 | -0.051772 | 121.1811 | 121.5069 | 121.1118 | -0.2603 | 0.10174 | 0.067469 | 0.17042 | 0.10603 | 0.004286 | 0.007038 | 0.016485 | -0.10009 | -0.2178 | 0.18416 | 0.10844 | 0.20853 | 0.108 | -0.28714 | 121.6266 | 121.5662 | 121.5756 | 0.32188 | -121.4574 | 121.3413 | 121.6671 | 121.272 | 0.38951 | -121.6592
776.2969 | 121.5088 | -0.14191 | 121.3715 | 1.4211e-13 | -0.015312 | 0.0022072 | 0.068195 | -0.010356 | 0.058471 | 0.00030522 | -0.0012349 | -0.00021359 | 0.060766 | 0.027662 | 0.054018 | 0.014783 | 0.16166 | -0.05877 | 121.471 | 121.4014 | 121.4063 | -0.044742 | 0.033099 | 0.23845 | -0.047194 | 121.172 | 121.5115 | 121.1942 | -0.25115 | 0.097165 | 0.099514 | 0.15669 | 0.083137 | -0.014028 | 0.029925 | 0.034794 | -0.10924 | -0.19949 | 0.17501 | 0.094713 | 0.20395 | 0.14004 | -0.17726 | 121.6129 | 121.5433 | 121.5482 | 0.30356 | -121.4162 | 121.3139 | 121.6534 | 121.3361 | 0.38036 | -121.6226
778 | 121.4722 | -0.14191 | 121.3989 | 1.4211e-13 | -0.015312 | 0.002421 | 0.068409 | -0.009929 | 0.058685 | 0.015566 | -0.0016621 | 1.2e-08 | 0.060552 | 0.027662 | 0.054232 | 0.019361 | 0.15708 | -0.054192 | 121.471 | 121.4105 | 121.4108 | -0.049321 | 0.02852 | 0.24303 | -0.051772 | 121.1765 | 121.5115 | 121.153 | -0.24657 | 0.092586 | 0.072048 | 0.16127 | 0.087715 | -0.004871 | 0.011617 | 0.011906 | -0.10466 | -0.22238 | 0.17043 | 0.090135 | 0.19479 | 0.11258 | -0.24593 | 121.6129 | 121.5525 | 121.5527 | 0.29899 | -121.4482 | 121.3185 | 121.6534 | 121.2949 | 0.38494 | -121.6455
779.6875 | 121.5042 | -0.14648 | 121.376 | 1.4211e-13 | -0.015098 | 0.0026346 | 0.068195 | -0.010356 | 0.058471 | -0.0073253 | -0.0014485 | 1.2e-08 | 0.060338 | 0.027662 | 0.053804 | 0.010204 | 0.15708 | -0.063349 | 121.4801 | 121.4014 | 121.4154 | -0.031005 | 0.02852 | 0.23387 | -0.042615 | 121.172 | 121.5115 | 121.2491 | -0.24199 | 0.11548 | 0.10409 | 0.15669 | 0.083135 | -0.032344 | 0.025347 | 0.039373 | -0.095505 | -0.20407 | 0.175 | 0.10387 | 0.19937 | 0.13547 | -0.12689 | 121.6266 | 121.5479 | 121.5619 | 0.30356 | -121.407 | 121.3185 | 121.658 | 121.3956 | 0.38036 | -121.618
781.3594 | 121.5134 | -0.15106 | 121.3989 | 1.4211e-13 | -0.015312 | 0.002421 | 0.068195 | -0.010143 | 0.058471 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.027662 | 0.053591 | -0.003531 | 0.16166 | -0.05877 | 121.471 | 121.406 | 121.4154 | -0.053899 | 0.023941 | 0.23387 | -0.056351 | 121.1811 | 121.5115 | 121.1072 | -0.25115 | 0.097163 | 0.072048 | 0.14753 | 0.092292 | -0.004871 | 0.007038 | 0.016485 | -0.10008 | -0.2178 | 0.175 | 0.094711 | 0.19479 | 0.11258 | -0.29172 | 121.622 | 121.557 | 121.5665 | 0.31272 | -121.4528 | 121.3322 | 121.6626 | 121.2583 | 0.38494 | -121.6501
783.0312 | 121.5225 | -0.14648 | 121.3715 | 1.4211e-13 | -0.015312 | 0.0019936 | 0.068195 | -0.010356 | 0.058685 | 0.015566 | -0.0018757 | 0.00042721 | 0.060338 | 0.027662 | 0.054018 | 0.019361 | 0.16166 | -0.054192 | 121.4756 | 121.4105 | 121.4246 | -0.053899 | 0.023941 | 0.24303 | -0.047194 | 121.1903 | 121.5161 | 121.1072 | -0.25115 | 0.092585 | 0.10409 | 0.16584 | 0.092292 | -0.000293 | 0.039083 | 0.053108 | -0.10466 | -0.18118 | 0.17042 | 0.09929 | 0.20395 | 0.14462 | -0.26425 | 121.622 | 121.557 | 121.5711 | 0.30814 | -121.4254 | 121.3368 | 121.6626 | 121.2537 | 0.38952 | -121.6226
784.7188 | 121.5637 | -0.12817 | 121.3669 | 1.4211e-13 | -0.015312 | 0.002421 | 0.068195 | -0.010356 | 0.058257 | 0.0079357 | -0.0018757 | 0.00021361 | 0.060338 | 0.027662 | 0.054018 | 0.010204 | 0.16624 | -0.054192 | 121.4801 | 121.4151 | 121.42 | -0.044742 | 0.037677 | 0.25219 | -0.047194 | 121.1903 | 121.5161 | 121.2079 | -0.25115 | 0.083432 | 0.11325 | 0.13838 | 0.073982 | -0.00945 | 0.04824 | 0.053107 | -0.12297 | -0.1766 | 0.16585 | 0.08098 | 0.20395 | 0.1492 | -0.15894 | 121.6083 | 121.5433 | 121.5482 | 0.29441 | -121.4116 | 121.3185 | 121.6443 | 121.3361 | 0.38036 | -121.618
786.4688 | 121.5271 | -0.13275 | 121.3715 | 1.4211e-13 | -0.015525 | 0.0028484 | 0.068195 | -0.010143 | 0.058257 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060766 | 0.027662 | 0.054018 | 0.005626 | 0.16624 | -0.05877 | 121.4756 | 121.406 | 121.4246 | -0.021847 | 0.02852 | 0.24303 | -0.047194 | 121.1949 | 121.5207 | 121.1988 | -0.25115 | 0.1109 | 0.10409 | 0.13838 | 0.073981 | -0.036923 | 0.034504 | 0.053108 | -0.11839 | -0.1766 | 0.16127 | 0.085557 | 0.20395 | 0.1492 | -0.17268 | 121.6083 | 121.5387 | 121.5573 | 0.29899 | -121.3933 | 121.3276 | 121.6534 | 121.3315 | 0.37578 | -121.6226
788.1406 | 121.5179 | -0.13733 | 121.3852 | 1.4211e-13 | -0.015739 | 0.002421 | 0.068409 | -0.010356 | 0.058257 | -0.0073253 | -0.0014485 | 0.00042721 | 0.060766 | 0.027449 | 0.054018 | 0.010204 | 0.16624 | -0.054192 | 121.4801 | 121.4197 | 121.4246 | -0.012689 | 0.037677 | 0.24761 | -0.051772 | 121.1857 | 121.5207 | 121.2904 | -0.25115 | 0.12464 | 0.094938 | 0.14753 | 0.083137 | -0.041503 | 0.034508 | 0.039375 | -0.11382 | -0.19949 | 0.17501 | 0.085557 | 0.19937 | 0.13547 | -0.09484 | 121.6175 | 121.557 | 121.5619 | 0.30356 | -121.3979 | 121.323 | 121.658 | 121.4277 | 0.38494 | -121.6363
789.8125 | 121.463 | -0.16937 | 121.4172 | 1.4211e-13 | -0.015953 | 0.002421 | 0.067981 | -0.009929 | 0.058257 | 0.00030522 | -0.0014485 | 0.00042721 | 0.060766 | 0.027235 | 0.054018 | 0.001048 | 0.15708 | -0.05877 | 121.4847 | 121.4243 | 121.4246 | -0.035584 | 0.033099 | 0.24761 | -0.051772 | 121.1857 | 121.5207 | 121.1667 | -0.25115 | 0.13379 | 0.067473 | 0.17042 | 0.1106 | -0.023186 | 0.007044 | 0.007332 | -0.081773 | -0.23153 | 0.20247 | 0.1176 | 0.19937 | 0.10342 | -0.25051 | 121.6541 | 121.5937 | 121.5939 | 0.32645 | -121.4528 | 121.3551 | 121.69 | 121.3361 | 0.41698 | -121.6684
791.5312 | 121.4767 | -0.15106 | 121.3943 | 1.4211e-13 | -0.015312 | 0.002421 | 0.068409 | -0.010356 | 0.058471 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060552 | 0.027662 | 0.054232 | 0.010204 | 0.16166 | -0.05877 | 121.4801 | 121.4197 | 121.4246 | -0.049321 | 0.037677 | 0.25219 | -0.047194 | 121.1949 | 121.5252 | 121.2583 | -0.24657 | 0.10174 | 0.085783 | 0.16127 | 0.092292 | -0.009449 | 0.025353 | 0.03022 | -0.095505 | -0.19948 | 0.18874 | 0.10387 | 0.19937 | 0.13089 | -0.13604 | 121.6312 | 121.5708 | 121.5756 | 0.31272 | -121.4437 | 121.3459 | 121.6763 | 121.4094 | 0.40325 | -121.6409
793.2031 | 121.4539 | -0.17853 | 121.3943 | 1.4211e-13 | -0.015739 | 0.0026346 | 0.068195 | -0.010356 | 0.058685 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060552 | 0.027876 | 0.054232 | 0.014783 | 0.16624 | -0.045036 | 121.4756 | 121.4197 | 121.4337 | -0.044742 | 0.033099 | 0.24761 | -0.047194 | 121.1994 | 121.5207 | 121.1667 | -0.25115 | 0.13379 | 0.081204 | 0.19331 | 0.13349 | -0.000294 | 0.025353 | 0.039377 | -0.072618 | -0.19491 | 0.21163 | 0.13133 | 0.20395 | 0.12631 | -0.22762 | 121.6541 | 121.5982 | 121.6123 | 0.34476 | -121.4391 | 121.378 | 121.6992 | 121.3453 | 0.42614 | -121.6455
794.9062 | 121.5088 | -0.11444 | 121.3577 | 1.4211e-13 | -0.015739 | 0.002421 | 0.067981 | -0.010143 | 0.058471 | 0.0079357 | -0.0016621 | 0.00042721 | 0.060338 | 0.027662 | 0.053804 | 0.005626 | 0.16166 | -0.049614 | 121.4893 | 121.4105 | 121.4291 | -0.021847 | 0.02852 | 0.25219 | -0.051772 | 121.1949 | 121.5161 | 121.1988 | -0.24657 | 0.092594 | 0.13156 | 0.12007 | 0.064827 | -0.027767 | 0.052816 | 0.07142 | -0.13213 | -0.16286 | 0.14296 | 0.062669 | 0.19479 | 0.15836 | -0.15895 | 121.6037 | 121.525 | 121.5436 | 0.2761 | -121.3796 | 121.3093 | 121.6305 | 121.3132 | 0.36663 | -121.6043
796.5781 | 121.4813 | -0.13733 | 121.3898 | 1.4211e-13 | -0.015525 | 0.002421 | 0.068409 | -0.010356 | 0.058257 | 0.015566 | -0.0012349 | 1.2e-08 | 0.060338 | 0.02809 | 0.054018 | 0.014783 | 0.16166 | -0.049614 | 121.4847 | 121.4197 | 121.4337 | -0.026426 | 0.02852 | 0.25219 | -0.051772 | 121.1903 | 121.5207 | 121.2034 | -0.25115 | 0.1109 | 0.094938 | 0.15211 | 0.087715 | -0.023188 | 0.02993 | 0.043954 | -0.11382 | -0.19949 | 0.16585 | 0.085557 | 0.19937 | 0.13089 | -0.18641 | 121.622 | 121.557 | 121.5711 | 0.29899 | -121.4162 | 121.3276 | 121.658 | 121.3407 | 0.38952 | -121.6409
798.2812 | 121.5637 | -0.10986 | 121.3806 | 1.4211e-13 | -0.015525 | 0.002421 | 0.068195 | -0.010356 | 0.058471 | 0.023196 | -0.0012349 | 0.00021361 | 0.060125 | 0.027662 | 0.054232 | 0.005626 | 0.16624 | -0.054192 | 121.4939 | 121.4243 | 121.4337 | -0.063057 | 0.02852 | 0.25219 | -0.051772 | 121.1903 | 121.5252 | 121.2171 | -0.24199 | 0.046806 | 0.11325 | 0.11549 | 0.055671 | 0.008865 | 0.043665 | 0.05311 | -0.13213 | -0.19033 | 0.13838 | 0.058091 | 0.19022 | 0.14462 | -0.16352 | 121.6037 | 121.5341 | 121.5436 | 0.2761 | -121.4437 | 121.3001 | 121.6351 | 121.327 | 0.36205 | -121.6226
799.9531 | 121.5729 | -0.1236 | 121.3715 | 1.4211e-13 | -0.015953 | 0.002421 | 0.068195 | -0.010356 | 0.058471 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.027876 | 0.054232 | 0.010204 | 0.17081 | -0.054192 | 121.4893 | 121.4289 | 121.4337 | -0.021847 | 0.02852 | 0.26134 | -0.042615 | 121.1903 | 121.5252 | 121.153 | -0.23741 | 0.10175 | 0.11783 | 0.1338 | 0.069404 | -0.032345 | 0.057399 | 0.062265 | -0.11381 | -0.18118 | 0.15212 | 0.080981 | 0.19479 | 0.15378 | -0.21846 | 121.6129 | 121.5525 | 121.5573 | 0.29441 | -121.3933 | 121.3139 | 121.6488 | 121.2766 | 0.38494 | -121.6089
801.625 | 121.463 | -0.17395 | 121.4172 | 1.4211e-13 | -0.015739 | 0.002421 | 0.068622 | -0.010356 | 0.058685 | -0.0073253 | -0.0012349 | 0.00021361 | 0.060338 | 0.02809 | 0.054232 | 0.014783 | 0.16624 | -0.049614 | 121.4939 | 121.4243 | 121.4383 | -0.049321 | 0.023941 | 0.26592 | -0.042615 | 121.1903 | 121.5252 | 121.272 | -0.24657 | 0.12463 | 0.07663 | 0.18873 | 0.12434 | -0.000293 | 0.007044 | 0.021068 | -0.072617 | -0.22695 | 0.19789 | 0.13133 | 0.20395 | 0.108 | -0.1452 | 121.6678 | 121.5982 | 121.6123 | 0.34019 | -121.4666 | 121.3642 | 121.6992 | 121.446 | 0.43987 | -121.6638
803.2969 | 121.4401 | -0.16479 | 121.4035 | 1.4211e-13 | -0.015739 | 0.0026346 | 0.068409 | -0.010784 | 0.058471 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.02809 | 0.054232 | 0.001048 | 0.16624 | -0.054192 | 121.4939 | 121.4243 | 121.4383 | -0.058478 | 0.033099 | 0.26592 | -0.042615 | 121.1949 | 121.5344 | 121.2629 | -0.24199 | 0.10632 | 0.090363 | 0.16584 | 0.1106 | 0.004286 | 0.020777 | 0.034801 | -0.077194 | -0.20864 | 0.19789 | 0.12218 | 0.19937 | 0.13089 | -0.14062 | 121.6587 | 121.5891 | 121.6031 | 0.33103 | -121.462 | 121.3597 | 121.6992 | 121.4277 | 0.43072 | -121.6455
804.9844 | 121.5683 | -0.12817 | 121.3623 | 1.4211e-13 | -0.015739 | 0.0019936 | 0.068409 | -0.010143 | 0.058257 | 0.015566 | -0.0012349 | 0.00021361 | 0.060552 | 0.027876 | 0.054445 | 0.010204 | 0.16624 | -0.05877 | 121.4984 | 121.4289 | 121.4337 | -0.040163 | 0.02852 | 0.2705 | -0.038036 | 121.1994 | 121.5298 | 121.2079 | -0.25115 | 0.088011 | 0.13614 | 0.13838 | 0.069404 | -0.018607 | 0.066554 | 0.07142 | -0.12297 | -0.16286 | 0.15669 | 0.090138 | 0.21311 | 0.16751 | -0.15437 | 121.6266 | 121.557 | 121.5619 | 0.29441 | -121.4025 | 121.3276 | 121.658 | 121.3361 | 0.39868 | -121.6135
806.6562 | 121.431 | -0.14648 | 121.4172 | 1.4211e-13 | -0.015739 | 0.0022072 | 0.068409 | -0.010143 | 0.058471 | 0.015566 | -0.0016621 | 0.00021361 | 0.060552 | 0.028303 | 0.054018 | 0.010204 | 0.16624 | -0.05877 | 121.4939 | 121.4289 | 121.4337 | -0.040163 | 0.02852 | 0.27508 | -0.047194 | 121.1949 | 121.5298 | 121.2858 | -0.25115 | 0.10632 | 0.07663 | 0.15669 | 0.087714 | -0.018607 | 0.011623 | 0.016489 | -0.10466 | -0.22237 | 0.175 | 0.09929 | 0.20395 | 0.11258 | -0.13146 | 121.6403 | 121.5753 | 121.5802 | 0.31272 | -121.4574 | 121.3413 | 121.6763 | 121.4323 | 0.42157 | -121.6684
808.3438 | 121.5546 | -0.10986 | 121.3806 | 1.4211e-13 | -0.015953 | 0.002421 | 0.067981 | -0.010356 | 0.058685 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060766 | 0.027876 | 0.054018 | 0.010204 | 0.16624 | -0.054192 | 121.4984 | 121.4243 | 121.4383 | -0.00811 | 0.02852 | 0.27966 | -0.042615 | 121.1994 | 121.5298 | 121.1667 | -0.25115 | 0.10175 | 0.11783 | 0.12007 | 0.055671 | -0.046082 | 0.043665 | 0.057689 | -0.14128 | -0.18117 | 0.13838 | 0.067248 | 0.20853 | 0.1492 | -0.21389 | 121.6083 | 121.5341 | 121.5482 | 0.2761 | -121.3887 | 121.3093 | 121.6397 | 121.2766 | 0.38952 | -121.6318
810.0312 | 121.5134 | -0.14648 | 121.3806 | 1.4211e-13 | -0.015312 | 0.0028484 | 0.067981 | -0.01057 | 0.058257 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.02809 | 0.054018 | 0.010204 | 0.16624 | -0.045036 | 121.4939 | 121.4289 | 121.4383 | -0.021847 | 0.033099 | 0.27508 | -0.047194 | 121.1903 | 121.5252 | 121.1393 | -0.24199 | 0.12464 | 0.11325 | 0.15669 | 0.10145 | -0.023189 | 0.048244 | 0.057689 | -0.095505 | -0.19033 | 0.17958 | 0.09929 | 0.19479 | 0.14462 | -0.24136 | 121.6403 | 121.5753 | 121.5848 | 0.31272 | -121.4025 | 121.3368 | 121.6717 | 121.2857 | 0.42157 | -121.6226
811.7188 | 121.4447 | -0.17853 | 121.4401 | 1.4211e-13 | -0.015953 | 0.0022072 | 0.068409 | -0.010356 | 0.058685 | 0.0079357 | -0.0016621 | 0.00042721 | 0.060552 | 0.027662 | 0.054018 | 0.019361 | 0.16166 | -0.054192 | 121.503 | 121.4334 | 121.4337 | -0.00811 | 0.037677 | 0.28424 | -0.051772 | 121.1994 | 121.5252 | 121.1759 | -0.24199 | 0.17042 | 0.062897 | 0.19789 | 0.12434 | -0.046082 | -0.006687 | -0.0064 | -0.063461 | -0.24068 | 0.2162 | 0.12676 | 0.19022 | 0.085114 | -0.26424 | 121.6816 | 121.612 | 121.6123 | 0.34019 | -121.4482 | 121.378 | 121.7038 | 121.3544 | 0.46277 | -121.6821
813.4688 | 121.4401 | -0.16022 | 121.4218 | 1.4211e-13 | -0.015739 | 0.0026346 | 0.068409 | -0.010784 | 0.058685 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060338 | 0.02809 | 0.054018 | 0.014783 | 0.16624 | -0.054192 | 121.4984 | 121.4243 | 121.4383 | -0.072215 | 0.037677 | 0.28882 | -0.047194 | 121.1994 | 121.5298 | 121.1667 | -0.24657 | 0.088002 | 0.07663 | 0.175 | 0.10603 | 0.018023 | 0.002466 | 0.01649 | -0.08635 | -0.22237 | 0.19789 | 0.11302 | 0.19937 | 0.108 | -0.25508 | 121.6587 | 121.5845 | 121.5985 | 0.32645 | -121.494 | 121.3597 | 121.69 | 121.3269 | 0.44904 | -121.6684
815.2188 | 121.5729 | -0.11902 | 121.3898 | 1.4211e-13 | -0.015312 | 0.0022072 | 0.068409 | -0.01057 | 0.058685 | 0.00030522 | -0.0014485 | -0.00021359 | 0.060338 | 0.027876 | 0.053804 | 0.001048 | 0.17081 | -0.054192 | 121.503 | 121.4334 | 121.4429 | -0.026426 | 0.033099 | 0.28424 | -0.047194 | 121.1994 | 121.5298 | 121.2217 | -0.24657 | 0.092593 | 0.11325 | 0.12007 | 0.064827 | -0.027766 | 0.043667 | 0.053111 | -0.12755 | -0.19033 | 0.15212 | 0.071825 | 0.19937 | 0.14005 | -0.1681 | 121.622 | 121.5525 | 121.5619 | 0.28983 | -121.4162 | 121.3185 | 121.6488 | 121.3407 | 0.40326 | -121.6363
816.9219 | 121.5042 | -0.14191 | 121.4081 | 1.4211e-13 | -0.015739 | 0.0026346 | 0.068409 | -0.010356 | 0.058471 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060979 | 0.02809 | 0.054018 | 0.014783 | 0.16624 | -0.049614 | 121.4984 | 121.438 | 121.4475 | -0.031005 | 0.037677 | 0.28882 | -0.038036 | 121.2086 | 121.5298 | 121.1438 | -0.24199 | 0.1109 | 0.090363 | 0.15669 | 0.092293 | -0.018609 | 0.029936 | 0.03938 | -0.10008 | -0.19948 | 0.17958 | 0.10387 | 0.20395 | 0.12174 | -0.26424 | 121.6404 | 121.5799 | 121.5894 | 0.30814 | -121.4391 | 121.3505 | 121.6717 | 121.2857 | 0.43073 | -121.6501
818.6719 | 121.5179 | -0.14191 | 121.3715 | 1.4211e-13 | -0.015525 | 0.0026346 | 0.068622 | -0.010356 | 0.058471 | 0.015566 | -0.0014485 | 1.2e-08 | 0.060338 | 0.02809 | 0.054018 | 0.014783 | 0.16166 | -0.045036 | 121.4939 | 121.4289 | 121.4475 | -0.031005 | 0.037677 | 0.2934 | -0.047194 | 121.2086 | 121.5344 | 121.1484 | -0.24657 | 0.1109 | 0.12241 | 0.15669 | 0.096871 | -0.014031 | 0.057399 | 0.076001 | -0.10466 | -0.16286 | 0.17958 | 0.094713 | 0.19937 | 0.16294 | -0.22304 | 121.6358 | 121.5708 | 121.5894 | 0.30356 | -121.4025 | 121.3505 | 121.6763 | 121.2903 | 0.4353 | -121.618
820.3594 | 121.4813 | -0.15106 | 121.4264 | 1.4211e-13 | -0.015739 | 0.0022072 | 0.068409 | -0.010784 | 0.058471 | 0.015566 | -0.0012349 | 1.2e-08 | 0.060338 | 0.028303 | 0.054232 | 0.014783 | 0.17081 | -0.05877 | 121.4984 | 121.4334 | 121.4429 | -0.012689 | 0.037677 | 0.28882 | -0.042615 | 121.1994 | 121.5344 | 121.2308 | -0.24657 | 0.13837 | 0.072052 | 0.16584 | 0.092292 | -0.046081 | 0.007046 | 0.01649 | -0.095505 | -0.22695 | 0.18874 | 0.10845 | 0.20395 | 0.108 | -0.19556 | 121.6495 | 121.5845 | 121.5939 | 0.32188 | -121.4391 | 121.3505 | 121.6855 | 121.3819 | 0.43988 | -121.673
822.1094 | 121.5591 | -0.14191 | 121.4127 | 1.4211e-13 | -0.015739 | 0.0019936 | 0.068195 | -0.010143 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.02809 | 0.054018 | 0.014783 | 0.17539 | -0.05877 | 121.503 | 121.4334 | 121.4475 | -0.003531 | 0.02852 | 0.2934 | -0.047194 | 121.2086 | 121.5298 | 121.1209 | -0.24657 | 0.13838 | 0.090363 | 0.15669 | 0.083137 | -0.055239 | 0.020779 | 0.034802 | -0.10466 | -0.20406 | 0.17043 | 0.094713 | 0.19937 | 0.11716 | -0.29172 | 121.6449 | 121.5753 | 121.5894 | 0.3173 | -121.4162 | 121.3505 | 121.6717 | 121.2629 | 0.4353 | -121.6592
823.7812 | 121.5179 | -0.11444 | 121.4035 | 1.4211e-13 | -0.015739 | 0.002421 | 0.068622 | -0.01057 | 0.058257 | -0.0073253 | -0.0014485 | 0.00021361 | 0.060338 | 0.02809 | 0.054018 | 0.010204 | 0.16166 | -0.049614 | 121.4939 | 121.4334 | 121.452 | -0.044742 | 0.033099 | 0.30713 | -0.042615 | 121.2178 | 121.5344 | 121.2171 | -0.24199 | 0.069699 | 0.090363 | 0.12465 | 0.064827 | -0.004872 | 0.029935 | 0.048537 | -0.12755 | -0.18575 | 0.14754 | 0.071826 | 0.19937 | 0.13089 | -0.18641 | 121.6083 | 121.5479 | 121.5665 | 0.2761 | -121.4482 | 121.3322 | 121.6488 | 121.3315 | 0.42157 | -121.6455
825.5312 | 121.5225 | -0.13733 | 121.3806 | 1.4211e-13 | -0.015739 | 0.0026346 | 0.068195 | -0.010143 | 0.058685 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060338 | 0.02809 | 0.054018 | 0.010204 | 0.16624 | -0.054192 | 121.4984 | 121.4426 | 121.452 | -0.012689 | 0.037677 | 0.30255 | -0.042615 | 121.2086 | 121.5298 | 121.1118 | -0.24199 | 0.12464 | 0.11783 | 0.14753 | 0.083137 | -0.041503 | 0.061981 | 0.071425 | -0.10466 | -0.17202 | 0.17501 | 0.094714 | 0.19937 | 0.1492 | -0.26883 | 121.6358 | 121.5799 | 121.5894 | 0.30356 | -121.3933 | 121.3459 | 121.6671 | 121.2491 | 0.43988 | -121.6226
827.2188 | 121.582 | -0.11902 | 121.3898 | 1.4211e-13 | -0.015739 | 0.0022072 | 0.068409 | -0.010356 | 0.058471 | 0.015566 | -0.0012349 | -0.00021359 | 0.060552 | 0.027662 | 0.053804 | 0.014783 | 0.16166 | -0.05877 | 121.503 | 121.4426 | 121.4429 | -0.021847 | 0.023941 | 0.30713 | -0.047194 | 121.2086 | 121.5298 | 121.2675 | -0.25115 | 0.097172 | 0.11325 | 0.1338 | 0.060249 | -0.036923 | 0.052825 | 0.053111 | -0.13213 | -0.18117 | 0.14296 | 0.071825 | 0.20395 | 0.14005 | -0.12231 | 121.622 | 121.5616 | 121.5619 | 0.28068 | -121.4116 | 121.3276 | 121.6488 | 121.3865 | 0.42615 | -121.6409
828.8906 | 121.5179 | -0.12817 | 121.4172 | 1.4211e-13 | -0.015953 | 0.0026346 | 0.068195 | -0.01057 | 0.058257 | 0.00030522 | -0.0014485 | 0.00042721 | 0.060766 | 0.028303 | 0.054018 | 0.014783 | 0.16166 | -0.054192 | 121.503 | 121.4426 | 121.4566 | -0.00811 | 0.033099 | 0.31171 | -0.042615 | 121.204 | 121.5344 | 121.185 | -0.24657 | 0.12006 | 0.085786 | 0.14296 | 0.073982 | -0.046082 | 0.02536 | 0.039382 | -0.11839 | -0.21322 | 0.16127 | 0.085559 | 0.20395 | 0.11716 | -0.23219 | 121.6312 | 121.5708 | 121.5848 | 0.28983 | -121.4253 | 121.3322 | 121.6626 | 121.3132 | 0.43989 | -121.6638
830.625 | 121.5317 | -0.13275 | 121.4081 | 1.4211e-13 | -0.015953 | 0.002421 | 0.068409 | -0.01057 | 0.058257 | 0.00030522 | -0.0012349 | 0.00064101 | 0.060338 | 0.02809 | 0.053591 | 0.010204 | 0.16166 | -0.054192 | 121.5076 | 121.4426 | 121.4475 | -0.031005 | 0.033099 | 0.31171 | -0.038036 | 121.2086 | 121.539 | 121.2629 | -0.25115 | 0.10175 | 0.09952 | 0.14295 | 0.078559 | -0.023187 | 0.034515 | 0.03938 | -0.11839 | -0.19948 | 0.16585 | 0.094715 | 0.21311 | 0.13089 | -0.1452 | 121.6404 | 121.5753 | 121.5802 | 0.29441 | -121.4391 | 121.3413 | 121.6717 | 121.3956 | 0.44446 | -121.6592
832.2969 | 121.4401 | -0.15106 | 121.431 | 1.4211e-13 | -0.015953 | 0.0022072 | 0.068409 | -0.010356 | 0.058257 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060338 | 0.028303 | 0.053804 | 0.014783 | 0.16166 | -0.05877 | 121.5168 | 121.4426 | 121.452 | -0.044742 | 0.02852 | 0.32545 | -0.047194 | 121.2178 | 121.5436 | 121.272 | -0.24199 | 0.10632 | 0.085789 | 0.16584 | 0.092292 | -0.014028 | 0.011627 | 0.021071 | -0.090927 | -0.21321 | 0.17958 | 0.10387 | 0.19479 | 0.11258 | -0.15893 | 121.6678 | 121.5937 | 121.6031 | 0.31272 | -121.4757 | 121.3688 | 121.6946 | 121.4231 | 0.47651 | -121.673
834.0312 | 121.4676 | -0.16022 | 121.4035 | 1.4211e-13 | -0.015525 | 0.0026346 | 0.068622 | -0.01057 | 0.058471 | 0.0079357 | -0.0012349 | -0.00021359 | 0.060552 | 0.02809 | 0.053804 | 0.010204 | 0.16166 | -0.049614 | 121.4984 | 121.4472 | 121.4612 | -0.021847 | 0.033099 | 0.31171 | -0.047194 | 121.2132 | 121.539 | 121.2125 | -0.24657 | 0.13837 | 0.094941 | 0.17042 | 0.1106 | -0.027767 | 0.043672 | 0.057694 | -0.08635 | -0.19033 | 0.19332 | 0.11302 | 0.19937 | 0.13547 | -0.19099 | 121.6587 | 121.6074 | 121.6214 | 0.32188 | -121.4253 | 121.3734 | 121.6992 | 121.3727 | 0.47193 | -121.6501
835.7031 | 121.5408 | -0.11902 | 121.4127 | 1.4211e-13 | -0.015953 | 0.0022072 | 0.068409 | -0.010356 | 0.058471 | -0.0073253 | -0.0014485 | -0.00021359 | 0.060338 | 0.02809 | 0.053804 | 0.014783 | 0.16166 | -0.054192 | 121.5168 | 121.4426 | 121.4612 | -0.003531 | 0.037677 | 0.32087 | -0.042615 | 121.2132 | 121.539 | 121.3087 | -0.25115 | 0.11549 | 0.1041 | 0.1338 | 0.064827 | -0.050661 | 0.029937 | 0.048538 | -0.13213 | -0.19948 | 0.1567 | 0.076404 | 0.20853 | 0.12632 | -0.10399 | 121.6358 | 121.5616 | 121.5802 | 0.28068 | -121.4162 | 121.3322 | 121.658 | 121.4277 | 0.43989 | -121.6638
837.4375 | 121.5225 | -0.1236 | 121.3989 | 1.4211e-13 | -0.015525 | 0.0019936 | 0.068195 | -0.010143 | 0.058257 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060338 | 0.02809 | 0.054018 | 0.014783 | 0.16624 | -0.054192 | 121.5076 | 121.4426 | 121.452 | -0.044742 | 0.02852 | 0.32545 | -0.042615 | 121.2178 | 121.5436 | 121.0797 | -0.23741 | 0.078854 | 0.10867 | 0.13838 | 0.069404 | -0.00945 | 0.04367 | 0.053114 | -0.11381 | -0.18117 | 0.15212 | 0.080981 | 0.19479 | 0.14463 | -0.31919 | 121.6312 | 121.5662 | 121.5756 | 0.28983 | -121.4437 | 121.3414 | 121.6671 | 121.2033 | 0.44904 | -121.6363
839.1094 | 121.4996 | -0.16479 | 121.4081 | 1.4211e-13 | -0.01638 | 0.002421 | 0.068409 | -0.010356 | 0.058257 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060552 | 0.028303 | 0.054232 | 0.014783 | 0.16166 | -0.054192 | 121.5122 | 121.4518 | 121.4612 | -0.012689 | 0.033099 | 0.33003 | -0.047194 | 121.2178 | 121.5481 | 121.2812 | -0.24657 | 0.15211 | 0.1041 | 0.17958 | 0.1106 | -0.041503 | 0.043673 | 0.053116 | -0.081772 | -0.19033 | 0.19789 | 0.1176 | 0.19937 | 0.14005 | -0.12689 | 121.677 | 121.6165 | 121.626 | 0.32645 | -121.4208 | 121.3825 | 121.7129 | 121.446 | 0.49482 | -121.6546
840.8438 | 121.4905 | -0.16022 | 121.4081 | 1.4211e-13 | -0.015739 | 0.0019936 | 0.068409 | -0.010784 | 0.058257 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060552 | 0.027876 | 0.054018 | 0.014783 | 0.16624 | -0.05877 | 121.5076 | 121.4472 | 121.4658 | -0.040163 | 0.02852 | 0.32545 | -0.042615 | 121.2223 | 121.5573 | 121.1393 | -0.23741 | 0.12005 | 0.09952 | 0.175 | 0.10145 | -0.018607 | 0.039094 | 0.057694 | -0.077193 | -0.18575 | 0.18874 | 0.1176 | 0.19479 | 0.14921 | -0.26882 | 121.6678 | 121.6074 | 121.626 | 0.32645 | -121.4482 | 121.3826 | 121.7175 | 121.2995 | 0.48566 | -121.6455
842.5938 | 121.4264 | -0.13275 | 121.4539 | 1.4211e-13 | -0.015739 | 0.0022072 | 0.067981 | -0.01057 | 0.058685 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060125 | 0.02809 | 0.054232 | 0.010204 | 0.15708 | -0.05877 | 121.5122 | 121.4472 | 121.4612 | -0.017268 | 0.02852 | 0.33003 | -0.047194 | 121.2178 | 121.5573 | 121.2446 | -0.24657 | 0.11548 | 0.058322 | 0.14295 | 0.073981 | -0.041502 | -0.006682 | 0.00734 | -0.11382 | -0.2361 | 0.16127 | 0.085557 | 0.19937 | 0.10343 | -0.20929 | 121.6449 | 121.5799 | 121.5939 | 0.28983 | -121.4711 | 121.3505 | 121.69 | 121.3773 | 0.46278 | -121.7004
844.2812 | 121.5683 | -0.10986 | 121.3898 | 1.4211e-13 | -0.016166 | 0.002421 | 0.068622 | -0.010143 | 0.058471 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.028303 | 0.053804 | 0.014783 | 0.17081 | -0.054192 | 121.5122 | 121.4518 | 121.4658 | -0.012689 | 0.02852 | 0.3346 | -0.051772 | 121.2223 | 121.5481 | 121.2537 | -0.24657 | 0.097174 | 0.12241 | 0.12465 | 0.055671 | -0.041503 | 0.061983 | 0.076004 | -0.1367 | -0.16744 | 0.13838 | 0.058091 | 0.19479 | 0.15836 | -0.13605 | 121.622 | 121.5616 | 121.5756 | 0.28068 | -121.4025 | 121.3322 | 121.658 | 121.3636 | 0.44447 | -121.6363
846.0312 | 121.5729 | -0.10529 | 121.3806 | 1.4211e-13 | -0.016166 | 0.0022072 | 0.068195 | -0.010143 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.028517 | 0.054232 | 0.010204 | 0.16166 | -0.054192 | 121.5122 | 121.4472 | 121.4612 | -0.044742 | 0.037677 | 0.33918 | -0.047194 | 121.2269 | 121.5481 | 121.2308 | -0.24657 | 0.060544 | 0.13156 | 0.11549 | 0.051094 | -0.00945 | 0.06656 | 0.080582 | -0.14128 | -0.1537 | 0.14296 | 0.058092 | 0.19937 | 0.16752 | -0.14978 | 121.6175 | 121.5525 | 121.5665 | 0.26694 | -121.4254 | 121.3322 | 121.6534 | 121.3361 | 0.44447 | -121.6272
847.7812 | 121.5729 | -0.10986 | 121.3715 | 1.4211e-13 | -0.015953 | 0.002421 | 0.068409 | -0.010356 | 0.058257 | 0.00030522 | -0.0010211 | -0.00021359 | 0.060338 | 0.028303 | 0.054018 | 0.014783 | 0.16624 | -0.049614 | 121.5076 | 121.4609 | 121.4612 | -0.021847 | 0.042256 | 0.33918 | -0.042615 | 121.2223 | 121.5573 | 121.3041 | -0.24199 | 0.088016 | 0.13614 | 0.12465 | 0.060249 | -0.027767 | 0.089451 | 0.089737 | -0.13213 | -0.14913 | 0.15212 | 0.067248 | 0.19937 | 0.18583 | -0.067371 | 121.6175 | 121.5708 | 121.5711 | 0.2761 | -121.3933 | 121.3322 | 121.6672 | 121.414 | 0.44905 | -121.6134
849.5312 | 121.5958 | -0.09613 | 121.4081 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068409 | -0.010356 | 0.058685 | 0.015566 | -0.0014485 | 0.00021361 | 0.060338 | 0.027876 | 0.053591 | 0.010204 | 0.16166 | -0.054192 | 121.5122 | 121.4563 | 121.4658 | -0.012689 | 0.033099 | 0.33918 | -0.042615 | 121.2269 | 121.5481 | 121.066 | -0.24199 | 0.083441 | 0.1041 | 0.10633 | 0.041938 | -0.041503 | 0.048251 | 0.057694 | -0.14586 | -0.18117 | 0.12923 | 0.053515 | 0.19937 | 0.14005 | -0.34208 | 121.6083 | 121.5525 | 121.5619 | 0.25779 | -121.4208 | 121.323 | 121.6443 | 121.1621 | 0.43531 | -121.6501
851.2188 | 121.4813 | -0.15564 | 121.4218 | 1.4211e-13 | -0.016166 | 0.002421 | 0.068622 | -0.010356 | 0.058685 | 0.015566 | -0.0010211 | 0.00021361 | 0.060338 | 0.028303 | 0.054018 | 0.019361 | 0.15708 | -0.045036 | 121.5213 | 121.4563 | 121.4704 | -0.035584 | 0.037677 | 0.33918 | -0.047194 | 121.2269 | 121.5481 | 121.1896 | -0.25115 | 0.12006 | 0.099522 | 0.175 | 0.1106 | -0.009452 | 0.034518 | 0.04854 | -0.095506 | -0.1949 | 0.19332 | 0.10845 | 0.20395 | 0.12632 | -0.23219 | 121.677 | 121.612 | 121.626 | 0.31272 | -121.4574 | 121.3826 | 121.7038 | 121.3453 | 0.49482 | -121.673
852.9062 | 121.5042 | -0.13275 | 121.4401 | 1.4211e-13 | -0.016166 | 0.002421 | 0.068409 | -0.010143 | 0.058471 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.028303 | 0.054018 | 0.010204 | 0.15708 | -0.049614 | 121.5168 | 121.4518 | 121.4612 | -0.003531 | 0.033099 | 0.34834 | -0.042615 | 121.2223 | 121.5573 | 121.3178 | -0.24657 | 0.12922 | 0.076633 | 0.14295 | 0.083137 | -0.046083 | 0.011629 | 0.021072 | -0.11382 | -0.21779 | 0.16585 | 0.090136 | 0.20395 | 0.11716 | -0.1223 | 121.6495 | 121.5845 | 121.5939 | 0.28983 | -121.4437 | 121.3551 | 121.69 | 121.4506 | 0.48109 | -121.6867
854.6562 | 121.6003 | -0.13275 | 121.3943 | 1.4211e-13 | -0.015739 | 0.002421 | 0.067981 | -0.010356 | 0.058471 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060338 | 0.028517 | 0.054018 | 0.014783 | 0.15708 | -0.054192 | 121.5213 | 121.4563 | 121.4749 | -0.00811 | 0.037677 | 0.36666 | -0.042615 | 121.2315 | 121.5573 | 121.1805 | -0.24199 | 0.12464 | 0.12699 | 0.14753 | 0.078559 | -0.046082 | 0.061984 | 0.080585 | -0.10924 | -0.16286 | 0.17043 | 0.090136 | 0.19937 | 0.16294 | -0.21388 | 121.6541 | 121.5891 | 121.6077 | 0.28983 | -121.4025 | 121.3642 | 121.69 | 121.3132 | 0.49941 | -121.6363
856.3281 | 121.5088 | -0.16022 | 121.4264 | 1.4211e-13 | -0.015953 | 0.002421 | 0.068195 | -0.01057 | 0.058257 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.028731 | 0.054018 | 0.010204 | 0.16624 | -0.05877 | 121.5122 | 121.4518 | 121.4749 | -0.031005 | 0.037677 | 0.3575 | -0.042615 | 121.2269 | 121.5527 | 121.1255 | -0.24199 | 0.12921 | 0.085787 | 0.17042 | 0.10145 | -0.027765 | 0.025362 | 0.048541 | -0.081772 | -0.19948 | 0.19789 | 0.1176 | 0.19937 | 0.12632 | -0.30087 | 121.6724 | 121.612 | 121.6351 | 0.32645 | -121.4574 | 121.3871 | 121.7129 | 121.2857 | 0.51771 | -121.6684
858.0625 | 121.4951 | -0.14648 | 121.4035 | 1.4211e-13 | -0.015525 | 0.002421 | 0.067981 | -0.01057 | 0.058257 | 0.015566 | -0.0014485 | 0.00021361 | 0.060125 | 0.028517 | 0.054018 | 0.014783 | 0.16624 | -0.05877 | 121.5213 | 121.4563 | 121.4749 | -0.017268 | 0.033099 | 0.37123 | -0.042615 | 121.2269 | 121.5619 | 121.2995 | -0.24657 | 0.12922 | 0.11783 | 0.16127 | 0.087714 | -0.041502 | 0.052829 | 0.07143 | -0.10008 | -0.17659 | 0.17958 | 0.10387 | 0.20395 | 0.15837 | -0.10399 | 121.6678 | 121.6028 | 121.6214 | 0.31272 | -121.4208 | 121.3734 | 121.7084 | 121.446 | 0.51772 | -121.6501
859.7344 | 121.5866 | -0.10986 | 121.3898 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068622 | -0.010356 | 0.058044 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060125 | 0.02809 | 0.054445 | 0.019361 | 0.16166 | -0.05877 | 121.5213 | 121.4609 | 121.4704 | -0.012689 | 0.033099 | 0.37581 | -0.047194 | 121.2223 | 121.5573 | 121.24 | -0.24199 | 0.097174 | 0.13157 | 0.12922 | 0.051093 | -0.046081 | 0.07114 | 0.080583 | -0.13213 | -0.16744 | 0.14296 | 0.062669 | 0.19479 | 0.16752 | -0.14978 | 121.6312 | 121.5708 | 121.5802 | 0.27152 | -121.4025 | 121.3322 | 121.6672 | 121.3499 | 0.48568 | -121.6318
861.5 | 121.5637 | -0.10986 | 121.431 | 1.4211e-13 | -0.01638 | 0.0019936 | 0.068622 | -0.01057 | 0.058257 | 0.0079357 | -0.0016621 | 1.2e-08 | 0.060552 | 0.028517 | 0.053804 | 0.014783 | 0.16166 | -0.054192 | 121.5213 | 121.4609 | 121.4749 | -0.012689 | 0.033099 | 0.39413 | -0.042615 | 121.2315 | 121.5527 | 121.2583 | -0.24199 | 0.097174 | 0.090367 | 0.12465 | 0.055671 | -0.041503 | 0.029942 | 0.043964 | -0.13213 | -0.19948 | 0.14296 | 0.067248 | 0.19937 | 0.12174 | -0.17267 | 121.6312 | 121.5708 | 121.5848 | 0.27152 | -121.4437 | 121.3414 | 121.6626 | 121.3682 | 0.50399 | -121.673
863.25 | 121.5637 | -0.11444 | 121.4127 | 1.4211e-13 | -0.015953 | 0.002421 | 0.068622 | -0.010143 | 0.058257 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060552 | 0.027876 | 0.054018 | 0.010204 | 0.16166 | -0.05877 | 121.5168 | 121.4518 | 121.4704 | -0.021847 | 0.046835 | 0.38955 | -0.047194 | 121.2269 | 121.5619 | 121.1942 | -0.25115 | 0.092594 | 0.1041 | 0.12465 | 0.055671 | -0.036923 | 0.039095 | 0.057695 | -0.1367 | -0.18575 | 0.16128 | 0.067247 | 0.20395 | 0.14921 | -0.21846 | 121.6312 | 121.5662 | 121.5848 | 0.2761 | -121.4345 | 121.3414 | 121.6763 | 121.3086 | 0.50399 | -121.6638
864.9219 | 121.5958 | -0.11902 | 121.4218 | 1.4211e-13 | -0.016166 | 0.0022072 | 0.068195 | -0.01057 | 0.058685 | 0.015566 | -0.0012349 | 0.00021361 | 0.060338 | 0.02809 | 0.053804 | 0.019361 | 0.16166 | -0.045036 | 121.5213 | 121.4655 | 121.4795 | -0.017268 | 0.046835 | 0.40329 | -0.047194 | 121.2315 | 121.5573 | 121.2491 | -0.24657 | 0.10175 | 0.099522 | 0.13838 | 0.073983 | -0.027768 | 0.043676 | 0.057697 | -0.12755 | -0.19032 | 0.16585 | 0.071825 | 0.19937 | 0.13547 | -0.17267 | 121.6404 | 121.5845 | 121.5985 | 0.28068 | -121.4391 | 121.3505 | 121.6763 | 121.3682 | 0.5223 | -121.6684
866.6719 | 121.4584 | -0.12817 | 121.431 | 1.4211e-13 | -0.015953 | 0.0019936 | 0.068409 | -0.01057 | 0.058257 | -0.0073253 | -0.0014485 | 0.00042721 | 0.060552 | 0.028303 | 0.054232 | 0.014783 | 0.16624 | -0.054192 | 121.5168 | 121.4655 | 121.4704 | -0.072215 | 0.02852 | 0.40786 | -0.038036 | 121.2361 | 121.5527 | 121.3499 | -0.24657 | 0.055959 | 0.085789 | 0.14296 | 0.073982 | 0.018023 | 0.034521 | 0.039385 | -0.11839 | -0.1949 | 0.15669 | 0.090138 | 0.20853 | 0.12174 | -0.081094 | 121.6449 | 121.5937 | 121.5985 | 0.29441 | -121.5032 | 121.3642 | 121.6809 | 121.478 | 0.53604 | -121.6775
868.3594 | 121.5454 | -0.13733 | 121.3898 | 1.4211e-13 | -0.016166 | 0.0022072 | 0.068409 | -0.01057 | 0.058685 | 0.0079357 | -0.0014485 | 0.00042721 | 0.060338 | 0.02809 | 0.054232 | 0.014783 | 0.16166 | -0.054192 | 121.5168 | 121.4609 | 121.4795 | 0.001048 | 0.033099 | 0.41702 | -0.047194 | 121.2269 | 121.5573 | 121.2446 | -0.24199 | 0.13838 | 0.12699 | 0.15211 | 0.083137 | -0.05524 | 0.07114 | 0.08974 | -0.10466 | -0.16286 | 0.17043 | 0.090135 | 0.19479 | 0.16752 | -0.1452 | 121.6541 | 121.5982 | 121.6168 | 0.29899 | -121.3887 | 121.3642 | 121.6946 | 121.3819 | 0.55435 | -121.6318
870.0938 | 121.5775 | -0.13733 | 121.4035 | 1.4211e-13 | -0.016166 | 0.002421 | 0.068409 | -0.01057 | 0.058257 | 0.0079357 | -0.0016621 | 0.00042721 | 0.059911 | 0.028731 | 0.053804 | 0.010204 | 0.16166 | -0.054192 | 121.5168 | 121.4701 | 121.4749 | -0.021847 | 0.037677 | 0.43076 | -0.047194 | 121.2315 | 121.5619 | 121.1622 | -0.24657 | 0.11548 | 0.11325 | 0.14753 | 0.083137 | -0.032345 | 0.066566 | 0.07143 | -0.10924 | -0.17201 | 0.17501 | 0.090135 | 0.19937 | 0.15837 | -0.24135 | 121.6541 | 121.6074 | 121.6123 | 0.29899 | -121.4253 | 121.3688 | 121.6992 | 121.2995 | 0.56809 | -121.6501
871.8438 | 121.5088 | -0.14191 | 121.4584 | 1.4211e-13 | -0.016166 | 0.0019936 | 0.068622 | -0.010356 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060766 | 0.02809 | 0.054232 | 0.010204 | 0.15708 | -0.054192 | 121.5213 | 121.4746 | 121.4887 | 0.001048 | 0.042256 | 0.43534 | -0.038036 | 121.2269 | 121.5573 | 121.2949 | -0.25115 | 0.14295 | 0.062901 | 0.15211 | 0.087715 | -0.05524 | 0.016213 | 0.030234 | -0.10924 | -0.23152 | 0.18416 | 0.10387 | 0.21311 | 0.098854 | -0.1635 | 121.6632 | 121.6166 | 121.6306 | 0.29899 | -121.4574 | 121.3688 | 121.6992 | 121.4368 | 0.57724 | -121.7096
873.5938 | 121.463 | -0.17853 | 121.4218 | 1.4211e-13 | -0.01638 | 0.0019936 | 0.068409 | -0.01057 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.028731 | 0.053804 | 0.010204 | 0.15708 | -0.05877 | 121.5305 | 121.4746 | 121.4841 | -0.035584 | 0.046835 | 0.43534 | -0.042615 | 121.2315 | 121.5573 | 121.2904 | -0.24199 | 0.14294 | 0.10868 | 0.18873 | 0.11976 | -0.023186 | 0.052834 | 0.062276 | -0.063461 | -0.19032 | 0.22536 | 0.13591 | 0.19937 | 0.13547 | -0.13146 | 121.709 | 121.6532 | 121.6626 | 0.33561 | -121.4574 | 121.41 | 121.7358 | 121.4689 | 0.61386 | -121.6638
875.3281 | 121.463 | -0.15106 | 121.4447 | 1.4211e-13 | -0.016166 | 0.0019936 | 0.068836 | -0.010356 | 0.058685 | 0.0079357 | -0.0014485 | 0.00042721 | 0.060338 | 0.028517 | 0.054232 | 0.010204 | 0.17081 | -0.05877 | 121.5305 | 121.4655 | 121.4841 | -0.049321 | 0.042256 | 0.44907 | -0.038036 | 121.2315 | 121.5619 | 121.2629 | -0.24657 | 0.10174 | 0.085791 | 0.16127 | 0.092292 | -0.009449 | 0.020788 | 0.039388 | -0.095505 | -0.21321 | 0.19332 | 0.11303 | 0.20853 | 0.11717 | -0.18182 | 121.6816 | 121.6166 | 121.6352 | 0.32188 | -121.494 | 121.3826 | 121.7129 | 121.4139 | 0.60013 | -121.6913
877 | 121.6003 | -0.11444 | 121.3943 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068622 | -0.01057 | 0.058471 | 0.015566 | -0.0014485 | 0.00021361 | 0.060552 | 0.028517 | 0.054018 | 0.010204 | 0.16166 | -0.054192 | 121.5213 | 121.4655 | 121.4795 | -0.044742 | 0.037677 | 0.45365 | -0.042615 | 121.2315 | 121.5619 | 121.2308 | -0.24657 | 0.069699 | 0.12699 | 0.12465 | 0.060249 | -0.00945 | 0.071142 | 0.085163 | -0.13213 | -0.16286 | 0.15212 | 0.071826 | 0.20395 | 0.16752 | -0.16352 | 121.6358 | 121.5799 | 121.594 | 0.2761 | -121.4391 | 121.3459 | 121.6763 | 121.3453 | 0.56809 | -121.6409
878.75 | 121.5317 | -0.13733 | 121.4081 | 1.4211e-13 | -0.016166 | 0.002421 | 0.068409 | -0.010784 | 0.058685 | -0.014956 | -0.0016621 | -0.00021359 | 0.060552 | 0.028303 | 0.054232 | 0.010204 | 0.16624 | -0.05877 | 121.5351 | 121.4655 | 121.4841 | -0.072215 | 0.042256 | 0.45823 | -0.047194 | 121.2315 | 121.571 | 121.3224 | -0.24199 | 0.065114 | 0.12699 | 0.14753 | 0.078559 | 0.013445 | 0.057409 | 0.076009 | -0.10466 | -0.17659 | 0.17958 | 0.090135 | 0.19479 | 0.16294 | -0.085678 | 121.6724 | 121.6028 | 121.6214 | 0.30356 | -121.4803 | 121.3688 | 121.7084 | 121.4597 | 0.59556 | -121.6501
880.4375 | 121.5866 | -0.09613 | 121.4081 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068195 | -0.01057 | 0.058898 | 0.0079357 | -0.00080746 | 0.00021361 | 0.060552 | 0.028517 | 0.053804 | 0.019361 | 0.16166 | -0.045036 | 121.5259 | 121.4746 | 121.4932 | -0.063057 | 0.042256 | 0.47654 | -0.028879 | 121.2406 | 121.5664 | 121.2446 | -0.24199 | 0.033073 | 0.11783 | 0.11549 | 0.051094 | 0.018021 | 0.066567 | 0.085166 | -0.14586 | -0.16743 | 0.13839 | 0.067251 | 0.21311 | 0.15837 | -0.16351 | 121.622 | 121.5708 | 121.5894 | 0.25779 | -121.4711 | 121.3368 | 121.6626 | 121.3407 | 0.57268 | -121.6501
882.1875 | 121.4813 | -0.14648 | 121.4493 | 1.4211e-13 | -0.01638 | 0.002421 | 0.068622 | -0.010356 | 0.058471 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.028303 | 0.054445 | 0.014783 | 0.16624 | -0.049614 | 121.5259 | 121.4701 | 121.4887 | 0.001048 | 0.037677 | 0.47654 | -0.042615 | 121.2452 | 121.5664 | 121.1255 | -0.24199 | 0.14753 | 0.076634 | 0.16127 | 0.09687 | -0.050662 | 0.020789 | 0.039389 | -0.095505 | -0.20405 | 0.18416 | 0.10387 | 0.19937 | 0.11717 | -0.32376 | 121.6724 | 121.6166 | 121.6352 | 0.31272 | -121.4482 | 121.3917 | 121.7129 | 121.272 | 0.62303 | -121.6913
883.9219 | 121.5179 | -0.13733 | 121.4172 | 1.4211e-13 | -0.016166 | 0.0019936 | 0.068195 | -0.010356 | 0.058471 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060125 | 0.028517 | 0.054018 | 0.014783 | 0.16624 | -0.054192 | 121.5259 | 121.4746 | 121.4932 | -0.00811 | 0.037677 | 0.4857 | -0.042615 | 121.2315 | 121.5664 | 121.3087 | -0.23741 | 0.12922 | 0.10868 | 0.15211 | 0.083137 | -0.046082 | 0.057412 | 0.076011 | -0.10008 | -0.18574 | 0.17501 | 0.094714 | 0.19479 | 0.14921 | -0.10857 | 121.6632 | 121.612 | 121.6306 | 0.30356 | -121.4253 | 121.3688 | 121.7038 | 121.446 | 0.62303 | -121.6546
885.6562 | 121.5134 | -0.14191 | 121.4264 | 1.4211e-13 | -0.015953 | 0.0022072 | 0.068622 | -0.010356 | 0.058685 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060125 | 0.028517 | 0.054445 | 0.014783 | 0.16624 | -0.049614 | 121.5259 | 121.4746 | 121.4978 | -0.031005 | 0.046835 | 0.49944 | -0.042615 | 121.2406 | 121.571 | 121.3361 | -0.24657 | 0.1109 | 0.099522 | 0.15669 | 0.092293 | -0.018609 | 0.048256 | 0.071434 | -0.10466 | -0.18574 | 0.18874 | 0.099292 | 0.20395 | 0.14463 | -0.090253 | 121.6678 | 121.6166 | 121.6397 | 0.30814 | -121.4574 | 121.3826 | 121.7129 | 121.478 | 0.64135 | -121.673
887.3438 | 121.5729 | -0.082397 | 121.3943 | 1.4211e-13 | -0.01638 | 0.002421 | 0.068836 | -0.01057 | 0.058257 | -0.0073253 | -0.0014485 | 1.2e-08 | 0.060338 | 0.028303 | 0.054018 | 0.014783 | 0.16166 | -0.054192 | 121.5213 | 121.4655 | 121.4887 | -0.035584 | 0.037677 | 0.49944 | -0.038036 | 121.2406 | 121.5619 | 121.327 | -0.25115 | 0.046813 | 0.12699 | 0.09718 | 0.028205 | -0.018608 | 0.071142 | 0.094321 | -0.16875 | -0.1537 | 0.12007 | 0.044361 | 0.21311 | 0.16752 | -0.067366 | 121.6037 | 121.5479 | 121.5711 | 0.24405 | -121.4299 | 121.323 | 121.6443 | 121.4094 | 0.58183 | -121.6455
889.0938 | 121.6232 | -0.11902 | 121.4264 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068409 | -0.010784 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060125 | 0.028517 | 0.054018 | 0.010204 | 0.16166 | -0.05877 | 121.5259 | 121.4746 | 121.4841 | -0.026426 | 0.046835 | 0.5086 | -0.047194 | 121.2406 | 121.571 | 121.24 | -0.25115 | 0.092593 | 0.099522 | 0.12922 | 0.060249 | -0.032344 | 0.048256 | 0.057698 | -0.13213 | -0.18574 | 0.16585 | 0.071825 | 0.20395 | 0.14463 | -0.1864 | 121.6449 | 121.5937 | 121.6031 | 0.28068 | -121.4528 | 121.3597 | 121.69 | 121.359 | 0.62762 | -121.6775
890.8281 | 121.4813 | -0.16022 | 121.4493 | 1.4211e-13 | -0.016594 | 0.0022072 | 0.068409 | -0.01057 | 0.058471 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060125 | 0.028517 | 0.054018 | 0.019361 | 0.16624 | -0.049614 | 121.5259 | 121.4792 | 121.4932 | -0.026426 | 0.037677 | 0.51775 | -0.051772 | 121.2361 | 121.5619 | 121.3636 | -0.24199 | 0.13379 | 0.076634 | 0.17958 | 0.1106 | -0.023188 | 0.029947 | 0.043967 | -0.081772 | -0.21321 | 0.19789 | 0.10844 | 0.19022 | 0.11259 | -0.08567 | 121.6861 | 121.6394 | 121.6535 | 0.32645 | -121.4757 | 121.3963 | 121.7221 | 121.5238 | 0.67797 | -121.6913
892.5781 | 121.6049 | -0.11902 | 121.431 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068409 | -0.01057 | 0.058685 | 0.0079357 | -0.0014485 | 1.2e-08 | 0.060338 | 0.028517 | 0.054018 | 0.014783 | 0.16624 | -0.054192 | 121.5351 | 121.4746 | 121.4932 | -0.049321 | 0.042256 | 0.53149 | -0.038036 | 121.2452 | 121.5664 | 121.2446 | -0.24199 | 0.069698 | 0.1041 | 0.1338 | 0.064827 | -0.004871 | 0.043679 | 0.062278 | -0.12297 | -0.18574 | 0.16128 | 0.080983 | 0.20395 | 0.13548 | -0.1864 | 121.6541 | 121.5937 | 121.6123 | 0.28525 | -121.4803 | 121.3642 | 121.6855 | 121.3636 | 0.65051 | -121.673
894.3125 | 121.5775 | -0.11902 | 121.3943 | 1.4211e-13 | -0.016166 | 0.0022072 | 0.068409 | -0.01057 | 0.058685 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060125 | 0.028517 | 0.053804 | 0.010204 | 0.16166 | -0.045036 | 121.5305 | 121.4701 | 121.4887 | 0.005627 | 0.051413 | 0.54065 | -0.042615 | 121.2406 | 121.571 | 120.9012 | -0.23741 | 0.12465 | 0.13615 | 0.12922 | 0.073983 | -0.050663 | 0.075721 | 0.094321 | -0.11839 | -0.1537 | 0.17043 | 0.076404 | 0.19479 | 0.17668 | -0.49318 | 121.6495 | 121.5891 | 121.6077 | 0.28068 | -121.3887 | 121.3597 | 121.69 | 121.0202 | 0.65967 | -121.6318
895.9844 | 121.5179 | -0.13275 | 121.4218 | 1.4211e-13 | -0.016594 | 0.0022072 | 0.068836 | -0.01057 | 0.058685 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.028517 | 0.054018 | 0.014783 | 0.17081 | -0.049614 | 121.5396 | 121.4838 | 121.4978 | 0.005627 | 0.037677 | 0.54522 | -0.047194 | 121.2406 | 121.571 | 120.9424 | -0.24657 | 0.13838 | 0.11784 | 0.14753 | 0.083137 | -0.055241 | 0.061992 | 0.076012 | -0.11382 | -0.18117 | 0.17043 | 0.085557 | 0.19937 | 0.14921 | -0.47943 | 121.6724 | 121.6166 | 121.6306 | 0.30357 | -121.4162 | 121.3734 | 121.7038 | 121.0751 | 0.67798 | -121.6684
897.7188 | 121.5729 | -0.1236 | 121.4127 | 1.4211e-13 | -0.016594 | 0.0022072 | 0.068622 | -0.01057 | 0.058898 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060766 | 0.028517 | 0.054018 | 0.005626 | 0.16624 | -0.054192 | 121.5396 | 121.4746 | 121.4932 | 0.010206 | 0.037677 | 0.56354 | -0.042615 | 121.2452 | 121.5756 | 120.9927 | -0.25115 | 0.1338 | 0.12699 | 0.12922 | 0.069404 | -0.064398 | 0.061989 | 0.080588 | -0.12755 | -0.16743 | 0.16127 | 0.080981 | 0.20853 | 0.16294 | -0.41992 | 121.6632 | 121.5982 | 121.6168 | 0.28983 | -121.4025 | 121.3688 | 121.6992 | 121.1163 | 0.68714 | -121.6638
899.4531 | 121.5591 | -0.10986 | 121.4127 | 1.4211e-13 | -0.015953 | 0.00178 | 0.068409 | -0.010784 | 0.058685 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060125 | 0.028303 | 0.053804 | 0.010204 | 0.16624 | -0.054192 | 121.5305 | 121.4838 | 121.4932 | 0.010206 | 0.042256 | 0.57728 | -0.042615 | 121.2452 | 121.5756 | 121.1255 | -0.25115 | 0.12007 | 0.11783 | 0.12007 | 0.055671 | -0.064398 | 0.071147 | 0.080588 | -0.14128 | -0.16743 | 0.15212 | 0.067248 | 0.20853 | 0.16294 | -0.28714 | 121.6404 | 121.5937 | 121.6031 | 0.2761 | -121.4025 | 121.3551 | 121.6855 | 121.2354 | 0.68714 | -121.6638
901.1406 | 121.4767 | -0.16022 | 121.4676 | 1.4211e-13 | -0.01638 | 0.0019936 | 0.068195 | -0.010997 | 0.058685 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.028303 | 0.054018 | 0.019361 | 0.17539 | -0.049614 | 121.5442 | 121.4746 | 121.4932 | 0.010206 | 0.042256 | 0.60017 | -0.038036 | 121.2452 | 121.5664 | 120.86 | -0.24657 | 0.17042 | 0.076638 | 0.17958 | 0.1106 | -0.05982 | 0.007058 | 0.025657 | -0.08635 | -0.22236 | 0.20247 | 0.12218 | 0.20853 | 0.098856 | -0.60763 | 121.7044 | 121.6349 | 121.6535 | 0.33561 | -121.4574 | 121.4054 | 121.7267 | 121.0202 | 0.76039 | -121.7142
902.8906 | 121.5546 | -0.12817 | 121.4355 | 1.4211e-13 | -0.01638 | 0.0019936 | 0.068195 | -0.01057 | 0.058471 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.028303 | 0.053804 | 0.010204 | 0.16166 | -0.049614 | 121.5305 | 121.4838 | 121.4932 | 0.010206 | 0.046835 | 0.60475 | -0.038036 | 121.2452 | 121.5664 | 120.9744 | -0.24199 | 0.13838 | 0.094946 | 0.13838 | 0.07856 | -0.05982 | 0.048259 | 0.0577 | -0.11381 | -0.19032 | 0.17501 | 0.090138 | 0.20395 | 0.1309 | -0.46112 | 121.6587 | 121.612 | 121.6214 | 0.28983 | -121.4253 | 121.3734 | 121.6946 | 121.1026 | 0.73292 | -121.6775
904.625 | 121.5225 | -0.1236 | 121.431 | 1.4211e-13 | -0.01638 | 0.0026346 | 0.068622 | -0.010356 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.028517 | 0.054232 | 0.010204 | 0.16624 | -0.049614 | 121.5305 | 121.4792 | 121.4978 | 0.005627 | 0.046835 | 0.62306 | -0.047194 | 121.2406 | 121.571 | 121.0477 | -0.24199 | 0.12922 | 0.099524 | 0.1338 | 0.073982 | -0.055241 | 0.048258 | 0.066857 | -0.11839 | -0.19032 | 0.17043 | 0.076402 | 0.19479 | 0.14006 | -0.38328 | 121.6541 | 121.6028 | 121.6214 | 0.28983 | -121.4253 | 121.3642 | 121.6946 | 121.1713 | 0.74666 | -121.673
906.2969 | 121.5088 | -0.16479 | 121.4539 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068409 | -0.01057 | 0.058471 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060338 | 0.02809 | 0.054018 | 0.014783 | 0.17081 | -0.05877 | 121.5305 | 121.4838 | 121.5024 | 0.005627 | 0.046835 | 0.63222 | -0.042615 | 121.2498 | 121.5756 | 120.9744 | -0.24657 | 0.17042 | 0.076636 | 0.17958 | 0.10602 | -0.064397 | 0.029949 | 0.048547 | -0.081772 | -0.20405 | 0.21163 | 0.12218 | 0.20395 | 0.12175 | -0.47943 | 121.6953 | 121.6486 | 121.6672 | 0.33561 | -121.4482 | 121.4146 | 121.7404 | 121.1392 | 0.79702 | -121.7004
908.0469 | 121.5546 | -0.10529 | 121.4539 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068409 | -0.010356 | 0.058898 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060125 | 0.028944 | 0.054018 | 0.014783 | 0.16166 | -0.049614 | 121.5396 | 121.4838 | 121.5024 | 0.010206 | 0.037677 | 0.65054 | -0.033458 | 121.2544 | 121.5756 | 121.1209 | -0.24199 | 0.11549 | 0.085793 | 0.12007 | 0.055672 | -0.05982 | 0.029949 | 0.048547 | -0.1367 | -0.19947 | 0.14296 | 0.071828 | 0.20853 | 0.12175 | -0.33291 | 121.6449 | 121.5891 | 121.6077 | 0.26694 | -121.4437 | 121.3597 | 121.6809 | 121.2262 | 0.75582 | -121.6958
909.7188 | 121.5088 | -0.15564 | 121.431 | 1.4211e-13 | -0.016594 | 0.0022072 | 0.06905 | -0.01057 | 0.059112 | 0.00030522 | -0.00080746 | 0.00042721 | 0.060125 | 0.028731 | 0.054232 | 0.019361 | 0.17539 | -0.049614 | 121.5442 | 121.4792 | 121.507 | 0.001048 | 0.051413 | 0.65511 | -0.038036 | 121.2498 | 121.5756 | 121.0981 | -0.24199 | 0.15669 | 0.11326 | 0.175 | 0.10603 | -0.050662 | 0.048258 | 0.076014 | -0.086349 | -0.18116 | 0.20705 | 0.1176 | 0.20395 | 0.14463 | -0.33292 | 121.6999 | 121.6349 | 121.6626 | 0.33103 | -121.4299 | 121.4054 | 121.7312 | 121.2537 | 0.81075 | -121.673
911.4844 | 121.5683 | -0.11902 | 121.4127 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068622 | -0.01057 | 0.058898 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.028517 | 0.054232 | 0.010204 | 0.16166 | -0.054192 | 121.5396 | 121.4838 | 121.4978 | 0.014784 | 0.037677 | 0.67343 | -0.028879 | 121.2544 | 121.5802 | 120.9241 | -0.24199 | 0.1338 | 0.12699 | 0.12922 | 0.064827 | -0.068976 | 0.071147 | 0.085167 | -0.12297 | -0.15828 | 0.1567 | 0.09014 | 0.21311 | 0.16752 | -0.48859 | 121.6587 | 121.6028 | 121.6168 | 0.28068 | -121.3979 | 121.3734 | 121.6992 | 121.0431 | 0.79245 | -121.6546
913.1719 | 121.5546 | -0.12817 | 121.4172 | 1.4211e-13 | -0.01638 | 0.0022072 | 0.068409 | -0.010356 | 0.058898 | 0.0079357 | -0.0016621 | 0.00021361 | 0.060338 | 0.028517 | 0.053804 | 0.005626 | 0.17081 | -0.054192 | 121.5351 | 121.4884 | 121.507 | 0.014784 | 0.046835 | 0.68259 | -0.042615 | 121.2361 | 121.571 | 120.9561 | -0.24199 | 0.14296 | 0.11783 | 0.1338 | 0.073982 | -0.068976 | 0.071149 | 0.089747 | -0.11381 | -0.18117 | 0.17501 | 0.085559 | 0.19937 | 0.15379 | -0.46112 | 121.6632 | 121.6166 | 121.6352 | 0.29899 | -121.4025 | 121.3642 | 121.6992 | 121.0843 | 0.81076 | -121.6592
914.8438 | 121.4996 | -0.15564 | 121.4539 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068195 | -0.010356 | 0.058898 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.028517 | 0.053804 | 0.019361 | 0.17081 | -0.05877 | 121.5396 | 121.4884 | 121.5024 | 0.010206 | 0.042256 | 0.7009 | -0.047194 | 121.2452 | 121.5756 | 121.0981 | -0.24657 | 0.16585 | 0.085793 | 0.175 | 0.09687 | -0.068976 | 0.034528 | 0.048547 | -0.090927 | -0.20863 | 0.1979 | 0.10845 | 0.19937 | 0.12175 | -0.35581 | 121.6953 | 121.644 | 121.658 | 0.32645 | -121.4437 | 121.4009 | 121.7312 | 121.2537 | 0.85654 | -121.7004
916.5938 | 121.5408 | -0.1236 | 121.4447 | 1.4211e-13 | -0.016166 | 0.002421 | 0.068836 | -0.010356 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.028517 | 0.053804 | 0.010204 | 0.16624 | -0.054192 | 121.5351 | 121.4792 | 121.5024 | 0.010206 | 0.033099 | 0.71006 | -0.042615 | 121.2498 | 121.5802 | 121.0294 | -0.24199 | 0.1338 | 0.090369 | 0.1338 | 0.069404 | -0.064398 | 0.034525 | 0.057702 | -0.11839 | -0.1949 | 0.1567 | 0.080981 | 0.19937 | 0.13548 | -0.41533 | 121.6587 | 121.6028 | 121.626 | 0.28983 | -121.4345 | 121.3734 | 121.7038 | 121.153 | 0.83366 | -121.6867
918.3438 | 121.4996 | -0.15564 | 121.4584 | 1.4211e-13 | -0.016807 | 0.00178 | 0.068836 | -0.01057 | 0.058898 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060125 | 0.028731 | 0.053591 | 0.010204 | 0.17539 | -0.05877 | 121.5396 | 121.4838 | 121.507 | 0.010206 | 0.046835 | 0.72379 | -0.047194 | 121.2452 | 121.571 | 121.0065 | -0.23741 | 0.16585 | 0.081215 | 0.16584 | 0.09687 | -0.068976 | 0.025371 | 0.048548 | -0.08177 | -0.21321 | 0.20248 | 0.10845 | 0.19022 | 0.11259 | -0.45196 | 121.6953 | 121.6394 | 121.6626 | 0.33103 | -121.4482 | 121.4009 | 121.7267 | 121.1621 | 0.87943 | -121.6958
920.0781 | 121.4676 | -0.15106 | 121.4676 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068622 | -0.01057 | 0.059112 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.028517 | 0.054018 | 0.014783 | 0.16624 | -0.05877 | 121.5351 | 121.4884 | 121.507 | 0.010206 | 0.042256 | 0.75127 | -0.038036 | 121.2498 | 121.5802 | 120.8874 | -0.25115 | 0.16127 | 0.067481 | 0.16584 | 0.092292 | -0.068976 | 0.020795 | 0.039393 | -0.10008 | -0.21779 | 0.19332 | 0.11303 | 0.21311 | 0.11259 | -0.58015 | 121.6861 | 121.6394 | 121.658 | 0.3173 | -121.4574 | 121.4009 | 121.7312 | 121.0385 | 0.90233 | -121.7187
921.75 | 121.4767 | -0.15106 | 121.4355 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068622 | -0.010784 | 0.058898 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060125 | 0.028944 | 0.053804 | 0.010204 | 0.17081 | -0.054192 | 121.5351 | 121.493 | 121.5116 | 0.014784 | 0.042256 | 0.76043 | -0.047194 | 121.2452 | 121.5802 | 121.0889 | -0.25115 | 0.16585 | 0.099524 | 0.16127 | 0.09687 | -0.068976 | 0.057417 | 0.076015 | -0.10008 | -0.19032 | 0.19332 | 0.10387 | 0.20395 | 0.14463 | -0.34665 | 121.6861 | 121.644 | 121.6626 | 0.32188 | -121.4208 | 121.3963 | 121.7312 | 121.24 | 0.91149 | -121.6867
923.4844 | 121.4722 | -0.15106 | 121.4493 | 1.4211e-13 | -0.016594 | 0.0022072 | 0.068622 | -0.01057 | 0.058257 | 0.023196 | -0.0010211 | 0.00042721 | 0.060338 | 0.028731 | 0.054018 | 0.014783 | 0.16624 | -0.054192 | 121.5396 | 121.4884 | 121.5116 | 0.014784 | 0.042256 | 0.77874 | -0.038036 | 121.2544 | 121.5802 | 120.9241 | -0.24199 | 0.16585 | 0.09037 | 0.16584 | 0.09687 | -0.068976 | 0.039105 | 0.062282 | -0.090927 | -0.1949 | 0.19332 | 0.11303 | 0.20395 | 0.1309 | -0.52522 | 121.6907 | 121.6394 | 121.6626 | 0.3173 | -121.4345 | 121.4054 | 121.7312 | 121.0751 | 0.9298 | -121.6913
925.1562 | 121.5958 | -0.13275 | 121.4355 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068622 | -0.01057 | 0.058898 | -0.0073253 | -0.0010211 | 0.00021361 | 0.060125 | 0.028517 | 0.054232 | 0.010204 | 0.16624 | -0.045036 | 121.5396 | 121.4975 | 121.5161 | 0.005627 | 0.046835 | 0.80163 | -0.038036 | 121.2544 | 121.5802 | 121.0111 | -0.25115 | 0.13838 | 0.1041 | 0.14295 | 0.087715 | -0.050663 | 0.061996 | 0.080593 | -0.11839 | -0.18116 | 0.17959 | 0.094715 | 0.21311 | 0.14463 | -0.42449 | 121.6724 | 121.6303 | 121.6489 | 0.29899 | -121.4299 | 121.3871 | 121.7129 | 121.1438 | 0.93438 | -121.6867
926.8281 | 121.4996 | -0.14648 | 121.463 | 1.4211e-13 | -0.017021 | 0.002421 | 0.068622 | -0.01057 | 0.058898 | 0.015566 | -0.0016621 | 1.2e-08 | 0.060125 | 0.029158 | 0.054018 | 0.010204 | 0.17539 | -0.054192 | 121.5396 | 121.4884 | 121.5116 | 0.014784 | 0.046835 | 0.83826 | -0.038036 | 121.259 | 121.5848 | 121.0248 | -0.24199 | 0.16127 | 0.076637 | 0.15669 | 0.092292 | -0.068976 | 0.025372 | 0.048549 | -0.095505 | -0.20405 | 0.19332 | 0.10845 | 0.20395 | 0.12175 | -0.43822 | 121.6861 | 121.6349 | 121.658 | 0.32188 | -121.4482 | 121.4054 | 121.7312 | 121.1713 | 0.98475 | -121.705
928.5781 | 121.6095 | -0.12817 | 121.4035 | 1.4211e-13 | -0.01638 | 0.002421 | 0.068622 | -0.01057 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.028731 | 0.053804 | 0.010204 | 0.17539 | -0.049614 | 121.5396 | 121.4975 | 121.5116 | -0.003531 | 0.046835 | 0.87947 | -0.038036 | 121.259 | 121.5756 | 121.1209 | -0.24199 | 0.12464 | 0.13615 | 0.13838 | 0.07856 | -0.046083 | 0.09404 | 0.10806 | -0.11381 | -0.14454 | 0.17501 | 0.090138 | 0.20395 | 0.1721 | -0.28256 | 121.6678 | 121.6257 | 121.6397 | 0.30357 | -121.407 | 121.3871 | 121.7038 | 121.2491 | 1.0076 | -121.6455
930.375 | 121.4813 | -0.16937 | 121.4401 | 1.4211e-13 | -0.017021 | 0.0022072 | 0.068409 | -0.010356 | 0.058898 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.028944 | 0.054018 | 0.014783 | 0.17081 | -0.049614 | 121.5396 | 121.493 | 121.5116 | 0.010206 | 0.051413 | 0.92984 | -0.047194 | 121.2544 | 121.5848 | 121.0111 | -0.24657 | 0.17958 | 0.099525 | 0.18416 | 0.11976 | -0.05982 | 0.052839 | 0.071437 | -0.077194 | -0.18574 | 0.22079 | 0.12218 | 0.19937 | 0.14464 | -0.42907 | 121.709 | 121.6623 | 121.6809 | 0.34019 | -121.4299 | 121.4238 | 121.7541 | 121.1804 | 1.0992 | -121.6867
932.0469 | 121.4813 | -0.15106 | 121.4264 | 1.4211e-13 | -0.01638 | 0.002421 | 0.068409 | -0.010356 | 0.058685 | 0.015566 | -0.0010211 | 1.2e-08 | 0.060125 | 0.028303 | 0.053804 | 0.010204 | 0.17081 | -0.054192 | 121.5442 | 121.493 | 121.5116 | 0.005627 | 0.046835 | 0.96189 | -0.033458 | 121.2544 | 121.5848 | 120.9699 | -0.25572 | 0.15669 | 0.11784 | 0.16127 | 0.09687 | -0.059819 | 0.066572 | 0.08517 | -0.10466 | -0.17201 | 0.1979 | 0.1176 | 0.22227 | 0.15837 | -0.45654 | 121.6953 | 121.644 | 121.6626 | 0.32188 | -121.4208 | 121.4054 | 121.7358 | 121.1209 | 1.1129 | -121.6821
933.7188 | 121.582 | -0.1236 | 121.4401 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068409 | -0.01057 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.028731 | 0.053804 | 0.019361 | 0.17081 | -0.045036 | 121.5396 | 121.493 | 121.5161 | 0.001048 | 0.046835 | 1.0077 | -0.038036 | 121.2544 | 121.5802 | 120.9195 | -0.25115 | 0.12464 | 0.099525 | 0.14296 | 0.07856 | -0.046084 | 0.052839 | 0.076015 | -0.12755 | -0.18574 | 0.17043 | 0.08556 | 0.21311 | 0.14006 | -0.52064 | 121.6632 | 121.6166 | 121.6397 | 0.29441 | -121.4391 | 121.378 | 121.7038 | 121.0431 | 1.1313 | -121.6913
935.4688 | 121.4859 | -0.1831 | 121.4539 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068195 | -0.01057 | 0.058685 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060552 | 0.028731 | 0.054018 | 0.005626 | 0.17081 | -0.054192 | 121.5442 | 121.4975 | 121.5116 | 0.005627 | 0.051413 | 1.0718 | -0.033458 | 121.2635 | 121.5893 | 120.9561 | -0.24657 | 0.18873 | 0.090371 | 0.18873 | 0.12891 | -0.059819 | 0.043686 | 0.057705 | -0.063462 | -0.19032 | 0.23452 | 0.14965 | 0.21311 | 0.13548 | -0.49774 | 121.7273 | 121.6806 | 121.6947 | 0.35392 | -121.4482 | 121.4466 | 121.7724 | 121.1392 | 1.2549 | -121.7004
937.2031 | 121.4996 | -0.13733 | 121.4447 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068409 | -0.010356 | 0.059112 | 0.0079357 | -0.0014485 | -0.00021359 | 0.060125 | 0.028731 | 0.054018 | 0.010204 | 0.17539 | -0.049614 | 121.5488 | 121.493 | 121.5161 | -0.003531 | 0.051413 | 1.1267 | -0.047194 | 121.259 | 121.5848 | 120.979 | -0.24199 | 0.1338 | 0.1041 | 0.14753 | 0.087715 | -0.046083 | 0.048262 | 0.071438 | -0.10466 | -0.18574 | 0.18874 | 0.090135 | 0.19479 | 0.14006 | -0.46569 | 121.6861 | 121.6303 | 121.6535 | 0.31272 | -121.4482 | 121.3963 | 121.7221 | 121.1163 | 1.2641 | -121.6867
938.8906 | 121.6049 | -0.10529 | 121.431 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068195 | -0.010784 | 0.058257 | 0.00030522 | -0.00080746 | -0.00021359 | 0.060338 | 0.028517 | 0.053804 | 0.001048 | 0.16624 | -0.049614 | 121.5442 | 121.493 | 121.5161 | 0.014784 | 0.051413 | 1.1817 | -0.038036 | 121.2452 | 121.5848 | 120.9286 | -0.24657 | 0.12007 | 0.11326 | 0.10633 | 0.055672 | -0.064398 | 0.061995 | 0.085171 | -0.14128 | -0.18574 | 0.1567 | 0.06725 | 0.20853 | 0.15379 | -0.50233 | 121.6495 | 121.5983 | 121.6214 | 0.27152 | -121.4162 | 121.3505 | 121.69 | 121.0339 | 1.287 | -121.6775
940.6406 | 121.5775 | -0.13733 | 121.4447 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068622 | -0.01057 | 0.058685 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.028944 | 0.053804 | 0.019361 | 0.17539 | -0.054192 | 121.5442 | 121.493 | 121.5161 | 0.010206 | 0.051413 | 1.2549 | -0.038036 | 121.259 | 121.5848 | 120.8783 | -0.25115 | 0.14753 | 0.099526 | 0.15669 | 0.083137 | -0.064398 | 0.048262 | 0.071438 | -0.11382 | -0.18574 | 0.18874 | 0.099293 | 0.21311 | 0.14006 | -0.56642 | 121.6816 | 121.6303 | 121.6535 | 0.31272 | -121.4345 | 121.3963 | 121.7221 | 121.0156 | 1.3923 | -121.6958
942.3281 | 121.6003 | -0.10529 | 121.4172 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.068409 | -0.01057 | 0.058898 | 0.00030522 | -0.0012349 | -0.00021359 | 0.060125 | 0.028731 | 0.053804 | 0.010204 | 0.16624 | -0.049614 | 121.5488 | 121.493 | 121.5207 | 0.001048 | 0.051413 | 1.3236 | -0.038036 | 121.259 | 121.5893 | 121.0019 | -0.23741 | 0.10633 | 0.13157 | 0.11549 | 0.055672 | -0.050662 | 0.075728 | 0.10348 | -0.13212 | -0.15827 | 0.1567 | 0.06725 | 0.19937 | 0.1721 | -0.41533 | 121.6541 | 121.5983 | 121.626 | 0.27152 | -121.4162 | 121.3642 | 121.6946 | 121.1072 | 1.4289 | -121.6546
944.0156 | 121.5729 | -0.11444 | 121.4401 | 1.4211e-13 | -0.016594 | 0.0019936 | 0.068195 | -0.010356 | 0.058685 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060338 | 0.028944 | 0.053804 | 0.010204 | 0.16624 | -0.049614 | 121.5442 | 121.493 | 121.5116 | 0.010206 | 0.051413 | 1.406 | -0.038036 | 121.2544 | 121.5893 | 121.034 | -0.24199 | 0.12465 | 0.1041 | 0.12465 | 0.064827 | -0.05982 | 0.052839 | 0.071437 | -0.12755 | -0.18574 | 0.16585 | 0.076405 | 0.20395 | 0.14921 | -0.40617 | 121.6587 | 121.6074 | 121.626 | 0.28068 | -121.4299 | 121.3688 | 121.7038 | 121.1484 | 1.5205 | -121.6821
945.6875 | 121.5179 | -0.15564 | 121.4676 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068622 | -0.010143 | 0.059112 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060338 | 0.028517 | 0.053804 | 0.019361 | 0.17081 | -0.049614 | 121.5534 | 121.4975 | 121.5207 | 0.001048 | 0.055992 | 1.5113 | -0.028879 | 121.2681 | 121.5939 | 120.9424 | -0.23741 | 0.15669 | 0.085795 | 0.175 | 0.10603 | -0.050662 | 0.029953 | 0.053129 | -0.08177 | -0.19947 | 0.21163 | 0.12676 | 0.20853 | 0.12633 | -0.52521 | 121.709 | 121.6532 | 121.6764 | 0.32645 | -121.4665 | 121.4238 | 121.7496 | 121.098 | 1.667 | -121.705
947.4219 | 121.6187 | -0.10986 | 121.4264 | 1.4211e-13 | -0.016594 | 0.002421 | 0.068195 | -0.01057 | 0.058898 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.028731 | 0.053804 | 0.010204 | 0.17081 | -0.049614 | 121.5534 | 121.4975 | 121.5161 | 0.010206 | 0.055992 | 1.5938 | -0.038036 | 121.2544 | 121.5893 | 121.0156 | -0.24199 | 0.12007 | 0.12699 | 0.12007 | 0.060249 | -0.05982 | 0.071151 | 0.089748 | -0.13213 | -0.17201 | 0.16586 | 0.071827 | 0.20395 | 0.16295 | -0.41076 | 121.6632 | 121.6074 | 121.626 | 0.28068 | -121.4162 | 121.3642 | 121.6992 | 121.1255 | 1.7036 | -121.6684
949.1875 | 121.6232 | -0.10071 | 121.4539 | 1.4211e-13 | -0.016807 | 0.002421 | 0.068409 | -0.010784 | 0.058685 | 0.0079357 | -0.00080746 | 0.00021361 | 0.060338 | 0.028517 | 0.054232 | 0.014783 | 0.17539 | -0.054192 | 121.5488 | 121.493 | 121.5161 | 0.001048 | 0.051413 | 1.6991 | -0.038036 | 121.2635 | 121.5939 | 120.9515 | -0.24199 | 0.10176 | 0.094949 | 0.11549 | 0.046516 | -0.05524 | 0.039107 | 0.062283 | -0.14128 | -0.19032 | 0.15212 | 0.062672 | 0.20395 | 0.14006 | -0.50232 | 121.6495 | 121.5937 | 121.6168 | 0.2761 | -121.4528 | 121.3642 | 121.6946 | 121.0522 | 1.7998 | -121.6958
950.8594 | 121.6599 | -0.1236 | 121.4264 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.068195 | -0.01057 | 0.058471 | -0.0073253 | -0.0014485 | 0.00064101 | 0.060338 | 0.028731 | 0.053804 | 0.014783 | 0.17081 | -0.054192 | 121.558 | 121.4975 | 121.5207 | 0.014784 | 0.055992 | 1.7723 | -0.038036 | 121.2544 | 121.5939 | 120.9103 | -0.24199 | 0.13838 | 0.13157 | 0.13838 | 0.069404 | -0.068976 | 0.071151 | 0.094327 | -0.11839 | -0.17201 | 0.17959 | 0.08556 | 0.20395 | 0.16753 | -0.51606 | 121.6816 | 121.6211 | 121.6443 | 0.29441 | -121.4116 | 121.378 | 121.7175 | 121.0339 | 1.8959 | -121.6684
952.6094 | 121.55 | -0.12817 | 121.4584 | 1.4211e-13 | -0.017021 | 0.0022072 | 0.068409 | -0.010784 | 0.058685 | 0.00030522 | -0.0010211 | 0.00021361 | 0.060338 | 0.028944 | 0.053804 | 0.010204 | 0.17081 | -0.054192 | 121.558 | 121.4975 | 121.5207 | 0.005627 | 0.051413 | 1.8364 | -0.033458 | 121.2544 | 121.5939 | 120.9241 | -0.24657 | 0.1338 | 0.099528 | 0.13838 | 0.073982 | -0.059819 | 0.039108 | 0.062284 | -0.11839 | -0.20405 | 0.17959 | 0.094716 | 0.21311 | 0.13548 | -0.53437 | 121.6861 | 121.6257 | 121.6489 | 0.29899 | -121.4528 | 121.3826 | 121.7221 | 121.0522 | 1.9646 | -121.705
954.3594 | 121.5683 | -0.13275 | 121.4401 | 1.4211e-13 | -0.01638 | 0.0019936 | 0.068409 | -0.010784 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060338 | 0.028944 | 0.053591 | 0.014783 | 0.16166 | -0.049614 | 121.558 | 121.493 | 121.5161 | 0.001048 | 0.055992 | 1.9005 | -0.042615 | 121.2544 | 121.5893 | 120.8417 | -0.24657 | 0.1338 | 0.11784 | 0.14753 | 0.083137 | -0.050662 | 0.052839 | 0.076015 | -0.11382 | -0.18574 | 0.18874 | 0.090136 | 0.20395 | 0.14921 | -0.59847 | 121.6907 | 121.6257 | 121.6489 | 0.29441 | -121.4391 | 121.3871 | 121.7221 | 120.9744 | 2.0333 | -121.6867
956.0469 | 121.6003 | -0.11902 | 121.4401 | 1.4211e-13 | -0.017235 | 0.0022072 | 0.067767 | -0.01057 | 0.058685 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060552 | 0.028731 | 0.053804 | 0.014783 | 0.17081 | -0.049614 | 121.5442 | 121.493 | 121.5116 | 0.010206 | 0.055992 | 1.9829 | -0.038036 | 121.2635 | 121.5893 | 120.8508 | -0.24199 | 0.12923 | 0.1041 | 0.1338 | 0.069405 | -0.05982 | 0.052839 | 0.071437 | -0.12297 | -0.17658 | 0.17501 | 0.080983 | 0.20395 | 0.14921 | -0.58932 | 121.6632 | 121.612 | 121.6306 | 0.28983 | -121.4299 | 121.3826 | 121.7084 | 120.9698 | 2.102 | -121.6821
957.7344 | 121.6095 | -0.12817 | 121.4401 | 1.4211e-13 | -0.017021 | 0.0026346 | 0.068409 | -0.010784 | 0.058685 | 0.0079357 | -0.0014485 | 0.00042721 | 0.060552 | 0.028517 | 0.054018 | 0.019361 | 0.16166 | -0.054192 | 121.5442 | 121.5021 | 121.5207 | 0.005627 | 0.051413 | 2.015 | -0.033458 | 121.2635 | 121.5848 | 121.0477 | -0.24657 | 0.1338 | 0.1041 | 0.14753 | 0.073982 | -0.059819 | 0.061997 | 0.080594 | -0.11839 | -0.17658 | 0.17959 | 0.094716 | 0.21311 | 0.14464 | -0.39244 | 121.6724 | 121.6303 | 121.6489 | 0.28983 | -121.4345 | 121.3917 | 121.7129 | 121.1759 | 2.1432 | -121.6867
959.4531 | 121.5088 | -0.16937 | 121.4447 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.068195 | -0.010784 | 0.058898 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060338 | 0.028517 | 0.054232 | 0.014783 | 0.17081 | -0.049614 | 121.5625 | 121.4975 | 121.5299 | 0.005627 | 0.060571 | 2.102 | -0.042615 | 121.2635 | 121.5939 | 120.9927 | -0.24657 | 0.175 | 0.11784 | 0.18416 | 0.11976 | -0.055241 | 0.052841 | 0.085174 | -0.077194 | -0.18116 | 0.22994 | 0.12676 | 0.20395 | 0.14922 | -0.45196 | 121.7319 | 121.6669 | 121.6992 | 0.34019 | -121.4391 | 121.4329 | 121.7633 | 121.1621 | 2.2714 | -121.6913
961.2031 | 121.5225 | -0.15564 | 121.463 | 1.4211e-13 | -0.016807 | 0.0019936 | 0.068195 | -0.01057 | 0.059112 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060338 | 0.028731 | 0.053804 | 0.005626 | 0.16624 | -0.049614 | 121.558 | 121.5021 | 121.5253 | 0.005627 | 0.060571 | 2.1798 | -0.038036 | 121.2635 | 121.5939 | 120.9332 | -0.24199 | 0.16127 | 0.09495 | 0.16127 | 0.10603 | -0.055241 | 0.039109 | 0.062284 | -0.086349 | -0.19947 | 0.21621 | 0.1176 | 0.20395 | 0.1309 | -0.52979 | 121.7136 | 121.6578 | 121.6809 | 0.32188 | -121.4574 | 121.4192 | 121.7496 | 121.0889 | 2.3355 | -121.705
962.8906 | 121.6095 | -0.09613 | 121.4081 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.067981 | -0.010997 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060552 | 0.028731 | 0.054018 | 0.019361 | 0.16166 | -0.049614 | 121.5534 | 121.4975 | 121.5207 | 0.005627 | 0.055992 | 2.2439 | -0.038036 | 121.2544 | 121.5848 | 120.8783 | -0.24657 | 0.10176 | 0.1453 | 0.11549 | 0.046516 | -0.055241 | 0.089462 | 0.11264 | -0.15044 | -0.1537 | 0.15212 | 0.058094 | 0.20853 | 0.17668 | -0.5298 | 121.6495 | 121.5937 | 121.6168 | 0.25779 | -121.4025 | 121.3505 | 121.6809 | 120.9744 | 2.3401 | -121.6546
964.6406 | 121.4813 | -0.17853 | 121.4859 | 1.4211e-13 | -0.016807 | 0.0026346 | 0.068409 | -0.01057 | 0.058898 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.028731 | 0.054232 | 0.010204 | 0.16624 | -0.045036 | 121.558 | 121.4975 | 121.5253 | 0.014784 | 0.06515 | 2.3263 | -0.033458 | 121.2681 | 121.5985 | 120.8737 | -0.24657 | 0.19331 | 0.072062 | 0.18873 | 0.13349 | -0.05982 | 0.011642 | 0.039396 | -0.068039 | -0.21778 | 0.24368 | 0.14507 | 0.21311 | 0.11259 | -0.6122 | 121.7365 | 121.6761 | 121.7038 | 0.34476 | -121.4711 | 121.4466 | 121.777 | 121.0522 | 2.5049 | -121.7325
966.3906 | 121.6141 | -0.10529 | 121.4401 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.067981 | -0.01057 | 0.058685 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060552 | 0.028944 | 0.053804 | 0.014783 | 0.17081 | -0.045036 | 121.5488 | 121.5067 | 121.5345 | -0.003531 | 0.060571 | 2.4271 | -0.028879 | 121.2544 | 121.6031 | 120.8966 | -0.25115 | 0.10175 | 0.10868 | 0.12007 | 0.06025 | -0.041505 | 0.066576 | 0.09433 | -0.14586 | -0.18574 | 0.16586 | 0.076407 | 0.22227 | 0.16295 | -0.54353 | 121.6541 | 121.612 | 121.6397 | 0.2761 | -121.4437 | 121.3597 | 121.7084 | 121.0019 | 2.5324 | -121.6913
968.125 | 121.4859 | -0.16022 | 121.4539 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.067981 | -0.010784 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.028517 | 0.054018 | 0.010204 | 0.17539 | -0.054192 | 121.5534 | 121.5067 | 121.5253 | 0.010206 | 0.06515 | 2.5141 | -0.038036 | 121.2635 | 121.5939 | 120.8966 | -0.25115 | 0.17042 | 0.099528 | 0.17042 | 0.10603 | -0.064398 | 0.052844 | 0.07144 | -0.090929 | -0.19032 | 0.22537 | 0.12218 | 0.21311 | 0.14006 | -0.55726 | 121.7136 | 121.6669 | 121.6855 | 0.33561 | -121.4437 | 121.4238 | 121.7541 | 121.0568 | 2.6743 | -121.705
969.8125 | 121.5637 | -0.11902 | 121.4722 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.068195 | -0.01057 | 0.058898 | 0.0079357 | -0.0012349 | 0.00042721 | 0.060552 | 0.028517 | 0.053591 | 0.014783 | 0.16624 | -0.049614 | 121.5442 | 121.5021 | 121.5253 | -0.017268 | 0.060571 | 2.6011 | -0.033458 | 121.2681 | 121.5985 | 121.0431 | -0.24657 | 0.10175 | 0.07206 | 0.1338 | 0.069405 | -0.032346 | 0.029954 | 0.053129 | -0.12755 | -0.20405 | 0.17959 | 0.085561 | 0.21311 | 0.12633 | -0.42906 | 121.6632 | 121.6211 | 121.6443 | 0.28525 | -121.4894 | 121.3871 | 121.7175 | 121.1621 | 2.7201 | -121.7187
971.5469 | 121.5363 | -0.16022 | 121.4355 | 1.4211e-13 | -0.016807 | 0.0019936 | 0.067981 | -0.010784 | 0.058898 | -0.0073253 | -0.0010211 | 0.00021361 | 0.060552 | 0.028731 | 0.054018 | 0.010204 | 0.17081 | -0.049614 | 121.558 | 121.4975 | 121.5299 | 0.005627 | 0.06515 | 2.6789 | -0.0243 | 121.2681 | 121.5939 | 120.9515 | -0.25115 | 0.16584 | 0.12242 | 0.17042 | 0.1106 | -0.055241 | 0.061996 | 0.094329 | -0.090929 | -0.16743 | 0.22537 | 0.13592 | 0.22685 | 0.15837 | -0.48401 | 121.7182 | 121.6578 | 121.6901 | 0.33103 | -121.4299 | 121.4283 | 121.7541 | 121.1118 | 2.8391 | -121.6867
973.2969 | 121.5546 | -0.16479 | 121.4447 | 1.4211e-13 | -0.017021 | 0.0022072 | 0.068195 | -0.010356 | 0.058685 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060766 | 0.028517 | 0.053804 | 0.010204 | 0.17081 | -0.049614 | 121.5534 | 121.5067 | 121.5253 | 0.005627 | 0.060571 | 2.7934 | -0.033458 | 121.2681 | 121.5939 | 120.8829 | -0.23741 | 0.17042 | 0.10868 | 0.175 | 0.11518 | -0.055241 | 0.061999 | 0.080595 | -0.072615 | -0.17658 | 0.22537 | 0.13134 | 0.20395 | 0.14922 | -0.56185 | 121.7182 | 121.6715 | 121.6901 | 0.33561 | -121.4391 | 121.4329 | 121.7587 | 121.0477 | 2.9582 | -121.6821
974.9688 | 121.5088 | -0.16937 | 121.4813 | 1.4211e-13 | -0.017021 | 0.0026346 | 0.067981 | -0.010784 | 0.058685 | 0.0079357 | -0.0014485 | 0.00021361 | 0.060552 | 0.028731 | 0.054018 | 0.014783 | 0.17081 | -0.049614 | 121.558 | 121.5067 | 121.5299 | 0.005627 | 0.069728 | 2.8941 | -0.028879 | 121.2681 | 121.5939 | 120.8874 | -0.24657 | 0.175 | 0.07664 | 0.18416 | 0.11976 | -0.055241 | 0.025378 | 0.048553 | -0.077194 | -0.2132 | 0.2391 | 0.14049 | 0.21769 | 0.11259 | -0.59389 | 121.7273 | 121.6761 | 121.6992 | 0.34019 | -121.4757 | 121.4375 | 121.7633 | 121.0568 | 3.0635 | -121.7279
976.6406 | 121.4859 | -0.15106 | 121.4676 | 1.4211e-13 | -0.016807 | 0.002421 | 0.067767 | -0.01057 | 0.058471 | -0.0073253 | -0.0012349 | 0.00021361 | 0.060338 | 0.028731 | 0.054232 | 0.010204 | 0.17081 | -0.054192 | 121.558 | 121.5067 | 121.5299 | 0.005627 | 0.069728 | 2.949 | -0.0243 | 121.2635 | 121.5985 | 120.9012 | -0.25572 | 0.15669 | 0.090373 | 0.16127 | 0.09687 | -0.059819 | 0.039111 | 0.062286 | -0.10466 | -0.20405 | 0.22079 | 0.12676 | 0.23142 | 0.13091 | -0.56642 | 121.709 | 121.6578 | 121.6809 | 0.32188 | -121.462 | 121.4146 | 121.7496 | 121.0522 | 3.1001 | -121.7233
978.3906 | 121.4951 | -0.16479 | 121.4813 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.068409 | -0.010784 | 0.058685 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060338 | 0.029158 | 0.053591 | 0.010204 | 0.16166 | -0.049614 | 121.5534 | 121.5113 | 121.5299 | 0.010206 | 0.069728 | 3.0269 | -0.033458 | 121.2635 | 121.5939 | 120.9607 | -0.24657 | 0.175 | 0.072062 | 0.175 | 0.11518 | -0.05982 | 0.029957 | 0.048553 | -0.081772 | -0.21778 | 0.23452 | 0.13134 | 0.21311 | 0.11259 | -0.52063 | 121.7182 | 121.6761 | 121.6947 | 0.32645 | -121.4711 | 121.4283 | 121.7587 | 121.1255 | 3.1917 | -121.7279
980.125 | 121.5317 | -0.16022 | 121.4447 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.068195 | -0.01057 | 0.058685 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060338 | 0.028944 | 0.053591 | 0.010204 | 0.16166 | -0.049614 | 121.5625 | 121.5067 | 121.5299 | 0.005627 | 0.069728 | 3.1459 | -0.0243 | 121.2635 | 121.6031 | 120.86 | -0.24657 | 0.16584 | 0.11784 | 0.17042 | 0.1106 | -0.055241 | 0.061999 | 0.085174 | -0.08635 | -0.18116 | 0.22995 | 0.13592 | 0.22227 | 0.15837 | -0.58474 | 121.7228 | 121.6669 | 121.6901 | 0.32188 | -121.4391 | 121.4238 | 121.7633 | 121.0202 | 3.3061 | -121.6913
981.7969 | 121.5271 | -0.13733 | 121.4722 | 1.4211e-13 | -0.017021 | 0.0022072 | 0.067981 | -0.01057 | 0.058685 | 0.00030522 | -0.00080746 | 1.2e-08 | 0.060125 | 0.029158 | 0.054018 | 0.014783 | 0.17081 | -0.05877 | 121.5534 | 121.5159 | 121.5299 | 0.010206 | 0.069728 | 3.1917 | -0.0243 | 121.2727 | 121.5939 | 120.9195 | -0.24199 | 0.14753 | 0.081217 | 0.15211 | 0.078559 | -0.068976 | 0.04369 | 0.057708 | -0.10466 | -0.19947 | 0.20706 | 0.11303 | 0.21769 | 0.12175 | -0.55268 | 121.6907 | 121.6532 | 121.6672 | 0.30814 | -121.462 | 121.41 | 121.7312 | 121.0568 | 3.329 | -121.7142
983.5469 | 121.5271 | -0.16479 | 121.4584 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.068195 | -0.010784 | 0.058471 | -0.0073253 | -0.0012349 | 0.00042721 | 0.060338 | 0.028944 | 0.053804 | 0.014783 | 0.17539 | -0.054192 | 121.5671 | 121.5113 | 121.539 | 0.001048 | 0.078886 | 3.297 | -0.028879 | 121.2681 | 121.5985 | 120.8691 | -0.2603 | 0.16584 | 0.10869 | 0.17958 | 0.1106 | -0.05524 | 0.052845 | 0.080598 | -0.095509 | -0.19032 | 0.24368 | 0.13592 | 0.23142 | 0.14006 | -0.58931 | 121.7319 | 121.6761 | 121.7038 | 0.34019 | -121.4574 | 121.4329 | 121.7633 | 121.0339 | 3.4618 | -121.7187
985.2812 | 121.5591 | -0.14191 | 121.4676 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.068195 | -0.01057 | 0.058685 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060766 | 0.029158 | 0.053804 | 0.005626 | 0.17081 | -0.054192 | 121.558 | 121.5067 | 121.5299 | 0.010206 | 0.069728 | 3.4115 | -0.028879 | 121.2681 | 121.5939 | 120.86 | -0.24657 | 0.15211 | 0.090373 | 0.14753 | 0.087715 | -0.064398 | 0.039111 | 0.062286 | -0.10466 | -0.19947 | 0.21164 | 0.11303 | 0.21769 | 0.12633 | -0.60763 | 121.6999 | 121.6486 | 121.6718 | 0.31272 | -121.4574 | 121.41 | 121.7358 | 121.0019 | 3.5534 | -121.7142
986.9531 | 121.6324 | -0.10529 | 121.4539 | 1.4211e-13 | -0.017235 | 0.0019936 | 0.067767 | -0.010784 | 0.058898 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060552 | 0.028944 | 0.054018 | 0.014783 | 0.17081 | -0.045036 | 121.5671 | 121.5113 | 121.539 | 0.005627 | 0.069728 | 3.5443 | -0.028879 | 121.2635 | 121.5985 | 120.8691 | -0.24199 | 0.11091 | 0.11326 | 0.12007 | 0.06025 | -0.050663 | 0.057423 | 0.085176 | -0.1367 | -0.19032 | 0.17501 | 0.076407 | 0.21311 | 0.14464 | -0.58474 | 121.6724 | 121.6166 | 121.6443 | 0.2761 | -121.4482 | 121.3688 | 121.7038 | 120.9744 | 3.6496 | -121.6958
988.625 | 121.4951 | -0.1831 | 121.463 | 1.4211e-13 | -0.017448 | 0.0019936 | 0.067981 | -0.01057 | 0.058685 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060125 | 0.028944 | 0.053804 | 0.005626 | 0.17081 | -0.045036 | 121.558 | 121.5159 | 121.5299 | 0.005627 | 0.074307 | 3.6725 | -0.033458 | 121.2681 | 121.6031 | 120.9103 | -0.24657 | 0.18873 | 0.09495 | 0.18873 | 0.13807 | -0.050663 | 0.052845 | 0.066863 | -0.063462 | -0.19489 | 0.25741 | 0.14965 | 0.21311 | 0.14006 | -0.55268 | 121.7411 | 121.699 | 121.713 | 0.35392 | -121.4574 | 121.4512 | 121.7862 | 121.0934 | 3.8556 | -121.7096
990.375 | 121.5225 | -0.14191 | 121.4722 | 1.4211e-13 | -0.017235 | 0.00178 | 0.067981 | -0.010784 | 0.059112 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060338 | 0.029158 | 0.053591 | 0.019361 | 0.17997 | -0.049614 | 121.5717 | 121.5113 | 121.539 | -0.017268 | 0.069728 | 3.8556 | -0.0243 | 121.2819 | 121.6031 | 120.9332 | -0.25115 | 0.12464 | 0.09953 | 0.16127 | 0.092293 | -0.032346 | 0.039112 | 0.066865 | -0.10924 | -0.19031 | 0.21164 | 0.11761 | 0.22685 | 0.13091 | -0.53895 | 121.7136 | 121.6532 | 121.6809 | 0.32188 | -121.4894 | 121.4238 | 121.745 | 121.0751 | 3.9975 | -121.7233
992.1094 | 121.5729 | -0.15564 | 121.4493 | 1.4211e-13 | -0.017235 | 0.0019936 | 0.067981 | -0.010356 | 0.059112 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.028944 | 0.054018 | 0.019361 | 0.16624 | -0.049614 | 121.5625 | 121.5159 | 121.5345 | 0.005627 | 0.078886 | 3.9884 | -0.0243 | 121.2681 | 121.5985 | 120.9241 | -0.24199 | 0.16127 | 0.11326 | 0.175 | 0.10603 | -0.055241 | 0.066578 | 0.085175 | -0.086349 | -0.18116 | 0.23453 | 0.13134 | 0.21769 | 0.14922 | -0.52522 | 121.7182 | 121.6715 | 121.6901 | 0.32188 | -121.4437 | 121.4238 | 121.7541 | 121.0797 | 4.1441 | -121.6913
993.8125 | 121.6003 | -0.12817 | 121.4401 | 1.4211e-13 | -0.017021 | 0.002421 | 0.068195 | -0.01057 | 0.058898 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060338 | 0.029158 | 0.053377 | 0.005626 | 0.17081 | -0.054192 | 121.558 | 121.5113 | 121.5345 | 0.005627 | 0.069728 | 4.0937 | -0.033458 | 121.2773 | 121.5939 | 120.9103 | -0.24657 | 0.1338 | 0.11784 | 0.1338 | 0.073982 | -0.059819 | 0.071155 | 0.09433 | -0.11839 | -0.16285 | 0.1979 | 0.094716 | 0.21311 | 0.15379 | -0.5298 | 121.6861 | 121.6395 | 121.6626 | 0.29899 | -121.4345 | 121.4055 | 121.7221 | 121.0385 | 4.2219 | -121.6867
995.5469 | 121.5042 | -0.17853 | 121.4493 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.067981 | -0.01057 | 0.058898 | -0.0073253 | -0.0012349 | 0.00042721 | 0.060338 | 0.028944 | 0.053591 | 0.014783 | 0.17539 | -0.045036 | 121.558 | 121.5159 | 121.5345 | 0.001048 | 0.083464 | 4.2265 | -0.0243 | 121.2727 | 121.6077 | 120.9103 | -0.24657 | 0.17958 | 0.10868 | 0.19331 | 0.13349 | -0.046084 | 0.066578 | 0.085175 | -0.068039 | -0.17658 | 0.26199 | 0.15423 | 0.22227 | 0.15837 | -0.53895 | 121.7365 | 121.6944 | 121.713 | 0.35392 | -121.4482 | 121.4512 | 121.7862 | 121.0889 | 4.405 | -121.6958
997.2344 | 121.4676 | -0.16022 | 121.4951 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.067981 | -0.010784 | 0.058471 | 0.015566 | -0.0012349 | 0.00042721 | 0.060552 | 0.029158 | 0.053804 | 0.014783 | 0.16624 | -0.049614 | 121.5625 | 121.5204 | 121.5345 | 0.005627 | 0.069728 | 4.3822 | -0.028879 | 121.2681 | 121.6031 | 121.0706 | -0.25572 | 0.16584 | 0.067486 | 0.175 | 0.1106 | -0.055241 | 0.025381 | 0.039399 | -0.095508 | -0.22694 | 0.22995 | 0.13134 | 0.22685 | 0.10802 | -0.42448 | 121.7228 | 121.6807 | 121.6947 | 0.32645 | -121.4894 | 121.4283 | 121.7633 | 121.2308 | 4.5424 | -121.7508
998.9844 | 121.6278 | -0.11902 | 121.431 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.067767 | -0.01057 | 0.058685 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.029372 | 0.054018 | 0.005626 | 0.17081 | -0.049614 | 121.558 | 121.5159 | 121.5436 | 0.010206 | 0.088043 | 4.5608 | -0.0243 | 121.2681 | 121.6077 | 120.9103 | -0.25115 | 0.12923 | 0.12699 | 0.12465 | 0.069405 | -0.05982 | 0.084889 | 0.11264 | -0.13213 | -0.16285 | 0.20706 | 0.094719 | 0.22685 | 0.17668 | -0.52064 | 121.677 | 121.6349 | 121.6626 | 0.28983 | -121.4208 | 121.3871 | 121.7267 | 121.0293 | 4.6798 | -121.6821
1000.7188 | 121.5408 | -0.15564 | 121.4813 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.068195 | -0.010784 | 0.058898 | 0.00030522 | -0.0014485 | 1.2e-08 | 0.060552 | 0.028944 | 0.054018 | 0.010204 | 0.17081 | -0.049614 | 121.558 | 121.5159 | 121.5436 | 0.001048 | 0.083464 | 4.7302 | -0.0243 | 121.2681 | 121.6077 | 121.0706 | -0.25115 | 0.15669 | 0.07664 | 0.16584 | 0.10603 | -0.050662 | 0.034535 | 0.062289 | -0.095506 | -0.2132 | 0.2391 | 0.13134 | 0.22685 | 0.12633 | -0.41074 | 121.7136 | 121.6715 | 121.6993 | 0.32645 | -121.4803 | 121.4238 | 121.7633 | 121.2262 | 4.8858 | -121.7325
1002.4688 | 121.5866 | -0.12817 | 121.4355 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.067981 | -0.010784 | 0.058685 | 0.0079357 | -0.0014485 | 0.00064101 | 0.060125 | 0.028944 | 0.053804 | 0.010204 | 0.17539 | -0.05877 | 121.5625 | 121.5067 | 121.539 | -0.003531 | 0.083464 | 4.8721 | -0.0243 | 121.2681 | 121.6031 | 120.947 | -0.24657 | 0.12464 | 0.12699 | 0.13838 | 0.069404 | -0.055239 | 0.071154 | 0.10349 | -0.11839 | -0.16743 | 0.21164 | 0.10387 | 0.22227 | 0.16753 | -0.48859 | 121.6907 | 121.6349 | 121.6672 | 0.30357 | -121.4391 | 121.3963 | 121.7312 | 121.0751 | 5.0003 | -121.6821
1004.2188 | 121.5179 | -0.16937 | 121.4676 | 1.4211e-13 | -0.017235 | 0.0019936 | 0.067554 | -0.010784 | 0.058471 | 0.00030522 | -0.0012349 | 1.2e-08 | 0.060552 | 0.029372 | 0.053804 | 0.005626 | 0.17539 | -0.054192 | 121.5671 | 121.5159 | 121.539 | -0.021847 | 0.083464 | 4.9591 | -0.015143 | 121.2727 | 121.5985 | 120.9515 | -0.24657 | 0.14753 | 0.09953 | 0.175 | 0.11518 | -0.032345 | 0.048268 | 0.071443 | -0.077194 | -0.19489 | 0.25284 | 0.15423 | 0.23142 | 0.13091 | -0.51605 | 121.7365 | 121.6852 | 121.7084 | 0.34477 | -121.4894 | 121.4421 | 121.7679 | 121.1209 | 5.1285 | -121.7142
1005.9062 | 121.5271 | -0.16479 | 121.4813 | 1.4211e-13 | -0.017021 | 0.0022072 | 0.068195 | -0.01057 | 0.059112 | 0.00030522 | -0.0016621 | 0.00042721 | 0.060125 | 0.029158 | 0.054018 | 0.005626 | 0.17539 | -0.045036 | 121.5625 | 121.5159 | 121.5436 | 0.001048 | 0.078886 | 5.1194 | -0.0243 | 121.2773 | 121.6031 | 120.9378 | -0.25115 | 0.16584 | 0.081219 | 0.17042 | 0.11976 | -0.046084 | 0.034535 | 0.062289 | -0.086351 | -0.20405 | 0.24368 | 0.1405 | 0.22685 | 0.12175 | -0.54352 | 121.7273 | 121.6807 | 121.7084 | 0.34019 | -121.4803 | 121.4421 | 121.7679 | 121.1026 | 5.2842 | -121.7325
1007.6406 | 121.5225 | -0.15564 | 121.4813 | 1.4211e-13 | -0.017021 | 0.00178 | 0.067767 | -0.01057 | 0.058685 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060125 | 0.029158 | 0.053804 | 0.014783 | 0.17997 | -0.054192 | 121.5671 | 121.5159 | 121.5345 | 0.001048 | 0.092622 | 5.2476 | -0.019721 | 121.2819 | 121.6077 | 120.8737 | -0.24657 | 0.15669 | 0.085797 | 0.17042 | 0.10145 | -0.05524 | 0.034535 | 0.053132 | -0.090927 | -0.19947 | 0.24826 | 0.13592 | 0.22685 | 0.12633 | -0.60762 | 121.7228 | 121.6715 | 121.6901 | 0.33561 | -121.4803 | 121.4375 | 121.7633 | 121.0293 | 5.4032 | -121.7279
1009.3906 | 121.5729 | -0.14191 | 121.4813 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.067981 | -0.011211 | 0.059112 | 0.015566 | -0.0012349 | 0.00021361 | 0.060125 | 0.028944 | 0.053804 | 0.005626 | 0.17539 | -0.05877 | 121.5671 | 121.5159 | 121.5345 | 0.005627 | 0.092622 | 5.5177 | -0.019721 | 121.2681 | 121.6122 | 121.034 | -0.2603 | 0.14753 | 0.085797 | 0.14753 | 0.083137 | -0.064397 | 0.034535 | 0.053132 | -0.1184 | -0.2132 | 0.23453 | 0.12219 | 0.24058 | 0.13091 | -0.44737 | 121.709 | 121.6578 | 121.6764 | 0.3173 | -121.4757 | 121.41 | 121.7541 | 121.1759 | 5.6596 | -121.7416
1011.0625 | 121.5775 | -0.11902 | 121.463 | 1.4211e-13 | -0.016807 | 0.0022072 | 0.067981 | -0.010356 | 0.058685 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060552 | 0.028944 | 0.053804 | 0.005626 | 0.17539 | -0.054192 | 121.5671 | 121.5204 | 121.5436 | 0.001048 | 0.092622 | 5.765 | -0.0243 | 121.2819 | 121.6077 | 120.9241 | -0.24199 | 0.12007 | 0.10411 | 0.12465 | 0.064827 | -0.05524 | 0.057424 | 0.080599 | -0.12297 | -0.18116 | 0.21164 | 0.094719 | 0.21769 | 0.14464 | -0.53895 | 121.6861 | 121.6395 | 121.6626 | 0.29441 | -121.462 | 121.4009 | 121.7267 | 121.0431 | 5.884 | -121.705
1012.7969 | 121.6278 | -0.10986 | 121.4355 | 1.4211e-13 | -0.017235 | 0.0022072 | 0.067981 | -0.010784 | 0.058685 | 0.015566 | -0.0014485 | 0.00021361 | 0.060125 | 0.029372 | 0.053591 | 0.005626 | 0.17997 | -0.05877 | 121.558 | 121.5159 | 121.5436 | 0.001048 | 0.097201 | 5.9115 | -0.015143 | 121.2727 | 121.6031 | 120.9012 | -0.25115 | 0.11091 | 0.12242 | 0.11549 | 0.051093 | -0.059818 | 0.080311 | 0.10806 | -0.14128 | -0.16285 | 0.20706 | 0.09472 | 0.236 | 0.16753 | -0.53437 | 121.6678 | 121.6257 | 121.6535 | 0.28984 | -121.4345 | 121.3826 | 121.7129 | 121.011 | 6.0213 | -121.6867
1014.5469 | 121.5363 | -0.17853 | 121.4813 | 1.4211e-13 | -0.017021 | 0.002421 | 0.067981 | -0.010784 | 0.058471 | -0.0073253 | -0.0012349 | 0.00021361 | 0.060338 | 0.029158 | 0.053804 | 0.014783 | 0.18455 | -0.054192 | 121.5671 | 121.525 | 121.539 | 0.001048 | 0.10178 | 6.1175 | -0.015143 | 121.2773 | 121.6077 | 121.0065 | -0.24657 | 0.17958 | 0.085797 | 0.19331 | 0.12434 | -0.05524 | 0.043693 | 0.05771 | -0.068039 | -0.20405 | 0.28031 | 0.16339 | 0.23142 | 0.12633 | -0.47484 | 121.7456 | 121.7035 | 121.7176 | 0.36308 | -121.4803 | 121.4558 | 121.7862 | 121.185 | 6.296 | -121.7279
1016.2344 | 121.5958 | -0.12817 | 121.4172 | 1.4211e-13 | -0.017448 | 0.0022072 | 0.067981 | -0.010784 | 0.058471 | -0.0073253 | -0.0010211 | 0.00021361 | 0.060338 | 0.029158 | 0.053591 | 0.005626 | 0.17081 | -0.05877 | 121.5717 | 121.5204 | 121.539 | 0.001048 | 0.10178 | 6.2961 | -0.015143 | 121.2681 | 121.6122 | 120.9103 | -0.25572 | 0.12922 | 0.15446 | 0.1338 | 0.069404 | -0.059818 | 0.1032 | 0.1218 | -0.12755 | -0.14912 | 0.22995 | 0.11303 | 0.24058 | 0.195 | -0.50691 | 121.6999 | 121.6486 | 121.6672 | 0.29899 | -121.4162 | 121.3963 | 121.7404 | 121.0385 | 6.4243 | -121.673
1017.9688 | 121.4996 | -0.16479 | 121.4722 | 1.4211e-13 | -0.017235 | 0.0015662 | 0.067981 | -0.010997 | 0.058898 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.028944 | 0.053804 | 0.001048 | 0.16624 | -0.054192 | 121.5671 | 121.5204 | 121.5482 | 0.001048 | 0.097201 | 6.5021 | -0.015143 | 121.2727 | 121.6031 | 120.9241 | -0.24657 | 0.16584 | 0.094952 | 0.16584 | 0.1106 | -0.05524 | 0.048269 | 0.076022 | -0.081772 | -0.19947 | 0.262 | 0.14965 | 0.23142 | 0.13091 | -0.5481 | 121.7319 | 121.6852 | 121.713 | 0.33103 | -121.4711 | 121.4375 | 121.7679 | 121.0889 | 6.6669 | -121.7187
1019.7188 | 121.4722 | -0.15564 | 121.4813 | 1.4211e-13 | -0.017021 | 0.0019936 | 0.068195 | -0.010784 | 0.058898 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060766 | 0.029158 | 0.053804 | 0.019361 | 0.17539 | -0.05877 | 121.5717 | 121.5204 | 121.5436 | 0.001048 | 0.10636 | 6.9966 | -0.015143 | 121.2727 | 121.6077 | 120.9699 | -0.25115 | 0.15669 | 0.090375 | 0.175 | 0.09687 | -0.059818 | 0.039114 | 0.062289 | -0.095506 | -0.20863 | 0.262 | 0.1405 | 0.236 | 0.12633 | -0.51147 | 121.7273 | 121.6761 | 121.6993 | 0.33103 | -121.4803 | 121.4283 | 121.7633 | 121.1255 | 7.1523 | -121.7325
1021.4688 | 121.6232 | -0.11444 | 121.4355 | 1.4211e-13 | -0.017448 | 0.0019936 | 0.067981 | -0.010784 | 0.058685 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060766 | 0.028944 | 0.054018 | 0.010204 | 0.17081 | -0.045036 | 121.5671 | 121.5204 | 121.5436 | 0.010206 | 0.10636 | 7.1386 | -0.015143 | 121.2773 | 121.6077 | 120.9332 | -0.25115 | 0.12465 | 0.13157 | 0.12465 | 0.069405 | -0.055242 | 0.08489 | 0.10806 | -0.1367 | -0.15827 | 0.2208 | 0.099298 | 0.236 | 0.17211 | -0.50232 | 121.6816 | 121.6349 | 121.6581 | 0.28526 | -121.4253 | 121.3917 | 121.7221 | 121.0477 | 7.253 | -121.6867
1023.1406 | 121.5042 | -0.17395 | 121.4539 | 1.4211e-13 | -0.017235 | 0.0019936 | 0.067767 | -0.010784 | 0.058898 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060338 | 0.029372 | 0.053804 | 0.010204 | 0.17539 | -0.049614 | 121.5717 | 121.5296 | 121.5482 | 0.005627 | 0.10636 | 7.253 | -0.010564 | 121.2727 | 121.6122 | 120.9561 | -0.24657 | 0.17958 | 0.11784 | 0.18415 | 0.12434 | -0.055241 | 0.075738 | 0.094333 | -0.072617 | -0.18116 | 0.28031 | 0.16339 | 0.236 | 0.15838 | -0.49774 | 121.7456 | 121.7035 | 121.7221 | 0.34934 | -121.4482 | 121.4466 | 121.7862 | 121.1301 | 7.427 | -121.7004
1024.875 | 121.4951 | -0.16022 | 121.4722 | 1.4211e-13 | -0.017235 | 0.0022072 | 0.067981 | -0.01057 | 0.058898 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060338 | 0.029372 | 0.053804 | 0.010204 | 0.17081 | -0.049614 | 121.5671 | 121.5204 | 121.5482 | 0.005627 | 0.11094 | 7.5323 | -0.005985 | 121.2773 | 121.6077 | 120.8874 | -0.25115 | 0.16584 | 0.094952 | 0.17042 | 0.1106 | -0.055241 | 0.048269 | 0.076022 | -0.090929 | -0.19489 | 0.27115 | 0.15423 | 0.24516 | 0.13549 | -0.58473 | 121.7273 | 121.6807 | 121.7084 | 0.33103 | -121.4665 | 121.4375 | 121.7679 | 121.0477 | 7.6926 | -121.7233
1026.6094 | 121.5775 | -0.1236 | 121.4493 | 1.4211e-13 | -0.017448 | 0.0022072 | 0.067981 | -0.01057 | 0.058898 | -0.0073253 | -0.0014485 | 0.00021361 | 0.060338 | 0.029158 | 0.053591 | 0.010204 | 0.17539 | -0.049614 | 121.5717 | 121.5204 | 121.5436 | 0.001048 | 0.12009 | 7.7292 | -0.005985 | 121.2819 | 121.6122 | 120.9607 | -0.24657 | 0.12464 | 0.12242 | 0.1338 | 0.073982 | -0.050662 | 0.071157 | 0.094332 | -0.12297 | -0.16743 | 0.24369 | 0.11761 | 0.24058 | 0.16295 | -0.48859 | 121.6953 | 121.644 | 121.6672 | 0.29899 | -121.4482 | 121.4055 | 121.7358 | 121.0843 | 7.8528 | -121.6958
1028.2969 | 121.5134 | -0.16479 | 121.4905 | 1.4211e-13 | -0.017448 | 0.0022072 | 0.067981 | -0.010997 | 0.058685 | 0.0079357 | -0.0010211 | 1.2e-08 | 0.060125 | 0.029158 | 0.053804 | 0.005626 | 0.17081 | -0.049614 | 121.5671 | 121.5204 | 121.5482 | 0.001048 | 0.12009 | 7.7704 | -0.015143 | 121.2819 | 121.6031 | 120.8645 | -0.24199 | 0.16584 | 0.076641 | 0.17042 | 0.11518 | -0.050662 | 0.029958 | 0.057711 | -0.077194 | -0.20862 | 0.28489 | 0.14965 | 0.22685 | 0.1126 | -0.62594 | 121.7319 | 121.6852 | 121.713 | 0.33561 | -121.4894 | 121.4466 | 121.7679 | 121.0293 | 7.9352 | -121.7325
1030.0469 | 121.5088 | -0.1831 | 121.4905 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.067981 | -0.010784 | 0.058685 | 0.00030522 | -0.0010211 | 0.00064101 | 0.060552 | 0.028944 | 0.053591 | 0.010204 | 0.17539 | -0.054192 | 121.5671 | 121.5296 | 121.5436 | 0.005627 | 0.12467 | 7.8895 | -0.001407 | 121.2864 | 121.6031 | 120.9424 | -0.24657 | 0.18873 | 0.076641 | 0.19331 | 0.12891 | -0.059819 | 0.039116 | 0.053133 | -0.063462 | -0.20405 | 0.30778 | 0.1817 | 0.24516 | 0.1126 | -0.5481 | 121.7502 | 121.7127 | 121.7267 | 0.3585 | -121.4849 | 121.4695 | 121.7862 | 121.1255 | 8.0726 | -121.737
1031.7969 | 121.5637 | -0.13275 | 121.4584 | 1.4211e-13 | -0.017448 | 0.0022072 | 0.068195 | -0.010997 | 0.058685 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060125 | 0.029372 | 0.053804 | 0.005626 | 0.17997 | -0.054192 | 121.5717 | 121.525 | 121.5482 | 0.005627 | 0.12467 | 7.981 | -0.001407 | 121.2864 | 121.6031 | 121.034 | -0.24657 | 0.13838 | 0.11326 | 0.13838 | 0.078559 | -0.059819 | 0.066581 | 0.089755 | -0.11382 | -0.172 | 0.25742 | 0.13134 | 0.24516 | 0.14464 | -0.42448 | 121.7044 | 121.6578 | 121.6809 | 0.31272 | -121.4528 | 121.4192 | 121.7358 | 121.1667 | 8.1138 | -121.705
1033.5469 | 121.4996 | -0.16022 | 121.4813 | 1.4211e-13 | -0.017235 | 0.0022072 | 0.067981 | -0.010784 | 0.058685 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060125 | 0.029158 | 0.053591 | 0.014783 | 0.17997 | -0.049614 | 121.5717 | 121.5296 | 121.5436 | 0.005627 | 0.12925 | 8.1688 | -0.001407 | 121.2819 | 121.6168 | 120.9332 | -0.25115 | 0.16584 | 0.090375 | 0.175 | 0.1106 | -0.055241 | 0.048272 | 0.062289 | -0.090929 | -0.19947 | 0.28947 | 0.15881 | 0.24974 | 0.13549 | -0.5481 | 121.7319 | 121.6898 | 121.7038 | 0.34019 | -121.4757 | 121.4421 | 121.777 | 121.0934 | 8.329 | -121.7325
1035.2344 | 121.6278 | -0.10986 | 121.4218 | 1.4211e-13 | -0.017235 | 0.0015662 | 0.068409 | -0.01057 | 0.058471 | 0.015566 | -0.0012349 | 0.00021361 | 0.060338 | 0.029158 | 0.053804 | 0.005626 | 0.17539 | -0.05877 | 121.5717 | 121.5296 | 121.5482 | 0.001048 | 0.12925 | 8.242 | 0.003172 | 121.2864 | 121.6122 | 120.9653 | -0.25115 | 0.11091 | 0.14988 | 0.11549 | 0.051093 | -0.059818 | 0.10778 | 0.12638 | -0.14128 | -0.13538 | 0.23911 | 0.11303 | 0.25432 | 0.19042 | -0.45654 | 121.6816 | 121.6395 | 121.6581 | 0.28526 | -121.4208 | 121.3963 | 121.7221 | 121.0751 | 8.3519 | -121.673
1036.9688 | 121.5454 | -0.15564 | 121.4722 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.067981 | -0.010997 | 0.058898 | 0.0079357 | -0.0016621 | 0.00042721 | 0.060552 | 0.029372 | 0.053804 | 0.014783 | 0.17539 | -0.054192 | 121.5671 | 121.5296 | 121.5528 | -0.003531 | 0.13383 | 8.2054 | 0.003172 | 121.2819 | 121.6031 | 121.0935 | -0.25115 | 0.15211 | 0.094952 | 0.17042 | 0.10145 | -0.050661 | 0.057427 | 0.080601 | -0.095506 | -0.19031 | 0.28947 | 0.15881 | 0.25432 | 0.13091 | -0.37869 | 121.7228 | 121.6852 | 121.7084 | 0.33103 | -121.4757 | 121.4375 | 121.7587 | 121.2491 | 8.361 | -121.7233
1038.6562 | 121.6141 | -0.14191 | 121.4264 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.067981 | -0.010784 | 0.058471 | 0.0079357 | -0.0012349 | 0.00021361 | 0.060338 | 0.028731 | 0.053804 | 0.010204 | 0.17539 | -0.054192 | 121.5671 | 121.525 | 121.5436 | -0.003531 | 0.13383 | 8.3199 | 0.003172 | 121.2773 | 121.6031 | 121.1118 | -0.25572 | 0.13838 | 0.14073 | 0.15211 | 0.087715 | -0.050661 | 0.098624 | 0.11722 | -0.11382 | -0.14912 | 0.27574 | 0.14508 | 0.2589 | 0.17668 | -0.31461 | 121.709 | 121.6669 | 121.6855 | 0.3173 | -121.4299 | 121.4192 | 121.745 | 121.2537 | 8.4618 | -121.6821
1040.4062 | 121.6095 | -0.11444 | 121.4447 | 1.4211e-13 | -0.017448 | 0.0022072 | 0.067981 | -0.010784 | 0.058471 | 0.015566 | -0.0012349 | 0.00042721 | 0.060766 | 0.029372 | 0.053591 | 0.014783 | 0.17081 | -0.05877 | 121.5671 | 121.5296 | 121.5528 | 0.001048 | 0.13841 | 8.416 | -0.001407 | 121.2864 | 121.6031 | 120.9103 | -0.25572 | 0.11549 | 0.12242 | 0.12922 | 0.055671 | -0.059818 | 0.084893 | 0.10807 | -0.14128 | -0.15827 | 0.25285 | 0.11303 | 0.25432 | 0.15837 | -0.53437 | 121.6816 | 121.644 | 121.6672 | 0.28526 | -121.4437 | 121.4009 | 121.7175 | 121.0248 | 8.5305 | -121.7004
1042.1406 | 121.5912 | -0.14191 | 121.4722 | 1.4211e-13 | -0.017448 | 0.0022072 | 0.068195 | -0.010784 | 0.058898 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060125 | 0.029158 | 0.053591 | 0.010204 | 0.17081 | -0.054192 | 121.5763 | 121.5159 | 121.5528 | 0.005627 | 0.14299 | 8.471 | -0.005985 | 121.2773 | 121.6122 | 120.9515 | -0.25115 | 0.14753 | 0.10411 | 0.15211 | 0.087715 | -0.059819 | 0.04369 | 0.080601 | -0.10924 | -0.19489 | 0.2849 | 0.13592 | 0.24516 | 0.14006 | -0.52063 | 121.7182 | 121.6578 | 121.6947 | 0.31272 | -121.4665 | 121.4192 | 121.7541 | 121.0934 | 8.6129 | -121.7233
1043.8906 | 121.5408 | -0.13733 | 121.4676 | 1.4211e-13 | -0.017448 | 0.0019936 | 0.067981 | -0.010784 | 0.058685 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060552 | 0.029372 | 0.053591 | 0.010204 | 0.18455 | -0.054192 | 121.5671 | 121.5204 | 121.5528 | 0.005627 | 0.14299 | 8.5488 | 0.003172 | 121.2727 | 121.6122 | 121.0065 | -0.24657 | 0.14296 | 0.09953 | 0.14753 | 0.083137 | -0.059819 | 0.052847 | 0.085179 | -0.10924 | -0.19489 | 0.28032 | 0.1405 | 0.24974 | 0.14464 | -0.46111 | 121.7044 | 121.6578 | 121.6901 | 0.32188 | -121.462 | 121.41 | 121.7496 | 121.1438 | 8.6861 | -121.7142
1045.6094 | 121.5179 | -0.16937 | 121.5042 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.067981 | -0.010997 | 0.059112 | 0.00030522 | -0.0012349 | 0.00064101 | 0.060552 | 0.029372 | 0.053804 | 0.010204 | 0.17997 | -0.054192 | 121.5717 | 121.525 | 121.5482 | -0.021847 | 0.13841 | 8.5717 | -0.001407 | 121.2864 | 121.5985 | 120.9836 | -0.25572 | 0.14753 | 0.067487 | 0.17958 | 0.11518 | -0.032345 | 0.020805 | 0.043979 | -0.086352 | -0.21778 | 0.30778 | 0.16797 | 0.25432 | 0.094285 | -0.52062 | 121.7411 | 121.6944 | 121.7176 | 0.34935 | -121.5261 | 121.4558 | 121.7679 | 121.153 | 8.7411 | -121.7599
1047.2969 | 121.5134 | -0.15564 | 121.4767 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.068195 | -0.010784 | 0.058898 | 0.0079357 | -0.00080746 | 0.00042721 | 0.060338 | 0.029372 | 0.053804 | 0.014783 | 0.17539 | -0.05877 | 121.5717 | 121.5204 | 121.5528 | 0.010206 | 0.14299 | 8.7091 | -0.001407 | 121.2819 | 121.6077 | 120.947 | -0.25572 | 0.16585 | 0.094952 | 0.17042 | 0.09687 | -0.068976 | 0.043691 | 0.076023 | -0.10008 | -0.19489 | 0.29863 | 0.15423 | 0.25432 | 0.13091 | -0.52979 | 121.7273 | 121.6761 | 121.7084 | 0.33103 | -121.4665 | 121.4375 | 121.7633 | 121.1026 | 8.8647 | -121.7325
1049.0469 | 121.6278 | -0.12817 | 121.4035 | 1.4211e-13 | -0.017235 | 0.00178 | 0.067981 | -0.010784 | 0.058898 | 0.015566 | -0.0010211 | 0.00021361 | 0.060338 | 0.029372 | 0.053591 | 0.005626 | 0.17081 | -0.049614 | 121.5717 | 121.5296 | 121.5482 | -0.003531 | 0.15672 | 8.7686 | 0.007751 | 121.2727 | 121.6168 | 120.8691 | -0.25115 | 0.12464 | 0.16819 | 0.1338 | 0.07856 | -0.046083 | 0.12609 | 0.14469 | -0.12297 | -0.13081 | 0.2849 | 0.13593 | 0.2589 | 0.21331 | -0.53438 | 121.6999 | 121.6578 | 121.6764 | 0.29899 | -121.407 | 121.4009 | 121.745 | 120.9973 | 8.8968 | -121.6546
1050.7344 | 121.5958 | -0.11902 | 121.4355 | 1.4211e-13 | -0.017448 | 0.0019936 | 0.067767 | -0.010356 | 0.058685 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060338 | 0.029372 | 0.053591 | 0.005626 | 0.16624 | -0.049614 | 121.5671 | 121.525 | 121.5482 | -0.021847 | 0.15215 | 8.8327 | 0.007751 | 121.2819 | 121.6031 | 120.9241 | -0.24657 | 0.097172 | 0.13157 | 0.12465 | 0.069405 | -0.027767 | 0.089469 | 0.11264 | -0.12755 | -0.15369 | 0.27116 | 0.12677 | 0.25432 | 0.16753 | -0.51148 | 121.6861 | 121.644 | 121.6672 | 0.28525 | -121.4574 | 121.4009 | 121.7221 | 121.0431 | 8.9517 | -121.6821
1052.4844 | 121.6141 | -0.1236 | 121.4493 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.068195 | -0.010784 | 0.058471 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060338 | 0.029372 | 0.053804 | 0.010204 | 0.17539 | -0.054192 | 121.5671 | 121.525 | 121.5482 | -0.00811 | 0.15672 | 8.8739 | 0.01233 | 121.2864 | 121.6077 | 121.0156 | -0.24657 | 0.11549 | 0.11784 | 0.1338 | 0.069404 | -0.046082 | 0.075736 | 0.09891 | -0.12297 | -0.16285 | 0.28032 | 0.13593 | 0.2589 | 0.15837 | -0.43364 | 121.6907 | 121.6486 | 121.6718 | 0.29899 | -121.4574 | 121.41 | 121.7313 | 121.1392 | 8.9975 | -121.6958
1054.2344 | 121.5546 | -0.15564 | 121.4905 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.068195 | -0.010997 | 0.058898 | 0.00030522 | -0.0012349 | 0.00021361 | 0.060125 | 0.029372 | 0.054018 | 0.014783 | 0.17997 | -0.05877 | 121.5717 | 121.525 | 121.5573 | 0.005627 | 0.1613 | 9.025 | 0.01233 | 121.2819 | 121.6077 | 121.0248 | -0.25115 | 0.16127 | 0.081219 | 0.17042 | 0.09687 | -0.064397 | 0.034537 | 0.066869 | -0.095506 | -0.20862 | 0.31694 | 0.16797 | 0.26348 | 0.11718 | -0.46568 | 121.7273 | 121.6807 | 121.713 | 0.33561 | -121.4849 | 121.4375 | 121.7633 | 121.1804 | 9.1806 | -121.7416
1055.9062 | 121.5866 | -0.13733 | 121.4584 | 1.4211e-13 | -0.017662 | 0.002421 | 0.067554 | -0.010784 | 0.058257 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060338 | 0.029372 | 0.054018 | 0.014783 | 0.17997 | -0.049614 | 121.5671 | 121.525 | 121.5528 | 0.005627 | 0.16588 | 8.9792 | 0.016908 | 121.2819 | 121.6122 | 120.9973 | -0.25115 | 0.14296 | 0.10869 | 0.15211 | 0.087715 | -0.055241 | 0.066581 | 0.094334 | -0.11382 | -0.17658 | 0.30321 | 0.15424 | 0.26805 | 0.1538 | -0.46111 | 121.7044 | 121.6623 | 121.6901 | 0.3173 | -121.4528 | 121.4192 | 121.7496 | 121.1347 | 9.1165 | -121.7096
1057.6406 | 121.5912 | -0.11444 | 121.4264 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.067981 | -0.01057 | 0.058898 | 0.00030522 | -0.0010211 | 0.00021361 | 0.060338 | 0.029158 | 0.053804 | 0.014783 | 0.18455 | -0.049614 | 121.5717 | 121.5296 | 121.5528 | 0.001048 | 0.16588 | 9.0342 | 0.01233 | 121.2819 | 121.6122 | 120.9241 | -0.25115 | 0.11549 | 0.14531 | 0.12922 | 0.064827 | -0.050662 | 0.1032 | 0.12638 | -0.1367 | -0.14454 | 0.28032 | 0.12677 | 0.26348 | 0.18584 | -0.50233 | 121.6861 | 121.644 | 121.6672 | 0.29899 | -121.4253 | 121.3963 | 121.7267 | 121.0385 | 9.1486 | -121.6775
1059.3281 | 121.5408 | -0.16479 | 121.4722 | 1.4211e-13 | -0.017876 | 0.00178 | 0.067554 | -0.010784 | 0.058685 | 0.00030522 | -0.00080746 | 0.00064101 | 0.060338 | 0.029372 | 0.054018 | 0.005626 | 0.17997 | -0.054192 | 121.5717 | 121.525 | 121.5482 | 0.005627 | 0.16588 | 9.0616 | 0.01233 | 121.2773 | 121.6214 | 120.9149 | -0.25115 | 0.17042 | 0.09953 | 0.17042 | 0.1106 | -0.059819 | 0.052848 | 0.076022 | -0.086351 | -0.19489 | 0.33068 | 0.17713 | 0.26348 | 0.14922 | -0.55726 | 121.7365 | 121.6898 | 121.713 | 0.34477 | -121.4665 | 121.4421 | 121.7862 | 121.0797 | 9.2264 | -121.7233
1061.0781 | 121.5637 | -0.14648 | 121.4493 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.068195 | -0.010997 | 0.058471 | 0.00030522 | -0.0010211 | 1.2e-08 | 0.060552 | 0.029372 | 0.053804 | 0.001048 | 0.16624 | -0.063349 | 121.5625 | 121.525 | 121.5528 | -0.003531 | 0.16588 | 9.057 | 0.01233 | 121.2819 | 121.6077 | 120.9241 | -0.25572 | 0.14295 | 0.11326 | 0.14753 | 0.083135 | -0.059818 | 0.075736 | 0.10349 | -0.10924 | -0.16743 | 0.31237 | 0.15881 | 0.26805 | 0.15837 | -0.52522 | 121.709 | 121.6715 | 121.6993 | 0.31272 | -121.4528 | 121.4283 | 121.7541 | 121.0705 | 9.2035 | -121.705
1062.7656 | 121.6187 | -0.13275 | 121.4676 | 1.4211e-13 | -0.017448 | 0.0019936 | 0.067554 | -0.010997 | 0.058898 | 0.0079357 | -0.0012349 | 0.00064101 | 0.060125 | 0.029585 | 0.053591 | 0.010204 | 0.17997 | -0.054192 | 121.5671 | 121.525 | 121.5482 | 0.010206 | 0.17046 | 9.2402 | 0.01233 | 121.2773 | 121.6077 | 120.9515 | -0.2603 | 0.14296 | 0.09953 | 0.14295 | 0.078559 | -0.064398 | 0.057426 | 0.0806 | -0.12755 | -0.19031 | 0.30321 | 0.14508 | 0.27263 | 0.14006 | -0.51605 | 121.6999 | 121.6578 | 121.6809 | 0.31272 | -121.4574 | 121.41 | 121.7404 | 121.0843 | 9.3729 | -121.7279
1064.5156 | 121.5271 | -0.15106 | 121.4722 | 1.4211e-13 | -0.017876 | 0.0022072 | 0.067554 | -0.01057 | 0.058471 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060552 | 0.029158 | 0.054018 | 0.001048 | 0.17081 | -0.05877 | 121.5625 | 121.5296 | 121.5619 | -0.003531 | 0.17962 | 9.4233 | 0.016908 | 121.2727 | 121.6122 | 120.9744 | -0.25115 | 0.14753 | 0.090374 | 0.15211 | 0.092292 | -0.055239 | 0.057427 | 0.089758 | -0.10008 | -0.19947 | 0.33068 | 0.16797 | 0.26805 | 0.14006 | -0.49774 | 121.7136 | 121.6807 | 121.713 | 0.32188 | -121.4757 | 121.4238 | 121.7633 | 121.1255 | 9.5744 | -121.7233
1066.2656 | 121.4951 | -0.16937 | 121.4584 | 1.4211e-13 | -0.018089 | 0.0019936 | 0.067981 | -0.010997 | 0.059112 | 0.0079357 | -0.0012349 | 1.2e-08 | 0.060338 | 0.029585 | 0.053804 | 0.005626 | 0.17539 | -0.05877 | 121.558 | 121.5159 | 121.5482 | -0.040163 | 0.1842 | 9.8171 | 0.016908 | 121.2819 | 121.6031 | 120.9744 | -0.25115 | 0.12921 | 0.099528 | 0.175 | 0.1106 | -0.018607 | 0.057423 | 0.089755 | -0.081773 | -0.17658 | 0.35357 | 0.18628 | 0.26805 | 0.14464 | -0.48401 | 121.7273 | 121.6852 | 121.7176 | 0.34477 | -121.4986 | 121.4512 | 121.7724 | 121.1438 | 9.9865 | -121.7096
1067.9375 | 121.4859 | -0.17853 | 121.4401 | 1.4211e-13 | -0.017876 | 0.002421 | 0.067981 | -0.010997 | 0.058471 | 0.00030522 | -0.0010211 | 0.00064101 | 0.060125 | 0.029372 | 0.053804 | 0.001048 | 0.17081 | -0.05877 | 121.558 | 121.5067 | 121.539 | -0.00811 | 0.1842 | 10.0369 | 0.016908 | 121.2681 | 121.5939 | 120.9515 | -0.2603 | 0.17042 | 0.11784 | 0.17958 | 0.11976 | -0.05066 | 0.066576 | 0.098908 | -0.081776 | -0.17201 | 0.36272 | 0.19544 | 0.27721 | 0.15379 | -0.48859 | 121.7365 | 121.6852 | 121.7176 | 0.34934 | -121.4482 | 121.4466 | 121.7724 | 121.1301 | 10.2154 | -121.7004
1069.6875 | 121.6095 | -0.14648 | 121.4539 | 1.4211e-13 | -0.018089 | 0.00178 | 0.068195 | -0.011425 | 0.058898 | 0.0079357 | -0.0012349 | 0.00042721 | 0.060338 | 0.029585 | 0.053804 | -0.003531 | 0.17997 | -0.063349 | 121.5534 | 121.5067 | 121.5345 | -0.021847 | 0.1842 | 10.4352 | 0.016908 | 121.2773 | 121.5848 | 120.9149 | -0.27404 | 0.12464 | 0.099528 | 0.14295 | 0.083135 | -0.041502 | 0.052844 | 0.080598 | -0.12756 | -0.17658 | 0.33068 | 0.16339 | 0.29095 | 0.1309 | -0.53895 | 121.6999 | 121.6532 | 121.6809 | 0.32646 | -121.4757 | 121.4238 | 121.7312 | 121.0614 | 10.5817 | -121.7279
1071.4375 | 121.6187 | -0.1236 | 121.4493 | 1.4211e-13 | -0.017448 | 0.00178 | 0.068195 | -0.010784 | 0.058898 | 0.015566 | -0.0012349 | 0.00064101 | 0.060552 | 0.029585 | 0.053804 | 0.005626 | 0.18455 | -0.063349 | 121.558 | 121.5159 | 121.5482 | -0.012689 | 0.19793 | 9.9636 | 0.016908 | 121.2727 | 121.6031 | 121.0019 | -0.2603 | 0.11091 | 0.10868 | 0.12922 | 0.060247 | -0.05066 | 0.066578 | 0.09891 | -0.13671 | -0.17658 | 0.32153 | 0.1405 | 0.27721 | 0.1538 | -0.44738 | 121.6816 | 121.6395 | 121.6718 | 0.30815 | -121.462 | 121.3963 | 121.7267 | 121.1255 | 10.0872 | -121.7096
1073.1875 | 121.6278 | -0.14648 | 121.4355 | 1.4211e-13 | -0.018089 | 0.0022072 | 0.067981 | -0.010997 | 0.058685 | 0.00030522 | -0.0014485 | 0.00021361 | 0.060125 | 0.029372 | 0.054018 | -0.003531 | 0.17539 | -0.063349 | 121.5442 | 121.5067 | 121.5345 | -0.058478 | 0.20251 | 10.7054 | 0.007751 | 121.259 | 121.5848 | 120.9149 | -0.27404 | 0.088006 | 0.10868 | 0.14295 | 0.083135 | -0.004871 | 0.071154 | 0.098908 | -0.12756 | -0.17659 | 0.34899 | 0.15424 | 0.28179 | 0.14921 | -0.52064 | 121.6907 | 121.6532 | 121.6809 | 0.32188 | -121.494 | 121.4054 | 121.7312 | 121.0614 | 10.8519 | -121.7096
1074.875 | 121.5179 | -0.20142 | 121.431 | 1.4211e-13 | -0.017662 | 0.0019936 | 0.067981 | -0.010784 | 0.058898 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060125 | 0.029585 | 0.054659 | -0.012688 | 0.17081 | -0.08624 | 121.5305 | 121.4838 | 121.5161 | -0.15921 | 0.19793 | 11.09 | -0.005985 | 121.2361 | 121.5664 | 120.9103 | -0.2832 | 0.042201 | 0.099524 | 0.18873 | 0.11518 | 0.072975 | 0.052837 | 0.085171 | -0.081782 | -0.1949 | 0.39935 | 0.19543 | 0.27721 | 0.13548 | -0.52064 | 121.7319 | 121.6852 | 121.7176 | 0.37223 | -121.5902 | 121.4375 | 121.7679 | 121.1117 | 11.2914 | -121.7142
1076.625 | 121.582 | -0.15564 | 121.376 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.067981 | -0.010997 | 0.058685 | 0.00030522 | -0.0010211 | 0.00064101 | 0.060766 | 0.029585 | 0.054232 | -0.008109 | 0.17997 | -0.067927 | 121.5168 | 121.4746 | 121.4978 | -0.15464 | 0.22083 | 11.8089 | 0.021487 | 121.2269 | 121.5664 | 120.8829 | -0.26946 | 0.001004 | 0.14072 | 0.14753 | 0.087713 | 0.086709 | 0.09861 | 0.12179 | -0.11382 | -0.14913 | 0.37647 | 0.17713 | 0.29095 | 0.19041 | -0.49318 | 121.6724 | 121.6303 | 121.6535 | 0.33561 | -121.5307 | 121.3826 | 121.7221 | 121.0385 | 11.9645 | -121.6455
1078.3594 | 121.5775 | -0.16022 | 121.3806 | 1.4211e-13 | -0.017662 | 0.0022072 | 0.067981 | -0.010997 | 0.058685 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060338 | 0.029585 | 0.053804 | -0.017266 | 0.18455 | -0.08624 | 121.5122 | 121.4655 | 121.4932 | -0.14548 | 0.23456 | 14.0249 | 0.030644 | 121.2178 | 121.5436 | 120.8371 | -0.2832 | 0.014739 | 0.13156 | 0.14295 | 0.073977 | 0.059238 | 0.084875 | 0.11263 | -0.12298 | -0.16286 | 0.39478 | 0.19086 | 0.31384 | 0.16294 | -0.54354 | 121.6724 | 121.6257 | 121.6535 | 0.34477 | -121.5261 | 121.378 | 121.7038 | 120.9973 | 14.1852 | -121.6638
1080.1094 | 121.55 | -0.16022 | 121.3715 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.067981 | -0.010784 | 0.058898 | -0.0073253 | -0.0010211 | 0.00042721 | 0.060338 | 0.029585 | 0.054232 | -0.017266 | 0.17997 | -0.081662 | 121.5076 | 121.4563 | 121.4841 | -0.09511 | 0.23914 | 13.9746 | 0.021487 | 121.2086 | 121.5436 | 120.8737 | -0.2832 | 0.065107 | 0.13614 | 0.14295 | 0.078555 | 0.013448 | 0.084872 | 0.11263 | -0.12298 | -0.16286 | 0.39936 | 0.1817 | 0.30468 | 0.17209 | -0.49776 | 121.6678 | 121.6165 | 121.6443 | 0.34019 | -121.4666 | 121.3688 | 121.7038 | 121.0339 | 14.1348 | -121.6547
1081.7812 | 121.4584 | -0.21057 | 121.3898 | 1.4211e-13 | -0.018089 | 0.0019936 | 0.067981 | -0.010997 | 0.058257 | 0.0079357 | -0.0010211 | 0.00021361 | 0.060766 | 0.030013 | 0.054018 | -0.031001 | 0.17539 | -0.081662 | 121.4984 | 121.4518 | 121.4795 | -0.15464 | 0.2254 | 14.0249 | 0.030644 | 121.204 | 121.539 | 120.8554 | -0.30151 | 0.055935 | 0.10867 | 0.17957 | 0.12891 | 0.072974 | 0.061983 | 0.08974 | -0.090942 | -0.18575 | 0.43598 | 0.24122 | 0.33216 | 0.1492 | -0.53439 | 121.709 | 121.6623 | 121.6901 | 0.38596 | -121.5444 | 121.4146 | 121.7495 | 121.066 | 14.2355 | -121.6913
1083.5156 | 121.4996 | -0.20142 | 121.3806 | 1.4211e-13 | -0.018089 | 0.00178 | 0.068195 | -0.010997 | 0.058685 | -0.0073253 | -0.0014485 | 1.2e-08 | 0.060125 | 0.029158 | 0.053804 | -0.026423 | 0.18455 | -0.090818 | 121.4847 | 121.4518 | 121.4749 | -0.17295 | 0.23914 | 14.1669 | 0.016908 | 121.1949 | 121.5298 | 120.8188 | -0.28778 | 0.028465 | 0.10409 | 0.17499 | 0.1106 | 0.082133 | 0.071139 | 0.094318 | -0.086361 | -0.18575 | 0.44056 | 0.21832 | 0.30468 | 0.1492 | -0.56186 | 121.6861 | 121.6532 | 121.6763 | 0.38597 | -121.5536 | 121.3963 | 121.7312 | 121.0202 | 14.3683 | -121.6684
1085.25 | 121.582 | -0.16479 | 121.3623 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.067767 | -0.010784 | 0.058685 | 0.0079357 | -0.0010211 | 0.00042721 | 0.060552 | 0.029799 | 0.054018 | -0.031001 | 0.17997 | -0.095397 | 121.471 | 121.4334 | 121.4566 | -0.18211 | 0.24372 | 14.2585 | 0.01233 | 121.1903 | 121.5161 | 120.8004 | -0.30151 | -0.017314 | 0.10867 | 0.13379 | 0.069398 | 0.086712 | 0.071133 | 0.094313 | -0.13672 | -0.17202 | 0.40851 | 0.17713 | 0.31384 | 0.15378 | -0.56186 | 121.6358 | 121.5982 | 121.6214 | 0.34477 | -121.5444 | 121.3551 | 121.6809 | 120.9652 | 14.4233 | -121.6638
1087 | 121.5408 | -0.2243 | 121.3165 | 1.4211e-13 | -0.017876 | 0.00178 | 0.067981 | -0.011211 | 0.058471 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060552 | 0.029799 | 0.054018 | -0.053893 | 0.18455 | -0.11829 | 121.4435 | 121.3922 | 121.4246 | -0.21416 | 0.21167 | 14.1898 | -0.015143 | 121.1445 | 121.4749 | 120.7821 | -0.33814 | 0.010142 | 0.12698 | 0.17041 | 0.10602 | 0.095874 | 0.0757 | 0.10804 | -0.11384 | -0.17203 | 0.43597 | 0.20916 | 0.323 | 0.15835 | -0.5344 | 121.6678 | 121.6165 | 121.6489 | 0.40885 | -121.5307 | 121.3688 | 121.6992 | 121.0064 | 14.4141 | -121.6547
1088.6875 | 121.5591 | -0.15564 | 121.344 | 1.4211e-13 | -0.018089 | 0.0019936 | 0.067981 | -0.010784 | 0.058471 | 0.00030522 | -0.00080746 | 0.00021361 | 0.060338 | 0.029372 | 0.054018 | -0.021844 | 0.17539 | -0.077084 | 121.4893 | 121.4426 | 121.4704 | -0.10885 | 0.27577 | 14.6156 | 0.039802 | 121.1994 | 121.5298 | 120.8188 | -0.2832 | 0.046793 | 0.14529 | 0.1338 | 0.078556 | 0.031763 | 0.098602 | 0.12636 | -0.12756 | -0.14455 | 0.43141 | 0.19544 | 0.323 | 0.18582 | -0.52524 | 121.6449 | 121.5982 | 121.626 | 0.33103 | -121.4528 | 121.3551 | 121.6855 | 120.9744 | 14.7712 | -121.6272
1090.4375 | 121.4905 | -0.16479 | 121.3806 | 1.4211e-13 | -0.018089 | 0.0019936 | 0.067767 | -0.01057 | 0.058898 | 0.00030522 | -0.0014485 | 0.0010682 | 0.060552 | 0.029799 | 0.053804 | -0.008109 | 0.18455 | -0.067927 | 121.4984 | 121.4518 | 121.4887 | -0.090531 | 0.29408 | 15.0094 | 0.053538 | 121.2132 | 121.539 | 120.8737 | -0.2603 | 0.074264 | 0.11783 | 0.15669 | 0.096868 | 0.022604 | 0.071139 | 0.10805 | -0.095509 | -0.16744 | 0.45888 | 0.21833 | 0.31384 | 0.15836 | -0.50692 | 121.6632 | 121.6165 | 121.6535 | 0.34935 | -121.4711 | 121.378 | 121.7038 | 121.0385 | 15.1742 | -121.6409
1092.1719 | 121.5683 | -0.19226 | 121.3211 | 1.4211e-13 | -0.017662 | 0.0022072 | 0.067981 | -0.010997 | 0.058898 | 0.00030522 | -0.0010211 | 0.00042721 | 0.060338 | 0.029799 | 0.054018 | -0.049315 | 0.17081 | -0.10455 | 121.4572 | 121.4243 | 121.452 | -0.20042 | 0.2483 | 13.6724 | 0.007751 | 121.1765 | 121.5023 | 120.7775 | -0.32441 | -0.008164 | 0.13613 | 0.14295 | 0.087708 | 0.095872 | 0.10317 | 0.13093 | -0.13215 | -0.14456 | 0.44056 | 0.20001 | 0.33216 | 0.18124 | -0.54356 | 121.6495 | 121.6165 | 121.6443 | 0.36308 | -121.5215 | 121.3688 | 121.6946 | 120.9698 | 13.8646 | -121.6455
1093.9062 | 121.3623 | -1.886 | 119.3573 | 1.4211e-13 | -0.018089 | 0.00178 | 0.067981 | -0.011211 | 0.058685 | 0.015566 | -0.0014485 | 0.00042721 | 0.060338 | 0.029799 | 0.053804 | -1.9356 | 0.18455 | -2.0183 | 119.3054 | 119.2676 | 119.2955 | -2.1465 | -1.6244 | 12.079 | -1.9336 | 119.0247 | 119.3504 | 118.882 | -2.2384 | -0.26048 | -0.051904 | -0.049625 | -0.13229 | 0.12819 | -0.089693 | -0.061782 | -0.35237 | -0.33264 | 0.26159 | -0.047636 | 0.30473 | -0.006897 | -0.47529 | 121.1914 | 121.1536 | 121.1815 | 2.0705 | -121.5038 | 120.9106 | 121.2364 | 120.768 | 13.965 | -121.5957
1095.6562 | 121.3577 | -0.18768 | 121.3394 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.068195 | -0.010997 | 0.058685 | 0.015566 | -0.0012349 | 0.00064101 | 0.060338 | 0.029799 | 0.053804 | -0.003531 | 0.18913 | -0.072505 | 121.4343 | 121.3876 | 121.4246 | -0.17753 | 0.29408 | 12.8482 | 0.058117 | 121.1445 | 121.4749 | 120.8325 | -0.26488 | 0.010153 | 0.09493 | 0.18415 | 0.11518 | 0.10502 | 0.048232 | 0.085151 | -0.0772 | -0.19492 | 0.48177 | 0.2458 | 0.323 | 0.13546 | -0.50692 | 121.622 | 121.5753 | 121.6123 | 0.37681 | -121.5169 | 121.3322 | 121.6626 | 121.0202 | 13.0359 | -121.6043
1097.3906 | 121.3715 | -1.1444 | 120.1859 | 1.4211e-13 | -0.017876 | 0.00178 | 0.067981 | -0.010997 | 0.058471 | 0.00030522 | -0.0012349 | 0.00042721 | 0.060338 | 0.029585 | 0.054018 | -0.55752 | 0.17997 | -0.63106 | 120.7613 | 120.7191 | 120.7515 | -0.78653 | -0.22789 | 14.9819 | -0.51422 | 120.476 | 120.8018 | 120.1686 | -0.85555 | 0.35788 | 0.57547 | 0.58689 | 0.51335 | 0.15547 | 0.53327 | 0.56566 | 0.28886 | 0.29019 | 0.91652 | 0.63019 | 0.34133 | 0.61597 | -0.017257 | 121.9057 | 121.8635 | 121.8959 | 1.3244 | -120.9724 | 121.6204 | 121.9462 | 121.313 | 16.1263 | -121.0414
1099.0625 | 121.1975 | -1.9958 | 119.2566 | 1.4211e-13 | -0.017876 | 0.00178 | 0.067981 | -0.011211 | 0.058685 | 0.00030522 | -0.0014485 | 0.00042721 | 0.060338 | 0.029799 | 0.053377 | -1.1619 | 0.17081 | -1.2445 | 120.0425 | 120.0094 | 120.0373 | -1.3955 | -0.81396 | 14.8583 | -1.1369 | 119.7526 | 120.083 | 119.491 | -1.4783 | 0.60033 | 0.78593 | 0.83399 | 0.7513 | 0.15098 | 0.7528 | 0.78066 | 0.51758 | 0.49605 | 1.1819 | 0.85892 | 0.34134 | 0.82639 | 0.23437 | 122.0384 | 122.0052 | 122.0331 | 2.1667 | -120.6521 | 121.7485 | 122.0788 | 121.4868 | 16.8541 | -120.7349
1100.7969 | 121.0876 | -43.4326 | 77.8061 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.06734 | -0.010784 | 0.058898 | 0.0079357 | -0.0014485 | 0.00021361 | 0.059484 | 0.029799 | 0.054445 | -43.718 | -0.044379 | -43.818 | 77.4772 | 77.4849 | 77.557 | -43.7872 | -43.0892 | 2.656 | -43.522 | 77.2825 | 77.4791 | 77.4228 | -43.9285 | -0.35459 | -0.32885 | -0.28536 | -0.38536 | -0.030768 | -0.32117 | -0.24911 | -0.49587 | -0.52358 | 0.34343 | -0.089427 | 0.40644 | -0.32701 | -0.38333 | 120.9099 | 120.9175 | 120.9896 | 43.3882 | -121.5933 | 120.7151 | 120.9117 | 120.8554 | 46.0886 | -121.7346
1102.5469 | 121.2204 | -70.8801 | 50.1984 | 1.4211e-13 | -0.018944 | 0.00178 | 0.06734 | -0.01057 | 0.059112 | 0.0079357 | -0.0020893 | -0.00021359 | 0.059484 | 0.030013 | 0.0553 | -73.3859 | -0.026065 | -73.5539 | 47.5483 | 47.5845 | 47.6862 | -73.6693 | -72.5028 | -5.3384 | -73.0776 | 47.4307 | 47.5945 | 47.5657 | -73.8556 | -2.7891 | -2.65 | -2.5058 | -2.6738 | 0.11536 | -2.6138 | -2.5122 | -2.9755 | -2.7676 | -1.6227 | -2.1975 | 0.77802 | -2.6038 | -2.6327 | 118.4284 | 118.4647 | 118.5663 | 70.8541 | -123.8676 | 118.3109 | 118.4747 | 118.4458 | 65.5417 | -124.054
1104.3125 | 121.0556 | -67.4377 | 53.5629 | 1.4211e-13 | -0.018517 | 0.0015662 | 0.06734 | -0.010997 | 0.058898 | 0.00030522 | -0.0016621 | 1.2e-08 | 0.059484 | 0.029799 | 0.054659 | -62.4573 | -0.2321 | -62.5706 | 58.5227 | 58.4915 | 58.6702 | -62.6844 | -61.6879 | -2.3119 | -62.2169 | 58.3184 | 58.5145 | 58.3529 | -62.8802 | 4.7533 | 4.9598 | 4.9804 | 4.8671 | 0.11382 | 4.9286 | 5.1073 | 4.5575 | 4.7555 | 5.7498 | 5.2208 | 0.66329 | 4.9516 | 4.79 | 125.9605 | 125.9293 | 126.108 | 67.2056 | -116.2474 | 125.7561 | 125.9523 | 125.7906 | 65.1259 | -116.4431
1106 | 121.0098 | -51.7868 | 69.1269 | 1.4211e-13 | -0.018517 | 0.0013526 | 0.067126 | -0.01057 | 0.058898 | 0.015566 | -0.0012349 | 1.2e-08 | 0.05927 | 0.030013 | 0.054659 | -51.2906 | -0.021486 | -51.3401 | 69.6757 | 69.6321 | 69.8375 | -51.4294 | -50.5159 | 1.2549 | -51.0494 | 69.5037 | 69.7275 | 69.488 | -51.5888 | 0.35737 | 0.54878 | 0.49617 | 0.44671 | 0.089342 | 0.50517 | 0.71056 | 0.19796 | 0.37676 | 1.2709 | 0.73736 | 0.5394 | 0.60062 | 0.36115 | 121.4625 | 121.4189 | 121.6243 | 51.7653 | -120.5563 | 121.2905 | 121.5143 | 121.2748 | 53.0417 | -120.7157
1107.6719 | 121.051 | -57.7057 | 63.0569 | 1.4211e-13 | -0.018517 | 0.00178 | 0.067126 | -0.010997 | 0.058898 | 0.0079357 | -0.0014485 | -0.00021359 | 0.059484 | 0.030013 | 0.054232 | -51.0205 | -0.14511 | -51.1066 | 69.955 | 69.9663 | 70.0572 | -51.1501 | -50.2228 | 1.7861 | -50.7793 | 69.7463 | 69.9427 | 69.8772 | -51.3416 | 6.5556 | 6.898 | 6.6852 | 6.5991 | 0.04352 | 6.9094 | 7.0003 | 6.3641 | 6.6894 | 7.4829 | 6.9264 | 0.56229 | 6.8858 | 6.8203 | 127.6606 | 127.672 | 127.7629 | 57.5606 | -114.2071 | 127.452 | 127.6484 | 127.5829 | 59.4917 | -114.3985
1109.4062 | 121.0648 | -34.7168 | 86.142 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.067126 | -0.010997 | 0.058898 | 0.0079357 | -0.0014485 | 0.00042721 | 0.059698 | 0.029799 | 0.054659 | -34.4559 | 0.14334 | -34.5561 | 86.5562 | 86.5787 | 86.6592 | -34.4325 | -33.744 | 6.7814 | -34.2318 | 86.412 | 86.6134 | 86.3877 | -34.5923 | 0.28433 | 0.41422 | 0.2609 | 0.16068 | -0.12365 | 0.4367 | 0.51727 | 0.12452 | 0.27007 | 0.97275 | 0.48496 | 0.36043 | 0.47143 | 0.2457 | 121.273 | 121.2955 | 121.376 | 34.8601 | -120.5744 | 121.1288 | 121.3302 | 121.1045 | 41.4982 | -120.7342
1111.1406 | 120.9045 | -46.8109 | 73.938 | 1.4211e-13 | -0.018517 | 0.0015662 | 0.06734 | -0.010997 | 0.059112 | 0.0079357 | -0.0014485 | -0.00021359 | 0.059698 | 0.029799 | 0.054232 | -45.9156 | -0.053537 | -45.9881 | 75.037 | 75.0123 | 75.1349 | -46.0171 | -45.1267 | 2.8849 | -45.6649 | 74.8147 | 75.0295 | 74.9045 | -46.1813 | 0.79377 | 1.099 | 0.89531 | 0.82283 | 0.029063 | 1.0743 | 1.1969 | 0.62965 | 0.87672 | 1.6842 | 1.146 | 0.51638 | 1.0915 | 0.96654 | 121.8479 | 121.8232 | 121.9458 | 46.7574 | -119.9551 | 121.6256 | 121.8404 | 121.7154 | 49.6959 | -120.1192
1112.8125 | 120.8496 | -36.9736 | 82.8644 | 1.4211e-13 | -0.018303 | 0.00178 | 0.06734 | -0.010997 | 0.058685 | -0.014956 | -0.0014485 | 0.00021361 | 0.059698 | 0.029799 | 0.054659 | -41.6348 | 0.90797 | -41.8539 | 79.0064 | 79.17 | 78.9947 | -41.6214 | -40.6808 | 4.6661 | -41.2464 | 79.0223 | 79.1365 | 79.2725 | -41.6894 | -4.6478 | -3.858 | -4.6612 | -4.8803 | -0.23252 | -3.6944 | -3.8697 | -4.7159 | -3.842 | -3.7072 | -4.2729 | 0.44302 | -3.7278 | -3.5919 | 115.98 | 116.1435 | 115.9682 | 37.8815 | -124.4858 | 115.9959 | 116.1101 | 116.2461 | 41.6396 | -124.5538
1114.5469 | 120.845 | -60.6995 | 59.9899 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.067126 | -0.010784 | 0.058898 | 0.015566 | -0.0016621 | 1.2e-08 | 0.059484 | 0.029799 | 0.0553 | -61.6927 | 0.051771 | -61.8198 | 59.0263 | 59.0456 | 59.1327 | -61.9014 | -60.7264 | -2.5042 | -61.3378 | 58.877 | 59.0502 | 59.0122 | -62.0789 | -1.202 | -0.96359 | -0.99327 | -1.1203 | 0.081658 | -0.94434 | -0.85725 | -1.3795 | -1.113 | -0.026918 | -0.63834 | 0.74111 | -0.93972 | -0.97773 | 119.7258 | 119.7451 | 119.8321 | 60.7512 | -121.8914 | 119.5764 | 119.7497 | 119.7117 | 58.1953 | -122.0688
1116.2969 | 120.9686 | -43.721 | 77.2339 | 1.4211e-13 | -0.018089 | 0.0019936 | 0.06734 | -0.010997 | 0.058898 | 0.0079357 | -0.0014485 | 0.00042721 | 0.059698 | 0.030226 | 0.054659 | -42.7382 | 0.17997 | -42.8794 | 78.1136 | 78.1763 | 78.1614 | -42.7844 | -41.8438 | 3.6038 | -42.4232 | 77.9968 | 78.143 | 78.105 | -42.9395 | 0.93659 | 0.87975 | 0.9828 | 0.84158 | -0.095005 | 0.94245 | 0.92747 | 0.78155 | 0.76287 | 1.8772 | 1.2979 | 0.51631 | 0.90909 | 0.87109 | 121.8346 | 121.8973 | 121.8824 | 43.901 | -120.0183 | 121.7178 | 121.864 | 121.826 | 47.3248 | -120.1733
1117.9844 | 121.0098 | -59.6695 | 61.116 | 1.4211e-13 | -0.01873 | 0.0013526 | 0.06734 | -0.010997 | 0.058898 | 0.0079357 | -0.0014485 | 0.00021361 | 0.059484 | 0.030226 | 0.054873 | -59.9392 | -0.026065 | -60.0251 | 60.8943 | 60.868 | 61.0557 | -60.1477 | -58.9178 | -2.4493 | -59.5887 | 60.6992 | 60.9229 | 60.7795 | -60.3252 | -0.47821 | -0.2217 | -0.26971 | -0.35559 | 0.12262 | -0.24802 | -0.060334 | -0.65573 | -0.41682 | 0.7517 | 0.080758 | 0.73649 | -0.19317 | -0.33649 | 120.5638 | 120.5375 | 120.7252 | 59.6434 | -121.2637 | 120.3687 | 120.5924 | 120.449 | 57.2202 | -121.4413
1119.7344 | 120.9732 | -33.11 | 87.9822 | 1.4211e-13 | -0.018303 | 0.0015662 | 0.067554 | -0.010997 | 0.058685 | 0.00030522 | -0.0014485 | 0.00021361 | 0.059698 | 0.029799 | 0.054659 | -38.2239 | 0.30359 | -38.3286 | 82.7561 | 82.8285 | 82.8682 | -38.2421 | -37.3063 | 5.1148 | -37.8948 | 82.6485 | 82.836 | 82.8026 | -38.3515 | -5.1321 | -5.2261 | -5.1139 | -5.2186 | -0.086488 | -5.1537 | -5.114 | -5.2414 | -5.3337 | -4.1962 | -4.7848 | 0.45667 | -5.1461 | -5.1796 | 115.8662 | 115.9386 | 115.9782 | 33.4136 | -126.2243 | 115.7586 | 115.9461 | 115.9127 | 38.2248 | -126.3337
1121.4844 | 121.0144 | -35.9894 | 84.8053 | 1.4211e-13 | -0.018303 | 0.00178 | 0.06734 | -0.010784 | 0.058471 | 0.00030522 | -0.0012349 | 0.00064101 | 0.059911 | 0.029799 | 0.054445 | -30.5688 | -0.067272 | -30.6417 | 90.5211 | 90.4799 | 90.5648 | -30.5679 | -29.7651 | 7.3446 | -30.3354 | 90.2717 | 90.5052 | 90.1971 | -30.7415 | 5.4215 | 5.7158 | 5.4205 | 5.3477 | -0.073831 | 5.6746 | 5.7595 | 5.2479 | 5.4664 | 6.2242 | 5.654 | 0.40613 | 5.6999 | 5.3918 | 126.5105 | 126.4693 | 126.5542 | 35.9221 | -115.3732 | 126.2611 | 126.4946 | 126.1864 | 43.334 | -115.5468
1123.1719 | 120.7855 | -25.0717 | 95.7825 | 1.4211e-13 | -0.018517 | 0.0015662 | 0.06734 | -0.010997 | 0.058685 | 0.00030522 | -0.0010211 | 0.00021361 | 0.059911 | 0.029585 | 0.054232 | -28.504 | 0.27612 | -28.5952 | 92.4669 | 92.4626 | 92.529 | -28.4982 | -27.6544 | 8.5534 | -28.2337 | 92.3091 | 92.5381 | 92.3353 | -28.6032 | -3.4265 | -3.3156 | -3.4323 | -3.5235 | -0.097014 | -3.3199 | -3.2535 | -3.5315 | -3.4733 | -2.5826 | -3.162 | 0.36945 | -3.2444 | -3.4472 | 117.5386 | 117.5343 | 117.6007 | 25.3478 | -124.2807 | 117.3809 | 117.6098 | 117.407 | 33.6251 | -124.3857
1124.8594 | 120.8725 | -26.4313 | 94.2856 | 1.4211e-13 | -0.017876 | 0.00178 | 0.067554 | -0.011211 | 0.058685 | 0.00030522 | -0.0014485 | 0.00042721 | 0.059911 | 0.030226 | 0.054659 | -36.9969 | 0.41806 | -37.065 | 83.8092 | 83.8176 | 83.9212 | -37.0104 | -35.9968 | 5.5772 | -36.6357 | 83.6741 | 83.8937 | 83.5856 | -37.1106 | -10.5791 | -10.4764 | -10.5656 | -10.6337 | -0.054613 | -10.468 | -10.3643 | -10.6794 | -10.6115 | -9.5655 | -10.2044 | 0.47496 | -10.3919 | -10.7 | 110.2404 | 110.2488 | 110.3525 | 26.8493 | -131.296 | 110.1054 | 110.325 | 110.0168 | 32.0085 | -131.3962
1126.5938 | 120.845 | -41.3315 | 79.1428 | 1.4211e-13 | -0.018517 | 0.00178 | 0.067554 | -0.010997 | 0.058471 | 0.00030522 | -0.0016621 | 0.00021361 | 0.05927 | 0.03044 | 0.054445 | -39.5425 | -0.035222 | -39.5831 | 81.2682 | 81.1938 | 81.3526 | -39.6112 | -38.5425 | 4.8675 | -39.2181 | 81.014 | 81.2656 | 81.0261 | -39.7663 | 1.7203 | 2.1254 | 1.789 | 1.7484 | 0.028163 | 2.0511 | 2.2099 | 1.5651 | 1.8712 | 2.7889 | 2.1134 | 0.54828 | 2.1228 | 1.8834 | 122.5996 | 122.5253 | 122.6841 | 41.2963 | -118.754 | 122.3455 | 122.5971 | 122.3576 | 46.199 | -118.9091
1128.3438 | 120.0714 | -81.6879 | 38.0173 | 1.4211e-13 | -0.018944 | 0.0013526 | 0.066699 | -0.010784 | 0.058257 | 0.00030522 | -0.0016621 | 0.00021361 | 0.05927 | 0.030654 | 0.054873 | -76.0551 | -0.36946 | -76.1177 | 43.9589 | 43.8665 | 44.1835 | -76.3708 | -74.7327 | -8.6488 | -75.5822 | 43.6993 | 43.9683 | 43.6785 | -76.5983 | 5.3171 | 5.9416 | 5.6328 | 5.5702 | 0.25309 | 5.8492 | 6.1663 | 5.0896 | 5.682 | 6.9553 | 6.1058 | 1.0162 | 5.951 | 5.6612 | 125.6468 | 125.5544 | 125.8715 | 81.3185 | -114.3881 | 125.3872 | 125.6562 | 125.3664 | 73.0391 | -114.6156
1130.0469 | 120.9229 | -0.32044 | 120.6848 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.067767 | -0.010997 | 0.058471 | 0.00030522 | -0.0012349 | 0.00085461 | 0.060338 | 0.030013 | 0.053377 | -0.15462 | 0.28528 | -0.2419 | 120.7613 | 120.7283 | 120.7607 | -0.3149 | 0.28035 | 9.7576 | -0.042615 | 120.476 | 120.811 | 120.1182 | -0.45719 | 0.005537 | 0.07651 | 0.16582 | 0.078533 | 0.072996 | 0.043469 | 0.075857 | -0.13676 | -0.20878 | 0.60078 | 0.27782 | 0.41458 | 0.12616 | -0.56658 | 121.0818 | 121.0487 | 121.0811 | 0.60572 | -120.9997 | 120.7965 | 121.1314 | 120.4387 | 10.078 | -121.142
1131.8125 | 121.0785 | -0.33875 | 120.726 | 1.4211e-13 | -0.018303 | 0.0019936 | 0.067981 | -0.011211 | 0.058257 | 0.0079357 | -0.0010211 | 0.00085461 | 0.060125 | 0.029799 | 0.054018 | -0.18209 | 0.25323 | -0.26937 | 120.8208 | 120.7924 | 120.811 | -0.33779 | 0.26203 | 9.7484 | -0.056351 | 120.5401 | 120.8705 | 120.1915 | -0.48009 | 0.000952 | 0.09483 | 0.15666 | 0.069374 | 0.068422 | 0.066375 | 0.085022 | -0.14134 | -0.18587 | 0.60078 | 0.28239 | 0.42374 | 0.14449 | -0.53452 | 121.1596 | 121.1311 | 121.1498 | 0.59198 | -121.0638 | 120.8789 | 121.2092 | 120.5302 | 10.0872 | -121.2061
1133.5469 | 120.9 | -3.7491 | 117.2195 | 1.4211e-13 | -0.018303 | 0.0019936 | 0.067767 | -0.010997 | 0.058257 | 0.00030522 | -0.0014485 | 0.00064101 | 0.060338 | 0.029799 | 0.053591 | -3.5426 | 0.22118 | -3.6115 | 117.3871 | 117.3582 | 117.3817 | -3.7262 | -3.0392 | 8.7182 | -3.4034 | 117.1154 | 117.4365 | 116.9086 | -3.8272 | 0.022887 | 0.16751 | 0.20646 | 0.13757 | 0.11468 | 0.13865 | 0.16212 | -0.078119 | -0.10412 | 0.70987 | 0.3457 | 0.42381 | 0.217 | -0.31091 | 121.1361 | 121.1073 | 121.1307 | 3.9703 | -120.9457 | 120.8645 | 121.1856 | 120.6577 | 12.4673 | -121.0467
1135.2344 | 121.0281 | -0.5127 | 120.6757 | 1.4211e-13 | -0.018089 | 0.0019936 | 0.067981 | -0.011211 | 0.058471 | 0.0079357 | -0.0010211 | 0.00085461 | 0.060552 | 0.029799 | 0.053377 | -0.78643 | 0.24865 | -0.85081 | 120.2257 | 120.2063 | 120.2067 | -0.9239 | -0.28741 | 9.5607 | -0.63327 | 119.9541 | 120.2661 | 119.6466 | -1.0616 | -0.4112 | -0.45001 | -0.27374 | -0.33812 | 0.073082 | -0.46937 | -0.469 | -0.5489 | -0.72157 | 0.22528 | -0.12057 | 0.42833 | -0.40954 | -1.029 | 120.7383 | 120.719 | 120.7194 | 0.76135 | -121.5996 | 120.4668 | 120.7788 | 120.1593 | 10.0734 | -121.7373
1136.9844 | 121.0693 | -0.64545 | 120.5338 | 1.4211e-13 | -0.01873 | 0.0022072 | 0.067767 | -0.010997 | 0.058257 | 0.00030522 | -0.0012349 | 0.001282 | 0.060766 | 0.030013 | 0.054018 | -0.498 | 0.20286 | -0.54407 | 120.5919 | 120.5543 | 120.5775 | -0.64458 | -0.017267 | 9.6981 | -0.34481 | 120.2929 | 120.6416 | 120.0312 | -0.78229 | 0.000866 | 0.058171 | 0.14745 | 0.10138 | 0.10051 | 0.020532 | 0.043775 | -0.13684 | -0.24085 | 0.62818 | 0.30064 | 0.43748 | 0.10782 | -0.50252 | 121.2374 | 121.1997 | 121.223 | 0.84831 | -121.1783 | 120.9383 | 121.287 | 120.6767 | 10.3435 | -121.316
1138.6719 | 121.1746 | -0.74616 | 120.3644 | 1.4211e-13 | -0.018303 | 0.0022072 | 0.067767 | -0.011211 | 0.058257 | 0.0079357 | -0.0012349 | 0.0010682 | 0.060552 | 0.029799 | 0.053804 | -0.56667 | 0.19371 | -0.61732 | 120.5278 | 120.4856 | 120.5134 | -0.70869 | -0.063054 | 9.6981 | -0.40891 | 120.238 | 120.5683 | 119.9076 | -0.84639 | 0.037469 | 0.16345 | 0.17948 | 0.12883 | 0.091365 | 0.12122 | 0.14905 | -0.10024 | -0.12642 | 0.6831 | 0.33724 | 0.43748 | 0.20393 | -0.45676 | 121.274 | 121.2318 | 121.2596 | 0.93986 | -121.0731 | 120.9841 | 121.3145 | 120.6538 | 10.4442 | -121.2108
1140.4219 | 121.138 | -4.097 | 116.9174 | 1.4211e-13 | -0.018517 | 0.00178 | 0.067981 | -0.010997 | 0.058257 | 0.0079357 | -0.0012349 | 0.00085461 | 0.060338 | 0.030013 | 0.054018 | -3.7853 | 0.16166 | -3.845 | 117.2634 | 117.2254 | 117.2626 | -3.9231 | -3.1903 | 8.7594 | -3.6186 | 116.9781 | 117.3083 | 116.6614 | -4.079 | 0.17389 | 0.34602 | 0.31171 | 0.25198 | 0.078083 | 0.30799 | 0.3452 | 0.017948 | 0.06065 | 0.90667 | 0.4784 | 0.46045 | 0.39093 | -0.25603 | 121.3604 | 121.3224 | 121.3596 | 4.2586 | -120.8405 | 121.0751 | 121.4053 | 120.7584 | 12.8564 | -120.9965
1142.1562 | 121.0785 | -2.243 | 118.8492 | 1.4211e-13 | -0.018517 | 0.002421 | 0.067981 | -0.011425 | 0.058471 | 0.00030522 | -0.0014485 | 0.001282 | 0.060338 | 0.030013 | 0.054018 | -1.7708 | 0.19829 | -1.8306 | 119.2413 | 119.2035 | 119.2268 | -1.9358 | -1.1757 | 9.4462 | -1.604 | 118.9606 | 119.2771 | 118.8683 | -2.0506 | 0.3072 | 0.39212 | 0.47225 | 0.41248 | 0.10527 | 0.35432 | 0.37766 | 0.19242 | 0.11137 | 1.0674 | 0.63909 | 0.44667 | 0.42796 | 0.01909 | 121.4843 | 121.4465 | 121.4699 | 2.4413 | -120.785 | 121.2036 | 121.5202 | 121.1113 | 11.6893 | -120.8998
1143.9062 | 121.0785 | -1.2177 | 119.9341 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.067981 | -0.010997 | 0.058471 | 0.0079357 | -0.00080746 | 0.0010682 | 0.060338 | 0.029799 | 0.054232 | -1.0382 | 0.19371 | -1.0843 | 120.0608 | 120.0186 | 120.0373 | -1.1803 | -0.44309 | 9.7072 | -0.84847 | 119.771 | 120.1059 | 119.3857 | -1.318 | 0.037336 | 0.12675 | 0.1794 | 0.13335 | 0.09601 | 0.084468 | 0.10317 | -0.10036 | -0.16313 | 0.77456 | 0.36918 | 0.46954 | 0.17179 | -0.54843 | 121.2785 | 121.2362 | 121.2549 | 1.4114 | -121.1144 | 120.9886 | 121.3235 | 120.6033 | 10.9249 | -121.2521
1145.6562 | 121.0007 | -5.9875 | 114.6973 | 1.4211e-13 | -0.018303 | 0.0019936 | 0.067981 | -0.010997 | 0.058471 | 0.0079357 | -0.0010211 | 0.0010682 | 0.060552 | 0.030226 | 0.054018 | -5.4884 | 0.12503 | -5.5481 | 115.4962 | 115.4442 | 115.4907 | -5.6448 | -4.8066 | 8.2924 | -5.2898 | 115.2016 | 115.5273 | 115.1642 | -5.7595 | 0.34278 | 0.79891 | 0.49911 | 0.43942 | 0.096637 | 0.74694 | 0.79343 | 0.22809 | 0.50435 | 1.181 | 0.69773 | 0.46965 | 0.83 | 0.46692 | 121.4837 | 121.4318 | 121.4782 | 6.1126 | -120.342 | 121.1892 | 121.5148 | 121.1517 | 14.28 | -120.4567
1147.3438 | 121.0785 | -1.5152 | 119.6365 | 1.4211e-13 | -0.018303 | 0.0019936 | 0.067767 | -0.011211 | 0.058471 | -0.0073253 | -0.00059386 | 0.001282 | 0.060766 | 0.03044 | 0.054018 | -1.3542 | 0.19371 | -1.3956 | 119.7266 | 119.6843 | 119.7213 | -1.5008 | -0.70865 | 9.6798 | -1.1507 | 119.4413 | 119.7762 | 119.0606 | -1.6339 | 0.014358 | 0.090072 | 0.16104 | 0.11957 | 0.10521 | 0.047753 | 0.084792 | -0.11875 | -0.19524 | 0.80655 | 0.36454 | 0.48329 | 0.13968 | -0.57596 | 121.2418 | 121.1995 | 121.2365 | 1.7089 | -121.1374 | 120.9565 | 121.2914 | 120.5758 | 11.195 | -121.2705
1149.0781 | 121.106 | -2.536 | 118.5562 | 1.4211e-13 | -0.018517 | 0.0022072 | 0.067554 | -0.010997 | 0.058471 | 0.015566 | -0.0010211 | 0.0010682 | 0.060766 | 0.030013 | 0.053591 | -2.3751 | 0.17997 | -2.4212 | 118.6965 | 118.6586 | 118.6957 | -2.5265 | -1.6931 | 9.3776 | -2.158 | 118.4111 | 118.7369 | 118.0624 | -2.6596 | 0.009492 | 0.14026 | 0.16087 | 0.11485 | 0.10536 | 0.1024 | 0.13951 | -0.12359 | -0.14508 | 0.84294 | 0.37803 | 0.50162 | 0.18066 | -0.49377 | 121.2325 | 121.1946 | 121.2317 | 2.716 | -121.0827 | 120.9471 | 121.2729 | 120.5984 | 11.9136 | -121.2158
1150.8281 | 121.0876 | -1.4191 | 119.751 | 1.4211e-13 | -0.017876 | 0.0019936 | 0.067981 | -0.010997 | 0.058257 | 0.0079357 | -0.0012349 | 0.0014956 | 0.060552 | 0.029799 | 0.053804 | -1.4503 | 0.20744 | -1.4918 | 119.6259 | 119.5927 | 119.6206 | -1.6016 | -0.77275 | 9.7439 | -1.2193 | 119.3452 | 119.6709 | 118.9965 | -1.7255 | -0.18251 | -0.12509 | -0.031234 | -0.072705 | 0.1098 | -0.15827 | -0.13038 | -0.30646 | -0.40583 | 0.64631 | 0.19972 | 0.50618 | -0.080072 | -0.7545 | 121.045 | 121.0118 | 121.0397 | 1.6265 | -121.3526 | 120.7642 | 121.09 | 120.4155 | 11.1629 | -121.4765
1152.5781 | 120.9549 | -5.1407 | 115.9195 | 1.4211e-13 | -0.018303 | 0.0019936 | 0.067767 | -0.011211 | 0.058471 | 0.0079357 | -0.0010211 | 0.001282 | 0.060766 | 0.030226 | 0.054018 | -4.6231 | 0.15708 | -4.692 | 116.3935 | 116.36 | 116.411 | -4.7793 | -3.8771 | 8.6816 | -4.3832 | 116.1127 | 116.4476 | 115.8693 | -4.8986 | 0.36134 | 0.47405 | 0.51756 | 0.4487 | 0.08736 | 0.44049 | 0.4915 | 0.24204 | 0.19324 | 1.2636 | 0.75745 | 0.51541 | 0.52807 | -0.050208 | 121.5342 | 121.5007 | 121.5517 | 5.2978 | -120.6988 | 121.2534 | 121.5883 | 121.01 | 13.8223 | -120.8181
1154.25 | 121.0968 | -3.36 | 117.6086 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.067554 | -0.011425 | 0.058257 | 0.0079357 | -0.0010211 | 0.00085461 | 0.060338 | 0.030226 | 0.054018 | -3.886 | 0.20286 | -3.9412 | 117.094 | 117.0697 | 117.0978 | -4.0101 | -3.1216 | 8.9563 | -3.6232 | 116.8224 | 117.1481 | 116.4187 | -4.1477 | -0.6501 | -0.51461 | -0.52602 | -0.58117 | 0.068938 | -0.53892 | -0.51085 | -0.78773 | -0.78624 | 0.23835 | -0.26318 | 0.52455 | -0.46055 | -1.1899 | 120.454 | 120.4297 | 120.4578 | 3.5629 | -121.6187 | 120.1824 | 120.5081 | 119.7787 | 12.3163 | -121.7564
1156 | 120.9778 | -5.2505 | 115.8966 | 1.4211e-13 | -0.018303 | 0.002421 | 0.067981 | -0.010997 | 0.058257 | 0.0079357 | -0.00080746 | 0.0010682 | 0.060338 | 0.029799 | 0.054018 | -5.3007 | 0.17081 | -5.3787 | 115.6885 | 115.6503 | 115.683 | -5.457 | -4.4907 | 8.4893 | -5.0288 | 115.4031 | 115.7287 | 115.2603 | -5.5717 | -0.20648 | -0.20814 | -0.050177 | -0.12818 | 0.078298 | -0.24635 | -0.21361 | -0.32118 | -0.49354 | 0.75988 | 0.22172 | 0.5429 | -0.16788 | -0.63627 | 120.939 | 120.9008 | 120.9336 | 5.4214 | -121.3536 | 120.6536 | 120.9793 | 120.5109 | 13.7398 | -121.4683
1157.6875 | 121.0281 | -6.1066 | 114.8071 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.067767 | -0.010997 | 0.058471 | 0.0079357 | -0.0012349 | 0.0017092 | 0.060552 | 0.030226 | 0.053804 | -6.1569 | 0.17997 | -6.2349 | 114.7591 | 114.7299 | 114.7673 | -6.2721 | -5.3103 | 8.2512 | -5.8622 | 114.4874 | 114.7993 | 114.2073 | -6.4097 | -0.16551 | -0.048072 | -0.050317 | -0.1283 | 0.037208 | -0.077237 | -0.039849 | -0.30309 | -0.31976 | 0.79631 | 0.24441 | 0.5475 | -0.007857 | -0.59987 | 120.8656 | 120.8365 | 120.8738 | 6.2865 | -121.0792 | 120.5939 | 120.9058 | 120.3138 | 14.3578 | -121.2168
1159.4219 | 120.7718 | -11.0092 | 109.6207 | 1.4211e-13 | -0.01873 | 0.00178 | 0.067767 | -0.010997 | 0.058257 | 0.00030522 | -0.0010211 | 0.0014956 | 0.060552 | 0.030226 | 0.054018 | -9.6136 | 0.13419 | -9.7281 | 111.1467 | 111.1125 | 111.1456 | -9.7337 | -8.6893 | 7.1386 | -9.287 | 110.8749 | 111.1868 | 110.8969 | -9.83 | 1.2755 | 1.526 | 1.3956 | 1.2811 | 0.005647 | 1.4919 | 1.5249 | 1.1792 | 1.2543 | 2.3199 | 1.7222 | 0.543 | 1.5661 | 1.2763 | 122.1559 | 122.1218 | 122.1548 | 11.1434 | -119.3544 | 121.8842 | 122.196 | 121.9061 | 18.1478 | -119.4507
1161.1562 | 120.6253 | -12.7808 | 107.9315 | 1.4211e-13 | -0.01873 | 0.002421 | 0.067554 | -0.011211 | 0.058044 | 0.0079357 | -0.00080746 | 0.00085461 | 0.060338 | 0.030226 | 0.054232 | -10.0485 | 0.10671 | -10.1401 | 110.6797 | 110.6455 | 110.7106 | -10.1687 | -9.0923 | 7.0058 | -9.7128 | 110.4537 | 110.7243 | 110.3338 | -10.2788 | 2.612 | 2.7482 | 2.7322 | 2.6406 | 0.0286 | 2.714 | 2.7791 | 2.502 | 2.5222 | 3.6885 | 3.0679 | 0.56591 | 2.7928 | 2.4022 | 123.4605 | 123.4263 | 123.4914 | 12.8875 | -118.1003 | 123.2345 | 123.5051 | 123.1145 | 19.7865 | -118.2103
1162.8906 | 120.5292 | -8.3588 | 111.9095 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.067554 | -0.010997 | 0.058044 | 0.0079357 | -0.0010211 | 0.0017092 | 0.060552 | 0.03044 | 0.053804 | -6.3446 | 0.0243 | -6.4134 | 114.2005 | 114.1484 | 114.2087 | -6.4873 | -5.4705 | 8.2466 | -6.0178 | 113.9105 | 114.2178 | 113.8684 | -6.6157 | 1.8715 | 2.291 | 2.0142 | 1.9453 | 0.073864 | 2.2389 | 2.2992 | 1.7431 | 2.001 | 2.8883 | 2.3409 | 0.59787 | 2.3083 | 1.959 | 122.5593 | 122.5071 | 122.5675 | 8.3831 | -118.3968 | 122.2692 | 122.5766 | 122.2272 | 16.6054 | -118.5252
1164.5781 | 120.7947 | -2.9755 | 117.6361 | 1.4211e-13 | -0.018517 | 0.002421 | 0.068195 | -0.010997 | 0.058471 | 0.015566 | -0.00080746 | 0.0014956 | 0.060338 | 0.030013 | 0.054018 | -2.8147 | 0.19829 | -2.8698 | 117.8907 | 117.8481 | 117.8807 | -2.989 | -1.9312 | 9.4874 | -2.4831 | 117.5916 | 117.9265 | 117.3894 | -3.0946 | -0.013526 | 0.25457 | 0.1608 | 0.10563 | 0.11915 | 0.21203 | 0.24462 | -0.11913 | -0.044521 | 1.0443 | 0.4924 | 0.61152 | 0.29035 | -0.24672 | 120.8661 | 120.8236 | 120.8562 | 3.1738 | -120.6251 | 120.5671 | 120.9019 | 120.3648 | 12.4629 | -120.7307
1166.3281 | 120.1538 | -25.2869 | 94.8807 | 1.4211e-13 | -0.01873 | 0.00178 | 0.067126 | -0.011211 | 0.058044 | 0.0079357 | -0.0012349 | 0.0010682 | 0.059484 | 0.030654 | 0.054232 | -21.4945 | -0.1909 | -21.4989 | 98.9682 | 98.8731 | 99.0718 | -21.5611 | -20.2735 | 2.917 | -21.0177 | 98.6641 | 98.971 | 98.4889 | -21.6983 | 3.7258 | 4.0875 | 3.7924 | 3.788 | 0.06225 | 3.9924 | 4.1912 | 3.5885 | 3.7834 | 5.0134 | 4.2692 | 0.68064 | 4.0904 | 3.6082 | 124.2551 | 124.1599 | 124.3587 | 25.096 | -116.4418 | 123.951 | 124.2579 | 123.7758 | 28.2039 | -116.579
1168.0781 | 120.8038 | -0.14648 | 120.6757 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.067981 | -0.011211 | 0.058044 | 0.00030522 | -0.0010211 | 0.0017092 | 0.060338 | 0.030226 | 0.054018 | -0.003531 | 0.23034 | -0.077084 | 120.7613 | 120.7374 | 120.7652 | -0.118 | 0.85269 | 10.5909 | 0.33742 | 120.4806 | 120.8201 | 120.1594 | -0.27862 | 0.02848 | 0.085665 | 0.14295 | 0.0694 | 0.04092 | 0.061782 | 0.08959 | -0.13214 | -0.19504 | 0.99917 | 0.4839 | 0.61604 | 0.14447 | -0.51622 | 120.9078 | 120.8839 | 120.9117 | 0.37682 | -120.7937 | 120.6271 | 120.9666 | 120.3059 | 10.7374 | -120.9543
1169.8281 | 120.9549 | -0.14191 | 120.7397 | 1.4211e-13 | -0.018517 | 0.0022072 | 0.067767 | -0.011211 | 0.058257 | 0.0079357 | -0.00080746 | 0.0021366 | 0.060766 | 0.030013 | 0.054018 | 0.001048 | 0.20286 | -0.072505 | 120.8758 | 120.8428 | 120.8706 | -0.10427 | 0.84811 | 10.6688 | 0.36031 | 120.5951 | 120.9209 | 120.2739 | -0.27862 | 0.037639 | 0.13604 | 0.14295 | 0.069402 | 0.031763 | 0.10301 | 0.13081 | -0.13671 | -0.14467 | 0.99002 | 0.50222 | 0.63893 | 0.18112 | -0.46584 | 121.0177 | 120.9847 | 121.0125 | 0.34477 | -120.844 | 120.737 | 121.0628 | 120.4158 | 10.8107 | -121.0184
1171.5781 | 120.8633 | -0.20599 | 120.8679 | 1.4211e-13 | -0.01873 | 0.0022072 | 0.067767 | -0.011211 | 0.058471 | 0.0079357 | -0.0010211 | 0.0017092 | 0.061193 | 0.03044 | 0.054232 | 0.005626 | 0.19829 | -0.067927 | 120.9307 | 120.8931 | 120.9301 | -0.10427 | 0.871 | 10.6871 | 0.36947 | 120.6409 | 120.9804 | 120.2419 | -0.2832 | 0.10173 | 0.062804 | 0.21162 | 0.13807 | 0.036341 | 0.025205 | 0.062159 | -0.077204 | -0.22705 | 1.077 | 0.57546 | 0.65267 | 0.11247 | -0.62607 | 121.1367 | 121.0991 | 121.1361 | 0.40428 | -120.9722 | 120.8469 | 121.1864 | 120.4478 | 10.8931 | -121.1511
1173.25 | 121.0236 | -0.13275 | 120.8359 | 1.4211e-13 | -0.018517 | 0.0022072 | 0.067767 | -0.011211 | 0.058471 | 0.00030522 | -0.00080746 | 0.001923 | 0.060979 | 0.030013 | 0.054232 | 0.001048 | 0.20286 | -0.072505 | 120.9719 | 120.9343 | 120.9621 | -0.090531 | 0.89848 | 10.7695 | 0.38321 | 120.6867 | 121.017 | 120.2602 | -0.28778 | 0.04222 | 0.13605 | 0.1338 | 0.060246 | 0.018026 | 0.098459 | 0.12625 | -0.15503 | -0.14923 | 1.0312 | 0.51596 | 0.67098 | 0.18114 | -0.57571 | 121.1047 | 121.0671 | 121.0949 | 0.33562 | -120.9264 | 120.8194 | 121.1498 | 120.3929 | 10.9022 | -121.1237
1174.9844 | 121.0373 | -0.15106 | 120.8633 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.067767 | -0.010997 | 0.058257 | 0.0079357 | -0.0010211 | 0.001923 | 0.060979 | 0.03044 | 0.054232 | -0.003531 | 0.20286 | -0.067927 | 121.004 | 120.9664 | 120.9942 | -0.10427 | 0.93053 | 10.8473 | 0.39694 | 120.7141 | 121.0536 | 120.3014 | -0.27404 | 0.046794 | 0.14064 | 0.14753 | 0.083135 | 0.036341 | 0.10305 | 0.13084 | -0.12298 | -0.14922 | 1.0816 | 0.548 | 0.67098 | 0.1903 | -0.56197 | 121.155 | 121.1174 | 121.1452 | 0.35393 | -120.9676 | 120.8652 | 121.2047 | 120.4524 | 10.9984 | -121.1374
1176.6719 | 121.0007 | -0.1831 | 120.9183 | 1.4211e-13 | -0.01873 | 0.0022072 | 0.068195 | -0.011425 | 0.058044 | 0.00030522 | -0.00080746 | 0.001923 | 0.060979 | 0.03044 | 0.054018 | 0.001048 | 0.18913 | -0.067927 | 121.0177 | 120.9801 | 121.0217 | -0.118 | 0.96258 | 10.9023 | 0.41526 | 120.7416 | 121.0628 | 120.3838 | -0.27862 | 0.065101 | 0.099439 | 0.18415 | 0.11518 | 0.050077 | 0.06185 | 0.10338 | -0.095514 | -0.17668 | 1.1457 | 0.59836 | 0.69388 | 0.14453 | -0.53449 | 121.2008 | 121.1632 | 121.2048 | 0.37223 | -121.0363 | 120.9247 | 121.2459 | 120.5669 | 11.0854 | -121.1969
1178.4219 | 121.0373 | -0.16479 | 120.9595 | 1.4211e-13 | -0.01873 | 0.0022072 | 0.067981 | -0.010997 | 0.058044 | 0.0079357 | -0.0010211 | 0.0017092 | 0.060552 | 0.03044 | 0.054232 | 0.001048 | 0.19371 | -0.067927 | 121.0498 | 121.003 | 121.0354 | -0.10885 | 0.99463 | 10.9938 | 0.43357 | 120.7599 | 121.0857 | 120.4204 | -0.2832 | 0.055948 | 0.090289 | 0.16584 | 0.096868 | 0.04092 | 0.043546 | 0.075914 | -0.1184 | -0.19957 | 1.1594 | 0.59837 | 0.71677 | 0.12622 | -0.53906 | 121.2146 | 121.1678 | 121.2002 | 0.3585 | -121.0683 | 120.9247 | 121.2505 | 120.5852 | 11.1586 | -121.2427
1180.1562 | 121.0007 | -0.1831 | 120.9641 | 1.4211e-13 | -0.01873 | 0.002421 | 0.068195 | -0.011211 | 0.058471 | 0.015566 | -0.00059386 | 0.0023502 | 0.060979 | 0.030013 | 0.054018 | 0.001048 | 0.19371 | -0.077084 | 121.0543 | 121.0259 | 121.0537 | -0.16837 | 1.0313 | 11.0442 | 0.44273 | 120.7782 | 121.104 | 120.4342 | -0.2832 | 0.014732 | 0.09029 | 0.18415 | 0.10602 | 0.091289 | 0.061864 | 0.089651 | -0.10009 | -0.18583 | 1.2144 | 0.62583 | 0.72593 | 0.13996 | -0.5299 | 121.2374 | 121.209 | 121.2368 | 0.37681 | -121.1324 | 120.9613 | 121.2871 | 120.6173 | 11.2273 | -121.2472
1181.9219 | 121.0052 | -0.19226 | 120.9824 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.067767 | -0.011211 | 0.058257 | 0.0079357 | -0.00080746 | 0.0023502 | 0.060979 | 0.03044 | 0.054018 | -0.003531 | 0.19371 | -0.072505 | 121.0727 | 121.0305 | 121.0766 | -0.14548 | 1.0633 | 11.1083 | 0.47478 | 120.7874 | 121.1223 | 120.3838 | -0.2832 | 0.046783 | 0.090293 | 0.18873 | 0.11976 | 0.072973 | 0.048131 | 0.094233 | -0.090937 | -0.19498 | 1.2556 | 0.66704 | 0.75798 | 0.13996 | -0.59857 | 121.2649 | 121.2228 | 121.2689 | 0.38597 | -121.1278 | 120.9796 | 121.3146 | 120.576 | 11.3006 | -121.2656
1183.6562 | 121.0876 | -0.1831 | 120.9915 | 1.4211e-13 | -0.018517 | 0.002421 | 0.068195 | -0.011425 | 0.058044 | 0.00030522 | -0.00059386 | 0.0021366 | 0.061193 | 0.030867 | 0.054232 | 0.001048 | 0.19371 | -0.072505 | 121.0864 | 121.0488 | 121.0858 | -0.1409 | 1.1091 | 11.2182 | 0.49309 | 120.8011 | 121.1269 | 120.4845 | -0.27862 | 0.042206 | 0.094873 | 0.18415 | 0.1106 | 0.068394 | 0.057292 | 0.094235 | -0.095514 | -0.1904 | 1.2922 | 0.6762 | 0.77171 | 0.13538 | -0.507 | 121.2695 | 121.2319 | 121.2689 | 0.37681 | -121.1324 | 120.9842 | 121.31 | 120.6676 | 11.4013 | -121.2701
1185.3438 | 121.17 | -0.14191 | 120.9824 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.068622 | -0.010997 | 0.058257 | 0.00030522 | -0.00080746 | 0.0023502 | 0.060766 | 0.030654 | 0.054232 | 0.001048 | 0.19829 | -0.067927 | 121.0955 | 121.0671 | 121.0903 | -0.13632 | 1.1411 | 11.3464 | 0.50683 | 120.8103 | 121.1315 | 120.4662 | -0.27862 | 0.005587 | 0.11319 | 0.14295 | 0.07398 | 0.068393 | 0.084763 | 0.10797 | -0.13671 | -0.17209 | 1.2831 | 0.64874 | 0.78545 | 0.14912 | -0.51616 | 121.2375 | 121.209 | 121.2322 | 0.34019 | -121.1187 | 120.9522 | 121.2734 | 120.6081 | 11.4883 | -121.261
1187.0938 | 121.1746 | -0.15564 | 120.9915 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.068195 | -0.010997 | 0.058685 | 0.015566 | -0.00038026 | 0.0023502 | 0.060979 | 0.030226 | 0.054018 | 0.010204 | 0.19371 | -0.067927 | 121.1093 | 121.0763 | 121.0995 | -0.14548 | 1.1732 | 11.4197 | 0.5343 | 120.8194 | 121.1544 | 120.4616 | -0.2832 | 0.010162 | 0.11776 | 0.16584 | 0.087713 | 0.077551 | 0.084766 | 0.10797 | -0.12756 | -0.17209 | 1.3288 | 0.68994 | 0.8175 | 0.16286 | -0.52989 | 121.2649 | 121.2319 | 121.2551 | 0.34935 | -121.137 | 120.9751 | 121.31 | 120.6173 | 11.5753 | -121.2747
1188.7812 | 121.1288 | -0.17853 | 121.0144 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.068409 | -0.011425 | 0.058044 | -0.014956 | -0.00059386 | 0.0023502 | 0.061407 | 0.03044 | 0.054659 | -0.003531 | 0.19371 | -0.077084 | 121.1184 | 121.0763 | 121.1086 | -0.12258 | 1.2236 | 11.6028 | 0.55262 | 120.8286 | 121.1635 | 120.4662 | -0.2832 | 0.055945 | 0.10403 | 0.175 | 0.10144 | 0.045499 | 0.061878 | 0.09424 | -0.10467 | -0.18582 | 1.4021 | 0.73115 | 0.83581 | 0.14912 | -0.5482 | 121.297 | 121.2548 | 121.2872 | 0.37224 | -121.137 | 121.0071 | 121.3421 | 120.6447 | 11.7813 | -121.2976
1190.5156 | 121.0876 | -0.19226 | 121.0556 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068409 | -0.011211 | 0.058257 | -0.0073253 | -0.00016666 | 0.0025638 | 0.061193 | 0.03044 | 0.054232 | -0.003531 | 0.19371 | -0.067927 | 121.123 | 121.09 | 121.1178 | -0.15921 | 1.2648 | 11.7356 | 0.57551 | 120.8377 | 121.1681 | 120.5624 | -0.28778 | 0.033046 | 0.067413 | 0.18873 | 0.12433 | 0.091288 | 0.034415 | 0.062199 | -0.095516 | -0.21786 | 1.457 | 0.76777 | 0.86329 | 0.1125 | -0.49325 | 121.3153 | 121.2823 | 121.3101 | 0.38597 | -121.2148 | 121.03 | 121.3604 | 120.7546 | 11.9279 | -121.3434
1192.2656 | 121.2204 | -0.13733 | 120.9869 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.068195 | -0.011425 | 0.058471 | 0.0079357 | -0.00080746 | 0.0029912 | 0.061193 | 0.030867 | 0.054445 | -0.003531 | 0.19371 | -0.072505 | 121.1276 | 121.0992 | 121.1224 | -0.15921 | 1.3472 | 12.0378 | 0.60298 | 120.8469 | 121.1773 | 120.5669 | -0.27404 | -0.021886 | 0.14066 | 0.1338 | 0.064824 | 0.08671 | 0.11224 | 0.13544 | -0.13671 | -0.14004 | 1.4845 | 0.74031 | 0.87702 | 0.19033 | -0.42 | 121.2649 | 121.2365 | 121.2597 | 0.33104 | -121.1462 | 120.9842 | 121.3146 | 120.7043 | 12.1751 | -121.261
1194.0156 | 121.2158 | -0.14648 | 121.0098 | 1.4211e-13 | -0.018517 | 0.0019936 | 0.068409 | -0.011425 | 0.058471 | 0.00030522 | -0.00016666 | 0.0036322 | 0.06162 | 0.030654 | 0.054232 | -0.003531 | 0.20744 | -0.077084 | 121.1413 | 121.0992 | 121.127 | -0.15464 | 1.4754 | 12.3949 | 0.62588 | 120.8561 | 121.1818 | 120.4433 | -0.2832 | -0.008152 | 0.1315 | 0.14295 | 0.0694 | 0.077552 | 0.089349 | 0.11713 | -0.13671 | -0.15377 | 1.6219 | 0.77236 | 0.90908 | 0.17202 | -0.56652 | 121.2878 | 121.2457 | 121.2734 | 0.35393 | -121.1645 | 121.0025 | 121.3283 | 120.5898 | 12.5414 | -121.293
1195.7031 | 121.1838 | -0.16479 | 121.0236 | 1.4211e-13 | -0.019158 | 0.00178 | 0.067767 | -0.011425 | 0.058471 | 0.0079357 | -0.00016666 | 0.0038458 | 0.061193 | 0.030226 | 0.054232 | -0.008109 | 0.20286 | -0.077084 | 121.1413 | 121.1038 | 121.1407 | -0.15921 | 1.5395 | 12.6101 | 0.65335 | 120.8606 | 121.1864 | 120.5166 | -0.28778 | 0.00558 | 0.11777 | 0.15669 | 0.087711 | 0.082131 | 0.080195 | 0.11713 | -0.12298 | -0.16293 | 1.7043 | 0.81814 | 0.94113 | 0.16286 | -0.50699 | 121.3061 | 121.2686 | 121.3055 | 0.36766 | -121.1828 | 121.0254 | 121.3512 | 120.6814 | 12.7749 | -121.3113
1197.4219 | 121.1472 | -0.18768 | 121.0373 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.068195 | -0.011425 | 0.058471 | 0.00030522 | -0.00016666 | 0.0040594 | 0.061407 | 0.030654 | 0.054873 | -0.008109 | 0.20286 | -0.072505 | 121.1505 | 121.1175 | 121.1453 | -0.15464 | 1.6128 | 12.8848 | 0.68082 | 120.8698 | 121.1956 | 120.4433 | -0.2832 | 0.033047 | 0.1132 | 0.17957 | 0.11518 | 0.082131 | 0.0802 | 0.10798 | -0.095515 | -0.1675 | 1.8004 | 0.8685 | 0.96402 | 0.15829 | -0.59398 | 121.3382 | 121.3052 | 121.333 | 0.39055 | -121.1919 | 121.0575 | 121.3833 | 120.631 | 13.0725 | -121.3205
1199.1562 | 121.1151 | -0.1831 | 121.0922 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.068409 | -0.011211 | 0.058471 | 0.0079357 | -0.00038026 | 0.0038458 | 0.06162 | 0.030226 | 0.054659 | -0.012688 | 0.20286 | -0.077084 | 121.1551 | 121.1221 | 121.1499 | -0.16837 | 1.6997 | 13.1596 | 0.70829 | 120.8698 | 121.2093 | 120.5166 | -0.27862 | 0.014732 | 0.062841 | 0.17042 | 0.10602 | 0.091289 | 0.029847 | 0.057628 | -0.095514 | -0.22243 | 1.8829 | 0.8914 | 0.98691 | 0.11709 | -0.57565 | 121.3382 | 121.3052 | 121.333 | 0.38597 | -121.2606 | 121.0529 | 121.3924 | 120.6997 | 13.3427 | -121.3708
1200.8438 | 121.2524 | -0.15106 | 121.0419 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.068622 | -0.011211 | 0.058257 | 0.00030522 | -0.00038026 | 0.0044868 | 0.061834 | 0.030867 | 0.054873 | -0.003531 | 0.19829 | -0.077084 | 121.1688 | 121.1221 | 121.159 | -0.17295 | 1.7913 | 13.448 | 0.73577 | 120.8789 | 121.2047 | 120.4662 | -0.28778 | -0.021889 | 0.12693 | 0.14753 | 0.073978 | 0.095867 | 0.080201 | 0.11714 | -0.13672 | -0.16292 | 1.9424 | 0.88683 | 1.0235 | 0.16287 | -0.57567 | 121.3199 | 121.2731 | 121.3101 | 0.34935 | -121.2148 | 121.03 | 121.3558 | 120.6173 | 13.5991 | -121.3296
1202.5938 | 121.2296 | -0.15106 | 121.0556 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.068409 | -0.011638 | 0.058257 | -0.0073253 | 4.6944e-05 | 0.0049142 | 0.062048 | 0.030867 | 0.0553 | -0.008109 | 0.19371 | -0.077084 | 121.1596 | 121.1266 | 121.1682 | -0.17295 | 1.9195 | 13.8006 | 0.77697 | 120.8789 | 121.2139 | 120.4937 | -0.29236 | -0.021889 | 0.10404 | 0.14295 | 0.073978 | 0.095867 | 0.071047 | 0.11256 | -0.14129 | -0.17666 | 2.0706 | 0.92804 | 1.0693 | 0.15829 | -0.56193 | 121.3107 | 121.2777 | 121.3192 | 0.34477 | -121.2286 | 121.03 | 121.365 | 120.6447 | 13.9517 | -121.348
1204.2969 | 121.257 | -0.15106 | 121.0739 | 1.4211e-13 | -0.018944 | 0.00178 | 0.068409 | -0.011211 | 0.058257 | 0.015566 | -0.00016666 | 0.0053414 | 0.062048 | 0.030654 | 0.055086 | -0.012688 | 0.20744 | -0.067927 | 121.1688 | 121.1404 | 121.1727 | -0.17295 | 2.034 | 14.0707 | 0.79987 | 120.8881 | 121.2139 | 120.4616 | -0.2832 | -0.021889 | 0.094886 | 0.13837 | 0.083135 | 0.10502 | 0.066473 | 0.098831 | -0.13214 | -0.18581 | 2.1851 | 0.95093 | 1.0831 | 0.13998 | -0.61229 | 121.3199 | 121.2914 | 121.3238 | 0.35851 | -121.2469 | 121.0392 | 121.365 | 120.6127 | 14.2218 | -121.3571
1206.0469 | 121.1884 | -0.1831 | 121.0739 | 1.4211e-13 | -0.018944 | 0.0019936 | 0.068195 | -0.011425 | 0.058257 | 0.015566 | -0.00038026 | 0.0057688 | 0.061834 | 0.030867 | 0.055086 | -0.012688 | 0.20744 | -0.077084 | 121.1825 | 121.1495 | 121.1727 | -0.14548 | 2.1851 | 14.4874 | 0.84566 | 120.8927 | 121.2139 | 120.5852 | -0.29236 | 0.037627 | 0.10862 | 0.17042 | 0.10602 | 0.068394 | 0.075631 | 0.098831 | -0.10925 | -0.18123 | 2.3682 | 1.0288 | 1.138 | 0.13998 | -0.48867 | 121.3656 | 121.3327 | 121.3559 | 0.39055 | -121.2194 | 121.0758 | 121.397 | 120.7684 | 14.6705 | -121.3663
1207.7344 | 121.1792 | -0.21057 | 121.0693 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.067981 | -0.011425 | 0.058257 | 0.00030522 | -0.00016666 | 0.0059824 | 0.062048 | 0.030654 | 0.0553 | -0.017266 | 0.19371 | -0.081662 | 121.1825 | 121.1495 | 121.1727 | -0.17753 | 2.3225 | 14.9224 | 0.87771 | 120.8881 | 121.2231 | 120.5715 | -0.29693 | 0.033041 | 0.1132 | 0.19331 | 0.12891 | 0.095868 | 0.080209 | 0.10341 | -0.086363 | -0.18123 | 2.533 | 1.0883 | 1.1746 | 0.15371 | -0.49782 | 121.3931 | 121.3601 | 121.3833 | 0.40428 | -121.2469 | 121.0987 | 121.4336 | 120.7821 | 15.1329 | -121.3663
1209.4844 | 121.2845 | -0.16937 | 121.0419 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.068409 | -0.011425 | 0.058471 | -0.014956 | -0.00038026 | 0.0066234 | 0.061834 | 0.030867 | 0.0553 | -0.017266 | 0.21202 | -0.08624 | 121.1688 | 121.1495 | 121.1819 | -0.17753 | 2.4644 | 15.2978 | 0.91891 | 120.8927 | 121.2231 | 120.5624 | -0.29236 | -0.008157 | 0.12693 | 0.15211 | 0.083133 | 0.09129 | 0.10768 | 0.14003 | -0.12298 | -0.14919 | 2.6338 | 1.0883 | 1.2113 | 0.18118 | -0.47952 | 121.3382 | 121.3189 | 121.3513 | 0.38139 | -121.2194 | 121.0621 | 121.3924 | 120.7317 | 15.4672 | -121.3342
1211.1719 | 121.2799 | -0.15106 | 121.0556 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068195 | -0.011211 | 0.058257 | 0.00030522 | -0.00038026 | 0.007478 | 0.062048 | 0.031081 | 0.055727 | -0.031001 | 0.19829 | -0.08624 | 121.1825 | 121.145 | 121.1773 | -0.18669 | 2.643 | 15.7786 | 0.94181 | 120.8927 | 121.2231 | 120.5395 | -0.30609 | -0.035626 | 0.12693 | 0.12006 | 0.064822 | 0.10045 | 0.089363 | 0.12172 | -0.15503 | -0.16292 | 2.794 | 1.0929 | 1.2479 | 0.16745 | -0.51614 | 121.3336 | 121.296 | 121.3284 | 0.34935 | -121.2423 | 121.0437 | 121.3741 | 120.6905 | 15.9297 | -121.3617
1212.8594 | 121.2753 | -0.16022 | 121.051 | 1.4211e-13 | -0.01873 | 0.0019936 | 0.068409 | -0.011425 | 0.058257 | 0.0079357 | 4.6944e-05 | 0.0079054 | 0.062475 | 0.030867 | 0.055941 | -0.021844 | 0.19371 | -0.095397 | 121.1825 | 121.1541 | 121.1865 | -0.18211 | 2.8032 | 16.0899 | 0.99217 | 120.9018 | 121.2368 | 120.4891 | -0.29236 | -0.021892 | 0.13151 | 0.13837 | 0.06482 | 0.086712 | 0.1031 | 0.13546 | -0.13214 | -0.14919 | 2.9634 | 1.1524 | 1.2845 | 0.18576 | -0.56193 | 121.3428 | 121.3143 | 121.3467 | 0.35392 | -121.2331 | 121.0621 | 121.397 | 120.6493 | 16.2502 | -121.3434
1214.6094 | 121.2936 | -0.16479 | 121.0648 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.068622 | -0.011425 | 0.058685 | 0.00030522 | -0.00016666 | 0.0083326 | 0.062261 | 0.031508 | 0.055727 | -0.031001 | 0.19829 | -0.090818 | 121.2008 | 121.1495 | 121.1865 | -0.19127 | 3.0138 | 16.4746 | 1.0425 | 120.9064 | 121.2459 | 120.4983 | -0.30609 | -0.026472 | 0.13609 | 0.13379 | 0.073977 | 0.10045 | 0.084787 | 0.12172 | -0.1413 | -0.15834 | 3.1786 | 1.2073 | 1.3486 | 0.18119 | -0.5665 | 121.3656 | 121.3143 | 121.3513 | 0.36308 | -121.256 | 121.0712 | 121.4107 | 120.663 | 16.6394 | -121.3709
1216.2969 | 121.2845 | -0.16022 | 121.0648 | 1.4211e-13 | -0.018944 | 0.0019936 | 0.068195 | -0.011425 | 0.058257 | 0.0079357 | -0.00016666 | 0.00876 | 0.062689 | 0.030867 | 0.055941 | -0.03558 | 0.19829 | -0.095397 | 121.1963 | 121.1587 | 121.1911 | -0.18669 | 3.1741 | 16.8454 | 1.0883 | 120.9064 | 121.2322 | 120.4754 | -0.30151 | -0.026471 | 0.13151 | 0.12464 | 0.06482 | 0.091291 | 0.093944 | 0.1263 | -0.1413 | -0.15834 | 3.3343 | 1.2485 | 1.3898 | 0.16745 | -0.5894 | 121.3565 | 121.3189 | 121.3513 | 0.3585 | -121.2514 | 121.0666 | 121.3924 | 120.6356 | 17.0056 | -121.3663
1218.0312 | 121.2662 | -0.15564 | 121.0648 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.068409 | -0.011211 | 0.058471 | 0.0079357 | 0.00047434 | 0.0091872 | 0.062902 | 0.031295 | 0.056155 | -0.021844 | 0.19829 | -0.090818 | 121.1963 | 121.1633 | 121.1956 | -0.18211 | 3.4076 | 17.4315 | 1.1387 | 120.9156 | 121.2505 | 120.5944 | -0.30151 | -0.026469 | 0.13151 | 0.1338 | 0.064822 | 0.091291 | 0.098523 | 0.13088 | -0.14587 | -0.14918 | 3.5632 | 1.2943 | 1.4402 | 0.18577 | -0.47035 | 121.3519 | 121.3189 | 121.3513 | 0.35393 | -121.2469 | 121.0712 | 121.4062 | 120.75 | 17.5871 | -121.3663
1219.7031 | 121.3303 | -0.16479 | 121.0693 | 1.4211e-13 | -0.018944 | 0.0019936 | 0.068409 | -0.011425 | 0.058471 | -0.0073253 | 4.6944e-05 | 0.010256 | 0.062689 | 0.031508 | 0.055941 | -0.026423 | 0.20286 | -0.090818 | 121.2054 | 121.1679 | 121.2002 | -0.18211 | 3.6091 | 18.0496 | 1.1982 | 120.9156 | 121.2551 | 120.6219 | -0.30151 | -0.017314 | 0.13609 | 0.13837 | 0.073977 | 0.091291 | 0.098524 | 0.13088 | -0.13672 | -0.15376 | 3.7739 | 1.363 | 1.4997 | 0.18576 | -0.44746 | 121.3702 | 121.3327 | 121.365 | 0.36766 | -121.2514 | 121.0804 | 121.4199 | 120.7867 | 18.2144 | -121.3708
1221.4531 | 121.1929 | -0.21973 | 121.1197 | 1.4211e-13 | -0.018944 | 0.002421 | 0.068622 | -0.011211 | 0.058257 | 0.00030522 | 0.00047434 | 0.010469 | 0.062689 | 0.031081 | 0.056368 | -0.031001 | 0.20744 | -0.099975 | 121.21 | 121.1724 | 121.2048 | -0.19127 | 3.8746 | 18.7273 | 1.2532 | 120.9156 | 121.2459 | 120.4983 | -0.31525 | 0.02846 | 0.090316 | 0.18873 | 0.11975 | 0.091292 | 0.052749 | 0.085105 | -0.095523 | -0.20412 | 4.0944 | 1.4729 | 1.5684 | 0.12625 | -0.62144 | 121.4297 | 121.3922 | 121.4245 | 0.42717 | -121.311 | 121.1353 | 121.4657 | 120.718 | 18.947 | -121.4349
1223.2031 | 121.2204 | -0.21515 | 121.0876 | 1.4211e-13 | -0.018944 | 0.0019936 | 0.068409 | -0.011425 | 0.058471 | 0.0079357 | 0.00068794 | 0.010897 | 0.062475 | 0.031081 | 0.057436 | -0.03558 | 0.20286 | -0.095397 | 121.2008 | 121.1587 | 121.2048 | -0.19127 | 5.3352 | 18.4159 | 1.3081 | 120.9156 | 121.2551 | 120.5852 | -0.31067 | 0.023882 | 0.1132 | 0.17957 | 0.11975 | 0.09587 | 0.071056 | 0.11715 | -0.095522 | -0.17207 | 5.5504 | 1.5233 | 1.6188 | 0.16745 | -0.5024 | 121.416 | 121.3739 | 121.4199 | 0.41801 | -121.2789 | 121.1307 | 121.4702 | 120.8004 | 18.6311 | -121.3983
1224.8906 | 121.1929 | -0.20142 | 121.0968 | 1.4211e-13 | -0.019158 | 0.0022072 | 0.068622 | -0.011211 | 0.058685 | 0.00030522 | 0.00068794 | 0.010897 | 0.062689 | 0.031081 | 0.057436 | -0.03558 | 0.19829 | -0.10455 | 121.2008 | 121.177 | 121.2094 | -0.19585 | 5.3627 | 18.2603 | 1.3447 | 120.9202 | 121.2551 | 120.544 | -0.30609 | 0.00557 | 0.10405 | 0.16584 | 0.096863 | 0.091293 | 0.080216 | 0.11257 | -0.10468 | -0.17665 | 5.5641 | 1.5462 | 1.6508 | 0.1583 | -0.55276 | 121.4023 | 121.3784 | 121.4108 | 0.3997 | -121.2926 | 121.1216 | 121.4565 | 120.7455 | 18.4617 | -121.4029
1226.6562 | 121.1884 | -0.2243 | 121.1243 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068409 | -0.011638 | 0.058471 | 0.0079357 | 0.00047434 | 0.011751 | 0.062902 | 0.031295 | 0.057864 | -0.044736 | 0.19829 | -0.095397 | 121.21 | 121.177 | 121.2048 | -0.19127 | 6.0953 | 18.709 | 1.4134 | 120.911 | 121.2551 | 120.631 | -0.31525 | 0.033037 | 0.085738 | 0.17957 | 0.12891 | 0.09587 | 0.05275 | 0.080527 | -0.090946 | -0.21327 | 6.3196 | 1.6377 | 1.7287 | 0.13083 | -0.49323 | 121.4343 | 121.4013 | 121.4291 | 0.42259 | -121.3155 | 121.1353 | 121.4794 | 120.8553 | 18.9333 | -121.4395
1228.3438 | 121.2799 | -0.19684 | 121.0922 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068195 | -0.011211 | 0.058257 | 0.00030522 | 0.00068794 | 0.012606 | 0.062902 | 0.031295 | 0.057436 | -0.044736 | 0.19371 | -0.099975 | 121.21 | 121.1816 | 121.214 | -0.205 | 5.523 | 19.3866 | 1.4729 | 120.9247 | 121.2551 | 120.5303 | -0.31525 | -0.008166 | 0.11778 | 0.1521 | 0.096863 | 0.10503 | 0.089373 | 0.12173 | -0.11841 | -0.16749 | 5.7198 | 1.6698 | 1.7882 | 0.16288 | -0.56192 | 121.4068 | 121.3784 | 121.4108 | 0.39055 | -121.2972 | 121.1216 | 121.4519 | 120.7271 | 19.5835 | -121.4075
1230.0938 | 121.1975 | -0.23804 | 121.106 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068195 | -0.011638 | 0.058471 | 0.0079357 | 0.00068794 | 0.01346 | 0.062902 | 0.031508 | 0.057864 | -0.040158 | 0.19829 | -0.10913 | 121.2008 | 121.177 | 121.2094 | -0.205 | 6.2693 | 19.5698 | 1.5508 | 120.9202 | 121.2459 | 120.5028 | -0.32899 | 0.033033 | 0.094892 | 0.19788 | 0.1289 | 0.095872 | 0.071061 | 0.10342 | -0.090949 | -0.1858 | 6.5073 | 1.7888 | 1.8798 | 0.13999 | -0.60312 | 121.4389 | 121.4151 | 121.4474 | 0.43632 | -121.311 | 121.1582 | 121.484 | 120.7409 | 19.8078 | -121.4349
1231.7656 | 121.2936 | -0.26093 | 121.0327 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068622 | -0.011425 | 0.058044 | 0.0079357 | 0.0011151 | 0.014529 | 0.06333 | 0.031936 | 0.059573 | -0.10426 | 0.19829 | -0.17323 | 121.1413 | 121.1129 | 121.1499 | -0.25995 | 8.0184 | 19.4782 | 1.5416 | 120.8561 | 121.191 | 120.5852 | -0.38393 | 0.000974 | 0.10862 | 0.15667 | 0.087698 | 0.086724 | 0.080198 | 0.11714 | -0.12301 | -0.17666 | 8.2793 | 1.8025 | 1.9256 | 0.15829 | -0.44747 | 121.4023 | 121.3738 | 121.4108 | 0.45921 | -121.2927 | 121.117 | 121.4519 | 120.8462 | 19.7391 | -121.4166
1233.5 | 121.312 | -0.2655 | 121.0052 | 1.4211e-13 | -0.018944 | 0.0019936 | 0.068622 | -0.011425 | 0.058257 | 0.00030522 | 0.0011151 | 0.015811 | 0.06333 | 0.031722 | 0.059787 | -0.10883 | 0.20286 | -0.17323 | 121.1413 | 121.1129 | 121.1407 | -0.26911 | 9.0257 | 19.6934 | 1.6103 | 120.8606 | 121.1864 | 120.4387 | -0.38851 | -0.003606 | 0.13608 | 0.15667 | 0.092276 | 0.095882 | 0.10766 | 0.13545 | -0.12301 | -0.14462 | 9.2912 | 1.8758 | 1.9988 | 0.18117 | -0.56652 | 121.4068 | 121.3784 | 121.4062 | 0.46837 | -121.2744 | 121.1261 | 121.4519 | 120.7042 | 19.9589 | -121.3938
1235.1719 | 121.2845 | -0.27008 | 121.0281 | 1.4211e-13 | -0.019372 | 0.0022072 | 0.068836 | -0.011425 | 0.058257 | 0.0079357 | 0.00090154 | 0.017093 | 0.06397 | 0.032149 | 0.060855 | -0.10883 | 0.20286 | -0.16865 | 121.1413 | 121.1129 | 121.1453 | -0.26911 | 9.2317 | 17.6009 | 1.6607 | 120.8561 | 121.1864 | 120.6036 | -0.38851 | 0.000972 | 0.11319 | 0.16125 | 0.10143 | 0.10046 | 0.084776 | 0.11714 | -0.11843 | -0.17208 | 9.5018 | 1.9307 | 2.0492 | 0.15828 | -0.42458 | 121.4114 | 121.383 | 121.4154 | 0.47295 | -121.2972 | 121.1261 | 121.4565 | 120.8736 | 17.871 | -121.4166
1236.9219 | 121.2341 | -0.27466 | 121.051 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068836 | -0.011425 | 0.058471 | -0.0073253 | 0.0013289 | 0.018161 | 0.064825 | 0.031936 | 0.061923 | -0.10883 | 0.19829 | -0.17323 | 121.1413 | 121.1175 | 121.1453 | -0.26911 | 9.7079 | 17.8299 | 1.8209 | 120.8515 | 121.1818 | 120.4479 | -0.38851 | 0.005549 | 0.090305 | 0.16582 | 0.10143 | 0.095882 | 0.066467 | 0.094248 | -0.11385 | -0.19955 | 9.9826 | 2.0956 | 2.2094 | 0.13082 | -0.60313 | 121.416 | 121.3922 | 121.4199 | 0.47294 | -121.3201 | 121.1261 | 121.4565 | 120.7225 | 18.1045 | -121.4395
1238.6719 | 121.257 | -0.29755 | 121.0373 | 1.4211e-13 | -0.018944 | 0.0022072 | 0.068622 | -0.011211 | 0.058685 | -0.0073253 | 0.0015425 | 0.019016 | 0.065252 | 0.031936 | 0.060855 | -0.11341 | 0.19829 | -0.18696 | 121.1413 | 121.0992 | 121.1499 | -0.26911 | 10.3535 | 20.8014 | 1.9903 | 120.8606 | 121.191 | 120.4479 | -0.39767 | 0.028437 | 0.10404 | 0.18413 | 0.11058 | 0.082147 | 0.061884 | 0.11256 | -0.10012 | -0.17666 | 10.6511 | 2.2879 | 2.388 | 0.15371 | -0.5894 | 121.4389 | 121.3967 | 121.4474 | 0.49583 | -121.3064 | 121.1582 | 121.4885 | 120.7454 | 21.099 | -121.435
1240.3594 | 121.2708 | -0.3067 | 121.0281 | 1.4211e-13 | -0.01873 | 0.00178 | 0.068195 | -0.011425 | 0.058257 | 0.0079357 | 0.0015425 | 0.019443 | 0.067389 | 0.032363 | 0.060641 | -0.12257 | 0.20744 | -0.18238 | 121.1368 | 121.1083 | 121.1453 | -0.27827 | 9.9506 | 20.3207 | 2.1735 | 120.8515 | 121.1818 | 120.4342 | -0.40225 | 0.028435 | 0.10861 | 0.18413 | 0.12432 | 0.095883 | 0.080197 | 0.11714 | -0.095545 | -0.17666 | 10.2573 | 2.4802 | 2.5757 | 0.15371 | -0.59398 | 121.4435 | 121.415 | 121.452 | 0.51415 | -121.3064 | 121.1582 | 121.4885 | 120.7409 | 20.6274 | -121.4304
1242.1094 | 121.3531 | -0.27466 | 121.0052 | 1.4211e-13 | -0.019372 | 0.0022072 | 0.068836 | -0.011425 | 0.058471 | 0.00030522 | 0.0019697 | 0.020725 | 0.067603 | 0.031936 | 0.060641 | -0.11799 | 0.19829 | -0.18696 | 121.1368 | 121.1129 | 121.1499 | -0.28285 | 10.1429 | 20.5359 | 2.2971 | 120.8515 | 121.1864 | 120.4662 | -0.40225 | -0.008188 | 0.1315 | 0.15667 | 0.087696 | 0.095884 | 0.10766 | 0.1446 | -0.12759 | -0.15377 | 10.4175 | 2.5718 | 2.6994 | 0.18117 | -0.53905 | 121.4114 | 121.3876 | 121.4245 | 0.47294 | -121.2881 | 121.1261 | 121.4611 | 120.7409 | 20.8105 | -121.4075
1243.8438 | 121.3074 | -0.28839 | 121.0327 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068409 | -0.011211 | 0.058257 | 0.0079357 | 0.0019697 | 0.023716 | 0.069312 | 0.032363 | 0.061282 | -0.11799 | 0.19829 | -0.18238 | 121.1459 | 121.1175 | 121.1544 | -0.27369 | 11.2921 | 20.9663 | 2.5444 | 120.8606 | 121.191 | 120.4616 | -0.39309 | 0.014703 | 0.11319 | 0.1704 | 0.10601 | 0.091304 | 0.084777 | 0.12172 | -0.1047 | -0.17208 | 11.5805 | 2.8327 | 2.9374 | 0.15829 | -0.57109 | 121.4343 | 121.4059 | 121.4428 | 0.48668 | -121.3064 | 121.149 | 121.4794 | 120.75 | 21.2547 | -121.4258
1245.5781 | 121.2021 | -0.30212 | 121.0602 | 1.4211e-13 | -0.019372 | 0.0019936 | 0.068622 | -0.011425 | 0.058471 | 0.0079357 | 0.0021833 | 0.031194 | 0.069953 | 0.032363 | 0.062778 | -0.11341 | 0.19371 | -0.17781 | 121.1551 | 121.1358 | 121.1682 | -0.26453 | 13.2427 | 22.0743 | 2.7275 | 120.8744 | 121.2002 | 120.4662 | -0.38851 | 0.037594 | 0.094884 | 0.18871 | 0.12432 | 0.086724 | 0.075627 | 0.10798 | -0.086387 | -0.18581 | 13.5448 | 3.0296 | 3.116 | 0.13998 | -0.59398 | 121.4572 | 121.4379 | 121.4703 | 0.49583 | -121.3247 | 121.1765 | 121.5023 | 120.7683 | 22.3764 | -121.4487
1247.3281 | 121.2387 | -0.26093 | 121.1014 | 1.4211e-13 | -0.019158 | 0.00178 | 0.068409 | -0.011638 | 0.058257 | -0.0073253 | 0.0017561 | 0.011965 | 0.070807 | 0.032577 | 0.058718 | -0.076785 | 0.19829 | -0.1366 | 121.1963 | 121.1679 | 121.2002 | -0.24163 | 6.4616 | 15.5863 | 2.7138 | 120.911 | 121.2414 | 120.4845 | -0.35188 | 0.01929 | 0.094891 | 0.18414 | 0.12432 | 0.10503 | 0.066481 | 0.098838 | -0.090955 | -0.19038 | 6.7225 | 2.9747 | 3.0656 | 0.13999 | -0.61686 | 121.4572 | 121.4288 | 121.4611 | 0.45921 | -121.343 | 121.1719 | 121.5023 | 120.7454 | 15.8472 | -121.4533
1249 | 121.2158 | -0.30212 | 121.0602 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068622 | -0.011425 | 0.058471 | 0.015566 | 0.0021833 | 0.05726 | 0.070594 | 0.03279 | 0.065342 | -0.11341 | 0.20286 | -0.18238 | 121.1551 | 121.1312 | 121.1682 | -0.26911 | 17.5421 | 25.316 | 3.0434 | 120.8652 | 121.1956 | 120.4708 | -0.39767 | 0.033015 | 0.094884 | 0.18871 | 0.11974 | 0.086725 | 0.071048 | 0.10798 | -0.095544 | -0.19497 | 17.8442 | 3.3456 | 3.4411 | 0.1354 | -0.5894 | 121.4572 | 121.4334 | 121.4703 | 0.50499 | -121.3293 | 121.1673 | 121.4977 | 120.7729 | 25.6182 | -121.4578
1250.7344 | 121.2387 | -0.29297 | 121.051 | 1.4211e-13 | -0.019372 | 0.0019936 | 0.068409 | -0.011425 | 0.058257 | 0.0079357 | 0.0023971 | 0.077344 | 0.071235 | 0.032577 | 0.067692 | -0.099677 | 0.21202 | -0.17323 | 121.1642 | 121.1404 | 121.1682 | -0.25995 | 20.3122 | 25.5725 | 3.2724 | 120.8652 | 121.2002 | 120.4479 | -0.37935 | 0.033018 | 0.1132 | 0.19329 | 0.11974 | 0.086724 | 0.089362 | 0.11714 | -0.086384 | -0.18581 | 20.6052 | 3.5653 | 3.6517 | 0.14913 | -0.60313 | 121.4572 | 121.4334 | 121.4611 | 0.50499 | -121.311 | 121.1582 | 121.4931 | 120.7409 | 25.8654 | -121.4304
1252.4844 | 121.3028 | -0.27924 | 121.0052 | 1.4211e-13 | -0.019585 | 0.0015662 | 0.068409 | -0.011638 | 0.05783 | 0.0079357 | 0.0023971 | 0.10341 | 0.072089 | 0.033004 | 0.068546 | -0.11341 | 0.19829 | -0.17781 | 121.1505 | 121.1175 | 121.1636 | -0.27827 | 21.5622 | 26.1677 | 3.4601 | 120.8515 | 121.1864 | 120.5211 | -0.39767 | 0.000969 | 0.14524 | 0.16582 | 0.10143 | 0.10046 | 0.11224 | 0.15834 | -0.11843 | -0.15377 | 21.8414 | 3.7393 | 3.8578 | 0.18117 | -0.4841 | 121.4297 | 121.3967 | 121.4428 | 0.47752 | -121.2835 | 121.1307 | 121.4657 | 120.8004 | 26.4469 | -121.4029
1254.1719 | 121.2845 | -0.37537 | 120.9366 | 1.4211e-13 | -0.019158 | 0.0022072 | 0.068409 | -0.011425 | 0.058471 | -0.014956 | 0.0021833 | 0.18994 | 0.073371 | 0.033431 | 0.070256 | -0.19124 | 0.20286 | -0.25106 | 121.0727 | 121.0396 | 121.0766 | -0.34237 | 23.3067 | 26.7675 | 3.6753 | 120.7599 | 121.0903 | 120.3929 | -0.47093 | 0.032994 | 0.13607 | 0.18412 | 0.12431 | 0.091314 | 0.10307 | 0.14001 | -0.095564 | -0.17668 | 23.682 | 4.0507 | 4.1462 | 0.15369 | -0.54364 | 121.448 | 121.415 | 121.452 | 0.57823 | -121.279 | 121.1353 | 121.4656 | 120.7683 | 27.1429 | -121.4075
1255.9219 | 121.2158 | -0.2243 | 121.0968 | 1.4211e-13 | -0.019372 | 0.00178 | 0.068622 | -0.011211 | 0.058898 | 0.0079357 | 0.0034653 | 0.018802 | 0.077003 | 0.03279 | 0.058932 | -0.049315 | 0.20286 | -0.12287 | 121.2054 | 121.1724 | 121.214 | -0.20958 | 4.5889 | 13.6861 | 3.4921 | 120.9156 | 121.2505 | 120.5166 | -0.33814 | 0.014721 | 0.10863 | 0.17499 | 0.10144 | 0.086717 | 0.075637 | 0.11715 | -0.11384 | -0.18123 | 4.8132 | 3.7165 | 3.8303 | 0.15372 | -0.58023 | 121.4297 | 121.3967 | 121.4383 | 0.42717 | -121.3064 | 121.1399 | 121.4748 | 120.7409 | 13.9104 | -121.4349
1257.6094 | 121.225 | -0.25635 | 121.1243 | 1.4211e-13 | -0.019158 | 0.00178 | 0.068622 | -0.011211 | 0.058471 | 0.00030522 | 0.0032515 | 0.028844 | 0.077858 | 0.033004 | 0.060428 | -0.06305 | 0.20286 | -0.12287 | 121.21 | 121.1816 | 121.2185 | -0.22332 | 6.8645 | 15.0689 | 3.6524 | 120.9247 | 121.2505 | 120.5349 | -0.33814 | 0.033028 | 0.085738 | 0.1933 | 0.13348 | 0.10045 | 0.057329 | 0.094263 | -0.081796 | -0.19954 | 7.1209 | 3.9088 | 3.9905 | 0.12626 | -0.58939 | 121.4664 | 121.4379 | 121.4749 | 0.45921 | -121.3476 | 121.1811 | 121.5069 | 120.7912 | 15.3252 | -121.4624
1259.3438 | 121.3257 | -0.22888 | 121.0739 | 1.4211e-13 | -0.019158 | 0.00178 | 0.068836 | -0.011211 | 0.058257 | 0.00030522 | 0.0028243 | 0.076917 | 0.07273 | 0.034072 | 0.072178 | -0.085942 | 0.20744 | -0.15491 | 121.1917 | 121.1587 | 121.1956 | -0.23706 | 24.749 | 27.555 | 4.5498 | 120.8927 | 121.2368 | 120.5028 | -0.35646 | -0.008174 | 0.11778 | 0.14294 | 0.073968 | 0.082142 | 0.084788 | 0.12172 | -0.12758 | -0.18123 | 24.9779 | 4.7787 | 4.9063 | 0.16287 | -0.57108 | 121.4206 | 121.3876 | 121.4245 | 0.43633 | -121.311 | 121.1216 | 121.4657 | 120.7317 | 27.7839 | -121.4304
1261.0938 | 121.225 | -0.30212 | 121.0556 | 1.4211e-13 | -0.019585 | 0.00178 | 0.068409 | -0.011211 | 0.058257 | 0.023196 | 0.0034653 | 0.36771 | 0.081276 | 0.033431 | 0.067264 | -0.34691 | 0.22576 | -0.40672 | 120.8895 | 120.8611 | 120.8935 | -0.50721 | 17.8214 | 21.6256 | 4.0462 | 120.563 | 120.8934 | 120.1778 | -0.63577 | -0.20509 | -0.16609 | -0.044786 | -0.1046 | 0.10049 | -0.19453 | -0.16215 | -0.33364 | -0.49257 | 18.1235 | 4.3483 | 4.6819 | -0.16221 | -0.87785 | 121.1916 | 121.1632 | 121.1956 | 0.52788 | -121.5628 | 120.8652 | 121.1955 | 120.4799 | 21.9277 | -121.6914
1262.8438 | 121.2387 | -0.20599 | 121.1197 | 1.4211e-13 | -0.019585 | 0.00178 | 0.068836 | -0.011425 | 0.058471 | 0.00030522 | -0.0025167 | 0.0066234 | 0.0206 | 0.03044 | -0.010719 | -0.031001 | 0.22576 | -0.10455 | 121.21 | 121.1908 | 121.214 | -0.24621 | -0.012689 | -0.054586 | -0.1113 | 0.21728 | 0.37542 | 0.32367 | -0.31525 | -0.04022 | 0.090316 | 0.17499 | 0.10144 | 0.14166 | 0.071065 | 0.094262 | -0.10926 | -120.9024 | 0.19331 | 0.094698 | 0.20395 | -120.7443 | -120.796 | 121.416 | 121.3967 | 121.4199 | 0.43175 | -121.3659 | 0.42328 | 0.58141 | 0.52967 | 0.15141 | -121.4349
1264.5938 | 121.2479 | -0.21973 | 121.1838 | 1.4211e-13 | -0.019585 | 0.00178 | 0.068836 | -0.011425 | 0.058471 | 0.00030522 | -0.0025167 | 0.0066234 | 0.018463 | 0.03044 | -0.010505 | -0.021844 | 0.23492 | -0.090818 | 121.2558 | 121.232 | 121.2597 | -0.18211 | -0.003531 | -0.059164 | -0.097559 | 0.14861 | 0.29758 | 0.255 | -0.31067 | 0.037618 | 0.072013 | 0.19788 | 0.12891 | 0.091291 | 0.048188 | 0.075961 | -0.090944 | -121.0352 | 0.2162 | 0.12217 | 0.21311 | -120.8862 | -120.9288 | 121.4755 | 121.4517 | 121.4795 | 0.45464 | -121.3659 | 0.36833 | 0.51731 | 0.47472 | 0.16056 | -121.4944
1266.2656 | 121.3531 | -0.16022 | 121.1288 | 1.4211e-13 | -0.019158 | 0.00178 | 0.068836 | -0.011211 | 0.058257 | 0.0079357 | -0.0023031 | 0.0064098 | 0.01825 | 0.03044 | -0.010719 | -0.031001 | 0.23034 | -0.090818 | 121.2649 | 121.2411 | 121.2689 | -0.18669 | 0.001048 | -0.0729 | -0.1113 | 0.13487 | 0.28842 | 0.24126 | -0.31067 | -0.026471 | 0.1361 | 0.12922 | 0.069399 | 0.09587 | 0.11228 | 0.14005 | -0.15045 | -120.994 | 0.16126 | 0.048921 | 0.19937 | -120.8404 | -120.8876 | 121.4252 | 121.4013 | 121.4291 | 0.39055 | -121.3155 | 0.29509 | 0.44864 | 0.40148 | 0.087317 | -121.4395
1268 | 121.312 | -0.17853 | 121.17 | 1.4211e-13 | -0.019372 | 0.00178 | 0.068409 | -0.011425 | 0.058471 | 0.00030522 | -0.0025167 | 0.006196 | 0.018463 | 0.030226 | -0.010505 | -0.040158 | 0.22576 | -0.090818 | 121.2787 | 121.2457 | 121.2826 | -0.17295 | -0.003531 | -0.068322 | -0.10214 | 0.13487 | 0.28842 | 0.24126 | -0.30151 | 0.005577 | 0.10864 | 0.13837 | 0.08771 | 0.082133 | 0.075658 | 0.11259 | -0.12298 | -121.0352 | 0.175 | 0.07639 | 0.19937 | -120.8816 | -120.9288 | 121.4572 | 121.4242 | 121.4612 | 0.40429 | -121.343 | 0.3134 | 0.46695 | 0.41979 | 0.11021 | -121.4716
1269.7344 | 121.3165 | -0.17395 | 121.1746 | 1.4211e-13 | -0.019372 | 0.0019936 | 0.068622 | -0.011638 | 0.058044 | 0.0079357 | -0.0025167 | 0.006196 | 0.018677 | 0.03044 | -0.010292 | -0.026423 | 0.20744 | -0.081662 | 121.297 | 121.2594 | 121.2872 | -0.17753 | 0.001048 | -0.050007 | -0.092981 | 0.13029 | 0.28842 | 0.2321 | -0.30151 | -0.00358 | 0.12237 | 0.14753 | 0.092288 | 0.095868 | 0.084817 | 0.11259 | -0.12756 | -121.0443 | 0.175 | 0.080969 | 0.20853 | -120.8862 | -120.9425 | 121.4709 | 121.4334 | 121.4612 | 0.38139 | -121.3522 | 0.30424 | 0.46237 | 0.40605 | 0.12394 | -121.4761
1271.5 | 121.4081 | -0.1831 | 121.1517 | 1.4211e-13 | -0.019372 | 0.0019936 | 0.068622 | -0.011211 | 0.058471 | 0.015566 | -0.0027303 | 0.0053414 | 0.01825 | 0.03044 | -0.010505 | -0.017266 | 0.20286 | -0.081662 | 121.2878 | 121.2594 | 121.3009 | -0.15464 | 0.005626 | -0.063743 | -0.097559 | 0.12114 | 0.27011 | 0.20005 | -0.31067 | 0.028469 | 0.13611 | 0.16584 | 0.10144 | 0.072974 | 0.10771 | 0.14921 | -0.12757 | -121.0306 | 0.18873 | 0.085546 | 0.21311 | -120.8816 | -120.9517 | 121.4709 | 121.4425 | 121.4841 | 0.38597 | -121.3064 | 0.30424 | 0.45321 | 0.38316 | 0.11936 | -121.4624
1273.1875 | 121.3715 | -0.15106 | 121.17 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068836 | -0.011211 | 0.058685 | 0.00030522 | -0.0020893 | 0.0051278 | 0.01825 | 0.030013 | -0.010505 | -0.026423 | 0.20286 | -0.090818 | 121.2924 | 121.264 | 121.3009 | -0.17753 | -0.012689 | -0.059164 | -0.092981 | 0.12571 | 0.27011 | 0.053537 | -0.30151 | -0.026468 | 0.12237 | 0.12464 | 0.060244 | 0.086712 | 0.093974 | 0.1309 | -0.15045 | -121.0443 | 0.13837 | 0.058081 | 0.20853 | -120.8999 | -121.1165 | 121.4435 | 121.4151 | 121.452 | 0.35393 | -121.3476 | 0.27678 | 0.42117 | 0.2046 | 0.091898 | -121.4716
1274.9219 | 121.3623 | -0.16937 | 121.1517 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068622 | -0.011425 | 0.058257 | -0.0073253 | -0.0025167 | 0.005555 | 0.018463 | 0.03044 | -0.010719 | -0.031001 | 0.20744 | -0.081662 | 121.3016 | 121.2686 | 121.3101 | -0.17295 | -0.00811 | -0.063743 | -0.092981 | 0.12571 | 0.26553 | 0.085587 | -0.30151 | -0.003578 | 0.14984 | 0.13837 | 0.087711 | 0.091289 | 0.11686 | 0.15837 | -0.13214 | -121.026 | 0.16126 | 0.076392 | 0.20853 | -120.8862 | -121.0661 | 121.4709 | 121.438 | 121.4795 | 0.37682 | -121.3247 | 0.29509 | 0.4349 | 0.25496 | 0.10563 | -121.4532
1276.6719 | 121.2753 | -0.21057 | 121.2341 | 1.4211e-13 | -0.019158 | 0.0015662 | 0.06905 | -0.011425 | 0.058471 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.03044 | -0.010292 | -0.031001 | 0.20286 | -0.090818 | 121.297 | 121.2778 | 121.3147 | -0.17753 | -0.00811 | -0.068322 | -0.070087 | 0.11656 | 0.26095 | 0.067272 | -0.30609 | 0.033041 | 0.062864 | 0.17957 | 0.11975 | 0.086712 | 0.043623 | 0.080551 | -0.095521 | -121.1176 | 0.20246 | 0.14048 | 0.236 | -120.9732 | -121.1669 | 121.5076 | 121.4883 | 121.5253 | 0.41344 | -121.4117 | 0.32713 | 0.47152 | 0.27784 | 0.14225 | -121.5402
1278.3594 | 121.4264 | -0.15106 | 121.1746 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068409 | -0.011425 | 0.058044 | 0.00030522 | -0.0025167 | 0.0051278 | 0.018463 | 0.030654 | -0.010719 | -0.026423 | 0.20286 | -0.072505 | 121.3062 | 121.2823 | 121.3193 | -0.17753 | -0.003531 | -0.045428 | -0.074666 | 0.11656 | 0.26095 | 0.026065 | -0.31067 | -0.026468 | 0.13153 | 0.12464 | 0.078557 | 0.10502 | 0.10771 | 0.14464 | -0.15961 | -121.0581 | 0.14753 | 0.076396 | 0.236 | -120.9137 | -121.1486 | 121.4572 | 121.4334 | 121.4703 | 0.35393 | -121.3522 | 0.26762 | 0.41201 | 0.17713 | 0.10563 | -121.4853
1280.0938 | 121.3943 | -0.16022 | 121.1792 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068409 | -0.011425 | 0.058257 | 0.015566 | -0.0027303 | 0.0049142 | 0.018677 | 0.030654 | -0.010292 | -0.026423 | 0.20744 | -0.081662 | 121.3062 | 121.2778 | 121.3238 | -0.18211 | -0.00811 | -0.040849 | -0.070087 | 0.11198 | 0.26553 | 0.090166 | -0.30151 | -0.021892 | 0.12695 | 0.13379 | 0.078555 | 0.10045 | 0.098555 | 0.14464 | -0.1413 | -121.0672 | 0.15211 | 0.09013 | 0.23143 | -120.9137 | -121.089 | 121.4664 | 121.438 | 121.4841 | 0.36766 | -121.3613 | 0.2722 | 0.42575 | 0.25038 | 0.11937 | -121.4807
1281.8438 | 121.2845 | -0.20599 | 121.225 | 1.4211e-13 | -0.019158 | 0.0019936 | 0.068622 | -0.011638 | 0.058471 | 0.015566 | -0.0023031 | 0.0051278 | 0.018677 | 0.030226 | -0.010719 | -0.021844 | 0.20286 | -0.08624 | 121.3107 | 121.2915 | 121.3193 | -0.15921 | -0.003531 | -0.036271 | -0.065509 | 0.10282 | 0.24721 | -0.005985 | -0.31067 | 0.046779 | 0.085754 | 0.18415 | 0.11975 | 0.072975 | 0.066515 | 0.094284 | -0.10468 | -121.1222 | 0.20246 | 0.14049 | 0.24516 | -120.9778 | -121.231 | 121.5167 | 121.4975 | 121.5253 | 0.40886 | -121.3842 | 0.30882 | 0.45321 | 0.20001 | 0.16972 | -121.5356
1283.5781 | 121.3715 | -0.17853 | 121.1929 | 1.4211e-13 | -0.019372 | 0.0019936 | 0.068409 | -0.011425 | 0.058685 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018677 | 0.030226 | -0.010505 | -0.026423 | 0.20744 | -0.08624 | 121.3199 | 121.2823 | 121.333 | -0.18211 | -0.003531 | -0.040849 | -0.074666 | 0.098244 | 0.25179 | 0.003172 | -0.31067 | -0.003581 | 0.12695 | 0.1521 | 0.092288 | 0.095869 | 0.089401 | 0.14006 | -0.13214 | -121.0947 | 0.175 | 0.10386 | 0.236 | -120.9411 | -121.1898 | 121.4984 | 121.4609 | 121.5115 | 0.38597 | -121.375 | 0.27677 | 0.43032 | 0.1817 | 0.13768 | -121.5036
1285.2656 | 121.3577 | -0.17395 | 121.2158 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068836 | -0.011638 | 0.058471 | 0.00030522 | -0.0023031 | 0.0053414 | 0.018463 | 0.030654 | -0.010719 | -0.017266 | 0.21202 | -0.08624 | 121.329 | 121.2961 | 121.3284 | -0.18211 | -0.00811 | -0.040849 | -0.065509 | 0.10282 | 0.26095 | -0.042614 | -0.30151 | -0.008159 | 0.11322 | 0.15668 | 0.08771 | 0.095869 | 0.08025 | 0.1126 | -0.12756 | -121.113 | 0.16584 | 0.10844 | 0.236 | -120.9549 | -121.2584 | 121.503 | 121.47 | 121.5024 | 0.38597 | -121.3979 | 0.27677 | 0.4349 | 0.13134 | 0.1331 | -121.5173
1287.0156 | 121.3028 | -0.1831 | 121.2341 | 1.4211e-13 | -0.019585 | 0.00178 | 0.068409 | -0.011425 | 0.058471 | 0.015566 | -0.0027303 | 0.005555 | 0.019318 | 0.03044 | -0.010933 | -0.017266 | 0.20286 | -0.081662 | 121.3199 | 121.2961 | 121.333 | -0.17753 | -0.003531 | -0.050007 | -0.070087 | 0.098244 | 0.24721 | -0.005985 | -0.29693 | 0.005575 | 0.085756 | 0.16584 | 0.10144 | 0.095868 | 0.061939 | 0.098865 | -0.11383 | -121.1359 | 0.17957 | 0.11302 | 0.22685 | -120.9869 | -121.2401 | 121.503 | 121.4792 | 121.5161 | 0.38597 | -121.4117 | 0.28135 | 0.43032 | 0.17712 | 0.1331 | -121.5311
1288.75 | 121.2708 | -0.20142 | 121.225 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068409 | -0.011638 | 0.058471 | 0.00030522 | -0.0025167 | 0.0051278 | 0.019318 | 0.030654 | -0.010505 | -0.021844 | 0.21202 | -0.081662 | 121.3245 | 121.3052 | 121.3422 | -0.14548 | -0.003531 | -0.045428 | -0.065509 | 0.1074 | 0.24264 | -0.070086 | -0.30609 | 0.055938 | 0.099489 | 0.17957 | 0.11975 | 0.063816 | 0.080252 | 0.11718 | -0.10468 | -121.1176 | 0.19789 | 0.13591 | 0.24058 | -120.9823 | -121.2951 | 121.5259 | 121.5066 | 121.5436 | 0.41344 | -121.3705 | 0.30882 | 0.44405 | 0.13133 | 0.15599 | -121.5311
1290.5 | 121.312 | -0.20599 | 121.2479 | 1.4211e-13 | -0.019585 | 0.0022072 | 0.068195 | -0.011425 | 0.058471 | 0.00030522 | -0.0025167 | 0.0051278 | 0.019104 | 0.030226 | -0.010719 | -0.021844 | 0.19829 | -0.081662 | 121.329 | 121.3006 | 121.3513 | -0.18211 | -0.003531 | -0.040849 | -0.079245 | 0.093665 | 0.24721 | -0.074664 | -0.30151 | 0.023885 | 0.08118 | 0.18415 | 0.12433 | 0.10045 | 0.052785 | 0.10345 | -0.095519 | -121.1542 | 0.20246 | 0.12675 | 0.22227 | -121.0006 | -121.3225 | 121.535 | 121.5066 | 121.5573 | 0.40428 | -121.43 | 0.29966 | 0.45321 | 0.13133 | 0.16515 | -121.5494
1292.1875 | 121.3623 | -0.18768 | 121.2021 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068622 | -0.011425 | 0.058257 | 0.015566 | -0.0023031 | 0.0053414 | 0.019532 | 0.030654 | -0.010719 | -0.026423 | 0.20286 | -0.08624 | 121.3245 | 121.3052 | 121.3422 | -0.19127 | 0.001048 | -0.040849 | -0.074666 | 0.098244 | 0.24264 | -0.0884 | -0.31067 | -0.003584 | 0.12238 | 0.16126 | 0.10144 | 0.10503 | 0.10314 | 0.14007 | -0.12299 | -121.1038 | 0.18873 | 0.11302 | 0.236 | -120.9595 | -121.2905 | 121.5121 | 121.4929 | 121.5298 | 0.39055 | -121.3934 | 0.28593 | 0.43032 | 0.099283 | 0.14683 | -121.5128
1293.9219 | 121.4264 | -0.16937 | 121.1975 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068836 | -0.011638 | 0.058685 | -0.0073253 | -0.0025167 | 0.005555 | 0.019104 | 0.030654 | -0.010719 | -0.026423 | 0.20286 | -0.095397 | 121.3336 | 121.3052 | 121.3467 | -0.18211 | -0.003531 | -0.045428 | -0.070087 | 0.093665 | 0.23806 | -0.10671 | -0.30151 | -0.012736 | 0.13611 | 0.14295 | 0.073976 | 0.086712 | 0.10772 | 0.14922 | -0.13214 | -121.1038 | 0.16584 | 0.099286 | 0.23143 | -120.9595 | -121.3042 | 121.503 | 121.4746 | 121.5161 | 0.37224 | -121.3796 | 0.26304 | 0.40743 | 0.062659 | 0.12394 | -121.499
1295.6562 | 121.3943 | -0.17853 | 121.2296 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068836 | -0.011425 | 0.058257 | 0.0079357 | -0.0020893 | 0.0051278 | 0.019104 | 0.03044 | -0.010505 | -0.026423 | 0.20744 | -0.090818 | 121.3428 | 121.3144 | 121.3513 | -0.18211 | 0.005626 | -0.050007 | -0.06093 | 0.089087 | 0.24264 | -0.10214 | -0.30609 | -0.003581 | 0.11323 | 0.1521 | 0.08771 | 0.091291 | 0.084833 | 0.12176 | -0.12756 | -121.1405 | 0.18415 | 0.1176 | 0.24516 | -120.9869 | -121.3317 | 121.5213 | 121.4929 | 121.5298 | 0.38597 | -121.4117 | 0.26761 | 0.42117 | 0.076392 | 0.12852 | -121.5356
1297.3438 | 121.3623 | -0.19684 | 121.2296 | 1.4211e-13 | -0.019585 | 0.00178 | 0.068836 | -0.011425 | 0.058257 | 0.00030522 | -0.0027303 | 0.0051278 | 0.019318 | 0.030654 | -0.010719 | -0.026423 | 0.20286 | -0.081662 | 121.3474 | 121.3144 | 121.3513 | -0.17295 | 0.001048 | -0.045428 | -0.056351 | 0.093665 | 0.24264 | -0.10214 | -0.29693 | 0.023887 | 0.1178 | 0.17042 | 0.11518 | 0.091289 | 0.084833 | 0.12176 | -0.1001 | -121.1359 | 0.19789 | 0.14049 | 0.24058 | -120.9869 | -121.3317 | 121.5442 | 121.5112 | 121.5481 | 0.3997 | -121.4025 | 0.2905 | 0.43948 | 0.094702 | 0.15141 | -121.5265
1299.0938 | 121.4081 | -0.16022 | 121.2112 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068622 | -0.011638 | 0.058471 | 0.0079357 | -0.0023031 | 0.0053414 | 0.018891 | 0.030654 | -0.010719 | -0.031001 | 0.20286 | -0.081662 | 121.3474 | 121.3235 | 121.3696 | -0.18669 | -0.003531 | -0.036271 | -0.065509 | 0.084508 | 0.23806 | -0.097557 | -0.30151 | -0.026471 | 0.13611 | 0.12922 | 0.078555 | 0.10503 | 0.1123 | 0.15838 | -0.1413 | -121.1267 | 0.15669 | 0.094708 | 0.236 | -120.9732 | -121.3088 | 121.5076 | 121.4838 | 121.5298 | 0.36308 | -121.3979 | 0.24472 | 0.39827 | 0.06266 | 0.12395 | -121.5128
1300.7812 | 121.4264 | -0.17853 | 121.2204 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068836 | -0.011425 | 0.058257 | -0.0073253 | -0.0025167 | 0.0051278 | 0.018891 | 0.030867 | -0.010292 | -0.026423 | 0.21202 | -0.077084 | 121.3565 | 121.319 | 121.3605 | -0.18211 | 0.001048 | -0.050007 | -0.056351 | 0.089087 | 0.24264 | -0.12961 | -0.31067 | -0.003581 | 0.13612 | 0.1521 | 0.10144 | 0.10502 | 0.098567 | 0.14007 | -0.13214 | -121.1313 | 0.17958 | 0.12218 | 0.25432 | -120.9778 | -121.35 | 121.535 | 121.4975 | 121.539 | 0.39055 | -121.4025 | 0.26761 | 0.42117 | 0.048921 | 0.12852 | -121.5311
1302.5469 | 121.3623 | -0.19226 | 121.2479 | 1.4211e-13 | -0.019585 | 0.0015662 | 0.068622 | -0.011852 | 0.058257 | 0.0079357 | -0.0023031 | 0.0051278 | 0.019318 | 0.030654 | -0.010505 | -0.021844 | 0.20744 | -0.077084 | 121.3474 | 121.3235 | 121.3696 | -0.14548 | -0.003531 | -0.031692 | -0.065509 | 0.089087 | 0.24264 | -0.11587 | -0.29693 | 0.046783 | 0.099493 | 0.17042 | 0.11518 | 0.068394 | 0.07568 | 0.12176 | -0.10467 | -121.1588 | 0.18873 | 0.12675 | 0.23142 | -121.0052 | -121.3637 | 121.5396 | 121.5158 | 121.5619 | 0.3997 | -121.3933 | 0.28135 | 0.4349 | 0.076389 | 0.16057 | -121.5448
1304.2188 | 121.4447 | -0.14191 | 121.2067 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068409 | -0.011425 | 0.058257 | 0.023196 | -0.0027303 | 0.005555 | 0.018891 | 0.030867 | -0.010719 | -0.021844 | 0.20744 | -0.072505 | 121.3657 | 121.3327 | 121.3742 | -0.17753 | 0.001048 | -0.040849 | -0.056351 | 0.084508 | 0.24264 | -0.13419 | -0.30609 | -0.035623 | 0.15901 | 0.12006 | 0.069402 | 0.10502 | 0.12604 | 0.16754 | -0.16418 | -121.1222 | 0.14295 | 0.085556 | 0.24974 | -120.964 | -121.3409 | 121.5076 | 121.4746 | 121.5161 | 0.34935 | -121.3842 | 0.22642 | 0.38454 | 0.007721 | 0.10106 | -121.5128
1305.9531 | 121.4539 | -0.14191 | 121.1975 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068836 | -0.011425 | 0.058257 | -0.0073253 | -0.0023031 | 0.0051278 | 0.019318 | 0.03044 | -0.010719 | -0.017266 | 0.2166 | -0.077084 | 121.3611 | 121.3419 | 121.3879 | -0.17295 | 0.010205 | -0.031692 | -0.06093 | 0.084508 | 0.24264 | -0.12503 | -0.30151 | -0.031044 | 0.16358 | 0.12464 | 0.064823 | 0.095867 | 0.14435 | 0.19043 | -0.15961 | -121.113 | 0.15211 | 0.080977 | 0.24058 | -120.9549 | -121.3225 | 121.503 | 121.4838 | 121.5298 | 0.35851 | -121.3705 | 0.22642 | 0.38454 | 0.016878 | 0.11022 | -121.499
1307.7031 | 121.3257 | -0.20599 | 121.2616 | 1.4211e-13 | -0.019799 | 0.0022072 | 0.068622 | -0.011638 | 0.058471 | 0.00030522 | -0.0027303 | 0.0051278 | 0.019104 | 0.030654 | -0.010505 | -0.017266 | 0.20744 | -0.077084 | 121.3657 | 121.3419 | 121.3788 | -0.17295 | 0.010205 | -0.036271 | -0.056351 | 0.089087 | 0.23806 | -0.13419 | -0.29693 | 0.033043 | 0.10407 | 0.18873 | 0.12891 | 0.095867 | 0.080262 | 0.11719 | -0.09094 | -121.1725 | 0.2162 | 0.14964 | 0.24058 | -121.0235 | -121.3958 | 121.5717 | 121.5479 | 121.5848 | 0.41344 | -121.4345 | 0.29508 | 0.44405 | 0.071808 | 0.16972 | -121.5585
1309.4531 | 121.4081 | -0.14648 | 121.2479 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068622 | -0.011638 | 0.058471 | 0.00030522 | -0.0027303 | 0.0053414 | 0.019104 | 0.030867 | -0.010292 | -0.012688 | 0.20744 | -0.072505 | 121.3657 | 121.3464 | 121.3925 | -0.17753 | 0.005626 | -0.031692 | -0.051772 | 0.089087 | 0.2289 | -0.12503 | -0.29693 | -0.031046 | 0.11781 | 0.1338 | 0.073979 | 0.10502 | 0.098574 | 0.14465 | -0.15045 | -121.1588 | 0.15211 | 0.094712 | 0.24516 | -121.019 | -121.3729 | 121.5122 | 121.4929 | 121.539 | 0.35393 | -121.4254 | 0.23557 | 0.37538 | 0.021455 | 0.11479 | -121.5448
1311.2031 | 121.3989 | -0.17853 | 121.2479 | 1.4211e-13 | -0.019799 | 0.00178 | 0.068409 | -0.011638 | 0.058471 | 0.0079357 | -0.0027303 | 0.0049142 | 0.019318 | 0.030654 | -0.010933 | -0.017266 | 0.20744 | -0.077084 | 121.3748 | 121.351 | 121.3834 | -0.17295 | 0.023941 | -0.031692 | -0.06093 | 0.07993 | 0.24721 | -0.083821 | -0.29693 | 0.005577 | 0.12696 | 0.16126 | 0.10144 | 0.095867 | 0.10315 | 0.1355 | -0.11841 | -121.1679 | 0.20247 | 0.1176 | 0.236 | -121.0006 | -121.3317 | 121.5534 | 121.5295 | 121.5619 | 0.38597 | -121.4208 | 0.25846 | 0.42574 | 0.094707 | 0.14684 | -121.5448
1312.8906 | 121.4081 | -0.16937 | 121.2524 | 1.4211e-13 | -0.019372 | 0.0019936 | 0.068622 | -0.011425 | 0.058471 | 0.0079357 | -0.0023031 | 0.0053414 | 0.018891 | 0.030654 | -0.010505 | -0.017266 | 0.20286 | -0.072505 | 121.3702 | 121.351 | 121.3925 | -0.16837 | 0.005626 | -0.036271 | -0.06093 | 0.075351 | 0.23348 | -0.12045 | -0.30151 | 0.001 | 0.11781 | 0.15211 | 0.096868 | 0.095868 | 0.098576 | 0.14008 | -0.13214 | -121.1771 | 0.175 | 0.10844 | 0.24058 | -121.019 | -121.3729 | 121.5396 | 121.5204 | 121.5619 | 0.37224 | -121.4208 | 0.24472 | 0.40285 | 0.048923 | 0.1331 | -121.554
1314.625 | 121.4081 | -0.17853 | 121.2662 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068836 | -0.011425 | 0.058471 | 0.00030522 | -0.0023031 | 0.0049142 | 0.019104 | 0.030654 | -0.010505 | -0.017266 | 0.21202 | -0.067927 | 121.3748 | 121.3556 | 121.4017 | -0.15006 | 0.010205 | -0.027113 | -0.056351 | 0.093665 | 0.23348 | -0.13419 | -0.29693 | 0.028471 | 0.10865 | 0.16126 | 0.1106 | 0.08213 | 0.089422 | 0.1355 | -0.11841 | -121.1725 | 0.18873 | 0.12218 | 0.24058 | -121.0327 | -121.4004 | 121.5534 | 121.5341 | 121.5802 | 0.39055 | -121.4162 | 0.27219 | 0.41201 | 0.044342 | 0.15141 | -121.5631
1316.3594 | 121.344 | -0.19684 | 121.2799 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.068836 | -0.011852 | 0.058471 | 0.015566 | -0.0025167 | 0.0053414 | 0.019104 | 0.030654 | -0.010505 | -0.017266 | 0.21202 | -0.072505 | 121.384 | 121.3556 | 121.4017 | -0.16837 | 0.014784 | -0.027113 | -0.051772 | 0.084508 | 0.2289 | -0.10214 | -0.29236 | 0.028465 | 0.10408 | 0.17957 | 0.12433 | 0.095868 | 0.075689 | 0.12177 | -0.095518 | -121.1954 | 0.21162 | 0.14507 | 0.24058 | -121.051 | -121.382 | 121.5808 | 121.5524 | 121.5985 | 0.40886 | -121.4483 | 0.28135 | 0.42574 | 0.094702 | 0.16973 | -121.5723
1318.0469 | 121.4035 | -0.16937 | 121.2524 | 1.4211e-13 | -0.019585 | 0.0015662 | 0.068622 | -0.011852 | 0.058471 | 0.00030522 | -0.0023031 | 0.0051278 | 0.019104 | 0.030654 | -0.010719 | -0.021844 | 0.20744 | -0.072505 | 121.384 | 121.3602 | 121.4063 | -0.17295 | 0.010205 | -0.036271 | -0.06093 | 0.084508 | 0.2289 | -0.083821 | -0.29236 | -0.003578 | 0.13154 | 0.14753 | 0.096868 | 0.10045 | 0.10773 | 0.15381 | -0.12298 | -121.1679 | 0.17958 | 0.10844 | 0.23143 | -121.0235 | -121.3363 | 121.5534 | 121.5295 | 121.5756 | 0.37682 | -121.4254 | 0.25388 | 0.39827 | 0.085552 | 0.1331 | -121.5448
1319.7969 | 121.4401 | -0.16022 | 121.2524 | 1.4211e-13 | -0.020013 | 0.00178 | 0.068836 | -0.011852 | 0.058257 | 0.00030522 | -0.0023031 | 0.0051278 | 0.019318 | 0.030654 | -0.010719 | -0.017266 | 0.20744 | -0.081662 | 121.3886 | 121.3602 | 121.4017 | -0.16379 | 0.010205 | -0.031692 | -0.06093 | 0.089087 | 0.23348 | -0.12503 | -0.29693 | -0.003577 | 0.13612 | 0.14295 | 0.078555 | 0.082132 | 0.10773 | 0.14923 | -0.13672 | -121.1634 | 0.17042 | 0.099287 | 0.236 | -121.019 | -121.3775 | 121.5488 | 121.5204 | 121.5619 | 0.36766 | -121.4162 | 0.2493 | 0.3937 | 0.035188 | 0.12853 | -121.5494
1321.5469 | 121.3898 | -0.19684 | 121.2936 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.068836 | -0.011852 | 0.058471 | -0.0073253 | -0.0025167 | 0.0051278 | 0.019104 | 0.03044 | -0.010292 | -0.012688 | 0.20744 | -0.077084 | 121.3931 | 121.3693 | 121.4063 | -0.17295 | 0.010205 | -0.031692 | -0.051772 | 0.07993 | 0.23348 | -0.12503 | -0.29693 | 0.023887 | 0.099501 | 0.18415 | 0.11975 | 0.095867 | 0.075693 | 0.11261 | -0.1001 | -121.2137 | 0.20704 | 0.14507 | 0.24516 | -121.0602 | -121.4187 | 121.59 | 121.5662 | 121.6031 | 0.40428 | -121.4666 | 0.27677 | 0.43032 | 0.071809 | 0.16515 | -121.5906
1323.2344 | 121.4218 | -0.14648 | 121.2662 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.068622 | -0.011638 | 0.05783 | 0.015566 | -0.0023031 | 0.0049142 | 0.019318 | 0.030654 | -0.010719 | -0.012688 | 0.20744 | -0.072505 | 121.3931 | 121.3739 | 121.4063 | -0.15464 | 0.010205 | -0.040849 | -0.056351 | 0.07993 | 0.2289 | -0.092979 | -0.28778 | -0.008152 | 0.12697 | 0.1338 | 0.073979 | 0.082131 | 0.10774 | 0.14008 | -0.14129 | -121.1862 | 0.15669 | 0.090133 | 0.23143 | -121.0373 | -121.3592 | 121.5396 | 121.5204 | 121.5527 | 0.35393 | -121.4208 | 0.22641 | 0.37538 | 0.053505 | 0.10564 | -121.554
1324.9688 | 121.3257 | -0.19226 | 121.3028 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068622 | -0.011425 | 0.058257 | 0.0079357 | -0.0025167 | 0.0053414 | 0.019104 | 0.031081 | -0.010505 | -0.012688 | 0.22118 | -0.067927 | 121.3977 | 121.3693 | 121.4108 | -0.12716 | 0.014784 | -0.040849 | -0.051772 | 0.084508 | 0.2289 | -0.12961 | -0.30151 | 0.065099 | 0.094925 | 0.17957 | 0.12433 | 0.059235 | 0.066538 | 0.10804 | -0.10925 | -121.2183 | 0.20704 | 0.14049 | 0.24974 | -121.0739 | -121.4324 | 121.59 | 121.5616 | 121.6031 | 0.41344 | -121.43 | 0.27677 | 0.42116 | 0.062654 | 0.15141 | -121.6043
1326.7031 | 121.3531 | -0.17853 | 121.2936 | 1.4211e-13 | -0.019585 | 0.0022072 | 0.068622 | -0.011211 | 0.058257 | 0.0079357 | -0.0023031 | 0.0051278 | 0.019318 | 0.030654 | -0.010505 | -0.008109 | 0.20744 | -0.067927 | 121.3977 | 121.3785 | 121.4154 | -0.15921 | 0.014784 | -0.040849 | -0.056351 | 0.084508 | 0.2289 | -0.12503 | -0.28778 | 0.019313 | 0.10408 | 0.17042 | 0.1106 | 0.091288 | 0.084851 | 0.12177 | -0.10925 | -121.2091 | 0.19331 | 0.12218 | 0.23143 | -121.0647 | -121.4187 | 121.5762 | 121.557 | 121.5939 | 0.38597 | -121.4529 | 0.26304 | 0.40743 | 0.053499 | 0.13768 | -121.5814
1328.4531 | 121.3806 | -0.1831 | 121.2936 | 1.4211e-13 | -0.019799 | 0.0022072 | 0.068836 | -0.011425 | 0.058257 | 0.00030522 | -0.0023031 | 0.0051278 | 0.019318 | 0.031081 | -0.010505 | -0.008109 | 0.21202 | -0.067927 | 121.4115 | 121.3876 | 121.4337 | -0.15006 | 0.014784 | -0.036271 | -0.051772 | 0.084508 | 0.2289 | -0.079243 | -0.29236 | 0.033048 | 0.11782 | 0.175 | 0.11518 | 0.08213 | 0.094009 | 0.14008 | -0.10925 | -121.2091 | 0.19789 | 0.13133 | 0.24058 | -121.0647 | -121.3729 | 121.5946 | 121.5708 | 121.6168 | 0.39513 | -121.4437 | 0.26761 | 0.41201 | 0.10386 | 0.14683 | -121.586
1330.1406 | 121.3989 | -0.16479 | 121.3028 | 1.4211e-13 | -0.019585 | 0.00178 | 0.06905 | -0.011425 | 0.058257 | 0.00030522 | -0.0023031 | 0.0051278 | 0.019104 | 0.030654 | -0.010719 | -0.017266 | 0.21202 | -0.063349 | 121.4069 | 121.3968 | 121.4291 | -0.099689 | 0.019362 | -0.031692 | -0.047194 | 0.084508 | 0.22432 | -0.12961 | -0.28778 | 0.065106 | 0.10408 | 0.14753 | 0.10145 | 0.03634 | 0.094011 | 0.12635 | -0.12298 | -121.2183 | 0.18416 | 0.1176 | 0.24058 | -121.0785 | -121.4324 | 121.5717 | 121.5616 | 121.5939 | 0.37682 | -121.4025 | 0.2493 | 0.38912 | 0.035188 | 0.1331 | -121.5906
1331.8906 | 121.4493 | -0.14191 | 121.2845 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068622 | -0.011638 | 0.058257 | 0.00030522 | -0.0025167 | 0.0051278 | 0.019318 | 0.031081 | -0.010719 | -0.008109 | 0.21202 | -0.063349 | 121.4115 | 121.3968 | 121.4291 | -0.12716 | 0.019362 | -0.022535 | -0.051772 | 0.089087 | 0.23806 | -0.13419 | -0.2832 | 0.014745 | 0.12697 | 0.1338 | 0.078558 | 0.063813 | 0.11232 | 0.14466 | -0.14129 | -121.1954 | 0.16127 | 0.090135 | 0.23143 | -121.0464 | -121.4187 | 121.5534 | 121.5387 | 121.5711 | 0.35393 | -121.4116 | 0.23099 | 0.37996 | 0.007721 | 0.11937 | -121.5677
1333.625 | 121.3669 | -0.19684 | 121.3257 | 1.4211e-13 | -0.019799 | 0.00178 | 0.068622 | -0.011638 | 0.058685 | 0.015566 | -0.0020893 | 0.0053414 | 0.019318 | 0.030867 | -0.010719 | -0.012688 | 0.2166 | -0.054192 | 121.4206 | 121.3922 | 121.4337 | -0.16837 | 0.010205 | -0.022535 | -0.042615 | 0.089087 | 0.23348 | -0.10214 | -0.28778 | 0.028465 | 0.094927 | 0.18415 | 0.14265 | 0.11418 | 0.066544 | 0.10804 | -0.090939 | -121.2366 | 0.20704 | 0.15422 | 0.24516 | -121.0922 | -121.4278 | 121.6174 | 121.5891 | 121.6306 | 0.41344 | -121.4941 | 0.28592 | 0.43032 | 0.094702 | 0.1743 | -121.6135
1335.3594 | 121.4859 | -0.14191 | 121.2616 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068836 | -0.011852 | 0.058257 | 0.0079357 | -0.0025167 | 0.0053414 | 0.019104 | 0.030867 | -0.010719 | -0.008109 | 0.20744 | -0.067927 | 121.4115 | 121.4014 | 121.4337 | -0.16837 | 0.019362 | -0.027113 | -0.056351 | 0.07993 | 0.23348 | -0.14334 | -0.28778 | -0.026466 | 0.14986 | 0.1338 | 0.07398 | 0.10045 | 0.13979 | 0.17213 | -0.14587 | -121.1817 | 0.16127 | 0.085556 | 0.23143 | -121.0281 | -121.4049 | 121.5534 | 121.5433 | 121.5756 | 0.34935 | -121.43 | 0.22184 | 0.37539 | -0.001436 | 0.11479 | -121.5494
1337.0469 | 121.3806 | -0.19684 | 121.3211 | 1.4211e-13 | -0.019799 | 0.00178 | 0.06905 | -0.011638 | 0.058044 | 0.0079357 | -0.0025167 | 0.005555 | 0.019318 | 0.030867 | -0.010719 | -0.017266 | 0.21202 | -0.077084 | 121.4115 | 121.3876 | 121.4337 | -0.15921 | 0.014784 | -0.031692 | -0.056351 | 0.07993 | 0.2289 | -0.12503 | -0.29693 | 0.037623 | 0.090349 | 0.17957 | 0.11975 | 0.082131 | 0.066543 | 0.11262 | -0.1001 | -121.2412 | 0.21162 | 0.14049 | 0.24058 | -121.0922 | -121.4461 | 121.6083 | 121.5845 | 121.6306 | 0.40886 | -121.4803 | 0.27677 | 0.42574 | 0.071809 | 0.16515 | -121.618
1338.7969 | 121.4539 | -0.16479 | 121.2662 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.06905 | -0.011638 | 0.058471 | 0.0079357 | -0.0029439 | 0.005555 | 0.019532 | 0.030654 | -0.010505 | -0.021844 | 0.2166 | -0.072505 | 121.4023 | 121.3831 | 121.4291 | -0.17295 | 0.010205 | -0.027113 | -0.06093 | 0.07993 | 0.2289 | -0.11129 | -0.29693 | -0.008156 | 0.13612 | 0.14295 | 0.09229 | 0.10045 | 0.1169 | 0.16297 | -0.13214 | -121.1862 | 0.175 | 0.10386 | 0.236 | -121.0373 | -121.3775 | 121.5671 | 121.5479 | 121.5939 | 0.3814 | -121.4391 | 0.24472 | 0.3937 | 0.053502 | 0.13768 | -121.5631
1340.5469 | 121.4035 | -0.18768 | 121.2936 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.068836 | -0.011638 | 0.058257 | 0.015566 | -0.0018757 | 0.0053414 | 0.019104 | 0.031081 | -0.010505 | -0.012688 | 0.21202 | -0.067927 | 121.4115 | 121.3876 | 121.4291 | -0.17295 | 0.014784 | -0.027113 | -0.056351 | 0.075351 | 0.23348 | -0.12961 | -0.30609 | 0.014732 | 0.11782 | 0.17499 | 0.11976 | 0.10502 | 0.094009 | 0.13551 | -0.11841 | -121.2183 | 0.20247 | 0.13133 | 0.24974 | -121.0602 | -121.4232 | 121.5991 | 121.5753 | 121.6168 | 0.3997 | -121.4666 | 0.26303 | 0.42116 | 0.058076 | 0.16057 | -121.5997
1342.2188 | 121.4905 | -0.16022 | 121.3074 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.068836 | -0.011425 | 0.058257 | 0.0079357 | -0.0023031 | 0.0053414 | 0.018891 | 0.031081 | -0.010719 | -0.021844 | 0.2166 | -0.072505 | 121.416 | 121.3876 | 121.4383 | -0.17753 | 0.019362 | -0.031692 | -0.056351 | 0.075351 | 0.2289 | -0.13876 | -0.29693 | -0.017313 | 0.10866 | 0.13837 | 0.087712 | 0.10502 | 0.080276 | 0.13093 | -0.13672 | -121.232 | 0.17958 | 0.10387 | 0.24058 | -121.0785 | -121.4461 | 121.5763 | 121.5479 | 121.5985 | 0.37682 | -121.4849 | 0.23557 | 0.38912 | 0.021452 | 0.12853 | -121.6043
1343.9688 | 121.4127 | -0.20599 | 121.312 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.068622 | -0.011638 | 0.058685 | -0.0073253 | -0.0025167 | 0.0053414 | 0.019104 | 0.030867 | -0.010505 | -0.021844 | 0.21202 | -0.077084 | 121.4206 | 121.3968 | 121.4475 | -0.17295 | 0.014784 | -0.017956 | -0.056351 | 0.089087 | 0.2289 | -0.13876 | -0.30151 | 0.033043 | 0.10866 | 0.18415 | 0.12891 | 0.095867 | 0.084855 | 0.13551 | -0.095519 | -121.2229 | 0.22078 | 0.14964 | 0.24516 | -121.0831 | -121.4507 | 121.6266 | 121.6028 | 121.6535 | 0.41802 | -121.4849 | 0.29508 | 0.4349 | 0.067229 | 0.18804 | -121.6135
1345.6562 | 121.3669 | -0.20599 | 121.2982 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.06905 | -0.011425 | 0.058685 | 0.0079357 | -0.0023031 | 0.005555 | 0.018891 | 0.030867 | -0.010719 | -0.017266 | 0.21202 | -0.072505 | 121.4206 | 121.3922 | 121.4475 | -0.17295 | 0.014784 | -0.031692 | -0.056351 | 0.084508 | 0.23348 | -0.12503 | -0.29693 | 0.033043 | 0.12239 | 0.18873 | 0.13349 | 0.10045 | 0.09401 | 0.14924 | -0.09094 | -121.2137 | 0.22078 | 0.14964 | 0.24058 | -121.0647 | -121.4232 | 121.6266 | 121.5982 | 121.6535 | 0.41802 | -121.4712 | 0.2905 | 0.43947 | 0.080965 | 0.1743 | -121.5952
1347.3906 | 121.431 | -0.19684 | 121.3211 | 1.4211e-13 | -0.019799 | 0.0019936 | 0.06905 | -0.011638 | 0.058685 | 0.00030522 | -0.0025167 | 0.005555 | 0.018891 | 0.030654 | -0.010933 | -0.017266 | 0.2166 | -0.067927 | 121.4252 | 121.406 | 121.4475 | -0.16837 | 0.014784 | -0.031692 | -0.06093 | 0.07993 | 0.22432 | -0.13419 | -0.30151 | 0.028465 | 0.10408 | 0.17957 | 0.12891 | 0.10045 | 0.084858 | 0.12636 | -0.10467 | -121.2412 | 0.21162 | 0.13591 | 0.24058 | -121.0968 | -121.4553 | 121.622 | 121.6028 | 121.6443 | 0.41344 | -121.4895 | 0.27677 | 0.42116 | 0.062652 | 0.16515 | -121.6226
1349.1406 | 121.4401 | -0.17853 | 121.2936 | 1.4211e-13 | -0.020013 | 0.00178 | 0.06905 | -0.011852 | 0.058257 | 0.0079357 | -0.0023031 | 0.005555 | 0.019104 | 0.031081 | -0.010505 | -0.008109 | 0.22118 | -0.067927 | 121.4298 | 121.4105 | 121.4566 | -0.11342 | 0.02852 | -0.031692 | -0.051772 | 0.089087 | 0.23348 | -0.13419 | -0.29236 | 0.065103 | 0.13613 | 0.17042 | 0.1106 | 0.045498 | 0.1169 | 0.16298 | -0.11383 | -121.2046 | 0.20705 | 0.12676 | 0.24058 | -121.0602 | -121.4278 | 121.6083 | 121.5891 | 121.6351 | 0.39971 | -121.4071 | 0.26761 | 0.41201 | 0.044342 | 0.14684 | -121.586
1350.8906 | 121.4859 | -0.15564 | 121.3165 | 1.4211e-13 | -0.019585 | 0.0019936 | 0.06905 | -0.011638 | 0.058471 | 0.00030522 | -0.0023031 | 0.0053414 | 0.018677 | 0.030867 | -0.010719 | -0.012688 | 0.22118 | -0.067927 | 121.4298 | 121.4151 | 121.4658 | -0.1409 | 0.014784 | -0.027113 | -0.056351 | 0.084508 | 0.2289 | -0.13419 | -0.29236 | 0.014741 | 0.11324 | 0.14295 | 0.087713 | 0.072972 | 0.098594 | 0.14925 | -0.13672 | -121.232 | 0.17042 | 0.099289 | 0.23601 | -121.0876 | -121.4507 | 121.5854 | 121.5708 | 121.6214 | 0.37682 | -121.4574 | 0.24015 | 0.38454 | 0.021454 | 0.12853 | -121.6089
1352.6406 | 121.4401 | -0.16937 | 121.3211 | 1.4211e-13 | -0.020013 | 0.00178 | 0.068836 | -0.011852 | 0.058257 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018891 | 0.031081 | -0.010505 | -0.012688 | 0.2166 | -0.063349 | 121.4435 | 121.4151 | 121.4566 | -0.17295 | 0.023941 | -0.027113 | -0.065509 | 0.07993 | 0.21516 | -0.12961 | -0.28778 | -0.003578 | 0.1224 | 0.15668 | 0.10602 | 0.1096 | 0.094016 | 0.13551 | -0.1184 | -121.2412 | 0.19331 | 0.10386 | 0.22227 | -121.1059 | -121.4507 | 121.6129 | 121.5845 | 121.626 | 0.38597 | -121.4941 | 0.2493 | 0.38454 | 0.039766 | 0.14226 | -121.6089
1354.3125 | 121.3943 | -0.17853 | 121.3211 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.068622 | -0.011425 | 0.058257 | 0.0079357 | -0.0025167 | 0.005555 | 0.019104 | 0.031081 | -0.010719 | -0.012688 | 0.2166 | -0.072505 | 121.4343 | 121.4151 | 121.4612 | -0.16379 | 0.014784 | -0.031692 | -0.06093 | 0.07993 | 0.2289 | -0.13419 | -0.29236 | 0.014734 | 0.11324 | 0.16584 | 0.10602 | 0.091289 | 0.094016 | 0.14009 | -0.11383 | -121.2412 | 0.19331 | 0.1176 | 0.23143 | -121.0922 | -121.4553 | 121.6129 | 121.5936 | 121.6397 | 0.39513 | -121.4849 | 0.25846 | 0.40743 | 0.044342 | 0.14684 | -121.6135
1356.0469 | 121.4355 | -0.25177 | 121.2296 | 1.4211e-13 | -0.019799 | 0.00178 | 0.06905 | -0.011852 | 0.058471 | 0.00030522 | -0.0023031 | 0.0053414 | 0.019104 | 0.030867 | -0.010505 | -0.081363 | 0.22118 | -0.14118 | 121.3428 | 121.3373 | 121.3834 | -0.23706 | -0.00811 | -0.0729 | -0.088402 | 0.043302 | 0.19227 | -0.14792 | -0.36562 | 0.014714 | 0.11323 | 0.17041 | 0.11059 | 0.095876 | 0.10773 | 0.15381 | -0.11385 | -121.1863 | 0.24366 | 0.16337 | 0.27722 | -121.0373 | -121.3775 | 121.5945 | 121.5891 | 121.6351 | 0.47295 | -121.4666 | 0.29507 | 0.44404 | 0.10385 | 0.17887 | -121.5952
1357.7969 | 121.5271 | -0.16479 | 121.2753 | 1.4211e-13 | -0.020226 | 0.00178 | 0.068622 | -0.011425 | 0.058471 | -0.0073253 | -0.0025167 | 0.0051278 | 0.019318 | 0.031081 | -0.010719 | -0.021844 | 0.22118 | -0.077084 | 121.4206 | 121.4014 | 121.4475 | -0.18211 | 0.010205 | -0.027113 | -0.065509 | 0.070773 | 0.21974 | -0.10671 | -0.30609 | -0.017314 | 0.14528 | 0.14295 | 0.087711 | 0.10502 | 0.12606 | 0.17213 | -0.1413 | -121.2046 | 0.175 | 0.099286 | 0.24058 | -121.0556 | -121.382 | 121.5854 | 121.5662 | 121.6123 | 0.38597 | -121.4574 | 0.23557 | 0.38454 | 0.058081 | 0.13768 | -121.5814
1359.4844 | 121.3623 | -0.37079 | 121.1014 | 1.4211e-13 | -0.020013 | 0.0019936 | 0.068836 | -0.011638 | 0.058471 | 0.0079357 | -0.0027303 | 0.0051278 | 0.019104 | 0.030867 | -0.010292 | -0.45679 | 0.2166 | -0.5166 | 120.9078 | 120.884 | 120.9347 | -0.64458 | -0.15005 | -0.24689 | -0.28986 | -0.12152 | 0.018285 | -0.097557 | -0.76397 | -0.27379 | -0.19355 | -0.086002 | -0.14581 | 0.12798 | -0.21741 | -0.16672 | -0.39319 | -121.2229 | 0.22074 | 0.080924 | 0.47411 | -121.0831 | -121.1989 | 121.2786 | 121.2548 | 121.3054 | 0.58739 | -121.746 | 0.24926 | 0.38907 | 0.27323 | 0.1239 | -121.8654
1361.2188 | 118.2678 | -92.2668 | 25.8408 | 1.4211e-13 | -0.021081 | 0.0011388 | 0.066272 | -0.011211 | 0.057403 | 0.0079357 | 0.0011151 | 0.0072644 | 0.013763 | 0.080439 | 0.10444 | -91.3927 | -0.31452 | -91.6427 | 26.5152 | 26.5215 | 26.7528 | -91.8613 | -34.3439 | -27.7924 | -27.5561 | -8.0789 | -8.0629 | -7.84 | -92.0564 | 0.40551 | 0.67445 | 0.87412 | 0.62415 | 0.21864 | 0.68073 | 0.91205 | 0.21041 | -33.9197 | 57.923 | 64.7108 | 64.5003 | -33.9037 | -33.6807 | 118.7821 | 118.7883 | 119.0196 | 91.9523 | -117.7021 | 84.1879 | 84.2039 | 84.4269 | 64.4744 | -117.8972
1362.9375 | 119.751 | -118.9819 | 0.81482 | 1.4211e-13 | -0.020654 | 0.00049784 | 0.066272 | -0.011211 | 0.057403 | 0.0079357 | 0.0019697 | 0.00876 | 0.011413 | 0.083431 | 0.12581 | -103.2004 | -1.0929 | -103.2257 | 14.8174 | 14.5201 | 15.1781 | -103.6429 | -37.5993 | -32.8153 | -32.4416 | -7.6257 | -7.5868 | -7.4325 | -103.9843 | 15.339 | 14.0026 | 15.7815 | 15.7562 | 0.41716 | 13.7053 | 14.3633 | 14.9977 | -8.4405 | 81.3826 | 86.5404 | 71.5427 | -8.4016 | -8.2473 | 133.7994 | 133.5021 | 134.16 | 117.8891 | -104.4577 | 111.3563 | 111.3952 | 111.5495 | 86.1667 | -104.7991
1364.7031 | 120.1859 | -33.4808 | 86.7142 | 1.4211e-13 | -0.020654 | 0.0015662 | 0.068195 | -0.011638 | 0.058471 | -0.0073253 | -0.00080746 | 0.0070506 | 0.015686 | 0.050098 | 0.03308 | -38.4666 | 0.41348 | -38.6125 | 81.6482 | 81.7571 | 81.696 | -38.4986 | -15.942 | -13.1726 | -13.3529 | -2.8411 | -2.6877 | -2.6616 | -38.6079 | -5.0177 | -5.066 | -4.9857 | -5.1316 | -0.11392 | -4.9571 | -5.0181 | -5.1271 | -89.5553 | 17.5388 | 20.1279 | 25.255 | -89.4018 | -89.3757 | 115.129 | 115.2379 | 115.1769 | 33.8943 | -125.2127 | 30.6397 | 30.7932 | 30.8193 | 20.3082 | -125.3221
1366.3906 | 120.4788 | -20.7047 | 99.765 | 1.4211e-13 | -0.02044 | 0.0013526 | 0.068195 | -0.011852 | 0.058257 | 0.0079357 | -0.0014485 | 0.0059824 | 0.016968 | 0.044115 | 0.019406 | -26.0454 | 0.31275 | -26.1092 | 94.5226 | 94.5139 | 94.6306 | -26.0576 | -10.269 | -8.2963 | -8.4033 | -2.1681 | -2.0192 | -1.9794 | -26.1581 | -5.353 | -5.2424 | -5.3407 | -5.4045 | -0.051575 | -5.2511 | -5.1344 | -5.4534 | -101.9331 | 10.4357 | 12.3013 | 17.7548 | -101.7842 | -101.7444 | 115.2272 | 115.2186 | 115.3352 | 21.0174 | -125.8226 | 18.5365 | 18.6855 | 18.7253 | 12.4084 | -125.9231
1368.1406 | 120.4559 | -24.6002 | 95.8237 | 1.4211e-13 | -0.02044 | 0.00178 | 0.068409 | -0.011638 | 0.058257 | 0.00030522 | -0.0010211 | 0.006196 | 0.017182 | 0.043688 | 0.017911 | -24.8871 | 0.16624 | -24.9784 | 95.7496 | 95.7365 | 95.821 | -24.89 | -10.008 | -7.4996 | -7.5792 | -2.1269 | -1.978 | -1.9519 | -25.0042 | -0.28977 | -0.074078 | -0.28685 | -0.37813 | -0.088365 | -0.087156 | -0.002646 | -0.40401 | -97.9506 | 14.5922 | 17.021 | 17.4251 | -97.8017 | -97.7756 | 120.3498 | 120.3367 | 120.4212 | 24.7665 | -120.7137 | 22.4733 | 22.6222 | 22.6483 | 17.1007 | -120.8279
1369.875 | 120.6207 | -8.0429 | 112.3581 | 1.4211e-13 | -0.02044 | 0.00178 | 0.068195 | -0.011425 | 0.058044 | -0.0073253 | -0.0025167 | 0.005555 | 0.018463 | 0.034927 | -0.0019593 | -7.8829 | 0.29902 | -8.0112 | 112.6805 | 112.674 | 112.7161 | -8.0304 | -3.1491 | -2.2753 | -2.3686 | -0.62974 | -0.48536 | -0.45927 | -8.1267 | 0.012522 | 0.32238 | 0.15997 | 0.031664 | 0.019142 | 0.31586 | 0.35797 | -0.083804 | -112.9878 | 4.8938 | 5.6743 | 5.7581 | -112.8435 | -112.8174 | 120.7234 | 120.7169 | 120.759 | 8.3419 | -120.3885 | 7.4132 | 7.5575 | 7.5836 | 5.7676 | -120.4848
1371.5625 | 120.6162 | -11.8195 | 108.7326 | 1.4211e-13 | -0.02044 | 0.0013526 | 0.067981 | -0.011852 | 0.058471 | 0.0079357 | -0.0014485 | 0.006837 | 0.016327 | 0.045824 | 0.014919 | -26.343 | 0.88965 | -26.4663 | 94.2525 | 94.3308 | 94.3192 | -26.3781 | -13.584 | -8.2596 | -8.4125 | -2.3925 | -2.2619 | -2.1946 | -26.4145 | -14.5587 | -14.4801 | -14.5235 | -14.6468 | -0.088156 | -14.4018 | -14.4134 | -14.5951 | -111.1251 | -1.7645 | 3.407 | 18.002 | -110.9945 | -110.9272 | 106.0719 | 106.1502 | 106.1387 | 12.7091 | -135.1107 | 9.427 | 9.5576 | 9.6249 | 3.5598 | -135.1471
1373.3125 | 119.7327 | -40.5579 | 79.2984 | 1.4211e-13 | -0.02044 | 0.0013526 | 0.067981 | -0.012066 | 0.058471 | 0.0079357 | -0.00059386 | 0.007478 | 0.015472 | 0.04326 | 0.014065 | -26.691 | -1.6148 | -26.6769 | 94.2525 | 93.9874 | 94.4841 | -26.9917 | -17.5263 | -7.4034 | -7.4555 | -2.2826 | -2.1291 | -2.1259 | -27.2799 | 13.5661 | 14.9541 | 13.8669 | 13.881 | 0.31482 | 14.689 | 15.1857 | 13.278 | -81.581 | 23.0316 | 33.1023 | 19.8244 | -81.4275 | -81.4243 | 134.8103 | 134.5452 | 135.0419 | 38.943 | -106.2901 | 38.2753 | 38.4288 | 38.432 | 33.1544 | -106.5783
1375.0625 | 120.4376 | -117.5903 | 2.5269 | 1.4211e-13 | -0.020867 | 0.00092524 | 0.067126 | -0.011425 | 0.059326 | 0.015566 | 0.0045333 | 0.014956 | 0.0028672 | 0.09155 | 0.11662 | -117.0729 | -0.34199 | -117.4367 | 2.7534 | 2.7706 | 3.0082 | -117.7002 | -68.2355 | -38.4379 | -38.6961 | -7.3464 | -7.2251 | -7.1486 | -117.9359 | -0.10988 | 0.22652 | 0.51742 | 0.1536 | 0.26348 | 0.24375 | 0.48132 | -0.34557 | -9.8732 | 49.3549 | 78.8942 | 79.2398 | -9.7519 | -9.6755 | 120.3437 | 120.3609 | 120.5985 | 117.2483 | -120.2271 | 110.2439 | 110.3653 | 110.4417 | 79.1524 | -120.4628
1376.75 | 120.607 | -117.7231 | 2.4994 | 1.4211e-13 | -0.020867 | 0.0011388 | 0.06734 | -0.011211 | 0.059112 | -0.0073253 | 0.0045333 | 0.014529 | 0.0032944 | 0.090482 | 0.12046 | -117.2515 | -0.27331 | -117.6153 | 2.7122 | 2.734 | 2.9715 | -117.865 | -65.7584 | -39.8298 | -40.0972 | -6.8428 | -6.7123 | -6.6633 | -118.1236 | -0.14197 | 0.21278 | 0.47162 | 0.1078 | 0.24977 | 0.23459 | 0.47215 | -0.40055 | -9.3421 | 51.9647 | 77.6259 | 78.0265 | -9.2117 | -9.1627 | 120.4353 | 120.4571 | 120.6946 | 117.4498 | -120.3644 | 110.8803 | 111.0108 | 111.0598 | 77.8932 | -120.623
1378.5 | 120.607 | -118.959 | 1.4923 | 1.4211e-13 | -0.021081 | 0.00092524 | 0.06734 | -0.011852 | 0.059112 | 0.00030522 | 0.0049607 | 0.014529 | 0.0032944 | 0.091337 | 0.12196 | -118.0389 | -0.24584 | -118.4439 | 1.9155 | 1.9647 | 2.2023 | -118.6938 | -70.0715 | -39.0377 | -39.3417 | -6.6642 | -6.5154 | -6.4801 | -118.957 | 0.26521 | 0.42322 | 0.9201 | 0.5151 | 0.24988 | 0.47241 | 0.71003 | 0.002063 | -8.1565 | 48.8875 | 79.6174 | 79.6153 | -8.0077 | -7.9724 | 120.8746 | 120.9238 | 121.1614 | 118.7132 | -120.1861 | 112.2949 | 112.4437 | 112.4789 | 79.9213 | -120.4493
1380.1875 | 120.575 | -118.9636 | 1.506 | 1.4211e-13 | -0.021081 | 0.00071164 | 0.067767 | -0.011638 | 0.059112 | 0.0079357 | 0.0051743 | 0.01517 | 0.0026534 | 0.09326 | 0.12645 | -118.4418 | -0.21379 | -118.8697 | 1.5081 | 1.5892 | 1.8177 | -119.1334 | -69.4855 | -37.6275 | -37.9085 | -6.5039 | -6.3597 | -6.3199 | -119.3737 | -0.16979 | 0.002013 | 0.52178 | 0.093894 | 0.26368 | 0.083204 | 0.31169 | -0.41003 | -8.01 | 49.4782 | 81.0551 | 81.4651 | -7.8658 | -7.8259 | 120.4717 | 120.5529 | 120.7814 | 118.7498 | -120.6395 | 112.4597 | 112.6039 | 112.6437 | 81.3361 | -120.8797
1381.9219 | 120.6162 | -119.4077 | 1.1856 | 1.4211e-13 | -0.021081 | 0.00092524 | 0.067554 | -0.011638 | 0.059326 | 0.0079357 | 0.0049607 | 0.01346 | 0.0039354 | 0.094115 | 0.13136 | -118.8035 | -0.20005 | -119.2406 | 1.1738 | 1.255 | 1.4881 | -119.4906 | -66.7703 | -36.4828 | -36.7639 | -6.5223 | -6.3918 | -6.3382 | -119.7445 | -0.082913 | -0.011775 | 0.60411 | 0.16709 | 0.25 | 0.069376 | 0.30247 | -0.33689 | -7.7079 | 52.6374 | 82.6438 | 82.9807 | -7.5774 | -7.5238 | 120.5815 | 120.6626 | 120.8957 | 119.2076 | -120.6762 | 112.8854 | 113.0159 | 113.0695 | 82.9249 | -120.9301
1383.6562 | 120.575 | -119.3756 | 1.2222 | 1.4211e-13 | -0.021295 | 0.00092524 | 0.067126 | -0.011425 | 0.059326 | 0.015566 | 0.0049607 | 0.012606 | 0.0043626 | 0.094328 | 0.13692 | -118.6616 | -0.20005 | -119.0941 | 1.3387 | 1.3374 | 1.6529 | -119.344 | -60.3189 | -36.437 | -36.7501 | -6.568 | -6.4238 | -6.3794 | -119.598 | 0.031568 | 0.11643 | 0.714 | 0.28155 | 0.24998 | 0.11518 | 0.43068 | -0.22241 | -7.7903 | 59.0567 | 82.6255 | 82.8479 | -7.646 | -7.6016 | 120.7143 | 120.713 | 121.0285 | 119.1756 | -120.5663 | 112.8076 | 112.9518 | 112.9962 | 82.9386 | -120.8202
1385.3281 | 120.5841 | -118.6203 | 1.9821 | 1.4211e-13 | -0.021081 | 0.00092524 | 0.067554 | -0.011638 | 0.059326 | 0.00030522 | 0.0034653 | 0.0079054 | 0.010986 | 0.09326 | 0.16661 | -117.3247 | -0.19547 | -117.7526 | 2.671 | 2.6424 | 2.9715 | -117.952 | -22.2881 | -36.611 | -36.9653 | -6.1835 | -6.0484 | -5.9994 | -118.2518 | 0.66825 | 0.68885 | 1.2956 | 0.86767 | 0.19942 | 0.66028 | 0.98942 | 0.36846 | -8.1656 | 96.3322 | 81.655 | 81.2865 | -8.0305 | -7.9815 | 121.2913 | 121.2627 | 121.5918 | 118.4248 | -119.9342 | 112.4368 | 112.5719 | 112.6209 | 82.0093 | -120.234
1387.0781 | 120.4285 | -115.2145 | 4.9255 | 1.4211e-13 | -0.021081 | 0.00071164 | 0.067126 | -0.011852 | 0.059539 | 0.015566 | 0.0034653 | 0.0072644 | 0.011199 | 0.092192 | 0.16426 | -114.944 | -0.15884 | -115.349 | 4.7496 | 4.7899 | 5.0044 | -115.5893 | -19.0922 | -35.2465 | -35.6192 | -6.1056 | -5.9659 | -5.9307 | -115.8388 | -0.37478 | -0.17598 | 0.27058 | -0.13449 | 0.24029 | -0.13562 | 0.078905 | -0.62427 | -11.0312 | 96.1224 | 79.5953 | 80.2196 | -10.8915 | -10.8562 | 119.9641 | 120.0045 | 120.219 | 115.0557 | -120.5149 | 109.1089 | 109.2486 | 109.2838 | 79.968 | -120.7643
1388.7656 | 120.5795 | -117.0456 | 3.3142 | 1.4211e-13 | -0.020867 | 0.00092524 | 0.067554 | -0.011425 | 0.059112 | 0.0079357 | 0.0036789 | 0.007478 | 0.011413 | 0.09326 | 0.17345 | -116.3495 | -0.18632 | -116.7591 | 3.5546 | 3.6314 | 3.8506 | -117.0134 | -18.4557 | -34.9169 | -35.2758 | -6.0965 | -5.9568 | -5.9261 | -117.2537 | 0.032224 | 0.24038 | 0.69607 | 0.28645 | 0.25423 | 0.31724 | 0.53642 | -0.20807 | -9.4107 | 98.5899 | 81.7698 | 81.9779 | -9.271 | -9.2403 | 120.6002 | 120.677 | 120.8962 | 116.8593 | -120.3276 | 110.9491 | 111.0888 | 111.1195 | 82.1287 | -120.5679
1390.5156 | 120.6848 | -116.7801 | 3.6484 | 1.4211e-13 | -0.021081 | 0.00092524 | 0.067126 | -0.011638 | 0.059112 | 0.015566 | 0.0034653 | 0.007478 | 0.010986 | 0.09326 | 0.17708 | -116.757 | -0.14511 | -117.1758 | 3.1929 | 3.2789 | 3.5027 | -117.3476 | -18.0162 | -35.6403 | -36.0038 | -6.0095 | -5.8561 | -5.8254 | -117.6749 | -0.56754 | -0.45547 | 0.02309 | -0.39567 | 0.17186 | -0.36951 | -0.14572 | -0.89482 | -9.6578 | 98.7639 | 80.7763 | 81.6711 | -9.5044 | -9.4738 | 119.973 | 120.059 | 120.2828 | 116.635 | -120.996 | 110.7706 | 110.924 | 110.9547 | 81.1398 | -121.3233
1392.2031 | 120.5978 | -117.6773 | 2.8473 | 1.4211e-13 | -0.021508 | 0.0011388 | 0.06734 | -0.011638 | 0.059326 | 0.0079357 | 0.0036789 | 0.009401 | 0.009063 | 0.093474 | 0.18178 | -117.1965 | -0.13595 | -117.6061 | 2.7854 | 2.7798 | 3.0814 | -117.7964 | -17.485 | -35.5991 | -35.958 | -6.6871 | -6.552 | -6.5168 | -118.1145 | -0.11906 | -0.061865 | 0.48078 | 0.071184 | 0.19024 | -0.067524 | 0.23414 | -0.43717 | -9.5344 | 100.1923 | 81.7193 | 82.1565 | -9.3993 | -9.364 | 120.4627 | 120.4571 | 120.7587 | 117.5414 | -120.6437 | 110.9902 | 111.1253 | 111.1605 | 82.0782 | -120.9618
1393.9531 | 120.6985 | -118.0847 | 2.4307 | 1.4211e-13 | -0.021508 | 0.00071164 | 0.067554 | -0.011425 | 0.059326 | 0.015566 | 0.0038925 | 0.0079054 | 0.010558 | 0.093901 | 0.18584 | -117.6132 | -0.168 | -118.0456 | 2.3917 | 2.4135 | 2.6922 | -118.2222 | -17.3797 | -35.3976 | -35.7566 | -6.7787 | -6.639 | -6.5992 | -118.5449 | -0.13749 | -0.039041 | 0.47156 | 0.039079 | 0.17657 | -0.017273 | 0.26152 | -0.46017 | -9.2094 | 100.705 | 82.3282 | 82.7883 | -9.0697 | -9.0299 | 120.4764 | 120.4982 | 120.777 | 117.9167 | -120.6529 | 111.3061 | 111.4457 | 111.4855 | 82.6871 | -120.9756
1395.7031 | 120.694 | -117.8604 | 2.6917 | 1.4211e-13 | -0.021295 | 0.0011388 | 0.067554 | -0.011425 | 0.059112 | 0.0079357 | 0.0034653 | 0.009401 | 0.0092766 | 0.09326 | 0.19225 | -117.3064 | -0.168 | -117.7343 | 2.7167 | 2.7386 | 3.0128 | -117.9154 | -16.7479 | -35.97 | -36.2053 | -6.7832 | -6.6482 | -6.6038 | -118.2381 | -0.055004 | 0.025099 | 0.55401 | 0.1261 | 0.1811 | 0.046906 | 0.3211 | -0.3777 | -9.4749 | 101.1125 | 81.6551 | 82.0328 | -9.3398 | -9.2954 | 120.5772 | 120.599 | 120.8732 | 117.6924 | -120.6071 | 111.0772 | 111.2123 | 111.2567 | 81.8904 | -120.9298
1397.4375 | 120.726 | -117.4118 | 3.1448 | 1.4211e-13 | -0.021508 | 0.0013526 | 0.067554 | -0.011425 | 0.059539 | 0.00030522 | 0.0036789 | 0.00876 | 0.0097038 | 0.094115 | 0.20635 | -116.8944 | -0.16342 | -117.3268 | 3.1425 | 3.1644 | 3.3928 | -117.4987 | -17.4118 | -34.2118 | -34.502 | -6.6367 | -6.5108 | -6.4664 | -117.8169 | -0.086931 | -0.002297 | 0.51745 | 0.084956 | 0.17189 | 0.01956 | 0.24794 | -0.40505 | -9.7816 | 100 | 82.9098 | 83.3149 | -9.6556 | -9.6112 | 120.5543 | 120.5762 | 120.8046 | 117.2484 | -120.6436 | 110.7751 | 110.901 | 110.9454 | 83.2 | -120.9617
1399.1719 | 120.5475 | -112.0377 | 8.5052 | 1.4211e-13 | -0.021295 | 0.0013526 | 0.067126 | -0.011425 | 0.059326 | 0.00030522 | 0.0038925 | 0.00876 | 0.0092766 | 0.090268 | 1.6765 | -112.403 | -0.13595 | -112.8081 | 7.579 | 7.5876 | 7.8203 | -112.9931 | -15.8504 | -34.1156 | -34.5295 | -6.4765 | -6.346 | -6.2832 | -113.1053 | -0.95541 | -0.92625 | -0.36529 | -0.77043 | 0.18499 | -0.91761 | -0.68497 | -1.0676 | -14.9817 | 96.1872 | 77.5082 | 78.5758 | -14.8512 | -14.7885 | 119.6167 | 119.6253 | 119.8579 | 111.9017 | -121.4983 | 105.5612 | 105.6917 | 105.7544 | 77.9221 | -121.6105
1400.8594 | 120.6802 | -113.5025 | 6.9397 | 1.4211e-13 | -0.021508 | 0.00071164 | 0.067554 | -0.011425 | 0.059112 | -0.0073253 | 0.0041061 | 0.0098282 | 0.0086356 | 0.088345 | 1.6741 | -112.9753 | -0.13137 | -113.3804 | 6.9884 | 6.9924 | 7.2296 | -113.5746 | -17.3935 | -37.7328 | -38.1054 | -6.7603 | -6.6207 | -6.5854 | -113.6913 | -0.072095 | 0.048688 | 0.52725 | 0.12213 | 0.19423 | 0.05268 | 0.28995 | -0.18884 | -13.7 | 96.109 | 75.3971 | 75.5859 | -13.5604 | -13.5251 | 120.4909 | 120.4949 | 120.7321 | 113.3711 | -120.5143 | 106.7422 | 106.8818 | 106.9171 | 75.7697 | -120.631
1402.5938 | 120.4788 | -115.8691 | 4.6463 | 1.4211e-13 | -0.021295 | 0.00092524 | 0.06734 | -0.011852 | 0.058898 | 0.0079357 | 0.0045333 | 0.009401 | 0.0086356 | 0.087491 | 1.2949 | -114.6921 | -0.18174 | -115.0926 | 5.2852 | 5.2432 | 5.531 | -115.3421 | -17.3156 | -40.2786 | -40.7382 | -6.7603 | -6.6161 | -6.5763 | -115.4633 | 0.52708 | 0.63892 | 1.177 | 0.77649 | 0.24941 | 0.59693 | 0.88468 | 0.4058 | -11.4066 | 98.5535 | 75.131 | 74.7252 | -11.2624 | -11.2226 | 121.1544 | 121.1124 | 121.4001 | 115.6874 | -119.9884 | 109.1088 | 109.253 | 109.2929 | 75.5906 | -120.1096
1404.2812 | 120.4788 | -113.0951 | 7.4203 | 1.4211e-13 | -0.021081 | 0.00092524 | 0.06734 | -0.011425 | 0.058898 | 0.0079357 | 0.0060289 | 0.010256 | 0.0064992 | 0.11121 | 1.894 | -112.8608 | -0.11764 | -113.2705 | 7.0754 | 7.1023 | 7.3166 | -113.4555 | -17.1371 | -101.3265 | -7.8447 | -5.9912 | -5.8469 | -5.8117 | -113.5402 | -0.36045 | -0.34497 | 0.2343 | -0.1754 | 0.18505 | -0.31808 | -0.10371 | -0.44515 | -13.4115 | 95.958 | 105.2504 | 105.6955 | -13.2673 | -13.232 | 120.1705 | 120.1974 | 120.4117 | 112.9775 | -120.8759 | 107.1039 | 107.2482 | 107.2834 | 11.7686 | -120.9606
1406.0312 | 120.0165 | -114.1022 | 5.7037 | 1.4211e-13 | -0.021295 | 0.0015662 | 0.067126 | -0.011638 | 0.058471 | 0.0079357 | 0.0045333 | 0.0098282 | 0.007781 | 0.1127 | 2.4555 | -112.9707 | -0.17258 | -113.3666 | 6.4161 | 6.42 | 6.6573 | -113.6066 | -17.279 | -66.0475 | -6.3521 | -5.7073 | -5.563 | -5.5415 | -113.5815 | 0.49552 | 0.71235 | 1.1315 | 0.73554 | 0.24001 | 0.71628 | 0.95358 | 0.52072 | -11.411 | 96.8232 | 107.7501 | 107.2294 | -11.2668 | -11.2453 | 120.5183 | 120.5222 | 120.7595 | 113.9296 | -119.3104 | 108.3949 | 108.5391 | 108.5607 | 48.0546 | -119.2852
1407.7188 | 120.1538 | -4.7104 | 115.2328 | 1.4211e-13 | -0.020654 | 0.0019936 | 0.067981 | -0.011638 | 0.057616 | 0.0079357 | -0.0018757 | 0.0051278 | 0.01825 | 0.034713 | 0.11961 | -4.8658 | 0.43179 | -4.9713 | 115.2169 | 115.1924 | 115.2389 | -5.0083 | -0.80938 | -1.5701 | -0.28986 | -0.16731 | -0.027501 | -0.074664 | -5.1001 | -0.29791 | -0.015953 | -0.15539 | -0.26088 | 0.037031 | -0.040485 | 0.006027 | -0.38973 | -115.4002 | 3.901 | 4.4205 | 4.8102 | -115.2604 | -115.3075 | 119.9273 | 119.9028 | 119.9493 | 5.1422 | -120.2411 | 4.5431 | 4.6829 | 4.6357 | 3.1402 | -120.333
1409.4688 | 119.751 | -4.5364 | 115.8188 | 1.4211e-13 | -0.020654 | 0.0019936 | 0.068195 | -0.011638 | 0.058044 | 0.0079357 | -0.0023031 | 0.0053414 | 0.01825 | 0.034072 | 0.12132 | -4.3484 | 0.34938 | -4.4356 | 115.8991 | 115.8746 | 115.9165 | -4.4955 | -0.63081 | -1.822 | -0.28986 | -0.14442 | -0.004608 | -0.083821 | -4.5827 | 0.040982 | 0.080289 | 0.18802 | 0.10083 | 0.059849 | 0.055836 | 0.097722 | -0.046269 | -115.9632 | 3.9056 | 4.2466 | 4.2928 | -115.8234 | -115.9026 | 120.4355 | 120.4111 | 120.4529 | 4.8858 | -120.3142 | 4.392 | 4.5318 | 4.4526 | 2.7145 | -120.4015
1411.2031 | 120.4056 | -4.3259 | 116.011 | 1.4211e-13 | -0.020867 | 0.00178 | 0.067767 | -0.012066 | 0.058257 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018463 | 0.033859 | 0.11897 | -4.1744 | 0.31275 | -4.2616 | 116.1463 | 116.1219 | 116.1821 | -4.3169 | -0.60792 | -1.7533 | -0.28986 | -0.13526 | -0.009187 | -0.0884 | -4.395 | 0.008989 | 0.13526 | 0.15142 | 0.064235 | 0.055246 | 0.11084 | 0.17102 | -0.069109 | -116.1463 | 3.7179 | 4.036 | 4.1051 | -116.0202 | -116.0994 | 120.4722 | 120.4478 | 120.5079 | 4.6386 | -120.3279 | 4.1906 | 4.3167 | 4.2375 | 2.5726 | -120.406
1412.9375 | 120.4147 | -3.8681 | 116.5695 | 1.4211e-13 | -0.020654 | 0.00178 | 0.068195 | -0.012279 | 0.058044 | 0.015566 | -0.0018757 | 0.0053414 | 0.018463 | 0.034286 | 0.11085 | -3.7624 | 0.29902 | -3.8038 | 116.6179 | 116.5844 | 116.6445 | -3.9048 | -1.9541 | -1.6526 | -0.3036 | -0.14442 | -0.004608 | -0.079243 | -3.992 | -0.036672 | 0.048364 | 0.10572 | 0.064299 | 0.10097 | 0.014838 | 0.074988 | -0.12394 | -116.7139 | 1.914 | 3.5645 | 3.6884 | -116.5741 | -116.6488 | 120.486 | 120.4525 | 120.5126 | 4.1671 | -120.4743 | 3.7237 | 3.8635 | 3.7889 | 2.2155 | -120.5616
1414.625 | 119.5724 | -3.7033 | 116.6931 | 1.4211e-13 | -0.020654 | 0.0015662 | 0.068409 | -0.011852 | 0.05783 | 0.0079357 | -0.0018757 | 0.0051278 | 0.018677 | 0.033645 | 0.070469 | -3.6571 | 0.32649 | -3.7397 | 116.7323 | 116.7126 | 116.7681 | -3.804 | -0.85975 | -0.97033 | -0.2395 | -0.12152 | 0.013707 | -0.092979 | -3.905 | -0.10073 | 0.039227 | 0.046224 | -0.0364 | 0.064331 | 0.019452 | 0.075014 | -0.20173 | -116.8146 | 2.8436 | 3.4638 | 3.6655 | -116.6794 | -116.7861 | 120.4357 | 120.4159 | 120.4714 | 4.0298 | -120.4972 | 3.5818 | 3.717 | 3.6103 | 2.733 | -120.5982
1416.3594 | 120.488 | -3.3737 | 117.0822 | 1.4211e-13 | -0.02044 | 0.0019936 | 0.068409 | -0.011638 | 0.05783 | 0.0079357 | -0.0023031 | 0.0051278 | 0.018463 | 0.033431 | 0.074315 | -3.2817 | 0.29444 | -3.3551 | 117.1536 | 117.1292 | 117.1894 | -3.424 | -0.85975 | -0.94743 | -0.2395 | -0.10779 | 0.027442 | -0.10214 | -3.5158 | -0.05027 | 0.07134 | 0.092061 | 0.018586 | 0.068856 | 0.047035 | 0.10715 | -0.14212 | -117.19 | 2.514 | 3.1342 | 3.2763 | -117.0548 | -117.1843 | 120.5273 | 120.503 | 120.5631 | 3.6682 | -120.5062 | 3.2659 | 3.4012 | 3.2716 | 2.4263 | -120.5981
1418.0938 | 120.5841 | -3.3737 | 117.1051 | 1.4211e-13 | -0.020654 | 0.0019936 | 0.068195 | -0.011638 | 0.058044 | 0.00030522 | -0.0020893 | 0.0053414 | 0.018463 | 0.033431 | 0.07987 | -3.2176 | 0.2807 | -3.3048 | 117.2451 | 117.2208 | 117.2764 | -3.369 | -0.81396 | -0.9978 | -0.24408 | -0.10321 | 0.0366 | -0.10214 | -3.4426 | 0.004677 | 0.14002 | 0.15616 | 0.068947 | 0.06427 | 0.11572 | 0.17125 | -0.068864 | -117.2083 | 2.5598 | 3.1296 | 3.1985 | -117.0685 | -117.2072 | 120.6188 | 120.5945 | 120.6501 | 3.6544 | -120.4741 | 3.2705 | 3.4103 | 3.2716 | 2.3759 | -120.5477
1419.8438 | 119.957 | -119.7876 | 0.21057 | 1.4211e-13 | -0.021508 | 0.0013526 | 0.067126 | -0.011425 | 0.058898 | 0.0079357 | -0.0020893 | 0.0049142 | 0.019104 | 0.031508 | 0.038421 | -119.1149 | -0.37862 | -119.4878 | 0.37261 | 0.38957 | 0.6273 | -119.747 | 0.051413 | -0.0729 | -0.028879 | 0.10282 | 0.25637 | 0.12222 | -0.5213 | 0.040611 | 0.16204 | 0.67273 | 0.2998 | 0.25919 | 0.179 | 0.41673 | 119.2663 | -0.10775 | 119.839 | 119.7587 | 0.49242 | 0.045801 | -0.088355 | 120.1602 | 120.1772 | 120.4149 | 119.409 | -119.9576 | 119.8904 | 120.044 | 119.9098 | 119.7147 | -0.73187
1421.5781 | 120.108 | -119.8425 | 0.1831 | 1.4211e-13 | -0.021508 | 0.0011388 | 0.067126 | -0.011425 | 0.058898 | 0.0079357 | -0.0023031 | 0.0051278 | 0.018677 | 0.031508 | 0.0076551 | -119.2568 | -0.29162 | -119.6847 | 0.28563 | 0.31173 | 0.53573 | -119.9439 | 0.074307 | 0.023253 | -0.010564 | 0.11656 | 0.25637 | 0.15427 | -0.20994 | -0.10135 | 0.10252 | 0.58573 | 0.15787 | 0.25922 | 0.12862 | 0.35262 | 119.6326 | -0.066548 | 119.9168 | 119.832 | 0.19937 | 0.073267 | -0.028839 | 120.1282 | 120.1543 | 120.3783 | 119.5509 | -120.127 | 119.9591 | 120.0989 | 119.9968 | 119.8658 | -0.39304
1423.2656 | 115.6769 | -83.606 | 31.8695 | 1.4211e-13 | -0.021722 | 0.0011388 | 0.063921 | -0.010997 | 0.054839 | -0.0073253 | -0.0023031 | 0.0051278 | 0.018677 | 0.031936 | 0.0078689 | -82.1444 | -0.13137 | -82.3488 | 32.957 | 32.9778 | 33.1995 | -82.5203 | 0.051413 | 0.014095 | -0.015143 | 0.11198 | 0.24721 | 0.048958 | -0.20536 | 1.0856 | 1.0875 | 1.4616 | 1.2572 | 0.17154 | 1.1083 | 1.33 | 83.4006 | -31.7575 | 83.6574 | 83.5908 | 0.19022 | -31.6223 | -31.8205 | 116.563 | 116.5837 | 116.8054 | 83.4746 | -114.3898 | 83.7179 | 83.8532 | 83.6549 | 83.6201 | -32.0749
1425.0156 | 119.8517 | -119.5999 | 0.16022 | 1.4211e-13 | -0.021722 | 0.0011388 | 0.066913 | -0.011425 | 0.058471 | 0.00030522 | -0.0025167 | 0.0049142 | 0.018891 | 0.031295 | 0.0076551 | -119.037 | -0.2321 | -119.4695 | 0.19864 | 0.26136 | 0.48994 | -119.7195 | 0.055992 | 0.014095 | -0.005985 | 0.11198 | 0.25179 | 0.14969 | -0.20078 | -0.1196 | 0.038419 | 0.56288 | 0.13043 | 0.25003 | 0.10114 | 0.32972 | 119.3991 | -0.048238 | 119.6559 | 119.5939 | 0.19479 | 0.091577 | -0.01053 | 119.7986 | 119.8613 | 120.0899 | 119.3678 | -119.8797 | 119.7119 | 119.8517 | 119.7496 | 119.614 | -0.361
1426.6875 | 119.9112 | -119.7784 | 0.19684 | 1.4211e-13 | -0.021508 | 0.00092524 | 0.067126 | -0.011852 | 0.058898 | 0.015566 | -0.0025167 | 0.0051278 | 0.019104 | 0.031295 | 0.0076551 | -119.1881 | -0.20921 | -119.6206 | 0.19864 | 0.2522 | 0.48078 | -119.8706 | 0.055992 | 0.014095 | -0.005985 | 0.11198 | 0.25637 | 0.14053 | -0.20078 | -0.092176 | 0.001798 | 0.59032 | 0.15788 | 0.25005 | 0.055362 | 0.28395 | 119.5777 | -0.084859 | 119.8344 | 119.7725 | 0.19479 | 0.059534 | -0.056308 | 119.9771 | 120.0306 | 120.2592 | 119.5692 | -120.0675 | 119.8904 | 120.0348 | 119.919 | 119.7925 | -0.39762
1428.4219 | 120.1218 | -119.8196 | 0.16937 | 1.4211e-13 | -0.022149 | 0.0011388 | 0.067126 | -0.011852 | 0.059112 | 0.015566 | -0.0029439 | 0.0051278 | 0.018677 | 0.031936 | 0.0076551 | -119.2751 | -0.19547 | -119.7076 | 0.18948 | 0.25678 | 0.48078 | -119.9714 | 0.055992 | 0.014095 | -0.010564 | 0.11656 | 0.26095 | 0.15427 | -0.19162 | -0.15171 | 0.020106 | 0.54453 | 0.11209 | 0.2638 | 0.087406 | 0.31141 | 119.628 | -0.052816 | 119.8756 | 119.8091 | 0.18106 | 0.091578 | -0.015107 | 120.0091 | 120.0764 | 120.3004 | 119.6242 | -120.1407 | 119.9362 | 120.0806 | 119.9739 | 119.8337 | -0.36099
1430.1094 | 120.1904 | -119.8517 | 0.13733 | 1.4211e-13 | -0.021295 | 0.00092524 | 0.067126 | -0.011425 | 0.059112 | 0.0079357 | -0.0023031 | 0.0051278 | 0.018463 | 0.031936 | 0.0076551 | -119.3255 | -0.1909 | -119.7671 | 0.19864 | 0.15146 | 0.48536 | -119.9439 | 0.055992 | 0.009516 | -0.010564 | 0.11656 | 0.26095 | 0.15427 | -0.19162 | -0.092196 | 0.061307 | 0.52621 | 0.084613 | 0.17681 | 0.014134 | 0.34803 | 119.6601 | -0.020772 | 119.9077 | 119.8411 | 0.18106 | 0.12362 | 0.016937 | 120.0503 | 120.0031 | 120.337 | 119.6608 | -120.0812 | 119.9682 | 120.1126 | 120.006 | 119.8612 | -0.32895
1431.8594 | 120.1447 | -119.7418 | 0.31586 | 1.4211e-13 | -0.021936 | 0.00092524 | 0.067126 | -0.011425 | 0.059112 | 0.015566 | -0.0023031 | 0.0053414 | 0.019104 | 0.031295 | 0.0076551 | -119.2156 | -0.17716 | -119.6526 | 0.32225 | 0.28883 | 0.61814 | -119.8294 | 0.055992 | 0.018674 | -0.010564 | 0.11656 | 0.26095 | 0.11764 | -0.1962 | -0.087587 | 0.006396 | 0.52623 | 0.089206 | 0.17679 | -0.027026 | 0.30228 | 119.5456 | -0.1993 | 119.7978 | 119.7313 | 0.18564 | -0.054906 | -0.19822 | 120.0641 | 120.0307 | 120.36 | 119.5647 | -120.1453 | 119.8584 | 120.0028 | 119.8595 | 119.7605 | -0.51206
1433.5938 | 120.1309 | -119.87 | 0.21973 | 1.4211e-13 | -0.021722 | 0.00092524 | 0.06734 | -0.011638 | 0.058685 | 0.015566 | -0.0025167 | 0.0047004 | 0.018891 | 0.031722 | 0.0072279 | -118.9684 | -0.18174 | -119.4054 | 0.52828 | 0.53151 | 0.83334 | -119.5821 | 0.051413 | 0.018674 | -0.015143 | 0.11656 | 0.25637 | 0.13137 | -0.19162 | 0.28785 | 0.30855 | 0.90163 | 0.46461 | 0.17676 | 0.31179 | 0.61361 | 119.6784 | -0.10317 | 119.9214 | 119.8549 | 0.17648 | 0.036645 | -0.088354 | 120.3983 | 120.4015 | 120.7033 | 119.6883 | -119.8019 | 119.9866 | 120.1264 | 120.0014 | 119.8887 | -0.41135
1435.3438 | 120.2225 | -120.0302 | 0.19226 | 1.4211e-13 | -0.021936 | 0.0013526 | 0.06734 | -0.011638 | 0.059112 | 0.00030522 | -0.0025167 | 0.0051278 | 0.019104 | 0.031508 | 0.0074415 | -119.4445 | -0.17716 | -119.8907 | 0.18032 | 0.14688 | 0.47163 | -120.0675 | 0.055992 | 0.014095 | -0.010564 | 0.12571 | 0.26095 | 0.14969 | -0.20536 | -0.0373 | -0.011938 | 0.5857 | 0.13953 | 0.17683 | -0.045376 | 0.27936 | 119.8249 | -0.066547 | 120.0862 | 120.0196 | 0.19479 | 0.06869 | -0.042574 | 120.2105 | 120.1771 | 120.5018 | 119.8531 | -120.2598 | 120.1559 | 120.2912 | 120.1799 | 120.0443 | -0.39762
1437.0469 | 120.3094 | -120.0394 | 0.17853 | 1.4211e-13 | -0.022149 | 0.0011388 | 0.06734 | -0.011638 | 0.058685 | -0.014956 | -0.0025167 | 0.0053414 | 0.018463 | 0.031295 | 0.0076551 | -119.4857 | -0.17716 | -119.9182 | 0.18948 | 0.15146 | 0.4762 | -120.1041 | 0.060571 | 0.009516 | -0.001407 | 0.12114 | 0.26095 | 0.12679 | -0.18704 | -0.064775 | 0.010951 | 0.55365 | 0.12121 | 0.18599 | -0.027065 | 0.29768 | 119.8523 | -0.057392 | 120.0999 | 120.038 | 0.18564 | 0.082423 | -0.051734 | 120.2288 | 120.1908 | 120.5156 | 119.8622 | -120.2827 | 120.1605 | 120.3003 | 120.1662 | 120.0489 | -0.36557
1438.7969 | 120.1904 | -119.9615 | 0.30212 | 1.4211e-13 | -0.021508 | 0.00092524 | 0.06734 | -0.011638 | 0.059326 | 0.00030522 | -0.0023031 | 0.0049142 | 0.019104 | 0.031508 | 0.0076551 | -119.3804 | -0.18174 | -119.822 | 0.28105 | 0.23388 | 0.57235 | -119.9942 | 0.055992 | 0.018674 | -0.005985 | 0.11656 | 0.26095 | 0.058115 | -0.18704 | -0.032701 | -0.021077 | 0.58113 | 0.13954 | 0.17224 | -0.06824 | 0.27023 | 119.7745 | -0.18557 | 120.0175 | 119.9556 | 0.18106 | -0.041173 | -0.24401 | 120.2426 | 120.1954 | 120.5339 | 119.7798 | -120.2964 | 120.0781 | 120.2225 | 120.0197 | 119.9802 | -0.48917
1440.5469 | 120.2499 | -120.1218 | 0.19226 | 1.4211e-13 | -0.021722 | 0.00071164 | 0.066913 | -0.011638 | 0.058898 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.031508 | 0.0076551 | -119.5361 | -0.17716 | -119.9823 | 0.18032 | 0.14231 | 0.48078 | -120.1591 | 0.060571 | 0.018674 | -0.001407 | 0.11656 | 0.25637 | 0.085587 | -0.19162 | -0.037325 | -0.011938 | 0.58568 | 0.13951 | 0.17684 | -0.049955 | 0.28852 | 119.9301 | -0.075704 | 120.1823 | 120.1204 | 0.19021 | 0.064111 | -0.10667 | 120.3021 | 120.2641 | 120.6025 | 119.9446 | -120.3514 | 120.2383 | 120.3781 | 120.2074 | 120.1404 | -0.38388
1442.2188 | 120.2682 | -120.1538 | 0.19226 | 1.4211e-13 | -0.021508 | 0.00071164 | 0.06734 | -0.011638 | 0.059326 | -0.0073253 | -0.0025167 | 0.0053414 | 0.018891 | 0.031722 | 0.0076551 | -119.559 | -0.17716 | -120.0051 | 0.1849 | 0.14688 | 0.42584 | -120.1774 | 0.051413 | 0.023253 | -0.001407 | 0.12114 | 0.25637 | 0.1039 | -0.20078 | -0.023597 | -0.00736 | 0.59484 | 0.14867 | 0.17226 | -0.045376 | 0.23358 | 119.953 | -0.071125 | 120.2052 | 120.1524 | 0.19937 | 0.064111 | -0.08836 | 120.3387 | 120.3007 | 120.5796 | 119.9766 | -120.3697 | 120.2749 | 120.4102 | 120.2577 | 120.1771 | -0.39304
1443.9688 | 120.2957 | -120.1675 | 0.1831 | 1.4211e-13 | -0.021936 | 0.0013526 | 0.067126 | -0.011852 | 0.059112 | 0.00030522 | -0.0023031 | 0.0051278 | 0.018891 | 0.031295 | 0.0074415 | -119.5773 | -0.17716 | -120.0235 | 0.1849 | 0.14231 | 0.42584 | -120.1957 | 0.060571 | 0.009516 | -0.001407 | 0.12114 | 0.26095 | 0.07643 | -0.1962 | -0.02818 | 0.001796 | 0.59025 | 0.14409 | 0.17227 | -0.040799 | 0.24273 | 119.9713 | -0.061969 | 120.2281 | 120.1661 | 0.19479 | 0.077846 | -0.10667 | 120.3524 | 120.3098 | 120.5934 | 119.9904 | -120.3788 | 120.2887 | 120.4285 | 120.244 | 120.1771 | -0.37931
1445.7188 | 120.2591 | -119.7784 | 0.50812 | 1.4211e-13 | -0.021722 | 0.00092524 | 0.067554 | -0.011638 | 0.058685 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018891 | 0.031722 | 0.0074415 | -119.2568 | -0.17258 | -119.6892 | 0.4596 | 0.4262 | 0.72345 | -119.8752 | 0.055992 | 0.018674 | -0.005985 | 0.11656 | 0.25179 | 0.016908 | -0.1962 | -0.096755 | -0.048514 | 0.52164 | 0.089201 | 0.18596 | -0.081919 | 0.21533 | 119.5822 | -0.39156 | 119.8344 | 119.7725 | 0.19022 | -0.25632 | -0.49121 | 120.238 | 120.2046 | 120.5019 | 119.6059 | -120.3833 | 119.895 | 120.0302 | 119.7953 | 119.7971 | -0.70432
1447.4688 | 120.369 | -120.2133 | 0.1831 | 1.4211e-13 | -0.021936 | 0.0011388 | 0.067554 | -0.011852 | 0.058898 | 0.0079357 | -0.0025167 | 0.0053414 | 0.018891 | 0.031936 | 0.0076551 | -119.6139 | -0.17258 | -120.0647 | 0.18032 | 0.13773 | 0.42584 | -120.2324 | 0.06515 | 0.023253 | -0.005985 | 0.11198 | 0.25179 | 0.021486 | -0.18704 | -0.019035 | -0.002782 | 0.5994 | 0.14866 | 0.16769 | -0.045378 | 0.24273 | 120.0263 | -0.071126 | 120.2785 | 120.2073 | 0.18106 | 0.068689 | -0.16162 | 120.3936 | 120.351 | 120.6392 | 120.0407 | -120.4155 | 120.3253 | 120.4651 | 120.2348 | 120.2366 | -0.37015
1449.1562 | 120.3552 | -120.2408 | 0.19684 | 1.4211e-13 | -0.021722 | 0.00092524 | 0.067126 | -0.011425 | 0.059112 | 0.0079357 | -0.0027303 | 0.0049142 | 0.019104 | 0.031295 | 0.0072279 | -119.6368 | -0.17716 | -120.0784 | 0.1849 | 0.14231 | 0.42584 | -120.2598 | 0.060571 | 0.023253 | -0.001407 | 0.11656 | 0.25637 | 0.058115 | -0.19162 | -0.019042 | -0.011937 | 0.60398 | 0.16239 | 0.18143 | -0.054532 | 0.229 | 120.0492 | -0.080281 | 120.3014 | 120.2394 | 0.19021 | 0.059534 | -0.13872 | 120.4257 | 120.3831 | 120.6666 | 120.0636 | -120.4567 | 120.3573 | 120.4972 | 120.2989 | 120.264 | -0.38846
1450.8906 | 120.4056 | -120.0439 | 0.28381 | 1.4211e-13 | -0.021936 | 0.00092524 | 0.06734 | -0.011425 | 0.059326 | 0.00030522 | -0.0023031 | 0.0049142 | 0.018891 | 0.031508 | 0.0076551 | -119.4857 | -0.17258 | -119.9273 | 0.29936 | 0.25678 | 0.5403 | -120.0996 | 0.055992 | 0.014095 | -0.005985 | 0.11656 | 0.25637 | 0.067272 | -0.18704 | -0.055619 | 0.015548 | 0.55823 | 0.11663 | 0.17225 | -0.027034 | 0.25649 | 119.8569 | -0.16726 | 120.0999 | 120.038 | 0.18106 | -0.027441 | -0.21654 | 120.3433 | 120.3007 | 120.5842 | 119.8714 | -120.3834 | 120.1605 | 120.3003 | 120.1112 | 120.058 | -0.47086
1452.6406 | 120.4376 | -120.1996 | 0.16937 | 1.4211e-13 | -0.021722 | 0.00092524 | 0.067554 | -0.011852 | 0.058898 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018891 | 0.031722 | 0.0074415 | -119.6597 | -0.17258 | -120.1059 | 0.18032 | 0.14231 | 0.42126 | -120.2736 | 0.060571 | 0.018674 | -0.001407 | 0.12114 | 0.24264 | 0.030644 | -0.18704 | -0.073978 | 0.01095 | 0.53989 | 0.093721 | 0.1677 | -0.027067 | 0.25189 | 120.0125 | -0.048237 | 120.2602 | 120.1982 | 0.18564 | 0.073264 | -0.13873 | 120.3799 | 120.3419 | 120.6208 | 120.027 | -120.4429 | 120.3207 | 120.4422 | 120.2302 | 120.2183 | -0.35642
1454.3438 | 120.4742 | -120.2271 | 0.15106 | 1.4211e-13 | -0.022149 | 0.00092524 | 0.06734 | -0.011425 | 0.059112 | 0.00030522 | -0.0023031 | 0.0051278 | 0.018891 | 0.031508 | 0.0074415 | -119.6734 | -0.17258 | -120.1288 | 0.1849 | 0.14231 | 0.41668 | -120.301 | 0.055992 | 0.018674 | -0.010564 | 0.12114 | 0.25179 | 0.12222 | -0.19162 | -0.073986 | 0.033839 | 0.55362 | 0.098295 | 0.17228 | -0.008756 | 0.26562 | 120.0354 | -0.029926 | 120.283 | 120.2165 | 0.18106 | 0.10073 | -0.028846 | 120.412 | 120.3694 | 120.6437 | 120.0545 | -120.4521 | 120.3482 | 120.4788 | 120.3493 | 120.2457 | -0.34268
1456.0938 | 120.5109 | -120.2133 | 0.14191 | 1.4211e-13 | -0.021936 | 0.0011388 | 0.06734 | -0.011852 | 0.059112 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018891 | 0.031722 | 0.0076551 | -119.6826 | -0.17716 | -120.1333 | 0.19864 | 0.14688 | 0.42584 | -120.3148 | 0.055992 | 0.014095 | -0.015143 | 0.12114 | 0.26095 | 0.1039 | -0.18246 | -0.10146 | 0.056729 | 0.53073 | 0.079984 | 0.18144 | 0.004978 | 0.28393 | 120.0309 | -0.020771 | 120.2693 | 120.1982 | 0.16732 | 0.11904 | -0.038006 | 120.412 | 120.3602 | 120.6392 | 120.0362 | -120.4567 | 120.3345 | 120.4743 | 120.3172 | 120.2274 | -0.32437
1457.7969 | 120.4971 | -120.2408 | 0.19684 | 1.4211e-13 | -0.021936 | 0.00071164 | 0.067126 | -0.011638 | 0.058898 | 0.0079357 | -0.0027303 | 0.0057688 | 0.018677 | 0.031508 | 0.0074415 | -119.6872 | -0.168 | -120.1471 | 0.19406 | 0.1652 | 0.435 | -120.4018 | 0.051413 | 0.023253 | -0.010564 | 0.12571 | 0.26095 | 0.168 | -0.22367 | -0.16099 | -0.00278 | 0.55362 | 0.093715 | 0.2547 | -0.031638 | 0.23816 | 120.0171 | -0.071124 | 120.2922 | 120.2302 | 0.21311 | 0.064113 | -0.028836 | 120.4348 | 120.406 | 120.6758 | 120.0728 | -120.5986 | 120.3665 | 120.5017 | 120.4088 | 120.264 | -0.42051
1459.5156 | 120.1813 | -119.8471 | 0.15564 | 1.4211e-13 | -0.022149 | 0.0011388 | 0.06734 | -0.011638 | 0.059112 | 0.0079357 | -0.0025167 | 0.005555 | 0.018891 | 0.031722 | 0.0074415 | -119.3026 | -0.168 | -119.7488 | 0.1849 | 0.14231 | 0.42584 | -119.9393 | 0.060571 | 0.018674 | 0.003172 | 0.11198 | 0.26095 | 0.14511 | -0.18704 | -0.092195 | 0.029261 | 0.54452 | 0.098348 | 0.19054 | -0.013334 | 0.2702 | 119.6601 | -0.043661 | 119.9077 | 119.8503 | 0.19021 | 0.10531 | -0.010531 | 120.032 | 119.9894 | 120.2729 | 119.6791 | -120.0949 | 119.9591 | 120.1081 | 119.9922 | 119.8658 | -0.34268
1461.2656 | 120.4422 | -120.1904 | 0.2243 | 1.4211e-13 | -0.022149 | 0.0011388 | 0.067767 | -0.011638 | 0.059112 | 0.015566 | -0.0029439 | 0.0053414 | 0.018677 | 0.031722 | 0.0074415 | -119.6231 | -0.17716 | -120.0738 | 0.23526 | 0.1881 | 0.46247 | -120.301 | 0.06515 | 0.018674 | -0.005985 | 0.11656 | 0.26553 | 0.15884 | -0.18704 | -0.11061 | 0.010959 | 0.56736 | 0.11661 | 0.22722 | -0.036209 | 0.23816 | 120.0034 | -0.10775 | 120.2556 | 120.1844 | 0.18106 | 0.041226 | -0.065459 | 120.4257 | 120.3785 | 120.6529 | 120.0133 | -120.5253 | 120.307 | 120.456 | 120.3493 | 120.2091 | -0.41135
1463.0156 | 120.3552 | -119.8929 | 0.51727 | 1.4211e-13 | -0.021936 | 0.0011388 | 0.067126 | -0.012066 | 0.059112 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018677 | 0.031936 | 0.0076551 | -119.3575 | -0.17258 | -119.8174 | 0.44587 | 0.41704 | 0.6914 | -119.9988 | 0.055992 | 0.018674 | -0.005985 | 0.11656 | 0.26095 | 0.099323 | -0.18704 | -0.10595 | -0.071404 | 0.53536 | 0.07545 | 0.1814 | -0.10023 | 0.17412 | 119.7058 | -0.40072 | 119.9489 | 119.8869 | 0.18106 | -0.25632 | -0.41795 | 120.3388 | 120.3099 | 120.5843 | 119.7203 | -120.5161 | 120.0094 | 120.1538 | 119.9922 | 119.9116 | -0.70432
1464.7031 | 120.4742 | -120.2911 | 0.19226 | 1.4211e-13 | -0.021936 | 0.0011388 | 0.066913 | -0.011638 | 0.058898 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018891 | 0.031936 | 0.0074415 | -119.6963 | -0.18174 | -120.1562 | 0.19406 | 0.15146 | 0.42126 | -120.3285 | 0.060571 | 0.023253 | 0.003172 | 0.12571 | 0.25637 | 0.13137 | -0.18246 | -0.037372 | 0.001797 | 0.59481 | 0.13491 | 0.17228 | -0.040798 | 0.229 | 120.1087 | -0.066547 | 120.3517 | 120.2943 | 0.18564 | 0.064111 | -0.060888 | 120.4852 | 120.4426 | 120.7124 | 120.1094 | -120.5208 | 120.4169 | 120.5475 | 120.4225 | 120.3144 | -0.37472
1466.4375 | 120.607 | -120.2728 | 0.15106 | 1.4211e-13 | -0.022149 | 0.00049784 | 0.067126 | -0.011425 | 0.059326 | 0.00030522 | -0.0025167 | 0.005555 | 0.019104 | 0.031936 | 0.0074415 | -119.7375 | -0.17716 | -120.1929 | 0.1849 | 0.13773 | 0.4121 | -120.4247 | 0.06515 | 0.014095 | -0.005985 | 0.11198 | 0.26553 | 0.10848 | -0.22367 | -0.15184 | 0.033839 | 0.5353 | 0.079975 | 0.23182 | -0.013335 | 0.26104 | 120.0492 | -0.039083 | 120.338 | 120.2668 | 0.21769 | 0.11447 | -0.042582 | 120.4577 | 120.4106 | 120.6849 | 120.0957 | -120.5757 | 120.3848 | 120.5384 | 120.3813 | 120.2869 | -0.37474
1468.1719 | 120.3003 | -119.2337 | 0.97961 | 1.4211e-13 | -0.021722 | 0.00092524 | 0.06734 | -0.011852 | 0.058898 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018891 | 0.031722 | 0.0078689 | -118.657 | -0.168 | -119.1032 | 1.0319 | 1.0306 | 1.2729 | -119.3303 | 0.060571 | 0.018674 | -0.005985 | 0.11198 | 0.26095 | 0.12679 | -0.2191 | -0.096601 | 0.052289 | 0.57667 | 0.13048 | 0.22708 | 0.051003 | 0.29327 | 119.0146 | -0.86763 | 119.2943 | 119.2277 | 0.21311 | -0.71866 | -0.85282 | 120.2656 | 120.2643 | 120.5066 | 119.0657 | -120.3099 | 119.3457 | 119.4947 | 119.3605 | 119.2524 | -1.1987
1469.9219 | 120.3735 | -119.7327 | 0.53101 | 1.4211e-13 | -0.021722 | 0.0011388 | 0.066913 | -0.011852 | 0.058898 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018677 | 0.031722 | 0.0074415 | -119.1286 | -0.17258 | -119.5794 | 0.47334 | 0.48573 | 0.70971 | -119.7653 | 0.060571 | 0.018674 | -0.005985 | 0.11656 | 0.25179 | 0.14969 | -0.22367 | -0.032637 | -0.057667 | 0.60406 | 0.1533 | 0.18594 | -0.045281 | 0.17871 | 119.509 | -0.41445 | 119.7932 | 119.7267 | 0.21769 | -0.27921 | -0.38132 | 120.206 | 120.2184 | 120.4424 | 119.5601 | -120.2963 | 119.8492 | 119.9845 | 119.8824 | 119.7513 | -0.75468
1471.5938 | 120.5429 | -120.2866 | 0.15106 | 1.4211e-13 | -0.021722 | 0.00092524 | 0.06734 | -0.012066 | 0.058898 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018677 | 0.031722 | 0.0076551 | -119.7192 | -0.18174 | -120.17 | 0.1849 | 0.13773 | 0.4121 | -120.356 | 0.060571 | 0.027831 | -0.001407 | 0.12114 | 0.26095 | 0.11306 | -0.22825 | -0.069424 | 0.033839 | 0.56734 | 0.1166 | 0.18602 | -0.013335 | 0.26104 | 120.0583 | -0.029926 | 120.3471 | 120.2852 | 0.22685 | 0.10989 | -0.038003 | 120.4715 | 120.4243 | 120.6987 | 120.1048 | -120.507 | 120.4077 | 120.5475 | 120.3996 | 120.3144 | -0.37931
1473.3281 | 120.4605 | -120.369 | 0.18768 | 1.4211e-13 | -0.022149 | 0.0011388 | 0.067554 | -0.012066 | 0.059112 | -0.0073253 | -0.0027303 | 0.0053414 | 0.018677 | 0.031722 | 0.0074415 | -119.7558 | -0.17258 | -120.2157 | 0.1849 | 0.14231 | 0.41668 | -120.3789 | 0.06515 | 0.023253 | -0.005985 | 0.11656 | 0.26095 | 0.10848 | -0.2191 | -0.009921 | -0.002782 | 0.61311 | 0.15322 | 0.16314 | -0.045377 | 0.229 | 120.1499 | -0.071126 | 120.4341 | 120.363 | 0.21311 | 0.073268 | -0.079203 | 120.5539 | 120.5113 | 120.7856 | 120.1964 | -120.5666 | 120.4855 | 120.6299 | 120.4774 | 120.3922 | -0.40678
1475.0781 | 120.5292 | -120.3827 | 0.18768 | 1.4211e-13 | -0.021936 | 0.00092524 | 0.067554 | -0.012066 | 0.059112 | 0.00030522 | -0.0025167 | 0.0051278 | 0.018891 | 0.031936 | 0.0072279 | -119.7925 | -0.17716 | -120.2386 | 0.19864 | 0.14688 | 0.41668 | -120.4201 | 0.060571 | 0.023253 | 0.007751 | 0.11198 | 0.25637 | 0.17716 | -0.22367 | -0.037399 | 0.010953 | 0.59022 | 0.14405 | 0.18145 | -0.040798 | 0.229 | 120.159 | -0.075704 | 120.4433 | 120.3904 | 0.23142 | 0.068689 | -0.010524 | 120.5813 | 120.5296 | 120.7994 | 120.2055 | -120.6078 | 120.4947 | 120.6391 | 120.5598 | 120.4059 | -0.41136
1476.7656 | 120.5795 | -120.3232 | 0.16022 | 1.4211e-13 | -0.022363 | 0.0011388 | 0.067767 | -0.011425 | 0.059112 | 0.0079357 | -0.0029439 | 0.0051278 | 0.018891 | 0.031722 | 0.0074415 | -119.7787 | -0.18632 | -120.2295 | 0.20321 | 0.16062 | 0.435 | -120.4201 | 0.06515 | 0.023253 | -0.005985 | 0.11656 | 0.25637 | 0.12222 | -0.22825 | -0.096908 | 0.042997 | 0.54445 | 0.093703 | 0.19061 | 0.000404 | 0.27478 | 120.0949 | -0.04366 | 120.3883 | 120.3172 | 0.22227 | 0.096155 | -0.038001 | 120.5264 | 120.4838 | 120.7582 | 120.1369 | -120.5803 | 120.4397 | 120.5796 | 120.4454 | 120.3464 | -0.38847
1478.5 | 120.639 | -120.3461 | 0.13733 | 1.4211e-13 | -0.022149 | 0.00092524 | 0.06734 | -0.011852 | 0.058685 | 0.00030522 | -0.0027303 | 0.005555 | 0.019104 | 0.031936 | 0.0076551 | -119.8199 | -0.18632 | -120.2661 | 0.18948 | 0.14231 | 0.41668 | -120.443 | 0.055992 | 0.018674 | -0.001407 | 0.11656 | 0.25637 | 0.17716 | -0.2191 | -0.096914 | 0.05215 | 0.52613 | 0.079965 | 0.17688 | 0.004977 | 0.27935 | 120.127 | -0.020772 | 120.4021 | 120.3447 | 0.21769 | 0.11904 | 0.03983 | 120.5355 | 120.4884 | 120.7628 | 120.1598 | -120.5803 | 120.4626 | 120.6024 | 120.5232 | 120.3647 | -0.35642
1480.25 | 120.5612 | -120.4193 | 0.16937 | 1.4211e-13 | -0.022149 | 0.00092524 | 0.067554 | -0.011425 | 0.059112 | 0.0079357 | -0.0029439 | 0.005555 | 0.019104 | 0.032149 | 0.0076551 | -119.8245 | -0.17716 | -120.2753 | 0.1849 | 0.14231 | 0.4121 | -120.4613 | 0.060571 | 0.014095 | -0.005985 | 0.11656 | 0.25637 | 0.168 | -0.2191 | -0.041987 | 0.015528 | 0.59479 | 0.14405 | 0.18604 | -0.027067 | 0.24273 | 120.2002 | -0.052816 | 120.4799 | 120.4133 | 0.21311 | 0.086999 | -0.001371 | 120.6042 | 120.5616 | 120.8314 | 120.2422 | -120.6307 | 120.5359 | 120.6757 | 120.5873 | 120.4334 | -0.38847
1481.9375 | 120.5887 | -120.3964 | 0.18768 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.067126 | -0.011852 | 0.059112 | 0.015566 | -0.0029439 | 0.0049142 | 0.018891 | 0.031936 | 0.0072279 | -119.8383 | -0.17258 | -120.2936 | 0.18948 | 0.14688 | 0.4121 | -120.4705 | 0.051413 | 0.018674 | -0.010564 | 0.11656 | 0.25637 | 0.17258 | -0.22367 | -0.074034 | 0.001796 | 0.55817 | 0.10285 | 0.17688 | -0.040798 | 0.22442 | 120.1727 | -0.071126 | 120.4478 | 120.3859 | 0.21311 | 0.068689 | -0.015103 | 120.5859 | 120.5433 | 120.8085 | 120.2238 | -120.6581 | 120.513 | 120.6528 | 120.569 | 120.4151 | -0.41136
1483.6094 | 120.5246 | -119.8059 | 0.6134 | 1.4211e-13 | -0.022149 | 0.0011388 | 0.06734 | -0.011638 | 0.058898 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018891 | 0.031508 | 0.0078689 | -119.124 | -0.18632 | -119.5748 | 0.74804 | 0.74672 | 0.98443 | -119.779 | 0.06515 | 0.009516 | -0.010564 | 0.11656 | 0.25179 | 0.17258 | -0.22367 | 0.026869 | 0.13464 | 0.68188 | 0.23112 | 0.20426 | 0.13332 | 0.37103 | 119.5822 | -0.49685 | 119.8711 | 119.7953 | 0.21311 | -0.36161 | -0.44082 | 120.554 | 120.5526 | 120.7903 | 119.6196 | -120.3924 | 119.9225 | 120.0577 | 119.9785 | 119.8154 | -0.83708
1485.3594 | 120.6665 | -120.076 | 0.46692 | 1.4211e-13 | -0.022149 | 0.00071164 | 0.067126 | -0.011638 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018677 | 0.031508 | 0.0074415 | -119.4582 | -0.17716 | -119.9273 | 0.45503 | 0.47657 | 0.68682 | -120.127 | 0.055992 | 0.023253 | -0.001407 | 0.12571 | 0.25179 | 0.17716 | -0.21452 | -0.051049 | -0.011893 | 0.61774 | 0.14868 | 0.19973 | 0.009648 | 0.2199 | 119.8615 | -0.3412 | 120.132 | 120.0746 | 0.21311 | -0.21512 | -0.28976 | 120.531 | 120.5526 | 120.7628 | 119.8988 | -120.594 | 120.2017 | 120.3278 | 120.2531 | 120.0992 | -0.68144
1487.1094 | 120.5612 | -120.2271 | 0.31586 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.067126 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018891 | 0.032149 | 0.0074415 | -119.6826 | -0.17716 | -120.1516 | 0.2902 | 0.29799 | 0.53115 | -120.3468 | 0.060571 | 0.014095 | -0.005985 | 0.11656 | 0.26095 | 0.17258 | -0.2191 | -0.11977 | -0.025653 | 0.54446 | 0.075404 | 0.19518 | -0.017868 | 0.21529 | 120.008 | -0.1993 | 120.2876 | 120.2211 | 0.21311 | -0.054906 | -0.14328 | 120.5173 | 120.525 | 120.7582 | 120.0499 | -120.6627 | 120.3436 | 120.488 | 120.3996 | 120.2411 | -0.53495
1488.7969 | 120.5795 | -120.0439 | 0.44403 | 1.4211e-13 | -0.022149 | 0.00071164 | 0.06734 | -0.011852 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.019318 | 0.031936 | 0.0076551 | -119.472 | -0.18174 | -119.941 | 0.45503 | 0.45825 | 0.6914 | -120.1225 | 0.055992 | 0.014095 | -0.005985 | 0.12114 | 0.25179 | 0.17716 | -0.22825 | -0.078514 | 0.010995 | 0.57196 | 0.1029 | 0.18141 | 0.01422 | 0.24737 | 119.8157 | -0.3229 | 120.0999 | 120.038 | 0.22227 | -0.19224 | -0.26687 | 120.499 | 120.5022 | 120.7353 | 119.8622 | -120.5665 | 120.1651 | 120.2957 | 120.2211 | 120.058 | -0.67228
1490.5469 | 120.3278 | -120.0623 | 0.17395 | 1.4211e-13 | -0.022577 | 0.00092524 | 0.067767 | -0.011638 | 0.059112 | 0.00030522 | -0.0025167 | 0.0053414 | 0.019104 | 0.031936 | 0.0074415 | -119.5132 | -0.19547 | -119.9823 | 0.22153 | 0.24762 | 0.47163 | -120.2324 | 0.060571 | 0.023253 | -0.001407 | 0.11656 | 0.25637 | 0.17258 | -0.22367 | -0.1701 | 0.047578 | 0.54907 | 0.080005 | 0.2501 | 0.073671 | 0.29768 | 119.8386 | -0.057393 | 120.1228 | 120.0608 | 0.22227 | 0.082422 | -0.00137 | 120.2838 | 120.3099 | 120.5339 | 119.8668 | -120.4063 | 120.1788 | 120.3186 | 120.2348 | 120.0855 | -0.39762
1492.2344 | 120.52 | -120.1996 | 0.15564 | 1.4211e-13 | -0.022363 | 0.00071164 | 0.067126 | -0.011425 | 0.059326 | -0.0073253 | -0.0027303 | 0.0053414 | 0.018891 | 0.031722 | 0.0078689 | -119.6689 | -0.18632 | -120.1242 | 0.18948 | 0.24304 | 0.46705 | -120.3056 | 0.060571 | 0.018674 | -0.001407 | 0.11198 | 0.25637 | 0.17716 | -0.21452 | -0.10603 | 0.033839 | 0.53073 | 0.075407 | 0.18144 | 0.087402 | 0.31141 | 119.9851 | -0.043661 | 120.2602 | 120.1982 | 0.21311 | 0.10073 | 0.021519 | 120.3891 | 120.4426 | 120.6666 | 120.0133 | -120.4613 | 120.3116 | 120.456 | 120.3767 | 120.2183 | -0.37016
1493.9844 | 120.5841 | -120.2362 | 0.15106 | 1.4211e-13 | -0.021936 | 0.00092524 | 0.06734 | -0.011638 | 0.059112 | 0.015566 | -0.0027303 | 0.0049142 | 0.019104 | 0.031936 | 0.0078689 | -119.7055 | -0.18174 | -120.17 | 0.19406 | 0.15604 | 0.4762 | -120.356 | 0.060571 | 0.018674 | -0.010564 | 0.11198 | 0.24721 | 0.15427 | -0.22825 | -0.11978 | 0.042996 | 0.53072 | 0.066246 | 0.18602 | 0.00498 | 0.32514 | 120.008 | -0.039083 | 120.2968 | 120.2256 | 0.21769 | 0.096153 | 0.003204 | 120.4303 | 120.3922 | 120.7124 | 120.0545 | -120.507 | 120.3482 | 120.4834 | 120.3905 | 120.2549 | -0.37931
1495.6719 | 120.4697 | -120.3598 | 0.18768 | 1.4211e-13 | -0.022149 | 0.00092524 | 0.06734 | -0.011638 | 0.058898 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018677 | 0.031936 | 0.0074415 | -119.7146 | -0.17716 | -120.1745 | 0.22153 | 0.21557 | 0.50368 | -120.3651 | 0.055992 | 0.014095 | -0.005985 | 0.11198 | 0.26095 | 0.168 | -0.21452 | -0.00534 | 0.033845 | 0.64516 | 0.18526 | 0.1906 | 0.027885 | 0.31599 | 120.1453 | -0.075704 | 120.4158 | 120.3538 | 0.20853 | 0.073268 | -0.019681 | 120.5813 | 120.5754 | 120.8635 | 120.1826 | -120.5528 | 120.4718 | 120.6208 | 120.5278 | 120.3739 | -0.4022
1497.4062 | 120.5429 | -119.902 | 0.53101 | 1.4211e-13 | -0.022363 | 0.0011388 | 0.067554 | -0.011852 | 0.059112 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018891 | 0.032149 | 0.0072279 | -119.4766 | -0.1909 | -119.941 | 0.4184 | 0.41246 | 0.70513 | -120.1728 | 0.055992 | 0.018674 | -0.001407 | 0.11198 | 0.25637 | 0.15884 | -0.22825 | -0.27079 | -0.11261 | 0.42548 | -0.039007 | 0.23178 | -0.11854 | 0.17413 | 119.6738 | -0.41903 | 119.958 | 119.9006 | 0.22685 | -0.27463 | -0.37216 | 120.3204 | 120.3145 | 120.6072 | 119.7111 | -120.7038 | 120.014 | 120.1584 | 120.0609 | 119.9207 | -0.75926
1499.1562 | 120.5841 | -119.9799 | 0.45776 | 1.4211e-13 | -0.022577 | 0.00092524 | 0.06734 | -0.012066 | 0.059112 | 0.00030522 | -0.0027303 | 0.0053414 | 0.019318 | 0.031508 | 0.0074415 | -119.385 | -0.1909 | -119.8495 | 0.50081 | 0.47199 | 0.78755 | -120.0767 | 0.060571 | 0.023253 | -0.010564 | 0.1074 | 0.25179 | 0.17258 | -0.22367 | -0.096812 | 0.043046 | 0.59486 | 0.13038 | 0.22719 | 0.014224 | 0.32979 | 119.7562 | -0.35036 | 120.0404 | 119.9693 | 0.21311 | -0.20597 | -0.28518 | 120.4807 | 120.4518 | 120.7674 | 119.789 | -120.5344 | 120.0873 | 120.2317 | 120.1524 | 120.0031 | -0.68144
1500.9062 | 120.5612 | -120.401 | 0.20142 | 1.4211e-13 | -0.022577 | 0.00092524 | 0.06734 | -0.011852 | 0.058898 | 0.0079357 | -0.0025167 | 0.0053414 | 0.018677 | 0.032149 | 0.0074415 | -119.8245 | -0.18174 | -120.2936 | 0.1849 | 0.14688 | 0.41668 | -120.4567 | 0.060571 | 0.023253 | -0.010564 | 0.12114 | 0.25637 | 0.16342 | -0.2191 | -0.055719 | -0.016515 | 0.57648 | 0.10743 | 0.16315 | -0.054531 | 0.21527 | 120.1819 | -0.08028 | 120.4616 | 120.3904 | 0.20853 | 0.054956 | -0.037993 | 120.5859 | 120.5479 | 120.8177 | 120.2193 | -120.6581 | 120.5221 | 120.6574 | 120.5644 | 120.4243 | -0.42051
1502.6406 | 120.6665 | -120.4147 | 0.17853 | 1.4211e-13 | -0.022149 | 0.00092524 | 0.06734 | -0.011852 | 0.059539 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018891 | 0.031722 | 0.0074415 | -119.8383 | -0.1909 | -120.3073 | 0.18948 | 0.16062 | 0.41668 | -120.4796 | 0.060571 | 0.014095 | 0.003172 | 0.11198 | 0.25637 | 0.16342 | -0.2191 | -0.064881 | 0.010951 | 0.57648 | 0.10742 | 0.17231 | -0.017907 | 0.23815 | 120.1956 | -0.066549 | 120.4753 | 120.4179 | 0.22227 | 0.077844 | -0.015105 | 120.6042 | 120.5754 | 120.8314 | 120.2238 | -120.6581 | 120.5267 | 120.6711 | 120.5782 | 120.4288 | -0.39762
1504.3281 | 120.5887 | -120.4193 | 0.18768 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.06734 | -0.011852 | 0.059112 | 0.0079357 | -0.0029439 | 0.0047004 | 0.018891 | 0.031936 | 0.0074415 | -119.852 | -0.18632 | -120.3256 | 0.1849 | 0.14688 | 0.4121 | -120.5025 | 0.06515 | 0.018674 | -0.005985 | 0.11198 | 0.26095 | 0.16342 | -0.22367 | -0.083197 | -0.002782 | 0.56732 | 0.09369 | 0.17689 | -0.040798 | 0.22442 | 120.1956 | -0.075704 | 120.4845 | 120.4133 | 0.21769 | 0.073268 | -0.02426 | 120.6042 | 120.5662 | 120.8314 | 120.233 | -120.6902 | 120.5313 | 120.6803 | 120.5827 | 120.438 | -0.41136
1506.0781 | 120.5978 | -120.4102 | 0.24261 | 1.4211e-13 | -0.022363 | 0.00071164 | 0.067126 | -0.011425 | 0.059326 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018463 | 0.031936 | 0.0078689 | -119.8337 | -0.18632 | -120.3027 | 0.21695 | 0.17436 | 0.43957 | -120.475 | 0.06515 | 0.018674 | -0.005985 | 0.1074 | 0.24721 | 0.17716 | -0.2191 | -0.06488 | -0.025665 | 0.57648 | 0.10743 | 0.17231 | -0.068257 | 0.19696 | 120.1911 | -0.13521 | 120.4753 | 120.4042 | 0.21311 | 0.0046 | -0.065456 | 120.6271 | 120.5845 | 120.8497 | 120.2238 | -120.7177 | 120.5176 | 120.6574 | 120.5873 | 120.4288 | -0.46171
1507.8281 | 120.7123 | -120.3918 | 0.1831 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.06734 | -0.012279 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.031936 | 0.0076551 | -119.797 | -0.1909 | -120.2569 | 0.23984 | 0.22473 | 0.4762 | -120.4613 | 0.069728 | 0.018674 | -0.001407 | 0.11656 | 0.26095 | 0.17716 | -0.21452 | -0.069453 | 0.056737 | 0.5948 | 0.1349 | 0.20435 | 0.041621 | 0.2931 | 120.1773 | -0.066548 | 120.4616 | 120.3904 | 0.21311 | 0.077846 | -0.005946 | 120.6317 | 120.6166 | 120.868 | 120.201 | -120.6444 | 120.5084 | 120.6528 | 120.569 | 120.4105 | -0.39762
1509.5781 | 120.6757 | -120.1126 | 0.42114 | 1.4211e-13 | -0.022149 | 0.00092524 | 0.067554 | -0.011638 | 0.059112 | 0.0079357 | -0.0029439 | 0.0053414 | 0.018891 | 0.031722 | 0.0074415 | -119.559 | -0.1909 | -120.0189 | 0.43671 | 0.43536 | 0.68224 | -120.214 | 0.060571 | 0.018674 | -0.001407 | 0.12114 | 0.25637 | 0.15427 | -0.22367 | -0.10143 | 0.015569 | 0.55364 | 0.093733 | 0.19516 | 0.014214 | 0.2611 | 119.8889 | -0.30001 | 120.1732 | 120.1112 | 0.22227 | -0.16477 | -0.26688 | 120.5493 | 120.548 | 120.7949 | 119.9217 | -120.6352 | 120.2337 | 120.369 | 120.2669 | 120.1313 | -0.64482
1511.3125 | 120.5566 | -119.6503 | 0.81482 | 1.4211e-13 | -0.022363 | 0.00071164 | 0.06734 | -0.011638 | 0.059112 | 0.00030522 | -0.0023031 | 0.0051278 | 0.018463 | 0.031722 | 0.0072279 | -119.2156 | -0.18632 | -119.6847 | 0.71142 | 0.71925 | 0.95238 | -119.9027 | 0.055992 | 0.014095 | -0.010564 | 0.11656 | 0.25179 | 0.168 | -0.2191 | -0.2524 | -0.1034 | 0.43467 | -0.034394 | 0.21801 | -0.095569 | 0.13756 | 119.4312 | -0.69826 | 119.7063 | 119.6397 | 0.20853 | -0.56302 | -0.64682 | 120.3617 | 120.3695 | 120.6026 | 119.464 | -120.7175 | 119.7668 | 119.9021 | 119.8183 | 119.6644 | -1.0339
1513 | 120.6162 | -119.8013 | 0.60425 | 1.4211e-13 | -0.022363 | 0.00028424 | 0.067126 | -0.011425 | 0.058685 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018677 | 0.032149 | 0.0076551 | -119.2385 | -0.19547 | -119.7121 | 0.67479 | 0.67804 | 0.92033 | -119.9027 | 0.060571 | 0.018674 | -0.010564 | 0.11656 | 0.25637 | 0.15884 | -0.21452 | -0.10134 | 0.07054 | 0.56285 | 0.089199 | 0.19054 | 0.073792 | 0.31608 | 119.5868 | -0.48769 | 119.8619 | 119.7908 | 0.20395 | -0.34788 | -0.4454 | 120.4761 | 120.4794 | 120.7217 | 119.6059 | -120.5069 | 119.9179 | 120.0577 | 119.9602 | 119.82 | -0.81876
1514.7344 | 120.5978 | -120.3918 | 0.24261 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.067126 | -0.011852 | 0.059112 | 0.015566 | -0.0025167 | 0.005555 | 0.018677 | 0.032149 | 0.0078689 | -119.852 | -0.19547 | -120.3119 | 0.21237 | 0.1652 | 0.43957 | -120.5254 | 0.060571 | 0.018674 | -0.005985 | 0.11198 | 0.26095 | 0.17258 | -0.22825 | -0.13356 | -0.030244 | 0.53986 | 0.079959 | 0.21352 | -0.077415 | 0.19696 | 120.1636 | -0.13064 | 120.4524 | 120.3859 | 0.22227 | 0.018336 | -0.070035 | 120.6042 | 120.557 | 120.8314 | 120.1964 | -120.768 | 120.5038 | 120.6528 | 120.5644 | 120.4105 | -0.47087
1516.4844 | 120.6482 | -120.3461 | 0.24719 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.067126 | -0.011852 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018891 | 0.031722 | 0.0078689 | -119.8154 | -0.19547 | -120.2844 | 0.249 | 0.20183 | 0.48078 | -120.4888 | 0.060571 | 0.018674 | -0.010564 | 0.12114 | 0.25179 | 0.168 | -0.2191 | -0.1427 | 0.001806 | 0.53071 | 0.061652 | 0.20436 | -0.04536 | 0.23359 | 120.127 | -0.12606 | 120.4066 | 120.3355 | 0.20853 | 0.004602 | -0.07919 | 120.5951 | 120.5479 | 120.8269 | 120.1506 | -120.736 | 120.4672 | 120.5979 | 120.5141 | 120.3647 | -0.46629
1518.1719 | 120.52 | -120.0211 | 0.55389 | 1.4211e-13 | -0.022363 | 0.00092524 | 0.06734 | -0.011638 | 0.059112 | 0.0079357 | -0.0029439 | 0.0051278 | 0.018891 | 0.031936 | 0.0074415 | -119.3484 | -0.1909 | -119.8037 | 0.5878 | 0.6002 | 0.83334 | -120.0034 | 0.055992 | 0.014095 | -0.005985 | 0.11198 | 0.25637 | 0.168 | -0.21452 | 0.01765 | 0.033905 | 0.67269 | 0.21736 | 0.19971 | 0.046304 | 0.27944 | 119.8065 | -0.44192 | 120.077 | 120.0151 | 0.20853 | -0.29752 | -0.38589 | 120.6089 | 120.6213 | 120.8544 | 119.8302 | -120.5573 | 120.133 | 120.2774 | 120.1891 | 120.0352 | -0.76841
1519.9062 | 120.6482 | -120.4651 | 0.1831 | 1.4211e-13 | -0.022577 | 0.0011388 | 0.06734 | -0.011852 | 0.059539 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018677 | 0.031508 | 0.0074415 | -119.8932 | -0.1909 | -120.3622 | 0.17574 | 0.12857 | 0.41668 | -120.5483 | 0.060571 | 0.014095 | -0.005985 | 0.11656 | 0.24721 | 0.168 | -0.22367 | -0.083211 | -0.007361 | 0.57189 | 0.10284 | 0.18605 | -0.054536 | 0.23358 | 120.2414 | -0.066548 | 120.5257 | 120.4591 | 0.21769 | 0.06411 | -0.015103 | 120.6408 | 120.5937 | 120.8818 | 120.2742 | -120.7314 | 120.5816 | 120.7123 | 120.6331 | 120.4792 | -0.40678
1521.6406 | 119.9615 | -119.6045 | 0.21057 | 1.4211e-13 | -0.022577 | 0.00092524 | 0.066485 | -0.011852 | 0.058685 | 0.00030522 | -0.0025167 | 0.0049142 | 0.018891 | 0.032149 | 0.0076551 | -116.116 | -0.37404 | -116.3837 | 2.8816 | 2.7614 | 3.1593 | -116.7203 | 0.055992 | 0.018674 | -0.001407 | 0.11198 | 0.25179 | 0.14511 | -0.22367 | 2.8842 | 2.671 | 3.4885 | 3.2208 | 0.3366 | 2.5509 | 2.9487 | 119.3808 | -0.098592 | 119.6605 | 119.6031 | 0.22227 | 0.041223 | -0.065462 | 122.4861 | 122.3659 | 122.7638 | 119.2305 | -116.9309 | 119.7165 | 119.8563 | 119.7496 | 119.6232 | -0.43424
1523.3125 | 120.488 | -120.1859 | 0.15106 | 1.4211e-13 | -0.022363 | 0.00071164 | 0.067126 | -0.011852 | 0.059112 | 0.0079357 | -0.0025167 | 0.005555 | 0.018463 | 0.031722 | 0.0072279 | -119.6963 | -0.21379 | -120.1288 | 0.18032 | 0.24304 | 0.46247 | -120.3697 | 0.06515 | 0.014095 | -0.015143 | 0.11198 | 0.25179 | 0.14511 | -0.21452 | -0.18387 | 0.029261 | 0.48953 | 0.057096 | 0.24097 | 0.09198 | 0.31141 | 119.9713 | -0.039083 | 120.251 | 120.1707 | 0.19937 | 0.10073 | -0.005953 | 120.3662 | 120.4289 | 120.6483 | 119.9721 | -120.5208 | 120.2978 | 120.4376 | 120.331 | 120.1999 | -0.36558
1525.0469 | 120.401 | -119.9478 | 0.43488 | 1.4211e-13 | -0.02279 | 0.0011388 | 0.067126 | -0.011638 | 0.059326 | 0.00030522 | -0.0025167 | 0.005555 | 0.018677 | 0.031936 | 0.0076551 | -119.3987 | -0.21379 | -119.8357 | 0.43213 | 0.40788 | 0.71887 | -120.0126 | 0.060571 | 0.014095 | -0.001407 | 0.1074 | 0.25637 | 0.168 | -0.21452 | -0.06475 | -0.002741 | 0.54909 | 0.11207 | 0.17682 | -0.026992 | 0.28399 | 119.7333 | -0.32747 | 120.0084 | 119.9464 | 0.21311 | -0.1785 | -0.26687 | 120.3799 | 120.3557 | 120.6667 | 119.734 | -120.4474 | 120.0552 | 120.2042 | 120.1158 | 119.9619 | -0.64939
1526.7969 | 120.5063 | -120.3186 | 0.17853 | 1.4211e-13 | -0.022577 | 0.00071164 | 0.067554 | -0.011852 | 0.059112 | 0.0079357 | -0.0025167 | 0.0053414 | 0.018891 | 0.031936 | 0.0074415 | -119.7925 | -0.20005 | -120.2203 | 0.1849 | 0.13773 | 0.46705 | -120.3972 | 0.060571 | 0.014095 | -0.001407 | 0.11656 | 0.25179 | 0.168 | -0.22367 | -0.07859 | 0.006373 | 0.52613 | 0.098282 | 0.17687 | -0.040801 | 0.28852 | 120.0949 | -0.061971 | 120.3792 | 120.3172 | 0.22227 | 0.073266 | -0.010526 | 120.5035 | 120.4563 | 120.7857 | 120.1186 | -120.5757 | 120.4352 | 120.5704 | 120.4866 | 120.3327 | -0.4022
1528.5469 | 120.5658 | -120.1904 | 0.14191 | 1.4211e-13 | -0.022577 | 0.00092524 | 0.06734 | -0.011638 | 0.059112 | 0.00030522 | -0.0029439 | 0.0053414 | 0.018891 | 0.031936 | 0.0074415 | -119.7192 | -0.20005 | -120.1471 | 0.20779 | 0.22473 | 0.44415 | -120.4064 | 0.051413 | 0.014095 | -0.005985 | 0.1074 | 0.25179 | 0.16342 | -0.2191 | -0.21592 | 0.065886 | 0.47121 | 0.043361 | 0.25928 | 0.082819 | 0.30225 | 119.9713 | -0.034506 | 120.2418 | 120.1844 | 0.21311 | 0.10989 | 0.021516 | 120.3982 | 120.4152 | 120.6346 | 119.9904 | -120.5483 | 120.2978 | 120.4422 | 120.3539 | 120.2045 | -0.361
1530.2344 | 120.5246 | -120.3827 | 0.14191 | 1.4211e-13 | -0.02279 | 0.00071164 | 0.067126 | -0.011852 | 0.059539 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018677 | 0.032149 | 0.0074415 | -119.8337 | -0.19547 | -120.2615 | 0.16201 | 0.22015 | 0.43957 | -120.4338 | 0.055992 | 0.009516 | -0.010564 | 0.11656 | 0.24721 | 0.13595 | -0.22367 | -0.051136 | 0.020102 | 0.54901 | 0.12116 | 0.1723 | 0.07824 | 0.29767 | 120.159 | -0.02535 | 120.4387 | 120.3721 | 0.21311 | 0.10531 | -0.005955 | 120.5447 | 120.6028 | 120.8223 | 120.1872 | -120.5757 | 120.4992 | 120.6299 | 120.5186 | 120.3922 | -0.36558
1531.9844 | 120.6482 | -120.3964 | 0.13733 | 1.4211e-13 | -0.02279 | 0.00092524 | 0.067126 | -0.011852 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018677 | 0.031508 | 0.0074415 | -119.8703 | -0.1909 | -120.3027 | 0.16201 | 0.12857 | 0.43957 | -120.475 | 0.055992 | 0.018674 | -0.010564 | 0.1074 | 0.25179 | 0.16342 | -0.22367 | -0.078613 | 0.02468 | 0.52612 | 0.093692 | 0.17231 | -0.00876 | 0.30225 | 120.1727 | -0.029928 | 120.4524 | 120.3859 | 0.21311 | 0.11447 | 0.026094 | 120.5584 | 120.525 | 120.836 | 120.2055 | -120.6124 | 120.5038 | 120.6482 | 120.5598 | 120.4151 | -0.361
1533.7344 | 120.575 | -120.4742 | 0.15564 | 1.4211e-13 | -0.02279 | 0.0013526 | 0.06734 | -0.011638 | 0.059539 | -0.0073253 | -0.0027303 | 0.0053414 | 0.018677 | 0.032149 | 0.0074415 | -119.8932 | -0.19547 | -120.3256 | 0.16659 | 0.11941 | 0.435 | -120.5071 | 0.055992 | 0.014095 | -0.001407 | 0.1074 | 0.25179 | 0.15427 | -0.2191 | -0.032845 | 0.010947 | 0.58105 | 0.14862 | 0.18147 | -0.036229 | 0.27936 | 120.2551 | -0.048239 | 120.5302 | 120.4728 | 0.21769 | 0.096154 | -0.001374 | 120.6408 | 120.5937 | 120.9092 | 120.2788 | -120.6627 | 120.5816 | 120.726 | 120.6285 | 120.4883 | -0.37474
1535.4688 | 120.726 | -120.4056 | 0.1236 | 1.4211e-13 | -0.023004 | 0.00071164 | 0.067126 | -0.011638 | 0.059112 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.032149 | 0.0072279 | -119.9298 | -0.19547 | -120.3485 | 0.15743 | 0.12399 | 0.435 | -120.53 | 0.060571 | 0.004938 | -0.001407 | 0.1074 | 0.25179 | 0.16342 | -0.22367 | -0.1244 | 0.033835 | 0.47576 | 0.057066 | 0.18147 | 0.000394 | 0.3114 | 120.1819 | -0.016195 | 120.4661 | 120.4042 | 0.22227 | 0.1282 | 0.039827 | 120.563 | 120.5296 | 120.8406 | 120.2101 | -120.6536 | 120.513 | 120.6574 | 120.569 | 120.4105 | -0.34727
1537.1562 | 120.6207 | -120.4834 | 0.17853 | 1.4211e-13 | -0.022577 | 0.00071164 | 0.067126 | -0.011638 | 0.059539 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018463 | 0.031936 | 0.0078689 | -119.9481 | -0.19547 | -120.3851 | 0.15285 | 0.11941 | 0.38921 | -120.5529 | 0.055992 | 0.023253 | -0.001407 | 0.1074 | 0.26095 | 0.15427 | -0.2191 | -0.06948 | -0.025676 | 0.53526 | 0.098258 | 0.16774 | -0.059117 | 0.21068 | 120.2643 | -0.071127 | 120.5394 | 120.482 | 0.21769 | 0.082423 | -0.024262 | 120.6362 | 120.6028 | 120.8726 | 120.2879 | -120.7314 | 120.5908 | 120.7443 | 120.6377 | 120.5067 | -0.39762
1538.8906 | 120.6573 | -120.3964 | 0.25635 | 1.4211e-13 | -0.023218 | 0.00049784 | 0.06734 | -0.012066 | 0.059326 | 0.00030522 | -0.0025167 | 0.0049142 | 0.018677 | 0.032149 | 0.0072279 | -119.8154 | -0.20463 | -120.2386 | 0.27189 | 0.25678 | 0.50368 | -120.4796 | 0.060571 | 0.018674 | -0.005985 | 0.11198 | 0.25179 | 0.17258 | -0.2191 | -0.083192 | 0.015542 | 0.58106 | 0.15779 | 0.24098 | 0.000431 | 0.24733 | 120.1773 | -0.14437 | 120.457 | 120.3904 | 0.21311 | -0.004554 | -0.083768 | 120.6683 | 120.6532 | 120.9001 | 120.1918 | -120.736 | 120.5084 | 120.6482 | 120.569 | 120.4151 | -0.47544
1540.6406 | 120.6207 | -120.0668 | 0.48065 | 1.4211e-13 | -0.023004 | 0.00071164 | 0.067126 | -0.012279 | 0.059326 | 0.015566 | -0.0027303 | 0.0051278 | 0.018463 | 0.032149 | 0.0072279 | -119.4445 | -0.20463 | -119.8769 | 0.55575 | 0.55441 | 0.78755 | -120.0721 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.25179 | 0.14053 | -0.2191 | -0.005258 | 0.075098 | 0.62232 | 0.18988 | 0.19514 | 0.073757 | 0.3069 | 119.8477 | -0.37325 | 120.1274 | 120.0608 | 0.21311 | -0.22886 | -0.34012 | 120.6226 | 120.6212 | 120.8544 | 119.8622 | -120.5527 | 120.1742 | 120.3186 | 120.2074 | 120.0901 | -0.69975
1542.3281 | 120.607 | -120.52 | 0.17395 | 1.4211e-13 | -0.022363 | 0.00071164 | 0.06734 | -0.011638 | 0.059112 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.032149 | 0.0074415 | -119.9619 | -0.19547 | -120.3989 | 0.16659 | 0.12857 | 0.38463 | -120.6032 | 0.055992 | 0.018674 | -0.010564 | 0.11198 | 0.26095 | 0.17258 | -0.22367 | -0.083226 | -0.007363 | 0.55815 | 0.12115 | 0.20437 | -0.045381 | 0.21068 | 120.2963 | -0.061971 | 120.576 | 120.5095 | 0.21311 | 0.087001 | -0.00137 | 120.6866 | 120.6486 | 120.9047 | 120.3245 | -120.7772 | 120.632 | 120.781 | 120.6926 | 120.5387 | -0.39762
1544.0781 | 120.7535 | -120.5109 | 0.10986 | 1.4211e-13 | -0.02279 | 0.0011388 | 0.067554 | -0.011425 | 0.059326 | 0.0079357 | -0.0027303 | 0.005555 | 0.018463 | 0.032149 | 0.0076551 | -119.9573 | -0.20463 | -120.4218 | 0.15743 | 0.12399 | 0.38921 | -120.5987 | 0.060571 | 0.014095 | -0.010564 | 0.1074 | 0.25179 | 0.14969 | -0.22367 | -0.087803 | 0.047568 | 0.55357 | 0.089098 | 0.1769 | 0.014127 | 0.27935 | 120.2872 | -0.002462 | 120.5714 | 120.5003 | 0.21311 | 0.14193 | 0.039824 | 120.6683 | 120.6349 | 120.9001 | 120.3062 | -120.7085 | 120.6183 | 120.7627 | 120.6606 | 120.525 | -0.33354
1545.8281 | 120.6757 | -120.5841 | 0.16022 | 1.4211e-13 | -0.02279 | 0.0011388 | 0.06734 | -0.011852 | 0.059326 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018677 | 0.032149 | 0.0074415 | -119.971 | -0.20005 | -120.4492 | 0.15743 | 0.12399 | 0.38921 | -120.6261 | 0.051413 | 0.018674 | -0.005985 | 0.1074 | 0.24721 | 0.17716 | -0.22367 | -0.042034 | -0.002786 | 0.61308 | 0.13487 | 0.1769 | -0.036227 | 0.22899 | 120.3604 | -0.052816 | 120.6355 | 120.5781 | 0.21769 | 0.086998 | 0.016942 | 120.7415 | 120.7081 | 120.9733 | 120.3841 | -120.7864 | 120.6915 | 120.8313 | 120.7613 | 120.6028 | -0.38389
1547.5781 | 120.4834 | -119.7144 | 0.83771 | 1.4211e-13 | -0.023004 | 0.0011388 | 0.067126 | -0.012066 | 0.059112 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018463 | 0.032149 | 0.0074415 | -119.0737 | -0.19547 | -119.5336 | 0.8625 | 0.86578 | 1.1035 | -119.747 | 0.055992 | 0.018674 | -0.001407 | 0.11656 | 0.25179 | 0.16342 | -0.21452 | -0.032632 | 0.024794 | 0.64069 | 0.18078 | 0.21341 | 0.028068 | 0.26576 | 119.4998 | -0.72115 | 119.7703 | 119.7129 | 0.21311 | -0.58591 | -0.67429 | 120.5769 | 120.5801 | 120.8178 | 119.5189 | -120.5847 | 119.8309 | 119.9661 | 119.8778 | 119.733 | -1.0522
1549.3281 | 120.726 | -120.2499 | 0.28839 | 1.4211e-13 | -0.023218 | 0.00092524 | 0.06734 | -0.012279 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018891 | 0.032363 | 0.0076551 | -119.504 | -0.20921 | -119.9731 | 0.47792 | 0.46741 | 0.71887 | -120.2003 | 0.055992 | 0.009516 | -0.001407 | 0.11198 | 0.25637 | 0.14969 | -0.2191 | 0.049639 | 0.18953 | 0.74591 | 0.27684 | 0.22721 | 0.17902 | 0.43048 | 120.0308 | -0.17641 | 120.3059 | 120.2485 | 0.21769 | -0.032019 | -0.1387 | 120.7279 | 120.7173 | 120.9688 | 120.0407 | -120.4887 | 120.3619 | 120.5063 | 120.3996 | 120.2595 | -0.50749
1551 | 120.7901 | -120.4926 | 0.13733 | 1.4211e-13 | -0.023004 | 0.00092524 | 0.067126 | -0.011852 | 0.059112 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018891 | 0.032363 | 0.0072279 | -119.9573 | -0.20005 | -120.4263 | 0.16201 | 0.12399 | 0.39379 | -120.617 | 0.060571 | 0.014095 | -0.001407 | 0.11198 | 0.24721 | 0.168 | -0.22367 | -0.12443 | 0.02468 | 0.53526 | 0.06621 | 0.19064 | -0.013339 | 0.25646 | 120.2689 | -0.02535 | 120.5531 | 120.4911 | 0.22227 | 0.10989 | 0.030673 | 120.6546 | 120.6165 | 120.8863 | 120.2925 | -120.7543 | 120.6045 | 120.7398 | 120.6606 | 120.5066 | -0.361
1552.75 | 120.6619 | -120.488 | 0.21973 | 1.4211e-13 | -0.022363 | 0.0011388 | 0.066913 | -0.012066 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018463 | 0.031722 | 0.0072279 | -119.8657 | -0.20921 | -120.3302 | 0.25816 | 0.21099 | 0.4762 | -120.5483 | 0.06515 | 0.018674 | -0.010564 | 0.11198 | 0.26095 | 0.12222 | -0.22825 | -0.060323 | 0.038428 | 0.62225 | 0.15778 | 0.2181 | -0.008737 | 0.25648 | 120.2597 | -0.10775 | 120.5531 | 120.4774 | 0.21769 | 0.041224 | -0.097511 | 120.7461 | 120.699 | 120.9642 | 120.2788 | -120.768 | 120.6 | 120.7489 | 120.6102 | 120.5067 | -0.44798
1554.5 | 120.694 | -120.5887 | 0.15564 | 1.4211e-13 | -0.02279 | 0.00071164 | 0.066913 | -0.011852 | 0.059326 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018677 | 0.032149 | 0.0072279 | -119.9985 | -0.20921 | -120.4675 | 0.15743 | 0.11483 | 0.38005 | -120.6536 | 0.06515 | 0.009516 | -0.005985 | 0.10282 | 0.24721 | 0.16342 | -0.2191 | -0.06493 | 0.001791 | 0.59019 | 0.12113 | 0.18606 | -0.040808 | 0.22441 | 120.3696 | -0.052818 | 120.6538 | 120.5827 | 0.21311 | 0.091575 | 0.007783 | 120.7461 | 120.7035 | 120.9687 | 120.3795 | -120.8093 | 120.6915 | 120.8359 | 120.7521 | 120.5982 | -0.37474
1556.1875 | 120.8084 | -120.5978 | 0.13275 | 1.4211e-13 | -0.023004 | 0.0011388 | 0.066913 | -0.011852 | 0.058898 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018891 | 0.031936 | 0.0074415 | -120.0031 | -0.20005 | -120.495 | 0.16659 | 0.11483 | 0.38463 | -120.6719 | 0.060571 | 0.018674 | -0.010564 | 0.1074 | 0.24721 | 0.14969 | -0.2191 | -0.074091 | 0.033836 | 0.59476 | 0.10282 | 0.17691 | -0.017919 | 0.25188 | 120.3787 | -0.02535 | 120.6584 | 120.5873 | 0.20853 | 0.11446 | 0.016936 | 120.7644 | 120.7127 | 120.9825 | 120.3978 | -120.8047 | 120.7052 | 120.8451 | 120.7475 | 120.6165 | -0.35185
1557.9219 | 120.7993 | -120.5841 | 0.14191 | 1.4211e-13 | -0.023004 | 0.0011388 | 0.067126 | -0.011852 | 0.059326 | 0.0079357 | -0.0029439 | 0.0057688 | 0.018677 | 0.032363 | 0.0076551 | -120.026 | -0.19547 | -120.495 | 0.16201 | 0.12857 | 0.38921 | -120.6811 | 0.055992 | 0.014095 | -0.001407 | 0.11198 | 0.25637 | 0.168 | -0.2191 | -0.096982 | 0.020102 | 0.55814 | 0.089088 | 0.18607 | -0.013338 | 0.2473 | 120.365 | -0.029928 | 120.6401 | 120.5827 | 0.21769 | 0.11446 | 0.026095 | 120.7461 | 120.7127 | 120.9733 | 120.3886 | -120.823 | 120.6961 | 120.8405 | 120.7521 | 120.5982 | -0.361
1559.6562 | 120.8176 | -120.575 | 0.14648 | 1.4211e-13 | -0.023218 | 0.00092524 | 0.067126 | -0.011638 | 0.059326 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018891 | 0.032149 | 0.0072279 | -120.0077 | -0.20921 | -120.4767 | 0.18032 | 0.13315 | 0.39837 | -120.6719 | 0.06515 | 0.009516 | -0.005985 | 0.11198 | 0.24721 | 0.16342 | -0.2191 | -0.096979 | 0.033839 | 0.5673 | 0.098246 | 0.19523 | -0.013336 | 0.25188 | 120.3559 | -0.034505 | 120.6401 | 120.569 | 0.21311 | 0.10073 | 0.016939 | 120.7553 | 120.7081 | 120.9733 | 120.3657 | -120.8184 | 120.6869 | 120.8222 | 120.7384 | 120.5845 | -0.36558
1561.3438 | 120.726 | -120.6436 | 0.17853 | 1.4211e-13 | -0.023004 | 0.0011388 | 0.066913 | -0.011638 | 0.059326 | 0.00030522 | -0.0023031 | 0.0049142 | 0.018677 | 0.032363 | 0.0076551 | -120.0351 | -0.20463 | -120.5179 | 0.16201 | 0.11941 | 0.38463 | -120.6948 | 0.060571 | 0.018674 | -0.010564 | 0.1074 | 0.25179 | 0.15427 | -0.22367 | -0.051208 | -0.016519 | 0.60849 | 0.12571 | 0.17691 | -0.059117 | 0.2061 | 120.4199 | -0.071127 | 120.7042 | 120.6331 | 0.21311 | 0.073266 | -0.024262 | 120.8056 | 120.763 | 121.0282 | 120.439 | -120.8734 | 120.751 | 120.8954 | 120.7979 | 120.6623 | -0.4022
1563.0938 | 120.7352 | -120.639 | 0.16479 | 1.4211e-13 | -0.023004 | 0.00092524 | 0.066699 | -0.012279 | 0.059326 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018891 | 0.032363 | 0.0074415 | -120.0534 | -0.20463 | -120.5271 | 0.15743 | 0.11025 | 0.38463 | -120.7131 | 0.055992 | 0.018674 | -0.001407 | 0.11198 | 0.25179 | 0.168 | -0.2191 | -0.074102 | -0.007364 | 0.5856 | 0.11197 | 0.18607 | -0.054542 | 0.21984 | 120.4199 | -0.052816 | 120.695 | 120.6376 | 0.21769 | 0.086999 | 0.003207 | 120.7965 | 120.7493 | 121.0237 | 120.4344 | -120.8779 | 120.751 | 120.8908 | 120.807 | 120.6577 | -0.38389
1564.8281 | 120.7809 | -120.6573 | 0.16022 | 1.4211e-13 | -0.023004 | 0.0011388 | 0.067126 | -0.011852 | 0.059112 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018463 | 0.032149 | 0.0080825 | -120.0672 | -0.20463 | -120.5408 | 0.15743 | 0.11483 | 0.38463 | -120.7269 | 0.055992 | 0.009516 | -0.005985 | 0.1074 | 0.24264 | 0.15427 | -0.22367 | -0.069528 | -0.002786 | 0.59018 | 0.11655 | 0.18608 | -0.045385 | 0.22441 | 120.4337 | -0.052816 | 120.7133 | 120.6514 | 0.21769 | 0.08242 | -0.005951 | 120.8148 | 120.7722 | 121.042 | 120.4527 | -120.8871 | 120.7647 | 120.9 | 120.8116 | 120.6669 | -0.38389
1566.5781 | 120.8313 | -120.5887 | 0.13275 | 1.4211e-13 | -0.023004 | 0.00071164 | 0.066913 | -0.011638 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018891 | 0.031936 | 0.0080825 | -120.0397 | -0.20463 | -120.5179 | 0.17574 | 0.12399 | 0.39379 | -120.6902 | 0.055992 | 0.014095 | -0.005985 | 0.10282 | 0.24721 | 0.15427 | -0.22825 | -0.10156 | 0.042993 | 0.54898 | 0.070774 | 0.17234 | -0.008761 | 0.26104 | 120.3604 | -0.029929 | 120.6447 | 120.5827 | 0.22227 | 0.11446 | 0.021515 | 120.7644 | 120.7127 | 120.9825 | 120.3841 | -120.823 | 120.6915 | 120.8359 | 120.743 | 120.6028 | -0.361
1568.2656 | 120.8817 | -120.639 | 0.11444 | 1.4211e-13 | -0.023218 | 0.00092524 | 0.066913 | -0.011852 | 0.059539 | 0.0079357 | -0.0023031 | 0.0051278 | 0.018463 | 0.032363 | 0.0085097 | -120.0809 | -0.21379 | -120.5545 | 0.15743 | 0.12399 | 0.38463 | -120.7406 | 0.06515 | 0.014095 | -0.010564 | 0.11198 | 0.24264 | 0.15427 | -0.2191 | -0.10158 | 0.04299 | 0.55813 | 0.084502 | 0.18608 | 0.009549 | 0.27019 | 120.4199 | -0.002462 | 120.7042 | 120.6285 | 0.20853 | 0.1282 | 0.039825 | 120.7965 | 120.763 | 121.0237 | 120.4253 | -120.8551 | 120.751 | 120.8817 | 120.7933 | 120.6531 | -0.33354
1570.0156 | 120.9091 | -120.6619 | 0.1236 | 1.4211e-13 | -0.023004 | 0.00049784 | 0.066913 | -0.011852 | 0.059112 | -0.0073253 | -0.0027303 | 0.0053414 | 0.018891 | 0.032363 | 0.0082961 | -120.0901 | -0.20921 | -120.5683 | 0.15743 | 0.11483 | 0.38463 | -120.7544 | 0.055992 | 0.014095 | -0.010564 | 0.11198 | 0.24264 | 0.14969 | -0.2191 | -0.092424 | 0.033835 | 0.57186 | 0.093655 | 0.18608 | -0.008764 | 0.26104 | 120.4428 | -0.011617 | 120.7179 | 120.6514 | 0.20853 | 0.11904 | 0.026091 | 120.8194 | 120.7768 | 121.0466 | 120.4527 | -120.8779 | 120.7739 | 120.9046 | 120.8116 | 120.676 | -0.34269
1571.7656 | 120.8084 | -120.6711 | 0.16022 | 1.4211e-13 | -0.023004 | 0.0011388 | 0.066699 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018891 | 0.032149 | 0.0078689 | -120.0992 | -0.20921 | -120.5774 | 0.15285 | 0.11483 | 0.38463 | -120.7589 | 0.055992 | 0.009516 | -0.001407 | 0.11198 | 0.25179 | 0.13137 | -0.22367 | -0.087847 | -0.007365 | 0.57186 | 0.093655 | 0.1815 | -0.045385 | 0.22441 | 120.4474 | -0.048238 | 120.7271 | 120.6697 | 0.22227 | 0.091577 | -0.028844 | 120.8239 | 120.7859 | 121.0557 | 120.4619 | -120.9191 | 120.7831 | 120.9229 | 120.8025 | 120.6806 | -0.38389
1573.5 | 120.9412 | -120.6619 | 0.11902 | 1.4211e-13 | -0.023218 | 0.00092524 | 0.066699 | -0.012279 | 0.059326 | 0.015566 | -0.0027303 | 0.005555 | 0.018891 | 0.032363 | 0.0080825 | -120.1084 | -0.21379 | -120.582 | 0.16201 | 0.11941 | 0.38005 | -120.7635 | 0.060571 | 0.018674 | -0.010564 | 0.1074 | 0.24264 | 0.12679 | -0.22367 | -0.10158 | 0.04299 | 0.55355 | 0.07992 | 0.1815 | 0.000392 | 0.26103 | 120.4383 | -0.011618 | 120.7225 | 120.6514 | 0.21311 | 0.12362 | 0.007775 | 120.8239 | 120.7813 | 121.042 | 120.4481 | -120.8825 | 120.7693 | 120.9046 | 120.7887 | 120.6806 | -0.34269
1575.1875 | 120.8542 | -120.7077 | 0.16022 | 1.4211e-13 | -0.02279 | 0.00092524 | 0.067126 | -0.011852 | 0.059326 | 0.0079357 | -0.0029439 | 0.0051278 | 0.018677 | 0.032363 | 0.0080825 | -120.1221 | -0.21379 | -120.6003 | 0.15285 | 0.12399 | 0.38463 | -120.7727 | 0.060571 | 0.018674 | -0.010564 | 0.1074 | 0.24264 | 0.15427 | -0.22367 | -0.064963 | -0.007365 | 0.58559 | 0.10738 | 0.17235 | -0.036227 | 0.22441 | 120.484 | -0.052816 | 120.7683 | 120.6971 | 0.21311 | 0.08242 | -0.005951 | 120.8606 | 120.8317 | 121.0923 | 120.4939 | -120.9329 | 120.8151 | 120.9503 | 120.862 | 120.7264 | -0.38389
1576.9531 | 120.9412 | -120.7123 | 0.15564 | 1.4211e-13 | -0.023431 | 0.0013526 | 0.066913 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018677 | 0.032577 | 0.0078689 | -120.1404 | -0.21379 | -120.6049 | 0.15743 | 0.11941 | 0.38005 | -120.791 | 0.051413 | 0.018674 | -0.001407 | 0.11198 | 0.24721 | 0.13137 | -0.22367 | -0.078702 | 0.001791 | 0.57185 | 0.10738 | 0.18609 | -0.036229 | 0.22441 | 120.4886 | -0.043661 | 120.7637 | 120.7109 | 0.22227 | 0.091575 | -0.024267 | 120.8697 | 120.8317 | 121.0923 | 120.4985 | -120.9466 | 120.8243 | 120.9595 | 120.8437 | 120.731 | -0.37931
1578.6406 | 120.8405 | -120.7397 | 0.16022 | 1.4211e-13 | -0.023218 | 0.00092524 | 0.067126 | -0.012279 | 0.059539 | 0.0079357 | -0.0023031 | 0.0053414 | 0.018891 | 0.032149 | 0.0078689 | -120.1496 | -0.21379 | -120.6141 | 0.15743 | 0.11941 | 0.38005 | -120.8001 | 0.060571 | 0.018674 | -0.001407 | 0.1074 | 0.24721 | 0.11764 | -0.2191 | -0.060394 | -0.002786 | 0.59016 | 0.12569 | 0.18609 | -0.040806 | 0.21984 | 120.5207 | -0.052816 | 120.8003 | 120.7383 | 0.21769 | 0.086998 | -0.04258 | 120.8972 | 120.8592 | 121.1198 | 120.526 | -120.9604 | 120.8471 | 120.987 | 120.8574 | 120.7584 | -0.37931
1580.375 | 120.845 | -120.7443 | 0.16022 | 1.4211e-13 | -0.023004 | 0.00071164 | 0.06734 | -0.011852 | 0.059539 | 0.00030522 | -0.0029439 | 0.005555 | 0.018677 | 0.032149 | 0.0080825 | -120.1496 | -0.20921 | -120.6186 | 0.16659 | 0.11483 | 0.38463 | -120.8185 | 0.06515 | 0.018674 | -0.005985 | 0.1074 | 0.24721 | 0.094744 | -0.2191 | -0.074131 | 0.00637 | 0.59474 | 0.12569 | 0.19982 | -0.045385 | 0.22441 | 120.5252 | -0.052816 | 120.8095 | 120.7383 | 0.21311 | 0.086998 | -0.065473 | 120.9109 | 120.8592 | 121.129 | 120.5351 | -120.9787 | 120.8517 | 120.9915 | 120.8391 | 120.763 | -0.37931
1582.125 | 120.9915 | -120.7306 | 0.14191 | 1.4211e-13 | -0.023004 | 0.00092524 | 0.067126 | -0.011425 | 0.059326 | 0.00030522 | -0.0031575 | 0.0053414 | 0.018677 | 0.032149 | 0.0078689 | -120.1587 | -0.21379 | -120.6278 | 0.16201 | 0.11941 | 0.38005 | -120.823 | 0.060571 | 0.023253 | -0.005985 | 0.11198 | 0.24264 | 0.14053 | -0.21452 | -0.092443 | 0.020102 | 0.57185 | 0.1028 | 0.19525 | -0.022496 | 0.23815 | 120.5161 | -0.029928 | 120.7912 | 120.7246 | 0.20853 | 0.10073 | -0.001377 | 120.8926 | 120.85 | 121.1106 | 120.5168 | -120.9649 | 120.8426 | 120.9732 | 120.8711 | 120.7538 | -0.35642
1583.8594 | 120.9045 | -120.7397 | 0.14648 | 1.4211e-13 | -0.023431 | 0.00092524 | 0.066913 | -0.011638 | 0.059539 | -0.0073253 | -0.0025167 | 0.0053414 | 0.018677 | 0.032363 | 0.0078689 | -120.1725 | -0.21379 | -120.6461 | 0.15743 | 0.11025 | 0.38005 | -120.8322 | 0.060571 | 0.018674 | -0.005985 | 0.1074 | 0.24264 | 0.14969 | -0.21452 | -0.092446 | 0.010947 | 0.56727 | 0.093644 | 0.18609 | -0.036231 | 0.23357 | 120.5252 | -0.039083 | 120.8003 | 120.7338 | 0.20853 | 0.096153 | 0.003203 | 120.8972 | 120.85 | 121.1198 | 120.526 | -120.9787 | 120.8471 | 120.9824 | 120.8894 | 120.7584 | -0.361
1585.5469 | 120.9641 | -120.7626 | 0.13733 | 1.4211e-13 | -0.023218 | 0.00071164 | 0.067126 | -0.012066 | 0.059753 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018677 | 0.032149 | 0.0080825 | -120.1725 | -0.21379 | -120.6553 | 0.15743 | 0.11483 | 0.38005 | -120.8414 | 0.055992 | 0.018674 | -0.001407 | 0.098244 | 0.24721 | 0.14969 | -0.21452 | -0.078716 | 0.020102 | 0.59016 | 0.10738 | 0.18609 | -0.022497 | 0.24272 | 120.5481 | -0.039085 | 120.8186 | 120.7612 | 0.21311 | 0.10989 | 0.012358 | 120.9201 | 120.8775 | 121.1427 | 120.5488 | -120.9787 | 120.8609 | 121.0098 | 120.9123 | 120.7813 | -0.35185
1587.3125 | 121.0052 | -120.726 | 0.13275 | 1.4211e-13 | -0.023218 | 0.00071164 | 0.066913 | -0.012066 | 0.059112 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018463 | 0.032149 | 0.0082961 | -120.1862 | -0.22295 | -120.669 | 0.15285 | 0.12399 | 0.37548 | -120.8414 | 0.051413 | 0.018674 | -0.005985 | 0.11198 | 0.24721 | 0.058115 | -0.22367 | -0.11534 | 0.020101 | 0.5398 | 0.05702 | 0.17236 | -0.008761 | 0.24272 | 120.5023 | -0.020772 | 120.7774 | 120.72 | 0.21769 | 0.11446 | -0.074636 | 120.8789 | 120.85 | 121.1015 | 120.5031 | -120.9741 | 120.838 | 120.9732 | 120.7841 | 120.7447 | -0.35642
1589 | 120.9 | -120.7809 | 0.15564 | 1.4211e-13 | -0.023218 | 0.0011388 | 0.066699 | -0.011638 | 0.059539 | 0.00030522 | -0.0031575 | 0.0053414 | 0.018463 | 0.032363 | 0.0080825 | -120.1954 | -0.21379 | -120.6827 | 0.15743 | 0.11483 | 0.38005 | -120.8551 | 0.051413 | 0.018674 | -0.001407 | 0.10282 | 0.25179 | 0.16342 | -0.2191 | -0.074142 | 0.001791 | 0.58558 | 0.098217 | 0.17236 | -0.040808 | 0.22441 | 120.5619 | -0.052818 | 120.8324 | 120.7795 | 0.21769 | 0.096154 | 0.007783 | 120.9384 | 120.8958 | 121.161 | 120.5672 | -121.0107 | 120.8838 | 121.0327 | 120.9444 | 120.7996 | -0.37474
1590.75 | 120.9824 | -120.7718 | 0.13733 | 1.4211e-13 | -0.023431 | 0.0011388 | 0.067126 | -0.012066 | 0.059326 | 0.0079357 | -0.0025167 | 0.0053414 | 0.01825 | 0.032363 | 0.0080825 | -120.2091 | -0.22295 | -120.6782 | 0.15743 | 0.11025 | 0.37548 | -120.8688 | 0.060571 | 0.014095 | -0.005985 | 0.11656 | 0.24721 | 0.090166 | -0.2191 | -0.097033 | 0.020102 | 0.56269 | 0.09364 | 0.19067 | -0.027076 | 0.23815 | 120.5527 | -0.020772 | 120.8324 | 120.7658 | 0.21311 | 0.10989 | -0.047163 | 120.9292 | 120.882 | 121.1473 | 120.5488 | -121.0062 | 120.8883 | 121.019 | 120.862 | 120.7859 | -0.35642
1592.5 | 121.0419 | -120.7443 | 0.11902 | 1.4211e-13 | -0.023431 | 0.00049784 | 0.066913 | -0.012066 | 0.059326 | 0.015566 | -0.0029439 | 0.0051278 | 0.018677 | 0.03279 | 0.0080825 | -120.2045 | -0.21837 | -120.6919 | 0.16201 | 0.11941 | 0.38463 | -120.8642 | 0.06515 | 0.014095 | -0.015143 | 0.1074 | 0.25179 | 0.14969 | -0.22367 | -0.11992 | 0.04299 | 0.5398 | 0.05244 | 0.17236 | 0.000392 | 0.26561 | 120.5207 | -0.011618 | 120.8095 | 120.7292 | 0.20853 | 0.13278 | 0.030668 | 120.9063 | 120.8637 | 121.129 | 120.526 | -120.9833 | 120.8517 | 120.9961 | 120.894 | 120.7584 | -0.34269
1594.1875 | 121.0052 | -120.7764 | 0.13733 | 1.4211e-13 | -0.023004 | 0.00092524 | 0.066699 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018463 | 0.032149 | 0.0080825 | -120.2228 | -0.21379 | -120.7056 | 0.15285 | 0.12399 | 0.38005 | -120.8871 | 0.06515 | 0.009516 | -0.010564 | 0.1074 | 0.25179 | 0.14969 | -0.21452 | -0.11077 | 0.015523 | 0.55353 | 0.070748 | 0.18152 | -0.013339 | 0.24272 | 120.5619 | -0.029928 | 120.8415 | 120.7658 | 0.20395 | 0.11447 | 0.012358 | 120.9292 | 120.9004 | 121.1564 | 120.5626 | -121.0245 | 120.8838 | 121.0282 | 120.9261 | 120.7859 | -0.35185
1595.9375 | 121.0602 | -120.7764 | 0.13733 | 1.4211e-13 | -0.023004 | 0.00049784 | 0.066699 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.032363 | 0.0082961 | -120.2366 | -0.22295 | -120.7102 | 0.16201 | 0.11483 | 0.37548 | -120.8871 | 0.060571 | 0.014095 | -0.005985 | 0.10282 | 0.25179 | 0.15884 | -0.2191 | -0.11077 | 0.02468 | 0.53979 | 0.066169 | 0.17694 | -0.022497 | 0.23815 | 120.5573 | -0.034507 | 120.8369 | 120.7704 | 0.21311 | 0.11447 | 0.021516 | 120.9384 | 120.8912 | 121.1518 | 120.5534 | -121.0245 | 120.8792 | 121.0282 | 120.9352 | 120.7905 | -0.35642
1597.6875 | 120.932 | -120.8267 | 0.15106 | 1.4211e-13 | -0.023004 | 0.00071164 | 0.066913 | -0.011852 | 0.059753 | 0.00030522 | -0.0025167 | 0.0053414 | 0.018463 | 0.032363 | 0.0078689 | -120.2412 | -0.22295 | -120.7239 | 0.15743 | 0.11483 | 0.38005 | -120.9009 | 0.055992 | 0.014095 | -0.001407 | 0.1074 | 0.24264 | 0.15884 | -0.2191 | -0.074155 | 0.006369 | 0.58557 | 0.10279 | 0.17694 | -0.03623 | 0.22899 | 120.6076 | -0.043661 | 120.8827 | 120.8253 | 0.21769 | 0.091575 | 0.007783 | 120.9842 | 120.9416 | 121.2068 | 120.6038 | -121.0519 | 120.9341 | 121.0694 | 120.9856 | 120.8408 | -0.37016
1599.3906 | 121.0236 | -120.7993 | 0.12817 | 1.4211e-13 | -0.02279 | 0.0013526 | 0.067126 | -0.011852 | 0.059539 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018677 | 0.032577 | 0.0080825 | -120.2412 | -0.22752 | -120.7239 | 0.15285 | 0.11483 | 0.38005 | -120.9055 | 0.060571 | 0.009516 | -0.001407 | 0.11198 | 0.23806 | 0.16342 | -0.22367 | -0.1062 | 0.024678 | 0.5581 | 0.075323 | 0.18152 | -0.013342 | 0.25188 | 120.5756 | -0.016195 | 120.8598 | 120.7978 | 0.22227 | 0.10988 | 0.035249 | 120.9521 | 120.9141 | 121.1793 | 120.5717 | -121.0336 | 120.9112 | 121.0373 | 120.9627 | 120.8088 | -0.35185
1601.125 | 120.9641 | -120.8359 | 0.17853 | 1.4211e-13 | -0.023218 | 0.00092524 | 0.067126 | -0.012279 | 0.059539 | -0.0073253 | -0.0027303 | 0.0051278 | 0.018677 | 0.032577 | 0.0078689 | -120.2549 | -0.22295 | -120.7422 | 0.16201 | 0.11025 | 0.38463 | -120.9192 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.24264 | 0.15884 | -0.21452 | -0.083316 | -0.016519 | 0.58099 | 0.093631 | 0.17695 | -0.068275 | 0.2061 | 120.6214 | -0.071127 | 120.901 | 120.8299 | 0.20853 | 0.064109 | -0.019683 | 120.9979 | 120.9461 | 121.2205 | 120.6129 | -121.0977 | 120.9433 | 121.0785 | 120.9947 | 120.8591 | -0.39304
1602.9219 | 120.9412 | -120.8542 | 0.16479 | 1.4211e-13 | -0.023431 | 0.00092524 | 0.067126 | -0.011852 | 0.059539 | 0.0079357 | -0.0023031 | 0.0051278 | 0.018677 | 0.032363 | 0.0080825 | -120.2595 | -0.22295 | -120.7514 | 0.16201 | 0.11483 | 0.38463 | -120.9238 | 0.060571 | 0.018674 | -0.010564 | 0.10282 | 0.24264 | 0.14969 | -0.22367 | -0.069584 | -0.002786 | 0.59472 | 0.10278 | 0.17237 | -0.049963 | 0.21984 | 120.6305 | -0.061973 | 120.9148 | 120.8436 | 0.21311 | 0.077842 | -0.015108 | 121.0162 | 120.969 | 121.2388 | 120.6312 | -121.0886 | 120.957 | 121.0968 | 121.0039 | 120.8729 | -0.38847
1604.6562 | 121.051 | -120.8313 | 0.1236 | 1.4211e-13 | -0.023645 | 0.0011388 | 0.066913 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018677 | 0.032363 | 0.0082961 | -120.2686 | -0.22295 | -120.756 | 0.15743 | 0.11483 | 0.38005 | -120.9283 | 0.060571 | 0.009516 | -0.001407 | 0.10282 | 0.24721 | 0.15427 | -0.2191 | -0.09705 | 0.033835 | 0.56268 | 0.075319 | 0.17237 | -0.008764 | 0.25646 | 120.6122 | -0.020774 | 120.8919 | 120.8299 | 0.21769 | 0.12362 | 0.03067 | 120.9887 | 120.9461 | 121.2114 | 120.6084 | -121.0519 | 120.9341 | 121.0785 | 120.9856 | 120.8408 | -0.34269
1606.3594 | 120.9641 | -120.8954 | 0.16022 | 1.4211e-13 | -0.023004 | 0.00049784 | 0.06734 | -0.012279 | 0.059539 | -0.0073253 | -0.0025167 | 0.0051278 | 0.018677 | 0.033004 | 0.0080825 | -120.2686 | -0.22752 | -120.7651 | 0.15743 | 0.11483 | 0.38005 | -120.9375 | 0.06515 | 0.023253 | -0.001407 | 0.1074 | 0.24721 | 0.15427 | -0.22367 | -0.042121 | -0.002786 | 0.62676 | 0.13025 | 0.17237 | -0.045385 | 0.21984 | 120.6717 | -0.052816 | 120.9605 | 120.894 | 0.22227 | 0.086998 | -0.005951 | 121.0528 | 121.0102 | 121.2754 | 120.6679 | -121.0977 | 121.0028 | 121.1426 | 121.0497 | 120.9186 | -0.38389
1608.0625 | 121.0098 | -120.8771 | 0.14648 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.066913 | -0.012279 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018891 | 0.032363 | 0.0080825 | -120.2869 | -0.22752 | -120.7743 | 0.15743 | 0.11941 | 0.38005 | -120.9421 | 0.055992 | 0.014095 | -0.005985 | 0.11656 | 0.25179 | 0.13595 | -0.22367 | -0.065011 | 0.010947 | 0.59014 | 0.10278 | 0.16779 | -0.027073 | 0.23357 | 120.6534 | -0.029927 | 120.9331 | 120.8711 | 0.21769 | 0.10531 | -0.010532 | 121.0345 | 120.9965 | 121.2571 | 120.6496 | -121.0886 | 120.9936 | 121.1289 | 121.013 | 120.8912 | -0.37016
1609.7656 | 120.9778 | -120.8862 | 0.15106 | 1.4211e-13 | -0.023431 | 0.00092524 | 0.067126 | -0.012279 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018891 | 0.032363 | 0.0082961 | -120.2869 | -0.22295 | -120.7835 | 0.16659 | 0.11941 | 0.37548 | -120.9558 | 0.060571 | 0.014095 | -0.005985 | 0.11198 | 0.24721 | 0.12679 | -0.2191 | -0.069593 | 0.015525 | 0.59929 | 0.10278 | 0.17237 | -0.031651 | 0.22441 | 120.6671 | -0.039083 | 120.9468 | 120.8802 | 0.21311 | 0.096153 | -0.024268 | 121.0528 | 121.0056 | 121.2617 | 120.6633 | -121.1069 | 120.9982 | 121.1334 | 121.013 | 120.9003 | -0.37016
1611.5156 | 121.0968 | -120.845 | 0.1236 | 1.4211e-13 | -0.023431 | 0.00092524 | 0.066699 | -0.012279 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018891 | 0.03279 | 0.0078689 | -120.2961 | -0.22752 | -120.7926 | 0.15285 | 0.11483 | 0.38463 | -120.9604 | 0.06515 | 0.014095 | -0.001407 | 0.11198 | 0.24264 | 0.14969 | -0.21452 | -0.11537 | 0.029256 | 0.54894 | 0.052425 | 0.16779 | -0.008764 | 0.26104 | 120.6305 | -0.011617 | 120.9102 | 120.8436 | 0.21311 | 0.11904 | 0.026091 | 120.9979 | 120.9599 | 121.2297 | 120.6175 | -121.084 | 120.957 | 121.0877 | 120.9947 | 120.8591 | -0.33811
1613.2031 | 121.0281 | -120.8908 | 0.14648 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.067126 | -0.012066 | 0.059112 | 0.0079357 | -0.0027303 | 0.005555 | 0.018463 | 0.032577 | 0.0080825 | -120.2961 | -0.2321 | -120.7972 | 0.16201 | 0.11025 | 0.38005 | -120.9696 | 0.060571 | 0.014095 | -0.010564 | 0.11198 | 0.24264 | 0.12222 | -0.2191 | -0.078752 | 0.015525 | 0.59472 | 0.093623 | 0.17238 | -0.036231 | 0.23357 | 120.6717 | -0.034505 | 120.9514 | 120.8802 | 0.20853 | 0.096153 | -0.024268 | 121.0528 | 121.0011 | 121.2709 | 120.6587 | -121.116 | 121.0028 | 121.1334 | 121.013 | 120.9049 | -0.36558
1614.9062 | 121.138 | -120.8633 | 0.13733 | 1.4211e-13 | -0.023645 | 0.00049784 | 0.066913 | -0.012066 | 0.059326 | -0.0073253 | -0.0025167 | 0.0047004 | 0.018463 | 0.032577 | 0.0078689 | -120.3053 | -0.23668 | -120.8063 | 0.15743 | 0.11483 | 0.38463 | -120.9787 | 0.06515 | 0.027831 | -0.010564 | 0.1074 | 0.24721 | 0.14969 | -0.2191 | -0.11538 | 0.020102 | 0.55809 | 0.057001 | 0.17238 | -0.022497 | 0.2473 | 120.6442 | -0.029928 | 120.9285 | 120.8528 | 0.20853 | 0.10989 | 0.012358 | 121.0208 | 120.9782 | 121.248 | 120.6267 | -121.116 | 120.9707 | 121.1106 | 121.013 | 120.8912 | -0.35642
1616.625 | 121.0007 | -120.9183 | 0.15106 | 1.4211e-13 | -0.023431 | 0.0011388 | 0.067126 | -0.012279 | 0.059539 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018891 | 0.032577 | 0.0080825 | -120.3144 | -0.22295 | -120.8109 | 0.15285 | 0.11025 | 0.37548 | -120.9879 | 0.055992 | 0.018674 | -0.001407 | 0.11656 | 0.24264 | 0.16342 | -0.2191 | -0.069601 | 0.00179 | 0.60387 | 0.10735 | 0.17696 | -0.040809 | 0.22441 | 120.6992 | -0.034505 | 120.9743 | 120.9169 | 0.21769 | 0.091575 | 0.012361 | 121.0711 | 121.0285 | 121.2937 | 120.6953 | -121.1389 | 121.0348 | 121.1609 | 121.0817 | 120.9369 | -0.37016
1618.3281 | 121.0464 | -120.9091 | 0.15564 | 1.4211e-13 | -0.023431 | 0.00049784 | 0.06734 | -0.011852 | 0.059753 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018463 | 0.032577 | 0.0078689 | -120.3236 | -0.22752 | -120.8247 | 0.14827 | 0.10567 | 0.37548 | -120.9925 | 0.060571 | 0.014095 | -0.010564 | 0.11656 | 0.25179 | 0.12679 | -0.2191 | -0.083335 | -0.007366 | 0.58555 | 0.084464 | 0.1678 | -0.049966 | 0.21984 | 120.69 | -0.039083 | 120.9697 | 120.8986 | 0.20853 | 0.096154 | -0.028846 | 121.0574 | 121.0148 | 121.2846 | 120.6816 | -121.1481 | 121.0257 | 121.1609 | 121.0359 | 120.9232 | -0.37474
1620.0312 | 121.1014 | -120.9 | 0.16937 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.067554 | -0.012066 | 0.059112 | 0.015566 | -0.0025167 | 0.0049142 | 0.018677 | 0.03279 | 0.0082961 | -120.3281 | -0.2321 | -120.8292 | 0.16201 | 0.11483 | 0.38463 | -120.997 | 0.055992 | 0.009516 | -0.005985 | 0.12114 | 0.24721 | 0.12679 | -0.21452 | -0.09707 | -0.007364 | 0.57182 | 0.07073 | 0.1678 | -0.054541 | 0.21526 | 120.6854 | -0.048237 | 120.956 | 120.894 | 0.20853 | 0.077842 | -0.042579 | 121.062 | 121.0148 | 121.2846 | 120.6679 | -121.1664 | 121.0211 | 121.1472 | 121.0268 | 120.9095 | -0.38389
1621.75 | 121.1563 | -120.932 | 0.13275 | 1.4211e-13 | -0.023431 | 0.00092524 | 0.067126 | -0.012066 | 0.059326 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018677 | 0.03279 | 0.0080825 | -120.3373 | -0.22752 | -120.8338 | 0.16201 | 0.11483 | 0.38005 | -121.0108 | 0.06515 | 0.018674 | -0.005985 | 0.11656 | 0.24721 | 0.14969 | -0.2191 | -0.078763 | 0.029258 | 0.59471 | 0.098196 | 0.17696 | -0.017919 | 0.2473 | 120.7129 | -0.016194 | 120.9972 | 120.926 | 0.21311 | 0.11446 | 0.016936 | 121.094 | 121.0468 | 121.3121 | 120.7045 | -121.1435 | 121.0486 | 121.1792 | 121.0817 | 120.9507 | -0.35185
1623.4844 | 121.1563 | -120.9366 | 0.10986 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.066699 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018891 | 0.032577 | 0.0080825 | -120.3465 | -0.22752 | -120.8338 | 0.15285 | 0.11025 | 0.38005 | -121.0153 | 0.060571 | 0.014095 | -0.001407 | 0.12114 | 0.25637 | 0.16342 | -0.2191 | -0.078765 | 0.042989 | 0.59013 | 0.10277 | 0.18154 | 0.00039 | 0.27019 | 120.7175 | 0.011273 | 120.9972 | 120.9352 | 0.21769 | 0.14651 | 0.05356 | 121.0894 | 121.0468 | 121.3166 | 120.7091 | -121.1252 | 121.0577 | 121.193 | 121.1 | 120.9507 | -0.32896
1625.1562 | 121.0785 | -120.9549 | 0.13733 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.06734 | -0.012279 | 0.059539 | 0.023196 | -0.0029439 | 0.0051278 | 0.018463 | 0.032577 | 0.0082961 | -120.3465 | -0.2321 | -120.8475 | 0.15743 | 0.11941 | 0.38463 | -121.0291 | 0.055992 | 0.018674 | -0.005985 | 0.12114 | 0.24721 | 0.12222 | -0.21452 | -0.074191 | 0.020102 | 0.60844 | 0.10735 | 0.18154 | -0.017918 | 0.2473 | 120.7404 | -0.016193 | 121.0109 | 120.9489 | 0.20853 | 0.10989 | -0.015113 | 121.1123 | 121.0743 | 121.3395 | 120.7228 | -121.1664 | 121.076 | 121.2021 | 121.0771 | 120.9736 | -0.35185
1626.8438 | 121.1517 | -120.932 | 0.1236 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.067126 | -0.012066 | 0.059112 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018463 | 0.033004 | 0.0076551 | -120.3602 | -0.23668 | -120.8521 | 0.15743 | 0.11483 | 0.38005 | -121.0245 | 0.055992 | 0.023253 | -0.005985 | 0.12114 | 0.25179 | 0.14969 | -0.22825 | -0.0925 | 0.033835 | 0.57182 | 0.079883 | 0.17238 | -0.008764 | 0.25646 | 120.7038 | -0.00246 | 120.988 | 120.926 | 0.22227 | 0.1282 | 0.026091 | 121.0894 | 121.0468 | 121.3121 | 120.6953 | -121.1481 | 121.0531 | 121.1838 | 121.0817 | 120.9553 | -0.35185
1628.5625 | 121.0785 | -120.9732 | 0.16022 | 1.4211e-13 | -0.023859 | 0.00028424 | 0.067554 | -0.012279 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.01825 | 0.03279 | 0.0078689 | -120.3602 | -0.23668 | -120.8567 | 0.15285 | 0.11941 | 0.38005 | -121.0382 | 0.06515 | 0.018674 | -0.005985 | 0.12114 | 0.24264 | 0.168 | -0.21452 | -0.065038 | -0.007365 | 0.61302 | 0.1165 | 0.18154 | -0.040806 | 0.21984 | 120.7587 | -0.039081 | 121.0384 | 120.9672 | 0.20853 | 0.08242 | 0.007785 | 121.1261 | 121.0926 | 121.3533 | 120.7365 | -121.1985 | 121.0943 | 121.2158 | 121.1412 | 120.9919 | -0.37473
1630.25 | 121.0739 | -120.9915 | 0.17395 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.067126 | -0.012493 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018677 | 0.032577 | 0.0078689 | -120.3693 | -0.24126 | -120.8659 | 0.15743 | 0.11025 | 0.37548 | -121.0428 | 0.060571 | 0.018674 | -0.005985 | 0.11656 | 0.25179 | 0.168 | -0.21452 | -0.051307 | -0.016519 | 0.62217 | 0.12566 | 0.17696 | -0.063697 | 0.20153 | 120.777 | -0.057393 | 121.0521 | 120.9855 | 0.20853 | 0.077844 | -0.005948 | 121.1489 | 121.1018 | 121.367 | 120.7503 | -121.2168 | 121.1081 | 121.2433 | 121.1595 | 121.0102 | -0.38847
1631.9531 | 121.1838 | -120.9091 | 0.1236 | 1.4211e-13 | -0.023645 | 0.00049784 | 0.067126 | -0.012066 | 0.059326 | -0.0073253 | -0.0029439 | 0.0051278 | 0.018463 | 0.03279 | 0.0078689 | -120.3785 | -0.24126 | -120.8704 | 0.15743 | 0.12399 | 0.38005 | -121.0474 | 0.06515 | 0.018674 | -0.010564 | 0.11656 | 0.23806 | 0.13595 | -0.20994 | -0.13828 | 0.033835 | 0.53061 | 0.038682 | 0.17697 | 0.000394 | 0.25646 | 120.6992 | -0.007039 | 120.9743 | 120.8986 | 0.19937 | 0.11446 | 0.012356 | 121.0666 | 121.0331 | 121.2892 | 120.6679 | -121.171 | 121.0257 | 121.1472 | 121.0451 | 120.9278 | -0.33353
1633.6875 | 121.257 | -120.9549 | 0.1236 | 1.4211e-13 | -0.023645 | 0.00049784 | 0.067126 | -0.012279 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018677 | 0.033004 | 0.0078689 | -120.3922 | -0.24126 | -120.8796 | 0.15285 | 0.11483 | 0.38463 | -121.0657 | 0.060571 | 0.014095 | -0.005985 | 0.11198 | 0.24721 | 0.15884 | -0.22367 | -0.11082 | 0.029256 | 0.56265 | 0.075301 | 0.18612 | -0.008764 | 0.26104 | 120.7312 | -0.011617 | 121.0155 | 120.9489 | 0.21769 | 0.12362 | 0.035249 | 121.1077 | 121.0697 | 121.3395 | 120.7136 | -121.1893 | 121.0669 | 121.2021 | 121.1137 | 120.969 | -0.34727
1635.4688 | 121.225 | -120.9549 | 0.1236 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.06734 | -0.012066 | 0.059539 | 0.00030522 | -0.0025167 | 0.0047004 | 0.018891 | 0.032577 | 0.0078689 | -120.3922 | -0.23668 | -120.8842 | 0.16659 | 0.11025 | 0.38005 | -121.0657 | 0.060571 | 0.023253 | -0.010564 | 0.12114 | 0.25179 | 0.14511 | -0.22367 | -0.11082 | 0.042991 | 0.56265 | 0.070723 | 0.18154 | -0.013343 | 0.25646 | 120.7312 | -0.00246 | 121.0155 | 120.9443 | 0.21311 | 0.1282 | 0.021513 | 121.1215 | 121.0651 | 121.3349 | 120.7182 | -121.1893 | 121.076 | 121.2067 | 121.1 | 120.9781 | -0.34727
1637.1719 | 121.0968 | -120.9778 | 0.15564 | 1.4211e-13 | -0.024072 | 0.00092524 | 0.067126 | -0.012066 | 0.059539 | 0.0079357 | -0.0029439 | 0.0049142 | 0.018463 | 0.032577 | 0.0080825 | -120.3968 | -0.24126 | -120.8888 | 0.16201 | 0.11483 | 0.37548 | -121.0703 | 0.060571 | 0.018674 | -0.001407 | 0.11198 | 0.25179 | 0.168 | -0.22367 | -0.092513 | 0.006369 | 0.58097 | 0.089033 | 0.18155 | -0.040808 | 0.21984 | 120.7541 | -0.043661 | 121.0384 | 120.9764 | 0.22227 | 0.096154 | 0.012362 | 121.1398 | 121.0926 | 121.3533 | 120.7365 | -121.2259 | 121.0898 | 121.2296 | 121.1458 | 120.9965 | -0.37931
1638.8594 | 121.1197 | -121.0236 | 0.17853 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.066913 | -0.012493 | 0.059326 | 0.0079357 | -0.0029439 | 0.0051278 | 0.018677 | 0.033004 | 0.0076551 | -120.4014 | -0.24126 | -120.8933 | 0.16201 | 0.11483 | 0.38005 | -121.084 | 0.06515 | 0.023253 | -0.005985 | 0.12114 | 0.25637 | 0.14969 | -0.2191 | -0.060473 | -0.016519 | 0.62216 | 0.13023 | 0.1907 | -0.063696 | 0.20152 | 120.8045 | -0.057392 | 121.0887 | 121.0176 | 0.21311 | 0.077844 | -0.028841 | 121.1856 | 121.1384 | 121.4036 | 120.7823 | -121.2626 | 121.1447 | 121.2799 | 121.1732 | 121.0468 | -0.39762
1640.5938 | 121.1288 | -121.0236 | 0.16479 | 1.4211e-13 | -0.023645 | 0.00049784 | 0.06734 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018677 | 0.032577 | 0.0078689 | -120.4106 | -0.24126 | -120.9025 | 0.16201 | 0.10567 | 0.3709 | -121.084 | 0.060571 | 0.023253 | -0.010564 | 0.11198 | 0.24721 | 0.15884 | -0.22367 | -0.060473 | -0.002786 | 0.61301 | 0.12108 | 0.18155 | -0.059121 | 0.2061 | 120.7999 | -0.052816 | 121.0841 | 121.013 | 0.21311 | 0.08242 | -0.00595 | 121.1856 | 121.1292 | 121.3945 | 120.7823 | -121.2488 | 121.1355 | 121.2708 | 121.1824 | 121.0468 | -0.38847
1642.3438 | 121.1929 | -120.9869 | 0.14191 | 1.4211e-13 | -0.023645 | 0.00092524 | 0.066913 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.032577 | 0.0082961 | -120.4197 | -0.24584 | -120.9162 | 0.15285 | 0.11941 | 0.38005 | -121.0932 | 0.060571 | 0.023253 | -0.005985 | 0.11656 | 0.24264 | 0.12222 | -0.22367 | -0.10625 | 0.010945 | 0.56723 | 0.070718 | 0.17697 | -0.022496 | 0.23815 | 120.7633 | -0.02535 | 121.0475 | 120.981 | 0.21769 | 0.10073 | -0.019691 | 121.1398 | 121.1063 | 121.367 | 120.7411 | -121.2351 | 121.1035 | 121.2296 | 121.1092 | 121.0102 | -0.36558
1644.0938 | 121.1746 | -121.0327 | 0.16022 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.06734 | -0.011852 | 0.059326 | -0.0073253 | -0.0029439 | 0.0053414 | 0.018677 | 0.03279 | 0.0080825 | -120.4289 | -0.25042 | -120.9116 | 0.15285 | 0.11483 | 0.38921 | -121.0978 | 0.060571 | 0.023253 | -0.010564 | 0.11656 | 0.24721 | 0.14511 | -0.22367 | -0.065055 | -0.007365 | 0.60385 | 0.12107 | 0.18613 | -0.045385 | 0.22899 | 120.809 | -0.04366 | 121.0933 | 121.0222 | 0.21311 | 0.086998 | -0.015108 | 121.1856 | 121.1475 | 121.4219 | 120.7823 | -121.258 | 121.1493 | 121.2799 | 121.1778 | 121.056 | -0.38389
1645.7656 | 121.2479 | -120.9686 | 0.12817 | 1.4211e-13 | -0.023645 | 0.0011388 | 0.066913 | -0.011852 | 0.059326 | 0.015566 | -0.0025167 | 0.0047004 | 0.018463 | 0.032577 | 0.0078689 | -120.4243 | -0.24584 | -120.9254 | 0.15743 | 0.11025 | 0.37548 | -121.1023 | 0.060571 | 0.023253 | -0.001407 | 0.11198 | 0.24264 | 0.14511 | -0.2191 | -0.13372 | 0.029257 | 0.54434 | 0.043251 | 0.17697 | -0.017921 | 0.2473 | 120.7495 | -0.016195 | 121.0292 | 120.9672 | 0.21769 | 0.11446 | 0.016935 | 121.1261 | 121.0789 | 121.3441 | 120.7228 | -121.2305 | 121.0806 | 121.2113 | 121.1137 | 120.9919 | -0.34727
1647.5 | 121.2708 | -120.9686 | 0.10986 | 1.4211e-13 | -0.023859 | 0.00092524 | 0.067126 | -0.012066 | 0.059539 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018677 | 0.033004 | 0.0080825 | -120.438 | -0.24584 | -120.9345 | 0.15285 | 0.11941 | 0.38463 | -121.1115 | 0.060571 | 0.014095 | -0.001407 | 0.11656 | 0.25179 | 0.168 | -0.21452 | -0.14288 | 0.042989 | 0.5306 | 0.034095 | 0.17697 | 0.009548 | 0.27477 | 120.7541 | 0.006694 | 121.0292 | 120.9672 | 0.21311 | 0.14193 | 0.058139 | 121.1215 | 121.088 | 121.3533 | 120.7228 | -121.2214 | 121.0852 | 121.2204 | 121.1366 | 120.9827 | -0.32438
1649.1875 | 121.2662 | -120.9961 | 0.12817 | 1.4211e-13 | -0.023431 | 0.00092524 | 0.06734 | -0.011852 | 0.059753 | 0.0079357 | -0.0025167 | 0.0051278 | 0.01825 | 0.03279 | 0.0078689 | -120.4426 | -0.25042 | -120.9345 | 0.14827 | 0.11025 | 0.38005 | -121.1161 | 0.06515 | 0.018674 | -0.005985 | 0.11198 | 0.23348 | 0.16342 | -0.20994 | -0.11999 | 0.0201 | 0.55349 | 0.061561 | 0.18155 | -0.017921 | 0.25188 | 120.7862 | -0.016195 | 121.0612 | 120.9901 | 0.20395 | 0.1053 | 0.035249 | 121.1444 | 121.1063 | 121.3761 | 120.7457 | -121.2443 | 121.1081 | 121.2296 | 121.1595 | 121.0148 | -0.33811
1650.9375 | 121.1884 | -121.0464 | 0.15106 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.066913 | -0.012066 | 0.059326 | 0.00030522 | -0.0029439 | 0.005555 | 0.01825 | 0.032577 | 0.0080825 | -120.438 | -0.25042 | -120.9391 | 0.16201 | 0.11483 | 0.37548 | -121.1252 | 0.055992 | 0.023253 | -0.005985 | 0.11656 | 0.24721 | 0.16342 | -0.22367 | -0.078795 | 0.010947 | 0.60842 | 0.10734 | 0.18613 | -0.03623 | 0.22441 | 120.8228 | -0.034505 | 121.1024 | 121.0405 | 0.21769 | 0.096153 | 0.012361 | 121.2085 | 121.1613 | 121.4219 | 120.796 | -121.2763 | 121.163 | 121.2937 | 121.2099 | 121.0697 | -0.37474
1652.625 | 121.2021 | -121.0556 | 0.15564 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.067126 | -0.012066 | 0.059967 | 0.0079357 | -0.0027303 | 0.005555 | 0.018463 | 0.032577 | 0.0080825 | -120.4609 | -0.25042 | -120.9483 | 0.15285 | 0.11025 | 0.37548 | -121.1298 | 0.06515 | 0.018674 | -0.010564 | 0.11656 | 0.25179 | 0.15884 | -0.2191 | -0.074219 | -0.002788 | 0.59469 | 0.10734 | 0.18155 | -0.045387 | 0.21984 | 120.8365 | -0.039083 | 121.1208 | 121.045 | 0.20853 | 0.096154 | 0.003205 | 121.2085 | 121.1659 | 121.4311 | 120.8052 | -121.2855 | 121.1722 | 121.3074 | 121.2144 | 121.0743 | -0.37474
1654.3594 | 121.1609 | -121.0693 | 0.16479 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.067126 | -0.012066 | 0.059539 | 0.00030522 | -0.0025167 | 0.0051278 | 0.018677 | 0.032577 | 0.0076551 | -120.4609 | -0.25042 | -120.9574 | 0.15743 | 0.11483 | 0.38005 | -121.1344 | 0.060571 | 0.023253 | -0.005985 | 0.11656 | 0.24721 | 0.168 | -0.2191 | -0.065065 | -0.007364 | 0.60842 | 0.11191 | 0.17698 | -0.049963 | 0.21526 | 120.8502 | -0.048238 | 121.1299 | 121.0634 | 0.21311 | 0.08242 | 0.003207 | 121.2268 | 121.1842 | 121.4494 | 120.8189 | -121.2992 | 121.1859 | 121.3166 | 121.2373 | 121.0926 | -0.38389
1656.0938 | 121.2708 | -121.0281 | 0.1236 | 1.4211e-13 | -0.024072 | 0.00092524 | 0.067554 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.01825 | 0.03279 | 0.0080825 | -120.4655 | -0.25042 | -120.9574 | 0.15743 | 0.11483 | 0.36174 | -121.139 | 0.060571 | 0.014095 | -0.010564 | 0.12114 | 0.24721 | 0.16342 | -0.22367 | -0.11084 | 0.033835 | 0.56264 | 0.070712 | 0.18156 | -0.008764 | 0.23814 | 120.8045 | -0.00246 | 121.0887 | 121.0176 | 0.21311 | 0.12362 | 0.039827 | 121.1856 | 121.143 | 121.3899 | 120.7777 | -121.2626 | 121.1493 | 121.2754 | 121.1916 | 121.0422 | -0.34727
1657.7812 | 121.1975 | -121.0648 | 0.16022 | 1.4211e-13 | -0.023859 | 0.00092524 | 0.06734 | -0.011852 | 0.059539 | -0.0073253 | -0.0027303 | 0.0053414 | 0.018677 | 0.032577 | 0.0078689 | -120.4701 | -0.25042 | -120.9757 | 0.15285 | 0.10567 | 0.3709 | -121.1436 | 0.051413 | 0.014095 | -0.001407 | 0.12114 | 0.25637 | 0.17258 | -0.2191 | -0.078801 | -0.007365 | 0.59469 | 0.08902 | 0.16782 | -0.054543 | 0.21068 | 120.8457 | -0.039081 | 121.1162 | 121.0634 | 0.21769 | 0.096155 | 0.012363 | 121.2176 | 121.1704 | 121.4357 | 120.8143 | -121.3038 | 121.1859 | 121.3211 | 121.2373 | 121.0789 | -0.37931
1659.5312 | 121.1975 | -121.106 | 0.17395 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.067554 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018677 | 0.032363 | 0.0074415 | -120.4747 | -0.255 | -120.9849 | 0.15743 | 0.11483 | 0.37548 | -121.1573 | 0.055992 | 0.018674 | -0.001407 | 0.12114 | 0.25179 | 0.14969 | -0.2191 | -0.051339 | -0.016519 | 0.63131 | 0.12106 | 0.1724 | -0.059118 | 0.20153 | 120.8869 | -0.052814 | 121.1619 | 121.1046 | 0.21769 | 0.077844 | -0.024263 | 121.2634 | 121.2208 | 121.4814 | 120.851 | -121.3312 | 121.2271 | 121.3578 | 121.2556 | 121.1246 | -0.39304
1661.2188 | 121.1884 | -121.0876 | 0.16937 | 1.4211e-13 | -0.023645 | 0.00092524 | 0.067126 | -0.012279 | 0.059753 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.03279 | 0.0076551 | -120.4884 | -0.26415 | -120.9849 | 0.15285 | 0.11025 | 0.37548 | -121.1573 | 0.060571 | 0.018674 | -0.005985 | 0.12571 | 0.25637 | 0.168 | -0.21452 | -0.06965 | -0.016521 | 0.59926 | 0.10275 | 0.1724 | -0.05912 | 0.2061 | 120.8731 | -0.043659 | 121.1482 | 121.0817 | 0.20853 | 0.086999 | -0.001371 | 121.2405 | 121.1979 | 121.4631 | 120.8235 | -121.3267 | 121.2134 | 121.344 | 121.2556 | 121.1063 | -0.38389
1662.9688 | 121.2524 | -121.0739 | 0.13275 | 1.4211e-13 | -0.024072 | 0.00071164 | 0.067126 | -0.012279 | 0.059753 | 0.023196 | -0.0029439 | 0.0047004 | 0.018677 | 0.033004 | 0.0082961 | -120.4884 | -0.25957 | -120.9941 | 0.15285 | 0.11941 | 0.37548 | -121.1619 | 0.060571 | 0.018674 | -0.001407 | 0.12114 | 0.24721 | 0.17258 | -0.21452 | -0.087961 | 0.020101 | 0.58553 | 0.079863 | 0.16782 | -0.01334 | 0.24272 | 120.8594 | -0.011615 | 121.1345 | 121.0725 | 0.21311 | 0.11446 | 0.039829 | 121.2268 | 121.1933 | 121.4494 | 120.8143 | -121.2946 | 121.1951 | 121.3211 | 121.2465 | 121.0926 | -0.34727
1664.6562 | 121.3165 | -121.0602 | 0.11902 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.067126 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.03279 | 0.0078689 | -120.493 | -0.25957 | -120.9941 | 0.15743 | 0.11483 | 0.38005 | -121.171 | 0.060571 | 0.027831 | 0.003172 | 0.12114 | 0.24721 | 0.13595 | -0.2191 | -0.11085 | 0.038412 | 0.56722 | 0.06613 | 0.17698 | -0.004187 | 0.26103 | 120.8411 | 0.002117 | 121.1208 | 121.0634 | 0.22227 | 0.1282 | 0.016933 | 121.2176 | 121.175 | 121.4402 | 120.8006 | -121.2901 | 121.1813 | 121.3074 | 121.1961 | 121.088 | -0.33811
1666.3906 | 121.1975 | -121.1288 | 0.16022 | 1.4211e-13 | -0.023645 | 0.0011388 | 0.06734 | -0.012279 | 0.059326 | 0.015566 | -0.0027303 | 0.0051278 | 0.018677 | 0.03279 | 0.0076551 | -120.5067 | -0.25957 | -121.0032 | 0.15743 | 0.11483 | 0.37548 | -121.1756 | 0.06515 | 0.018674 | -0.001407 | 0.11198 | 0.25179 | 0.15884 | -0.21452 | -0.046766 | -0.002786 | 0.62215 | 0.12564 | 0.1724 | -0.045385 | 0.21526 | 120.9143 | -0.048238 | 121.194 | 121.1274 | 0.21311 | 0.091577 | -0.001372 | 121.2863 | 121.2437 | 121.5043 | 120.8693 | -121.3358 | 121.2408 | 121.3806 | 121.2877 | 121.1475 | -0.37473
1668.1406 | 121.3028 | -121.0648 | 0.1236 | 1.4211e-13 | -0.023431 | 0.00071164 | 0.06734 | -0.012066 | 0.059753 | -0.0073253 | -0.0027303 | 0.0051278 | 0.01825 | 0.03279 | 0.0076551 | -120.5021 | -0.26415 | -121.0124 | 0.15743 | 0.10567 | 0.38921 | -121.1848 | 0.060571 | 0.018674 | -0.010564 | 0.12114 | 0.24721 | 0.168 | -0.2191 | -0.12001 | 0.033835 | 0.56264 | 0.052394 | 0.1724 | -0.017922 | 0.26561 | 120.8457 | -0.00246 | 121.1253 | 121.0542 | 0.20853 | 0.12362 | 0.044406 | 121.2222 | 121.1704 | 121.454 | 120.8006 | -121.3084 | 121.1859 | 121.312 | 121.2328 | 121.0834 | -0.34269
1669.8906 | 121.2616 | -121.1014 | 0.13733 | 1.4211e-13 | -0.024072 | 0.00071164 | 0.067126 | -0.012279 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018677 | 0.033004 | 0.0082961 | -120.5113 | -0.26415 | -121.0169 | 0.15285 | 0.11025 | 0.37548 | -121.1802 | 0.060571 | 0.018674 | -0.005985 | 0.11656 | 0.25637 | 0.14511 | -0.2191 | -0.078811 | 0.015523 | 0.5901 | 0.084437 | 0.16325 | -0.027076 | 0.23815 | 120.8823 | -0.020772 | 121.1619 | 121.0954 | 0.21311 | 0.11904 | 0.00778 | 121.2542 | 121.2116 | 121.4769 | 120.8372 | -121.3175 | 121.2179 | 121.3578 | 121.2465 | 121.1201 | -0.35642
1671.5781 | 121.2479 | -121.1151 | 0.15564 | 1.4211e-13 | -0.024072 | 0.00092524 | 0.067126 | -0.011852 | 0.059326 | 0.0079357 | -0.0029439 | 0.0053414 | 0.018677 | 0.033004 | 0.0078689 | -120.5204 | -0.26415 | -121.0169 | 0.15743 | 0.10567 | 0.3709 | -121.1893 | 0.055992 | 0.023253 | -0.001407 | 0.11198 | 0.25179 | 0.15427 | -0.22367 | -0.074236 | 0.001791 | 0.59468 | 0.09817 | 0.17241 | -0.049966 | 0.21526 | 120.8914 | -0.043661 | 121.1711 | 121.1137 | 0.22227 | 0.096154 | -0.001374 | 121.2725 | 121.2208 | 121.486 | 120.851 | -121.345 | 121.2271 | 121.3669 | 121.2694 | 121.1384 | -0.37931
1673.3125 | 121.3486 | -121.0831 | 0.11444 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.066699 | -0.012279 | 0.059539 | 0.0079357 | -0.0023031 | 0.0051278 | 0.018677 | 0.033004 | 0.0078689 | -120.5204 | -0.26415 | -121.0261 | 0.15743 | 0.11483 | 0.38463 | -121.1939 | 0.06515 | 0.018674 | -0.005985 | 0.11656 | 0.25179 | 0.15427 | -0.2191 | -0.11086 | 0.04299 | 0.56263 | 0.05697 | 0.16783 | 0.000391 | 0.27019 | 120.864 | 0.002116 | 121.1482 | 121.0771 | 0.21311 | 0.13735 | 0.039825 | 121.2405 | 121.1979 | 121.4677 | 120.8189 | -121.3084 | 121.1996 | 121.3349 | 121.2373 | 121.1017 | -0.33354
1675.0625 | 121.3074 | -121.1197 | 0.13733 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.06734 | -0.012066 | 0.059112 | 0.0079357 | -0.0027303 | 0.0053414 | 0.01825 | 0.03279 | 0.0082961 | -120.5342 | -0.26415 | -121.0307 | 0.15743 | 0.11025 | 0.3709 | -121.2031 | 0.069728 | 0.023253 | -0.001407 | 0.11198 | 0.24721 | 0.15884 | -0.2191 | -0.083395 | 0.020102 | 0.58552 | 0.089013 | 0.17241 | -0.027076 | 0.23357 | 120.9006 | -0.02535 | 121.1894 | 121.1183 | 0.21769 | 0.10989 | 0.021516 | 121.2771 | 121.2299 | 121.4906 | 120.8555 | -121.3404 | 121.2317 | 121.3669 | 121.2785 | 121.1429 | -0.35642
1676.75 | 120.9961 | -119.7601 | 1.1902 | 1.4211e-13 | -0.023859 | 0.00049784 | 0.067126 | -0.01292 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.033004 | 0.0080825 | -119.2843 | -0.255 | -119.7854 | 1.1143 | 1.1222 | 1.3461 | -119.9942 | 0.060571 | 0.014095 | -0.001407 | 0.11656 | 0.24264 | 0.168 | -0.20994 | -0.23412 | -0.075872 | 0.47586 | -0.025253 | 0.20886 | -0.06799 | 0.15595 | 119.5502 | -1.0736 | 119.8207 | 119.7587 | 0.20853 | -0.94755 | -1.0222 | 120.8744 | 120.8823 | 121.1063 | 119.5051 | -121.1844 | 119.8767 | 120.0028 | 119.9281 | 119.7742 | -1.4001
1678.5 | 120.4651 | -5.2414 | 115.4022 | 1.4211e-13 | -0.023004 | 0.0015662 | 0.067554 | -0.012279 | 0.058257 | 0.0079357 | -0.0025167 | 0.0053414 | 0.018677 | 0.033004 | 0.0076551 | -7.2649 | 0.76145 | -7.4252 | 112.9002 | 112.8983 | 112.8168 | -7.426 | 0.037677 | 0.004938 | -0.028879 | 0.093665 | 0.22432 | -0.015142 | -0.24199 | -2.1846 | -2.502 | -2.0235 | -2.1838 | 0.000744 | -2.5039 | -2.5854 | 4.9994 | -115.3086 | 5.2791 | 5.2125 | 0.21311 | -115.1779 | -115.4174 | 118.1416 | 118.1397 | 118.0582 | 6.0028 | -122.8282 | 5.3351 | 5.4657 | 5.2263 | 5.2463 | -115.6442
1680.2344 | 120.8038 | -3.8315 | 116.9449 | 1.4211e-13 | -0.02279 | 0.0015662 | 0.067981 | -0.012279 | 0.058257 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018677 | 0.03279 | 0.0078689 | -4.005 | 0.46842 | -4.106 | 116.6545 | 116.621 | 116.6399 | -4.207 | 0.042256 | 0.009516 | -0.028879 | 0.098244 | 0.21974 | 0.030644 | -0.24657 | -0.3755 | -0.29037 | -0.17356 | -0.27449 | 0.10101 | -0.3239 | -0.30496 | 3.5849 | -116.8466 | 3.8737 | 3.8026 | 0.21769 | -116.7251 | -116.9142 | 120.486 | 120.4525 | 120.4714 | 4.2999 | -121.1519 | 3.9297 | 4.0512 | 3.8621 | 3.841 | -117.1915
1681.9844 | 120.7718 | -2.7512 | 118.158 | 1.4211e-13 | -0.022577 | 0.0015662 | 0.068195 | -0.012279 | 0.05783 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018463 | 0.033218 | 0.0076551 | -2.9291 | 0.41348 | -3.0118 | 117.8495 | 117.8024 | 117.8395 | -3.1493 | 0.037677 | 0.000359 | -0.028879 | 0.089087 | 0.2289 | 0.058115 | -0.24657 | -0.39809 | -0.30849 | -0.17796 | -0.2606 | 0.13749 | -0.35561 | -0.31844 | 2.5046 | -118.0689 | 2.7888 | 2.7223 | 0.21769 | -117.9291 | -118.0998 | 120.6006 | 120.5535 | 120.5907 | 3.1646 | -121.3072 | 2.8402 | 2.9801 | 2.8093 | 2.7515 | -118.4045
1683.6719 | 120.9732 | -4.1153 | 116.748 | 1.4211e-13 | -0.023004 | 0.0015662 | 0.068195 | -0.012493 | 0.058471 | 0.00030522 | -0.0025167 | 0.0051278 | 0.018677 | 0.03279 | 0.0076551 | -4.5499 | 0.34938 | -4.6371 | 116.2882 | 116.2364 | 116.292 | -4.7702 | 0.042256 | 0.000359 | -0.028879 | 0.093665 | 0.22432 | 0.021486 | -0.24657 | -0.6549 | -0.45981 | -0.43458 | -0.52176 | 0.13314 | -0.51169 | -0.45609 | 3.8687 | -116.6544 | 4.1576 | 4.0864 | 0.21769 | -116.5237 | -116.7266 | 120.4035 | 120.3517 | 120.4073 | 4.4647 | -121.5182 | 4.209 | 4.3396 | 4.1368 | 4.1157 | -116.9946
1685.4062 | 120.9686 | -114.9628 | 5.8548 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.066699 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.033004 | 0.0078689 | -113.7124 | -0.52971 | -114.0671 | 6.7778 | 6.7497 | 7.019 | -114.3439 | 0.055992 | 0.023253 | -0.005985 | 0.1074 | 0.24721 | 0.14511 | -0.2191 | 0.61891 | 0.92298 | 1.2504 | 0.89566 | 0.27674 | 0.8949 | 1.1642 | 114.7437 | -5.7474 | 115.0188 | 114.9568 | 0.21311 | -5.6076 | -5.7097 | 121.7405 | 121.7125 | 121.9818 | 114.4331 | -120.1987 | 115.0702 | 115.21 | 115.1079 | 114.986 | -6.0739
1687.1562 | 121.1563 | -118.0344 | 2.7969 | 1.4211e-13 | -0.023859 | 0.00028424 | 0.066913 | -0.012279 | 0.059112 | 0.00030522 | -0.0025167 | 0.0049142 | 0.018463 | 0.033004 | 0.0078689 | -117.572 | -0.3832 | -118.0136 | 2.9045 | 2.9171 | 3.1272 | -118.2634 | 0.060571 | 0.023253 | -0.005985 | 0.11656 | 0.25179 | 0.14053 | -0.2191 | -0.22905 | 0.10753 | 0.46241 | 0.020773 | 0.24983 | 0.1202 | 0.33028 | 117.8153 | -2.6804 | 118.0949 | 118.0284 | 0.21311 | -2.5451 | -2.6564 | 120.9388 | 120.9515 | 121.1616 | 117.6512 | -121.0604 | 118.1509 | 118.2862 | 118.1749 | 118.0576 | -3.016
1688.8906 | 121.0556 | -119.101 | 1.8997 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.066913 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.018677 | 0.033004 | 0.0076551 | -118.5151 | -0.34657 | -119.0071 | 1.8972 | 1.9601 | 2.1794 | -119.2479 | 0.060571 | 0.023253 | 0.003172 | 0.11656 | 0.24264 | 0.15884 | -0.20536 | -0.14693 | -0.002501 | 0.58585 | 0.093875 | 0.24081 | 0.06042 | 0.27973 | 118.8956 | -1.7832 | 119.1615 | 119.1041 | 0.20853 | -1.6571 | -1.7409 | 120.9982 | 121.0611 | 121.2804 | 118.7544 | -121.1476 | 119.2175 | 119.3436 | 119.2598 | 119.1242 | -2.1051
1690.625 | 121.0739 | -119.8746 | 1.1124 | 1.4211e-13 | -0.023859 | 0.00028424 | 0.066913 | -0.012066 | 0.059326 | 0.0079357 | -0.0025167 | 0.0051278 | 0.018677 | 0.03279 | 0.0078689 | -119.266 | -0.33283 | -119.7625 | 1.1601 | 1.2321 | 1.4514 | -120.008 | 0.060571 | 0.018674 | -0.001407 | 0.12114 | 0.24264 | 0.14053 | -0.22367 | -0.13341 | 0.047732 | 0.60862 | 0.11208 | 0.24549 | 0.11972 | 0.33908 | 119.6509 | -0.99123 | 119.9351 | 119.8732 | 0.22227 | -0.86973 | -0.97184 | 121.0347 | 121.1067 | 121.326 | 119.5417 | -121.1204 | 119.9957 | 120.1172 | 120.0151 | 119.8932 | -1.336
1692.3125 | 121.0373 | -120.0211 | 1.0162 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.067126 | -0.012279 | 0.059326 | 0.015566 | -0.0025167 | 0.0053414 | 0.018677 | 0.03279 | 0.0076551 | -119.5544 | -0.31452 | -120.0647 | 0.88082 | 0.95735 | 1.1722 | -120.3056 | 0.06515 | 0.014095 | -0.001407 | 0.11656 | 0.25637 | 0.16342 | -0.2191 | -0.28456 | -0.13542 | 0.46666 | -0.043603 | 0.24096 | -0.058881 | 0.15592 | 119.802 | -0.89968 | 120.0862 | 120.0196 | 0.21769 | -0.75986 | -0.85281 | 120.9019 | 120.9784 | 121.1932 | 119.7065 | -121.3219 | 120.1376 | 120.2774 | 120.1845 | 120.0352 | -1.2353
1694.0625 | 121.1975 | -119.4168 | 1.5884 | 1.4211e-13 | -0.023859 | 0.0011388 | 0.067554 | -0.011852 | 0.059112 | 0.015566 | -0.0029439 | 0.0049142 | 0.01825 | 0.033004 | 0.0078689 | -118.8081 | -0.30994 | -119.3001 | 1.6591 | 1.7266 | 1.9414 | -119.5364 | 0.055992 | 0.023253 | -0.001407 | 0.11198 | 0.25179 | 0.15884 | -0.22367 | -0.11955 | 0.070702 | 0.60869 | 0.11672 | 0.23627 | 0.13817 | 0.35292 | 119.1931 | -1.4765 | 119.4728 | 119.4154 | 0.22227 | -1.3366 | -1.4296 | 121.076 | 121.1434 | 121.3582 | 119.1069 | -121.1248 | 119.5288 | 119.6686 | 119.5757 | 119.4401 | -1.8121
1695.75 | 121.1334 | -120.2591 | 0.79193 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.06734 | -0.012279 | 0.059112 | 0.00030522 | -0.0031575 | 0.005555 | 0.018463 | 0.033004 | 0.0076551 | -119.678 | -0.30536 | -120.1883 | 0.79841 | 0.80625 | 1.0852 | -120.4247 | 0.055992 | 0.023253 | -0.001407 | 0.11656 | 0.24264 | 0.14969 | -0.20994 | -0.16557 | 0.006474 | 0.58108 | 0.07082 | 0.23639 | 0.014319 | 0.29323 | 120.0492 | -0.67537 | 120.3151 | 120.2577 | 0.20853 | -0.54929 | -0.64224 | 121.0575 | 121.0653 | 121.3443 | 119.9537 | -121.2166 | 120.3757 | 120.5017 | 120.4088 | 120.2823 | -1.0019
1697.5 | 121.2524 | -117.572 | 3.3829 | 1.4211e-13 | -0.023645 | 0.00071164 | 0.06734 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0053414 | 0.01825 | 0.033218 | 0.0080825 | -117.0317 | -0.29162 | -117.5146 | 3.4997 | 3.5216 | 3.7362 | -117.7552 | 0.06515 | 0.023253 | -0.005985 | 0.11198 | 0.25179 | 0.13595 | -0.22367 | -0.18313 | 0.11678 | 0.54032 | 0.057463 | 0.2406 | 0.13868 | 0.35329 | 117.3483 | -3.2709 | 117.6372 | 117.566 | 0.21769 | -3.1311 | -3.2469 | 121.0717 | 121.0936 | 121.3082 | 117.2804 | -121.138 | 117.684 | 117.8238 | 117.708 | 117.5953 | -3.6065
1699.25 | 121.2341 | -118.4052 | 2.5909 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.066913 | -0.012493 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018463 | 0.033431 | 0.0078689 | -117.8924 | -0.30078 | -118.3844 | 2.6114 | 2.679 | 2.8983 | -118.6206 | 0.060571 | 0.014095 | -0.010564 | 0.11656 | 0.25179 | 0.14969 | -0.2191 | -0.21542 | 0.020505 | 0.51271 | 0.02072 | 0.23614 | 0.088088 | 0.30734 | 118.1861 | -2.4744 | 118.4657 | 118.3946 | 0.20853 | -2.3391 | -2.4413 | 121.0166 | 121.0842 | 121.3034 | 118.1044 | -121.2115 | 118.5217 | 118.6569 | 118.5548 | 118.4192 | -2.81
1701 | 121.257 | -118.6844 | 2.3346 | 1.4211e-13 | -0.024286 | 0.00092524 | 0.067126 | -0.012279 | 0.058898 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.033218 | 0.0076551 | -118.0389 | -0.30536 | -118.5309 | 2.4741 | 2.5462 | 2.7655 | -118.7763 | 0.06515 | 0.018674 | -0.001407 | 0.11656 | 0.25179 | 0.15884 | -0.21452 | -0.091868 | 0.1395 | 0.64544 | 0.15345 | 0.24532 | 0.21165 | 0.43091 | 118.4699 | -2.218 | 118.7495 | 118.683 | 0.21311 | -2.0828 | -2.1758 | 121.1585 | 121.2306 | 121.4499 | 118.379 | -121.1108 | 118.8009 | 118.9362 | 118.8432 | 118.7031 | -2.5491
1702.75 | 121.1746 | -118.2999 | 2.8015 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.067126 | -0.012279 | 0.059326 | 0.00030522 | -0.0025167 | 0.0053414 | 0.01825 | 0.033218 | 0.0078689 | -117.7276 | -0.28704 | -118.2242 | 2.7946 | 2.7981 | 3.0768 | -118.3825 | 0.060571 | 0.023253 | -0.001407 | 0.12114 | 0.23806 | 0.12679 | -0.2191 | -0.082601 | -0.006932 | 0.57225 | 0.075675 | 0.15828 | -0.003432 | 0.27534 | 118.0808 | -2.6804 | 118.3604 | 118.2985 | 0.21769 | -2.5635 | -2.6747 | 121.0944 | 121.0979 | 121.3767 | 118.0128 | -121.184 | 118.421 | 118.5379 | 118.4267 | 118.3231 | -3.0206
1704.5156 | 121.1197 | -118.7164 | 2.4765 | 1.4211e-13 | -0.024072 | 0.00092524 | 0.06734 | -0.012279 | 0.059753 | 0.015566 | -0.0027303 | 0.0053414 | 0.018891 | 0.033431 | 0.0078689 | -118.0344 | -0.29162 | -118.5355 | 2.4924 | 2.5096 | 2.7792 | -118.6938 | 0.06515 | 0.023253 | -0.005985 | 0.11198 | 0.24264 | 0.094744 | -0.21452 | 0.022597 | 0.015907 | 0.68206 | 0.18092 | 0.15832 | 0.033109 | 0.30274 | 118.5019 | -2.3645 | 118.7816 | 118.7104 | 0.20853 | -2.2339 | -2.3818 | 121.2088 | 121.226 | 121.4957 | 118.4248 | -121.1703 | 118.8284 | 118.9591 | 118.8112 | 118.7397 | -2.691
1706.2656 | 121.1243 | -118.9911 | 2.1973 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.06734 | -0.012279 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018463 | 0.033431 | 0.0076551 | -118.3365 | -0.30078 | -118.8377 | 2.204 | 2.2211 | 2.4862 | -119.0006 | 0.06515 | 0.018674 | -0.005985 | 0.11656 | 0.24721 | 0.14969 | -0.22367 | -0.009533 | 0.006704 | 0.65455 | 0.15341 | 0.16294 | 0.023871 | 0.28894 | 118.7674 | -2.0807 | 119.0562 | 118.9851 | 0.21769 | -1.9501 | -2.0476 | 121.1951 | 121.2122 | 121.4773 | 118.6903 | -121.1979 | 119.1076 | 119.2383 | 119.1408 | 119.0098 | -2.4209
1708.0156 | 121.257 | -118.8675 | 2.2614 | 1.4211e-13 | -0.023859 | 0.00049784 | 0.06734 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018036 | 0.033004 | 0.0078689 | -118.3594 | -0.2962 | -118.8651 | 2.1902 | 2.1982 | 2.4679 | -119.0235 | 0.055992 | 0.027831 | -0.001407 | 0.11656 | 0.24264 | 0.14969 | -0.22825 | -0.15602 | -0.071118 | 0.50806 | 0.002343 | 0.15837 | -0.06311 | 0.20654 | 118.6392 | -2.1448 | 118.9235 | 118.8661 | 0.22685 | -2.0187 | -2.1117 | 121.0577 | 121.0657 | 121.3354 | 118.5713 | -121.2849 | 118.984 | 119.1101 | 119.0172 | 118.8953 | -2.4896
1709.7031 | 121.2662 | -118.3044 | 2.8015 | 1.4211e-13 | -0.024072 | 0.00071164 | 0.067126 | -0.012279 | 0.059539 | -0.0073253 | -0.0027303 | 0.0051278 | 0.01825 | 0.033431 | 0.0076551 | -118.0161 | -0.26873 | -118.5264 | 2.5428 | 2.5554 | 2.8159 | -118.6709 | 0.060571 | 0.023253 | -0.010564 | 0.11198 | 0.24264 | 0.1039 | -0.22367 | -0.3665 | -0.25874 | 0.28839 | -0.22191 | 0.14458 | -0.24612 | 0.014356 | 118.0808 | -2.6895 | 118.365 | 118.2939 | 0.21311 | -2.5589 | -2.6976 | 120.8472 | 120.8598 | 121.1203 | 118.0357 | -121.4725 | 118.4164 | 118.5471 | 118.4083 | 118.3277 | -3.0252
1711.4531 | 121.1838 | -118.9911 | 2.1469 | 1.4211e-13 | -0.024286 | 0.00092524 | 0.06734 | -0.012066 | 0.059539 | 0.00030522 | -0.0025167 | 0.0051278 | 0.018463 | 0.033218 | 0.0076551 | -118.4098 | -0.28247 | -118.9064 | 2.1628 | 2.1845 | 2.445 | -119.0739 | 0.055992 | 0.023253 | -0.010564 | 0.11198 | 0.25179 | 0.14053 | -0.21452 | -0.082796 | 0.015852 | 0.58129 | 0.084734 | 0.16753 | 0.037594 | 0.29809 | 118.7766 | -2.0349 | 119.0471 | 118.9805 | 0.20395 | -1.8951 | -2.0064 | 121.1539 | 121.1756 | 121.4361 | 118.7086 | -121.2208 | 119.1031 | 119.2429 | 119.1316 | 119.0143 | -2.3614
1713.2031 | 121.2982 | -119.1513 | 2.0187 | 1.4211e-13 | -0.024286 | 0.00092524 | 0.067554 | -0.012493 | 0.059753 | 0.0079357 | -0.0029439 | 0.0051278 | 0.01825 | 0.033431 | 0.0078689 | -118.5655 | -0.28704 | -119.0758 | 2.0117 | 2.0242 | 2.2939 | -119.2341 | 0.06515 | 0.018674 | -0.001407 | 0.1074 | 0.24264 | 0.14969 | -0.22367 | -0.082841 | -0.00706 | 0.58584 | 0.075555 | 0.1584 | 0.005506 | 0.27517 | 118.9276 | -1.9113 | 119.2165 | 119.1499 | 0.22227 | -1.7761 | -1.8691 | 121.163 | 121.1756 | 121.4452 | 118.8643 | -121.2529 | 119.2587 | 119.3939 | 119.301 | 119.17 | -2.2424
1714.9375 | 121.2524 | -119.4351 | 1.7441 | 1.4211e-13 | -0.024286 | 0.00071164 | 0.067554 | -0.012279 | 0.059112 | 0.0079357 | -0.0025167 | 0.0053414 | 0.01825 | 0.033431 | 0.0080825 | -118.7898 | -0.28704 | -119.2909 | 1.8011 | 1.8136 | 2.0879 | -119.4494 | 0.06515 | 0.018674 | 0.003172 | 0.11656 | 0.24721 | 0.058115 | -0.2191 | -0.014237 | 0.056992 | 0.64532 | 0.14419 | 0.15843 | 0.069533 | 0.34379 | 119.216 | -1.6275 | 119.5003 | 119.4383 | 0.22227 | -1.4969 | -1.686 | 121.2362 | 121.2487 | 121.523 | 119.1481 | -121.1934 | 119.5517 | 119.6823 | 119.4932 | 119.4538 | -1.9632
1716.625 | 121.2936 | -119.371 | 1.7624 | 1.4211e-13 | -0.024286 | 0.00049784 | 0.06734 | -0.012066 | 0.059753 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018463 | 0.033431 | 0.0078689 | -118.7806 | -0.2962 | -119.2909 | 1.8102 | 1.8274 | 2.0421 | -119.4539 | 0.060571 | 0.023253 | -0.001407 | 0.12114 | 0.24264 | 0.14969 | -0.22367 | -0.082903 | 0.047839 | 0.59039 | 0.080102 | 0.163 | 0.06496 | 0.2797 | 119.1474 | -1.6413 | 119.4316 | 119.3696 | 0.22227 | -1.5198 | -1.6127 | 121.1813 | 121.1984 | 121.4131 | 119.0748 | -121.2163 | 119.4922 | 119.6137 | 119.5207 | 119.3943 | -1.9861
1718.375 | 121.1975 | -119.5541 | 1.68 | 1.4211e-13 | -0.024286 | 0.00049784 | 0.06734 | -0.012066 | 0.059539 | 0.00030522 | -0.0029439 | 0.0053414 | 0.01825 | 0.033218 | 0.0080825 | -118.9363 | -0.2962 | -119.442 | 1.6637 | 1.6762 | 1.8956 | -119.605 | 0.060571 | 0.023253 | -0.001407 | 0.12114 | 0.25637 | 0.12679 | -0.21452 | -0.050902 | -0.016273 | 0.61783 | 0.11212 | 0.16303 | -0.003748 | 0.21558 | 119.3396 | -1.5589 | 119.6147 | 119.5527 | 0.21311 | -1.4236 | -1.5532 | 121.2179 | 121.2304 | 121.4497 | 119.2579 | -121.285 | 119.6753 | 119.8105 | 119.6809 | 119.5774 | -1.8945
1720.0625 | 121.2708 | -119.6182 | 1.5472 | 1.4211e-13 | -0.024286 | 0.0011388 | 0.06734 | -0.012279 | 0.059326 | -0.0073253 | -0.0027303 | 0.0053414 | 0.01825 | 0.033004 | 0.0078689 | -119.2202 | -0.30078 | -119.7259 | 1.3982 | 1.4015 | 1.6254 | -119.8844 | 0.06515 | 0.023253 | -0.005985 | 0.11656 | 0.25179 | 0.12679 | -0.22367 | -0.26613 | -0.14907 | 0.39805 | -0.10764 | 0.15849 | -0.14573 | 0.078192 | 119.3946 | -1.4307 | 119.6834 | 119.6122 | 0.21769 | -1.2954 | -1.4204 | 121.0164 | 121.0197 | 121.2437 | 119.3174 | -121.4316 | 119.7348 | 119.87 | 119.745 | 119.6415 | -1.7709
1721.7969 | 121.3257 | -119.7556 | 1.3733 | 1.4211e-13 | -0.023859 | 0.00028424 | 0.067554 | -0.012493 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.033431 | 0.0080825 | -119.211 | -0.30078 | -119.7259 | 1.4073 | 1.4107 | 1.6437 | -119.8844 | 0.060571 | 0.023253 | -0.005985 | 0.11198 | 0.24721 | 0.094744 | -0.2191 | -0.1288 | 0.034039 | 0.54454 | 0.029687 | 0.15849 | 0.037377 | 0.27046 | 119.5365 | -1.2613 | 119.8161 | 119.7496 | 0.21311 | -1.1261 | -1.2785 | 121.1629 | 121.1662 | 121.3993 | 119.4548 | -121.2576 | 119.8675 | 120.0028 | 119.8503 | 119.7788 | -1.5924
1723.5469 | 121.2662 | -119.5129 | 1.7075 | 1.4211e-13 | -0.0245 | 0.00071164 | 0.06734 | -0.012493 | 0.059326 | 0.015566 | -0.0025167 | 0.0053414 | 0.01825 | 0.033431 | 0.0074415 | -118.8402 | -0.30078 | -119.3596 | 1.7782 | 1.7953 | 2.0146 | -119.518 | 0.06515 | 0.027831 | -0.005985 | 0.11198 | 0.24721 | 0.14053 | -0.22825 | -0.005102 | 0.070722 | 0.67277 | 0.15333 | 0.15844 | 0.087839 | 0.30716 | 119.2847 | -1.5955 | 119.5781 | 119.507 | 0.22227 | -1.4602 | -1.5669 | 121.2911 | 121.3082 | 121.5276 | 119.2122 | -121.2255 | 119.6249 | 119.7602 | 119.6535 | 119.5408 | -1.9357
1725.2969 | 121.2708 | -119.6732 | 1.5472 | 1.4211e-13 | -0.024286 | 0.00071164 | 0.067767 | -0.012066 | 0.059326 | 0.015566 | -0.0027303 | 0.0051278 | 0.018036 | 0.033431 | 0.0076551 | -119.0874 | -0.2962 | -119.5794 | 1.5493 | 1.5664 | 1.7857 | -119.7516 | 0.06515 | 0.018674 | -0.005985 | 0.11198 | 0.24264 | 0.15427 | -0.22367 | -0.078409 | 0.00202 | 0.58576 | 0.093795 | 0.1722 | 0.01911 | 0.23844 | 119.4495 | -1.4353 | 119.7383 | 119.6672 | 0.21769 | -1.3046 | -1.393 | 121.2224 | 121.2395 | 121.4588 | 119.377 | -121.2988 | 119.7851 | 119.9158 | 119.8274 | 119.6918 | -1.7709
1727.0469 | 121.225 | -119.7235 | 1.5472 | 1.4211e-13 | -0.024286 | 0.00049784 | 0.067126 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.033218 | 0.0078689 | -119.1194 | -0.30078 | -119.6251 | 1.5172 | 1.5389 | 1.7536 | -119.7974 | 0.055992 | 0.018674 | -0.010564 | 0.11198 | 0.25179 | 0.15427 | -0.22825 | -0.073844 | -0.030029 | 0.60406 | 0.098366 | 0.17221 | -0.008363 | 0.20639 | 119.4953 | -1.4353 | 119.7795 | 119.7129 | 0.21769 | -1.2954 | -1.393 | 121.2407 | 121.2624 | 121.4771 | 119.4227 | -121.3446 | 119.8355 | 119.9753 | 119.8778 | 119.7422 | -1.7755
1728.7344 | 121.344 | -119.8608 | 1.3184 | 1.4211e-13 | -0.023859 | 0.00071164 | 0.067126 | -0.012066 | 0.059539 | 0.015566 | -0.0027303 | 0.0051278 | 0.018036 | 0.033218 | 0.0078689 | -119.3163 | -0.30994 | -119.822 | 1.3387 | 1.3466 | 1.5705 | -119.9805 | 0.06515 | 0.027831 | -0.005985 | 0.11656 | 0.24721 | 0.14511 | -0.2191 | -0.11967 | 0.020296 | 0.54452 | 0.038829 | 0.1585 | 0.028204 | 0.25213 | 119.6417 | -1.2018 | 119.926 | 119.8549 | 0.21311 | -1.0711 | -1.1733 | 121.1995 | 121.2074 | 121.4313 | 119.5509 | -121.2989 | 119.9774 | 120.1081 | 120.0059 | 119.8887 | -1.5375
1730.4844 | 121.2799 | -119.9295 | 1.3092 | 1.4211e-13 | -0.024072 | 0.00049784 | 0.067554 | -0.011852 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.01825 | 0.033218 | 0.0076551 | -119.3804 | -0.30536 | -119.8769 | 1.2837 | 1.2916 | 1.5064 | -120.0446 | 0.060571 | 0.018674 | -0.005985 | 0.12571 | 0.25637 | 0.14053 | -0.21452 | -0.11511 | -0.02549 | 0.54909 | 0.052554 | 0.16767 | -0.017588 | 0.19719 | 119.715 | -1.1835 | 119.9901 | 119.9235 | 0.20853 | -1.0528 | -1.1687 | 121.2132 | 121.2211 | 121.4359 | 119.6241 | -121.3538 | 120.0552 | 120.1859 | 120.07 | 119.9482 | -1.5237
1732.2344 | 121.2341 | -120.0119 | 1.2863 | 1.4211e-13 | -0.0245 | 0.00092524 | 0.06734 | -0.012066 | 0.059753 | -0.0073253 | -0.0027303 | 0.0053414 | 0.018463 | 0.033431 | 0.0078689 | -119.3942 | -0.30994 | -119.8953 | 1.2746 | 1.2733 | 1.511 | -120.0675 | 0.055992 | 0.023253 | -0.010564 | 0.11656 | 0.24264 | 0.14511 | -0.22367 | -0.05561 | -0.011759 | 0.61775 | 0.11664 | 0.17225 | -0.013016 | 0.22465 | 119.7882 | -1.1698 | 120.0679 | 120.0013 | 0.21311 | -1.0437 | -1.1412 | 121.2865 | 121.2852 | 121.5229 | 119.702 | -121.3538 | 120.1285 | 120.2545 | 120.157 | 120.0352 | -1.51
1734 | 121.2341 | -119.9982 | 1.2726 | 1.4211e-13 | -0.024286 | 0.00071164 | 0.06734 | -0.012493 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018036 | 0.033218 | 0.0078689 | -119.4033 | -0.3191 | -119.9136 | 1.2517 | 1.2687 | 1.4789 | -120.0858 | 0.060571 | 0.023253 | -0.001407 | 0.12114 | 0.24721 | 0.13595 | -0.22367 | -0.087658 | -0.020918 | 0.59486 | 0.084592 | 0.17225 | -0.003862 | 0.20633 | 119.7745 | -1.1514 | 120.0587 | 119.9968 | 0.22227 | -1.0254 | -1.1366 | 121.2498 | 121.2669 | 121.4771 | 119.6791 | -121.3584 | 120.1193 | 120.2454 | 120.1341 | 120.0214 | -1.4963
1735.6875 | 121.3943 | -119.8883 | 1.3458 | 1.4211e-13 | -0.024927 | 0.00092524 | 0.06734 | -0.012493 | 0.059753 | 0.0079357 | -0.0025167 | 0.0053414 | 0.018463 | 0.033431 | 0.0076551 | -119.3163 | -0.3191 | -119.822 | 1.3615 | 1.374 | 1.5934 | -119.9897 | 0.060571 | 0.018674 | -0.001407 | 0.11198 | 0.25179 | 0.12222 | -0.2191 | -0.10136 | 0.015722 | 0.57199 | 0.066295 | 0.16766 | 0.028211 | 0.24756 | 119.6692 | -1.2338 | 119.9489 | 119.8869 | 0.21769 | -1.094 | -1.2236 | 121.2499 | 121.2623 | 121.4817 | 119.5692 | -121.3355 | 120.0003 | 120.1401 | 120.0105 | 119.907 | -1.5649
1737.4219 | 121.2616 | -119.9799 | 1.3458 | 1.4211e-13 | -0.024286 | 0.00092524 | 0.067554 | -0.012279 | 0.059753 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018463 | 0.033431 | 0.0078689 | -119.3621 | -0.32367 | -119.8541 | 1.3249 | 1.342 | 1.5522 | -120.0217 | 0.055992 | 0.018674 | -0.001407 | 0.1074 | 0.25179 | 0.14053 | -0.21452 | -0.041864 | -0.020905 | 0.61776 | 0.1258 | 0.16766 | -0.003841 | 0.20635 | 119.7653 | -1.2384 | 120.0358 | 119.9785 | 0.21311 | -1.094 | -1.2053 | 121.3048 | 121.3218 | 121.532 | 119.6562 | -121.3675 | 120.0873 | 120.2317 | 120.1204 | 119.9985 | -1.5603
1739.1094 | 121.3852 | -119.8883 | 1.3367 | 1.4211e-13 | -0.024286 | 0.00071164 | 0.067554 | -0.012066 | 0.059326 | 0.0079357 | -0.0029439 | 0.0053414 | 0.018677 | 0.033645 | 0.0076551 | -119.3255 | -0.32367 | -119.822 | 1.357 | 1.3695 | 1.5934 | -119.9942 | 0.055992 | 0.018674 | -0.001407 | 0.11198 | 0.24721 | 0.07643 | -0.21452 | -0.10594 | 0.020298 | 0.56283 | 0.066295 | 0.17224 | 0.032787 | 0.25671 | 119.6738 | -1.2247 | 119.9443 | 119.8869 | 0.21311 | -1.0895 | -1.2602 | 121.2453 | 121.2578 | 121.4817 | 119.5646 | -121.3309 | 120.0003 | 120.1355 | 119.9647 | 119.907 | -1.5512
1740.7969 | 121.2753 | -119.902 | 1.4053 | 1.4211e-13 | -0.0245 | 0.00071164 | 0.06734 | -0.012279 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.033645 | 0.0076551 | -119.4033 | -0.3191 | -119.909 | 1.2929 | 1.2962 | 1.5155 | -120.0721 | 0.055992 | 0.023253 | -0.005985 | 0.11656 | 0.25179 | 0.11306 | -0.21452 | -0.17005 | -0.11246 | 0.49873 | -0.006959 | 0.16309 | -0.10914 | 0.11021 | 119.6875 | -1.2888 | 119.958 | 119.8961 | 0.20853 | -1.1535 | -1.2923 | 121.1949 | 121.1982 | 121.4176 | 119.5829 | -121.4774 | 120.0186 | 120.1538 | 120.0151 | 119.9253 | -1.6199
1742.5469 | 121.3486 | -120.0394 | 1.2085 | 1.4211e-13 | -0.0245 | 0.00092524 | 0.067554 | -0.012493 | 0.059326 | -0.0073253 | -0.0025167 | 0.0051278 | 0.01825 | 0.033218 | 0.0076551 | -119.4766 | -0.32825 | -119.9823 | 1.2196 | 1.2367 | 1.4514 | -120.1408 | 0.055992 | 0.023253 | -0.005985 | 0.11198 | 0.24721 | 0.094744 | -0.21452 | -0.10141 | 0.011121 | 0.56281 | 0.057117 | 0.15852 | 0.028173 | 0.24295 | 119.8249 | -1.0965 | 120.0954 | 120.0334 | 0.20853 | -0.96128 | -1.1138 | 121.259 | 121.276 | 121.4908 | 119.7111 | -121.3493 | 120.1513 | 120.2866 | 120.1341 | 120.0626 | -1.423
1744.2969 | 121.2936 | -120.0714 | 1.2268 | 1.4211e-13 | -0.024286 | 0.00092524 | 0.06734 | -0.012279 | 0.059539 | 0.015566 | -0.0027303 | 0.0051278 | 0.018463 | 0.033218 | 0.0076551 | -119.4811 | -0.32367 | -119.9914 | 1.2059 | 1.2275 | 1.4423 | -120.1545 | 0.06515 | 0.018674 | -0.010564 | 0.12114 | 0.24721 | 0.13595 | -0.20536 | -0.0831 | -0.020926 | 0.59027 | 0.080004 | 0.1631 | 0.000704 | 0.21548 | 119.8661 | -1.1057 | 120.1366 | 120.0608 | 0.19479 | -0.97959 | -1.0909 | 121.2773 | 121.2989 | 121.5137 | 119.7477 | -121.3813 | 120.1925 | 120.3186 | 120.2074 | 120.0901 | -1.4322
1745.9844 | 121.3943 | -120.0989 | 1.1581 | 1.4211e-13 | -0.024286 | 0.00071164 | 0.067554 | -0.011638 | 0.059112 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.033645 | 0.0074415 | -119.5315 | -0.32825 | -120.0372 | 1.1693 | 1.1817 | 1.3965 | -120.2049 | 0.06515 | 0.023253 | -0.005985 | 0.11656 | 0.25179 | 0.14969 | -0.22367 | -0.106 | 0.011112 | 0.56737 | 0.061687 | 0.16769 | 0.02358 | 0.23836 | 119.8752 | -1.0416 | 120.164 | 120.0929 | 0.21769 | -0.90635 | -1.0085 | 121.2681 | 121.2806 | 121.4954 | 119.7706 | -121.363 | 120.2154 | 120.3507 | 120.2486 | 120.1221 | -1.3818
1747.7344 | 121.344 | -120.1721 | 1.1353 | 1.4211e-13 | -0.024286 | 0.00049784 | 0.067767 | -0.012279 | 0.059539 | 0.015566 | -0.0025167 | 0.0051278 | 0.018463 | 0.033218 | 0.0076551 | -119.5819 | -0.32825 | -120.083 | 1.128 | 1.1359 | 1.3553 | -120.2598 | 0.055992 | 0.023253 | -0.010564 | 0.11656 | 0.23806 | 0.12679 | -0.2191 | -0.087707 | -0.007205 | 0.59025 | 0.089146 | 0.17685 | 0.000678 | 0.22004 | 119.953 | -1.0187 | 120.2281 | 120.1616 | 0.20853 | -0.8972 | -1.0085 | 121.3002 | 121.3081 | 121.5274 | 119.8439 | -121.3951 | 120.2887 | 120.4102 | 120.2989 | 120.1954 | -1.3543
1749.5 | 121.3715 | -120.1584 | 1.1261 | 1.4211e-13 | -0.0245 | 0.00049784 | 0.06734 | -0.012066 | 0.059326 | 0.00030522 | -0.0029439 | 0.0053414 | 0.018036 | 0.033431 | 0.0078689 | -119.591 | -0.33741 | -120.1013 | 1.1235 | 1.1405 | 1.3599 | -120.2644 | 0.055992 | 0.018674 | -0.001407 | 0.11656 | 0.24264 | 0.13595 | -0.22367 | -0.10602 | -0.002629 | 0.56736 | 0.0571 | 0.16312 | 0.014412 | 0.23378 | 119.9347 | -1.0095 | 120.2144 | 120.157 | 0.22227 | -0.88346 | -0.99015 | 121.2819 | 121.2989 | 121.5183 | 119.821 | -121.3905 | 120.2749 | 120.401 | 120.2943 | 120.1771 | -1.3498
1751.1875 | 121.431 | -120.1538 | 1.1032 | 1.4211e-13 | -0.0245 | 0.00092524 | 0.067981 | -0.011852 | 0.059753 | 0.00030522 | -0.0023031 | 0.0053414 | 0.018463 | 0.033218 | 0.0076551 | -119.6093 | -0.33741 | -120.1104 | 1.1189 | 1.1314 | 1.3416 | -120.2827 | 0.060571 | 0.023253 | 0.003172 | 0.12114 | 0.24264 | 0.13137 | -0.2191 | -0.12891 | 0.015682 | 0.54447 | 0.043366 | 0.17228 | 0.028143 | 0.23835 | 119.9347 | -0.98207 | 120.2144 | 120.157 | 0.22227 | -0.86057 | -0.97184 | 121.2727 | 121.2852 | 121.4954 | 119.8164 | -121.3859 | 120.2749 | 120.3964 | 120.2852 | 120.1771 | -1.3223
1752.9375 | 121.376 | -120.1813 | 1.1444 | 1.4211e-13 | -0.0245 | 0.00071164 | 0.06734 | -0.012066 | 0.059326 | 0.0079357 | -0.0031575 | 0.0051278 | 0.018463 | 0.033431 | 0.0074415 | -119.6002 | -0.33741 | -120.1059 | 1.1326 | 1.1542 | 1.369 | -120.2736 | 0.06515 | 0.023253 | -0.005985 | 0.11198 | 0.23806 | 0.14511 | -0.20994 | -0.092289 | -0.011782 | 0.5811 | 0.07541 | 0.1677 | 0.009839 | 0.22462 | 119.9713 | -1.0324 | 120.2464 | 120.1753 | 0.20395 | -0.90635 | -0.9993 | 121.3139 | 121.3355 | 121.5503 | 119.8439 | -121.418 | 120.2933 | 120.4193 | 120.3264 | 120.2045 | -1.3543
1754.6094 | 121.3348 | -120.3827 | 0.95673 | 1.4211e-13 | -0.0245 | 0.0011388 | 0.067554 | -0.012066 | 0.059539 | 0.00030522 | -0.0031575 | 0.0049142 | 0.01825 | 0.033218 | 0.0078689 | -119.7879 | -0.34657 | -120.289 | 0.94034 | 0.95735 | 1.1767 | -120.4705 | 0.069728 | 0.023253 | -0.005985 | 0.1074 | 0.23806 | 0.13137 | -0.22367 | -0.087767 | -0.016391 | 0.5948 | 0.093694 | 0.18146 | 0.000628 | 0.22 | 120.159 | -0.84932 | 120.4524 | 120.3767 | 0.21769 | -0.71867 | -0.82535 | 121.323 | 121.34 | 121.5594 | 120.0361 | -121.4272 | 120.4901 | 120.6207 | 120.5141 | 120.4059 | -1.1804
1756.3594 | 121.4264 | -120.3918 | 0.91095 | 1.4211e-13 | -0.024713 | 0.00092524 | 0.067554 | -0.012066 | 0.059326 | 0.00030522 | -0.0031575 | 0.0049142 | 0.018463 | 0.033645 | 0.0076551 | -119.8199 | -0.35115 | -120.3348 | 0.91287 | 0.9253 | 1.1447 | -120.4979 | 0.055992 | 0.023253 | -0.001407 | 0.11198 | 0.23806 | 0.14053 | -0.2191 | -0.10608 | 0.001915 | 0.57191 | 0.057067 | 0.16315 | 0.014352 | 0.23373 | 120.1728 | -0.79897 | 120.4478 | 120.3904 | 0.21769 | -0.67289 | -0.77042 | 121.3047 | 121.3171 | 121.5365 | 120.0407 | -121.4089 | 120.5038 | 120.6299 | 120.5324 | 120.4151 | -1.13
1758.1094 | 121.4401 | -120.401 | 0.88348 | 1.4211e-13 | -0.024713 | 0.00092524 | 0.067767 | -0.012279 | 0.059539 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018677 | 0.033645 | 0.0076551 | -119.8337 | -0.34199 | -120.3485 | 0.90371 | 0.91614 | 1.1309 | -120.5117 | 0.055992 | 0.014095 | -0.005985 | 0.11656 | 0.23348 | 0.15427 | -0.2191 | -0.11067 | 0.020224 | 0.56732 | 0.052488 | 0.16315 | 0.03266 | 0.24746 | 120.1819 | -0.76693 | 120.457 | 120.395 | 0.21311 | -0.65001 | -0.72922 | 121.3047 | 121.3171 | 121.5319 | 120.059 | -121.3952 | 120.5176 | 120.6345 | 120.5553 | 120.4151 | -1.1026
1759.7969 | 121.3211 | -120.4514 | 0.92468 | 1.4211e-13 | -0.024286 | 0.00071164 | 0.067554 | -0.012493 | 0.059539 | 0.0079357 | -0.0025167 | 0.0051278 | 0.01825 | 0.033645 | 0.0072279 | -119.852 | -0.35115 | -120.3622 | 0.89455 | 0.90241 | 1.1264 | -120.53 | 0.069728 | 0.023253 | -0.005985 | 0.11198 | 0.23806 | 0.14969 | -0.21452 | -0.078628 | -0.030132 | 0.59937 | 0.089107 | 0.16774 | -0.022276 | 0.20168 | 120.2368 | -0.8127 | 120.5211 | 120.4454 | 0.20853 | -0.68663 | -0.775 | 121.3459 | 121.3538 | 121.5777 | 120.1002 | -121.4547 | 120.5633 | 120.6894 | 120.601 | 120.4746 | -1.1392
1761.5625 | 121.3806 | -120.4742 | 0.86975 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067767 | -0.011852 | 0.059112 | 0.00030522 | -0.0023031 | 0.0051278 | 0.018463 | 0.033645 | 0.0076551 | -119.884 | -0.35115 | -120.3897 | 0.87166 | 0.87951 | 1.1035 | -120.5529 | 0.060571 | 0.018674 | -0.001407 | 0.11198 | 0.24721 | 0.11764 | -0.2191 | -0.078635 | 0.001908 | 0.5902 | 0.084525 | 0.16316 | 0.009761 | 0.23372 | 120.2551 | -0.75777 | 120.5348 | 120.4728 | 0.21769 | -0.62254 | -0.75211 | 121.3459 | 121.3538 | 121.5777 | 120.1231 | -121.4226 | 120.5862 | 120.7215 | 120.5919 | 120.4929 | -1.0888
1763.3281 | 121.4584 | -120.4971 | 0.82855 | 1.4211e-13 | -0.024713 | 0.00092524 | 0.067767 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.033431 | 0.0074415 | -119.9161 | -0.35572 | -120.4263 | 0.83961 | 0.84746 | 1.076 | -120.6032 | 0.060571 | 0.018674 | -0.005985 | 0.11656 | 0.24721 | 0.13137 | -0.2191 | -0.10612 | 0.011058 | 0.58104 | 0.070787 | 0.1769 | 0.018908 | 0.24745 | 120.278 | -0.71199 | 120.5577 | 120.4911 | 0.21311 | -0.58134 | -0.69718 | 121.3367 | 121.3446 | 121.5731 | 120.1414 | -121.4318 | 120.6137 | 120.7443 | 120.6285 | 120.5158 | -1.0476
1765.0156 | 121.463 | -120.4971 | 0.81024 | 1.4211e-13 | -0.0245 | 0.00071164 | 0.067767 | -0.011852 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.033431 | 0.0078689 | -119.9527 | -0.35572 | -120.4492 | 0.81672 | 0.82456 | 1.0531 | -120.6261 | 0.060571 | 0.023253 | -0.005985 | 0.11198 | 0.24264 | 0.15427 | -0.2191 | -0.12901 | 0.006476 | 0.54442 | 0.047895 | 0.1769 | 0.014323 | 0.24287 | 120.278 | -0.69826 | 120.5577 | 120.4911 | 0.21311 | -0.56761 | -0.65598 | 121.3138 | 121.3217 | 121.5502 | 120.1414 | -121.4364 | 120.6091 | 120.7398 | 120.6514 | 120.5204 | -1.0293
1766.75 | 121.344 | -120.5795 | 0.81024 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067554 | -0.012066 | 0.059326 | 0.00030522 | -0.0025167 | 0.0051278 | 0.01825 | 0.033645 | 0.0074415 | -119.9802 | -0.35572 | -120.4859 | 0.78009 | 0.79709 | 1.0211 | -120.6628 | 0.06515 | 0.014095 | -0.005985 | 0.11656 | 0.24721 | 0.099323 | -0.21452 | -0.083243 | -0.030151 | 0.59934 | 0.093667 | 0.17691 | -0.01315 | 0.21082 | 120.365 | -0.69368 | 120.6447 | 120.5735 | 0.20853 | -0.56303 | -0.71092 | 121.3596 | 121.3766 | 121.6006 | 120.2238 | -121.473 | 120.6961 | 120.8267 | 120.6789 | 120.5936 | -1.0248
1768.5 | 121.4676 | -120.5383 | 0.77362 | 1.4211e-13 | -0.024286 | 0.0011388 | 0.067767 | -0.011852 | 0.059326 | -0.0073253 | -0.0029439 | 0.0051278 | 0.01825 | 0.033645 | 0.0076551 | -119.9756 | -0.35572 | -120.4904 | 0.78925 | 0.80167 | 1.0256 | -120.6582 | 0.060571 | 0.014095 | -0.001407 | 0.11198 | 0.23806 | 0.14511 | -0.2191 | -0.11986 | 0.015627 | 0.56272 | 0.04789 | 0.16775 | 0.02805 | 0.25201 | 120.3192 | -0.66164 | 120.5989 | 120.5369 | 0.21769 | -0.53556 | -0.62851 | 121.3276 | 121.34 | 121.564 | 120.1826 | -121.4318 | 120.6503 | 120.7764 | 120.6834 | 120.5524 | -0.99272
1770.1875 | 121.3577 | -120.5978 | 0.80566 | 1.4211e-13 | -0.0245 | 0.00092524 | 0.067981 | -0.012066 | 0.059326 | 0.015566 | -0.0029439 | 0.0049142 | 0.01825 | 0.033859 | 0.0076551 | -119.9939 | -0.35572 | -120.495 | 0.78009 | 0.80167 | 1.0165 | -120.6674 | 0.069728 | 0.018674 | -0.010564 | 0.11656 | 0.25179 | 0.13137 | -0.2191 | -0.069512 | -0.025573 | 0.60392 | 0.10282 | 0.17233 | -0.003993 | 0.21081 | 120.3787 | -0.68911 | 120.6676 | 120.5873 | 0.20853 | -0.55387 | -0.67429 | 121.3779 | 121.3995 | 121.6143 | 120.2421 | -121.473 | 120.7144 | 120.8496 | 120.7292 | 120.6165 | -1.0248
1771.9375 | 121.4447 | -117.8787 | 3.392 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0029439 | 0.0053414 | 0.01825 | 0.033431 | 0.0076551 | -117.3613 | -0.39235 | -117.8442 | 3.4676 | 3.4849 | 3.695 | -118.1032 | 0.060571 | 0.014095 | -0.005985 | 0.12571 | 0.24264 | 0.1039 | -0.21452 | -0.22443 | 0.075576 | 0.51738 | 0.034529 | 0.25896 | 0.092892 | 0.30293 | 117.6642 | -3.2663 | 117.9393 | 117.8727 | 0.20853 | -3.1494 | -3.2881 | 121.3463 | 121.3636 | 121.5737 | 117.4864 | -121.4952 | 118.0044 | 118.1214 | 117.9826 | 117.8928 | -3.6065
1773.6875 | 121.5363 | -117.7185 | 3.5751 | 1.4211e-13 | -0.024713 | 0.0011388 | 0.067767 | -0.011638 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.018036 | 0.033218 | 0.0076551 | -117.3018 | -0.37862 | -117.7893 | 3.5317 | 3.5444 | 3.7591 | -118.0345 | 0.060571 | 0.023253 | -0.001407 | 0.11198 | 0.23348 | 0.12679 | -0.22367 | -0.31596 | -0.043432 | 0.41668 | -0.070749 | 0.24521 | -0.030687 | 0.18393 | 117.4948 | -3.4632 | 117.7791 | 117.7171 | 0.22227 | -3.3417 | -3.4483 | 121.2502 | 121.263 | 121.4776 | 117.3399 | -121.6096 | 117.8305 | 117.952 | 117.8453 | 117.7418 | -3.7988
1775.4219 | 121.4081 | -117.8696 | 3.4836 | 1.4211e-13 | -0.0245 | 0.00071164 | 0.067767 | -0.012066 | 0.059112 | 0.0079357 | -0.0025167 | 0.0051278 | 0.01825 | 0.033645 | 0.0078689 | -117.2927 | -0.3603 | -117.7847 | 3.4905 | 3.5582 | 3.7728 | -117.9795 | 0.060571 | 0.027831 | 0.003172 | 0.11656 | 0.24721 | 0.062694 | -0.21452 | -0.10995 | 0.006915 | 0.5769 | 0.084892 | 0.19485 | 0.074601 | 0.28922 | 117.6551 | -3.367 | 117.9301 | 117.8727 | 0.21769 | -3.2364 | -3.4209 | 121.3601 | 121.4278 | 121.6424 | 117.5093 | -121.4631 | 117.9861 | 118.1168 | 117.9323 | 117.8974 | -3.6981
1777.1719 | 121.431 | -118.3456 | 3.0716 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067981 | -0.011852 | 0.059539 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.033645 | 0.0078689 | -117.7368 | -0.36488 | -118.2242 | 3.0556 | 3.1323 | 3.3378 | -118.3962 | 0.055992 | 0.018674 | -0.010564 | 0.1074 | 0.24264 | 0.14511 | -0.21452 | -0.050562 | -0.016044 | 0.60887 | 0.12145 | 0.17201 | 0.060749 | 0.26624 | 118.1311 | -2.9642 | 118.4016 | 118.3351 | 0.20395 | -2.829 | -2.9265 | 121.4012 | 121.478 | 121.6835 | 117.9808 | -121.4678 | 118.453 | 118.5883 | 118.4908 | 118.3643 | -3.2861
1778.8594 | 121.4355 | -119.0369 | 2.3621 | 1.4211e-13 | -0.024713 | 0.00092524 | 0.067767 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.033431 | 0.0076551 | -118.4556 | -0.37862 | -118.9567 | 2.3413 | 2.3493 | 2.6236 | -119.1197 | 0.060571 | 0.018674 | -0.001407 | 0.11656 | 0.24264 | 0.14511 | -0.2191 | -0.082809 | -0.020739 | 0.58128 | 0.080149 | 0.16296 | -0.012714 | 0.26151 | 118.8178 | -2.2455 | 119.0974 | 119.0355 | 0.21769 | -2.1194 | -2.217 | 121.3782 | 121.3862 | 121.6604 | 118.6582 | -121.4817 | 119.1534 | 119.2795 | 119.182 | 119.0555 | -2.5812
1780.5938 | 121.2204 | -45.4971 | 75.8423 | 1.4211e-13 | -0.0245 | 0.00092524 | 0.068195 | -0.011852 | 0.059112 | 0.015566 | -0.0031575 | 0.0049142 | 0.01825 | 0.033431 | 0.0078689 | -87.5286 | 2.3411 | -88.3646 | 32.8563 | 33.5501 | 32.9156 | -88.0929 | 0.060571 | 0.014095 | -0.019721 | 0.1074 | 0.2289 | 0.085587 | -0.22367 | -42.5958 | -42.986 | -42.0314 | -42.8675 | -0.27176 | -42.2921 | -42.9267 | 45.2735 | -75.7349 | 45.5577 | 45.4774 | 0.20395 | -75.6134 | -75.7567 | 78.3534 | 79.0473 | 78.4127 | 47.8382 | -163.9352 | 45.6045 | 45.726 | 45.5827 | 45.5112 | -76.066
1782.3281 | 121.5729 | -118.6569 | 2.5955 | 1.4211e-13 | -0.0245 | 0.0011388 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0025167 | 0.0049142 | 0.018463 | 0.033645 | 0.0078689 | -118.1717 | -0.39693 | -118.6683 | 2.6893 | 2.7065 | 2.912 | -118.9136 | 0.055992 | 0.014095 | -0.005985 | 0.12114 | 0.24264 | 0.168 | -0.2191 | -0.2567 | 0.093759 | 0.4852 | -0.011363 | 0.24534 | 0.11098 | 0.3165 | 118.4378 | -2.4744 | 118.7129 | 118.6509 | 0.21311 | -2.3529 | -2.4275 | 121.3462 | 121.3634 | 121.5689 | 118.26 | -121.5091 | 118.7781 | 118.8996 | 118.8249 | 118.671 | -2.8146
1784.0312 | 121.4996 | -118.2312 | 3.1082 | 1.4211e-13 | -0.0245 | 0.00071164 | 0.067767 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018036 | 0.033645 | 0.0078689 | -117.6498 | -0.37404 | -118.1418 | 3.1609 | 3.2285 | 3.4386 | -118.3779 | 0.06515 | 0.023253 | -0.001407 | 0.11198 | 0.23806 | 0.094744 | -0.21452 | -0.14669 | 0.052638 | 0.58142 | 0.089419 | 0.23611 | 0.12029 | 0.33034 | 118.0167 | -2.9962 | 118.2964 | 118.2298 | 0.21311 | -2.8702 | -3.0135 | 121.3921 | 121.4597 | 121.6698 | 117.8572 | -121.4861 | 118.3432 | 118.4693 | 118.3259 | 118.2545 | -3.3227
1785.7188 | 121.5454 | -118.4052 | 2.916 | 1.4211e-13 | -0.024713 | 0.00092524 | 0.067981 | -0.011638 | 0.059539 | 0.0079357 | -0.0029439 | 0.0051278 | 0.01825 | 0.033859 | 0.0076551 | -117.8558 | -0.37862 | -118.357 | 2.9502 | 3.0316 | 3.2325 | -118.5153 | 0.051413 | 0.027831 | -0.001407 | 0.12114 | 0.24721 | 0.11764 | -0.2191 | -0.1101 | 0.034292 | 0.54934 | 0.04819 | 0.15829 | 0.11565 | 0.31657 | 118.1861 | -2.7948 | 118.4566 | 118.4037 | 0.21769 | -2.6687 | -2.7983 | 121.3554 | 121.4368 | 121.6377 | 118.0265 | -121.4312 | 118.5263 | 118.6524 | 118.5228 | 118.433 | -3.135
1787.4688 | 121.4493 | -118.6615 | 2.7832 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067767 | -0.011852 | 0.059112 | 0.0079357 | -0.0029439 | 0.0051278 | 0.018677 | 0.033645 | 0.0076551 | -118.0023 | -0.3832 | -118.5035 | 2.8175 | 2.8301 | 3.0952 | -118.6709 | 0.060571 | 0.018674 | -0.001407 | 0.11656 | 0.23806 | 0.12679 | -0.22367 | -0.009441 | 0.034271 | 0.65918 | 0.15803 | 0.16747 | 0.046931 | 0.31196 | 118.4378 | -2.6666 | 118.7221 | 118.6601 | 0.22227 | -2.5451 | -2.6564 | 121.479 | 121.4916 | 121.7567 | 118.2783 | -121.4541 | 118.7781 | 118.8996 | 118.7883 | 118.6802 | -3.0069
1789.1719 | 121.4127 | -118.9957 | 2.449 | 1.4211e-13 | -0.0245 | 0.00028424 | 0.067981 | -0.011638 | 0.059539 | -0.0073253 | -0.0029439 | 0.0051278 | 0.018036 | 0.033431 | 0.0074415 | -118.3686 | -0.38777 | -118.8697 | 2.4604 | 2.4684 | 2.7335 | -119.0327 | 0.060571 | 0.018674 | -0.005985 | 0.11198 | 0.24264 | 0.14053 | -0.21452 | -0.037008 | 0.011324 | 0.62707 | 0.12594 | 0.16295 | 0.019363 | 0.28442 | 118.7812 | -2.3371 | 119.0562 | 118.9897 | 0.20853 | -2.2064 | -2.3085 | 121.456 | 121.4641 | 121.7291 | 118.6079 | -121.4817 | 119.1076 | 119.2383 | 119.1362 | 119.0143 | -2.6636
1790.9219 | 121.4127 | -119.989 | 1.4465 | 1.4211e-13 | -0.024713 | 0.00049784 | 0.067981 | -0.011852 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.033431 | 0.0076551 | -119.3438 | -0.40151 | -119.8449 | 1.4806 | 1.4931 | 1.7719 | -120.0217 | 0.051413 | 0.018674 | -0.001407 | 0.11656 | 0.24264 | 0.14969 | -0.21452 | -0.032708 | 0.034052 | 0.64522 | 0.14411 | 0.17682 | 0.046555 | 0.32542 | 119.7745 | -1.33 | 120.0404 | 119.9876 | 0.21311 | -1.2039 | -1.2968 | 121.4696 | 121.4821 | 121.761 | 119.5875 | -121.4683 | 120.1056 | 120.2317 | 120.1387 | 120.0077 | -1.661
1792.6719 | 121.4493 | -120.2637 | 1.1444 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067554 | -0.011852 | 0.059753 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018036 | 0.033859 | 0.0076551 | -119.6048 | -0.39693 | -120.1104 | 1.2242 | 1.2367 | 1.4972 | -120.2827 | 0.060571 | 0.023253 | -0.001407 | 0.11198 | 0.24721 | 0.14053 | -0.21452 | -0.019049 | 0.079786 | 0.65891 | 0.15323 | 0.17228 | 0.09226 | 0.35282 | 120.0492 | -1.0324 | 120.3242 | 120.2623 | 0.21311 | -0.89719 | -1.0039 | 121.4879 | 121.5003 | 121.7609 | 119.8667 | -121.4271 | 120.3757 | 120.5109 | 120.4042 | 120.2869 | -1.3589
1794.3594 | 121.4127 | -120.6985 | 0.7782 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.067981 | -0.012066 | 0.058898 | 0.0079357 | -0.0027303 | 0.0047004 | 0.01825 | 0.033645 | 0.0072279 | -120.0763 | -0.40609 | -120.5912 | 0.76178 | 0.76962 | 1.044 | -120.7544 | 0.055992 | 0.018674 | -0.001407 | 0.11656 | 0.24264 | 0.058115 | -0.22367 | -0.055803 | -0.01642 | 0.62222 | 0.10739 | 0.16319 | -0.00858 | 0.26575 | 120.4749 | -0.66164 | 120.7545 | 120.6971 | 0.22227 | -0.53556 | -0.72008 | 121.4603 | 121.4682 | 121.7425 | 120.2925 | -121.5325 | 120.8151 | 120.9412 | 120.7567 | 120.7172 | -1.0019
1796.1094 | 121.4218 | -120.8176 | 0.69122 | 1.4211e-13 | -0.024927 | 0.00071164 | 0.067981 | -0.011852 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.033645 | 0.0074415 | -120.1633 | -0.41983 | -120.669 | 0.67479 | 0.69636 | 0.91575 | -120.8368 | 0.060571 | 0.014095 | 0.003172 | 0.1074 | 0.24264 | 0.094744 | -0.20994 | -0.019205 | -0.016435 | 0.65425 | 0.14857 | 0.16778 | 0.005133 | 0.22453 | 120.6076 | -0.58382 | 120.8781 | 120.8207 | 0.21311 | -0.44859 | -0.59648 | 121.4924 | 121.5139 | 121.7333 | 120.3977 | -121.528 | 120.925 | 121.0602 | 120.9123 | 120.8317 | -0.90116
1797.8281 | 121.4767 | -120.8313 | 0.64087 | 1.4211e-13 | -0.024713 | 0.00071164 | 0.067767 | -0.012066 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018677 | 0.033645 | 0.0074415 | -120.2183 | -0.40609 | -120.7285 | 0.63816 | 0.64141 | 0.86538 | -120.9009 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.24264 | 0.1039 | -0.22367 | -0.069577 | -0.002708 | 0.61304 | 0.10279 | 0.17236 | 0.000539 | 0.22452 | 120.6076 | -0.54263 | 120.8919 | 120.8299 | 0.22227 | -0.39823 | -0.53697 | 121.4695 | 121.4727 | 121.6967 | 120.4252 | -121.5417 | 120.9295 | 121.0739 | 120.9352 | 120.85 | -0.86454
1799.5312 | 121.4539 | -120.8771 | 0.60425 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.067981 | -0.011852 | 0.059326 | 0.0079357 | -0.0031575 | 0.005555 | 0.018463 | 0.033645 | 0.0078689 | -120.264 | -0.41983 | -120.7789 | 0.59696 | 0.60478 | 0.81502 | -120.9375 | 0.06515 | 0.018674 | 0.003172 | 0.1074 | 0.24721 | 0.099323 | -0.22825 | -0.060432 | -0.007292 | 0.61303 | 0.098203 | 0.15863 | 0.000529 | 0.21077 | 120.6488 | -0.49685 | 120.9422 | 120.8802 | 0.23142 | -0.35703 | -0.50493 | 121.474 | 121.4819 | 121.6921 | 120.4573 | -121.5418 | 120.9845 | 121.1243 | 120.9764 | 120.8957 | -0.8325
1801.2812 | 121.4081 | -120.9091 | 0.59967 | 1.4211e-13 | -0.024927 | 0.00092524 | 0.067767 | -0.011425 | 0.059539 | 0.0079357 | -0.0029439 | 0.0047004 | 0.018463 | 0.033431 | 0.0072279 | -120.2824 | -0.41983 | -120.7926 | 0.56949 | 0.58188 | 0.80586 | -120.9696 | 0.06515 | 0.018674 | 0.003172 | 0.1074 | 0.24264 | 0.13137 | -0.21452 | -0.060441 | -0.030184 | 0.62676 | 0.11651 | 0.17695 | -0.017788 | 0.20619 | 120.6946 | -0.49227 | 120.9743 | 120.9123 | 0.21769 | -0.35703 | -0.4683 | 121.4786 | 121.491 | 121.715 | 120.4893 | -121.5692 | 121.0165 | 121.1518 | 121.0405 | 120.9278 | -0.81419
1802.9531 | 121.5683 | -120.8771 | 0.55389 | 1.4211e-13 | -0.024927 | 0.00092524 | 0.067554 | -0.011852 | 0.059112 | 0.0079357 | -0.0031575 | 0.0051278 | 0.01825 | 0.033645 | 0.0076551 | -120.3053 | -0.4244 | -120.8155 | 0.56033 | 0.55899 | 0.78755 | -120.997 | 0.060571 | 0.027831 | -0.005985 | 0.10282 | 0.24721 | 0.11306 | -0.22367 | -0.11996 | 0.006435 | 0.57183 | 0.061577 | 0.18153 | 0.005094 | 0.23366 | 120.6534 | -0.45107 | 120.9376 | 120.8711 | 0.21769 | -0.30668 | -0.44083 | 121.4374 | 121.4361 | 121.6646 | 120.4527 | -121.5509 | 120.9799 | 121.1243 | 120.9901 | 120.9049 | -0.77757
1804.6875 | 121.4264 | -120.3415 | 0.99792 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.067767 | -0.012066 | 0.059539 | 0.015566 | -0.0029439 | 0.0049142 | 0.01825 | 0.033645 | 0.0076551 | -119.7696 | -0.45645 | -120.2478 | 1.1189 | 1.1405 | 1.3507 | -120.4888 | 0.06515 | 0.023253 | -0.010564 | 0.1074 | 0.23806 | 0.1039 | -0.21452 | -0.14728 | 0.12097 | 0.57191 | 0.093701 | 0.24098 | 0.14259 | 0.35279 | 120.127 | -0.89052 | 120.4066 | 120.3309 | 0.20395 | -0.75987 | -0.89402 | 121.4604 | 121.482 | 121.6922 | 119.885 | -121.4867 | 120.4489 | 120.5795 | 120.4454 | 120.3647 | -1.2124
1806.4375 | 121.5775 | -120.2866 | 1.0803 | 1.4211e-13 | -0.024927 | 0.0011388 | 0.067981 | -0.011852 | 0.059539 | -0.0073253 | -0.0031575 | 0.0051278 | 0.01825 | 0.033431 | 0.0072279 | -119.8108 | -0.45188 | -120.2753 | 1.0548 | 1.1268 | 1.3461 | -120.4796 | 0.060571 | 0.023253 | -0.010564 | 0.10282 | 0.23806 | 0.13595 | -0.2191 | -0.19306 | -0.025527 | 0.47578 | 0.011299 | 0.20435 | 0.046452 | 0.26582 | 120.0675 | -0.9775 | 120.3471 | 120.276 | 0.20853 | -0.84226 | -0.94437 | 121.3414 | 121.4133 | 121.6327 | 119.8347 | -121.5599 | 120.3894 | 120.5246 | 120.4225 | 120.3098 | -1.2994
1808.1562 | 121.5958 | -120.6162 | 0.75989 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.067981 | -0.012279 | 0.059326 | 0.00030522 | -0.0031575 | 0.0051278 | 0.017823 | 0.033645 | 0.0076551 | -120.113 | -0.42898 | -120.5774 | 0.77551 | 0.82914 | 1.0577 | -120.7498 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.25179 | 0.14053 | -0.20994 | -0.13362 | 0.015625 | 0.50319 | 0.038723 | 0.17234 | 0.069256 | 0.2978 | 120.4062 | -0.65707 | 120.6767 | 120.6147 | 0.20853 | -0.50809 | -0.61936 | 121.3917 | 121.4453 | 121.6738 | 120.1872 | -121.5097 | 120.719 | 120.8679 | 120.7567 | 120.6394 | -0.96983
1809.8281 | 121.4767 | -120.7809 | 0.66834 | 1.4211e-13 | -0.025141 | 0.0011388 | 0.067981 | -0.011852 | 0.059539 | 0.0079357 | -0.0029439 | 0.0051278 | 0.01825 | 0.033431 | 0.0076551 | -120.1816 | -0.44272 | -120.6965 | 0.66105 | 0.66888 | 0.94322 | -120.8642 | 0.055992 | 0.018674 | -0.010564 | 0.10282 | 0.24721 | 0.13137 | -0.2191 | -0.0833 | -0.007282 | 0.59931 | 0.084482 | 0.16778 | 0.000547 | 0.27489 | 120.5619 | -0.56551 | 120.8369 | 120.7704 | 0.20853 | -0.42112 | -0.53696 | 121.442 | 121.4498 | 121.7242 | 120.3382 | -121.5326 | 120.8838 | 121.0282 | 120.9123 | 120.7996 | -0.88743
1811.5469 | 121.5775 | -120.813 | 0.59052 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.067981 | -0.012279 | 0.059753 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018463 | 0.033645 | 0.0076551 | -120.232 | -0.43814 | -120.756 | 0.61069 | 0.63225 | 0.90659 | -120.9192 | 0.06515 | 0.018674 | -0.005985 | 0.098244 | 0.24264 | 0.039801 | -0.21452 | -0.1062 | 0.020176 | 0.58099 | 0.057008 | 0.16321 | 0.041736 | 0.31608 | 120.5985 | -0.49227 | 120.8781 | 120.807 | 0.20853 | -0.34788 | -0.55071 | 121.4237 | 121.4452 | 121.7196 | 120.3748 | -121.5097 | 120.9112 | 121.0556 | 120.8528 | 120.8317 | -0.80503
1813.2344 | 121.5591 | -120.7901 | 0.65002 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.068195 | -0.011852 | 0.059539 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018036 | 0.033645 | 0.0074415 | -120.1908 | -0.44272 | -120.7194 | 0.65648 | 0.67346 | 0.89743 | -120.8826 | 0.060571 | 0.027831 | -0.001407 | 0.098244 | 0.24264 | 0.11306 | -0.20536 | -0.09246 | 0.006451 | 0.59931 | 0.070746 | 0.16321 | 0.023437 | 0.24741 | 120.5847 | -0.55178 | 120.8507 | 120.7887 | 0.20395 | -0.40739 | -0.53697 | 121.4466 | 121.4636 | 121.6875 | 120.3474 | -121.5326 | 120.8883 | 121.0327 | 120.9032 | 120.8179 | -0.85538
1814.9531 | 121.4996 | -120.8359 | 0.66376 | 1.4211e-13 | -0.024927 | 0.00071164 | 0.067981 | -0.012066 | 0.059967 | 0.00030522 | -0.0027303 | 0.0053414 | 0.01825 | 0.033431 | 0.0078689 | -120.2228 | -0.44272 | -120.7468 | 0.62901 | 0.64599 | 0.86996 | -120.9146 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.25637 | 0.1039 | -0.21452 | -0.078737 | -0.034752 | 0.61304 | 0.089052 | 0.16779 | -0.01777 | 0.20621 | 120.6214 | -0.55636 | 120.901 | 120.8299 | 0.20853 | -0.40739 | -0.55986 | 121.4649 | 121.4819 | 121.7058 | 120.3932 | -121.5784 | 120.9433 | 121.0922 | 120.9398 | 120.8591 | -0.87827
1816.6406 | 121.4493 | -120.9045 | 0.61798 | 1.4211e-13 | -0.025141 | 0.00092524 | 0.067767 | -0.012066 | 0.059539 | 0.00030522 | -0.0031575 | 0.0047004 | 0.018463 | 0.033431 | 0.0074415 | -120.2778 | -0.44272 | -120.8018 | 0.59238 | 0.60478 | 0.8196 | -120.965 | 0.055992 | 0.023253 | -0.001407 | 0.10282 | 0.25179 | 0.12222 | -0.22367 | -0.06044 | -0.025604 | 0.62676 | 0.10278 | 0.16322 | -0.013204 | 0.20162 | 120.6809 | -0.51516 | 120.9605 | 120.9031 | 0.22227 | -0.36619 | -0.49577 | 121.4969 | 121.5093 | 121.7241 | 120.4618 | -121.583 | 121.0074 | 121.1563 | 121.0268 | 120.9278 | -0.84165
1818.3281 | 121.4767 | -120.9412 | 0.6134 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067981 | -0.012066 | 0.059753 | 0.015566 | -0.0027303 | 0.0049142 | 0.018036 | 0.034072 | 0.0074415 | -120.2869 | -0.45645 | -120.8109 | 0.59238 | 0.59562 | 0.81044 | -120.9741 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.24264 | 0.13595 | -0.21452 | -0.032977 | -0.021026 | 0.65423 | 0.13024 | 0.16322 | -0.017784 | 0.19704 | 120.7266 | -0.51058 | 121.0017 | 120.9398 | 0.21311 | -0.37077 | -0.47745 | 121.5335 | 121.5368 | 121.7516 | 120.4847 | -121.5875 | 121.044 | 121.1838 | 121.0771 | 120.9644 | -0.82792
1820.0938 | 121.4493 | -120.9412 | 0.54932 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.067767 | -0.012066 | 0.059539 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018036 | 0.033859 | 0.0076551 | -120.3419 | -0.45188 | -120.8613 | 0.53744 | 0.54525 | 0.76924 | -121.0291 | 0.06515 | 0.027831 | -0.005985 | 0.1074 | 0.25179 | 0.13137 | -0.2191 | -0.087924 | -0.011879 | 0.59929 | 0.079881 | 0.16781 | -0.004065 | 0.21992 | 120.7221 | -0.44192 | 121.0063 | 120.9352 | 0.21311 | -0.29752 | -0.41794 | 121.4786 | 121.4864 | 121.7104 | 120.4893 | -121.5784 | 121.0486 | 121.193 | 121.0725 | 120.969 | -0.76841
1821.7812 | 121.5912 | -120.9457 | 0.49896 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067554 | -0.011638 | 0.059326 | 0.0079357 | -0.0031575 | 0.0049142 | 0.01825 | 0.033431 | 0.0072279 | -120.3831 | -0.46103 | -120.8979 | 0.50997 | 0.51778 | 0.74176 | -121.0566 | 0.06515 | 0.023253 | -0.001407 | 0.1074 | 0.23806 | 0.14511 | -0.2191 | -0.11082 | 0.011004 | 0.56266 | 0.047833 | 0.15865 | 0.018815 | 0.2428 | 120.7266 | -0.39156 | 121.0109 | 120.9443 | 0.21769 | -0.2609 | -0.35385 | 121.4557 | 121.4635 | 121.6875 | 120.4847 | -121.5555 | 121.0531 | 121.1838 | 121.0908 | 120.969 | -0.71806
1823.5156 | 121.5546 | -120.9824 | 0.4715 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067767 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.033859 | 0.0074415 | -120.3968 | -0.47019 | -120.9208 | 0.48707 | 0.50404 | 0.72345 | -121.084 | 0.055992 | 0.023253 | -0.005985 | 0.098244 | 0.24721 | 0.14053 | -0.21452 | -0.10167 | 0.015578 | 0.58554 | 0.061563 | 0.16324 | 0.032544 | 0.25195 | 120.7678 | -0.37325 | 121.0384 | 120.9764 | 0.20853 | -0.22428 | -0.33097 | 121.4694 | 121.4864 | 121.7058 | 120.5122 | -121.5555 | 121.0806 | 121.2296 | 121.1229 | 121.0056 | -0.68601
1825.1875 | 121.4539 | -121.0556 | 0.44861 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.067981 | -0.012066 | 0.059112 | 0.015566 | -0.0031575 | 0.0049142 | 0.017823 | 0.033645 | 0.0078689 | -120.4518 | -0.47019 | -120.9757 | 0.45045 | 0.46283 | 0.68224 | -121.1298 | 0.060571 | 0.027831 | -0.010564 | 0.098244 | 0.25179 | 0.11306 | -0.21452 | -0.074219 | 0.001839 | 0.60384 | 0.079865 | 0.15408 | 0.014222 | 0.23363 | 120.8411 | -0.35036 | 121.1162 | 121.045 | 0.20395 | -0.19681 | -0.33555 | 121.5061 | 121.5184 | 121.7378 | 120.5854 | -121.5784 | 121.1538 | 121.3074 | 121.1687 | 121.0834 | -0.66312
1826.875 | 121.5408 | -121.0602 | 0.44403 | 1.4211e-13 | -0.025141 | 0.0011388 | 0.068195 | -0.012066 | 0.059753 | 0.015566 | -0.0029439 | 0.0051278 | 0.018677 | 0.033645 | 0.0074415 | -120.4655 | -0.48392 | -120.9803 | 0.43671 | 0.45367 | 0.66851 | -121.1527 | 0.06515 | 0.023253 | -0.001407 | 0.10282 | 0.23806 | 0.12222 | -0.22367 | -0.092536 | -0.007319 | 0.59469 | 0.079865 | 0.1724 | 0.009642 | 0.22447 | 120.8365 | -0.34121 | 121.1253 | 121.0588 | 0.22227 | -0.20597 | -0.32182 | 121.4969 | 121.5139 | 121.7287 | 120.5763 | -121.5967 | 121.163 | 121.2982 | 121.1824 | 121.0834 | -0.6677
1828.5781 | 121.4767 | -121.0602 | 0.44403 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.067767 | -0.012493 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018036 | 0.033645 | 0.0072279 | -120.4609 | -0.47019 | -120.9803 | 0.43213 | 0.45367 | 0.66851 | -121.1527 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.25179 | 0.094744 | -0.22367 | -0.092536 | -0.011897 | 0.59927 | 0.079865 | 0.1724 | 0.009642 | 0.22447 | 120.8365 | -0.33663 | 121.1208 | 121.0588 | 0.22227 | -0.19224 | -0.34929 | 121.4923 | 121.5139 | 121.7287 | 120.59 | -121.5967 | 121.1676 | 121.312 | 121.1549 | 121.0834 | -0.6677
1830.2812 | 121.5179 | -121.0739 | 0.4303 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.067981 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.033645 | 0.0076551 | -120.4838 | -0.47935 | -121.0032 | 0.40924 | 0.43536 | 0.65019 | -121.1756 | 0.06515 | 0.023253 | 0.003172 | 0.1074 | 0.25179 | 0.11306 | -0.21452 | -0.1017 | -0.021056 | 0.59011 | 0.070707 | 0.1724 | 0.005059 | 0.21989 | 120.8594 | -0.3229 | 121.1391 | 121.0771 | 0.21769 | -0.1785 | -0.31724 | 121.4832 | 121.5093 | 121.7241 | 120.5946 | -121.6059 | 121.1813 | 121.3257 | 121.187 | 121.0972 | -0.64481
1831.9688 | 121.6095 | -121.051 | 0.41199 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067767 | -0.011638 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.033859 | 0.0072279 | -120.5021 | -0.48392 | -121.0215 | 0.41382 | 0.42162 | 0.63645 | -121.1848 | 0.06515 | 0.023253 | -0.001407 | 0.10282 | 0.24264 | 0.071851 | -0.21452 | -0.13374 | 0.001833 | 0.5489 | 0.029504 | 0.16325 | 0.009633 | 0.22447 | 120.8365 | -0.30917 | 121.1162 | 121.0496 | 0.21311 | -0.16935 | -0.34014 | 121.4648 | 121.4726 | 121.6875 | 120.5671 | -121.5968 | 121.1538 | 121.2937 | 121.1229 | 121.0743 | -0.6265
1833.6406 | 121.4951 | -121.0968 | 0.41657 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.067554 | -0.012066 | 0.059326 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018463 | 0.033859 | 0.0074415 | -120.5021 | -0.4885 | -121.0215 | 0.40009 | 0.41704 | 0.64103 | -121.1893 | 0.055992 | 0.023253 | -0.005985 | 0.10282 | 0.24721 | 0.12679 | -0.21452 | -0.092546 | -0.01648 | 0.59468 | 0.075281 | 0.16783 | 0.000476 | 0.22447 | 120.8823 | -0.31374 | 121.1528 | 121.0908 | 0.20853 | -0.16935 | -0.28977 | 121.4969 | 121.5138 | 121.7378 | 120.6083 | -121.6059 | 121.1996 | 121.344 | 121.2236 | 121.1201 | -0.63108
1835.3594 | 121.4996 | -121.1426 | 0.42572 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067981 | -0.012066 | 0.059326 | -0.0073253 | -0.0027303 | 0.0053414 | 0.01825 | 0.033859 | 0.0076551 | -120.5067 | -0.4885 | -121.0353 | 0.40466 | 0.41246 | 0.63645 | -121.2031 | 0.060571 | 0.027831 | -0.005985 | 0.1074 | 0.25179 | 0.10848 | -0.2191 | -0.060507 | -0.021056 | 0.63588 | 0.10732 | 0.16783 | -0.013258 | 0.21074 | 120.9235 | -0.31832 | 121.2031 | 121.1366 | 0.21311 | -0.17393 | -0.31724 | 121.5472 | 121.555 | 121.779 | 120.6541 | -121.6288 | 121.25 | 121.3944 | 121.2511 | 121.1704 | -0.64482
1837.0469 | 121.6049 | -121.1014 | 0.40283 | 1.4211e-13 | -0.025354 | 0.0011388 | 0.067981 | -0.011852 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.033645 | 0.0078689 | -120.5204 | -0.49766 | -121.0444 | 0.40466 | 0.41246 | 0.63645 | -121.2077 | 0.06515 | 0.018674 | 0.003172 | 0.1074 | 0.24721 | 0.12222 | -0.2191 | -0.10628 | 0.001832 | 0.58094 | 0.056967 | 0.16325 | 0.00963 | 0.23362 | 120.8823 | -0.29543 | 121.1665 | 121.1046 | 0.22227 | -0.15562 | -0.28062 | 121.506 | 121.5138 | 121.7378 | 120.6037 | -121.6105 | 121.2088 | 121.3486 | 121.2236 | 121.1201 | -0.62193
1838.7188 | 121.5546 | -121.1014 | 0.4303 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018463 | 0.033859 | 0.0076551 | -120.5204 | -0.49308 | -121.0536 | 0.40466 | 0.41246 | 0.6273 | -121.2168 | 0.060571 | 0.027831 | -0.005985 | 0.098244 | 0.23348 | 0.048958 | -0.22367 | -0.11544 | -0.025634 | 0.58094 | 0.04781 | 0.16325 | -0.017836 | 0.197 | 120.8777 | -0.33205 | 121.1619 | 121.0954 | 0.21769 | -0.19682 | -0.38134 | 121.506 | 121.5138 | 121.7287 | 120.6083 | -121.6471 | 121.1996 | 121.3349 | 121.1503 | 121.1292 | -0.65397
1840.4688 | 121.5225 | -121.1105 | 0.42114 | 1.4211e-13 | -0.025568 | 0.00049784 | 0.068195 | -0.012066 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.033859 | 0.0074415 | -120.5296 | -0.49766 | -121.0536 | 0.39551 | 0.40788 | 0.6273 | -121.2214 | 0.060571 | 0.018674 | -0.001407 | 0.1074 | 0.23806 | 0.13595 | -0.22367 | -0.11087 | -0.025636 | 0.58094 | 0.056966 | 0.16783 | -0.01326 | 0.20616 | 120.8869 | -0.31374 | 121.1711 | 121.1091 | 0.22227 | -0.18308 | -0.28519 | 121.506 | 121.5184 | 121.7378 | 120.6129 | -121.6425 | 121.2179 | 121.3486 | 121.2465 | 121.1292 | -0.64482
1842.2031 | 121.5134 | -121.1655 | 0.40741 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067981 | -0.012279 | 0.059326 | -0.0073253 | -0.0027303 | 0.0047004 | 0.01825 | 0.034072 | 0.0076551 | -120.5387 | -0.50682 | -121.0719 | 0.40009 | 0.41246 | 0.62272 | -121.2397 | 0.055992 | 0.023253 | -0.005985 | 0.10282 | 0.24721 | 0.085587 | -0.2191 | -0.07425 | -0.007325 | 0.62672 | 0.093584 | 0.16783 | 0.005052 | 0.21531 | 120.9464 | -0.30459 | 121.2215 | 121.1595 | 0.21311 | -0.1602 | -0.32182 | 121.5656 | 121.5779 | 121.7882 | 120.6586 | -121.6471 | 121.2683 | 121.4127 | 121.2511 | 121.1887 | -0.6265
1843.875 | 121.5591 | -121.1517 | 0.38452 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.068195 | -0.011852 | 0.059112 | 0.00030522 | -0.0031575 | 0.0053414 | 0.018036 | 0.033645 | 0.0076551 | -120.5571 | -0.5114 | -121.0765 | 0.38177 | 0.4033 | 0.62272 | -121.2306 | 0.055992 | 0.023253 | -0.005985 | 0.10282 | 0.24721 | 0.13137 | -0.2191 | -0.078825 | -0.002749 | 0.59467 | 0.075273 | 0.1541 | 0.018783 | 0.2382 | 120.9326 | -0.2817 | 121.2077 | 121.1457 | 0.21311 | -0.13731 | -0.25315 | 121.5335 | 121.555 | 121.7745 | 120.6403 | -121.6151 | 121.2546 | 121.3989 | 121.2831 | 121.175 | -0.60362
1845.5625 | 121.6003 | -121.1288 | 0.37537 | 1.4211e-13 | -0.025568 | 0.00049784 | 0.068195 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.033859 | 0.0076551 | -120.5616 | -0.52055 | -121.0902 | 0.37719 | 0.4033 | 0.61356 | -121.2351 | 0.06515 | 0.018674 | -0.001407 | 0.11656 | 0.24721 | 0.15427 | -0.2191 | -0.10629 | 0.001827 | 0.56721 | 0.03865 | 0.14494 | 0.027938 | 0.2382 | 120.9098 | -0.25881 | 121.194 | 121.1274 | 0.21769 | -0.12815 | -0.2211 | 121.506 | 121.5321 | 121.7424 | 120.6083 | -121.6105 | 121.2454 | 121.3761 | 121.2831 | 121.1475 | -0.59446
1847.2344 | 121.5683 | -121.138 | 0.39825 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067767 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0053414 | 0.01825 | 0.034072 | 0.0074415 | -120.5616 | -0.5114 | -121.0856 | 0.38635 | 0.40788 | 0.61814 | -121.2489 | 0.055992 | 0.023253 | -0.005985 | 0.1074 | 0.24264 | 0.13137 | -0.21452 | -0.11087 | -0.011904 | 0.57636 | 0.052383 | 0.16326 | 0.009629 | 0.21989 | 120.9235 | -0.29085 | 121.194 | 121.132 | 0.20853 | -0.15562 | -0.26688 | 121.5243 | 121.5459 | 121.7561 | 120.6266 | -121.6471 | 121.2454 | 121.3806 | 121.2694 | 121.1613 | -0.61277
1848.9219 | 121.5454 | -121.1929 | 0.3891 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.067981 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018036 | 0.033859 | 0.0068005 | -120.5708 | -0.52513 | -121.0948 | 0.38635 | 0.4033 | 0.61356 | -121.2535 | 0.069728 | 0.027831 | 0.003172 | 0.10282 | 0.24264 | 0.13137 | -0.2191 | -0.060521 | -0.002749 | 0.62214 | 0.098159 | 0.15868 | 0.014205 | 0.22446 | 120.9738 | -0.28628 | 121.2627 | 121.1961 | 0.22227 | -0.14646 | -0.25773 | 121.5793 | 121.5962 | 121.8065 | 120.6678 | -121.6426 | 121.2958 | 121.4356 | 121.3243 | 121.2208 | -0.60819
1850.5938 | 121.6049 | -121.1426 | 0.36163 | 1.4211e-13 | -0.025782 | 0.00092524 | 0.068195 | -0.011852 | 0.059539 | -0.014956 | -0.0027303 | 0.0051278 | 0.01825 | 0.034072 | 0.0074415 | -120.58 | -0.52513 | -121.1039 | 0.38177 | 0.38957 | 0.61814 | -121.2535 | 0.060571 | 0.018674 | -0.010564 | 0.098244 | 0.24264 | 0.099323 | -0.2191 | -0.11087 | 0.020139 | 0.56262 | 0.038648 | 0.14952 | 0.027935 | 0.25651 | 120.9235 | -0.26339 | 121.2031 | 121.132 | 0.20853 | -0.119 | -0.26231 | 121.5243 | 121.5321 | 121.7607 | 120.6174 | -121.6151 | 121.2408 | 121.3852 | 121.2419 | 121.1613 | -0.58073
1852.2969 | 121.6553 | -121.1151 | 0.36163 | 1.4211e-13 | -0.025354 | 0.00049784 | 0.068195 | -0.011852 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018463 | 0.033859 | 0.0074415 | -120.58 | -0.52513 | -121.0994 | 0.38177 | 0.39872 | 0.61356 | -121.2626 | 0.06515 | 0.023253 | -0.005985 | 0.10282 | 0.24264 | 0.081008 | -0.2191 | -0.1475 | 0.020139 | 0.53516 | 0.015761 | 0.16326 | 0.037092 | 0.25193 | 120.896 | -0.25881 | 121.1803 | 121.1091 | 0.21311 | -0.119 | -0.28063 | 121.4969 | 121.5138 | 121.7287 | 120.59 | -121.6242 | 121.2179 | 121.3577 | 121.1961 | 121.1384 | -0.58073
1854.0156 | 121.6644 | -121.1472 | 0.37079 | 1.4211e-13 | -0.025354 | 0.00049784 | 0.067981 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.01825 | 0.033859 | 0.0076551 | -120.5708 | -0.53429 | -121.0948 | 0.39093 | 0.39415 | 0.60898 | -121.258 | 0.060571 | 0.023253 | -0.001407 | 0.098244 | 0.24264 | 0.11306 | -0.2191 | -0.11088 | 0.020139 | 0.57636 | 0.052383 | 0.16326 | 0.023357 | 0.23819 | 120.9281 | -0.27254 | 121.2077 | 121.1457 | 0.21769 | -0.12815 | -0.25773 | 121.5381 | 121.5413 | 121.7561 | 120.6129 | -121.6288 | 121.2454 | 121.3898 | 121.2602 | 121.1704 | -0.58988
1855.7031 | 121.5775 | -121.1792 | 0.3891 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.068195 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018036 | 0.033859 | 0.0076551 | -120.58 | -0.53429 | -121.1131 | 0.38177 | 0.38957 | 0.61356 | -121.2718 | 0.069728 | 0.018674 | -0.001407 | 0.098244 | 0.24721 | 0.099323 | -0.2191 | -0.09257 | -0.007327 | 0.59924 | 0.066113 | 0.15868 | 0.000469 | 0.22446 | 120.9601 | -0.29085 | 121.2489 | 121.1778 | 0.21769 | -0.14188 | -0.28978 | 121.561 | 121.5688 | 121.7928 | 120.6449 | -121.6609 | 121.2774 | 121.4264 | 121.2785 | 121.1979 | -0.60819
1857.3906 | 121.5866 | -121.1884 | 0.37537 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.068195 | -0.012279 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.01825 | 0.034286 | 0.0074415 | -120.5845 | -0.53887 | -121.1177 | 0.37719 | 0.39415 | 0.60898 | -121.2718 | 0.06515 | 0.018674 | -0.005985 | 0.11198 | 0.24264 | 0.081008 | -0.2191 | -0.083415 | 0.001827 | 0.60382 | 0.07069 | 0.15411 | 0.01878 | 0.23362 | 120.9693 | -0.26339 | 121.2535 | 121.1824 | 0.21311 | -0.13273 | -0.29436 | 121.5655 | 121.5825 | 121.7973 | 120.6495 | -121.6471 | 121.3003 | 121.431 | 121.2694 | 121.207 | -0.59446
1859.125 | 121.6782 | -121.1426 | 0.37079 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0029439 | 0.0047004 | 0.01825 | 0.034072 | 0.0074415 | -120.5891 | -0.54345 | -121.1085 | 0.37719 | 0.39415 | 0.59983 | -121.2855 | 0.060571 | 0.018674 | -0.001407 | 0.11656 | 0.24721 | 0.081008 | -0.22367 | -0.14293 | 0.006404 | 0.55347 | 0.03407 | 0.177 | 0.023357 | 0.22904 | 120.9189 | -0.25423 | 121.2031 | 121.1412 | 0.22227 | -0.12357 | -0.28978 | 121.5198 | 121.5367 | 121.7424 | 120.5991 | -121.6563 | 121.2591 | 121.3898 | 121.2236 | 121.1613 | -0.59446
1860.8281 | 121.5912 | -121.1975 | 0.41657 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.067767 | -0.012066 | 0.059539 | 0.00030522 | -0.0031575 | 0.0051278 | 0.018036 | 0.033645 | 0.0076551 | -120.5708 | -0.54345 | -121.0948 | 0.40009 | 0.41704 | 0.6273 | -121.258 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.24721 | 0.11764 | -0.21452 | -0.060522 | -0.01648 | 0.62671 | 0.10274 | 0.16326 | 0.000476 | 0.21073 | 120.983 | -0.30916 | 121.2581 | 121.1915 | 0.20853 | -0.16935 | -0.29893 | 121.5976 | 121.6146 | 121.8248 | 120.6541 | -121.6746 | 121.3049 | 121.4447 | 121.3151 | 121.2208 | -0.63108
1862.5156 | 121.55 | -121.2021 | 0.41657 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.067981 | -0.012066 | 0.059539 | 0.00030522 | -0.0029439 | 0.0047004 | 0.01825 | 0.034072 | 0.0076551 | -120.5983 | -0.55718 | -121.1177 | 0.38635 | 0.38499 | 0.61356 | -121.2947 | 0.06515 | 0.023253 | 0.003172 | 0.10282 | 0.24264 | 0.11306 | -0.21452 | -0.092576 | -0.030215 | 0.60382 | 0.084423 | 0.177 | -0.031576 | 0.197 | 120.9876 | -0.31374 | 121.2672 | 121.2053 | 0.21769 | -0.17393 | -0.30351 | 121.5884 | 121.5871 | 121.8156 | 120.6449 | -121.7112 | 121.3049 | 121.4447 | 121.3151 | 121.2253 | -0.63108
1864.2188 | 121.5546 | -121.2204 | 0.37079 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.068195 | -0.012066 | 0.059753 | -0.0073253 | -0.0029439 | 0.0049142 | 0.01825 | 0.034072 | 0.0078689 | -120.6166 | -0.56176 | -121.1451 | 0.35888 | 0.37583 | 0.59525 | -121.3038 | 0.055992 | 0.018674 | -0.005985 | 0.10282 | 0.24721 | 0.13595 | -0.21452 | -0.083423 | -0.011909 | 0.60382 | 0.075264 | 0.15869 | 0.005042 | 0.22446 | 121.0059 | -0.26797 | 121.2764 | 121.2144 | 0.20853 | -0.12357 | -0.23484 | 121.5793 | 121.5962 | 121.8156 | 120.6586 | -121.6746 | 121.3232 | 121.4676 | 121.3564 | 121.2391 | -0.5853
1865.9219 | 121.5408 | -121.2341 | 0.36163 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.067981 | -0.011852 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.018463 | 0.034072 | 0.0078689 | -120.6303 | -0.55718 | -121.1497 | 0.3543 | 0.35294 | 0.58609 | -121.313 | 0.060571 | 0.027831 | -0.001407 | 0.1074 | 0.24264 | 0.12222 | -0.21452 | -0.078848 | -0.007332 | 0.60382 | 0.084419 | 0.16327 | -0.008697 | 0.22446 | 121.0196 | -0.25423 | 121.2947 | 121.2327 | 0.21311 | -0.119 | -0.23942 | 121.5884 | 121.5871 | 121.8202 | 120.6769 | -121.6746 | 121.3415 | 121.4768 | 121.3563 | 121.262 | -0.57615
1867.5938 | 121.7102 | -121.1792 | 0.34332 | 1.4211e-13 | -0.025141 | 0.00071164 | 0.068195 | -0.011852 | 0.059539 | 0.00030522 | -0.0025167 | 0.0049142 | 0.01825 | 0.033645 | 0.0076551 | -120.6303 | -0.56634 | -121.1497 | 0.36346 | 0.33004 | 0.59067 | -121.3176 | 0.060571 | 0.027831 | -0.001407 | 0.10282 | 0.25179 | 0.048958 | -0.21452 | -0.13836 | 0.020135 | 0.54888 | 0.029487 | 0.16785 | -0.013281 | 0.24735 | 120.9647 | -0.2405 | 121.2398 | 121.1778 | 0.21311 | -0.091529 | -0.29436 | 121.5427 | 121.5092 | 121.7699 | 120.6129 | -121.6609 | 121.282 | 121.431 | 121.2282 | 121.207 | -0.55784
1869.2812 | 121.6095 | -121.2524 | 0.37079 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.068195 | -0.011852 | 0.059753 | -0.0073253 | -0.0029439 | 0.0051278 | 0.01825 | 0.033859 | 0.0076551 | -120.6349 | -0.5755 | -121.1634 | 0.35888 | 0.34836 | 0.58151 | -121.3267 | 0.060571 | 0.03241 | -0.010564 | 0.098244 | 0.23348 | 0.14053 | -0.2191 | -0.074275 | -0.011909 | 0.61755 | 0.088994 | 0.16327 | -0.022432 | 0.21072 | 121.0333 | -0.27254 | 121.313 | 121.2419 | 0.20853 | -0.13731 | -0.23026 | 121.6113 | 121.6008 | 121.834 | 120.6769 | -121.6975 | 121.3507 | 121.4859 | 121.393 | 121.2849 | -0.58988
1871 | 121.6599 | -121.2158 | 0.33875 | 1.4211e-13 | -0.025354 | 0.00092524 | 0.068195 | -0.012279 | 0.059753 | 0.0079357 | -0.0031575 | 0.0051278 | 0.018036 | 0.034072 | 0.0076551 | -120.6441 | -0.58008 | -121.1634 | 0.34514 | 0.35294 | 0.58151 | -121.3359 | 0.060571 | 0.03241 | 0.003172 | 0.10282 | 0.24721 | 0.085587 | -0.21452 | -0.12005 | 0.0064 | 0.57177 | 0.052373 | 0.17243 | 0.014191 | 0.24277 | 121.0013 | -0.23592 | 121.2764 | 121.219 | 0.21769 | -0.09153 | -0.25316 | 121.561 | 121.5688 | 121.7973 | 120.6357 | -121.6746 | 121.3186 | 121.463 | 121.3014 | 121.2482 | -0.55326
1872.7031 | 121.5775 | -121.2387 | 0.37079 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.067981 | -0.012279 | 0.059539 | 0.0079357 | -0.0029439 | 0.0047004 | 0.01825 | 0.034286 | 0.0076551 | -120.6349 | -0.5755 | -121.1634 | 0.35888 | 0.37125 | 0.58609 | -121.3267 | 0.055992 | 0.023253 | -0.005985 | 0.1074 | 0.24721 | 0.081008 | -0.20994 | -0.088008 | -0.011909 | 0.60381 | 0.075261 | 0.16327 | 0.000463 | 0.2153 | 121.0288 | -0.26339 | 121.2947 | 121.2327 | 0.20395 | -0.12357 | -0.28978 | 121.5976 | 121.61 | 121.8248 | 120.6632 | -121.6975 | 121.3461 | 121.4859 | 121.3197 | 121.262 | -0.58073
1874.4531 | 121.582 | -121.2708 | 0.37994 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.067767 | -0.012066 | 0.059326 | 0.0079357 | -0.0025167 | 0.0047004 | 0.017823 | 0.034286 | 0.0072279 | -120.6486 | -0.58923 | -121.1772 | 0.3543 | 0.35752 | 0.57693 | -121.345 | 0.060571 | 0.014095 | 0.003172 | 0.11198 | 0.23348 | 0.085587 | -0.2191 | -0.07428 | -0.025643 | 0.62212 | 0.09357 | 0.16785 | -0.022429 | 0.19699 | 121.0517 | -0.26797 | 121.3313 | 121.2739 | 0.22227 | -0.14647 | -0.29436 | 121.6251 | 121.6283 | 121.8477 | 120.6815 | -121.725 | 121.3827 | 121.5042 | 121.3563 | 121.2848 | -0.59904
1876.1406 | 121.7102 | -121.2158 | 0.32959 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.067767 | -0.012066 | 0.059539 | 0.0079357 | -0.0029439 | 0.0049142 | 0.01825 | 0.033645 | 0.0076551 | -120.6578 | -0.58466 | -121.1863 | 0.34057 | 0.34378 | 0.56778 | -121.3496 | 0.06515 | 0.023253 | -0.001407 | 0.1074 | 0.25179 | 0.14053 | -0.2191 | -0.13379 | 0.010976 | 0.55803 | 0.029481 | 0.16327 | 0.014188 | 0.23819 | 120.9967 | -0.22219 | 121.281 | 121.2144 | 0.21769 | -0.077796 | -0.18906 | 121.5564 | 121.5596 | 121.7836 | 120.6312 | -121.6792 | 121.3232 | 121.4676 | 121.3563 | 121.2391 | -0.54868
1877.8281 | 121.5729 | -121.2708 | 0.35248 | 1.4211e-13 | -0.025782 | 0.00092524 | 0.067981 | -0.011852 | 0.059326 | 0.00030522 | -0.0025167 | 0.0047004 | 0.01825 | 0.033859 | 0.0078689 | -120.6669 | -0.59381 | -121.1909 | 0.34057 | 0.34378 | 0.56778 | -121.3588 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.23806 | 0.039801 | -0.2191 | -0.088016 | -0.011912 | 0.60381 | 0.079835 | 0.16785 | -0.0087 | 0.2153 | 121.0517 | -0.24508 | 121.3313 | 121.2648 | 0.21311 | -0.11442 | -0.31268 | 121.6113 | 121.6145 | 121.8385 | 120.6769 | -121.7112 | 121.3782 | 121.5088 | 121.3106 | 121.294 | -0.57157
1879.5469 | 121.6187 | -121.2753 | 0.34332 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.067981 | -0.012279 | 0.059753 | 0.0079357 | -0.0031575 | 0.0049142 | 0.018463 | 0.033859 | 0.0074415 | -120.6715 | -0.59839 | -121.1955 | 0.33599 | 0.33462 | 0.55862 | -121.3633 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.23348 | 0.14511 | -0.2191 | -0.088017 | -0.007335 | 0.60381 | 0.079835 | 0.16785 | -0.008703 | 0.2153 | 121.0562 | -0.23592 | 121.3359 | 121.2739 | 0.21769 | -0.10984 | -0.19821 | 121.6113 | 121.6099 | 121.8339 | 120.6769 | -121.7067 | 121.3827 | 121.5088 | 121.4204 | 121.2986 | -0.56242
1881.2344 | 121.7056 | -121.2479 | 0.32044 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.067981 | -0.012066 | 0.059539 | 0.0079357 | -0.0025167 | 0.0051278 | 0.01825 | 0.033859 | 0.0076551 | -120.6853 | -0.60755 | -121.2001 | 0.33141 | 0.34378 | 0.55862 | -121.3725 | 0.06515 | 0.018674 | -0.005985 | 0.10282 | 0.23806 | 0.13137 | -0.2191 | -0.12464 | 0.010974 | 0.56261 | 0.04779 | 0.17243 | 0.023343 | 0.23818 | 121.0288 | -0.21761 | 121.313 | 121.2419 | 0.21311 | -0.082377 | -0.18906 | 121.5793 | 121.5916 | 121.8065 | 120.6403 | -121.6929 | 121.3507 | 121.4859 | 121.3792 | 121.2665 | -0.53953
1882.9062 | 121.5958 | -121.2982 | 0.33417 | 1.4211e-13 | -0.025568 | 0.00028424 | 0.067981 | -0.012279 | 0.059326 | 0.00030522 | -0.0031575 | 0.0049142 | 0.01825 | 0.034072 | 0.0078689 | -120.6807 | -0.60755 | -121.2092 | 0.32683 | 0.33004 | 0.55862 | -121.3771 | 0.06515 | 0.023253 | -0.005985 | 0.11656 | 0.24721 | 0.044379 | -0.21452 | -0.078866 | -0.007336 | 0.61754 | 0.088988 | 0.16785 | -0.004125 | 0.22445 | 121.0837 | -0.21761 | 121.3634 | 121.2922 | 0.20853 | -0.086952 | -0.28979 | 121.625 | 121.6283 | 121.8568 | 120.6907 | -121.7113 | 121.4148 | 121.5454 | 121.3426 | 121.3215 | -0.54868
1884.6094 | 121.5912 | -121.3074 | 0.34332 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.067981 | -0.012279 | 0.059753 | 0.00030522 | -0.0033713 | 0.0051278 | 0.018036 | 0.034072 | 0.0076551 | -120.699 | -0.6167 | -121.2184 | 0.32225 | 0.32546 | 0.54488 | -121.3862 | 0.06515 | 0.027831 | -0.005985 | 0.098244 | 0.24264 | 0.11306 | -0.2191 | -0.078869 | -0.02107 | 0.60838 | 0.088986 | 0.16785 | -0.01786 | 0.20156 | 121.0883 | -0.24508 | 121.3725 | 121.3014 | 0.21311 | -0.10069 | -0.23026 | 121.6296 | 121.6328 | 121.8523 | 120.6907 | -121.7296 | 121.4056 | 121.55 | 121.4204 | 121.3352 | -0.56242
1886.2969 | 121.6187 | -121.2753 | 0.34332 | 1.4211e-13 | -0.025568 | 0.00092524 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0025167 | 0.0051278 | 0.01825 | 0.033645 | 0.0074415 | -120.6944 | -0.60755 | -121.2184 | 0.33141 | 0.32088 | 0.55404 | -121.3862 | 0.060571 | 0.023253 | 0.003172 | 0.10282 | 0.24721 | 0.099323 | -0.2191 | -0.11091 | -0.011914 | 0.58092 | 0.056943 | 0.16785 | -0.022439 | 0.21072 | 121.0562 | -0.2405 | 121.3359 | 121.2785 | 0.22227 | -0.096108 | -0.244 | 121.6067 | 121.5962 | 121.8294 | 120.6678 | -121.7296 | 121.3782 | 121.5225 | 121.3747 | 121.2986 | -0.56242
1887.9688 | 121.637 | -121.2936 | 0.33417 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.068195 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018036 | 0.034072 | 0.0076551 | -120.7081 | -0.62128 | -121.223 | 0.32683 | 0.32088 | 0.55404 | -121.4046 | 0.055992 | 0.023253 | -0.001407 | 0.098244 | 0.24264 | 0.071851 | -0.22367 | -0.11092 | -0.007336 | 0.58549 | 0.070675 | 0.18159 | -0.013283 | 0.21987 | 121.07 | -0.23592 | 121.3496 | 121.2922 | 0.22227 | -0.09153 | -0.26232 | 121.6205 | 121.6145 | 121.8477 | 120.6724 | -121.7387 | 121.3919 | 121.5363 | 121.3655 | 121.3169 | -0.55784
1889.6562 | 121.6141 | -121.2891 | 0.37537 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.068195 | -0.011852 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.034072 | 0.0074415 | -120.6898 | -0.62586 | -121.2001 | 0.34514 | 0.30257 | 0.5632 | -121.3679 | 0.055992 | 0.027831 | -0.005985 | 0.1074 | 0.23806 | 0.012329 | -0.21452 | -0.078864 | -0.030221 | 0.59923 | 0.088988 | 0.16785 | -0.072798 | 0.18783 | 121.0745 | -0.26797 | 121.3451 | 121.2831 | 0.20853 | -0.13731 | -0.36304 | 121.6342 | 121.5916 | 121.8523 | 120.6632 | -121.7433 | 121.3965 | 121.5271 | 121.3014 | 121.3169 | -0.58988
1891.3281 | 121.6187 | -121.2845 | 0.35706 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.067767 | -0.012279 | 0.059539 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018036 | 0.033645 | 0.0072279 | -120.6853 | -0.63044 | -121.2047 | 0.34514 | 0.34836 | 0.57235 | -121.3679 | 0.060571 | 0.018674 | -0.005985 | 0.10282 | 0.23806 | 0.13137 | -0.2191 | -0.083441 | -0.011911 | 0.59923 | 0.079833 | 0.16327 | -0.008699 | 0.2153 | 121.0654 | -0.25423 | 121.3451 | 121.2785 | 0.21311 | -0.119 | -0.22568 | 121.6296 | 121.6328 | 121.8568 | 120.654 | -121.725 | 121.3873 | 121.5225 | 121.4159 | 121.3032 | -0.57615
1893 | 121.7148 | -121.257 | 0.32044 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.067981 | -0.011425 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.01825 | 0.034286 | 0.0078689 | -120.6944 | -0.63502 | -121.2184 | 0.34514 | 0.32088 | 0.57235 | -121.3954 | 0.055992 | 0.027831 | -0.005985 | 0.1074 | 0.24264 | 0.11306 | -0.2191 | -0.13838 | 0.02471 | 0.56261 | 0.038632 | 0.17701 | 0.000449 | 0.25192 | 121.0379 | -0.21303 | 121.313 | 121.251 | 0.21311 | -0.077798 | -0.20738 | 121.6022 | 121.5779 | 121.8294 | 120.622 | -121.7158 | 121.3644 | 121.4997 | 121.3701 | 121.2849 | -0.53953
1894.6875 | 121.701 | -121.2799 | 0.33875 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.068195 | -0.011852 | 0.059753 | 0.00030522 | -0.0027303 | 0.0053414 | 0.018463 | 0.033859 | 0.0078689 | -120.699 | -0.64418 | -121.223 | 0.33141 | 0.33462 | 0.5632 | -121.3908 | 0.060571 | 0.027831 | -0.005985 | 0.098244 | 0.23806 | 0.13595 | -0.2191 | -0.11091 | -0.007336 | 0.58091 | 0.056942 | 0.16786 | -0.004125 | 0.22445 | 121.0608 | -0.2405 | 121.3405 | 121.2739 | 0.21311 | -0.10069 | -0.20279 | 121.6113 | 121.6145 | 121.8431 | 120.6357 | -121.7296 | 121.3782 | 121.518 | 121.4159 | 121.3077 | -0.55784
1896.375 | 121.7331 | -121.2708 | 0.31586 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.067767 | -0.011852 | 0.059539 | 0.00030522 | -0.0031575 | 0.0049142 | 0.018036 | 0.033859 | 0.0074415 | -120.699 | -0.65333 | -121.2275 | 0.33141 | 0.32546 | 0.55862 | -121.3862 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.23806 | 0.12222 | -0.22367 | -0.11549 | 0.015552 | 0.57176 | 0.043209 | 0.1587 | 0.009606 | 0.24276 | 121.0471 | -0.21304 | 121.3313 | 121.2693 | 0.22227 | -0.077799 | -0.19364 | 121.6022 | 121.5962 | 121.8294 | 120.6174 | -121.7021 | 121.3736 | 121.5088 | 121.393 | 121.294 | -0.53953
1898.0625 | 121.7148 | -121.2891 | 0.33417 | 1.4211e-13 | -0.025995 | 0.00092524 | 0.067981 | -0.012279 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.034072 | 0.0076551 | -120.7173 | -0.65333 | -121.2321 | 0.32225 | 0.3392 | 0.55862 | -121.4137 | 0.060571 | 0.023253 | -0.005985 | 0.098244 | 0.24264 | 0.099323 | -0.22367 | -0.12465 | -0.011914 | 0.57176 | 0.05694 | 0.18159 | 0.005032 | 0.22445 | 121.0654 | -0.23592 | 121.3496 | 121.2831 | 0.21769 | -0.09153 | -0.23484 | 121.6113 | 121.6283 | 121.8477 | 120.6357 | -121.7479 | 121.3873 | 121.5317 | 121.3884 | 121.3123 | -0.55784
1899.75 | 121.6187 | -121.3486 | 0.3479 | 1.4211e-13 | -0.025782 | 0.00092524 | 0.067981 | -0.012066 | 0.059326 | 0.015566 | -0.0027303 | 0.0051278 | 0.018463 | 0.033859 | 0.0078689 | -120.7173 | -0.65791 | -121.2459 | 0.31767 | 0.30257 | 0.54488 | -121.4137 | 0.060571 | 0.027831 | -0.010564 | 0.11198 | 0.24264 | 0.14969 | -0.2191 | -0.065143 | -0.030226 | 0.63127 | 0.10272 | 0.16786 | -0.045332 | 0.19698 | 121.1295 | -0.23592 | 121.4091 | 121.338 | 0.20853 | -0.10526 | -0.19821 | 121.6662 | 121.6511 | 121.8935 | 120.6907 | -121.7616 | 121.4606 | 121.5912 | 121.4983 | 121.3764 | -0.567
1901.5 | 121.6553 | -121.3486 | 0.31128 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.067767 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018677 | 0.034072 | 0.0076551 | -120.731 | -0.66249 | -121.2504 | 0.3131 | 0.31631 | 0.54946 | -121.4275 | 0.060571 | 0.03241 | -0.005985 | 0.10282 | 0.24264 | 0.12679 | -0.2191 | -0.07888 | 0.001817 | 0.61753 | 0.098137 | 0.17702 | 0.005026 | 0.23818 | 121.1295 | -0.20846 | 121.4091 | 121.3426 | 0.21311 | -0.068642 | -0.18448 | 121.6617 | 121.6649 | 121.898 | 120.6861 | -121.7387 | 121.4514 | 121.5912 | 121.4754 | 121.381 | -0.53037
1903.1875 | 121.7834 | -121.3074 | 0.30212 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.068195 | -0.012066 | 0.059539 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018463 | 0.034072 | 0.0072279 | -120.7494 | -0.66249 | -121.2687 | 0.31767 | 0.30257 | 0.53115 | -121.4412 | 0.060571 | 0.023253 | 0.003172 | 0.098244 | 0.24721 | 0.048958 | -0.21452 | -0.13382 | 0.01555 | 0.55802 | 0.038625 | 0.17244 | 0.000444 | 0.22902 | 121.0929 | -0.20388 | 121.3679 | 121.3105 | 0.21769 | -0.054909 | -0.25317 | 121.625 | 121.6099 | 121.8385 | 120.6449 | -121.7433 | 121.4056 | 121.5546 | 121.3563 | 121.3306 | -0.51664
1904.8906 | 121.637 | -121.3531 | 0.32044 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.067767 | -0.012493 | 0.059753 | 0.0079357 | -0.0033713 | 0.0049142 | 0.01825 | 0.033859 | 0.0076551 | -120.7448 | -0.67623 | -121.2642 | 0.30852 | 0.31173 | 0.5403 | -121.4412 | 0.069728 | 0.014095 | -0.005985 | 0.1074 | 0.23806 | 0.15884 | -0.21452 | -0.08804 | -0.011918 | 0.60837 | 0.08898 | 0.17702 | -0.008709 | 0.21987 | 121.1386 | -0.21303 | 121.4229 | 121.3472 | 0.20853 | -0.082377 | -0.16159 | 121.6617 | 121.6649 | 121.8935 | 120.6769 | -121.7616 | 121.4605 | 121.5912 | 121.512 | 121.3672 | -0.53495
1906.5938 | 121.6095 | -121.3577 | 0.32959 | 1.4211e-13 | -0.025782 | 0.0011388 | 0.068409 | -0.012279 | 0.059753 | 0.0079357 | -0.0027303 | 0.0047004 | 0.01825 | 0.0345 | 0.0076551 | -120.7539 | -0.67623 | -121.2733 | 0.29478 | 0.29799 | 0.52657 | -121.4412 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.23806 | 0.099323 | -0.22825 | -0.083462 | -0.034808 | 0.60379 | 0.084401 | 0.16786 | -0.031601 | 0.19698 | 121.1295 | -0.22219 | 121.4183 | 121.3517 | 0.22227 | -0.091532 | -0.23027 | 121.6525 | 121.6557 | 121.8843 | 120.6815 | -121.7708 | 121.4651 | 121.5958 | 121.457 | 121.381 | -0.55784
1908.2969 | 121.7789 | -121.3577 | 0.27924 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.067767 | -0.012493 | 0.059539 | 0.015566 | -0.0025167 | 0.0047004 | 0.018463 | 0.034072 | 0.0074415 | -120.7631 | -0.6808 | -121.2779 | 0.29936 | 0.29799 | 0.52199 | -121.4549 | 0.060571 | 0.014095 | -0.001407 | 0.098244 | 0.24264 | 0.13137 | -0.22367 | -0.097199 | 0.020125 | 0.59464 | 0.079823 | 0.17702 | 0.018753 | 0.24275 | 121.1341 | -0.18099 | 121.4183 | 121.3563 | 0.22227 | -0.036599 | -0.14786 | 121.6571 | 121.6557 | 121.8797 | 120.6769 | -121.7342 | 121.456 | 121.6004 | 121.4891 | 121.3718 | -0.50291
1909.9844 | 121.637 | -121.4035 | 0.3067 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.068195 | -0.012493 | 0.059326 | -0.0073253 | -0.0027303 | 0.0051278 | 0.018463 | 0.034072 | 0.0074415 | -120.7768 | -0.68996 | -121.2962 | 0.28105 | 0.28883 | 0.50368 | -121.4687 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.24721 | 0.13137 | -0.22367 | -0.06516 | -0.025655 | 0.62668 | 0.10729 | 0.17245 | -0.017871 | 0.19697 | 121.1798 | -0.20388 | 121.4641 | 121.4021 | 0.22227 | -0.059487 | -0.17533 | 121.6846 | 121.6923 | 121.9072 | 120.7135 | -121.7754 | 121.5063 | 121.6507 | 121.5349 | 121.4268 | -0.53038
1911.6719 | 121.6599 | -121.4035 | 0.27466 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.067981 | -0.011852 | 0.059539 | -0.0073253 | -0.0031575 | 0.0047004 | 0.018463 | 0.034072 | 0.0074415 | -120.7906 | -0.68996 | -121.3191 | 0.27647 | 0.26136 | 0.50368 | -121.4824 | 0.060571 | 0.014095 | 0.003172 | 0.1074 | 0.23806 | 0.062694 | -0.2191 | -0.078896 | 0.001811 | 0.61294 | 0.084394 | 0.16329 | -0.0133 | 0.22902 | 121.1844 | -0.16726 | 121.4641 | 121.4067 | 0.22227 | -0.0366 | -0.21196 | 121.68 | 121.6649 | 121.9072 | 120.7135 | -121.7571 | 121.5109 | 121.6416 | 121.4662 | 121.4176 | -0.49375
1913.4062 | 121.7331 | -121.3715 | 0.27466 | 1.4211e-13 | -0.025782 | 0.0011388 | 0.067981 | -0.012066 | 0.059753 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018036 | 0.034072 | 0.0074415 | -120.8043 | -0.69454 | -121.3145 | 0.26731 | 0.27052 | 0.48994 | -121.4961 | 0.06515 | 0.018674 | -0.005985 | 0.1074 | 0.23806 | 0.13595 | -0.21452 | -0.12468 | -0.007346 | 0.56717 | 0.056929 | 0.18161 | -0.004142 | 0.21528 | 121.1569 | -0.16726 | 121.4366 | 121.3655 | 0.20853 | -0.0366 | -0.13871 | 121.6388 | 121.642 | 121.8614 | 120.6769 | -121.7708 | 121.4789 | 121.6095 | 121.5074 | 121.3901 | -0.48917
1915.1406 | 121.7468 | -121.3806 | 0.26093 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.067981 | -0.011852 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.034286 | 0.0074415 | -120.8043 | -0.7037 | -121.3283 | 0.26731 | 0.24762 | 0.48078 | -121.5053 | 0.055992 | 0.023253 | -0.005985 | 0.098244 | 0.24721 | 0.099323 | -0.2191 | -0.12468 | 0.006387 | 0.57632 | 0.05235 | 0.17703 | -0.013304 | 0.21986 | 121.1615 | -0.16268 | 121.4366 | 121.3746 | 0.21311 | -0.01371 | -0.1616 | 121.6479 | 121.6282 | 121.8614 | 120.6769 | -121.7662 | 121.4789 | 121.6278 | 121.4799 | 121.4039 | -0.48002
1916.8281 | 121.5958 | -121.138 | 0.27008 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.067981 | -0.012066 | 0.059326 | 0.015566 | -0.0029439 | 0.0051278 | 0.01825 | 0.034286 | 0.0072279 | -120.5937 | -0.72201 | -121.1177 | 0.31767 | 0.33004 | 0.54946 | -121.3679 | 0.060571 | 0.03241 | -0.001407 | 0.10282 | 0.23348 | -0.019721 | -0.2191 | -0.22993 | 0.047593 | 0.54431 | 0.020336 | 0.25026 | 0.059961 | 0.27938 | 120.9189 | -0.16726 | 121.1986 | 121.1366 | 0.21769 | -0.036602 | -0.2898 | 121.4557 | 121.468 | 121.6875 | 120.416 | -121.638 | 121.2408 | 121.3715 | 121.1183 | 121.1704 | -0.48918
1918.5469 | 121.6049 | -121.257 | 0.29755 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.067981 | -0.012279 | 0.059326 | 0.0079357 | -0.0029439 | 0.0051278 | 0.01825 | 0.034072 | 0.0076551 | -120.6807 | -0.71743 | -121.2001 | 0.29478 | 0.34378 | 0.55404 | -121.4229 | 0.060571 | 0.018674 | -0.005985 | 0.10282 | 0.24264 | 0.012329 | -0.22367 | -0.16585 | -0.002764 | 0.57634 | 0.056945 | 0.2228 | 0.046232 | 0.25649 | 121.0333 | -0.19472 | 121.3176 | 121.251 | 0.21769 | -0.054909 | -0.28522 | 121.5518 | 121.6008 | 121.8111 | 120.5396 | -121.7204 | 121.3598 | 121.4997 | 121.2693 | 121.2757 | -0.52122
1920.2344 | 121.6507 | -121.2341 | 0.25177 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.067981 | -0.012279 | 0.059539 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.034286 | 0.0074415 | -120.7036 | -0.71743 | -121.223 | 0.27647 | 0.35752 | 0.5632 | -121.3954 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.23348 | -0.051771 | -0.22367 | -0.16127 | 0.024699 | 0.53056 | 0.011166 | 0.17243 | 0.10575 | 0.31143 | 121.0105 | -0.15353 | 121.2947 | 121.2327 | 0.22227 | -0.018291 | -0.30354 | 121.5106 | 121.5916 | 121.7973 | 120.5167 | -121.6472 | 121.3324 | 121.4676 | 121.1824 | 121.2528 | -0.47544
1921.9219 | 121.5683 | -121.3257 | 0.31128 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.068195 | -0.011852 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018463 | 0.034286 | 0.0074415 | -120.7081 | -0.72659 | -121.2367 | 0.28563 | 0.24304 | 0.5632 | -121.4091 | 0.055992 | 0.018674 | -0.005985 | 0.1074 | 0.25179 | -0.042614 | -0.21452 | -0.083453 | -0.025654 | 0.61754 | 0.088984 | 0.17244 | -0.068237 | 0.25192 | 121.1112 | -0.20388 | 121.3817 | 121.3197 | 0.20853 | -0.059485 | -0.35389 | 121.6113 | 121.5687 | 121.8889 | 120.5991 | -121.7204 | 121.4331 | 121.5775 | 121.2831 | 121.3444 | -0.5258
1923.6094 | 121.5958 | -121.3394 | 0.29297 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.067981 | -0.012279 | 0.059539 | 0.0079357 | -0.0029439 | 0.0051278 | 0.01825 | 0.0345 | 0.0072279 | -120.7219 | -0.73575 | -121.2459 | 0.2902 | 0.23846 | 0.5632 | -121.4091 | 0.06515 | 0.027831 | -0.005985 | 0.11198 | 0.23806 | -0.015142 | -0.21452 | -0.06972 | -0.002765 | 0.61753 | 0.093561 | 0.16328 | -0.054506 | 0.27023 | 121.1249 | -0.18099 | 121.4046 | 121.3334 | 0.20853 | -0.054911 | -0.30811 | 121.6296 | 121.5779 | 121.9026 | 120.6037 | -121.7021 | 121.4514 | 121.5775 | 121.3243 | 121.3672 | -0.50748
1925.2812 | 121.7102 | -121.2982 | 0.27466 | 1.4211e-13 | -0.025782 | 0.00092524 | 0.068195 | -0.012279 | 0.059112 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017823 | 0.034286 | 0.0078689 | -120.731 | -0.72659 | -121.2459 | 0.29478 | 0.24304 | 0.51283 | -121.4183 | 0.06515 | 0.018674 | -0.005985 | 0.093665 | 0.24264 | -0.010564 | -0.2191 | -0.12008 | 0.020124 | 0.56718 | 0.052362 | 0.17244 | -0.031616 | 0.23817 | 121.0791 | -0.18099 | 121.3634 | 121.2922 | 0.21311 | -0.032021 | -0.28522 | 121.593 | 121.5413 | 121.8111 | 120.5716 | -121.693 | 121.3919 | 121.5409 | 121.2877 | 121.3169 | -0.49375
1926.9688 | 121.6599 | -121.3257 | 0.29297 | 1.4211e-13 | -0.026209 | 0.0011388 | 0.067981 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018036 | 0.034072 | 0.0074415 | -120.731 | -0.74033 | -121.255 | 0.28563 | 0.26136 | 0.51741 | -121.4275 | 0.06515 | 0.027831 | 0.003172 | 0.1074 | 0.24264 | -0.042614 | -0.2191 | -0.10177 | -0.007344 | 0.59464 | 0.070671 | 0.17244 | -0.031611 | 0.22444 | 121.1066 | -0.18557 | 121.3908 | 121.3289 | 0.22227 | -0.050332 | -0.33558 | 121.6113 | 121.587 | 121.8431 | 120.5854 | -121.7204 | 121.4331 | 121.5683 | 121.2831 | 121.3535 | -0.51206
1928.6562 | 121.7331 | -121.312 | 0.26093 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.068409 | -0.012066 | 0.059539 | -0.0073253 | -0.0027303 | 0.0051278 | 0.018463 | 0.034286 | 0.0074415 | -120.7448 | -0.75406 | -121.2687 | 0.29478 | 0.2522 | 0.51283 | -121.432 | 0.06515 | 0.027831 | -0.001407 | 0.10282 | 0.24264 | -0.065507 | -0.21452 | -0.12008 | 0.033857 | 0.56717 | 0.043203 | 0.16328 | -0.008725 | 0.25191 | 121.0974 | -0.1581 | 121.3771 | 121.3105 | 0.21311 | -0.018288 | -0.32643 | 121.6067 | 121.5642 | 121.8248 | 120.5579 | -121.693 | 121.4148 | 121.5546 | 121.2464 | 121.3398 | -0.47544
1930.375 | 121.6232 | -121.344 | 0.32044 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.068195 | -0.012066 | 0.059539 | -0.0073253 | -0.0029439 | 0.0051278 | 0.018036 | 0.0345 | 0.0074415 | -120.7539 | -0.75406 | -121.2642 | 0.29936 | 0.27967 | 0.52199 | -121.432 | 0.06515 | 0.018674 | -0.001407 | 0.10282 | 0.24721 | -0.0884 | -0.20994 | -0.088037 | -0.021074 | 0.59006 | 0.079825 | 0.16786 | -0.040762 | 0.20155 | 121.1341 | -0.21761 | 121.4091 | 121.3426 | 0.20853 | -0.07322 | -0.40884 | 121.6434 | 121.6237 | 121.866 | 120.5899 | -121.7525 | 121.4468 | 121.5912 | 121.2556 | 121.3627 | -0.53037
1932.0469 | 121.7056 | -121.3348 | 0.28839 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.067981 | -0.012707 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.01825 | 0.034286 | 0.0078689 | -120.7494 | -0.74948 | -121.2733 | 0.29936 | 0.2522 | 0.51283 | -121.4458 | 0.060571 | 0.027831 | 0.003172 | 0.1074 | 0.24721 | -0.074664 | -0.21452 | -0.11093 | 0.01097 | 0.58549 | 0.061513 | 0.17244 | -0.036191 | 0.22444 | 121.1203 | -0.18099 | 121.3954 | 121.338 | 0.21769 | -0.041176 | -0.36306 | 121.6342 | 121.587 | 121.8477 | 120.5854 | -121.7342 | 121.4422 | 121.5821 | 121.2602 | 121.3627 | -0.50291
1933.7188 | 121.7468 | -121.3394 | 0.29297 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.067981 | -0.012066 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.018036 | 0.034286 | 0.0078689 | -120.7585 | -0.77238 | -121.2779 | 0.29478 | 0.2522 | 0.51283 | -121.4549 | 0.06515 | 0.027831 | -0.001407 | 0.10282 | 0.23806 | -0.038035 | -0.21452 | -0.11551 | 0.001813 | 0.58091 | 0.061513 | 0.17702 | -0.040769 | 0.21986 | 121.1249 | -0.19015 | 121.4046 | 121.338 | 0.21311 | -0.054911 | -0.331 | 121.6342 | 121.5916 | 121.8522 | 120.567 | -121.7479 | 121.4422 | 121.5775 | 121.3014 | 121.3672 | -0.50748
1935.4062 | 121.6232 | -121.3806 | 0.31586 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.068409 | -0.012066 | 0.059326 | 0.0079357 | -0.0033713 | 0.0049142 | 0.018036 | 0.034072 | 0.0076551 | -120.7631 | -0.78153 | -121.2871 | 0.29478 | 0.2522 | 0.52199 | -121.4595 | 0.060571 | 0.03241 | -0.005985 | 0.10282 | 0.24264 | -0.005985 | -0.2191 | -0.07889 | -0.021075 | 0.61753 | 0.093554 | 0.17244 | -0.063657 | 0.20613 | 121.1615 | -0.21304 | 121.4412 | 121.3746 | 0.21311 | -0.07322 | -0.32184 | 121.6754 | 121.6328 | 121.9026 | 120.5991 | -121.7754 | 121.4834 | 121.6233 | 121.3746 | 121.413 | -0.53495
1937.0938 | 121.7102 | -121.3669 | 0.29755 | 1.4211e-13 | -0.026636 | 0.00071164 | 0.068195 | -0.012493 | 0.059539 | 0.0079357 | -0.0029439 | 0.0049142 | 0.01825 | 0.034286 | 0.0072279 | -120.7677 | -0.78153 | -121.2962 | 0.29936 | 0.24304 | 0.51283 | -121.4595 | 0.060571 | 0.03241 | 0.003172 | 0.10282 | 0.23806 | -0.019721 | -0.2191 | -0.092623 | 0.001815 | 0.59922 | 0.070665 | 0.16329 | -0.054504 | 0.21529 | 121.1478 | -0.19472 | 121.4275 | 121.3701 | 0.22227 | -0.059488 | -0.31727 | 121.6662 | 121.6099 | 121.8797 | 120.5853 | -121.7571 | 121.4697 | 121.6049 | 121.3472 | 121.3993 | -0.51664
1938.7812 | 121.7606 | -121.2982 | 0.28381 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.067981 | -0.011852 | 0.059112 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018463 | 0.0345 | 0.0078689 | -120.7631 | -0.78611 | -121.2962 | 0.29478 | 0.27052 | 0.52199 | -121.4549 | 0.060571 | 0.023253 | -0.005985 | 0.10282 | 0.24721 | -0.015142 | -0.2191 | -0.15671 | 0.010969 | 0.53513 | 0.002001 | 0.15871 | -0.013297 | 0.23818 | 121.0791 | -0.18099 | 121.3588 | 121.2922 | 0.21311 | -0.036598 | -0.29895 | 121.593 | 121.5687 | 121.8202 | 120.5121 | -121.7387 | 121.401 | 121.5454 | 121.2831 | 121.3215 | -0.50291
1940.5156 | 121.788 | -121.3486 | 0.27466 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.068409 | -0.012279 | 0.059539 | 0.00030522 | -0.0027303 | 0.0047004 | 0.018036 | 0.034713 | 0.0074415 | -120.7722 | -0.79527 | -121.2962 | 0.30394 | 0.27509 | 0.51741 | -121.4641 | 0.060571 | 0.018674 | -0.005985 | 0.10282 | 0.23806 | -0.015142 | -0.20994 | -0.11551 | 0.029281 | 0.57633 | 0.052355 | 0.16787 | 0.000436 | 0.24275 | 121.1386 | -0.17184 | 121.4091 | 121.3426 | 0.20395 | -0.0366 | -0.2898 | 121.6525 | 121.6237 | 121.866 | 120.5533 | -121.7387 | 121.4514 | 121.5866 | 121.3334 | 121.3672 | -0.48459
1942.2031 | 121.7285 | -121.2845 | 0.25635 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.068195 | -0.011852 | 0.058898 | 0.00030522 | -0.0033713 | 0.0049142 | 0.018463 | 0.034072 | 0.0074415 | -120.7173 | -0.8319 | -121.2321 | 0.31767 | 0.3392 | 0.55404 | -121.487 | 0.060571 | 0.018674 | -0.005985 | 0.10282 | 0.23806 | -0.083821 | -0.21452 | -0.20249 | 0.061326 | 0.56718 | 0.052363 | 0.25486 | 0.082851 | 0.29769 | 121.07 | -0.15353 | 121.3451 | 121.2785 | 0.20853 | -0.01829 | -0.34017 | 121.6022 | 121.6237 | 121.8385 | 120.4526 | -121.7433 | 121.3873 | 121.5225 | 121.2007 | 121.3032 | -0.47086
1943.9062 | 121.6599 | -121.3211 | 0.28381 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.01825 | 0.0345 | 0.0074415 | -120.7356 | -0.80443 | -121.2642 | 0.27647 | 0.34836 | 0.55404 | -121.432 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.24264 | -0.047193 | -0.22825 | -0.11092 | -0.007344 | 0.58549 | 0.056937 | 0.16786 | 0.064544 | 0.27023 | 121.0929 | -0.17641 | 121.3863 | 121.3151 | 0.22227 | -0.041176 | -0.33101 | 121.5976 | 121.6695 | 121.8751 | 120.5167 | -121.7158 | 121.4285 | 121.5637 | 121.2739 | 121.3444 | -0.51206
1945.6094 | 121.637 | -121.3486 | 0.28381 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.068195 | -0.012066 | 0.059753 | 0.00030522 | -0.0023031 | 0.0049142 | 0.01825 | 0.0345 | 0.0074415 | -120.7539 | -0.81359 | -121.2825 | 0.28563 | 0.27052 | 0.55404 | -121.4458 | 0.060571 | 0.018674 | -0.005985 | 0.098244 | 0.24264 | -0.051771 | -0.22367 | -0.097196 | 0.001812 | 0.59464 | 0.066089 | 0.16329 | -0.013297 | 0.27023 | 121.1249 | -0.18557 | 121.4091 | 121.3426 | 0.21769 | -0.041176 | -0.33558 | 121.6342 | 121.6191 | 121.9026 | 120.535 | -121.7296 | 121.4468 | 121.5912 | 121.2968 | 121.3672 | -0.50749
1947.2812 | 121.7606 | -121.3211 | 0.2655 | 1.4211e-13 | -0.026209 | 0.00092524 | 0.067981 | -0.012066 | 0.059539 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018036 | 0.034286 | 0.0076551 | -120.7677 | -0.82274 | -121.2871 | 0.28563 | 0.26136 | 0.5632 | -121.4595 | 0.055992 | 0.027831 | -0.001407 | 0.1074 | 0.25179 | -0.015142 | -0.2191 | -0.1384 | 0.020122 | 0.55344 | 0.034045 | 0.17244 | -0.004145 | 0.29769 | 121.102 | -0.1581 | 121.3771 | 121.3197 | 0.21769 | -0.013709 | -0.28064 | 121.6067 | 121.5825 | 121.8843 | 120.4984 | -121.725 | 121.4285 | 121.5729 | 121.306 | 121.3489 | -0.4846
1948.9688 | 121.6461 | -121.3943 | 0.29297 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.068622 | -0.012066 | 0.059326 | 0.00030522 | -0.0029439 | 0.0049142 | 0.01825 | 0.034286 | 0.0074415 | -120.7768 | -0.81816 | -121.3008 | 0.27647 | 0.23388 | 0.55404 | -121.4641 | 0.055992 | 0.027831 | -0.001407 | 0.1074 | 0.24264 | -0.015142 | -0.20994 | -0.069736 | -0.0165 | 0.61752 | 0.093552 | 0.16329 | -0.059085 | 0.26107 | 121.1844 | -0.18557 | 121.4503 | 121.3929 | 0.20853 | -0.050332 | -0.30811 | 121.6708 | 121.6282 | 121.9484 | 120.5762 | -121.7571 | 121.5017 | 121.637 | 121.3792 | 121.4222 | -0.50291
1950.6562 | 121.582 | -121.2479 | 0.21515 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.068195 | -0.012279 | 0.059326 | 0.00030522 | -0.0027303 | 0.0051278 | 0.017823 | 0.034713 | 0.0076551 | -120.7036 | -0.87311 | -121.2184 | 0.25816 | 0.27509 | 0.48536 | -121.4732 | 0.060571 | 0.027831 | -0.010564 | 0.1074 | 0.24721 | -0.092979 | -0.2191 | -0.22538 | 0.043006 | 0.54429 | 0.029477 | 0.25485 | 0.059945 | 0.27021 | 121.0288 | -0.10775 | 121.3084 | 121.2373 | 0.20853 | 0.032066 | -0.30813 | 121.506 | 121.523 | 121.7332 | 120.3748 | -121.6884 | 121.3553 | 121.4951 | 121.1549 | 121.2757 | -0.43424
1952.3281 | 121.7194 | -121.3028 | 0.21515 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.068409 | -0.012279 | 0.059112 | -0.0073253 | -0.0027303 | 0.0047004 | 0.018036 | 0.0345 | 0.0074415 | -120.7402 | -0.86395 | -121.2687 | 0.23526 | 0.29799 | 0.50825 | -121.4824 | 0.060571 | 0.036989 | -0.005985 | 0.10282 | 0.25179 | -0.079243 | -0.2191 | -0.1796 | 0.020114 | 0.5626 | 0.034047 | 0.21365 | 0.08284 | 0.2931 | 121.0837 | -0.11233 | 121.3634 | 121.2968 | 0.21311 | 0.036645 | -0.29439 | 121.5381 | 121.6008 | 121.811 | 120.4388 | -121.6975 | 121.4056 | 121.5546 | 121.2236 | 121.3398 | -0.43424
1954.0156 | 121.6507 | -121.3486 | 0.23346 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.068195 | -0.011852 | 0.059112 | 0.00030522 | -0.0027303 | 0.0044868 | 0.01825 | 0.034286 | 0.0074415 | -120.7722 | -0.84564 | -121.2871 | 0.23526 | 0.29799 | 0.50825 | -121.4641 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.24264 | -0.051771 | -0.2191 | -0.11551 | 0.001804 | 0.57633 | 0.061511 | 0.17702 | 0.06453 | 0.2748 | 121.1295 | -0.13064 | 121.4091 | 121.3472 | 0.21769 | 0.009178 | -0.28523 | 121.5838 | 121.6466 | 121.8568 | 120.5029 | -121.6975 | 121.4514 | 121.5912 | 121.2968 | 121.3718 | -0.45255
1955.7031 | 121.7194 | -121.3531 | 0.20142 | 1.4211e-13 | -0.026423 | 0.0011388 | 0.067981 | -0.012066 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.018036 | 0.0345 | 0.0074415 | -120.786 | -0.85479 | -121.31 | 0.23069 | 0.1881 | 0.50825 | -121.4687 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.23806 | -0.097557 | -0.2191 | -0.11551 | 0.029269 | 0.56717 | 0.043197 | 0.15871 | -0.013321 | 0.30684 | 121.1341 | -0.094015 | 121.4137 | 121.3472 | 0.21311 | 0.036642 | -0.29897 | 121.5838 | 121.5412 | 121.8614 | 120.4984 | -121.6701 | 121.4605 | 121.5912 | 121.2556 | 121.3764 | -0.42051
1957.3906 | 121.7468 | -121.3486 | 0.19684 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.068409 | -0.012066 | 0.059326 | 0.015566 | -0.0027303 | 0.0051278 | 0.018463 | 0.034713 | 0.0074415 | -120.7951 | -0.85479 | -121.3145 | 0.23984 | 0.18352 | 0.51283 | -121.4732 | 0.06515 | 0.027831 | -0.001407 | 0.1074 | 0.23348 | -0.060928 | -0.21452 | -0.12467 | 0.043004 | 0.55343 | 0.034041 | 0.15871 | -0.013322 | 0.31599 | 121.1341 | -0.089437 | 121.4137 | 121.3472 | 0.21311 | 0.036641 | -0.25777 | 121.5884 | 121.5321 | 121.8614 | 120.4938 | -121.6701 | 121.456 | 121.5821 | 121.2876 | 121.3764 | -0.41135
1959.0781 | 121.6187 | -121.4081 | 0.29297 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.068409 | -0.012066 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.01825 | 0.0345 | 0.0076551 | -120.786 | -0.86395 | -121.3191 | 0.25358 | 0.20641 | 0.52657 | -121.5007 | 0.060571 | 0.023253 | 0.003172 | 0.11198 | 0.24721 | -0.079243 | -0.2191 | -0.092634 | -0.039392 | 0.6221 | 0.088972 | 0.18161 | -0.086558 | 0.2336 | 121.189 | -0.18099 | 121.4687 | 121.4113 | 0.22227 | -0.045754 | -0.37221 | 121.6617 | 121.6145 | 121.9346 | 120.5441 | -121.7937 | 121.5201 | 121.6553 | 121.3288 | 121.4313 | -0.51206
1960.7656 | 121.7468 | -121.3531 | 0.23804 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.067981 | -0.011852 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.01825 | 0.034286 | 0.0074415 | -120.7814 | -0.86853 | -121.31 | 0.249 | 0.21557 | 0.4762 | -121.5053 | 0.060571 | 0.018674 | -0.005985 | 0.10282 | 0.24264 | 0.016908 | -0.21452 | -0.15215 | 0.010961 | 0.57175 | 0.043197 | 0.19534 | -0.022469 | 0.23817 | 121.1386 | -0.13522 | 121.4137 | 121.3472 | 0.20853 | 0.0046 | -0.22113 | 121.6021 | 121.5687 | 121.8294 | 120.4846 | -121.7433 | 121.456 | 121.5958 | 121.3701 | 121.3718 | -0.45255
1962.5 | 121.7056 | -121.3943 | 0.23346 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.068195 | -0.012066 | 0.058898 | 0.023196 | -0.0029439 | 0.0049142 | 0.018036 | 0.0345 | 0.0076551 | -120.7997 | -0.87769 | -121.3283 | 0.25358 | 0.21557 | 0.47163 | -121.5007 | 0.06515 | 0.027831 | 0.003172 | 0.098244 | 0.24264 | -0.0243 | -0.21452 | -0.10637 | 0.020118 | 0.59463 | 0.066083 | 0.17245 | -0.017891 | 0.23817 | 121.1798 | -0.13522 | 121.4595 | 121.3975 | 0.21769 | 0.009178 | -0.25776 | 121.6479 | 121.6099 | 121.866 | 120.5167 | -121.7342 | 121.4926 | 121.637 | 121.37 | 121.4222 | -0.44798
1964.1719 | 121.6782 | -121.4218 | 0.23804 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.068195 | -0.012493 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017823 | 0.0345 | 0.0072279 | -120.8135 | -0.88684 | -121.3374 | 0.249 | 0.19725 | 0.47163 | -121.5145 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.23806 | -0.10214 | -0.22367 | -0.092638 | 0.010961 | 0.60836 | 0.084392 | 0.17703 | -0.040784 | 0.23359 | 121.1981 | -0.13522 | 121.4824 | 121.4204 | 0.22227 | 2.1e-05 | -0.34017 | 121.6708 | 121.6191 | 121.8934 | 120.535 | -121.7525 | 121.5246 | 121.6599 | 121.3197 | 121.4451 | -0.46171
1965.8594 | 121.7743 | -121.3806 | 0.2243 | 1.4211e-13 | -0.02685 | 0.00092524 | 0.067981 | -0.012279 | 0.059326 | 0.0079357 | -0.0027303 | 0.0047004 | 0.017823 | 0.0345 | 0.0076551 | -120.8043 | -0.89142 | -121.3328 | 0.25358 | 0.22931 | 0.4762 | -121.5557 | 0.06515 | 0.023253 | -0.001407 | 0.11198 | 0.24264 | 0.016908 | -0.2191 | -0.17505 | 0.029273 | 0.57632 | 0.047771 | 0.22282 | 0.005001 | 0.2519 | 121.1615 | -0.11233 | 121.4458 | 121.3792 | 0.21769 | 0.018333 | -0.2074 | 121.6342 | 121.6099 | 121.8568 | 120.4892 | -121.78 | 121.4926 | 121.6233 | 121.3975 | 121.4039 | -0.4434
1967.5781 | 121.7194 | -121.431 | 0.2243 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.068195 | -0.012279 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017823 | 0.034286 | 0.0074415 | -120.8226 | -0.896 | -121.342 | 0.24442 | 0.21557 | 0.46247 | -121.5236 | 0.060571 | 0.018674 | -0.010564 | 0.098244 | 0.24264 | 0.030644 | -0.22367 | -0.092641 | 0.020116 | 0.60836 | 0.088969 | 0.18161 | -0.008736 | 0.23816 | 121.2073 | -0.12606 | 121.4915 | 121.4204 | 0.21311 | 0.018333 | -0.19366 | 121.6754 | 121.6465 | 121.8934 | 120.535 | -121.7479 | 121.5292 | 121.6736 | 121.4616 | 121.4496 | -0.44798
1969.2656 | 121.701 | -121.4264 | 0.2655 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.068409 | -0.012066 | 0.059326 | 0.0079357 | -0.0025167 | 0.0049142 | 0.018036 | 0.034286 | 0.0076551 | -120.8272 | -0.90516 | -121.3512 | 0.24442 | 0.20641 | 0.47163 | -121.519 | 0.060571 | 0.018674 | 0.003172 | 0.1074 | 0.23806 | -0.0243 | -0.21452 | -0.092639 | -0.021083 | 0.59921 | 0.075235 | 0.16787 | -0.059092 | 0.20612 | 121.2119 | -0.1581 | 121.487 | 121.4296 | 0.21769 | -0.027445 | -0.2898 | 121.6708 | 121.6328 | 121.898 | 120.5212 | -121.7845 | 121.5338 | 121.6645 | 121.4021 | 121.4451 | -0.48002
1970.9531 | 121.6553 | -121.3806 | 0.31586 | 1.4211e-13 | -0.026636 | 0.0011388 | 0.067767 | -0.012279 | 0.059539 | -0.0073253 | -0.0025167 | 0.0047004 | 0.018036 | 0.034286 | 0.0076551 | -120.7768 | -0.90516 | -121.3008 | 0.30394 | 0.24304 | 0.52657 | -121.5053 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.23806 | -0.060928 | -0.2191 | -0.12468 | -0.011918 | 0.60379 | 0.079819 | 0.2045 | -0.072815 | 0.21071 | 121.1615 | -0.20846 | 121.4412 | 121.3746 | 0.21311 | -0.077799 | -0.37678 | 121.6846 | 121.6237 | 121.9072 | 120.4755 | -121.8212 | 121.488 | 121.6187 | 121.3197 | 121.4039 | -0.53495
1972.6562 | 121.7606 | -121.3943 | 0.23346 | 1.4211e-13 | -0.026636 | 0.00071164 | 0.068195 | -0.012279 | 0.059326 | 0.0079357 | -0.0025167 | 0.0049142 | 0.017823 | 0.0345 | 0.0076551 | -120.8135 | -0.91889 | -121.342 | 0.26273 | 0.22931 | 0.48536 | -121.5282 | 0.06515 | 0.03241 | -0.001407 | 0.10282 | 0.23806 | -0.001407 | -0.21452 | -0.13384 | 0.029275 | 0.5809 | 0.052348 | 0.18619 | -0.004154 | 0.2519 | 121.1798 | -0.13064 | 121.4595 | 121.3929 | 0.21311 | 0.004599 | -0.23487 | 121.6571 | 121.6237 | 121.8797 | 120.4755 | -121.7616 | 121.4972 | 121.6324 | 121.3929 | 121.4268 | -0.44798
1974.3281 | 121.7834 | -121.3348 | 0.27008 | 1.4211e-13 | -0.025995 | 0.00092524 | 0.067981 | -0.012066 | 0.059326 | 0.0079357 | -0.0027303 | 0.0051278 | 0.01825 | 0.034286 | 0.0074415 | -120.7997 | -0.91889 | -121.3237 | 0.28105 | 0.24304 | 0.50368 | -121.5419 | 0.069728 | 0.018674 | -0.005985 | 0.10282 | 0.24721 | 0.035222 | -0.2191 | -0.20709 | 0.010966 | 0.53512 | 0.011152 | 0.21824 | -0.027039 | 0.23359 | 121.1157 | -0.16726 | 121.4046 | 121.3289 | 0.21311 | -0.022866 | -0.23486 | 121.6159 | 121.5779 | 121.8385 | 120.4159 | -121.812 | 121.4377 | 121.5821 | 121.3701 | 121.3535 | -0.48918
1976.0156 | 120.9778 | -119.1422 | 1.7212 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.067554 | -0.012493 | 0.058898 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017823 | 0.034713 | 0.0074415 | -117.5445 | -1.0013 | -117.9724 | 2.6572 | 2.6149 | 2.9074 | -118.268 | 0.060571 | 0.018674 | -0.005985 | 0.11198 | 0.24264 | -0.083821 | -0.2191 | 0.87416 | 0.93604 | 1.5977 | 1.1698 | 0.29561 | 0.89373 | 1.1863 | 118.9231 | -1.6092 | 119.2027 | 119.1362 | 0.21311 | -1.4786 | -1.805 | 121.7994 | 121.7571 | 122.0496 | 118.1408 | -119.9892 | 119.2541 | 119.3848 | 119.0583 | 119.1608 | -1.9403
1977.7031 | 121.344 | -120.3415 | 0.97504 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.067767 | -0.012493 | 0.058685 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017823 | 0.034286 | 0.0076551 | -119.8383 | -0.96926 | -120.3531 | 0.86708 | 0.9482 | 1.1538 | -120.6078 | 0.060571 | 0.027831 | -0.005985 | 0.098244 | 0.24264 | -0.065507 | -0.22367 | -0.26633 | -0.10796 | 0.50324 | -0.0116 | 0.25473 | -0.026841 | 0.1788 | 120.1178 | -0.87679 | 120.4021 | 120.3355 | 0.21769 | -0.7324 | -1.0405 | 121.2086 | 121.2897 | 121.4953 | 119.3722 | -121.5829 | 120.4397 | 120.5841 | 120.276 | 120.3693 | -1.1987
1979.4062 | 121.4493 | -120.6848 | 0.71411 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.067554 | -0.012279 | 0.059539 | 0.00030522 | -0.0029439 | 0.0051278 | 0.01825 | 0.0345 | 0.0076551 | -120.0626 | -0.96926 | -120.5912 | 0.72973 | 0.80167 | 1.0256 | -120.7544 | 0.06515 | 0.018674 | -0.005985 | 0.10282 | 0.24264 | -0.11129 | -0.2191 | -0.069536 | 0.015618 | 0.62222 | 0.093652 | 0.16319 | 0.08756 | 0.31152 | 120.4657 | -0.61129 | 120.75 | 120.6788 | 0.21311 | -0.47147 | -0.8254 | 121.4145 | 121.4865 | 121.7105 | 119.7156 | -121.4685 | 120.7876 | 120.9275 | 120.5735 | 120.7035 | -0.93321
1981.1094 | 121.3989 | -120.5933 | 0.87433 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.067767 | -0.012279 | 0.059112 | -0.0073253 | -0.0029439 | 0.0049142 | 0.01825 | 0.034713 | 0.0072279 | -119.971 | -0.96926 | -120.4904 | 0.86708 | 0.86578 | 1.1493 | -120.6765 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.23806 | -0.12503 | -0.2191 | -0.083247 | -0.007248 | 0.62223 | 0.10282 | 0.18607 | -0.008553 | 0.27493 | 120.3742 | -0.76693 | 120.6584 | 120.5873 | 0.21311 | -0.63627 | -0.99936 | 121.4603 | 121.459 | 121.7425 | 119.624 | -121.5508 | 120.7007 | 120.8313 | 120.4682 | 120.6165 | -1.0934
1982.7969 | 121.5775 | -120.6573 | 0.74616 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.067981 | -0.012707 | 0.059539 | 0.00030522 | -0.0029439 | 0.0047004 | 0.018036 | 0.034286 | 0.0074415 | -120.0626 | -0.97841 | -120.5866 | 0.79841 | 0.80625 | 1.076 | -120.7635 | 0.06515 | 0.027831 | -0.001407 | 0.10282 | 0.23348 | -0.079243 | -0.2191 | -0.10616 | 0.05225 | 0.59475 | 0.070765 | 0.17692 | 0.060095 | 0.32985 | 120.4383 | -0.64333 | 120.7225 | 120.6559 | 0.21769 | -0.51268 | -0.8254 | 121.4558 | 121.4636 | 121.7334 | 119.6789 | -121.5097 | 120.7602 | 120.8908 | 120.5781 | 120.6852 | -0.96525
1984.4844 | 121.6049 | -120.6894 | 0.71869 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.068409 | -0.012279 | 0.059326 | 0.0079357 | -0.0031575 | 0.0049142 | 0.01825 | 0.034286 | 0.0074415 | -120.0855 | -0.98299 | -120.6141 | 0.84419 | 0.85662 | 1.0668 | -120.8688 | 0.06515 | 0.023253 | -0.005985 | 0.10282 | 0.24264 | -0.0884 | -0.21452 | -0.17943 | 0.1255 | 0.6039 | 0.075338 | 0.25477 | 0.13793 | 0.34815 | 120.4749 | -0.61587 | 120.7545 | 120.6834 | 0.20853 | -0.47605 | -0.80709 | 121.5336 | 121.546 | 121.7562 | 119.7064 | -121.5875 | 120.7922 | 120.932 | 120.601 | 120.7126 | -0.93321
1986.1719 | 121.6278 | -120.8176 | 0.54016 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.067981 | -0.011852 | 0.059326 | -0.0073253 | -0.0029439 | 0.0049142 | 0.017823 | 0.034286 | 0.0070143 | -120.2732 | -0.99215 | -120.8018 | 0.62443 | 0.69636 | 0.91117 | -121.0474 | 0.06515 | 0.027831 | -0.010564 | 0.10282 | 0.25179 | -0.11587 | -0.22367 | -0.22984 | 0.084265 | 0.54436 | 0.015803 | 0.24564 | 0.15619 | 0.37101 | 120.5939 | -0.43734 | 120.8827 | 120.807 | 0.21311 | -0.28837 | -0.65603 | 121.442 | 121.5139 | 121.7287 | 119.8254 | -121.5876 | 120.9204 | 121.0694 | 120.7017 | 120.8454 | -0.76383
1987.8438 | 121.6003 | -120.8313 | 0.59509 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0031575 | 0.0044868 | 0.01825 | 0.034286 | 0.0072279 | -120.3831 | -1.0105 | -120.9071 | 0.5237 | 0.6002 | 0.81044 | -121.084 | 0.06515 | 0.027831 | -0.005985 | 0.11198 | 0.24264 | -0.092979 | -0.2191 | -0.25273 | -0.071391 | 0.44822 | -0.075765 | 0.17697 | 0.005105 | 0.21535 | 120.6122 | -0.48311 | 120.8964 | 120.8253 | 0.21311 | -0.35246 | -0.68807 | 121.355 | 121.4315 | 121.6417 | 119.8208 | -121.6791 | 120.9433 | 121.0739 | 120.7383 | 120.8591 | -0.81419
1989.5156 | 121.6553 | -121.019 | 0.45319 | 1.4211e-13 | -0.02685 | 0.00071164 | 0.067981 | -0.012279 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.018036 | 0.0345 | 0.0072279 | -120.4289 | -1.0059 | -120.962 | 0.48707 | 0.47657 | 0.76924 | -121.1344 | 0.06515 | 0.018674 | -0.005985 | 0.10282 | 0.24721 | -0.074664 | -0.2191 | -0.11542 | 0.033889 | 0.59011 | 0.056979 | 0.1724 | 0.023381 | 0.31605 | 120.7999 | -0.35036 | 121.0841 | 121.013 | 0.21311 | -0.20597 | -0.52785 | 121.5061 | 121.4955 | 121.7882 | 120.0131 | -121.5876 | 121.1218 | 121.2662 | 120.9443 | 121.0377 | -0.67228
1991.2344 | 121.5225 | -121.1014 | 0.49439 | 1.4211e-13 | -0.026636 | 0.00071164 | 0.067981 | -0.012279 | 0.058898 | 0.00030522 | -0.0031575 | 0.0047004 | 0.01825 | 0.034286 | 0.0074415 | -120.4518 | -1.0105 | -120.9849 | 0.46876 | 0.44909 | 0.75092 | -121.1573 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.23806 | -0.070086 | -0.2191 | -0.055917 | -0.025624 | 0.64962 | 0.11648 | 0.1724 | -0.045291 | 0.25654 | 120.8823 | -0.38698 | 121.1619 | 121.1 | 0.21769 | -0.25633 | -0.56447 | 121.5701 | 121.5505 | 121.8523 | 120.0909 | -121.6517 | 121.2088 | 121.3394 | 121.0313 | 121.1246 | -0.71348
1992.9219 | 121.6049 | -121.1151 | 0.40741 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.067767 | -0.012279 | 0.059112 | -0.0073253 | -0.0031575 | 0.0049142 | 0.01825 | 0.034927 | 0.0076551 | -120.525 | -0.98299 | -121.049 | 0.4184 | 0.37583 | 0.70513 | -121.2168 | 0.055992 | 0.018674 | -0.005985 | 0.10282 | 0.23806 | -0.12503 | -0.22367 | -0.10171 | 0.010989 | 0.5901 | 0.066122 | 0.16783 | -0.031579 | 0.29772 | 120.8914 | -0.30459 | 121.1711 | 121.1091 | 0.21769 | -0.16935 | -0.53244 | 121.5335 | 121.4909 | 121.8202 | 120.1321 | -121.6242 | 121.2179 | 121.3532 | 120.9901 | 121.1338 | -0.63108
1994.625 | 121.6461 | -121.106 | 0.39368 | 1.4211e-13 | -0.026636 | 0.00071164 | 0.068409 | -0.012066 | 0.058898 | 0.0079357 | -0.0027303 | 0.0051278 | 0.018036 | 0.034286 | 0.0074415 | -120.5021 | -0.99215 | -121.0307 | 0.44129 | 0.41704 | 0.72803 | -121.1893 | 0.051413 | 0.023253 | -0.005985 | 0.10282 | 0.23806 | -0.074664 | -0.22367 | -0.083391 | 0.047614 | 0.60384 | 0.07528 | 0.15867 | 0.023364 | 0.33435 | 120.8823 | -0.29085 | 121.1574 | 121.1 | 0.21769 | -0.15562 | -0.46834 | 121.5472 | 121.523 | 121.834 | 120.1138 | -121.583 | 121.2088 | 121.344 | 121.0313 | 121.1292 | -0.61735
1996.3438 | 121.7056 | -121.0739 | 0.44861 | 1.4211e-13 | -0.026636 | 0.00092524 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0029439 | 0.0049142 | 0.01825 | 0.0345 | 0.0072279 | -120.4609 | -1.0013 | -120.9849 | 0.49165 | 0.49488 | 0.73261 | -121.1619 | 0.055992 | 0.023253 | -0.005985 | 0.098244 | 0.24264 | -0.019721 | -0.2191 | -0.087961 | 0.043045 | 0.613 | 0.08902 | 0.17698 | 0.046275 | 0.284 | 120.8548 | -0.35036 | 121.1299 | 121.0679 | 0.21311 | -0.20597 | -0.46833 | 121.5656 | 121.5688 | 121.8065 | 120.0726 | -121.6105 | 121.1722 | 121.3166 | 121.0542 | 121.0972 | -0.6677
1998.0312 | 121.6187 | -120.4514 | 0.93842 | 1.4211e-13 | -0.026423 | 0.00071164 | 0.067981 | -0.012066 | 0.059326 | 0.015566 | -0.0027303 | 0.0049142 | 0.01825 | 0.034713 | 0.0074415 | -120.493 | -0.99215 | -121.0261 | 0.47334 | 0.4262 | 0.70513 | -121.2122 | 0.069728 | 0.027831 | -0.005985 | 0.10282 | 0.24264 | -0.019721 | -0.2191 | -0.76089 | -0.46508 | -0.041609 | -0.57474 | 0.18614 | -0.51222 | -0.23328 | 120.2323 | -0.83559 | 120.5211 | 120.4454 | 0.21311 | -0.69578 | -0.95814 | 120.9247 | 120.8776 | 121.1565 | 119.4592 | -122.1507 | 120.5542 | 120.694 | 120.4316 | 120.4792 | -1.1575
1999.7188 | 121.6049 | -121.0556 | 0.54474 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.067981 | -0.012279 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017823 | 0.034713 | 0.0074415 | -120.4289 | -0.99673 | -120.9528 | 0.53744 | 0.53609 | 0.77381 | -121.1893 | 0.055992 | 0.023253 | -0.005985 | 0.098244 | 0.24264 | -0.042614 | -0.22367 | -0.13374 | -0.007302 | 0.62674 | 0.10276 | 0.2365 | -0.008646 | 0.22907 | 120.8319 | -0.44649 | 121.1116 | 121.0496 | 0.21769 | -0.3021 | -0.58735 | 121.593 | 121.5917 | 121.8294 | 120.0589 | -121.7341 | 121.1538 | 121.2982 | 121.013 | 121.0789 | -0.76841
2001.4531 | 121.6095 | -121.0602 | 0.50354 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.068195 | -0.012066 | 0.059326 | -0.0073253 | -0.0029439 | 0.0049142 | 0.01825 | 0.0345 | 0.0072279 | -120.4884 | -1.0059 | -121.0124 | 0.49165 | 0.44451 | 0.72345 | -121.2214 | 0.055992 | 0.027831 | -0.005985 | 0.1074 | 0.24264 | -0.065507 | -0.22367 | -0.16122 | -0.011887 | 0.57179 | 0.047817 | 0.20904 | -0.059025 | 0.21991 | 120.8365 | -0.39614 | 121.1162 | 121.0542 | 0.21769 | -0.2609 | -0.56905 | 121.5518 | 121.5047 | 121.7836 | 120.0543 | -121.7249 | 121.1676 | 121.3028 | 120.9947 | 121.088 | -0.72721
2003.1406 | 121.701 | -120.7718 | 0.80566 | 1.4211e-13 | -0.02685 | 0.00071164 | 0.067981 | -0.012493 | 0.059539 | 0.0079357 | -0.0029439 | 0.0053414 | 0.01825 | 0.0345 | 0.0076551 | -120.0077 | -1.0013 | -120.5408 | 0.95865 | 0.91156 | 1.1996 | -120.7681 | 0.060571 | 0.018674 | 0.003172 | 0.098244 | 0.23806 | -0.0884 | -0.22367 | 0.003703 | 0.15298 | 0.76413 | 0.23099 | 0.22729 | 0.1059 | 0.39396 | 120.5481 | -0.70742 | 120.8324 | 120.775 | 0.22685 | -0.56761 | -0.89406 | 121.7304 | 121.6834 | 121.9714 | 119.7705 | -121.5738 | 120.87 | 121.0098 | 120.6834 | 120.7905 | -1.0293
2004.9688 | 121.6965 | -121.138 | 0.39825 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.068195 | -0.012066 | 0.059326 | 0.00030522 | -0.0027303 | 0.0047004 | 0.01825 | 0.034713 | 0.0074415 | -120.5845 | -1.0379 | -121.1268 | 0.39551 | 0.36667 | 0.67766 | -121.2535 | 0.055992 | 0.027831 | -0.001407 | 0.10282 | 0.24264 | -0.11587 | -0.22367 | -0.11545 | -0.002747 | 0.55347 | 0.011179 | 0.12663 | -0.031581 | 0.27941 | 120.9143 | -0.29543 | 121.194 | 121.1366 | 0.22227 | -0.15562 | -0.51413 | 121.5335 | 121.5047 | 121.8157 | 120.1001 | -121.6517 | 121.2408 | 121.3806 | 121.0221 | 121.1658 | -0.62193
2006.8125 | 121.637 | -121.1151 | 0.43945 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.067767 | -0.012279 | 0.059326 | 0.0079357 | -0.0029439 | 0.0053414 | 0.01825 | 0.034927 | 0.0072279 | -120.5296 | -1.0288 | -121.0627 | 0.46418 | 0.42162 | 0.70056 | -121.2397 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.25179 | -0.070086 | -0.2191 | -0.1246 | 0.02473 | 0.58552 | 0.052387 | 0.17699 | -0.017833 | 0.2611 | 120.896 | -0.33663 | 121.1757 | 121.1137 | 0.21769 | -0.18766 | -0.50954 | 121.5793 | 121.5367 | 121.8157 | 120.0863 | -121.6792 | 121.2179 | 121.3669 | 121.045 | 121.1384 | -0.65855
2008.6719 | 121.6782 | -121.0693 | 0.48981 | 1.4211e-13 | -0.02685 | 0.00071164 | 0.068195 | -0.011852 | 0.059326 | 0.00030522 | -0.0031575 | 0.0047004 | 0.01825 | 0.034713 | 0.0072279 | -120.4426 | -1.0379 | -120.9757 | 0.56033 | 0.54067 | 0.79671 | -121.1665 | 0.055992 | 0.023253 | -0.005985 | 0.10282 | 0.24721 | -0.0884 | -0.2191 | -0.097118 | 0.070522 | 0.62673 | 0.093598 | 0.19072 | 0.050865 | 0.3069 | 120.8502 | -0.38699 | 121.1253 | 121.0634 | 0.21311 | -0.24259 | -0.57821 | 121.6297 | 121.61 | 121.866 | 120.0314 | -121.6563 | 121.1722 | 121.3166 | 120.9809 | 121.0926 | -0.7089
2010.7188 | 121.7331 | -121.1472 | 0.38452 | 1.4211e-13 | -0.02685 | 0.00092524 | 0.068195 | -0.012279 | 0.059326 | 0.00030522 | -0.0027303 | 0.0047004 | 0.018036 | 0.034286 | 0.0070143 | -120.5387 | -1.0471 | -121.0765 | 0.46876 | 0.43078 | 0.70056 | -121.2855 | 0.055992 | 0.018674 | -0.005985 | 0.098244 | 0.24264 | -0.12045 | -0.21452 | -0.13835 | 0.08424 | 0.60841 | 0.070696 | 0.20905 | 0.046257 | 0.31603 | 120.9326 | -0.28628 | 121.2031 | 121.1412 | 0.20853 | -0.14188 | -0.50497 | 121.6159 | 121.5779 | 121.8477 | 120.1001 | -121.67 | 121.2454 | 121.3898 | 121.0267 | 121.1658 | -0.59904
2012.6875 | 121.5912 | -121.2936 | 0.38452 | 1.4211e-13 | -0.027064 | 0.00049784 | 0.067981 | -0.012066 | 0.059112 | 0.015566 | -0.0029439 | 0.0049142 | 0.01825 | 0.034713 | 0.0072279 | -120.6395 | -1.0425 | -121.168 | 0.38177 | 0.34378 | 0.60898 | -121.3405 | 0.060571 | 0.027831 | -0.001407 | 0.10282 | 0.24264 | -0.051771 | -0.21452 | -0.046813 | -0.002749 | 0.65417 | 0.12561 | 0.17243 | -0.040743 | 0.22446 | 121.0791 | -0.2817 | 121.3542 | 121.2922 | 0.21311 | -0.14188 | -0.43629 | 121.6754 | 121.6374 | 121.9026 | 120.2511 | -121.725 | 121.3965 | 121.5363 | 121.2419 | 121.3215 | -0.59904
2016.1875 | 121.5912 | -121.1746 | 0.48065 | 1.4211e-13 | -0.026636 | 0.00092524 | 0.068195 | -0.012279 | 0.059112 | 0.0079357 | -0.0031575 | 0.0049142 | 0.018036 | 0.034713 | 0.0074415 | -120.5433 | -1.0563 | -121.0673 | 0.47334 | 0.45367 | 0.70971 | -121.313 | 0.060571 | 0.018674 | -0.001407 | 0.10282 | 0.24721 | -0.05635 | -0.2191 | -0.13836 | -0.007313 | 0.6313 | 0.10732 | 0.24568 | -0.026979 | 0.22906 | 120.9555 | -0.37783 | 121.2352 | 121.1732 | 0.21769 | -0.23344 | -0.537 | 121.648 | 121.6283 | 121.8843 | 120.1184 | -121.7936 | 121.2774 | 121.4218 | 121.1183 | 121.1933 | -0.69975
2017.9844 | 121.0281 | -119.989 | 0.83771 | 1.4211e-13 | -0.02685 | 0.00071164 | 0.067767 | -0.012279 | 0.058685 | 0.00030522 | -0.0029439 | 0.0049142 | 0.01825 | 0.034927 | 0.0074415 | -118.9729 | -1.1432 | -119.4374 | 1.27 | 1.2458 | 1.511 | -119.7104 | 0.060571 | 0.027831 | -0.005985 | 0.1074 | 0.24721 | -0.11129 | -0.22367 | 0.27866 | 0.43227 | 1.0161 | 0.55158 | 0.27292 | 0.40812 | 0.67326 | 119.7653 | -0.73031 | 120.0496 | 119.983 | 0.21769 | -0.59049 | -0.949 | 121.259 | 121.2348 | 121.5 | 118.8458 | -120.5481 | 120.0964 | 120.2362 | 119.8777 | 120.0168 | -1.0614
2019.6719 | 121.3715 | -120.7947 | 0.39825 | 1.4211e-13 | -0.026636 | 0.00071164 | 0.068195 | -0.012066 | 0.059112 | 0.015566 | -0.0029439 | 0.0051278 | 0.018036 | 0.034713 | 0.0072279 | -120.2503 | -1.1066 | -120.7789 | 0.45503 | 0.47199 | 0.68224 | -121.0337 | 0.060571 | 0.018674 | 0.003172 | 0.10282 | 0.24721 | -0.12503 | -0.22367 | -0.23899 | 0.056772 | 0.54437 | 0.015806 | 0.25479 | 0.073734 | 0.28399 | 120.571 | -0.29543 | 120.8552 | 120.7979 | 0.22685 | -0.15104 | -0.52328 | 121.2497 | 121.2667 | 121.4769 | 119.6881 | -121.4319 | 120.8975 | 121.0419 | 120.6696 | 120.8134 | -0.62193
2021.3594 | 121.3715 | -120.8267 | 0.48065 | 1.4211e-13 | -0.027064 | 7.0442e-05 | 0.067981 | -0.012279 | 0.058898 | 0.00030522 | -0.0027303 | 0.0047004 | 0.01825 | 0.034713 | 0.0074415 | -120.2686 | -1.1066 | -120.8063 | 0.46418 | 0.52694 | 0.74176 | -121.0062 | 0.055992 | 0.027831 | -0.005985 | 0.1074 | 0.24721 | -0.097557 | -0.22367 | -0.17947 | -0.016469 | 0.5581 | 0.02038 | 0.19985 | 0.046283 | 0.26111 | 120.603 | -0.37325 | 120.8827 | 120.8207 | 0.21769 | -0.23344 | -0.57821 | 121.2909 | 121.3537 | 121.5685 | 119.7201 | -121.4868 | 120.9341 | 121.0739 | 120.7292 | 120.8546 | -0.70433
2023.0312 | 121.4584 | -121.0373 | 0.27466 | 1.4211e-13 | -0.027064 | 0.00071164 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018463 | 0.034927 | 0.0076551 | -120.3327 | -1.0929 | -120.8613 | 0.45045 | 0.41246 | 0.72803 | -121.1069 | 0.060571 | 0.023253 | -0.010564 | 0.098244 | 0.25179 | -0.11587 | -0.22367 | -0.069636 | 0.17579 | 0.70457 | 0.17601 | 0.24565 | 0.1378 | 0.45337 | 120.8136 | -0.17641 | 121.0979 | 121.0267 | 0.21311 | -0.022864 | -0.39053 | 121.4877 | 121.4498 | 121.7653 | 119.9444 | -121.3816 | 121.1355 | 121.2891 | 120.9214 | 121.0605 | -0.49833
2024.7188 | 121.5088 | -121.0144 | 0.3067 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.067981 | -0.012066 | 0.058898 | 0.015566 | -0.0031575 | 0.0047004 | 0.017823 | 0.0345 | 0.0068005 | -120.3281 | -1.0563 | -120.8521 | 0.47334 | 0.44451 | 0.75092 | -121.0932 | 0.060571 | 0.018674 | -0.001407 | 0.10282 | 0.24264 | -0.083821 | -0.22367 | -0.078787 | 0.16664 | 0.68626 | 0.16228 | 0.24107 | 0.13781 | 0.44422 | 120.7907 | -0.20388 | 121.075 | 121.013 | 0.22227 | -0.064065 | -0.39052 | 121.4877 | 121.4589 | 121.7653 | 119.9582 | -121.3999 | 121.1172 | 121.257 | 120.9306 | 121.0331 | -0.53038
2026.4531 | 120.9686 | -120.7855 | 0.17853 | 1.4211e-13 | -0.027277 | 0.00028424 | 0.067767 | -0.012279 | 0.059112 | -0.0073253 | -0.0029439 | 0.0049142 | 0.01825 | 0.0345 | 0.0072279 | -120.0763 | -1.1341 | -120.6049 | 0.3131 | 0.33462 | 0.54946 | -120.8459 | 0.060571 | 0.018674 | -0.001407 | 0.10282 | 0.24264 | -0.11129 | -0.2191 | -0.060407 | 0.13457 | 0.70919 | 0.18063 | 0.24103 | 0.15609 | 0.37093 | 120.5664 | -0.075706 | 120.8461 | 120.7841 | 0.21769 | 0.064109 | -0.28982 | 121.0986 | 121.1201 | 121.335 | 119.6514 | -121.0245 | 120.8883 | 121.0282 | 120.6742 | 120.8042 | -0.39762
2028.1406 | 120.8725 | -120.7901 | 0.13733 | 1.4211e-13 | -0.027064 | 7.0442e-05 | 0.067554 | -0.012279 | 0.059112 | 0.00030522 | -0.0031575 | 0.0051278 | 0.017823 | 0.034713 | 0.0076551 | -119.5819 | -1.1616 | -120.0647 | 0.63358 | 0.61851 | 0.87912 | -120.3377 | 0.055992 | 0.018674 | 0.003172 | 0.10282 | 0.24264 | -0.12961 | -0.2191 | 0.45243 | 0.49625 | 1.2082 | 0.72544 | 0.27301 | 0.48118 | 0.74179 | 120.571 | -0.034507 | 120.8461 | 120.7933 | 0.22227 | 0.10531 | -0.26694 | 121.4237 | 121.4086 | 121.6692 | 119.6285 | -120.475 | 120.8929 | 121.0327 | 120.6605 | 120.8088 | -0.35642
2029.8125 | 120.7443 | -120.5887 | 0.11902 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.067554 | -0.012279 | 0.058898 | 0.00030522 | -0.0027303 | 0.0047004 | 0.018036 | 0.034927 | 0.0074415 | -119.4674 | -1.1661 | -119.8998 | 0.61985 | 0.59104 | 0.85623 | -120.1682 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.24721 | -0.079243 | -0.22367 | 0.42044 | 0.50083 | 1.1213 | 0.68884 | 0.26841 | 0.47202 | 0.73721 | 120.365 | -0.020775 | 120.6493 | 120.5873 | 0.22227 | 0.1282 | -0.19826 | 121.2085 | 121.1797 | 121.4449 | 119.4225 | -120.2873 | 120.6869 | 120.8359 | 120.5094 | 120.6074 | -0.34269
2031.5312 | 121.0236 | -120.9595 | 0.13275 | 1.4211e-13 | -0.02685 | 0.00071164 | 0.067767 | -0.012279 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.018036 | 0.034927 | 0.0074415 | -120.3648 | -1.1341 | -120.8475 | 0.15285 | 0.19725 | 0.41668 | -121.0978 | 0.06515 | 0.023253 | -0.005985 | 0.10282 | 0.24264 | -0.05635 | -0.2191 | -0.1383 | 0.020101 | 0.5947 | 0.11193 | 0.25022 | 0.064502 | 0.28393 | 120.7404 | -0.029929 | 121.0246 | 120.9535 | 0.21311 | 0.10989 | -0.1891 | 121.1123 | 121.1567 | 121.3762 | 119.8254 | -121.2305 | 121.0623 | 121.2021 | 120.9031 | 120.9827 | -0.35185
2033.2188 | 121.138 | -120.9869 | 0.11444 | 1.4211e-13 | -0.02685 | 0.00092524 | 0.067981 | -0.012066 | 0.059112 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018036 | 0.034713 | 0.0072279 | -120.3877 | -1.1341 | -120.8659 | 0.18032 | 0.23846 | 0.44873 | -121.0428 | 0.060571 | 0.018674 | -0.010564 | 0.10282 | 0.24721 | -0.079243 | -0.22825 | -0.055885 | 0.065882 | 0.59928 | 0.12108 | 0.17696 | 0.12402 | 0.33429 | 120.7587 | -0.011619 | 121.0475 | 120.9764 | 0.21769 | 0.13277 | -0.19368 | 121.1673 | 121.2254 | 121.4357 | 119.8529 | -121.1573 | 121.0898 | 121.2342 | 120.9077 | 121.0056 | -0.34269
2034.9219 | 121.2753 | -121.0052 | 0.11902 | 1.4211e-13 | -0.027064 | 0.00071164 | 0.067981 | -0.012493 | 0.059326 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018036 | 0.034713 | 0.0072279 | -120.4792 | -1.1387 | -120.9666 | 0.14827 | 0.10567 | 0.4121 | -121.1207 | 0.055992 | 0.027831 | -0.001407 | 0.10282 | 0.24264 | -0.097557 | -0.22367 | -0.11541 | 0.029255 | 0.52602 | 0.038668 | 0.15408 | -0.013345 | 0.29309 | 120.7816 | -0.016197 | 121.0612 | 121.0038 | 0.22227 | 0.12362 | -0.21658 | 121.1535 | 121.1109 | 121.4174 | 119.8666 | -121.2397 | 121.1081 | 121.2479 | 120.9077 | 121.0331 | -0.34269
2036.6094 | 121.2891 | -121.0464 | 0.11902 | 1.4211e-13 | -0.027064 | 0.00049784 | 0.067767 | -0.012279 | 0.059326 | 0.00030522 | -0.0029439 | 0.0047004 | 0.01825 | 0.034713 | 0.0072279 | -120.5159 | -1.1341 | -121.0032 | 0.14827 | 0.096516 | 0.4121 | -121.171 | 0.06515 | 0.023253 | -0.005985 | 0.10282 | 0.24264 | -0.083821 | -0.2191 | -0.12458 | 0.029255 | 0.53059 | 0.043241 | 0.16782 | -0.022503 | 0.29309 | 120.8274 | -0.016197 | 121.1116 | 121.0405 | 0.21311 | 0.12362 | -0.20284 | 121.1947 | 121.143 | 121.4586 | 119.9124 | -121.2901 | 121.1493 | 121.2891 | 120.9626 | 121.0697 | -0.33811
2038.2969 | 121.2021 | -121.1105 | 0.15564 | 1.4211e-13 | -0.027277 | 0.00028424 | 0.067981 | -0.012493 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.01825 | 0.034927 | 0.0072279 | -120.5342 | -1.1066 | -121.0353 | 0.15285 | 0.1011 | 0.41668 | -121.1893 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.24264 | -0.11587 | -0.22367 | -0.078813 | -0.002788 | 0.57636 | 0.07528 | 0.15409 | -0.054545 | 0.26104 | 120.8869 | -0.048239 | 121.1711 | 121.1091 | 0.22227 | 0.086997 | -0.27151 | 121.2634 | 121.2116 | 121.5272 | 120.0039 | -121.345 | 121.2179 | 121.3532 | 120.9947 | 121.1338 | -0.37931
2040 | 121.3394 | -121.0968 | 0.11902 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.067981 | -0.012707 | 0.058898 | 0.00030522 | -0.0029439 | 0.0049142 | 0.018036 | 0.034927 | 0.0074415 | -120.5616 | -1.1112 | -121.0444 | 0.14369 | 0.1011 | 0.41668 | -121.2168 | 0.06515 | 0.018674 | -0.001407 | 0.10282 | 0.23806 | -0.042614 | -0.2191 | -0.12002 | 0.024676 | 0.53516 | 0.05239 | 0.17241 | -0.017924 | 0.29766 | 120.8777 | -0.016197 | 121.162 | 121.0954 | 0.21769 | 0.11904 | -0.16163 | 121.2405 | 121.1979 | 121.5135 | 119.9856 | -121.3358 | 121.1996 | 121.3349 | 121.0542 | 121.1155 | -0.33811
2041.6875 | 121.2479 | -121.17 | 0.14191 | 1.4211e-13 | -0.027064 | 0.00071164 | 0.067981 | -0.012066 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.01825 | 0.0345 | 0.0076551 | -120.5845 | -1.1112 | -121.0673 | 0.15285 | 0.096516 | 0.37548 | -121.2397 | 0.06515 | 0.027831 | -0.001407 | 0.10282 | 0.25179 | -0.047193 | -0.2191 | -0.069672 | 0.010945 | 0.58551 | 0.10274 | 0.17241 | -0.045391 | 0.23357 | 120.9509 | -0.039085 | 121.2352 | 121.1686 | 0.21769 | 0.10989 | -0.1891 | 121.3229 | 121.2666 | 121.5455 | 120.0589 | -121.3816 | 121.2729 | 121.4218 | 121.1229 | 121.1979 | -0.361
2043.3594 | 121.3577 | -121.1105 | 0.10986 | 1.4211e-13 | -0.027064 | 0.00028424 | 0.068195 | -0.012066 | 0.059326 | 0.00030522 | -0.0033713 | 0.0049142 | 0.017823 | 0.034713 | 0.0074415 | -120.5983 | -1.1204 | -121.0856 | 0.14827 | 0.1011 | 0.35716 | -121.2397 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.24264 | -0.010564 | -0.22367 | -0.12918 | 0.038411 | 0.51227 | 0.024918 | 0.1541 | -0.008768 | 0.2473 | 120.8869 | -0.007041 | 121.1711 | 121.1091 | 0.22227 | 0.13277 | -0.12043 | 121.2588 | 121.2116 | 121.4677 | 119.9902 | -121.3496 | 121.2134 | 121.3532 | 121.1 | 121.1338 | -0.33354
2045.0469 | 121.3211 | -121.1746 | 0.13733 | 1.4211e-13 | -0.027277 | 0.00049784 | 0.067981 | -0.012279 | 0.059112 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017823 | 0.034713 | 0.0070143 | -120.6074 | -1.1249 | -121.1039 | 0.13912 | 0.10567 | 0.35716 | -121.2718 | 0.060571 | 0.023253 | -0.005985 | 0.098244 | 0.23806 | -0.038035 | -0.22367 | -0.097147 | 0.001788 | 0.5672 | 0.070692 | 0.16784 | -0.031655 | 0.21983 | 120.9509 | -0.039085 | 121.2352 | 121.1686 | 0.21769 | 0.10073 | -0.17536 | 121.3137 | 121.2803 | 121.5318 | 120.0497 | -121.4091 | 121.2729 | 121.4127 | 121.1366 | 121.1979 | -0.361
2046.75 | 121.3486 | -121.17 | 0.13275 | 1.4211e-13 | -0.027277 | 0.00049784 | 0.068195 | -0.012707 | 0.058898 | 0.0079357 | -0.0029439 | 0.0047004 | 0.01825 | 0.034713 | 0.0074415 | -120.6257 | -1.1295 | -121.1085 | 0.14827 | 0.096516 | 0.3709 | -121.2763 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.23806 | -0.11129 | -0.22367 | -0.1063 | 0.015523 | 0.54431 | 0.061536 | 0.16784 | -0.036235 | 0.23814 | 120.9464 | -0.029929 | 121.2306 | 121.1686 | 0.22227 | 0.10531 | -0.24404 | 121.3183 | 121.2666 | 121.5409 | 120.0405 | -121.4091 | 121.2729 | 121.4081 | 121.0588 | 121.1933 | -0.35642
2048.5 | 121.3074 | -121.1975 | 0.14191 | 1.4211e-13 | -0.027277 | 0.00028424 | 0.067981 | -0.012279 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017823 | 0.034713 | 0.0074415 | -120.6349 | -1.1295 | -121.1268 | 0.14827 | 0.1011 | 0.36174 | -121.2901 | 0.055992 | 0.023253 | -0.001407 | 0.1074 | 0.24264 | -0.12503 | -0.2191 | -0.092575 | 0.006367 | 0.56262 | 0.070689 | 0.16326 | -0.040812 | 0.21983 | 120.9784 | -0.034506 | 121.2535 | 121.1961 | 0.21769 | 0.10073 | -0.26694 | 121.3458 | 121.2986 | 121.5592 | 120.068 | -121.432 | 121.3049 | 121.4401 | 121.0725 | 121.2208 | -0.361
2050.1875 | 121.4355 | -121.1975 | 0.10071 | 1.4211e-13 | -0.027277 | 0.00071164 | 0.067981 | -0.012707 | 0.059326 | 0.00030522 | -0.0031575 | 0.0047004 | 0.01825 | 0.035354 | 0.0074415 | -120.6486 | -1.1387 | -121.136 | 0.13912 | 0.1011 | 0.36632 | -121.2947 | 0.06515 | 0.014095 | -0.005985 | 0.093665 | 0.23806 | -0.0243 | -0.2191 | -0.097153 | 0.038409 | 0.54888 | 0.061532 | 0.15869 | 0.000387 | 0.26561 | 120.9784 | -0.007043 | 121.2627 | 121.1915 | 0.21311 | 0.13735 | -0.12501 | 121.3366 | 121.2986 | 121.5638 | 120.0588 | -121.3954 | 121.2912 | 121.4356 | 121.1732 | 121.2116 | -0.3198
2051.9062 | 121.4127 | -121.1792 | 0.10986 | 1.4211e-13 | -0.027064 | 0.00049784 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0027303 | 0.0047004 | 0.017823 | 0.034927 | 0.0076551 | -120.6624 | -1.1387 | -121.1451 | 0.14827 | 0.10567 | 0.3709 | -121.313 | 0.060571 | 0.023253 | -0.005985 | 0.093665 | 0.24264 | -0.11587 | -0.22367 | -0.13378 | 0.038411 | 0.51683 | 0.034065 | 0.16784 | -0.004189 | 0.26103 | 120.9555 | -0.016198 | 121.2398 | 121.1732 | 0.21769 | 0.13277 | -0.22574 | 121.3275 | 121.2849 | 121.5501 | 120.0405 | -121.4228 | 121.2729 | 121.4218 | 121.0633 | 121.2025 | -0.33354
2053.5938 | 121.431 | -121.2067 | 0.14191 | 1.4211e-13 | -0.027064 | 0.00071164 | 0.067981 | -0.012279 | 0.059112 | 0.00030522 | -0.0025167 | 0.0051278 | 0.01825 | 0.034927 | 0.0070143 | -120.6761 | -1.1387 | -121.1543 | 0.14827 | 0.1011 | 0.36632 | -121.313 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.23806 | -0.10671 | -0.2191 | -0.10631 | 0.006367 | 0.53056 | 0.052374 | 0.15869 | -0.040812 | 0.22441 | 120.9876 | -0.034506 | 121.2672 | 121.2053 | 0.21769 | 0.096151 | -0.24862 | 121.3549 | 121.3078 | 121.573 | 120.068 | -121.4549 | 121.3141 | 121.4447 | 121.1 | 121.2299 | -0.361
2055.2812 | 121.3348 | -121.2479 | 0.15106 | 1.4211e-13 | -0.027064 | 0.00028424 | 0.067981 | -0.012279 | 0.059539 | 0.00030522 | -0.0031575 | 0.0049142 | 0.01825 | 0.034927 | 0.0070143 | -120.6898 | -1.1478 | -121.1726 | 0.14827 | 0.091937 | 0.36174 | -121.3359 | 0.060571 | 0.014095 | -0.001407 | 0.10282 | 0.24721 | -0.05635 | -0.22367 | -0.08801 | -0.002788 | 0.55803 | 0.07526 | 0.16327 | -0.059125 | 0.21068 | 121.0242 | -0.04824 | 121.3084 | 121.2465 | 0.22227 | 0.096153 | -0.20741 | 121.3961 | 121.3398 | 121.6096 | 120.1 | -121.4869 | 121.3507 | 121.4951 | 121.1915 | 121.262 | -0.37474
2056.9844 | 121.4722 | -121.1929 | 0.10529 | 1.4211e-13 | -0.027064 | 0.00049784 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0031575 | 0.0047004 | 0.018036 | 0.034713 | 0.0074415 | -120.6853 | -1.1478 | -121.1772 | 0.14369 | 0.096516 | 0.36632 | -121.3405 | 0.06515 | 0.018674 | -0.001407 | 0.1074 | 0.24264 | -0.074664 | -0.22825 | -0.14752 | 0.038409 | 0.50768 | 0.01575 | 0.16327 | -0.00877 | 0.26103 | 120.9647 | 0.002115 | 121.2581 | 121.1915 | 0.22685 | 0.13735 | -0.17995 | 121.3366 | 121.2894 | 121.5593 | 120.0451 | -121.4457 | 121.3003 | 121.4356 | 121.1183 | 121.2116 | -0.33354
2058.6719 | 121.3577 | -121.2845 | 0.15564 | 1.4211e-13 | -0.027064 | 0.00028424 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0031575 | 0.0047004 | 0.01825 | 0.034927 | 0.0072279 | -120.699 | -1.157 | -121.1863 | 0.14827 | 0.1011 | 0.35716 | -121.3588 | 0.051413 | 0.023253 | -0.005985 | 0.10282 | 0.24264 | -0.12503 | -0.2191 | -0.074283 | -0.007366 | 0.58549 | 0.098146 | 0.17243 | -0.054545 | 0.20152 | 121.0654 | -0.052818 | 121.3359 | 121.2785 | 0.21311 | 0.086997 | -0.28067 | 121.4328 | 121.3856 | 121.6416 | 120.1275 | -121.5144 | 121.3873 | 121.5271 | 121.1595 | 121.3077 | -0.37474
2060.375 | 121.5042 | -121.2341 | 0.10986 | 1.4211e-13 | -0.027277 | 0.00071164 | 0.068195 | -0.012279 | 0.058898 | -0.0073253 | -0.0029439 | 0.0049142 | 0.017609 | 0.035141 | 0.0070143 | -120.7127 | -1.1616 | -121.2001 | 0.14827 | 0.1011 | 0.36632 | -121.3588 | 0.060571 | 0.023253 | -0.005985 | 0.10282 | 0.24264 | -0.065507 | -0.22367 | -0.12464 | 0.038411 | 0.5214 | 0.034057 | 0.15869 | -0.008768 | 0.25645 | 121.0105 | -0.007041 | 121.2947 | 121.2281 | 0.21769 | 0.13277 | -0.17537 | 121.3824 | 121.3352 | 121.6004 | 120.0726 | -121.4686 | 121.337 | 121.4768 | 121.1686 | 121.2574 | -0.33354
2062.0781 | 121.5134 | -121.2753 | 0.10986 | 1.4211e-13 | -0.027277 | 0.00028424 | 0.067981 | -0.012279 | 0.058685 | 0.00030522 | -0.0029439 | 0.0047004 | 0.01825 | 0.034927 | 0.0070143 | -120.7081 | -1.1616 | -121.1909 | 0.15285 | 0.11025 | 0.36632 | -121.4137 | 0.060571 | 0.023253 | -0.001407 | 0.098244 | 0.24264 | -0.12503 | -0.22367 | -0.13838 | 0.042989 | 0.56718 | 0.084413 | 0.2228 | 0.00039 | 0.25645 | 121.0517 | -0.011619 | 121.3359 | 121.2739 | 0.22227 | 0.13277 | -0.23489 | 121.4282 | 121.3856 | 121.6416 | 120.1138 | -121.5236 | 121.3736 | 121.518 | 121.1503 | 121.2986 | -0.33354
2063.7812 | 121.5088 | -121.2799 | 0.10529 | 1.4211e-13 | -0.027491 | 0.00071164 | 0.068195 | -0.012493 | 0.059326 | -0.0073253 | -0.0027303 | 0.0049142 | 0.017823 | 0.034927 | 0.0072279 | -120.7173 | -1.157 | -121.223 | 0.14827 | 0.096516 | 0.36174 | -121.3771 | 0.060571 | 0.018674 | -0.001407 | 0.1074 | 0.24721 | -0.097557 | -0.22367 | -0.097177 | 0.042988 | 0.5626 | 0.056942 | 0.15412 | -0.00877 | 0.25645 | 121.0562 | 0.002115 | 121.3405 | 121.2785 | 0.22227 | 0.14193 | -0.20284 | 121.4282 | 121.3764 | 121.6416 | 120.1229 | -121.4824 | 121.3873 | 121.5271 | 121.1823 | 121.2986 | -0.32896
2065.5156 | 121.4813 | -121.2891 | 0.12817 | 1.4211e-13 | -0.027064 | 0.00071164 | 0.067981 | -0.012279 | 0.059112 | 0.015566 | -0.0029439 | 0.0049142 | 0.018036 | 0.035141 | 0.0076551 | -120.7265 | -1.1753 | -121.223 | 0.14369 | 0.1011 | 0.36632 | -121.3908 | 0.06515 | 0.018674 | -0.001407 | 0.098244 | 0.25179 | -0.0884 | -0.2191 | -0.10176 | 0.015521 | 0.5626 | 0.066097 | 0.16786 | -0.027079 | 0.23814 | 121.07 | -0.02993 | 121.3542 | 121.2877 | 0.21769 | 0.12362 | -0.21657 | 121.4328 | 121.3902 | 121.6554 | 120.1138 | -121.519 | 121.3873 | 121.5409 | 121.2007 | 121.3077 | -0.34727
2067.2031 | 121.3943 | -121.2891 | 0.13733 | 1.4211e-13 | -0.027064 | 0.00028424 | 0.067767 | -0.012493 | 0.058898 | 0.00030522 | -0.0027303 | 0.0049142 | 0.018036 | 0.035141 | 0.0074415 | -120.7402 | -1.1753 | -121.2321 | 0.13912 | 0.1011 | 0.36174 | -121.3862 | 0.060571 | 0.018674 | -0.001407 | 0.1074 | 0.24264 | -0.079243 | -0.22825 | -0.09718 | 0.001788 | 0.54887 | 0.05694 | 0.15412 | -0.036234 | 0.22441 | 121.0608 | -0.029928 | 121.3496 | 121.2877 | 0.22685 | 0.10531 | -0.21657 | 121.4282 | 121.3902 | 121.6508 | 120.1138 | -121.5236 | 121.3965 | 121.5317 | 121.2098 | 121.3077 | -0.36558
2068.9062 | 121.4493 | -121.3028 | 0.14191 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.067981 | -0.012279 | 0.059112 | 0.00030522 | -0.0027303 | 0.0044868 | 0.017823 | 0.035141 | 0.0074415 | -120.7448 | -1.1799 | -121.2321 | 0.14369 | 0.10567 | 0.36632 | -121.3954 | 0.060571 | 0.023253 | -0.010564 | 0.098244 | 0.24264 | -0.033457 | -0.22367 | -0.092605 | 0.001788 | 0.55802 | 0.070673 | 0.16328 | -0.036233 | 0.22441 | 121.0791 | -0.043663 | 121.3634 | 121.2922 | 0.21311 | 0.10073 | -0.17536 | 121.4465 | 121.4085 | 121.6691 | 120.1229 | -121.5373 | 121.401 | 121.5454 | 121.2693 | 121.326 | -0.36558
2070.6094 | 121.4172 | -121.3165 | 0.16022 | 1.4211e-13 | -0.027491 | 0.00028424 | 0.068409 | -0.012707 | 0.059539 | 0.0079357 | -0.0027303 | 0.0044868 | 0.018036 | 0.034927 | 0.0072279 | -120.7448 | -1.1799 | -121.2459 | 0.14369 | 0.10567 | 0.36174 | -121.4046 | 0.060571 | 0.018674 | -0.010564 | 0.10282 | 0.24721 | -0.065507 | -0.2191 | -0.08803 | -0.016522 | 0.57175 | 0.070672 | 0.1587 | -0.054543 | 0.20152 | 121.0974 | -0.057395 | 121.3771 | 121.306 | 0.20853 | 0.086998 | -0.22572 | 121.4602 | 121.4222 | 121.6783 | 120.1367 | -121.5648 | 121.4194 | 121.5637 | 121.251 | 121.3352 | -0.37931
2072.2969 | 121.463 | -121.3074 | 0.12817 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0027303 | 0.0047004 | 0.018036 | 0.034927 | 0.0072279 | -120.7631 | -1.1707 | -121.2459 | 0.14369 | 0.11025 | 0.36632 | -121.3954 | 0.060571 | 0.023253 | 0.003172 | 0.10282 | 0.24264 | -0.092979 | -0.22367 | -0.088027 | 0.015521 | 0.54428 | 0.061517 | 0.14954 | -0.017921 | 0.23814 | 121.0837 | -0.025352 | 121.3679 | 121.3105 | 0.22685 | 0.11446 | -0.22115 | 121.4511 | 121.4176 | 121.6737 | 120.1367 | -121.5236 | 121.4102 | 121.55 | 121.2144 | 121.3306 | -0.35185
2074 | 121.4813 | -121.3303 | 0.14191 | 1.4211e-13 | -0.027064 | 0.00049784 | 0.068195 | -0.012707 | 0.059753 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017395 | 0.034927 | 0.0074415 | -120.7677 | -1.1936 | -121.255 | 0.14827 | 0.10567 | 0.3709 | -121.4091 | 0.06515 | 0.027831 | -0.001407 | 0.1074 | 0.24264 | -0.12503 | -0.2191 | -0.078876 | 0.006367 | 0.56259 | 0.075248 | 0.15412 | -0.036233 | 0.22899 | 121.1112 | -0.034506 | 121.3954 | 121.3289 | 0.21769 | 0.10073 | -0.26694 | 121.4785 | 121.4359 | 121.7012 | 120.1367 | -121.551 | 121.4377 | 121.5729 | 121.2052 | 121.3581 | -0.361
2075.6875 | 121.5271 | -121.3028 | 0.10986 | 1.4211e-13 | -0.027491 | 0.00028424 | 0.067981 | -0.012707 | 0.059539 | 0.0079357 | -0.0027303 | 0.0047004 | 0.018036 | 0.035141 | 0.0074415 | -120.7814 | -1.2028 | -121.2642 | 0.14827 | 0.11025 | 0.3709 | -121.4091 | 0.060571 | 0.027831 | -0.015143 | 0.10282 | 0.24721 | -0.033457 | -0.22367 | -0.10634 | 0.038411 | 0.52139 | 0.038626 | 0.14497 | 0.00039 | 0.26103 | 121.0791 | -0.007041 | 121.3634 | 121.2877 | 0.20853 | 0.13735 | -0.14332 | 121.4511 | 121.413 | 121.6737 | 120.1 | -121.519 | 121.4056 | 121.55 | 121.2693 | 121.3306 | -0.33354
2077.375 | 121.4401 | -121.3577 | 0.13733 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.068195 | -0.012493 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.018036 | 0.034927 | 0.0076551 | -120.731 | -1.1982 | -121.2687 | 0.14827 | 0.10567 | 0.36632 | -121.4137 | 0.06515 | 0.018674 | -0.001407 | 0.10282 | 0.24264 | -0.12503 | -0.22825 | -0.055988 | 0.010945 | 0.62669 | 0.088979 | 0.14497 | -0.031655 | 0.22899 | 121.1295 | -0.034507 | 121.4229 | 121.3563 | 0.22685 | 0.10531 | -0.26236 | 121.506 | 121.4634 | 121.724 | 120.1595 | -121.551 | 121.4605 | 121.6004 | 121.2327 | 121.3764 | -0.36558
2079.0625 | 121.5408 | -121.3348 | 0.10986 | 1.4211e-13 | -0.027277 | 0.00049784 | 0.067981 | -0.012066 | 0.059326 | 0.00030522 | -0.0031575 | 0.0047004 | 0.018036 | 0.035354 | 0.0072279 | -120.7402 | -1.2028 | -121.2779 | 0.14827 | 0.1011 | 0.3709 | -121.4366 | 0.06515 | 0.018674 | -0.005985 | 0.098244 | 0.24721 | -0.092979 | -0.22367 | -0.10177 | 0.038411 | 0.59464 | 0.056935 | 0.15871 | -0.008768 | 0.26103 | 121.1112 | -0.011619 | 121.4 | 121.3289 | 0.21769 | 0.13735 | -0.20284 | 121.4831 | 121.4359 | 121.7057 | 120.1321 | -121.5465 | 121.4331 | 121.5821 | 121.2419 | 121.3535 | -0.33354
2080.7656 | 121.4539 | -121.3531 | 0.15106 | 1.4211e-13 | -0.027705 | 0.00071164 | 0.067981 | -0.012279 | 0.059539 | 0.015566 | -0.0027303 | 0.0049142 | 0.01825 | 0.034927 | 0.0076551 | -120.7402 | -1.2211 | -121.2825 | 0.15285 | 0.091937 | 0.36174 | -121.4229 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.23806 | -0.092979 | -0.22825 | -0.069724 | 0.00179 | 0.61295 | 0.070666 | 0.14039 | -0.059125 | 0.21068 | 121.1249 | -0.052818 | 121.4137 | 121.3517 | 0.22685 | 0.086996 | -0.24404 | 121.506 | 121.4451 | 121.7149 | 120.1321 | -121.5739 | 121.4514 | 121.5912 | 121.2602 | 121.3718 | -0.37931
2082.5156 | 121.4493 | -121.3852 | 0.14648 | 1.4211e-13 | -0.027277 | 0.00049784 | 0.068195 | -0.012707 | 0.059539 | 0.0079357 | -0.0027303 | 0.0044868 | 0.01825 | 0.034927 | 0.0072279 | -120.7448 | -1.2257 | -121.2779 | 0.14369 | 0.096516 | 0.36632 | -121.4549 | 0.055992 | 0.018674 | -0.001407 | 0.098244 | 0.24264 | -0.092979 | -0.2191 | -0.069733 | -0.002789 | 0.64042 | 0.10729 | 0.17702 | -0.049968 | 0.21983 | 121.1661 | -0.04824 | 121.4412 | 121.3838 | 0.21769 | 0.096153 | -0.23946 | 121.5289 | 121.4817 | 121.7515 | 120.1595 | -121.6014 | 121.4834 | 121.6278 | 121.2922 | 121.4039 | -0.36558
2084.2031 | 121.6232 | -121.3348 | 0.11444 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.067767 | -0.012707 | 0.059326 | -0.0073253 | -0.0029439 | 0.0047004 | 0.017823 | 0.035354 | 0.0072279 | -120.7539 | -1.2211 | -121.3008 | 0.14827 | 0.10567 | 0.36174 | -121.4595 | 0.06515 | 0.027831 | 0.003172 | 0.1074 | 0.24264 | -0.0884 | -0.22367 | -0.12467 | 0.033833 | 0.58091 | 0.034043 | 0.15871 | -0.008767 | 0.2473 | 121.1112 | -0.00704 | 121.4 | 121.338 | 0.22685 | 0.1282 | -0.20284 | 121.4831 | 121.4405 | 121.6966 | 120.1138 | -121.5739 | 121.4422 | 121.5775 | 121.2464 | 121.3627 | -0.33811
2085.9062 | 121.6049 | -121.3348 | 0.1236 | 1.4211e-13 | -0.027277 | 0.00071164 | 0.068195 | -0.012279 | 0.059326 | 0.0079357 | -0.0027303 | 0.0047004 | 0.017823 | 0.035141 | 0.0074415 | -120.7585 | -1.2302 | -121.3008 | 0.14369 | 0.1011 | 0.36632 | -121.4595 | 0.06515 | 0.009516 | -0.001407 | 0.1074 | 0.25179 | -0.12503 | -0.2191 | -0.12467 | 0.020099 | 0.57633 | 0.034043 | 0.15871 | -0.022501 | 0.24272 | 121.1157 | -0.016195 | 121.4 | 121.3334 | 0.21769 | 0.1282 | -0.24862 | 121.4785 | 121.4359 | 121.7012 | 120.1046 | -121.5831 | 121.4422 | 121.5866 | 121.2098 | 121.3444 | -0.34269
2087.5938 | 121.5454 | -121.3715 | 0.12817 | 1.4211e-13 | -0.027705 | 0.00028424 | 0.068195 | -0.01292 | 0.059112 | 0.00030522 | -0.0029439 | 0.0051278 | 0.017823 | 0.035141 | 0.0070143 | -120.7722 | -1.2394 | -121.3008 | 0.14369 | 0.11025 | 0.36632 | -121.4595 | 0.06515 | 0.014095 | -0.005985 | 0.1074 | 0.24264 | -0.13419 | -0.2191 | -0.088045 | 0.015521 | 0.59921 | 0.070664 | 0.15871 | -0.017921 | 0.23814 | 121.1524 | -0.020773 | 121.4366 | 121.3655 | 0.21311 | 0.11446 | -0.26236 | 121.5152 | 121.4817 | 121.7378 | 120.1321 | -121.5877 | 121.4789 | 121.6141 | 121.2373 | 121.3856 | -0.34727
2089.2812 | 121.4859 | -121.3806 | 0.15564 | 1.4211e-13 | -0.027491 | 0.00071164 | 0.068409 | -0.012279 | 0.059112 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018036 | 0.035141 | 0.0072279 | -120.7677 | -1.2348 | -121.31 | 0.14369 | 0.10567 | 0.36174 | -121.4458 | 0.060571 | 0.018674 | -0.005985 | 0.1074 | 0.24721 | -0.083821 | -0.22367 | -0.065153 | -0.011945 | 0.61295 | 0.070663 | 0.13582 | -0.049966 | 0.2061 | 121.1569 | -0.048239 | 121.4412 | 121.3746 | 0.21769 | 0.091575 | -0.23946 | 121.5243 | 121.4863 | 121.7424 | 120.1458 | -121.6014 | 121.488 | 121.6278 | 121.2968 | 121.3993 | -0.37931
2090.9688 | 121.4813 | -121.4035 | 0.15564 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.068409 | -0.012066 | 0.059539 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017823 | 0.035354 | 0.0072279 | -120.7722 | -1.2486 | -121.3145 | 0.13912 | 0.1011 | 0.36632 | -121.4641 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.24264 | -0.079243 | -0.22367 | -0.060581 | -0.016523 | 0.63126 | 0.088972 | 0.14955 | -0.054545 | 0.21068 | 121.1798 | -0.057396 | 121.4641 | 121.4021 | 0.22227 | 0.086997 | -0.23488 | 121.5426 | 121.5046 | 121.7698 | 120.155 | -121.6197 | 121.5017 | 121.6461 | 121.3243 | 121.4222 | -0.37931
2092.6562 | 121.6278 | -121.3577 | 0.10071 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0027303 | 0.0047004 | 0.01825 | 0.035141 | 0.0072279 | -120.7768 | -1.244 | -121.3191 | 0.14369 | 0.10567 | 0.36174 | -121.4732 | 0.069728 | 0.018674 | -0.001407 | 0.098244 | 0.24721 | -0.0884 | -0.22367 | -0.11551 | 0.042987 | 0.5809 | 0.038618 | 0.15413 | 0.004966 | 0.26103 | 121.1341 | -0.002464 | 121.4275 | 121.3563 | 0.22227 | 0.14651 | -0.18911 | 121.5014 | 121.4634 | 121.7195 | 120.1138 | -121.5739 | 121.456 | 121.6049 | 121.2693 | 121.3764 | -0.32438
2094.3438 | 121.5088 | -121.4081 | 0.12817 | 1.4211e-13 | -0.027277 | 0.00028424 | 0.068195 | -0.012279 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.018036 | 0.035141 | 0.0074415 | -120.7814 | -1.2531 | -121.3237 | 0.14827 | 0.1011 | 0.3709 | -121.4641 | 0.060571 | 0.014095 | -0.010564 | 0.1074 | 0.24264 | -0.12961 | -0.22367 | -0.056003 | 0.0201 | 0.62668 | 0.084394 | 0.1404 | -0.027079 | 0.24272 | 121.1844 | -0.020773 | 121.4687 | 121.3975 | 0.21311 | 0.11446 | -0.25778 | 121.5564 | 121.5092 | 121.779 | 120.1549 | -121.5923 | 121.5155 | 121.6507 | 121.2785 | 121.4222 | -0.35185
2096.0312 | 121.5088 | -121.4264 | 0.14191 | 1.4211e-13 | -0.027705 | 0.00049784 | 0.068195 | -0.012493 | 0.059539 | -0.0073253 | -0.0027303 | 0.0049142 | 0.017609 | 0.035141 | 0.0070143 | -120.7997 | -1.2623 | -121.3283 | 0.14827 | 0.1011 | 0.3709 | -121.487 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.23806 | -0.11587 | -0.22367 | -0.060586 | 0.006367 | 0.62668 | 0.098127 | 0.15871 | -0.040812 | 0.22899 | 121.2027 | -0.043663 | 121.487 | 121.425 | 0.22227 | 0.096151 | -0.25778 | 121.5747 | 121.5275 | 121.7973 | 120.1641 | -121.6289 | 121.5246 | 121.6645 | 121.3105 | 121.4451 | -0.36558
2097.7188 | 121.6324 | -121.3989 | 0.11444 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.067981 | -0.012279 | 0.059539 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018036 | 0.035141 | 0.0074415 | -120.7951 | -1.2623 | -121.3328 | 0.14369 | 0.1011 | 0.36632 | -121.4641 | 0.055992 | 0.009516 | -0.005985 | 0.10282 | 0.23806 | -0.12045 | -0.22825 | -0.065158 | 0.029254 | 0.60379 | 0.066082 | 0.13124 | -0.013346 | 0.25188 | 121.1707 | -0.011619 | 121.4549 | 121.3929 | 0.22227 | 0.12362 | -0.23489 | 121.5426 | 121.5 | 121.7652 | 120.1366 | -121.5785 | 121.5017 | 121.637 | 121.2785 | 121.4084 | -0.34269
2099.4531 | 121.5637 | -121.4035 | 0.12817 | 1.4211e-13 | -0.027491 | 0.00028424 | 0.067981 | -0.012279 | 0.058898 | -0.0073253 | -0.0029439 | 0.0044868 | 0.017823 | 0.035141 | 0.0074415 | -120.7951 | -1.2577 | -121.3283 | 0.14827 | 0.1011 | 0.36632 | -121.4778 | 0.055992 | 0.014095 | -0.005985 | 0.098244 | 0.24721 | -0.12045 | -0.23283 | -0.074317 | 0.0201 | 0.60837 | 0.075238 | 0.14955 | -0.027079 | 0.23814 | 121.1707 | -0.02993 | 121.4595 | 121.3975 | 0.22685 | 0.11904 | -0.24862 | 121.5518 | 121.5046 | 121.7698 | 120.1458 | -121.606 | 121.5017 | 121.6507 | 121.2831 | 121.4176 | -0.36101
2101.1406 | 121.6553 | -121.3989 | 0.11902 | 1.4211e-13 | -0.027491 | 7.0442e-05 | 0.068622 | -0.012493 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017609 | 0.035141 | 0.0072279 | -120.8043 | -1.2714 | -121.3466 | 0.14369 | 0.1011 | 0.36174 | -121.4961 | 0.069728 | 0.014095 | 0.003172 | 0.10282 | 0.24264 | -0.12045 | -0.22825 | -0.09721 | 0.024676 | 0.59463 | 0.052347 | 0.14956 | -0.017924 | 0.24272 | 121.1707 | -0.016197 | 121.4687 | 121.4021 | 0.23142 | 0.12362 | -0.23947 | 121.5426 | 121.5 | 121.7607 | 120.1275 | -121.6152 | 121.5017 | 121.6416 | 121.2785 | 121.413 | -0.34727
2102.8281 | 121.6461 | -121.3806 | 0.11902 | 1.4211e-13 | -0.027491 | 0.00028424 | 0.067981 | -0.012493 | 0.059326 | -0.0073253 | -0.0027303 | 0.0047004 | 0.01825 | 0.035141 | 0.0076551 | -120.8089 | -1.2669 | -121.3466 | 0.14369 | 0.1011 | 0.36174 | -121.5099 | 0.060571 | 0.018674 | 0.003172 | 0.1074 | 0.24264 | -0.12503 | -0.22367 | -0.12926 | 0.024676 | 0.57174 | 0.034036 | 0.16329 | -0.017924 | 0.24272 | 121.1569 | -0.011618 | 121.4412 | 121.3838 | 0.22685 | 0.12362 | -0.24405 | 121.5243 | 121.4817 | 121.7424 | 120.1137 | -121.6289 | 121.488 | 121.6233 | 121.2556 | 121.3993 | -0.34269
2104.5469 | 121.5591 | -121.4264 | 0.14648 | 1.4211e-13 | -0.027918 | 0.00092524 | 0.068195 | -0.012707 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017823 | 0.035354 | 0.0068005 | -120.8135 | -1.2714 | -121.3466 | 0.14827 | 0.096516 | 0.36174 | -121.519 | 0.060571 | 0.014095 | -0.001407 | 0.098244 | 0.23806 | -0.11129 | -0.21452 | -0.092639 | 0.00179 | 0.61294 | 0.079813 | 0.17245 | -0.049968 | 0.21525 | 121.2119 | -0.04824 | 121.487 | 121.425 | 0.21311 | 0.091574 | -0.25778 | 121.5747 | 121.5229 | 121.7881 | 120.1549 | -121.6655 | 121.5246 | 121.6645 | 121.3151 | 121.4405 | -0.361
2106.2344 | 121.6644 | -121.376 | 0.11444 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.068195 | -0.012707 | 0.059112 | 0.0079357 | -0.0029439 | 0.0047004 | 0.01825 | 0.035141 | 0.0072279 | -120.818 | -1.276 | -121.3557 | 0.14827 | 0.10567 | 0.35716 | -121.519 | 0.055992 | 0.014095 | -0.005985 | 0.10282 | 0.24264 | -0.079243 | -0.21452 | -0.14299 | 0.033833 | 0.55801 | 0.020303 | 0.1633 | -0.008767 | 0.24272 | 121.1615 | -0.011619 | 121.432 | 121.3701 | 0.20853 | 0.1282 | -0.19368 | 121.5243 | 121.4817 | 121.7332 | 120.1 | -121.6335 | 121.4789 | 121.6187 | 121.2968 | 121.3901 | -0.32896
2107.9375 | 121.6141 | -121.4081 | 0.11444 | 1.4211e-13 | -0.027491 | 0.00071164 | 0.067981 | -0.012707 | 0.059112 | 0.00030522 | -0.0027303 | 0.0049142 | 0.01825 | 0.035141 | 0.0072279 | -120.818 | -1.2898 | -121.3649 | 0.14827 | 0.10567 | 0.35716 | -121.5236 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.24264 | -0.051771 | -0.21452 | -0.11553 | 0.033833 | 0.59005 | 0.043189 | 0.15872 | -0.008767 | 0.24272 | 121.1936 | -0.011619 | 121.4687 | 121.4067 | 0.21311 | 0.1282 | -0.16621 | 121.5564 | 121.5138 | 121.7652 | 120.1183 | -121.6381 | 121.5109 | 121.6507 | 121.3563 | 121.4313 | -0.32896
2109.6562 | 121.5454 | -121.4539 | 0.12817 | 1.4211e-13 | -0.027491 | 0.00028424 | 0.068195 | -0.012279 | 0.059539 | 0.0079357 | -0.0029439 | 0.0047004 | 0.018036 | 0.035354 | 0.0074415 | -120.818 | -1.2852 | -121.3649 | 0.15285 | 0.1011 | 0.36174 | -121.5236 | 0.069728 | 0.018674 | -0.001407 | 0.098244 | 0.24721 | -0.079243 | -0.22367 | -0.069753 | 0.024678 | 0.63583 | 0.088965 | 0.15872 | -0.027079 | 0.23356 | 121.2302 | -0.02993 | 121.5236 | 121.4524 | 0.22227 | 0.11904 | -0.20742 | 121.6067 | 121.555 | 121.8156 | 120.1687 | -121.6518 | 121.5521 | 121.7011 | 121.3746 | 121.4725 | -0.35185
2111.375 | 121.5958 | -121.4401 | 0.16479 | 1.4211e-13 | -0.027705 | 0.00071164 | 0.068195 | -0.012493 | 0.059326 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017609 | 0.035354 | 0.0072279 | -120.8318 | -1.2806 | -121.374 | 0.13912 | 0.1011 | 0.36632 | -121.5373 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.23806 | -0.12045 | -0.23283 | -0.097221 | -0.025678 | 0.60836 | 0.066077 | 0.1633 | -0.0637 | 0.20152 | 121.2073 | -0.061973 | 121.5007 | 121.4387 | 0.23142 | 0.073263 | -0.28524 | 121.5792 | 121.5412 | 121.8064 | 120.1595 | -121.7021 | 121.5429 | 121.6782 | 121.3197 | 121.4634 | -0.39763
2113.0938 | 121.5958 | -121.4539 | 0.14191 | 1.4211e-13 | -0.027491 | 0.00028424 | 0.067981 | -0.012493 | 0.059539 | 0.0079357 | -0.0033713 | 0.0044868 | 0.01825 | 0.035568 | 0.0070143 | -120.8318 | -1.2898 | -121.3695 | 0.14827 | 0.096516 | 0.36632 | -121.5419 | 0.06515 | 0.018674 | 0.003172 | 0.1074 | 0.23806 | -0.11129 | -0.22367 | -0.088068 | 0.006367 | 0.62209 | 0.084387 | 0.17245 | -0.045391 | 0.22441 | 121.2302 | -0.034506 | 121.519 | 121.457 | 0.22685 | 0.096151 | -0.2532 | 121.6021 | 121.5504 | 121.8202 | 120.1641 | -121.6838 | 121.5613 | 121.6919 | 121.3426 | 121.4725 | -0.36558
2114.7969 | 121.5454 | -121.4722 | 0.15106 | 1.4211e-13 | -0.027705 | 0.00049784 | 0.068195 | -0.012279 | 0.059112 | 0.00030522 | -0.0027303 | 0.0051278 | 0.018463 | 0.035354 | 0.0072279 | -120.8409 | -1.2806 | -121.374 | 0.14827 | 0.096516 | 0.36174 | -121.5236 | 0.06515 | 0.018674 | -0.001407 | 0.098244 | 0.24264 | -0.10671 | -0.22367 | -0.051442 | -0.002788 | 0.63125 | 0.09812 | 0.14956 | -0.054546 | 0.21068 | 121.2485 | -0.052818 | 121.5373 | 121.4708 | 0.22227 | 0.091575 | -0.25778 | 121.6204 | 121.5687 | 121.8339 | 120.1916 | -121.6747 | 121.5704 | 121.7148 | 121.3655 | 121.4908 | -0.37474
2116.5312 | 121.5912 | -121.4539 | 0.13733 | 1.4211e-13 | -0.027705 | 0.00049784 | 0.068195 | -0.012707 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017823 | 0.035354 | 0.0072279 | -120.8409 | -1.2989 | -121.3832 | 0.14827 | 0.091937 | 0.3709 | -121.5465 | 0.069728 | 0.014095 | -0.001407 | 0.098244 | 0.23348 | -0.051771 | -0.22367 | -0.092647 | 0.010945 | 0.61293 | 0.070652 | 0.1633 | -0.045392 | 0.23357 | 121.2302 | -0.039085 | 121.5236 | 121.4524 | 0.22227 | 0.09615 | -0.1891 | 121.6021 | 121.5458 | 121.8248 | 120.1549 | -121.6838 | 121.5521 | 121.6873 | 121.4021 | 121.468 | -0.361
2118.2188 | 121.6461 | -121.431 | 0.11444 | 1.4211e-13 | -0.027491 | 0.00092524 | 0.067981 | -0.012279 | 0.059326 | -0.0073253 | -0.0027303 | 0.0044868 | 0.018036 | 0.035141 | 0.0072279 | -120.8409 | -1.2806 | -121.3832 | 0.14369 | 0.10567 | 0.36174 | -121.5373 | 0.060571 | 0.004938 | -0.001407 | 0.098244 | 0.24721 | -0.12503 | -0.22367 | -0.10638 | 0.029254 | 0.59005 | 0.047764 | 0.15414 | -0.008767 | 0.2473 | 121.2073 | -0.016197 | 121.4915 | 121.4296 | 0.22227 | 0.13277 | -0.23947 | 121.5747 | 121.5366 | 121.7927 | 120.1504 | -121.6518 | 121.5292 | 121.6782 | 121.3059 | 121.4359 | -0.33811
2119.9219 | 121.5683 | -121.4813 | 0.14648 | 1.4211e-13 | -0.027918 | 0.00049784 | 0.068195 | -0.012493 | 0.059326 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017823 | 0.035568 | 0.0074415 | -120.8501 | -1.2714 | -121.3924 | 0.14827 | 0.1011 | 0.35716 | -121.5602 | 0.06515 | 0.018674 | -0.005985 | 0.098244 | 0.24264 | -0.092979 | -0.22825 | -0.078918 | 0.00179 | 0.63125 | 0.088962 | 0.16788 | -0.045389 | 0.21068 | 121.2531 | -0.04824 | 121.5465 | 121.4753 | 0.22227 | 0.096153 | -0.23946 | 121.6296 | 121.5824 | 121.8385 | 120.2099 | -121.7067 | 121.5796 | 121.724 | 121.3883 | 121.5 | -0.37474
2121.6094 | 121.6782 | -121.463 | 0.10529 | 1.4211e-13 | -0.027277 | 0.00071164 | 0.068409 | -0.012707 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.01825 | 0.035568 | 0.0074415 | -120.8455 | -1.2669 | -121.3924 | 0.13912 | 0.1011 | 0.36632 | -121.5465 | 0.060571 | 0.018674 | -0.005985 | 0.1074 | 0.24264 | -0.0884 | -0.2191 | -0.083491 | 0.033831 | 0.61751 | 0.070652 | 0.15414 | -0.004191 | 0.26103 | 121.2439 | 0.002115 | 121.5236 | 121.457 | 0.21311 | 0.13735 | -0.19369 | 121.6021 | 121.5641 | 121.8293 | 120.1961 | -121.6518 | 121.5704 | 121.7057 | 121.3746 | 121.4817 | -0.32438
2123.2812 | 121.582 | -121.463 | 0.16479 | 1.4211e-13 | -0.027918 | 0.00028424 | 0.068409 | -0.012279 | 0.059539 | 0.015566 | -0.0029439 | 0.0044868 | 0.017609 | 0.035568 | 0.0070143 | -120.8501 | -1.276 | -121.3969 | 0.14369 | 0.10567 | 0.3709 | -121.5694 | 0.060571 | 0.014095 | -0.010564 | 0.098244 | 0.23348 | -0.11129 | -0.22367 | -0.10639 | -0.0211 | 0.61294 | 0.066073 | 0.17246 | -0.059121 | 0.2061 | 121.2393 | -0.066551 | 121.5236 | 121.4524 | 0.21311 | 0.068684 | -0.27609 | 121.6067 | 121.5687 | 121.8339 | 120.187 | -121.7342 | 121.5613 | 121.6965 | 121.3517 | 121.4771 | -0.38847
2124.9844 | 121.7056 | -121.431 | 0.11902 | 1.4211e-13 | -0.027491 | 0.00071164 | 0.068195 | -0.01292 | 0.059326 | 0.00030522 | -0.0029439 | 0.0044868 | 0.018036 | 0.035568 | 0.0070143 | -120.8592 | -1.2669 | -121.3969 | 0.14827 | 0.1011 | 0.36174 | -121.5694 | 0.06515 | 0.018674 | -0.001407 | 0.10282 | 0.23806 | -0.028878 | -0.22825 | -0.13843 | 0.029255 | 0.57173 | 0.034029 | 0.17246 | -0.017924 | 0.24272 | 121.2027 | -0.016197 | 121.4961 | 121.4296 | 0.22685 | 0.11904 | -0.1479 | 121.5792 | 121.5321 | 121.7927 | 120.1641 | -121.6884 | 121.5338 | 121.669 | 121.4021 | 121.4496 | -0.34727
2126.7188 | 121.6507 | -121.4722 | 0.12817 | 1.4211e-13 | -0.027491 | 0.00049784 | 0.068195 | -0.012493 | 0.059539 | 0.0079357 | -0.0027303 | 0.0044868 | 0.018036 | 0.035568 | 0.0074415 | -120.8547 | -1.2714 | -121.4015 | 0.13912 | 0.10567 | 0.36632 | -121.5786 | 0.069728 | 0.018674 | -0.005985 | 0.089087 | 0.23806 | -0.0884 | -0.22825 | -0.10639 | 0.010943 | 0.61751 | 0.07065 | 0.17704 | -0.0225 | 0.23814 | 121.2439 | -0.039087 | 121.5419 | 121.4662 | 0.22227 | 0.10988 | -0.21657 | 121.6113 | 121.5778 | 121.8385 | 120.2007 | -121.7067 | 121.5613 | 121.7102 | 121.3838 | 121.4908 | -0.35643
2128.4688 | 121.5591 | -121.4767 | 0.14648 | 1.4211e-13 | -0.027491 | 0.00092524 | 0.068195 | -0.012707 | 0.059112 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017823 | 0.035568 | 0.0072279 | -120.8592 | -1.2669 | -121.4198 | 0.13912 | 0.096516 | 0.36174 | -121.5648 | 0.051413 | 0.014095 | 0.003172 | 0.10282 | 0.23348 | -0.12503 | -0.2191 | -0.088074 | -0.007367 | 0.61751 | 0.056915 | 0.14499 | -0.049968 | 0.21525 | 121.2577 | -0.043662 | 121.5282 | 121.4799 | 0.22227 | 0.086995 | -0.27151 | 121.6159 | 121.5733 | 121.8385 | 120.2099 | -121.7113 | 121.5796 | 121.7102 | 121.3517 | 121.4908 | -0.36558
2130.1719 | 121.6095 | -121.4996 | 0.13275 | 1.4211e-13 | -0.027705 | 0.00028424 | 0.067981 | -0.012493 | 0.058898 | -0.0073253 | -0.0027303 | 0.0049142 | 0.018036 | 0.035141 | 0.0076551 | -120.8638 | -1.2623 | -121.4107 | 0.14369 | 0.1011 | 0.36632 | -121.574 | 0.055992 | 0.014095 | -0.005985 | 0.1074 | 0.24264 | -0.12503 | -0.22367 | -0.074344 | 0.010944 | 0.63582 | 0.08896 | 0.1633 | -0.031656 | 0.23357 | 121.276 | -0.02535 | 121.5556 | 121.4936 | 0.21769 | 0.10989 | -0.25778 | 121.6433 | 121.6007 | 121.866 | 120.2373 | -121.7067 | 121.607 | 121.7423 | 121.3746 | 121.5137 | -0.35642
2131.875 | 121.7194 | -121.4584 | 0.10986 | 1.4211e-13 | -0.027705 | 0.00028424 | 0.068195 | -0.012279 | 0.059539 | 0.0079357 | -0.0029439 | 0.0049142 | 0.018036 | 0.035568 | 0.0076551 | -120.8638 | -1.2669 | -121.4107 | 0.15285 | 0.1011 | 0.36632 | -121.5877 | 0.06515 | 0.009516 | -0.010564 | 0.098244 | 0.23806 | -0.12503 | -0.22825 | -0.12928 | 0.042989 | 0.59462 | 0.047761 | 0.17704 | -0.008768 | 0.25645 | 121.2302 | -0.011619 | 121.5236 | 121.4479 | 0.21769 | 0.1282 | -0.23489 | 121.6113 | 121.5595 | 121.8248 | 120.1916 | -121.6976 | 121.5567 | 121.6965 | 121.3334 | 121.468 | -0.33811
2133.5938 | 121.7331 | -121.4493 | 0.11444 | 1.4211e-13 | -0.027918 | 0.00092524 | 0.067981 | -0.012707 | 0.059112 | 0.0079357 | -0.0027303 | 0.0042732 | 0.01825 | 0.035354 | 0.0070143 | -120.873 | -1.2714 | -121.4107 | 0.14827 | 0.1011 | 0.36632 | -121.5694 | 0.051413 | 0.009516 | -0.005985 | 0.1074 | 0.24264 | -0.11587 | -0.22367 | -0.12012 | 0.033833 | 0.57631 | 0.038606 | 0.15873 | -0.013346 | 0.25188 | 121.2256 | -0.00704 | 121.5007 | 121.4433 | 0.21769 | 0.1282 | -0.23031 | 121.5976 | 121.5504 | 121.8156 | 120.1778 | -121.6838 | 121.5567 | 121.6919 | 121.3334 | 121.4588 | -0.33811
2135.3125 | 121.6827 | -121.4722 | 0.10986 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068195 | -0.012707 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017609 | 0.035568 | 0.0068005 | -120.8775 | -1.2669 | -121.4153 | 0.14827 | 0.10567 | 0.36632 | -121.5877 | 0.055992 | 0.018674 | -0.001407 | 0.1074 | 0.24264 | -0.12503 | -0.23283 | -0.11555 | 0.038411 | 0.59462 | 0.056915 | 0.17246 | -0.004189 | 0.25645 | 121.2393 | -0.002462 | 121.5282 | 121.4708 | 0.23142 | 0.13277 | -0.23489 | 121.6204 | 121.5778 | 121.8385 | 120.2053 | -121.6976 | 121.5796 | 121.7148 | 121.3471 | 121.4908 | -0.34269
2137 | 121.6415 | -121.4951 | 0.1236 | 1.4211e-13 | -0.027918 | 0.00071164 | 0.068195 | -0.013134 | 0.059326 | 0.00030522 | -0.0029439 | 0.0047004 | 0.018036 | 0.035568 | 0.0072279 | -120.873 | -1.2714 | -121.4198 | 0.13912 | 0.11025 | 0.36174 | -121.574 | 0.06515 | 0.009516 | -0.005985 | 0.098244 | 0.23806 | -0.12045 | -0.22367 | -0.078922 | 0.015521 | 0.62209 | 0.075225 | 0.15415 | -0.013343 | 0.23814 | 121.2714 | -0.025352 | 121.5602 | 121.4891 | 0.21769 | 0.11446 | -0.24405 | 121.6342 | 121.6053 | 121.8568 | 120.2236 | -121.6976 | 121.5933 | 121.7331 | 121.3746 | 121.5046 | -0.34727
2138.6875 | 121.7056 | -121.4493 | 0.11902 | 1.4211e-13 | -0.027918 | 0.00049784 | 0.068409 | -0.012707 | 0.059112 | 0.00030522 | -0.0027303 | 0.0044868 | 0.018036 | 0.035568 | 0.0074415 | -120.8821 | -1.2806 | -121.4198 | 0.15285 | 0.11025 | 0.36632 | -121.5923 | 0.060571 | 0.014095 | 0.003172 | 0.098244 | 0.24264 | -0.12045 | -0.22825 | -0.14301 | 0.033833 | 0.56715 | 0.029449 | 0.17246 | -0.008766 | 0.2473 | 121.221 | -0.020775 | 121.5099 | 121.4525 | 0.23142 | 0.12362 | -0.23947 | 121.6021 | 121.5595 | 121.8156 | 120.1687 | -121.7113 | 121.5475 | 121.6919 | 121.3288 | 121.4634 | -0.34727
2140.375 | 121.7422 | -121.4447 | 0.10986 | 1.4211e-13 | -0.027705 | 0.00071164 | 0.067981 | -0.012707 | 0.059326 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017823 | 0.035354 | 0.0072279 | -120.8821 | -1.2898 | -121.4244 | 0.15285 | 0.1011 | 0.36632 | -121.5557 | 0.060571 | 0.014095 | -0.001407 | 0.10282 | 0.23806 | -0.12045 | -0.22367 | -0.11096 | 0.042989 | 0.56258 | 0.020293 | 0.13125 | -0.008768 | 0.25645 | 121.221 | -0.007041 | 121.5053 | 121.4433 | 0.22227 | 0.1282 | -0.23031 | 121.5976 | 121.5458 | 121.811 | 120.1549 | -121.6655 | 121.5475 | 121.6828 | 121.3243 | 121.4588 | -0.33354
2142.0625 | 121.6278 | -121.5088 | 0.14191 | 1.4211e-13 | -0.027491 | 0.00092524 | 0.068195 | -0.012493 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017823 | 0.035354 | 0.0074415 | -120.873 | -1.2806 | -121.4336 | 0.14827 | 0.10567 | 0.36632 | -121.5602 | 0.055992 | 0.018674 | -0.010564 | 0.10282 | 0.23348 | -0.10214 | -0.22367 | -0.051452 | 0.006367 | 0.63582 | 0.075223 | 0.12668 | -0.036233 | 0.22441 | 121.2851 | -0.039085 | 121.5648 | 121.4982 | 0.21311 | 0.091572 | -0.24404 | 121.6571 | 121.6145 | 121.8751 | 120.2282 | -121.7021 | 121.6116 | 121.7423 | 121.4067 | 121.5275 | -0.36558
2143.75 | 121.6873 | -121.5042 | 0.13733 | 1.4211e-13 | -0.027491 | 0.00071164 | 0.068195 | -0.012707 | 0.059112 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017823 | 0.035568 | 0.0072279 | -120.8821 | -1.2898 | -121.4381 | 0.14369 | 0.10567 | 0.36632 | -121.5648 | 0.060571 | 0.014095 | -0.001407 | 0.10282 | 0.23806 | -0.12961 | -0.22367 | -0.060609 | 0.006366 | 0.62208 | 0.066067 | 0.12668 | -0.031655 | 0.22899 | 121.2805 | -0.034507 | 121.5648 | 121.5028 | 0.22227 | 0.10073 | -0.26694 | 121.6479 | 121.6099 | 121.8705 | 120.2145 | -121.7021 | 121.607 | 121.7423 | 121.3746 | 121.5183 | -0.361
2145.4844 | 121.7056 | -121.4767 | 0.14648 | 1.4211e-13 | -0.027918 | 0.00049784 | 0.068195 | -0.012707 | 0.059539 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017609 | 0.035354 | 0.0074415 | -120.9004 | -1.2852 | -121.4427 | 0.15285 | 0.11025 | 0.36174 | -121.6015 | 0.060571 | 0.018674 | -0.005985 | 0.10282 | 0.24264 | -0.083821 | -0.2191 | -0.1247 | 0.006368 | 0.57631 | 0.034024 | 0.15873 | -0.036231 | 0.21525 | 121.2577 | -0.043662 | 121.5373 | 121.4708 | 0.21311 | 0.096153 | -0.23031 | 121.6296 | 121.587 | 121.8385 | 120.1916 | -121.7479 | 121.5796 | 121.7194 | 121.3929 | 121.4954 | -0.36558
2147.1719 | 121.7148 | -121.4996 | 0.11902 | 1.4211e-13 | -0.027918 | 7.0442e-05 | 0.068409 | -0.012493 | 0.059326 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017823 | 0.035568 | 0.0074415 | -120.8913 | -1.2806 | -121.4381 | 0.14827 | 0.1011 | 0.36174 | -121.606 | 0.060571 | 0.018674 | -0.001407 | 0.10282 | 0.24264 | -0.11587 | -0.22367 | -0.1064 | 0.029255 | 0.60835 | 0.06149 | 0.16789 | -0.017924 | 0.24272 | 121.276 | -0.016197 | 121.5602 | 121.4982 | 0.22227 | 0.12362 | -0.23489 | 121.6479 | 121.6007 | 121.8614 | 120.219 | -121.725 | 121.6025 | 121.7423 | 121.3838 | 121.5183 | -0.34269
2148.8594 | 121.6507 | -121.5271 | 0.1236 | 1.4211e-13 | -0.027705 | 0.00049784 | 0.068409 | -0.012493 | 0.059539 | 0.015566 | -0.0029439 | 0.0044868 | 0.017823 | 0.035568 | 0.0072279 | -120.8959 | -1.2577 | -121.4473 | 0.14827 | 0.10567 | 0.35716 | -121.6015 | 0.06515 | 0.018674 | -0.001407 | 0.10282 | 0.24721 | -0.083821 | -0.22367 | -0.074351 | 0.024678 | 0.63124 | 0.079799 | 0.15415 | -0.017922 | 0.23356 | 121.3034 | -0.020774 | 121.5923 | 121.5257 | 0.22227 | 0.12362 | -0.20742 | 121.6754 | 121.6328 | 121.8843 | 120.2694 | -121.725 | 121.6299 | 121.7743 | 121.4433 | 121.5458 | -0.34727
2150.5625 | 121.6827 | -121.5088 | 0.15106 | 1.4211e-13 | -0.027918 | 0.00071164 | 0.068409 | -0.012493 | 0.059326 | 0.015566 | -0.0027303 | 0.0047004 | 0.017609 | 0.035354 | 0.0074415 | -120.8959 | -1.2623 | -121.4473 | 0.15285 | 0.1011 | 0.3709 | -121.6015 | 0.051413 | 0.018674 | -0.001407 | 0.093665 | 0.23806 | -0.12961 | -0.22367 | -0.092662 | 0.00179 | 0.61293 | 0.061488 | 0.15415 | -0.049967 | 0.21983 | 121.2851 | -0.057397 | 121.5602 | 121.5074 | 0.22227 | 0.086996 | -0.28067 | 121.6616 | 121.6099 | 121.8797 | 120.2465 | -121.7525 | 121.6025 | 121.7468 | 121.3792 | 121.5275 | -0.37474
2152.2344 | 121.7743 | -121.463 | 0.11902 | 1.4211e-13 | -0.027705 | 0.00049784 | 0.068195 | -0.012707 | 0.059326 | -0.0073253 | -0.0031575 | 0.0051278 | 0.018036 | 0.035354 | 0.0070143 | -120.9004 | -1.2714 | -121.4427 | 0.15285 | 0.11025 | 0.36174 | -121.6106 | 0.06515 | 0.014095 | -0.001407 | 0.098244 | 0.24264 | -0.092979 | -0.22367 | -0.1476 | 0.033833 | 0.56257 | 0.020291 | 0.16789 | -0.008766 | 0.24272 | 121.2393 | -0.020775 | 121.5282 | 121.4616 | 0.22227 | 0.12362 | -0.212 | 121.6159 | 121.5733 | 121.8248 | 120.1916 | -121.7296 | 121.5613 | 121.7057 | 121.37 | 121.4771 | -0.34269
2153.9219 | 121.7468 | -121.4859 | 0.10529 | 1.4211e-13 | -0.028132 | 0.00092524 | 0.068409 | -0.012707 | 0.059753 | -0.0073253 | -0.0029439 | 0.0051278 | 0.017609 | 0.035782 | 0.0068005 | -120.9004 | -1.2577 | -121.4473 | 0.14827 | 0.1011 | 0.36174 | -121.606 | 0.060571 | 0.009516 | -0.010564 | 0.10282 | 0.23806 | -0.0884 | -0.2191 | -0.12013 | 0.042988 | 0.58546 | 0.0386 | 0.15873 | -0.004191 | 0.25645 | 121.2668 | -0.002464 | 121.5465 | 121.4753 | 0.20853 | 0.13277 | -0.19369 | 121.6342 | 121.587 | 121.8476 | 120.2282 | -121.7113 | 121.5887 | 121.724 | 121.3975 | 121.4954 | -0.32438
2155.6094 | 121.7331 | -121.4722 | 0.13275 | 1.4211e-13 | -0.027918 | 0.00049784 | 0.068409 | -0.012707 | 0.059539 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017823 | 0.035568 | 0.0074415 | -120.8913 | -1.2211 | -121.429 | 0.15743 | 0.11941 | 0.38005 | -121.6015 | 0.060571 | 0.018674 | -0.001407 | 0.10282 | 0.24264 | -0.083821 | -0.22367 | -0.12928 | 0.02468 | 0.58088 | 0.04318 | 0.17246 | -0.01334 | 0.2473 | 121.2485 | -0.029929 | 121.5327 | 121.4708 | 0.22227 | 0.10989 | -0.21657 | 121.6296 | 121.5916 | 121.8522 | 120.2511 | -121.7342 | 121.575 | 121.7148 | 121.3883 | 121.4908 | -0.35642
2157.2969 | 121.6827 | -121.5179 | 0.15564 | 1.4211e-13 | -0.028346 | 7.0442e-05 | 0.068195 | -0.012279 | 0.059539 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017823 | 0.035354 | 0.0070143 | -120.8913 | -1.2211 | -121.429 | 0.16659 | 0.11941 | 0.38463 | -121.5923 | 0.069728 | 0.014095 | -0.001407 | 0.098244 | 0.24721 | -0.10214 | -0.2191 | -0.07435 | 0.010947 | 0.62666 | 0.088956 | 0.16331 | -0.036229 | 0.22899 | 121.2988 | -0.057396 | 121.5877 | 121.5165 | 0.21769 | 0.091575 | -0.25778 | 121.6845 | 121.6374 | 121.9026 | 120.2969 | -121.7479 | 121.6162 | 121.7652 | 121.4158 | 121.532 | -0.37474
2158.9844 | 121.637 | -121.4859 | 0.16937 | 1.4211e-13 | -0.028132 | 0.00028424 | 0.068195 | -0.012707 | 0.059539 | 0.0079357 | -0.0027303 | 0.0047004 | 0.018036 | 0.035782 | 0.0074415 | -120.8867 | -1.2119 | -121.4381 | 0.16659 | 0.12399 | 0.38463 | -121.6015 | 0.060571 | 0.014095 | -0.005985 | 0.098244 | 0.23806 | -0.13419 | -0.22825 | -0.11555 | -0.002786 | 0.59919 | 0.047757 | 0.16331 | -0.045383 | 0.21526 | 121.2576 | -0.071129 | 121.5465 | 121.4799 | 0.22227 | 0.068685 | -0.30356 | 121.6525 | 121.6099 | 121.8705 | 120.274 | -121.7708 | 121.5841 | 121.724 | 121.3517 | 121.5 | -0.39763
2160.6719 | 121.6827 | -121.5225 | 0.17853 | 1.4211e-13 | -0.028132 | 0.00028424 | 0.068409 | -0.012279 | 0.059539 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017609 | 0.035568 | 0.0072279 | -120.8959 | -1.2257 | -121.4244 | 0.16659 | 0.11941 | 0.38005 | -121.6152 | 0.055992 | 0.018674 | -0.005985 | 0.10282 | 0.24264 | -0.05635 | -0.22367 | -0.092666 | -0.011941 | 0.62666 | 0.098113 | 0.19078 | -0.059117 | 0.20152 | 121.2988 | -0.075706 | 121.5785 | 121.5165 | 0.21769 | 0.064109 | -0.23488 | 121.6891 | 121.6419 | 121.9026 | 120.2969 | -121.7937 | 121.6253 | 121.7652 | 121.4662 | 121.5412 | -0.4022
2162.3906 | 121.6736 | -121.5042 | 0.16022 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068195 | -0.012707 | 0.059539 | 0.023196 | -0.0027303 | 0.0049142 | 0.018036 | 0.035782 | 0.0070143 | -120.8821 | -1.2257 | -121.4336 | 0.17117 | 0.11025 | 0.38463 | -121.6106 | 0.055992 | 0.009516 | -0.001407 | 0.098244 | 0.23806 | -0.10214 | -0.22367 | -0.1064 | 0.010949 | 0.62208 | 0.070645 | 0.17704 | -0.049964 | 0.22441 | 121.2805 | -0.061973 | 121.5602 | 121.5028 | 0.22227 | 0.077841 | -0.26235 | 121.6754 | 121.6145 | 121.8888 | 120.2786 | -121.7708 | 121.6025 | 121.7423 | 121.4021 | 121.5137 | -0.38389
2164.0938 | 121.7285 | -121.4767 | 0.13733 | 1.4211e-13 | -0.028132 | 0.00028424 | 0.068195 | -0.012707 | 0.058898 | 0.00030522 | -0.0027303 | 0.0047004 | 0.017823 | 0.035354 | 0.0070143 | -120.8821 | -1.2257 | -121.429 | 0.16659 | 0.12399 | 0.38921 | -121.6152 | 0.060571 | 0.009516 | -0.010564 | 0.098244 | 0.24721 | -0.12961 | -0.22367 | -0.13844 | 0.029258 | 0.59462 | 0.047758 | 0.1862 | -0.013339 | 0.25188 | 121.2531 | -0.039085 | 121.5373 | 121.4662 | 0.21311 | 0.10989 | -0.26694 | 121.6433 | 121.6007 | 121.866 | 120.2511 | -121.7525 | 121.575 | 121.724 | 121.3471 | 121.4863 | -0.361
2165.7812 | 121.6644 | -121.5088 | 0.16022 | 1.4211e-13 | -0.027918 | 0.00049784 | 0.067981 | -0.012707 | 0.059326 | -0.0073253 | -0.0031575 | 0.0044868 | 0.018036 | 0.035568 | 0.0072279 | -120.8867 | -1.2486 | -121.429 | 0.16659 | 0.12399 | 0.38921 | -121.606 | 0.06515 | 0.014095 | -0.001407 | 0.10282 | 0.23806 | -0.11587 | -0.22367 | -0.097241 | 0.00637 | 0.62208 | 0.079801 | 0.17704 | -0.036227 | 0.22899 | 121.2851 | -0.057395 | 121.5739 | 121.5074 | 0.22227 | 0.077841 | -0.27609 | 121.6754 | 121.6328 | 121.898 | 120.2602 | -121.7662 | 121.6116 | 121.7468 | 121.3929 | 121.5229 | -0.38389
2167.4844 | 121.7972 | -121.4767 | 0.14648 | 1.4211e-13 | -0.028346 | 0.00071164 | 0.068622 | -0.012707 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017609 | 0.035568 | 0.0074415 | -120.8867 | -1.2394 | -121.4244 | 0.18032 | 0.12857 | 0.39837 | -121.6472 | 0.055992 | 0.014095 | -0.005985 | 0.098244 | 0.23348 | -0.12503 | -0.22825 | -0.17049 | 0.033839 | 0.59004 | 0.052337 | 0.22283 | -0.017915 | 0.25188 | 121.2485 | -0.04824 | 121.5327 | 121.4708 | 0.22227 | 0.086995 | -0.27151 | 121.6571 | 121.6053 | 121.8751 | 120.2374 | -121.7937 | 121.575 | 121.7102 | 121.3517 | 121.4908 | -0.37474
2169.1875 | 121.7468 | -121.4081 | 0.10986 | 1.4211e-13 | -0.027918 | 0.00049784 | 0.068195 | -0.012707 | 0.059326 | 0.0079357 | -0.0031575 | 0.0044868 | 0.018036 | 0.035568 | 0.0072279 | -120.8455 | -1.0059 | -121.3924 | 0.1849 | 0.20641 | 0.4121 | -121.6564 | 0.055992 | 0.009516 | -0.005985 | 0.098244 | 0.24264 | -0.12503 | -0.22825 | -0.24832 | 0.075038 | 0.56258 | 0.01572 | 0.26404 | 0.096548 | 0.30224 | 121.1798 | -0.011619 | 121.4641 | 121.4021 | 0.22227 | 0.13277 | -0.23489 | 121.593 | 121.6145 | 121.8202 | 120.4022 | -121.7663 | 121.5063 | 121.6507 | 121.2831 | 121.4176 | -0.33811
2170.8906 | 121.6278 | -121.4859 | 0.13733 | 1.4211e-13 | -0.027918 | 0.00092524 | 0.068195 | -0.012493 | 0.059326 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017823 | 0.035782 | 0.0070143 | -120.8821 | -1.015 | -121.4381 | 0.14827 | 0.20183 | 0.4121 | -121.6243 | 0.060571 | 0.018674 | -0.005985 | 0.093665 | 0.23806 | -0.11587 | -0.22367 | -0.13845 | 0.010945 | 0.60377 | 0.047757 | 0.1862 | 0.064503 | 0.27477 | 121.2622 | -0.043664 | 121.5465 | 121.4799 | 0.21769 | 0.10073 | -0.2532 | 121.6342 | 121.6877 | 121.898 | 120.4709 | -121.7617 | 121.5796 | 121.724 | 121.37 | 121.5046 | -0.361
2172.5938 | 121.6965 | -121.5088 | 0.12817 | 1.4211e-13 | -0.027918 | 0.00028424 | 0.068409 | -0.012279 | 0.059539 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017823 | 0.035568 | 0.0072279 | -120.9004 | -1.0105 | -121.4565 | 0.14827 | 0.1011 | 0.4121 | -121.6243 | 0.06515 | 0.014095 | -0.005985 | 0.10282 | 0.24264 | -0.11129 | -0.22367 | -0.11556 | 0.0201 | 0.60835 | 0.052332 | 0.16789 | -0.027079 | 0.28393 | 121.2851 | -0.025352 | 121.5739 | 121.5028 | 0.21769 | 0.11446 | -0.23947 | 121.6571 | 121.6099 | 121.9209 | 120.4983 | -121.7525 | 121.6116 | 121.7514 | 121.3975 | 121.5229 | -0.35185
2174.2656 | 121.7606 | -121.4813 | 0.11902 | 1.4211e-13 | -0.028132 | 0.00071164 | 0.068409 | -0.012707 | 0.059112 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017823 | 0.035995 | 0.0072279 | -120.9142 | -0.98299 | -121.461 | 0.14369 | 0.11025 | 0.42126 | -121.6381 | 0.055992 | 0.004938 | -0.005985 | 0.10282 | 0.23348 | -0.12961 | -0.23283 | -0.15676 | 0.024676 | 0.56715 | 0.020287 | 0.17705 | -0.008766 | 0.30224 | 121.2485 | -0.016197 | 121.5373 | 121.4753 | 0.22685 | 0.11446 | -0.24863 | 121.625 | 121.5916 | 121.9026 | 120.4983 | -121.7571 | 121.5841 | 121.7148 | 121.3517 | 121.4863 | -0.35185
2175.9531 | 121.6324 | -121.5546 | 0.15564 | 1.4211e-13 | -0.028132 | 0.00028424 | 0.068622 | -0.012279 | 0.059539 | 0.0079357 | -0.0027303 | 0.0047004 | 0.018036 | 0.035782 | 0.0070143 | -120.9096 | -0.9601 | -121.4656 | 0.14369 | 0.11025 | 0.42584 | -121.6701 | 0.055992 | 0.009516 | -0.001407 | 0.098244 | 0.24264 | -0.12503 | -0.22825 | -0.11557 | -0.011945 | 0.64497 | 0.088951 | 0.20452 | -0.045387 | 0.2702 | 121.3263 | -0.057396 | 121.6106 | 121.5532 | 0.22685 | 0.086997 | -0.28067 | 121.6983 | 121.6648 | 121.9804 | 120.5945 | -121.8258 | 121.6528 | 121.7972 | 121.4295 | 121.5641 | -0.38389
2177.6562 | 120.9824 | -98.877 | 21.7987 | 1.4211e-13 | -0.028346 | 7.0442e-05 | 0.067981 | -0.013134 | 0.058685 | 0.00030522 | -0.0031575 | 0.0051278 | 0.017609 | 0.035568 | 0.0065869 | -91.8185 | -0.87311 | -92.2333 | 28.4656 | 28.4996 | 28.6483 | -87.6762 | 0.055992 | 0.004938 | -0.010564 | 0.098244 | 0.23348 | -0.083821 | -0.22825 | 11.2008 | 6.6669 | 7.0584 | 6.6437 | -4.5571 | 6.7009 | 6.8496 | 98.6487 | -21.7005 | 98.9329 | 98.8664 | 0.21769 | -21.5652 | -21.8825 | 127.3426 | 127.3765 | 127.5253 | 98.0038 | -109.4749 | 98.9752 | 99.1104 | 98.7931 | 98.8819 | -22.027
2179.3281 | 121.2387 | -10.0067 | 111.1267 | 1.4211e-13 | -0.027277 | 0.0013526 | 0.068836 | -0.01292 | 0.058044 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017609 | 0.035354 | 0.0070143 | -11.802 | 0.98581 | -11.9623 | 109.3291 | 109.3084 | 109.3233 | -11.982 | 0.033099 | -0.013377 | -0.038036 | 0.07993 | 0.21059 | -0.14792 | -0.25572 | -1.9753 | -1.7976 | -1.7953 | -1.9556 | 0.019698 | -1.8183 | -1.8034 | 9.751 | -111.0468 | 10.0398 | 9.9687 | 0.21769 | -110.9161 | -111.2746 | 119.3358 | 119.3152 | 119.33 | 10.9925 | -123.1087 | 10.0866 | 10.2173 | 9.8588 | 9.9933 | -111.3824
2181.0156 | 121.2662 | -70.2255 | 50.8392 | 1.4211e-13 | -0.027491 | 0.00071164 | 0.068836 | -0.012707 | 0.058471 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017823 | 0.035782 | 0.0068005 | -50.8557 | -1.8758 | -50.6991 | 70.8844 | 70.4471 | 71.2614 | -51.3058 | 0.046835 | 0.004938 | -0.019721 | 0.07993 | 0.2289 | -0.14334 | -0.24657 | 18.9197 | 20.0451 | 19.3698 | 19.5264 | 0.60667 | 19.6079 | 20.4222 | 69.979 | -50.7593 | 70.2724 | 70.2058 | 0.22685 | -50.6103 | -50.9826 | 141.1099 | 140.6726 | 141.4869 | 68.3497 | -102.145 | 70.3055 | 70.4544 | 70.0822 | 70.2305 | -51.0858
2182.7031 | 121.4951 | -118.8538 | 2.3621 | 1.4211e-13 | -0.028346 | 0.00071164 | 0.067981 | -0.01292 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017823 | 0.036209 | 0.0068005 | -118.451 | -1.0929 | -118.943 | 2.3734 | 2.3814 | 2.5961 | -119.1838 | 0.06515 | 0.014095 | -0.001407 | 0.1074 | 0.24264 | -0.10671 | -0.22367 | -0.33002 | 0.011309 | 0.40276 | -0.089221 | 0.2408 | 0.019339 | 0.23404 | 118.6301 | -2.2547 | 118.9189 | 118.8524 | 0.22227 | -2.1194 | -2.4688 | 121.2271 | 121.2352 | 121.4499 | 117.7609 | -121.5458 | 118.9612 | 119.0964 | 118.747 | 118.8679 | -2.5857
2184.375 | 121.3989 | -96.1349 | 25.0854 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068622 | -0.012707 | 0.058898 | -0.0073253 | -0.0031575 | 0.0051278 | 0.017609 | 0.035782 | 0.0072279 | -64.5176 | -1.7568 | -64.672 | 56.9203 | 56.6188 | 57.0769 | -64.9235 | 0.037677 | 0.004938 | -0.019721 | 0.089087 | 0.22432 | -0.13876 | -0.23741 | 31.2114 | 31.8348 | 31.6174 | 31.4629 | 0.25148 | 31.5333 | 31.9914 | 95.8975 | -24.9964 | 96.1726 | 96.1152 | 0.21769 | -24.8611 | -25.2242 | 153.0552 | 152.7537 | 153.2118 | 94.3782 | -90.009 | 96.224 | 96.3593 | 95.9962 | 96.1399 | -25.3229
2186.0625 | 121.4493 | -114.9399 | 6.3492 | 1.4211e-13 | -0.028132 | 0.00028424 | 0.067981 | -0.012707 | 0.059112 | -0.0073253 | -0.0029439 | 0.0047004 | 0.017609 | 0.035354 | 0.0070143 | -115.0813 | -0.90058 | -115.5734 | 5.7614 | 5.8019 | 5.9705 | -115.8 | 0.051413 | 0.018674 | -0.005985 | 0.098244 | 0.24264 | -0.074664 | -0.2191 | -0.86007 | -0.5878 | -0.14143 | -0.63349 | 0.22659 | -0.54733 | -0.37866 | 114.7208 | -6.2509 | 114.9913 | 114.9339 | 0.21311 | -6.1065 | -6.4238 | 120.7013 | 120.7417 | 120.9104 | 114.0393 | -122.1491 | 115.0381 | 115.1825 | 114.8652 | 114.9586 | -6.5683
2187.7656 | 121.4264 | -116.7526 | 4.6051 | 1.4211e-13 | -0.027918 | 0.00028424 | 0.068409 | -0.012707 | 0.058898 | 0.00030522 | -0.0029439 | 0.0051278 | 0.017395 | 0.035568 | 0.0070143 | -116.116 | -0.94179 | -116.6447 | 4.6397 | 4.6892 | 4.89 | -116.8852 | 0.055992 | 0.014095 | -0.001407 | 0.093665 | 0.23348 | -0.05635 | -0.22825 | -0.13253 | 0.034569 | 0.6366 | 0.10794 | 0.24048 | 0.084075 | 0.28487 | 116.5244 | -4.5114 | 116.8086 | 116.7512 | 0.22685 | -4.3716 | -4.6615 | 121.3923 | 121.4418 | 121.6426 | 115.8108 | -121.4903 | 116.8463 | 116.9861 | 116.6963 | 116.7667 | -4.8334
2189.5156 | 121.3943 | -117.2104 | 4.1656 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068195 | -0.012493 | 0.059753 | -0.0073253 | -0.0025167 | 0.0047004 | 0.017609 | 0.035995 | 0.0070143 | -116.5922 | -0.94179 | -117.1162 | 4.1498 | 4.2221 | 4.4321 | -117.3614 | 0.060571 | 0.014095 | -0.005985 | 0.10282 | 0.24264 | -0.12045 | -0.22825 | -0.15098 | -0.015864 | 0.61821 | 0.094141 | 0.24512 | 0.056478 | 0.26647 | 116.9821 | -4.0628 | 117.271 | 117.2044 | 0.22227 | -3.923 | -4.2861 | 121.3602 | 121.4325 | 121.6425 | 116.2686 | -121.527 | 117.3132 | 117.453 | 117.0899 | 117.2245 | -4.3939
2191.2031 | 121.5271 | -117.3706 | 3.9368 | 1.4211e-13 | -0.027918 | 0.00028424 | 0.068195 | -0.012493 | 0.058898 | 0.0079357 | -0.0031575 | 0.0047004 | 0.018036 | 0.035995 | 0.0068005 | -116.789 | -0.95094 | -117.3085 | 3.9621 | 4.0298 | 4.2398 | -117.5491 | 0.060571 | 0.014095 | -0.010564 | 0.10282 | 0.23348 | -0.10214 | -0.22367 | -0.1785 | 0.025303 | 0.58156 | 0.06207 | 0.24057 | 0.093045 | 0.30305 | 117.1469 | -3.8339 | 117.4312 | 117.36 | 0.21311 | -3.7033 | -4.0389 | 121.3327 | 121.4004 | 121.6104 | 116.4197 | -121.4859 | 117.4734 | 117.6041 | 117.2685 | 117.3847 | -4.1604
2192.9688 | 121.3943 | -117.4667 | 3.9368 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017823 | 0.035782 | 0.0070143 | -116.8074 | -0.91889 | -117.336 | 3.9483 | 3.9611 | 4.2261 | -117.5812 | 0.055992 | 0.014095 | -0.005985 | 0.10282 | 0.23806 | -0.083821 | -0.22825 | -0.11442 | 0.011568 | 0.65937 | 0.13073 | 0.24515 | 0.024361 | 0.28931 | 117.2385 | -3.8339 | 117.5227 | 117.4608 | 0.22227 | -3.6987 | -4.0206 | 121.4151 | 121.4279 | 121.6928 | 116.5478 | -121.5179 | 117.5696 | 117.7048 | 117.3829 | 117.4808 | -4.165
2194.7812 | 121.4447 | -117.5903 | 3.7674 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068195 | -0.012707 | 0.059112 | 0.00030522 | -0.0027303 | 0.0051278 | 0.017609 | 0.035568 | 0.0072279 | -116.9951 | -0.92347 | -117.5146 | 3.7606 | 3.778 | 4.0521 | -117.7597 | 0.060571 | 0.018674 | -0.010564 | 0.098244 | 0.24721 | -0.12503 | -0.22825 | -0.1694 | -0.006773 | 0.59526 | 0.075774 | 0.24518 | 0.010577 | 0.2847 | 117.3621 | -3.6692 | 117.6509 | 117.5798 | 0.21769 | -3.5202 | -3.8924 | 121.351 | 121.3683 | 121.6424 | 116.6669 | -121.5271 | 117.6886 | 117.8375 | 117.4653 | 117.609 | -3.9956
2196.5625 | 121.4996 | -117.5674 | 3.7628 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068409 | -0.012493 | 0.059112 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017823 | 0.035782 | 0.0072279 | -116.9768 | -0.91431 | -117.5054 | 3.7835 | 3.7917 | 4.0613 | -117.7552 | 0.051413 | 0.014095 | 0.003172 | 0.098244 | 0.24264 | -0.0884 | -0.22825 | -0.18771 | 0.020697 | 0.59068 | 0.062043 | 0.24975 | 0.028892 | 0.29843 | 117.3392 | -3.6646 | 117.6189 | 117.5706 | 0.23142 | -3.5202 | -3.8512 | 121.351 | 121.3592 | 121.6287 | 116.6531 | -121.518 | 117.6657 | 117.8101 | 117.479 | 117.5815 | -3.9911
2198.3125 | 121.5225 | -117.6865 | 3.6255 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068409 | -0.012707 | 0.059112 | 0.015566 | -0.0027303 | 0.0044868 | 0.017823 | 0.035568 | 0.0072279 | -117.1233 | -0.91889 | -117.6473 | 3.637 | 3.6635 | 3.9193 | -117.8925 | 0.060571 | 0.014095 | -0.001407 | 0.1074 | 0.23348 | -0.12961 | -0.23741 | -0.20606 | 0.011517 | 0.56319 | 0.039134 | 0.24519 | 0.038011 | 0.29383 | 117.4491 | -3.5181 | 117.747 | 117.6851 | 0.236 | -3.392 | -3.7551 | 121.3235 | 121.35 | 121.6058 | 116.7676 | -121.518 | 117.7939 | 117.9199 | 117.5569 | 117.7006 | -3.8629
2200.0781 | 121.5317 | -117.8741 | 3.4195 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.068195 | -0.012707 | 0.059112 | 0.00030522 | -0.0029439 | 0.0047004 | 0.018036 | 0.036209 | 0.0072279 | -117.2835 | -0.92347 | -117.8167 | 3.4813 | 3.4941 | 3.7133 | -118.0619 | 0.055992 | 0.014095 | -0.005985 | 0.10282 | 0.24264 | -0.12961 | -0.22825 | -0.1878 | 0.061845 | 0.59063 | 0.057422 | 0.24522 | 0.074583 | 0.29378 | 117.6459 | -3.3167 | 117.9301 | 117.8682 | 0.22227 | -3.1769 | -3.5491 | 121.3555 | 121.3682 | 121.5874 | 116.9507 | -121.4814 | 117.977 | 118.1168 | 117.7445 | 117.8882 | -3.6477
2201.7812 | 121.5408 | -117.7551 | 3.5522 | 1.4211e-13 | -0.028346 | 0.00071164 | 0.068195 | -0.012493 | 0.059112 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017823 | 0.035995 | 0.0074415 | -117.224 | -0.92805 | -117.7481 | 3.5409 | 3.5536 | 3.7728 | -118.0024 | 0.060571 | 0.014095 | -0.005985 | 0.098244 | 0.23348 | -0.13876 | -0.22367 | -0.24729 | -0.011387 | 0.53113 | 0.007077 | 0.25437 | 0.001358 | 0.22055 | 117.5315 | -3.454 | 117.8157 | 117.7491 | 0.21769 | -3.3188 | -3.691 | 121.296 | 121.3087 | 121.5279 | 116.8271 | -121.5547 | 117.8534 | 117.9886 | 117.6164 | 117.7692 | -3.7759
2203.5312 | 121.5179 | -117.7597 | 3.5614 | 1.4211e-13 | -0.028346 | 0.00049784 | 0.068195 | -0.012707 | 0.058898 | 0.00030522 | -0.0025167 | 0.0049142 | 0.017823 | 0.035782 | 0.0072279 | -117.1919 | -0.94179 | -117.7252 | 3.5592 | 3.5765 | 3.7957 | -117.9795 | 0.055992 | 0.014095 | -0.010564 | 0.10282 | 0.24264 | -0.10214 | -0.22367 | -0.21982 | -0.002228 | 0.56776 | 0.034546 | 0.25436 | 0.015098 | 0.23429 | 117.536 | -3.4586 | 117.8157 | 117.7491 | 0.21311 | -3.3188 | -3.6635 | 121.3189 | 121.3362 | 121.5554 | 116.8179 | -121.5409 | 117.8625 | 118.0023 | 117.6576 | 117.7738 | -3.7851
2205.2812 | 121.4081 | -117.8009 | 3.598 | 1.4211e-13 | -0.028346 | 0.00049784 | 0.068409 | -0.012707 | 0.058898 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017609 | 0.035782 | 0.0072279 | -117.1965 | -0.94636 | -117.7343 | 3.5592 | 3.5719 | 3.7865 | -117.9887 | 0.060571 | 0.014095 | -0.005985 | 0.10282 | 0.25179 | -0.13876 | -0.22367 | -0.18778 | -0.038849 | 0.60438 | 0.066588 | 0.25437 | -0.026102 | 0.18851 | 117.5772 | -3.4952 | 117.8615 | 117.7949 | 0.21769 | -3.3462 | -3.7368 | 121.3601 | 121.3728 | 121.5874 | 116.8545 | -121.5867 | 117.9037 | 118.0527 | 117.6621 | 117.815 | -3.8217
2207.0312 | 121.4767 | -117.8284 | 3.5294 | 1.4211e-13 | -0.028346 | 0.00049784 | 0.068195 | -0.012707 | 0.059326 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017609 | 0.035995 | 0.0065869 | -117.2332 | -0.95552 | -117.7709 | 3.5271 | 3.5353 | 3.7545 | -118.0207 | 0.055992 | 0.014095 | -0.005985 | 0.10282 | 0.24721 | -0.12961 | -0.22367 | -0.19236 | -0.002234 | 0.59522 | 0.057428 | 0.24979 | 0.005931 | 0.22512 | 117.6047 | -3.4265 | 117.8844 | 117.8224 | 0.21769 | -3.2821 | -3.659 | 121.3555 | 121.3637 | 121.5829 | 116.8728 | -121.5501 | 117.9312 | 118.0756 | 117.6988 | 117.8425 | -3.753
2208.7188 | 121.4081 | -117.7917 | 3.598 | 1.4211e-13 | -0.028346 | 0.00049784 | 0.068409 | -0.012707 | 0.059326 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017823 | 0.035568 | 0.0074415 | -117.1874 | -0.96468 | -117.7206 | 3.5729 | 3.5857 | 3.8003 | -117.9795 | 0.06515 | 0.018674 | -0.001407 | 0.098244 | 0.23806 | -0.12961 | -0.22825 | -0.18777 | -0.025114 | 0.60438 | 0.071168 | 0.25894 | -0.012365 | 0.20225 | 117.5635 | -3.4998 | 117.8569 | 117.7903 | 0.22685 | -3.36 | -3.7276 | 121.3647 | 121.3774 | 121.592 | 116.8271 | -121.5775 | 117.89 | 118.0298 | 117.6621 | 117.8104 | -3.8263
2210.4844 | 121.4355 | -117.8787 | 3.5248 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068622 | -0.01292 | 0.058898 | -0.0073253 | -0.0027303 | 0.0049142 | 0.017823 | 0.035568 | 0.0068005 | -117.2377 | -0.99215 | -117.7755 | 3.5225 | 3.5353 | 3.7453 | -118.039 | 0.055992 | 0.014095 | -0.005985 | 0.093665 | 0.23806 | -0.12045 | -0.22367 | -0.16033 | -0.002234 | 0.64099 | 0.1032 | 0.26353 | 0.010509 | 0.22055 | 117.655 | -3.4311 | 117.9347 | 117.8727 | 0.21769 | -3.2867 | -3.6452 | 121.4013 | 121.414 | 121.624 | 116.8866 | -121.5638 | 117.9724 | 118.1168 | 117.7583 | 117.8928 | -3.7485
2212.2344 | 121.5088 | -117.6086 | 3.7354 | 1.4211e-13 | -0.028346 | 0.00028424 | 0.068409 | -0.01292 | 0.059539 | 0.00030522 | -0.0031575 | 0.0051278 | 0.017609 | 0.035568 | 0.0070143 | -116.9951 | -0.99673 | -117.5283 | 3.7606 | 3.7826 | 3.9926 | -117.7872 | 0.06515 | 0.014095 | -0.005985 | 0.10282 | 0.23348 | -0.12961 | -0.22825 | -0.17856 | 0.02527 | 0.61357 | 0.08035 | 0.25891 | 0.047199 | 0.25722 | 117.3804 | -3.6325 | 117.6738 | 117.6027 | 0.22227 | -3.5019 | -3.865 | 121.3693 | 121.3912 | 121.6012 | 116.6119 | -121.5226 | 117.7115 | 117.8421 | 117.479 | 117.6227 | -3.9636
2213.9219 | 121.5317 | -117.7551 | 3.5797 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068195 | -0.01292 | 0.058898 | 0.00030522 | -0.0027303 | 0.0051278 | 0.017395 | 0.035782 | 0.0070143 | -117.1782 | -1.015 | -117.7206 | 3.5775 | 3.5994 | 3.814 | -117.9704 | 0.055992 | 0.004938 | -0.005985 | 0.098244 | 0.24264 | -0.12503 | -0.22825 | -0.21524 | -0.002226 | 0.57692 | 0.034547 | 0.24978 | 0.019682 | 0.23429 | 117.5269 | -3.4815 | 117.8111 | 117.7491 | 0.22227 | -3.3371 | -3.7047 | 121.3326 | 121.3545 | 121.5691 | 116.7401 | -121.5501 | 117.8534 | 117.9978 | 117.6301 | 117.7601 | -3.808
2215.6719 | 121.4264 | -117.897 | 3.5156 | 1.4211e-13 | -0.028132 | 0.00071164 | 0.068622 | -0.01292 | 0.058898 | -0.0073253 | -0.0033713 | 0.0049142 | 0.017609 | 0.035354 | 0.0065869 | -117.2286 | -1.0563 | -117.7755 | 3.518 | 3.5353 | 3.7499 | -118.0345 | 0.060571 | 0.014095 | -0.001407 | 0.10282 | 0.23806 | -0.10671 | -0.23283 | -0.13743 | 0.002342 | 0.66846 | 0.12151 | 0.25895 | 0.019664 | 0.23428 | 117.6642 | -3.4128 | 117.9576 | 117.8956 | 0.23142 | -3.2776 | -3.6223 | 121.415 | 121.4323 | 121.6469 | 116.8408 | -121.5501 | 117.9999 | 118.1351 | 117.7903 | 117.9111 | -3.7485
2217.4062 | 121.4218 | -117.9337 | 3.4103 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.067981 | -0.012707 | 0.059112 | 0.0079357 | -0.0025167 | 0.0047004 | 0.017823 | 0.035782 | 0.0072279 | -117.343 | -1.0929 | -117.8946 | 3.3944 | 3.4162 | 3.6263 | -118.1581 | 0.055992 | 0.014095 | -0.005985 | 0.093665 | 0.24721 | -0.12503 | -0.22825 | -0.22445 | -0.015988 | 0.59062 | 0.0391 | 0.26355 | 0.005898 | 0.21594 | 117.7054 | -3.3167 | 117.9896 | 117.9277 | 0.22227 | -3.1631 | -3.5354 | 121.328 | 121.3499 | 121.5599 | 116.8408 | -121.5684 | 118.0273 | 118.1809 | 117.8086 | 117.9477 | -3.6386
2219.0938 | 121.5088 | -118.4738 | 2.8473 | 1.4211e-13 | -0.028346 | 0.00028424 | 0.067554 | -0.01292 | 0.059539 | 0.0079357 | -0.0029439 | 0.0044868 | 0.017609 | 0.035782 | 0.0068005 | -117.9062 | -1.1295 | -118.4577 | 2.8358 | 2.9126 | 3.0723 | -118.7259 | 0.055992 | 0.009516 | -0.010564 | 0.093665 | 0.23806 | -0.11587 | -0.2191 | -0.25207 | -0.011502 | 0.56764 | 0.016132 | 0.2682 | 0.065265 | 0.22498 | 118.2547 | -2.7536 | 118.5298 | 118.4633 | 0.20853 | -2.6092 | -2.9632 | 121.3096 | 121.3864 | 121.5461 | 117.3443 | -121.5732 | 118.5675 | 118.7119 | 118.3579 | 118.4833 | -3.0664
2220.7969 | 121.4081 | -118.5013 | 2.8839 | 1.4211e-13 | -0.028773 | 0.00049784 | 0.068409 | -0.012707 | 0.059326 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017395 | 0.035568 | 0.0070143 | -117.8833 | -1.189 | -118.4348 | 2.8587 | 2.8805 | 3.086 | -118.6435 | 0.055992 | 0.023253 | -0.001407 | 0.10282 | 0.23806 | -0.12503 | -0.22825 | -0.14218 | -0.025232 | 0.618 | 0.06649 | 0.20867 | -0.003408 | 0.2021 | 118.273 | -2.7811 | 118.5573 | 118.4999 | 0.22685 | -2.6459 | -3.0089 | 121.36 | 121.3818 | 121.5873 | 117.3123 | -121.5274 | 118.6041 | 118.7393 | 118.3763 | 118.5245 | -3.1122
2222.4844 | 121.0373 | -32.4142 | 88.266 | 1.4211e-13 | -0.027277 | 0.0013526 | 0.068622 | -0.01292 | 0.058044 | 0.0079357 | -0.0027303 | 0.0042732 | 0.017823 | 0.035995 | 0.0068005 | -32.5696 | 0.75688 | -32.6973 | 88.328 | 88.3049 | 88.3762 | -32.6925 | 0.033099 | -0.008798 | -0.028879 | 0.07993 | 0.21974 | -0.1525 | -0.25115 | -0.27823 | 0.062033 | -0.15536 | -0.28309 | -0.004858 | 0.038928 | 0.11022 | 32.1631 | -88.1861 | 32.4473 | 32.3854 | 0.22227 | -88.0462 | -88.4185 | 120.7423 | 120.7192 | 120.7905 | 33.1711 | -120.9585 | 32.4942 | 32.634 | 32.2617 | 32.4054 | -88.5171
2224.2188 | 120.282 | -33.3618 | 87.085 | 1.4211e-13 | -0.027491 | 0.0011388 | 0.068836 | -0.013134 | 0.058044 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017823 | 0.035782 | 0.0070143 | -34.7947 | 0.66073 | -34.959 | 86.2815 | 86.2902 | 86.3158 | -34.927 | 0.033099 | -0.008798 | -0.033458 | 0.07993 | 0.21974 | -0.13876 | -0.24657 | -1.5652 | -0.80348 | -1.4329 | -1.5972 | -0.032014 | -0.79477 | -0.76912 | 33.1152 | -87.005 | 33.3949 | 33.3284 | 0.21311 | -86.8652 | -87.2237 | 119.6433 | 119.652 | 119.6777 | 34.0225 | -122.012 | 33.4417 | 33.5816 | 33.2231 | 33.353 | -87.3315
2225.9688 | 121.3943 | -116.011 | 4.9576 | 1.4211e-13 | -0.028559 | 0.00071164 | 0.068409 | -0.012707 | 0.058898 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017609 | 0.035568 | 0.0068005 | -115.3835 | -1.3951 | -115.9213 | 5.1525 | 5.17 | 5.3799 | -116.1846 | 0.055992 | 0.018674 | -0.010564 | 0.10282 | 0.23806 | -0.12503 | -0.22825 | -0.17354 | 0.19487 | 0.62756 | 0.089731 | 0.26327 | 0.21238 | 0.42231 | 115.7828 | -4.8548 | 116.067 | 116.0005 | 0.21769 | -4.7195 | -5.0826 | 121.1635 | 121.181 | 121.3909 | 114.616 | -121.1422 | 116.1139 | 116.2491 | 115.886 | 116.0297 | -5.1858
2227.6562 | 121.3394 | -116.684 | 4.3762 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.068195 | -0.012707 | 0.058898 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017609 | 0.035782 | 0.0070143 | -116.0748 | -1.4271 | -116.6264 | 4.4794 | 4.4923 | 4.7068 | -116.8897 | 0.060571 | 0.004938 | -0.015143 | 0.10282 | 0.23806 | -0.12503 | -0.22367 | -0.20578 | 0.10321 | 0.60914 | 0.057589 | 0.26337 | 0.11606 | 0.33061 | 116.4603 | -4.2734 | 116.7445 | 116.6688 | 0.20853 | -4.1382 | -4.5012 | 121.1634 | 121.1762 | 121.3908 | 115.2568 | -121.266 | 116.7868 | 116.922 | 116.5589 | 116.6889 | -4.5999
2229.4219 | 121.2936 | -117.16 | 3.9688 | 1.4211e-13 | -0.028773 | 0.00049784 | 0.068409 | -0.01292 | 0.058898 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017609 | 0.035568 | 0.0072279 | -116.5052 | -1.4729 | -117.0567 | 4.017 | 4.0802 | 4.2948 | -117.3202 | 0.060571 | 0.014095 | -0.001407 | 0.10282 | 0.24264 | -0.12961 | -0.22825 | -0.16012 | 0.048201 | 0.65485 | 0.1033 | 0.26343 | 0.11137 | 0.32595 | 116.9318 | -3.866 | 117.2206 | 117.1586 | 0.22685 | -3.7262 | -4.0984 | 121.177 | 121.2402 | 121.4548 | 115.6871 | -121.289 | 117.2629 | 117.4027 | 117.0304 | 117.1741 | -4.1971
2231.1094 | 121.2524 | -118.1213 | 3.0304 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.068409 | -0.012707 | 0.059326 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017823 | 0.035568 | 0.0065869 | -117.2515 | -1.3447 | -117.8076 | 3.2936 | 3.3018 | 3.5256 | -118.0848 | 0.055992 | 0.004938 | -0.010564 | 0.098244 | 0.23348 | -0.14334 | -0.22825 | 0.036501 | 0.26323 | 0.86987 | 0.31377 | 0.27727 | 0.27137 | 0.49516 | 117.8931 | -2.9322 | 118.1773 | 118.1108 | 0.21769 | -2.7969 | -3.1737 | 121.415 | 121.4231 | 121.6469 | 116.7766 | -121.1152 | 118.2196 | 118.3548 | 117.978 | 118.1263 | -3.2586
2232.8594 | 121.3806 | -118.3228 | 2.8564 | 1.4211e-13 | -0.028559 | 0.00071164 | 0.068195 | -0.012493 | 0.059326 | 0.015566 | -0.0027303 | 0.0051278 | 0.017823 | 0.035568 | 0.0070143 | -117.7826 | -1.3768 | -118.3707 | 2.8587 | 2.8897 | 3.086 | -118.6343 | 0.055992 | 0.018674 | -0.010564 | 0.093665 | 0.23806 | -0.12961 | -0.22825 | -0.31155 | 0.002234 | 0.54019 | -0.047942 | 0.26361 | 0.033215 | 0.22956 | 118.0945 | -2.7628 | 118.3787 | 118.3122 | 0.21769 | -2.6184 | -2.9861 | 121.1814 | 121.2124 | 121.4088 | 116.946 | -121.4908 | 118.4164 | 118.5608 | 118.1931 | 118.3414 | -3.0847
2234.625 | 121.3943 | -119.632 | 1.6937 | 1.4211e-13 | -0.028346 | 7.0442e-05 | 0.067767 | -0.012707 | 0.059326 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017823 | 0.035782 | 0.0070143 | -118.7303 | -1.4821 | -119.3276 | 1.8697 | 1.951 | 2.1566 | -119.4997 | 0.051413 | 0.014095 | -0.010564 | 0.098244 | 0.23806 | -0.12503 | -0.23283 | 0.13223 | 0.17602 | 0.90167 | 0.3044 | 0.17217 | 0.25726 | 0.46282 | 119.3991 | -1.5955 | 119.6834 | 119.6214 | 0.22227 | -1.4557 | -1.8188 | 121.5017 | 121.5829 | 121.7885 | 118.1499 | -121.1935 | 119.7302 | 119.87 | 119.5069 | 119.6461 | -1.9266
2236.3125 | 121.4767 | -120.0485 | 1.2909 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.068195 | -0.012493 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017609 | 0.035995 | 0.0070143 | -119.3438 | -1.6148 | -119.9548 | 1.27 | 1.3466 | 1.5568 | -120.1408 | 0.06515 | 0.018674 | -0.010564 | 0.098244 | 0.23348 | -0.12503 | -0.22825 | -0.092251 | -0.020915 | 0.70473 | 0.093742 | 0.18599 | 0.055669 | 0.26586 | 119.8203 | -1.1926 | 120.1137 | 120.038 | 0.21769 | -1.0574 | -1.4159 | 121.3185 | 121.3951 | 121.6053 | 118.4337 | -121.4317 | 120.1468 | 120.282 | 119.9235 | 120.0672 | -1.5191
2238.0625 | 121.3531 | -120.076 | 1.3229 | 1.4211e-13 | -0.028773 | 0.00092524 | 0.068409 | -0.012707 | 0.058898 | -0.0073253 | -0.0029439 | 0.0047004 | 0.017395 | 0.035782 | 0.0070143 | -119.3255 | -1.7293 | -119.9319 | 1.302 | 1.3191 | 1.598 | -120.127 | 0.055992 | 0.014095 | -0.005985 | 0.093665 | 0.24264 | -0.0884 | -0.22825 | -0.051049 | -0.020909 | 0.75051 | 0.1441 | 0.19515 | -0.003848 | 0.27503 | 119.8477 | -1.2293 | 120.132 | 120.07 | 0.22227 | -1.0803 | -1.4113 | 121.378 | 121.3951 | 121.674 | 118.3467 | -121.45 | 120.1697 | 120.3186 | 119.9876 | 120.0901 | -1.5512
2239.75 | 121.3806 | -120.6802 | 0.75073 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.068195 | -0.012707 | 0.059326 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017395 | 0.035995 | 0.0070143 | -119.8703 | -1.9124 | -120.4767 | 0.78467 | 0.7742 | 1.0668 | -120.6765 | 0.060571 | 0.009516 | -0.005985 | 0.098244 | 0.24264 | -0.13419 | -0.23283 | 0.003728 | 0.033938 | 0.80993 | 0.20353 | 0.1998 | 0.023465 | 0.31611 | 120.4474 | -0.65249 | 120.7408 | 120.6743 | 0.22685 | -0.50809 | -0.88492 | 121.4649 | 121.4544 | 121.7471 | 118.7678 | -121.4272 | 120.7785 | 120.9229 | 120.5461 | 120.6898 | -0.98356
2241.5156 | 121.4264 | -120.8817 | 0.53101 | 1.4211e-13 | -0.028346 | 0.00028424 | 0.068195 | -0.012707 | 0.059326 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017823 | 0.035568 | 0.0070143 | -120.145 | -2.059 | -120.7697 | 0.50539 | 0.47199 | 0.78755 | -120.9696 | 0.055992 | 0.018674 | -0.005985 | 0.098244 | 0.23806 | -0.13419 | -0.22825 | -0.087907 | -0.025618 | 0.73665 | 0.11194 | 0.19984 | -0.059018 | 0.25654 | 120.6534 | -0.43276 | 120.9376 | 120.8757 | 0.22227 | -0.29295 | -0.66519 | 121.387 | 121.3536 | 121.6692 | 118.8227 | -121.5006 | 120.9799 | 121.1197 | 120.7475 | 120.9003 | -0.75926
2243.2031 | 121.431 | -120.9 | 0.54016 | 1.4211e-13 | -0.028559 | 0.00028424 | 0.067767 | -0.012707 | 0.059326 | 0.0079357 | -0.0029439 | 0.0051278 | 0.017823 | 0.035782 | 0.0065869 | -120.0718 | -2.2375 | -120.7148 | 0.57406 | 0.55899 | 0.81502 | -120.9009 | 0.055992 | 0.009516 | -0.005985 | 0.10282 | 0.24264 | -0.12503 | -0.23283 | -0.000913 | 0.033903 | 0.82821 | 0.18519 | 0.1861 | 0.018827 | 0.27486 | 120.6671 | -0.43734 | 120.956 | 120.894 | 0.22685 | -0.29752 | -0.66519 | 121.474 | 121.459 | 121.715 | 118.6624 | -121.441 | 121.0028 | 121.1426 | 120.7749 | 120.9095 | -0.77299
2244.8906 | 121.0327 | -113.8412 | 6.8939 | 1.4211e-13 | -0.028559 | 0.00071164 | 0.067767 | -0.012493 | 0.058898 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017609 | 0.035782 | 0.0068005 | -113.4285 | -2.1643 | -114.0351 | 6.7228 | 6.7543 | 6.9458 | -114.3164 | 0.060571 | 0.014095 | -0.001407 | 0.093665 | 0.24264 | -0.13419 | -0.22367 | -0.47513 | -0.17108 | 0.41274 | -0.19382 | 0.28132 | -0.13965 | 0.051848 | 113.6176 | -6.8003 | 113.9018 | 113.8398 | 0.22227 | -6.6513 | -7.0281 | 120.5641 | 120.5955 | 120.787 | 111.677 | -121.2103 | 113.9349 | 114.0839 | 113.7071 | 113.8553 | -7.1176
2246.6406 | 121.1975 | -116.8625 | 4.216 | 1.4211e-13 | -0.028559 | 0.00092524 | 0.067981 | -0.012493 | 0.058898 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017609 | 0.035782 | 0.0070143 | -116.1527 | -2.5077 | -116.7775 | 4.2139 | 4.2817 | 4.4962 | -117.0683 | 0.060571 | 0.014095 | -0.015143 | 0.098244 | 0.24721 | -0.12961 | -0.23283 | -0.20583 | -0.002121 | 0.70984 | 0.085033 | 0.29086 | 0.06565 | 0.28021 | 116.6297 | -4.1178 | 116.9231 | 116.8473 | 0.21769 | -3.9688 | -4.3456 | 121.0764 | 121.1441 | 121.3587 | 114.3548 | -121.2843 | 116.9607 | 117.1097 | 116.7329 | 116.8766 | -4.4488
2248.3906 | 121.2662 | -117.0273 | 4.1153 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.067981 | -0.012707 | 0.059112 | -0.0073253 | -0.0029439 | 0.0044868 | 0.017395 | 0.036209 | 0.0072279 | -116.2992 | -2.7641 | -116.9285 | 4.1315 | 4.1992 | 4.4138 | -117.1324 | 0.06515 | 0.014095 | -0.010564 | 0.098244 | 0.24721 | -0.079243 | -0.22367 | -0.10514 | 0.016176 | 0.72812 | 0.098745 | 0.20388 | 0.083938 | 0.29851 | 116.8036 | -4.0171 | 117.0924 | 117.0167 | 0.21311 | -3.8681 | -4.1945 | 121.1588 | 121.2265 | 121.4411 | 114.2632 | -121.2477 | 117.1255 | 117.2745 | 116.948 | 117.0414 | -4.339
2250.0781 | 121.376 | -117.4667 | 3.7399 | 1.4211e-13 | -0.028346 | 0.00049784 | 0.067981 | -0.012707 | 0.059539 | -0.0073253 | -0.0029439 | 0.0047004 | 0.017823 | 0.035995 | 0.0070143 | -116.496 | -3.025 | -117.1346 | 3.9575 | 3.9657 | 4.2307 | -117.3385 | 0.051413 | 0.014095 | -0.001407 | 0.10282 | 0.24721 | -0.12503 | -0.23283 | 0.12826 | 0.21756 | 0.9707 | 0.33218 | 0.20391 | 0.22578 | 0.49073 | 117.2339 | -3.6371 | 117.5181 | 117.4653 | 0.23142 | -3.4927 | -3.865 | 121.4242 | 121.4324 | 121.6974 | 114.4417 | -121.0784 | 117.5696 | 117.714 | 117.3417 | 117.4808 | -3.9728
2251.7812 | 121.3486 | -117.8055 | 3.4378 | 1.4211e-13 | -0.028773 | 0.00049784 | 0.067981 | -0.012707 | 0.059539 | 0.015566 | -0.0031575 | 0.0047004 | 0.017609 | 0.035782 | 0.0072279 | -117.018 | -3.3547 | -117.6519 | 3.4722 | 3.4895 | 3.7407 | -117.8513 | 0.060571 | 0.018674 | -0.010564 | 0.098244 | 0.24264 | -0.13419 | -0.22825 | -0.045831 | 0.034378 | 0.78751 | 0.15358 | 0.19941 | 0.051694 | 0.30294 | 117.5772 | -3.3396 | 117.8661 | 117.7949 | 0.21769 | -3.1952 | -3.572 | 121.2777 | 121.295 | 121.5462 | 114.4508 | -121.2891 | 117.9037 | 118.0481 | 117.6713 | 117.8242 | -3.6661
2253.5156 | 121.3486 | -118.0893 | 3.2043 | 1.4211e-13 | -0.028132 | 0.00049784 | 0.068195 | -0.012707 | 0.059112 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017395 | 0.035995 | 0.0068005 | -117.2789 | -3.6889 | -117.9266 | 3.2295 | 3.2331 | 3.4569 | -118.1444 | 0.060571 | 0.014095 | -0.010564 | 0.10282 | 0.23806 | -0.12961 | -0.23283 | -0.055069 | 0.025183 | 0.81036 | 0.16269 | 0.21776 | 0.028734 | 0.25253 | 117.8565 | -3.1015 | 118.1499 | 118.0787 | 0.22227 | -2.9663 | -3.334 | 121.3188 | 121.3224 | 121.5462 | 114.4003 | -121.3487 | 118.1921 | 118.3274 | 117.9597 | 118.1034 | -3.4372
2255.2656 | 121.4584 | -118.1854 | 3.0624 | 1.4211e-13 | -0.028346 | 0.00028424 | 0.067981 | -0.012707 | 0.058898 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017395 | 0.035995 | 0.0070143 | -117.4071 | -4.0781 | -118.0823 | 3.0922 | 3.1049 | 3.3195 | -118.2772 | 0.055992 | 0.014095 | -0.010564 | 0.093665 | 0.23806 | -0.12503 | -0.22825 | -0.091727 | 0.029738 | 0.77829 | 0.10316 | 0.19489 | 0.042431 | 0.25708 | 117.9572 | -2.9688 | 118.2414 | 118.1749 | 0.21769 | -2.8244 | -3.1875 | 121.2776 | 121.2903 | 121.5049 | 114.1073 | -121.3396 | 118.2791 | 118.4235 | 118.0604 | 118.1995 | -3.2907
2256.9688 | 121.3348 | -118.483 | 2.8564 | 1.4211e-13 | -0.028132 | 0.00071164 | 0.067767 | -0.01292 | 0.059326 | -0.0073253 | -0.0031575 | 0.0049142 | 0.018036 | 0.035995 | 0.0070143 | -117.5811 | -4.4582 | -118.2425 | 2.9411 | 2.9492 | 3.1776 | -118.4695 | 0.055992 | 0.004938 | -0.005985 | 0.1074 | 0.23348 | -0.12961 | -0.22825 | 0.013504 | 0.084645 | 0.90186 | 0.24047 | 0.22696 | 0.092741 | 0.32113 | 118.2547 | -2.749 | 118.539 | 118.477 | 0.22227 | -2.623 | -2.9861 | 121.4241 | 121.4322 | 121.6606 | 114.0248 | -121.3259 | 118.5904 | 118.7165 | 118.3534 | 118.4879 | -3.0847
2258.6562 | 121.3623 | -118.7439 | 2.623 | 1.4211e-13 | -0.028559 | 0.00028424 | 0.068195 | -0.012493 | 0.059326 | 0.015566 | -0.0031575 | 0.0047004 | 0.017823 | 0.035995 | 0.0072279 | -118.0847 | -4.9069 | -118.7507 | 2.4512 | 2.4363 | 2.6739 | -118.9915 | 0.060571 | 0.009516 | -0.005985 | 0.098244 | 0.24264 | -0.12503 | -0.23283 | -0.24757 | -0.17178 | 0.65916 | -0.006797 | 0.24077 | -0.18664 | 0.050947 | 118.5111 | -2.5247 | 118.8045 | 118.7379 | 0.22685 | -2.3803 | -2.748 | 121.1951 | 121.1802 | 121.4178 | 113.837 | -121.6144 | 118.8421 | 118.9865 | 118.6189 | 118.7534 | -2.8558
2260.4062 | 121.0876 | -118.1946 | 2.5223 | 1.4211e-13 | -0.028773 | 0.00071164 | 0.067981 | -0.01292 | 0.059112 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017609 | 0.035354 | 0.0072279 | -117.4071 | -5.383 | -118.0823 | 2.6801 | 2.6928 | 2.912 | -118.3916 | 0.055992 | 0.004938 | 0.003172 | 0.093665 | 0.24264 | -0.13419 | -0.22825 | -0.19705 | 0.15784 | 0.78745 | 0.11232 | 0.30936 | 0.17049 | 0.38974 | 117.9663 | -2.4286 | 118.2506 | 118.1978 | 0.23142 | -2.2796 | -2.6565 | 120.8747 | 120.8873 | 121.1066 | 112.8115 | -120.9139 | 118.2882 | 118.4372 | 118.0604 | 118.1995 | -2.7505
2262.1562 | 121.2479 | -120.4971 | 0.45319 | 1.4211e-13 | -0.028346 | 0.00028424 | 0.067767 | -0.012707 | 0.059112 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017395 | 0.035782 | 0.0070143 | -119.7467 | -6.1843 | -120.4492 | 0.47334 | 0.54983 | 0.76924 | -120.7635 | 0.055992 | 0.004938 | -0.001407 | 0.10282 | 0.24264 | -0.12961 | -0.22825 | -0.26638 | 0.020153 | 0.75044 | 0.047895 | 0.31427 | 0.096644 | 0.31605 | 120.2689 | -0.35036 | 120.5531 | 120.4957 | 0.22685 | -0.21055 | -0.58279 | 120.9705 | 121.047 | 121.2664 | 114.3128 | -121.2167 | 120.6 | 120.7398 | 120.3675 | 120.5021 | -0.68144
2263.9062 | 121.2204 | -119.7327 | 1.3733 | 1.4211e-13 | -0.028559 | 0.00028424 | 0.067554 | -0.01292 | 0.059753 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017823 | 0.035995 | 0.0068005 | -119.678 | -6.839 | -120.3851 | 0.5878 | 0.6643 | 0.87912 | -120.6811 | 0.060571 | 0.018674 | -0.001407 | 0.098244 | 0.23348 | -0.12503 | -0.23283 | -0.94842 | -0.78549 | 0.054655 | -0.65247 | 0.29595 | -0.70899 | -0.49417 | 119.4998 | -1.275 | 119.7932 | 119.7313 | 0.23142 | -1.1398 | -1.4983 | 120.3205 | 120.397 | 120.6118 | 112.8936 | -122.0544 | 119.8309 | 119.9661 | 119.6076 | 119.7513 | -1.6061
2265.6094 | 121.1975 | -120.6162 | 0.60883 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.067767 | -0.013134 | 0.059112 | 0.015566 | -0.0025167 | 0.0051278 | 0.017609 | 0.035782 | 0.0072279 | -119.7284 | -7.5762 | -120.4355 | 0.58322 | 0.58646 | 0.87454 | -120.6857 | 0.06515 | 0.014095 | -0.001407 | 0.098244 | 0.25179 | -0.12503 | -0.22825 | -0.069516 | -0.025605 | 0.88778 | 0.18065 | 0.25016 | -0.022365 | 0.26572 | 120.3879 | -0.51058 | 120.6813 | 120.6147 | 0.22685 | -0.35703 | -0.73385 | 121.1994 | 121.2026 | 121.4907 | 113.04 | -121.2945 | 120.7144 | 120.8679 | 120.4911 | 120.6302 | -0.83708
2267.3594 | 121.3074 | -120.6985 | 0.48065 | 1.4211e-13 | -0.028559 | 0.00071164 | 0.067767 | -0.012493 | 0.059539 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017823 | 0.035995 | 0.0070143 | -119.8428 | -8.176 | -120.5454 | 0.49165 | 0.47657 | 0.77839 | -120.8093 | 0.055992 | 0.009516 | 0.003172 | 0.10282 | 0.24264 | -0.10671 | -0.22367 | -0.11075 | 0.011001 | 0.85571 | 0.15317 | 0.26392 | -0.004085 | 0.29774 | 120.4749 | -0.37783 | 120.7545 | 120.7017 | 0.22685 | -0.23802 | -0.58737 | 121.1902 | 121.1751 | 121.4769 | 112.5226 | -121.2899 | 120.8014 | 120.9412 | 120.5918 | 120.7081 | -0.70433
2269.1094 | 121.3486 | -120.7993 | 0.4303 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.068195 | -0.01292 | 0.059753 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017823 | 0.035782 | 0.0068005 | -119.9252 | -8.7483 | -120.6415 | 0.43213 | 0.40788 | 0.71887 | -120.9055 | 0.055992 | 0.018674 | -0.005985 | 0.098244 | 0.23806 | -0.12961 | -0.23283 | -0.1062 | 0.001836 | 0.87401 | 0.15773 | 0.26393 | -0.022415 | 0.28857 | 120.5664 | -0.33205 | 120.8552 | 120.7933 | 0.22685 | -0.19224 | -0.5599 | 121.2314 | 121.2071 | 121.5181 | 112.051 | -121.3358 | 120.8975 | 121.0373 | 120.6696 | 120.8179 | -0.66313
2270.8594 | 121.2708 | -120.9091 | 0.42572 | 1.4211e-13 | -0.028987 | 0.00049784 | 0.068195 | -0.01292 | 0.059112 | 0.015566 | -0.0031575 | 0.0044868 | 0.017609 | 0.035782 | 0.0070143 | -119.9664 | -9.3069 | -120.6827 | 0.40009 | 0.41704 | 0.6914 | -120.9467 | 0.060571 | 0.018674 | -0.001407 | 0.1074 | 0.23348 | -0.05635 | -0.22825 | -0.037546 | -0.025635 | 0.94267 | 0.22639 | 0.26394 | -0.008679 | 0.26568 | 120.6809 | -0.31832 | 120.9697 | 120.9077 | 0.22685 | -0.19224 | -0.48207 | 121.3092 | 121.3262 | 121.6005 | 111.6022 | -121.3724 | 121.0165 | 121.1426 | 120.8528 | 120.9278 | -0.65397
2272.5469 | 121.2799 | -120.8954 | 0.42572 | 1.4211e-13 | -0.028559 | 0.00049784 | 0.067767 | -0.01292 | 0.059326 | -0.014956 | -0.0029439 | 0.0049142 | 0.017823 | 0.035995 | 0.0068005 | -119.9802 | -9.8884 | -120.7056 | 0.40009 | 0.41704 | 0.64103 | -120.9787 | 0.060571 | 0.014095 | -0.005985 | 0.098244 | 0.23806 | -0.038035 | -0.22825 | -0.083332 | -0.025635 | 0.9152 | 0.18977 | 0.2731 | -0.008679 | 0.21531 | 120.6671 | -0.32748 | 120.956 | 120.8894 | 0.22227 | -0.18766 | -0.46375 | 121.2955 | 121.3124 | 121.5364 | 111.007 | -121.4044 | 120.9936 | 121.1334 | 120.8574 | 120.9095 | -0.65397
2274.2969 | 121.2936 | -120.8817 | 0.45776 | 1.4211e-13 | -0.0292 | 0.00028424 | 0.067981 | -0.01292 | 0.059326 | 0.015566 | -0.0029439 | 0.0049142 | 0.017609 | 0.035782 | 0.0070143 | -119.971 | -10.5752 | -120.6965 | 0.4184 | 0.4262 | 0.65019 | -120.9787 | 0.060571 | 0.014095 | -0.001407 | 0.098244 | 0.23806 | 0.026065 | -0.22825 | -0.097065 | -0.039365 | 0.91062 | 0.18519 | 0.28226 | -0.031565 | 0.19243 | 120.6534 | -0.35952 | 120.9422 | 120.8802 | 0.22685 | -0.21971 | -0.4317 | 121.3001 | 121.3079 | 121.5318 | 110.3065 | -121.4365 | 120.9799 | 121.1197 | 120.9077 | 120.8957 | -0.68602
2275.9844 | 121.3028 | -120.9 | 0.42114 | 1.4211e-13 | -0.028773 | 0.00049784 | 0.067981 | -0.01292 | 0.059753 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017823 | 0.035995 | 0.0065869 | -119.9848 | -11.1109 | -120.7148 | 0.40466 | 0.41246 | 0.64561 | -121.0062 | 0.06515 | 0.014095 | 0.003172 | 0.1074 | 0.24264 | -0.010564 | -0.23283 | -0.10623 | -0.016479 | 0.9152 | 0.18519 | 0.29142 | -0.008681 | 0.22447 | 120.6671 | -0.31374 | 120.9651 | 120.9031 | 0.236 | -0.17851 | -0.43171 | 121.3046 | 121.3124 | 121.5456 | 109.7891 | -121.4273 | 121.0074 | 121.1426 | 120.8894 | 120.9141 | -0.65397
2277.6719 | 121.3577 | -120.8817 | 0.46234 | 1.4211e-13 | -0.028987 | 0.00049784 | 0.067981 | -0.012493 | 0.059326 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017823 | 0.035995 | 0.0070143 | -119.9619 | -11.903 | -120.6965 | 0.44129 | 0.43994 | 0.67308 | -120.9879 | 0.055992 | 0.014095 | -0.005985 | 0.10282 | 0.23348 | -0.028878 | -0.22367 | -0.10622 | -0.02105 | 0.91978 | 0.18519 | 0.29141 | -0.022405 | 0.21074 | 120.658 | -0.35952 | 120.9376 | 120.8757 | 0.21769 | -0.22886 | -0.49122 | 121.3229 | 121.3216 | 121.5547 | 108.9787 | -121.4502 | 120.9845 | 121.1151 | 120.8528 | 120.8957 | -0.68601
2279.4062 | 121.3715 | -120.8908 | 0.45776 | 1.4211e-13 | -0.028987 | 7.0442e-05 | 0.067767 | -0.01292 | 0.059326 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017609 | 0.035995 | 0.0068005 | -119.9436 | -12.3654 | -120.6782 | 0.45503 | 0.45825 | 0.68682 | -121.0062 | 0.060571 | 0.009516 | -0.010564 | 0.098244 | 0.24264 | -0.070086 | -0.22825 | -0.11538 | -0.002738 | 0.94725 | 0.21266 | 0.32804 | 0.000487 | 0.22906 | 120.6626 | -0.35952 | 120.9514 | 120.8802 | 0.21769 | -0.21513 | -0.52785 | 121.3458 | 121.3491 | 121.5776 | 108.5254 | -121.464 | 120.9891 | 121.1334 | 120.8207 | 120.9003 | -0.68602
2281.1562 | 121.2021 | -119.2474 | 1.593 | 1.4211e-13 | -0.028987 | 0.00028424 | 0.067554 | -0.012493 | 0.059326 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017395 | 0.035995 | 0.0068005 | -118.5151 | -12.7271 | -119.2406 | 1.595 | 1.6167 | 1.8269 | -119.6234 | 0.060571 | 0.018674 | -0.010564 | 0.10282 | 0.24264 | 0.016908 | -0.23283 | -0.37592 | 0.002026 | 0.73234 | 0.006868 | 0.38279 | 0.023701 | 0.23387 | 119.0146 | -1.4902 | 119.308 | 119.2369 | 0.22227 | -1.3504 | -1.5761 | 120.8425 | 120.8642 | 121.0743 | 106.5203 | -121.2164 | 119.3503 | 119.4901 | 119.2643 | 119.2661 | -1.8258
2282.8438 | 121.3394 | -120.6162 | 0.45776 | 1.4211e-13 | -0.028773 | 0.00049784 | 0.067981 | -0.012707 | 0.059967 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017609 | 0.036209 | 0.0070143 | -119.7513 | -13.4276 | -120.4904 | 0.45503 | 0.52694 | 0.74634 | -120.8826 | 0.055992 | 0.009516 | -0.010564 | 0.098244 | 0.23348 | 0.007751 | -0.22825 | -0.26641 | -0.002738 | 0.86489 | 0.12571 | 0.39212 | 0.069171 | 0.28858 | 120.3879 | -0.35952 | 120.6721 | 120.6056 | 0.21769 | -0.22429 | -0.45001 | 121.0712 | 121.1431 | 121.3625 | 107.1885 | -121.3403 | 120.7144 | 120.8496 | 120.6239 | 120.6257 | -0.68602
2284.5938 | 121.3486 | -120.6665 | 0.48523 | 1.4211e-13 | -0.028773 | 0.00071164 | 0.067767 | -0.012707 | 0.059539 | 0.0079357 | -0.0031575 | 0.0049142 | 0.018036 | 0.036209 | 0.0072279 | -119.7696 | -13.9633 | -120.4996 | 0.48707 | 0.55899 | 0.77839 | -120.823 | 0.055992 | 0.004938 | -0.001407 | 0.098244 | 0.24264 | 0.003172 | -0.22825 | -0.15653 | 0.001846 | 0.89693 | 0.16691 | 0.32344 | 0.073759 | 0.29316 | 120.4383 | -0.38699 | 120.7225 | 120.6651 | 0.22685 | -0.24259 | -0.48206 | 121.1536 | 121.2255 | 121.4449 | 106.7032 | -121.3083 | 120.7647 | 120.9091 | 120.6697 | 120.6714 | -0.71348
2286.2812 | 121.0648 | -2.092 | 118.5379 | 1.4211e-13 | -0.027705 | 0.0011388 | 0.068836 | -0.013348 | 0.05783 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017823 | 0.035995 | 0.0068005 | -2.0272 | 11.0221 | -2.1922 | 118.7651 | 118.709 | 118.7552 | -2.4533 | 0.02852 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.26488 | -0.36128 | 0.22724 | 0.064802 | -0.10027 | 0.26101 | 0.17108 | 0.21734 | 1.8271 | -118.4763 | 2.1205 | 2.0448 | 0.21769 | -118.3319 | -118.6904 | 120.8571 | 120.801 | 120.8472 | 13.1141 | -120.9912 | 2.1536 | 2.298 | 1.9395 | 2.074 | -118.8028
2288.0312 | 121.2158 | -0.1831 | 120.4605 | 1.4211e-13 | -0.028132 | 0.0015662 | 0.068836 | -0.013561 | 0.058044 | 0.015566 | -0.0027303 | 0.0047004 | 0.017395 | 0.036209 | 0.0068005 | 0.083459 | 10.2208 | -0.049614 | 120.949 | 120.8885 | 120.9392 | -0.32864 | 0.033099 | -0.017956 | -0.033458 | 0.070773 | 0.21059 | -0.15708 | -0.26488 | -0.14553 | 0.48853 | 0.26656 | 0.13349 | 0.27902 | 0.42804 | 0.47873 | -0.081778 | -120.3897 | 0.2162 | 0.14965 | 0.23142 | -120.2499 | -120.6176 | 121.1321 | 121.0717 | 121.1223 | 10.404 | -120.7891 | 0.25388 | 0.39369 | 0.026026 | 0.16515 | -120.7254
2289.7031 | 121.2662 | -0.14191 | 120.8679 | 1.4211e-13 | -0.027705 | 0.00178 | 0.068622 | -0.01292 | 0.058044 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017823 | 0.035995 | 0.0070143 | 0.092615 | 10.578 | -0.045036 | 121.0269 | 120.9801 | 121.0171 | -0.31032 | 0.02852 | -0.008798 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.2603 | -0.16841 | 0.15895 | 0.23452 | 0.096871 | 0.26528 | 0.1122 | 0.14915 | -0.1184 | -120.8017 | 0.17043 | 0.10387 | 0.22227 | -120.6573 | -121.0204 | 121.1688 | 121.122 | 121.159 | 10.7199 | -121.1782 | 0.2081 | 0.35249 | -0.010593 | 0.13311 | -121.1282
2291.4688 | 116.7435 | -51.6174 | 64.4852 | 1.4211e-13 | -0.028559 | 0.00028424 | 0.066272 | -0.012279 | 0.056121 | 0.015566 | -0.0033713 | 0.0049142 | 0.017609 | 0.035995 | 0.0068005 | -38.7916 | 1.5307 | -38.7773 | 79.4368 | 79.1059 | 79.7913 | -39.3869 | 0.042256 | 0.000359 | -0.019721 | 0.075351 | 0.21974 | -0.14334 | -0.2603 | 12.2306 | 14.9516 | 12.8258 | 12.8401 | 0.60957 | 14.6207 | 15.3062 | 51.3571 | -64.4098 | 51.6597 | 51.5977 | 0.24058 | -64.2654 | -64.6285 | 131.0542 | 130.7233 | 131.4088 | 53.1481 | -103.872 | 51.6928 | 51.8372 | 51.4741 | 51.6178 | -64.7455
2293.1562 | 120.7443 | -0.89264 | 119.8746 | 1.4211e-13 | -0.028132 | 0.0013526 | 0.068622 | -0.013134 | 0.05783 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017395 | 0.036209 | 0.0070143 | -0.58956 | 11.0679 | -0.73178 | 119.9372 | 119.8858 | 119.9319 | -0.94221 | 0.023941 | -0.008798 | -0.038036 | 0.066194 | 0.20601 | -0.1525 | -0.2603 | -0.049572 | 0.062641 | 0.30307 | 0.16086 | 0.21043 | 0.011188 | 0.057371 | 0.63233 | -119.8084 | 0.91658 | 0.8546 | 0.22227 | -119.6686 | -120.0271 | 120.8299 | 120.7784 | 120.8246 | 11.9605 | -120.8168 | 0.95883 | 1.0986 | 0.74014 | 0.88384 | -120.1349
2294.9062 | 120.9778 | -0.78735 | 120.0302 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068836 | -0.01292 | 0.05783 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017823 | 0.036209 | 0.0072279 | -0.49342 | 11.5486 | -0.63563 | 120.1753 | 120.1193 | 120.17 | -0.85521 | 0.033099 | -0.008798 | -0.033458 | 0.070773 | 0.21059 | -0.1525 | -0.25572 | -0.067857 | 0.14508 | 0.29394 | 0.15172 | 0.21958 | 0.089074 | 0.13982 | 0.53163 | -119.9594 | 0.82045 | 0.7539 | 0.22227 | -119.8196 | -120.1827 | 120.9626 | 120.9066 | 120.9574 | 12.336 | -120.8854 | 0.85813 | 0.99794 | 0.63485 | 0.77856 | -120.2859
2296.6562 | 121.019 | -0.70496 | 120.2271 | 1.4211e-13 | -0.027705 | 0.0013526 | 0.06905 | -0.013134 | 0.058044 | 0.015566 | -0.0029439 | 0.0049142 | 0.017823 | 0.036209 | 0.0070143 | -0.37896 | 11.9149 | -0.53033 | 120.3218 | 120.2704 | 120.3257 | -0.76821 | 0.037677 | -0.013377 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.26488 | -0.063256 | 0.094747 | 0.326 | 0.17462 | 0.23788 | 0.04334 | 0.098652 | 0.44007 | -120.1563 | 0.74263 | 0.66692 | 0.22685 | -120.0165 | -120.3796 | 121.0268 | 120.9753 | 121.0307 | 12.6199 | -120.9953 | 0.77573 | 0.91554 | 0.55246 | 0.69158 | -120.4919
2298.4062 | 120.5566 | -0.71411 | 120.3461 | 1.4211e-13 | -0.027918 | 0.0015662 | 0.068836 | -0.013134 | 0.058257 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017609 | 0.035782 | 0.0070143 | -0.33317 | 12.3224 | -0.47997 | 120.4134 | 120.3665 | 120.4127 | -0.727 | 0.023941 | -0.013377 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.2603 | -0.01289 | 0.067297 | 0.38094 | 0.23414 | 0.24703 | 0.020479 | 0.066628 | 0.45381 | -120.2753 | 0.73805 | 0.67608 | 0.22227 | -120.1355 | -120.4986 | 121.1275 | 121.0807 | 121.1268 | 13.0365 | -121.0731 | 0.78488 | 0.9247 | 0.56161 | 0.70073 | -120.6064
2300.1562 | 120.726 | -0.737 | 120.314 | 1.4211e-13 | -0.027705 | 0.00178 | 0.068622 | -0.01292 | 0.058044 | 0.015566 | -0.0033713 | 0.0049142 | 0.017395 | 0.035995 | 0.0068005 | -0.37438 | 12.5742 | -0.5166 | 120.4134 | 120.3711 | 120.4081 | -0.76363 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.14792 | -0.2603 | -0.026633 | 0.09934 | 0.36262 | 0.2204 | 0.24703 | 0.057101 | 0.094092 | 0.4767 | -120.2433 | 0.76552 | 0.69439 | 0.21769 | -120.1034 | -120.4619 | 121.1504 | 121.1081 | 121.1451 | 13.3112 | -121.0777 | 0.80777 | 0.94759 | 0.58908 | 0.72362 | -120.5743
2301.9219 | 121.106 | -0.71411 | 120.3323 | 1.4211e-13 | -0.027918 | 0.0015662 | 0.06905 | -0.013348 | 0.058257 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017609 | 0.035995 | 0.0072279 | -0.37438 | 12.881 | -0.51202 | 120.4363 | 120.394 | 120.4447 | -0.76821 | 0.037677 | -0.013377 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.2603 | -0.054101 | 0.10392 | 0.33973 | 0.20209 | 0.25619 | 0.061686 | 0.11241 | 0.45381 | -120.2661 | 0.75179 | 0.67608 | 0.22227 | -120.1217 | -120.4848 | 121.1504 | 121.1081 | 121.1589 | 13.5951 | -121.1005 | 0.78031 | 0.9247 | 0.56161 | 0.70073 | -120.5926
2303.6094 | 120.7718 | -0.67291 | 120.3461 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068409 | -0.01292 | 0.058471 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017395 | 0.035995 | 0.0070143 | -0.36064 | 13.2107 | -0.50744 | 120.4683 | 120.4169 | 120.4722 | -0.77279 | 0.02852 | -0.017956 | -0.042615 | 0.075351 | 0.21059 | -0.1525 | -0.2603 | -0.099878 | 0.12224 | 0.31227 | 0.16547 | 0.26535 | 0.070848 | 0.12615 | 0.41261 | -120.2707 | 0.70143 | 0.6303 | 0.21769 | -120.1355 | -120.4986 | 121.1412 | 121.0898 | 121.1451 | 13.8836 | -121.1189 | 0.74826 | 0.8835 | 0.52041 | 0.65496 | -120.6064
2305.3594 | 121.0098 | -0.69122 | 120.3003 | 1.4211e-13 | -0.027918 | 0.00178 | 0.06905 | -0.013134 | 0.058044 | 0.015566 | -0.0031575 | 0.0051278 | 0.017395 | 0.035995 | 0.0070143 | -0.34233 | 13.4213 | -0.49371 | 120.4958 | 120.449 | 120.4997 | -0.76821 | 0.023941 | -0.013377 | -0.038036 | 0.075351 | 0.21059 | -0.15708 | -0.2603 | -0.076989 | 0.19548 | 0.34889 | 0.19752 | 0.2745 | 0.14868 | 0.1994 | 0.43092 | -120.2249 | 0.71516 | 0.65319 | 0.22227 | -120.0897 | -120.4574 | 121.187 | 121.1402 | 121.1909 | 14.1125 | -121.0685 | 0.76657 | 0.90181 | 0.53414 | 0.67785 | -120.5606
2307.1094 | 120.3232 | -0.70496 | 120.0623 | 1.4211e-13 | -0.027705 | 0.0015662 | 0.068622 | -0.013134 | 0.058257 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017395 | 0.036209 | 0.0070143 | -0.33775 | 13.7235 | -0.49828 | 120.5141 | 120.481 | 120.5317 | -0.75448 | 0.042256 | -0.008798 | -0.033458 | 0.066194 | 0.20143 | -0.14792 | -0.2603 | -0.049519 | 0.45183 | 0.3672 | 0.20667 | 0.25619 | 0.41877 | 0.46948 | 0.44465 | -119.9961 | 0.74721 | 0.6715 | 0.22685 | -119.8608 | -120.2102 | 121.219 | 121.186 | 121.2367 | 14.4284 | -120.8167 | 0.77115 | 0.90638 | 0.55703 | 0.69616 | -120.3226
2308.7969 | 117.2974 | -0.72784 | 120.0897 | 1.4211e-13 | -0.027918 | 0.0015662 | 0.068409 | -0.013134 | 0.058044 | 0.015566 | -0.0029439 | 0.0053414 | 0.017395 | 0.035782 | 0.0070143 | -0.34691 | 13.9753 | -0.50286 | 120.5324 | 120.481 | 120.5363 | -0.76821 | 0.02852 | -0.017956 | -0.042615 | 0.070773 | 0.20601 | -0.13876 | -0.2603 | -0.040368 | 0.44268 | 0.38093 | 0.22498 | 0.26535 | 0.3913 | 0.4466 | 0.46754 | -120.0189 | 0.75636 | 0.68523 | 0.21769 | -119.8837 | -120.2285 | 121.2602 | 121.2089 | 121.2642 | 14.7031 | -120.8579 | 0.79862 | 0.93385 | 0.58908 | 0.70989 | -120.35
2310.5469 | 121.1929 | -0.70953 | 120.4514 | 1.4211e-13 | -0.027705 | 0.0015662 | 0.068622 | -0.013134 | 0.058044 | 0.0079357 | -0.0029439 | 0.0051278 | 0.017395 | 0.036209 | 0.0072279 | -0.33317 | 14.2134 | -0.49828 | 120.5507 | 120.5131 | 120.5546 | -0.75905 | 0.02852 | -0.017956 | -0.033458 | 0.070773 | 0.20601 | -0.14792 | -0.2603 | -0.04952 | 0.099363 | 0.37636 | 0.21125 | 0.26077 | 0.061719 | 0.10328 | 0.44923 | -120.3806 | 0.73805 | 0.67608 | 0.22685 | -120.2453 | -120.5993 | 121.2603 | 121.2226 | 121.2642 | 14.9229 | -121.2104 | 0.78031 | 0.91554 | 0.56161 | 0.69158 | -120.7117
2312.25 | 121.2204 | -0.71411 | 120.4376 | 1.4211e-13 | -0.027918 | 0.0015662 | 0.06905 | -0.01292 | 0.058257 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017823 | 0.035995 | 0.0070143 | -0.33317 | 14.4881 | -0.49371 | 120.5645 | 120.5177 | 120.5729 | -0.75905 | 0.033099 | -0.008798 | -0.047194 | 0.057037 | 0.21059 | -0.14334 | -0.25572 | -0.044943 | 0.12683 | 0.38094 | 0.2204 | 0.26535 | 0.080031 | 0.13533 | 0.45839 | -120.3806 | 0.74721 | 0.66692 | 0.20853 | -120.227 | -120.581 | 121.2786 | 121.2318 | 121.2871 | 15.2022 | -121.1967 | 0.77115 | 0.9247 | 0.57077 | 0.70531 | -120.6933
2314 | 120.7993 | -0.74616 | 120.1447 | 1.4211e-13 | -0.028132 | 0.00178 | 0.068836 | -0.013134 | 0.058257 | -0.0073253 | -0.0031575 | 0.0047004 | 0.017182 | 0.035995 | 0.0065869 | -0.3286 | 14.7491 | -0.48455 | 120.5828 | 120.536 | 120.5913 | -0.76363 | 0.033099 | -0.008798 | -0.033458 | 0.066194 | 0.21059 | -0.14792 | -0.2603 | -0.017478 | 0.43811 | 0.41756 | 0.2616 | 0.27908 | 0.39132 | 0.44661 | 0.48585 | -120.0785 | 0.77925 | 0.7127 | 0.22685 | -119.9341 | -120.2926 | 121.3289 | 121.2821 | 121.3374 | 15.4952 | -120.9083 | 0.81235 | 0.95674 | 0.59823 | 0.73736 | -120.405
2315.75 | 120.6024 | -0.75531 | 120.3552 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068622 | -0.013134 | 0.05783 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017609 | 0.036209 | 0.0068005 | -0.32402 | 15.0604 | -0.49371 | 120.5873 | 120.5451 | 120.6004 | -0.76363 | 0.023941 | -0.008798 | -0.038036 | 0.070773 | 0.21059 | -0.14792 | -0.2603 | -0.008323 | 0.23212 | 0.43129 | 0.2616 | 0.26993 | 0.1899 | 0.24519 | 0.49501 | -120.2845 | 0.77925 | 0.71727 | 0.22227 | -120.1446 | -120.5031 | 121.3427 | 121.3004 | 121.3557 | 15.8157 | -121.1189 | 0.82608 | 0.9659 | 0.60739 | 0.74651 | -120.6155
2317.5 | 120.4468 | -0.74158 | 120.3369 | 1.4211e-13 | -0.027918 | 0.00178 | 0.06905 | -0.013134 | 0.058257 | 0.0079357 | -0.0027303 | 0.0047004 | 0.017609 | 0.036209 | 0.0072279 | -0.31944 | 15.3031 | -0.47997 | 120.6011 | 120.5589 | 120.6187 | -0.75448 | 0.033099 | -0.013377 | -0.038036 | 0.070773 | 0.20143 | -0.14334 | -0.2603 | -0.012898 | 0.26417 | 0.42214 | 0.26161 | 0.2745 | 0.22195 | 0.28182 | 0.48127 | -120.2661 | 0.77468 | 0.70354 | 0.22227 | -120.1355 | -120.4803 | 121.3427 | 121.3004 | 121.3603 | 16.0447 | -121.0914 | 0.81235 | 0.94301 | 0.59823 | 0.7282 | -120.5972
2319.25 | 120.5658 | -0.72784 | 120.5475 | 1.4211e-13 | -0.027705 | 0.0015662 | 0.068836 | -0.012707 | 0.058471 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017395 | 0.036209 | 0.0074415 | -0.29197 | 15.5915 | -0.47082 | 120.6331 | 120.5818 | 120.6462 | -0.74532 | 0.02852 | -0.008798 | -0.038036 | 0.070773 | 0.20601 | -0.15708 | -0.26488 | -0.017473 | 0.085644 | 0.43588 | 0.25703 | 0.2745 | 0.034273 | 0.098721 | 0.46296 | -120.4767 | 0.75636 | 0.68981 | 0.22685 | -120.3415 | -120.7046 | 121.361 | 121.3096 | 121.3741 | 16.3194 | -121.2928 | 0.79862 | 0.93385 | 0.57077 | 0.71905 | -120.8124
2320.9531 | 121.2524 | -0.70038 | 120.5521 | 1.4211e-13 | -0.027705 | 0.0019936 | 0.06905 | -0.01292 | 0.058257 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017395 | 0.035568 | 0.0068005 | -0.29197 | 15.8525 | -0.47082 | 120.6469 | 120.6092 | 120.6691 | -0.74532 | 0.037677 | -0.017956 | -0.038036 | 0.061616 | 0.21059 | -0.15708 | -0.25572 | -0.044939 | 0.094801 | 0.40841 | 0.22956 | 0.2745 | 0.057168 | 0.11704 | 0.44465 | -120.4904 | 0.73805 | 0.66234 | 0.21769 | -120.3415 | -120.7091 | 121.3472 | 121.3096 | 121.3695 | 16.5529 | -121.2974 | 0.76199 | 0.91096 | 0.5433 | 0.68242 | -120.8078
2322.6406 | 120.8633 | -0.737 | 120.575 | 1.4211e-13 | -0.028346 | 0.00178 | 0.068836 | -0.013134 | 0.058471 | 0.00030522 | -0.0029439 | 0.0051278 | 0.017609 | 0.036209 | 0.0072279 | -0.28281 | 16.0906 | -0.46624 | 120.6606 | 120.6138 | 120.6737 | -0.74532 | 0.033099 | -0.013377 | -0.038036 | 0.070773 | 0.20601 | -0.15708 | -0.2603 | -0.008317 | 0.085648 | 0.45419 | 0.27076 | 0.27908 | 0.038859 | 0.098726 | 0.4767 | -120.5042 | 0.7701 | 0.69896 | 0.22227 | -120.3689 | -120.732 | 121.3976 | 121.3508 | 121.4107 | 16.8276 | -121.3203 | 0.80777 | 0.94301 | 0.57992 | 0.72362 | -120.8353
2324.3906 | 120.9549 | -0.75073 | 120.5795 | 1.4211e-13 | -0.028346 | 0.00178 | 0.068836 | -0.013134 | 0.058257 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017609 | 0.036209 | 0.0065869 | -0.29197 | 16.3745 | -0.46624 | 120.6514 | 120.6138 | 120.6737 | -0.75905 | 0.02852 | -0.013377 | -0.038036 | 0.066194 | 0.20601 | -0.1525 | -0.25572 | -0.008322 | 0.071913 | 0.45876 | 0.28449 | 0.29282 | 0.034281 | 0.094148 | 0.49501 | -120.5133 | 0.77925 | 0.7127 | 0.21769 | -120.3735 | -120.732 | 121.4022 | 121.3645 | 121.4244 | 17.1252 | -121.3386 | 0.81693 | 0.95674 | 0.59823 | 0.73735 | -120.8353
2326.1406 | 121.3577 | -0.70038 | 120.5292 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068836 | -0.013134 | 0.058044 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017609 | 0.035995 | 0.0068005 | -0.28739 | 16.6217 | -0.47082 | 120.6606 | 120.6184 | 120.6828 | -0.76363 | 0.02852 | -0.013377 | -0.028879 | 0.070773 | 0.20143 | -0.16166 | -0.25572 | -0.063255 | 0.13142 | 0.41299 | 0.22956 | 0.29282 | 0.089214 | 0.15366 | 0.44465 | -120.4584 | 0.7289 | 0.6715 | 0.22685 | -120.3277 | -120.6908 | 121.361 | 121.3188 | 121.3832 | 17.3221 | -121.2928 | 0.77115 | 0.90181 | 0.53872 | 0.687 | -120.7849
2327.8281 | 120.9503 | -0.737 | 120.4376 | 1.4211e-13 | -0.027918 | 0.0015662 | 0.06905 | -0.013134 | 0.058685 | 0.00030522 | -0.0027303 | 0.0047004 | 0.017609 | 0.036209 | 0.0068005 | -0.28281 | 16.9422 | -0.47082 | 120.6743 | 120.6275 | 120.6874 | -0.75905 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.14334 | -0.2603 | -0.022054 | 0.23671 | 0.45419 | 0.26618 | 0.28824 | 0.18993 | 0.24979 | 0.4767 | -120.3668 | 0.76552 | 0.69439 | 0.21769 | -120.227 | -120.581 | 121.4113 | 121.3645 | 121.4244 | 17.6792 | -121.1967 | 0.80777 | 0.94759 | 0.59366 | 0.72362 | -120.6979
2329.5156 | 121.3531 | -0.70496 | 120.5612 | 1.4211e-13 | -0.027918 | 0.0019936 | 0.069477 | -0.013134 | 0.058257 | 0.0079357 | -0.0027303 | 0.0049142 | 0.017609 | 0.035782 | 0.0068005 | -0.27823 | 17.1483 | -0.47082 | 120.6835 | 120.6321 | 120.692 | -0.76821 | 0.02852 | -0.013377 | -0.038036 | 0.070773 | 0.20601 | -0.14334 | -0.2603 | -0.063256 | 0.12227 | 0.42672 | 0.23414 | 0.2974 | 0.070908 | 0.13077 | 0.44465 | -120.4904 | 0.73348 | 0.66692 | 0.22227 | -120.3552 | -120.7046 | 121.3884 | 121.3371 | 121.3969 | 17.8532 | -121.3294 | 0.77573 | 0.91096 | 0.56161 | 0.69158 | -120.8215
2331.2656 | 121.2479 | -0.75989 | 120.6024 | 1.4211e-13 | -0.028346 | 0.0015662 | 0.069263 | -0.01292 | 0.058257 | 0.0079357 | -0.0027303 | 0.0053414 | 0.017395 | 0.036423 | 0.0068005 | -0.26908 | 17.4276 | -0.47082 | 120.6835 | 120.6459 | 120.7103 | -0.77279 | 0.033099 | -0.013377 | -0.028879 | 0.061616 | 0.21059 | -0.1525 | -0.2603 | -0.012903 | 0.081074 | 0.49081 | 0.28907 | 0.30197 | 0.043446 | 0.10789 | 0.49958 | -120.5408 | 0.79299 | 0.73101 | 0.23142 | -120.3918 | -120.7549 | 121.4434 | 121.4058 | 121.4702 | 18.1875 | -121.3752 | 0.8215 | 0.97047 | 0.60739 | 0.74651 | -120.8627
2333.0312 | 121.2891 | -0.72327 | 120.639 | 1.4211e-13 | -0.027705 | 0.0013526 | 0.068622 | -0.013134 | 0.058471 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017609 | 0.036209 | 0.0072279 | -0.26908 | 17.6977 | -0.46166 | 120.6972 | 120.6504 | 120.7103 | -0.76821 | 0.033099 | -0.008798 | -0.033458 | 0.070773 | 0.21059 | -0.1525 | -0.2603 | -0.044945 | 0.058188 | 0.45419 | 0.26161 | 0.30655 | 0.011404 | 0.071268 | 0.46296 | -120.5683 | 0.75637 | 0.68981 | 0.22685 | -120.4285 | -120.7915 | 121.4205 | 121.3737 | 121.4336 | 18.421 | -121.4073 | 0.79404 | 0.93385 | 0.57077 | 0.71447 | -120.8993
2334.7188 | 121.3623 | -0.71411 | 120.5566 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068622 | -0.013134 | 0.058685 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017182 | 0.036423 | 0.0070143 | -0.2645 | 17.9312 | -0.46166 | 120.7018 | 120.655 | 120.7149 | -0.76821 | 0.02852 | -0.017956 | -0.038036 | 0.066194 | 0.21059 | -0.15708 | -0.26946 | -0.054101 | 0.14516 | 0.44961 | 0.25245 | 0.30655 | 0.09838 | 0.15824 | 0.44465 | -120.4904 | 0.74263 | 0.67608 | 0.23143 | -120.3461 | -120.7137 | 121.4159 | 121.3691 | 121.429 | 18.6453 | -121.3249 | 0.78031 | 0.9247 | 0.55703 | 0.69616 | -120.8261
2336.4688 | 121.3989 | -0.72327 | 120.5521 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068836 | -0.013134 | 0.058257 | -0.0073253 | -0.0027303 | 0.0049142 | 0.017395 | 0.035995 | 0.0068005 | -0.26908 | 18.1922 | -0.47997 | 120.6926 | 120.6459 | 120.7057 | -0.78195 | 0.023941 | -0.017956 | -0.038036 | 0.070773 | 0.21059 | -0.14792 | -0.26488 | -0.058681 | 0.14059 | 0.45419 | 0.24329 | 0.30198 | 0.0938 | 0.15366 | 0.45838 | -120.4813 | 0.74721 | 0.68523 | 0.22685 | -120.3415 | -120.7 | 121.4159 | 121.3691 | 121.429 | 18.9155 | -121.334 | 0.79404 | 0.93385 | 0.57534 | 0.70531 | -120.8169
2338.2188 | 121.3348 | -0.78278 | 120.6162 | 1.4211e-13 | -0.027918 | 0.00178 | 0.069477 | -0.012707 | 0.058257 | 0.015566 | -0.0031575 | 0.0049142 | 0.017823 | 0.036423 | 0.0072279 | -0.27823 | 18.4394 | -0.48455 | 120.6835 | 120.6459 | 120.7011 | -0.79111 | 0.02852 | -0.008798 | -0.042615 | 0.061616 | 0.21974 | -0.1525 | -0.25115 | -0.00833 | 0.067341 | 0.50454 | 0.29823 | 0.30655 | 0.029713 | 0.084999 | 0.53163 | -120.5545 | 0.8113 | 0.74016 | 0.20853 | -120.3964 | -120.7687 | 121.4663 | 121.4286 | 121.4839 | 19.2222 | -121.4073 | 0.84439 | 1.0025 | 0.63028 | 0.77398 | -120.8673
2339.9688 | 121.3943 | -0.75989 | 120.5658 | 1.4211e-13 | -0.027918 | 0.00178 | 0.06905 | -0.013348 | 0.058257 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017395 | 0.036209 | 0.0065869 | -0.28739 | 18.6867 | -0.49371 | 120.6743 | 120.6504 | 120.7011 | -0.814 | 0.023941 | -0.008798 | -0.033458 | 0.070773 | 0.21516 | -0.15708 | -0.2603 | -0.054113 | 0.10854 | 0.4725 | 0.26618 | 0.32029 | 0.084646 | 0.13535 | 0.49958 | -120.495 | 0.78383 | 0.72643 | 0.22685 | -120.3506 | -120.7229 | 121.4342 | 121.4103 | 121.461 | 19.4466 | -121.3798 | 0.83066 | 0.97505 | 0.60281 | 0.75109 | -120.8261
2341.6562 | 121.4172 | -0.75531 | 120.5658 | 1.4211e-13 | -0.027918 | 0.00178 | 0.068622 | -0.013134 | 0.058471 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017182 | 0.035995 | 0.0068005 | -0.27823 | 18.9248 | -0.49371 | 120.6881 | 120.6459 | 120.7057 | -0.814 | 0.033099 | -0.013377 | -0.042615 | 0.061616 | 0.21059 | -0.14334 | -0.27404 | -0.058691 | 0.12227 | 0.47708 | 0.2616 | 0.32029 | 0.080067 | 0.13993 | 0.48127 | -120.5042 | 0.78841 | 0.7127 | 0.23142 | -120.3552 | -120.7091 | 121.4434 | 121.4012 | 121.461 | 19.6801 | -121.3798 | 0.81693 | 0.9659 | 0.61197 | 0.74193 | -120.8398
2343.4219 | 121.2753 | -0.80109 | 120.5933 | 1.4211e-13 | -0.027918 | 0.0019936 | 0.069263 | -0.013134 | 0.058257 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017823 | 0.036209 | 0.0068005 | -0.26908 | 19.1583 | -0.48913 | 120.6926 | 120.6596 | 120.7149 | -0.80942 | 0.023941 | -0.013377 | -0.033458 | 0.075351 | 0.21059 | -0.1525 | -0.26946 | -0.008336 | 0.099386 | 0.53201 | 0.31196 | 0.32029 | 0.066338 | 0.12162 | 0.53162 | -120.5179 | 0.82503 | 0.76763 | 0.236 | -120.3827 | -120.7458 | 121.4937 | 121.4607 | 121.516 | 19.9594 | -121.4027 | 0.87644 | 1.0117 | 0.64859 | 0.78771 | -120.8627
2345.1719 | 121.3211 | -0.81024 | 120.6116 | 1.4211e-13 | -0.028346 | 0.00178 | 0.06905 | -0.013134 | 0.058257 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017182 | 0.036209 | 0.0070143 | -0.25992 | 19.3597 | -0.50286 | 120.6881 | 120.6596 | 120.724 | -0.81858 | 0.033099 | -0.00422 | -0.038036 | 0.066194 | 0.20601 | -0.15708 | -0.2603 | -0.008338 | 0.076497 | 0.55032 | 0.30738 | 0.31572 | 0.048028 | 0.11247 | 0.54994 | -120.5454 | 0.84334 | 0.77221 | 0.22227 | -120.4056 | -120.7687 | 121.4983 | 121.4698 | 121.5343 | 20.17 | -121.4302 | 0.87644 | 1.0163 | 0.65316 | 0.80602 | -120.8719
2346.8594 | 121.376 | -0.80566 | 120.6253 | 1.4211e-13 | -0.028346 | 0.00178 | 0.06905 | -0.013348 | 0.058685 | 0.0079357 | -0.0027303 | 0.0047004 | 0.017395 | 0.036636 | 0.0070143 | -0.25076 | 19.5795 | -0.48455 | 120.7064 | 120.6688 | 120.7286 | -0.814 | 0.02852 | -0.008798 | -0.042615 | 0.061616 | 0.20601 | -0.1525 | -0.26488 | -0.008337 | 0.081078 | 0.5549 | 0.32111 | 0.32945 | 0.043452 | 0.10332 | 0.54078 | -120.5637 | 0.83418 | 0.76305 | 0.22227 | -120.4193 | -120.7778 | 121.512 | 121.4744 | 121.5343 | 20.3852 | -121.4393 | 0.86728 | 1.0117 | 0.65316 | 0.79687 | -120.8902
2348.6094 | 121.4127 | -0.76904 | 120.6024 | 1.4211e-13 | -0.027918 | 0.0019936 | 0.06905 | -0.01292 | 0.058257 | 0.023196 | -0.0033713 | 0.0047004 | 0.017823 | 0.035782 | 0.0068005 | -0.23703 | 19.8039 | -0.47082 | 120.7201 | 120.6871 | 120.7469 | -0.80942 | 0.02852 | -0.013377 | -0.033458 | 0.066194 | 0.21516 | -0.1525 | -0.26488 | -0.040379 | 0.1177 | 0.53201 | 0.29823 | 0.33861 | 0.084656 | 0.14452 | 0.50416 | -120.5362 | 0.79756 | 0.73559 | 0.23142 | -120.3873 | -120.7549 | 121.4892 | 121.4561 | 121.516 | 20.5729 | -121.4118 | 0.83524 | 0.98421 | 0.61654 | 0.75567 | -120.8673
2350.375 | 121.4584 | -0.75531 | 120.5475 | 1.4211e-13 | -0.028346 | 0.0019936 | 0.06905 | -0.013348 | 0.058044 | 0.00030522 | -0.0031575 | 0.0051278 | 0.017609 | 0.036209 | 0.0068005 | -0.24161 | 20.0786 | -0.48913 | 120.7064 | 120.6779 | 120.7286 | -0.82774 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.2603 | -0.072428 | 0.1589 | 0.5137 | 0.26618 | 0.33861 | 0.13043 | 0.18114 | 0.49501 | -120.4813 | 0.77925 | 0.70812 | 0.21311 | -120.3369 | -120.7 | 121.4617 | 121.4332 | 121.4839 | 20.8339 | -121.3752 | 0.8215 | 0.9659 | 0.60281 | 0.74193 | -120.8078
2352.0938 | 121.4584 | -0.76904 | 120.5658 | 1.4211e-13 | -0.028132 | 0.00178 | 0.06905 | -0.013134 | 0.058257 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017395 | 0.036209 | 0.0070143 | -0.25076 | 20.2984 | -0.49828 | 120.7018 | 120.6642 | 120.7286 | -0.84147 | 0.033099 | -0.013377 | -0.038036 | 0.061616 | 0.21059 | -0.14792 | -0.26488 | -0.072431 | 0.13601 | 0.51828 | 0.27076 | 0.34319 | 0.098382 | 0.16282 | 0.50416 | -120.5042 | 0.80214 | 0.73101 | 0.22685 | -120.3552 | -120.7137 | 121.4708 | 121.4332 | 121.4977 | 21.0674 | -121.4073 | 0.83066 | 0.97963 | 0.62112 | 0.75567 | -120.8307
2353.8438 | 121.4813 | -0.78735 | 120.5887 | 1.4211e-13 | -0.028132 | 0.0015662 | 0.069263 | -0.013134 | 0.058471 | 0.0079357 | -0.0033713 | 0.0047004 | 0.017182 | 0.036209 | 0.0068005 | -0.24161 | 20.5456 | -0.49371 | 120.711 | 120.6733 | 120.7332 | -0.84147 | 0.033099 | -0.013377 | -0.033458 | 0.075351 | 0.21974 | -0.1525 | -0.25572 | -0.05412 | 0.12228 | 0.54575 | 0.29365 | 0.34777 | 0.084652 | 0.14451 | 0.53163 | -120.5133 | 0.82045 | 0.7539 | 0.22227 | -120.3689 | -120.7412 | 121.4983 | 121.4607 | 121.5206 | 21.333 | -121.4302 | 0.86271 | 1.0071 | 0.63485 | 0.77398 | -120.8444
2355.5781 | 121.3943 | -0.8194 | 120.639 | 1.4211e-13 | -0.028132 | 0.0022072 | 0.06905 | -0.013348 | 0.058257 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017609 | 0.03685 | 0.0070143 | -0.22787 | 20.7699 | -0.48913 | 120.711 | 120.6825 | 120.7469 | -0.84605 | 0.033099 | -0.008798 | -0.038036 | 0.066194 | 0.21974 | -0.15708 | -0.25572 | -0.026656 | 0.071923 | 0.59153 | 0.33027 | 0.35692 | 0.043456 | 0.1079 | 0.56367 | -120.5728 | 0.8525 | 0.78136 | 0.21769 | -120.4193 | -120.7961 | 121.5304 | 121.5019 | 121.5663 | 21.5893 | -121.4851 | 0.88559 | 1.0391 | 0.66232 | 0.8106 | -120.8948
2357.3281 | 121.3898 | -0.84228 | 120.639 | 1.4211e-13 | -0.028346 | 0.00178 | 0.06905 | -0.013348 | 0.058471 | 0.015566 | -0.0027303 | 0.0047004 | 0.017395 | 0.036423 | 0.0068005 | -0.21871 | 20.9897 | -0.47997 | 120.7201 | 120.6962 | 120.7561 | -0.84605 | 0.023941 | -0.008798 | -0.033458 | 0.070773 | 0.21516 | -0.1525 | -0.2603 | -0.003768 | 0.08108 | 0.62357 | 0.36231 | 0.36608 | 0.057193 | 0.11705 | 0.58198 | -120.5683 | 0.86623 | 0.80883 | 0.22685 | -120.4239 | -120.7915 | 121.5624 | 121.5385 | 121.5984 | 21.832 | -121.4851 | 0.91306 | 1.0575 | 0.68978 | 0.83349 | -120.8993
2359.0156 | 121.4722 | -0.80566 | 120.6207 | 1.4211e-13 | -0.028132 | 0.0015662 | 0.068836 | -0.013348 | 0.058471 | -0.0073253 | -0.0031575 | 0.0049142 | 0.017395 | 0.036209 | 0.0065869 | -0.21871 | 21.2232 | -0.49371 | 120.7247 | 120.6871 | 120.7469 | -0.85063 | 0.033099 | -0.017956 | -0.042615 | 0.075351 | 0.21516 | -0.1525 | -0.25572 | -0.044968 | 0.10397 | 0.58695 | 0.31196 | 0.35693 | 0.066345 | 0.12621 | 0.54994 | -120.5454 | 0.83876 | 0.76305 | 0.21311 | -120.4056 | -120.7732 | 121.5304 | 121.4927 | 121.5526 | 22.0289 | -121.4714 | 0.88102 | 1.0208 | 0.65316 | 0.78771 | -120.8765
2360.7656 | 121.4172 | -0.85602 | 120.607 | 1.4211e-13 | -0.028132 | 0.0022072 | 0.068622 | -0.013348 | 0.058685 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017609 | 0.036209 | 0.0068005 | -0.21871 | 21.4522 | -0.48913 | 120.7155 | 120.6871 | 120.7515 | -0.85979 | 0.033099 | -0.00422 | -0.028879 | 0.066194 | 0.21059 | -0.14792 | -0.2603 | -0.003772 | 0.10855 | 0.6373 | 0.36689 | 0.37066 | 0.080078 | 0.14452 | 0.59571 | -120.5408 | 0.88912 | 0.82714 | 0.23142 | -120.3964 | -120.7549 | 121.5716 | 121.5431 | 121.6075 | 22.3082 | -121.4668 | 0.92221 | 1.0666 | 0.7081 | 0.8518 | -120.8673
2362.5156 | 121.3806 | -0.85602 | 120.6207 | 1.4211e-13 | -0.028132 | 0.00178 | 0.06905 | -0.013348 | 0.058257 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017823 | 0.036423 | 0.0068005 | -0.22329 | 21.6582 | -0.49371 | 120.711 | 120.6871 | 120.7515 | -0.89184 | 0.02852 | -0.00422 | -0.038036 | 0.070773 | 0.21516 | -0.15708 | -0.2603 | -0.035825 | 0.090233 | 0.63272 | 0.36231 | 0.39814 | 0.066345 | 0.13079 | 0.59571 | -120.55 | 0.88454 | 0.81798 | 0.22227 | -120.4056 | -120.7778 | 121.567 | 121.5431 | 121.6075 | 22.5142 | -121.5126 | 0.92679 | 1.0712 | 0.69894 | 0.8518 | -120.881
2364.2031 | 121.4813 | -0.8606 | 120.5795 | 1.4211e-13 | -0.027918 | 0.0015662 | 0.06905 | -0.01292 | 0.058685 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017182 | 0.036209 | 0.0068005 | -0.22329 | 21.8184 | -0.51202 | 120.7018 | 120.6733 | 120.7286 | -0.92847 | 0.033099 | -0.017956 | -0.038036 | 0.061616 | 0.21516 | -0.1525 | -0.25115 | -0.067878 | 0.12228 | 0.6373 | 0.34858 | 0.41645 | 0.093807 | 0.14909 | 0.60945 | -120.5179 | 0.8937 | 0.82256 | 0.21311 | -120.3644 | -120.732 | 121.5624 | 121.5339 | 121.5892 | 22.679 | -121.508 | 0.92221 | 1.0758 | 0.7081 | 0.84264 | -120.8307
2365.9688 | 121.5729 | -0.83313 | 120.5612 | 1.4211e-13 | -0.028132 | 0.0019936 | 0.068836 | -0.01292 | 0.058471 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017182 | 0.035995 | 0.0068005 | -0.21871 | 21.9421 | -0.5166 | 120.6972 | 120.6688 | 120.7286 | -0.89642 | 0.02852 | -0.013377 | -0.033458 | 0.061616 | 0.21059 | -0.15708 | -0.25572 | -0.063292 | 0.13601 | 0.61442 | 0.31653 | 0.37982 | 0.10754 | 0.1674 | 0.57741 | -120.4996 | 0.86165 | 0.79967 | 0.22227 | -120.3506 | -120.7183 | 121.5304 | 121.5019 | 121.5618 | 22.7752 | -121.4576 | 0.89475 | 1.0437 | 0.67605 | 0.81975 | -120.8169
2367.6719 | 121.4355 | -0.91095 | 120.5795 | 1.4211e-13 | -0.028132 | 0.0019936 | 0.069477 | -0.013348 | 0.058898 | 0.015566 | -0.0029439 | 0.0049142 | 0.017395 | 0.036209 | 0.0068005 | -0.22329 | 22.1069 | -0.52575 | 120.6881 | 120.655 | 120.724 | -0.91016 | 0.033099 | -0.008798 | -0.038036 | 0.061616 | 0.20601 | -0.1525 | -0.2603 | 0.000792 | 0.10854 | 0.68766 | 0.3852 | 0.3844 | 0.075492 | 0.14451 | 0.65065 | -120.5179 | 0.94405 | 0.87291 | 0.22227 | -120.3735 | -120.732 | 121.599 | 121.566 | 121.635 | 23.0178 | -121.4897 | 0.97257 | 1.117 | 0.75845 | 0.90215 | -120.8398
2369.4219 | 121.5225 | -0.90637 | 120.4971 | 1.4211e-13 | -0.028132 | 0.00178 | 0.06905 | -0.013134 | 0.058898 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017609 | 0.036423 | 0.0068005 | -0.23703 | 22.2717 | -0.53491 | 120.6743 | 120.6459 | 120.7103 | -0.92847 | 0.023941 | -0.017956 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.26488 | -0.022102 | 0.1772 | 0.66934 | 0.37146 | 0.39356 | 0.14873 | 0.21318 | 0.64149 | -120.4264 | 0.93031 | 0.86376 | 0.22227 | -120.2865 | -120.6496 | 121.5807 | 121.5522 | 121.6167 | 23.1781 | -121.4256 | 0.97714 | 1.117 | 0.75387 | 0.88842 | -120.762
2371.1719 | 121.5225 | -0.90637 | 120.5475 | 1.4211e-13 | -0.028132 | 0.00178 | 0.06905 | -0.01292 | 0.059112 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017609 | 0.036209 | 0.0068005 | -0.23703 | 22.3816 | -0.54865 | 120.6698 | 120.6367 | 120.7011 | -0.95595 | 0.02852 | -0.017956 | -0.038036 | 0.061616 | 0.21059 | -0.14792 | -0.2603 | -0.049576 | 0.12227 | 0.66934 | 0.35773 | 0.4073 | 0.08922 | 0.15366 | 0.64607 | -120.4859 | 0.93489 | 0.86834 | 0.22227 | -120.3369 | -120.6954 | 121.5761 | 121.5431 | 121.6075 | 23.288 | -121.5034 | 0.96799 | 1.117 | 0.75845 | 0.88842 | -120.8078
2372.8594 | 121.5088 | -0.90637 | 120.5475 | 1.4211e-13 | -0.028132 | 0.00178 | 0.06905 | -0.012707 | 0.058685 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017395 | 0.036423 | 0.0068005 | -0.24161 | 22.519 | -0.57154 | 120.6469 | 120.6275 | 120.6874 | -0.97884 | 0.02852 | -0.013377 | -0.033458 | 0.070773 | 0.20601 | -0.1525 | -0.2603 | -0.07247 | 0.099379 | 0.66476 | 0.33483 | 0.4073 | 0.080062 | 0.13993 | 0.64607 | -120.4767 | 0.93489 | 0.87291 | 0.22685 | -120.3415 | -120.7 | 121.5532 | 121.5339 | 121.5938 | 23.4253 | -121.5263 | 0.97714 | 1.1124 | 0.75387 | 0.89299 | -120.8078
2374.6094 | 121.4264 | -0.98419 | 120.5429 | 1.4211e-13 | -0.028346 | 0.00178 | 0.068836 | -0.01292 | 0.058685 | -0.0073253 | -0.0031575 | 0.0042732 | 0.017609 | 0.036209 | 0.0068005 | -0.25076 | 22.6701 | -0.57612 | 120.6331 | 120.6047 | 120.6691 | -1.0017 | 0.037677 | -0.008798 | -0.033458 | 0.070773 | 0.21516 | -0.16166 | -0.2603 | -0.017545 | 0.090221 | 0.73343 | 0.40808 | 0.42562 | 0.061744 | 0.12619 | 0.72389 | -120.4721 | 1.0219 | 0.95073 | 0.22685 | -120.3277 | -120.7046 | 121.6173 | 121.5888 | 121.6533 | 23.6543 | -121.5446 | 1.055 | 1.1994 | 0.82253 | 0.97539 | -120.8032
2376.2969 | 121.4264 | -0.99335 | 120.5383 | 1.4211e-13 | -0.027918 | 0.00178 | 0.069263 | -0.013134 | 0.058471 | 0.00030522 | -0.0029439 | 0.0053414 | 0.017395 | 0.036423 | 0.0068005 | -0.29197 | 22.8257 | -0.62648 | 120.5873 | 120.5634 | 120.6233 | -1.0704 | 0.033099 | -0.008798 | -0.042615 | 0.070773 | 0.21059 | -0.14334 | -0.25572 | -0.077074 | 0.049015 | 0.70138 | 0.36687 | 0.44394 | 0.025112 | 0.084983 | 0.73762 | -120.4676 | 1.0264 | 0.95073 | 0.21311 | -120.3277 | -120.6817 | 121.5807 | 121.5568 | 121.6167 | 23.8191 | -121.6088 | 1.0641 | 1.2039 | 0.85 | 0.98455 | -120.7941
2378.0469 | 121.4676 | -1.2222 | 120.2042 | 1.4211e-13 | -0.028346 | 0.00178 | 0.069263 | -0.013348 | 0.058685 | -0.014956 | -0.0029439 | 0.0047004 | 0.017395 | 0.036209 | 0.0065869 | -0.45221 | 22.8532 | -0.80045 | 120.4134 | 120.3894 | 120.4447 | -1.2353 | 0.02852 | -0.008798 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.2603 | -0.013033 | 0.2092 | 0.77002 | 0.42178 | 0.43481 | 0.18528 | 0.24058 | 0.96193 | -120.1334 | 1.2507 | 1.1796 | 0.21769 | -119.9936 | -120.3567 | 121.6356 | 121.6117 | 121.667 | 24.0754 | -121.4394 | 1.293 | 1.4328 | 1.0697 | 1.2134 | -120.4645
2379.7969 | 121.431 | -1.1536 | 120.3781 | 1.4211e-13 | -0.027918 | 0.00178 | 0.06905 | -0.013561 | 0.058471 | 0.015566 | -0.0029439 | 0.0049142 | 0.017609 | 0.036636 | 0.0070143 | -0.45221 | 23.0089 | -0.81876 | 120.3951 | 120.3711 | 120.4264 | -1.2536 | 0.02852 | -0.017956 | -0.038036 | 0.070773 | 0.21059 | -0.15708 | -0.2603 | -0.10001 | 0.01694 | 0.70135 | 0.3348 | 0.43481 | -0.006986 | 0.04832 | 0.89326 | -120.3073 | 1.1821 | 1.1155 | 0.22227 | -120.1675 | -120.5352 | 121.5486 | 121.5247 | 121.58 | 24.1624 | -121.6317 | 1.2243 | 1.3641 | 0.99649 | 1.1356 | -120.6384
2381.5469 | 121.5179 | -1.268 | 120.2454 | 1.4211e-13 | -0.028559 | 0.00178 | 0.06905 | -0.01292 | 0.058471 | 0.030827 | -0.0031575 | 0.0049142 | 0.017609 | 0.036423 | 0.0063733 | -0.47053 | 23.1737 | -0.80961 | 120.3905 | 120.362 | 120.4402 | -1.249 | 0.033099 | -0.013377 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.26488 | 0.019006 | 0.14511 | 0.79748 | 0.4584 | 0.43939 | 0.11661 | 0.19481 | 1.0031 | -120.1792 | 1.3011 | 1.23 | 0.22685 | -120.0348 | -120.3979 | 121.6585 | 121.63 | 121.7082 | 24.4417 | -121.4944 | 1.3342 | 1.4786 | 1.1155 | 1.2546 | -120.5102
2383.3594 | 121.4676 | -1.2772 | 120.2728 | 1.4211e-13 | -0.028132 | 0.0019936 | 0.069263 | -0.013561 | 0.058898 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017182 | 0.036209 | 0.0068005 | -0.48426 | 23.3523 | -0.83708 | 120.3676 | 120.3437 | 120.4127 | -1.2856 | 0.037677 | -0.013377 | -0.051772 | 0.066194 | 0.20601 | -0.1525 | -0.25572 | -0.008469 | 0.094755 | 0.7929 | 0.44008 | 0.44855 | 0.070827 | 0.13987 | 1.0214 | -120.2066 | 1.3148 | 1.2254 | 0.20395 | -120.0668 | -120.4253 | 121.6447 | 121.6208 | 121.6899 | 24.6294 | -121.5585 | 1.3434 | 1.4832 | 1.1247 | 1.2638 | -120.5286
2385.0625 | 121.6095 | -1.2589 | 120.2271 | 1.4211e-13 | -0.028346 | 0.00178 | 0.06905 | -0.013134 | 0.058898 | 0.015566 | -0.0031575 | 0.0047004 | 0.017609 | 0.035782 | 0.0068005 | -0.57583 | 23.4255 | -0.9378 | 120.2669 | 120.2429 | 120.3074 | -1.3909 | 0.02852 | -0.013377 | -0.042615 | 0.066194 | 0.21059 | -0.15708 | -0.26488 | -0.1321 | 0.039807 | 0.68302 | 0.32105 | 0.45315 | 0.015866 | 0.080338 | 0.99397 | -120.1609 | 1.2874 | 1.2162 | 0.22227 | -120.0165 | -120.3841 | 121.5257 | 121.5018 | 121.5662 | 24.6844 | -121.618 | 1.325 | 1.4694 | 1.1018 | 1.2455 | -120.4919
2386.8438 | 121.5912 | -1.1032 | 120.3506 | 1.4211e-13 | -0.028346 | 0.0019936 | 0.069477 | -0.01292 | 0.058898 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017823 | 0.035995 | 0.0068005 | -0.34691 | 23.6819 | -0.71804 | 120.4958 | 120.4627 | 120.5317 | -1.1666 | 0.023941 | -0.013377 | -0.038036 | 0.066194 | 0.20143 | -0.1525 | -0.26488 | -0.063368 | 0.14513 | 0.7563 | 0.38517 | 0.44853 | 0.11206 | 0.18109 | 0.83833 | -120.2845 | 1.1272 | 1.0652 | 0.22685 | -120.1492 | -120.5031 | 121.599 | 121.5659 | 121.635 | 24.7851 | -121.5172 | 1.1694 | 1.3046 | 0.95071 | 1.0898 | -120.6155
2388.625 | 117.1051 | -59.3079 | 57.5592 | 1.4211e-13 | -0.028987 | 0.00049784 | 0.066485 | -0.01292 | 0.057189 | -0.014956 | -0.0033713 | 0.0051278 | 0.017823 | 0.036423 | 0.0065869 | -47.8523 | -1.9079 | -48.2818 | 70.1793 | 69.9938 | 70.4876 | -48.9385 | 0.042256 | 0.000359 | -0.028879 | 0.07993 | 0.21974 | -0.14792 | -0.24657 | 10.3694 | 12.6201 | 11.4556 | 11.0261 | 0.6567 | 12.4346 | 12.9284 | 59.0613 | -57.4793 | 59.3501 | 59.279 | 0.21769 | -57.3395 | -57.7071 | 129.4872 | 129.3017 | 129.7955 | 57.4 | -106.4977 | 59.3878 | 59.5276 | 59.1599 | 59.3082 | -57.8058
2390.3281 | 120.2637 | -0.16937 | 120.0714 | 1.4211e-13 | -0.028346 | 0.00178 | 0.068409 | -0.01292 | 0.05783 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017395 | 0.036423 | 0.0065869 | -0.88258 | 23.2607 | -1.3544 | 118.3119 | 118.3518 | 118.2653 | -1.7115 | 0.033099 | -0.017956 | -0.038036 | 0.070773 | 0.20601 | -0.14792 | -0.2603 | -1.5421 | -1.7595 | -0.71321 | -1.1851 | 0.35705 | -1.7196 | -1.8061 | -0.090931 | -120.0006 | 0.20247 | 0.13134 | 0.22227 | -119.8654 | -120.2193 | 118.4813 | 118.5212 | 118.4347 | 23.4301 | -121.7829 | 0.24015 | 0.37538 | 0.021451 | 0.15142 | -120.3317
2392.0781 | 120.7031 | -0.14191 | 120.4468 | 1.4211e-13 | -0.028559 | 0.0019936 | 0.068836 | -0.013134 | 0.05783 | -0.014956 | -0.0029439 | 0.0049142 | 0.017395 | 0.036209 | 0.0068005 | 0.63744 | 24.2817 | 0.21593 | 120.569 | 120.5451 | 120.605 | -0.24621 | 0.023941 | -0.013377 | -0.033458 | 0.061616 | 0.21059 | -0.15708 | -0.26488 | -0.10431 | 0.12225 | 0.77935 | 0.35783 | 0.46214 | 0.098349 | 0.15822 | -0.12298 | -120.3852 | 0.16585 | 0.10845 | 0.23142 | -120.2362 | -120.6039 | 120.7109 | 120.687 | 120.7469 | 24.4236 | -120.693 | 0.20352 | 0.35249 | -0.015172 | 0.12853 | -120.7117
2393.7812 | 120.8221 | -0.16022 | 120.52 | 1.4211e-13 | -0.028132 | 0.00178 | 0.068622 | -0.01292 | 0.058257 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017395 | 0.036209 | 0.0065869 | 0.65118 | 24.4328 | 0.22508 | 120.6606 | 120.6459 | 120.7103 | -0.23248 | 0.023941 | -0.00422 | -0.038036 | 0.075351 | 0.21059 | -0.14792 | -0.26946 | -0.07226 | 0.14058 | 0.8114 | 0.3853 | 0.45756 | 0.12584 | 0.19029 | -0.10924 | -120.4447 | 0.18416 | 0.12218 | 0.23143 | -120.3094 | -120.6679 | 120.8208 | 120.8061 | 120.8705 | 24.593 | -120.7525 | 0.23557 | 0.3708 | 0.012295 | 0.156 | -120.7895
2395.5625 | 120.8817 | -0.15106 | 120.5795 | 1.4211e-13 | -0.028132 | 0.0019936 | 0.06905 | -0.013134 | 0.058257 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017395 | 0.036423 | 0.0065869 | 0.66949 | 24.616 | 0.20219 | 120.7201 | 120.71 | 120.7607 | -0.25995 | 0.033099 | -0.017956 | -0.038036 | 0.061616 | 0.21516 | -0.15708 | -0.26488 | -0.10889 | 0.14059 | 0.82055 | 0.35325 | 0.46214 | 0.13044 | 0.18114 | -0.11382 | -120.5179 | 0.18416 | 0.11303 | 0.22685 | -120.3644 | -120.7366 | 120.8712 | 120.861 | 120.9117 | 24.767 | -120.8395 | 0.21268 | 0.36623 | -0.006017 | 0.13311 | -120.8444
2397.2656 | 120.7947 | -0.19226 | 120.6573 | 1.4211e-13 | -0.028132 | 0.00178 | 0.068622 | -0.013134 | 0.058257 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017395 | 0.036209 | 0.0068005 | 0.69238 | 24.7716 | 0.22051 | 120.7705 | 120.7558 | 120.8156 | -0.23248 | 0.02852 | -0.013377 | -0.033458 | 0.061616 | 0.20601 | -0.1525 | -0.26488 | -0.040216 | 0.11313 | 0.88465 | 0.41277 | 0.45298 | 0.098408 | 0.15827 | -0.072622 | -120.5957 | 0.22078 | 0.1588 | 0.23142 | -120.4513 | -120.8098 | 120.9627 | 120.948 | 121.0079 | 24.9639 | -120.8898 | 0.25388 | 0.39827 | 0.039761 | 0.17888 | -120.9222
2399.0312 | 120.9229 | -0.16022 | 120.6573 | 1.4211e-13 | -0.027918 | 0.0019936 | 0.069263 | -0.013134 | 0.058471 | -0.0073253 | -0.0025167 | 0.0049142 | 0.017182 | 0.036209 | 0.0070143 | 0.7107 | 24.8403 | 0.22051 | 120.8163 | 120.7878 | 120.8614 | -0.23248 | 0.023941 | -0.017956 | -0.042615 | 0.070773 | 0.21059 | -0.15708 | -0.26946 | -0.07226 | 0.15892 | 0.87092 | 0.38072 | 0.45298 | 0.13046 | 0.20405 | -0.10924 | -120.5866 | 0.18416 | 0.1176 | 0.22685 | -120.4468 | -120.8144 | 120.9765 | 120.948 | 121.0216 | 25.0005 | -120.8898 | 0.23099 | 0.3708 | 0.003138 | 0.14226 | -120.9268
2400.7188 | 120.9824 | -0.14191 | 120.694 | 1.4211e-13 | -0.028559 | 0.00178 | 0.069263 | -0.013134 | 0.058257 | 0.0079357 | -0.0033713 | 0.0044868 | 0.017823 | 0.036423 | 0.0065869 | 0.71985 | 24.9502 | 0.22966 | 120.8437 | 120.8244 | 120.8843 | -0.22332 | 0.033099 | -0.013377 | -0.042615 | 0.075351 | 0.20601 | -0.1525 | -0.2603 | -0.081413 | 0.14977 | 0.86176 | 0.37157 | 0.45298 | 0.13047 | 0.19032 | -0.1184 | -120.6186 | 0.17501 | 0.099292 | 0.21769 | -120.488 | -120.8465 | 120.9856 | 120.9663 | 121.0262 | 25.0921 | -120.9173 | 0.21726 | 0.34791 | -0.010593 | 0.12853 | -120.9543
2402.4688 | 121.0007 | -0.18768 | 120.7169 | 1.4211e-13 | -0.028132 | 0.0022072 | 0.06905 | -0.013134 | 0.058257 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017609 | 0.036209 | 0.0068005 | 0.74733 | 25.0555 | 0.2434 | 120.8758 | 120.8519 | 120.9163 | -0.23706 | 0.023941 | -0.013377 | -0.033458 | 0.066194 | 0.20601 | -0.15708 | -0.26488 | -0.049373 | 0.15892 | 0.93501 | 0.43108 | 0.48045 | 0.13506 | 0.19948 | -0.0772 | -120.6507 | 0.21162 | 0.15423 | 0.23142 | -120.5109 | -120.8739 | 121.0635 | 121.0396 | 121.104 | 25.2432 | -120.9539 | 0.25388 | 0.39369 | 0.030604 | 0.17431 | -120.9817
2404.2188 | 121.0648 | -0.15564 | 120.7443 | 1.4211e-13 | -0.027918 | 0.0022072 | 0.068836 | -0.01292 | 0.058685 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017395 | 0.036209 | 0.0065869 | 0.75648 | 25.1517 | 0.2434 | 120.8987 | 120.884 | 120.9484 | -0.2279 | 0.023941 | -0.00422 | -0.038036 | 0.066194 | 0.20143 | -0.14792 | -0.27404 | -0.072259 | 0.15435 | 0.91212 | 0.39904 | 0.4713 | 0.13964 | 0.20407 | -0.1184 | -120.6781 | 0.17958 | 0.1176 | 0.236 | -120.5429 | -120.8922 | 121.0543 | 121.0396 | 121.104 | 25.3073 | -120.9722 | 0.22183 | 0.35707 | 0.007718 | 0.15142 | -121.0184
2405.9062 | 120.9274 | -0.21515 | 120.813 | 1.4211e-13 | -0.028132 | 0.00178 | 0.068622 | -0.012707 | 0.058257 | 0.00030522 | -0.0027303 | 0.0049142 | 0.017609 | 0.035995 | 0.0065869 | 0.7748 | 25.3073 | 0.25255 | 120.917 | 120.9023 | 120.9667 | -0.22332 | 0.02852 | -0.027113 | -0.042615 | 0.066194 | 0.21516 | -0.14792 | -0.26946 | -0.008171 | 0.104 | 0.98994 | 0.4677 | 0.47587 | 0.089295 | 0.15372 | -0.054313 | -120.7468 | 0.24367 | 0.17253 | 0.22685 | -120.5978 | -120.9609 | 121.1321 | 121.1174 | 121.1819 | 25.5225 | -121.0363 | 0.28134 | 0.43031 | 0.067227 | 0.18804 | -121.0825
2407.6562 | 120.9732 | -0.20599 | 120.8771 | 1.4211e-13 | -0.028346 | 0.00178 | 0.068622 | -0.013134 | 0.058685 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016968 | 0.03685 | 0.0063733 | 0.80227 | 25.4218 | 0.26629 | 120.949 | 120.9252 | 120.9942 | -0.22332 | 0.033099 | -0.008798 | -0.038036 | 0.061616 | 0.20601 | -0.1525 | -0.2603 | -0.017326 | 0.071963 | 1.0083 | 0.47228 | 0.48961 | 0.048102 | 0.1171 | -0.05431 | -120.8155 | 0.23909 | 0.16796 | 0.22227 | -120.6711 | -121.0296 | 121.155 | 121.1312 | 121.2002 | 25.6278 | -121.1004 | 0.26761 | 0.412 | 0.053494 | 0.1972 | -121.1374
2409.4062 | 120.9778 | -0.20142 | 120.8633 | 1.4211e-13 | -0.028346 | 0.0022072 | 0.068622 | -0.012707 | 0.058685 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017182 | 0.036209 | 0.0068005 | 0.81142 | 25.5134 | 0.27087 | 120.9582 | 120.9435 | 121.0125 | -0.23248 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20143 | -0.15708 | -0.26488 | -0.031061 | 0.094852 | 1.0128 | 0.47228 | 0.50334 | 0.080151 | 0.14915 | -0.063467 | -120.7971 | 0.22536 | 0.15422 | 0.21769 | -120.6619 | -121.0204 | 121.1596 | 121.1449 | 121.2139 | 25.7148 | -121.0958 | 0.26761 | 0.40285 | 0.044337 | 0.18804 | -121.1282
2411.1562 | 121.0602 | -0.19226 | 120.8771 | 1.4211e-13 | -0.028773 | 0.0022072 | 0.06905 | -0.01292 | 0.058685 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017395 | 0.035995 | 0.0068005 | 0.83431 | 25.6233 | 0.28002 | 120.9857 | 120.9664 | 121.0308 | -0.23248 | 0.023941 | -0.013377 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.26488 | -0.040216 | 0.10859 | 1.0266 | 0.47228 | 0.5125 | 0.089313 | 0.15373 | -0.072622 | -120.8063 | 0.2162 | 0.14965 | 0.22227 | -120.6711 | -121.0296 | 121.1779 | 121.1586 | 121.2231 | 25.8155 | -121.1096 | 0.26303 | 0.39827 | 0.039761 | 0.17888 | -121.142
2412.8594 | 121.1472 | -0.15564 | 120.8496 | 1.4211e-13 | -0.028132 | 0.0019936 | 0.06905 | -0.013134 | 0.058898 | 0.00030522 | -0.0027303 | 0.0044868 | 0.017395 | 0.036423 | 0.0068005 | 0.86178 | 25.6828 | 0.2846 | 120.9948 | 120.9893 | 121.0491 | -0.2279 | 0.019362 | -0.013377 | -0.033458 | 0.066194 | 0.20601 | -0.15708 | -0.26488 | -0.072259 | 0.14521 | 1.0174 | 0.44024 | 0.5125 | 0.13967 | 0.19951 | -0.10924 | -120.7834 | 0.175 | 0.12218 | 0.23142 | -120.6436 | -121.0067 | 121.1505 | 121.1449 | 121.2048 | 25.8384 | -121.0775 | 0.22183 | 0.36165 | -0.001439 | 0.14226 | -121.1145
2414.625 | 121.1426 | -0.25177 | 120.7764 | 1.4211e-13 | -0.028346 | 0.0022072 | 0.069263 | -0.013134 | 0.058685 | 0.0079357 | -0.0033713 | 0.0044868 | 0.017395 | 0.036423 | 0.0063733 | 0.77022 | 25.7011 | 0.19304 | 120.9216 | 120.9023 | 120.9713 | -0.3149 | 0.023941 | -0.013377 | -0.047194 | 0.075351 | 0.21516 | -0.1525 | -0.26488 | -0.063128 | 0.1452 | 1.022 | 0.44481 | 0.50793 | 0.12592 | 0.19492 | -0.013113 | -120.701 | 0.27571 | 0.20458 | 0.21769 | -120.5612 | -120.9289 | 121.1733 | 121.1541 | 121.2231 | 25.9529 | -121.0913 | 0.32712 | 0.46693 | 0.09927 | 0.23839 | -121.0412
2416.375 | 121.0602 | -0.29755 | 120.8405 | 1.4211e-13 | -0.028346 | 0.002421 | 0.069263 | -0.012707 | 0.058685 | 0.015566 | -0.0029439 | 0.0051278 | 0.017182 | 0.036423 | 0.0068005 | 0.80227 | 25.7835 | 0.22966 | 120.9582 | 120.9389 | 121.0033 | -0.30116 | 0.033099 | -0.017956 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.2603 | -0.003615 | 0.11774 | 1.0998 | 0.52721 | 0.53082 | 0.09846 | 0.16288 | 0.037242 | -120.7697 | 0.33064 | 0.25951 | 0.22227 | -120.6299 | -120.993 | 121.2557 | 121.2365 | 121.3009 | 26.0811 | -121.1416 | 0.36832 | 0.50813 | 0.14505 | 0.27959 | -121.1008
2418.125 | 121.0693 | -0.31586 | 120.845 | 1.4211e-13 | -0.028346 | 0.0022072 | 0.06905 | -0.01292 | 0.058898 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017395 | 0.036423 | 0.0070143 | 0.82974 | 25.9255 | 0.22966 | 120.9674 | 120.9435 | 121.0079 | -0.3149 | 0.02852 | -0.017956 | -0.033458 | 0.052459 | 0.20143 | -0.1525 | -0.26488 | 0.000959 | 0.12232 | 1.1456 | 0.54552 | 0.54456 | 0.098461 | 0.16288 | 0.050974 | -120.7926 | 0.34438 | 0.2824 | 0.23142 | -120.6436 | -120.9975 | 121.2832 | 121.2593 | 121.3238 | 26.2413 | -121.1599 | 0.36832 | 0.51729 | 0.16336 | 0.2979 | -121.1099
2419.8125 | 121.1884 | -0.24261 | 120.845 | 1.4211e-13 | -0.028132 | 0.0019936 | 0.06905 | -0.013348 | 0.058898 | 0.0079357 | -0.0029439 | 0.0044868 | 0.017182 | 0.036423 | 0.0065869 | 0.84347 | 26.0262 | 0.23882 | 120.9857 | 120.9572 | 121.0217 | -0.31948 | 0.033099 | -0.017956 | -0.042615 | 0.070773 | 0.20601 | -0.16166 | -0.26946 | -0.076862 | 0.14063 | 1.0861 | 0.48143 | 0.55829 | 0.1122 | 0.17662 | -0.026847 | -120.7743 | 0.27571 | 0.2 | 0.22685 | -120.639 | -121.0067 | 121.2283 | 121.1998 | 121.2643 | 26.2688 | -121.1645 | 0.31339 | 0.44862 | 0.080957 | 0.22466 | -121.1145
2421.5625 | 120.3644 | -0.17395 | 120.1492 | 1.4211e-13 | -0.027705 | 0.0022072 | 0.068622 | -0.01292 | 0.058471 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017182 | 0.03685 | 0.0068005 | 0.9213 | 26.0124 | 0.33038 | 120.1936 | 120.1834 | 120.2387 | -0.25537 | 0.02852 | -0.027113 | -0.033458 | 0.070773 | 0.21059 | -0.1525 | -0.2603 | -0.081422 | 0.044373 | 1.0953 | 0.50433 | 0.58576 | 0.03416 | 0.089479 | -0.086354 | -120.0785 | 0.20247 | 0.14049 | 0.22685 | -119.9386 | -120.3017 | 120.3676 | 120.3573 | 120.4127 | 26.1864 | -120.4046 | 0.24472 | 0.38454 | 0.02145 | 0.14684 | -120.4095
2423.3125 | 120.5795 | -0.1831 | 120.4376 | 1.4211e-13 | -0.028346 | 0.0019936 | 0.068409 | -0.013134 | 0.058257 | 0.015566 | -0.0031575 | 0.0044868 | 0.017182 | 0.036636 | 0.0065869 | 0.96251 | 26.1819 | 0.37159 | 120.5278 | 120.5085 | 120.5775 | -0.23248 | 0.023941 | -0.013377 | -0.038036 | 0.07993 | 0.21059 | -0.1525 | -0.26488 | -0.049372 | 0.090204 | 1.1456 | 0.55469 | 0.60406 | 0.070873 | 0.1399 | -0.081778 | -120.3577 | 0.20705 | 0.14507 | 0.22685 | -120.227 | -120.5901 | 120.7109 | 120.6916 | 120.7606 | 26.365 | -120.6701 | 0.26304 | 0.39369 | 0.030605 | 0.16973 | -120.7025
2425.0625 | 120.6757 | -0.19684 | 120.5063 | 1.4211e-13 | -0.028559 | 0.002421 | 0.069263 | -0.01292 | 0.058471 | -0.0073253 | -0.0031575 | 0.0049142 | 0.017395 | 0.036636 | 0.0065869 | 0.98082 | 26.1223 | 0.35328 | 120.6331 | 120.6092 | 120.6783 | -0.2279 | 0.014784 | -0.013377 | -0.042615 | 0.075351 | 0.20601 | -0.1525 | -0.2603 | -0.031061 | 0.12684 | 1.1777 | 0.55011 | 0.58117 | 0.10294 | 0.17197 | -0.063466 | -120.4309 | 0.21162 | 0.15422 | 0.21769 | -120.3003 | -120.6588 | 120.83 | 120.8061 | 120.8751 | 26.3192 | -120.7342 | 0.27219 | 0.40285 | 0.044338 | 0.18346 | -120.7666
2426.7656 | 120.6894 | -0.21057 | 120.6024 | 1.4211e-13 | -0.028559 | 0.0022072 | 0.06905 | -0.01292 | 0.058898 | 0.00030522 | -0.0033713 | 0.0051278 | 0.017609 | 0.036636 | 0.0068005 | 1.0083 | 26.1132 | 0.35785 | 120.6835 | 120.6688 | 120.7286 | -0.22332 | 0.02852 | -0.017956 | -0.038036 | 0.07993 | 0.21516 | -0.14792 | -0.26488 | -0.012749 | 0.081074 | 1.2189 | 0.56842 | 0.58117 | 0.06634 | 0.1262 | -0.054312 | -120.5225 | 0.23909 | 0.17253 | 0.22685 | -120.3873 | -120.7503 | 120.8941 | 120.8793 | 120.9392 | 26.3237 | -120.8257 | 0.2905 | 0.42574 | 0.062649 | 0.19262 | -120.8673
2428.5312 | 120.7855 | -0.17853 | 120.6162 | 1.4211e-13 | -0.028559 | 0.0019936 | 0.068836 | -0.013134 | 0.058471 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017609 | 0.036423 | 0.0065869 | 1.0312 | 26.1178 | 0.36243 | 120.7293 | 120.7191 | 120.7836 | -0.22332 | 0.023941 | -0.022535 | -0.042615 | 0.075351 | 0.20143 | -0.15708 | -0.2603 | -0.044792 | 0.11312 | 1.2097 | 0.54096 | 0.58575 | 0.10298 | 0.16741 | -0.081776 | -120.5408 | 0.20247 | 0.13591 | 0.21769 | -120.4147 | -120.7732 | 120.9078 | 120.8977 | 120.9621 | 26.2963 | -120.8395 | 0.25388 | 0.37996 | 0.021449 | 0.15599 | -120.8765
2430.2812 | 120.9 | -0.16022 | 120.6619 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069263 | -0.013348 | 0.058898 | 0.015566 | -0.0031575 | 0.0044868 | 0.017182 | 0.036423 | 0.0065869 | 1.0541 | 26.191 | 0.38532 | 120.7705 | 120.7603 | 120.8248 | -0.22332 | 0.023941 | -0.013377 | -0.047194 | 0.075351 | 0.21059 | -0.1525 | -0.25572 | -0.063103 | 0.10855 | 1.2143 | 0.54554 | 0.60864 | 0.09841 | 0.16285 | -0.095508 | -120.5866 | 0.18416 | 0.11302 | 0.20853 | -120.4513 | -120.8144 | 120.9307 | 120.9206 | 120.985 | 26.3512 | -120.8852 | 0.23557 | 0.3708 | 0.007717 | 0.14684 | -120.9177
2431.9844 | 120.3049 | -0.20142 | 120.1675 | 1.4211e-13 | -0.028559 | 0.002421 | 0.068409 | -0.01292 | 0.058685 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017395 | 0.036636 | 0.0068005 | 1.0541 | 26.0628 | 0.39906 | 120.2394 | 120.22 | 120.2845 | -0.24163 | 0.033099 | -0.008798 | -0.033458 | 0.075351 | 0.21059 | -0.14792 | -0.26488 | -0.040219 | 0.071845 | 1.2555 | 0.60047 | 0.64069 | 0.052481 | 0.11695 | -0.063467 | -120.0922 | 0.23452 | 0.16796 | 0.23142 | -119.957 | -120.3155 | 120.4408 | 120.4214 | 120.4859 | 26.2642 | -120.4092 | 0.27677 | 0.412 | 0.053494 | 0.19262 | -120.4324
2433.6875 | 120.6619 | -0.15106 | 120.3964 | 1.4211e-13 | -0.028346 | 0.0022072 | 0.06905 | -0.012707 | 0.058685 | 0.0079357 | -0.0027303 | 0.0044868 | 0.017182 | 0.03685 | 0.0070143 | 1.0861 | 26.1681 | 0.39906 | 120.5095 | 120.4993 | 120.5638 | -0.2279 | 0.033099 | -0.017956 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.2603 | -0.076837 | 0.11309 | 1.2372 | 0.55012 | 0.62696 | 0.10291 | 0.16737 | -0.10924 | -120.3256 | 0.18416 | 0.10845 | 0.21769 | -120.1858 | -120.5489 | 120.6606 | 120.6504 | 120.7149 | 26.3192 | -120.6243 | 0.22184 | 0.36165 | -0.001438 | 0.13311 | -120.6567
2435.4375 | 120.7443 | -0.15106 | 120.4834 | 1.4211e-13 | -0.028559 | 0.0022072 | 0.06905 | -0.01292 | 0.058257 | -0.0073253 | -0.0031575 | 0.0047004 | 0.017182 | 0.036423 | 0.0065869 | 1.1136 | 26.1727 | 0.40821 | 120.6057 | 120.5955 | 120.6645 | -0.22332 | 0.02852 | -0.013377 | -0.038036 | 0.07993 | 0.21059 | -0.14334 | -0.26488 | -0.072258 | 0.12226 | 1.2647 | 0.55928 | 0.63153 | 0.1121 | 0.18112 | -0.11382 | -120.4035 | 0.17958 | 0.11303 | 0.22685 | -120.2728 | -120.6267 | 120.7567 | 120.7466 | 120.8156 | 26.3238 | -120.7067 | 0.23099 | 0.36165 | 0.007719 | 0.13769 | -120.7483
2437.1406 | 120.7443 | -0.16937 | 120.5338 | 1.4211e-13 | -0.028559 | 0.002421 | 0.068622 | -0.013134 | 0.058257 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017395 | 0.036636 | 0.0063733 | 1.1273 | 26.1956 | 0.42195 | 120.6652 | 120.655 | 120.7195 | -0.22332 | 0.02852 | -0.013377 | -0.042615 | 0.07993 | 0.21059 | -0.14792 | -0.2603 | -0.053947 | 0.13142 | 1.2967 | 0.59132 | 0.64527 | 0.12127 | 0.18571 | -0.090931 | -120.4538 | 0.19789 | 0.12676 | 0.21769 | -120.3232 | -120.6817 | 120.8345 | 120.8244 | 120.8888 | 26.365 | -120.7571 | 0.2493 | 0.37996 | 0.021451 | 0.156 | -120.7941
2438.9062 | 120.7123 | -0.1831 | 120.6116 | 1.4211e-13 | -0.028132 | 0.002421 | 0.069263 | -0.013134 | 0.058685 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017182 | 0.036636 | 0.0063733 | 1.1548 | 26.246 | 0.43568 | 120.7018 | 120.6962 | 120.7607 | -0.2279 | 0.02852 | -0.017956 | -0.038036 | 0.07993 | 0.20601 | -0.15708 | -0.25572 | -0.044794 | 0.090233 | 1.3379 | 0.61879 | 0.66358 | 0.084659 | 0.1491 | -0.07262 | -120.5316 | 0.21162 | 0.14507 | 0.21769 | -120.4056 | -120.7687 | 120.8849 | 120.8793 | 120.9438 | 26.4291 | -120.8395 | 0.26304 | 0.38911 | 0.026026 | 0.16515 | -120.8673
2440.6562 | 120.7443 | -0.20142 | 120.6116 | 1.4211e-13 | -0.028559 | 0.0022072 | 0.06905 | -0.01292 | 0.058685 | -0.0073253 | -0.0027303 | 0.0047004 | 0.017609 | 0.036423 | 0.0068005 | 1.1456 | 26.191 | 0.44026 | 120.7384 | 120.7283 | 120.7881 | -0.22332 | 0.023941 | -0.017956 | -0.042615 | 0.084508 | 0.20601 | -0.14792 | -0.26488 | -0.021904 | 0.12686 | 1.3471 | 0.64168 | 0.66358 | 0.11671 | 0.17657 | -0.063467 | -120.5271 | 0.22536 | 0.1588 | 0.22227 | -120.4056 | -120.7595 | 120.9398 | 120.9297 | 120.9896 | 26.3924 | -120.8349 | 0.28592 | 0.40742 | 0.053494 | 0.18346 | -120.8765
2442.4062 | 120.8038 | -0.20599 | 120.6436 | 1.4211e-13 | -0.028773 | 0.0026346 | 0.068836 | -0.012707 | 0.058898 | 0.015566 | -0.0031575 | 0.0042732 | 0.017609 | 0.036209 | 0.0065869 | 1.164 | 26.1544 | 0.46315 | 120.7705 | 120.7558 | 120.8248 | -0.21874 | 0.023941 | -0.013377 | -0.047194 | 0.07993 | 0.20601 | -0.1525 | -0.2603 | -0.012747 | 0.12686 | 1.37 | 0.66915 | 0.6819 | 0.11214 | 0.18116 | -0.05431 | -120.5637 | 0.22994 | 0.1588 | 0.21311 | -120.4376 | -120.7961 | 120.9765 | 120.9618 | 121.0308 | 26.3604 | -120.8624 | 0.28592 | 0.412 | 0.053494 | 0.19262 | -120.9039
2444.1719 | 120.9091 | -0.15564 | 120.694 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.06905 | -0.013134 | 0.058685 | 0.0079357 | -0.0033713 | 0.0049142 | 0.017182 | 0.036209 | 0.0065869 | 1.1868 | 26.2185 | 0.47689 | 120.7888 | 120.7878 | 120.8431 | -0.22332 | 0.023941 | -0.013377 | -0.042615 | 0.07993 | 0.21059 | -0.14792 | -0.2603 | -0.06768 | 0.094824 | 1.3425 | 0.63253 | 0.70021 | 0.093839 | 0.14912 | -0.10466 | -120.614 | 0.17958 | 0.11303 | 0.21769 | -120.4834 | -120.8419 | 120.9444 | 120.9434 | 120.9987 | 26.3741 | -120.9173 | 0.23557 | 0.36623 | 0.007718 | 0.14226 | -120.9543
2445.8594 | 120.8267 | -0.21515 | 120.7352 | 1.4211e-13 | -0.028559 | 0.002421 | 0.069263 | -0.01292 | 0.058898 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017609 | 0.036209 | 0.0065869 | 1.2143 | 26.3421 | 0.48147 | 120.8163 | 120.8015 | 120.866 | -0.23248 | 0.023941 | -0.017956 | -0.042615 | 0.070773 | 0.20601 | -0.13876 | -0.26488 | -0.017328 | 0.081096 | 1.4295 | 0.69662 | 0.71394 | 0.066378 | 0.13081 | -0.049734 | -120.6644 | 0.23909 | 0.17253 | 0.22227 | -120.5292 | -120.8739 | 121.0314 | 121.0167 | 121.0811 | 26.5573 | -120.9676 | 0.28592 | 0.42116 | 0.076384 | 0.19719 | -121.0001
2447.5469 | 120.9595 | -0.16937 | 120.694 | 1.4211e-13 | -0.028346 | 0.0022072 | 0.06905 | -0.012707 | 0.058898 | 0.015566 | -0.0029439 | 0.0049142 | 0.017182 | 0.036423 | 0.0065869 | 1.2372 | 26.3513 | 0.49978 | 120.8346 | 120.8244 | 120.8889 | -0.23248 | 0.019362 | -0.017956 | -0.047194 | 0.084508 | 0.20601 | -0.16166 | -0.2603 | -0.063104 | 0.14061 | 1.4066 | 0.66915 | 0.73226 | 0.13047 | 0.1949 | -0.090931 | -120.6095 | 0.18873 | 0.12218 | 0.21311 | -120.488 | -120.8556 | 121.004 | 120.9938 | 121.0582 | 26.5206 | -120.9264 | 0.25388 | 0.37538 | 0.007715 | 0.15142 | -120.9543
2449.25 | 120.9183 | -0.18768 | 120.7581 | 1.4211e-13 | -0.028346 | 0.002421 | 0.068836 | -0.012707 | 0.058898 | 0.015566 | -0.0031575 | 0.0047004 | 0.017395 | 0.036636 | 0.0065869 | 1.2601 | 26.3742 | 0.50894 | 120.862 | 120.8428 | 120.9072 | -0.2279 | 0.02852 | -0.013377 | -0.033458 | 0.07993 | 0.21059 | -0.1525 | -0.2603 | -0.040216 | 0.10399 | 1.4478 | 0.69662 | 0.73684 | 0.0847 | 0.14913 | -0.072621 | -120.6781 | 0.2162 | 0.15423 | 0.22685 | -120.5475 | -120.9106 | 121.0497 | 121.0304 | 121.0949 | 26.5618 | -120.986 | 0.26761 | 0.39827 | 0.035183 | 0.17431 | -121.0184
2451 | 120.9641 | -0.16022 | 120.726 | 1.4211e-13 | -0.028559 | 0.0022072 | 0.069477 | -0.013348 | 0.059326 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017395 | 0.036423 | 0.0068005 | 1.283 | 26.3513 | 0.51352 | 120.8758 | 120.8702 | 120.9301 | -0.2279 | 0.023941 | -0.017956 | -0.042615 | 0.07993 | 0.21059 | -0.1525 | -0.25572 | -0.067682 | 0.14977 | 1.4432 | 0.67373 | 0.74141 | 0.14422 | 0.20407 | -0.095508 | -120.6461 | 0.18416 | 0.1176 | 0.21311 | -120.5154 | -120.8785 | 121.036 | 121.0304 | 121.0903 | 26.5115 | -120.9539 | 0.24015 | 0.3708 | 0.007717 | 0.14226 | -120.9817
2452.75 | 120.932 | -0.21515 | 120.7993 | 1.4211e-13 | -0.028346 | 0.002421 | 0.069263 | -0.012707 | 0.058898 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017395 | 0.036209 | 0.0068005 | 1.315 | 26.4016 | 0.53641 | 120.8895 | 120.8794 | 120.9484 | -0.21874 | 0.02852 | -0.017956 | -0.042615 | 0.075351 | 0.20143 | -0.1525 | -0.2603 | -0.003592 | 0.090263 | 1.5302 | 0.75156 | 0.75515 | 0.080133 | 0.14914 | -0.045155 | -120.7239 | 0.24367 | 0.17253 | 0.21769 | -120.5978 | -120.9518 | 121.1047 | 121.0945 | 121.1635 | 26.6168 | -121.018 | 0.2905 | 0.41658 | 0.062649 | 0.19719 | -121.0596
2454.5156 | 120.8908 | -0.19684 | 120.813 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069263 | -0.012707 | 0.058898 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017182 | 0.036423 | 0.0065869 | 1.3471 | 26.3696 | 0.54556 | 120.917 | 120.8931 | 120.9576 | -0.22332 | 0.02852 | -0.017956 | -0.042615 | 0.07993 | 0.21516 | -0.1525 | -0.2603 | -0.026482 | 0.104 | 1.5439 | 0.7424 | 0.76888 | 0.080137 | 0.14456 | -0.063466 | -120.7331 | 0.22536 | 0.15422 | 0.21769 | -120.5978 | -120.9655 | 121.1138 | 121.09 | 121.1544 | 26.5664 | -121.0363 | 0.27677 | 0.412 | 0.044338 | 0.17888 | -121.0733
2456.2812 | 120.9091 | -0.20599 | 120.8267 | 1.4211e-13 | -0.028346 | 0.002421 | 0.069477 | -0.01292 | 0.059112 | 0.015566 | -0.0033713 | 0.0049142 | 0.017609 | 0.036636 | 0.0065869 | 1.3654 | 26.365 | 0.56388 | 120.9261 | 120.9114 | 120.9759 | -0.22332 | 0.033099 | -0.013377 | -0.042615 | 0.07993 | 0.21059 | -0.15708 | -0.26488 | -0.017326 | 0.099425 | 1.5714 | 0.76987 | 0.7872 | 0.084719 | 0.14914 | -0.058889 | -120.7468 | 0.23909 | 0.16338 | 0.22227 | -120.6161 | -120.9838 | 121.1321 | 121.1174 | 121.1819 | 26.571 | -121.05 | 0.28592 | 0.41658 | 0.048915 | 0.19262 | -121.0916
2457.9688 | 121.0327 | -0.16937 | 120.813 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069477 | -0.013348 | 0.058898 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017395 | 0.036423 | 0.0065869 | 1.402 | 26.3238 | 0.58219 | 120.9353 | 120.9298 | 120.9942 | -0.22332 | 0.02852 | -0.022535 | -0.038036 | 0.07993 | 0.21059 | -0.1525 | -0.26488 | -0.053947 | 0.12231 | 1.5714 | 0.75156 | 0.80551 | 0.11677 | 0.18119 | -0.09551 | -120.7331 | 0.19789 | 0.13134 | 0.22685 | -120.6024 | -120.9655 | 121.1047 | 121.0991 | 121.1636 | 26.4932 | -121.0363 | 0.2493 | 0.37996 | 0.016873 | 0.14684 | -121.0779
2459.6719 | 121.0327 | -0.16479 | 120.8313 | 1.4211e-13 | -0.028346 | 0.0019936 | 0.069263 | -0.01292 | 0.058898 | 0.0079357 | -0.0029439 | 0.0044868 | 0.017395 | 0.036636 | 0.0063733 | 1.4249 | 26.2688 | 0.59592 | 120.949 | 120.9435 | 121.0079 | -0.22332 | 0.023941 | -0.017956 | -0.047194 | 0.070773 | 0.21516 | -0.15708 | -0.2603 | -0.058525 | 0.11774 | 1.5897 | 0.76072 | 0.81924 | 0.11219 | 0.17662 | -0.095509 | -120.7605 | 0.18874 | 0.1176 | 0.21311 | -120.6161 | -120.9884 | 121.1138 | 121.1083 | 121.1727 | 26.4336 | -121.0546 | 0.23557 | 0.37996 | 0.007716 | 0.14684 | -121.0916
2461.4219 | 120.9641 | -0.20142 | 120.8496 | 1.4211e-13 | -0.028773 | 0.0026346 | 0.06905 | -0.013134 | 0.059539 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016968 | 0.036423 | 0.0065869 | 1.457 | 26.2551 | 0.60966 | 120.9674 | 120.9481 | 121.0262 | -0.2279 | 0.02852 | -0.013377 | -0.042615 | 0.07993 | 0.20601 | -0.14334 | -0.2603 | -0.026483 | 0.11774 | 1.6584 | 0.81107 | 0.83756 | 0.098463 | 0.17662 | -0.058888 | -120.7697 | 0.22994 | 0.1588 | 0.21769 | -120.6436 | -120.993 | 121.1688 | 121.1495 | 121.2276 | 26.4565 | -121.0775 | 0.28135 | 0.40742 | 0.058073 | 0.18804 | -121.1099
2463.1094 | 121.0968 | -0.16022 | 120.8679 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069477 | -0.012707 | 0.059326 | 0.015566 | -0.0033713 | 0.0049142 | 0.017395 | 0.036423 | 0.0065869 | 1.4844 | 26.2917 | 0.62339 | 120.9811 | 120.971 | 121.0308 | -0.22332 | 0.023941 | -0.013377 | -0.047194 | 0.075351 | 0.20601 | -0.1525 | -0.26488 | -0.063103 | 0.11317 | 1.6447 | 0.78361 | 0.84671 | 0.10305 | 0.16289 | -0.10467 | -120.7926 | 0.18416 | 0.11302 | 0.21769 | -120.6619 | -121.0204 | 121.1413 | 121.1312 | 121.191 | 26.452 | -121.0912 | 0.23557 | 0.36623 | 0.007717 | 0.14684 | -121.1328
2464.8125 | 120.9915 | -0.18768 | 120.8954 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069477 | -0.012707 | 0.059326 | 0.00030522 | -0.0031575 | 0.0051278 | 0.017395 | 0.036636 | 0.0065869 | 1.5119 | 26.3787 | 0.64628 | 120.9902 | 120.9755 | 121.0445 | -0.22332 | 0.019362 | -0.022535 | -0.038036 | 0.075351 | 0.21059 | -0.15708 | -0.26488 | -0.035637 | 0.094857 | 1.6996 | 0.83397 | 0.8696 | 0.080159 | 0.14916 | -0.0772 | -120.82 | 0.20704 | 0.14965 | 0.22685 | -120.6848 | -121.0525 | 121.1779 | 121.1632 | 121.2322 | 26.5664 | -121.1187 | 0.26303 | 0.39827 | 0.030604 | 0.16515 | -121.1603
2466.5781 | 120.9961 | -0.17853 | 120.8954 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069263 | -0.012707 | 0.059112 | -0.0073253 | -0.0029439 | 0.0049142 | 0.017395 | 0.036423 | 0.0068005 | 1.5302 | 26.3513 | 0.65086 | 121.004 | 120.9893 | 121.0674 | -0.22332 | 0.023941 | -0.013377 | -0.038036 | 0.075351 | 0.21516 | -0.1525 | -0.2603 | -0.044792 | 0.10859 | 1.7088 | 0.82939 | 0.87418 | 0.093896 | 0.17205 | -0.081776 | -120.82 | 0.20247 | 0.14049 | 0.22227 | -120.6802 | -121.0479 | 121.1825 | 121.1678 | 121.246 | 26.5298 | -121.1187 | 0.25388 | 0.39369 | 0.026028 | 0.16515 | -121.1557
2468.3281 | 121.106 | -0.16479 | 120.8862 | 1.4211e-13 | -0.028773 | 0.002421 | 0.069691 | -0.012707 | 0.059112 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017609 | 0.03685 | 0.0063733 | 1.5669 | 26.3375 | 0.66918 | 121.0223 | 121.0076 | 121.0812 | -0.22332 | 0.02852 | -0.008798 | -0.038036 | 0.07993 | 0.20601 | -0.12045 | -0.26488 | -0.058525 | 0.13606 | 1.7317 | 0.83397 | 0.8925 | 0.12137 | 0.19494 | -0.10009 | -120.8063 | 0.19331 | 0.12676 | 0.22685 | -120.6802 | -121.0067 | 121.1871 | 121.1724 | 121.246 | 26.5023 | -121.1095 | 0.24472 | 0.3708 | 0.044345 | 0.156 | -121.1511
2470.0156 | 121.0556 | -0.19226 | 120.9457 | 1.4211e-13 | -0.028559 | 0.0022072 | 0.069263 | -0.012707 | 0.059967 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017395 | 0.03685 | 0.0070143 | 1.5806 | 26.2826 | 0.68291 | 121.0269 | 121.0259 | 121.0812 | -0.2279 | 0.02852 | -0.017956 | -0.047194 | 0.070773 | 0.21059 | -0.1525 | -0.25115 | -0.035638 | 0.08113 | 1.7729 | 0.87517 | 0.91081 | 0.080174 | 0.13543 | -0.058885 | -120.875 | 0.22078 | 0.14507 | 0.20395 | -120.7352 | -121.0982 | 121.2191 | 121.2182 | 121.2734 | 26.4748 | -121.1736 | 0.26303 | 0.40285 | 0.039761 | 0.1743 | -121.1969
2471.7656 | 121.0693 | -0.17853 | 120.9366 | 1.4211e-13 | -0.028559 | 0.002421 | 0.069691 | -0.01292 | 0.059112 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017395 | 0.036636 | 0.0065869 | 1.6081 | 26.3284 | 0.69207 | 121.0314 | 121.0305 | 121.0995 | -0.2279 | 0.02852 | -0.013377 | -0.033458 | 0.075351 | 0.21059 | -0.14334 | -0.25572 | -0.049371 | 0.094865 | 1.7866 | 0.8706 | 0.91997 | 0.093908 | 0.1629 | -0.077197 | -120.8612 | 0.20705 | 0.14507 | 0.22227 | -120.726 | -121.0799 | 121.21 | 121.209 | 121.278 | 26.5069 | -121.1645 | 0.25388 | 0.38911 | 0.035185 | 0.16515 | -121.1923
2473.5156 | 121.0281 | -0.21973 | 120.9503 | 1.4211e-13 | -0.028559 | 0.0028484 | 0.069691 | -0.012707 | 0.059326 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017395 | 0.036423 | 0.0065869 | 1.6447 | 26.5161 | 0.71954 | 121.0498 | 121.0442 | 121.1041 | -0.22332 | 0.02852 | -0.008798 | -0.033458 | 0.084508 | 0.20601 | -0.060928 | -0.26488 | -0.003593 | 0.099445 | 1.8644 | 0.93926 | 0.94286 | 0.093912 | 0.15375 | -0.045156 | -120.8658 | 0.24825 | 0.18627 | 0.23142 | -120.7443 | -121.0112 | 121.2695 | 121.264 | 121.3238 | 26.7358 | -121.1736 | 0.30424 | 0.42573 | 0.1588 | 0.21093 | -121.2152
2475.2656 | 121.106 | -0.20142 | 120.9503 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069263 | -0.013134 | 0.059539 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017609 | 0.036636 | 0.0068005 | 1.6584 | 26.6351 | 0.72869 | 121.0543 | 121.058 | 121.127 | -0.22332 | 0.02852 | -0.013377 | -0.038036 | 0.07993 | 0.21059 | -0.11587 | -0.2603 | -0.021904 | 0.10402 | 1.8598 | 0.93011 | 0.95201 | 0.10765 | 0.17664 | -0.058888 | -120.8704 | 0.22994 | 0.16338 | 0.22227 | -120.7397 | -121.0662 | 121.2558 | 121.2594 | 121.3284 | 26.8366 | -121.1736 | 0.28135 | 0.412 | 0.085544 | 0.18804 | -121.2106
2477.0156 | 121.0693 | -0.21057 | 120.9686 | 1.4211e-13 | -0.028773 | 0.002421 | 0.070118 | -0.013134 | 0.059326 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.036636 | 0.0063733 | 1.6813 | 26.6535 | 0.74243 | 121.0727 | 121.0717 | 121.1361 | -0.22332 | 0.023941 | -0.022535 | -0.038036 | 0.084508 | 0.21059 | -0.070086 | -0.2603 | -0.012749 | 0.10403 | 1.8919 | 0.953 | 0.96575 | 0.10308 | 0.16749 | -0.049733 | -120.8841 | 0.23451 | 0.17253 | 0.22227 | -120.758 | -121.0387 | 121.2832 | 121.2823 | 121.3467 | 26.864 | -121.1919 | 0.29508 | 0.42116 | 0.14049 | 0.18804 | -121.2289
2478.7188 | 121.0785 | -0.19684 | 120.9869 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069263 | -0.012707 | 0.059112 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017182 | 0.036423 | 0.0065869 | 1.7042 | 26.7771 | 0.76074 | 121.0818 | 121.0717 | 121.1407 | -0.22332 | 0.023941 | -0.008798 | -0.038036 | 0.075351 | 0.21059 | -0.074664 | -0.26488 | -0.026482 | 0.094873 | 1.901 | 0.95758 | 0.98406 | 0.084765 | 0.15376 | -0.068045 | -120.9116 | 0.22078 | 0.1588 | 0.22685 | -120.7764 | -121.0616 | 121.2786 | 121.2685 | 121.3375 | 26.9739 | -121.2103 | 0.27219 | 0.40742 | 0.12217 | 0.18804 | -121.2518
2480.4688 | 121.106 | -0.23346 | 121.0098 | 1.4211e-13 | -0.028773 | 0.0028484 | 0.069691 | -0.013134 | 0.059326 | -0.0073253 | -0.0033713 | 0.0051278 | 0.017395 | 0.036423 | 0.0068005 | 1.7363 | 26.8961 | 0.77906 | 121.091 | 121.09 | 121.1544 | -0.22332 | 0.023941 | -0.013377 | -0.038036 | 0.07993 | 0.20601 | -0.0884 | -0.2603 | 0.010139 | 0.081141 | 1.9697 | 1.0125 | 1.0024 | 0.080191 | 0.1446 | -0.026845 | -120.9299 | 0.2574 | 0.19542 | 0.22227 | -120.8038 | -121.0982 | 121.3244 | 121.3235 | 121.3879 | 27.1296 | -121.2331 | 0.31339 | 0.43947 | 0.14506 | 0.22008 | -121.2701
2482.1562 | 121.2021 | -0.16479 | 120.9824 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069691 | -0.01292 | 0.059539 | 0.00030522 | -0.0033713 | 0.0049142 | 0.017395 | 0.036636 | 0.0065869 | 1.7637 | 26.9236 | 0.78821 | 121.1093 | 121.0946 | 121.1636 | -0.22332 | 0.023941 | -0.013377 | -0.038036 | 0.070773 | 0.20601 | -0.074664 | -0.26488 | -0.058525 | 0.12692 | 1.9285 | 0.95301 | 1.0115 | 0.11224 | 0.18123 | -0.10009 | -120.9116 | 0.18874 | 0.12676 | 0.22685 | -120.7764 | -121.057 | 121.2741 | 121.2594 | 121.3284 | 27.0884 | -121.2057 | 0.23557 | 0.3708 | 0.090131 | 0.15142 | -121.2472
2483.9219 | 121.2341 | -0.15106 | 120.9732 | 1.4211e-13 | -0.028559 | 0.0028484 | 0.069691 | -0.013134 | 0.059326 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017182 | 0.036423 | 0.0068005 | 1.7912 | 27.0014 | 0.80653 | 121.1093 | 121.1129 | 121.1819 | -0.22332 | 0.023941 | -0.013377 | -0.033458 | 0.07993 | 0.21059 | -0.1525 | -0.26946 | -0.072258 | 0.13607 | 1.9423 | 0.95759 | 1.0298 | 0.13971 | 0.2087 | -0.1184 | -120.8933 | 0.175 | 0.1176 | 0.236 | -120.7626 | -121.1257 | 121.2603 | 121.264 | 121.333 | 27.1525 | -121.1965 | 0.23099 | 0.36165 | -0.001438 | 0.13769 | -121.2427
2485.6875 | 121.2296 | -0.16022 | 120.9961 | 1.4211e-13 | -0.028346 | 0.0022072 | 0.069904 | -0.012707 | 0.059539 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017182 | 0.03685 | 0.0065869 | 1.8187 | 27.0609 | 0.82026 | 121.1184 | 121.1175 | 121.1865 | -0.21416 | 0.02852 | -0.008798 | -0.033458 | 0.07993 | 0.20601 | -0.11129 | -0.25572 | -0.053945 | 0.12234 | 1.9789 | 0.98048 | 1.0344 | 0.1214 | 0.19039 | -0.095508 | -120.9162 | 0.18874 | 0.12676 | 0.22227 | -120.7901 | -121.1074 | 121.2787 | 121.2777 | 121.3467 | 27.2212 | -121.2103 | 0.24015 | 0.36623 | 0.048924 | 0.15142 | -121.2518
2487.4375 | 121.17 | -0.16937 | 121.0236 | 1.4211e-13 | -0.028132 | 0.0028484 | 0.069904 | -0.01292 | 0.059326 | 0.015566 | -0.0031575 | 0.0049142 | 0.017182 | 0.03685 | 0.0068005 | 1.8278 | 26.974 | 0.83857 | 121.1368 | 121.1312 | 121.1865 | -0.22332 | 0.02852 | -0.008798 | -0.038036 | 0.075351 | 0.20601 | -0.14334 | -0.2603 | -0.053947 | 0.11319 | 1.9972 | 1.0079 | 1.0619 | 0.10767 | 0.16292 | -0.090931 | -120.9482 | 0.19789 | 0.13134 | 0.22227 | -120.8176 | -121.1669 | 121.3061 | 121.3006 | 121.3559 | 27.1433 | -121.2469 | 0.24472 | 0.37538 | 0.02603 | 0.16057 | -121.2839
2489.1406 | 121.2616 | -0.15564 | 121.0098 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069691 | -0.012707 | 0.059539 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017182 | 0.03685 | 0.0065869 | 1.8599 | 27.1296 | 0.85689 | 121.1413 | 121.1404 | 121.2048 | -0.21874 | 0.023941 | -0.013377 | -0.042615 | 0.075351 | 0.21516 | -0.1525 | -0.2603 | -0.063101 | 0.1315 | 2.0155 | 1.0125 | 1.0756 | 0.13056 | 0.19497 | -0.10466 | -120.9345 | 0.17958 | 0.11303 | 0.21769 | -120.7947 | -121.1623 | 121.297 | 121.296 | 121.3604 | 27.2853 | -121.2286 | 0.23099 | 0.3708 | 0.00314 | 0.14226 | -121.2701
2490.8438 | 121.257 | -0.16479 | 121.0327 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.070118 | -0.012707 | 0.059753 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017182 | 0.036636 | 0.0068005 | 1.8828 | 27.2487 | 0.87062 | 121.1551 | 121.1495 | 121.2185 | -0.22332 | 0.033099 | -0.017956 | -0.047194 | 0.07993 | 0.20601 | -0.12961 | -0.26488 | -0.058525 | 0.12235 | 2.0476 | 1.0354 | 1.0939 | 0.11683 | 0.18582 | -0.10009 | -120.9528 | 0.19789 | 0.1176 | 0.21769 | -120.8267 | -121.1623 | 121.3199 | 121.3143 | 121.3833 | 27.4135 | -121.256 | 0.24472 | 0.3708 | 0.035188 | 0.14684 | -121.2976
2492.5938 | 121.2433 | -0.16022 | 121.019 | 1.4211e-13 | -0.028559 | 0.0028484 | 0.069691 | -0.012493 | 0.059539 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017609 | 0.036636 | 0.0065869 | 1.924 | 27.4181 | 0.88436 | 121.1642 | 121.1495 | 121.2277 | -0.21416 | 0.023941 | -0.017956 | -0.038036 | 0.084508 | 0.20601 | -0.12961 | -0.26946 | -0.053945 | 0.14524 | 2.0842 | 1.0446 | 1.0985 | 0.13056 | 0.20871 | -0.10924 | -120.9345 | 0.18416 | 0.12218 | 0.23143 | -120.813 | -121.1486 | 121.3244 | 121.3098 | 121.3879 | 27.5783 | -121.2331 | 0.24472 | 0.36623 | 0.03061 | 0.14226 | -121.2884
2494.3438 | 121.225 | -0.16479 | 121.0327 | 1.4211e-13 | -0.028132 | 0.002421 | 0.069691 | -0.012707 | 0.059539 | 0.015566 | -0.0031575 | 0.0044868 | 0.017182 | 0.036636 | 0.0070143 | 1.9469 | 27.4639 | 0.90725 | 121.1734 | 121.1679 | 121.2414 | -0.21874 | 0.02852 | -0.017956 | -0.038036 | 0.070773 | 0.20143 | -0.11587 | -0.26488 | -0.053946 | 0.14066 | 2.1117 | 1.072 | 1.126 | 0.13515 | 0.20871 | -0.10009 | -120.9619 | 0.19331 | 0.12676 | 0.22685 | -120.8313 | -121.1486 | 121.3382 | 121.3327 | 121.4062 | 27.6287 | -121.2515 | 0.23557 | 0.36622 | 0.048923 | 0.14684 | -121.2976
2496.0938 | 121.1563 | -0.21515 | 121.0739 | 1.4211e-13 | -0.028559 | 0.0028484 | 0.069904 | -0.01292 | 0.059539 | 0.00030522 | -0.0033713 | 0.0042732 | 0.017182 | 0.03685 | 0.0065869 | 1.9835 | 27.6104 | 0.92556 | 121.1825 | 121.177 | 121.2506 | -0.21416 | 0.033099 | -0.017956 | -0.042615 | 0.075351 | 0.20143 | -0.11587 | -0.26946 | 0.000987 | 0.10862 | 2.1986 | 1.1407 | 1.1397 | 0.1031 | 0.17667 | -0.054313 | -120.9986 | 0.24825 | 0.17253 | 0.22685 | -120.8725 | -121.1898 | 121.3977 | 121.3922 | 121.4657 | 27.8255 | -121.2881 | 0.2905 | 0.41658 | 0.099277 | 0.19719 | -121.3434
2497.7969 | 121.17 | -0.21057 | 121.106 | 1.4211e-13 | -0.028346 | 0.0026346 | 0.069691 | -0.012707 | 0.059539 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017395 | 0.036423 | 0.0065869 | 2.0201 | 27.7935 | 0.93472 | 121.1871 | 121.1816 | 121.2552 | -0.21874 | 0.037677 | -0.013377 | -0.042615 | 0.075351 | 0.20601 | -0.12045 | -0.2603 | -0.00817 | 0.081157 | 2.2307 | 1.1453 | 1.1535 | 0.07564 | 0.1492 | -0.049733 | -121.0306 | 0.24825 | 0.16796 | 0.21769 | -120.8999 | -121.2264 | 121.3977 | 121.3922 | 121.4657 | 28.0041 | -121.3247 | 0.28592 | 0.41658 | 0.090121 | 0.19719 | -121.3663
2499.5625 | 121.3028 | -0.14191 | 121.0648 | 1.4211e-13 | -0.028132 | 0.0026346 | 0.069904 | -0.012707 | 0.059967 | -0.0073253 | -0.0031575 | 0.0044868 | 0.017182 | 0.037064 | 0.0063733 | 2.0384 | 27.6516 | 0.95761 | 121.2008 | 121.1908 | 121.2597 | -0.21416 | 0.023941 | -0.017956 | -0.042615 | 0.07993 | 0.20601 | -0.12503 | -0.26488 | -0.072255 | 0.13609 | 2.1803 | 1.0995 | 1.1718 | 0.126 | 0.19498 | -0.12298 | -120.9848 | 0.16585 | 0.099292 | 0.22227 | -120.8588 | -121.1898 | 121.3428 | 121.3327 | 121.4016 | 27.7935 | -121.2789 | 0.22184 | 0.34791 | 0.016878 | 0.12395 | -121.3296
2501.25 | 121.1884 | -0.21057 | 121.1151 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069691 | -0.012707 | 0.059753 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017395 | 0.03685 | 0.0065869 | 2.0796 | 27.7889 | 0.97134 | 121.2146 | 121.1999 | 121.2781 | -0.21416 | 0.02852 | -0.008798 | -0.042615 | 0.07993 | 0.20601 | -0.12961 | -0.2603 | -0.003591 | 0.099472 | 2.2902 | 1.1819 | 1.1855 | 0.084801 | 0.16294 | -0.049733 | -121.0352 | 0.23909 | 0.16796 | 0.21769 | -120.9091 | -121.2447 | 121.4252 | 121.4105 | 121.4886 | 27.9995 | -121.3293 | 0.2905 | 0.41658 | 0.080964 | 0.20177 | -121.3754
2502.9375 | 121.2433 | -0.20142 | 121.106 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069477 | -0.013134 | 0.059539 | -0.0073253 | -0.0033713 | 0.0042732 | 0.017182 | 0.036636 | 0.0063733 | 2.0934 | 27.8393 | 0.98966 | 121.2192 | 121.2045 | 121.2781 | -0.22332 | 0.033099 | -0.008798 | -0.038036 | 0.075351 | 0.20143 | -0.12503 | -0.26488 | -0.021904 | 0.1132 | 2.2948 | 1.1911 | 1.213 | 0.098535 | 0.1721 | -0.063467 | -121.0306 | 0.23452 | 0.16338 | 0.22685 | -120.9045 | -121.231 | 121.4206 | 121.4059 | 121.4795 | 28.0407 | -121.3293 | 0.27677 | 0.40285 | 0.076387 | 0.19262 | -121.3708
2504.6875 | 121.3165 | -0.1831 | 121.1014 | 1.4211e-13 | -0.028559 | 0.0026346 | 0.069691 | -0.012279 | 0.059967 | 0.00030522 | -0.0029439 | 0.0051278 | 0.017182 | 0.03685 | 0.0068005 | 2.13 | 28.0499 | 1.0034 | 121.2237 | 121.2182 | 121.2918 | -0.21416 | 0.023941 | -0.00422 | -0.042615 | 0.07993 | 0.21059 | -0.14792 | -0.2603 | -0.031057 | 0.12236 | 2.3131 | 1.1865 | 1.2176 | 0.11685 | 0.19041 | -0.077199 | -121.0214 | 0.20705 | 0.14049 | 0.21769 | -120.8908 | -121.2493 | 121.4068 | 121.4013 | 121.4749 | 28.233 | -121.3155 | 0.26304 | 0.39369 | 0.035183 | 0.17888 | -121.3617
2506.4375 | 121.2021 | -0.20142 | 121.1426 | 1.4211e-13 | -0.028132 | 0.0026346 | 0.069904 | -0.012707 | 0.059967 | 0.015566 | -0.0031575 | 0.0047004 | 0.017609 | 0.036636 | 0.0065869 | 2.1804 | 28.1598 | 1.0125 | 121.2283 | 121.2365 | 121.2918 | -0.20958 | 0.02852 | -0.008798 | -0.042615 | 0.070773 | 0.20601 | -0.11587 | -0.26488 | -0.008167 | 0.085741 | 2.3818 | 1.214 | 1.2221 | 0.093966 | 0.14921 | -0.063467 | -121.0718 | 0.22994 | 0.1588 | 0.22227 | -120.9366 | -121.2584 | 121.4297 | 121.438 | 121.4932 | 28.3612 | -121.3522 | 0.27219 | 0.40742 | 0.085544 | 0.19262 | -121.4075
2508.125 | 121.3028 | -0.16022 | 121.0876 | 1.4211e-13 | -0.028559 | 0.0028484 | 0.069904 | -0.012279 | 0.059967 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017395 | 0.03685 | 0.0063733 | 2.2261 | 28.2193 | 1.0263 | 121.2375 | 121.2365 | 121.2964 | -0.21874 | 0.02852 | -0.013377 | -0.038036 | 0.07993 | 0.20601 | -0.12503 | -0.2603 | -0.058524 | 0.14983 | 2.3864 | 1.1865 | 1.245 | 0.1489 | 0.20872 | -0.10009 | -121.0077 | 0.18874 | 0.12218 | 0.22227 | -120.8816 | -121.2127 | 121.3977 | 121.3968 | 121.4566 | 28.3796 | -121.3064 | 0.24015 | 0.36623 | 0.035188 | 0.14684 | -121.348
2509.8125 | 121.3852 | -0.16479 | 121.0876 | 1.4211e-13 | -0.028346 | 0.003062 | 0.069477 | -0.012493 | 0.059967 | 0.00030522 | -0.0035849 | 0.0044868 | 0.017182 | 0.036636 | 0.0065869 | 2.2719 | 28.2193 | 1.0538 | 121.2466 | 121.2457 | 121.3147 | -0.21416 | 0.02852 | -0.008798 | -0.038036 | 0.070773 | 0.19685 | -0.1525 | -0.26488 | -0.049367 | 0.15899 | 2.4367 | 1.2185 | 1.2679 | 0.15806 | 0.22704 | -0.10009 | -121.0169 | 0.19331 | 0.12676 | 0.22685 | -120.8908 | -121.2401 | 121.4114 | 121.4105 | 121.4795 | 28.3841 | -121.3018 | 0.23557 | 0.36165 | 0.012295 | 0.156 | -121.3525
2511.5625 | 121.2616 | -0.21515 | 121.1517 | 1.4211e-13 | -0.028559 | 0.0028484 | 0.069904 | -0.01292 | 0.06018 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017395 | 0.03685 | 0.0068005 | 2.3177 | 28.3613 | 1.0721 | 121.2604 | 121.2503 | 121.3238 | -0.22332 | 0.02852 | -0.017956 | -0.038036 | 0.075351 | 0.20601 | -0.1525 | -0.26488 | -0.008171 | 0.10864 | 2.5329 | 1.2872 | 1.2954 | 0.098548 | 0.17211 | -0.049734 | -121.0764 | 0.24367 | 0.17711 | 0.22685 | -120.9457 | -121.3042 | 121.4755 | 121.4654 | 121.539 | 28.5764 | -121.3751 | 0.2905 | 0.42116 | 0.062649 | 0.19719 | -121.4166
2513.25 | 121.2891 | -0.19226 | 121.1609 | 1.4211e-13 | -0.028132 | 0.003062 | 0.069904 | -0.012493 | 0.060394 | 0.0079357 | -0.0033713 | 0.0049142 | 0.017395 | 0.03685 | 0.0065869 | 2.3543 | 28.1369 | 1.0858 | 121.2649 | 121.2594 | 121.3284 | -0.21874 | 0.023941 | -0.017956 | -0.042615 | 0.07993 | 0.20601 | -0.14334 | -0.26946 | -0.02648 | 0.10406 | 2.5466 | 1.2781 | 1.3045 | 0.09855 | 0.16753 | -0.077201 | -121.081 | 0.2162 | 0.14965 | 0.22685 | -120.9549 | -121.3042 | 121.4572 | 121.4517 | 121.5207 | 28.3292 | -121.3796 | 0.27219 | 0.39827 | 0.048918 | 0.1743 | -121.4304
2515 | 121.2982 | -0.18768 | 121.1838 | 1.4211e-13 | -0.028132 | 0.0028484 | 0.070118 | -0.012493 | 0.059967 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017182 | 0.037064 | 0.0065869 | 2.3772 | 27.908 | 1.095 | 121.2741 | 121.2686 | 121.3422 | -0.22332 | 0.02852 | -0.008798 | -0.038036 | 0.075351 | 0.21059 | -0.1525 | -0.26946 | -0.035637 | 0.090326 | 2.5649 | 1.2826 | 1.3183 | 0.08482 | 0.15838 | -0.081779 | -121.1084 | 0.2162 | 0.14965 | 0.23143 | -120.9732 | -121.3363 | 121.4618 | 121.4563 | 121.5298 | 28.0957 | -121.4071 | 0.26303 | 0.39827 | 0.035183 | 0.17888 | -121.4532
2516.6875 | 121.3074 | -0.20599 | 121.1655 | 1.4211e-13 | -0.028132 | 0.003062 | 0.070118 | -0.012066 | 0.060394 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017395 | 0.03685 | 0.0068005 | 2.4276 | 28.2468 | 1.127 | 121.2741 | 121.2778 | 121.3376 | -0.22332 | 0.02852 | -0.008798 | -0.038036 | 0.075351 | 0.20601 | -0.15708 | -0.25572 | -0.017326 | 0.10864 | 2.6336 | 1.333 | 1.3503 | 0.11229 | 0.17211 | -0.049731 | -121.0901 | 0.23451 | 0.16796 | 0.21769 | -120.9595 | -121.3225 | 121.4801 | 121.4837 | 121.5436 | 28.4528 | -121.3888 | 0.28135 | 0.412 | 0.048915 | 0.1972 | -121.4212
2518.4375 | 121.344 | -0.16937 | 121.1517 | 1.4211e-13 | -0.028346 | 0.003062 | 0.070332 | -0.012707 | 0.059967 | -0.0073253 | -0.0031575 | 0.0051278 | 0.016968 | 0.037278 | 0.0065869 | 2.4825 | 28.2743 | 1.1499 | 121.297 | 121.2869 | 121.3559 | -0.22332 | 0.023941 | -0.013377 | -0.051772 | 0.070773 | 0.20143 | -0.1525 | -0.26946 | -0.053947 | 0.14526 | 2.6519 | 1.3193 | 1.3732 | 0.13518 | 0.20416 | -0.10009 | -121.081 | 0.19331 | 0.1176 | 0.21769 | -120.9503 | -121.3042 | 121.4664 | 121.4563 | 121.5253 | 28.4437 | -121.3751 | 0.24015 | 0.3708 | 0.016873 | 0.156 | -121.4212
2520.125 | 121.4081 | -0.16937 | 121.1563 | 1.4211e-13 | -0.028346 | 0.003062 | 0.070118 | -0.012493 | 0.06018 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017395 | 0.036423 | 0.0065869 | 2.5329 | 28.3704 | 1.1682 | 121.297 | 121.2961 | 121.3559 | -0.21874 | 0.033099 | -0.008798 | -0.033458 | 0.070773 | 0.20143 | -0.14792 | -0.26488 | -0.049368 | 0.14068 | 2.7023 | 1.3376 | 1.387 | 0.13976 | 0.19958 | -0.09551 | -121.0855 | 0.20247 | 0.13592 | 0.23142 | -120.9549 | -121.3042 | 121.4664 | 121.4654 | 121.5253 | 28.5398 | -121.3751 | 0.24015 | 0.3708 | 0.021451 | 0.16057 | -121.4212
2521.875 | 121.2845 | -0.20599 | 121.1838 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070118 | -0.012279 | 0.06018 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017395 | 0.03685 | 0.0065869 | 2.5787 | 28.4208 | 1.2048 | 121.297 | 121.2961 | 121.365 | -0.22332 | 0.02852 | -0.013377 | -0.047194 | 0.075351 | 0.20601 | -0.1525 | -0.26488 | -0.017326 | 0.11322 | 2.7847 | 1.4108 | 1.4282 | 0.11229 | 0.18127 | -0.058889 | -121.1084 | 0.23451 | 0.1588 | 0.21769 | -120.9778 | -121.3363 | 121.503 | 121.5021 | 121.571 | 28.6268 | -121.4071 | 0.28135 | 0.412 | 0.053494 | 0.19262 | -121.4487
2523.6094 | 121.344 | -0.17853 | 121.1609 | 1.4211e-13 | -0.027918 | 0.0032756 | 0.070332 | -0.012493 | 0.060394 | 0.0079357 | -0.0035849 | 0.0047004 | 0.017609 | 0.03685 | 0.0065869 | 2.629 | 28.4528 | 1.2369 | 121.3016 | 121.3006 | 121.3742 | -0.25995 | 0.023941 | -0.017956 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.26488 | -0.081423 | 0.14068 | 2.8076 | 1.4154 | 1.4968 | 0.13976 | 0.21331 | -0.086355 | -121.0901 | 0.20247 | 0.14049 | 0.22685 | -120.9503 | -121.3134 | 121.4801 | 121.4792 | 121.5527 | 28.6314 | -121.4208 | 0.2493 | 0.38911 | 0.026028 | 0.16057 | -121.4258
2525.3594 | 121.4218 | -0.15564 | 121.17 | 1.4211e-13 | -0.028346 | 0.0028484 | 0.070332 | -0.012493 | 0.06018 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017609 | 0.036423 | 0.0065869 | 2.684 | 28.5627 | 1.2506 | 121.3153 | 121.3144 | 121.3788 | -0.21874 | 0.023941 | -0.008798 | -0.047194 | 0.075351 | 0.21059 | -0.16166 | -0.26946 | -0.063101 | 0.14526 | 2.8396 | 1.4063 | 1.4694 | 0.14434 | 0.20874 | -0.11382 | -121.0947 | 0.17958 | 0.10845 | 0.22227 | -120.9595 | -121.3317 | 121.4709 | 121.47 | 121.5344 | 28.7184 | -121.3888 | 0.23099 | 0.36623 | -0.006018 | 0.14684 | -121.4395
2527.0469 | 121.4035 | -0.16479 | 121.1792 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070545 | -0.012279 | 0.060608 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017395 | 0.036636 | 0.0063733 | 2.716 | 28.6039 | 1.2552 | 121.3107 | 121.3098 | 121.3834 | -0.2279 | 0.02852 | -0.013377 | -0.033458 | 0.075351 | 0.21516 | -0.15708 | -0.26488 | -0.063104 | 0.13153 | 2.8808 | 1.42 | 1.4831 | 0.13061 | 0.20416 | -0.10009 | -121.1038 | 0.19331 | 0.13134 | 0.23142 | -120.964 | -121.3363 | 121.4755 | 121.4746 | 121.5482 | 28.7687 | -121.4071 | 0.24015 | 0.37996 | 0.007716 | 0.15142 | -121.4441
2528.7969 | 121.3211 | -0.21973 | 121.225 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070332 | -0.012493 | 0.060608 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017182 | 0.037064 | 0.0068005 | 2.7756 | 28.3933 | 1.3468 | 121.3245 | 121.3235 | 121.4017 | -0.23706 | 0.023941 | -0.008798 | -0.047194 | 0.075351 | 0.20601 | -0.15708 | -0.2603 | -0.017329 | 0.099489 | 2.9953 | 1.5665 | 1.5838 | 0.098568 | 0.1767 | -0.040577 | -121.1496 | 0.24367 | 0.17253 | 0.21311 | -121.019 | -121.3821 | 121.5442 | 121.5433 | 121.6214 | 28.613 | -121.462 | 0.29508 | 0.42573 | 0.062648 | 0.21093 | -121.4853
2530.5625 | 121.344 | -0.18768 | 121.2021 | 1.4211e-13 | -0.028132 | 0.003062 | 0.070118 | -0.012279 | 0.060608 | 0.0079357 | -0.0029439 | 0.0044868 | 0.017609 | 0.037064 | 0.0063733 | 2.8168 | 28.288 | 1.4063 | 121.329 | 121.3281 | 121.4017 | -0.21874 | 0.02852 | -0.008798 | -0.038036 | 0.07993 | 0.20601 | -0.14792 | -0.26488 | -0.031058 | 0.12696 | 3.0044 | 1.594 | 1.625 | 0.12604 | 0.19959 | -0.0772 | -121.1222 | 0.2162 | 0.14965 | 0.22685 | -120.9961 | -121.35 | 121.5167 | 121.5158 | 121.5894 | 28.4757 | -121.4208 | 0.26761 | 0.39369 | 0.039761 | 0.17888 | -121.467
2532.3125 | 121.3989 | -0.19684 | 121.2387 | 1.4211e-13 | -0.028132 | 0.003062 | 0.070118 | -0.012279 | 0.060608 | 0.023196 | -0.0031575 | 0.0049142 | 0.017182 | 0.03685 | 0.0068005 | 2.8763 | 28.2789 | 1.4475 | 121.3428 | 121.3373 | 121.4108 | -0.22332 | 0.023941 | -0.013377 | -0.042615 | 0.075351 | 0.20601 | -0.15708 | -0.26488 | -0.026482 | 0.10407 | 3.0731 | 1.6443 | 1.6708 | 0.098572 | 0.17212 | -0.068045 | -121.1634 | 0.22078 | 0.15422 | 0.22227 | -121.0327 | -121.3958 | 121.5396 | 121.5341 | 121.6077 | 28.4757 | -121.462 | 0.27219 | 0.40285 | 0.039759 | 0.18346 | -121.5036
2534 | 121.3898 | -0.19226 | 121.225 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070118 | -0.012066 | 0.060608 | 0.015566 | -0.0029439 | 0.0047004 | 0.016968 | 0.036636 | 0.0065869 | 2.9221 | 28.256 | 1.4887 | 121.3474 | 121.3373 | 121.42 | -0.23248 | 0.023941 | -0.008798 | -0.051772 | 0.075351 | 0.21059 | -0.1525 | -0.26488 | -0.040216 | 0.12238 | 3.1143 | 1.6809 | 1.7212 | 0.1123 | 0.19501 | -0.072622 | -121.1496 | 0.2162 | 0.14049 | 0.21311 | -121.0144 | -121.3775 | 121.5396 | 121.5295 | 121.6123 | 28.4482 | -121.4575 | 0.26761 | 0.40285 | 0.039761 | 0.18346 | -121.4899
2535.6875 | 121.431 | -0.16479 | 121.2067 | 1.4211e-13 | -0.027918 | 0.003062 | 0.070545 | -0.012279 | 0.060821 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017609 | 0.03685 | 0.0063733 | 2.9724 | 28.2285 | 1.5253 | 121.3428 | 121.3464 | 121.4154 | -0.23248 | 0.02852 | -0.008798 | -0.042615 | 0.07993 | 0.20143 | -0.1525 | -0.2603 | -0.067682 | 0.13611 | 3.1372 | 1.6901 | 1.7578 | 0.13977 | 0.20875 | -0.095509 | -121.1267 | 0.19331 | 0.12218 | 0.21769 | -121.0052 | -121.3592 | 121.5076 | 121.5112 | 121.5802 | 28.3933 | -121.4391 | 0.24472 | 0.36622 | 0.012295 | 0.156 | -121.467
2537.4375 | 121.4401 | -0.19684 | 121.2021 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070545 | -0.011852 | 0.060821 | -0.0073253 | -0.0029439 | 0.0047004 | 0.017395 | 0.036636 | 0.0063733 | 3.0274 | 28.1507 | 1.5757 | 121.3474 | 121.3419 | 121.4108 | -0.25995 | 0.023941 | -0.008798 | -0.042615 | 0.075351 | 0.21059 | -0.14792 | -0.2603 | -0.063113 | 0.14527 | 3.2242 | 1.7725 | 1.8356 | 0.13977 | 0.20874 | -0.063466 | -121.1267 | 0.22078 | 0.15422 | 0.21769 | -120.9915 | -121.35 | 121.5442 | 121.5387 | 121.6077 | 28.3475 | -121.462 | 0.27219 | 0.40742 | 0.048916 | 0.18804 | -121.4624
2539.125 | 121.4447 | -0.17395 | 121.2433 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070332 | -0.012066 | 0.060394 | 0.00030522 | -0.0035849 | 0.0049142 | 0.017395 | 0.03685 | 0.0065869 | 3.1006 | 28.1049 | 1.6169 | 121.3565 | 121.351 | 121.4246 | -0.26911 | 0.02852 | -0.008798 | -0.042615 | 0.084508 | 0.20601 | -0.14792 | -0.26488 | -0.095159 | 0.11323 | 3.2746 | 1.7908 | 1.886 | 0.10773 | 0.18128 | -0.090933 | -121.1588 | 0.20247 | 0.13133 | 0.22227 | -121.0373 | -121.3912 | 121.5305 | 121.525 | 121.5985 | 28.2788 | -121.5124 | 0.25846 | 0.37996 | 0.026028 | 0.16515 | -121.5082
2540.8125 | 120.8176 | -0.21515 | 120.7443 | 1.4211e-13 | -0.028132 | 0.0032756 | 0.070332 | -0.012279 | 0.060608 | -0.0073253 | -0.0033713 | 0.0047004 | 0.017395 | 0.037064 | 0.0068005 | 3.183 | 27.8897 | 1.6901 | 120.8163 | 120.8153 | 120.8889 | -0.25995 | 0.033099 | -0.00422 | -0.042615 | 0.075351 | 0.21059 | -0.15708 | -0.26488 | -0.044802 | 0.07194 | 3.3982 | 1.9053 | 1.9501 | 0.070959 | 0.14455 | -0.049734 | -120.669 | 0.24825 | 0.17253 | 0.22227 | -120.5337 | -120.9014 | 121.0314 | 121.0304 | 121.104 | 28.1048 | -121.0043 | 0.2905 | 0.42573 | 0.05807 | 0.21093 | -121.0092
2542.5625 | 120.9915 | -0.1831 | 120.9045 | 1.4211e-13 | -0.027918 | 0.0034894 | 0.070545 | -0.012279 | 0.060608 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016968 | 0.037064 | 0.0061595 | 3.2059 | 27.8393 | 1.713 | 120.9902 | 120.9939 | 121.0629 | -0.22332 | 0.023941 | -0.008798 | -0.038036 | 0.07993 | 0.20601 | -0.1525 | -0.2603 | -0.040215 | 0.085702 | 3.389 | 1.8961 | 1.9363 | 0.08932 | 0.15832 | -0.077199 | -120.8246 | 0.20705 | 0.14507 | 0.22227 | -120.6985 | -121.057 | 121.1733 | 121.177 | 121.246 | 28.0224 | -121.1279 | 0.26304 | 0.38911 | 0.030605 | 0.17431 | -121.1648
2544.2656 | 121.1884 | -0.14191 | 120.8908 | 1.4211e-13 | -0.028132 | 0.003062 | 0.070545 | -0.012066 | 0.060608 | 0.015566 | -0.0029439 | 0.0044868 | 0.017182 | 0.036423 | 0.0068005 | 3.2792 | 27.853 | 1.7634 | 121.0681 | 121.0625 | 121.1315 | -0.21416 | 0.02852 | -0.008798 | -0.038036 | 0.075351 | 0.21059 | -0.14792 | -0.27404 | -0.072255 | 0.17727 | 3.4211 | 1.9053 | 1.9775 | 0.17174 | 0.24073 | -0.13213 | -120.8155 | 0.17043 | 0.10387 | 0.236 | -120.6802 | -121.0387 | 121.21 | 121.2045 | 121.2734 | 27.995 | -121.105 | 0.21726 | 0.35249 | -0.006015 | 0.13311 | -121.1648
2546.0312 | 121.0831 | -0.18768 | 121.0098 | 1.4211e-13 | -0.027918 | 0.003062 | 0.070332 | -0.012066 | 0.060821 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017182 | 0.037064 | 0.0068005 | 3.3524 | 27.8439 | 1.8229 | 121.1047 | 121.1083 | 121.1773 | -0.21416 | 0.023941 | -0.013377 | -0.042615 | 0.075351 | 0.20601 | -0.1525 | -0.26946 | -0.026479 | 0.094876 | 3.5401 | 2.0106 | 2.0371 | 0.098507 | 0.1675 | -0.081779 | -120.9345 | 0.21162 | 0.14507 | 0.22685 | -120.8038 | -121.1623 | 121.2924 | 121.296 | 121.365 | 28.0316 | -121.224 | 0.26303 | 0.39369 | 0.035183 | 0.17431 | -121.2793
2547.7188 | 121.1243 | -0.19226 | 121.0144 | 1.4211e-13 | -0.028132 | 0.003703 | 0.070332 | -0.011852 | 0.060394 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017395 | 0.036636 | 0.0065869 | 3.4211 | 27.7935 | 1.8687 | 121.1322 | 121.1312 | 121.2048 | -0.21874 | 0.033099 | -0.013377 | -0.038036 | 0.075351 | 0.21059 | -0.13876 | -0.26488 | -0.02648 | 0.11777 | 3.6134 | 2.0609 | 2.0874 | 0.11683 | 0.19039 | -0.072622 | -120.9391 | 0.22536 | 0.15423 | 0.22685 | -120.8038 | -121.1532 | 121.3244 | 121.3235 | 121.3971 | 27.9858 | -121.2331 | 0.26761 | 0.40285 | 0.053496 | 0.17888 | -121.2793
2549.4688 | 121.1517 | -0.20599 | 121.0693 | 1.4211e-13 | -0.027918 | 0.0034894 | 0.070759 | -0.012066 | 0.061035 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017609 | 0.03685 | 0.0065869 | 3.5035 | 27.8347 | 1.9328 | 121.1596 | 121.1495 | 121.2323 | -0.21416 | 0.02852 | -0.008798 | -0.033458 | 0.070773 | 0.21059 | -0.14792 | -0.26488 | -0.008168 | 0.090307 | 3.7095 | 2.1388 | 2.1469 | 0.080209 | 0.16293 | -0.058889 | -120.9986 | 0.23451 | 0.17254 | 0.23142 | -120.8588 | -121.2173 | 121.3656 | 121.3555 | 121.4383 | 28.0407 | -121.2835 | 0.27677 | 0.41658 | 0.058072 | 0.1972 | -121.3342
2551.1719 | 121.2433 | -0.16937 | 121.051 | 1.4211e-13 | -0.028132 | 0.003062 | 0.070973 | -0.012066 | 0.061249 | 0.015566 | -0.0031575 | 0.0044868 | 0.017395 | 0.03685 | 0.0061595 | 3.5722 | 27.8485 | 1.9969 | 121.178 | 121.177 | 121.246 | -0.21416 | 0.02852 | 0.000359 | -0.038036 | 0.075351 | 0.20601 | -0.14792 | -0.2603 | -0.044789 | 0.12693 | 3.7416 | 2.1662 | 2.211 | 0.12599 | 0.19498 | -0.090931 | -120.9757 | 0.19789 | 0.13134 | 0.22227 | -120.845 | -121.1989 | 121.3473 | 121.3464 | 121.4154 | 28.0178 | -121.2652 | 0.24472 | 0.37538 | 0.021451 | 0.16973 | -121.3113
2552.9219 | 121.2799 | -0.14648 | 121.0556 | 1.4211e-13 | -0.027705 | 0.0032756 | 0.070545 | -0.011852 | 0.061035 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017182 | 0.03685 | 0.0068005 | 3.6546 | 27.7844 | 2.0518 | 121.1963 | 121.1999 | 121.2689 | -0.21874 | 0.019362 | -0.00422 | -0.033458 | 0.07993 | 0.20601 | -0.1525 | -0.26946 | -0.072257 | 0.14067 | 3.8011 | 2.1983 | 2.2706 | 0.14431 | 0.21329 | -0.12298 | -120.9757 | 0.16585 | 0.11303 | 0.236 | -120.8496 | -121.2081 | 121.3428 | 121.3464 | 121.4154 | 27.9309 | -121.2743 | 0.22641 | 0.35249 | -0.006016 | 0.14226 | -121.3251
2554.6875 | 120.4056 | -5.2185 | 115.1596 | 1.4211e-13 | -0.027918 | 0.0034894 | 0.070118 | -0.012066 | 0.061035 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017395 | 0.03685 | 0.0065869 | -1.2626 | 23.5308 | -2.9339 | 115.2261 | 115.2336 | 115.3121 | -5.2739 | 0.023941 | -0.00422 | -0.033458 | 0.07993 | 0.20143 | -0.14792 | -0.26946 | -0.055367 | 0.066446 | 3.9559 | 2.2846 | 2.3399 | 0.073967 | 0.15253 | 4.949 | -115.0797 | 5.2424 | 5.185 | 0.236 | -114.9582 | -115.3075 | 120.4446 | 120.4521 | 120.5306 | 28.7494 | -120.4335 | 5.2984 | 5.4199 | 5.0706 | 5.2143 | -115.4291
2556.375 | 120.6162 | -6.5094 | 115.2878 | 1.4211e-13 | -0.027918 | 0.0034894 | 0.070759 | -0.011638 | 0.060821 | -0.0073253 | -0.0031575 | 0.0044868 | 0.017182 | 0.03685 | 0.0065869 | -1.052 | 23.6774 | -2.7371 | 115.5969 | 115.6045 | 115.6876 | -5.1411 | 0.019362 | -0.008798 | -0.042615 | 0.075351 | 0.21059 | -0.15708 | -0.2603 | 1.3683 | 0.30912 | 5.4574 | 3.7723 | 2.404 | 0.31669 | 0.3998 | 6.2491 | -115.2124 | 6.5288 | 6.4668 | 0.21769 | -115.0772 | -115.4449 | 122.1063 | 122.1139 | 122.197 | 30.1868 | -120.4289 | 6.5848 | 6.72 | 6.3523 | 6.5006 | -115.5481
2558.125 | 120.6802 | -6.6605 | 114.0427 | 1.4211e-13 | -0.027705 | 0.0041304 | 0.070332 | -0.011638 | 0.061462 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017609 | 0.03685 | 0.0065869 | -2.4713 | 22.4411 | -4.2021 | 114.1501 | 114.1575 | 114.2453 | -6.6888 | 0.02852 | -0.013377 | -0.042615 | 0.084508 | 0.21059 | -0.11587 | -0.2603 | -0.0283 | 0.10747 | 4.1892 | 2.4583 | 2.4866 | 0.11486 | 0.20265 | 6.4002 | -113.9582 | 6.689 | 6.6178 | 0.21769 | -113.8321 | -114.1585 | 120.8106 | 120.818 | 120.9058 | 29.1016 | -120.7314 | 6.745 | 6.871 | 6.5446 | 6.6471 | -114.303
2559.875 | 120.8176 | -7.0312 | 113.6719 | 1.4211e-13 | -0.027705 | 0.0034894 | 0.070332 | -0.011425 | 0.061676 | 0.0079357 | -0.0031575 | 0.0049142 | 0.017395 | 0.03685 | 0.0065869 | -2.6819 | 22.1298 | -4.4264 | 113.8846 | 113.8828 | 113.966 | -7.0139 | 0.033099 | -0.00422 | -0.042615 | 0.075351 | 0.21059 | -0.15708 | -0.2603 | 0.017385 | 0.21271 | 4.3494 | 2.6048 | 2.5874 | 0.21092 | 0.29415 | 6.7709 | -113.5965 | 7.0643 | 6.9886 | 0.21769 | -113.4613 | -113.829 | 120.9158 | 120.914 | 120.9973 | 29.161 | -120.6857 | 7.1066 | 7.2418 | 6.8742 | 7.027 | -113.9322
2561.5469 | 120.7397 | -6.7337 | 114.1159 | 1.4211e-13 | -0.027918 | 0.003703 | 0.070545 | -0.012066 | 0.061462 | 0.00030522 | -0.0035849 | 0.0042732 | 0.017182 | 0.036636 | 0.0063733 | -2.6361 | 22.1069 | -4.4173 | 113.9029 | 113.9194 | 113.9935 | -7.0139 | 0.019362 | -0.00422 | -0.038036 | 0.07993 | 0.21516 | -0.1525 | -0.25572 | -0.28016 | -0.21301 | 4.0976 | 2.3164 | 2.5966 | -0.19648 | -0.12241 | 6.478 | -114.036 | 6.7531 | 6.6957 | 0.21769 | -113.9007 | -114.2684 | 120.6366 | 120.6531 | 120.7272 | 28.8406 | -121.1298 | 6.8136 | 6.9489 | 6.5812 | 6.7295 | -114.3716
2563.2969 | 120.8359 | -6.0287 | 114.8163 | 1.4211e-13 | -0.027705 | 0.003703 | 0.070545 | -0.011638 | 0.06189 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017395 | 0.03685 | 0.0063733 | -1.6334 | 22.9219 | -3.433 | 114.8506 | 114.8581 | 114.9321 | -6.1301 | 0.02852 | -0.00422 | -0.038036 | 0.070773 | 0.21059 | -0.14792 | -0.27404 | -0.10138 | 0.034341 | 4.3953 | 2.5958 | 2.6972 | 0.041818 | 0.11583 | 5.7547 | -114.7455 | 6.0573 | 5.9907 | 0.236 | -114.6057 | -114.9642 | 120.8794 | 120.8869 | 120.9609 | 28.9506 | -120.9464 | 6.0995 | 6.2393 | 5.8808 | 6.0245 | -115.0903
2564.9844 | 120.7855 | -6.8436 | 114.0427 | 1.4211e-13 | -0.027277 | 0.003703 | 0.071186 | -0.011638 | 0.061676 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016968 | 0.036636 | 0.0065869 | -2.2561 | 22.3816 | -4.051 | 114.1547 | 114.1667 | 114.2453 | -6.8719 | 0.02852 | 0.000359 | -0.038036 | 0.070773 | 0.20601 | -0.12961 | -0.26946 | -0.028351 | 0.11205 | 4.5875 | 2.7925 | 2.8209 | 0.12402 | 0.20265 | 6.5741 | -113.9719 | 6.8721 | 6.8055 | 0.23143 | -113.8367 | -114.1723 | 120.9983 | 121.0103 | 121.0889 | 29.2252 | -120.9146 | 6.9143 | 7.0496 | 6.714 | 6.8439 | -114.3121
2566.7344 | 120.8221 | -7.3517 | 113.5803 | 1.4211e-13 | -0.027705 | 0.0034894 | 0.070759 | -0.010997 | 0.06189 | -0.0073253 | -0.0029439 | 0.0044868 | 0.017182 | 0.03685 | 0.0065869 | -2.5857 | 22.0291 | -4.4585 | 113.6923 | 113.6996 | 113.7737 | -7.3344 | 0.02852 | -0.00422 | -0.038036 | 0.075351 | 0.20601 | -0.13419 | -0.2603 | 0.017296 | 0.11197 | 4.7659 | 2.8932 | 2.8759 | 0.11931 | 0.1934 | 7.0914 | -113.505 | 7.3802 | 7.3136 | 0.22227 | -113.3743 | -113.7145 | 121.044 | 121.0513 | 121.1254 | 29.3807 | -120.9147 | 7.427 | 7.5577 | 7.2175 | 7.3475 | -113.8406
2568.4844 | 120.8588 | -7.4203 | 113.5529 | 1.4211e-13 | -0.027277 | 0.003703 | 0.070759 | -0.011425 | 0.062103 | 0.0079357 | -0.0033713 | 0.0049142 | 0.017182 | 0.037278 | 0.0065869 | -2.5812 | 22.052 | -4.4951 | 113.6007 | 113.5989 | 113.6867 | -7.458 | 0.02852 | -0.00422 | -0.042615 | 0.07993 | 0.21516 | -0.11129 | -0.25572 | -0.037671 | 0.047869 | 4.8392 | 2.9252 | 2.9629 | 0.046042 | 0.13387 | 7.1646 | -113.4729 | 7.4489 | 7.3777 | 0.21311 | -113.3377 | -113.6641 | 121.0211 | 121.0192 | 121.1071 | 29.4723 | -121.0109 | 7.5003 | 7.6355 | 7.3091 | 7.4161 | -113.8086
2570.1719 | 120.9 | -7.3151 | 113.6581 | 1.4211e-13 | -0.027277 | 0.0039166 | 0.070973 | -0.011425 | 0.06189 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017182 | 0.037064 | 0.0065869 | -2.3477 | 22.1985 | -4.2983 | 113.7289 | 113.7363 | 113.8149 | -7.3481 | 0.033099 | -0.00422 | -0.042615 | 0.075351 | 0.20601 | -0.14334 | -0.26488 | -0.033063 | 0.070778 | 4.9674 | 3.0168 | 3.0499 | 0.078124 | 0.15679 | 7.0502 | -113.5828 | 7.3482 | 7.2724 | 0.22227 | -113.4521 | -113.8015 | 121.044 | 121.0513 | 121.13 | 29.5135 | -121.0063 | 7.3904 | 7.5211 | 7.1717 | 7.3108 | -113.923
2571.875 | 121.0144 | -7.1594 | 113.7497 | 1.4211e-13 | -0.027277 | 0.003703 | 0.071186 | -0.011425 | 0.062103 | -0.0073253 | -0.0031575 | 0.0044868 | 0.017182 | 0.03685 | 0.0065869 | -2.0455 | 22.3954 | -4.019 | 113.9349 | 113.9377 | 114.021 | -7.165 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.14792 | -0.26488 | -0.005545 | 0.18525 | 5.1139 | 3.1404 | 3.146 | 0.18804 | 0.27127 | 6.8945 | -113.6789 | 7.1879 | 7.1168 | 0.22227 | -113.5391 | -113.8976 | 121.0944 | 121.0972 | 121.1804 | 29.5548 | -120.9147 | 7.2302 | 7.37 | 7.0115 | 7.146 | -114.0146
2573.6406 | 120.9869 | -7.0679 | 113.9099 | 1.4211e-13 | -0.027064 | 0.003703 | 0.070759 | -0.011425 | 0.062317 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.03685 | 0.0065869 | -1.8395 | 22.6014 | -3.8587 | 114.0128 | 114.0247 | 114.1217 | -7.1009 | 0.023941 | -0.008798 | -0.042615 | 0.07993 | 0.21516 | -0.1525 | -0.26488 | -0.032993 | 0.10287 | 5.2284 | 3.2091 | 3.2421 | 0.11483 | 0.21178 | 6.803 | -113.83 | 7.0918 | 7.0253 | 0.22227 | -113.6947 | -114.0624 | 121.0807 | 121.0926 | 121.1896 | 29.6693 | -121.0108 | 7.1478 | 7.283 | 6.9154 | 7.0591 | -114.1748
2575.3906 | 121.0648 | -5.6122 | 115.416 | 1.4211e-13 | -0.027064 | 0.0039166 | 0.070973 | -0.010997 | 0.062317 | 0.0079357 | -0.0029439 | 0.0047004 | 0.016968 | 0.037278 | 0.0063733 | -0.52089 | 23.746 | -2.5631 | 115.2718 | 115.2931 | 115.3579 | -5.9287 | 0.02852 | -0.008798 | -0.047194 | 0.07993 | 0.21516 | -0.1525 | -0.26946 | -0.31648 | -0.14412 | 5.0913 | 3.0491 | 3.3656 | -0.12286 | -0.058035 | 5.3427 | -115.336 | 5.6407 | 5.565 | 0.22227 | -115.2008 | -115.5685 | 120.884 | 120.9053 | 120.9701 | 29.3582 | -121.3446 | 5.6921 | 5.8273 | 5.4597 | 5.6034 | -115.6854
2577.1094 | 120.9595 | -6.4957 | 114.5828 | 1.4211e-13 | -0.02685 | 0.0041304 | 0.0714 | -0.010784 | 0.062103 | 0.0079357 | -0.0033713 | 0.0049142 | 0.017182 | 0.037278 | 0.0065869 | -0.80933 | 23.5034 | -2.8973 | 114.8735 | 114.8764 | 114.9642 | -6.3637 | 0.02852 | -0.00422 | -0.042615 | 0.07993 | 0.20601 | -0.15708 | -0.2603 | 0.13201 | 0.29069 | 5.6863 | 3.5984 | 3.4664 | 0.29359 | 0.38134 | 6.2354 | -114.5029 | 6.5242 | 6.4531 | 0.21769 | -114.3768 | -114.7399 | 121.3692 | 121.3721 | 121.4598 | 29.999 | -120.9465 | 6.5756 | 6.7017 | 6.3386 | 6.4914 | -114.8431
2578.8594 | 121.0739 | -6.7383 | 114.2715 | 1.4211e-13 | -0.02685 | 0.0039166 | 0.071186 | -0.010997 | 0.062744 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017395 | 0.03685 | 0.0068005 | -1.1344 | 23.3614 | -3.2681 | 114.3791 | 114.3911 | 114.4651 | -6.8032 | 0.033099 | -0.00422 | -0.038036 | 0.089087 | 0.21516 | -0.14792 | -0.2603 | -0.064953 | 0.10751 | 5.6039 | 3.4701 | 3.5351 | 0.11951 | 0.19355 | 6.478 | -114.1825 | 6.7714 | 6.7002 | 0.22227 | -114.0564 | -114.4195 | 121.1173 | 121.1293 | 121.2034 | 30.0997 | -121.0748 | 6.8274 | 6.9534 | 6.5904 | 6.7341 | -114.5318
2580.5469 | 121.0693 | -6.8893 | 114.1434 | 1.4211e-13 | -0.026636 | 0.004344 | 0.071186 | -0.010784 | 0.062744 | 0.0079357 | -0.0033713 | 0.0042732 | 0.017395 | 0.03685 | 0.0063733 | -1.1252 | 23.4301 | -3.3002 | 114.2463 | 114.2537 | 114.3369 | -6.9452 | 0.023941 | -0.00422 | -0.042615 | 0.07993 | 0.21059 | -0.16166 | -0.2603 | -0.055838 | 0.10291 | 5.7641 | 3.5892 | 3.645 | 0.11031 | 0.19352 | 6.629 | -114.0634 | 6.9133 | 6.8467 | 0.21769 | -113.9328 | -114.305 | 121.1356 | 121.143 | 121.2262 | 30.3195 | -121.0886 | 6.9693 | 7.0999 | 6.7277 | 6.8851 | -114.4037
2582.2969 | 121.1472 | -12.0575 | 108.9203 | 1.4211e-13 | -0.026423 | 0.0039166 | 0.071186 | -0.010784 | 0.063385 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.037064 | 0.0068005 | -4.614 | 20.7562 | -6.8575 | 110.6889 | 110.6775 | 110.8159 | -10.6404 | 0.02852 | 0.004938 | -0.042615 | 0.084508 | 0.21516 | -0.1525 | -0.2603 | 1.4171 | 1.7686 | 7.4435 | 5.2 | 3.7829 | 1.7573 | 1.8957 | 11.7972 | -108.8358 | 12.086 | 12.0149 | 0.21769 | -108.7051 | -109.0728 | 122.7464 | 122.735 | 122.8734 | 32.8137 | -119.5607 | 12.142 | 12.2727 | 11.905 | 12.0624 | -109.1806
2584.0469 | 121.0693 | -9.7366 | 111.3373 | 1.4211e-13 | -0.026423 | 0.0041304 | 0.071186 | -0.010784 | 0.062958 | 0.00030522 | -0.0027303 | 0.0047004 | 0.017182 | 0.037491 | 0.0068005 | -3.5426 | 21.7406 | -5.8869 | 111.4992 | 111.5155 | 111.608 | -9.7109 | 0.02852 | 0.000359 | -0.042615 | 0.07993 | 0.21516 | -0.16166 | -0.26946 | 0.025782 | 0.16196 | 6.194 | 3.8497 | 3.8239 | 0.17821 | 0.27076 | 9.4672 | -111.2574 | 9.7652 | 9.694 | 0.22685 | -111.1221 | -111.4989 | 121.2359 | 121.2521 | 121.3447 | 31.4772 | -121.0481 | 9.8166 | 9.9518 | 9.575 | 9.737 | -111.6067
2585.8125 | 121.0602 | -7.1091 | 114.0427 | 1.4211e-13 | -0.026423 | 0.0041304 | 0.071186 | -0.010784 | 0.063385 | 0.0079357 | -0.0033713 | 0.0047004 | 0.017182 | 0.037491 | 0.0065869 | -0.85511 | 24.2726 | -3.1949 | 114.0769 | 114.0797 | 114.1675 | -7.165 | 0.02852 | -0.00422 | -0.028879 | 0.07993 | 0.21516 | -0.14334 | -0.26488 | -0.055899 | 0.034213 | 6.254 | 3.9142 | 3.9701 | 0.037021 | 0.12482 | 6.8442 | -113.9627 | 7.1376 | 7.0802 | 0.236 | -113.8275 | -114.186 | 121.1859 | 121.1888 | 121.2766 | 31.3816 | -121.2076 | 7.189 | 7.3242 | 6.9657 | 7.1048 | -114.3075
2587.5625 | 121.1884 | -8.4091 | 112.6785 | 1.4211e-13 | -0.026209 | 0.0045578 | 0.0714 | -0.010143 | 0.063813 | 0.0079357 | -0.0029439 | 0.0049142 | 0.017395 | 0.037064 | 0.0063733 | -1.9722 | 23.5537 | -4.344 | 112.7675 | 112.7838 | 112.8672 | -8.4745 | 0.02852 | -0.013377 | -0.042615 | 0.084508 | 0.21059 | -0.14792 | -0.2603 | -0.065423 | 0.08893 | 6.4369 | 4.0651 | 4.1305 | 0.10532 | 0.18863 | 8.1488 | -112.594 | 8.4376 | 8.3665 | 0.21769 | -112.4679 | -112.8264 | 121.1766 | 121.193 | 121.2763 | 31.9629 | -121.1531 | 8.4936 | 8.6197 | 8.2612 | 8.3957 | -112.9388
2589.25 | 121.2112 | -6.5598 | 114.4867 | 1.4211e-13 | -0.025995 | 0.0045578 | 0.071186 | -0.01057 | 0.063599 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016968 | 0.03685 | 0.0063733 | -0.59872 | 24.9594 | -3.0118 | 113.967 | 113.9698 | 114.0668 | -7.284 | 0.02852 | -0.008798 | -0.038036 | 0.075351 | 0.21516 | -0.14792 | -0.26946 | -0.72427 | -0.5197 | 5.961 | 3.548 | 4.2723 | -0.5169 | -0.41994 | 6.2903 | -114.4113 | 6.5883 | 6.5217 | 0.23143 | -114.2715 | -114.6346 | 120.5267 | 120.5295 | 120.6265 | 31.5191 | -121.7707 | 6.6351 | 6.7749 | 6.4118 | 6.551 | -114.7562
2591.0156 | 121.0693 | -8.2718 | 112.9211 | 1.4211e-13 | -0.025782 | 0.0045578 | 0.0714 | -0.010143 | 0.063813 | -0.0073253 | -0.0029439 | 0.0047004 | 0.017395 | 0.037064 | 0.0065869 | -1.4915 | 24.5061 | -3.9595 | 112.8728 | 112.8892 | 112.9633 | -8.3921 | 0.02852 | -0.008798 | -0.038036 | 0.084508 | 0.20601 | -0.1525 | -0.26946 | -0.12033 | -0.048382 | 6.7803 | 4.3123 | 4.4327 | -0.031978 | 0.042168 | 8.0023 | -112.8366 | 8.3003 | 8.2338 | 0.23143 | -112.7151 | -113.0736 | 121.1446 | 121.161 | 121.2351 | 32.7779 | -121.3133 | 8.3563 | 8.4778 | 8.1193 | 8.263 | -113.1906
2592.7656 | 121.1334 | -8.2031 | 112.9898 | 1.4211e-13 | -0.025568 | 0.0045578 | 0.071827 | -0.009929 | 0.064454 | 0.015566 | -0.0031575 | 0.0049142 | 0.016754 | 0.037278 | 0.0063733 | -1.1344 | 25.2341 | -3.6527 | 113.033 | 113.0448 | 113.1281 | -8.241 | 0.033099 | -0.00422 | -0.038036 | 0.075351 | 0.21059 | -0.14792 | -0.27404 | -0.037892 | 0.043198 | 7.0687 | 4.5504 | 4.5883 | 0.055041 | 0.13833 | 7.9291 | -112.9145 | 8.2362 | 8.1651 | 0.236 | -112.7792 | -113.1377 | 121.2361 | 121.248 | 121.3313 | 33.4372 | -121.2308 | 8.2785 | 8.4137 | 8.0552 | 8.1989 | -113.2638
2594.5156 | 121.1975 | -6.958 | 114.1846 | 1.4211e-13 | -0.025568 | 0.0047714 | 0.071827 | -0.009929 | 0.064454 | 0.015566 | -0.0031575 | 0.0047004 | 0.016968 | 0.03685 | 0.0072279 | 0.2437 | 26.7633 | -2.2335 | 114.2875 | 114.2949 | 114.3735 | -7.0139 | 0.02852 | -0.00422 | -0.038036 | 0.084508 | 0.21059 | -0.14792 | -0.26488 | -0.055857 | 0.10291 | 7.2017 | 4.7246 | 4.7804 | 0.11032 | 0.18895 | 6.6931 | -114.1001 | 6.9865 | 6.92 | 0.22685 | -113.974 | -114.3325 | 121.2455 | 121.2529 | 121.3315 | 33.7213 | -121.1984 | 7.0425 | 7.1686 | 6.8101 | 6.9538 | -114.4495
2596.2188 | 121.2067 | -6.8985 | 114.2853 | 1.4211e-13 | -0.025141 | 0.0047714 | 0.071827 | -0.009929 | 0.064667 | 0.0079357 | -0.0031575 | 0.0042732 | 0.017182 | 0.037064 | 0.0065869 | 0.5825 | 27.3128 | -1.9359 | 114.4477 | 114.4597 | 114.5475 | -6.8582 | 0.033099 | -0.008798 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.25572 | 0.040318 | 0.16245 | 7.481 | 4.9626 | 4.9223 | 0.17446 | 0.26223 | 6.6428 | -114.2145 | 6.9316 | 6.8559 | 0.21311 | -114.0793 | -114.4378 | 121.3462 | 121.3582 | 121.446 | 34.2113 | -121.1435 | 6.9693 | 7.1045 | 6.746 | 6.8897 | -114.541
2597.9688 | 121.1426 | -5.5023 | 115.7089 | 1.4211e-13 | -0.025141 | 0.0045578 | 0.072255 | -0.0097152 | 0.065308 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016754 | 0.037491 | 0.0065869 | 2.043 | 28.9244 | -0.50744 | 115.7297 | 115.7464 | 115.8295 | -5.5898 | 0.02852 | -0.008798 | -0.042615 | 0.084508 | 0.20601 | -0.15708 | -0.26488 | -0.0875 | 0.020752 | 7.5453 | 4.9949 | 5.0824 | 0.037491 | 0.12059 | 5.2374 | -115.6244 | 5.5308 | 5.4597 | 0.22227 | -115.5029 | -115.866 | 121.232 | 121.2487 | 121.3318 | 34.4268 | -121.2987 | 5.5868 | 5.7083 | 5.3452 | 5.4935 | -115.9738
2599.6719 | 121.2524 | -6.6788 | 114.5004 | 1.4211e-13 | -0.025141 | 0.0047714 | 0.072041 | -0.0095016 | 0.065095 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016754 | 0.03685 | 0.0065869 | 1.3013 | 28.7092 | -1.3086 | 114.7545 | 114.7711 | 114.8451 | -6.5789 | 0.02852 | -0.00422 | -0.042615 | 0.070773 | 0.21059 | -0.14792 | -0.27404 | 0.099905 | 0.25405 | 7.9801 | 5.3701 | 5.2702 | 0.27068 | 0.34469 | 6.4047 | -114.4297 | 6.7073 | 6.6362 | 0.23142 | -114.2898 | -114.6483 | 121.4333 | 121.4499 | 121.5239 | 35.388 | -121.0793 | 6.7495 | 6.8894 | 6.5309 | 6.6746 | -114.7745
2601.4219 | 121.1243 | -6.2393 | 115.0452 | 1.4211e-13 | -0.024286 | 0.0047714 | 0.071827 | -0.0097152 | 0.065308 | 0.015566 | -0.0031575 | 0.0047004 | 0.016968 | 0.037278 | 0.0065869 | 0.55961 | 28.5444 | -2.1098 | 113.761 | 113.7683 | 113.8561 | -7.5771 | 0.033099 | -0.013377 | -0.033458 | 0.075351 | 0.20601 | -0.14792 | -0.26946 | -1.3378 | -1.2842 | 6.7989 | 4.1295 | 5.4672 | -1.2768 | -1.189 | 5.9699 | -114.9698 | 6.2724 | 6.2059 | 0.236 | -114.8392 | -115.1931 | 120.0003 | 120.0076 | 120.0955 | 34.7837 | -122.6222 | 6.3147 | 6.4453 | 6.0914 | 6.2259 | -115.3146
2603.1719 | 121.3028 | -6.5048 | 114.6744 | 1.4211e-13 | -0.024072 | 0.004985 | 0.072255 | -0.0097152 | 0.065736 | 0.0079357 | -0.0033713 | 0.0044868 | 0.017395 | 0.037491 | 0.0065869 | 1.7729 | 30.0554 | -0.95154 | 114.7453 | 114.7574 | 114.8405 | -6.6018 | 0.033099 | 0.000359 | -0.038036 | 0.075351 | 0.20601 | -0.14792 | -0.26488 | -0.09694 | 0.070945 | 8.2777 | 5.5533 | 5.6502 | 0.082989 | 0.16616 | 6.2399 | -114.599 | 6.5379 | 6.4668 | 0.22685 | -114.4684 | -114.8223 | 121.2501 | 121.2622 | 121.3454 | 36.5602 | -121.2761 | 6.5802 | 6.7108 | 6.3569 | 6.5052 | -114.9393
2604.9219 | 121.2845 | -6.459 | 114.7385 | 1.4211e-13 | -0.023645 | 0.004985 | 0.072255 | -0.009288 | 0.066377 | -0.0073253 | -0.0035849 | 0.0049142 | 0.017395 | 0.037064 | 0.0065869 | 2.0247 | 30.646 | -0.73178 | 114.7865 | 114.794 | 114.8817 | -6.5834 | 0.02852 | -0.008798 | -0.038036 | 0.07993 | 0.21059 | -0.15708 | -0.26488 | -0.1244 | 0.048063 | 8.4837 | 5.7273 | 5.8517 | 0.055533 | 0.14328 | 6.1942 | -114.6585 | 6.4876 | 6.421 | 0.22685 | -114.5279 | -114.8955 | 121.2456 | 121.253 | 121.3408 | 37.105 | -121.3219 | 6.539 | 6.6696 | 6.302 | 6.4502 | -115.0033
2606.6094 | 121.2296 | -6.2393 | 114.9811 | 1.4211e-13 | -0.023218 | 0.004985 | 0.072041 | -0.0090744 | 0.066377 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017182 | 0.037278 | 0.0068005 | 2.6428 | 31.6258 | -0.19154 | 115.1528 | 115.174 | 115.2572 | -6.2171 | 0.037677 | -0.008798 | -0.042615 | 0.07993 | 0.20601 | -0.1525 | -0.26488 | 0.022187 | 0.17172 | 8.8821 | 6.0478 | 6.0256 | 0.19297 | 0.27611 | 5.9744 | -114.9011 | 6.277 | 6.1967 | 0.22227 | -114.7751 | -115.1336 | 121.3921 | 121.4134 | 121.4965 | 37.8651 | -121.1982 | 6.3192 | 6.4453 | 6.0868 | 6.2305 | -115.246
2608.3594 | 121.2799 | -5.7861 | 115.4388 | 1.4211e-13 | -0.023218 | 0.0051988 | 0.072041 | -0.008647 | 0.066804 | 0.00030522 | -0.0029439 | 0.0049142 | 0.017395 | 0.037064 | 0.0063733 | 3.2105 | 32.6239 | 0.26171 | 115.4687 | 115.4763 | 115.5548 | -5.9103 | 0.033099 | -0.00422 | -0.038036 | 0.07993 | 0.20601 | -0.15708 | -0.26946 | -0.12421 | 0.029864 | 8.9966 | 6.0478 | 6.1721 | 0.037414 | 0.11596 | 5.5167 | -115.3589 | 5.8192 | 5.7481 | 0.23143 | -115.2328 | -115.5959 | 121.2548 | 121.2624 | 121.3409 | 38.4101 | -121.3492 | 5.8661 | 5.9921 | 5.6291 | 5.7819 | -115.7083
2610.1094 | 121.225 | -5.8594 | 115.4022 | 1.4211e-13 | -0.022577 | 0.0051988 | 0.072682 | -0.0084334 | 0.066804 | 0.015566 | -0.0033713 | 0.0047004 | 0.016968 | 0.037278 | 0.0063733 | 3.5127 | 33.3062 | 0.4952 | 115.5099 | 115.522 | 115.6006 | -5.8874 | 0.023941 | -0.00422 | -0.033458 | 0.066194 | 0.21059 | -0.14792 | -0.26488 | -0.028074 | 0.10769 | 9.372 | 6.3546 | 6.3826 | 0.11982 | 0.19836 | 5.5945 | -115.336 | 5.8833 | 5.8259 | 0.23142 | -115.1916 | -115.5501 | 121.3693 | 121.3814 | 121.46 | 39.1655 | -121.2897 | 5.9256 | 6.07 | 5.7115 | 5.8552 | -115.6671
2611.875 | 121.3211 | -6.8848 | 114.3631 | 1.4211e-13 | -0.022363 | 0.0051988 | 0.072255 | -0.0084334 | 0.067231 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.037491 | 0.0065869 | 2.7939 | 33.0543 | -0.22817 | 114.5164 | 114.5238 | 114.6116 | -6.8857 | 0.019362 | -0.00422 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.26946 | -0.000889 | 0.15331 | 9.6786 | 6.6566 | 6.6575 | 0.16074 | 0.24851 | 6.6153 | -114.2923 | 6.9041 | 6.8422 | 0.22685 | -114.1571 | -114.5156 | 121.4012 | 121.4086 | 121.4964 | 39.9391 | -121.2488 | 6.9555 | 7.0908 | 6.7323 | 6.8805 | -114.6326
2613.6094 | 121.2112 | -6.1661 | 115.1459 | 1.4211e-13 | -0.021936 | 0.004985 | 0.072469 | -0.008647 | 0.067018 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017395 | 0.037278 | 0.0068005 | 3.357 | 33.8419 | 0.21593 | 114.8415 | 114.8306 | 114.9275 | -6.5834 | 0.033099 | -0.008798 | -0.033458 | 0.061616 | 0.20143 | -0.1525 | -0.26946 | -0.41737 | -0.30441 | 9.5231 | 6.382 | 6.7994 | -0.31525 | -0.21834 | 5.8966 | -115.0843 | 6.1992 | 6.1326 | 0.236 | -114.9444 | -115.2984 | 121.0075 | 120.9967 | 121.0936 | 40.0079 | -121.7293 | 6.2277 | 6.3675 | 6.0136 | 6.1573 | -115.4153
2615.3125 | 121.3394 | -6.015 | 115.2374 | 1.4211e-13 | -0.021936 | 0.0051988 | 0.072682 | -0.0084334 | 0.067659 | -0.0073253 | -0.0033713 | 0.0049142 | 0.017609 | 0.037491 | 0.0063733 | 4.0712 | 34.7484 | 0.87978 | 115.3314 | 115.3435 | 115.422 | -6.0935 | 0.033099 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.26488 | -0.078486 | 0.093929 | 10.0862 | 6.8948 | 6.9733 | 0.10604 | 0.18459 | 5.7501 | -115.1712 | 6.0481 | 5.9678 | 0.21769 | -115.0268 | -115.3899 | 121.3464 | 121.3585 | 121.437 | 40.7634 | -121.3309 | 6.0812 | 6.2256 | 5.8625 | 6.0016 | -115.5023
2617.0625 | 121.2479 | -6.2576 | 115.0909 | 1.4211e-13 | -0.021508 | 0.0054124 | 0.072896 | -0.0082196 | 0.0683 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.037064 | 0.0068005 | 4.2177 | 35.0598 | 0.96676 | 115.2398 | 115.2473 | 115.3396 | -6.1897 | 0.02852 | -0.008798 | -0.038036 | 0.061616 | 0.21059 | -0.14334 | -0.2603 | 0.067971 | 0.14885 | 10.4754 | 7.2244 | 7.1564 | 0.15637 | 0.24866 | 5.9973 | -115.0293 | 6.2861 | 6.2196 | 0.22227 | -114.8804 | -115.2343 | 121.4974 | 121.5049 | 121.5972 | 41.3174 | -121.2806 | 6.3192 | 6.4682 | 6.1143 | 6.2488 | -115.3512
2618.75 | 121.3394 | -6.0974 | 115.1367 | 1.4211e-13 | -0.021295 | 0.0051988 | 0.072682 | -0.008006 | 0.068086 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.037064 | 0.0065869 | 4.4192 | 35.3482 | 1.1316 | 115.2398 | 115.2565 | 115.3396 | -6.1897 | 0.02852 | -0.008798 | -0.042615 | 0.070773 | 0.21059 | -0.15708 | -0.26946 | -0.092246 | 0.10307 | 10.5166 | 7.229 | 7.3212 | 0.11975 | 0.20289 | 5.828 | -115.0659 | 6.1259 | 6.0548 | 0.22685 | -114.9261 | -115.2938 | 121.3372 | 121.3539 | 121.437 | 41.4456 | -121.3264 | 6.1682 | 6.308 | 5.9403 | 6.0886 | -115.4062
2620.5 | 121.312 | -6.3034 | 115.036 | 1.4211e-13 | -0.020867 | 0.0054124 | 0.072896 | -0.008006 | 0.068513 | 0.00030522 | -0.0033713 | 0.0049142 | 0.016968 | 0.037064 | 0.0065869 | 4.3047 | 35.2704 | 0.96219 | 114.9193 | 114.9176 | 115.0099 | -6.5377 | 0.02852 | -0.00422 | -0.047194 | 0.070773 | 0.20601 | -0.1525 | -0.26946 | -0.23425 | -0.11671 | 10.6081 | 7.2656 | 7.4998 | -0.11838 | -0.026065 | 6.0339 | -114.9652 | 6.3319 | 6.2562 | 0.22227 | -114.83 | -115.1885 | 121.2227 | 121.221 | 121.3134 | 41.5738 | -121.5737 | 6.3742 | 6.5094 | 6.1509 | 6.2992 | -115.3055
2622.25 | 121.3074 | -6.7062 | 114.6332 | 1.4211e-13 | -0.020654 | 0.0056262 | 0.072896 | -0.0082196 | 0.068727 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017395 | 0.037278 | 0.0068005 | 4.3276 | 35.2933 | 0.93929 | 114.7224 | 114.7345 | 114.8222 | -6.7254 | 0.02852 | -0.008798 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.26488 | -0.019154 | 0.089251 | 11.0339 | 7.6455 | 7.6647 | 0.10129 | 0.18904 | 6.4414 | -114.5624 | 6.7348 | 6.6682 | 0.22685 | -114.4226 | -114.7857 | 121.4287 | 121.4407 | 121.5285 | 41.9995 | -121.3586 | 6.777 | 6.9168 | 6.5537 | 6.6974 | -114.8981
2623.9375 | 121.3348 | -6.6238 | 114.6835 | 1.4211e-13 | -0.020654 | 0.0054124 | 0.073323 | -0.007365 | 0.069154 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.037278 | 0.0068005 | 4.6161 | 35.5817 | 1.2003 | 114.8415 | 114.8535 | 114.9367 | -6.6201 | 0.033099 | -0.017956 | -0.042615 | 0.066194 | 0.21516 | -0.1525 | -0.26946 | 0.003763 | 0.15794 | 11.2399 | 7.8241 | 7.8203 | 0.16999 | 0.25316 | 6.3544 | -114.6173 | 6.6569 | 6.5812 | 0.22685 | -114.4684 | -114.836 | 121.4653 | 121.4774 | 121.5605 | 42.2056 | -121.3036 | 6.69 | 6.839 | 6.4713 | 6.6059 | -114.953
2625.7031 | 121.2891 | -6.4362 | 114.9536 | 1.4211e-13 | -0.020013 | 0.0054124 | 0.072896 | -0.0075786 | 0.069154 | 0.015566 | -0.0031575 | 0.0047004 | 0.017182 | 0.037278 | 0.0065869 | 4.9961 | 35.9114 | 1.5436 | 115.0383 | 115.0413 | 115.1244 | -6.4369 | 0.037677 | -0.00422 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.26488 | -0.000763 | 0.084726 | 11.4322 | 7.9798 | 7.9805 | 0.087646 | 0.1708 | 6.1713 | -114.8874 | 6.4738 | 6.3981 | 0.22685 | -114.743 | -115.1061 | 121.4745 | 121.4774 | 121.5606 | 42.3475 | -121.3905 | 6.5024 | 6.6467 | 6.2837 | 6.4319 | -115.2185
2627.4062 | 121.2753 | -6.4041 | 114.9673 | 1.4211e-13 | -0.020013 | 0.0056262 | 0.072896 | -0.0075786 | 0.069368 | -0.0073253 | -0.0029439 | 0.0044868 | 0.016968 | 0.037278 | 0.0063733 | 5.2525 | 36.1541 | 1.8092 | 115.1208 | 115.1283 | 115.2114 | -6.3866 | 0.023941 | -0.00422 | -0.042615 | 0.070773 | 0.21059 | -0.14792 | -0.2603 | 0.017562 | 0.1534 | 11.6566 | 8.2133 | 8.1957 | 0.16091 | 0.24406 | 6.1438 | -114.8966 | 6.4281 | 6.3615 | 0.21769 | -114.7568 | -115.1153 | 121.5249 | 121.5324 | 121.6155 | 42.5582 | -121.3539 | 6.4749 | 6.6147 | 6.2562 | 6.3999 | -115.2277
2629.1719 | 121.3165 | -6.6376 | 114.7797 | 1.4211e-13 | -0.019585 | 0.0056262 | 0.072896 | -0.007365 | 0.069795 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017395 | 0.037491 | 0.0065869 | 5.2799 | 36.1953 | 1.768 | 114.9513 | 114.968 | 115.0512 | -6.5239 | 0.033099 | -0.008798 | -0.042615 | 0.061616 | 0.21059 | -0.1525 | -0.26946 | 0.11365 | 0.17169 | 11.9175 | 8.4055 | 8.2919 | 0.18833 | 0.27149 | 6.3681 | -114.718 | 6.6707 | 6.595 | 0.22685 | -114.5691 | -114.9322 | 121.5889 | 121.6056 | 121.6887 | 42.8328 | -121.3036 | 6.6992 | 6.8482 | 6.4851 | 6.6288 | -115.0491
2630.875 | 121.2845 | -10.2402 | 111.1084 | 1.4211e-13 | -0.019158 | 0.0058398 | 0.07311 | -0.007365 | 0.069795 | -0.0073253 | -0.0035849 | 0.0047004 | 0.017609 | 0.037705 | 0.0063733 | 1.8507 | 33.0177 | -1.6703 | 111.2429 | 111.2545 | 111.3471 | -10.2191 | 0.02852 | -0.00422 | -0.038036 | 0.070773 | 0.20601 | -0.16166 | -0.2603 | 0.021061 | 0.13446 | 12.0909 | 8.5698 | 8.5488 | 0.14609 | 0.23867 | 9.9799 | -111.0376 | 10.2687 | 10.2021 | 0.22227 | -110.9024 | -111.2701 | 121.483 | 121.4947 | 121.5872 | 43.2579 | -121.3275 | 10.3109 | 10.4462 | 10.0785 | 10.236 | -111.3687
2632.625 | 121.4355 | -9.6909 | 111.6074 | 1.4211e-13 | -0.019372 | 0.0056262 | 0.07311 | -0.0071514 | 0.070222 | 0.00030522 | -0.0027303 | 0.0047004 | 0.017182 | 0.037278 | 0.0065869 | 2.4917 | 33.5259 | -1.0339 | 111.719 | 111.7307 | 111.8232 | -9.7521 | 0.042256 | -0.008798 | -0.038036 | 0.066194 | 0.21059 | -0.12503 | -0.2603 | -0.061205 | 0.11165 | 12.1825 | 8.6569 | 8.7181 | 0.12334 | 0.21588 | 9.4306 | -111.5412 | 9.7331 | 9.6528 | 0.22227 | -111.3968 | -111.7324 | 121.4099 | 121.4216 | 121.5141 | 43.2168 | -121.3594 | 9.7571 | 9.9014 | 9.5658 | 9.6821 | -111.8677
2634.3125 | 121.3623 | -8.963 | 112.3856 | 1.4211e-13 | -0.018944 | 0.0056262 | 0.07311 | -0.0069376 | 0.070436 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017182 | 0.037491 | 0.0065869 | 2.9312 | 33.8922 | -0.62648 | 111.9846 | 112.0054 | 112.0842 | -9.4911 | 0.02852 | -0.008798 | -0.047194 | 0.070773 | 0.21516 | -0.15708 | -0.26946 | -0.52805 | -0.401 | 11.8942 | 8.3365 | 8.8646 | -0.38013 | -0.30134 | 8.6936 | -112.3148 | 8.9915 | 8.9158 | 0.22227 | -112.1704 | -112.5426 | 120.9476 | 120.9684 | 121.0472 | 42.8552 | -121.8766 | 9.0338 | 9.1782 | 8.8059 | 8.9542 | -112.655
2636.0781 | 121.3623 | -7.4615 | 113.9053 | 1.4211e-13 | -0.018517 | 0.0058398 | 0.07311 | -0.006724 | 0.070436 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017395 | 0.037278 | 0.0063733 | 5.17 | 35.774 | 1.507 | 114.0311 | 114.0522 | 114.1309 | -7.5359 | 0.033099 | -0.008798 | -0.042615 | 0.07993 | 0.21059 | -0.14792 | -0.26488 | -0.074314 | 0.12576 | 12.6316 | 8.9685 | 9.0429 | 0.14688 | 0.22552 | 7.1967 | -113.8254 | 7.4946 | 7.4189 | 0.22227 | -113.6947 | -114.0533 | 121.4926 | 121.5138 | 121.5924 | 43.2356 | -121.4412 | 7.5415 | 7.6721 | 7.3136 | 7.4527 | -114.1702
2637.7656 | 121.431 | -6.4911 | 114.8254 | 1.4211e-13 | -0.01873 | 0.0058398 | 0.073537 | -0.006724 | 0.070222 | 0.0079357 | -0.0033713 | 0.0047004 | 0.017182 | 0.037278 | 0.0068005 | 5.6508 | 36.1632 | 1.9694 | 114.3928 | 114.4048 | 114.4971 | -7.1192 | 0.02852 | -0.008798 | -0.042615 | 0.061616 | 0.20601 | -0.14792 | -0.2603 | -0.62809 | -0.43265 | 12.1419 | 8.4605 | 9.0886 | -0.42065 | -0.3283 | 6.2308 | -114.7638 | 6.5196 | 6.4485 | 0.21769 | -114.6194 | -114.9734 | 120.8839 | 120.8959 | 120.9882 | 42.6543 | -121.9446 | 6.5527 | 6.6971 | 6.3432 | 6.4823 | -115.0857
2639.5156 | 121.376 | -7.0129 | 114.3951 | 1.4211e-13 | -0.018303 | 0.0064808 | 0.073323 | -0.006724 | 0.070436 | 0.015566 | -0.0031575 | 0.0044868 | 0.017182 | 0.037278 | 0.0063733 | 6.3879 | 36.6989 | 2.7294 | 114.9651 | 114.9955 | 115.0695 | -6.5514 | 0.033099 | -0.008798 | -0.042615 | 0.061616 | 0.20601 | -0.1525 | -0.2603 | 0.46155 | 0.56994 | 13.4008 | 9.7423 | 9.2808 | 0.60033 | 0.67433 | 6.7526 | -114.3335 | 7.046 | 6.9703 | 0.21769 | -114.1891 | -114.5476 | 121.978 | 122.0084 | 122.0824 | 43.7118 | -120.9465 | 7.0746 | 7.2189 | 6.8604 | 7.0041 | -114.6554
2641.2656 | 120.7901 | -120.1538 | 0.56763 | 1.4211e-13 | -0.019799 | 0.0039166 | 0.071186 | -0.005442 | 0.073855 | 0.00030522 | -0.0031575 | 0.0042732 | 0.017395 | 0.037278 | 0.0065869 | -104.4457 | -64.9323 | -108.8479 | 1.1784 | 1.2138 | 1.4606 | -119.7607 | 0.060571 | 0.027831 | -0.005985 | 0.098244 | 0.24264 | 0.090166 | -0.23283 | 0.39308 | 0.61078 | 15.7081 | 11.3059 | 10.9129 | 0.64615 | 0.89298 | 119.921 | -0.46938 | 120.2144 | 120.1478 | 0.22685 | -0.32499 | -0.47746 | 121.3322 | 121.3676 | 121.6144 | 55.2215 | -120.3284 | 120.2521 | 120.3964 | 120.244 | 120.1816 | -0.80046
2642.9531 | 120.932 | -118.7897 | 2.1469 | 1.4211e-13 | -0.019372 | 0.004344 | 0.0714 | -0.0050148 | 0.074496 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017182 | 0.037278 | 0.0063733 | -104.2214 | -64.914 | -108.6373 | 1.4119 | 1.4519 | 1.7033 | -119.747 | 0.060571 | 0.023253 | -0.001407 | 0.10282 | 0.24721 | 0.044379 | -0.23283 | -0.95731 | -0.735 | 14.5683 | 10.1524 | 11.1097 | -0.69503 | -0.44364 | 118.5568 | -2.0441 | 118.8502 | 118.7883 | 0.23142 | -1.8997 | -2.1025 | 120.2016 | 120.2416 | 120.4929 | 53.8757 | -121.8939 | 118.8925 | 119.0369 | 118.8341 | 118.8129 | -2.3797
2644.7031 | 121.4447 | -76.5244 | 44.2017 | 1.4211e-13 | -0.019158 | 0.0039166 | 0.071827 | -0.0052284 | 0.074282 | -0.0073253 | -0.0035849 | 0.0047004 | 0.017609 | 0.037491 | 0.0065869 | -86.6221 | -49.0858 | -90.9468 | 19.231 | 19.3692 | 19.4911 | -101.8709 | 0.055992 | 0.023253 | -0.005985 | 0.089087 | 0.2289 | -0.0243 | -0.22825 | -25.3465 | -24.9707 | -10.0977 | -14.4224 | 10.9241 | -24.8324 | -24.7105 | 76.2961 | -44.1126 | 76.5803 | 76.5184 | 0.22227 | -43.9728 | -44.226 | 95.7553 | 95.8936 | 96.0155 | 27.4386 | -146.0725 | 76.6134 | 76.7533 | 76.5001 | 76.5476 | -44.4299
2646.4688 | 95.0912 | -5.9418 | 89.1174 | 1.4211e-13 | -0.017662 | 0.0064808 | 0.073537 | -0.0065104 | 0.071077 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017395 | 0.037278 | 0.0068005 | 7.5188 | 36.9095 | 3.7732 | 115.0612 | 115.0916 | 115.1336 | -6.1851 | 0.02852 | -0.008798 | -0.033458 | 0.070773 | 0.20143 | -0.1525 | -0.2603 | -0.24331 | 25.9438 | 13.4605 | 9.715 | 9.9583 | 25.9742 | 26.0161 | 5.6815 | -89.0467 | 5.9703 | 5.9083 | 0.22685 | -88.916 | -89.2699 | 121.003 | 121.0334 | 121.0753 | 42.8513 | -95.3025 | 6.0125 | 6.1432 | 5.7893 | 5.933 | -89.3777
2648.1719 | 119.0323 | -79.9393 | 38.887 | 1.4211e-13 | -0.018303 | 0.0054124 | 0.072469 | -0.0062966 | 0.072786 | 0.015566 | -0.0033713 | 0.0044868 | 0.016968 | 0.037491 | 0.0068005 | -39.7348 | -6.3674 | -43.3052 | 67.4277 | 66.9442 | 67.9785 | -54.4332 | 0.051413 | 0.009516 | -0.0243 | 0.07993 | 0.22432 | 0.012329 | -0.25115 | 25.5061 | 28.5407 | 40.2045 | 36.6341 | 11.128 | 28.0572 | 29.0915 | 79.6881 | -38.8071 | 79.9907 | 79.915 | 0.22685 | -38.6627 | -38.8747 | 147.367 | 146.8835 | 147.9178 | 73.5718 | -93.3202 | 80.0192 | 80.1636 | 79.9516 | 79.9488 | -39.1382
2649.9219 | 120.7352 | -118.0481 | 2.3895 | 1.4211e-13 | -0.018944 | 0.004344 | 0.0714 | -0.004801 | 0.075137 | 0.00030522 | -0.0033713 | 0.0049142 | 0.017182 | 0.037491 | 0.0065869 | -101.1676 | -63.1055 | -105.6202 | 3.3577 | 3.4025 | 3.64 | -117.3431 | 0.074307 | 0.027831 | 0.003172 | 0.11656 | 0.26095 | 0.030644 | -0.2191 | 0.70504 | 0.9682 | 16.8805 | 12.4279 | 11.7229 | 1.013 | 1.2505 | 117.829 | -2.273 | 118.1224 | 118.0513 | 0.22227 | -2.1286 | -2.3589 | 121.4058 | 121.4506 | 121.6881 | 54.9426 | -119.7326 | 118.1647 | 118.309 | 118.0787 | 118.0759 | -2.6086
2651.6719 | 120.1492 | -4.3396 | 105.9814 | 1.4211e-13 | -0.017021 | 0.0062672 | 0.073751 | -0.006083 | 0.071504 | 0.015566 | -0.0031575 | 0.0049142 | 0.017182 | 0.037705 | 0.0061595 | 9.341 | 38.1274 | 5.5542 | 115.9998 | 116.0211 | 116.0951 | -4.816 | 0.019362 | -0.008798 | -0.051772 | 0.066194 | 0.20143 | -0.15708 | -0.27404 | -0.47638 | 10.0184 | 13.6806 | 9.8938 | 10.3702 | 10.0397 | 10.1136 | 4.0656 | -105.9153 | 4.359 | 4.2878 | 0.22227 | -105.78 | -106.1385 | 120.3394 | 120.3607 | 120.4347 | 42.467 | -110.7974 | 4.4058 | 4.541 | 4.1825 | 4.3308 | -106.2555
2653.3594 | 120.607 | -3.6484 | 117.1188 | 1.4211e-13 | -0.016807 | 0.0069082 | 0.073751 | -0.0058694 | 0.071932 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017182 | 0.037278 | 0.0068005 | 10.5313 | 39.0294 | 6.7079 | 117.1123 | 117.1292 | 117.2123 | -3.8132 | 0.014784 | -0.017956 | -0.051772 | 0.057037 | 0.19685 | -0.1525 | -0.27862 | -0.16482 | -0.006486 | 14.1797 | 10.3563 | 10.5211 | 0.010414 | 0.093419 | 3.3698 | -117.0618 | 3.6632 | 3.5966 | 0.22685 | -116.922 | -117.2713 | 120.7607 | 120.7776 | 120.8606 | 42.6778 | -120.932 | 3.7054 | 3.8452 | 3.4959 | 3.6304 | -117.3975
2655.1094 | 96.4096 | -4.2068 | 107.4463 | 1.4211e-13 | -0.016594 | 0.0066946 | 0.073964 | -0.005442 | 0.071932 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.037491 | 0.0068005 | 10.3757 | 38.7501 | 6.5248 | 116.8605 | 116.882 | 116.9696 | -4.12 | 0.019362 | -0.008798 | -0.056351 | 0.061616 | 0.20143 | -0.1525 | -0.27404 | 0.086864 | 9.4142 | 14.5825 | 10.7316 | 10.6448 | 9.4357 | 9.5233 | 3.9328 | -107.3847 | 4.2262 | 4.1505 | 0.21769 | -107.2449 | -107.5988 | 121.0674 | 121.0888 | 121.1764 | 42.957 | -111.5663 | 4.2685 | 4.4083 | 4.0543 | 4.1981 | -107.7203
2656.8594 | 98.4879 | -5.2643 | 114.8575 | 1.4211e-13 | -0.016807 | 0.0071218 | 0.073751 | -0.005442 | 0.072573 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017395 | 0.037491 | 0.0065869 | 9.1761 | 37.5368 | 5.2932 | 115.5053 | 115.522 | 115.6097 | -5.5211 | 0.02852 | -0.017956 | -0.051772 | 0.057037 | 0.19685 | -0.15708 | -0.27404 | -0.25685 | 0.64785 | 14.4404 | 10.5575 | 10.8144 | 0.66456 | 0.75226 | 4.9902 | -114.8004 | 5.2928 | 5.2125 | 0.22227 | -114.6606 | -115.0146 | 120.7696 | 120.7863 | 120.874 | 42.8011 | -120.3786 | 5.3213 | 5.4611 | 5.1072 | 5.2463 | -115.1315
2658.6094 | 120.4147 | -18.663 | 101.6006 | 1.4211e-13 | -0.016594 | 0.0069082 | 0.073751 | -0.0052284 | 0.073 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.037491 | 0.0065869 | -3.4923 | 25.7606 | -7.5122 | 102.3745 | 102.408 | 102.5058 | -18.626 | 0.02852 | -0.00422 | -0.038036 | 0.061616 | 0.21059 | -0.1525 | -0.26946 | 0.037008 | 0.77387 | 15.1708 | 11.1508 | 11.1138 | 0.80736 | 0.90514 | 18.3936 | -101.539 | 18.6915 | 18.625 | 0.23143 | -101.3901 | -101.7531 | 121.0375 | 121.071 | 121.1688 | 44.4236 | -120.2267 | 18.7246 | 18.8736 | 18.5105 | 18.6588 | -101.8701
2660.3594 | 120.5521 | -14.8727 | 105.2673 | 1.4211e-13 | -0.016166 | 0.0064808 | 0.073751 | -0.0050148 | 0.073427 | 0.00030522 | -0.0029439 | 0.0047004 | 0.016968 | 0.037278 | 0.0063733 | 0.16587 | 28.9153 | -3.7626 | 105.9731 | 105.9887 | 106.0908 | -15.0178 | 0.023941 | -0.00422 | -0.047194 | 0.052459 | 0.20143 | -0.12961 | -0.27404 | -0.14508 | 0.7058 | 15.0386 | 11.1101 | 11.2552 | 0.72139 | 0.82349 | 14.5987 | -105.2149 | 14.8967 | 14.8255 | 0.22685 | -105.0659 | -105.3969 | 120.8459 | 120.8615 | 120.9636 | 43.788 | -120.2852 | 14.9252 | 15.0742 | 14.7431 | 14.8685 | -105.5414
2662.125 | 91.3559 | -14.4424 | 80.983 | 1.4211e-13 | -0.016166 | 0.0066946 | 0.073751 | -0.0045874 | 0.073214 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016968 | 0.037705 | 0.0063733 | 0.67865 | 29.3136 | -3.204 | 106.4127 | 106.4191 | 106.5258 | -14.6149 | 0.033099 | -0.008798 | -0.042615 | 0.066194 | 0.21059 | -0.14334 | -0.26946 | -0.17244 | 25.4297 | 15.1211 | 11.2384 | 11.4108 | 25.4362 | 25.5428 | 14.173 | -80.9168 | 14.4755 | 14.3998 | 0.22685 | -80.7724 | -81.1263 | 120.8551 | 120.8616 | 120.9682 | 43.7561 | -95.5979 | 14.5086 | 14.653 | 14.2991 | 14.4336 | -81.2524
2663.8125 | 95.3934 | -14.4516 | 91.2323 | 1.4211e-13 | -0.016166 | 0.0066946 | 0.073537 | -0.004801 | 0.073427 | -0.0073253 | -0.0031575 | 0.0044868 | 0.017182 | 0.037919 | 0.0061595 | 0.62371 | 29.0572 | -3.2681 | 106.2387 | 106.2543 | 106.3472 | -14.8118 | 0.02852 | -0.013377 | -0.042615 | 0.061616 | 0.20601 | -0.1525 | -0.26946 | -0.36017 | 15.0064 | 15.0753 | 11.1835 | 11.5436 | 15.022 | 15.1149 | 14.1821 | -91.1707 | 14.4801 | 14.409 | 0.22685 | -91.0263 | -91.3848 | 120.6903 | 120.7059 | 120.7988 | 43.5088 | -106.0441 | 14.5132 | 14.6576 | 14.2991 | 14.4382 | -91.5018
2665.5625 | 120.9686 | -15.7745 | 105.0888 | 1.4211e-13 | -0.015525 | 0.0066946 | 0.074178 | -0.0045874 | 0.073641 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017182 | 0.037705 | 0.0065869 | -0.18209 | 28.1232 | -4.1426 | 105.1948 | 105.2057 | 105.3125 | -15.8649 | 0.023941 | 0.000359 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.26946 | -0.09039 | 0.106 | 15.5924 | 11.6319 | 11.7223 | 0.11692 | 0.22366 | 15.5051 | -105.0272 | 15.7985 | 15.7273 | 0.22227 | -104.8828 | -105.2413 | 120.9693 | 120.9803 | 121.087 | 43.8977 | -120.9537 | 15.8362 | 15.9805 | 15.622 | 15.7749 | -105.3583
2667.3281 | 120.195 | -17.2211 | 103.0701 | 1.4211e-13 | -0.015525 | 0.0064808 | 0.073964 | -0.004801 | 0.073855 | 0.015566 | -0.0033713 | 0.0051278 | 0.017182 | 0.037491 | 0.0061595 | -1.5922 | 26.6351 | -5.6443 | 103.5512 | 103.5711 | 103.6687 | -17.5317 | 0.033099 | -0.008798 | -0.038036 | 0.070773 | 0.21516 | -0.1525 | -0.27404 | -0.31058 | 0.4811 | 15.6288 | 11.5768 | 11.8874 | 0.50099 | 0.59868 | 16.947 | -102.9993 | 17.2542 | 17.183 | 0.236 | -102.8549 | -103.2226 | 120.7722 | 120.7921 | 120.8898 | 43.8562 | -120.6017 | 17.2918 | 17.4362 | 17.0686 | 17.2123 | -103.3441
2669.0156 | 120.845 | -16.8137 | 104.1046 | 1.4211e-13 | -0.015525 | 0.0069082 | 0.073964 | -0.0045874 | 0.073855 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017182 | 0.037278 | 0.0063733 | -0.84595 | 27.1159 | -4.9117 | 104.128 | 104.1526 | 104.2457 | -16.9684 | 0.023941 | -0.008798 | -0.042615 | 0.052459 | 0.21059 | -0.1525 | -0.26488 | -0.15479 | 0.023427 | 15.9677 | 11.9019 | 12.0567 | 0.047963 | 0.14104 | 16.5488 | -104.0522 | 16.8376 | 16.771 | 0.22227 | -103.894 | -104.2571 | 120.9417 | 120.9662 | 121.0593 | 43.9296 | -121.0731 | 16.8661 | 17.0242 | 16.6612 | 16.8049 | -104.3695
2670.7812 | 121.1334 | -18.3975 | 102.5391 | 1.4211e-13 | -0.015312 | 0.0071218 | 0.074392 | -0.00416 | 0.074068 | -0.0073253 | -0.0033713 | 0.0044868 | 0.017182 | 0.037491 | 0.0065869 | -2.1187 | 25.7652 | -6.2349 | 102.663 | 102.6782 | 102.7897 | -18.452 | 0.02852 | -0.00422 | -0.042615 | 0.070773 | 0.20601 | -0.12503 | -0.27404 | -0.054496 | 0.12389 | 16.2788 | 12.1627 | 12.2171 | 0.1391 | 0.25059 | 18.1235 | -102.4683 | 18.426 | 18.3549 | 0.23142 | -102.3331 | -102.6641 | 121.0605 | 121.0757 | 121.1872 | 44.1627 | -120.9911 | 18.4683 | 18.6035 | 18.2725 | 18.3933 | -102.8131
2672.5625 | 120.4926 | -18.8141 | 102.2278 | 1.4211e-13 | -0.015098 | 0.0071218 | 0.074392 | -0.0039464 | 0.074496 | -0.0073253 | -0.0031575 | 0.0047004 | 0.017182 | 0.037491 | 0.0061595 | -2.2332 | 25.4768 | -6.3814 | 102.3516 | 102.376 | 102.4737 | -18.768 | 0.02852 | -0.008798 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.26946 | 0.046123 | 0.12384 | 16.5809 | 12.4327 | 12.3866 | 0.14817 | 0.24595 | 18.5446 | -102.157 | 18.8426 | 18.7761 | 0.23143 | -102.0172 | -102.3803 | 121.1657 | 121.19 | 121.2878 | 44.2908 | -120.9957 | 18.8849 | 19.0247 | 18.6616 | 18.8053 | -102.4972
2674.25 | 104.4937 | -17.2028 | 102.8961 | 1.4211e-13 | -0.014457 | 0.0073356 | 0.074605 | -0.0039464 | 0.075137 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016968 | 0.037705 | 0.0063733 | -0.85511 | 26.6306 | -4.9713 | 103.6473 | 103.6672 | 103.7603 | -17.4996 | 0.02852 | -0.00422 | -0.042615 | 0.066194 | 0.21516 | -0.1525 | -0.26946 | -0.29684 | 0.75119 | 16.3476 | 12.2315 | 12.5283 | 0.77109 | 0.8642 | 16.9333 | -102.8299 | 17.2313 | 17.1601 | 0.22685 | -102.681 | -103.0486 | 120.8501 | 120.87 | 120.9631 | 43.8333 | -120.3957 | 17.269 | 17.4179 | 17.0503 | 17.1985 | -103.1656
2676.0156 | 120.7764 | -17.2623 | 103.5004 | 1.4211e-13 | -0.014671 | 0.0071218 | 0.074605 | -0.00416 | 0.074709 | 0.0079357 | -0.0035849 | 0.0047004 | 0.017395 | 0.037491 | 0.0063733 | -0.66282 | 26.5939 | -4.811 | 103.6107 | 103.6306 | 103.7283 | -17.5408 | 0.023941 | -0.008798 | -0.051772 | 0.061616 | 0.20601 | -0.1525 | -0.2603 | -0.27854 | 0.11032 | 16.5994 | 12.4512 | 12.7298 | 0.13021 | 0.2279 | 17.002 | -103.4387 | 17.2862 | 17.2105 | 0.20853 | -103.2944 | -103.6529 | 120.873 | 120.8928 | 120.9905 | 43.8562 | -121.0412 | 17.3239 | 17.4683 | 17.1098 | 17.2535 | -103.7607
2677.7031 | 121.1792 | -18.924 | 102.0584 | 1.4211e-13 | -0.014243 | 0.0075492 | 0.074605 | -0.0039464 | 0.07535 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016968 | 0.037491 | 0.0063733 | -1.6792 | 25.4584 | -5.8732 | 102.3974 | 102.408 | 102.5149 | -18.7863 | 0.02852 | -0.008798 | -0.047194 | 0.066194 | 0.21516 | -0.16166 | -0.26946 | 0.13767 | 0.339 | 17.2447 | 13.0508 | 12.9131 | 0.34959 | 0.45653 | 18.6545 | -101.9922 | 18.9525 | 18.8768 | 0.22227 | -101.8432 | -102.2201 | 121.3214 | 121.332 | 121.4389 | 44.3824 | -120.8447 | 18.9901 | 19.1391 | 18.7623 | 18.9152 | -102.3279
2679.4531 | 120.5566 | -19.5648 | 101.0468 | 1.4211e-13 | -0.014243 | 0.0075492 | 0.074605 | -0.003519 | 0.07535 | 0.00030522 | -0.0029439 | 0.0044868 | 0.017182 | 0.037919 | 0.0063733 | -2.1966 | 24.7625 | -6.418 | 101.6694 | 101.6891 | 101.7915 | -19.5098 | 0.033099 | -0.013377 | -0.038036 | 0.066194 | 0.20601 | -0.15708 | -0.26946 | 0.055069 | 0.62269 | 17.3682 | 13.1468 | 13.0917 | 0.64236 | 0.74477 | 19.2954 | -100.9806 | 19.5979 | 19.5268 | 0.23143 | -100.8407 | -101.2038 | 121.2343 | 121.2539 | 121.3563 | 44.3273 | -120.5565 | 19.631 | 19.7708 | 19.4077 | 19.5514 | -101.3162
2681.2188 | 121.1655 | -19.7571 | 101.2802 | 1.4211e-13 | -0.01403 | 0.0075492 | 0.074819 | -0.003519 | 0.075778 | 0.015566 | -0.0031575 | 0.0049142 | 0.017609 | 0.037491 | 0.0065869 | -2.3614 | 24.4145 | -6.6149 | 101.2894 | 101.3091 | 101.4207 | -19.8944 | 0.02852 | -0.008798 | -0.047194 | 0.075351 | 0.20143 | -0.15708 | -0.27404 | -0.1373 | 0.009228 | 17.3957 | 13.1422 | 13.2795 | 0.028852 | 0.14044 | 19.483 | -101.2049 | 19.7856 | 19.7099 | 0.22685 | -101.0788 | -101.4373 | 121.0465 | 121.0661 | 121.1777 | 44.1716 | -121.1746 | 19.8324 | 19.9585 | 19.6 | 19.7483 | -101.5543
2682.9688 | 105.1392 | -9.343 | 111.5707 | 1.4211e-13 | -0.013816 | 0.007763 | 0.074819 | -0.0033054 | 0.075564 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017182 | 0.037705 | 0.0063733 | 7.9812 | 33.8235 | 3.7824 | 111.7053 | 111.717 | 111.8003 | -9.5369 | 0.019362 | -0.008798 | -0.047194 | 0.066194 | 0.20143 | -0.1525 | -0.27404 | -0.19389 | 0.13453 | 17.3241 | 13.1254 | 13.3193 | 0.14622 | 0.22961 | 9.0689 | -111.5045 | 9.3623 | 9.2958 | 0.22685 | -111.3693 | -111.7232 | 121.0482 | 121.0599 | 121.1433 | 43.1665 | -121.1076 | 9.4092 | 9.5444 | 9.1905 | 9.3342 | -111.8448
2684.6562 | 121.1197 | -8.5739 | 112.5641 | 1.4211e-13 | -0.013389 | 0.0079766 | 0.075246 | -0.003519 | 0.075991 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.037491 | 0.0065869 | 9.0983 | 34.6568 | 4.8904 | 112.6576 | 112.6831 | 112.7664 | -8.5982 | 0.023941 | -0.008798 | -0.047194 | 0.057037 | 0.19685 | -0.1525 | -0.27404 | -0.024259 | 0.09349 | 17.6722 | 13.4643 | 13.4885 | 0.11903 | 0.20234 | 8.2999 | -112.5071 | 8.5979 | 8.5267 | 0.22685 | -112.3672 | -112.7166 | 121.2315 | 121.257 | 121.3403 | 43.2308 | -121.1623 | 8.631 | 8.7708 | 8.4214 | 8.5651 | -112.8381
2686.4062 | 121.2524 | -8.1436 | 112.9807 | 1.4211e-13 | -0.013389 | 0.0081902 | 0.07546 | -0.002878 | 0.076205 | 0.0079357 | -0.0035849 | 0.0049142 | 0.017182 | 0.037919 | 0.0061595 | 9.5699 | 34.9316 | 5.339 | 112.9735 | 112.9945 | 113.0824 | -8.3005 | 0.02852 | -0.017956 | -0.051772 | 0.061616 | 0.19685 | -0.1525 | -0.27404 | -0.15693 | -0.007166 | 17.7135 | 13.4826 | 13.6396 | 0.013828 | 0.1017 | 7.8696 | -112.919 | 8.1721 | 8.0918 | 0.22227 | -112.7838 | -113.1332 | 121.1171 | 121.1381 | 121.226 | 43.0752 | -121.2812 | 8.2052 | 8.3405 | 7.9911 | 8.1257 | -113.2547
2688.1562 | 121.0007 | -7.869 | 113.2507 | 1.4211e-13 | -0.013389 | 0.0086176 | 0.075674 | -0.0030918 | 0.076419 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016754 | 0.037919 | 0.0063733 | 10.1925 | 35.275 | 5.9296 | 113.4084 | 113.4249 | 113.5219 | -7.8655 | 0.023941 | -0.013377 | -0.06093 | 0.061616 | 0.20601 | -0.1525 | -0.27862 | 0.003413 | 0.1577 | 18.0615 | 13.7986 | 13.7952 | 0.17417 | 0.27117 | 7.5903 | -113.1891 | 7.8929 | 7.808 | 0.21769 | -113.0447 | -113.4032 | 121.2774 | 121.2939 | 121.3909 | 43.1439 | -121.1163 | 7.9306 | 8.075 | 7.7165 | 7.8556 | -113.5294
2689.9062 | 121.0281 | -7.6492 | 113.5574 | 1.4211e-13 | -0.012748 | 0.008404 | 0.07546 | -0.0030918 | 0.076419 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.037705 | 0.0063733 | 10.5954 | 35.4215 | 6.3188 | 113.6099 | 113.6172 | 113.7096 | -7.687 | 0.019362 | -0.017956 | -0.056351 | 0.052459 | 0.20143 | -0.15708 | -0.26946 | -0.037736 | 0.052448 | 18.2447 | 13.968 | 14.0057 | 0.05978 | 0.15219 | 7.3798 | -113.505 | 7.6686 | 7.5929 | 0.21311 | -113.356 | -113.7145 | 121.2591 | 121.2664 | 121.3589 | 43.0707 | -121.2444 | 7.7017 | 7.8507 | 7.4922 | 7.6313 | -113.8269
2691.6562 | 120.7031 | -7.4982 | 113.5712 | 1.4211e-13 | -0.01232 | 0.008404 | 0.075674 | -0.0026644 | 0.07706 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016968 | 0.037278 | 0.0061595 | 10.9754 | 35.5588 | 6.685 | 113.8022 | 113.8187 | 113.9019 | -7.5038 | 0.02852 | -0.017956 | -0.056351 | 0.052459 | 0.20143 | -0.1525 | -0.27404 | -0.005641 | 0.23101 | 18.4736 | 14.1832 | 14.1888 | 0.24752 | 0.33076 | 7.2241 | -113.5187 | 7.5267 | 7.4418 | 0.21769 | -113.3697 | -113.7237 | 121.3003 | 121.3169 | 121.4001 | 43.057 | -121.075 | 7.5506 | 7.6996 | 7.3457 | 7.4802 | -113.8452
2693.3438 | 121.2708 | -7.3517 | 113.768 | 1.4211e-13 | -0.012107 | 0.008404 | 0.075887 | -0.002878 | 0.077273 | 0.030827 | -0.0033713 | 0.0044868 | 0.017182 | 0.037705 | 0.0065869 | 11.2639 | 35.5726 | 6.9414 | 113.8892 | 113.8965 | 113.9981 | -7.426 | 0.014784 | -0.017956 | -0.051772 | 0.061616 | 0.20143 | -0.14792 | -0.27862 | -0.074283 | 0.12116 | 18.6156 | 14.2931 | 14.3674 | 0.12852 | 0.23007 | 7.0731 | -113.7064 | 7.3665 | 7.2999 | 0.22685 | -113.5666 | -113.9159 | 121.2408 | 121.2482 | 121.3498 | 42.9243 | -121.194 | 7.4133 | 7.5531 | 7.2038 | 7.3337 | -114.0466
2695.0938 | 120.5704 | -7.2052 | 113.5803 | 1.4211e-13 | -0.01232 | 0.0081902 | 0.075887 | -0.0026644 | 0.077487 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017395 | 0.037705 | 0.0065869 | 11.6759 | 35.7603 | 7.3489 | 114.1089 | 114.1117 | 114.2041 | -7.2245 | 0.023941 | -0.017956 | -0.051772 | 0.061616 | 0.19685 | -0.1525 | -0.27404 | -0.019295 | 0.5286 | 18.8811 | 14.5541 | 14.5734 | 0.53142 | 0.62379 | 6.9312 | -113.5187 | 7.2291 | 7.1534 | 0.22227 | -113.3835 | -113.7328 | 121.3141 | 121.3169 | 121.4093 | 42.9655 | -120.8048 | 7.2668 | 7.4021 | 7.0527 | 7.1872 | -113.8544
2696.7969 | 121.138 | -7.164 | 113.9969 | 1.4211e-13 | -0.011893 | 0.0088312 | 0.076315 | -0.0024508 | 0.077914 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016968 | 0.037705 | 0.0063733 | 11.9049 | 35.7053 | 7.5366 | 114.1272 | 114.1484 | 114.2362 | -7.2016 | 0.019362 | -0.022535 | -0.051772 | 0.061616 | 0.19685 | -0.1525 | -0.27862 | -0.0376 | 0.13035 | 19.0689 | 14.7006 | 14.7382 | 0.15148 | 0.23927 | 6.8854 | -113.9353 | 7.1834 | 7.1122 | 0.22685 | -113.8 | -114.1494 | 121.2912 | 121.3124 | 121.4002 | 42.8693 | -121.1985 | 7.2256 | 7.3609 | 7.0115 | 7.1415 | -114.2755
2698.5625 | 120.9869 | -7.1777 | 114.0701 | 1.4211e-13 | -0.011893 | 0.008404 | 0.076101 | -0.002237 | 0.078128 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016968 | 0.037705 | 0.0068005 | 12.1567 | 35.6916 | 7.7609 | 114.1776 | 114.1896 | 114.2774 | -7.1695 | 0.023941 | -0.013377 | -0.051772 | 0.057037 | 0.19685 | -0.15708 | -0.27404 | 0.008186 | 0.10747 | 19.3344 | 14.9387 | 14.9305 | 0.11945 | 0.20724 | 6.9037 | -114.0131 | 7.2017 | 7.126 | 0.22227 | -113.8733 | -114.2272 | 121.3553 | 121.3673 | 121.4551 | 42.8693 | -121.2397 | 7.2348 | 7.3746 | 7.0207 | 7.1644 | -114.3442
2700.25 | 121.2158 | -8.6014 | 112.6556 | 1.4211e-13 | -0.011679 | 0.0088312 | 0.075674 | -0.0020234 | 0.078555 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017182 | 0.037705 | 0.0063733 | 11.0304 | 34.4096 | 6.6118 | 112.827 | 112.8434 | 112.9404 | -8.5249 | 0.014784 | -0.017956 | -0.047194 | 0.057037 | 0.19685 | -0.1525 | -0.27862 | 0.076469 | 0.17134 | 19.6318 | 15.2132 | 15.1367 | 0.18773 | 0.28478 | 8.3228 | -112.5986 | 8.6162 | 8.5542 | 0.23142 | -112.4588 | -112.8081 | 121.4284 | 121.4448 | 121.5418 | 43.011 | -121.1806 | 8.6584 | 8.7982 | 8.4489 | 8.5834 | -112.9343
2702.0156 | 121.2753 | -9.0271 | 112.1429 | 1.4211e-13 | -0.011466 | 0.0086176 | 0.076315 | -0.0018098 | 0.078342 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.037491 | 0.0063733 | 10.3848 | 33.5397 | 5.9571 | 111.9433 | 111.978 | 112.0567 | -9.3903 | 0.019362 | -0.017956 | -0.051772 | 0.052459 | 0.20143 | -0.14792 | -0.27862 | -0.36323 | -0.1996 | 19.4119 | 14.9842 | 15.3474 | -0.16499 | -0.086197 | 8.7485 | -112.0905 | 9.0465 | 8.9753 | 0.22685 | -111.9415 | -112.2909 | 120.9704 | 121.0051 | 121.0838 | 42.5668 | -121.5333 | 9.0796 | 9.2285 | 8.8792 | 9.0091 | -112.4216
2703.7656 | 121.2067 | -9.6909 | 111.5707 | 1.4211e-13 | -0.011466 | 0.009045 | 0.076742 | -0.0020234 | 0.078769 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016968 | 0.037705 | 0.0065869 | 10.2841 | 33.1917 | 5.8289 | 111.6366 | 111.6437 | 111.7408 | -9.7383 | 0.02852 | -0.008798 | -0.051772 | 0.057037 | 0.20601 | -0.1525 | -0.27404 | -0.047468 | 0.065857 | 19.975 | 15.5198 | 15.5672 | 0.072957 | 0.17008 | 9.4168 | -111.5137 | 9.7194 | 9.6391 | 0.22227 | -111.3647 | -111.7232 | 121.3275 | 121.3346 | 121.4317 | 42.8826 | -121.3091 | 9.7479 | 9.8969 | 9.5384 | 9.6821 | -111.8448
2705.5156 | 121.2936 | -9.8923 | 111.3007 | 1.4211e-13 | -0.010825 | 0.0092586 | 0.076956 | -0.0018098 | 0.078983 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.037491 | 0.0063733 | 10.22 | 32.8712 | 5.7373 | 111.3298 | 111.3552 | 111.4341 | -10.0314 | 0.023941 | -0.022535 | -0.056351 | 0.052459 | 0.20601 | -0.1525 | -0.27404 | -0.1391 | 0.029186 | 20.1123 | 15.6296 | 15.7687 | 0.054566 | 0.1334 | 9.6182 | -111.2482 | 9.9162 | 9.8359 | 0.21769 | -111.0947 | -111.4532 | 121.2221 | 121.2475 | 121.3263 | 42.7635 | -121.332 | 9.9447 | 10.0983 | 9.7398 | 9.8697 | -111.5747
2707.2344 | 121.2021 | -9.3887 | 111.8774 | 1.4211e-13 | -0.010611 | 0.009045 | 0.07717 | -0.0011688 | 0.079196 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016968 | 0.037705 | 0.0063733 | 11.067 | 33.416 | 6.5568 | 111.9617 | 111.9825 | 112.0751 | -9.4086 | 0.019362 | -0.013377 | -0.051772 | 0.066194 | 0.20601 | -0.14792 | -0.27404 | -0.019909 | 0.084221 | 20.4557 | 15.9456 | 15.9655 | 0.1051 | 0.19762 | 9.1147 | -111.8112 | 9.4081 | 9.337 | 0.22227 | -111.6714 | -112.0254 | 121.3504 | 121.3713 | 121.4638 | 42.8048 | -121.2861 | 9.4549 | 9.5947 | 9.2408 | 9.3754 | -112.1515
2708.9844 | 121.2845 | -9.3887 | 111.8454 | 1.4211e-13 | -0.010397 | 0.009686 | 0.076742 | -0.0015962 | 0.079837 | 0.0079357 | -0.0029439 | 0.0044868 | 0.017182 | 0.037705 | 0.0068005 | 11.36 | 33.384 | 6.8224 | 112.0166 | 112.0329 | 112.13 | -9.3674 | 0.023941 | -0.013377 | -0.042615 | 0.057037 | 0.20601 | -0.14792 | -0.26946 | 0.021301 | 0.17121 | 20.7488 | 16.2111 | 16.1898 | 0.18751 | 0.28461 | 9.1193 | -111.7884 | 9.4127 | 9.3461 | 0.22685 | -111.6394 | -111.9933 | 121.4053 | 121.4216 | 121.5187 | 42.7727 | -121.2128 | 9.4458 | 9.5947 | 9.2408 | 9.3754 | -112.1149
2710.7344 | 121.1792 | -9.169 | 112.1338 | 1.4211e-13 | -0.0099699 | 0.009686 | 0.076742 | -0.00074136 | 0.080051 | 0.0079357 | -0.0033713 | 0.0044868 | 0.017182 | 0.038132 | 0.0065869 | 11.7904 | 33.5259 | 7.2161 | 112.2043 | 112.2252 | 112.3131 | -9.198 | 0.019362 | -0.013377 | -0.051772 | 0.070773 | 0.19685 | -0.1525 | -0.26946 | -0.029006 | 0.070528 | 20.9594 | 16.3851 | 16.4141 | 0.091432 | 0.17936 | 8.8995 | -112.063 | 9.1884 | 9.1172 | 0.21769 | -111.9369 | -112.2863 | 121.3733 | 121.3942 | 121.4822 | 42.6949 | -121.3318 | 9.2398 | 9.3659 | 9.0165 | 9.1556 | -112.4033
2712.5312 | 121.3623 | -8.6197 | 112.5824 | 1.4211e-13 | -0.0099699 | 0.009686 | 0.07717 | -0.00074136 | 0.079837 | 0.00030522 | -0.0031575 | 0.0042732 | 0.017182 | 0.037491 | 0.0063733 | 12.5046 | 33.906 | 7.9074 | 112.6667 | 112.6877 | 112.7756 | -8.7264 | 0.019362 | -0.013377 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.26488 | -0.10669 | 0.084337 | 21.1243 | 16.5271 | 16.6338 | 0.10529 | 0.19319 | 8.3548 | -112.5208 | 8.6391 | 8.5725 | 0.21769 | -112.3764 | -112.7349 | 121.2864 | 121.3074 | 121.3953 | 42.5256 | -121.3088 | 8.6813 | 8.8257 | 8.4672 | 8.6063 | -112.8473
2714.2969 | 121.3669 | -7.9788 | 113.2553 | 1.4211e-13 | -0.0095427 | 0.010541 | 0.076956 | -0.00074136 | 0.080478 | 0.0079357 | -0.0029439 | 0.0047004 | 0.017182 | 0.037705 | 0.0065869 | 13.4615 | 34.4966 | 8.8231 | 113.3855 | 113.402 | 113.4899 | -8.0258 | 0.023941 | -0.017956 | -0.047194 | 0.066194 | 0.20601 | -0.14792 | -0.26488 | -0.046986 | 0.13023 | 21.4403 | 16.8019 | 16.8489 | 0.14669 | 0.23454 | 7.7139 | -113.1891 | 8.0028 | 7.9316 | 0.21769 | -113.0493 | -113.4032 | 121.3644 | 121.3808 | 121.4687 | 42.4754 | -121.2811 | 8.045 | 8.1848 | 7.8309 | 7.9609 | -113.5202
2715.9844 | 121.3577 | -7.901 | 113.3698 | 1.4211e-13 | -0.0093289 | 0.0098996 | 0.077597 | -0.00052776 | 0.080906 | 0.015566 | -0.0031575 | 0.0042732 | 0.017182 | 0.037491 | 0.0065869 | 13.7957 | 34.5012 | 9.1527 | 113.4863 | 113.4982 | 113.5997 | -7.9342 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20143 | -0.14792 | -0.27404 | -0.033228 | 0.11651 | 21.6967 | 17.0537 | 17.087 | 0.12841 | 0.22998 | 7.627 | -113.3036 | 7.9249 | 7.8538 | 0.22685 | -113.1683 | -113.5177 | 121.3873 | 121.3992 | 121.5007 | 42.4022 | -121.304 | 7.9672 | 8.1024 | 7.7531 | 7.8876 | -113.6438
2717.75 | 121.4081 | -7.3059 | 113.9557 | 1.4211e-13 | -0.0091153 | 0.010327 | 0.077811 | -0.00052776 | 0.081119 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016754 | 0.037705 | 0.0063733 | 14.6015 | 34.9636 | 9.9402 | 114.0494 | 114.0705 | 114.1537 | -7.3848 | 0.02852 | -0.013377 | -0.056351 | 0.066194 | 0.20143 | -0.15708 | -0.26946 | -0.07885 | 0.093719 | 21.9074 | 17.2461 | 17.325 | 0.11484 | 0.19806 | 7.0364 | -113.8895 | 7.3344 | 7.2496 | 0.21311 | -113.7543 | -114.1128 | 121.3553 | 121.3764 | 121.4597 | 42.2695 | -121.3404 | 7.3721 | 7.5073 | 7.1488 | 7.2925 | -114.2251
2719.5156 | 121.3943 | -7.5897 | 113.6444 | 1.4211e-13 | -0.0091153 | 0.010541 | 0.077811 | -0.00031416 | 0.081333 | -0.0073253 | -0.0029439 | 0.0047004 | 0.016754 | 0.037919 | 0.0063733 | 14.5283 | 34.5927 | 9.8578 | 113.7243 | 113.7317 | 113.8287 | -7.719 | 0.023941 | -0.017956 | -0.047194 | 0.057037 | 0.20143 | -0.15708 | -0.26946 | -0.1293 | 0.079932 | 22.118 | 17.4475 | 17.5768 | 0.087278 | 0.18426 | 7.3203 | -113.5874 | 7.6137 | 7.5425 | 0.22227 | -113.443 | -113.8015 | 121.3141 | 121.3214 | 121.4184 | 42.1825 | -121.3634 | 7.6468 | 7.7912 | 7.4326 | 7.5718 | -113.9139
2721.2188 | 121.4081 | -7.4844 | 113.7817 | 1.4211e-13 | -0.0084743 | 0.010541 | 0.077811 | -0.00010036 | 0.081333 | 0.015566 | -0.0029439 | 0.0047004 | 0.017182 | 0.037705 | 0.0063733 | 14.9586 | 34.6431 | 10.2332 | 113.88 | 113.9011 | 113.9889 | -7.5588 | 0.023941 | -0.013377 | -0.051772 | 0.061616 | 0.20143 | -0.1525 | -0.27404 | -0.074321 | 0.098269 | 22.4431 | 17.7176 | 17.792 | 0.11937 | 0.20718 | 7.2104 | -113.7201 | 7.5084 | 7.4327 | 0.22227 | -113.5803 | -113.9342 | 121.3644 | 121.3855 | 121.4734 | 42.1275 | -121.3405 | 7.5461 | 7.6859 | 7.3319 | 7.4711 | -114.0558
2722.9219 | 121.0098 | -8.5098 | 112.8571 | 1.4211e-13 | -0.0084743 | 0.010968 | 0.078024 | 0.00011324 | 0.081974 | -0.0073253 | -0.0035849 | 0.0047004 | 0.017182 | 0.037705 | 0.0063733 | 14.1849 | 33.5855 | 9.4091 | 112.8087 | 112.8342 | 112.9221 | -8.6302 | 0.019362 | -0.013377 | -0.047194 | 0.061616 | 0.20601 | -0.14792 | -0.27862 | -0.1204 | -0.048392 | 22.6947 | 17.9189 | 18.0393 | -0.022838 | 0.065047 | 8.2312 | -112.7954 | 8.5292 | 8.4626 | 0.23142 | -112.651 | -113.005 | 121.3185 | 121.344 | 121.4319 | 42.0953 | -121.4873 | 8.5714 | 8.7158 | 8.3619 | 8.4964 | -113.1357
2724.6875 | 120.9961 | -8.1482 | 113.1775 | 1.4211e-13 | -0.0080469 | 0.010754 | 0.078238 | 0.00011324 | 0.082401 | -0.0073253 | -0.0033713 | 0.0047004 | 0.017182 | 0.037919 | 0.0065869 | 15.0365 | 34.0708 | 10.2561 | 113.3947 | 113.4295 | 113.499 | -8.1036 | 0.023941 | -0.008798 | -0.047194 | 0.057037 | 0.20601 | -0.14334 | -0.26946 | 0.044544 | 0.21721 | 23.1847 | 18.4043 | 18.3597 | 0.25199 | 0.32152 | 7.8787 | -113.1205 | 8.1721 | 8.101 | 0.22227 | -112.9715 | -113.3208 | 121.5429 | 121.5777 | 121.6472 | 42.219 | -121.2811 | 8.2052 | 8.3542 | 8.0048 | 8.1394 | -113.447
2726.375 | 121.106 | -8.8165 | 112.5275 | 1.4211e-13 | -0.0078333 | 0.010968 | 0.078238 | 0.00032684 | 0.082829 | -0.014956 | -0.0035849 | 0.0047004 | 0.016541 | 0.037491 | 0.0065869 | 14.5054 | 33.2695 | 9.7159 | 112.6072 | 112.6236 | 112.7298 | -8.8546 | 0.033099 | -0.013377 | -0.047194 | 0.057037 | 0.20143 | -0.14334 | -0.27404 | -0.038064 | 0.079749 | 23.3219 | 18.5324 | 18.5705 | 0.096121 | 0.20234 | 8.5425 | -112.4704 | 8.8496 | 8.7693 | 0.22685 | -112.326 | -112.6708 | 121.4237 | 121.4401 | 121.5463 | 42.0861 | -121.3821 | 8.8736 | 9.018 | 8.6732 | 8.8032 | -112.8015
2728.1406 | 119.7098 | -5.0262 | 115.4846 | 1.4211e-13 | -0.0074059 | 0.011395 | 0.078879 | 0.00054064 | 0.083256 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.037705 | 0.0065869 | 16.5473 | 34.6935 | 11.7211 | 114.228 | 114.3178 | 114.2362 | -7.1421 | 0.019362 | -0.022535 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27404 | -2.1158 | -1.2567 | 21.5736 | 16.7474 | 18.8632 | -1.1668 | -1.2485 | 4.7522 | -115.423 | 5.0456 | 4.9791 | 0.22685 | -115.2786 | -115.6371 | 119.2542 | 119.344 | 119.2624 | 39.7197 | -122.6267 | 5.0879 | 5.2323 | 4.8737 | 5.0037 | -115.7587
2729.8906 | 120.9091 | -3.8773 | 117.3248 | 1.4211e-13 | -0.0071923 | 0.011609 | 0.078879 | 0.00054064 | 0.083683 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016968 | 0.037705 | 0.0061595 | 19.9125 | 37.6925 | 15.1869 | 117.6114 | 117.6284 | 117.7067 | -3.9551 | 0.02852 | -0.017956 | -0.047194 | 0.057037 | 0.20601 | -0.15708 | -0.27862 | -0.077885 | 0.28656 | 23.7897 | 19.0642 | 19.142 | 0.30352 | 0.38191 | 3.5986 | -117.2678 | 3.9058 | 3.8301 | 0.23142 | -117.1188 | -117.4819 | 121.4887 | 121.5056 | 121.584 | 41.5697 | -121.28 | 3.9343 | 4.0833 | 3.7202 | 3.8593 | -117.6034
2731.5781 | 120.7855 | -3.8406 | 116.8396 | 1.4211e-13 | -0.0069785 | 0.012036 | 0.079093 | 0.0011816 | 0.08347 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017395 | 0.037919 | 0.0065869 | 20.0498 | 37.5459 | 15.2785 | 117.4786 | 117.491 | 117.5785 | -4.0834 | 0.014784 | -0.022535 | -0.051772 | 0.061616 | 0.20143 | -0.14792 | -0.27862 | -0.24272 | 0.63902 | 23.8904 | 19.1191 | 19.3618 | 0.65138 | 0.73894 | 3.562 | -116.778 | 3.8554 | 3.7889 | 0.22685 | -116.6382 | -116.9875 | 121.3193 | 121.3316 | 121.4192 | 41.3866 | -120.923 | 3.9023 | 4.0421 | 3.6927 | 3.8181 | -117.1182
2733.3438 | 121.2845 | -3.5248 | 117.7277 | 1.4211e-13 | -0.0067649 | 0.011609 | 0.079093 | 0.0016088 | 0.083897 | 0.0079357 | -0.0029439 | 0.0047004 | 0.016968 | 0.037705 | 0.0061595 | 20.7824 | 37.9077 | 16.0202 | 117.9548 | 117.9718 | 118.0593 | -3.6209 | 0.023941 | -0.017956 | -0.042615 | 0.061616 | 0.21516 | -0.1525 | -0.27862 | -0.096102 | 0.22711 | 24.3071 | 19.5449 | 19.641 | 0.24411 | 0.33163 | 3.2462 | -117.666 | 3.5487 | 3.4822 | 0.236 | -117.5125 | -117.8802 | 121.4796 | 121.4966 | 121.5841 | 41.4324 | -121.3485 | 3.5864 | 3.7399 | 3.3723 | 3.5068 | -118.0063
2735.1094 | 121.4264 | -3.0579 | 118.2495 | 1.4211e-13 | -0.0063375 | 0.011823 | 0.079734 | 0.0011816 | 0.084752 | 0.0079357 | -0.0027303 | 0.0044868 | 0.017182 | 0.037705 | 0.0061595 | 21.4966 | 38.2968 | 16.771 | 118.4309 | 118.4434 | 118.5355 | -3.0989 | 0.019362 | -0.013377 | -0.047194 | 0.061616 | 0.20601 | -0.14792 | -0.27404 | -0.041023 | 0.18141 | 24.5544 | 19.8288 | 19.8699 | 0.19389 | 0.28596 | 2.7838 | -118.1879 | 3.0772 | 3.0107 | 0.22685 | -118.0435 | -118.3974 | 121.4888 | 121.5013 | 121.5933 | 41.3547 | -121.3484 | 3.1195 | 3.2639 | 2.9099 | 3.0445 | -118.5236
2736.8125 | 121.4813 | -3.1631 | 118.1671 | 1.4211e-13 | -0.0059103 | 0.01225 | 0.079734 | 0.0018226 | 0.084965 | 0.023196 | -0.0033713 | 0.0047004 | 0.017395 | 0.037919 | 0.0061595 | 21.6385 | 38.1412 | 16.9038 | 118.3027 | 118.3289 | 118.4073 | -3.25 | 0.019362 | -0.008798 | -0.051772 | 0.061616 | 0.20143 | -0.14792 | -0.2832 | -0.086842 | 0.13562 | 24.8017 | 20.0669 | 20.1537 | 0.16181 | 0.24016 | 2.8799 | -118.1055 | 3.1825 | 3.1114 | 0.23143 | -117.9657 | -118.315 | 121.4659 | 121.4921 | 121.5704 | 41.3043 | -121.4171 | 3.2248 | 3.3646 | 3.0152 | 3.1543 | -118.4503
2738.5625 | 121.3577 | -2.8381 | 118.5379 | 1.4211e-13 | -0.0054829 | 0.012464 | 0.079734 | 0.0020362 | 0.085606 | 0.00030522 | -0.0031575 | 0.0042732 | 0.017182 | 0.037705 | 0.0063733 | 22.3802 | 38.5807 | 17.6638 | 118.7835 | 118.796 | 118.8789 | -2.7784 | 0.019362 | -0.013377 | -0.056351 | 0.061616 | 0.20601 | -0.14792 | -0.2832 | 0.059775 | 0.24556 | 25.2183 | 20.5019 | 20.4421 | 0.25807 | 0.34096 | 2.5549 | -118.4763 | 2.8575 | 2.7818 | 0.22685 | -118.3319 | -118.6858 | 121.6216 | 121.6341 | 121.717 | 41.4188 | -121.3163 | 2.8998 | 3.0441 | 2.6902 | 2.8248 | -118.8211
2740.25 | 121.4767 | -3.0304 | 118.4235 | 1.4211e-13 | -0.0052691 | 0.01225 | 0.079947 | 0.0018226 | 0.086034 | 0.00030522 | -0.0029439 | 0.0047004 | 0.017182 | 0.037705 | 0.0068005 | 22.1101 | 38.013 | 17.3799 | 118.2157 | 118.2419 | 118.3249 | -3.3324 | 0.023941 | -0.017956 | -0.051772 | 0.057037 | 0.21059 | -0.1525 | -0.27404 | -0.30201 | -0.20772 | 25.1405 | 20.4103 | 20.7123 | -0.18153 | -0.098608 | 2.7564 | -118.3664 | 3.0543 | 2.9786 | 0.22227 | -118.2129 | -118.576 | 121.2461 | 121.2723 | 121.3552 | 41.0434 | -121.7559 | 3.0874 | 3.241 | 2.8779 | 3.0124 | -118.6975
2742.0469 | 116.3544 | -81.8665 | 34.3369 | 1.4211e-13 | -0.0078333 | 0.0092586 | 0.074819 | 0.0035318 | 0.085393 | -0.0073253 | -0.0031575 | 0.0044868 | 0.017182 | 0.038132 | 0.0065869 | -56.0705 | -36.2291 | -60.4417 | 34.6693 | 34.4705 | 35.0996 | -82.7493 | 0.055992 | 0.018674 | -0.015143 | 0.093665 | 0.24264 | -0.015142 | -0.23741 | -0.88282 | 0.33246 | 25.796 | 21.4247 | 22.3076 | 0.13365 | 0.76274 | 81.629 | -34.2432 | 81.9224 | 81.8513 | 0.22227 | -34.0942 | -34.352 | 116.5358 | 116.337 | 116.9661 | 45.6374 | -117.0861 | 81.9601 | 82.1091 | 81.8513 | 81.8851 | -34.5743
2743.7344 | 121.0785 | -120.7214 | 0.1831 | 1.4211e-13 | -0.0071923 | 0.0094724 | 0.076529 | 0.0048138 | 0.092443 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.037919 | 0.0063733 | -91.727 | -69.4514 | -96.6376 | 0.29478 | 0.33004 | 0.59525 | -120.8734 | 0.069728 | 0.027831 | 0.003172 | 0.11198 | 0.26095 | 0.035222 | -0.22367 | -0.15197 | 0.11168 | 28.9945 | 24.0838 | 24.2358 | 0.14694 | 0.41214 | 120.4978 | -0.071126 | 120.7912 | 120.7246 | 0.22685 | 0.077846 | -0.14788 | 121.0162 | 121.0515 | 121.3167 | 51.27 | -121.0565 | 120.8334 | 120.9824 | 120.7567 | 120.7493 | -0.40678
2745.4844 | 121.1563 | -120.8496 | 0.21057 | 1.4211e-13 | -0.0067649 | 0.0094724 | 0.076956 | 0.0050274 | 0.092657 | 0.00030522 | -0.0031575 | 0.0049142 | 0.017182 | 0.037919 | 0.0065869 | -91.5438 | -69.6712 | -96.427 | 0.27647 | 0.31631 | 0.57235 | -121.0062 | 0.069728 | 0.03241 | 0.003172 | 0.1074 | 0.25179 | 0.048958 | -0.22825 | -0.15658 | 0.065898 | 29.3058 | 24.4226 | 24.5792 | 0.10573 | 0.36178 | 120.6214 | -0.10317 | 120.9193 | 120.8528 | 0.23142 | 0.041223 | -0.16161 | 121.1261 | 121.1659 | 121.422 | 51.1784 | -121.2168 | 120.957 | 121.1014 | 120.8986 | 120.882 | -0.43882
2747.25 | 121.1243 | -120.9686 | 0.21973 | 1.4211e-13 | -0.0063375 | 0.0094724 | 0.076742 | 0.0052412 | 0.093298 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016968 | 0.037705 | 0.0063733 | -91.2874 | -69.7948 | -96.1248 | 0.23526 | 0.31631 | 0.56778 | -121.0703 | 0.074307 | 0.03241 | 0.007751 | 0.11656 | 0.25637 | 0.085587 | -0.22367 | -0.10167 | 0.015536 | 29.6812 | 24.8438 | 24.9455 | 0.096578 | 0.34805 | 120.745 | -0.10317 | 121.0429 | 120.9764 | 0.23142 | 0.036645 | -0.13414 | 121.2039 | 121.2849 | 121.5364 | 51.1738 | -121.29 | 121.0852 | 121.225 | 121.0542 | 121.001 | -0.4434
2748.9375 | 116.6885 | -83.0887 | 33.6136 | 1.4211e-13 | -0.0063375 | 0.010327 | 0.076315 | 0.0050274 | 0.090093 | 0.0079357 | -0.0033713 | 0.0049142 | 0.016968 | 0.037919 | 0.0065869 | -70.6343 | -51.311 | -75.6508 | 19.2447 | 19.6668 | 19.4957 | -99.5173 | 0.060571 | 0.027831 | -0.005985 | 0.098244 | 0.23348 | -0.0243 | -0.23283 | -16.4286 | -14.3689 | 12.4544 | 7.4379 | 23.8665 | -13.9467 | -14.1179 | 82.8559 | -33.5153 | 83.1493 | 83.0827 | 0.22685 | -33.3801 | -33.6379 | 102.3334 | 102.7555 | 102.5844 | 31.7777 | -133.1309 | 83.1869 | 83.3222 | 83.0644 | 83.1165 | -33.8464
2750.7031 | 120.8405 | -120.6985 | 0.20599 | 1.4211e-13 | -0.0054829 | 0.0098996 | 0.076956 | 0.0058822 | 0.094366 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.037919 | 0.0063733 | -90.4954 | -69.804 | -95.2366 | 0.27189 | 0.30715 | 0.55404 | -120.7864 | 0.078886 | 0.03241 | 0.007751 | 0.11656 | 0.24721 | 0.14969 | -0.22367 | -0.087856 | 0.065896 | 30.2032 | 25.4619 | 25.5498 | 0.10115 | 0.34805 | 120.4749 | -0.089437 | 120.7774 | 120.7063 | 0.23142 | 0.041221 | -0.056307 | 120.9704 | 121.0057 | 121.2526 | 50.8946 | -120.9924 | 120.8151 | 120.9458 | 120.8482 | 120.731 | -0.42967
2752.4844 | 121.0327 | -120.7443 | 0.1831 | 1.4211e-13 | -0.0054829 | 0.010113 | 0.077383 | 0.0060958 | 0.094366 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017182 | 0.037919 | 0.0065869 | -90.2619 | -69.8635 | -95.0032 | 0.22611 | 0.31173 | 0.5632 | -120.9009 | 0.069728 | 0.018674 | -0.001407 | 0.11656 | 0.25179 | 0.10848 | -0.2191 | -0.15655 | 0.043001 | 30.4825 | 25.7412 | 25.8977 | 0.12862 | 0.38009 | 120.5252 | -0.066548 | 120.8141 | 120.7429 | 0.21769 | 0.068689 | -0.074625 | 120.9704 | 121.056 | 121.3075 | 50.8808 | -121.084 | 120.8609 | 120.9961 | 120.8528 | 120.763 | -0.4022
2754.1719 | 121.1197 | -120.7947 | 0.17853 | 1.4211e-13 | -0.0046281 | 0.0098996 | 0.077811 | 0.0060958 | 0.095648 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016968 | 0.037919 | 0.0063733 | -90.0284 | -70.0008 | -94.7193 | 0.22611 | 0.26594 | 0.55862 | -120.965 | 0.06515 | 0.03241 | -0.001407 | 0.11198 | 0.25637 | 0.10848 | -0.22825 | -0.1703 | 0.047578 | 30.7663 | 26.0754 | 26.2457 | 0.087409 | 0.38009 | 120.5664 | -0.066549 | 120.8598 | 120.7933 | 0.22685 | 0.077844 | -0.070048 | 121.0208 | 121.0606 | 121.3533 | 50.7938 | -121.1435 | 120.9067 | 121.0511 | 120.9032 | 120.8271 | -0.40678
2755.8594 | 121.0968 | -120.8542 | 0.19684 | 1.4211e-13 | -0.0046281 | 0.010113 | 0.077811 | 0.006523 | 0.095862 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016968 | 0.037705 | 0.0063733 | -89.772 | -70.0466 | -94.4583 | 0.22611 | 0.25678 | 0.55404 | -120.9329 | 0.069728 | 0.03241 | 0.003172 | 0.11198 | 0.24721 | 0.12679 | -0.22367 | -0.078741 | 0.029268 | 31.0822 | 26.3958 | 26.4746 | 0.059941 | 0.3572 | 120.6305 | -0.084859 | 120.9239 | 120.8574 | 0.22685 | 0.050377 | -0.070044 | 121.0803 | 121.111 | 121.4082 | 50.8076 | -121.1298 | 120.9662 | 121.1014 | 120.981 | 120.8866 | -0.42051
2757.625 | 121.1655 | -120.8633 | 0.17853 | 1.4211e-13 | -0.0044145 | 0.010327 | 0.078024 | 0.0067368 | 0.096289 | 0.015566 | -0.0029439 | 0.0044868 | 0.016968 | 0.037491 | 0.0063733 | -89.4744 | -70.0512 | -94.1516 | 0.21695 | 0.25678 | 0.49452 | -120.965 | 0.074307 | 0.027831 | -0.001407 | 0.11656 | 0.25179 | 0.053537 | -0.23283 | -0.10164 | 0.038422 | 31.389 | 26.7118 | 26.8134 | 0.078251 | 0.31599 | 120.6305 | -0.061971 | 120.9376 | 120.8619 | 0.23142 | 0.073266 | -0.12499 | 121.0803 | 121.1201 | 121.3579 | 50.8121 | -121.1435 | 120.9799 | 121.1151 | 120.9169 | 120.8912 | -0.41136
2759.3125 | 121.0602 | -120.9274 | 0.21057 | 1.4211e-13 | -0.0042009 | 0.010754 | 0.078238 | 0.0067368 | 0.097144 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016968 | 0.037919 | 0.0065869 | -89.2272 | -70.1382 | -93.8677 | 0.22611 | 0.25678 | 0.49452 | -120.9787 | 0.069728 | 0.027831 | 0.003172 | 0.11656 | 0.25637 | 0.067272 | -0.22367 | -0.051289 | 0.015535 | 31.7003 | 27.0597 | 27.111 | 0.046208 | 0.28395 | 120.7038 | -0.094014 | 120.9972 | 120.9306 | 0.22685 | 0.045801 | -0.1433 | 121.1535 | 121.1842 | 121.4219 | 50.7892 | -121.1893 | 121.044 | 121.1838 | 120.9947 | 120.9553 | -0.43424
2761.0625 | 121.2112 | -120.9183 | 0.18768 | 1.4211e-13 | -0.0035599 | 0.010968 | 0.078238 | 0.007164 | 0.097785 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016968 | 0.037705 | 0.0065869 | -88.9433 | -70.2069 | -93.5564 | 0.22153 | 0.24762 | 0.48994 | -121.0108 | 0.06515 | 0.027831 | 0.007751 | 0.11656 | 0.25637 | 0.044379 | -0.22367 | -0.092496 | 0.033845 | 31.975 | 27.3619 | 27.4544 | 0.059938 | 0.30226 | 120.6946 | -0.071126 | 120.9834 | 120.926 | 0.23142 | 0.068689 | -0.1433 | 121.1398 | 121.1659 | 121.4082 | 50.7114 | -121.1985 | 121.0348 | 121.1746 | 120.9627 | 120.9461 | -0.41136
2762.8281 | 121.106 | -120.9869 | 0.19684 | 1.4211e-13 | -0.0033461 | 0.010968 | 0.078879 | 0.0073778 | 0.098212 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017609 | 0.038346 | 0.0063733 | -88.6365 | -70.271 | -93.2268 | 0.21695 | 0.2522 | 0.48536 | -121.0199 | 0.06515 | 0.018674 | -0.001407 | 0.11198 | 0.25179 | 0.11764 | -0.22825 | -0.03299 | 0.020112 | 32.3504 | 27.7602 | 27.7931 | 0.055362 | 0.28852 | 120.7587 | -0.084859 | 121.0521 | 120.9855 | 0.22685 | 0.054956 | -0.079201 | 121.2039 | 121.2391 | 121.4723 | 50.716 | -121.2168 | 121.0989 | 121.2387 | 121.1046 | 121.0056 | -0.42509
2764.5938 | 115.7593 | -77.6001 | 38.1454 | 1.4211e-13 | -0.0035599 | 0.011182 | 0.075887 | 0.0069504 | 0.092016 | 0.0079357 | -0.0035849 | 0.0044868 | 0.016968 | 0.037919 | 0.0065869 | -53.8271 | -38.3307 | -58.0244 | 32.371 | 32.3688 | 32.6272 | -84.1184 | 0.051413 | 0.009516 | -0.015143 | 0.093665 | 0.23348 | -0.12503 | -0.24199 | -6.5183 | -5.7745 | 23.773 | 19.5757 | 26.094 | -5.7767 | -5.5183 | 77.3581 | -38.0518 | 77.6515 | 77.585 | 0.22685 | -37.912 | -38.2705 | 109.9711 | 109.9689 | 110.2272 | 39.2694 | -122.2638 | 77.6938 | 77.8336 | 77.4751 | 77.6096 | -38.3874
2766.2812 | 120.7352 | -119.8563 | 0.74158 | 1.4211e-13 | -0.0022777 | 0.011182 | 0.078238 | 0.0082324 | 0.098853 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016968 | 0.037705 | 0.0061595 | -87.1989 | -69.5201 | -91.6335 | 0.80298 | 0.84288 | 1.0897 | -120.0767 | 0.074307 | 0.03241 | -0.001407 | 0.11198 | 0.25179 | 0.067272 | -0.22825 | -0.22041 | 0.061406 | 32.6573 | 28.2227 | 28.4431 | 0.1013 | 0.34816 | 119.628 | -0.6296 | 119.9306 | 119.8549 | 0.22685 | -0.48978 | -0.67431 | 120.6592 | 120.6991 | 120.946 | 50.3362 | -120.8182 | 119.9682 | 120.1081 | 119.9235 | 119.8887 | -0.96983
2768.0469 | 120.7855 | -120.0943 | 0.70496 | 1.4211e-13 | -0.0018505 | 0.011182 | 0.078238 | 0.0082324 | 0.099494 | 0.00030522 | -0.0027303 | 0.0044868 | 0.016754 | 0.037919 | 0.0068005 | -87.0753 | -69.6162 | -91.4596 | 0.71599 | 0.81083 | 1.0577 | -120.2324 | 0.069728 | 0.027831 | 0.003172 | 0.11198 | 0.26095 | 0.085587 | -0.22367 | -0.13805 | 0.011038 | 33.019 | 28.6347 | 28.7728 | 0.10587 | 0.35273 | 119.8706 | -0.59298 | 120.164 | 120.0975 | 0.22685 | -0.44401 | -0.61937 | 120.8103 | 120.9051 | 121.152 | 50.4781 | -120.9373 | 120.2063 | 120.3553 | 120.1799 | 120.1221 | -0.92863
2769.7344 | 120.9045 | -118.8812 | 2.0233 | 1.4211e-13 | -0.0016367 | 0.011395 | 0.078879 | 0.0082324 | 0.10035 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017182 | 0.037919 | 0.0065869 | -86.6221 | -69.5109 | -90.9697 | 0.94949 | 1.0489 | 1.2866 | -120.0492 | 0.06515 | 0.027831 | -0.001407 | 0.11198 | 0.25637 | -0.005985 | -0.22367 | -1.168 | -1.0738 | 32.2592 | 27.9115 | 29.0795 | -0.97438 | -0.7367 | 118.6576 | -1.9113 | 118.9464 | 118.8798 | 0.22227 | -1.7669 | -2.0293 | 119.8307 | 119.9302 | 120.1678 | 49.3703 | -122.0725 | 118.9932 | 119.1376 | 118.8752 | 118.9091 | -2.247
2771.4844 | 120.9137 | -120.3049 | 0.59052 | 1.4211e-13 | -0.0014231 | 0.011609 | 0.079306 | 0.0086598 | 0.10078 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016968 | 0.038132 | 0.0065869 | -86.7365 | -69.8085 | -91.02 | 0.59238 | 0.62767 | 0.93406 | -120.4018 | 0.069728 | 0.023253 | 0.003172 | 0.11198 | 0.25179 | -0.005985 | -0.22825 | -0.096902 | 0.001862 | 33.5684 | 29.2848 | 29.3817 | 0.037157 | 0.34355 | 120.0766 | -0.47854 | 120.3746 | 120.308 | 0.23142 | -0.33872 | -0.5965 | 120.8972 | 120.9325 | 121.2389 | 50.4963 | -120.9923 | 120.4169 | 120.5567 | 120.2989 | 120.3281 | -0.81877
2773.2344 | 120.9641 | -120.3918 | 0.55847 | 1.4211e-13 | -0.00099569 | 0.011823 | 0.078879 | 0.0088734 | 0.10163 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016968 | 0.037919 | 0.0063733 | -86.5305 | -69.9596 | -90.8323 | 0.57864 | 0.6002 | 0.90659 | -120.4476 | 0.078886 | 0.03241 | 0.003172 | 0.11198 | 0.26095 | 0.062694 | -0.22825 | -0.055716 | 0.02017 | 33.8614 | 29.5595 | 29.6152 | 0.041726 | 0.34812 | 120.1636 | -0.44649 | 120.4707 | 120.395 | 0.23142 | -0.29752 | -0.49578 | 120.9705 | 120.992 | 121.2984 | 50.4322 | -121.006 | 120.5038 | 120.6528 | 120.4545 | 120.4243 | -0.78672
2774.9844 | 120.6345 | -120.314 | 0.58136 | 1.4211e-13 | -0.00056829 | 0.011609 | 0.079306 | 0.009087 | 0.10206 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.037919 | 0.0065869 | -86.242 | -69.9505 | -90.4844 | 0.61985 | 0.65514 | 0.95238 | -120.5117 | 0.06515 | 0.027831 | 0.007751 | 0.11656 | 0.24721 | 0.062694 | -0.2191 | -0.19764 | 0.038488 | 34.072 | 29.8296 | 30.0273 | 0.073785 | 0.37102 | 120.0949 | -0.4648 | 120.3792 | 120.3218 | 0.22685 | -0.33415 | -0.51867 | 120.9339 | 120.9692 | 121.2664 | 50.3635 | -121.093 | 120.4306 | 120.5612 | 120.3767 | 120.3419 | -0.80046
2776.7344 | 121.0098 | -120.3918 | 0.60883 | 1.4211e-13 | -0.00014109 | 0.011823 | 0.07952 | 0.009087 | 0.1027 | 0.00030522 | -0.0027303 | 0.0044868 | 0.017182 | 0.037919 | 0.0063733 | -85.9673 | -69.8543 | -90.0952 | 0.58322 | 0.62767 | 0.92949 | -120.4934 | 0.074307 | 0.027831 | 0.01233 | 0.10282 | 0.25637 | -0.001407 | -0.22367 | -0.10151 | -0.025605 | 34.4245 | 30.2966 | 30.3981 | 0.018846 | 0.32066 | 120.1682 | -0.506 | 120.4662 | 120.4042 | 0.236 | -0.35245 | -0.61023 | 120.9751 | 121.0195 | 121.3213 | 50.5375 | -121.1022 | 120.4947 | 120.6482 | 120.3904 | 120.4197 | -0.8325
2778.5 | 121.1151 | -120.3552 | 0.59509 | 1.4211e-13 | -0.00014109 | 0.012464 | 0.079306 | 0.0095144 | 0.10291 | 0.0079357 | -0.0031575 | 0.0044868 | 0.017395 | 0.037919 | 0.0061595 | -85.7293 | -69.7032 | -89.7519 | 0.61985 | 0.65057 | 0.90201 | -120.4842 | 0.074307 | 0.03241 | -0.001407 | 0.11198 | 0.24721 | 0.085587 | -0.22825 | -0.12897 | 0.024755 | 34.626 | 30.6034 | 30.7323 | 0.055473 | 0.30692 | 120.127 | -0.48311 | 120.4295 | 120.3538 | 0.22685 | -0.34788 | -0.50951 | 120.9751 | 121.0058 | 121.2572 | 50.652 | -121.0793 | 120.4672 | 120.6024 | 120.4408 | 120.3876 | -0.82334
2780.25 | 121.1243 | -120.4834 | 0.49439 | 1.4211e-13 | 0.00028631 | 0.012464 | 0.079947 | 0.009728 | 0.10355 | 0.0079357 | -0.0029439 | 0.0042732 | 0.016754 | 0.038346 | 0.0063733 | -85.6011 | -69.8131 | -89.5321 | 0.5237 | 0.60936 | 0.85623 | -120.6399 | 0.069728 | 0.03241 | -0.001407 | 0.11656 | 0.25179 | -0.010564 | -0.22367 | -0.15648 | 0.029317 | 34.8823 | 30.9513 | 31.1078 | 0.11497 | 0.36184 | 120.2597 | -0.37783 | 120.5531 | 120.482 | 0.22227 | -0.24259 | -0.50495 | 121.0071 | 121.0928 | 121.3396 | 50.6703 | -121.1343 | 120.6 | 120.7352 | 120.4728 | 120.5158 | -0.71806
2781.9375 | 121.1151 | -120.5475 | 0.48065 | 1.4211e-13 | 0.00049991 | 0.01225 | 0.079947 | 0.009728 | 0.10398 | 0.00030522 | -0.0029439 | 0.0044868 | 0.016754 | 0.037919 | 0.0063733 | -85.4546 | -69.8269 | -89.2803 | 0.50081 | 0.53609 | 0.83791 | -120.6628 | 0.06515 | 0.03241 | 0.007751 | 0.11198 | 0.25179 | 0.012329 | -0.22825 | -0.11529 | 0.020158 | 35.0929 | 31.2672 | 31.3825 | 0.055441 | 0.35726 | 120.3192 | -0.36867 | 120.6126 | 120.5552 | 0.236 | -0.22886 | -0.46832 | 121.0483 | 121.0836 | 121.3854 | 50.7206 | -121.1434 | 120.6595 | 120.7993 | 120.5598 | 120.5799 | -0.7089
2783.6875 | 121.1105 | -120.5109 | 0.46234 | 1.4211e-13 | 0.0011411 | 0.01225 | 0.080161 | 0.010369 | 0.10484 | -0.0073253 | -0.0027303 | 0.0042732 | 0.016968 | 0.037919 | 0.0063733 | -85.1936 | -69.8681 | -88.8911 | 0.4825 | 0.50862 | 0.76466 | -120.6261 | 0.074307 | 0.027831 | 0.007751 | 0.1074 | 0.25637 | 0.085587 | -0.23741 | -0.11528 | 0.020155 | 35.3173 | 31.6197 | 31.735 | 0.046279 | 0.30232 | 120.2735 | -0.35494 | 120.5852 | 120.5186 | 0.24516 | -0.20597 | -0.37675 | 120.9934 | 121.0195 | 121.2755 | 50.6428 | -121.0885 | 120.6183 | 120.7672 | 120.5965 | 120.5387 | -0.69975
2785.4375 | 120.9412 | -120.52 | 0.49896 | 1.4211e-13 | 0.0017821 | 0.012678 | 0.080375 | 0.010796 | 0.10526 | 0.00030522 | -0.0029439 | 0.0047004 | 0.016968 | 0.037919 | 0.0063733 | -84.9601 | -69.6987 | -88.5295 | 0.4825 | 0.5132 | 0.76466 | -120.6261 | 0.074307 | 0.023253 | -0.005985 | 0.11198 | 0.25637 | 0.012329 | -0.22825 | -0.10612 | -0.016466 | 35.5599 | 31.9906 | 32.0967 | 0.014237 | 0.26569 | 120.2918 | -0.38698 | 120.5943 | 120.514 | 0.22227 | -0.24259 | -0.48663 | 121.0025 | 121.0332 | 121.2847 | 50.8214 | -121.1251 | 120.632 | 120.7764 | 120.5323 | 120.5433 | -0.72721
2787.2031 | 118.7668 | -91.5619 | 27.7039 | 1.4211e-13 | 0.0019957 | 0.01225 | 0.080375 | 0.011224 | 0.1059 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016968 | 0.038132 | 0.0063733 | -84.5023 | -69.5064 | -88.1083 | 0.49165 | 0.5132 | 0.76466 | -120.5804 | 0.069728 | 0.023253 | 0.003172 | 0.11198 | 0.25179 | -0.001407 | -0.22825 | -29.0185 | -27.2122 | 7.0596 | 3.4536 | 32.4721 | -27.1907 | -26.9392 | 91.3336 | -27.5919 | 91.6316 | 91.5651 | 0.23142 | -27.4521 | -27.7053 | 92.0535 | 92.0751 | 92.3265 | 22.0555 | -148.2842 | 91.6739 | 91.8137 | 91.5605 | 91.5851 | -27.9321
2788.8906 | 120.7397 | -99.5911 | 20.9335 | 1.4211e-13 | 0.0026367 | 0.013532 | 0.08123 | 0.010796 | 0.10484 | 0.00030522 | -0.0033713 | 0.0049142 | 0.016754 | 0.037278 | 0.0065869 | -64.2566 | -50.7249 | -67.7578 | 21.0852 | 21.1367 | 21.3363 | -99.7371 | 0.055992 | 0.023253 | -0.005985 | 0.10282 | 0.25179 | 0.007751 | -0.24199 | -0.14602 | 0.15171 | 35.3344 | 31.8333 | 31.9793 | 0.20314 | 0.40278 | 99.3491 | -20.8307 | 99.6471 | 99.5851 | 0.236 | -20.6817 | -20.9258 | 120.6763 | 120.7277 | 120.9274 | 48.8661 | -120.6706 | 99.6939 | 99.8429 | 99.5988 | 99.6143 | -21.1755
2790.6406 | 120.9549 | -114.8163 | 5.896 | 1.4211e-13 | 0.0030641 | 0.013105 | 0.080802 | 0.01101 | 0.10676 | 0.0079357 | -0.0031575 | 0.0042732 | 0.017182 | 0.037919 | 0.0065869 | -78.6648 | -64.3325 | -82.1657 | 6.0223 | 6.0491 | 6.2956 | -114.9895 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.25637 | -0.005985 | -0.23741 | -0.1732 | 0.12635 | 36.1515 | 32.6506 | 32.8238 | 0.15312 | 0.39961 | 114.5789 | -5.7886 | 114.8814 | 114.8103 | 0.23143 | -5.6396 | -5.902 | 120.8386 | 120.8654 | 121.1119 | 50.4837 | -120.8855 | 114.9237 | 115.0727 | 114.8103 | 114.8395 | -6.1334
2792.3281 | 121.051 | -115.4297 | 5.3009 | 1.4211e-13 | 0.0032777 | 0.012891 | 0.081443 | 0.011437 | 0.10719 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016754 | 0.038132 | 0.0063733 | -78.9441 | -64.7446 | -82.3122 | 5.5004 | 5.5821 | 5.8194 | -115.452 | 0.06515 | 0.023253 | -0.001407 | 0.1074 | 0.25637 | 0.067272 | -0.23283 | -0.022269 | 0.19951 | 36.4856 | 33.1175 | 33.1398 | 0.28116 | 0.51853 | 115.1969 | -5.1935 | 115.4948 | 115.4283 | 0.23142 | -5.0445 | -5.2336 | 120.9301 | 121.0118 | 121.2491 | 50.6851 | -120.7529 | 115.5371 | 115.6861 | 115.497 | 115.4529 | -5.5337
2794.0781 | 120.9595 | -115.2328 | 5.6763 | 1.4211e-13 | 0.0037051 | 0.013105 | 0.08123 | 0.011651 | 0.10825 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016968 | 0.038132 | 0.0065869 | -78.8113 | -64.8362 | -82.129 | 5.3905 | 5.4355 | 5.7141 | -115.5985 | 0.06515 | 0.023253 | -0.010564 | 0.1074 | 0.25637 | 0.003172 | -0.23283 | -0.36563 | -0.28574 | 36.4215 | 33.1038 | 33.4695 | -0.24073 | 0.037855 | 115 | -5.5689 | 115.298 | 115.2223 | 0.22227 | -5.4199 | -5.6731 | 120.6234 | 120.6684 | 120.947 | 50.3967 | -121.2748 | 115.3402 | 115.4892 | 115.236 | 115.2561 | -5.9091
2795.8281 | 121.0876 | -104.3427 | 16.5253 | 1.4211e-13 | 0.0039187 | 0.013532 | 0.08123 | 0.011865 | 0.10847 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.038132 | 0.0068005 | -77.9277 | -64.099 | -81.1951 | 6.1093 | 6.2094 | 6.4192 | -114.9803 | 0.06515 | 0.041567 | -0.001407 | 0.1074 | 0.24721 | 0.003172 | -0.23283 | -10.6377 | -10.4159 | 26.415 | 23.1476 | 33.7853 | -10.3159 | -10.106 | 104.1098 | -16.4179 | 104.4078 | 104.3412 | 0.23142 | -16.2781 | -16.5221 | 110.452 | 110.552 | 110.7619 | 40.2436 | -131.5056 | 104.4501 | 104.5899 | 104.3458 | 104.3842 | -16.7581
2797.5938 | 121.0693 | -12.3505 | 108.5953 | 1.4211e-13 | 0.0069101 | 0.018019 | 0.086144 | 0.009087 | 0.10163 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016754 | 0.037919 | 0.0063733 | 21.3272 | 28.4986 | 17.7233 | 108.4226 | 108.4385 | 108.5175 | -12.6597 | 0.02852 | -0.013377 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.26946 | -0.30922 | -0.17271 | 33.6776 | 30.0737 | 30.383 | -0.15683 | -0.077788 | 12.081 | -108.5291 | 12.379 | 12.3078 | 0.22685 | -108.3893 | -108.7478 | 120.773 | 120.7889 | 120.868 | 40.8491 | -121.255 | 12.4167 | 12.5565 | 12.198 | 12.3371 | -108.8647
2799.2969 | 120.3506 | -11.2335 | 109.8404 | 1.4211e-13 | 0.0075513 | 0.018233 | 0.086785 | 0.009087 | 0.10184 | -0.0073253 | -0.0031575 | 0.0042732 | 0.016968 | 0.038132 | 0.0065869 | 22.9159 | 29.7669 | 19.3302 | 109.8373 | 109.8625 | 109.9414 | -11.286 | 0.033099 | -0.013377 | -0.038036 | 0.061616 | 0.21059 | -0.15708 | -0.27404 | -0.05248 | -0.003103 | 34.1494 | 30.5638 | 30.6162 | 0.022103 | 0.10104 | 10.9595 | -109.7788 | 11.2666 | 11.1955 | 0.236 | -109.6298 | -109.9975 | 121.0708 | 121.096 | 121.175 | 41.0004 | -121.1264 | 11.2951 | 11.4441 | 11.0764 | 11.2201 | -110.1144
2801.0469 | 121.0419 | -10.7483 | 110.2753 | 1.4211e-13 | 0.0081923 | 0.018233 | 0.087213 | 0.0093008 | 0.1027 | 0.0079357 | -0.0033713 | 0.0049142 | 0.016968 | 0.038132 | 0.0063733 | 23.5706 | 30.2064 | 20.104 | 110.3226 | 110.3387 | 110.4222 | -10.819 | 0.02852 | -0.013377 | -0.042615 | 0.057037 | 0.20143 | -0.14792 | -0.2832 | -0.07066 | 0.04733 | 34.3189 | 30.8523 | 30.9229 | 0.063435 | 0.14692 | 10.4651 | -110.2182 | 10.7768 | 10.7057 | 0.24058 | -110.0738 | -110.4232 | 121.0709 | 121.087 | 121.1705 | 40.9547 | -121.0942 | 10.8053 | 10.9497 | 10.6004 | 10.7349 | -110.5585
2802.7344 | 120.8359 | -10.6934 | 110.3851 | 1.4211e-13 | 0.0086195 | 0.018447 | 0.086999 | 0.0095144 | 0.1027 | -0.0073253 | -0.0029439 | 0.0044868 | 0.016754 | 0.037705 | 0.0065869 | 23.8773 | 30.2797 | 20.4428 | 110.4462 | 110.4623 | 110.5504 | -10.7228 | 0.019362 | -0.017956 | -0.033458 | 0.070773 | 0.20143 | -0.16166 | -0.26946 | -0.029435 | 0.061084 | 34.5707 | 31.1361 | 31.1656 | 0.077203 | 0.16526 | 10.4239 | -110.3144 | 10.7127 | 10.6599 | 0.236 | -110.1837 | -110.5468 | 121.1396 | 121.1557 | 121.2437 | 40.9731 | -121.1079 | 10.7641 | 10.8948 | 10.5317 | 10.6754 | -110.6546
2804.5 | 121.106 | -10.5698 | 110.4584 | 1.4211e-13 | 0.0088333 | 0.01866 | 0.087213 | 0.0095144 | 0.10355 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.037919 | 0.0061595 | 24.207 | 30.4308 | 20.8273 | 110.5744 | 110.5814 | 110.6694 | -10.6221 | 0.02852 | -0.022535 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27404 | -0.052294 | 0.11604 | 34.7767 | 31.3971 | 31.4494 | 0.12301 | 0.21106 | 10.2957 | -110.3968 | 10.5983 | 10.5226 | 0.22685 | -110.2524 | -110.6109 | 121.1442 | 121.1512 | 121.2392 | 41.0006 | -121.0804 | 10.6314 | 10.7758 | 10.4173 | 10.5472 | -110.7324
2806.25 | 121.1609 | -10.4187 | 110.5911 | 1.4211e-13 | 0.0094743 | 0.01866 | 0.087426 | 0.0099418 | 0.10398 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017182 | 0.038132 | 0.0063733 | 24.5366 | 30.4903 | 21.1707 | 110.7026 | 110.7233 | 110.8022 | -10.503 | 0.023941 | -0.008798 | -0.051772 | 0.070773 | 0.20601 | -0.14792 | -0.26488 | -0.084304 | 0.11148 | 34.9553 | 31.5894 | 31.6737 | 0.13221 | 0.21108 | 10.1538 | -110.5204 | 10.4426 | 10.3669 | 0.21311 | -110.3851 | -110.739 | 121.1213 | 121.142 | 121.2209 | 40.909 | -121.0941 | 10.4895 | 10.6247 | 10.2708 | 10.4099 | -110.856
2807.9375 | 121.0922 | -10.3958 | 110.701 | 1.4211e-13 | 0.0099017 | 0.01866 | 0.087426 | 0.010155 | 0.10441 | -0.0073253 | -0.0031575 | 0.0049142 | 0.016754 | 0.038346 | 0.0063733 | 24.7839 | 30.5819 | 21.4683 | 110.7667 | 110.7874 | 110.8663 | -10.4526 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.20143 | -0.15708 | -0.27862 | -0.056824 | 0.065714 | 35.1797 | 31.8641 | 31.9209 | 0.086449 | 0.16532 | 10.1172 | -110.6302 | 10.4243 | 10.3486 | 0.23142 | -110.4996 | -110.8581 | 121.1625 | 121.1833 | 121.2621 | 40.9777 | -121.1536 | 10.4666 | 10.5972 | 10.2387 | 10.3824 | -110.9796
2809.6875 | 121.1151 | -10.3638 | 110.7468 | 1.4211e-13 | 0.010115 | 0.019088 | 0.08764 | 0.010583 | 0.10484 | 0.015566 | -0.0031575 | 0.0044868 | 0.016541 | 0.037919 | 0.0065869 | 25.0631 | 30.6826 | 21.8025 | 110.8766 | 110.8928 | 110.9716 | -10.3611 | 0.014784 | -0.008798 | -0.047194 | 0.061616 | 0.20601 | -0.14792 | -0.27862 | 0.002711 | 0.12982 | 35.4269 | 32.1663 | 32.1636 | 0.14599 | 0.22485 | 10.0852 | -110.6851 | 10.3786 | 10.3166 | 0.23142 | -110.5408 | -110.8947 | 121.2404 | 121.2565 | 121.3354 | 41.0464 | -121.1078 | 10.4254 | 10.5698 | 10.2158 | 10.355 | -111.0254
2811.375 | 121.2204 | -10.2127 | 110.8475 | 1.4211e-13 | 0.010543 | 0.018874 | 0.088067 | 0.010796 | 0.10569 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016541 | 0.038132 | 0.0065869 | 25.3195 | 30.7925 | 22.0635 | 110.9132 | 110.9294 | 111.0266 | -10.329 | 0.019362 | -0.008798 | -0.051772 | 0.061616 | 0.21059 | -0.1525 | -0.27862 | -0.1163 | 0.065738 | 35.5322 | 32.2762 | 32.3925 | 0.081912 | 0.17909 | 9.9341 | -110.7859 | 10.2321 | 10.1609 | 0.22685 | -110.6369 | -111 | 121.1259 | 121.1421 | 121.2393 | 41.0052 | -121.1765 | 10.2743 | 10.4233 | 10.0602 | 10.2039 | -111.1261
2813.1406 | 121.138 | -9.8602 | 111.2915 | 1.4211e-13 | 0.011184 | 0.019302 | 0.088708 | 0.01101 | 0.1059 | -0.0073253 | -0.0031575 | 0.0047004 | 0.016968 | 0.037919 | 0.0063733 | 25.8506 | 31.2687 | 22.7594 | 111.3756 | 111.3919 | 111.4753 | -9.8849 | 0.02852 | -0.008798 | -0.051772 | 0.061616 | 0.21059 | -0.14792 | -0.27862 | -0.024621 | 0.084125 | 35.7109 | 32.6196 | 32.6442 | 0.10035 | 0.18376 | 9.5816 | -111.2299 | 9.8887 | 9.8085 | 0.22685 | -111.0809 | -111.4394 | 121.2359 | 121.2521 | 121.3355 | 41.1289 | -121.1764 | 9.9218 | 10.0708 | 9.7123 | 9.8514 | -111.5701
2814.8438 | 121.225 | -9.8099 | 111.2915 | 1.4211e-13 | 0.011397 | 0.019729 | 0.088922 | 0.010796 | 0.10633 | -0.0073253 | -0.0031575 | 0.0047004 | 0.017182 | 0.038132 | 0.0061595 | 26.02 | 31.3877 | 23.0203 | 111.3939 | 111.4102 | 111.4936 | -9.8711 | 0.023941 | -0.017956 | -0.047194 | 0.075351 | 0.21059 | -0.15708 | -0.27862 | -0.061239 | 0.10244 | 35.8299 | 32.8302 | 32.8915 | 0.11867 | 0.20207 | 9.5313 | -111.2162 | 9.8338 | 9.7627 | 0.23142 | -111.0809 | -111.4486 | 121.2038 | 121.22 | 121.3035 | 41.1976 | -121.1626 | 9.8852 | 10.0205 | 9.6528 | 9.7919 | -111.5701
2816.5938 | 121.1472 | -9.8465 | 111.319 | 1.4211e-13 | 0.011825 | 0.019302 | 0.089136 | 0.011437 | 0.10697 | 0.0079357 | -0.0035849 | 0.0044868 | 0.016754 | 0.037705 | 0.0063733 | 26.3817 | 31.6441 | 23.5148 | 111.5954 | 111.6162 | 111.7088 | -9.6925 | 0.023941 | -0.013377 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.27404 | 0.15396 | 0.27642 | 36.2282 | 33.3613 | 33.2073 | 0.29725 | 0.3898 | 9.5725 | -111.2528 | 9.8704 | 9.8039 | 0.23142 | -111.113 | -111.4715 | 121.4419 | 121.4627 | 121.5553 | 41.4906 | -121.0115 | 9.9127 | 10.0525 | 9.694 | 9.8331 | -111.593
2818.3594 | 121.1975 | -9.6771 | 111.438 | 1.4211e-13 | 0.012038 | 0.019943 | 0.089563 | 0.011437 | 0.10697 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016754 | 0.038346 | 0.0061595 | 26.4367 | 31.7403 | 23.7025 | 111.5084 | 111.5155 | 111.6126 | -9.7979 | 0.02852 | -0.022535 | -0.047194 | 0.066194 | 0.19685 | -0.15708 | -0.27404 | -0.12073 | 0.070414 | 36.1138 | 33.3796 | 33.5004 | 0.077499 | 0.17463 | 9.4031 | -111.3718 | 9.7056 | 9.6299 | 0.22685 | -111.2411 | -111.5951 | 121.1855 | 121.1926 | 121.2897 | 41.4174 | -121.2358 | 9.7433 | 9.874 | 9.52 | 9.6546 | -111.712
2820.0625 | 121.2708 | -9.7321 | 111.3739 | 1.4211e-13 | 0.012679 | 0.019729 | 0.090204 | 0.011865 | 0.10761 | 0.00030522 | -0.0029439 | 0.0047004 | 0.016968 | 0.037919 | 0.0065869 | 26.6015 | 31.7586 | 24.0047 | 111.4992 | 111.5201 | 111.5989 | -9.8024 | 0.023941 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27862 | -0.070374 | 0.12534 | 36.3335 | 33.7367 | 33.8071 | 0.14616 | 0.22499 | 9.4534 | -111.3123 | 9.756 | 9.6849 | 0.23142 | -111.1679 | -111.5264 | 121.2313 | 121.2521 | 121.3309 | 41.4907 | -121.1763 | 9.7937 | 9.9381 | 9.5796 | 9.7141 | -111.6525
2821.75 | 121.2021 | -9.6863 | 111.4929 | 1.4211e-13 | 0.01332 | 0.019515 | 0.090418 | 0.011865 | 0.10825 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016968 | 0.038346 | 0.0061595 | 26.8029 | 31.896 | 24.2794 | 111.5679 | 111.5796 | 111.6676 | -9.7475 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.20601 | -0.1525 | -0.26488 | -0.061204 | 0.075001 | 36.4892 | 33.9656 | 34.0269 | 0.086672 | 0.17465 | 9.4214 | -111.4267 | 9.7148 | 9.6391 | 0.21769 | -111.2869 | -111.6454 | 121.2542 | 121.2659 | 121.3538 | 41.5822 | -121.2404 | 9.7525 | 9.8923 | 9.5338 | 9.6729 | -111.7578
2823.5 | 121.3165 | -9.3933 | 111.7493 | 1.4211e-13 | 0.013534 | 0.020156 | 0.091273 | 0.012292 | 0.10825 | 0.015566 | -0.0033713 | 0.0038458 | 0.016754 | 0.038132 | 0.0063733 | 27.2287 | 32.0837 | 24.8425 | 111.8472 | 111.8635 | 111.9469 | -9.4819 | 0.023941 | -0.017956 | -0.038036 | 0.066194 | 0.20601 | -0.1525 | -0.27862 | -0.088594 | 0.097934 | 36.622 | 34.2358 | 34.3244 | 0.11422 | 0.19759 | 9.1147 | -111.6831 | 9.4173 | 9.3553 | 0.24058 | -111.5433 | -111.9018 | 121.2405 | 121.2568 | 121.3402 | 41.477 | -121.2312 | 9.4595 | 9.5993 | 9.2408 | 9.3754 | -112.0279
2825.25 | 121.2799 | -8.7433 | 112.413 | 1.4211e-13 | 0.013534 | 0.020156 | 0.091486 | 0.012078 | 0.10868 | -0.0073253 | -0.0031575 | 0.0047004 | 0.017182 | 0.037705 | 0.0063733 | 27.9933 | 32.6514 | 25.7444 | 112.5523 | 112.5686 | 112.6565 | -8.7813 | 0.014784 | -0.017956 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.27404 | -0.038044 | 0.13925 | 36.7366 | 34.4877 | 34.5257 | 0.15561 | 0.24352 | 8.4692 | -112.3423 | 8.7581 | 8.7007 | 0.23142 | -112.207 | -112.5655 | 121.2956 | 121.3119 | 121.3998 | 41.3947 | -121.1944 | 8.8141 | 8.9493 | 8.5908 | 8.7253 | -112.6871
2826.9375 | 121.2845 | -8.3862 | 112.7975 | 1.4211e-13 | 0.013534 | 0.020156 | 0.091914 | 0.012078 | 0.10868 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016754 | 0.037919 | 0.0063733 | 28.268 | 32.7476 | 26.1794 | 112.8316 | 112.8571 | 112.9358 | -8.5203 | 0.023941 | -0.013377 | -0.051772 | 0.061616 | 0.20601 | -0.14792 | -0.27404 | -0.1341 | 0.03401 | 36.6542 | 34.5656 | 34.6997 | 0.059566 | 0.13829 | 8.1122 | -112.7359 | 8.4102 | 8.3345 | 0.22227 | -112.5915 | -112.9455 | 121.2178 | 121.2433 | 121.3221 | 41.1338 | -121.3179 | 8.4478 | 8.5922 | 8.2383 | 8.3729 | -113.0716
2828.6875 | 121.3348 | -7.8781 | 113.3057 | 1.4211e-13 | 0.013534 | 0.02037 | 0.092555 | 0.012719 | 0.10911 | 0.0079357 | -0.0029439 | 0.0047004 | 0.016968 | 0.037919 | 0.0061595 | 28.6984 | 32.917 | 26.7425 | 113.1978 | 113.2143 | 113.3067 | -8.1769 | 0.023941 | -0.00422 | -0.047194 | 0.061616 | 0.20601 | -0.14792 | -0.27862 | -0.2988 | -0.10784 | 36.5765 | 34.6206 | 34.9194 | -0.091396 | 0.001042 | 7.5995 | -113.244 | 7.9021 | 7.8309 | 0.23142 | -113.0997 | -113.4536 | 121.0759 | 121.0924 | 121.1848 | 40.7951 | -121.4826 | 7.9397 | 8.0841 | 7.7302 | 7.8739 | -113.5843
2830.375 | 121.2204 | -7.8552 | 113.4293 | 1.4211e-13 | 0.013748 | 0.020584 | 0.093837 | 0.012506 | 0.10932 | 0.00030522 | -0.0029439 | 0.0044868 | 0.016968 | 0.038132 | 0.0063733 | 29.55 | 33.6496 | 27.7497 | 113.9762 | 113.9927 | 114.0668 | -7.3893 | 0.023941 | -0.017956 | -0.051772 | 0.061616 | 0.20601 | -0.15708 | -0.27404 | 0.46589 | 0.54689 | 37.4052 | 35.6049 | 35.139 | 0.56342 | 0.63749 | 7.5812 | -113.3676 | 7.8792 | 7.8035 | 0.22227 | -113.2233 | -113.5863 | 121.8314 | 121.8479 | 121.922 | 41.5048 | -120.8186 | 7.9168 | 8.0612 | 7.6981 | 7.8373 | -113.7033
2832.125 | 121.2662 | -6.9351 | 114.3539 | 1.4211e-13 | 0.013961 | 0.021225 | 0.094051 | 0.012719 | 0.10954 | 0.0079357 | -0.0031575 | 0.0047004 | 0.017182 | 0.038132 | 0.0061595 | 29.9483 | 33.7686 | 28.2716 | 114.3012 | 114.3224 | 114.4147 | -7.078 | 0.023941 | -0.013377 | -0.051772 | 0.061616 | 0.20143 | -0.14334 | -0.27862 | -0.14285 | -0.052725 | 36.8834 | 35.2067 | 35.3496 | -0.031575 | 0.060785 | 6.6565 | -114.2923 | 6.9591 | 6.8833 | 0.22685 | -114.1525 | -114.4973 | 121.2363 | 121.2575 | 121.3498 | 40.7037 | -121.4319 | 6.9967 | 7.1365 | 6.7918 | 6.9217 | -114.6326
2833.8906 | 121.2982 | -6.7795 | 114.4959 | 1.4211e-13 | 0.013748 | 0.020797 | 0.094692 | 0.012933 | 0.10996 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016968 | 0.038132 | 0.0061595 | 30.3008 | 34.1349 | 28.7157 | 114.6125 | 114.6292 | 114.7123 | -6.7849 | 0.019362 | -0.027113 | -0.042615 | 0.057037 | 0.20143 | -0.1525 | -0.27404 | -0.005439 | 0.1167 | 37.0803 | 35.4952 | 35.5006 | 0.13331 | 0.21649 | 6.5054 | -114.4388 | 6.7988 | 6.7369 | 0.23142 | -114.2944 | -114.6484 | 121.392 | 121.4086 | 121.4918 | 40.9144 | -121.2808 | 6.8365 | 6.9809 | 6.627 | 6.7524 | -114.7699
2835.6406 | 121.2753 | -6.6422 | 114.6423 | 1.4211e-13 | 0.014175 | 0.020797 | 0.09576 | 0.013147 | 0.11018 | 0.00030522 | -0.0029439 | 0.0044868 | 0.016754 | 0.03856 | 0.0061595 | 30.4473 | 34.5424 | 29.0133 | 114.6721 | 114.6933 | 114.781 | -6.73 | 0.023941 | -0.013377 | -0.051772 | 0.066194 | 0.20601 | -0.1525 | -0.27404 | -0.08782 | 0.029734 | 37.0895 | 35.6555 | 35.7433 | 0.050927 | 0.13868 | 6.3681 | -114.5761 | 6.6661 | 6.5904 | 0.22227 | -114.4363 | -114.7948 | 121.3142 | 121.3354 | 121.4232 | 41.1845 | -121.3723 | 6.7083 | 6.8482 | 6.4897 | 6.6288 | -114.9164
2837.3281 | 121.2616 | -6.6879 | 114.6744 | 1.4211e-13 | 0.015457 | 0.021438 | 0.094478 | 0.013147 | 0.11082 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.03856 | 0.0063733 | 30.7861 | 34.8995 | 29.2926 | 114.7224 | 114.7345 | 114.8176 | -6.7071 | 0.019362 | -0.017956 | -0.051772 | 0.075351 | 0.20601 | -0.1525 | -0.27862 | -0.01915 | 0.048053 | 37.4741 | 35.9805 | 35.9997 | 0.060094 | 0.14327 | 6.4093 | -114.599 | 6.7073 | 6.6362 | 0.22685 | -114.4684 | -114.8269 | 121.4104 | 121.4224 | 121.5056 | 41.5874 | -121.3815 | 6.7633 | 6.8939 | 6.5354 | 6.67 | -114.953
2839.0781 | 121.2387 | -6.5186 | 114.798 | 1.4211e-13 | 0.016098 | 0.021225 | 0.094264 | 0.013147 | 0.11125 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016968 | 0.037919 | 0.0063733 | 31.1844 | 35.2521 | 29.7825 | 114.9468 | 114.9588 | 115.0466 | -6.4781 | 0.023941 | -0.017956 | -0.051772 | 0.061616 | 0.21059 | -0.15708 | -0.2832 | 0.040424 | 0.1488 | 37.703 | 36.301 | 36.2606 | 0.16087 | 0.2486 | 6.2354 | -114.7364 | 6.5425 | 6.4668 | 0.23143 | -114.5874 | -114.9551 | 121.4653 | 121.4774 | 121.5651 | 41.7706 | -121.2761 | 6.5802 | 6.7291 | 6.3615 | 6.5006 | -115.0812
2840.7656 | 121.2616 | -6.8848 | 114.4501 | 1.4211e-13 | 0.016953 | 0.021866 | 0.094478 | 0.01336 | 0.1121 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016968 | 0.038132 | 0.0061595 | 30.9418 | 35.2109 | 29.6451 | 114.5072 | 114.5238 | 114.6162 | -6.9177 | 0.019362 | -0.017956 | -0.056351 | 0.061616 | 0.21059 | -0.1525 | -0.27862 | -0.032941 | 0.057173 | 37.8266 | 36.5299 | 36.5628 | 0.073768 | 0.16611 | 6.6061 | -114.3885 | 6.9041 | 6.8284 | 0.22227 | -114.2395 | -114.6026 | 121.392 | 121.4086 | 121.501 | 42.0956 | -121.3678 | 6.9464 | 7.0954 | 6.7323 | 6.8668 | -114.7287
2842.5312 | 121.3852 | -6.546 | 114.7385 | 1.4211e-13 | 0.017808 | 0.021011 | 0.095546 | 0.014001 | 0.11253 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016754 | 0.038132 | 0.0063733 | 31.3126 | 35.8656 | 30.254 | 114.7545 | 114.7711 | 114.8634 | -6.6796 | 0.023941 | -0.013377 | -0.056351 | 0.057037 | 0.20143 | -0.1525 | -0.26946 | -0.13358 | 0.016015 | 37.8587 | 36.8 | 36.9336 | 0.032639 | 0.12497 | 6.2766 | -114.6814 | 6.57 | 6.4897 | 0.21311 | -114.537 | -114.891 | 121.3005 | 121.3171 | 121.4095 | 42.4116 | -121.4181 | 6.6031 | 6.7474 | 6.3935 | 6.5326 | -115.0079
2844.2344 | 121.3943 | -6.427 | 114.8117 | 1.4211e-13 | 0.018449 | 0.022079 | 0.096187 | 0.014215 | 0.11274 | -0.014956 | -0.0033713 | 0.0047004 | 0.017182 | 0.038132 | 0.0061595 | 31.6148 | 36.4883 | 30.7576 | 114.9422 | 114.9588 | 115.042 | -6.501 | 0.019362 | -0.008798 | -0.051772 | 0.070773 | 0.20143 | -0.14792 | -0.2832 | -0.074023 | 0.13049 | 38.0418 | 37.1846 | 37.2587 | 0.14713 | 0.23029 | 6.1438 | -114.7409 | 6.4464 | 6.3752 | 0.23143 | -114.6103 | -114.9596 | 121.3692 | 121.3858 | 121.469 | 42.9153 | -121.3127 | 6.4978 | 6.6284 | 6.2791 | 6.4182 | -115.0949
2845.9688 | 121.2891 | -6.8069 | 114.5874 | 1.4211e-13 | 0.019517 | 0.021866 | 0.096615 | 0.014215 | 0.11381 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016968 | 0.038346 | 0.0063733 | 31.244 | 36.2731 | 30.6935 | 114.5851 | 114.6063 | 114.6894 | -6.8811 | 0.023941 | -0.017956 | -0.047194 | 0.061616 | 0.20143 | -0.14792 | -0.27862 | -0.07413 | -0.002324 | 38.0509 | 37.5005 | 37.5746 | 0.018859 | 0.10204 | 6.5283 | -114.5258 | 6.8309 | 6.7598 | 0.23142 | -114.386 | -114.7353 | 121.392 | 121.4132 | 121.4964 | 43.08 | -121.4685 | 6.8686 | 7.0084 | 6.659 | 6.789 | -114.866
2847.6719 | 120.5017 | -25.3143 | 95.5032 | 1.4211e-13 | 0.01909 | 0.020797 | 0.094264 | 0.015283 | 0.11573 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016968 | 0.038132 | 0.0063733 | 12.3764 | 19.4284 | 12.211 | 94.3578 | 94.404 | 94.5253 | -26.5796 | 0.033099 | -0.008798 | -0.038036 | 0.075351 | 0.21059 | -0.15708 | -0.26946 | -1.2653 | -1.1455 | 37.6908 | 37.5254 | 38.7906 | -1.0992 | -0.97796 | 25.0449 | -95.4279 | 25.3474 | 25.2763 | 0.23143 | -95.2926 | -95.6603 | 119.6721 | 119.7184 | 119.8396 | 44.7427 | -122.0828 | 25.3897 | 25.5249 | 25.1573 | 25.3055 | -95.7727
2849.4375 | 120.7443 | -6.7566 | 114.2212 | 1.4211e-13 | 0.020585 | 0.021866 | 0.096828 | 0.014642 | 0.11381 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016541 | 0.038346 | 0.0063733 | 31.4179 | 36.5158 | 31.0232 | 114.1913 | 114.2125 | 114.2957 | -6.9269 | 0.023941 | -0.017956 | -0.042615 | 0.061616 | 0.20601 | -0.1525 | -0.27862 | -0.17027 | -0.029854 | 38.1745 | 37.7798 | 37.95 | -0.008717 | 0.074493 | 6.478 | -114.1596 | 6.7805 | 6.714 | 0.236 | -114.0152 | -114.3737 | 120.9479 | 120.9691 | 121.0523 | 43.2724 | -121.1481 | 6.8182 | 6.9626 | 6.6041 | 6.7386 | -114.4998
2851.1406 | 121.0922 | -5.809 | 115.2145 | 1.4211e-13 | 0.02144 | 0.021866 | 0.097897 | 0.014642 | 0.11445 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.038132 | 0.0063733 | 32.6495 | 37.665 | 32.273 | 115.3176 | 115.3343 | 115.4174 | -5.8646 | 0.023941 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.2832 | -0.055534 | 0.10308 | 38.4586 | 38.0821 | 38.1376 | 0.11977 | 0.2029 | 5.5258 | -115.1529 | 5.833 | 5.7618 | 0.236 | -115.0085 | -115.367 | 121.1266 | 121.1433 | 121.2265 | 43.474 | -121.0791 | 5.8706 | 6.015 | 5.6565 | 5.7911 | -115.4977
2852.8906 | 120.3186 | -5.7587 | 115.3061 | 1.4211e-13 | 0.02144 | 0.022507 | 0.096828 | 0.014856 | 0.11531 | 0.00030522 | -0.0029439 | 0.0042732 | 0.017182 | 0.038132 | 0.0061595 | 32.9654 | 37.7337 | 32.5432 | 115.4733 | 115.4946 | 115.5868 | -5.7959 | 0.023941 | -0.027113 | -0.051772 | 0.057037 | 0.21059 | -0.1525 | -0.2832 | -0.037204 | 0.1672 | 38.7241 | 38.3018 | 38.339 | 0.18848 | 0.28076 | 5.4755 | -115.2491 | 5.7826 | 5.7069 | 0.23143 | -115.0955 | -115.4586 | 121.232 | 121.2532 | 121.3455 | 43.4923 | -121.102 | 5.8157 | 5.9693 | 5.6062 | 5.7316 | -115.5893
2854.5938 | 121.1975 | -5.8365 | 115.2832 | 1.4211e-13 | 0.022508 | 0.022293 | 0.097683 | 0.015283 | 0.11573 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.037919 | 0.0059459 | 32.9792 | 37.7108 | 32.6714 | 115.3588 | 115.3847 | 115.4632 | -5.8829 | 0.014784 | -0.008798 | -0.047194 | 0.061616 | 0.20601 | -0.14334 | -0.26946 | -0.046383 | 0.075623 | 38.8157 | 38.5078 | 38.5542 | 0.10148 | 0.18003 | 5.567 | -115.2216 | 5.8513 | 5.7893 | 0.22227 | -115.0772 | -115.4265 | 121.1953 | 121.2212 | 121.2997 | 43.5473 | -121.1661 | 5.8981 | 6.0425 | 5.6931 | 5.8277 | -115.5527
2856.3438 | 121.1792 | -5.0034 | 116.098 | 1.4211e-13 | 0.023363 | 0.02272 | 0.098111 | 0.014856 | 0.11573 | 0.00030522 | -0.0029439 | 0.0049142 | 0.016754 | 0.03856 | 0.0063733 | 33.9086 | 38.1412 | 33.555 | 116.1829 | 116.2043 | 116.292 | -5.0907 | 0.010205 | -0.013377 | -0.047194 | 0.061616 | 0.20143 | -0.14334 | -0.27862 | -0.087359 | 0.084914 | 38.9119 | 38.5583 | 38.6457 | 0.10628 | 0.19393 | 4.7247 | -116.0364 | 5.0136 | 4.9562 | 0.23142 | -115.8966 | -116.2414 | 121.1863 | 121.2077 | 121.2953 | 43.1445 | -121.1887 | 5.065 | 5.2048 | 4.86 | 4.99 | -116.3766
2858.0938 | 121.0785 | -4.7379 | 116.4734 | 1.4211e-13 | 0.028919 | 0.022507 | 0.097469 | 0.018488 | 0.11637 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016754 | 0.038346 | 0.0063733 | 34.4351 | 39.881 | 38.3255 | 116.5355 | 116.5569 | 116.6399 | -4.7565 | 0.023941 | -0.022535 | -0.047194 | 0.066194 | 0.20143 | -0.1525 | -0.27404 | -0.018601 | 0.062083 | 39.173 | 43.0634 | 43.082 | 0.083494 | 0.16654 | 4.4638 | -116.4072 | 4.7618 | 4.6907 | 0.22685 | -116.272 | -116.6259 | 121.2733 | 121.2947 | 121.3778 | 44.6189 | -121.2298 | 4.804 | 4.9393 | 4.5854 | 4.7153 | -116.7474
2859.7812 | 121.2204 | -4.66 | 116.5146 | 1.4211e-13 | 0.12293 | 0.021225 | 0.079734 | 0.075964 | 0.12471 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016113 | 0.038346 | 0.0061595 | 35.1814 | 67.3343 | 115.7763 | 116.302 | 116.3188 | 116.3973 | -4.9991 | 0.02852 | -0.017956 | -0.051772 | 0.066194 | 0.21059 | -0.16166 | -0.27862 | -0.3391 | -0.21261 | 39.8414 | 120.4363 | 120.7754 | -0.19581 | -0.11732 | 4.3814 | -116.4484 | 4.6886 | 4.6083 | 0.22685 | -116.304 | -116.6762 | 120.962 | 120.9788 | 121.0573 | 71.9944 | -121.5137 | 4.7262 | 4.8706 | 4.4984 | 4.6421 | -116.7932
2861.5156 | 121.1792 | -3.5385 | 117.7231 | 1.4211e-13 | 0.12251 | 0.021866 | 0.079947 | 0.076391 | 0.12407 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.03856 | 0.0061595 | 36.5 | 64.9764 | 117.3375 | 117.6526 | 117.6787 | 117.7571 | -3.6575 | 0.023941 | -0.022535 | -0.042615 | 0.066194 | 0.20143 | -0.15708 | -0.2832 | -0.119 | -0.070485 | 40.0385 | 120.876 | 120.995 | -0.044363 | 0.034024 | 3.2553 | -117.6569 | 3.5625 | 3.4959 | 0.24058 | -117.5217 | -117.8802 | 121.1911 | 121.2172 | 121.2956 | 68.5149 | -121.3806 | 3.6047 | 3.7399 | 3.3814 | 3.516 | -118.0063
2863.2656 | 121.3074 | -3.5477 | 117.659 | 1.4211e-13 | 0.14217 | 0.021225 | 0.079734 | 0.076391 | 0.13496 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.038132 | 0.0063733 | 37.4706 | 105.497 | 117.3283 | 117.6297 | 117.6558 | 117.7388 | -3.685 | 0.023941 | -0.013377 | -0.047194 | 0.061616 | 0.20143 | -0.15708 | -0.27862 | -0.13732 | -0.029291 | 41.0182 | 120.876 | 121.0133 | -0.003172 | 0.079796 | 3.269 | -117.5974 | 3.5716 | 3.5005 | 0.23142 | -117.4576 | -117.8161 | 121.1774 | 121.2035 | 121.2865 | 109.0447 | -121.344 | 3.6093 | 3.7491 | 3.3906 | 3.5343 | -117.9376
2865.0312 | 121.2112 | -3.0899 | 118.1488 | 1.4211e-13 | 0.14452 | 0.021652 | 0.080375 | 0.076177 | 0.13582 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.038346 | 0.0065869 | 38.1207 | 108.757 | 117.951 | 118.2478 | 118.274 | 118.3432 | -3.0989 | 0.019362 | -0.022535 | -0.051772 | 0.066194 | 0.19685 | -0.14792 | -0.26946 | -0.008979 | 0.098985 | 41.2106 | 121.0409 | 121.0499 | 0.12518 | 0.19437 | 2.8204 | -118.0826 | 3.1093 | 3.0381 | 0.21769 | -117.952 | -118.2967 | 121.3377 | 121.3639 | 121.4331 | 111.8469 | -121.2477 | 3.1561 | 3.2868 | 2.942 | 3.0674 | -118.4183
2866.7344 | 121.2158 | -3.3737 | 117.897 | 1.4211e-13 | 0.1505 | 0.021225 | 0.080802 | 0.076177 | 0.13902 | -0.0073253 | -0.0031575 | 0.0040594 | 0.016968 | 0.038132 | 0.0061595 | 38.0246 | 117.8684 | 117.6488 | 117.941 | 117.9626 | 118.0501 | -3.4103 | 0.023941 | -0.022535 | -0.047194 | 0.057037 | 0.20143 | -0.15708 | -0.2832 | -0.036533 | 0.044003 | 41.3983 | 121.0225 | 121.0591 | 0.065579 | 0.1531 | 3.0905 | -117.84 | 3.3977 | 3.3265 | 0.236 | -117.6956 | -118.0541 | 121.3148 | 121.3363 | 121.4239 | 121.2421 | -121.3073 | 3.4308 | 3.5751 | 3.2166 | 3.3512 | -118.1802
2868.4844 | 121.225 | -3.4058 | 117.9062 | 1.4211e-13 | 0.15135 | 0.021652 | 0.079947 | 0.076391 | 0.13924 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016968 | 0.038132 | 0.0063733 | 38.1207 | 117.9645 | 117.7083 | 117.996 | 118.0267 | 118.1051 | -3.369 | 0.014784 | -0.022535 | -0.051772 | 0.057037 | 0.19685 | -0.15708 | -0.27862 | 0.036721 | 0.089788 | 41.5265 | 121.1141 | 121.0774 | 0.12053 | 0.19889 | 3.1271 | -117.8492 | 3.4205 | 3.354 | 0.22685 | -117.7093 | -118.0633 | 121.4017 | 121.4325 | 121.5108 | 121.3703 | -121.2752 | 3.4628 | 3.6026 | 3.2487 | 3.3832 | -118.1848
2870.2344 | 121.2112 | -3.3646 | 117.984 | 1.4211e-13 | 0.15306 | 0.021652 | 0.078665 | 0.07575 | 0.13902 | 0.015566 | -0.0033713 | 0.0047004 | 0.016541 | 0.038346 | 0.0061595 | 38.1024 | 118.0012 | 117.7312 | 118.0143 | 118.0405 | 118.1188 | -3.3645 | 0.033099 | -0.008798 | -0.051772 | 0.057037 | 0.19685 | -0.15708 | -0.27862 | 0.000101 | 0.030282 | 41.467 | 121.0958 | 121.0957 | 0.056446 | 0.13481 | 3.0859 | -117.927 | 3.3977 | 3.3128 | 0.22685 | -117.7872 | -118.1411 | 121.3789 | 121.405 | 121.4834 | 121.3657 | -121.3485 | 3.4216 | 3.5614 | 3.2075 | 3.3558 | -118.2626
2871.9219 | 121.2341 | -3.6667 | 117.6544 | 1.4211e-13 | 0.15264 | 0.021438 | 0.080588 | 0.075536 | 0.13924 | 0.015566 | -0.0035849 | 0.0042732 | 0.016541 | 0.038132 | 0.0061595 | 37.846 | 117.6669 | 117.3879 | 117.6892 | 117.7108 | 117.7937 | -3.6987 | 0.014784 | -0.017956 | -0.051772 | 0.052459 | 0.20143 | -0.1525 | -0.27862 | -0.032036 | 0.034806 | 41.5127 | 121.0545 | 121.0866 | 0.056353 | 0.13932 | 3.3881 | -117.602 | 3.6815 | 3.6149 | 0.22685 | -117.453 | -117.8069 | 121.3559 | 121.3775 | 121.4604 | 121.3336 | -121.3531 | 3.7191 | 3.8681 | 3.5142 | 3.6487 | -117.933
2873.6719 | 121.2845 | -2.7466 | 118.5516 | 1.4211e-13 | 0.14879 | 0.022079 | 0.078665 | 0.075964 | 0.13817 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.038346 | 0.0061595 | 38.5511 | 118.5872 | 118.2623 | 118.6141 | 118.6357 | 118.7232 | -2.7829 | 0.023941 | -0.017956 | -0.047194 | 0.057037 | 0.20601 | -0.1525 | -0.27404 | -0.036356 | 0.062424 | 41.2977 | 121.0089 | 121.0452 | 0.084079 | 0.17156 | 2.4725 | -118.4946 | 2.7705 | 2.6994 | 0.22685 | -118.3456 | -118.7041 | 121.3606 | 121.3823 | 121.4698 | 121.3338 | -121.3346 | 2.8036 | 2.9526 | 2.5941 | 2.7286 | -118.8257
2875.4375 | 121.3623 | -2.2842 | 118.9865 | 1.4211e-13 | 0.14751 | 0.022079 | 0.079734 | 0.073186 | 0.1403 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016754 | 0.03856 | 0.0063733 | 39.0639 | 119.0268 | 116.0373 | 119.049 | 119.0753 | 119.1536 | -2.3571 | 0.019362 | -0.027113 | -0.06093 | 0.066194 | 0.19227 | -0.1525 | -0.27862 | -0.072857 | 0.062496 | 41.3481 | 118.3215 | 118.3944 | 0.088781 | 0.16707 | 2.0056 | -118.9203 | 2.3036 | 2.2233 | 0.21769 | -118.7942 | -119.139 | 121.3332 | 121.3595 | 121.4378 | 121.311 | -121.3436 | 2.3504 | 2.4765 | 2.1317 | 2.2571 | -119.2651
2877.125 | 121.3165 | -2.0004 | 119.2841 | 1.4211e-13 | 0.14387 | 0.024002 | 0.08123 | 0.069981 | 0.14116 | 0.00030522 | -0.0033713 | 0.0040594 | 0.017182 | 0.038132 | 0.0065869 | 40.9914 | 119.3289 | 112.0587 | 119.3512 | 119.3638 | 119.4466 | -2.0778 | 0.019362 | -0.022535 | -0.047194 | 0.066194 | 0.20143 | -0.1525 | -0.27862 | -0.077357 | 0.067122 | 42.9918 | 114.0592 | 114.1365 | 0.079706 | 0.16255 | 1.7218 | -119.2179 | 2.0198 | 1.9532 | 0.23142 | -119.0826 | -119.4366 | 121.3516 | 121.3642 | 121.447 | 121.3294 | -121.3618 | 2.0666 | 2.2019 | 1.8479 | 1.9779 | -119.5627
2878.875 | 121.312 | -1.8311 | 119.4672 | 1.4211e-13 | 0.14644 | 0.025071 | 0.081871 | 0.067844 | 0.14671 | 0.00030522 | -0.0029439 | 0.0044868 | 0.016968 | 0.038346 | 0.0063733 | 42.1543 | 119.5533 | 109.7788 | 119.5664 | 119.5881 | 119.6755 | -1.8717 | 0.019362 | -0.017956 | -0.056351 | 0.057037 | 0.21059 | -0.1525 | -0.2832 | -0.040677 | 0.099201 | 43.9853 | 111.6098 | 111.6505 | 0.12097 | 0.20838 | 1.5479 | -119.4101 | 1.8504 | 1.7747 | 0.22685 | -119.2566 | -119.6197 | 121.3974 | 121.4192 | 121.5066 | 121.3844 | -121.3389 | 1.8881 | 2.0416 | 1.6786 | 1.8131 | -119.7504
2880.5625 | 121.3715 | -1.5381 | 119.7784 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.0017394 | -0.012707 | 0.013388 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.03856 | 0.0065869 | -1.2443 | -1.07 | -1.1301 | -0.81777 | -0.77806 | -0.52193 | -1.597 | 0.019362 | -0.017956 | -0.047194 | 0.061616 | 0.21059 | -0.14792 | -0.27862 | -0.058911 | -120.5962 | 0.29381 | 0.408 | 0.46691 | -120.5565 | -120.3004 | 1.2595 | -119.7168 | 1.5574 | 1.4909 | 0.23142 | -119.5679 | -119.9264 | 0.72032 | 0.76003 | 1.0162 | 0.4681 | -121.3754 | 1.5997 | 1.7487 | 1.3902 | 1.5201 | -120.0571
2882.3125 | 121.3348 | -1.6434 | 119.7601 | 1.4211e-13 | -0.018517 | -0.00035676 | 0.001953 | -0.013134 | 0.013174 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.03856 | 0.0065869 | -1.1985 | -1.2211 | -1.3041 | -0.9597 | -0.92458 | -0.67302 | -1.6474 | 0.023941 | -0.008798 | -0.047194 | 0.061616 | 0.21516 | -0.15708 | -0.26946 | -0.003993 | -120.7198 | 0.44488 | 0.33931 | 0.3433 | -120.6847 | -120.4332 | 1.3739 | -119.6985 | 1.6673 | 1.5962 | 0.22227 | -119.545 | -119.9172 | 0.68368 | 0.71879 | 0.97035 | 0.42229 | -121.4075 | 1.705 | 1.8585 | 1.4863 | 1.6346 | -120.0296
2884.0781 | 121.3669 | -1.6022 | 119.8196 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.0021668 | -0.013561 | 0.012961 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.038346 | 0.0061595 | -1.2031 | -1.2119 | -1.2949 | -0.96885 | -0.92458 | -0.67302 | -1.6153 | 0.02852 | -0.013377 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27862 | -0.01314 | -120.7885 | 0.39911 | 0.30727 | 0.32041 | -120.7442 | -120.4927 | 1.3236 | -119.758 | 1.6307 | 1.555 | 0.23142 | -119.6136 | -119.9721 | 0.63332 | 0.67759 | 0.92915 | 0.39025 | -121.435 | 1.6638 | 1.8082 | 1.4497 | 1.5888 | -120.0983
2885.7656 | 121.3623 | -1.5884 | 119.8059 | 1.4211e-13 | -0.017448 | -0.00035676 | 0.0017394 | -0.013348 | 0.013815 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016541 | 0.038346 | 0.0063733 | -1.1573 | -1.1753 | -1.2812 | -0.8956 | -0.90169 | -0.64555 | -1.6062 | 0.023941 | -0.013377 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27404 | -0.017715 | -120.7015 | 0.43116 | 0.30727 | 0.32498 | -120.7076 | -120.4515 | 1.3144 | -119.7443 | 1.6124 | 1.5412 | 0.22685 | -119.5999 | -119.9584 | 0.69284 | 0.68675 | 0.94289 | 0.41315 | -121.4121 | 1.6501 | 1.7944 | 1.4359 | 1.5751 | -120.0799
2887.4531 | 121.4584 | -1.5518 | 119.8196 | 1.4211e-13 | -0.017876 | -0.00057056 | 0.0015258 | -0.013348 | 0.014243 | -0.014956 | -0.0033713 | 0.0047004 | 0.016754 | 0.03856 | 0.0061595 | -1.1664 | -1.1295 | -1.2537 | -0.90018 | -0.90169 | -0.65013 | -1.597 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.21516 | -0.1525 | -0.2832 | -0.045178 | -120.7198 | 0.38538 | 0.29812 | 0.34329 | -120.7213 | -120.4698 | 1.2686 | -119.7489 | 1.5803 | 1.5046 | 0.236 | -119.6045 | -119.9721 | 0.65164 | 0.65013 | 0.90169 | 0.42231 | -121.4166 | 1.6226 | 1.767 | 1.3993 | 1.5384 | -120.1028
2889.2188 | 121.3531 | -1.5427 | 119.8654 | 1.4211e-13 | -0.017876 | -0.00014316 | 0.001953 | -0.013561 | 0.013815 | 0.0079357 | -0.0029439 | 0.0049142 | 0.016754 | 0.038346 | 0.0063733 | -1.1664 | -1.1295 | -1.2583 | -0.8956 | -0.91543 | -0.65471 | -1.5833 | 0.023941 | -0.013377 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27862 | -0.040596 | -120.761 | 0.37622 | 0.28438 | 0.32498 | -120.7808 | -120.5201 | 1.264 | -119.8038 | 1.5666 | 1.4955 | 0.23142 | -119.6594 | -120.0179 | 0.64707 | 0.62724 | 0.88795 | 0.41316 | -121.4487 | 1.6043 | 1.7487 | 1.3902 | 1.5293 | -120.144
2890.9062 | 121.3394 | -1.5564 | 119.9066 | 1.4211e-13 | -0.018089 | -0.00014316 | 0.0017394 | -0.013134 | 0.014243 | 0.00030522 | -0.0033713 | 0.0047004 | 0.017182 | 0.038346 | 0.0063733 | -1.139 | -1.1616 | -1.2445 | -0.86355 | -0.81469 | -0.6135 | -1.5604 | 0.014784 | -0.013377 | -0.056351 | 0.061616 | 0.21516 | -0.15708 | -0.27404 | -0.00397 | -120.7702 | 0.41742 | 0.31185 | 0.31582 | -120.7213 | -120.5201 | 1.2824 | -119.845 | 1.5712 | 1.5 | 0.21769 | -119.6915 | -120.0637 | 0.69285 | 0.74171 | 0.94289 | 0.39484 | -121.467 | 1.618 | 1.7716 | 1.3993 | 1.543 | -120.1807
2892.6562 | 121.463 | -1.5198 | 119.8975 | 1.4211e-13 | -0.017876 | -0.00014316 | 0.0021668 | -0.01292 | 0.014029 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016968 | 0.038132 | 0.0065869 | -1.1161 | -1.1432 | -1.24 | -0.84981 | -0.79637 | -0.60893 | -1.5466 | 0.02852 | -0.017956 | -0.056351 | 0.070773 | 0.20143 | -0.15708 | -0.26946 | -0.026854 | -120.7473 | 0.4037 | 0.27981 | 0.30666 | -120.6938 | -120.5064 | 1.2503 | -119.8267 | 1.5483 | 1.4634 | 0.21311 | -119.696 | -120.0545 | 0.66996 | 0.7234 | 0.91085 | 0.37653 | -121.4441 | 1.5905 | 1.7212 | 1.3627 | 1.5018 | -120.1669
2894.4062 | 121.376 | -1.5335 | 119.9341 | 1.4211e-13 | -0.017662 | -0.00014316 | 0.0017394 | -0.013561 | 0.014029 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016968 | 0.038132 | 0.0061595 | -1.377 | -1.4042 | -1.3773 | -1.1154 | -1.0665 | -0.87906 | -1.5558 | 0.023941 | -0.017956 | -0.042615 | 0.061616 | 0.21059 | -0.15708 | -0.26946 | -0.022279 | -121.0494 | 0.15646 | 0.15619 | 0.17847 | -121.0006 | -120.8131 | 1.264 | -119.8725 | 1.5574 | 1.4909 | 0.22685 | -119.7235 | -120.0912 | 0.41815 | 0.46698 | 0.65445 | 0.12928 | -121.4899 | 1.5951 | 1.7441 | 1.3764 | 1.5156 | -120.2035
2896.0938 | 121.3898 | -1.387 | 120.1263 | 1.4211e-13 | -0.017876 | -0.00057056 | 0.0021668 | -0.013561 | 0.014456 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016968 | 0.038346 | 0.0063733 | -1.2489 | -1.2669 | -1.2079 | -0.99174 | -0.9429 | -0.75544 | -1.423 | 0.02852 | -0.013377 | -0.047194 | 0.061616 | 0.20143 | -0.1525 | -0.27404 | -0.035974 | -121.1181 | 0.13817 | 0.17911 | 0.21508 | -121.0692 | -120.8818 | 1.113 | -120.0647 | 1.4155 | 1.3398 | 0.22685 | -119.9249 | -120.2788 | 0.39528 | 0.44412 | 0.63158 | 0.12016 | -121.5493 | 1.4486 | 1.5885 | 1.2345 | 1.3736 | -120.4004
2897.8438 | 121.4676 | -1.4282 | 120.0073 | 1.4211e-13 | -0.017662 | -0.00035676 | 0.0015258 | -0.013775 | 0.014243 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016541 | 0.03856 | 0.0063733 | -1.2809 | -1.3035 | -1.2125 | -1.0238 | -0.97953 | -0.79207 | -1.455 | 0.02852 | -0.013377 | -0.056351 | 0.070773 | 0.20143 | -0.14792 | -0.27862 | -0.026827 | -121.0311 | 0.14732 | 0.21573 | 0.24255 | -120.9869 | -120.7994 | 1.1496 | -119.9366 | 1.4567 | 1.3719 | 0.22227 | -119.8059 | -120.1552 | 0.40443 | 0.44869 | 0.63615 | 0.12473 | -121.4624 | 1.499 | 1.6297 | 1.2803 | 1.4148 | -120.2859
2899.6094 | 121.3943 | -1.4694 | 120.0531 | 1.4211e-13 | -0.018089 | -0.00035676 | 0.001953 | -0.013561 | 0.014243 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016968 | 0.038346 | 0.0061595 | -1.2946 | -1.3172 | -1.2125 | -1.0375 | -0.99327 | -0.79207 | -1.5283 | 0.019362 | -0.008798 | -0.038036 | 0.066194 | 0.20143 | -0.14792 | -0.27862 | -0.058892 | -121.0906 | 0.17479 | 0.25692 | 0.31582 | -121.0464 | -120.8452 | 1.1908 | -119.9869 | 1.4888 | 1.4314 | 0.24058 | -119.8517 | -120.201 | 0.43189 | 0.47615 | 0.67735 | 0.15219 | -121.5814 | 1.5356 | 1.6709 | 1.3215 | 1.4606 | -120.3317
2901.2969 | 121.4035 | -1.4603 | 120.0211 | 1.4211e-13 | -0.017876 | -0.00014316 | 0.0017394 | -0.013561 | 0.014029 | 0.0079357 | -0.0031575 | 0.0047004 | 0.016541 | 0.038346 | 0.0061595 | -1.084 | -1.1066 | -1.0797 | -0.82692 | -0.78264 | -0.53567 | -1.4642 | 0.023941 | -0.013377 | -0.042615 | 0.061616 | 0.21059 | -0.15708 | -0.27862 | -0.003942 | -120.848 | 0.37624 | 0.38054 | 0.38448 | -120.8037 | -120.5567 | 1.1816 | -119.9594 | 1.4842 | 1.4177 | 0.236 | -119.8105 | -120.1781 | 0.63334 | 0.67763 | 0.9246 | 0.35365 | -121.4853 | 1.5219 | 1.6709 | 1.3032 | 1.4469 | -120.2997
2903.0469 | 121.0098 | -31.4163 | 89.566 | 1.4211e-13 | -0.015525 | -0.0027074 | 0.0021668 | -0.008647 | 0.040951 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016754 | 0.03856 | 0.0063733 | -49.2349 | -49.5437 | -45.9286 | -8.427 | -8.2875 | -8.5162 | -52.0796 | 0.046835 | 0.004938 | -0.019721 | 0.07993 | 0.22432 | -0.12961 | -0.25572 | -20.6633 | -97.9931 | -17.8186 | -14.5122 | 6.1511 | -97.8535 | -98.0822 | 31.1606 | -89.4861 | 31.4632 | 31.3966 | 0.236 | -89.3417 | -89.6956 | 22.9893 | 23.1288 | 22.9002 | -18.1273 | -141.6457 | 31.4963 | 31.6406 | 31.2867 | 31.4213 | -89.8218
2904.7344 | 120.5566 | -13.2843 | 107.8857 | 1.4211e-13 | -0.017235 | -0.00057056 | 0.0015258 | -0.01292 | 0.02108 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.038346 | 0.0061595 | -13.2809 | -13.3452 | -12.2004 | -8.4316 | -8.2967 | -8.5162 | -13.4885 | 0.033099 | -0.00422 | -0.042615 | 0.075351 | 0.21059 | -0.14792 | -0.26946 | -0.20416 | -116.3174 | 0.003446 | 1.0839 | 1.2881 | -116.1824 | -116.4019 | 13.0148 | -107.8104 | 13.3174 | 13.2417 | 0.22685 | -107.6752 | -108.0337 | 4.8527 | 4.9877 | 4.7681 | -0.060918 | -121.3742 | 13.3597 | 13.4949 | 13.1364 | 13.2801 | -108.1552
2906.4844 | 120.9366 | -11.5311 | 109.6985 | 1.4211e-13 | -0.017235 | -0.00078416 | 0.0015258 | -0.01292 | 0.020225 | 0.00030522 | -0.0029439 | 0.0044868 | 0.016754 | 0.03856 | 0.0061595 | -11.6326 | -11.6923 | -10.4927 | -8.3538 | -8.2005 | -8.3742 | -11.6615 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.14334 | -0.27404 | -0.13041 | -118.0523 | -0.10157 | 1.0384 | 1.1688 | -117.899 | -118.0727 | 11.257 | -109.6277 | 11.5596 | 11.4885 | 0.23142 | -109.4879 | -109.8418 | 3.1773 | 3.3306 | 3.1568 | -0.16128 | -121.36 | 11.6018 | 11.7417 | 11.3877 | 11.5177 | -109.9725
2908.1719 | 121.2112 | -10.8582 | 110.376 | 1.4211e-13 | -0.017448 | -0.00078416 | 0.0017394 | -0.01292 | 0.019798 | 0.015566 | -0.0031575 | 0.0049142 | 0.016754 | 0.038132 | 0.0059459 | -10.9779 | -11.0376 | -9.8471 | -8.3034 | -8.1227 | -8.2735 | -11.0113 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.21059 | -0.14792 | -0.27404 | -0.15311 | -118.6794 | -0.11977 | 1.011 | 1.1641 | -118.4986 | -118.6495 | 10.5841 | -110.3052 | 10.8867 | 10.811 | 0.22685 | -110.1654 | -110.5239 | 2.5547 | 2.7355 | 2.5846 | -0.17945 | -121.3872 | 10.9289 | 11.0687 | 10.7102 | 10.8448 | -110.65
2909.9375 | 121.2021 | -10.2722 | 111.0214 | 1.4211e-13 | -0.017235 | -0.00078416 | 0.001953 | -0.013348 | 0.019798 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016754 | 0.038132 | 0.0061595 | -10.1904 | -10.2409 | -9.4397 | -8.1844 | -7.999 | -8.0904 | -10.2832 | 0.019362 | -0.013377 | -0.038036 | 0.075351 | 0.21059 | -0.1525 | -0.27404 | -0.011 | -119.2058 | 0.081773 | 0.83255 | 0.84355 | -119.0204 | -119.1118 | 9.9982 | -110.9461 | 10.2916 | 10.2342 | 0.236 | -110.8108 | -111.1739 | 2.0878 | 2.2732 | 2.1819 | 0.03129 | -121.3046 | 10.3476 | 10.4828 | 10.1197 | 10.2588 | -111.2955
2911.7031 | 121.1655 | -10.1395 | 111.145 | 1.4211e-13 | -0.017448 | -0.00057056 | 0.001953 | -0.012279 | 0.018302 | 0.0079357 | -0.0035849 | 0.0044868 | 0.016968 | 0.038346 | 0.0063733 | -7.8738 | -7.9058 | -7.9975 | -7.2046 | -7.0603 | -6.9366 | -10.2191 | 0.02852 | -0.008798 | -0.038036 | 0.070773 | 0.20601 | -0.1525 | -0.27404 | -0.079647 | -118.3496 | 2.2657 | 2.142 | 2.2216 | -118.2054 | -118.0816 | 9.8654 | -111.0742 | 10.168 | 10.1014 | 0.236 | -110.939 | -111.2975 | 2.9348 | 3.0791 | 3.2029 | 2.2336 | -121.3641 | 10.2102 | 10.3455 | 9.987 | 10.1307 | -111.4191
2913.4531 | 121.344 | -9.0591 | 112.175 | 1.4211e-13 | -0.017662 | -0.00057056 | 0.001953 | -0.012066 | 0.017448 | 0.0079357 | -0.0033713 | 0.0040594 | 0.016968 | 0.038773 | 0.0059459 | -7.3335 | -7.3518 | -7.4069 | -6.7834 | -6.662 | -6.497 | -9.5048 | 0.02852 | -0.013377 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.27404 | -0.44566 | -118.9584 | 1.7256 | 1.6522 | 2.0979 | -118.837 | -118.672 | 8.7851 | -112.1088 | 9.0877 | 9.0165 | 0.23142 | -111.9644 | -112.3275 | 2.2757 | 2.3972 | 2.5621 | 1.7073 | -121.6798 | 9.1253 | 9.2697 | 8.9066 | 9.0458 | -112.449
2915.1562 | 121.2524 | -6.4499 | 114.9307 | 1.4211e-13 | -0.017876 | -0.00057056 | 0.0017394 | -0.012707 | 0.016379 | -0.0073253 | -0.0031575 | 0.0047004 | 0.016968 | 0.038346 | 0.0061595 | -5.3648 | -5.3693 | -5.3879 | -5.0024 | -4.9449 | -4.7068 | -7.0139 | 0.02852 | -0.008798 | -0.038036 | 0.066194 | 0.21059 | -0.15708 | -0.27404 | -0.56398 | -119.9331 | 1.0851 | 1.062 | 1.626 | -119.8756 | -119.6375 | 6.1758 | -114.8645 | 6.4784 | 6.4119 | 0.236 | -114.7201 | -115.0878 | 1.4475 | 1.505 | 1.7431 | 1.0806 | -121.9446 | 6.5161 | 6.6605 | 6.2928 | 6.4411 | -115.2048
2916.9062 | 121.3623 | -5.5801 | 115.7455 | 1.4211e-13 | -0.017662 | -0.00035676 | 0.0015258 | -0.012707 | 0.015952 | 0.015566 | -0.0035849 | 0.0044868 | 0.016968 | 0.038773 | 0.0061595 | -4.2614 | -4.2659 | -4.2937 | -3.9494 | -3.9055 | -3.6629 | -5.6951 | 0.02852 | -0.013377 | -0.038036 | 0.075351 | 0.21059 | -0.14792 | -0.27404 | -0.115 | -119.6949 | 1.3187 | 1.2865 | 1.4015 | -119.651 | -119.4084 | 5.3061 | -115.6702 | 5.6087 | 5.5421 | 0.236 | -115.535 | -115.8935 | 1.6308 | 1.6747 | 1.9173 | 1.3143 | -121.4407 | 5.6555 | 5.7907 | 5.4322 | 5.5668 | -116.0196
2918.6719 | 121.4355 | -5.2643 | 116.0522 | 1.4211e-13 | -0.018089 | -0.00014316 | 0.0017394 | -0.012707 | 0.015952 | -0.0073253 | -0.0029439 | 0.0044868 | 0.016754 | 0.038132 | 0.0061595 | -3.9455 | -3.9499 | -3.9549 | -3.6426 | -3.5987 | -3.3469 | -5.3471 | 0.023941 | -0.013377 | -0.047194 | 0.070773 | 0.21516 | -0.15708 | -0.26946 | -0.082854 | -119.6949 | 1.3188 | 1.3094 | 1.3922 | -119.6509 | -119.3992 | 4.9948 | -115.9815 | 5.2882 | 5.2171 | 0.22227 | -115.8371 | -116.2093 | 1.6217 | 1.6656 | 1.9174 | 1.3144 | -121.3994 | 5.3351 | 5.4794 | 5.1072 | 5.2509 | -116.3217
2920.375 | 121.4355 | -5.3467 | 115.9882 | 1.4211e-13 | -0.017876 | -0.00014316 | 0.0017394 | -0.012707 | 0.016379 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.038132 | 0.0059459 | -4.0188 | -4.0186 | -4.0144 | -3.7159 | -3.6719 | -3.4248 | -5.4891 | 0.02852 | -0.017956 | -0.042615 | 0.070773 | 0.20601 | -0.15708 | -0.26946 | -0.1424 | -119.704 | 1.3279 | 1.3323 | 1.4747 | -119.6601 | -119.4129 | 5.0772 | -115.9174 | 5.3752 | 5.3041 | 0.22685 | -115.7822 | -116.1452 | 1.6308 | 1.6747 | 1.9219 | 1.3281 | -121.4772 | 5.4175 | 5.5527 | 5.1896 | 5.3287 | -116.2576
2922.125 | 121.3303 | -5.0674 | 116.3452 | 1.4211e-13 | -0.018089 | -0.00014316 | 0.001953 | -0.012707 | 0.015952 | -0.0073253 | -0.0029439 | 0.0040594 | 0.016968 | 0.038773 | 0.0059459 | -3.68 | -3.6844 | -3.6848 | -3.3817 | -3.3285 | -3.0905 | -5.0724 | 0.019362 | -0.017956 | -0.042615 | 0.070773 | 0.21516 | -0.1525 | -0.26946 | -0.004957 | -119.7269 | 1.3875 | 1.3827 | 1.3876 | -119.6737 | -119.4357 | 4.798 | -116.2744 | 5.0868 | 5.0248 | 0.22685 | -116.13 | -116.4977 | 1.6858 | 1.7389 | 1.9769 | 1.3831 | -121.4176 | 5.1382 | 5.2826 | 4.9149 | 5.0495 | -116.6147
2923.875 | 121.4401 | -5.3467 | 116.0889 | 1.4211e-13 | -0.018089 | -0.00057056 | 0.0021668 | -0.012493 | 0.015952 | 0.00030522 | -0.0037985 | 0.0049142 | 0.017182 | 0.03856 | 0.0061595 | -3.9409 | -3.9362 | -3.9412 | -3.6335 | -3.5895 | -3.3424 | -5.4982 | 0.033099 | -0.008798 | -0.038036 | 0.066194 | 0.20601 | -0.1525 | -0.27404 | -0.15156 | -119.7223 | 1.4057 | 1.4055 | 1.5571 | -119.6784 | -119.4312 | 5.0726 | -116.0227 | 5.3798 | 5.3086 | 0.236 | -115.8829 | -116.2414 | 1.7132 | 1.7572 | 2.0043 | 1.4105 | -121.5871 | 5.4129 | 5.5527 | 5.1942 | 5.3379 | -116.3629
2925.625 | 121.431 | -5.6763 | 115.7043 | 1.4211e-13 | -0.018089 | -0.00057056 | 0.0021668 | -0.012493 | 0.016593 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.038132 | 0.0063733 | -4.1103 | -4.1102 | -4.138 | -3.7983 | -3.7544 | -3.5118 | -5.8371 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.20601 | -0.14792 | -0.27862 | -0.16081 | -119.5026 | 1.5659 | 1.5383 | 1.6991 | -119.4587 | -119.2161 | 5.3977 | -115.6336 | 5.7048 | 5.6291 | 0.23142 | -115.4983 | -115.8523 | 1.878 | 1.9219 | 2.1645 | 1.5661 | -121.5414 | 5.747 | 5.8823 | 5.5283 | 5.6629 | -115.983
2927.3125 | 121.4905 | -5.9967 | 115.3976 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.0015258 | -0.012493 | 0.01702 | 0.00030522 | -0.0033713 | 0.0040594 | 0.016754 | 0.038346 | 0.0063733 | -4.266 | -4.275 | -4.3074 | -3.9585 | -3.91 | -3.6537 | -6.153 | 0.037677 | -0.008798 | -0.042615 | 0.070773 | 0.21059 | -0.14792 | -0.26488 | -0.15632 | -119.3562 | 1.7307 | 1.6893 | 1.8456 | -119.3077 | -119.0513 | 5.7318 | -115.3269 | 6.0344 | 5.9541 | 0.22227 | -115.1871 | -115.5456 | 2.0382 | 2.0867 | 2.343 | 1.7217 | -121.5507 | 6.0675 | 6.2073 | 5.8488 | 5.9879 | -115.6625
2929.0625 | 121.4951 | -5.9326 | 115.4755 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.001953 | -0.012493 | 0.01702 | 0.00030522 | -0.0033713 | 0.0042732 | 0.017182 | 0.03856 | 0.0061595 | -4.0417 | -4.0461 | -4.0831 | -3.7434 | -3.6948 | -3.4477 | -5.9241 | 0.02852 | -0.008798 | -0.042615 | 0.061616 | 0.20601 | -0.1525 | -0.26946 | 0.008536 | -119.2188 | 1.8909 | 1.8495 | 1.841 | -119.1703 | -118.9231 | 5.6632 | -115.4138 | 5.9611 | 5.89 | 0.22685 | -115.2695 | -115.628 | 2.1893 | 2.2378 | 2.485 | 1.8865 | -121.3995 | 5.9942 | 6.1386 | 5.7801 | 5.9238 | -115.7449
2930.75 | 121.4355 | -5.5344 | 115.947 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.0017394 | -0.012707 | 0.016593 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016541 | 0.03856 | 0.0057323 | -3.6937 | -3.7027 | -3.7351 | -3.4091 | -3.3652 | -3.1226 | -5.5532 | 0.019362 | -0.013377 | -0.042615 | 0.066194 | 0.21974 | -0.1525 | -0.27404 | -0.018825 | -119.3561 | 1.8407 | 1.7992 | 1.8181 | -119.3121 | -119.0695 | 5.2603 | -115.8808 | 5.5537 | 5.4917 | 0.23142 | -115.7272 | -116.0995 | 2.1252 | 2.1692 | 2.4118 | 1.8317 | -121.5001 | 5.6006 | 5.7541 | 5.3819 | 5.521 | -116.221
2932.5 | 121.4127 | -5.3192 | 116.185 | 1.4211e-13 | -0.018089 | -0.00014316 | 0.0015258 | -0.012493 | 0.016807 | 0.015566 | -0.0035849 | 0.0042732 | 0.016968 | 0.038346 | 0.0063733 | -3.5014 | -3.4966 | -3.5337 | -3.2123 | -3.1683 | -2.9211 | -5.3242 | 0.023941 | -0.008798 | -0.042615 | 0.070773 | 0.21059 | -0.14792 | -0.27404 | -0.005028 | -119.3973 | 1.8178 | 1.7855 | 1.7906 | -119.3533 | -119.1061 | 5.0452 | -116.1142 | 5.3432 | 5.2766 | 0.23142 | -115.9744 | -116.3329 | 2.107 | 2.151 | 2.3981 | 1.8226 | -121.5092 | 5.39 | 5.5298 | 5.1713 | 5.3104 | -116.459
2934.2656 | 121.4905 | -4.9576 | 116.4642 | 1.4211e-13 | -0.018089 | -0.00014316 | 0.0017394 | -0.012493 | 0.016593 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016968 | 0.03856 | 0.0059459 | -3.2633 | -3.2586 | -3.2819 | -2.9742 | -2.9256 | -2.6922 | -5.0495 | 0.02852 | -0.017956 | -0.047194 | 0.066194 | 0.21516 | -0.15708 | -0.26946 | -0.091925 | -119.4384 | 1.6942 | 1.6757 | 1.7676 | -119.3898 | -119.1564 | 4.6881 | -116.398 | 4.9861 | 4.9104 | 0.22227 | -116.2491 | -116.6213 | 1.9834 | 2.032 | 2.2654 | 1.699 | -121.5137 | 5.0238 | 5.1727 | 4.8005 | 4.9396 | -116.7337
2935.9688 | 121.4951 | -4.8981 | 116.597 | 1.4211e-13 | -0.017876 | -0.00035676 | 0.0017394 | -0.012707 | 0.016807 | -0.0073253 | -0.0031575 | 0.0040594 | 0.016754 | 0.03856 | 0.0059459 | -3.0985 | -3.1212 | -3.1491 | -2.8506 | -2.8019 | -2.5594 | -4.903 | 0.019362 | -0.013377 | -0.038036 | 0.061616 | 0.21516 | -0.1525 | -0.27862 | -0.00491 | -119.4476 | 1.7995 | 1.749 | 1.7539 | -119.3989 | -119.1564 | 4.6195 | -116.5354 | 4.9174 | 4.86 | 0.24058 | -116.3818 | -116.7495 | 2.0475 | 2.0961 | 2.3387 | 1.7769 | -121.5 | 4.9597 | 5.1132 | 4.7456 | 4.8847 | -116.8756
2937.6719 | 121.4676 | -4.7562 | 116.748 | 1.4211e-13 | -0.018089 | -0.00014316 | 0.001953 | -0.012707 | 0.016593 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016754 | 0.03856 | 0.0061595 | -3.1306 | -3.0342 | -3.0621 | -2.7544 | -2.7149 | -2.4587 | -4.7839 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.21059 | -0.15708 | -0.26946 | -0.027763 | -119.5025 | 1.6256 | 1.694 | 1.7218 | -119.463 | -119.2067 | 4.4867 | -116.6773 | 4.7847 | 4.709 | 0.22227 | -116.5375 | -116.9051 | 2.0017 | 2.0412 | 2.2975 | 1.722 | -121.532 | 4.8269 | 4.9668 | 4.5991 | 4.7428 | -117.0175
2939.4375 | 121.5637 | -4.6005 | 116.8671 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.0017394 | -0.013989 | 0.019157 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017182 | 0.03856 | 0.0061595 | -4.3713 | -4.4627 | -4.4951 | -4.1417 | -4.1024 | -3.8506 | -4.6237 | 0.023941 | -0.013377 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.26488 | -0.023141 | -121.0087 | 0.22921 | 0.1054 | 0.12854 | -120.9694 | -120.7176 | 4.3356 | -116.7963 | 4.6245 | 4.5625 | 0.22685 | -116.6565 | -117.0196 | 0.45885 | 0.49817 | 0.74995 | 0.13779 | -121.4907 | 4.6713 | 4.8111 | 4.448 | 4.5871 | -117.1319
2941.1406 | 121.4447 | -4.4998 | 117.041 | 1.4211e-13 | -0.018303 | 7.0442e-05 | 0.0015258 | -0.013775 | 0.019584 | 0.015566 | -0.0035849 | 0.0040594 | 0.016754 | 0.03856 | 0.0061595 | -4.0371 | -4.3712 | -4.4127 | -4.0593 | -4.0016 | -3.759 | -4.5138 | 0.023941 | -0.017956 | -0.047194 | 0.057037 | 0.21516 | -0.14792 | -0.27404 | -0.013955 | -121.1003 | 0.46273 | 0.087102 | 0.10106 | -121.0426 | -120.8 | 4.2258 | -116.984 | 4.5238 | 4.4526 | 0.22685 | -116.8259 | -117.1889 | 0.44055 | 0.4982 | 0.74081 | 0.12866 | -121.5548 | 4.5569 | 4.715 | 4.3519 | 4.4819 | -117.3151
2942.8906 | 121.5408 | -4.1519 | 117.3294 | 1.4211e-13 | -0.018303 | -0.00057056 | 0.0015258 | -0.013989 | 0.020012 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016754 | 0.03856 | 0.0061595 | -3.7899 | -4.1056 | -4.1426 | -3.8029 | -3.7544 | -3.5118 | -4.2528 | 0.023941 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.15708 | -0.27862 | -0.10086 | -121.1323 | 0.36206 | 0.00932 | 0.11018 | -121.0838 | -120.8412 | 3.8733 | -117.2586 | 4.1759 | 4.1093 | 0.236 | -117.1188 | -117.4865 | 0.34904 | 0.39756 | 0.64016 | 0.046317 | -121.5822 | 4.2227 | 4.3625 | 3.9948 | 4.1385 | -117.608
2944.5781 | 121.4539 | -4.8981 | 116.6382 | 1.4211e-13 | -0.018089 | 7.0442e-05 | 0.0015258 | -0.014202 | 0.020653 | -0.0073253 | -0.0035849 | 0.0044868 | 0.016754 | 0.03856 | 0.0059459 | -4.5361 | -4.742 | -4.7744 | -4.4164 | -4.3725 | -4.1207 | -4.8755 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.21516 | -0.15708 | -0.27862 | 0.022564 | -121.0546 | 0.36194 | 0.12367 | 0.10111 | -121.0107 | -120.7589 | 4.6195 | -116.572 | 4.922 | 4.8509 | 0.23142 | -116.423 | -116.7953 | 0.48169 | 0.52556 | 0.77736 | 0.15604 | -121.5137 | 4.9643 | 5.1132 | 4.741 | 4.8847 | -116.9168
2946.3281 | 121.463 | -3.7765 | 117.8009 | 1.4211e-13 | -0.017876 | 0.00028424 | 0.0015258 | -0.013989 | 0.020012 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016754 | 0.03856 | 0.0059459 | -3.6983 | -3.9453 | -3.9824 | -3.6518 | -3.6124 | -3.3698 | -4.0971 | 0.02852 | -0.022535 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.27404 | -0.32054 | -121.4527 | 0.07826 | -0.20581 | 0.11473 | -121.4133 | -121.1707 | 3.5025 | -117.7347 | 3.8051 | 3.7339 | 0.23142 | -117.5903 | -117.9534 | 0.12476 | 0.16414 | 0.40673 | -0.1688 | -121.898 | 3.8427 | 3.9871 | 3.624 | 3.754 | -118.0749
2948.0156 | 121.5088 | -2.9022 | 118.6707 | 1.4211e-13 | -0.017876 | -0.00035676 | 0.0010984 | -0.013775 | 0.018089 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016968 | 0.03856 | 0.0061595 | -2.7139 | -2.7824 | -2.8195 | -2.5255 | -2.4814 | -2.2298 | -2.9432 | 0.023941 | -0.008798 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.27404 | -0.040979 | -121.1962 | 0.18829 | 0.082748 | 0.12373 | -121.1521 | -120.9004 | 2.6282 | -118.6045 | 2.9262 | 2.8596 | 0.23142 | -118.4601 | -118.8232 | 0.37672 | 0.4208 | 0.67247 | 0.11984 | -121.6139 | 2.9684 | 3.1128 | 2.7497 | 2.8934 | -118.9447
2949.7812 | 121.5958 | -2.4445 | 119.0826 | 1.4211e-13 | -0.018303 | 0.00049784 | 0.0017394 | -0.013989 | 0.017448 | 0.00030522 | -0.0031575 | 0.0047004 | 0.016754 | 0.03856 | 0.0059459 | -2.2561 | -2.3108 | -2.3433 | -2.0677 | -2.0235 | -1.781 | -2.4853 | 0.033099 | -0.008798 | -0.042615 | 0.066194 | 0.21516 | -0.14792 | -0.26946 | -0.04085 | -121.1503 | 0.18836 | 0.10113 | 0.14198 | -121.1062 | -120.8637 | 2.175 | -119.0164 | 2.4776 | 2.4018 | 0.22685 | -118.8675 | -119.2306 | 0.37679 | 0.42093 | 0.66341 | 0.13367 | -121.568 | 2.5107 | 2.6596 | 2.2965 | 2.4357 | -119.3521
2951.5312 | 121.4859 | -2.3758 | 119.2383 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.001312 | -0.013989 | 0.017875 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016754 | 0.038346 | 0.0061595 | -2.192 | -2.2513 | -2.2792 | -1.999 | -1.9548 | -1.7078 | -2.412 | 0.023941 | -0.008798 | -0.042615 | 0.066194 | 0.21059 | -0.14792 | -0.26946 | -0.036253 | -121.2373 | 0.18379 | 0.096556 | 0.13281 | -121.1931 | -120.9461 | 2.1063 | -119.1721 | 2.3997 | 2.3332 | 0.22685 | -119.0277 | -119.3862 | 0.3768 | 0.42095 | 0.668 | 0.12453 | -121.6503 | 2.442 | 2.5864 | 2.2279 | 2.367 | -119.5077
2953.2812 | 121.5408 | -2.2751 | 119.3161 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.001312 | -0.013989 | 0.017661 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016541 | 0.038346 | 0.0063733 | -2.0913 | -2.1505 | -2.1785 | -1.9028 | -1.8587 | -1.6116 | -2.3159 | 0.033099 | -0.017956 | -0.028879 | 0.061616 | 0.20601 | -0.1525 | -0.26946 | -0.040803 | -121.2189 | 0.18381 | 0.096571 | 0.13737 | -121.1748 | -120.9277 | 2.0056 | -119.2545 | 2.3082 | 2.2462 | 0.24058 | -119.1101 | -119.4686 | 0.37224 | 0.4164 | 0.66345 | 0.12455 | -121.632 | 2.3367 | 2.4811 | 2.1226 | 2.2571 | -119.5856
2954.9844 | 121.5683 | -2.2842 | 119.2932 | 1.4211e-13 | -0.018303 | 7.0442e-05 | 0.001312 | -0.013561 | 0.017661 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016754 | 0.03856 | 0.0061595 | -2.0775 | -2.1276 | -2.1648 | -1.88 | -1.8404 | -1.5979 | -2.3022 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.27404 | -0.01791 | -121.1732 | 0.2067 | 0.11946 | 0.13737 | -121.1336 | -120.8911 | 2.0102 | -119.227 | 2.3128 | 2.237 | 0.22685 | -119.0826 | -119.4457 | 0.40429 | 0.44387 | 0.68634 | 0.1566 | -121.5954 | 2.3504 | 2.4948 | 2.1317 | 2.2709 | -119.5673
2956.6719 | 121.6324 | -2.1744 | 119.3481 | 1.4211e-13 | -0.017876 | 7.0442e-05 | 0.0015258 | -0.014202 | 0.017661 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016754 | 0.038773 | 0.0061595 | -2.0089 | -2.059 | -2.1007 | -1.8113 | -1.7763 | -1.5292 | -2.2289 | 0.033099 | -0.013377 | -0.047194 | 0.061616 | 0.21059 | -0.14334 | -0.26488 | -0.054512 | -121.1594 | 0.16551 | 0.073693 | 0.1282 | -121.1244 | -120.8774 | 1.9095 | -119.2865 | 2.2075 | 2.1272 | 0.21769 | -119.1376 | -119.4915 | 0.3631 | 0.39811 | 0.64515 | 0.11541 | -121.577 | 2.236 | 2.385 | 2.031 | 2.161 | -119.613
2958.4219 | 121.5591 | -2.1561 | 119.458 | 1.4211e-13 | -0.018089 | 7.0442e-05 | 0.0015258 | -0.013989 | 0.017661 | 0.00030522 | -0.0029439 | 0.0047004 | 0.016754 | 0.03856 | 0.0059459 | -1.9402 | -2.004 | -2.0183 | -1.7472 | -1.7122 | -1.456 | -2.1648 | 0.023941 | -0.008798 | -0.051772 | 0.066194 | 0.21059 | -0.1525 | -0.27862 | -0.008717 | -121.2052 | 0.21588 | 0.13779 | 0.14651 | -121.1702 | -120.914 | 1.8774 | -119.3918 | 2.18 | 2.1043 | 0.22685 | -119.2474 | -119.6105 | 0.40889 | 0.44391 | 0.7001 | 0.15205 | -121.6228 | 2.2223 | 2.3667 | 2.0036 | 2.1473 | -119.7366
2960.1875 | 121.6553 | -2.1652 | 119.4077 | 1.4211e-13 | -0.018089 | 7.0442e-05 | 0.0015258 | -0.013348 | 0.018302 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.03856 | 0.0065869 | -2.0226 | -2.0452 | -2.0732 | -1.8021 | -1.7579 | -1.5109 | -2.2106 | 0.02852 | -0.017956 | -0.038036 | 0.061616 | 0.20143 | -0.1525 | -0.27404 | -0.045351 | -121.2098 | 0.14262 | 0.092008 | 0.13736 | -121.1656 | -120.9186 | 1.8912 | -119.346 | 2.1937 | 2.1272 | 0.236 | -119.2062 | -119.5602 | 0.3631 | 0.40727 | 0.65431 | 0.11999 | -121.6182 | 2.2268 | 2.3667 | 2.0127 | 2.1473 | -119.6817
2961.9375 | 121.5179 | -2.2064 | 119.4031 | 1.4211e-13 | -0.017876 | 7.0442e-05 | 0.001312 | -0.013989 | 0.018089 | 0.00030522 | -0.0031575 | 0.0047004 | 0.017182 | 0.03856 | 0.0061595 | -2.0363 | -2.0727 | -2.0915 | -1.825 | -1.7808 | -1.5292 | -2.2426 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.21516 | -0.1525 | -0.27862 | -0.036204 | -121.2281 | 0.17009 | 0.11489 | 0.1511 | -121.1839 | -120.9323 | 1.9278 | -119.3369 | 2.2349 | 2.1592 | 0.23142 | -119.1879 | -119.5556 | 0.38141 | 0.42558 | 0.6772 | 0.13372 | -121.6457 | 2.2726 | 2.4216 | 2.0539 | 2.193 | -119.6817
2963.6875 | 121.5958 | -2.0828 | 119.4946 | 1.4211e-13 | -0.018303 | 7.0442e-05 | 0.0017394 | -0.013989 | 0.017875 | 0.00030522 | -0.0033713 | 0.0049142 | 0.017182 | 0.038773 | 0.0059459 | -1.931 | -1.9582 | -1.9908 | -1.7289 | -1.6801 | -1.4285 | -2.1465 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.27862 | -0.063643 | -121.2235 | 0.15179 | 0.09202 | 0.15566 | -121.1747 | -120.9231 | 1.8042 | -119.4284 | 2.1113 | 2.0356 | 0.23142 | -119.284 | -119.6471 | 0.35396 | 0.40272 | 0.65433 | 0.12459 | -121.6411 | 2.149 | 2.2934 | 1.9303 | 2.0694 | -119.7732
2965.3906 | 121.55 | -2.0599 | 119.5724 | 1.4211e-13 | -0.018303 | 7.0442e-05 | 0.0015258 | -0.013775 | 0.018089 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016754 | 0.03856 | 0.0059459 | -1.8898 | -1.917 | -1.945 | -1.6739 | -1.6297 | -1.3827 | -2.1007 | 0.023941 | -0.017956 | -0.047194 | 0.070773 | 0.21516 | -0.14792 | -0.27404 | -0.040742 | -121.2464 | 0.17011 | 0.11492 | 0.15566 | -121.2022 | -120.9552 | 1.7859 | -119.5017 | 2.0839 | 2.0127 | 0.22685 | -119.3573 | -119.7204 | 0.38601 | 0.4302 | 0.67723 | 0.14291 | -121.6731 | 2.1307 | 2.2751 | 1.912 | 2.042 | -119.8465
2967.1562 | 121.5775 | -2.005 | 119.632 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.001953 | -0.013989 | 0.018302 | 0.0079357 | -0.0037985 | 0.0044868 | 0.016968 | 0.038346 | 0.0061595 | -1.8303 | -1.8575 | -1.8763 | -1.6098 | -1.5702 | -1.3186 | -2.0274 | 0.023941 | -0.013377 | -0.051772 | 0.070773 | 0.21059 | -0.1525 | -0.27862 | -0.022411 | -121.2418 | 0.1747 | 0.12866 | 0.15107 | -121.2022 | -120.9506 | 1.7264 | -119.5612 | 2.0289 | 1.9532 | 0.22685 | -119.4214 | -119.7845 | 0.39518 | 0.43479 | 0.6864 | 0.1475 | -121.6594 | 2.0758 | 2.2156 | 1.8525 | 1.9916 | -119.9106
2968.8438 | 121.6095 | -1.8814 | 119.751 | 1.4211e-13 | -0.018517 | -0.00035676 | 0.0017394 | -0.013989 | 0.017661 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.03856 | 0.0061595 | -1.7342 | -1.7614 | -1.7939 | -1.5183 | -1.4786 | -1.2316 | -1.9404 | 0.02852 | -0.013377 | -0.038036 | 0.070773 | 0.21516 | -0.15708 | -0.27404 | -0.059007 | -121.2692 | 0.14725 | 0.08747 | 0.14648 | -121.2296 | -120.9826 | 1.6074 | -119.6802 | 1.9099 | 1.8434 | 0.236 | -119.5358 | -119.9081 | 0.36315 | 0.40278 | 0.64979 | 0.12005 | -121.6914 | 1.9522 | 2.0966 | 1.7243 | 1.868 | -120.025
2970.5938 | 121.6003 | -1.8631 | 119.7876 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.0017394 | -0.013561 | 0.017875 | -0.014956 | -0.0031575 | 0.0044868 | 0.016754 | 0.038773 | 0.0061595 | -1.7067 | -1.7293 | -1.7619 | -1.4908 | -1.4557 | -1.2133 | -1.9084 | 0.02852 | -0.017956 | -0.038036 | 0.061616 | 0.21059 | -0.1525 | -0.27404 | -0.045266 | -121.2784 | 0.15641 | 0.10121 | 0.14647 | -121.2433 | -121.0009 | 1.5891 | -119.726 | 1.8916 | 1.8251 | 0.236 | -119.577 | -119.9401 | 0.37231 | 0.40736 | 0.6498 | 0.13379 | -121.696 | 1.9247 | 2.0737 | 1.7106 | 1.8451 | -120.0616
2972.3438 | 121.6003 | -1.7853 | 119.8608 | 1.4211e-13 | -0.018517 | -0.00014316 | 0.0017394 | -0.013775 | 0.017875 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016754 | 0.03856 | 0.0063733 | -1.6014 | -1.624 | -1.6566 | -1.3992 | -1.3458 | -1.108 | -1.7985 | 0.02852 | -0.013377 | -0.051772 | 0.061616 | 0.21059 | -0.14792 | -0.27862 | -0.013192 | -121.2601 | 0.18389 | 0.12869 | 0.14188 | -121.2067 | -120.9688 | 1.5067 | -119.7992 | 1.8138 | 1.7335 | 0.22685 | -119.6503 | -120.0088 | 0.38606 | 0.43943 | 0.67728 | 0.16128 | -121.6593 | 1.8469 | 1.9959 | 1.6374 | 1.7719 | -120.1395
2974.0938 | 121.6049 | -1.6571 | 119.989 | 1.4211e-13 | -0.018303 | 7.0442e-05 | 0.0015258 | -0.013775 | 0.01702 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.03856 | 0.0061595 | -1.5419 | -1.5645 | -1.5925 | -1.326 | -1.2909 | -1.0439 | -1.7435 | 0.033099 | -0.013377 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.26946 | -0.086419 | -121.315 | 0.11523 | 0.06461 | 0.15103 | -121.2799 | -121.0329 | 1.3876 | -119.9228 | 1.6902 | 1.6191 | 0.23143 | -119.7784 | -120.1415 | 0.33114 | 0.36621 | 0.61321 | 0.092628 | -121.7325 | 1.7233 | 1.8677 | 1.5046 | 1.6437 | -120.2585
2975.7812 | 121.6919 | -1.5518 | 120.0485 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.0015258 | -0.013989 | 0.01702 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016754 | 0.03856 | 0.0059459 | -1.3679 | -1.3905 | -1.4139 | -1.1474 | -1.1169 | -0.86991 | -1.5649 | 0.02852 | -0.013377 | -0.038036 | 0.070773 | 0.20143 | -0.1525 | -0.27862 | -0.013126 | -121.1959 | 0.18393 | 0.13788 | 0.151 | -121.1654 | -120.9184 | 1.2732 | -119.9778 | 1.5803 | 1.5138 | 0.24058 | -119.8471 | -120.201 | 0.40441 | 0.43492 | 0.68191 | 0.16133 | -121.6135 | 1.6226 | 1.7532 | 1.3993 | 1.5384 | -120.3271
2977.5469 | 121.6187 | -1.593 | 120.0806 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.0017394 | -0.013561 | 0.016807 | -0.0073253 | -0.0031575 | 0.0042732 | 0.016541 | 0.038987 | 0.0059459 | -1.3587 | -1.3905 | -1.4185 | -1.1611 | -1.1169 | -0.86991 | -1.5649 | 0.02852 | -0.017956 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.27404 | 0.028073 | -121.2417 | 0.23428 | 0.1745 | 0.14643 | -121.1975 | -120.9505 | 1.319 | -120.0098 | 1.6215 | 1.5504 | 0.23142 | -119.87 | -120.2331 | 0.43187 | 0.47612 | 0.72311 | 0.20253 | -121.6455 | 1.6638 | 1.8036 | 1.4405 | 1.5751 | -120.3546
2979.2344 | 121.669 | -1.4923 | 120.163 | 1.4211e-13 | -0.018517 | -0.00035676 | 0.0017394 | -0.013989 | 0.017234 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.038346 | 0.0061595 | -1.345 | -1.3722 | -1.4002 | -1.1428 | -1.0986 | -0.85617 | -1.5466 | 0.02852 | -0.017956 | -0.038036 | 0.070773 | 0.21516 | -0.14792 | -0.27862 | -0.054319 | -121.3058 | 0.14731 | 0.092103 | 0.14642 | -121.2615 | -121.0191 | 1.2137 | -120.0922 | 1.5208 | 1.4543 | 0.24058 | -119.9478 | -120.3109 | 0.34948 | 0.39373 | 0.63614 | 0.12014 | -121.7096 | 1.5631 | 1.7075 | 1.3444 | 1.4744 | -120.4416
2980.9219 | 121.6919 | -0.20599 | 121.431 | 1.4211e-13 | -0.018517 | -0.00014316 | 0.001953 | -0.013989 | 0.014029 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016541 | 0.03856 | 0.0059459 | -0.085942 | -0.11306 | -0.13202 | 0.056706 | -0.027115 | 0.32053 | -0.27369 | 0.033099 | -0.008798 | -0.042615 | 0.066194 | 0.20601 | -0.14334 | -0.27404 | -0.067694 | -121.3743 | 0.12005 | 0.073971 | 0.14166 | -121.4581 | -121.1104 | -0.068046 | -121.3648 | 0.23909 | 0.16338 | 0.23142 | -121.225 | -121.5743 | 0.2627 | 0.17888 | 0.52653 | 0.092935 | -121.7047 | 0.27219 | 0.412 | 0.062651 | 0.1972 | -121.705
2982.6875 | 121.701 | -0.21515 | 121.4218 | 1.4211e-13 | -0.018303 | 7.0442e-05 | 0.0017394 | -0.013989 | 0.014029 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.038773 | 0.0057323 | -0.085942 | -0.10848 | -0.13202 | 0.07502 | 0.009517 | 0.32511 | -0.27369 | 0.02852 | -0.013377 | -0.038036 | 0.061616 | 0.21516 | -0.1525 | -0.27862 | -0.058539 | -121.3468 | 0.12921 | 0.083126 | 0.14166 | -121.4123 | -121.0967 | -0.06347 | -121.3602 | 0.24367 | 0.17711 | 0.24058 | -121.2066 | -121.5743 | 0.29017 | 0.22467 | 0.54026 | 0.10667 | -121.6955 | 0.27676 | 0.43031 | 0.062649 | 0.20177 | -121.7004
2984.3906 | 121.3577 | -0.22888 | 121.4951 | 1.4211e-13 | -0.01873 | 7.0442e-05 | 0.001953 | -0.013775 | 0.014243 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016754 | 0.038773 | 0.0059459 | -0.09052 | -0.1039 | -0.12287 | 0.056706 | -0.017957 | 0.31595 | -0.27827 | 0.033099 | -0.013377 | -0.042615 | 0.066194 | 0.21059 | -0.14792 | -0.27404 | -0.049385 | -121.4383 | 0.13836 | 0.10602 | 0.1554 | -121.513 | -121.1791 | -0.045158 | -121.4289 | 0.26198 | 0.18627 | 0.23142 | -121.2845 | -121.643 | 0.28559 | 0.21093 | 0.54483 | 0.12498 | -121.7733 | 0.29508 | 0.43947 | 0.08096 | 0.21551 | -121.7691
2986.1562 | 121.6415 | -0.23804 | 121.4676 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.0017394 | -0.013775 | 0.014456 | -0.0073253 | -0.0033713 | 0.0047004 | 0.017182 | 0.03856 | 0.0059459 | -0.09052 | -0.11764 | -0.1366 | 0.056706 | -0.008799 | 0.31137 | -0.31032 | 0.023941 | -0.008798 | -0.047194 | 0.070773 | 0.20601 | -0.14334 | -0.27862 | -0.072282 | -121.4109 | 0.14752 | 0.10144 | 0.17372 | -121.4764 | -121.1562 | -0.040582 | -121.3968 | 0.26198 | 0.19084 | 0.23142 | -121.2616 | -121.6109 | 0.29474 | 0.22924 | 0.54941 | 0.1204 | -121.7779 | 0.30881 | 0.44405 | 0.094694 | 0.22924 | -121.7462
2987.8594 | 121.7331 | -0.23346 | 121.463 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.0017394 | -0.013989 | 0.014243 | 0.00030522 | -0.0037985 | 0.0044868 | 0.016754 | 0.038987 | 0.0059459 | -0.081363 | -0.1039 | -0.12287 | 0.065863 | -0.008799 | 0.32511 | -0.29658 | 0.019362 | -0.013377 | -0.051772 | 0.061616 | 0.20143 | -0.1525 | -0.27404 | -0.063123 | -121.3972 | 0.1521 | 0.11059 | 0.17372 | -121.4718 | -121.1379 | -0.040581 | -121.4014 | 0.25282 | 0.18169 | 0.22227 | -121.2616 | -121.6155 | 0.29932 | 0.22466 | 0.55857 | 0.12956 | -121.7596 | 0.29507 | 0.43489 | 0.080959 | 0.22008 | -121.7371
2989.625 | 115.4709 | -45.1813 | 70.1202 | 1.4211e-13 | -0.017021 | 0.0011388 | -0.0021068 | -0.008647 | 0.1356 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016968 | 0.03856 | 0.0061595 | -42.9259 | -42.9505 | -42.8428 | -8.1066 | -8.0311 | -8.1774 | -48.563 | 0.042256 | 0.000359 | -0.015143 | 0.084508 | 0.2289 | -0.1525 | -0.25572 | -3.3818 | -78.2268 | 2.2554 | 2.3385 | 5.7202 | -78.1513 | -78.2976 | 44.9255 | -70.0357 | 45.2235 | 45.1661 | 0.24058 | -69.8913 | -70.2727 | 37.0747 | 37.1502 | 37.0039 | 2.2308 | -118.6833 | 45.2658 | 45.4102 | 45.0288 | 45.1816 | -70.376
2991.375 | 120.575 | -0.18768 | 120.5017 | 1.4211e-13 | -0.018517 | -0.00057056 | 0.001953 | -0.014202 | 0.014243 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016541 | 0.038773 | 0.0057323 | -0.021844 | -0.048958 | -0.08624 | 0.1208 | 0.1011 | 0.38005 | -0.22332 | 0.02852 | -0.017956 | -0.042615 | 0.066194 | 0.21516 | -0.14792 | -0.27404 | -0.035637 | -120.3809 | 0.16584 | 0.10144 | 0.13708 | -120.4006 | -120.1217 | -0.086357 | -120.4355 | 0.2162 | 0.14507 | 0.23142 | -120.2865 | -120.6496 | 0.30849 | 0.28878 | 0.56774 | 0.13872 | -120.725 | 0.25388 | 0.40285 | 0.039761 | 0.16973 | -120.7757
2993.0781 | 120.845 | -0.16022 | 120.6528 | 1.4211e-13 | -0.018517 | -0.00014316 | 0.0015258 | -0.013775 | 0.013602 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016754 | 0.038773 | 0.0059459 | -0.021844 | -0.044379 | -0.063349 | 0.12996 | 0.1011 | 0.38921 | -0.25537 | 0.023941 | -0.008798 | -0.042615 | 0.061616 | 0.21059 | -0.1525 | -0.27404 | -0.095155 | -120.5228 | 0.13837 | 0.096868 | 0.19202 | -120.5517 | -120.2636 | -0.11382 | -120.5912 | 0.18416 | 0.1176 | 0.23142 | -120.4422 | -120.8053 | 0.29018 | 0.26131 | 0.54943 | 0.11584 | -120.9081 | 0.22183 | 0.3708 | 0.007717 | 0.15142 | -120.9268
2994.7812 | 120.8038 | -0.76446 | 120.1904 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.0017394 | -0.013561 | 0.015097 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016754 | 0.038987 | 0.0057323 | -0.45679 | -0.58466 | -0.49828 | -0.27294 | -0.19196 | -0.022864 | -0.76821 | 0.023941 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.26946 | -0.003747 | -120.4634 | 0.30767 | 0.26618 | 0.26993 | -120.3824 | -120.2133 | 0.495 | -120.1197 | 0.78841 | 0.72185 | 0.22685 | -119.9798 | -120.3429 | 0.49153 | 0.57251 | 0.7416 | 0.17981 | -120.9586 | 0.83524 | 0.97505 | 0.61196 | 0.75109 | -120.4599
2996.5312 | 120.9869 | -0.6134 | 120.2911 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.001953 | -0.013775 | 0.01467 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016754 | 0.03856 | 0.0059459 | -0.34691 | -0.47935 | -0.39756 | -0.17221 | -0.040851 | 0.03208 | -0.67663 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.14792 | -0.26488 | -0.06323 | -120.4634 | 0.26649 | 0.21584 | 0.27907 | -120.332 | -120.2591 | 0.34852 | -120.2249 | 0.64192 | 0.56621 | 0.21769 | -120.0806 | -120.4391 | 0.44119 | 0.57255 | 0.64548 | 0.13406 | -120.9678 | 0.6796 | 0.82399 | 0.46548 | 0.60003 | -120.556
2998.2344 | 120.9274 | -0.65002 | 120.4056 | 1.4211e-13 | -0.018517 | -0.00057056 | 0.0015258 | -0.013775 | 0.014884 | 0.00030522 | -0.0033713 | 0.0044868 | 0.017182 | 0.03856 | 0.0059459 | -0.38354 | -0.4244 | -0.42503 | -0.20426 | -0.068325 | -0.027442 | -0.62626 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.26946 | 0.023759 | -120.6098 | 0.26649 | 0.22499 | 0.20123 | -120.4739 | -120.433 | 0.38056 | -120.3394 | 0.67854 | 0.60283 | 0.22227 | -120.195 | -120.5581 | 0.44576 | 0.5817 | 0.62258 | 0.22562 | -121.0318 | 0.71622 | 0.86061 | 0.49752 | 0.63665 | -120.675
2999.9844 | 121.1014 | -0.56305 | 120.4651 | 1.4211e-13 | -0.018517 | -0.00057056 | 0.0017394 | -0.013561 | 0.014884 | 0.015566 | -0.0031575 | 0.0040594 | 0.016541 | 0.03856 | 0.0059459 | -0.36064 | -0.39693 | -0.40672 | -0.18595 | -0.031693 | -0.004549 | -0.61253 | 0.02852 | -0.008798 | -0.047194 | 0.061616 | 0.20601 | -0.15708 | -0.27862 | -0.049479 | -120.651 | 0.2024 | 0.15633 | 0.20581 | -120.4968 | -120.4696 | 0.28443 | -120.4035 | 0.59157 | 0.51586 | 0.23142 | -120.2591 | -120.6222 | 0.3771 | 0.53136 | 0.5585 | 0.16612 | -121.0776 | 0.62467 | 0.76906 | 0.40597 | 0.55425 | -120.7437
3001.6875 | 121.0327 | -0.54932 | 120.5566 | 1.4211e-13 | -0.018517 | 7.0442e-05 | 0.001953 | -0.013989 | 0.01467 | 0.023196 | -0.0031575 | 0.0044868 | 0.017182 | 0.038773 | 0.0059459 | -0.37896 | -0.39693 | -0.42961 | -0.19968 | -0.054588 | -0.004549 | -0.5759 | 0.033099 | -0.013377 | -0.051772 | 0.075351 | 0.21059 | -0.15708 | -0.27404 | -0.026581 | -120.7563 | 0.17036 | 0.11971 | 0.14629 | -120.6112 | -120.5612 | 0.27528 | -120.4813 | 0.58242 | 0.49754 | 0.22227 | -120.3461 | -120.7137 | 0.34963 | 0.49473 | 0.54477 | 0.15238 | -121.1325 | 0.62467 | 0.7599 | 0.39224 | 0.53594 | -120.8307
3003.4375 | 121.1609 | -0.45776 | 120.6482 | 1.4211e-13 | -0.018517 | -0.00014316 | 0.0017394 | -0.013989 | 0.014243 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017182 | 0.038773 | 0.0061595 | -0.3057 | -0.32825 | -0.35178 | -0.13559 | -0.022536 | 0.10534 | -0.48432 | 0.02852 | -0.013377 | -0.051772 | 0.066194 | 0.21059 | -0.14334 | -0.27862 | -0.026554 | -120.7838 | 0.15206 | 0.10598 | 0.13254 | -120.6707 | -120.5429 | 0.17914 | -120.582 | 0.48628 | 0.40599 | 0.22685 | -120.4376 | -120.7915 | 0.32218 | 0.43523 | 0.5631 | 0.12951 | -121.1325 | 0.52396 | 0.66835 | 0.31442 | 0.44439 | -120.9268
3005.125 | 121.1609 | -0.42114 | 120.6802 | 1.4211e-13 | -0.018089 | 7.0442e-05 | 0.0017394 | -0.013989 | 0.015097 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016541 | 0.038132 | 0.0059459 | -0.27823 | -0.30994 | -0.32431 | -0.10812 | -0.036272 | 0.11907 | -0.46142 | 0.02852 | -0.017956 | -0.047194 | 0.066194 | 0.20601 | -0.14792 | -0.2832 | -0.040281 | -120.7884 | 0.14291 | 0.096832 | 0.13711 | -120.7165 | -120.5612 | 0.13794 | -120.614 | 0.44966 | 0.37395 | 0.236 | -120.4742 | -120.8282 | 0.31303 | 0.38487 | 0.54022 | 0.1112 | -121.1417 | 0.48734 | 0.62715 | 0.27322 | 0.40319 | -120.9634
3006.8906 | 121.2158 | -0.4303 | 120.7031 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.0017394 | -0.013775 | 0.015097 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016754 | 0.038773 | 0.0059459 | -0.26908 | -0.30078 | -0.32431 | -0.11269 | -0.031693 | 0.11907 | -0.47058 | 0.019362 | -0.017956 | -0.038036 | 0.066194 | 0.20601 | -0.14792 | -0.27862 | -0.040284 | -120.8158 | 0.16122 | 0.10599 | 0.14627 | -120.7348 | -120.5841 | 0.15168 | -120.6369 | 0.44966 | 0.39226 | 0.24058 | -120.4971 | -120.851 | 0.3176 | 0.3986 | 0.54937 | 0.12952 | -121.1737 | 0.49649 | 0.63631 | 0.28238 | 0.41234 | -120.9817
3008.6406 | 121.1243 | -0.48981 | 120.7352 | 1.4211e-13 | -0.018517 | 7.0442e-05 | 0.0017394 | -0.013561 | 0.014456 | 0.0079357 | -0.0037985 | 0.0044868 | 0.016968 | 0.038773 | 0.0061595 | -0.28281 | -0.30536 | -0.32431 | -0.11727 | -0.036272 | 0.12365 | -0.47058 | 0.019362 | -0.013377 | -0.042615 | 0.070773 | 0.20601 | -0.14792 | -0.26946 | 0.019225 | -120.8524 | 0.20699 | 0.1655 | 0.14627 | -120.7714 | -120.6115 | 0.22035 | -120.6644 | 0.50917 | 0.44719 | 0.22685 | -120.5292 | -120.8831 | 0.37253 | 0.45354 | 0.61346 | 0.18445 | -121.2057 | 0.56058 | 0.69581 | 0.34188 | 0.47643 | -121.0046
3010.3906 | 121.2341 | -0.44861 | 120.7352 | 1.4211e-13 | -0.018944 | 7.0442e-05 | 0.0015258 | -0.013775 | 0.014884 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.03856 | 0.0059459 | -0.3057 | -0.32367 | -0.34262 | -0.13559 | -0.027115 | 0.10076 | -0.49806 | 0.023941 | -0.013377 | -0.042615 | 0.066194 | 0.20143 | -0.15708 | -0.27862 | -0.049447 | -120.8708 | 0.1429 | 0.10598 | 0.15543 | -120.7623 | -120.6344 | 0.16999 | -120.669 | 0.47255 | 0.40599 | 0.236 | -120.5337 | -120.8922 | 0.31302 | 0.42149 | 0.54937 | 0.12493 | -121.2332 | 0.5148 | 0.65004 | 0.29153 | 0.43523 | -121.0138
3012.0938 | 121.2479 | -0.35706 | 120.7901 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.001953 | -0.013561 | 0.014456 | 0.0079357 | -0.0035849 | 0.0047004 | 0.017182 | 0.03856 | 0.0059459 | -0.27823 | -0.30078 | -0.32431 | -0.098959 | -0.036272 | 0.13281 | -0.46142 | 0.023941 | -0.017956 | -0.047194 | 0.066194 | 0.21059 | -0.14792 | -0.2832 | -0.10437 | -120.8891 | 0.078822 | 0.032745 | 0.13711 | -120.8264 | -120.6573 | 0.073858 | -120.7239 | 0.381 | 0.30986 | 0.236 | -120.5795 | -120.938 | 0.2581 | 0.32078 | 0.48986 | 0.056275 | -121.2515 | 0.42325 | 0.56764 | 0.20913 | 0.3391 | -121.0733
3013.8438 | 121.1746 | -0.43945 | 120.8038 | 1.4211e-13 | -0.018303 | -0.00057056 | 0.0017394 | -0.013775 | 0.014884 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.038773 | 0.0059459 | -0.28739 | -0.30078 | -0.32431 | -0.11727 | -0.031693 | 0.12365 | -0.466 | 0.02852 | -0.013377 | -0.038036 | 0.066194 | 0.20601 | -0.15708 | -0.27404 | -0.02655 | -120.9211 | 0.15206 | 0.11514 | 0.14169 | -120.8355 | -120.6802 | 0.16541 | -120.7376 | 0.46797 | 0.40142 | 0.236 | -120.5978 | -120.9609 | 0.32218 | 0.40776 | 0.5631 | 0.13867 | -121.2698 | 0.50565 | 0.64546 | 0.28237 | 0.42608 | -121.0779
3015.5781 | 121.225 | -0.40741 | 120.8771 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.0015258 | -0.013775 | 0.014884 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016541 | 0.03856 | 0.0061595 | -0.24161 | -0.27331 | -0.29684 | -0.089802 | -0.04543 | 0.16028 | -0.43395 | 0.02852 | -0.017956 | -0.047194 | 0.070773 | 0.21059 | -0.14792 | -0.2832 | -0.02654 | -120.9669 | 0.1658 | 0.11057 | 0.13711 | -120.9225 | -120.7168 | 0.12421 | -120.8063 | 0.43593 | 0.36022 | 0.236 | -120.6665 | -121.025 | 0.31761 | 0.36198 | 0.56769 | 0.1341 | -121.311 | 0.47818 | 0.618 | 0.25949 | 0.38945 | -121.1603
3017.2812 | 121.2341 | -0.42572 | 120.8496 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.0017394 | -0.013561 | 0.01467 | 0.0079357 | -0.0033713 | 0.0040594 | 0.016968 | 0.038773 | 0.0061595 | -0.25992 | -0.27789 | -0.31058 | -0.098959 | -0.040851 | 0.14197 | -0.45227 | 0.02852 | -0.013377 | -0.042615 | 0.066194 | 0.21059 | -0.15708 | -0.27404 | -0.026546 | -120.9486 | 0.1658 | 0.11514 | 0.14169 | -120.8905 | -120.7076 | 0.15168 | -120.7834 | 0.45424 | 0.3831 | 0.23142 | -120.639 | -121.0067 | 0.32676 | 0.38487 | 0.56769 | 0.14783 | -121.3019 | 0.49191 | 0.63631 | 0.26864 | 0.41234 | -121.1236
3019.0312 | 121.2936 | -0.42114 | 120.8725 | 1.4211e-13 | -0.018517 | -0.00035676 | 0.0015258 | -0.013561 | 0.01467 | 0.015566 | -0.0031575 | 0.0042732 | 0.016541 | 0.038773 | 0.0059459 | -0.26908 | -0.2962 | -0.31973 | -0.10812 | -0.036272 | 0.13281 | -0.46142 | 0.023941 | -0.008798 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.27404 | -0.040281 | -120.9806 | 0.15207 | 0.10141 | 0.14169 | -120.9088 | -120.7397 | 0.1471 | -120.8017 | 0.44508 | 0.37853 | 0.23142 | -120.6665 | -121.025 | 0.31303 | 0.38487 | 0.55395 | 0.12494 | -121.3339 | 0.49192 | 0.62715 | 0.26864 | 0.41234 | -121.1465
3020.7344 | 121.225 | -0.43945 | 120.8862 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.0017394 | -0.013989 | 0.015097 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016327 | 0.03856 | 0.0059459 | -0.27366 | -0.29162 | -0.31973 | -0.10812 | -0.040851 | 0.13739 | -0.46142 | 0.023941 | -0.013377 | -0.042615 | 0.070773 | 0.21516 | -0.15708 | -0.27404 | -0.021971 | -120.9943 | 0.1658 | 0.11972 | 0.14169 | -120.9271 | -120.7488 | 0.16541 | -120.8155 | 0.46339 | 0.39684 | 0.23142 | -120.6711 | -121.0433 | 0.33134 | 0.3986 | 0.57684 | 0.14783 | -121.3477 | 0.51023 | 0.65462 | 0.28237 | 0.42608 | -121.1603
3022.5 | 121.2845 | -0.54016 | 120.7809 | 1.4211e-13 | -0.018303 | -0.00035676 | 0.001953 | -0.013775 | 0.015311 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016968 | 0.038987 | 0.0059459 | -0.35149 | -0.37404 | -0.38841 | -0.17221 | -0.040851 | 0.036658 | -0.54384 | 0.033099 | -0.008798 | -0.047194 | 0.070773 | 0.20143 | -0.15708 | -0.27404 | -0.003683 | -120.9532 | 0.18867 | 0.15175 | 0.15544 | -120.8218 | -120.7443 | 0.26612 | -120.7102 | 0.57326 | 0.49297 | 0.22685 | -120.5795 | -120.938 | 0.36795 | 0.49931 | 0.57682 | 0.16612 | -121.3248 | 0.61093 | 0.74159 | 0.38308 | 0.53136 | -121.055
3024.2656 | 121.3715 | -0.48523 | 120.8176 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.0017394 | -0.013989 | 0.014884 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016754 | 0.038773 | 0.0057323 | -0.36522 | -0.3832 | -0.40214 | -0.19053 | -0.050009 | -0.004549 | -0.56216 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20601 | -0.1525 | -0.26946 | -0.076931 | -121.0081 | 0.12001 | 0.083087 | 0.16002 | -120.8676 | -120.8221 | 0.21577 | -120.7514 | 0.50917 | 0.43804 | 0.22227 | -120.6116 | -120.9701 | 0.2947 | 0.43522 | 0.48068 | 0.10203 | -121.3797 | 0.55142 | 0.69124 | 0.33273 | 0.47185 | -121.087
3026.0312 | 121.4127 | -0.43488 | 120.8954 | 1.4211e-13 | -0.01873 | 7.0442e-05 | 0.001953 | -0.013775 | 0.015311 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016968 | 0.038773 | 0.0059459 | -0.31028 | -0.32825 | -0.3472 | -0.14474 | -0.022536 | 0.087023 | -0.49348 | 0.033099 | -0.013377 | -0.038036 | 0.061616 | 0.20601 | -0.15708 | -0.2832 | -0.058601 | -121.0401 | 0.12459 | 0.087673 | 0.14627 | -120.9179 | -120.8084 | 0.15168 | -120.8338 | 0.46797 | 0.39684 | 0.24516 | -120.6894 | -121.0525 | 0.29013 | 0.41234 | 0.5219 | 0.10662 | -121.3889 | 0.49649 | 0.64088 | 0.2778 | 0.4215 | -121.1786
3027.7188 | 121.4035 | -0.46692 | 120.8496 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.0015258 | -0.013989 | 0.015097 | -0.0073253 | -0.0035849 | 0.0040594 | 0.016541 | 0.038987 | 0.0059459 | -0.3286 | -0.33741 | -0.37009 | -0.15848 | -0.013378 | 0.077866 | -0.51637 | 0.033099 | -0.00422 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.27862 | -0.049452 | -121.0081 | 0.13832 | 0.096825 | 0.14628 | -120.863 | -120.7717 | 0.1883 | -120.7834 | 0.50002 | 0.4243 | 0.236 | -120.6436 | -121.0021 | 0.30844 | 0.45354 | 0.54478 | 0.12951 | -121.366 | 0.53311 | 0.67293 | 0.31442 | 0.4627 | -121.1282
3029.4688 | 121.3257 | -0.43488 | 120.9732 | 1.4211e-13 | -0.018303 | -0.00014316 | 0.001953 | -0.013775 | 0.01467 | 0.015566 | -0.0035849 | 0.0044868 | 0.016327 | 0.038346 | 0.0059459 | -0.25534 | -0.26873 | -0.306 | -0.089802 | -0.040851 | 0.14197 | -0.44311 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20143 | -0.1525 | -0.27862 | -0.008233 | -121.063 | 0.17953 | 0.12888 | 0.13711 | -121.0141 | -120.8312 | 0.15626 | -120.907 | 0.45882 | 0.38768 | 0.23142 | -120.7718 | -121.1257 | 0.34507 | 0.39402 | 0.57684 | 0.16614 | -121.4163 | 0.50107 | 0.6363 | 0.28238 | 0.4215 | -121.2518
3031.2344 | 121.4539 | -0.37537 | 120.9457 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.001953 | -0.013989 | 0.014884 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016754 | 0.038773 | 0.0059459 | -0.27366 | -0.28247 | -0.31058 | -0.10812 | -0.040851 | 0.14655 | -0.4889 | 0.02852 | -0.017956 | -0.047194 | 0.070773 | 0.21516 | -0.1525 | -0.27404 | -0.11353 | -121.0539 | 0.10171 | 0.06479 | 0.17832 | -120.9866 | -120.7992 | 0.10133 | -120.875 | 0.40389 | 0.32817 | 0.22685 | -120.7306 | -121.0982 | 0.26725 | 0.33452 | 0.52191 | 0.092899 | -121.4346 | 0.44614 | 0.59053 | 0.22287 | 0.35741 | -121.2198
3032.9844 | 121.3486 | -0.43488 | 121.0236 | 1.4211e-13 | -0.018517 | -0.00035676 | 0.0017394 | -0.013775 | 0.01467 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016968 | 0.038987 | 0.0061595 | -0.24161 | -0.255 | -0.28768 | -0.080646 | -0.050009 | 0.16028 | -0.42937 | 0.02852 | -0.013377 | -0.047194 | 0.061616 | 0.21059 | -0.1525 | -0.26946 | 0.005504 | -121.1042 | 0.19327 | 0.14719 | 0.14169 | -121.0736 | -120.8633 | 0.16541 | -120.9619 | 0.4634 | 0.38768 | 0.22227 | -120.813 | -121.1761 | 0.35423 | 0.38487 | 0.59515 | 0.17988 | -121.4529 | 0.49649 | 0.64546 | 0.28238 | 0.4215 | -121.293
3034.75 | 121.344 | -0.37079 | 121.0785 | 1.4211e-13 | -0.018944 | -0.00035676 | 0.0015258 | -0.013989 | 0.014456 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016327 | 0.038773 | 0.0059459 | -0.20498 | -0.22295 | -0.25106 | -0.048597 | -0.063746 | 0.20149 | -0.38358 | 0.023941 | -0.017956 | -0.033458 | 0.066194 | 0.21059 | -0.16166 | -0.27862 | -0.012793 | -121.1271 | 0.16581 | 0.11973 | 0.13252 | -121.1422 | -120.877 | 0.09217 | -121.0123 | 0.39473 | 0.33733 | 0.24516 | -120.8679 | -121.2401 | 0.32219 | 0.30704 | 0.57228 | 0.14784 | -121.4621 | 0.43698 | 0.58137 | 0.20913 | 0.35283 | -121.3571
3036.4531 | 121.3303 | -0.3891 | 121.0693 | 1.4211e-13 | -0.018517 | -0.00035676 | 0.001953 | -0.013775 | 0.014884 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.039201 | 0.0061595 | -0.20956 | -0.22752 | -0.2419 | -0.053175 | -0.050009 | 0.19233 | -0.39274 | 0.033099 | -0.008798 | -0.042615 | 0.070773 | 0.20143 | -0.1525 | -0.26946 | -0.003641 | -121.1225 | 0.17954 | 0.1472 | 0.15084 | -121.1193 | -120.877 | 0.11964 | -120.9986 | 0.4222 | 0.34648 | 0.22685 | -120.8679 | -121.2218 | 0.33592 | 0.33909 | 0.58143 | 0.16157 | -121.4621 | 0.45987 | 0.59053 | 0.2366 | 0.3803 | -121.3388
3038.2031 | 121.4218 | -0.28839 | 121.1334 | 1.4211e-13 | -0.018944 | 7.0442e-05 | 0.0017394 | -0.013989 | 0.014456 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016754 | 0.03856 | 0.0055187 | -0.16377 | -0.17258 | -0.2007 | -0.016548 | -0.077483 | 0.24269 | -0.34695 | 0.023941 | -0.008798 | -0.038036 | 0.066194 | 0.21059 | -0.14792 | -0.27862 | -0.05856 | -121.15 | 0.12462 | 0.087694 | 0.14625 | -121.2109 | -120.8907 | 0.009772 | -121.0672 | 0.31233 | 0.25035 | 0.24058 | -120.9228 | -121.2813 | 0.27184 | 0.21091 | 0.53109 | 0.11581 | -121.4804 | 0.35459 | 0.49898 | 0.14047 | 0.27959 | -121.412
3039.9531 | 121.4813 | -0.27924 | 121.1151 | 1.4211e-13 | -0.019158 | -0.00035676 | 0.001953 | -0.013775 | 0.014243 | -0.0073253 | -0.0035849 | 0.0047004 | 0.016541 | 0.03856 | 0.0059459 | -0.17293 | -0.17716 | -0.2007 | -0.021127 | -0.082062 | 0.24269 | -0.34237 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.20601 | -0.14792 | -0.27862 | -0.063136 | -121.1362 | 0.1063 | 0.078539 | 0.14168 | -121.1972 | -120.8724 | 0.000617 | -121.0443 | 0.30776 | 0.23662 | 0.236 | -120.9091 | -121.263 | 0.25811 | 0.19717 | 0.52193 | 0.10208 | -121.4575 | 0.35001 | 0.48524 | 0.13131 | 0.26586 | -121.3937
3041.7031 | 121.4493 | -0.37537 | 121.0327 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.0015258 | -0.013775 | 0.01467 | 0.0079357 | -0.0033713 | 0.0040594 | 0.016541 | 0.03856 | 0.0059459 | -0.24161 | -0.24126 | -0.26937 | -0.057754 | -0.059167 | 0.1786 | -0.41563 | 0.033099 | -0.017956 | -0.042615 | 0.075351 | 0.21059 | -0.15708 | -0.27862 | -0.040268 | -121.0905 | 0.13376 | 0.10599 | 0.14626 | -121.0919 | -120.8541 | 0.096747 | -120.9574 | 0.40846 | 0.33275 | 0.236 | -120.8221 | -121.1898 | 0.31761 | 0.3162 | 0.55396 | 0.13411 | -121.4483 | 0.45072 | 0.58595 | 0.21829 | 0.35741 | -121.3113
3043.4531 | 121.4401 | -0.40283 | 121.0236 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.001953 | -0.014202 | 0.014456 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016968 | 0.038773 | 0.0059459 | -0.25076 | -0.25042 | -0.28768 | -0.080646 | -0.050009 | 0.16486 | -0.42021 | 0.02852 | -0.017956 | -0.042615 | 0.061616 | 0.20601 | -0.1525 | -0.2832 | -0.017381 | -121.1042 | 0.15207 | 0.11515 | 0.13253 | -121.0736 | -120.8587 | 0.11963 | -120.9619 | 0.43135 | 0.36022 | 0.24058 | -120.8176 | -121.1761 | 0.32219 | 0.35282 | 0.56769 | 0.15242 | -121.4438 | 0.46445 | 0.60884 | 0.25033 | 0.38488 | -121.3068
3045.2031 | 121.3852 | -0.39825 | 121.1014 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.001953 | -0.013989 | 0.014243 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016968 | 0.03856 | 0.0059459 | -0.2645 | -0.26415 | -0.29684 | -0.080646 | -0.050009 | 0.1557 | -0.44769 | 0.02852 | -0.017956 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.2832 | -0.049433 | -121.182 | 0.13376 | 0.10141 | 0.15085 | -121.1514 | -120.9457 | 0.11506 | -121.0352 | 0.42677 | 0.35564 | 0.24058 | -120.8954 | -121.2539 | 0.31761 | 0.34825 | 0.55396 | 0.1341 | -121.5491 | 0.46445 | 0.60426 | 0.24575 | 0.3803 | -121.3846
3046.9062 | 121.5042 | -0.3479 | 121.0968 | 1.4211e-13 | -0.01873 | -0.00035676 | 0.0017394 | -0.013989 | 0.014456 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.038773 | 0.0061595 | -0.21871 | -0.22295 | -0.25106 | -0.048597 | -0.059167 | 0.19233 | -0.39274 | 0.023941 | -0.008798 | -0.047194 | 0.061616 | 0.21059 | -0.1525 | -0.27862 | -0.04484 | -121.1454 | 0.12918 | 0.096842 | 0.14168 | -121.156 | -120.9045 | 0.069281 | -121.0352 | 0.37184 | 0.30071 | 0.23142 | -120.8862 | -121.2493 | 0.2993 | 0.28873 | 0.54023 | 0.12495 | -121.4895 | 0.40952 | 0.55849 | 0.1954 | 0.3391 | -121.3754
3048.6562 | 121.4584 | -0.2243 | 121.2845 | 1.4211e-13 | -0.018089 | -0.00078416 | 0.0015258 | -0.013775 | 0.04031 | 0.00030522 | -0.0035849 | 0.0040594 | 0.016541 | 0.039201 | 0.0063733 | -0.076785 | -0.094744 | -0.11829 | 0.07502 | 0.046148 | 0.32969 | -0.26911 | 0.019362 | -0.008798 | -0.042615 | 0.061616 | 0.21059 | -0.14792 | -0.27862 | -0.044805 | -121.2095 | 0.14752 | 0.10602 | 0.15082 | -121.2383 | -120.9548 | -0.054315 | -121.2229 | 0.24367 | 0.18169 | 0.236 | -121.0739 | -121.4324 | 0.29932 | 0.27045 | 0.55399 | 0.12956 | -121.5536 | 0.28592 | 0.43489 | 0.076382 | 0.21551 | -121.5631
3050.4219 | 121.5363 | -0.17853 | 121.2616 | 1.4211e-13 | -0.018303 | -0.00078416 | 0.001953 | -0.013561 | 0.042233 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016968 | 0.038987 | 0.0059459 | -0.053893 | -0.071851 | -0.095397 | 0.093333 | 0.069043 | 0.35258 | -0.24621 | 0.033099 | -0.008798 | -0.042615 | 0.070773 | 0.21516 | -0.1525 | -0.2832 | -0.067686 | -121.1683 | 0.12463 | 0.083131 | 0.15082 | -121.1926 | -120.909 | -0.10467 | -121.1908 | 0.21163 | 0.13591 | 0.24058 | -121.0464 | -121.4141 | 0.27186 | 0.24757 | 0.53111 | 0.10668 | -121.5078 | 0.2493 | 0.39369 | 0.026028 | 0.16973 | -121.5448
3052.1875 | 121.5271 | -0.17395 | 121.2845 | 1.4211e-13 | -0.01873 | -0.00057056 | 0.0015258 | -0.014416 | 0.038173 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016968 | 0.038773 | 0.0061595 | -0.040158 | -0.067272 | -0.081662 | 0.097912 | 0.073622 | 0.35716 | -0.24163 | 0.033099 | -0.008798 | -0.047194 | 0.061616 | 0.20601 | -0.15708 | -0.27862 | -0.067685 | -121.1866 | 0.13379 | 0.092288 | 0.15997 | -121.2109 | -120.9273 | -0.10467 | -121.2229 | 0.20705 | 0.12676 | 0.23142 | -121.0785 | -121.4416 | 0.27186 | 0.24757 | 0.53111 | 0.10668 | -121.5261 | 0.23557 | 0.37996 | 0.016871 | 0.16515 | -121.5631
3053.875 | 121.4218 | -0.22888 | 121.3303 | 1.4211e-13 | -0.018517 | -0.00057056 | 0.0017394 | -0.013561 | 0.037318 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016968 | 0.038987 | 0.0061595 | -0.058472 | -0.07643 | -0.099975 | 0.084176 | 0.064464 | 0.33885 | -0.25079 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20601 | -0.15708 | -0.2832 | -0.021911 | -121.2461 | 0.17041 | 0.12891 | 0.15082 | -121.2658 | -120.9914 | -0.054316 | -121.2641 | 0.25282 | 0.18169 | 0.236 | -121.1243 | -121.4873 | 0.31306 | 0.29335 | 0.56773 | 0.15245 | -121.5811 | 0.29508 | 0.43489 | 0.071803 | 0.21551 | -121.6135
3055.6094 | 121.55 | -0.16937 | 121.3211 | 1.4211e-13 | -0.01873 | -0.00078416 | 0.001953 | -0.013989 | 0.044156 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016541 | 0.038773 | 0.0061595 | -0.053893 | -0.081008 | -0.095397 | 0.084176 | 0.069043 | 0.34342 | -0.25079 | 0.023941 | -0.017956 | -0.038036 | 0.061616 | 0.21059 | -0.1525 | -0.27862 | -0.08142 | -121.2369 | 0.11548 | 0.073976 | 0.1554 | -121.2521 | -120.9777 | -0.10925 | -121.2595 | 0.19331 | 0.13134 | 0.24058 | -121.1105 | -121.4736 | 0.25355 | 0.23842 | 0.5128 | 0.088365 | -121.5719 | 0.23099 | 0.37996 | 0.016873 | 0.15142 | -121.5997
3057.3125 | 121.4172 | -0.23804 | 121.3486 | 1.4211e-13 | -0.018944 | -0.00057056 | 0.0017394 | -0.013775 | 0.042874 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016754 | 0.039201 | 0.0057323 | -0.053893 | -0.07643 | -0.090818 | 0.084176 | 0.073622 | 0.348 | -0.25537 | 0.023941 | -0.013377 | -0.033458 | 0.075351 | 0.20601 | -0.1525 | -0.27862 | -0.017335 | -121.2644 | 0.18414 | 0.14722 | 0.16455 | -121.275 | -121.0006 | -0.040582 | -121.2732 | 0.26198 | 0.20458 | 0.24516 | -121.1426 | -121.5011 | 0.32221 | 0.31166 | 0.58604 | 0.16161 | -121.6039 | 0.31339 | 0.44405 | 0.085537 | 0.22466 | -121.6272
3059.0625 | 121.4905 | -0.21973 | 121.3348 | 1.4211e-13 | -0.018303 | -0.00078416 | 0.0017394 | -0.013561 | 0.045865 | 0.015566 | -0.0033713 | 0.0047004 | 0.016968 | 0.038773 | 0.0061595 | -0.058472 | -0.081008 | -0.10455 | 0.088755 | 0.059885 | 0.34342 | -0.25537 | 0.023941 | -0.017956 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.26946 | -0.035645 | -121.2461 | 0.16126 | 0.11517 | 0.15082 | -121.275 | -120.9914 | -0.049735 | -121.2686 | 0.24367 | 0.18169 | 0.23143 | -121.1243 | -121.4873 | 0.30848 | 0.27961 | 0.56315 | 0.13872 | -121.5902 | 0.28592 | 0.43031 | 0.067227 | 0.20177 | -121.6043
3060.8125 | 121.4127 | -0.23804 | 121.2982 | 1.4211e-13 | -0.018517 | -0.00057056 | 0.001312 | -0.013989 | 0.051634 | 0.00030522 | -0.0035849 | 0.0044868 | 0.016968 | 0.038773 | 0.0059459 | -0.072207 | -0.094744 | -0.11371 | 0.070441 | 0.018675 | 0.32511 | -0.27827 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20601 | -0.15708 | -0.27862 | -0.04023 | -121.2278 | 0.16583 | 0.12433 | 0.16456 | -121.2795 | -120.9731 | -0.040582 | -121.232 | 0.26198 | 0.19084 | 0.23142 | -121.0922 | -121.4553 | 0.30848 | 0.25671 | 0.56315 | 0.14329 | -121.5765 | 0.30423 | 0.44405 | 0.080958 | 0.22466 | -121.5768
3062.5781 | 121.5546 | -0.24719 | 121.2662 | 1.4211e-13 | -0.01873 | -0.00014316 | 0.001953 | -0.013989 | 0.0339 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016968 | 0.039201 | 0.0061595 | -0.12715 | -0.14511 | -0.16407 | 0.010922 | -0.082062 | 0.27017 | -0.33321 | 0.023941 | -0.017956 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.27862 | -0.086022 | -121.2553 | 0.12004 | 0.083121 | 0.16914 | -121.3482 | -120.996 | -0.031427 | -121.2 | 0.27113 | 0.20458 | 0.236 | -121.0556 | -121.4187 | 0.25811 | 0.16513 | 0.51736 | 0.10208 | -121.5994 | 0.31339 | 0.45778 | 0.094692 | 0.22924 | -121.5448
3064.2656 | 115.9744 | -40.036 | 75.737 | 1.4211e-13 | -0.01638 | -0.0039894 | -0.00061124 | -0.011211 | 5.9252 | 0.0079357 | -0.0035849 | 0.0044868 | 0.016754 | 0.038987 | 0.0061595 | -7.828 | -10.479 | -10.543 | -3.7846 | -3.6628 | -3.6674 | -12.9253 | 0.037677 | -0.00422 | -0.028879 | 0.075351 | 0.21059 | -0.1525 | -0.26946 | 27.1108 | -79.5216 | 32.208 | 29.493 | 2.3822 | -79.3998 | -79.4044 | 39.7665 | -75.6616 | 40.0737 | 40.0071 | 0.24058 | -75.5264 | -75.8895 | 36.2515 | 36.3732 | 36.3686 | 29.557 | -88.6623 | 40.1114 | 40.2466 | 39.8835 | 40.0318 | -76.0065
3066.0156 | 120.5292 | -0.13275 | 120.4239 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.00409 | -0.013775 | 0.018516 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016754 | 0.038773 | 0.0057323 | 0.005626 | -0.016908 | -0.035879 | 0.14369 | 0.12857 | 0.39837 | -0.17753 | 0.023941 | -0.017956 | -0.051772 | 0.061616 | 0.20601 | -0.1525 | -0.27404 | -0.044779 | -120.2802 | 0.13838 | 0.096872 | 0.14165 | -120.2953 | -120.0255 | -0.14129 | -120.3623 | 0.15669 | 0.080979 | 0.22227 | -120.2179 | -120.5764 | 0.27645 | 0.26132 | 0.53112 | 0.11584 | -120.6014 | 0.19437 | 0.33876 | -0.019749 | 0.1148 | -120.6979
3067.7031 | 120.6848 | -0.20142 | 120.6619 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.00409 | -0.014202 | 0.018516 | 0.015566 | -0.0031575 | 0.0047004 | 0.016754 | 0.038987 | 0.0057323 | 0.005626 | -0.012329 | -0.031301 | 0.14827 | 0.13773 | 0.40295 | -0.17753 | 0.02852 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.14792 | -0.27862 | 0.023886 | -120.5137 | 0.20704 | 0.17012 | 0.14623 | -120.5242 | -120.259 | -0.077203 | -120.6003 | 0.22994 | 0.15422 | 0.23142 | -120.4559 | -120.8098 | 0.34969 | 0.33914 | 0.60436 | 0.18909 | -120.8395 | 0.26303 | 0.40742 | 0.053494 | 0.18346 | -120.9405
3069.4531 | 120.9045 | -0.14648 | 120.6848 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.00409 | -0.013775 | 0.018516 | 0.00030522 | -0.0031575 | 0.0044868 | 0.017182 | 0.039201 | 0.0059459 | 0.001048 | -0.021486 | -0.040457 | 0.14369 | 0.12857 | 0.40295 | -0.16837 | 0.023941 | -0.022535 | -0.051772 | 0.057037 | 0.20143 | -0.14792 | -0.2832 | -0.021889 | -120.5411 | 0.14753 | 0.10603 | 0.12792 | -120.5562 | -120.2819 | -0.13671 | -120.6278 | 0.17042 | 0.094712 | 0.23143 | -120.4834 | -120.8327 | 0.29018 | 0.27505 | 0.54943 | 0.125 | -120.8532 | 0.20352 | 0.34791 | -0.001438 | 0.12395 | -120.968
3071.1875 | 120.8359 | -0.1831 | 120.813 | 1.4211e-13 | -0.025568 | 0.00049784 | 0.00409 | -0.013775 | 0.018516 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.038773 | 0.0057323 | -0.003531 | -0.012329 | -0.040457 | 0.15285 | 0.13315 | 0.40295 | -0.17753 | 0.023941 | -0.013377 | -0.047194 | 0.070773 | 0.20601 | -0.1525 | -0.28778 | 0.005575 | -120.6601 | 0.17957 | 0.14265 | 0.13707 | -120.6798 | -120.41 | -0.10467 | -120.7422 | 0.20705 | 0.13591 | 0.24058 | -120.607 | -120.9655 | 0.33596 | 0.31625 | 0.58605 | 0.17078 | -120.9905 | 0.25388 | 0.38911 | 0.030605 | 0.16973 | -121.1008
3072.9531 | 120.8908 | -0.17853 | 120.8405 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.0043036 | -0.014202 | 0.01873 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016754 | 0.038987 | 0.0057323 | -0.003531 | -0.016908 | -0.035879 | 0.14827 | 0.13315 | 0.40295 | -0.17753 | 0.014784 | -0.013377 | -0.051772 | 0.061616 | 0.20143 | -0.15708 | -0.28778 | 0.000998 | -120.6922 | 0.175 | 0.14265 | 0.14165 | -120.7073 | -120.4375 | -0.10925 | -120.7788 | 0.19331 | 0.12676 | 0.23601 | -120.639 | -120.9975 | 0.3268 | 0.31168 | 0.58147 | 0.16162 | -121.018 | 0.24014 | 0.37996 | 0.021449 | 0.16515 | -121.1282
3074.6562 | 121.0464 | -0.1236 | 120.8176 | 1.4211e-13 | -0.025782 | 0.00028424 | 0.00409 | -0.013989 | 0.01873 | 0.015566 | -0.0031575 | 0.0042732 | 0.016754 | 0.038987 | 0.0061595 | -0.008109 | -0.021486 | -0.035879 | 0.14369 | 0.12857 | 0.39837 | -0.15921 | 0.014784 | -0.017956 | -0.051772 | 0.061616 | 0.20143 | -0.1525 | -0.2832 | -0.035619 | -120.6739 | 0.11549 | 0.087717 | 0.12334 | -120.689 | -120.4192 | -0.1596 | -120.7559 | 0.13838 | 0.071824 | 0.23143 | -120.6161 | -120.9701 | 0.26729 | 0.25216 | 0.52196 | 0.10211 | -120.9768 | 0.18521 | 0.32503 | -0.028904 | 0.10564 | -121.1008
3076.4062 | 120.9457 | -0.19226 | 120.9091 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.0043036 | -0.013989 | 0.019371 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016968 | 0.039201 | 0.0057323 | -0.008109 | -0.016908 | -0.040457 | 0.14827 | 0.12399 | 0.40753 | -0.18211 | 0.014784 | -0.017956 | -0.047194 | 0.070773 | 0.21059 | -0.1525 | -0.2832 | 0.010152 | -120.7608 | 0.18415 | 0.1518 | 0.14165 | -120.7851 | -120.5016 | -0.090937 | -120.8383 | 0.20704 | 0.14507 | 0.236 | -120.6985 | -121.0616 | 0.34053 | 0.31625 | 0.59979 | 0.17535 | -121.0912 | 0.26303 | 0.40285 | 0.039761 | 0.1743 | -121.1923
3078.1562 | 121.0373 | -0.16937 | 120.9274 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.0036626 | -0.013989 | 0.019371 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016968 | 0.038987 | 0.0059459 | 0.001048 | -0.012329 | -0.040457 | 0.14827 | 0.12857 | 0.39837 | -0.17753 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.2832 | -0.008157 | -120.7792 | 0.17042 | 0.12892 | 0.13707 | -120.7989 | -120.5291 | -0.11383 | -120.8612 | 0.19331 | 0.12218 | 0.236 | -120.7168 | -121.0799 | 0.31765 | 0.29794 | 0.56774 | 0.15704 | -121.105 | 0.23557 | 0.37996 | 0.016873 | 0.156 | -121.2106
3079.9219 | 121.0968 | -0.16937 | 120.9229 | 1.4211e-13 | -0.025568 | 0.00028424 | 0.00409 | -0.014416 | 0.019157 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016541 | 0.038773 | 0.0055187 | 0.001048 | -0.016908 | -0.035879 | 0.15743 | 0.12857 | 0.40295 | -0.17295 | 0.02852 | -0.017956 | -0.047194 | 0.070773 | 0.20601 | -0.1525 | -0.27404 | -0.003578 | -120.7654 | 0.17042 | 0.13349 | 0.13707 | -120.7943 | -120.5199 | -0.10467 | -120.8521 | 0.19789 | 0.12218 | 0.22685 | -120.7168 | -121.0754 | 0.3268 | 0.29794 | 0.57232 | 0.15246 | -121.0958 | 0.24015 | 0.37538 | 0.016873 | 0.15142 | -121.1969
3081.6875 | 121.1655 | -0.12817 | 120.932 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.0043036 | -0.014202 | 0.019584 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.038987 | 0.0057323 | 0.005626 | -0.021486 | -0.035879 | 0.14369 | 0.12857 | 0.39837 | -0.17295 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.2832 | -0.044777 | -120.7883 | 0.1338 | 0.092295 | 0.13707 | -120.8034 | -120.5336 | -0.15502 | -120.8658 | 0.15212 | 0.08098 | 0.236 | -120.7214 | -121.0845 | 0.27187 | 0.25674 | 0.52654 | 0.10669 | -121.105 | 0.19437 | 0.33876 | -0.024326 | 0.1148 | -121.2152
3083.375 | 121.0831 | -0.18768 | 120.9732 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.0043036 | -0.014202 | 0.019371 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016968 | 0.039201 | 0.0061595 | 0.001048 | -0.016908 | -0.035879 | 0.14827 | 0.12399 | 0.39837 | -0.17295 | 0.014784 | -0.017956 | -0.051772 | 0.066194 | 0.20601 | -0.1525 | -0.2832 | 0.014732 | -120.8249 | 0.18873 | 0.1518 | 0.13707 | -120.8492 | -120.5748 | -0.095515 | -120.907 | 0.20247 | 0.13591 | 0.23143 | -120.7672 | -121.1257 | 0.33596 | 0.31167 | 0.58605 | 0.17077 | -121.1462 | 0.25388 | 0.39369 | 0.035183 | 0.16973 | -121.2564
3085.125 | 121.1105 | -0.18768 | 121.0144 | 1.4211e-13 | -0.025354 | 0.00071164 | 0.0043036 | -0.014202 | 0.019157 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016541 | 0.038773 | 0.0061595 | 0.005626 | -0.021486 | -0.045036 | 0.15285 | 0.16978 | 0.40295 | -0.18669 | 0.023941 | -0.017956 | -0.047194 | 0.066194 | 0.21516 | 0.085587 | -0.27862 | 0.000995 | -120.8616 | 0.19331 | 0.14265 | 0.14165 | -120.8446 | -120.6115 | -0.090936 | -120.9482 | 0.21162 | 0.14049 | 0.23142 | -120.7992 | -120.9288 | 0.34053 | 0.35746 | 0.59063 | 0.1662 | -121.2011 | 0.25388 | 0.40285 | 0.27327 | 0.16973 | -121.293
3086.8906 | 121.1197 | -0.26093 | 120.9732 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.00409 | -0.013775 | 0.019584 | 0.0079357 | -0.0029439 | 0.0042732 | 0.016541 | 0.039201 | 0.0059459 | -0.003531 | -0.021486 | -0.031301 | 0.14827 | 0.14231 | 0.40753 | -0.18669 | 0.02852 | -0.017956 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.27862 | 0.074237 | -120.8249 | 0.25739 | 0.22962 | 0.15539 | -120.8309 | -120.5657 | -0.017694 | -120.9024 | 0.28945 | 0.21831 | 0.236 | -120.7626 | -121.1257 | 0.4092 | 0.40323 | 0.66845 | 0.23944 | -121.1599 | 0.3317 | 0.47151 | 0.10843 | 0.24297 | -121.2518
3088.5781 | 121.1288 | -0.26093 | 120.9869 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.0043036 | -0.014416 | 0.019157 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016754 | 0.038987 | 0.0055187 | 0.005626 | -0.021486 | -0.031301 | 0.14369 | 0.12857 | 0.40295 | -0.15006 | 0.023941 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.1525 | -0.27862 | 0.11087 | -120.8432 | 0.26655 | 0.22962 | 0.11876 | -120.8584 | -120.584 | -0.017694 | -120.9253 | 0.28487 | 0.21373 | 0.23142 | -120.7809 | -121.1394 | 0.40462 | 0.38949 | 0.66387 | 0.23944 | -121.137 | 0.32254 | 0.46693 | 0.10843 | 0.24297 | -121.2656
3090.3281 | 121.257 | -0.18768 | 121.0144 | 1.4211e-13 | -0.025568 | 0.00049784 | 0.00409 | -0.014202 | 0.018943 | 0.00030522 | -0.0029439 | 0.0042732 | 0.016968 | 0.038987 | 0.0061595 | 0.001048 | -0.012329 | -0.035879 | 0.15285 | 0.12399 | 0.39837 | -0.15921 | 0.02852 | -0.013377 | -0.051772 | 0.066194 | 0.21059 | -0.1525 | -0.2832 | 0.028468 | -120.8616 | 0.18873 | 0.1518 | 0.12334 | -120.8904 | -120.616 | -0.095515 | -120.9482 | 0.2162 | 0.13591 | 0.23143 | -120.8038 | -121.1669 | 0.34053 | 0.31167 | 0.58605 | 0.17535 | -121.1736 | 0.25388 | 0.39827 | 0.035183 | 0.17431 | -121.2976
3092.0312 | 121.1243 | -0.23346 | 121.051 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.00409 | -0.013775 | 0.019371 | 0.0079357 | -0.0029439 | 0.0042732 | 0.016968 | 0.039201 | 0.0059459 | 0.005626 | -0.016908 | -0.035879 | 0.14827 | 0.14231 | 0.40295 | -0.17295 | 0.023941 | -0.017956 | -0.051772 | 0.066194 | 0.21059 | -0.14792 | -0.2832 | 0.060508 | -120.9028 | 0.23908 | 0.19758 | 0.13707 | -120.9087 | -120.6481 | -0.049739 | -120.9848 | 0.2574 | 0.18169 | 0.23143 | -120.8404 | -121.1989 | 0.38173 | 0.37577 | 0.6364 | 0.21655 | -121.224 | 0.29965 | 0.44405 | 0.085537 | 0.2155 | -121.3342
3093.7812 | 121.3028 | -0.1831 | 121.0144 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.00409 | -0.014202 | 0.019371 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016968 | 0.038987 | 0.0061595 | 0.001048 | -0.012329 | -0.035879 | 0.15285 | 0.12399 | 0.39837 | -0.18211 | 0.02852 | -0.017956 | -0.051772 | 0.070773 | 0.20601 | -0.1525 | -0.2832 | 0.000996 | -120.8616 | 0.18415 | 0.14723 | 0.14623 | -120.8904 | -120.616 | -0.10009 | -120.9436 | 0.21162 | 0.13133 | 0.23143 | -120.8084 | -121.1669 | 0.33596 | 0.3071 | 0.58147 | 0.17078 | -121.1965 | 0.25388 | 0.38911 | 0.030605 | 0.16515 | -121.2976
3095.5312 | 121.2753 | -0.2243 | 121.0602 | 1.4211e-13 | -0.025568 | 0.00049784 | 0.0043036 | -0.014202 | 0.019157 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016754 | 0.038773 | 0.0057323 | -0.003531 | -0.021486 | -0.040457 | 0.14369 | 0.12399 | 0.39837 | -0.17295 | 0.033099 | -0.008798 | -0.042615 | 0.070773 | 0.20143 | -0.1525 | -0.27862 | 0.051353 | -120.9165 | 0.22077 | 0.18385 | 0.13249 | -120.9362 | -120.6618 | -0.054315 | -120.9894 | 0.2574 | 0.18169 | 0.236 | -120.8588 | -121.2127 | 0.368 | 0.34829 | 0.62267 | 0.20282 | -121.2331 | 0.29508 | 0.42573 | 0.071804 | 0.21551 | -121.3388
3097.2188 | 121.1563 | -0.25177 | 121.0602 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.0043036 | -0.014202 | 0.019371 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016968 | 0.038773 | 0.0061595 | 0.005626 | -0.016908 | -0.035879 | 0.14369 | 0.13773 | 0.40295 | -0.17295 | 0.019362 | -0.027113 | -0.047194 | 0.057037 | 0.21059 | -0.15708 | -0.27862 | 0.078819 | -120.9165 | 0.2574 | 0.21589 | 0.13707 | -120.9225 | -120.6572 | -0.026849 | -121.0031 | 0.27113 | 0.20458 | 0.23142 | -120.8496 | -121.2173 | 0.39546 | 0.3895 | 0.65472 | 0.23486 | -121.2331 | 0.30881 | 0.46236 | 0.094691 | 0.22466 | -121.3388
3098.9688 | 121.2433 | -0.23346 | 121.0785 | 1.4211e-13 | -0.025782 | 0.00028424 | 0.00409 | -0.014202 | 0.019371 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016541 | 0.038773 | 0.0059459 | 0.005626 | -0.016908 | -0.031301 | 0.15285 | 0.14231 | 0.40753 | -0.17295 | 0.019362 | -0.017956 | -0.051772 | 0.061616 | 0.20601 | -0.16166 | -0.2832 | 0.060508 | -120.9256 | 0.23908 | 0.20216 | 0.14165 | -120.9362 | -120.671 | -0.049739 | -121.0169 | 0.25282 | 0.18169 | 0.23143 | -120.8725 | -121.2401 | 0.38631 | 0.37577 | 0.64098 | 0.21655 | -121.2514 | 0.29507 | 0.43947 | 0.071801 | 0.2155 | -121.3617
3100.6562 | 121.1884 | -0.22888 | 121.1472 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.0043036 | -0.013989 | 0.019157 | 0.015566 | -0.0033713 | 0.0042732 | 0.016754 | 0.038773 | 0.0059459 | 0.001048 | -0.016908 | -0.035879 | 0.14827 | 0.12857 | 0.40295 | -0.17295 | 0.014784 | -0.017956 | -0.056351 | 0.066194 | 0.21516 | -0.1525 | -0.27404 | 0.055931 | -120.9989 | 0.22993 | 0.193 | 0.13707 | -121.0186 | -120.7442 | -0.045158 | -121.081 | 0.24367 | 0.17253 | 0.21769 | -120.932 | -121.2997 | 0.37716 | 0.35745 | 0.63183 | 0.21197 | -121.3201 | 0.29508 | 0.44405 | 0.076382 | 0.21093 | -121.4212
3102.4219 | 120.2316 | -82.8644 | 37.1292 | 1.4211e-13 | -0.025568 | 0.00071164 | 0.0038762 | -0.013989 | 0.019371 | -0.0073253 | -0.0031575 | 0.0042732 | 0.016541 | 0.038987 | 0.0061595 | 0.023939 | 0.010564 | -0.012988 | 0.18032 | 0.17894 | 0.43042 | -0.099689 | 0.046835 | 0.009516 | -0.019721 | 0.10282 | 0.2289 | -0.12961 | -0.24657 | 82.7647 | -36.9489 | 82.8883 | 82.8514 | 0.086701 | -36.9503 | -36.6988 | 82.6178 | -37.0264 | 82.9112 | 82.8447 | 0.22685 | -36.9003 | -37.2588 | 83.0447 | 83.0433 | 83.2948 | 82.8749 | -37.2289 | 82.9672 | 83.0933 | 82.7348 | 82.8739 | -37.3758
3104.1719 | 120.6894 | -8.757 | 112.1979 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.00409 | -0.014202 | 0.019157 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016541 | 0.038773 | 0.0059459 | 0.005626 | -0.007751 | -0.022144 | 0.15743 | 0.14231 | 0.40753 | -0.16837 | 0.023941 | -0.013377 | -0.042615 | 0.066194 | 0.21516 | -0.1525 | -0.27862 | 8.5886 | -112.0404 | 8.7626 | 8.7349 | 0.14623 | -112.0556 | -111.7904 | 8.4784 | -112.1317 | 8.781 | 8.7144 | 0.236 | -111.9827 | -112.3504 | 8.9145 | 8.8993 | 9.1645 | 8.7493 | -112.3662 | 8.8232 | 8.9722 | 8.6045 | 8.7436 | -112.4765
3105.9219 | 121.0693 | -7.8461 | 113.2004 | 1.4211e-13 | -0.025568 | 0.00049784 | 0.0043036 | -0.014202 | 0.01873 | 0.0079357 | -0.0031575 | 0.0042732 | 0.016541 | 0.038773 | 0.0057323 | -0.003531 | -0.016908 | -0.031301 | 0.15285 | 0.14688 | 0.39837 | -0.16837 | 0.014784 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.27862 | 7.6777 | -113.0475 | 7.8425 | 7.8148 | 0.13707 | -113.0535 | -112.802 | 7.5675 | -113.1342 | 7.8609 | 7.7989 | 0.23142 | -112.9898 | -113.3529 | 7.9989 | 7.993 | 8.2444 | 7.8292 | -113.3688 | 7.9123 | 8.0567 | 7.6936 | 7.8327 | -113.479
3107.6875 | 121.019 | -7.3425 | 113.8458 | 1.4211e-13 | -0.025782 | 0.00028424 | 0.00409 | -0.014202 | 0.019157 | 0.00030522 | -0.0035849 | 0.0044868 | 0.016754 | 0.038773 | 0.0057323 | 0.005626 | -0.012329 | -0.031301 | 0.14827 | 0.13773 | 0.4121 | -0.15921 | 0.019362 | -0.013377 | -0.038036 | 0.070773 | 0.21516 | -0.16166 | -0.27862 | 7.1833 | -113.6976 | 7.3482 | 7.3112 | 0.12791 | -113.7081 | -113.4337 | 7.0639 | -113.7751 | 7.3619 | 7.3045 | 0.24058 | -113.6307 | -114.0075 | 7.4908 | 7.4803 | 7.7546 | 7.3302 | -114.005 | 7.4133 | 7.5577 | 7.1809 | 7.3292 | -114.1244
3109.4375 | 121.1288 | -6.1478 | 114.9216 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.00409 | -0.014416 | 0.019157 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016754 | 0.038773 | 0.0057323 | 0.010204 | -0.012329 | -0.026723 | 0.14369 | 0.12399 | 0.40753 | -0.16837 | 0.02852 | -0.008798 | -0.042615 | 0.070773 | 0.20601 | -0.14792 | -0.27404 | 5.9794 | -114.7779 | 6.158 | 6.121 | 0.14165 | -114.7976 | -114.514 | 5.8737 | -114.8508 | 6.1763 | 6.1052 | 0.23142 | -114.7156 | -115.0695 | 6.2915 | 6.2718 | 6.5553 | 6.1354 | -115.0899 | 6.2185 | 6.3538 | 5.9998 | 6.139 | -115.1956
3111.125 | 121.17 | -6.2576 | 114.8804 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.0043036 | -0.013775 | 0.019371 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016754 | 0.039414 | 0.0059459 | 0.005626 | -0.016908 | -0.035879 | 0.15285 | 0.13315 | 0.40295 | -0.16837 | 0.02852 | -0.013377 | -0.047194 | 0.066194 | 0.21059 | -0.16166 | -0.2832 | 6.0893 | -114.7275 | 6.2633 | 6.2217 | 0.13249 | -114.7472 | -114.4774 | 5.9744 | -114.8142 | 6.2861 | 6.2104 | 0.236 | -114.6698 | -115.042 | 6.4105 | 6.3908 | 6.6606 | 6.2407 | -115.0487 | 6.3238 | 6.4682 | 6.096 | 6.2443 | -115.1636
3112.8906 | 121.2112 | -6.1386 | 115.036 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.0043036 | -0.013989 | 0.019371 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016541 | 0.038987 | 0.0059459 | 0.005626 | -0.012329 | -0.026723 | 0.14827 | 0.15146 | 0.40753 | -0.17295 | 0.023941 | -0.00422 | -0.038036 | 0.066194 | 0.21059 | -0.15708 | -0.27404 | 5.9657 | -114.8877 | 6.1442 | 6.1119 | 0.14623 | -114.8845 | -114.6285 | 5.8646 | -114.9698 | 6.1626 | 6.1006 | 0.236 | -114.8254 | -115.1931 | 6.2869 | 6.2901 | 6.5461 | 6.1263 | -115.209 | 6.2048 | 6.3492 | 5.9815 | 6.1344 | -115.3101
3114.6562 | 121.257 | -6.0471 | 115.0864 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.00409 | -0.013989 | 0.019157 | 0.015566 | -0.0033713 | 0.0042732 | 0.016541 | 0.038987 | 0.0057323 | 0.005626 | -0.007751 | -0.026723 | 0.15285 | 0.12857 | 0.40295 | -0.17295 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.21059 | -0.1525 | -0.27404 | 5.8741 | -114.9335 | 6.0527 | 6.0203 | 0.14623 | -114.9578 | -114.6834 | 5.773 | -115.0156 | 6.0756 | 6.0044 | 0.23142 | -114.8758 | -115.2389 | 6.1999 | 6.1756 | 6.45 | 6.0393 | -115.2593 | 6.1178 | 6.2576 | 5.8946 | 6.0337 | -115.3604
3116.3438 | 121.2708 | -6.0287 | 115.155 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.00409 | -0.013989 | 0.01873 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016754 | 0.039201 | 0.0057323 | 0.005626 | -0.021486 | -0.040457 | 0.14369 | 0.13315 | 0.39379 | -0.14548 | 0.02852 | -0.013377 | -0.047194 | 0.075351 | 0.20143 | -0.15708 | -0.2832 | 5.8833 | -115.0113 | 6.0344 | 5.9883 | 0.10502 | -115.0219 | -114.7612 | 5.7456 | -115.0797 | 6.0573 | 5.9816 | 0.236 | -114.9536 | -115.3121 | 6.1724 | 6.1619 | 6.4225 | 6.0073 | -115.3005 | 6.1041 | 6.2302 | 5.8717 | 6.0154 | -115.4382
3118.0938 | 121.1792 | -6.0562 | 115.2054 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.00409 | -0.014202 | 0.019584 | 0.015566 | -0.0035849 | 0.0042732 | 0.016541 | 0.038987 | 0.0061595 | 0.010204 | -0.016908 | -0.031301 | 0.14369 | 0.12857 | 0.40295 | -0.16837 | 0.02852 | -0.008798 | -0.047194 | 0.066194 | 0.20601 | -0.15708 | -0.28778 | 5.8878 | -115.0617 | 6.0664 | 6.0249 | 0.13707 | -115.0768 | -114.8024 | 5.7684 | -115.1392 | 6.0847 | 6.009 | 0.24058 | -114.9994 | -115.3625 | 6.1999 | 6.1848 | 6.4592 | 6.0393 | -115.3738 | 6.1224 | 6.2622 | 5.8991 | 6.0474 | -115.4932
3119.8594 | 121.312 | -5.9692 | 115.242 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.0043036 | -0.014202 | 0.019157 | 0.015566 | -0.0031575 | 0.0042732 | 0.016327 | 0.039201 | 0.0057323 | 0.010204 | -0.016908 | -0.031301 | 0.15285 | 0.12399 | 0.38921 | -0.1409 | 0.023941 | -0.013377 | -0.047194 | 0.070773 | 0.20601 | -0.1525 | -0.2832 | 5.8283 | -115.0892 | 5.9794 | 5.9379 | 0.1096 | -115.118 | -114.8528 | 5.686 | -115.1712 | 5.9932 | 5.922 | 0.236 | -115.036 | -115.3945 | 6.1221 | 6.0932 | 6.3584 | 5.9523 | -115.3829 | 6.04 | 6.1752 | 5.8167 | 5.9559 | -115.5252
3121.6094 | 121.2936 | -6.0287 | 115.2283 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.0043036 | -0.014416 | 0.019157 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016327 | 0.038987 | 0.0057323 | 0.010204 | -0.012329 | -0.026723 | 0.13912 | 0.11941 | 0.40753 | -0.16837 | 0.019362 | -0.013377 | -0.047194 | 0.066194 | 0.20601 | -0.1525 | -0.2832 | 5.8604 | -115.0892 | 6.039 | 6.002 | 0.14165 | -115.1089 | -114.8207 | 5.7456 | -115.1621 | 6.0481 | 5.9816 | 0.236 | -115.0223 | -115.3808 | 6.1679 | 6.1482 | 6.4363 | 6.0164 | -115.3966 | 6.0949 | 6.2348 | 5.8762 | 6.0154 | -115.5115
3123.3125 | 121.2204 | -6.189 | 115.1688 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.00409 | -0.014202 | 0.018943 | -0.0073253 | -0.0033713 | 0.0042732 | 0.017182 | 0.038987 | 0.0059459 | 0.001048 | -0.016908 | -0.031301 | 0.15285 | 0.12857 | 0.39837 | -0.14548 | 0.014784 | -0.008798 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.27404 | 6.0435 | -115.0159 | 6.19 | 6.1577 | 0.11418 | -115.0402 | -114.7704 | 5.9149 | -115.1026 | 6.2037 | 6.1463 | 0.23142 | -114.9582 | -115.3213 | 6.3418 | 6.3175 | 6.5873 | 6.1721 | -115.3142 | 6.2552 | 6.3996 | 6.0365 | 6.1802 | -115.4428
3125.0781 | 121.2708 | -6.0745 | 115.2237 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.0043036 | -0.014416 | 0.018943 | 0.00030522 | -0.0029439 | 0.0047004 | 0.016541 | 0.039201 | 0.0059459 | 0.005626 | -0.021486 | -0.035879 | 0.14369 | 0.13315 | 0.40295 | -0.15921 | 0.023941 | -0.013377 | -0.042615 | 0.061616 | 0.21516 | -0.15708 | -0.27404 | 5.9153 | -115.08 | 6.0802 | 6.0386 | 0.12334 | -115.0905 | -114.8207 | 5.8005 | -115.1621 | 6.0985 | 6.0319 | 0.23142 | -115.0085 | -115.3808 | 6.2182 | 6.2077 | 6.4775 | 6.053 | -115.3829 | 6.1361 | 6.2897 | 5.9174 | 6.0611 | -115.4977
3126.7656 | 121.344 | -5.9921 | 115.2649 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.00409 | -0.013989 | 0.019157 | -0.0073253 | -0.0031575 | 0.0042732 | 0.016541 | 0.038987 | 0.0057323 | 0.010204 | -0.016908 | -0.031301 | 0.15285 | 0.12857 | 0.40295 | -0.118 | 0.023941 | -0.008798 | -0.042615 | 0.070773 | 0.21516 | -0.15708 | -0.27404 | 5.8741 | -115.112 | 6.0023 | 5.9608 | 0.086703 | -115.1363 | -114.8619 | 5.7181 | -115.1941 | 6.0161 | 5.9495 | 0.23142 | -115.0497 | -115.422 | 6.145 | 6.1207 | 6.3951 | 5.9752 | -115.3829 | 6.0629 | 6.2073 | 5.835 | 5.9833 | -115.5389
3128.5312 | 121.3348 | -5.8823 | 115.4205 | 1.4211e-13 | -0.025995 | 0.00092524 | 0.0038762 | -0.014416 | 0.019371 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016541 | 0.038987 | 0.0057323 | -0.003531 | -0.016908 | -0.040457 | 0.15285 | 0.12857 | 0.39379 | -0.17295 | 0.02852 | -0.017956 | -0.051772 | 0.061616 | 0.20143 | -0.1525 | -0.27862 | 5.7093 | -115.2677 | 5.8787 | 5.8418 | 0.13249 | -115.292 | -115.0267 | 5.6036 | -115.3589 | 5.9108 | 5.8305 | 0.22685 | -115.2191 | -115.573 | 6.0351 | 6.0108 | 6.2761 | 5.8654 | -115.5935 | 5.9439 | 6.0837 | 5.7298 | 5.8643 | -115.6992
3130.2656 | 121.3165 | -5.9418 | 115.4388 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.014202 | 0.019371 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016541 | 0.038987 | 0.0059459 | 0.005626 | -0.016908 | -0.035879 | 0.14827 | 0.12399 | 0.40295 | -0.16379 | 0.014784 | -0.013377 | -0.042615 | 0.066194 | 0.20601 | -0.15708 | -0.27862 | 5.778 | -115.2906 | 5.9474 | 5.9059 | 0.12792 | -115.3149 | -115.0359 | 5.6632 | -115.3726 | 5.9566 | 5.8992 | 0.236 | -115.2328 | -115.5959 | 6.09 | 6.0658 | 6.3447 | 5.9249 | -115.6026 | 6.008 | 6.1478 | 5.7847 | 5.9284 | -115.7175
3131.9531 | 121.2891 | -5.9509 | 115.3885 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.0043036 | -0.013989 | 0.019157 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016541 | 0.039201 | 0.0055187 | 0.001048 | -0.021486 | -0.035879 | 0.14369 | 0.12399 | 0.39379 | -0.15464 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.21516 | -0.14792 | -0.27404 | 5.7963 | -115.2448 | 5.952 | 5.915 | 0.11876 | -115.2645 | -114.9947 | 5.6769 | -115.3177 | 5.9794 | 5.9037 | 0.22685 | -115.1733 | -115.5364 | 6.0946 | 6.0749 | 6.3447 | 5.9294 | -115.5431 | 6.0217 | 6.1661 | 5.803 | 5.9376 | -115.6625
3133.7188 | 121.2708 | -5.8594 | 115.5029 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.00409 | -0.014202 | 0.019371 | -0.0073253 | -0.0035849 | 0.0044868 | 0.016541 | 0.038773 | 0.0059459 | 0.005626 | -0.016908 | -0.035879 | 0.14827 | 0.12399 | 0.40295 | -0.15006 | 0.023941 | -0.013377 | -0.042615 | 0.066194 | 0.21516 | -0.14792 | -0.27862 | 5.7093 | -115.3547 | 5.865 | 5.8235 | 0.11418 | -115.3789 | -115.1 | 5.5808 | -115.4367 | 5.8833 | 5.8168 | 0.236 | -115.2878 | -115.6509 | 6.0076 | 5.9834 | 6.2623 | 5.8425 | -115.653 | 5.9256 | 6.0745 | 5.7115 | 5.846 | -115.7815
3135.4688 | 121.3531 | -5.928 | 115.4388 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.00409 | -0.014202 | 0.019157 | 0.0079357 | -0.0029439 | 0.0042732 | 0.016754 | 0.039201 | 0.0059459 | 0.010204 | -0.007751 | -0.035879 | 0.14369 | 0.11941 | 0.39837 | -0.15921 | 0.02852 | -0.013377 | -0.042615 | 0.070773 | 0.20601 | -0.14792 | -0.2832 | 5.7688 | -115.2951 | 5.9382 | 5.8922 | 0.12334 | -115.3194 | -115.0405 | 5.6448 | -115.3681 | 5.9566 | 5.8854 | 0.24058 | -115.2328 | -115.5868 | 6.0717 | 6.0475 | 6.3264 | 5.9203 | -115.5981 | 5.9988 | 6.134 | 5.7801 | 5.9147 | -115.722
3137.2344 | 121.4447 | -5.8594 | 115.4434 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.00409 | -0.013989 | 0.019157 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016541 | 0.038987 | 0.0061595 | 0.001048 | -0.012329 | -0.040457 | 0.14827 | 0.13315 | 0.39379 | -0.16837 | 0.019362 | -0.017956 | -0.051772 | 0.070773 | 0.21516 | -0.14792 | -0.27862 | 5.691 | -115.2951 | 5.8604 | 5.8189 | 0.12792 | -115.3103 | -115.0496 | 5.5808 | -115.3726 | 5.8787 | 5.8076 | 0.22685 | -115.2283 | -115.5913 | 6.0076 | 5.9925 | 6.2532 | 5.847 | -115.6118 | 5.9301 | 6.0745 | 5.7115 | 5.8414 | -115.722
3138.9375 | 121.4172 | -5.8777 | 115.4892 | 1.4211e-13 | -0.025782 | 0.00028424 | 0.00409 | -0.013989 | 0.019157 | 0.015566 | -0.0031575 | 0.0042732 | 0.016754 | 0.039201 | 0.0057323 | 0.001048 | -0.021486 | -0.040457 | 0.14827 | 0.13315 | 0.39837 | -0.15464 | 0.023941 | -0.013377 | -0.042615 | 0.075351 | 0.21059 | -0.1525 | -0.27862 | 5.723 | -115.3409 | 5.8787 | 5.8372 | 0.11418 | -115.356 | -115.0908 | 5.5991 | -115.4138 | 5.9016 | 5.8351 | 0.236 | -115.2786 | -115.6417 | 6.026 | 6.0108 | 6.2761 | 5.8562 | -115.6438 | 5.953 | 6.0883 | 5.7252 | 5.8643 | -115.7678
3140.6875 | 121.344 | -5.8823 | 115.5716 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.0043036 | -0.01463 | 0.019157 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016541 | 0.039414 | 0.0061595 | 0.010204 | -0.012329 | -0.031301 | 0.15285 | 0.12857 | 0.39837 | -0.17295 | 0.02852 | -0.017956 | -0.042615 | 0.075351 | 0.21059 | -0.1525 | -0.2832 | 5.7093 | -115.4187 | 5.8925 | 5.851 | 0.14165 | -115.443 | -115.1732 | 5.5991 | -115.4962 | 5.9108 | 5.8396 | 0.24058 | -115.361 | -115.7241 | 6.0351 | 6.0108 | 6.2806 | 5.8699 | -115.7445 | 5.9576 | 6.0928 | 5.7298 | 5.8643 | -115.8548
3142.375 | 121.3577 | -6.0516 | 115.3793 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.0043036 | -0.014416 | 0.019157 | 0.00030522 | -0.0035849 | 0.0044868 | 0.016754 | 0.038987 | 0.0055187 | 0.005626 | -0.012329 | -0.040457 | 0.14827 | 0.12399 | 0.39837 | -0.17295 | 0.023941 | -0.017956 | -0.051772 | 0.075351 | 0.21059 | -0.15708 | -0.27862 | 5.8787 | -115.2311 | 6.0573 | 6.0112 | 0.13249 | -115.2553 | -114.981 | 5.773 | -115.304 | 6.0756 | 5.9999 | 0.22685 | -115.1687 | -115.5364 | 6.1999 | 6.1756 | 6.45 | 6.0393 | -115.5523 | 6.127 | 6.2622 | 5.8946 | 6.0337 | -115.658
3144.125 | 121.4859 | -5.8319 | 115.5304 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.00409 | -0.014416 | 0.019371 | 0.00030522 | -0.0029439 | 0.0040594 | 0.016541 | 0.039201 | 0.0055187 | 0.010204 | -0.007751 | -0.031301 | 0.14369 | 0.13315 | 0.40753 | -0.16837 | 0.023941 | -0.013377 | -0.042615 | 0.061616 | 0.21059 | -0.1525 | -0.2832 | 5.6635 | -115.3867 | 5.8421 | 5.8006 | 0.13707 | -115.3972 | -115.1229 | 5.5487 | -115.4688 | 5.8558 | 5.7893 | 0.24058 | -115.3198 | -115.6829 | 5.9756 | 5.9651 | 6.2394 | 5.8242 | -115.6988 | 5.8935 | 6.0425 | 5.6794 | 5.8185 | -115.8136
3145.875 | 121.5042 | -5.928 | 115.4388 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.00409 | -0.014202 | 0.018943 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016754 | 0.039201 | 0.0057323 | 0.001048 | -0.007751 | -0.035879 | 0.14369 | 0.12399 | 0.39837 | -0.17295 | 0.023941 | -0.013377 | -0.042615 | 0.066194 | 0.20143 | -0.15708 | -0.27862 | 5.7551 | -115.2951 | 5.9291 | 5.8922 | 0.13707 | -115.3149 | -115.0405 | 5.6494 | -115.3726 | 5.952 | 5.8854 | 0.236 | -115.2374 | -115.5959 | 6.0717 | 6.052 | 6.3264 | 5.9203 | -115.6118 | 5.9942 | 6.1295 | 5.771 | 5.9147 | -115.7175
3147.6406 | 121.4035 | -6.0379 | 115.4205 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.0038762 | -0.013989 | 0.019157 | 0.0079357 | -0.0031575 | 0.0049142 | 0.016541 | 0.039201 | 0.0059459 | 0.005626 | -0.016908 | -0.031301 | 0.14827 | 0.12399 | 0.39837 | -0.14548 | 0.02852 | -0.013377 | -0.038036 | 0.070773 | 0.21516 | -0.14334 | -0.28778 | 5.8924 | -115.2723 | 6.0435 | 6.0066 | 0.11418 | -115.2965 | -115.0222 | 5.7501 | -115.3498 | 6.0664 | 5.9999 | 0.24974 | -115.2054 | -115.5639 | 6.1862 | 6.1619 | 6.4363 | 6.021 | -115.566 | 6.1087 | 6.2531 | 5.8946 | 6.0245 | -115.7083
3149.3906 | 121.4401 | -5.9921 | 115.4572 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.014202 | 0.019157 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016327 | 0.039414 | 0.0061595 | 0.010204 | -0.012329 | -0.035879 | 0.14827 | 0.14688 | 0.39379 | -0.16379 | 0.02852 | -0.008798 | -0.038036 | 0.061616 | 0.21059 | -0.1525 | -0.2832 | 5.8283 | -115.3089 | 6.0023 | 5.9562 | 0.12792 | -115.3103 | -115.0634 | 5.7089 | -115.3955 | 6.0206 | 5.9541 | 0.24516 | -115.2466 | -115.6097 | 6.1404 | 6.139 | 6.3859 | 5.9798 | -115.6209 | 6.0537 | 6.2027 | 5.8396 | 5.9833 | -115.7404
3151.1562 | 121.5454 | -6.0059 | 115.3793 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.00409 | -0.014202 | 0.019371 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016541 | 0.039414 | 0.0061595 | 0.005626 | -0.012329 | -0.040457 | 0.14369 | 0.14688 | 0.39837 | -0.17295 | 0.02852 | -0.013377 | -0.051772 | 0.066194 | 0.21516 | -0.1525 | -0.27862 | 5.8329 | -115.2356 | 6.0115 | 5.9654 | 0.13249 | -115.2324 | -114.981 | 5.7272 | -115.3131 | 6.0344 | 5.9541 | 0.22685 | -115.1642 | -115.5318 | 6.1496 | 6.1527 | 6.4042 | 5.9935 | -115.5523 | 6.0721 | 6.221 | 5.8534 | 5.9925 | -115.658
3152.8594 | 121.4767 | -5.9601 | 115.4892 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.0045172 | -0.013775 | 0.019157 | 0.00030522 | -0.0031575 | 0.0040594 | 0.016754 | 0.038987 | 0.0059459 | 0.005626 | -0.016908 | -0.031301 | 0.14827 | 0.15146 | 0.39837 | -0.15464 | 0.02852 | -0.013377 | -0.051772 | 0.057037 | 0.21059 | -0.1525 | -0.28778 | 5.8054 | -115.3409 | 5.9657 | 5.9288 | 0.12334 | -115.3377 | -115.0908 | 5.6723 | -115.4322 | 5.9886 | 5.9083 | 0.23601 | -115.2786 | -115.6417 | 6.1084 | 6.1115 | 6.3585 | 5.9432 | -115.6438 | 6.0171 | 6.1707 | 5.8076 | 5.9467 | -115.777
3154.6094 | 121.4767 | -5.9738 | 115.4526 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.0043036 | -0.013775 | 0.019371 | 0.015566 | -0.0035849 | 0.0044868 | 0.016754 | 0.039414 | 0.0059459 | 0.005626 | -0.012329 | -0.035879 | 0.14369 | 0.12399 | 0.40295 | -0.16837 | 0.033099 | -0.017956 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.27862 | 5.8054 | -115.3089 | 5.9794 | 5.9379 | 0.13249 | -115.3286 | -115.0496 | 5.6952 | -115.3864 | 6.0069 | 5.9312 | 0.236 | -115.2466 | -115.6051 | 6.1175 | 6.0978 | 6.3768 | 5.9615 | -115.6209 | 6.04 | 6.1798 | 5.8213 | 5.9559 | -115.7312
3156.2969 | 121.4127 | -6.0196 | 115.4755 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.0043036 | -0.014202 | 0.018943 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016541 | 0.038987 | 0.0059459 | 0.005626 | -0.016908 | -0.031301 | 0.15285 | 0.12399 | 0.40295 | -0.16379 | 0.023941 | -0.017956 | -0.056351 | 0.070773 | 0.21059 | -0.1525 | -0.2832 | 5.8558 | -115.3226 | 6.0252 | 5.9883 | 0.13249 | -115.3515 | -115.0725 | 5.7364 | -115.4047 | 6.0435 | 5.9632 | 0.22685 | -115.2649 | -115.628 | 6.1724 | 6.1436 | 6.4225 | 6.0027 | -115.6393 | 6.0904 | 6.2302 | 5.8671 | 6.0016 | -115.7587
3158.0625 | 121.431 | -6.0287 | 115.4434 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.00409 | -0.013989 | 0.018943 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016754 | 0.038987 | 0.0055187 | 0.005626 | -0.021486 | -0.040457 | 0.14827 | 0.13315 | 0.39837 | -0.17295 | 0.023941 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.16166 | -0.26946 | 5.8558 | -115.2951 | 6.0344 | 5.9883 | 0.13249 | -115.3103 | -115.0451 | 5.7593 | -115.3818 | 6.0527 | 5.9816 | 0.22227 | -115.2374 | -115.6051 | 6.177 | 6.1619 | 6.4271 | 6.0073 | -115.6164 | 6.0904 | 6.2348 | 5.8671 | 6.0108 | -115.7129
3159.8281 | 121.4493 | -6.0745 | 115.4251 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.00409 | -0.014202 | 0.018943 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016754 | 0.039201 | 0.0059459 | 0.001048 | -0.016908 | -0.035879 | 0.14827 | 0.12399 | 0.40295 | -0.16379 | 0.023941 | -0.017956 | -0.047194 | 0.061616 | 0.20601 | -0.15708 | -0.27404 | 5.9107 | -115.2768 | 6.0756 | 6.0386 | 0.12792 | -115.3011 | -115.0222 | 5.8005 | -115.3635 | 6.0985 | 6.0273 | 0.22685 | -115.2191 | -115.5822 | 6.2228 | 6.1985 | 6.4775 | 6.0576 | -115.5889 | 6.1361 | 6.2805 | 5.9174 | 6.0566 | -115.6992
3161.5781 | 121.4401 | -6.0471 | 115.4572 | 1.4211e-13 | -0.025782 | 0.00071164 | 0.0045172 | -0.014202 | 0.019371 | 0.00030522 | -0.0035849 | 0.0044868 | 0.016327 | 0.039414 | 0.0055187 | 0.001048 | -0.016908 | -0.040457 | 0.14827 | 0.12857 | 0.40295 | -0.16837 | 0.023941 | -0.013377 | -0.047194 | 0.066194 | 0.20601 | -0.15708 | -0.2832 | 5.8787 | -115.3089 | 6.0481 | 6.0066 | 0.12792 | -115.3286 | -115.0542 | 5.7639 | -115.391 | 6.071 | 5.9999 | 0.236 | -115.2511 | -115.6142 | 6.1953 | 6.1756 | 6.45 | 6.0301 | -115.6255 | 6.1133 | 6.2531 | 5.89 | 6.0337 | -115.7404
3163.2812 | 121.2524 | -86.8698 | 33.8425 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.0043036 | -0.014416 | 0.019157 | 0.015566 | -0.0033713 | 0.0044868 | 0.016754 | 0.039201 | 0.0057323 | 0.028518 | 0.010564 | -0.012988 | 0.17574 | 0.19267 | 0.43042 | -0.026426 | 0.046835 | 0.014095 | -0.005985 | 0.098244 | 0.23806 | -0.10214 | -0.24657 | 86.8434 | -33.6667 | 86.8983 | 86.8568 | 0.013438 | -33.6498 | -33.412 | 86.6232 | -33.7442 | 86.9166 | 86.8638 | 0.24058 | -33.6044 | -33.9446 | 87.0456 | 87.0625 | 87.3002 | 86.8804 | -33.8689 | 86.9681 | 87.1079 | 86.7677 | 86.8839 | -34.089
3165.0469 | 120.9503 | -10.9222 | 110.5179 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.0045172 | -0.013989 | 0.018943 | 0.015566 | -0.0033713 | 0.0044868 | 0.016327 | 0.039201 | 0.0057323 | 0.014783 | -0.016908 | -0.031301 | 0.14827 | 0.12399 | 0.39837 | -0.16837 | 0.033099 | -0.022535 | -0.047194 | 0.070773 | 0.20601 | -0.1525 | -0.27404 | 10.7539 | -110.3696 | 10.937 | 10.8909 | 0.13707 | -110.3939 | -110.1195 | 10.6482 | -110.4471 | 10.9553 | 10.875 | 0.22685 | -110.3119 | -110.6704 | 11.0705 | 11.0462 | 11.3206 | 10.9053 | -110.6863 | 10.993 | 11.1282 | 10.7697 | 10.8997 | -110.7919
3166.7344 | 121.3852 | -7.3425 | 114.0106 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.01463 | 0.019371 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016327 | 0.039201 | 0.0055187 | 0.001048 | -0.012329 | -0.035879 | 0.14827 | 0.13315 | 0.40295 | -0.16379 | 0.02852 | -0.00422 | -0.047194 | 0.066194 | 0.20601 | -0.14792 | -0.27404 | 7.1787 | -113.8623 | 7.3436 | 7.3066 | 0.12792 | -113.8775 | -113.6077 | 7.0685 | -113.9444 | 7.371 | 7.2953 | 0.22685 | -113.8046 | -114.1585 | 7.4908 | 7.4757 | 7.7455 | 7.3302 | -114.1744 | 7.4087 | 7.5485 | 7.1946 | 7.3383 | -114.2847
3168.5 | 121.344 | -6.6742 | 114.7659 | 1.4211e-13 | -0.025782 | 0.00028424 | 0.0038762 | -0.014416 | 0.018943 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016541 | 0.039201 | 0.0059459 | 0.005626 | -0.012329 | -0.035879 | 0.15285 | 0.13315 | 0.39379 | -0.16837 | 0.014784 | -0.013377 | -0.051772 | 0.066194 | 0.20601 | -0.15708 | -0.27404 | 6.5058 | -114.6131 | 6.6798 | 6.6383 | 0.13249 | -114.6328 | -114.3721 | 6.4002 | -114.6997 | 6.689 | 6.6224 | 0.22227 | -114.5599 | -114.923 | 6.827 | 6.8073 | 7.068 | 6.6619 | -114.9343 | 6.7404 | 6.8802 | 6.5171 | 6.6608 | -115.04
3170.25 | 121.3623 | -7.4844 | 113.9465 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0045172 | -0.014202 | 0.019157 | 0.0079357 | -0.0029439 | 0.0044868 | 0.016113 | 0.038987 | 0.0057323 | 0.001048 | -0.021486 | -0.031301 | 0.15743 | 0.12857 | 0.40295 | -0.16837 | 0.023941 | -0.008798 | -0.042615 | 0.066194 | 0.21516 | -0.1525 | -0.27862 | 7.3161 | -113.7891 | 7.4855 | 7.4531 | 0.13707 | -113.818 | -113.5436 | 7.2058 | -113.8803 | 7.5084 | 7.4418 | 0.236 | -113.7314 | -114.099 | 7.6419 | 7.613 | 7.8874 | 7.4629 | -114.1149 | 7.5506 | 7.6996 | 7.3319 | 7.4756 | -114.2252
3171.9375 | 121.4127 | -7.338 | 114.1296 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.00409 | -0.013989 | 0.018943 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016754 | 0.039414 | 0.0059459 | 0.005626 | -0.012329 | -0.031301 | 0.15285 | 0.12857 | 0.39837 | -0.16379 | 0.02852 | -0.017956 | -0.038036 | 0.066194 | 0.21516 | -0.1525 | -0.27862 | 7.1742 | -113.9768 | 7.3436 | 7.3067 | 0.13249 | -114.0011 | -113.7313 | 7.0593 | -114.0634 | 7.3665 | 7.2999 | 0.24058 | -113.9145 | -114.2821 | 7.4908 | 7.4665 | 7.7363 | 7.3256 | -114.2934 | 7.4041 | 7.5531 | 7.1855 | 7.32 | -114.4083
3173.7031 | 121.4767 | -7.2739 | 114.1571 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.0043036 | -0.014416 | 0.019157 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016541 | 0.038987 | 0.0059459 | 0.010204 | -0.012329 | -0.040457 | 0.15285 | 0.12399 | 0.40295 | -0.16837 | 0.023941 | -0.013377 | -0.051772 | 0.066194 | 0.21516 | -0.15708 | -0.2832 | 7.1055 | -114.0043 | 7.2841 | 7.2334 | 0.12792 | -114.0331 | -113.7542 | 6.9907 | -114.0909 | 7.2978 | 7.2221 | 0.23143 | -113.9419 | -114.3142 | 7.4267 | 7.3979 | 7.6768 | 7.2615 | -114.3255 | 7.3401 | 7.489 | 7.1168 | 7.2605 | -114.4403
3175.3906 | 121.4127 | -7.5302 | 113.9877 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.0043036 | -0.014202 | 0.019371 | -0.0073253 | -0.0035849 | 0.0047004 | 0.016754 | 0.039628 | 0.0057323 | 0.005626 | -0.007751 | -0.035879 | 0.14369 | 0.13315 | 0.40753 | -0.17295 | 0.023941 | -0.008798 | -0.047194 | 0.070773 | 0.21516 | -0.15708 | -0.27862 | 7.3573 | -113.844 | 7.5358 | 7.4943 | 0.13707 | -113.8546 | -113.5802 | 7.2516 | -113.917 | 7.5542 | 7.483 | 0.23142 | -113.7726 | -114.1448 | 7.6739 | 7.6634 | 7.9377 | 7.5225 | -114.1607 | 7.601 | 7.7454 | 7.3731 | 7.5214 | -114.2664
3177.1562 | 121.4722 | -7.0999 | 114.3997 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.0038762 | -0.01463 | 0.019371 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016541 | 0.038987 | 0.0057323 | 0.014783 | -0.012329 | -0.035879 | 0.15285 | 0.12399 | 0.40295 | -0.17753 | 0.023941 | -0.017956 | -0.042615 | 0.070773 | 0.20601 | -0.15708 | -0.27862 | 6.9224 | -114.2469 | 7.1147 | 7.064 | 0.14165 | -114.2757 | -113.9968 | 6.8213 | -114.3289 | 7.1239 | 7.0573 | 0.236 | -114.1937 | -114.5568 | 7.2528 | 7.2239 | 7.5029 | 7.0876 | -114.5772 | 7.1707 | 7.3059 | 6.9428 | 7.082 | -114.6783
3178.8594 | 121.463 | -7.2189 | 114.4318 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.00409 | -0.014202 | 0.019371 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.038987 | 0.0057323 | 0.019361 | -0.016908 | -0.026723 | 0.14827 | 0.15146 | 0.39379 | -0.17753 | 0.019362 | -0.017956 | -0.051772 | 0.066194 | 0.21059 | -0.16166 | -0.27862 | 7.0414 | -114.2835 | 7.2383 | 7.1922 | 0.15081 | -114.2803 | -114.038 | 6.9403 | -114.3656 | 7.2383 | 7.1672 | 0.22685 | -114.2212 | -114.5934 | 7.3672 | 7.3704 | 7.6127 | 7.202 | -114.6093 | 7.2851 | 7.4295 | 7.0573 | 7.201 | -114.7104
3180.6094 | 120.7031 | -10.8994 | 109.6024 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.013989 | 0.018943 | 0.0079357 | -0.0035849 | 0.0044868 | 0.016113 | 0.039414 | 0.0059459 | 0.005626 | -0.012329 | -0.026723 | 0.14827 | 0.1652 | 0.4121 | -0.15464 | 0.023941 | -0.017956 | -0.042615 | 0.075351 | 0.21516 | -0.1525 | -0.26946 | 10.7447 | -109.4541 | 10.905 | 10.8726 | 0.12791 | -109.4372 | -109.1903 | 10.6299 | -109.527 | 10.9233 | 10.8567 | 0.22685 | -109.3872 | -109.7549 | 11.0476 | 11.0646 | 11.3115 | 10.887 | -109.757 | 10.9747 | 11.1145 | 10.7469 | 10.8814 | -109.8718
3182.3594 | 120.9 | -6.0837 | 115.1413 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.0043036 | -0.014416 | 0.018943 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016541 | 0.039414 | 0.0055187 | 0.001048 | -0.012329 | -0.031301 | 0.14827 | 0.13773 | 0.40753 | -0.15921 | 0.019362 | -0.008798 | -0.038036 | 0.070773 | 0.21059 | -0.15708 | -0.2832 | 5.9245 | -114.993 | 6.0847 | 6.0524 | 0.12791 | -115.0036 | -114.7338 | 5.8005 | -115.0705 | 6.103 | 6.0456 | 0.24516 | -114.9307 | -115.2984 | 6.232 | 6.2214 | 6.4912 | 6.0713 | -115.3005 | 6.1545 | 6.2943 | 5.9266 | 6.0749 | -115.4245
3184.0625 | 121.1792 | -5.69 | 115.5991 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.0043036 | -0.013989 | 0.019157 | -0.0073253 | -0.0035849 | 0.0047004 | 0.016541 | 0.039414 | 0.0057323 | 0.010204 | -0.012329 | -0.035879 | 0.14827 | 0.13315 | 0.40295 | -0.16379 | 0.019362 | -0.013377 | -0.042615 | 0.070773 | 0.21516 | -0.1525 | -0.26946 | 5.5262 | -115.4508 | 5.7002 | 5.6541 | 0.12792 | -115.4659 | -115.1961 | 5.4205 | -115.5283 | 5.7094 | 5.6474 | 0.22685 | -115.3839 | -115.7516 | 5.8383 | 5.8232 | 6.0929 | 5.6777 | -115.7629 | 5.7608 | 5.9052 | 5.5375 | 5.6766 | -115.8685
3185.8125 | 121.2204 | -6.0562 | 115.2191 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.0043036 | -0.014202 | 0.019157 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0059459 | 0.005626 | -0.016908 | -0.035879 | 0.14827 | 0.13773 | 0.40295 | -0.1409 | 0.02852 | -0.013377 | -0.038036 | 0.066194 | 0.21516 | -0.14792 | -0.27862 | 5.9153 | -115.0708 | 6.0618 | 6.0203 | 0.10502 | -115.0814 | -114.8162 | 5.7776 | -115.1529 | 6.0847 | 6.0182 | 0.24058 | -115.004 | -115.367 | 6.2045 | 6.1939 | 6.4592 | 6.0393 | -115.36 | 6.1224 | 6.2714 | 5.9083 | 6.0428 | -115.4977
3187.5781 | 121.3257 | -6.5826 | 114.5874 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.0043036 | -0.013989 | 0.019157 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016327 | 0.039201 | 0.0057323 | 0.010204 | -0.007751 | -0.045036 | 0.15285 | 0.13773 | 0.39837 | -0.16837 | 0.02852 | -0.017956 | -0.047194 | 0.070773 | 0.21059 | -0.1525 | -0.27862 | 6.4143 | -114.4346 | 6.5928 | 6.5376 | 0.12334 | -114.4497 | -114.189 | 6.304 | -114.5166 | 6.6112 | 6.5354 | 0.23142 | -114.3768 | -114.7399 | 6.7355 | 6.7204 | 6.981 | 6.5749 | -114.7558 | 6.6534 | 6.7932 | 6.4301 | 6.5647 | -114.866
3189.2812 | 121.3074 | -5.1865 | 116.1301 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.0043036 | -0.013989 | 0.019157 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016968 | 0.039414 | 0.0059459 | 0.010204 | -0.012329 | -0.040457 | 0.15285 | 0.12399 | 0.40295 | -0.17295 | 0.023941 | -0.013377 | -0.038036 | 0.066194 | 0.21516 | -0.1525 | -0.27404 | 5.0135 | -115.9772 | 5.1967 | 5.146 | 0.13249 | -116.0061 | -115.7271 | 4.9124 | -116.0639 | 5.2104 | 5.1484 | 0.236 | -115.9149 | -116.2826 | 5.3393 | 5.3105 | 5.5894 | 5.1741 | -116.303 | 5.2527 | 5.4016 | 5.034 | 5.1731 | -116.4041
3191.0312 | 121.3303 | -7.4341 | 114.2303 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.00409 | -0.01463 | 0.019157 | -0.014956 | -0.0031575 | 0.0044868 | 0.016541 | 0.039201 | 0.0061595 | 0.005626 | -0.007751 | -0.035879 | 0.15285 | 0.12857 | 0.40295 | -0.1409 | 0.023941 | -0.017956 | -0.042615 | 0.061616 | 0.21059 | -0.1525 | -0.27862 | 7.2932 | -114.0775 | 7.4397 | 7.3982 | 0.10502 | -114.1018 | -113.8274 | 7.1555 | -114.1687 | 7.458 | 7.3915 | 0.236 | -114.0198 | -114.3828 | 7.5869 | 7.5627 | 7.837 | 7.4263 | -114.3712 | 7.4957 | 7.6447 | 7.2816 | 7.4161 | -114.509
3192.7188 | 121.431 | -5.864 | 115.4892 | 1.4211e-13 | -0.025995 | 0.00071164 | 0.0045172 | -0.014202 | 0.019157 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016327 | 0.039414 | 0.0057323 | 0.010204 | -0.016908 | -0.031301 | 0.14827 | 0.13315 | 0.40295 | -0.15921 | 0.023941 | -0.00422 | -0.042615 | 0.066194 | 0.21516 | -0.1525 | -0.2832 | 5.7047 | -115.3409 | 5.8742 | 5.8327 | 0.12791 | -115.356 | -115.0863 | 5.5808 | -115.423 | 5.8879 | 5.8213 | 0.24058 | -115.274 | -115.6417 | 6.0122 | 5.9971 | 6.2669 | 5.847 | -115.6484 | 5.9301 | 6.0791 | 5.7115 | 5.8597 | -115.7724
3194.4844 | 121.4264 | -4.921 | 116.4368 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.0038762 | -0.014202 | 0.019157 | -0.014956 | -0.0035849 | 0.0044868 | 0.016327 | 0.039414 | 0.0057323 | 0.005626 | -0.012329 | -0.035879 | 0.14369 | 0.12857 | 0.39837 | -0.15006 | 0.023941 | -0.013377 | -0.042615 | 0.070773 | 0.21516 | -0.1525 | -0.27404 | 4.7709 | -116.2931 | 4.9266 | 4.8851 | 0.11418 | -116.3082 | -116.0384 | 4.6469 | -116.366 | 4.9449 | 4.8783 | 0.23142 | -116.2216 | -116.5893 | 5.0647 | 5.0495 | 5.3193 | 4.9086 | -116.5868 | 4.9917 | 5.1361 | 4.7685 | 4.9076 | -116.7108
3196.1719 | 121.4722 | -5.0262 | 116.2766 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.00409 | -0.014416 | 0.019157 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016327 | 0.039201 | 0.0059459 | 0.010204 | -0.016908 | -0.035879 | 0.14369 | 0.12857 | 0.39837 | -0.15464 | 0.02852 | -0.013377 | -0.047194 | 0.070773 | 0.21974 | -0.1525 | -0.27404 | 4.8716 | -116.1329 | 5.0364 | 4.9904 | 0.11876 | -116.148 | -115.8782 | 4.7522 | -116.2058 | 5.0548 | 4.9791 | 0.22685 | -116.0568 | -116.4291 | 5.1699 | 5.1548 | 5.4246 | 5.0093 | -116.4312 | 5.097 | 5.246 | 4.8737 | 5.0129 | -116.5506
3197.9219 | 121.376 | -5.5847 | 115.8325 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.00409 | -0.013989 | 0.019157 | 0.0079357 | -0.0035849 | 0.0047004 | 0.016327 | 0.039414 | 0.0057323 | 0.014783 | -0.016908 | -0.035879 | 0.13912 | 0.11941 | 0.40295 | -0.14548 | 0.023941 | -0.008798 | -0.047194 | 0.070773 | 0.20601 | -0.15708 | -0.27862 | 5.4392 | -115.6934 | 5.5995 | 5.5488 | 0.1096 | -115.7131 | -115.4296 | 5.3061 | -115.7617 | 5.6087 | 5.5375 | 0.23142 | -115.6265 | -115.9896 | 5.7238 | 5.7041 | 5.9877 | 5.5678 | -115.978 | 5.6555 | 5.7907 | 5.4276 | 5.5759 | -116.1111
3199.6875 | 115.8096 | -62.5854 | 53.6957 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0038762 | -0.013989 | 0.018089 | 0.015566 | -0.0033713 | 0.0040594 | 0.016113 | 0.038987 | 0.0059459 | 0.019361 | 0.001407 | -0.022144 | 0.17117 | 0.15604 | 0.40753 | -0.12258 | 0.033099 | -0.00422 | -0.033458 | 0.07993 | 0.23348 | -0.14792 | -0.2603 | 62.4629 | -53.5245 | 62.6048 | 62.5633 | 0.10044 | -53.5396 | -53.2882 | 62.3251 | -53.6157 | 62.6185 | 62.552 | 0.22685 | -53.4622 | -53.8436 | 62.7566 | 62.7415 | 62.993 | 62.5869 | -53.8183 | 62.6654 | 62.8189 | 62.4375 | 62.5812 | -53.956
3201.375 | 117.0731 | -7.988 | 109.9182 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.00409 | -0.014202 | 0.019157 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016541 | 0.039414 | 0.0057323 | 0.005626 | -0.012329 | -0.031301 | 0.15285 | 0.13773 | 0.39837 | -0.1409 | 0.02852 | -0.008798 | -0.047194 | 0.070773 | 0.21516 | -0.15708 | -0.26946 | 7.8471 | -109.7654 | 7.9936 | 7.9567 | 0.1096 | -109.7805 | -109.5198 | 7.7185 | -109.8474 | 8.0165 | 7.9408 | 0.22227 | -109.703 | -110.0753 | 8.1408 | 8.1257 | 8.3863 | 7.9756 | -110.0591 | 8.0587 | 8.2031 | 7.8309 | 7.9792 | -110.1877
3203.1406 | 120.401 | -4.6051 | 115.6265 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.00409 | -0.014202 | 0.019157 | 0.00030522 | -0.0035849 | 0.0044868 | 0.016327 | 0.039414 | 0.0055187 | 0.010204 | -0.016908 | -0.031301 | 0.14369 | 0.11941 | 0.39837 | -0.12258 | 0.023941 | -0.008798 | -0.042615 | 0.075351 | 0.21516 | -0.15708 | -0.2832 | 4.4825 | -115.4828 | 4.6153 | 4.5738 | 0.091282 | -115.5071 | -115.2282 | 4.3219 | -115.5512 | 4.629 | 4.5625 | 0.24058 | -115.4114 | -115.7836 | 4.7488 | 4.7245 | 5.0035 | 4.5882 | -115.7491 | 4.6805 | 4.8203 | 4.448 | 4.5963 | -115.9097
3204.8906 | 120.5109 | -4.0192 | 116.5375 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.00409 | -0.014416 | 0.018943 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016754 | 0.039201 | 0.0055187 | 0.005626 | -0.007751 | -0.035879 | 0.14827 | 0.11941 | 0.39837 | -0.14548 | 0.019362 | -0.008798 | -0.042615 | 0.061616 | 0.21059 | -0.1525 | -0.2832 | 3.8737 | -116.3892 | 4.0248 | 3.9833 | 0.1096 | -116.4181 | -116.1391 | 3.736 | -116.4759 | 4.0385 | 3.9766 | 0.24058 | -116.3269 | -116.69 | 4.1674 | 4.1386 | 4.4175 | 4.0114 | -116.683 | 4.0808 | 4.2298 | 3.8667 | 4.0104 | -116.8207
3206.6406 | 106.4804 | -3.5797 | 116.4642 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0043036 | -0.01463 | 0.01873 | 0.00030522 | -0.0031575 | 0.0038458 | 0.016968 | 0.039628 | 0.0059459 | 0.005626 | -0.003172 | -0.040457 | 0.14827 | 0.11941 | 0.39837 | -0.16379 | 0.02852 | -0.00422 | -0.047194 | 0.075351 | 0.21059 | -0.1525 | -0.27862 | 3.4159 | -116.316 | 3.5853 | 3.5393 | 0.12334 | -116.3448 | -116.0659 | 3.3011 | -116.3889 | 3.6082 | 3.5325 | 0.23142 | -116.2536 | -116.6167 | 3.728 | 3.6991 | 3.9781 | 3.5765 | -116.628 | 3.6551 | 3.7903 | 3.4272 | 3.5755 | -116.7429
3208.3438 | 93.5989 | -3.5202 | 99.7284 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.0043036 | -0.014202 | 0.018943 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016327 | 0.039201 | 0.0057323 | 0.001048 | -0.016908 | -0.040457 | 0.14369 | 0.11483 | 0.39379 | -0.16379 | 0.02852 | -0.013377 | -0.038036 | 0.070773 | 0.21974 | -0.1525 | -0.26946 | 3.3564 | -99.5847 | 3.5213 | 3.4797 | 0.12334 | -99.6136 | -99.3346 | 3.2507 | -99.6576 | 3.5487 | 3.4822 | 0.23143 | -99.5086 | -99.8809 | 3.6639 | 3.635 | 3.914 | 3.5033 | -99.8922 | 3.591 | 3.7399 | 3.3677 | 3.5068 | -99.9979
3210.0938 | 120.8679 | -3.566 | 117.2791 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0045172 | -0.014416 | 0.01873 | -0.0073253 | -0.0031575 | 0.0044868 | 0.016327 | 0.039201 | 0.0059459 | 0.001048 | -0.012329 | -0.031301 | 0.13912 | 0.12399 | 0.38921 | -0.1409 | 0.023941 | -0.013377 | -0.038036 | 0.070773 | 0.21974 | -0.15708 | -0.27404 | 3.4251 | -117.1399 | 3.567 | 3.5347 | 0.1096 | -117.1551 | -116.8898 | 3.2919 | -117.2083 | 3.5899 | 3.5279 | 0.236 | -117.0593 | -117.4361 | 3.7051 | 3.69 | 3.9552 | 3.5537 | -117.42 | 3.6368 | 3.7857 | 3.4089 | 3.5526 | -117.5531
3211.8438 | 120.9045 | -3.6667 | 117.2882 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.013989 | 0.018943 | 0.00030522 | -0.0033713 | 0.0047004 | 0.016541 | 0.039414 | 0.0055187 | 0.001048 | -0.016908 | -0.035879 | 0.13912 | 0.12399 | 0.39379 | -0.16379 | 0.02852 | -0.008798 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.27404 | 3.5029 | -117.1491 | 3.6677 | 3.6308 | 0.12792 | -117.1642 | -116.8944 | 3.3926 | -117.2174 | 3.6952 | 3.6241 | 0.23142 | -117.0822 | -117.4407 | 3.8058 | 3.7907 | 4.0605 | 3.6498 | -117.452 | 3.7375 | 3.8727 | 3.5142 | 3.6579 | -117.5622
3213.5938 | 104.6448 | -3.7399 | 116.8167 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0038762 | -0.014202 | 0.018943 | 0.00030522 | -0.0035849 | 0.0040594 | 0.016541 | 0.039628 | 0.0061595 | 0.001048 | -0.016908 | -0.035879 | 0.14369 | 0.11941 | 0.39837 | -0.15006 | 0.02852 | -0.013377 | -0.047194 | 0.061616 | 0.21059 | -0.14792 | -0.27862 | 3.5899 | -116.673 | 3.741 | 3.7041 | 0.11418 | -116.6973 | -116.4183 | 3.4613 | -116.7551 | 3.7684 | 3.6927 | 0.23142 | -116.6061 | -116.9646 | 3.8836 | 3.8593 | 4.1383 | 3.723 | -116.9668 | 3.8015 | 3.9505 | 3.592 | 3.7266 | -117.0953
3215.2812 | 109.8816 | -3.9459 | 116.8671 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.00409 | -0.014202 | 0.018943 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016541 | 0.038987 | 0.0061595 | 0.005626 | -0.003172 | -0.031301 | 0.14827 | 0.12399 | 0.39837 | -0.15464 | 0.02852 | -0.013377 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.27862 | 3.7913 | -116.7188 | 3.9515 | 3.9146 | 0.12334 | -116.7431 | -116.4687 | 3.6673 | -116.8009 | 3.9744 | 3.9033 | 0.236 | -116.6611 | -117.0196 | 4.0942 | 4.0699 | 4.3443 | 3.9428 | -117.0217 | 4.0121 | 4.1519 | 3.7934 | 3.9325 | -117.1457
3217.0312 | 121.2341 | -4.0604 | 116.8625 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.0036626 | -0.014416 | 0.018943 | 0.015566 | -0.0031575 | 0.0047004 | 0.016754 | 0.039414 | 0.0055187 | 0.005626 | -0.012329 | -0.031301 | 0.14369 | 0.12399 | 0.39379 | -0.15464 | 0.02852 | -0.00422 | -0.042615 | 0.070773 | 0.20601 | -0.14792 | -0.2832 | 3.9057 | -116.7188 | 4.066 | 4.0291 | 0.12334 | -116.7385 | -116.4687 | 3.7772 | -116.7917 | 4.0889 | 4.0177 | 0.24058 | -116.6565 | -117.0104 | 4.2041 | 4.1844 | 4.4542 | 4.048 | -117.0171 | 4.1311 | 4.2664 | 3.9124 | 4.0561 | -117.1457
3218.7188 | 121.2479 | -4.0924 | 116.6794 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.0038762 | -0.01463 | 0.01873 | 0.015566 | -0.0031575 | 0.0044868 | 0.016541 | 0.039414 | 0.0057323 | 0.005626 | -0.016908 | -0.035879 | 0.14827 | 0.13773 | 0.40295 | -0.16837 | 0.023941 | -0.00422 | -0.051772 | 0.070773 | 0.20601 | -0.1525 | -0.2832 | 3.924 | -116.5311 | 4.098 | 4.0565 | 0.13249 | -116.5417 | -116.2764 | 3.8092 | -116.6086 | 4.1163 | 4.0406 | 0.23143 | -116.4734 | -116.8319 | 4.2407 | 4.2301 | 4.4954 | 4.0755 | -116.8478 | 4.1632 | 4.2984 | 3.9399 | 4.0882 | -116.9626
3220.4844 | 121.2524 | -4.0466 | 116.9403 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.00409 | -0.014416 | 0.019157 | -0.0073253 | -0.0040121 | 0.0042732 | 0.016327 | 0.039628 | 0.0059459 | -0.003531 | -0.016908 | -0.031301 | 0.14369 | 0.11483 | 0.38921 | -0.15464 | 0.023941 | -0.00422 | -0.042615 | 0.061616 | 0.21974 | -0.1525 | -0.27862 | 3.892 | -116.7966 | 4.0431 | 4.0153 | 0.12334 | -116.8255 | -116.5511 | 3.768 | -116.8787 | 4.0706 | 4.004 | 0.236 | -116.7206 | -117.0928 | 4.1903 | 4.1615 | 4.4358 | 4.0297 | -117.0949 | 4.1082 | 4.2664 | 3.8941 | 4.0424 | -117.2189
3222.1719 | 121.0831 | -4.1153 | 116.5878 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0045172 | -0.013989 | 0.018943 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.039414 | 0.0057323 | 0.010204 | -0.012329 | -0.035879 | 0.14369 | 0.12399 | 0.39837 | -0.1409 | 0.02852 | -0.013377 | -0.038036 | 0.066194 | 0.21516 | -0.1525 | -0.27862 | 3.9744 | -116.4441 | 4.1255 | 4.0794 | 0.10502 | -116.4638 | -116.1895 | 3.8367 | -116.5216 | 4.1438 | 4.0773 | 0.24058 | -116.3727 | -116.7403 | 4.259 | 4.2393 | 4.5137 | 4.103 | -116.7287 | 4.1815 | 4.3305 | 3.9628 | 4.1019 | -116.8664
3223.9375 | 121.257 | -4.097 | 116.9495 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.00409 | -0.013989 | 0.018943 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016541 | 0.039628 | 0.0061595 | 0.005626 | -0.007751 | -0.031301 | 0.15285 | 0.14231 | 0.39837 | -0.15921 | 0.023941 | -0.013377 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.27862 | 3.9378 | -116.7966 | 4.1026 | 4.0657 | 0.12791 | -116.8072 | -116.5511 | 3.8184 | -116.8833 | 4.1209 | 4.0544 | 0.236 | -116.7389 | -117.102 | 4.2498 | 4.2393 | 4.4954 | 4.0892 | -117.1087 | 4.1632 | 4.3076 | 3.9445 | 4.0836 | -117.2281
3225.6875 | 121.257 | -4.1336 | 117.0685 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0043036 | -0.014416 | 0.018943 | -0.0073253 | -0.0035849 | 0.0042732 | 0.016327 | 0.039628 | 0.0057323 | 0.005626 | -0.007751 | -0.035879 | 0.13912 | 0.14231 | 0.39379 | -0.15464 | 0.02852 | -0.00422 | -0.042615 | 0.066194 | 0.21059 | -0.1525 | -0.2832 | 3.979 | -116.9294 | 4.1392 | 4.0977 | 0.11876 | -116.9262 | -116.6747 | 3.8504 | -117.0023 | 4.1621 | 4.091 | 0.24058 | -116.8579 | -117.221 | 4.2727 | 4.2759 | 4.5274 | 4.1259 | -117.2231 | 4.1998 | 4.3442 | 3.9811 | 4.1294 | -117.3517
3227.375 | 121.3577 | -4.1519 | 117.0273 | 1.4211e-13 | -0.025995 | 7.0442e-05 | 0.0045172 | -0.014416 | 0.019157 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0055187 | 0.010204 | -0.007751 | -0.035879 | 0.14827 | 0.11941 | 0.39837 | -0.13174 | 0.023941 | -0.00422 | -0.033458 | 0.066194 | 0.21059 | -0.15708 | -0.2832 | 4.0202 | -116.879 | 4.1621 | 4.116 | 0.095862 | -116.9079 | -116.6289 | 3.8687 | -116.9611 | 4.1759 | 4.1185 | 0.24974 | -116.8167 | -117.1844 | 4.3002 | 4.2713 | 4.5503 | 4.1442 | -117.159 | 4.2181 | 4.3625 | 3.9948 | 4.1477 | -117.3105
3229.125 | 120.607 | -4.2984 | 116.9724 | 1.4211e-13 | -0.025782 | 0.00028424 | 0.00409 | -0.014416 | 0.019371 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016541 | 0.039201 | 0.0057323 | 0.005626 | -0.012329 | -0.031301 | 0.14369 | 0.12399 | 0.39379 | -0.16379 | 0.023941 | -0.00422 | -0.042615 | 0.070773 | 0.20601 | -0.15708 | -0.27862 | 4.1346 | -116.8287 | 4.304 | 4.2671 | 0.13249 | -116.8484 | -116.5786 | 4.0198 | -116.9016 | 4.3223 | 4.2558 | 0.236 | -116.7663 | -117.1294 | 4.4421 | 4.4224 | 4.6922 | 4.2861 | -117.1361 | 4.3692 | 4.5044 | 4.1413 | 4.2942 | -117.251
3230.875 | 121.3394 | -4.2938 | 116.9403 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.014202 | 0.019371 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016754 | 0.039201 | 0.0055187 | 0.010204 | -0.012329 | -0.026723 | 0.15743 | 0.13315 | 0.39837 | -0.16837 | 0.033099 | -0.008798 | -0.047194 | 0.070773 | 0.20143 | -0.1525 | -0.27862 | 4.1254 | -116.7829 | 4.304 | 4.2671 | 0.14165 | -116.8072 | -116.5419 | 4.0152 | -116.8695 | 4.3269 | 4.2466 | 0.23142 | -116.7389 | -117.0928 | 4.4513 | 4.427 | 4.6922 | 4.2815 | -117.1087 | 4.3646 | 4.4953 | 4.1413 | 4.285 | -117.2189
3232.5781 | 121.3531 | -4.4449 | 116.8121 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.00409 | -0.01463 | 0.018943 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016327 | 0.039414 | 0.0057323 | 0.005626 | -0.012329 | -0.031301 | 0.14369 | 0.12857 | 0.39837 | -0.16837 | 0.033099 | -0.013377 | -0.047194 | 0.070773 | 0.21059 | -0.1525 | -0.27862 | 4.2765 | -116.6684 | 4.4505 | 4.4136 | 0.13707 | -116.6836 | -116.4138 | 4.1663 | -116.7414 | 4.478 | 4.3977 | 0.23142 | -116.6015 | -116.9646 | 4.5886 | 4.5735 | 4.8433 | 4.4326 | -116.9805 | 4.5157 | 4.6555 | 4.2924 | 4.4315 | -117.0908
3234.3438 | 121.312 | -4.4678 | 116.8213 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.004731 | -0.014416 | 0.019371 | 0.015566 | -0.0031575 | 0.0042732 | 0.016541 | 0.039201 | 0.0057323 | -0.003531 | -0.012329 | -0.031301 | 0.14827 | 0.12399 | 0.39837 | -0.15921 | 0.02852 | -0.008798 | -0.042615 | 0.075351 | 0.20601 | -0.14792 | -0.2832 | 4.3086 | -116.673 | 4.4642 | 4.4365 | 0.12791 | -116.6973 | -116.4229 | 4.1846 | -116.7459 | 4.4963 | 4.4252 | 0.24058 | -116.6153 | -116.9692 | 4.616 | 4.5918 | 4.8661 | 4.4554 | -116.9805 | 4.5431 | 4.6738 | 4.3199 | 4.459 | -117.1045
3236.0312 | 120.8084 | -4.4952 | 116.8762 | 1.4211e-13 | -0.025995 | 0.00028424 | 0.0043036 | -0.014416 | 0.018943 | -0.0073253 | -0.0033713 | 0.0042732 | 0.016754 | 0.039201 | 0.0059459 | 0.001048 | -0.012329 | -0.035879 | 0.14827 | 0.12857 | 0.39379 | -0.15006 | 0.02852 | -0.017956 | -0.042615 | 0.070773 | 0.20143 | -0.1525 | -0.27862 | 4.3452 | -116.7279 | 4.4963 | 4.4594 | 0.11418 | -116.7477 | -116.4824 | 4.2166 | -116.8054 | 4.5238 | 4.4526 | 0.236 | -116.6748 | -117.0287 | 4.6435 | 4.6238 | 4.889 | 4.4829 | -117.0263 | 4.566 | 4.6967 | 4.3427 | 4.4773 | -117.1548
3237.7812 | 120.9732 | -4.4724 | 116.922 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.00409 | -0.013989 | 0.019157 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016327 | 0.039414 | 0.0059459 | 0.005626 | -0.007751 | -0.031301 | 0.14827 | 0.12399 | 0.39837 | -0.14548 | 0.019362 | -0.017956 | -0.042615 | 0.07993 | 0.21059 | -0.14792 | -0.27404 | 4.3269 | -116.7737 | 4.478 | 4.441 | 0.11418 | -116.798 | -116.5236 | 4.1983 | -116.8421 | 4.4917 | 4.4297 | 0.23142 | -116.7114 | -117.0699 | 4.6206 | 4.5963 | 4.8707 | 4.4646 | -117.0675 | 4.5523 | 4.6829 | 4.3244 | 4.4544 | -117.196
3239.4844 | 121.3943 | -4.3945 | 116.8671 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.014202 | 0.019371 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016541 | 0.039842 | 0.0059459 | 0.010204 | -0.016908 | -0.040457 | 0.14369 | 0.11941 | 0.39837 | -0.15921 | 0.023941 | -0.008798 | -0.042615 | 0.066194 | 0.20601 | -0.1525 | -0.27862 | 4.2353 | -116.7234 | 4.4047 | 4.3541 | 0.11876 | -116.7477 | -116.4687 | 4.1159 | -116.8009 | 4.4185 | 4.3519 | 0.236 | -116.6611 | -117.0196 | 4.5382 | 4.5139 | 4.7929 | 4.3776 | -117.0263 | 4.4607 | 4.6005 | 4.242 | 4.3857 | -117.1457
3241.25 | 121.3852 | -4.5364 | 116.8167 | 1.4211e-13 | -0.026423 | -0.00014316 | 0.0038762 | -0.014416 | 0.019584 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016754 | 0.039201 | 0.0057323 | 0.001048 | -0.012329 | -0.035879 | 0.15285 | 0.11483 | 0.39379 | -0.16837 | 0.033099 | -0.00422 | -0.042615 | 0.066194 | 0.21516 | -0.15708 | -0.26946 | 4.3681 | -116.6639 | 4.5375 | 4.5006 | 0.13249 | -116.7019 | -116.4229 | 4.267 | -116.7505 | 4.5695 | 4.4938 | 0.22685 | -116.6015 | -116.9738 | 4.6893 | 4.6513 | 4.9302 | 4.5241 | -116.9851 | 4.6026 | 4.7516 | 4.3794 | 4.5322 | -117.0862
3243.0625 | 121.4539 | -4.4174 | 116.922 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.014416 | 0.01873 | 0.015566 | -0.0031575 | 0.0042732 | 0.016541 | 0.039201 | 0.0055187 | 0.001048 | -0.007751 | -0.031301 | 0.14827 | 0.12399 | 0.39379 | -0.11342 | 0.02852 | 0.000359 | -0.051772 | 0.070773 | 0.21059 | -0.14792 | -0.28778 | 4.304 | -116.7737 | 4.4185 | 4.3861 | 0.082124 | -116.798 | -116.5282 | 4.1296 | -116.8512 | 4.4459 | 4.3656 | 0.23601 | -116.7114 | -117.0699 | 4.5657 | 4.5414 | 4.8112 | 4.4097 | -117.0354 | 4.4882 | 4.628 | 4.2695 | 4.4178 | -117.2098
3244.8125 | 121.3715 | -4.6509 | 116.716 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.0043036 | -0.014416 | 0.018943 | 0.015566 | -0.0035849 | 0.0044868 | 0.016113 | 0.039414 | 0.0057323 | 0.001048 | -0.012329 | -0.031301 | 0.15285 | 0.11483 | 0.39837 | -0.15921 | 0.019362 | -0.013377 | -0.047194 | 0.075351 | 0.20143 | -0.1525 | -0.2832 | 4.4917 | -116.5632 | 4.6519 | 4.6196 | 0.12791 | -116.6012 | -116.3176 | 4.3677 | -116.6407 | 4.6702 | 4.6037 | 0.236 | -116.5146 | -116.8685 | 4.8037 | 4.7657 | 5.0492 | 4.6385 | -116.8752 | 4.7262 | 4.8523 | 4.4984 | 4.6375 | -116.9992
3246.5625 | 121.3211 | -4.7195 | 116.6702 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.0043036 | -0.014202 | 0.019371 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016327 | 0.039414 | 0.0057323 | 0.010204 | -0.007751 | -0.031301 | 0.15285 | 0.11941 | 0.39837 | -0.15006 | 0.02852 | -0.00422 | -0.047194 | 0.07993 | 0.21059 | -0.1525 | -0.27862 | 4.5695 | -116.5174 | 4.7297 | 4.6882 | 0.11876 | -116.5508 | -116.2719 | 4.4409 | -116.5903 | 4.7481 | 4.6723 | 0.23142 | -116.4596 | -116.8227 | 4.8724 | 4.839 | 5.1179 | 4.7118 | -116.8203 | 4.7995 | 4.9301 | 4.567 | 4.7153 | -116.9488
3248.3125 | 121.3989 | -5.3055 | 116.0797 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0038762 | -0.014416 | 0.018943 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016754 | 0.039201 | 0.0059459 | 0.005626 | -0.007751 | -0.035879 | 0.14827 | 0.11025 | 0.39837 | -0.16379 | 0.02852 | -0.008798 | -0.042615 | 0.070773 | 0.21974 | -0.1525 | -0.2832 | 5.1417 | -115.9314 | 5.3111 | 5.2696 | 0.12792 | -115.9695 | -115.6813 | 5.0223 | -116.0089 | 5.334 | 5.2629 | 0.24058 | -115.86 | -116.2322 | 5.4538 | 5.4157 | 5.7038 | 5.2977 | -116.2435 | 5.3763 | 5.5252 | 5.153 | 5.2967 | -116.3629
3250.0156 | 121.3989 | -2.9892 | 118.4189 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.00409 | -0.014416 | 0.019584 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016113 | 0.039414 | 0.0057323 | 0.014783 | -0.012329 | -0.035879 | 0.14827 | 0.11941 | 0.39379 | -0.1409 | 0.023941 | -0.008798 | -0.042615 | 0.070773 | 0.20601 | -0.1525 | -0.2832 | 2.8483 | -118.2706 | 3.004 | 2.9533 | 0.10502 | -118.2995 | -118.0251 | 2.706 | -118.3481 | 3.0131 | 2.9466 | 0.24058 | -118.2129 | -118.5714 | 3.1375 | 3.1086 | 3.383 | 2.9769 | -118.5598 | 3.06 | 3.1952 | 2.8367 | 2.9804 | -118.7021
3251.7031 | 121.3989 | -5.1773 | 116.0889 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.0043036 | -0.014416 | 0.018943 | 0.0079357 | -0.0035849 | 0.0044868 | 0.016541 | 0.039414 | 0.0055187 | 0.014783 | -0.007751 | -0.040457 | 0.14369 | 0.12857 | 0.38463 | -0.15921 | 0.02852 | -0.00422 | -0.042615 | 0.061616 | 0.21974 | -0.1525 | -0.27862 | 5.0181 | -115.9452 | 5.1921 | 5.1368 | 0.11876 | -115.9603 | -115.7042 | 4.8987 | -116.0273 | 5.2058 | 5.1347 | 0.236 | -115.8691 | -116.2414 | 5.321 | 5.3059 | 5.5619 | 5.1696 | -116.2481 | 5.2389 | 5.3971 | 5.0248 | 5.1731 | -116.3675
3253.4531 | 121.4081 | -4.9072 | 116.4825 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.00409 | -0.014416 | 0.01873 | 0.00030522 | -0.0031575 | 0.0044868 | 0.016541 | 0.039414 | 0.0059459 | 0.001048 | -0.007751 | -0.040457 | 0.14369 | 0.11483 | 0.39379 | -0.10427 | 0.023941 | -0.013377 | -0.051772 | 0.075351 | 0.20601 | -0.15708 | -0.27404 | 4.803 | -116.3388 | 4.9083 | 4.8668 | 0.063811 | -116.3677 | -116.0888 | 4.6332 | -116.4072 | 4.9312 | 4.8555 | 0.22227 | -116.2765 | -116.6396 | 5.0509 | 5.0221 | 5.301 | 4.8995 | -116.5868 | 4.9826 | 5.1132 | 4.7501 | 4.8938 | -116.7566
3255.2188 | 121.3531 | -2.3529 | 119.1193 | 1.4211e-13 | -0.025782 | 0.00049784 | 0.0038762 | -0.014202 | 0.01873 | 0.015566 | -0.0033713 | 0.0044868 | 0.016541 | 0.039414 | 0.0057323 | 0.010204 | -0.016908 | -0.040457 | 0.14369 | 0.11941 | 0.39379 | -0.17753 | 0.033099 | -0.013377 | -0.038036 | 0.070773 | 0.21059 | -0.1525 | -0.27862 | 2.1754 | -118.9756 | 2.3631 | 2.3124 | 0.13707 | -118.9999 | -118.7255 | 2.0743 | -119.0485 | 2.386 | 2.3149 | 0.24058 | -118.9087 | -119.2718 | 2.4966 | 2.4723 | 2.7467 | 2.336 | -119.2968 | 2.4237 | 2.5635 | 2.2004 | 2.3395 | -119.3979
3256.9062 | 121.3531 | -2.2751 | 119.2245 | 1.4211e-13 | -0.025782 | 7.0442e-05 | 0.0043036 | -0.01463 | 0.019157 | 0.015566 | -0.0035849 | 0.0044868 | 0.016541 | 0.039414 | 0.0061595 | 0.001048 | -0.016908 | -0.035879 | 0.14369 | 0.11941 | 0.39379 | -0.15921 | 0.019362 | -0.008798 | -0.042615 | 0.075351 | 0.20601 | -0.1525 | -0.26946 | 2.1159 | -119.0809 | 2.2761 | 2.2392 | 0.12334 | -119.1051 | -118.8308 | 2.0056 | -119.1492 | 2.2944 | 2.2325 | 0.22685 | -119.0185 | -119.377 | 2.4188 | 2.3945 | 2.6689 | 2.2582 | -119.3838 | 2.3504 | 2.4811 | 2.1226 | 2.2663 | -119.494
3258.6094 | 121.5271 | -2.3209 | 119.101 | 1.4211e-13 | -0.025995 | 0.00049784 | 0.00409 | -0.014416 | 0.018943 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0059459 | 0.005626 | -0.012329 | -0.040457 | 0.14369 | 0.13315 | 0.39837 | -0.11342 | 0.023941 | -0.00422 | -0.042615 | 0.066194 | 0.21059 | -0.15708 | -0.27404 | 2.2074 | -118.9573 | 2.3265 | 2.2804 | 0.072968 | -118.9678 | -118.7026 | 2.0468 | -119.0348 | 2.3448 | 2.2782 | 0.23142 | -118.8904 | -119.258 | 2.4646 | 2.454 | 2.7192 | 2.3085 | -119.2144 | 2.3871 | 2.5314 | 2.1638 | 2.3166 | -119.375
3260.375 | 121.5088 | -1.9501 | 119.4626 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.0045172 | -0.013989 | 0.018943 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016754 | 0.039628 | 0.0059459 | 0.005626 | -0.012329 | -0.040457 | 0.14827 | 0.12857 | 0.39837 | -0.16379 | 0.02852 | -0.008798 | -0.042615 | 0.061616 | 0.21516 | -0.15708 | -0.27862 | 1.7863 | -119.3143 | 1.9557 | 1.9096 | 0.12334 | -119.334 | -119.0642 | 1.6715 | -119.401 | 1.9786 | 1.9075 | 0.236 | -119.2474 | -119.6197 | 2.0983 | 2.0786 | 2.3484 | 1.9377 | -119.6264 | 2.0117 | 2.1652 | 1.793 | 1.9413 | -119.7412
3262.0625 | 121.4081 | -2.2339 | 119.0002 | 1.4211e-13 | -0.026209 | 0.00071164 | 0.00409 | -0.013989 | 0.019157 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016541 | 0.039201 | 0.0057323 | 0.005626 | -0.007751 | -0.031301 | 0.14369 | 0.13315 | 0.38921 | -0.17295 | 0.02852 | -0.00422 | -0.038036 | 0.066194 | 0.21059 | -0.1525 | -0.27862 | 2.0609 | -118.8565 | 2.2395 | 2.2026 | 0.14165 | -118.8671 | -118.611 | 1.9553 | -118.934 | 2.2624 | 2.1959 | 0.24058 | -118.7897 | -119.1527 | 2.3776 | 2.367 | 2.6231 | 2.2261 | -119.1732 | 2.3001 | 2.4445 | 2.0814 | 2.2297 | -119.2789
3263.75 | 121.6827 | -1.6983 | 119.7189 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.0038762 | -0.014416 | 0.019371 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016541 | 0.039201 | 0.0055187 | 0.010204 | -0.016908 | -0.031301 | 0.15285 | 0.12399 | 0.39837 | -0.16837 | 0.02852 | -0.008798 | -0.047194 | 0.066194 | 0.21516 | -0.15708 | -0.27404 | 1.5299 | -119.5661 | 1.7085 | 1.667 | 0.13707 | -119.5949 | -119.3206 | 1.4243 | -119.6527 | 1.7268 | 1.6511 | 0.22685 | -119.5038 | -119.876 | 1.8512 | 1.8223 | 2.0967 | 1.6814 | -119.8873 | 1.7645 | 1.9135 | 1.5412 | 1.6895 | -119.993
3265.5 | 121.5271 | -1.5198 | 119.9478 | 1.4211e-13 | -0.026209 | 0.00028424 | 0.0038762 | -0.014416 | 0.018943 | 0.0079357 | -0.0031575 | 0.0040594 | 0.016541 | 0.039628 | 0.0059459 | 0.001048 | -0.016908 | -0.035879 | 0.14369 | 0.12399 | 0.39837 | -0.17295 | 0.033099 | -0.008798 | -0.047194 | 0.061616 | 0.21974 | -0.1525 | -0.27862 | 1.3468 | -119.8041 | 1.5208 | 1.4839 | 0.13707 | -119.8238 | -119.5494 | 1.2412 | -119.8862 | 1.5529 | 1.4726 | 0.23142 | -119.7281 | -120.1003 | 1.6635 | 1.6438 | 1.9181 | 1.5029 | -120.1208 | 1.5814 | 1.7395 | 1.3673 | 1.511 | -120.2264
3267.25 | 121.5317 | -1.7166 | 119.7327 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.0038762 | -0.014416 | 0.019584 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016754 | 0.039628 | 0.0057323 | 0.005626 | -0.016908 | -0.035879 | 0.14369 | 0.11483 | 0.39837 | -0.14548 | 0.023941 | -0.00422 | -0.047194 | 0.061616 | 0.21516 | -0.15708 | -0.2832 | 1.5711 | -119.589 | 1.7222 | 1.6807 | 0.1096 | -119.6178 | -119.3343 | 1.4334 | -119.671 | 1.7406 | 1.6694 | 0.236 | -119.5175 | -119.8897 | 1.8603 | 1.8314 | 2.115 | 1.6997 | -119.8781 | 1.7782 | 1.9318 | 1.5595 | 1.7124 | -120.0159
3268.9375 | 121.5408 | -1.5152 | 119.9295 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.0043036 | -0.014202 | 0.019157 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016327 | 0.039414 | 0.0057323 | 0.005626 | -0.007751 | -0.040457 | 0.14827 | 0.11483 | 0.38921 | -0.17753 | 0.023941 | -0.008798 | -0.042615 | 0.061616 | 0.21059 | -0.15708 | -0.2832 | 1.3377 | -119.7812 | 1.5208 | 1.4747 | 0.13707 | -119.8147 | -119.5403 | 1.232 | -119.8679 | 1.5391 | 1.4726 | 0.24058 | -119.7189 | -120.0866 | 1.6635 | 1.63 | 1.9044 | 1.5074 | -120.107 | 1.5768 | 1.7258 | 1.3581 | 1.5064 | -120.2127
3270.6875 | 121.5637 | -1.6022 | 119.9158 | 1.4211e-13 | -0.026209 | 0.00049784 | 0.0043036 | -0.014416 | 0.01873 | 0.0079357 | -0.0029439 | 0.0040594 | 0.016113 | 0.039628 | 0.0055187 | 0.001048 | -0.007751 | -0.040457 | 0.14369 | 0.13315 | 0.39837 | -0.15006 | 0.019362 | -0.008798 | -0.047194 | 0.066194 | 0.22432 | -0.15708 | -0.27862 | 1.4521 | -119.7721 | 1.6032 | 1.5617 | 0.1096 | -119.7826 | -119.5174 | 1.3236 | -119.8496 | 1.6215 | 1.555 | 0.23142 | -119.6914 | -120.0729 | 1.7459 | 1.7353 | 2.0005 | 1.5944 | -120.0658 | 1.6684 | 1.8265 | 1.4451 | 1.5934 | -120.1944
3272.3906 | 121.4355 | -1.3596 | 120.195 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.00409 | -0.014416 | 0.018943 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0057323 | 0.001048 | -0.012329 | -0.035879 | 0.13912 | 0.12399 | 0.39379 | -0.17295 | 0.019362 | -0.00422 | -0.042615 | 0.070773 | 0.20601 | -0.15708 | -0.27862 | 1.1866 | -120.0559 | 1.3606 | 1.3237 | 0.13707 | -120.071 | -119.8012 | 1.0809 | -120.1242 | 1.3789 | 1.3169 | 0.236 | -119.989 | -120.3521 | 1.4987 | 1.4835 | 1.7533 | 1.3472 | -120.368 | 1.4303 | 1.5656 | 1.2025 | 1.3553 | -120.4736
3274.1562 | 121.5225 | -1.4145 | 120.0943 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.00409 | -0.014416 | 0.019157 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016327 | 0.039414 | 0.0059459 | 0.001048 | -0.012329 | -0.031301 | 0.14827 | 0.12857 | 0.39379 | -0.1409 | 0.023941 | -0.00422 | -0.051772 | 0.070773 | 0.21516 | -0.15708 | -0.2832 | 1.2736 | -119.946 | 1.4155 | 1.3832 | 0.1096 | -119.9657 | -119.7005 | 1.1313 | -120.0235 | 1.4384 | 1.3627 | 0.23143 | -119.8791 | -120.2514 | 1.5628 | 1.5431 | 1.8083 | 1.4022 | -120.2352 | 1.4853 | 1.6297 | 1.2574 | 1.4103 | -120.3775
3275.8438 | 121.6278 | -1.3504 | 120.1538 | 1.4211e-13 | -0.026636 | 7.0442e-05 | 0.00409 | -0.014202 | 0.019157 | 0.00030522 | -0.0033713 | 0.0040594 | 0.016541 | 0.039628 | 0.0059459 | 0.005626 | -0.012329 | -0.035879 | 0.13912 | 0.12857 | 0.40295 | -0.16837 | 0.023941 | -0.008798 | -0.047194 | 0.066194 | 0.21059 | -0.1525 | -0.27404 | 1.182 | -120.0147 | 1.356 | 1.3145 | 0.13249 | -120.0252 | -119.7509 | 1.0764 | -120.0876 | 1.3743 | 1.3032 | 0.22685 | -119.9432 | -120.3063 | 1.4895 | 1.479 | 1.7533 | 1.3381 | -120.3222 | 1.4166 | 1.561 | 1.1979 | 1.3416 | -120.4278
3277.5938 | 120.7214 | -120.5795 | 0.19226 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.0038762 | -0.014416 | 0.018943 | 0.00030522 | -0.0035849 | 0.0044868 | 0.016968 | 0.039414 | 0.0057323 | 0.037675 | 0.0243 | 0.000747 | 0.1849 | 0.20183 | 0.43957 | 0.010206 | 0.060571 | 0.027831 | -0.005985 | 0.11656 | 0.25179 | -0.074664 | -0.24199 | 120.5897 | -0.00736 | 120.6172 | 120.5803 | -0.009459 | 0.009571 | 0.24731 | 120.3375 | -0.075704 | 120.6401 | 120.5735 | 0.236 | 0.059533 | -0.26692 | 120.7644 | 120.7814 | 121.0191 | 120.6038 | -0.18205 | 120.6961 | 120.8313 | 120.5049 | 120.6074 | -0.43425
3279.2969 | 121.1105 | -120.7947 | 0.1831 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.0043036 | -0.014416 | 0.018943 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016113 | 0.039414 | 0.0055187 | 0.037675 | 0.0243 | -0.003831 | 0.17574 | 0.20183 | 0.43042 | 0.010206 | 0.060571 | 0.03241 | -0.001407 | 0.10282 | 0.25179 | -0.12503 | -0.24199 | 120.8049 | -0.007361 | 120.8324 | 120.7908 | -0.014037 | 0.018727 | 0.24731 | 120.5527 | -0.080283 | 120.8552 | 120.7933 | 0.24058 | 0.068689 | -0.30813 | 120.9704 | 120.9965 | 121.2251 | 120.819 | -0.1729 | 120.8975 | 121.0465 | 120.6696 | 120.8271 | -0.42509
3281.0625 | 121.0831 | -120.9366 | 0.18768 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.00409 | -0.014843 | 0.018943 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016541 | 0.039414 | 0.0055187 | 0.042253 | 0.0243 | 0.000747 | 0.18032 | 0.19267 | 0.42584 | 0.010206 | 0.060571 | 0.023253 | -0.010564 | 0.10282 | 0.24721 | -0.13419 | -0.23741 | 120.9468 | -0.00736 | 120.9788 | 120.9373 | -0.009459 | 0.004991 | 0.23816 | 120.6992 | -0.084861 | 120.9972 | 120.926 | 0.22685 | 0.059532 | -0.32187 | 121.1169 | 121.1293 | 121.3624 | 120.9609 | -0.17748 | 121.0394 | 121.1838 | 120.8024 | 120.9598 | -0.42509
3282.8125 | 121.1243 | -120.9869 | 0.20599 | 1.4211e-13 | -0.026636 | 7.0442e-05 | 0.0043036 | -0.01463 | 0.01873 | 0.0079357 | -0.0037985 | 0.0042732 | 0.016327 | 0.039414 | 0.0053049 | 0.037675 | 0.0243 | 0.005325 | 0.1849 | 0.19267 | 0.435 | 0.005627 | 0.069728 | 0.027831 | -0.010564 | 0.10282 | 0.25179 | -0.11587 | -0.24199 | 120.9926 | -0.021093 | 121.0246 | 120.9923 | -0.000302 | -0.01332 | 0.229 | 120.7449 | -0.10317 | 121.0567 | 120.9764 | 0.23143 | 0.0458 | -0.32187 | 121.1718 | 121.1796 | 121.4219 | 121.0112 | -0.20037 | 121.0898 | 121.2387 | 120.8711 | 121.0148 | -0.44798
3284.5625 | 121.3074 | -120.9915 | 0.17395 | 1.4211e-13 | -0.026636 | 7.0442e-05 | 0.004731 | -0.014416 | 0.018943 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016541 | 0.039628 | 0.0059459 | 0.037675 | 0.0243 | 0.009904 | 0.18948 | 0.1881 | 0.43042 | 0.001048 | 0.060571 | 0.027831 | 0.003172 | 0.10282 | 0.25179 | -0.083821 | -0.23283 | 120.9926 | 0.015529 | 121.0292 | 121.0014 | 0.008856 | 0.014145 | 0.25647 | 120.7587 | -0.071128 | 121.0521 | 120.9947 | 0.236 | 0.077844 | -0.25777 | 121.181 | 121.1796 | 121.4219 | 121.0158 | -0.1729 | 121.0943 | 121.2433 | 120.9077 | 121.0193 | -0.40678
3286.25 | 121.3211 | -120.9686 | 0.17853 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.0038762 | -0.014416 | 0.018943 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016541 | 0.039414 | 0.0061595 | 0.037675 | 0.019721 | -0.008409 | 0.18032 | 0.17436 | 0.42584 | 0.005627 | 0.055992 | 0.023253 | -0.005985 | 0.11656 | 0.24264 | -0.097557 | -0.24657 | 120.9743 | 0.001795 | 121.0063 | 120.9602 | -0.014036 | -0.00417 | 0.24731 | 120.7221 | -0.061971 | 121.0246 | 120.9626 | 0.24058 | 0.064109 | -0.27609 | 121.149 | 121.143 | 121.3945 | 120.9883 | -0.1729 | 121.0852 | 121.2113 | 120.8711 | 120.9919 | -0.4251
3288 | 121.1929 | -121.0922 | 0.20142 | 1.4211e-13 | -0.026636 | 7.0442e-05 | 0.00409 | -0.013989 | 0.019157 | -0.0073253 | -0.0033713 | 0.0040594 | 0.016327 | 0.039414 | 0.0057323 | 0.037675 | 0.0243 | 0.000747 | 0.1849 | 0.1881 | 0.42126 | 0.010206 | 0.06515 | 0.018674 | -0.005985 | 0.11198 | 0.25179 | -0.092979 | -0.23741 | 121.1024 | -0.016515 | 121.1299 | 121.093 | -0.009459 | -0.013321 | 0.21984 | 120.8548 | -0.089437 | 121.1574 | 121.0862 | 0.23143 | 0.050378 | -0.2944 | 121.2771 | 121.2803 | 121.5135 | 121.1165 | -0.19121 | 121.2042 | 121.344 | 120.9992 | 121.1109 | -0.43883
3289.7031 | 121.3715 | -121.051 | 0.16937 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.00409 | -0.01463 | 0.018943 | 0.015566 | -0.0035849 | 0.0044868 | 0.016541 | 0.039628 | 0.0055187 | 0.042253 | 0.033457 | 0.005325 | 0.1849 | 0.19267 | 0.435 | 0.005627 | 0.06515 | 0.03241 | -0.005985 | 0.1074 | 0.25637 | -0.028878 | -0.23741 | 121.0567 | 0.015528 | 121.0933 | 121.0563 | -0.000302 | 0.023301 | 0.26562 | 120.8136 | -0.061972 | 121.1162 | 121.045 | 0.23143 | 0.086999 | -0.19825 | 121.2359 | 121.2437 | 121.486 | 121.0845 | -0.16375 | 121.1584 | 121.3074 | 121.0221 | 121.0834 | -0.40678
3291.4531 | 121.2845 | -121.1105 | 0.21973 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.00409 | -0.014202 | 0.018943 | 0.0079357 | -0.0037985 | 0.0042732 | 0.016327 | 0.039414 | 0.0057323 | 0.042253 | 0.019721 | -0.008409 | 0.17574 | 0.18352 | 0.43042 | 0.005627 | 0.06515 | 0.03241 | -0.005985 | 0.11656 | 0.25637 | -0.0884 | -0.24657 | 121.1162 | -0.043983 | 121.1528 | 121.1021 | -0.014036 | -0.036211 | 0.21069 | 120.864 | -0.10317 | 121.1757 | 121.1046 | 0.24058 | 0.036645 | -0.30813 | 121.2863 | 121.2941 | 121.541 | 121.1303 | -0.2141 | 121.2271 | 121.3669 | 121.0221 | 121.1429 | -0.46629
3293.2031 | 121.3257 | -121.1243 | 0.21057 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0043036 | -0.01463 | 0.018943 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016968 | 0.039414 | 0.0055187 | 0.037675 | 0.019721 | 0.000747 | 0.18032 | 0.1881 | 0.435 | 0.001048 | 0.069728 | 0.027831 | -0.005985 | 0.1074 | 0.25179 | -0.097557 | -0.24199 | 121.1253 | -0.030248 | 121.1619 | 121.125 | -0.000301 | -0.022476 | 0.22443 | 120.8823 | -0.10317 | 121.194 | 121.1183 | 0.236 | 0.041223 | -0.30813 | 121.3046 | 121.3124 | 121.5593 | 121.144 | -0.20952 | 121.2317 | 121.3761 | 121.0267 | 121.1521 | -0.45256
3294.9844 | 121.4218 | -121.0968 | 0.16937 | 1.4211e-13 | -0.02685 | -0.00014316 | 0.00409 | -0.014416 | 0.018943 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016541 | 0.039628 | 0.0057323 | 0.05141 | 0.0243 | 0.009904 | 0.1849 | 0.17436 | 0.43042 | -0.00811 | 0.06515 | 0.023253 | -0.001407 | 0.1074 | 0.24721 | -0.11129 | -0.23741 | 121.0887 | 0.015528 | 121.1482 | 121.1067 | 0.018014 | 0.004985 | 0.26105 | 120.8594 | -0.061972 | 121.162 | 121.0954 | 0.236 | 0.077842 | -0.28067 | 121.2817 | 121.2712 | 121.5272 | 121.1211 | -0.17748 | 121.2042 | 121.344 | 120.9855 | 121.1201 | -0.40678
3296.6719 | 121.4539 | -121.1563 | 0.19684 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.0043036 | -0.01463 | 0.01873 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0059459 | 0.046831 | 0.0243 | 0.000747 | 0.1849 | 0.17436 | 0.435 | 0.010206 | 0.060571 | 0.023253 | -0.001407 | 0.11198 | 0.25179 | -0.070086 | -0.24199 | 121.1665 | -0.011937 | 121.2031 | 121.1571 | -0.009459 | -0.02248 | 0.23816 | 120.9143 | -0.084859 | 121.2169 | 121.1549 | 0.24058 | 0.054956 | -0.26692 | 121.3412 | 121.3307 | 121.5913 | 121.1806 | -0.18663 | 121.2683 | 121.4081 | 121.0862 | 121.1796 | -0.43883
3298.4219 | 121.4355 | -121.1563 | 0.16937 | 1.4211e-13 | -0.026636 | 7.0442e-05 | 0.0036626 | -0.014416 | 0.018943 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016327 | 0.039414 | 0.0059459 | 0.042253 | 0.019721 | 0.000747 | 0.1849 | 0.19267 | 0.435 | 0.001048 | 0.060571 | 0.027831 | -0.005985 | 0.10282 | 0.25637 | -0.060928 | -0.24199 | 121.1574 | 0.015528 | 121.1986 | 121.1571 | -0.000301 | 0.023301 | 0.26562 | 120.9143 | -0.066551 | 121.2169 | 121.1503 | 0.236 | 0.086999 | -0.2303 | 121.3412 | 121.349 | 121.5913 | 121.176 | -0.16833 | 121.2591 | 121.4127 | 121.0954 | 121.1841 | -0.41136
3300.125 | 121.3394 | -121.2112 | 0.21973 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.00409 | -0.014416 | 0.01873 | 0.00030522 | -0.0035849 | 0.0040594 | 0.016113 | 0.039842 | 0.0055187 | 0.042253 | 0.0243 | 0.000747 | 0.1849 | 0.17436 | 0.435 | 0.005627 | 0.060571 | 0.036989 | -0.010564 | 0.11198 | 0.24721 | -0.12045 | -0.23741 | 121.2169 | -0.034826 | 121.2535 | 121.212 | -0.00488 | -0.045369 | 0.21527 | 120.9738 | -0.10775 | 121.2718 | 121.2007 | 0.22685 | 0.027488 | -0.34018 | 121.3961 | 121.3856 | 121.6462 | 121.2355 | -0.2141 | 121.3232 | 121.4585 | 121.0908 | 121.2482 | -0.45714
3301.875 | 121.4859 | -121.1884 | 0.16022 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.00409 | -0.013989 | 0.019157 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016327 | 0.039628 | 0.0057323 | 0.046831 | 0.028878 | -0.003831 | 0.1849 | 0.16978 | 0.43042 | 0.010206 | 0.06515 | 0.018674 | 0.003172 | 0.1074 | 0.24264 | -0.13876 | -0.23741 | 121.1986 | 0.024684 | 121.2352 | 121.1845 | -0.014037 | 0.009562 | 0.2702 | 120.9509 | -0.052816 | 121.2535 | 121.1915 | 0.24058 | 0.08242 | -0.29898 | 121.3733 | 121.3581 | 121.6188 | 121.2172 | -0.15001 | 121.2958 | 121.431 | 121.0496 | 121.207 | -0.39763
3303.625 | 121.4127 | -121.2067 | 0.21057 | 1.4211e-13 | -0.026423 | 0.00028424 | 0.00409 | -0.01463 | 0.01873 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016327 | 0.039201 | 0.0055187 | 0.037675 | 0.0243 | -0.008409 | 0.18032 | 0.16978 | 0.43042 | 0.005627 | 0.055992 | 0.027831 | -0.001407 | 0.11198 | 0.25637 | -0.13876 | -0.24657 | 121.2123 | -0.030248 | 121.2443 | 121.1983 | -0.014036 | -0.040792 | 0.21985 | 120.9601 | -0.098592 | 121.2627 | 121.2053 | 0.24516 | 0.045801 | -0.34934 | 121.387 | 121.3764 | 121.6371 | 121.231 | -0.20494 | 121.3186 | 121.463 | 121.0679 | 121.2345 | -0.45714
3305.3281 | 121.4539 | -121.2158 | 0.18768 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.00409 | -0.014416 | 0.01873 | 0.00030522 | -0.0037985 | 0.0042732 | 0.016541 | 0.039628 | 0.0055187 | 0.042253 | 0.019721 | 0.000747 | 0.18032 | 0.17894 | 0.435 | 0.010206 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.24721 | -0.060928 | -0.24199 | 121.226 | -0.00736 | 121.2581 | 121.2166 | -0.009459 | -0.008746 | 0.24731 | 120.9738 | -0.080282 | 121.2764 | 121.2144 | 0.24058 | 0.059532 | -0.24861 | 121.3961 | 121.3948 | 121.6508 | 121.2355 | -0.17748 | 121.3232 | 121.463 | 121.1549 | 121.2391 | -0.42967
3307.0938 | 121.4905 | -121.2158 | 0.1831 | 1.4211e-13 | -0.02685 | 7.0442e-05 | 0.00409 | -0.014202 | 0.018943 | 0.0079357 | -0.0033713 | 0.0040594 | 0.016541 | 0.039842 | 0.0057323 | 0.042253 | 0.0243 | 0.005325 | 0.18032 | 0.17894 | 0.435 | 0.005627 | 0.055992 | 0.036989 | 0.003172 | 0.1074 | 0.25179 | -0.092979 | -0.24199 | 121.2214 | -0.002782 | 121.2581 | 121.2211 | -0.000302 | -0.004168 | 0.25189 | 120.9738 | -0.075704 | 121.2718 | 121.219 | 0.24516 | 0.068689 | -0.27608 | 121.3961 | 121.3948 | 121.6508 | 121.2401 | -0.17748 | 121.3232 | 121.4676 | 121.1228 | 121.2528 | -0.42509
3308.7969 | 121.5225 | -121.2204 | 0.17395 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.0043036 | -0.014202 | 0.019157 | 0.0079357 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0055187 | 0.046831 | 0.028878 | 0.000747 | 0.1849 | 0.19725 | 0.43042 | 0.001048 | 0.06515 | 0.027831 | -0.005985 | 0.10282 | 0.25179 | -0.10671 | -0.24199 | 121.2214 | 0.010951 | 121.2672 | 121.2211 | -0.000301 | 0.023303 | 0.25647 | 120.9784 | -0.071128 | 121.2855 | 121.2144 | 0.236 | 0.077844 | -0.28066 | 121.4053 | 121.4177 | 121.6508 | 121.2493 | -0.1729 | 121.3232 | 121.4722 | 121.1137 | 121.2482 | -0.41594
3310.5625 | 121.5546 | -121.2387 | 0.17853 | 1.4211e-13 | -0.026423 | 0.00049784 | 0.0043036 | -0.01463 | 0.019157 | -0.0073253 | -0.0035849 | 0.0044868 | 0.016327 | 0.039414 | 0.0055187 | 0.042253 | 0.015142 | 0.005325 | 0.1849 | 0.20183 | 0.43042 | 0.005627 | 0.069728 | 0.023253 | -0.010564 | 0.10282 | 0.25179 | -0.097557 | -0.23741 | 121.2443 | 0.006373 | 121.281 | 121.244 | -0.000302 | 0.023304 | 0.25189 | 121.0013 | -0.075706 | 121.3084 | 121.2281 | 0.22685 | 0.073266 | -0.27609 | 121.4236 | 121.4405 | 121.6691 | 121.2538 | -0.1729 | 121.3415 | 121.4905 | 121.1412 | 121.262 | -0.41594
3312.3281 | 121.4401 | -121.2479 | 0.21057 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.00409 | -0.014416 | 0.018943 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016754 | 0.039414 | 0.0055187 | 0.042253 | 0.0243 | 0.000747 | 0.18032 | 0.17894 | 0.43042 | 0.005627 | 0.074307 | 0.027831 | -0.001407 | 0.1074 | 0.25637 | -0.070086 | -0.23741 | 121.2535 | -0.030248 | 121.2901 | 121.2486 | -0.00488 | -0.031634 | 0.21985 | 121.0105 | -0.10317 | 121.3222 | 121.2465 | 0.236 | 0.045801 | -0.28066 | 121.4282 | 121.4268 | 121.6783 | 121.2722 | -0.20494 | 121.3553 | 121.5042 | 121.1778 | 121.2757 | -0.44798
3314.0156 | 121.4355 | -121.2799 | 0.21973 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.0038762 | -0.014416 | 0.019157 | 0.00030522 | -0.0037985 | 0.0044868 | 0.016327 | 0.039414 | 0.0057323 | 0.05141 | 0.0243 | -0.003831 | 0.17574 | 0.19725 | 0.43042 | 0.005627 | 0.060571 | 0.023253 | -0.005985 | 0.1074 | 0.25179 | -0.070086 | -0.23741 | 121.2855 | -0.043983 | 121.3313 | 121.2761 | -0.009458 | -0.022474 | 0.21069 | 121.0425 | -0.11233 | 121.3405 | 121.2739 | 0.23143 | 0.032067 | -0.28981 | 121.4557 | 121.4772 | 121.7103 | 121.3042 | -0.2141 | 121.3873 | 121.5317 | 121.2098 | 121.3032 | -0.45714
3315.7656 | 121.4767 | -121.2936 | 0.20599 | 1.4211e-13 | -0.026423 | 7.0442e-05 | 0.0043036 | -0.01463 | 0.018943 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016327 | 0.039414 | 0.0053049 | 0.042253 | 0.0243 | 0.000747 | 0.18032 | 0.20183 | 0.42584 | 0.005627 | 0.06515 | 0.027831 | -0.005985 | 0.11198 | 0.25637 | -0.12961 | -0.24199 | 121.2993 | -0.025671 | 121.3359 | 121.2944 | -0.00488 | -0.004162 | 0.21985 | 121.0517 | -0.094015 | 121.3588 | 121.2877 | 0.236 | 0.050378 | -0.3356 | 121.474 | 121.4955 | 121.7195 | 121.3179 | -0.20037 | 121.4056 | 121.55 | 121.164 | 121.3215 | -0.44798
3317.5312 | 121.5775 | -121.2662 | 0.19226 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.0038762 | -0.014202 | 0.018943 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016541 | 0.039414 | 0.0053049 | 0.042253 | 0.019721 | -0.003831 | 0.18032 | 0.20183 | 0.43042 | 0.001048 | 0.060571 | 0.027831 | -0.001407 | 0.1074 | 0.25637 | -0.0884 | -0.24199 | 121.2672 | -0.011938 | 121.3084 | 121.2623 | -0.004879 | 0.009571 | 0.23816 | 121.0242 | -0.08486 | 121.3267 | 121.2648 | 0.24058 | 0.064111 | -0.28066 | 121.4465 | 121.468 | 121.6966 | 121.2859 | -0.19121 | 121.3736 | 121.5225 | 121.1778 | 121.294 | -0.43425
3319.2344 | 121.5408 | -121.2936 | 0.19226 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.00409 | -0.014843 | 0.018943 | -0.0073253 | -0.0035849 | 0.0042732 | 0.016541 | 0.039842 | 0.0055187 | 0.046831 | 0.019721 | -0.003831 | 0.1849 | 0.19725 | 0.43957 | 0.001048 | 0.055992 | 0.023253 | -0.005985 | 0.11656 | 0.25637 | -0.11129 | -0.23741 | 121.2947 | -0.00736 | 121.3405 | 121.2898 | -0.004879 | 0.004992 | 0.24731 | 121.0562 | -0.075704 | 121.3496 | 121.2877 | 0.23143 | 0.064111 | -0.30355 | 121.4785 | 121.4909 | 121.7332 | 121.3134 | -0.19121 | 121.4102 | 121.55 | 121.1823 | 121.3169 | -0.42967
3321 | 121.5958 | -121.2936 | 0.16022 | 1.4211e-13 | -0.026423 | -0.00014316 | 0.00409 | -0.014416 | 0.018943 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016541 | 0.040055 | 0.0057323 | 0.042253 | 0.0243 | 0.000747 | 0.1849 | 0.20641 | 0.435 | -0.021847 | 0.060571 | 0.023253 | -0.010564 | 0.1074 | 0.25179 | -0.11129 | -0.24199 | 121.2718 | 0.024684 | 121.3359 | 121.2944 | 0.022594 | 0.046194 | 0.27478 | 121.0517 | -0.052816 | 121.3542 | 121.2831 | 0.23143 | 0.091577 | -0.27151 | 121.4785 | 121.5001 | 121.7286 | 121.3179 | -0.18206 | 121.401 | 121.5454 | 121.1823 | 121.3169 | -0.40221
3322.6875 | 121.5546 | -121.3257 | 0.18768 | 1.4211e-13 | -0.02685 | 7.0442e-05 | 0.0038762 | -0.014202 | 0.019157 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016113 | 0.039414 | 0.0055187 | 0.042253 | 0.0243 | 0.000747 | 0.18032 | 0.21099 | 0.43042 | -0.021847 | 0.069728 | 0.027831 | -0.001407 | 0.10282 | 0.25637 | -0.05635 | -0.24199 | 121.3038 | -0.00736 | 121.3679 | 121.3264 | 0.022594 | 0.023307 | 0.24274 | 121.0837 | -0.084861 | 121.3954 | 121.3243 | 0.24058 | 0.068689 | -0.24403 | 121.506 | 121.5367 | 121.7561 | 121.35 | -0.20953 | 121.4285 | 121.5821 | 121.2693 | 121.3535 | -0.42967
3324.4375 | 121.669 | -121.3165 | 0.16479 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.00409 | -0.013989 | 0.018943 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016327 | 0.039628 | 0.0055187 | 0.046831 | 0.019721 | 0.000747 | 0.17574 | 0.20641 | 0.42584 | -0.063057 | 0.055992 | 0.023253 | -0.005985 | 0.11198 | 0.25179 | -0.079243 | -0.23741 | 121.2535 | 0.010949 | 121.3634 | 121.3173 | 0.063804 | 0.041616 | 0.26104 | 121.0791 | -0.052816 | 121.3725 | 121.3105 | 0.23143 | 0.086999 | -0.24404 | 121.4923 | 121.5229 | 121.7424 | 121.3362 | -0.22785 | 121.4285 | 121.5683 | 121.2373 | 121.3398 | -0.40221
3326.1875 | 120.4971 | -120.2316 | 0.15106 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.00409 | -0.014416 | 0.018943 | 0.0079357 | -0.0031575 | 0.0040594 | 0.016754 | 0.039842 | 0.0050913 | 0.028518 | 0.0243 | 0.005325 | 0.17117 | 0.20183 | 0.43042 | -0.012689 | 0.06515 | 0.027831 | -0.001407 | 0.1074 | 0.24721 | -0.079243 | -0.24657 | 120.2189 | 0.020104 | 120.2601 | 120.237 | 0.018014 | 0.05077 | 0.27936 | 119.9851 | -0.043661 | 120.2968 | 120.2302 | 0.24516 | 0.096153 | -0.2303 | 120.4028 | 120.4335 | 120.662 | 120.2559 | -0.16375 | 120.339 | 120.4788 | 120.1524 | 120.2595 | -0.39763
3327.9375 | 121.1151 | -120.8817 | 0.16479 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.00409 | -0.014416 | 0.018943 | -0.0073253 | -0.0033713 | 0.0044868 | 0.016541 | 0.039628 | 0.0057323 | 0.037675 | 0.0243 | -0.003831 | 0.1849 | 0.19267 | 0.42584 | 0.005627 | 0.06515 | 0.027831 | -0.005985 | 0.11656 | 0.25637 | -0.074664 | -0.24199 | 120.8873 | 0.020106 | 120.9193 | 120.8778 | -0.009458 | 0.027879 | 0.26104 | 120.6397 | -0.048238 | 120.9468 | 120.8757 | 0.236 | 0.091577 | -0.23946 | 121.0666 | 121.0743 | 121.3075 | 120.906 | -0.15917 | 120.9982 | 121.138 | 120.807 | 120.9095 | -0.40678
3329.7031 | 121.1792 | -121.0098 | 0.18768 | 1.4211e-13 | -0.02685 | 0.00092524 | 0.00409 | -0.014843 | 0.019371 | 0.00030522 | -0.0033713 | 0.0044868 | 0.016327 | 0.039628 | 0.0057323 | 0.042253 | 0.0243 | -0.003831 | 0.17574 | 0.19725 | 0.43042 | 0.005627 | 0.055992 | 0.027831 | -0.010564 | 0.11198 | 0.24721 | -0.12961 | -0.23283 | 121.0155 | -0.011939 | 121.0521 | 121.006 | -0.009458 | 0.00957 | 0.24274 | 120.777 | -0.075704 | 121.0658 | 120.9993 | 0.22227 | 0.059532 | -0.31729 | 121.1856 | 121.2071 | 121.4402 | 121.0341 | -0.18206 | 121.1218 | 121.257 | 120.8802 | 121.0377 | -0.42051
3331.4062 | 121.2433 | -121.0602 | 0.19226 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.0043036 | -0.01463 | 0.019157 | 0.0079357 | -0.0037985 | 0.0049142 | 0.016327 | 0.039628 | 0.0055187 | 0.037675 | 0.028878 | 0.000747 | 0.1849 | 0.19725 | 0.43042 | 0.005627 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.24721 | -0.092979 | -0.23283 | 121.0658 | -0.00736 | 121.0979 | 121.0609 | -0.00488 | 0.004992 | 0.23816 | 120.8273 | -0.08486 | 121.1253 | 121.0542 | 0.22685 | 0.054954 | -0.28524 | 121.2451 | 121.2574 | 121.4906 | 121.0891 | -0.18663 | 121.1676 | 121.3074 | 120.9672 | 121.0834 | -0.42509
3333.1719 | 121.3623 | -121.0144 | 0.16479 | 1.4211e-13 | -0.02685 | -0.00014316 | 0.0043036 | -0.014416 | 0.019157 | 0.00030522 | -0.0031575 | 0.0042732 | 0.016541 | 0.039628 | 0.0057323 | 0.046831 | 0.0243 | 0.000747 | 0.18032 | 0.19725 | 0.42126 | -0.00811 | 0.069728 | 0.027831 | 0.003172 | 0.098244 | 0.25179 | -0.060928 | -0.24657 | 121.0063 | 0.015528 | 121.0612 | 121.0152 | 0.008857 | 0.032458 | 0.25647 | 120.7678 | -0.066551 | 121.0841 | 121.0176 | 0.24974 | 0.086999 | -0.22572 | 121.1947 | 121.2117 | 121.4357 | 121.0387 | -0.17291 | 121.1126 | 121.2662 | 120.9535 | 121.0422 | -0.41136
3334.875 | 121.3394 | -121.0922 | 0.16022 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.0038762 | -0.01463 | 0.019157 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016327 | 0.039842 | 0.0055187 | 0.042253 | 0.0243 | 0.000747 | 0.18032 | 0.20641 | 0.43042 | 0.001048 | 0.06515 | 0.03241 | -0.005985 | 0.11198 | 0.25179 | -0.033457 | -0.24199 | 121.0933 | 0.020106 | 121.1345 | 121.093 | -0.000301 | 0.046194 | 0.2702 | 120.8502 | -0.048238 | 121.1574 | 121.0862 | 0.236 | 0.091577 | -0.19367 | 121.2725 | 121.2986 | 121.5226 | 121.1165 | -0.15917 | 121.2042 | 121.344 | 121.0588 | 121.1246 | -0.40221
3336.625 | 121.2799 | -121.1563 | 0.19226 | 1.4211e-13 | -0.026209 | 7.0442e-05 | 0.0038762 | -0.014202 | 0.019157 | -0.0073253 | -0.0033713 | 0.0047004 | 0.016113 | 0.039628 | 0.0057323 | 0.037675 | 0.019721 | -0.003831 | 0.1849 | 0.17894 | 0.42584 | 0.010206 | 0.060571 | 0.023253 | -0.001407 | 0.1074 | 0.25179 | -0.12503 | -0.23741 | 121.1665 | -0.00736 | 121.194 | 121.1525 | -0.014037 | -0.013324 | 0.23358 | 120.9189 | -0.08486 | 121.2169 | 121.1549 | 0.236 | 0.059533 | -0.31729 | 121.3412 | 121.3352 | 121.5821 | 121.176 | -0.18205 | 121.2637 | 121.4081 | 121.0313 | 121.1796 | -0.42967
3338.3281 | 121.3257 | -121.1655 | 0.16937 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.00409 | -0.014416 | 0.019584 | 0.0079357 | -0.0037985 | 0.0044868 | 0.016541 | 0.039628 | 0.0053049 | 0.037675 | 0.0243 | 0.000747 | 0.18032 | 0.17436 | 0.42126 | 0.001048 | 0.060571 | 0.027831 | -0.005985 | 0.10282 | 0.25637 | -0.0884 | -0.24199 | 121.1665 | 0.01095 | 121.2031 | 121.1662 | -0.000301 | 0.004985 | 0.25189 | 120.9235 | -0.066551 | 121.226 | 121.1595 | 0.236 | 0.086999 | -0.25777 | 121.3458 | 121.3398 | 121.5867 | 121.1898 | -0.16833 | 121.2683 | 121.4218 | 121.0771 | 121.1933 | -0.41136
3340.0938 | 121.4127 | -121.1563 | 0.17395 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.0043036 | -0.014202 | 0.018943 | 0.015566 | -0.0033713 | 0.0044868 | 0.016541 | 0.039414 | 0.0057323 | 0.033096 | 0.0243 | 0.000747 | 0.18032 | 0.1881 | 0.435 | 0.005627 | 0.06515 | 0.036989 | -0.005985 | 0.1074 | 0.25179 | -0.13419 | -0.23741 | 121.1619 | 0.006373 | 121.1894 | 121.1571 | -0.00488 | 0.014145 | 0.26105 | 120.9189 | -0.066549 | 121.2215 | 121.1503 | 0.23143 | 0.077844 | -0.30814 | 121.3366 | 121.3444 | 121.5913 | 121.1806 | -0.16832 | 121.2637 | 121.4081 | 121.0221 | 121.1933 | -0.41136
3341.8281 | 121.431 | -121.1609 | 0.19226 | 1.4211e-13 | -0.026636 | 0.00028424 | 0.0038762 | -0.014416 | 0.018943 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016327 | 0.039628 | 0.0055187 | 0.042253 | 0.028878 | 0.005325 | 0.1849 | 0.19725 | 0.42584 | 0.010206 | 0.06515 | 0.023253 | -0.005985 | 0.1074 | 0.24721 | -0.065507 | -0.23741 | 121.1711 | -0.00736 | 121.2031 | 121.1662 | -0.004881 | 0.004992 | 0.23358 | 120.9235 | -0.08486 | 121.226 | 121.1549 | 0.23143 | 0.054954 | -0.25777 | 121.3458 | 121.3581 | 121.5867 | 121.1898 | -0.18205 | 121.2683 | 121.4081 | 121.0954 | 121.1841 | -0.42967
3343.5312 | 121.4035 | -121.1975 | 0.1831 | 1.4211e-13 | -0.026636 | 7.0442e-05 | 0.00409 | -0.014202 | 0.019157 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016541 | 0.039628 | 0.0055187 | 0.042253 | 0.0243 | 0.009904 | 0.18032 | 0.17436 | 0.43042 | 0.005627 | 0.06515 | 0.027831 | -0.001407 | 0.11656 | 0.26095 | -0.13419 | -0.23741 | 121.2031 | -0.002782 | 121.2398 | 121.2074 | 0.004277 | -0.008747 | 0.24731 | 120.9601 | -0.066548 | 121.2627 | 121.1961 | 0.236 | 0.077846 | -0.31729 | 121.3778 | 121.3719 | 121.6279 | 121.2218 | -0.17748 | 121.3141 | 121.4585 | 121.0633 | 121.2253 | -0.42051
3345.2969 | 121.1746 | -121.0739 | 0.20142 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.0038762 | -0.014416 | 0.019584 | 0.00030522 | -0.0033713 | 0.0042732 | 0.016541 | 0.039414 | 0.0057323 | 0.046831 | 0.019721 | 0.000747 | 0.1849 | 0.17436 | 0.43042 | 0.005627 | 0.060571 | 0.03241 | -0.005985 | 0.11198 | 0.25637 | -0.13419 | -0.24657 | 121.0795 | -0.016515 | 121.1207 | 121.0747 | -0.00488 | -0.027058 | 0.229 | 120.8273 | -0.089437 | 121.1345 | 121.0679 | 0.24058 | 0.054956 | -0.3356 | 121.2588 | 121.2483 | 121.5043 | 121.0936 | -0.19579 | 121.1859 | 121.3303 | 120.9397 | 121.1063 | -0.44798
3347 | 121.2387 | -121.1517 | 0.21973 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.00409 | -0.014416 | 0.018943 | 0.00030522 | -0.0037985 | 0.0042732 | 0.016541 | 0.039842 | 0.0057323 | 0.037675 | 0.0243 | -0.003831 | 0.1849 | 0.16978 | 0.42126 | 0.010206 | 0.055992 | 0.027831 | -0.005985 | 0.11198 | 0.25637 | -0.11129 | -0.23741 | 121.1619 | -0.034826 | 121.1894 | 121.1479 | -0.014037 | -0.049948 | 0.20153 | 120.9143 | -0.10775 | 121.2077 | 121.1457 | 0.23143 | 0.036645 | -0.33102 | 121.3366 | 121.3215 | 121.573 | 121.176 | -0.20952 | 121.2637 | 121.4081 | 121.0404 | 121.1796 | -0.45714
3348.75 | 121.4218 | -121.1243 | 0.16937 | 1.4211e-13 | -0.027064 | -0.00014316 | 0.00409 | -0.01463 | 0.019157 | -0.0073253 | -0.0035849 | 0.0047004 | 0.016541 | 0.039628 | 0.0057323 | 0.046831 | 0.019721 | 0.005325 | 0.18032 | 0.1652 | 0.43042 | 0.010206 | 0.055992 | 0.023253 | -0.005985 | 0.11198 | 0.24721 | -0.10214 | -0.23741 | 121.1345 | 0.01095 | 121.1711 | 121.1296 | -0.004881 | -0.004173 | 0.26105 | 120.8869 | -0.057394 | 121.1803 | 121.1183 | 0.23143 | 0.077842 | -0.27151 | 121.3046 | 121.2895 | 121.5547 | 121.144 | -0.15917 | 121.2362 | 121.3715 | 121.0221 | 121.1475 | -0.40678
3350.5156 | 121.3165 | -121.1609 | 0.21057 | 1.4211e-13 | -0.027277 | 0.00071164 | 0.0045172 | -0.014416 | 0.019371 | 0.00030522 | -0.0035849 | 0.0047004 | 0.016327 | 0.039201 | 0.0053049 | 0.042253 | 0.019721 | 0.000747 | 0.17574 | 0.17436 | 0.41668 | 0.010206 | 0.06515 | 0.027831 | -0.001407 | 0.11656 | 0.24264 | -0.10671 | -0.24199 | 121.1711 | -0.034827 | 121.2031 | 121.1616 | -0.009459 | -0.036213 | 0.20611 | 120.9189 | -0.094014 | 121.226 | 121.1595 | 0.24058 | 0.032066 | -0.31729 | 121.3366 | 121.3352 | 121.5776 | 121.1806 | -0.20037 | 121.2774 | 121.4035 | 121.0542 | 121.1887 | -0.45256
3352.2188 | 121.4401 | -121.1792 | 0.16937 | 1.4211e-13 | -0.026636 | 0.00049784 | 0.004731 | -0.014416 | 0.018943 | 0.0079357 | -0.0033713 | 0.0044868 | 0.016327 | 0.039628 | 0.0057323 | 0.037675 | 0.019721 | -0.003831 | 0.18032 | 0.17894 | 0.43042 | 0.010206 | 0.060571 | 0.023253 | -0.010564 | 0.11198 | 0.25637 | -0.051771 | -0.24199 | 121.1894 | 0.01095 | 121.2169 | 121.1754 | -0.014037 | 0.009564 | 0.26105 | 120.9372 | -0.057394 | 121.2398 | 121.1686 | 0.23143 | 0.086999 | -0.22114 | 121.3595 | 121.3581 | 121.6096 | 121.1989 | -0.15917 | 121.2912 | 121.4356 | 121.1274 | 121.2025 | -0.41136
3353.9688 | 121.3394 | -121.2067 | 0.19684 | 1.4211e-13 | -0.027277 | -0.00014316 | 0.00409 | -0.01463 | 0.018943 | 0.0079357 | -0.0040121 | 0.0049142 | 0.016327 | 0.039628 | 0.0055187 | 0.042253 | 0.019721 | -0.008409 | 0.1849 | 0.18352 | 0.43042 | 0.005627 | 0.060571 | 0.027831 | -0.001407 | 0.11198 | 0.25179 | -0.097557 | -0.23741 | 121.2123 | -0.011937 | 121.2489 | 121.1983 | -0.014036 | -0.013322 | 0.23358 | 120.9693 | -0.084859 | 121.2672 | 121.2053 | 0.236 | 0.054956 | -0.2944 | 121.3916 | 121.3902 | 121.6371 | 121.2264 | -0.19121 | 121.3186 | 121.4585 | 121.1091 | 121.2345 | -0.43425
3355.6719 | 121.463 | -121.1975 | 0.18768 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.00409 | -0.014416 | 0.01873 | 0.00030522 | -0.0035849 | 0.0042732 | 0.016113 | 0.039414 | 0.0055187 | 0.037675 | 0.0243 | -0.003831 | 0.18032 | 0.16062 | 0.43042 | 0.001048 | 0.069728 | 0.018674 | -0.005985 | 0.1074 | 0.25179 | -0.12045 | -0.23741 | 121.1986 | -0.00736 | 121.2352 | 121.1937 | -0.004879 | -0.027062 | 0.24274 | 120.9601 | -0.080282 | 121.2672 | 121.1915 | 0.23143 | 0.064111 | -0.30813 | 121.3778 | 121.3581 | 121.6279 | 121.2218 | -0.18663 | 121.3049 | 121.4493 | 121.0771 | 121.2162 | -0.42509
3357.4375 | 121.5363 | -121.1792 | 0.1831 | 1.4211e-13 | -0.02685 | 7.0442e-05 | 0.00409 | -0.01463 | 0.019157 | 0.015566 | -0.0040121 | 0.0044868 | 0.016327 | 0.039842 | 0.0055187 | 0.033096 | 0.0243 | 0.000747 | 0.17574 | 0.17436 | 0.43042 | 0.014784 | 0.060571 | 0.036989 | -0.001407 | 0.11198 | 0.24721 | -0.079243 | -0.24199 | 121.194 | -0.007361 | 121.2123 | 121.1799 | -0.014037 | -0.008747 | 0.24731 | 120.9372 | -0.071126 | 121.2398 | 121.1778 | 0.24058 | 0.06411 | -0.26235 | 121.3549 | 121.3536 | 121.6096 | 121.2035 | -0.16832 | 121.2912 | 121.4264 | 121.1 | 121.2162 | -0.42509
3359.1875 | 121.3898 | -121.2753 | 0.23346 | 1.4211e-13 | -0.027064 | 0.00071164 | 0.00409 | -0.014202 | 0.019157 | 0.0079357 | -0.0033713 | 0.0047004 | 0.016327 | 0.039628 | 0.0053049 | 0.042253 | 0.0243 | -0.003831 | 0.17574 | 0.1881 | 0.43042 | 0.001048 | 0.06515 | 0.027831 | -0.001407 | 0.1074 | 0.25637 | -0.051771 | -0.24199 | 121.2764 | -0.057715 | 121.3176 | 121.2715 | -0.004879 | -0.045364 | 0.19696 | 121.0333 | -0.12606 | 121.3405 | 121.2739 | 0.24058 | 0.022913 | -0.28523 | 121.4511 | 121.4634 | 121.7057 | 121.2996 | -0.23241 | 121.3827 | 121.5317 | 121.2236 | 121.3032 | -0.47545
3360.9531 | 121.4264 | -121.2433 | 0.23346 | 1.4211e-13 | -0.02685 | 0.00049784 | 0.00409 | -0.01463 | 0.01873 | -0.0073253 | -0.0035849 | 0.0047004 | 0.016541 | 0.039628 | 0.0055187 | 0.042253 | 0.019721 | 0.000747 | 0.1849 | 0.17894 | 0.42126 | -0.003531 | 0.060571 | 0.027831 | -0.005985 | 0.1074 | 0.25179 | -0.092979 | -0.24199 | 121.2398 | -0.048558 | 121.2855 | 121.244 | 0.004278 | -0.054522 | 0.1878 | 121.0013 | -0.12606 | 121.3039 | 121.2373 | 0.236 | 0.018335 | -0.32644 | 121.4282 | 121.4222 | 121.6645 | 121.263 | -0.23699 | 121.3507 | 121.4951 | 121.1503 | 121.2711 | -0.47545
3362.7031 | 121.4905 | -121.2753 | 0.20599 | 1.4211e-13 | -0.02685 | 7.0442e-05 | 0.0043036 | -0.014416 | 0.019371 | 0.0079357 | -0.0035849 | 0.0042732 | 0.016541 | 0.040055 | 0.0053049 | 0.037675 | 0.0243 | 0.000747 | 0.17574 | 0.16978 | 0.43042 | 0.005627 | 0.060571 | 0.03241 | -0.001407 | 0.10282 | 0.25637 | -0.11587 | -0.24657 | 121.281 | -0.03025 | 121.313 | 121.2761 | -0.00488 | -0.036215 | 0.22442 | 121.0288 | -0.10317 | 121.3359 | 121.2739 | 0.24516 | 0.050378 | -0.32187 | 121.4511 | 121.4451 | 121.7057 | 121.2996 | -0.20037 | 121.3782 | 121.5317 | 121.1595 | 121.3077 | -0.45256
3364.4688 | 121.5317 | -121.2433 | 0.18768 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.00409 | -0.014416 | 0.018943 | 0.0079357 | -0.0031575 | 0.0044868 | 0.016327 | 0.039842 | 0.0057323 | 0.037675 | 0.019721 | -0.003831 | 0.18032 | 0.16062 | 0.42584 | 0.001048 | 0.06515 | 0.03241 | -0.001407 | 0.1074 | 0.25179 | -0.11587 | -0.24199 | 121.2443 | -0.00736 | 121.281 | 121.2395 | -0.004879 | -0.027062 | 0.23816 | 121.0013 | -0.080282 | 121.3084 | 121.2419 | 0.24058 | 0.064111 | -0.30356 | 121.4236 | 121.4039 | 121.6691 | 121.263 | -0.18663 | 121.3507 | 121.4951 | 121.1274 | 121.2757 | -0.42967
3366.1719 | 121.5088 | -121.2799 | 0.19684 | 1.4211e-13 | -0.02685 | 0.00071164 | 0.0043036 | -0.01463 | 0.019157 | 0.0079357 | -0.0035849 | 0.0047004 | 0.016541 | 0.039414 | 0.0055187 | 0.037675 | 0.028878 | 0.000747 | 0.18032 | 0.19267 | 0.43042 | 0.005627 | 0.069728 | 0.03241 | 0.007751 | 0.11198 | 0.24721 | -0.001407 | -0.23741 | 121.2855 | -0.016515 | 121.3176 | 121.2807 | -0.00488 | -0.004164 | 0.23358 | 121.0425 | -0.084859 | 121.3496 | 121.2877 | 0.24516 | 0.050377 | -0.19825 | 121.4602 | 121.4726 | 121.7103 | 121.3088 | -0.19121 | 121.3919 | 121.5271 | 121.2785 | 121.3123 | -0.43425
3367.9219 | 121.582 | -121.3028 | 0.18768 | 1.4211e-13 | -0.02685 | 0.00028424 | 0.00409 | -0.01463 | 0.019157 | -0.0073253 | -0.0031575 | 0.0040594 | 0.016541 | 0.039842 | 0.0050913 | 0.037675 | 0.028878 | 0.000747 | 0.1849 | 0.20641 | 0.43042 | -0.012689 | 0.06515 | 0.03241 | -0.001407 | 0.11198 | 0.25637 | 0.012329 | -0.24199 | 121.2901 | -0.002782 | 121.3405 | 121.3035 | 0.013436 | 0.018728 | 0.24274 | 121.0608 | -0.075704 | 121.3679 | 121.3014 | 0.24058 | 0.068689 | -0.17535 | 121.4877 | 121.5092 | 121.7332 | 121.3317 | -0.20037 | 121.4148 | 121.5592 | 121.3151 | 121.3352 | -0.42967
3369.6094 | 121.4767 | -121.3257 | 0.20599 | 1.4211e-13 | -0.027064 | 0.00028424 | 0.0043036 | -0.014416 | 0.01873 | 0.0079357 | -0.0037985 | 0.0042732 | 0.016754 | 0.039628 | 0.0055187 | 0.046831 | 0.015142 | 0.005325 | 0.18948 | 0.19725 | 0.43042 | -0.021847 | 0.06515 | 0.027831 | -0.010564 | 0.11198 | 0.25179 | -0.11129 | -0.24199 | 121.3038 | -0.016515 | 121.3725 | 121.331 | 0.027172 | -0.008741 | 0.22442 | 121.0837 | -0.094015 | 121.3908 | 121.3151 | 0.23143 | 0.0458 | -0.31729 | 121.5152 | 121.5229 | 121.7561 | 121.3408 | -0.22784 | 121.4377 | 121.5775 | 121.2144 | 121.3535 | -0.44798
3371.3594 | 121.55 | -121.3348 | 0.21515 | 1.4211e-13 | -0.027064 | 0.00028424 | 0.00409 | -0.014202 | 0.018943 | 0.0079357 | -0.0035849 | 0.0047004 | 0.016541 | 0.039628 | 0.0053049 | 0.042253 | 0.019721 | -0.008409 | 0.18032 | 0.20183 | 0.43042 | 0.005627 | 0.069728 | 0.036989 | -0.001407 | 0.1074 | 0.25179 | -0.0243 | -0.23741 | 121.3405 | -0.034826 | 121.3771 | 121.3264 | -0.014036 | -0.013317 | 0.21527 | 121.0974 | -0.10775 | 121.4046 | 121.3334 | 0.236 | 0.036645 | -0.23945 | 121.5152 | 121.5367 | 121.7653 | 121.3546 | -0.20952 | 121.4422 | 121.5866 | 121.3105 | 121.3718 | -0.45256

## Thermal Data
Fire Time | B Position - Middle | D Position - 3' | D Position - Middle | D Position - 7'
-0.9333 | 47.0533 | 29.8408 | 39.0888 | 20.0061
0.0667 | 52.2255 | 32.0066 | 42.3466 | 21.6258
1.0667 | 57.1678 | 33.9033 | 46.2088 | 23.3999
2.0667 | 62.1347 | 37.2101 | 50.2079 | 25.4017
3.0667 | 67.0844 | 39.0939 | 54.1077 | 28.1734
4.0667 | 72.8609 | 41.4162 | 57.5962 | 30.1215
5.0667 | 76.0718 | 43.2746 | 61.2584 | 31.463
6.0667 | 79.6514 | 45.4654 | 65.6862 | 33.8015
7.0667 | 82.0351 | 47.8089 | 70.3938 | 35.5289
8.0667 | 85.502 | 50.4464 | 74.0309 | 37.3262
9.0667 | 90.0959 | 53.0042 | 77.6917 | 39.2287
10.0667 | 94.6243 | 54.8772 | 81.7783 | 42.127
11.0667 | 98.6346 | 57.3767 | 85.4402 | 45.367
12.0667 | 101.0036 | 59.9009 | 88.73 | 47.7212
13.0667 | 103.1846 | 62.5485 | 93.1873 | 49.9095
14.0667 | 106.4169 | 64.4155 | 96.0448 | 51.3737
15.0667 | 107.3523 | 65.9682 | 98.39 | 52.0381
16.0667 | 109.401 | 67.4539 | 99.8424 | 53.3625
17.0667 | 110.8764 | 69.718 | 102.5641 | 54.3371
18.0667 | 111.9689 | 71.0703 | 103.8459 | 54.8776
19.0667 | 114.5906 | 73.0866 | 106.7377 | 56.8632
20.0667 | 116.8741 | 75.1274 | 109.6107 | 58.8067
21.0667 | 118.8911 | 77.4333 | 110.793 | 60.4186
22.0667 | 120.288 | 79.7639 | 112.5564 | 62.204
23.0667 | 123.12 | 82.1442 | 113.7876 | 63.6373
24.0667 | 125.4812 | 83.9821 | 115.4767 | 64.9257
25.0667 | 126.3737 | 86.8868 | 117.0343 | 66.7037
26.0667 | 127.0617 | 89.4059 | 117.8886 | 68.0656
27.0667 | 128.5173 | 90.2617 | 119.3335 | 69.3511
28.0667 | 129.3353 | 92.3184 | 120.5438 | 71.1555
29.0667 | 129.8423 | 94.0489 | 121.6253 | 72.5791
30.0667 | 130.9993 | 97.494 | 123.5 | 73.9462
31.0667 | 133.0806 | 100.5085 | 125.3832 | 75.3184
32.0667 | 135.4033 | 102.0465 | 126.6632 | 76.3994
33.0667 | 137.7977 | 102.9079 | 129.09 | 77.9187
34.0667 | 139.4207 | 103.9244 | 130.9514 | 79.1308
35.0667 | 140.6077 | 105.474 | 133.1963 | 80.643
36.0667 | 140.7491 | 107.2189 | 133.1506 | 81.3808
37.0667 | 142.0317 | 107.5014 | 133.6263 | 81.4772
38.0667 | 143.0859 | 108.0497 | 133.8395 | 81.3605
39.0667 | 145.3907 | 108.3908 | 134.7158 | 82.5679
40.0667 | 146.7188 | 109.1859 | 136.6345 | 82.9252
41.0667 | 146.7901 | 109.6351 | 136.6561 | 83.5279
42.0667 | 146.8029 | 110.713 | 137.1757 | 84.032
43.0667 | 147.6043 | 112.001 | 138.1195 | 84.6314
44.0667 | 147.9695 | 113.7529 | 140.4937 | 87.504
45.0667 | 149.4075 | 114.7348 | 141.3175 | 88.37
46.0667 | 151.5325 | 115.4069 | 141.5938 | 88.1566
47.0667 | 153.21 | 116.4483 | 142.6145 | 88.4321
48.0667 | 154.0192 | 117.7042 | 144.1324 | 88.2036
49.0667 | 155.4111 | 118.3989 | 144.7833 | 89.5392
50.0667 | 155.5003 | 118.4928 | 145.4761 | 90.189
51.0667 | 155.939 | 119.7073 | 146.6232 | 90.8278
52.0667 | 156.6932 | 119.797 | 146.0432 | 90.7298
53.0667 | 157.4178 | 120.2009 | 146.3275 | 90.6006
54.0667 | 157.6677 | 120.961 | 146.9322 | 90.8956
55.0667 | 157.8724 | 121.7487 | 148.4362 | 91.5331
56.0667 | 159.0988 | 122.3061 | 150.3459 | 93.2831
57.0667 | 160.952 | 123.2454 | 151.3383 | 94.5467
58.0667 | 163.4491 | 124.2097 | 152.6512 | 94.1615
59.0667 | 164.139 | 125.6663 | 154.2074 | 97.1541
60.0667 | 165.6236 | 125.9957 | 155.5789 | 99.2179
61.0667 | 166.08 | 125.8923 | 156.2959 | 100.0809
62.0667 | 166.6292 | 125.8201 | 156.5133 | 102.6878
63.0667 | 167.9312 | 126.0406 | 157.7295 | 103.674
64.0667 | 168.5647 | 126.7697 | 158.977 | 104.7242
65.0667 | 170.1678 | 126.8124 | 158.7958 | 106.226
66.0667 | 171.7585 | 127.4312 | 159.0706 | 106.9575
67.0667 | 173.0053 | 127.36 | 159.4326 | 106.7636
68.0667 | 174.7556 | 127.9291 | 160.395 | 107.249
69.0667 | 175.2837 | 128.7053 | 160.7018 | 109.6434
70.0667 | 176.261 | 129.0183 | 160.5983 | 109.6505
71.0667 | 177.1052 | 129.647 | 161.687 | 112.1623
72.0667 | 176.7359 | 129.8296 | 161.6641 | 112.8299
73.0667 | 177.8397 | 130.0447 | 161.9689 | 113.0737
74.0667 | 179.2157 | 130.1603 | 161.971 | 113.7714
75.0667 | 179.7053 | 130.3636 | 162.061 | 114.0134
76.0667 | 180.5372 | 130.6844 | 161.947 | 114.7204
77.0667 | 180.2724 | 130.4081 | 161.6294 | 114.8477
78.0667 | 179.7 | 130.1037 | 159.9408 | 114.2555
79.0667 | 180.7497 | 130.3636 | 160.2381 | 114.9545
80.0667 | 181.4114 | 130.7101 | 161.2517 | 115.5899
81.0667 | 181.9159 | 130.4213 | 160.6786 | 116.1092
82.0667 | 183.642 | 130.6282 | 161.1106 | 115.4392
83.0667 | 184.5309 | 131.2559 | 162.6723 | 116.1658
84.0667 | 184.6082 | 131.6273 | 162.8845 | 117.5102
85.0667 | 185.6675 | 132.1012 | 163.1881 | 118.0192
86.0667 | 188.023 | 132.4757 | 163.6095 | 119.6377
87.0667 | 189.311 | 132.8682 | 164.2432 | 119.3805
88.0667 | 189.0595 | 132.8743 | 164.8976 | 119.8775
89.0667 | 189.9073 | 133.0047 | 164.4807 | 120.7374
90.0823 | 190.1523 | 133.3906 | 165.863 | 122.2067
91.0667 | 189.8541 | 134.3808 | 166.7357 | 123.0964
92.0667 | 190.2897 | 134.4334 | 166.7343 | 124.8505
93.0667 | 189.9378 | 134.6479 | 167.8628 | 125.6699
94.0667 | 189.3957 | 134.7729 | 168.8926 | 126.3715
95.0667 | 189.5597 | 134.7631 | 170.4674 | 126.5389
96.0667 | 189.1278 | 135.7034 | 170.8718 | 128.0803
97.0667 | 189.7165 | 135.5975 | 172.7445 | 129.5645
98.0667 | 189.1107 | 136.9475 | 173.3791 | 130.229
99.0667 | 190.3076 | 137.5046 | 174.7251 | 130.7899
100.0667 | 192.2025 | 138.4248 | 175.8151 | 131.7246
101.0667 | 195.1794 | 139.0486 | 176.9373 | 132.4712
102.0667 | 197.8873 | 139.5325 | 177.9723 | 134.3668
103.0667 | 197.8743 | 139.872 | 178.4296 | 134.6968
104.0667 | 198.8274 | 140.3642 | 179.9645 | 134.0412
105.0667 | 199.981 | 140.6852 | 181.1204 | 133.5802
106.0667 | 200.9457 | 141.5545 | 182.4406 | 134.2988
107.0667 | 200.8811 | 141.9533 | 182.2618 | 135.9555
108.0667 | 200.6296 | 142.2248 | 182.0916 | 137.9024
109.0667 | 200.8958 | 142.5487 | 183.1919 | 138.184
110.0667 | 200.5451 | 143.4938 | 183.0842 | 139.1357
111.0667 | 201.2092 | 143.333 | 183.6174 | 139.333
112.0667 | 200.1576 | 143.285 | 183.9482 | 138.1925
113.0667 | 198.5477 | 142.8714 | 182.3009 | 138.1278
114.0667 | 197.6275 | 142.4478 | 182.3049 | 137.7937
115.0667 | 197.6218 | 142.0987 | 182.3382 | 137.1335
116.0667 | 197.1554 | 142.4657 | 182.8648 | 137.3127
117.0667 | 197.2472 | 142.7103 | 183.2105 | 137.3614
118.0667 | 197.3171 | 142.5493 | 184.7117 | 137.0479
119.0667 | 196.1563 | 142.7638 | 185.0832 | 136.4449
120.0667 | 194.7487 | 142.8738 | 184.563 | 136.248
121.0667 | 194.4871 | 142.8618 | 185.9212 | 135.0852
122.0667 | 194.6668 | 142.8771 | 185.9103 | 134.8205
123.0667 | 194.5339 | 142.9453 | 185.7058 | 134.9739
124.0667 | 194.0728 | 143.0258 | 185.8907 | 135.1074
125.0667 | 192.9534 | 142.675 | 187.312 | 135.7192
126.0979 | 193.0692 | 142.7084 | 186.1934 | 136.4397
127.0823 | 193.9951 | 142.7692 | 187.8237 | 137.7409
128.0667 | 193.3068 | 142.9056 | 187.9764 | 137.5667
129.0667 | 194.2937 | 142.6789 | 188.2344 | 138.7957
130.0823 | 193.7449 | 142.8079 | 188.4202 | 138.911
131.0667 | 192.8048 | 143.0407 | 188.1728 | 139.2234
132.0667 | 192.9017 | 142.7084 | 186.7875 | 139.0942
133.0667 | 193.8441 | 142.6612 | 186.0557 | 139.6614
134.0667 | 195.9176 | 142.626 | 186.9424 | 140.556
135.0823 | 196.1127 | 142.6791 | 186.5268 | 141.2052
136.0667 | 195.4215 | 142.6334 | 186.5646 | 140.9408
137.0667 | 195.2986 | 143.2309 | 187.3286 | 140.7956
138.0667 | 194.6728 | 143.1963 | 187.2833 | 140.8082
139.0667 | 194.7682 | 143.4183 | 187.6597 | 140.0271
140.0667 | 194.1325 | 143.5453 | 187.6294 | 139.8885
141.0667 | 192.3081 | 143.7175 | 186.4557 | 141.5391
142.0667 | 192.6735 | 143.5212 | 185.8648 | 142.5168
143.0667 | 192.0905 | 143.4544 | 185.5282 | 141.5313
144.0667 | 191.7624 | 143.4069 | 184.0101 | 141.2377
145.0823 | 191.9932 | 144.1377 | 184.9508 | 141.2867
146.0667 | 191.9554 | 144.6806 | 185.098 | 141.8491
147.0667 | 191.0239 | 145.9777 | 185.2448 | 142.9942
148.0667 | 190.9283 | 146.4428 | 185.0911 | 143.8041
149.0667 | 191.9121 | 146.7515 | 186.1376 | 145.0578
150.0667 | 193.3254 | 147.4193 | 186.2894 | 145.6513
151.0667 | 194.5152 | 148.2902 | 187.071 | 145.5592
152.0667 | 196.8827 | 148.8212 | 188.8373 | 146.6345
153.0667 | 197.6668 | 150.2311 | 189.6998 | 148.1802
154.0667 | 198.8783 | 150.1704 | 190.1771 | 148.7912
155.0667 | 199.838 | 150.481 | 190.873 | 149.8501
156.0667 | 201.2585 | 150.5219 | 191.0327 | 151.7635
157.0667 | 201.7656 | 150.2218 | 191.1565 | 151.1875
158.0667 | 202.6667 | 150.234 | 190.7044 | 151.9359
159.0667 | 204.4536 | 149.6497 | 191.7887 | 151.6826
160.0667 | 204.0543 | 149.7676 | 192.5136 | 152.53
161.0667 | 202.7942 | 150.3131 | 191.9652 | 153.6458
162.0667 | 202.1637 | 150.3817 | 192.0149 | 154.4141
163.0667 | 202.3653 | 149.8946 | 192.2241 | 155.2954
164.0667 | 204.6517 | 150.0063 | 193.6645 | 154.8576
165.0667 | 205.4579 | 150.4397 | 193.6912 | 154.9591
166.0667 | 205.0562 | 150.9062 | 193.692 | 155.1649
167.0667 | 204.711 | 151.4448 | 194.4091 | 155.1796
168.0667 | 204.6816 | 151.2816 | 194.2855 | 154.8917
169.0667 | 205.4859 | 150.908 | 194.32 | 154.9265
170.0667 | 205.7988 | 150.872 | 195.2658 | 155.386
171.0667 | 205.387 | 150.766 | 195.4147 | 155.2239
172.0667 | 205.6265 | 150.6703 | 194.5733 | 155.6719
173.0667 | 205.7479 | 150.6155 | 195.382 | 155.5346
174.0667 | 205.1161 | 150.9669 | 195.9981 | 156.0665
175.0667 | 205.9656 | 151.3683 | 196.2901 | 157.8401
176.0667 | 207.2351 | 151.2428 | 197.0672 | 158.0206
177.0667 | 208.5756 | 151.3947 | 197.8165 | 159.3193
178.0823 | 210.0017 | 151.2023 | 197.6447 | 159.0635
179.0823 | 208.7975 | 151.5574 | 197.7155 | 158.5454
180.0667 | 208.913 | 151.7356 | 197.0034 | 159.1698
181.0667 | 208.7606 | 152.1964 | 197.4706 | 157.8714
182.0667 | 209.7349 | 152.134 | 197.2004 | 157.989
183.0667 | 210.736 | 152.7935 | 198.8676 | 157.6483
184.0667 | 210.483 | 154.0769 | 199.2402 | 156.6843
185.0667 | 209.7347 | 154.4566 | 199.1533 | 156.7711
186.0667 | 210.5548 | 156.9763 | 199.7812 | 156.8681
187.0667 | 211.0353 | 157.0649 | 198.9532 | 157.5147
188.0667 | 211.6096 | 157.0066 | 199.4751 | 157.8197
189.0667 | 212.8086 | 157.0743 | 199.816 | 158.0757
190.0667 | 215.1099 | 157.6751 | 202.4049 | 157.9238
191.0667 | 216.2178 | 157.5028 | 204.2405 | 157.9164
192.0667 | 215.4331 | 157.9076 | 203.078 | 158.1576
193.0667 | 214.244 | 158.3499 | 202.6118 | 157.5742
194.0667 | 213.5472 | 157.9786 | 202.1561 | 157.6998
195.0667 | 213.1899 | 157.424 | 201.2432 | 159.0302
196.0667 | 213.4794 | 157.0032 | 202.2865 | 159.6904
197.0667 | 213.7311 | 156.8608 | 201.6155 | 159.4109
198.0667 | 212.8954 | 156.7133 | 201.7209 | 160.3784
199.0667 | 210.9482 | 156.5956 | 201.0132 | 159.8382
200.0667 | 210.3881 | 156.1172 | 199.6635 | 159.3378
201.0667 | 210.4614 | 155.6974 | 199.1185 | 158.4623
202.0667 | 210.0082 | 155.8533 | 199.1882 | 158.9304
203.0667 | 209.611 | 155.8513 | 198.6878 | 158.8182
204.0667 | 209.369 | 155.411 | 197.8779 | 159.1252
205.0667 | 208.9264 | 155.2075 | 198.1316 | 159.6255
206.0667 | 209.2161 | 155.517 | 199.4243 | 161.585
207.0667 | 209.1029 | 157.0215 | 199.3744 | 162.4425
208.0667 | 209.1004 | 158.0986 | 198.9 | 161.5367
209.0667 | 208.897 | 157.8209 | 198.8739 | 162.1293
210.0667 | 209.7329 | 158.2844 | 199.2631 | 162.3662
211.0667 | 208.543 | 159.2855 | 198.4357 | 162.5452
212.0667 | 209.5106 | 159.0718 | 197.0436 | 161.8554
213.0667 | 211.1815 | 159.129 | 196.7577 | 161.3756
214.0667 | 210.3512 | 159.0633 | 196.9317 | 161.1524
215.0667 | 210.6362 | 158.9913 | 198.094 | 160.8782
216.0667 | 210.9205 | 159.558 | 199.4234 | 161.4655
217.0667 | 210.0035 | 159.2278 | 200.1793 | 162.9563
218.0667 | 208.9447 | 160.7113 | 200.7839 | 164.1706
219.0667 | 208.7567 | 160.9322 | 200.4951 | 164.4693
220.0667 | 208.9527 | 161.0604 | 199.8955 | 164.3936
221.0667 | 210.0211 | 161.0124 | 199.5703 | 164.2448
222.0667 | 212.0078 | 160.7363 | 199.6939 | 163.5638
223.0667 | 213.5059 | 160.9203 | 200.6792 | 163.5068
224.0667 | 215.2725 | 161.8524 | 201.6866 | 164.5482
225.0667 | 215.7895 | 163.0093 | 202.8931 | 164.7273
226.0667 | 216.4057 | 162.8945 | 203.8919 | 164.9776
227.0667 | 216.0377 | 164.5175 | 204.5013 | 165.5345
228.0667 | 216.4153 | 164.4867 | 205.1859 | 165.708
229.0667 | 217.8775 | 167.322 | 205.8853 | 165.238
230.0667 | 217.0205 | 167.1136 | 206.2922 | 165.6379
231.0667 | 216.7095 | 166.3044 | 205.0491 | 165.838
232.0667 | 217.7781 | 167.2682 | 205.6148 | 166.5208
233.0667 | 217.6738 | 166.8998 | 205.9965 | 167.3281
234.0667 | 217.3512 | 166.0587 | 205.4716 | 167.5028
235.0667 | 216.8771 | 165.7046 | 205.3178 | 167.1377
236.0667 | 215.7162 | 165.3957 | 204.8017 | 167.778
237.0667 | 215.8239 | 166.4603 | 204.7155 | 169.5616
238.0667 | 216.0235 | 166.4835 | 204.7632 | 170.7907
239.0667 | 217.2325 | 166.7686 | 204.6226 | 170.9558
240.0667 | 216.0786 | 167.0488 | 204.422 | 171.347
241.0667 | 215.0707 | 167.1778 | 204.1653 | 171.0458
242.0667 | 214.9743 | 166.9042 | 204.3107 | 171.2998
243.0667 | 215.2958 | 166.2857 | 203.9342 | 171.5243
244.0667 | 214.87 | 165.93 | 204.4512 | 171.5202
245.0667 | 213.4889 | 165.4007 | 203.6058 | 171.2222
246.0667 | 212.3117 | 164.7446 | 202.1194 | 170.1285
247.0667 | 212.1622 | 164.132 | 201.7221 | 169.1373
248.0667 | 213.3973 | 164.3149 | 202.6148 | 168.5197
249.0667 | 214.9292 | 163.8511 | 202.1695 | 168.1275
250.0667 | 214.9928 | 163.5672 | 200.8076 | 167.4512
251.0667 | 214.6567 | 162.9913 | 200.0348 | 167.8772
252.0667 | 215.0216 | 162.7815 | 200.7118 | 168.5668
253.0667 | 215.3093 | 163.0504 | 200.5585 | 167.8211
254.0667 | 214.552 | 163.5794 | 200.5966 | 169.4229
255.0667 | 214.3406 | 163.6204 | 201.5939 | 169.0067
256.0667 | 214.1407 | 163.7408 | 202.4874 | 169.7391
257.0667 | 214.6291 | 164.1918 | 203.4403 | 171.1689
258.0667 | 213.874 | 164.3974 | 204.0202 | 171.4653
259.0667 | 213.3145 | 164.2618 | 203.2063 | 170.5204
260.0667 | 212.9696 | 165.0597 | 202.9257 | 171.3264
261.0667 | 214.1193 | 164.6861 | 202.8535 | 170.4503
262.0667 | 213.7251 | 165.2418 | 203.2164 | 170.5448
263.0667 | 213.0702 | 165.0808 | 203.1329 | 171.3601
264.0667 | 212.9076 | 164.5702 | 203.6889 | 170.8684
265.0667 | 212.1403 | 166.0408 | 203.8508 | 171.1066
266.0667 | 212.3186 | 166.1001 | 203.4831 | 170.8015
267.0667 | 213.429 | 165.762 | 202.6966 | 169.5801
268.0667 | 213.7878 | 165.6152 | 201.8337 | 169.5659
269.0667 | 215.345 | 165.3504 | 201.0967 | 169.1647
270.0667 | 215.3326 | 165.0447 | 201.2325 | 169.3786
271.0667 | 215.6161 | 165.031 | 201.7749 | 170.4089
272.0667 | 214.9847 | 164.6605 | 202.7552 | 171.3325
273.0667 | 213.7622 | 166.0323 | 202.7645 | 171.25
274.0667 | 214.7328 | 167.9242 | 203.9368 | 171.0337
275.0667 | 214.4653 | 168.384 | 204.9947 | 170.9811
276.0667 | 213.8153 | 168.7123 | 205.3293 | 171.114
277.0667 | 214.676 | 168.3099 | 205.1837 | 171.7296
278.0667 | 215.1174 | 168.5928 | 206.3169 | 171.4004
279.0667 | 216.6609 | 168.838 | 207.5221 | 171.6363
280.0667 | 217.5027 | 168.8276 | 208.3528 | 171.2097
281.0667 | 218.007 | 169.4743 | 208.2388 | 172.4579
282.0667 | 217.511 | 169.1965 | 208.9262 | 173.5418
283.0667 | 217.4488 | 169.2713 | 208.3515 | 173.4707
284.0667 | 218.1715 | 168.8073 | 208.4604 | 174.0629
285.0667 | 219.1696 | 168.6436 | 208.4183 | 174.1879
286.0667 | 221.5767 | 168.655 | 208.5189 | 174.9204
287.0667 | 222.1604 | 168.9333 | 209.48 | 175.2776
288.0667 | 223.7078 | 168.7289 | 209.5498 | 174.8799
289.0667 | 224.3343 | 169.5926 | 210.2595 | 174.8554
290.0667 | 225.4207 | 169.7667 | 210.5002 | 175.4299
291.0667 | 224.5983 | 169.5957 | 210.138 | 174.0217
292.0667 | 223.4267 | 169.5369 | 209.2354 | 174.6388
293.0667 | 223.0942 | 169.869 | 208.9426 | 175.5155
294.0667 | 223.659 | 170.3319 | 209.3005 | 174.8833
295.0667 | 223.6936 | 170.5101 | 208.8424 | 174.8997
296.0667 | 225.5251 | 170.3744 | 207.8528 | 174.5147
297.0667 | 225.885 | 169.8368 | 208.6294 | 175.0451
298.0667 | 226.9803 | 169.2565 | 208.273 | 174.6115
299.0667 | 227.0669 | 168.8265 | 208.0686 | 173.4034
300.0667 | 227.3118 | 168.6417 | 207.955 | 172.9069
301.0667 | 228.1795 | 168.3867 | 206.5704 | 172.7102
302.0667 | 228.6372 | 168.3862 | 206.8314 | 172.193
303.0823 | 229.8566 | 168.3541 | 207.5274 | 172.8287
304.0823 | 230.2122 | 168.431 | 207.116 | 173.1625
305.0667 | 230.258 | 169.3377 | 208.4775 | 173.1977
306.0667 | 231.5056 | 168.8704 | 209.0031 | 173.7762
307.0667 | 231.3361 | 169.2479 | 208.9694 | 172.5811
308.0667 | 231.7388 | 170.6501 | 209.5676 | 173.5787
309.0667 | 231.9628 | 171.9023 | 209.8152 | 175.4709
310.0667 | 231.4106 | 171.9938 | 209.8858 | 175.0802
311.0667 | 231.6246 | 173.6033 | 210.6891 | 174.7024
312.0667 | 230.7449 | 174.5751 | 211.724 | 175.2286
313.0667 | 229.5912 | 174.9093 | 212.2926 | 176.2286
314.0667 | 229.4468 | 174.5019 | 212.0083 | 175.7729
315.0667 | 229.5873 | 174.2364 | 212.1349 | 175.5891
316.0667 | 230.2231 | 173.7861 | 212.8051 | 174.8023
317.0667 | 230.663 | 173.248 | 211.5142 | 174.6822
318.0667 | 230.6191 | 172.5934 | 210.6465 | 173.8696
319.0667 | 231.0209 | 171.9441 | 209.6323 | 173.6254
320.0667 | 230.724 | 171.7958 | 209.1922 | 173.5186
321.0667 | 230.7197 | 171.5637 | 208.7045 | 176.022
322.0667 | 230.3963 | 171.2205 | 208.1738 | 177.5171
323.0667 | 230.9904 | 171.4276 | 208.6286 | 177.4008
324.0667 | 230.8511 | 171.123 | 208.5866 | 178.1172
325.0667 | 231.217 | 171.3792 | 207.6999 | 178.1521
326.0667 | 232.1389 | 171.1552 | 207.5641 | 177.7691
327.0667 | 232.7318 | 171.1357 | 208.3746 | 178.8035
328.0667 | 232.6376 | 172.4174 | 208.3313 | 178.6926
329.0667 | 232.1648 | 173.2447 | 208.2683 | 177.8426
330.0667 | 231.8412 | 173.3005 | 208.8875 | 177.6276
331.0667 | 231.8251 | 172.7203 | 209.3406 | 177.4484
332.0667 | 231.4453 | 172.3208 | 209.5012 | 178.2106
333.0667 | 230.9633 | 171.8245 | 209.921 | 179.6062
334.0667 | 231.1247 | 171.8794 | 210.6549 | 180.2517
335.0667 | 231.3215 | 172.502 | 210.7157 | 182.7829
336.0667 | 231.1226 | 171.9576 | 209.729 | 182.2257
337.0667 | 231.6384 | 171.8479 | 210.1033 | 183.0827
338.0667 | 232.5199 | 172.7674 | 212.1111 | 184.3756
339.0667 | 234.7522 | 173.3821 | 211.4203 | 183.8167
340.0667 | 234.9237 | 173.1082 | 211.5542 | 183.6997
341.0667 | 234.91 | 172.5589 | 210.9066 | 182.5398
342.0667 | 234.0196 | 171.9894 | 210.2853 | 183.8565
343.0667 | 233.4791 | 171.6505 | 210.6294 | 183.114
344.0823 | 233.0592 | 171.6916 | 210.947 | 183.8017
345.0667 | 232.9003 | 171.3609 | 211.2772 | 182.6249
346.0667 | 232.5732 | 171.1111 | 210.9982 | 182.431
347.0667 | 232.6185 | 171.1439 | 211.3526 | 181.7729
348.0667 | 232.1858 | 171.8493 | 212.5431 | 180.7091
349.0667 | 232.5908 | 172.6556 | 213.1857 | 180.2568
350.0667 | 231.9329 | 173.3113 | 214.4749 | 180.6045
351.0667 | 231.827 | 173.4646 | 215.2985 | 179.7842
352.0667 | 231.1903 | 174.5838 | 215.849 | 180.2067
353.0667 | 231.0652 | 175.8746 | 217.6494 | 180.5553
354.0667 | 230.3524 | 176.2767 | 218.2461 | 179.8602
355.0667 | 230.0752 | 175.7979 | 219.0636 | 179.6634
356.0667 | 229.7096 | 175.3948 | 217.8506 | 180.5174
357.0667 | 229.1107 | 175.2947 | 217.1502 | 181.2862
358.0667 | 229.0716 | 174.8668 | 215.9048 | 181.8447
359.0667 | 229.0719 | 174.7855 | 215.1241 | 181.1749
360.0667 | 228.1682 | 174.313 | 216.2495 | 180.7014
361.0667 | 227.7825 | 174.5914 | 216.1987 | 180.8939
362.0667 | 228.0862 | 174.1902 | 215.9227 | 180.605
363.0667 | 228.9376 | 174.4756 | 216.6357 | 180.7399
364.0667 | 229.9249 | 174.8886 | 217.0426 | 182.5276
365.0667 | 229.8467 | 174.4786 | 216.2063 | 181.1176
366.0667 | 230.088 | 174.7178 | 216.4979 | 181.4098
367.0667 | 230.6772 | 174.7654 | 216.4142 | 182.416
368.0823 | 232.1315 | 174.0531 | 215.6388 | 181.7787
369.0667 | 233.1367 | 173.3212 | 215.1395 | 181.2718
370.0667 | 232.2867 | 174.0868 | 215.7341 | 181.0421
371.0667 | 232.8458 | 174.3513 | 216.8609 | 181.5446
372.0667 | 232.2034 | 174.093 | 216.0588 | 181.4235
373.0667 | 232.7193 | 174.1353 | 215.4135 | 180.5065
374.0823 | 233.4055 | 174.971 | 216.1502 | 180.9582
375.0667 | 232.9728 | 175.4114 | 217.9236 | 180.7457
376.0667 | 232.2302 | 175.7225 | 217.7545 | 180.9752
377.0667 | 233.0014 | 175.198 | 217.7467 | 181.7598
378.0667 | 233.0843 | 175.2911 | 218.2053 | 182.0427
379.0667 | 234.0385 | 176.0181 | 218.5029 | 183.0685
380.0667 | 233.4692 | 176.3941 | 218.2124 | 183.9946
381.0667 | 234.2501 | 176.1086 | 217.4297 | 183.469
382.0667 | 234.9935 | 176.352 | 217.3337 | 184.4134
383.0667 | 236.5164 | 175.8749 | 217.4047 | 184.1611
384.0667 | 235.7378 | 176.5123 | 218.3885 | 183.7891
385.0667 | 235.1146 | 176.485 | 217.3362 | 184.2894
386.0667 | 235.8978 | 176.4995 | 217.2558 | 184.0203
387.0667 | 235.4816 | 177.3323 | 217.2933 | 183.8621
388.0667 | 234.4574 | 177.3964 | 217.5969 | 184.1369
389.0667 | 234.1444 | 179.7561 | 218.4152 | 183.7505
390.0667 | 234.0578 | 180.5007 | 219.8605 | 183.8265
391.0667 | 233.8852 | 180.7575 | 220.606 | 184.4004
392.0667 | 233.3435 | 180.7156 | 220.1875 | 184.0041
393.0823 | 233.7611 | 180.6632 | 220.0195 | 183.3942
394.0823 | 235.114 | 180.3174 | 219.31 | 182.5807
395.0667 | 235.8363 | 179.8745 | 218.9562 | 183.2011
396.0667 | 237.2118 | 179.5963 | 217.3318 | 182.5674
397.0667 | 237.6671 | 179.0648 | 218.1146 | 182.6716
398.0667 | 238.1605 | 180.1355 | 218.7998 | 182.2876
399.0667 | 237.9157 | 180.4163 | 219.1479 | 182.0019
400.0667 | 237.3528 | 180.4941 | 220.5366 | 181.3109
401.0667 | 237.7915 | 180.1387 | 221.1044 | 181.7257
402.0667 | 237.1505 | 180.4516 | 221.169 | 181.0658
403.0667 | 236.1211 | 182.1043 | 221.4001 | 180.6806
404.0823 | 235.3238 | 182.2605 | 221.1826 | 180.2605
405.0667 | 235.3256 | 181.234 | 220.1241 | 180.5176
406.0667 | 234.6212 | 180.9958 | 221.025 | 181.5657
407.0667 | 234.8092 | 181.2595 | 221.6034 | 182.1278
408.0667 | 233.8119 | 181.5464 | 221.4499 | 182.79
409.0667 | 233.5055 | 180.9274 | 221.5771 | 182.2562
410.0667 | 234.0041 | 180.4523 | 222.4784 | 184.3375
411.0667 | 235.1228 | 180.5554 | 222.2923 | 185.6822
412.0667 | 236.9381 | 180.7999 | 222.5761 | 185.0934
413.0667 | 237.0229 | 181.2276 | 223.3064 | 184.816
414.0667 | 235.8442 | 181.1288 | 222.853 | 185.6659
415.0667 | 235.5868 | 180.5819 | 221.0055 | 184.0763
416.0667 | 235.9665 | 180.1845 | 221.171 | 184.4536
417.0667 | 235.4136 | 179.4413 | 221.3671 | 185.1993
418.0667 | 234.3952 | 179.1031 | 221.2326 | 185.6996
419.0667 | 234.6153 | 178.6418 | 220.7849 | 184.6071
420.0667 | 234.2971 | 178.1296 | 219.9435 | 184.2882
421.0667 | 234.7912 | 177.8182 | 219.0871 | 183.9294
422.0667 | 234.7596 | 177.63 | 219.203 | 184.7679
423.0667 | 234.1753 | 177.7272 | 218.6699 | 185.3679
424.0667 | 234.6797 | 177.5317 | 217.6822 | 186.0866
425.0667 | 234.8801 | 177.2301 | 217.164 | 185.6179
426.0667 | 234.0602 | 177.0857 | 215.9124 | 185.2737
427.0667 | 233.4721 | 176.7771 | 215.4552 | 184.9754
428.0667 | 233.2337 | 176.8939 | 216.0241 | 186.2569
429.0667 | 233.2767 | 177.9786 | 216.2398 | 186.9129
430.0667 | 232.6788 | 178.9483 | 216.3457 | 185.9481
431.0667 | 232.3824 | 179.0268 | 217.7931 | 185.7711
432.0667 | 231.7593 | 179.272 | 218.578 | 185.362
433.0667 | 231.0059 | 179.7141 | 219.2 | 185.641
434.0667 | 231.0399 | 180.3841 | 219.1624 | 185.0383
435.0667 | 230.8314 | 181.7506 | 220.3181 | 184.4779
436.0667 | 231.5811 | 182.8484 | 220.5381 | 183.8364
437.0667 | 232.4815 | 182.7948 | 220.6054 | 183.3623
438.0667 | 232.4384 | 182.1295 | 220.4771 | 182.6536
439.0667 | 232.6679 | 181.6868 | 219.3567 | 182.0011
440.0667 | 233.8365 | 181.6414 | 218.8773 | 181.0527
441.0667 | 233.1956 | 181.6898 | 217.3215 | 179.5584
442.0667 | 232.8443 | 181.544 | 217.3565 | 178.9629
443.0667 | 232.1056 | 181.3051 | 218.0555 | 179.1038
444.0667 | 231.8781 | 182.03 | 219.3958 | 178.7185
445.0667 | 232.5354 | 182.8373 | 219.8124 | 178.3616
446.0667 | 234.497 | 183.9242 | 220.2233 | 177.2824
447.0667 | 236.051 | 184.9308 | 220.5668 | 176.6402
448.0667 | 236.9892 | 185.4393 | 221.4361 | 176.0962
449.0667 | 237.5067 | 186.3485 | 222.61 | 176.0791
450.0667 | 238.0715 | 187.2774 | 223.7512 | 175.1959
451.0667 | 238.2708 | 189.1996 | 224.8158 | 175.0203
452.0667 | 239.3771 | 190.0465 | 225.7407 | 174.9825
453.0667 | 240.2962 | 190.293 | 226.9544 | 175.0853
454.0667 | 240.4222 | 190.1324 | 227.1531 | 175.205
455.0667 | 239.7865 | 190.2714 | 227.4286 | 175.5537
456.0667 | 240.1416 | 190.6729 | 227.1929 | 175.8864
457.0667 | 241.1096 | 190.7356 | 228.2628 | 176.9495
458.0667 | 242.4357 | 190.4413 | 227.4637 | 175.9351
459.0667 | 242.7908 | 190.7514 | 227.7931 | 176.2595
460.0667 | 243.5833 | 191.556 | 228.5577 | 176.5344
461.0667 | 245.1029 | 192.331 | 229.6718 | 175.8814
462.0667 | 245.7237 | 192.0728 | 231.1384 | 175.7419
463.0667 | 245.4557 | 191.8017 | 230.7577 | 175.1915
464.0667 | 245.1771 | 191.3962 | 229.2423 | 175.8082
465.0667 | 245.2499 | 190.9932 | 229.1923 | 178.2135
466.0667 | 244.9399 | 191.1745 | 230.0578 | 178.478
467.0667 | 245.1059 | 191.5816 | 232.0182 | 180.4664
468.0667 | 245.4826 | 192.3504 | 232.4207 | 181.8692
469.0667 | 245.4073 | 192.5615 | 232.8923 | 182.1971
470.0667 | 246.0144 | 192.4157 | 233.4101 | 182.1445
471.0667 | 247.0631 | 192.0053 | 233.043 | 182.873
472.0667 | 247.3827 | 191.5159 | 233.5789 | 183.1742
473.0667 | 248.9994 | 191.0119 | 233.9569 | 183.7853
474.0667 | 248.463 | 190.7991 | 233.6392 | 184.9726
475.0667 | 248.46 | 190.3155 | 232.9409 | 186.0116
476.0667 | 248.2654 | 189.6456 | 231.5542 | 186.0966
477.0667 | 249.4667 | 189.6074 | 231.8366 | 186.1784
478.0667 | 249.9998 | 189.7754 | 233.5575 | 185.5568
479.0667 | 250.8171 | 190.6873 | 234.8153 | 185.052
480.0667 | 250.713 | 190.894 | 235.3289 | 184.9613
481.0667 | 251.2669 | 191.4648 | 235.7513 | 183.9109
482.0667 | 251.5212 | 193.0863 | 236.6491 | 182.8319
483.0667 | 251.5887 | 194.4247 | 238.4151 | 182.763
484.0667 | 251.6824 | 196.0554 | 240.0531 | 182.2859
485.0667 | 251.2915 | 197.4365 | 239.5907 | 181.0254
486.0667 | 251.0432 | 198.4616 | 239.7337 | 180.886
487.0667 | 251.5091 | 200.0852 | 240.9491 | 180.3445
488.0667 | 252.3729 | 201.2539 | 241.5495 | 180.2358
489.0667 | 252.6062 | 201.2759 | 241.6849 | 179.6784
490.0667 | 252.3202 | 201.8415 | 241.8803 | 180.0249
491.0667 | 252.8439 | 201.8848 | 242.8153 | 179.9503
492.0667 | 253.9526 | 202.3626 | 243.8556 | 179.7072
493.0667 | 254.4797 | 202.2886 | 244.1641 | 179.244
494.0823 | 255.8317 | 203.027 | 245.1791 | 178.7502
495.0667 | 256.3852 | 204.5937 | 246.2465 | 179.1354
496.0667 | 258.7491 | 206.4683 | 244.9998 | 178.8115
497.0667 | 257.2807 | 206.8004 | 246.2025 | 179.4821
498.0667 | 257.0499 | 207.2104 | 246.9838 | 179.835
499.0667 | 256.9524 | 207.6336 | 247.958 | 179.4803
500.0667 | 258.1197 | 208.4769 | 247.3929 | 180.1173
501.0667 | 258.8246 | 208.5883 | 248.0979 | 180.8823
502.0667 | 259.0201 | 208.3811 | 247.8732 | 180.7858
503.0667 | 260.9431 | 208.2684 | 248.927 | 180.0458
504.0667 | 261.0004 | 208.7612 | 250.9396 | 179.7264
505.0667 | 264.3336 | 209.7659 | 250.872 | 179.3715
506.0667 | 265.4816 | 209.2136 | 252.0769 | 178.4835
507.0667 | 263.9467 | 208.7981 | 252.922 | 177.9459
508.0667 | 263.4364 | 208.1428 | 251.9537 | 177.3245
509.0667 | 262.9366 | 207.5506 | 251.868 | 176.545
510.0667 | 261.8583 | 207.3459 | 250.7173 | 176.8423
511.0667 | 261.0595 | 207.8828 | 251.5949 | 178.0723
512.0667 | 261.2521 | 209.8765 | 252.6647 | 179.209
513.0667 | 260.7396 | 211.4185 | 253.5595 | 181.8043
514.0667 | 260.3329 | 211.7899 | 253.6278 | 183.2065
515.0667 | 260.406 | 210.9388 | 252.6676 | 184.7618
516.0823 | 260.6648 | 210.6431 | 253.3625 | 185.8187
517.0823 | 260.6023 | 210.1779 | 252.6896 | 185.8116
518.0667 | 260.5924 | 210.871 | 252.5053 | 185.5995
519.0667 | 260.4454 | 211.7093 | 252.4559 | 186.1913
520.0667 | 260.7973 | 212.2595 | 252.1154 | 188.5165
521.0823 | 260.922 | 212.4579 | 251.5452 | 188.8306
522.0667 | 260.7128 | 212.3801 | 253.0656 | 188.9291
523.0823 | 259.8722 | 212.2041 | 252.8476 | 187.9786
524.0823 | 259.6138 | 212.891 | 253.1298 | 186.9833
525.0667 | 258.9317 | 212.5222 | 254.4387 | 187.1064
526.0667 | 258.6799 | 212.6027 | 256.2863 | 188.5253
527.0667 | 258.3867 | 211.7793 | 256.1471 | 188.2351
528.0667 | 257.8048 | 211.8515 | 256.6445 | 188.2359
529.0667 | 257.5761 | 211.412 | 256.3589 | 188.5089
530.0667 | 258.517 | 211.968 | 256.0644 | 188.5843
531.0667 | 260.9406 | 213.5568 | 255.8072 | 188.6201
532.0667 | 263.0956 | 214.7189 | 256.296 | 187.8715
533.0667 | 262.9074 | 214.3223 | 256.5867 | 186.6428
534.0667 | 263.4112 | 213.8576 | 256.1733 | 185.7902
535.0667 | 264.2594 | 215.2464 | 256.9684 | 184.96
536.0667 | 265.5381 | 214.5396 | 257.0744 | 183.7299
537.0667 | 265.4397 | 214.196 | 257.4185 | 182.7373
538.0667 | 265.4813 | 215.2015 | 257.5235 | 183.2777
539.0667 | 265.7873 | 215.4686 | 257.5567 | 183.7247
540.0667 | 265.0039 | 217.8114 | 258.2844 | 185.5352
541.0667 | 265.3905 | 219.4875 | 258.3093 | 186.0962
542.0667 | 265.6408 | 219.5051 | 258.4666 | 188.4493
543.0667 | 265.968 | 219.6229 | 259.5542 | 188.5813
544.0667 | 265.8265 | 220.8646 | 259.8928 | 188.2458
545.0667 | 266.5602 | 221.4959 | 260.7978 | 188.5374
546.0667 | 266.3842 | 221.2252 | 261.1171 | 189.98
547.0667 | 267.1977 | 220.8218 | 261.57 | 189.6216
548.0667 | 267.0949 | 220.328 | 262.4103 | 189.7231
549.0667 | 266.7019 | 219.5789 | 261.7058 | 190.813
550.0667 | 265.8413 | 219.2877 | 260.5897 | 191.822
551.0667 | 265.7851 | 218.2157 | 259.8531 | 192.8661
552.0823 | 265.1913 | 217.2541 | 259.6688 | 192.1767
553.0667 | 265.1381 | 216.8662 | 258.9725 | 191.6798
554.0823 | 264.5841 | 216.219 | 258.7179 | 192.7513
555.0667 | 264.2975 | 215.6178 | 259.3603 | 192.2118
556.0667 | 264.4381 | 214.9352 | 258.6907 | 192.3155
557.0667 | 264.3241 | 214.0776 | 258.9807 | 192.3212
558.0667 | 264.6361 | 213.9546 | 258.2308 | 193.3107
559.0823 | 265.3024 | 213.4011 | 257.9574 | 193.3077
560.0667 | 266.3491 | 213.9952 | 258.3891 | 195.5763
561.0667 | 266.8151 | 213.6127 | 258.4851 | 195.9154
562.0823 | 267.4439 | 213.3542 | 258.8756 | 195.8317
563.0667 | 267.8618 | 213.4823 | 259.8746 | 195.36
564.0667 | 268.0967 | 213.3339 | 260.6191 | 195.5948
565.0667 | 267.5464 | 213.109 | 260.6633 | 196.2752
566.0667 | 267.0791 | 213.029 | 261.0472 | 196.7471
567.0667 | 267.2887 | 212.5726 | 261.1031 | 197.7913
568.0667 | 267.1596 | 212.1592 | 260.9347 | 199.4442
569.0667 | 267.7824 | 211.4228 | 260.9428 | 199.91
570.0667 | 268.4756 | 211.4918 | 260.9018 | 200.0276
571.0667 | 268.7583 | 211.3222 | 260.9394 | 199.7442
572.0667 | 269.3109 | 211.1925 | 261.0841 | 199.6246
573.0667 | 269.3694 | 210.357 | 260.7621 | 199.2777
574.0667 | 269.5399 | 209.8319 | 260.2836 | 199.2834
575.0667 | 269.3006 | 210.2282 | 260.497 | 199.4469
576.0667 | 268.6455 | 209.9181 | 260.3565 | 199.4164
577.0667 | 268.6629 | 209.2964 | 259.9617 | 199.9515
578.0667 | 268.6067 | 209.1222 | 259.6099 | 199.6343
579.0667 | 269.6865 | 209.6583 | 260.9258 | 200.02
580.0667 | 269.388 | 210.2694 | 262.2081 | 200.6992
581.0667 | 269.5107 | 210.0999 | 262.2708 | 199.9001
582.0667 | 270.0258 | 210.4878 | 263.095 | 199.789
583.0667 | 271.5097 | 211.3975 | 263.0643 | 199.7328
584.0823 | 272.6321 | 211.1791 | 262.5176 | 199.7052
585.0667 | 272.592 | 210.649 | 263.3514 | 199.0933
586.0667 | 272.4562 | 210.1376 | 262.6197 | 199.7283
587.0667 | 273.2091 | 210.2704 | 263.2784 | 200.1115
588.0667 | 273.3971 | 210.0956 | 263.2662 | 199.3856
589.0667 | 272.7213 | 210.0127 | 262.4645 | 199.7184
590.0667 | 272.8048 | 210.3216 | 262.7487 | 199.6122
591.0667 | 272.177 | 210.5175 | 263.0389 | 199.4066
592.0667 | 272.4561 | 210.6712 | 264.3257 | 199.9359
593.0667 | 271.8796 | 211.6066 | 262.511 | 199.6083
594.0667 | 271.6773 | 212.4468 | 263.059 | 199.0057
595.0667 | 272.012 | 212.735 | 262.4666 | 198.7392
596.0667 | 272.6425 | 212.6585 | 263.1658 | 197.8715
597.0667 | 273.133 | 211.9499 | 264.1764 | 197.3533
598.0667 | 272.9964 | 211.2476 | 264.9667 | 196.631
599.0667 | 273.5178 | 210.8841 | 264.4965 | 195.5988
600.0667 | 274.3262 | 210.7481 | 264.9509 | 194.988
601.0667 | 274.3695 | 210.9588 | 264.8678 | 194.2476
602.0667 | 273.656 | 211.6628 | 265.9865 | 194.0599
603.0667 | 274.5823 | 211.299 | 266.2968 | 194.2276
604.0667 | 274.42 | 211.267 | 265.8134 | 194.1621
605.0667 | 274.9961 | 212.421 | 266.2038 | 194.9058
606.0667 | 276.0377 | 213.5185 | 266.8378 | 195.3615
607.0667 | 275.5124 | 215.2201 | 266.7447 | 196.2041
608.0667 | 275.209 | 215.3585 | 266.4991 | 196.2259
609.0667 | 274.9004 | 215.1464 | 266.6672 | 197.1443
610.0667 | 274.3422 | 214.8703 | 266.607 | 196.6689
611.0667 | 274.9484 | 215.5871 | 267.1148 | 197.0005
612.0667 | 275.9121 | 217.8216 | 266.9373 | 196.8414
613.0667 | 276.8627 | 220.141 | 267.4175 | 197.5807
614.0667 | 276.9638 | 221.0531 | 268.5103 | 197.7757
615.0667 | 276.8638 | 221.552 | 268.5916 | 196.9316
616.0667 | 276.0467 | 222.0814 | 267.6738 | 196.3359
617.0667 | 275.6102 | 221.8026 | 267.2646 | 196.0757
618.0667 | 275.301 | 221.5315 | 267.0679 | 195.7621
619.0667 | 274.8943 | 222.0494 | 267.3159 | 195.6213
620.0667 | 276.066 | 222.5088 | 268.4059 | 195.0805
621.0667 | 276.4697 | 222.7509 | 269.42 | 194.6558
622.0667 | 277.6362 | 221.5994 | 269.4926 | 194.6027
623.0667 | 278.0511 | 221.2813 | 269.8611 | 195.3642
624.0667 | 278.426 | 221.335 | 269.7745 | 196.0067
625.0667 | 278.5558 | 221.2245 | 271.6475 | 195.524
626.0667 | 279.8529 | 221.6099 | 271.8439 | 196.0728
627.0667 | 280.4791 | 221.2681 | 272.5057 | 195.3944
628.0667 | 280.3421 | 222.4133 | 271.7827 | 194.7792
629.0667 | 280.6153 | 223.6343 | 272.1253 | 194.9143
630.0667 | 280.8455 | 223.8627 | 272.3894 | 195.129
631.0667 | 279.6419 | 224.2048 | 272.6971 | 194.9771
632.0667 | 279.9819 | 223.8186 | 272.4553 | 195.3261
633.0667 | 279.4161 | 223.008 | 272.2457 | 195.2345
634.0667 | 278.9675 | 222.2773 | 272.407 | 195.1246
635.0667 | 278.5141 | 221.9876 | 272.2505 | 195.531
636.0667 | 278.3144 | 222.7141 | 271.5297 | 197.2643
637.0667 | 278.5433 | 222.2115 | 271.0444 | 197.4082
638.0667 | 278.6391 | 221.5846 | 270.7023 | 197.1841
639.0667 | 278.7428 | 222.0739 | 270.9932 | 198.1403
640.0667 | 278.4837 | 221.1908 | 270.896 | 199.2698
641.0667 | 278.4424 | 220.7539 | 270.4707 | 200.7179
642.0667 | 277.8791 | 220.3676 | 270.2508 | 200.3799
643.0667 | 276.9473 | 220.0066 | 270.2508 | 200.0609
644.0667 | 276.7841 | 219.3443 | 269.3401 | 199.416
645.0667 | 277.2389 | 219.0389 | 269.5729 | 199.3235
646.0667 | 277.8042 | 218.6311 | 269.9863 | 199.1908
647.0667 | 279.1868 | 219.6447 | 270.1552 | 200.0802
648.0667 | 278.8588 | 220.2787 | 270.4858 | 199.5141
649.0667 | 278.35 | 220.166 | 269.9366 | 199.4884
650.0667 | 277.4476 | 220.1248 | 269.1368 | 199.3607
651.0667 | 276.4142 | 220.1224 | 268.7722 | 199.3947
652.0667 | 277.4131 | 219.8854 | 268.4719 | 199.0811
653.0667 | 276.8966 | 219.2408 | 268.5759 | 199.3805
654.0667 | 275.3534 | 219.6996 | 267.8275 | 199.1911
655.0667 | 274.677 | 219.5436 | 266.9414 | 199.0468
656.0667 | 275.449 | 219.0151 | 266.6387 | 198.7779
657.0667 | 275.8474 | 218.1189 | 266.5242 | 197.9581
658.0667 | 276.0214 | 218.7077 | 266.3682 | 197.5529
659.0667 | 276.7071 | 219.8911 | 265.2195 | 197.3462
660.0667 | 277.5385 | 220.4197 | 266.2215 | 197.3519
661.0667 | 279.1563 | 221.7415 | 266.5903 | 196.4858
662.0667 | 280.4757 | 221.9949 | 266.2517 | 195.6984
663.0667 | 280.0035 | 221.3419 | 265.7771 | 195.3775
664.0667 | 279.1289 | 221.5867 | 266.508 | 196.5253
665.0667 | 278.248 | 220.5571 | 266.5774 | 197.4214
666.0667 | 277.1734 | 220.0513 | 266.9246 | 197.2813
667.0667 | 276.3979 | 219.6844 | 267.5375 | 197.1812
668.0667 | 276.4288 | 220.6336 | 268.1855 | 197.9609
669.0667 | 276.5877 | 219.9841 | 268.2762 | 198.1706
670.0667 | 275.9905 | 220.0425 | 268.4958 | 198.6292
671.0667 | 275.189 | 220.6645 | 268.3452 | 198.1727
672.0667 | 273.9519 | 220.2939 | 268.4814 | 198.449
673.0667 | 273.7785 | 219.8595 | 269.2329 | 197.8874
674.0667 | 275.0096 | 219.0209 | 268.6465 | 197.2221
675.0667 | 274.4847 | 219.1899 | 268.9988 | 196.1361
676.0667 | 273.9647 | 220.5566 | 268.3734 | 196.0074
677.0667 | 274.6204 | 220.6137 | 268.182 | 196.7138
678.0667 | 274.9237 | 221.0014 | 267.2769 | 195.892
679.0667 | 275.9822 | 220.9063 | 266.4639 | 195.0625
680.0667 | 277.0695 | 220.2928 | 266.7468 | 194.4846
681.0667 | 277.4421 | 221.0663 | 268.7327 | 194.1383
682.0667 | 276.4594 | 220.8128 | 267.7607 | 193.6242
683.0667 | 276.1463 | 220.8118 | 267.2581 | 192.9807
684.0667 | 276.8009 | 221.488 | 267.6794 | 193.5746
685.0667 | 276.7554 | 221.3876 | 268.457 | 193.3975
686.0667 | 277.2424 | 222.0242 | 268.5234 | 194.846
687.0667 | 277.8526 | 221.6477 | 268.4964 | 194.7861
688.0667 | 278.2286 | 223.3953 | 269.0108 | 194.7773
689.0667 | 279.2501 | 224.2594 | 269.4861 | 195.0238
690.0667 | 280.1405 | 225.6049 | 270.871 | 195.2954
691.0667 | 281.6788 | 224.8516 | 270.1986 | 194.8404
692.0667 | 283.4749 | 225.6581 | 270.3122 | 194.2284
693.0667 | 283.3704 | 225.3255 | 271.1053 | 193.9183
694.0667 | 282.7068 | 225.0769 | 270.499 | 193.6747
695.0667 | 281.0209 | 225.6446 | 270.3181 | 193.9457
696.0667 | 280.2819 | 227.2547 | 270.4731 | 193.9313
697.0667 | 280.8661 | 229.7042 | 271.4183 | 194.8866
698.0667 | 281.2801 | 230.0437 | 270.7446 | 196.3881
699.0667 | 280.5489 | 230.253 | 270.9449 | 197.9349
700.0667 | 279.9716 | 229.4001 | 270.3947 | 197.6446
701.0667 | 279.9147 | 229.0112 | 270.7617 | 197.8074
702.0667 | 280.1813 | 228.6916 | 271.0898 | 198.3529
703.0667 | 279.5393 | 229.3241 | 270.8585 | 198.856
704.0667 | 279.6374 | 228.8651 | 270.4052 | 198.5325
705.0667 | 279.3815 | 229.8147 | 270.0083 | 198.9043
706.0667 | 279.9464 | 228.7359 | 269.0454 | 198.968
707.0667 | 279.558 | 228.557 | 269.6327 | 198.9107
708.0667 | 279.2928 | 228.6292 | 271.1569 | 199.1581
709.0667 | 278.9532 | 227.9731 | 271.1513 | 197.9541
710.0667 | 279.4063 | 227.0746 | 270.7543 | 197.0726
711.0667 | 278.8157 | 225.9191 | 271.7592 | 196.875
712.0667 | 277.2894 | 225.0884 | 271.8415 | 197.3654
713.0667 | 277.4344 | 225.3873 | 271.0599 | 197.5846
714.0667 | 278.6425 | 226.0438 | 270.7372 | 197.7797
715.0667 | 280.8342 | 227.5885 | 272.2855 | 198.2415
716.0667 | 279.5929 | 228.1319 | 272.5207 | 198.4584
717.0667 | 279.2267 | 227.9609 | 271.6044 | 198.2236
718.0667 | 280.8086 | 228.1624 | 272.2639 | 197.9034
719.0667 | 280.2959 | 227.9497 | 273.023 | 198.6523
720.0667 | 280.6166 | 229.3288 | 273.2253 | 197.8292
721.0667 | 281.0417 | 228.3164 | 273.9048 | 197.6089
722.0667 | 281.4121 | 227.3525 | 273.8594 | 196.9003
723.0667 | 282.1412 | 226.9724 | 274.3724 | 197.7794
724.0667 | 281.3244 | 227.3512 | 275.0036 | 198.9127
725.0667 | 281.3868 | 228.2695 | 275.4815 | 199.4185
726.0667 | 282.1425 | 229.9831 | 275.974 | 199.5622
727.0667 | 283.405 | 229.4254 | 275.9085 | 199.0876
728.0667 | 283.7832 | 228.3554 | 276.595 | 198.6928
729.0667 | 284.5654 | 228.7629 | 276.7107 | 199.3047
730.0667 | 285.4884 | 229.8445 | 276.7708 | 199.8279
731.0667 | 285.5483 | 229.8941 | 276.3182 | 200.5556
732.0667 | 285.5918 | 229.4013 | 275.2609 | 200.3441
733.0667 | 286.9142 | 229.1582 | 275.8319 | 200.0212
734.0667 | 287.6257 | 231.1006 | 276.9835 | 200.2911
735.0667 | 286.7887 | 231.9432 | 277.849 | 201.3375
736.0667 | 286.1051 | 232.4778 | 278.4009 | 200.647
737.0667 | 285.4027 | 232.9136 | 277.4793 | 199.7792
738.0667 | 284.5551 | 233.2363 | 276.9547 | 199.7268
739.0667 | 284.4156 | 234.2395 | 278.3807 | 201.1132
740.0667 | 284.4281 | 234.1296 | 279.3456 | 200.9695
741.0667 | 286.117 | 234.7686 | 279.6509 | 200.9036
742.0667 | 287.2847 | 235.0382 | 279.4602 | 199.9808
743.0667 | 287.0435 | 236.2336 | 279.7782 | 199.6672
744.0667 | 287.6165 | 236.101 | 279.8769 | 199.6276
745.0667 | 286.102 | 236.645 | 279.5207 | 200.0099
746.0667 | 286.1272 | 236.4121 | 279.6182 | 200.438
747.0667 | 285.3568 | 236.9975 | 280.1501 | 201.5177
748.0823 | 285.4995 | 237.9622 | 281.1357 | 202.5576
749.0667 | 286.1866 | 236.938 | 280.7554 | 203.6999
750.0823 | 286.026 | 235.3115 | 280.3017 | 203.9691
751.0667 | 286.3513 | 234.237 | 280.7087 | 204.0608
752.0667 | 286.2439 | 233.7846 | 280.5997 | 203.2839
753.0667 | 285.8583 | 232.3518 | 280.1101 | 203.1853
754.0823 | 285.342 | 232.1199 | 280.5482 | 203.4116
755.0667 | 287.1918 | 232.4311 | 281.2634 | 204.7102
756.0667 | 287.0254 | 232.0615 | 281.2697 | 204.7662
757.0667 | 288.6567 | 231.1915 | 281.0868 | 204.8148
758.0667 | 288.7461 | 231.9667 | 280.918 | 205.876
759.0667 | 290.1532 | 232.282 | 280.8723 | 205.3169
760.0667 | 289.0792 | 233.4265 | 280.7586 | 205.4602
761.0667 | 288.5807 | 233.8853 | 280.5944 | 206.0831
762.0667 | 288.6835 | 234.3289 | 281.1562 | 206.0264
763.0667 | 288.02 | 235.9649 | 281.8292 | 206.6573
764.0667 | 287.2284 | 235.3945 | 281.0333 | 207.3386
765.0667 | 286.7305 | 235.5957 | 280.3501 | 207.1467
766.0667 | 286.1946 | 235.1153 | 279.9024 | 208.2931
767.0667 | 286.5793 | 234.2517 | 279.3122 | 207.8008
768.0667 | 287.0146 | 234.0562 | 279.2479 | 207.706
769.0667 | 286.2975 | 234.1988 | 279.7345 | 207.548
770.0667 | 286.6246 | 235.1133 | 279.7635 | 208.0042
771.0667 | 286.8645 | 234.8431 | 280.2621 | 208.9581
772.0667 | 289.2712 | 235.1553 | 281.166 | 208.2968
773.0667 | 290.7141 | 234.2186 | 279.7436 | 208.2841
774.0667 | 290.2582 | 233.2909 | 279.7641 | 209.4809
775.0667 | 291.5735 | 232.4184 | 280.0102 | 208.4431
776.0667 | 290.9639 | 232.0794 | 279.5065 | 208.6335
777.0667 | 291.4152 | 232.8999 | 279.2197 | 209.0202
778.0667 | 291.8757 | 232.838 | 278.6809 | 209.5823
779.0667 | 292.047 | 234.62 | 278.8344 | 210.9245
780.0667 | 291.8858 | 235.6492 | 278.6897 | 211.652
781.0667 | 292.0614 | 235.7516 | 279.5569 | 211.8187
782.0667 | 293.4851 | 235.3308 | 279.976 | 211.1292
783.0667 | 293.6449 | 235.4883 | 280.0067 | 212.5185
784.0667 | 292.9215 | 234.4874 | 280.4482 | 211.662
785.0667 | 292.9226 | 233.84 | 279.2703 | 211.2961
786.0667 | 292.9771 | 233.4267 | 279.8523 | 212.3056
787.0667 | 292.2051 | 233.4888 | 281.9087 | 212.7712
788.0667 | 292.326 | 233.4665 | 282.0743 | 212.7344
789.0667 | 292.9671 | 233.8775 | 282.6854 | 212.5081
790.0667 | 291.8596 | 232.9766 | 282.2229 | 213.831
791.0667 | 290.7028 | 232.1241 | 281.3486 | 214.2543
792.0667 | 289.4029 | 232.3362 | 281.1984 | 214.1808
793.0667 | 289.6952 | 232.3644 | 281.411 | 215.1636
794.0667 | 289.558 | 233.0163 | 282.0253 | 216.188
795.0667 | 289.3843 | 233.417 | 281.735 | 217.6847
796.0667 | 288.8211 | 233.5587 | 281.3371 | 216.9386
797.0667 | 288.431 | 234.4884 | 281.2901 | 217.718
798.0667 | 287.6572 | 236.2705 | 281.6294 | 218.8311
799.0667 | 286.8827 | 235.9702 | 281.1524 | 218.0165
800.0667 | 286.4894 | 236.0619 | 280.346 | 217.6384
801.0823 | 286.2744 | 235.1338 | 279.2286 | 217.1096
802.0667 | 284.918 | 234.4459 | 277.9584 | 217.074
803.0667 | 284.0917 | 234.3858 | 278.4961 | 216.3968
804.0667 | 283.4088 | 234.1076 | 278.8569 | 216.1714
805.0823 | 284.2535 | 234.9278 | 279.4339 | 215.5756
806.0667 | 285.0633 | 235.2174 | 279.6204 | 215.2063
807.0667 | 286.3183 | 236.5237 | 280.912 | 214.4485
808.0667 | 287.2453 | 237.994 | 282.4939 | 214.342
809.0667 | 289.4225 | 238.6129 | 283.3608 | 214.128
810.0667 | 289.3197 | 239.9708 | 283.8534 | 213.1792
811.0667 | 288.4969 | 240.8008 | 284.396 | 212.1354
812.0667 | 287.7271 | 241.0808 | 283.963 | 211.3531
813.0667 | 288.5755 | 241.3626 | 284.0102 | 210.574
814.0667 | 289.4248 | 242.4853 | 285.2566 | 210.6993
815.0667 | 290.4792 | 244.4474 | 286.6935 | 211.6031
816.0667 | 290.6641 | 245.7375 | 287.3092 | 211.4853
817.0667 | 291.1902 | 245.2005 | 287.2551 | 210.7084
818.0667 | 290.7826 | 244.9221 | 287.8043 | 210.5249
819.0667 | 290.3637 | 244.9119 | 288.1465 | 210.1737
820.0667 | 290.2755 | 245.1527 | 288.7194 | 209.2716
821.0823 | 290.1118 | 245.9558 | 289.1001 | 209.9177
822.0667 | 290.3348 | 247.2086 | 289.5246 | 209.2987
823.0667 | 291.3114 | 248.8358 | 289.2949 | 208.7165
824.0667 | 291.8884 | 249.7756 | 289.7704 | 208.1134
825.0667 | 291.6148 | 250.7505 | 290.1682 | 207.2005
826.0667 | 289.8935 | 251.1423 | 289.94 | 206.5211
827.0667 | 289.8636 | 252.0184 | 289.2651 | 206.1242
828.0667 | 289.5655 | 252.781 | 289.8119 | 206.1421
829.0667 | 289.3012 | 253.799 | 291.1686 | 206.1318
830.0667 | 288.8417 | 253.5086 | 291.9937 | 206.4026
831.0667 | 287.988 | 254.1069 | 292.5103 | 205.3335
832.0667 | 288.0207 | 253.9868 | 291.6191 | 205.0581
833.0667 | 287.265 | 255.0409 | 292.3273 | 204.8004
834.0667 | 285.8925 | 255.1211 | 292.318 | 204.0933
835.0667 | 285.96 | 254.9954 | 291.9987 | 204.1036
836.0667 | 286.532 | 256.1262 | 291.9984 | 204.3151
837.0667 | 286.2358 | 258.8102 | 291.4204 | 204.0546
838.0667 | 286.1022 | 261.7879 | 290.9758 | 203.5292
839.0667 | 285.2084 | 262.0256 | 291.3676 | 203.3491
840.0667 | 283.7726 | 261.7705 | 290.7346 | 202.7403
841.0667 | 283.3372 | 261.4961 | 291.093 | 202.4697
842.0667 | 283.2619 | 262.3332 | 290.9662 | 202.6972
843.0667 | 284.2878 | 263.2676 | 292.6163 | 203.0378
844.0667 | 285.0917 | 264.0972 | 293.769 | 202.9564
845.0667 | 286.8008 | 264.8304 | 294.8901 | 203.1296
846.0667 | 288.6456 | 265.4445 | 295.6011 | 204.2898
847.0667 | 288.2696 | 264.0443 | 295.3639 | 204.364
848.0667 | 289.2142 | 264.6007 | 297.6745 | 204.3123
849.0667 | 290.7895 | 264.7179 | 298.0694 | 203.8957
850.0667 | 290.8248 | 265.338 | 297.8213 | 203.615
851.0667 | 290.159 | 265.7357 | 297.5671 | 203.58
852.0667 | 290.4109 | 266.1606 | 298.2413 | 203.3222
853.0667 | 292.2016 | 268.3294 | 298.7783 | 203.6849
854.0667 | 291.5424 | 268.2859 | 300.1849 | 203.4536
855.0667 | 290.6317 | 267.0193 | 300.4753 | 203.1926
856.0667 | 289.6546 | 265.6182 | 300.0989 | 202.7197
857.0667 | 289.012 | 265.2853 | 299.1062 | 202.2373
858.0667 | 288.7232 | 264.6249 | 298.3208 | 202.0564
859.0823 | 287.8492 | 263.3791 | 298.2492 | 201.649
860.0823 | 287.0482 | 262.5311 | 297.9488 | 201.3348
861.0667 | 286.97 | 262.201 | 297.5225 | 201.1237
862.0667 | 287.1591 | 261.3715 | 297.3546 | 201.0635
863.0667 | 284.9784 | 260.2087 | 296.3618 | 200.973
864.0667 | 284.6904 | 259.472 | 294.8428 | 200.8974
865.0667 | 283.9976 | 258.9716 | 294.6566 | 201.1657
866.0667 | 284.0175 | 258.3788 | 294.3587 | 201.185
867.0667 | 283.5163 | 258.3406 | 293.7033 | 200.7022
868.0667 | 282.9918 | 258.852 | 293.1601 | 200.5924
869.0667 | 283.0269 | 259.0826 | 292.6404 | 200.8262
870.0667 | 282.2289 | 258.9121 | 292.8524 | 201.0018
871.0667 | 281.4213 | 260.0633 | 291.5241 | 202.4726
872.0667 | 280.4437 | 260.8101 | 291.6152 | 202.8341
873.0667 | 281.8594 | 261.8687 | 291.2077 | 202.3585
874.0667 | 282.1717 | 262.661 | 291.4826 | 201.949
875.0667 | 281.3987 | 264.0014 | 292.402 | 201.6138
876.0667 | 281.9118 | 263.9316 | 291.8204 | 202.0035
877.0667 | 282.0659 | 264.8499 | 291.9929 | 202.2666
878.0667 | 282.7004 | 265.7979 | 292.5854 | 202.235
879.0667 | 282.2036 | 265.8775 | 292.7776 | 202.0397
880.0667 | 280.9159 | 265.1504 | 292.5584 | 202.2144
881.0667 | 280.3184 | 264.3198 | 292.5155 | 202.5922
882.0667 | 279.5158 | 264.3268 | 292.1936 | 203.004
883.0667 | 279.6789 | 263.707 | 292.6251 | 203.1411
884.0667 | 278.9138 | 263.434 | 292.36 | 203.0434
885.0667 | 278.6659 | 264.5197 | 290.9602 | 203.1104
886.0667 | 278.7237 | 265.6478 | 291.7017 | 203.2601
887.0667 | 277.4774 | 265.4889 | 291.6116 | 202.9943
888.0667 | 276.8656 | 265.3286 | 290.237 | 203.0517
889.0667 | 276.4037 | 264.3515 | 290.2802 | 203.2705
890.0667 | 276.6851 | 264.832 | 290.3904 | 203.0447
891.0667 | 276.2763 | 265.2047 | 290.7332 | 203.0461
892.0667 | 274.5839 | 264.6294 | 291.4138 | 203.0428
893.0667 | 274.1116 | 263.663 | 290.6551 | 203.1608
894.0667 | 273.8048 | 263.539 | 290.8318 | 202.9268
895.0667 | 274.1592 | 263.7302 | 289.8045 | 202.8474
896.0667 | 275.1888 | 264.1867 | 289.0842 | 202.238
897.0667 | 275.7328 | 263.7646 | 289.508 | 202.1405
898.0667 | 275.2736 | 263.0117 | 291.2397 | 202.0886
899.0667 | 274.7053 | 262.4787 | 289.9101 | 202.4277
900.0667 | 274.7011 | 263.5116 | 288.9728 | 202.7992
901.0667 | 274.3826 | 262.4336 | 289.7106 | 202.9659
902.0667 | 273.9713 | 262.7883 | 288.6017 | 203.3892
903.0667 | 273.5369 | 263.2957 | 287.2959 | 202.8594
904.0667 | 273.9994 | 264.857 | 286.8167 | 202.3897
905.0667 | 273.6404 | 267.1997 | 286.831 | 201.9616
906.0667 | 274.7915 | 269.9883 | 287.1178 | 201.3544
907.0667 | 274.7218 | 271.9889 | 288.2284 | 201.4851
908.0667 | 274.3219 | 272.3898 | 288.4487 | 201.7277
909.0667 | 273.5955 | 272.2182 | 288.8455 | 201.4876
910.0667 | 272.9269 | 272.3348 | 288.5432 | 201.6782
911.0667 | 272.5835 | 272.4441 | 288.6841 | 201.7291
912.0667 | 272.1191 | 273.041 | 288.5273 | 202.1199
913.0667 | 272.0007 | 273.1156 | 289.2802 | 201.9879
914.0667 | 272.9371 | 273.7541 | 289.4375 | 201.9688
915.0667 | 273.2001 | 274.0588 | 290.1439 | 201.5695
916.0667 | 272.6391 | 274.8892 | 290.2598 | 201.3578
917.0667 | 271.4099 | 276.6955 | 291.1114 | 201.0572
918.0667 | 271.061 | 276.8025 | 290.7082 | 200.834
919.0667 | 271.3333 | 275.9439 | 290.38 | 201.2105
920.0667 | 271.8741 | 275.9125 | 291.39 | 201.2116
921.0667 | 272.7034 | 277.4969 | 291.9925 | 201.5418
922.0667 | 272.8087 | 279.9486 | 293.7627 | 202.0796
923.0667 | 275.5407 | 281.3747 | 294.6858 | 202.7599
924.0667 | 276.754 | 283.0712 | 295.7364 | 203.4577
925.0667 | 278.6163 | 284.3661 | 295.3569 | 203.768
926.0667 | 281.0141 | 285.0132 | 297.0838 | 204.3411
927.0667 | 283.205 | 285.6387 | 298.1934 | 204.2414
928.0667 | 284.0388 | 286.8746 | 300.0453 | 204.6456
929.0667 | 285.0538 | 288.0206 | 300.9477 | 205.285
930.0667 | 286.3008 | 288.7424 | 302.8568 | 205.7617
931.0667 | 287.6749 | 288.9489 | 303.8077 | 205.942
932.0667 | 289.2255 | 289.6084 | 305.0704 | 207.6496
933.0667 | 289.5246 | 288.9898 | 306.1123 | 209.4266
934.0667 | 290.7066 | 290.5697 | 308.1816 | 209.8862
935.0667 | 289.9252 | 291.3379 | 308.7626 | 210.2012
936.0667 | 289.5475 | 292.1153 | 308.2647 | 209.9738
937.0667 | 290.8779 | 293.384 | 307.1796 | 209.7844
938.0667 | 292.0607 | 295.0226 | 306.6452 | 209.5851
939.0667 | 292.9995 | 296.1126 | 308.224 | 209.2657
940.0667 | 293.5007 | 296.4164 | 309.1674 | 209.5884
941.0667 | 294.8912 | 297.1996 | 310.1397 | 210.4524
942.0667 | 294.9831 | 297.1407 | 311.5447 | 211.357
943.0667 | 295.7082 | 297.3645 | 312.6444 | 212.2272
944.0667 | 296.5229 | 297.1333 | 313.046 | 212.4966
945.0667 | 296.8911 | 297.6128 | 313.7409 | 212.3623
946.0667 | 297.8564 | 298.896 | 314.3793 | 212.5701
947.0667 | 298.5038 | 298.8573 | 314.8143 | 213.4455
948.0667 | 299.1454 | 299.5894 | 314.8109 | 213.1939
949.0667 | 299.126 | 299.9984 | 315.6727 | 213.8984
950.0667 | 299.5986 | 300.7523 | 315.1683 | 214.4097
951.0667 | 298.9357 | 302.1176 | 316.0669 | 215.0618
952.0667 | 297.9791 | 302.5924 | 315.6841 | 214.6382
953.0667 | 297.9606 | 301.9981 | 315.7122 | 215.1388
954.0667 | 297.7756 | 302.4805 | 317.4046 | 215.1262
955.0667 | 299.25 | 303.1286 | 317.0412 | 214.9991
956.0667 | 299.2013 | 303.0588 | 317.262 | 214.9473
957.0667 | 298.2765 | 303.9692 | 317.3503 | 215.0216
958.0667 | 297.398 | 304.0654 | 316.8622 | 215.9598
959.0667 | 298.6715 | 303.973 | 317.3266 | 215.8384
960.0667 | 301.2647 | 303.7222 | 317.7274 | 215.6081
961.0667 | 301.1459 | 303.4209 | 317.7628 | 216.714
962.0667 | 302.0098 | 303.8724 | 318.1708 | 216.7996
963.0667 | 304.7808 | 305.052 | 319.1736 | 219.1173
964.0667 | 307.3556 | 306.57 | 320.0175 | 222.479
965.0667 | 309.1755 | 306.0313 | 320.9138 | 226.613
966.0667 | 310.7368 | 307.2303 | 322.3924 | 228.2051
967.0667 | 312.2872 | 307.1805 | 323.3251 | 229.3406
968.0667 | 314.0645 | 307.2072 | 324.3309 | 231.086
969.0667 | 313.0976 | 307.1421 | 324.7696 | 231.2425
970.0667 | 313.3123 | 306.7975 | 325.4074 | 231.2262
971.0667 | 313.9007 | 306.2289 | 326.2316 | 230.6575
972.0667 | 314.2474 | 305.1082 | 326.2874 | 230.3489
973.0667 | 313.4679 | 304.0457 | 326.2738 | 229.9394
974.0667 | 314.4609 | 302.8443 | 325.8909 | 229.429
975.0667 | 314.5194 | 301.6892 | 326.2237 | 229.3958
976.0667 | 315.0327 | 300.2393 | 325.8576 | 229.309
977.0667 | 315.872 | 300.3045 | 326.2349 | 230.1881
978.0667 | 315.893 | 299.1633 | 325.9315 | 229.8147
979.0667 | 316.3489 | 298.6739 | 326.7803 | 229.5571
980.0667 | 316.0459 | 299.5262 | 327.0039 | 229.7051
981.0667 | 317.2894 | 299.3964 | 327.1182 | 229.969
982.0667 | 319.1964 | 298.8643 | 328.0707 | 231.5925
983.0667 | 320.6155 | 299.0876 | 328.5249 | 233.2582
984.0667 | 320.9356 | 298.0359 | 328.9231 | 233.2446
985.0667 | 320.5317 | 298.5366 | 328.2175 | 233.5058
986.0667 | 320.3578 | 297.396 | 328.1682 | 233.9023
987.0667 | 321.3151 | 297.0768 | 328.413 | 233.7025
988.0667 | 322.3634 | 296.6057 | 328.6983 | 234.1525
989.0667 | 322.6769 | 295.9665 | 329.07 | 233.2376
990.0667 | 322.6158 | 296.787 | 328.7195 | 233.5277
991.0667 | 322.4165 | 297.1943 | 327.9194 | 233.941
992.0667 | 322.3832 | 296.1002 | 327.1602 | 233.9711
993.0667 | 322.6817 | 295.0872 | 327.3482 | 234.34
994.0667 | 324.2465 | 296.7423 | 327.8987 | 235.1912
995.0667 | 325.1455 | 295.4928 | 328.011 | 235.1988
996.0823 | 325.1315 | 295.6483 | 328.5117 | 234.7081
997.0823 | 324.9582 | 295.1894 | 328.1018 | 234.8983
998.0667 | 324.8226 | 294.9149 | 327.8879 | 235.0337
999.0667 | 324.892 | 294.2759 | 327.7069 | 235.3921
1000.0823 | 324.5665 | 294.4695 | 327.4313 | 235.0118
1001.0667 | 325.0439 | 293.7767 | 327.5245 | 234.8096
1002.0823 | 325.7757 | 292.2263 | 327.5597 | 235.2242
1003.0667 | 326.3692 | 290.4829 | 327.1485 | 235.5891
1004.0667 | 325.8642 | 289.4468 | 328.1563 | 235.1981
1005.0667 | 326.293 | 289.1668 | 328.2871 | 235.362
1006.0667 | 326.5057 | 288.0188 | 329.4238 | 235.0858
1007.0667 | 327.0824 | 287.7109 | 329.5869 | 236.1228
1008.0667 | 328.0423 | 289.5746 | 329.7407 | 237.4701
1009.0667 | 327.8852 | 289.786 | 329.5196 | 239.3105
1010.0667 | 328.386 | 289.9492 | 329.3336 | 240.9818
1011.0667 | 328.6506 | 289.6721 | 328.8194 | 242.0647
1012.0667 | 328.1302 | 289.3597 | 328.5857 | 241.9627
1013.0667 | 328.0922 | 288.8493 | 329.9631 | 241.7114
1014.0667 | 327.8109 | 289.399 | 329.8776 | 242.1601
1015.0667 | 328.5362 | 290.1483 | 330.131 | 242.5642
1016.0667 | 329.4916 | 289.7441 | 329.4479 | 242.6767
1017.0667 | 329.8051 | 288.6246 | 329.7361 | 242.6407
1018.0667 | 330.4123 | 287.8307 | 329.8739 | 242.4069
1019.0667 | 330.9002 | 287.1578 | 330.1083 | 242.8262
1020.0667 | 331.2078 | 286.4964 | 330.2128 | 243.6641
1021.0667 | 330.7634 | 286.1402 | 330.3527 | 243.349
1022.0667 | 330.7102 | 286.2657 | 330.3906 | 243.2038
1023.0667 | 329.8332 | 286.4171 | 330.2931 | 242.2798
1024.0667 | 330.5046 | 286.7403 | 329.0396 | 242.1493
1025.0667 | 332.0437 | 286.9592 | 329.2557 | 242.5777
1026.0667 | 333.1008 | 286.9497 | 329.0085 | 243.1661
1027.0667 | 333.2108 | 287.3844 | 329.3806 | 243.8615
1028.0823 | 331.5969 | 287.8354 | 329.1607 | 243.1014
1029.0667 | 331.0351 | 288.4055 | 328.6282 | 242.5316
1030.0667 | 330.8798 | 290.5984 | 329.2517 | 242.1802
1031.0667 | 332.0878 | 291.1697 | 329.7536 | 242.4079
1032.0667 | 332.7577 | 290.5116 | 329.7327 | 242.4604
1033.0667 | 333.4733 | 291.5279 | 330.3349 | 243.0728
1034.0667 | 333.9069 | 292.2904 | 331.7658 | 242.1042
1035.0667 | 333.4407 | 292.7066 | 332.7088 | 241.3892
1036.0667 | 333.2298 | 293.0212 | 333.3086 | 240.6327
1037.0667 | 333.1387 | 292.6775 | 333.3283 | 240.3757
1038.0667 | 333.9775 | 292.9999 | 333.4281 | 241.0913
1039.0667 | 332.8057 | 292.6274 | 333.8601 | 242.4734
1040.0667 | 334.4063 | 292.8403 | 333.2311 | 243.1142
1041.0667 | 336.1201 | 294.2848 | 333.5163 | 242.9705
1042.0667 | 336.7584 | 295.2239 | 334.3726 | 243.0669
1043.0667 | 338.4994 | 295.1323 | 334.7797 | 243.7319
1044.0667 | 339.4314 | 294.6415 | 335.4433 | 243.2739
1045.0667 | 338.6357 | 295.0514 | 336.2875 | 243.5633
1046.0667 | 338.9614 | 295.9495 | 336.394 | 243.3193
1047.0667 | 339.1439 | 296.3943 | 336.8498 | 245.0402
1048.0667 | 339.9392 | 295.4282 | 337.8926 | 245.8897
1049.0667 | 340.1503 | 294.7325 | 338.4935 | 245.7595
1050.0667 | 339.8627 | 294.5583 | 337.2208 | 245.0027
1051.0667 | 339.6411 | 293.525 | 336.7456 | 244.7932
1052.0667 | 339.5447 | 294.5083 | 336.4172 | 245.4743
1053.0667 | 338.7785 | 294.0514 | 335.6537 | 244.8774
1054.0667 | 338.5007 | 294.9307 | 335.4341 | 245.243
1055.0667 | 339.7951 | 294.1313 | 335.0656 | 245.8546
1056.0667 | 340.4099 | 295.0338 | 335.1075 | 247.1318
1057.0667 | 341.6816 | 294.9392 | 335.4498 | 246.9614
1058.0667 | 341.5901 | 295.1085 | 334.7949 | 247.2478
1059.0667 | 340.933 | 295.1961 | 334.4241 | 246.6901
1060.0667 | 338.857 | 295.2401 | 334.7502 | 246.3599
1061.0667 | 338.4015 | 295.5141 | 334.0574 | 245.5749
1062.0667 | 338.9582 | 296.2442 | 334.9198 | 245.3036
1063.0667 | 340.4243 | 296.3884 | 335.2827 | 245.342
1064.0667 | 341.11 | 296.3998 | 335.5318 | 244.7399
1065.0667 | 341.7098 | 296.0119 | 335.9924 | 244.7417
1066.0667 | 342.1804 | 294.2806 | 336.4506 | 246.1802
1067.0667 | 343.7835 | 294.6235 | 337.552 | 247.186
1068.0667 | 345.6569 | 294.0579 | 337.932 | 246.5821
1069.0667 | 346.4155 | 293.1044 | 337.8156 | 246.822
1070.0667 | 346.6731 | 293.7556 | 337.7075 | 247.6159
1071.0667 | 347.7013 | 292.5812 | 337.5518 | 247.542
1072.0667 | 348.0277 | 293.0108 | 337.6749 | 248.4307
1073.0667 | 347.3855 | 294.1996 | 339.0126 | 249.0542
1074.0667 | 346.582 | 294.4956 | 339.0714 | 249.0065
1075.0667 | 347.0853 | 294.2163 | 338.9123 | 248.9372
1076.0667 | 348.1296 | 294.9668 | 339.8948 | 250.0472
1077.0667 | 349.5652 | 294.947 | 340.1661 | 249.8692
1078.0667 | 350.1575 | 294.3179 | 340.1915 | 251.0973
1079.0667 | 351.1239 | 294.8616 | 339.8663 | 251.203
1080.0667 | 350.4398 | 295.4261 | 339.2936 | 251.5444
1081.0667 | 349.7976 | 295.977 | 339.121 | 250.7971
1082.0667 | 350.515 | 295.2027 | 338.9544 | 249.855
1083.0667 | 350.2888 | 295.6458 | 340.1479 | 248.9795
1084.0667 | 350.2105 | 296.4399 | 341.248 | 249.2493
1085.0667 | 350.9637 | 296.9345 | 341.6189 | 249.8372
1086.0667 | 351.442 | 297.0767 | 342.3196 | 250.8551
1087.0667 | 351.9275 | 296.5191 | 342.856 | 251.7945
1088.0667 | 351.8759 | 296.6576 | 343.47 | 252.8198
1089.0667 | 351.841 | 297.2782 | 343.3115 | 254.1075
1090.0667 | 351.9567 | 297.6332 | 342.7779 | 254.9004
1091.0667 | 352.6685 | 297.8198 | 344.1457 | 254.4675
1092.0667 | 354.8226 | 298.6317 | 344.5777 | 254.4887
1093.0667 | 355.8878 | 298.7539 | 344.8254 | 254.275
1094.0667 | 354.8372 | 298.5258 | 344.8167 | 254.8487
1095.0667 | 355.6062 | 298.8277 | 344.7774 | 255.8957
1096.0667 | 356.8195 | 299.2059 | 345.6187 | 255.9221
1097.0667 | 357.3066 | 298.1095 | 345.9424 | 256.39
1098.0667 | 357.6273 | 298.4127 | 346.8367 | 256.4877
1099.0667 | 356.9941 | 296.7918 | 347.0148 | 256.5396
1100.0667 | 355.649 | 296.549 | 345.8084 | 257.7877
1101.0667 | 356.32 | 297.7467 | 345.2381 | 258.7919
1102.0667 | 358.7118 | 298.1406 | 345.5813 | 258.4806
1103.0667 | 359.5151 | 297.0917 | 345.6126 | 259.0917
1104.0667 | 360.049 | 296.9718 | 346.3244 | 259.6514
1105.0823 | 359.3831 | 296.2201 | 346.6414 | 261.4549
1106.0667 | 358.1089 | 296.0424 | 346.3627 | 261.7546
1107.0667 | 357.784 | 297.916 | 345.6026 | 261.3966
1108.0667 | 356.7284 | 298.32 | 346.8154 | 261.5907
1109.0667 | 355.9181 | 298.5765 | 346.2955 | 261.7072
1110.0667 | 355.9442 | 298.8025 | 345.8497 | 260.969
1111.0667 | 354.873 | 299.3237 | 345.8102 | 260.165
1112.0667 | 353.3707 | 299.3108 | 345.774 | 260.3618
1113.0667 | 352.3755 | 298.7873 | 345.4912 | 260.1105
1114.0667 | 353.1917 | 298.2211 | 344.9708 | 260.3528
1115.0667 | 353.5284 | 298.651 | 344.9064 | 260.8244
1116.0667 | 354.4852 | 299.645 | 344.8797 | 261.2613
1117.0667 | 356.4963 | 299.476 | 345.5434 | 261.1646
1118.0667 | 356.7086 | 299.1316 | 346.1376 | 262.2347
1119.0667 | 357.6347 | 299.107 | 347.5633 | 263.1633
1120.0667 | 356.7999 | 299.2565 | 349.4005 | 262.7897
1121.0667 | 355.681 | 298.7485 | 349.0763 | 262.3344
1122.0667 | 354.6883 | 298.0038 | 349.0857 | 261.1079
1123.0667 | 354.4897 | 297.1065 | 347.8502 | 260.8686
1124.0667 | 353.9762 | 296.7786 | 348.6415 | 261.1518
1125.0667 | 354.4723 | 296.1305 | 348.2618 | 260.679
1126.0667 | 354.2464 | 296.5202 | 347.7822 | 260.5965
1127.0667 | 354.1906 | 296.9504 | 347.8613 | 260.5695
1128.0667 | 353.8691 | 297.0539 | 348.3271 | 260.0132
1129.0667 | 354.4857 | 297.435 | 348.6399 | 260.2066
1130.0667 | 355.0238 | 297.8122 | 348.8687 | 259.6513
1131.0667 | 354.382 | 298.2851 | 347.8107 | 259.5487
1132.0667 | 353.6492 | 299.7048 | 347.368 | 259.2801
1133.0667 | 354.7288 | 300.6336 | 347.0068 | 258.521
1134.0667 | 356.6996 | 300.112 | 346.6093 | 257.7359
1135.0667 | 356.0921 | 299.3734 | 346.6237 | 257.3944
1136.0667 | 355.6834 | 299.3375 | 347.6389 | 258.2153
1137.0667 | 357.3541 | 299.4472 | 346.9022 | 257.76
1138.0667 | 354.2363 | 300.6867 | 346.6831 | 256.9319
1139.0667 | 350.7156 | 302.0128 | 344.9385 | 256.1701
1140.0667 | 348.2534 | 303.6205 | 343.7494 | 255.0046
1141.0667 | 346.06 | 303.7364 | 342.0149 | 254.1649
1142.0667 | 345.447 | 304.0504 | 341.2801 | 253.4433
1143.0667 | 345.2639 | 304.6008 | 341.563 | 253.2587
1144.0667 | 344.413 | 303.9086 | 341.3597 | 254.2876
1145.0667 | 345.0248 | 303.0225 | 341.2061 | 254.2394
1146.0667 | 345.9066 | 302.1113 | 341.5694 | 254.378
1147.0667 | 344.7303 | 301.4391 | 341.3399 | 254.7621
1148.0667 | 343.3779 | 301.6872 | 340.7223 | 254.4449
1149.0667 | 344.1272 | 301.112 | 340.719 | 253.5716
1150.0667 | 344.1587 | 300.7369 | 341.0906 | 254.2427
1151.0667 | 345.2576 | 300.1725 | 341.6476 | 254.6961
1152.0667 | 345.3125 | 299.8359 | 341.7046 | 255.3486
1153.0667 | 345.6316 | 299.2556 | 342.2523 | 255.3419
1154.0667 | 345.6279 | 299.1374 | 342.9409 | 256.0453
1155.0667 | 345.2311 | 298.4926 | 343.0427 | 255.9573
1156.0667 | 344.9649 | 299.3432 | 344.264 | 256.8091
1157.0667 | 347.6938 | 298.6483 | 344.583 | 257.6225
1158.0667 | 347.8459 | 298.4534 | 344.8992 | 258.786
1159.0667 | 347.9753 | 297.5665 | 344.4346 | 257.9478
1160.0667 | 348.1655 | 297.0939 | 344.2869 | 257.5027
1161.0667 | 347.4125 | 296.8298 | 344.479 | 257.4848
1162.0667 | 348.1533 | 297.0571 | 344.6699 | 257.2369
1163.0667 | 348.9208 | 296.696 | 345.6991 | 257.0969
1164.0667 | 349.4338 | 297.3705 | 345.4282 | 257.5499
1165.0667 | 349.976 | 298.164 | 346.7272 | 257.5588
1166.0667 | 350.5167 | 298.5114 | 347.8842 | 257.7283
1167.0667 | 350.7167 | 298.7222 | 348.5329 | 257.5162
1168.0667 | 350.9472 | 299.7245 | 348.6175 | 257.5506
1169.0667 | 353.3471 | 299.9994 | 347.6655 | 257.8696
1170.0667 | 354.3461 | 299.9249 | 348.2632 | 258.637
1171.0667 | 355.4748 | 299.4425 | 348.0589 | 259.8769
1172.0667 | 354.8067 | 299.7528 | 348.8121 | 259.3055
1173.0667 | 354.3732 | 300.0728 | 348.599 | 258.9179
1174.0667 | 353.9052 | 299.9846 | 347.5647 | 258.9909
1175.0667 | 353.2838 | 300.2699 | 347.5392 | 259.7577
1176.0667 | 352.7559 | 300.3833 | 347.3201 | 260.9122
1177.0667 | 353.3368 | 300.7362 | 347.4133 | 260.3677
1178.0667 | 353.0889 | 300.9861 | 347.4696 | 260.1585
1179.0667 | 352.6836 | 301.3957 | 348.0075 | 259.7238
1180.0667 | 351.9154 | 302.2478 | 348.3794 | 259.7117
1181.0667 | 352.1131 | 301.3543 | 348.9976 | 259.7204
1182.0667 | 354.0355 | 300.5531 | 350.1428 | 259.5975
1183.0667 | 355.7327 | 301.497 | 349.5784 | 261.3937
1184.0667 | 356.5019 | 300.3249 | 349.9059 | 262.0139
1185.0667 | 356.0417 | 299.6692 | 350.6044 | 262.0688
1186.0667 | 355.9686 | 299.2155 | 350.642 | 262.5553
1187.0667 | 355.2941 | 299.6313 | 350.86 | 262.0292
1188.0667 | 353.9477 | 299.7136 | 350.2122 | 261.6782
1189.0667 | 355.2543 | 299.3643 | 349.6306 | 262.1472
1190.0667 | 354.8829 | 299.3786 | 348.9107 | 262.2183
1191.0667 | 356.6487 | 299.392 | 348.4197 | 263.2849
1192.0667 | 359.3169 | 299.2448 | 348.0409 | 264.9619
1193.0667 | 361.4543 | 298.2753 | 347.5781 | 266.2179
1194.0667 | 362.5876 | 298.2805 | 348.9056 | 266.2881
1195.0667 | 362.0616 | 299.5581 | 349.6627 | 266.7901
1196.0667 | 362.1984 | 299.0509 | 349.6479 | 267.6314
1197.0667 | 361.9142 | 299.285 | 349.4073 | 267.6857
1198.0667 | 363.1451 | 299.7156 | 349.5476 | 267.4788
1199.0667 | 363.737 | 300.0181 | 350.1493 | 267.1456
1200.0667 | 362.9766 | 301.4018 | 349.929 | 268.4278
1201.0667 | 361.9212 | 302.2135 | 350.583 | 268.7029
1202.0667 | 361.8089 | 302.3252 | 350.8782 | 267.7126
1203.0667 | 361.6657 | 302.7316 | 350.8332 | 267.6785
1204.0667 | 361.1989 | 302.7711 | 350.5286 | 267.635
1205.0667 | 362.2773 | 303.2941 | 350.1156 | 266.9362
1206.0667 | 364.2886 | 303.975 | 350.4534 | 266.6508
1207.0667 | 364.7117 | 303.3042 | 351.4411 | 268.2859
1208.0667 | 366.0705 | 302.7133 | 350.646 | 269.5365
1209.0667 | 366.3267 | 301.3332 | 350.3507 | 269.7148
1210.0667 | 366.6425 | 301.0389 | 350.6315 | 270.5732
1211.0667 | 365.8233 | 300.3042 | 350.6047 | 270.947
1212.0667 | 365.9755 | 300.5421 | 350.5781 | 270.198
1213.0667 | 365.8127 | 301.4816 | 351.2347 | 269.5939
1214.0667 | 369.5356 | 302.5726 | 351.4472 | 269.1041
1215.0667 | 370.3576 | 303.3965 | 351.9717 | 269.5984
1216.0667 | 370.922 | 303.8349 | 351.8036 | 269.2581
1217.0667 | 371.433 | 304.8733 | 353.4648 | 268.5539
1218.0667 | 372.883 | 304.9969 | 354.2454 | 268.9331
1219.0667 | 373.3997 | 305.422 | 354.856 | 269.4858
1220.0667 | 372.8894 | 305.0103 | 354.7703 | 268.634
1221.0667 | 372.6953 | 305.1235 | 355.4746 | 268.7395
1222.0667 | 371.5873 | 304.4227 | 355.8832 | 269.4195
1223.0667 | 371.2324 | 304.0247 | 356.3303 | 270.215
1224.0667 | 370.1917 | 303.8536 | 357.2672 | 269.8781
1225.0667 | 370.0128 | 303.7423 | 357.4448 | 269.9443
1226.0667 | 370.1693 | 303.5657 | 357.3008 | 271.0458
1227.0667 | 369.6103 | 303.371 | 357.0724 | 271.2958
1228.0667 | 369.7782 | 302.6886 | 357.8257 | 270.8181
1229.0667 | 369.2418 | 302.6437 | 357.0589 | 269.5775
1230.0667 | 372.2219 | 302.5802 | 357.0146 | 268.3964
1231.0667 | 375.8999 | 302.7201 | 356.6475 | 267.7489
1232.0667 | 375.3665 | 302.8088 | 357.3654 | 266.972
1233.0667 | 376.5612 | 303.0586 | 357.0047 | 266.3178
1234.0667 | 377.428 | 304.2351 | 357.0225 | 267.9225
1235.0667 | 377.3267 | 304.3381 | 356.9978 | 268.4234
1236.0667 | 376.771 | 303.6049 | 356.1758 | 268.7969
1237.0667 | 375.2514 | 303.4977 | 356.1457 | 268.4625
1238.0667 | 373.502 | 303.2675 | 354.9772 | 268.2169
1239.0667 | 372.1603 | 303.1708 | 353.8517 | 267.8428
1240.0667 | 371.8121 | 303.065 | 353.8687 | 267.5294
1241.0667 | 372.3378 | 302.4928 | 354.3637 | 267.7229
1242.0667 | 372.4566 | 301.7873 | 354.7132 | 267.9703
1243.0667 | 372.5674 | 301.52 | 355.1375 | 267.4202
1244.0823 | 370.6176 | 301.5781 | 354.1315 | 267.3186
1245.0667 | 368.7984 | 301.8528 | 353.2198 | 266.7765
1246.0667 | 368.0754 | 301.6264 | 352.7162 | 265.9846
1247.0667 | 367.57 | 300.932 | 352.91 | 265.9224
1248.0667 | 368.1369 | 300.5295 | 353.3727 | 266.4782
1249.0667 | 369.2616 | 300.4147 | 353.4491 | 266.4679
1250.0667 | 369.3405 | 300.8811 | 353.5621 | 267.0795
1251.0667 | 370.9294 | 300.1774 | 352.6727 | 268.3257
1252.0667 | 372.5908 | 300.4764 | 352.2223 | 269.6728
1253.0667 | 372.7592 | 300.6327 | 352.0988 | 271.2564
1254.0667 | 374.9177 | 300.8529 | 351.9293 | 271.7521
1255.0667 | 375.9371 | 300.7665 | 352.8196 | 271.6841
1256.0667 | 375.7829 | 301.7939 | 353.4992 | 270.8121
1257.0667 | 377.5236 | 302.3797 | 353.8728 | 271.4594
1258.0667 | 379.2799 | 302.497 | 353.752 | 270.6192
1259.0667 | 378.0192 | 303.7984 | 354.4037 | 270.6477
1260.0667 | 377.7618 | 305.3655 | 354.639 | 270.5868
1261.0667 | 377.788 | 305.4531 | 355.9377 | 270.5177
1262.0667 | 376.5873 | 306.5685 | 356.4537 | 270.0982
1263.0667 | 377.0565 | 307.4156 | 357.4492 | 269.1793
1264.0667 | 378.7976 | 308.1767 | 357.0944 | 269.6048
1265.0667 | 377.93 | 308.8187 | 357.378 | 270.502
1266.0667 | 376.4707 | 309.744 | 357.869 | 270.0386
1267.0667 | 374.8706 | 310.7094 | 357.954 | 269.7723
1268.0667 | 374.32 | 311.0657 | 357.9179 | 269.3726
1269.0667 | 373.8475 | 311.0751 | 357.1854 | 270.2627
1270.0667 | 375.736 | 311.7914 | 357.5137 | 269.7463
1271.0667 | 377.4525 | 312.2154 | 358.6965 | 270.5837
1272.0667 | 378.9295 | 312.0099 | 358.7858 | 270.759
1273.0667 | 379.7576 | 311.4986 | 360.1215 | 270.608
1274.0667 | 380.221 | 310.8407 | 360.4543 | 271.0788
1275.0667 | 381.2094 | 310.0542 | 360.7609 | 271.7423
1276.0667 | 380.2959 | 310.93 | 360.2057 | 271.358
1277.0667 | 379.2156 | 311.5226 | 360.3224 | 270.9687
1278.0667 | 385.5511 | 311.9945 | 359.8793 | 270.8952
1279.0667 | 383.1475 | 313.2106 | 360.6407 | 270.2537
1280.0667 | 384.6002 | 313.7666 | 360.9691 | 269.6493
1281.0667 | 384.4964 | 313.6381 | 360.4835 | 270.464
1282.0667 | 383.6684 | 313.9017 | 360.5319 | 270.4299
1283.0667 | 383.6338 | 312.7951 | 359.9716 | 270.7637
1284.0667 | 382.0996 | 312.9553 | 360.4243 | 270.2403
1285.0667 | 381.2021 | 313.159 | 359.9125 | 269.9074
1286.0667 | 382.7079 | 312.8852 | 362.3127 | 269.0847
1287.0667 | 383.5491 | 312.994 | 362.896 | 269.0783
1288.0667 | 382.8461 | 312.7396 | 362.7293 | 268.8256
1289.0667 | 381.4107 | 312.6381 | 363.6769 | 268.7783
1290.0667 | 384.7047 | 311.9503 | 364.0743 | 268.4877
1291.0667 | 383.5245 | 312.6433 | 366.1632 | 268.4291
1292.0667 | 382.665 | 313.4669 | 366.9518 | 268.392
1293.0667 | 382.7306 | 312.9478 | 366.8811 | 267.9099
1294.0667 | 383.4285 | 312.7407 | 366.2513 | 267.4207
1295.0667 | 382.9145 | 313.0028 | 365.4234 | 267.0281
1296.0667 | 381.8578 | 312.4312 | 365.2245 | 266.9127
1297.0667 | 381.8839 | 311.9696 | 364.7137 | 266.5791
1298.0667 | 382.8674 | 311.8727 | 366.2854 | 266.4774
1299.0667 | 382.6131 | 311.352 | 369.3516 | 266.951
1300.0667 | 381.7749 | 312.0253 | 369.941 | 267.0683
1301.0667 | 381.7363 | 311.9649 | 370.5711 | 267.1981
1302.0667 | 381.7823 | 310.8061 | 370.5298 | 267.2568
1303.0667 | 381.5995 | 309.4446 | 370.6939 | 266.9369
1304.0667 | 382.1785 | 308.1255 | 370.5971 | 267.0644
1305.0667 | 382.0951 | 308.6794 | 370.0833 | 267.6411
1306.0667 | 383.8169 | 308.9266 | 368.9898 | 268.4195
1307.0667 | 382.9509 | 308.7455 | 368.8158 | 269.48
1308.0667 | 384.1314 | 308.7771 | 367.5704 | 269.771
1309.0667 | 383.6012 | 308.745 | 367.111 | 270.08
1310.0667 | 383.0059 | 308.3993 | 366.7349 | 269.7702
1311.0667 | 382.0508 | 310.5844 | 367.1128 | 269.4923
1312.0667 | 380.4858 | 311.2085 | 367.6781 | 269.6216
1313.0667 | 378.3959 | 311.7856 | 367.3754 | 269.2166
1314.0667 | 383.5137 | 313.3818 | 367.3723 | 268.9948
1315.0667 | 383.2696 | 314.2071 | 367.8524 | 269.1235
1316.0667 | 385.8629 | 314.7437 | 367.5446 | 268.4269
1317.0667 | 386.2745 | 316.2141 | 369.689 | 267.9457
1318.0667 | 385.2103 | 316.6627 | 369.6131 | 267.8144
1319.0667 | 386.5896 | 316.6477 | 371.0215 | 267.6412
1320.0667 | 385.2555 | 316.9942 | 372.5971 | 267.9437
1321.0667 | 383.8376 | 318.3349 | 370.9161 | 267.3986
1322.0667 | 382.9569 | 318.9414 | 369.6034 | 267.2516
1323.0667 | 383.1166 | 319.7177 | 369.6704 | 267.0135
1324.0667 | 380.9009 | 319.8274 | 370.7526 | 267.0456
1325.0667 | 380.4627 | 320.2967 | 370.4767 | 266.9309
1326.0667 | 379.5636 | 321.6294 | 370.6348 | 266.3842
1327.0667 | 377.6284 | 322.5385 | 369.5571 | 266.1376
1328.0667 | 376.5611 | 322.0128 | 369.2772 | 265.6022
1329.0667 | 375.9716 | 322.0272 | 368.5567 | 264.9454
1330.0667 | 376.9245 | 325.2092 | 367.8323 | 264.5834
1331.0667 | 377.265 | 326.6726 | 367.3759 | 263.989
1332.0667 | 377.1085 | 327.497 | 367.367 | 263.8936
1333.0667 | 376.0013 | 328.324 | 367.8176 | 263.2817
1334.0667 | 374.79 | 327.9212 | 367.9985 | 262.9045
1335.0667 | 373.5808 | 328.1008 | 366.9705 | 262.7703
1336.0667 | 373.5432 | 328.4456 | 367.5677 | 263.0087
1337.0667 | 371.9398 | 328.4642 | 367.9538 | 263.0454
1338.0667 | 370.8518 | 330.5094 | 366.8159 | 263.1247
1339.0667 | 371.6561 | 332.0587 | 364.7405 | 262.5231
1340.0667 | 371.9869 | 332.8081 | 363.3206 | 262.0522
1341.0667 | 370.6005 | 332.9323 | 364.2017 | 261.6551
1342.0667 | 370.456 | 332.5143 | 365.6221 | 261.8958
1343.0667 | 369.3056 | 333.0267 | 368.6855 | 261.8778
1344.0667 | 371.3076 | 334.1279 | 367.9543 | 262.1675
1345.0667 | 372.1806 | 335.0394 | 367.2481 | 262.3606
1346.0667 | 370.9261 | 336.1317 | 367.9922 | 262.1023
1347.0667 | 370.4448 | 335.7522 | 369.2107 | 262.15
1348.0667 | 370.3207 | 334.8217 | 368.5487 | 262.2216
1349.0667 | 371.2274 | 336.0564 | 366.9152 | 261.8373
1350.0667 | 376.6084 | 336.9252 | 366.3646 | 261.612
1351.0667 | 376.9694 | 336.4083 | 368.1141 | 261.7486
1352.0667 | 376.7261 | 335.193 | 368.6824 | 261.7584
1353.0667 | 376.9487 | 335.9907 | 368.3683 | 261.8717
1354.0667 | 376.7943 | 337.5713 | 368.4921 | 261.6601
1355.0667 | 376.163 | 338.9229 | 368.1696 | 261.9371
1356.0667 | 374.4631 | 338.3017 | 368.1902 | 261.7611
1357.0667 | 373.6165 | 337.3005 | 367.6767 | 262.0003
1358.0667 | 375.1329 | 336.0016 | 367.7494 | 261.9712
1359.0667 | 374.4596 | 334.8693 | 367.2328 | 261.9061
1360.0667 | 374.9739 | 335.2726 | 366.606 | 262.1515
1361.0667 | 375.1026 | 335.133 | 366.5534 | 261.96
1362.0667 | 375.8732 | 334.5168 | 366.0894 | 261.9488
1363.0667 | 378.0235 | 333.914 | 367.2019 | 262.1018
1364.0667 | 377.3934 | 333.113 | 368.0953 | 262.5178
1365.0667 | 376.0571 | 332.2086 | 368.8629 | 262.3679
1366.0667 | 376.4296 | 331.432 | 367.4296 | 261.9759
1367.0667 | 375.3225 | 330.1859 | 367.3016 | 261.5726
1368.0667 | 375.8815 | 329.6326 | 366.9832 | 261.7959
1369.0667 | 375.2461 | 330.2092 | 367.444 | 262.2365
1370.0667 | 373.6673 | 331.9612 | 367.9371 | 262.1468
1371.0667 | 372.6694 | 332.394 | 368.0655 | 262.2019
1372.0667 | 372.9287 | 331.535 | 368.3138 | 262.2548
1373.0667 | 373.5015 | 332.0366 | 369.4824 | 262.4639
1374.0667 | 372.5224 | 331.1475 | 371.8554 | 262.4396
1375.0667 | 372.1342 | 331.0847 | 370.5569 | 262.7843
1376.0667 | 371.4197 | 332.0703 | 371.0245 | 263.0367
1377.0667 | 370.9634 | 331.999 | 369.9334 | 263.2803
1378.0667 | 371.0653 | 331.5154 | 369.1992 | 263.9975
1379.0667 | 369.9945 | 333.8404 | 368.6064 | 263.9709
1380.0667 | 370.3878 | 334.7831 | 367.3866 | 263.9672
1381.0667 | 370.763 | 334.4413 | 367.8277 | 263.9258
1382.0667 | 370.6065 | 334.8118 | 366.6217 | 264.1345
1383.0667 | 370.1845 | 335.0041 | 365.2386 | 263.7422
1384.0667 | 370.2103 | 334.9741 | 362.8781 | 263.4987
1385.0667 | 369.916 | 334.722 | 361.4043 | 263.8588
1386.0667 | 370.2775 | 336.419 | 361.352 | 263.6331
1387.0667 | 369.4295 | 337.0899 | 361.0836 | 263.8332
1388.0667 | 368.9211 | 337.7114 | 361.056 | 263.9929
1389.0667 | 367.7129 | 338.2401 | 359.6043 | 263.9196
1390.0667 | 367.1944 | 337.938 | 359.6259 | 263.436
1391.0667 | 367.5766 | 337.7312 | 358.5898 | 263.1655
1392.0667 | 366.7815 | 338.0217 | 358.2676 | 262.9448
1393.0667 | 366.07 | 337.2244 | 358.6328 | 263.0778
1394.0667 | 365.4666 | 336.2788 | 358.9729 | 263.6934
1395.0667 | 364.6766 | 333.9224 | 357.9035 | 264.0164
1396.2542 | 365.2156 | 331.6638 | 357.5718 | 263.9691
1397.1292 | 365.0315 | 330.1743 | 357.1767 | 263.911
1398.2385 | 366.2421 | 328.6738 | 356.7292 | 263.9418
1399.1135 | 365.8394 | 327.0999 | 356.8325 | 264.3838
1400.5823 | 365.0352 | 326.8723 | 357.3999 | 264.4278
1401.3479 | 364.7934 | 327.1973 | 356.6338 | 264.8884
1402.0667 | 365.3273 | 327.3804 | 356.2508 | 264.7229
1403.0667 | 365.5675 | 326.5499 | 355.7133 | 264.4681
1404.0667 | 367.1884 | 325.7856 | 356.0385 | 265.0826
1405.0667 | 368.3459 | 325.5909 | 356.7713 | 265.7737
1406.0667 | 368.402 | 325.8036 | 357.4732 | 266.3067
1407.0667 | 368.6207 | 325.6075 | 357.1131 | 266.0266
1408.0667 | 367.8181 | 326.0029 | 357.5343 | 265.9718
1409.0667 | 368.2183 | 325.7534 | 356.9152 | 265.8389
1410.0667 | 368.0393 | 325.9861 | 356.801 | 265.7103
1411.0667 | 367.1221 | 326.6551 | 356.4614 | 266.5261
1412.0667 | 366.6283 | 327.6308 | 355.8229 | 266.8468
1413.0667 | 366.0179 | 327.3529 | 356.8577 | 266.8206
1414.0667 | 364.5804 | 328.3723 | 356.6909 | 266.4525
1415.0667 | 362.6359 | 328.9018 | 355.906 | 265.9037
1416.0667 | 362.7777 | 328.4158 | 355.9043 | 265.3415
1417.0667 | 364.1053 | 327.7219 | 355.2815 | 264.9178
1418.0667 | 364.3839 | 327.8313 | 354.3806 | 264.6441
1419.0667 | 363.6588 | 328.315 | 355.4762 | 264.4497
1420.0667 | 364.2901 | 328.0178 | 355.9131 | 264.6624
1421.0667 | 363.9701 | 329.4447 | 355.7054 | 264.6248
1422.0667 | 365.243 | 329.2055 | 354.5482 | 264.3668
1423.0667 | 365.0394 | 328.7211 | 353.7309 | 263.9626
1424.0667 | 364.1389 | 329.2104 | 353.3774 | 263.7074
1425.0667 | 365.5236 | 331.43 | 352.4756 | 263.4933
1426.0667 | 367.0824 | 333.1273 | 352.3161 | 263.7253
1427.0667 | 368.2088 | 336.3481 | 353.2087 | 264.0256
1428.0667 | 372.1975 | 338.5328 | 353.7221 | 264.2699
1429.0667 | 374.7059 | 339.0481 | 354.3832 | 264.7798
1430.0667 | 377.9264 | 339.3901 | 354.1294 | 264.5136
1431.0667 | 377.7472 | 340.6382 | 353.7157 | 264.5604
1432.0667 | 378.6736 | 341.6035 | 353.1371 | 264.634
1433.0667 | 379.1407 | 341.5835 | 354.6042 | 264.704
1434.0823 | 378.3854 | 340.6694 | 354.4954 | 264.7277
1435.0667 | 378.0847 | 339.7936 | 354.4844 | 265.0807
1436.0823 | 377.0079 | 338.563 | 353.6788 | 265.0322
1437.0667 | 376.4744 | 337.43 | 354.3736 | 265.0907
1438.0979 | 376.3666 | 336.6908 | 354.8856 | 265.6568
1439.0667 | 375.744 | 335.9198 | 354.8972 | 265.2713
1440.0667 | 374.3792 | 335.2707 | 354.7833 | 265.8464
1441.0667 | 375.3632 | 334.5108 | 354.2891 | 265.7089
1442.0667 | 373.4596 | 332.9511 | 354.6046 | 265.6907
1443.0667 | 373.2487 | 332.7576 | 354.5804 | 265.4134
1444.0667 | 373.3021 | 332.1014 | 353.7978 | 265.1636
1445.0667 | 373.202 | 332.2984 | 353.9808 | 264.9482
1446.0667 | 372.038 | 331.1438 | 355.0374 | 265.0672
1447.0667 | 370.1726 | 329.9513 | 355.0588 | 265.3011
1448.0667 | 369.5881 | 328.6222 | 354.5815 | 265.1114
1449.0667 | 368.2225 | 326.861 | 353.6477 | 265.1404
1450.0667 | 368.3096 | 326.4667 | 353.3718 | 265.3481
1451.0667 | 368.7586 | 326.5943 | 353.0287 | 265.9184
1452.0667 | 369.8263 | 326.0286 | 353.3926 | 267.119
1453.0667 | 370.6094 | 325.5717 | 353.8919 | 268.6238
1454.0667 | 370.6743 | 325.2013 | 354.493 | 268.7643
1455.0823 | 370.5461 | 324.342 | 353.661 | 268.8206
1456.0667 | 370.1916 | 324.6923 | 353.6464 | 268.3517
1457.0667 | 369.6517 | 324.298 | 353.2264 | 268.0641
1458.0667 | 369.6768 | 323.3927 | 353.4753 | 267.7392
1459.0667 | 370.6829 | 322.5099 | 353.4 | 268.1262
1460.0667 | 372.4912 | 321.1307 | 354.6401 | 268.7919
1461.0667 | 374.3604 | 320.004 | 354.8547 | 270.2535
1462.0667 | 375.9431 | 320.0122 | 355.5198 | 271.6007
1463.0667 | 376.7397 | 319.9546 | 355.5244 | 271.572
1464.0667 | 378.0878 | 320.3006 | 355.8737 | 271.1538
1465.0667 | 378.0721 | 319.751 | 356.4117 | 270.933
1466.0667 | 377.0289 | 319.2376 | 357.3124 | 271.8357
1467.0667 | 377.0811 | 318.207 | 357.112 | 272.836
1468.0823 | 378.9215 | 317.109 | 356.1239 | 273.3713
1469.0979 | 379.3595 | 317.0331 | 356.1809 | 273.5484
1470.0823 | 380.14 | 315.8347 | 355.4552 | 274.4298
1471.0823 | 382.0277 | 314.7559 | 355.4683 | 275.128
1472.0667 | 381.9951 | 313.4286 | 354.5025 | 276.3423
1473.0823 | 382.5933 | 311.9417 | 353.3407 | 277.3847
1474.0667 | 384.2037 | 311.2419 | 353.4561 | 278.2301
1475.0667 | 383.7752 | 311.1435 | 353.6021 | 278.1267
1476.0667 | 382.3301 | 310.7392 | 353.9862 | 278.1938
1477.0667 | 382.856 | 311.1888 | 353.2221 | 277.6313
1478.0667 | 381.8048 | 312.3087 | 353.6252 | 277.52
1479.0667 | 379.7439 | 312.2829 | 353.103 | 277.2243
1480.0667 | 378.7581 | 313.2113 | 352.3181 | 277.1823
1481.0667 | 376.4898 | 312.5547 | 352.0342 | 276.7267
1482.0667 | 375.4743 | 312.4708 | 352.2934 | 276.4357
1483.0667 | 374.9134 | 311.385 | 351.7522 | 276.0946
1484.0667 | 377.0905 | 309.9881 | 350.3619 | 276.1864
1485.0823 | 377.921 | 308.6187 | 349.573 | 277.1403
1486.0667 | 379.3469 | 307.9484 | 349.8225 | 278.0675
1487.0667 | 379.0754 | 308.8679 | 350.8631 | 278.3795
1488.0667 | 377.9981 | 309.066 | 351.0402 | 278.0587
1489.0667 | 377.9759 | 309.7199 | 351.252 | 277.9976
1490.0667 | 378.1332 | 309.1731 | 351.2734 | 277.5125
1491.0667 | 379.9101 | 308.7257 | 351.0689 | 276.9924
1492.0667 | 379.84 | 309.0591 | 351.595 | 276.8582
1493.0667 | 378.7444 | 309.9366 | 352.0087 | 276.5713
1494.0667 | 376.457 | 310.78 | 351.9252 | 275.8022
1495.0667 | 374.7252 | 312.2043 | 351.9386 | 275.0948
1496.0667 | 373.2576 | 312.5361 | 351.3175 | 274.4551
1497.0667 | 373.2027 | 313.0361 | 351.6185 | 273.8895
1498.0667 | 373.2711 | 313.1176 | 351.565 | 273.3642
1499.0667 | 373.881 | 313.0066 | 352.0995 | 273.0707
1500.0667 | 374.356 | 312.391 | 353.3959 | 273.0282
1501.0667 | 374.795 | 311.7053 | 352.394 | 272.5265
1502.0667 | 375.2007 | 311.389 | 352.1855 | 272.1627
1503.0667 | 373.9814 | 311.4171 | 352.5402 | 272.1085
1504.0667 | 374.9128 | 311.0624 | 352.6296 | 272.9154
1505.0667 | 376.0622 | 311.2601 | 353.2334 | 272.9035
1506.0667 | 376.3572 | 311.1624 | 354.1314 | 273.4186
1507.0667 | 377.9542 | 310.8847 | 354.3948 | 273.6224
1508.0667 | 377.5146 | 311.0706 | 354.7802 | 274.3198
1509.0667 | 377.3203 | 311.1664 | 354.4671 | 274.3156
1510.0667 | 377.2092 | 310.7546 | 355.5735 | 274.6484
1511.0667 | 376.9134 | 311.6239 | 357.5992 | 274.7971
1512.0667 | 376.6404 | 312.8707 | 357.9116 | 275.004
1513.0667 | 375.7724 | 314.2085 | 357.9461 | 274.4577
1514.0667 | 374.422 | 315.8377 | 357.9369 | 274.1404
1515.0667 | 373.1112 | 316.2489 | 357.2715 | 273.6933
1516.0667 | 371.9439 | 316.6256 | 356.497 | 273.3387
1517.0667 | 370.1544 | 317.5341 | 354.8683 | 272.791
1518.0667 | 369.3062 | 318.1036 | 354.0832 | 272.2043
1519.0667 | 369.2855 | 318.904 | 354.4551 | 271.7793
1520.0667 | 368.4793 | 320.762 | 353.9351 | 271.3504
1521.0667 | 367.3207 | 322.6337 | 353.5252 | 271.1943
1522.0667 | 366.4353 | 322.6917 | 351.9265 | 271.4137
1523.0667 | 365.5307 | 321.6393 | 350.5708 | 271.6673
1524.0667 | 366.3342 | 320.209 | 350.0219 | 271.4339
1525.0667 | 367.5867 | 318.9103 | 349.9101 | 272.2011
1526.0667 | 367.2884 | 318.7269 | 350.1081 | 272.8037
1527.0667 | 365.5856 | 318.907 | 349.7309 | 272.4401
1528.0667 | 365.5879 | 319.6872 | 349.2264 | 271.8723
1529.0667 | 365.493 | 319.5801 | 349.7586 | 272.201
1530.0667 | 364.8965 | 318.8328 | 348.6694 | 272.1663
1531.0667 | 365.9734 | 317.7911 | 348.9263 | 272.3634
1532.0667 | 367.9506 | 316.6709 | 349.5588 | 273.3333
1533.0667 | 367.8663 | 316.2638 | 349.9241 | 273.8585
1534.0667 | 368.9416 | 315.9955 | 349.5104 | 273.7521
1535.0667 | 368.6415 | 315.4912 | 350.0108 | 273.3737
1536.0667 | 370.6576 | 314.9259 | 350.2013 | 273.1494
1537.0667 | 372.8956 | 314.2805 | 350.9309 | 273.1933
1538.0667 | 374.9427 | 313.5401 | 351.5627 | 273.2867
1539.0667 | 377.9613 | 312.6613 | 351.9327 | 273.8317
1540.0667 | 376.2105 | 314.157 | 353.0575 | 273.8943
1541.0667 | 373.4852 | 315.3613 | 351.9579 | 273.6839
1542.0667 | 371.4047 | 315.2731 | 350.4013 | 273.0807
1543.0667 | 370.0478 | 314.3635 | 349.5972 | 272.8888
1544.0667 | 369.7231 | 314.9344 | 348.7005 | 272.7952
1545.0667 | 369.4879 | 314.9715 | 348.2301 | 273.0208
1546.0667 | 369.0547 | 315.8081 | 348.7599 | 272.6712
1547.0667 | 368.7271 | 315.6637 | 349.1494 | 272.8133
1548.0667 | 368.5632 | 316.1064 | 349.4866 | 272.7615
1549.0667 | 368.1744 | 316.657 | 350.0642 | 272.5061
1550.0667 | 367.0267 | 316.7528 | 348.9235 | 272.2553
1551.0667 | 366.547 | 316.8016 | 348.6786 | 271.862
1552.0667 | 365.7142 | 317.2851 | 348.9089 | 271.5616
1553.0667 | 363.9799 | 317.8069 | 348.7664 | 271.2468
1554.0667 | 362.6279 | 317.6927 | 348.7986 | 270.9243
1555.0667 | 362.8833 | 318.7449 | 348.1741 | 270.4747
1556.0667 | 362.6656 | 319.5688 | 348.4484 | 270.2947
1557.0667 | 362.6944 | 319.5138 | 348.4133 | 270.0468
1558.0667 | 364.5172 | 318.8118 | 348.4029 | 269.9097
1559.0667 | 364.4585 | 319.0007 | 348.8774 | 269.6716
1560.0667 | 363.0265 | 319.1951 | 348.0485 | 269.6931
1561.0667 | 362.3243 | 319.1583 | 346.2807 | 269.494
1562.0667 | 361.8326 | 318.9533 | 345.931 | 269.2074
1563.0667 | 362.4803 | 319.5445 | 346.6885 | 269.0481
1564.0667 | 363.0485 | 319.1894 | 346.9819 | 269.0439
1565.0667 | 362.8607 | 317.9754 | 346.608 | 269.5443
1566.0667 | 364.5238 | 316.2417 | 345.9181 | 269.9089
1567.0667 | 368.2904 | 314.5409 | 344.905 | 270.5508
1568.0667 | 375.6618 | 313.0924 | 344.9107 | 272.557
1569.0667 | 379.2308 | 312.6641 | 347.1717 | 273.8714
1570.0667 | 378.1374 | 312.4219 | 348.4343 | 274.9954
1571.0667 | 374.539 | 313.539 | 347.9327 | 274.5979
1572.0667 | 371.9429 | 314.4182 | 346.5319 | 273.9334
1573.0667 | 371.3594 | 314.6423 | 345.0755 | 273.3732
1574.0667 | 369.9129 | 314.5728 | 345.3779 | 273.4456
1575.0823 | 369.8899 | 313.787 | 345.0763 | 273.8588
1576.0667 | 371.9921 | 312.4644 | 345.5813 | 274.7864
1577.0667 | 372.9317 | 311.091 | 345.3503 | 275.673
1578.0667 | 376.4263 | 310.5451 | 346.1888 | 276.0273
1579.0667 | 374.5832 | 310.1646 | 346.3309 | 275.6249
1580.0667 | 375.8208 | 309.9336 | 345.9961 | 275.159
1581.0667 | 377.5088 | 309.1895 | 346.5772 | 275.6035
1582.0667 | 376.4138 | 309.8019 | 347.7864 | 275.6835
1583.0667 | 375.7169 | 309.61 | 347.5572 | 275.153
1584.0667 | 376.1911 | 309.1887 | 347.0002 | 275.3039
1585.0667 | 377.8538 | 308.5543 | 346.8673 | 275.9716
1586.0667 | 377.6633 | 307.6484 | 346.2377 | 276.1689
1587.0667 | 378.1271 | 307.4472 | 346.4795 | 276.6137
1588.0667 | 376.2214 | 307.2107 | 347.0851 | 276.6527
1589.0667 | 374.2349 | 306.9929 | 346.5352 | 276.2362
1590.0667 | 372.9572 | 307.2662 | 346.1 | 275.6317
1591.0667 | 373.4728 | 307.2152 | 345.2914 | 275.2858
1592.0667 | 374.2087 | 306.6616 | 345.9013 | 275.92
1593.0667 | 380.6082 | 307.3945 | 347.4459 | 276.2745
1594.0667 | 380.5746 | 308.181 | 347.8701 | 276.0738
1595.0667 | 377.7845 | 308.2383 | 347.4011 | 275.5872
1596.0667 | 374.8792 | 308.7738 | 346.6133 | 274.9277
1597.0667 | 372.5274 | 310.2472 | 346.7993 | 274.3165
1598.0667 | 370.3929 | 312.879 | 346.715 | 273.969
1599.0667 | 369.4127 | 314.89 | 346.5346 | 273.5415
1600.0667 | 368.7012 | 316.3332 | 347.5943 | 273.4856
1601.0667 | 366.0284 | 316.9904 | 347.2951 | 273.0516
1602.0667 | 364.0158 | 316.8589 | 346.293 | 272.4521
1603.0667 | 363.8998 | 316.7197 | 345.4572 | 272.1239
1604.0667 | 362.9314 | 316.5135 | 344.8991 | 271.9645
1605.0667 | 361.2197 | 316.3176 | 344.1655 | 271.876
1606.0667 | 360.2544 | 316.2745 | 343.8895 | 271.9684
1607.0667 | 360.6781 | 316.2625 | 344.0097 | 271.6527
1608.0667 | 361.0296 | 318.978 | 344.338 | 271.5756
1609.0667 | 360.5303 | 320.8871 | 344.8287 | 271.2221
1610.0667 | 358.6679 | 322.4381 | 343.9776 | 270.7996
1611.0667 | 358.2878 | 323.0525 | 342.7485 | 270.4524
1612.0667 | 358.1208 | 324.4883 | 342.8917 | 270.1452
1613.0667 | 358.0756 | 325.7681 | 343.3424 | 270.2254
1614.0667 | 357.3133 | 326.8388 | 343.735 | 269.9426
1615.0667 | 357.1619 | 326.3412 | 344.4304 | 269.8273
1616.0667 | 356.5822 | 325.0091 | 344.6289 | 269.8532
1617.0667 | 355.867 | 323.3463 | 343.9398 | 269.8394
1618.0667 | 355.7173 | 321.6075 | 343.394 | 269.8495
1619.0667 | 356.0929 | 320.46 | 343.4918 | 270.1934
1620.0667 | 357.1159 | 319.8775 | 343.3628 | 270.5517
1621.0667 | 358.4741 | 319.4539 | 344.6054 | 270.964
1622.0667 | 358.4551 | 318.6311 | 345.9731 | 271.3701
1623.0667 | 359.8295 | 317.9279 | 346.2125 | 271.3035
1624.0667 | 360.3817 | 317.7401 | 347.6069 | 271.4003
1625.0667 | 360.8325 | 318.4768 | 349.0126 | 271.4961
1626.0667 | 361.7036 | 317.9573 | 348.8194 | 271.3948
1627.0667 | 361.9283 | 317.1493 | 348.5684 | 271.5436
1628.0667 | 363.1163 | 316.1641 | 348.9827 | 271.8085
1629.0667 | 364.0525 | 316.348 | 348.5906 | 272.0812
1630.0667 | 366.2046 | 316.4255 | 348.868 | 272.2012
1631.0667 | 367.0556 | 316.3551 | 349.6088 | 272.3113
1632.0667 | 368.7153 | 315.7744 | 349.9316 | 272.6412
1633.0667 | 370.0854 | 316.4375 | 351.6347 | 273.1913
1634.0667 | 370.7086 | 317.3488 | 352.4945 | 273.307
1635.0667 | 372.0507 | 317.6534 | 353.053 | 273.5963
1636.0667 | 372.6173 | 319.5116 | 353.6361 | 273.8901
1637.0667 | 372.3517 | 320.2467 | 355.1271 | 274.0678
1638.0667 | 373.3197 | 320.5411 | 355.0773 | 274.5241
1639.0667 | 373.2243 | 320.9883 | 354.2698 | 274.4806
1640.0667 | 373.9537 | 319.908 | 353.37 | 275.0341
1641.0667 | 375.3163 | 319.9808 | 352.9598 | 275.7251
1642.0667 | 373.9815 | 319.7904 | 352.2754 | 275.9805
1643.0667 | 372.9698 | 319.3728 | 351.6577 | 275.9406
1644.0667 | 372.816 | 318.8262 | 350.9092 | 275.7233
1645.0667 | 373.3593 | 318.0086 | 351.5344 | 275.5281
1646.0667 | 372.4853 | 317.8203 | 352.191 | 275.363
1647.0667 | 371.7515 | 317.872 | 350.9584 | 275.1502
1648.0667 | 371.4107 | 317.3637 | 350.7676 | 275.1655
1649.0667 | 372.1484 | 317.0367 | 350.9949 | 275.5944
1650.0667 | 373.9899 | 317.1796 | 352.5651 | 275.5723
1651.0667 | 374.8308 | 317.4711 | 352.022 | 275.4102
1652.0667 | 373.1104 | 316.7581 | 351.9363 | 274.9455
1653.0667 | 372.1369 | 318.1755 | 351.1242 | 274.582
1654.0667 | 371.425 | 318.2045 | 351.6182 | 274.3126
1655.0667 | 369.9319 | 318.4195 | 351.5438 | 273.9744
1656.0667 | 368.2174 | 320.315 | 351.1185 | 273.6982
1657.0667 | 367.0647 | 321.7742 | 349.7955 | 273.3029
1658.0667 | 365.9463 | 322.832 | 349.1167 | 272.9697
1659.0667 | 364.8313 | 323.0994 | 348.5082 | 272.7437
1660.0667 | 364.2211 | 322.4169 | 347.9113 | 272.5755
1661.0667 | 365.079 | 322.4705 | 347.5434 | 273.0259
1662.0667 | 366.9535 | 322.5612 | 347.6181 | 273.0747
1663.0667 | 369.9018 | 321.3872 | 349.3988 | 273.218
1664.0667 | 369.1633 | 320.8373 | 350.878 | 273.4438
1665.0667 | 369.3286 | 320.2664 | 351.2575 | 273.5874
1666.0667 | 369.5521 | 320.4468 | 351.7936 | 273.5801
1667.0667 | 370.778 | 319.7379 | 353.0221 | 273.6583
1668.0667 | 371.3569 | 318.7659 | 354.0453 | 273.9673
1669.0667 | 371.2502 | 317.8927 | 353.7458 | 274.7588
1670.0667 | 372.4509 | 317.2235 | 353.462 | 275.2281
1671.0667 | 373.472 | 317.2176 | 353.7821 | 275.832
1672.0667 | 373.7024 | 318.0568 | 353.595 | 276.1337
1673.0667 | 374.1573 | 318.5134 | 354.0106 | 276.3269
1674.0667 | 374.8029 | 318.694 | 354.8713 | 276.8301
1675.0667 | 374.4719 | 319.0234 | 355.0946 | 277.2346
1676.0667 | 373.5477 | 318.9686 | 355.1314 | 277.2622
1677.0667 | 372.7639 | 319.0554 | 354.8454 | 277.21
1678.0667 | 371.7291 | 319.5045 | 354.6428 | 276.9864
1679.0667 | 371.3684 | 320.6853 | 355.5029 | 276.8963
1680.0667 | 370.4142 | 322.2745 | 354.5555 | 276.7284
1681.0667 | 369.641 | 322.0411 | 354.1019 | 276.4109
1682.0667 | 370.1102 | 322.9108 | 353.1644 | 276.1967
1683.0667 | 370.394 | 322.4779 | 352.1933 | 275.7668
1684.0667 | 369.5499 | 323.4129 | 351.8706 | 275.502
1685.0667 | 370.1234 | 323.4324 | 351.1787 | 275.1191
1686.0667 | 369.6146 | 324.9372 | 351.5219 | 275.0123
1687.0667 | 368.2266 | 325.2034 | 351.1808 | 274.7768
1688.0667 | 367.2896 | 324.7206 | 350.7935 | 274.6368
1689.0667 | 368.0505 | 323.8485 | 350.7964 | 274.9463
1690.0667 | 368.5674 | 322.463 | 351.3516 | 275.3385
1691.0667 | 370.4755 | 322.4328 | 352.79 | 275.4
1692.0667 | 371.4575 | 322.3278 | 355.5534 | 275.457
1693.0667 | 372.2742 | 321.797 | 356.6788 | 275.4362
1694.0667 | 372.8084 | 322.0185 | 358.1072 | 275.52
1695.0667 | 373.2957 | 321.5481 | 359.4482 | 275.5026
1696.0667 | 373.2518 | 321.6805 | 359.7886 | 276.034
1697.0667 | 375.205 | 321.798 | 360.1345 | 276.3155
1698.0667 | 377.2227 | 321.8603 | 360.1583 | 276.9151
1699.0667 | 376.9298 | 321.7089 | 360.2501 | 277.4196
1700.0667 | 378.0652 | 321.6449 | 359.4812 | 277.8416
1701.0667 | 378.1688 | 321.698 | 358.6134 | 277.8043
1702.0667 | 378.0381 | 321.5214 | 358.2638 | 277.4977
1703.0667 | 378.2537 | 321.7908 | 358.0585 | 277.1959
1704.0667 | 378.0927 | 322.225 | 357.3936 | 277.2591
1705.0667 | 379.6152 | 322.1868 | 357.5813 | 277.7235
1706.0667 | 381.3675 | 322.3696 | 358.232 | 278.5539
1707.0667 | 383.4135 | 322.5338 | 359.6135 | 279.4616
1708.0667 | 385.3797 | 321.9782 | 360.1324 | 280.5663
1709.0667 | 387.417 | 321.5263 | 360.6102 | 281.2511
1710.0667 | 387.7673 | 322.9882 | 361.5701 | 281.9154
1711.0667 | 388.2959 | 324.2735 | 362.8932 | 282.6221
1712.0667 | 389.3077 | 325.1614 | 364.095 | 283.2791
1713.0667 | 392.2093 | 326.373 | 365.6057 | 284.639
1714.0667 | 396.4274 | 327.9788 | 368.457 | 285.0939
1715.0667 | 405.6953 | 329.7979 | 370.6096 | 285.9646
1716.0667 | 408.5613 | 331.4507 | 371.8099 | 287.1007
1717.0667 | 407.7366 | 331.9962 | 372.9089 | 287.7328
1718.0667 | 407.6872 | 332.2931 | 373.2046 | 288.1457
1719.0667 | 409.6236 | 331.583 | 373.0887 | 288.8564
1720.0667 | 410.9916 | 330.9259 | 373.6459 | 289.9144
1721.0667 | 412.888 | 330.1866 | 373.6147 | 291.2384
1722.0667 | 412.8199 | 329.8709 | 373.8243 | 292.8221
1723.0667 | 414.7964 | 329.1719 | 373.9403 | 293.3756
1724.0667 | 414.3291 | 328.5574 | 373.7851 | 293.7388
1725.0667 | 414.122 | 328.1345 | 373.3711 | 294.0039
1726.0667 | 415.1712 | 328.1839 | 374.5057 | 294.7604
1727.0667 | 412.5851 | 328.7019 | 374.2291 | 294.4364
1728.0667 | 409.7488 | 330.0623 | 373.9659 | 293.8079
1729.0667 | 408.1798 | 330.6821 | 372.9675 | 293.0986
1730.0667 | 407.7739 | 330.3848 | 372.594 | 292.6569
1731.0667 | 407.0727 | 331.4907 | 374.2127 | 292.4566
1732.0667 | 406.0473 | 332.462 | 375.4279 | 292.2556
1733.0667 | 404.208 | 334.3879 | 378.7869 | 292.1667
1734.0667 | 400.8747 | 334.9496 | 378.2783 | 291.8552
1735.0667 | 398.4571 | 336.5389 | 377.1224 | 291.3889
1736.0667 | 396.0405 | 339.9283 | 376.9196 | 290.7678
1737.0667 | 393.4116 | 344.2605 | 375.8719 | 290.2511
1738.0667 | 390.9471 | 348.154 | 375.2274 | 289.9014
1739.0667 | 389.4029 | 348.7375 | 373.8991 | 289.5565
1740.0667 | 387.9031 | 350.0876 | 373.4537 | 289.1336
1741.0667 | 387.1411 | 350.1262 | 373.1382 | 288.7526
1742.0667 | 385.3908 | 352.0275 | 371.8356 | 288.7315
1743.0667 | 385.3264 | 353.5227 | 372.239 | 289.2937
1744.0667 | 384.4042 | 354.4982 | 374.5141 | 289.5634
1745.0667 | 383.7666 | 355.9168 | 375.8766 | 290.3355
1746.0667 | 382.6096 | 356.7119 | 376.007 | 289.8927
1747.0667 | 381.2873 | 357.9874 | 374.447 | 289.5529
1748.0667 | 380.3927 | 359.0374 | 373.4698 | 289.3566
1749.0667 | 379.8116 | 361.3885 | 373.0889 | 289.3349
1750.0667 | 380.0573 | 363.2442 | 372.2266 | 289.0904
1751.0667 | 380.6463 | 364.9664 | 372.786 | 288.6879
1752.0667 | 380.8734 | 364.6172 | 373.7978 | 288.5825
1753.0667 | 381.8243 | 363.4613 | 373.8663 | 288.3389
1754.0667 | 381.7957 | 361.5022 | 373.8032 | 288.2636
1755.0667 | 385.7695 | 359.2341 | 374.2807 | 288.7165
1756.0667 | 390.0494 | 356.9096 | 375.802 | 289.2887
1757.0667 | 392.0464 | 355.5494 | 378.1827 | 289.7139
1758.0667 | 394.264 | 357.8268 | 378.8053 | 289.7471
1759.0667 | 394.9496 | 358.9036 | 380.8196 | 289.6517
1760.0667 | 394.6399 | 360.5676 | 381.8403 | 289.7027
1761.0667 | 395.5442 | 361.3246 | 381.326 | 289.821
1762.0667 | 395.76 | 360.9019 | 381.621 | 290.1281
1763.0667 | 396.4462 | 359.0214 | 381.6955 | 290.5678
1764.0667 | 398.0491 | 357.1655 | 380.9325 | 291.1759
1765.0667 | 398.9072 | 355.6254 | 381.3367 | 292.0692
1766.0667 | 400.4787 | 355.7762 | 382.1388 | 292.5434
1767.0667 | 400.3067 | 355.8305 | 381.8595 | 292.7868
1768.0667 | 398.47 | 357.3294 | 382.5785 | 292.9316
1769.0667 | 398.6674 | 356.8723 | 382.0191 | 292.8023
1770.0667 | 399.158 | 355.5133 | 381.8597 | 292.8165
1771.0667 | 399.8505 | 353.7821 | 380.9974 | 292.8564
1772.0667 | 402.2142 | 352.8277 | 381.3797 | 294.5111
1773.0667 | 404.4331 | 351.6547 | 381.4828 | 295.5915
1774.0667 | 405.0034 | 352.6008 | 381.1461 | 295.8891
1775.0667 | 404.1575 | 353.5401 | 380.8179 | 295.5584
1776.0667 | 404.7519 | 353.2434 | 380.5884 | 295.6796
1777.0667 | 407.8885 | 352.5822 | 381.5466 | 297.1147
1778.0667 | 409.233 | 353.4435 | 382.6814 | 297.5168
1779.0667 | 408.3494 | 353.9924 | 382.9146 | 297.75
1780.0667 | 406.4357 | 356.061 | 381.5273 | 297.3457
1781.0667 | 404.7513 | 355.869 | 380.0685 | 296.8448
1782.0667 | 404.3553 | 356.1004 | 379.9003 | 297.3352
1783.0667 | 403.287 | 355.3821 | 380.549 | 297.8625
1784.0667 | 402.7421 | 355.4057 | 381.2085 | 298.2282
1785.0667 | 401.0438 | 355.7108 | 382.0195 | 298.1237
1786.0667 | 399.3166 | 355.4486 | 381.2369 | 297.547
1787.0667 | 398.4594 | 355.8095 | 381.2635 | 297.1394
1788.0667 | 398.0967 | 356.2777 | 381.2281 | 296.6391
1789.0667 | 399.6472 | 356.0423 | 381.0401 | 296.3463
1790.0667 | 400.3635 | 356.2859 | 381.9066 | 296.4597
1791.0667 | 399.3089 | 356.3001 | 382.3726 | 296.8879
1792.0667 | 400.1027 | 356.43 | 382.3893 | 296.8236
1793.0667 | 402.1466 | 355.1941 | 382.0911 | 296.9845
1794.0667 | 409.8655 | 353.1337 | 382.3635 | 297.6528
1795.0667 | 413.1803 | 351.3631 | 384.5281 | 299.1655
1796.0667 | 414.8221 | 349.8767 | 384.6436 | 300.6785
1797.0667 | 415.3953 | 349.7714 | 384.1319 | 301.6472
1798.0667 | 414.9822 | 351.8105 | 384.0649 | 301.5367
1799.0667 | 413.1033 | 352.4613 | 385.2496 | 301.7657
1800.0667 | 410.9549 | 352.3836 | 384.2991 | 301.9934
1801.0667 | 412.369 | 352.1379 | 382.876 | 301.6565
1802.0667 | 412.1029 | 354.4242 | 383.663 | 302.4527
1803.0667 | 410.8363 | 356.1928 | 383.1145 | 301.9507
1804.0667 | 409.6955 | 357.0723 | 382.4984 | 301.8665
1805.0667 | 409.3639 | 357.6034 | 383.8018 | 302.2655
1806.0667 | 409.694 | 356.8824 | 384.4405 | 302.2509
1807.0667 | 409.0765 | 357.2098 | 384.3554 | 302.0301
1808.0667 | 408.9093 | 358.1439 | 384.5753 | 301.7616
1809.0667 | 408.7761 | 359.0599 | 388.5167 | 301.69
1810.0667 | 408.3095 | 358.9748 | 388.9666 | 301.6816
1811.0667 | 409.5305 | 359.3574 | 388.8169 | 302.2813
1812.0667 | 408.0295 | 358.862 | 389.0394 | 302.4283
1813.0667 | 406.3501 | 358.6736 | 388.821 | 301.9976
1814.0667 | 406.5131 | 358.0263 | 388.5204 | 303.1842
1815.0667 | 407.0751 | 358.0758 | 388.5966 | 303.3289
1816.0667 | 407.7322 | 358.0829 | 387.8727 | 303.1589
1817.0667 | 407.4299 | 358.4352 | 388.2202 | 303.2025
1818.0667 | 406.1634 | 358.5898 | 388.0608 | 302.5756
1819.0667 | 406.4419 | 358.1122 | 387.9557 | 302.7436
1820.0667 | 406.5155 | 357.3728 | 387.8237 | 302.6349
1821.0667 | 409.891 | 355.4239 | 385.901 | 302.9653
1822.0667 | 412.1997 | 353.577 | 384.904 | 303.624
1823.0667 | 412.5723 | 353.4413 | 385.098 | 303.9895
1824.0667 | 410.194 | 354.499 | 385.0049 | 303.8275
1825.0667 | 409.7821 | 355.7931 | 383.9717 | 303.5676
1826.0667 | 410.43 | 357.4277 | 383.9385 | 303.7104
1827.0667 | 411.8497 | 358.5446 | 385.7317 | 304.4135
1828.0667 | 413.3227 | 359.94 | 387.2159 | 304.8048
1829.0667 | 413.6647 | 359.8508 | 388.3218 | 304.9041
1830.0667 | 413.8709 | 360.1179 | 388.9596 | 304.975
1831.0667 | 414.2511 | 359.6846 | 389.7511 | 304.9651
1832.0667 | 415.9941 | 358.5893 | 390.6644 | 305.3021
1833.0667 | 416.7408 | 357.7663 | 390.3017 | 305.2724
1834.0667 | 417.637 | 357.4666 | 390.6371 | 305.3461
1835.0667 | 418.7928 | 358.2529 | 391.0122 | 305.2183
1836.0667 | 420.5325 | 358.7837 | 391.5314 | 305.3739
1837.0667 | 419.5201 | 358.9347 | 391.9803 | 305.2056
1838.0667 | 419.5998 | 358.5165 | 392.5163 | 305.8922
1839.0667 | 420.5694 | 359.6292 | 393.6589 | 305.8554
1840.0667 | 418.3515 | 361.2548 | 393.8667 | 305.598
1841.0667 | 415.924 | 361.1126 | 392.7471 | 304.995
1842.0667 | 416.571 | 360.7125 | 391.9608 | 304.5913
1843.0667 | 416.47 | 360.6556 | 391.5753 | 304.4456
1844.0667 | 417.3085 | 361.1626 | 391.7588 | 304.842
1845.0667 | 416.8295 | 360.5634 | 391.3718 | 305.0406
1846.0667 | 419.2139 | 359.9516 | 391.9006 | 305.6145
1847.0667 | 421.8656 | 359.4122 | 392.8911 | 306.5887
1848.0667 | 422.7974 | 359.6715 | 393.7265 | 307.0618
1849.0667 | 421.7736 | 359.5158 | 392.8272 | 307.5368
1850.0667 | 421.6828 | 359.3033 | 393.12 | 307.5124
1851.0667 | 420.6633 | 358.8089 | 392.9347 | 307.3439
1852.0667 | 419.9875 | 358.1423 | 392.5603 | 307.3414
1853.0667 | 419.6119 | 357.8764 | 391.795 | 307.1192
1854.0667 | 421.0722 | 357.4484 | 391.9391 | 308.4751
1855.0667 | 422.5157 | 356.2301 | 391.9649 | 309.3751
1856.0667 | 424.6049 | 356.6724 | 392.161 | 310.1625
1857.0667 | 426.3445 | 358.162 | 393.144 | 310.7422
1858.0667 | 424.057 | 358.1394 | 392.2803 | 310.1468
1859.0667 | 422.4721 | 357.2598 | 390.8293 | 309.4772
1860.0667 | 421.1932 | 355.6131 | 389.8632 | 309.811
1861.0667 | 424.385 | 354.1997 | 389.3173 | 310.7658
1862.0667 | 423.5731 | 353.8436 | 390.448 | 311.2968
1863.0667 | 422.6243 | 353.9097 | 390.1863 | 310.7278
1864.0667 | 420.8979 | 353.6439 | 389.8301 | 309.8921
1865.0667 | 419.0606 | 354.5288 | 390.4923 | 309.2646
1866.0667 | 417.3712 | 355.6223 | 391.231 | 309.0315
1867.0667 | 417.1707 | 355.0491 | 390.7277 | 308.3452
1868.0667 | 416.7103 | 355.9439 | 390.948 | 307.9943
1869.0667 | 415.3234 | 356.171 | 392.7495 | 307.7529
1870.0667 | 414.04 | 357.4011 | 392.4005 | 307.5506
1871.0667 | 412.1986 | 359.302 | 391.7548 | 307.0954
1872.0667 | 410.7088 | 359.8264 | 391.0431 | 306.5266
1873.0667 | 410.1869 | 360.3014 | 390.0983 | 305.9115
1874.0667 | 408.2455 | 359.5759 | 389.4605 | 305.387
1875.0667 | 406.9746 | 360.3425 | 389.1096 | 304.9123
1876.0667 | 404.9883 | 360.3573 | 389.4074 | 304.4426
1877.0667 | 403.7491 | 360.3356 | 390.3042 | 304.0674
1878.0667 | 402.1639 | 359.3801 | 389.1908 | 303.6761
1879.0667 | 402.1962 | 358.2146 | 388.6159 | 303.476
1880.0667 | 402.1519 | 357.5072 | 388.3492 | 303.4412
1881.0667 | 403.4456 | 357.2053 | 388.7012 | 303.2352
1882.0823 | 403.0157 | 358.0415 | 388.8782 | 303.0909
1883.0823 | 403.6683 | 358.1649 | 387.9887 | 302.9182
1884.0667 | 402.9985 | 358.1306 | 388.5737 | 303.0504
1885.0667 | 402.9631 | 359.2266 | 388.5482 | 302.9254
1886.0667 | 403.247 | 360.9605 | 389.2023 | 302.8947
1887.0667 | 402.5114 | 363.2233 | 390.3247 | 302.7882
1888.0667 | 402.0551 | 364.6289 | 389.8459 | 302.5184
1889.0667 | 401.1554 | 365.239 | 389.5543 | 302.2841
1890.0823 | 401.0378 | 365.5335 | 390.2947 | 302.064
1891.0667 | 400.6274 | 366.1526 | 390.5416 | 301.9079
1892.0667 | 400.6514 | 366.4534 | 389.5983 | 301.7942
1893.0667 | 401.9272 | 366.9005 | 391.5024 | 302.0125
1894.0667 | 402.4652 | 366.1302 | 391.564 | 302.3985
1895.0667 | 403.0787 | 364.6989 | 391.5419 | 302.6241
1896.0667 | 403.8345 | 365.3943 | 392.0871 | 302.8453
1897.0667 | 404.3775 | 367.1871 | 392.7688 | 302.9771
1898.0667 | 404.5815 | 369.6056 | 392.8652 | 303.0549
1899.0667 | 404.9483 | 371.3475 | 392.2296 | 303.0248
1900.0667 | 403.9536 | 372.7362 | 391.1942 | 302.9514
1901.0667 | 402.9028 | 372.9214 | 391.0611 | 303.1472
1902.0667 | 402.3278 | 372.5192 | 390.1778 | 303.0727
1903.0667 | 402.3837 | 371.9799 | 390.7803 | 303.1982
1904.0667 | 402.5039 | 373.7297 | 391.5129 | 303.1445
1905.0667 | 402.6968 | 374.5697 | 392.9747 | 303.23
1906.0667 | 401.8299 | 374.7794 | 393.6145 | 303.2972
1907.0667 | 401.5544 | 376.401 | 393.4385 | 303.4457
1908.0667 | 402.1607 | 377.7143 | 393.4493 | 303.5081
1909.0667 | 403.7679 | 379.3077 | 396.2187 | 303.8111
1910.0667 | 403.8231 | 379.5719 | 396.4236 | 304.6106
1911.0667 | 404.1078 | 379.1103 | 395.4116 | 304.2728
1912.0667 | 403.7576 | 378.9045 | 395.6946 | 304.592
1913.0667 | 405.3416 | 378.4342 | 395.8346 | 305.1915
1914.0667 | 405.5224 | 377.7655 | 395.6353 | 305.3461
1915.0667 | 407.2511 | 377.1046 | 396.1803 | 305.5846
1916.0667 | 409.4406 | 376.138 | 396.315 | 306.4989
1917.0667 | 412.3989 | 374.8221 | 396.4311 | 307.7604
1918.0667 | 415.0428 | 373.7526 | 396.4359 | 308.874
1919.0667 | 417.0687 | 372.6774 | 396.7638 | 309.6163
1920.0667 | 417.2369 | 372.6941 | 397.4096 | 310.0621
1921.0667 | 418.0413 | 372.9067 | 396.6587 | 309.9466
1922.0667 | 420.3853 | 372.6417 | 396.8438 | 310.4002
1923.0667 | 422.6533 | 371.8721 | 398.3738 | 310.9548
1924.0667 | 421.3574 | 371.4491 | 398.7671 | 310.9133
1925.0667 | 423.3898 | 370.6005 | 400.0898 | 310.8349
1926.0667 | 424.8997 | 369.2307 | 402.9686 | 311.1859
1927.0667 | 424.8477 | 368.0986 | 403.7166 | 311.6396
1928.0667 | 424.5309 | 366.7515 | 403.4064 | 311.6496
1929.0667 | 424.7994 | 367.3548 | 403.9728 | 312.1872
1930.0667 | 423.8861 | 367.7562 | 406.0068 | 312.4134
1931.0667 | 423.5193 | 367.3744 | 407.0434 | 312.5136
1932.0667 | 423.2997 | 367.3911 | 406.8726 | 312.6787
1933.0667 | 423.4779 | 366.603 | 405.6251 | 312.9491
1934.0667 | 427.6065 | 365.2713 | 405.3388 | 313.5121
1935.0667 | 428.522 | 364.3721 | 408.8442 | 314.3507
1936.0667 | 429.7005 | 364.133 | 407.3735 | 315.6862
1937.0667 | 430.964 | 364.4525 | 406.7931 | 316.0013
1938.0667 | 431.6195 | 363.7405 | 406.3952 | 316.7993
1939.0667 | 434.5702 | 362.5754 | 405.2896 | 317.7393
1940.0667 | 436.0947 | 361.6629 | 405.1959 | 318.619
1941.0667 | 438.5084 | 361.2061 | 405.2155 | 319.3151
1942.0667 | 438.849 | 361.1742 | 406.1365 | 319.3743
1943.0667 | 438.9175 | 361.6438 | 406.945 | 320.0579
1944.0667 | 440.3542 | 362.2965 | 407.572 | 320.3922
1945.0667 | 440.5378 | 364.5014 | 408.4213 | 320.3338
1946.0667 | 439.117 | 365.6612 | 410.2998 | 320.1444
1947.0667 | 437.3337 | 367.1613 | 409.7294 | 320.3012
1948.0667 | 435.839 | 367.9 | 408.5132 | 319.8651
1949.0667 | 434.8363 | 368.3185 | 408.5669 | 319.6467
1950.0667 | 433.8824 | 368.2599 | 408.0226 | 320.4093
1951.0667 | 433.422 | 369.4 | 407.3365 | 320.2615
1952.0667 | 431.6791 | 370.4579 | 406.1905 | 319.7743
1953.0667 | 430.2622 | 370.6805 | 407.5304 | 319.5228
1954.0667 | 431.3063 | 371.0052 | 407.1676 | 319.5432
1955.0667 | 431.1197 | 371.3128 | 407.1091 | 319.3356
1956.0667 | 430.3245 | 371.728 | 405.9466 | 319.1312
1957.0667 | 430.8989 | 370.3993 | 404.3977 | 318.9984
1958.0667 | 430.7497 | 369.292 | 403.4494 | 318.9381
1959.0667 | 433.3466 | 367.5589 | 402.1507 | 319.6088
1960.0667 | 436.4033 | 366.3217 | 401.5907 | 321.5111
1961.0667 | 436.3041 | 364.8031 | 400.9401 | 322.4434
1962.0667 | 438.2021 | 364.1468 | 400.9493 | 322.6643
1963.0667 | 438.7249 | 362.5089 | 401.3362 | 323.14
1964.0667 | 441.1203 | 361.3459 | 401.7699 | 323.6731
1965.0667 | 439.8673 | 362.0841 | 402.212 | 323.6346
1966.0667 | 438.3473 | 363.0277 | 401.8663 | 323.3242
1967.0667 | 437.5891 | 365.0096 | 403.1454 | 322.8001
1968.0667 | 435.5812 | 365.5194 | 402.9141 | 322.2409
1969.0667 | 435.7588 | 365.5155 | 405.5706 | 322.6142
1970.0667 | 435.5141 | 365.5854 | 405.5592 | 322.6238
1971.0667 | 434.8977 | 365.4199 | 405.4264 | 322.2958
1972.0667 | 433.6193 | 366.0733 | 405.0202 | 322.0648
1973.0667 | 434.6883 | 365.4893 | 404.548 | 321.935
1974.0667 | 437.7247 | 365.9376 | 406.0932 | 322.346
1975.0667 | 439.9254 | 366.812 | 407.4971 | 322.3293
1976.0667 | 440.5784 | 366.8283 | 408.9712 | 323.347
1977.0667 | 441.0625 | 367.7744 | 410.3628 | 323.4277
1978.0667 | 441.1324 | 369.3136 | 409.9644 | 323.0057
1979.0667 | 442.2549 | 372.0052 | 413.0093 | 322.6726
1980.0667 | 441.9266 | 372.28 | 414.2348 | 322.3548
1981.0667 | 442.1396 | 373.511 | 417.4827 | 322.233
1982.0667 | 441.9701 | 374.7177 | 417.609 | 322.1324
1983.0667 | 443.0666 | 374.7197 | 417.1472 | 321.6507
1984.0667 | 454.2586 | 374.4659 | 418.4723 | 321.4718
1985.0667 | 457.7063 | 375.1895 | 422.7187 | 321.4917
1986.0667 | 461.6075 | 376.0444 | 426.6114 | 322.1581
1987.0667 | 463.7922 | 375.8231 | 432.0216 | 323.3995
1988.0667 | 468.3654 | 376.7376 | 437.7135 | 323.8514
1989.0667 | 469.0996 | 376.9486 | 445.6182 | 324.6577
1990.0667 | 471.0372 | 377.1416 | 463.5583 | 325.0734
1991.0667 | 472.2948 | 377.8412 | 472.6534 | 325.3045
1992.0667 | 471.2894 | 379.2967 | 477.4433 | 325.2776
1993.0667 | 471.2323 | 380.5549 | 487.4102 | 325.1489
1994.0667 | 470.1746 | 385.0061 | 491.5992 | 325.1166
1995.0667 | 471.2107 | 386.6203 | 489.5489 | 325.3118
1996.0667 | 469.3591 | 388.0314 | 487.8041 | 325.7002
1997.0667 | 476.8123 | 390.053 | 486.8977 | 326.0744
1998.0667 | 485.6367 | 390.8909 | 485.9395 | 326.848
1999.0667 | 484.0164 | 390.976 | 481.7762 | 327.4099
2000.0667 | 485.471 | 390.2305 | 476.3776 | 327.3018
2001.0667 | 492.3979 | 389.3868 | 479.5032 | 327.6981
2002.0667 | 489.9671 | 391.4929 | 485.0374 | 328.0455
2003.0667 | 486.461 | 395.6599 | 484.9455 | 327.8196
2004.0667 | 481.2578 | 398.5757 | 479.506 | 327.2879
2005.0667 | 475.6561 | 400.0914 | 474.9347 | 326.7872
2006.0667 | 470.1991 | 400.8641 | 476.7705 | 326.3614
2007.0667 | 465.5255 | 401.9252 | 472.5933 | 325.8723
2008.0667 | 461.1698 | 402.0813 | 468.463 | 325.5308
2009.0667 | 458.8115 | 403.3011 | 464.6833 | 325.2307
2010.0667 | 456.6182 | 404.0438 | 462.6632 | 324.978
2011.0667 | 454.0073 | 404.7257 | 466.5345 | 325.2046
2012.0667 | 451.2573 | 404.5446 | 467.6675 | 325.4775
2013.0667 | 450.8601 | 402.0459 | 462.0335 | 325.4404
2014.0667 | 450.2434 | 401.046 | 464.7133 | 325.9295
2015.0667 | 449.4084 | 400.5738 | 464.2169 | 326.1362
2016.0667 | 447.8343 | 400.1813 | 462.3702 | 326.1368
2017.0667 | 447.5574 | 398.8778 | 458.8217 | 326.2322
2018.0667 | 447.5387 | 397.7918 | 456.0819 | 326.5109
2019.0667 | 448.0929 | 396.1639 | 454.3958 | 327.0908
2020.0667 | 447.1157 | 396.1931 | 453.4831 | 327.0785
2021.0667 | 446.5945 | 398.4143 | 458.5621 | 327.022
2022.0667 | 450.948 | 400.324 | 459.0358 | 326.7614
2023.0667 | 450.0545 | 402.352 | 458.753 | 326.5544
2024.0667 | 453.2067 | 404.7814 | 457.7666 | 326.37
2025.0667 | 455.198 | 406.2184 | 460.605 | 326.3385
2026.0667 | 457.1676 | 406.6778 | 464.2271 | 326.7175
2027.0667 | 458.1984 | 406.9805 | 472.6991 | 327.0987
2028.0667 | 459.0364 | 407.5016 | 479.208 | 327.6359
2029.0667 | 458.098 | 408.677 | 483.7416 | 328.0133
2030.0667 | 457.763 | 409.1999 | 483.8658 | 328.0774
2031.0667 | 457.588 | 409.016 | 485.3331 | 328.1849
2032.0667 | 458.6946 | 411.8053 | 487.338 | 328.1266
2033.0667 | 458.9856 | 412.708 | 486.8925 | 328.0555
2034.0667 | 459.1312 | 414.3988 | 489.1501 | 328.1845
2035.0667 | 457.0392 | 414.6412 | 487.1929 | 328.3962
2036.0667 | 455.0143 | 415.4443 | 486.2311 | 328.6959
2037.0667 | 457.0149 | 415.8244 | 489.9181 | 328.7205
2038.0667 | 457.3158 | 418.038 | 491.6026 | 328.6416
2039.0667 | 458.2461 | 419.6795 | 491.7272 | 328.7607
2040.0667 | 457.4725 | 420.8132 | 496.6004 | 328.7666
2041.0667 | 455.9031 | 423.8026 | 497.1985 | 328.7216
2042.0667 | 455.315 | 428.3377 | 496.6983 | 328.7755
2043.0667 | 456.6354 | 431.0326 | 496.3463 | 329.0453
2044.0667 | 459.9069 | 431.1274 | 500.9607 | 329.4697
2045.0667 | 461.8355 | 432.5424 | 508.4552 | 330.1587
2046.0667 | 462.4208 | 434.6784 | 510.0522 | 330.5588
2047.0667 | 461.9789 | 435.8284 | 512.0356 | 330.8914
2048.0667 | 462.2773 | 435.028 | 514.8056 | 331.3383
2049.0667 | 463.1035 | 437.2421 | 520.5963 | 331.7684
2050.0667 | 462.7531 | 437.3964 | 523.8854 | 331.9401
2051.0667 | 462.4671 | 438.4225 | 528.5922 | 332.5345
2052.0667 | 461.8922 | 437.7524 | 529.3545 | 332.8835
2053.0667 | 462.7559 | 438.297 | 528.4178 | 332.9974
2054.0667 | 463.1109 | 438.375 | 533.4789 | 333.2865
2055.0667 | 465.2416 | 440.0214 | 537.538 | 333.6685
2056.0667 | 467.2417 | 440.0776 | 540.8319 | 334.1192
2057.0667 | 470.9866 | 439.401 | 544.6008 | 334.401
2058.0667 | 473.2975 | 439.9142 | 546.7266 | 334.8272
2059.0667 | 474.6936 | 442.0811 | 549.666 | 335.1411
2060.0667 | 475.0727 | 443.9106 | 553.7225 | 335.4004
2061.0667 | 473.2475 | 443.5007 | 555.4383 | 335.8119
2062.0667 | 473.6471 | 444.5274 | 562.3552 | 336.1352
2063.0667 | 476.7639 | 444.06 | 563.14 | 336.8158
2064.0667 | 479.1292 | 442.6479 | 562.807 | 337.2792
2065.0667 | 479.4839 | 442.0455 | 567.4951 | 337.5395
2066.0667 | 478.9546 | 443.3769 | 571.2656 | 337.8824
2067.0667 | 477.927 | 443.2351 | 573.0644 | 338.156
2068.0667 | 478.3908 | 442.1723 | 573.5257 | 338.2264
2069.0667 | 476.7664 | 443.1856 | 575.8164 | 338.23
2070.0667 | 476.2582 | 442.7692 | 572.2128 | 338.2415
2071.0667 | 475.1764 | 441.876 | 569.8211 | 338.1175
2072.0667 | 476.3839 | 441.1827 | 565.2061 | 337.8908
2073.0667 | 483.7732 | 443.7692 | 565.2056 | 338.0725
2074.0667 | 482.5087 | 442.7275 | 563.047 | 338.471
2075.0667 | 481.7067 | 442.2188 | 560.0126 | 339.0855
2076.0667 | 481.6501 | 441.5536 | 562.474 | 339.96
2077.0667 | 481.0423 | 439.785 | 560.9361 | 340.4262
2078.0667 | 488.3376 | 438.7675 | 557.4179 | 340.74
2079.0667 | 489.8946 | 441.0798 | 556.7924 | 341.1042
2080.0667 | 493.6735 | 441.7127 | 554.6415 | 341.556
2081.0667 | 492.2742 | 442.2877 | 553.4567 | 342.114
2082.0667 | 491.4997 | 443.9256 | 552.7196 | 342.764
2083.0667 | 491.5367 | 446.3924 | 551.3018 | 343.5423
2084.0667 | 492.832 | 448.1335 | 551.9005 | 344.5094
2085.0667 | 494.2684 | 448.5822 | 549.5448 | 345.369
2086.0667 | 492.6901 | 448.734 | 546.1915 | 345.5414
2087.0667 | 492.2347 | 448.9294 | 543.529 | 345.9489
2088.0667 | 490.3873 | 450.904 | 543.8513 | 346.1903
2089.0667 | 489.0322 | 453.1999 | 543.1706 | 346.6542
2090.0823 | 489.4589 | 455.2443 | 542.7584 | 347.0636
2091.0667 | 488.8574 | 457.7961 | 542.6772 | 347.6732
2092.0667 | 489.4337 | 457.8046 | 539.9519 | 347.826
2093.0667 | 488.7945 | 458.5627 | 538.904 | 348.0936
2094.0667 | 488.1757 | 457.674 | 535.7454 | 348.3899
2095.0667 | 487.3734 | 457.9235 | 532.0677 | 348.4958
2096.0667 | 485.1731 | 456.5727 | 528.2746 | 348.2559
2097.0667 | 485.2544 | 459.4043 | 527.6433 | 348.0857
2098.0667 | 483.5138 | 459.191 | 524.596 | 348.1507
2099.0667 | 485.4087 | 461.7866 | 525.2792 | 348.7613
2100.0667 | 484.6901 | 462.9941 | 524.7792 | 348.8781
2101.0667 | 481.8723 | 464.1853 | 525.0995 | 348.7791
2102.0667 | 478.4589 | 465.9703 | 524.28 | 348.8368
2103.0667 | 477.2095 | 468.1573 | 523.4419 | 348.6642
2104.0667 | 474.6992 | 470.1642 | 522.5251 | 348.3505
2105.0667 | 473.1859 | 470.0739 | 521.9787 | 348.6723
2106.0667 | 473.7259 | 470.9164 | 520.3794 | 348.8646
2107.0667 | 472.3915 | 470.3077 | 516.8897 | 349.0983
2108.0667 | 470.6776 | 469.5163 | 514.2034 | 348.9239
2109.0667 | 471.799 | 471.1059 | 518.0321 | 349.1177
2110.0667 | 470.3768 | 471.9524 | 518.8493 | 349.1358
2111.0667 | 469.1319 | 471.8879 | 518.78 | 348.8214
2112.0667 | 468.7228 | 472.4172 | 517.7525 | 348.4064
2113.0667 | 468.9001 | 474.2955 | 517.9535 | 347.8871
2114.0667 | 468.6012 | 477.0013 | 516.116 | 347.3254
2115.0667 | 469.0472 | 479.3779 | 516.9764 | 347.2703
2116.0667 | 468.8342 | 481.4007 | 517.42 | 347.3632
2117.0667 | 469.7407 | 481.3026 | 520.632 | 347.998
2118.0667 | 470.8962 | 481.409 | 525.1125 | 348.1353
2119.0667 | 472.702 | 485.0833 | 527.0897 | 348.1965
2120.0667 | 472.3634 | 486.7737 | 526.146 | 348.23
2121.0667 | 474.4565 | 490.5632 | 531.9681 | 348.8781
2122.0667 | 471.7631 | 492.9532 | 533.034 | 349.1735
2123.0667 | 470.5383 | 498.1416 | 530.8002 | 349.0954
2124.0667 | 469.7631 | 502.7782 | 530.0702 | 348.828
2125.0667 | 471.0751 | 504.9138 | 531.7936 | 348.636
2126.0667 | 474.3163 | 506.8403 | 533.9742 | 348.587
2127.0667 | 474.9465 | 509.3719 | 535.6796 | 348.5677
2128.0667 | 474.4371 | 510.555 | 533.3006 | 348.604
2129.0667 | 474.097 | 512.3314 | 534.4362 | 348.5979
2130.0667 | 475.0274 | 512.6955 | 535.6299 | 348.6968
2131.0667 | 476.2447 | 515.8444 | 537.3009 | 349.2885
2132.0667 | 477.7919 | 518.0483 | 538.51 | 349.4651
2133.0667 | 479.9599 | 519.3997 | 537.3724 | 350.0612
2134.0667 | 490.9241 | 521.034 | 539.4476 | 350.0491
2135.0667 | 495.7887 | 522.4635 | 541.4499 | 350.372
2136.0667 | 498.6878 | 523.2159 | 544.468 | 351.336
2137.0667 | 499.7708 | 524.8211 | 545.8281 | 352.0492
2138.0667 | 499.4307 | 524.0537 | 546.3931 | 352.5726
2139.0667 | 498.4483 | 524.5759 | 547.6264 | 353.2217
2140.0667 | 497.6885 | 525.5177 | 548.8282 | 354.0437
2141.0667 | 498.1265 | 526.5267 | 550.386 | 354.7781
2142.0667 | 498.8124 | 526.3008 | 544.6864 | 355.1353
2143.0667 | 496.3188 | 529.1529 | 546.0863 | 355.4444
2144.0667 | 494.7463 | 531.2584 | 548.6852 | 355.886
2145.0667 | 493.4171 | 533.8709 | 548.3973 | 356.3055
2146.0667 | 492.0035 | 538.0096 | 551.551 | 356.8656
2147.0667 | 492.3108 | 538.1874 | 551.4834 | 357.4268
2148.0667 | 493.9108 | 538.6295 | 549.6644 | 358.0432
2149.0667 | 493.5329 | 539.351 | 550.6992 | 358.2105
2150.0667 | 493.5603 | 539.5541 | 555.7577 | 358.6175
2151.0667 | 494.6176 | 542.1635 | 556.4076 | 359.0565
2152.0667 | 497.9188 | 543.3147 | 556.7272 | 359.6799
2153.0667 | 497.3922 | 545.0542 | 558.0931 | 360.1614
2154.0667 | 497.3394 | 548.4615 | 559.0102 | 360.8211
2155.0667 | 496.5703 | 551.0978 | 557.9912 | 361.558
2156.0667 | 495.3374 | 551.2941 | 556.3677 | 361.9684
2157.0667 | 495.4454 | 550.5652 | 560.5765 | 362.1401
2158.0667 | 495.3463 | 550.4019 | 562.6613 | 362.961
2159.0667 | 498.3779 | 549.3702 | 560.4312 | 363.3135
2160.0667 | 500.1205 | 549.0729 | 563.0178 | 363.6867
2161.0667 | 505.044 | 547.9197 | 560.3399 | 363.8964
2162.0667 | 521.4333 | 545.2767 | 559.5074 | 363.655
2163.0667 | 521.3565 | 543.4577 | 557.8756 | 363.9004
2164.0667 | 517.4722 | 541.5888 | 559.1814 | 364.5864
2165.0667 | 518.9753 | 536.77 | 559.9295 | 365.7263
2166.0667 | 516.5258 | 532.7632 | 560.4128 | 366.7052
2167.0667 | 512.7272 | 531.6026 | 557.0117 | 367.0748
2168.0667 | 509.5505 | 531.0159 | 557.4539 | 367.0258
2169.0667 | 512.3203 | 529.2355 | 559.7359 | 367.0358
2170.0667 | 510.6478 | 528.2511 | 559.6953 | 367.5795
2171.0667 | 508.0469 | 526.4646 | 556.9049 | 367.6394
2172.0667 | 504.2624 | 523.7386 | 550.8835 | 367.6362
2173.0667 | 503.3231 | 524.5035 | 552.4438 | 367.8184
2174.0667 | 502.1125 | 525.5923 | 556.4611 | 368.1717
2175.0667 | 503.3983 | 524.4325 | 553.8686 | 368.774
2176.0667 | 506.7662 | 522.1417 | 551.727 | 369.1733
2177.0667 | 507.2812 | 518.9602 | 552.2481 | 370.3433
2178.0667 | 507.7236 | 515.4527 | 550.3561 | 370.9319
2179.0667 | 508.9965 | 513.0721 | 552.4557 | 371.6323
2180.0667 | 508.0244 | 514.3946 | 551.7816 | 372.2359
2181.0667 | 505.9584 | 514.2327 | 551.2368 | 372.8549
2182.0667 | 502.0203 | 516.7152 | 548.2136 | 372.922
2183.0667 | 502.013 | 517.5671 | 548.2981 | 372.7145
2184.0667 | 502.6945 | 518.3181 | 548.7437 | 372.6063
2185.0667 | 501.0821 | 517.4655 | 553.7095 | 372.6691
2186.0667 | 505.2113 | 516.4972 | 556.6869 | 373.0844
2187.0667 | 503.8814 | 514.5243 | 556.547 | 373.5785
2188.0667 | 503.7867 | 512.791 | 555.561 | 374.3035
2189.0667 | 502.8083 | 511.0678 | 555.5226 | 375.3431
2190.0667 | 501.6018 | 514.0971 | 556.1406 | 375.9813
2191.0667 | 501.0471 | 520.0046 | 561.3431 | 377.239
2192.0667 | 496.042 | 519.1944 | 560.8102 | 378.1444
2193.0667 | 493.0314 | 519.9854 | 559.7337 | 378.1344
2194.0667 | 494.3376 | 524.2701 | 560.6466 | 379.1903
2195.0667 | 495.0426 | 524.301 | 561.2107 | 380.4063
2196.0667 | 496.1698 | 524.1745 | 561.289 | 380.8677
2197.0667 | 497.3275 | 521.6106 | 560.4379 | 381.3532
2198.0667 | 495.0616 | 518.9206 | 558.5426 | 381.5266
2199.0667 | 494.1856 | 517.7581 | 557.0919 | 382.1113
2200.0667 | 493.5136 | 518.1363 | 563.7284 | 382.1456
2201.0667 | 493.1311 | 518.3866 | 563.4008 | 382.2253
2202.0667 | 489.8046 | 519.2473 | 560.4322 | 381.9361
2203.0667 | 487.3132 | 521.5118 | 555.8334 | 381.9566
2204.0667 | 491.336 | 526.73 | 556.9999 | 382.8399
2205.0667 | 495.3699 | 526.1298 | 558.0751 | 383.6612
2206.0667 | 501.6064 | 523.9096 | 563.2484 | 384.066
2207.0667 | 504.7789 | 522.5774 | 564.2849 | 383.8807
2208.0667 | 501.3969 | 523.1595 | 561.4308 | 383.3083
2209.0667 | 498.2058 | 524.328 | 558.7707 | 382.5525
2210.0667 | 495.6271 | 526.3055 | 559.2239 | 382.1631
2211.0667 | 495.4525 | 528.9096 | 558.1942 | 382.4726
2212.0667 | 493.8735 | 531.9467 | 560.3948 | 382.381
2213.0667 | 491.662 | 532.4315 | 559.6527 | 382.6306
2214.0667 | 488.1103 | 532.396 | 554.42 | 382.101
2215.0667 | 483.9517 | 536.4917 | 550.7515 | 381.9657
2216.0667 | 486.6679 | 541.5416 | 548.5835 | 382.0253
2217.0667 | 488.0614 | 542.0599 | 547.1645 | 382.6553
2218.0667 | 486.8211 | 542.2991 | 545.9872 | 382.568
2219.0667 | 485.4712 | 544.8214 | 545.9516 | 381.8661
2220.0823 | 481.6398 | 547.7796 | 547.7074 | 381.5264
2221.0667 | 480.5102 | 550.008 | 544.2608 | 381.0701
2222.0667 | 478.6286 | 553.6105 | 545.6651 | 380.3232
2223.0667 | 477.2746 | 555.686 | 545.6133 | 380.0898
2224.0667 | 477.7601 | 558.6709 | 548.2174 | 380.313
2225.0667 | 476.2332 | 560.6796 | 549.2451 | 380.1587
2226.0667 | 475.8619 | 561.0737 | 548.5845 | 379.8601
2227.0667 | 476.1255 | 565.0286 | 550.5024 | 380.1347
2228.0667 | 478.2061 | 566.5456 | 554.1311 | 380.3719
2229.0667 | 477.9207 | 569.0183 | 557.4261 | 380.8964
2230.0667 | 478.0571 | 570.7055 | 556.9088 | 380.9026
2231.0667 | 476.9217 | 571.4475 | 556.5143 | 380.8282
2232.0667 | 475.0595 | 572.0322 | 557.7161 | 380.959
2233.0667 | 473.65 | 574.429 | 555.0661 | 380.85
2234.0667 | 473.1576 | 575.6415 | 552.6269 | 380.645
2235.0667 | 475.588 | 576.9595 | 554.378 | 380.4826
2236.0667 | 476.4184 | 577.4626 | 555.6225 | 380.7478
2237.0667 | 477.9836 | 577.9139 | 555.5749 | 380.7918
2238.0667 | 482.8915 | 578.1731 | 556.6008 | 381.0151
2239.0667 | 498.3045 | 576.4506 | 557.9314 | 381.0067
2240.0667 | 497.7501 | 574.2941 | 557.8111 | 381.0897
2241.0667 | 499.0108 | 571.363 | 555.5592 | 382.2158
2242.0667 | 496.6996 | 569.805 | 555.7866 | 382.6762
2243.0667 | 495.7455 | 567.0588 | 554.4051 | 382.6299
2244.0667 | 493.9041 | 564.6897 | 552.5795 | 382.1665
2245.0667 | 490.9277 | 563.6287 | 552.0974 | 381.8226
2246.0667 | 487.1631 | 562.8296 | 549.6811 | 381.6783
2247.0667 | 485.0696 | 565.3179 | 550.7606 | 381.8686
2248.0823 | 483.6148 | 566.8689 | 551.9305 | 381.7006
2249.0667 | 481.589 | 567.8955 | 551.6556 | 381.6726
2250.0667 | 479.9229 | 567.594 | 551.298 | 381.6306
2251.0667 | 480.5718 | 568.3339 | 551.8824 | 381.8294
2252.0667 | 480.9929 | 570.1612 | 555.545 | 382.2937
2253.0667 | 481.1778 | 570.5046 | 557.9552 | 382.4795
2254.0667 | 480.5074 | 569.5241 | 560.0719 | 383.0014
2255.0667 | 480.7106 | 569.449 | 561.316 | 383.2222
2256.0667 | 484.8226 | 568.3839 | 560.9699 | 383.3505
2257.0667 | 486.1345 | 568.0071 | 561.3488 | 383.7039
2258.0667 | 485.3003 | 566.4747 | 558.9874 | 383.6873
2259.0667 | 483.8808 | 566.2344 | 555.8387 | 383.6485
2260.0667 | 484.4446 | 571.6788 | 556.5368 | 383.9539
2261.0667 | 486.6427 | 572.2272 | 557.5895 | 384.4869
2262.0667 | 491.051 | 571.1805 | 560.8225 | 384.527
2263.0667 | 492.0616 | 570.483 | 563.0057 | 384.4427
2264.0667 | 491.7607 | 568.89 | 563.0565 | 384.4409
2265.0667 | 490.4061 | 568.0788 | 560.905 | 384.2682
2266.0667 | 490.0658 | 568.1527 | 564.0799 | 384.2857
2267.0667 | 492.3941 | 569.1038 | 562.9618 | 384.3315
2268.0667 | 491.6992 | 567.3432 | 563.049 | 384.0916
2269.0667 | 492.8811 | 567.2005 | 562.5649 | 384.0937
2270.0667 | 491.3057 | 568.0402 | 561.9296 | 384.5494
2271.0667 | 491.1631 | 566.9062 | 561.2929 | 385.0471
2272.0667 | 491.9591 | 564.7434 | 559.2019 | 384.9633
2273.0667 | 491.5746 | 564.6569 | 556.2976 | 384.2829
2274.0667 | 508.404 | 563.4974 | 558.3223 | 384.2279
2275.0667 | 504.6299 | 562.5561 | 558.8633 | 384.1805
2276.0667 | 502.1708 | 562.2545 | 558.0168 | 384.0774
2277.0667 | 501.1421 | 563.2955 | 558.0046 | 384.2689
2278.0667 | 497.7734 | 563.6573 | 558.9869 | 384.5256
2279.0667 | 496.0664 | 562.874 | 558.4559 | 384.8408
2280.0667 | 497.6924 | 561.8135 | 560.9175 | 385.0703
2281.0667 | 495.9455 | 557.377 | 562.3161 | 385.4674
2282.0667 | 496.6432 | 556.8797 | 562.3769 | 386.2411
2283.0667 | 500.3176 | 557.5524 | 563.4635 | 386.749
2284.0667 | 495.0545 | 556.7854 | 560.0046 | 386.8226
2285.0667 | 492.2036 | 554.8984 | 558.2264 | 386.5187
2286.0667 | 491.9689 | 556.0657 | 561.5381 | 386.5084
2287.0667 | 492.7791 | 555.3388 | 561.0532 | 386.5704
2288.0667 | 493.045 | 551.7261 | 559.5886 | 386.7317
2289.0667 | 491.8873 | 549.1355 | 559.571 | 386.5237
2290.0667 | 498.4265 | 549.1312 | 561.2055 | 386.2972
2291.0667 | 502.4581 | 547.2326 | 562.3364 | 385.9839
2292.0667 | 503.2075 | 545.6757 | 565.5725 | 385.8771
2293.0667 | 501.8468 | 543.055 | 564.7323 | 385.8684
2294.0667 | 500.6739 | 540.1302 | 565.3387 | 385.9437
2295.0667 | 497.9435 | 539.3526 | 565.0445 | 385.7699
2296.0667 | 495.4474 | 541.1168 | 565.9958 | 385.6854
2297.0667 | 494.1003 | 544.1596 | 567.5556 | 385.7398
2298.0667 | 492.5265 | 546.2865 | 566.7483 | 385.7942
2299.0667 | 490.9976 | 546.7272 | 567.0326 | 385.8627
2300.0667 | 492.2533 | 547.6062 | 567.6727 | 385.7241
2301.0667 | 491.5631 | 547.0806 | 567.313 | 385.5963
2302.0667 | 491.1506 | 546.9658 | 568.1162 | 385.6349
2303.0667 | 492.6888 | 546.6859 | 569.3924 | 385.841
2304.0667 | 490.839 | 547.2966 | 565.5576 | 385.7886
2305.0667 | 486.8466 | 547.5967 | 564.76 | 385.5744
2306.0667 | 483.2788 | 548.1955 | 560.6949 | 385.1614
2307.0667 | 481.3703 | 548.5568 | 562.1859 | 384.5928
2308.0667 | 480.0881 | 549.8732 | 561.9502 | 384.3223
2309.0667 | 479.9327 | 549.6871 | 560.3478 | 384.3863
2310.0667 | 481.7843 | 551.0176 | 559.9324 | 384.4786
2311.0667 | 487.4012 | 550.1028 | 557.8847 | 384.6726
2312.0667 | 484.9922 | 546.0193 | 556.5365 | 384.9417
2313.0667 | 481.9547 | 545.2386 | 554.3082 | 385.0966
2314.0667 | 478.0915 | 544.9136 | 550.2162 | 385.0783
2315.0667 | 477.0757 | 545.2484 | 550.3316 | 385.053
2316.0667 | 477.0681 | 546.6224 | 550.373 | 385.1679
2317.0667 | 477.7573 | 544.5743 | 547.1547 | 385.0534
2318.0667 | 477.5112 | 543.785 | 545.8018 | 384.9581
2319.0667 | 478.4133 | 540.6664 | 543.4474 | 384.8853
2320.0667 | 484.7398 | 538.3573 | 542.1264 | 385.0288
2321.0667 | 484.4117 | 534.9965 | 540.3904 | 385.4313
2322.0667 | 482.9737 | 531.8558 | 537.9492 | 385.6465
2323.0667 | 484.6296 | 532.3792 | 538.0527 | 385.7546
2324.0667 | 482.412 | 529.4023 | 535.5267 | 385.7531
2325.0667 | 480.1729 | 527.5876 | 533.0624 | 385.5204
2326.0667 | 481.7413 | 528.3439 | 531.6405 | 385.204
2327.0667 | 482.6319 | 528.3783 | 531.8376 | 385.0297
2328.0667 | 482.6017 | 530.4481 | 531.0715 | 384.6776
2329.0667 | 480.3917 | 529.7172 | 527.7164 | 384.1948
2330.0667 | 481.4497 | 527.1403 | 523.1506 | 383.7636
2331.0667 | 483.3047 | 529.3856 | 524.2822 | 383.814
2332.0667 | 484.6661 | 529.0545 | 525.1471 | 383.9209
2333.0667 | 483.8373 | 526.353 | 524.2095 | 384.121
2334.0667 | 481.8402 | 524.7611 | 521.0454 | 384.0953
2335.0667 | 479.8663 | 525.2119 | 529.1555 | 384.1087
2336.0667 | 478.9753 | 524.8797 | 530.9837 | 384.1135
2337.0667 | 477.2553 | 525.96 | 530.1339 | 384.1297
2338.0667 | 475.3484 | 524.1855 | 530.9009 | 384.1046
2339.0667 | 476.0209 | 523.6608 | 529.9657 | 383.9222
2340.0667 | 477.1698 | 524.0841 | 528.5376 | 383.9458
2341.0667 | 478.2819 | 523.7571 | 527.7962 | 383.8979
2342.0667 | 479.1658 | 522.8024 | 528.1939 | 383.9397
2343.0667 | 479.6488 | 520.1105 | 530.9229 | 384.0333
2344.0667 | 478.8922 | 519.1165 | 531.4968 | 384.2215
2345.0667 | 480.5975 | 515.9821 | 533.8387 | 384.6424
2346.0667 | 481.6257 | 513.9451 | 536.27 | 384.9245
2347.0667 | 481.8682 | 513.7228 | 538.5839 | 385.115
2348.0667 | 482.4059 | 514.3988 | 539.3931 | 385.3288
2349.0667 | 483.5484 | 515.3188 | 538.7346 | 385.597
2350.0667 | 485.3937 | 514.1131 | 541.1599 | 385.6873
2351.0667 | 485.4352 | 513.1866 | 540.1079 | 385.7414
2352.0667 | 484.2758 | 513.1417 | 544.3917 | 385.7624
2353.0667 | 484.9188 | 513.9287 | 543.4435 | 385.8248
2354.0667 | 482.2978 | 515.9677 | 540.2171 | 385.782
2355.0667 | 483.7907 | 516.8428 | 541.537 | 385.85
2356.0667 | 484.147 | 516.7505 | 543.0012 | 386.2081
2357.0667 | 485.6229 | 516.6101 | 545.0893 | 386.6745
2358.0667 | 485.5542 | 516.4612 | 548.2582 | 387.0931
2359.0667 | 483.696 | 517.0667 | 549.5465 | 387.4078
2360.0667 | 488.0778 | 516.4217 | 548.5542 | 387.626
2361.0667 | 488.5199 | 515.6615 | 548.7041 | 387.7299
2362.0667 | 487.8279 | 514.9579 | 549.8216 | 387.8557
2363.0667 | 487.3347 | 517.0834 | 549.6665 | 388.0082
2364.0667 | 489.7171 | 518.7508 | 552.2146 | 388.3193
2365.0667 | 491.3501 | 519.9963 | 553.4278 | 388.5664
2366.0667 | 500.2396 | 519.8425 | 558.1008 | 388.8891
2367.0667 | 499.9891 | 517.8388 | 555.2677 | 388.958
2368.0667 | 502.5864 | 516.1079 | 552.2786 | 389.0656
2369.0667 | 502.9845 | 516.2266 | 554.1538 | 389.2432
2370.0667 | 500.6471 | 515.9974 | 555.7269 | 389.5527
2371.0667 | 496.8963 | 516.917 | 559.0621 | 389.739
2372.0667 | 493.8403 | 518.5567 | 556.7274 | 389.802
2373.0667 | 491.7912 | 520.1462 | 558.1231 | 389.7621
2374.0667 | 488.6238 | 521.3317 | 557.1876 | 389.6028
2375.0667 | 487.22 | 522.2485 | 556.8728 | 389.4717
2376.0667 | 486.6353 | 522.7054 | 556.9932 | 389.6693
2377.0667 | 487.3079 | 525.6686 | 556.977 | 389.9192
2378.0667 | 486.5024 | 527.036 | 566.3587 | 390.1062
2379.0667 | 487.9736 | 527.3624 | 567.7074 | 390.3443
2380.0667 | 487.8658 | 526.4535 | 566.7345 | 390.5863
2381.0667 | 485.9524 | 526.8046 | 564.0277 | 390.7982
2382.0667 | 486.048 | 525.3134 | 567.3581 | 391.1617
2383.0667 | 486.4568 | 524.2809 | 571.1117 | 391.8776
2384.0667 | 487.5899 | 524.7068 | 572.2228 | 392.6067
2385.0667 | 487.2829 | 524.2361 | 570.9622 | 393.5029
2386.0667 | 489.6806 | 525.663 | 570.571 | 394.3529
2387.0667 | 489.5214 | 526.2658 | 571.78 | 395.3086
2388.0667 | 491.9529 | 525.2908 | 570.9107 | 395.9588
2389.0667 | 489.6978 | 524.5489 | 570.5991 | 396.2162
2390.0667 | 491.3308 | 525.9951 | 571.7105 | 396.3845
2391.0667 | 490.0311 | 524.4351 | 568.278 | 396.6298
2392.0667 | 489.6444 | 524.1554 | 566.2046 | 396.7976
2393.0667 | 491.2781 | 523.1608 | 563.8963 | 396.8502
2394.0667 | 490.8588 | 523.3892 | 564.8113 | 397.0015
2395.0667 | 492.5116 | 523.345 | 561.0122 | 397.1
2396.0667 | 492.687 | 518.9637 | 556.0555 | 396.9491
2397.0667 | 495.7592 | 517.876 | 555.1312 | 397.0553
2398.0667 | 493.9453 | 515.3201 | 552.5625 | 396.9869
2399.0667 | 495.525 | 513.0697 | 553.5318 | 397.0487
2400.0667 | 498.6792 | 512.5801 | 553.3577 | 397.4128
2401.0667 | 499.5546 | 511.7646 | 552.6741 | 397.3976
2402.0667 | 497.9634 | 511.1632 | 551.2302 | 397.1062
2403.0667 | 507.9715 | 510.8083 | 553.1925 | 396.7543
2404.0667 | 509.7606 | 511.5527 | 552.0736 | 396.3788
2405.0667 | 508.816 | 511.0202 | 553.646 | 396.0166
2406.0667 | 516.1803 | 507.8266 | 547.7381 | 395.7071
2407.0667 | 514.9338 | 505.2812 | 546.3104 | 395.6295
2408.0667 | 512.0281 | 503.4813 | 547.0854 | 395.4192
2409.0667 | 513.142 | 501.0852 | 544.8984 | 395.2701
2410.0667 | 514.2609 | 498.7882 | 545.6027 | 395.0686
2411.0667 | 512.0709 | 497.5453 | 543.1183 | 394.8243
2412.0667 | 509.4908 | 498.2904 | 544.3004 | 394.594
2413.0667 | 503.9764 | 496.6291 | 541.174 | 394.2958
2414.0667 | 513.236 | 495.7769 | 538.9109 | 394.0059
2415.0667 | 508.9138 | 498.3185 | 541.9424 | 393.7988
2416.0667 | 506.6384 | 497.4958 | 536.012 | 393.5544
2417.0667 | 504.6778 | 497.6785 | 534.0002 | 393.3479
2418.0667 | 505.7419 | 496.8737 | 534.8226 | 393.3369
2419.0667 | 507.04 | 494.0526 | 533.0435 | 393.2865
2420.0667 | 505.0314 | 492.7376 | 531.3397 | 393.0772
2421.0667 | 504.0467 | 491.0726 | 529.3612 | 392.909
2422.0667 | 503.3675 | 488.7776 | 527.9711 | 392.6532
2423.0667 | 503.8458 | 487.4615 | 526.1602 | 392.328
2424.0667 | 506.4646 | 485.6844 | 529.3466 | 391.9269
2425.0667 | 505.1892 | 485.8685 | 535.0998 | 391.5161
2426.0667 | 516.2407 | 486.776 | 534.5547 | 390.8797
2427.0667 | 515.692 | 488.0816 | 531.7692 | 390.5912
2428.0667 | 515.3741 | 487.8895 | 533.0605 | 390.964
2429.0667 | 515.8636 | 486.4273 | 530.4047 | 391.1895
2430.0667 | 510.6658 | 485.168 | 531.6154 | 391.2569
2431.0667 | 507.2739 | 485.2322 | 532.1085 | 391.1601
2432.0667 | 514.3032 | 487.2298 | 531.742 | 391.0373
2433.0667 | 524.926 | 491.6754 | 530.6709 | 390.8973
2434.0667 | 517.1011 | 493.3804 | 530.9734 | 390.627
2435.0823 | 511.7729 | 495.8548 | 531.2775 | 390.3913
2436.0667 | 509.9015 | 496.9389 | 532.7694 | 390.0821
2437.0667 | 504.9443 | 497.319 | 532.2021 | 389.7967
2438.0667 | 500.2814 | 498.4701 | 530.6881 | 389.5712
2439.0667 | 497.551 | 499.5749 | 534.0287 | 389.6954
2440.0667 | 503.3745 | 500.0443 | 538.7076 | 390.0937
2441.0667 | 502.0109 | 500.5586 | 538.5085 | 390.5687
2442.0667 | 500.801 | 499.0337 | 540.7506 | 390.9369
2443.0667 | 497.9383 | 497.6601 | 540.9731 | 391.1887
2444.0667 | 497.1321 | 496.5719 | 540.3241 | 391.3903
2445.0667 | 494.2284 | 495.2163 | 535.5758 | 391.4258
2446.0823 | 495.662 | 494.5474 | 533.7688 | 391.4124
2447.0667 | 491.5149 | 495.5754 | 531.1119 | 391.5595
2448.0667 | 490.9633 | 494.9344 | 528.3629 | 391.5532
2449.0667 | 490.3413 | 495.2645 | 530.4725 | 391.608
2450.0667 | 488.1283 | 497.0267 | 526.7325 | 391.4117
2451.0667 | 486.1552 | 498.9864 | 527.3631 | 391.1486
2452.0667 | 484.4054 | 501.2438 | 533.3364 | 390.9488
2453.0667 | 484.2613 | 503.3909 | 531.1424 | 390.8544
2454.0667 | 482.2145 | 505.4213 | 533.8015 | 390.8544
2455.0667 | 480.9894 | 507.2698 | 533.4847 | 390.8105
2456.0667 | 482.4989 | 508.2413 | 536.4693 | 390.8468
2457.0667 | 480.6995 | 511.1833 | 535.3451 | 390.8043
2458.0667 | 480.4119 | 513.3779 | 535.1797 | 390.8848
2459.0667 | 478.4955 | 516.1367 | 535.5928 | 390.9945
2460.0667 | 483.1766 | 517.7838 | 537.9459 | 391.2923
2461.0667 | 484.1475 | 517.6404 | 542.1563 | 391.7023
2462.0667 | 482.9246 | 518.8264 | 543.0256 | 392.161
2463.0667 | 479.5051 | 521.4378 | 543.062 | 392.5503
2464.0667 | 485.7696 | 527.3477 | 542.6819 | 392.9166
2465.0667 | 495.7703 | 527.8903 | 543.4644 | 393.4017
2466.0667 | 494.6935 | 525.5158 | 544.1947 | 393.8667
2467.0667 | 495.7932 | 524.3375 | 541.0641 | 394.1013
2468.0667 | 493.8115 | 523.7438 | 540.5577 | 394.2476
2469.0667 | 494.3023 | 524.0244 | 538.4819 | 394.4207
2470.0667 | 495.0211 | 524.3325 | 540.4916 | 394.5714
2471.0667 | 499.4201 | 525.4684 | 539.0215 | 394.8881
2472.0667 | 500.6195 | 526.0388 | 540.5274 | 395.252
2473.0667 | 501.2321 | 526.505 | 538.5915 | 395.4558
2474.0667 | 499.1602 | 525.6871 | 536.9767 | 395.4652
2475.0667 | 510.85 | 525.2893 | 537.4093 | 395.6364
2476.0823 | 514.386 | 523.5345 | 537.4084 | 395.817
2477.0667 | 511.9102 | 521.0108 | 536.9361 | 395.851
2478.0667 | 510.741 | 520.9446 | 536.6188 | 395.8457
2479.0667 | 510.6087 | 519.7151 | 535.8757 | 395.9446
2480.0667 | 508.974 | 522.5304 | 533.4528 | 396.083
2481.0667 | 511.2153 | 522.3568 | 531.7491 | 396.466
2482.0667 | 511.5981 | 520.5975 | 533.8735 | 396.7046
2483.0667 | 508.0958 | 520.178 | 533.796 | 396.8167
2484.0667 | 508.112 | 517.8844 | 534.2371 | 396.7476
2485.0667 | 506.2046 | 517.4467 | 531.4333 | 396.5863
2486.0667 | 503.1579 | 517.6887 | 533.0681 | 396.651
2487.0667 | 503.8631 | 517.6325 | 531.1463 | 396.9274
2488.0667 | 504.0586 | 516.0014 | 534.0642 | 397.2139
2489.0667 | 501.4908 | 514.7791 | 538.5207 | 397.3403
2490.0667 | 497.4697 | 518.2344 | 539.6337 | 397.3289
2491.0667 | 494.9355 | 519.3678 | 537.7045 | 397.0497
2492.0667 | 516.2617 | 519.2578 | 534.2198 | 396.6431
2493.0667 | 512.6015 | 518.37 | 534.781 | 396.4683
2494.0667 | 510.51 | 514.9315 | 533.4116 | 396.5768
2495.0667 | 521.8245 | 513.8403 | 533.2234 | 396.8217
2496.0667 | 513.9453 | 511.7266 | 531.6457 | 397.0488
2497.0667 | 508.409 | 510.8369 | 534.8625 | 397.1295
2498.0667 | 506.5927 | 509.7105 | 535.1188 | 397.2095
2499.0667 | 503.7755 | 511.6598 | 537.8615 | 397.3623
2500.0667 | 502.6585 | 511.8484 | 538.8943 | 397.5266
2501.0667 | 503.295 | 512.9043 | 536.1238 | 397.5966
2502.0667 | 521.1319 | 513.5173 | 537.1093 | 397.7187
2503.0667 | 526.5424 | 511.2878 | 538.0131 | 397.9057
2504.0667 | 534.8032 | 512.7346 | 537.0038 | 398.177
2505.0667 | 536.0378 | 512.0053 | 537.0423 | 398.2898
2506.0667 | 540.7924 | 509.6175 | 536.6734 | 398.5828
2507.0667 | 544.2564 | 510.6931 | 535.1942 | 398.7778
2508.0667 | 541.3742 | 510.5882 | 534.8339 | 399.0127
2509.0667 | 545.7802 | 509.6329 | 535.6543 | 399.3653
2510.0667 | 539.6582 | 507.6833 | 533.9279 | 399.7794
2511.0823 | 537.6202 | 507.2606 | 531.3719 | 400.0296
2512.0667 | 531.8901 | 509.0004 | 530.9766 | 400.0832
2513.0667 | 524.4458 | 511.6548 | 530.2261 | 399.9355
2514.0667 | 519.4182 | 515.0794 | 528.1527 | 399.6606
2515.0667 | 513.2123 | 516.6799 | 529.5087 | 399.6182
2516.0667 | 521.0533 | 516.7302 | 527.5914 | 399.6477
2517.0667 | 529.4507 | 518.491 | 529.9266 | 399.8247
2518.0667 | 534.1911 | 519.1934 | 528.1282 | 399.9917
2519.0823 | 531.2015 | 518.0549 | 530.3426 | 400.1948
2520.0667 | 529.4296 | 518.085 | 528.6327 | 400.2514
2521.0667 | 521.8786 | 519.5437 | 527.2149 | 400.1494
2522.0667 | 537.0475 | 522.13 | 527.6922 | 400.1875
2523.0667 | 539.6953 | 524.2049 | 532.3061 | 400.3636
2524.0667 | 537.8739 | 524.4308 | 531.0996 | 400.4891
2525.0667 | 534.2331 | 525.1043 | 527.1763 | 400.5117
2526.0667 | 529.8523 | 524.2316 | 525.6008 | 400.3424
2527.0667 | 523.473 | 523.4309 | 523.9118 | 400.0145
2528.0667 | 516.4594 | 523.822 | 521.5073 | 399.5542
2529.0667 | 511.4976 | 530.4993 | 520.4434 | 399.1083
2530.0667 | 512.5331 | 532.5508 | 519.7441 | 398.8971
2531.0667 | 514.0446 | 536.1008 | 519.9509 | 398.7555
2532.0667 | 511.0913 | 536.6926 | 521.0369 | 398.5502
2533.0667 | 508.1109 | 539.6413 | 532.4168 | 398.3551
2534.0667 | 510.6649 | 538.8934 | 530.7096 | 398.2742
2535.0667 | 510.6475 | 540.3188 | 529.7301 | 398.5231
2536.0823 | 511.6883 | 538.5646 | 530.456 | 398.6761
2537.0667 | 529.9149 | 539.0951 | 533.2502 | 398.7642
2538.0667 | 526.5408 | 539.9652 | 534.6386 | 398.8446
2539.0667 | 522.2511 | 542.9885 | 534.3663 | 398.8676
2540.0667 | 530.5371 | 546.2499 | 531.8163 | 398.9016
2541.0667 | 527.9023 | 550.5278 | 532.7396 | 399.0196
2542.0667 | 527.3053 | 551.6601 | 536.086 | 399.3248
2543.0667 | 521.1988 | 552.5702 | 538.9034 | 399.4762
2544.0667 | 521.4091 | 553.0673 | 534.7077 | 399.6789
2545.0667 | 516.068 | 552.4723 | 534.9522 | 399.7684
2546.0667 | 519.9127 | 553.0485 | 535.9451 | 399.9813
2547.0667 | 525.0312 | 554.3704 | 533.3695 | 400.333
2548.0823 | 545.1159 | 553.7189 | 532.4699 | 400.8021
2549.0667 | 569.8987 | 551.5308 | 530.5506 | 401.291
2550.0667 | 577.5993 | 550.5551 | 531.7113 | 401.957
2551.0667 | 584.0016 | 549.558 | 531.45 | 402.4891
2552.0667 | 584.6849 | 546.6758 | 529.7879 | 402.8754
2553.0667 | 586.8725 | 545.082 | 529.0922 | 403.2154
2554.0667 | 589.4773 | 543.9961 | 528.7619 | 403.4425
2555.0667 | 590.6059 | 546.1403 | 529.0692 | 403.6382
2556.0667 | 588.5277 | 549.0307 | 528.8781 | 404.0317
2557.0667 | 581.4968 | 550.3901 | 529.7738 | 404.5118
2558.0667 | 586.3354 | 555.451 | 528.9083 | 404.9664
2559.0667 | 591.2645 | 555.793 | 527.3776 | 405.3561
2560.0667 | 590.258 | 553.2674 | 527.3643 | 405.7129
2561.0667 | 580.9576 | 554.2854 | 525.8948 | 406.2427
2562.0667 | 579.7573 | 553.0284 | 524.6962 | 406.7591
2563.0667 | 581.9985 | 550.6029 | 525.5729 | 407.2345
2564.0667 | 585.1634 | 552.2133 | 525.8238 | 407.5483
2565.0667 | 602.1874 | 552.631 | 526.127 | 407.6479
2566.0823 | 599.7804 | 552.3362 | 526.537 | 407.6774
2567.0667 | 586.9163 | 551.3397 | 525.4233 | 407.7515
2568.0667 | 587.19 | 553.976 | 526.3901 | 407.9597
2569.0667 | 595.4583 | 553.2853 | 530.7532 | 408.3402
2570.0667 | 597.318 | 549.2297 | 532.5151 | 408.8056
2571.0667 | 591.1522 | 545.3411 | 532.1433 | 409.1799
2572.0667 | 586.3506 | 545.3167 | 529.7528 | 409.3488
2573.0667 | 584.7551 | 545.4603 | 530.1376 | 409.3871
2574.0667 | 582.2227 | 545.6273 | 529.9504 | 409.4633
2575.0667 | 577.7529 | 545.7239 | 531.0941 | 409.6631
2576.0667 | 595.511 | 545.6452 | 533.2964 | 410.0503
2577.0667 | 585.0188 | 546.1555 | 533.802 | 410.2971
2578.0667 | 590.7884 | 545.5542 | 531.8727 | 410.5124
2579.0667 | 587.1356 | 544.7186 | 529.9552 | 410.6354
2580.0667 | 588.8162 | 544.4076 | 528.7439 | 410.72
2581.0667 | 588.9669 | 545.1422 | 529.9511 | 410.6722
2582.0667 | 598.9415 | 549.33 | 531.6746 | 410.7039
2583.0667 | 593.2428 | 551.7519 | 534.9182 | 410.8929
2584.0667 | 585.3719 | 553.2006 | 531.8458 | 411.0672
2585.0667 | 597.0497 | 553.687 | 531.0631 | 411.1505
2586.0667 | 605.9638 | 553.4676 | 531.5731 | 411.0307
2587.0667 | 608.1543 | 554.8651 | 530.4111 | 410.897
2588.0667 | 598.6191 | 557.8879 | 531.8232 | 410.8372
2589.0667 | 586.0541 | 561.3057 | 532.2302 | 410.7977
2590.0667 | 573.978 | 562.5622 | 532.0718 | 410.8306
2591.0667 | 567.2185 | 563.5809 | 531.9697 | 411.0481
2592.0667 | 579.0897 | 565.0323 | 530.0606 | 411.2757
2593.0667 | 582.8489 | 565.4016 | 529.6464 | 411.3366
2594.0667 | 574.5381 | 565.1236 | 530.4548 | 411.4674
2595.0667 | 564.8484 | 566.6737 | 528.0509 | 411.4118
2596.0823 | 560.3002 | 564.1251 | 526.2629 | 411.2907
2597.0667 | 557.6006 | 561.4231 | 526.5252 | 411.1688
2598.0667 | 561.4911 | 563.0862 | 528.5003 | 411.1
2599.0667 | 559.5426 | 565.0193 | 530.0391 | 410.9859
2600.0667 | 558.3419 | 565.9905 | 528.7436 | 410.8072
2601.0667 | 559.1478 | 565.9844 | 527.7176 | 410.7288
2602.0667 | 565.1925 | 565.9449 | 525.6649 | 410.8699
2603.0667 | 578.7174 | 569.1096 | 527.8699 | 411.25
2604.0667 | 582.4999 | 570.409 | 531.5648 | 411.6797
2605.0667 | 593.3329 | 568.6248 | 530.7208 | 412.0661
2606.0667 | 615.6619 | 570.1196 | 531.2155 | 412.3527
2607.0667 | 623.8266 | 568.8435 | 533.9251 | 412.5024
2608.0667 | 626.9724 | 567.4702 | 533.4015 | 412.5057
2609.0667 | 624.4125 | 572.8 | 533.5113 | 412.4102
2610.0667 | 626.3531 | 573.3633 | 532.4296 | 412.2588
2611.0667 | 624.7917 | 574.2075 | 530.6103 | 412.1639
2612.0667 | 628.3227 | 573.8985 | 528.7956 | 412.2381
2613.0667 | 625.8271 | 573.168 | 527.3229 | 412.4239
2614.0667 | 624.2489 | 580.1306 | 532.5567 | 412.7729
2615.0667 | 617.6797 | 579.6881 | 533.2716 | 412.9187
2616.0667 | 608.291 | 580.9944 | 534.8052 | 412.9838
2617.0667 | 605.5325 | 582.7681 | 534.6287 | 412.9731
2618.0667 | 600.3701 | 589.6231 | 535.4497 | 413.0151
2619.0667 | 597.9819 | 593.6009 | 534.1997 | 413.1519
2620.0667 | 595.2528 | 594.4257 | 531.1452 | 413.2332
2621.0667 | 589.6697 | 592.2382 | 528.2868 | 413.1914
2622.0667 | 591.0368 | 588.4534 | 526.3984 | 413.3973
2623.0667 | 603.4101 | 592.3422 | 532.4147 | 413.6925
2624.0667 | 610.9278 | 593.9197 | 533.4633 | 413.9859
2625.0667 | 608.7628 | 594.4665 | 533.617 | 414.0721
2626.0823 | 610.1358 | 599.2679 | 531.9417 | 414.1313
2627.0667 | 605.1756 | 597.4013 | 532.7984 | 414.3546
2628.0667 | 598.5576 | 594.0083 | 532.3241 | 414.6797
2629.0667 | 596.1294 | 592.9443 | 532.5235 | 415.0184
2630.0667 | 587.3633 | 594.8328 | 532.1597 | 415.2081
2631.0667 | 582.2001 | 597.2566 | 533.6337 | 415.3725
2632.0667 | 576.3795 | 597.4804 | 533.1084 | 415.5086
2633.0667 | 566.6338 | 599.4502 | 532.1596 | 415.7052
2634.0667 | 566.7177 | 601.7143 | 531.059 | 415.8524
2635.0667 | 564.5203 | 606.0607 | 537.933 | 416.0551
2636.0667 | 564.0923 | 607.2368 | 539.7106 | 416.3411
2637.0667 | 555.638 | 607.2795 | 539.8118 | 416.9288
2638.0667 | 553.656 | 604.7829 | 539.3406 | 417.6326
2639.0667 | 557.5975 | 607.3824 | 542.1901 | 418.9753
2640.0667 | 565.8227 | 614.0757 | 548.2506 | 419.9824
2641.0667 | 575.0037 | 611.9145 | 550.3489 | 420.5869
2642.0667 | 598.5042 | 606.4161 | 554.3247 | 421.2003
2643.0667 | 616.4587 | 610.4423 | 554.9045 | 421.6039
2644.0667 | 613.9595 | 604.7818 | 551.6959 | 421.6916
2645.0667 | 616.2843 | 596.6396 | 549.0694 | 421.9933
2646.0667 | 618.2138 | 595.0317 | 546.3824 | 422.4672
2647.0667 | 618.9714 | 606.4558 | 550.571 | 423.0422
2648.0667 | 626.7997 | 610.6184 | 547.9784 | 423.4766
2649.0667 | 628.1878 | 605.4015 | 545.8658 | 423.7738
2650.0667 | 621.6601 | 619.6657 | 542.9299 | 423.8776
2651.0667 | 617.0078 | 617.3077 | 539.3735 | 424.0446
2652.0667 | 614.2739 | 615.4427 | 538.0179 | 424.1657
2653.0667 | 611.3891 | 614.1321 | 539.7509 | 424.7562
2654.0667 | 610.134 | 614.7271 | 539.1703 | 425.1025
2655.0667 | 599.6026 | 614.2298 | 537.9639 | 425.2791
2656.0823 | 593.6472 | 618.8051 | 537.2362 | 425.4886
2657.0667 | 587.6251 | 617.8714 | 540.3234 | 425.7423
2658.0667 | 590.4786 | 611.8172 | 539.3111 | 425.7284
2659.0667 | 586.4722 | 608.6423 | 538.1589 | 425.8523
2660.0667 | 586.6268 | 613.9524 | 538.0378 | 425.8646
2661.0667 | 587.5057 | 613.8459 | 537.9841 | 425.8611
2662.0667 | 582.9355 | 612.3651 | 540.0192 | 425.7848
2663.0667 | 579.5958 | 608.9123 | 541.8742 | 425.8519
2664.0667 | 574.6702 | 622.8818 | 552.7071 | 426.0333
2665.0667 | 567.3937 | 626.7244 | 551.3675 | 426.2297
2666.0667 | 562.6949 | 621.2793 | 549.3272 | 426.2034
2667.0667 | 560.6766 | 619.5927 | 550.7876 | 426.2066
2668.0667 | 577.6433 | 620.1709 | 550.2772 | 426.2482
2669.0667 | 577.5666 | 621.1775 | 546.7338 | 426.4375
2670.0823 | 574.4064 | 618.3348 | 543.3293 | 426.7866
2671.0667 | 583.0971 | 628.8207 | 541.7778 | 427.0108
2672.0667 | 583.9572 | 628.0066 | 540.3405 | 426.9172
2673.0667 | 584.6415 | 632.4163 | 536.0156 | 426.6788
2674.0667 | 593.3797 | 629.4814 | 534.8808 | 426.6187
2675.0667 | 590.4421 | 631.7423 | 532.4819 | 426.5169
2676.0667 | 588.9143 | 650.4989 | 532.3066 | 426.7458
2677.0667 | 584.071 | 648.1691 | 532.02 | 427.0863
2678.0667 | 585.344 | 644.8879 | 530.6894 | 427.2547
2679.0667 | 589.4986 | 639.8489 | 529.4354 | 427.1801
2680.0667 | 585.3851 | 638.206 | 528.2962 | 427.0012
2681.0667 | 579.585 | 637.9135 | 529.0047 | 426.8793
2682.0667 | 576.2813 | 631.3069 | 527.0122 | 426.7904
2683.0667 | 572.6461 | 644.0454 | 526.1222 | 426.6722
2684.0667 | 572.5034 | 653.4504 | 528.9359 | 426.9195
2685.0667 | 573.6735 | 653.6927 | 532.9692 | 427.3818
2686.0667 | 579.1438 | 649.2541 | 534.6622 | 427.7555
2687.0667 | 578.11 | 641.0718 | 533.6548 | 428.0239
2688.0667 | 576.7788 | 649.0574 | 534.1501 | 428.2779
2689.0667 | 575.9849 | 651.4771 | 534.5266 | 428.5523
2690.0667 | 588.1222 | 645.0573 | 533.5383 | 429.0483
2691.0667 | 590.1964 | 639.1093 | 533.9772 | 429.4691
2692.0667 | 591.5118 | 655.8754 | 534.9101 | 429.8668
2693.0667 | 598.1028 | 663.8012 | 537.2067 | 430.2485
2694.0667 | 604.3997 | 660.1503 | 538.1389 | 430.5529
2695.0667 | 598.8869 | 661.7826 | 538.8998 | 431.0112
2696.0667 | 595.1508 | 662.398 | 538.5558 | 431.4985
2697.0667 | 596.2662 | 667.7622 | 536.6381 | 432.0578
2698.0667 | 601.9738 | 671.7102 | 538.695 | 432.704
2699.0667 | 602.5182 | 670.1968 | 538.7276 | 433.2629
2700.0667 | 603.4532 | 664.3255 | 538.073 | 433.6179
2701.0667 | 594.6068 | 669.1206 | 537.3642 | 433.9024
2702.0667 | 590.3425 | 664.7289 | 534.9367 | 434.1225
2703.0667 | 589.8535 | 669.0445 | 535.1039 | 434.3485
2704.0667 | 589.6981 | 672.3738 | 534.5508 | 434.4599
2705.0667 | 587.8279 | 676.9849 | 535.8695 | 434.6516
2706.0667 | 584.1418 | 673.3894 | 535.2327 | 434.7902
2707.0667 | 580.004 | 666.436 | 533.5186 | 434.9192
2708.0667 | 578.2704 | 658.5418 | 533.6895 | 435.3924
2709.0667 | 573.5531 | 664.0886 | 535.9398 | 435.7299
2710.0667 | 581.756 | 660.7633 | 535.3642 | 435.9748
2711.0667 | 581.1084 | 655.8894 | 536.2433 | 436.0285
2712.0667 | 581.46 | 654.8751 | 535.3202 | 436.0856
2713.0667 | 584.0959 | 650.7673 | 537.1178 | 436.4918
2714.0667 | 579.4462 | 651.5145 | 537.2494 | 437.0065
2715.0667 | 577.6337 | 648.315 | 537.7291 | 437.4075
2716.0667 | 580.7202 | 651.5914 | 539.1973 | 437.7979
2717.0667 | 582.2134 | 645.8572 | 539.6618 | 438.0033
2718.0667 | 577.868 | 639.9511 | 541.4739 | 438.3142
2719.0667 | 576.3068 | 639.5128 | 539.9012 | 438.7538
2720.0667 | 581.5847 | 646.6674 | 539.665 | 439.0044
2721.0667 | 584.927 | 643.4601 | 540.0348 | 439.1149
2722.0667 | 574.0298 | 639.1349 | 538.0323 | 439.0425
2723.0667 | 579.3563 | 644.5717 | 538.0514 | 438.9676
2724.0667 | 577.6912 | 648.9328 | 539.7353 | 438.9969
2725.0667 | 576.9759 | 651.2294 | 539.3935 | 439.2756
2726.0667 | 581.555 | 658.0658 | 539.964 | 440.1614
2727.0667 | 585.829 | 658.9664 | 541.6176 | 440.7524
2728.0823 | 577.6242 | 652.8038 | 538.6613 | 441.0302
2729.0667 | 583.0203 | 657.8216 | 540.3718 | 440.8881
2730.0667 | 583.9928 | 652.4 | 540.7007 | 441.0925
2731.0667 | 581.5713 | 654.1797 | 539.7802 | 441.0868
2732.0667 | 581.0118 | 666.0497 | 537.2727 | 441.1888
2733.0667 | 579.6359 | 669.2006 | 535.598 | 441.5175
2734.0667 | 578.6027 | 681.7094 | 534.7309 | 441.6411
2735.0667 | 580.1255 | 686.104 | 535.8072 | 441.7923
2736.0667 | 573.9622 | 677.5885 | 538.9461 | 441.848
2737.0667 | 564.8146 | 667.818 | 539.2975 | 441.7739
2738.0667 | 558.6017 | 672.7478 | 536.004 | 441.555
2739.0667 | 562.2785 | 664.5694 | 536.5399 | 441.3604
2740.0667 | 560.2495 | 666.6569 | 540.2617 | 441.3843
2741.0667 | 553.6978 | 660.1475 | 539.2803 | 441.4348
2742.0667 | 551.7686 | 660.6434 | 539.4541 | 441.5639
2743.0667 | 557.9278 | 652.1565 | 538.7034 | 441.683
2744.0667 | 558.3415 | 651.7383 | 542.6037 | 442.0843
2745.0667 | 555.9877 | 648.1854 | 544.0516 | 442.3545
2746.0667 | 553.592 | 644.6176 | 543.5981 | 442.3015
2747.0667 | 551.8261 | 640.724 | 547.165 | 442.4944
2748.0667 | 549.5993 | 639.0046 | 547.2844 | 442.4927
2749.0667 | 559.9937 | 638.1859 | 544.3245 | 442.4926
2750.0667 | 554.1751 | 633.5024 | 544.7456 | 442.4371
2751.0667 | 548.3909 | 631.9227 | 543.9381 | 442.3098
2752.0667 | 550.5125 | 631.4566 | 541.4464 | 442.2832
2753.0667 | 551.559 | 636.2778 | 542.9887 | 442.5593
2754.0667 | 549.0809 | 633.9677 | 544.0542 | 442.7287
2755.0667 | 548.3569 | 627.6109 | 543.0209 | 442.912
2756.0667 | 551.1138 | 630.5771 | 545.8614 | 443.115
2757.0667 | 550.9422 | 633.7832 | 545.9509 | 443.148
2758.0667 | 547.537 | 633.9278 | 544.5507 | 443.2361
2759.0667 | 550.1398 | 636.9699 | 544.2376 | 443.3461
2760.0667 | 552.1222 | 639.2592 | 545.379 | 443.3812
2761.0667 | 550.0871 | 641.0727 | 547.5178 | 443.394
2762.0667 | 553.5811 | 637.2042 | 550.4041 | 443.544
2763.0667 | 551.1788 | 633.643 | 551.1242 | 443.5837
2764.0667 | 550.7331 | 635.2402 | 550.0299 | 443.4915
2765.0667 | 554.8979 | 637.1503 | 551.2247 | 443.4049
2766.0667 | 560.7766 | 647.3884 | 552.5478 | 443.4142
2767.0667 | 563.4357 | 660.7123 | 552.7295 | 443.7298
2768.0667 | 561.1752 | 659.4789 | 551.857 | 444.189
2769.0667 | 557.2217 | 649.7145 | 551.2685 | 444.481
2770.0667 | 565.6996 | 642.747 | 551.6631 | 444.5305
2771.0667 | 559.3587 | 642.8524 | 552.9153 | 444.5396
2772.0667 | 552.3322 | 652.9168 | 551.0491 | 444.5399
2773.0667 | 548.1198 | 662.0352 | 549.0636 | 445.0124
2774.0667 | 544.5244 | 666.3604 | 546.8336 | 445.5078
2775.0667 | 542.2798 | 661.8386 | 544.6406 | 446.0901
2776.0667 | 537.7522 | 665.2653 | 545.8198 | 446.5649
2777.0667 | 535.2651 | 655.4932 | 544.8068 | 446.8987
2778.0667 | 536.5901 | 645.4155 | 545.806 | 447.8681
2779.0667 | 534.4232 | 637.2831 | 544.6146 | 448.8641
2780.0667 | 534.2603 | 634.2284 | 543.1964 | 449.5741
2781.0667 | 541.6197 | 641.9788 | 544.7221 | 450.1156
2782.0667 | 548.8678 | 643.7362 | 544.9931 | 450.3621
2783.0667 | 551.0675 | 650.2923 | 545.7788 | 450.9945
2784.0667 | 549.6644 | 653.2809 | 546.4731 | 451.8447
2785.0667 | 548.4688 | 654.2607 | 548.7345 | 453.1809
2786.0667 | 546.1994 | 649.4829 | 548.1847 | 454.0095
2787.0667 | 542.4938 | 647.2603 | 548.375 | 454.442
2788.0667 | 535.2305 | 644.2178 | 547.345 | 454.9166
2789.0667 | 535.2337 | 639.6238 | 545.8443 | 455.3758
2790.0667 | 530.2108 | 631.9939 | 544.0281 | 455.776
2791.0667 | 528.5649 | 639.0897 | 545.4495 | 456.2786
2792.0667 | 527.1655 | 642.9077 | 550.4819 | 456.8404
2793.0667 | 528.1964 | 644.1246 | 554.2516 | 457.547
2794.0667 | 526.6784 | 644.0256 | 565.121 | 458.7854
2795.0667 | 525.6885 | 638.168 | 563.8144 | 460.0999
2796.0667 | 532.7045 | 636.4525 | 562.7974 | 461.3538
2797.0667 | 529.9546 | 634.042 | 563.7405 | 462.9307
2798.0667 | 531.2675 | 632.5501 | 560.829 | 464.2279
2799.0667 | 528.5295 | 626.1023 | 560.4411 | 464.9251
2800.0667 | 527.4633 | 624.416 | 557.3807 | 465.2188
2801.0667 | 526.93 | 628.2659 | 554.3484 | 466.0751
2802.0667 | 526.0411 | 626.229 | 567.2322 | 467.7951
2803.0667 | 525.5359 | 630.5373 | 570.6182 | 469.4178
2804.0667 | 525.0973 | 630.7578 | 566.5607 | 471.0205
2805.0667 | 532.1273 | 629.6637 | 560.0876 | 472.0059
2806.0667 | 534.9037 | 629.8561 | 560.199 | 473.4243
2807.0667 | 532.3949 | 623.5557 | 565.3556 | 474.6739
2808.0667 | 531.6791 | 626.5413 | 562.3531 | 475.9172
2809.0667 | 532.5591 | 628.0739 | 561.1445 | 476.7175
2810.0667 | 534.3416 | 631.0322 | 559.3776 | 478.2953
2811.0667 | 536.1584 | 631.672 | 557.3 | 479.6396
2812.0667 | 532.4167 | 635.9215 | 555.7304 | 480.6036
2813.0667 | 531.821 | 630.5118 | 551.4248 | 481.2767
2814.0667 | 526.4834 | 636.5747 | 549.3505 | 481.6201
2815.0667 | 524.4394 | 641.5463 | 547.5412 | 482.0405
2816.0667 | 521.7743 | 640.0149 | 553.8729 | 482.4161
2817.0667 | 519.6073 | 635.5321 | 561.2019 | 483.3405
2818.0667 | 525.8353 | 639.7078 | 560.3731 | 484.4259
2819.0667 | 527.9172 | 640.2595 | 558.8423 | 485.9075
2820.0667 | 534.887 | 635.0856 | 557.3046 | 486.9875
2821.0667 | 536.0365 | 638.0493 | 555.8043 | 487.6118
2822.0667 | 532.7243 | 635.6309 | 554.1414 | 488.2753
2823.0667 | 528.9992 | 631.9774 | 553.3905 | 488.5803
2824.0667 | 526.4072 | 632.5361 | 553.0871 | 488.4366
2825.0667 | 527.1383 | 638.5261 | 554.7168 | 488.9325
2826.0667 | 532.8034 | 636.1177 | 555.6774 | 489.9805
2827.0667 | 532.2338 | 633.2182 | 553.9091 | 490.6387
2828.0667 | 529.2019 | 634.5104 | 550.9431 | 490.8726
2829.0667 | 524.9236 | 629.6488 | 546.9473 | 491.235
2830.0667 | 520.6548 | 622.5238 | 542.2672 | 491.4571
2831.0667 | 519.4006 | 620.3274 | 542.6345 | 491.9106
2832.0667 | 520.5824 | 615.8574 | 551.9112 | 492.387
2833.0667 | 522.0602 | 619.1335 | 550.4042 | 492.7204
2834.0667 | 522.5427 | 624.2645 | 555.1733 | 493.2119
2835.0667 | 524.5664 | 625.6264 | 552.2181 | 493.2116
2836.0667 | 528.1881 | 634.9991 | 551.2774 | 493.2823
2837.0667 | 532.3832 | 629.0034 | 552.5804 | 493.5077
2838.0667 | 529.2602 | 617.6378 | 554.0941 | 493.4881
2839.0667 | 528.2172 | 627.3392 | 564.4004 | 493.7221
2840.0667 | 528.3543 | 633.0252 | 564.9333 | 493.7562
2841.0667 | 527.4068 | 629.4205 | 563.273 | 493.8275
2842.0667 | 526.3398 | 617.8511 | 557.5738 | 493.9653
2843.0667 | 526.1409 | 609.2413 | 553.0337 | 493.8736
2844.0667 | 526.0151 | 610.4825 | 552.321 | 493.914
2845.0667 | 524.5075 | 607.0205 | 552.1946 | 494.2944
2846.0667 | 523.5595 | 602.9653 | 558.1041 | 494.3426
2847.0667 | 519.7934 | 601.5419 | 556.1656 | 494.9591
2848.0823 | 518.0054 | 595.3867 | 563.6274 | 495.9064
2849.0667 | 517.8044 | 593.333 | 568.8111 | 496.6699
2850.0667 | 519.0918 | 593.1938 | 569.9953 | 497.3896
2851.0667 | 520.8437 | 600.4335 | 568.1161 | 497.8202
2852.0667 | 519.7514 | 598.7494 | 567.5411 | 498.5379
2853.0667 | 519.6187 | 595.9429 | 565.6961 | 498.9298
2854.0667 | 519.0106 | 593.1224 | 564.1147 | 499.0313
2855.0667 | 518.7923 | 588.3324 | 567.346 | 499.5438
2856.0667 | 517.4272 | 586.0456 | 574.3521 | 499.6277
2857.0667 | 515.8998 | 592.9056 | 573.3928 | 499.6655
2858.0667 | 515.9295 | 593.4679 | 576.695 | 500.2668
2859.0667 | 514.4962 | 595.1652 | 574.5811 | 500.4783
2860.0667 | 513.3178 | 595.7547 | 574.7756 | 500.3535
2861.0667 | 511.784 | 593.8074 | 577.0431 | 500.2782
2862.0667 | 508.6408 | 591.6961 | 582.1736 | 500.4782
2863.0667 | 508.1162 | 597.2638 | 575.0143 | 500.5154
2864.0667 | 508.9696 | 601.6179 | 570.1613 | 500.0621
2865.0667 | 515.7956 | 594.9138 | 566.5672 | 499.5593
2866.0667 | 518.9057 | 591.8079 | 565.6155 | 500.0314
2867.0667 | 516.839 | 586.4654 | 562.4361 | 500.3865
2868.0667 | 515.8925 | 583.8903 | 561.0737 | 500.5251
2869.0667 | 515.4285 | 586.9677 | 558.7972 | 500.4349
2870.0667 | 514.9394 | 591.1674 | 555.4532 | 500.2197
2871.0667 | 512.2809 | 590.8952 | 560.0435 | 499.9239
2872.0667 | 512.3232 | 588.5579 | 557.9198 | 500.0692
2873.0667 | 511.8238 | 586.1141 | 564.9746 | 500.3686
2874.0667 | 511.9571 | 584.5682 | 565.3248 | 500.3824
2875.0667 | 510.9398 | 583.7236 | 573.9053 | 500.3287
2876.0667 | 510.8389 | 583.1489 | 570.4094 | 500.4182
2877.0667 | 509.3525 | 587.567 | 574.8605 | 500.6282
2878.0667 | 508.927 | 593.94 | 576.9358 | 501.1882
2879.0667 | 508.1141 | 588.9283 | 575.5772 | 501.602
2880.0667 | 508.8116 | 593.4017 | 572.1488 | 502.4293
2881.0667 | 508.1499 | 592.3339 | 570.5014 | 503.6331
2882.0667 | 508.479 | 598.6578 | 569.4657 | 504.653
2883.0667 | 508.7468 | 594.4568 | 569.8876 | 505.1855
2884.0667 | 507.6353 | 593.2502 | 571.0789 | 505.2398
2885.0667 | 506.4192 | 591.1269 | 572.6151 | 505.3819
2886.0667 | 505.35 | 587.6206 | 577.6591 | 505.6024
2887.0667 | 506.5879 | 589.5267 | 576.3509 | 506.0643
2888.0667 | 508.5816 | 588.7519 | 579.367 | 506.9185
2889.0667 | 507.2975 | 595.3426 | 575.9439 | 507.2384
2890.0667 | 507.3957 | 596.4915 | 581.3293 | 507.1053
2891.0667 | 506.8884 | 593.2616 | 577.231 | 506.779
2892.0667 | 509.5301 | 590.917 | 580.3546 | 506.6797
2893.0667 | 512.5121 | 594.3782 | 576.8542 | 506.8571
2894.0667 | 513.0738 | 596.7022 | 575.8334 | 506.553
2895.0667 | 512.4744 | 601.0693 | 573.4326 | 506.022
2896.0667 | 514.0193 | 604.5555 | 577.8459 | 505.3435
2897.0667 | 513.1416 | 604.9794 | 576.0435 | 504.7994
2898.0667 | 511.4162 | 601.647 | 577.4535 | 504.7786
2899.0667 | 510.7786 | 596.6184 | 574.2611 | 505.3709
2900.0667 | 511.5326 | 595.1783 | 572.651 | 506.0336
2901.0667 | 512.9813 | 597.0573 | 570.9327 | 506.5042
2902.0667 | 513.1245 | 593.7635 | 572.14 | 506.7825
2903.0667 | 513.5212 | 589.723 | 568.8185 | 506.9624
2904.0667 | 513.2969 | 593.8737 | 566.3751 | 507.0551
2905.0667 | 512.319 | 588.0573 | 571.0108 | 507.3168
2906.0667 | 511.4043 | 585.2657 | 571.9013 | 507.3553
2907.0667 | 511.93 | 579.5761 | 581.4067 | 507.4563
2908.0667 | 513.166 | 583.997 | 580.6152 | 507.1386
2909.0667 | 513.9453 | 578.0115 | 576.0424 | 506.6572
2910.0667 | 514.0326 | 582.8451 | 571.0479 | 506.1403
2911.0667 | 513.2943 | 590.661 | 566.7407 | 506.0323
2912.0667 | 512.1068 | 586.2861 | 571.047 | 506.365
2913.0667 | 512.6764 | 580.9996 | 570.3012 | 506.7084
2914.0667 | 515.8022 | 579.5694 | 571.4976 | 506.8155
2915.0667 | 515.3204 | 578.1565 | 569.0575 | 506.7004
2916.0667 | 514.0708 | 574.0406 | 565.3093 | 506.5238
2917.0667 | 514.4945 | 568.7431 | 572.876 | 506.7787
2918.0667 | 515.6876 | 563.8042 | 570.8095 | 507.0873
2919.0667 | 517.6441 | 559.5936 | 571.3146 | 506.8792
2920.0667 | 523.6326 | 559.5987 | 568.8192 | 506.1515
2921.0667 | 523.4533 | 564.9957 | 563.7093 | 505.4488
2922.0667 | 527.5846 | 561.1278 | 559.8428 | 504.7038
2923.0667 | 529.069 | 571.5861 | 558.0325 | 504.0408
2924.0667 | 531.7573 | 566.7039 | 555.32 | 503.397
2925.0667 | 530.3973 | 561.5983 | 553.3825 | 503.0766
2926.0667 | 532.1706 | 556.6933 | 549.5483 | 502.4766
2927.0667 | 535.1186 | 554.1314 | 548.2061 | 502.0628
2928.0667 | 537.9598 | 550.9567 | 546.321 | 502.196
2929.0667 | 541.4046 | 560.0232 | 545.3691 | 502.4458
2930.0667 | 544.5766 | 562.5688 | 546.6357 | 503.2827
2931.0667 | 544.4829 | 564.7869 | 545.7893 | 504.0602
2932.0667 | 541.7 | 561.0195 | 543.9792 | 504.5175
2933.0667 | 539.1885 | 558.3341 | 542.9714 | 505.1548
2934.0667 | 540.7503 | 556.1483 | 542.1354 | 506.1311
2935.0667 | 542.4691 | 554.4357 | 542.4191 | 507.0506
2936.0667 | 545.1846 | 552.6401 | 540.8499 | 507.8399
2937.0667 | 543.4936 | 550.2691 | 539.6277 | 509.119
2938.0667 | 543.932 | 547.5045 | 539.8397 | 510.175
2939.0667 | 541.6299 | 546.428 | 540.4313 | 510.8086
2940.0667 | 540.1809 | 545.7826 | 539.8545 | 511.0844
2941.0667 | 537.2051 | 543.3413 | 539.0215 | 511.1904
2942.0667 | 536.4733 | 540.3341 | 539.072 | 511.2374
2943.0667 | 533.348 | 537.0025 | 538.0487 | 511.3897
2944.0667 | 530.538 | 532.9432 | 534.9389 | 511.4561
2945.0667 | 529.8001 | 529.4417 | 533.6762 | 511.1643
2946.0667 | 528.7157 | 545.5514 | 535.256 | 510.8508
2947.0667 | 528.0042 | 550.9819 | 537.6993 | 510.5856
2948.0667 | 527.1145 | 551.8287 | 540.5886 | 510.7214
2949.0667 | 525.6072 | 560.3074 | 542.0475 | 511.2093
2950.0667 | 525.0545 | 569.332 | 549.4171 | 511.5686
2951.0667 | 524.3831 | 566.5554 | 555.1615 | 511.7583
2952.0667 | 524.928 | 561.1322 | 554.8868 | 512.4704
2953.0667 | 525.942 | 573.5028 | 554.9131 | 513.5612
2954.0667 | 528.1792 | 576.1575 | 552.9734 | 514.4172
2955.0667 | 528.5646 | 573.8775 | 550.9138 | 514.9743
2956.0667 | 527.7539 | 570.8498 | 549.0923 | 515.302
2957.0667 | 525.2049 | 565.9694 | 549.4542 | 515.5811
2958.0667 | 524.2952 | 571.3559 | 551.8375 | 515.8899
2959.0667 | 522.7817 | 567.1435 | 552.1282 | 516.1972
2960.0667 | 523.2041 | 563.5754 | 554.4622 | 516.6204
2961.0667 | 522.0571 | 560.8283 | 558.3227 | 516.9937
2962.0667 | 521.3737 | 560.6188 | 558.9215 | 517.2891
2963.0667 | 522.0281 | 557.5155 | 557.0114 | 517.1798
2964.0667 | 521.4776 | 555.1172 | 560.6754 | 516.874
2965.0667 | 518.0309 | 553.391 | 558.531 | 516.3518
2966.0667 | 516.2918 | 554.741 | 558.0843 | 515.8896
2967.0667 | 514.9871 | 554.7292 | 560.8757 | 515.8328
2968.0667 | 514.3544 | 555.822 | 558.6958 | 516.1027
2969.0667 | 513.3058 | 553.3978 | 558.7318 | 516.7142
2970.0667 | 513.283 | 549.3422 | 568.9784 | 517.1398
2971.0667 | 515.1602 | 546.1946 | 570.9713 | 517.4014
2972.0667 | 515.3539 | 544.4241 | 570.3403 | 517.805
2973.0667 | 514.8014 | 544.4022 | 569.6575 | 517.8575
2974.0667 | 513.3666 | 547.5667 | 571.9109 | 517.829
2975.0667 | 512.2924 | 547.9755 | 572.3748 | 517.7672
2976.0667 | 510.6319 | 545.4862 | 569.8021 | 517.9238
2977.0667 | 510.5048 | 543.8964 | 566.8188 | 518.5768
2978.0667 | 511.3934 | 546.7253 | 568.5935 | 519.0651
2979.0667 | 512.9597 | 542.6319 | 569.8267 | 519.4717
2980.0667 | 515.8585 | 544.6542 | 568.6469 | 519.5247
2981.0667 | 517.3099 | 546.387 | 564.5205 | 519.4022
2982.0667 | 520.5361 | 545.4594 | 564.818 | 519.7204
2983.0667 | 525.4429 | 541.1136 | 561.2281 | 520.0509
2984.0667 | 527.9145 | 540.6099 | 559.8934 | 520.0827
2985.0667 | 528.6296 | 540.3302 | 558.683 | 520.3463
2986.0667 | 528.4963 | 537.7055 | 557.645 | 521.1385
2987.0667 | 527.7574 | 534.9699 | 557.8598 | 521.982
2988.0667 | 524.4051 | 535.1314 | 558.5018 | 522.4016
2989.0667 | 520.6183 | 536.6768 | 557.2083 | 522.4715
2990.0667 | 516.7537 | 536.2275 | 561.7635 | 522.3375
2991.0667 | 514.9349 | 535.853 | 564.8241 | 522.3394
2992.0667 | 513.9841 | 538.6147 | 566.8422 | 522.5998
2993.0667 | 512.983 | 542.8929 | 568.2418 | 522.9092
2994.0667 | 510.8411 | 543.4843 | 570.0515 | 523.3773
2995.0667 | 508.3117 | 543.7659 | 584.9378 | 523.6512
2996.0667 | 507.651 | 544.9469 | 582.2959 | 523.5064
2997.0667 | 506.406 | 544.8484 | 573.6978 | 523.1998
2998.0667 | 504.6894 | 544.1743 | 575.0845 | 522.7921
2999.0667 | 503.0078 | 541.6809 | 569.786 | 522.2416
3000.0667 | 503.9882 | 538.6294 | 563.4429 | 521.7534
3001.0667 | 504.4545 | 536.3915 | 557.8425 | 521.3678
3002.0667 | 504.4341 | 535.7369 | 559.7295 | 521.2944
3003.0667 | 505.6842 | 534.9273 | 558.569 | 521.5842
3004.0667 | 506.6191 | 530.7683 | 561.4127 | 522.1378
3005.0667 | 509.8918 | 537.5042 | 559.1536 | 522.5617
3006.0667 | 513.5997 | 536.6867 | 558.6354 | 522.9998
3007.0667 | 516.8819 | 536.6932 | 557.3104 | 523.4837
3008.0667 | 515.3423 | 536.3245 | 560.1172 | 523.5412
3009.0667 | 514.3133 | 536.8739 | 562.5711 | 523.304
3010.0667 | 512.1407 | 537.3315 | 560.3608 | 523.1573
3011.0667 | 510.7665 | 534.3449 | 558.055 | 523.2522
3012.0667 | 510.1638 | 533.6476 | 556.6554 | 523.3986
3013.0667 | 509.4073 | 533.2855 | 556.0177 | 523.3683
3014.0667 | 509.4419 | 534.0177 | 557.2101 | 523.1485
3015.0667 | 509.0835 | 533.4601 | 558.324 | 522.8758
3016.0667 | 507.6859 | 533.4073 | 554.0079 | 522.6873
3017.0667 | 507.2806 | 535.3574 | 551.4485 | 522.6741
3018.0667 | 505.4623 | 535.9931 | 551.9567 | 522.9729
3019.0667 | 504.7651 | 535.3394 | 549.6745 | 523.0043
3020.0667 | 506.2184 | 534.5884 | 552.3029 | 522.8951
3021.0667 | 507.6781 | 532.5628 | 551.0624 | 522.8316
3022.0667 | 509.5417 | 530.8495 | 550.5099 | 522.9176
3023.0667 | 510.7818 | 529.3649 | 550.2707 | 522.7932
3024.0667 | 510.4931 | 531.1374 | 549.9458 | 522.4646
3025.0667 | 511.1182 | 537.5166 | 553.332 | 521.7883
3026.0667 | 510.9297 | 534.9075 | 552.3297 | 520.9614
3027.0667 | 510.8527 | 532.7569 | 550.0407 | 520.1232
3028.0667 | 511.5253 | 530.7766 | 548.2855 | 519.1694
3029.0667 | 512.6073 | 528.8787 | 549.7992 | 517.9655
3030.0667 | 511.9144 | 527.6826 | 548.0291 | 516.4182
3031.0667 | 510.7619 | 527.5878 | 546.6389 | 515.0805
3032.0667 | 511.6261 | 526.3183 | 543.9476 | 514.2509
3033.0667 | 513.9183 | 524.19 | 541.7129 | 513.5438
3034.0667 | 517.862 | 521.7791 | 540.6993 | 512.9943
3035.0667 | 522.0873 | 518.5971 | 539.7294 | 512.497
3036.0667 | 525.363 | 516.3924 | 539.2369 | 512.2229
3037.0667 | 527.847 | 515.3541 | 541.3595 | 512.1226
3038.0667 | 525.7019 | 513.8959 | 541.6162 | 512.1748
3039.0667 | 524.0845 | 512.5895 | 540.0136 | 512.3146
3040.0667 | 524.926 | 511.5716 | 540.6982 | 512.5399
3041.0667 | 523.6993 | 512.5952 | 539.7669 | 512.5944
3042.0667 | 523.329 | 513.3024 | 541.3254 | 512.6295
3043.0667 | 524.1881 | 512.0073 | 545.004 | 512.4562
3044.0667 | 524.1866 | 510.7233 | 543.0173 | 512.2534
3045.0667 | 523.8388 | 510.6792 | 543.8749 | 512.1947
3046.0667 | 524.0488 | 511.6345 | 546.9944 | 511.9739
3047.0667 | 525.4707 | 519.8302 | 550.2017 | 511.8313
3048.0667 | 526.2301 | 523.2812 | 559.2282 | 511.6522
3049.0667 | 524.9369 | 525.3959 | 566.6482 | 511.378
3050.0667 | 523.9801 | 524.6351 | 568.2162 | 510.877
3051.0667 | 523.3006 | 530.9088 | 565.0992 | 510.409
3052.0667 | 523.7399 | 529.4721 | 562.8302 | 509.4743
3053.0667 | 525.0425 | 526.77 | 562.1835 | 509.0706
3054.0667 | 525.4553 | 525.0015 | 559.8773 | 507.842
3055.0667 | 524.5859 | 524.4659 | 554.4971 | 507.637
3056.0667 | 524.2457 | 526.4457 | 550.0414 | 506.1396
3057.0667 | 523.8145 | 525.1744 | 546.6894 | 505.8674
3058.0667 | 522.4387 | 525.7228 | 549.4334 | 505.0164
3059.0667 | 521.3741 | 525.3028 | 548.6499 | 503.4371
3060.0667 | 521.1156 | 527.3422 | 546.7787 | 503.3636
3061.0667 | 521.4436 | 527.9213 | 546.5912 | 502.0153
3062.0667 | 518.2972 | 526.0121 | 545.0461 | 501.7813
3063.0667 | 517.4946 | 523.1517 | 547.3238 | 501.7141
3064.0667 | 518.4698 | 520.5281 | 553.525 | 501.4609
3065.0667 | 518.427 | 517.8802 | 560.6154 | 501.0751
3066.0823 | 515.9959 | 515.5194 | 557.9061 | 500.7874
3067.0823 | 514.0522 | 514.595 | 551.9366 | 501.0455
3068.0667 | 511.9737 | 515.3744 | 558.0005 | 500.7344
3069.0667 | 513.8252 | 520.042 | 558.2641 | 500.3496
3070.0667 | 514.5729 | 518.6811 | 556.0961 | 500.8755
3071.0667 | 516.1603 | 518.2862 | 553.5061 | 501.092
3072.0667 | 523.0972 | 520.5602 | 550.9639 | 501.6495
3073.0667 | 519.7755 | 520.7287 | 548.0438 | 501.5372
3074.0667 | 516.4848 | 519.7679 | 544.5232 | 501.5125
3075.0667 | 514.3063 | 520.4542 | 541.2936 | 501.1218
3076.0667 | 512.4533 | 519.8174 | 540.7668 | 501.6019
3077.0667 | 513.1826 | 519.2553 | 544.7602 | 501.6374
3078.0667 | 511.3612 | 517.8341 | 543.5536 | 502.3379
3079.0667 | 512.5331 | 525.7167 | 543.4008 | 501.6911
3080.0667 | 514.4494 | 526.8804 | 543.5025 | 502.7927
3081.0667 | 513.6768 | 524.1042 | 540.8101 | 503.8386
3082.0667 | 514.4695 | 522.2106 | 538.1302 | 504.0518
3083.0667 | 516.5089 | 521.2964 | 537.7594 | 504.8586
3084.0667 | 517.6097 | 519.3392 | 537.7019 | 505.1892
3085.0667 | 517.7227 | 518.8731 | 536.8881 | 505.281
3086.0667 | 516.5957 | 517.2933 | 534.7007 | 505.7463
3087.0667 | 516.7362 | 518.244 | 533.6736 | 505.9695
3088.0667 | 516.1036 | 521.8268 | 533.2289 | 506.1076
3089.0667 | 515.8497 | 521.2436 | 540.2615 | 506.1414
3090.0667 | 516.5976 | 517.7384 | 542.3849 | 506.8306
3091.0667 | 517.8045 | 515.7025 | 541.6145 | 507.4705
3092.0667 | 520.3189 | 514.1004 | 543.4621 | 507.4308
3093.0667 | 523.923 | 512.4544 | 544.4318 | 507.5671
3094.0667 | 528.1575 | 510.6033 | 543.725 | 507.7641
3095.0667 | 528.603 | 512.6205 | 544.2401 | 507.5883
3096.0667 | 525.6839 | 513.3339 | 546.0186 | 507.3721
3097.0667 | 522.7397 | 513.1365 | 547.0351 | 506.8905
3098.0667 | 520.8635 | 513.5554 | 544.2203 | 507.0478
3099.0667 | 520.3534 | 513.5259 | 543.3195 | 506.5055
3100.0667 | 521.1509 | 511.7377 | 541.5733 | 506.9907
3101.0667 | 524.0968 | 509.2179 | 540.8875 | 506.6639
3102.0667 | 526.3574 | 508.2499 | 540.5005 | 507.6231
3103.0667 | 528.4776 | 506.9224 | 538.8801 | 508.4809
3104.0667 | 532.1843 | 507.4304 | 536.1536 | 509.1734
3105.0667 | 535.1758 | 506.7406 | 533.5086 | 509.7954
3106.0667 | 536.6802 | 506.2664 | 532.8662 | 510.5115
3107.0667 | 536.1462 | 506.0969 | 532.5639 | 511.2307
3108.0667 | 535.354 | 506.6937 | 531.8312 | 511.9911
3109.0667 | 533.5619 | 506.2627 | 531.8743 | 512.4563
3110.0667 | 533.5851 | 505.7225 | 534.1131 | 512.9432
3111.0667 | 531.7486 | 506.7783 | 536.022 | 513.3891
3112.0667 | 530.3238 | 505.7774 | 536.0504 | 513.7054
3113.0667 | 531.5374 | 505.3663 | 536.1727 | 512.9723
3114.0667 | 531.6283 | 507.8939 | 537.8061 | 513.5146
3115.0667 | 532.8507 | 507.8546 | 539.5154 | 514.0411
3116.0667 | 533.4652 | 506.3664 | 539.1074 | 513.911
3117.0667 | 534.2937 | 506.6021 | 541.2766 | 514.6375
3118.0667 | 534.3589 | 506.911 | 542.0786 | 514.1629
3119.0667 | 533.5792 | 506.2365 | 543.1732 | 514.6313
3120.0667 | 531.7236 | 506.4761 | 544.87 | 514.4798
3121.0667 | 531.4774 | 506.3953 | 546.7616 | 514.3046
3122.0667 | 531.0553 | 507.2967 | 555.8843 | 514.8665
3123.0667 | 532.7059 | 508.1755 | 557.0866 | 515.6186
3124.0667 | 533.1285 | 511.5556 | 559.5322 | 515.8287
3125.0667 | 528.9018 | 515.4001 | 558.455 | 515.7088
3126.0667 | 525.6641 | 518.5438 | 555.9615 | 516.0779
3127.0667 | 521.7002 | 519.3299 | 553.7747 | 515.3056
3128.0667 | 520.5347 | 520.4627 | 552.3958 | 514.8513
3129.0667 | 520.6803 | 520.6036 | 552.6341 | 515.174
3130.0667 | 519.2553 | 523.0043 | 552.2036 | 515.1677
3131.0667 | 519.0678 | 523.535 | 551.1001 | 515.2091
3132.0667 | 519.3814 | 523.2523 | 549.748 | 515.5782
3133.0667 | 521.3809 | 522.6387 | 550.7408 | 516.2533
3134.0667 | 522.0951 | 527.4286 | 554.0131 | 516.5464
3135.0667 | 519.9134 | 529.928 | 553.4172 | 517.3023
3136.0667 | 518.0364 | 530.823 | 553.7599 | 517.8758
3137.0667 | 516.8368 | 530.5514 | 551.0923 | 518.2756
3138.0667 | 515.8857 | 531.5933 | 549.6303 | 518.5699
3139.0667 | 517.8094 | 531.0559 | 548.4163 | 518.7302
3140.0667 | 519.1386 | 531.0704 | 550.097 | 518.914
3141.0667 | 520.0042 | 531.1446 | 550.9793 | 519.446
3142.0667 | 518.8187 | 529.8415 | 549.0173 | 520.0082
3143.0667 | 517.7939 | 530.589 | 549.0007 | 520.6011
3144.0667 | 516.7274 | 529.3942 | 548.8588 | 521.2117
3145.0667 | 517.0266 | 527.672 | 548.6562 | 521.8237
3146.0667 | 517.991 | 527.5922 | 547.3456 | 522.3479
3147.0667 | 519.2256 | 530.6661 | 547.2253 | 522.9178
3148.0667 | 519.8091 | 532.6393 | 546.7175 | 523.5287
3149.0667 | 519.1264 | 530.5835 | 544.8774 | 524.0107
3150.0667 | 518.4169 | 529.3979 | 543.6415 | 524.401
3151.0667 | 517.528 | 529.0904 | 544.1542 | 524.794
3152.0667 | 517.1745 | 531.0947 | 544.9948 | 525.2649
3153.0667 | 518.868 | 530.1906 | 546.5923 | 525.7577
3154.0667 | 520.0932 | 532.1612 | 546.9355 | 526.3118
3155.0667 | 521.3396 | 532.2071 | 546.8908 | 526.9291
3156.0667 | 521.8835 | 535.133 | 547.5794 | 527.5358
3157.0667 | 522.0867 | 536.7797 | 547.8614 | 528.1108
3158.0667 | 521.2036 | 536.1037 | 548.5809 | 528.568
3159.0667 | 521.0314 | 534.1181 | 546.5916 | 528.9621
3160.0667 | 520.5505 | 533.372 | 544.8239 | 529.4618
3161.0667 | 519.316 | 531.9162 | 542.837 | 530.043
3162.0667 | 519.9647 | 530.5606 | 541.72 | 530.5809
3163.0667 | 520.7824 | 530.6304 | 541.7499 | 531.134
3164.0667 | 520.8504 | 531.0762 | 541.8548 | 531.739
3165.0667 | 521.4033 | 529.938 | 542.5851 | 532.3745
3166.0667 | 523.9903 | 530.8171 | 543.619 | 533.1587
3167.0667 | 522.8922 | 530.1493 | 544.8034 | 534.0392
3168.0667 | 523.3285 | 528.7688 | 542.8908 | 534.8703
3169.0667 | 523.8233 | 528.0816 | 542.742 | 535.6146
3170.0667 | 524.1688 | 527.0339 | 541.6901 | 536.1795
3171.0667 | 525.1756 | 525.5252 | 541.4118 | 536.6021
3172.0667 | 525.7009 | 524.648 | 541.2335 | 536.9982
3173.0667 | 526.78 | 523.0697 | 540.5827 | 537.3646
3174.0667 | 527.9603 | 523.3312 | 539.6835 | 537.6278
3175.0667 | 528.0669 | 522.7656 | 538.9815 | 537.8872
3176.0667 | 529.7238 | 521.6698 | 538.415 | 538.3013
3177.0667 | 533.2932 | 520.4238 | 538.2506 | 538.7729
3178.0667 | 535.6005 | 519.549 | 540.7801 | 539.0572
3179.0667 | 535.0056 | 519.0576 | 540.9326 | 539.2396
3180.0667 | 534.7664 | 520.3256 | 541.1403 | 539.6722
3181.0667 | 534.6962 | 520.2199 | 540.5283 | 540.2151
3182.0667 | 535.0124 | 519.2904 | 540.4145 | 540.8012
3183.0667 | 536.3099 | 519.2398 | 541.6981 | 541.294
3184.0667 | 533.8833 | 520.7441 | 542.7283 | 541.6591
3185.0667 | 530.7195 | 519.4019 | 540.356 | 542.0597
3186.0667 | 530.3003 | 518.234 | 538.6779 | 542.4193
3187.0667 | 531.8918 | 516.9467 | 538.2732 | 542.7463
3188.0667 | 533.0552 | 514.207 | 538.1025 | 543.0997
3189.0667 | 534.8416 | 512.9791 | 537.5027 | 543.3257
3190.0667 | 535.7201 | 512.7355 | 537.9756 | 543.5993
3191.0667 | 537.5538 | 512.0577 | 538.5062 | 543.9239
3192.0667 | 538.8872 | 510.3692 | 539.2104 | 544.0735
3193.0667 | 540.4732 | 508.2984 | 541.5768 | 544.0249
3194.0667 | 541.2869 | 509.0858 | 543.8168 | 544.0848
3195.0667 | 539.5334 | 509.2753 | 544.2708 | 544.136
3196.0667 | 537.3224 | 511.9705 | 545.1667 | 544.0035
3197.0667 | 535.6014 | 513.5682 | 543.7175 | 543.8199
3198.0667 | 534.9177 | 513.3692 | 543.3559 | 543.8134
3199.0667 | 534.0882 | 514.5356 | 543.3901 | 543.8975
3200.0667 | 532.58 | 515.101 | 542.4106 | 543.9509
3201.0667 | 532.7033 | 514.2665 | 541.3925 | 544.2731
3202.0667 | 533.4992 | 512.4705 | 540.5084 | 544.6654
3203.0667 | 534.2381 | 511.8892 | 538.5313 | 545.0429
3204.0667 | 536.4344 | 510.7718 | 537.9013 | 545.3874
3205.0667 | 536.6001 | 509.3096 | 538.9511 | 545.9044
3206.0667 | 537.0436 | 508.5581 | 538.8043 | 546.5069
3207.0667 | 535.8465 | 509.3374 | 539.8231 | 546.9134
3208.0667 | 535.3745 | 510.5423 | 541.7307 | 547.0967
3209.0667 | 533.1833 | 511.0855 | 542.3697 | 547.1358
3210.0667 | 530.4941 | 512.1894 | 543.5467 | 546.9648
3211.0667 | 530.8155 | 513.4551 | 544.8568 | 546.8628
3212.0667 | 530.4733 | 513.0176 | 544.0206 | 546.7937
3213.0667 | 529.1798 | 513.218 | 543.0631 | 546.8594
3214.0667 | 529.6911 | 514.8058 | 541.796 | 546.8776
3215.0667 | 529.0247 | 515.2114 | 541.5872 | 546.9159
3216.0667 | 528.8084 | 516.3667 | 542.857 | 546.8543
3217.0667 | 529.1297 | 517.8415 | 543.3005 | 546.7152
3218.0667 | 527.7737 | 518.988 | 544.2856 | 546.4928
3219.0667 | 526.8937 | 521.0761 | 543.5047 | 546.228
3220.0667 | 524.6319 | 521.6663 | 543.5346 | 545.9829
3221.0667 | 521.9888 | 524.2794 | 542.5515 | 545.7074
3222.0667 | 519.7382 | 525.6645 | 540.1365 | 545.2666
3223.0667 | 518.8735 | 527.7399 | 540.4146 | 544.7007
3224.0667 | 519.2687 | 526.9993 | 540.569 | 544.1188
3225.0667 | 522.7119 | 526.6185 | 539.9024 | 543.5698
3226.0667 | 525.738 | 526.3291 | 542.7365 | 543.1717
3227.0667 | 527.3331 | 525.6744 | 544.602 | 543.0297
3228.0667 | 528.4993 | 524.866 | 545.9285 | 543.0647
3229.0667 | 528.6478 | 525.3816 | 545.9848 | 543.0429
3230.0667 | 527.9163 | 528.4352 | 545.9479 | 543.0136
3231.0667 | 528.1928 | 530.9323 | 546.5988 | 542.9149
3232.0667 | 527.1967 | 531.4431 | 546.2214 | 542.8662
3233.0667 | 526.0733 | 533.1599 | 544.392 | 542.6512
3234.0667 | 524.9342 | 532.3545 | 542.8501 | 542.1986
3235.0667 | 525.0188 | 530.5279 | 540.6732 | 541.6602
3236.0667 | 527.3617 | 529.9276 | 544.5339 | 541.3421
3237.0667 | 529.5226 | 528.9761 | 547.3718 | 541.2059
3238.0667 | 530.9195 | 527.4441 | 550.0286 | 541.1645
3239.0667 | 530.9022 | 526.8018 | 549.3661 | 540.9889
3240.0667 | 530.6348 | 526.1497 | 549.9145 | 540.6497
3241.0667 | 532.3107 | 524.3891 | 548.3732 | 540.4468
3242.0667 | 532.518 | 523.4074 | 547.1448 | 540.4688
3243.0667 | 534.8104 | 522.2895 | 546.4104 | 540.5813
3244.0667 | 538.7172 | 521.902 | 546.2116 | 540.9418
3245.0667 | 540.6826 | 520.9107 | 547.3561 | 541.363
3246.0667 | 541.42 | 519.9829 | 546.699 | 541.6711
3247.0667 | 541.2742 | 521.5078 | 545.7144 | 541.6488
3248.0667 | 539.7694 | 520.7389 | 546.7096 | 541.2876
3249.0667 | 540.0527 | 518.9406 | 546.6982 | 540.5978
3250.0667 | 541.0457 | 517.3038 | 545.9237 | 539.7747
3251.0667 | 543.6709 | 516.1538 | 545.8225 | 538.928
3252.0667 | 546.501 | 514.6949 | 545.928 | 538.1863
3253.0667 | 547.027 | 514.1659 | 545.4189 | 537.5657
3254.0667 | 547.3313 | 513.2508 | 544.6304 | 536.9774
3255.0667 | 547.4618 | 511.7148 | 544.9671 | 536.3595
3256.0667 | 545.1087 | 512.5085 | 544.6516 | 535.6934
3257.0667 | 542.4914 | 512.8976 | 543.0332 | 535.0365
3258.0667 | 541.5332 | 511.9108 | 540.9504 | 534.368
3259.0667 | 542.0526 | 511.4984 | 541.4668 | 533.7858
3260.0667 | 542.0548 | 511.3034 | 543.5562 | 533.377
3261.0667 | 540.9856 | 510.319 | 542.4148 | 532.9211
3262.0667 | 541.7898 | 510.4349 | 542.4051 | 532.3776
3263.0667 | 542.343 | 511.4083 | 542.969 | 531.775
3264.0667 | 542.4197 | 511.5268 | 542.6484 | 531.2572
3265.0667 | 544.2318 | 511.4399 | 541.7953 | 530.8548
3266.0667 | 544.3635 | 510.4773 | 540.6817 | 530.6158
3267.0667 | 543.0353 | 509.9318 | 540.4452 | 530.4052
3268.0667 | 541.3337 | 509.639 | 540.9562 | 530.3915
3269.0667 | 540.6366 | 509.2597 | 541.705 | 530.4997
3270.0667 | 539.6794 | 508.6212 | 540.4711 | 530.6567
3271.0667 | 541.4153 | 508.3235 | 541.1189 | 530.9135
3272.0667 | 542.3779 | 507.8255 | 543.4726 | 531.1534
3273.0667 | 543.4252 | 508.4 | 546.8836 | 531.3545
3274.0667 | 542.8023 | 508.5509 | 546.7578 | 531.6275
3275.0667 | 541.6112 | 509.2951 | 544.8649 | 531.771
3276.0667 | 540.2059 | 512.9626 | 542.7615 | 531.6957
3277.0667 | 537.2653 | 514.0577 | 541.0982 | 531.5356
3278.0667 | 537.4808 | 514.1783 | 540.231 | 531.5582
3279.0667 | 538.1734 | 514.1103 | 540.4249 | 531.8596
3280.0667 | 538.9776 | 513.2341 | 541.2485 | 532.2543
3281.0667 | 538.6412 | 512.5753 | 539.6341 | 532.2801
3282.0667 | 537.7501 | 512.3174 | 539.0157 | 532.0506
3283.0667 | 536.3005 | 513.2102 | 538.2441 | 531.6478
3284.0667 | 534.563 | 514.4751 | 539.4844 | 531.1328
3285.0667 | 534.305 | 515.8407 | 539.1377 | 530.5891
3286.0667 | 533.5937 | 515.4937 | 538.2677 | 530.0573
3287.0667 | 534.7777 | 515.5323 | 537.6051 | 529.4668
3288.0667 | 534.3665 | 516.0659 | 538.3564 | 528.9571
3289.0667 | 534.3829 | 514.241 | 536.8756 | 528.4175
3290.0667 | 534.3361 | 514.0273 | 536.0972 | 527.9369
3291.0667 | 536.1081 | 515.0114 | 536.1565 | 527.6992
3292.0667 | 537.5612 | 514.4054 | 537.0831 | 527.4402
3293.0667 | 536.7537 | 512.5162 | 536.6215 | 527.1714
3294.0667 | 536.1321 | 512.3388 | 535.1337 | 526.8592
3295.0667 | 535.2993 | 515.074 | 535.8786 | 526.3911
3296.0667 | 533.638 | 517.0885 | 535.5147 | 525.8613
3297.0667 | 532.7121 | 517.6741 | 534.4021 | 525.4011
3298.0667 | 531.7838 | 516.5505 | 533.3427 | 525.0243
3299.0667 | 531.4845 | 515.2472 | 533.1295 | 524.6756
3300.0667 | 531.1331 | 515.4839 | 534.7558 | 524.3318
3301.0667 | 528.2235 | 516.1082 | 534.6714 | 523.9461
3302.0667 | 527.7245 | 517.2907 | 533.6756 | 523.5045
3303.0667 | 528.0802 | 517.9878 | 533.7935 | 523.0071
3304.0667 | 528.9796 | 516.9434 | 535.3283 | 522.5439
3305.0667 | 529.3866 | 515.8095 | 533.7334 | 522.2283
3306.0667 | 527.883 | 515.7182 | 532.8149 | 522.1117
3307.0667 | 528.2894 | 515.0289 | 532.2021 | 522.0133
3308.0667 | 529.3666 | 513.4577 | 530.6317 | 521.944
3309.0667 | 530.9406 | 512.6432 | 531.325 | 521.9281
3310.0667 | 530.3705 | 512.8778 | 531.2786 | 521.8512
3311.0667 | 530.275 | 512.3138 | 530.5057 | 521.6096
3312.0667 | 527.7245 | 512.0141 | 530.9876 | 521.3034
3313.0667 | 525.6565 | 511.4722 | 529.6577 | 520.9639
3314.0667 | 525.0623 | 514.1175 | 529.7141 | 520.6575
3315.0667 | 523.9969 | 516.0437 | 529.6962 | 520.3107
3316.0667 | 523.4828 | 516.542 | 530.4179 | 519.8889
3317.0667 | 523.8378 | 515.2038 | 531.3858 | 519.5883
3318.0667 | 524.111 | 516.11 | 529.3596 | 519.6726
3319.0667 | 522.8257 | 516.3417 | 528.028 | 519.7978
3320.0667 | 523.1604 | 516.8301 | 528.1357 | 519.9969
3321.0667 | 521.401 | 517.5739 | 528.3532 | 520.3242
3322.0667 | 521.5516 | 517.2112 | 527.1288 | 520.7197
3323.0667 | 523.9798 | 515.6349 | 526.0211 | 520.9976
3324.0667 | 527.8195 | 513.81 | 527.4114 | 521.4249
3325.0667 | 532.0807 | 512.2688 | 528.9988 | 522.1839
3326.0667 | 532.9019 | 511.5133 | 529.6358 | 522.8803
3327.0667 | 532.4444 | 511.1676 | 529.8704 | 523.512
3328.0667 | 530.9992 | 510.9827 | 530.6301 | 523.8803
3329.0667 | 530.6406 | 511.4148 | 531.1004 | 524.1234
3330.0667 | 531.5424 | 510.7027 | 531.2385 | 524.3098
3331.0667 | 532.4411 | 510.6505 | 532.8451 | 524.808
3332.0667 | 532.3019 | 511.7481 | 534.6897 | 525.3734
3333.0667 | 531.2041 | 513.5623 | 534.9224 | 525.7314
3334.0667 | 530.6116 | 514.0947 | 534.4393 | 525.8542
3335.0667 | 528.2367 | 514.0191 | 533.4083 | 525.9778
3336.0667 | 527.5727 | 513.5879 | 533.3147 | 526.1032
3337.0667 | 528.5443 | 513.4035 | 534.6484 | 526.4223
3338.0667 | 529.3965 | 513.5524 | 533.506 | 526.6931
3339.0667 | 528.9617 | 512.6881 | 533.7215 | 526.7975
3340.0667 | 528.6472 | 511.3938 | 533.5194 | 526.6979
3341.0667 | 530.9044 | 511.2618 | 535.9208 | 526.4353
3342.0667 | 531.638 | 510.9848 | 535.3716 | 526.2463
3343.0667 | 530.7459 | 511.9009 | 534.47 | 526.0645
3344.0667 | 531.6535 | 512.7823 | 533.7119 | 525.835
3345.0667 | 531.7177 | 512.5531 | 534.1106 | 525.4575
3346.0667 | 530.9869 | 512.1139 | 533.8568 | 525.0156
3347.0667 | 530.0147 | 513.0929 | 533.159 | 524.5524
3348.0667 | 529.0409 | 513.3269 | 531.8261 | 524.1469
3349.0667 | 527.9596 | 513.2525 | 531.3584 | 523.696
3350.0667 | 526.9653 | 512.7986 | 530.96 | 523.1712
3351.0667 | 526.6416 | 512.0762 | 530.1917 | 522.6478
3352.0667 | 527.9427 | 512.4615 | 530.4069 | 522.1144
3353.0667 | 527.6973 | 511.2616 | 529.9266 | 521.658
3354.0667 | 527.8496 | 509.9831 | 530.0159 | 521.3331
3355.0667 | 527.812 | 509.7025 | 530.4179 | 521.0919
3356.0667 | 527.6772 | 510.8556 | 529.5415 | 520.8324
3357.0667 | 528.792 | 510.1244 | 529.5315 | 520.5066
3358.0667 | 526.7982 | 510.5045 | 529.0262 | 520.1278
3359.0667 | 525.0023 | 510.4842 | 528.0469 | 519.6417
3360.0667 | 522.2265 | 509.9612 | 527.8452 | 519.1821
3361.0667 | 522.2777 | 509.4393 | 527.0188 | 518.6998
3362.0667 | 523.2819 | 508.5835 | 527.1894 | 518.1855
3363.0667 | 525.0483 | 507.5323 | 527.2538 | 517.8884
3364.0667 | 526.8856 | 506.779 | 527.6458 | 517.7367
3365.0667 | 528.3757 | 506.8512 | 527.7752 | 517.5186
3366.0667 | 529.3714 | 506.4351 | 529.0534 | 517.243
3367.0667 | 529.5933 | 506.2664 | 529.2901 | 517.0714
3368.0667 | 527.1455 | 506.4269 | 528.9048 | 516.974
3369.0667 | 526.7435 | 507.8644 | 527.6047 | 516.8857
3370.0667 | 525.5855 | 507.9754 | 527.4298 | 516.777