## Test Conditions
DESIREE-FIRE Intermediate Scale Test 4 - Circuit Simulator Data Only
Test Date: | 2009-11-12
DCSim DAQ Start Time | 10:31
DCSim Time for Synchronization | 10:32
Heat Source Synchronization | 0:01 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:31
Fire Time | 11:20
Offset | 0:49 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2940 | seconds
Heat Source Offset | 0:49 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2935 | seconds
Heat Source Stop Time | 13:12
Test Duration | 1:52 | hours:minutes:seconds
| 6720 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
Intercable Configuration | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 1 which is defined as "B Position - Middle" in the Temperature Data File respresents the temperature in the center of the cable tray.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.90625 | 121.8338 | -61.2488 | 60.3333 | 0.11727 | 0.046477 | -0.030314 | -0.029595 | 0.004219 | 0.085583 | -0.039826 | 60.2322 | 60.2632 | 60.191 | 60.1262 | 61.2721 | 61.3144 | 60.9598 | 61.2482 | 61.3661 | 61.2953 | 61.2185 | 61.2192 | 61.253 | 61.3344 | 61.209 | 60.2734 | 60.3044 | 60.2322 | 60.1674 | 61.3133 | 61.3556 | 61.001 | 61.2894 | -1.0399 | -0.72757 | -1.0811 | -0.76879
0.78125 | 121.9116 | -61.1664 | 60.3561 | 0.11269 | 0.046477 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.044405 | 60.2414 | 60.2632 | 60.2002 | 60.1216 | 61.2721 | 61.3144 | 60.9598 | 61.2482 | 61.2791 | 61.2129 | 61.1361 | 61.1368 | 61.1569 | 61.252 | 61.122 | 60.2826 | 60.3044 | 60.2414 | 60.1628 | 61.3133 | 61.3556 | 61.001 | 61.2894 | -1.0308 | -0.71841 | -1.072 | -0.75963
2.5312 | 121.9208 | -61.2762 | 60.2692 | 0.10812 | 0.037319 | -0.025735 | -0.029595 | -0.004937 | 0.081005 | -0.035248 | 60.246 | 60.2678 | 60.2002 | 60.1216 | 61.2721 | 61.3098 | 60.9552 | 61.2528 | 61.3844 | 61.3136 | 61.2505 | 61.2467 | 61.2713 | 61.3573 | 61.241 | 60.2872 | 60.309 | 60.2414 | 60.1628 | 61.3133 | 61.351 | 60.9964 | 61.294 | -1.0262 | -0.70926 | -1.072 | -0.75505
4.2188 | 121.9208 | -61.171 | 60.3882 | 0.11727 | 0.037319 | -0.034893 | -0.029595 | -0.004937 | 0.076426 | -0.044405 | 60.2322 | 60.2678 | 60.2002 | 60.1216 | 61.2767 | 61.3189 | 60.969 | 61.2528 | 61.2882 | 61.2083 | 61.1361 | 61.1414 | 61.166 | 61.2474 | 61.1266 | 60.2734 | 60.309 | 60.2414 | 60.1628 | 61.3179 | 61.3601 | 61.0102 | 61.294 | -1.0445 | -0.73673 | -1.0766 | -0.76879
5.9688 | 121.7697 | -61.3037 | 60.3195 | 0.11727 | 0.046477 | -0.021157 | -0.020438 | -0.004937 | 0.081005 | -0.039826 | 60.246 | 60.2632 | 60.2002 | 60.1262 | 61.2676 | 61.3098 | 60.9415 | 61.2482 | 61.421 | 61.3502 | 61.2826 | 61.2833 | 61.2988 | 61.3847 | 61.2639 | 60.2872 | 60.3044 | 60.2414 | 60.1674 | 61.3088 | 61.351 | 60.9827 | 61.2894 | -1.0216 | -0.69552 | -1.0674 | -0.74132
7.7188 | 121.8796 | -61.2167 | 60.3149 | 0.11269 | 0.037319 | -0.025735 | -0.034174 | -0.009515 | 0.071848 | -0.048983 | 60.2414 | 60.2586 | 60.1956 | 60.1262 | 61.2767 | 61.3189 | 60.9552 | 61.2528 | 61.3294 | 61.2541 | 61.191 | 61.1826 | 61.2072 | 61.2886 | 61.1678 | 60.2826 | 60.2998 | 60.2368 | 60.1674 | 61.3179 | 61.3601 | 60.9964 | 61.294 | -1.0353 | -0.71383 | -1.0811 | -0.75963
9.3906 | 121.9299 | -61.1526 | 60.3745 | 0.11727 | 0.046477 | -0.030314 | -0.034174 | -0.009515 | 0.076426 | -0.048983 | 60.2322 | 60.2632 | 60.2047 | 60.1262 | 61.2813 | 61.3189 | 60.9644 | 61.2436 | 61.2699 | 61.1991 | 61.1223 | 61.1185 | 61.1431 | 61.2291 | 61.1037 | 60.2734 | 60.3044 | 60.2459 | 60.1674 | 61.3225 | 61.3601 | 61.0056 | 61.2848 | -1.0491 | -0.73215 | -1.0766 | -0.75963
11.1406 | 121.8979 | -61.2808 | 60.2463 | 0.12185 | 0.037319 | -0.021157 | -0.034174 | -0.004937 | 0.085583 | -0.044405 | 60.2368 | 60.2769 | 60.2002 | 60.1171 | 61.2721 | 61.3189 | 60.9369 | 61.2482 | 61.4027 | 61.3181 | 61.2597 | 61.2466 | 61.2759 | 61.3664 | 61.2364 | 60.278 | 60.3181 | 60.2414 | 60.1583 | 61.3133 | 61.3601 | 60.9781 | 61.2894 | -1.0353 | -0.7001 | -1.072 | -0.73674
12.8281 | 121.8842 | -61.235 | 60.3378 | 0.11269 | 0.037319 | -0.025735 | -0.038752 | -0.009515 | 0.076426 | -0.035248 | 60.2368 | 60.2678 | 60.2002 | 60.1262 | 61.2813 | 61.3189 | 60.9369 | 61.2482 | 61.3477 | 61.2724 | 61.2093 | 61.1963 | 61.2255 | 61.3115 | 61.1998 | 60.278 | 60.309 | 60.2414 | 60.1674 | 61.3225 | 61.3601 | 60.9781 | 61.2894 | -1.0445 | -0.7001 | -1.0811 | -0.73674
14.5625 | 121.8658 | -61.2076 | 60.347 | 0.11269 | 0.041898 | -0.025735 | -0.038752 | -0.009515 | 0.076426 | -0.035248 | 60.2414 | 60.2586 | 60.2002 | 60.1216 | 61.2813 | 61.3235 | 60.9644 | 61.2436 | 61.3203 | 61.2495 | 61.1818 | 61.1688 | 61.1981 | 61.284 | 61.1723 | 60.2826 | 60.2998 | 60.2414 | 60.1628 | 61.3225 | 61.3647 | 61.0056 | 61.2848 | -1.0399 | -0.72299 | -1.0811 | -0.76421
16.2969 | 121.8246 | -61.29 | 60.3012 | 0.12185 | 0.041898 | -0.025735 | -0.025017 | -0.004937 | 0.085583 | -0.044405 | 60.2414 | 60.2678 | 60.191 | 60.1308 | 61.2721 | 61.3144 | 60.9323 | 61.2436 | 61.4118 | 61.3319 | 61.2642 | 61.265 | 61.285 | 61.3756 | 61.2456 | 60.2826 | 60.309 | 60.2322 | 60.172 | 61.3133 | 61.3556 | 60.9735 | 61.2848 | -1.0308 | -0.69094 | -1.0811 | -0.74132
18.0625 | 121.8979 | -61.2167 | 60.3424 | 0.11727 | 0.037319 | -0.021157 | -0.034174 | -0.009515 | 0.081005 | -0.044405 | 60.2414 | 60.2723 | 60.2047 | 60.1216 | 61.2767 | 61.3189 | 60.9461 | 61.2528 | 61.334 | 61.2541 | 61.1956 | 61.1826 | 61.2072 | 61.2977 | 61.1723 | 60.2826 | 60.3135 | 60.2459 | 60.1628 | 61.3179 | 61.3601 | 60.9873 | 61.294 | -1.0353 | -0.70468 | -1.072 | -0.74132
19.7344 | 121.8384 | -61.2717 | 60.3058 | 0.12185 | 0.037319 | -0.021157 | -0.029595 | -0.004937 | 0.076426 | -0.035248 | 60.2368 | 60.2678 | 60.2047 | 60.14 | 61.2813 | 61.3098 | 60.9323 | 61.2482 | 61.3935 | 61.309 | 61.2505 | 61.2421 | 61.2667 | 61.3481 | 61.2364 | 60.278 | 60.309 | 60.2459 | 60.1812 | 61.3225 | 61.351 | 60.9735 | 61.2894 | -1.0445 | -0.69552 | -1.0766 | -0.72758
21.4688 | 121.8842 | -61.203 | 60.3699 | 0.10812 | 0.037319 | -0.025735 | -0.034174 | -0.009515 | 0.076426 | -0.035248 | 60.246 | 60.2678 | 60.1956 | 60.1354 | 61.2813 | 61.3144 | 60.9369 | 61.2482 | 61.3111 | 61.2403 | 61.1773 | 61.1688 | 61.1935 | 61.2794 | 61.1678 | 60.2872 | 60.309 | 60.2368 | 60.1766 | 61.3225 | 61.3556 | 60.9781 | 61.2894 | -1.0353 | -0.69094 | -1.0857 | -0.74132
23.2344 | 121.7926 | -61.3266 | 60.3195 | 0.11727 | 0.051056 | -0.021157 | -0.020438 | -0.000359 | 0.085583 | -0.039826 | 60.2322 | 60.2678 | 60.2002 | 60.1262 | 61.2767 | 61.3098 | 60.9369 | 61.2528 | 61.4439 | 61.3777 | 61.3054 | 61.3062 | 61.3262 | 61.4122 | 61.2868 | 60.2734 | 60.309 | 60.2414 | 60.1674 | 61.3179 | 61.351 | 60.9781 | 61.294 | -1.0445 | -0.70468 | -1.0766 | -0.73674
24.9688 | 121.7926 | -61.3266 | 60.3012 | 0.11269 | 0.041898 | -0.021157 | -0.034174 | -0.009515 | 0.081005 | -0.039826 | 60.2368 | 60.2632 | 60.2002 | 60.1354 | 61.2721 | 61.3144 | 60.9186 | 61.2482 | 61.4393 | 61.3685 | 61.3054 | 61.2924 | 61.3171 | 61.4076 | 61.2868 | 60.278 | 60.3044 | 60.2414 | 60.1766 | 61.3133 | 61.3556 | 60.9598 | 61.2894 | -1.0353 | -0.68179 | -1.072 | -0.71842
26.7031 | 121.7834 | -61.3129 | 60.3149 | 0.11727 | 0.046477 | -0.021157 | -0.029595 | -0.014093 | 0.085583 | -0.044405 | 60.246 | 60.2678 | 60.2047 | 60.1262 | 61.2813 | 61.3144 | 60.9552 | 61.2436 | 61.4301 | 61.3593 | 61.2917 | 61.2833 | 61.2988 | 61.3984 | 61.2685 | 60.2872 | 60.309 | 60.2459 | 60.1674 | 61.3225 | 61.3556 | 60.9964 | 61.2848 | -1.0353 | -0.70926 | -1.0766 | -0.75047
28.4531 | 121.907 | -61.2717 | 60.2829 | 0.11269 | 0.046477 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.044405 | 60.2414 | 60.2632 | 60.2002 | 60.1262 | 61.2721 | 61.3189 | 60.9232 | 61.2482 | 61.3844 | 61.3181 | 61.2459 | 61.2467 | 61.2622 | 61.3573 | 61.2273 | 60.2826 | 60.3044 | 60.2414 | 60.1674 | 61.3133 | 61.3601 | 60.9644 | 61.2894 | -1.0308 | -0.68179 | -1.072 | -0.723
30.2031 | 121.8887 | -61.2396 | 60.347 | 0.11269 | 0.037319 | -0.021157 | -0.034174 | -0.014093 | 0.076426 | -0.044405 | 60.246 | 60.2678 | 60.1956 | 60.1262 | 61.2859 | 61.3144 | 60.9323 | 61.2436 | 61.3523 | 61.2769 | 61.2185 | 61.2054 | 61.2255 | 61.316 | 61.1952 | 60.2872 | 60.309 | 60.2368 | 60.1674 | 61.3271 | 61.3556 | 60.9735 | 61.2848 | -1.0399 | -0.68636 | -1.0903 | -0.73674
31.8906 | 121.8521 | -61.2579 | 60.3378 | 0.11269 | 0.046477 | -0.025735 | -0.029595 | -0.004937 | 0.085583 | -0.035248 | 60.246 | 60.2678 | 60.2047 | 60.1262 | 61.2721 | 61.3189 | 60.9323 | 61.2482 | 61.3706 | 61.3044 | 61.2322 | 61.2283 | 61.253 | 61.3435 | 61.2227 | 60.2872 | 60.309 | 60.2459 | 60.1674 | 61.3133 | 61.3601 | 60.9735 | 61.2894 | -1.0262 | -0.68636 | -1.0674 | -0.72758
33.6406 | 121.8979 | -61.2625 | 60.2921 | 0.10812 | 0.041898 | -0.025735 | -0.029595 | -0.009515 | 0.090161 | -0.039826 | 60.2414 | 60.2632 | 60.1956 | 60.1216 | 61.2721 | 61.3235 | 60.9323 | 61.2482 | 61.3706 | 61.3044 | 61.2368 | 61.2329 | 61.253 | 61.3527 | 61.2227 | 60.2826 | 60.3044 | 60.2368 | 60.1628 | 61.3133 | 61.3647 | 60.9735 | 61.2894 | -1.0308 | -0.69094 | -1.0766 | -0.73674
35.3281 | 121.907 | -61.1984 | 60.3607 | 0.11727 | 0.041898 | -0.025735 | -0.034174 | -0.014093 | 0.085583 | -0.044405 | 60.2414 | 60.2678 | 60.2002 | 60.1171 | 61.2813 | 61.3144 | 60.9278 | 61.2528 | 61.3157 | 61.2403 | 61.1727 | 61.1643 | 61.1843 | 61.284 | 61.154 | 60.2826 | 60.309 | 60.2414 | 60.1583 | 61.3225 | 61.3556 | 60.9689 | 61.294 | -1.0399 | -0.68636 | -1.0811 | -0.72758
37.0625 | 121.8887 | -61.203 | 60.3516 | 0.11727 | 0.041898 | -0.034893 | -0.038752 | -0.009515 | 0.076426 | -0.039826 | 60.246 | 60.2632 | 60.1956 | 60.1216 | 61.2721 | 61.3144 | 60.9278 | 61.2482 | 61.3203 | 61.2449 | 61.1681 | 61.1643 | 61.1935 | 61.2794 | 61.1632 | 60.2872 | 60.3044 | 60.2368 | 60.1628 | 61.3133 | 61.3556 | 60.9689 | 61.2894 | -1.0262 | -0.68179 | -1.0766 | -0.73216
38.8125 | 121.8475 | -61.2579 | 60.347 | 0.12643 | 0.046477 | -0.025735 | -0.034174 | -0.009515 | 0.081005 | -0.039826 | 60.2414 | 60.2632 | 60.2047 | 60.1308 | 61.2767 | 61.3189 | 60.9232 | 61.2436 | 61.3844 | 61.3044 | 61.2322 | 61.2238 | 61.2484 | 61.3389 | 61.2181 | 60.2826 | 60.3044 | 60.2459 | 60.172 | 61.3179 | 61.3601 | 60.9644 | 61.2848 | -1.0353 | -0.68179 | -1.072 | -0.71842
40.5625 | 121.7834 | -61.2442 | 60.4019 | 0.12185 | 0.046477 | -0.021157 | -0.034174 | -0.004937 | 0.090161 | -0.039826 | 60.2414 | 60.2586 | 60.2002 | 60.1354 | 61.2767 | 61.3144 | 60.9278 | 61.2482 | 61.3661 | 61.2907 | 61.223 | 61.21 | 61.2393 | 61.3344 | 61.2044 | 60.2826 | 60.2998 | 60.2414 | 60.1766 | 61.3179 | 61.3556 | 60.9689 | 61.2894 | -1.0353 | -0.68636 | -1.0766 | -0.72758
42.25 | 121.788 | -61.2991 | 60.2783 | 0.11727 | 0.046477 | -0.021157 | -0.020438 | -0.000359 | 0.081005 | -0.035248 | 60.246 | 60.2678 | 60.2047 | 60.1262 | 61.2767 | 61.3189 | 60.9186 | 61.2528 | 61.4164 | 61.3456 | 61.278 | 61.2787 | 61.2988 | 61.3801 | 61.2639 | 60.2872 | 60.309 | 60.2459 | 60.1674 | 61.3179 | 61.3601 | 60.9598 | 61.294 | -1.0308 | -0.67263 | -1.072 | -0.71384
44 | 121.907 | -61.1938 | 60.3836 | 0.11727 | 0.046477 | -0.030314 | -0.029595 | -0.009515 | 0.081005 | -0.044405 | 60.2414 | 60.2678 | 60.2047 | 60.1216 | 61.2767 | 61.3235 | 60.9278 | 61.2574 | 61.3111 | 61.2403 | 61.1635 | 61.1643 | 61.1843 | 61.2749 | 61.1494 | 60.2826 | 60.309 | 60.2459 | 60.1628 | 61.3179 | 61.3647 | 60.9689 | 61.2986 | -1.0353 | -0.68636 | -1.072 | -0.723
45.7344 | 121.9116 | -61.1755 | 60.3516 | 0.12185 | 0.03274 | -0.034893 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.2414 | 60.2632 | 60.2002 | 60.1308 | 61.2813 | 61.3098 | 60.9323 | 61.2482 | 61.2974 | 61.2083 | 61.1406 | 61.1414 | 61.166 | 61.2611 | 61.1357 | 60.2826 | 60.3044 | 60.2414 | 60.172 | 61.3225 | 61.351 | 60.9735 | 61.2894 | -1.0399 | -0.69094 | -1.0811 | -0.73216
47.4062 | 121.9162 | -61.1847 | 60.347 | 0.11269 | 0.03274 | -0.030314 | -0.029595 | -0.009515 | 0.076426 | -0.039826 | 60.2414 | 60.2723 | 60.191 | 60.1262 | 61.2767 | 61.3189 | 60.9415 | 61.2482 | 61.2974 | 61.2174 | 61.1544 | 61.1551 | 61.1752 | 61.2611 | 61.1449 | 60.2826 | 60.3135 | 60.2322 | 60.1674 | 61.3179 | 61.3601 | 60.9827 | 61.2894 | -1.0353 | -0.7001 | -1.0857 | -0.75047
49.1406 | 121.8338 | -61.2625 | 60.3195 | 0.12185 | 0.037319 | -0.021157 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2414 | 60.2678 | 60.2002 | 60.1308 | 61.2813 | 61.3144 | 60.9232 | 61.2482 | 61.3844 | 61.2998 | 61.2414 | 61.2421 | 61.2576 | 61.3481 | 61.2273 | 60.2826 | 60.309 | 60.2414 | 60.172 | 61.3225 | 61.3556 | 60.9644 | 61.2894 | -1.0399 | -0.68179 | -1.0811 | -0.723
50.8281 | 121.9162 | -61.1801 | 60.379 | 0.11727 | 0.037319 | -0.025735 | -0.038752 | -0.014093 | 0.076426 | -0.048983 | 60.2414 | 60.2632 | 60.2047 | 60.1308 | 61.2859 | 61.3189 | 60.9461 | 61.2482 | 61.2974 | 61.2174 | 61.1544 | 61.1414 | 61.166 | 61.2565 | 61.1311 | 60.2826 | 60.3044 | 60.2459 | 60.172 | 61.3271 | 61.3601 | 60.9873 | 61.2894 | -1.0445 | -0.70468 | -1.0811 | -0.74132
52.5781 | 121.9345 | -61.1618 | 60.379 | 0.11727 | 0.051056 | -0.025735 | -0.038752 | -0.009515 | 0.081005 | -0.044405 | 60.2368 | 60.2678 | 60.1956 | 60.1262 | 61.2767 | 61.3144 | 60.9369 | 61.2436 | 61.2791 | 61.2129 | 61.1361 | 61.1231 | 61.1523 | 61.2428 | 61.1174 | 60.278 | 60.309 | 60.2368 | 60.1674 | 61.3179 | 61.3556 | 60.9781 | 61.2848 | -1.0399 | -0.7001 | -1.0811 | -0.74132
54.3281 | 121.843 | -61.2579 | 60.3378 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.009515 | 0.085583 | -0.039826 | 60.2368 | 60.2632 | 60.2047 | 60.1354 | 61.2767 | 61.3144 | 60.9278 | 61.2482 | 61.3752 | 61.2953 | 61.2368 | 61.2283 | 61.2484 | 61.3435 | 61.2181 | 60.278 | 60.3044 | 60.2459 | 60.1766 | 61.3179 | 61.3556 | 60.9689 | 61.2894 | -1.0399 | -0.69094 | -1.072 | -0.723
56.0625 | 121.9254 | -61.2488 | 60.2554 | 0.11269 | 0.037319 | -0.030314 | -0.038752 | -0.004937 | 0.090161 | -0.039826 | 60.246 | 60.2678 | 60.2047 | 60.1262 | 61.2859 | 61.3189 | 60.9323 | 61.2528 | 61.3615 | 61.2861 | 61.2185 | 61.21 | 61.2438 | 61.3389 | 61.209 | 60.2872 | 60.309 | 60.2459 | 60.1674 | 61.3271 | 61.3601 | 60.9735 | 61.294 | -1.0399 | -0.68636 | -1.0811 | -0.72758
57.8125 | 121.9162 | -61.171 | 60.3561 | 0.11727 | 0.037319 | -0.030314 | -0.034174 | -0.000359 | 0.085583 | -0.039826 | 60.246 | 60.2632 | 60.2002 | 60.1216 | 61.2767 | 61.3235 | 60.9369 | 61.2574 | 61.2882 | 61.2083 | 61.1406 | 61.1368 | 61.1706 | 61.2565 | 61.1311 | 60.2872 | 60.3044 | 60.2414 | 60.1628 | 61.3179 | 61.3647 | 60.9781 | 61.2986 | -1.0308 | -0.69094 | -1.0766 | -0.73674
59.5625 | 121.8063 | -61.2762 | 60.3195 | 0.11727 | 0.037319 | -0.021157 | -0.034174 | -0.004937 | 0.09474 | -0.03067 | 60.2414 | 60.2632 | 60.2047 | 60.1262 | 61.2721 | 61.3144 | 60.9278 | 61.2482 | 61.3935 | 61.3136 | 61.2551 | 61.2421 | 61.2713 | 61.371 | 61.2456 | 60.2826 | 60.3044 | 60.2459 | 60.1674 | 61.3133 | 61.3556 | 60.9689 | 61.2894 | -1.0308 | -0.68636 | -1.0674 | -0.723
61.2344 | 121.8979 | -61.2122 | 60.3561 | 0.11269 | 0.041898 | -0.030314 | -0.038752 | -0.009515 | 0.081005 | -0.039826 | 60.2414 | 60.2678 | 60.2002 | 60.1262 | 61.2767 | 61.3144 | 60.969 | 61.2482 | 61.3249 | 61.2541 | 61.1818 | 61.1734 | 61.2026 | 61.2932 | 61.1723 | 60.2826 | 60.309 | 60.2414 | 60.1674 | 61.3179 | 61.3556 | 61.0102 | 61.2894 | -1.0353 | -0.72757 | -1.0766 | -0.76879
62.9844 | 121.9208 | -61.1435 | 60.3699 | 0.11727 | 0.03274 | -0.021157 | -0.034174 | -0.009515 | 0.081005 | -0.03067 | 60.2414 | 60.2678 | 60.2002 | 60.1262 | 61.2767 | 61.3144 | 60.9461 | 61.2482 | 61.2608 | 61.1762 | 61.1223 | 61.1093 | 61.134 | 61.2245 | 61.1128 | 60.2826 | 60.309 | 60.2414 | 60.1674 | 61.3179 | 61.3556 | 60.9873 | 61.2894 | -1.0353 | -0.70468 | -1.0766 | -0.74589
64.7344 | 121.7972 | -61.2213 | 60.4202 | 0.12185 | 0.03274 | -0.025735 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.2414 | 60.2632 | 60.1956 | 60.1262 | 61.2859 | 61.3144 | 60.9323 | 61.2482 | 61.3432 | 61.2541 | 61.1956 | 61.1871 | 61.2118 | 61.3069 | 61.1815 | 60.2826 | 60.3044 | 60.2368 | 60.1674 | 61.3271 | 61.3556 | 60.9735 | 61.2894 | -1.0445 | -0.69094 | -1.0903 | -0.73674
66.4219 | 121.7834 | -61.322 | 60.3104 | 0.12185 | 0.051056 | -0.021157 | -0.029595 | -0.004937 | 0.09474 | -0.039826 | 60.246 | 60.2723 | 60.2093 | 60.1308 | 61.2767 | 61.3189 | 60.9278 | 61.2528 | 61.4439 | 61.3731 | 61.3009 | 61.2924 | 61.3171 | 61.4168 | 61.2822 | 60.2872 | 60.3135 | 60.2505 | 60.172 | 61.3179 | 61.3601 | 60.9689 | 61.294 | -1.0308 | -0.68179 | -1.0674 | -0.71842
68.1719 | 121.8201 | -61.2808 | 60.3241 | 0.11269 | 0.051056 | -0.021157 | -0.029595 | -0.009515 | 0.09474 | -0.03067 | 60.2551 | 60.2723 | 60.2047 | 60.1262 | 61.2721 | 61.3189 | 60.9232 | 61.2528 | 61.3935 | 61.3319 | 61.2597 | 61.2512 | 61.2713 | 61.3756 | 61.2502 | 60.2963 | 60.3135 | 60.2459 | 60.1674 | 61.3133 | 61.3601 | 60.9644 | 61.294 | -1.017 | -0.66805 | -1.0674 | -0.71842
69.9219 | 121.9162 | -61.1755 | 60.3378 | 0.12185 | 0.037319 | -0.025735 | -0.034174 | -0.014093 | 0.085583 | -0.044405 | 60.246 | 60.2723 | 60.1956 | 60.1308 | 61.2813 | 61.3189 | 60.9415 | 61.2574 | 61.2974 | 61.2129 | 61.1498 | 61.1414 | 61.1614 | 61.2611 | 61.1311 | 60.2872 | 60.3135 | 60.2368 | 60.172 | 61.3225 | 61.3601 | 60.9827 | 61.2986 | -1.0353 | -0.69552 | -1.0857 | -0.74589
71.5938 | 121.875 | -61.2122 | 60.3287 | 0.11269 | 0.041898 | -0.025735 | -0.034174 | -0.014093 | 0.085583 | -0.044405 | 60.246 | 60.2678 | 60.1956 | 60.1262 | 61.2767 | 61.3098 | 60.9278 | 61.2528 | 61.3249 | 61.2541 | 61.1864 | 61.178 | 61.1981 | 61.2977 | 61.1678 | 60.2872 | 60.309 | 60.2368 | 60.1674 | 61.3179 | 61.351 | 60.9689 | 61.294 | -1.0308 | -0.68179 | -1.0811 | -0.73216
73.3438 | 121.9299 | -61.2808 | 60.2783 | 0.11269 | 0.041898 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.044405 | 60.2414 | 60.2632 | 60.2002 | 60.1216 | 61.2813 | 61.3144 | 60.9278 | 61.2436 | 61.3935 | 61.3227 | 61.2505 | 61.2512 | 61.2713 | 61.3664 | 61.2364 | 60.2826 | 60.3044 | 60.2414 | 60.1628 | 61.3225 | 61.3556 | 60.9689 | 61.2848 | -1.0399 | -0.68636 | -1.0811 | -0.72758
75.0938 | 121.8292 | -61.2762 | 60.3333 | 0.11727 | 0.041898 | -0.025735 | -0.029595 | -0.004937 | 0.090161 | -0.03067 | 60.2414 | 60.2678 | 60.2047 | 60.1308 | 61.2813 | 61.3144 | 60.9278 | 61.2482 | 61.3935 | 61.3181 | 61.2505 | 61.2467 | 61.2713 | 61.3664 | 61.2456 | 60.2826 | 60.309 | 60.2459 | 60.172 | 61.3225 | 61.3556 | 60.9689 | 61.2894 | -1.0399 | -0.68636 | -1.0766 | -0.723
76.7812 | 121.9025 | -61.2213 | 60.3012 | 0.11269 | 0.037319 | -0.025735 | -0.029595 | -0.014093 | 0.081005 | -0.044405 | 60.246 | 60.2723 | 60.2093 | 60.1262 | 61.2813 | 61.3235 | 60.9278 | 61.2528 | 61.334 | 61.2586 | 61.1956 | 61.1917 | 61.2072 | 61.3023 | 61.1769 | 60.2872 | 60.3135 | 60.2505 | 60.1674 | 61.3225 | 61.3647 | 60.9689 | 61.294 | -1.0353 | -0.68179 | -1.072 | -0.71842
78.5312 | 121.9574 | -61.1572 | 60.3561 | 0.12185 | 0.037319 | -0.025735 | -0.029595 | -0.004937 | 0.085583 | -0.035248 | 60.2414 | 60.2678 | 60.2047 | 60.1262 | 61.2859 | 61.3235 | 60.9369 | 61.2482 | 61.2791 | 61.1945 | 61.1315 | 61.1276 | 61.1523 | 61.2428 | 61.122 | 60.2826 | 60.309 | 60.2459 | 60.1674 | 61.3271 | 61.3647 | 60.9781 | 61.2894 | -1.0445 | -0.69552 | -1.0811 | -0.73216
80.2656 | 121.8979 | -61.2579 | 60.26 | 0.11269 | 0.051056 | -0.030314 | -0.029595 | -0.009515 | 0.090161 | -0.039826 | 60.246 | 60.2678 | 60.1956 | 60.1308 | 61.2813 | 61.3189 | 60.9369 | 61.2528 | 61.3706 | 61.309 | 61.2276 | 61.2283 | 61.2484 | 61.3481 | 61.2181 | 60.2872 | 60.309 | 60.2368 | 60.172 | 61.3225 | 61.3601 | 60.9781 | 61.294 | -1.0353 | -0.69094 | -1.0857 | -0.74132
81.9531 | 121.9528 | -61.1893 | 60.3653 | 0.11727 | 0.041898 | -0.025735 | -0.020438 | -0.009515 | 0.085583 | -0.044405 | 60.2414 | 60.2723 | 60.2002 | 60.1308 | 61.2767 | 61.3235 | 60.9415 | 61.2482 | 61.3065 | 61.2312 | 61.1635 | 61.1688 | 61.1798 | 61.2749 | 61.1449 | 60.2826 | 60.3135 | 60.2414 | 60.172 | 61.3179 | 61.3647 | 60.9827 | 61.2894 | -1.0353 | -0.7001 | -1.0766 | -0.74132
83.7031 | 121.7789 | -61.3083 | 60.3012 | 0.11269 | 0.041898 | -0.025735 | -0.029595 | -0.004937 | 0.090161 | -0.044405 | 60.2368 | 60.2632 | 60.2047 | 60.1308 | 61.2813 | 61.3144 | 60.9415 | 61.2482 | 61.421 | 61.3502 | 61.2826 | 61.2787 | 61.3034 | 61.3985 | 61.2639 | 60.278 | 60.3044 | 60.2459 | 60.172 | 61.3225 | 61.3556 | 60.9827 | 61.2894 | -1.0445 | -0.70468 | -1.0766 | -0.73674
85.4375 | 121.8384 | -61.2488 | 60.3699 | 0.11727 | 0.051056 | -0.025735 | -0.025017 | -0.014093 | 0.090161 | -0.039826 | 60.246 | 60.2678 | 60.2047 | 60.1262 | 61.2767 | 61.3189 | 60.9232 | 61.2528 | 61.3661 | 61.2998 | 61.223 | 61.2238 | 61.2347 | 61.3389 | 61.209 | 60.2872 | 60.309 | 60.2459 | 60.1674 | 61.3179 | 61.3601 | 60.9644 | 61.294 | -1.0308 | -0.67721 | -1.072 | -0.71842
87.125 | 121.8109 | -61.3083 | 60.3058 | 0.11727 | 0.051056 | -0.025735 | -0.025017 | -0.009515 | 0.090161 | -0.035248 | 60.2505 | 60.2723 | 60.2047 | 60.1308 | 61.2813 | 61.3189 | 60.9323 | 61.2482 | 61.4256 | 61.3593 | 61.2826 | 61.2833 | 61.2988 | 61.3985 | 61.273 | 60.2917 | 60.3135 | 60.2459 | 60.172 | 61.3225 | 61.3601 | 60.9735 | 61.2894 | -1.0308 | -0.68178 | -1.0766 | -0.72758
88.875 | 121.8887 | -61.2762 | 60.2692 | 0.12185 | 0.041898 | -0.021157 | -0.034174 | -0.018671 | 0.090161 | -0.039826 | 60.2414 | 60.2632 | 60.2047 | 60.1308 | 61.2813 | 61.3144 | 60.9278 | 61.2574 | 61.3981 | 61.3181 | 61.2551 | 61.2421 | 61.2576 | 61.3664 | 61.2364 | 60.2826 | 60.3044 | 60.2459 | 60.172 | 61.3225 | 61.3556 | 60.9689 | 61.2986 | -1.0399 | -0.68636 | -1.0766 | -0.723
90.625 | 121.8475 | -61.1847 | 60.4019 | 0.11727 | 0.046477 | -0.025735 | -0.038752 | -0.014093 | 0.085583 | -0.044405 | 60.246 | 60.2769 | 60.2047 | 60.1262 | 61.2859 | 61.3235 | 60.9369 | 61.2482 | 61.302 | 61.2312 | 61.159 | 61.1459 | 61.1706 | 61.2703 | 61.1403 | 60.2872 | 60.3181 | 60.2459 | 60.1674 | 61.3271 | 61.3647 | 60.9781 | 61.2894 | -1.0399 | -0.69094 | -1.0811 | -0.73216
92.2969 | 121.9208 | -61.1984 | 60.3653 | 0.12185 | 0.041898 | -0.021157 | -0.025017 | -0.014093 | 0.085583 | -0.039826 | 60.246 | 60.2723 | 60.2002 | 60.1262 | 61.2859 | 61.3189 | 60.9506 | 61.2436 | 61.3203 | 61.2403 | 61.1773 | 61.1734 | 61.1843 | 61.284 | 61.1586 | 60.2872 | 60.3135 | 60.2414 | 60.1674 | 61.3271 | 61.3601 | 60.9918 | 61.2848 | -1.0399 | -0.70468 | -1.0857 | -0.75047
94.0312 | 121.8155 | -61.2854 | 60.3195 | 0.12185 | 0.046477 | -0.021157 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.2414 | 60.2632 | 60.2002 | 60.1262 | 61.2767 | 61.3189 | 60.9461 | 61.2436 | 61.4073 | 61.3319 | 61.2642 | 61.2558 | 61.2805 | 61.3756 | 61.2502 | 60.2826 | 60.3044 | 60.2414 | 60.1674 | 61.3179 | 61.3601 | 60.9873 | 61.2848 | -1.0353 | -0.70468 | -1.0766 | -0.74589
95.7188 | 121.9116 | -61.1801 | 60.3653 | 0.11269 | 0.037319 | -0.030314 | -0.034174 | -0.014093 | 0.085583 | -0.039826 | 60.2505 | 60.2723 | 60.2002 | 60.1262 | 61.2859 | 61.3144 | 60.9369 | 61.2528 | 61.2928 | 61.2174 | 61.1498 | 61.1459 | 61.166 | 61.2657 | 61.1403 | 60.2917 | 60.3135 | 60.2414 | 60.1674 | 61.3271 | 61.3556 | 60.9781 | 61.294 | -1.0353 | -0.68636 | -1.0857 | -0.73674
97.4531 | 121.9299 | -61.2534 | 60.2737 | 0.11727 | 0.046477 | -0.021157 | -0.029595 | -0.014093 | 0.085583 | -0.039826 | 60.246 | 60.2723 | 60.2093 | 60.1308 | 61.2767 | 61.3144 | 60.9323 | 61.2528 | 61.3706 | 61.2998 | 61.2322 | 61.2238 | 61.2393 | 61.3389 | 61.2135 | 60.2872 | 60.3135 | 60.2505 | 60.172 | 61.3179 | 61.3556 | 60.9735 | 61.294 | -1.0308 | -0.68636 | -1.0674 | -0.723
99.2031 | 121.7834 | -61.2305 | 60.4111 | 0.11269 | 0.041898 | -0.030314 | -0.025017 | -0.014093 | 0.085583 | -0.035248 | 60.246 | 60.2678 | 60.2047 | 60.1354 | 61.2767 | 61.3144 | 60.9461 | 61.2528 | 61.3432 | 61.2724 | 61.2002 | 61.2055 | 61.2164 | 61.3161 | 61.1952 | 60.2872 | 60.309 | 60.2459 | 60.1766 | 61.3179 | 61.3556 | 60.9873 | 61.294 | -1.0308 | -0.7001 | -1.072 | -0.74132
100.8906 | 121.8567 | -61.2488 | 60.3653 | 0.11727 | 0.046477 | -0.021157 | -0.025017 | -0.009515 | 0.090161 | -0.035248 | 60.2505 | 60.2678 | 60.2093 | 60.14 | 61.2767 | 61.3144 | 60.9506 | 61.2436 | 61.3661 | 61.2953 | 61.2276 | 61.2238 | 61.2393 | 61.3389 | 61.2135 | 60.2917 | 60.309 | 60.2505 | 60.1812 | 61.3179 | 61.3556 | 60.9918 | 61.2848 | -1.0262 | -0.7001 | -1.0674 | -0.74132
102.6406 | 121.8063 | -61.2442 | 60.379 | 0.11727 | 0.041898 | -0.025735 | -0.025017 | -0.009515 | 0.09474 | -0.044405 | 60.2551 | 60.2723 | 60.2047 | 60.1308 | 61.2767 | 61.3144 | 60.9461 | 61.2482 | 61.3615 | 61.2861 | 61.2185 | 61.2192 | 61.2347 | 61.3389 | 61.1998 | 60.2963 | 60.3135 | 60.2459 | 60.172 | 61.3179 | 61.3556 | 60.9873 | 61.2894 | -1.0216 | -0.69094 | -1.072 | -0.74132
104.3906 | 121.9254 | -61.2671 | 60.2509 | 0.11727 | 0.046477 | -0.021157 | -0.029595 | -0.014093 | 0.081005 | -0.035248 | 60.2505 | 60.2678 | 60.2002 | 60.1262 | 61.2767 | 61.3098 | 60.9232 | 61.2436 | 61.3844 | 61.3136 | 61.2459 | 61.2375 | 61.253 | 61.3481 | 61.2318 | 60.2917 | 60.309 | 60.2414 | 60.1674 | 61.3179 | 61.351 | 60.9644 | 61.2848 | -1.0262 | -0.67263 | -1.0766 | -0.723
106.0625 | 121.9391 | -61.1847 | 60.3653 | 0.12185 | 0.041898 | -0.025735 | -0.029595 | -0.014093 | 0.085583 | -0.048983 | 60.2505 | 60.2723 | 60.2139 | 60.1262 | 61.2813 | 61.3144 | 60.9369 | 61.2436 | 61.3065 | 61.2266 | 61.159 | 61.1551 | 61.1706 | 61.2703 | 61.1357 | 60.2917 | 60.3135 | 60.2551 | 60.1674 | 61.3225 | 61.3556 | 60.9781 | 61.2848 | -1.0308 | -0.68636 | -1.0674 | -0.723
107.7969 | 121.8338 | -61.2579 | 60.3836 | 0.11727 | 0.046477 | -0.021157 | -0.029595 | -0.009515 | 0.081005 | -0.039826 | 60.246 | 60.2678 | 60.2093 | 60.1308 | 61.2767 | 61.3235 | 60.9278 | 61.2528 | 61.3752 | 61.3044 | 61.2368 | 61.2283 | 61.2484 | 61.3389 | 61.2181 | 60.2872 | 60.309 | 60.2505 | 60.172 | 61.3179 | 61.3647 | 60.9689 | 61.294 | -1.0308 | -0.68179 | -1.0674 | -0.71842
109.5625 | 121.8567 | -61.2579 | 60.3149 | 0.11727 | 0.051056 | -0.021157 | -0.029595 | -0.009515 | 0.090161 | -0.039826 | 60.2414 | 60.2723 | 60.2047 | 60.1262 | 61.2813 | 61.3098 | 60.9415 | 61.2528 | 61.3752 | 61.309 | 61.2368 | 61.2283 | 61.2484 | 61.3481 | 61.2181 | 60.2826 | 60.3135 | 60.2459 | 60.1674 | 61.3225 | 61.351 | 60.9827 | 61.294 | -1.0399 | -0.7001 | -1.0766 | -0.73674
111.2344 | 121.8384 | -61.3037 | 60.2829 | 0.11269 | 0.046477 | -0.025735 | -0.029595 | -0.004937 | 0.085583 | -0.035248 | 60.246 | 60.2723 | 60.2047 | 60.1262 | 61.2813 | 61.3144 | 60.9369 | 61.2574 | 61.4164 | 61.3502 | 61.278 | 61.2741 | 61.2988 | 61.3893 | 61.2685 | 60.2872 | 60.3135 | 60.2459 | 60.1674 | 61.3225 | 61.3556 | 60.9781 | 61.2986 | -1.0353 | -0.69094 | -1.0766 | -0.73216
112.9844 | 121.8384 | -61.2305 | 60.3882 | 0.12185 | 0.055634 | -0.021157 | -0.034174 | -0.009515 | 0.09474 | -0.039826 | 60.246 | 60.2632 | 60.2002 | 60.1308 | 61.2813 | 61.3189 | 60.9369 | 61.2574 | 61.3523 | 61.2861 | 61.2093 | 61.1963 | 61.221 | 61.3252 | 61.1906 | 60.2872 | 60.3044 | 60.2414 | 60.172 | 61.3225 | 61.3601 | 60.9781 | 61.2986 | -1.0353 | -0.69094 | -1.0811 | -0.73674
114.7188 | 121.843 | -61.2625 | 60.3836 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.014093 | 0.090161 | -0.039826 | 60.246 | 60.2678 | 60.2002 | 60.1308 | 61.2813 | 61.3189 | 60.9461 | 61.2482 | 61.3798 | 61.2998 | 61.2414 | 61.2329 | 61.2484 | 61.3527 | 61.2227 | 60.2872 | 60.309 | 60.2414 | 60.172 | 61.3225 | 61.3601 | 60.9873 | 61.2894 | -1.0353 | -0.7001 | -1.0811 | -0.74589
116.4531 | 121.8201 | -61.2671 | 60.3241 | 0.12643 | 0.051056 | -0.021157 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.246 | 60.2769 | 60.2047 | 60.1354 | 61.2813 | 61.3189 | 60.9232 | 61.2436 | 61.3935 | 61.3181 | 61.2459 | 61.2375 | 61.2622 | 61.3573 | 61.2318 | 60.2872 | 60.3181 | 60.2459 | 60.1766 | 61.3225 | 61.3601 | 60.9644 | 61.2848 | -1.0353 | -0.67721 | -1.0766 | -0.71842
118.2031 | 121.9208 | -61.2579 | 60.2737 | 0.12185 | 0.041898 | -0.021157 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.246 | 60.2723 | 60.2047 | 60.1354 | 61.2813 | 61.3281 | 60.9461 | 61.2528 | 61.3798 | 61.2998 | 61.2368 | 61.2238 | 61.2484 | 61.3435 | 61.2181 | 60.2872 | 60.3135 | 60.2459 | 60.1766 | 61.3225 | 61.3693 | 60.9873 | 61.294 | -1.0353 | -0.7001 | -1.0766 | -0.74132
119.8906 | 121.7972 | -61.2122 | 60.4065 | 0.11727 | 0.037319 | -0.025735 | -0.025017 | -0.009515 | 0.09474 | -0.035248 | 60.246 | 60.2723 | 60.1956 | 60.1308 | 61.2813 | 61.3189 | 60.9369 | 61.2436 | 61.3294 | 61.2495 | 61.1864 | 61.1871 | 61.2026 | 61.3069 | 61.1769 | 60.2872 | 60.3135 | 60.2368 | 60.172 | 61.3225 | 61.3601 | 60.9781 | 61.2848 | -1.0353 | -0.69094 | -1.0857 | -0.74132
121.6406 | 121.8796 | -61.2167 | 60.3561 | 0.12185 | 0.037319 | -0.025735 | -0.034174 | -0.014093 | 0.085583 | -0.048983 | 60.246 | 60.2769 | 60.2002 | 60.1262 | 61.2767 | 61.3281 | 60.9323 | 61.2436 | 61.3386 | 61.2541 | 61.191 | 61.1826 | 61.2026 | 61.3023 | 61.1678 | 60.2872 | 60.3181 | 60.2414 | 60.1674 | 61.3179 | 61.3693 | 60.9735 | 61.2848 | -1.0308 | -0.68636 | -1.0766 | -0.73216
123.3906 | 121.9025 | -61.203 | 60.3653 | 0.11727 | 0.046477 | -0.030314 | -0.029595 | -0.014093 | 0.081005 | -0.039826 | 60.246 | 60.2723 | 60.1956 | 60.1262 | 61.2859 | 61.3144 | 60.9506 | 61.2482 | 61.3203 | 61.2495 | 61.1727 | 61.1734 | 61.1889 | 61.284 | 61.1632 | 60.2872 | 60.3135 | 60.2368 | 60.1674 | 61.3271 | 61.3556 | 60.9918 | 61.2894 | -1.0399 | -0.70468 | -1.0903 | -0.75505
125.0781 | 121.8796 | -61.2167 | 60.3424 | 0.11727 | 0.037319 | -0.034893 | -0.029595 | -0.014093 | 0.076426 | -0.039826 | 60.2505 | 60.2678 | 60.2002 | 60.1354 | 61.2721 | 61.3189 | 60.9461 | 61.2528 | 61.334 | 61.2541 | 61.1818 | 61.1871 | 61.2026 | 61.2932 | 61.1769 | 60.2917 | 60.309 | 60.2414 | 60.1766 | 61.3133 | 61.3601 | 60.9873 | 61.294 | -1.0216 | -0.69552 | -1.072 | -0.74589
126.8125 | 121.8887 | -61.1847 | 60.4111 | 0.11269 | 0.046477 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.044405 | 60.2505 | 60.2678 | 60.1956 | 60.1262 | 61.2813 | 61.3235 | 60.9415 | 61.2482 | 61.2974 | 61.2312 | 61.1544 | 61.1551 | 61.1752 | 61.2703 | 61.1403 | 60.2917 | 60.309 | 60.2368 | 60.1674 | 61.3225 | 61.3647 | 60.9827 | 61.2894 | -1.0308 | -0.69094 | -1.0857 | -0.74589
128.5625 | 121.8201 | -61.2808 | 60.3333 | 0.11727 | 0.055634 | -0.016578 | -0.020438 | -0.004937 | 0.09474 | -0.035248 | 60.246 | 60.2723 | 60.2093 | 60.1354 | 61.2767 | 61.3189 | 60.9369 | 61.2482 | 61.3981 | 61.3365 | 61.2642 | 61.2604 | 61.2759 | 61.3756 | 61.2456 | 60.2872 | 60.3135 | 60.2505 | 60.1766 | 61.3179 | 61.3601 | 60.9781 | 61.2894 | -1.0308 | -0.69094 | -1.0674 | -0.72758
130.3125 | 121.8887 | -61.2305 | 60.2921 | 0.11727 | 0.046477 | -0.025735 | -0.034174 | -0.004937 | 0.09474 | -0.039826 | 60.246 | 60.2815 | 60.2002 | 60.1262 | 61.2859 | 61.3189 | 60.9232 | 61.2482 | 61.3477 | 61.2769 | 61.2047 | 61.1963 | 61.2255 | 61.3252 | 61.1906 | 60.2872 | 60.3227 | 60.2414 | 60.1674 | 61.3271 | 61.3601 | 60.9644 | 61.2894 | -1.0399 | -0.67721 | -1.0857 | -0.723
131.9844 | 121.875 | -61.1893 | 60.4156 | 0.11269 | 0.037319 | -0.025735 | -0.025017 | -0.014093 | 0.081005 | -0.035248 | 60.2505 | 60.2678 | 60.2139 | 60.1216 | 61.2813 | 61.3189 | 60.9323 | 61.2528 | 61.302 | 61.2266 | 61.1635 | 61.1643 | 61.1752 | 61.2703 | 61.154 | 60.2917 | 60.309 | 60.2551 | 60.1628 | 61.3225 | 61.3601 | 60.9735 | 61.294 | -1.0308 | -0.68178 | -1.0674 | -0.71842
133.7188 | 121.8292 | -61.2396 | 60.3699 | 0.11727 | 0.041898 | -0.030314 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.246 | 60.2769 | 60.1956 | 60.1308 | 61.2767 | 61.3144 | 60.9461 | 61.2436 | 61.3569 | 61.2815 | 61.2093 | 61.21 | 61.2347 | 61.3298 | 61.2044 | 60.2872 | 60.3181 | 60.2368 | 60.172 | 61.3179 | 61.3556 | 60.9873 | 61.2848 | -1.0308 | -0.7001 | -1.0811 | -0.75047
135.3906 | 121.9345 | -61.2579 | 60.2692 | 0.12185 | 0.037319 | -0.030314 | -0.034174 | -0.014093 | 0.090161 | -0.044405 | 60.2414 | 60.2723 | 60.2002 | 60.1308 | 61.2813 | 61.3281 | 60.9461 | 61.2482 | 61.3798 | 61.2953 | 61.2276 | 61.2238 | 61.2438 | 61.3481 | 61.2135 | 60.2826 | 60.3135 | 60.2414 | 60.172 | 61.3225 | 61.3693 | 60.9873 | 61.2894 | -1.0399 | -0.70468 | -1.0811 | -0.74589
137.1406 | 121.9208 | -61.2442 | 60.3149 | 0.12185 | 0.041898 | -0.030314 | -0.034174 | -0.009515 | 0.090161 | -0.039826 | 60.2505 | 60.2769 | 60.2002 | 60.1216 | 61.2859 | 61.3189 | 60.9461 | 61.2528 | 61.3661 | 61.2861 | 61.2139 | 61.21 | 61.2347 | 61.3344 | 61.2044 | 60.2917 | 60.3181 | 60.2414 | 60.1628 | 61.3271 | 61.3601 | 60.9873 | 61.294 | -1.0353 | -0.69552 | -1.0857 | -0.74589
138.8281 | 121.8155 | -61.2762 | 60.3882 | 0.12185 | 0.046477 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.039826 | 60.2505 | 60.2723 | 60.2093 | 60.1262 | 61.2859 | 61.3189 | 60.9461 | 61.2482 | 61.3981 | 61.3227 | 61.2505 | 61.2512 | 61.2667 | 61.3618 | 61.2364 | 60.2917 | 60.3135 | 60.2505 | 60.1674 | 61.3271 | 61.3601 | 60.9873 | 61.2894 | -1.0353 | -0.69552 | -1.0766 | -0.73674
140.5938 | 121.9254 | -61.1847 | 60.3607 | 0.11727 | 0.037319 | -0.030314 | -0.029595 | -0.014093 | 0.081005 | -0.044405 | 60.2505 | 60.2723 | 60.2047 | 60.1262 | 61.2813 | 61.3189 | 60.9415 | 61.2528 | 61.302 | 61.222 | 61.1544 | 61.1551 | 61.1706 | 61.2657 | 61.1403 | 60.2917 | 60.3135 | 60.2459 | 60.1674 | 61.3225 | 61.3601 | 60.9827 | 61.294 | -1.0308 | -0.69094 | -1.0766 | -0.73674
142.3281 | 121.8887 | -61.2488 | 60.347 | 0.11269 | 0.046477 | -0.034893 | -0.029595 | -0.009515 | 0.081005 | -0.035248 | 60.246 | 60.2723 | 60.2002 | 60.1216 | 61.2813 | 61.3281 | 60.9552 | 61.2528 | 61.3615 | 61.2953 | 61.2139 | 61.2192 | 61.2393 | 61.3298 | 61.2135 | 60.2872 | 60.3135 | 60.2414 | 60.1628 | 61.3225 | 61.3693 | 60.9964 | 61.294 | -1.0353 | -0.70926 | -1.0811 | -0.75505
144.0156 | 121.9208 | -61.1938 | 60.3928 | 0.12185 | 0.037319 | -0.025735 | -0.029595 | -0.014093 | 0.085583 | -0.035248 | 60.2505 | 60.2678 | 60.1956 | 60.1262 | 61.2813 | 61.3189 | 60.9506 | 61.2528 | 61.3157 | 61.2312 | 61.1681 | 61.1643 | 61.1798 | 61.2794 | 61.1586 | 60.2917 | 60.309 | 60.2368 | 60.1674 | 61.3225 | 61.3601 | 60.9918 | 61.294 | -1.0308 | -0.7001 | -1.0857 | -0.75505
145.7656 | 121.8933 | -61.2213 | 60.3287 | 0.11269 | 0.037319 | -0.030314 | -0.029595 | -0.018671 | 0.085583 | -0.039826 | 60.246 | 60.2723 | 60.2047 | 60.1308 | 61.2767 | 61.3189 | 60.9552 | 61.2482 | 61.334 | 61.2586 | 61.191 | 61.1917 | 61.2026 | 61.3069 | 61.1815 | 60.2872 | 60.3135 | 60.2459 | 60.172 | 61.3179 | 61.3601 | 60.9964 | 61.2894 | -1.0308 | -0.70926 | -1.072 | -0.75047
147.4375 | 121.9345 | -61.1847 | 60.3195 | 0.11269 | 0.041898 | -0.030314 | -0.029595 | -0.014093 | 0.085583 | -0.035248 | 60.246 | 60.2723 | 60.2002 | 60.1308 | 61.2859 | 61.3189 | 60.9369 | 61.2528 | 61.2974 | 61.2266 | 61.1544 | 61.1551 | 61.1706 | 61.2703 | 61.1494 | 60.2872 | 60.3135 | 60.2414 | 60.172 | 61.3271 | 61.3601 | 60.9781 | 61.294 | -1.0399 | -0.69094 | -1.0857 | -0.73674
149.1719 | 121.8704 | -61.2259 | 60.3287 | 0.11727 | 0.037319 | -0.021157 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.2505 | 60.2632 | 60.1956 | 60.1354 | 61.2905 | 61.3235 | 60.9461 | 61.2528 | 61.3432 | 61.2632 | 61.2047 | 61.1917 | 61.2164 | 61.3115 | 61.1861 | 60.2917 | 60.3044 | 60.2368 | 60.1766 | 61.3317 | 61.3647 | 60.9873 | 61.294 | -1.0399 | -0.69552 | -1.0949 | -0.75047
150.9375 | 121.7926 | -61.3266 | 60.3241 | 0.12185 | 0.046477 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.039826 | 60.246 | 60.2723 | 60.1956 | 60.1262 | 61.2859 | 61.3144 | 60.9415 | 61.2574 | 61.4485 | 61.3731 | 61.3009 | 61.3016 | 61.3171 | 61.4122 | 61.2868 | 60.2872 | 60.3135 | 60.2368 | 60.1674 | 61.3271 | 61.3556 | 60.9827 | 61.2986 | -1.0399 | -0.69552 | -1.0903 | -0.74589
152.6875 | 121.8155 | -61.2854 | 60.3058 | 0.12185 | 0.041898 | -0.016578 | -0.029595 | -0.000359 | 0.085583 | -0.035248 | 60.2551 | 60.2723 | 60.2093 | 60.1262 | 61.2813 | 61.3144 | 60.9415 | 61.2528 | 61.4073 | 61.3273 | 61.2688 | 61.2558 | 61.285 | 61.371 | 61.2502 | 60.2963 | 60.3135 | 60.2505 | 60.1674 | 61.3225 | 61.3556 | 60.9827 | 61.294 | -1.0262 | -0.68636 | -1.072 | -0.73216
154.4219 | 121.7926 | -61.3037 | 60.3012 | 0.12185 | 0.041898 | -0.025735 | -0.034174 | -0.004937 | 0.090161 | -0.035248 | 60.2505 | 60.2769 | 60.2002 | 60.1308 | 61.2767 | 61.3098 | 60.9278 | 61.2482 | 61.4256 | 61.3456 | 61.278 | 61.2695 | 61.2988 | 61.3939 | 61.2685 | 60.2917 | 60.3181 | 60.2414 | 60.172 | 61.3179 | 61.351 | 60.9689 | 61.2894 | -1.0262 | -0.67721 | -1.0766 | -0.72758
156.125 | 121.9025 | -61.203 | 60.3607 | 0.11727 | 0.041898 | -0.030314 | -0.034174 | -0.014093 | 0.076426 | -0.044405 | 60.2505 | 60.2769 | 60.1956 | 60.1262 | 61.2813 | 61.3235 | 60.9461 | 61.2574 | 61.3203 | 61.2449 | 61.1727 | 61.1688 | 61.1889 | 61.2794 | 61.1586 | 60.2917 | 60.3181 | 60.2368 | 60.1674 | 61.3225 | 61.3647 | 60.9873 | 61.2986 | -1.0308 | -0.69552 | -1.0857 | -0.75047
157.8125 | 121.8796 | -61.2213 | 60.3241 | 0.11269 | 0.041898 | -0.030314 | -0.025017 | -0.009515 | 0.085583 | -0.039826 | 60.2551 | 60.2815 | 60.1956 | 60.1262 | 61.2859 | 61.3144 | 60.9506 | 61.2574 | 61.334 | 61.2632 | 61.191 | 61.1963 | 61.2118 | 61.3069 | 61.1815 | 60.2963 | 60.3227 | 60.2368 | 60.1674 | 61.3271 | 61.3556 | 60.9918 | 61.2986 | -1.0308 | -0.69552 | -1.0903 | -0.75505
159.5469 | 121.8063 | -61.235 | 60.3836 | 0.11727 | 0.037319 | -0.016578 | -0.025017 | -0.009515 | 0.085583 | -0.039826 | 60.2551 | 60.2678 | 60.1956 | 60.1262 | 61.2767 | 61.3235 | 60.9369 | 61.2528 | 61.3523 | 61.2724 | 61.2185 | 61.21 | 61.2255 | 61.3206 | 61.1952 | 60.2963 | 60.309 | 60.2368 | 60.1674 | 61.3179 | 61.3647 | 60.9781 | 61.294 | -1.0216 | -0.68179 | -1.0811 | -0.74132
161.3125 | 121.907 | -61.203 | 60.379 | 0.12185 | 0.037319 | -0.025735 | -0.029595 | -0.018671 | 0.081005 | -0.044405 | 60.246 | 60.2723 | 60.1956 | 60.1262 | 61.2813 | 61.3235 | 60.9506 | 61.2482 | 61.3249 | 61.2403 | 61.1773 | 61.1734 | 61.1843 | 61.284 | 61.1586 | 60.2872 | 60.3135 | 60.2368 | 60.1674 | 61.3225 | 61.3647 | 60.9918 | 61.2894 | -1.0353 | -0.70468 | -1.0857 | -0.75505
163 | 121.7743 | -61.3174 | 60.2875 | 0.12185 | 0.046477 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.246 | 60.2723 | 60.2047 | 60.1354 | 61.2767 | 61.3235 | 60.9506 | 61.2436 | 61.4393 | 61.3639 | 61.2917 | 61.297 | 61.3125 | 61.403 | 61.2822 | 60.2872 | 60.3135 | 60.2459 | 60.1766 | 61.3179 | 61.3647 | 60.9918 | 61.2848 | -1.0308 | -0.70468 | -1.072 | -0.74589
164.75 | 121.9528 | -61.1755 | 60.3836 | 0.11269 | 0.041898 | -0.034893 | -0.034174 | -0.004937 | 0.085583 | -0.039826 | 60.246 | 60.2769 | 60.2093 | 60.1262 | 61.2859 | 61.3189 | 60.9506 | 61.2482 | 61.2882 | 61.2174 | 61.1406 | 61.1414 | 61.1706 | 61.2611 | 61.1357 | 60.2872 | 60.3181 | 60.2505 | 60.1674 | 61.3271 | 61.3601 | 60.9918 | 61.2894 | -1.0399 | -0.70468 | -1.0766 | -0.74132
166.4844 | 121.875 | -61.2305 | 60.3561 | 0.11727 | 0.037319 | -0.030314 | -0.025017 | -0.014093 | 0.081005 | -0.044405 | 60.2551 | 60.2723 | 60.2002 | 60.1262 | 61.2676 | 61.3189 | 60.9506 | 61.2482 | 61.3477 | 61.2678 | 61.2002 | 61.2055 | 61.2164 | 61.3115 | 61.1861 | 60.2963 | 60.3135 | 60.2414 | 60.1674 | 61.3088 | 61.3601 | 60.9918 | 61.2894 | -1.0124 | -0.69552 | -1.0674 | -0.75047
168.2188 | 121.8933 | -61.235 | 60.3378 | 0.12185 | 0.046477 | -0.030314 | -0.029595 | -0.014093 | 0.071848 | -0.039826 | 60.2505 | 60.2769 | 60.2002 | 60.1262 | 61.2859 | 61.3281 | 60.9369 | 61.2574 | 61.3569 | 61.2815 | 61.2047 | 61.2055 | 61.221 | 61.3069 | 61.1952 | 60.2917 | 60.3181 | 60.2414 | 60.1674 | 61.3271 | 61.3693 | 60.9781 | 61.2986 | -1.0353 | -0.68636 | -1.0857 | -0.73674
169.9062 | 121.7697 | -61.3174 | 60.3012 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.004937 | 0.090161 | -0.026092 | 60.2505 | 60.2723 | 60.2047 | 60.1308 | 61.2859 | 61.3235 | 60.9506 | 61.2619 | 61.4347 | 61.3548 | 61.2963 | 61.2878 | 61.3125 | 61.4076 | 61.2914 | 60.2917 | 60.3135 | 60.2459 | 60.172 | 61.3271 | 61.3647 | 60.9918 | 61.3031 | -1.0353 | -0.7001 | -1.0811 | -0.74589
171.6562 | 121.9208 | -61.2946 | 60.2417 | 0.12185 | 0.041898 | -0.025735 | -0.025017 | -0.014093 | 0.085583 | -0.039826 | 60.2505 | 60.2723 | 60.2047 | 60.1216 | 61.2859 | 61.3281 | 60.9506 | 61.2482 | 61.4164 | 61.3365 | 61.2688 | 61.2695 | 61.2805 | 61.3801 | 61.2547 | 60.2917 | 60.3135 | 60.2459 | 60.1628 | 61.3271 | 61.3693 | 60.9918 | 61.2894 | -1.0353 | -0.7001 | -1.0811 | -0.74589
173.4062 | 121.8796 | -61.2259 | 60.3516 | 0.11269 | 0.037319 | -0.025735 | -0.029595 | -0.009515 | 0.081005 | -0.035248 | 60.2551 | 60.2769 | 60.2002 | 60.1354 | 61.2813 | 61.3235 | 60.9461 | 61.2482 | 61.3386 | 61.2632 | 61.2002 | 61.1963 | 61.2164 | 61.3069 | 61.1906 | 60.2963 | 60.3181 | 60.2414 | 60.1766 | 61.3225 | 61.3647 | 60.9873 | 61.2894 | -1.0262 | -0.69094 | -1.0811 | -0.74589
175.1562 | 121.8658 | -61.2122 | 60.4019 | 0.12185 | 0.041898 | -0.025735 | -0.029595 | -0.009515 | 0.090161 | -0.039826 | 60.2551 | 60.2723 | 60.2002 | 60.1308 | 61.2813 | 61.3189 | 60.9461 | 61.2482 | 61.334 | 61.2541 | 61.1864 | 61.1826 | 61.2026 | 61.3023 | 61.1723 | 60.2963 | 60.3135 | 60.2414 | 60.172 | 61.3225 | 61.3601 | 60.9873 | 61.2894 | -1.0262 | -0.69094 | -1.0811 | -0.74589
176.8281 | 121.9208 | -61.2442 | 60.3012 | 0.12185 | 0.051056 | -0.030314 | -0.029595 | -0.009515 | 0.081005 | -0.039826 | 60.2551 | 60.2723 | 60.2002 | 60.1262 | 61.2813 | 61.3235 | 60.9415 | 61.2528 | 61.3661 | 61.2953 | 61.2139 | 61.2146 | 61.2347 | 61.3252 | 61.2044 | 60.2963 | 60.3135 | 60.2414 | 60.1674 | 61.3225 | 61.3647 | 60.9827 | 61.294 | -1.0262 | -0.68636 | -1.0811 | -0.74132
178.5625 | 121.9116 | -61.2671 | 60.2829 | 0.11727 | 0.037319 | -0.025735 | -0.034174 | -0.014093 | 0.085583 | -0.035248 | 60.246 | 60.2769 | 60.2047 | 60.1262 | 61.2859 | 61.3189 | 60.9369 | 61.2436 | 61.3844 | 61.3044 | 61.2414 | 61.2329 | 61.253 | 61.3527 | 61.2318 | 60.2872 | 60.3181 | 60.2459 | 60.1674 | 61.3271 | 61.3601 | 60.9781 | 61.2848 | -1.0399 | -0.69094 | -1.0811 | -0.73216
180.2344 | 121.9162 | -61.1847 | 60.3745 | 0.11727 | 0.03274 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.044405 | 60.2505 | 60.2769 | 60.2047 | 60.1262 | 61.2767 | 61.3189 | 60.9415 | 61.2528 | 61.302 | 61.2174 | 61.159 | 61.1597 | 61.1752 | 61.2703 | 61.1403 | 60.2917 | 60.3181 | 60.2459 | 60.1674 | 61.3179 | 61.3601 | 60.9827 | 61.294 | -1.0262 | -0.69094 | -1.072 | -0.73674
181.9844 | 121.8384 | -61.2854 | 60.3653 | 0.12185 | 0.037319 | -0.030314 | -0.029595 | -0.004937 | 0.085583 | -0.039826 | 60.2597 | 60.2769 | 60.2047 | 60.1354 | 61.2813 | 61.3144 | 60.9415 | 61.2482 | 61.4073 | 61.3227 | 61.2551 | 61.2558 | 61.2805 | 61.371 | 61.2456 | 60.3009 | 60.3181 | 60.2459 | 60.1766 | 61.3225 | 61.3556 | 60.9827 | 61.2894 | -1.0216 | -0.68178 | -1.0766 | -0.73674
183.7188 | 121.9482 | -61.1893 | 60.3516 | 0.12643 | 0.03274 | -0.025735 | -0.029595 | -0.009515 | 0.085583 | -0.039826 | 60.2414 | 60.2723 | 60.2002 | 60.1308 | 61.2813 | 61.3235 | 60.9415 | 61.2482 | 61.3157 | 61.222 | 61.1635 | 61.1597 | 61.1798 | 61.2749 | 61.1494 | 60.2826 | 60.3135 | 60.2414 | 60.172 | 61.3225 | 61.3647 | 60.9827 | 61.2894 | -1.0399 | -0.7001 | -1.0811 | -0.74132
185.4531 | 121.788 | -61.2305 | 60.4477 | 0.11727 | 0.041898 | -0.021157 | -0.025017 | -0.009515 | 0.081005 | -0.039826 | 60.2505 | 60.2723 | 60.2047 | 60.1308 | 61.2813 | 61.3189 | 60.9461 | 61.2528 | 61.3477 | 61.2724 | 61.2093 | 61.2055 | 61.221 | 61.3115 | 61.1906 | 60.2917 | 60.3135 | 60.2459 | 60.172 | 61.3225 | 61.3601 | 60.9873 | 61.294 | -1.0308 | -0.69552 | -1.0766 | -0.74132
187.1406 | 121.8796 | -61.2305 | 60.3195 | 0.11727 | 0.037319 | -0.030314 | -0.029595 | -0.014093 | 0.081005 | -0.048983 | 60.2505 | 60.2815 | 60.2047 | 60.1262 | 61.2859 | 61.3189 | 60.9506 | 61.2574 | 61.3477 | 61.2678 | 61.2002 | 61.2009 | 61.2164 | 61.3115 | 61.1815 | 60.2917 | 60.3227 | 60.2459 | 60.1674 | 61.3271 | 61.3601 | 60.9918 | 61.2986 | -1.0353 | -0.7001 | -1.0811 | -0.74589
188.8906 | 121.8887 | -61.2305 | 60.3287 | 0.11727 | 0.037319 | -0.030314 | -0.029595 | -0.004937 | 0.081005 | -0.035248 | 60.2597 | 60.2815 | 60.2002 | 60.1308 | 61.2859 | 61.3189 | 60.9552 | 61.2528 | 61.3477 | 61.2678 | 61.2002 | 61.2009 | 61.2255 | 61.3115 | 61.1952 | 60.3009 | 60.3227 | 60.2414 | 60.172 | 61.3271 | 61.3601 | 60.9964 | 61.294 | -1.0262 | -0.69552 | -1.0857 | -0.75505
190.5781 | 121.8109 | -61.2488 | 60.3973 | 0.11727 | 0.037319 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.035248 | 60.246 | 60.2769 | 60.2047 | 60.1308 | 61.2859 | 61.3189 | 60.9369 | 61.2528 | 61.3661 | 61.2861 | 61.2185 | 61.2238 | 61.2393 | 61.3389 | 61.2135 | 60.2872 | 60.3181 | 60.2459 | 60.172 | 61.3271 | 61.3601 | 60.9781 | 61.294 | -1.0399 | -0.69094 | -1.0811 | -0.73216
192.3281 | 121.8018 | -61.2259 | 60.4019 | 0.11727 | 0.041898 | -0.030314 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2505 | 60.2815 | 60.2047 | 60.1262 | 61.2859 | 61.3235 | 60.9552 | 61.2482 | 61.3432 | 61.2678 | 61.1956 | 61.2055 | 61.221 | 61.3115 | 61.1906 | 60.2917 | 60.3227 | 60.2459 | 60.1674 | 61.3271 | 61.3647 | 60.9964 | 61.2894 | -1.0353 | -0.70468 | -1.0811 | -0.75047
194.0781 | 121.8979 | -61.2076 | 60.3653 | 0.12185 | 0.03274 | -0.034893 | -0.034174 | -0.009515 | 0.081005 | -0.044405 | 60.2551 | 60.2815 | 60.2002 | 60.1262 | 61.2813 | 61.3189 | 60.9461 | 61.2528 | 61.3294 | 61.2403 | 61.1727 | 61.1734 | 61.1981 | 61.2886 | 61.1632 | 60.2963 | 60.3227 | 60.2414 | 60.1674 | 61.3225 | 61.3601 | 60.9873 | 61.294 | -1.0262 | -0.69094 | -1.0811 | -0.74589
195.8281 | 121.8063 | -61.2991 | 60.3287 | 0.12185 | 0.041898 | -0.034893 | -0.029595 | -0.004937 | 0.090161 | -0.039826 | 60.246 | 60.2861 | 60.2093 | 60.1308 | 61.2905 | 61.3189 | 60.9369 | 61.2528 | 61.421 | 61.341 | 61.2642 | 61.2695 | 61.2942 | 61.3893 | 61.2593 | 60.2872 | 60.3273 | 60.2505 | 60.172 | 61.3317 | 61.3601 | 60.9781 | 61.294 | -1.0445 | -0.69094 | -1.0811 | -0.72758
197.5625 | 121.875 | -61.2122 | 60.3195 | 0.11727 | 0.03274 | -0.030314 | -0.034174 | -0.014093 | 0.090161 | -0.039826 | 60.2505 | 60.2769 | 60.2002 | 60.1262 | 61.2813 | 61.3189 | 60.9415 | 61.2528 | 61.3294 | 61.2449 | 61.1818 | 61.178 | 61.1981 | 61.3023 | 61.1723 | 60.2917 | 60.3181 | 60.2414 | 60.1674 | 61.3225 | 61.3601 | 60.9827 | 61.294 | -1.0308 | -0.69094 | -1.0811 | -0.74132
199.2344 | 121.8292 | -61.2122 | 60.4065 | 0.11269 | 0.03274 | -0.025735 | -0.029595 | -0.009515 | 0.085583 | -0.035248 | 60.2551 | 60.2769 | 60.2002 | 60.1308 | 61.2905 | 61.3144 | 60.9461 | 61.2574 | 61.3249 | 61.2449 | 61.1864 | 61.1826 | 61.2026 | 61.2977 | 61.1769 | 60.2963 | 60.3181 | 60.2414 | 60.172 | 61.3317 | 61.3556 | 60.9873 | 61.2986 | -1.0353 | -0.69094 | -1.0903 | -0.74589
200.9844 | 121.8384 | -61.2625 | 60.3745 | 0.11727 | 0.03274 | -0.021157 | -0.025017 | -0.014093 | 0.090161 | -0.039826 | 60.2597 | 60.2723 | 60.2047 | 60.1262 | 61.2813 | 61.3189 | 60.9506 | 61.2482 | 61.3798 | 61.2953 | 61.2414 | 61.2375 | 61.2484 | 61.3527 | 61.2227 | 60.3009 | 60.3135 | 60.2459 | 60.1674 | 61.3225 | 61.3601 | 60.9918 | 61.2894 | -1.0216 | -0.69094 | -1.0766 | -0.74589
202.7344 | 121.843 | -61.2671 | 60.347 | 0.12185 | 0.041898 | -0.025735 | -0.029595 | -0.014093 | 0.085583 | -0.035248 | 60.2551 | 60.2815 | 60.2093 | 60.1354 | 61.2767 | 61.3144 | 60.9461 | 61.2528 | 61.3889 | 61.309 | 61.2414 | 61.2375 | 61.253 | 61.3527 | 61.2318 | 60.2963 | 60.3227 | 60.2505 | 60.1766 | 61.3179 | 61.3556 | 60.9873 | 61.294 | -1.0216 | -0.69094 | -1.0674 | -0.73674
204.4219 | 121.9254 | -61.29 | 60.2509 | 0.12185 | 0.03274 | -0.034893 | -0.025017 | -0.004937 | 0.081005 | -0.03067 | 60.2505 | 60.2815 | 60.2002 | 60.1308 | 61.2905 | 61.3189 | 60.9506 | 61.2482 | 61.4118 | 61.3227 | 61.2551 | 61.265 | 61.285 | 61.371 | 61.2593 | 60.2917 | 60.3227 | 60.2414 | 60.172 | 61.3317 | 61.3601 | 60.9918 | 61.2894 | -1.0399 | -0.7001 | -1.0903 | -0.75047
206.1875 | 121.8018 | -61.3037 | 60.3333 | 0.11269 | 0.041898 | -0.025735 | -0.020438 | -0.004937 | 0.090161 | -0.03067 | 60.2505 | 60.2815 | 60.2047 | 60.1216 | 61.2767 | 61.3189 | 60.9506 | 61.2528 | 61.4164 | 61.3456 | 61.278 | 61.2833 | 61.2988 | 61.3939 | 61.273 | 60.2917 | 60.3227 | 60.2459 | 60.1628 | 61.3179 | 61.3601 | 60.9918 | 61.294 | -1.0262 | -0.7001 | -1.072 | -0.74589
207.9375 | 121.8109 | -61.3037 | 60.3104 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | -0.004937 | 0.090161 | -0.035248 | 60.2551 | 60.2769 | 60.2047 | 60.1308 | 61.2813 | 61.3144 | 60.9323 | 61.2528 | 61.4256 | 61.3365 | 61.2826 | 61.2833 | 61.2988 | 61.3939 | 61.2685 | 60.2963 | 60.3181 | 60.2459 | 60.172 | 61.3225 | 61.3556 | 60.9735 | 61.294 | -1.0262 | -0.67721 | -1.0766 | -0.72758
209.6719 | 121.8063 | -61.2305 | 60.4202 | 0.11727 | 0.028162 | -0.025735 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.246 | 60.2769 | 60.2093 | 60.1262 | 61.2767 | 61.3235 | 60.9415 | 61.2528 | 61.3477 | 61.2586 | 61.2047 | 61.1963 | 61.221 | 61.3161 | 61.1906 | 60.2872 | 60.3181 | 60.2505 | 60.1674 | 61.3179 | 61.3647 | 60.9827 | 61.294 | -1.0308 | -0.69552 | -1.0674 | -0.73216
211.3594 | 121.9345 | -61.2625 | 60.2646 | 0.11727 | 0.03274 | -0.025735 | -0.034174 | -0.004937 | 0.076426 | -0.035248 | 60.2551 | 60.2769 | 60.2047 | 60.1262 | 61.2813 | 61.3281 | 60.9369 | 61.2574 | 61.3798 | 61.2953 | 61.2368 | 61.2283 | 61.2576 | 61.3389 | 61.2273 | 60.2963 | 60.3181 | 60.2459 | 60.1674 | 61.3225 | 61.3693 | 60.9781 | 61.2986 | -1.0262 | -0.68179 | -1.0766 | -0.73216
213.125 | 121.8201 | -61.3129 | 60.2966 | 0.11269 | 0.03274 | -0.025735 | -0.029595 | -0.004937 | 0.076426 | -0.035248 | 60.2551 | 60.2815 | 60.2093 | 60.1354 | 61.2813 | 61.3235 | 60.9461 | 61.2482 | 61.4256 | 61.3456 | 61.2871 | 61.2833 | 61.3079 | 61.3893 | 61.2776 | 60.2963 | 60.3227 | 60.2505 | 60.1766 | 61.3225 | 61.3647 | 60.9873 | 61.2894 | -1.0262 | -0.69094 | -1.072 | -0.73674
214.8125 | 121.8887 | -61.2396 | 60.3333 | 0.12185 | 0.03274 | -0.025735 | -0.038752 | -0.009515 | 0.076426 | -0.039826 | 60.2551 | 60.2723 | 60.2047 | 60.1308 | 61.2859 | 61.3235 | 60.9461 | 61.2528 | 61.3615 | 61.2724 | 61.2139 | 61.2009 | 61.2301 | 61.316 | 61.1998 | 60.2963 | 60.3135 | 60.2459 | 60.172 | 61.3271 | 61.3647 | 60.9873 | 61.294 | -1.0308 | -0.69094 | -1.0811 | -0.74132
216.5625 | 121.8155 | -61.2991 | 60.3241 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.009515 | 0.081005 | -0.03067 | 60.2551 | 60.2769 | 60.2047 | 60.1354 | 61.2813 | 61.3189 | 60.9461 | 61.2482 | 61.4164 | 61.3365 | 61.278 | 61.2695 | 61.2896 | 61.3801 | 61.2685 | 60.2963 | 60.3181 | 60.2459 | 60.1766 | 61.3225 | 61.3601 | 60.9873 | 61.2894 | -1.0262 | -0.69094 | -1.0766 | -0.74132
218.25 | 121.8201 | -61.1847 | 60.3973 | 0.11727 | 0.03274 | -0.030314 | -0.029595 | -0.004937 | 0.090161 | -0.044405 | 60.2551 | 60.2815 | 60.2047 | 60.1354 | 61.2859 | 61.3235 | 60.9415 | 61.2574 | 61.302 | 61.2174 | 61.1544 | 61.1551 | 61.1798 | 61.2749 | 61.1403 | 60.2963 | 60.3227 | 60.2459 | 60.1766 | 61.3271 | 61.3647 | 60.9827 | 61.2986 | -1.0308 | -0.68636 | -1.0811 | -0.73674
219.9844 | 121.8933 | -61.2213 | 60.3699 | 0.11727 | 0.023583 | -0.025735 | -0.029595 | -0.009515 | 0.085583 | -0.048983 | 60.2597 | 60.2769 | 60.2002 | 60.1262 | 61.2813 | 61.3235 | 60.9506 | 61.2482 | 61.3386 | 61.2449 | 61.1956 | 61.1917 | 61.2118 | 61.3069 | 61.1723 | 60.3009 | 60.3181 | 60.2414 | 60.1674 | 61.3225 | 61.3647 | 60.9918 | 61.2894 | -1.0216 | -0.69094 | -1.0811 | -0.75047
221.7344 | 121.8979 | -61.1984 | 60.4202 | 0.11269 | 0.03274 | -0.025735 | -0.025017 | -0.014093 | 0.081005 | -0.039826 | 60.2551 | 60.2815 | 60.2047 | 60.1354 | 61.2859 | 61.3281 | 60.9461 | 61.2528 | 61.3111 | 61.2312 | 61.1727 | 61.1734 | 61.1843 | 61.2794 | 61.1586 | 60.2963 | 60.3227 | 60.2459 | 60.1766 | 61.3271 | 61.3693 | 60.9873 | 61.294 | -1.0308 | -0.69094 | -1.0811 | -0.74132
223.4844 | 121.7834 | -61.3266 | 60.3104 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2505 | 60.2861 | 60.2185 | 60.14 | 61.2813 | 61.3235 | 60.9461 | 61.2528 | 61.4485 | 61.3593 | 61.3054 | 61.3016 | 61.3217 | 61.4122 | 61.2914 | 60.2917 | 60.3273 | 60.2597 | 60.1812 | 61.3225 | 61.3647 | 60.9873 | 61.294 | -1.0308 | -0.69552 | -1.0628 | -0.72758
225.2188 | 121.9345 | -61.2854 | 60.2737 | 0.12185 | 0.028162 | -0.021157 | -0.029595 | -0.004937 | 0.085583 | -0.035248 | 60.2597 | 60.2815 | 60.2093 | 60.1216 | 61.2813 | 61.3281 | 60.9506 | 61.2574 | 61.4073 | 61.3136 | 61.2642 | 61.2558 | 61.2805 | 61.371 | 61.2502 | 60.3009 | 60.3227 | 60.2505 | 60.1628 | 61.3225 | 61.3693 | 60.9918 | 61.2986 | -1.0216 | -0.69094 | -1.072 | -0.74132
226.9062 | 121.9299 | -61.2625 | 60.2783 | 0.11269 | 0.03274 | -0.030314 | -0.034174 | -0.014093 | 0.081005 | -0.035248 | 60.2551 | 60.2907 | 60.2047 | 60.1308 | 61.2859 | 61.3327 | 60.9415 | 61.2528 | 61.3752 | 61.2953 | 61.2322 | 61.2283 | 61.2484 | 61.3435 | 61.2273 | 60.2963 | 60.3319 | 60.2459 | 60.172 | 61.3271 | 61.3739 | 60.9827 | 61.294 | -1.0308 | -0.68636 | -1.0811 | -0.73674
228.6406 | 121.7926 | -61.2991 | 60.3424 | 0.11727 | 0.03274 | -0.030314 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2551 | 60.2723 | 60.2093 | 60.14 | 61.2813 | 61.3235 | 60.9415 | 61.2528 | 61.4164 | 61.3319 | 61.2688 | 61.2741 | 61.2942 | 61.3847 | 61.2639 | 60.2963 | 60.3135 | 60.2505 | 60.1812 | 61.3225 | 61.3647 | 60.9827 | 61.294 | -1.0262 | -0.68636 | -1.072 | -0.73216
230.3125 | 121.8521 | -61.2579 | 60.3287 | 0.11727 | 0.041898 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.03067 | 60.2551 | 60.2769 | 60.2047 | 60.1354 | 61.2813 | 61.3144 | 60.9415 | 61.2482 | 61.3752 | 61.2998 | 61.2322 | 61.2329 | 61.2576 | 61.3435 | 61.2273 | 60.2963 | 60.3181 | 60.2459 | 60.1766 | 61.3225 | 61.3556 | 60.9827 | 61.2894 | -1.0262 | -0.68636 | -1.0766 | -0.73674
232.0625 | 121.8887 | -61.203 | 60.4111 | 0.11727 | 0.03274 | -0.030314 | -0.025017 | -0.014093 | 0.081005 | -0.044405 | 60.2551 | 60.2815 | 60.2139 | 60.14 | 61.2813 | 61.3189 | 60.9506 | 61.2574 | 61.3203 | 61.2357 | 61.1727 | 61.178 | 61.1889 | 61.284 | 61.1586 | 60.2963 | 60.3227 | 60.2551 | 60.1812 | 61.3225 | 61.3601 | 60.9918 | 61.2986 | -1.0262 | -0.69552 | -1.0674 | -0.73674
233.7969 | 121.9208 | -61.1847 | 60.3836 | 0.11269 | 0.037319 | -0.034893 | -0.020438 | -0.014093 | 0.081005 | -0.044405 | 60.2551 | 60.2769 | 60.2047 | 60.1354 | 61.2859 | 61.3281 | 60.9552 | 61.2528 | 61.2974 | 61.222 | 61.1498 | 61.1643 | 61.1706 | 61.2657 | 61.1403 | 60.2963 | 60.3181 | 60.2459 | 60.1766 | 61.3271 | 61.3693 | 60.9964 | 61.294 | -1.0308 | -0.7001 | -1.0811 | -0.75047
235.4688 | 121.8887 | -61.2259 | 60.347 | 0.12185 | 0.023583 | -0.034893 | -0.034174 | -0.004937 | 0.090161 | -0.039826 | 60.2597 | 60.2769 | 60.2047 | 60.1262 | 61.2859 | 61.3189 | 60.9506 | 61.2528 | 61.3477 | 61.2495 | 61.191 | 61.1917 | 61.221 | 61.3161 | 61.1861 | 60.3009 | 60.3181 | 60.2459 | 60.1674 | 61.3271 | 61.3601 | 60.9918 | 61.294 | -1.0262 | -0.69094 | -1.0811 | -0.74589
237.2188 | 121.8567 | -61.2534 | 60.3149 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | -0.000359 | 0.09474 | -0.035248 | 60.2551 | 60.2815 | 60.2139 | 60.1354 | 61.2905 | 61.3098 | 60.9506 | 61.2574 | 61.3752 | 61.2861 | 61.2322 | 61.2283 | 61.253 | 61.3481 | 61.2181 | 60.2963 | 60.3227 | 60.2551 | 60.1766 | 61.3317 | 61.351 | 60.9918 | 61.2986 | -1.0353 | -0.69552 | -1.0766 | -0.73674
238.8906 | 121.8842 | -61.2396 | 60.3333 | 0.11269 | 0.028162 | -0.021157 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.2505 | 60.2815 | 60.2002 | 60.1308 | 61.2813 | 61.3235 | 60.9506 | 61.2574 | 61.3523 | 61.2678 | 61.2185 | 61.2054 | 61.2301 | 61.3252 | 61.1998 | 60.2917 | 60.3227 | 60.2414 | 60.172 | 61.3225 | 61.3647 | 60.9918 | 61.2986 | -1.0308 | -0.7001 | -1.0811 | -0.75047
240.6406 | 121.8658 | -61.1984 | 60.4019 | 0.12185 | 0.03274 | -0.034893 | -0.025017 | -0.009515 | 0.085583 | -0.044405 | 60.2551 | 60.2769 | 60.2093 | 60.1308 | 61.2859 | 61.3235 | 60.9552 | 61.2528 | 61.3203 | 61.2312 | 61.1635 | 61.1734 | 61.1889 | 61.284 | 61.154 | 60.2963 | 60.3181 | 60.2505 | 60.172 | 61.3271 | 61.3647 | 60.9964 | 61.294 | -1.0308 | -0.7001 | -1.0766 | -0.74589
242.375 | 121.9254 | -61.1755 | 60.3699 | 0.11269 | 0.028162 | -0.025735 | -0.029595 | -0.004937 | 0.081005 | -0.03067 | 60.2551 | 60.2769 | 60.2047 | 60.1308 | 61.2905 | 61.3189 | 60.9506 | 61.2574 | 61.2882 | 61.2037 | 61.1498 | 61.1459 | 61.1706 | 61.2565 | 61.1449 | 60.2963 | 60.3181 | 60.2459 | 60.172 | 61.3317 | 61.3601 | 60.9918 | 61.2986 | -1.0353 | -0.69552 | -1.0857 | -0.74589
244.1094 | 121.9208 | -61.1801 | 60.379 | 0.11727 | 0.037319 | -0.025735 | -0.025017 | -0.000359 | 0.081005 | -0.039826 | 60.2505 | 60.2861 | 60.2047 | 60.1354 | 61.2859 | 61.3281 | 60.9506 | 61.2574 | 61.2974 | 61.2174 | 61.1544 | 61.1551 | 61.1798 | 61.2611 | 61.1403 | 60.2917 | 60.3273 | 60.2459 | 60.1766 | 61.3271 | 61.3693 | 60.9918 | 61.2986 | -1.0353 | -0.7001 | -1.0811 | -0.74589
245.7969 | 121.9391 | -61.2488 | 60.2875 | 0.11727 | 0.041898 | -0.021157 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2551 | 60.2769 | 60.2139 | 60.14 | 61.2859 | 61.3281 | 60.9369 | 61.2528 | 61.3661 | 61.2907 | 61.2276 | 61.2283 | 61.2438 | 61.3344 | 61.2135 | 60.2963 | 60.3181 | 60.2551 | 60.1812 | 61.3271 | 61.3693 | 60.9781 | 61.294 | -1.0308 | -0.68179 | -1.072 | -0.723
247.5469 | 121.8063 | -61.203 | 60.4294 | 0.11727 | 0.03274 | -0.021157 | -0.025017 | -0.000359 | 0.081005 | -0.039826 | 60.2597 | 60.2815 | 60.2185 | 60.14 | 61.2813 | 61.3235 | 60.9461 | 61.2482 | 61.3203 | 61.2357 | 61.1818 | 61.178 | 61.2026 | 61.284 | 61.1632 | 60.3009 | 60.3227 | 60.2597 | 60.1812 | 61.3225 | 61.3647 | 60.9873 | 61.2894 | -1.0216 | -0.68636 | -1.0628 | -0.72758
249.2812 | 121.8292 | -61.2396 | 60.3882 | 0.12643 | 0.037319 | -0.025735 | -0.029595 | -0.009515 | 0.081005 | -0.035248 | 60.2551 | 60.2815 | 60.2139 | 60.1354 | 61.2813 | 61.3235 | 60.9415 | 61.2528 | 61.3661 | 61.2769 | 61.2139 | 61.21 | 61.2301 | 61.3206 | 61.2044 | 60.2963 | 60.3227 | 60.2551 | 60.1766 | 61.3225 | 61.3647 | 60.9827 | 61.294 | -1.0262 | -0.68636 | -1.0674 | -0.72758
250.9688 | 121.843 | -61.2671 | 60.3561 | 0.11727 | 0.037319 | -0.025735 | -0.029595 | -0.000359 | 0.090161 | -0.035248 | 60.2551 | 60.2769 | 60.2093 | 60.14 | 61.2813 | 61.3189 | 60.9461 | 61.2482 | 61.3844 | 61.3044 | 61.2414 | 61.2375 | 61.2667 | 61.3573 | 61.2318 | 60.2963 | 60.3181 | 60.2505 | 60.1812 | 61.3225 | 61.3601 | 60.9873 | 61.2894 | -1.0262 | -0.69094 | -1.072 | -0.73674
252.7031 | 121.8979 | -61.235 | 60.3516 | 0.12185 | 0.041898 | -0.025735 | -0.029595 | -0.009515 | 0.076426 | -0.035248 | 60.2597 | 60.2723 | 60.2047 | 60.1354 | 61.2859 | 61.3235 | 60.9506 | 61.2528 | 61.3569 | 61.2769 | 61.2093 | 61.2055 | 61.2255 | 61.3115 | 61.1998 | 60.3009 | 60.3135 | 60.2459 | 60.1766 | 61.3271 | 61.3647 | 60.9918 | 61.294 | -1.0262 | -0.69094 | -1.0811 | -0.74589
254.375 | 121.9574 | -61.1526 | 60.379 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.014093 | 0.081005 | -0.039826 | 60.2551 | 60.2723 | 60.2093 | 60.1354 | 61.2905 | 61.3235 | 60.9598 | 61.2482 | 61.2699 | 61.19 | 61.1315 | 61.1231 | 61.1386 | 61.2337 | 61.1128 | 60.2963 | 60.3135 | 60.2505 | 60.1766 | 61.3317 | 61.3647 | 61.001 | 61.2894 | -1.0353 | -0.70468 | -1.0811 | -0.75047
256.125 | 121.907 | -61.2625 | 60.2692 | 0.12185 | 0.037319 | -0.025735 | -0.029595 | -0.000359 | 0.081005 | -0.035248 | 60.2551 | 60.2815 | 60.2139 | 60.1445 | 61.2905 | 61.3235 | 60.9461 | 61.2574 | 61.3844 | 61.2998 | 61.2368 | 61.2329 | 61.2622 | 61.3435 | 61.2273 | 60.2963 | 60.3227 | 60.2551 | 60.1857 | 61.3317 | 61.3647 | 60.9873 | 61.2986 | -1.0353 | -0.69094 | -1.0766 | -0.73216
257.7969 | 121.8292 | -61.2396 | 60.3882 | 0.11727 | 0.037319 | -0.030314 | -0.029595 | -0.004937 | 0.085583 | -0.035248 | 60.246 | 60.2861 | 60.2093 | 60.1354 | 61.2813 | 61.3235 | 60.9506 | 61.2528 | 61.3569 | 61.2769 | 61.2093 | 61.21 | 61.2347 | 61.3252 | 61.2044 | 60.2872 | 60.3273 | 60.2505 | 60.1766 | 61.3225 | 61.3647 | 60.9918 | 61.294 | -1.0353 | -0.70468 | -1.072 | -0.74132
259.5312 | 121.962 | -61.171 | 60.3882 | 0.10812 | 0.028162 | -0.034893 | -0.038752 | -0.004937 | 0.085583 | -0.035248 | 60.2551 | 60.2769 | 60.2047 | 60.1354 | 61.2813 | 61.3235 | 60.9506 | 61.2528 | 61.2791 | 61.1991 | 61.1361 | 61.1322 | 61.166 | 61.2565 | 61.1357 | 60.2963 | 60.3181 | 60.2459 | 60.1766 | 61.3225 | 61.3647 | 60.9918 | 61.294 | -1.0262 | -0.69552 | -1.0766 | -0.74589
261.2812 | 121.907 | -61.2717 | 60.2692 | 0.12643 | 0.037319 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2597 | 60.2815 | 60.2139 | 60.14 | 61.2813 | 61.3281 | 60.9461 | 61.2528 | 61.3981 | 61.309 | 61.2459 | 61.2512 | 61.2667 | 61.3573 | 61.2364 | 60.3009 | 60.3227 | 60.2551 | 60.1812 | 61.3225 | 61.3693 | 60.9873 | 61.294 | -1.0216 | -0.68636 | -1.0674 | -0.73216
262.9688 | 121.9437 | -61.1572 | 60.3836 | 0.11727 | 0.037319 | -0.025735 | -0.029595 | -0.009515 | 0.076426 | -0.035248 | 60.2551 | 60.2769 | 60.2185 | 60.1308 | 61.2905 | 61.3235 | 60.9598 | 61.2482 | 61.2745 | 61.1945 | 61.1315 | 61.1276 | 61.1477 | 61.2337 | 61.122 | 60.2963 | 60.3181 | 60.2597 | 60.172 | 61.3317 | 61.3647 | 61.001 | 61.2894 | -1.0353 | -0.70468 | -1.072 | -0.74132
264.7188 | 121.9299 | -61.171 | 60.3836 | 0.12185 | 0.03274 | -0.034893 | -0.029595 | -0.009515 | 0.081005 | -0.039826 | 60.2551 | 60.2769 | 60.2047 | 60.1354 | 61.2905 | 61.3235 | 60.9552 | 61.2528 | 61.2928 | 61.2037 | 61.1361 | 61.1414 | 61.1614 | 61.252 | 61.1311 | 60.2963 | 60.3181 | 60.2459 | 60.1766 | 61.3317 | 61.3647 | 60.9964 | 61.294 | -1.0353 | -0.7001 | -1.0857 | -0.75047
266.4062 | 121.8979 | -61.2259 | 60.347 | 0.11727 | 0.03274 | -0.030314 | -0.029595 | -0.009515 | 0.076426 | -0.035248 | 60.2551 | 60.2815 | 60.2093 | 60.1354 | 61.2859 | 61.3327 | 60.9506 | 61.2574 | 61.3432 | 61.2586 | 61.1956 | 61.1963 | 61.2164 | 61.3023 | 61.1906 | 60.2963 | 60.3227 | 60.2505 | 60.1766 | 61.3271 | 61.3739 | 60.9918 | 61.2986 | -1.0308 | -0.69552 | -1.0766 | -0.74132
268.1562 | 121.843 | -61.2259 | 60.3973 | 0.11727 | 0.041898 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.039826 | 60.2505 | 60.2815 | 60.2185 | 60.1354 | 61.2859 | 61.3189 | 60.9461 | 61.2619 | 61.3432 | 61.2678 | 61.1956 | 61.2009 | 61.2164 | 61.3161 | 61.1861 | 60.2917 | 60.3227 | 60.2597 | 60.1766 | 61.3271 | 61.3601 | 60.9873 | 61.3031 | -1.0353 | -0.69552 | -1.0674 | -0.72758
269.9062 | 121.8246 | -61.2122 | 60.3836 | 0.12185 | 0.041898 | -0.025735 | -0.029595 | -0.004937 | 0.085583 | -0.039826 | 60.2597 | 60.2769 | 60.2185 | 60.14 | 61.2859 | 61.3189 | 60.9506 | 61.2528 | 61.334 | 61.2541 | 61.1864 | 61.1826 | 61.2072 | 61.2977 | 61.1723 | 60.3009 | 60.3181 | 60.2597 | 60.1812 | 61.3271 | 61.3601 | 60.9918 | 61.294 | -1.0262 | -0.69094 | -1.0674 | -0.73216
271.5938 | 121.9254 | -61.2717 | 60.2921 | 0.12185 | 0.041898 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.039826 | 60.2597 | 60.2815 | 60.2139 | 60.1354 | 61.2859 | 61.3189 | 60.9506 | 61.2574 | 61.3935 | 61.3136 | 61.2459 | 61.2512 | 61.2667 | 61.3573 | 61.2318 | 60.3009 | 60.3227 | 60.2551 | 60.1766 | 61.3271 | 61.3601 | 60.9918 | 61.2986 | -1.0262 | -0.69094 | -1.072 | -0.73674
273.3281 | 121.8475 | -61.2625 | 60.3149 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.004937 | 0.09474 | -0.03067 | 60.2643 | 60.2769 | 60.2093 | 60.1354 | 61.2859 | 61.3235 | 60.9552 | 61.2528 | 61.3798 | 61.2998 | 61.2414 | 61.2329 | 61.2576 | 61.3573 | 61.2318 | 60.3055 | 60.3181 | 60.2505 | 60.1766 | 61.3271 | 61.3647 | 60.9964 | 61.294 | -1.0216 | -0.69094 | -1.0766 | -0.74589
275.0781 | 121.8796 | -61.2305 | 60.3241 | 0.11727 | 0.041898 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.039826 | 60.2597 | 60.2769 | 60.2093 | 60.14 | 61.2905 | 61.3235 | 60.9415 | 61.2574 | 61.3477 | 61.2724 | 61.2002 | 61.2009 | 61.221 | 61.3161 | 61.1906 | 60.3009 | 60.3181 | 60.2505 | 60.1812 | 61.3317 | 61.3647 | 60.9827 | 61.2986 | -1.0308 | -0.68178 | -1.0811 | -0.73216
276.8125 | 121.8384 | -61.2534 | 60.347 | 0.11727 | 0.041898 | -0.021157 | -0.025017 | -0.004937 | 0.085583 | -0.03067 | 60.2505 | 60.2815 | 60.2093 | 60.1354 | 61.2905 | 61.3281 | 60.9415 | 61.2574 | 61.3706 | 61.2953 | 61.2322 | 61.2283 | 61.2484 | 61.3389 | 61.2227 | 60.2917 | 60.3227 | 60.2505 | 60.1766 | 61.3317 | 61.3693 | 60.9827 | 61.2986 | -1.0399 | -0.69094 | -1.0811 | -0.73216
278.5625 | 121.8155 | -61.2213 | 60.4111 | 0.11727 | 0.041898 | -0.021157 | -0.034174 | -0.004937 | 0.090161 | -0.039826 | 60.2597 | 60.2861 | 60.2185 | 60.1354 | 61.2859 | 61.3235 | 60.9415 | 61.2528 | 61.3386 | 61.2632 | 61.2002 | 61.1871 | 61.2164 | 61.3115 | 61.1815 | 60.3009 | 60.3273 | 60.2597 | 60.1766 | 61.3271 | 61.3647 | 60.9827 | 61.294 | -1.0262 | -0.68178 | -1.0674 | -0.723
280.2969 | 121.8338 | -61.2396 | 60.379 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | -0.009515 | 0.090161 | -0.035248 | 60.2551 | 60.2815 | 60.2139 | 60.1308 | 61.2859 | 61.3281 | 60.9461 | 61.2528 | 61.3569 | 61.2769 | 61.2185 | 61.21 | 61.2301 | 61.3298 | 61.2044 | 60.2963 | 60.3227 | 60.2551 | 60.172 | 61.3271 | 61.3693 | 60.9873 | 61.294 | -1.0308 | -0.69094 | -1.072 | -0.73216
282.0469 | 121.8384 | -61.2579 | 60.3241 | 0.12185 | 0.037319 | -0.021157 | -0.025017 | -0.004937 | 0.099318 | -0.035248 | 60.2597 | 60.2861 | 60.2139 | 60.14 | 61.2721 | 61.3281 | 60.9552 | 61.2574 | 61.3798 | 61.2953 | 61.2368 | 61.2329 | 61.253 | 61.3573 | 61.2227 | 60.3009 | 60.3273 | 60.2551 | 60.1812 | 61.3133 | 61.3693 | 60.9964 | 61.2986 | -1.0124 | -0.69552 | -1.0582 | -0.74132
283.7344 | 121.9208 | -61.2625 | 60.3058 | 0.12185 | 0.041898 | -0.030314 | -0.025017 | -0.009515 | 0.085583 | -0.044405 | 60.2551 | 60.2861 | 60.2139 | 60.1308 | 61.2905 | 61.3189 | 60.9415 | 61.2528 | 61.3844 | 61.3044 | 61.2322 | 61.2375 | 61.253 | 61.3481 | 61.2181 | 60.2963 | 60.3273 | 60.2551 | 60.172 | 61.3317 | 61.3601 | 60.9827 | 61.294 | -1.0353 | -0.68636 | -1.0766 | -0.72758
285.4844 | 121.875 | -61.2488 | 60.3378 | 0.12643 | 0.037319 | -0.030314 | -0.029595 | -0.004937 | 0.090161 | -0.039826 | 60.2597 | 60.2815 | 60.2093 | 60.14 | 61.2859 | 61.3189 | 60.9415 | 61.2574 | 61.3752 | 61.2861 | 61.2185 | 61.2192 | 61.2438 | 61.3389 | 61.209 | 60.3009 | 60.3227 | 60.2505 | 60.1812 | 61.3271 | 61.3601 | 60.9827 | 61.2986 | -1.0262 | -0.68178 | -1.0766 | -0.73216
287.1719 | 121.9437 | -61.2579 | 60.2646 | 0.12185 | 0.041898 | -0.025735 | -0.029595 | -0.009515 | 0.085583 | -0.035248 | 60.246 | 60.2815 | 60.2139 | 60.1308 | 61.2859 | 61.3235 | 60.9415 | 61.2528 | 61.3798 | 61.2998 | 61.2322 | 61.2283 | 61.2484 | 61.3435 | 61.2227 | 60.2872 | 60.3227 | 60.2551 | 60.172 | 61.3271 | 61.3647 | 60.9827 | 61.294 | -1.0399 | -0.69552 | -1.072 | -0.72758
288.9219 | 121.9482 | -61.1938 | 60.3836 | 0.11727 | 0.03274 | -0.030314 | -0.025017 | -0.009515 | 0.085583 | -0.039826 | 60.2505 | 60.2815 | 60.2139 | 60.1354 | 61.2905 | 61.3281 | 60.9552 | 61.2619 | 61.3111 | 61.2266 | 61.1635 | 61.1688 | 61.1843 | 61.2794 | 61.154 | 60.2917 | 60.3227 | 60.2551 | 60.1766 | 61.3317 | 61.3693 | 60.9964 | 61.3031 | -1.0399 | -0.70468 | -1.0766 | -0.74132
290.6719 | 121.8155 | -61.2305 | 60.4202 | 0.11727 | 0.037319 | -0.025735 | -0.029595 | -0.000359 | 0.085583 | -0.035248 | 60.2551 | 60.2815 | 60.2185 | 60.1308 | 61.2905 | 61.3189 | 60.9506 | 61.2574 | 61.3477 | 61.2678 | 61.2047 | 61.2009 | 61.2301 | 61.3161 | 61.1952 | 60.2963 | 60.3227 | 60.2597 | 60.172 | 61.3317 | 61.3601 | 60.9918 | 61.2986 | -1.0353 | -0.69552 | -1.072 | -0.73216
292.3594 | 121.9162 | -61.171 | 60.4019 | 0.11727 | 0.041898 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.039826 | 60.2551 | 60.2861 | 60.2093 | 60.1308 | 61.2859 | 61.3235 | 60.9552 | 61.2528 | 61.2882 | 61.2129 | 61.1406 | 61.1414 | 61.1614 | 61.2565 | 61.1311 | 60.2963 | 60.3273 | 60.2505 | 60.172 | 61.3271 | 61.3647 | 60.9964 | 61.294 | -1.0308 | -0.7001 | -1.0766 | -0.74589
294.1094 | 121.8704 | -61.2717 | 60.3516 | 0.11727 | 0.028162 | -0.030314 | -0.029595 | -0.004937 | 0.09474 | -0.035248 | 60.2643 | 60.2907 | 60.2139 | 60.14 | 61.2859 | 61.3235 | 60.9415 | 61.2528 | 61.3889 | 61.2998 | 61.2414 | 61.2421 | 61.2667 | 61.3664 | 61.2364 | 60.3055 | 60.3319 | 60.2551 | 60.1812 | 61.3271 | 61.3647 | 60.9827 | 61.294 | -1.0216 | -0.67721 | -1.072 | -0.72758
295.7969 | 121.9574 | -61.1755 | 60.3653 | 0.11269 | 0.03274 | -0.025735 | -0.029595 | -0.009515 | 0.081005 | -0.039826 | 60.2505 | 60.2815 | 60.2093 | 60.1308 | 61.2905 | 61.3327 | 60.9461 | 61.2619 | 61.2882 | 61.2083 | 61.1498 | 61.1459 | 61.166 | 61.2565 | 61.1357 | 60.2917 | 60.3227 | 60.2505 | 60.172 | 61.3317 | 61.3739 | 60.9873 | 61.3031 | -1.0399 | -0.69552 | -1.0811 | -0.73674
297.5312 | 121.9025 | -61.235 | 60.3378 | 0.11727 | 0.023583 | -0.025735 | -0.025017 | -0.014093 | 0.090161 | -0.03067 | 60.2643 | 60.2861 | 60.2185 | 60.1308 | 61.2859 | 61.3235 | 60.9461 | 61.2574 | 61.3523 | 61.2586 | 61.2093 | 61.21 | 61.221 | 61.3252 | 61.2044 | 60.3055 | 60.3273 | 60.2597 | 60.172 | 61.3271 | 61.3647 | 60.9873 | 61.2986 | -1.0216 | -0.68179 | -1.0674 | -0.72758
299.2812 | 121.8338 | -61.2854 | 60.3973 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | -0.004937 | 0.090161 | -0.035248 | 60.2643 | 60.2815 | 60.2093 | 60.1308 | 61.2859 | 61.3327 | 60.9506 | 61.2574 | 61.4073 | 61.3181 | 61.2642 | 61.2604 | 61.2805 | 61.3756 | 61.2502 | 60.3055 | 60.3227 | 60.2505 | 60.172 | 61.3271 | 61.3739 | 60.9918 | 61.2986 | -1.0216 | -0.68636 | -1.0766 | -0.74132
300.9688 | 121.9299 | -61.1618 | 60.379 | 0.11727 | 0.023583 | -0.025735 | -0.029595 | -0.009515 | 0.090161 | -0.035248 | 60.2505 | 60.2815 | 60.2093 | 60.1354 | 61.2905 | 61.3281 | 60.9461 | 61.2528 | 61.2791 | 61.1854 | 61.1361 | 61.1322 | 61.1523 | 61.252 | 61.1266 | 60.2917 | 60.3227 | 60.2505 | 60.1766 | 61.3317 | 61.3693 | 60.9873 | 61.294 | -1.0399 | -0.69552 | -1.0811 | -0.73674
302.7188 | 121.8201 | -61.2946 | 60.3287 | 0.12643 | 0.037319 | -0.025735 | -0.025017 | -0.004937 | 0.085583 | -0.03067 | 60.2551 | 60.2815 | 60.2139 | 60.14 | 61.2813 | 61.3189 | 60.9506 | 61.2528 | 61.421 | 61.3319 | 61.2688 | 61.2695 | 61.2896 | 61.3801 | 61.2639 | 60.2963 | 60.3227 | 60.2551 | 60.1812 | 61.3225 | 61.3601 | 60.9918 | 61.294 | -1.0262 | -0.69552 | -1.0674 | -0.73674
304.4531 | 121.9162 | -61.235 | 60.3333 | 0.11727 | 0.028162 | -0.034893 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2643 | 60.2907 | 60.2093 | 60.1308 | 61.295 | 61.3281 | 60.9461 | 61.2528 | 61.3523 | 61.2632 | 61.2002 | 61.21 | 61.2301 | 61.3206 | 61.1998 | 60.3055 | 60.3319 | 60.2505 | 60.172 | 61.3362 | 61.3693 | 60.9873 | 61.294 | -1.0308 | -0.68179 | -1.0857 | -0.73674
306.2031 | 121.9208 | -61.2808 | 60.3149 | 0.12185 | 0.023583 | -0.025735 | -0.029595 | -0.004937 | 0.090161 | -0.03067 | 60.2551 | 60.2815 | 60.2139 | 60.1354 | 61.2813 | 61.3189 | 60.9415 | 61.2528 | 61.4027 | 61.3044 | 61.2551 | 61.2512 | 61.2759 | 61.371 | 61.2502 | 60.2963 | 60.3227 | 60.2551 | 60.1766 | 61.3225 | 61.3601 | 60.9827 | 61.294 | -1.0262 | -0.68636 | -1.0674 | -0.72758
307.9375 | 121.8613 | -61.2579 | 60.3378 | 0.12185 | 0.037319 | -0.025735 | -0.029595 | -0.009515 | 0.090161 | -0.03067 | 60.2643 | 60.2815 | 60.2139 | 60.1354 | 61.2859 | 61.3235 | 60.9506 | 61.2528 | 61.3798 | 61.2953 | 61.2322 | 61.2283 | 61.2484 | 61.3481 | 61.2273 | 60.3055 | 60.3227 | 60.2551 | 60.1766 | 61.3271 | 61.3647 | 60.9918 | 61.294 | -1.0216 | -0.68636 | -1.072 | -0.73674
309.625 | 121.8109 | -61.3129 | 60.2875 | 0.11727 | 0.041898 | -0.025735 | -0.020438 | -0.004937 | 0.090161 | -0.03067 | 60.2643 | 60.2861 | 60.2185 | 60.1354 | 61.295 | 61.3281 | 60.9461 | 61.2528 | 61.4301 | 61.3548 | 61.2871 | 61.2924 | 61.3079 | 61.403 | 61.2822 | 60.3055 | 60.3273 | 60.2597 | 60.1766 | 61.3362 | 61.3693 | 60.9873 | 61.294 | -1.0308 | -0.68179 | -1.0766 | -0.72758
311.3594 | 121.8201 | -61.2534 | 60.379 | 0.12185 | 0.03274 | -0.025735 | -0.020438 | -0.014093 | 0.085583 | -0.044405 | 60.2551 | 60.2815 | 60.2139 | 60.1354 | 61.295 | 61.3235 | 60.9461 | 61.2574 | 61.3752 | 61.2861 | 61.2276 | 61.2329 | 61.2393 | 61.3389 | 61.209 | 60.2963 | 60.3227 | 60.2551 | 60.1766 | 61.3362 | 61.3647 | 60.9873 | 61.2986 | -1.0399 | -0.69094 | -1.0811 | -0.73216
313.1094 | 121.9437 | -61.1801 | 60.379 | 0.12643 | 0.037319 | -0.030314 | -0.034174 | -0.009515 | 0.090161 | -0.044405 | 60.2643 | 60.2769 | 60.2139 | 60.1354 | 61.2905 | 61.3189 | 60.9506 | 61.2482 | 61.3065 | 61.2174 | 61.1498 | 61.1459 | 61.1706 | 61.2703 | 61.1357 | 60.3055 | 60.3181 | 60.2551 | 60.1766 | 61.3317 | 61.3601 | 60.9918 | 61.2894 | -1.0262 | -0.68636 | -1.0766 | -0.73674
314.7812 | 121.8201 | -61.2991 | 60.3195 | 0.12643 | 0.028162 | -0.025735 | -0.020438 | -0.004937 | 0.09474 | -0.03067 | 60.2643 | 60.2907 | 60.2139 | 60.1308 | 61.2859 | 61.3144 | 60.9415 | 61.2574 | 61.4256 | 61.3273 | 61.2734 | 61.2787 | 61.2942 | 61.3939 | 61.2685 | 60.3055 | 60.3319 | 60.2551 | 60.172 | 61.3271 | 61.3556 | 60.9827 | 61.2986 | -1.0216 | -0.67721 | -1.072 | -0.72758
316.5312 | 121.9666 | -61.1755 | 60.3882 | 0.11727 | 0.028162 | -0.034893 | -0.034174 | -0.014093 | 0.085583 | -0.039826 | 60.2551 | 60.2769 | 60.2139 | 60.1354 | 61.2859 | 61.3235 | 60.9461 | 61.2528 | 61.2928 | 61.2037 | 61.1406 | 61.1414 | 61.1614 | 61.2611 | 61.1357 | 60.2963 | 60.3181 | 60.2551 | 60.1766 | 61.3271 | 61.3647 | 60.9873 | 61.294 | -1.0308 | -0.69094 | -1.072 | -0.73216
318.2969 | 121.9391 | -61.2534 | 60.2783 | 0.12185 | 0.028162 | -0.021157 | -0.029595 | -0.009515 | 0.090161 | -0.026092 | 60.2597 | 60.2861 | 60.2185 | 60.14 | 61.2905 | 61.3327 | 60.9415 | 61.2574 | 61.3752 | 61.2815 | 61.2322 | 61.2238 | 61.2438 | 61.3435 | 61.2273 | 60.3009 | 60.3273 | 60.2597 | 60.1812 | 61.3317 | 61.3739 | 60.9827 | 61.2986 | -1.0308 | -0.68178 | -1.072 | -0.723
319.9844 | 121.8292 | -61.2122 | 60.4111 | 0.11727 | 0.023583 | -0.030314 | -0.034174 | -0.014093 | 0.090161 | -0.035248 | 60.2643 | 60.2861 | 60.2139 | 60.14 | 61.2859 | 61.3235 | 60.9461 | 61.2528 | 61.3294 | 61.2357 | 61.1818 | 61.178 | 61.1981 | 61.3023 | 61.1769 | 60.3055 | 60.3273 | 60.2551 | 60.1812 | 61.3271 | 61.3647 | 60.9873 | 61.294 | -1.0216 | -0.68179 | -1.072 | -0.73216
321.7344 | 121.9025 | -61.1847 | 60.4065 | 0.11727 | 0.028162 | -0.034893 | -0.025017 | -0.014093 | 0.090161 | -0.03067 | 60.2597 | 60.2815 | 60.2093 | 60.14 | 61.2905 | 61.3189 | 60.9506 | 61.2574 | 61.302 | 61.2129 | 61.1498 | 61.1597 | 61.1706 | 61.2749 | 61.154 | 60.3009 | 60.3227 | 60.2505 | 60.1812 | 61.3317 | 61.3601 | 60.9918 | 61.2986 | -1.0308 | -0.69094 | -1.0811 | -0.74132
323.5 | 121.9162 | -61.1847 | 60.3699 | 0.11727 | 0.023583 | -0.025735 | -0.034174 | -0.009515 | 0.085583 | -0.039826 | 60.2551 | 60.2907 | 60.2139 | 60.1354 | 61.2905 | 61.3281 | 60.9506 | 61.2619 | 61.302 | 61.2083 | 61.159 | 61.1505 | 61.1752 | 61.2703 | 61.1449 | 60.2963 | 60.3319 | 60.2551 | 60.1766 | 61.3317 | 61.3693 | 60.9918 | 61.3031 | -1.0353 | -0.69552 | -1.0766 | -0.73674
325.25 | 121.907 | -61.2762 | 60.2783 | 0.12185 | 0.023583 | -0.025735 | -0.020438 | -0.014093 | 0.081005 | -0.03067 | 60.2643 | 60.2861 | 60.2139 | 60.1308 | 61.2859 | 61.3281 | 60.9415 | 61.2528 | 61.3981 | 61.2998 | 61.2505 | 61.2558 | 61.2622 | 61.3573 | 61.2456 | 60.3055 | 60.3273 | 60.2551 | 60.172 | 61.3271 | 61.3693 | 60.9827 | 61.294 | -1.0216 | -0.67721 | -1.072 | -0.72758
326.9375 | 121.8567 | -61.2442 | 60.3928 | 0.12643 | 0.028162 | -0.021157 | -0.025017 | -0.000359 | 0.09474 | -0.03067 | 60.2643 | 60.2815 | 60.2139 | 60.1445 | 61.2905 | 61.3281 | 60.9415 | 61.2528 | 61.3706 | 61.2724 | 61.223 | 61.2192 | 61.2438 | 61.3389 | 61.2135 | 60.3055 | 60.3227 | 60.2551 | 60.1857 | 61.3317 | 61.3693 | 60.9827 | 61.294 | -1.0262 | -0.67721 | -1.0766 | -0.72758
328.6875 | 121.843 | -61.3083 | 60.3287 | 0.12185 | 0.019004 | -0.025735 | -0.025017 | -0.004937 | 0.090161 | -0.039826 | 60.2643 | 60.2861 | 60.2185 | 60.1354 | 61.2859 | 61.3281 | 60.9369 | 61.2528 | 61.4301 | 61.3273 | 61.2826 | 61.2833 | 61.3034 | 61.3985 | 61.2685 | 60.3055 | 60.3273 | 60.2597 | 60.1766 | 61.3271 | 61.3693 | 60.9781 | 61.294 | -1.0216 | -0.67263 | -1.0674 | -0.71842
330.4375 | 121.9391 | -61.1847 | 60.4019 | 0.11269 | 0.028162 | -0.025735 | -0.034174 | -0.009515 | 0.090161 | -0.039826 | 60.2643 | 60.2815 | 60.2139 | 60.14 | 61.2813 | 61.3281 | 60.9461 | 61.2574 | 61.2974 | 61.2129 | 61.159 | 61.1505 | 61.1752 | 61.2749 | 61.1449 | 60.3055 | 60.3227 | 60.2551 | 60.1812 | 61.3225 | 61.3693 | 60.9873 | 61.2986 | -1.017 | -0.68179 | -1.0674 | -0.73216
332.1875 | 121.8292 | -61.2946 | 60.3104 | 0.12185 | 0.023583 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.03067 | 60.2643 | 60.2769 | 60.2231 | 60.1308 | 61.2859 | 61.3189 | 60.9369 | 61.2482 | 61.4164 | 61.3181 | 61.2642 | 61.2695 | 61.285 | 61.3847 | 61.2639 | 60.3055 | 60.3181 | 60.2643 | 60.172 | 61.3271 | 61.3601 | 60.9781 | 61.2894 | -1.0216 | -0.67263 | -1.0628 | -0.71385
333.875 | 121.8613 | -61.2396 | 60.3653 | 0.12643 | 0.023583 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2643 | 60.2815 | 60.2231 | 60.14 | 61.2905 | 61.3189 | 60.9461 | 61.2619 | 61.3661 | 61.2632 | 61.2139 | 61.2192 | 61.2347 | 61.3252 | 61.2044 | 60.3055 | 60.3227 | 60.2643 | 60.1812 | 61.3317 | 61.3601 | 60.9873 | 61.3031 | -1.0262 | -0.68179 | -1.0674 | -0.723
335.6094 | 121.7972 | -61.3129 | 60.3241 | 0.12185 | 0.023583 | -0.030314 | -0.025017 | -0.004937 | 0.085583 | -0.039826 | 60.2643 | 60.2769 | 60.2139 | 60.1354 | 61.2859 | 61.3281 | 60.9506 | 61.2528 | 61.4347 | 61.3364 | 61.2826 | 61.2878 | 61.3079 | 61.3984 | 61.273 | 60.3055 | 60.3181 | 60.2551 | 60.1766 | 61.3271 | 61.3693 | 60.9918 | 61.294 | -1.0216 | -0.68636 | -1.072 | -0.73674
337.3594 | 121.8521 | -61.2396 | 60.4111 | 0.12185 | 0.019004 | -0.030314 | -0.025017 | -0.014093 | 0.090161 | -0.03067 | 60.2597 | 60.2861 | 60.2185 | 60.1445 | 61.2767 | 61.3281 | 60.9461 | 61.2574 | 61.3615 | 61.2586 | 61.2093 | 61.2146 | 61.2255 | 61.3298 | 61.209 | 60.3009 | 60.3273 | 60.2597 | 60.1857 | 61.3179 | 61.3693 | 60.9873 | 61.2986 | -1.017 | -0.68636 | -1.0582 | -0.72758
339.1094 | 121.9162 | -61.2167 | 60.3653 | 0.11727 | 0.028162 | -0.034893 | -0.029595 | -0.004937 | 0.081005 | -0.044405 | 60.2643 | 60.2769 | 60.2185 | 60.14 | 61.2859 | 61.3281 | 60.9506 | 61.2528 | 61.334 | 61.2449 | 61.1818 | 61.1871 | 61.2118 | 61.2977 | 61.1723 | 60.3055 | 60.3181 | 60.2597 | 60.1812 | 61.3271 | 61.3693 | 60.9918 | 61.294 | -1.0216 | -0.68636 | -1.0674 | -0.73216
340.7969 | 121.9299 | -61.2808 | 60.2783 | 0.11727 | 0.023583 | -0.030314 | -0.029595 | -0.009515 | 0.081005 | -0.035248 | 60.2643 | 60.2815 | 60.2185 | 60.14 | 61.2996 | 61.3235 | 60.9369 | 61.2528 | 61.3981 | 61.3044 | 61.2505 | 61.2512 | 61.2713 | 61.3618 | 61.2456 | 60.3055 | 60.3227 | 60.2597 | 60.1812 | 61.3408 | 61.3647 | 60.9781 | 61.294 | -1.0353 | -0.67263 | -1.0811 | -0.71842
342.5469 | 121.7972 | -61.2259 | 60.4065 | 0.12643 | 0.028162 | -0.025735 | -0.029595 | -0.004937 | 0.09474 | -0.039826 | 60.2643 | 60.2907 | 60.2185 | 60.14 | 61.2996 | 61.3327 | 60.9506 | 61.2528 | 61.3523 | 61.2541 | 61.2002 | 61.1963 | 61.221 | 61.3206 | 61.1861 | 60.3055 | 60.3319 | 60.2597 | 60.1812 | 61.3408 | 61.3739 | 60.9918 | 61.294 | -1.0353 | -0.68636 | -1.0811 | -0.73216
344.2969 | 121.907 | -61.2076 | 60.3928 | 0.12185 | 0.019004 | -0.034893 | -0.029595 | -0.004937 | 0.090161 | -0.039826 | 60.2597 | 60.2769 | 60.2231 | 60.1445 | 61.295 | 61.3235 | 60.9552 | 61.2528 | 61.3294 | 61.2266 | 61.1727 | 61.178 | 61.2026 | 61.2977 | 61.1678 | 60.3009 | 60.3181 | 60.2643 | 60.1857 | 61.3362 | 61.3647 | 60.9964 | 61.294 | -1.0353 | -0.69552 | -1.072 | -0.73216
345.9844 | 121.8384 | -61.3312 | 60.3149 | 0.11727 | 0.03274 | -0.034893 | -0.025017 | -0.004937 | 0.090161 | -0.035248 | 60.2643 | 60.2769 | 60.2185 | 60.14 | 61.2859 | 61.3189 | 60.9506 | 61.2574 | 61.4484 | 61.3639 | 61.2963 | 61.3062 | 61.3262 | 61.4213 | 61.2959 | 60.3055 | 60.3181 | 60.2597 | 60.1812 | 61.3271 | 61.3601 | 60.9918 | 61.2986 | -1.0216 | -0.68636 | -1.0674 | -0.73216
347.7344 | 121.8933 | -61.2396 | 60.3241 | 0.12185 | 0.028162 | -0.025735 | -0.029595 | -0.000359 | 0.085583 | -0.039826 | 60.2551 | 60.2861 | 60.2139 | 60.1354 | 61.2813 | 61.3281 | 60.9506 | 61.2574 | 61.3615 | 61.2678 | 61.2139 | 61.21 | 61.2393 | 61.3252 | 61.1998 | 60.2963 | 60.3273 | 60.2551 | 60.1766 | 61.3225 | 61.3693 | 60.9918 | 61.2986 | -1.0262 | -0.69552 | -1.0674 | -0.73674
349.4688 | 121.9528 | -61.1755 | 60.3607 | 0.11269 | 0.028162 | -0.034893 | -0.025017 | -0.009515 | 0.090161 | -0.026092 | 60.2551 | 60.2861 | 60.2185 | 60.14 | 61.2859 | 61.3281 | 60.9461 | 61.2574 | 61.2882 | 61.2037 | 61.1406 | 61.1505 | 61.166 | 61.2657 | 61.1494 | 60.2963 | 60.3273 | 60.2597 | 60.1812 | 61.3271 | 61.3693 | 60.9873 | 61.2986 | -1.0308 | -0.69094 | -1.0674 | -0.72758
351.1562 | 121.8842 | -61.2442 | 60.3516 | 0.12185 | 0.023583 | -0.030314 | -0.029595 | -0.004937 | 0.085583 | -0.044405 | 60.2689 | 60.2815 | 60.2139 | 60.14 | 61.2859 | 61.3281 | 60.9415 | 61.2619 | 61.3661 | 61.2678 | 61.2139 | 61.2146 | 61.2393 | 61.3298 | 61.1998 | 60.3101 | 60.3227 | 60.2551 | 60.1812 | 61.3271 | 61.3693 | 60.9827 | 61.3031 | -1.017 | -0.67263 | -1.072 | -0.72758
352.8438 | 121.907 | -61.2488 | 60.3333 | 0.11727 | 0.023583 | -0.034893 | -0.038752 | -0.004937 | 0.085583 | -0.03067 | 60.2643 | 60.2815 | 60.2093 | 60.1308 | 61.295 | 61.3281 | 60.9369 | 61.2482 | 61.3661 | 61.2724 | 61.2139 | 61.21 | 61.2438 | 61.3344 | 61.2181 | 60.3055 | 60.3227 | 60.2505 | 60.172 | 61.3362 | 61.3693 | 60.9781 | 61.2894 | -1.0308 | -0.67263 | -1.0857 | -0.72758
354.5938 | 121.8246 | -61.3129 | 60.3195 | 0.12643 | 0.023583 | -0.025735 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2689 | 60.2815 | 60.2185 | 60.14 | 61.2859 | 61.3235 | 60.9415 | 61.2574 | 61.4393 | 61.3364 | 61.2871 | 61.2878 | 61.3079 | 61.3984 | 61.2776 | 60.3101 | 60.3227 | 60.2597 | 60.1812 | 61.3271 | 61.3647 | 60.9827 | 61.2986 | -1.017 | -0.67263 | -1.0674 | -0.723
356.3125 | 121.9528 | -61.1755 | 60.3882 | 0.11727 | 0.023583 | -0.034893 | -0.029595 | -0.009515 | 0.090161 | -0.035248 | 60.2597 | 60.2861 | 60.2185 | 60.14 | 61.2905 | 61.3235 | 60.9461 | 61.2528 | 61.2928 | 61.1991 | 61.1406 | 61.1459 | 61.166 | 61.2657 | 61.1403 | 60.3009 | 60.3273 | 60.2597 | 60.1812 | 61.3317 | 61.3647 | 60.9873 | 61.294 | -1.0308 | -0.68636 | -1.072 | -0.72758
358 | 121.9299 | -61.203 | 60.3607 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | -0.009515 | 0.081005 | -0.035248 | 60.2551 | 60.2769 | 60.2139 | 60.14 | 61.295 | 61.3327 | 60.9552 | 61.2528 | 61.3249 | 61.222 | 61.1727 | 61.1734 | 61.1935 | 61.284 | 61.1678 | 60.2963 | 60.3181 | 60.2551 | 60.1812 | 61.3362 | 61.3739 | 60.9964 | 61.294 | -1.0399 | -0.7001 | -1.0811 | -0.74132
359.7344 | 121.9437 | -61.1801 | 60.3882 | 0.12643 | 0.028162 | -0.034893 | -0.025017 | -0.014093 | 0.090161 | -0.035248 | 60.2597 | 60.2815 | 60.2185 | 60.14 | 61.295 | 61.3327 | 60.9461 | 61.2528 | 61.3065 | 61.2083 | 61.1452 | 61.1551 | 61.166 | 61.2703 | 61.1449 | 60.3009 | 60.3227 | 60.2597 | 60.1812 | 61.3362 | 61.3739 | 60.9873 | 61.294 | -1.0353 | -0.68636 | -1.0766 | -0.72758
361.4062 | 121.9574 | -61.203 | 60.3607 | 0.11269 | 0.023583 | -0.025735 | -0.034174 | -0.009515 | 0.085583 | -0.035248 | 60.2505 | 60.2861 | 60.2231 | 60.14 | 61.2813 | 61.3281 | 60.9506 | 61.2528 | 61.3157 | 61.2266 | 61.1773 | 61.1688 | 61.1935 | 61.2886 | 61.1678 | 60.2917 | 60.3273 | 60.2643 | 60.1812 | 61.3225 | 61.3693 | 60.9918 | 61.294 | -1.0308 | -0.7001 | -1.0582 | -0.72758
363.1719 | 121.8338 | -61.29 | 60.3104 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | -0.004937 | 0.099318 | -0.035248 | 60.2643 | 60.2815 | 60.2185 | 60.14 | 61.2905 | 61.3281 | 60.9461 | 61.2574 | 61.4073 | 61.3181 | 61.2688 | 61.2695 | 61.285 | 61.3893 | 61.2547 | 60.3055 | 60.3227 | 60.2597 | 60.1812 | 61.3317 | 61.3693 | 60.9873 | 61.2986 | -1.0262 | -0.68179 | -1.072 | -0.72758
364.9219 | 121.9254 | -61.171 | 60.3653 | 0.11727 | 0.023583 | -0.034893 | -0.029595 | -0.014093 | 0.081005 | -0.039826 | 60.2597 | 60.2815 | 60.2231 | 60.1354 | 61.2859 | 61.3327 | 60.9415 | 61.2482 | 61.2882 | 61.1945 | 61.1361 | 61.1414 | 61.1569 | 61.252 | 61.1311 | 60.3009 | 60.3227 | 60.2643 | 60.1766 | 61.3271 | 61.3739 | 60.9827 | 61.2894 | -1.0262 | -0.68178 | -1.0628 | -0.71842
366.6094 | 121.9162 | -61.1893 | 60.3699 | 0.12185 | 0.019004 | -0.034893 | -0.034174 | -0.004937 | 0.085583 | -0.03067 | 60.2597 | 60.2861 | 60.2185 | 60.1354 | 61.2859 | 61.3235 | 60.9461 | 61.2574 | 61.3111 | 61.2083 | 61.1544 | 61.1551 | 61.1843 | 61.2749 | 61.1586 | 60.3009 | 60.3273 | 60.2597 | 60.1766 | 61.3271 | 61.3647 | 60.9873 | 61.2986 | -1.0262 | -0.68636 | -1.0674 | -0.72758
368.375 | 121.8933 | -61.2396 | 60.3561 | 0.12185 | 0.023583 | -0.021157 | -0.029595 | -0.014093 | 0.085583 | -0.03067 | 60.2643 | 60.2861 | 60.2185 | 60.14 | 61.2859 | 61.3235 | 60.9461 | 61.2528 | 61.3615 | 61.2632 | 61.2185 | 61.21 | 61.2255 | 61.3252 | 61.209 | 60.3055 | 60.3273 | 60.2597 | 60.1812 | 61.3271 | 61.3647 | 60.9873 | 61.294 | -1.0216 | -0.68179 | -1.0674 | -0.72758
370.0625 | 121.9391 | -61.1664 | 60.3516 | 0.12185 | 0.023583 | -0.025735 | -0.038752 | -0.009515 | 0.090161 | -0.035248 | 60.2689 | 60.2815 | 60.2185 | 60.1354 | 61.2905 | 61.3281 | 60.9415 | 61.2482 | 61.2882 | 61.19 | 61.1406 | 61.1276 | 61.1569 | 61.2565 | 61.1311 | 60.3101 | 60.3227 | 60.2597 | 60.1766 | 61.3317 | 61.3693 | 60.9827 | 61.2894 | -1.0216 | -0.67263 | -1.072 | -0.723
371.8125 | 121.8201 | -61.235 | 60.4477 | 0.12643 | 0.019004 | -0.030314 | -0.025017 | -0.004937 | 0.085583 | -0.03067 | 60.2597 | 60.2861 | 60.2093 | 60.14 | 61.295 | 61.3235 | 60.9461 | 61.2528 | 61.3615 | 61.254 | 61.2047 | 61.21 | 61.2301 | 61.3206 | 61.2044 | 60.3009 | 60.3273 | 60.2505 | 60.1812 | 61.3362 | 61.3647 | 60.9873 | 61.294 | -1.0353 | -0.68636 | -1.0857 | -0.73674
373.5938 | 121.8796 | -61.2122 | 60.3745 | 0.11269 | 0.023583 | -0.030314 | -0.034174 | -0.009515 | 0.081005 | -0.044405 | 60.2597 | 60.2861 | 60.2231 | 60.1354 | 61.2905 | 61.3327 | 60.9461 | 61.2665 | 61.3249 | 61.2357 | 61.1818 | 61.178 | 61.2026 | 61.2932 | 61.1678 | 60.3009 | 60.3273 | 60.2643 | 60.1766 | 61.3317 | 61.3739 | 60.9873 | 61.3077 | -1.0308 | -0.68636 | -1.0674 | -0.723
375.3438 | 121.8613 | -61.2808 | 60.3241 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | -0.004937 | 0.099318 | -0.026092 | 60.2597 | 60.2861 | 60.2231 | 60.14 | 61.2905 | 61.3189 | 60.9415 | 61.2619 | 61.4027 | 61.3044 | 61.2597 | 61.2558 | 61.2759 | 61.3801 | 61.2547 | 60.3009 | 60.3273 | 60.2643 | 60.1812 | 61.3317 | 61.3601 | 60.9827 | 61.3031 | -1.0308 | -0.68178 | -1.0674 | -0.71842
377.0156 | 121.8109 | -61.2854 | 60.3241 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | 0.008797 | 0.09474 | -0.035248 | 60.2643 | 60.2907 | 60.2231 | 60.14 | 61.2859 | 61.3189 | 60.9415 | 61.2574 | 61.4073 | 61.3044 | 61.2551 | 61.2558 | 61.2942 | 61.3801 | 61.2502 | 60.3055 | 60.3319 | 60.2643 | 60.1812 | 61.3271 | 61.3601 | 60.9827 | 61.2986 | -1.0216 | -0.67721 | -1.0628 | -0.71842
378.7812 | 121.9345 | -61.1755 | 60.3607 | 0.12185 | 0.019004 | -0.030314 | -0.025017 | -0.009515 | 0.085583 | -0.035248 | 60.2643 | 60.2907 | 60.2139 | 60.1354 | 61.2905 | 61.3281 | 60.9506 | 61.2528 | 61.2974 | 61.1945 | 61.1452 | 61.1505 | 61.166 | 61.2611 | 61.1403 | 60.3055 | 60.3319 | 60.2551 | 60.1766 | 61.3317 | 61.3693 | 60.9918 | 61.294 | -1.0262 | -0.68636 | -1.0766 | -0.73674
380.4688 | 121.7926 | -61.3266 | 60.3195 | 0.11727 | 0.014425 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.03067 | 60.2689 | 60.2861 | 60.2185 | 60.1445 | 61.2905 | 61.3235 | 60.9415 | 61.2574 | 61.4439 | 61.341 | 61.3009 | 61.3016 | 61.3262 | 61.4122 | 61.2959 | 60.3101 | 60.3273 | 60.2597 | 60.1857 | 61.3317 | 61.3647 | 60.9827 | 61.2986 | -1.0216 | -0.67263 | -1.072 | -0.723
382.2188 | 121.8979 | -61.2213 | 60.3607 | 0.12185 | 0.019004 | -0.025735 | -0.034174 | -0.009515 | 0.090161 | -0.039826 | 60.2689 | 60.2861 | 60.2185 | 60.14 | 61.295 | 61.3235 | 60.9323 | 61.2574 | 61.3432 | 61.2403 | 61.1956 | 61.1871 | 61.2118 | 61.3115 | 61.1815 | 60.3101 | 60.3273 | 60.2597 | 60.1812 | 61.3362 | 61.3647 | 60.9735 | 61.2986 | -1.0262 | -0.66347 | -1.0766 | -0.71384
383.9688 | 121.9025 | -61.2167 | 60.3653 | 0.11727 | 0.019004 | -0.030314 | -0.038752 | -0.014093 | 0.081005 | -0.026092 | 60.2643 | 60.2815 | 60.2139 | 60.1308 | 61.2905 | 61.3327 | 60.9369 | 61.2619 | 61.334 | 61.2357 | 61.1864 | 61.178 | 61.2026 | 61.2977 | 61.1906 | 60.3055 | 60.3227 | 60.2551 | 60.172 | 61.3317 | 61.3739 | 60.9781 | 61.3031 | -1.0262 | -0.67263 | -1.0766 | -0.723
385.6406 | 121.8613 | -61.2488 | 60.347 | 0.12643 | 0.023583 | -0.034893 | -0.025017 | -0.004937 | 0.099318 | -0.035248 | 60.2643 | 60.2907 | 60.2185 | 60.1354 | 61.2905 | 61.3235 | 60.9369 | 61.2528 | 61.3752 | 61.2724 | 61.2139 | 61.2238 | 61.2438 | 61.3481 | 61.2135 | 60.3055 | 60.3319 | 60.2597 | 60.1766 | 61.3317 | 61.3647 | 60.9781 | 61.294 | -1.0262 | -0.67263 | -1.072 | -0.71842
387.375 | 121.8018 | -61.322 | 60.3149 | 0.11727 | 0.023583 | -0.021157 | -0.025017 | -0.004937 | 0.090161 | -0.026092 | 60.2643 | 60.2815 | 60.2139 | 60.1354 | 61.2859 | 61.3235 | 60.9415 | 61.2528 | 61.4393 | 61.3456 | 61.3009 | 61.297 | 61.3171 | 61.4122 | 61.2959 | 60.3055 | 60.3227 | 60.2551 | 60.1766 | 61.3271 | 61.3647 | 60.9827 | 61.294 | -1.0216 | -0.67721 | -1.072 | -0.72758
389.125 | 121.8338 | -61.2396 | 60.3836 | 0.12185 | 0.014425 | -0.030314 | -0.020438 | -0.009515 | 0.09474 | -0.03067 | 60.2689 | 60.2907 | 60.2231 | 60.1445 | 61.2859 | 61.3281 | 60.9415 | 61.2619 | 61.3615 | 61.254 | 61.2093 | 61.2192 | 61.2301 | 61.3344 | 61.209 | 60.3101 | 60.3319 | 60.2643 | 60.1857 | 61.3271 | 61.3693 | 60.9827 | 61.3031 | -1.017 | -0.67263 | -1.0628 | -0.71842
390.8594 | 121.8201 | -61.2946 | 60.3058 | 0.12185 | 0.023583 | -0.030314 | -0.029595 | -0.000359 | 0.090161 | -0.035248 | 60.2689 | 60.2815 | 60.2185 | 60.14 | 61.2859 | 61.3281 | 60.9369 | 61.2574 | 61.4164 | 61.3181 | 61.2642 | 61.265 | 61.2942 | 61.3847 | 61.2593 | 60.3101 | 60.3227 | 60.2597 | 60.1812 | 61.3271 | 61.3693 | 60.9781 | 61.2986 | -1.017 | -0.66805 | -1.0674 | -0.71842
392.6094 | 121.9391 | -61.1893 | 60.347 | 0.12185 | 0.023583 | -0.025735 | -0.029595 | -0.009515 | 0.081005 | -0.03067 | 60.2643 | 60.2815 | 60.2139 | 60.1354 | 61.2905 | 61.3281 | 60.9461 | 61.2574 | 61.3111 | 61.2129 | 61.1635 | 61.1597 | 61.1798 | 61.2703 | 61.1586 | 60.3055 | 60.3227 | 60.2551 | 60.1766 | 61.3317 | 61.3693 | 60.9873 | 61.2986 | -1.0262 | -0.68179 | -1.0766 | -0.73216
394.2969 | 121.9025 | -61.235 | 60.347 | 0.10812 | 0.023583 | -0.034893 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2734 | 60.2815 | 60.2185 | 60.14 | 61.2859 | 61.3327 | 60.9461 | 61.2574 | 61.3432 | 61.2586 | 61.2002 | 61.21 | 61.2301 | 61.3206 | 61.1998 | 60.3146 | 60.3227 | 60.2597 | 60.1812 | 61.3271 | 61.3739 | 60.9873 | 61.2986 | -1.0124 | -0.67263 | -1.0674 | -0.72758
395.9844 | 121.8109 | -61.3129 | 60.3333 | 0.11727 | 0.023583 | -0.025735 | -0.025017 | -0.004937 | 0.09474 | -0.03067 | 60.2689 | 60.2815 | 60.2276 | 60.1445 | 61.2905 | 61.3235 | 60.9415 | 61.2528 | 61.4301 | 61.3364 | 61.2871 | 61.2878 | 61.3079 | 61.4076 | 61.2822 | 60.3101 | 60.3227 | 60.2688 | 60.1857 | 61.3317 | 61.3647 | 60.9827 | 61.294 | -1.0216 | -0.67263 | -1.0628 | -0.71385
397.7344 | 121.788 | -61.3129 | 60.3241 | 0.11727 | 0.019004 | -0.025735 | -0.025017 | -0.004937 | 0.09474 | -0.03067 | 60.2689 | 60.2861 | 60.2231 | 60.14 | 61.2905 | 61.3189 | 60.9415 | 61.2619 | 61.4301 | 61.3319 | 61.2871 | 61.2878 | 61.3079 | 61.4076 | 61.2822 | 60.3101 | 60.3273 | 60.2643 | 60.1812 | 61.3317 | 61.3601 | 60.9827 | 61.3031 | -1.0216 | -0.67263 | -1.0674 | -0.71842
399.5 | 121.8475 | -61.2854 | 60.3516 | 0.12643 | 0.019004 | -0.030314 | -0.034174 | -0.009515 | 0.090161 | -0.03067 | 60.2643 | 60.2861 | 60.2185 | 60.1354 | 61.295 | 61.3327 | 60.9506 | 61.2574 | 61.4118 | 61.3044 | 61.2551 | 61.2512 | 61.2759 | 61.3756 | 61.2547 | 60.3055 | 60.3273 | 60.2597 | 60.1766 | 61.3362 | 61.3739 | 60.9918 | 61.2986 | -1.0308 | -0.68636 | -1.0766 | -0.73216
401.1875 | 121.8338 | -61.3037 | 60.3195 | 0.11727 | 0.014425 | -0.025735 | -0.029595 | -0.004937 | 0.090161 | -0.03067 | 60.2689 | 60.2952 | 60.2185 | 60.14 | 61.2859 | 61.3281 | 60.9415 | 61.2528 | 61.421 | 61.3181 | 61.278 | 61.2741 | 61.2988 | 61.3939 | 61.273 | 60.3101 | 60.3364 | 60.2597 | 60.1812 | 61.3271 | 61.3693 | 60.9827 | 61.294 | -1.017 | -0.67263 | -1.0674 | -0.723
402.9531 | 121.8704 | -61.2808 | 60.3104 | 0.13101 | 0.028162 | -0.016578 | -0.025017 | -0.009515 | 0.090161 | -0.026092 | 60.2597 | 60.2861 | 60.2231 | 60.14 | 61.2813 | 61.3235 | 60.9461 | 61.2574 | 61.4118 | 61.309 | 61.2642 | 61.2558 | 61.2713 | 61.371 | 61.2547 | 60.3009 | 60.3273 | 60.2643 | 60.1812 | 61.3225 | 61.3647 | 60.9873 | 61.2986 | -1.0216 | -0.68636 | -1.0582 | -0.723
404.7031 | 121.8613 | -61.2762 | 60.3653 | 0.12185 | 0.019004 | -0.025735 | -0.025017 | -0.000359 | 0.090161 | -0.03067 | 60.2689 | 60.2907 | 60.2231 | 60.1491 | 61.2859 | 61.3235 | 60.9415 | 61.2619 | 61.3981 | 61.2952 | 61.2505 | 61.2512 | 61.2759 | 61.3664 | 61.2456 | 60.3101 | 60.3319 | 60.2643 | 60.1903 | 61.3271 | 61.3647 | 60.9827 | 61.3031 | -1.017 | -0.67263 | -1.0628 | -0.71842
406.3906 | 121.7972 | -61.3129 | 60.3516 | 0.13101 | 0.019004 | -0.025735 | -0.025017 | -0.009515 | 0.099318 | -0.026092 | 60.2689 | 60.2861 | 60.2231 | 60.14 | 61.2813 | 61.3235 | 60.9369 | 61.2528 | 61.4439 | 61.3319 | 61.2871 | 61.2878 | 61.3034 | 61.4122 | 61.2868 | 60.3101 | 60.3273 | 60.2643 | 60.1812 | 61.3225 | 61.3647 | 60.9781 | 61.294 | -1.0124 | -0.66805 | -1.0582 | -0.71385
408.1562 | 121.8475 | -61.2808 | 60.3561 | 0.12185 | 0.023583 | -0.025735 | -0.020438 | -0.004937 | 0.090161 | -0.03067 | 60.2643 | 60.2861 | 60.2185 | 60.14 | 61.2905 | 61.3281 | 60.9415 | 61.2574 | 61.4027 | 61.3044 | 61.2551 | 61.2604 | 61.2759 | 61.371 | 61.2502 | 60.3055 | 60.3273 | 60.2597 | 60.1812 | 61.3317 | 61.3693 | 60.9827 | 61.2986 | -1.0262 | -0.67721 | -1.072 | -0.723
410.125 | 121.8979 | -61.235 | 60.3607 | 0.11727 | 0.019004 | -0.021157 | -0.029595 | -0.004937 | 0.081005 | -0.039826 | 60.2597 | 60.2815 | 60.2185 | 60.1445 | 61.2859 | 61.3327 | 60.9415 | 61.2619 | 61.3523 | 61.254 | 61.2139 | 61.2055 | 61.2301 | 61.3161 | 61.1952 | 60.3009 | 60.3227 | 60.2597 | 60.1857 | 61.3271 | 61.3739 | 60.9827 | 61.3031 | -1.0262 | -0.68178 | -1.0674 | -0.723
413.9219 | 121.8567 | -61.1938 | 60.3928 | 0.12643 | 0.014425 | -0.025735 | -0.029595 | -0.009515 | 0.085583 | -0.026092 | 60.2597 | 60.2907 | 60.2276 | 60.14 | 61.2905 | 61.3327 | 60.9506 | 61.2574 | 61.3203 | 61.2083 | 61.1681 | 61.1643 | 61.1843 | 61.2794 | 61.1678 | 60.3009 | 60.3319 | 60.2688 | 60.1812 | 61.3317 | 61.3739 | 60.9918 | 61.2986 | -1.0308 | -0.69094 | -1.0628 | -0.723
417.2656 | 121.8979 | -61.2305 | 60.3516 | 0.11727 | 0.019004 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.039826 | 60.2643 | 60.2907 | 60.2185 | 60.1491 | 61.2905 | 61.3327 | 60.9369 | 61.2574 | 61.3477 | 61.2495 | 61.2002 | 61.2055 | 61.221 | 61.3206 | 61.1906 | 60.3055 | 60.3319 | 60.2597 | 60.1903 | 61.3317 | 61.3739 | 60.9781 | 61.2986 | -1.0262 | -0.67263 | -1.072 | -0.71842
422.9375 | 121.9299 | -61.1755 | 60.3973 | 0.11727 | 0.019004 | -0.021157 | -0.029595 | -0.009515 | 0.09474 | -0.03067 | 60.2643 | 60.2861 | 60.2231 | 60.14 | 61.295 | 61.3281 | 60.9415 | 61.2574 | 61.2928 | 61.1945 | 61.1544 | 61.1459 | 61.166 | 61.2703 | 61.1449 | 60.3055 | 60.3273 | 60.2643 | 60.1812 | 61.3362 | 61.3693 | 60.9827 | 61.2986 | -1.0308 | -0.67721 | -1.072 | -0.71842
424.7031 | 121.8063 | -61.235 | 60.434 | 0.12643 | 0.023583 | -0.034893 | -0.029595 | -0.000359 | 0.085583 | -0.026092 | 60.2734 | 60.2907 | 60.2185 | 60.1491 | 61.2905 | 61.3327 | 60.9415 | 61.2619 | 61.3615 | 61.2586 | 61.2002 | 61.2055 | 61.2347 | 61.3206 | 61.209 | 60.3146 | 60.3319 | 60.2597 | 60.1903 | 61.3317 | 61.3739 | 60.9827 | 61.3031 | -1.017 | -0.66805 | -1.072 | -0.723
426.4531 | 121.907 | -61.235 | 60.347 | 0.12185 | 0.014425 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.035248 | 60.2689 | 60.2861 | 60.2276 | 60.1445 | 61.2905 | 61.3281 | 60.9369 | 61.2574 | 61.3569 | 61.2495 | 61.2047 | 61.2055 | 61.2255 | 61.3206 | 61.1998 | 60.3101 | 60.3273 | 60.2688 | 60.1857 | 61.3317 | 61.3693 | 60.9781 | 61.2986 | -1.0216 | -0.66805 | -1.0628 | -0.70927
428.2031 | 121.843 | -61.3129 | 60.347 | 0.11727 | 0.019004 | -0.030314 | -0.025017 | -0.000359 | 0.09474 | -0.03067 | 60.2643 | 60.2907 | 60.2231 | 60.1445 | 61.2859 | 61.3281 | 60.9415 | 61.2574 | 61.4301 | 61.3319 | 61.2826 | 61.2878 | 61.3125 | 61.4076 | 61.2822 | 60.3055 | 60.3319 | 60.2643 | 60.1857 | 61.3271 | 61.3693 | 60.9827 | 61.2986 | -1.0216 | -0.67721 | -1.0628 | -0.71842
429.9375 | 121.9482 | -61.1984 | 60.3516 | 0.12185 | 0.019004 | -0.025735 | -0.034174 | -0.004937 | 0.081005 | -0.03067 | 60.2734 | 60.2861 | 60.2231 | 60.1445 | 61.295 | 61.3235 | 60.9461 | 61.2574 | 61.3203 | 61.2174 | 61.1727 | 61.1643 | 61.1935 | 61.2794 | 61.1678 | 60.3146 | 60.3273 | 60.2643 | 60.1857 | 61.3362 | 61.3647 | 60.9873 | 61.2986 | -1.0216 | -0.67263 | -1.072 | -0.723
431.6094 | 121.8338 | -61.2259 | 60.3973 | 0.12185 | 0.023583 | -0.025735 | -0.025017 | -0.009515 | 0.090161 | -0.039826 | 60.2643 | 60.2815 | 60.2185 | 60.1491 | 61.2905 | 61.3327 | 60.9461 | 61.2436 | 61.3477 | 61.2495 | 61.2002 | 61.2009 | 61.2164 | 61.3161 | 61.1861 | 60.3055 | 60.3227 | 60.2597 | 60.1903 | 61.3317 | 61.3739 | 60.9873 | 61.2848 | -1.0262 | -0.68179 | -1.072 | -0.72758
433.3594 | 121.9254 | -61.2762 | 60.2783 | 0.11727 | 0.019004 | -0.025735 | -0.029595 | -0.004937 | 0.099318 | -0.039826 | 60.2597 | 60.2769 | 60.2276 | 60.14 | 61.2859 | 61.3235 | 60.9369 | 61.2574 | 61.3935 | 61.2952 | 61.2505 | 61.2467 | 61.2713 | 61.3756 | 61.2364 | 60.3009 | 60.3181 | 60.2688 | 60.1812 | 61.3271 | 61.3647 | 60.9781 | 61.2986 | -1.0262 | -0.67721 | -1.0582 | -0.70927
435.0312 | 121.8521 | -61.2671 | 60.347 | 0.12185 | 0.014425 | -0.025735 | -0.029595 | -0.009515 | 0.090161 | -0.035248 | 60.2734 | 60.2907 | 60.2231 | 60.14 | 61.2905 | 61.3281 | 60.9369 | 61.2574 | 61.3889 | 61.2815 | 61.2414 | 61.2375 | 61.2576 | 61.3573 | 61.2318 | 60.3146 | 60.3319 | 60.2643 | 60.1812 | 61.3317 | 61.3693 | 60.9781 | 61.2986 | -1.017 | -0.66347 | -1.0674 | -0.71385
436.7188 | 121.9528 | -61.2625 | 60.2692 | 0.12643 | 0.014425 | -0.034893 | -0.034174 | -0.004937 | 0.090161 | -0.035248 | 60.2643 | 60.2907 | 60.2276 | 60.1445 | 61.2905 | 61.3281 | 60.9369 | 61.2574 | 61.3889 | 61.2769 | 61.2276 | 61.2283 | 61.2576 | 61.3527 | 61.2273 | 60.3055 | 60.3319 | 60.2688 | 60.1857 | 61.3317 | 61.3693 | 60.9781 | 61.2986 | -1.0262 | -0.67263 | -1.0628 | -0.70927
438.4688 | 121.9025 | -61.2213 | 60.3516 | 0.12643 | 0.014425 | -0.025735 | -0.038752 | -0.009515 | 0.09474 | -0.03067 | 60.2689 | 60.2815 | 60.2231 | 60.1445 | 61.2905 | 61.3235 | 60.9369 | 61.2574 | 61.3477 | 61.2357 | 61.1956 | 61.1826 | 61.2118 | 61.3161 | 61.1906 | 60.3101 | 60.3227 | 60.2643 | 60.1857 | 61.3317 | 61.3647 | 60.9781 | 61.2986 | -1.0216 | -0.66805 | -1.0674 | -0.71385
440.1719 | 121.9254 | -61.2534 | 60.3058 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.2689 | 60.2952 | 60.2231 | 60.14 | 61.295 | 61.3281 | 60.9415 | 61.2528 | 61.3752 | 61.2724 | 61.223 | 61.2238 | 61.2484 | 61.3435 | 61.2181 | 60.3101 | 60.3364 | 60.2643 | 60.1812 | 61.3362 | 61.3693 | 60.9827 | 61.294 | -1.0262 | -0.67263 | -1.072 | -0.71842
441.9062 | 121.9482 | -61.2671 | 60.2829 | 0.12185 | 0.014425 | -0.030314 | -0.029595 | -0.009515 | 0.09474 | -0.039826 | 60.2689 | 60.2907 | 60.2185 | 60.14 | 61.2905 | 61.3281 | 60.9278 | 61.2619 | 61.3889 | 61.2815 | 61.2368 | 61.2375 | 61.2576 | 61.3618 | 61.2273 | 60.3101 | 60.3319 | 60.2597 | 60.1812 | 61.3317 | 61.3693 | 60.9689 | 61.3031 | -1.0216 | -0.65889 | -1.072 | -0.70927
443.5781 | 121.8796 | -61.2167 | 60.3973 | 0.12185 | 0.014425 | -0.021157 | -0.034174 | -0.004937 | 0.090161 | -0.035248 | 60.2734 | 60.2907 | 60.2231 | 60.1354 | 61.295 | 61.3281 | 60.9415 | 61.2482 | 61.3386 | 61.2312 | 61.1956 | 61.1826 | 61.2118 | 61.3069 | 61.1815 | 60.3146 | 60.3319 | 60.2643 | 60.1766 | 61.3362 | 61.3693 | 60.9827 | 61.2894 | -1.0216 | -0.66805 | -1.072 | -0.71842
445.3125 | 121.9116 | -61.1938 | 60.4019 | 0.11727 | 0.014425 | -0.025735 | -0.034174 | -0.009515 | 0.085583 | -0.035248 | 60.2643 | 60.2815 | 60.2276 | 60.14 | 61.2905 | 61.3235 | 60.9461 | 61.2665 | 61.3111 | 61.2083 | 61.1681 | 61.1597 | 61.1843 | 61.2794 | 61.1586 | 60.3055 | 60.3227 | 60.2688 | 60.1812 | 61.3317 | 61.3647 | 60.9873 | 61.3077 | -1.0262 | -0.68179 | -1.0628 | -0.71842
446.9844 | 121.8292 | -61.2854 | 60.3104 | 0.12185 | 0.019004 | -0.025735 | -0.020438 | -0.000359 | 0.081005 | -0.035248 | 60.2689 | 60.2861 | 60.2231 | 60.1445 | 61.2813 | 61.3235 | 60.9415 | 61.2482 | 61.4073 | 61.3044 | 61.2597 | 61.265 | 61.285 | 61.3664 | 61.2502 | 60.3101 | 60.3273 | 60.2643 | 60.1857 | 61.3225 | 61.3647 | 60.9827 | 61.2894 | -1.0124 | -0.67263 | -1.0582 | -0.71842
448.7344 | 121.7972 | -61.3449 | 60.3012 | 0.11727 | 0.009846 | -0.030314 | -0.034174 | -0.004937 | 0.099318 | -0.035248 | 60.2689 | 60.2861 | 60.2322 | 60.1445 | 61.2905 | 61.3235 | 60.9415 | 61.2528 | 61.4622 | 61.3548 | 61.3146 | 61.3107 | 61.34 | 61.4442 | 61.3097 | 60.3101 | 60.3273 | 60.2734 | 60.1857 | 61.3317 | 61.3647 | 60.9827 | 61.294 | -1.0216 | -0.67263 | -1.0582 | -0.70927
450.5 | 121.8567 | -61.2534 | 60.347 | 0.12643 | 0.014425 | -0.021157 | -0.034174 | -0.009515 | 0.09474 | -0.026092 | 60.2734 | 60.2861 | 60.2276 | 60.1354 | 61.2905 | 61.3281 | 60.9369 | 61.2528 | 61.3798 | 61.2678 | 61.2322 | 61.2192 | 61.2438 | 61.3481 | 61.2273 | 60.3146 | 60.3273 | 60.2688 | 60.1766 | 61.3317 | 61.3693 | 60.9781 | 61.294 | -1.017 | -0.66347 | -1.0628 | -0.70927
452.1719 | 121.9345 | -61.2946 | 60.26 | 0.11727 | 0.019004 | -0.025735 | -0.020438 | 0.004219 | 0.099318 | -0.03067 | 60.2643 | 60.2861 | 60.2276 | 60.1445 | 61.2905 | 61.3373 | 60.9415 | 61.2574 | 61.4118 | 61.3136 | 61.2688 | 61.2741 | 61.2988 | 61.3939 | 61.2639 | 60.3055 | 60.3273 | 60.2688 | 60.1857 | 61.3317 | 61.3785 | 60.9827 | 61.2986 | -1.0262 | -0.67721 | -1.0628 | -0.71385
453.9062 | 121.8018 | -61.3266 | 60.3058 | 0.12643 | 0.023583 | -0.025735 | -0.029595 | -0.000359 | 0.09474 | -0.03067 | 60.2689 | 60.2907 | 60.2231 | 60.1445 | 61.2905 | 61.3327 | 60.9369 | 61.2619 | 61.453 | 61.3502 | 61.3009 | 61.297 | 61.3262 | 61.4213 | 61.2959 | 60.3101 | 60.3319 | 60.2643 | 60.1857 | 61.3317 | 61.3739 | 60.9781 | 61.3031 | -1.0216 | -0.66805 | -1.0674 | -0.71385
455.6562 | 121.9116 | -61.2213 | 60.3653 | 0.12185 | 0.028162 | -0.030314 | -0.029595 | -0.009515 | 0.090161 | -0.03067 | 60.2689 | 60.2815 | 60.2231 | 60.1491 | 61.295 | 61.3235 | 60.9415 | 61.2619 | 61.3432 | 61.2495 | 61.191 | 61.1917 | 61.2118 | 61.3115 | 61.1906 | 60.3101 | 60.3227 | 60.2643 | 60.1903 | 61.3362 | 61.3647 | 60.9827 | 61.3031 | -1.0262 | -0.67263 | -1.072 | -0.71842
457.4062 | 121.8613 | -61.2808 | 60.3516 | 0.12185 | 0.019004 | -0.034893 | -0.025017 | -0.000359 | 0.09474 | -0.039826 | 60.2689 | 60.2861 | 60.2276 | 60.1491 | 61.295 | 61.3373 | 60.9369 | 61.2619 | 61.4027 | 61.2998 | 61.2459 | 61.2558 | 61.2805 | 61.3756 | 61.241 | 60.3101 | 60.3273 | 60.2688 | 60.1903 | 61.3362 | 61.3785 | 60.9781 | 61.3031 | -1.0262 | -0.66805 | -1.0674 | -0.70927
459.1562 | 121.9666 | -61.1801 | 60.3928 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | -0.004937 | 0.09474 | -0.039826 | 60.2643 | 60.2861 | 60.2231 | 60.14 | 61.2996 | 61.3327 | 60.9415 | 61.2574 | 61.302 | 61.1991 | 61.1498 | 61.1505 | 61.1752 | 61.2749 | 61.1403 | 60.3055 | 60.3273 | 60.2643 | 60.1812 | 61.3408 | 61.3739 | 60.9827 | 61.2986 | -1.0353 | -0.67721 | -1.0766 | -0.71842
460.8438 | 121.8201 | -61.3037 | 60.3287 | 0.12643 | 0.028162 | -0.030314 | -0.025017 | -0.004937 | 0.090161 | -0.03067 | 60.2689 | 60.2952 | 60.2231 | 60.1491 | 61.2905 | 61.3235 | 60.9278 | 61.2528 | 61.4301 | 61.3319 | 61.2734 | 61.2787 | 61.2988 | 61.3939 | 61.273 | 60.3101 | 60.3364 | 60.2643 | 60.1903 | 61.3317 | 61.3647 | 60.9689 | 61.294 | -1.0216 | -0.65889 | -1.0674 | -0.70469
462.5938 | 121.9391 | -61.2671 | 60.2875 | 0.11727 | 0.014425 | -0.030314 | -0.034174 | -0.004937 | 0.090161 | -0.03067 | 60.2689 | 60.2861 | 60.2231 | 60.1491 | 61.2905 | 61.3327 | 60.9369 | 61.2528 | 61.3844 | 61.2815 | 61.2368 | 61.2329 | 61.2622 | 61.3573 | 61.2364 | 60.3101 | 60.3273 | 60.2643 | 60.1903 | 61.3317 | 61.3739 | 60.9781 | 61.294 | -1.0216 | -0.66805 | -1.0674 | -0.71385
464.2656 | 121.8567 | -61.203 | 60.4294 | 0.13101 | 0.019004 | -0.016578 | -0.034174 | -0.009515 | 0.085583 | -0.026092 | 60.2689 | 60.2907 | 60.2231 | 60.1491 | 61.295 | 61.3281 | 60.9552 | 61.2619 | 61.334 | 61.222 | 61.1864 | 61.1688 | 61.1935 | 61.2886 | 61.1769 | 60.3101 | 60.3319 | 60.2643 | 60.1903 | 61.3362 | 61.3693 | 60.9964 | 61.3031 | -1.0262 | -0.68636 | -1.072 | -0.73216
466.0156 | 121.8658 | -61.3083 | 60.2966 | 0.12185 | 0.023583 | -0.039471 | -0.025017 | -0.009515 | 0.090161 | -0.03067 | 60.278 | 60.2952 | 60.2276 | 60.1491 | 61.2859 | 61.3281 | 60.9369 | 61.2528 | 61.4301 | 61.3319 | 61.2688 | 61.2833 | 61.2988 | 61.3985 | 61.2776 | 60.3192 | 60.3364 | 60.2688 | 60.1903 | 61.3271 | 61.3693 | 60.9781 | 61.294 | -1.0079 | -0.65889 | -1.0582 | -0.70927
467.7031 | 121.9437 | -61.1618 | 60.379 | 0.11727 | 0.019004 | -0.034893 | -0.038752 | -0.004937 | 0.09474 | -0.039826 | 60.2689 | 60.2907 | 60.2276 | 60.14 | 61.295 | 61.3327 | 60.9415 | 61.2574 | 61.2791 | 61.1808 | 61.1269 | 61.1231 | 61.1569 | 61.2565 | 61.122 | 60.3101 | 60.3319 | 60.2688 | 60.1812 | 61.3362 | 61.3739 | 60.9827 | 61.2986 | -1.0262 | -0.67263 | -1.0674 | -0.71385
469.4531 | 121.9574 | -61.2762 | 60.2875 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.2734 | 60.2952 | 60.2276 | 60.1354 | 61.2859 | 61.3189 | 60.9323 | 61.2665 | 61.3981 | 61.2952 | 61.2459 | 61.2467 | 61.2713 | 61.3664 | 61.241 | 60.3146 | 60.3364 | 60.2688 | 60.1766 | 61.3271 | 61.3601 | 60.9735 | 61.3077 | -1.0124 | -0.65889 | -1.0582 | -0.70469
471.2031 | 121.907 | -61.2259 | 60.3561 | 0.12185 | 0.014425 | -0.034893 | -0.025017 | -0.014093 | 0.085583 | -0.035248 | 60.2734 | 60.2907 | 60.2276 | 60.14 | 61.2905 | 61.3235 | 60.9323 | 61.2574 | 61.3477 | 61.2403 | 61.191 | 61.2009 | 61.2118 | 61.3115 | 61.1906 | 60.3146 | 60.3319 | 60.2688 | 60.1812 | 61.3317 | 61.3647 | 60.9735 | 61.2986 | -1.017 | -0.65889 | -1.0628 | -0.70469
472.9375 | 121.9345 | -61.2625 | 60.2966 | 0.13101 | 0.019004 | -0.025735 | -0.025017 | -0.009515 | 0.090161 | -0.035248 | 60.2643 | 60.2907 | 60.2231 | 60.14 | 61.295 | 61.3327 | 60.9369 | 61.2528 | 61.3935 | 61.2815 | 61.2368 | 61.2375 | 61.253 | 61.3527 | 61.2273 | 60.3055 | 60.3319 | 60.2643 | 60.1812 | 61.3362 | 61.3739 | 60.9781 | 61.294 | -1.0308 | -0.67263 | -1.072 | -0.71385
474.6719 | 121.9208 | -61.29 | 60.3104 | 0.12643 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.09474 | -0.035248 | 60.2734 | 60.2861 | 60.2368 | 60.1445 | 61.2859 | 61.3281 | 60.9278 | 61.2619 | 61.4164 | 61.3136 | 61.2642 | 61.2695 | 61.2988 | 61.3847 | 61.2547 | 60.3146 | 60.3273 | 60.278 | 60.1857 | 61.3271 | 61.3693 | 60.9689 | 61.3031 | -1.0124 | -0.65432 | -1.0491 | -0.69095
476.3594 | 121.8567 | -61.2579 | 60.347 | 0.12643 | 0.03274 | -0.021157 | -0.025017 | -0.014093 | 0.09474 | -0.03067 | 60.2689 | 60.2907 | 60.2322 | 60.1491 | 61.2905 | 61.3327 | 60.9369 | 61.2619 | 61.3844 | 61.2907 | 61.2368 | 61.2329 | 61.2438 | 61.3527 | 61.2273 | 60.3101 | 60.3319 | 60.2734 | 60.1903 | 61.3317 | 61.3739 | 60.9781 | 61.3031 | -1.0216 | -0.66805 | -1.0582 | -0.70469
478.1094 | 121.8109 | -61.322 | 60.3287 | 0.12185 | 0.028162 | -0.030314 | -0.01586 | -0.004937 | 0.09474 | -0.026092 | 60.2689 | 60.2907 | 60.2322 | 60.1491 | 61.295 | 61.3281 | 60.9323 | 61.2574 | 61.4439 | 61.3502 | 61.2917 | 61.3062 | 61.3171 | 61.4168 | 61.2959 | 60.3101 | 60.3319 | 60.2734 | 60.1903 | 61.3362 | 61.3693 | 60.9735 | 61.2986 | -1.0262 | -0.66347 | -1.0628 | -0.70011
479.8594 | 121.9528 | -61.1755 | 60.3928 | 0.12185 | 0.023583 | -0.030314 | -0.025017 | -0.009515 | 0.09474 | -0.03067 | 60.2689 | 60.2907 | 60.2139 | 60.1445 | 61.2905 | 61.3235 | 60.9415 | 61.2574 | 61.2974 | 61.1991 | 61.1452 | 61.1505 | 61.166 | 61.2703 | 61.1449 | 60.3101 | 60.3319 | 60.2551 | 60.1857 | 61.3317 | 61.3647 | 60.9827 | 61.2986 | -1.0216 | -0.67263 | -1.0766 | -0.72758
481.5469 | 121.9254 | -61.2579 | 60.2875 | 0.11727 | 0.023583 | -0.025735 | -0.029595 | -0.014093 | 0.09474 | -0.026092 | 60.2734 | 60.2907 | 60.2276 | 60.1445 | 61.2905 | 61.3281 | 60.9369 | 61.2574 | 61.3752 | 61.2815 | 61.2322 | 61.2283 | 61.2438 | 61.3527 | 61.2318 | 60.3146 | 60.3319 | 60.2688 | 60.1857 | 61.3317 | 61.3693 | 60.9781 | 61.2986 | -1.017 | -0.66347 | -1.0628 | -0.70927
483.2969 | 121.8338 | -61.3083 | 60.3104 | 0.11727 | 0.023583 | -0.030314 | -0.029595 | -0.000359 | 0.09474 | -0.03067 | 60.2689 | 60.2952 | 60.2276 | 60.1491 | 61.2905 | 61.3235 | 60.9323 | 61.2574 | 61.4256 | 61.3319 | 61.278 | 61.2787 | 61.3079 | 61.403 | 61.2776 | 60.3101 | 60.3364 | 60.2688 | 60.1903 | 61.3317 | 61.3647 | 60.9735 | 61.2986 | -1.0216 | -0.66347 | -1.0628 | -0.70469
485.0469 | 121.8613 | -61.2488 | 60.3836 | 0.12185 | 0.028162 | -0.030314 | -0.025017 | -0.004937 | 0.09474 | -0.035248 | 60.2643 | 60.2998 | 60.2276 | 60.1491 | 61.2905 | 61.3235 | 60.9323 | 61.2574 | 61.3706 | 61.2769 | 61.2185 | 61.2238 | 61.2438 | 61.3435 | 61.2135 | 60.3055 | 60.341 | 60.2688 | 60.1903 | 61.3317 | 61.3647 | 60.9735 | 61.2986 | -1.0262 | -0.66805 | -1.0628 | -0.70469
486.7344 | 121.9437 | -61.1618 | 60.4019 | 0.11727 | 0.023583 | -0.021157 | -0.029595 | -0.009515 | 0.085583 | -0.03067 | 60.2643 | 60.2861 | 60.2276 | 60.14 | 61.2859 | 61.3235 | 60.9461 | 61.2574 | 61.2791 | 61.1854 | 61.1406 | 61.1322 | 61.1523 | 61.2474 | 61.1311 | 60.3055 | 60.3273 | 60.2688 | 60.1812 | 61.3271 | 61.3647 | 60.9873 | 61.2986 | -1.0216 | -0.68179 | -1.0582 | -0.71842
488.4844 | 121.8109 | -61.2396 | 60.434 | 0.12643 | 0.03274 | -0.025735 | -0.034174 | -0.000359 | 0.090161 | -0.03067 | 60.2734 | 60.2861 | 60.2322 | 60.14 | 61.2996 | 61.3281 | 60.9415 | 61.2619 | 61.3661 | 61.2724 | 61.2139 | 61.2054 | 61.2393 | 61.3298 | 61.209 | 60.3146 | 60.3273 | 60.2734 | 60.1812 | 61.3408 | 61.3693 | 60.9827 | 61.3031 | -1.0262 | -0.66805 | -1.0674 | -0.70927
490.25 | 121.9345 | -61.1938 | 60.4202 | 0.12185 | 0.023583 | -0.030314 | -0.034174 | -0.009515 | 0.090161 | -0.039826 | 60.2597 | 60.2861 | 60.2276 | 60.1491 | 61.295 | 61.3281 | 60.9415 | 61.2665 | 61.3157 | 61.2174 | 61.1635 | 61.1597 | 61.1843 | 61.284 | 61.154 | 60.3009 | 60.3273 | 60.2688 | 60.1903 | 61.3362 | 61.3693 | 60.9827 | 61.3077 | -1.0353 | -0.68178 | -1.0674 | -0.71385
492 | 121.8613 | -61.2076 | 60.4248 | 0.12185 | 0.028162 | -0.025735 | -0.029595 | -0.009515 | 0.09474 | -0.035248 | 60.2689 | 60.2952 | 60.2231 | 60.14 | 61.2905 | 61.3327 | 60.9369 | 61.2528 | 61.3294 | 61.2357 | 61.1818 | 61.178 | 61.1981 | 61.3023 | 61.1723 | 60.3101 | 60.3364 | 60.2643 | 60.1812 | 61.3317 | 61.3739 | 60.9781 | 61.294 | -1.0216 | -0.66805 | -1.0674 | -0.71385
493.75 | 121.8384 | -61.2122 | 60.3973 | 0.12185 | 0.023583 | -0.021157 | -0.029595 | -0.000359 | 0.090161 | -0.03067 | 60.2643 | 60.2907 | 60.2276 | 60.14 | 61.295 | 61.3327 | 60.9369 | 61.2574 | 61.334 | 61.2357 | 61.191 | 61.1826 | 61.2118 | 61.3023 | 61.1815 | 60.3055 | 60.3319 | 60.2688 | 60.1812 | 61.3362 | 61.3739 | 60.9781 | 61.2986 | -1.0308 | -0.67263 | -1.0674 | -0.70927
495.5 | 121.8109 | -61.3449 | 60.3058 | 0.11727 | 0.023583 | -0.021157 | -0.034174 | -0.004937 | 0.09474 | -0.03067 | 60.2689 | 60.2952 | 60.2231 | 60.1491 | 61.2905 | 61.3281 | 60.9323 | 61.2574 | 61.4622 | 61.3685 | 61.3238 | 61.3107 | 61.34 | 61.4397 | 61.3142 | 60.3101 | 60.3364 | 60.2643 | 60.1903 | 61.3317 | 61.3693 | 60.9735 | 61.2986 | -1.0216 | -0.66347 | -1.0674 | -0.70927
497.1875 | 121.8658 | -61.2671 | 60.347 | 0.12643 | 0.023583 | -0.025735 | -0.01586 | -0.004937 | 0.09474 | -0.026092 | 60.2734 | 60.2952 | 60.2322 | 60.1537 | 61.2905 | 61.3281 | 60.9369 | 61.2574 | 61.3935 | 61.2907 | 61.2414 | 61.2512 | 61.2622 | 61.3618 | 61.241 | 60.3146 | 60.3364 | 60.2734 | 60.1949 | 61.3317 | 61.3693 | 60.9781 | 61.2986 | -1.017 | -0.66347 | -1.0582 | -0.70469
498.9219 | 121.8109 | -61.2213 | 60.3973 | 0.12185 | 0.023583 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.03067 | 60.2734 | 60.2907 | 60.2322 | 60.1491 | 61.295 | 61.3281 | 60.9369 | 61.2619 | 61.3432 | 61.2449 | 61.1956 | 61.2009 | 61.221 | 61.3069 | 61.1906 | 60.3146 | 60.3319 | 60.2734 | 60.1903 | 61.3362 | 61.3693 | 60.9781 | 61.3031 | -1.0216 | -0.66347 | -1.0628 | -0.70469
500.6719 | 121.9528 | -61.1847 | 60.3699 | 0.12185 | 0.028162 | -0.034893 | -0.034174 | -0.004937 | 0.090161 | -0.039826 | 60.278 | 60.2815 | 60.2322 | 60.14 | 61.2905 | 61.3281 | 60.9369 | 61.2574 | 61.3065 | 61.2129 | 61.1498 | 61.1505 | 61.1798 | 61.2749 | 61.1449 | 60.3192 | 60.3227 | 60.2734 | 60.1812 | 61.3317 | 61.3693 | 60.9781 | 61.2986 | -1.0124 | -0.65889 | -1.0582 | -0.70469
502.3594 | 121.8887 | -61.2396 | 60.3561 | 0.12643 | 0.019004 | -0.030314 | -0.034174 | -0.009515 | 0.090161 | -0.035248 | 60.2734 | 60.2907 | 60.2231 | 60.1445 | 61.2996 | 61.3281 | 60.9415 | 61.2574 | 61.3661 | 61.2586 | 61.2093 | 61.2054 | 61.2301 | 61.3298 | 61.2044 | 60.3146 | 60.3319 | 60.2643 | 60.1857 | 61.3408 | 61.3693 | 60.9827 | 61.2986 | -1.0262 | -0.66805 | -1.0766 | -0.71842
504.125 | 121.7926 | -61.3037 | 60.3333 | 0.12643 | 0.03274 | -0.030314 | -0.025017 | -0.000359 | 0.090161 | -0.03067 | 60.278 | 60.2952 | 60.2276 | 60.1537 | 61.2859 | 61.3281 | 60.9415 | 61.2528 | 61.4301 | 61.3365 | 61.2734 | 61.2787 | 61.3034 | 61.3939 | 61.273 | 60.3192 | 60.3364 | 60.2688 | 60.1949 | 61.3271 | 61.3693 | 60.9827 | 61.294 | -1.0079 | -0.66347 | -1.0582 | -0.71385
505.8125 | 121.9025 | -61.2259 | 60.3607 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | -0.014093 | 0.090161 | -0.03067 | 60.2643 | 60.2998 | 60.2231 | 60.1537 | 61.2996 | 61.3281 | 60.9415 | 61.2574 | 61.3477 | 61.2449 | 61.1956 | 61.1963 | 61.2118 | 61.3161 | 61.1952 | 60.3055 | 60.341 | 60.2643 | 60.1949 | 61.3408 | 61.3693 | 60.9827 | 61.2986 | -1.0353 | -0.67721 | -1.0766 | -0.71842
507.5625 | 121.8109 | -61.3403 | 60.3287 | 0.11727 | 0.028162 | -0.025735 | -0.029595 | -0.009515 | 0.09474 | -0.026092 | 60.2689 | 60.2907 | 60.2322 | 60.1445 | 61.295 | 61.3235 | 60.9415 | 61.2619 | 61.4576 | 61.3685 | 61.3146 | 61.3107 | 61.3308 | 61.4351 | 61.3142 | 60.3101 | 60.3319 | 60.2734 | 60.1857 | 61.3362 | 61.3647 | 60.9827 | 61.3031 | -1.0262 | -0.67263 | -1.0628 | -0.70927
509.2344 | 121.962 | -61.1618 | 60.3882 | 0.12185 | 0.023583 | -0.034893 | -0.034174 | -0.014093 | 0.085583 | -0.03067 | 60.2734 | 60.2952 | 60.2276 | 60.1445 | 61.2996 | 61.3373 | 60.9369 | 61.2528 | 61.2837 | 61.1854 | 61.1269 | 61.1276 | 61.1477 | 61.2474 | 61.1311 | 60.3146 | 60.3364 | 60.2688 | 60.1857 | 61.3408 | 61.3785 | 60.9781 | 61.294 | -1.0262 | -0.66347 | -1.072 | -0.70927
510.9844 | 121.8475 | -61.2579 | 60.3699 | 0.12185 | 0.028162 | -0.034893 | -0.029595 | -0.004937 | 0.09474 | -0.03067 | 60.2689 | 60.2952 | 60.2276 | 60.1491 | 61.2859 | 61.3235 | 60.9461 | 61.2528 | 61.3798 | 61.2861 | 61.223 | 61.2283 | 61.253 | 61.3527 | 61.2273 | 60.3101 | 60.3364 | 60.2688 | 60.1903 | 61.3271 | 61.3647 | 60.9873 | 61.294 | -1.017 | -0.67721 | -1.0582 | -0.71842
512.75 | 121.8155 | -61.2305 | 60.4111 | 0.11727 | 0.023583 | -0.025735 | -0.020438 | -0.004937 | 0.081005 | -0.03067 | 60.2689 | 60.2907 | 60.2276 | 60.1491 | 61.2905 | 61.3373 | 60.9461 | 61.2574 | 61.3477 | 61.2541 | 61.2047 | 61.21 | 61.2255 | 61.3115 | 61.1998 | 60.3101 | 60.3319 | 60.2688 | 60.1903 | 61.3317 | 61.3785 | 60.9873 | 61.2986 | -1.0216 | -0.67721 | -1.0628 | -0.71842
514.4375 | 121.8292 | -61.3174 | 60.3104 | 0.12643 | 0.037319 | -0.021157 | -0.029595 | -0.004937 | 0.09474 | -0.026092 | 60.2689 | 60.2861 | 60.2322 | 60.1537 | 61.295 | 61.3327 | 60.9415 | 61.2574 | 61.4439 | 61.3548 | 61.2963 | 61.2878 | 61.3125 | 61.4122 | 61.2914 | 60.3101 | 60.3273 | 60.2734 | 60.1949 | 61.3362 | 61.3739 | 60.9827 | 61.2986 | -1.0262 | -0.67263 | -1.0628 | -0.70927
516.1875 | 121.8658 | -61.3037 | 60.2737 | 0.12185 | 0.023583 | -0.030314 | -0.020438 | -0.004937 | 0.09474 | -0.035248 | 60.2689 | 60.2907 | 60.2322 | 60.1445 | 61.2859 | 61.3281 | 60.9461 | 61.2619 | 61.4256 | 61.3273 | 61.2734 | 61.2833 | 61.2988 | 61.3985 | 61.2685 | 60.3101 | 60.3319 | 60.2734 | 60.1857 | 61.3271 | 61.3693 | 60.9873 | 61.3031 | -1.017 | -0.67721 | -1.0537 | -0.71384
517.9375 | 121.9391 | -61.2579 | 60.2692 | 0.11727 | 0.023583 | -0.025735 | -0.034174 | -0.014093 | 0.090161 | -0.035248 | 60.2734 | 60.2952 | 60.2276 | 60.1445 | 61.2905 | 61.3327 | 60.9323 | 61.2482 | 61.3752 | 61.2815 | 61.2322 | 61.2238 | 61.2438 | 61.3481 | 61.2227 | 60.3146 | 60.3364 | 60.2688 | 60.1857 | 61.3317 | 61.3739 | 60.9735 | 61.2894 | -1.017 | -0.65889 | -1.0628 | -0.70469
519.6875 | 121.8613 | -61.2808 | 60.3607 | 0.11727 | 0.023583 | -0.021157 | -0.025017 | -0.004937 | 0.099318 | -0.035248 | 60.2734 | 60.2907 | 60.2322 | 60.1583 | 61.295 | 61.3281 | 60.9415 | 61.2619 | 61.3981 | 61.3044 | 61.2597 | 61.2558 | 61.2759 | 61.3801 | 61.2456 | 60.3146 | 60.3319 | 60.2734 | 60.1995 | 61.3362 | 61.3693 | 60.9827 | 61.3031 | -1.0216 | -0.66805 | -1.0628 | -0.70927
521.375 | 121.9299 | -61.2213 | 60.379 | 0.12185 | 0.028162 | -0.030314 | -0.025017 | -0.014093 | 0.085583 | -0.039826 | 60.2643 | 60.2952 | 60.2276 | 60.1445 | 61.295 | 61.3281 | 60.9415 | 61.2619 | 61.3432 | 61.2495 | 61.191 | 61.1963 | 61.2072 | 61.3069 | 61.1815 | 60.3055 | 60.3364 | 60.2688 | 60.1857 | 61.3362 | 61.3693 | 60.9827 | 61.3031 | -1.0308 | -0.67721 | -1.0674 | -0.71385
523.125 | 121.8658 | -61.2762 | 60.347 | 0.12643 | 0.028162 | -0.030314 | -0.025017 | -0.004937 | 0.09474 | -0.026092 | 60.2643 | 60.2907 | 60.2322 | 60.1491 | 61.295 | 61.3281 | 60.9415 | 61.2528 | 61.4027 | 61.3044 | 61.2459 | 61.2512 | 61.2713 | 61.371 | 61.2502 | 60.3055 | 60.3319 | 60.2734 | 60.1903 | 61.3362 | 61.3693 | 60.9827 | 61.294 | -1.0308 | -0.67721 | -1.0628 | -0.70927
524.8125 | 121.9528 | -61.171 | 60.4065 | 0.12185 | 0.028162 | -0.034893 | -0.025017 | -0.014093 | 0.085583 | -0.039826 | 60.2734 | 60.2952 | 60.2231 | 60.1445 | 61.2905 | 61.3373 | 60.9369 | 61.2619 | 61.2928 | 61.1991 | 61.1361 | 61.1459 | 61.1569 | 61.2565 | 61.1311 | 60.3146 | 60.3364 | 60.2643 | 60.1857 | 61.3317 | 61.3785 | 60.9781 | 61.3031 | -1.017 | -0.66347 | -1.0674 | -0.71385
526.5625 | 121.8018 | -61.2991 | 60.3195 | 0.12185 | 0.03274 | -0.025735 | -0.025017 | -0.004937 | 0.090161 | -0.03067 | 60.2734 | 60.2907 | 60.2276 | 60.1491 | 61.2905 | 61.3235 | 60.9369 | 61.2574 | 61.421 | 61.3319 | 61.2734 | 61.2741 | 61.2942 | 61.3893 | 61.2685 | 60.3146 | 60.3319 | 60.2688 | 60.1903 | 61.3317 | 61.3647 | 60.9781 | 61.2986 | -1.017 | -0.66347 | -1.0628 | -0.70927
528.2969 | 121.9345 | -61.2717 | 60.26 | 0.12643 | 0.03274 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.03067 | 60.2734 | 60.2861 | 60.2322 | 60.1445 | 61.295 | 61.3235 | 60.9415 | 61.2619 | 61.3981 | 61.3044 | 61.2459 | 61.2467 | 61.2713 | 61.3573 | 61.241 | 60.3146 | 60.3273 | 60.2734 | 60.1857 | 61.3362 | 61.3647 | 60.9827 | 61.3031 | -1.0216 | -0.66805 | -1.0628 | -0.70927
529.9688 | 121.8292 | -61.2305 | 60.4431 | 0.12185 | 0.03274 | -0.030314 | -0.025017 | -0.009515 | 0.09474 | -0.03067 | 60.2643 | 60.2952 | 60.2322 | 60.1537 | 61.295 | 61.3281 | 60.9323 | 61.2619 | 61.3523 | 61.2632 | 61.2002 | 61.2055 | 61.221 | 61.3252 | 61.1998 | 60.3055 | 60.3364 | 60.2734 | 60.1949 | 61.3362 | 61.3693 | 60.9735 | 61.3031 | -1.0308 | -0.66805 | -1.0628 | -0.70011
531.7188 | 121.8979 | -61.2259 | 60.3516 | 0.11727 | 0.023583 | -0.021157 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.2551 | 60.2998 | 60.2231 | 60.14 | 61.295 | 61.3327 | 60.9369 | 61.2619 | 61.3432 | 61.2495 | 61.2047 | 61.1963 | 61.221 | 61.3161 | 61.1906 | 60.2963 | 60.341 | 60.2643 | 60.1812 | 61.3362 | 61.3739 | 60.9781 | 61.3031 | -1.0399 | -0.68179 | -1.072 | -0.71385
533.4531 | 121.9254 | -61.3037 | 60.2829 | 0.11727 | 0.03274 | -0.021157 | -0.020438 | -0.009515 | 0.090161 | -0.035248 | 60.2689 | 60.2952 | 60.2322 | 60.1491 | 61.295 | 61.3281 | 60.9323 | 61.2574 | 61.421 | 61.3365 | 61.2826 | 61.2833 | 61.2942 | 61.3939 | 61.2685 | 60.3101 | 60.3364 | 60.2734 | 60.1903 | 61.3362 | 61.3693 | 60.9735 | 61.2986 | -1.0262 | -0.66347 | -1.0628 | -0.70011
535.2031 | 121.8658 | -61.2671 | 60.347 | 0.12185 | 0.03274 | -0.030314 | -0.01586 | -0.009515 | 0.099318 | -0.026092 | 60.2689 | 60.2998 | 60.2276 | 60.1491 | 61.2996 | 61.3327 | 60.9415 | 61.2574 | 61.3889 | 61.2998 | 61.2368 | 61.2512 | 61.2576 | 61.3664 | 61.241 | 60.3101 | 60.341 | 60.2688 | 60.1903 | 61.3408 | 61.3739 | 60.9827 | 61.2986 | -1.0308 | -0.67263 | -1.072 | -0.71385
536.8906 | 121.9162 | -61.1847 | 60.3973 | 0.12185 | 0.023583 | -0.025735 | -0.025017 | -0.004937 | 0.085583 | -0.03067 | 60.2734 | 60.2952 | 60.2276 | 60.1491 | 61.2996 | 61.3327 | 60.9369 | 61.2574 | 61.3065 | 61.2083 | 61.159 | 61.1597 | 61.1798 | 61.2703 | 61.154 | 60.3146 | 60.3364 | 60.2688 | 60.1903 | 61.3408 | 61.3739 | 60.9781 | 61.2986 | -1.0262 | -0.66347 | -1.072 | -0.70927
538.6406 | 121.9437 | -61.1847 | 60.4156 | 0.12185 | 0.037319 | -0.021157 | -0.025017 | -0.009515 | 0.085583 | -0.03067 | 60.2643 | 60.2907 | 60.2322 | 60.14 | 61.295 | 61.3327 | 60.9369 | 61.2619 | 61.3065 | 61.222 | 61.1635 | 61.1597 | 61.1752 | 61.2703 | 61.154 | 60.3055 | 60.3319 | 60.2734 | 60.1812 | 61.3362 | 61.3739 | 60.9781 | 61.3031 | -1.0308 | -0.67263 | -1.0628 | -0.70469
540.3906 | 121.8979 | -61.1938 | 60.4156 | 0.12185 | 0.03274 | -0.034893 | -0.011281 | -0.004937 | 0.085583 | -0.03067 | 60.2689 | 60.2907 | 60.2368 | 60.1491 | 61.2905 | 61.3327 | 60.9415 | 61.2482 | 61.3157 | 61.2266 | 61.159 | 61.1826 | 61.1889 | 61.2794 | 61.1632 | 60.3101 | 60.3319 | 60.278 | 60.1903 | 61.3317 | 61.3739 | 60.9827 | 61.2894 | -1.0216 | -0.67263 | -1.0537 | -0.70469
542.0938 | 121.9528 | -61.1938 | 60.3928 | 0.13101 | 0.028162 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.039826 | 60.2689 | 60.2952 | 60.2276 | 60.1491 | 61.295 | 61.3327 | 60.9461 | 61.2574 | 61.3249 | 61.222 | 61.1635 | 61.1688 | 61.1843 | 61.284 | 61.154 | 60.3101 | 60.3364 | 60.2688 | 60.1903 | 61.3362 | 61.3739 | 60.9873 | 61.2986 | -1.0262 | -0.67721 | -1.0674 | -0.71842
543.8438 | 121.8201 | -61.2167 | 60.3928 | 0.12185 | 0.037319 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.03067 | 60.2734 | 60.2952 | 60.2322 | 60.1491 | 61.295 | 61.3281 | 60.9323 | 61.2528 | 61.3386 | 61.2541 | 61.191 | 61.1963 | 61.2164 | 61.3023 | 61.1861 | 60.3146 | 60.3364 | 60.2734 | 60.1903 | 61.3362 | 61.3693 | 60.9735 | 61.294 | -1.0216 | -0.65889 | -1.0628 | -0.70011
545.5938 | 121.7926 | -61.3037 | 60.3012 | 0.11727 | 0.03274 | -0.021157 | -0.01586 | -0.004937 | 0.09474 | -0.026092 | 60.2689 | 60.2907 | 60.2276 | 60.1537 | 61.2859 | 61.3281 | 60.9369 | 61.2528 | 61.421 | 61.3365 | 61.2826 | 61.2879 | 61.2988 | 61.3985 | 61.2776 | 60.3101 | 60.3319 | 60.2688 | 60.1949 | 61.3271 | 61.3693 | 60.9781 | 61.294 | -1.017 | -0.66805 | -1.0582 | -0.70927
547.3438 | 121.8567 | -61.2854 | 60.3378 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | -0.000359 | 0.090161 | -0.03067 | 60.2734 | 60.2952 | 60.2322 | 60.1445 | 61.2905 | 61.3281 | 60.9415 | 61.2574 | 61.4073 | 61.3181 | 61.2642 | 61.265 | 61.285 | 61.3756 | 61.2547 | 60.3146 | 60.3364 | 60.2734 | 60.1857 | 61.3317 | 61.3693 | 60.9827 | 61.2986 | -1.017 | -0.66805 | -1.0582 | -0.70927
549.0938 | 121.9391 | -61.2579 | 60.26 | 0.12643 | 0.037319 | -0.030314 | -0.01586 | -0.009515 | 0.09474 | -0.035248 | 60.2734 | 60.2998 | 60.2322 | 60.1491 | 61.2859 | 61.3327 | 60.9323 | 61.2574 | 61.3844 | 61.2953 | 61.2276 | 61.2421 | 61.2484 | 61.3527 | 61.2227 | 60.3146 | 60.341 | 60.2734 | 60.1903 | 61.3271 | 61.3739 | 60.9735 | 61.2986 | -1.0124 | -0.65889 | -1.0537 | -0.70011
550.7656 | 121.9437 | -61.1755 | 60.4111 | 0.12185 | 0.03274 | -0.030314 | -0.01586 | -0.009515 | 0.085583 | -0.03067 | 60.2643 | 60.2861 | 60.2276 | 60.1491 | 61.295 | 61.3327 | 60.9461 | 61.2665 | 61.2974 | 61.2083 | 61.1452 | 61.1597 | 61.166 | 61.2611 | 61.1449 | 60.3055 | 60.3273 | 60.2688 | 60.1903 | 61.3362 | 61.3739 | 60.9873 | 61.3077 | -1.0308 | -0.68179 | -1.0674 | -0.71842
552.5156 | 121.8521 | -61.29 | 60.3195 | 0.12185 | 0.037319 | -0.025735 | -0.01586 | -0.000359 | 0.090161 | -0.03067 | 60.2689 | 60.2998 | 60.2322 | 60.1583 | 61.295 | 61.3373 | 60.9323 | 61.2574 | 61.4118 | 61.3273 | 61.2642 | 61.2741 | 61.2896 | 61.3801 | 61.2593 | 60.3101 | 60.341 | 60.2734 | 60.1995 | 61.3362 | 61.3785 | 60.9735 | 61.2986 | -1.0262 | -0.66347 | -1.0628 | -0.70011
554.2656 | 121.8109 | -61.322 | 60.3333 | 0.12185 | 0.037319 | -0.025735 | -0.025017 | -0.004937 | 0.090161 | -0.03067 | 60.2734 | 60.2952 | 60.2322 | 60.1491 | 61.295 | 61.3327 | 60.9323 | 61.2528 | 61.4439 | 61.3593 | 61.2963 | 61.297 | 61.3171 | 61.4122 | 61.2914 | 60.3146 | 60.3364 | 60.2734 | 60.1903 | 61.3362 | 61.3739 | 60.9735 | 61.294 | -1.0216 | -0.65889 | -1.0628 | -0.70011
555.9531 | 121.9437 | -61.2534 | 60.2737 | 0.12185 | 0.03274 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.035248 | 60.2689 | 60.2998 | 60.2322 | 60.1445 | 61.295 | 61.3281 | 60.9323 | 61.2619 | 61.3752 | 61.2861 | 61.2276 | 61.2329 | 61.253 | 61.3389 | 61.2181 | 60.3101 | 60.341 | 60.2734 | 60.1857 | 61.3362 | 61.3693 | 60.9735 | 61.3031 | -1.0262 | -0.66347 | -1.0628 | -0.70011
557.7031 | 121.9116 | -61.2579 | 60.347 | 0.12185 | 0.03274 | -0.030314 | -0.025017 | -0.004937 | 0.085583 | -0.03067 | 60.278 | 60.2907 | 60.2368 | 60.1537 | 61.2996 | 61.3418 | 60.9369 | 61.2665 | 61.3798 | 61.2907 | 61.2276 | 61.2329 | 61.253 | 61.3435 | 61.2273 | 60.3192 | 60.3319 | 60.278 | 60.1949 | 61.3408 | 61.383 | 60.9781 | 61.3077 | -1.0216 | -0.65889 | -1.0628 | -0.70011
559.3906 | 121.962 | -61.1664 | 60.3607 | 0.12643 | 0.03274 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.044405 | 60.2689 | 60.2952 | 60.2322 | 60.1491 | 61.295 | 61.3327 | 60.9461 | 61.2619 | 61.2928 | 61.1991 | 61.1406 | 61.1414 | 61.1569 | 61.252 | 61.122 | 60.3101 | 60.3364 | 60.2734 | 60.1903 | 61.3362 | 61.3739 | 60.9873 | 61.3031 | -1.0262 | -0.67721 | -1.0628 | -0.71384
561.1406 | 121.8796 | -61.2534 | 60.3561 | 0.13101 | 0.028162 | -0.021157 | -0.01586 | -0.004937 | 0.085583 | -0.026092 | 60.2597 | 60.2998 | 60.2322 | 60.1583 | 61.295 | 61.3281 | 60.9369 | 61.2619 | 61.3844 | 61.2815 | 61.2322 | 61.2375 | 61.2484 | 61.3389 | 61.2273 | 60.3009 | 60.341 | 60.2734 | 60.1995 | 61.3362 | 61.3693 | 60.9781 | 61.3031 | -1.0353 | -0.67721 | -1.0628 | -0.70469
562.875 | 121.8018 | -61.3083 | 60.3104 | 0.12643 | 0.028162 | -0.016578 | -0.020438 | -0.000359 | 0.090161 | -0.03067 | 60.2872 | 60.2907 | 60.2276 | 60.1537 | 61.2905 | 61.3281 | 60.9323 | 61.2619 | 61.4347 | 61.3365 | 61.2917 | 61.2879 | 61.3079 | 61.3985 | 61.2776 | 60.3284 | 60.3319 | 60.2688 | 60.1949 | 61.3317 | 61.3693 | 60.9735 | 61.3031 | -1.0033 | -0.64516 | -1.0628 | -0.70469
564.625 | 121.8292 | -61.3174 | 60.3195 | 0.12643 | 0.03274 | -0.025735 | -0.01586 | -0.004937 | 0.090161 | -0.026092 | 60.278 | 60.2952 | 60.2231 | 60.1445 | 61.2859 | 61.3373 | 60.9323 | 61.2574 | 61.4439 | 61.3502 | 61.2917 | 61.3016 | 61.3125 | 61.4076 | 61.2914 | 60.3192 | 60.3364 | 60.2643 | 60.1857 | 61.3271 | 61.3785 | 60.9735 | 61.2986 | -1.0079 | -0.65431 | -1.0628 | -0.70927
566.375 | 121.9528 | -61.1893 | 60.3607 | 0.11727 | 0.037319 | -0.030314 | -0.029595 | -0.009515 | 0.09474 | -0.039826 | 60.2689 | 60.2907 | 60.2276 | 60.1491 | 61.2996 | 61.3327 | 60.9323 | 61.2574 | 61.3065 | 61.2266 | 61.159 | 61.1597 | 61.1798 | 61.284 | 61.1494 | 60.3101 | 60.3319 | 60.2688 | 60.1903 | 61.3408 | 61.3739 | 60.9735 | 61.2986 | -1.0308 | -0.66347 | -1.072 | -0.70469
568.0625 | 121.8292 | -61.3174 | 60.3287 | 0.12185 | 0.028162 | -0.025735 | -0.01586 | -0.004937 | 0.090161 | -0.035248 | 60.278 | 60.2907 | 60.2276 | 60.1537 | 61.2905 | 61.3418 | 60.9369 | 61.2528 | 61.4393 | 61.3456 | 61.2917 | 61.3016 | 61.3125 | 61.4076 | 61.2822 | 60.3192 | 60.3319 | 60.2688 | 60.1949 | 61.3317 | 61.383 | 60.9781 | 61.294 | -1.0124 | -0.65889 | -1.0628 | -0.70927
569.75 | 121.8384 | -61.2442 | 60.4111 | 0.12643 | 0.03274 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.026092 | 60.2734 | 60.2952 | 60.2231 | 60.1445 | 61.2905 | 61.3281 | 60.9461 | 61.2574 | 61.3706 | 61.2769 | 61.2185 | 61.2238 | 61.2393 | 61.3298 | 61.2181 | 60.3146 | 60.3364 | 60.2643 | 60.1857 | 61.3317 | 61.3693 | 60.9873 | 61.2986 | -1.017 | -0.67263 | -1.0674 | -0.723
571.5 | 121.8292 | -61.2991 | 60.2966 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.026092 | 60.2643 | 60.2907 | 60.2276 | 60.1537 | 61.295 | 61.3281 | 60.9232 | 61.2574 | 61.4118 | 61.3273 | 61.278 | 61.2833 | 61.3034 | 61.3847 | 61.273 | 60.3055 | 60.3319 | 60.2688 | 60.1949 | 61.3362 | 61.3693 | 60.9644 | 61.2986 | -1.0308 | -0.65889 | -1.0674 | -0.69553
573.25 | 121.8567 | -61.3266 | 60.2783 | 0.12185 | 0.037319 | -0.030314 | -0.025017 | -0.004937 | 0.081005 | -0.026092 | 60.2734 | 60.2998 | 60.2322 | 60.1445 | 61.2905 | 61.3281 | 60.9323 | 61.2574 | 61.4485 | 61.3639 | 61.2963 | 61.3016 | 61.3217 | 61.4076 | 61.3005 | 60.3146 | 60.341 | 60.2734 | 60.1857 | 61.3317 | 61.3693 | 60.9735 | 61.2986 | -1.017 | -0.65889 | -1.0582 | -0.70011
575 | 121.9391 | -61.171 | 60.3699 | 0.11727 | 0.03274 | -0.025735 | -0.020438 | -0.009515 | 0.085583 | -0.035248 | 60.2689 | 60.2952 | 60.2322 | 60.1445 | 61.2996 | 61.3281 | 60.9369 | 61.2619 | 61.2882 | 61.2037 | 61.1452 | 61.1505 | 61.1614 | 61.2565 | 61.1357 | 60.3101 | 60.3364 | 60.2734 | 60.1857 | 61.3408 | 61.3693 | 60.9781 | 61.3031 | -1.0308 | -0.66805 | -1.0674 | -0.70469
576.75 | 121.8521 | -61.2534 | 60.3699 | 0.12185 | 0.03274 | -0.030314 | -0.020438 | 0.004219 | 0.090161 | -0.03067 | 60.2734 | 60.2907 | 60.2368 | 60.1583 | 61.295 | 61.3327 | 60.9278 | 61.2574 | 61.3752 | 61.2861 | 61.223 | 61.2329 | 61.2576 | 61.3435 | 61.2227 | 60.3146 | 60.3319 | 60.278 | 60.1995 | 61.3362 | 61.3739 | 60.9689 | 61.2986 | -1.0216 | -0.65432 | -1.0582 | -0.69095
578.4375 | 121.8933 | -61.2213 | 60.3653 | 0.11269 | 0.028162 | -0.025735 | -0.020438 | -0.004937 | 0.081005 | -0.039826 | 60.2734 | 60.3044 | 60.2368 | 60.1445 | 61.295 | 61.3327 | 60.9415 | 61.2574 | 61.334 | 61.2495 | 61.1956 | 61.2009 | 61.2164 | 61.3023 | 61.1815 | 60.3146 | 60.3456 | 60.278 | 60.1857 | 61.3362 | 61.3739 | 60.9827 | 61.2986 | -1.0216 | -0.66805 | -1.0582 | -0.70469
580.1875 | 121.8704 | -61.2625 | 60.3653 | 0.12643 | 0.03274 | -0.030314 | -0.01586 | -0.000359 | 0.085583 | -0.026092 | 60.2689 | 60.2998 | 60.2368 | 60.1491 | 61.2859 | 61.3373 | 60.9323 | 61.2665 | 61.3889 | 61.2953 | 61.2322 | 61.2467 | 61.2622 | 61.3481 | 61.2364 | 60.3101 | 60.341 | 60.278 | 60.1903 | 61.3271 | 61.3785 | 60.9735 | 61.3077 | -1.017 | -0.66347 | -1.0491 | -0.69553
581.9375 | 121.843 | -61.3174 | 60.3104 | 0.12185 | 0.037319 | -0.021157 | -0.01586 | -0.009515 | 0.085583 | -0.039826 | 60.278 | 60.2907 | 60.2322 | 60.1537 | 61.295 | 61.3327 | 60.9278 | 61.2574 | 61.4393 | 61.3548 | 61.2963 | 61.3016 | 61.3079 | 61.403 | 61.2776 | 60.3192 | 60.3319 | 60.2734 | 60.1949 | 61.3362 | 61.3739 | 60.9689 | 61.2986 | -1.017 | -0.64974 | -1.0628 | -0.69553
583.6875 | 121.8658 | -61.2122 | 60.4065 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2689 | 60.2952 | 60.2276 | 60.1445 | 61.295 | 61.3327 | 60.9415 | 61.2528 | 61.334 | 61.2357 | 61.191 | 61.1871 | 61.2072 | 61.2977 | 61.1769 | 60.3101 | 60.3364 | 60.2688 | 60.1857 | 61.3362 | 61.3739 | 60.9827 | 61.294 | -1.0262 | -0.67263 | -1.0674 | -0.71385
585.3594 | 121.8292 | -61.2991 | 60.2921 | 0.12643 | 0.037319 | -0.025735 | -0.020438 | -0.004937 | 0.090161 | -0.026092 | 60.2826 | 60.2998 | 60.2368 | 60.1491 | 61.295 | 61.3327 | 60.9323 | 61.2619 | 61.4256 | 61.3365 | 61.2734 | 61.2787 | 61.2942 | 61.3893 | 61.273 | 60.3238 | 60.341 | 60.278 | 60.1903 | 61.3362 | 61.3739 | 60.9735 | 61.3031 | -1.0124 | -0.64974 | -1.0582 | -0.69553
587.1094 | 121.9299 | -61.203 | 60.3745 | 0.11727 | 0.019004 | -0.034893 | -0.020438 | -0.004937 | 0.090161 | -0.03067 | 60.2734 | 60.2998 | 60.2276 | 60.1445 | 61.2905 | 61.3327 | 60.9369 | 61.2528 | 61.3203 | 61.222 | 61.1681 | 61.1826 | 61.1981 | 61.2932 | 61.1723 | 60.3146 | 60.341 | 60.2688 | 60.1857 | 61.3317 | 61.3739 | 60.9781 | 61.294 | -1.017 | -0.66347 | -1.0628 | -0.70927
588.8438 | 121.9391 | -61.2717 | 60.2966 | 0.12643 | 0.019004 | -0.034893 | -0.020438 | -0.004937 | 0.085583 | -0.03067 | 60.278 | 60.2952 | 60.2368 | 60.1629 | 61.295 | 61.3327 | 60.9369 | 61.2574 | 61.3981 | 61.2907 | 61.2368 | 61.2512 | 61.2667 | 61.3573 | 61.241 | 60.3192 | 60.3364 | 60.278 | 60.2041 | 61.3362 | 61.3739 | 60.9781 | 61.2986 | -1.017 | -0.65889 | -1.0582 | -0.70011
590.5781 | 121.962 | -61.1847 | 60.3745 | 0.11269 | 0.028162 | -0.030314 | -0.025017 | -0.009515 | 0.085583 | -0.035248 | 60.2643 | 60.2998 | 60.2322 | 60.1491 | 61.295 | 61.3418 | 60.9369 | 61.2528 | 61.2974 | 61.2129 | 61.1544 | 61.1597 | 61.1752 | 61.2703 | 61.1494 | 60.3055 | 60.341 | 60.2734 | 60.1903 | 61.3362 | 61.383 | 60.9781 | 61.294 | -1.0308 | -0.67263 | -1.0628 | -0.70469
592.3281 | 121.9574 | -61.2579 | 60.2783 | 0.11269 | 0.023583 | -0.030314 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.278 | 60.2952 | 60.2276 | 60.14 | 61.295 | 61.3373 | 60.9278 | 61.2619 | 61.3706 | 61.2815 | 61.2276 | 61.2329 | 61.253 | 61.3435 | 61.2227 | 60.3192 | 60.3364 | 60.2688 | 60.1812 | 61.3362 | 61.3785 | 60.9689 | 61.3031 | -1.017 | -0.64974 | -1.0674 | -0.70011
594 | 121.8384 | -61.2122 | 60.434 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | -0.009515 | 0.085583 | -0.035248 | 60.2689 | 60.2998 | 60.2276 | 60.1445 | 61.2905 | 61.3281 | 60.9461 | 61.2619 | 61.3294 | 61.2357 | 61.191 | 61.1917 | 61.2026 | 61.2977 | 61.1769 | 60.3101 | 60.341 | 60.2688 | 60.1857 | 61.3317 | 61.3693 | 60.9873 | 61.3031 | -1.0216 | -0.67721 | -1.0628 | -0.71842
595.7344 | 121.8613 | -61.2671 | 60.3836 | 0.12185 | 0.028162 | -0.025735 | -0.020438 | -0.004937 | 0.090161 | -0.026092 | 60.278 | 60.2998 | 60.2368 | 60.1491 | 61.295 | 61.3327 | 60.9369 | 61.2619 | 61.3889 | 61.2953 | 61.2414 | 61.2467 | 61.2622 | 61.3573 | 61.241 | 60.3192 | 60.341 | 60.278 | 60.1903 | 61.3362 | 61.3739 | 60.9781 | 61.3031 | -1.017 | -0.65889 | -1.0582 | -0.70011
597.4219 | 121.8704 | -61.2671 | 60.3653 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | -0.004937 | 0.090161 | -0.035248 | 60.2689 | 60.2952 | 60.2414 | 60.1445 | 61.295 | 61.3327 | 60.9369 | 61.2619 | 61.3844 | 61.2907 | 61.2459 | 61.2467 | 61.2622 | 61.3573 | 61.2318 | 60.3101 | 60.3364 | 60.2826 | 60.1857 | 61.3362 | 61.3739 | 60.9781 | 61.3031 | -1.0262 | -0.66805 | -1.0537 | -0.69553
599.1562 | 121.8018 | -61.3312 | 60.3149 | 0.12185 | 0.023583 | -0.030314 | -0.020438 | -0.004937 | 0.090161 | -0.03067 | 60.2826 | 60.2952 | 60.2414 | 60.1491 | 61.295 | 61.3281 | 60.9323 | 61.2619 | 61.453 | 61.3548 | 61.3009 | 61.3107 | 61.3262 | 61.4213 | 61.3005 | 60.3238 | 60.3364 | 60.2826 | 60.1903 | 61.3362 | 61.3693 | 60.9735 | 61.3031 | -1.0124 | -0.64974 | -1.0537 | -0.69095
600.9062 | 121.8842 | -61.2213 | 60.3516 | 0.12643 | 0.023583 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.026092 | 60.2734 | 60.2998 | 60.2322 | 60.14 | 61.2859 | 61.3373 | 60.9461 | 61.2574 | 61.3477 | 61.2449 | 61.1956 | 61.2009 | 61.2164 | 61.3069 | 61.1952 | 60.3146 | 60.341 | 60.2734 | 60.1812 | 61.3271 | 61.3785 | 60.9873 | 61.2986 | -1.0124 | -0.67263 | -1.0537 | -0.71384
602.5938 | 121.8796 | -61.2396 | 60.4111 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | -0.014093 | 0.085583 | -0.035248 | 60.2734 | 60.3044 | 60.2368 | 60.1537 | 61.2905 | 61.3281 | 60.9461 | 61.2619 | 61.3615 | 61.2678 | 61.2185 | 61.2192 | 61.2255 | 61.3252 | 61.2044 | 60.3146 | 60.3456 | 60.278 | 60.1949 | 61.3317 | 61.3693 | 60.9873 | 61.3031 | -1.017 | -0.67263 | -1.0537 | -0.70927
604.3281 | 121.9162 | -61.2076 | 60.379 | 0.12643 | 0.028162 | -0.039471 | -0.029595 | -0.004937 | 0.085583 | -0.035248 | 60.2734 | 60.2998 | 60.2414 | 60.1445 | 61.2905 | 61.3327 | 60.9461 | 61.2574 | 61.334 | 61.2357 | 61.1681 | 61.178 | 61.2026 | 61.2932 | 61.1723 | 60.3146 | 60.341 | 60.2826 | 60.1857 | 61.3317 | 61.3739 | 60.9873 | 61.2986 | -1.017 | -0.67263 | -1.0491 | -0.70469
606 | 121.8201 | -61.2442 | 60.434 | 0.12185 | 0.023583 | -0.025735 | -0.01586 | -0.004937 | 0.090161 | -0.03067 | 60.278 | 60.2998 | 60.2322 | 60.1537 | 61.295 | 61.3235 | 60.9461 | 61.2574 | 61.3661 | 61.2678 | 61.2185 | 61.2283 | 61.2393 | 61.3344 | 61.2135 | 60.3192 | 60.341 | 60.2734 | 60.1949 | 61.3362 | 61.3647 | 60.9873 | 61.2986 | -1.017 | -0.66805 | -1.0628 | -0.71384
607.75 | 121.9528 | -61.2579 | 60.2829 | 0.11727 | 0.03274 | -0.034893 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2643 | 60.2952 | 60.2322 | 60.1445 | 61.2905 | 61.3327 | 60.9278 | 61.2574 | 61.3752 | 61.2907 | 61.223 | 61.2375 | 61.253 | 61.3435 | 61.2227 | 60.3055 | 60.3364 | 60.2734 | 60.1857 | 61.3317 | 61.3739 | 60.9689 | 61.2986 | -1.0262 | -0.66347 | -1.0582 | -0.69553
609.5 | 121.9299 | -61.2717 | 60.3012 | 0.11727 | 0.019004 | -0.034893 | -0.01586 | -0.009515 | 0.081005 | -0.03067 | 60.2689 | 60.2998 | 60.2368 | 60.1491 | 61.2996 | 61.3373 | 60.9369 | 61.2574 | 61.3889 | 61.2907 | 61.2368 | 61.2558 | 61.2622 | 61.3527 | 61.241 | 60.3101 | 60.341 | 60.278 | 60.1903 | 61.3408 | 61.3785 | 60.9781 | 61.2986 | -1.0308 | -0.66805 | -1.0628 | -0.70011
611.1875 | 121.8109 | -61.3266 | 60.3058 | 0.11727 | 0.023583 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.035248 | 60.278 | 60.2952 | 60.2322 | 60.1445 | 61.295 | 61.3281 | 60.9323 | 61.2574 | 61.4439 | 61.3502 | 61.3009 | 61.3062 | 61.3262 | 61.4122 | 61.2914 | 60.3192 | 60.3364 | 60.2734 | 60.1857 | 61.3362 | 61.3693 | 60.9735 | 61.2986 | -1.017 | -0.65431 | -1.0628 | -0.70011
612.9375 | 121.907 | -61.2259 | 60.3745 | 0.12643 | 0.019004 | -0.021157 | -0.01586 | -0.014093 | 0.085583 | -0.026092 | 60.2734 | 60.2907 | 60.2322 | 60.14 | 61.295 | 61.3281 | 60.9323 | 61.2619 | 61.3523 | 61.2449 | 61.2047 | 61.21 | 61.2118 | 61.3115 | 61.1998 | 60.3146 | 60.3319 | 60.2734 | 60.1812 | 61.3362 | 61.3693 | 60.9735 | 61.3031 | -1.0216 | -0.65889 | -1.0628 | -0.70011
614.6875 | 121.875 | -61.2076 | 60.4065 | 0.12185 | 0.023583 | -0.030314 | -0.01586 | -0.004937 | 0.081005 | -0.03067 | 60.278 | 60.2952 | 60.2322 | 60.1537 | 61.295 | 61.3327 | 60.9369 | 61.2619 | 61.3294 | 61.2312 | 61.1773 | 61.1917 | 61.2026 | 61.2886 | 61.1769 | 60.3192 | 60.3364 | 60.2734 | 60.1949 | 61.3362 | 61.3739 | 60.9781 | 61.3031 | -1.017 | -0.65889 | -1.0628 | -0.70469
616.375 | 121.8658 | -61.3129 | 60.2783 | 0.12185 | 0.019004 | -0.025735 | -0.020438 | 0.004219 | 0.09474 | -0.03067 | 60.2734 | 60.2998 | 60.2414 | 60.1491 | 61.2905 | 61.3327 | 60.9369 | 61.2528 | 61.4347 | 61.3319 | 61.2871 | 61.2924 | 61.3171 | 61.4076 | 61.2822 | 60.3146 | 60.341 | 60.2826 | 60.1903 | 61.3317 | 61.3739 | 60.9781 | 61.294 | -1.017 | -0.66347 | -1.0491 | -0.69553
618.125 | 121.9345 | -61.1755 | 60.3836 | 0.12185 | 0.019004 | -0.034893 | -0.020438 | -0.009515 | 0.081005 | -0.035248 | 60.2734 | 60.2952 | 60.2368 | 60.1491 | 61.295 | 61.3373 | 60.9323 | 61.2665 | 61.2974 | 61.1945 | 61.1406 | 61.1551 | 61.166 | 61.2565 | 61.1403 | 60.3146 | 60.3364 | 60.278 | 60.1903 | 61.3362 | 61.3785 | 60.9735 | 61.3077 | -1.0216 | -0.65889 | -1.0582 | -0.69553
619.8125 | 121.907 | -61.2213 | 60.3516 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | -0.009515 | 0.085583 | -0.035248 | 60.2734 | 60.2952 | 60.2322 | 60.1445 | 61.2905 | 61.3189 | 60.9415 | 61.2619 | 61.3432 | 61.2449 | 61.2002 | 61.2055 | 61.2118 | 61.3069 | 61.1861 | 60.3146 | 60.3364 | 60.2734 | 60.1857 | 61.3317 | 61.3601 | 60.9827 | 61.3031 | -1.017 | -0.66805 | -1.0582 | -0.70927
621.5625 | 121.8018 | -61.3449 | 60.3149 | 0.12643 | 0.028162 | -0.025735 | -0.01586 | 0.004219 | 0.085583 | -0.035248 | 60.278 | 60.2998 | 60.2322 | 60.1491 | 61.295 | 61.3327 | 60.9415 | 61.2574 | 61.4713 | 61.3731 | 61.3192 | 61.329 | 61.3491 | 61.4305 | 61.3097 | 60.3192 | 60.341 | 60.2734 | 60.1903 | 61.3362 | 61.3739 | 60.9827 | 61.2986 | -1.017 | -0.66347 | -1.0628 | -0.70927
623.25 | 121.7972 | -61.3358 | 60.3149 | 0.12185 | 0.023583 | -0.025735 | -0.01586 | -0.004937 | 0.090161 | -0.03067 | 60.278 | 60.2998 | 60.2414 | 60.1537 | 61.295 | 61.3327 | 60.9323 | 61.2619 | 61.4576 | 61.3593 | 61.31 | 61.3199 | 61.3308 | 61.4259 | 61.3051 | 60.3192 | 60.341 | 60.2826 | 60.1949 | 61.3362 | 61.3739 | 60.9735 | 61.3031 | -1.017 | -0.65431 | -1.0537 | -0.69095
624.9375 | 121.962 | -61.203 | 60.3836 | 0.11727 | 0.019004 | -0.030314 | -0.01586 | -0.009515 | 0.085583 | -0.03067 | 60.2689 | 60.2861 | 60.2368 | 60.1537 | 61.2905 | 61.3373 | 60.9323 | 61.2574 | 61.3203 | 61.222 | 61.1727 | 61.1871 | 61.1935 | 61.2886 | 61.1723 | 60.3101 | 60.3273 | 60.278 | 60.1949 | 61.3317 | 61.3785 | 60.9735 | 61.2986 | -1.0216 | -0.66347 | -1.0537 | -0.69553
626.6875 | 121.9391 | -61.1893 | 60.3928 | 0.12185 | 0.023583 | -0.030314 | -0.01586 | -0.009515 | 0.085583 | -0.026092 | 60.278 | 60.2952 | 60.2368 | 60.1445 | 61.2905 | 61.3373 | 60.9369 | 61.2574 | 61.3111 | 61.2129 | 61.159 | 61.1734 | 61.1798 | 61.2749 | 61.1632 | 60.3192 | 60.3364 | 60.278 | 60.1857 | 61.3317 | 61.3785 | 60.9781 | 61.2986 | -1.0124 | -0.65889 | -1.0537 | -0.70011
628.375 | 121.9208 | -61.2488 | 60.3241 | 0.12185 | 0.023583 | -0.030314 | -0.020438 | -0.004937 | 0.090161 | -0.035248 | 60.2734 | 60.2952 | 60.246 | 60.1491 | 61.2996 | 61.3327 | 60.9323 | 61.2665 | 61.3706 | 61.2724 | 61.2185 | 61.2283 | 61.2438 | 61.3389 | 61.2135 | 60.3146 | 60.3364 | 60.2872 | 60.1903 | 61.3408 | 61.3739 | 60.9735 | 61.3077 | -1.0262 | -0.65889 | -1.0537 | -0.68637
630.125 | 121.9482 | -61.171 | 60.3836 | 0.12185 | 0.028162 | -0.025735 | -0.025017 | -0.009515 | 0.090161 | -0.03067 | 60.278 | 60.2907 | 60.2368 | 60.1491 | 61.295 | 61.3373 | 60.9461 | 61.2619 | 61.2928 | 61.1991 | 61.1452 | 61.1459 | 61.1614 | 61.2611 | 61.1403 | 60.3192 | 60.3319 | 60.278 | 60.1903 | 61.3362 | 61.3785 | 60.9873 | 61.3031 | -1.017 | -0.66805 | -1.0582 | -0.70927
631.8125 | 121.8109 | -61.322 | 60.3378 | 0.12643 | 0.028162 | -0.030314 | -0.025017 | -0.000359 | 0.090161 | -0.035248 | 60.2826 | 60.2907 | 60.2368 | 60.1491 | 61.2996 | 61.3327 | 60.9323 | 61.2619 | 61.4485 | 61.3502 | 61.2917 | 61.297 | 61.3217 | 61.4122 | 61.2868 | 60.3238 | 60.3319 | 60.278 | 60.1903 | 61.3408 | 61.3739 | 60.9735 | 61.3031 | -1.017 | -0.64974 | -1.0628 | -0.69553
633.5625 | 121.8155 | -61.3174 | 60.3378 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | -0.004937 | 0.090161 | -0.026092 | 60.2689 | 60.2998 | 60.2414 | 60.1491 | 61.2996 | 61.3373 | 60.9323 | 61.2574 | 61.4393 | 61.341 | 61.2963 | 61.3016 | 61.3125 | 61.4076 | 61.2914 | 60.3101 | 60.341 | 60.2826 | 60.1903 | 61.3408 | 61.3785 | 60.9735 | 61.2986 | -1.0308 | -0.66347 | -1.0582 | -0.69095
635.25 | 121.8933 | -61.235 | 60.3699 | 0.11727 | 0.023583 | -0.030314 | -0.020438 | -0.009515 | 0.085583 | -0.039826 | 60.2689 | 60.3044 | 60.2368 | 60.1491 | 61.295 | 61.3281 | 60.9369 | 61.2574 | 61.3523 | 61.2586 | 61.2047 | 61.2146 | 61.2255 | 61.3206 | 61.1952 | 60.3101 | 60.3456 | 60.278 | 60.1903 | 61.3362 | 61.3693 | 60.9781 | 61.2986 | -1.0262 | -0.66805 | -1.0582 | -0.70011
637 | 121.9116 | -61.2488 | 60.3104 | 0.12185 | 0.028162 | -0.025735 | -0.020438 | -0.004937 | 0.085583 | -0.039826 | 60.278 | 60.2998 | 60.2276 | 60.1537 | 61.2905 | 61.3373 | 60.9369 | 61.2528 | 61.3706 | 61.2769 | 61.223 | 61.2283 | 61.2438 | 61.3344 | 61.209 | 60.3192 | 60.341 | 60.2688 | 60.1949 | 61.3317 | 61.3785 | 60.9781 | 61.294 | -1.0124 | -0.65889 | -1.0628 | -0.70927
638.7656 | 121.875 | -61.2854 | 60.347 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | -0.004937 | 0.090161 | -0.021514 | 60.2872 | 60.2998 | 60.2368 | 60.1445 | 61.2905 | 61.3235 | 60.9323 | 61.2574 | 61.4118 | 61.3136 | 61.2642 | 61.265 | 61.2805 | 61.3756 | 61.2639 | 60.3284 | 60.341 | 60.278 | 60.1857 | 61.3317 | 61.3647 | 60.9735 | 61.2986 | -1.0033 | -0.64516 | -1.0537 | -0.69553
640.4375 | 121.9345 | -61.2762 | 60.2783 | 0.12643 | 0.023583 | -0.025735 | -0.01586 | -0.000359 | 0.09474 | -0.026092 | 60.2826 | 60.3044 | 60.2368 | 60.1491 | 61.2996 | 61.3373 | 60.9323 | 61.2528 | 61.4027 | 61.2998 | 61.2505 | 61.2604 | 61.2759 | 61.371 | 61.2502 | 60.3238 | 60.3456 | 60.278 | 60.1903 | 61.3408 | 61.3785 | 60.9735 | 61.294 | -1.017 | -0.64974 | -1.0628 | -0.69553
642.1875 | 121.907 | -61.2213 | 60.3241 | 0.11727 | 0.023583 | -0.030314 | -0.025017 | -0.009515 | 0.085583 | -0.026092 | 60.2734 | 60.2998 | 60.2276 | 60.1537 | 61.2996 | 61.3327 | 60.9278 | 61.2619 | 61.3386 | 61.2449 | 61.191 | 61.1963 | 61.2118 | 61.3069 | 61.1952 | 60.3146 | 60.341 | 60.2688 | 60.1949 | 61.3408 | 61.3739 | 60.9689 | 61.3031 | -1.0262 | -0.65432 | -1.072 | -0.70011
643.875 | 121.8796 | -61.2854 | 60.3836 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | -0.000359 | 0.090161 | -0.026092 | 60.2826 | 60.2998 | 60.2368 | 60.1445 | 61.2996 | 61.3281 | 60.9369 | 61.2619 | 61.4118 | 61.3136 | 61.2642 | 61.265 | 61.285 | 61.3756 | 61.2593 | 60.3238 | 60.341 | 60.278 | 60.1857 | 61.3408 | 61.3693 | 60.9781 | 61.3031 | -1.017 | -0.65431 | -1.0628 | -0.70011
645.625 | 121.8338 | -61.2534 | 60.3973 | 0.13101 | 0.03274 | -0.021157 | -0.025017 | -0.000359 | 0.085583 | -0.035248 | 60.2826 | 60.2952 | 60.2368 | 60.1354 | 61.2859 | 61.3281 | 60.9323 | 61.2574 | 61.3844 | 61.2861 | 61.2322 | 61.2283 | 61.253 | 61.3389 | 61.2181 | 60.3238 | 60.3364 | 60.278 | 60.1766 | 61.3271 | 61.3693 | 60.9735 | 61.2986 | -1.0033 | -0.64974 | -1.0491 | -0.69553
647.3125 | 121.8887 | -61.2122 | 60.4202 | 0.12185 | 0.028162 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.026092 | 60.2734 | 60.2998 | 60.2368 | 60.1491 | 61.2996 | 61.3327 | 60.9323 | 61.2574 | 61.334 | 61.2403 | 61.1818 | 61.1871 | 61.2026 | 61.3023 | 61.1861 | 60.3146 | 60.341 | 60.278 | 60.1903 | 61.3408 | 61.3739 | 60.9735 | 61.2986 | -1.0262 | -0.65889 | -1.0628 | -0.69553
649.0625 | 121.7926 | -61.3266 | 60.3012 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | -0.000359 | 0.090161 | -0.021514 | 60.2826 | 60.3044 | 60.2322 | 60.1491 | 61.295 | 61.3418 | 60.9323 | 61.2619 | 61.4485 | 61.3548 | 61.3054 | 61.3062 | 61.3262 | 61.4168 | 61.3051 | 60.3238 | 60.3456 | 60.2734 | 60.1903 | 61.3362 | 61.383 | 60.9735 | 61.3031 | -1.0124 | -0.64974 | -1.0628 | -0.70011
650.8125 | 121.8018 | -61.2991 | 60.3287 | 0.11727 | 0.023583 | -0.025735 | -0.011281 | -0.009515 | 0.085583 | -0.039826 | 60.2734 | 60.2952 | 60.2322 | 60.1491 | 61.295 | 61.3418 | 60.9278 | 61.2574 | 61.4164 | 61.3227 | 61.2734 | 61.2879 | 61.2896 | 61.3847 | 61.2593 | 60.3146 | 60.3364 | 60.2734 | 60.1903 | 61.3362 | 61.383 | 60.9689 | 61.2986 | -1.0216 | -0.65432 | -1.0628 | -0.69553
652.5156 | 121.9025 | -61.2305 | 60.347 | 0.12185 | 0.023583 | -0.030314 | -0.025017 | -0.004937 | 0.090161 | -0.035248 | 60.2689 | 60.2998 | 60.2368 | 60.1445 | 61.2996 | 61.3327 | 60.9278 | 61.2619 | 61.3523 | 61.2541 | 61.2002 | 61.2055 | 61.2255 | 61.3206 | 61.1952 | 60.3101 | 60.341 | 60.278 | 60.1857 | 61.3408 | 61.3739 | 60.9689 | 61.3031 | -1.0308 | -0.65889 | -1.0628 | -0.69095
654.25 | 121.962 | -61.1984 | 60.3973 | 0.12643 | 0.023583 | -0.016578 | -0.025017 | -0.009515 | 0.090161 | -0.035248 | 60.2734 | 60.2907 | 60.2368 | 60.14 | 61.295 | 61.3373 | 60.9415 | 61.2619 | 61.3249 | 61.222 | 61.1818 | 61.1734 | 61.1889 | 61.2886 | 61.1632 | 60.3146 | 60.3319 | 60.278 | 60.1812 | 61.3362 | 61.3785 | 60.9827 | 61.3031 | -1.0216 | -0.66805 | -1.0582 | -0.70469
655.9219 | 121.8567 | -61.2579 | 60.3424 | 0.13101 | 0.03274 | -0.025735 | -0.025017 | -0.000359 | 0.09474 | -0.026092 | 60.2826 | 60.2952 | 60.2368 | 60.1491 | 61.2996 | 61.3418 | 60.9369 | 61.2619 | 61.3889 | 61.2907 | 61.2322 | 61.2329 | 61.2576 | 61.3527 | 61.2318 | 60.3238 | 60.3364 | 60.278 | 60.1903 | 61.3408 | 61.383 | 60.9781 | 61.3031 | -1.017 | -0.65431 | -1.0628 | -0.70011
657.6562 | 121.7972 | -61.3174 | 60.3149 | 0.11269 | 0.03274 | -0.021157 | -0.020438 | -0.004937 | 0.090161 | -0.03067 | 60.2826 | 60.2998 | 60.2414 | 60.1491 | 61.2996 | 61.3327 | 60.9278 | 61.2574 | 61.4301 | 61.3502 | 61.2963 | 61.297 | 61.3125 | 61.4076 | 61.2868 | 60.3238 | 60.341 | 60.2826 | 60.1903 | 61.3408 | 61.3739 | 60.9689 | 61.2986 | -1.017 | -0.64516 | -1.0582 | -0.68638
659.3438 | 121.8933 | -61.2442 | 60.3745 | 0.12185 | 0.028162 | -0.030314 | -0.020438 | -0.009515 | 0.085583 | -0.035248 | 60.2826 | 60.3044 | 60.2368 | 60.1491 | 61.2996 | 61.3327 | 60.9323 | 61.2574 | 61.3661 | 61.2724 | 61.2139 | 61.2238 | 61.2347 | 61.3298 | 61.209 | 60.3238 | 60.3456 | 60.278 | 60.1903 | 61.3408 | 61.3739 | 60.9735 | 61.2986 | -1.017 | -0.64974 | -1.0628 | -0.69553
661.0781 | 121.9162 | -61.2488 | 60.3745 | 0.11727 | 0.028162 | -0.034893 | -0.020438 | -0.009515 | 0.081005 | -0.039826 | 60.2734 | 60.2952 | 60.2414 | 60.1445 | 61.2996 | 61.3327 | 60.9323 | 61.2574 | 61.3661 | 61.2769 | 61.2139 | 61.2283 | 61.2393 | 61.3298 | 61.209 | 60.3146 | 60.3364 | 60.2826 | 60.1857 | 61.3408 | 61.3739 | 60.9735 | 61.2986 | -1.0262 | -0.65889 | -1.0582 | -0.69095
662.8438 | 121.8246 | -61.3358 | 60.3058 | 0.12643 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.026092 | 60.278 | 60.2998 | 60.2414 | 60.1537 | 61.295 | 61.3327 | 60.9323 | 61.2574 | 61.4622 | 61.3639 | 61.3146 | 61.3199 | 61.3446 | 61.4213 | 61.3097 | 60.3192 | 60.341 | 60.2826 | 60.1949 | 61.3362 | 61.3739 | 60.9735 | 61.2986 | -1.017 | -0.65431 | -1.0537 | -0.69095
664.5156 | 121.962 | -61.2122 | 60.4019 | 0.12185 | 0.03274 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.026092 | 60.2872 | 60.2952 | 60.2276 | 60.1537 | 61.3042 | 61.3373 | 60.9369 | 61.2574 | 61.334 | 61.2449 | 61.1818 | 61.1871 | 61.2118 | 61.2977 | 61.1861 | 60.3284 | 60.3364 | 60.2688 | 60.1949 | 61.3454 | 61.3785 | 60.9781 | 61.2986 | -1.017 | -0.64974 | -1.0766 | -0.70927
666.25 | 121.8842 | -61.203 | 60.4019 | 0.12643 | 0.03274 | -0.030314 | -0.01586 | -0.009515 | 0.085583 | -0.039826 | 60.278 | 60.2998 | 60.2414 | 60.1491 | 61.2996 | 61.3418 | 60.9415 | 61.2619 | 61.3294 | 61.2357 | 61.1727 | 61.1871 | 61.1935 | 61.2886 | 61.1632 | 60.3192 | 60.341 | 60.2826 | 60.1903 | 61.3408 | 61.383 | 60.9827 | 61.3031 | -1.0216 | -0.66347 | -1.0582 | -0.70011
667.9375 | 121.8384 | -61.235 | 60.3928 | 0.12185 | 0.03274 | -0.034893 | -0.025017 | -0.004937 | 0.090161 | -0.021514 | 60.2734 | 60.3044 | 60.2368 | 60.1491 | 61.3042 | 61.3327 | 60.9232 | 61.2711 | 61.3569 | 61.2678 | 61.2002 | 61.21 | 61.2301 | 61.3252 | 61.2135 | 60.3146 | 60.3456 | 60.278 | 60.1903 | 61.3454 | 61.3739 | 60.9644 | 61.3123 | -1.0308 | -0.64974 | -1.0674 | -0.68638
669.6719 | 121.8704 | -61.2625 | 60.3607 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | -0.000359 | 0.081005 | -0.03067 | 60.278 | 60.2998 | 60.246 | 60.1583 | 61.2996 | 61.3327 | 60.9369 | 61.2619 | 61.3844 | 61.2953 | 61.2414 | 61.2467 | 61.2622 | 61.3435 | 61.2318 | 60.3192 | 60.341 | 60.2872 | 60.1995 | 61.3408 | 61.3739 | 60.9781 | 61.3031 | -1.0216 | -0.65889 | -1.0537 | -0.69095
671.3438 | 121.9482 | -61.2671 | 60.2737 | 0.12643 | 0.03274 | -0.030314 | -0.025017 | -0.004937 | 0.081005 | -0.03067 | 60.278 | 60.3044 | 60.2414 | 60.1491 | 61.2996 | 61.3327 | 60.9278 | 61.2665 | 61.3935 | 61.2998 | 61.2368 | 61.2421 | 61.2622 | 61.3481 | 61.2364 | 60.3192 | 60.3456 | 60.2826 | 60.1903 | 61.3408 | 61.3739 | 60.9689 | 61.3077 | -1.0216 | -0.64974 | -1.0582 | -0.68638
673.0938 | 121.9528 | -61.2717 | 60.26 | 0.12185 | 0.037319 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.035248 | 60.278 | 60.2998 | 60.2322 | 60.1491 | 61.3042 | 61.3373 | 60.9369 | 61.2619 | 61.3935 | 61.309 | 61.2414 | 61.2467 | 61.2622 | 61.3618 | 61.2364 | 60.3192 | 60.341 | 60.2734 | 60.1903 | 61.3454 | 61.3785 | 60.9781 | 61.3031 | -1.0262 | -0.65889 | -1.072 | -0.70469
674.7812 | 121.8521 | -61.2625 | 60.3333 | 0.12185 | 0.041898 | -0.025735 | -0.020438 | -0.000359 | 0.090161 | -0.03067 | 60.2734 | 60.3044 | 60.2368 | 60.1491 | 61.2905 | 61.3327 | 60.9278 | 61.2528 | 61.3844 | 61.3044 | 61.2368 | 61.2421 | 61.2622 | 61.3527 | 61.2318 | 60.3146 | 60.3456 | 60.278 | 60.1903 | 61.3317 | 61.3739 | 60.9689 | 61.294 | -1.017 | -0.65432 | -1.0537 | -0.69095
676.5312 | 121.9437 | -61.2808 | 60.2829 | 0.12643 | 0.03274 | -0.030314 | -0.01586 | -0.004937 | 0.090161 | -0.035248 | 60.278 | 60.2998 | 60.2368 | 60.1491 | 61.2996 | 61.3373 | 60.9369 | 61.2574 | 61.4073 | 61.3136 | 61.2505 | 61.265 | 61.2759 | 61.371 | 61.2456 | 60.3192 | 60.341 | 60.278 | 60.1903 | 61.3408 | 61.3785 | 60.9781 | 61.2986 | -1.0216 | -0.65889 | -1.0628 | -0.70011
678.2812 | 121.9437 | -61.2534 | 60.3058 | 0.12185 | 0.03274 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.035248 | 60.278 | 60.2952 | 60.2414 | 60.1491 | 61.295 | 61.3281 | 60.9278 | 61.2574 | 61.3752 | 61.2861 | 61.2276 | 61.2329 | 61.253 | 61.3389 | 61.2181 | 60.3192 | 60.3364 | 60.2826 | 60.1903 | 61.3362 | 61.3693 | 60.9689 | 61.2986 | -1.017 | -0.64974 | -1.0537 | -0.68638
680.0312 | 121.8521 | -61.2213 | 60.4431 | 0.12643 | 0.03274 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.026092 | 60.2734 | 60.2998 | 60.2414 | 60.1491 | 61.2905 | 61.3281 | 60.9278 | 61.2619 | 61.3477 | 61.2541 | 61.1956 | 61.1963 | 61.2118 | 61.3069 | 61.1952 | 60.3146 | 60.341 | 60.2826 | 60.1903 | 61.3317 | 61.3693 | 60.9689 | 61.3031 | -1.017 | -0.65432 | -1.0491 | -0.68638
681.7188 | 121.8155 | -61.3266 | 60.3195 | 0.12643 | 0.037319 | -0.030314 | -0.020438 | -0.000359 | 0.090161 | -0.026092 | 60.2826 | 60.2952 | 60.2414 | 60.1491 | 61.3042 | 61.3373 | 60.9323 | 61.2574 | 61.453 | 61.3639 | 61.2963 | 61.3062 | 61.3262 | 61.4168 | 61.3005 | 60.3238 | 60.3364 | 60.2826 | 60.1903 | 61.3454 | 61.3785 | 60.9735 | 61.2986 | -1.0216 | -0.64974 | -1.0628 | -0.69095
683.4688 | 121.8338 | -61.3129 | 60.3012 | 0.12643 | 0.041898 | -0.030314 | -0.020438 | -0.004937 | 0.090161 | -0.026092 | 60.278 | 60.2952 | 60.2368 | 60.1445 | 61.2996 | 61.3327 | 60.9369 | 61.2574 | 61.4393 | 61.3548 | 61.2826 | 61.2924 | 61.3079 | 61.403 | 61.2868 | 60.3192 | 60.3364 | 60.278 | 60.1857 | 61.3408 | 61.3739 | 60.9781 | 61.2986 | -1.0216 | -0.65889 | -1.0628 | -0.70011
685.2344 | 121.8246 | -61.2488 | 60.4202 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.03067 | 60.278 | 60.2907 | 60.2414 | 60.1537 | 61.2905 | 61.3373 | 60.9323 | 61.2619 | 61.3706 | 61.2815 | 61.2276 | 61.2283 | 61.253 | 61.3298 | 61.2181 | 60.3192 | 60.3319 | 60.2826 | 60.1949 | 61.3317 | 61.3785 | 60.9735 | 61.3031 | -1.0124 | -0.65431 | -1.0491 | -0.69095
686.9844 | 121.9345 | -61.2854 | 60.3058 | 0.11727 | 0.028162 | -0.034893 | -0.020438 | -0.004937 | 0.090161 | -0.021514 | 60.278 | 60.2998 | 60.2322 | 60.1491 | 61.2996 | 61.3327 | 60.9323 | 61.2665 | 61.4027 | 61.3136 | 61.2505 | 61.265 | 61.2805 | 61.3756 | 61.2639 | 60.3192 | 60.341 | 60.2734 | 60.1903 | 61.3408 | 61.3739 | 60.9735 | 61.3077 | -1.0216 | -0.65431 | -1.0674 | -0.70011
688.6719 | 121.8246 | -61.3174 | 60.3241 | 0.12643 | 0.041898 | -0.025735 | -0.01586 | -0.000359 | 0.09474 | -0.03067 | 60.278 | 60.309 | 60.2414 | 60.1491 | 61.2996 | 61.3327 | 60.9369 | 61.2574 | 61.4439 | 61.3593 | 61.2917 | 61.3016 | 61.3171 | 61.4122 | 61.2868 | 60.3192 | 60.3502 | 60.2826 | 60.1903 | 61.3408 | 61.3739 | 60.9781 | 61.2986 | -1.0216 | -0.65889 | -1.0582 | -0.69553
690.4062 | 121.875 | -61.2717 | 60.3287 | 0.12185 | 0.037319 | -0.025735 | -0.020438 | 0.004219 | 0.090161 | -0.035248 | 60.2872 | 60.309 | 60.2414 | 60.1491 | 61.3042 | 61.3373 | 60.9232 | 61.2619 | 61.3935 | 61.309 | 61.2459 | 61.2512 | 61.2759 | 61.3618 | 61.2364 | 60.3284 | 60.3502 | 60.2826 | 60.1903 | 61.3454 | 61.3785 | 60.9644 | 61.3031 | -1.017 | -0.636 | -1.0628 | -0.6818
692.1562 | 121.8567 | -61.3312 | 60.2966 | 0.12185 | 0.028162 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.026092 | 60.2872 | 60.2998 | 60.2322 | 60.1445 | 61.2996 | 61.3281 | 60.9323 | 61.2574 | 61.453 | 61.3593 | 61.3054 | 61.3062 | 61.3217 | 61.4168 | 61.3051 | 60.3284 | 60.341 | 60.2734 | 60.1857 | 61.3408 | 61.3693 | 60.9735 | 61.2986 | -1.0124 | -0.64516 | -1.0674 | -0.70011
693.8438 | 121.7972 | -61.3129 | 60.3195 | 0.12185 | 0.03274 | -0.025735 | -0.01586 | -0.004937 | 0.09474 | -0.026092 | 60.2734 | 60.2907 | 60.2368 | 60.1445 | 61.3042 | 61.3373 | 60.9232 | 61.2574 | 61.4347 | 61.3456 | 61.2871 | 61.297 | 61.3079 | 61.4076 | 61.2868 | 60.3146 | 60.3319 | 60.278 | 60.1857 | 61.3454 | 61.3785 | 60.9644 | 61.2986 | -1.0308 | -0.64974 | -1.0674 | -0.68638
695.5781 | 121.8109 | -61.2213 | 60.4202 | 0.11727 | 0.037319 | -0.025735 | -0.01586 | -0.000359 | 0.090161 | -0.021514 | 60.2826 | 60.2952 | 60.2414 | 60.1537 | 61.2996 | 61.3327 | 60.9323 | 61.2665 | 61.3386 | 61.2586 | 61.1956 | 61.2055 | 61.221 | 61.3115 | 61.1998 | 60.3238 | 60.3364 | 60.2826 | 60.1949 | 61.3408 | 61.3739 | 60.9735 | 61.3077 | -1.017 | -0.64974 | -1.0582 | -0.69095
697.3125 | 121.875 | -61.203 | 60.4202 | 0.12185 | 0.03274 | -0.030314 | -0.025017 | 0.004219 | 0.081005 | -0.03067 | 60.2826 | 60.2952 | 60.2322 | 60.1491 | 61.2996 | 61.3327 | 60.9278 | 61.2619 | 61.3249 | 61.2357 | 61.1727 | 61.178 | 61.2072 | 61.284 | 61.1723 | 60.3238 | 60.3364 | 60.2734 | 60.1903 | 61.3408 | 61.3739 | 60.9689 | 61.3031 | -1.017 | -0.64516 | -1.0674 | -0.69553
699.0781 | 121.9574 | -61.1755 | 60.3973 | 0.12185 | 0.03274 | -0.030314 | -0.020438 | -0.009515 | 0.090161 | -0.035248 | 60.2872 | 60.3044 | 60.2322 | 60.1445 | 61.3042 | 61.3235 | 60.9278 | 61.2574 | 61.2974 | 61.2083 | 61.1452 | 61.1551 | 61.166 | 61.2657 | 61.1403 | 60.3284 | 60.3456 | 60.2734 | 60.1857 | 61.3454 | 61.3647 | 60.9689 | 61.2986 | -1.017 | -0.64058 | -1.072 | -0.69553
700.7656 | 121.8063 | -61.3083 | 60.3287 | 0.13101 | 0.041898 | -0.025735 | -0.020438 | 0.004219 | 0.09474 | -0.035248 | 60.2826 | 60.2952 | 60.2368 | 60.1537 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.4393 | 61.3502 | 61.2826 | 61.2879 | 61.3125 | 61.403 | 61.273 | 60.3238 | 60.3364 | 60.278 | 60.1949 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -1.017 | -0.64058 | -1.0628 | -0.68638
702.5 | 121.9528 | -61.2717 | 60.2966 | 0.12643 | 0.051056 | -0.021157 | -0.020438 | -0.009515 | 0.085583 | -0.035248 | 60.278 | 60.2998 | 60.2368 | 60.1491 | 61.3042 | 61.3373 | 60.9186 | 61.2619 | 61.3981 | 61.3227 | 61.2505 | 61.2512 | 61.2622 | 61.3573 | 61.2364 | 60.3192 | 60.341 | 60.278 | 60.1903 | 61.3454 | 61.3785 | 60.9598 | 61.3031 | -1.0262 | -0.64058 | -1.0674 | -0.6818
704.25 | 121.9666 | -61.2991 | 60.2875 | 0.12185 | 0.046477 | -0.030314 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.278 | 60.2998 | 60.2368 | 60.1537 | 61.295 | 61.3464 | 60.9278 | 61.2574 | 61.421 | 61.3456 | 61.2688 | 61.2787 | 61.2942 | 61.3847 | 61.2639 | 60.3192 | 60.341 | 60.278 | 60.1949 | 61.3362 | 61.3876 | 60.9689 | 61.2986 | -1.017 | -0.64974 | -1.0582 | -0.69095
705.9219 | 121.8933 | -61.1664 | 60.4065 | 0.12643 | 0.041898 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.03067 | 60.2734 | 60.2998 | 60.2276 | 60.1583 | 61.2996 | 61.3327 | 60.9369 | 61.2711 | 61.2928 | 61.2083 | 61.1361 | 61.1414 | 61.166 | 61.252 | 61.1357 | 60.3146 | 60.341 | 60.2688 | 60.1995 | 61.3408 | 61.3739 | 60.9781 | 61.3123 | -1.0262 | -0.66347 | -1.072 | -0.70927
707.6719 | 121.962 | -61.1847 | 60.3882 | 0.12185 | 0.041898 | -0.034893 | -0.020438 | -0.004937 | 0.090161 | -0.035248 | 60.2826 | 60.2998 | 60.2322 | 60.1491 | 61.2996 | 61.3373 | 60.9232 | 61.2665 | 61.3065 | 61.2266 | 61.1498 | 61.1643 | 61.1798 | 61.2749 | 61.1494 | 60.3238 | 60.341 | 60.2734 | 60.1903 | 61.3408 | 61.3785 | 60.9644 | 61.3077 | -1.017 | -0.64058 | -1.0674 | -0.69095
709.4219 | 121.843 | -61.235 | 60.3973 | 0.13101 | 0.051056 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.03067 | 60.278 | 60.3044 | 60.2322 | 60.1537 | 61.295 | 61.3373 | 60.9369 | 61.2619 | 61.3661 | 61.2861 | 61.2093 | 61.2192 | 61.2347 | 61.3206 | 61.2044 | 60.3192 | 60.3456 | 60.2734 | 60.1949 | 61.3362 | 61.3785 | 60.9781 | 61.3031 | -1.017 | -0.65889 | -1.0628 | -0.70469
711.1719 | 121.8796 | -61.2625 | 60.347 | 0.12185 | 0.055634 | -0.021157 | -0.01586 | -0.004937 | 0.090161 | -0.026092 | 60.2734 | 60.2998 | 60.2368 | 60.1491 | 61.295 | 61.3373 | 60.9278 | 61.2574 | 61.3844 | 61.3181 | 61.2414 | 61.2467 | 61.2576 | 61.3527 | 61.2364 | 60.3146 | 60.341 | 60.278 | 60.1903 | 61.3362 | 61.3785 | 60.9689 | 61.2986 | -1.0216 | -0.65432 | -1.0582 | -0.69095
712.8594 | 121.8292 | -61.2396 | 60.4294 | 0.12185 | 0.051056 | -0.025735 | -0.020438 | -0.009515 | 0.085583 | -0.026092 | 60.2826 | 60.2998 | 60.2368 | 60.1537 | 61.2996 | 61.3373 | 60.9415 | 61.2665 | 61.3615 | 61.2907 | 61.2139 | 61.2192 | 61.2301 | 61.3252 | 61.2135 | 60.3238 | 60.341 | 60.278 | 60.1949 | 61.3408 | 61.3785 | 60.9827 | 61.3077 | -1.017 | -0.65889 | -1.0628 | -0.70469
714.6094 | 121.9437 | -61.235 | 60.2966 | 0.12643 | 0.051056 | -0.025735 | -0.025017 | -0.009515 | 0.090161 | -0.026092 | 60.278 | 60.3044 | 60.2368 | 60.1537 | 61.2996 | 61.3373 | 60.9278 | 61.2574 | 61.3615 | 61.2861 | 61.2093 | 61.21 | 61.2255 | 61.3252 | 61.209 | 60.3192 | 60.3456 | 60.278 | 60.1949 | 61.3408 | 61.3785 | 60.9689 | 61.2986 | -1.0216 | -0.64974 | -1.0628 | -0.69095
716.3594 | 121.8246 | -61.2167 | 60.4156 | 0.12185 | 0.041898 | -0.021157 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.2872 | 60.2952 | 60.2322 | 60.1537 | 61.295 | 61.3373 | 60.9278 | 61.2619 | 61.3386 | 61.2586 | 61.1956 | 61.1963 | 61.221 | 61.3069 | 61.1906 | 60.3284 | 60.3364 | 60.2734 | 60.1949 | 61.3362 | 61.3785 | 60.9689 | 61.3031 | -1.0079 | -0.64058 | -1.0628 | -0.69553
718.0938 | 121.8018 | -61.3358 | 60.3012 | 0.13101 | 0.055634 | -0.025735 | -0.020438 | -0.000359 | 0.090161 | -0.026092 | 60.2872 | 60.309 | 60.2368 | 60.1491 | 61.3042 | 61.3281 | 60.9278 | 61.2619 | 61.4668 | 61.3914 | 61.31 | 61.3153 | 61.3354 | 61.4259 | 61.3097 | 60.3284 | 60.3502 | 60.278 | 60.1903 | 61.3454 | 61.3693 | 60.9689 | 61.3031 | -1.017 | -0.64058 | -1.0674 | -0.69095
719.7812 | 121.8521 | -61.2167 | 60.434 | 0.12185 | 0.051056 | -0.025735 | -0.01586 | -0.009515 | 0.085583 | -0.026092 | 60.2826 | 60.2952 | 60.2368 | 60.1537 | 61.295 | 61.3373 | 60.9323 | 61.2619 | 61.3386 | 61.2678 | 61.191 | 61.2009 | 61.2072 | 61.3023 | 61.1906 | 60.3238 | 60.3364 | 60.278 | 60.1949 | 61.3362 | 61.3785 | 60.9735 | 61.3031 | -1.0124 | -0.64974 | -1.0582 | -0.69553
721.5156 | 121.9025 | -61.2488 | 60.3653 | 0.11727 | 0.046477 | -0.021157 | -0.020438 | -0.009515 | 0.076426 | -0.035248 | 60.2734 | 60.2998 | 60.2368 | 60.1537 | 61.295 | 61.3373 | 60.9323 | 61.2528 | 61.3661 | 61.2953 | 61.2276 | 61.2283 | 61.2393 | 61.3252 | 61.2135 | 60.3146 | 60.341 | 60.278 | 60.1949 | 61.3362 | 61.3785 | 60.9735 | 61.294 | -1.0216 | -0.65889 | -1.0582 | -0.69553
723.2656 | 121.8979 | -61.2167 | 60.3607 | 0.11727 | 0.046477 | -0.025735 | -0.025017 | -0.009515 | 0.085583 | -0.035248 | 60.278 | 60.2998 | 60.2368 | 60.1537 | 61.295 | 61.3418 | 60.9323 | 61.2665 | 61.334 | 61.2632 | 61.191 | 61.1917 | 61.2072 | 61.3023 | 61.1815 | 60.3192 | 60.341 | 60.278 | 60.1949 | 61.3362 | 61.383 | 60.9735 | 61.3077 | -1.017 | -0.65431 | -1.0582 | -0.69553
724.9531 | 121.8155 | -61.3449 | 60.3149 | 0.12185 | 0.046477 | -0.025735 | -0.020438 | -0.000359 | 0.090161 | -0.035248 | 60.2872 | 60.309 | 60.2414 | 60.1537 | 61.295 | 61.3373 | 60.9232 | 61.2574 | 61.4668 | 61.3914 | 61.3192 | 61.3245 | 61.3446 | 61.4351 | 61.3097 | 60.3284 | 60.3502 | 60.2826 | 60.1949 | 61.3362 | 61.3785 | 60.9644 | 61.2986 | -1.0079 | -0.636 | -1.0537 | -0.6818
726.7031 | 121.962 | -61.2717 | 60.2737 | 0.12185 | 0.046477 | -0.030314 | -0.025017 | -0.004937 | 0.085583 | -0.03067 | 60.278 | 60.3044 | 60.2322 | 60.1537 | 61.295 | 61.3327 | 60.9186 | 61.2619 | 61.3935 | 61.3181 | 61.2414 | 61.2467 | 61.2667 | 61.3573 | 61.241 | 60.3192 | 60.3456 | 60.2734 | 60.1949 | 61.3362 | 61.3739 | 60.9598 | 61.3031 | -1.017 | -0.64058 | -1.0628 | -0.68637
728.4531 | 121.8338 | -61.3083 | 60.3104 | 0.12185 | 0.055634 | -0.025735 | -0.01586 | -0.004937 | 0.090161 | -0.035248 | 60.2872 | 60.3044 | 60.2322 | 60.1583 | 61.2996 | 61.3327 | 60.9278 | 61.2574 | 61.4301 | 61.3639 | 61.2826 | 61.2924 | 61.3034 | 61.3985 | 61.273 | 60.3284 | 60.3456 | 60.2734 | 60.1995 | 61.3408 | 61.3739 | 60.9689 | 61.2986 | -1.0124 | -0.64058 | -1.0674 | -0.69553
730.1562 | 121.8292 | -61.3174 | 60.3378 | 0.12643 | 0.046477 | -0.030314 | -0.01586 | -0.004937 | 0.090161 | -0.026092 | 60.2826 | 60.2998 | 60.2368 | 60.1491 | 61.2996 | 61.3373 | 60.9278 | 61.2619 | 61.4439 | 61.3639 | 61.2871 | 61.3016 | 61.3125 | 61.4076 | 61.2914 | 60.3238 | 60.341 | 60.278 | 60.1903 | 61.3408 | 61.3785 | 60.9689 | 61.3031 | -1.017 | -0.64516 | -1.0628 | -0.69095
731.8906 | 121.843 | -61.3037 | 60.3058 | 0.12643 | 0.046477 | -0.016578 | -0.025017 | -0.000359 | 0.090161 | -0.03067 | 60.278 | 60.2998 | 60.2414 | 60.1583 | 61.3042 | 61.3327 | 60.9232 | 61.2574 | 61.4301 | 61.3502 | 61.2871 | 61.2787 | 61.3034 | 61.3939 | 61.273 | 60.3192 | 60.341 | 60.2826 | 60.1995 | 61.3454 | 61.3739 | 60.9644 | 61.2986 | -1.0262 | -0.64516 | -1.0628 | -0.6818
733.6406 | 121.9254 | -61.235 | 60.3424 | 0.12185 | 0.041898 | -0.030314 | -0.020438 | 0.004219 | 0.09474 | -0.03067 | 60.2734 | 60.3044 | 60.2368 | 60.1491 | 61.3042 | 61.3464 | 60.9232 | 61.2665 | 61.3569 | 61.2769 | 61.2047 | 61.2146 | 61.2393 | 61.3298 | 61.2044 | 60.3146 | 60.3456 | 60.278 | 60.1903 | 61.3454 | 61.3876 | 60.9644 | 61.3077 | -1.0308 | -0.64974 | -1.0674 | -0.68638
735.3906 | 121.907 | -61.2305 | 60.379 | 0.12185 | 0.041898 | -0.034893 | -0.020438 | -0.009515 | 0.085583 | -0.035248 | 60.2826 | 60.3044 | 60.2322 | 60.1445 | 61.3042 | 61.3373 | 60.9278 | 61.2619 | 61.3523 | 61.2724 | 61.1956 | 61.21 | 61.221 | 61.3161 | 61.1952 | 60.3238 | 60.3456 | 60.2734 | 60.1857 | 61.3454 | 61.3785 | 60.9689 | 61.3031 | -1.0216 | -0.64516 | -1.072 | -0.69553
737.1406 | 121.875 | -61.2762 | 60.347 | 0.12185 | 0.046477 | -0.025735 | -0.01586 | -0.009515 | 0.099318 | -0.026092 | 60.2872 | 60.3044 | 60.2505 | 60.1537 | 61.3042 | 61.3373 | 60.9369 | 61.2574 | 61.3981 | 61.3227 | 61.2505 | 61.2604 | 61.2667 | 61.3756 | 61.2502 | 60.3284 | 60.3456 | 60.2917 | 60.1949 | 61.3454 | 61.3785 | 60.9781 | 61.2986 | -1.017 | -0.64974 | -1.0537 | -0.68638
738.8281 | 121.9345 | -61.2442 | 60.3012 | 0.11727 | 0.046477 | -0.025735 | -0.025017 | -0.000359 | 0.081005 | -0.026092 | 60.2826 | 60.3044 | 60.2414 | 60.1445 | 61.2996 | 61.3373 | 60.9278 | 61.2619 | 61.3615 | 61.2907 | 61.2185 | 61.2192 | 61.2438 | 61.3252 | 61.2181 | 60.3238 | 60.3456 | 60.2826 | 60.1857 | 61.3408 | 61.3785 | 60.9689 | 61.3031 | -1.017 | -0.64516 | -1.0582 | -0.68638
740.5625 | 121.9116 | -61.2305 | 60.3424 | 0.11727 | 0.041898 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.03067 | 60.278 | 60.3044 | 60.2368 | 60.1537 | 61.3042 | 61.3281 | 60.9232 | 61.2619 | 61.3477 | 61.2724 | 61.2047 | 61.2055 | 61.2301 | 61.3161 | 61.1998 | 60.3192 | 60.3456 | 60.278 | 60.1949 | 61.3454 | 61.3693 | 60.9644 | 61.3031 | -1.0262 | -0.64516 | -1.0674 | -0.68638
742.2969 | 121.9299 | -61.29 | 60.2829 | 0.12185 | 0.046477 | -0.030314 | -0.01586 | -0.000359 | 0.085583 | -0.03067 | 60.2872 | 60.3044 | 60.2322 | 60.1491 | 61.2996 | 61.3418 | 60.9323 | 61.2574 | 61.4118 | 61.3365 | 61.2597 | 61.2741 | 61.2896 | 61.3756 | 61.2593 | 60.3284 | 60.3456 | 60.2734 | 60.1903 | 61.3408 | 61.383 | 60.9735 | 61.2986 | -1.0124 | -0.64516 | -1.0674 | -0.70011
743.9844 | 121.8658 | -61.29 | 60.347 | 0.11727 | 0.046477 | -0.021157 | -0.020438 | -0.004937 | 0.085583 | -0.026092 | 60.2872 | 60.3044 | 60.2368 | 60.1537 | 61.295 | 61.3327 | 60.9323 | 61.2619 | 61.4073 | 61.3365 | 61.2688 | 61.2695 | 61.285 | 61.3756 | 61.2639 | 60.3284 | 60.3456 | 60.278 | 60.1949 | 61.3362 | 61.3739 | 60.9735 | 61.3031 | -1.0079 | -0.64516 | -1.0582 | -0.69553
745.7344 | 121.8567 | -61.2167 | 60.4202 | 0.12643 | 0.041898 | -0.030314 | -0.025017 | -0.000359 | 0.090161 | -0.021514 | 60.2872 | 60.2998 | 60.2414 | 60.1445 | 61.2996 | 61.3464 | 60.9278 | 61.2619 | 61.3432 | 61.2586 | 61.1864 | 61.1917 | 61.2164 | 61.3069 | 61.1952 | 60.3284 | 60.341 | 60.2826 | 60.1857 | 61.3408 | 61.3876 | 60.9689 | 61.3031 | -1.0124 | -0.64058 | -1.0582 | -0.68638
747.4844 | 121.8475 | -61.2991 | 60.3333 | 0.12643 | 0.046477 | -0.025735 | -0.020438 | 0.004219 | 0.085583 | -0.026092 | 60.2872 | 60.3044 | 60.2414 | 60.1629 | 61.3042 | 61.3327 | 60.9232 | 61.2665 | 61.4256 | 61.3456 | 61.2734 | 61.2787 | 61.3034 | 61.3847 | 61.273 | 60.3284 | 60.3456 | 60.2826 | 60.2041 | 61.3454 | 61.3739 | 60.9644 | 61.3077 | -1.017 | -0.636 | -1.0628 | -0.6818
749.1719 | 121.8613 | -61.2671 | 60.347 | 0.12643 | 0.046477 | -0.016578 | -0.01586 | -0.000359 | 0.090161 | -0.026092 | 60.2826 | 60.3044 | 60.2505 | 60.1537 | 61.3042 | 61.3327 | 60.9323 | 61.2528 | 61.3935 | 61.3136 | 61.2505 | 61.2512 | 61.2667 | 61.3573 | 61.241 | 60.3238 | 60.3456 | 60.2917 | 60.1949 | 61.3454 | 61.3739 | 60.9735 | 61.294 | -1.0216 | -0.64974 | -1.0537 | -0.6818
750.9219 | 121.8475 | -61.322 | 60.3241 | 0.12643 | 0.046477 | -0.030314 | -0.029595 | 0.004219 | 0.1039 | -0.035248 | 60.2872 | 60.3044 | 60.2414 | 60.1629 | 61.295 | 61.3327 | 60.9369 | 61.2574 | 61.4485 | 61.3685 | 61.2917 | 61.2924 | 61.3262 | 61.4259 | 61.2868 | 60.3284 | 60.3456 | 60.2826 | 60.2041 | 61.3362 | 61.3739 | 60.9781 | 61.2986 | -1.0079 | -0.64974 | -1.0537 | -0.69553
752.6719 | 121.9437 | -61.2762 | 60.2875 | 0.11727 | 0.037319 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.035248 | 60.278 | 60.3044 | 60.2414 | 60.1537 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.3935 | 61.3136 | 61.2505 | 61.2512 | 61.2759 | 61.3618 | 61.241 | 60.3192 | 60.3456 | 60.2826 | 60.1949 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -1.0216 | -0.64516 | -1.0582 | -0.6818
754.3594 | 121.8933 | -61.29 | 60.3516 | 0.11727 | 0.051056 | -0.025735 | -0.01586 | -0.000359 | 0.090161 | -0.026092 | 60.2872 | 60.2952 | 60.2414 | 60.1537 | 61.2996 | 61.3418 | 60.9369 | 61.2619 | 61.4073 | 61.341 | 61.2642 | 61.2741 | 61.2896 | 61.3801 | 61.2639 | 60.3284 | 60.3364 | 60.2826 | 60.1949 | 61.3408 | 61.383 | 60.9781 | 61.3031 | -1.0124 | -0.64974 | -1.0582 | -0.69553
756.0938 | 121.9482 | -61.203 | 60.3882 | 0.12185 | 0.046477 | -0.030314 | -0.020438 | -0.004937 | 0.085583 | -0.03067 | 60.2872 | 60.309 | 60.2414 | 60.1537 | 61.3088 | 61.3327 | 60.9278 | 61.2665 | 61.3249 | 61.2495 | 61.1727 | 61.1826 | 61.1981 | 61.2886 | 61.1723 | 60.3284 | 60.3502 | 60.2826 | 60.1949 | 61.35 | 61.3739 | 60.9689 | 61.3077 | -1.0216 | -0.64058 | -1.0674 | -0.68638
757.8594 | 121.9666 | -61.2808 | 60.2783 | 0.12185 | 0.041898 | -0.025735 | -0.020438 | 0.004219 | 0.085583 | -0.03067 | 60.2826 | 60.3044 | 60.2322 | 60.1537 | 61.3042 | 61.3373 | 60.9094 | 61.2574 | 61.4027 | 61.3227 | 61.2551 | 61.2604 | 61.285 | 61.3664 | 61.2502 | 60.3238 | 60.3456 | 60.2734 | 60.1949 | 61.3454 | 61.3785 | 60.9506 | 61.2986 | -1.0216 | -0.62684 | -1.072 | -0.67722
759.5469 | 121.9574 | -61.2762 | 60.2783 | 0.11269 | 0.051056 | -0.030314 | -0.01586 | -0.004937 | 0.085583 | -0.03067 | 60.2872 | 60.3044 | 60.2368 | 60.1445 | 61.295 | 61.3373 | 60.9323 | 61.2619 | 61.3889 | 61.3273 | 61.2459 | 61.2604 | 61.2713 | 61.3618 | 61.2456 | 60.3284 | 60.3456 | 60.278 | 60.1857 | 61.3362 | 61.3785 | 60.9735 | 61.3031 | -1.0079 | -0.64516 | -1.0582 | -0.69553
761.2812 | 121.9437 | -61.2946 | 60.2875 | 0.12185 | 0.051056 | -0.021157 | -0.020438 | -0.004937 | 0.09474 | -0.035248 | 60.2826 | 60.3044 | 60.2322 | 60.1491 | 61.2996 | 61.3327 | 60.914 | 61.2619 | 61.4164 | 61.3456 | 61.2734 | 61.2741 | 61.2896 | 61.3893 | 61.2593 | 60.3238 | 60.3456 | 60.2734 | 60.1903 | 61.3408 | 61.3739 | 60.9552 | 61.3031 | -1.017 | -0.63142 | -1.0674 | -0.6818
763.0469 | 121.9711 | -61.2122 | 60.3699 | 0.12185 | 0.046477 | -0.030314 | -0.025017 | -0.004937 | 0.081005 | -0.03067 | 60.278 | 60.3044 | 60.2368 | 60.1537 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.334 | 61.2586 | 61.1818 | 61.1871 | 61.2072 | 61.2932 | 61.1815 | 60.3192 | 60.3456 | 60.278 | 60.1949 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -1.0216 | -0.64974 | -1.0628 | -0.69095
764.7344 | 121.9299 | -61.1847 | 60.3882 | 0.12185 | 0.041898 | -0.030314 | -0.020438 | -0.004937 | 0.085583 | -0.035248 | 60.2917 | 60.309 | 60.2322 | 60.1537 | 61.295 | 61.3327 | 60.9323 | 61.2619 | 61.3065 | 61.2266 | 61.1544 | 61.1643 | 61.1798 | 61.2703 | 61.1494 | 60.3329 | 60.3502 | 60.2734 | 60.1949 | 61.3362 | 61.3739 | 60.9735 | 61.3031 | -1.0033 | -0.64058 | -1.0628 | -0.70011
766.4688 | 121.9299 | -61.2076 | 60.3745 | 0.12185 | 0.055634 | -0.039471 | -0.025017 | -0.009515 | 0.090161 | -0.039826 | 60.2872 | 60.3136 | 60.2414 | 60.1537 | 61.3042 | 61.3327 | 60.9232 | 61.2619 | 61.3294 | 61.2632 | 61.1681 | 61.1826 | 61.1981 | 61.2977 | 61.1678 | 60.3284 | 60.3548 | 60.2826 | 60.1949 | 61.3454 | 61.3739 | 60.9644 | 61.3031 | -1.017 | -0.636 | -1.0628 | -0.6818
768.2031 | 121.907 | -61.203 | 60.4111 | 0.12643 | 0.046477 | -0.030314 | -0.020438 | -0.009515 | 0.081005 | -0.03067 | 60.2917 | 60.309 | 60.2414 | 60.1445 | 61.2996 | 61.3327 | 60.9232 | 61.2665 | 61.3294 | 61.2495 | 61.1727 | 61.1826 | 61.1935 | 61.284 | 61.1723 | 60.3329 | 60.3502 | 60.2826 | 60.1857 | 61.3408 | 61.3739 | 60.9644 | 61.3077 | -1.0079 | -0.63142 | -1.0582 | -0.6818
769.9531 | 121.9254 | -61.2488 | 60.3241 | 0.11727 | 0.051056 | -0.030314 | -0.029595 | -0.000359 | 0.085583 | -0.035248 | 60.2826 | 60.3044 | 60.2322 | 60.1491 | 61.3042 | 61.3418 | 60.9278 | 61.2619 | 61.3661 | 61.2998 | 61.2185 | 61.2192 | 61.2484 | 61.3344 | 61.2135 | 60.3238 | 60.3456 | 60.2734 | 60.1903 | 61.3454 | 61.383 | 60.9689 | 61.3031 | -1.0216 | -0.64516 | -1.072 | -0.69553
771.625 | 121.9666 | -61.2625 | 60.3012 | 0.11269 | 0.046477 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.026092 | 60.2917 | 60.3044 | 60.2368 | 60.1583 | 61.2905 | 61.3327 | 60.9278 | 61.2574 | 61.3752 | 61.309 | 61.2322 | 61.2375 | 61.2622 | 61.3481 | 61.2364 | 60.3329 | 60.3456 | 60.278 | 60.1995 | 61.3317 | 61.3739 | 60.9689 | 61.2986 | -0.99871 | -0.636 | -1.0537 | -0.69095
773.375 | 121.9437 | -61.2762 | 60.3012 | 0.12643 | 0.046477 | -0.034893 | -0.020438 | -0.000359 | 0.085583 | -0.03067 | 60.2917 | 60.2998 | 60.2322 | 60.1445 | 61.3042 | 61.3373 | 60.9232 | 61.2711 | 61.4027 | 61.3227 | 61.2414 | 61.2558 | 61.2759 | 61.3618 | 61.2456 | 60.3329 | 60.341 | 60.2734 | 60.1857 | 61.3454 | 61.3785 | 60.9644 | 61.3123 | -1.0124 | -0.63142 | -1.072 | -0.69095
775.125 | 121.8887 | -61.2488 | 60.3516 | 0.12643 | 0.046477 | -0.021157 | -0.011281 | -0.000359 | 0.085583 | -0.03067 | 60.2872 | 60.3044 | 60.2322 | 60.1491 | 61.2996 | 61.3418 | 60.9232 | 61.2619 | 61.3752 | 61.2953 | 61.2276 | 61.2375 | 61.2484 | 61.3344 | 61.2181 | 60.3284 | 60.3456 | 60.2734 | 60.1903 | 61.3408 | 61.383 | 60.9644 | 61.3031 | -1.0124 | -0.636 | -1.0674 | -0.69095
776.8125 | 121.9162 | -61.2305 | 60.3378 | 0.11727 | 0.037319 | -0.034893 | -0.025017 | -0.000359 | 0.09474 | -0.035248 | 60.2917 | 60.3044 | 60.2414 | 60.1537 | 61.3042 | 61.3418 | 60.9323 | 61.2619 | 61.3477 | 61.2678 | 61.1956 | 61.2055 | 61.2301 | 61.3252 | 61.1952 | 60.3329 | 60.3456 | 60.2826 | 60.1949 | 61.3454 | 61.383 | 60.9735 | 61.3031 | -1.0124 | -0.64058 | -1.0628 | -0.69095
778.5625 | 121.9162 | -61.2488 | 60.3699 | 0.12643 | 0.041898 | -0.034893 | -0.025017 | -0.004937 | 0.085583 | -0.035248 | 60.2917 | 60.3044 | 60.2414 | 60.1491 | 61.3088 | 61.3418 | 60.9278 | 61.2619 | 61.3752 | 61.2907 | 61.2139 | 61.2238 | 61.2438 | 61.3344 | 61.2135 | 60.3329 | 60.3456 | 60.2826 | 60.1903 | 61.35 | 61.383 | 60.9689 | 61.3031 | -1.017 | -0.636 | -1.0674 | -0.68638
780.3281 | 121.8475 | -61.2946 | 60.3241 | 0.12643 | 0.046477 | -0.030314 | -0.020438 | -0.000359 | 0.085583 | -0.026092 | 60.2872 | 60.3044 | 60.2414 | 60.1583 | 61.295 | 61.3373 | 60.9232 | 61.2619 | 61.421 | 61.341 | 61.2642 | 61.2741 | 61.2942 | 61.3801 | 61.2685 | 60.3284 | 60.3456 | 60.2826 | 60.1995 | 61.3362 | 61.3785 | 60.9644 | 61.3031 | -1.0079 | -0.636 | -1.0537 | -0.6818
782.0156 | 121.9208 | -61.2442 | 60.3333 | 0.11727 | 0.041898 | -0.030314 | -0.025017 | -0.009515 | 0.090161 | -0.026092 | 60.2963 | 60.3044 | 60.2414 | 60.1583 | 61.2996 | 61.3418 | 60.9278 | 61.2665 | 61.3615 | 61.2861 | 61.2139 | 61.2192 | 61.2347 | 61.3344 | 61.2181 | 60.3375 | 60.3456 | 60.2826 | 60.1995 | 61.3408 | 61.383 | 60.9689 | 61.3077 | -1.0033 | -0.63142 | -1.0582 | -0.68638
783.7656 | 121.9162 | -61.2488 | 60.3607 | 0.11727 | 0.037319 | -0.034893 | -0.029595 | -0.004937 | 0.090161 | -0.035248 | 60.2917 | 60.3136 | 60.2414 | 60.1491 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.3661 | 61.2861 | 61.2139 | 61.2192 | 61.2438 | 61.3389 | 61.2135 | 60.3329 | 60.3548 | 60.2826 | 60.1903 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -1.0079 | -0.636 | -1.0582 | -0.68638
785.5156 | 121.9482 | -61.1664 | 60.3973 | 0.11727 | 0.046477 | -0.030314 | -0.029595 | -0.009515 | 0.085583 | -0.03067 | 60.2826 | 60.3044 | 60.2322 | 60.1491 | 61.2996 | 61.3373 | 60.9323 | 61.2574 | 61.2837 | 61.2129 | 61.1361 | 61.1368 | 61.1569 | 61.252 | 61.1357 | 60.3238 | 60.3456 | 60.2734 | 60.1903 | 61.3408 | 61.3785 | 60.9735 | 61.2986 | -1.017 | -0.64974 | -1.0674 | -0.70011
787.2031 | 121.8246 | -61.2488 | 60.4202 | 0.12643 | 0.051056 | -0.025735 | -0.025017 | 0.004219 | 0.090161 | -0.03067 | 60.2826 | 60.2998 | 60.2414 | 60.1537 | 61.2996 | 61.3373 | 60.9323 | 61.2619 | 61.3752 | 61.2998 | 61.223 | 61.2238 | 61.253 | 61.3389 | 61.2181 | 60.3238 | 60.341 | 60.2826 | 60.1949 | 61.3408 | 61.3785 | 60.9735 | 61.3031 | -1.017 | -0.64974 | -1.0582 | -0.69095
788.9688 | 121.8933 | -61.2534 | 60.347 | 0.11727 | 0.046477 | -0.021157 | -0.025017 | -0.014093 | 0.085583 | -0.03067 | 60.2872 | 60.309 | 60.2368 | 60.1491 | 61.2996 | 61.3418 | 60.9323 | 61.2665 | 61.3706 | 61.2998 | 61.2322 | 61.2283 | 61.2393 | 61.3389 | 61.2227 | 60.3284 | 60.3502 | 60.278 | 60.1903 | 61.3408 | 61.383 | 60.9735 | 61.3077 | -1.0124 | -0.64516 | -1.0628 | -0.69553
790.7188 | 121.8933 | -61.2167 | 60.3561 | 0.11727 | 0.041898 | -0.039471 | -0.025017 | -0.004937 | 0.090161 | -0.03067 | 60.2734 | 60.309 | 60.2414 | 60.1491 | 61.2996 | 61.3418 | 60.9323 | 61.2665 | 61.334 | 61.2586 | 61.1773 | 61.1917 | 61.2118 | 61.3069 | 61.1861 | 60.3146 | 60.3502 | 60.2826 | 60.1903 | 61.3408 | 61.383 | 60.9735 | 61.3077 | -1.0262 | -0.65889 | -1.0582 | -0.69095
792.4062 | 121.9482 | -61.2808 | 60.2783 | 0.12643 | 0.041898 | -0.025735 | -0.020438 | -0.004937 | 0.09474 | -0.035248 | 60.2872 | 60.3044 | 60.2414 | 60.1445 | 61.2996 | 61.3373 | 60.9186 | 61.2574 | 61.4073 | 61.3227 | 61.2551 | 61.2604 | 61.2759 | 61.3756 | 61.2456 | 60.3284 | 60.3456 | 60.2826 | 60.1857 | 61.3408 | 61.3785 | 60.9598 | 61.2986 | -1.0124 | -0.63142 | -1.0582 | -0.67722
794.1562 | 121.8658 | -61.2167 | 60.4111 | 0.12185 | 0.046477 | -0.030314 | -0.025017 | -0.000359 | 0.090161 | -0.026092 | 60.2872 | 60.2998 | 60.2368 | 60.1537 | 61.2996 | 61.3373 | 60.9323 | 61.2574 | 61.3386 | 61.2632 | 61.1864 | 61.1917 | 61.2164 | 61.3069 | 61.1906 | 60.3284 | 60.341 | 60.278 | 60.1949 | 61.3408 | 61.3785 | 60.9735 | 61.2986 | -1.0124 | -0.64516 | -1.0628 | -0.69553
795.9062 | 121.8338 | -61.2259 | 60.4202 | 0.12185 | 0.051056 | -0.025735 | -0.025017 | -0.000359 | 0.081005 | -0.03067 | 60.2826 | 60.309 | 60.2322 | 60.1537 | 61.2996 | 61.3373 | 60.9278 | 61.2619 | 61.3477 | 61.2769 | 61.2002 | 61.2009 | 61.2255 | 61.3069 | 61.1952 | 60.3238 | 60.3502 | 60.2734 | 60.1949 | 61.3408 | 61.3785 | 60.9689 | 61.3031 | -1.017 | -0.64516 | -1.0674 | -0.69553
797.5938 | 121.8979 | -61.3129 | 60.2829 | 0.11727 | 0.051056 | -0.021157 | -0.020438 | 0.004219 | 0.09474 | -0.026092 | 60.2872 | 60.3044 | 60.2322 | 60.1583 | 61.2996 | 61.3373 | 60.9232 | 61.2711 | 61.4301 | 61.3639 | 61.2917 | 61.2924 | 61.3171 | 61.4076 | 61.2868 | 60.3284 | 60.3456 | 60.2734 | 60.1995 | 61.3408 | 61.3785 | 60.9644 | 61.3123 | -1.0124 | -0.636 | -1.0674 | -0.69095
799.3438 | 121.8704 | -61.2167 | 60.4019 | 0.12185 | 0.046477 | -0.030314 | -0.011281 | -0.004937 | 0.09474 | -0.026092 | 60.2826 | 60.3136 | 60.2414 | 60.1537 | 61.2996 | 61.3418 | 60.9369 | 61.2619 | 61.3386 | 61.2632 | 61.1864 | 61.2055 | 61.2118 | 61.3115 | 61.1906 | 60.3238 | 60.3548 | 60.2826 | 60.1949 | 61.3408 | 61.383 | 60.9781 | 61.3031 | -1.017 | -0.65431 | -1.0582 | -0.69553
801.0781 | 121.8613 | -61.2442 | 60.3836 | 0.11727 | 0.046477 | -0.025735 | -0.025017 | -0.004937 | 0.090161 | -0.03067 | 60.2872 | 60.309 | 60.246 | 60.1583 | 61.295 | 61.3373 | 60.9278 | 61.2619 | 61.3615 | 61.2907 | 61.2185 | 61.2192 | 61.2393 | 61.3344 | 61.2135 | 60.3284 | 60.3502 | 60.2872 | 60.1995 | 61.3362 | 61.3785 | 60.9689 | 61.3031 | -1.0079 | -0.64058 | -1.0491 | -0.6818
802.8125 | 121.8155 | -61.3403 | 60.3195 | 0.11727 | 0.046477 | -0.025735 | -0.01586 | 0.004219 | 0.090161 | -0.026092 | 60.2917 | 60.3044 | 60.246 | 60.1491 | 61.3088 | 61.3327 | 60.9278 | 61.2574 | 61.4576 | 61.3868 | 61.3146 | 61.3245 | 61.3446 | 61.4305 | 61.3142 | 60.3329 | 60.3456 | 60.2872 | 60.1903 | 61.35 | 61.3739 | 60.9689 | 61.2986 | -1.017 | -0.636 | -1.0628 | -0.6818
804.5625 | 121.8155 | -61.3129 | 60.3424 | 0.12643 | 0.041898 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.026092 | 60.2917 | 60.3044 | 60.246 | 60.1583 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.4393 | 61.3548 | 61.2917 | 61.297 | 61.3171 | 61.403 | 61.2868 | 60.3329 | 60.3456 | 60.2872 | 60.1995 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -1.0079 | -0.63142 | -1.0537 | -0.67722
806.2344 | 121.962 | -61.2762 | 60.2966 | 0.11727 | 0.041898 | -0.030314 | -0.020438 | -0.000359 | 0.090161 | -0.039826 | 60.2872 | 60.3044 | 60.246 | 60.1445 | 61.2996 | 61.3281 | 60.9278 | 61.2574 | 61.3935 | 61.3181 | 61.2459 | 61.2558 | 61.2759 | 61.3664 | 61.2364 | 60.3284 | 60.3456 | 60.2872 | 60.1857 | 61.3408 | 61.3693 | 60.9689 | 61.2986 | -1.0124 | -0.64058 | -1.0537 | -0.6818
807.9219 | 121.8613 | -61.2762 | 60.3424 | 0.11727 | 0.046477 | -0.025735 | -0.020438 | -0.009515 | 0.090161 | -0.021514 | 60.2826 | 60.2998 | 60.2368 | 60.1537 | 61.3042 | 61.3327 | 60.9278 | 61.2665 | 61.3935 | 61.3227 | 61.2505 | 61.2558 | 61.2667 | 61.3664 | 61.2547 | 60.3238 | 60.341 | 60.278 | 60.1949 | 61.3454 | 61.3739 | 60.9689 | 61.3077 | -1.0216 | -0.64516 | -1.0674 | -0.69095
809.6719 | 121.843 | -61.2488 | 60.434 | 0.11727 | 0.041898 | -0.021157 | -0.025017 | 0.004219 | 0.09474 | -0.03067 | 60.2826 | 60.3044 | 60.246 | 60.1537 | 61.2996 | 61.3327 | 60.9278 | 61.2665 | 61.3661 | 61.2907 | 61.2276 | 61.2238 | 61.253 | 61.3435 | 61.2181 | 60.3238 | 60.3456 | 60.2872 | 60.1949 | 61.3408 | 61.3739 | 60.9689 | 61.3077 | -1.017 | -0.64516 | -1.0537 | -0.6818
811.3438 | 121.8384 | -61.235 | 60.4294 | 0.12643 | 0.041898 | -0.025735 | -0.025017 | -0.000359 | 0.090161 | -0.026092 | 60.2917 | 60.309 | 60.246 | 60.1491 | 61.3042 | 61.3373 | 60.9278 | 61.2574 | 61.3615 | 61.2769 | 61.2093 | 61.21 | 61.2347 | 61.3252 | 61.209 | 60.3329 | 60.3502 | 60.2872 | 60.1903 | 61.3454 | 61.3785 | 60.9689 | 61.2986 | -1.0124 | -0.636 | -1.0582 | -0.6818
813.1094 | 121.9528 | -61.2808 | 60.26 | 0.12643 | 0.041898 | -0.030314 | -0.025017 | -0.000359 | 0.090161 | -0.026092 | 60.2872 | 60.309 | 60.2368 | 60.1583 | 61.3042 | 61.3327 | 60.9278 | 61.2574 | 61.4073 | 61.3227 | 61.2505 | 61.2558 | 61.2805 | 61.371 | 61.2547 | 60.3284 | 60.3502 | 60.278 | 60.1995 | 61.3454 | 61.3739 | 60.9689 | 61.2986 | -1.017 | -0.64058 | -1.0674 | -0.69095
814.7969 | 121.9528 | -61.2625 | 60.2829 | 0.11727 | 0.037319 | -0.025735 | -0.025017 | -0.009515 | 0.090161 | -0.016936 | 60.2872 | 60.3044 | 60.2368 | 60.1491 | 61.2996 | 61.3418 | 60.9232 | 61.2619 | 61.3798 | 61.2998 | 61.2368 | 61.2375 | 61.253 | 61.3527 | 61.2456 | 60.3284 | 60.3456 | 60.278 | 60.1903 | 61.3408 | 61.383 | 60.9644 | 61.3031 | -1.0124 | -0.636 | -1.0628 | -0.68638
816.5312 | 121.9116 | -61.2808 | 60.2966 | 0.11727 | 0.037319 | -0.034893 | -0.020438 | -0.000359 | 0.081005 | -0.026092 | 60.2872 | 60.2998 | 60.2368 | 60.1537 | 61.3088 | 61.3327 | 60.9278 | 61.2619 | 61.3981 | 61.3181 | 61.2459 | 61.2604 | 61.2805 | 61.3618 | 61.2547 | 60.3284 | 60.341 | 60.278 | 60.1949 | 61.35 | 61.3739 | 60.9689 | 61.3031 | -1.0216 | -0.64058 | -1.072 | -0.69095
818.2656 | 121.9574 | -61.2808 | 60.2875 | 0.11727 | 0.037319 | -0.030314 | -0.025017 | 0.004219 | 0.090161 | -0.026092 | 60.2872 | 60.309 | 60.246 | 60.1445 | 61.3088 | 61.3327 | 60.9278 | 61.2665 | 61.3981 | 61.3181 | 61.2505 | 61.2558 | 61.285 | 61.371 | 61.2547 | 60.3284 | 60.3502 | 60.2872 | 60.1857 | 61.35 | 61.3739 | 60.9689 | 61.3077 | -1.0216 | -0.64058 | -1.0628 | -0.6818
820.0156 | 121.8704 | -61.3129 | 60.3104 | 0.12185 | 0.041898 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.026092 | 60.2917 | 60.3044 | 60.2368 | 60.1629 | 61.3042 | 61.3327 | 60.9232 | 61.2619 | 61.4347 | 61.3548 | 61.2826 | 61.2878 | 61.3125 | 61.3984 | 61.2868 | 60.3329 | 60.3456 | 60.278 | 60.2041 | 61.3454 | 61.3739 | 60.9644 | 61.3031 | -1.0124 | -0.63142 | -1.0674 | -0.68638
821.75 | 121.8979 | -61.2991 | 60.2921 | 0.11727 | 0.037319 | -0.025735 | -0.029595 | -0.000359 | 0.081005 | -0.026092 | 60.2872 | 60.3044 | 60.2414 | 60.1537 | 61.2996 | 61.3327 | 60.9186 | 61.2665 | 61.4164 | 61.3365 | 61.2734 | 61.2695 | 61.2988 | 61.3801 | 61.273 | 60.3284 | 60.3456 | 60.2826 | 60.1949 | 61.3408 | 61.3739 | 60.9598 | 61.3077 | -1.0124 | -0.63142 | -1.0582 | -0.67722
823.4844 | 121.9345 | -61.2213 | 60.3745 | 0.11727 | 0.041898 | -0.030314 | -0.020438 | -0.000359 | 0.081005 | -0.035248 | 60.2872 | 60.3044 | 60.2414 | 60.1537 | 61.3042 | 61.3373 | 60.9323 | 61.2665 | 61.3386 | 61.2632 | 61.191 | 61.2009 | 61.221 | 61.3023 | 61.1861 | 60.3284 | 60.3456 | 60.2826 | 60.1949 | 61.3454 | 61.3785 | 60.9735 | 61.3077 | -1.017 | -0.64516 | -1.0628 | -0.69095
825.2344 | 121.8704 | -61.2625 | 60.3928 | 0.13101 | 0.037319 | -0.030314 | -0.020438 | 0.004219 | 0.09474 | -0.026092 | 60.2826 | 60.309 | 60.246 | 60.1537 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.3935 | 61.2998 | 61.2322 | 61.2421 | 61.2667 | 61.3573 | 61.2364 | 60.3238 | 60.3502 | 60.2872 | 60.1949 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -1.017 | -0.64058 | -1.0537 | -0.67722
826.9219 | 121.9116 | -61.2442 | 60.347 | 0.12643 | 0.041898 | -0.030314 | -0.011281 | -0.000359 | 0.085583 | -0.03067 | 60.2917 | 60.3044 | 60.2368 | 60.1537 | 61.3088 | 61.3418 | 60.9232 | 61.2574 | 61.3706 | 61.2861 | 61.2139 | 61.2329 | 61.2438 | 61.3298 | 61.2135 | 60.3329 | 60.3456 | 60.278 | 60.1949 | 61.35 | 61.383 | 60.9644 | 61.2986 | -1.017 | -0.63142 | -1.072 | -0.68638
828.6562 | 121.8979 | -61.2167 | 60.3882 | 0.12185 | 0.041898 | -0.034893 | -0.029595 | 0.004219 | 0.09474 | -0.035248 | 60.2826 | 60.3044 | 60.2322 | 60.1491 | 61.2996 | 61.3327 | 60.9278 | 61.2574 | 61.3386 | 61.2586 | 61.1818 | 61.1871 | 61.221 | 61.3115 | 61.1815 | 60.3238 | 60.3456 | 60.2734 | 60.1903 | 61.3408 | 61.3739 | 60.9689 | 61.2986 | -1.017 | -0.64516 | -1.0674 | -0.69553
830.4062 | 121.9299 | -61.29 | 60.2875 | 0.12643 | 0.041898 | -0.025735 | -0.025017 | 0.004219 | 0.09474 | -0.021514 | 60.2826 | 60.309 | 60.2368 | 60.1537 | 61.3088 | 61.3327 | 60.9186 | 61.2619 | 61.4164 | 61.3319 | 61.2642 | 61.265 | 61.2942 | 61.3847 | 61.2685 | 60.3238 | 60.3502 | 60.278 | 60.1949 | 61.35 | 61.3739 | 60.9598 | 61.3031 | -1.0262 | -0.636 | -1.072 | -0.6818
832.1562 | 121.962 | -61.2946 | 60.2875 | 0.12185 | 0.041898 | -0.025735 | -0.020438 | -0.004937 | 0.09474 | -0.03067 | 60.2917 | 60.309 | 60.2368 | 60.1583 | 61.295 | 61.3327 | 60.9232 | 61.2665 | 61.4164 | 61.3365 | 61.2688 | 61.2741 | 61.2896 | 61.3893 | 61.2639 | 60.3329 | 60.3502 | 60.278 | 60.1995 | 61.3362 | 61.3739 | 60.9644 | 61.3077 | -1.0033 | -0.63142 | -1.0582 | -0.68638
833.8438 | 121.8475 | -61.29 | 60.3333 | 0.12185 | 0.041898 | -0.021157 | -0.011281 | -0.000359 | 0.09474 | -0.026092 | 60.2917 | 60.309 | 60.2368 | 60.1491 | 61.3042 | 61.3327 | 60.9323 | 61.2619 | 61.4118 | 61.3319 | 61.2688 | 61.2787 | 61.2896 | 61.3847 | 61.2639 | 60.3329 | 60.3502 | 60.278 | 60.1903 | 61.3454 | 61.3739 | 60.9735 | 61.3031 | -1.0124 | -0.64058 | -1.0674 | -0.69553
835.5938 | 121.8292 | -61.2167 | 60.4385 | 0.12643 | 0.041898 | -0.030314 | -0.020438 | 0.004219 | 0.090161 | -0.035248 | 60.2826 | 60.3044 | 60.2368 | 60.1583 | 61.3042 | 61.3418 | 60.9415 | 61.2619 | 61.3432 | 61.2586 | 61.1864 | 61.1963 | 61.221 | 61.3069 | 61.1815 | 60.3238 | 60.3456 | 60.278 | 60.1995 | 61.3454 | 61.383 | 60.9827 | 61.3031 | -1.0216 | -0.65889 | -1.0674 | -0.70469
837.3281 | 121.8933 | -61.2625 | 60.3424 | 0.11727 | 0.046477 | -0.021157 | -0.01586 | 0.004219 | 0.1039 | -0.026092 | 60.2872 | 60.3044 | 60.2414 | 60.1629 | 61.2996 | 61.3373 | 60.9186 | 61.2619 | 61.3798 | 61.309 | 61.2414 | 61.2467 | 61.2667 | 61.3664 | 61.2364 | 60.3284 | 60.3456 | 60.2826 | 60.2041 | 61.3408 | 61.3785 | 60.9598 | 61.3031 | -1.0124 | -0.63142 | -1.0582 | -0.67722
839.0781 | 121.907 | -61.2534 | 60.3424 | 0.11269 | 0.041898 | -0.025735 | -0.01586 | -0.004937 | 0.090161 | -0.03067 | 60.2917 | 60.3044 | 60.2414 | 60.1537 | 61.2996 | 61.3373 | 60.9232 | 61.2665 | 61.3661 | 61.2953 | 61.2276 | 61.2375 | 61.2484 | 61.3435 | 61.2227 | 60.3329 | 60.3456 | 60.2826 | 60.1949 | 61.3408 | 61.3785 | 60.9644 | 61.3077 | -1.0079 | -0.63142 | -1.0582 | -0.6818
840.7656 | 121.9116 | -61.2167 | 60.3607 | 0.12643 | 0.03274 | -0.030314 | -0.025017 | 0.004219 | 0.085583 | -0.026092 | 60.2872 | 60.309 | 60.2368 | 60.1537 | 61.3088 | 61.3327 | 60.9323 | 61.2619 | 61.3432 | 61.2495 | 61.1864 | 61.1917 | 61.221 | 61.3023 | 61.1906 | 60.3284 | 60.3502 | 60.278 | 60.1949 | 61.35 | 61.3739 | 60.9735 | 61.3031 | -1.0216 | -0.64516 | -1.072 | -0.69553
842.5156 | 121.9437 | -61.1984 | 60.4065 | 0.12185 | 0.03274 | -0.030314 | -0.029595 | -0.000359 | 0.081005 | -0.035248 | 60.2917 | 60.309 | 60.2368 | 60.1583 | 61.3042 | 61.3418 | 60.9323 | 61.2619 | 61.3203 | 61.2312 | 61.1681 | 61.1688 | 61.1981 | 61.2794 | 61.1632 | 60.3329 | 60.3502 | 60.278 | 60.1995 | 61.3454 | 61.383 | 60.9735 | 61.3031 | -1.0124 | -0.64058 | -1.0674 | -0.69553
844.2656 | 121.8704 | -61.3174 | 60.3287 | 0.13101 | 0.037319 | -0.025735 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.2872 | 60.3044 | 60.246 | 60.1583 | 61.3042 | 61.3327 | 60.9278 | 61.2619 | 61.4485 | 61.3548 | 61.2917 | 61.297 | 61.3217 | 61.4076 | 61.2914 | 60.3284 | 60.3456 | 60.2872 | 60.1995 | 61.3454 | 61.3739 | 60.9689 | 61.3031 | -1.017 | -0.64058 | -1.0582 | -0.6818
845.9531 | 121.9803 | -61.1893 | 60.3745 | 0.11727 | 0.037319 | -0.025735 | -0.020438 | -0.000359 | 0.09474 | -0.03067 | 60.2872 | 60.2952 | 60.2414 | 60.1537 | 61.3088 | 61.3327 | 60.9278 | 61.2665 | 61.3065 | 61.2266 | 61.1635 | 61.1688 | 61.1889 | 61.284 | 61.1586 | 60.3284 | 60.3364 | 60.2826 | 60.1949 | 61.35 | 61.3739 | 60.9689 | 61.3077 | -1.0216 | -0.64058 | -1.0674 | -0.68638
847.7031 | 121.8475 | -61.3037 | 60.3378 | 0.12643 | 0.046477 | -0.021157 | -0.025017 | 0.004219 | 0.090161 | -0.03067 | 60.2917 | 60.309 | 60.2414 | 60.1537 | 61.3042 | 61.3327 | 60.9232 | 61.2619 | 61.4301 | 61.3502 | 61.2826 | 61.2787 | 61.3079 | 61.3939 | 61.273 | 60.3329 | 60.3502 | 60.2826 | 60.1949 | 61.3454 | 61.3739 | 60.9644 | 61.3031 | -1.0124 | -0.63142 | -1.0628 | -0.6818
849.4531 | 121.8338 | -61.3312 | 60.3378 | 0.12185 | 0.037319 | -0.034893 | -0.01586 | -0.004937 | 0.090161 | -0.026092 | 60.2872 | 60.3136 | 60.2414 | 60.1537 | 61.2996 | 61.3327 | 60.9323 | 61.2619 | 61.453 | 61.3685 | 61.2963 | 61.3153 | 61.3262 | 61.4213 | 61.3051 | 60.3284 | 60.3548 | 60.2826 | 60.1949 | 61.3408 | 61.3739 | 60.9735 | 61.3031 | -1.0124 | -0.64516 | -1.0582 | -0.69095
851.2188 | 121.8796 | -61.2534 | 60.3607 | 0.13101 | 0.041898 | -0.021157 | -0.020438 | -0.000359 | 0.09474 | -0.021514 | 60.2872 | 60.2998 | 60.246 | 60.1583 | 61.2996 | 61.3373 | 60.9278 | 61.2711 | 61.3844 | 61.2953 | 61.2322 | 61.2329 | 61.253 | 61.3481 | 61.2318 | 60.3284 | 60.341 | 60.2872 | 60.1995 | 61.3408 | 61.3785 | 60.9689 | 61.3123 | -1.0124 | -0.64058 | -1.0537 | -0.6818
852.9688 | 121.9437 | -61.2488 | 60.2829 | 0.12185 | 0.03274 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.03067 | 60.2917 | 60.3136 | 60.246 | 60.1537 | 61.3088 | 61.3418 | 60.9232 | 61.2574 | 61.3706 | 61.2815 | 61.2185 | 61.2238 | 61.2484 | 61.3344 | 61.2181 | 60.3329 | 60.3548 | 60.2872 | 60.1949 | 61.35 | 61.383 | 60.9644 | 61.2986 | -1.017 | -0.63142 | -1.0628 | -0.67722
854.6406 | 121.8704 | -61.2534 | 60.3699 | 0.12185 | 0.041898 | -0.025735 | -0.020438 | 0.004219 | 0.09474 | -0.026092 | 60.2917 | 60.3136 | 60.246 | 60.1629 | 61.2996 | 61.3418 | 60.9232 | 61.2574 | 61.3752 | 61.2953 | 61.2276 | 61.2329 | 61.2576 | 61.3481 | 61.2273 | 60.3329 | 60.3548 | 60.2872 | 60.2041 | 61.3408 | 61.383 | 60.9644 | 61.2986 | -1.0079 | -0.63142 | -1.0537 | -0.67722
856.3906 | 121.9299 | -61.2076 | 60.4202 | 0.11727 | 0.037319 | -0.030314 | -0.020438 | -0.000359 | 0.085583 | -0.021514 | 60.2963 | 60.3044 | 60.2414 | 60.1537 | 61.3133 | 61.3373 | 60.9323 | 61.2619 | 61.3249 | 61.2449 | 61.1773 | 61.1871 | 61.2072 | 61.2932 | 61.1861 | 60.3375 | 60.3456 | 60.2826 | 60.1949 | 61.3545 | 61.3785 | 60.9735 | 61.3031 | -1.017 | -0.636 | -1.072 | -0.69095
858.1406 | 121.8796 | -61.2671 | 60.3928 | 0.11727 | 0.046477 | -0.025735 | -0.025017 | -0.000359 | 0.09474 | -0.03067 | 60.2963 | 60.309 | 60.246 | 60.1583 | 61.2996 | 61.3327 | 60.9278 | 61.2711 | 61.3844 | 61.3136 | 61.2414 | 61.2421 | 61.2667 | 61.3618 | 61.2364 | 60.3375 | 60.3502 | 60.2872 | 60.1995 | 61.3408 | 61.3739 | 60.9689 | 61.3123 | -1.0033 | -0.63142 | -1.0537 | -0.6818
859.8281 | 121.962 | -61.1984 | 60.3882 | 0.12185 | 0.046477 | -0.025735 | -0.025017 | -0.000359 | 0.090161 | -0.03067 | 60.2917 | 60.3136 | 60.2368 | 60.1491 | 61.3042 | 61.3373 | 60.9186 | 61.2619 | 61.3203 | 61.2449 | 61.1727 | 61.1734 | 61.1981 | 61.2886 | 61.1678 | 60.3329 | 60.3548 | 60.278 | 60.1903 | 61.3454 | 61.3785 | 60.9598 | 61.3031 | -1.0124 | -0.62684 | -1.0674 | -0.6818
861.5781 | 121.8246 | -61.2213 | 60.4202 | 0.12643 | 0.041898 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.03067 | 60.2917 | 60.309 | 60.2368 | 60.1583 | 61.3042 | 61.3418 | 60.9369 | 61.2619 | 61.3477 | 61.2632 | 61.1956 | 61.2055 | 61.2301 | 61.3115 | 61.1906 | 60.3329 | 60.3502 | 60.278 | 60.1995 | 61.3454 | 61.383 | 60.9781 | 61.3031 | -1.0124 | -0.64516 | -1.0674 | -0.70011
863.3125 | 121.9437 | -61.1755 | 60.3745 | 0.11269 | 0.041898 | -0.025735 | -0.025017 | 0.004219 | 0.09474 | -0.026092 | 60.2917 | 60.309 | 60.2414 | 60.1537 | 61.3088 | 61.3418 | 60.9323 | 61.2711 | 61.2882 | 61.2174 | 61.1498 | 61.1505 | 61.1798 | 61.2703 | 61.1494 | 60.3329 | 60.3502 | 60.2826 | 60.1949 | 61.35 | 61.383 | 60.9735 | 61.3123 | -1.017 | -0.64058 | -1.0674 | -0.69095
865.0781 | 121.843 | -61.235 | 60.4019 | 0.11269 | 0.037319 | -0.021157 | -0.020438 | -0.000359 | 0.090161 | -0.03067 | 60.2826 | 60.3136 | 60.246 | 60.1583 | 61.295 | 61.3327 | 60.9369 | 61.2665 | 61.3477 | 61.2724 | 61.2139 | 61.2146 | 61.2347 | 61.3252 | 61.2044 | 60.3238 | 60.3548 | 60.2872 | 60.1995 | 61.3362 | 61.3739 | 60.9781 | 61.3077 | -1.0124 | -0.65431 | -1.0491 | -0.69095
866.75 | 121.9574 | -61.203 | 60.3745 | 0.11727 | 0.037319 | -0.030314 | -0.025017 | 0.004219 | 0.085583 | -0.03067 | 60.2963 | 60.309 | 60.2322 | 60.1491 | 61.3042 | 61.3327 | 60.9278 | 61.2619 | 61.3203 | 61.2403 | 61.1727 | 61.178 | 61.2072 | 61.2886 | 61.1723 | 60.3375 | 60.3502 | 60.2734 | 60.1903 | 61.3454 | 61.3739 | 60.9689 | 61.3031 | -1.0079 | -0.63142 | -1.072 | -0.69553
868.5 | 121.875 | -61.2534 | 60.3745 | 0.12185 | 0.037319 | -0.030314 | -0.01586 | 0.004219 | 0.090161 | -0.016936 | 60.2917 | 60.309 | 60.246 | 60.1537 | 61.3042 | 61.3327 | 60.9278 | 61.2619 | 61.3752 | 61.2907 | 61.223 | 61.2375 | 61.2576 | 61.3435 | 61.2364 | 60.3329 | 60.3502 | 60.2872 | 60.1949 | 61.3454 | 61.3739 | 60.9689 | 61.3031 | -1.0124 | -0.636 | -1.0582 | -0.6818
870.2656 | 121.9574 | -61.1847 | 60.3745 | 0.11727 | 0.037319 | -0.030314 | -0.029595 | -0.000359 | 0.085583 | -0.035248 | 60.2872 | 60.3136 | 60.2368 | 60.1491 | 61.3042 | 61.3418 | 60.9232 | 61.2619 | 61.302 | 61.222 | 61.1544 | 61.1551 | 61.1843 | 61.2703 | 61.1494 | 60.3284 | 60.3548 | 60.278 | 60.1903 | 61.3454 | 61.383 | 60.9644 | 61.3031 | -1.017 | -0.636 | -1.0674 | -0.68638
871.9531 | 121.8887 | -61.2854 | 60.347 | 0.11727 | 0.046477 | -0.025735 | -0.020438 | -0.000359 | 0.090161 | -0.03067 | 60.2872 | 60.309 | 60.246 | 60.1491 | 61.3042 | 61.3373 | 60.9323 | 61.2711 | 61.4027 | 61.3319 | 61.2597 | 61.265 | 61.285 | 61.3756 | 61.2547 | 60.3284 | 60.3502 | 60.2872 | 60.1903 | 61.3454 | 61.3785 | 60.9735 | 61.3123 | -1.017 | -0.64516 | -1.0582 | -0.68637
873.7031 | 121.9711 | -61.2808 | 60.2875 | 0.12185 | 0.041898 | -0.025735 | -0.020438 | -0.000359 | 0.090161 | -0.021514 | 60.2917 | 60.3136 | 60.2414 | 60.1583 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.4027 | 61.3227 | 61.2551 | 61.2604 | 61.2805 | 61.371 | 61.2593 | 60.3329 | 60.3548 | 60.2826 | 60.1995 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -1.0079 | -0.63142 | -1.0582 | -0.6818
875.4531 | 121.8384 | -61.203 | 60.4294 | 0.11269 | 0.03274 | -0.021157 | -0.025017 | 0.004219 | 0.090161 | -0.03067 | 60.2872 | 60.309 | 60.2414 | 60.1583 | 61.3042 | 61.3373 | 60.9369 | 61.2665 | 61.3157 | 61.2357 | 61.1818 | 61.178 | 61.2072 | 61.2932 | 61.1723 | 60.3284 | 60.3502 | 60.2826 | 60.1995 | 61.3454 | 61.3785 | 60.9781 | 61.3077 | -1.017 | -0.64974 | -1.0628 | -0.69553
877.2031 | 121.9803 | -61.1847 | 60.3928 | 0.12185 | 0.037319 | -0.030314 | -0.025017 | -0.000359 | 0.090161 | -0.03067 | 60.2872 | 60.309 | 60.2414 | 60.1537 | 61.3042 | 61.3327 | 60.9323 | 61.2574 | 61.3065 | 61.222 | 61.1544 | 61.1597 | 61.1843 | 61.2749 | 61.154 | 60.3284 | 60.3502 | 60.2826 | 60.1949 | 61.3454 | 61.3739 | 60.9735 | 61.2986 | -1.017 | -0.64516 | -1.0628 | -0.69095
878.9531 | 121.9345 | -61.2488 | 60.347 | 0.11269 | 0.028162 | -0.021157 | -0.020438 | -0.000359 | 0.090161 | -0.035248 | 60.2917 | 60.309 | 60.2414 | 60.1537 | 61.3042 | 61.3373 | 60.9278 | 61.2619 | 61.3615 | 61.2769 | 61.2276 | 61.2283 | 61.2484 | 61.3389 | 61.2135 | 60.3329 | 60.3502 | 60.2826 | 60.1949 | 61.3454 | 61.3785 | 60.9689 | 61.3031 | -1.0124 | -0.636 | -1.0628 | -0.68638
880.6406 | 121.8338 | -61.203 | 60.4248 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.2872 | 60.3181 | 60.246 | 60.1491 | 61.3133 | 61.3373 | 60.9369 | 61.2665 | 61.3249 | 61.2357 | 61.1818 | 61.1826 | 61.2072 | 61.2932 | 61.1769 | 60.3284 | 60.3593 | 60.2872 | 60.1903 | 61.3545 | 61.3785 | 60.9781 | 61.3077 | -1.0262 | -0.64974 | -1.0674 | -0.69095
882.375 | 121.8292 | -61.2625 | 60.4111 | 0.12185 | 0.03274 | -0.016578 | -0.025017 | 0.004219 | 0.085583 | -0.026092 | 60.2963 | 60.309 | 60.2414 | 60.1491 | 61.3042 | 61.3418 | 60.9278 | 61.2619 | 61.3844 | 61.2953 | 61.2459 | 61.2375 | 61.2667 | 61.3481 | 61.2364 | 60.3375 | 60.3502 | 60.2826 | 60.1903 | 61.3454 | 61.383 | 60.9689 | 61.3031 | -1.0079 | -0.63142 | -1.0628 | -0.68638
884.125 | 121.8338 | -61.2396 | 60.4294 | 0.11727 | 0.028162 | -0.030314 | -0.020438 | -0.000359 | 0.090161 | -0.026092 | 60.2872 | 60.3044 | 60.2414 | 60.1583 | 61.3088 | 61.3418 | 60.9278 | 61.2619 | 61.3569 | 61.2678 | 61.2093 | 61.2192 | 61.2393 | 61.3298 | 61.2135 | 60.3284 | 60.3456 | 60.2826 | 60.1995 | 61.35 | 61.383 | 60.9689 | 61.3031 | -1.0216 | -0.64058 | -1.0674 | -0.68638
885.8125 | 121.8842 | -61.2808 | 60.3424 | 0.11727 | 0.03274 | -0.021157 | -0.029595 | 0.004219 | 0.09474 | -0.021514 | 60.2917 | 60.3181 | 60.2414 | 60.1537 | 61.2996 | 61.3418 | 60.9323 | 61.2665 | 61.3981 | 61.3136 | 61.2597 | 61.2512 | 61.285 | 61.3756 | 61.2593 | 60.3329 | 60.3593 | 60.2826 | 60.1949 | 61.3408 | 61.383 | 60.9735 | 61.3077 | -1.0079 | -0.64058 | -1.0582 | -0.69095
887.5469 | 121.8018 | -61.2991 | 60.3607 | 0.12643 | 0.046477 | -0.025735 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.2917 | 60.3044 | 60.2414 | 60.1537 | 61.2905 | 61.3281 | 60.9278 | 61.2574 | 61.4256 | 61.3456 | 61.2734 | 61.2787 | 61.3034 | 61.3893 | 61.273 | 60.3329 | 60.3456 | 60.2826 | 60.1949 | 61.3317 | 61.3693 | 60.9689 | 61.2986 | -0.99871 | -0.636 | -1.0491 | -0.68638
889.2969 | 121.8979 | -61.235 | 60.3699 | 0.11727 | 0.028162 | -0.030314 | -0.020438 | 0.008797 | 0.090161 | -0.03067 | 60.2872 | 60.3136 | 60.2414 | 60.1583 | 61.2996 | 61.3418 | 60.9232 | 61.2665 | 61.3523 | 61.2632 | 61.2047 | 61.2146 | 61.2438 | 61.3252 | 61.2044 | 60.3284 | 60.3548 | 60.2826 | 60.1995 | 61.3408 | 61.383 | 60.9644 | 61.3077 | -1.0124 | -0.636 | -1.0582 | -0.6818
890.9844 | 121.9711 | -61.1938 | 60.3973 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.035248 | 60.2872 | 60.3136 | 60.246 | 60.1583 | 61.3133 | 61.3373 | 60.9369 | 61.2619 | 61.3111 | 61.222 | 61.1727 | 61.1734 | 61.1981 | 61.2749 | 61.1586 | 60.3284 | 60.3548 | 60.2872 | 60.1995 | 61.3545 | 61.3785 | 60.9781 | 61.3031 | -1.0262 | -0.64974 | -1.0674 | -0.69095
892.7188 | 121.9254 | -61.2167 | 60.3745 | 0.12185 | 0.023583 | -0.025735 | -0.029595 | -0.000359 | 0.090161 | -0.021514 | 60.2872 | 60.309 | 60.2414 | 60.1537 | 61.3088 | 61.3373 | 60.9323 | 61.2711 | 61.3386 | 61.2403 | 61.191 | 61.1871 | 61.2164 | 61.3069 | 61.1952 | 60.3284 | 60.3502 | 60.2826 | 60.1949 | 61.35 | 61.3785 | 60.9735 | 61.3123 | -1.0216 | -0.64516 | -1.0674 | -0.69095
894.4688 | 121.8384 | -61.2534 | 60.3973 | 0.12185 | 0.037319 | -0.021157 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.2917 | 60.309 | 60.2368 | 60.1674 | 61.2996 | 61.3418 | 60.9323 | 61.2619 | 61.3752 | 61.2907 | 61.2322 | 61.2329 | 61.2576 | 61.3435 | 61.2273 | 60.3329 | 60.3502 | 60.278 | 60.2086 | 61.3408 | 61.383 | 60.9735 | 61.3031 | -1.0079 | -0.64058 | -1.0628 | -0.69553
896.2344 | 121.8567 | -61.322 | 60.3012 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.008797 | 0.09474 | -0.03067 | 60.2963 | 60.309 | 60.2322 | 60.1537 | 61.2996 | 61.3373 | 60.9278 | 61.2619 | 61.4439 | 61.3548 | 61.3009 | 61.3016 | 61.3308 | 61.4168 | 61.2914 | 60.3375 | 60.3502 | 60.2734 | 60.1949 | 61.3408 | 61.3785 | 60.9689 | 61.3031 | -1.0033 | -0.63142 | -1.0674 | -0.69553
897.9062 | 121.843 | -61.2396 | 60.434 | 0.12185 | 0.028162 | -0.025735 | -0.025017 | 0.013375 | 0.09474 | -0.021514 | 60.2917 | 60.3136 | 60.2505 | 60.1537 | 61.3042 | 61.3373 | 60.9323 | 61.2574 | 61.3615 | 61.2678 | 61.2139 | 61.2146 | 61.253 | 61.3344 | 61.2181 | 60.3329 | 60.3548 | 60.2917 | 60.1949 | 61.3454 | 61.3785 | 60.9735 | 61.2986 | -1.0124 | -0.64058 | -1.0537 | -0.6818
899.6406 | 121.8613 | -61.2442 | 60.4248 | 0.11727 | 0.037319 | -0.030314 | -0.020438 | 0.004219 | 0.090161 | -0.021514 | 60.2917 | 60.3136 | 60.2414 | 60.1537 | 61.3088 | 61.3418 | 60.9369 | 61.2711 | 61.3615 | 61.2815 | 61.2139 | 61.2238 | 61.2484 | 61.3344 | 61.2227 | 60.3329 | 60.3548 | 60.2826 | 60.1949 | 61.35 | 61.383 | 60.9781 | 61.3123 | -1.017 | -0.64516 | -1.0674 | -0.69553
901.3906 | 121.8292 | -61.2442 | 60.4202 | 0.11727 | 0.028162 | -0.025735 | -0.01586 | 0.004219 | 0.090161 | -0.026092 | 60.2963 | 60.309 | 60.2368 | 60.1583 | 61.3042 | 61.3418 | 60.9323 | 61.2619 | 61.3615 | 61.2724 | 61.2185 | 61.2283 | 61.2484 | 61.3344 | 61.2181 | 60.3375 | 60.3502 | 60.278 | 60.1995 | 61.3454 | 61.383 | 60.9735 | 61.3031 | -1.0079 | -0.636 | -1.0674 | -0.69553
903.0781 | 121.9116 | -61.235 | 60.3607 | 0.11727 | 0.028162 | -0.021157 | -0.029595 | -0.000359 | 0.085583 | -0.026092 | 60.2917 | 60.309 | 60.2322 | 60.1537 | 61.3042 | 61.3418 | 60.9278 | 61.2619 | 61.3523 | 61.2632 | 61.2139 | 61.2055 | 61.2347 | 61.3206 | 61.209 | 60.3329 | 60.3502 | 60.2734 | 60.1949 | 61.3454 | 61.383 | 60.9689 | 61.3031 | -1.0124 | -0.636 | -1.072 | -0.69553
904.8281 | 121.8842 | -61.2717 | 60.3287 | 0.11727 | 0.03274 | -0.025735 | -0.025017 | 0.013375 | 0.09474 | -0.026092 | 60.2917 | 60.3044 | 60.246 | 60.1583 | 61.2996 | 61.3327 | 60.9323 | 61.2574 | 61.3889 | 61.3044 | 61.2459 | 61.2467 | 61.285 | 61.3664 | 61.2456 | 60.3329 | 60.3456 | 60.2872 | 60.1995 | 61.3408 | 61.3739 | 60.9735 | 61.2986 | -1.0079 | -0.64058 | -1.0537 | -0.68637
906.5781 | 121.8521 | -61.235 | 60.4248 | 0.12643 | 0.03274 | -0.025735 | -0.029595 | 0.004219 | 0.085583 | -0.03067 | 60.3009 | 60.3044 | 60.2368 | 60.1537 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.3615 | 61.2678 | 61.2093 | 61.2055 | 61.2393 | 61.3206 | 61.2044 | 60.3421 | 60.3456 | 60.278 | 60.1949 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -0.99871 | -0.62684 | -1.0628 | -0.69095
908.3281 | 121.8567 | -61.3312 | 60.3149 | 0.11727 | 0.03274 | -0.021157 | -0.01586 | 0.013375 | 0.090161 | -0.026092 | 60.2963 | 60.3136 | 60.2414 | 60.1583 | 61.3042 | 61.3418 | 60.9323 | 61.2665 | 61.4484 | 61.3639 | 61.31 | 61.3153 | 61.3446 | 61.4213 | 61.3051 | 60.3375 | 60.3548 | 60.2826 | 60.1995 | 61.3454 | 61.383 | 60.9735 | 61.3077 | -1.0079 | -0.636 | -1.0628 | -0.69095
910.0312 | 121.9299 | -61.1938 | 60.3928 | 0.12185 | 0.03274 | -0.025735 | -0.025017 | 0.008797 | 0.085583 | -0.021514 | 60.2872 | 60.3181 | 60.2368 | 60.1583 | 61.3133 | 61.3418 | 60.9369 | 61.2665 | 61.3157 | 61.2266 | 61.1681 | 61.1688 | 61.2026 | 61.2794 | 61.1723 | 60.3284 | 60.3593 | 60.278 | 60.1995 | 61.3545 | 61.383 | 60.9781 | 61.3077 | -1.0262 | -0.64974 | -1.0766 | -0.70011
911.7812 | 121.8567 | -61.2946 | 60.3333 | 0.11727 | 0.037319 | -0.025735 | -0.029595 | 0.008797 | 0.090161 | -0.021514 | 60.2963 | 60.309 | 60.2368 | 60.1583 | 61.3088 | 61.3373 | 60.9278 | 61.2619 | 61.4118 | 61.3319 | 61.2688 | 61.265 | 61.3034 | 61.3847 | 61.273 | 60.3375 | 60.3502 | 60.278 | 60.1995 | 61.35 | 61.3785 | 60.9689 | 61.3031 | -1.0124 | -0.63142 | -1.072 | -0.69095
913.5156 | 121.9116 | -61.2396 | 60.3287 | 0.12185 | 0.03274 | -0.030314 | -0.020438 | -0.000359 | 0.090161 | -0.03067 | 60.2917 | 60.3181 | 60.2414 | 60.1583 | 61.3042 | 61.3373 | 60.9278 | 61.2619 | 61.3615 | 61.2724 | 61.2093 | 61.2192 | 61.2393 | 61.3298 | 61.209 | 60.3329 | 60.3593 | 60.2826 | 60.1995 | 61.3454 | 61.3785 | 60.9689 | 61.3031 | -1.0124 | -0.636 | -1.0628 | -0.68638
915.25 | 121.9849 | -61.1618 | 60.379 | 0.12185 | 0.028162 | -0.021157 | -0.029595 | -0.000359 | 0.081005 | -0.03067 | 60.2917 | 60.3181 | 60.2368 | 60.1537 | 61.3042 | 61.3373 | 60.9323 | 61.2665 | 61.2837 | 61.19 | 61.1406 | 61.1322 | 61.1614 | 61.2428 | 61.1311 | 60.3329 | 60.3593 | 60.278 | 60.1949 | 61.3454 | 61.3785 | 60.9735 | 61.3077 | -1.0124 | -0.64058 | -1.0674 | -0.69553
916.9375 | 121.8384 | -61.2213 | 60.4294 | 0.12185 | 0.037319 | -0.030314 | -0.025017 | 0.008797 | 0.085583 | -0.03067 | 60.3009 | 60.309 | 60.246 | 60.1583 | 61.295 | 61.3327 | 60.9323 | 61.2665 | 61.3432 | 61.2586 | 61.191 | 61.1963 | 61.2301 | 61.3069 | 61.1906 | 60.3421 | 60.3502 | 60.2872 | 60.1995 | 61.3362 | 61.3739 | 60.9735 | 61.3077 | -0.99413 | -0.63142 | -1.0491 | -0.68637
918.625 | 121.9482 | -61.2808 | 60.2829 | 0.11727 | 0.023583 | -0.025735 | -0.025017 | 0.013375 | 0.090161 | -0.035248 | 60.2963 | 60.309 | 60.2368 | 60.1583 | 61.2996 | 61.3373 | 60.9186 | 61.2619 | 61.3981 | 61.3044 | 61.2551 | 61.2558 | 61.2942 | 61.371 | 61.2456 | 60.3375 | 60.3502 | 60.278 | 60.1995 | 61.3408 | 61.3785 | 60.9598 | 61.3031 | -1.0033 | -0.62226 | -1.0628 | -0.6818
920.375 | 121.9666 | -61.2625 | 60.3104 | 0.11727 | 0.03274 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.03067 | 60.3009 | 60.3136 | 60.2414 | 60.1537 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.3798 | 61.2953 | 61.2414 | 61.2421 | 61.2713 | 61.3481 | 61.2318 | 60.3421 | 60.3548 | 60.2826 | 60.1949 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -0.99871 | -0.62684 | -1.0582 | -0.68638
922.125 | 121.8796 | -61.2854 | 60.3836 | 0.12185 | 0.037319 | -0.016578 | -0.020438 | 0.013375 | 0.09474 | -0.026092 | 60.2917 | 60.3136 | 60.246 | 60.1629 | 61.2996 | 61.3373 | 60.9369 | 61.2619 | 61.4073 | 61.3227 | 61.2688 | 61.265 | 61.2988 | 61.3801 | 61.2593 | 60.3329 | 60.3548 | 60.2872 | 60.2041 | 61.3408 | 61.3785 | 60.9781 | 61.3031 | -1.0079 | -0.64516 | -1.0537 | -0.69095
923.7969 | 121.9574 | -61.29 | 60.2921 | 0.12643 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.2963 | 60.309 | 60.2368 | 60.1583 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.4164 | 61.3181 | 61.2734 | 61.2695 | 61.2942 | 61.3801 | 61.2639 | 60.3375 | 60.3502 | 60.278 | 60.1995 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -1.0033 | -0.63142 | -1.0628 | -0.69095
925.5469 | 121.9299 | -61.1755 | 60.4202 | 0.11727 | 0.03274 | -0.025735 | -0.025017 | 0.013375 | 0.085583 | -0.021514 | 60.2872 | 60.3044 | 60.2505 | 60.1583 | 61.2996 | 61.3373 | 60.9278 | 61.2711 | 61.2928 | 61.2083 | 61.1498 | 61.1505 | 61.1889 | 61.2611 | 61.154 | 60.3284 | 60.3456 | 60.2917 | 60.1995 | 61.3408 | 61.3785 | 60.9689 | 61.3123 | -1.0124 | -0.64058 | -1.0491 | -0.67722
927.2969 | 121.9345 | -61.235 | 60.3836 | 0.12185 | 0.028162 | -0.034893 | -0.01586 | 0.004219 | 0.085583 | -0.026092 | 60.2963 | 60.3136 | 60.246 | 60.1491 | 61.3088 | 61.3418 | 60.9323 | 61.2665 | 61.3569 | 61.2632 | 61.2002 | 61.2192 | 61.2393 | 61.3206 | 61.209 | 60.3375 | 60.3548 | 60.2872 | 60.1903 | 61.35 | 61.383 | 60.9735 | 61.3077 | -1.0124 | -0.636 | -1.0628 | -0.68637
928.9844 | 121.8292 | -61.3358 | 60.3104 | 0.11269 | 0.028162 | -0.030314 | -0.011281 | 0.004219 | 0.081005 | -0.026092 | 60.3009 | 60.3136 | 60.2368 | 60.1537 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.4484 | 61.3639 | 61.3054 | 61.3245 | 61.34 | 61.4168 | 61.3097 | 60.3421 | 60.3548 | 60.278 | 60.1949 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -0.99871 | -0.62227 | -1.0628 | -0.68638
930.7344 | 121.9254 | -61.2122 | 60.3607 | 0.11269 | 0.03274 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.035248 | 60.2917 | 60.3136 | 60.2414 | 60.1537 | 61.3088 | 61.3464 | 60.9323 | 61.2665 | 61.3249 | 61.2449 | 61.1864 | 61.1871 | 61.2118 | 61.2977 | 61.1769 | 60.3329 | 60.3548 | 60.2826 | 60.1949 | 61.35 | 61.3876 | 60.9735 | 61.3077 | -1.017 | -0.64058 | -1.0674 | -0.69095
932.4844 | 121.9711 | -61.1938 | 60.4019 | 0.12185 | 0.028162 | -0.025735 | -0.034174 | 0.004219 | 0.09474 | -0.03067 | 60.2917 | 60.309 | 60.2414 | 60.1491 | 61.3088 | 61.3418 | 60.9323 | 61.2619 | 61.3157 | 61.222 | 61.1681 | 61.1597 | 61.1981 | 61.2886 | 61.1632 | 60.3329 | 60.3502 | 60.2826 | 60.1903 | 61.35 | 61.383 | 60.9735 | 61.3031 | -1.017 | -0.64058 | -1.0674 | -0.69095
934.1719 | 121.8155 | -61.3495 | 60.3195 | 0.12643 | 0.03274 | -0.025735 | -0.025017 | 0.013375 | 0.090161 | -0.026092 | 60.2963 | 60.3044 | 60.2368 | 60.1491 | 61.2996 | 61.3373 | 60.9232 | 61.2619 | 61.4759 | 61.3822 | 61.3238 | 61.3245 | 61.3629 | 61.4396 | 61.3234 | 60.3375 | 60.3456 | 60.278 | 60.1903 | 61.3408 | 61.3785 | 60.9644 | 61.3031 | -1.0033 | -0.62684 | -1.0628 | -0.68638
935.875 | 121.8292 | -61.3083 | 60.3149 | 0.12185 | 0.037319 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.2963 | 60.3136 | 60.2368 | 60.1491 | 61.3042 | 61.3327 | 60.9323 | 61.2665 | 61.4301 | 61.3456 | 61.2826 | 61.2879 | 61.3171 | 61.3985 | 61.2868 | 60.3375 | 60.3548 | 60.278 | 60.1903 | 61.3454 | 61.3739 | 60.9735 | 61.3077 | -1.0079 | -0.636 | -1.0674 | -0.69553
937.6094 | 121.8658 | -61.2854 | 60.3424 | 0.11727 | 0.037319 | -0.021157 | -0.020438 | 0.004219 | 0.09474 | -0.021514 | 60.2917 | 60.3181 | 60.2414 | 60.1537 | 61.3042 | 61.3327 | 60.9323 | 61.2665 | 61.4027 | 61.3227 | 61.2642 | 61.265 | 61.2896 | 61.3801 | 61.2639 | 60.3329 | 60.3593 | 60.2826 | 60.1949 | 61.3454 | 61.3739 | 60.9735 | 61.3077 | -1.0124 | -0.64058 | -1.0628 | -0.69095
939.3438 | 121.8521 | -61.2946 | 60.3378 | 0.12185 | 0.041898 | -0.030314 | -0.020438 | 0.017953 | 0.09474 | -0.016936 | 60.2872 | 60.3136 | 60.246 | 60.1674 | 61.2996 | 61.3418 | 60.9323 | 61.2619 | 61.4164 | 61.3365 | 61.2642 | 61.2741 | 61.3125 | 61.3893 | 61.2776 | 60.3284 | 60.3548 | 60.2872 | 60.2086 | 61.3408 | 61.383 | 60.9735 | 61.3031 | -1.0124 | -0.64516 | -1.0537 | -0.68637
941.1094 | 121.9299 | -61.2808 | 60.3424 | 0.11727 | 0.037319 | -0.030314 | -0.025017 | 0.004219 | 0.090161 | -0.026092 | 60.2963 | 60.309 | 60.2414 | 60.1583 | 61.3042 | 61.3418 | 60.9278 | 61.2711 | 61.3981 | 61.3181 | 61.2505 | 61.2558 | 61.285 | 61.371 | 61.2547 | 60.3375 | 60.3502 | 60.2826 | 60.1995 | 61.3454 | 61.383 | 60.9689 | 61.3123 | -1.0079 | -0.63142 | -1.0628 | -0.68638
942.7969 | 121.9666 | -61.2122 | 60.3653 | 0.11727 | 0.023583 | -0.030314 | -0.020438 | 0.013375 | 0.090161 | -0.03067 | 60.2917 | 60.3136 | 60.2322 | 60.1629 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.3294 | 61.2357 | 61.1818 | 61.1917 | 61.2255 | 61.3023 | 61.1815 | 60.3329 | 60.3548 | 60.2734 | 60.2041 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -1.0079 | -0.636 | -1.0674 | -0.69553
944.5312 | 121.9711 | -61.1938 | 60.4156 | 0.12185 | 0.028162 | -0.030314 | -0.029595 | -0.000359 | 0.090161 | -0.03067 | 60.2917 | 60.3181 | 60.2414 | 60.1537 | 61.3042 | 61.3373 | 60.9323 | 61.2574 | 61.3157 | 61.222 | 61.1635 | 61.1643 | 61.1935 | 61.284 | 61.1632 | 60.3329 | 60.3593 | 60.2826 | 60.1949 | 61.3454 | 61.3785 | 60.9735 | 61.2986 | -1.0124 | -0.64058 | -1.0628 | -0.69095
946.2344 | 121.9345 | -61.1984 | 60.4065 | 0.11269 | 0.028162 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.026092 | 60.3055 | 60.3136 | 60.2368 | 60.1583 | 61.3042 | 61.3464 | 60.9323 | 61.2619 | 61.3111 | 61.2266 | 61.1727 | 61.1826 | 61.1981 | 61.284 | 61.1723 | 60.3467 | 60.3548 | 60.278 | 60.1995 | 61.3454 | 61.3876 | 60.9735 | 61.3031 | -0.99871 | -0.62684 | -1.0674 | -0.69553
947.9688 | 121.8567 | -61.2305 | 60.4156 | 0.12185 | 0.03274 | -0.021157 | -0.029595 | 0.008797 | 0.09474 | -0.026092 | 60.3009 | 60.309 | 60.2414 | 60.1583 | 61.3088 | 61.3373 | 60.9415 | 61.2665 | 61.3523 | 61.2632 | 61.2093 | 61.2009 | 61.2393 | 61.3252 | 61.2044 | 60.3421 | 60.3502 | 60.2826 | 60.1995 | 61.35 | 61.3785 | 60.9827 | 61.3077 | -1.0079 | -0.64058 | -1.0674 | -0.70011
949.7188 | 121.8796 | -61.2717 | 60.3516 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.090161 | -0.021514 | 60.3009 | 60.3136 | 60.2414 | 60.1629 | 61.3042 | 61.3327 | 60.9323 | 61.2665 | 61.3935 | 61.2998 | 61.2551 | 61.2512 | 61.2759 | 61.3618 | 61.2502 | 60.3421 | 60.3548 | 60.2826 | 60.2041 | 61.3454 | 61.3739 | 60.9735 | 61.3077 | -1.0033 | -0.63142 | -1.0628 | -0.69095
951.4062 | 121.8979 | -61.1938 | 60.4202 | 0.12185 | 0.028162 | -0.030314 | -0.020438 | -0.000359 | 0.090161 | -0.021514 | 60.2963 | 60.3181 | 60.2414 | 60.1537 | 61.3133 | 61.3373 | 60.9415 | 61.2665 | 61.3157 | 61.222 | 61.1635 | 61.1734 | 61.1935 | 61.284 | 61.1723 | 60.3375 | 60.3593 | 60.2826 | 60.1949 | 61.3545 | 61.3785 | 60.9827 | 61.3077 | -1.017 | -0.64516 | -1.072 | -0.70011
953.1562 | 121.8887 | -61.3083 | 60.2966 | 0.11727 | 0.023583 | -0.016578 | -0.025017 | 0.013375 | 0.1039 | -0.026092 | 60.2963 | 60.309 | 60.2414 | 60.1537 | 61.3133 | 61.3373 | 60.9278 | 61.2665 | 61.4256 | 61.3319 | 61.2917 | 61.2833 | 61.3217 | 61.4122 | 61.2822 | 60.3375 | 60.3502 | 60.2826 | 60.1949 | 61.3545 | 61.3785 | 60.9689 | 61.3077 | -1.017 | -0.63142 | -1.072 | -0.68638
954.8438 | 121.8658 | -61.2305 | 60.4111 | 0.11727 | 0.037319 | -0.025735 | -0.025017 | 0.008797 | 0.085583 | -0.026092 | 60.2963 | 60.3136 | 60.2414 | 60.1629 | 61.3042 | 61.3418 | 60.9278 | 61.2711 | 61.3477 | 61.2678 | 61.2047 | 61.2055 | 61.2393 | 61.3161 | 61.2044 | 60.3375 | 60.3548 | 60.2826 | 60.2041 | 61.3454 | 61.383 | 60.9689 | 61.3123 | -1.0079 | -0.63142 | -1.0628 | -0.68638
956.5938 | 121.9482 | -61.1893 | 60.4202 | 0.12185 | 0.028162 | -0.025735 | -0.025017 | -0.004937 | 0.085583 | -0.026092 | 60.2917 | 60.3136 | 60.2414 | 60.1537 | 61.3042 | 61.3418 | 60.9369 | 61.2665 | 61.3111 | 61.2174 | 61.1635 | 61.1643 | 61.1843 | 61.2749 | 61.1632 | 60.3329 | 60.3548 | 60.2826 | 60.1949 | 61.3454 | 61.383 | 60.9781 | 61.3077 | -1.0124 | -0.64516 | -1.0628 | -0.69553
958.2812 | 121.8567 | -61.322 | 60.3424 | 0.12185 | 0.03274 | -0.030314 | -0.01586 | 0.008797 | 0.090161 | -0.016936 | 60.2963 | 60.3136 | 60.2414 | 60.1583 | 61.3088 | 61.3327 | 60.9278 | 61.2574 | 61.4439 | 61.3548 | 61.2917 | 61.3062 | 61.3308 | 61.4122 | 61.3051 | 60.3375 | 60.3548 | 60.2826 | 60.1995 | 61.35 | 61.3739 | 60.9689 | 61.2986 | -1.0124 | -0.63142 | -1.0674 | -0.68638
960.0312 | 121.9666 | -61.1893 | 60.379 | 0.12185 | 0.028162 | -0.025735 | -0.029595 | 0.004219 | 0.090161 | -0.021514 | 60.3009 | 60.3227 | 60.246 | 60.1537 | 61.3042 | 61.3327 | 60.9323 | 61.2619 | 61.3111 | 61.2174 | 61.1635 | 61.1597 | 61.1935 | 61.2794 | 61.1678 | 60.3421 | 60.3639 | 60.2872 | 60.1949 | 61.3454 | 61.3739 | 60.9735 | 61.3031 | -1.0033 | -0.63142 | -1.0582 | -0.68637
961.7344 | 121.8521 | -61.3083 | 60.3424 | 0.12643 | 0.03274 | -0.021157 | -0.025017 | 0.013375 | 0.09474 | -0.016936 | 60.2917 | 60.3136 | 60.246 | 60.1629 | 61.3042 | 61.3418 | 60.9369 | 61.2711 | 61.4347 | 61.341 | 61.2871 | 61.2833 | 61.3217 | 61.403 | 61.2914 | 60.3329 | 60.3548 | 60.2872 | 60.2041 | 61.3454 | 61.383 | 60.9781 | 61.3123 | -1.0124 | -0.64516 | -1.0582 | -0.69095
963.4688 | 121.8613 | -61.3037 | 60.3516 | 0.12643 | 0.028162 | -0.016578 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.3009 | 60.3227 | 60.2414 | 60.1583 | 61.2996 | 61.3327 | 60.9323 | 61.2665 | 61.4301 | 61.3319 | 61.2871 | 61.2833 | 61.3125 | 61.3939 | 61.2822 | 60.3421 | 60.3639 | 60.2826 | 60.1995 | 61.3408 | 61.3739 | 60.9735 | 61.3077 | -0.99871 | -0.63142 | -1.0582 | -0.69095
965.2188 | 121.8521 | -61.2305 | 60.4477 | 0.12185 | 0.028162 | -0.025735 | -0.01586 | 0.013375 | 0.090161 | -0.03067 | 60.2917 | 60.309 | 60.246 | 60.1583 | 61.2996 | 61.3327 | 60.9415 | 61.2574 | 61.3523 | 61.2586 | 61.2047 | 61.2146 | 61.2438 | 61.3206 | 61.1998 | 60.3329 | 60.3502 | 60.2872 | 60.1995 | 61.3408 | 61.3739 | 60.9827 | 61.2986 | -1.0079 | -0.64974 | -1.0537 | -0.69553
966.9062 | 121.907 | -61.2259 | 60.3699 | 0.12185 | 0.019004 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.03067 | 60.2963 | 60.309 | 60.2414 | 60.1537 | 61.3042 | 61.3418 | 60.9232 | 61.2665 | 61.3477 | 61.2449 | 61.2002 | 61.2055 | 61.2255 | 61.3115 | 61.1952 | 60.3375 | 60.3502 | 60.2826 | 60.1949 | 61.3454 | 61.383 | 60.9644 | 61.3077 | -1.0079 | -0.62684 | -1.0628 | -0.6818
968.6562 | 121.9666 | -61.1938 | 60.4019 | 0.12185 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.09474 | -0.03067 | 60.3055 | 60.3181 | 60.2505 | 60.1537 | 61.3042 | 61.3327 | 60.9323 | 61.2711 | 61.3157 | 61.2174 | 61.1681 | 61.1734 | 61.2026 | 61.2886 | 61.1632 | 60.3467 | 60.3593 | 60.2917 | 60.1949 | 61.3454 | 61.3739 | 60.9735 | 61.3123 | -0.99871 | -0.62684 | -1.0537 | -0.6818
970.3438 | 121.8887 | -61.3037 | 60.2692 | 0.12643 | 0.023583 | -0.030314 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.3009 | 60.309 | 60.246 | 60.1629 | 61.3088 | 61.3418 | 60.9278 | 61.2619 | 61.4301 | 61.3273 | 61.2734 | 61.2833 | 61.3125 | 61.3939 | 61.2822 | 60.3421 | 60.3502 | 60.2872 | 60.2041 | 61.35 | 61.383 | 60.9689 | 61.3031 | -1.0079 | -0.62684 | -1.0628 | -0.6818
972.0781 | 121.9116 | -61.2396 | 60.3699 | 0.11727 | 0.023583 | -0.030314 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.3009 | 60.3136 | 60.2414 | 60.1537 | 61.3088 | 61.3373 | 60.9232 | 61.2711 | 61.3569 | 61.2632 | 61.2093 | 61.2192 | 61.2438 | 61.3298 | 61.2135 | 60.3421 | 60.3548 | 60.2826 | 60.1949 | 61.35 | 61.3785 | 60.9644 | 61.3123 | -1.0079 | -0.62227 | -1.0674 | -0.6818
973.8125 | 121.9803 | -61.2076 | 60.3836 | 0.11269 | 0.019004 | -0.025735 | -0.025017 | 0.008797 | 0.081005 | -0.035248 | 60.3009 | 60.3136 | 60.2368 | 60.1583 | 61.3088 | 61.3373 | 60.9369 | 61.2711 | 61.3203 | 61.2266 | 61.1818 | 61.1826 | 61.2164 | 61.2886 | 61.1723 | 60.3421 | 60.3548 | 60.278 | 60.1995 | 61.35 | 61.3785 | 60.9781 | 61.3123 | -1.0079 | -0.636 | -1.072 | -0.70011
975.5625 | 121.8521 | -61.2442 | 60.4111 | 0.12185 | 0.028162 | -0.021157 | -0.025017 | 0.008797 | 0.090161 | -0.03067 | 60.3009 | 60.3136 | 60.246 | 60.1629 | 61.3088 | 61.3327 | 60.9369 | 61.2619 | 61.3661 | 61.2724 | 61.223 | 61.2192 | 61.253 | 61.3344 | 61.2135 | 60.3421 | 60.3548 | 60.2872 | 60.2041 | 61.35 | 61.3739 | 60.9781 | 61.3031 | -1.0079 | -0.636 | -1.0628 | -0.69095
977.25 | 121.875 | -61.2076 | 60.4156 | 0.12185 | 0.019004 | -0.030314 | -0.029595 | 0.004219 | 0.085583 | -0.026092 | 60.2963 | 60.3181 | 60.2414 | 60.1537 | 61.3088 | 61.3418 | 60.9323 | 61.2619 | 61.3294 | 61.2266 | 61.1773 | 61.178 | 61.2118 | 61.2932 | 61.1815 | 60.3375 | 60.3593 | 60.2826 | 60.1949 | 61.35 | 61.383 | 60.9735 | 61.3031 | -1.0124 | -0.636 | -1.0674 | -0.69095
979 | 121.8246 | -61.3129 | 60.3424 | 0.12185 | 0.023583 | -0.025735 | -0.025017 | 0.004219 | 0.090161 | -0.021514 | 60.3101 | 60.3136 | 60.2505 | 60.1674 | 61.3042 | 61.3418 | 60.9323 | 61.2711 | 61.4347 | 61.3364 | 61.2871 | 61.2878 | 61.3171 | 61.403 | 61.2914 | 60.3513 | 60.3548 | 60.2917 | 60.2086 | 61.3454 | 61.383 | 60.9735 | 61.3123 | -0.99413 | -0.62226 | -1.0537 | -0.6818
980.75 | 121.9711 | -61.2808 | 60.2737 | 0.11727 | 0.028162 | -0.030314 | -0.029595 | 0.008797 | 0.090161 | -0.026092 | 60.3055 | 60.3136 | 60.2505 | 60.1674 | 61.3042 | 61.3464 | 60.9278 | 61.2619 | 61.3981 | 61.309 | 61.2505 | 61.2512 | 61.2896 | 61.371 | 61.2547 | 60.3467 | 60.3548 | 60.2917 | 60.2086 | 61.3454 | 61.3876 | 60.9689 | 61.3031 | -0.99871 | -0.62227 | -1.0537 | -0.67722
982.4375 | 121.9391 | -61.2946 | 60.2966 | 0.11727 | 0.028162 | -0.034893 | -0.025017 | 0.008797 | 0.090161 | -0.016936 | 60.3009 | 60.3136 | 60.246 | 60.1629 | 61.3042 | 61.3373 | 60.9232 | 61.2665 | 61.4118 | 61.3227 | 61.2597 | 61.2695 | 61.3034 | 61.3847 | 61.2776 | 60.3421 | 60.3548 | 60.2872 | 60.2041 | 61.3454 | 61.3785 | 60.9644 | 61.3077 | -1.0033 | -0.62227 | -1.0582 | -0.67722
984.1875 | 121.9482 | -61.2671 | 60.2875 | 0.12185 | 0.028162 | -0.025735 | -0.020438 | 0.008797 | 0.09474 | -0.026092 | 60.3055 | 60.3136 | 60.246 | 60.1537 | 61.3042 | 61.3373 | 60.9278 | 61.2665 | 61.3889 | 61.2953 | 61.2414 | 61.2467 | 61.2759 | 61.3618 | 61.241 | 60.3467 | 60.3548 | 60.2872 | 60.1949 | 61.3454 | 61.3785 | 60.9689 | 61.3077 | -0.99871 | -0.62227 | -1.0582 | -0.6818
985.9375 | 121.8384 | -61.3312 | 60.3149 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | 0.013375 | 0.099318 | -0.026092 | 60.3055 | 60.3181 | 60.2505 | 60.1537 | 61.3088 | 61.3373 | 60.9278 | 61.2711 | 61.453 | 61.3639 | 61.31 | 61.3062 | 61.3446 | 61.4305 | 61.3051 | 60.3467 | 60.3593 | 60.2917 | 60.1949 | 61.35 | 61.3785 | 60.9689 | 61.3123 | -1.0033 | -0.62227 | -1.0582 | -0.67722
987.625 | 121.8384 | -61.2259 | 60.4065 | 0.12643 | 0.037319 | -0.016578 | -0.020438 | 0.004219 | 0.085583 | -0.016936 | 60.3009 | 60.3227 | 60.2505 | 60.1629 | 61.3088 | 61.3373 | 60.9369 | 61.2757 | 61.3523 | 61.2632 | 61.2093 | 61.2055 | 61.2301 | 61.3115 | 61.209 | 60.3421 | 60.3639 | 60.2917 | 60.2041 | 61.35 | 61.3785 | 60.9781 | 61.3169 | -1.0079 | -0.636 | -1.0582 | -0.68638
989.375 | 121.8567 | -61.235 | 60.4385 | 0.11727 | 0.028162 | -0.030314 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 60.3009 | 60.3181 | 60.2505 | 60.1629 | 61.3088 | 61.3373 | 60.9323 | 61.2574 | 61.3523 | 61.2632 | 61.2047 | 61.2146 | 61.2438 | 61.3206 | 61.2135 | 60.3421 | 60.3593 | 60.2917 | 60.2041 | 61.35 | 61.3785 | 60.9735 | 61.2986 | -1.0079 | -0.63142 | -1.0582 | -0.6818
991.125 | 121.8292 | -61.235 | 60.434 | 0.11727 | 0.03274 | -0.025735 | -0.029595 | 0.008797 | 0.09474 | -0.026092 | 60.3055 | 60.3136 | 60.2414 | 60.1629 | 61.3042 | 61.3373 | 60.9369 | 61.2619 | 61.3523 | 61.2678 | 61.2093 | 61.2055 | 61.2438 | 61.3298 | 61.209 | 60.3467 | 60.3548 | 60.2826 | 60.2041 | 61.3454 | 61.3785 | 60.9781 | 61.3031 | -0.99871 | -0.63142 | -1.0628 | -0.69553
992.875 | 121.8521 | -61.3495 | 60.3104 | 0.11727 | 0.03274 | -0.025735 | -0.020438 | 0.004219 | 0.09474 | -0.026092 | 60.3009 | 60.3136 | 60.2414 | 60.1583 | 61.2996 | 61.3373 | 60.9278 | 61.2574 | 61.4668 | 61.3822 | 61.3238 | 61.329 | 61.3537 | 61.4442 | 61.3234 | 60.3421 | 60.3548 | 60.2826 | 60.1995 | 61.3408 | 61.3785 | 60.9689 | 61.2986 | -0.99871 | -0.62684 | -1.0582 | -0.68638
994.625 | 121.8613 | -61.2762 | 60.4248 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.017953 | 0.090161 | -0.026092 | 60.3055 | 60.3136 | 60.2505 | 60.1583 | 61.3042 | 61.3418 | 60.9323 | 61.2619 | 61.3935 | 61.3044 | 61.2551 | 61.2558 | 61.2942 | 61.3664 | 61.2502 | 60.3467 | 60.3548 | 60.2917 | 60.1995 | 61.3454 | 61.383 | 60.9735 | 61.3031 | -0.99871 | -0.62684 | -1.0537 | -0.6818
996.3125 | 121.8521 | -61.322 | 60.3378 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.09474 | -0.021514 | 60.3009 | 60.3136 | 60.246 | 60.1629 | 61.3042 | 61.3373 | 60.9278 | 61.2665 | 61.4393 | 61.3502 | 61.3009 | 61.3016 | 61.3262 | 61.4168 | 61.3005 | 60.3421 | 60.3548 | 60.2872 | 60.2041 | 61.3454 | 61.3785 | 60.9689 | 61.3077 | -1.0033 | -0.62684 | -1.0582 | -0.6818
998.0625 | 121.9574 | -61.2259 | 60.3928 | 0.12185 | 0.019004 | -0.034893 | -0.025017 | -0.000359 | 0.085583 | -0.021514 | 60.2963 | 60.3136 | 60.2368 | 60.1537 | 61.3088 | 61.3327 | 60.9278 | 61.2619 | 61.3477 | 61.2449 | 61.191 | 61.2009 | 61.2255 | 61.3115 | 61.2044 | 60.3375 | 60.3548 | 60.278 | 60.1949 | 61.35 | 61.3739 | 60.9689 | 61.3031 | -1.0124 | -0.63142 | -1.072 | -0.69095
999.8125 | 121.8842 | -61.2946 | 60.3516 | 0.12185 | 0.028162 | -0.025735 | -0.01586 | 0.004219 | 0.099318 | -0.03067 | 60.3055 | 60.3227 | 60.2414 | 60.1629 | 61.2996 | 61.3418 | 60.9278 | 61.2665 | 61.4164 | 61.3227 | 61.2688 | 61.2787 | 61.2988 | 61.3939 | 61.2639 | 60.3467 | 60.3639 | 60.2826 | 60.2041 | 61.3408 | 61.383 | 60.9689 | 61.3077 | -0.99413 | -0.62227 | -1.0582 | -0.68638
1001.5625 | 121.9345 | -61.2396 | 60.3882 | 0.11727 | 0.03274 | -0.025735 | -0.025017 | 0.004219 | 0.085583 | -0.035248 | 60.3055 | 60.3181 | 60.2414 | 60.1583 | 61.3042 | 61.3418 | 60.9278 | 61.2711 | 61.3569 | 61.2724 | 61.2139 | 61.2146 | 61.2438 | 61.3252 | 61.2044 | 60.3467 | 60.3593 | 60.2826 | 60.1995 | 61.3454 | 61.383 | 60.9689 | 61.3123 | -0.99871 | -0.62227 | -1.0628 | -0.68638
1003.25 | 121.9574 | -61.2579 | 60.2966 | 0.11727 | 0.023583 | -0.030314 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.3101 | 60.3136 | 60.246 | 60.1629 | 61.3088 | 61.3327 | 60.9186 | 61.2619 | 61.3752 | 61.2815 | 61.2276 | 61.2375 | 61.2667 | 61.3481 | 61.2364 | 60.3513 | 60.3548 | 60.2872 | 60.2041 | 61.35 | 61.3739 | 60.9598 | 61.3031 | -0.99871 | -0.60853 | -1.0628 | -0.67264
1005 | 121.9803 | -61.1801 | 60.4111 | 0.11727 | 0.023583 | -0.034893 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.2963 | 60.3136 | 60.2414 | 60.1629 | 61.3042 | 61.3327 | 60.9415 | 61.2574 | 61.2974 | 61.2037 | 61.1452 | 61.1551 | 61.1889 | 61.2703 | 61.154 | 60.3375 | 60.3548 | 60.2826 | 60.2041 | 61.3454 | 61.3739 | 60.9827 | 61.2986 | -1.0079 | -0.64516 | -1.0628 | -0.70011
1006.7344 | 121.8658 | -61.203 | 60.4294 | 0.11269 | 0.023583 | -0.030314 | -0.025017 | 0.004219 | 0.085583 | -0.026092 | 60.2963 | 60.3273 | 60.2368 | 60.1674 | 61.3042 | 61.3373 | 60.9369 | 61.2619 | 61.3157 | 61.2266 | 61.1727 | 61.178 | 61.2072 | 61.2886 | 61.1769 | 60.3375 | 60.3685 | 60.278 | 60.2086 | 61.3454 | 61.3785 | 60.9781 | 61.3031 | -1.0079 | -0.64058 | -1.0674 | -0.70011
1008.4844 | 121.9162 | -61.2122 | 60.4294 | 0.11727 | 0.023583 | -0.030314 | -0.025017 | 0.013375 | 0.09474 | -0.026092 | 60.3055 | 60.3227 | 60.2414 | 60.1674 | 61.3088 | 61.3327 | 60.9369 | 61.2665 | 61.3294 | 61.2357 | 61.1818 | 61.1871 | 61.2255 | 61.3069 | 61.1861 | 60.3467 | 60.3639 | 60.2826 | 60.2086 | 61.35 | 61.3739 | 60.9781 | 61.3077 | -1.0033 | -0.63142 | -1.0674 | -0.69553
1010.1562 | 121.9803 | -61.2717 | 60.2921 | 0.12185 | 0.028162 | -0.030314 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.3055 | 60.3136 | 60.246 | 60.1629 | 61.3042 | 61.3464 | 60.9232 | 61.2711 | 61.3935 | 61.2998 | 61.2414 | 61.2512 | 61.2759 | 61.3618 | 61.2456 | 60.3467 | 60.3548 | 60.2872 | 60.2041 | 61.3454 | 61.3876 | 60.9644 | 61.3123 | -0.99871 | -0.61769 | -1.0582 | -0.67722
1011.9062 | 121.9299 | -61.2442 | 60.3607 | 0.12185 | 0.023583 | -0.021157 | -0.029595 | 0.004219 | 0.090161 | -0.021514 | 60.3101 | 60.3181 | 60.2505 | 60.1629 | 61.3088 | 61.3327 | 60.9369 | 61.2711 | 61.3661 | 61.2678 | 61.223 | 61.2146 | 61.2484 | 61.3344 | 61.2227 | 60.3513 | 60.3593 | 60.2917 | 60.2041 | 61.35 | 61.3739 | 60.9781 | 61.3123 | -0.99871 | -0.62684 | -1.0582 | -0.68638
1013.5781 | 121.9482 | -61.2122 | 60.4156 | 0.11727 | 0.023583 | -0.025735 | -0.020438 | -0.000359 | 0.085583 | -0.026092 | 60.3009 | 60.3044 | 60.2414 | 60.1629 | 61.3133 | 61.3418 | 60.9278 | 61.2665 | 61.3294 | 61.2357 | 61.1864 | 61.1917 | 61.2118 | 61.2977 | 61.1861 | 60.3421 | 60.3456 | 60.2826 | 60.2041 | 61.3545 | 61.383 | 60.9689 | 61.3077 | -1.0124 | -0.62684 | -1.072 | -0.68638
1015.3125 | 122.0032 | -61.1938 | 60.4111 | 0.11727 | 0.028162 | -0.030314 | -0.029595 | 0.013375 | 0.09474 | -0.026092 | 60.3009 | 60.309 | 60.246 | 60.1629 | 61.3042 | 61.3418 | 60.9323 | 61.2665 | 61.3111 | 61.222 | 61.1635 | 61.1643 | 61.2072 | 61.2886 | 61.1678 | 60.3421 | 60.3502 | 60.2872 | 60.2041 | 61.3454 | 61.383 | 60.9735 | 61.3077 | -1.0033 | -0.63142 | -1.0582 | -0.68637
1017.0625 | 121.9482 | -61.2762 | 60.3104 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.03067 | 60.3009 | 60.3136 | 60.2505 | 60.1629 | 61.2996 | 61.3418 | 60.9323 | 61.2711 | 61.3981 | 61.2952 | 61.2551 | 61.2558 | 61.285 | 61.3618 | 61.2456 | 60.3421 | 60.3548 | 60.2917 | 60.2041 | 61.3408 | 61.383 | 60.9735 | 61.3123 | -0.99871 | -0.63142 | -1.0491 | -0.6818
1018.7344 | 121.8338 | -61.3449 | 60.3424 | 0.11727 | 0.03274 | -0.025735 | -0.020438 | 0.008797 | 0.09474 | -0.021514 | 60.3009 | 60.3181 | 60.2505 | 60.1583 | 61.3042 | 61.3327 | 60.9232 | 61.2619 | 61.4622 | 61.3776 | 61.3192 | 61.3245 | 61.3537 | 61.4397 | 61.3234 | 60.3421 | 60.3593 | 60.2917 | 60.1995 | 61.3454 | 61.3739 | 60.9644 | 61.3031 | -1.0033 | -0.62227 | -1.0537 | -0.67264
1020.4844 | 121.9116 | -61.235 | 60.3745 | 0.12185 | 0.037319 | -0.034893 | -0.029595 | 0.013375 | 0.090161 | -0.021514 | 60.3055 | 60.3227 | 60.2414 | 60.1629 | 61.3088 | 61.3373 | 60.9278 | 61.2665 | 61.3569 | 61.2724 | 61.2002 | 61.2055 | 61.2484 | 61.3252 | 61.2135 | 60.3467 | 60.3639 | 60.2826 | 60.2041 | 61.35 | 61.3785 | 60.9689 | 61.3077 | -1.0033 | -0.62227 | -1.0674 | -0.68638
1022.25 | 121.8887 | -61.3266 | 60.3104 | 0.11269 | 0.028162 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.3009 | 60.3227 | 60.2414 | 60.1629 | 61.2996 | 61.3418 | 60.9278 | 61.2665 | 61.4393 | 61.3548 | 61.3009 | 61.3062 | 61.3354 | 61.4168 | 61.3051 | 60.3421 | 60.3639 | 60.2826 | 60.2041 | 61.3408 | 61.383 | 60.9689 | 61.3077 | -0.99871 | -0.62684 | -1.0582 | -0.68638
1023.9375 | 121.8842 | -61.2762 | 60.3516 | 0.12185 | 0.028162 | -0.021157 | -0.029595 | 0.017953 | 0.090161 | -0.026092 | 60.3101 | 60.3136 | 60.246 | 60.1629 | 61.3088 | 61.3373 | 60.9369 | 61.2619 | 61.3981 | 61.3044 | 61.2551 | 61.2467 | 61.2942 | 61.3664 | 61.2502 | 60.3513 | 60.3548 | 60.2872 | 60.2041 | 61.35 | 61.3785 | 60.9781 | 61.3031 | -0.99871 | -0.62684 | -1.0628 | -0.69095
1025.6719 | 121.8613 | -61.322 | 60.3195 | 0.11727 | 0.028162 | -0.030314 | -0.011281 | 0.008797 | 0.090161 | -0.021514 | 60.3101 | 60.309 | 60.2505 | 60.1629 | 61.3042 | 61.3418 | 60.9278 | 61.2619 | 61.4393 | 61.3502 | 61.2917 | 61.3107 | 61.3308 | 61.4122 | 61.3005 | 60.3513 | 60.3502 | 60.2917 | 60.2041 | 61.3454 | 61.383 | 60.9689 | 61.3031 | -0.99413 | -0.61769 | -1.0537 | -0.67722
1027.4219 | 121.8292 | -61.2213 | 60.4385 | 0.12643 | 0.03274 | -0.025735 | -0.020438 | 0.004219 | 0.090161 | -0.03067 | 60.3009 | 60.3181 | 60.246 | 60.1629 | 61.3088 | 61.3327 | 60.9369 | 61.2665 | 61.3477 | 61.2541 | 61.1956 | 61.2009 | 61.2255 | 61.3115 | 61.1906 | 60.3421 | 60.3593 | 60.2872 | 60.2041 | 61.35 | 61.3739 | 60.9781 | 61.3077 | -1.0079 | -0.636 | -1.0628 | -0.69095
1029.1875 | 121.8796 | -61.2717 | 60.3516 | 0.11269 | 0.03274 | -0.021157 | -0.01586 | 0.004219 | 0.09474 | -0.021514 | 60.3055 | 60.3181 | 60.246 | 60.172 | 61.3042 | 61.3373 | 60.9278 | 61.2665 | 61.3844 | 61.3044 | 61.2505 | 61.2558 | 61.2759 | 61.3664 | 61.2502 | 60.3467 | 60.3593 | 60.2872 | 60.2132 | 61.3454 | 61.3785 | 60.9689 | 61.3077 | -0.99871 | -0.62227 | -1.0582 | -0.6818
1030.875 | 121.8658 | -61.29 | 60.3653 | 0.11727 | 0.037319 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.03067 | 60.3009 | 60.3227 | 60.2505 | 60.1629 | 61.2996 | 61.3327 | 60.9323 | 61.2665 | 61.4073 | 61.3273 | 61.2688 | 61.2604 | 61.2988 | 61.3756 | 61.2593 | 60.3421 | 60.3639 | 60.2917 | 60.2041 | 61.3408 | 61.3739 | 60.9735 | 61.3077 | -0.99871 | -0.63142 | -1.0491 | -0.6818
1032.6406 | 121.8842 | -61.2534 | 60.3745 | 0.11727 | 0.023583 | -0.030314 | -0.025017 | 0.013375 | 0.09474 | -0.021514 | 60.3009 | 60.3181 | 60.2414 | 60.172 | 61.3042 | 61.3327 | 60.9278 | 61.2665 | 61.3706 | 61.2769 | 61.223 | 61.2283 | 61.2667 | 61.3481 | 61.2318 | 60.3421 | 60.3593 | 60.2826 | 60.2132 | 61.3454 | 61.3739 | 60.9689 | 61.3077 | -1.0033 | -0.62684 | -1.0628 | -0.68638
1034.3281 | 121.907 | -61.2396 | 60.3424 | 0.11727 | 0.03274 | -0.025735 | -0.034174 | -0.000359 | 0.085583 | -0.026092 | 60.3055 | 60.3227 | 60.2505 | 60.1629 | 61.3088 | 61.3373 | 60.9323 | 61.2619 | 61.3569 | 61.2724 | 61.2139 | 61.2054 | 61.2393 | 61.3252 | 61.2135 | 60.3467 | 60.3639 | 60.2917 | 60.2041 | 61.35 | 61.3785 | 60.9735 | 61.3031 | -1.0033 | -0.62684 | -1.0582 | -0.6818
1036.0625 | 121.8384 | -61.2579 | 60.4156 | 0.12185 | 0.037319 | -0.030314 | -0.029595 | 0.008797 | 0.099318 | -0.026092 | 60.3009 | 60.3136 | 60.2414 | 60.1629 | 61.3088 | 61.3327 | 60.9323 | 61.2619 | 61.3798 | 61.2953 | 61.2276 | 61.2283 | 61.2667 | 61.3573 | 61.2318 | 60.3421 | 60.3548 | 60.2826 | 60.2041 | 61.35 | 61.3739 | 60.9735 | 61.3031 | -1.0079 | -0.63142 | -1.0674 | -0.69095
1037.75 | 121.8796 | -61.2854 | 60.3745 | 0.11727 | 0.03274 | -0.016578 | -0.020438 | 0.004219 | 0.090161 | -0.016936 | 60.3009 | 60.3136 | 60.246 | 60.1674 | 61.3088 | 61.3327 | 60.9369 | 61.2619 | 61.4027 | 61.3181 | 61.2688 | 61.265 | 61.2896 | 61.3756 | 61.2685 | 60.3421 | 60.3548 | 60.2872 | 60.2086 | 61.35 | 61.3739 | 60.9781 | 61.3031 | -1.0079 | -0.636 | -1.0628 | -0.69095
1039.4844 | 121.8338 | -61.3037 | 60.3104 | 0.12185 | 0.028162 | -0.012 | -0.020438 | 0.008797 | 0.09474 | -0.016936 | 60.3009 | 60.3227 | 60.246 | 60.1629 | 61.2996 | 61.3281 | 60.9278 | 61.2619 | 61.4256 | 61.3319 | 61.2917 | 61.2833 | 61.3125 | 61.3985 | 61.2868 | 60.3421 | 60.3639 | 60.2872 | 60.2041 | 61.3408 | 61.3693 | 60.9689 | 61.3031 | -0.99871 | -0.62684 | -1.0537 | -0.6818
1041.2344 | 121.9482 | -61.2717 | 60.3012 | 0.12185 | 0.028162 | -0.030314 | -0.020438 | 0.008797 | 0.090161 | -0.026092 | 60.2963 | 60.3181 | 60.2505 | 60.1629 | 61.2996 | 61.3418 | 60.9278 | 61.2711 | 61.3935 | 61.2998 | 61.2414 | 61.2512 | 61.2805 | 61.3618 | 61.2456 | 60.3375 | 60.3593 | 60.2917 | 60.2041 | 61.3408 | 61.383 | 60.9689 | 61.3123 | -1.0033 | -0.63142 | -1.0491 | -0.67722
1042.9844 | 121.9574 | -61.1893 | 60.3973 | 0.11727 | 0.023583 | -0.025735 | -0.025017 | 0.008797 | 0.085583 | -0.026092 | 60.3009 | 60.3273 | 60.2414 | 60.172 | 61.3088 | 61.3464 | 60.9369 | 61.2574 | 61.3065 | 61.2129 | 61.1635 | 61.1643 | 61.1981 | 61.2749 | 61.1632 | 60.3421 | 60.3685 | 60.2826 | 60.2132 | 61.35 | 61.3876 | 60.9781 | 61.2986 | -1.0079 | -0.636 | -1.0674 | -0.69553
1044.6719 | 121.9574 | -61.2442 | 60.3195 | 0.12185 | 0.03274 | -0.025735 | -0.020438 | 0.004219 | 0.085583 | -0.026092 | 60.3055 | 60.3181 | 60.246 | 60.1674 | 61.3042 | 61.3418 | 60.9278 | 61.2711 | 61.3661 | 61.2769 | 61.2185 | 61.2238 | 61.2484 | 61.3298 | 61.2181 | 60.3467 | 60.3593 | 60.2872 | 60.2086 | 61.3454 | 61.383 | 60.9689 | 61.3123 | -0.99871 | -0.62227 | -1.0582 | -0.6818
1046.4062 | 121.9528 | -61.2534 | 60.3104 | 0.11727 | 0.028162 | -0.030314 | -0.029595 | 0.004219 | 0.09474 | -0.021514 | 60.3055 | 60.3227 | 60.2414 | 60.1674 | 61.3088 | 61.3418 | 60.9323 | 61.2665 | 61.3706 | 61.2815 | 61.223 | 61.2238 | 61.2576 | 61.3481 | 61.2318 | 60.3467 | 60.3639 | 60.2826 | 60.2086 | 61.35 | 61.383 | 60.9735 | 61.3077 | -1.0033 | -0.62684 | -1.0674 | -0.69095
1048.1562 | 121.9757 | -61.2122 | 60.3745 | 0.12185 | 0.028162 | -0.025735 | -0.029595 | 0.004219 | 0.085583 | -0.035248 | 60.3009 | 60.3181 | 60.246 | 60.172 | 61.3042 | 61.3418 | 60.9369 | 61.2665 | 61.334 | 61.2403 | 61.1864 | 61.1826 | 61.2164 | 61.2977 | 61.1769 | 60.3421 | 60.3593 | 60.2872 | 60.2132 | 61.3454 | 61.383 | 60.9781 | 61.3077 | -1.0033 | -0.636 | -1.0582 | -0.69095
1049.8281 | 121.843 | -61.322 | 60.347 | 0.11727 | 0.037319 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 60.3009 | 60.3181 | 60.246 | 60.1629 | 61.3088 | 61.3418 | 60.9186 | 61.2619 | 61.4393 | 61.3593 | 61.3054 | 61.3016 | 61.3308 | 61.4076 | 61.3005 | 60.3421 | 60.3593 | 60.2872 | 60.2041 | 61.35 | 61.383 | 60.9598 | 61.3031 | -1.0079 | -0.61769 | -1.0628 | -0.67264
1051.5781 | 121.8567 | -61.3266 | 60.3424 | 0.11727 | 0.03274 | -0.021157 | -0.025017 | 0.013375 | 0.09474 | -0.026092 | 60.3055 | 60.3181 | 60.2505 | 60.1629 | 61.295 | 61.3373 | 60.9186 | 61.2574 | 61.4439 | 61.3593 | 61.3054 | 61.3016 | 61.34 | 61.4213 | 61.3005 | 60.3467 | 60.3593 | 60.2917 | 60.2041 | 61.3362 | 61.3785 | 60.9598 | 61.2986 | -0.98955 | -0.61311 | -1.0445 | -0.66806
1053.3281 | 121.8933 | -61.2534 | 60.3561 | 0.12185 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.026092 | 60.3055 | 60.3273 | 60.246 | 60.1629 | 61.2996 | 61.3373 | 60.9278 | 61.2711 | 61.3752 | 61.2815 | 61.2322 | 61.2421 | 61.2622 | 61.3435 | 61.2273 | 60.3467 | 60.3685 | 60.2872 | 60.2041 | 61.3408 | 61.3785 | 60.9689 | 61.3123 | -0.99413 | -0.62227 | -1.0537 | -0.6818
1055.0625 | 121.8384 | -61.2991 | 60.3424 | 0.11727 | 0.028162 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.3101 | 60.3227 | 60.2505 | 60.1629 | 61.3088 | 61.3327 | 60.9278 | 61.2665 | 61.4164 | 61.3273 | 61.2734 | 61.2787 | 61.3079 | 61.3893 | 61.2776 | 60.3513 | 60.3639 | 60.2917 | 60.2041 | 61.35 | 61.3739 | 60.9689 | 61.3077 | -0.99871 | -0.61769 | -1.0582 | -0.67722
1056.75 | 121.8933 | -61.29 | 60.3882 | 0.12185 | 0.03274 | -0.025735 | -0.025017 | 0.013375 | 0.090161 | -0.03067 | 60.3101 | 60.3227 | 60.2414 | 60.1674 | 61.3042 | 61.3418 | 60.9323 | 61.2665 | 61.4118 | 61.3227 | 61.2642 | 61.265 | 61.3034 | 61.3801 | 61.2593 | 60.3513 | 60.3639 | 60.2826 | 60.2086 | 61.3454 | 61.383 | 60.9735 | 61.3077 | -0.99413 | -0.62226 | -1.0628 | -0.69095
1058.4844 | 121.9803 | -61.2946 | 60.2692 | 0.11727 | 0.03274 | -0.021157 | -0.029595 | 0.008797 | 0.090161 | -0.016936 | 60.3055 | 60.3227 | 60.2505 | 60.1674 | 61.2996 | 61.351 | 60.9232 | 61.2665 | 61.4118 | 61.3273 | 61.2734 | 61.265 | 61.3034 | 61.3847 | 61.2776 | 60.3467 | 60.3639 | 60.2917 | 60.2086 | 61.3408 | 61.3922 | 60.9644 | 61.3077 | -0.99413 | -0.61769 | -1.0491 | -0.67264
1060.2344 | 121.8338 | -61.2534 | 60.4294 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | 0.013375 | 0.090161 | -0.016936 | 60.3055 | 60.3227 | 60.2551 | 60.1674 | 61.3088 | 61.3418 | 60.9369 | 61.2711 | 61.3798 | 61.2815 | 61.2322 | 61.2329 | 61.2667 | 61.3435 | 61.2364 | 60.3467 | 60.3639 | 60.2963 | 60.2086 | 61.35 | 61.383 | 60.9781 | 61.3123 | -1.0033 | -0.63142 | -1.0537 | -0.6818
1061.9844 | 121.8384 | -61.3083 | 60.347 | 0.11727 | 0.028162 | -0.030314 | -0.025017 | 0.017953 | 0.09474 | -0.026092 | 60.3101 | 60.3227 | 60.2505 | 60.1674 | 61.3042 | 61.3327 | 60.9232 | 61.2619 | 61.4256 | 61.3365 | 61.278 | 61.2833 | 61.3262 | 61.403 | 61.2822 | 60.3513 | 60.3639 | 60.2917 | 60.2086 | 61.3454 | 61.3739 | 60.9644 | 61.3031 | -0.99413 | -0.61311 | -1.0537 | -0.67264
1063.7344 | 121.9757 | -61.1755 | 60.3882 | 0.11727 | 0.023583 | -0.030314 | -0.01586 | 0.008797 | 0.090161 | -0.021514 | 60.3009 | 60.3319 | 60.246 | 60.1629 | 61.2996 | 61.3327 | 60.9369 | 61.2619 | 61.2928 | 61.1991 | 61.1452 | 61.1597 | 61.1843 | 61.2657 | 61.154 | 60.3421 | 60.3731 | 60.2872 | 60.2041 | 61.3408 | 61.3739 | 60.9781 | 61.3031 | -0.99871 | -0.636 | -1.0537 | -0.69095
1065.4219 | 121.8933 | -61.2396 | 60.3882 | 0.12185 | 0.037319 | -0.025735 | -0.020438 | 0.013375 | 0.09474 | -0.021514 | 60.3101 | 60.3227 | 60.2505 | 60.1629 | 61.3042 | 61.3281 | 60.9323 | 61.2619 | 61.3615 | 61.2769 | 61.2139 | 61.2192 | 61.253 | 61.3344 | 61.2181 | 60.3513 | 60.3639 | 60.2917 | 60.2041 | 61.3454 | 61.3693 | 60.9735 | 61.3031 | -0.99413 | -0.62226 | -1.0537 | -0.6818
1067.1719 | 121.9757 | -61.1938 | 60.3928 | 0.11727 | 0.03274 | -0.025735 | -0.029595 | 0.004219 | 0.090161 | -0.026092 | 60.3009 | 60.3273 | 60.2505 | 60.1629 | 61.3088 | 61.3327 | 60.9232 | 61.2665 | 61.3111 | 61.2266 | 61.1681 | 61.1643 | 61.1981 | 61.284 | 61.1678 | 60.3421 | 60.3685 | 60.2917 | 60.2041 | 61.35 | 61.3739 | 60.9644 | 61.3077 | -1.0079 | -0.62227 | -1.0582 | -0.67264
1068.8594 | 121.843 | -61.2167 | 60.434 | 0.12185 | 0.028162 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.026092 | 60.3101 | 60.3227 | 60.2505 | 60.1674 | 61.3042 | 61.3373 | 60.9461 | 61.2711 | 61.3386 | 61.2449 | 61.191 | 61.1963 | 61.2255 | 61.3069 | 61.1906 | 60.3513 | 60.3639 | 60.2917 | 60.2086 | 61.3454 | 61.3785 | 60.9873 | 61.3123 | -0.99413 | -0.636 | -1.0537 | -0.69553
1070.6094 | 121.9299 | -61.2579 | 60.3058 | 0.12185 | 0.03274 | -0.034893 | -0.020438 | 0.008797 | 0.090161 | -0.026092 | 60.3055 | 60.3181 | 60.2505 | 60.1629 | 61.3042 | 61.3327 | 60.9232 | 61.2665 | 61.3798 | 61.2907 | 61.223 | 61.2375 | 61.2667 | 61.3481 | 61.2318 | 60.3467 | 60.3593 | 60.2917 | 60.2041 | 61.3454 | 61.3739 | 60.9644 | 61.3077 | -0.99871 | -0.61769 | -1.0537 | -0.67264
1072.3594 | 121.9803 | -61.1755 | 60.4248 | 0.11269 | 0.028162 | -0.030314 | -0.025017 | 0.004219 | 0.090161 | -0.03067 | 60.3101 | 60.3227 | 60.2505 | 60.1629 | 61.3042 | 61.3373 | 60.9369 | 61.2665 | 61.2882 | 61.2037 | 61.1452 | 61.1505 | 61.1798 | 61.2657 | 61.1449 | 60.3513 | 60.3639 | 60.2917 | 60.2041 | 61.3454 | 61.3785 | 60.9781 | 61.3077 | -0.99413 | -0.62684 | -1.0537 | -0.68638
1074.0469 | 121.9345 | -61.1618 | 60.4294 | 0.12643 | 0.028162 | -0.030314 | -0.020438 | 0.004219 | 0.085583 | -0.03067 | 60.3009 | 60.3227 | 60.2505 | 60.172 | 61.3133 | 61.3373 | 60.9369 | 61.2619 | 61.2882 | 61.19 | 61.1315 | 61.1414 | 61.166 | 61.2474 | 61.1311 | 60.3421 | 60.3639 | 60.2917 | 60.2132 | 61.3545 | 61.3785 | 60.9781 | 61.3031 | -1.0124 | -0.636 | -1.0628 | -0.68638
1075.8125 | 121.9299 | -61.2625 | 60.3104 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.013375 | 0.09474 | -0.026092 | 60.3146 | 60.3227 | 60.246 | 60.1629 | 61.3088 | 61.3327 | 60.9278 | 61.2619 | 61.3752 | 61.2907 | 61.2414 | 61.2512 | 61.2759 | 61.3573 | 61.2364 | 60.3558 | 60.3639 | 60.2872 | 60.2041 | 61.35 | 61.3739 | 60.9689 | 61.3031 | -0.99413 | -0.61311 | -1.0628 | -0.6818
1077.5469 | 121.962 | -61.2671 | 60.2921 | 0.11727 | 0.037319 | -0.021157 | -0.020438 | 0.008797 | 0.09474 | -0.026092 | 60.3055 | 60.3319 | 60.246 | 60.1674 | 61.2996 | 61.3327 | 60.9232 | 61.2619 | 61.3844 | 61.3044 | 61.2459 | 61.2467 | 61.2759 | 61.3618 | 61.241 | 60.3467 | 60.3731 | 60.2872 | 60.2086 | 61.3408 | 61.3739 | 60.9644 | 61.3031 | -0.99413 | -0.61769 | -1.0537 | -0.67722
1079.2969 | 121.8567 | -61.322 | 60.3424 | 0.12185 | 0.041898 | -0.021157 | -0.020438 | 0.008797 | 0.099318 | -0.03067 | 60.3146 | 60.3227 | 60.2414 | 60.1674 | 61.3042 | 61.3373 | 60.9323 | 61.2711 | 61.4439 | 61.3639 | 61.3009 | 61.3016 | 61.3308 | 61.4213 | 61.2914 | 60.3558 | 60.3639 | 60.2826 | 60.2086 | 61.3454 | 61.3785 | 60.9735 | 61.3123 | -0.98955 | -0.61769 | -1.0628 | -0.69095
1080.9844 | 121.8842 | -61.2717 | 60.3516 | 0.11727 | 0.037319 | -0.025735 | -0.01586 | 0.013375 | 0.090161 | -0.016936 | 60.3101 | 60.3181 | 60.2551 | 60.1766 | 61.295 | 61.3281 | 60.9232 | 61.2665 | 61.3889 | 61.309 | 61.2459 | 61.2558 | 61.285 | 61.3618 | 61.2547 | 60.3513 | 60.3593 | 60.2963 | 60.2178 | 61.3362 | 61.3693 | 60.9644 | 61.3077 | -0.98497 | -0.61311 | -1.0399 | -0.66806
1082.7344 | 121.9254 | -61.2625 | 60.3699 | 0.11727 | 0.028162 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.03067 | 60.3192 | 60.3273 | 60.2505 | 60.172 | 61.2996 | 61.3373 | 60.9232 | 61.2619 | 61.3798 | 61.2907 | 61.2368 | 61.2421 | 61.2713 | 61.3527 | 61.2318 | 60.3604 | 60.3685 | 60.2917 | 60.2132 | 61.3408 | 61.3785 | 60.9644 | 61.3031 | -0.9804 | -0.60395 | -1.0491 | -0.67264
1084.4688 | 121.9894 | -61.171 | 60.3973 | 0.12185 | 0.028162 | -0.025735 | -0.025017 | 0.004219 | 0.09474 | -0.021514 | 60.3055 | 60.3227 | 60.246 | 60.1629 | 61.2996 | 61.3373 | 60.9323 | 61.2619 | 61.2928 | 61.1991 | 61.1452 | 61.1459 | 61.1752 | 61.2657 | 61.1494 | 60.3467 | 60.3639 | 60.2872 | 60.2041 | 61.3408 | 61.3785 | 60.9735 | 61.3031 | -0.99413 | -0.62684 | -1.0537 | -0.68637
1086.2188 | 121.9666 | -61.2671 | 60.3012 | 0.11727 | 0.03274 | -0.034893 | -0.020438 | 0.004219 | 0.099318 | -0.03067 | 60.3101 | 60.3227 | 60.2505 | 60.1674 | 61.3042 | 61.3418 | 60.9323 | 61.2665 | 61.3844 | 61.2998 | 61.2322 | 61.2467 | 61.2713 | 61.3664 | 61.2364 | 60.3513 | 60.3639 | 60.2917 | 60.2086 | 61.3454 | 61.383 | 60.9735 | 61.3077 | -0.99413 | -0.62226 | -1.0537 | -0.6818
1087.9062 | 121.8292 | -61.322 | 60.347 | 0.11269 | 0.037319 | -0.016578 | -0.025017 | 0.013375 | 0.09474 | -0.021514 | 60.3146 | 60.3227 | 60.2551 | 60.1812 | 61.2996 | 61.3327 | 60.9278 | 61.2619 | 61.4347 | 61.3593 | 61.3054 | 61.297 | 61.3354 | 61.4168 | 61.3005 | 60.3558 | 60.3639 | 60.2963 | 60.2224 | 61.3408 | 61.3739 | 60.9689 | 61.3031 | -0.98497 | -0.61311 | -1.0445 | -0.67264
1089.6562 | 121.9666 | -61.29 | 60.3058 | 0.11727 | 0.028162 | -0.025735 | -0.01586 | 0.013375 | 0.090161 | -0.026092 | 60.3055 | 60.3227 | 60.2505 | 60.1674 | 61.3042 | 61.3373 | 60.9186 | 61.2665 | 61.4073 | 61.3181 | 61.2642 | 61.2741 | 61.3034 | 61.3801 | 61.2639 | 60.3467 | 60.3639 | 60.2917 | 60.2086 | 61.3454 | 61.3785 | 60.9598 | 61.3077 | -0.99871 | -0.61311 | -1.0537 | -0.66806
1091.4219 | 121.8704 | -61.2991 | 60.3424 | 0.12185 | 0.028162 | -0.025735 | -0.01586 | 0.013375 | 0.090161 | -0.021514 | 60.3146 | 60.3227 | 60.2505 | 60.1629 | 61.3042 | 61.3373 | 60.9186 | 61.2619 | 61.421 | 61.3273 | 61.2734 | 61.2833 | 61.3125 | 61.3893 | 61.2776 | 60.3558 | 60.3639 | 60.2917 | 60.2041 | 61.3454 | 61.3785 | 60.9598 | 61.3031 | -0.98955 | -0.60395 | -1.0537 | -0.66806
1093.1875 | 121.8567 | -61.3129 | 60.3378 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | 0.017953 | 0.09474 | -0.021514 | 60.3101 | 60.3227 | 60.2551 | 60.1674 | 61.3042 | 61.3373 | 60.9232 | 61.2711 | 61.4347 | 61.341 | 61.2917 | 61.2924 | 61.3308 | 61.4076 | 61.2914 | 60.3513 | 60.3639 | 60.2963 | 60.2086 | 61.3454 | 61.3785 | 60.9644 | 61.3123 | -0.99413 | -0.61311 | -1.0491 | -0.66806
1094.875 | 121.9666 | -61.1801 | 60.4202 | 0.12185 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.03067 | 60.3101 | 60.3227 | 60.2505 | 60.1674 | 61.3088 | 61.3373 | 60.9232 | 61.2665 | 61.302 | 61.2037 | 61.1544 | 61.1597 | 61.1889 | 61.2703 | 61.1494 | 60.3513 | 60.3639 | 60.2917 | 60.2086 | 61.35 | 61.3785 | 60.9644 | 61.3077 | -0.99871 | -0.61311 | -1.0582 | -0.67264
1096.625 | 121.9345 | -61.235 | 60.379 | 0.11727 | 0.028162 | -0.025735 | -0.020438 | 0.008797 | 0.099318 | -0.03067 | 60.3146 | 60.3227 | 60.246 | 60.172 | 61.3088 | 61.3373 | 60.9323 | 61.2665 | 61.3523 | 61.2632 | 61.2093 | 61.2146 | 61.2438 | 61.3344 | 61.2044 | 60.3558 | 60.3639 | 60.2872 | 60.2132 | 61.35 | 61.3785 | 60.9735 | 61.3077 | -0.99413 | -0.61769 | -1.0628 | -0.68637
1098.3281 | 121.907 | -61.2213 | 60.3836 | 0.11269 | 0.03274 | -0.025735 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.3009 | 60.3227 | 60.2505 | 60.1674 | 61.2996 | 61.3373 | 60.9278 | 61.2665 | 61.334 | 61.2541 | 61.1956 | 61.1963 | 61.2301 | 61.3115 | 61.1952 | 60.3421 | 60.3639 | 60.2917 | 60.2086 | 61.3408 | 61.3785 | 60.9689 | 61.3077 | -0.99871 | -0.62684 | -1.0491 | -0.67722
1100.0781 | 121.8567 | -61.322 | 60.3241 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | 0.008797 | 0.09474 | -0.021514 | 60.3146 | 60.3319 | 60.2505 | 60.1674 | 61.2996 | 61.3281 | 60.9278 | 61.2619 | 61.4439 | 61.3548 | 61.3009 | 61.3062 | 61.3308 | 61.4168 | 61.3005 | 60.3558 | 60.3731 | 60.2917 | 60.2086 | 61.3408 | 61.3693 | 60.9689 | 61.3031 | -0.98497 | -0.61311 | -1.0491 | -0.67722
1101.8281 | 121.9391 | -61.2167 | 60.379 | 0.12185 | 0.023583 | -0.030314 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.3146 | 60.3273 | 60.2597 | 60.1629 | 61.3042 | 61.3327 | 60.9323 | 61.2619 | 61.3386 | 61.2403 | 61.1864 | 61.1963 | 61.221 | 61.3069 | 61.1906 | 60.3558 | 60.3685 | 60.3009 | 60.2041 | 61.3454 | 61.3739 | 60.9735 | 61.3031 | -0.98955 | -0.61769 | -1.0445 | -0.67264
1103.5781 | 121.9711 | -61.2946 | 60.2829 | 0.12185 | 0.03274 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.03067 | 60.3055 | 60.3319 | 60.2505 | 60.1766 | 61.295 | 61.3373 | 60.9323 | 61.2619 | 61.4164 | 61.3273 | 61.2688 | 61.2741 | 61.3034 | 61.3847 | 61.2639 | 60.3467 | 60.3731 | 60.2917 | 60.2178 | 61.3362 | 61.3785 | 60.9735 | 61.3031 | -0.98955 | -0.62684 | -1.0445 | -0.6818
1105.3281 | 121.962 | -61.203 | 60.4065 | 0.11727 | 0.037319 | -0.025735 | -0.01586 | 0.004219 | 0.090161 | -0.026092 | 60.3009 | 60.3227 | 60.2551 | 60.172 | 61.2996 | 61.3373 | 60.9369 | 61.2711 | 61.3203 | 61.2403 | 61.1773 | 61.1871 | 61.2072 | 61.2932 | 61.1769 | 60.3421 | 60.3639 | 60.2963 | 60.2132 | 61.3408 | 61.3785 | 60.9781 | 61.3123 | -0.99871 | -0.636 | -1.0445 | -0.6818
1107.0156 | 121.9437 | -61.2305 | 60.3516 | 0.11727 | 0.023583 | -0.030314 | -0.025017 | 0.004219 | 0.085583 | -0.03067 | 60.3101 | 60.3181 | 60.2505 | 60.1674 | 61.3088 | 61.3373 | 60.9186 | 61.2619 | 61.3477 | 61.2541 | 61.2002 | 61.2055 | 61.2347 | 61.3161 | 61.1998 | 60.3513 | 60.3593 | 60.2917 | 60.2086 | 61.35 | 61.3785 | 60.9598 | 61.3031 | -0.99871 | -0.60853 | -1.0582 | -0.66806
1108.7656 | 122.0032 | -61.1664 | 60.4065 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.09474 | -0.026092 | 60.3101 | 60.3227 | 60.2505 | 60.172 | 61.2996 | 61.3327 | 60.9369 | 61.2619 | 61.2882 | 61.1945 | 61.1452 | 61.1459 | 61.1752 | 61.2611 | 61.1403 | 60.3513 | 60.3639 | 60.2917 | 60.2132 | 61.3408 | 61.3739 | 60.9781 | 61.3031 | -0.98955 | -0.62684 | -1.0491 | -0.68638
1110.5 | 121.9437 | -61.1847 | 60.4019 | 0.13101 | 0.023583 | -0.030314 | -0.025017 | 0.008797 | 0.09474 | -0.021514 | 60.3101 | 60.3273 | 60.246 | 60.172 | 61.3042 | 61.3327 | 60.9278 | 61.2619 | 61.3157 | 61.2083 | 61.1544 | 61.1597 | 61.1935 | 61.2794 | 61.1632 | 60.3513 | 60.3685 | 60.2872 | 60.2132 | 61.3454 | 61.3739 | 60.9689 | 61.3031 | -0.99413 | -0.61769 | -1.0582 | -0.6818
1112.1875 | 121.9574 | -61.2762 | 60.2875 | 0.12643 | 0.03274 | -0.025735 | -0.020438 | 0.008797 | 0.085583 | -0.03067 | 60.3101 | 60.3227 | 60.2551 | 60.172 | 61.3042 | 61.3281 | 60.9232 | 61.2711 | 61.4027 | 61.309 | 61.2505 | 61.2558 | 61.285 | 61.3618 | 61.2456 | 60.3513 | 60.3639 | 60.2963 | 60.2132 | 61.3454 | 61.3693 | 60.9644 | 61.3123 | -0.99413 | -0.61311 | -1.0491 | -0.66806
1113.9531 | 121.8979 | -61.2717 | 60.3378 | 0.12185 | 0.03274 | -0.030314 | -0.01586 | -0.000359 | 0.09474 | -0.016936 | 60.3101 | 60.3319 | 60.2597 | 60.1674 | 61.3042 | 61.3281 | 60.9278 | 61.2619 | 61.3935 | 61.3044 | 61.2414 | 61.2558 | 61.2713 | 61.3664 | 61.2547 | 60.3513 | 60.3731 | 60.3009 | 60.2086 | 61.3454 | 61.3693 | 60.9689 | 61.3031 | -0.99413 | -0.61769 | -1.0445 | -0.66806
1115.7031 | 121.8384 | -61.3403 | 60.3333 | 0.12643 | 0.037319 | -0.030314 | -0.011281 | 0.004219 | 0.09474 | -0.016936 | 60.3101 | 60.3273 | 60.2505 | 60.172 | 61.2996 | 61.3327 | 60.9278 | 61.2665 | 61.4668 | 61.3777 | 61.31 | 61.3291 | 61.3446 | 61.4351 | 61.3234 | 60.3513 | 60.3685 | 60.2917 | 60.2132 | 61.3408 | 61.3739 | 60.9689 | 61.3077 | -0.98955 | -0.61769 | -1.0491 | -0.67722
1117.3906 | 121.9528 | -61.1938 | 60.3882 | 0.11269 | 0.019004 | -0.030314 | -0.029595 | 0.004219 | 0.081005 | -0.026092 | 60.3101 | 60.3273 | 60.2551 | 60.1766 | 61.295 | 61.3418 | 60.9278 | 61.2619 | 61.3065 | 61.2129 | 61.1635 | 61.1643 | 61.1981 | 61.2749 | 61.1678 | 60.3513 | 60.3685 | 60.2963 | 60.2178 | 61.3362 | 61.383 | 60.9689 | 61.3031 | -0.98497 | -0.61769 | -1.0399 | -0.67264
1119.1719 | 121.8613 | -61.3129 | 60.3241 | 0.11727 | 0.028162 | -0.025735 | -0.01586 | 0.013375 | 0.085583 | -0.016936 | 60.3146 | 60.3273 | 60.2551 | 60.172 | 61.2996 | 61.3281 | 60.9232 | 61.2619 | 61.4301 | 61.341 | 61.2871 | 61.297 | 61.3262 | 61.3984 | 61.2959 | 60.3558 | 60.3685 | 60.2963 | 60.2132 | 61.3408 | 61.3693 | 60.9644 | 61.3031 | -0.98497 | -0.60853 | -1.0445 | -0.66806
1120.8594 | 121.843 | -61.3266 | 60.3378 | 0.11727 | 0.03274 | -0.025735 | -0.020438 | 0.013375 | 0.099318 | -0.016936 | 60.3101 | 60.3273 | 60.2551 | 60.1766 | 61.2996 | 61.3373 | 60.9232 | 61.2665 | 61.4439 | 61.3593 | 61.3009 | 61.3062 | 61.34 | 61.4259 | 61.3097 | 60.3513 | 60.3685 | 60.2963 | 60.2178 | 61.3408 | 61.3785 | 60.9644 | 61.3077 | -0.98955 | -0.61311 | -1.0445 | -0.66806
1122.5938 | 121.8338 | -61.3174 | 60.347 | 0.12185 | 0.03274 | -0.016578 | -0.011281 | 0.008797 | 0.09474 | -0.016936 | 60.3055 | 60.3273 | 60.2505 | 60.1766 | 61.3042 | 61.3327 | 60.9186 | 61.2665 | 61.4393 | 61.3502 | 61.3009 | 61.3062 | 61.3262 | 61.4122 | 61.3005 | 60.3467 | 60.3685 | 60.2917 | 60.2178 | 61.3454 | 61.3739 | 60.9598 | 61.3077 | -0.99871 | -0.61311 | -1.0537 | -0.66806
1124.3438 | 121.9208 | -61.1847 | 60.3973 | 0.11727 | 0.028162 | -0.030314 | -0.025017 | 0.013375 | 0.09474 | -0.021514 | 60.3192 | 60.3365 | 60.2551 | 60.172 | 61.3042 | 61.3327 | 60.9232 | 61.2665 | 61.302 | 61.2129 | 61.1544 | 61.1597 | 61.1981 | 61.2794 | 61.1632 | 60.3604 | 60.3776 | 60.2963 | 60.2132 | 61.3454 | 61.3739 | 60.9644 | 61.3077 | -0.98497 | -0.60395 | -1.0491 | -0.66806
1126.0938 | 121.8613 | -61.3358 | 60.3012 | 0.11269 | 0.03274 | -0.021157 | -0.011281 | 0.013375 | 0.090161 | -0.021514 | 60.3146 | 60.3365 | 60.2643 | 60.172 | 61.3042 | 61.3281 | 60.9232 | 61.2665 | 61.4484 | 61.3685 | 61.3146 | 61.3245 | 61.3491 | 61.4259 | 61.3142 | 60.3558 | 60.3776 | 60.3055 | 60.2132 | 61.3454 | 61.3693 | 60.9644 | 61.3077 | -0.98955 | -0.60853 | -1.0399 | -0.65891
1127.7812 | 121.8475 | -61.2167 | 60.4294 | 0.11727 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.3101 | 60.3227 | 60.2551 | 60.172 | 61.3133 | 61.3373 | 60.9278 | 61.2619 | 61.334 | 61.2403 | 61.191 | 61.1963 | 61.2255 | 61.3069 | 61.1952 | 60.3513 | 60.3639 | 60.2963 | 60.2132 | 61.3545 | 61.3785 | 60.9689 | 61.3031 | -1.0033 | -0.61769 | -1.0582 | -0.67264
1129.5469 | 121.8201 | -61.3449 | 60.3378 | 0.11269 | 0.028162 | -0.025735 | -0.01586 | 0.008797 | 0.09474 | -0.021514 | 60.3192 | 60.3227 | 60.2505 | 60.172 | 61.3042 | 61.3327 | 60.914 | 61.2619 | 61.4576 | 61.3731 | 61.3192 | 61.329 | 61.3537 | 61.4397 | 61.3234 | 60.3604 | 60.3639 | 60.2917 | 60.2132 | 61.3454 | 61.3739 | 60.9552 | 61.3031 | -0.98497 | -0.59479 | -1.0537 | -0.66348
1131.2344 | 121.8658 | -61.2625 | 60.4248 | 0.12185 | 0.019004 | -0.021157 | -0.01586 | 0.013375 | 0.090161 | -0.021514 | 60.3146 | 60.3227 | 60.2597 | 60.172 | 61.2996 | 61.3327 | 60.9278 | 61.2619 | 61.3844 | 61.2815 | 61.2414 | 61.2467 | 61.2759 | 61.3527 | 61.241 | 60.3558 | 60.3639 | 60.3009 | 60.2132 | 61.3408 | 61.3739 | 60.9689 | 61.3031 | -0.98497 | -0.61311 | -1.0399 | -0.66806
1133 | 121.8887 | -61.2579 | 60.3699 | 0.11727 | 0.03274 | -0.021157 | -0.020438 | 0.008797 | 0.09474 | -0.021514 | 60.3192 | 60.3273 | 60.2551 | 60.1766 | 61.2996 | 61.3327 | 60.9278 | 61.2619 | 61.3752 | 61.2907 | 61.2368 | 61.2375 | 61.2667 | 61.3527 | 61.2364 | 60.3604 | 60.3685 | 60.2963 | 60.2178 | 61.3408 | 61.3739 | 60.9689 | 61.3031 | -0.9804 | -0.60853 | -1.0445 | -0.67264
1134.75 | 121.8842 | -61.2854 | 60.3607 | 0.13101 | 0.023583 | -0.021157 | -0.011281 | 0.017953 | 0.09474 | -0.021514 | 60.3192 | 60.3319 | 60.2643 | 60.1812 | 61.3042 | 61.3327 | 60.9232 | 61.2619 | 61.4164 | 61.309 | 61.2642 | 61.2741 | 61.3034 | 61.3801 | 61.2639 | 60.3604 | 60.3731 | 60.3055 | 60.2224 | 61.3454 | 61.3739 | 60.9644 | 61.3031 | -0.98497 | -0.60395 | -1.0399 | -0.65891
1136.4531 | 121.8887 | -61.2762 | 60.4294 | 0.12185 | 0.03274 | -0.025735 | -0.011281 | 0.013375 | 0.09474 | -0.021514 | 60.3146 | 60.3365 | 60.2643 | 60.1812 | 61.295 | 61.3327 | 60.9232 | 61.2619 | 61.3981 | 61.309 | 61.2505 | 61.265 | 61.2896 | 61.371 | 61.2547 | 60.3558 | 60.3776 | 60.3055 | 60.2224 | 61.3362 | 61.3739 | 60.9644 | 61.3031 | -0.9804 | -0.60853 | -1.0308 | -0.65891
1138.2031 | 121.9299 | -61.2305 | 60.3241 | 0.11269 | 0.023583 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.021514 | 60.3192 | 60.3273 | 60.2597 | 60.1766 | 61.3042 | 61.3235 | 60.9278 | 61.2619 | 61.3432 | 61.2541 | 61.2047 | 61.2146 | 61.2301 | 61.3161 | 61.209 | 60.3604 | 60.3685 | 60.3009 | 60.2178 | 61.3454 | 61.3647 | 60.9689 | 61.3031 | -0.98497 | -0.60853 | -1.0445 | -0.66806
1139.8906 | 121.9254 | -61.2122 | 60.3516 | 0.12643 | 0.028162 | -0.025735 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.3192 | 60.3227 | 60.2505 | 60.172 | 61.3088 | 61.3327 | 60.9278 | 61.2574 | 61.3386 | 61.2403 | 61.1864 | 61.1871 | 61.221 | 61.3023 | 61.1861 | 60.3604 | 60.3639 | 60.2917 | 60.2132 | 61.35 | 61.3739 | 60.9689 | 61.2986 | -0.98955 | -0.60853 | -1.0582 | -0.67722
1141.6406 | 121.9711 | -61.2671 | 60.3012 | 0.12185 | 0.028162 | -0.030314 | -0.029595 | 0.013375 | 0.09474 | -0.03067 | 60.3192 | 60.3319 | 60.2551 | 60.1766 | 61.2996 | 61.3281 | 60.9232 | 61.2574 | 61.3889 | 61.2953 | 61.2368 | 61.2375 | 61.2805 | 61.3618 | 61.2364 | 60.3604 | 60.3731 | 60.2963 | 60.2178 | 61.3408 | 61.3693 | 60.9644 | 61.2986 | -0.9804 | -0.60395 | -1.0445 | -0.66806
1143.3906 | 121.9711 | -61.2534 | 60.2829 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.03067 | 60.3146 | 60.3319 | 60.2597 | 60.1766 | 61.2996 | 61.3281 | 60.9232 | 61.2665 | 61.3752 | 61.2769 | 61.2322 | 61.2283 | 61.2622 | 61.3389 | 61.2227 | 60.3558 | 60.3731 | 60.3009 | 60.2178 | 61.3408 | 61.3693 | 60.9644 | 61.3077 | -0.98497 | -0.60853 | -1.0399 | -0.66348
1145.1562 | 121.8933 | -61.3037 | 60.3745 | 0.12185 | 0.028162 | -0.025735 | -0.020438 | 0.013375 | 0.090161 | -0.021514 | 60.3146 | 60.3319 | 60.2643 | 60.1766 | 61.2996 | 61.3281 | 60.9232 | 61.2619 | 61.4256 | 61.3319 | 61.278 | 61.2833 | 61.3171 | 61.3939 | 61.2822 | 60.3558 | 60.3731 | 60.3055 | 60.2178 | 61.3408 | 61.3693 | 60.9644 | 61.3031 | -0.98497 | -0.60853 | -1.0353 | -0.65891
1146.8438 | 121.8704 | -61.2076 | 60.4385 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.09474 | -0.021514 | 60.3146 | 60.3365 | 60.2597 | 60.1766 | 61.295 | 61.3373 | 60.9232 | 61.2619 | 61.334 | 61.2357 | 61.1864 | 61.1871 | 61.2118 | 61.3023 | 61.1861 | 60.3558 | 60.3776 | 60.3009 | 60.2178 | 61.3362 | 61.3785 | 60.9644 | 61.3031 | -0.9804 | -0.60853 | -1.0354 | -0.66348
1148.5938 | 121.8475 | -61.3312 | 60.3241 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.09474 | -0.016936 | 60.3192 | 60.3273 | 60.2597 | 60.1766 | 61.3042 | 61.3373 | 60.9186 | 61.2619 | 61.4484 | 61.3593 | 61.31 | 61.3107 | 61.34 | 61.4259 | 61.3142 | 60.3604 | 60.3685 | 60.3009 | 60.2178 | 61.3454 | 61.3785 | 60.9598 | 61.3031 | -0.98497 | -0.59937 | -1.0445 | -0.65891
1150.3281 | 121.8842 | -61.2625 | 60.4019 | 0.12643 | 0.023583 | -0.016578 | -0.020438 | 0.004219 | 0.09474 | -0.021514 | 60.3192 | 60.3365 | 60.2643 | 60.1766 | 61.2996 | 61.3281 | 60.9232 | 61.2619 | 61.3889 | 61.2861 | 61.2459 | 61.2421 | 61.2667 | 61.3573 | 61.241 | 60.3604 | 60.3776 | 60.3055 | 60.2178 | 61.3408 | 61.3693 | 60.9644 | 61.3031 | -0.9804 | -0.60395 | -1.0353 | -0.65891
1152.0781 | 121.8475 | -61.2991 | 60.3378 | 0.11727 | 0.03274 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 60.3238 | 60.3365 | 60.2597 | 60.172 | 61.2996 | 61.3281 | 60.9278 | 61.2619 | 61.4164 | 61.3319 | 61.2826 | 61.2879 | 61.3079 | 61.3893 | 61.2822 | 60.365 | 60.3776 | 60.3009 | 60.2132 | 61.3408 | 61.3693 | 60.9689 | 61.3031 | -0.97582 | -0.60395 | -1.0399 | -0.66806
1153.7656 | 121.9803 | -61.2671 | 60.2921 | 0.12185 | 0.019004 | -0.025735 | -0.01586 | 0.017953 | 0.090161 | -0.026092 | 60.3238 | 60.3319 | 60.2551 | 60.1812 | 61.2996 | 61.3327 | 60.9232 | 61.2574 | 61.3889 | 61.2861 | 61.2414 | 61.2512 | 61.285 | 61.3573 | 61.241 | 60.365 | 60.3731 | 60.2963 | 60.2224 | 61.3408 | 61.3739 | 60.9644 | 61.2986 | -0.97582 | -0.59937 | -1.0445 | -0.66806
1155.5156 | 121.9208 | -61.2213 | 60.3607 | 0.12185 | 0.023583 | -0.030314 | -0.025017 | 0.004219 | 0.090161 | -0.026092 | 60.3146 | 60.3227 | 60.2597 | 60.1766 | 61.3042 | 61.3373 | 60.914 | 61.2528 | 61.3432 | 61.2449 | 61.191 | 61.1963 | 61.2255 | 61.3115 | 61.1952 | 60.3558 | 60.3639 | 60.3009 | 60.2178 | 61.3454 | 61.3785 | 60.9552 | 61.294 | -0.98955 | -0.59937 | -1.0445 | -0.65433
1157.2656 | 121.8384 | -61.3083 | 60.3745 | 0.11269 | 0.03274 | -0.016578 | -0.020438 | 0.013375 | 0.09474 | -0.021514 | 60.3146 | 60.341 | 60.2643 | 60.1766 | 61.2996 | 61.3327 | 60.9186 | 61.2665 | 61.421 | 61.341 | 61.2917 | 61.2879 | 61.3217 | 61.403 | 61.2868 | 60.3558 | 60.3822 | 60.3055 | 60.2178 | 61.3408 | 61.3739 | 60.9598 | 61.3077 | -0.98497 | -0.60395 | -1.0353 | -0.65433
1159.0156 | 121.907 | -61.1938 | 60.4385 | 0.11727 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.09474 | -0.021514 | 60.3284 | 60.3227 | 60.2643 | 60.172 | 61.2905 | 61.3281 | 60.9232 | 61.2528 | 61.3111 | 61.2174 | 61.1681 | 61.1734 | 61.2026 | 61.2886 | 61.1723 | 60.3696 | 60.3639 | 60.3055 | 60.2132 | 61.3317 | 61.3693 | 60.9644 | 61.294 | -0.96208 | -0.59479 | -1.0262 | -0.65891
1160.7031 | 121.9345 | -61.2122 | 60.3561 | 0.12185 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.09474 | -0.021514 | 60.3192 | 60.3365 | 60.2597 | 60.172 | 61.295 | 61.3327 | 60.9186 | 61.2619 | 61.334 | 61.2357 | 61.1956 | 61.1963 | 61.2164 | 61.3069 | 61.1906 | 60.3604 | 60.3776 | 60.3009 | 60.2132 | 61.3362 | 61.3739 | 60.9598 | 61.3031 | -0.97582 | -0.59937 | -1.0354 | -0.65891
1162.4375 | 121.9803 | -61.1847 | 60.4019 | 0.11727 | 0.019004 | -0.021157 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.3192 | 60.3273 | 60.2597 | 60.172 | 61.2996 | 61.3327 | 60.9232 | 61.2574 | 61.302 | 61.2037 | 61.1635 | 61.1643 | 61.1889 | 61.2749 | 61.1586 | 60.3604 | 60.3685 | 60.3009 | 60.2132 | 61.3408 | 61.3739 | 60.9644 | 61.2986 | -0.9804 | -0.60395 | -1.0399 | -0.66348
1164.1875 | 121.8567 | -61.2122 | 60.4431 | 0.12643 | 0.028162 | -0.016578 | -0.01586 | 0.013375 | 0.090161 | -0.021514 | 60.3192 | 60.3319 | 60.2551 | 60.1766 | 61.2996 | 61.3418 | 60.9232 | 61.2665 | 61.3386 | 61.2403 | 61.1956 | 61.1963 | 61.2255 | 61.3023 | 61.1906 | 60.3604 | 60.3731 | 60.2963 | 60.2178 | 61.3408 | 61.383 | 60.9644 | 61.3077 | -0.9804 | -0.60395 | -1.0445 | -0.66806
1165.875 | 121.9757 | -61.2762 | 60.2921 | 0.12185 | 0.023583 | -0.030314 | -0.01586 | 0.008797 | 0.09474 | -0.021514 | 60.3238 | 60.3319 | 60.2597 | 60.1766 | 61.3042 | 61.3327 | 60.9232 | 61.2574 | 61.3981 | 61.2998 | 61.2459 | 61.2604 | 61.285 | 61.371 | 61.2547 | 60.365 | 60.3731 | 60.3009 | 60.2178 | 61.3454 | 61.3739 | 60.9644 | 61.2986 | -0.98039 | -0.59937 | -1.0445 | -0.66348
1167.625 | 121.9666 | -61.2625 | 60.3287 | 0.11727 | 0.023583 | -0.012 | -0.01586 | 0.004219 | 0.090161 | -0.016936 | 60.3192 | 60.3319 | 60.2597 | 60.1766 | 61.2996 | 61.3235 | 60.9278 | 61.2574 | 61.3798 | 61.2861 | 61.2505 | 61.2467 | 61.2667 | 61.3527 | 61.2456 | 60.3604 | 60.3731 | 60.3009 | 60.2178 | 61.3408 | 61.3647 | 60.9689 | 61.2986 | -0.9804 | -0.60853 | -1.0399 | -0.66806
1169.3906 | 121.8521 | -61.3129 | 60.3745 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.099318 | -0.026092 | 60.3238 | 60.3319 | 60.2551 | 60.172 | 61.3042 | 61.3327 | 60.9186 | 61.2574 | 61.4393 | 61.341 | 61.2917 | 61.2924 | 61.3217 | 61.4122 | 61.2868 | 60.365 | 60.3731 | 60.2963 | 60.2132 | 61.3454 | 61.3739 | 60.9598 | 61.2986 | -0.98039 | -0.59479 | -1.0491 | -0.66348
1171.1406 | 121.9025 | -61.2442 | 60.4019 | 0.12643 | 0.019004 | -0.012 | -0.011281 | 0.013375 | 0.09474 | -0.016936 | 60.3192 | 60.3319 | 60.2551 | 60.172 | 61.2996 | 61.3327 | 60.9278 | 61.2574 | 61.3706 | 61.2632 | 61.2322 | 61.2329 | 61.2576 | 61.3389 | 61.2273 | 60.3604 | 60.3731 | 60.2963 | 60.2132 | 61.3408 | 61.3739 | 60.9689 | 61.2986 | -0.9804 | -0.60853 | -1.0445 | -0.67264
1172.8281 | 121.8933 | -61.3129 | 60.3149 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.021514 | 60.3146 | 60.3319 | 60.2597 | 60.1766 | 61.295 | 61.3327 | 60.9232 | 61.2574 | 61.4393 | 61.341 | 61.2917 | 61.2924 | 61.3262 | 61.3984 | 61.2914 | 60.3558 | 60.3731 | 60.3009 | 60.2178 | 61.3362 | 61.3739 | 60.9644 | 61.2986 | -0.9804 | -0.60853 | -1.0354 | -0.66348
1174.5781 | 121.9757 | -61.1435 | 60.4019 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | 0.008797 | 0.09474 | -0.026092 | 60.3238 | 60.3365 | 60.2551 | 60.1766 | 61.295 | 61.3327 | 60.9278 | 61.2619 | 61.2653 | 61.1762 | 61.1223 | 61.1185 | 61.1523 | 61.2382 | 61.1174 | 60.365 | 60.3776 | 60.2963 | 60.2178 | 61.3362 | 61.3739 | 60.9689 | 61.3031 | -0.97124 | -0.60395 | -1.0399 | -0.67264
1176.2812 | 121.9254 | -61.2167 | 60.3653 | 0.12185 | 0.023583 | -0.012 | -0.01586 | 0.013375 | 0.085583 | -0.026092 | 60.3146 | 60.3319 | 60.2505 | 60.1812 | 61.3042 | 61.3327 | 60.9278 | 61.2574 | 61.3386 | 61.2403 | 61.2047 | 61.2009 | 61.2301 | 61.3023 | 61.1906 | 60.3558 | 60.3731 | 60.2917 | 60.2224 | 61.3454 | 61.3739 | 60.9689 | 61.2986 | -0.98955 | -0.61311 | -1.0537 | -0.67722
1178.0312 | 122.0123 | -61.1984 | 60.3928 | 0.12185 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.090161 | -0.03067 | 60.3192 | 60.3319 | 60.2643 | 60.1812 | 61.2996 | 61.3327 | 60.9278 | 61.2665 | 61.3203 | 61.2266 | 61.1773 | 61.1826 | 61.2072 | 61.2886 | 61.1678 | 60.3604 | 60.3731 | 60.3055 | 60.2224 | 61.3408 | 61.3739 | 60.9689 | 61.3077 | -0.9804 | -0.60853 | -1.0353 | -0.66348
1179.7344 | 121.8338 | -61.2259 | 60.4431 | 0.12643 | 0.023583 | -0.016578 | -0.020438 | 0.013375 | 0.090161 | -0.021514 | 60.3192 | 60.3365 | 60.2597 | 60.1857 | 61.2996 | 61.3235 | 60.9278 | 61.2574 | 61.3523 | 61.2495 | 61.2093 | 61.2055 | 61.2393 | 61.3161 | 61.2044 | 60.3604 | 60.3776 | 60.3009 | 60.2269 | 61.3408 | 61.3647 | 60.9689 | 61.2986 | -0.9804 | -0.60853 | -1.0399 | -0.66806
1181.4844 | 121.8704 | -61.2122 | 60.4568 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.026092 | 60.3192 | 60.3365 | 60.2597 | 60.1812 | 61.2996 | 61.3281 | 60.9232 | 61.2528 | 61.334 | 61.2449 | 61.191 | 61.1917 | 61.221 | 61.2977 | 61.1861 | 60.3604 | 60.3776 | 60.3009 | 60.2224 | 61.3408 | 61.3693 | 60.9644 | 61.294 | -0.9804 | -0.60395 | -1.0399 | -0.66348
1183.1719 | 121.9757 | -61.1847 | 60.4202 | 0.11269 | 0.028162 | -0.025735 | -0.01586 | 0.013375 | 0.090161 | -0.026092 | 60.3238 | 60.3319 | 60.2643 | 60.1766 | 61.295 | 61.3235 | 60.9232 | 61.2528 | 61.2974 | 61.2129 | 61.159 | 61.1688 | 61.1981 | 61.2749 | 61.1586 | 60.365 | 60.3731 | 60.3055 | 60.2178 | 61.3362 | 61.3647 | 60.9644 | 61.294 | -0.97124 | -0.59937 | -1.0308 | -0.65891
1184.9062 | 121.8796 | -61.2717 | 60.3882 | 0.12185 | 0.03274 | -0.021157 | -0.011281 | 0.017953 | 0.09474 | -0.016936 | 60.3284 | 60.3365 | 60.2643 | 60.1903 | 61.2905 | 61.3189 | 60.9094 | 61.2528 | 61.3935 | 61.3044 | 61.2505 | 61.2604 | 61.2896 | 61.3664 | 61.2547 | 60.3696 | 60.3776 | 60.3055 | 60.2315 | 61.3317 | 61.3601 | 60.9506 | 61.294 | -0.96208 | -0.58106 | -1.0262 | -0.64517
1186.6562 | 121.9299 | -61.2122 | 60.3653 | 0.12185 | 0.028162 | -0.021157 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.3284 | 60.3502 | 60.2688 | 60.1857 | 61.2996 | 61.3235 | 60.9094 | 61.2482 | 61.334 | 61.2403 | 61.191 | 61.1871 | 61.221 | 61.3023 | 61.1861 | 60.3696 | 60.3914 | 60.31 | 60.2269 | 61.3408 | 61.3647 | 60.9506 | 61.2894 | -0.97124 | -0.58106 | -1.0308 | -0.64059
1188.3438 | 121.8246 | -61.322 | 60.3424 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.022531 | 0.099318 | -0.016936 | 60.3375 | 60.341 | 60.278 | 60.1949 | 61.2859 | 61.3189 | 60.9094 | 61.2482 | 61.4393 | 61.3502 | 61.3054 | 61.3062 | 61.3446 | 61.4213 | 61.3051 | 60.3787 | 60.3822 | 60.3192 | 60.2361 | 61.3271 | 61.3601 | 60.9506 | 61.2894 | -0.94835 | -0.5719 | -1.0079 | -0.63143
1190.0938 | 121.8933 | -61.2946 | 60.347 | 0.11727 | 0.023583 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.03067 | 60.333 | 60.341 | 60.2826 | 60.1857 | 61.2813 | 61.3189 | 60.914 | 61.2436 | 61.4118 | 61.3181 | 61.278 | 61.2741 | 61.3079 | 61.3801 | 61.2639 | 60.3742 | 60.3822 | 60.3238 | 60.2269 | 61.3225 | 61.3601 | 60.9552 | 61.2848 | -0.94835 | -0.58106 | -0.99872 | -0.63144
1191.7812 | 121.9757 | -61.1526 | 60.4202 | 0.11727 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 60.3375 | 60.3502 | 60.2734 | 60.1903 | 61.2905 | 61.3144 | 60.914 | 61.2528 | 61.2699 | 61.1717 | 61.1315 | 61.1368 | 61.1614 | 61.2382 | 61.1311 | 60.3787 | 60.3914 | 60.3146 | 60.2315 | 61.3317 | 61.3556 | 60.9552 | 61.294 | -0.95293 | -0.57648 | -1.017 | -0.64059
1193.5312 | 121.843 | -61.2122 | 60.4706 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.099318 | -0.026092 | 60.3421 | 60.3548 | 60.2734 | 60.1995 | 61.2813 | 61.3144 | 60.9049 | 61.2345 | 61.334 | 61.2357 | 61.191 | 61.1963 | 61.2164 | 61.3115 | 61.1861 | 60.3833 | 60.396 | 60.3146 | 60.2407 | 61.3225 | 61.3556 | 60.9461 | 61.2757 | -0.93919 | -0.56275 | -1.0079 | -0.63144
1195.2188 | 121.8704 | -61.1938 | 60.4614 | 0.11727 | 0.019004 | -0.012 | -0.025017 | 0.013375 | 0.090161 | -0.021514 | 60.3421 | 60.3548 | 60.278 | 60.1949 | 61.2767 | 61.3189 | 60.9003 | 61.2299 | 61.3111 | 61.2129 | 61.1818 | 61.1688 | 61.2072 | 61.284 | 61.1723 | 60.3833 | 60.396 | 60.3192 | 60.2361 | 61.3179 | 61.3601 | 60.9415 | 61.2711 | -0.93461 | -0.55817 | -0.99872 | -0.62228
1196.9688 | 121.9208 | -61.203 | 60.3973 | 0.12643 | 0.019004 | -0.021157 | -0.01586 | 0.017953 | 0.085583 | -0.021514 | 60.3467 | 60.3548 | 60.2872 | 60.2041 | 61.2767 | 61.3189 | 60.9003 | 61.2345 | 61.3294 | 61.222 | 61.1818 | 61.1871 | 61.221 | 61.2886 | 61.1815 | 60.3879 | 60.396 | 60.3284 | 60.2453 | 61.3179 | 61.3601 | 60.9415 | 61.2757 | -0.93003 | -0.55359 | -0.98957 | -0.61312
1198.6562 | 121.8567 | -61.2717 | 60.3561 | 0.12185 | 0.023583 | -0.025735 | -0.011281 | 0.013375 | 0.090161 | -0.021514 | 60.3375 | 60.3593 | 60.2872 | 60.2041 | 61.2767 | 61.3052 | 60.9003 | 61.2345 | 61.3935 | 61.2953 | 61.2459 | 61.2604 | 61.285 | 61.3618 | 61.2502 | 60.3787 | 60.4005 | 60.3284 | 60.2453 | 61.3179 | 61.3464 | 60.9415 | 61.2757 | -0.93919 | -0.56275 | -0.98957 | -0.61312
1200.4062 | 121.8979 | -61.2579 | 60.3607 | 0.12185 | 0.019004 | -0.016578 | -0.011281 | 0.017953 | 0.090161 | -0.021514 | 60.3467 | 60.3639 | 60.2826 | 60.2041 | 61.2721 | 61.3144 | 60.8865 | 61.2345 | 61.3798 | 61.2769 | 61.2414 | 61.2467 | 61.2759 | 61.3481 | 61.2364 | 60.3879 | 60.4051 | 60.3238 | 60.2453 | 61.3133 | 61.3556 | 60.9277 | 61.2757 | -0.92545 | -0.53985 | -0.98957 | -0.60397
1202.1562 | 121.907 | -61.2991 | 60.3378 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | 0.017953 | 0.090161 | -0.021514 | 60.3513 | 60.3639 | 60.2872 | 60.2086 | 61.2676 | 61.3052 | 60.9003 | 61.2299 | 61.421 | 61.3227 | 61.278 | 61.2833 | 61.3171 | 61.3893 | 61.2776 | 60.3925 | 60.4051 | 60.3284 | 60.2498 | 61.3088 | 61.3464 | 60.9415 | 61.2711 | -0.9163 | -0.54901 | -0.98041 | -0.61312
1203.9062 | 121.9254 | -61.1755 | 60.4065 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.03067 | 60.3467 | 60.3593 | 60.2872 | 60.2132 | 61.2721 | 61.3052 | 60.9003 | 61.2253 | 61.2974 | 61.1945 | 61.1544 | 61.1551 | 61.1843 | 61.2565 | 61.1449 | 60.3879 | 60.4005 | 60.3284 | 60.2544 | 61.3133 | 61.3464 | 60.9415 | 61.2665 | -0.92545 | -0.55359 | -0.98499 | -0.61312
1205.6562 | 121.843 | -61.1893 | 60.4614 | 0.11727 | 0.014425 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.026092 | 60.3558 | 60.3639 | 60.2917 | 60.2041 | 61.2721 | 61.2961 | 60.8957 | 61.2299 | 61.3065 | 61.2037 | 61.1727 | 61.1734 | 61.1981 | 61.2703 | 61.1632 | 60.397 | 60.4051 | 60.3329 | 60.2453 | 61.3133 | 61.3373 | 60.9369 | 61.2711 | -0.9163 | -0.53985 | -0.98041 | -0.60397
1207.3906 | 121.8475 | -61.29 | 60.3882 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.016936 | 60.3513 | 60.3639 | 60.2917 | 60.2041 | 61.2676 | 61.2961 | 60.8865 | 61.2253 | 61.4118 | 61.3227 | 61.2688 | 61.2695 | 61.3034 | 61.3756 | 61.273 | 60.3925 | 60.4051 | 60.3329 | 60.2453 | 61.3088 | 61.3373 | 60.9277 | 61.2665 | -0.9163 | -0.53527 | -0.97583 | -0.59481
1209.0938 | 121.9849 | -61.1481 | 60.4477 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.026092 | 60.3558 | 60.3685 | 60.2917 | 60.2086 | 61.2584 | 61.3006 | 60.9049 | 61.2299 | 61.2608 | 61.1717 | 61.1269 | 61.1322 | 61.1569 | 61.2337 | 61.122 | 60.397 | 60.4097 | 60.3329 | 60.2498 | 61.2996 | 61.3418 | 60.9461 | 61.2711 | -0.90256 | -0.54901 | -0.96668 | -0.61312
1210.8438 | 121.9299 | -61.2762 | 60.3424 | 0.12185 | 0.023583 | -0.025735 | -0.01586 | 0.017953 | 0.09474 | -0.021514 | 60.3467 | 60.3685 | 60.2917 | 60.2178 | 61.2721 | 61.3052 | 60.8957 | 61.2253 | 61.3981 | 61.2998 | 61.2505 | 61.2604 | 61.2942 | 61.371 | 61.2547 | 60.3879 | 60.4097 | 60.3329 | 60.259 | 61.3133 | 61.3464 | 60.9369 | 61.2665 | -0.92545 | -0.54901 | -0.98041 | -0.60397
1212.5938 | 121.9986 | -61.1572 | 60.4294 | 0.11727 | 0.023583 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.021514 | 60.3513 | 60.3685 | 60.2917 | 60.2132 | 61.2676 | 61.2961 | 60.8957 | 61.2299 | 61.2745 | 61.1808 | 61.1315 | 61.1414 | 61.1614 | 61.2382 | 61.1357 | 60.3925 | 60.4097 | 60.3329 | 60.2544 | 61.3088 | 61.3373 | 60.9369 | 61.2711 | -0.9163 | -0.54443 | -0.97583 | -0.60397
1214.3438 | 121.9482 | -61.2259 | 60.3653 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 60.3513 | 60.3685 | 60.2963 | 60.2086 | 61.263 | 61.3006 | 60.8865 | 61.2299 | 61.3432 | 61.2495 | 61.2047 | 61.2146 | 61.2301 | 61.3115 | 61.2044 | 60.3925 | 60.4097 | 60.3375 | 60.2498 | 61.3042 | 61.3418 | 60.9277 | 61.2711 | -0.91172 | -0.53527 | -0.96668 | -0.59023
1216.0312 | 121.9757 | -61.2488 | 60.347 | 0.12185 | 0.028162 | -0.021157 | -0.01586 | 0.013375 | 0.090161 | -0.026092 | 60.3558 | 60.3639 | 60.2917 | 60.2132 | 61.2584 | 61.2961 | 60.8865 | 61.2299 | 61.3706 | 61.2769 | 61.2276 | 61.2329 | 61.2622 | 61.3389 | 61.2227 | 60.397 | 60.4051 | 60.3329 | 60.2544 | 61.2996 | 61.3373 | 60.9277 | 61.2711 | -0.90256 | -0.5307 | -0.96668 | -0.59481
1217.7812 | 121.875 | -61.1572 | 60.4935 | 0.11727 | 0.023583 | -0.030314 | -0.01586 | 0.013375 | 0.090161 | -0.026092 | 60.3513 | 60.3685 | 60.2917 | 60.2178 | 61.263 | 61.2961 | 60.8911 | 61.2253 | 61.2745 | 61.1808 | 61.1269 | 61.1414 | 61.1706 | 61.2474 | 61.1311 | 60.3925 | 60.4097 | 60.3329 | 60.259 | 61.3042 | 61.3373 | 60.9323 | 61.2665 | -0.91172 | -0.53985 | -0.97125 | -0.59939
1219.4844 | 121.9757 | -61.1343 | 60.4202 | 0.12643 | 0.019004 | -0.021157 | -0.025017 | 0.008797 | 0.076426 | -0.03067 | 60.3558 | 60.3685 | 60.2917 | 60.2041 | 61.2721 | 61.3052 | 60.8957 | 61.2345 | 61.2608 | 61.1533 | 61.1132 | 61.1093 | 61.1431 | 61.2108 | 61.1037 | 60.397 | 60.4097 | 60.3329 | 60.2453 | 61.3133 | 61.3464 | 60.9369 | 61.2757 | -0.9163 | -0.53985 | -0.98041 | -0.60397
1221.2344 | 121.8613 | -61.2122 | 60.4568 | 0.12643 | 0.019004 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 60.3558 | 60.3685 | 60.2963 | 60.2178 | 61.2721 | 61.3098 | 60.8957 | 61.2345 | 61.3386 | 61.2312 | 61.1956 | 61.1917 | 61.2255 | 61.2932 | 61.1906 | 60.397 | 60.4097 | 60.3375 | 60.259 | 61.3133 | 61.351 | 60.9369 | 61.2757 | -0.9163 | -0.53985 | -0.97583 | -0.59939
1222.9844 | 121.9482 | -61.2625 | 60.3516 | 0.12643 | 0.023583 | -0.025735 | -0.01586 | 0.013375 | 0.081005 | -0.021514 | 60.3467 | 60.3685 | 60.2917 | 60.2041 | 61.2721 | 61.3006 | 60.8957 | 61.2345 | 61.3889 | 61.2861 | 61.2368 | 61.2467 | 61.2759 | 61.3435 | 61.241 | 60.3879 | 60.4097 | 60.3329 | 60.2453 | 61.3133 | 61.3418 | 60.9369 | 61.2757 | -0.92545 | -0.54901 | -0.98041 | -0.60397
1224.7344 | 121.8475 | -61.1893 | 60.466 | 0.11269 | 0.023583 | -0.012 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 60.3513 | 60.3548 | 60.2826 | 60.2132 | 61.2767 | 61.3098 | 60.9049 | 61.2391 | 61.302 | 61.2129 | 61.1773 | 61.1734 | 61.1981 | 61.2703 | 61.1678 | 60.3925 | 60.396 | 60.3238 | 60.2544 | 61.3179 | 61.351 | 60.9461 | 61.2803 | -0.92545 | -0.55359 | -0.99415 | -0.62228
1226.5 | 121.8384 | -61.2122 | 60.4523 | 0.12185 | 0.023583 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.016936 | 60.3467 | 60.3593 | 60.2872 | 60.2086 | 61.2767 | 61.3098 | 60.9049 | 61.2391 | 61.334 | 61.2357 | 61.1956 | 61.1917 | 61.221 | 61.2977 | 61.1952 | 60.3879 | 60.4005 | 60.3284 | 60.2498 | 61.3179 | 61.351 | 60.9461 | 61.2803 | -0.93003 | -0.55817 | -0.98957 | -0.6177
1228.1875 | 121.9482 | -61.1481 | 60.4752 | 0.12185 | 0.014425 | -0.021157 | -0.020438 | 0.004219 | 0.076426 | -0.03067 | 60.3421 | 60.3685 | 60.278 | 60.1995 | 61.2767 | 61.3098 | 60.9049 | 61.2345 | 61.2699 | 61.1625 | 61.1269 | 61.1276 | 61.1523 | 61.2245 | 61.1174 | 60.3833 | 60.4097 | 60.3192 | 60.2407 | 61.3179 | 61.351 | 60.9461 | 61.2757 | -0.93461 | -0.56275 | -0.99872 | -0.62686
1229.9375 | 121.9345 | -61.2076 | 60.3882 | 0.12185 | 0.019004 | -0.025735 | -0.020438 | 0.004219 | 0.090161 | -0.026092 | 60.3467 | 60.3593 | 60.2872 | 60.1995 | 61.2767 | 61.3144 | 60.9003 | 61.2391 | 61.3294 | 61.2266 | 61.1818 | 61.1871 | 61.2118 | 61.2977 | 61.1815 | 60.3879 | 60.4005 | 60.3284 | 60.2407 | 61.3179 | 61.3556 | 60.9415 | 61.2803 | -0.93003 | -0.55359 | -0.98957 | -0.61312
1231.6719 | 121.9757 | -61.1481 | 60.4614 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.016936 | 60.3375 | 60.3548 | 60.2917 | 60.1995 | 61.2721 | 61.3098 | 60.9049 | 61.2345 | 61.2653 | 61.1717 | 61.1269 | 61.1276 | 61.1569 | 61.2337 | 61.1311 | 60.3787 | 60.396 | 60.3329 | 60.2407 | 61.3133 | 61.351 | 60.9461 | 61.2757 | -0.93461 | -0.56732 | -0.98041 | -0.61312
1233.3438 | 121.843 | -61.1893 | 60.4843 | 0.11727 | 0.028162 | -0.025735 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.3421 | 60.3548 | 60.2826 | 60.1949 | 61.2859 | 61.3098 | 60.9094 | 61.2345 | 61.3065 | 61.2174 | 61.1635 | 61.1643 | 61.1981 | 61.2794 | 61.1632 | 60.3833 | 60.396 | 60.3238 | 60.2361 | 61.3271 | 61.351 | 60.9506 | 61.2757 | -0.94377 | -0.56732 | -1.0033 | -0.62686
1235.0938 | 121.8567 | -61.2259 | 60.4614 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.090161 | -0.016936 | 60.3421 | 60.3548 | 60.2826 | 60.2041 | 61.2859 | 61.3189 | 60.9094 | 61.2391 | 61.3432 | 61.2541 | 61.2047 | 61.2055 | 61.2347 | 61.3161 | 61.209 | 60.3833 | 60.396 | 60.3238 | 60.2453 | 61.3271 | 61.3601 | 60.9506 | 61.2803 | -0.94377 | -0.56732 | -1.0033 | -0.62686
1236.7812 | 121.9025 | -61.2167 | 60.3653 | 0.11269 | 0.028162 | -0.012 | -0.020438 | 0.008797 | 0.085583 | -0.03067 | 60.3375 | 60.3456 | 60.2872 | 60.1949 | 61.2813 | 61.3098 | 60.9049 | 61.2482 | 61.3294 | 61.2449 | 61.2047 | 61.1963 | 61.2255 | 61.3023 | 61.1861 | 60.3787 | 60.3868 | 60.3284 | 60.2361 | 61.3225 | 61.351 | 60.9461 | 61.2894 | -0.94377 | -0.56732 | -0.99414 | -0.6177
1238.5469 | 121.8567 | -61.2991 | 60.3333 | 0.11727 | 0.03274 | -0.016578 | -0.020438 | 0.013375 | 0.09474 | -0.021514 | 60.3375 | 60.3548 | 60.278 | 60.1903 | 61.2905 | 61.3144 | 60.9049 | 61.2436 | 61.4164 | 61.3319 | 61.2826 | 61.2787 | 61.3125 | 61.3939 | 61.2776 | 60.3787 | 60.396 | 60.3192 | 60.2315 | 61.3317 | 61.3556 | 60.9461 | 61.2848 | -0.95293 | -0.56732 | -1.0125 | -0.62686
1240.2344 | 121.9482 | -61.2396 | 60.3561 | 0.12185 | 0.023583 | -0.034893 | -0.020438 | 0.004219 | 0.085583 | -0.026092 | 60.3375 | 60.3502 | 60.2734 | 60.1903 | 61.2905 | 61.3144 | 60.9003 | 61.2391 | 61.3615 | 61.2632 | 61.2047 | 61.2192 | 61.2438 | 61.3252 | 61.2135 | 60.3787 | 60.3914 | 60.3146 | 60.2315 | 61.3317 | 61.3556 | 60.9415 | 61.2803 | -0.95293 | -0.56275 | -1.017 | -0.62686
1241.9844 | 121.9711 | -61.1618 | 60.4202 | 0.11727 | 0.019004 | -0.021157 | -0.020438 | 0.013375 | 0.090161 | -0.026092 | 60.333 | 60.341 | 60.2734 | 60.1857 | 61.295 | 61.3189 | 60.9186 | 61.2436 | 61.2791 | 61.1808 | 61.1406 | 61.1414 | 61.1752 | 61.252 | 61.1357 | 60.3742 | 60.3822 | 60.3146 | 60.2269 | 61.3362 | 61.3601 | 60.9598 | 61.2848 | -0.96208 | -0.58564 | -1.0216 | -0.64517
1243.7344 | 121.8521 | -61.235 | 60.4797 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.021514 | 60.3375 | 60.3502 | 60.278 | 60.1903 | 61.2813 | 61.3144 | 60.914 | 61.2482 | 61.3569 | 61.254 | 61.2139 | 61.2146 | 61.2484 | 61.3206 | 61.2135 | 60.3787 | 60.3914 | 60.3192 | 60.2315 | 61.3225 | 61.3556 | 60.9552 | 61.2894 | -0.94377 | -0.57648 | -1.0033 | -0.63601
1245.4219 | 121.8475 | -61.2808 | 60.3516 | 0.11727 | 0.03274 | -0.016578 | -0.01586 | 0.008797 | 0.076426 | -0.016936 | 60.3284 | 60.3456 | 60.2734 | 60.1949 | 61.2767 | 61.3235 | 60.9094 | 61.2436 | 61.3981 | 61.3136 | 61.2642 | 61.265 | 61.2896 | 61.3572 | 61.2639 | 60.3696 | 60.3868 | 60.3146 | 60.2361 | 61.3179 | 61.3647 | 60.9506 | 61.2848 | -0.94835 | -0.58106 | -1.0033 | -0.63601
1247.1719 | 121.8384 | -61.3083 | 60.3653 | 0.11269 | 0.028162 | -0.012 | -0.020438 | 0.017953 | 0.081005 | -0.016936 | 60.3375 | 60.3502 | 60.2734 | 60.1903 | 61.295 | 61.3281 | 60.9094 | 61.2528 | 61.421 | 61.3365 | 61.2963 | 61.2879 | 61.3262 | 61.3893 | 61.2914 | 60.3787 | 60.3914 | 60.3146 | 60.2315 | 61.3362 | 61.3693 | 60.9506 | 61.294 | -0.9575 | -0.5719 | -1.0216 | -0.63601
1248.9219 | 121.9345 | -61.235 | 60.3699 | 0.11727 | 0.028162 | -0.030314 | -0.025017 | 0.013375 | 0.085583 | -0.03067 | 60.333 | 60.3456 | 60.2688 | 60.1812 | 61.2859 | 61.3189 | 60.914 | 61.2528 | 61.3523 | 61.2632 | 61.2047 | 61.21 | 61.2484 | 61.3206 | 61.2044 | 60.3742 | 60.3868 | 60.31 | 60.2224 | 61.3271 | 61.3601 | 60.9552 | 61.294 | -0.95293 | -0.58106 | -1.017 | -0.64517
1250.6719 | 121.8155 | -61.3129 | 60.3561 | 0.12643 | 0.03274 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.021514 | 60.333 | 60.3456 | 60.2688 | 60.1903 | 61.2905 | 61.3189 | 60.9049 | 61.2528 | 61.4393 | 61.3456 | 61.2963 | 61.297 | 61.3217 | 61.403 | 61.2914 | 60.3742 | 60.3868 | 60.31 | 60.2315 | 61.3317 | 61.3601 | 60.9461 | 61.294 | -0.9575 | -0.5719 | -1.0216 | -0.63601
1252.3594 | 121.8887 | -61.2625 | 60.3928 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.013375 | 0.085583 | -0.021514 | 60.3238 | 60.341 | 60.2734 | 60.1857 | 61.2996 | 61.3327 | 60.9186 | 61.2528 | 61.3798 | 61.2907 | 61.2459 | 61.2467 | 61.2759 | 61.3481 | 61.241 | 60.365 | 60.3822 | 60.3146 | 60.2269 | 61.3408 | 61.3739 | 60.9598 | 61.294 | -0.97582 | -0.59479 | -1.0262 | -0.64517
1254.1094 | 121.8887 | -61.1893 | 60.4477 | 0.11727 | 0.03274 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.021514 | 60.3192 | 60.341 | 60.2688 | 60.1812 | 61.2996 | 61.3327 | 60.9232 | 61.2528 | 61.3065 | 61.222 | 61.1681 | 61.1734 | 61.1935 | 61.2794 | 61.1678 | 60.3604 | 60.3822 | 60.31 | 60.2224 | 61.3408 | 61.3739 | 60.9644 | 61.294 | -0.9804 | -0.60395 | -1.0308 | -0.65433
1255.7969 | 121.8613 | -61.2213 | 60.4385 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | 0.017953 | 0.085583 | -0.021514 | 60.3238 | 60.341 | 60.2597 | 60.1857 | 61.295 | 61.3327 | 60.9278 | 61.2482 | 61.3432 | 61.2495 | 61.2047 | 61.2009 | 61.2393 | 61.3069 | 61.1998 | 60.365 | 60.3822 | 60.3009 | 60.2269 | 61.3362 | 61.3739 | 60.9689 | 61.2894 | -0.97124 | -0.60395 | -1.0354 | -0.66806
1257.5469 | 121.9711 | -61.2579 | 60.2829 | 0.11269 | 0.028162 | -0.021157 | -0.025017 | 0.013375 | 0.090161 | -0.026092 | 60.3284 | 60.341 | 60.2597 | 60.172 | 61.3042 | 61.3281 | 60.914 | 61.2574 | 61.3706 | 61.2861 | 61.2368 | 61.2329 | 61.2713 | 61.3481 | 61.2318 | 60.3696 | 60.3822 | 60.3009 | 60.2132 | 61.3454 | 61.3693 | 60.9552 | 61.2986 | -0.97582 | -0.58564 | -1.0445 | -0.65433
1259.2344 | 121.8796 | -61.2808 | 60.3607 | 0.11727 | 0.03274 | -0.012 | -0.025017 | 0.017953 | 0.09474 | -0.016936 | 60.333 | 60.3365 | 60.2688 | 60.1812 | 61.2996 | 61.3235 | 60.9232 | 61.2528 | 61.3981 | 61.3136 | 61.2688 | 61.2558 | 61.2988 | 61.3756 | 61.2639 | 60.3742 | 60.3776 | 60.31 | 60.2224 | 61.3408 | 61.3647 | 60.9644 | 61.294 | -0.96666 | -0.59022 | -1.0308 | -0.65433
1260.9844 | 121.8933 | -61.2488 | 60.379 | 0.12185 | 0.03274 | -0.012 | -0.020438 | 0.017953 | 0.09474 | -0.012357 | 60.3238 | 60.3365 | 60.2688 | 60.1766 | 61.2996 | 61.3373 | 60.9232 | 61.2619 | 61.3706 | 61.2815 | 61.2368 | 61.2283 | 61.2667 | 61.3435 | 61.2364 | 60.365 | 60.3776 | 60.31 | 60.2178 | 61.3408 | 61.3785 | 60.9644 | 61.3031 | -0.97582 | -0.59937 | -1.0308 | -0.65433
1262.7344 | 121.9437 | -61.2534 | 60.3195 | 0.11269 | 0.03274 | -0.021157 | -0.029595 | 0.013375 | 0.085583 | -0.021514 | 60.3101 | 60.3181 | 60.2505 | 60.1629 | 61.3179 | 61.3418 | 60.9369 | 61.2665 | 61.3661 | 61.2861 | 61.2322 | 61.2238 | 61.2667 | 61.3389 | 61.2318 | 60.3513 | 60.3593 | 60.2917 | 60.2041 | 61.3591 | 61.383 | 60.9781 | 61.3077 | -1.0079 | -0.62684 | -1.0674 | -0.68638
1264.4219 | 121.8613 | -61.2579 | 60.4019 | 0.12185 | 0.037319 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 60.3009 | 60.3273 | 60.2414 | 60.1629 | 61.3042 | 61.3464 | 60.9369 | 61.2803 | 61.3798 | 61.2953 | 61.2414 | 61.2421 | 61.2667 | 61.3389 | 61.2364 | 60.3421 | 60.3685 | 60.2826 | 60.2041 | 61.3454 | 61.3876 | 60.9781 | 61.3215 | -1.0033 | -0.636 | -1.0628 | -0.69553
1266.1875 | 121.9574 | -61.2076 | 60.3882 | 0.11727 | 0.03274 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.026092 | 60.3101 | 60.3227 | 60.2505 | 60.1674 | 61.3133 | 61.3418 | 60.9461 | 61.2757 | 61.3249 | 61.2403 | 61.191 | 61.1826 | 61.2164 | 61.2932 | 61.1815 | 60.3513 | 60.3639 | 60.2917 | 60.2086 | 61.3545 | 61.383 | 60.9873 | 61.3169 | -1.0033 | -0.636 | -1.0628 | -0.69553
1267.9375 | 121.9574 | -61.1984 | 60.4019 | 0.12185 | 0.028162 | -0.021157 | -0.025017 | 0.004219 | 0.090161 | -0.021514 | 60.2963 | 60.3227 | 60.2414 | 60.1491 | 61.3271 | 61.3556 | 60.9506 | 61.2848 | 61.3203 | 61.2266 | 61.1773 | 61.1734 | 61.2026 | 61.2886 | 61.1769 | 60.3375 | 60.3639 | 60.2826 | 60.1903 | 61.3683 | 61.3968 | 60.9918 | 61.326 | -1.0308 | -0.65431 | -1.0857 | -0.70927
1269.6875 | 121.8567 | -61.2534 | 60.4477 | 0.11727 | 0.028162 | -0.025735 | -0.020438 | 0.013375 | 0.085583 | -0.021514 | 60.2963 | 60.309 | 60.2368 | 60.1583 | 61.3317 | 61.3647 | 60.9552 | 61.2894 | 61.3706 | 61.2815 | 61.2276 | 61.2329 | 61.2667 | 61.3389 | 61.2318 | 60.3375 | 60.3502 | 60.278 | 60.1995 | 61.3729 | 61.4059 | 60.9964 | 61.3306 | -1.0353 | -0.65889 | -1.0949 | -0.71842
1271.375 | 121.9025 | -61.2259 | 60.3516 | 0.12185 | 0.037319 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.026092 | 60.3055 | 60.309 | 60.2414 | 60.1445 | 61.3362 | 61.3693 | 60.9506 | 61.2986 | 61.3477 | 61.2632 | 61.2047 | 61.2009 | 61.2393 | 61.3069 | 61.1998 | 60.3467 | 60.3502 | 60.2826 | 60.1857 | 61.3774 | 61.4105 | 60.9918 | 61.3398 | -1.0308 | -0.64516 | -1.0949 | -0.70927
1273.125 | 121.9391 | -61.2488 | 60.3745 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.026092 | 60.2963 | 60.3044 | 60.2276 | 60.1491 | 61.3362 | 61.3647 | 60.9552 | 61.2986 | 61.3706 | 61.2724 | 61.2276 | 61.2238 | 61.2576 | 61.3344 | 61.2227 | 60.3375 | 60.3456 | 60.2688 | 60.1903 | 61.3774 | 61.4059 | 60.9964 | 61.3398 | -1.0399 | -0.65889 | -1.1086 | -0.72758
1274.875 | 121.9116 | -61.2213 | 60.3836 | 0.11727 | 0.037319 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.026092 | 60.2917 | 60.2998 | 60.2276 | 60.14 | 61.3362 | 61.3739 | 60.9735 | 61.2986 | 61.3386 | 61.2586 | 61.2002 | 61.2009 | 61.2347 | 61.3069 | 61.1952 | 60.3329 | 60.341 | 60.2688 | 60.1812 | 61.3774 | 61.4151 | 61.0147 | 61.3398 | -1.0445 | -0.68178 | -1.1086 | -0.74589
1276.5625 | 121.962 | -61.2213 | 60.3836 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.2689 | 60.2998 | 60.2231 | 60.1445 | 61.3408 | 61.3785 | 60.969 | 61.3031 | 61.3432 | 61.2541 | 61.2002 | 61.1963 | 61.2301 | 61.3115 | 61.1952 | 60.3101 | 60.341 | 60.2643 | 60.1857 | 61.382 | 61.4197 | 61.0102 | 61.3443 | -1.072 | -0.7001 | -1.1178 | -0.74589
1278.2969 | 121.8979 | -61.29 | 60.3287 | 0.11727 | 0.03274 | -0.012 | -0.020438 | 0.022531 | 0.090161 | -0.026092 | 60.278 | 60.2952 | 60.2276 | 60.14 | 61.35 | 61.3785 | 60.969 | 61.3031 | 61.4073 | 61.3227 | 61.278 | 61.2695 | 61.3125 | 61.3801 | 61.2639 | 60.3192 | 60.3364 | 60.2688 | 60.1812 | 61.3912 | 61.4197 | 61.0102 | 61.3443 | -1.072 | -0.69094 | -1.1223 | -0.74132
1280.0469 | 121.907 | -61.3174 | 60.3241 | 0.11727 | 0.03274 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.016936 | 60.2734 | 60.2952 | 60.2231 | 60.14 | 61.35 | 61.3739 | 60.9644 | 61.3077 | 61.4347 | 61.3502 | 61.2963 | 61.297 | 61.3308 | 61.403 | 61.3005 | 60.3146 | 60.3364 | 60.2643 | 60.1812 | 61.3912 | 61.4151 | 61.0056 | 61.3489 | -1.0765 | -0.69094 | -1.1269 | -0.74132
1281.7969 | 121.9803 | -61.2305 | 60.3333 | 0.11269 | 0.037319 | -0.030314 | -0.025017 | 0.008797 | 0.081005 | -0.026092 | 60.2826 | 60.2815 | 60.2093 | 60.1354 | 61.35 | 61.383 | 60.9781 | 61.3077 | 61.3432 | 61.2678 | 61.2002 | 61.2055 | 61.2393 | 61.3115 | 61.2044 | 60.3238 | 60.3227 | 60.2505 | 60.1766 | 61.3912 | 61.4242 | 61.0193 | 61.3489 | -1.0674 | -0.69552 | -1.1406 | -0.76879
1283.5625 | 121.8796 | -61.3678 | 60.2783 | 0.11269 | 0.03274 | -0.021157 | -0.01586 | 0.017953 | 0.076426 | -0.016936 | 60.2689 | 60.2769 | 60.2093 | 60.1262 | 61.3591 | 61.383 | 60.969 | 61.3077 | 61.4805 | 61.4005 | 61.3466 | 61.3519 | 61.3858 | 61.4442 | 61.3509 | 60.3101 | 60.3181 | 60.2505 | 60.1674 | 61.4003 | 61.4242 | 61.0102 | 61.3489 | -1.0903 | -0.7001 | -1.1498 | -0.75963
1285.25 | 121.9803 | -61.2946 | 60.2509 | 0.11727 | 0.023583 | -0.016578 | -0.025017 | 0.004219 | 0.081005 | -0.021514 | 60.2643 | 60.2815 | 60.2093 | 60.1171 | 61.3591 | 61.3968 | 60.9735 | 61.3169 | 61.4118 | 61.3181 | 61.278 | 61.2695 | 61.2988 | 61.3756 | 61.273 | 60.3055 | 60.3227 | 60.2505 | 60.1583 | 61.4003 | 61.438 | 61.0147 | 61.3581 | -1.0949 | -0.70926 | -1.1498 | -0.76421
1287 | 121.8658 | -61.2946 | 60.3836 | 0.12643 | 0.03274 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.03067 | 60.2643 | 60.2769 | 60.2002 | 60.1171 | 61.3637 | 61.3922 | 60.9873 | 61.3169 | 61.421 | 61.3273 | 61.2734 | 61.2695 | 61.3034 | 61.3756 | 61.2639 | 60.3055 | 60.3181 | 60.2414 | 60.1583 | 61.4049 | 61.4334 | 61.0285 | 61.3581 | -1.0994 | -0.72299 | -1.1635 | -0.7871
1288.6719 | 121.9254 | -61.29 | 60.3149 | 0.11727 | 0.028162 | -0.016578 | -0.025017 | 0.008797 | 0.081005 | -0.026092 | 60.2689 | 60.2723 | 60.2047 | 60.1079 | 61.3591 | 61.4014 | 60.9827 | 61.3215 | 61.4073 | 61.3181 | 61.2734 | 61.265 | 61.2988 | 61.371 | 61.2639 | 60.3101 | 60.3135 | 60.2459 | 60.1491 | 61.4003 | 61.4425 | 61.0239 | 61.3627 | -1.0903 | -0.71383 | -1.1544 | -0.77794
1290.4219 | 121.875 | -61.29 | 60.3653 | 0.11727 | 0.03274 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.021514 | 60.2597 | 60.2723 | 60.2047 | 60.1171 | 61.3683 | 61.3968 | 60.9873 | 61.3306 | 61.4073 | 61.3227 | 61.2688 | 61.265 | 61.3034 | 61.371 | 61.2685 | 60.3009 | 60.3135 | 60.2459 | 60.1583 | 61.4095 | 61.438 | 61.0285 | 61.3718 | -1.1086 | -0.72757 | -1.1635 | -0.78252
1292.1094 | 121.8887 | -61.2579 | 60.3607 | 0.11269 | 0.03274 | -0.012 | -0.020438 | 0.013375 | 0.076426 | -0.016936 | 60.2505 | 60.2723 | 60.2047 | 60.1125 | 61.3683 | 61.3968 | 60.9918 | 61.326 | 61.3706 | 61.2907 | 61.2459 | 61.2375 | 61.2713 | 61.3344 | 61.241 | 60.2917 | 60.3135 | 60.2459 | 60.1537 | 61.4095 | 61.438 | 61.033 | 61.3672 | -1.1177 | -0.7413 | -1.1635 | -0.7871
1293.8594 | 121.9803 | -61.2717 | 60.3195 | 0.11269 | 0.03274 | -0.016578 | -0.020438 | 0.004219 | 0.081005 | -0.03067 | 60.2551 | 60.2632 | 60.191 | 60.1033 | 61.3683 | 61.4059 | 60.9964 | 61.326 | 61.3844 | 61.3044 | 61.2551 | 61.2512 | 61.2759 | 61.3527 | 61.241 | 60.2963 | 60.3044 | 60.2322 | 60.1445 | 61.4095 | 61.4471 | 61.0376 | 61.3672 | -1.1132 | -0.7413 | -1.1773 | -0.80541
1295.6094 | 121.9894 | -61.2213 | 60.3561 | 0.11269 | 0.03274 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.026092 | 60.2551 | 60.2632 | 60.1956 | 60.1079 | 61.3774 | 61.4059 | 61.001 | 61.3398 | 61.334 | 61.2541 | 61.2047 | 61.2009 | 61.2347 | 61.3023 | 61.1952 | 60.2963 | 60.3044 | 60.2368 | 60.1491 | 61.4186 | 61.4471 | 61.0422 | 61.381 | -1.1223 | -0.74588 | -1.1819 | -0.80541
1297.2812 | 121.8658 | -61.409 | 60.2463 | 0.12185 | 0.037319 | -0.025735 | -0.011281 | 0.008797 | 0.090161 | -0.021514 | 60.2551 | 60.2632 | 60.1864 | 60.0987 | 61.382 | 61.4105 | 60.9873 | 61.3398 | 61.5308 | 61.4463 | 61.3833 | 61.3977 | 61.4178 | 61.4992 | 61.3875 | 60.2963 | 60.3044 | 60.2276 | 60.1399 | 61.4232 | 61.4517 | 61.0285 | 61.381 | -1.1269 | -0.73215 | -1.1956 | -0.80083
1299.0469 | 121.9574 | -61.3449 | 60.2051 | 0.11727 | 0.03274 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 60.246 | 60.2586 | 60.1864 | 60.0942 | 61.382 | 61.4151 | 61.0147 | 61.3398 | 61.4622 | 61.3776 | 61.3238 | 61.329 | 61.3537 | 61.4305 | 61.3234 | 60.2872 | 60.2998 | 60.2276 | 60.1354 | 61.4232 | 61.4563 | 61.0559 | 61.381 | -1.1361 | -0.76877 | -1.1956 | -0.8283
1300.8125 | 121.8292 | -61.3953 | 60.2966 | 0.11727 | 0.03274 | -0.012 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 60.246 | 60.254 | 60.1819 | 60.0896 | 61.3866 | 61.4105 | 61.0147 | 61.3443 | 61.5125 | 61.428 | 61.3833 | 61.3748 | 61.4041 | 61.4854 | 61.3738 | 60.2872 | 60.2952 | 60.2231 | 60.1308 | 61.4278 | 61.4517 | 61.0559 | 61.3855 | -1.1406 | -0.76877 | -1.2047 | -0.83288
1302.5625 | 121.875 | -61.3541 | 60.2783 | 0.12643 | 0.041898 | -0.025735 | -0.01586 | 0.013375 | 0.081005 | -0.021514 | 60.2414 | 60.2495 | 60.1819 | 60.0896 | 61.3866 | 61.4197 | 61.0193 | 61.3443 | 61.4805 | 61.396 | 61.3283 | 61.3382 | 61.3674 | 61.4351 | 61.3326 | 60.2826 | 60.2907 | 60.2231 | 60.1308 | 61.4278 | 61.4609 | 61.0605 | 61.3855 | -1.1452 | -0.77793 | -1.2047 | -0.83746
1304.25 | 121.9666 | -61.2625 | 60.3241 | 0.11727 | 0.03274 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.021514 | 60.2368 | 60.2586 | 60.1727 | 60.085 | 61.382 | 61.4197 | 61.0147 | 61.3535 | 61.3798 | 61.2953 | 61.2414 | 61.2375 | 61.2759 | 61.3435 | 61.241 | 60.278 | 60.2998 | 60.2139 | 60.1262 | 61.4232 | 61.4609 | 61.0559 | 61.3947 | -1.1452 | -0.77793 | -1.2093 | -0.84204
1306 | 121.9254 | -61.3632 | 60.2325 | 0.11727 | 0.03274 | -0.025735 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 60.2231 | 60.2403 | 60.1819 | 60.0896 | 61.3912 | 61.4197 | 61.0147 | 61.3443 | 61.4805 | 61.396 | 61.3375 | 61.3428 | 61.3766 | 61.4442 | 61.3417 | 60.2643 | 60.2815 | 60.2231 | 60.1308 | 61.4324 | 61.4609 | 61.0559 | 61.3855 | -1.1681 | -0.79167 | -1.2093 | -0.83288
1307.75 | 121.9803 | -61.2717 | 60.3104 | 0.11727 | 0.03274 | -0.016578 | -0.020438 | 0.004219 | 0.076426 | -0.026092 | 60.2322 | 60.2449 | 60.1635 | 60.0804 | 61.4003 | 61.4334 | 61.0239 | 61.3535 | 61.3889 | 61.3044 | 61.2551 | 61.2512 | 61.2759 | 61.3481 | 61.2456 | 60.2734 | 60.2861 | 60.2047 | 60.1216 | 61.4415 | 61.4746 | 61.0651 | 61.3947 | -1.1681 | -0.79167 | -1.2368 | -0.86035
1309.5 | 121.9482 | -61.3861 | 60.2097 | 0.11269 | 0.03274 | -0.016578 | -0.020438 | 0.013375 | 0.090161 | -0.021514 | 60.2276 | 60.2403 | 60.159 | 60.0759 | 61.3958 | 61.4334 | 61.0147 | 61.3581 | 61.4988 | 61.4188 | 61.3695 | 61.3657 | 61.3995 | 61.4763 | 61.3646 | 60.2688 | 60.2815 | 60.2002 | 60.117 | 61.437 | 61.4746 | 61.0559 | 61.3993 | -1.1681 | -0.78709 | -1.2368 | -0.85577
1311.1875 | 121.9711 | -61.3678 | 60.2509 | 0.12185 | 0.03274 | -0.016578 | -0.025017 | 0.013375 | 0.076426 | -0.026092 | 60.2368 | 60.2311 | 60.1727 | 60.0804 | 61.4003 | 61.4334 | 61.0102 | 61.3535 | 61.4896 | 61.4005 | 61.3512 | 61.3428 | 61.3812 | 61.4442 | 61.3417 | 60.278 | 60.2723 | 60.2139 | 60.1216 | 61.4415 | 61.4746 | 61.0514 | 61.3947 | -1.1635 | -0.77335 | -1.2276 | -0.83746
1312.9375 | 121.9254 | -61.2808 | 60.3378 | 0.11269 | 0.037319 | -0.016578 | -0.025017 | 0.004219 | 0.081005 | -0.03067 | 60.2276 | 60.2449 | 60.1681 | 60.0942 | 61.3912 | 61.4242 | 61.0239 | 61.3535 | 61.3935 | 61.3181 | 61.2642 | 61.2558 | 61.285 | 61.3618 | 61.2502 | 60.2688 | 60.2861 | 60.2093 | 60.1354 | 61.4324 | 61.4654 | 61.0651 | 61.3947 | -1.1635 | -0.79625 | -1.2231 | -0.85577
1314.625 | 121.907 | -61.3358 | 60.2829 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.085583 | -0.016936 | 60.2322 | 60.2449 | 60.1681 | 60.085 | 61.3958 | 61.4334 | 61.0239 | 61.3535 | 61.453 | 61.3639 | 61.3146 | 61.3153 | 61.34 | 61.4213 | 61.3188 | 60.2734 | 60.2861 | 60.2093 | 60.1262 | 61.437 | 61.4746 | 61.0651 | 61.3947 | -1.1635 | -0.79167 | -1.2276 | -0.85577
1316.375 | 121.962 | -61.2854 | 60.3058 | 0.12643 | 0.03274 | -0.025735 | -0.020438 | 0.008797 | 0.085583 | -0.026092 | 60.2276 | 60.2311 | 60.1681 | 60.0804 | 61.3958 | 61.4334 | 61.0147 | 61.3627 | 61.4118 | 61.3181 | 61.2597 | 61.265 | 61.2942 | 61.371 | 61.2593 | 60.2688 | 60.2723 | 60.2093 | 60.1216 | 61.437 | 61.4746 | 61.0559 | 61.4039 | -1.1681 | -0.78709 | -1.2276 | -0.84662
1318.125 | 121.9666 | -61.3495 | 60.228 | 0.12185 | 0.037319 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.021514 | 60.2231 | 60.2403 | 60.159 | 60.0759 | 61.4049 | 61.4334 | 61.0193 | 61.3627 | 61.4713 | 61.3868 | 61.3283 | 61.3199 | 61.3583 | 61.4351 | 61.328 | 60.2643 | 60.2815 | 60.2002 | 60.117 | 61.4461 | 61.4746 | 61.0605 | 61.4039 | -1.1818 | -0.79625 | -1.2459 | -0.86035
1319.8594 | 121.9803 | -61.2854 | 60.3012 | 0.13101 | 0.037319 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.016936 | 60.2322 | 60.2357 | 60.159 | 60.085 | 61.4003 | 61.4288 | 61.0193 | 61.3718 | 61.4164 | 61.3227 | 61.2642 | 61.2604 | 61.2988 | 61.3664 | 61.2685 | 60.2734 | 60.2769 | 60.2002 | 60.1262 | 61.4415 | 61.47 | 61.0605 | 61.413 | -1.1681 | -0.78709 | -1.2414 | -0.86035
1321.5469 | 121.8658 | -61.3083 | 60.3607 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | 0.013375 | 0.076426 | -0.021514 | 60.2322 | 60.2449 | 60.1727 | 60.085 | 61.3958 | 61.4242 | 61.0239 | 61.3581 | 61.4301 | 61.341 | 61.2871 | 61.2924 | 61.3217 | 61.3847 | 61.2868 | 60.2734 | 60.2861 | 60.2139 | 60.1262 | 61.437 | 61.4654 | 61.0651 | 61.3993 | -1.1635 | -0.79167 | -1.2231 | -0.8512
1323.2969 | 122.0078 | -61.2762 | 60.3058 | 0.11269 | 0.03274 | -0.021157 | -0.025017 | 0.008797 | 0.076426 | -0.03067 | 60.2368 | 60.2495 | 60.1727 | 60.0896 | 61.3958 | 61.4242 | 61.0147 | 61.3489 | 61.3889 | 61.309 | 61.2551 | 61.2512 | 61.285 | 61.3527 | 61.2456 | 60.278 | 60.2907 | 60.2139 | 60.1308 | 61.437 | 61.4654 | 61.0559 | 61.3901 | -1.159 | -0.77793 | -1.2231 | -0.84204
1325.0312 | 121.8933 | -61.3586 | 60.2646 | 0.11727 | 0.03274 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.026092 | 60.2368 | 60.254 | 60.1819 | 60.0896 | 61.3912 | 61.4242 | 61.0056 | 61.3489 | 61.4759 | 61.3914 | 61.3421 | 61.3336 | 61.3674 | 61.4488 | 61.3326 | 60.278 | 60.2952 | 60.2231 | 60.1308 | 61.4324 | 61.4654 | 61.0468 | 61.3901 | -1.1544 | -0.76877 | -1.2093 | -0.82372
1326.7812 | 121.9528 | -61.2946 | 60.3149 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | 0.004219 | 0.081005 | -0.021514 | 60.2368 | 60.2449 | 60.1773 | 60.0896 | 61.3912 | 61.4242 | 61.0147 | 61.3535 | 61.4164 | 61.3273 | 61.2734 | 61.2695 | 61.2988 | 61.3756 | 61.273 | 60.278 | 60.2861 | 60.2185 | 60.1308 | 61.4324 | 61.4654 | 61.0559 | 61.3947 | -1.1544 | -0.77793 | -1.2139 | -0.83746
1328.5469 | 121.8842 | -61.3861 | 60.2921 | 0.12185 | 0.037319 | -0.016578 | -0.020438 | 0.013375 | 0.076426 | -0.016936 | 60.2322 | 60.254 | 60.191 | 60.0942 | 61.382 | 61.4197 | 61.0102 | 61.3489 | 61.508 | 61.4234 | 61.3695 | 61.3657 | 61.3995 | 61.4625 | 61.3692 | 60.2734 | 60.2952 | 60.2322 | 60.1354 | 61.4232 | 61.4609 | 61.0514 | 61.3901 | -1.1498 | -0.77793 | -1.191 | -0.81915
1330.2344 | 121.9391 | -61.29 | 60.2783 | 0.11269 | 0.03274 | -0.016578 | -0.025017 | 0.004219 | 0.081005 | -0.021514 | 60.2368 | 60.2586 | 60.1819 | 60.0942 | 61.3866 | 61.4151 | 61.0056 | 61.3398 | 61.4027 | 61.3227 | 61.2734 | 61.265 | 61.2942 | 61.371 | 61.2685 | 60.278 | 60.2998 | 60.2231 | 60.1354 | 61.4278 | 61.4563 | 61.0468 | 61.381 | -1.1498 | -0.76877 | -1.2047 | -0.82372
1331.9844 | 121.8338 | -61.3815 | 60.26 | 0.12643 | 0.03274 | -0.012 | -0.020438 | 0.013375 | 0.085583 | -0.016936 | 60.2414 | 60.2586 | 60.191 | 60.0987 | 61.3866 | 61.4197 | 61.0056 | 61.3443 | 61.508 | 61.4143 | 61.3695 | 61.3611 | 61.3949 | 61.4671 | 61.3646 | 60.2826 | 60.2998 | 60.2322 | 60.1399 | 61.4278 | 61.4609 | 61.0468 | 61.3855 | -1.1452 | -0.7642 | -1.1956 | -0.81457
1333.6719 | 121.875 | -61.3174 | 60.347 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 60.2368 | 60.2586 | 60.1773 | 60.0896 | 61.3866 | 61.4242 | 61.0147 | 61.3352 | 61.4393 | 61.3502 | 61.2963 | 61.297 | 61.3262 | 61.3984 | 61.2959 | 60.278 | 60.2998 | 60.2185 | 60.1308 | 61.4278 | 61.4654 | 61.0559 | 61.3764 | -1.1498 | -0.77793 | -1.2093 | -0.83746
1335.4219 | 121.843 | -61.3129 | 60.3653 | 0.12643 | 0.037319 | -0.016578 | -0.025017 | 0.008797 | 0.081005 | -0.026092 | 60.2368 | 60.2495 | 60.1773 | 60.0942 | 61.3866 | 61.4151 | 61.0102 | 61.3489 | 61.4393 | 61.3502 | 61.2963 | 61.2878 | 61.3217 | 61.3939 | 61.2868 | 60.278 | 60.2907 | 60.2185 | 60.1354 | 61.4278 | 61.4563 | 61.0514 | 61.3901 | -1.1498 | -0.77335 | -1.2093 | -0.83288
1337.1875 | 121.9803 | -61.2305 | 60.3424 | 0.12185 | 0.028162 | -0.021157 | -0.029595 | 0.004219 | 0.071848 | -0.026092 | 60.2414 | 60.2495 | 60.1864 | 60.085 | 61.3912 | 61.4197 | 61.0193 | 61.3535 | 61.3523 | 61.2586 | 61.2093 | 61.2009 | 61.2347 | 61.3023 | 61.2044 | 60.2826 | 60.2907 | 60.2276 | 60.1262 | 61.4324 | 61.4609 | 61.0605 | 61.3947 | -1.1498 | -0.77793 | -1.2047 | -0.83288
1338.9688 | 121.9803 | -61.3586 | 60.2417 | 0.12643 | 0.037319 | -0.021157 | -0.029595 | 0.013375 | 0.081005 | -0.016936 | 60.2276 | 60.2495 | 60.1681 | 60.085 | 61.3912 | 61.4288 | 61.0147 | 61.3489 | 61.4851 | 61.396 | 61.3375 | 61.329 | 61.372 | 61.4396 | 61.3417 | 60.2688 | 60.2907 | 60.2093 | 60.1262 | 61.4324 | 61.47 | 61.0559 | 61.3901 | -1.1635 | -0.78709 | -1.2231 | -0.84662
1340.7188 | 121.9025 | -61.3678 | 60.2646 | 0.12185 | 0.037319 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.012357 | 60.2276 | 60.2311 | 60.1727 | 60.085 | 61.3958 | 61.4242 | 61.0193 | 61.3581 | 61.4896 | 61.4051 | 61.3466 | 61.3474 | 61.3812 | 61.4534 | 61.3554 | 60.2688 | 60.2723 | 60.2139 | 60.1262 | 61.437 | 61.4654 | 61.0605 | 61.3993 | -1.1681 | -0.79167 | -1.2231 | -0.84662
1342.4062 | 121.8658 | -61.4044 | 60.2692 | 0.12643 | 0.041898 | -0.016578 | -0.020438 | 0.017953 | 0.090161 | -0.021514 | 60.2185 | 60.2266 | 60.1635 | 60.0759 | 61.4049 | 61.438 | 61.0285 | 61.3581 | 61.5308 | 61.4463 | 61.3878 | 61.384 | 61.4224 | 61.4946 | 61.3829 | 60.2597 | 60.2678 | 60.2047 | 60.117 | 61.4461 | 61.4792 | 61.0697 | 61.3993 | -1.1864 | -0.80998 | -1.2414 | -0.86493
1344.1562 | 121.962 | -61.2946 | 60.3058 | 0.11269 | 0.03274 | -0.025735 | -0.020438 | 0.013375 | 0.085583 | -0.03067 | 60.2139 | 60.2311 | 60.159 | 60.0713 | 61.4141 | 61.4471 | 61.0376 | 61.3672 | 61.4072 | 61.3273 | 61.2688 | 61.2741 | 61.3079 | 61.3801 | 61.2639 | 60.2551 | 60.2723 | 60.2002 | 60.1125 | 61.4553 | 61.4883 | 61.0788 | 61.4084 | -1.2002 | -0.82372 | -1.2551 | -0.87867
1345.9062 | 121.8521 | -61.4227 | 60.2646 | 0.12185 | 0.028162 | -0.021157 | -0.01586 | 0.017953 | 0.081005 | -0.026092 | 60.2139 | 60.222 | 60.1544 | 60.0667 | 61.4186 | 61.4609 | 61.0331 | 61.3718 | 61.5446 | 61.4509 | 61.4016 | 61.4069 | 61.4407 | 61.5037 | 61.3966 | 60.2551 | 60.2632 | 60.1956 | 60.1079 | 61.4598 | 61.5021 | 61.0743 | 61.413 | -1.2047 | -0.81914 | -1.2643 | -0.87867
1347.6562 | 121.8292 | -61.4456 | 60.2188 | 0.11727 | 0.03274 | -0.012 | -0.020438 | 0.017953 | 0.081005 | -0.026092 | 60.2093 | 60.222 | 60.1452 | 60.053 | 61.4232 | 61.4609 | 61.0468 | 61.381 | 61.5629 | 61.4784 | 61.4336 | 61.4252 | 61.4636 | 61.5266 | 61.4195 | 60.2505 | 60.2632 | 60.1864 | 60.0942 | 61.4644 | 61.5021 | 61.088 | 61.4222 | -1.2139 | -0.83745 | -1.278 | -0.90156
1349.3438 | 121.9803 | -61.2991 | 60.3012 | 0.11727 | 0.03274 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.021514 | 60.2048 | 60.2174 | 60.1407 | 60.0621 | 61.4232 | 61.4609 | 61.0514 | 61.3856 | 61.4164 | 61.3319 | 61.278 | 61.2787 | 61.3034 | 61.3801 | 61.2776 | 60.246 | 60.2586 | 60.1819 | 60.1033 | 61.4644 | 61.5021 | 61.0926 | 61.4268 | -1.2185 | -0.84661 | -1.2826 | -0.91071
1351.1094 | 121.9391 | -61.3586 | 60.2463 | 0.12185 | 0.037319 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 60.1956 | 60.2037 | 60.1361 | 60.0438 | 61.437 | 61.4654 | 61.0468 | 61.3947 | 61.4805 | 61.396 | 61.3421 | 61.3382 | 61.3674 | 61.4396 | 61.3417 | 60.2368 | 60.2449 | 60.1773 | 60.085 | 61.4782 | 61.5066 | 61.088 | 61.4359 | -1.2414 | -0.85119 | -1.3009 | -0.91071
1352.8594 | 121.9666 | -61.3953 | 60.1501 | 0.12185 | 0.03274 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.021514 | 60.1819 | 60.2037 | 60.1269 | 60.0438 | 61.437 | 61.47 | 61.0605 | 61.3993 | 61.5171 | 61.428 | 61.3741 | 61.3702 | 61.4041 | 61.4763 | 61.3738 | 60.2231 | 60.2449 | 60.1681 | 60.085 | 61.4782 | 61.5112 | 61.1017 | 61.4405 | -1.2551 | -0.87866 | -1.31 | -0.93361
1354.6094 | 121.8475 | -61.4639 | 60.2188 | 0.11727 | 0.037319 | -0.012 | -0.020438 | 0.017953 | 0.085583 | -0.021514 | 60.1864 | 60.1945 | 60.1269 | 60.0346 | 61.4415 | 61.4746 | 61.0651 | 61.413 | 61.5812 | 61.5012 | 61.4519 | 61.4435 | 61.4819 | 61.5495 | 61.4424 | 60.2276 | 60.2357 | 60.1681 | 60.0758 | 61.4827 | 61.5158 | 61.1063 | 61.4542 | -1.2551 | -0.87866 | -1.3146 | -0.93819
1356.2969 | 121.8933 | -61.4273 | 60.2371 | 0.12185 | 0.037319 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.021514 | 60.1773 | 60.1808 | 60.1223 | 60.0346 | 61.4553 | 61.4883 | 61.0743 | 61.413 | 61.5492 | 61.4646 | 61.4016 | 61.4114 | 61.4269 | 61.5129 | 61.4058 | 60.2185 | 60.222 | 60.1635 | 60.0758 | 61.4965 | 61.5295 | 61.1155 | 61.4542 | -1.278 | -0.89697 | -1.3329 | -0.95192
1358.0469 | 121.9482 | -61.409 | 60.1822 | 0.11727 | 0.03274 | -0.016578 | -0.025017 | 0.017953 | 0.081005 | -0.016936 | 60.1727 | 60.1899 | 60.1086 | 60.0346 | 61.4553 | 61.4838 | 61.0743 | 61.4176 | 61.5263 | 61.4417 | 61.3924 | 61.384 | 61.4269 | 61.49 | 61.3921 | 60.2139 | 60.2311 | 60.1498 | 60.0758 | 61.4965 | 61.525 | 61.1155 | 61.4588 | -1.2826 | -0.90155 | -1.3467 | -0.96565
1359.7969 | 121.8521 | -61.4548 | 60.1959 | 0.11727 | 0.037319 | -0.021157 | -0.020438 | 0.013375 | 0.090161 | -0.026092 | 60.1681 | 60.1854 | 60.1132 | 60.0301 | 61.4507 | 61.4838 | 61.0788 | 61.413 | 61.572 | 61.4921 | 61.4336 | 61.4343 | 61.4681 | 61.5449 | 61.4287 | 60.2093 | 60.2265 | 60.1544 | 60.0713 | 61.4919 | 61.525 | 61.12 | 61.4542 | -1.2826 | -0.91071 | -1.3375 | -0.96565
1361.5625 | 121.8613 | -61.3815 | 60.2646 | 0.11727 | 0.03274 | -0.016578 | -0.025017 | 0.004219 | 0.090161 | -0.021514 | 60.1636 | 60.1716 | 60.104 | 60.0163 | 61.469 | 61.5021 | 61.0926 | 61.4222 | 61.4988 | 61.4143 | 61.365 | 61.3565 | 61.3858 | 61.4717 | 61.36 | 60.2047 | 60.2128 | 60.1452 | 60.0575 | 61.5102 | 61.5433 | 61.1338 | 61.4634 | -1.3055 | -0.92902 | -1.365 | -0.98855
1363.25 | 121.9894 | -61.3861 | 60.2097 | 0.12643 | 0.03274 | -0.021157 | -0.025017 | 0.008797 | 0.076426 | -0.021514 | 60.1452 | 60.1625 | 60.0857 | 59.998 | 61.4827 | 61.5158 | 61.1063 | 61.4451 | 61.5125 | 61.4188 | 61.365 | 61.3611 | 61.3949 | 61.4625 | 61.3646 | 60.1864 | 60.2037 | 60.1269 | 60.0392 | 61.5239 | 61.557 | 61.1475 | 61.4863 | -1.3375 | -0.96107 | -1.397 | -1.0206
1364.9844 | 121.843 | -61.5051 | 60.1776 | 0.12185 | 0.028162 | -0.007421 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 60.0537 | 60.0709 | 59.9987 | 59.9156 | 61.5697 | 61.5982 | 61.1979 | 61.5321 | 61.627 | 61.5333 | 61.4977 | 61.4847 | 61.5139 | 61.5907 | 61.4836 | 60.0949 | 60.1121 | 60.0399 | 59.9568 | 61.6109 | 61.6394 | 61.2391 | 61.5733 | -1.5161 | -1.1442 | -1.571 | -1.1992
1366.7344 | 121.8475 | -62.3062 | 59.3491 | 0.11269 | 0.03274 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.016936 | 59.4997 | 59.4619 | 59.4448 | 59.3524 | 62.0001 | 62.1567 | 61.7473 | 62.0769 | 62.4189 | 62.339 | 62.2896 | 62.2858 | 62.315 | 62.3918 | 62.2893 | 59.5409 | 59.5031 | 59.486 | 59.3936 | 62.0413 | 62.1979 | 61.7885 | 62.1181 | -2.5004 | -2.2476 | -2.5553 | -2.3025
1368.4844 | 121.9849 | -62.8784 | 58.7448 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | 0.004219 | 0.081005 | -0.026092 | 59.4081 | 59.3566 | 59.3578 | 59.2654 | 62.142 | 62.2574 | 61.8526 | 62.173 | 63.0003 | 62.902 | 62.8573 | 62.8534 | 62.8826 | 62.9594 | 62.8523 | 59.4493 | 59.3978 | 59.399 | 59.3066 | 62.1832 | 62.2986 | 61.8938 | 62.2142 | -2.7339 | -2.4445 | -2.7842 | -2.4948
1370.1719 | 121.9482 | -62.1689 | 59.4452 | 0.11269 | 0.028162 | -0.016578 | -0.01586 | 0.017953 | 0.076426 | -0.021514 | 59.4127 | 59.3703 | 59.3578 | 59.2654 | 62.1237 | 62.2437 | 61.8297 | 62.173 | 62.2816 | 62.197 | 62.1523 | 62.153 | 62.1868 | 62.2453 | 62.1474 | 59.4539 | 59.4115 | 59.399 | 59.3066 | 62.1649 | 62.2849 | 61.8709 | 62.2142 | -2.711 | -2.417 | -2.7659 | -2.4719
1371.9219 | 121.8887 | -62.0041 | 59.6558 | 0.11727 | 0.023583 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.026092 | 59.5409 | 59.4985 | 59.4905 | 59.3936 | 62.0138 | 62.1155 | 61.7107 | 62.0402 | 62.1214 | 62.0277 | 61.9829 | 61.9791 | 62.0129 | 62.0851 | 61.978 | 59.5821 | 59.5397 | 59.5317 | 59.4348 | 62.055 | 62.1567 | 61.7519 | 62.0814 | -2.4729 | -2.1698 | -2.5233 | -2.2201
1373.6719 | 121.8979 | -62.0087 | 59.6649 | 0.11727 | 0.028162 | -0.021157 | -0.025017 | 0.017953 | 0.081005 | -0.016936 | 59.6233 | 59.5809 | 59.5592 | 59.4714 | 61.9314 | 62.0423 | 61.6282 | 61.967 | 62.1259 | 62.0368 | 61.9875 | 61.9837 | 62.0266 | 62.0897 | 61.9917 | 59.6645 | 59.6221 | 59.6004 | 59.5126 | 61.9726 | 62.0835 | 61.6694 | 62.0082 | -2.3081 | -2.005 | -2.3722 | -2.069
1375.3594 | 121.9711 | -62.0041 | 59.5688 | 0.12643 | 0.028162 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.021514 | 59.5821 | 59.526 | 59.5272 | 59.4348 | 61.9635 | 62.0835 | 61.6603 | 62.0082 | 62.1305 | 62.0323 | 61.9829 | 61.9745 | 62.0129 | 62.0897 | 61.9826 | 59.6233 | 59.5672 | 59.5684 | 59.476 | 62.0046 | 62.1247 | 61.7015 | 62.0494 | -2.3814 | -2.0782 | -2.4363 | -2.1331
1377.125 | 121.8979 | -62.1094 | 59.5322 | 0.11269 | 0.028162 | -0.012 | -0.020438 | 0.008797 | 0.090161 | -0.021514 | 59.518 | 59.4665 | 59.4585 | 59.3707 | 62.023 | 62.1476 | 61.729 | 62.0723 | 62.2221 | 62.1375 | 62.0974 | 62.0889 | 62.1182 | 62.1995 | 62.0879 | 59.5592 | 59.5077 | 59.4997 | 59.4119 | 62.0642 | 62.1888 | 61.7702 | 62.1135 | -2.505 | -2.211 | -2.5645 | -2.2705
1378.8594 | 121.8475 | -62.2055 | 59.4589 | 0.11727 | 0.028162 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.012357 | 59.4401 | 59.3932 | 59.3852 | 59.2928 | 62.1191 | 62.23 | 61.8068 | 62.1547 | 62.3228 | 62.2337 | 62.1889 | 62.1851 | 62.2189 | 62.2865 | 62.1931 | 59.4813 | 59.4344 | 59.4264 | 59.334 | 62.1603 | 62.2712 | 61.848 | 62.1959 | -2.679 | -2.3667 | -2.7339 | -2.4216
1380.625 | 121.9757 | -62.1506 | 59.4452 | 0.12185 | 0.028162 | -0.021157 | -0.029595 | 0.004219 | 0.076426 | -0.021514 | 59.2753 | 59.2421 | 59.2158 | 59.128 | 62.2748 | 62.3902 | 61.9762 | 62.3103 | 62.2724 | 62.1787 | 62.1294 | 62.121 | 62.1548 | 62.227 | 62.1291 | 59.3165 | 59.2833 | 59.257 | 59.1692 | 62.316 | 62.4314 | 62.0174 | 62.3515 | -2.9994 | -2.7009 | -3.0589 | -2.7604
1382.3125 | 121.9391 | -62.2925 | 59.3124 | 0.11269 | 0.023583 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.026092 | 59.3028 | 59.2559 | 59.2387 | 59.1509 | 62.2519 | 62.3582 | 61.9487 | 62.2875 | 62.4052 | 62.3161 | 62.2713 | 62.2629 | 62.3013 | 62.3781 | 62.2664 | 59.344 | 59.297 | 59.2799 | 59.1921 | 62.2931 | 62.3994 | 61.9899 | 62.3287 | -2.9491 | -2.6459 | -3.0131 | -2.71
1384.0625 | 121.9666 | -62.4023 | 59.1934 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.016936 | 59.1975 | 59.146 | 59.1426 | 59.0501 | 62.3709 | 62.468 | 62.0495 | 62.3973 | 62.5242 | 62.4213 | 62.3812 | 62.3819 | 62.4066 | 62.4833 | 62.3854 | 59.2387 | 59.1872 | 59.1838 | 59.0913 | 62.4121 | 62.5092 | 62.0907 | 62.4385 | -3.1734 | -2.852 | -3.2283 | -2.9069
1385.8125 | 121.8475 | -62.5305 | 59.1751 | 0.12185 | 0.03274 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 59.0968 | 59.0452 | 59.0327 | 58.9494 | 62.4716 | 62.5688 | 62.1593 | 62.498 | 62.6524 | 62.5633 | 62.5139 | 62.5101 | 62.5393 | 62.6115 | 62.509 | 59.138 | 59.0864 | 59.0739 | 58.9906 | 62.5128 | 62.61 | 62.2005 | 62.5392 | -3.3749 | -3.0626 | -3.4389 | -3.1266
1387.4844 | 121.962 | -64.5035 | 57.0923 | 0.11727 | 0.028162 | -0.021157 | -0.029595 | 0.008797 | 0.076426 | -0.03067 | 57.9888 | 57.96 | 57.9522 | 57.855 | 63.5704 | 63.6538 | 63.2719 | 63.5739 | 64.6208 | 64.5316 | 64.4823 | 64.4739 | 64.5123 | 64.5799 | 64.4728 | 58.03 | 58.0012 | 57.9934 | 57.8962 | 63.6116 | 63.695 | 63.3131 | 63.6151 | -5.5816 | -5.2831 | -5.6182 | -5.3197
1389.25 | 121.9574 | -62.677 | 58.905 | 0.11269 | 0.023583 | -0.021157 | -0.029595 | 0.008797 | 0.081005 | -0.026092 | 58.8175 | 58.7888 | 58.7672 | 58.6792 | 62.7372 | 62.8343 | 62.434 | 62.7682 | 62.7897 | 62.7006 | 62.6558 | 62.6474 | 62.6858 | 62.758 | 62.6509 | 58.8587 | 58.83 | 58.8084 | 58.7204 | 62.7784 | 62.8755 | 62.4752 | 62.8094 | -3.9197 | -3.6166 | -3.97 | -3.6669
1391 | 121.9666 | -62.6678 | 58.9417 | 0.12185 | 0.019004 | -0.016578 | -0.025017 | 0.008797 | 0.081005 | -0.016936 | 58.6343 | 58.5919 | 58.5611 | 58.4823 | 62.9249 | 63.0357 | 62.6309 | 62.9604 | 62.7897 | 62.6869 | 62.6513 | 62.6428 | 62.6766 | 62.7489 | 62.6509 | 58.6755 | 58.6331 | 58.6023 | 58.5235 | 62.9661 | 63.0769 | 62.6721 | 63.0016 | -4.2905 | -3.9966 | -4.3637 | -4.0698
1392.7031 | 121.8567 | -63.2172 | 58.4564 | 0.12185 | 0.028162 | -0.016578 | -0.025017 | 0.004219 | 0.085583 | -0.016936 | 58.3459 | 58.3035 | 58.2819 | 58.2076 | 63.2133 | 63.3104 | 62.9056 | 63.2443 | 63.339 | 63.2453 | 63.2006 | 63.1921 | 63.2214 | 63.3027 | 63.2002 | 58.3871 | 58.3447 | 58.3231 | 58.2488 | 63.2545 | 63.3516 | 62.9468 | 63.2855 | -4.8674 | -4.5597 | -4.9314 | -4.6237
1394.4531 | 121.994 | -63.1302 | 58.4518 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.076426 | -0.026092 | 58.3825 | 58.3309 | 58.3139 | 58.2305 | 63.1858 | 63.2784 | 62.8644 | 63.2122 | 63.2475 | 63.1538 | 63.109 | 63.1097 | 63.139 | 63.2066 | 63.1041 | 58.4237 | 58.3721 | 58.3551 | 58.2717 | 63.227 | 63.3196 | 62.9056 | 63.2534 | -4.8033 | -4.4819 | -4.8719 | -4.5505
1396.2031 | 121.875 | -63.3545 | 58.2458 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.016936 | 58.2131 | 58.1707 | 58.1491 | 58.0748 | 63.3369 | 63.4569 | 63.0338 | 63.3725 | 63.4763 | 63.3827 | 63.3379 | 63.3341 | 63.3679 | 63.4355 | 63.3376 | 58.2543 | 58.2119 | 58.1903 | 58.116 | 63.3781 | 63.4981 | 63.075 | 63.4137 | -5.1238 | -4.8207 | -5.1878 | -4.8847
1397.9688 | 121.843 | -65.5884 | 56.0669 | 0.12185 | 0.023583 | -0.021157 | -0.029595 | 0.013375 | 0.081005 | -0.03067 | 56.4412 | 56.4032 | 56.4231 | 56.3348 | 65.1911 | 65.2195 | 64.8926 | 65.1259 | 65.7102 | 65.612 | 65.5672 | 65.5588 | 65.6018 | 65.6694 | 65.5577 | 56.4824 | 56.4444 | 56.4643 | 56.376 | 65.2323 | 65.2607 | 64.9338 | 65.1671 | -8.7498 | -8.4514 | -8.768 | -8.4695
1399.6562 | 121.8796 | -63.7848 | 57.8888 | 0.12643 | 0.019004 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.016936 | 57.7186 | 57.6853 | 57.6684 | 57.5803 | 63.8863 | 63.9468 | 63.5374 | 63.8669 | 63.9112 | 63.8038 | 63.7728 | 63.7598 | 63.7936 | 63.8704 | 63.7679 | 57.7598 | 57.7265 | 57.7096 | 57.6215 | 63.9275 | 63.988 | 63.5786 | 63.9081 | -6.1676 | -5.8188 | -6.2179 | -5.8691
1401.4062 | 121.8613 | -63.8809 | 57.7744 | 0.12643 | 0.028162 | -0.021157 | -0.025017 | 0.017953 | 0.085583 | -0.026092 | 56.1986 | 56.1789 | 56.1484 | 56.0738 | 65.4291 | 65.4621 | 65.1216 | 65.3869 | 64.0073 | 63.9091 | 63.8598 | 63.8559 | 63.8989 | 63.9665 | 63.8548 | 56.2398 | 56.2201 | 56.1896 | 56.115 | 65.4703 | 65.5033 | 65.1628 | 65.4281 | -9.2306 | -8.923 | -9.2807 | -8.9732
1403.1094 | 121.9666 | -70.079 | 51.4664 | 0.11269 | 0.019004 | -0.030314 | -0.029595 | -0.000359 | 0.071848 | -0.026092 | 55.7316 | 55.6981 | 55.6906 | 55.5976 | 65.8412 | 65.9291 | 65.529 | 65.6616 | 70.1917 | 70.098 | 70.0487 | 70.0494 | 70.0787 | 70.1509 | 70.0529 | 55.7728 | 55.7393 | 55.7318 | 55.6388 | 65.8824 | 65.9703 | 65.5702 | 65.7028 | -10.1096 | -9.7975 | -10.1506 | -9.8385
1404.8125 | 121.9849 | -64.2105 | 57.399 | 0.11727 | 0.014425 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 56.2718 | 56.2567 | 56.2216 | 56.147 | 65.3055 | 65.3843 | 65.0162 | 65.3182 | 64.3278 | 64.2249 | 64.1894 | 64.1901 | 64.2193 | 64.2961 | 64.189 | 56.313 | 56.2979 | 56.2628 | 56.1882 | 65.3467 | 65.4255 | 65.0574 | 65.3594 | -9.0337 | -8.7444 | -9.0839 | -8.7946
1406.5625 | 121.9208 | -71.2784 | 50.3036 | 0.11727 | 0.023583 | -0.025735 | -0.034174 | -0.000359 | 0.071848 | -0.026092 | 55.2234 | 55.1761 | 55.2098 | 55.0939 | 66.4043 | 66.4281 | 66.0922 | 66.3437 | 71.3957 | 71.302 | 71.2526 | 71.2442 | 71.278 | 71.3502 | 71.2523 | 55.2646 | 55.2173 | 55.251 | 55.1351 | 66.4455 | 66.4693 | 66.1334 | 66.3849 | -11.1809 | -10.8688 | -11.1944 | -10.8823
1408.3125 | 121.875 | -66.5039 | 55.2017 | 0.12643 | 0.023583 | -0.016578 | -0.029595 | 0.004219 | 0.081005 | -0.021514 | 55.5072 | 55.4829 | 55.4571 | 55.3732 | 66.0655 | 66.1488 | 65.7808 | 66.0782 | 66.6303 | 66.5275 | 66.4873 | 66.4743 | 66.5081 | 66.5849 | 66.4824 | 55.5484 | 55.5241 | 55.4983 | 55.4144 | 66.1067 | 66.19 | 65.822 | 66.1194 | -10.5583 | -10.2736 | -10.6084 | -10.3238
1409.9844 | 121.9437 | -66.4627 | 55.1285 | 0.12185 | 0.019004 | -0.021157 | -0.029595 | 0.008797 | 0.076426 | -0.021514 | 54.8021 | 54.7686 | 54.7612 | 54.6818 | 66.7751 | 66.8584 | 66.463 | 66.7741 | 66.5846 | 66.4817 | 66.4416 | 66.4331 | 66.4715 | 66.5391 | 66.4412 | 54.8433 | 54.8098 | 54.8024 | 54.7229 | 66.8163 | 66.8996 | 66.5042 | 66.8153 | -11.973 | -11.6609 | -12.0139 | -11.7018
1411.7344 | 121.8842 | -66.5863 | 55.0735 | 0.12185 | 0.023583 | -0.016578 | -0.029595 | 0.008797 | 0.085583 | -0.021514 | 54.9761 | 54.9518 | 54.9443 | 54.8512 | 66.6149 | 66.6753 | 66.3074 | 66.4444 | 66.7082 | 66.6099 | 66.5697 | 66.5567 | 66.5951 | 66.6719 | 66.5648 | 55.0173 | 54.993 | 54.9855 | 54.8924 | 66.6561 | 66.7165 | 66.3486 | 66.4856 | -11.6388 | -11.3312 | -11.6706 | -11.3631
1413.4375 | 121.9391 | -67.6071 | 53.9795 | 0.12185 | 0.019004 | -0.030314 | -0.025017 | 0.008797 | 0.081005 | -0.012357 | 55.7728 | 55.7439 | 55.718 | 55.6342 | 65.7725 | 65.8879 | 65.4832 | 65.6249 | 67.729 | 67.6261 | 67.5768 | 67.5821 | 67.6159 | 67.6881 | 67.5948 | 55.814 | 55.7851 | 55.7592 | 55.6754 | 65.8137 | 65.9291 | 65.5244 | 65.6661 | -9.9997 | -9.7105 | -10.0545 | -9.7652
1415.1875 | 121.8567 | -66.4124 | 55.2887 | 0.12185 | 0.028162 | -0.016578 | -0.025017 | 0.013375 | 0.090161 | -0.026092 | 55.1409 | 55.112 | 55.0817 | 54.9931 | 66.4226 | 66.515 | 66.1105 | 66.2476 | 66.5342 | 66.4405 | 66.3958 | 66.3873 | 66.4257 | 66.5025 | 66.3863 | 55.1821 | 55.1532 | 55.1229 | 55.0343 | 66.4638 | 66.5562 | 66.1517 | 66.2888 | -11.2816 | -10.9695 | -11.3409 | -11.0288
1416.9375 | 121.9482 | -66.5817 | 54.9911 | 0.11727 | 0.019004 | -0.016578 | -0.029595 | 0.004219 | 0.090161 | -0.021514 | 54.6419 | 54.6084 | 54.5872 | 54.5032 | 66.9949 | 67.0232 | 66.6187 | 66.7558 | 66.699 | 66.6007 | 66.5651 | 66.5521 | 66.5859 | 66.6719 | 66.5602 | 54.6831 | 54.6495 | 54.6284 | 54.5444 | 67.0361 | 67.0644 | 66.6599 | 66.7969 | -12.353 | -11.9768 | -12.4077 | -12.0315
1418.6875 | 121.8613 | -66.6595 | 55.0049 | 0.12185 | 0.03274 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 54.5137 | 54.4847 | 54.459 | 54.375 | 67.004 | 67.1514 | 66.8018 | 66.9663 | 66.7814 | 66.6923 | 66.643 | 66.6391 | 66.6683 | 66.7406 | 66.6426 | 54.5549 | 54.5259 | 54.5002 | 54.4162 | 67.0452 | 67.1926 | 66.843 | 67.0075 | -12.4903 | -12.2881 | -12.545 | -12.3428
1420.3906 | 121.8292 | -68.1839 | 53.4714 | 0.12643 | 0.028162 | -0.016578 | -0.025017 | 0.017953 | 0.090161 | -0.021514 | 53.1539 | 53.1386 | 53.1084 | 53.0287 | 68.3637 | 68.4882 | 68.0792 | 68.2345 | 68.3103 | 68.2121 | 68.1673 | 68.1589 | 68.2019 | 68.2741 | 68.1624 | 53.1951 | 53.1797 | 53.1496 | 53.0699 | 68.4049 | 68.5294 | 68.1204 | 68.2757 | -15.2099 | -14.9253 | -15.2553 | -14.9708
1422.1406 | 121.8384 | -68.1015 | 53.5629 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.017953 | 0.081005 | -0.026092 | 53.4286 | 53.4133 | 53.3785 | 53.2989 | 68.1211 | 68.2181 | 67.8091 | 67.9461 | 68.2234 | 68.1205 | 68.0803 | 68.0811 | 68.1195 | 68.1825 | 68.0754 | 53.4698 | 53.4545 | 53.4197 | 53.3401 | 68.1623 | 68.2593 | 67.8503 | 67.9873 | -14.6925 | -14.3805 | -14.7426 | -14.4305
1423.8281 | 121.962 | -69.5297 | 52.0203 | 0.12185 | 0.019004 | -0.012 | -0.025017 | 0.004219 | 0.085583 | -0.026092 | 51.9818 | 51.9481 | 51.9318 | 51.8473 | 69.5632 | 69.6785 | 69.265 | 69.3928 | 69.6516 | 69.5487 | 69.5177 | 69.5047 | 69.5339 | 69.6153 | 69.5036 | 52.023 | 51.9893 | 51.973 | 51.8885 | 69.6044 | 69.7197 | 69.3062 | 69.434 | -17.5814 | -17.2832 | -17.6314 | -17.3332
1425.5781 | 121.907 | -69.9188 | 51.7044 | 0.11727 | 0.028162 | -0.016578 | -0.025017 | 0.013375 | 0.090161 | -0.016936 | 51.6613 | 51.6138 | 51.6022 | 51.5085 | 69.902 | 70.0035 | 69.5946 | 69.7361 | 70.0361 | 69.947 | 69.9022 | 69.8938 | 69.9322 | 70.009 | 69.9019 | 51.7025 | 51.655 | 51.6434 | 51.5497 | 69.9432 | 70.0447 | 69.6358 | 69.7773 | -18.2407 | -17.9334 | -18.2998 | -17.9925
1427.2656 | 121.8384 | -70.2209 | 51.4343 | 0.11727 | 0.028162 | -0.012 | -0.025017 | 0.008797 | 0.081005 | -0.016936 | 51.2492 | 51.22 | 51.1855 | 51.1101 | 70.2911 | 70.4018 | 70.0021 | 70.1528 | 70.3382 | 70.2491 | 70.2089 | 70.1959 | 70.2297 | 70.302 | 70.204 | 51.2904 | 51.2612 | 51.2267 | 51.1513 | 70.3323 | 70.443 | 70.0433 | 70.194 | -19.0419 | -18.7529 | -19.1056 | -18.8166
1429.0156 | 121.9254 | -70.5231 | 51.0635 | 0.10812 | 0.023583 | -0.016578 | -0.029595 | 0.008797 | 0.076426 | -0.026092 | 51.1164 | 51.0735 | 51.0573 | 50.9727 | 70.4468 | 70.5437 | 70.144 | 70.2764 | 70.6312 | 70.5467 | 70.5065 | 70.4935 | 70.5319 | 70.5995 | 70.497 | 51.1576 | 51.1147 | 51.0985 | 51.0139 | 70.488 | 70.5849 | 70.1852 | 70.3176 | -19.3304 | -19.0276 | -19.3895 | -19.0867
1430.7031 | 121.9803 | -71.0678 | 50.5142 | 0.12185 | 0.019004 | -0.021157 | -0.025017 | 0.008797 | 0.076426 | -0.021514 | 50.4022 | 50.3729 | 50.3523 | 50.263 | 71.1564 | 71.2488 | 70.84 | 70.9814 | 71.1897 | 71.0868 | 71.0467 | 71.0428 | 71.0766 | 71.1442 | 71.0463 | 50.4434 | 50.4141 | 50.3935 | 50.3042 | 71.1976 | 71.29 | 70.8812 | 71.0226 | -20.7542 | -20.4378 | -20.8041 | -20.4877
1432.4531 | 121.9482 | -72.5464 | 49.0448 | 0.11727 | 0.019004 | -0.025735 | -0.029595 | 0.013375 | 0.076426 | -0.021514 | 48.905 | 48.9398 | 48.846 | 48.7656 | 72.6718 | 72.7412 | 72.3371 | 72.4785 | 72.6637 | 72.5654 | 72.5207 | 72.5168 | 72.5598 | 72.6228 | 72.5249 | 48.9462 | 48.981 | 48.8872 | 48.8068 | 72.713 | 72.7824 | 72.3783 | 72.5197 | -23.7668 | -23.4321 | -23.8258 | -23.4911
1434.1875 | 121.8384 | -71.2234 | 50.4639 | 0.12185 | 0.023583 | -0.016578 | -0.025017 | 0.013375 | 0.076426 | -0.021514 | 50.3518 | 50.3684 | 50.2973 | 50.2035 | 71.2068 | 71.3083 | 70.8949 | 71.0363 | 71.3453 | 71.247 | 71.2069 | 71.1984 | 71.2368 | 71.2999 | 71.2019 | 50.393 | 50.4096 | 50.3385 | 50.2447 | 71.248 | 71.3495 | 70.9361 | 71.0775 | -20.8549 | -20.5431 | -20.9094 | -20.5976
1435.9375 | 121.8887 | -71.9421 | 49.7177 | 0.12185 | 0.028162 | -0.007421 | -0.025017 | 0.013375 | 0.076426 | -0.021514 | 50.1595 | 50.1761 | 50.1142 | 50.0157 | 71.4128 | 71.496 | 71.1055 | 71.2469 | 72.064 | 71.9703 | 71.9347 | 71.9171 | 71.9555 | 72.0186 | 71.9206 | 50.2007 | 50.2173 | 50.1554 | 50.0569 | 71.454 | 71.5372 | 71.1467 | 71.2881 | -21.2533 | -20.946 | -21.2986 | -20.9913
1437.7031 | 121.8613 | -71.4249 | 50.2121 | 0.12185 | 0.023583 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.021514 | 50.187 | 50.2081 | 50.1234 | 50.0478 | 71.3808 | 71.4731 | 71.0735 | 71.2057 | 71.5467 | 71.4484 | 71.4129 | 71.3998 | 71.4337 | 71.5104 | 71.4034 | 50.2282 | 50.2493 | 50.1646 | 50.089 | 71.422 | 71.5143 | 71.1147 | 71.2469 | -21.1937 | -20.8864 | -21.2574 | -20.9501
1439.3906 | 121.843 | -71.4523 | 50.2121 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | 0.008797 | 0.085583 | -0.016936 | 50.2923 | 50.3134 | 50.2333 | 50.1439 | 71.2663 | 71.3678 | 70.9727 | 71.105 | 71.5742 | 71.4759 | 71.4312 | 71.4273 | 71.4611 | 71.5379 | 71.4354 | 50.3335 | 50.3546 | 50.2745 | 50.1851 | 71.3075 | 71.409 | 71.0139 | 71.1462 | -20.974 | -20.6804 | -21.033 | -20.7395
1441.1406 | 121.8658 | -72.5784 | 49.0768 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | 0.017953 | 0.090161 | -0.021514 | 48.9417 | 48.9581 | 48.8827 | 48.7977 | 72.6123 | 72.7183 | 72.3005 | 72.6387 | 72.7003 | 72.6066 | 72.5619 | 72.558 | 72.5964 | 72.6686 | 72.5569 | 48.9829 | 48.9993 | 48.9239 | 48.8389 | 72.6535 | 72.7595 | 72.3417 | 72.6799 | -23.6706 | -23.3588 | -23.7296 | -23.4178
1442.8438 | 121.9437 | -72.8165 | 48.7518 | 0.11727 | 0.028162 | -0.016578 | -0.034174 | 0.008797 | 0.081005 | -0.021514 | 48.5067 | 48.5231 | 48.4386 | 48.3581 | 73.0472 | 73.1532 | 72.7308 | 73.0736 | 72.9337 | 72.8446 | 72.7999 | 72.7823 | 72.8253 | 72.8975 | 72.795 | 48.5479 | 48.5643 | 48.4798 | 48.3993 | 73.0884 | 73.1944 | 72.772 | 73.1148 | -24.5405 | -24.2241 | -24.6086 | -24.2923
1444.6094 | 121.9757 | -72.7844 | 48.8113 | 0.10812 | 0.028162 | -0.016578 | -0.020438 | 0.008797 | 0.076426 | -0.016936 | 48.5845 | 48.6009 | 48.5164 | 48.4268 | 72.9923 | 73.0846 | 72.6667 | 73.0095 | 72.8925 | 72.8126 | 72.7678 | 72.764 | 72.7932 | 72.8608 | 72.7675 | 48.6257 | 48.6421 | 48.5576 | 48.468 | 73.0335 | 73.1258 | 72.7079 | 73.0507 | -24.4077 | -24.0822 | -24.4759 | -24.1503
1446.3594 | 121.8567 | -73.1003 | 48.5596 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.026092 | 48.3007 | 48.3354 | 48.2509 | 48.1749 | 73.2486 | 73.3455 | 72.9369 | 73.2659 | 73.2221 | 73.1284 | 73.0837 | 73.0844 | 73.1091 | 73.1904 | 73.0742 | 48.3419 | 48.3766 | 48.2921 | 48.2161 | 73.2898 | 73.3867 | 72.9781 | 73.3071 | -24.948 | -24.6362 | -24.9978 | -24.686
1448.0469 | 121.9757 | -73.8007 | 47.7859 | 0.12185 | 0.019004 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.026092 | 47.8428 | 47.8683 | 47.7839 | 47.7033 | 73.7202 | 73.8125 | 73.3947 | 73.7375 | 73.9225 | 73.8197 | 73.7841 | 73.7802 | 73.814 | 73.8862 | 73.7746 | 47.884 | 47.9095 | 47.8251 | 47.7445 | 73.7614 | 73.8537 | 73.4359 | 73.7787 | -25.8774 | -25.5519 | -25.9363 | -25.6108
1449.7812 | 121.9208 | -74.1531 | 47.4426 | 0.12185 | 0.023583 | -0.021157 | -0.029595 | 0.008797 | 0.085583 | -0.021514 | 47.4628 | 47.4746 | 47.3947 | 47.3187 | 74.0956 | 74.2016 | 73.7747 | 74.1129 | 74.275 | 74.1767 | 74.132 | 74.1235 | 74.1619 | 74.2387 | 74.1316 | 47.504 | 47.5158 | 47.4359 | 47.3599 | 74.1368 | 74.2428 | 73.8159 | 74.1541 | -26.6328 | -26.3119 | -26.7009 | -26.38
1451.5312 | 121.9757 | -74.8077 | 46.756 | 0.11269 | 0.023583 | -0.016578 | -0.029595 | 0.004219 | 0.076426 | -0.03067 | 46.8264 | 46.8564 | 46.7767 | 46.6913 | 74.7228 | 74.8242 | 74.4065 | 74.7401 | 74.9204 | 74.8313 | 74.7912 | 74.7781 | 74.812 | 74.8842 | 74.7771 | 46.8676 | 46.8976 | 46.8178 | 46.7325 | 74.764 | 74.8654 | 74.4477 | 74.7813 | -27.8964 | -27.5801 | -27.9462 | -27.6299
1453.2344 | 121.8292 | -75.9567 | 45.694 | 0.11727 | 0.028162 | -0.025735 | -0.020438 | 0.017953 | 0.076426 | -0.021514 | 45.7276 | 45.7529 | 45.6824 | 45.597 | 75.8216 | 75.923 | 75.5099 | 75.8434 | 76.074 | 75.9849 | 75.931 | 75.9363 | 75.9747 | 76.0332 | 75.9352 | 45.7688 | 45.7941 | 45.7236 | 45.6382 | 75.8628 | 75.9642 | 75.5511 | 75.8846 | -30.094 | -29.7824 | -30.1391 | -29.8275
1454.9844 | 121.9437 | -76.0483 | 45.5521 | 0.12185 | 0.023583 | -0.021157 | -0.029595 | 0.004219 | 0.081005 | -0.021514 | 45.4208 | 45.4553 | 45.3757 | 45.2902 | 76.1283 | 76.2205 | 75.8121 | 76.1456 | 76.1701 | 76.0719 | 76.0271 | 76.0187 | 76.0525 | 76.1293 | 76.0268 | 45.462 | 45.4965 | 45.4169 | 45.3314 | 76.1695 | 76.2617 | 75.8533 | 76.1868 | -30.7075 | -30.3913 | -30.7526 | -30.4364
1456.7344 | 121.8613 | -76.712 | 44.8975 | 0.11727 | 0.028162 | -0.016578 | -0.029595 | 0.013375 | 0.081005 | -0.016936 | 44.6608 | 44.6815 | 44.602 | 44.5255 | 76.902 | 76.9988 | 76.5996 | 76.9193 | 76.8293 | 76.7402 | 76.6955 | 76.6824 | 76.7254 | 76.793 | 76.6951 | 44.702 | 44.7227 | 44.6432 | 44.5667 | 76.9432 | 77.04 | 76.6408 | 76.9605 | -32.2413 | -31.9388 | -32.3001 | -31.9976
1458.4688 | 121.9711 | -77.1973 | 44.3802 | 0.11727 | 0.019004 | -0.030314 | -0.029595 | 0.013375 | 0.076426 | -0.026092 | 44.4822 | 44.4983 | 44.4234 | 44.3377 | 77.0714 | 77.1636 | 76.7552 | 77.0841 | 77.3145 | 77.2163 | 77.167 | 77.1677 | 77.2106 | 77.2737 | 77.1712 | 44.5234 | 44.5395 | 44.4646 | 44.3789 | 77.1126 | 77.2048 | 76.7964 | 77.1253 | -32.5892 | -32.273 | -32.648 | -32.3318
1460.1719 | 121.8887 | -76.4053 | 45.2454 | 0.12185 | 0.023583 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.021514 | 45.0316 | 45.0569 | 44.982 | 44.9055 | 76.5129 | 76.6143 | 76.1967 | 76.5347 | 76.5272 | 76.4289 | 76.3933 | 76.3803 | 76.4141 | 76.4909 | 76.3838 | 45.0728 | 45.0981 | 45.0232 | 44.9467 | 76.5541 | 76.6555 | 76.2379 | 76.5759 | -31.4813 | -31.165 | -31.5309 | -31.2147
1461.875 | 121.9254 | -78.4882 | 43.0573 | 0.11269 | 0.019004 | -0.016578 | -0.025017 | 0.022531 | 0.085583 | -0.016936 | 44.2029 | 44.2236 | 44.1487 | 44.0767 | 77.3553 | 77.4475 | 77.0483 | 77.3634 | 78.6009 | 78.5072 | 78.4716 | 78.4631 | 78.5107 | 78.5737 | 78.4712 | 44.2441 | 44.2648 | 44.1899 | 44.1179 | 77.3965 | 77.4887 | 77.0895 | 77.4046 | -33.1524 | -32.8453 | -33.2066 | -32.8995
1463.6406 | 121.8979 | -77.33 | 44.2841 | 0.11727 | 0.023583 | -0.016578 | -0.025017 | 0.022531 | 0.081005 | -0.012357 | 43.9419 | 43.9672 | 43.8832 | 43.8066 | 77.6116 | 77.7176 | 77.3046 | 77.6335 | 77.4473 | 77.3536 | 77.3134 | 77.305 | 77.3525 | 77.411 | 77.3177 | 43.9831 | 44.0084 | 43.9244 | 43.8477 | 77.6528 | 77.7588 | 77.3458 | 77.6747 | -33.6697 | -33.3627 | -33.7285 | -33.4215
1465.3438 | 121.9849 | -77.9205 | 43.6203 | 0.12643 | 0.028162 | -0.025735 | -0.029595 | 0.013375 | 0.081005 | -0.012357 | 43.6214 | 43.6421 | 43.5627 | 43.4814 | 77.9367 | 78.0335 | 77.616 | 77.954 | 78.047 | 77.9487 | 77.8948 | 77.8909 | 77.9339 | 78.0015 | 77.9082 | 43.6626 | 43.6833 | 43.6039 | 43.5226 | 77.9779 | 78.0747 | 77.6572 | 77.9952 | -34.3152 | -33.9945 | -34.374 | -34.0533
1467.0781 | 121.8201 | -78.1082 | 43.5425 | 0.11727 | 0.028162 | -0.012 | -0.025017 | 0.008797 | 0.081005 | -0.016936 | 43.3513 | 43.3719 | 43.2926 | 43.2067 | 78.2068 | 78.3081 | 77.8861 | 78.2332 | 78.2255 | 78.1364 | 78.0962 | 78.0832 | 78.117 | 78.1892 | 78.0913 | 43.3925 | 43.4131 | 43.3338 | 43.2479 | 78.248 | 78.3493 | 77.9273 | 78.2744 | -34.8555 | -34.5348 | -34.9142 | -34.5935
1468.7656 | 121.9025 | -78.273 | 43.3594 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 43.1224 | 43.1522 | 43.0637 | 42.9915 | 78.4266 | 78.5325 | 78.1059 | 78.4484 | 78.3949 | 78.2966 | 78.2519 | 78.2526 | 78.2864 | 78.354 | 78.2515 | 43.1636 | 43.1934 | 43.1049 | 43.0327 | 78.4678 | 78.5737 | 78.1471 | 78.4896 | -35.3042 | -34.9835 | -35.3629 | -35.0422
1470.4844 | 121.8246 | -78.3829 | 43.2724 | 0.12185 | 0.028162 | -0.021157 | -0.025017 | 0.017953 | 0.076426 | -0.021514 | 43.159 | 43.1934 | 43.114 | 43.0327 | 78.3899 | 78.4775 | 78.083 | 78.4118 | 78.5047 | 78.411 | 78.3617 | 78.3579 | 78.4008 | 78.4593 | 78.3614 | 43.2002 | 43.2346 | 43.1552 | 43.0739 | 78.4311 | 78.5187 | 78.1242 | 78.453 | -35.2309 | -34.9239 | -35.2759 | -34.9689
1472.2031 | 121.843 | -77.124 | 44.5541 | 0.12185 | 0.028162 | -0.012 | -0.025017 | 0.017953 | 0.085583 | -0.016936 | 43.7909 | 43.8161 | 43.7367 | 43.6692 | 77.7581 | 77.8549 | 77.442 | 77.78 | 77.2459 | 77.1522 | 77.112 | 77.099 | 77.142 | 77.2096 | 77.1071 | 43.8321 | 43.8573 | 43.7779 | 43.7104 | 77.7993 | 77.8961 | 77.4832 | 77.8212 | -33.9673 | -33.6511 | -34.0215 | -33.7053
1473.9219 | 121.8384 | -77.9572 | 43.6844 | 0.12185 | 0.019004 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.026092 | 43.626 | 43.6558 | 43.5719 | 43.4952 | 77.923 | 78.0152 | 77.6068 | 77.9402 | 78.079 | 77.9762 | 77.9406 | 77.9276 | 77.9705 | 78.0427 | 77.9311 | 43.6672 | 43.697 | 43.6131 | 43.5364 | 77.9642 | 78.0564 | 77.648 | 77.9814 | -34.2969 | -33.9808 | -34.3511 | -34.035
1475.6562 | 121.9528 | -78.1586 | 43.4052 | 0.12185 | 0.019004 | -0.012 | -0.025017 | 0.017953 | 0.076426 | -0.03067 | 43.7725 | 43.7978 | 43.7229 | 43.6417 | 77.781 | 77.8778 | 77.4649 | 77.7891 | 78.2804 | 78.1776 | 78.1466 | 78.1336 | 78.1765 | 78.235 | 78.1279 | 43.8137 | 43.839 | 43.7641 | 43.6829 | 77.8222 | 77.919 | 77.5061 | 77.8303 | -34.0085 | -33.6923 | -34.0581 | -33.7419
1477.3594 | 121.875 | -77.5452 | 44.1101 | 0.12185 | 0.028162 | -0.016578 | -0.029595 | 0.013375 | 0.076426 | -0.016936 | 43.9145 | 43.9443 | 43.8557 | 43.7882 | 77.63 | 77.7313 | 77.3184 | 77.6518 | 77.667 | 77.5733 | 77.5286 | 77.5156 | 77.5585 | 77.6216 | 77.5282 | 43.9557 | 43.9855 | 43.8969 | 43.8294 | 77.6712 | 77.7725 | 77.3596 | 77.693 | -33.7155 | -33.4039 | -33.7743 | -33.4627
1479.0625 | 121.9757 | -77.124 | 44.4626 | 0.11269 | 0.028162 | -0.016578 | -0.025017 | 0.017953 | 0.085583 | -0.026092 | 44.0472 | 44.0771 | 43.9885 | 43.9119 | 77.5063 | 77.5985 | 77.1993 | 77.5236 | 77.2367 | 77.1522 | 77.1074 | 77.099 | 77.142 | 77.2096 | 77.0979 | 44.0884 | 44.1183 | 44.0297 | 43.9531 | 77.5475 | 77.6397 | 77.2405 | 77.5648 | -33.4591 | -33.1521 | -33.5179 | -33.2109
1480.8125 | 121.8246 | -76.3412 | 45.3461 | 0.11727 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.026092 | 45.3521 | 45.382 | 45.2979 | 45.2169 | 76.2016 | 76.2938 | 75.8808 | 76.2097 | 76.4585 | 76.3603 | 76.3201 | 76.3208 | 76.35 | 76.4223 | 76.3152 | 45.3933 | 45.4232 | 45.3391 | 45.2581 | 76.2428 | 76.335 | 75.922 | 76.2509 | -30.8495 | -30.5286 | -30.9037 | -30.5829
1482.5938 | 121.8796 | -76.8723 | 44.7281 | 0.11727 | 0.028162 | -0.021157 | -0.029595 | 0.013375 | 0.090161 | -0.021514 | 44.8119 | 44.8417 | 44.7576 | 44.672 | 76.7326 | 76.8294 | 76.421 | 76.7545 | 76.9895 | 76.9004 | 76.8511 | 76.8427 | 76.8856 | 76.9624 | 76.8507 | 44.8531 | 44.8829 | 44.7988 | 44.7132 | 76.7738 | 76.8706 | 76.4622 | 76.7957 | -31.9208 | -31.6092 | -31.975 | -31.6634
1484.2969 | 121.8933 | -76.918 | 44.6777 | 0.11727 | 0.023583 | -0.021157 | -0.029595 | 0.008797 | 0.081005 | -0.021514 | 44.2212 | 44.2419 | 44.1579 | 44.0859 | 77.3232 | 77.4337 | 77.0208 | 77.3496 | 77.0353 | 76.9416 | 76.8969 | 76.8884 | 76.9268 | 76.999 | 76.8965 | 44.2624 | 44.2831 | 44.1991 | 44.1271 | 77.3644 | 77.4749 | 77.062 | 77.3908 | -33.102 | -32.7996 | -33.1653 | -32.8629
1486.0469 | 121.8842 | -77.3209 | 44.2841 | 0.11727 | 0.023583 | -0.016578 | -0.020438 | 0.022531 | 0.081005 | -0.021514 | 44.2716 | 44.306 | 44.2265 | 44.15 | 77.2729 | 77.3651 | 76.9567 | 77.2855 | 77.4381 | 77.3444 | 77.3043 | 77.3004 | 77.3434 | 77.4019 | 77.2993 | 44.3128 | 44.3472 | 44.2677 | 44.1912 | 77.3141 | 77.4063 | 76.9979 | 77.3267 | -33.0013 | -32.6851 | -33.0463 | -32.7301
1487.7344 | 121.962 | -77.1103 | 44.4489 | 0.11727 | 0.019004 | -0.021157 | -0.029595 | 0.013375 | 0.081005 | -0.021514 | 44.7935 | 44.8188 | 44.7347 | 44.6583 | 76.751 | 76.8432 | 76.4347 | 76.7728 | 77.2276 | 77.1293 | 77.0891 | 77.0807 | 77.1237 | 77.1913 | 77.0888 | 44.8347 | 44.86 | 44.7759 | 44.6994 | 76.7921 | 76.8844 | 76.4759 | 76.814 | -31.9574 | -31.6412 | -32.0162 | -31.7
1489.4062 | 121.8567 | -77.2797 | 44.3481 | 0.12643 | 0.023583 | -0.021157 | -0.029595 | 0.008797 | 0.090161 | -0.021514 | 44.1388 | 44.1732 | 44.0892 | 44.0126 | 77.3965 | 77.5024 | 77.0895 | 77.4275 | 77.4061 | 77.3032 | 77.2585 | 77.2501 | 77.2885 | 77.3698 | 77.2581 | 44.18 | 44.2144 | 44.1304 | 44.0538 | 77.4377 | 77.5436 | 77.1307 | 77.4687 | -33.2577 | -32.9506 | -33.3073 | -33.0003
1491.0938 | 121.8796 | -77.0462 | 44.5908 | 0.11727 | 0.023583 | -0.012 | -0.025017 | 0.013375 | 0.085583 | -0.026092 | 44.3998 | 44.4296 | 44.3502 | 44.269 | 77.1447 | 77.2506 | 76.8331 | 77.1574 | 77.1635 | 77.0698 | 77.0342 | 77.0212 | 77.0596 | 77.1318 | 77.0201 | 44.441 | 44.4708 | 44.3914 | 44.3102 | 77.1859 | 77.2918 | 76.8743 | 77.1986 | -32.7449 | -32.4333 | -32.7945 | -32.4829
1492.7656 | 121.843 | -76.918 | 44.7418 | 0.11269 | 0.028162 | -0.016578 | -0.029595 | 0.008797 | 0.076426 | -0.016936 | 44.7432 | 44.7089 | 44.6981 | 44.6125 | 76.8013 | 76.8981 | 76.4897 | 76.8094 | 77.0307 | 76.9462 | 76.9015 | 76.8884 | 76.9268 | 76.9945 | 76.9011 | 44.7844 | 44.7501 | 44.7393 | 44.6537 | 76.8425 | 76.9393 | 76.5309 | 76.8506 | -32.0581 | -31.7465 | -32.1032 | -31.7916
1494.4531 | 121.962 | -75.4349 | 46.1792 | 0.11727 | 0.023583 | -0.021157 | -0.025017 | 0.004219 | 0.081005 | -0.03067 | 46.1946 | 46.165 | 46.1448 | 46.0549 | 75.35 | 75.4514 | 75.0292 | 75.1842 | 75.5521 | 75.4585 | 75.4137 | 75.4099 | 75.4391 | 75.5159 | 75.4042 | 46.2358 | 46.2062 | 46.186 | 46.0961 | 75.3912 | 75.4926 | 75.0704 | 75.2254 | -29.1555 | -28.8346 | -29.2052 | -28.8843
1496.1406 | 121.875 | -72.8622 | 48.793 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.090161 | -0.016936 | 48.7768 | 48.752 | 48.7316 | 48.6466 | 72.7588 | 72.8557 | 72.4516 | 72.5792 | 72.9841 | 72.8904 | 72.8457 | 72.8418 | 72.8665 | 72.9524 | 72.8453 | 48.818 | 48.7932 | 48.7728 | 48.6878 | 72.8 | 72.8969 | 72.4928 | 72.6204 | -23.9819 | -23.6747 | -24.0272 | -23.72
1497.8281 | 121.843 | -71.9238 | 49.7314 | 0.12185 | 0.014425 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.016936 | 49.8345 | 49.796 | 49.7846 | 49.7043 | 71.7104 | 71.8027 | 71.4123 | 71.5445 | 72.0457 | 71.9383 | 71.9027 | 71.9034 | 71.9372 | 72.0094 | 71.9069 | 49.8757 | 49.8372 | 49.8258 | 49.7455 | 71.7516 | 71.8439 | 71.4535 | 71.5857 | -21.8759 | -21.5778 | -21.9258 | -21.6277
1499.5781 | 121.8155 | -71.3562 | 50.2625 | 0.12185 | 0.023583 | -0.016578 | -0.020438 | 0.017953 | 0.090161 | -0.016936 | 50.3198 | 50.2905 | 50.2745 | 50.1943 | 71.2159 | 71.3174 | 70.9041 | 71.0409 | 71.4781 | 71.3798 | 71.3396 | 71.3358 | 71.3742 | 71.4464 | 71.3393 | 50.361 | 50.3317 | 50.3157 | 50.2355 | 71.2571 | 71.3586 | 70.9453 | 71.0821 | -20.8962 | -20.5843 | -20.9415 | -20.6296
1501.2656 | 121.8338 | -71.5988 | 50.0427 | 0.12185 | 0.023583 | -0.016578 | -0.025017 | 0.013375 | 0.081005 | -0.021514 | 49.9031 | 49.8693 | 49.8441 | 49.7639 | 71.6417 | 71.734 | 71.3298 | 71.4713 | 71.7207 | 71.6224 | 71.5822 | 71.5738 | 71.6122 | 71.6798 | 71.5773 | 49.9443 | 49.9105 | 49.8853 | 49.8051 | 71.6829 | 71.7752 | 71.371 | 71.5125 | -21.7386 | -21.4267 | -21.7976 | -21.4857
1503.0156 | 121.9116 | -71.1823 | 50.3998 | 0.12185 | 0.019004 | -0.016578 | -0.025017 | 0.013375 | 0.081005 | -0.026092 | 50.1275 | 50.0936 | 50.0639 | 49.9882 | 71.4174 | 71.5143 | 71.0963 | 71.2424 | 71.3041 | 71.2013 | 71.1657 | 71.1572 | 71.1956 | 71.2633 | 71.1562 | 50.1687 | 50.1348 | 50.1051 | 50.0294 | 71.4586 | 71.5555 | 71.1375 | 71.2836 | -21.2899 | -20.9689 | -21.3535 | -21.0325
1504.8281 | 121.8338 | -70.3308 | 51.3062 | 0.11727 | 0.028162 | -0.021157 | -0.029595 | 0.013375 | 0.081005 | -0.021514 | 51.2996 | 51.2567 | 51.2313 | 51.1559 | 70.2545 | 70.3469 | 69.9426 | 70.0841 | 70.4481 | 70.359 | 70.3097 | 70.3012 | 70.3442 | 70.4118 | 70.3093 | 51.3408 | 51.2979 | 51.2725 | 51.1971 | 70.2957 | 70.3881 | 69.9838 | 70.1253 | -18.9549 | -18.643 | -19.0232 | -18.7113
1506.5781 | 121.9208 | -69.1635 | 52.446 | 0.11727 | 0.019004 | -0.025735 | -0.025017 | 0.008797 | 0.081005 | -0.026092 | 52.5037 | 52.4609 | 52.44 | 52.3556 | 69.0459 | 69.1383 | 68.7339 | 68.8663 | 69.2808 | 69.1825 | 69.1378 | 69.1385 | 69.1723 | 69.2445 | 69.1374 | 52.5449 | 52.5021 | 52.4812 | 52.3968 | 69.0871 | 69.1795 | 68.7751 | 68.9075 | -16.5422 | -16.2302 | -16.6059 | -16.2939
1508.3438 | 121.9162 | -69.6991 | 51.8921 | 0.11727 | 0.019004 | -0.021157 | -0.034174 | 0.008797 | 0.076426 | -0.026092 | 51.9864 | 51.9526 | 51.9272 | 51.8519 | 69.5541 | 69.651 | 69.2375 | 69.379 | 69.8164 | 69.7181 | 69.6779 | 69.6649 | 69.7079 | 69.7755 | 69.673 | 52.0276 | 51.9938 | 51.9684 | 51.8931 | 69.5953 | 69.6922 | 69.2787 | 69.4202 | -17.5677 | -17.2512 | -17.6268 | -17.3103
1510.0938 | 121.8979 | -69.9326 | 51.6541 | 0.12185 | 0.014425 | -0.021157 | -0.025017 | 0.008797 | 0.071848 | -0.026092 | 51.5468 | 51.5177 | 51.4877 | 51.3986 | 69.9844 | 70.0905 | 69.6816 | 69.8094 | 70.0544 | 69.947 | 69.9114 | 69.9075 | 69.9414 | 70.0044 | 69.9065 | 51.588 | 51.5588 | 51.5289 | 51.4398 | 70.0256 | 70.1317 | 69.7228 | 69.8506 | -18.4376 | -18.1348 | -18.4967 | -18.1939
1511.7812 | 121.843 | -68.6188 | 53.0273 | 0.11727 | 0.019004 | -0.016578 | -0.029595 | 0.013375 | 0.085583 | -0.021514 | 53.1493 | 53.1157 | 53.113 | 53.015 | 68.3866 | 68.4882 | 68.0746 | 68.207 | 68.736 | 68.6378 | 68.6022 | 68.5892 | 68.6321 | 68.7044 | 68.5973 | 53.1905 | 53.1569 | 53.1542 | 53.0562 | 68.4278 | 68.5294 | 68.1158 | 68.2482 | -15.2373 | -14.9253 | -15.2736 | -14.9616
1513.5312 | 121.8979 | -67.2546 | 54.3137 | 0.12185 | 0.014425 | -0.021157 | -0.025017 | 0.013375 | 0.081005 | -0.016936 | 54.1245 | 54.0864 | 54.0653 | 53.9857 | 67.3977 | 67.5176 | 67.1086 | 67.241 | 67.3765 | 67.2691 | 67.2335 | 67.2296 | 67.268 | 67.3356 | 67.2377 | 54.1657 | 54.1276 | 54.1065 | 54.0269 | 67.4389 | 67.5588 | 67.1498 | 67.2822 | -13.2732 | -12.9841 | -13.3325 | -13.0433
1515.2812 | 122.0078 | -83.6792 | 37.8845 | 0.11269 | 0.009846 | -0.025735 | -0.029595 | 0.008797 | 0.076426 | -0.016936 | 43.0262 | 42.9553 | 43.0087 | 42.8907 | 78.5227 | 78.6057 | 78.1929 | 78.3111 | 83.7919 | 83.689 | 83.6535 | 83.6496 | 83.688 | 83.7556 | 83.6623 | 43.0674 | 42.9965 | 43.0499 | 42.9319 | 78.5639 | 78.6469 | 78.234 | 78.3523 | -35.4965 | -35.1666 | -35.514 | -35.1841
1516.9688 | 121.7743 | -82.0908 | 39.6103 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | 0.017953 | 0.090161 | -0.007779 | 34.7621 | 34.805 | 34.7495 | 34.6805 | 86.8046 | 86.8417 | 86.5896 | 86.7303 | 82.2126 | 82.1189 | 82.0742 | 82.0749 | 82.1087 | 82.1809 | 82.083 | 34.8033 | 34.8462 | 34.7907 | 34.7217 | 86.8458 | 86.8829 | 86.6308 | 86.7715 | -52.0426 | -51.8276 | -52.0551 | -51.8401
1518.7188 | 121.8201 | -53.4531 | 68.0649 | 0.12185 | 0.014425 | -0.025735 | -0.029595 | 0.017953 | 0.081005 | -0.026092 | 67.979 | 67.9831 | 67.9787 | 67.8877 | 53.5533 | 53.5637 | 53.2727 | 53.5065 | 53.5749 | 53.4675 | 53.4273 | 53.4235 | 53.471 | 53.5341 | 53.427 | 68.0202 | 68.0243 | 68.0199 | 67.9289 | 53.5945 | 53.6049 | 53.3139 | 53.5477 | 14.4257 | 14.7064 | 14.4253 | 14.706
1520.4688 | 121.6736 | -64.2517 | 57.1243 | 0.11727 | 0.023583 | -0.007421 | -0.020438 | 0.008797 | 0.09474 | -0.016936 | 58.3825 | 58.4225 | 58.3277 | 58.2809 | 63.0943 | 63.1181 | 62.9239 | 63.052 | 64.369 | 64.2753 | 64.2443 | 64.2313 | 64.2605 | 64.3464 | 64.2348 | 58.4237 | 58.4637 | 58.3689 | 58.3221 | 63.1355 | 63.1593 | 62.9651 | 63.0932 | -4.7117 | -4.5414 | -4.7666 | -4.5963
1522.2188 | 121.4813 | -61.4685 | 60.3378 | 0.12185 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.021514 | 55.9605 | 55.9866 | 55.8462 | 55.8219 | 65.4383 | 65.4758 | 65.2772 | 65.4098 | 61.5904 | 61.4921 | 61.4519 | 61.4572 | 61.4819 | 61.5541 | 61.447 | 56.0017 | 56.0278 | 55.8874 | 55.8631 | 65.4795 | 65.517 | 65.3184 | 65.451 | -9.4778 | -9.3167 | -9.5921 | -9.431
1523.9062 | 121.5546 | -60.7315 | 60.5118 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 61.1113 | 61.1194 | 61.0838 | 61.0054 | 60.1688 | 60.1973 | 60.0075 | 60.1311 | 60.8534 | 60.7551 | 60.7103 | 60.7111 | 60.7403 | 60.8125 | 60.7146 | 61.1525 | 61.1606 | 61.125 | 61.0466 | 60.21 | 60.2385 | 60.0487 | 60.1723 | 0.94249 | 1.1038 | 0.91497 | 1.0763
1525.6406 | 121.5591 | -65.0803 | 56.0349 | 0.11727 | 0.009846 | -0.025735 | -0.029595 | 0.008797 | 0.081005 | -0.026092 | 55.7041 | 55.6569 | 55.7363 | 55.6067 | 65.507 | 65.517 | 65.3184 | 65.4281 | 65.1975 | 65.0901 | 65.0545 | 65.0507 | 65.0891 | 65.1613 | 65.0542 | 55.7453 | 55.6981 | 55.7775 | 55.6479 | 65.5482 | 65.5582 | 65.3596 | 65.4693 | -9.8029 | -9.6143 | -9.7706 | -9.5821
1527.3281 | 121.5591 | -69.7952 | 51.3474 | 0.12185 | 0.019004 | -0.025735 | -0.029595 | -0.000359 | 0.076426 | -0.03067 | 56.0658 | 56.0186 | 56.0889 | 55.9685 | 65.1499 | 65.1828 | 64.9659 | 65.071 | 69.9171 | 69.8142 | 69.7695 | 69.7656 | 69.7949 | 69.8717 | 69.7646 | 56.107 | 56.0598 | 56.1301 | 56.0097 | 65.1911 | 65.224 | 65.0071 | 65.1122 | -9.0841 | -8.9001 | -9.061 | -8.877
1529.0781 | 121.5363 | -62.1231 | 59.0286 | 0.11727 | 0.019004 | -0.021157 | -0.029595 | 0.004219 | 0.085583 | -0.021514 | 59.9804 | 59.9656 | 59.9621 | 59.8652 | 61.2081 | 61.2411 | 61.0193 | 61.1338 | 62.2404 | 62.1421 | 62.102 | 62.0935 | 62.1273 | 62.2087 | 62.1016 | 60.0216 | 60.0068 | 60.0033 | 59.9064 | 61.2493 | 61.2823 | 61.0605 | 61.175 | -1.2276 | -1.0389 | -1.246 | -1.0572
1530.8125 | 121.4035 | -60.1685 | 60.9695 | 0.12643 | 0.019004 | -0.021157 | -0.029595 | 0.008797 | 0.081005 | -0.016936 | 61.1662 | 61.1835 | 61.125 | 61.0695 | 59.9765 | 60.0096 | 59.8198 | 59.9343 | 60.2949 | 60.1875 | 60.1473 | 60.1389 | 60.1773 | 60.2495 | 60.1515 | 61.2074 | 61.2247 | 61.1662 | 61.1107 | 60.0177 | 60.0508 | 59.861 | 59.9755 | 1.1897 | 1.3465 | 1.1485 | 1.3052
1532.5 | 121.5317 | -0.56763 | 120.8908 | 0.12185 | 0.019004 | -0.016578 | -0.025017 | 0.004219 | 0.081005 | -0.021514 | 120.6501 | 120.6212 | 120.6197 | 120.5465 | 0.3916 | 0.5909 | 0.36941 | 0.48212 | 0.68948 | 0.58663 | 0.55105 | 0.54261 | 0.57185 | 0.64863 | 0.54611 | 120.6913 | 120.6624 | 120.6609 | 120.5877 | 0.4328 | 0.6321 | 0.41061 | 0.52331 | 120.2585 | 120.2806 | 120.2281 | 120.2503
1534.25 | 121.6919 | -0.51727 | 121.0373 | 0.11727 | 0.014425 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.021514 | 120.8744 | 120.8593 | 120.8487 | 120.7892 | 0.32293 | 0.51307 | 0.30989 | 0.39055 | 0.63455 | 0.5317 | 0.49612 | 0.49226 | 0.52607 | 0.59828 | 0.49576 | 120.9156 | 120.9005 | 120.8899 | 120.8304 | 0.36412 | 0.55427 | 0.35109 | 0.43175 | 120.5515 | 120.5645 | 120.5257 | 120.5388
1535.9375 | 121.6095 | -0.65002 | 121.019 | 0.12643 | 0.014425 | -0.021157 | -0.020438 | 0.013375 | 0.081005 | -0.016936 | 120.8469 | 120.818 | 120.8166 | 120.748 | 0.37329 | 0.5909 | 0.36941 | 0.4638 | 0.77645 | 0.66445 | 0.62887 | 0.62959 | 0.6634 | 0.73103 | 0.63309 | 120.8881 | 120.8592 | 120.8578 | 120.7892 | 0.41448 | 0.6321 | 0.41061 | 0.505 | 120.4736 | 120.4775 | 120.4433 | 120.4472
1537.625 | 121.637 | -0.6546 | 121.0236 | 0.12185 | 0.028162 | -0.016578 | -0.029595 | 0.017953 | 0.090161 | -0.016936 | 120.8561 | 120.8272 | 120.8395 | 120.7572 | 0.38702 | 0.59548 | 0.36941 | 0.4638 | 0.77645 | 0.68276 | 0.63802 | 0.62501 | 0.67256 | 0.74476 | 0.63767 | 120.8973 | 120.8684 | 120.8807 | 120.7984 | 0.42822 | 0.63668 | 0.41061 | 0.505 | 120.4691 | 120.4867 | 120.4525 | 120.4701
1539.3906 | 121.7697 | -0.65918 | 120.9549 | 0.11727 | 0.009846 | -0.025735 | -0.025017 | 0.008797 | 0.076426 | -0.026092 | 120.8378 | 120.8043 | 120.8074 | 120.7343 | 0.4328 | 0.65041 | 0.42435 | 0.51416 | 0.77645 | 0.66903 | 0.63345 | 0.63416 | 0.66798 | 0.73561 | 0.63309 | 120.879 | 120.8455 | 120.8486 | 120.7755 | 0.474 | 0.69161 | 0.46555 | 0.55536 | 120.405 | 120.4134 | 120.3746 | 120.3831
1541.1406 | 121.8292 | -5.7495 | 115.6952 | 0.12185 | 0.014425 | -0.025735 | -0.020438 | 0.013375 | 0.081005 | -0.03067 | 115.4123 | 115.3784 | 115.3913 | 115.3081 | 5.9724 | 6.048 | 5.7994 | 5.9027 | 5.8714 | 5.7639 | 5.7238 | 5.7291 | 5.7629 | 5.8305 | 5.7188 | 115.4535 | 115.4196 | 115.4325 | 115.3493 | 6.0136 | 6.0892 | 5.8406 | 5.9439 | 109.4399 | 109.6129 | 109.4189 | 109.592
1542.8438 | 121.8155 | -7.37 | 114.1708 | 0.12643 | 0.019004 | -0.021157 | -0.029595 | 0.008797 | 0.071848 | -0.026092 | 117.6923 | 117.6449 | 117.6896 | 117.6114 | 3.5963 | 3.7772 | 3.556 | 3.6365 | 7.4964 | 7.389 | 7.3488 | 7.3404 | 7.3788 | 7.4418 | 7.3439 | 117.7335 | 117.6861 | 117.7308 | 117.6526 | 3.6375 | 3.8184 | 3.5972 | 3.6777 | 114.096 | 114.1364 | 114.0933 | 114.1337
1544.6094 | 121.6782 | -1.3962 | 120.2499 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.016936 | 119.6474 | 119.6459 | 119.585 | 119.5254 | 1.6048 | 1.8499 | 1.6102 | 1.6953 | 1.518 | 1.4198 | 1.375 | 1.3803 | 1.405 | 1.4772 | 1.3792 | 119.6886 | 119.6871 | 119.6262 | 119.5666 | 1.646 | 1.8911 | 1.6514 | 1.7365 | 118.0425 | 118.0372 | 117.9802 | 117.9749
1546.3438 | 121.7422 | -1.7532 | 119.8654 | 0.11727 | 0.009846 | -0.012 | -0.025017 | 0.008797 | 0.076426 | -0.016936 | 119.8397 | 119.8153 | 119.8185 | 119.7406 | 1.4171 | 1.6393 | 1.395 | 1.4939 | 1.8705 | 1.7631 | 1.7412 | 1.7282 | 1.762 | 1.8297 | 1.7363 | 119.8809 | 119.8565 | 119.8597 | 119.7818 | 1.4583 | 1.6805 | 1.4362 | 1.5351 | 118.4225 | 118.4447 | 118.4014 | 118.4236
1548.0938 | 121.6141 | -8.812 | 113.8321 | 0.12643 | 0.019004 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.016936 | 111.6899 | 111.6238 | 111.6097 | 111.535 | 9.7494 | 9.7882 | 9.604 | 9.7483 | 8.9384 | 8.831 | 8.7908 | 8.7869 | 8.8207 | 8.893 | 8.795 | 111.7311 | 111.665 | 111.6509 | 111.5762 | 9.7906 | 9.8294 | 9.6452 | 9.7895 | 101.9406 | 102.0859 | 101.8603 | 102.0057
1549.7812 | 121.6599 | -12.0895 | 109.4421 | 0.11727 | 0.019004 | -0.021157 | -0.020438 | 0.013375 | 0.090161 | -0.012357 | 110.6094 | 110.5569 | 110.5429 | 110.4727 | 10.7612 | 10.8046 | 10.6662 | 10.7647 | 12.2068 | 12.1085 | 12.0684 | 12.0691 | 12.1029 | 12.1797 | 12.0772 | 110.6506 | 110.5981 | 110.5841 | 110.5139 | 10.8024 | 10.8458 | 10.7074 | 10.8059 | 99.8482 | 99.9432 | 99.7818 | 99.8767
1551.5156 | 121.6507 | -1.7258 | 119.7922 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.090161 | -0.016936 | 118.6355 | 118.6156 | 118.587 | 118.518 | 2.7036 | 2.7838 | 2.6907 | 2.7666 | 1.8476 | 1.7448 | 1.7046 | 1.7053 | 1.7346 | 1.8159 | 1.7088 | 118.6767 | 118.6568 | 118.6282 | 118.5592 | 2.7448 | 2.825 | 2.7319 | 2.8078 | 115.9319 | 115.9449 | 115.8834 | 115.8963
1553.2656 | 121.6049 | -0.5127 | 121.1288 | 0.11727 | 0.023583 | -0.016578 | -0.025017 | 0.008797 | 0.090161 | -0.012357 | 119.6703 | 119.6642 | 119.5942 | 119.5437 | 1.7147 | 1.8087 | 1.6559 | 1.7228 | 0.62997 | 0.53628 | 0.49612 | 0.48768 | 0.52149 | 0.60286 | 0.50034 | 119.7115 | 119.7054 | 119.6354 | 119.5849 | 1.7559 | 1.8499 | 1.6971 | 1.764 | 117.9556 | 118.0143 | 117.8795 | 117.9383
1554.9688 | 121.6232 | -0.48981 | 121.1655 | 0.13101 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 121.0118 | 120.9829 | 120.986 | 120.9174 | 0.41907 | 0.45814 | 0.27327 | 0.35393 | 0.62082 | 0.51797 | 0.46865 | 0.46937 | 0.4986 | 0.57081 | 0.47287 | 121.053 | 121.0241 | 121.0272 | 120.9586 | 0.46027 | 0.49933 | 0.31447 | 0.39513 | 120.5927 | 120.7385 | 120.5669 | 120.7127
1556.7188 | 121.6461 | -0.62256 | 121.0236 | 0.12643 | 0.023583 | -0.016578 | -0.01586 | 0.013375 | 0.081005 | -0.021514 | 120.9385 | 120.9096 | 120.9219 | 120.8442 | 0.50148 | 0.54512 | 0.32821 | 0.41802 | 0.74899 | 0.64614 | 0.60598 | 0.6067 | 0.63593 | 0.70356 | 0.60104 | 120.9797 | 120.9508 | 120.9631 | 120.8854 | 0.54267 | 0.58632 | 0.36941 | 0.45922 | 120.437 | 120.6103 | 120.4204 | 120.5937
1558.4844 | 121.6599 | -0.64545 | 121.0739 | 0.12643 | 0.019004 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 119.9404 | 119.9114 | 119.9193 | 119.8505 | 1.5133 | 1.5431 | 1.3904 | 1.4573 | 0.77188 | 0.66445 | 0.62887 | 0.62501 | 0.65882 | 0.72645 | 0.62393 | 119.9816 | 119.9526 | 119.9605 | 119.8917 | 1.5544 | 1.5843 | 1.4316 | 1.4985 | 118.4271 | 118.55 | 118.406 | 118.5289
1560.25 | 121.6278 | -3.9688 | 117.7917 | 0.13101 | 0.019004 | -0.034893 | -0.025017 | -0.000359 | 0.076426 | -0.021514 | 118.5027 | 118.4554 | 118.4679 | 118.3807 | 2.9874 | 2.999 | 2.8417 | 3.0001 | 4.0998 | 3.9878 | 3.9339 | 3.9438 | 3.9685 | 4.0452 | 3.9473 | 118.5439 | 118.4966 | 118.5091 | 118.4219 | 3.0286 | 3.0402 | 2.8829 | 3.0413 | 115.5153 | 115.661 | 115.4805 | 115.6262
1561.9531 | 121.6919 | -3.0029 | 118.5974 | 0.11727 | 0.019004 | -0.016578 | -0.020438 | 0.017953 | 0.085583 | -0.026092 | 119.0888 | 119.0506 | 119.0631 | 118.9851 | 2.3099 | 2.4038 | 2.2099 | 2.3912 | 3.1202 | 3.0219 | 2.9864 | 2.9825 | 3.0209 | 3.0885 | 2.9768 | 119.13 | 119.0918 | 119.1043 | 119.0263 | 2.3511 | 2.445 | 2.2511 | 2.4324 | 116.7789 | 116.8789 | 116.7533 | 116.8532
1563.7031 | 121.7056 | -5.4016 | 116.2125 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | 0.017953 | 0.085583 | -0.021514 | 116.2501 | 116.2255 | 116.2292 | 116.1415 | 5.1895 | 5.2193 | 5.0623 | 5.2022 | 5.5235 | 5.4298 | 5.385 | 5.3812 | 5.4196 | 5.4872 | 5.3801 | 116.2913 | 116.2667 | 116.2704 | 116.1827 | 5.2307 | 5.2605 | 5.1035 | 5.2434 | 111.0606 | 111.1879 | 111.0396 | 111.1669
1565.4688 | 121.6827 | -1.6388 | 120.0348 | 0.12185 | 0.028162 | -0.012 | -0.025017 | 0.008797 | 0.085583 | -0.021514 | 118.5073 | 118.4737 | 118.4771 | 118.4036 | 2.8455 | 2.9807 | 2.8509 | 2.8811 | 1.7606 | 1.667 | 1.6268 | 1.6138 | 1.6476 | 1.7244 | 1.6173 | 118.5485 | 118.5149 | 118.5183 | 118.4448 | 2.8867 | 3.0219 | 2.8921 | 2.9223 | 115.6618 | 115.6564 | 115.6316 | 115.6262
1567.2188 | 121.6599 | -16.713 | 104.6539 | 0.11727 | 0.014425 | -0.021157 | -0.029595 | 0.013375 | 0.076426 | -0.026092 | 106.4018 | 106.381 | 106.3492 | 106.2691 | 14.9731 | 15.0027 | 14.8371 | 14.9675 | 16.8302 | 16.7274 | 16.6918 | 16.6834 | 16.7263 | 16.7894 | 16.6869 | 106.443 | 106.4222 | 106.3904 | 106.3103 | 15.0143 | 15.0439 | 14.8783 | 15.0087 | 91.4287 | 91.5647 | 91.3762 | 91.5121
1568.9688 | 121.6873 | -3.2043 | 118.4052 | 0.12185 | 0.019004 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 118.9148 | 118.8812 | 118.8983 | 118.8203 | 2.493 | 2.5228 | 2.3427 | 2.4004 | 3.3262 | 3.2233 | 3.1878 | 3.1839 | 3.2131 | 3.2854 | 3.1874 | 118.956 | 118.9224 | 118.9395 | 118.8615 | 2.5342 | 2.564 | 2.3839 | 2.4416 | 116.4218 | 116.5721 | 116.4053 | 116.5556
1570.6562 | 121.6278 | -5.7999 | 115.741 | 0.12185 | 0.014425 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.021514 | 116.3371 | 116.3125 | 116.3345 | 116.256 | 5.0201 | 5.0591 | 4.8105 | 4.9046 | 5.9217 | 5.8143 | 5.7833 | 5.7886 | 5.8132 | 5.8854 | 5.7784 | 116.3783 | 116.3537 | 116.3757 | 116.2972 | 5.0613 | 5.1003 | 4.8516 | 4.9458 | 111.317 | 111.5267 | 111.3143 | 111.524
1572.4062 | 121.6507 | -9.1461 | 112.1933 | 0.11269 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.076426 | -0.021514 | 114.8583 | 114.8381 | 114.8465 | 114.7632 | 6.3661 | 6.4966 | 6.2618 | 6.3559 | 9.2588 | 9.1697 | 9.125 | 9.1257 | 9.1549 | 9.2225 | 9.1246 | 114.8995 | 114.8793 | 114.8877 | 114.8044 | 6.4073 | 6.5378 | 6.303 | 6.3971 | 108.4921 | 108.5965 | 108.4804 | 108.5847
1574.1719 | 121.5775 | -1.6708 | 119.9295 | 0.11727 | 0.019004 | -0.021157 | -0.01586 | 0.017953 | 0.090161 | -0.007779 | 119.4139 | 119.3849 | 119.3699 | 119.3056 | 1.8429 | 2.0055 | 1.8849 | 1.9059 | 1.7881 | 1.6898 | 1.6497 | 1.655 | 1.6888 | 1.761 | 1.6631 | 119.4551 | 119.4261 | 119.4111 | 119.3468 | 1.8841 | 2.0467 | 1.9261 | 1.9471 | 117.571 | 117.529 | 117.527 | 117.485
1575.8594 | 121.6415 | -1.3367 | 120.2911 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.013375 | 0.090161 | -0.016936 | 120.1693 | 120.1266 | 120.1528 | 120.0795 | 1.2386 | 1.2639 | 1.0516 | 1.1414 | 1.4585 | 1.3603 | 1.3155 | 1.3162 | 1.35 | 1.4268 | 1.3197 | 120.2105 | 120.1678 | 120.194 | 120.1207 | 1.2798 | 1.3051 | 1.0928 | 1.1826 | 118.9307 | 119.1177 | 118.9142 | 119.1012
1577.6094 | 121.7194 | -1.0712 | 120.6482 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.09474 | -0.03067 | 116.2364 | 116.2026 | 116.1513 | 116.0957 | 5.1987 | 5.2514 | 5.1401 | 5.1702 | 1.193 | 1.0947 | 1.05 | 1.0553 | 1.0845 | 1.1659 | 1.0405 | 116.2776 | 116.2438 | 116.1925 | 116.1369 | 5.2399 | 5.2926 | 5.1813 | 5.2114 | 111.0377 | 111.0963 | 110.9527 | 111.0112
1579.3594 | 121.701 | -9.7458 | 111.7355 | 0.11727 | 0.023583 | -0.025735 | -0.025017 | 0.004219 | 0.081005 | -0.016936 | 112.7338 | 112.6861 | 112.7176 | 112.634 | 8.6277 | 8.6437 | 8.5144 | 8.6221 | 9.8631 | 9.7694 | 9.7201 | 9.7208 | 9.75 | 9.8268 | 9.7289 | 112.775 | 112.7273 | 112.7588 | 112.6752 | 8.6689 | 8.6849 | 8.5556 | 8.6633 | 104.1061 | 104.2195 | 104.0899 | 104.2033
1581.1094 | 121.5866 | -12.8448 | 108.4396 | 0.12185 | 0.009846 | -0.021157 | -0.029595 | 0.004219 | 0.076426 | -0.026092 | 110.8246 | 110.7538 | 110.8039 | 110.7016 | 10.4956 | 10.507 | 10.3732 | 10.4396 | 12.9667 | 12.8547 | 12.8237 | 12.8153 | 12.8491 | 12.9213 | 12.8188 | 110.8658 | 110.795 | 110.8451 | 110.7428 | 10.5368 | 10.5482 | 10.4144 | 10.4808 | 100.329 | 100.4514 | 100.3083 | 100.4307
1582.7969 | 121.5088 | -13.5132 | 107.9407 | 0.12643 | 0.019004 | -0.021157 | -0.01586 | 0.004219 | 0.076426 | -0.012357 | 106.9329 | 106.8984 | 106.8116 | 106.7637 | 14.2268 | 14.3343 | 14.1275 | 14.3036 | 13.6396 | 13.5322 | 13.492 | 13.4973 | 13.5174 | 13.5896 | 13.5008 | 106.9741 | 106.9396 | 106.8528 | 106.8049 | 14.268 | 14.3755 | 14.1687 | 14.3448 | 92.706 | 92.8054 | 92.5848 | 92.6842
1584.5469 | 121.3211 | -20.1553 | 100.9094 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.013375 | 0.081005 | -0.012357 | 93.875 | 93.8992 | 93.8276 | 93.7729 | 27.1052 | 27.1712 | 27.0294 | 27.1225 | 20.2726 | 20.1835 | 20.1388 | 20.1395 | 20.1687 | 20.2363 | 20.143 | 93.9162 | 93.9404 | 93.8688 | 93.8141 | 27.1464 | 27.2123 | 27.0706 | 27.1637 | 66.7698 | 66.8456 | 66.7224 | 66.7983
1586.2969 | 121.1426 | -17.3264 | 103.6606 | 0.12643 | 0.014425 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.016936 | 103.4212 | 103.4002 | 103.3688 | 103.3019 | 17.5643 | 17.603 | 17.4834 | 17.5679 | 17.4528 | 17.3408 | 17.3098 | 17.3059 | 17.3352 | 17.4119 | 17.3094 | 103.4624 | 103.4414 | 103.41 | 103.3431 | 17.6055 | 17.6442 | 17.5246 | 17.6091 | 85.8568 | 85.9377 | 85.8045 | 85.8853
1587.9844 | 121.5088 | -0.19684 | 121.2524 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.076426 | -0.016936 | 121.1308 | 121.0882 | 121.1005 | 121.0228 | 0.048236 | 0.15141 | 0.044348 | 0.097548 | 0.31869 | 0.22042 | 0.17568 | 0.1764 | 0.20564 | 0.27326 | 0.1799 | 121.172 | 121.1294 | 121.1417 | 121.064 | 0.089435 | 0.19261 | 0.085547 | 0.13875 | 121.0826 | 121.0864 | 121.0522 | 121.0561
1589.7344 | 121.5546 | -0.21515 | 121.3623 | 0.12643 | 0.023583 | -0.016578 | -0.025017 | 0.008797 | 0.085583 | -0.026092 | 121.1995 | 121.1706 | 121.1829 | 121.0915 | 0.043657 | 0.14683 | 0.048926 | 0.09297 | 0.34158 | 0.23873 | 0.19857 | 0.19013 | 0.22395 | 0.30073 | 0.18906 | 121.2407 | 121.2118 | 121.2241 | 121.1327 | 0.084856 | 0.18803 | 0.090125 | 0.13417 | 121.1558 | 121.1505 | 121.1392 | 121.1339
1591.4219 | 121.6141 | -0.20599 | 121.3898 | 0.11727 | 0.023583 | -0.016578 | -0.020438 | 0.017953 | 0.085583 | -0.026092 | 121.2269 | 121.1981 | 121.2103 | 121.1281 | 0.052814 | 0.16056 | 0.053505 | 0.097548 | 0.32327 | 0.22958 | 0.18942 | 0.18556 | 0.22395 | 0.29158 | 0.1799 | 121.2681 | 121.2393 | 121.2515 | 121.1693 | 0.094013 | 0.20176 | 0.094704 | 0.13875 | 121.1741 | 121.1734 | 121.1575 | 121.1568
1593.1562 | 121.5958 | -0.22888 | 121.376 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.026092 | 121.2453 | 121.2164 | 121.2241 | 121.1418 | 0.057392 | 0.16514 | 0.048926 | 0.10213 | 0.35073 | 0.25246 | 0.20772 | 0.20844 | 0.2331 | 0.30989 | 0.20279 | 121.2865 | 121.2576 | 121.2653 | 121.183 | 0.098591 | 0.20634 | 0.090125 | 0.14332 | 121.1879 | 121.1963 | 121.1667 | 121.1751
1594.9062 | 121.5866 | -0.24261 | 121.4172 | 0.11727 | 0.019004 | -0.016578 | -0.006703 | 0.017953 | 0.085583 | -0.016936 | 121.2636 | 121.221 | 121.247 | 121.1601 | 0.052814 | 0.16514 | 0.058083 | 0.10213 | 0.35989 | 0.26162 | 0.22604 | 0.23591 | 0.26057 | 0.3282 | 0.22568 | 121.3048 | 121.2622 | 121.2882 | 121.2013 | 0.094013 | 0.20634 | 0.099282 | 0.14332 | 121.2108 | 121.2055 | 121.1941 | 121.1889
1596.6562 | 121.6553 | -0.23346 | 121.376 | 0.12643 | 0.019004 | -0.016578 | -0.01586 | 0.017953 | 0.085583 | -0.016936 | 121.2773 | 121.2393 | 121.2515 | 121.1739 | 0.057392 | 0.1743 | 0.062662 | 0.11128 | 0.35989 | 0.25246 | 0.21688 | 0.2176 | 0.25141 | 0.31904 | 0.21652 | 121.3185 | 121.2805 | 121.2927 | 121.2151 | 0.098591 | 0.21549 | 0.10386 | 0.15248 | 121.2199 | 121.2146 | 121.1941 | 121.1889
1598.4062 | 121.6278 | -0.25635 | 121.4218 | 0.12185 | 0.023583 | -0.012 | -0.029595 | 0.008797 | 0.085583 | -0.016936 | 121.2819 | 121.2439 | 121.2515 | 121.1785 | 0.071126 | 0.18345 | 0.06724 | 0.12044 | 0.3782 | 0.27993 | 0.24435 | 0.22675 | 0.26515 | 0.34193 | 0.23941 | 121.3231 | 121.2851 | 121.2927 | 121.2197 | 0.11232 | 0.22465 | 0.10844 | 0.16164 | 121.2108 | 121.2146 | 121.1804 | 121.1843
1600.1562 | 121.6736 | -0.2243 | 121.431 | 0.12643 | 0.028162 | -0.021157 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 121.291 | 121.253 | 121.2744 | 121.1922 | 0.075705 | 0.17887 | 0.062662 | 0.12044 | 0.35073 | 0.25247 | 0.20315 | 0.20387 | 0.23768 | 0.30531 | 0.20279 | 121.3322 | 121.2942 | 121.3156 | 121.2334 | 0.1169 | 0.22007 | 0.10386 | 0.16164 | 121.2153 | 121.2284 | 121.1987 | 121.2118
1601.8438 | 121.7789 | -0.21973 | 121.376 | 0.12185 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.076426 | -0.016936 | 121.2956 | 121.2576 | 121.2699 | 121.1922 | 0.075705 | 0.18345 | 0.06724 | 0.12502 | 0.34158 | 0.24331 | 0.19399 | 0.19929 | 0.22852 | 0.29615 | 0.20279 | 121.3368 | 121.2988 | 121.3111 | 121.2334 | 0.1169 | 0.22465 | 0.10844 | 0.16622 | 121.2199 | 121.2284 | 121.1941 | 121.2026
1603.5938 | 121.6827 | -0.25635 | 121.4218 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 121.3048 | 121.2759 | 121.2836 | 121.2013 | 0.071126 | 0.18345 | 0.071818 | 0.12044 | 0.3782 | 0.27993 | 0.23519 | 0.23591 | 0.26972 | 0.33735 | 0.23483 | 121.346 | 121.3171 | 121.3248 | 121.2425 | 0.11232 | 0.22465 | 0.11302 | 0.16164 | 121.2336 | 121.233 | 121.2125 | 121.2118
1605.3594 | 121.756 | -0.2243 | 121.4081 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.026092 | 121.3094 | 121.2851 | 121.2836 | 121.2105 | 0.075705 | 0.18803 | 0.06724 | 0.12502 | 0.34158 | 0.24789 | 0.20315 | 0.20387 | 0.2331 | 0.30531 | 0.19821 | 121.3506 | 121.3263 | 121.3248 | 121.2517 | 0.1169 | 0.22923 | 0.10844 | 0.16622 | 121.2336 | 121.2421 | 121.2079 | 121.2163
1607.1094 | 121.6736 | -0.25177 | 121.4584 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | 0.017953 | 0.076426 | -0.016936 | 121.3185 | 121.2897 | 121.2882 | 121.2197 | 0.071126 | 0.17887 | 0.06724 | 0.12502 | 0.37362 | 0.28451 | 0.23061 | 0.23591 | 0.26972 | 0.3282 | 0.23483 | 121.3597 | 121.3309 | 121.3294 | 121.2609 | 0.11232 | 0.22007 | 0.10844 | 0.16622 | 121.2474 | 121.2513 | 121.217 | 121.2209
1608.7969 | 121.6644 | -0.27008 | 121.463 | 0.12185 | 0.023583 | -0.016578 | -0.020438 | 0.004219 | 0.081005 | -0.021514 | 121.3231 | 121.2942 | 121.2973 | 121.2288 | 0.075705 | 0.18345 | 0.076397 | 0.12044 | 0.39193 | 0.29366 | 0.2535 | 0.24964 | 0.2743 | 0.35109 | 0.24857 | 121.3643 | 121.3354 | 121.3385 | 121.27 | 0.1169 | 0.22465 | 0.1176 | 0.16164 | 121.2474 | 121.2467 | 121.2216 | 121.2209
1610.5469 | 121.8109 | -0.21057 | 121.4035 | 0.12185 | 0.019004 | -0.016578 | -0.01586 | 0.017953 | 0.085583 | -0.026092 | 121.3322 | 121.2988 | 121.2973 | 121.2242 | 0.071126 | 0.19261 | 0.071818 | 0.12502 | 0.33242 | 0.22958 | 0.19399 | 0.19471 | 0.22852 | 0.29615 | 0.18448 | 121.3734 | 121.34 | 121.3385 | 121.2654 | 0.11232 | 0.23381 | 0.11302 | 0.16622 | 121.2611 | 121.2604 | 121.2262 | 121.2255
1612.2969 | 121.8475 | -0.21973 | 121.4172 | 0.12185 | 0.019004 | -0.025735 | -0.025017 | 0.008797 | 0.081005 | -0.026092 | 121.3322 | 121.2897 | 121.3019 | 121.2242 | 0.080283 | 0.20176 | 0.071818 | 0.13417 | 0.34158 | 0.23873 | 0.19399 | 0.19471 | 0.22852 | 0.30073 | 0.19364 | 121.3734 | 121.3309 | 121.3431 | 121.2654 | 0.12148 | 0.24296 | 0.11302 | 0.17537 | 121.252 | 121.2604 | 121.2216 | 121.2301
1614.0469 | 121.7972 | -0.23804 | 121.4401 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.022531 | 0.085583 | -0.016936 | 121.3368 | 121.2897 | 121.3019 | 121.238 | 0.080283 | 0.20176 | 0.076397 | 0.12959 | 0.35989 | 0.26162 | 0.21688 | 0.2176 | 0.26057 | 0.32362 | 0.2211 | 121.378 | 121.3309 | 121.3431 | 121.2792 | 0.12148 | 0.24296 | 0.1176 | 0.17079 | 121.2565 | 121.2604 | 121.2216 | 121.2255
1615.7344 | 121.8063 | -0.24261 | 121.4127 | 0.12643 | 0.028162 | -0.021157 | -0.01586 | 0.017953 | 0.076426 | -0.016936 | 121.3185 | 121.2851 | 121.2927 | 121.2151 | 0.084861 | 0.22008 | 0.085554 | 0.15249 | 0.36904 | 0.27078 | 0.22146 | 0.22675 | 0.26057 | 0.31904 | 0.22568 | 121.3597 | 121.3263 | 121.3339 | 121.2563 | 0.12606 | 0.26128 | 0.12675 | 0.19368 | 121.2336 | 121.233 | 121.2079 | 121.2072
1617.4844 | 121.701 | -0.34332 | 121.3715 | 0.12185 | 0.023583 | -0.016578 | -0.01586 | 0.013375 | 0.076426 | -0.021514 | 121.2865 | 121.2393 | 121.2515 | 121.1785 | 0.13064 | 0.26586 | 0.13592 | 0.18911 | 0.46517 | 0.36691 | 0.32675 | 0.32746 | 0.3567 | 0.41975 | 0.32181 | 121.3277 | 121.2805 | 121.2927 | 121.2197 | 0.17184 | 0.30706 | 0.17712 | 0.23031 | 121.1558 | 121.1505 | 121.1209 | 121.1156
1619.2344 | 121.8109 | -0.30212 | 121.3852 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 121.2956 | 121.2576 | 121.2699 | 121.183 | 0.12149 | 0.2567 | 0.12218 | 0.18453 | 0.42397 | 0.32571 | 0.28097 | 0.28626 | 0.30634 | 0.38771 | 0.28519 | 121.3368 | 121.2988 | 121.3111 | 121.2242 | 0.16268 | 0.2979 | 0.16338 | 0.22573 | 121.1741 | 121.1734 | 121.1484 | 121.1477
1620.9219 | 121.756 | -0.33417 | 121.4035 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.090161 | -0.016936 | 121.2819 | 121.2485 | 121.2607 | 121.1785 | 0.13064 | 0.27044 | 0.13134 | 0.19369 | 0.45602 | 0.36233 | 0.31301 | 0.31373 | 0.33839 | 0.42433 | 0.31723 | 121.3231 | 121.2897 | 121.3019 | 121.2197 | 0.17184 | 0.31163 | 0.17254 | 0.23489 | 121.1512 | 121.1505 | 121.1301 | 121.1294
1622.6719 | 121.788 | -0.33875 | 121.3806 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.021514 | 121.2819 | 121.2347 | 121.2515 | 121.1739 | 0.14438 | 0.28417 | 0.13592 | 0.20285 | 0.45602 | 0.36233 | 0.31759 | 0.31831 | 0.35212 | 0.42433 | 0.31723 | 121.3231 | 121.2759 | 121.2927 | 121.2151 | 0.18558 | 0.32537 | 0.17712 | 0.24405 | 121.1375 | 121.146 | 121.1072 | 121.1156
1624.4219 | 121.8246 | -0.33875 | 121.3486 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.021514 | 121.2544 | 121.2256 | 121.2378 | 121.151 | 0.15353 | 0.2979 | 0.14965 | 0.22116 | 0.4606 | 0.35775 | 0.31759 | 0.31831 | 0.34296 | 0.41975 | 0.31723 | 121.2956 | 121.2668 | 121.279 | 121.1922 | 0.19473 | 0.3391 | 0.19085 | 0.26236 | 121.1009 | 121.1048 | 121.0843 | 121.0882
1626.125 | 121.8292 | -0.33875 | 121.3577 | 0.11727 | 0.019004 | -0.025735 | -0.020438 | 0.008797 | 0.085583 | -0.03067 | 121.2636 | 121.2256 | 121.2286 | 121.1372 | 0.17185 | 0.31164 | 0.16339 | 0.23489 | 0.45602 | 0.35775 | 0.31301 | 0.31831 | 0.34754 | 0.42433 | 0.30808 | 121.3048 | 121.2668 | 121.2698 | 121.1784 | 0.21304 | 0.35284 | 0.20459 | 0.27609 | 121.0917 | 121.1002 | 121.0568 | 121.0653
1627.8906 | 121.788 | -0.36163 | 121.3669 | 0.12643 | 0.028162 | -0.021157 | -0.025017 | 0.013375 | 0.090161 | -0.012357 | 121.2727 | 121.221 | 121.2378 | 121.1601 | 0.16727 | 0.31164 | 0.15881 | 0.22574 | 0.48806 | 0.3898 | 0.34048 | 0.33662 | 0.37501 | 0.45179 | 0.34928 | 121.3139 | 121.2622 | 121.279 | 121.2013 | 0.20847 | 0.35284 | 0.20001 | 0.26694 | 121.1055 | 121.1139 | 121.0705 | 121.079
1629.6406 | 121.8063 | -0.3479 | 121.3669 | 0.11727 | 0.019004 | -0.025735 | -0.020438 | 0.008797 | 0.076426 | -0.021514 | 121.2773 | 121.2301 | 121.247 | 121.1739 | 0.15353 | 0.2979 | 0.15423 | 0.21658 | 0.46517 | 0.3669 | 0.32216 | 0.32746 | 0.3567 | 0.42433 | 0.32639 | 121.3185 | 121.2713 | 121.2882 | 121.2151 | 0.19473 | 0.3391 | 0.19543 | 0.25778 | 121.1238 | 121.1231 | 121.0934 | 121.0927
1631.3281 | 121.8567 | -0.32959 | 121.3669 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 121.2819 | 121.2347 | 121.247 | 121.1693 | 0.15811 | 0.30706 | 0.15881 | 0.22116 | 0.44686 | 0.35775 | 0.30843 | 0.30915 | 0.33839 | 0.41059 | 0.30808 | 121.3231 | 121.2759 | 121.2882 | 121.2105 | 0.19931 | 0.34826 | 0.20001 | 0.26236 | 121.1238 | 121.1231 | 121.0888 | 121.0882
1633.1094 | 121.8384 | -0.3479 | 121.3531 | 0.11269 | 0.023583 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.026092 | 121.2636 | 121.2256 | 121.2378 | 121.1601 | 0.16727 | 0.31622 | 0.16797 | 0.23947 | 0.46059 | 0.37148 | 0.33132 | 0.32746 | 0.36128 | 0.43348 | 0.32181 | 121.3048 | 121.2668 | 121.279 | 121.2013 | 0.20847 | 0.35741 | 0.20916 | 0.28067 | 121.0963 | 121.0956 | 121.0705 | 121.0698
1634.7969 | 121.8246 | -0.37537 | 121.3211 | 0.11727 | 0.019004 | -0.021157 | -0.025017 | 0.004219 | 0.085583 | -0.03067 | 121.2269 | 121.1844 | 121.1966 | 121.1235 | 0.19931 | 0.362 | 0.19543 | 0.27152 | 0.49264 | 0.39437 | 0.35421 | 0.35035 | 0.37958 | 0.46095 | 0.3447 | 121.2681 | 121.2256 | 121.2378 | 121.1647 | 0.24051 | 0.4032 | 0.23663 | 0.31272 | 121.0276 | 121.0315 | 120.9973 | 121.0012
1636.5469 | 121.8246 | -1.0345 | 120.694 | 0.11269 | 0.019004 | -0.021157 | -0.025017 | 0.008797 | 0.090161 | -0.021514 | 120.5493 | 120.5113 | 120.5236 | 120.4412 | 0.80821 | 1.0258 | 0.79978 | 0.89415 | 1.1472 | 1.0535 | 1.0134 | 1.0095 | 1.0433 | 1.1247 | 1.013 | 120.5905 | 120.5525 | 120.5648 | 120.4824 | 0.84941 | 1.067 | 0.84098 | 0.93535 | 119.7411 | 119.7495 | 119.7154 | 119.7238
1638.2969 | 121.8796 | -0.32044 | 121.376 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 121.3277 | 121.2851 | 121.2973 | 121.2151 | 0.12149 | 0.2567 | 0.12218 | 0.18453 | 0.44229 | 0.33944 | 0.29928 | 0.3 | 0.32923 | 0.40602 | 0.29892 | 121.3689 | 121.3263 | 121.3385 | 121.2563 | 0.16268 | 0.2979 | 0.16338 | 0.22573 | 121.2062 | 121.2055 | 121.1758 | 121.1751
1639.9844 | 121.8658 | -0.29297 | 121.3989 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.026092 | 121.3231 | 121.2851 | 121.2927 | 121.2197 | 0.13064 | 0.26586 | 0.12676 | 0.18911 | 0.41024 | 0.31655 | 0.27181 | 0.27253 | 0.30177 | 0.37397 | 0.26688 | 121.3643 | 121.3263 | 121.3339 | 121.2609 | 0.17184 | 0.30706 | 0.16796 | 0.23031 | 121.1924 | 121.1963 | 121.1621 | 121.166
1641.75 | 121.8887 | -0.30212 | 121.3943 | 0.12643 | 0.019004 | -0.016578 | -0.020438 | 0.008797 | 0.076426 | -0.021514 | 121.3231 | 121.2851 | 121.3019 | 121.2197 | 0.13064 | 0.27501 | 0.13134 | 0.19369 | 0.42855 | 0.32113 | 0.28555 | 0.28169 | 0.31092 | 0.37855 | 0.28061 | 121.3643 | 121.3263 | 121.3431 | 121.2609 | 0.17184 | 0.31621 | 0.17254 | 0.23489 | 121.1924 | 121.1918 | 121.1713 | 121.1706
1643.4844 | 121.7697 | -0.36163 | 121.4493 | 0.12643 | 0.023583 | -0.012 | -0.025017 | 0.008797 | 0.090161 | -0.021514 | 121.3277 | 121.2851 | 121.3019 | 121.2105 | 0.13522 | 0.27044 | 0.14507 | 0.20742 | 0.48806 | 0.38522 | 0.34963 | 0.33662 | 0.37043 | 0.45179 | 0.34012 | 121.3689 | 121.3263 | 121.3431 | 121.2517 | 0.17642 | 0.31163 | 0.18627 | 0.24862 | 121.1924 | 121.1826 | 121.1667 | 121.1568
1645.2344 | 121.8613 | -0.33875 | 121.3852 | 0.12185 | 0.023583 | -0.012 | -0.01586 | 0.013375 | 0.085583 | -0.021514 | 121.3002 | 121.2576 | 121.279 | 121.2013 | 0.15353 | 0.2979 | 0.14965 | 0.21658 | 0.4606 | 0.36233 | 0.32675 | 0.32289 | 0.35212 | 0.42433 | 0.31723 | 121.3414 | 121.2988 | 121.3202 | 121.2425 | 0.19473 | 0.3391 | 0.19085 | 0.25778 | 121.1467 | 121.1505 | 121.1255 | 121.1294
1647.0312 | 121.7697 | -0.36163 | 121.4081 | 0.11727 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.012357 | 121.2956 | 121.253 | 121.2699 | 121.1785 | 0.16727 | 0.31164 | 0.15423 | 0.23947 | 0.47891 | 0.38522 | 0.34048 | 0.34577 | 0.37501 | 0.44722 | 0.34928 | 121.3368 | 121.2942 | 121.3111 | 121.2197 | 0.20847 | 0.35284 | 0.19543 | 0.28067 | 121.1284 | 121.1414 | 121.1026 | 121.1156
1648.7188 | 121.8018 | -0.42572 | 121.376 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.012357 | 121.2544 | 121.221 | 121.2286 | 121.1418 | 0.19474 | 0.35284 | 0.20001 | 0.26694 | 0.54757 | 0.45388 | 0.40456 | 0.40528 | 0.42994 | 0.50672 | 0.41336 | 121.2956 | 121.2622 | 121.2698 | 121.183 | 0.23594 | 0.39404 | 0.24121 | 0.30814 | 121.0597 | 121.0544 | 121.0339 | 121.0286
1650.4688 | 121.7834 | -0.4303 | 121.3806 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | 0.008797 | 0.081005 | -0.016936 | 121.2544 | 121.2164 | 121.2286 | 121.1556 | 0.20847 | 0.35284 | 0.19086 | 0.27152 | 0.55215 | 0.45388 | 0.40914 | 0.40528 | 0.4391 | 0.5113 | 0.41336 | 121.2956 | 121.2576 | 121.2698 | 121.1968 | 0.24967 | 0.39404 | 0.23206 | 0.31272 | 121.0459 | 121.0636 | 121.0202 | 121.0378
1652.2188 | 121.8567 | -0.42114 | 121.3074 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.076426 | -0.012357 | 121.2498 | 121.2027 | 121.2195 | 121.1327 | 0.19931 | 0.362 | 0.19543 | 0.28068 | 0.53842 | 0.44473 | 0.39999 | 0.4007 | 0.42536 | 0.49757 | 0.40879 | 121.291 | 121.2439 | 121.2607 | 121.1739 | 0.24051 | 0.4032 | 0.23663 | 0.32187 | 121.0505 | 121.0544 | 121.0202 | 121.0241
1653.9062 | 121.8704 | -0.39825 | 121.3303 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.026092 | 121.2407 | 121.2072 | 121.2149 | 121.1235 | 0.20847 | 0.36657 | 0.20001 | 0.28068 | 0.52011 | 0.42184 | 0.3771 | 0.37782 | 0.40705 | 0.48384 | 0.37216 | 121.2819 | 121.2484 | 121.2561 | 121.1647 | 0.24967 | 0.40777 | 0.24121 | 0.32187 | 121.0322 | 121.0407 | 121.0064 | 121.0149
1655.6719 | 121.7834 | -0.48981 | 121.344 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.026092 | 121.2178 | 121.1798 | 121.1874 | 121.1006 | 0.23136 | 0.4032 | 0.2229 | 0.30357 | 0.60708 | 0.51797 | 0.47323 | 0.47395 | 0.4986 | 0.57081 | 0.46371 | 121.259 | 121.221 | 121.2286 | 121.1418 | 0.27256 | 0.4444 | 0.2641 | 0.34476 | 120.9864 | 120.9949 | 120.9561 | 120.9645
1657.3594 | 121.8521 | -0.93384 | 120.7809 | 0.11269 | 0.019004 | -0.012 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 120.7096 | 120.6669 | 120.6884 | 120.6015 | 0.6846 | 0.89763 | 0.67617 | 0.76596 | 1.0465 | 0.95284 | 0.92184 | 0.9134 | 0.94263 | 1.0194 | 0.91232 | 120.7508 | 120.7081 | 120.7296 | 120.6427 | 0.7258 | 0.93883 | 0.71737 | 0.80716 | 120.025 | 120.0334 | 120.0038 | 120.0122
1659.1094 | 121.8201 | -2.1881 | 119.5404 | 0.12643 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.071848 | -0.021514 | 119.7069 | 119.6596 | 119.6903 | 119.5987 | 1.6872 | 1.8865 | 1.6605 | 1.7548 | 2.3145 | 2.2117 | 2.1624 | 2.1677 | 2.1969 | 2.26 | 2.1666 | 119.7481 | 119.7008 | 119.7315 | 119.6399 | 1.7284 | 1.9277 | 1.7017 | 1.796 | 118.0197 | 118.0464 | 118.0031 | 118.0298
1660.8125 | 121.9116 | -2.2476 | 119.4489 | 0.12185 | 0.023583 | -0.021157 | -0.025017 | 0.004219 | 0.081005 | -0.03067 | 118.7912 | 118.7301 | 118.7747 | 118.6691 | 2.7722 | 2.7929 | 2.654 | 2.6842 | 2.3695 | 2.2712 | 2.2265 | 2.2226 | 2.2518 | 2.3286 | 2.2169 | 118.8324 | 118.7713 | 118.8159 | 118.7103 | 2.8134 | 2.8341 | 2.6952 | 2.7254 | 116.0189 | 116.1372 | 116.0024 | 116.1207
1662.5625 | 121.8658 | -0.64087 | 121.1014 | 0.12185 | 0.028162 | -0.025735 | -0.020438 | -0.000359 | 0.076426 | -0.016936 | 120.9568 | 120.9096 | 120.9265 | 120.8396 | 0.42365 | 0.65041 | 0.42893 | 0.51416 | 0.76272 | 0.66903 | 0.61513 | 0.62043 | 0.64051 | 0.7173 | 0.62393 | 120.998 | 120.9508 | 120.9677 | 120.8808 | 0.46485 | 0.69161 | 0.47013 | 0.55536 | 120.5332 | 120.5279 | 120.5028 | 120.4976
1664.25 | 121.8384 | -2.1286 | 119.6228 | 0.12185 | 0.028162 | -0.025735 | -0.01586 | 0.013375 | 0.076426 | -0.016936 | 120.6867 | 120.6486 | 120.6655 | 120.5786 | 0.71207 | 0.91136 | 0.6899 | 0.78885 | 2.2505 | 2.1568 | 2.1029 | 2.1127 | 2.142 | 2.205 | 2.1117 | 120.7279 | 120.6898 | 120.7067 | 120.6198 | 0.75327 | 0.95256 | 0.7311 | 0.83005 | 119.9746 | 119.9968 | 119.9535 | 119.9756
1666.0156 | 121.6965 | -7.7728 | 113.887 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.076426 | -0.012357 | 113.883 | 113.8399 | 113.8439 | 113.7696 | 7.6251 | 7.6594 | 7.3972 | 7.5005 | 7.8901 | 7.7964 | 7.7562 | 7.757 | 7.7816 | 7.8493 | 7.7605 | 113.9242 | 113.8811 | 113.8851 | 113.8108 | 7.6663 | 7.7006 | 7.4384 | 7.5417 | 106.2579 | 106.4858 | 106.2188 | 106.4466
1667.7656 | 121.669 | -17.7658 | 103.7201 | 0.12185 | 0.014425 | -0.016578 | -0.020438 | -0.000359 | 0.076426 | -0.021514 | 105.2892 | 105.1951 | 105.31 | 105.2068 | 15.9803 | 16.1197 | 15.9222 | 15.9975 | 17.8877 | 17.7802 | 17.7492 | 17.7454 | 17.7654 | 17.8422 | 17.7443 | 105.3304 | 105.2363 | 105.3512 | 105.248 | 16.0215 | 16.1609 | 15.9634 | 16.0387 | 89.3089 | 89.367 | 89.3297 | 89.3878
1669.4531 | 120.845 | -75.737 | 44.7601 | 0.11269 | 0.019004 | -0.021157 | -0.025017 | 0.008797 | 0.071848 | -0.016936 | 45.1507 | 45.1256 | 45.1376 | 45.0566 | 75.4507 | 75.5018 | 75.3039 | 75.4131 | 75.8497 | 75.756 | 75.7158 | 75.712 | 75.7458 | 75.8088 | 75.7201 | 45.1919 | 45.1668 | 45.1788 | 45.0978 | 75.4919 | 75.543 | 75.3451 | 75.4543 | -30.3001 | -30.1532 | -30.3131 | -30.1663
1671.2188 | 121.4447 | -116.185 | 4.9301 | 0.11727 | 0.014425 | -0.025735 | -0.020438 | 0.004219 | 0.081005 | -0.026092 | 7.2499 | 7.1581 | 7.2112 | 7.1102 | 113.6419 | 113.9118 | 113.6525 | 113.6362 | 116.3023 | 116.1994 | 116.1593 | 116.1646 | 116.1892 | 116.266 | 116.1589 | 7.2911 | 7.1993 | 7.2523 | 7.1514 | 113.6831 | 113.953 | 113.6937 | 113.6774 | -106.392 | -106.4026 | -106.4307 | -106.4413
1672.9375 | 120.8908 | -68.1564 | 52.5558 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.016936 | 51.556 | 51.5909 | 51.506 | 51.4581 | 69.0734 | 69.1108 | 68.917 | 69.054 | 68.2737 | 68.18 | 68.1399 | 68.1406 | 68.1652 | 68.2466 | 68.1395 | 51.5972 | 51.6321 | 51.5472 | 51.4993 | 69.1146 | 69.152 | 68.9582 | 69.0952 | -17.5174 | -17.3611 | -17.5673 | -17.411
1674.7031 | 120.9274 | -0.26093 | 120.9503 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 120.7599 | 120.7265 | 120.7342 | 120.6519 | 0.094017 | 0.20176 | 0.09471 | 0.14791 | 0.38278 | 0.28909 | 0.24435 | 0.24507 | 0.26514 | 0.34651 | 0.24399 | 120.8011 | 120.7677 | 120.7754 | 120.6931 | 0.13522 | 0.24296 | 0.13591 | 0.18911 | 120.6659 | 120.6652 | 120.6402 | 120.6395
1676.3906 | 121.3486 | -0.1831 | 121.0236 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.026092 | 120.9248 | 120.8867 | 120.8853 | 120.8076 | 0.039079 | 0.14225 | 0.03977 | 0.09297 | 0.30496 | 0.21584 | 0.16195 | 0.16724 | 0.1919 | 0.26411 | 0.15701 | 120.966 | 120.9279 | 120.9265 | 120.8488 | 0.080278 | 0.18345 | 0.080969 | 0.13417 | 120.8857 | 120.885 | 120.8462 | 120.8455
1678.1406 | 121.2845 | -0.21515 | 121.1197 | 0.12643 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.012357 | 120.9797 | 120.9325 | 120.9402 | 120.8625 | 0.043657 | 0.15598 | 0.048926 | 0.097548 | 0.34158 | 0.23415 | 0.19399 | 0.19929 | 0.22395 | 0.29615 | 0.20279 | 121.0209 | 120.9737 | 120.9814 | 120.9037 | 0.084856 | 0.19718 | 0.090125 | 0.13875 | 120.936 | 120.9308 | 120.8966 | 120.8913
1679.8281 | 121.344 | -0.2243 | 121.1197 | 0.12185 | 0.023583 | -0.025735 | -0.025017 | -0.000359 | 0.085583 | -0.016936 | 120.9934 | 120.9554 | 120.9768 | 120.89 | 0.06197 | 0.1743 | 0.062662 | 0.1067 | 0.34615 | 0.24789 | 0.19857 | 0.19929 | 0.22395 | 0.30989 | 0.20737 | 121.0346 | 120.9966 | 121.018 | 120.9312 | 0.10317 | 0.21549 | 0.10386 | 0.1479 | 120.9315 | 120.9308 | 120.9149 | 120.9142
1681.5781 | 121.4035 | -0.24261 | 121.0968 | 0.12185 | 0.023583 | -0.030314 | -0.025017 | 0.004219 | 0.081005 | -0.026092 | 121.0163 | 120.9646 | 120.9814 | 120.9037 | 0.071126 | 0.18345 | 0.071818 | 0.12959 | 0.36447 | 0.2662 | 0.2123 | 0.2176 | 0.24683 | 0.32362 | 0.21652 | 121.0575 | 121.0058 | 121.0226 | 120.9449 | 0.11232 | 0.22465 | 0.11302 | 0.17079 | 120.9452 | 120.9445 | 120.9103 | 120.9096
1683.3281 | 121.376 | -0.26093 | 121.1472 | 0.11727 | 0.023583 | -0.012 | -0.020438 | 0.004219 | 0.085583 | -0.012357 | 121.0255 | 120.9875 | 120.9906 | 120.9083 | 0.071126 | 0.20176 | 0.076397 | 0.13875 | 0.3782 | 0.28451 | 0.24893 | 0.24049 | 0.26514 | 0.34651 | 0.24857 | 121.0667 | 121.0287 | 121.0318 | 120.9495 | 0.11232 | 0.24296 | 0.1176 | 0.17995 | 120.9544 | 120.9491 | 120.9195 | 120.9142
1685.0938 | 121.4035 | -0.28381 | 121.138 | 0.12185 | 0.028162 | -0.012 | -0.020438 | 0.008797 | 0.081005 | -0.012357 | 121.0301 | 120.9966 | 121.0043 | 120.922 | 0.084861 | 0.22008 | 0.090132 | 0.13875 | 0.40566 | 0.31198 | 0.27181 | 0.26337 | 0.29261 | 0.36482 | 0.27146 | 121.0713 | 121.0378 | 121.0455 | 120.9632 | 0.12606 | 0.26128 | 0.13133 | 0.17995 | 120.9452 | 120.9399 | 120.9195 | 120.9142
1686.7969 | 121.4172 | -0.32044 | 121.1426 | 0.11727 | 0.028162 | -0.025735 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 121.0301 | 120.992 | 121.0089 | 120.922 | 0.098596 | 0.23381 | 0.10845 | 0.16622 | 0.43771 | 0.3486 | 0.2947 | 0.30458 | 0.32465 | 0.40602 | 0.30808 | 121.0713 | 121.0332 | 121.0501 | 120.9632 | 0.1398 | 0.27501 | 0.14965 | 0.20742 | 120.9315 | 120.9216 | 120.9103 | 120.9004
1688.5469 | 121.4355 | -0.31128 | 121.1472 | 0.11727 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.085583 | -0.026092 | 121.0255 | 120.992 | 120.9952 | 120.922 | 0.12149 | 0.25212 | 0.11302 | 0.17538 | 0.42855 | 0.33944 | 0.2947 | 0.29084 | 0.3155 | 0.39686 | 0.28519 | 121.0667 | 121.0332 | 121.0364 | 120.9632 | 0.16268 | 0.29332 | 0.15422 | 0.21658 | 120.904 | 120.9125 | 120.8737 | 120.8821
1690.25 | 121.5637 | -0.2655 | 121.0831 | 0.11269 | 0.028162 | -0.012 | -0.020438 | 0.004219 | 0.081005 | -0.026092 | 121.0255 | 120.992 | 120.9997 | 120.9174 | 0.12607 | 0.26586 | 0.12676 | 0.19369 | 0.3782 | 0.29367 | 0.2535 | 0.24506 | 0.26972 | 0.34651 | 0.23941 | 121.0667 | 121.0332 | 121.0409 | 120.9586 | 0.16726 | 0.30706 | 0.16796 | 0.23489 | 120.8994 | 120.8987 | 120.8737 | 120.873
1692.0625 | 121.582 | -0.28839 | 121.138 | 0.12185 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 121.0346 | 121.0012 | 121.0043 | 120.9266 | 0.1398 | 0.27959 | 0.13134 | 0.20285 | 0.41024 | 0.31197 | 0.26723 | 0.27711 | 0.29261 | 0.37397 | 0.26688 | 121.0758 | 121.0424 | 121.0455 | 120.9678 | 0.181 | 0.32079 | 0.17254 | 0.24405 | 120.8948 | 120.9033 | 120.8645 | 120.873
1693.7969 | 121.5363 | -0.32501 | 121.17 | 0.12643 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.090161 | -0.012357 | 121.0621 | 121.0287 | 121.0272 | 120.9495 | 0.12607 | 0.26586 | 0.13134 | 0.19369 | 0.45144 | 0.35317 | 0.30843 | 0.30457 | 0.32923 | 0.41517 | 0.31266 | 121.1033 | 121.0699 | 121.0684 | 120.9907 | 0.16726 | 0.30706 | 0.17254 | 0.23489 | 120.9361 | 120.9308 | 120.9011 | 120.8959
1695.5312 | 121.582 | -0.31586 | 121.1426 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 121.0575 | 121.0287 | 121.0272 | 120.9449 | 0.14896 | 0.27959 | 0.14049 | 0.20285 | 0.43313 | 0.33944 | 0.2947 | 0.30458 | 0.32008 | 0.40144 | 0.29434 | 121.0987 | 121.0699 | 121.0684 | 120.9861 | 0.19015 | 0.32079 | 0.18169 | 0.24405 | 120.9086 | 120.917 | 120.8782 | 120.8867
1697.2812 | 121.4996 | -0.37079 | 121.1746 | 0.12185 | 0.03274 | -0.016578 | -0.01586 | 0.004219 | 0.090161 | -0.016936 | 121.053 | 121.0149 | 121.0272 | 120.9403 | 0.15811 | 0.31164 | 0.15423 | 0.22116 | 0.49264 | 0.40353 | 0.35421 | 0.35493 | 0.37501 | 0.46095 | 0.35385 | 121.0942 | 121.0561 | 121.0684 | 120.9815 | 0.19931 | 0.35284 | 0.19543 | 0.26236 | 120.8948 | 120.8987 | 120.8691 | 120.873
1698.9844 | 121.6553 | -0.32044 | 121.1334 | 0.11727 | 0.028162 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.016936 | 121.0575 | 121.0195 | 121.0226 | 120.9495 | 0.16269 | 0.31164 | 0.16339 | 0.22574 | 0.43771 | 0.3486 | 0.30386 | 0.3 | 0.32923 | 0.40602 | 0.3035 | 121.0987 | 121.0607 | 121.0638 | 120.9907 | 0.20389 | 0.35284 | 0.20459 | 0.26694 | 120.8948 | 120.8942 | 120.8599 | 120.8592
1700.7344 | 121.669 | -0.34332 | 121.1243 | 0.12185 | 0.023583 | -0.025735 | -0.025017 | 0.008797 | 0.081005 | -0.021514 | 121.0621 | 121.0195 | 121.0272 | 120.9403 | 0.17185 | 0.31622 | 0.15881 | 0.24405 | 0.46517 | 0.36691 | 0.31759 | 0.31831 | 0.35212 | 0.42433 | 0.32181 | 121.1033 | 121.0607 | 121.0684 | 120.9815 | 0.21304 | 0.35741 | 0.20001 | 0.28525 | 120.8903 | 120.9033 | 120.8554 | 120.8684
1702.4531 | 121.637 | -0.37537 | 121.1655 | 0.12643 | 0.019004 | -0.025735 | -0.011281 | 0.004219 | 0.076426 | -0.026092 | 121.0438 | 121.0058 | 121.0226 | 120.9403 | 0.17642 | 0.33911 | 0.16797 | 0.25321 | 0.50179 | 0.39437 | 0.34963 | 0.36408 | 0.37958 | 0.45179 | 0.34927 | 121.085 | 121.047 | 121.0638 | 120.9815 | 0.21762 | 0.38031 | 0.20916 | 0.2944 | 120.8674 | 120.8758 | 120.8462 | 120.8547
1704.1875 | 121.6782 | -0.37994 | 121.138 | 0.12185 | 0.023583 | -0.025735 | -0.025017 | 0.004219 | 0.081005 | -0.026092 | 121.0346 | 121.0058 | 121.0089 | 120.922 | 0.19474 | 0.35742 | 0.19086 | 0.27152 | 0.50179 | 0.40353 | 0.35421 | 0.35493 | 0.38416 | 0.46095 | 0.35385 | 121.0758 | 121.047 | 121.0501 | 120.9632 | 0.23594 | 0.39862 | 0.23206 | 0.31272 | 120.8399 | 120.8438 | 120.8142 | 120.818
1705.9062 | 121.6324 | -0.43945 | 121.1105 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | -0.004937 | 0.081005 | -0.026092 | 121.0026 | 120.9646 | 120.9723 | 120.8946 | 0.22678 | 0.39862 | 0.23206 | 0.30814 | 0.55673 | 0.46304 | 0.4183 | 0.42817 | 0.43452 | 0.52046 | 0.41336 | 121.0438 | 121.0058 | 121.0135 | 120.9358 | 0.26798 | 0.43982 | 0.27326 | 0.34934 | 120.7758 | 120.7705 | 120.7455 | 120.7402
1707.6562 | 121.6507 | -0.48523 | 121.0648 | 0.12185 | 0.023583 | -0.016578 | -0.020438 | -0.000359 | 0.081005 | -0.016936 | 120.966 | 120.9371 | 120.9311 | 120.8579 | 0.26799 | 0.44898 | 0.25495 | 0.34477 | 0.60708 | 0.50881 | 0.46865 | 0.46479 | 0.48487 | 0.56623 | 0.46829 | 121.0072 | 120.9783 | 120.9723 | 120.8991 | 0.30919 | 0.49018 | 0.29615 | 0.38597 | 120.698 | 120.711 | 120.6631 | 120.6761
1709.375 | 121.6553 | -0.48065 | 121.0419 | 0.11727 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.076426 | -0.016936 | 120.9751 | 120.9325 | 120.9448 | 120.8579 | 0.26341 | 0.44898 | 0.25495 | 0.34477 | 0.59793 | 0.50881 | 0.46407 | 0.46021 | 0.48487 | 0.55708 | 0.46372 | 121.0163 | 120.9737 | 120.986 | 120.8991 | 0.30461 | 0.49018 | 0.29615 | 0.38597 | 120.7117 | 120.7202 | 120.6814 | 120.6898
1711.1562 | 121.5912 | -0.52643 | 121.106 | 0.11727 | 0.023583 | -0.016578 | -0.020438 | -0.004937 | 0.081005 | -0.026092 | 120.9889 | 120.96 | 120.9677 | 120.8854 | 0.26799 | 0.4444 | 0.25495 | 0.34477 | 0.6437 | 0.55001 | 0.50985 | 0.50599 | 0.52149 | 0.60743 | 0.50034 | 121.0301 | 121.0012 | 121.0089 | 120.9266 | 0.30919 | 0.4856 | 0.29615 | 0.38597 | 120.7209 | 120.7339 | 120.6997 | 120.7127
1712.9844 | 121.669 | -0.44403 | 121.106 | 0.11727 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.076426 | -0.021514 | 121.0163 | 120.9737 | 120.9906 | 120.9129 | 0.2451 | 0.42609 | 0.23206 | 0.32188 | 0.5613 | 0.46761 | 0.42287 | 0.42359 | 0.44825 | 0.52046 | 0.42252 | 121.0575 | 121.0149 | 121.0318 | 120.9541 | 0.2863 | 0.46729 | 0.27326 | 0.36308 | 120.7712 | 120.7843 | 120.7455 | 120.7585
1714.6875 | 121.6873 | -0.46234 | 121.0831 | 0.11727 | 0.028162 | -0.016578 | -0.006703 | -0.004937 | 0.076426 | -0.026092 | 121.0163 | 120.9783 | 120.986 | 120.8946 | 0.25425 | 0.43067 | 0.2458 | 0.33104 | 0.57961 | 0.4905 | 0.44576 | 0.45564 | 0.4574 | 0.53877 | 0.43625 | 121.0575 | 121.0195 | 121.0272 | 120.9358 | 0.29545 | 0.47187 | 0.287 | 0.37223 | 120.7621 | 120.7705 | 120.7317 | 120.7402
1716.4375 | 121.7377 | -0.45319 | 121.1288 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.076426 | -0.016936 | 121.0301 | 120.9966 | 121.0043 | 120.922 | 0.2451 | 0.42151 | 0.23206 | 0.32188 | 0.57504 | 0.47219 | 0.43203 | 0.43275 | 0.46198 | 0.52961 | 0.43625 | 121.0713 | 121.0378 | 121.0455 | 120.9632 | 0.2863 | 0.46271 | 0.27326 | 0.36308 | 120.785 | 120.798 | 120.7592 | 120.7723
1718.1875 | 121.6187 | -0.5127 | 121.17 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.021514 | 121.0255 | 120.9875 | 120.9997 | 120.922 | 0.24968 | 0.43982 | 0.2458 | 0.33561 | 0.63455 | 0.53628 | 0.49154 | 0.49226 | 0.52607 | 0.59828 | 0.49118 | 121.0667 | 121.0287 | 121.0409 | 120.9632 | 0.29087 | 0.48102 | 0.287 | 0.37681 | 120.7758 | 120.7797 | 120.7501 | 120.7539
1719.8906 | 121.637 | -0.49439 | 121.1334 | 0.12643 | 0.03274 | -0.012 | -0.01586 | 0.008797 | 0.076426 | -0.021514 | 121.0438 | 121.0012 | 121.0043 | 120.922 | 0.25425 | 0.43525 | 0.2458 | 0.33104 | 0.62081 | 0.52713 | 0.48239 | 0.47853 | 0.50318 | 0.57081 | 0.47287 | 121.085 | 121.0424 | 121.0455 | 120.9632 | 0.29545 | 0.47645 | 0.287 | 0.37223 | 120.7895 | 120.798 | 120.7501 | 120.7585
1721.6562 | 121.6232 | -0.49896 | 121.1472 | 0.12643 | 0.03274 | -0.012 | -0.011281 | 0.004219 | 0.090161 | -0.021514 | 121.0484 | 121.0149 | 121.0272 | 120.9266 | 0.25883 | 0.43982 | 0.2458 | 0.34019 | 0.62539 | 0.5317 | 0.48696 | 0.48768 | 0.50318 | 0.58912 | 0.47745 | 121.0896 | 121.0561 | 121.0684 | 120.9678 | 0.30003 | 0.48102 | 0.287 | 0.38139 | 120.7895 | 120.8026 | 120.7684 | 120.7814
1723.3438 | 121.6415 | -0.50812 | 121.1792 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | -0.000359 | 0.076426 | -0.016936 | 121.053 | 121.0195 | 121.0226 | 120.9358 | 0.25883 | 0.43067 | 0.25038 | 0.33104 | 0.62997 | 0.53628 | 0.49154 | 0.49226 | 0.50776 | 0.58454 | 0.49118 | 121.0942 | 121.0607 | 121.0638 | 120.977 | 0.30003 | 0.47187 | 0.29157 | 0.37223 | 120.7941 | 120.8026 | 120.7638 | 120.7723
1725.0938 | 121.6873 | -0.49439 | 121.1426 | 0.12643 | 0.03274 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.021514 | 121.053 | 121.0149 | 121.018 | 120.9449 | 0.26799 | 0.44898 | 0.25953 | 0.34019 | 0.62081 | 0.52713 | 0.47323 | 0.47395 | 0.4986 | 0.57539 | 0.47287 | 121.0942 | 121.0561 | 121.0592 | 120.9861 | 0.30919 | 0.49018 | 0.30073 | 0.38139 | 120.785 | 120.7934 | 120.7501 | 120.7585
1726.8438 | 121.6827 | -0.4715 | 121.1746 | 0.12643 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.081005 | -0.016936 | 121.0804 | 121.0424 | 121.0455 | 120.9678 | 0.25425 | 0.42609 | 0.23664 | 0.32188 | 0.59793 | 0.49966 | 0.45492 | 0.45106 | 0.47572 | 0.5525 | 0.45456 | 121.1216 | 121.0836 | 121.0867 | 121.009 | 0.29545 | 0.46729 | 0.27784 | 0.36308 | 120.8262 | 120.8438 | 120.7913 | 120.8089
1728.5938 | 121.7148 | -0.50354 | 121.1609 | 0.12643 | 0.019004 | -0.016578 | -0.025017 | 0.008797 | 0.081005 | -0.021514 | 121.0438 | 121.0149 | 121.0135 | 120.9403 | 0.26799 | 0.45356 | 0.26411 | 0.3585 | 0.62997 | 0.52254 | 0.48696 | 0.47852 | 0.51234 | 0.58454 | 0.48203 | 121.085 | 121.0561 | 121.0547 | 120.9815 | 0.30919 | 0.49476 | 0.30531 | 0.3997 | 120.7758 | 120.7797 | 120.7455 | 120.7494
1730.2812 | 121.6644 | -0.52185 | 121.1655 | 0.11727 | 0.028162 | -0.025735 | -0.020438 | -0.000359 | 0.081005 | -0.016936 | 121.0484 | 121.0058 | 121.0135 | 120.9403 | 0.28172 | 0.46729 | 0.26411 | 0.3585 | 0.63912 | 0.55001 | 0.49612 | 0.50141 | 0.52149 | 0.60286 | 0.50492 | 121.0896 | 121.047 | 121.0547 | 120.9815 | 0.32292 | 0.50849 | 0.30531 | 0.3997 | 120.7667 | 120.7843 | 120.7317 | 120.7494
1732.0312 | 121.7194 | -0.53558 | 121.1426 | 0.11727 | 0.028162 | -0.016578 | -0.020438 | -0.000359 | 0.085583 | -0.016936 | 121.0575 | 121.0149 | 121.0226 | 120.9358 | 0.2863 | 0.45814 | 0.27785 | 0.36766 | 0.65286 | 0.56375 | 0.51901 | 0.51515 | 0.53522 | 0.62117 | 0.51865 | 121.0987 | 121.0561 | 121.0638 | 120.977 | 0.3275 | 0.49933 | 0.31904 | 0.40886 | 120.7712 | 120.7797 | 120.7363 | 120.7448
1733.7812 | 121.7697 | -0.52185 | 121.1472 | 0.11727 | 0.019004 | -0.025735 | -0.025017 | 0.004219 | 0.076426 | -0.026092 | 121.0667 | 121.0195 | 121.0318 | 120.9495 | 0.27714 | 0.45814 | 0.26411 | 0.36308 | 0.63912 | 0.54085 | 0.49612 | 0.49683 | 0.52607 | 0.59828 | 0.49576 | 121.1079 | 121.0607 | 121.073 | 120.9907 | 0.31834 | 0.49933 | 0.30531 | 0.40428 | 120.7895 | 120.8026 | 120.7546 | 120.7677
1735.4688 | 121.701 | -0.50812 | 121.1975 | 0.12643 | 0.028162 | -0.016578 | -0.011281 | -0.000359 | 0.081005 | -0.016936 | 121.085 | 121.047 | 121.0547 | 120.9678 | 0.26341 | 0.43982 | 0.25495 | 0.34477 | 0.63455 | 0.53628 | 0.49154 | 0.49684 | 0.50776 | 0.58912 | 0.49118 | 121.1262 | 121.0882 | 121.0959 | 121.009 | 0.30461 | 0.48102 | 0.29615 | 0.38597 | 120.8216 | 120.8301 | 120.7913 | 120.7997
1737.2344 | 121.6827 | -0.50354 | 121.225 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.021514 | 121.0942 | 121.0561 | 121.0684 | 120.9861 | 0.25883 | 0.4444 | 0.25495 | 0.34019 | 0.62539 | 0.5317 | 0.48696 | 0.48768 | 0.50776 | 0.58912 | 0.48203 | 121.1354 | 121.0973 | 121.1096 | 121.0273 | 0.30003 | 0.4856 | 0.29615 | 0.38139 | 120.8353 | 120.8392 | 120.8096 | 120.8135
1739 | 121.6919 | -0.51727 | 121.2387 | 0.12185 | 0.023583 | -0.016578 | -0.01586 | -0.000359 | 0.081005 | -0.021514 | 121.1079 | 121.0699 | 121.073 | 120.9861 | 0.26341 | 0.43525 | 0.25495 | 0.34477 | 0.63912 | 0.54086 | 0.5007 | 0.50141 | 0.51691 | 0.59828 | 0.49576 | 121.1491 | 121.1111 | 121.1142 | 121.0273 | 0.30461 | 0.47645 | 0.29615 | 0.38597 | 120.8445 | 120.8529 | 120.8096 | 120.818
1740.75 | 121.6919 | -0.50812 | 121.2387 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | -0.000359 | 0.085583 | -0.016936 | 121.1171 | 121.0699 | 121.0821 | 120.9953 | 0.26341 | 0.43525 | 0.2458 | 0.34019 | 0.62997 | 0.53628 | 0.48696 | 0.48768 | 0.50776 | 0.5937 | 0.49118 | 121.1583 | 121.1111 | 121.1233 | 121.0365 | 0.30461 | 0.47645 | 0.287 | 0.38139 | 120.8536 | 120.8713 | 120.8187 | 120.8363
1742.4531 | 121.6873 | -0.50354 | 121.2479 | 0.11727 | 0.03274 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.021514 | 121.1262 | 121.0836 | 121.1005 | 121.009 | 0.25425 | 0.43525 | 0.2458 | 0.32646 | 0.62081 | 0.53628 | 0.48238 | 0.49684 | 0.51234 | 0.58912 | 0.48203 | 121.1674 | 121.1248 | 121.1417 | 121.0502 | 0.29545 | 0.47645 | 0.287 | 0.36766 | 120.872 | 120.8804 | 120.8462 | 120.8547
1744.2031 | 121.8018 | -0.46234 | 121.2067 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.016936 | 121.1262 | 121.0882 | 121.0959 | 121.0136 | 0.25425 | 0.43525 | 0.25038 | 0.33561 | 0.58419 | 0.48592 | 0.44118 | 0.4419 | 0.46656 | 0.54335 | 0.4454 | 121.1674 | 121.1294 | 121.1371 | 121.0548 | 0.29545 | 0.47645 | 0.29157 | 0.37681 | 120.872 | 120.8758 | 120.8416 | 120.8455
1745.9531 | 121.8338 | -0.43488 | 121.2112 | 0.12185 | 0.028162 | -0.016578 | -0.025017 | -0.000359 | 0.076426 | -0.026092 | 121.1354 | 121.0928 | 121.1005 | 121.0273 | 0.25425 | 0.42609 | 0.25038 | 0.33104 | 0.55673 | 0.46304 | 0.4183 | 0.40986 | 0.43452 | 0.5113 | 0.40878 | 121.1766 | 121.134 | 121.1417 | 121.0685 | 0.29545 | 0.46729 | 0.29157 | 0.37223 | 120.8811 | 120.885 | 120.8462 | 120.8501
1747.7188 | 121.7285 | -0.48065 | 121.2479 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 121.1628 | 121.1019 | 121.1188 | 121.0365 | 0.24052 | 0.41693 | 0.24122 | 0.33104 | 0.6025 | 0.50881 | 0.46407 | 0.46479 | 0.48487 | 0.56624 | 0.46372 | 121.204 | 121.1431 | 121.16 | 121.0777 | 0.28172 | 0.45813 | 0.28242 | 0.37223 | 120.9223 | 120.9216 | 120.8783 | 120.8776
1749.4688 | 121.8475 | -0.43945 | 121.2067 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | -0.000359 | 0.085583 | -0.021514 | 121.1583 | 121.1248 | 121.1325 | 121.0502 | 0.24052 | 0.42151 | 0.24122 | 0.31272 | 0.5613 | 0.46304 | 0.4183 | 0.41901 | 0.43909 | 0.52504 | 0.41794 | 121.1995 | 121.166 | 121.1737 | 121.0914 | 0.28172 | 0.46271 | 0.28242 | 0.35392 | 120.9177 | 120.917 | 120.892 | 120.8913
1751.1562 | 121.8475 | -0.4303 | 121.2158 | 0.11727 | 0.023583 | -0.012 | -0.01586 | -0.000359 | 0.081005 | -0.021514 | 121.172 | 121.134 | 121.1417 | 121.0594 | 0.22678 | 0.4032 | 0.22748 | 0.31272 | 0.54757 | 0.45388 | 0.4183 | 0.41444 | 0.42994 | 0.5113 | 0.40878 | 121.2132 | 121.1752 | 121.1829 | 121.1006 | 0.26798 | 0.4444 | 0.26868 | 0.35392 | 120.9452 | 120.9445 | 120.9149 | 120.9142
1752.9219 | 121.8704 | -0.41657 | 121.2158 | 0.11727 | 0.028162 | -0.012 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 121.1812 | 121.1477 | 121.1508 | 121.0594 | 0.23594 | 0.4032 | 0.21833 | 0.30814 | 0.53384 | 0.44473 | 0.40457 | 0.40071 | 0.42078 | 0.50215 | 0.39963 | 121.2224 | 121.1889 | 121.192 | 121.1006 | 0.27714 | 0.4444 | 0.25953 | 0.34934 | 120.9452 | 120.9628 | 120.9149 | 120.9325
1754.6094 | 121.756 | -0.46234 | 121.2799 | 0.12185 | 0.023583 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.021514 | 121.1903 | 121.1477 | 121.16 | 121.0686 | 0.23594 | 0.40778 | 0.22748 | 0.30814 | 0.58419 | 0.48592 | 0.44576 | 0.45564 | 0.47572 | 0.54335 | 0.44083 | 121.2315 | 121.1889 | 121.2012 | 121.1098 | 0.27714 | 0.44898 | 0.26868 | 0.34934 | 120.9544 | 120.9628 | 120.924 | 120.9325
1756.3438 | 121.8246 | -0.41657 | 121.2662 | 0.12185 | 0.019004 | -0.021157 | -0.01586 | 0.004219 | 0.076426 | -0.016936 | 121.1903 | 121.1477 | 121.1508 | 121.0686 | 0.22678 | 0.40778 | 0.22748 | 0.30814 | 0.53842 | 0.43557 | 0.39541 | 0.40071 | 0.42078 | 0.49299 | 0.39963 | 121.2315 | 121.1889 | 121.192 | 121.1098 | 0.26798 | 0.44898 | 0.26868 | 0.34934 | 120.9635 | 120.9628 | 120.924 | 120.9233
1758.125 | 121.8384 | -0.44403 | 121.3074 | 0.12185 | 0.023583 | -0.016578 | -0.020438 | -0.004937 | 0.076426 | -0.021514 | 121.2086 | 121.166 | 121.1783 | 121.0869 | 0.21763 | 0.38947 | 0.21833 | 0.29441 | 0.56588 | 0.46761 | 0.42745 | 0.42359 | 0.43909 | 0.52046 | 0.42252 | 121.2498 | 121.2072 | 121.2195 | 121.1281 | 0.25883 | 0.43066 | 0.25953 | 0.33561 | 120.991 | 120.9903 | 120.9607 | 120.96
1759.8281 | 121.8796 | -0.3891 | 121.2708 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | -0.000359 | 0.076426 | -0.026092 | 121.2132 | 121.1798 | 121.1829 | 121.096 | 0.21305 | 0.37573 | 0.20917 | 0.28983 | 0.51095 | 0.4081 | 0.36794 | 0.36866 | 0.38874 | 0.46552 | 0.36301 | 121.2544 | 121.221 | 121.2241 | 121.1372 | 0.25425 | 0.41693 | 0.25037 | 0.33103 | 121.0002 | 121.004 | 120.9698 | 120.9737
1761.5625 | 121.8018 | -0.45776 | 121.312 | 0.11727 | 0.023583 | -0.021157 | -0.01586 | -0.000359 | 0.081005 | -0.021514 | 121.2178 | 121.1844 | 121.1783 | 121.1006 | 0.22221 | 0.38947 | 0.2229 | 0.29899 | 0.57504 | 0.48135 | 0.43661 | 0.4419 | 0.45741 | 0.53877 | 0.43625 | 121.259 | 121.2256 | 121.2195 | 121.1418 | 0.26341 | 0.43066 | 0.2641 | 0.34019 | 120.9956 | 120.9949 | 120.9561 | 120.9554
1763.25 | 121.7651 | -0.48981 | 121.3669 | 0.12185 | 0.019004 | -0.012 | -0.01586 | -0.000359 | 0.081005 | -0.03067 | 121.2178 | 121.1844 | 121.1966 | 121.1052 | 0.21305 | 0.38031 | 0.21833 | 0.29899 | 0.61166 | 0.50881 | 0.47781 | 0.47395 | 0.48945 | 0.57081 | 0.45914 | 121.259 | 121.2256 | 121.2378 | 121.1464 | 0.25425 | 0.42151 | 0.25953 | 0.34019 | 121.0047 | 120.9995 | 120.9836 | 120.9783
1765 | 121.8887 | -0.38452 | 121.3211 | 0.12185 | 0.028162 | -0.021157 | -0.025017 | 0.004219 | 0.081005 | -0.021514 | 121.2453 | 121.2118 | 121.2149 | 121.1281 | 0.19931 | 0.362 | 0.20459 | 0.28068 | 0.50637 | 0.41268 | 0.36336 | 0.3595 | 0.38874 | 0.46553 | 0.36301 | 121.2865 | 121.253 | 121.2561 | 121.1693 | 0.24051 | 0.4032 | 0.24579 | 0.32187 | 121.0459 | 121.0407 | 121.0156 | 121.0103
1766.75 | 121.8796 | -0.3479 | 121.3669 | 0.11269 | 0.014425 | -0.021157 | -0.020438 | -0.000359 | 0.076426 | -0.021514 | 121.3002 | 121.2622 | 121.2699 | 121.183 | 0.16269 | 0.32079 | 0.16797 | 0.24405 | 0.46059 | 0.36233 | 0.32674 | 0.32746 | 0.34754 | 0.42433 | 0.32639 | 121.3414 | 121.3034 | 121.3111 | 121.2242 | 0.20389 | 0.36199 | 0.20916 | 0.28525 | 121.1375 | 121.1322 | 121.1072 | 121.1019
1768.4375 | 121.7697 | -0.39825 | 121.4172 | 0.12185 | 0.019004 | -0.021157 | -0.020438 | -0.004937 | 0.076426 | -0.026092 | 121.3094 | 121.2668 | 121.279 | 121.183 | 0.16727 | 0.30706 | 0.15881 | 0.23947 | 0.52011 | 0.41726 | 0.3771 | 0.37782 | 0.39332 | 0.47468 | 0.37216 | 121.3506 | 121.308 | 121.3202 | 121.2242 | 0.20847 | 0.34826 | 0.20001 | 0.28067 | 121.1421 | 121.1505 | 121.1117 | 121.1202
1770.1875 | 121.8201 | -0.36621 | 121.4401 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | -0.000359 | 0.081005 | -0.012357 | 121.3277 | 121.2851 | 121.2836 | 121.2059 | 0.14896 | 0.30248 | 0.14965 | 0.22116 | 0.48806 | 0.39437 | 0.34963 | 0.35035 | 0.36585 | 0.44722 | 0.35385 | 121.3689 | 121.3263 | 121.3248 | 121.2471 | 0.19015 | 0.34368 | 0.19085 | 0.26236 | 121.1787 | 121.178 | 121.1346 | 121.1339
1771.9375 | 121.8475 | -0.32044 | 121.4035 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.076426 | -0.021514 | 121.3414 | 121.2988 | 121.3019 | 121.2242 | 0.14438 | 0.28417 | 0.15423 | 0.21658 | 0.43771 | 0.3486 | 0.29928 | 0.3 | 0.32465 | 0.39686 | 0.29892 | 121.3826 | 121.34 | 121.3431 | 121.2654 | 0.18558 | 0.32537 | 0.19543 | 0.25778 | 121.197 | 121.1872 | 121.1575 | 121.1477
1773.7031 | 121.8201 | -0.31586 | 121.4539 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 121.3643 | 121.3355 | 121.334 | 121.2471 | 0.12607 | 0.26128 | 0.1176 | 0.19369 | 0.43313 | 0.33944 | 0.29928 | 0.3 | 0.32008 | 0.39686 | 0.29892 | 121.4055 | 121.3767 | 121.3751 | 121.2883 | 0.16726 | 0.30248 | 0.1588 | 0.23489 | 121.2382 | 121.2467 | 121.2079 | 121.2163
1775.4375 | 121.8155 | -0.29755 | 121.4996 | 0.10812 | 0.028162 | -0.021157 | -0.01586 | -0.000359 | 0.085583 | -0.021514 | 121.3963 | 121.3583 | 121.3568 | 121.2655 | 0.11691 | 0.24754 | 0.11302 | 0.18453 | 0.40566 | 0.32571 | 0.27639 | 0.28169 | 0.29719 | 0.38313 | 0.27603 | 121.4375 | 121.3995 | 121.398 | 121.3067 | 0.15811 | 0.28874 | 0.15422 | 0.22573 | 121.2794 | 121.2833 | 121.2399 | 121.2438
1777.125 | 121.875 | -0.26093 | 121.4676 | 0.11727 | 0.019004 | -0.021157 | -0.020438 | -0.000359 | 0.081005 | -0.016936 | 121.3963 | 121.3583 | 121.3706 | 121.2746 | 0.10775 | 0.24297 | 0.11302 | 0.1708 | 0.3782 | 0.27993 | 0.23977 | 0.24049 | 0.26057 | 0.34193 | 0.24399 | 121.4375 | 121.3995 | 121.4118 | 121.3158 | 0.14895 | 0.28417 | 0.15422 | 0.212 | 121.2886 | 121.2833 | 121.2628 | 121.2576
1778.875 | 121.8018 | -0.31586 | 121.5225 | 0.12185 | 0.028162 | -0.016578 | -0.020438 | -0.000359 | 0.076426 | -0.012357 | 121.4101 | 121.3675 | 121.3706 | 121.2883 | 0.11233 | 0.24297 | 0.11302 | 0.16622 | 0.43771 | 0.34402 | 0.29928 | 0.29542 | 0.3155 | 0.39228 | 0.3035 | 121.4513 | 121.4087 | 121.4118 | 121.3295 | 0.15353 | 0.28417 | 0.15422 | 0.20742 | 121.2978 | 121.2971 | 121.2582 | 121.2576
1780.6406 | 121.9208 | -0.26093 | 121.4767 | 0.11727 | 0.03274 | -0.016578 | -0.020438 | 0.004219 | 0.085583 | -0.026092 | 121.4192 | 121.3721 | 121.3843 | 121.2975 | 0.10317 | 0.23381 | 0.10845 | 0.16622 | 0.3782 | 0.29367 | 0.24435 | 0.24049 | 0.26514 | 0.34651 | 0.23483 | 121.4604 | 121.4133 | 121.4255 | 121.3387 | 0.14437 | 0.27501 | 0.14965 | 0.20742 | 121.3161 | 121.3108 | 121.2811 | 121.2759
1782.3906 | 121.8979 | -0.24719 | 121.4859 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.016936 | 121.4238 | 121.3858 | 121.3843 | 121.3021 | 0.098596 | 0.22923 | 0.10387 | 0.16164 | 0.36904 | 0.27077 | 0.22603 | 0.22675 | 0.25141 | 0.3282 | 0.23026 | 121.465 | 121.427 | 121.4255 | 121.3433 | 0.1398 | 0.27043 | 0.14507 | 0.20284 | 121.3252 | 121.32 | 121.2857 | 121.2804
1784.1406 | 121.8338 | -0.27466 | 121.5408 | 0.12185 | 0.023583 | -0.016578 | -0.01586 | -0.000359 | 0.085583 | -0.021514 | 121.433 | 121.3904 | 121.398 | 121.3067 | 0.089439 | 0.22465 | 0.10845 | 0.16164 | 0.39651 | 0.29824 | 0.25808 | 0.2588 | 0.2743 | 0.36024 | 0.25314 | 121.4742 | 121.4316 | 121.4392 | 121.3479 | 0.13064 | 0.26585 | 0.14965 | 0.20284 | 121.3435 | 121.3245 | 121.3086 | 121.2896
1785.8438 | 121.7926 | -0.29755 | 121.5271 | 0.12185 | 0.023583 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.016936 | 121.4376 | 121.4041 | 121.4026 | 121.3204 | 0.098596 | 0.2155 | 0.10387 | 0.15706 | 0.4194 | 0.32113 | 0.27181 | 0.28169 | 0.29719 | 0.38313 | 0.28061 | 121.4788 | 121.4453 | 121.4438 | 121.3616 | 0.1398 | 0.2567 | 0.14507 | 0.19826 | 121.339 | 121.3337 | 121.304 | 121.2988
1787.5938 | 121.9391 | -0.24719 | 121.5134 | 0.12643 | 0.023583 | -0.016578 | -0.025017 | -0.009515 | 0.071848 | -0.021514 | 121.4513 | 121.4133 | 121.4164 | 121.325 | 0.094017 | 0.22008 | 0.090132 | 0.14791 | 0.37362 | 0.27077 | 0.23061 | 0.22217 | 0.23768 | 0.31904 | 0.22568 | 121.4925 | 121.4545 | 121.4576 | 121.3662 | 0.13522 | 0.26128 | 0.13133 | 0.18911 | 121.3573 | 121.3612 | 121.3223 | 121.3262
1789.3438 | 121.9025 | -0.25177 | 121.5363 | 0.12643 | 0.023583 | -0.030314 | -0.020438 | 0.008797 | 0.076426 | -0.03067 | 121.4513 | 121.4133 | 121.4255 | 121.3341 | 0.089439 | 0.21092 | 0.09471 | 0.15249 | 0.3782 | 0.27535 | 0.22146 | 0.23133 | 0.26057 | 0.3282 | 0.2211 | 121.4925 | 121.4545 | 121.4667 | 121.3753 | 0.13064 | 0.25212 | 0.13591 | 0.19368 | 121.3618 | 121.3566 | 121.3361 | 121.3308
1791.125 | 121.8475 | -0.27008 | 121.5546 | 0.11269 | 0.028162 | -0.016578 | -0.01586 | 0.004219 | 0.076426 | -0.016936 | 121.4604 | 121.4225 | 121.4118 | 121.3341 | 0.089439 | 0.21092 | 0.085554 | 0.15249 | 0.38278 | 0.29824 | 0.2535 | 0.25422 | 0.2743 | 0.34651 | 0.25315 | 121.5016 | 121.4637 | 121.453 | 121.3753 | 0.13064 | 0.25212 | 0.12675 | 0.19368 | 121.371 | 121.3749 | 121.3223 | 121.3262
1792.8281 | 121.843 | -0.27924 | 121.5179 | 0.11727 | 0.03274 | -0.016578 | -0.01586 | 0.004219 | 0.081005 | -0.026092 | 121.4742 | 121.4316 | 121.4255 | 121.3433 | 0.084861 | 0.20634 | 0.080975 | 0.13875 | 0.39651 | 0.31198 | 0.26266 | 0.26338 | 0.28345 | 0.36024 | 0.25314 | 121.5154 | 121.4728 | 121.4667 | 121.3845 | 0.12606 | 0.24754 | 0.12217 | 0.17995 | 121.3893 | 121.3932 | 121.3407 | 121.3445
1794.5938 | 121.8704 | -0.27466 | 121.5866 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.026092 | 121.4742 | 121.4316 | 121.4393 | 121.357 | 0.080283 | 0.20634 | 0.080975 | 0.13875 | 0.38735 | 0.30282 | 0.2535 | 0.2588 | 0.28346 | 0.35566 | 0.24857 | 121.5154 | 121.4728 | 121.4804 | 121.3982 | 0.12148 | 0.24754 | 0.12217 | 0.17995 | 121.3939 | 121.3932 | 121.359 | 121.3583
1796.3438 | 121.907 | -0.23346 | 121.5637 | 0.12185 | 0.019004 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 121.4879 | 121.4453 | 121.4438 | 121.3616 | 0.075705 | 0.19719 | 0.085554 | 0.13875 | 0.35531 | 0.25246 | 0.21688 | 0.2176 | 0.23768 | 0.31904 | 0.2211 | 121.5291 | 121.4865 | 121.485 | 121.4028 | 0.1169 | 0.23839 | 0.12675 | 0.17995 | 121.4122 | 121.4024 | 121.3681 | 121.3583
1798.0469 | 121.9254 | -0.2243 | 121.5363 | 0.12185 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 121.4925 | 121.4453 | 121.4438 | 121.3616 | 0.080283 | 0.19719 | 0.076397 | 0.12959 | 0.34615 | 0.24331 | 0.20773 | 0.21302 | 0.22852 | 0.30989 | 0.20737 | 121.5337 | 121.4865 | 121.485 | 121.4028 | 0.12148 | 0.23839 | 0.1176 | 0.17079 | 121.4122 | 121.4161 | 121.3635 | 121.3674
1799.7969 | 121.8246 | -0.27924 | 121.5866 | 0.12185 | 0.028162 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 121.4833 | 121.4591 | 121.453 | 121.3662 | 0.066548 | 0.19261 | 0.076397 | 0.12502 | 0.40109 | 0.3074 | 0.2535 | 0.26338 | 0.28345 | 0.36024 | 0.2623 | 121.5245 | 121.5003 | 121.4942 | 121.4074 | 0.10775 | 0.23381 | 0.1176 | 0.16622 | 121.4168 | 121.4069 | 121.3864 | 121.3766
1801.5469 | 121.9025 | -0.23804 | 121.5408 | 0.12643 | 0.014425 | -0.021157 | -0.020438 | -0.004937 | 0.076426 | -0.021514 | 121.4971 | 121.4637 | 121.4621 | 121.3708 | 0.075705 | 0.18803 | 0.071818 | 0.12502 | 0.36447 | 0.25246 | 0.21688 | 0.2176 | 0.2331 | 0.31446 | 0.21652 | 121.5383 | 121.5049 | 121.5033 | 121.412 | 0.1169 | 0.22923 | 0.11302 | 0.16622 | 121.4214 | 121.4253 | 121.3864 | 121.3903
1803.25 | 121.875 | -0.25177 | 121.5729 | 0.12643 | 0.028162 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.016936 | 121.5062 | 121.4728 | 121.4713 | 121.3799 | 0.071126 | 0.19261 | 0.071818 | 0.12502 | 0.3782 | 0.27993 | 0.23061 | 0.24507 | 0.25599 | 0.33277 | 0.23483 | 121.5474 | 121.514 | 121.5125 | 121.4211 | 0.11232 | 0.23381 | 0.11302 | 0.16622 | 121.4351 | 121.4344 | 121.4002 | 121.3995
1805 | 121.8979 | -0.22888 | 121.5637 | 0.12185 | 0.028162 | -0.025735 | -0.025017 | 0.004219 | 0.081005 | -0.016936 | 121.5062 | 121.4728 | 121.4667 | 121.3845 | 0.06197 | 0.18345 | 0.06724 | 0.12044 | 0.35073 | 0.25704 | 0.20315 | 0.20386 | 0.2331 | 0.30989 | 0.21195 | 121.5474 | 121.514 | 121.5079 | 121.4257 | 0.10317 | 0.22465 | 0.10844 | 0.16164 | 121.4443 | 121.439 | 121.4047 | 121.3995
1806.75 | 121.8887 | -0.23804 | 121.6095 | 0.11727 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 121.5154 | 121.4866 | 121.4805 | 121.3937 | 0.066548 | 0.18345 | 0.071818 | 0.12044 | 0.35531 | 0.2662 | 0.21688 | 0.22676 | 0.24683 | 0.31904 | 0.21652 | 121.5566 | 121.5278 | 121.5217 | 121.4349 | 0.10775 | 0.22465 | 0.11302 | 0.16164 | 121.4488 | 121.4436 | 121.4139 | 121.4086
1808.4375 | 121.8887 | -0.23346 | 121.5958 | 0.12185 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 121.52 | 121.4728 | 121.485 | 121.3937 | 0.057392 | 0.17887 | 0.06724 | 0.12044 | 0.35531 | 0.26162 | 0.2123 | 0.22218 | 0.24226 | 0.31446 | 0.21194 | 121.5612 | 121.514 | 121.5262 | 121.4349 | 0.098591 | 0.22007 | 0.10844 | 0.16164 | 121.4626 | 121.4527 | 121.4276 | 121.4178
1810.1875 | 121.8384 | -0.24261 | 121.6232 | 0.12185 | 0.03274 | -0.016578 | -0.011281 | 0.004219 | 0.090161 | -0.016936 | 121.5291 | 121.4957 | 121.4896 | 121.4028 | 0.057392 | 0.1743 | 0.06724 | 0.12044 | 0.36447 | 0.27536 | 0.22604 | 0.23133 | 0.24683 | 0.33278 | 0.22568 | 121.5703 | 121.5369 | 121.5308 | 121.444 | 0.098591 | 0.21549 | 0.10844 | 0.16164 | 121.4717 | 121.4619 | 121.4322 | 121.4224
1811.875 | 121.8796 | -0.24261 | 121.6187 | 0.12185 | 0.028162 | -0.021157 | -0.020438 | -0.000359 | 0.085583 | -0.026092 | 121.5245 | 121.4957 | 121.4988 | 121.4074 | 0.06197 | 0.18345 | 0.071818 | 0.12044 | 0.36447 | 0.27078 | 0.22146 | 0.22218 | 0.24226 | 0.3282 | 0.21652 | 121.5657 | 121.5369 | 121.54 | 121.4486 | 0.10317 | 0.22465 | 0.11302 | 0.16164 | 121.4626 | 121.4527 | 121.4368 | 121.427
1813.5781 | 121.8338 | -0.23804 | 121.6324 | 0.12185 | 0.028162 | -0.012 | -0.006703 | -0.000359 | 0.085583 | -0.021514 | 121.5383 | 121.5003 | 121.4942 | 121.412 | 0.057392 | 0.1743 | 0.062662 | 0.11586 | 0.35989 | 0.2662 | 0.22604 | 0.23133 | 0.23768 | 0.32362 | 0.21652 | 121.5795 | 121.5415 | 121.5354 | 121.4532 | 0.098591 | 0.21549 | 0.10386 | 0.15706 | 121.4809 | 121.4756 | 121.4368 | 121.4315
1815.3281 | 121.962 | -0.20599 | 121.5912 | 0.11269 | 0.019004 | -0.021157 | -0.01586 | -0.000359 | 0.076426 | -0.021514 | 121.5383 | 121.5003 | 121.4942 | 121.4211 | 0.048236 | 0.1743 | 0.062662 | 0.12044 | 0.31869 | 0.225 | 0.18484 | 0.19013 | 0.20564 | 0.28242 | 0.18448 | 121.5795 | 121.5415 | 121.5354 | 121.4623 | 0.089435 | 0.21549 | 0.10386 | 0.16164 | 121.49 | 121.4756 | 121.446 | 121.4315
1817.0938 | 121.8658 | -0.23346 | 121.6232 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.021514 | 121.5474 | 121.514 | 121.5033 | 121.4211 | 0.06197 | 0.16056 | 0.062662 | 0.11586 | 0.35531 | 0.2662 | 0.2123 | 0.21302 | 0.23768 | 0.31446 | 0.21194 | 121.5886 | 121.5552 | 121.5445 | 121.4623 | 0.10317 | 0.20176 | 0.10386 | 0.15706 | 121.4855 | 121.4848 | 121.4414 | 121.4407
1818.7969 | 121.9025 | -0.24261 | 121.637 | 0.12185 | 0.028162 | -0.021157 | -0.011281 | -0.000359 | 0.076426 | -0.021514 | 121.5429 | 121.5094 | 121.5033 | 121.4257 | 0.057392 | 0.1743 | 0.062662 | 0.11128 | 0.36447 | 0.27078 | 0.22146 | 0.23133 | 0.24226 | 0.31904 | 0.2211 | 121.5841 | 121.5506 | 121.5445 | 121.4669 | 0.098591 | 0.21549 | 0.10386 | 0.15248 | 121.4855 | 121.4802 | 121.446 | 121.4407
1820.5469 | 121.9116 | -0.2243 | 121.637 | 0.11727 | 0.028162 | -0.021157 | -0.01586 | -0.004937 | 0.076426 | -0.021514 | 121.5566 | 121.514 | 121.5262 | 121.4349 | 0.048236 | 0.16056 | 0.053505 | 0.11128 | 0.34158 | 0.25247 | 0.20315 | 0.20844 | 0.21937 | 0.30073 | 0.20279 | 121.5978 | 121.5552 | 121.5674 | 121.4761 | 0.089435 | 0.20176 | 0.094704 | 0.15248 | 121.5084 | 121.5031 | 121.478 | 121.4727
1822.2969 | 121.875 | -0.24261 | 121.6599 | 0.12185 | 0.023583 | -0.021157 | -0.020438 | -0.004937 | 0.076426 | -0.021514 | 121.5566 | 121.5232 | 121.5217 | 121.4395 | 0.048236 | 0.16056 | 0.053505 | 0.10213 | 0.36447 | 0.2662 | 0.22146 | 0.22218 | 0.23768 | 0.31904 | 0.2211 | 121.5978 | 121.5644 | 121.5629 | 121.4807 | 0.089435 | 0.20176 | 0.094704 | 0.14332 | 121.5084 | 121.5031 | 121.4734 | 121.4682
1823.9844 | 121.962 | -0.19684 | 121.6324 | 0.11727 | 0.028162 | -0.016578 | -0.020438 | 0.004219 | 0.081005 | -0.026092 | 121.5612 | 121.5278 | 121.5217 | 121.444 | 0.048236 | 0.16056 | 0.053505 | 0.097548 | 0.31411 | 0.225 | 0.18026 | 0.1764 | 0.20106 | 0.27784 | 0.17075 | 121.6024 | 121.569 | 121.5629 | 121.4852 | 0.089435 | 0.20176 | 0.094704 | 0.13875 | 121.5129 | 121.5077 | 121.4734 | 121.4682
1825.7344 | 121.8979 | -0.21057 | 121.6599 | 0.12185 | 0.03274 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.021514 | 121.5749 | 121.5323 | 121.54 | 121.444 | 0.039079 | 0.16056 | 0.058083 | 0.09297 | 0.33242 | 0.24331 | 0.18484 | 0.19471 | 0.21479 | 0.29158 | 0.18906 | 121.6161 | 121.5735 | 121.5812 | 121.4852 | 0.080278 | 0.20176 | 0.099282 | 0.13417 | 121.5358 | 121.5168 | 121.5009 | 121.4819
1827.4844 | 121.9894 | -0.18768 | 121.6232 | 0.10812 | 0.023583 | -0.025735 | -0.020438 | 0.004219 | 0.081005 | -0.016936 | 121.5749 | 121.5369 | 121.5354 | 121.4532 | 0.048236 | 0.16972 | 0.048926 | 0.09297 | 0.2958 | 0.21127 | 0.16195 | 0.16724 | 0.1919 | 0.26869 | 0.17075 | 121.6161 | 121.5781 | 121.5766 | 121.4944 | 0.089435 | 0.21092 | 0.090125 | 0.13417 | 121.5267 | 121.526 | 121.4872 | 121.4865
1829.25 | 121.8521 | -0.25635 | 121.6873 | 0.12643 | 0.03274 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.012357 | 121.5703 | 121.5369 | 121.5354 | 121.4532 | 0.039079 | 0.16056 | 0.048926 | 0.088392 | 0.38278 | 0.28909 | 0.23977 | 0.24049 | 0.26515 | 0.34651 | 0.24399 | 121.6115 | 121.5781 | 121.5766 | 121.4944 | 0.080278 | 0.20176 | 0.090125 | 0.12959 | 121.5312 | 121.5214 | 121.4963 | 121.4865
1830.9375 | 121.9162 | -0.21973 | 121.6599 | 0.11727 | 0.028162 | -0.012 | -0.025017 | -0.000359 | 0.081005 | -0.016936 | 121.5886 | 121.5461 | 121.54 | 121.4578 | 0.043657 | 0.15598 | 0.053505 | 0.088392 | 0.337 | 0.24789 | 0.20773 | 0.19471 | 0.21937 | 0.30073 | 0.20279 | 121.6298 | 121.5873 | 121.5812 | 121.499 | 0.084856 | 0.19718 | 0.094704 | 0.12959 | 121.545 | 121.5351 | 121.4963 | 121.4865
1832.6875 | 122.0169 | -0.17395 | 121.6324 | 0.11269 | 0.03274 | -0.021157 | -0.025017 | -0.000359 | 0.081005 | -0.021514 | 121.5886 | 121.5507 | 121.5446 | 121.4578 | 0.043657 | 0.15141 | 0.044348 | 0.088392 | 0.28664 | 0.20669 | 0.15279 | 0.14893 | 0.17359 | 0.25495 | 0.15244 | 121.6298 | 121.5919 | 121.5858 | 121.499 | 0.084856 | 0.19261 | 0.085547 | 0.12959 | 121.545 | 121.5443 | 121.5009 | 121.5002
1834.4375 | 121.994 | -0.16479 | 121.6415 | 0.12185 | 0.019004 | -0.030314 | -0.020438 | -0.000359 | 0.085583 | -0.03067 | 121.5932 | 121.5552 | 121.5583 | 121.4669 | 0.043657 | 0.14683 | 0.048926 | 0.088392 | 0.28665 | 0.1838 | 0.13448 | 0.14436 | 0.16444 | 0.25038 | 0.13412 | 121.6344 | 121.5964 | 121.5995 | 121.5081 | 0.084856 | 0.18803 | 0.090125 | 0.12959 | 121.5496 | 121.5443 | 121.5146 | 121.5094
1836.1875 | 121.9528 | -0.20599 | 121.669 | 0.11727 | 0.028162 | -0.030314 | -0.011281 | 0.004219 | 0.076426 | -0.021514 | 121.6024 | 121.5552 | 121.5537 | 121.4669 | 0.039079 | 0.15141 | 0.048926 | 0.088392 | 0.32327 | 0.23416 | 0.17568 | 0.19471 | 0.21021 | 0.28242 | 0.18448 | 121.6436 | 121.5964 | 121.5949 | 121.5081 | 0.080278 | 0.19261 | 0.090125 | 0.12959 | 121.5633 | 121.5535 | 121.5146 | 121.5048
1837.875 | 121.8887 | -0.20599 | 121.6827 | 0.11727 | 0.028162 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.021514 | 121.5978 | 121.5598 | 121.5629 | 121.4761 | 0.034501 | 0.15141 | 0.044348 | 0.079235 | 0.32327 | 0.23416 | 0.18484 | 0.19013 | 0.21021 | 0.29158 | 0.18448 | 121.639 | 121.601 | 121.6041 | 121.5173 | 0.0757 | 0.19261 | 0.085547 | 0.12043 | 121.5633 | 121.5535 | 121.5284 | 121.5185
1839.625 | 122.0215 | -0.17395 | 121.637 | 0.11269 | 0.028162 | -0.016578 | -0.020438 | -0.000359 | 0.076426 | -0.021514 | 121.5932 | 121.5644 | 121.5583 | 121.4715 | 0.043657 | 0.14225 | 0.048926 | 0.079235 | 0.28664 | 0.20211 | 0.15737 | 0.15351 | 0.17359 | 0.25038 | 0.15244 | 121.6344 | 121.6056 | 121.5995 | 121.5127 | 0.084856 | 0.18345 | 0.090125 | 0.12043 | 121.5496 | 121.5443 | 121.5146 | 121.5094
1841.3594 | 121.8796 | -0.21973 | 121.6919 | 0.11727 | 0.03274 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.012357 | 121.607 | 121.5736 | 121.5629 | 121.4807 | 0.039079 | 0.14683 | 0.044348 | 0.088392 | 0.337 | 0.25247 | 0.20315 | 0.20387 | 0.22852 | 0.30531 | 0.20737 | 121.6482 | 121.6148 | 121.6041 | 121.5219 | 0.080278 | 0.18803 | 0.085547 | 0.12959 | 121.5679 | 121.5626 | 121.5238 | 121.5185
1843.0469 | 122.0352 | -0.17853 | 121.6599 | 0.11727 | 0.023583 | -0.021157 | -0.025017 | -0.000359 | 0.071848 | -0.021514 | 121.6115 | 121.5736 | 121.572 | 121.4807 | 0.034501 | 0.14225 | 0.048926 | 0.083814 | 0.2958 | 0.20211 | 0.15737 | 0.15351 | 0.17817 | 0.25038 | 0.15701 | 121.6527 | 121.6148 | 121.6132 | 121.5219 | 0.0757 | 0.18345 | 0.090125 | 0.12501 | 121.577 | 121.5626 | 121.5375 | 121.5231
1844.75 | 122.0306 | -0.17853 | 121.6599 | 0.11727 | 0.023583 | -0.030314 | -0.011281 | -0.000359 | 0.081005 | -0.021514 | 121.6115 | 121.5827 | 121.5812 | 121.4852 | 0.034501 | 0.14683 | 0.03977 | 0.074657 | 0.2958 | 0.20211 | 0.14821 | 0.16725 | 0.17817 | 0.25953 | 0.15701 | 121.6527 | 121.6239 | 121.6224 | 121.5264 | 0.0757 | 0.18803 | 0.080969 | 0.11586 | 121.577 | 121.5718 | 121.5467 | 121.5414
1846.5 | 121.8933 | -0.21515 | 121.7285 | 0.12185 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.076426 | -0.012357 | 121.6253 | 121.5736 | 121.5766 | 121.4898 | 0.034501 | 0.13767 | 0.044348 | 0.083814 | 0.337 | 0.23873 | 0.19857 | 0.19929 | 0.22395 | 0.29158 | 0.20279 | 121.6665 | 121.6148 | 121.6178 | 121.531 | 0.0757 | 0.17887 | 0.085547 | 0.12501 | 121.5908 | 121.5809 | 121.5421 | 121.5323
1848.2812 | 122.0123 | -0.18768 | 121.6965 | 0.12185 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.03067 | 121.6161 | 121.5827 | 121.5812 | 121.5036 | 0.025345 | 0.13767 | 0.035191 | 0.083814 | 0.30953 | 0.21584 | 0.16653 | 0.17182 | 0.19648 | 0.26869 | 0.15701 | 121.6573 | 121.6239 | 121.6224 | 121.5448 | 0.066544 | 0.17887 | 0.07639 | 0.12501 | 121.5908 | 121.5809 | 121.5558 | 121.546
1849.9688 | 121.9757 | -0.1831 | 121.6873 | 0.11269 | 0.028162 | -0.016578 | -0.020438 | -0.000359 | 0.081005 | -0.021514 | 121.6253 | 121.5873 | 121.5812 | 121.5036 | 0.025345 | 0.14225 | 0.044348 | 0.074657 | 0.2958 | 0.21127 | 0.16653 | 0.16267 | 0.18275 | 0.26411 | 0.16159 | 121.6665 | 121.6285 | 121.6224 | 121.5448 | 0.066544 | 0.18345 | 0.085547 | 0.11586 | 121.5999 | 121.5809 | 121.5558 | 121.5368
1851.7031 | 121.8933 | -0.21515 | 121.701 | 0.11269 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 121.6207 | 121.5919 | 121.5858 | 121.4944 | 0.034501 | 0.13767 | 0.035191 | 0.079235 | 0.32784 | 0.23415 | 0.19857 | 0.20387 | 0.21937 | 0.30073 | 0.19364 | 121.6619 | 121.6331 | 121.627 | 121.5356 | 0.0757 | 0.17887 | 0.07639 | 0.12043 | 121.5862 | 121.5855 | 121.5513 | 121.5506
1853.4531 | 121.9437 | -0.19684 | 121.6827 | 0.12185 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 121.6298 | 121.5919 | 121.5903 | 121.5036 | 0.029923 | 0.13309 | 0.03977 | 0.074657 | 0.31869 | 0.22042 | 0.18026 | 0.18556 | 0.20564 | 0.28242 | 0.18448 | 121.671 | 121.6331 | 121.6315 | 121.5448 | 0.071122 | 0.17429 | 0.080969 | 0.11586 | 121.5999 | 121.5901 | 121.5604 | 121.5506
1855.2188 | 121.9025 | -0.21515 | 121.7194 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | -0.000359 | 0.085583 | -0.021514 | 121.6253 | 121.5964 | 121.5903 | 121.5081 | 0.025345 | 0.13767 | 0.03977 | 0.074657 | 0.33242 | 0.23873 | 0.19857 | 0.20387 | 0.21479 | 0.30073 | 0.19364 | 121.6665 | 121.6376 | 121.6315 | 121.5493 | 0.066544 | 0.17887 | 0.080969 | 0.11586 | 121.5999 | 121.5855 | 121.565 | 121.5506
1856.9062 | 121.994 | -0.16937 | 121.6324 | 0.10812 | 0.028162 | -0.025735 | -0.011281 | -0.000359 | 0.081005 | -0.016936 | 121.5978 | 121.5644 | 121.5583 | 121.4715 | 0.10775 | 0.14225 | 0.044348 | 0.079235 | 0.27749 | 0.19753 | 0.14364 | 0.15809 | 0.16901 | 0.25038 | 0.15244 | 121.639 | 121.6056 | 121.5995 | 121.5127 | 0.14895 | 0.18345 | 0.085547 | 0.12043 | 121.49 | 121.5535 | 121.4505 | 121.5139
1858.6562 | 121.962 | -0.19226 | 121.5958 | 0.11727 | 0.019004 | -0.012 | -0.01586 | -0.004937 | 0.081005 | -0.026092 | 121.5657 | 121.5232 | 121.5217 | 121.4395 | 0.11233 | 0.15141 | 0.048926 | 0.083814 | 0.30953 | 0.21126 | 0.18026 | 0.1764 | 0.18732 | 0.27327 | 0.16617 | 121.6069 | 121.5644 | 121.5629 | 121.4807 | 0.15353 | 0.19261 | 0.090125 | 0.12501 | 121.4534 | 121.5168 | 121.4093 | 121.4727
1860.3906 | 121.8018 | -0.21057 | 121.6232 | 0.12185 | 0.023583 | -0.021157 | -0.002124 | 0.008797 | 0.081005 | -0.016936 | 121.5383 | 121.5003 | 121.5033 | 121.4028 | 0.10317 | 0.14225 | 0.044348 | 0.083814 | 0.33242 | 0.23415 | 0.18941 | 0.20845 | 0.21937 | 0.29158 | 0.19364 | 121.5795 | 121.5415 | 121.5445 | 121.444 | 0.14437 | 0.18345 | 0.085547 | 0.12501 | 121.4351 | 121.4939 | 121.4002 | 121.459
1862.1562 | 121.8109 | -0.21057 | 121.6324 | 0.11727 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.016936 | 121.5245 | 121.482 | 121.4805 | 121.3937 | 0.10775 | 0.13767 | 0.03977 | 0.079235 | 0.32784 | 0.23415 | 0.18941 | 0.19471 | 0.21937 | 0.29615 | 0.19364 | 121.5657 | 121.5232 | 121.5217 | 121.4349 | 0.14895 | 0.17887 | 0.080969 | 0.12043 | 121.4168 | 121.4848 | 121.3727 | 121.4407
1863.8438 | 121.9162 | -0.17395 | 121.5637 | 0.10812 | 0.023583 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.021514 | 121.5062 | 121.4774 | 121.4759 | 121.3845 | 0.10775 | 0.14683 | 0.044348 | 0.083814 | 0.28207 | 0.19753 | 0.16195 | 0.16725 | 0.17817 | 0.25038 | 0.15244 | 121.5474 | 121.5186 | 121.5171 | 121.4257 | 0.14895 | 0.18803 | 0.085547 | 0.12501 | 121.3985 | 121.4619 | 121.3681 | 121.4315
1865.5938 | 121.8521 | -0.17853 | 121.5454 | 0.12185 | 0.03274 | -0.021157 | -0.020438 | -0.000359 | 0.081005 | -0.021514 | 121.5017 | 121.4728 | 121.4621 | 121.3845 | 0.11233 | 0.14225 | 0.03977 | 0.079235 | 0.30038 | 0.21127 | 0.15737 | 0.15809 | 0.17817 | 0.25953 | 0.15701 | 121.5429 | 121.514 | 121.5033 | 121.4257 | 0.15353 | 0.18345 | 0.080969 | 0.12043 | 121.3893 | 121.4619 | 121.3498 | 121.4224
1867.3438 | 121.8338 | -0.19226 | 121.5683 | 0.12185 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.076426 | -0.016936 | 121.4925 | 121.4545 | 121.453 | 121.3662 | 0.10317 | 0.14683 | 0.03977 | 0.083814 | 0.31411 | 0.21584 | 0.1711 | 0.18098 | 0.19648 | 0.26869 | 0.17532 | 121.5337 | 121.4957 | 121.4942 | 121.4074 | 0.14437 | 0.18803 | 0.080969 | 0.12501 | 121.3893 | 121.4527 | 121.3498 | 121.4132
1869.1094 | 121.8338 | -0.18768 | 121.5637 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.071848 | -0.021514 | 121.4879 | 121.4591 | 121.4484 | 121.357 | 0.10317 | 0.14683 | 0.03977 | 0.083814 | 0.30496 | 0.21127 | 0.16653 | 0.1764 | 0.1919 | 0.25953 | 0.16617 | 121.5291 | 121.5003 | 121.4896 | 121.3982 | 0.14437 | 0.18803 | 0.080969 | 0.12501 | 121.3847 | 121.4481 | 121.3452 | 121.4086
1870.7969 | 121.7651 | -0.21057 | 121.5317 | 0.11727 | 0.023583 | -0.012 | -0.01586 | 0.004219 | 0.081005 | -0.012357 | 121.4925 | 121.4499 | 121.4393 | 121.3662 | 0.10317 | 0.13767 | 0.03977 | 0.079235 | 0.32784 | 0.23415 | 0.19857 | 0.19471 | 0.21479 | 0.29158 | 0.19821 | 121.5337 | 121.4911 | 121.4804 | 121.4074 | 0.14437 | 0.17887 | 0.080969 | 0.12043 | 121.3893 | 121.4527 | 121.3361 | 121.3995
1872.5469 | 121.7606 | -0.20142 | 121.5408 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 121.4788 | 121.4408 | 121.4347 | 121.3525 | 0.098596 | 0.15141 | 0.03977 | 0.079235 | 0.31869 | 0.225 | 0.18484 | 0.19013 | 0.21021 | 0.28242 | 0.18448 | 121.52 | 121.482 | 121.4759 | 121.3937 | 0.1398 | 0.19261 | 0.080969 | 0.12043 | 121.3802 | 121.439 | 121.3361 | 121.3949
1874.2969 | 121.7926 | -0.2243 | 121.5317 | 0.11727 | 0.03274 | -0.016578 | -0.020438 | 0.004219 | 0.081005 | -0.021514 | 121.4742 | 121.4362 | 121.4301 | 121.3479 | 0.098596 | 0.13767 | 0.035191 | 0.083814 | 0.34158 | 0.25704 | 0.20773 | 0.20387 | 0.22852 | 0.30531 | 0.20279 | 121.5154 | 121.4774 | 121.4713 | 121.3891 | 0.1398 | 0.17887 | 0.07639 | 0.12501 | 121.3756 | 121.439 | 121.3315 | 121.3949
1876 | 121.7834 | -0.20599 | 121.5729 | 0.12643 | 0.03274 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 121.4696 | 121.4362 | 121.4301 | 121.3433 | 0.10775 | 0.13767 | 0.03977 | 0.079235 | 0.33242 | 0.23873 | 0.19399 | 0.19929 | 0.20564 | 0.287 | 0.19822 | 121.5108 | 121.4774 | 121.4713 | 121.3845 | 0.14895 | 0.17887 | 0.080969 | 0.12043 | 121.3618 | 121.4298 | 121.3223 | 121.3903
1877.75 | 121.875 | -0.19226 | 121.5225 | 0.12643 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.071848 | -0.021514 | 121.4559 | 121.4179 | 121.4164 | 121.3341 | 0.098596 | 0.14683 | 0.044348 | 0.074657 | 0.31869 | 0.21584 | 0.1711 | 0.17182 | 0.19648 | 0.26411 | 0.17075 | 121.4971 | 121.4591 | 121.4576 | 121.3753 | 0.1398 | 0.18803 | 0.085547 | 0.11586 | 121.3573 | 121.4115 | 121.3178 | 121.372
1879.5156 | 121.7377 | -0.21057 | 121.5317 | 0.11269 | 0.028162 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.016936 | 121.4604 | 121.4179 | 121.4164 | 121.3341 | 0.094017 | 0.13767 | 0.044348 | 0.083814 | 0.32327 | 0.23873 | 0.18941 | 0.20387 | 0.21479 | 0.29158 | 0.19364 | 121.5016 | 121.4591 | 121.4576 | 121.3753 | 0.13522 | 0.17887 | 0.085547 | 0.12501 | 121.3664 | 121.4161 | 121.3223 | 121.372
1881.2656 | 121.8109 | -0.1831 | 121.5271 | 0.12185 | 0.023583 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.007779 | 121.4559 | 121.4087 | 121.4164 | 121.3158 | 0.10775 | 0.13767 | 0.035191 | 0.079235 | 0.30496 | 0.20669 | 0.15737 | 0.16724 | 0.18732 | 0.26411 | 0.17533 | 121.4971 | 121.4499 | 121.4576 | 121.357 | 0.14895 | 0.17887 | 0.07639 | 0.12043 | 121.3481 | 121.4207 | 121.3086 | 121.3812
1882.9531 | 121.843 | -0.19226 | 121.5042 | 0.11269 | 0.028162 | -0.030314 | -0.01586 | -0.000359 | 0.076426 | -0.026092 | 121.4513 | 121.4179 | 121.4164 | 121.325 | 0.10317 | 0.14225 | 0.044348 | 0.079235 | 0.30495 | 0.22042 | 0.16195 | 0.1764 | 0.1919 | 0.26869 | 0.16617 | 121.4925 | 121.4591 | 121.4576 | 121.3662 | 0.14437 | 0.18345 | 0.085547 | 0.12043 | 121.3481 | 121.4069 | 121.3132 | 121.372
1884.7031 | 121.8109 | -0.18768 | 121.4676 | 0.10812 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.021514 | 121.4513 | 121.4179 | 121.4072 | 121.3296 | 0.10317 | 0.13767 | 0.044348 | 0.083814 | 0.2958 | 0.21127 | 0.16653 | 0.17182 | 0.1919 | 0.26869 | 0.16617 | 121.4925 | 121.4591 | 121.4484 | 121.3708 | 0.14437 | 0.17887 | 0.085547 | 0.12501 | 121.3481 | 121.4069 | 121.304 | 121.3629
1886.4531 | 121.7148 | -0.21515 | 121.5454 | 0.12643 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 121.4559 | 121.4041 | 121.4164 | 121.3204 | 0.098596 | 0.14225 | 0.044348 | 0.079235 | 0.34158 | 0.24331 | 0.19857 | 0.20387 | 0.22852 | 0.30531 | 0.19821 | 121.4971 | 121.4453 | 121.4576 | 121.3616 | 0.1398 | 0.18345 | 0.085547 | 0.12043 | 121.3573 | 121.4115 | 121.3178 | 121.372
1888.2031 | 121.7148 | -0.23804 | 121.5134 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | -0.000359 | 0.085583 | -0.03067 | 121.4421 | 121.3996 | 121.398 | 121.3112 | 0.094017 | 0.13309 | 0.03977 | 0.074657 | 0.35073 | 0.2662 | 0.21688 | 0.22218 | 0.23768 | 0.32362 | 0.20737 | 121.4833 | 121.4408 | 121.4392 | 121.3524 | 0.13522 | 0.17429 | 0.080969 | 0.11586 | 121.3481 | 121.4024 | 121.304 | 121.3583
1889.8906 | 121.7697 | -0.20142 | 121.4996 | 0.11727 | 0.028162 | -0.025735 | -0.006703 | 0.004219 | 0.081005 | -0.016936 | 121.4421 | 121.4041 | 121.4026 | 121.3158 | 0.098596 | 0.14225 | 0.035191 | 0.083814 | 0.31869 | 0.22958 | 0.17568 | 0.19471 | 0.20564 | 0.28242 | 0.18448 | 121.4833 | 121.4453 | 121.4438 | 121.357 | 0.1398 | 0.18345 | 0.07639 | 0.12501 | 121.3435 | 121.4069 | 121.304 | 121.3674
1891.6406 | 121.7194 | -0.20599 | 121.5225 | 0.11727 | 0.03274 | -0.025735 | -0.006703 | -0.000359 | 0.081005 | -0.021514 | 121.4467 | 121.4087 | 121.4072 | 121.3158 | 0.10317 | 0.13309 | 0.03977 | 0.074657 | 0.32327 | 0.23873 | 0.18026 | 0.19929 | 0.20564 | 0.287 | 0.18448 | 121.4879 | 121.4499 | 121.4484 | 121.357 | 0.14437 | 0.17429 | 0.080969 | 0.11586 | 121.3435 | 121.4069 | 121.304 | 121.3674
1893.4062 | 121.8063 | -0.17853 | 121.4859 | 0.11727 | 0.028162 | -0.021157 | -0.020438 | -0.004937 | 0.076426 | -0.021514 | 121.4421 | 121.395 | 121.398 | 121.3204 | 0.098596 | 0.13767 | 0.035191 | 0.074657 | 0.2958 | 0.20669 | 0.15737 | 0.15809 | 0.17359 | 0.25495 | 0.15701 | 121.4833 | 121.4362 | 121.4392 | 121.3616 | 0.1398 | 0.17887 | 0.07639 | 0.11586 | 121.3435 | 121.4069 | 121.2994 | 121.3629
1895.1562 | 121.8338 | -0.14648 | 121.4859 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.026092 | 121.3872 | 121.3629 | 121.3568 | 121.27 | 0.071126 | 0.10562 | 0.012299 | 0.051766 | 0.25918 | 0.17007 | 0.12533 | 0.13978 | 0.15528 | 0.22749 | 0.12039 | 121.4284 | 121.4041 | 121.398 | 121.3112 | 0.11232 | 0.14682 | 0.053498 | 0.092965 | 121.3161 | 121.3749 | 121.2857 | 121.3445
1896.8438 | 121.843 | -0.16479 | 121.5454 | 0.11727 | 0.03274 | -0.025735 | -0.01586 | 0.008797 | 0.076426 | -0.03067 | 121.5657 | 121.5369 | 121.4759 | 121.3799 | 0.071126 | 0.1102 | 0.026035 | 0.060923 | 0.28207 | 0.19753 | 0.13906 | 0.14893 | 0.17359 | 0.24122 | 0.13412 | 121.6069 | 121.5781 | 121.5171 | 121.4211 | 0.11232 | 0.1514 | 0.067234 | 0.10212 | 121.4946 | 121.5397 | 121.4047 | 121.4498
1898.5938 | 121.8384 | -0.19226 | 121.6141 | 0.11269 | 0.028162 | -0.012 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 121.5932 | 121.5552 | 121.5033 | 121.412 | 0.075705 | 0.11478 | 0.035191 | 0.070079 | 0.30495 | 0.22042 | 0.18026 | 0.1764 | 0.19648 | 0.27784 | 0.17532 | 121.6344 | 121.5964 | 121.5445 | 121.4532 | 0.1169 | 0.15598 | 0.07639 | 0.11128 | 121.5175 | 121.558 | 121.4276 | 121.4682
1900.3594 | 121.875 | -0.16479 | 121.637 | 0.10812 | 0.028162 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.026092 | 121.607 | 121.5781 | 121.5171 | 121.4303 | 0.075705 | 0.11936 | 0.026035 | 0.065501 | 0.27291 | 0.19296 | 0.14822 | 0.14436 | 0.17359 | 0.25038 | 0.1387 | 121.6482 | 121.6193 | 121.5583 | 121.4715 | 0.1169 | 0.16056 | 0.067234 | 0.1067 | 121.5313 | 121.5809 | 121.4414 | 121.491
1902.1094 | 121.8796 | -0.18768 | 121.6507 | 0.12185 | 0.03274 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.012357 | 121.6253 | 121.5873 | 121.5354 | 121.4486 | 0.075705 | 0.11478 | 0.021456 | 0.060923 | 0.30953 | 0.22042 | 0.1711 | 0.18098 | 0.20106 | 0.26869 | 0.17533 | 121.6665 | 121.6285 | 121.5766 | 121.4898 | 0.1169 | 0.15598 | 0.062655 | 0.10212 | 121.5496 | 121.6038 | 121.4597 | 121.5139
1903.7969 | 121.8246 | -0.17395 | 121.637 | 0.11727 | 0.028162 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 121.6436 | 121.6056 | 121.5446 | 121.4578 | 0.075705 | 0.12394 | 0.026035 | 0.065501 | 0.29122 | 0.20211 | 0.16195 | 0.16725 | 0.18275 | 0.25953 | 0.16159 | 121.6848 | 121.6468 | 121.5858 | 121.499 | 0.1169 | 0.16514 | 0.067234 | 0.1067 | 121.5679 | 121.6176 | 121.4688 | 121.5185
1905.5469 | 121.8887 | -0.18768 | 121.6827 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.016936 | 121.639 | 121.6239 | 121.5583 | 121.4624 | 0.075705 | 0.11936 | 0.030613 | 0.065501 | 0.30496 | 0.21127 | 0.1711 | 0.17182 | 0.19648 | 0.26869 | 0.17075 | 121.6802 | 121.6651 | 121.5995 | 121.5036 | 0.1169 | 0.16056 | 0.071812 | 0.1067 | 121.5633 | 121.6084 | 121.4826 | 121.5277
1907.2969 | 121.962 | -0.15564 | 121.6644 | 0.11727 | 0.028162 | -0.025735 | -0.011281 | 0.013375 | 0.076426 | -0.021514 | 121.6619 | 121.6285 | 121.5629 | 121.4761 | 0.080283 | 0.11936 | 0.021456 | 0.060923 | 0.27291 | 0.1838 | 0.1299 | 0.14436 | 0.16901 | 0.23207 | 0.13413 | 121.7031 | 121.6697 | 121.6041 | 121.5173 | 0.12148 | 0.16056 | 0.062655 | 0.10212 | 121.5816 | 121.6404 | 121.4826 | 121.5414
1909 | 121.9849 | -0.15564 | 121.6415 | 0.11727 | 0.023583 | -0.012 | -0.011281 | 0.004219 | 0.076426 | -0.021514 | 121.6665 | 121.6377 | 121.572 | 121.4852 | 0.071126 | 0.11936 | 0.026035 | 0.060923 | 0.27291 | 0.17922 | 0.14364 | 0.14436 | 0.15986 | 0.23207 | 0.13413 | 121.7077 | 121.6789 | 121.6132 | 121.5264 | 0.11232 | 0.16056 | 0.067234 | 0.10212 | 121.5954 | 121.6404 | 121.5009 | 121.546
1910.75 | 121.875 | -0.20142 | 121.6965 | 0.11727 | 0.028162 | -0.021157 | -0.011281 | 0.013375 | 0.076426 | -0.012357 | 121.6619 | 121.6331 | 121.5674 | 121.4807 | 0.084861 | 0.12851 | 0.030613 | 0.060923 | 0.31869 | 0.22958 | 0.18026 | 0.19013 | 0.21479 | 0.27784 | 0.18906 | 121.7031 | 121.6743 | 121.6086 | 121.5219 | 0.12606 | 0.16971 | 0.071812 | 0.10212 | 121.577 | 121.6313 | 121.4826 | 121.5368
1912.5 | 121.9482 | -0.16937 | 121.6873 | 0.11269 | 0.023583 | -0.025735 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 121.6711 | 121.6331 | 121.572 | 121.4852 | 0.084861 | 0.12851 | 0.035191 | 0.060923 | 0.28207 | 0.19296 | 0.14364 | 0.15351 | 0.17817 | 0.25038 | 0.14786 | 121.7123 | 121.6743 | 121.6132 | 121.5264 | 0.12606 | 0.16971 | 0.07639 | 0.10212 | 121.5862 | 121.6359 | 121.4872 | 121.5368
1914.25 | 121.9849 | -0.16479 | 121.6965 | 0.11269 | 0.028162 | -0.021157 | -0.020438 | 0.004219 | 0.076426 | -0.021514 | 121.6802 | 121.6514 | 121.5858 | 121.4898 | 0.089439 | 0.12851 | 0.026035 | 0.065501 | 0.27749 | 0.19296 | 0.14364 | 0.14436 | 0.16901 | 0.24122 | 0.14328 | 121.7214 | 121.6926 | 121.627 | 121.531 | 0.13064 | 0.16971 | 0.067234 | 0.1067 | 121.5908 | 121.6542 | 121.4963 | 121.5597
1915.9375 | 121.9757 | -0.13733 | 121.6919 | 0.11269 | 0.03274 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.026092 | 121.6894 | 121.6514 | 121.5858 | 121.5081 | 0.084861 | 0.12394 | 0.035191 | 0.070079 | 0.25002 | 0.17007 | 0.11617 | 0.12605 | 0.14155 | 0.21833 | 0.11124 | 121.7306 | 121.6926 | 121.627 | 121.5493 | 0.12606 | 0.16514 | 0.07639 | 0.11128 | 121.6045 | 121.6542 | 121.5009 | 121.5506
1917.6719 | 121.9025 | -0.20599 | 121.701 | 0.10812 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 121.6894 | 121.6606 | 121.5903 | 121.5081 | 0.080283 | 0.12851 | 0.030613 | 0.060923 | 0.31411 | 0.225 | 0.18942 | 0.19929 | 0.21479 | 0.29158 | 0.19364 | 121.7306 | 121.7017 | 121.6315 | 121.5493 | 0.12148 | 0.16971 | 0.071812 | 0.10212 | 121.6091 | 121.6588 | 121.5101 | 121.5597
1919.4375 | 121.8842 | -0.18768 | 121.7422 | 0.10812 | 0.028162 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 121.6939 | 121.6743 | 121.5995 | 121.5081 | 0.084861 | 0.12394 | 0.026035 | 0.060923 | 0.2958 | 0.21584 | 0.16653 | 0.18098 | 0.19648 | 0.27327 | 0.17075 | 121.7351 | 121.7155 | 121.6407 | 121.5493 | 0.12606 | 0.16514 | 0.067234 | 0.10212 | 121.6091 | 121.6679 | 121.5146 | 121.5735
1921.2031 | 121.9254 | -0.20142 | 121.7377 | 0.11269 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.081005 | -0.021514 | 121.7031 | 121.6651 | 121.6086 | 121.5219 | 0.084861 | 0.12394 | 0.026035 | 0.070079 | 0.31411 | 0.22958 | 0.18484 | 0.19013 | 0.21479 | 0.28242 | 0.1799 | 121.7443 | 121.7063 | 121.6498 | 121.5631 | 0.12606 | 0.16514 | 0.067234 | 0.11128 | 121.6182 | 121.6771 | 121.5238 | 121.5826
1922.9062 | 121.907 | -0.21057 | 121.7697 | 0.12185 | 0.028162 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 121.7077 | 121.6743 | 121.6132 | 121.5265 | 0.075705 | 0.12394 | 0.030613 | 0.065501 | 0.33242 | 0.23873 | 0.18941 | 0.20387 | 0.21937 | 0.29158 | 0.19821 | 121.7489 | 121.7155 | 121.6544 | 121.5677 | 0.1169 | 0.16514 | 0.071812 | 0.1067 | 121.632 | 121.6771 | 121.5375 | 121.5826
1924.6719 | 122.0306 | -0.16479 | 121.7377 | 0.11269 | 0.023583 | -0.025735 | -0.006703 | -0.009515 | 0.067269 | -0.021514 | 121.7214 | 121.6834 | 121.6224 | 121.5265 | 0.089439 | 0.12394 | 0.021456 | 0.065501 | 0.27749 | 0.18838 | 0.13906 | 0.15809 | 0.15528 | 0.23206 | 0.14328 | 121.7626 | 121.7246 | 121.6636 | 121.5677 | 0.13064 | 0.16514 | 0.062655 | 0.1067 | 121.632 | 121.7 | 121.5329 | 121.6009
1926.4219 | 121.9391 | -0.17395 | 121.7514 | 0.11269 | 0.037319 | -0.016578 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 121.726 | 121.688 | 121.6224 | 121.5494 | 0.080283 | 0.11936 | 0.016878 | 0.056344 | 0.28664 | 0.21127 | 0.15737 | 0.16267 | 0.17817 | 0.25495 | 0.15244 | 121.7672 | 121.7292 | 121.6636 | 121.5906 | 0.12148 | 0.16056 | 0.058077 | 0.097543 | 121.6457 | 121.7091 | 121.5421 | 121.6055
1928.1719 | 121.9345 | -0.19684 | 121.7743 | 0.11727 | 0.023583 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.021514 | 121.7214 | 121.7018 | 121.6315 | 121.5448 | 0.080283 | 0.11478 | 0.030613 | 0.065501 | 0.31411 | 0.22042 | 0.18484 | 0.19014 | 0.19648 | 0.27784 | 0.17532 | 121.7626 | 121.743 | 121.6727 | 121.586 | 0.12148 | 0.15598 | 0.071812 | 0.1067 | 121.6411 | 121.6908 | 121.5513 | 121.6009
1929.8594 | 121.9482 | -0.20142 | 121.7606 | 0.11727 | 0.023583 | -0.016578 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 121.726 | 121.7018 | 121.6361 | 121.5539 | 0.080283 | 0.11936 | 0.021456 | 0.065501 | 0.31869 | 0.225 | 0.18484 | 0.18098 | 0.21021 | 0.287 | 0.1799 | 121.7672 | 121.743 | 121.6773 | 121.5951 | 0.12148 | 0.16056 | 0.062655 | 0.1067 | 121.6457 | 121.7045 | 121.5558 | 121.6147
1931.5938 | 121.9757 | -0.16937 | 121.7422 | 0.12185 | 0.028162 | -0.016578 | -0.011281 | 0.017953 | 0.081005 | -0.016936 | 121.7352 | 121.7109 | 121.6453 | 121.5585 | 0.075705 | 0.11936 | 0.026035 | 0.065501 | 0.29122 | 0.19753 | 0.15279 | 0.15809 | 0.18733 | 0.25038 | 0.15244 | 121.7764 | 121.7521 | 121.6865 | 121.5997 | 0.1169 | 0.16056 | 0.067234 | 0.1067 | 121.6594 | 121.7091 | 121.5696 | 121.6192
1933.3438 | 121.9986 | -0.16022 | 121.7468 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.7443 | 121.7109 | 121.6544 | 121.5539 | 0.066548 | 0.1102 | 0.016878 | 0.051766 | 0.27749 | 0.17922 | 0.13906 | 0.14894 | 0.16901 | 0.2458 | 0.14328 | 121.7855 | 121.7521 | 121.6956 | 121.5951 | 0.10775 | 0.1514 | 0.058077 | 0.092965 | 121.6778 | 121.7274 | 121.5879 | 121.6376
1935.0938 | 121.9711 | -0.1831 | 121.7651 | 0.12185 | 0.028162 | -0.025735 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 121.7443 | 121.7155 | 121.6453 | 121.5585 | 0.066548 | 0.11936 | 0.026035 | 0.060923 | 0.30496 | 0.21127 | 0.15737 | 0.17182 | 0.18732 | 0.26869 | 0.16159 | 121.7855 | 121.7567 | 121.6865 | 121.5997 | 0.10775 | 0.16056 | 0.067234 | 0.10212 | 121.6778 | 121.7183 | 121.5787 | 121.6192
1936.7812 | 122.0261 | -0.16022 | 121.7651 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 121.7443 | 121.7201 | 121.6499 | 121.5585 | 0.075705 | 0.11478 | 0.021456 | 0.065501 | 0.27749 | 0.17922 | 0.13906 | 0.14894 | 0.16901 | 0.24122 | 0.14328 | 121.7855 | 121.7613 | 121.6911 | 121.5997 | 0.1169 | 0.15598 | 0.062655 | 0.1067 | 121.6686 | 121.7229 | 121.5741 | 121.6284
1938.5312 | 121.9482 | -0.19226 | 121.7789 | 0.11727 | 0.023583 | -0.012 | -0.006703 | 0.008797 | 0.071848 | -0.016936 | 121.7443 | 121.7247 | 121.659 | 121.5677 | 0.075705 | 0.12394 | 0.026035 | 0.056344 | 0.30953 | 0.21584 | 0.18026 | 0.18556 | 0.20106 | 0.26411 | 0.17532 | 121.7855 | 121.7659 | 121.7002 | 121.6089 | 0.1169 | 0.16514 | 0.067234 | 0.097543 | 121.6686 | 121.7183 | 121.5833 | 121.633
1940.2969 | 121.9894 | -0.17395 | 121.7606 | 0.11727 | 0.037319 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 121.758 | 121.7247 | 121.659 | 121.5768 | 0.080283 | 0.10562 | 0.021456 | 0.060923 | 0.29122 | 0.21127 | 0.15279 | 0.15809 | 0.18275 | 0.25495 | 0.15244 | 121.7992 | 121.7659 | 121.7002 | 121.618 | 0.12148 | 0.14682 | 0.062655 | 0.10212 | 121.6778 | 121.7366 | 121.5787 | 121.6376
1941.9844 | 121.9894 | -0.19226 | 121.7651 | 0.11727 | 0.023583 | -0.030314 | -0.01586 | 0.017953 | 0.081005 | -0.016936 | 121.7489 | 121.7155 | 121.659 | 121.5677 | 0.084861 | 0.12394 | 0.016878 | 0.060923 | 0.30953 | 0.21584 | 0.16195 | 0.1764 | 0.21021 | 0.27327 | 0.17532 | 121.7901 | 121.7567 | 121.7002 | 121.6089 | 0.12606 | 0.16514 | 0.058077 | 0.10212 | 121.664 | 121.732 | 121.5741 | 121.6421
1943.7344 | 122.0306 | -0.17853 | 121.7743 | 0.12185 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.076426 | -0.026092 | 121.7626 | 121.7247 | 121.6682 | 121.5677 | 0.080283 | 0.11936 | 0.026035 | 0.065501 | 0.30038 | 0.20211 | 0.15737 | 0.16267 | 0.1919 | 0.25495 | 0.15244 | 121.8038 | 121.7659 | 121.7094 | 121.6089 | 0.12148 | 0.16056 | 0.067234 | 0.1067 | 121.6823 | 121.7366 | 121.5879 | 121.6421
1945.4844 | 122.0581 | -0.16937 | 121.7697 | 0.11269 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 121.758 | 121.7292 | 121.659 | 121.5677 | 0.089439 | 0.12394 | 0.026035 | 0.065501 | 0.28207 | 0.19296 | 0.14822 | 0.14893 | 0.17817 | 0.25038 | 0.14786 | 121.7992 | 121.7704 | 121.7002 | 121.6089 | 0.13064 | 0.16514 | 0.067234 | 0.1067 | 121.6686 | 121.732 | 121.5696 | 121.633
1947.2344 | 122.049 | -0.16479 | 121.7331 | 0.10812 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 121.7626 | 121.7292 | 121.6636 | 121.5722 | 0.075705 | 0.12394 | 0.021456 | 0.060923 | 0.27291 | 0.18838 | 0.14364 | 0.14893 | 0.17359 | 0.2458 | 0.14328 | 121.8038 | 121.7704 | 121.7048 | 121.6134 | 0.1169 | 0.16514 | 0.062655 | 0.10212 | 121.6869 | 121.7412 | 121.5879 | 121.6421
1948.9844 | 121.9894 | -0.17395 | 121.7743 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.081005 | -0.021514 | 121.7626 | 121.7292 | 121.6682 | 121.586 | 0.084861 | 0.12394 | 0.026035 | 0.060923 | 0.28664 | 0.19295 | 0.15279 | 0.16267 | 0.18732 | 0.25495 | 0.15244 | 121.8038 | 121.7704 | 121.7094 | 121.6272 | 0.12606 | 0.16514 | 0.067234 | 0.10212 | 121.6778 | 121.7366 | 121.5833 | 121.6421
1950.6875 | 122.0398 | -0.17395 | 121.7834 | 0.11727 | 0.023583 | -0.025735 | -0.01586 | 0.008797 | 0.076426 | -0.016936 | 121.7672 | 121.7338 | 121.6819 | 121.5768 | 0.075705 | 0.11478 | 0.021456 | 0.070079 | 0.29122 | 0.19753 | 0.14821 | 0.15809 | 0.18275 | 0.25038 | 0.15701 | 121.8084 | 121.775 | 121.7231 | 121.618 | 0.1169 | 0.15598 | 0.062655 | 0.11128 | 121.6915 | 121.7457 | 121.6062 | 121.6604
1952.4375 | 122.0169 | -0.16937 | 121.7834 | 0.11727 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 121.7718 | 121.7338 | 121.6773 | 121.5906 | 0.080283 | 0.11478 | 0.021456 | 0.060923 | 0.28665 | 0.19296 | 0.14822 | 0.15351 | 0.17359 | 0.25038 | 0.15244 | 121.813 | 121.775 | 121.7185 | 121.6318 | 0.12148 | 0.15598 | 0.062655 | 0.10212 | 121.6915 | 121.7503 | 121.597 | 121.6559
1954.1875 | 122.0123 | -0.16022 | 121.8063 | 0.11269 | 0.023583 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.016936 | 121.7764 | 121.7521 | 121.6727 | 121.5906 | 0.080283 | 0.1102 | 0.035191 | 0.060923 | 0.27291 | 0.1838 | 0.14822 | 0.15351 | 0.16444 | 0.24122 | 0.14328 | 121.8176 | 121.7933 | 121.7139 | 121.6318 | 0.12148 | 0.1514 | 0.07639 | 0.10212 | 121.6961 | 121.7412 | 121.5925 | 121.6376
1955.8906 | 122.0947 | -0.15106 | 121.7743 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.026092 | 121.7809 | 121.7521 | 121.6773 | 121.5906 | 0.080283 | 0.11478 | 0.026035 | 0.060923 | 0.26376 | 0.17464 | 0.1299 | 0.14436 | 0.15986 | 0.23207 | 0.12497 | 121.8221 | 121.7933 | 121.7185 | 121.6318 | 0.12148 | 0.15598 | 0.067234 | 0.10212 | 121.7007 | 121.7549 | 121.597 | 121.6513
1957.6406 | 122.0673 | -0.13733 | 121.7651 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.076426 | -0.021514 | 121.7855 | 121.7475 | 121.6819 | 121.6043 | 0.075705 | 0.1102 | 0.021456 | 0.056344 | 0.2546 | 0.16091 | 0.12075 | 0.12605 | 0.14613 | 0.21376 | 0.11582 | 121.8267 | 121.7887 | 121.7231 | 121.6455 | 0.1169 | 0.1514 | 0.062655 | 0.097543 | 121.7098 | 121.7641 | 121.6062 | 121.6604
1959.4062 | 121.9666 | -0.18768 | 121.7972 | 0.11727 | 0.019004 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.016936 | 121.7809 | 121.7567 | 121.6865 | 121.5997 | 0.066548 | 0.1102 | 0.026035 | 0.056344 | 0.30496 | 0.20669 | 0.16653 | 0.18098 | 0.20106 | 0.27784 | 0.17075 | 121.8221 | 121.7979 | 121.7277 | 121.6409 | 0.10775 | 0.1514 | 0.067234 | 0.097543 | 121.7144 | 121.7549 | 121.6199 | 121.6604
1961.1875 | 121.9574 | -0.17853 | 121.8201 | 0.11269 | 0.028162 | -0.012 | -0.020438 | 0.008797 | 0.085583 | -0.021514 | 121.7901 | 121.7521 | 121.6956 | 121.6089 | 0.066548 | 0.1102 | 0.021456 | 0.056344 | 0.29122 | 0.20669 | 0.16653 | 0.15809 | 0.18732 | 0.26411 | 0.15701 | 121.8313 | 121.7933 | 121.7368 | 121.6501 | 0.10775 | 0.1514 | 0.062655 | 0.097543 | 121.7235 | 121.7686 | 121.6291 | 121.6742
1962.875 | 121.9849 | -0.18768 | 121.8063 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.012357 | 121.7901 | 121.7613 | 121.6865 | 121.5997 | 0.071126 | 0.11478 | 0.021456 | 0.060923 | 0.30496 | 0.21127 | 0.16653 | 0.1764 | 0.19648 | 0.26869 | 0.17533 | 121.8313 | 121.8025 | 121.7277 | 121.6409 | 0.11232 | 0.15598 | 0.062655 | 0.10212 | 121.719 | 121.7686 | 121.6154 | 121.665
1964.625 | 122.0856 | -0.13275 | 121.8018 | 0.11727 | 0.014425 | -0.016578 | -0.01586 | 0.004219 | 0.081005 | -0.021514 | 121.7901 | 121.7613 | 121.7002 | 121.6135 | 0.075705 | 0.11936 | 0.021456 | 0.065501 | 0.25002 | 0.14718 | 0.11617 | 0.11689 | 0.13697 | 0.21376 | 0.11124 | 121.8313 | 121.8025 | 121.7414 | 121.6547 | 0.1169 | 0.16056 | 0.062655 | 0.1067 | 121.7144 | 121.7686 | 121.6245 | 121.6788
1966.375 | 121.9803 | -0.16937 | 121.8246 | 0.11269 | 0.019004 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 121.7993 | 121.7659 | 121.7094 | 121.618 | 0.080283 | 0.11478 | 0.021456 | 0.056344 | 0.28207 | 0.18838 | 0.15737 | 0.16267 | 0.17817 | 0.25496 | 0.15702 | 121.8405 | 121.8071 | 121.7506 | 121.6592 | 0.12148 | 0.15598 | 0.062655 | 0.097543 | 121.719 | 121.7778 | 121.6291 | 121.6879
1968.0625 | 121.9666 | -0.15564 | 121.8338 | 0.11727 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.7947 | 121.7613 | 121.7002 | 121.6135 | 0.071126 | 0.1102 | 0.016878 | 0.056344 | 0.27291 | 0.1838 | 0.13448 | 0.14436 | 0.16444 | 0.24122 | 0.1387 | 121.8359 | 121.8025 | 121.7414 | 121.6547 | 0.11232 | 0.1514 | 0.058077 | 0.097543 | 121.7235 | 121.7778 | 121.6291 | 121.6833
1969.8125 | 122.113 | -0.15106 | 121.7972 | 0.11727 | 0.019004 | -0.025735 | -0.01586 | 0.013375 | 0.076426 | -0.012357 | 121.7947 | 121.7659 | 121.7048 | 121.618 | 0.075705 | 0.1102 | 0.035191 | 0.060923 | 0.26833 | 0.17007 | 0.12533 | 0.1352 | 0.16444 | 0.22749 | 0.1387 | 121.8359 | 121.8071 | 121.746 | 121.6592 | 0.1169 | 0.1514 | 0.07639 | 0.10212 | 121.719 | 121.7595 | 121.6291 | 121.6696
1971.5625 | 122.0993 | -0.14191 | 121.8063 | 0.11269 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.021514 | 121.8038 | 121.775 | 121.7048 | 121.6135 | 0.071126 | 0.1102 | 0.016878 | 0.060923 | 0.2546 | 0.16091 | 0.12533 | 0.1352 | 0.15528 | 0.22291 | 0.12039 | 121.845 | 121.8162 | 121.746 | 121.6547 | 0.11232 | 0.1514 | 0.058077 | 0.10212 | 121.7327 | 121.787 | 121.6337 | 121.6879
1973.3125 | 122.0993 | -0.14648 | 121.8109 | 0.11727 | 0.014425 | -0.016578 | -0.025017 | 0.008797 | 0.076426 | -0.021514 | 121.8084 | 121.775 | 121.7094 | 121.6272 | 0.071126 | 0.11478 | 0.021456 | 0.051766 | 0.26376 | 0.16091 | 0.12991 | 0.12147 | 0.15528 | 0.22291 | 0.12497 | 121.8496 | 121.8162 | 121.7506 | 121.6684 | 0.11232 | 0.15598 | 0.062655 | 0.092965 | 121.7373 | 121.787 | 121.6382 | 121.6879
1975.0156 | 122.0352 | -0.1831 | 121.8109 | 0.11269 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.8084 | 121.7796 | 121.7139 | 121.6272 | 0.071126 | 0.1102 | 0.021456 | 0.060923 | 0.2958 | 0.19753 | 0.16195 | 0.17182 | 0.1919 | 0.26869 | 0.16617 | 121.8496 | 121.8208 | 121.7551 | 121.6684 | 0.11232 | 0.1514 | 0.062655 | 0.10212 | 121.7373 | 121.787 | 121.6428 | 121.6925
1976.7656 | 121.9711 | -0.19226 | 121.8246 | 0.11727 | 0.023583 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 121.8084 | 121.7842 | 121.7094 | 121.6226 | 0.075705 | 0.11936 | 0.016878 | 0.060923 | 0.30953 | 0.21584 | 0.1711 | 0.18556 | 0.20564 | 0.27784 | 0.17532 | 121.8496 | 121.8254 | 121.7506 | 121.6638 | 0.1169 | 0.16056 | 0.058077 | 0.10212 | 121.7327 | 121.7915 | 121.6337 | 121.6925
1978.5312 | 122.1222 | -0.14648 | 121.7834 | 0.11269 | 0.023583 | -0.025735 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 121.813 | 121.7842 | 121.7094 | 121.6318 | 0.075705 | 0.1102 | 0.016878 | 0.060923 | 0.25918 | 0.17007 | 0.12075 | 0.13062 | 0.1507 | 0.23207 | 0.12955 | 121.8542 | 121.8254 | 121.7506 | 121.673 | 0.1169 | 0.1514 | 0.058077 | 0.10212 | 121.7373 | 121.7961 | 121.6337 | 121.6925
1980.2812 | 122.0718 | -0.16937 | 121.8063 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.026092 | 121.813 | 121.7796 | 121.7139 | 121.618 | 0.075705 | 0.11936 | 0.021456 | 0.056344 | 0.28207 | 0.19296 | 0.14822 | 0.15351 | 0.17817 | 0.25038 | 0.14328 | 121.8542 | 121.8208 | 121.7551 | 121.6592 | 0.1169 | 0.16056 | 0.062655 | 0.097543 | 121.7373 | 121.7915 | 121.6382 | 121.6925
1981.9688 | 122.1359 | -0.14191 | 121.8018 | 0.11727 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.076426 | -0.016936 | 121.813 | 121.7842 | 121.7139 | 121.6364 | 0.075705 | 0.1102 | 0.026035 | 0.056344 | 0.25918 | 0.16091 | 0.11617 | 0.12605 | 0.1507 | 0.21833 | 0.12497 | 121.8542 | 121.8254 | 121.7551 | 121.6776 | 0.1169 | 0.1514 | 0.067234 | 0.097543 | 121.7373 | 121.787 | 121.6382 | 121.6879
1983.7188 | 121.994 | -0.19684 | 121.8567 | 0.11269 | 0.028162 | -0.016578 | -0.011281 | 0.004219 | 0.076426 | -0.016936 | 121.8176 | 121.7933 | 121.7231 | 121.6409 | 0.066548 | 0.1102 | 0.030613 | 0.056344 | 0.30953 | 0.225 | 0.18026 | 0.18556 | 0.20106 | 0.27326 | 0.1799 | 121.8588 | 121.8345 | 121.7643 | 121.6821 | 0.10775 | 0.1514 | 0.071812 | 0.097543 | 121.751 | 121.787 | 121.6566 | 121.6925
1985.4688 | 122.1497 | -0.13733 | 121.8063 | 0.11727 | 0.028162 | -0.016578 | -0.011281 | 0.008797 | 0.076426 | -0.021514 | 121.8267 | 121.7842 | 121.7231 | 121.6409 | 0.071126 | 0.10562 | 0.026035 | 0.056344 | 0.2546 | 0.16549 | 0.12075 | 0.12605 | 0.14613 | 0.21376 | 0.11582 | 121.8679 | 121.8254 | 121.7643 | 121.6821 | 0.11232 | 0.14682 | 0.067234 | 0.097543 | 121.7556 | 121.8007 | 121.652 | 121.6971
1987.2188 | 121.9849 | -0.17853 | 121.875 | 0.12185 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.021514 | 121.8221 | 121.7933 | 121.7277 | 121.6409 | 0.075705 | 0.1102 | 0.021456 | 0.060923 | 0.30038 | 0.20211 | 0.15737 | 0.16725 | 0.18732 | 0.26411 | 0.15701 | 121.8633 | 121.8345 | 121.7689 | 121.6821 | 0.1169 | 0.1514 | 0.062655 | 0.10212 | 121.7464 | 121.8007 | 121.652 | 121.7062
1988.9062 | 122.0169 | -0.16022 | 121.843 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 121.8313 | 121.7933 | 121.7323 | 121.6409 | 0.066548 | 0.11478 | 0.021456 | 0.056344 | 0.27749 | 0.1838 | 0.14364 | 0.14894 | 0.16901 | 0.24122 | 0.1387 | 121.8725 | 121.8345 | 121.7735 | 121.6821 | 0.10775 | 0.15598 | 0.062655 | 0.097543 | 121.7648 | 121.8098 | 121.6657 | 121.7108
1990.6562 | 122.0398 | -0.16022 | 121.8475 | 0.11727 | 0.03274 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.021514 | 121.8267 | 121.8025 | 121.7231 | 121.6409 | 0.071126 | 0.1102 | 0.026035 | 0.056344 | 0.27749 | 0.19296 | 0.13906 | 0.15351 | 0.17359 | 0.2458 | 0.1387 | 121.8679 | 121.8437 | 121.7643 | 121.6821 | 0.11232 | 0.1514 | 0.067234 | 0.097543 | 121.7556 | 121.8007 | 121.652 | 121.6971
1992.3906 | 122.1085 | -0.13733 | 121.8292 | 0.11727 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.8313 | 121.7979 | 121.7368 | 121.6501 | 0.066548 | 0.10562 | 0.021456 | 0.051766 | 0.2546 | 0.15633 | 0.12075 | 0.12605 | 0.14613 | 0.22291 | 0.12039 | 121.8725 | 121.8391 | 121.778 | 121.6913 | 0.10775 | 0.14682 | 0.062655 | 0.092965 | 121.7648 | 121.8098 | 121.6703 | 121.7154
1994.0781 | 122.0169 | -0.17853 | 121.8796 | 0.11269 | 0.023583 | -0.012 | -0.01586 | 0.013375 | 0.081005 | -0.016936 | 121.8405 | 121.8117 | 121.7414 | 121.6547 | 0.066548 | 0.10562 | 0.016878 | 0.051766 | 0.29122 | 0.20211 | 0.16653 | 0.16267 | 0.1919 | 0.25953 | 0.16159 | 121.8817 | 121.8529 | 121.7826 | 121.6959 | 0.10775 | 0.14682 | 0.058077 | 0.092965 | 121.7739 | 121.8236 | 121.6749 | 121.7245
1995.7812 | 122.1542 | -0.11902 | 121.8384 | 0.11269 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.076426 | -0.026092 | 121.8496 | 121.8208 | 121.746 | 121.6593 | 0.06197 | 0.096469 | 0.007721 | 0.051766 | 0.23171 | 0.1426 | 0.097862 | 0.10774 | 0.12324 | 0.19544 | 0.092927 | 121.8908 | 121.862 | 121.7872 | 121.7005 | 0.10317 | 0.13767 | 0.04892 | 0.092965 | 121.7876 | 121.8419 | 121.684 | 121.7383
1997.5156 | 122.0215 | -0.17853 | 121.8887 | 0.10812 | 0.023583 | -0.021157 | -0.002124 | 0.004219 | 0.076426 | -0.026092 | 121.8588 | 121.8162 | 121.7506 | 121.6684 | 0.052814 | 0.096469 | 0.012299 | 0.04261 | 0.28664 | 0.20211 | 0.15737 | 0.1764 | 0.18275 | 0.25495 | 0.15244 | 121.9 | 121.8574 | 121.7918 | 121.7096 | 0.094013 | 0.13767 | 0.053498 | 0.083809 | 121.806 | 121.8465 | 121.6978 | 121.7383
1999.2656 | 122.1405 | -0.1236 | 121.8475 | 0.11727 | 0.023583 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.021514 | 121.8588 | 121.8254 | 121.7506 | 121.6684 | 0.057392 | 0.087313 | 0.007721 | 0.04261 | 0.24087 | 0.14718 | 0.10702 | 0.12147 | 0.12781 | 0.2046 | 0.10208 | 121.9 | 121.8666 | 121.7918 | 121.7096 | 0.098591 | 0.12851 | 0.04892 | 0.083809 | 121.8014 | 121.8511 | 121.6932 | 121.7429
2000.9688 | 122.1451 | -0.13733 | 121.8384 | 0.10354 | 0.023583 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.012357 | 121.8588 | 121.8254 | 121.7552 | 121.673 | 0.052814 | 0.087313 | 0.007721 | 0.04261 | 0.24087 | 0.16091 | 0.11159 | 0.12147 | 0.14155 | 0.21833 | 0.12497 | 121.9 | 121.8666 | 121.7964 | 121.7142 | 0.094013 | 0.12851 | 0.04892 | 0.083809 | 121.806 | 121.8511 | 121.7023 | 121.7474
2002.7188 | 122.1588 | -0.13275 | 121.8338 | 0.11727 | 0.019004 | -0.030314 | -0.025017 | -0.000359 | 0.085583 | -0.016936 | 121.8679 | 121.8391 | 121.7643 | 121.6821 | 0.048236 | 0.087313 | 0.021456 | 0.051766 | 0.25002 | 0.15176 | 0.10244 | 0.10773 | 0.13239 | 0.21833 | 0.11582 | 121.9091 | 121.8803 | 121.8055 | 121.7233 | 0.089435 | 0.12851 | 0.062655 | 0.092965 | 121.8197 | 121.8465 | 121.7161 | 121.7429
2004.4844 | 122.1497 | -0.11902 | 121.8292 | 0.11269 | 0.019004 | -0.025735 | -0.011281 | 0.013375 | 0.081005 | -0.021514 | 121.8679 | 121.8391 | 121.7735 | 121.6867 | 0.052814 | 0.087313 | 0.007721 | 0.047188 | 0.23171 | 0.13802 | 0.093284 | 0.10774 | 0.13239 | 0.20002 | 0.097505 | 121.9091 | 121.8803 | 121.8147 | 121.7279 | 0.094013 | 0.12851 | 0.04892 | 0.088387 | 121.8151 | 121.8602 | 121.7207 | 121.7657
2006.25 | 122.1634 | -0.09613 | 121.8475 | 0.10812 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.026092 | 121.8725 | 121.8391 | 121.7643 | 121.6821 | 0.048236 | 0.087313 | 0.012299 | 0.04261 | 0.20425 | 0.11513 | 0.074973 | 0.084849 | 0.10493 | 0.17713 | 0.070038 | 121.9137 | 121.8803 | 121.8055 | 121.7233 | 0.089435 | 0.12851 | 0.053498 | 0.083809 | 121.8243 | 121.8602 | 121.7161 | 121.752
2007.9531 | 122.0215 | -0.15564 | 121.8887 | 0.11727 | 0.03274 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 121.8771 | 121.8391 | 121.7735 | 121.6913 | 0.052814 | 0.082735 | -0.001436 | 0.04261 | 0.27291 | 0.18838 | 0.13448 | 0.14894 | 0.16901 | 0.24122 | 0.1387 | 121.9183 | 121.8803 | 121.8147 | 121.7325 | 0.094013 | 0.12393 | 0.039763 | 0.083809 | 121.8243 | 121.8785 | 121.7207 | 121.7749
2009.6875 | 122.1497 | -0.12817 | 121.8384 | 0.11269 | 0.019004 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 121.8862 | 121.8483 | 121.778 | 121.6959 | 0.039079 | 0.087313 | 0.003143 | 0.038032 | 0.24087 | 0.14718 | 0.1116 | 0.11231 | 0.13697 | 0.20918 | 0.10666 | 121.9274 | 121.8895 | 121.8192 | 121.7371 | 0.080278 | 0.12851 | 0.044342 | 0.079231 | 121.8472 | 121.8831 | 121.739 | 121.7749
2011.4531 | 122.1405 | -0.10529 | 121.8658 | 0.10812 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 121.8862 | 121.8483 | 121.778 | 121.7005 | 0.039079 | 0.078157 | 0.003143 | 0.033454 | 0.2134 | 0.12887 | 0.084129 | 0.084848 | 0.11408 | 0.18629 | 0.08835 | 121.9274 | 121.8895 | 121.8192 | 121.7417 | 0.080278 | 0.11936 | 0.044342 | 0.074653 | 121.8472 | 121.8831 | 121.739 | 121.7749
2013.1406 | 122.0535 | -0.13733 | 121.8842 | 0.11727 | 0.023583 | -0.030314 | -0.020438 | 0.008797 | 0.081005 | -0.016936 | 121.8862 | 121.8483 | 121.7826 | 121.705 | 0.043657 | 0.078157 | 0.003143 | 0.04261 | 0.2546 | 0.16091 | 0.10701 | 0.11689 | 0.14613 | 0.21833 | 0.12039 | 121.9274 | 121.8895 | 121.8238 | 121.7462 | 0.084856 | 0.11936 | 0.044342 | 0.083809 | 121.8426 | 121.8831 | 121.739 | 121.7795
2014.8906 | 122.049 | -0.14648 | 121.9208 | 0.10812 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 121.8908 | 121.8574 | 121.7872 | 121.705 | 0.043657 | 0.082735 | 0.007721 | 0.038032 | 0.2546 | 0.17007 | 0.12533 | 0.13978 | 0.15528 | 0.23207 | 0.12955 | 121.932 | 121.8986 | 121.8284 | 121.7462 | 0.084856 | 0.12393 | 0.04892 | 0.079231 | 121.8472 | 121.8831 | 121.7435 | 121.7795
2016.6406 | 122.1222 | -0.11902 | 121.8704 | 0.11727 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.076426 | -0.026092 | 121.9046 | 121.8574 | 121.7964 | 121.7005 | 0.034501 | 0.082735 | -0.001436 | 0.04261 | 0.23629 | 0.13802 | 0.097862 | 0.10316 | 0.12782 | 0.19544 | 0.092927 | 121.9458 | 121.8986 | 121.8376 | 121.7417 | 0.0757 | 0.12393 | 0.039763 | 0.083809 | 121.8701 | 121.906 | 121.7619 | 121.7978
2018.3906 | 122.0947 | -0.14648 | 121.8933 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.013375 | 0.090161 | -0.021514 | 121.8954 | 121.8574 | 121.8009 | 121.7005 | 0.034501 | 0.078157 | 0.012299 | 0.038032 | 0.26376 | 0.17465 | 0.12991 | 0.13062 | 0.15986 | 0.23664 | 0.12497 | 121.9366 | 121.8986 | 121.8421 | 121.7417 | 0.0757 | 0.11936 | 0.053498 | 0.079231 | 121.8609 | 121.8831 | 121.7664 | 121.7886
2020.0781 | 122.1405 | -0.13733 | 121.8887 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 121.9046 | 121.862 | 121.7872 | 121.705 | 0.039079 | 0.078157 | 0.003143 | 0.038032 | 0.2546 | 0.16091 | 0.12075 | 0.12147 | 0.14155 | 0.21833 | 0.12039 | 121.9458 | 121.9032 | 121.8284 | 121.7462 | 0.080278 | 0.11936 | 0.044342 | 0.079231 | 121.8655 | 121.9014 | 121.7481 | 121.7841
2021.8281 | 122.1497 | -0.086975 | 121.8704 | 0.12185 | 0.023583 | -0.025735 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 121.9 | 121.8712 | 121.8009 | 121.7142 | 0.039079 | 0.073579 | 0.003143 | 0.038032 | 0.20883 | 0.11056 | 0.06124 | 0.075694 | 0.091194 | 0.16798 | 0.065461 | 121.9412 | 121.9124 | 121.8421 | 121.7554 | 0.080278 | 0.11478 | 0.044342 | 0.079231 | 121.8609 | 121.8968 | 121.7619 | 121.7978
2023.5781 | 122.0993 | -0.14191 | 121.9391 | 0.11727 | 0.019004 | -0.016578 | -0.011281 | 0.017953 | 0.085583 | -0.012357 | 121.9091 | 121.8712 | 121.8055 | 121.7142 | 0.039079 | 0.078157 | -0.006014 | 0.04261 | 0.25918 | 0.16091 | 0.12533 | 0.13063 | 0.15986 | 0.22749 | 0.12955 | 121.9503 | 121.9124 | 121.8467 | 121.7554 | 0.080278 | 0.11936 | 0.035185 | 0.083809 | 121.8701 | 121.9152 | 121.7664 | 121.8115
2025.3281 | 122.1313 | -0.10986 | 121.8933 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.004219 | 0.076426 | -0.021514 | 121.9046 | 121.8758 | 121.8009 | 121.7188 | 0.029923 | 0.078157 | -0.001436 | 0.033454 | 0.22256 | 0.12887 | 0.088706 | 0.098582 | 0.11408 | 0.18629 | 0.088349 | 121.9458 | 121.917 | 121.8421 | 121.76 | 0.071122 | 0.11936 | 0.039763 | 0.074653 | 121.8746 | 121.906 | 121.771 | 121.8024
2027.0938 | 122.081 | -0.14648 | 121.9345 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 121.9046 | 121.8712 | 121.8101 | 121.7279 | 0.039079 | 0.078157 | 0.007721 | 0.033454 | 0.26376 | 0.17007 | 0.12991 | 0.1352 | 0.15986 | 0.23664 | 0.12955 | 121.9458 | 121.9124 | 121.8513 | 121.7691 | 0.080278 | 0.11936 | 0.04892 | 0.074653 | 121.8655 | 121.8968 | 121.771 | 121.8024
2028.7812 | 122.049 | -0.15106 | 121.9437 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.026092 | 121.9137 | 121.8758 | 121.8147 | 121.7234 | 0.034501 | 0.064423 | -0.001436 | 0.038032 | 0.26376 | 0.17922 | 0.1299 | 0.13978 | 0.15986 | 0.23664 | 0.12497 | 121.9549 | 121.917 | 121.8559 | 121.7646 | 0.0757 | 0.10562 | 0.039763 | 0.079231 | 121.8792 | 121.9152 | 121.7802 | 121.8161
2030.5312 | 122.1771 | -0.10986 | 121.9025 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.9137 | 121.8803 | 121.8238 | 121.7234 | 0.029923 | 0.073579 | -0.010593 | 0.04261 | 0.22714 | 0.12887 | 0.088706 | 0.098582 | 0.11866 | 0.19545 | 0.092927 | 121.9549 | 121.9215 | 121.865 | 121.7646 | 0.071122 | 0.11478 | 0.030606 | 0.083809 | 121.8838 | 121.9243 | 121.7939 | 121.8344
2032.2812 | 122.0901 | -0.14648 | 121.9025 | 0.12185 | 0.023583 | -0.012 | -0.006703 | 0.017953 | 0.090161 | -0.016936 | 121.9183 | 121.8803 | 121.8192 | 121.7279 | 0.034501 | 0.073579 | -0.001436 | 0.028875 | 0.26833 | 0.17007 | 0.13448 | 0.13978 | 0.16444 | 0.23664 | 0.12955 | 121.9595 | 121.9215 | 121.8604 | 121.7691 | 0.0757 | 0.11478 | 0.039763 | 0.070074 | 121.8838 | 121.9197 | 121.7847 | 121.8207
2033.9844 | 122.1176 | -0.11902 | 121.9162 | 0.11727 | 0.028162 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 121.9229 | 121.8758 | 121.8192 | 121.7279 | 0.029923 | 0.078157 | -0.001436 | 0.033454 | 0.23629 | 0.14718 | 0.10702 | 0.11232 | 0.12782 | 0.2046 | 0.10208 | 121.9641 | 121.917 | 121.8604 | 121.7691 | 0.071122 | 0.11936 | 0.039763 | 0.074653 | 121.8929 | 121.9243 | 121.7893 | 121.8207
2035.75 | 122.0581 | -0.16022 | 121.9299 | 0.11727 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.026092 | 121.9275 | 121.8849 | 121.8192 | 121.7371 | 0.034501 | 0.073579 | -0.001436 | 0.033454 | 0.27749 | 0.17922 | 0.14364 | 0.14894 | 0.16444 | 0.2458 | 0.13412 | 121.9687 | 121.9261 | 121.8604 | 121.7783 | 0.0757 | 0.11478 | 0.039763 | 0.074653 | 121.8929 | 121.9289 | 121.7847 | 121.8207
2037.5 | 122.1222 | -0.12817 | 121.907 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.081005 | -0.021514 | 121.9229 | 121.8941 | 121.8192 | 121.7417 | 0.034501 | 0.069001 | -0.006014 | 0.033454 | 0.24545 | 0.15176 | 0.10702 | 0.11689 | 0.14155 | 0.20918 | 0.10666 | 121.9641 | 121.9353 | 121.8604 | 121.7829 | 0.0757 | 0.1102 | 0.035185 | 0.074653 | 121.8884 | 121.9289 | 121.7847 | 121.8253
2039.25 | 122.0306 | -0.15564 | 121.9437 | 0.11269 | 0.037319 | -0.016578 | -0.011281 | 0.017953 | 0.09474 | -0.016936 | 121.9229 | 121.8895 | 121.8238 | 121.7417 | 0.025345 | 0.073579 | -0.006014 | 0.028875 | 0.26833 | 0.19296 | 0.13906 | 0.14436 | 0.17359 | 0.25038 | 0.1387 | 121.9641 | 121.9307 | 121.865 | 121.7829 | 0.066544 | 0.11478 | 0.035185 | 0.070074 | 121.8975 | 121.9289 | 121.7985 | 121.8298
2040.9531 | 122.1863 | -0.11444 | 121.9254 | 0.10812 | 0.023583 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 121.9366 | 121.8986 | 121.8284 | 121.7371 | 0.029923 | 0.073579 | -0.001436 | 0.028875 | 0.22256 | 0.13802 | 0.097863 | 0.094003 | 0.12324 | 0.19545 | 0.092927 | 121.9778 | 121.9398 | 121.8696 | 121.7783 | 0.071122 | 0.11478 | 0.039763 | 0.070074 | 121.9067 | 121.938 | 121.7985 | 121.8298
2042.6875 | 122.0398 | -0.14648 | 121.9437 | 0.12185 | 0.03274 | -0.016578 | -0.006703 | 0.013375 | 0.090161 | -0.016936 | 121.932 | 121.8986 | 121.8284 | 121.7417 | 0.029923 | 0.073579 | -0.006014 | 0.028875 | 0.26833 | 0.17922 | 0.12991 | 0.13978 | 0.15986 | 0.23664 | 0.12955 | 121.9732 | 121.9398 | 121.8696 | 121.7829 | 0.071122 | 0.11478 | 0.035185 | 0.070074 | 121.9021 | 121.938 | 121.7985 | 121.8344
2044.4375 | 122.1039 | -0.1236 | 121.9574 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 121.9366 | 121.9032 | 121.8284 | 121.7463 | 0.029923 | 0.064423 | -0.006014 | 0.033454 | 0.23629 | 0.15176 | 0.10244 | 0.11231 | 0.13239 | 0.21376 | 0.11124 | 121.9778 | 121.9444 | 121.8696 | 121.7875 | 0.071122 | 0.10562 | 0.035185 | 0.074653 | 121.9067 | 121.9426 | 121.7985 | 121.8344
2046.1406 | 122.1542 | -0.1236 | 121.9299 | 0.10812 | 0.019004 | -0.030314 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.9366 | 121.8986 | 121.8376 | 121.7417 | 0.025345 | 0.073579 | -0.001436 | 0.04261 | 0.23171 | 0.1426 | 0.093282 | 0.11231 | 0.13239 | 0.20918 | 0.10666 | 121.9778 | 121.9398 | 121.8788 | 121.7829 | 0.066544 | 0.11478 | 0.039763 | 0.083809 | 121.9113 | 121.938 | 121.8122 | 121.839
2047.8906 | 122.1497 | -0.11444 | 121.9299 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | -0.000359 | 0.071848 | -0.021514 | 121.9412 | 121.8986 | 121.8376 | 121.7508 | 0.029923 | 0.069001 | -0.006014 | 0.038032 | 0.22256 | 0.13802 | 0.093284 | 0.10316 | 0.11408 | 0.18629 | 0.092927 | 121.9824 | 121.9398 | 121.8788 | 121.792 | 0.071122 | 0.1102 | 0.035185 | 0.079231 | 121.9113 | 121.9472 | 121.8076 | 121.8436
2049.6406 | 122.1313 | -0.11444 | 121.9208 | 0.12185 | 0.028162 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 121.9458 | 121.8986 | 121.833 | 121.7417 | 0.029923 | 0.069001 | -0.006014 | 0.038032 | 0.23629 | 0.1426 | 0.097863 | 0.098581 | 0.12324 | 0.19545 | 0.092927 | 121.987 | 121.9398 | 121.8742 | 121.7829 | 0.071122 | 0.1102 | 0.035185 | 0.079231 | 121.9158 | 121.9518 | 121.8031 | 121.839
2051.3906 | 122.1451 | -0.10529 | 121.9345 | 0.10812 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.016936 | 121.9458 | 121.9078 | 121.8421 | 121.7463 | 0.029923 | 0.064423 | -0.006014 | 0.033454 | 0.2134 | 0.12429 | 0.084129 | 0.094005 | 0.11866 | 0.19087 | 0.08835 | 121.987 | 121.949 | 121.8833 | 121.7875 | 0.071122 | 0.10562 | 0.035185 | 0.074653 | 121.9158 | 121.9518 | 121.8122 | 121.8482
2053.1406 | 122.0627 | -0.14191 | 121.9345 | 0.11727 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.012357 | 121.9458 | 121.9078 | 121.8376 | 121.7508 | 0.025345 | 0.069001 | -0.006014 | 0.033454 | 0.25918 | 0.15633 | 0.12533 | 0.13063 | 0.1507 | 0.22291 | 0.12955 | 121.987 | 121.949 | 121.8788 | 121.792 | 0.066544 | 0.1102 | 0.035185 | 0.074653 | 121.9204 | 121.9518 | 121.8122 | 121.8436
2054.8281 | 122.2 | -0.082397 | 121.9116 | 0.11269 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.085583 | -0.026092 | 121.9503 | 121.9124 | 121.8421 | 121.7646 | 0.029923 | 0.069001 | -0.006014 | 0.024297 | 0.19509 | 0.10598 | 0.06124 | 0.061959 | 0.086616 | 0.16798 | 0.056305 | 121.9915 | 121.9536 | 121.8833 | 121.8058 | 0.071122 | 0.1102 | 0.035185 | 0.065496 | 121.9204 | 121.9564 | 121.8122 | 121.8482
2056.5781 | 122.0993 | -0.12817 | 121.9482 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.9595 | 121.9124 | 121.8467 | 121.7554 | 0.029923 | 0.064423 | -0.001436 | 0.028875 | 0.24087 | 0.14718 | 0.10702 | 0.11689 | 0.13697 | 0.21376 | 0.11124 | 122.0007 | 121.9536 | 121.8879 | 121.7966 | 0.071122 | 0.10562 | 0.039763 | 0.070074 | 121.9296 | 121.9609 | 121.8168 | 121.8482
2058.3281 | 122.168 | -0.10986 | 121.9391 | 0.10354 | 0.019004 | -0.030314 | -0.011281 | 0.008797 | 0.076426 | -0.026092 | 121.9503 | 121.917 | 121.8513 | 121.7646 | 0.029923 | 0.069001 | -0.001436 | 0.028875 | 0.2134 | 0.12887 | 0.079549 | 0.098582 | 0.11866 | 0.18629 | 0.083771 | 121.9915 | 121.9582 | 121.8925 | 121.8058 | 0.071122 | 0.1102 | 0.039763 | 0.070074 | 121.9204 | 121.9518 | 121.8214 | 121.8527
2060.0781 | 122.1771 | -0.1236 | 121.9391 | 0.11269 | 0.019004 | -0.021157 | -0.01586 | -0.000359 | 0.081005 | -0.021514 | 121.9503 | 121.9124 | 121.8513 | 121.7691 | 0.025345 | 0.069001 | -0.010593 | 0.024297 | 0.23629 | 0.1426 | 0.10244 | 0.10774 | 0.12324 | 0.2046 | 0.10208 | 121.9915 | 121.9536 | 121.8925 | 121.8103 | 0.066544 | 0.1102 | 0.030606 | 0.065496 | 121.925 | 121.9609 | 121.8259 | 121.8619
2061.7656 | 122.0993 | -0.13733 | 121.9711 | 0.11727 | 0.028162 | -0.012 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 121.9503 | 121.9215 | 121.8513 | 121.7691 | 0.020767 | 0.064423 | -0.001436 | 0.024297 | 0.2546 | 0.16549 | 0.12533 | 0.12605 | 0.14613 | 0.22749 | 0.12039 | 121.9915 | 121.9627 | 121.8925 | 121.8103 | 0.061966 | 0.10562 | 0.039763 | 0.065496 | 121.9296 | 121.9518 | 121.8305 | 121.8527
2063.5156 | 122.081 | -0.13733 | 121.9757 | 0.12185 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.090161 | -0.012357 | 121.9549 | 121.9261 | 121.8559 | 121.7737 | 0.025345 | 0.059844 | -0.006014 | 0.024297 | 0.25918 | 0.16091 | 0.12075 | 0.12605 | 0.1507 | 0.22749 | 0.12497 | 121.9961 | 121.9673 | 121.8971 | 121.8149 | 0.066544 | 0.10104 | 0.035185 | 0.065496 | 121.9296 | 121.9609 | 121.8305 | 121.8619
2065.2656 | 122.2 | -0.082397 | 121.9437 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.017953 | 0.085583 | -0.016936 | 121.9641 | 121.9261 | 121.8605 | 121.7646 | 0.029923 | 0.064423 | -0.006014 | 0.033454 | 0.19509 | 0.10598 | 0.06124 | 0.075694 | 0.10035 | 0.16798 | 0.065461 | 122.0053 | 121.9673 | 121.9017 | 121.8058 | 0.071122 | 0.10562 | 0.035185 | 0.074653 | 121.9342 | 121.9701 | 121.8305 | 121.8665
2066.9531 | 122.1634 | -0.10071 | 121.9437 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 121.9595 | 121.9307 | 121.8559 | 121.7691 | 0.025345 | 0.064423 | -0.010593 | 0.019719 | 0.20882 | 0.12429 | 0.079551 | 0.089427 | 0.10493 | 0.18171 | 0.079194 | 122.0007 | 121.9719 | 121.8971 | 121.8103 | 0.066544 | 0.10562 | 0.030606 | 0.060918 | 121.9342 | 121.9701 | 121.8305 | 121.8665
2068.7031 | 122.1313 | -0.11902 | 121.9391 | 0.12185 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 121.9549 | 121.9215 | 121.865 | 121.7691 | 0.025345 | 0.059844 | -0.010593 | 0.028875 | 0.24087 | 0.13802 | 0.097862 | 0.10316 | 0.12782 | 0.20002 | 0.097505 | 121.9961 | 121.9627 | 121.9062 | 121.8103 | 0.066544 | 0.10104 | 0.030606 | 0.070074 | 121.9296 | 121.9655 | 121.8397 | 121.8756
2070.3906 | 122.1176 | -0.13275 | 121.9666 | 0.11727 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 121.9595 | 121.9307 | 121.865 | 121.7829 | 0.020767 | 0.064423 | -0.010593 | 0.028875 | 0.25002 | 0.16091 | 0.11159 | 0.12147 | 0.14155 | 0.21376 | 0.11124 | 122.0007 | 121.9719 | 121.9062 | 121.8241 | 0.061966 | 0.10562 | 0.030606 | 0.070074 | 121.9387 | 121.9701 | 121.8443 | 121.8756
2072.1406 | 122.081 | -0.14191 | 121.9849 | 0.11269 | 0.023583 | -0.016578 | -0.002124 | 0.004219 | 0.085583 | -0.021514 | 121.9641 | 121.9307 | 121.8605 | 121.7783 | 0.025345 | 0.064423 | -0.015171 | 0.028875 | 0.2546 | 0.16549 | 0.12533 | 0.13978 | 0.14613 | 0.22749 | 0.12039 | 122.0053 | 121.9719 | 121.9017 | 121.8195 | 0.066544 | 0.10562 | 0.026028 | 0.070074 | 121.9387 | 121.9792 | 121.8351 | 121.8756
2073.8281 | 122.0856 | -0.15564 | 121.9711 | 0.11269 | 0.019004 | -0.025735 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 121.9595 | 121.9307 | 121.8605 | 121.7737 | 0.025345 | 0.064423 | -0.006014 | 0.028875 | 0.26833 | 0.17464 | 0.1299 | 0.14436 | 0.16444 | 0.24122 | 0.1387 | 122.0007 | 121.9719 | 121.9017 | 121.8149 | 0.066544 | 0.10562 | 0.035185 | 0.070074 | 121.9342 | 121.9655 | 121.8351 | 121.8665
2075.5625 | 122.0718 | -0.11902 | 121.9803 | 0.11727 | 0.023583 | -0.016578 | -0.006703 | 0.013375 | 0.085583 | -0.012357 | 121.9641 | 121.9399 | 121.8605 | 121.7783 | 0.025345 | 0.064423 | -0.006014 | 0.028875 | 0.23629 | 0.1426 | 0.10244 | 0.11232 | 0.13239 | 0.2046 | 0.10666 | 122.0053 | 121.9811 | 121.9017 | 121.8195 | 0.066544 | 0.10562 | 0.035185 | 0.070074 | 121.9387 | 121.9701 | 121.8351 | 121.8665
2077.25 | 122.168 | -0.11444 | 121.9528 | 0.11269 | 0.019004 | -0.016578 | -0.006703 | 0.004219 | 0.076426 | -0.026092 | 121.9732 | 121.9353 | 121.8696 | 121.7783 | 0.034501 | 0.069001 | -0.006014 | 0.028875 | 0.22714 | 0.13345 | 0.097863 | 0.10774 | 0.11866 | 0.19087 | 0.088349 | 122.0144 | 121.9765 | 121.9108 | 121.8195 | 0.0757 | 0.1102 | 0.035185 | 0.070074 | 121.9387 | 121.9792 | 121.8351 | 121.8756
2078.9375 | 122.0947 | -0.12817 | 121.9711 | 0.11269 | 0.019004 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 121.9687 | 121.9353 | 121.865 | 121.7875 | 0.020767 | 0.064423 | -0.010593 | 0.019719 | 0.24087 | 0.14718 | 0.11617 | 0.12147 | 0.13697 | 0.21376 | 0.11124 | 122.0099 | 121.9765 | 121.9062 | 121.8287 | 0.061966 | 0.10562 | 0.030606 | 0.060918 | 121.9479 | 121.9793 | 121.8443 | 121.8756
2080.6875 | 122.2092 | -0.1236 | 121.9666 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 121.9732 | 121.9444 | 121.8742 | 121.7829 | 0.016188 | 0.064423 | -0.010593 | 0.019719 | 0.24087 | 0.1426 | 0.10244 | 0.11231 | 0.12781 | 0.20918 | 0.10208 | 122.0144 | 121.9856 | 121.9154 | 121.8241 | 0.057387 | 0.10562 | 0.030606 | 0.060918 | 121.957 | 121.9838 | 121.858 | 121.8848
2082.3906 | 122.0718 | -0.14648 | 122.0032 | 0.11727 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 121.9732 | 121.9399 | 121.8696 | 121.7875 | 0.025345 | 0.069001 | -0.006014 | 0.033454 | 0.26376 | 0.16549 | 0.12991 | 0.13978 | 0.15528 | 0.23207 | 0.13413 | 122.0144 | 121.9811 | 121.9108 | 121.8287 | 0.066544 | 0.1102 | 0.035185 | 0.074653 | 121.9479 | 121.9792 | 121.8443 | 121.8756
2084.1406 | 122.1313 | -0.12817 | 121.9894 | 0.11269 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 121.9732 | 121.9444 | 121.8696 | 121.792 | 0.025345 | 0.064423 | -0.010593 | 0.019719 | 0.24087 | 0.15176 | 0.10702 | 0.11689 | 0.13697 | 0.20918 | 0.11124 | 122.0144 | 121.9856 | 121.9108 | 121.8332 | 0.066544 | 0.10562 | 0.030606 | 0.060918 | 121.9479 | 121.9838 | 121.8443 | 121.8802
2085.8281 | 122.1451 | -0.14648 | 121.9482 | 0.11727 | 0.019004 | -0.021157 | -0.006703 | 0.017953 | 0.081005 | -0.016936 | 121.9778 | 121.9399 | 121.8742 | 121.792 | 0.01161 | 0.059844 | -0.006014 | 0.024297 | 0.26376 | 0.16549 | 0.12533 | 0.13978 | 0.16444 | 0.22749 | 0.12955 | 122.019 | 121.9811 | 121.9154 | 121.8332 | 0.052809 | 0.10104 | 0.035185 | 0.065496 | 121.9662 | 121.9838 | 121.8626 | 121.8802
2087.5781 | 122.168 | -0.082397 | 121.9482 | 0.12185 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 121.9778 | 121.949 | 121.8742 | 121.792 | 0.016188 | 0.059844 | -0.010593 | 0.019719 | 0.20425 | 0.11056 | 0.06124 | 0.071116 | 0.091194 | 0.1634 | 0.060883 | 122.019 | 121.9902 | 121.9154 | 121.8332 | 0.057387 | 0.10104 | 0.030606 | 0.060918 | 121.9616 | 121.9884 | 121.858 | 121.8848
2089.2656 | 122.1863 | -0.10986 | 121.9757 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.076426 | -0.021514 | 121.9916 | 121.9536 | 121.8788 | 121.7966 | 0.020767 | 0.059844 | -0.006014 | 0.024297 | 0.22256 | 0.12887 | 0.088706 | 0.098582 | 0.12324 | 0.18629 | 0.088349 | 122.0327 | 121.9948 | 121.92 | 121.8378 | 0.061966 | 0.10104 | 0.035185 | 0.065496 | 121.9708 | 121.9976 | 121.858 | 121.8848
2091.0156 | 122.1451 | -0.11902 | 121.9803 | 0.10812 | 0.028162 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.026092 | 121.9824 | 121.9536 | 121.8788 | 121.8012 | 0.020767 | 0.055266 | -0.010593 | 0.024297 | 0.22714 | 0.14718 | 0.097862 | 0.10316 | 0.13239 | 0.2046 | 0.092927 | 122.0236 | 121.9948 | 121.92 | 121.8424 | 0.061966 | 0.096465 | 0.030606 | 0.065496 | 121.9616 | 121.993 | 121.858 | 121.8894
2092.7656 | 122.2321 | -0.082397 | 121.9803 | 0.11269 | 0.023583 | -0.021157 | -0.020438 | 0.004219 | 0.076426 | -0.026092 | 121.9778 | 121.9582 | 121.8788 | 121.8012 | 0.016188 | 0.050688 | -0.006014 | 0.028875 | 0.19509 | 0.10598 | 0.06124 | 0.061959 | 0.086616 | 0.15882 | 0.056305 | 122.019 | 121.9994 | 121.92 | 121.8424 | 0.057387 | 0.091887 | 0.035185 | 0.070074 | 121.9616 | 121.9838 | 121.8626 | 121.8848
2094.5312 | 122.1954 | -0.11444 | 121.9711 | 0.11269 | 0.019004 | -0.025735 | -0.020438 | 0.004219 | 0.085583 | -0.021514 | 121.9916 | 121.9582 | 121.8788 | 121.8058 | 0.016188 | 0.055266 | -0.006014 | 0.024297 | 0.22714 | 0.13345 | 0.088706 | 0.094003 | 0.11866 | 0.20002 | 0.092927 | 122.0327 | 121.9994 | 121.92 | 121.847 | 0.057387 | 0.096465 | 0.035185 | 0.065496 | 121.9754 | 121.9976 | 121.8626 | 121.8848
2096.2812 | 122.1634 | -0.13733 | 121.9986 | 0.11269 | 0.028162 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.021514 | 121.9916 | 121.9536 | 121.8833 | 121.8058 | 0.016188 | 0.059844 | -0.010593 | 0.024297 | 0.25002 | 0.16549 | 0.11617 | 0.13063 | 0.14155 | 0.22291 | 0.11582 | 122.0327 | 121.9948 | 121.9245 | 121.847 | 0.057387 | 0.10104 | 0.030606 | 0.065496 | 121.9754 | 122.0021 | 121.8672 | 121.8939
2097.9688 | 122.2092 | -0.10986 | 121.9803 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.016936 | 121.987 | 121.9582 | 121.8879 | 121.8058 | 0.01161 | 0.059844 | -0.010593 | 0.019719 | 0.23171 | 0.1426 | 0.088706 | 0.094003 | 0.12324 | 0.19545 | 0.092927 | 122.0282 | 121.9994 | 121.9291 | 121.847 | 0.052809 | 0.10104 | 0.030606 | 0.060918 | 121.9754 | 121.9976 | 121.8763 | 121.8985
2099.7188 | 122.1085 | -0.13733 | 122.0032 | 0.12185 | 0.023583 | -0.016578 | -0.002124 | 0.004219 | 0.09474 | -0.021514 | 121.9916 | 121.9582 | 121.8833 | 121.8058 | 0.020767 | 0.059844 | -0.015171 | 0.028875 | 0.25918 | 0.16091 | 0.12075 | 0.13521 | 0.14155 | 0.23207 | 0.11582 | 122.0327 | 121.9994 | 121.9245 | 121.847 | 0.061966 | 0.10104 | 0.026028 | 0.070074 | 121.9708 | 122.0067 | 121.8626 | 121.8985
2101.4062 | 122.1497 | -0.12817 | 121.9757 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.016936 | 121.9961 | 121.9582 | 121.8971 | 121.8104 | 0.020767 | 0.050688 | -0.015171 | 0.024297 | 0.24545 | 0.15634 | 0.1116 | 0.11231 | 0.13697 | 0.20918 | 0.11124 | 122.0373 | 121.9994 | 121.9383 | 121.8516 | 0.061966 | 0.091887 | 0.026028 | 0.065496 | 121.9754 | 122.0113 | 121.8763 | 121.9122
2103.1719 | 122.1268 | -0.14648 | 121.9986 | 0.11727 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.016936 | 122.0007 | 121.9673 | 121.8879 | 121.8104 | 0.016188 | 0.055266 | -0.024328 | 0.028875 | 0.26376 | 0.17007 | 0.12533 | 0.13062 | 0.15986 | 0.23207 | 0.12955 | 122.0419 | 122.0085 | 121.9291 | 121.8516 | 0.057387 | 0.096465 | 0.016871 | 0.070074 | 121.9845 | 122.025 | 121.8717 | 121.9123
2104.8594 | 122.1634 | -0.09613 | 121.9849 | 0.11727 | 0.028162 | -0.025735 | -0.002124 | 0.008797 | 0.090161 | -0.016936 | 121.9916 | 121.9628 | 121.8971 | 121.8195 | 0.01161 | 0.050688 | -0.010593 | 0.015141 | 0.2134 | 0.12429 | 0.070395 | 0.094006 | 0.10493 | 0.18629 | 0.079194 | 122.0327 | 122.004 | 121.9383 | 121.8607 | 0.052809 | 0.091887 | 0.030606 | 0.05634 | 121.9799 | 122.0021 | 121.8855 | 121.9077
2106.6094 | 122.2321 | -0.10071 | 121.9757 | 0.11269 | 0.019004 | -0.016578 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 121.9961 | 121.9673 | 121.8971 | 121.8195 | 0.016188 | 0.055266 | -0.015171 | 0.024297 | 0.2134 | 0.11971 | 0.08413 | 0.08027 | 0.10951 | 0.18171 | 0.079194 | 122.0373 | 122.0085 | 121.9383 | 121.8607 | 0.057387 | 0.096465 | 0.026028 | 0.065496 | 121.9799 | 122.0113 | 121.8809 | 121.9122
2108.3594 | 122.2275 | -0.07782 | 121.9482 | 0.11269 | 0.023583 | -0.012 | -0.020438 | 0.017953 | 0.081005 | -0.021514 | 121.9961 | 121.9719 | 121.8925 | 121.8149 | 0.020767 | 0.059844 | -0.015171 | 0.019719 | 0.19051 | 0.1014 | 0.06582 | 0.057382 | 0.095773 | 0.15882 | 0.056306 | 122.0373 | 122.0131 | 121.9337 | 121.8561 | 0.061966 | 0.10104 | 0.026028 | 0.060918 | 121.9754 | 122.0113 | 121.8717 | 121.9077
2110.125 | 122.1359 | -0.12817 | 122.0306 | 0.11727 | 0.03274 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 121.9961 | 121.9673 | 121.8925 | 121.8195 | 0.016188 | 0.059844 | -0.010593 | 0.028875 | 0.24545 | 0.16091 | 0.1116 | 0.11689 | 0.13697 | 0.20918 | 0.10666 | 122.0373 | 122.0085 | 121.9337 | 121.8607 | 0.057387 | 0.10104 | 0.030606 | 0.070074 | 121.9799 | 122.0067 | 121.8763 | 121.9031
2111.8281 | 122.2412 | -0.082397 | 121.9849 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.081005 | -0.012357 | 122.0144 | 121.9719 | 121.9062 | 121.8195 | 0.016188 | 0.055266 | -0.006014 | 0.015141 | 0.19967 | 0.10598 | 0.065819 | 0.066537 | 0.086616 | 0.1634 | 0.07004 | 122.0556 | 122.0131 | 121.9474 | 121.8607 | 0.057387 | 0.096465 | 0.035185 | 0.05634 | 121.9983 | 122.0205 | 121.89 | 121.9122
2113.5781 | 122.2366 | -0.091553 | 121.9894 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 122.0099 | 121.9811 | 121.9017 | 121.8195 | 0.016188 | 0.059844 | -0.010593 | 0.024297 | 0.19967 | 0.11514 | 0.070396 | 0.080272 | 0.095772 | 0.17256 | 0.070039 | 122.0511 | 122.0223 | 121.9429 | 121.8607 | 0.057387 | 0.10104 | 0.030606 | 0.065496 | 121.9937 | 122.0205 | 121.8855 | 121.9123
2115.3438 | 122.1176 | -0.13733 | 121.9986 | 0.11727 | 0.03274 | -0.025735 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 122.0099 | 121.9719 | 121.9017 | 121.8195 | 0.020767 | 0.055266 | -0.015171 | 0.024297 | 0.2546 | 0.17007 | 0.11159 | 0.12147 | 0.14155 | 0.22291 | 0.12039 | 122.0511 | 122.0131 | 121.9429 | 121.8607 | 0.061966 | 0.096465 | 0.026028 | 0.065496 | 121.9891 | 122.025 | 121.8809 | 121.9168
2117.1094 | 122.1268 | -0.1236 | 122.049 | 0.12185 | 0.023583 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.0099 | 121.9673 | 121.9062 | 121.8241 | 0.01161 | 0.059844 | -0.010593 | 0.024297 | 0.24545 | 0.14718 | 0.10244 | 0.11689 | 0.13697 | 0.21376 | 0.11124 | 122.0511 | 122.0085 | 121.9474 | 121.8653 | 0.052809 | 0.10104 | 0.030606 | 0.065496 | 121.9983 | 122.0205 | 121.8946 | 121.9168
2118.7969 | 122.1817 | -0.12817 | 122.0123 | 0.11727 | 0.023583 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.0144 | 121.9811 | 121.9017 | 121.8287 | 0.01161 | 0.04611 | -0.015171 | 0.024297 | 0.24545 | 0.15176 | 0.10702 | 0.12147 | 0.13239 | 0.21376 | 0.11124 | 122.0556 | 122.0223 | 121.9429 | 121.8699 | 0.052809 | 0.087309 | 0.026028 | 0.065496 | 122.0028 | 122.0296 | 121.89 | 121.9168
2120.5469 | 122.2595 | -0.086975 | 121.9711 | 0.12643 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.016936 | 122.0099 | 121.9765 | 121.9062 | 121.8149 | 0.016188 | 0.055266 | -0.010593 | 0.019719 | 0.2134 | 0.11056 | 0.065818 | 0.071115 | 0.10035 | 0.17256 | 0.070039 | 122.0511 | 122.0177 | 121.9474 | 121.8561 | 0.057387 | 0.096465 | 0.030606 | 0.060918 | 121.9937 | 122.0205 | 121.89 | 121.9168
2122.3125 | 122.1451 | -0.11902 | 122.0398 | 0.11727 | 0.03274 | -0.025735 | -0.002124 | 0.008797 | 0.085583 | -0.016936 | 122.0099 | 121.9719 | 121.9062 | 121.8195 | 0.01161 | 0.055266 | -0.015171 | 0.024297 | 0.23629 | 0.15176 | 0.093284 | 0.11689 | 0.12782 | 0.2046 | 0.10208 | 122.0511 | 122.0131 | 121.9474 | 121.8607 | 0.052809 | 0.096465 | 0.026028 | 0.065496 | 121.9983 | 122.025 | 121.8946 | 121.9214
2124 | 122.2183 | -0.10986 | 121.994 | 0.11269 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 122.0099 | 121.9765 | 121.9062 | 121.8104 | 0.016188 | 0.059844 | -0.006014 | 0.019719 | 0.22256 | 0.13345 | 0.088706 | 0.098582 | 0.11408 | 0.19087 | 0.088349 | 122.0511 | 122.0177 | 121.9474 | 121.8516 | 0.057387 | 0.10104 | 0.035185 | 0.060918 | 121.9937 | 122.0159 | 121.89 | 121.9122
2125.75 | 122.2366 | -0.07782 | 122.0078 | 0.11269 | 0.028162 | -0.016578 | -0.020438 | 0.013375 | 0.085583 | -0.026092 | 122.0144 | 121.9811 | 121.92 | 121.8195 | 0.016188 | 0.055266 | -0.001436 | 0.019719 | 0.19051 | 0.10598 | 0.061242 | 0.057382 | 0.091195 | 0.1634 | 0.051728 | 122.0556 | 122.0223 | 121.9612 | 121.8607 | 0.057387 | 0.096465 | 0.039763 | 0.060918 | 121.9983 | 122.0159 | 121.9038 | 121.9214
2127.5 | 122.168 | -0.14191 | 122.0398 | 0.10812 | 0.028162 | -0.016578 | -0.011281 | 0.004219 | 0.090161 | -0.021514 | 122.0282 | 121.9811 | 121.9154 | 121.8378 | 0.01161 | 0.059844 | -0.006014 | 0.015141 | 0.25002 | 0.17007 | 0.12533 | 0.13063 | 0.14613 | 0.23207 | 0.12039 | 122.0694 | 122.0223 | 121.9566 | 121.879 | 0.052809 | 0.10104 | 0.035185 | 0.05634 | 122.0166 | 122.0342 | 121.9038 | 121.9214
2129.25 | 122.2458 | -0.091553 | 122.0444 | 0.11269 | 0.019004 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.021514 | 122.019 | 121.9856 | 121.9108 | 121.8241 | 0.007032 | 0.04611 | -0.019749 | 0.024297 | 0.20425 | 0.11056 | 0.070396 | 0.075693 | 0.10493 | 0.17714 | 0.070039 | 122.0602 | 122.0268 | 121.952 | 121.8653 | 0.048231 | 0.087309 | 0.02145 | 0.065496 | 122.012 | 122.0388 | 121.9038 | 121.9306
2130.9531 | 122.1451 | -0.13275 | 122.0398 | 0.11727 | 0.028162 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.026092 | 122.019 | 121.9856 | 121.92 | 121.8333 | 0.002454 | 0.059844 | -0.015171 | 0.019719 | 0.25002 | 0.16091 | 0.11617 | 0.12605 | 0.14155 | 0.21833 | 0.10666 | 122.0602 | 122.0268 | 121.9612 | 121.8745 | 0.043653 | 0.10104 | 0.026028 | 0.060918 | 122.0166 | 122.0342 | 121.9175 | 121.9351
2132.7031 | 122.1222 | -0.13733 | 122.0444 | 0.11269 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.090161 | -0.012357 | 122.0282 | 121.9856 | 121.9108 | 121.8333 | 0.01161 | 0.050688 | -0.015171 | 0.019719 | 0.25002 | 0.16091 | 0.11617 | 0.12605 | 0.1507 | 0.22749 | 0.12497 | 122.0694 | 122.0268 | 121.952 | 121.8745 | 0.052809 | 0.091887 | 0.026028 | 0.060918 | 122.0166 | 122.0433 | 121.8992 | 121.926
2134.4531 | 122.2824 | -0.086975 | 122.0123 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 122.0282 | 121.9902 | 121.9154 | 121.8333 | 0.01161 | 0.059844 | -0.019749 | 0.019719 | 0.19967 | 0.11056 | 0.070397 | 0.075694 | 0.091194 | 0.16798 | 0.065461 | 122.0694 | 122.0314 | 121.9566 | 121.8745 | 0.052809 | 0.10104 | 0.02145 | 0.060918 | 122.0166 | 122.0479 | 121.9038 | 121.9351
2136.2188 | 122.1451 | -0.1236 | 122.0261 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.017953 | 0.085583 | -0.012357 | 122.0236 | 121.9902 | 121.92 | 121.8287 | 0.016188 | 0.055266 | -0.015171 | 0.019719 | 0.23629 | 0.15176 | 0.10244 | 0.11231 | 0.14155 | 0.20918 | 0.11124 | 122.0648 | 122.0314 | 121.9612 | 121.8699 | 0.057387 | 0.096465 | 0.026028 | 0.060918 | 122.0074 | 122.0388 | 121.9038 | 121.9351
2137.9062 | 122.2733 | -0.091553 | 121.994 | 0.11269 | 0.023583 | -0.025735 | -0.006703 | 0.004219 | 0.090161 | -0.016936 | 122.0236 | 121.9948 | 121.9108 | 121.8333 | 0.016188 | 0.050688 | -0.015171 | 0.015141 | 0.20425 | 0.11514 | 0.065818 | 0.08485 | 0.095772 | 0.18171 | 0.074617 | 122.0648 | 122.036 | 121.952 | 121.8745 | 0.057387 | 0.091887 | 0.026028 | 0.05634 | 122.0074 | 122.0388 | 121.8946 | 121.926
2139.6406 | 122.2412 | -0.10071 | 122.0123 | 0.11269 | 0.023583 | -0.012 | -0.011281 | 0.017953 | 0.081005 | -0.016936 | 122.0328 | 121.9948 | 121.92 | 121.8378 | 0.016188 | 0.041532 | -0.010593 | 0.024297 | 0.2134 | 0.12429 | 0.088708 | 0.089427 | 0.11866 | 0.18171 | 0.083772 | 122.074 | 122.036 | 121.9612 | 121.879 | 0.057387 | 0.082731 | 0.030606 | 0.065496 | 122.0166 | 122.0434 | 121.9038 | 121.9306
2141.3906 | 122.1222 | -0.14191 | 122.0398 | 0.11727 | 0.023583 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.021514 | 122.0282 | 121.9948 | 121.9245 | 121.8378 | 0.01161 | 0.04611 | -0.015171 | 0.019719 | 0.25918 | 0.16549 | 0.12991 | 0.1352 | 0.14613 | 0.22291 | 0.12039 | 122.0694 | 122.036 | 121.9657 | 121.879 | 0.052809 | 0.087309 | 0.026028 | 0.060918 | 122.0166 | 122.0433 | 121.9129 | 121.9397
2143.1562 | 122.2549 | -0.086975 | 122.0169 | 0.11269 | 0.023583 | -0.030314 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.0373 | 121.9994 | 121.9154 | 121.847 | 0.01161 | 0.050688 | -0.015171 | 0.024297 | 0.19967 | 0.11056 | 0.056661 | 0.075694 | 0.095772 | 0.16798 | 0.065461 | 122.0785 | 122.0406 | 121.9566 | 121.8882 | 0.052809 | 0.091887 | 0.026028 | 0.065496 | 122.0257 | 122.0525 | 121.9038 | 121.9306
2144.8438 | 122.2778 | -0.07782 | 122.0215 | 0.11727 | 0.03274 | -0.021157 | -0.020438 | 0.013375 | 0.085583 | -0.012357 | 122.0282 | 121.9948 | 121.9245 | 121.8333 | 0.016188 | 0.041532 | -0.015171 | 0.019719 | 0.19509 | 0.11056 | 0.056663 | 0.057382 | 0.091195 | 0.1634 | 0.065463 | 122.0694 | 122.036 | 121.9657 | 121.8745 | 0.057387 | 0.082731 | 0.026028 | 0.060918 | 122.012 | 122.0433 | 121.9084 | 121.9397
2146.6094 | 122.168 | -0.11902 | 122.0444 | 0.10812 | 0.023583 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.016936 | 122.0328 | 122.004 | 121.9291 | 121.8516 | 0.007032 | 0.04611 | -0.010593 | 0.028875 | 0.22714 | 0.1426 | 0.093284 | 0.10316 | 0.12782 | 0.20918 | 0.10208 | 122.074 | 122.0452 | 121.9703 | 121.8928 | 0.048231 | 0.087309 | 0.030606 | 0.070074 | 122.0257 | 122.0434 | 121.9221 | 121.9397
2148.375 | 122.2137 | -0.086975 | 122.0398 | 0.11727 | 0.028162 | -0.021157 | -0.011281 | 0.017953 | 0.081005 | -0.021514 | 122.0328 | 122.004 | 121.9291 | 121.8424 | 0.01161 | 0.050688 | -0.010593 | 0.019719 | 0.20425 | 0.11514 | 0.065818 | 0.075694 | 0.10493 | 0.16798 | 0.065461 | 122.074 | 122.0452 | 121.9703 | 121.8836 | 0.052809 | 0.091887 | 0.030606 | 0.060918 | 122.0211 | 122.0434 | 121.9175 | 121.9397
2150.0625 | 122.2321 | -0.082397 | 121.9803 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | -0.000359 | 0.071848 | -0.012357 | 122.0373 | 122.004 | 121.9245 | 121.847 | 0.01161 | 0.055266 | -0.015171 | 0.019719 | 0.19967 | 0.10598 | 0.06124 | 0.071116 | 0.082038 | 0.15424 | 0.07004 | 122.0785 | 122.0452 | 121.9657 | 121.8882 | 0.052809 | 0.096465 | 0.026028 | 0.060918 | 122.0257 | 122.0525 | 121.9129 | 121.9397
2151.8125 | 122.2046 | -0.10529 | 122.0261 | 0.12185 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.0328 | 121.9948 | 121.9245 | 121.847 | 0.007032 | 0.050688 | -0.019749 | 0.028875 | 0.22714 | 0.13345 | 0.084129 | 0.094005 | 0.11408 | 0.18629 | 0.08835 | 122.074 | 122.036 | 121.9657 | 121.8882 | 0.048231 | 0.091887 | 0.02145 | 0.070074 | 122.0257 | 122.0525 | 121.9175 | 121.9443
2153.5938 | 122.2229 | -0.10071 | 122.0306 | 0.10812 | 0.03274 | -0.025735 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 122.0419 | 121.9994 | 121.9383 | 121.847 | 0.01161 | 0.04611 | -0.010593 | 0.019719 | 0.20882 | 0.13345 | 0.074973 | 0.084848 | 0.10951 | 0.18629 | 0.079194 | 122.0831 | 122.0406 | 121.9795 | 121.8882 | 0.052809 | 0.087309 | 0.030606 | 0.060918 | 122.0303 | 122.0525 | 121.9267 | 121.9489
2155.2656 | 122.2321 | -0.09613 | 122.0078 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 122.0465 | 122.004 | 121.9291 | 121.8516 | 0.002454 | 0.055266 | -0.015171 | 0.019719 | 0.20882 | 0.12429 | 0.074973 | 0.08027 | 0.10493 | 0.18171 | 0.074616 | 122.0877 | 122.0452 | 121.9703 | 121.8928 | 0.043653 | 0.096465 | 0.026028 | 0.060918 | 122.044 | 122.0617 | 121.9267 | 121.9443
2157.0156 | 122.1771 | -0.10986 | 122.0261 | 0.11269 | 0.023583 | -0.025735 | -0.011281 | 0.013375 | 0.081005 | -0.012357 | 122.0419 | 122.004 | 121.9337 | 121.8424 | 0.007032 | 0.04611 | -0.015171 | 0.015141 | 0.22256 | 0.13345 | 0.084128 | 0.098582 | 0.12324 | 0.19087 | 0.097506 | 122.0831 | 122.0452 | 121.9749 | 121.8836 | 0.048231 | 0.087309 | 0.026028 | 0.05634 | 122.0349 | 122.0571 | 121.9267 | 121.9489
2158.7188 | 122.1542 | -0.14191 | 122.0718 | 0.10812 | 0.028162 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.021514 | 122.0419 | 121.9994 | 121.9337 | 121.8561 | 0.016188 | 0.059844 | -0.006014 | 0.015141 | 0.25002 | 0.17007 | 0.12075 | 0.13063 | 0.15528 | 0.22749 | 0.12039 | 122.0831 | 122.0406 | 121.9749 | 121.8973 | 0.057387 | 0.10104 | 0.035185 | 0.05634 | 122.0257 | 122.0479 | 121.9175 | 121.9397
2160.4688 | 122.2321 | -0.082397 | 122.0352 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.0419 | 122.0085 | 121.9337 | 121.8516 | 0.002454 | 0.04611 | -0.015171 | 0.015141 | 0.19509 | 0.11056 | 0.06124 | 0.071116 | 0.091194 | 0.1634 | 0.065461 | 122.0831 | 122.0497 | 121.9749 | 121.8928 | 0.043653 | 0.087309 | 0.026028 | 0.05634 | 122.0395 | 122.0571 | 121.9313 | 121.9489
2162.2344 | 122.2458 | -0.091553 | 122.0306 | 0.11269 | 0.028162 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.021514 | 122.0511 | 122.004 | 121.9337 | 121.8561 | 0.007032 | 0.04611 | -0.019749 | 0.015141 | 0.20425 | 0.11971 | 0.070396 | 0.08485 | 0.10493 | 0.17714 | 0.070039 | 122.0923 | 122.0452 | 121.9749 | 121.8973 | 0.048231 | 0.087309 | 0.02145 | 0.05634 | 122.044 | 122.0708 | 121.9267 | 121.9535
2164 | 122.2824 | -0.07782 | 122.0398 | 0.11727 | 0.019004 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.03067 | 122.0511 | 122.0085 | 121.9383 | 121.8561 | 0.01161 | 0.050688 | -0.015171 | 0.015141 | 0.19509 | 0.096824 | 0.056663 | 0.071117 | 0.086617 | 0.15882 | 0.04715 | 122.0923 | 122.0497 | 121.9795 | 121.8973 | 0.052809 | 0.091887 | 0.026028 | 0.05634 | 122.0395 | 122.0662 | 121.9267 | 121.9535
2165.7031 | 122.2641 | -0.091553 | 122.0032 | 0.11269 | 0.03274 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.012357 | 122.0556 | 122.0223 | 121.9383 | 121.8607 | 0.002454 | 0.050688 | -0.006014 | 0.015141 | 0.20425 | 0.12429 | 0.074975 | 0.08485 | 0.10493 | 0.17256 | 0.079196 | 122.0968 | 122.0635 | 121.9795 | 121.9019 | 0.043653 | 0.091887 | 0.035185 | 0.05634 | 122.0532 | 122.0617 | 121.9358 | 121.9443
2167.4531 | 122.2916 | -0.068665 | 122.0078 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.021514 | 122.0556 | 122.0085 | 121.9383 | 121.8653 | 0.002454 | 0.041532 | -0.019749 | 0.019719 | 0.18136 | 0.092248 | 0.047508 | 0.061962 | 0.072884 | 0.14967 | 0.047151 | 122.0968 | 122.0497 | 121.9795 | 121.9065 | 0.043653 | 0.082731 | 0.02145 | 0.060918 | 122.0532 | 122.0754 | 121.9358 | 121.958
2169.1406 | 122.1588 | -0.12817 | 122.0627 | 0.11727 | 0.03274 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.016936 | 122.0511 | 122.0085 | 121.9474 | 121.8607 | 0.01161 | 0.04611 | -0.010593 | 0.015141 | 0.24545 | 0.16091 | 0.1116 | 0.11689 | 0.14155 | 0.21376 | 0.11124 | 122.0923 | 122.0497 | 121.9886 | 121.9019 | 0.052809 | 0.087309 | 0.030606 | 0.05634 | 122.0395 | 122.0617 | 121.9358 | 121.958
2170.9062 | 122.2092 | -0.10529 | 122.081 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.012357 | 122.0511 | 122.0085 | 121.952 | 121.8561 | 0.002454 | 0.04611 | -0.019749 | 0.015141 | 0.22256 | 0.12887 | 0.084129 | 0.094005 | 0.11408 | 0.18629 | 0.092929 | 122.0923 | 122.0497 | 121.9932 | 121.8973 | 0.043653 | 0.087309 | 0.02145 | 0.05634 | 122.0486 | 122.0708 | 121.9496 | 121.9718
2172.6719 | 122.1405 | -0.1236 | 122.0764 | 0.11269 | 0.03274 | -0.016578 | -0.002124 | 0.008797 | 0.090161 | -0.012357 | 122.0511 | 122.0177 | 121.9429 | 121.8653 | 0.01161 | 0.050688 | -0.019749 | 0.015141 | 0.23629 | 0.15634 | 0.10702 | 0.12147 | 0.13239 | 0.21376 | 0.11124 | 122.0923 | 122.0589 | 121.9841 | 121.9065 | 0.052809 | 0.091887 | 0.02145 | 0.05634 | 122.0395 | 122.0708 | 121.9313 | 121.9626
2174.3594 | 122.2092 | -0.091553 | 122.0581 | 0.10812 | 0.03274 | -0.012 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 122.0511 | 122.0177 | 121.9474 | 121.8561 | 0.016188 | 0.04611 | -0.015171 | 0.019719 | 0.19967 | 0.12429 | 0.079553 | 0.080272 | 0.10493 | 0.18171 | 0.074617 | 122.0923 | 122.0589 | 121.9886 | 121.8973 | 0.057387 | 0.087309 | 0.026028 | 0.060918 | 122.0349 | 122.0662 | 121.9313 | 121.9626
2176.125 | 122.2778 | -0.064087 | 122.0261 | 0.11269 | 0.028162 | -0.012 | -0.01586 | 0.008797 | 0.076426 | -0.016936 | 122.0465 | 122.0177 | 121.9429 | 121.8699 | 0.01161 | 0.050688 | -0.019749 | 0.019719 | 0.17678 | 0.092249 | 0.052087 | 0.048227 | 0.072884 | 0.14051 | 0.047151 | 122.0877 | 122.0589 | 121.9841 | 121.9111 | 0.052809 | 0.091887 | 0.02145 | 0.060918 | 122.0349 | 122.0662 | 121.9313 | 121.9626
2177.8906 | 122.168 | -0.12817 | 122.0581 | 0.11269 | 0.037319 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.016936 | 122.0556 | 122.0223 | 121.9474 | 121.8745 | 0.002454 | 0.041532 | -0.028906 | 0.019719 | 0.24087 | 0.16549 | 0.11617 | 0.13063 | 0.14155 | 0.20918 | 0.11124 | 122.0968 | 122.0635 | 121.9886 | 121.9157 | 0.043653 | 0.082731 | 0.012293 | 0.060918 | 122.0532 | 122.0846 | 121.945 | 121.9763
2179.6406 | 122.2458 | -0.09613 | 122.0352 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 122.0602 | 122.0177 | 121.952 | 121.8653 | 0.002454 | 0.041532 | -0.010593 | 0.019719 | 0.20882 | 0.12429 | 0.074973 | 0.08027 | 0.10493 | 0.18171 | 0.074616 | 122.1014 | 122.0589 | 121.9932 | 121.9065 | 0.043653 | 0.082731 | 0.030606 | 0.060918 | 122.0578 | 122.0708 | 121.9496 | 121.9626
2181.3281 | 122.2549 | -0.07782 | 122.0444 | 0.10812 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.0602 | 122.0223 | 121.9474 | 121.8653 | 0.007032 | 0.055266 | -0.015171 | 0.019719 | 0.18594 | 0.10598 | 0.056663 | 0.066539 | 0.086617 | 0.15882 | 0.060884 | 122.1014 | 122.0635 | 121.9886 | 121.9065 | 0.048231 | 0.096465 | 0.026028 | 0.060918 | 122.0532 | 122.0754 | 121.9404 | 121.9626
2183.0938 | 122.2687 | -0.073242 | 122.0673 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.026092 | 122.0602 | 122.0223 | 121.952 | 121.8699 | 0.007032 | 0.04611 | -0.015171 | 0.019719 | 0.18594 | 0.1014 | 0.052085 | 0.061961 | 0.082039 | 0.15425 | 0.04715 | 122.1014 | 122.0635 | 121.9932 | 121.9111 | 0.048231 | 0.087309 | 0.026028 | 0.060918 | 122.0532 | 122.0754 | 121.945 | 121.9672
2184.8438 | 122.3007 | -0.068665 | 122.0123 | 0.10812 | 0.028162 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.021514 | 122.0602 | 122.0223 | 121.9429 | 121.8653 | 0.01161 | 0.04611 | -0.019749 | 0.015141 | 0.17678 | 0.096827 | 0.052087 | 0.061962 | 0.077462 | 0.15425 | 0.047151 | 122.1014 | 122.0635 | 121.9841 | 121.9065 | 0.052809 | 0.087309 | 0.02145 | 0.05634 | 122.0486 | 122.08 | 121.9313 | 121.9626
2186.6094 | 122.2916 | -0.07782 | 122.0352 | 0.11269 | 0.023583 | -0.030314 | -0.01586 | 0.004219 | 0.090161 | -0.016936 | 122.0694 | 122.0177 | 121.9566 | 121.879 | 0.007032 | 0.050688 | -0.015171 | 0.019719 | 0.19051 | 0.1014 | 0.047506 | 0.06196 | 0.082039 | 0.16798 | 0.060884 | 122.1106 | 122.0589 | 121.9978 | 121.9202 | 0.048231 | 0.091887 | 0.026028 | 0.060918 | 122.0624 | 122.0846 | 121.9496 | 121.9718
2188.2969 | 122.1588 | -0.1236 | 122.0535 | 0.11269 | 0.03274 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.016936 | 122.0694 | 122.0269 | 121.9566 | 121.8745 | 0.002454 | 0.04611 | -0.019749 | 0.010563 | 0.23629 | 0.15634 | 0.10702 | 0.11689 | 0.13239 | 0.2046 | 0.10666 | 122.1106 | 122.0681 | 121.9978 | 121.9157 | 0.043653 | 0.087309 | 0.02145 | 0.051762 | 122.0669 | 122.0891 | 121.9541 | 121.9763
2190.0469 | 122.168 | -0.13275 | 122.0947 | 0.11727 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 122.0694 | 122.0223 | 121.9612 | 121.8745 | 0.01161 | 0.04611 | -0.015171 | 0.019719 | 0.25002 | 0.16091 | 0.11159 | 0.12147 | 0.14155 | 0.22291 | 0.12039 | 122.1106 | 122.0635 | 122.0024 | 121.9157 | 0.052809 | 0.087309 | 0.026028 | 0.060918 | 122.0578 | 122.0846 | 121.9496 | 121.9763
2191.7344 | 122.1817 | -0.10986 | 122.081 | 0.11727 | 0.03274 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.021514 | 122.0694 | 122.0269 | 121.9566 | 121.8745 | 0.007032 | 0.04611 | -0.015171 | 0.019719 | 0.22714 | 0.1426 | 0.088706 | 0.10316 | 0.12324 | 0.19545 | 0.088349 | 122.1106 | 122.0681 | 121.9978 | 121.9157 | 0.048231 | 0.087309 | 0.026028 | 0.060918 | 122.0624 | 122.0846 | 121.9496 | 121.9718
2193.4844 | 122.2229 | -0.10071 | 122.081 | 0.11727 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.090161 | -0.021514 | 122.0694 | 122.0314 | 121.9612 | 121.8745 | 0.002454 | 0.050688 | -0.010593 | 0.015141 | 0.21798 | 0.12429 | 0.08413 | 0.084848 | 0.10493 | 0.19087 | 0.079194 | 122.1106 | 122.0726 | 122.0024 | 121.9157 | 0.043653 | 0.091887 | 0.030606 | 0.05634 | 122.0669 | 122.08 | 121.9587 | 121.9718
2195.2344 | 122.1725 | -0.1236 | 122.0993 | 0.11269 | 0.028162 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.021514 | 122.0694 | 122.0269 | 121.9566 | 121.8836 | 0.002454 | 0.04611 | -0.019749 | 0.015141 | 0.23629 | 0.15176 | 0.1116 | 0.12147 | 0.12781 | 0.2046 | 0.10208 | 122.1106 | 122.0681 | 121.9978 | 121.9248 | 0.043653 | 0.087309 | 0.02145 | 0.05634 | 122.0669 | 122.0891 | 121.9541 | 121.9763
2197 | 122.3053 | -0.082397 | 122.0398 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.021514 | 122.074 | 122.0314 | 121.9612 | 121.8745 | 0.007032 | 0.041532 | -0.015171 | 0.015141 | 0.19509 | 0.11056 | 0.06124 | 0.066537 | 0.086616 | 0.17256 | 0.060883 | 122.1152 | 122.0726 | 122.0024 | 121.9157 | 0.048231 | 0.082731 | 0.026028 | 0.05634 | 122.0669 | 122.0891 | 121.9541 | 121.9763
2198.7031 | 122.2321 | -0.091553 | 122.0535 | 0.10812 | 0.028162 | -0.012 | -0.006703 | 0.004219 | 0.085583 | -0.021514 | 122.0694 | 122.0314 | 121.9658 | 121.879 | -0.002124 | 0.041532 | -0.019749 | 0.010563 | 0.19967 | 0.11971 | 0.079553 | 0.08485 | 0.095772 | 0.17714 | 0.070039 | 122.1106 | 122.0726 | 122.007 | 121.9202 | 0.039075 | 0.082731 | 0.02145 | 0.051762 | 122.0715 | 122.0891 | 121.9679 | 121.9855
2200.4688 | 122.287 | -0.054932 | 122.0306 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.0785 | 122.036 | 121.9612 | 121.8882 | 0.01161 | 0.04611 | -0.019749 | 0.010563 | 0.16763 | 0.078515 | 0.038354 | 0.043651 | 0.063729 | 0.14509 | 0.037996 | 122.1197 | 122.0772 | 122.0024 | 121.9294 | 0.052809 | 0.087309 | 0.02145 | 0.051762 | 122.0669 | 122.0983 | 121.9496 | 121.9809
2202.2188 | 122.3145 | -0.073242 | 122.0398 | 0.11269 | 0.028162 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.021514 | 122.074 | 122.0314 | 121.9566 | 121.8836 | 0.007032 | 0.036954 | -0.024328 | 0.015141 | 0.18594 | 0.1014 | 0.052085 | 0.057382 | 0.077461 | 0.15425 | 0.051728 | 122.1152 | 122.0726 | 121.9978 | 121.9248 | 0.048231 | 0.078153 | 0.016871 | 0.05634 | 122.0669 | 122.0983 | 121.9496 | 121.9809
2203.9219 | 122.1909 | -0.13733 | 122.0673 | 0.12643 | 0.028162 | -0.025735 | -0.002124 | 0.004219 | 0.085583 | -0.016936 | 122.0785 | 122.0406 | 121.9658 | 121.8836 | 0.002454 | 0.041532 | -0.015171 | 0.015141 | 0.26376 | 0.16549 | 0.11159 | 0.13521 | 0.14155 | 0.22291 | 0.12039 | 122.1197 | 122.0818 | 122.007 | 121.9248 | 0.043653 | 0.082731 | 0.026028 | 0.05634 | 122.0761 | 122.0937 | 121.9633 | 121.9809
2205.6719 | 122.1954 | -0.11902 | 122.0993 | 0.11269 | 0.019004 | -0.012 | -0.006703 | 0.004219 | 0.085583 | -0.021514 | 122.0785 | 122.0269 | 121.9658 | 121.8882 | 0.002454 | 0.041532 | -0.024328 | 0.019719 | 0.23171 | 0.13802 | 0.10702 | 0.11232 | 0.12324 | 0.2046 | 0.097505 | 122.1197 | 122.0681 | 122.007 | 121.9294 | 0.043653 | 0.082731 | 0.016871 | 0.060918 | 122.0761 | 122.1029 | 121.9633 | 121.9901
2207.3594 | 122.287 | -0.07782 | 122.0535 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.026092 | 122.074 | 122.0314 | 121.9703 | 121.8882 | 0.007032 | 0.041532 | -0.010593 | 0.015141 | 0.19051 | 0.1014 | 0.056663 | 0.06196 | 0.082039 | 0.15882 | 0.051728 | 122.1152 | 122.0726 | 122.0115 | 121.9294 | 0.048231 | 0.082731 | 0.030606 | 0.05634 | 122.0669 | 122.0846 | 121.9633 | 121.9809
2209.1094 | 122.2275 | -0.11444 | 122.0718 | 0.10354 | 0.028162 | -0.016578 | -0.002124 | 0.008797 | 0.085583 | -0.016936 | 122.0785 | 122.0452 | 121.9703 | 121.8928 | -0.002124 | 0.041532 | -0.019749 | 0.019719 | 0.21798 | 0.1426 | 0.097863 | 0.11232 | 0.12324 | 0.20002 | 0.097505 | 122.1197 | 122.0864 | 122.0115 | 121.934 | 0.039075 | 0.082731 | 0.02145 | 0.060918 | 122.0807 | 122.0983 | 121.9725 | 121.9901
2210.7969 | 122.1725 | -0.10529 | 122.113 | 0.11727 | 0.023583 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.0831 | 122.0406 | 121.9703 | 121.879 | -0.002124 | 0.04611 | -0.019749 | 0.015141 | 0.22256 | 0.12887 | 0.084129 | 0.098583 | 0.11866 | 0.19545 | 0.092929 | 122.1243 | 122.0818 | 122.0115 | 121.9202 | 0.039075 | 0.087309 | 0.02145 | 0.05634 | 122.0852 | 122.1029 | 121.9725 | 121.9901
2212.5469 | 122.2824 | -0.068665 | 122.081 | 0.10812 | 0.019004 | -0.021157 | -0.011281 | 0.017953 | 0.085583 | -0.016936 | 122.0831 | 122.0406 | 121.9703 | 121.8928 | 0.007032 | 0.050688 | -0.024328 | 0.010563 | 0.17678 | 0.087669 | 0.047508 | 0.057384 | 0.086618 | 0.15425 | 0.051729 | 122.1243 | 122.0818 | 122.0115 | 121.934 | 0.048231 | 0.091887 | 0.016871 | 0.051762 | 122.0761 | 122.1074 | 121.9633 | 121.9947
2214.25 | 122.1817 | -0.11902 | 122.1039 | 0.11727 | 0.028162 | -0.012 | 0.002454 | 0.022531 | 0.090161 | -0.012357 | 122.0877 | 122.0452 | 121.9703 | 121.8882 | 0.007032 | 0.041532 | -0.019749 | 0.015141 | 0.23629 | 0.14718 | 0.10702 | 0.12147 | 0.14155 | 0.20918 | 0.10666 | 122.1289 | 122.0864 | 122.0115 | 121.9294 | 0.048231 | 0.082731 | 0.02145 | 0.05634 | 122.0807 | 122.1074 | 121.9633 | 121.9901
2216 | 122.2961 | -0.059509 | 122.0261 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.021514 | 122.0831 | 122.0498 | 121.9703 | 121.8882 | 0.002454 | 0.041532 | -0.015171 | 0.010563 | 0.17678 | 0.083092 | 0.038352 | 0.048228 | 0.068306 | 0.14509 | 0.037995 | 122.1243 | 122.0909 | 122.0115 | 121.9294 | 0.043653 | 0.082731 | 0.026028 | 0.051762 | 122.0807 | 122.0983 | 121.9679 | 121.9855
2217.6875 | 122.2961 | -0.068665 | 122.0627 | 0.10812 | 0.023583 | -0.025735 | -0.006703 | 0.008797 | 0.081005 | -0.021514 | 122.0785 | 122.0498 | 121.9749 | 121.8882 | 0.002454 | 0.036954 | -0.019749 | 0.010563 | 0.17678 | 0.092248 | 0.04293 | 0.061962 | 0.077462 | 0.14967 | 0.047151 | 122.1197 | 122.0909 | 122.0161 | 121.9294 | 0.043653 | 0.078153 | 0.02145 | 0.051762 | 122.0761 | 122.0983 | 121.9725 | 121.9947
2219.4375 | 122.1817 | -0.11902 | 122.1268 | 0.11269 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.090161 | -0.007779 | 122.0831 | 122.0452 | 121.9749 | 121.8928 | 0.007032 | 0.04611 | -0.024328 | 0.010563 | 0.23171 | 0.1426 | 0.097862 | 0.10774 | 0.13239 | 0.20918 | 0.11124 | 122.1243 | 122.0864 | 122.0161 | 121.934 | 0.048231 | 0.087309 | 0.016871 | 0.051762 | 122.0761 | 122.1074 | 121.9679 | 121.9992
2221.2031 | 122.3465 | -0.059509 | 122.049 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.021514 | 122.0831 | 122.0498 | 121.9658 | 121.8928 | -0.002124 | 0.041532 | -0.019749 | 0.015141 | 0.1722 | 0.083092 | 0.038352 | 0.052806 | 0.068306 | 0.14509 | 0.037995 | 122.1243 | 122.0909 | 122.007 | 121.934 | 0.039075 | 0.082731 | 0.02145 | 0.05634 | 122.0852 | 122.1029 | 121.9679 | 121.9855
2222.8906 | 122.3328 | -0.082397 | 122.0306 | 0.11269 | 0.019004 | -0.025735 | -0.011281 | 0.004219 | 0.081005 | -0.021514 | 122.0831 | 122.0543 | 121.9749 | 121.8974 | -0.002124 | 0.036954 | -0.028906 | 0.015141 | 0.19509 | 0.1014 | 0.056662 | 0.071116 | 0.086616 | 0.1634 | 0.060883 | 122.1243 | 122.0955 | 122.0161 | 121.9386 | 0.039075 | 0.078153 | 0.012293 | 0.05634 | 122.0852 | 122.112 | 121.977 | 122.0038
2224.6406 | 122.3053 | -0.068665 | 122.0215 | 0.11269 | 0.03274 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.016936 | 122.0877 | 122.0498 | 121.9749 | 121.8836 | -0.002124 | 0.04611 | -0.024328 | 0.010563 | 0.18136 | 0.1014 | 0.056665 | 0.066541 | 0.08204 | 0.15425 | 0.051729 | 122.1289 | 122.0909 | 122.0161 | 121.9248 | 0.039075 | 0.087309 | 0.016871 | 0.051762 | 122.0898 | 122.112 | 121.977 | 121.9992
2226.3281 | 122.1909 | -0.11902 | 122.0856 | 0.11727 | 0.019004 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.016936 | 122.0877 | 122.0406 | 121.9841 | 121.9065 | 0.002454 | 0.041532 | -0.015171 | 0.019719 | 0.23629 | 0.13802 | 0.097862 | 0.11232 | 0.13239 | 0.20918 | 0.10208 | 122.1289 | 122.0818 | 122.0253 | 121.9477 | 0.043653 | 0.082731 | 0.026028 | 0.060918 | 122.0852 | 122.1029 | 121.9816 | 121.9992
2228.0781 | 122.2412 | -0.10529 | 122.0856 | 0.11727 | 0.023583 | -0.012 | -0.002124 | 0.013375 | 0.090161 | -0.016936 | 122.0831 | 122.0543 | 121.9886 | 121.8928 | 0.007032 | 0.041532 | -0.019749 | 0.015141 | 0.22256 | 0.12887 | 0.093286 | 0.10316 | 0.11866 | 0.19545 | 0.08835 | 122.1243 | 122.0955 | 122.0298 | 121.934 | 0.048231 | 0.082731 | 0.02145 | 0.05634 | 122.0761 | 122.1029 | 121.9816 | 122.0084
2229.8281 | 122.1771 | -0.13275 | 122.0993 | 0.11727 | 0.023583 | -0.016578 | -0.006703 | 0.017953 | 0.090161 | -0.016936 | 122.0877 | 122.0543 | 121.9795 | 121.8974 | -0.002124 | 0.036954 | -0.019749 | 0.010563 | 0.25002 | 0.15633 | 0.11617 | 0.12605 | 0.1507 | 0.22291 | 0.11582 | 122.1289 | 122.0955 | 122.0207 | 121.9386 | 0.039075 | 0.078153 | 0.02145 | 0.051762 | 122.0898 | 122.1074 | 121.9816 | 121.9992
2231.5625 | 122.287 | -0.086975 | 122.0673 | 0.12185 | 0.023583 | -0.016578 | -0.002124 | 0.004219 | 0.085583 | -0.016936 | 122.0923 | 122.0452 | 121.9841 | 121.9019 | -0.006702 | 0.041532 | -0.024328 | 0.010563 | 0.20883 | 0.11056 | 0.070397 | 0.084851 | 0.091194 | 0.17256 | 0.070039 | 122.1335 | 122.0864 | 122.0253 | 121.9431 | 0.034497 | 0.082731 | 0.016871 | 0.051762 | 122.099 | 122.1166 | 121.9908 | 122.0084
2233.3125 | 122.1725 | -0.11444 | 122.0901 | 0.11727 | 0.023583 | -0.025735 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.0877 | 122.0543 | 121.9841 | 121.8974 | 0.002454 | 0.036954 | -0.024328 | 0.005985 | 0.23171 | 0.13802 | 0.088706 | 0.10774 | 0.12324 | 0.20002 | 0.10208 | 122.1289 | 122.0955 | 122.0253 | 121.9386 | 0.043653 | 0.078153 | 0.016871 | 0.047184 | 122.0852 | 122.112 | 121.9816 | 122.0084
2235 | 122.168 | -0.11444 | 122.1176 | 0.11269 | 0.023583 | -0.016578 | -0.002124 | 0.013375 | 0.09474 | -0.012357 | 122.0969 | 122.0543 | 121.9841 | 121.9019 | -0.002124 | 0.041532 | -0.015171 | 0.019719 | 0.22714 | 0.13802 | 0.097863 | 0.11232 | 0.12782 | 0.20918 | 0.10208 | 122.1381 | 122.0955 | 122.0253 | 121.9431 | 0.039075 | 0.082731 | 0.026028 | 0.060918 | 122.099 | 122.112 | 121.9862 | 121.9992
2236.7344 | 122.3419 | -0.07782 | 122.0581 | 0.11269 | 0.019004 | -0.025735 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.0923 | 122.0589 | 121.9841 | 121.9019 | 0.002454 | 0.041532 | -0.024328 | 0.015141 | 0.19051 | 0.096824 | 0.052085 | 0.066539 | 0.086617 | 0.1634 | 0.060884 | 122.1335 | 122.1001 | 122.0253 | 121.9431 | 0.043653 | 0.082731 | 0.016871 | 0.05634 | 122.0898 | 122.1166 | 121.9816 | 122.0084
2238.4375 | 122.3053 | -0.064087 | 122.0535 | 0.11727 | 0.028162 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.106 | 122.0543 | 121.9841 | 121.8974 | 0.007032 | 0.041532 | -0.024328 | 0.019719 | 0.18136 | 0.092249 | 0.047509 | 0.052806 | 0.072884 | 0.14509 | 0.047151 | 122.1472 | 122.0955 | 122.0253 | 121.9386 | 0.048231 | 0.082731 | 0.016871 | 0.060918 | 122.099 | 122.1303 | 121.977 | 122.0084
2240.1875 | 122.2458 | -0.10986 | 122.1268 | 0.11269 | 0.03274 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.1014 | 122.0589 | 121.9841 | 121.9019 | -0.002124 | 0.041532 | -0.019749 | 0.005985 | 0.22256 | 0.1426 | 0.088706 | 0.10316 | 0.12324 | 0.19545 | 0.092927 | 122.1426 | 122.1001 | 122.0253 | 121.9431 | 0.039075 | 0.082731 | 0.02145 | 0.047184 | 122.1036 | 122.1212 | 121.9862 | 122.0038
2241.9375 | 122.1817 | -0.13733 | 122.1085 | 0.11269 | 0.03274 | -0.016578 | -0.006703 | 0.004219 | 0.076426 | -0.026092 | 122.1014 | 122.0543 | 121.9886 | 121.9065 | 0.002454 | 0.041532 | -0.015171 | 0.019719 | 0.25002 | 0.17007 | 0.12075 | 0.13063 | 0.14155 | 0.21376 | 0.11124 | 122.1426 | 122.0955 | 122.0298 | 121.9477 | 0.043653 | 0.082731 | 0.026028 | 0.060918 | 122.099 | 122.1166 | 121.9862 | 122.0038
2243.6406 | 122.1771 | -0.11444 | 122.1085 | 0.11727 | 0.028162 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.016936 | 122.1014 | 122.0589 | 121.9932 | 121.9019 | -0.002124 | 0.041532 | -0.006014 | 0.010563 | 0.23171 | 0.1426 | 0.093284 | 0.10774 | 0.12782 | 0.2046 | 0.097505 | 122.1426 | 122.1001 | 122.0344 | 121.9431 | 0.039075 | 0.082731 | 0.035185 | 0.051762 | 122.1036 | 122.1074 | 121.9953 | 121.9992
2245.3906 | 122.3099 | -0.073242 | 122.0581 | 0.11727 | 0.03274 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 122.1014 | 122.0589 | 121.9886 | 121.9065 | -0.011281 | 0.032376 | -0.015171 | 0.005985 | 0.19051 | 0.10598 | 0.056664 | 0.071118 | 0.082039 | 0.15425 | 0.060885 | 122.1426 | 122.1001 | 122.0298 | 121.9477 | 0.029918 | 0.073575 | 0.026028 | 0.047184 | 122.1127 | 122.1166 | 121.9999 | 122.0038
2247.1406 | 122.2046 | -0.13275 | 122.1085 | 0.11269 | 0.014425 | -0.016578 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.1014 | 122.0635 | 121.9841 | 121.9157 | 0.002454 | 0.041532 | -0.019749 | 0.005985 | 0.24545 | 0.14718 | 0.11617 | 0.12605 | 0.14613 | 0.21833 | 0.11582 | 122.1426 | 122.1047 | 122.0253 | 121.9569 | 0.043653 | 0.082731 | 0.02145 | 0.047184 | 122.099 | 122.1212 | 121.9816 | 122.0038
2248.8281 | 122.319 | -0.07782 | 122.0581 | 0.12185 | 0.03274 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 122.1106 | 122.0589 | 121.9932 | 121.9065 | -0.002124 | 0.036954 | -0.019749 | 0.005985 | 0.19967 | 0.11056 | 0.056663 | 0.06196 | 0.082039 | 0.15882 | 0.060884 | 122.1518 | 122.1001 | 122.0344 | 121.9477 | 0.039075 | 0.078153 | 0.02145 | 0.047184 | 122.1127 | 122.1303 | 121.9953 | 122.013
2250.5781 | 122.2092 | -0.10071 | 122.1085 | 0.11269 | 0.037319 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.012357 | 122.1014 | 122.0589 | 121.9932 | 121.9111 | 0.007032 | 0.036954 | -0.028906 | 0.015141 | 0.2134 | 0.13803 | 0.08413 | 0.089427 | 0.11408 | 0.18629 | 0.088351 | 122.1426 | 122.1001 | 122.0344 | 121.9523 | 0.048231 | 0.078153 | 0.012293 | 0.05634 | 122.0944 | 122.1303 | 121.9862 | 122.0221
2252.2656 | 122.1817 | -0.10986 | 122.1359 | 0.12185 | 0.023583 | -0.016578 | -0.006703 | 0.013375 | 0.090161 | -0.016936 | 122.106 | 122.0635 | 121.9932 | 121.9065 | -0.002124 | 0.036954 | -0.024328 | 0.015141 | 0.23171 | 0.13345 | 0.093285 | 0.10316 | 0.12324 | 0.20002 | 0.092927 | 122.1472 | 122.1047 | 122.0344 | 121.9477 | 0.039075 | 0.078153 | 0.016871 | 0.05634 | 122.1081 | 122.1303 | 121.9953 | 122.0175
2254.0312 | 122.1863 | -0.11444 | 122.0993 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.016936 | 122.106 | 122.0589 | 121.9932 | 121.9111 | -0.006702 | 0.041532 | -0.019749 | 0.010563 | 0.22714 | 0.13802 | 0.097863 | 0.10316 | 0.12782 | 0.20002 | 0.097505 | 122.1472 | 122.1001 | 122.0344 | 121.9523 | 0.034497 | 0.082731 | 0.02145 | 0.051762 | 122.1127 | 122.1258 | 121.9999 | 122.013
2255.7812 | 122.287 | -0.091553 | 122.0581 | 0.11727 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 122.106 | 122.0589 | 121.9932 | 121.9065 | 0.002454 | 0.036954 | -0.019749 | 0.015141 | 0.20883 | 0.11056 | 0.070396 | 0.075693 | 0.10035 | 0.17256 | 0.070039 | 122.1472 | 122.1001 | 122.0344 | 121.9477 | 0.043653 | 0.078153 | 0.02145 | 0.05634 | 122.1036 | 122.1258 | 121.9908 | 122.013
2257.4688 | 122.2595 | -0.086975 | 122.0764 | 0.11727 | 0.028162 | -0.021157 | -0.006703 | 0.013375 | 0.081005 | -0.012357 | 122.1152 | 122.0726 | 121.9978 | 121.9111 | -0.002124 | 0.036954 | -0.024328 | 0.010563 | 0.20425 | 0.11514 | 0.065818 | 0.080272 | 0.10035 | 0.16798 | 0.074618 | 122.1564 | 122.1138 | 122.039 | 121.9523 | 0.039075 | 0.078153 | 0.016871 | 0.051762 | 122.1173 | 122.1395 | 121.9999 | 122.0221
2259.2344 | 122.2458 | -0.1236 | 122.1222 | 0.11727 | 0.037319 | -0.021157 | -0.011281 | 0.017953 | 0.09474 | -0.016936 | 122.1152 | 122.0726 | 121.9978 | 121.9157 | -0.002124 | 0.036954 | -0.024328 | 0.015141 | 0.24087 | 0.16092 | 0.10244 | 0.11231 | 0.14155 | 0.21834 | 0.10666 | 122.1564 | 122.1138 | 122.039 | 121.9569 | 0.039075 | 0.078153 | 0.016871 | 0.05634 | 122.1173 | 122.1395 | 121.9999 | 122.0221
2260.9375 | 122.1817 | -0.1236 | 122.1176 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.007779 | 122.1106 | 122.0681 | 121.9886 | 121.9111 | -0.002124 | 0.036954 | -0.019749 | 0.010563 | 0.24087 | 0.14718 | 0.10702 | 0.11231 | 0.13697 | 0.20918 | 0.11582 | 122.1518 | 122.1093 | 122.0298 | 121.9523 | 0.039075 | 0.078153 | 0.02145 | 0.051762 | 122.1127 | 122.1303 | 121.9908 | 122.0084
2262.6875 | 122.2092 | -0.11444 | 122.1085 | 0.10812 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.021514 | 122.106 | 122.0681 | 121.9932 | 121.9111 | -0.002124 | 0.036954 | -0.024328 | -0.003172 | 0.22256 | 0.1426 | 0.093284 | 0.10316 | 0.12324 | 0.2046 | 0.092927 | 122.1472 | 122.1093 | 122.0344 | 121.9523 | 0.039075 | 0.078153 | 0.016871 | 0.038027 | 122.1081 | 122.1303 | 121.9953 | 122.0175
2264.4375 | 122.1954 | -0.10986 | 122.1222 | 0.10812 | 0.028162 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.106 | 122.0681 | 121.9978 | 121.9157 | -0.002124 | 0.04611 | -0.024328 | 0.010563 | 0.21798 | 0.13803 | 0.088706 | 0.10316 | 0.12324 | 0.19545 | 0.092927 | 122.1472 | 122.1093 | 122.039 | 121.9569 | 0.039075 | 0.087309 | 0.016871 | 0.051762 | 122.1081 | 122.1303 | 121.9999 | 122.0221
2266.1406 | 122.3236 | -0.073242 | 122.0993 | 0.10812 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.076426 | -0.021514 | 122.1197 | 122.0726 | 122.007 | 121.9157 | -0.006702 | 0.036954 | -0.015171 | 0.005985 | 0.18136 | 0.096825 | 0.056664 | 0.057382 | 0.082039 | 0.14967 | 0.051728 | 122.1609 | 122.1138 | 122.0482 | 121.9569 | 0.034497 | 0.078153 | 0.026028 | 0.047184 | 122.1265 | 122.1349 | 122.0137 | 122.0221
2267.8906 | 122.2549 | -0.11444 | 122.1222 | 0.11269 | 0.023583 | -0.016578 | -0.002124 | 0.008797 | 0.090161 | -0.016936 | 122.1152 | 122.0772 | 121.9932 | 121.9157 | -0.006702 | 0.041532 | -0.010593 | 0.019719 | 0.22714 | 0.13802 | 0.097863 | 0.11232 | 0.12324 | 0.2046 | 0.097505 | 122.1564 | 122.1184 | 122.0344 | 121.9569 | 0.034497 | 0.082731 | 0.030606 | 0.060918 | 122.1219 | 122.1258 | 121.9999 | 122.0038
2269.6406 | 122.287 | -0.07782 | 122.0627 | 0.10812 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.076426 | -0.012357 | 122.106 | 122.0772 | 121.9932 | 121.9111 | 0.002454 | 0.04611 | -0.033484 | 0.015141 | 0.18594 | 0.1014 | 0.056663 | 0.071117 | 0.086617 | 0.15425 | 0.065463 | 122.1472 | 122.1184 | 122.0344 | 121.9523 | 0.043653 | 0.087309 | 0.007715 | 0.05634 | 122.1036 | 122.1395 | 121.9908 | 122.0267
2271.3281 | 122.3007 | -0.082397 | 122.0856 | 0.10812 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 122.1152 | 122.0726 | 121.9978 | 121.9157 | -0.006702 | 0.041532 | -0.019749 | 0.005985 | 0.19051 | 0.1014 | 0.065819 | 0.071116 | 0.086616 | 0.16798 | 0.065461 | 122.1564 | 122.1138 | 122.039 | 121.9569 | 0.034497 | 0.082731 | 0.02145 | 0.047184 | 122.1219 | 122.1349 | 122.0045 | 122.0175
2273.0781 | 122.2 | -0.12817 | 122.1176 | 0.11269 | 0.028162 | -0.025735 | -0.006703 | 0.013375 | 0.09474 | -0.021514 | 122.1106 | 122.0726 | 122.0024 | 121.9157 | 0.002454 | 0.041532 | -0.010593 | 0.010563 | 0.24087 | 0.15634 | 0.10244 | 0.12147 | 0.14155 | 0.22291 | 0.10666 | 122.1518 | 122.1138 | 122.0436 | 121.9569 | 0.043653 | 0.082731 | 0.030606 | 0.051762 | 122.1081 | 122.1212 | 121.9999 | 122.013
2274.8438 | 122.2504 | -0.11444 | 122.1176 | 0.11269 | 0.028162 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.021514 | 122.1106 | 122.0681 | 122.0024 | 121.9203 | 0.002454 | 0.050688 | -0.015171 | 0.015141 | 0.22714 | 0.1426 | 0.097863 | 0.10774 | 0.11866 | 0.2046 | 0.092927 | 122.1518 | 122.1093 | 122.0436 | 121.9615 | 0.043653 | 0.091887 | 0.026028 | 0.05634 | 122.1081 | 122.1258 | 121.9999 | 122.0175
2276.6094 | 122.2 | -0.13733 | 122.1405 | 0.11727 | 0.028162 | -0.016578 | -0.011281 | 0.017953 | 0.085583 | -0.021514 | 122.1106 | 122.0726 | 122.0024 | 121.9111 | 0.002454 | 0.041532 | -0.015171 | 0.010563 | 0.2546 | 0.16549 | 0.12075 | 0.12605 | 0.15528 | 0.22291 | 0.11582 | 122.1518 | 122.1138 | 122.0436 | 121.9523 | 0.043653 | 0.082731 | 0.026028 | 0.051762 | 122.1081 | 122.1258 | 121.9999 | 122.0175
2278.375 | 122.2961 | -0.10071 | 122.081 | 0.10812 | 0.03274 | -0.021157 | -0.002124 | 0.008797 | 0.085583 | -0.021514 | 122.1106 | 122.0726 | 121.9886 | 121.9111 | 0.002454 | 0.04611 | -0.019749 | 0.019719 | 0.20882 | 0.13345 | 0.079551 | 0.098584 | 0.10951 | 0.18629 | 0.079194 | 122.1518 | 122.1138 | 122.0298 | 121.9523 | 0.043653 | 0.087309 | 0.02145 | 0.060918 | 122.1081 | 122.1303 | 121.9862 | 122.0084
2280.1406 | 122.2778 | -0.086975 | 122.0718 | 0.11269 | 0.028162 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.1197 | 122.0681 | 121.9932 | 121.9157 | -0.002124 | 0.050688 | -0.015171 | 0.005985 | 0.19967 | 0.11514 | 0.065818 | 0.075694 | 0.095772 | 0.17714 | 0.070039 | 122.1609 | 122.1093 | 122.0344 | 121.9569 | 0.039075 | 0.091887 | 0.026028 | 0.047184 | 122.1219 | 122.1349 | 121.9953 | 122.0084
2281.8281 | 122.3328 | -0.073242 | 122.0901 | 0.11727 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 122.1197 | 122.0681 | 121.9978 | 121.9203 | 0.007032 | 0.04611 | -0.015171 | 0.019719 | 0.19051 | 0.096825 | 0.052085 | 0.066539 | 0.082039 | 0.15882 | 0.056306 | 122.1609 | 122.1093 | 122.039 | 121.9615 | 0.048231 | 0.087309 | 0.026028 | 0.060918 | 122.1127 | 122.1349 | 121.9908 | 122.013
2283.5781 | 122.3602 | -0.059509 | 122.0627 | 0.10812 | 0.028162 | -0.025735 | -0.01586 | 0.004219 | 0.076426 | -0.021514 | 122.1152 | 122.0681 | 121.9978 | 121.9203 | 0.002454 | 0.041532 | -0.019749 | 0.010563 | 0.16762 | 0.087671 | 0.033774 | 0.043649 | 0.063728 | 0.13594 | 0.037995 | 122.1564 | 122.1093 | 122.039 | 121.9615 | 0.043653 | 0.082731 | 0.02145 | 0.051762 | 122.1127 | 122.1349 | 121.9953 | 122.0175
2285.3281 | 122.3419 | -0.07782 | 122.081 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.1106 | 122.0726 | 122.0024 | 121.9203 | 0.007032 | 0.036954 | -0.019749 | 0.015141 | 0.18594 | 0.1014 | 0.056663 | 0.066539 | 0.086617 | 0.16798 | 0.060884 | 122.1518 | 122.1138 | 122.0436 | 121.9615 | 0.048231 | 0.078153 | 0.02145 | 0.05634 | 122.1036 | 122.1303 | 121.9953 | 122.0221
2287.0781 | 122.3419 | -0.10071 | 122.0856 | 0.11269 | 0.03274 | -0.025735 | -0.011281 | 0.017953 | 0.081005 | -0.021514 | 122.1197 | 122.0726 | 122.0024 | 121.9203 | 0.002454 | 0.041532 | -0.010593 | 0.010563 | 0.2134 | 0.13345 | 0.074973 | 0.089427 | 0.11866 | 0.18171 | 0.079194 | 122.1609 | 122.1138 | 122.0436 | 121.9615 | 0.043653 | 0.082731 | 0.030606 | 0.051762 | 122.1173 | 122.1303 | 121.9999 | 122.013
2288.8438 | 122.2275 | -0.11444 | 122.113 | 0.12185 | 0.028162 | -0.002842 | -0.011281 | 0.008797 | 0.09474 | -0.012357 | 122.1152 | 122.0726 | 122.0024 | 121.9157 | 0.002454 | 0.041532 | -0.019749 | 0.015141 | 0.23629 | 0.1426 | 0.1116 | 0.10316 | 0.12324 | 0.20918 | 0.10208 | 122.1564 | 122.1138 | 122.0436 | 121.9569 | 0.043653 | 0.082731 | 0.02145 | 0.05634 | 122.1127 | 122.1349 | 121.9999 | 122.0221
2290.5312 | 122.2275 | -0.10986 | 122.1268 | 0.11269 | 0.028162 | -0.016578 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.1197 | 122.0681 | 121.9978 | 121.9203 | 0.002454 | 0.050688 | -0.015171 | 0.010563 | 0.22256 | 0.13803 | 0.093285 | 0.10316 | 0.12324 | 0.19545 | 0.092927 | 122.1609 | 122.1093 | 122.039 | 121.9615 | 0.043653 | 0.091887 | 0.026028 | 0.051762 | 122.1173 | 122.1349 | 121.9953 | 122.013
2292.2812 | 122.319 | -0.064087 | 122.081 | 0.10812 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.081005 | -0.021514 | 122.1197 | 122.0726 | 122.007 | 121.9248 | 0.002454 | 0.041532 | -0.019749 | 0.015141 | 0.1722 | 0.08767 | 0.047509 | 0.048227 | 0.072884 | 0.14509 | 0.042573 | 122.1609 | 122.1138 | 122.0482 | 121.966 | 0.043653 | 0.082731 | 0.02145 | 0.05634 | 122.1173 | 122.1395 | 122.0045 | 122.0267
2294.0312 | 122.3145 | -0.086975 | 122.0901 | 0.10812 | 0.028162 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.026092 | 122.1152 | 122.0726 | 122.0024 | 121.9203 | 0.002454 | 0.041532 | -0.015171 | 0.019719 | 0.19509 | 0.11514 | 0.065818 | 0.071115 | 0.095772 | 0.17256 | 0.060883 | 122.1564 | 122.1138 | 122.0436 | 121.9615 | 0.043653 | 0.082731 | 0.026028 | 0.060918 | 122.1127 | 122.1303 | 121.9999 | 122.0175
2295.7188 | 122.2229 | -0.12817 | 122.1085 | 0.11269 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.016936 | 122.1197 | 122.0772 | 121.9978 | 121.9248 | 0.007032 | 0.04611 | -0.019749 | 0.019719 | 0.24087 | 0.15176 | 0.10702 | 0.11689 | 0.14155 | 0.21376 | 0.11124 | 122.1609 | 122.1184 | 122.039 | 121.966 | 0.048231 | 0.087309 | 0.02145 | 0.060918 | 122.1127 | 122.1395 | 121.9908 | 122.0175
2297.4688 | 122.2229 | -0.1236 | 122.1039 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.1243 | 122.0772 | 122.0024 | 121.9248 | 0.002454 | 0.04611 | -0.019749 | 0.015141 | 0.23629 | 0.14718 | 0.10244 | 0.11689 | 0.13697 | 0.21376 | 0.11124 | 122.1655 | 122.1184 | 122.0436 | 121.966 | 0.043653 | 0.087309 | 0.02145 | 0.05634 | 122.1219 | 122.1441 | 121.9999 | 122.0221
2299.2344 | 122.2961 | -0.07782 | 122.1039 | 0.10812 | 0.028162 | -0.012 | -0.006703 | 0.008797 | 0.081005 | -0.021514 | 122.1243 | 122.0772 | 122.0161 | 121.9248 | -0.002124 | 0.036954 | -0.019749 | 0.015141 | 0.18594 | 0.10598 | 0.06582 | 0.071117 | 0.086617 | 0.15882 | 0.056306 | 122.1655 | 122.1184 | 122.0573 | 121.966 | 0.039075 | 0.078153 | 0.02145 | 0.05634 | 122.1265 | 122.1441 | 122.0182 | 122.0359
2300.9375 | 122.3145 | -0.09613 | 122.081 | 0.11727 | 0.028162 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.021514 | 122.1152 | 122.0818 | 122.0024 | 121.9248 | 0.007032 | 0.04611 | -0.024328 | 0.015141 | 0.2134 | 0.12429 | 0.079552 | 0.089427 | 0.10493 | 0.18171 | 0.074616 | 122.1564 | 122.123 | 122.0436 | 121.966 | 0.048231 | 0.087309 | 0.016871 | 0.05634 | 122.1081 | 122.1395 | 121.9953 | 122.0267
2302.6875 | 122.2092 | -0.1236 | 122.1176 | 0.11269 | 0.03274 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.016936 | 122.1289 | 122.0818 | 122.007 | 121.9203 | 0.002454 | 0.04611 | -0.019749 | 0.019719 | 0.23629 | 0.15634 | 0.10702 | 0.10774 | 0.13239 | 0.20918 | 0.10666 | 122.1701 | 122.123 | 122.0482 | 121.9615 | 0.043653 | 0.087309 | 0.02145 | 0.060918 | 122.1265 | 122.1487 | 122.0045 | 122.0267
2304.4531 | 122.2092 | -0.13275 | 122.1268 | 0.12185 | 0.037319 | -0.016578 | -0.006703 | 0.008797 | 0.09474 | -0.012357 | 122.1197 | 122.0726 | 122.0115 | 121.9294 | 0.01161 | 0.041532 | -0.019749 | 0.015141 | 0.2546 | 0.17007 | 0.11617 | 0.12605 | 0.14155 | 0.22749 | 0.12039 | 122.1609 | 122.1138 | 122.0527 | 121.9706 | 0.052809 | 0.082731 | 0.02145 | 0.05634 | 122.1081 | 122.1395 | 121.9999 | 122.0313
2306.2031 | 122.2275 | -0.1236 | 122.1313 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 122.1289 | 122.0772 | 122.007 | 121.9294 | 0.002454 | 0.041532 | -0.015171 | 0.010563 | 0.24087 | 0.14718 | 0.10244 | 0.11231 | 0.13697 | 0.21376 | 0.10666 | 122.1701 | 122.1184 | 122.0482 | 121.9706 | 0.043653 | 0.082731 | 0.026028 | 0.051762 | 122.1265 | 122.1441 | 122.0045 | 122.0221
2307.9531 | 122.2275 | -0.12817 | 122.1313 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.021514 | 122.1243 | 122.0864 | 122.0115 | 121.934 | 0.002454 | 0.041532 | -0.019749 | 0.010563 | 0.24087 | 0.15176 | 0.1116 | 0.11689 | 0.13697 | 0.21834 | 0.10666 | 122.1655 | 122.1276 | 122.0527 | 121.9752 | 0.043653 | 0.082731 | 0.02145 | 0.051762 | 122.1219 | 122.1441 | 122.0091 | 122.0313
2309.6406 | 122.2504 | -0.091553 | 122.1268 | 0.10812 | 0.019004 | -0.007421 | -0.011281 | -0.000359 | 0.076426 | -0.016936 | 122.1152 | 122.0818 | 122.0115 | 121.9294 | 0.002454 | 0.04611 | -0.024328 | 0.015141 | 0.19967 | 0.11056 | 0.084132 | 0.080272 | 0.091194 | 0.16798 | 0.074617 | 122.1564 | 122.123 | 122.0527 | 121.9706 | 0.043653 | 0.087309 | 0.016871 | 0.05634 | 122.1127 | 122.1395 | 122.0091 | 122.0359
2311.3906 | 122.3373 | -0.068665 | 122.0718 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.09474 | -0.016936 | 122.1289 | 122.0772 | 122.0024 | 121.9294 | 0.007032 | 0.041532 | -0.033484 | 0.015141 | 0.18136 | 0.092248 | 0.052087 | 0.057384 | 0.077462 | 0.16341 | 0.051729 | 122.1701 | 122.1184 | 122.0436 | 121.9706 | 0.048231 | 0.082731 | 0.007715 | 0.05634 | 122.1219 | 122.1624 | 121.9953 | 122.0359
2313.1406 | 122.2595 | -0.09613 | 122.1313 | 0.10812 | 0.028162 | -0.021157 | -0.006703 | 0.013375 | 0.085583 | -0.021514 | 122.1289 | 122.0955 | 122.0207 | 121.9386 | 0.007032 | 0.050688 | -0.015171 | 0.015141 | 0.20425 | 0.12429 | 0.074973 | 0.089427 | 0.1095 | 0.18171 | 0.074616 | 122.1701 | 122.1367 | 122.0619 | 121.9798 | 0.048231 | 0.091887 | 0.026028 | 0.05634 | 122.1219 | 122.1441 | 122.0137 | 122.0359
2314.8438 | 122.2229 | -0.1236 | 122.1268 | 0.11269 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 122.1289 | 122.0864 | 122.0115 | 121.9294 | -0.002124 | 0.036954 | -0.019749 | 0.005985 | 0.23629 | 0.15176 | 0.10702 | 0.11231 | 0.13697 | 0.21376 | 0.10666 | 122.1701 | 122.1276 | 122.0527 | 121.9706 | 0.039075 | 0.078153 | 0.02145 | 0.047184 | 122.131 | 122.1487 | 122.0137 | 122.0313
2316.5938 | 122.3557 | -0.073242 | 122.0718 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.021514 | 122.1335 | 122.091 | 122.0115 | 121.9294 | 0.007032 | 0.041532 | -0.019749 | 0.010563 | 0.18594 | 0.096825 | 0.052085 | 0.057382 | 0.086617 | 0.15882 | 0.051728 | 122.1747 | 122.1322 | 122.0527 | 121.9706 | 0.048231 | 0.082731 | 0.02145 | 0.051762 | 122.1265 | 122.1532 | 122.0045 | 122.0313
2318.3438 | 122.2275 | -0.14191 | 122.1313 | 0.11727 | 0.023583 | -0.012 | -0.01586 | 0.008797 | 0.090161 | -0.021514 | 122.1289 | 122.0818 | 122.0207 | 121.934 | -0.002124 | 0.041532 | -0.028906 | 0.010563 | 0.25918 | 0.16549 | 0.12991 | 0.12605 | 0.1507 | 0.23207 | 0.12039 | 122.1701 | 122.123 | 122.0619 | 121.9752 | 0.039075 | 0.082731 | 0.012293 | 0.051762 | 122.131 | 122.1578 | 122.0228 | 122.0496
2320.1094 | 122.2275 | -0.10529 | 122.1176 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 122.1335 | 122.0818 | 122.0161 | 121.9386 | -0.002124 | 0.04611 | -0.019749 | 0.005985 | 0.21798 | 0.12887 | 0.084129 | 0.098583 | 0.11408 | 0.18629 | 0.097507 | 122.1747 | 122.123 | 122.0573 | 121.9798 | 0.039075 | 0.087309 | 0.02145 | 0.047184 | 122.1356 | 122.1532 | 122.0182 | 122.0359
2321.8125 | 122.2687 | -0.11444 | 122.1176 | 0.11727 | 0.023583 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.003201 | 122.1335 | 122.0818 | 122.0207 | 121.9432 | 0.002454 | 0.041532 | -0.015171 | 0.010563 | 0.23171 | 0.13802 | 0.097863 | 0.10774 | 0.12782 | 0.19545 | 0.11124 | 122.1747 | 122.123 | 122.0619 | 121.9844 | 0.043653 | 0.082731 | 0.026028 | 0.051762 | 122.131 | 122.1487 | 122.0182 | 122.0359
2323.5625 | 122.2275 | -0.11902 | 122.1542 | 0.10812 | 0.019004 | -0.012 | -0.01586 | 0.013375 | 0.090161 | -0.016936 | 122.1381 | 122.091 | 122.0161 | 121.934 | 0.007032 | 0.041532 | -0.024328 | 0.015141 | 0.22714 | 0.13802 | 0.10702 | 0.10316 | 0.13239 | 0.20918 | 0.10208 | 122.1793 | 122.1322 | 122.0573 | 121.9752 | 0.048231 | 0.082731 | 0.016871 | 0.05634 | 122.131 | 122.1624 | 122.0091 | 122.0404
2325.2656 | 122.3557 | -0.068665 | 122.0856 | 0.11269 | 0.019004 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.007779 | 122.1335 | 122.0955 | 122.007 | 121.9386 | -0.002124 | 0.041532 | -0.019749 | 0.019719 | 0.18136 | 0.087669 | 0.052087 | 0.052805 | 0.072884 | 0.15425 | 0.060886 | 122.1747 | 122.1367 | 122.0482 | 121.9798 | 0.039075 | 0.082731 | 0.02145 | 0.060918 | 122.1356 | 122.1532 | 122.0091 | 122.0267
2327.0156 | 122.2733 | -0.1236 | 122.1405 | 0.11727 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.016936 | 122.1335 | 122.091 | 122.0298 | 121.9386 | -0.002124 | 0.041532 | -0.024328 | 0.015141 | 0.24087 | 0.14718 | 0.10702 | 0.11689 | 0.13239 | 0.2046 | 0.10666 | 122.1747 | 122.1322 | 122.071 | 121.9798 | 0.039075 | 0.082731 | 0.016871 | 0.05634 | 122.1356 | 122.1578 | 122.032 | 122.0542
2328.7812 | 122.2275 | -0.12817 | 122.1588 | 0.10812 | 0.028162 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 122.1335 | 122.0864 | 122.0207 | 121.9386 | 0.007032 | 0.041532 | -0.015171 | 0.015141 | 0.23629 | 0.15634 | 0.1116 | 0.11689 | 0.13239 | 0.21376 | 0.11124 | 122.1747 | 122.1276 | 122.0619 | 121.9798 | 0.048231 | 0.082731 | 0.026028 | 0.05634 | 122.1265 | 122.1487 | 122.0137 | 122.0359
2330.5312 | 122.2641 | -0.1236 | 122.1451 | 0.10812 | 0.028162 | -0.021157 | -0.006703 | 0.017953 | 0.090161 | -0.012357 | 122.1381 | 122.091 | 122.0298 | 121.9386 | -0.002124 | 0.036954 | -0.028906 | 0.010563 | 0.23171 | 0.15176 | 0.10244 | 0.11689 | 0.14155 | 0.21376 | 0.11124 | 122.1793 | 122.1322 | 122.071 | 121.9798 | 0.039075 | 0.078153 | 0.012293 | 0.051762 | 122.1402 | 122.167 | 122.032 | 122.0588
2332.2812 | 122.3007 | -0.082397 | 122.1085 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.017953 | 0.081005 | -0.021514 | 122.1335 | 122.091 | 122.0207 | 121.9432 | 0.01161 | 0.041532 | -0.019749 | 0.010563 | 0.19967 | 0.1014 | 0.06124 | 0.071116 | 0.10035 | 0.1634 | 0.060883 | 122.1747 | 122.1322 | 122.0619 | 121.9844 | 0.052809 | 0.082731 | 0.02145 | 0.051762 | 122.1219 | 122.1532 | 122.0091 | 122.0404
2333.9688 | 122.3053 | -0.064087 | 122.113 | 0.11269 | 0.019004 | -0.025735 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.1426 | 122.0955 | 122.0161 | 121.9432 | -0.006702 | 0.041532 | -0.015171 | 0.019719 | 0.17678 | 0.083091 | 0.038352 | 0.052806 | 0.072884 | 0.14967 | 0.05173 | 122.1838 | 122.1367 | 122.0573 | 121.9844 | 0.034497 | 0.082731 | 0.026028 | 0.060918 | 122.1493 | 122.1578 | 122.0228 | 122.0313
2335.7344 | 122.2458 | -0.12817 | 122.1588 | 0.10812 | 0.023583 | -0.025735 | -0.01586 | 0.008797 | 0.085583 | -0.016936 | 122.1335 | 122.1001 | 122.0207 | 121.9386 | 0.002454 | 0.04611 | -0.019749 | 0.010563 | 0.23629 | 0.15176 | 0.10244 | 0.11231 | 0.13697 | 0.21376 | 0.11124 | 122.1747 | 122.1413 | 122.0619 | 121.9798 | 0.043653 | 0.087309 | 0.02145 | 0.051762 | 122.131 | 122.1532 | 122.0182 | 122.0404
2337.4844 | 122.2961 | -0.09613 | 122.1085 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.1426 | 122.0955 | 122.0253 | 121.9432 | 0.002454 | 0.036954 | -0.019749 | 0.015141 | 0.2134 | 0.11513 | 0.074973 | 0.084849 | 0.10493 | 0.17713 | 0.079194 | 122.1838 | 122.1367 | 122.0665 | 121.9844 | 0.043653 | 0.078153 | 0.02145 | 0.05634 | 122.1402 | 122.1624 | 122.0228 | 122.045
2339.2344 | 122.2412 | -0.1236 | 122.1405 | 0.11727 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.012357 | 122.1426 | 122.0955 | 122.0298 | 121.9432 | 0.002454 | 0.036954 | -0.015171 | 0.019719 | 0.24087 | 0.14718 | 0.10244 | 0.10774 | 0.12781 | 0.21376 | 0.11124 | 122.1838 | 122.1367 | 122.071 | 121.9844 | 0.043653 | 0.078153 | 0.026028 | 0.060918 | 122.1402 | 122.1578 | 122.0274 | 122.045
2340.9375 | 122.2275 | -0.1236 | 122.1222 | 0.11727 | 0.019004 | -0.016578 | -0.01586 | 0.013375 | 0.090161 | -0.016936 | 122.1335 | 122.1001 | 122.0253 | 121.9432 | 0.002454 | 0.04611 | -0.024328 | 0.010563 | 0.24087 | 0.1426 | 0.10702 | 0.10774 | 0.13697 | 0.21376 | 0.10666 | 122.1747 | 122.1413 | 122.0665 | 121.9844 | 0.043653 | 0.087309 | 0.016871 | 0.051762 | 122.131 | 122.1578 | 122.0228 | 122.0496
2342.6875 | 122.2961 | -0.086975 | 122.1176 | 0.10354 | 0.019004 | -0.016578 | -0.011281 | 0.013375 | 0.081005 | -0.021514 | 122.1426 | 122.1001 | 122.0207 | 121.9477 | 0.002454 | 0.036954 | -0.024328 | 0.010563 | 0.19051 | 0.10598 | 0.070397 | 0.075694 | 0.10035 | 0.16798 | 0.065461 | 122.1838 | 122.1413 | 122.0619 | 121.9889 | 0.043653 | 0.078153 | 0.016871 | 0.051762 | 122.1402 | 122.167 | 122.0182 | 122.045
2344.4375 | 122.3465 | -0.068665 | 122.081 | 0.11727 | 0.014425 | -0.025735 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.1426 | 122.1001 | 122.0298 | 121.9432 | 0.007032 | 0.041532 | -0.028906 | 0.015141 | 0.18594 | 0.08309 | 0.04293 | 0.057384 | 0.072884 | 0.15425 | 0.056308 | 122.1838 | 122.1413 | 122.071 | 121.9844 | 0.048231 | 0.082731 | 0.012293 | 0.05634 | 122.1356 | 122.1715 | 122.0228 | 122.0588
2346.2188 | 122.2733 | -0.1236 | 122.1405 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.017953 | 0.090161 | -0.016936 | 122.1381 | 122.0955 | 122.0253 | 121.9432 | -0.006702 | 0.036954 | -0.024328 | 0.019719 | 0.23629 | 0.14718 | 0.10244 | 0.10774 | 0.14155 | 0.21376 | 0.10666 | 122.1793 | 122.1367 | 122.0665 | 121.9844 | 0.034497 | 0.078153 | 0.016871 | 0.060918 | 122.1448 | 122.1624 | 122.032 | 122.0496
2347.9062 | 122.2412 | -0.12817 | 122.113 | 0.10812 | 0.019004 | -0.025735 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.1426 | 122.1001 | 122.0253 | 121.9523 | 0.002454 | 0.032376 | -0.024328 | 0.010563 | 0.23629 | 0.14718 | 0.10244 | 0.12147 | 0.14155 | 0.21376 | 0.11124 | 122.1838 | 122.1413 | 122.0665 | 121.9935 | 0.043653 | 0.073575 | 0.016871 | 0.051762 | 122.1402 | 122.167 | 122.0228 | 122.0496
2349.6406 | 122.3602 | -0.054932 | 122.1222 | 0.10812 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.1426 | 122.0955 | 122.0344 | 121.9477 | 0.002454 | 0.036954 | -0.019749 | 0.010563 | 0.16305 | 0.078515 | 0.038354 | 0.043651 | 0.063729 | 0.13594 | 0.033418 | 122.1838 | 122.1367 | 122.0756 | 121.9889 | 0.043653 | 0.078153 | 0.02145 | 0.051762 | 122.1402 | 122.1624 | 122.032 | 122.0542
2351.3906 | 122.2412 | -0.09613 | 122.1359 | 0.10812 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.1426 | 122.1001 | 122.0253 | 121.9523 | 0.002454 | 0.036954 | -0.024328 | 0.015141 | 0.20425 | 0.11513 | 0.074973 | 0.084849 | 0.10493 | 0.18171 | 0.083773 | 122.1838 | 122.1413 | 122.0665 | 121.9935 | 0.043653 | 0.078153 | 0.016871 | 0.05634 | 122.1402 | 122.167 | 122.0228 | 122.0496
2353.1406 | 122.3648 | -0.068665 | 122.1176 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.016936 | 122.1564 | 122.1001 | 122.0253 | 121.9569 | -0.002124 | 0.041532 | -0.015171 | 0.015141 | 0.17678 | 0.092248 | 0.047508 | 0.057384 | 0.072884 | 0.14967 | 0.051729 | 122.1976 | 122.1413 | 122.0665 | 121.9981 | 0.039075 | 0.082731 | 0.026028 | 0.05634 | 122.1585 | 122.1715 | 122.0274 | 122.0404
2354.8438 | 122.2321 | -0.1236 | 122.1497 | 0.10812 | 0.023583 | -0.016578 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.1426 | 122.1001 | 122.0344 | 121.9569 | -0.006702 | 0.032376 | -0.024328 | 0.010563 | 0.23171 | 0.14718 | 0.10702 | 0.11689 | 0.13697 | 0.20918 | 0.10666 | 122.1838 | 122.1413 | 122.0756 | 121.9981 | 0.034497 | 0.073575 | 0.016871 | 0.051762 | 122.1493 | 122.167 | 122.0411 | 122.0588
2356.5938 | 122.319 | -0.07782 | 122.1176 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.085583 | -0.021514 | 122.1472 | 122.1047 | 122.0298 | 121.9477 | -0.006702 | 0.041532 | -0.019749 | 0.015141 | 0.19051 | 0.1014 | 0.056663 | 0.06196 | 0.091195 | 0.1634 | 0.056306 | 122.1884 | 122.1459 | 122.071 | 121.9889 | 0.034497 | 0.082731 | 0.02145 | 0.05634 | 122.1539 | 122.167 | 122.0366 | 122.0496
2358.3594 | 122.3236 | -0.082397 | 122.1039 | 0.10812 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.021514 | 122.1472 | 122.1093 | 122.0344 | 121.9477 | 0.002454 | 0.041532 | -0.024328 | 0.005985 | 0.19051 | 0.1014 | 0.06124 | 0.071116 | 0.091194 | 0.16798 | 0.060883 | 122.1884 | 122.1505 | 122.0756 | 121.9889 | 0.043653 | 0.082731 | 0.016871 | 0.047184 | 122.1448 | 122.1715 | 122.032 | 122.0588
2360.125 | 122.3511 | -0.082397 | 122.1039 | 0.10812 | 0.014425 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 122.1518 | 122.1047 | 122.0344 | 121.9523 | -0.002124 | 0.041532 | -0.010593 | 0.005985 | 0.19051 | 0.096822 | 0.06124 | 0.066537 | 0.086616 | 0.1634 | 0.065461 | 122.193 | 122.1459 | 122.0756 | 121.9935 | 0.039075 | 0.082731 | 0.030606 | 0.047184 | 122.1539 | 122.1624 | 122.0366 | 122.045
2361.8125 | 122.3648 | -0.073242 | 122.1085 | 0.10812 | 0.014425 | -0.016578 | -0.020438 | 0.013375 | 0.081005 | -0.021514 | 122.1518 | 122.1139 | 122.0298 | 121.9477 | -0.002124 | 0.041532 | -0.024328 | 0.010563 | 0.18136 | 0.087667 | 0.056664 | 0.052804 | 0.086617 | 0.15425 | 0.051728 | 122.193 | 122.1551 | 122.071 | 121.9889 | 0.039075 | 0.082731 | 0.016871 | 0.051762 | 122.1539 | 122.1761 | 122.032 | 122.0542
2363.5625 | 122.2824 | -0.091553 | 122.1634 | 0.11269 | 0.03274 | -0.012 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.1518 | 122.1047 | 122.0344 | 121.9569 | -0.002124 | 0.032376 | -0.015171 | 0.015141 | 0.20425 | 0.12429 | 0.079553 | 0.080272 | 0.10035 | 0.17714 | 0.079196 | 122.193 | 122.1459 | 122.0756 | 121.9981 | 0.039075 | 0.073575 | 0.026028 | 0.05634 | 122.1539 | 122.167 | 122.0366 | 122.0496
2365.3281 | 122.3602 | -0.07782 | 122.1176 | 0.10812 | 0.019004 | -0.025735 | -0.01586 | 0.013375 | 0.085583 | -0.016936 | 122.1564 | 122.1093 | 122.0298 | 121.9615 | -0.002124 | 0.041532 | -0.024328 | 0.010563 | 0.18594 | 0.096824 | 0.052085 | 0.06196 | 0.091195 | 0.1634 | 0.060884 | 122.1976 | 122.1505 | 122.071 | 122.0027 | 0.039075 | 0.082731 | 0.016871 | 0.051762 | 122.1585 | 122.1807 | 122.032 | 122.0542
2367.0781 | 122.3694 | -0.064087 | 122.1039 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.012357 | 122.1564 | 122.1047 | 122.0298 | 121.9569 | -0.006702 | 0.041532 | -0.019749 | 0.005985 | 0.1722 | 0.08767 | 0.04293 | 0.052806 | 0.072884 | 0.14509 | 0.05173 | 122.1976 | 122.1459 | 122.071 | 121.9981 | 0.034497 | 0.082731 | 0.02145 | 0.047184 | 122.1631 | 122.1761 | 122.0366 | 122.0496
2368.7812 | 122.2961 | -0.086975 | 122.1039 | 0.11269 | 0.014425 | -0.025735 | -0.01586 | 0.013375 | 0.081005 | -0.021514 | 122.1518 | 122.1047 | 122.039 | 121.9523 | -0.002124 | 0.036954 | -0.019749 | 0.010563 | 0.19967 | 0.1014 | 0.06124 | 0.071115 | 0.10035 | 0.16798 | 0.065461 | 122.193 | 122.1459 | 122.0802 | 121.9935 | 0.039075 | 0.078153 | 0.02145 | 0.051762 | 122.1539 | 122.1715 | 122.0411 | 122.0588
2370.5312 | 122.3465 | -0.045776 | 122.1222 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.012357 | 122.1518 | 122.1093 | 122.039 | 121.9569 | -0.006702 | 0.032376 | -0.019749 | 0.005985 | 0.15847 | 0.069359 | 0.029198 | 0.034495 | 0.054573 | 0.12678 | 0.033419 | 122.193 | 122.1505 | 122.0802 | 121.9981 | 0.034497 | 0.073575 | 0.02145 | 0.047184 | 122.1585 | 122.1715 | 122.0457 | 122.0588
2372.2188 | 122.2641 | -0.091553 | 122.1268 | 0.10354 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 122.1472 | 122.1139 | 122.039 | 121.9569 | 0.002454 | 0.041532 | -0.019749 | 0.005985 | 0.19509 | 0.11971 | 0.074975 | 0.080272 | 0.10493 | 0.18171 | 0.074617 | 122.1884 | 122.1551 | 122.0802 | 121.9981 | 0.043653 | 0.082731 | 0.02145 | 0.047184 | 122.1448 | 122.167 | 122.0366 | 122.0588
2373.9688 | 122.2458 | -0.09613 | 122.168 | 0.11269 | 0.023583 | -0.016578 | -0.01586 | 0.017953 | 0.085583 | -0.012357 | 122.1564 | 122.1047 | 122.039 | 121.9569 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.20882 | 0.11971 | 0.079552 | 0.08027 | 0.11408 | 0.18171 | 0.083773 | 122.1976 | 122.1459 | 122.0802 | 121.9981 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.1631 | 122.1853 | 122.0457 | 122.0679
2375.7188 | 122.3465 | -0.059509 | 122.1222 | 0.11269 | 0.023583 | -0.016578 | -0.011281 | 0.017953 | 0.085583 | -0.016936 | 122.1564 | 122.1139 | 122.0344 | 121.9523 | 0.002454 | 0.036954 | -0.028906 | 0.010563 | 0.1722 | 0.083092 | 0.042931 | 0.048228 | 0.077462 | 0.14509 | 0.042573 | 122.1976 | 122.1551 | 122.0756 | 121.9935 | 0.043653 | 0.078153 | 0.012293 | 0.051762 | 122.1539 | 122.1853 | 122.032 | 122.0633
2377.4688 | 122.2733 | -0.091553 | 122.1497 | 0.12185 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 122.1564 | 122.1093 | 122.0436 | 121.9615 | -0.006702 | 0.036954 | -0.019749 | 0.015141 | 0.2134 | 0.11514 | 0.070396 | 0.080272 | 0.10035 | 0.18171 | 0.079196 | 122.1976 | 122.1505 | 122.0848 | 122.0027 | 0.034497 | 0.078153 | 0.02145 | 0.05634 | 122.1631 | 122.1761 | 122.0503 | 122.0633
2379.1562 | 122.3694 | -0.091553 | 122.0856 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.081005 | -0.021514 | 122.161 | 122.1093 | 122.0344 | 121.9569 | -0.006702 | 0.04611 | -0.019749 | 0.015141 | 0.20425 | 0.11514 | 0.070396 | 0.075693 | 0.10493 | 0.17256 | 0.070039 | 122.2022 | 122.1505 | 122.0756 | 121.9981 | 0.034497 | 0.087309 | 0.02145 | 0.05634 | 122.1677 | 122.1807 | 122.0411 | 122.0542
2380.9219 | 122.3602 | -0.041199 | 122.1039 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.017953 | 0.090161 | -0.016936 | 122.161 | 122.1139 | 122.039 | 121.9615 | -0.002124 | 0.032376 | -0.024328 | 0.005985 | 0.15389 | 0.064782 | 0.020042 | 0.025339 | 0.059152 | 0.13136 | 0.024263 | 122.2022 | 122.1551 | 122.0802 | 122.0027 | 0.039075 | 0.073575 | 0.016871 | 0.047184 | 122.1631 | 122.1853 | 122.0411 | 122.0633
2382.6094 | 122.3694 | -0.068665 | 122.0993 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 122.1518 | 122.1184 | 122.039 | 121.9615 | -0.006702 | 0.041532 | -0.028906 | 0.005985 | 0.18594 | 0.092248 | 0.047508 | 0.057384 | 0.072884 | 0.15425 | 0.051729 | 122.193 | 122.1596 | 122.0802 | 122.0027 | 0.034497 | 0.082731 | 0.012293 | 0.047184 | 122.1585 | 122.1807 | 122.0457 | 122.0679
2384.375 | 122.2733 | -0.10529 | 122.1634 | 0.11727 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.09474 | -0.012357 | 122.161 | 122.1139 | 122.0436 | 121.966 | -0.011281 | 0.036954 | -0.024328 | 0.010563 | 0.22256 | 0.13345 | 0.088708 | 0.094005 | 0.11866 | 0.20003 | 0.092929 | 122.2022 | 122.1551 | 122.0848 | 122.0072 | 0.029918 | 0.078153 | 0.016871 | 0.051762 | 122.1722 | 122.1853 | 122.0549 | 122.0679
2386.0938 | 122.3557 | -0.064087 | 122.1176 | 0.11269 | 0.023583 | -0.016578 | -0.020438 | 0.013375 | 0.090161 | -0.012357 | 122.1564 | 122.1184 | 122.039 | 121.966 | -0.002124 | 0.027798 | -0.019749 | 0.015141 | 0.17678 | 0.08767 | 0.047509 | 0.043649 | 0.077462 | 0.15425 | 0.05173 | 122.1976 | 122.1596 | 122.0802 | 122.0072 | 0.039075 | 0.068997 | 0.02145 | 0.05634 | 122.1585 | 122.1761 | 122.0411 | 122.0588
2387.8438 | 122.2504 | -0.11902 | 122.1542 | 0.11727 | 0.028162 | -0.016578 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.161 | 122.1093 | 122.0482 | 121.966 | -0.002124 | 0.041532 | -0.024328 | 0.010563 | 0.23629 | 0.14718 | 0.10244 | 0.11232 | 0.13239 | 0.20918 | 0.10666 | 122.2022 | 122.1505 | 122.0894 | 122.0072 | 0.039075 | 0.082731 | 0.016871 | 0.051762 | 122.1631 | 122.1853 | 122.0503 | 122.0725
2389.5938 | 122.2458 | -0.12817 | 122.1542 | 0.10812 | 0.019004 | -0.021157 | -0.006703 | 0.013375 | 0.09474 | -0.016936 | 122.161 | 122.1184 | 122.0436 | 121.9615 | -0.011281 | 0.041532 | -0.024328 | 0.010563 | 0.23629 | 0.14718 | 0.10702 | 0.12147 | 0.14155 | 0.22291 | 0.11124 | 122.2022 | 122.1596 | 122.0848 | 122.0027 | 0.029918 | 0.082731 | 0.016871 | 0.051762 | 122.1722 | 122.1853 | 122.0549 | 122.0679
2391.2812 | 122.2366 | -0.10071 | 122.1771 | 0.10812 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.090161 | -0.012357 | 122.1655 | 122.123 | 122.0436 | 121.966 | -0.002124 | 0.036954 | -0.028906 | 0.010563 | 0.20882 | 0.12429 | 0.08413 | 0.094005 | 0.10951 | 0.19087 | 0.088351 | 122.2067 | 122.1642 | 122.0848 | 122.0072 | 0.039075 | 0.078153 | 0.012293 | 0.051762 | 122.1677 | 122.1944 | 122.0457 | 122.0725
2393.0312 | 122.3648 | -0.059509 | 122.1039 | 0.11269 | 0.019004 | -0.016578 | -0.01586 | 0.013375 | 0.081005 | -0.021514 | 122.161 | 122.1276 | 122.0527 | 121.9706 | -0.011281 | 0.041532 | -0.028906 | -0.003172 | 0.1722 | 0.078513 | 0.042931 | 0.043649 | 0.072884 | 0.14051 | 0.037995 | 122.2022 | 122.1688 | 122.0939 | 122.0118 | 0.029918 | 0.082731 | 0.012293 | 0.038027 | 122.1722 | 122.1899 | 122.064 | 122.0816
2394.7812 | 122.2961 | -0.07782 | 122.1497 | 0.11269 | 0.023583 | -0.021157 | -0.006703 | 0.022531 | 0.081005 | -0.012357 | 122.161 | 122.123 | 122.039 | 121.966 | -0.006702 | 0.036954 | -0.028906 | 0.005985 | 0.19051 | 0.1014 | 0.056663 | 0.071117 | 0.10035 | 0.15882 | 0.065463 | 122.2022 | 122.1642 | 122.0802 | 122.0072 | 0.034497 | 0.078153 | 0.012293 | 0.047184 | 122.1677 | 122.1899 | 122.0457 | 122.0679
2396.4688 | 122.3831 | -0.054932 | 122.1039 | 0.10812 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.021514 | 122.161 | 122.1184 | 122.0436 | 121.966 | -0.002124 | 0.036954 | -0.019749 | 0.010563 | 0.16305 | 0.073936 | 0.029197 | 0.039072 | 0.063729 | 0.14509 | 0.033418 | 122.2022 | 122.1596 | 122.0848 | 122.0072 | 0.039075 | 0.078153 | 0.02145 | 0.051762 | 122.1631 | 122.1807 | 122.0457 | 122.0633
2398.2188 | 122.2504 | -0.1236 | 122.1588 | 0.10812 | 0.014425 | -0.025735 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.1655 | 122.1184 | 122.0436 | 121.9706 | -0.011281 | 0.036954 | -0.028906 | 0.010563 | 0.23171 | 0.13802 | 0.097861 | 0.11689 | 0.13697 | 0.21376 | 0.11124 | 122.2067 | 122.1596 | 122.0848 | 122.0118 | 0.029918 | 0.078153 | 0.012293 | 0.051762 | 122.1768 | 122.1944 | 122.0549 | 122.0725
2399.9688 | 122.3831 | -0.059509 | 122.1222 | 0.11269 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.081005 | -0.016936 | 122.1701 | 122.1184 | 122.0482 | 121.9706 | -0.011281 | 0.036954 | -0.024328 | 0.010563 | 0.1722 | 0.078513 | 0.033774 | 0.043649 | 0.068306 | 0.14051 | 0.042573 | 122.2113 | 122.1596 | 122.0894 | 122.0118 | 0.029918 | 0.078153 | 0.016871 | 0.051762 | 122.1814 | 122.1944 | 122.0594 | 122.0725
2401.7188 | 122.3282 | -0.068665 | 122.1497 | 0.11727 | 0.014425 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.026092 | 122.1655 | 122.1184 | 122.0527 | 121.9798 | -0.002124 | 0.032376 | -0.019749 | 0.005985 | 0.18594 | 0.08309 | 0.047508 | 0.052805 | 0.077462 | 0.15425 | 0.042573 | 122.2067 | 122.1596 | 122.0939 | 122.021 | 0.039075 | 0.073575 | 0.02145 | 0.047184 | 122.1677 | 122.1853 | 122.0549 | 122.0725
2403.4219 | 122.3465 | -0.068665 | 122.1268 | 0.10812 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.076426 | -0.012357 | 122.1655 | 122.123 | 122.0527 | 121.966 | -0.006702 | 0.036954 | -0.019749 | 0.010563 | 0.17678 | 0.092248 | 0.047508 | 0.052805 | 0.077462 | 0.14509 | 0.056308 | 122.2067 | 122.1642 | 122.0939 | 122.0072 | 0.034497 | 0.078153 | 0.02145 | 0.051762 | 122.1722 | 122.1853 | 122.0594 | 122.0725
2405.1719 | 122.2733 | -0.09613 | 122.1405 | 0.11269 | 0.019004 | -0.025735 | 0.002454 | 0.017953 | 0.090161 | -0.016936 | 122.161 | 122.1276 | 122.0527 | 121.9706 | -0.002124 | 0.032376 | -0.024328 | 0.010563 | 0.20882 | 0.11513 | 0.070395 | 0.098584 | 0.11408 | 0.18629 | 0.079194 | 122.2022 | 122.1688 | 122.0939 | 122.0118 | 0.039075 | 0.073575 | 0.016871 | 0.051762 | 122.1631 | 122.1853 | 122.0549 | 122.0771
2406.875 | 122.3877 | -0.054932 | 122.1268 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 122.161 | 122.123 | 122.0482 | 121.9706 | -0.002124 | 0.036954 | -0.028906 | 0.010563 | 0.16763 | 0.078515 | 0.033775 | 0.039072 | 0.063729 | 0.14052 | 0.033418 | 122.2022 | 122.1642 | 122.0894 | 122.0118 | 0.039075 | 0.078153 | 0.012293 | 0.051762 | 122.1631 | 122.1899 | 122.0503 | 122.0771
2408.625 | 122.3694 | -0.054932 | 122.1405 | 0.11727 | 0.023583 | -0.021157 | -0.011281 | 0.017953 | 0.081005 | -0.012357 | 122.1701 | 122.123 | 122.0573 | 121.9752 | -0.006702 | 0.036954 | -0.024328 | 0.005985 | 0.1722 | 0.078515 | 0.033775 | 0.043651 | 0.072885 | 0.13594 | 0.042575 | 122.2113 | 122.1642 | 122.0985 | 122.0164 | 0.034497 | 0.078153 | 0.016871 | 0.047184 | 122.1768 | 122.1944 | 122.064 | 122.0816
2410.3125 | 122.2366 | -0.1236 | 122.1588 | 0.10812 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.1655 | 122.123 | 122.0573 | 121.9798 | -0.011281 | 0.036954 | -0.024328 | 0.005985 | 0.23171 | 0.1426 | 0.10702 | 0.11231 | 0.12781 | 0.20918 | 0.11124 | 122.2067 | 122.1642 | 122.0985 | 122.021 | 0.029918 | 0.078153 | 0.016871 | 0.047184 | 122.1768 | 122.1899 | 122.0686 | 122.0816
2412.0156 | 122.3282 | -0.073242 | 122.1313 | 0.10354 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.1701 | 122.1276 | 122.0527 | 121.966 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.17678 | 0.087667 | 0.052085 | 0.061961 | 0.082039 | 0.15425 | 0.051728 | 122.2113 | 122.1688 | 122.0939 | 122.0072 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.1814 | 122.2036 | 122.064 | 122.0862
2413.7812 | 122.2916 | -0.09613 | 122.1771 | 0.10812 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.012357 | 122.1701 | 122.1322 | 122.0527 | 121.9752 | -0.011281 | 0.04611 | -0.028906 | 0.005985 | 0.20425 | 0.11513 | 0.074973 | 0.08027 | 0.10493 | 0.18171 | 0.083773 | 122.2113 | 122.1734 | 122.0939 | 122.0164 | 0.029918 | 0.087309 | 0.012293 | 0.047184 | 122.1814 | 122.199 | 122.064 | 122.0816
2415.5625 | 122.3648 | -0.059509 | 122.1542 | 0.10812 | 0.019004 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.021514 | 122.1747 | 122.1276 | 122.0573 | 121.9752 | -0.006702 | 0.032376 | -0.024328 | 0.010563 | 0.16762 | 0.078513 | 0.042931 | 0.048228 | 0.072884 | 0.14509 | 0.037995 | 122.2159 | 122.1688 | 122.0985 | 122.0164 | 0.034497 | 0.073575 | 0.016871 | 0.051762 | 122.1814 | 122.199 | 122.064 | 122.0816
2417.25 | 122.3511 | -0.064087 | 122.1451 | 0.11269 | 0.014425 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.016936 | 122.1793 | 122.1322 | 122.0527 | 121.9798 | -0.002124 | 0.036954 | -0.028906 | 0.005985 | 0.17678 | 0.078512 | 0.047509 | 0.048227 | 0.072884 | 0.15425 | 0.047151 | 122.2205 | 122.1734 | 122.0939 | 122.021 | 0.039075 | 0.078153 | 0.012293 | 0.047184 | 122.1814 | 122.2082 | 122.0549 | 122.0816
2419 | 122.2504 | -0.091553 | 122.1588 | 0.11727 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.09474 | -0.012357 | 122.1747 | 122.1276 | 122.0573 | 121.9752 | -0.011281 | 0.032376 | -0.024328 | 0.005985 | 0.20883 | 0.11514 | 0.074975 | 0.080272 | 0.10493 | 0.18629 | 0.079196 | 122.2159 | 122.1688 | 122.0985 | 122.0164 | 0.029918 | 0.073575 | 0.016871 | 0.047184 | 122.186 | 122.199 | 122.0686 | 122.0816
2420.6875 | 122.3511 | -0.073242 | 122.1222 | 0.10812 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.1747 | 122.1276 | 122.0573 | 121.9706 | -0.006702 | 0.036954 | -0.015171 | 0.015141 | 0.18136 | 0.096825 | 0.052085 | 0.061961 | 0.082039 | 0.15425 | 0.056306 | 122.2159 | 122.1688 | 122.0985 | 122.0118 | 0.034497 | 0.078153 | 0.026028 | 0.05634 | 122.1814 | 122.1899 | 122.064 | 122.0725
2422.4219 | 122.287 | -0.086975 | 122.1863 | 0.11727 | 0.023583 | -0.021157 | -0.002124 | 0.013375 | 0.085583 | -0.021514 | 122.1655 | 122.1322 | 122.0573 | 121.9798 | -0.011281 | 0.027798 | -0.019749 | 0.015141 | 0.20425 | 0.11056 | 0.065818 | 0.084851 | 0.10035 | 0.17256 | 0.065461 | 122.2067 | 122.1734 | 122.0985 | 122.021 | 0.029918 | 0.068997 | 0.02145 | 0.05634 | 122.1768 | 122.1853 | 122.0686 | 122.0771
2424.1719 | 122.3557 | -0.059509 | 122.1313 | 0.11269 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.076426 | -0.016936 | 122.1747 | 122.1276 | 122.0573 | 121.9798 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.1722 | 0.078513 | 0.033774 | 0.043649 | 0.068306 | 0.13594 | 0.042573 | 122.2159 | 122.1688 | 122.0985 | 122.021 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.1814 | 122.2036 | 122.064 | 122.0862
2425.9375 | 122.2733 | -0.09613 | 122.1771 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.012357 | 122.1793 | 122.1276 | 122.0665 | 121.9798 | -0.011281 | 0.036954 | -0.028906 | 0.010563 | 0.20882 | 0.11513 | 0.074973 | 0.084849 | 0.1095 | 0.18171 | 0.083773 | 122.2205 | 122.1688 | 122.1077 | 122.021 | 0.029918 | 0.078153 | 0.012293 | 0.051762 | 122.1905 | 122.2082 | 122.0778 | 122.0954
2427.6875 | 122.3923 | -0.082397 | 122.1085 | 0.10812 | 0.014425 | -0.021157 | -0.01586 | 0.013375 | 0.081005 | -0.016936 | 122.1793 | 122.1276 | 122.0573 | 121.9706 | -0.002124 | 0.032376 | -0.019749 | 0.005985 | 0.19051 | 0.096822 | 0.06124 | 0.066537 | 0.095772 | 0.1634 | 0.065461 | 122.2205 | 122.1688 | 122.0985 | 122.0118 | 0.039075 | 0.073575 | 0.02145 | 0.047184 | 122.1814 | 122.199 | 122.0594 | 122.0771
2429.375 | 122.3877 | -0.054932 | 122.1268 | 0.10812 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.021514 | 122.1793 | 122.1322 | 122.0619 | 121.9844 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.16305 | 0.069357 | 0.033775 | 0.043651 | 0.063729 | 0.14509 | 0.033418 | 122.2205 | 122.1734 | 122.1031 | 122.0256 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.186 | 122.2082 | 122.0686 | 122.0908
2431.1406 | 122.3007 | -0.073242 | 122.1497 | 0.10812 | 0.014425 | -0.025735 | -0.011281 | 0.008797 | 0.090161 | -0.021514 | 122.1838 | 122.1367 | 122.0573 | 121.9798 | -0.002124 | 0.036954 | -0.028906 | 0.001406 | 0.18136 | 0.087667 | 0.047507 | 0.061961 | 0.082039 | 0.1634 | 0.051728 | 122.225 | 122.1779 | 122.0985 | 122.021 | 0.039075 | 0.078153 | 0.012293 | 0.042605 | 122.186 | 122.2128 | 122.0594 | 122.0862
2432.875 | 122.2687 | -0.11444 | 122.1863 | 0.12185 | 0.019004 | -0.021157 | -0.006703 | 0.013375 | 0.081005 | -0.016936 | 122.1793 | 122.1322 | 122.0619 | 121.9889 | -0.015859 | 0.036954 | -0.019749 | 0.010563 | 0.23629 | 0.13345 | 0.093284 | 0.10774 | 0.12782 | 0.19545 | 0.097505 | 122.2205 | 122.1734 | 122.1031 | 122.0301 | 0.02534 | 0.078153 | 0.02145 | 0.051762 | 122.1951 | 122.199 | 122.0778 | 122.0816
2434.625 | 122.2595 | -0.10986 | 122.168 | 0.11269 | 0.023583 | -0.021157 | -0.002124 | 0.017953 | 0.09474 | -0.012357 | 122.1838 | 122.1322 | 122.0619 | 121.9798 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.22256 | 0.13345 | 0.088706 | 0.10774 | 0.12782 | 0.2046 | 0.097506 | 122.225 | 122.1734 | 122.1031 | 122.021 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.1997 | 122.2128 | 122.0778 | 122.0908
2436.375 | 122.2824 | -0.10529 | 122.1634 | 0.11269 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.007779 | 122.1793 | 122.1413 | 122.0665 | 121.9798 | -0.006702 | 0.02322 | -0.024328 | 0.005985 | 0.21798 | 0.12887 | 0.084129 | 0.089426 | 0.11408 | 0.19087 | 0.097507 | 122.2205 | 122.1825 | 122.1077 | 122.021 | 0.034497 | 0.064419 | 0.016871 | 0.047184 | 122.186 | 122.2036 | 122.0732 | 122.0908
2438.125 | 122.2595 | -0.10529 | 122.1634 | 0.11727 | 0.014425 | -0.012 | -0.006703 | 0.017953 | 0.085583 | -0.012357 | 122.1793 | 122.1413 | 122.0619 | 121.9798 | -0.011281 | 0.036954 | -0.024328 | 0.005985 | 0.22256 | 0.11971 | 0.093286 | 0.098583 | 0.12324 | 0.19087 | 0.092929 | 122.2205 | 122.1825 | 122.1031 | 122.021 | 0.029918 | 0.078153 | 0.016871 | 0.047184 | 122.1905 | 122.2036 | 122.0732 | 122.0862
2439.8125 | 122.3923 | -0.050354 | 122.1497 | 0.11727 | 0.014425 | -0.025735 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.1793 | 122.1367 | 122.0619 | 121.9798 | -0.006702 | 0.027798 | -0.028906 | 0.010563 | 0.16763 | 0.064779 | 0.024619 | 0.039073 | 0.059151 | 0.13594 | 0.033418 | 122.2205 | 122.1779 | 122.1031 | 122.021 | 0.034497 | 0.068997 | 0.012293 | 0.051762 | 122.186 | 122.2082 | 122.0686 | 122.0908
2441.5781 | 122.3007 | -0.10071 | 122.2046 | 0.11269 | 0.014425 | -0.025735 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.1838 | 122.1367 | 122.0665 | 121.9844 | -0.015859 | 0.032376 | -0.024328 | 0.005985 | 0.2134 | 0.11513 | 0.074973 | 0.089427 | 0.10951 | 0.18171 | 0.079194 | 122.225 | 122.1779 | 122.1077 | 122.0256 | 0.02534 | 0.073575 | 0.016871 | 0.047184 | 122.1997 | 122.2082 | 122.0823 | 122.0908
2443.2656 | 122.406 | -0.068665 | 122.1313 | 0.11269 | 0.014425 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.021514 | 122.1884 | 122.1413 | 122.0711 | 121.9798 | -0.011281 | 0.036954 | -0.024328 | 0.005985 | 0.18136 | 0.08309 | 0.04293 | 0.052805 | 0.077462 | 0.15883 | 0.047151 | 122.2296 | 122.1825 | 122.1123 | 122.021 | 0.029918 | 0.078153 | 0.016871 | 0.047184 | 122.1997 | 122.2128 | 122.0823 | 122.0954
2445.0156 | 122.3007 | -0.082397 | 122.1817 | 0.11269 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.012357 | 122.1793 | 122.1413 | 122.0711 | 121.9844 | -0.006702 | 0.027798 | -0.024328 | 0.010563 | 0.19509 | 0.1014 | 0.065819 | 0.075694 | 0.095772 | 0.1634 | 0.07004 | 122.2205 | 122.1825 | 122.1123 | 122.0256 | 0.034497 | 0.068997 | 0.016871 | 0.051762 | 122.186 | 122.2036 | 122.0778 | 122.0954
2446.7812 | 122.3053 | -0.09613 | 122.1634 | 0.11269 | 0.019004 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.012357 | 122.1884 | 122.1413 | 122.0665 | 121.9889 | -0.006702 | 0.032376 | -0.024328 | 0.005985 | 0.20882 | 0.11513 | 0.079552 | 0.08027 | 0.10493 | 0.18629 | 0.083773 | 122.2296 | 122.1825 | 122.1077 | 122.0301 | 0.034497 | 0.073575 | 0.016871 | 0.047184 | 122.1951 | 122.2128 | 122.0732 | 122.0908
2448.4844 | 122.3419 | -0.086975 | 122.1725 | 0.11727 | 0.019004 | -0.007421 | -0.01586 | 0.017953 | 0.090161 | -0.012357 | 122.1793 | 122.1367 | 122.0711 | 121.9844 | -0.006702 | 0.032376 | -0.019749 | 0.005985 | 0.20425 | 0.10598 | 0.079554 | 0.071115 | 0.10493 | 0.17714 | 0.074618 | 122.2205 | 122.1779 | 122.1123 | 122.0256 | 0.034497 | 0.073575 | 0.02145 | 0.047184 | 122.186 | 122.199 | 122.0778 | 122.0908
2450.2344 | 122.3236 | -0.082397 | 122.1451 | 0.11727 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.1838 | 122.1367 | 122.0711 | 121.9844 | -0.006702 | 0.027798 | -0.019749 | 0.005985 | 0.19967 | 0.096822 | 0.065819 | 0.071116 | 0.091194 | 0.1634 | 0.060883 | 122.225 | 122.1779 | 122.1123 | 122.0256 | 0.034497 | 0.068997 | 0.02145 | 0.047184 | 122.1905 | 122.2036 | 122.0778 | 122.0908
2451.9844 | 122.3053 | -0.091553 | 122.1771 | 0.11727 | 0.028162 | -0.016578 | -0.01586 | 0.013375 | 0.090161 | -0.016936 | 122.193 | 122.1367 | 122.0665 | 121.9981 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.20883 | 0.11971 | 0.074975 | 0.075693 | 0.10493 | 0.18171 | 0.074617 | 122.2342 | 122.1779 | 122.1077 | 122.0393 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.2089 | 122.2219 | 122.0823 | 122.0954
2453.7344 | 122.4014 | -0.059509 | 122.1359 | 0.11727 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.016936 | 122.1838 | 122.1413 | 122.0711 | 121.9889 | -0.006702 | 0.032376 | -0.024328 | 0.005985 | 0.17678 | 0.078513 | 0.038352 | 0.048228 | 0.072884 | 0.14509 | 0.042573 | 122.225 | 122.1825 | 122.1123 | 122.0301 | 0.034497 | 0.073575 | 0.016871 | 0.047184 | 122.1905 | 122.2082 | 122.0778 | 122.0954
2455.4219 | 122.3557 | -0.07782 | 122.1359 | 0.10812 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.081005 | -0.021514 | 122.1884 | 122.1322 | 122.0665 | 121.9844 | -0.011281 | 0.041532 | -0.024328 | 0.005985 | 0.18594 | 0.096824 | 0.056663 | 0.066539 | 0.091195 | 0.15882 | 0.056306 | 122.2296 | 122.1734 | 122.1077 | 122.0256 | 0.029918 | 0.082731 | 0.016871 | 0.047184 | 122.1997 | 122.2128 | 122.0778 | 122.0908
2457.1875 | 122.2504 | -0.10071 | 122.1863 | 0.11269 | 0.019004 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.012357 | 122.1884 | 122.1413 | 122.0711 | 121.9844 | -0.006702 | 0.036954 | -0.024328 | 0.010563 | 0.2134 | 0.11971 | 0.088708 | 0.098584 | 0.11408 | 0.18629 | 0.088351 | 122.2296 | 122.1825 | 122.1123 | 122.0256 | 0.034497 | 0.078153 | 0.016871 | 0.051762 | 122.1951 | 122.2128 | 122.0778 | 122.0954
2458.9375 | 122.2778 | -0.10986 | 122.2046 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.193 | 122.1367 | 122.0756 | 121.9889 | -0.011281 | 0.027798 | -0.019749 | -0.003172 | 0.22256 | 0.12887 | 0.088706 | 0.098582 | 0.11866 | 0.19545 | 0.092927 | 122.2342 | 122.1779 | 122.1168 | 122.0301 | 0.029918 | 0.068997 | 0.02145 | 0.038027 | 122.2043 | 122.2128 | 122.0869 | 122.0954
2460.7031 | 122.2504 | -0.1236 | 122.1542 | 0.11269 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.012357 | 122.193 | 122.1413 | 122.0665 | 121.9889 | -0.015859 | 0.036954 | -0.024328 | 0.001406 | 0.23629 | 0.1426 | 0.10244 | 0.11231 | 0.13697 | 0.20918 | 0.11124 | 122.2342 | 122.1825 | 122.1077 | 122.0301 | 0.02534 | 0.078153 | 0.016871 | 0.042605 | 122.2089 | 122.2173 | 122.0823 | 122.0908
2462.4219 | 122.2687 | -0.10986 | 122.1863 | 0.10812 | 0.014425 | -0.021157 | -0.020438 | 0.008797 | 0.085583 | -0.016936 | 122.1884 | 122.1459 | 122.0802 | 121.9844 | -0.011281 | 0.018642 | -0.028906 | 0.010563 | 0.21798 | 0.12429 | 0.088706 | 0.089425 | 0.11866 | 0.19545 | 0.092927 | 122.2296 | 122.1871 | 122.1214 | 122.0256 | 0.029918 | 0.059841 | 0.012293 | 0.051762 | 122.1997 | 122.2173 | 122.0915 | 122.1091
2464.1719 | 122.406 | -0.054932 | 122.1863 | 0.10812 | 0.014425 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.012357 | 122.193 | 122.1413 | 122.0802 | 121.9981 | -0.015859 | 0.027798 | -0.024328 | 0.010563 | 0.16305 | 0.069357 | 0.033775 | 0.039072 | 0.059151 | 0.14509 | 0.042575 | 122.2342 | 122.1825 | 122.1214 | 122.0393 | 0.02534 | 0.068997 | 0.016871 | 0.051762 | 122.2089 | 122.2173 | 122.0961 | 122.1045
2465.875 | 122.2458 | -0.10986 | 122.1771 | 0.11269 | 0.019004 | -0.016578 | -0.01586 | 0.013375 | 0.090161 | -0.012357 | 122.1884 | 122.1413 | 122.0802 | 121.9889 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.22256 | 0.12887 | 0.093285 | 0.094003 | 0.12324 | 0.20002 | 0.097506 | 122.2296 | 122.1825 | 122.1214 | 122.0301 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.1951 | 122.2173 | 122.0869 | 122.1091
2467.6406 | 122.2824 | -0.086975 | 122.1909 | 0.11727 | 0.019004 | -0.025735 | -0.006703 | 0.013375 | 0.090161 | -0.016936 | 122.193 | 122.1367 | 122.0756 | 121.9889 | -0.006702 | 0.036954 | -0.028906 | 0.005985 | 0.20425 | 0.10598 | 0.06124 | 0.080272 | 0.10035 | 0.17714 | 0.070039 | 122.2342 | 122.1779 | 122.1168 | 122.0301 | 0.034497 | 0.078153 | 0.012293 | 0.047184 | 122.1997 | 122.2219 | 122.0823 | 122.1045
2469.3281 | 122.2458 | -0.10529 | 122.1725 | 0.11269 | 0.019004 | -0.016578 | -0.006703 | 0.017953 | 0.085583 | -0.012357 | 122.1976 | 122.1505 | 122.0756 | 121.9935 | -0.011281 | 0.027798 | -0.024328 | 0.001406 | 0.21798 | 0.12429 | 0.088708 | 0.098583 | 0.12324 | 0.19087 | 0.092929 | 122.2388 | 122.1917 | 122.1168 | 122.0347 | 0.029918 | 0.068997 | 0.016871 | 0.042605 | 122.2089 | 122.2219 | 122.0869 | 122.1
2471.0938 | 122.3419 | -0.059509 | 122.1405 | 0.10812 | 0.009846 | -0.025735 | -0.01586 | 0.013375 | 0.085583 | -0.021514 | 122.193 | 122.1459 | 122.0756 | 121.9889 | -0.015859 | 0.036954 | -0.024328 | 0.010563 | 0.16762 | 0.069355 | 0.033774 | 0.043649 | 0.072884 | 0.14509 | 0.037995 | 122.2342 | 122.1871 | 122.1168 | 122.0301 | 0.02534 | 0.078153 | 0.016871 | 0.051762 | 122.2089 | 122.2173 | 122.0915 | 122.1
2472.8594 | 122.2916 | -0.11902 | 122.1863 | 0.10812 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.193 | 122.1413 | 122.0711 | 121.9844 | -0.011281 | 0.032376 | -0.019749 | -0.003172 | 0.22714 | 0.13344 | 0.097862 | 0.10774 | 0.12782 | 0.2046 | 0.10208 | 122.2342 | 122.1825 | 122.1123 | 122.0256 | 0.029918 | 0.073575 | 0.02145 | 0.038027 | 122.2043 | 122.2128 | 122.0823 | 122.0908
2474.5469 | 122.2824 | -0.11902 | 122.2046 | 0.10812 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.081005 | -0.012357 | 122.1884 | 122.1459 | 122.0848 | 121.9889 | -0.002124 | 0.027798 | -0.033484 | 0.010563 | 0.22714 | 0.13802 | 0.10244 | 0.11232 | 0.13239 | 0.20002 | 0.10666 | 122.2296 | 122.1871 | 122.126 | 122.0301 | 0.039075 | 0.068997 | 0.007715 | 0.051762 | 122.1905 | 122.2219 | 122.0869 | 122.1183
2476.2969 | 122.2916 | -0.091553 | 122.1725 | 0.11269 | 0.014425 | -0.012 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.193 | 122.1459 | 122.0802 | 121.9935 | -0.011281 | 0.04611 | -0.024328 | 0.005985 | 0.20425 | 0.10598 | 0.079553 | 0.080272 | 0.10035 | 0.18171 | 0.074617 | 122.2342 | 122.1871 | 122.1214 | 122.0347 | 0.029918 | 0.087309 | 0.016871 | 0.047184 | 122.2043 | 122.2173 | 122.0915 | 122.1045
2478.0625 | 122.2641 | -0.1236 | 122.1634 | 0.10812 | 0.019004 | -0.021157 | -0.01586 | 0.013375 | 0.090161 | -0.016936 | 122.1884 | 122.1505 | 122.0665 | 121.9889 | -0.002124 | 0.027798 | -0.033484 | 0.005985 | 0.23171 | 0.1426 | 0.10244 | 0.10774 | 0.13697 | 0.21376 | 0.10666 | 122.2296 | 122.1917 | 122.1077 | 122.0301 | 0.039075 | 0.068997 | 0.007715 | 0.047184 | 122.1905 | 122.2219 | 122.0686 | 122.1
2479.8281 | 122.3511 | -0.07782 | 122.168 | 0.10812 | 0.014425 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.026092 | 122.1884 | 122.1413 | 122.0756 | 121.9889 | -0.011281 | 0.032376 | -0.028906 | 0.010563 | 0.18594 | 0.092245 | 0.052085 | 0.06196 | 0.077461 | 0.1634 | 0.051728 | 122.2296 | 122.1825 | 122.1168 | 122.0301 | 0.029918 | 0.073575 | 0.012293 | 0.051762 | 122.1997 | 122.2173 | 122.0869 | 122.1045
2481.5938 | 123.8342 | -0.09613 | 122.1542 | 2.1455 | 0.15179 | 0.32682 | 0.28632 | 0.26059 | 1.0013 | -0.003201 | 122.1793 | 122.1367 | 122.0665 | 121.9935 | -0.011281 | 0.041532 | -0.019749 | 0.005985 | 2.2416 | 0.24792 | 0.42295 | 0.38245 | 0.35672 | 1.0974 | 0.092929 | 122.2205 | 122.1779 | 122.1077 | 122.0347 | 0.029918 | 0.082731 | 0.02145 | 0.047184 | 122.1905 | 122.199 | 122.0778 | 122.0862
2483.2969 | 122.4976 | -0.091553 | 122.1634 | 0.41487 | 0.096844 | 0.061258 | 0.19475 | 0.12782 | 0.1039 | 0.005955 | 122.193 | 122.1505 | 122.0802 | 122.0073 | -0.006702 | 0.032376 | -0.028906 | 0.010563 | 0.50642 | 0.1884 | 0.15281 | 0.2863 | 0.21938 | 0.19545 | 0.097508 | 122.2342 | 122.1917 | 122.1214 | 122.0485 | 0.034497 | 0.073575 | 0.012293 | 0.051762 | 122.1997 | 122.2219 | 122.0869 | 122.1091
2485.0469 | 122.5525 | -0.068665 | 122.1588 | 0.218 | 0.10142 | 0.10247 | 0.23596 | 0.2789 | 0.49764 | 0.028846 | 122.1976 | 122.1459 | 122.0711 | 121.9889 | -0.015859 | 0.032376 | -0.019749 | 0.005985 | 0.28666 | 0.17009 | 0.17113 | 0.30462 | 0.34756 | 0.5663 | 0.097511 | 122.2388 | 122.1871 | 122.1123 | 122.0301 | 0.02534 | 0.073575 | 0.02145 | 0.047184 | 122.2134 | 122.2173 | 122.0869 | 122.0908
2486.8125 | 122.4792 | -0.054932 | 122.1542 | 0.25005 | 0.096844 | -0.057786 | 0.26801 | 0.082044 | 0.13595 | -0.007779 | 122.1884 | 122.1459 | 122.0756 | 121.9935 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.30498 | 0.15178 | -0.002854 | 0.32294 | 0.13698 | 0.19088 | 0.047153 | 122.2296 | 122.1871 | 122.1168 | 122.0347 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.1951 | 122.2219 | 122.0823 | 122.1091
2488.5 | 122.3557 | -0.09613 | 122.1863 | 0.24089 | 0.060213 | 0.006315 | 0.071132 | 0.027109 | 0.10848 | -0.007779 | 122.1976 | 122.1505 | 122.0848 | 121.9981 | -0.015859 | 0.036954 | -0.024328 | 0.005985 | 0.33702 | 0.15634 | 0.10244 | 0.16726 | 0.12324 | 0.2046 | 0.088351 | 122.2388 | 122.1917 | 122.126 | 122.0393 | 0.02534 | 0.078153 | 0.016871 | 0.047184 | 122.2134 | 122.2219 | 122.1006 | 122.1091
2490.25 | 122.4014 | -0.068665 | 122.1634 | 0.094381 | 0.023583 | -0.007421 | -0.006703 | 0.008797 | 0.1039 | -0.021514 | 122.1976 | 122.1551 | 122.0802 | 122.0027 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.16305 | 0.092248 | 0.061244 | 0.061962 | 0.077462 | 0.17256 | 0.047151 | 122.2388 | 122.1963 | 122.1214 | 122.0439 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.2043 | 122.2265 | 122.0869 | 122.1091
2492.0156 | 122.3511 | -0.091553 | 122.1497 | 0.14474 | 0.023583 | -0.016578 | 0.01619 | 0.008797 | 0.1039 | -0.012357 | 122.2022 | 122.1459 | 122.0848 | 121.9889 | -0.006702 | 0.027798 | -0.028906 | 0.010563 | 0.2363 | 0.11514 | 0.074975 | 0.10774 | 0.10035 | 0.19545 | 0.079196 | 122.2434 | 122.1871 | 122.126 | 122.0301 | 0.034497 | 0.068997 | 0.012293 | 0.051762 | 122.2089 | 122.2311 | 122.0915 | 122.1137
2493.7031 | 122.374 | -0.07782 | 122.1634 | 0.13559 | 0.014425 | -0.016578 | 0.011611 | -0.000359 | 0.090161 | 0.001377 | 122.1976 | 122.1505 | 122.0802 | 121.9935 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.21341 | 0.092245 | 0.061242 | 0.089431 | 0.077461 | 0.16798 | 0.079197 | 122.2388 | 122.1917 | 122.1214 | 122.0347 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2089 | 122.2265 | 122.0915 | 122.1091
2495.4375 | 122.3923 | -0.09613 | 122.1954 | 0.13559 | 0.03274 | 0.001736 | -0.002124 | -0.000359 | 0.13137 | -0.012357 | 122.1976 | 122.1596 | 122.0848 | 122.0027 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.23172 | 0.12887 | 0.097866 | 0.094006 | 0.095771 | 0.2275 | 0.083773 | 122.2388 | 122.2008 | 122.126 | 122.0439 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.2089 | 122.2219 | 122.0961 | 122.1091
2497.1875 | 122.3373 | -0.10529 | 122.2 | 0.12643 | 0.028162 | 0.001736 | -0.002124 | 0.008797 | 0.11763 | -0.007779 | 122.2022 | 122.1459 | 122.0848 | 122.0027 | -0.011281 | 0.032376 | -0.024328 | 0.005985 | 0.23172 | 0.13345 | 0.10702 | 0.10316 | 0.11408 | 0.22292 | 0.097507 | 122.2434 | 122.1871 | 122.126 | 122.0439 | 0.029918 | 0.073575 | 0.016871 | 0.047184 | 122.2134 | 122.2265 | 122.0961 | 122.1091
2498.9375 | 122.4518 | -0.050354 | 122.168 | 0.12643 | 0.03274 | -0.016578 | -0.006703 | -0.000359 | 0.11305 | -0.012357 | 122.2022 | 122.1505 | 122.0848 | 122.0027 | -0.011281 | 0.032376 | -0.024328 | 0.005985 | 0.17678 | 0.083094 | 0.033776 | 0.043651 | 0.049995 | 0.16341 | 0.037997 | 122.2434 | 122.1917 | 122.126 | 122.0439 | 0.029918 | 0.073575 | 0.016871 | 0.047184 | 122.2134 | 122.2265 | 122.0961 | 122.1091
2500.6406 | 122.319 | -0.10071 | 122.2321 | 0.13101 | 0.037319 | -0.007421 | -0.011281 | 0.004219 | 0.11763 | -0.007779 | 122.1976 | 122.1551 | 122.0939 | 122.0073 | -0.020437 | 0.036954 | -0.028906 | 0.001406 | 0.23172 | 0.13803 | 0.093287 | 0.089427 | 0.10493 | 0.21834 | 0.092929 | 122.2388 | 122.1963 | 122.1351 | 122.0485 | 0.020762 | 0.078153 | 0.012293 | 0.042605 | 122.218 | 122.2265 | 122.1144 | 122.1228
2502.3906 | 122.3465 | -0.11444 | 122.1725 | 0.12185 | 0.023583 | 0.001736 | -0.006703 | 0.008797 | 0.11763 | -0.012357 | 122.2067 | 122.1505 | 122.0848 | 121.9981 | -0.011281 | 0.02322 | -0.028906 | 0.010563 | 0.23629 | 0.13802 | 0.11618 | 0.10774 | 0.12324 | 0.23207 | 0.10208 | 122.2479 | 122.1917 | 122.126 | 122.0393 | 0.029918 | 0.064419 | 0.012293 | 0.051762 | 122.218 | 122.2356 | 122.0961 | 122.1137
2504.1406 | 122.4243 | -0.073242 | 122.1634 | 0.12643 | 0.028162 | -0.002842 | -0.011281 | 0.004219 | 0.12221 | -0.012357 | 122.2022 | 122.1505 | 122.0894 | 121.9935 | -0.011281 | 0.027798 | -0.024328 | 0.010563 | 0.19967 | 0.1014 | 0.0704 | 0.061961 | 0.077461 | 0.19545 | 0.060885 | 122.2434 | 122.1917 | 122.1306 | 122.0347 | 0.029918 | 0.068997 | 0.016871 | 0.051762 | 122.2134 | 122.2265 | 122.1006 | 122.1137
2505.8906 | 122.3373 | -0.091553 | 122.1451 | 0.12185 | 0.03274 | -0.007421 | -0.011281 | 0.004219 | 0.10848 | -0.012357 | 122.2067 | 122.1551 | 122.0848 | 122.0118 | -0.006702 | 0.027798 | -0.028906 | 0.005985 | 0.2134 | 0.12429 | 0.084132 | 0.080272 | 0.095772 | 0.20003 | 0.079196 | 122.2479 | 122.1963 | 122.126 | 122.053 | 0.034497 | 0.068997 | 0.012293 | 0.047184 | 122.2134 | 122.2356 | 122.0915 | 122.1137
2507.6406 | 122.4014 | -0.073242 | 122.1451 | 0.11727 | 0.028162 | -0.012 | -0.011281 | -0.000359 | 0.099318 | -0.012357 | 122.2022 | 122.1551 | 122.0848 | 122.0073 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.19051 | 0.1014 | 0.061242 | 0.061961 | 0.072883 | 0.17256 | 0.060885 | 122.2434 | 122.1963 | 122.126 | 122.0485 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.2089 | 122.2311 | 122.0915 | 122.1137
2509.3906 | 122.4289 | -0.064087 | 122.1405 | 0.11727 | 0.028162 | -0.002842 | -0.011281 | 0.004219 | 0.099318 | -0.021514 | 122.1976 | 122.1551 | 122.0894 | 122.0073 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.18136 | 0.092249 | 0.061245 | 0.052806 | 0.068306 | 0.16341 | 0.042573 | 122.2388 | 122.1963 | 122.1306 | 122.0485 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.2134 | 122.2311 | 122.1052 | 122.1228
2511.0938 | 122.4289 | -0.054932 | 122.1268 | 0.11727 | 0.03274 | -0.007421 | -0.006703 | 0.008797 | 0.11305 | -0.012357 | 122.2067 | 122.1551 | 122.0848 | 122.0027 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.1722 | 0.087672 | 0.047511 | 0.048229 | 0.063729 | 0.16798 | 0.042575 | 122.2479 | 122.1963 | 122.126 | 122.0439 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.218 | 122.2402 | 122.0961 | 122.1183
2512.8594 | 122.4289 | -0.059509 | 122.1542 | 0.11269 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.1039 | -0.016936 | 122.2067 | 122.1551 | 122.0894 | 121.9981 | -0.006702 | 0.032376 | -0.042641 | 0.005985 | 0.1722 | 0.083092 | 0.042931 | 0.052806 | 0.068306 | 0.1634 | 0.042573 | 122.2479 | 122.1963 | 122.1306 | 122.0393 | 0.034497 | 0.073575 | -0.001442 | 0.047184 | 122.2134 | 122.2494 | 122.0961 | 122.132
2514.625 | 122.2778 | -0.10986 | 122.2092 | 0.11269 | 0.023583 | -0.021157 | 0.011611 | 0.008797 | 0.090161 | 0.005955 | 122.2067 | 122.1551 | 122.0894 | 122.0073 | -0.011281 | 0.036954 | -0.028906 | 0.010563 | 0.22256 | 0.13345 | 0.088706 | 0.12147 | 0.11866 | 0.20002 | 0.11582 | 122.2479 | 122.1963 | 122.1306 | 122.0485 | 0.029918 | 0.078153 | 0.012293 | 0.051762 | 122.218 | 122.2356 | 122.1006 | 122.1183
2516.3125 | 122.287 | -0.10986 | 122.2046 | 0.10812 | 0.023583 | -0.04405 | 0.043661 | 0.017953 | 0.1039 | 0.01969 | 122.2022 | 122.1551 | 122.0985 | 122.0073 | -0.015859 | 0.032376 | -0.028906 | 0.010563 | 0.21798 | 0.13345 | 0.065813 | 0.15352 | 0.12782 | 0.21376 | 0.12955 | 122.2434 | 122.1963 | 122.1397 | 122.0485 | 0.02534 | 0.073575 | 0.012293 | 0.051762 | 122.218 | 122.2311 | 122.1144 | 122.1274
2518.0625 | 122.319 | -0.082397 | 122.1634 | 0.10354 | 0.019004 | -0.030314 | 0.039082 | 0.022531 | 0.1039 | 0.015112 | 122.2113 | 122.1551 | 122.0894 | 122.0027 | -0.002124 | 0.036954 | -0.024328 | 0.005985 | 0.18593 | 0.1014 | 0.052083 | 0.12148 | 0.10493 | 0.18629 | 0.097509 | 122.2525 | 122.1963 | 122.1306 | 122.0439 | 0.039075 | 0.078153 | 0.016871 | 0.047184 | 122.2134 | 122.2356 | 122.0915 | 122.1137
2519.8125 | 122.3145 | -0.086975 | 122.1863 | 0.10354 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.09474 | -0.012357 | 122.2022 | 122.1596 | 122.0939 | 122.0073 | -0.011281 | 0.032376 | -0.024328 | 0.001406 | 0.19051 | 0.10598 | 0.065818 | 0.071115 | 0.095772 | 0.18172 | 0.074618 | 122.2434 | 122.2008 | 122.1351 | 122.0485 | 0.029918 | 0.073575 | 0.016871 | 0.042605 | 122.2134 | 122.2265 | 122.1052 | 122.1183
2521.5 | 122.3282 | -0.10529 | 122.1863 | 0.10354 | 0.014425 | -0.021157 | -0.006703 | -0.000359 | 0.090161 | -0.012357 | 122.2113 | 122.1596 | 122.0985 | 122.0073 | -0.011281 | 0.032376 | -0.028906 | 0.010563 | 0.20882 | 0.11971 | 0.084129 | 0.098583 | 0.10493 | 0.19545 | 0.092929 | 122.2525 | 122.2008 | 122.1397 | 122.0485 | 0.029918 | 0.073575 | 0.012293 | 0.051762 | 122.2226 | 122.2402 | 122.1098 | 122.1274
2523.2656 | 122.3053 | -0.11902 | 122.1771 | 0.094381 | 0.019004 | -0.016578 | -0.002124 | 0.004219 | 0.090161 | -0.012357 | 122.2022 | 122.1505 | 122.0985 | 122.0073 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.2134 | 0.13802 | 0.10244 | 0.11689 | 0.12324 | 0.20918 | 0.10666 | 122.2434 | 122.1917 | 122.1397 | 122.0485 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2134 | 122.2356 | 122.1098 | 122.132
2525.0312 | 122.3785 | -0.07782 | 122.1542 | 0.089802 | 0.009846 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.012357 | 122.2113 | 122.1642 | 122.0894 | 122.0073 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.16762 | 0.087666 | 0.052085 | 0.06196 | 0.082039 | 0.15882 | 0.065463 | 122.2525 | 122.2054 | 122.1306 | 122.0485 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.218 | 122.2402 | 122.0961 | 122.1183
2526.7812 | 122.3831 | -0.082397 | 122.1542 | 0.089802 | 0.014425 | -0.025735 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.2067 | 122.1642 | 122.0939 | 122.0073 | -0.006702 | 0.036954 | -0.019749 | 0.005985 | 0.1722 | 0.096822 | 0.056662 | 0.071116 | 0.091194 | 0.1634 | 0.060883 | 122.2479 | 122.2054 | 122.1351 | 122.0485 | 0.034497 | 0.078153 | 0.02145 | 0.047184 | 122.2134 | 122.2265 | 122.1006 | 122.1137
2528.4844 | 122.3145 | -0.10529 | 122.1863 | 0.098959 | 0.019004 | -0.007421 | -0.011281 | 0.004219 | 0.09474 | -0.016936 | 122.2067 | 122.1551 | 122.0894 | 122.0027 | -0.006702 | 0.036954 | -0.028906 | 0.005985 | 0.20425 | 0.12429 | 0.097865 | 0.094005 | 0.10951 | 0.20003 | 0.08835 | 122.2479 | 122.1963 | 122.1306 | 122.0439 | 0.034497 | 0.078153 | 0.012293 | 0.047184 | 122.2134 | 122.2356 | 122.0961 | 122.1183
2530.2344 | 122.3648 | -0.073242 | 122.1725 | 0.098959 | 0.023583 | -0.025735 | -0.006703 | 0.004219 | 0.085583 | -0.012357 | 122.2113 | 122.1596 | 122.0939 | 122.0118 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.1722 | 0.096825 | 0.047507 | 0.066539 | 0.077461 | 0.15882 | 0.060885 | 122.2525 | 122.2008 | 122.1351 | 122.053 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.2272 | 122.2448 | 122.1098 | 122.1274
2531.9844 | 122.3694 | -0.07782 | 122.1817 | 0.098959 | 0.014425 | -0.016578 | -0.002124 | 0.004219 | 0.085583 | -0.016936 | 122.2067 | 122.1551 | 122.0894 | 122.0073 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.17678 | 0.092245 | 0.061242 | 0.075696 | 0.082039 | 0.1634 | 0.060884 | 122.2479 | 122.1963 | 122.1306 | 122.0485 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.218 | 122.2356 | 122.1006 | 122.1183
2533.6719 | 122.2733 | -0.10529 | 122.2229 | 0.094381 | 0.019004 | -0.012 | -0.006703 | 0.013375 | 0.090161 | -0.021514 | 122.2067 | 122.1642 | 122.0985 | 122.0073 | -0.020437 | 0.027798 | -0.019749 | 0.005985 | 0.19967 | 0.12429 | 0.093286 | 0.098583 | 0.11866 | 0.19545 | 0.083772 | 122.2479 | 122.2054 | 122.1397 | 122.0485 | 0.020762 | 0.068997 | 0.02145 | 0.047184 | 122.2272 | 122.2265 | 122.119 | 122.1183
2535.4219 | 122.3877 | -0.054932 | 122.1634 | 0.089802 | 0.014425 | -0.025735 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 122.2113 | 122.1596 | 122.0985 | 122.0073 | -0.011281 | 0.032376 | -0.024328 | 0.005985 | 0.14473 | 0.069357 | 0.029197 | 0.043651 | 0.059151 | 0.14052 | 0.037996 | 122.2525 | 122.2008 | 122.1397 | 122.0485 | 0.029918 | 0.073575 | 0.016871 | 0.047184 | 122.2226 | 122.2356 | 122.1098 | 122.1229
2537.1875 | 122.3236 | -0.091553 | 122.2046 | 0.094381 | 0.023583 | -0.025735 | -0.002124 | 0.008797 | 0.085583 | -0.016936 | 122.2113 | 122.1505 | 122.1031 | 122.0073 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.18593 | 0.11514 | 0.065818 | 0.089429 | 0.10035 | 0.17714 | 0.074617 | 122.2525 | 122.1917 | 122.1443 | 122.0485 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.2272 | 122.2356 | 122.119 | 122.1274
2538.9531 | 122.319 | -0.10986 | 122.1954 | 0.10354 | 0.014425 | -0.016578 | -0.006703 | 0.017953 | 0.090161 | -0.012357 | 122.2022 | 122.1642 | 122.0985 | 122.0118 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.2134 | 0.12429 | 0.093285 | 0.10316 | 0.12782 | 0.20002 | 0.097506 | 122.2434 | 122.2054 | 122.1397 | 122.053 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2134 | 122.2311 | 122.1098 | 122.1274
2540.7031 | 122.2961 | -0.10071 | 122.2 | 0.10354 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.09474 | -0.012357 | 122.2159 | 122.1596 | 122.1031 | 122.0073 | -0.015859 | 0.032376 | -0.019749 | 0.005985 | 0.20425 | 0.11971 | 0.08413 | 0.089427 | 0.10951 | 0.19545 | 0.088351 | 122.2571 | 122.2008 | 122.1443 | 122.0485 | 0.02534 | 0.073575 | 0.02145 | 0.047184 | 122.2318 | 122.2356 | 122.119 | 122.1228
2542.3906 | 122.3236 | -0.073242 | 122.1817 | 0.10354 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.2205 | 122.1642 | 122.0985 | 121.9981 | -0.015859 | 0.027798 | -0.024328 | 0.010563 | 0.17678 | 0.092246 | 0.052085 | 0.061961 | 0.082039 | 0.1634 | 0.056306 | 122.2617 | 122.2054 | 122.1397 | 122.0393 | 0.02534 | 0.068997 | 0.016871 | 0.051762 | 122.2363 | 122.2448 | 122.1144 | 122.1229
2544.1406 | 122.3602 | -0.068665 | 122.1634 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 122.2159 | 122.1596 | 122.0985 | 122.0118 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 0.16762 | 0.087669 | 0.04293 | 0.052805 | 0.072884 | 0.15425 | 0.051729 | 122.2571 | 122.2008 | 122.1397 | 122.053 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 122.2226 | 122.2448 | 122.1052 | 122.1274
2545.8906 | 122.2687 | -0.091553 | 122.2137 | 0.098959 | 0.019004 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.2205 | 122.1642 | 122.0894 | 122.0164 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.19051 | 0.11056 | 0.070396 | 0.08485 | 0.10035 | 0.17714 | 0.079196 | 122.2617 | 122.2054 | 122.1306 | 122.0576 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.2363 | 122.2494 | 122.1052 | 122.1183
2547.6406 | 122.3145 | -0.10529 | 122.168 | 0.10354 | 0.014425 | -0.025735 | -0.002124 | 0.004219 | 0.090161 | -0.012357 | 122.2067 | 122.1596 | 122.0985 | 122.0027 | -0.006702 | 0.032376 | -0.033484 | 0.010563 | 0.20882 | 0.11971 | 0.079551 | 0.10316 | 0.10951 | 0.19545 | 0.092929 | 122.2479 | 122.2008 | 122.1397 | 122.0439 | 0.034497 | 0.073575 | 0.007715 | 0.051762 | 122.2134 | 122.2402 | 122.1052 | 122.132
2549.3281 | 122.3602 | -0.082397 | 122.1405 | 0.094381 | 0.019004 | -0.025735 | -0.006703 | 0.008797 | 0.081005 | -0.016936 | 122.2205 | 122.1642 | 122.1031 | 122.0073 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.17678 | 0.1014 | 0.056662 | 0.075694 | 0.091194 | 0.1634 | 0.065461 | 122.2617 | 122.2054 | 122.1443 | 122.0485 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.2363 | 122.2494 | 122.119 | 122.132
2551.0938 | 122.3557 | -0.086975 | 122.168 | 0.10354 | 0.019004 | -0.016578 | -0.01586 | -0.000359 | 0.085583 | -0.021514 | 122.2113 | 122.1688 | 122.0985 | 122.0164 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.19051 | 0.10598 | 0.070397 | 0.071115 | 0.086616 | 0.17256 | 0.065461 | 122.2525 | 122.21 | 122.1397 | 122.0576 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.218 | 122.2402 | 122.1052 | 122.1274
2552.7812 | 122.2961 | -0.10071 | 122.2137 | 0.098959 | 0.014425 | -0.025735 | -0.011281 | 0.004219 | 0.090161 | -0.016936 | 122.2159 | 122.1596 | 122.1031 | 122.0118 | -0.015859 | 0.032376 | -0.024328 | 0.005985 | 0.19967 | 0.11513 | 0.074973 | 0.089427 | 0.10493 | 0.19087 | 0.083772 | 122.2571 | 122.2008 | 122.1443 | 122.053 | 0.02534 | 0.073575 | 0.016871 | 0.047184 | 122.2318 | 122.2402 | 122.119 | 122.1274
2554.5312 | 122.287 | -0.10071 | 122.1909 | 0.098959 | 0.019004 | -0.025735 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.2159 | 122.1734 | 122.0939 | 122.0118 | -0.025015 | 0.032376 | -0.028906 | 0.001406 | 0.19967 | 0.11971 | 0.074973 | 0.089427 | 0.10951 | 0.19087 | 0.083772 | 122.2571 | 122.2146 | 122.1351 | 122.053 | 0.016184 | 0.073575 | 0.012293 | 0.042605 | 122.2409 | 122.2448 | 122.119 | 122.1228
2556.2812 | 122.4289 | -0.059509 | 122.1542 | 0.094381 | 0.009846 | -0.021157 | -0.011281 | -0.000359 | 0.090161 | -0.012357 | 122.2159 | 122.178 | 122.1031 | 122.0164 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.15389 | 0.069355 | 0.038352 | 0.048228 | 0.05915 | 0.14967 | 0.047152 | 122.2571 | 122.2192 | 122.1443 | 122.0576 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.2272 | 122.2402 | 122.1144 | 122.1274
2558.0312 | 122.3099 | -0.10071 | 122.1817 | 0.10354 | 0.014425 | -0.016578 | -0.002124 | 0.008797 | 0.090161 | -0.016936 | 122.2205 | 122.1688 | 122.0985 | 122.0118 | -0.011281 | 0.027798 | -0.033484 | 0.010563 | 0.20425 | 0.11513 | 0.08413 | 0.098584 | 0.10951 | 0.19087 | 0.083772 | 122.2617 | 122.21 | 122.1397 | 122.053 | 0.029918 | 0.068997 | 0.007715 | 0.051762 | 122.2318 | 122.254 | 122.1098 | 122.132
2559.7188 | 122.3419 | -0.07782 | 122.1725 | 0.098959 | 0.019004 | -0.025735 | -0.006703 | 0.008797 | 0.085583 | -0.021514 | 122.2159 | 122.1688 | 122.1031 | 122.0164 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.17678 | 0.096824 | 0.052085 | 0.071117 | 0.086617 | 0.1634 | 0.056306 | 122.2571 | 122.21 | 122.1443 | 122.0576 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.2272 | 122.2402 | 122.1144 | 122.1274
2561.4688 | 122.2961 | -0.09613 | 122.1954 | 0.098959 | 0.023583 | -0.021157 | -0.006703 | -0.000359 | 0.085583 | -0.016936 | 122.2251 | 122.1688 | 122.0939 | 122.0073 | -0.015859 | 0.036954 | -0.028906 | 0.001406 | 0.19509 | 0.11971 | 0.074973 | 0.089427 | 0.095771 | 0.18171 | 0.079194 | 122.2663 | 122.21 | 122.1351 | 122.0485 | 0.02534 | 0.078153 | 0.012293 | 0.042605 | 122.2409 | 122.254 | 122.1098 | 122.1228
2563.2344 | 122.3419 | -0.082397 | 122.1725 | 0.10354 | 0.023583 | -0.025735 | -0.011281 | 0.008797 | 0.090161 | -0.007779 | 122.2159 | 122.1734 | 122.0985 | 122.0118 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.18593 | 0.10598 | 0.056662 | 0.071116 | 0.091194 | 0.17256 | 0.074618 | 122.2571 | 122.2146 | 122.1397 | 122.053 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2272 | 122.2448 | 122.1098 | 122.1274
2564.9844 | 122.2687 | -0.09613 | 122.2229 | 0.10354 | 0.023583 | -0.021157 | -0.002124 | 0.008797 | 0.09474 | -0.012357 | 122.2205 | 122.1688 | 122.0985 | 122.021 | -0.006702 | 0.027798 | -0.019749 | 0.005985 | 0.19967 | 0.11971 | 0.074973 | 0.094006 | 0.10493 | 0.19087 | 0.083773 | 122.2617 | 122.21 | 122.1397 | 122.0622 | 0.034497 | 0.068997 | 0.02145 | 0.047184 | 122.2272 | 122.2402 | 122.1052 | 122.1183
2566.6719 | 122.319 | -0.082397 | 122.2137 | 0.10354 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.016936 | 122.2205 | 122.1734 | 122.0985 | 122.0164 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.18593 | 0.10598 | 0.06124 | 0.066537 | 0.091194 | 0.16798 | 0.065461 | 122.2617 | 122.2146 | 122.1397 | 122.0576 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.2318 | 122.2494 | 122.1098 | 122.1274
2568.4219 | 122.4289 | -0.073242 | 122.1588 | 0.089802 | 0.019004 | -0.021157 | -0.020438 | 0.004219 | 0.081005 | -0.016936 | 122.2205 | 122.1596 | 122.0894 | 122.0164 | -0.020437 | 0.032376 | -0.028906 | 0.005985 | 0.16304 | 0.092246 | 0.052085 | 0.052804 | 0.077461 | 0.15425 | 0.056306 | 122.2617 | 122.2008 | 122.1306 | 122.0576 | 0.020762 | 0.073575 | 0.012293 | 0.047184 | 122.2409 | 122.2494 | 122.1098 | 122.1183
2570.1719 | 122.3923 | -0.07782 | 122.1817 | 0.094381 | 0.028162 | -0.025735 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.2159 | 122.1734 | 122.1077 | 122.021 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.1722 | 0.10598 | 0.052085 | 0.066539 | 0.086617 | 0.15882 | 0.060884 | 122.2571 | 122.2146 | 122.1489 | 122.0622 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.2272 | 122.2448 | 122.119 | 122.1366
2571.8594 | 122.3831 | -0.064087 | 122.1909 | 0.098959 | 0.019004 | -0.025735 | -0.011281 | -0.000359 | 0.081005 | -0.012357 | 122.2159 | 122.1688 | 122.1031 | 122.0164 | -0.006702 | 0.032376 | -0.024328 | 0.001406 | 0.16305 | 0.083091 | 0.038352 | 0.052806 | 0.063728 | 0.14509 | 0.05173 | 122.2571 | 122.21 | 122.1443 | 122.0576 | 0.034497 | 0.073575 | 0.016871 | 0.042605 | 122.2226 | 122.2402 | 122.1098 | 122.1274
2573.625 | 122.2687 | -0.10529 | 122.2046 | 0.094381 | 0.023583 | -0.025735 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2205 | 122.1734 | 122.1031 | 122.021 | -0.011281 | 0.027798 | -0.033484 | 0.010563 | 0.19967 | 0.12887 | 0.079551 | 0.098583 | 0.10951 | 0.19545 | 0.092929 | 122.2617 | 122.2146 | 122.1443 | 122.0622 | 0.029918 | 0.068997 | 0.007715 | 0.051762 | 122.2318 | 122.254 | 122.1144 | 122.1366
2575.3906 | 122.2641 | -0.10071 | 122.1909 | 0.098959 | 0.028162 | -0.021157 | -0.006703 | 0.004219 | 0.090161 | -0.021514 | 122.2251 | 122.1688 | 122.1031 | 122.0164 | -0.006702 | 0.027798 | -0.019749 | 0.001406 | 0.19967 | 0.12887 | 0.079551 | 0.094005 | 0.10493 | 0.19087 | 0.079194 | 122.2663 | 122.21 | 122.1443 | 122.0576 | 0.034497 | 0.068997 | 0.02145 | 0.042605 | 122.2318 | 122.2448 | 122.1098 | 122.1228
2577.1406 | 122.287 | -0.09613 | 122.1909 | 0.10354 | 0.028162 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2251 | 122.1688 | 122.1077 | 122.0118 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.19967 | 0.12429 | 0.074973 | 0.089427 | 0.10035 | 0.18171 | 0.079194 | 122.2663 | 122.21 | 122.1489 | 122.053 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2363 | 122.254 | 122.119 | 122.1366
2578.8594 | 122.4197 | -0.068665 | 122.1954 | 0.089802 | 0.019004 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.016936 | 122.2159 | 122.1688 | 122.1077 | 122.021 | -0.015859 | 0.032376 | -0.024328 | 0.005985 | 0.15847 | 0.087669 | 0.04293 | 0.052805 | 0.068306 | 0.15425 | 0.051729 | 122.2571 | 122.21 | 122.1489 | 122.0622 | 0.02534 | 0.073575 | 0.016871 | 0.047184 | 122.2318 | 122.2402 | 122.1235 | 122.132
2580.625 | 122.2916 | -0.10529 | 122.2275 | 0.10354 | 0.023583 | -0.021157 | -0.006703 | 0.004219 | 0.09474 | -0.012357 | 122.2251 | 122.1688 | 122.1031 | 122.0164 | -0.006702 | 0.032376 | -0.033484 | 0.005985 | 0.20882 | 0.12887 | 0.084129 | 0.098583 | 0.10951 | 0.20003 | 0.092929 | 122.2663 | 122.21 | 122.1443 | 122.0576 | 0.034497 | 0.073575 | 0.007715 | 0.047184 | 122.2318 | 122.2585 | 122.1098 | 122.1366
2582.3125 | 122.287 | -0.091553 | 122.2137 | 0.098959 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.016936 | 122.2251 | 122.1688 | 122.1077 | 122.0256 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.19051 | 0.11971 | 0.074975 | 0.080272 | 0.10493 | 0.17714 | 0.074617 | 122.2663 | 122.21 | 122.1489 | 122.0668 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2363 | 122.254 | 122.119 | 122.1366
2584.0781 | 122.2961 | -0.11444 | 122.2229 | 0.098959 | 0.023583 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.012357 | 122.2296 | 122.1825 | 122.1077 | 122.0302 | -0.015859 | 0.032376 | -0.033484 | 0.010563 | 0.2134 | 0.13802 | 0.093284 | 0.098581 | 0.12324 | 0.20002 | 0.10208 | 122.2708 | 122.2237 | 122.1489 | 122.0714 | 0.02534 | 0.073575 | 0.007715 | 0.051762 | 122.2455 | 122.2631 | 122.1235 | 122.1412
2585.8281 | 122.3282 | -0.09613 | 122.1863 | 0.094381 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 122.2205 | 122.1734 | 122.1077 | 122.0256 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.19051 | 0.11055 | 0.079552 | 0.084849 | 0.10493 | 0.18629 | 0.083773 | 122.2617 | 122.2146 | 122.1489 | 122.0668 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.2363 | 122.2448 | 122.1235 | 122.132
2587.5156 | 122.3648 | -0.086975 | 122.1771 | 0.094381 | 0.009846 | -0.025735 | -0.006703 | -0.000359 | 0.090161 | -0.012357 | 122.2205 | 122.1688 | 122.1077 | 122.021 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.18136 | 0.096821 | 0.06124 | 0.080272 | 0.086616 | 0.17714 | 0.074618 | 122.2617 | 122.21 | 122.1489 | 122.0622 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.2363 | 122.254 | 122.1235 | 122.1412
2589.2656 | 122.3877 | -0.068665 | 122.1771 | 0.10354 | 0.009846 | -0.016578 | -0.011281 | -0.004937 | 0.085583 | -0.016936 | 122.2251 | 122.1688 | 122.1031 | 122.0164 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.1722 | 0.078511 | 0.052087 | 0.057384 | 0.063728 | 0.15425 | 0.051729 | 122.2663 | 122.21 | 122.1443 | 122.0576 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2363 | 122.254 | 122.1144 | 122.132
2591.0156 | 122.4289 | -0.054932 | 122.1634 | 0.10354 | 0.014425 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.026092 | 122.2296 | 122.1734 | 122.1031 | 122.021 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.15847 | 0.069357 | 0.033775 | 0.039072 | 0.059151 | 0.14509 | 0.02884 | 122.2708 | 122.2146 | 122.1443 | 122.0622 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.2455 | 122.2585 | 122.119 | 122.132
2592.7031 | 122.3465 | -0.086975 | 122.1817 | 0.10812 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.021514 | 122.2251 | 122.178 | 122.1168 | 122.0164 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.19509 | 0.1014 | 0.070397 | 0.075694 | 0.095772 | 0.17256 | 0.065461 | 122.2663 | 122.2192 | 122.158 | 122.0576 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.2409 | 122.254 | 122.1327 | 122.1457
2594.4688 | 122.3831 | -0.073242 | 122.1771 | 0.10354 | 0.019004 | -0.021157 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2205 | 122.1871 | 122.1077 | 122.0256 | -0.011281 | 0.02322 | -0.019749 | 0.010563 | 0.17678 | 0.092246 | 0.052085 | 0.066539 | 0.077461 | 0.1634 | 0.060885 | 122.2617 | 122.2283 | 122.1489 | 122.0668 | 0.029918 | 0.064419 | 0.02145 | 0.051762 | 122.2318 | 122.2402 | 122.119 | 122.1274
2596.1562 | 122.4014 | -0.032043 | 122.1863 | 0.10354 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.076426 | -0.026092 | 122.2205 | 122.1825 | 122.1123 | 122.0256 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 0.13558 | 0.046468 | 0.015465 | 0.020762 | 0.04084 | 0.10847 | 0.005951 | 122.2617 | 122.2237 | 122.1535 | 122.0668 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 122.2318 | 122.2494 | 122.1235 | 122.1412
2597.9062 | 122.2687 | -0.07782 | 122.2412 | 0.098959 | 0.028162 | -0.016578 | -0.011281 | 0.004219 | 0.09474 | -0.012357 | 122.2342 | 122.178 | 122.1168 | 122.0256 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.17678 | 0.10598 | 0.061242 | 0.066539 | 0.082039 | 0.17256 | 0.065463 | 122.2754 | 122.2192 | 122.158 | 122.0668 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.2501 | 122.2631 | 122.1327 | 122.1457
2599.6562 | 122.4106 | -0.054932 | 122.168 | 0.098959 | 0.03274 | -0.025735 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 122.2296 | 122.178 | 122.1168 | 122.021 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.15389 | 0.087672 | 0.029197 | 0.039072 | 0.059151 | 0.13594 | 0.037996 | 122.2708 | 122.2192 | 122.158 | 122.0622 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.2455 | 122.2585 | 122.1327 | 122.1457
2601.3438 | 122.2961 | -0.09613 | 122.2229 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.2251 | 122.178 | 122.1168 | 122.021 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.19509 | 0.11971 | 0.074973 | 0.084849 | 0.10493 | 0.18171 | 0.083773 | 122.2663 | 122.2192 | 122.158 | 122.0622 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2409 | 122.254 | 122.1327 | 122.1457
2603.1094 | 122.4106 | -0.059509 | 122.1817 | 0.10354 | 0.014425 | -0.016578 | -0.006703 | 0.004219 | 0.085583 | -0.021514 | 122.2296 | 122.178 | 122.1031 | 122.0256 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.16305 | 0.073934 | 0.042931 | 0.052806 | 0.063728 | 0.14509 | 0.037995 | 122.2708 | 122.2192 | 122.1443 | 122.0668 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2409 | 122.2585 | 122.1144 | 122.132
2604.8125 | 122.2687 | -0.10529 | 122.2183 | 0.10354 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2251 | 122.178 | 122.1123 | 122.0302 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.20882 | 0.12887 | 0.088708 | 0.098583 | 0.10951 | 0.19545 | 0.092929 | 122.2663 | 122.2192 | 122.1535 | 122.0714 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.2363 | 122.254 | 122.1235 | 122.1412
2606.5625 | 122.2778 | -0.091553 | 122.2046 | 0.094381 | 0.028162 | -0.012 | -0.011281 | 0.004219 | 0.090161 | -0.012357 | 122.2342 | 122.1871 | 122.1123 | 122.0164 | -0.020437 | 0.032376 | -0.028906 | 0.001406 | 0.18593 | 0.11971 | 0.079553 | 0.080272 | 0.095772 | 0.18171 | 0.079196 | 122.2754 | 122.2283 | 122.1535 | 122.0576 | 0.020762 | 0.073575 | 0.012293 | 0.042605 | 122.2546 | 122.2631 | 122.1327 | 122.1412
2608.3281 | 122.2824 | -0.10071 | 122.2 | 0.094381 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.09474 | -0.012357 | 122.2342 | 122.1734 | 122.1077 | 122.021 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.19509 | 0.11971 | 0.08413 | 0.094005 | 0.10951 | 0.19545 | 0.088351 | 122.2754 | 122.2146 | 122.1489 | 122.0622 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.2501 | 122.2631 | 122.1235 | 122.1366
2610.0938 | 122.3923 | -0.064087 | 122.1771 | 0.10354 | 0.023583 | -0.025735 | -0.011281 | -0.000359 | 0.085583 | -0.016936 | 122.2251 | 122.178 | 122.1123 | 122.0302 | -0.011281 | 0.02322 | -0.024328 | -0.003172 | 0.16762 | 0.08767 | 0.038352 | 0.052806 | 0.063728 | 0.14967 | 0.047151 | 122.2663 | 122.2192 | 122.1535 | 122.0714 | 0.029918 | 0.064419 | 0.016871 | 0.038027 | 122.2363 | 122.2494 | 122.1235 | 122.1366
2611.875 | 122.2778 | -0.10529 | 122.2321 | 0.094381 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.012357 | 122.2296 | 122.178 | 122.1123 | 122.0256 | -0.006702 | 0.027798 | -0.033484 | 0.005985 | 0.19967 | 0.12887 | 0.088708 | 0.094005 | 0.11866 | 0.19087 | 0.092929 | 122.2708 | 122.2192 | 122.1535 | 122.0668 | 0.034497 | 0.068997 | 0.007715 | 0.047184 | 122.2363 | 122.2631 | 122.119 | 122.1457
2613.5625 | 122.3831 | -0.064087 | 122.1954 | 0.089802 | 0.023583 | -0.025735 | -0.01586 | -0.000359 | 0.081005 | -0.007779 | 122.2296 | 122.178 | 122.1077 | 122.0256 | -0.011281 | 0.032376 | -0.028906 | 0.010563 | 0.15389 | 0.08767 | 0.038352 | 0.048227 | 0.063728 | 0.14509 | 0.056308 | 122.2708 | 122.2192 | 122.1489 | 122.0668 | 0.029918 | 0.073575 | 0.012293 | 0.051762 | 122.2409 | 122.2585 | 122.119 | 122.1366
2615.3281 | 122.4106 | -0.059509 | 122.1771 | 0.098959 | 0.019004 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 122.2251 | 122.178 | 122.1123 | 122.021 | -0.011281 | 0.027798 | -0.024328 | 0.001406 | 0.15847 | 0.078513 | 0.038352 | 0.048228 | 0.063728 | 0.14509 | 0.037995 | 122.2663 | 122.2192 | 122.1535 | 122.0622 | 0.029918 | 0.068997 | 0.016871 | 0.042605 | 122.2363 | 122.2494 | 122.1235 | 122.1366
2617.0938 | 122.3236 | -0.091553 | 122.2092 | 0.10354 | 0.028162 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.016936 | 122.2251 | 122.178 | 122.126 | 122.0302 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.19509 | 0.11971 | 0.074975 | 0.075693 | 0.10035 | 0.17714 | 0.074617 | 122.2663 | 122.2192 | 122.1672 | 122.0714 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.2363 | 122.254 | 122.1373 | 122.1549
2618.8594 | 122.3923 | -0.07782 | 122.1909 | 0.098959 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.016936 | 122.2251 | 122.1825 | 122.1168 | 122.0256 | -0.015859 | 0.02322 | -0.024328 | -0.003172 | 0.17678 | 0.1014 | 0.061242 | 0.071117 | 0.082039 | 0.16798 | 0.060884 | 122.2663 | 122.2237 | 122.158 | 122.0668 | 0.02534 | 0.064419 | 0.016871 | 0.038027 | 122.2409 | 122.2494 | 122.1327 | 122.1412
2620.625 | 122.3969 | -0.073242 | 122.1634 | 0.089802 | 0.009846 | -0.021157 | -0.01586 | -0.000359 | 0.085583 | -0.012357 | 122.2251 | 122.178 | 122.1123 | 122.0302 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.16304 | 0.083088 | 0.052085 | 0.057382 | 0.072883 | 0.15882 | 0.060885 | 122.2663 | 122.2192 | 122.1535 | 122.0714 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.2409 | 122.254 | 122.1281 | 122.1412
2622.3281 | 122.4014 | -0.073242 | 122.1863 | 0.098959 | 0.023583 | -0.016578 | -0.011281 | -0.000359 | 0.090161 | -0.016936 | 122.2251 | 122.178 | 122.1077 | 122.0302 | -0.006702 | 0.02322 | -0.028906 | -0.003172 | 0.1722 | 0.096825 | 0.056664 | 0.061961 | 0.072883 | 0.1634 | 0.056306 | 122.2663 | 122.2192 | 122.1489 | 122.0714 | 0.034497 | 0.064419 | 0.012293 | 0.038027 | 122.2318 | 122.254 | 122.1144 | 122.1366
2624.0938 | 122.3785 | -0.068665 | 122.1817 | 0.10354 | 0.019004 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.012357 | 122.2296 | 122.1871 | 122.1168 | 122.0256 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.1722 | 0.087669 | 0.052087 | 0.052805 | 0.077462 | 0.15425 | 0.056308 | 122.2708 | 122.2283 | 122.158 | 122.0668 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.2455 | 122.2631 | 122.1327 | 122.1503
2625.7812 | 122.3785 | -0.086975 | 122.2046 | 0.10354 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.081005 | -0.007779 | 122.2251 | 122.1825 | 122.1168 | 122.0256 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.19051 | 0.1014 | 0.065818 | 0.075694 | 0.095772 | 0.16798 | 0.079196 | 122.2663 | 122.2237 | 122.158 | 122.0668 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.2409 | 122.2585 | 122.1327 | 122.1503
2627.5312 | 122.2916 | -0.11444 | 122.2275 | 0.098959 | 0.028162 | -0.021157 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 122.2251 | 122.1825 | 122.1123 | 122.0256 | -0.020437 | 0.032376 | -0.024328 | 0.001406 | 0.2134 | 0.1426 | 0.093284 | 0.11232 | 0.12324 | 0.20002 | 0.10666 | 122.2663 | 122.2237 | 122.1535 | 122.0668 | 0.020762 | 0.073575 | 0.016871 | 0.042605 | 122.2455 | 122.2494 | 122.1327 | 122.1366
2629.2344 | 122.3099 | -0.086975 | 122.2275 | 0.098959 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.2342 | 122.1825 | 122.1077 | 122.0347 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.18593 | 0.11056 | 0.065818 | 0.080272 | 0.095772 | 0.17256 | 0.074618 | 122.2754 | 122.2237 | 122.1489 | 122.0759 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.2501 | 122.2631 | 122.1235 | 122.1366
2630.9844 | 122.3602 | -0.082397 | 122.2 | 0.094381 | 0.019004 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2296 | 122.1825 | 122.1214 | 122.0347 | -0.015859 | 0.02322 | -0.033484 | 0.015141 | 0.17678 | 0.1014 | 0.06124 | 0.075694 | 0.086616 | 0.16798 | 0.065461 | 122.2708 | 122.2237 | 122.1626 | 122.0759 | 0.02534 | 0.064419 | 0.007715 | 0.05634 | 122.2455 | 122.2631 | 122.1373 | 122.1549
2632.7344 | 122.3053 | -0.10529 | 122.2092 | 0.098959 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 122.2342 | 122.1825 | 122.1123 | 122.0347 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.20425 | 0.12887 | 0.088708 | 0.094005 | 0.10951 | 0.19087 | 0.083772 | 122.2754 | 122.2237 | 122.1535 | 122.0759 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.2455 | 122.2631 | 122.1235 | 122.1412
2634.4219 | 122.3648 | -0.064087 | 122.2 | 0.098959 | 0.019004 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.021514 | 122.2342 | 122.178 | 122.1168 | 122.0347 | -0.015859 | 0.027798 | -0.033484 | 0.010563 | 0.16305 | 0.083091 | 0.047509 | 0.048227 | 0.068306 | 0.14967 | 0.042573 | 122.2754 | 122.2192 | 122.158 | 122.0759 | 0.02534 | 0.068997 | 0.007715 | 0.051762 | 122.2501 | 122.2677 | 122.1327 | 122.1503
2636.1719 | 122.3785 | -0.045776 | 122.1909 | 0.098959 | 0.019004 | -0.016578 | -0.011281 | -0.000359 | 0.076426 | -0.007779 | 122.2388 | 122.1825 | 122.1214 | 122.0347 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.14474 | 0.06478 | 0.029198 | 0.034495 | 0.045417 | 0.1222 | 0.037997 | 122.28 | 122.2237 | 122.1626 | 122.0759 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2501 | 122.2723 | 122.1327 | 122.1549
2637.8594 | 122.374 | -0.07782 | 122.1909 | 0.094381 | 0.014425 | -0.016578 | -0.020438 | 0.004219 | 0.076426 | -0.021514 | 122.2342 | 122.178 | 122.1214 | 122.0347 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.1722 | 0.092245 | 0.061242 | 0.057382 | 0.082039 | 0.15425 | 0.056306 | 122.2754 | 122.2192 | 122.1626 | 122.0759 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2455 | 122.2631 | 122.1327 | 122.1503
2639.625 | 122.3923 | -0.050354 | 122.2046 | 0.098959 | 0.005267 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.012357 | 122.2342 | 122.1871 | 122.1077 | 122.0347 | -0.011281 | 0.032376 | -0.028906 | -0.00775 | 0.14931 | 0.055621 | 0.024619 | 0.034494 | 0.049995 | 0.13594 | 0.037997 | 122.2754 | 122.2283 | 122.1489 | 122.0759 | 0.029918 | 0.073575 | 0.012293 | 0.033449 | 122.2455 | 122.2631 | 122.119 | 122.1366
2641.375 | 122.2824 | -0.10529 | 122.2366 | 0.098959 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 122.2388 | 122.1917 | 122.1168 | 122.0347 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.20425 | 0.12429 | 0.084129 | 0.094005 | 0.11408 | 0.19545 | 0.092929 | 122.28 | 122.2329 | 122.158 | 122.0759 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.2546 | 122.2723 | 122.1327 | 122.1503
2643.0781 | 122.4152 | -0.054932 | 122.1909 | 0.10354 | 0.023583 | -0.025735 | -0.011281 | -0.000359 | 0.085583 | -0.012357 | 122.2296 | 122.1871 | 122.126 | 122.0347 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.15847 | 0.078515 | 0.029197 | 0.043651 | 0.054573 | 0.14052 | 0.042575 | 122.2708 | 122.2283 | 122.1672 | 122.0759 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.2455 | 122.2585 | 122.1419 | 122.1549
2644.8438 | 122.3785 | -0.068665 | 122.2137 | 0.094381 | 0.023583 | -0.025735 | -0.011281 | -0.000359 | 0.085583 | -0.016936 | 122.2434 | 122.178 | 122.1214 | 122.0347 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.16305 | 0.092248 | 0.04293 | 0.057384 | 0.068306 | 0.15425 | 0.051729 | 122.2846 | 122.2192 | 122.1626 | 122.0759 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.2592 | 122.2723 | 122.1373 | 122.1503
2646.6094 | 122.3831 | -0.07782 | 122.1954 | 0.098959 | 0.019004 | -0.025735 | -0.011281 | -0.000359 | 0.085583 | -0.016936 | 122.2251 | 122.1825 | 122.126 | 122.0302 | -0.011281 | 0.027798 | -0.028906 | 0.010563 | 0.17678 | 0.096824 | 0.052085 | 0.066539 | 0.077461 | 0.1634 | 0.060884 | 122.2663 | 122.2237 | 122.1672 | 122.0714 | 0.029918 | 0.068997 | 0.012293 | 0.051762 | 122.2363 | 122.254 | 122.1373 | 122.1549
2648.375 | 122.2778 | -0.10986 | 122.2412 | 0.098959 | 0.03274 | -0.021157 | -0.006703 | -0.000359 | 0.081005 | -0.016936 | 122.2342 | 122.1825 | 122.1168 | 122.0393 | -0.015859 | 0.027798 | -0.024328 | 0.010563 | 0.20882 | 0.1426 | 0.088706 | 0.10316 | 0.1095 | 0.19087 | 0.092927 | 122.2754 | 122.2237 | 122.158 | 122.0805 | 0.02534 | 0.068997 | 0.016871 | 0.051762 | 122.2501 | 122.2585 | 122.1327 | 122.1412
2650.0781 | 122.3511 | -0.073242 | 122.2046 | 0.098959 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.090161 | -0.016936 | 122.2342 | 122.1825 | 122.126 | 122.0393 | -0.006702 | 0.02322 | -0.038063 | 0.010563 | 0.1722 | 0.092246 | 0.056664 | 0.061961 | 0.077461 | 0.1634 | 0.056306 | 122.2754 | 122.2237 | 122.1672 | 122.0805 | 0.034497 | 0.064419 | 0.003136 | 0.051762 | 122.2409 | 122.2723 | 122.1327 | 122.1641
2651.8281 | 122.406 | -0.050354 | 122.1588 | 0.089802 | 0.014425 | -0.021157 | -0.006703 | 0.004219 | 0.09474 | -0.012357 | 122.2342 | 122.1825 | 122.1214 | 122.0393 | -0.020437 | 0.027798 | -0.033484 | 0.001406 | 0.14016 | 0.064779 | 0.029197 | 0.043651 | 0.054573 | 0.14509 | 0.037997 | 122.2754 | 122.2237 | 122.1626 | 122.0805 | 0.020762 | 0.068997 | 0.007715 | 0.042605 | 122.2546 | 122.2677 | 122.1419 | 122.1549
2653.5781 | 122.2961 | -0.10071 | 122.2137 | 0.10354 | 0.023583 | -0.016578 | -0.01586 | -0.000359 | 0.085583 | -0.007779 | 122.2342 | 122.1825 | 122.1214 | 122.0347 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.20425 | 0.12429 | 0.08413 | 0.084848 | 0.10035 | 0.18629 | 0.092929 | 122.2754 | 122.2237 | 122.1626 | 122.0759 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.2501 | 122.2585 | 122.1373 | 122.1457
2655.2656 | 122.374 | -0.073242 | 122.1954 | 0.098959 | 0.014425 | -0.021157 | -0.01586 | -0.004937 | 0.085583 | -0.016936 | 122.2388 | 122.1825 | 122.1214 | 122.0393 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.1722 | 0.087667 | 0.052085 | 0.057382 | 0.068305 | 0.15882 | 0.056306 | 122.28 | 122.2237 | 122.1626 | 122.0805 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.2546 | 122.2631 | 122.1373 | 122.1457
2657.0156 | 122.3282 | -0.086975 | 122.2137 | 0.11269 | 0.014425 | -0.025735 | -0.01586 | 0.008797 | 0.085583 | -0.016936 | 122.2388 | 122.1871 | 122.1123 | 122.0347 | -0.015859 | 0.032376 | -0.024328 | 0.001406 | 0.19967 | 0.1014 | 0.06124 | 0.071115 | 0.095772 | 0.17256 | 0.070039 | 122.28 | 122.2283 | 122.1535 | 122.0759 | 0.02534 | 0.073575 | 0.016871 | 0.042605 | 122.2546 | 122.2631 | 122.1281 | 122.1366
2658.7031 | 122.3419 | -0.082397 | 122.1954 | 0.094381 | 0.023583 | -0.012 | -0.006703 | 0.004219 | 0.090161 | -0.007779 | 122.2342 | 122.1871 | 122.1214 | 122.0347 | -0.011281 | 0.027798 | -0.024328 | 0.001406 | 0.17678 | 0.10598 | 0.070397 | 0.075694 | 0.086616 | 0.17256 | 0.074618 | 122.2754 | 122.2283 | 122.1626 | 122.0759 | 0.029918 | 0.068997 | 0.016871 | 0.042605 | 122.2455 | 122.2585 | 122.1327 | 122.1457
2660.4688 | 122.3969 | -0.050354 | 122.1863 | 0.10354 | 0.023583 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 122.2388 | 122.1871 | 122.126 | 122.0347 | -0.015859 | 0.032376 | -0.033484 | 0.005985 | 0.15389 | 0.073937 | 0.033776 | 0.04823 | 0.054573 | 0.13136 | 0.037997 | 122.28 | 122.2283 | 122.1672 | 122.0759 | 0.02534 | 0.073575 | 0.007715 | 0.047184 | 122.2546 | 122.2723 | 122.1419 | 122.1595
2662.1562 | 122.4014 | -0.050354 | 122.2 | 0.098959 | 0.014425 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 122.2388 | 122.1917 | 122.1168 | 122.0393 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.14931 | 0.064779 | 0.029197 | 0.034494 | 0.054573 | 0.13594 | 0.037997 | 122.28 | 122.2329 | 122.158 | 122.0805 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2501 | 122.2677 | 122.1281 | 122.1457
2663.9219 | 122.3877 | -0.064087 | 122.2 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | -0.000359 | 0.085583 | -0.012357 | 122.2342 | 122.1917 | 122.1214 | 122.0393 | -0.025015 | 0.018642 | -0.033484 | 0.010563 | 0.16305 | 0.08767 | 0.04293 | 0.052806 | 0.063728 | 0.14967 | 0.05173 | 122.2754 | 122.2329 | 122.1626 | 122.0805 | 0.016184 | 0.059841 | 0.007715 | 0.051762 | 122.2592 | 122.2677 | 122.1464 | 122.1549
2665.6719 | 122.374 | -0.073242 | 122.1863 | 0.098959 | 0.009846 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.012357 | 122.2342 | 122.1917 | 122.126 | 122.0439 | -0.015859 | 0.02322 | -0.024328 | 0.005985 | 0.1722 | 0.083088 | 0.052085 | 0.057382 | 0.077461 | 0.15425 | 0.060885 | 122.2754 | 122.2329 | 122.1672 | 122.0851 | 0.02534 | 0.064419 | 0.016871 | 0.047184 | 122.2501 | 122.2585 | 122.1419 | 122.1503
2667.3594 | 122.3969 | -0.059509 | 122.1771 | 0.10354 | 0.014425 | -0.021157 | -0.01586 | 0.008797 | 0.090161 | -0.021514 | 122.2388 | 122.1963 | 122.1168 | 122.0302 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 0.16305 | 0.073934 | 0.038352 | 0.043649 | 0.068306 | 0.14967 | 0.037995 | 122.28 | 122.2375 | 122.158 | 122.0714 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 122.2501 | 122.2677 | 122.1281 | 122.1457
2669.1094 | 122.4335 | -0.064087 | 122.1954 | 0.089802 | 0.005267 | -0.025735 | -0.011281 | -0.000359 | 0.090161 | -0.016936 | 122.2388 | 122.178 | 122.1168 | 122.0393 | -0.015859 | 0.036954 | -0.028906 | 0.010563 | 0.15389 | 0.069354 | 0.038352 | 0.052806 | 0.063728 | 0.15425 | 0.047151 | 122.28 | 122.2192 | 122.158 | 122.0805 | 0.02534 | 0.078153 | 0.012293 | 0.051762 | 122.2546 | 122.2677 | 122.1327 | 122.1457
2670.8125 | 122.3785 | -0.07782 | 122.2046 | 0.098959 | 0.009846 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2479 | 122.1825 | 122.126 | 122.0485 | -0.011281 | 0.027798 | -0.038063 | 0.005985 | 0.17678 | 0.087666 | 0.056663 | 0.071117 | 0.082039 | 0.1634 | 0.060884 | 122.2891 | 122.2237 | 122.1672 | 122.0897 | 0.029918 | 0.068997 | 0.003136 | 0.047184 | 122.2592 | 122.286 | 122.1373 | 122.1641
2672.5625 | 122.3007 | -0.11902 | 122.2046 | 0.098959 | 0.019004 | -0.012 | -0.006703 | 0.004219 | 0.090161 | -0.016936 | 122.2434 | 122.1276 | 122.1306 | 122.0393 | -0.011281 | 0.018642 | -0.028906 | 0.001406 | 0.21798 | 0.13802 | 0.10702 | 0.11232 | 0.12324 | 0.20918 | 0.10208 | 122.2846 | 122.1688 | 122.1718 | 122.0805 | 0.029918 | 0.059841 | 0.012293 | 0.042605 | 122.2546 | 122.2723 | 122.1419 | 122.1595
2674.3125 | 122.3053 | -0.1236 | 122.2046 | 0.10354 | 0.019004 | -0.021157 | -0.002124 | 0.013375 | 0.090161 | -0.016936 | 122.2388 | 122.1322 | 122.126 | 122.0393 | -0.006702 | 0.032376 | -0.019749 | 0.005985 | 0.22713 | 0.1426 | 0.10244 | 0.12147 | 0.13697 | 0.21376 | 0.10666 | 122.28 | 122.1734 | 122.1672 | 122.0805 | 0.034497 | 0.073575 | 0.02145 | 0.047184 | 122.2455 | 122.2585 | 122.1327 | 122.1457
2676.0625 | 122.4106 | -0.036621 | 122.2 | 0.094381 | 0.009846 | -0.016578 | -0.020438 | -0.000359 | 0.085583 | -0.016936 | 122.2525 | 122.1276 | 122.1214 | 122.0485 | -0.011281 | 0.02322 | -0.028906 | 0.010563 | 0.131 | 0.046467 | 0.020043 | 0.016183 | 0.036262 | 0.1222 | 0.019685 | 122.2937 | 122.1688 | 122.1626 | 122.0897 | 0.029918 | 0.064419 | 0.012293 | 0.051762 | 122.2638 | 122.2814 | 122.1327 | 122.1503
2677.8125 | 122.3053 | -0.10986 | 122.2321 | 0.098959 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.2388 | 122.1276 | 122.1168 | 122.0347 | -0.011281 | 0.027798 | -0.019749 | 0.001406 | 0.20882 | 0.12887 | 0.093285 | 0.098582 | 0.11408 | 0.19545 | 0.097506 | 122.28 | 122.1688 | 122.158 | 122.0759 | 0.029918 | 0.068997 | 0.02145 | 0.042605 | 122.2501 | 122.2585 | 122.1281 | 122.1366
2679.5781 | 122.2824 | -0.091553 | 122.2183 | 0.10354 | 0.019004 | -0.021157 | -0.002124 | 0.008797 | 0.090161 | -0.007779 | 122.2388 | 122.1322 | 122.126 | 122.0439 | -0.020437 | 0.02322 | -0.028906 | 0.010563 | 0.19509 | 0.11056 | 0.070396 | 0.089429 | 0.10035 | 0.18171 | 0.083774 | 122.28 | 122.1734 | 122.1672 | 122.0851 | 0.020762 | 0.064419 | 0.012293 | 0.051762 | 122.2592 | 122.2677 | 122.1464 | 122.1549
2681.2812 | 122.406 | -0.054932 | 122.1909 | 0.094381 | 0.014425 | -0.016578 | -0.011281 | 0.004219 | 0.081005 | -0.016936 | 122.2525 | 122.1322 | 122.126 | 122.0347 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.14931 | 0.069357 | 0.038354 | 0.043651 | 0.059151 | 0.13594 | 0.037996 | 122.2937 | 122.1734 | 122.1672 | 122.0759 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.2638 | 122.286 | 122.1373 | 122.1595
2682.9844 | 122.3831 | -0.064087 | 122.1771 | 0.10354 | 0.014425 | -0.025735 | -0.011281 | -0.000359 | 0.076426 | -0.016936 | 122.2434 | 122.123 | 122.126 | 122.0439 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.16762 | 0.078512 | 0.038352 | 0.052806 | 0.063728 | 0.14051 | 0.047151 | 122.2846 | 122.1642 | 122.1672 | 122.0851 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.2546 | 122.2677 | 122.1373 | 122.1503
2684.7344 | 122.2916 | -0.10071 | 122.2366 | 0.094381 | 0.023583 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.2342 | 122.1367 | 122.1214 | 122.0439 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.19509 | 0.12429 | 0.079551 | 0.094005 | 0.11408 | 0.19087 | 0.088351 | 122.2754 | 122.1779 | 122.1626 | 122.0851 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2455 | 122.2677 | 122.1327 | 122.1549
2686.4844 | 122.3785 | -0.068665 | 122.1863 | 0.089802 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.2342 | 122.1276 | 122.1214 | 122.0393 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.15847 | 0.08309 | 0.047508 | 0.057384 | 0.077462 | 0.15425 | 0.056308 | 122.2754 | 122.1688 | 122.1626 | 122.0805 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2455 | 122.2631 | 122.1327 | 122.1503
2688.1719 | 122.4014 | -0.059509 | 122.2046 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | -0.000359 | 0.081005 | -0.012357 | 122.2434 | 122.1322 | 122.126 | 122.0439 | -0.011281 | 0.036954 | -0.024328 | 0.001406 | 0.15847 | 0.078513 | 0.033774 | 0.043649 | 0.05915 | 0.14051 | 0.047152 | 122.2846 | 122.1734 | 122.1672 | 122.0851 | 0.029918 | 0.078153 | 0.016871 | 0.042605 | 122.2546 | 122.2677 | 122.1373 | 122.1503
2689.9375 | 122.3877 | -0.054932 | 122.1954 | 0.089802 | 0.019004 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2434 | 122.1322 | 122.1306 | 122.0347 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.14473 | 0.073936 | 0.033775 | 0.048229 | 0.059151 | 0.14052 | 0.037996 | 122.2846 | 122.1734 | 122.1718 | 122.0759 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.2592 | 122.2769 | 122.1464 | 122.1641
2691.6875 | 122.3236 | -0.091553 | 122.2092 | 0.10354 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.007779 | 122.2434 | 122.1276 | 122.1306 | 122.0439 | -0.020437 | 0.02322 | -0.033484 | -0.00775 | 0.19509 | 0.11514 | 0.070396 | 0.080272 | 0.095772 | 0.17714 | 0.083774 | 122.2846 | 122.1688 | 122.1718 | 122.0851 | 0.020762 | 0.064419 | 0.007715 | 0.033449 | 122.2638 | 122.2769 | 122.151 | 122.1641
2693.375 | 122.3007 | -0.091553 | 122.2 | 0.10354 | 0.023583 | -0.025735 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.2434 | 122.1367 | 122.1306 | 122.0347 | -0.020437 | 0.032376 | -0.033484 | -0.003172 | 0.19509 | 0.11514 | 0.065818 | 0.08485 | 0.10035 | 0.17714 | 0.079196 | 122.2846 | 122.1779 | 122.1718 | 122.0759 | 0.020762 | 0.073575 | 0.007715 | 0.038027 | 122.2638 | 122.2769 | 122.151 | 122.1641
2695.1406 | 122.287 | -0.11444 | 122.2412 | 0.098959 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.085583 | -0.021514 | 122.2434 | 122.1276 | 122.1214 | 122.0485 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.2134 | 0.13345 | 0.097863 | 0.10774 | 0.12782 | 0.20002 | 0.092927 | 122.2846 | 122.1688 | 122.1626 | 122.0897 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.2546 | 122.2769 | 122.1327 | 122.1549
2696.8281 | 122.3511 | -0.09613 | 122.2137 | 0.094381 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.081005 | -0.012357 | 122.2434 | 122.1367 | 122.1351 | 122.0393 | -0.020437 | 0.032376 | -0.024328 | 0.005985 | 0.19051 | 0.11971 | 0.074973 | 0.084849 | 0.1095 | 0.17713 | 0.083773 | 122.2846 | 122.1779 | 122.1763 | 122.0805 | 0.020762 | 0.073575 | 0.016871 | 0.047184 | 122.2638 | 122.2677 | 122.1556 | 122.1595
2698.5781 | 122.3877 | -0.059509 | 122.2137 | 0.098959 | 0.019004 | -0.030314 | -0.011281 | 0.008797 | 0.081005 | -0.007779 | 122.2479 | 122.1367 | 122.1306 | 122.0485 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.15847 | 0.078513 | 0.029195 | 0.048228 | 0.068306 | 0.14051 | 0.05173 | 122.2891 | 122.1779 | 122.1718 | 122.0897 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.2638 | 122.2814 | 122.1464 | 122.1641
2700.3281 | 122.3969 | -0.064087 | 122.2046 | 0.098959 | 0.014425 | -0.021157 | -0.011281 | 0.013375 | 0.090161 | -0.012357 | 122.2434 | 122.1322 | 122.126 | 122.0393 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 0.16305 | 0.078512 | 0.04293 | 0.052806 | 0.077462 | 0.15425 | 0.05173 | 122.2846 | 122.1734 | 122.1672 | 122.0805 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.2638 | 122.2723 | 122.1464 | 122.1549
2702.0938 | 122.3831 | -0.068665 | 122.1909 | 0.098959 | 0.014425 | -0.016578 | -0.01586 | 0.004219 | 0.081005 | -0.016936 | 122.2434 | 122.1367 | 122.126 | 122.0485 | -0.020437 | 0.027798 | -0.033484 | 0.001406 | 0.16762 | 0.08309 | 0.052087 | 0.052805 | 0.072884 | 0.14967 | 0.051729 | 122.2846 | 122.1779 | 122.1672 | 122.0897 | 0.020762 | 0.068997 | 0.007715 | 0.042605 | 122.2638 | 122.2769 | 122.1464 | 122.1595
2703.8594 | 122.4289 | -0.068665 | 122.1817 | 0.098959 | 0.014425 | -0.025735 | -0.006703 | -0.000359 | 0.081005 | -0.012357 | 122.2434 | 122.1367 | 122.1306 | 122.0439 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.16762 | 0.08309 | 0.04293 | 0.061962 | 0.068306 | 0.14967 | 0.056308 | 122.2846 | 122.1779 | 122.1718 | 122.0851 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.2592 | 122.2723 | 122.1464 | 122.1595
2705.625 | 122.4289 | -0.059509 | 122.1771 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | -0.004937 | 0.085583 | -0.021514 | 122.2479 | 122.1367 | 122.1306 | 122.0393 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.15847 | 0.078513 | 0.033774 | 0.043649 | 0.054572 | 0.14509 | 0.037995 | 122.2891 | 122.1779 | 122.1718 | 122.0805 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.2684 | 122.2814 | 122.151 | 122.1641
2707.375 | 122.3831 | -0.054932 | 122.2092 | 0.098959 | 0.009846 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.007779 | 122.2479 | 122.1413 | 122.126 | 122.0393 | -0.011281 | 0.027798 | -0.024328 | 0.001406 | 0.15389 | 0.064778 | 0.033775 | 0.039072 | 0.059151 | 0.14052 | 0.047153 | 122.2891 | 122.1825 | 122.1672 | 122.0805 | 0.029918 | 0.068997 | 0.016871 | 0.042605 | 122.2592 | 122.2723 | 122.1373 | 122.1503
2709.125 | 122.319 | -0.086975 | 122.2321 | 0.10354 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.090161 | -0.012357 | 122.2525 | 122.1367 | 122.126 | 122.0485 | -0.015859 | 0.032376 | -0.024328 | 0.005985 | 0.19051 | 0.11056 | 0.065818 | 0.080272 | 0.095772 | 0.17714 | 0.074618 | 122.2937 | 122.1779 | 122.1672 | 122.0897 | 0.02534 | 0.073575 | 0.016871 | 0.047184 | 122.2684 | 122.2769 | 122.1419 | 122.1503
2710.8125 | 122.4014 | -0.050354 | 122.1909 | 0.094381 | 0.014425 | -0.016578 | -0.002124 | -0.000359 | 0.085583 | -0.012357 | 122.2479 | 122.1322 | 122.1306 | 122.0485 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.14474 | 0.064779 | 0.033776 | 0.04823 | 0.049995 | 0.13594 | 0.037997 | 122.2891 | 122.1734 | 122.1718 | 122.0897 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.2638 | 122.2769 | 122.1464 | 122.1595
2712.5625 | 122.2916 | -0.09613 | 122.2183 | 0.098959 | 0.023583 | -0.012 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2525 | 122.1413 | 122.1306 | 122.0485 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.19509 | 0.11971 | 0.08413 | 0.089427 | 0.10493 | 0.19087 | 0.088351 | 122.2937 | 122.1825 | 122.1718 | 122.0897 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2638 | 122.286 | 122.1419 | 122.1641
2714.3125 | 122.3969 | -0.050354 | 122.2183 | 0.094381 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 122.2479 | 122.1322 | 122.1306 | 122.0393 | -0.006702 | 0.027798 | -0.024328 | 0.010563 | 0.14474 | 0.073937 | 0.033776 | 0.039073 | 0.054573 | 0.13594 | 0.033418 | 122.2891 | 122.1734 | 122.1718 | 122.0805 | 0.034497 | 0.068997 | 0.016871 | 0.051762 | 122.2546 | 122.2723 | 122.1373 | 122.1549
2716 | 122.3145 | -0.082397 | 122.2275 | 0.098959 | 0.028162 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 122.2525 | 122.1413 | 122.1306 | 122.053 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.18136 | 0.11056 | 0.070397 | 0.080273 | 0.091194 | 0.1634 | 0.07004 | 122.2937 | 122.1825 | 122.1718 | 122.0942 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.2684 | 122.2769 | 122.1464 | 122.1549
2717.75 | 122.3694 | -0.082397 | 122.2 | 0.094381 | 0.023583 | -0.025735 | -0.01586 | -0.000359 | 0.081005 | -0.012357 | 122.2479 | 122.1367 | 122.1351 | 122.0485 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.17678 | 0.10598 | 0.056662 | 0.066537 | 0.082038 | 0.1634 | 0.07004 | 122.2891 | 122.1779 | 122.1763 | 122.0897 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.2592 | 122.2769 | 122.1464 | 122.1641
2719.4531 | 122.3785 | -0.064087 | 122.1954 | 0.094381 | 0.023583 | -0.030314 | -0.006703 | 0.004219 | 0.076426 | -0.012357 | 122.2434 | 122.1413 | 122.1351 | 122.0439 | -0.011281 | 0.027798 | -0.042641 | -0.003172 | 0.15847 | 0.08767 | 0.033773 | 0.057384 | 0.068306 | 0.14051 | 0.05173 | 122.2846 | 122.1825 | 122.1763 | 122.0851 | 0.029918 | 0.068997 | -0.001442 | 0.038027 | 122.2546 | 122.286 | 122.1464 | 122.1778
2721.2188 | 122.3328 | -0.10986 | 122.2412 | 0.098959 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.090161 | -0.007779 | 122.2479 | 122.1459 | 122.1306 | 122.053 | -0.015859 | 0.02322 | -0.038063 | 0.010563 | 0.20882 | 0.13345 | 0.093285 | 0.098582 | 0.11408 | 0.20002 | 0.10208 | 122.2891 | 122.1871 | 122.1718 | 122.0942 | 0.02534 | 0.064419 | 0.003136 | 0.051762 | 122.2638 | 122.286 | 122.1464 | 122.1686
2722.9688 | 122.4289 | -0.073242 | 122.2046 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | 0.013375 | 0.081005 | -0.016936 | 122.2479 | 122.1322 | 122.1351 | 122.0439 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.1722 | 0.092246 | 0.047507 | 0.057382 | 0.086617 | 0.15425 | 0.056306 | 122.2891 | 122.1734 | 122.1763 | 122.0851 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2638 | 122.2769 | 122.151 | 122.1641
2724.7344 | 122.374 | -0.059509 | 122.1863 | 0.10354 | 0.014425 | -0.021157 | -0.006703 | -0.000359 | 0.081005 | -0.012357 | 122.2525 | 122.1367 | 122.1306 | 122.0439 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.16305 | 0.073934 | 0.038352 | 0.052806 | 0.05915 | 0.14051 | 0.047152 | 122.2937 | 122.1779 | 122.1718 | 122.0851 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.2684 | 122.2814 | 122.1464 | 122.1595
2726.4375 | 122.3373 | -0.10071 | 122.2412 | 0.098959 | 0.023583 | -0.021157 | -0.006703 | 0.004219 | 0.090161 | -0.007779 | 122.2479 | 122.1413 | 122.1443 | 122.053 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.19967 | 0.12429 | 0.079551 | 0.094005 | 0.10493 | 0.19087 | 0.092929 | 122.2891 | 122.1825 | 122.1855 | 122.0942 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.2684 | 122.2814 | 122.1647 | 122.1778
2728.1875 | 122.4701 | -0.068665 | 122.2092 | 0.094381 | 0.014425 | -0.025735 | -0.01586 | -0.000359 | 0.085583 | -0.016936 | 122.2571 | 122.1322 | 122.1306 | 122.0439 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 0.16305 | 0.08309 | 0.04293 | 0.052805 | 0.068306 | 0.15425 | 0.051729 | 122.2983 | 122.1734 | 122.1718 | 122.0851 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 122.2638 | 122.2906 | 122.1373 | 122.1641
2729.9531 | 122.4518 | -0.073242 | 122.2229 | 0.098959 | 0.014425 | -0.021157 | -0.020438 | 0.004219 | 0.085583 | -0.012357 | 122.2479 | 122.1322 | 122.1306 | 122.0439 | -0.025015 | 0.032376 | -0.038063 | 0.001406 | 0.1722 | 0.087667 | 0.052085 | 0.052804 | 0.077461 | 0.15882 | 0.060885 | 122.2891 | 122.1734 | 122.1718 | 122.0851 | 0.016184 | 0.073575 | 0.003136 | 0.042605 | 122.273 | 122.286 | 122.1556 | 122.1686
2731.7188 | 122.3007 | -0.09613 | 122.2412 | 0.098959 | 0.019004 | -0.025735 | -0.006703 | 0.013375 | 0.085583 | -0.016936 | 122.2617 | 122.1367 | 122.1306 | 122.0439 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.19509 | 0.11513 | 0.070395 | 0.089427 | 0.1095 | 0.18171 | 0.079194 | 122.3029 | 122.1779 | 122.1718 | 122.0851 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.273 | 122.2906 | 122.1419 | 122.1595
2733.4062 | 122.4197 | -0.068665 | 122.1817 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | -0.000359 | 0.090161 | -0.012357 | 122.2479 | 122.1413 | 122.1397 | 122.0485 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.16762 | 0.087669 | 0.04293 | 0.052805 | 0.068306 | 0.15883 | 0.056308 | 122.2891 | 122.1825 | 122.1809 | 122.0897 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.2638 | 122.2814 | 122.1556 | 122.1732
2735.1562 | 122.3053 | -0.10986 | 122.2458 | 0.098959 | 0.019004 | -0.021157 | -0.006703 | -0.000359 | 0.09474 | -0.012357 | 122.2434 | 122.1459 | 122.1397 | 122.053 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.20882 | 0.12887 | 0.088706 | 0.10316 | 0.1095 | 0.2046 | 0.097506 | 122.2846 | 122.1871 | 122.1809 | 122.0942 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.2592 | 122.2677 | 122.1556 | 122.1641
2736.9062 | 122.3282 | -0.09613 | 122.2595 | 0.10354 | 0.028162 | -0.021157 | -0.01586 | -0.000359 | 0.085583 | -0.016936 | 122.2525 | 122.1413 | 122.1351 | 122.053 | -0.020437 | 0.032376 | -0.038063 | 0.005985 | 0.19967 | 0.12429 | 0.074973 | 0.08027 | 0.095771 | 0.18171 | 0.079194 | 122.2937 | 122.1825 | 122.1763 | 122.0942 | 0.020762 | 0.073575 | 0.003136 | 0.047184 | 122.273 | 122.2906 | 122.1556 | 122.1732
2738.6562 | 122.3465 | -0.10071 | 122.2183 | 0.10354 | 0.028162 | -0.016578 | -0.011281 | 0.004219 | 0.09474 | -0.016936 | 122.2479 | 122.1459 | 122.1351 | 122.0485 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.20425 | 0.12887 | 0.08413 | 0.089427 | 0.10493 | 0.19545 | 0.083772 | 122.2891 | 122.1871 | 122.1763 | 122.0897 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2592 | 122.2814 | 122.1464 | 122.1686
2740.3438 | 122.3602 | -0.086975 | 122.1863 | 0.098959 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.090161 | -0.012357 | 122.2525 | 122.1276 | 122.1351 | 122.0393 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.18593 | 0.10598 | 0.070397 | 0.080272 | 0.095772 | 0.17714 | 0.074618 | 122.2937 | 122.1688 | 122.1763 | 122.0805 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.2684 | 122.2906 | 122.151 | 122.1732
2742.1094 | 122.4472 | -0.054932 | 122.1771 | 0.098959 | 0.014425 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.016936 | 122.2525 | 122.1367 | 122.1351 | 122.0485 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.15389 | 0.069357 | 0.033775 | 0.043651 | 0.059151 | 0.13594 | 0.037996 | 122.2937 | 122.1779 | 122.1763 | 122.0897 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.2638 | 122.2814 | 122.1464 | 122.1641
2743.8594 | 122.3877 | -0.064087 | 122.2092 | 0.10354 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.076426 | -0.007779 | 122.2479 | 122.1413 | 122.1351 | 122.0485 | -0.020437 | 0.032376 | -0.028906 | 0.001406 | 0.16762 | 0.083091 | 0.04293 | 0.052806 | 0.077462 | 0.14051 | 0.056308 | 122.2891 | 122.1825 | 122.1763 | 122.0897 | 0.020762 | 0.073575 | 0.012293 | 0.042605 | 122.2684 | 122.2769 | 122.1556 | 122.1641
2745.625 | 122.3419 | -0.091553 | 122.2595 | 0.10354 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.007779 | 122.2525 | 122.1413 | 122.1351 | 122.053 | -0.015859 | 0.027798 | -0.019749 | 0.001406 | 0.19509 | 0.11056 | 0.074975 | 0.080272 | 0.095772 | 0.17714 | 0.083774 | 122.2937 | 122.1825 | 122.1763 | 122.0942 | 0.02534 | 0.068997 | 0.02145 | 0.042605 | 122.2684 | 122.2723 | 122.151 | 122.1549
2747.3125 | 122.319 | -0.10529 | 122.2595 | 0.098959 | 0.019004 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 122.2571 | 122.1413 | 122.1397 | 122.0485 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.20425 | 0.12429 | 0.088708 | 0.089426 | 0.10951 | 0.19087 | 0.092929 | 122.2983 | 122.1825 | 122.1809 | 122.0897 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2684 | 122.286 | 122.151 | 122.1686
2749.0781 | 122.3511 | -0.086975 | 122.2183 | 0.10354 | 0.019004 | -0.016578 | -0.002124 | 0.004219 | 0.090161 | -0.016936 | 122.2571 | 122.1413 | 122.1351 | 122.053 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.19051 | 0.10598 | 0.070397 | 0.084851 | 0.091194 | 0.17714 | 0.070039 | 122.2983 | 122.1825 | 122.1763 | 122.0942 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.2684 | 122.2906 | 122.1464 | 122.1686
2750.8438 | 122.438 | -0.045776 | 122.1909 | 0.094381 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.021514 | 122.2479 | 122.1367 | 122.1351 | 122.0393 | -0.011281 | 0.032376 | -0.024328 | 0.001406 | 0.14016 | 0.060201 | 0.029198 | 0.034495 | 0.054573 | 0.12678 | 0.024262 | 122.2891 | 122.1779 | 122.1763 | 122.0805 | 0.029918 | 0.073575 | 0.016871 | 0.042605 | 122.2592 | 122.2723 | 122.1464 | 122.1595
2752.5312 | 122.3694 | -0.073242 | 122.2046 | 0.10354 | 0.014425 | -0.021157 | -0.01586 | 0.013375 | 0.081005 | -0.007779 | 122.2479 | 122.1413 | 122.1351 | 122.0439 | -0.011281 | 0.02322 | -0.024328 | 0.001406 | 0.17678 | 0.087667 | 0.052085 | 0.057382 | 0.086617 | 0.15425 | 0.065463 | 122.2891 | 122.1825 | 122.1763 | 122.0851 | 0.029918 | 0.064419 | 0.016871 | 0.042605 | 122.2592 | 122.2723 | 122.1464 | 122.1595
2754.2812 | 122.3145 | -0.09613 | 122.2275 | 0.10354 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.2434 | 122.1367 | 122.1397 | 122.0485 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.19967 | 0.11971 | 0.074973 | 0.084849 | 0.10493 | 0.18171 | 0.083773 | 122.2846 | 122.1779 | 122.1809 | 122.0897 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.2592 | 122.2677 | 122.1556 | 122.1641
2755.9844 | 122.3007 | -0.10071 | 122.2366 | 0.10812 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2525 | 122.1459 | 122.1397 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.20882 | 0.11971 | 0.08413 | 0.094005 | 0.10951 | 0.19545 | 0.092929 | 122.2937 | 122.1871 | 122.1809 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.273 | 122.286 | 122.1602 | 122.1732
2757.7344 | 122.3099 | -0.1236 | 122.2 | 0.10354 | 0.014425 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.012357 | 122.2571 | 122.1413 | 122.1351 | 122.0485 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.22713 | 0.13802 | 0.10244 | 0.11689 | 0.12781 | 0.20918 | 0.11124 | 122.2983 | 122.1825 | 122.1763 | 122.0897 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2684 | 122.2906 | 122.1464 | 122.1686
2759.4219 | 122.4197 | -0.059509 | 122.2092 | 0.10354 | 0.023583 | -0.021157 | -0.020438 | 0.008797 | 0.090161 | -0.016936 | 122.2479 | 122.1367 | 122.1397 | 122.0439 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.16305 | 0.083092 | 0.038352 | 0.039071 | 0.068306 | 0.14967 | 0.042573 | 122.2891 | 122.1779 | 122.1809 | 122.0851 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.2638 | 122.286 | 122.1556 | 122.1778
2761.1875 | 122.3236 | -0.086975 | 122.2229 | 0.098959 | 0.019004 | -0.021157 | -0.011281 | -0.000359 | 0.09474 | -0.016936 | 122.2479 | 122.1459 | 122.1397 | 122.0576 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.18593 | 0.10598 | 0.065818 | 0.075694 | 0.086616 | 0.18172 | 0.070039 | 122.2891 | 122.1871 | 122.1809 | 122.0988 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2592 | 122.2814 | 122.151 | 122.1732
2762.9375 | 122.4243 | -0.054932 | 122.2092 | 0.098959 | 0.019004 | -0.025735 | -0.011281 | 0.008797 | 0.081005 | -0.016936 | 122.2571 | 122.1367 | 122.1397 | 122.0485 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.15389 | 0.073936 | 0.029197 | 0.043651 | 0.063729 | 0.13594 | 0.037996 | 122.2983 | 122.1779 | 122.1809 | 122.0897 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.2684 | 122.286 | 122.151 | 122.1686
2764.6875 | 122.4289 | -0.054932 | 122.1909 | 0.094381 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.2525 | 122.1413 | 122.1397 | 122.0393 | -0.011281 | 0.018642 | -0.024328 | 0.001406 | 0.14931 | 0.078515 | 0.033775 | 0.043651 | 0.063729 | 0.14052 | 0.042575 | 122.2937 | 122.1825 | 122.1809 | 122.0805 | 0.029918 | 0.059841 | 0.016871 | 0.042605 | 122.2638 | 122.2769 | 122.151 | 122.1641
2766.375 | 122.438 | -0.064087 | 122.1954 | 0.10354 | 0.014425 | -0.021157 | -0.011281 | -0.000359 | 0.085583 | -0.021514 | 122.2525 | 122.1413 | 122.1443 | 122.0485 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.16762 | 0.078512 | 0.04293 | 0.052806 | 0.063728 | 0.14967 | 0.042573 | 122.2937 | 122.1825 | 122.1855 | 122.0897 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.2684 | 122.286 | 122.1602 | 122.1778
2768.125 | 122.406 | -0.059509 | 122.2046 | 0.10354 | 0.014425 | -0.025735 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 122.2525 | 122.1367 | 122.1443 | 122.053 | -0.015859 | 0.018642 | -0.033484 | -0.003172 | 0.16305 | 0.073934 | 0.033774 | 0.048228 | 0.072884 | 0.14967 | 0.042573 | 122.2937 | 122.1779 | 122.1855 | 122.0942 | 0.02534 | 0.059841 | 0.007715 | 0.038027 | 122.2684 | 122.286 | 122.1602 | 122.1778
2769.8125 | 122.3511 | -0.091553 | 122.2504 | 0.098959 | 0.028162 | -0.021157 | -0.020438 | 0.008797 | 0.090161 | -0.016936 | 122.2571 | 122.1459 | 122.1397 | 122.053 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.19051 | 0.11971 | 0.070396 | 0.071115 | 0.10035 | 0.18171 | 0.074617 | 122.2983 | 122.1871 | 122.1809 | 122.0942 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.273 | 122.286 | 122.1556 | 122.1686
2771.5625 | 122.3694 | -0.068665 | 122.2137 | 0.098959 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.016936 | 122.2571 | 122.1459 | 122.1397 | 122.0485 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.16762 | 0.087669 | 0.052087 | 0.057384 | 0.077462 | 0.15883 | 0.051729 | 122.2983 | 122.1871 | 122.1809 | 122.0897 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2684 | 122.2906 | 122.151 | 122.1732
2773.25 | 122.3785 | -0.073242 | 122.2092 | 0.098959 | 0.023583 | -0.025735 | -0.020438 | 0.008797 | 0.081005 | -0.021514 | 122.2571 | 122.1413 | 122.1351 | 122.0485 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.1722 | 0.096825 | 0.047507 | 0.052804 | 0.082039 | 0.15425 | 0.051728 | 122.2983 | 122.1825 | 122.1763 | 122.0897 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.2684 | 122.2906 | 122.1464 | 122.1686
2775 | 122.406 | -0.064087 | 122.1863 | 0.10812 | 0.023583 | -0.021157 | -0.01586 | -0.000359 | 0.085583 | -0.012357 | 122.2525 | 122.1367 | 122.1351 | 122.0485 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.1722 | 0.08767 | 0.04293 | 0.048227 | 0.063728 | 0.14967 | 0.05173 | 122.2937 | 122.1779 | 122.1763 | 122.0897 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.273 | 122.286 | 122.1556 | 122.1686
2776.7656 | 122.4243 | -0.068665 | 122.1909 | 0.094381 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.090161 | -0.016936 | 122.2571 | 122.1413 | 122.1443 | 122.0485 | -0.020437 | 0.02322 | -0.028906 | 0.005985 | 0.16305 | 0.092248 | 0.052087 | 0.052805 | 0.077462 | 0.15883 | 0.051729 | 122.2983 | 122.1825 | 122.1855 | 122.0897 | 0.020762 | 0.064419 | 0.012293 | 0.047184 | 122.2775 | 122.286 | 122.1647 | 122.1732
2778.4531 | 122.3785 | -0.054932 | 122.2046 | 0.094381 | 0.014425 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.2617 | 122.1367 | 122.1397 | 122.0439 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.14931 | 0.069357 | 0.038354 | 0.043651 | 0.063729 | 0.14052 | 0.042575 | 122.3029 | 122.1779 | 122.1809 | 122.0851 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2775 | 122.2906 | 122.1556 | 122.1686
2780.2031 | 122.3877 | -0.068665 | 122.2092 | 0.10354 | 0.019004 | -0.021157 | -0.01586 | 0.004219 | 0.081005 | -0.012357 | 122.2617 | 122.1459 | 122.1397 | 122.0439 | -0.015859 | 0.027798 | -0.042641 | 0.005985 | 0.1722 | 0.087669 | 0.047508 | 0.052805 | 0.072884 | 0.14967 | 0.056308 | 122.3029 | 122.1871 | 122.1809 | 122.0851 | 0.02534 | 0.068997 | -0.001442 | 0.047184 | 122.2775 | 122.3043 | 122.1556 | 122.1824
2781.9688 | 122.3602 | -0.086975 | 122.2137 | 0.098959 | 0.023583 | -0.021157 | -0.002124 | -0.000359 | 0.085583 | -0.012357 | 122.2617 | 122.1459 | 122.1535 | 122.0393 | -0.015859 | 0.02322 | -0.024328 | 0.010563 | 0.18593 | 0.11056 | 0.065818 | 0.084851 | 0.086616 | 0.17256 | 0.074618 | 122.3029 | 122.1871 | 122.1947 | 122.0805 | 0.02534 | 0.064419 | 0.016871 | 0.051762 | 122.2775 | 122.286 | 122.1693 | 122.1778
2783.7344 | 122.4289 | -0.050354 | 122.2092 | 0.098959 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.085583 | -0.026092 | 122.2571 | 122.1459 | 122.1397 | 122.0393 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.14931 | 0.069358 | 0.029197 | 0.034494 | 0.059151 | 0.13594 | 0.024262 | 122.2983 | 122.1871 | 122.1809 | 122.0805 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2684 | 122.2906 | 122.151 | 122.1732
2785.4219 | 122.3328 | -0.07782 | 122.2366 | 0.10354 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.021514 | 122.2617 | 122.1367 | 122.1443 | 122.0393 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 0.18136 | 0.1014 | 0.061242 | 0.06196 | 0.082039 | 0.1634 | 0.056306 | 122.3029 | 122.1779 | 122.1855 | 122.0805 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.2821 | 122.2906 | 122.1647 | 122.1732
2787.1875 | 122.3145 | -0.1236 | 122.2275 | 0.098959 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.085583 | -0.012357 | 122.2617 | 122.1551 | 122.1443 | 122.053 | -0.011281 | 0.02322 | -0.024328 | 0.010563 | 0.22256 | 0.14718 | 0.10702 | 0.11689 | 0.12781 | 0.20918 | 0.11124 | 122.3029 | 122.1963 | 122.1855 | 122.0942 | 0.029918 | 0.064419 | 0.016871 | 0.051762 | 122.273 | 122.286 | 122.1556 | 122.1686
2788.875 | 122.3236 | -0.10071 | 122.2137 | 0.094381 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.007779 | 122.2617 | 122.1459 | 122.1443 | 122.053 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.19509 | 0.11971 | 0.079551 | 0.089427 | 0.10951 | 0.18629 | 0.092929 | 122.3029 | 122.1871 | 122.1855 | 122.0942 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.2775 | 122.2906 | 122.1602 | 122.1732
2790.625 | 122.3923 | -0.059509 | 122.2137 | 0.094381 | 0.028162 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 122.2525 | 122.1505 | 122.1397 | 122.0576 | -0.025015 | 0.027798 | -0.019749 | 0.001406 | 0.15389 | 0.087671 | 0.038352 | 0.043649 | 0.063728 | 0.14509 | 0.047152 | 122.2937 | 122.1917 | 122.1809 | 122.0988 | 0.016184 | 0.068997 | 0.02145 | 0.042605 | 122.2775 | 122.2723 | 122.1647 | 122.1595
2792.3125 | 122.4197 | -0.064087 | 122.2275 | 0.085224 | 0.014425 | -0.025735 | -0.011281 | 0.004219 | 0.090161 | -0.016936 | 122.2617 | 122.1413 | 122.1489 | 122.0485 | -0.020437 | 0.02322 | -0.028906 | -0.00775 | 0.14931 | 0.078512 | 0.038352 | 0.052806 | 0.068306 | 0.15425 | 0.047151 | 122.3029 | 122.1825 | 122.1901 | 122.0897 | 0.020762 | 0.064419 | 0.012293 | 0.033449 | 122.2821 | 122.2906 | 122.1693 | 122.1778
2794.0625 | 122.3923 | -0.064087 | 122.2183 | 0.094381 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2571 | 122.1596 | 122.1397 | 122.0439 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 0.15847 | 0.08767 | 0.047509 | 0.057384 | 0.068306 | 0.14967 | 0.047151 | 122.2983 | 122.2008 | 122.1809 | 122.0851 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.2775 | 122.286 | 122.1602 | 122.1686
2795.8125 | 122.438 | -0.059509 | 122.1817 | 0.098959 | 0.019004 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.016936 | 122.2617 | 122.1413 | 122.1443 | 122.0485 | -0.020437 | 0.018642 | -0.033484 | 0.001406 | 0.15847 | 0.078513 | 0.038352 | 0.043649 | 0.063728 | 0.14967 | 0.042573 | 122.3029 | 122.1825 | 122.1855 | 122.0897 | 0.020762 | 0.059841 | 0.007715 | 0.042605 | 122.2821 | 122.2952 | 122.1647 | 122.1778
2797.5 | 122.3373 | -0.09613 | 122.2229 | 0.094381 | 0.019004 | -0.021157 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2571 | 122.1505 | 122.1443 | 122.053 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.19051 | 0.11513 | 0.074973 | 0.089427 | 0.10035 | 0.18629 | 0.083773 | 122.2983 | 122.1917 | 122.1855 | 122.0942 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.2775 | 122.286 | 122.1647 | 122.1732
2799.2656 | 122.3419 | -0.073242 | 122.2321 | 0.094381 | 0.019004 | -0.021157 | -0.011281 | 0.004219 | 0.09474 | -0.012357 | 122.2663 | 122.1459 | 122.1397 | 122.0485 | -0.006702 | 0.018642 | -0.028906 | 0.005985 | 0.16762 | 0.092246 | 0.052085 | 0.061961 | 0.077461 | 0.16798 | 0.060885 | 122.3075 | 122.1871 | 122.1809 | 122.0897 | 0.034497 | 0.059841 | 0.012293 | 0.047184 | 122.273 | 122.2952 | 122.1464 | 122.1686
2801.0312 | 122.3007 | -0.10986 | 122.2321 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 122.2571 | 122.1459 | 122.1489 | 122.0485 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.20882 | 0.13345 | 0.088706 | 0.098582 | 0.11866 | 0.20002 | 0.097506 | 122.2983 | 122.1871 | 122.1901 | 122.0897 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.273 | 122.2906 | 122.1647 | 122.1824
2802.7812 | 122.3511 | -0.086975 | 122.2229 | 0.094381 | 0.019004 | -0.025735 | -0.006703 | 0.008797 | 0.085583 | -0.003201 | 122.2617 | 122.1459 | 122.1443 | 122.0576 | -0.015859 | 0.018642 | -0.024328 | -0.003172 | 0.18136 | 0.10598 | 0.06124 | 0.080272 | 0.095772 | 0.17256 | 0.083774 | 122.3029 | 122.1871 | 122.1855 | 122.0988 | 0.02534 | 0.059841 | 0.016871 | 0.038027 | 122.2775 | 122.286 | 122.1602 | 122.1686
2804.5312 | 122.3465 | -0.086975 | 122.2641 | 0.098959 | 0.023583 | -0.012 | -0.006703 | 0.013375 | 0.081005 | -0.007779 | 122.2663 | 122.1505 | 122.1535 | 122.053 | -0.020437 | 0.02322 | -0.019749 | 0.001406 | 0.18593 | 0.11056 | 0.074975 | 0.080272 | 0.10035 | 0.16798 | 0.079196 | 122.3075 | 122.1917 | 122.1947 | 122.0942 | 0.020762 | 0.064419 | 0.02145 | 0.042605 | 122.2867 | 122.286 | 122.1739 | 122.1732
2806.2969 | 122.4152 | -0.054932 | 122.1954 | 0.10354 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.2571 | 122.1505 | 122.1489 | 122.0485 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.15847 | 0.078515 | 0.038354 | 0.043651 | 0.059151 | 0.14052 | 0.042575 | 122.2983 | 122.1917 | 122.1901 | 122.0897 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.273 | 122.286 | 122.1647 | 122.1778
2808 | 122.3831 | -0.041199 | 122.1863 | 0.098959 | 0.019004 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.2617 | 122.1505 | 122.1397 | 122.0485 | -0.006702 | 0.018642 | -0.024328 | 0.001406 | 0.14016 | 0.060203 | 0.020042 | 0.034496 | 0.049996 | 0.12678 | 0.028842 | 122.3029 | 122.1917 | 122.1809 | 122.0897 | 0.034497 | 0.059841 | 0.016871 | 0.042605 | 122.2684 | 122.286 | 122.1464 | 122.1641
2809.6875 | 122.3145 | -0.10071 | 122.2641 | 0.098959 | 0.028162 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.2617 | 122.1505 | 122.1443 | 122.0485 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.19967 | 0.12887 | 0.079551 | 0.089427 | 0.10493 | 0.18629 | 0.088351 | 122.3029 | 122.1917 | 122.1855 | 122.0897 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2775 | 122.2906 | 122.1602 | 122.1732
2811.4375 | 122.4701 | -0.054932 | 122.2183 | 0.098959 | 0.019004 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.021514 | 122.2571 | 122.1505 | 122.1443 | 122.0485 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.15389 | 0.073936 | 0.038354 | 0.043651 | 0.059151 | 0.14052 | 0.033418 | 122.2983 | 122.1917 | 122.1855 | 122.0897 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.273 | 122.2814 | 122.1602 | 122.1686
2813.1875 | 122.3145 | -0.09613 | 122.2321 | 0.10354 | 0.019004 | -0.012 | -0.002124 | 0.008797 | 0.085583 | -0.016936 | 122.2571 | 122.1551 | 122.1489 | 122.053 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.19967 | 0.11513 | 0.08413 | 0.094006 | 0.10493 | 0.18171 | 0.079194 | 122.2983 | 122.1963 | 122.1901 | 122.0942 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.273 | 122.2952 | 122.1647 | 122.1869
2814.9375 | 122.3236 | -0.091553 | 122.2458 | 0.10354 | 0.023583 | -0.021157 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 122.2617 | 122.1413 | 122.1443 | 122.053 | -0.020437 | 0.018642 | -0.024328 | 0.001406 | 0.19509 | 0.11514 | 0.070396 | 0.089429 | 0.095772 | 0.17256 | 0.088352 | 122.3029 | 122.1825 | 122.1855 | 122.0942 | 0.020762 | 0.059841 | 0.016871 | 0.042605 | 122.2821 | 122.286 | 122.1647 | 122.1686
2816.6406 | 122.4197 | -0.054932 | 122.2046 | 0.094381 | 0.023583 | -0.016578 | -0.01586 | 0.004219 | 0.085583 | -0.016936 | 122.2708 | 122.1505 | 122.1443 | 122.0439 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.14931 | 0.078515 | 0.038354 | 0.039072 | 0.059151 | 0.14052 | 0.037996 | 122.312 | 122.1917 | 122.1855 | 122.0851 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.2867 | 122.3043 | 122.1602 | 122.1778
2818.3906 | 122.3465 | -0.086975 | 122.2275 | 0.098959 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.090161 | -0.012357 | 122.2571 | 122.1459 | 122.1489 | 122.0485 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.18593 | 0.10598 | 0.070397 | 0.080272 | 0.095772 | 0.17714 | 0.074618 | 122.2983 | 122.1871 | 122.1901 | 122.0897 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.273 | 122.2906 | 122.1647 | 122.1824
2820.0938 | 122.4564 | -0.045776 | 122.2137 | 0.10812 | 0.023583 | -0.025735 | -0.006703 | 0.004219 | 0.081005 | -0.021514 | 122.2571 | 122.1551 | 122.1443 | 122.053 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.15389 | 0.069359 | 0.020041 | 0.039073 | 0.049995 | 0.12678 | 0.024262 | 122.2983 | 122.1963 | 122.1855 | 122.0942 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.273 | 122.286 | 122.1602 | 122.1732
2821.8594 | 122.3007 | -0.09613 | 122.2321 | 0.094381 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.099318 | 0.001377 | 122.2617 | 122.1505 | 122.1535 | 122.0485 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.19051 | 0.11513 | 0.074973 | 0.084849 | 0.1095 | 0.19545 | 0.097507 | 122.3029 | 122.1917 | 122.1947 | 122.0897 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2775 | 122.2906 | 122.1693 | 122.1824
2823.6094 | 122.438 | -0.050354 | 122.2137 | 0.094381 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.2571 | 122.1459 | 122.1535 | 122.053 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.14474 | 0.073937 | 0.033776 | 0.043651 | 0.059151 | 0.13594 | 0.037997 | 122.2983 | 122.1871 | 122.1947 | 122.0942 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.2684 | 122.2906 | 122.1647 | 122.1869
2825.3594 | 122.374 | -0.059509 | 122.2183 | 0.094381 | 0.019004 | -0.021157 | -0.020438 | 0.008797 | 0.081005 | -0.007779 | 122.2617 | 122.1505 | 122.1443 | 122.0439 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.15389 | 0.078513 | 0.038352 | 0.039071 | 0.068306 | 0.14051 | 0.05173 | 122.3029 | 122.1917 | 122.1855 | 122.0851 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.2775 | 122.2952 | 122.1602 | 122.1778
2827.0625 | 122.3145 | -0.09613 | 122.2412 | 0.094381 | 0.028162 | -0.021157 | 0.002454 | 0.008797 | 0.090161 | -0.012357 | 122.2617 | 122.1551 | 122.1443 | 122.053 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.19051 | 0.12429 | 0.074973 | 0.098584 | 0.10493 | 0.18629 | 0.083773 | 122.3029 | 122.1963 | 122.1855 | 122.0942 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.273 | 122.286 | 122.1556 | 122.1686
2828.8281 | 122.4335 | -0.036621 | 122.2321 | 0.10354 | 0.028162 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.021514 | 122.2571 | 122.1459 | 122.1535 | 122.053 | -0.006702 | 0.02322 | -0.028906 | 0.001406 | 0.14016 | 0.064783 | 0.020043 | 0.020761 | 0.045418 | 0.1222 | 0.015107 | 122.2983 | 122.1871 | 122.1947 | 122.0942 | 0.034497 | 0.064419 | 0.012293 | 0.042605 | 122.2638 | 122.286 | 122.1602 | 122.1824
2830.5156 | 122.3969 | -0.068665 | 122.2229 | 0.10354 | 0.023583 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2617 | 122.1551 | 122.1535 | 122.0485 | -0.015859 | 0.02322 | -0.024328 | 0.010563 | 0.1722 | 0.092248 | 0.047508 | 0.061962 | 0.072884 | 0.15425 | 0.051729 | 122.3029 | 122.1963 | 122.1947 | 122.0897 | 0.02534 | 0.064419 | 0.016871 | 0.051762 | 122.2775 | 122.286 | 122.1693 | 122.1778
2832.2812 | 122.4289 | -0.059509 | 122.2092 | 0.098959 | 0.023583 | -0.025735 | -0.011281 | 0.004219 | 0.081005 | -0.007779 | 122.2663 | 122.1413 | 122.1397 | 122.053 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.15847 | 0.083092 | 0.033774 | 0.048228 | 0.063728 | 0.14051 | 0.05173 | 122.3075 | 122.1825 | 122.1809 | 122.0942 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.2821 | 122.2997 | 122.1556 | 122.1732
2834.0469 | 122.4335 | -0.064087 | 122.2275 | 0.094381 | 0.019004 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 122.2617 | 122.1505 | 122.1443 | 122.0439 | -0.020437 | 0.018642 | -0.033484 | 0.010563 | 0.15847 | 0.083091 | 0.04293 | 0.048227 | 0.068306 | 0.14967 | 0.05173 | 122.3029 | 122.1917 | 122.1855 | 122.0851 | 0.020762 | 0.059841 | 0.007715 | 0.051762 | 122.2821 | 122.2952 | 122.1647 | 122.1778
2835.7969 | 122.438 | -0.045776 | 122.2137 | 0.10354 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.081005 | -0.012357 | 122.2617 | 122.1505 | 122.1535 | 122.0576 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.14931 | 0.069359 | 0.029198 | 0.034495 | 0.049995 | 0.12678 | 0.033419 | 122.3029 | 122.1917 | 122.1947 | 122.0988 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.2775 | 122.286 | 122.1693 | 122.1778
2837.5469 | 122.3145 | -0.082397 | 122.2504 | 0.10812 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 122.2571 | 122.1459 | 122.1443 | 122.053 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.19051 | 0.10598 | 0.065819 | 0.075694 | 0.091194 | 0.16798 | 0.074618 | 122.2983 | 122.1871 | 122.1855 | 122.0942 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.273 | 122.286 | 122.1602 | 122.1732
2839.25 | 122.319 | -0.086975 | 122.2458 | 0.098959 | 0.023583 | -0.016578 | -0.011281 | 0.013375 | 0.090161 | -0.007779 | 122.2571 | 122.1551 | 122.1535 | 122.053 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.18593 | 0.11056 | 0.070397 | 0.075694 | 0.10035 | 0.17714 | 0.079196 | 122.2983 | 122.1963 | 122.1947 | 122.0942 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.2775 | 122.2906 | 122.1739 | 122.1869
2841 | 122.3145 | -0.10529 | 122.2504 | 0.10354 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.09474 | -0.016936 | 122.2663 | 122.1596 | 122.1489 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.20882 | 0.12429 | 0.084129 | 0.094005 | 0.11866 | 0.20003 | 0.08835 | 122.3075 | 122.2008 | 122.1901 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.2867 | 122.2997 | 122.1693 | 122.1824
2842.75 | 122.3328 | -0.09613 | 122.2549 | 0.094381 | 0.023583 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 122.2617 | 122.1551 | 122.1443 | 122.0576 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.19051 | 0.11971 | 0.074973 | 0.089427 | 0.10035 | 0.17713 | 0.083773 | 122.3029 | 122.1963 | 122.1855 | 122.0988 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.2775 | 122.286 | 122.1602 | 122.1686
2844.5 | 122.4564 | -0.054932 | 122.1863 | 0.10354 | 0.019004 | -0.021157 | -0.006703 | -0.000359 | 0.085583 | -0.021514 | 122.2571 | 122.1596 | 122.1489 | 122.0576 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 0.15847 | 0.073936 | 0.033775 | 0.048229 | 0.054573 | 0.14052 | 0.033418 | 122.2983 | 122.2008 | 122.1901 | 122.0988 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 122.2684 | 122.2952 | 122.1602 | 122.1869
2846.1875 | 122.319 | -0.11902 | 122.2321 | 0.094381 | 0.019004 | -0.021157 | -0.002124 | 0.008797 | 0.090161 | -0.016936 | 122.2663 | 122.1551 | 122.1535 | 122.0576 | -0.011281 | 0.018642 | -0.028906 | -0.003172 | 0.2134 | 0.13802 | 0.097862 | 0.11689 | 0.12782 | 0.20918 | 0.10208 | 122.3075 | 122.1963 | 122.1947 | 122.0988 | 0.029918 | 0.059841 | 0.012293 | 0.038027 | 122.2775 | 122.2952 | 122.1647 | 122.1824
2847.9375 | 122.3099 | -0.091553 | 122.2687 | 0.098959 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2617 | 122.1551 | 122.1443 | 122.053 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.19051 | 0.11514 | 0.070396 | 0.08485 | 0.10035 | 0.18629 | 0.083774 | 122.3029 | 122.1963 | 122.1855 | 122.0942 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.273 | 122.2906 | 122.1556 | 122.1732
2849.6875 | 122.2916 | -0.10986 | 122.2275 | 0.094381 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.090161 | -0.016936 | 122.2663 | 122.1505 | 122.1489 | 122.0622 | -0.020437 | 0.027798 | -0.033484 | 0.005985 | 0.20424 | 0.13345 | 0.093285 | 0.10316 | 0.11866 | 0.20002 | 0.092927 | 122.3075 | 122.1917 | 122.1901 | 122.1034 | 0.020762 | 0.068997 | 0.007715 | 0.047184 | 122.2867 | 122.2997 | 122.1693 | 122.1824
2851.3906 | 122.4472 | -0.068665 | 122.1909 | 0.094381 | 0.009846 | -0.025735 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2754 | 122.1551 | 122.1489 | 122.053 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.16305 | 0.078511 | 0.04293 | 0.061962 | 0.072884 | 0.15883 | 0.056308 | 122.3166 | 122.1963 | 122.1901 | 122.0942 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2913 | 122.3043 | 122.1647 | 122.1778
2853.1562 | 122.3511 | -0.10986 | 122.2458 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.2663 | 122.1551 | 122.158 | 122.053 | -0.006702 | 0.02322 | -0.028906 | 0.005985 | 0.20882 | 0.13345 | 0.088706 | 0.098582 | 0.11408 | 0.19545 | 0.097506 | 122.3075 | 122.1963 | 122.1992 | 122.0942 | 0.034497 | 0.064419 | 0.012293 | 0.047184 | 122.273 | 122.2952 | 122.1647 | 122.1869
2854.8594 | 122.3511 | -0.082397 | 122.2366 | 0.098959 | 0.023583 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 122.2663 | 122.1596 | 122.1489 | 122.0576 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.18136 | 0.10598 | 0.070397 | 0.075694 | 0.091194 | 0.16798 | 0.074618 | 122.3075 | 122.2008 | 122.1901 | 122.0988 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2775 | 122.2952 | 122.1602 | 122.1778
2856.625 | 122.3053 | -0.10529 | 122.2549 | 0.10354 | 0.019004 | -0.021157 | -0.002124 | 0.013375 | 0.099318 | -0.012357 | 122.2617 | 122.1551 | 122.1489 | 122.0668 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 0.20882 | 0.12429 | 0.084129 | 0.10316 | 0.11866 | 0.2046 | 0.092929 | 122.3029 | 122.1963 | 122.1901 | 122.108 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.2821 | 122.2906 | 122.1693 | 122.1778
2858.375 | 122.3236 | -0.11444 | 122.2595 | 0.098959 | 0.019004 | -0.021157 | -0.002124 | 0.008797 | 0.090161 | -0.007779 | 122.2708 | 122.1505 | 122.158 | 122.0485 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.2134 | 0.13345 | 0.093284 | 0.11232 | 0.12324 | 0.2046 | 0.10666 | 122.312 | 122.1917 | 122.1992 | 122.0897 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.2867 | 122.3043 | 122.1739 | 122.1915
2860.0625 | 122.3511 | -0.091553 | 122.2412 | 0.094381 | 0.019004 | -0.025735 | -0.011281 | 0.004219 | 0.090161 | -0.007779 | 122.2663 | 122.1596 | 122.1489 | 122.0576 | -0.011281 | 0.02322 | -0.024328 | 0.005985 | 0.18593 | 0.11056 | 0.065818 | 0.080272 | 0.095772 | 0.18171 | 0.083774 | 122.3075 | 122.2008 | 122.1901 | 122.0988 | 0.029918 | 0.064419 | 0.016871 | 0.047184 | 122.2775 | 122.2906 | 122.1602 | 122.1732
2861.7656 | 122.4289 | -0.059509 | 122.2229 | 0.098959 | 0.019004 | -0.021157 | -0.006703 | 0.004219 | 0.085583 | -0.016936 | 122.2708 | 122.1551 | 122.1535 | 122.0576 | -0.020437 | 0.027798 | -0.024328 | 0.001406 | 0.15847 | 0.078513 | 0.038352 | 0.052806 | 0.063728 | 0.14509 | 0.042573 | 122.312 | 122.1963 | 122.1947 | 122.0988 | 0.020762 | 0.068997 | 0.016871 | 0.042605 | 122.2913 | 122.2952 | 122.1739 | 122.1778
2863.5312 | 122.4426 | -0.045776 | 122.2092 | 0.10354 | 0.019004 | -0.021157 | -0.01586 | 0.004219 | 0.085583 | -0.012357 | 122.2663 | 122.1551 | 122.1489 | 122.0576 | -0.011281 | 0.018642 | -0.033484 | 0.005985 | 0.14931 | 0.06478 | 0.024619 | 0.029916 | 0.049995 | 0.13136 | 0.033419 | 122.3075 | 122.1963 | 122.1901 | 122.0988 | 0.029918 | 0.059841 | 0.007715 | 0.047184 | 122.2775 | 122.2997 | 122.1602 | 122.1824
2865.2969 | 122.438 | -0.054932 | 122.2 | 0.094381 | 0.014425 | -0.025735 | -0.020438 | 0.004219 | 0.085583 | -0.012357 | 122.2708 | 122.1551 | 122.1535 | 122.0485 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.14931 | 0.069357 | 0.029197 | 0.034494 | 0.059151 | 0.14052 | 0.042575 | 122.312 | 122.1963 | 122.1947 | 122.0897 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.2867 | 122.3043 | 122.1693 | 122.1869
2867 | 122.3419 | -0.091553 | 122.2458 | 0.10812 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.003201 | 122.2754 | 122.1596 | 122.1626 | 122.0576 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.19967 | 0.11056 | 0.074975 | 0.080272 | 0.10035 | 0.18171 | 0.088352 | 122.3166 | 122.2008 | 122.2038 | 122.0988 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.2867 | 122.3089 | 122.1739 | 122.1961
2868.75 | 122.4197 | -0.064087 | 122.2183 | 0.094381 | 0.019004 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.016936 | 122.2663 | 122.1505 | 122.1443 | 122.053 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.15847 | 0.083091 | 0.04293 | 0.052806 | 0.068306 | 0.14509 | 0.047151 | 122.3075 | 122.1917 | 122.1855 | 122.0942 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.2775 | 122.2997 | 122.1556 | 122.1778
2870.4531 | 122.3236 | -0.10529 | 122.2275 | 0.098959 | 0.009846 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.2708 | 122.1596 | 122.1535 | 122.0576 | -0.011281 | 0.027798 | -0.024328 | -0.003172 | 0.20425 | 0.11513 | 0.084129 | 0.094005 | 0.10951 | 0.19087 | 0.092929 | 122.312 | 122.2008 | 122.1947 | 122.0988 | 0.029918 | 0.068997 | 0.016871 | 0.038027 | 122.2821 | 122.2952 | 122.1647 | 122.1778
2872.2188 | 122.3694 | -0.086975 | 122.2549 | 0.10354 | 0.023583 | -0.021157 | -0.01586 | 0.013375 | 0.09474 | -0.012357 | 122.2708 | 122.1642 | 122.1535 | 122.0576 | -0.020437 | 0.018642 | -0.033484 | -0.003172 | 0.19051 | 0.11056 | 0.065818 | 0.071115 | 0.10035 | 0.18172 | 0.074618 | 122.312 | 122.2054 | 122.1947 | 122.0988 | 0.020762 | 0.059841 | 0.007715 | 0.038027 | 122.2913 | 122.3043 | 122.1739 | 122.1869
2873.9219 | 122.319 | -0.11444 | 122.2412 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.2663 | 122.1596 | 122.1489 | 122.0576 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.2134 | 0.13802 | 0.093284 | 0.10316 | 0.12324 | 0.20002 | 0.097505 | 122.3075 | 122.2008 | 122.1901 | 122.0988 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.2821 | 122.3043 | 122.1647 | 122.1869
2875.6719 | 122.3511 | -0.073242 | 122.2275 | 0.094381 | 0.019004 | -0.016578 | -0.002124 | 0.008797 | 0.090161 | -0.012357 | 122.2754 | 122.1596 | 122.1489 | 122.0622 | -0.020437 | 0.018642 | -0.028906 | 0.001406 | 0.16762 | 0.092246 | 0.056664 | 0.071118 | 0.082039 | 0.1634 | 0.060885 | 122.3166 | 122.2008 | 122.1901 | 122.1034 | 0.020762 | 0.059841 | 0.012293 | 0.042605 | 122.2959 | 122.3043 | 122.1693 | 122.1778
2877.3594 | 122.3557 | -0.091553 | 122.2092 | 0.10354 | 0.019004 | -0.021157 | -0.006703 | 0.013375 | 0.09474 | -0.007779 | 122.2663 | 122.1551 | 122.1489 | 122.0576 | -0.011281 | 0.027798 | -0.038063 | 0.010563 | 0.19509 | 0.11056 | 0.070396 | 0.08485 | 0.10493 | 0.18629 | 0.083774 | 122.3075 | 122.1963 | 122.1901 | 122.0988 | 0.029918 | 0.068997 | 0.003136 | 0.051762 | 122.2775 | 122.3043 | 122.1602 | 122.1869
2879.1094 | 122.3877 | -0.073242 | 122.1909 | 0.094381 | 0.028162 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.007779 | 122.2617 | 122.1551 | 122.1535 | 122.0576 | -0.020437 | 0.02322 | -0.028906 | -0.003172 | 0.16762 | 0.1014 | 0.056664 | 0.061961 | 0.086617 | 0.15882 | 0.065463 | 122.3029 | 122.1963 | 122.1947 | 122.0988 | 0.020762 | 0.064419 | 0.012293 | 0.038027 | 122.2821 | 122.2906 | 122.1739 | 122.1824
2880.875 | 122.3877 | -0.068665 | 122.2046 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | -0.000359 | 0.085583 | -0.012357 | 122.2708 | 122.1642 | 122.1535 | 122.0485 | -0.020437 | 0.032376 | -0.038063 | 0.010563 | 0.16762 | 0.092248 | 0.047508 | 0.057384 | 0.068306 | 0.15425 | 0.056308 | 122.312 | 122.2054 | 122.1947 | 122.0897 | 0.020762 | 0.073575 | 0.003136 | 0.051762 | 122.2913 | 122.3089 | 122.1739 | 122.1915
2882.5781 | 122.3145 | -0.09613 | 122.2504 | 0.10354 | 0.023583 | -0.021157 | -0.011281 | 0.013375 | 0.090161 | 0.001377 | 122.2708 | 122.1505 | 122.1489 | 122.0485 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.19967 | 0.11971 | 0.074973 | 0.084849 | 0.1095 | 0.18629 | 0.097507 | 122.312 | 122.1917 | 122.1901 | 122.0897 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2821 | 122.3043 | 122.1602 | 122.1824
2884.3281 | 122.3831 | -0.07782 | 122.2 | 0.094381 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 122.2754 | 122.1596 | 122.1443 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.1722 | 0.1014 | 0.061242 | 0.071117 | 0.082039 | 0.15882 | 0.065463 | 122.3166 | 122.2008 | 122.1855 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.2959 | 122.3089 | 122.1647 | 122.1778
2886.0781 | 122.4243 | -0.045776 | 122.2275 | 0.094381 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.007779 | 122.2754 | 122.1551 | 122.1489 | 122.0622 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.14016 | 0.069359 | 0.029198 | 0.034495 | 0.054573 | 0.12678 | 0.037997 | 122.3166 | 122.1963 | 122.1901 | 122.1034 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.2959 | 122.3043 | 122.1693 | 122.1778
2887.8438 | 122.3373 | -0.082397 | 122.2595 | 0.098959 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2708 | 122.1505 | 122.158 | 122.0576 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.18136 | 0.10598 | 0.065819 | 0.075694 | 0.086616 | 0.17256 | 0.07004 | 122.312 | 122.1917 | 122.1992 | 122.0988 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.2867 | 122.3043 | 122.1739 | 122.1915
2889.5312 | 122.3282 | -0.10986 | 122.2412 | 0.098959 | 0.023583 | -0.021157 | -0.006703 | -0.000359 | 0.081005 | -0.003201 | 122.2708 | 122.1551 | 122.1535 | 122.0622 | -0.020437 | 0.018642 | -0.033484 | 0.005985 | 0.20882 | 0.13345 | 0.088706 | 0.10316 | 0.1095 | 0.19087 | 0.10666 | 122.312 | 122.1963 | 122.1947 | 122.1034 | 0.020762 | 0.059841 | 0.007715 | 0.047184 | 122.2913 | 122.3043 | 122.1739 | 122.1869
2891.2812 | 122.4518 | -0.059509 | 122.2092 | 0.094381 | 0.028162 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.016936 | 122.2708 | 122.1551 | 122.1535 | 122.0576 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.15389 | 0.087671 | 0.038352 | 0.048228 | 0.063728 | 0.14509 | 0.042573 | 122.312 | 122.1963 | 122.1947 | 122.0988 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2821 | 122.2997 | 122.1647 | 122.1824
2893.0469 | 122.438 | -0.068665 | 122.2137 | 0.098959 | 0.023583 | -0.025735 | -0.011281 | -0.000359 | 0.081005 | -0.012357 | 122.2708 | 122.1596 | 122.158 | 122.053 | -0.015859 | 0.018642 | -0.028906 | 0.001406 | 0.16762 | 0.092248 | 0.04293 | 0.057384 | 0.068306 | 0.14967 | 0.056308 | 122.312 | 122.2008 | 122.1992 | 122.0942 | 0.02534 | 0.059841 | 0.012293 | 0.042605 | 122.2867 | 122.2997 | 122.1739 | 122.1869
2894.7344 | 122.3557 | -0.082397 | 122.2275 | 0.10354 | 0.023583 | -0.016578 | -0.006703 | -0.000359 | 0.085583 | -0.007779 | 122.2708 | 122.1551 | 122.1535 | 122.0576 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.18593 | 0.10598 | 0.065819 | 0.075694 | 0.082038 | 0.16798 | 0.074618 | 122.312 | 122.1963 | 122.1947 | 122.0988 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2821 | 122.2997 | 122.1647 | 122.1824
2896.4844 | 122.3282 | -0.10071 | 122.2549 | 0.098959 | 0.028162 | -0.012 | -0.006703 | 0.008797 | 0.090161 | -0.007779 | 122.2663 | 122.1596 | 122.1535 | 122.0576 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.19967 | 0.12887 | 0.088708 | 0.094005 | 0.10951 | 0.19087 | 0.092929 | 122.3075 | 122.2008 | 122.1947 | 122.0988 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.2821 | 122.2906 | 122.1693 | 122.1778
2898.2344 | 122.4289 | -0.032043 | 122.1725 | 0.098959 | 0.028162 | -0.025735 | -0.006703 | -0.000359 | 0.085583 | -0.012357 | 122.2754 | 122.1551 | 122.1535 | 122.053 | -0.020437 | 0.02322 | -0.038063 | 0.005985 | 0.131 | 0.060205 | 0.006308 | 0.02534 | 0.031684 | 0.11763 | 0.019686 | 122.3166 | 122.1963 | 122.1947 | 122.0942 | 0.020762 | 0.064419 | 0.003136 | 0.047184 | 122.2959 | 122.3135 | 122.1739 | 122.1915
2899.9219 | 122.3557 | -0.086975 | 122.2504 | 0.10354 | 0.028162 | -0.016578 | -0.01586 | -0.000359 | 0.09474 | -0.012357 | 122.2708 | 122.1596 | 122.158 | 122.0576 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.19051 | 0.11514 | 0.070397 | 0.071115 | 0.086616 | 0.18172 | 0.074618 | 122.312 | 122.2008 | 122.1992 | 122.0988 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2821 | 122.2997 | 122.1693 | 122.1869
2901.6719 | 122.3648 | -0.082397 | 122.2458 | 0.098959 | 0.028162 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.007779 | 122.2617 | 122.1688 | 122.1535 | 122.0622 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.18136 | 0.11056 | 0.06124 | 0.071116 | 0.086616 | 0.16798 | 0.074618 | 122.3029 | 122.21 | 122.1947 | 122.1034 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.273 | 122.2952 | 122.1647 | 122.1869
2903.375 | 122.3877 | -0.059509 | 122.2458 | 0.089802 | 0.028162 | -0.025735 | -0.006703 | -0.000359 | 0.085583 | -0.003201 | 122.2754 | 122.1551 | 122.1535 | 122.0485 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.14931 | 0.087671 | 0.033774 | 0.052806 | 0.05915 | 0.14509 | 0.056308 | 122.3166 | 122.1963 | 122.1947 | 122.0897 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.2913 | 122.3089 | 122.1693 | 122.1869
2905.1406 | 122.319 | -0.091553 | 122.2321 | 0.10812 | 0.028162 | -0.012 | -0.006703 | 0.013375 | 0.09474 | -0.007779 | 122.2708 | 122.1596 | 122.1626 | 122.0668 | -0.015859 | 0.014064 | -0.028906 | 0.005985 | 0.19967 | 0.11971 | 0.079553 | 0.08485 | 0.10493 | 0.18629 | 0.083774 | 122.312 | 122.2008 | 122.2038 | 122.108 | 0.02534 | 0.055263 | 0.012293 | 0.047184 | 122.2867 | 122.2997 | 122.1785 | 122.1915
2906.9062 | 122.3145 | -0.10986 | 122.2641 | 0.098959 | 0.028162 | -0.012 | -0.006703 | 0.008797 | 0.090161 | -0.012357 | 122.2708 | 122.1596 | 122.1626 | 122.0622 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.20882 | 0.13803 | 0.097863 | 0.10316 | 0.11866 | 0.20002 | 0.097506 | 122.312 | 122.2008 | 122.2038 | 122.1034 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.2821 | 122.3043 | 122.1739 | 122.1961
2908.6094 | 122.2961 | -0.10529 | 122.2641 | 0.10354 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.09474 | -0.007779 | 122.2754 | 122.1596 | 122.1626 | 122.0576 | -0.015859 | 0.018642 | -0.024328 | 0.005985 | 0.20882 | 0.12429 | 0.088708 | 0.094005 | 0.11408 | 0.20003 | 0.097507 | 122.3166 | 122.2008 | 122.2038 | 122.0988 | 0.02534 | 0.059841 | 0.016871 | 0.047184 | 122.2913 | 122.2997 | 122.1785 | 122.1869
2910.3594 | 122.3007 | -0.11444 | 122.2504 | 0.10812 | 0.028162 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 122.2708 | 122.1505 | 122.1626 | 122.053 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.22256 | 0.1426 | 0.097863 | 0.11232 | 0.11866 | 0.19545 | 0.10666 | 122.312 | 122.1917 | 122.2038 | 122.0942 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.2913 | 122.2997 | 122.1831 | 122.1915
2912.125 | 122.3419 | -0.09613 | 122.2733 | 0.098959 | 0.028162 | -0.012 | -0.006703 | -0.000359 | 0.09474 | -0.012357 | 122.2663 | 122.1551 | 122.1535 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.19509 | 0.12429 | 0.08413 | 0.089427 | 0.095771 | 0.19087 | 0.083773 | 122.3075 | 122.1963 | 122.1947 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.2867 | 122.2997 | 122.1739 | 122.1869
2913.8281 | 122.3511 | -0.10071 | 122.2641 | 0.098959 | 0.028162 | -0.016578 | -0.006703 | -0.000359 | 0.085583 | -0.003201 | 122.2663 | 122.1688 | 122.158 | 122.0622 | -0.011281 | 0.018642 | -0.028906 | 0.001406 | 0.19967 | 0.12887 | 0.08413 | 0.094005 | 0.10035 | 0.18629 | 0.097507 | 122.3075 | 122.21 | 122.1992 | 122.1034 | 0.029918 | 0.059841 | 0.012293 | 0.042605 | 122.2775 | 122.2952 | 122.1693 | 122.1869
2915.5781 | 122.4701 | -0.068665 | 122.2229 | 0.10354 | 0.023583 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.007779 | 122.2663 | 122.1505 | 122.1489 | 122.0622 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.1722 | 0.092248 | 0.052087 | 0.061962 | 0.072884 | 0.15883 | 0.060886 | 122.3075 | 122.1917 | 122.1901 | 122.1034 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.2821 | 122.2997 | 122.1647 | 122.1824
2917.3281 | 122.3923 | -0.064087 | 122.2366 | 0.089802 | 0.023583 | -0.021157 | -0.01586 | 0.004219 | 0.090161 | -0.016936 | 122.2663 | 122.1551 | 122.158 | 122.0576 | -0.011281 | 0.02322 | -0.033484 | 0.010563 | 0.15389 | 0.08767 | 0.04293 | 0.048227 | 0.068306 | 0.15425 | 0.047151 | 122.3075 | 122.1963 | 122.1992 | 122.0988 | 0.029918 | 0.064419 | 0.007715 | 0.051762 | 122.2775 | 122.2997 | 122.1693 | 122.1915
2919.0938 | 122.4014 | -0.07782 | 122.2321 | 0.089802 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.085583 | -0.012357 | 122.2708 | 122.1551 | 122.158 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.16762 | 0.096824 | 0.052085 | 0.06196 | 0.086617 | 0.1634 | 0.065463 | 122.312 | 122.1963 | 122.1992 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.2913 | 122.3043 | 122.1785 | 122.1915
2920.7969 | 122.3648 | -0.09613 | 122.2137 | 0.098959 | 0.023583 | -0.025735 | -0.002124 | 0.017953 | 0.085583 | -0.016936 | 122.28 | 122.1551 | 122.1626 | 122.0576 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.19509 | 0.11971 | 0.070395 | 0.094006 | 0.11408 | 0.18171 | 0.079194 | 122.3212 | 122.1963 | 122.2038 | 122.0988 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.2913 | 122.3089 | 122.1739 | 122.1915
2922.5625 | 122.319 | -0.073242 | 122.2824 | 0.10354 | 0.023583 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.012357 | 122.2663 | 122.1642 | 122.158 | 122.0576 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.17678 | 0.096825 | 0.056664 | 0.057382 | 0.082039 | 0.15882 | 0.060885 | 122.3075 | 122.2054 | 122.1992 | 122.0988 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.2821 | 122.2997 | 122.1739 | 122.1915
2924.2812 | 122.3557 | -0.082397 | 122.2275 | 0.094381 | 0.028162 | -0.016578 | -0.002124 | 0.008797 | 0.090161 | -0.012357 | 122.2663 | 122.1596 | 122.1672 | 122.0576 | -0.020437 | 0.032376 | -0.028906 | 0.005985 | 0.17678 | 0.11056 | 0.065819 | 0.080273 | 0.091194 | 0.17256 | 0.07004 | 122.3075 | 122.2008 | 122.2084 | 122.0988 | 0.020762 | 0.073575 | 0.012293 | 0.047184 | 122.2867 | 122.2952 | 122.1876 | 122.1961
2926.0312 | 122.4289 | -0.045776 | 122.2092 | 0.094381 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.2754 | 122.1596 | 122.1535 | 122.0622 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.14016 | 0.06478 | 0.029198 | 0.034495 | 0.054573 | 0.13136 | 0.02884 | 122.3166 | 122.2008 | 122.1947 | 122.1034 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.2959 | 122.3043 | 122.1739 | 122.1824
2927.7812 | 122.3007 | -0.10071 | 122.2641 | 0.094381 | 0.03274 | -0.016578 | -0.011281 | 0.017953 | 0.085583 | 0.001377 | 122.28 | 122.1596 | 122.1535 | 122.0622 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.19509 | 0.13345 | 0.08413 | 0.089427 | 0.11866 | 0.18629 | 0.10209 | 122.3212 | 122.2008 | 122.1947 | 122.1034 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.2959 | 122.3089 | 122.1693 | 122.1824
2929.5469 | 122.3328 | -0.11444 | 122.2458 | 0.089802 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.007779 | 122.2708 | 122.1596 | 122.1626 | 122.0622 | -0.020437 | 0.018642 | -0.033484 | 0.001406 | 0.20424 | 0.13345 | 0.097863 | 0.10316 | 0.12324 | 0.20002 | 0.10666 | 122.312 | 122.2008 | 122.2038 | 122.1034 | 0.020762 | 0.059841 | 0.007715 | 0.042605 | 122.2913 | 122.3043 | 122.1831 | 122.1961
2931.2969 | 122.3145 | -0.068665 | 122.2595 | 0.10354 | 0.023583 | -0.021157 | -0.002124 | 0.013375 | 0.090161 | -0.007779 | 122.2754 | 122.1596 | 122.1535 | 122.0576 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.1722 | 0.092248 | 0.047508 | 0.066541 | 0.08204 | 0.15883 | 0.060886 | 122.3166 | 122.2008 | 122.1947 | 122.0988 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.2913 | 122.3135 | 122.1693 | 122.1915
2933.0469 | 122.3419 | -0.086975 | 122.2412 | 0.094381 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.007779 | 122.2846 | 122.1642 | 122.1535 | 122.0622 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.18136 | 0.11056 | 0.070397 | 0.075694 | 0.095772 | 0.17714 | 0.079196 | 122.3258 | 122.2054 | 122.1947 | 122.1034 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3004 | 122.3135 | 122.1693 | 122.1824
2934.7344 | 122.4518 | -0.032043 | 122.2183 | 0.094381 | 0.014425 | -0.012 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 122.28 | 122.1642 | 122.158 | 122.0622 | -0.020437 | 0.018642 | -0.024328 | 0.001406 | 0.12642 | 0.046468 | 0.020043 | 0.020762 | 0.04084 | 0.11763 | 0.019686 | 122.3212 | 122.2054 | 122.1992 | 122.1034 | 0.020762 | 0.059841 | 0.016871 | 0.042605 | 122.3004 | 122.3043 | 122.1785 | 122.1824
2936.4844 | 122.4243 | -0.059509 | 122.2366 | 0.089802 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 122.2754 | 122.1596 | 122.158 | 122.053 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.14931 | 0.083092 | 0.038352 | 0.052806 | 0.068306 | 0.14509 | 0.05173 | 122.3166 | 122.2008 | 122.1992 | 122.0942 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.2867 | 122.3089 | 122.1693 | 122.1915
2938.2344 | 122.4564 | -0.064087 | 122.2046 | 0.098959 | 0.019004 | -0.016578 | -0.01586 | -0.000359 | 0.085583 | -0.007779 | 122.28 | 122.1642 | 122.1626 | 122.053 | -0.025015 | 0.02322 | -0.033484 | 0.001406 | 0.16305 | 0.083091 | 0.047509 | 0.048227 | 0.063728 | 0.14967 | 0.056308 | 122.3212 | 122.2054 | 122.2038 | 122.0942 | 0.016184 | 0.064419 | 0.007715 | 0.042605 | 122.305 | 122.3135 | 122.1876 | 122.1961
2939.9375 | 122.3785 | -0.073242 | 122.2412 | 0.10354 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 122.2754 | 122.1596 | 122.1626 | 122.053 | -0.020437 | 0.018642 | -0.028906 | 0.005985 | 0.17678 | 0.096825 | 0.052085 | 0.066539 | 0.082039 | 0.15882 | 0.065463 | 122.3166 | 122.2008 | 122.2038 | 122.0942 | 0.020762 | 0.059841 | 0.012293 | 0.047184 | 122.2959 | 122.3043 | 122.1831 | 122.1915
2941.7031 | 122.3099 | -0.082397 | 122.2504 | 0.10354 | 0.019004 | -0.021157 | -0.006703 | 0.013375 | 0.081005 | -0.003201 | 122.2754 | 122.1688 | 122.158 | 122.0622 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.18593 | 0.1014 | 0.06124 | 0.075694 | 0.095772 | 0.1634 | 0.079196 | 122.3166 | 122.21 | 122.1992 | 122.1034 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.2913 | 122.3089 | 122.1739 | 122.1915
2943.4062 | 122.4518 | -0.045776 | 122.2137 | 0.094381 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.007779 | 122.2754 | 122.1596 | 122.1535 | 122.0622 | -0.020437 | 0.018642 | -0.038063 | 0.005985 | 0.14016 | 0.06478 | 0.024619 | 0.034495 | 0.054573 | 0.13594 | 0.037997 | 122.3166 | 122.2008 | 122.1947 | 122.1034 | 0.020762 | 0.059841 | 0.003136 | 0.047184 | 122.2959 | 122.3135 | 122.1739 | 122.1915
2945.1562 | 122.438 | -0.050354 | 122.1954 | 0.098959 | 0.023583 | -0.012 | -0.006703 | 0.008797 | 0.090161 | -0.007779 | 122.2708 | 122.1734 | 122.158 | 122.0622 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.14931 | 0.073937 | 0.038354 | 0.043651 | 0.059151 | 0.14052 | 0.042575 | 122.312 | 122.2146 | 122.1992 | 122.1034 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2821 | 122.2997 | 122.1693 | 122.1869
2946.9219 | 122.3602 | -0.10071 | 122.2183 | 0.10812 | 0.023583 | -0.016578 | -0.01586 | 0.013375 | 0.081005 | -0.007779 | 122.2754 | 122.1688 | 122.158 | 122.0576 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.20882 | 0.12429 | 0.08413 | 0.084848 | 0.11408 | 0.18171 | 0.092929 | 122.3166 | 122.21 | 122.1992 | 122.0988 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.2913 | 122.3043 | 122.1739 | 122.1869
2948.6719 | 122.3053 | -0.091553 | 122.2595 | 0.098959 | 0.023583 | -0.012 | -0.006703 | 0.013375 | 0.090161 | -0.007779 | 122.28 | 122.1688 | 122.158 | 122.053 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.19051 | 0.11514 | 0.079553 | 0.08485 | 0.10493 | 0.18171 | 0.083774 | 122.3212 | 122.21 | 122.1992 | 122.0942 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.2913 | 122.3135 | 122.1693 | 122.1915
2950.3594 | 122.4152 | -0.073242 | 122.2229 | 0.098959 | 0.019004 | -0.021157 | -0.01586 | 0.008797 | 0.081005 | -0.007779 | 122.28 | 122.1596 | 122.158 | 122.0576 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.1722 | 0.092246 | 0.052085 | 0.057382 | 0.082039 | 0.15425 | 0.065463 | 122.3212 | 122.2008 | 122.1992 | 122.0988 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.2913 | 122.3135 | 122.1693 | 122.1915
2952.125 | 122.319 | -0.10529 | 122.2595 | 0.094381 | 0.023583 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.007779 | 122.2846 | 122.1642 | 122.1626 | 122.0714 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.19967 | 0.12887 | 0.084129 | 0.094005 | 0.11408 | 0.19087 | 0.097507 | 122.3258 | 122.2054 | 122.2038 | 122.1126 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.305 | 122.3135 | 122.1831 | 122.1915
2953.9062 | 122.438 | -0.059509 | 122.2 | 0.098959 | 0.019004 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.012357 | 122.2708 | 122.1688 | 122.1672 | 122.0622 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 0.15847 | 0.078513 | 0.042931 | 0.048228 | 0.068306 | 0.14967 | 0.047152 | 122.312 | 122.21 | 122.2084 | 122.1034 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.2913 | 122.2997 | 122.1876 | 122.1961
2955.6562 | 122.3282 | -0.10529 | 122.287 | 0.098959 | 0.019004 | -0.012 | -0.01586 | 0.013375 | 0.09474 | -0.012357 | 122.2708 | 122.1596 | 122.1672 | 122.0668 | -0.015859 | 0.02322 | -0.028906 | -0.00775 | 0.20425 | 0.12429 | 0.093286 | 0.089426 | 0.11866 | 0.20003 | 0.092929 | 122.312 | 122.2008 | 122.2084 | 122.108 | 0.02534 | 0.064419 | 0.012293 | 0.033449 | 122.2867 | 122.2997 | 122.1831 | 122.1961
2957.3438 | 122.4197 | -0.064087 | 122.2275 | 0.094381 | 0.028162 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.007779 | 122.28 | 122.1551 | 122.158 | 122.0668 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.15847 | 0.092249 | 0.04293 | 0.052806 | 0.068306 | 0.14967 | 0.056308 | 122.3212 | 122.1963 | 122.1992 | 122.108 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2913 | 122.3135 | 122.1693 | 122.1915
2959.1094 | 122.4335 | -0.054932 | 122.2321 | 0.098959 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.085583 | -0.007779 | 122.2846 | 122.1642 | 122.1535 | 122.0576 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.15389 | 0.073936 | 0.038354 | 0.048229 | 0.068307 | 0.14052 | 0.047153 | 122.3258 | 122.2054 | 122.1947 | 122.0988 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.2959 | 122.3226 | 122.1647 | 122.1915
2960.7969 | 122.374 | -0.10071 | 122.2504 | 0.098959 | 0.023583 | -0.016578 | -0.01586 | 0.017953 | 0.085583 | -0.007779 | 122.2754 | 122.1642 | 122.1626 | 122.0668 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.19967 | 0.12429 | 0.08413 | 0.084848 | 0.11866 | 0.18629 | 0.092929 | 122.3166 | 122.2054 | 122.2038 | 122.108 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.2913 | 122.3043 | 122.1785 | 122.1915
2962.5469 | 122.3831 | -0.07782 | 122.2229 | 0.089802 | 0.009846 | -0.012 | -0.011281 | 0.004219 | 0.09474 | -0.016936 | 122.2846 | 122.1642 | 122.158 | 122.0576 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.16762 | 0.087666 | 0.06582 | 0.066539 | 0.082039 | 0.17256 | 0.060884 | 122.3258 | 122.2054 | 122.1992 | 122.0988 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2959 | 122.3181 | 122.1693 | 122.1915
2964.3125 | 122.3282 | -0.10071 | 122.2549 | 0.094381 | 0.014425 | -0.021157 | -0.011281 | 0.004219 | 0.090161 | -0.007779 | 122.28 | 122.1688 | 122.1672 | 122.0622 | -0.020437 | 0.018642 | -0.033484 | 0.005985 | 0.19509 | 0.11513 | 0.079551 | 0.089427 | 0.10493 | 0.19087 | 0.092929 | 122.3212 | 122.21 | 122.2084 | 122.1034 | 0.020762 | 0.059841 | 0.007715 | 0.047184 | 122.3004 | 122.3135 | 122.1876 | 122.2007
2966 | 122.3648 | -0.086975 | 122.2549 | 0.098959 | 0.014425 | -0.016578 | -0.006703 | 0.017953 | 0.090161 | 0.001377 | 122.2708 | 122.1688 | 122.1672 | 122.0668 | -0.020437 | 0.018642 | -0.024328 | 0.001406 | 0.18593 | 0.1014 | 0.070397 | 0.080272 | 0.10493 | 0.17714 | 0.088352 | 122.312 | 122.21 | 122.2084 | 122.108 | 0.020762 | 0.059841 | 0.016871 | 0.042605 | 122.2913 | 122.2952 | 122.1876 | 122.1915
2967.75 | 122.4243 | -0.064087 | 122.2687 | 0.094381 | 0.009846 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.003201 | 122.28 | 122.1596 | 122.158 | 122.0576 | -0.020437 | 0.02322 | -0.028906 | 0.005985 | 0.15847 | 0.073933 | 0.047509 | 0.052806 | 0.072884 | 0.14509 | 0.060886 | 122.3212 | 122.2008 | 122.1992 | 122.0988 | 0.020762 | 0.064419 | 0.012293 | 0.047184 | 122.3004 | 122.3089 | 122.1785 | 122.1869
2969.4531 | 122.406 | -0.073242 | 122.1954 | 0.094381 | 0.014425 | -0.012 | -0.011281 | 0.013375 | 0.085583 | -0.012357 | 122.28 | 122.1551 | 122.1626 | 122.0622 | -0.025015 | 0.027798 | -0.028906 | -0.003172 | 0.16762 | 0.087667 | 0.061242 | 0.061961 | 0.086617 | 0.15882 | 0.060885 | 122.3212 | 122.1963 | 122.2038 | 122.1034 | 0.016184 | 0.068997 | 0.012293 | 0.038027 | 122.305 | 122.3089 | 122.1876 | 122.1915
2971.2031 | 122.3694 | -0.10071 | 122.2321 | 0.098959 | 0.019004 | -0.021157 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.28 | 122.1596 | 122.1672 | 122.0622 | -0.025015 | 0.02322 | -0.038063 | -0.003172 | 0.19967 | 0.11971 | 0.079551 | 0.094005 | 0.10951 | 0.19545 | 0.092929 | 122.3212 | 122.2008 | 122.2084 | 122.1034 | 0.016184 | 0.064419 | 0.003136 | 0.038027 | 122.305 | 122.3181 | 122.1922 | 122.2053
2972.9688 | 122.4243 | -0.064087 | 122.2092 | 0.089802 | 0.019004 | -0.025735 | -0.011281 | 0.004219 | 0.090161 | -0.007779 | 122.2846 | 122.1734 | 122.158 | 122.0576 | -0.015859 | 0.018642 | -0.028906 | 0.001406 | 0.15389 | 0.083091 | 0.038352 | 0.052806 | 0.068306 | 0.15425 | 0.056308 | 122.3258 | 122.2146 | 122.1992 | 122.0988 | 0.02534 | 0.059841 | 0.012293 | 0.042605 | 122.3004 | 122.3135 | 122.1739 | 122.1869
2974.6562 | 122.3785 | -0.073242 | 122.2549 | 0.098959 | 0.019004 | -0.012 | -0.006703 | 0.017953 | 0.09474 | -0.016936 | 122.2846 | 122.1642 | 122.1672 | 122.0622 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.1722 | 0.092246 | 0.061242 | 0.066539 | 0.091195 | 0.16798 | 0.056306 | 122.3258 | 122.2054 | 122.2084 | 122.1034 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.305 | 122.3181 | 122.1876 | 122.2007
2976.4062 | 122.374 | -0.10071 | 122.2412 | 0.098959 | 0.023583 | -0.025735 | -0.006703 | 0.008797 | 0.090161 | -0.007779 | 122.28 | 122.1642 | 122.1672 | 122.0622 | -0.015859 | 0.018642 | -0.033484 | 0.005985 | 0.19967 | 0.12429 | 0.074973 | 0.094005 | 0.10951 | 0.19087 | 0.092929 | 122.3212 | 122.2054 | 122.2084 | 122.1034 | 0.02534 | 0.059841 | 0.007715 | 0.047184 | 122.2959 | 122.3135 | 122.1831 | 122.2007
2978.0938 | 122.374 | -0.086975 | 122.2275 | 0.094381 | 0.014425 | -0.016578 | -0.01586 | 0.008797 | 0.085583 | -0.007779 | 122.28 | 122.1596 | 122.158 | 122.0576 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.18136 | 0.1014 | 0.070397 | 0.071115 | 0.095772 | 0.17256 | 0.079196 | 122.3212 | 122.2008 | 122.1992 | 122.0988 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2913 | 122.3089 | 122.1693 | 122.1869
2979.8438 | 122.3511 | -0.10529 | 122.2275 | 0.094381 | 0.019004 | -0.007421 | -0.011281 | 0.013375 | 0.090161 | -0.016936 | 122.2754 | 122.1642 | 122.158 | 122.0668 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.19967 | 0.12429 | 0.097865 | 0.094005 | 0.11866 | 0.19545 | 0.08835 | 122.3166 | 122.2054 | 122.1992 | 122.108 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.2913 | 122.3043 | 122.1739 | 122.1869
2981.6094 | 122.438 | -0.050354 | 122.2046 | 0.098959 | 0.019004 | -0.021157 | -0.011281 | 0.013375 | 0.085583 | -0.007779 | 122.28 | 122.1688 | 122.158 | 122.0622 | -0.020437 | 0.02322 | -0.038063 | -0.00775 | 0.14931 | 0.069358 | 0.029197 | 0.039073 | 0.063729 | 0.13594 | 0.042575 | 122.3212 | 122.21 | 122.1992 | 122.1034 | 0.020762 | 0.064419 | 0.003136 | 0.033449 | 122.3004 | 122.3181 | 122.1785 | 122.1961
2983.3125 | 122.3373 | -0.091553 | 122.2504 | 0.098959 | 0.019004 | -0.012 | -0.011281 | 0.008797 | 0.085583 | -0.007779 | 122.28 | 122.1642 | 122.1626 | 122.0622 | -0.011281 | 0.032376 | -0.038063 | 0.001406 | 0.19051 | 0.11056 | 0.079553 | 0.080272 | 0.10035 | 0.17714 | 0.083774 | 122.3212 | 122.2054 | 122.2038 | 122.1034 | 0.029918 | 0.073575 | 0.003136 | 0.042605 | 122.2913 | 122.3181 | 122.1739 | 122.2007
2985.0781 | 122.3236 | -0.10529 | 122.2641 | 0.094381 | 0.023583 | -0.012 | -0.006703 | 0.013375 | 0.090161 | -0.003201 | 122.2754 | 122.1642 | 122.158 | 122.0622 | -0.020437 | 0.027798 | -0.038063 | 0.001406 | 0.19967 | 0.12887 | 0.093286 | 0.098583 | 0.11866 | 0.19545 | 0.10209 | 122.3166 | 122.2054 | 122.1992 | 122.1034 | 0.020762 | 0.068997 | 0.003136 | 0.042605 | 122.2959 | 122.3135 | 122.1785 | 122.1961
2986.7656 | 122.3328 | -0.10529 | 122.2687 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.007779 | 122.28 | 122.1688 | 122.1672 | 122.0576 | -0.020437 | 0.027798 | -0.042641 | -0.003172 | 0.20425 | 0.12429 | 0.079551 | 0.089426 | 0.11408 | 0.19545 | 0.097507 | 122.3212 | 122.21 | 122.2084 | 122.0988 | 0.020762 | 0.068997 | -0.001442 | 0.038027 | 122.3004 | 122.3226 | 122.1876 | 122.2098
2988.5156 | 122.4106 | -0.073242 | 122.2412 | 0.098959 | 0.023583 | -0.021157 | -0.011281 | 0.004219 | 0.085583 | -0.003201 | 122.28 | 122.1596 | 122.1672 | 122.0668 | -0.020437 | 0.02322 | -0.024328 | 0.005985 | 0.1722 | 0.096825 | 0.052085 | 0.061961 | 0.077461 | 0.15882 | 0.070041 | 122.3212 | 122.2008 | 122.2084 | 122.108 | 0.020762 | 0.064419 | 0.016871 | 0.047184 | 122.3004 | 122.3043 | 122.1876 | 122.1915
2990.2031 | 122.3602 | -0.068665 | 122.2504 | 0.098959 | 0.023583 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 122.2754 | 122.1688 | 122.158 | 122.0714 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.16762 | 0.092248 | 0.052087 | 0.061962 | 0.077462 | 0.14967 | 0.056308 | 122.3166 | 122.21 | 122.1992 | 122.1126 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.2867 | 122.3089 | 122.1693 | 122.1915
2991.9688 | 122.406 | -0.050354 | 122.2275 | 0.094381 | 0.028162 | -0.016578 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.2846 | 122.1642 | 122.158 | 122.0714 | -0.006702 | 0.02322 | -0.033484 | 0.005985 | 0.14474 | 0.078516 | 0.033776 | 0.039073 | 0.059151 | 0.13594 | 0.033418 | 122.3258 | 122.2054 | 122.1992 | 122.1126 | 0.034497 | 0.064419 | 0.007715 | 0.047184 | 122.2913 | 122.3181 | 122.1647 | 122.1915
2993.7344 | 122.4335 | -0.059509 | 122.2366 | 0.094381 | 0.023583 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.2846 | 122.1688 | 122.1626 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.15389 | 0.083092 | 0.038352 | 0.052806 | 0.068306 | 0.14509 | 0.047152 | 122.3258 | 122.21 | 122.2038 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.305 | 122.3181 | 122.1831 | 122.1961
2995.4844 | 122.3145 | -0.10071 | 122.2778 | 0.10354 | 0.023583 | -0.016578 | -0.011281 | 0.004219 | 0.099318 | -0.007779 | 122.2754 | 122.1734 | 122.1626 | 122.0668 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.20425 | 0.12429 | 0.08413 | 0.089427 | 0.10493 | 0.20003 | 0.092929 | 122.3166 | 122.2146 | 122.2038 | 122.108 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.2913 | 122.3089 | 122.1785 | 122.1961
2997.1875 | 122.3602 | -0.086975 | 122.2549 | 0.098959 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.09474 | -0.007779 | 122.2754 | 122.1642 | 122.1672 | 122.0622 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.18593 | 0.10598 | 0.065818 | 0.075694 | 0.095772 | 0.18172 | 0.079196 | 122.3166 | 122.2054 | 122.2084 | 122.1034 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.2913 | 122.3135 | 122.1831 | 122.2053
2998.9531 | 122.4197 | -0.064087 | 122.2549 | 0.094381 | 0.019004 | -0.016578 | -0.011281 | -0.000359 | 0.081005 | -0.012357 | 122.28 | 122.1596 | 122.1626 | 122.0668 | -0.011281 | 0.02322 | -0.024328 | 0.001406 | 0.15847 | 0.083091 | 0.047509 | 0.052806 | 0.063728 | 0.14509 | 0.05173 | 122.3212 | 122.2008 | 122.2038 | 122.108 | 0.029918 | 0.064419 | 0.016871 | 0.042605 | 122.2913 | 122.3043 | 122.1739 | 122.1869
3000.7188 | 122.4197 | -0.041199 | 122.2275 | 0.094381 | 0.023583 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 122.28 | 122.1642 | 122.158 | 122.0668 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.13558 | 0.064782 | 0.029199 | 0.034496 | 0.049996 | 0.12678 | 0.024263 | 122.3212 | 122.2054 | 122.1992 | 122.108 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3004 | 122.3089 | 122.1785 | 122.1869
3002.4844 | 122.4609 | -0.054932 | 122.2 | 0.094381 | 0.014425 | -0.021157 | -0.006703 | 0.004219 | 0.090161 | -0.012357 | 122.2846 | 122.1688 | 122.1672 | 122.0576 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.14931 | 0.069357 | 0.033775 | 0.048229 | 0.059151 | 0.14509 | 0.042575 | 122.3258 | 122.21 | 122.2084 | 122.0988 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.305 | 122.3181 | 122.1876 | 122.2007
3004.1875 | 122.4518 | -0.036621 | 122.2366 | 0.098959 | 0.014425 | -0.021157 | -0.011281 | 0.008797 | 0.085583 | -0.016936 | 122.28 | 122.1642 | 122.158 | 122.0668 | -0.015859 | 0.027798 | -0.038063 | 0.005985 | 0.13558 | 0.051046 | 0.015464 | 0.02534 | 0.045418 | 0.1222 | 0.019685 | 122.3212 | 122.2054 | 122.1992 | 122.108 | 0.02534 | 0.068997 | 0.003136 | 0.047184 | 122.2959 | 122.3181 | 122.1739 | 122.1961
3005.9375 | 122.4472 | -0.054932 | 122.2412 | 0.094381 | 0.014425 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 122.28 | 122.1688 | 122.1626 | 122.0714 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.14931 | 0.069357 | 0.042932 | 0.048229 | 0.063729 | 0.14052 | 0.042575 | 122.3212 | 122.21 | 122.2038 | 122.1126 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.2959 | 122.3181 | 122.1785 | 122.2007
3007.6875 | 122.3785 | -0.054932 | 122.2366 | 0.098959 | 0.019004 | -0.025735 | -0.01586 | 0.008797 | 0.090161 | -0.012357 | 122.2846 | 122.1734 | 122.1672 | 122.0668 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.15389 | 0.073936 | 0.029197 | 0.039072 | 0.063729 | 0.14509 | 0.042575 | 122.3258 | 122.2146 | 122.2084 | 122.108 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3004 | 122.3181 | 122.1831 | 122.2007
3009.4531 | 122.3145 | -0.10529 | 122.2687 | 0.10354 | 0.019004 | -0.021157 | -0.011281 | 0.004219 | 0.09474 | -0.003201 | 122.28 | 122.1642 | 122.1626 | 122.0668 | -0.006702 | 0.02322 | -0.038063 | 0.005985 | 0.20882 | 0.12429 | 0.084129 | 0.094005 | 0.10951 | 0.20003 | 0.10209 | 122.3212 | 122.2054 | 122.2038 | 122.108 | 0.034497 | 0.064419 | 0.003136 | 0.047184 | 122.2867 | 122.3181 | 122.1693 | 122.2007
3011.1562 | 122.3328 | -0.10071 | 122.2595 | 0.098959 | 0.019004 | -0.025735 | -0.006703 | 0.008797 | 0.09474 | -0.003201 | 122.28 | 122.1688 | 122.1672 | 122.0668 | -0.020437 | 0.032376 | -0.033484 | 0.005985 | 0.19967 | 0.11971 | 0.074973 | 0.094005 | 0.10951 | 0.19545 | 0.097507 | 122.3212 | 122.21 | 122.2084 | 122.108 | 0.020762 | 0.073575 | 0.007715 | 0.047184 | 122.3004 | 122.3135 | 122.1876 | 122.2007
3012.9062 | 122.3694 | -0.07782 | 122.2321 | 0.094381 | 0.014425 | -0.012 | -0.011281 | 0.004219 | 0.090161 | -0.007779 | 122.2892 | 122.1688 | 122.1626 | 122.0714 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.1722 | 0.092245 | 0.06582 | 0.066539 | 0.082039 | 0.16798 | 0.070041 | 122.3304 | 122.21 | 122.2038 | 122.1126 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.305 | 122.3226 | 122.1785 | 122.1961
3014.6719 | 122.4792 | -0.050354 | 122.2321 | 0.094381 | 0.005267 | -0.025735 | -0.011281 | 0.013375 | 0.085583 | -0.012357 | 122.28 | 122.1688 | 122.1626 | 122.0668 | -0.015859 | 0.014064 | -0.033484 | 0.001406 | 0.14474 | 0.055621 | 0.024619 | 0.039073 | 0.063729 | 0.13594 | 0.037997 | 122.3212 | 122.21 | 122.2038 | 122.108 | 0.02534 | 0.055263 | 0.007715 | 0.042605 | 122.2959 | 122.3135 | 122.1785 | 122.1961
3016.4219 | 122.406 | -0.064087 | 122.2549 | 0.098959 | 0.014425 | -0.012 | -0.011281 | 0.008797 | 0.09474 | -0.012357 | 122.28 | 122.1596 | 122.1672 | 122.0622 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.16305 | 0.078512 | 0.052087 | 0.052806 | 0.072884 | 0.15883 | 0.05173 | 122.3212 | 122.2008 | 122.2084 | 122.1034 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.2959 | 122.3089 | 122.1831 | 122.1961
3018.125 | 122.4747 | -0.045776 | 122.2458 | 0.094381 | 0.019004 | -0.025735 | -0.002124 | 0.017953 | 0.081005 | -0.007779 | 122.28 | 122.1688 | 122.1626 | 122.0622 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.14016 | 0.06478 | 0.020041 | 0.043652 | 0.063729 | 0.12678 | 0.037997 | 122.3212 | 122.21 | 122.2038 | 122.1034 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2913 | 122.3135 | 122.1739 | 122.1961
3019.8906 | 122.3694 | -0.086975 | 122.2504 | 0.10354 | 0.014425 | -0.007421 | -0.006703 | 0.004219 | 0.085583 | -0.007779 | 122.28 | 122.1688 | 122.1672 | 122.0714 | -0.020437 | 0.027798 | -0.024328 | 0.005985 | 0.19051 | 0.1014 | 0.079554 | 0.080272 | 0.091194 | 0.17256 | 0.079196 | 122.3212 | 122.21 | 122.2084 | 122.1126 | 0.020762 | 0.068997 | 0.016871 | 0.047184 | 122.3004 | 122.3043 | 122.1876 | 122.1915
3021.6406 | 122.3648 | -0.086975 | 122.2458 | 0.094381 | 0.019004 | -0.012 | -0.011281 | 0.008797 | 0.099318 | -0.007779 | 122.2754 | 122.1688 | 122.1764 | 122.0714 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.18136 | 0.10598 | 0.074975 | 0.075694 | 0.095772 | 0.18629 | 0.079196 | 122.3166 | 122.21 | 122.2176 | 122.1126 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2867 | 122.3089 | 122.1876 | 122.2098
3023.3281 | 122.319 | -0.11444 | 122.2549 | 0.098959 | 0.014425 | -0.012 | -0.006703 | 0.013375 | 0.09474 | -0.012357 | 122.2754 | 122.1642 | 122.1626 | 122.0668 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.2134 | 0.12887 | 0.10244 | 0.10774 | 0.12782 | 0.20918 | 0.10208 | 122.3166 | 122.2054 | 122.2038 | 122.108 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.2913 | 122.3135 | 122.1785 | 122.2007
3025.1094 | 122.3465 | -0.091553 | 122.2412 | 0.098959 | 0.014425 | -0.016578 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2754 | 122.1642 | 122.1626 | 122.0714 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.19051 | 0.10598 | 0.074975 | 0.08485 | 0.10035 | 0.18629 | 0.083774 | 122.3166 | 122.2054 | 122.2038 | 122.1126 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.2821 | 122.3089 | 122.1693 | 122.1961
3026.875 | 122.3373 | -0.1236 | 122.2366 | 0.094381 | 0.005267 | -0.021157 | -0.006703 | 0.004219 | 0.09474 | -0.016936 | 122.2846 | 122.1734 | 122.1626 | 122.0668 | -0.025015 | 0.027798 | -0.028906 | 0.001406 | 0.21798 | 0.12886 | 0.10244 | 0.11689 | 0.12781 | 0.21834 | 0.10666 | 122.3258 | 122.2146 | 122.2038 | 122.108 | 0.016184 | 0.068997 | 0.012293 | 0.042605 | 122.3096 | 122.3135 | 122.1876 | 122.1915
3028.6406 | 122.4289 | -0.064087 | 122.2092 | 0.098959 | 0.019004 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 122.2846 | 122.178 | 122.1672 | 122.0622 | -0.011281 | 0.027798 | -0.033484 | 0.010563 | 0.16305 | 0.083091 | 0.052087 | 0.057384 | 0.072884 | 0.14967 | 0.056308 | 122.3258 | 122.2192 | 122.2084 | 122.1034 | 0.029918 | 0.068997 | 0.007715 | 0.051762 | 122.2959 | 122.3181 | 122.1785 | 122.2007
3030.3281 | 122.4197 | -0.082397 | 122.2275 | 0.098959 | 0.014425 | -0.016578 | -0.011281 | 0.004219 | 0.085583 | -0.012357 | 122.28 | 122.1734 | 122.1672 | 122.0576 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.18136 | 0.096822 | 0.065819 | 0.071116 | 0.086616 | 0.16798 | 0.07004 | 122.3212 | 122.2146 | 122.2084 | 122.0988 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.2959 | 122.3089 | 122.1831 | 122.1961
3032.0938 | 122.3373 | -0.10529 | 122.2504 | 0.10354 | 0.014425 | -0.021157 | -0.01586 | 0.013375 | 0.090161 | -0.016936 | 122.2754 | 122.1734 | 122.1672 | 122.0714 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.20882 | 0.11971 | 0.084129 | 0.089426 | 0.11866 | 0.19545 | 0.08835 | 122.3166 | 122.2146 | 122.2084 | 122.1126 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.2913 | 122.3089 | 122.1831 | 122.2007
3033.7812 | 122.3099 | -0.082397 | 122.2321 | 0.098959 | 0.019004 | -0.012 | -0.002124 | 0.008797 | 0.09474 | -0.003201 | 122.28 | 122.1688 | 122.1672 | 122.0714 | -0.025015 | 0.02322 | -0.038063 | -0.003172 | 0.18136 | 0.1014 | 0.070397 | 0.080273 | 0.091194 | 0.17714 | 0.079196 | 122.3212 | 122.21 | 122.2084 | 122.1126 | 0.016184 | 0.064419 | 0.003136 | 0.038027 | 122.305 | 122.3181 | 122.1922 | 122.2053
3035.5469 | 122.3373 | -0.10529 | 122.2595 | 0.098959 | 0.014425 | -0.012 | -0.006703 | 0.013375 | 0.090161 | -0.012357 | 122.2892 | 122.1688 | 122.1672 | 122.0668 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.20425 | 0.11971 | 0.093286 | 0.098583 | 0.11866 | 0.19545 | 0.092929 | 122.3304 | 122.21 | 122.2084 | 122.108 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3004 | 122.3226 | 122.1785 | 122.2007
3037.2969 | 122.4106 | -0.050354 | 122.2275 | 0.10354 | 0.014425 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.003201 | 122.28 | 122.1642 | 122.1672 | 122.0622 | -0.011281 | 0.027798 | -0.019749 | 0.001406 | 0.15389 | 0.064779 | 0.033776 | 0.043651 | 0.059151 | 0.13594 | 0.047153 | 122.3212 | 122.2054 | 122.2084 | 122.1034 | 0.029918 | 0.068997 | 0.02145 | 0.042605 | 122.2913 | 122.2997 | 122.1785 | 122.1869
3039.0625 | 122.406 | -0.054932 | 122.2183 | 0.094381 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 122.2846 | 122.1734 | 122.158 | 122.0622 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.14931 | 0.073936 | 0.038354 | 0.048229 | 0.063729 | 0.14052 | 0.047153 | 122.3258 | 122.2146 | 122.1992 | 122.1034 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.2959 | 122.3181 | 122.1693 | 122.1915
3040.7656 | 122.3099 | -0.10986 | 122.2504 | 0.098959 | 0.014425 | -0.007421 | -0.011281 | 0.004219 | 0.085583 | -0.007779 | 122.28 | 122.1734 | 122.1672 | 122.0714 | -0.011281 | 0.027798 | -0.042641 | 0.001406 | 0.20882 | 0.12429 | 0.10244 | 0.098582 | 0.11408 | 0.19545 | 0.10208 | 122.3212 | 122.2146 | 122.2084 | 122.1126 | 0.029918 | 0.068997 | -0.001442 | 0.042605 | 122.2913 | 122.3226 | 122.1785 | 122.2098
3042.5156 | 122.4289 | -0.064087 | 122.2183 | 0.098959 | 0.009846 | -0.016578 | -0.002124 | 0.013375 | 0.099318 | -0.012357 | 122.2892 | 122.1734 | 122.1672 | 122.0714 | -0.015859 | 0.02322 | -0.024328 | -0.00775 | 0.16305 | 0.073933 | 0.047509 | 0.061963 | 0.077462 | 0.16341 | 0.05173 | 122.3304 | 122.2146 | 122.2084 | 122.1126 | 0.02534 | 0.064419 | 0.016871 | 0.033449 | 122.305 | 122.3135 | 122.1831 | 122.1915
3044.2031 | 122.3145 | -0.091553 | 122.2733 | 0.098959 | 0.014425 | -0.016578 | -0.006703 | 0.004219 | 0.09474 | -0.003201 | 122.28 | 122.1688 | 122.1718 | 122.0759 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.19051 | 0.10598 | 0.074975 | 0.08485 | 0.095772 | 0.18629 | 0.088352 | 122.3212 | 122.21 | 122.213 | 122.1171 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2913 | 122.3089 | 122.1831 | 122.2007
3045.9688 | 122.3328 | -0.091553 | 122.2824 | 0.098959 | 0.014425 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.007779 | 122.2892 | 122.1734 | 122.1672 | 122.0622 | -0.020437 | 0.018642 | -0.033484 | 0.010563 | 0.19051 | 0.10598 | 0.074975 | 0.08485 | 0.095772 | 0.18171 | 0.083774 | 122.3304 | 122.2146 | 122.2084 | 122.1034 | 0.020762 | 0.059841 | 0.007715 | 0.051762 | 122.3096 | 122.3226 | 122.1876 | 122.2007
3047.6562 | 122.3373 | -0.10529 | 122.2733 | 0.098959 | 0.014425 | -0.016578 | -0.002124 | 0.008797 | 0.090161 | -0.003201 | 122.2754 | 122.1734 | 122.1672 | 122.0622 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.20425 | 0.11971 | 0.088708 | 0.10316 | 0.11408 | 0.19545 | 0.10209 | 122.3166 | 122.2146 | 122.2084 | 122.1034 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.2913 | 122.3043 | 122.1831 | 122.1961
3049.4062 | 122.3145 | -0.10986 | 122.2412 | 0.098959 | 0.019004 | -0.021157 | -0.011281 | 0.008797 | 0.090161 | -0.003201 | 122.2892 | 122.1688 | 122.1672 | 122.0714 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.20882 | 0.12887 | 0.088706 | 0.098582 | 0.11866 | 0.20002 | 0.10666 | 122.3304 | 122.21 | 122.2084 | 122.1126 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.3004 | 122.3181 | 122.1785 | 122.1961
3051.1719 | 122.3099 | -0.086975 | 122.2778 | 0.098959 | 0.014425 | -0.012 | -0.006703 | 0.008797 | 0.090161 | 0.001377 | 122.2892 | 122.1734 | 122.1718 | 122.0668 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.18593 | 0.1014 | 0.074975 | 0.080272 | 0.095772 | 0.17714 | 0.088352 | 122.3304 | 122.2146 | 122.213 | 122.108 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.305 | 122.3226 | 122.1876 | 122.2053
3052.9219 | 122.3145 | -0.091553 | 122.2641 | 0.098959 | 0.009846 | -0.007421 | -0.006703 | 0.013375 | 0.090161 | -0.007779 | 122.2846 | 122.178 | 122.1626 | 122.0668 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.19051 | 0.1014 | 0.084132 | 0.08485 | 0.10493 | 0.18171 | 0.083774 | 122.3258 | 122.2192 | 122.2038 | 122.108 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3004 | 122.3135 | 122.1785 | 122.1915
3054.6875 | 122.3694 | -0.091553 | 122.2733 | 0.10354 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.090161 | -0.007779 | 122.2892 | 122.178 | 122.1626 | 122.0668 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.19509 | 0.11056 | 0.074975 | 0.08485 | 0.10493 | 0.18171 | 0.083774 | 122.3304 | 122.2192 | 122.2038 | 122.108 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.305 | 122.3226 | 122.1785 | 122.1961
3056.375 | 122.3694 | -0.086975 | 122.2504 | 0.098959 | 0.019004 | -0.021157 | 0.002454 | 0.004219 | 0.09474 | -0.012357 | 122.28 | 122.1688 | 122.1718 | 122.0668 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.18593 | 0.10598 | 0.065818 | 0.089429 | 0.091194 | 0.18172 | 0.074618 | 122.3212 | 122.21 | 122.213 | 122.108 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.2959 | 122.3181 | 122.1876 | 122.2098
3058.125 | 122.3373 | -0.12817 | 122.2778 | 0.094381 | 0.014425 | -0.021157 | -0.006703 | 0.008797 | 0.090161 | -0.007779 | 122.2754 | 122.1688 | 122.1626 | 122.0759 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.22256 | 0.1426 | 0.10702 | 0.12147 | 0.13697 | 0.21834 | 0.1204 | 122.3166 | 122.21 | 122.2038 | 122.1171 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.2913 | 122.3089 | 122.1785 | 122.1961
3059.8281 | 122.4655 | -0.027466 | 122.2321 | 0.094381 | 0.009846 | -0.021157 | -0.006703 | 0.013375 | 0.090161 | -0.003201 | 122.2892 | 122.1688 | 122.1672 | 122.0668 | -0.025015 | 0.02322 | -0.028906 | -0.003172 | 0.12185 | 0.037312 | 0.006309 | 0.020763 | 0.040841 | 0.11763 | 0.024265 | 122.3304 | 122.21 | 122.2084 | 122.108 | 0.016184 | 0.064419 | 0.012293 | 0.038027 | 122.3142 | 122.3181 | 122.1922 | 122.1961
3061.5781 | 122.4426 | -0.050354 | 122.2137 | 0.098959 | 0.014425 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 122.2937 | 122.1688 | 122.1672 | 122.0759 | -0.020437 | 0.027798 | -0.028906 | -0.00775 | 0.14931 | 0.064779 | 0.033776 | 0.043651 | 0.054573 | 0.13136 | 0.042575 | 122.3349 | 122.21 | 122.2084 | 122.1171 | 0.020762 | 0.068997 | 0.012293 | 0.033449 | 122.3142 | 122.3226 | 122.1876 | 122.1961
3063.3438 | 122.3053 | -0.09613 | 122.2641 | 0.10354 | 0.009846 | -0.007421 | -0.006703 | 0.008797 | 0.09474 | -0.003201 | 122.2846 | 122.178 | 122.1672 | 122.0714 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.19967 | 0.10598 | 0.088709 | 0.089427 | 0.10493 | 0.19087 | 0.092929 | 122.3258 | 122.2192 | 122.2084 | 122.1126 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3004 | 122.3181 | 122.1831 | 122.2007
3065.0469 | 122.4426 | -0.059509 | 122.2412 | 0.098959 | 0.014425 | -0.016578 | -0.002124 | 0.004219 | 0.09474 | -0.007779 | 122.2937 | 122.1642 | 122.1626 | 122.0622 | -0.020437 | 0.02322 | -0.024328 | -0.003172 | 0.15847 | 0.073934 | 0.042931 | 0.057385 | 0.063728 | 0.15425 | 0.05173 | 122.3349 | 122.2054 | 122.2038 | 122.1034 | 0.020762 | 0.064419 | 0.016871 | 0.038027 | 122.3142 | 122.3181 | 122.1831 | 122.1869
3066.7969 | 122.374 | -0.07782 | 122.2321 | 0.098959 | 0.005267 | -0.021157 | -0.002124 | 0.008797 | 0.090161 | -0.007779 | 122.2846 | 122.1688 | 122.1718 | 122.0668 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.17678 | 0.083087 | 0.056663 | 0.075696 | 0.086617 | 0.16798 | 0.070041 | 122.3258 | 122.21 | 122.213 | 122.108 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.305 | 122.3181 | 122.1922 | 122.2053
3068.5625 | 122.3099 | -0.09613 | 122.3007 | 0.098959 | 0.019004 | -0.007421 | -0.006703 | 0.013375 | 0.09474 | -0.003201 | 122.2846 | 122.1688 | 122.1672 | 122.0759 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.19509 | 0.11513 | 0.088709 | 0.089427 | 0.1095 | 0.19087 | 0.092929 | 122.3258 | 122.21 | 122.2084 | 122.1171 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3004 | 122.3135 | 122.1831 | 122.1961
3070.3281 | 122.3511 | -0.10986 | 122.2641 | 0.10812 | 0.019004 | -0.012 | -0.011281 | 0.004219 | 0.090161 | -0.007779 | 122.2846 | 122.1642 | 122.1764 | 122.0668 | -0.020437 | 0.018642 | -0.033484 | 0.001406 | 0.21798 | 0.12887 | 0.097863 | 0.098582 | 0.11408 | 0.20002 | 0.10208 | 122.3258 | 122.2054 | 122.2176 | 122.108 | 0.020762 | 0.059841 | 0.007715 | 0.042605 | 122.305 | 122.3181 | 122.1968 | 122.2098
3072.0156 | 122.4289 | -0.050354 | 122.2092 | 0.098959 | 0.014425 | -0.016578 | -0.011281 | 0.013375 | 0.085583 | -0.007779 | 122.2846 | 122.1734 | 122.1718 | 122.0714 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.14931 | 0.064779 | 0.033776 | 0.039073 | 0.063729 | 0.13594 | 0.042575 | 122.3258 | 122.2146 | 122.213 | 122.1126 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.305 | 122.3181 | 122.1922 | 122.2053
3073.7656 | 122.3923 | -0.050354 | 122.2366 | 0.098959 | 0.019004 | -0.021157 | -0.002124 | 0.004219 | 0.09474 | -0.003201 | 122.2937 | 122.178 | 122.1672 | 122.0668 | -0.020437 | 0.032376 | -0.033484 | -0.003172 | 0.14931 | 0.069358 | 0.029197 | 0.04823 | 0.054573 | 0.14509 | 0.047153 | 122.3349 | 122.2192 | 122.2084 | 122.108 | 0.020762 | 0.073575 | 0.007715 | 0.038027 | 122.3142 | 122.3272 | 122.1876 | 122.2007
3075.5312 | 122.3648 | -0.082397 | 122.2916 | 0.094381 | 0.019004 | -0.016578 | -0.002124 | 0.013375 | 0.09474 | -0.003201 | 122.2937 | 122.178 | 122.1718 | 122.0759 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.17678 | 0.1014 | 0.065819 | 0.080273 | 0.095772 | 0.17714 | 0.079196 | 122.3349 | 122.2192 | 122.213 | 122.1171 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.305 | 122.3272 | 122.1831 | 122.2053
3077.2188 | 122.2916 | -0.10529 | 122.2641 | 0.094381 | 0.023583 | -0.012 | 0.002454 | 0.013375 | 0.090161 | -0.003201 | 122.2892 | 122.178 | 122.1626 | 122.0759 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.19967 | 0.12887 | 0.093286 | 0.10774 | 0.11866 | 0.19545 | 0.10209 | 122.3304 | 122.2192 | 122.2038 | 122.1171 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.305 | 122.3181 | 122.1785 | 122.1915
3078.9844 | 122.3282 | -0.086975 | 122.2961 | 0.10812 | 0.014425 | -0.002842 | -0.006703 | 0.013375 | 0.09474 | -0.007779 | 122.28 | 122.1734 | 122.1718 | 122.0714 | -0.015859 | 0.036954 | -0.038063 | 0.005985 | 0.19509 | 0.1014 | 0.084133 | 0.080272 | 0.10035 | 0.18172 | 0.079196 | 122.3212 | 122.2146 | 122.213 | 122.1126 | 0.02534 | 0.078153 | 0.003136 | 0.047184 | 122.2959 | 122.3181 | 122.1876 | 122.2098
3080.75 | 122.4289 | -0.059509 | 122.2275 | 0.094381 | 0.005267 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.003201 | 122.2754 | 122.1734 | 122.1672 | 122.0714 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.15389 | 0.064776 | 0.038352 | 0.052806 | 0.068306 | 0.14509 | 0.056308 | 122.3166 | 122.2146 | 122.2084 | 122.1126 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.2913 | 122.3135 | 122.1831 | 122.2053
3082.4375 | 122.3328 | -0.10529 | 122.2504 | 0.094381 | 0.019004 | -0.012 | 0.002454 | 0.013375 | 0.09474 | -0.003201 | 122.2892 | 122.1688 | 122.1718 | 122.0668 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 0.19967 | 0.12429 | 0.093286 | 0.10774 | 0.11866 | 0.20003 | 0.10209 | 122.3304 | 122.21 | 122.213 | 122.108 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.3096 | 122.3181 | 122.1922 | 122.2007
3084.1875 | 122.4335 | -0.07782 | 122.2412 | 0.10354 | 0.023583 | -0.016578 | -0.002124 | 0.013375 | 0.09474 | -0.007779 | 122.2892 | 122.1688 | 122.1672 | 122.0759 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.18136 | 0.1014 | 0.061242 | 0.075696 | 0.091195 | 0.17256 | 0.070041 | 122.3304 | 122.21 | 122.2084 | 122.1171 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.3096 | 122.3226 | 122.1876 | 122.2007
3085.8906 | 122.4472 | -0.036621 | 122.2137 | 0.094381 | 0.023583 | -0.012 | -0.002124 | 0.008797 | 0.090161 | -0.012357 | 122.28 | 122.1688 | 122.1672 | 122.0622 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.131 | 0.060204 | 0.024621 | 0.034497 | 0.045418 | 0.12678 | 0.024264 | 122.3212 | 122.21 | 122.2084 | 122.1034 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.2959 | 122.3135 | 122.1831 | 122.2007
3087.6562 | 122.4289 | -0.064087 | 122.2504 | 0.098959 | 0.009846 | -0.016578 | -0.002124 | 0.004219 | 0.090161 | -0.007779 | 122.28 | 122.1688 | 122.1718 | 122.0759 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.16305 | 0.073933 | 0.047509 | 0.061963 | 0.068306 | 0.15425 | 0.056308 | 122.3212 | 122.21 | 122.213 | 122.1171 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2913 | 122.3135 | 122.1831 | 122.2053
3089.3594 | 122.4335 | -0.041199 | 122.2321 | 0.10354 | 0.019004 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.016936 | 122.2846 | 122.1734 | 122.1672 | 122.0622 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.14474 | 0.060203 | 0.024621 | 0.039075 | 0.049996 | 0.1222 | 0.024263 | 122.3258 | 122.2146 | 122.2084 | 122.1034 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.2913 | 122.3181 | 122.1739 | 122.2007
3091.125 | 122.4838 | -0.050354 | 122.2229 | 0.098959 | 0.009846 | -0.012 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 122.2846 | 122.1734 | 122.1626 | 122.0714 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.14931 | 0.0602 | 0.038354 | 0.04823 | 0.059151 | 0.13594 | 0.042575 | 122.3258 | 122.2146 | 122.2038 | 122.1126 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3004 | 122.3181 | 122.1785 | 122.1961
3092.8906 | 122.4335 | -0.064087 | 122.2412 | 0.10354 | 0.014425 | -0.012 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2846 | 122.178 | 122.1718 | 122.0759 | -0.025015 | 0.032376 | -0.028906 | 0.001406 | 0.16762 | 0.078512 | 0.052087 | 0.057384 | 0.072884 | 0.15883 | 0.056308 | 122.3258 | 122.2192 | 122.213 | 122.1171 | 0.016184 | 0.073575 | 0.012293 | 0.042605 | 122.3096 | 122.3135 | 122.1968 | 122.2007
3094.6875 | 122.4106 | -0.059509 | 122.2366 | 0.22258 | 0.03274 | 0.13452 | 0.039082 | 0.004219 | 0.11763 | 0.01969 | 122.2892 | 122.1734 | 122.1672 | 122.0714 | -0.020437 | 0.018642 | -0.038063 | 0.001406 | 0.28208 | 0.092249 | 0.19403 | 0.098591 | 0.063728 | 0.17714 | 0.079199 | 122.3304 | 122.2146 | 122.2084 | 122.1126 | 0.020762 | 0.059841 | 0.003136 | 0.042605 | 122.3096 | 122.3272 | 122.1876 | 122.2053
3096.3906 | 122.3419 | -0.09613 | 122.2366 | 0.098959 | 0.019004 | -0.012 | -0.002124 | 0.013375 | 0.099318 | -0.007779 | 122.2892 | 122.1688 | 122.1764 | 122.0759 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.19509 | 0.11513 | 0.08413 | 0.094006 | 0.1095 | 0.19545 | 0.088351 | 122.3304 | 122.21 | 122.2176 | 122.1171 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.305 | 122.3181 | 122.1922 | 122.2053
3098.1562 | 122.4655 | -0.064087 | 122.2229 | 0.10354 | 0.014425 | -0.021157 | -0.006703 | 0.008797 | 0.09474 | -0.003201 | 122.2892 | 122.1688 | 122.1718 | 122.0714 | -0.006702 | 0.02322 | -0.033484 | -0.003172 | 0.16762 | 0.078512 | 0.04293 | 0.057384 | 0.072884 | 0.15883 | 0.060886 | 122.3304 | 122.21 | 122.213 | 122.1126 | 0.034497 | 0.064419 | 0.007715 | 0.038027 | 122.2959 | 122.3226 | 122.1785 | 122.2053
3099.8438 | 122.374 | -0.10071 | 122.2549 | 0.094381 | 0.028162 | -0.016578 | -0.006703 | 0.013375 | 0.09474 | -0.003201 | 122.2892 | 122.178 | 122.1672 | 122.0668 | -0.015859 | 0.02322 | -0.033484 | -0.00775 | 0.19509 | 0.12887 | 0.08413 | 0.094005 | 0.11408 | 0.19545 | 0.097507 | 122.3304 | 122.2192 | 122.2084 | 122.108 | 0.02534 | 0.064419 | 0.007715 | 0.033449 | 122.305 | 122.3226 | 122.1831 | 122.2007
3101.625 | 122.4289 | -0.059509 | 122.2137 | 0.098959 | 0.023583 | -0.012 | 0.002454 | 0.013375 | 0.090161 | -0.007779 | 122.2846 | 122.1688 | 122.1672 | 122.0714 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.15847 | 0.083092 | 0.047509 | 0.061963 | 0.072884 | 0.14967 | 0.05173 | 122.3258 | 122.21 | 122.2084 | 122.1126 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3004 | 122.3181 | 122.1831 | 122.2007
3103.3125 | 122.4472 | -0.054932 | 122.2366 | 0.098959 | 0.009846 | -0.012 | -0.002124 | 0.008797 | 0.09474 | -0.003201 | 122.2846 | 122.178 | 122.1718 | 122.0759 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.15389 | 0.064778 | 0.042932 | 0.052808 | 0.063729 | 0.14967 | 0.051731 | 122.3258 | 122.2192 | 122.213 | 122.1171 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3004 | 122.3181 | 122.1876 | 122.2053
3105.0625 | 122.3557 | -0.091553 | 122.2504 | 0.098959 | 0.019004 | -0.007421 | -0.002124 | 0.013375 | 0.099318 | -0.003201 | 122.2892 | 122.1688 | 122.1718 | 122.0714 | -0.015859 | 0.018642 | -0.038063 | 0.005985 | 0.19051 | 0.11056 | 0.084132 | 0.089429 | 0.10493 | 0.19087 | 0.088352 | 122.3304 | 122.21 | 122.213 | 122.1126 | 0.02534 | 0.059841 | 0.003136 | 0.047184 | 122.305 | 122.3272 | 122.1876 | 122.2098
3106.7656 | 122.3648 | -0.091553 | 122.2412 | 0.098959 | 0.019004 | -0.007421 | -0.002124 | 0.013375 | 0.090161 | -0.007779 | 122.2937 | 122.178 | 122.1764 | 122.0851 | -0.020437 | 0.032376 | -0.028906 | 0.005985 | 0.19051 | 0.11056 | 0.084132 | 0.089429 | 0.10493 | 0.18171 | 0.083774 | 122.3349 | 122.2192 | 122.2176 | 122.1263 | 0.020762 | 0.073575 | 0.012293 | 0.047184 | 122.3142 | 122.3226 | 122.1968 | 122.2053
3108.5156 | 122.3282 | -0.10071 | 122.2595 | 0.10354 | 0.014425 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 122.2846 | 122.178 | 122.1718 | 122.0714 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.20425 | 0.11513 | 0.088708 | 0.10316 | 0.10951 | 0.18629 | 0.092929 | 122.3258 | 122.2192 | 122.213 | 122.1126 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.2959 | 122.3181 | 122.1831 | 122.2053
3110.2812 | 122.3465 | -0.10529 | 122.2412 | 0.10354 | 0.019004 | -0.007421 | -0.002124 | 0.008797 | 0.090161 | -0.003201 | 122.2892 | 122.1825 | 122.1718 | 122.0714 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.20882 | 0.12429 | 0.097865 | 0.10316 | 0.11408 | 0.19545 | 0.10209 | 122.3304 | 122.2237 | 122.213 | 122.1126 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.305 | 122.3226 | 122.1876 | 122.2053
3112.0469 | 122.3923 | -0.086975 | 122.2687 | 0.10354 | 0.019004 | -0.021157 | -0.002124 | -0.000359 | 0.090161 | -0.012357 | 122.2892 | 122.178 | 122.1718 | 122.0805 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.19051 | 0.10598 | 0.065818 | 0.084851 | 0.086616 | 0.17714 | 0.074618 | 122.3304 | 122.2192 | 122.213 | 122.1217 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.305 | 122.3181 | 122.1876 | 122.2007
3113.75 | 122.4243 | -0.054932 | 122.2412 | 0.098959 | 0.014425 | -0.016578 | -0.002124 | 0.008797 | 0.09474 | -0.007779 | 122.2937 | 122.178 | 122.1764 | 122.0668 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.15389 | 0.069357 | 0.038354 | 0.052808 | 0.063729 | 0.14967 | 0.047153 | 122.3349 | 122.2192 | 122.2176 | 122.108 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.3096 | 122.3272 | 122.1922 | 122.2098
3115.5156 | 122.3785 | -0.10529 | 122.2595 | 0.098959 | 0.023583 | -0.021157 | -0.006703 | 0.013375 | 0.09474 | -0.003201 | 122.2892 | 122.178 | 122.1718 | 122.0759 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.20425 | 0.12887 | 0.084129 | 0.098583 | 0.11866 | 0.20003 | 0.10209 | 122.3304 | 122.2192 | 122.213 | 122.1171 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.305 | 122.3226 | 122.1876 | 122.2053
3117.2656 | 122.4609 | -0.068665 | 122.2092 | 0.098959 | 0.014425 | -0.016578 | -0.002124 | 0.008797 | 0.09474 | -0.007779 | 122.2892 | 122.1688 | 122.1718 | 122.0622 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.16762 | 0.08309 | 0.052087 | 0.066541 | 0.077462 | 0.16341 | 0.060886 | 122.3304 | 122.21 | 122.213 | 122.1034 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.305 | 122.3226 | 122.1876 | 122.2053
3119.0156 | 122.4243 | -0.045776 | 122.2321 | 0.10354 | 0.019004 | -0.012 | -0.011281 | 0.004219 | 0.085583 | -0.003201 | 122.2892 | 122.1825 | 122.1672 | 122.0759 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.14931 | 0.06478 | 0.033776 | 0.034495 | 0.049995 | 0.13136 | 0.042575 | 122.3304 | 122.2237 | 122.2084 | 122.1171 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.3004 | 122.3226 | 122.1785 | 122.2007
3120.7812 | 122.4106 | -0.059509 | 122.2321 | 0.10354 | 0.019004 | -0.016578 | -0.006703 | 0.008797 | 0.090161 | -0.007779 | 122.2937 | 122.1734 | 122.1718 | 122.0714 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.16305 | 0.078513 | 0.042931 | 0.052806 | 0.068306 | 0.14967 | 0.05173 | 122.3349 | 122.2146 | 122.213 | 122.1126 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.3096 | 122.3318 | 122.1876 | 122.2098
3122.4688 | 122.3831 | -0.09613 | 122.2595 | 0.098959 | 0.019004 | -0.012 | -0.002124 | 0.017953 | 0.09474 | 0.001377 | 122.2983 | 122.1734 | 122.1626 | 122.0759 | -0.020437 | 0.018642 | -0.038063 | -0.00775 | 0.19509 | 0.11513 | 0.08413 | 0.094006 | 0.11408 | 0.19087 | 0.097507 | 122.3395 | 122.2146 | 122.2038 | 122.1171 | 0.020762 | 0.059841 | 0.003136 | 0.033449 | 122.3187 | 122.3364 | 122.1831 | 122.2007
3124.2344 | 122.2916 | -0.10071 | 122.2733 | 0.098959 | 0.019004 | -0.012 | -0.006703 | 0.004219 | 0.09474 | -0.003201 | 122.2937 | 122.1825 | 122.1764 | 122.0714 | -0.015859 | 0.02322 | -0.038063 | 0.005985 | 0.19967 | 0.11971 | 0.088708 | 0.094005 | 0.10493 | 0.19545 | 0.097507 | 122.3349 | 122.2237 | 122.2176 | 122.1126 | 0.02534 | 0.064419 | 0.003136 | 0.047184 | 122.3096 | 122.3318 | 122.1922 | 122.2144
3126 | 122.4701 | -0.032043 | 122.2137 | 0.10812 | 0.014425 | -0.012 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2846 | 122.178 | 122.1718 | 122.0622 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.14016 | 0.046468 | 0.020043 | 0.02534 | 0.04084 | 0.12678 | 0.024264 | 122.3258 | 122.2192 | 122.213 | 122.1034 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3004 | 122.3181 | 122.1876 | 122.2053
3127.7031 | 122.4243 | -0.059509 | 122.2549 | 0.098959 | 0.019004 | -0.016578 | -0.006703 | 0.017953 | 0.085583 | -0.012357 | 122.2846 | 122.1734 | 122.1718 | 122.0759 | -0.015859 | 0.02322 | -0.038063 | 0.010563 | 0.15847 | 0.078513 | 0.042931 | 0.052806 | 0.077462 | 0.14509 | 0.047152 | 122.3258 | 122.2146 | 122.213 | 122.1171 | 0.02534 | 0.064419 | 0.003136 | 0.051762 | 122.3004 | 122.3226 | 122.1876 | 122.2098
3129.4531 | 122.4106 | -0.064087 | 122.2321 | 0.094381 | 0.019004 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 122.2892 | 122.1734 | 122.1809 | 122.0714 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.15847 | 0.083091 | 0.047509 | 0.061963 | 0.068306 | 0.14509 | 0.056308 | 122.3304 | 122.2146 | 122.2221 | 122.1126 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3004 | 122.3226 | 122.1922 | 122.2144
3131.2188 | 122.3282 | -0.10986 | 122.2549 | 0.094381 | 0.019004 | -0.016578 | 0.002454 | 0.008797 | 0.090161 | -0.003201 | 122.2892 | 122.1734 | 122.1764 | 122.0759 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.20424 | 0.12887 | 0.093285 | 0.11232 | 0.11866 | 0.20002 | 0.10666 | 122.3304 | 122.2146 | 122.2176 | 122.1171 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.305 | 122.3181 | 122.1922 | 122.2053
3132.9844 | 122.319 | -0.09613 | 122.2595 | 0.094381 | 0.014425 | -0.012 | -0.002124 | 0.008797 | 0.09474 | -0.007779 | 122.2846 | 122.178 | 122.1764 | 122.0759 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.19051 | 0.11055 | 0.08413 | 0.094006 | 0.10493 | 0.19087 | 0.088351 | 122.3258 | 122.2192 | 122.2176 | 122.1171 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3004 | 122.3135 | 122.1922 | 122.2053
3134.75 | 122.4335 | -0.07782 | 122.2321 | 0.098959 | 0.014425 | -0.016578 | -0.006703 | 0.017953 | 0.085583 | -0.003201 | 122.2983 | 122.1734 | 122.1718 | 122.0714 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.17678 | 0.092245 | 0.061242 | 0.071117 | 0.095773 | 0.1634 | 0.074619 | 122.3395 | 122.2146 | 122.213 | 122.1126 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.3142 | 122.3364 | 122.1876 | 122.2098
3136.5156 | 122.3236 | -0.10071 | 122.2733 | 0.094381 | 0.023583 | -0.012 | -0.002124 | 0.013375 | 0.099318 | 0.001377 | 122.2937 | 122.178 | 122.1764 | 122.0668 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.19509 | 0.12429 | 0.088708 | 0.098584 | 0.11408 | 0.20003 | 0.10209 | 122.3349 | 122.2192 | 122.2176 | 122.108 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.305 | 122.3272 | 122.1876 | 122.2098
3138.2031 | 122.4564 | -0.036621 | 122.2092 | 0.098959 | 0.023583 | -0.007421 | -0.006703 | 0.008797 | 0.085583 | 0.001377 | 122.2937 | 122.1734 | 122.1718 | 122.0668 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.13558 | 0.060204 | 0.0292 | 0.029918 | 0.045418 | 0.1222 | 0.037998 | 122.3349 | 122.2146 | 122.213 | 122.108 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.305 | 122.3272 | 122.1831 | 122.2053
3139.9531 | 122.3557 | -0.073242 | 122.2504 | 0.098959 | 0.028162 | -0.002842 | -0.006703 | 0.017953 | 0.09474 | -0.003201 | 122.2846 | 122.1917 | 122.1809 | 122.0851 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.1722 | 0.1014 | 0.0704 | 0.066539 | 0.091195 | 0.16798 | 0.070041 | 122.3258 | 122.2329 | 122.2221 | 122.1263 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3004 | 122.3135 | 122.1968 | 122.2098
3141.7188 | 122.493 | -0.045776 | 122.2137 | 0.10354 | 0.009846 | -0.012 | -0.006703 | 0.008797 | 0.09474 | -0.007779 | 122.2937 | 122.1734 | 122.1764 | 122.0668 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.14931 | 0.055622 | 0.033776 | 0.039073 | 0.054573 | 0.14052 | 0.037997 | 122.3349 | 122.2146 | 122.2176 | 122.108 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3142 | 122.3272 | 122.1968 | 122.2098
3143.4062 | 122.3694 | -0.09613 | 122.2458 | 0.098959 | 0.014425 | -0.007421 | 0.002454 | 0.013375 | 0.090161 | -0.007779 | 122.2892 | 122.1825 | 122.1718 | 122.0805 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.19509 | 0.11055 | 0.088709 | 0.098584 | 0.1095 | 0.18629 | 0.088351 | 122.3304 | 122.2237 | 122.213 | 122.1217 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.305 | 122.3181 | 122.1876 | 122.2007
3145.1562 | 122.3282 | -0.10986 | 122.2595 | 0.10354 | 0.019004 | -0.016578 | -0.006703 | 0.013375 | 0.090161 | -0.003201 | 122.2892 | 122.1688 | 122.1764 | 122.0668 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.2134 | 0.12887 | 0.093285 | 0.10316 | 0.12324 | 0.20002 | 0.10666 | 122.3304 | 122.21 | 122.2176 | 122.108 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3096 | 122.3226 | 122.1968 | 122.2098
3146.9062 | 122.3877 | -0.064087 | 122.2458 | 0.098959 | 0.014425 | -0.012 | -0.006703 | 0.008797 | 0.090161 | -0.012357 | 122.2846 | 122.1734 | 122.1718 | 122.0759 | -0.020437 | 0.027798 | -0.024328 | 0.001406 | 0.16305 | 0.078512 | 0.052087 | 0.057384 | 0.072884 | 0.15425 | 0.05173 | 122.3258 | 122.2146 | 122.213 | 122.1171 | 0.020762 | 0.068997 | 0.016871 | 0.042605 | 122.305 | 122.3089 | 122.1922 | 122.1961
3148.6094 | 122.4014 | -0.073242 | 122.2275 | 0.098959 | 0.023583 | -0.016578 | -0.002124 | 0.013375 | 0.090161 | -0.003201 | 122.2983 | 122.1871 | 122.1672 | 122.0759 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.1722 | 0.096825 | 0.056664 | 0.071118 | 0.086617 | 0.1634 | 0.070041 | 122.3395 | 122.2283 | 122.2084 | 122.1171 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.3187 | 122.3318 | 122.1876 | 122.2007
3150.375 | 122.4152 | -0.064087 | 122.2366 | 0.098959 | 0.023583 | -0.016578 | -0.011281 | 0.008797 | 0.090161 | -0.007779 | 122.2937 | 122.1688 | 122.1672 | 122.0668 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.16305 | 0.08767 | 0.047509 | 0.052806 | 0.072884 | 0.15425 | 0.056308 | 122.3349 | 122.21 | 122.2084 | 122.108 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3096 | 122.3272 | 122.1831 | 122.2007
3152.1562 | 122.4152 | -0.054932 | 122.2321 | 0.094381 | 0.019004 | -0.012 | -0.006703 | 0.017953 | 0.090161 | 0.001377 | 122.2937 | 122.1734 | 122.1718 | 122.0759 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.14931 | 0.073936 | 0.042932 | 0.048229 | 0.072885 | 0.14509 | 0.056309 | 122.3349 | 122.2146 | 122.213 | 122.1171 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.3004 | 122.3272 | 122.1785 | 122.2053
3153.8438 | 122.4518 | -0.050354 | 122.2321 | 0.098959 | 0.028162 | -0.012 | -0.002124 | 0.008797 | 0.09474 | -0.012357 | 122.2892 | 122.1734 | 122.1764 | 122.0759 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.14931 | 0.078516 | 0.038354 | 0.04823 | 0.059151 | 0.14509 | 0.037997 | 122.3304 | 122.2146 | 122.2176 | 122.1171 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.305 | 122.3226 | 122.1922 | 122.2098
3155.5938 | 122.3373 | -0.082397 | 122.2549 | 0.10812 | 0.014425 | -0.002842 | 0.002454 | 0.013375 | 0.090161 | 0.001377 | 122.2846 | 122.1825 | 122.1718 | 122.0759 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.19051 | 0.096822 | 0.079555 | 0.084851 | 0.095772 | 0.17256 | 0.083774 | 122.3258 | 122.2237 | 122.213 | 122.1171 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2959 | 122.3181 | 122.1831 | 122.2053
3157.3594 | 122.3099 | -0.10529 | 122.2641 | 0.10354 | 0.019004 | -0.012 | -0.002124 | 0.013375 | 0.090161 | 0.001377 | 122.2846 | 122.1871 | 122.1764 | 122.0759 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.20882 | 0.12429 | 0.093286 | 0.10316 | 0.11866 | 0.19545 | 0.10666 | 122.3258 | 122.2283 | 122.2176 | 122.1171 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3004 | 122.3181 | 122.1922 | 122.2098
3159.0625 | 122.4289 | -0.054932 | 122.2458 | 0.098959 | 0.019004 | -0.016578 | -0.006703 | 0.004219 | 0.090161 | -0.007779 | 122.2937 | 122.178 | 122.1764 | 122.0805 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.15389 | 0.073936 | 0.038354 | 0.048229 | 0.059151 | 0.14509 | 0.047153 | 122.3349 | 122.2192 | 122.2176 | 122.1217 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3096 | 122.3226 | 122.1922 | 122.2053
3160.8281 | 122.3145 | -0.09613 | 122.2778 | 0.098959 | 0.019004 | -0.002842 | 0.002454 | 0.017953 | 0.099318 | 0.005955 | 122.2892 | 122.1825 | 122.1764 | 122.0668 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.19509 | 0.11513 | 0.093288 | 0.098584 | 0.11408 | 0.19545 | 0.10208 | 122.3304 | 122.2237 | 122.2176 | 122.108 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.305 | 122.3226 | 122.1922 | 122.2098
3162.5938 | 122.3328 | -0.10529 | 122.2778 | 0.10812 | 0.019004 | -0.012 | -0.002124 | 0.013375 | 0.099318 | -0.007779 | 122.2937 | 122.1825 | 122.1718 | 122.0759 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.2134 | 0.12429 | 0.093286 | 0.10316 | 0.11866 | 0.2046 | 0.097507 | 122.3349 | 122.2237 | 122.213 | 122.1171 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3096 | 122.3226 | 122.1876 | 122.2007
3164.3594 | 122.3236 | -0.10529 | 122.2412 | 0.10354 | 0.023583 | -0.012 | 0.002454 | 0.013375 | 0.099318 | -0.007779 | 122.2937 | 122.1734 | 122.1718 | 122.0714 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.20882 | 0.12887 | 0.093286 | 0.10774 | 0.11866 | 0.2046 | 0.097507 | 122.3349 | 122.2146 | 122.213 | 122.1126 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.3004 | 122.3272 | 122.1785 | 122.2053
3166.1094 | 122.3373 | -0.10986 | 122.2549 | 0.10354 | 0.019004 | -0.012 | -0.002124 | 0.004219 | 0.09474 | -0.003201 | 122.2892 | 122.1825 | 122.1809 | 122.0851 | -0.020437 | 0.02322 | -0.028906 | 0.010563 | 0.2134 | 0.12887 | 0.097863 | 0.10774 | 0.11408 | 0.2046 | 0.10666 | 122.3304 | 122.2237 | 122.2221 | 122.1263 | 0.020762 | 0.064419 | 0.012293 | 0.051762 | 122.3096 | 122.3181 | 122.2014 | 122.2098
3167.8125 | 122.4152 | -0.054932 | 122.2321 | 0.10354 | 0.019004 | -0.012 | -0.002124 | 0.013375 | 0.090161 | -0.007779 | 122.2983 | 122.178 | 122.1764 | 122.0714 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.15847 | 0.073936 | 0.042932 | 0.052808 | 0.068307 | 0.14509 | 0.047153 | 122.3395 | 122.2192 | 122.2176 | 122.1126 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3142 | 122.3318 | 122.1922 | 122.2098
3169.5781 | 122.4152 | -0.082397 | 122.2366 | 0.10354 | 0.014425 | -0.012 | -0.006703 | 0.008797 | 0.09474 | -0.003201 | 122.2983 | 122.1734 | 122.1672 | 122.0668 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.18593 | 0.096822 | 0.070397 | 0.075694 | 0.091194 | 0.17714 | 0.079196 | 122.3395 | 122.2146 | 122.2084 | 122.108 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3142 | 122.3318 | 122.1831 | 122.2007
3171.3438 | 122.374 | -0.068665 | 122.2458 | 0.10354 | 0.028162 | -0.012 | 0.002454 | 0.017953 | 0.099318 | 0.001377 | 122.2846 | 122.178 | 122.1809 | 122.0805 | -0.015859 | 0.032376 | -0.024328 | -0.003172 | 0.1722 | 0.096827 | 0.056665 | 0.071119 | 0.086618 | 0.16798 | 0.070042 | 122.3258 | 122.2192 | 122.2221 | 122.1217 | 0.02534 | 0.073575 | 0.016871 | 0.038027 | 122.3004 | 122.3089 | 122.1968 | 122.2053
3173.1094 | 122.4197 | -0.050354 | 122.2183 | 0.10354 | 0.019004 | -0.012 | -0.006703 | 0.017953 | 0.09474 | 0.001377 | 122.2892 | 122.1825 | 122.1718 | 122.0759 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.15389 | 0.069358 | 0.038354 | 0.043651 | 0.068307 | 0.14509 | 0.051731 | 122.3304 | 122.2237 | 122.213 | 122.1171 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.305 | 122.3272 | 122.1876 | 122.2098
3174.7969 | 122.4609 | -0.054932 | 122.2412 | 0.094381 | 0.019004 | -0.007421 | 0.002454 | 0.008797 | 0.09474 | -0.003201 | 122.2846 | 122.1825 | 122.1718 | 122.0805 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.14931 | 0.073936 | 0.047511 | 0.057386 | 0.063729 | 0.14967 | 0.051731 | 122.3258 | 122.2237 | 122.213 | 122.1217 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2959 | 122.3135 | 122.1831 | 122.2007
3176.5625 | 122.3602 | -0.09613 | 122.2595 | 0.098959 | 0.009846 | -0.007421 | 0.002454 | 0.013375 | 0.099318 | -0.003201 | 122.2937 | 122.1734 | 122.1718 | 122.0805 | -0.020437 | 0.02322 | -0.038063 | 0.005985 | 0.19509 | 0.10598 | 0.088709 | 0.098584 | 0.1095 | 0.19545 | 0.092929 | 122.3349 | 122.2146 | 122.213 | 122.1217 | 0.020762 | 0.064419 | 0.003136 | 0.047184 | 122.3142 | 122.3318 | 122.1922 | 122.2098
3178.2656 | 122.3419 | -0.10529 | 122.2687 | 0.10354 | 0.023583 | -0.007421 | 0.002454 | 0.013375 | 0.09474 | 0.001377 | 122.2892 | 122.178 | 122.1764 | 122.0851 | -0.015859 | 0.032376 | -0.033484 | 0.005985 | 0.20882 | 0.12887 | 0.097865 | 0.10774 | 0.11866 | 0.20003 | 0.10666 | 122.3304 | 122.2192 | 122.2176 | 122.1263 | 0.02534 | 0.073575 | 0.007715 | 0.047184 | 122.305 | 122.3226 | 122.1922 | 122.2098
3180.0312 | 122.4976 | -0.091553 | 122.2321 | 0.11269 | 0.037319 | 0.010893 | 0.029925 | 0.027109 | 0.1451 | -0.003201 | 122.2937 | 122.1825 | 122.1764 | 122.0714 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.20425 | 0.12887 | 0.10245 | 0.12148 | 0.11866 | 0.23666 | 0.088352 | 122.3349 | 122.2237 | 122.2176 | 122.1126 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.305 | 122.3272 | 122.1876 | 122.2098
3181.7969 | 122.4518 | -0.10986 | 122.2687 | 0.12185 | 0.03274 | 0.020051 | 0.029925 | 0.031687 | 0.15884 | 0.001377 | 122.2892 | 122.178 | 122.1809 | 122.0805 | -0.015859 | 0.02322 | -0.019749 | 0.010563 | 0.23171 | 0.1426 | 0.12991 | 0.13979 | 0.14155 | 0.2687 | 0.11124 | 122.3304 | 122.2192 | 122.2221 | 122.1217 | 0.02534 | 0.064419 | 0.02145 | 0.051762 | 122.305 | 122.3089 | 122.1968 | 122.2007
3183.5 | 122.374 | -0.09613 | 122.2641 | 0.10812 | 0.023583 | -0.002842 | -0.006703 | 0.013375 | 0.099318 | -0.003201 | 122.2892 | 122.178 | 122.1764 | 122.0759 | -0.015859 | 0.018642 | -0.038063 | 0.001406 | 0.20425 | 0.11971 | 0.093288 | 0.089427 | 0.1095 | 0.19545 | 0.092929 | 122.3304 | 122.2192 | 122.2176 | 122.1171 | 0.02534 | 0.059841 | 0.003136 | 0.042605 | 122.305 | 122.3272 | 122.1922 | 122.2144
3185.2656 | 122.3419 | -0.091553 | 122.2687 | 0.098959 | 0.019004 | -0.007421 | 0.002454 | 0.013375 | 0.099318 | 0.001377 | 122.2892 | 122.178 | 122.1764 | 122.0851 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.19051 | 0.11056 | 0.084132 | 0.094007 | 0.10493 | 0.19087 | 0.09293 | 122.3304 | 122.2192 | 122.2176 | 122.1263 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3004 | 122.3181 | 122.1876 | 122.2053
3186.9688 | 122.3785 | -0.10071 | 122.2824 | 0.10812 | 0.023583 | -0.007421 | 0.002454 | 0.017953 | 0.09474 | -0.007779 | 122.2937 | 122.1825 | 122.1718 | 122.0805 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.20882 | 0.12429 | 0.093287 | 0.10316 | 0.11866 | 0.19545 | 0.092929 | 122.3349 | 122.2237 | 122.213 | 122.1217 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.305 | 122.3272 | 122.1831 | 122.2053
3188.7188 | 122.3236 | -0.09613 | 122.2824 | 0.10812 | 0.023583 | -0.007421 | -0.002124 | 0.022531 | 0.099318 | -0.003201 | 122.2937 | 122.1825 | 122.1718 | 122.0759 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.20425 | 0.11971 | 0.088709 | 0.094006 | 0.11866 | 0.19545 | 0.092929 | 122.3349 | 122.2237 | 122.213 | 122.1171 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3142 | 122.3226 | 122.1922 | 122.2007
3190.4688 | 122.4243 | -0.045776 | 122.2366 | 0.094381 | 0.019004 | -0.012 | -0.002124 | 0.017953 | 0.090161 | -0.003201 | 122.2983 | 122.178 | 122.1718 | 122.0759 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.14016 | 0.06478 | 0.033776 | 0.043652 | 0.063729 | 0.13594 | 0.042575 | 122.3395 | 122.2192 | 122.213 | 122.1171 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.3142 | 122.3318 | 122.1876 | 122.2053
3192.1875 | 122.3511 | -0.11902 | 122.2778 | 0.10354 | 0.019004 | -0.007421 | 0.002454 | 0.022531 | 0.099318 | -0.003201 | 122.2983 | 122.1825 | 122.1764 | 122.0759 | -0.025015 | 0.02322 | -0.033484 | 0.001406 | 0.22256 | 0.13802 | 0.1116 | 0.12147 | 0.14155 | 0.21834 | 0.11582 | 122.3395 | 122.2237 | 122.2176 | 122.1171 | 0.016184 | 0.064419 | 0.007715 | 0.042605 | 122.3233 | 122.3318 | 122.2014 | 122.2098
3193.9531 | 122.4792 | -0.059509 | 122.2412 | 0.094381 | 0.019004 | -0.007421 | -0.002124 | 0.013375 | 0.09474 | 0.001377 | 122.2983 | 122.1825 | 122.1764 | 122.0759 | -0.025015 | 0.02322 | -0.033484 | 0.005985 | 0.15389 | 0.078513 | 0.052088 | 0.057385 | 0.072884 | 0.15425 | 0.060886 | 122.3395 | 122.2237 | 122.2176 | 122.1171 | 0.016184 | 0.064419 | 0.007715 | 0.047184 | 122.3233 | 122.3318 | 122.2014 | 122.2098
3195.7031 | 122.493 | -0.045776 | 122.2366 | 0.098959 | 0.019004 | -0.007421 | -0.006703 | 0.017953 | 0.090161 | -0.003201 | 122.2892 | 122.1825 | 122.1764 | 122.0805 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.14474 | 0.06478 | 0.038355 | 0.039073 | 0.063729 | 0.13594 | 0.042575 | 122.3304 | 122.2237 | 122.2176 | 122.1217 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3096 | 122.3226 | 122.1968 | 122.2098
3197.4688 | 122.3419 | -0.10986 | 122.2778 | 0.098959 | 0.019004 | -0.012 | 0.007033 | 0.013375 | 0.09474 | 0.001377 | 122.2937 | 122.1734 | 122.1718 | 122.0805 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.20882 | 0.12887 | 0.097863 | 0.1169 | 0.12324 | 0.2046 | 0.11124 | 122.3349 | 122.2146 | 122.213 | 122.1217 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.305 | 122.3272 | 122.1831 | 122.2053
3199.2344 | 122.3694 | -0.086975 | 122.2549 | 0.10354 | 0.023583 | -0.002842 | 0.002454 | 0.017953 | 0.099318 | 0.005955 | 122.2892 | 122.1825 | 122.1809 | 122.0805 | -0.015859 | 0.027798 | -0.024328 | -0.00775 | 0.19051 | 0.11056 | 0.084133 | 0.089429 | 0.10493 | 0.18629 | 0.09293 | 122.3304 | 122.2237 | 122.2221 | 122.1217 | 0.02534 | 0.068997 | 0.016871 | 0.033449 | 122.305 | 122.3135 | 122.1968 | 122.2053
3200.9375 | 122.3145 | -0.09613 | 122.2916 | 0.098959 | 0.023583 | 0.001736 | 0.007033 | 0.017953 | 0.099318 | 0.001377 | 122.2846 | 122.1825 | 122.1718 | 122.0759 | -0.015859 | 0.018642 | -0.028906 | 0.001406 | 0.19509 | 0.11971 | 0.097866 | 0.10316 | 0.11408 | 0.19545 | 0.097507 | 122.3258 | 122.2237 | 122.213 | 122.1171 | 0.02534 | 0.059841 | 0.012293 | 0.042605 | 122.3004 | 122.3135 | 122.1876 | 122.2007
3202.6406 | 122.3831 | -0.091553 | 122.2595 | 0.10354 | 0.028162 | -0.007421 | 0.002454 | 0.017953 | 0.09474 | 0.001377 | 122.2937 | 122.1871 | 122.1718 | 122.0805 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.19509 | 0.11971 | 0.084132 | 0.094007 | 0.10951 | 0.18629 | 0.09293 | 122.3349 | 122.2283 | 122.213 | 122.1217 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3096 | 122.3226 | 122.1876 | 122.2007
3204.3906 | 122.3465 | -0.10529 | 122.2412 | 0.094381 | 0.028162 | -0.002842 | 0.007033 | 0.022531 | 0.1039 | -0.003201 | 122.2937 | 122.1871 | 122.1718 | 122.0759 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.19967 | 0.13345 | 0.10244 | 0.11232 | 0.12782 | 0.20918 | 0.10209 | 122.3349 | 122.2283 | 122.213 | 122.1171 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3096 | 122.3272 | 122.1876 | 122.2053
3206.1562 | 122.3465 | -0.10529 | 122.2687 | 0.094381 | 0.023583 | 0.001736 | 0.002454 | 0.017953 | 0.09474 | 0.001377 | 122.2937 | 122.178 | 122.1718 | 122.0851 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.19967 | 0.12887 | 0.10702 | 0.10774 | 0.12324 | 0.20003 | 0.10666 | 122.3349 | 122.2192 | 122.213 | 122.1263 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.305 | 122.3226 | 122.1831 | 122.2007
3207.8594 | 122.4701 | -0.068665 | 122.2366 | 0.098959 | 0.028162 | -0.012 | -0.002124 | 0.017953 | 0.090161 | -0.003201 | 122.2892 | 122.1734 | 122.1672 | 122.0805 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.16762 | 0.096827 | 0.056665 | 0.066541 | 0.086618 | 0.15883 | 0.065464 | 122.3304 | 122.2146 | 122.2084 | 122.1217 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.305 | 122.3226 | 122.1831 | 122.2007
3209.625 | 122.4747 | -0.068665 | 122.2137 | 0.094381 | 0.019004 | -0.002842 | 0.002454 | 0.013375 | 0.09474 | 0.005955 | 122.2937 | 122.178 | 122.1764 | 122.0805 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.16305 | 0.087669 | 0.065823 | 0.071119 | 0.08204 | 0.16341 | 0.07462 | 122.3349 | 122.2192 | 122.2176 | 122.1217 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.3096 | 122.3318 | 122.1922 | 122.2144
3211.3906 | 122.4518 | -0.054932 | 122.2229 | 0.10354 | 0.028162 | -0.002842 | 0.002454 | 0.008797 | 0.099318 | -0.007779 | 122.2937 | 122.178 | 122.1764 | 122.0805 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.15847 | 0.083094 | 0.05209 | 0.057386 | 0.063729 | 0.15425 | 0.047153 | 122.3349 | 122.2192 | 122.2176 | 122.1217 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.305 | 122.3272 | 122.1876 | 122.2098
3213.0938 | 122.3236 | -0.09613 | 122.2321 | 0.094381 | 0.023583 | -0.002842 | 0.002454 | 0.022531 | 0.099318 | 0.005955 | 122.2983 | 122.178 | 122.1718 | 122.0759 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.19051 | 0.11971 | 0.093288 | 0.098584 | 0.11866 | 0.19545 | 0.10208 | 122.3395 | 122.2192 | 122.213 | 122.1171 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.3142 | 122.3272 | 122.1876 | 122.2007
3214.8594 | 122.3511 | -0.10529 | 122.2733 | 0.098959 | 0.028162 | 0.001736 | 0.002454 | 0.017953 | 0.1039 | 0.001377 | 122.2983 | 122.1825 | 122.1764 | 122.0759 | -0.015859 | 0.02322 | -0.042641 | -0.003172 | 0.20425 | 0.13345 | 0.10702 | 0.10774 | 0.12324 | 0.20918 | 0.10666 | 122.3395 | 122.2237 | 122.2176 | 122.1171 | 0.02534 | 0.064419 | -0.001442 | 0.038027 | 122.3142 | 122.341 | 122.1922 | 122.219
3216.6406 | 122.3282 | -0.10986 | 122.2641 | 0.094381 | 0.023583 | -0.002842 | 0.002454 | 0.022531 | 0.1039 | 0.001377 | 122.2937 | 122.1871 | 122.1809 | 122.0805 | -0.015859 | 0.036954 | -0.028906 | 0.005985 | 0.20424 | 0.13345 | 0.10702 | 0.11232 | 0.13239 | 0.21376 | 0.11124 | 122.3349 | 122.2283 | 122.2221 | 122.1217 | 0.02534 | 0.078153 | 0.012293 | 0.047184 | 122.3096 | 122.3226 | 122.1968 | 122.2098
3218.4062 | 122.3282 | -0.10986 | 122.2778 | 0.10354 | 0.019004 | -0.007421 | 0.002454 | 0.022531 | 0.1039 | 0.001377 | 122.2892 | 122.1871 | 122.1718 | 122.0759 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.2134 | 0.12887 | 0.10244 | 0.11232 | 0.13239 | 0.21376 | 0.11124 | 122.3304 | 122.2283 | 122.213 | 122.1171 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.3004 | 122.3181 | 122.1831 | 122.2007
3220.1562 | 122.3328 | -0.082397 | 122.2733 | 0.098959 | 0.028162 | 0.001736 | 0.007033 | 0.022531 | 0.1039 | 0.005955 | 122.2892 | 122.178 | 122.1764 | 122.0805 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.18136 | 0.11056 | 0.084133 | 0.08943 | 0.10493 | 0.18629 | 0.088352 | 122.3304 | 122.2192 | 122.2176 | 122.1217 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.305 | 122.3226 | 122.1922 | 122.2098
3221.8594 | 122.3602 | -0.091553 | 122.2595 | 0.10354 | 0.023583 | -0.002842 | 0.002454 | 0.017953 | 0.10848 | 0.001377 | 122.2983 | 122.178 | 122.1718 | 122.0759 | -0.025015 | 0.027798 | -0.033484 | 0.001406 | 0.19509 | 0.11514 | 0.088711 | 0.094007 | 0.10951 | 0.20003 | 0.09293 | 122.3395 | 122.2192 | 122.213 | 122.1171 | 0.016184 | 0.068997 | 0.007715 | 0.042605 | 122.3233 | 122.3318 | 122.1968 | 122.2053
3223.625 | 122.3419 | -0.10529 | 122.2961 | 0.098959 | 0.023583 | -0.007421 | 0.007033 | 0.022531 | 0.09474 | -0.003201 | 122.3029 | 122.178 | 122.1764 | 122.0805 | -0.011281 | 0.018642 | -0.038063 | -0.003172 | 0.20425 | 0.12887 | 0.097865 | 0.11232 | 0.12782 | 0.20003 | 0.10209 | 122.3441 | 122.2192 | 122.2176 | 122.1217 | 0.029918 | 0.059841 | 0.003136 | 0.038027 | 122.3142 | 122.341 | 122.1876 | 122.2144
3225.3281 | 122.4197 | -0.064087 | 122.2504 | 0.10354 | 0.03274 | -0.002842 | 0.002454 | 0.022531 | 0.09474 | 0.010533 | 122.2983 | 122.178 | 122.1764 | 122.0805 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.16762 | 0.096827 | 0.061245 | 0.066541 | 0.086618 | 0.15883 | 0.07462 | 122.3395 | 122.2192 | 122.2176 | 122.1217 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3142 | 122.3272 | 122.1922 | 122.2053
3227.0938 | 122.4609 | -0.050354 | 122.2412 | 0.098959 | 0.028162 | -0.002842 | -0.002124 | 0.022531 | 0.09474 | 0.001377 | 122.2983 | 122.1871 | 122.1764 | 122.0805 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.14931 | 0.078516 | 0.047512 | 0.04823 | 0.072885 | 0.14509 | 0.051731 | 122.3395 | 122.2283 | 122.2176 | 122.1217 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3096 | 122.3318 | 122.1876 | 122.2098
3228.7812 | 122.3145 | -0.10529 | 122.2778 | 0.10354 | 0.028162 | -0.002842 | 0.011611 | 0.022531 | 0.1039 | 0.001377 | 122.2937 | 122.1825 | 122.1718 | 122.0805 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.20882 | 0.13345 | 0.10244 | 0.1169 | 0.12782 | 0.20918 | 0.10666 | 122.3349 | 122.2237 | 122.213 | 122.1217 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3096 | 122.3226 | 122.1876 | 122.2007
3230.5312 | 122.3282 | -0.10071 | 122.2778 | 0.098959 | 0.028162 | -0.002842 | 0.007033 | 0.027109 | 0.099318 | 0.001377 | 122.2983 | 122.1871 | 122.1809 | 122.0714 | -0.011281 | 0.018642 | -0.038063 | 0.001406 | 0.19967 | 0.12887 | 0.097866 | 0.10774 | 0.12782 | 0.20003 | 0.10209 | 122.3395 | 122.2283 | 122.2221 | 122.1126 | 0.029918 | 0.059841 | 0.003136 | 0.042605 | 122.3096 | 122.3364 | 122.1922 | 122.219
3232.2812 | 122.3557 | -0.091553 | 122.2412 | 0.10812 | 0.023583 | -0.002842 | 0.002454 | 0.017953 | 0.099318 | 0.001377 | 122.2983 | 122.1825 | 122.1764 | 122.0714 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.19967 | 0.11514 | 0.088711 | 0.094007 | 0.10951 | 0.19087 | 0.09293 | 122.3395 | 122.2237 | 122.2176 | 122.1126 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3142 | 122.3318 | 122.1922 | 122.2098
3234.0469 | 122.3282 | -0.11444 | 122.2641 | 0.10354 | 0.023583 | -0.007421 | 0.007033 | 0.027109 | 0.1039 | -0.003201 | 122.2937 | 122.178 | 122.1718 | 122.0759 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.21798 | 0.13802 | 0.10702 | 0.12147 | 0.14155 | 0.21834 | 0.11124 | 122.3349 | 122.2192 | 122.213 | 122.1171 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3096 | 122.3272 | 122.1876 | 122.2053
3235.7344 | 122.4518 | -0.07782 | 122.2275 | 0.098959 | 0.028162 | -0.012 | 0.002454 | 0.022531 | 0.090161 | 0.001377 | 122.2983 | 122.1734 | 122.1809 | 122.0805 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.17678 | 0.10598 | 0.06582 | 0.080274 | 0.10035 | 0.16798 | 0.079197 | 122.3395 | 122.2146 | 122.2221 | 122.1217 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3096 | 122.3318 | 122.1922 | 122.2144
3237.5 | 122.3282 | -0.10529 | 122.2733 | 0.094381 | 0.028162 | -0.002842 | 0.007033 | 0.022531 | 0.099318 | 0.001377 | 122.2892 | 122.1825 | 122.1809 | 122.0759 | -0.015859 | 0.02322 | -0.033484 | -0.00775 | 0.19967 | 0.13345 | 0.10244 | 0.11232 | 0.12782 | 0.2046 | 0.10666 | 122.3304 | 122.2237 | 122.2221 | 122.1171 | 0.02534 | 0.064419 | 0.007715 | 0.033449 | 122.305 | 122.3226 | 122.1968 | 122.2144
3239.2656 | 122.3923 | -0.082397 | 122.2595 | 0.098959 | 0.023583 | -0.002842 | -0.002124 | 0.022531 | 0.1039 | 0.005955 | 122.2937 | 122.178 | 122.1764 | 122.0759 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.18136 | 0.10598 | 0.079555 | 0.080273 | 0.10493 | 0.18629 | 0.088352 | 122.3349 | 122.2192 | 122.2176 | 122.1171 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3096 | 122.3226 | 122.1922 | 122.2053
3241.0312 | 122.4838 | -0.050354 | 122.2275 | 0.089802 | 0.023583 | -0.002842 | 0.002454 | 0.017953 | 0.09474 | -0.003201 | 122.2983 | 122.178 | 122.1764 | 122.0759 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.14016 | 0.073937 | 0.047512 | 0.052808 | 0.068307 | 0.14509 | 0.047153 | 122.3395 | 122.2192 | 122.2176 | 122.1171 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3142 | 122.3272 | 122.1922 | 122.2053
3242.7969 | 122.4701 | -0.032043 | 122.2458 | 0.10354 | 0.023583 | -0.002842 | 0.020768 | 0.022531 | 0.099318 | 0.005955 | 122.2983 | 122.178 | 122.1764 | 122.0805 | -0.025015 | 0.032376 | -0.028906 | 0.001406 | 0.13558 | 0.055626 | 0.029201 | 0.052811 | 0.054574 | 0.13136 | 0.037998 | 122.3395 | 122.2192 | 122.2176 | 122.1217 | 0.016184 | 0.073575 | 0.012293 | 0.042605 | 122.3233 | 122.3272 | 122.2014 | 122.2053
3244.5 | 122.3923 | -0.073242 | 122.2549 | 0.098959 | 0.023583 | -0.002842 | 0.002454 | 0.017953 | 0.099318 | 0.001377 | 122.2937 | 122.1871 | 122.1764 | 122.0897 | -0.020437 | 0.02322 | -0.028906 | 0.005985 | 0.1722 | 0.096825 | 0.0704 | 0.075696 | 0.091195 | 0.17256 | 0.074619 | 122.3349 | 122.2283 | 122.2176 | 122.1309 | 0.020762 | 0.064419 | 0.012293 | 0.047184 | 122.3142 | 122.3226 | 122.1968 | 122.2053
3246.2656 | 122.3419 | -0.09613 | 122.2824 | 0.094381 | 0.03274 | -0.002842 | 0.002454 | 0.017953 | 0.099318 | 0.010533 | 122.2937 | 122.178 | 122.1718 | 122.0759 | -0.002124 | 0.032376 | -0.033484 | 0.001406 | 0.19051 | 0.12887 | 0.093288 | 0.098584 | 0.11408 | 0.19545 | 0.10666 | 122.3349 | 122.2192 | 122.213 | 122.1171 | 0.039075 | 0.073575 | 0.007715 | 0.042605 | 122.2959 | 122.3272 | 122.1739 | 122.2053
3248.0312 | 122.3282 | -0.07782 | 122.2778 | 0.098959 | 0.03274 | -0.002842 | 0.011611 | 0.022531 | 0.099318 | 0.001377 | 122.2983 | 122.1825 | 122.1764 | 122.0851 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.17678 | 0.11056 | 0.074978 | 0.089431 | 0.10035 | 0.17714 | 0.079197 | 122.3395 | 122.2237 | 122.2176 | 122.1263 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3142 | 122.3272 | 122.1922 | 122.2053
3249.7344 | 122.3785 | -0.086975 | 122.2504 | 0.098959 | 0.028162 | 0.001736 | 0.011611 | 0.027109 | 0.1039 | 0.005955 | 122.2983 | 122.1825 | 122.1764 | 122.0805 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.18593 | 0.11514 | 0.088711 | 0.098586 | 0.11408 | 0.19087 | 0.09293 | 122.3395 | 122.2237 | 122.2176 | 122.1217 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.3096 | 122.3272 | 122.1876 | 122.2053
3251.4844 | 122.4152 | -0.086975 | 122.2549 | 0.094381 | 0.028162 | -0.002842 | 0.002454 | 0.022531 | 0.1039 | 0.010533 | 122.3029 | 122.1825 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.024328 | 0.005985 | 0.18136 | 0.11514 | 0.084133 | 0.089429 | 0.10951 | 0.19087 | 0.097508 | 122.3441 | 122.2237 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.016871 | 0.047184 | 122.3187 | 122.3272 | 122.1922 | 122.2007
3253.2344 | 122.3602 | -0.091553 | 122.2412 | 0.098959 | 0.023583 | -0.002842 | 0.011611 | 0.027109 | 0.099318 | 0.005955 | 122.3029 | 122.1871 | 122.1672 | 122.0851 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 0.19051 | 0.11514 | 0.088711 | 0.10316 | 0.11866 | 0.19087 | 0.097508 | 122.3441 | 122.2283 | 122.2084 | 122.1263 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 122.3142 | 122.3364 | 122.1785 | 122.2007
3255 | 122.3465 | -0.10986 | 122.2824 | 0.10354 | 0.037319 | -0.002842 | 0.007033 | 0.031687 | 0.10848 | 0.005955 | 122.2983 | 122.1825 | 122.1764 | 122.0759 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.2134 | 0.14718 | 0.10702 | 0.1169 | 0.14155 | 0.21834 | 0.11582 | 122.3395 | 122.2237 | 122.2176 | 122.1171 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3187 | 122.3318 | 122.1968 | 122.2098
3256.7031 | 122.3419 | -0.10071 | 122.2733 | 0.098959 | 0.028162 | -0.007421 | 0.002454 | 0.027109 | 0.10848 | 0.005955 | 122.3029 | 122.178 | 122.1764 | 122.0805 | -0.011281 | 0.027798 | -0.042641 | 0.001406 | 0.19967 | 0.12887 | 0.093287 | 0.10316 | 0.12782 | 0.20918 | 0.10666 | 122.3441 | 122.2192 | 122.2176 | 122.1217 | 0.029918 | 0.068997 | -0.001442 | 0.042605 | 122.3142 | 122.3455 | 122.1876 | 122.219
3258.4688 | 122.4152 | -0.068665 | 122.2549 | 0.094381 | 0.028162 | -0.007421 | 0.007033 | 0.022531 | 0.099318 | -0.003201 | 122.2983 | 122.1871 | 122.1718 | 122.0851 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.16305 | 0.096827 | 0.061244 | 0.075698 | 0.091196 | 0.16798 | 0.065464 | 122.3395 | 122.2283 | 122.213 | 122.1263 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.3142 | 122.3364 | 122.1876 | 122.2098
3260.1719 | 122.3511 | -0.09613 | 122.2687 | 0.098959 | 0.023583 | -0.002842 | 0.007033 | 0.027109 | 0.1039 | 0.001377 | 122.2983 | 122.1825 | 122.1718 | 122.0805 | -0.015859 | 0.018642 | -0.028906 | 0.005985 | 0.19509 | 0.11971 | 0.093288 | 0.10316 | 0.12324 | 0.20003 | 0.097507 | 122.3395 | 122.2237 | 122.213 | 122.1217 | 0.02534 | 0.059841 | 0.012293 | 0.047184 | 122.3142 | 122.3272 | 122.1876 | 122.2007
3261.9375 | 122.4472 | -0.045776 | 122.2229 | 0.10354 | 0.03274 | 0.001736 | 0.002454 | 0.022531 | 0.09474 | 0.005955 | 122.2983 | 122.1825 | 122.1718 | 122.0805 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.14931 | 0.078516 | 0.047512 | 0.04823 | 0.068307 | 0.14052 | 0.051731 | 122.3395 | 122.2237 | 122.213 | 122.1217 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.3187 | 122.3318 | 122.1922 | 122.2053
3263.7031 | 122.3373 | -0.086975 | 122.2504 | 0.098959 | 0.03274 | 0.001736 | 0.011611 | 0.031687 | 0.099318 | 0.010533 | 122.2937 | 122.178 | 122.1809 | 122.0805 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.18593 | 0.11971 | 0.088711 | 0.098586 | 0.11866 | 0.18629 | 0.097508 | 122.3349 | 122.2192 | 122.2221 | 122.1217 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.305 | 122.3226 | 122.1922 | 122.2098
3265.3906 | 122.4701 | -0.064087 | 122.2412 | 0.10354 | 0.028162 | 0.006315 | 0.011611 | 0.022531 | 0.10848 | 0.005955 | 122.2983 | 122.1825 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.16762 | 0.092249 | 0.070402 | 0.075698 | 0.086618 | 0.17256 | 0.070042 | 122.3395 | 122.2237 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3142 | 122.3318 | 122.1922 | 122.2098
3267.1562 | 122.3465 | -0.10529 | 122.287 | 0.098959 | 0.03274 | 0.006315 | 0.007033 | 0.017953 | 0.1039 | 0.010533 | 122.2937 | 122.1871 | 122.1718 | 122.0851 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.20425 | 0.13803 | 0.1116 | 0.11232 | 0.12324 | 0.20918 | 0.11582 | 122.3349 | 122.2283 | 122.213 | 122.1263 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.305 | 122.3226 | 122.1831 | 122.2007
3268.9219 | 122.4609 | -0.059509 | 122.2275 | 0.10812 | 0.028162 | -0.002842 | 0.007033 | 0.022531 | 0.1039 | 0.001377 | 122.2937 | 122.1871 | 122.1764 | 122.0805 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.16762 | 0.087671 | 0.056667 | 0.066542 | 0.08204 | 0.1634 | 0.060886 | 122.3349 | 122.2283 | 122.2176 | 122.1217 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.305 | 122.3226 | 122.1876 | 122.2053
3270.6719 | 122.4335 | -0.054932 | 122.2229 | 0.10812 | 0.03274 | 0.010893 | 0.011611 | 0.022531 | 0.09474 | 0.001377 | 122.3029 | 122.1825 | 122.1764 | 122.0805 | -0.020437 | 0.018642 | -0.028906 | 0.005985 | 0.16305 | 0.087672 | 0.065825 | 0.066543 | 0.077463 | 0.14967 | 0.056309 | 122.3441 | 122.2237 | 122.2176 | 122.1217 | 0.020762 | 0.059841 | 0.012293 | 0.047184 | 122.3233 | 122.3318 | 122.1968 | 122.2053
3272.375 | 122.3557 | -0.091553 | 122.2778 | 0.10354 | 0.03274 | 0.001736 | 0.007033 | 0.022531 | 0.10848 | 0.010533 | 122.3075 | 122.1825 | 122.1764 | 122.0851 | -0.011281 | 0.018642 | -0.024328 | 0.001406 | 0.19509 | 0.12429 | 0.093289 | 0.098586 | 0.11408 | 0.20003 | 0.10209 | 122.3487 | 122.2237 | 122.2176 | 122.1263 | 0.029918 | 0.059841 | 0.016871 | 0.042605 | 122.3187 | 122.3318 | 122.1876 | 122.2007
3274.1406 | 122.4472 | -0.045776 | 122.2366 | 0.10354 | 0.03274 | 0.001736 | 0.01619 | 0.022531 | 0.1039 | 0.005955 | 122.312 | 122.1825 | 122.1764 | 122.0805 | -0.015859 | 0.032376 | -0.033484 | 0.005985 | 0.14931 | 0.078516 | 0.047512 | 0.061966 | 0.068307 | 0.14967 | 0.051731 | 122.3532 | 122.2237 | 122.2176 | 122.1217 | 0.02534 | 0.073575 | 0.007715 | 0.047184 | 122.3279 | 122.3455 | 122.1922 | 122.2098
3275.875 | 122.3373 | -0.10986 | 122.2641 | 0.098959 | 0.037319 | -0.002842 | 0.002454 | 0.027109 | 0.099318 | 0.015112 | 122.2937 | 122.1871 | 122.1718 | 122.0805 | -0.015859 | 0.027798 | -0.028906 | -0.00775 | 0.20882 | 0.14718 | 0.10702 | 0.11232 | 0.13697 | 0.20918 | 0.12498 | 122.3349 | 122.2283 | 122.213 | 122.1217 | 0.02534 | 0.068997 | 0.012293 | 0.033449 | 122.3096 | 122.3226 | 122.1876 | 122.2007
3277.6406 | 122.319 | -0.086975 | 122.2504 | 0.10354 | 0.037319 | 0.006315 | 0.01619 | 0.031687 | 0.1039 | 0.015112 | 122.3029 | 122.1871 | 122.1809 | 122.0851 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.19051 | 0.12429 | 0.09329 | 0.10316 | 0.11866 | 0.19087 | 0.10209 | 122.3441 | 122.2283 | 122.2221 | 122.1263 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3142 | 122.3318 | 122.1922 | 122.2098
3279.4219 | 122.4884 | -0.050354 | 122.2 | 0.10812 | 0.03274 | -0.002842 | 0.01619 | 0.027109 | 0.1039 | 0.005955 | 122.2983 | 122.1825 | 122.1718 | 122.0805 | -0.015859 | 0.032376 | -0.024328 | 0.005985 | 0.15847 | 0.083094 | 0.047512 | 0.066544 | 0.077463 | 0.15425 | 0.056309 | 122.3395 | 122.2237 | 122.213 | 122.1217 | 0.02534 | 0.073575 | 0.016871 | 0.047184 | 122.3142 | 122.3226 | 122.1876 | 122.1961
3281.125 | 122.3648 | -0.09613 | 122.2321 | 0.10354 | 0.028162 | 0.006315 | 0.01619 | 0.031687 | 0.10848 | 0.015112 | 122.2983 | 122.1871 | 122.1855 | 122.0851 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.19967 | 0.12429 | 0.10244 | 0.11232 | 0.12782 | 0.2046 | 0.11124 | 122.3395 | 122.2283 | 122.2267 | 122.1263 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.3142 | 122.3364 | 122.2014 | 122.2236
3282.875 | 122.3511 | -0.09613 | 122.2595 | 0.10354 | 0.028162 | -0.002842 | 0.011611 | 0.031687 | 0.1039 | 0.010533 | 122.3029 | 122.1871 | 122.1764 | 122.0805 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.19967 | 0.12429 | 0.093288 | 0.10774 | 0.12782 | 0.20003 | 0.10666 | 122.3441 | 122.2283 | 122.2176 | 122.1217 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3187 | 122.3364 | 122.1922 | 122.2098
3284.6406 | 122.4838 | -0.032043 | 122.2183 | 0.094381 | 0.03274 | 0.001736 | 0.007033 | 0.027109 | 0.1039 | 0.010533 | 122.2937 | 122.1825 | 122.1672 | 122.0805 | -0.015859 | 0.027798 | -0.033484 | 0.010563 | 0.12642 | 0.064783 | 0.033779 | 0.039076 | 0.059152 | 0.13594 | 0.042576 | 122.3349 | 122.2237 | 122.2084 | 122.1217 | 0.02534 | 0.068997 | 0.007715 | 0.051762 | 122.3096 | 122.3272 | 122.1831 | 122.2007
3286.3906 | 122.438 | -0.036621 | 122.2137 | 0.098959 | 0.03274 | 0.006315 | 0.007033 | 0.036265 | 0.1039 | 0.010533 | 122.2937 | 122.1871 | 122.1764 | 122.0805 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.13558 | 0.069361 | 0.042936 | 0.043654 | 0.072886 | 0.14052 | 0.047154 | 122.3349 | 122.2283 | 122.2176 | 122.1217 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.305 | 122.3226 | 122.1876 | 122.2053
3288.0781 | 122.3648 | -0.09613 | 122.2778 | 0.10354 | 0.041898 | 0.006315 | 0.01619 | 0.036265 | 0.10848 | 0.015112 | 122.2983 | 122.1871 | 122.1764 | 122.0805 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.19967 | 0.13803 | 0.10244 | 0.11232 | 0.13239 | 0.2046 | 0.11124 | 122.3395 | 122.2283 | 122.2176 | 122.1217 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3187 | 122.3318 | 122.1968 | 122.2098
3289.8438 | 122.4426 | -0.054932 | 122.2321 | 0.094381 | 0.03274 | 0.001736 | 0.011611 | 0.022531 | 0.10848 | 0.015112 | 122.2983 | 122.1917 | 122.1718 | 122.0805 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.14931 | 0.087672 | 0.056668 | 0.066543 | 0.077463 | 0.16341 | 0.070044 | 122.3395 | 122.2329 | 122.213 | 122.1217 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.3096 | 122.3318 | 122.1831 | 122.2053
3291.6094 | 122.3602 | -0.07782 | 122.2824 | 0.094381 | 0.037319 | 0.006315 | 0.011611 | 0.036265 | 0.10848 | 0.01969 | 122.3029 | 122.1871 | 122.1809 | 122.0851 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 0.1722 | 0.11514 | 0.084135 | 0.089431 | 0.11408 | 0.18629 | 0.09751 | 122.3441 | 122.2283 | 122.2221 | 122.1263 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.3233 | 122.3318 | 122.2014 | 122.2098
3293.375 | 122.3511 | -0.068665 | 122.2549 | 0.098959 | 0.041898 | 0.015472 | 0.025347 | 0.036265 | 0.11305 | 0.01969 | 122.3075 | 122.1871 | 122.1764 | 122.0805 | -0.020437 | 0.032376 | -0.033484 | 0.005985 | 0.16762 | 0.11056 | 0.084137 | 0.094012 | 0.10493 | 0.18172 | 0.088355 | 122.3487 | 122.2283 | 122.2176 | 122.1217 | 0.020762 | 0.073575 | 0.007715 | 0.047184 | 122.3279 | 122.341 | 122.1968 | 122.2098
3295.0781 | 122.4426 | -0.032043 | 122.2412 | 0.10354 | 0.037319 | 0.015472 | 0.025347 | 0.040843 | 0.10848 | 0.01969 | 122.2983 | 122.1825 | 122.1764 | 122.0805 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.13558 | 0.069362 | 0.047515 | 0.05739 | 0.072886 | 0.14052 | 0.051733 | 122.3395 | 122.2237 | 122.2176 | 122.1217 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.305 | 122.3318 | 122.1831 | 122.2098
3296.8594 | 122.3236 | -0.10529 | 122.2504 | 0.10354 | 0.037319 | 0.006315 | 0.025347 | 0.036265 | 0.10848 | 0.01969 | 122.3029 | 122.1917 | 122.1809 | 122.0805 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.20882 | 0.14261 | 0.1116 | 0.13063 | 0.14155 | 0.21376 | 0.12498 | 122.3441 | 122.2329 | 122.2221 | 122.1217 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3233 | 122.3364 | 122.2014 | 122.2144
3298.5625 | 122.4518 | -0.050354 | 122.2183 | 0.098959 | 0.03274 | 0.006315 | 0.020768 | 0.031687 | 0.10848 | 0.015112 | 122.3075 | 122.1917 | 122.1764 | 122.0805 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.14931 | 0.083094 | 0.056669 | 0.071122 | 0.082041 | 0.15883 | 0.065466 | 122.3487 | 122.2329 | 122.2176 | 122.1217 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3233 | 122.3455 | 122.1922 | 122.2144
3300.3281 | 122.4197 | -0.064087 | 122.2366 | 0.10354 | 0.041898 | 0.015472 | 0.025347 | 0.036265 | 0.10848 | 0.01969 | 122.3029 | 122.1871 | 122.1718 | 122.0851 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.16762 | 0.10598 | 0.079559 | 0.089434 | 0.10035 | 0.17256 | 0.083777 | 122.3441 | 122.2283 | 122.213 | 122.1263 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3233 | 122.3318 | 122.1922 | 122.2007
3302.1094 | 122.4014 | -0.07782 | 122.2504 | 0.10812 | 0.046477 | 0.010893 | 0.01619 | 0.040843 | 0.11305 | 0.024268 | 122.3029 | 122.1871 | 122.1809 | 122.0805 | -0.011281 | 0.027798 | -0.024328 | -0.003172 | 0.18594 | 0.1243 | 0.088713 | 0.09401 | 0.11866 | 0.19087 | 0.10209 | 122.3441 | 122.2283 | 122.2221 | 122.1217 | 0.029918 | 0.068997 | 0.016871 | 0.038027 | 122.3142 | 122.3272 | 122.1922 | 122.2053
3303.8125 | 122.3785 | -0.091553 | 122.287 | 0.10354 | 0.037319 | 0.015472 | 0.025347 | 0.036265 | 0.11763 | 0.01969 | 122.3029 | 122.1825 | 122.1809 | 122.0805 | -0.011281 | 0.032376 | -0.038063 | 0.005985 | 0.19509 | 0.12887 | 0.10702 | 0.1169 | 0.12782 | 0.20919 | 0.11124 | 122.3441 | 122.2237 | 122.2221 | 122.1217 | 0.029918 | 0.073575 | 0.003136 | 0.047184 | 122.3142 | 122.341 | 122.1922 | 122.219
3305.5625 | 122.4655 | -0.050354 | 122.2321 | 0.10354 | 0.037319 | 0.015472 | 0.020768 | 0.036265 | 0.11305 | 0.010533 | 122.2983 | 122.1871 | 122.1809 | 122.0851 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.15389 | 0.087673 | 0.065826 | 0.071122 | 0.086619 | 0.16341 | 0.060887 | 122.3395 | 122.2283 | 122.2221 | 122.1263 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.3142 | 122.3318 | 122.1968 | 122.2144
3307.3125 | 122.3877 | -0.073242 | 122.2504 | 0.098959 | 0.046477 | 0.020051 | 0.020768 | 0.040843 | 0.11763 | 0.01969 | 122.2983 | 122.1871 | 122.1809 | 122.0897 | -0.015859 | 0.02322 | -0.042641 | 0.001406 | 0.1722 | 0.11972 | 0.093293 | 0.09401 | 0.11408 | 0.19087 | 0.092932 | 122.3395 | 122.2283 | 122.2221 | 122.1309 | 0.02534 | 0.064419 | -0.001442 | 0.042605 | 122.3142 | 122.341 | 122.1968 | 122.2236
3309.0781 | 122.3419 | -0.09613 | 122.2687 | 0.10354 | 0.041898 | 0.015472 | 0.025347 | 0.040843 | 0.11763 | 0.033424 | 122.2983 | 122.1825 | 122.1718 | 122.0897 | -0.025015 | 0.032376 | -0.033484 | 0.001406 | 0.19967 | 0.13803 | 0.1116 | 0.12148 | 0.13697 | 0.21376 | 0.12955 | 122.3395 | 122.2237 | 122.213 | 122.1309 | 0.016184 | 0.073575 | 0.007715 | 0.042605 | 122.3233 | 122.3318 | 122.1968 | 122.2053
3310.7812 | 122.406 | -0.059509 | 122.2458 | 0.10354 | 0.046477 | 0.020051 | 0.029925 | 0.040843 | 0.11305 | 0.01969 | 122.2983 | 122.1825 | 122.1764 | 122.0897 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.16305 | 0.10599 | 0.07956 | 0.089434 | 0.10035 | 0.17256 | 0.079199 | 122.3395 | 122.2237 | 122.2176 | 122.1309 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.3142 | 122.3272 | 122.1922 | 122.2053
3312.5312 | 122.4243 | -0.059509 | 122.2458 | 0.098959 | 0.037319 | 0.010893 | 0.020768 | 0.036265 | 0.12221 | 0.01969 | 122.3029 | 122.1825 | 122.1855 | 122.0943 | -0.020437 | 0.036954 | -0.038063 | -0.003172 | 0.15847 | 0.096828 | 0.070402 | 0.080277 | 0.095774 | 0.18172 | 0.079199 | 122.3441 | 122.2237 | 122.2267 | 122.1355 | 0.020762 | 0.078153 | 0.003136 | 0.038027 | 122.3233 | 122.341 | 122.2059 | 122.2236
3314.2812 | 122.406 | -0.064087 | 122.2412 | 0.10354 | 0.041898 | 0.015472 | 0.020768 | 0.045421 | 0.12221 | 0.028846 | 122.3075 | 122.1917 | 122.1718 | 122.0851 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.16762 | 0.10598 | 0.079559 | 0.084855 | 0.10951 | 0.1863 | 0.092933 | 122.3487 | 122.2329 | 122.213 | 122.1263 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.3142 | 122.3364 | 122.1785 | 122.2007
3316.0312 | 122.4518 | -0.041199 | 122.2595 | 0.098959 | 0.046477 | 0.020051 | 0.025347 | 0.054577 | 0.12679 | 0.01969 | 122.3029 | 122.1871 | 122.1764 | 122.0805 | -0.015859 | 0.032376 | -0.038063 | 0.001406 | 0.14016 | 0.087676 | 0.06125 | 0.066546 | 0.095776 | 0.16799 | 0.060889 | 122.3441 | 122.2283 | 122.2176 | 122.1217 | 0.02534 | 0.073575 | 0.003136 | 0.042605 | 122.3187 | 122.341 | 122.1922 | 122.2144
3317.7812 | 122.4243 | -0.082397 | 122.2229 | 0.10354 | 0.041898 | 0.015472 | 0.034504 | 0.045421 | 0.12221 | 0.01969 | 122.3029 | 122.1825 | 122.1764 | 122.0943 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.18593 | 0.12429 | 0.097869 | 0.1169 | 0.12782 | 0.20461 | 0.10209 | 122.3441 | 122.2237 | 122.2176 | 122.1355 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3187 | 122.3318 | 122.1922 | 122.2053
3319.4844 | 122.4152 | -0.082397 | 122.2137 | 0.098959 | 0.037319 | 0.020051 | 0.029925 | 0.040843 | 0.12221 | 0.028846 | 122.3029 | 122.1871 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.18136 | 0.11972 | 0.10245 | 0.11232 | 0.12324 | 0.20461 | 0.11124 | 122.3441 | 122.2283 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3187 | 122.3318 | 122.1922 | 122.2053
3321.2344 | 122.406 | -0.064087 | 122.2092 | 0.094381 | 0.046477 | 0.010893 | 0.034504 | 0.045421 | 0.11763 | 0.024268 | 122.3029 | 122.1871 | 122.1764 | 122.0851 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.15847 | 0.11056 | 0.07498 | 0.098591 | 0.10951 | 0.18172 | 0.088355 | 122.3441 | 122.2283 | 122.2176 | 122.1263 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3142 | 122.3364 | 122.1876 | 122.2098
3322.9219 | 122.3923 | -0.082397 | 122.2366 | 0.10812 | 0.041898 | 0.024629 | 0.029925 | 0.049999 | 0.11763 | 0.033424 | 122.2937 | 122.1871 | 122.1809 | 122.0897 | -0.020437 | 0.027798 | -0.033484 | 0.001406 | 0.19051 | 0.12429 | 0.10703 | 0.11232 | 0.1324 | 0.20003 | 0.11582 | 122.3349 | 122.2283 | 122.2221 | 122.1309 | 0.020762 | 0.068997 | 0.007715 | 0.042605 | 122.3142 | 122.3272 | 122.2014 | 122.2144
3324.6875 | 122.3419 | -0.091553 | 122.2778 | 0.10812 | 0.051056 | 0.024629 | 0.034504 | 0.049999 | 0.11763 | 0.028846 | 122.2983 | 122.1917 | 122.1809 | 122.0851 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.19967 | 0.14261 | 0.11618 | 0.12606 | 0.14155 | 0.20919 | 0.1204 | 122.3395 | 122.2329 | 122.2221 | 122.1263 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.3096 | 122.3226 | 122.1922 | 122.2053
3326.4375 | 122.3282 | -0.10529 | 122.2778 | 0.094381 | 0.041898 | 0.029208 | 0.029925 | 0.045421 | 0.12679 | 0.028846 | 122.3075 | 122.1917 | 122.1764 | 122.0851 | -0.020437 | 0.032376 | -0.038063 | -0.003172 | 0.19967 | 0.14718 | 0.13449 | 0.13521 | 0.15071 | 0.23207 | 0.13413 | 122.3487 | 122.2329 | 122.2176 | 122.1263 | 0.020762 | 0.073575 | 0.003136 | 0.038027 | 122.3279 | 122.3455 | 122.1968 | 122.2144
3328.125 | 122.3602 | -0.10529 | 122.2595 | 0.098959 | 0.046477 | 0.020051 | 0.034504 | 0.049999 | 0.11763 | 0.028846 | 122.3029 | 122.1825 | 122.1809 | 122.0851 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.20425 | 0.15176 | 0.12534 | 0.13979 | 0.15529 | 0.22292 | 0.13413 | 122.3441 | 122.2237 | 122.2221 | 122.1263 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.3187 | 122.3364 | 122.1968 | 122.2144
3329.9062 | 122.4472 | -0.054932 | 122.2321 | 0.098959 | 0.046477 | 0.020051 | 0.025347 | 0.040843 | 0.12221 | 0.033424 | 122.2983 | 122.178 | 122.1809 | 122.0805 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.15389 | 0.10141 | 0.074983 | 0.080279 | 0.095775 | 0.17714 | 0.088356 | 122.3395 | 122.2192 | 122.2221 | 122.1217 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3142 | 122.3272 | 122.1968 | 122.2098
3331.6562 | 122.3465 | -0.10529 | 122.2961 | 0.094381 | 0.046477 | 0.020051 | 0.034504 | 0.049999 | 0.13137 | 0.028846 | 122.3029 | 122.1963 | 122.1718 | 122.0805 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.19967 | 0.15176 | 0.12534 | 0.13979 | 0.15529 | 0.23665 | 0.13413 | 122.3441 | 122.2375 | 122.213 | 122.1217 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.3142 | 122.3318 | 122.1831 | 122.2007
3333.4062 | 122.4564 | -0.054932 | 122.2183 | 0.098959 | 0.055634 | 0.029208 | 0.034504 | 0.049999 | 0.12221 | 0.033424 | 122.3075 | 122.1917 | 122.1764 | 122.0897 | -0.011281 | 0.018642 | -0.028906 | 0.001406 | 0.15389 | 0.11057 | 0.08414 | 0.089436 | 0.10493 | 0.17714 | 0.088356 | 122.3487 | 122.2329 | 122.2176 | 122.1309 | 0.029918 | 0.059841 | 0.012293 | 0.042605 | 122.3187 | 122.3364 | 122.1876 | 122.2053
3335.1719 | 122.4609 | -0.054932 | 122.2275 | 0.094381 | 0.055634 | 0.029208 | 0.034504 | 0.049999 | 0.12679 | 0.028846 | 122.2983 | 122.1825 | 122.1764 | 122.0851 | -0.011281 | 0.032376 | -0.033484 | 0.010563 | 0.14931 | 0.11057 | 0.08414 | 0.089436 | 0.10493 | 0.18172 | 0.083778 | 122.3395 | 122.2237 | 122.2176 | 122.1263 | 0.029918 | 0.073575 | 0.007715 | 0.051762 | 122.3096 | 122.3318 | 122.1876 | 122.2098
3336.875 | 122.4426 | -0.045776 | 122.2183 | 0.094381 | 0.046477 | 0.029208 | 0.048239 | 0.059155 | 0.12679 | 0.028846 | 122.3029 | 122.1871 | 122.1718 | 122.0851 | -0.020437 | 0.02322 | -0.038063 | 0.005985 | 0.14016 | 0.092253 | 0.074984 | 0.094015 | 0.10493 | 0.17256 | 0.074622 | 122.3441 | 122.2283 | 122.213 | 122.1263 | 0.020762 | 0.064419 | 0.003136 | 0.047184 | 122.3233 | 122.341 | 122.1922 | 122.2098
3338.6406 | 122.4243 | -0.059509 | 122.2595 | 0.098959 | 0.055634 | 0.033786 | 0.034504 | 0.054577 | 0.12221 | 0.033424 | 122.3075 | 122.1825 | 122.1718 | 122.0851 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.15847 | 0.11514 | 0.093295 | 0.094013 | 0.11409 | 0.18172 | 0.092933 | 122.3487 | 122.2237 | 122.213 | 122.1263 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.3187 | 122.3364 | 122.1831 | 122.2007
3340.4062 | 122.438 | -0.059509 | 122.2321 | 0.098959 | 0.055634 | 0.033786 | 0.034504 | 0.049999 | 0.13137 | 0.042581 | 122.3029 | 122.1871 | 122.1718 | 122.0805 | -0.015859 | 0.027798 | -0.042641 | -0.003172 | 0.15847 | 0.11514 | 0.093295 | 0.094013 | 0.10951 | 0.19088 | 0.10209 | 122.3441 | 122.2283 | 122.213 | 122.1217 | 0.02534 | 0.068997 | -0.001442 | 0.038027 | 122.3187 | 122.3455 | 122.1876 | 122.2144
3342.1875 | 122.4426 | -0.041199 | 122.2183 | 0.098959 | 0.055634 | 0.029208 | 0.039082 | 0.059155 | 0.13595 | 0.033424 | 122.3029 | 122.1871 | 122.1764 | 122.0805 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.14016 | 0.096833 | 0.070407 | 0.080281 | 0.10035 | 0.17714 | 0.074623 | 122.3441 | 122.2283 | 122.2176 | 122.1217 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.3142 | 122.341 | 122.1876 | 122.2144
3343.9531 | 122.4792 | -0.050354 | 122.2183 | 0.10354 | 0.051056 | 0.029208 | 0.034504 | 0.049999 | 0.13137 | 0.038003 | 122.312 | 122.1871 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.028906 | 0.010563 | 0.15389 | 0.10141 | 0.079562 | 0.084858 | 0.10035 | 0.18172 | 0.088357 | 122.3532 | 122.2283 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.012293 | 0.051762 | 122.3279 | 122.341 | 122.1922 | 122.2053
3345.6406 | 122.4472 | -0.054932 | 122.2366 | 0.10354 | 0.055634 | 0.038365 | 0.043661 | 0.054577 | 0.13137 | 0.028846 | 122.3029 | 122.1825 | 122.1764 | 122.0897 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.15847 | 0.11057 | 0.093297 | 0.098593 | 0.10951 | 0.1863 | 0.083778 | 122.3441 | 122.2237 | 122.2176 | 122.1309 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3187 | 122.3318 | 122.1922 | 122.2053
3347.3281 | 122.4701 | -0.054932 | 122.2183 | 0.098959 | 0.055634 | 0.038365 | 0.039082 | 0.049999 | 0.12679 | 0.033424 | 122.3075 | 122.1871 | 122.1718 | 122.0897 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.15389 | 0.11057 | 0.093297 | 0.094014 | 0.10493 | 0.18172 | 0.088356 | 122.3487 | 122.2283 | 122.213 | 122.1309 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.3233 | 122.3455 | 122.1876 | 122.2098
3349.0938 | 122.3602 | -0.086975 | 122.2504 | 0.10354 | 0.060213 | 0.042944 | 0.043661 | 0.054577 | 0.14052 | 0.033424 | 122.3029 | 122.1917 | 122.1764 | 122.0851 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.19051 | 0.14719 | 0.12992 | 0.13064 | 0.14155 | 0.2275 | 0.1204 | 122.3441 | 122.2329 | 122.2176 | 122.1263 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.3142 | 122.341 | 122.1876 | 122.2144
3350.7812 | 122.4152 | -0.068665 | 122.2321 | 0.098959 | 0.051056 | 0.042944 | 0.039082 | 0.059155 | 0.13137 | 0.038003 | 122.3075 | 122.1871 | 122.1718 | 122.0851 | -0.020437 | 0.018642 | -0.028906 | 0.001406 | 0.16762 | 0.11972 | 0.11161 | 0.10775 | 0.12782 | 0.20003 | 0.10667 | 122.3487 | 122.2283 | 122.213 | 122.1263 | 0.020762 | 0.059841 | 0.012293 | 0.042605 | 122.3279 | 122.3364 | 122.1922 | 122.2007
3352.5469 | 122.3877 | -0.082397 | 122.2549 | 0.10354 | 0.064792 | 0.047522 | 0.052818 | 0.06831 | 0.14052 | 0.047159 | 122.3075 | 122.1917 | 122.1764 | 122.0897 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.18593 | 0.14719 | 0.12992 | 0.13522 | 0.15071 | 0.22292 | 0.12956 | 122.3487 | 122.2329 | 122.2176 | 122.1309 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3187 | 122.341 | 122.1876 | 122.2098
3354.3125 | 122.438 | -0.064087 | 122.2275 | 0.10354 | 0.064792 | 0.047522 | 0.043661 | 0.063733 | 0.13595 | 0.038003 | 122.3075 | 122.1963 | 122.1672 | 122.0897 | -0.020437 | 0.018642 | -0.033484 | -0.003172 | 0.16762 | 0.12888 | 0.11161 | 0.10775 | 0.12782 | 0.20003 | 0.10209 | 122.3487 | 122.2375 | 122.2084 | 122.1309 | 0.020762 | 0.059841 | 0.007715 | 0.038027 | 122.3279 | 122.341 | 122.1876 | 122.2007
3356.0781 | 122.3831 | -0.082397 | 122.2549 | 0.10354 | 0.064792 | 0.042944 | 0.048239 | 0.06831 | 0.1451 | 0.047159 | 122.3029 | 122.1917 | 122.1855 | 122.0897 | -0.011281 | 0.02322 | -0.019749 | 0.005985 | 0.18593 | 0.14719 | 0.12534 | 0.13064 | 0.15071 | 0.2275 | 0.12956 | 122.3441 | 122.2329 | 122.2267 | 122.1309 | 0.029918 | 0.064419 | 0.02145 | 0.047184 | 122.3142 | 122.3226 | 122.1968 | 122.2053
3357.7656 | 122.4243 | -0.050354 | 122.2504 | 0.098959 | 0.064792 | 0.047522 | 0.048239 | 0.06831 | 0.14052 | 0.042581 | 122.312 | 122.1871 | 122.1718 | 122.0851 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.14931 | 0.11515 | 0.097876 | 0.098593 | 0.11866 | 0.19088 | 0.092935 | 122.3532 | 122.2283 | 122.213 | 122.1263 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3325 | 122.3455 | 122.1922 | 122.2053
3359.5312 | 122.406 | -0.059509 | 122.2046 | 0.10354 | 0.055634 | 0.038365 | 0.043661 | 0.063733 | 0.14968 | 0.038003 | 122.3029 | 122.1871 | 122.1764 | 122.0851 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.16305 | 0.11514 | 0.097874 | 0.10317 | 0.12324 | 0.20919 | 0.097512 | 122.3441 | 122.2283 | 122.2176 | 122.1263 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.3142 | 122.3364 | 122.1876 | 122.2098
3361.2969 | 122.4701 | -0.045776 | 122.2366 | 0.10812 | 0.069371 | 0.042944 | 0.048239 | 0.063733 | 0.13595 | 0.042581 | 122.3029 | 122.1917 | 122.1809 | 122.0805 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.15389 | 0.11515 | 0.08872 | 0.094015 | 0.10951 | 0.18172 | 0.088357 | 122.3441 | 122.2329 | 122.2221 | 122.1217 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.3187 | 122.3318 | 122.1968 | 122.2098
3362.9844 | 122.4106 | -0.082397 | 122.2504 | 0.098959 | 0.069371 | 0.047522 | 0.052818 | 0.063733 | 0.14052 | 0.042581 | 122.312 | 122.1917 | 122.1718 | 122.0897 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.18136 | 0.15177 | 0.12992 | 0.13522 | 0.14613 | 0.22292 | 0.12498 | 122.3532 | 122.2329 | 122.213 | 122.1309 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3279 | 122.341 | 122.1876 | 122.2007
3364.75 | 122.319 | -0.10529 | 122.2504 | 0.10812 | 0.064792 | 0.056679 | 0.061975 | 0.06831 | 0.1451 | 0.060893 | 122.312 | 122.1963 | 122.1718 | 122.0851 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.2134 | 0.17008 | 0.16196 | 0.16726 | 0.1736 | 0.25039 | 0.16618 | 122.3532 | 122.2375 | 122.213 | 122.1263 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.3279 | 122.3455 | 122.1876 | 122.2053
3366.5 | 122.3465 | -0.10071 | 122.2778 | 0.10354 | 0.064792 | 0.052101 | 0.057396 | 0.072888 | 0.14968 | 0.047159 | 122.312 | 122.1871 | 122.1809 | 122.0851 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.20425 | 0.1655 | 0.15281 | 0.1581 | 0.1736 | 0.25039 | 0.14787 | 122.3532 | 122.2283 | 122.2221 | 122.1263 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.3279 | 122.3455 | 122.1968 | 122.2144
3368.2656 | 122.4014 | -0.073242 | 122.2366 | 0.10354 | 0.078529 | 0.056679 | 0.057396 | 0.072888 | 0.14052 | 0.056315 | 122.3029 | 122.1917 | 122.1764 | 122.0805 | -0.015859 | 0.02322 | -0.028906 | -0.00775 | 0.17678 | 0.15177 | 0.12992 | 0.13064 | 0.14613 | 0.21377 | 0.12956 | 122.3441 | 122.2329 | 122.2176 | 122.1217 | 0.02534 | 0.064419 | 0.012293 | 0.033449 | 122.3187 | 122.3318 | 122.1922 | 122.2053
3369.9688 | 122.4747 | -0.059509 | 122.2549 | 0.10354 | 0.07395 | 0.047522 | 0.052818 | 0.072888 | 0.1451 | 0.056315 | 122.3075 | 122.1917 | 122.1764 | 122.0851 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.16305 | 0.13346 | 0.10703 | 0.11233 | 0.1324 | 0.20461 | 0.11582 | 122.3487 | 122.2329 | 122.2176 | 122.1263 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3187 | 122.341 | 122.1876 | 122.2098
3371.7344 | 122.3877 | -0.082397 | 122.2687 | 0.10812 | 0.07395 | 0.047522 | 0.061975 | 0.072888 | 0.16342 | 0.051737 | 122.3029 | 122.1963 | 122.1764 | 122.0943 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.19051 | 0.15635 | 0.12992 | 0.14437 | 0.15529 | 0.24581 | 0.13413 | 122.3441 | 122.2375 | 122.2176 | 122.1355 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3233 | 122.3364 | 122.1968 | 122.2098
3373.4844 | 122.4564 | -0.059509 | 122.2321 | 0.10354 | 0.069371 | 0.052101 | 0.057396 | 0.06831 | 0.14968 | 0.056315 | 122.312 | 122.1963 | 122.1764 | 122.0805 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.16305 | 0.12888 | 0.11161 | 0.11691 | 0.12782 | 0.20919 | 0.11582 | 122.3532 | 122.2375 | 122.2176 | 122.1217 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.3279 | 122.341 | 122.1922 | 122.2053
3375.2656 | 122.406 | -0.054932 | 122.2412 | 0.10354 | 0.069371 | 0.052101 | 0.066553 | 0.072888 | 0.1451 | 0.056315 | 122.2983 | 122.1963 | 122.1855 | 122.0943 | -0.025015 | 0.02322 | -0.028906 | 0.001406 | 0.15847 | 0.1243 | 0.10703 | 0.12149 | 0.12782 | 0.20003 | 0.11125 | 122.3395 | 122.2375 | 122.2267 | 122.1355 | 0.016184 | 0.064419 | 0.012293 | 0.042605 | 122.3233 | 122.3272 | 122.2105 | 122.2144
3376.9688 | 122.374 | -0.07782 | 122.2229 | 0.10812 | 0.078529 | 0.061258 | 0.061975 | 0.077466 | 0.15884 | 0.060893 | 122.3029 | 122.1963 | 122.1809 | 122.0943 | -0.020437 | 0.014064 | -0.028906 | -0.003172 | 0.18594 | 0.15635 | 0.13908 | 0.1398 | 0.15529 | 0.23666 | 0.13871 | 122.3441 | 122.2375 | 122.2221 | 122.1355 | 0.020762 | 0.055263 | 0.012293 | 0.038027 | 122.3233 | 122.3318 | 122.2014 | 122.2098
3378.7188 | 122.406 | -0.082397 | 122.2412 | 0.10812 | 0.069371 | 0.061258 | 0.057396 | 0.072888 | 0.15426 | 0.051737 | 122.312 | 122.2009 | 122.1809 | 122.0805 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.19051 | 0.15177 | 0.14366 | 0.13979 | 0.15529 | 0.23666 | 0.13413 | 122.3532 | 122.2421 | 122.2221 | 122.1217 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3233 | 122.341 | 122.1922 | 122.2098
3380.4844 | 122.374 | -0.082397 | 122.2687 | 0.11269 | 0.078529 | 0.056679 | 0.061975 | 0.086622 | 0.15884 | 0.065472 | 122.3029 | 122.1917 | 122.1764 | 122.0897 | -0.020437 | 0.018642 | -0.038063 | 0.005985 | 0.19509 | 0.16093 | 0.13908 | 0.14437 | 0.16902 | 0.24123 | 0.14787 | 122.3441 | 122.2329 | 122.2176 | 122.1309 | 0.020762 | 0.059841 | 0.003136 | 0.047184 | 122.3233 | 122.341 | 122.1968 | 122.2144
3382.25 | 122.4106 | -0.082397 | 122.2275 | 0.098959 | 0.078529 | 0.061258 | 0.066553 | 0.077466 | 0.15426 | 0.060893 | 122.3075 | 122.1825 | 122.1809 | 122.0851 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.18136 | 0.16093 | 0.14366 | 0.14895 | 0.15986 | 0.23666 | 0.14329 | 122.3487 | 122.2237 | 122.2221 | 122.1263 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.3233 | 122.341 | 122.1968 | 122.2144
3384.0156 | 122.3328 | -0.11444 | 122.2733 | 0.10812 | 0.083107 | 0.056679 | 0.066553 | 0.082044 | 0.16342 | 0.065472 | 122.3075 | 122.1963 | 122.1855 | 122.0851 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.22256 | 0.19755 | 0.17112 | 0.18099 | 0.19649 | 0.27786 | 0.17991 | 122.3487 | 122.2375 | 122.2267 | 122.1263 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3233 | 122.341 | 122.2014 | 122.219
3385.7188 | 122.3602 | -0.09613 | 122.2549 | 0.10812 | 0.087686 | 0.061258 | 0.071132 | 0.086622 | 0.16799 | 0.074628 | 122.3166 | 122.178 | 122.1809 | 122.0851 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.20425 | 0.18382 | 0.15739 | 0.16726 | 0.18275 | 0.26412 | 0.17076 | 122.3578 | 122.2192 | 122.2221 | 122.1263 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3455 | 122.1968 | 122.2098
3387.4688 | 122.4106 | -0.064087 | 122.2321 | 0.11269 | 0.078529 | 0.070415 | 0.066553 | 0.077466 | 0.14968 | 0.060893 | 122.3075 | 122.1871 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.17678 | 0.14262 | 0.1345 | 0.13064 | 0.14155 | 0.21377 | 0.12498 | 122.3487 | 122.2283 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.3233 | 122.3455 | 122.1922 | 122.2144
3389.2344 | 122.4243 | -0.059509 | 122.2458 | 0.10354 | 0.087686 | 0.061258 | 0.071132 | 0.082044 | 0.15884 | 0.060893 | 122.3075 | 122.1917 | 122.1764 | 122.0851 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.16305 | 0.14719 | 0.12077 | 0.13064 | 0.14155 | 0.21835 | 0.1204 | 122.3487 | 122.2329 | 122.2176 | 122.1263 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3187 | 122.3364 | 122.1876 | 122.2053
3391 | 122.4243 | -0.054932 | 122.2229 | 0.11269 | 0.078529 | 0.070415 | 0.07571 | 0.086622 | 0.16799 | 0.065472 | 122.312 | 122.1871 | 122.1764 | 122.0851 | -0.020437 | 0.027798 | -0.033484 | 0.005985 | 0.16763 | 0.13346 | 0.12535 | 0.13064 | 0.14155 | 0.22293 | 0.1204 | 122.3532 | 122.2283 | 122.2176 | 122.1263 | 0.020762 | 0.068997 | 0.007715 | 0.047184 | 122.3325 | 122.3455 | 122.1968 | 122.2098
3392.7031 | 122.4838 | -0.059509 | 122.2229 | 0.10812 | 0.083107 | 0.070415 | 0.071132 | 0.077466 | 0.16342 | 0.056315 | 122.3029 | 122.1871 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.16762 | 0.14262 | 0.12992 | 0.13064 | 0.13697 | 0.22292 | 0.11582 | 122.3441 | 122.2283 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3187 | 122.3364 | 122.1922 | 122.2098
3394.4688 | 122.3694 | -0.11444 | 122.2595 | 0.10812 | 0.092265 | 0.079572 | 0.080288 | 0.10036 | 0.16799 | 0.074628 | 122.3075 | 122.1963 | 122.1764 | 122.0897 | -0.011281 | 0.027798 | -0.042641 | -0.003172 | 0.22256 | 0.20671 | 0.19401 | 0.19473 | 0.2148 | 0.28243 | 0.18907 | 122.3487 | 122.2375 | 122.2176 | 122.1309 | 0.029918 | 0.068997 | -0.001442 | 0.038027 | 122.3187 | 122.3501 | 122.1876 | 122.219
3396.1562 | 122.4106 | -0.082397 | 122.2504 | 0.10812 | 0.078529 | 0.070415 | 0.071132 | 0.082044 | 0.16799 | 0.065472 | 122.3075 | 122.1917 | 122.1809 | 122.0851 | -0.020437 | 0.02322 | -0.038063 | -0.00775 | 0.19051 | 0.16093 | 0.15281 | 0.15353 | 0.16444 | 0.25039 | 0.14787 | 122.3487 | 122.2329 | 122.2221 | 122.1263 | 0.020762 | 0.064419 | 0.003136 | 0.033449 | 122.3279 | 122.3455 | 122.2014 | 122.219
3397.9062 | 122.4197 | -0.064087 | 122.2458 | 0.10812 | 0.087686 | 0.074994 | 0.080288 | 0.086622 | 0.15884 | 0.074628 | 122.312 | 122.1917 | 122.1809 | 122.0943 | -0.015859 | 0.02322 | -0.024328 | 0.001406 | 0.1722 | 0.15177 | 0.13908 | 0.14438 | 0.15071 | 0.22292 | 0.13872 | 122.3532 | 122.2329 | 122.2221 | 122.1355 | 0.02534 | 0.064419 | 0.016871 | 0.042605 | 122.3279 | 122.3364 | 122.1968 | 122.2053
3399.6094 | 122.4426 | -0.036621 | 122.2458 | 0.10812 | 0.092265 | 0.074994 | 0.07571 | 0.095778 | 0.17257 | 0.074628 | 122.3075 | 122.1963 | 122.1718 | 122.0943 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.14474 | 0.12889 | 0.11162 | 0.11233 | 0.1324 | 0.20919 | 0.11125 | 122.3487 | 122.2375 | 122.213 | 122.1355 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.3187 | 122.3364 | 122.1831 | 122.2007
3401.3594 | 122.4518 | -0.064087 | 122.2183 | 0.10354 | 0.092265 | 0.074994 | 0.084867 | 0.095778 | 0.16799 | 0.079206 | 122.312 | 122.1963 | 122.1764 | 122.0897 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.16762 | 0.15635 | 0.13908 | 0.14895 | 0.15987 | 0.23208 | 0.14329 | 122.3532 | 122.2375 | 122.2176 | 122.1309 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.3233 | 122.341 | 122.1876 | 122.2053
3403.1094 | 122.4655 | -0.050354 | 122.2321 | 0.10354 | 0.096844 | 0.070415 | 0.084867 | 0.095778 | 0.17715 | 0.074628 | 122.3029 | 122.1917 | 122.1764 | 122.0851 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.15389 | 0.1472 | 0.12077 | 0.13522 | 0.14613 | 0.22751 | 0.12498 | 122.3441 | 122.2329 | 122.2176 | 122.1263 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.3142 | 122.3318 | 122.1876 | 122.2053
3404.875 | 122.3877 | -0.091553 | 122.2641 | 0.11269 | 0.092265 | 0.079572 | 0.084867 | 0.095778 | 0.17715 | 0.079206 | 122.3029 | 122.1917 | 122.1809 | 122.0897 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.20425 | 0.18382 | 0.17112 | 0.17642 | 0.18733 | 0.2687 | 0.17076 | 122.3441 | 122.2329 | 122.2221 | 122.1309 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3187 | 122.341 | 122.1968 | 122.219
3406.6562 | 122.4335 | -0.064087 | 122.2641 | 0.10354 | 0.092265 | 0.070415 | 0.080288 | 0.10951 | 0.17257 | 0.074628 | 122.3029 | 122.1871 | 122.1809 | 122.0897 | -0.020437 | 0.02322 | -0.028906 | 0.005985 | 0.16762 | 0.15635 | 0.1345 | 0.14438 | 0.1736 | 0.23666 | 0.13872 | 122.3441 | 122.2283 | 122.2221 | 122.1309 | 0.020762 | 0.064419 | 0.012293 | 0.047184 | 122.3233 | 122.3318 | 122.2014 | 122.2098
3408.3438 | 122.3969 | -0.059509 | 122.2549 | 0.10354 | 0.096844 | 0.079572 | 0.084867 | 0.10036 | 0.16799 | 0.083784 | 122.2983 | 122.1963 | 122.1764 | 122.0805 | -0.020437 | 0.032376 | -0.028906 | -0.003172 | 0.16305 | 0.15635 | 0.13908 | 0.14438 | 0.15987 | 0.2275 | 0.14329 | 122.3395 | 122.2375 | 122.2176 | 122.1217 | 0.020762 | 0.073575 | 0.012293 | 0.038027 | 122.3187 | 122.3272 | 122.1968 | 122.2053
3410.1094 | 122.3511 | -0.10071 | 122.2961 | 0.10812 | 0.106 | 0.084151 | 0.089445 | 0.10036 | 0.17715 | 0.074628 | 122.312 | 122.1963 | 122.1809 | 122.0897 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 0.20882 | 0.20671 | 0.18486 | 0.19015 | 0.20106 | 0.27786 | 0.17534 | 122.3532 | 122.2375 | 122.2221 | 122.1309 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 122.3233 | 122.3501 | 122.1922 | 122.219
3411.8125 | 122.3145 | -0.10071 | 122.2641 | 0.11269 | 0.096844 | 0.093308 | 0.094024 | 0.10493 | 0.17715 | 0.088362 | 122.312 | 122.1963 | 122.1718 | 122.0897 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.2134 | 0.19755 | 0.19402 | 0.19473 | 0.20564 | 0.27786 | 0.18907 | 122.3532 | 122.2375 | 122.213 | 122.1309 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.3279 | 122.3455 | 122.1876 | 122.2053
3413.5781 | 122.3373 | -0.10986 | 122.2412 | 0.10812 | 0.10142 | 0.08873 | 0.089445 | 0.095778 | 0.17715 | 0.079206 | 122.312 | 122.1963 | 122.1809 | 122.0943 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.21798 | 0.21129 | 0.19859 | 0.19931 | 0.20564 | 0.28701 | 0.18907 | 122.3532 | 122.2375 | 122.2221 | 122.1355 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3279 | 122.341 | 122.1968 | 122.2098
3415.3438 | 122.3373 | -0.10071 | 122.2778 | 0.11269 | 0.106 | 0.079572 | 0.089445 | 0.10036 | 0.18173 | 0.088362 | 122.3075 | 122.1917 | 122.1718 | 122.0897 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.2134 | 0.20671 | 0.18028 | 0.19015 | 0.20106 | 0.28244 | 0.18907 | 122.3487 | 122.2329 | 122.213 | 122.1309 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3233 | 122.341 | 122.1876 | 122.2053
3417.1094 | 122.374 | -0.091553 | 122.2778 | 0.10812 | 0.10142 | 0.08873 | 0.094024 | 0.10951 | 0.18631 | 0.097519 | 122.312 | 122.1963 | 122.1855 | 122.0897 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.19967 | 0.19298 | 0.18028 | 0.18558 | 0.20106 | 0.27786 | 0.18907 | 122.3532 | 122.2375 | 122.2267 | 122.1309 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.3187 | 122.341 | 122.1922 | 122.2144
3418.8125 | 122.4564 | -0.050354 | 122.2366 | 0.10812 | 0.11058 | 0.08873 | 0.084867 | 0.10036 | 0.17715 | 0.088362 | 122.3075 | 122.1917 | 122.1764 | 122.0851 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.15847 | 0.16093 | 0.13908 | 0.13522 | 0.15071 | 0.22751 | 0.13872 | 122.3487 | 122.2329 | 122.2176 | 122.1263 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3233 | 122.3364 | 122.1922 | 122.2053
3420.5781 | 122.3694 | -0.10529 | 122.287 | 0.10812 | 0.087686 | 0.074994 | 0.07571 | 0.082044 | 0.16799 | 0.074628 | 122.3029 | 122.1871 | 122.1764 | 122.0897 | -0.006702 | 0.02322 | -0.033484 | 0.010563 | 0.2134 | 0.19297 | 0.18028 | 0.181 | 0.18733 | 0.27328 | 0.17991 | 122.3441 | 122.2283 | 122.2176 | 122.1309 | 0.034497 | 0.064419 | 0.007715 | 0.051762 | 122.3096 | 122.3364 | 122.1831 | 122.2098
3422.3281 | 122.319 | -0.091553 | 122.2824 | 0.10812 | 0.092265 | 0.074994 | 0.080288 | 0.0912 | 0.17257 | 0.079206 | 122.3075 | 122.1917 | 122.1764 | 122.0897 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.19967 | 0.18382 | 0.16655 | 0.17184 | 0.18275 | 0.26412 | 0.17076 | 122.3487 | 122.2329 | 122.2176 | 122.1309 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.3187 | 122.341 | 122.1876 | 122.2098
3424.0938 | 122.3373 | -0.10529 | 122.2595 | 0.11269 | 0.087686 | 0.070415 | 0.080288 | 0.0912 | 0.16342 | 0.07005 | 122.312 | 122.1963 | 122.1809 | 122.0897 | -0.015859 | 0.018642 | -0.028906 | 0.001406 | 0.21798 | 0.19297 | 0.1757 | 0.18557 | 0.19649 | 0.2687 | 0.17534 | 122.3532 | 122.2375 | 122.2221 | 122.1309 | 0.02534 | 0.059841 | 0.012293 | 0.042605 | 122.3279 | 122.341 | 122.1968 | 122.2098
3425.8594 | 122.4426 | -0.059509 | 122.2275 | 0.10354 | 0.092265 | 0.079572 | 0.084867 | 0.0912 | 0.16799 | 0.07005 | 122.312 | 122.1963 | 122.1855 | 122.0851 | -0.015859 | 0.032376 | -0.019749 | 0.005985 | 0.16305 | 0.15177 | 0.13908 | 0.14438 | 0.15071 | 0.2275 | 0.12956 | 122.3532 | 122.2375 | 122.2267 | 122.1263 | 0.02534 | 0.073575 | 0.02145 | 0.047184 | 122.3279 | 122.3318 | 122.2014 | 122.2053
3427.625 | 122.3419 | -0.10986 | 122.2824 | 0.10812 | 0.087686 | 0.079572 | 0.084867 | 0.10493 | 0.16799 | 0.074628 | 122.3075 | 122.1917 | 122.1809 | 122.0897 | -0.015859 | 0.02322 | -0.024328 | -0.003172 | 0.21798 | 0.19755 | 0.18944 | 0.19473 | 0.2148 | 0.27786 | 0.18449 | 122.3487 | 122.2329 | 122.2221 | 122.1309 | 0.02534 | 0.064419 | 0.016871 | 0.038027 | 122.3233 | 122.3318 | 122.1968 | 122.2053
3429.3281 | 122.3602 | -0.073242 | 122.2824 | 0.10812 | 0.096844 | 0.084151 | 0.094024 | 0.095778 | 0.17257 | 0.079206 | 122.3075 | 122.1917 | 122.1764 | 122.0943 | -0.015859 | 0.018642 | -0.038063 | -0.003172 | 0.18136 | 0.17009 | 0.15739 | 0.16727 | 0.16902 | 0.24581 | 0.15245 | 122.3487 | 122.2329 | 122.2176 | 122.1355 | 0.02534 | 0.059841 | 0.003136 | 0.038027 | 122.3233 | 122.3455 | 122.1922 | 122.2144
3431.1094 | 122.4609 | -0.068665 | 122.2229 | 0.10354 | 0.096844 | 0.079572 | 0.084867 | 0.0912 | 0.16799 | 0.074628 | 122.3029 | 122.1963 | 122.1764 | 122.0897 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.1722 | 0.16551 | 0.14824 | 0.15353 | 0.15987 | 0.23666 | 0.14329 | 122.3441 | 122.2375 | 122.2176 | 122.1309 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3187 | 122.3318 | 122.1922 | 122.2053
3432.8125 | 122.3877 | -0.073242 | 122.2778 | 0.11269 | 0.096844 | 0.084151 | 0.084867 | 0.10493 | 0.18173 | 0.079206 | 122.3075 | 122.1963 | 122.1855 | 122.0988 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.18594 | 0.17009 | 0.15739 | 0.15811 | 0.17818 | 0.25497 | 0.15245 | 122.3487 | 122.2375 | 122.2267 | 122.14 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3233 | 122.3364 | 122.2014 | 122.2144
3434.5781 | 122.3419 | -0.10071 | 122.2641 | 0.10812 | 0.10142 | 0.084151 | 0.094024 | 0.10493 | 0.18631 | 0.083784 | 122.3075 | 122.2009 | 122.1809 | 122.0897 | -0.020437 | 0.018642 | -0.033484 | 0.001406 | 0.20882 | 0.20213 | 0.18486 | 0.19473 | 0.20564 | 0.28702 | 0.18449 | 122.3487 | 122.2421 | 122.2221 | 122.1309 | 0.020762 | 0.059841 | 0.007715 | 0.042605 | 122.3279 | 122.341 | 122.2014 | 122.2144
3436.3281 | 122.4472 | -0.073242 | 122.2366 | 0.10812 | 0.096844 | 0.079572 | 0.084867 | 0.10036 | 0.17715 | 0.079206 | 122.3075 | 122.1963 | 122.1809 | 122.0897 | -0.011281 | 0.02322 | -0.019749 | -0.003172 | 0.18136 | 0.17009 | 0.15281 | 0.15811 | 0.1736 | 0.25039 | 0.15245 | 122.3487 | 122.2375 | 122.2221 | 122.1309 | 0.029918 | 0.064419 | 0.02145 | 0.038027 | 122.3187 | 122.3272 | 122.1922 | 122.2007
3438.0781 | 122.4472 | -0.054932 | 122.2412 | 0.11269 | 0.11058 | 0.093308 | 0.094024 | 0.11409 | 0.18631 | 0.088362 | 122.3075 | 122.1917 | 122.1809 | 122.0851 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.16763 | 0.16551 | 0.14824 | 0.14896 | 0.16902 | 0.24124 | 0.14329 | 122.3487 | 122.2329 | 122.2221 | 122.1263 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.3187 | 122.3455 | 122.1922 | 122.219
3439.8438 | 122.4152 | -0.064087 | 122.2549 | 0.10354 | 0.10142 | 0.084151 | 0.089445 | 0.10493 | 0.18173 | 0.083784 | 122.312 | 122.1917 | 122.1809 | 122.0851 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.16762 | 0.16551 | 0.14824 | 0.15353 | 0.16902 | 0.24582 | 0.14787 | 122.3532 | 122.2329 | 122.2221 | 122.1263 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3279 | 122.3501 | 122.1968 | 122.219
3441.6094 | 122.4564 | -0.041199 | 122.2275 | 0.10812 | 0.11058 | 0.08873 | 0.094024 | 0.10951 | 0.19089 | 0.088362 | 122.312 | 122.1871 | 122.1855 | 122.0943 | -0.015859 | 0.018642 | -0.033484 | -0.003172 | 0.14932 | 0.15178 | 0.12993 | 0.13522 | 0.15071 | 0.23208 | 0.12956 | 122.3532 | 122.2283 | 122.2267 | 122.1355 | 0.02534 | 0.059841 | 0.007715 | 0.038027 | 122.3279 | 122.3455 | 122.2014 | 122.219
3443.3594 | 122.4701 | -0.064087 | 122.2458 | 0.11727 | 0.11516 | 0.093308 | 0.094024 | 0.10951 | 0.19089 | 0.092941 | 122.3075 | 122.1963 | 122.1809 | 122.0851 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.18136 | 0.17925 | 0.1574 | 0.15811 | 0.1736 | 0.25497 | 0.15703 | 122.3487 | 122.2375 | 122.2221 | 122.1263 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3279 | 122.341 | 122.2014 | 122.2144
3445.1094 | 122.4152 | -0.07782 | 122.2412 | 0.11269 | 0.11516 | 0.093308 | 0.10318 | 0.10493 | 0.18173 | 0.088362 | 122.3166 | 122.1963 | 122.1809 | 122.0943 | -0.020437 | 0.027798 | -0.024328 | -0.003172 | 0.19051 | 0.19298 | 0.17113 | 0.181 | 0.18275 | 0.25955 | 0.16618 | 122.3578 | 122.2375 | 122.2221 | 122.1355 | 0.020762 | 0.068997 | 0.016871 | 0.038027 | 122.3371 | 122.341 | 122.2014 | 122.2053
3446.8125 | 122.4655 | -0.064087 | 122.2595 | 0.12185 | 0.11058 | 0.093308 | 0.094024 | 0.10951 | 0.18631 | 0.092941 | 122.3029 | 122.1963 | 122.1809 | 122.0805 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.18594 | 0.17467 | 0.1574 | 0.15811 | 0.1736 | 0.25039 | 0.15703 | 122.3441 | 122.2375 | 122.2221 | 122.1217 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3187 | 122.3318 | 122.1968 | 122.2098
3448.5625 | 122.4609 | -0.054932 | 122.2366 | 0.11269 | 0.11058 | 0.10247 | 0.10318 | 0.11409 | 0.18631 | 0.092941 | 122.312 | 122.2009 | 122.1855 | 122.0988 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.16763 | 0.16551 | 0.1574 | 0.15811 | 0.16902 | 0.24124 | 0.14787 | 122.3532 | 122.2421 | 122.2267 | 122.14 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3233 | 122.3455 | 122.1968 | 122.219
3450.3281 | 122.4106 | -0.07782 | 122.2366 | 0.11727 | 0.11516 | 0.097887 | 0.10318 | 0.11409 | 0.19089 | 0.088362 | 122.3075 | 122.1917 | 122.1809 | 122.0897 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.19509 | 0.19298 | 0.17571 | 0.181 | 0.19191 | 0.26871 | 0.16618 | 122.3487 | 122.2329 | 122.2221 | 122.1309 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3233 | 122.3364 | 122.1968 | 122.2098
3452.0312 | 122.4197 | -0.07782 | 122.2366 | 0.12185 | 0.11974 | 0.10247 | 0.10776 | 0.11867 | 0.19089 | 0.097519 | 122.3212 | 122.1963 | 122.1809 | 122.0851 | -0.015859 | 0.02322 | -0.024328 | 0.005985 | 0.19967 | 0.19756 | 0.18029 | 0.18558 | 0.19649 | 0.26871 | 0.17534 | 122.3624 | 122.2375 | 122.2221 | 122.1263 | 0.02534 | 0.064419 | 0.016871 | 0.047184 | 122.3371 | 122.3455 | 122.1968 | 122.2053
3453.7812 | 122.4655 | -0.054932 | 122.2504 | 0.11269 | 0.11974 | 0.10247 | 0.11234 | 0.1324 | 0.20004 | 0.1021 | 122.312 | 122.1917 | 122.1855 | 122.0897 | -0.006702 | 0.02322 | -0.028906 | 0.005985 | 0.16763 | 0.17467 | 0.1574 | 0.16727 | 0.18733 | 0.25498 | 0.15703 | 122.3532 | 122.2329 | 122.2267 | 122.1309 | 0.034497 | 0.064419 | 0.012293 | 0.047184 | 122.3187 | 122.341 | 122.1922 | 122.2144
3455.5469 | 122.4747 | -0.050354 | 122.2092 | 0.12643 | 0.12432 | 0.10247 | 0.10776 | 0.12325 | 0.18631 | 0.1021 | 122.312 | 122.1871 | 122.1764 | 122.0851 | -0.015859 | 0.027798 | -0.038063 | 0.005985 | 0.17678 | 0.17467 | 0.15282 | 0.15811 | 0.1736 | 0.23666 | 0.15245 | 122.3532 | 122.2283 | 122.2176 | 122.1263 | 0.02534 | 0.068997 | 0.003136 | 0.047184 | 122.3279 | 122.3501 | 122.1922 | 122.2144
3457.3125 | 122.4747 | -0.036621 | 122.2504 | 0.11727 | 0.1289 | 0.10704 | 0.11234 | 0.12325 | 0.20462 | 0.097519 | 122.3029 | 122.1963 | 122.1809 | 122.0897 | -0.020437 | 0.02322 | -0.038063 | 0.001406 | 0.15389 | 0.16552 | 0.14366 | 0.14896 | 0.15987 | 0.24124 | 0.13414 | 122.3441 | 122.2375 | 122.2221 | 122.1309 | 0.020762 | 0.064419 | 0.003136 | 0.042605 | 122.3233 | 122.341 | 122.2014 | 122.219
3459.0156 | 122.3877 | -0.10071 | 122.2412 | 0.12185 | 0.1289 | 0.10704 | 0.1215 | 0.12782 | 0.2092 | 0.10668 | 122.312 | 122.1963 | 122.1809 | 122.0988 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.22256 | 0.2296 | 0.20775 | 0.2222 | 0.22853 | 0.30991 | 0.20738 | 122.3532 | 122.2375 | 122.2221 | 122.14 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3279 | 122.3455 | 122.1968 | 122.2144
3460.7969 | 122.4564 | -0.045776 | 122.2504 | 0.11727 | 0.13347 | 0.11162 | 0.11692 | 0.12782 | 0.20462 | 0.10668 | 122.3075 | 122.1917 | 122.1764 | 122.0851 | -0.020437 | 0.027798 | -0.028906 | -0.003172 | 0.16305 | 0.17925 | 0.1574 | 0.16269 | 0.1736 | 0.2504 | 0.15245 | 122.3487 | 122.2329 | 122.2176 | 122.1263 | 0.020762 | 0.068997 | 0.012293 | 0.038027 | 122.3279 | 122.3364 | 122.1968 | 122.2053
3462.5625 | 122.374 | -0.086975 | 122.2549 | 0.12185 | 0.13347 | 0.11162 | 0.1215 | 0.12782 | 0.20462 | 0.11125 | 122.3075 | 122.2009 | 122.1764 | 122.0851 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.20883 | 0.22045 | 0.1986 | 0.20847 | 0.2148 | 0.2916 | 0.19823 | 122.3487 | 122.2421 | 122.2176 | 122.1263 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.3187 | 122.3364 | 122.1876 | 122.2053
3464.3125 | 122.3419 | -0.086975 | 122.2778 | 0.12643 | 0.1289 | 0.10704 | 0.11692 | 0.12782 | 0.2092 | 0.11583 | 122.3075 | 122.1963 | 122.1809 | 122.0851 | -0.020437 | 0.027798 | -0.033484 | 0.005985 | 0.2134 | 0.21587 | 0.19402 | 0.20389 | 0.2148 | 0.29617 | 0.20281 | 122.3487 | 122.2375 | 122.2221 | 122.1263 | 0.020762 | 0.068997 | 0.007715 | 0.047184 | 122.3279 | 122.341 | 122.2014 | 122.2144
3466 | 122.493 | -0.059509 | 122.2321 | 0.11727 | 0.13347 | 0.12078 | 0.1215 | 0.12782 | 0.2092 | 0.11125 | 122.312 | 122.1963 | 122.1855 | 122.0988 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.17678 | 0.19298 | 0.18029 | 0.181 | 0.18733 | 0.26871 | 0.17076 | 122.3532 | 122.2375 | 122.2267 | 122.14 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3279 | 122.3455 | 122.2014 | 122.219
3467.75 | 122.4106 | -0.064087 | 122.2504 | 0.11727 | 0.14263 | 0.12536 | 0.12607 | 0.14156 | 0.22293 | 0.12041 | 122.3075 | 122.1917 | 122.1809 | 122.0897 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.18136 | 0.20672 | 0.18945 | 0.19016 | 0.20564 | 0.28702 | 0.1845 | 122.3487 | 122.2329 | 122.2221 | 122.1309 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3187 | 122.3364 | 122.1922 | 122.2098
3469.5156 | 122.3785 | -0.082397 | 122.2366 | 0.11727 | 0.14263 | 0.1162 | 0.13065 | 0.14156 | 0.21378 | 0.12499 | 122.3166 | 122.1963 | 122.1901 | 122.0897 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.19967 | 0.22503 | 0.1986 | 0.21305 | 0.22395 | 0.29617 | 0.20738 | 122.3578 | 122.2375 | 122.2313 | 122.1309 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.3279 | 122.3455 | 122.2014 | 122.219
3471.2344 | 122.4609 | -0.054932 | 122.2366 | 0.11727 | 0.14263 | 0.12078 | 0.13065 | 0.14614 | 0.21378 | 0.11125 | 122.312 | 122.2009 | 122.1809 | 122.0851 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.1722 | 0.19756 | 0.17571 | 0.18558 | 0.20107 | 0.26871 | 0.16618 | 122.3532 | 122.2421 | 122.2221 | 122.1263 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.3233 | 122.3455 | 122.1922 | 122.2144
3472.9844 | 122.4426 | -0.073242 | 122.2412 | 0.12185 | 0.14721 | 0.12078 | 0.13065 | 0.13698 | 0.21836 | 0.12499 | 122.3075 | 122.1917 | 122.1901 | 122.0851 | -0.020437 | 0.027798 | -0.038063 | -0.00775 | 0.19509 | 0.22045 | 0.19402 | 0.20389 | 0.21022 | 0.2916 | 0.19823 | 122.3487 | 122.2329 | 122.2313 | 122.1263 | 0.020762 | 0.068997 | 0.003136 | 0.033449 | 122.3279 | 122.3455 | 122.2105 | 122.2282
3474.7344 | 122.4152 | -0.068665 | 122.2549 | 0.11727 | 0.15637 | 0.13909 | 0.14439 | 0.15987 | 0.23209 | 0.12957 | 122.3075 | 122.1871 | 122.1809 | 122.0851 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.18594 | 0.22503 | 0.20776 | 0.21305 | 0.22854 | 0.30076 | 0.19823 | 122.3487 | 122.2283 | 122.2221 | 122.1263 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3233 | 122.3364 | 122.1968 | 122.2098
3476.5 | 122.3602 | -0.10986 | 122.2824 | 0.11269 | 0.14263 | 0.12994 | 0.13065 | 0.14614 | 0.22293 | 0.12041 | 122.3166 | 122.1963 | 122.1809 | 122.0897 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.22256 | 0.2525 | 0.2398 | 0.24051 | 0.256 | 0.3328 | 0.23027 | 122.3578 | 122.2375 | 122.2221 | 122.1309 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3325 | 122.3501 | 122.1968 | 122.2144
3478.2031 | 122.3282 | -0.091553 | 122.2687 | 0.12185 | 0.14721 | 0.12994 | 0.13981 | 0.15529 | 0.23667 | 0.13414 | 122.312 | 122.1917 | 122.1855 | 122.0988 | -0.020437 | 0.02322 | -0.028906 | -0.003172 | 0.2134 | 0.23876 | 0.22149 | 0.23136 | 0.24685 | 0.32822 | 0.2257 | 122.3532 | 122.2329 | 122.2267 | 122.14 | 0.020762 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.341 | 122.2059 | 122.2144
3479.9844 | 122.4106 | -0.086975 | 122.2733 | 0.11727 | 0.14263 | 0.12994 | 0.13523 | 0.14614 | 0.22293 | 0.12041 | 122.3166 | 122.2009 | 122.1809 | 122.0897 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.20425 | 0.22961 | 0.21691 | 0.2222 | 0.23311 | 0.30991 | 0.20738 | 122.3578 | 122.2421 | 122.2221 | 122.1309 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3501 | 122.2014 | 122.2144
3481.6875 | 122.4335 | -0.068665 | 122.2366 | 0.12185 | 0.14721 | 0.13452 | 0.13523 | 0.15071 | 0.22293 | 0.12499 | 122.312 | 122.2054 | 122.1809 | 122.0943 | -0.015859 | 0.032376 | -0.024328 | 0.001406 | 0.19052 | 0.21588 | 0.20318 | 0.20389 | 0.21938 | 0.2916 | 0.19365 | 122.3532 | 122.2466 | 122.2221 | 122.1355 | 0.02534 | 0.073575 | 0.016871 | 0.042605 | 122.3279 | 122.3364 | 122.1968 | 122.2053
3483.4375 | 122.319 | -0.09613 | 122.2961 | 0.12643 | 0.15179 | 0.13452 | 0.13981 | 0.15529 | 0.23209 | 0.13872 | 122.3166 | 122.1917 | 122.1855 | 122.0943 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.22256 | 0.24792 | 0.23065 | 0.23594 | 0.25142 | 0.32822 | 0.23485 | 122.3578 | 122.2329 | 122.2267 | 122.1355 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3325 | 122.3501 | 122.2014 | 122.219
3485.2031 | 122.4609 | -0.032043 | 122.2321 | 0.12643 | 0.15179 | 0.14367 | 0.14439 | 0.15529 | 0.22293 | 0.13414 | 122.312 | 122.1963 | 122.1855 | 122.0943 | -0.020437 | 0.032376 | -0.028906 | -0.00775 | 0.15847 | 0.18383 | 0.17572 | 0.17643 | 0.18734 | 0.25498 | 0.16619 | 122.3532 | 122.2375 | 122.2267 | 122.1355 | 0.020762 | 0.073575 | 0.012293 | 0.033449 | 122.3325 | 122.341 | 122.2059 | 122.2144
3486.9688 | 122.3877 | -0.086975 | 122.2504 | 0.13101 | 0.16553 | 0.13909 | 0.13981 | 0.15529 | 0.22751 | 0.1433 | 122.3166 | 122.2054 | 122.1901 | 122.0943 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.21798 | 0.2525 | 0.22607 | 0.22678 | 0.24227 | 0.31449 | 0.23028 | 122.3578 | 122.2466 | 122.2313 | 122.1355 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.3279 | 122.3455 | 122.2014 | 122.219
3488.6719 | 122.4747 | -0.059509 | 122.2229 | 0.11727 | 0.15637 | 0.14367 | 0.13981 | 0.15987 | 0.22293 | 0.13414 | 122.3075 | 122.1963 | 122.1855 | 122.0943 | -0.020437 | 0.027798 | -0.024328 | 0.001406 | 0.17678 | 0.21588 | 0.20318 | 0.19932 | 0.21938 | 0.28244 | 0.19365 | 122.3487 | 122.2375 | 122.2267 | 122.1355 | 0.020762 | 0.068997 | 0.016871 | 0.042605 | 122.3279 | 122.3318 | 122.2059 | 122.2098
3490.4219 | 122.4976 | -0.045776 | 122.2549 | 0.11727 | 0.15637 | 0.14367 | 0.13523 | 0.15529 | 0.23209 | 0.13872 | 122.3075 | 122.1871 | 122.1855 | 122.0897 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.16305 | 0.20214 | 0.18945 | 0.18101 | 0.20107 | 0.27787 | 0.1845 | 122.3487 | 122.2283 | 122.2267 | 122.1309 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3233 | 122.341 | 122.2014 | 122.219
3492.1875 | 122.4106 | -0.064087 | 122.2504 | 0.12185 | 0.15637 | 0.14825 | 0.14439 | 0.15529 | 0.23209 | 0.13872 | 122.3212 | 122.2009 | 122.1809 | 122.0943 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.18594 | 0.22046 | 0.21234 | 0.20847 | 0.21938 | 0.29618 | 0.20281 | 122.3624 | 122.2421 | 122.2221 | 122.1355 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3547 | 122.1968 | 122.2144
3493.9375 | 122.4472 | -0.064087 | 122.2321 | 0.12185 | 0.16095 | 0.14367 | 0.14439 | 0.16445 | 0.24125 | 0.1433 | 122.3075 | 122.2054 | 122.1809 | 122.0897 | -0.020437 | 0.018642 | -0.033484 | 0.010563 | 0.18594 | 0.22503 | 0.20776 | 0.20847 | 0.22854 | 0.30534 | 0.20739 | 122.3487 | 122.2466 | 122.2221 | 122.1309 | 0.020762 | 0.059841 | 0.007715 | 0.051762 | 122.3279 | 122.341 | 122.2014 | 122.2144
3495.6875 | 122.4152 | -0.045776 | 122.2458 | 0.12643 | 0.15637 | 0.15741 | 0.15354 | 0.16445 | 0.23667 | 0.14788 | 122.3212 | 122.1963 | 122.1809 | 122.0897 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.1722 | 0.20214 | 0.20319 | 0.19932 | 0.21022 | 0.28245 | 0.19366 | 122.3624 | 122.2375 | 122.2221 | 122.1309 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3371 | 122.3501 | 122.1968 | 122.2098
3497.4531 | 122.4609 | -0.050354 | 122.2366 | 0.13101 | 0.16095 | 0.15283 | 0.15354 | 0.16445 | 0.24125 | 0.13872 | 122.3166 | 122.2009 | 122.1855 | 122.0897 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.18136 | 0.2113 | 0.20318 | 0.2039 | 0.2148 | 0.2916 | 0.18908 | 122.3578 | 122.2421 | 122.2267 | 122.1309 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.3279 | 122.3501 | 122.1968 | 122.219
3499.1562 | 122.3969 | -0.091553 | 122.2595 | 0.13559 | 0.17011 | 0.16657 | 0.16728 | 0.1736 | 0.2504 | 0.1433 | 122.312 | 122.2054 | 122.1901 | 122.0943 | -0.015859 | 0.032376 | -0.024328 | -0.003172 | 0.22714 | 0.26166 | 0.25812 | 0.25883 | 0.26516 | 0.34196 | 0.23485 | 122.3532 | 122.2466 | 122.2313 | 122.1355 | 0.02534 | 0.073575 | 0.016871 | 0.038027 | 122.3279 | 122.3364 | 122.2059 | 122.2144
3500.9219 | 122.3877 | -0.086975 | 122.2595 | 0.13101 | 0.17011 | 0.16199 | 0.15812 | 0.1736 | 0.2504 | 0.14788 | 122.312 | 122.1963 | 122.1855 | 122.0943 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.21798 | 0.25708 | 0.24896 | 0.2451 | 0.26058 | 0.33738 | 0.23485 | 122.3532 | 122.2375 | 122.2267 | 122.1355 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3233 | 122.3455 | 122.1968 | 122.219
3502.6875 | 122.4701 | -0.050354 | 122.2458 | 0.12185 | 0.17011 | 0.15741 | 0.17186 | 0.1736 | 0.2504 | 0.15704 | 122.3166 | 122.1963 | 122.1764 | 122.0943 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.1722 | 0.22046 | 0.20776 | 0.22221 | 0.22396 | 0.30076 | 0.20739 | 122.3578 | 122.2375 | 122.2176 | 122.1355 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3325 | 122.3455 | 122.1922 | 122.2053
3504.3906 | 122.3328 | -0.086975 | 122.2733 | 0.13101 | 0.17926 | 0.15741 | 0.17186 | 0.18276 | 0.25956 | 0.16161 | 122.3075 | 122.2009 | 122.1855 | 122.0943 | -0.015859 | 0.027798 | -0.042641 | 0.005985 | 0.21798 | 0.26624 | 0.24438 | 0.25883 | 0.26973 | 0.34654 | 0.24859 | 122.3487 | 122.2421 | 122.2267 | 122.1355 | 0.02534 | 0.068997 | -0.001442 | 0.047184 | 122.3233 | 122.3501 | 122.2014 | 122.2282
3506.1406 | 122.3602 | -0.09613 | 122.2961 | 0.13101 | 0.17468 | 0.17114 | 0.17644 | 0.17818 | 0.25498 | 0.16161 | 122.3212 | 122.2009 | 122.1855 | 122.0943 | -0.025015 | 0.02322 | -0.028906 | 0.001406 | 0.22714 | 0.27081 | 0.26727 | 0.27257 | 0.27431 | 0.35111 | 0.25774 | 122.3624 | 122.2421 | 122.2267 | 122.1355 | 0.016184 | 0.064419 | 0.012293 | 0.042605 | 122.3462 | 122.3501 | 122.2105 | 122.2144
3507.9062 | 122.374 | -0.07782 | 122.2687 | 0.13101 | 0.18842 | 0.17114 | 0.17186 | 0.18734 | 0.26414 | 0.17077 | 122.3075 | 122.2054 | 122.1901 | 122.0988 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.20883 | 0.26624 | 0.24896 | 0.24968 | 0.26516 | 0.34196 | 0.24859 | 122.3487 | 122.2466 | 122.2313 | 122.14 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3233 | 122.3364 | 122.2059 | 122.219
3509.6562 | 122.4518 | -0.073242 | 122.2504 | 0.13101 | 0.18384 | 0.17114 | 0.16728 | 0.18734 | 0.25956 | 0.16161 | 122.312 | 122.1963 | 122.1809 | 122.0851 | -0.011281 | 0.018642 | -0.028906 | -0.003172 | 0.20425 | 0.25708 | 0.24439 | 0.24052 | 0.26058 | 0.3328 | 0.23486 | 122.3532 | 122.2375 | 122.2221 | 122.1263 | 0.029918 | 0.059841 | 0.012293 | 0.038027 | 122.3233 | 122.341 | 122.1922 | 122.2098
3511.3438 | 122.4564 | -0.041199 | 122.2458 | 0.14017 | 0.19758 | 0.18946 | 0.18559 | 0.19192 | 0.27787 | 0.16619 | 122.3212 | 122.1917 | 122.1855 | 122.0943 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.18136 | 0.23878 | 0.23066 | 0.22679 | 0.23311 | 0.31907 | 0.20739 | 122.3624 | 122.2329 | 122.2267 | 122.1355 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3416 | 122.3547 | 122.2059 | 122.219
3513.1094 | 122.3648 | -0.091553 | 122.2733 | 0.13559 | 0.20216 | 0.19404 | 0.18559 | 0.20565 | 0.2733 | 0.17535 | 122.312 | 122.21 | 122.1855 | 122.0988 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.22714 | 0.29371 | 0.28559 | 0.27715 | 0.2972 | 0.36485 | 0.2669 | 122.3532 | 122.2512 | 122.2267 | 122.14 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3279 | 122.341 | 122.2014 | 122.2144
3514.8125 | 122.3831 | -0.10071 | 122.2778 | 0.14017 | 0.19758 | 0.1803 | 0.18102 | 0.20107 | 0.26414 | 0.17535 | 122.3166 | 122.1963 | 122.1855 | 122.0897 | -0.020437 | 0.018642 | -0.033484 | -0.00775 | 0.24087 | 0.29829 | 0.28101 | 0.28172 | 0.30178 | 0.36485 | 0.27606 | 122.3578 | 122.2375 | 122.2267 | 122.1309 | 0.020762 | 0.059841 | 0.007715 | 0.033449 | 122.3371 | 122.3501 | 122.2059 | 122.219
3516.5781 | 122.4106 | -0.073242 | 122.2321 | 0.12643 | 0.193 | 0.18488 | 0.18559 | 0.19649 | 0.2733 | 0.17993 | 122.3166 | 122.2054 | 122.1809 | 122.0943 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.19967 | 0.26624 | 0.25812 | 0.25884 | 0.26974 | 0.34654 | 0.25317 | 122.3578 | 122.2466 | 122.2221 | 122.1355 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3325 | 122.3547 | 122.1968 | 122.219
3518.3438 | 122.4884 | -0.064087 | 122.2366 | 0.13101 | 0.20216 | 0.18488 | 0.18559 | 0.20107 | 0.27787 | 0.17993 | 122.312 | 122.1963 | 122.1901 | 122.0943 | -0.006702 | 0.02322 | -0.033484 | 0.005985 | 0.1951 | 0.26624 | 0.24897 | 0.24968 | 0.26516 | 0.34196 | 0.24401 | 122.3532 | 122.2375 | 122.2313 | 122.1355 | 0.034497 | 0.064419 | 0.007715 | 0.047184 | 122.3187 | 122.3455 | 122.1968 | 122.2236
3520.0625 | 122.3877 | -0.082397 | 122.2778 | 0.14017 | 0.21589 | 0.19862 | 0.19933 | 0.21023 | 0.29161 | 0.19824 | 122.3212 | 122.1917 | 122.1855 | 122.0943 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.22256 | 0.29829 | 0.28101 | 0.28173 | 0.29262 | 0.37401 | 0.28064 | 122.3624 | 122.2329 | 122.2267 | 122.1355 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.2014 | 122.219
3521.8438 | 122.4609 | -0.050354 | 122.2366 | 0.14474 | 0.21589 | 0.19862 | 0.19475 | 0.21023 | 0.28703 | 0.18908 | 122.3166 | 122.2009 | 122.1901 | 122.0897 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.1951 | 0.26625 | 0.24897 | 0.24511 | 0.26058 | 0.33739 | 0.23944 | 122.3578 | 122.2421 | 122.2313 | 122.1309 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3523.6094 | 122.438 | -0.050354 | 122.2412 | 0.14017 | 0.193 | 0.18946 | 0.18102 | 0.19649 | 0.27787 | 0.1845 | 122.312 | 122.1963 | 122.1809 | 122.0897 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.19052 | 0.24335 | 0.23981 | 0.23137 | 0.24685 | 0.32823 | 0.23486 | 122.3532 | 122.2375 | 122.2221 | 122.1309 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3279 | 122.3501 | 122.1968 | 122.219
3525.375 | 122.3328 | -0.10071 | 122.2778 | 0.14474 | 0.20674 | 0.19862 | 0.19933 | 0.21023 | 0.28703 | 0.19366 | 122.312 | 122.1917 | 122.1855 | 122.0988 | -0.015859 | 0.027798 | -0.038063 | -0.012328 | 0.24545 | 0.30744 | 0.29932 | 0.30004 | 0.31094 | 0.38774 | 0.29437 | 122.3532 | 122.2329 | 122.2267 | 122.14 | 0.02534 | 0.068997 | 0.003136 | 0.028871 | 122.3279 | 122.3501 | 122.2014 | 122.2236
3527.0938 | 122.525 | -0.054932 | 122.2549 | 0.14017 | 0.21131 | 0.20777 | 0.19475 | 0.21938 | 0.28245 | 0.19366 | 122.3166 | 122.1963 | 122.1809 | 122.0943 | -0.015859 | 0.027798 | -0.042641 | 0.001406 | 0.1951 | 0.26625 | 0.26271 | 0.24968 | 0.27431 | 0.33739 | 0.24859 | 122.3578 | 122.2375 | 122.2221 | 122.1355 | 0.02534 | 0.068997 | -0.001442 | 0.042605 | 122.3325 | 122.3593 | 122.1968 | 122.2236
3528.8594 | 122.4472 | -0.050354 | 122.2183 | 0.14017 | 0.21589 | 0.20777 | 0.19933 | 0.21938 | 0.28703 | 0.19824 | 122.312 | 122.1963 | 122.1855 | 122.0988 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.19052 | 0.26625 | 0.25813 | 0.24968 | 0.26974 | 0.33739 | 0.24859 | 122.3532 | 122.2375 | 122.2267 | 122.14 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3279 | 122.3455 | 122.2014 | 122.219
3530.625 | 122.4701 | -0.036621 | 122.2366 | 0.14932 | 0.22047 | 0.21235 | 0.20849 | 0.22396 | 0.28703 | 0.19824 | 122.312 | 122.1963 | 122.1809 | 122.0897 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.18594 | 0.25709 | 0.24897 | 0.24511 | 0.26058 | 0.32365 | 0.23486 | 122.3532 | 122.2375 | 122.2221 | 122.1309 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.3233 | 122.3455 | 122.1922 | 122.2144
3532.3281 | 122.3465 | -0.10529 | 122.2687 | 0.14474 | 0.22963 | 0.22151 | 0.21307 | 0.23312 | 0.30992 | 0.20739 | 122.312 | 122.1917 | 122.1855 | 122.0943 | -0.025015 | 0.027798 | -0.028906 | -0.012328 | 0.25003 | 0.33492 | 0.3268 | 0.31835 | 0.3384 | 0.41521 | 0.31268 | 122.3532 | 122.2329 | 122.2267 | 122.1355 | 0.016184 | 0.068997 | 0.012293 | 0.028871 | 122.3371 | 122.341 | 122.2105 | 122.2144
3534.1406 | 122.4655 | -0.068665 | 122.2549 | 0.14474 | 0.22963 | 0.22151 | 0.21764 | 0.23312 | 0.30535 | 0.20739 | 122.3166 | 122.1917 | 122.1855 | 122.1034 | -0.015859 | 0.02322 | -0.024328 | 0.005985 | 0.21341 | 0.29829 | 0.29017 | 0.28631 | 0.30178 | 0.37401 | 0.27606 | 122.3578 | 122.2329 | 122.2267 | 122.1446 | 0.02534 | 0.064419 | 0.016871 | 0.047184 | 122.3325 | 122.341 | 122.2014 | 122.2098
3535.8438 | 122.3373 | -0.09613 | 122.2549 | 0.15848 | 0.24794 | 0.23525 | 0.23138 | 0.24685 | 0.31908 | 0.21655 | 122.3212 | 122.1917 | 122.1855 | 122.0943 | -0.015859 | 0.027798 | -0.038063 | -0.00775 | 0.25461 | 0.34408 | 0.33137 | 0.32751 | 0.34298 | 0.41521 | 0.31268 | 122.3624 | 122.2329 | 122.2267 | 122.1355 | 0.02534 | 0.068997 | 0.003136 | 0.033449 | 122.3371 | 122.3593 | 122.2014 | 122.2236
3537.5781 | 122.4335 | -0.064087 | 122.2275 | 0.1539 | 0.23879 | 0.23067 | 0.2268 | 0.23769 | 0.3145 | 0.22113 | 122.3212 | 122.2009 | 122.1855 | 122.0897 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.21799 | 0.30287 | 0.29475 | 0.29089 | 0.30178 | 0.37859 | 0.28522 | 122.3624 | 122.2421 | 122.2267 | 122.1309 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3501 | 122.1968 | 122.2144
3539.3594 | 122.4747 | -0.041199 | 122.2549 | 0.1539 | 0.24337 | 0.23525 | 0.23596 | 0.24685 | 0.32366 | 0.21655 | 122.3212 | 122.2009 | 122.1901 | 122.0943 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.1951 | 0.28457 | 0.27644 | 0.27716 | 0.28805 | 0.36486 | 0.25775 | 122.3624 | 122.2421 | 122.2313 | 122.1355 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3541.0781 | 122.3511 | -0.11444 | 122.2641 | 0.15848 | 0.2571 | 0.2444 | 0.23596 | 0.25601 | 0.32366 | 0.23029 | 122.312 | 122.2009 | 122.1855 | 122.0943 | -0.020437 | 0.027798 | -0.033484 | 0.001406 | 0.27292 | 0.37154 | 0.35884 | 0.3504 | 0.37045 | 0.4381 | 0.34473 | 122.3532 | 122.2421 | 122.2267 | 122.1355 | 0.020762 | 0.068997 | 0.007715 | 0.042605 | 122.3325 | 122.3455 | 122.2059 | 122.219
3542.8594 | 122.3969 | -0.064087 | 122.2229 | 0.16306 | 0.2571 | 0.2444 | 0.24511 | 0.26059 | 0.33282 | 0.23486 | 122.3212 | 122.1963 | 122.1809 | 122.0897 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.22714 | 0.32119 | 0.30849 | 0.3092 | 0.32467 | 0.3969 | 0.29895 | 122.3624 | 122.2375 | 122.2221 | 122.1309 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.1968 | 122.2144
3544.6406 | 122.4838 | -0.064087 | 122.2458 | 0.14932 | 0.2571 | 0.25356 | 0.24511 | 0.26974 | 0.33282 | 0.23944 | 122.312 | 122.2009 | 122.1901 | 122.0943 | -0.015859 | 0.018642 | -0.038063 | -0.003172 | 0.21341 | 0.32119 | 0.31765 | 0.3092 | 0.33383 | 0.3969 | 0.30353 | 122.3532 | 122.2421 | 122.2313 | 122.1355 | 0.02534 | 0.059841 | 0.003136 | 0.038027 | 122.3279 | 122.3501 | 122.2059 | 122.2282
3546.3281 | 122.493 | -0.054932 | 122.2366 | 0.1539 | 0.26626 | 0.25814 | 0.25427 | 0.26516 | 0.32824 | 0.23944 | 122.312 | 122.1963 | 122.1855 | 122.0943 | -0.015859 | 0.027798 | -0.04722 | 0.005985 | 0.20883 | 0.32119 | 0.31307 | 0.3092 | 0.32009 | 0.38317 | 0.29437 | 122.3532 | 122.2375 | 122.2267 | 122.1355 | 0.02534 | 0.068997 | -0.006021 | 0.047184 | 122.3279 | 122.3593 | 122.2014 | 122.2327
3548.0938 | 122.3373 | -0.091553 | 122.2824 | 0.16306 | 0.26626 | 0.25814 | 0.25427 | 0.26974 | 0.33739 | 0.24402 | 122.3212 | 122.2054 | 122.1947 | 122.0943 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.25461 | 0.35781 | 0.34969 | 0.34582 | 0.36129 | 0.42895 | 0.33557 | 122.3624 | 122.2466 | 122.2359 | 122.1355 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3371 | 122.3501 | 122.2105 | 122.2236
3549.8438 | 122.3923 | -0.11444 | 122.2824 | 0.15848 | 0.27542 | 0.2673 | 0.26343 | 0.27432 | 0.35571 | 0.26233 | 122.312 | 122.2054 | 122.1901 | 122.0943 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 0.27292 | 0.38986 | 0.38174 | 0.37787 | 0.38876 | 0.47015 | 0.37677 | 122.3532 | 122.2466 | 122.2313 | 122.1355 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 122.3233 | 122.3501 | 122.2014 | 122.2282
3551.5938 | 122.3648 | -0.10986 | 122.2641 | 0.15848 | 0.28458 | 0.2673 | 0.25885 | 0.2789 | 0.35113 | 0.26233 | 122.3212 | 122.21 | 122.1855 | 122.0988 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.26834 | 0.39444 | 0.37716 | 0.36871 | 0.38876 | 0.46099 | 0.3722 | 122.3624 | 122.2512 | 122.2267 | 122.14 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3371 | 122.3547 | 122.2014 | 122.219
3553.2812 | 122.4701 | -0.050354 | 122.2458 | 0.16306 | 0.28 | 0.27187 | 0.26343 | 0.2789 | 0.35571 | 0.26233 | 122.3166 | 122.1963 | 122.1901 | 122.0943 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 0.21341 | 0.33035 | 0.32223 | 0.31378 | 0.32925 | 0.40606 | 0.31269 | 122.3578 | 122.2375 | 122.2313 | 122.1355 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 122.3233 | 122.3547 | 122.1968 | 122.2282
3555.0469 | 122.4335 | -0.059509 | 122.2412 | 0.16764 | 0.28458 | 0.27645 | 0.27259 | 0.28805 | 0.35113 | 0.26691 | 122.3212 | 122.1963 | 122.1855 | 122.0988 | -0.015859 | 0.014064 | -0.033484 | 0.001406 | 0.22714 | 0.34408 | 0.33596 | 0.33209 | 0.34756 | 0.41064 | 0.32642 | 122.3624 | 122.2375 | 122.2267 | 122.14 | 0.02534 | 0.055263 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.2014 | 122.219
3556.75 | 122.3923 | -0.09613 | 122.2504 | 0.16764 | 0.29831 | 0.28103 | 0.28174 | 0.29721 | 0.37402 | 0.27607 | 122.3166 | 122.1917 | 122.1992 | 122.1034 | -0.015859 | 0.018642 | -0.042641 | -0.00775 | 0.26377 | 0.39444 | 0.37716 | 0.37787 | 0.39334 | 0.47015 | 0.3722 | 122.3578 | 122.2329 | 122.2404 | 122.1446 | 0.02534 | 0.059841 | -0.001442 | 0.033449 | 122.3325 | 122.3593 | 122.2151 | 122.2419
3558.5156 | 122.4701 | -0.050354 | 122.2321 | 0.16306 | 0.28 | 0.28561 | 0.27716 | 0.29263 | 0.36944 | 0.27607 | 122.312 | 122.1963 | 122.1855 | 122.0851 | -0.015859 | 0.032376 | -0.038063 | 0.001406 | 0.21341 | 0.33035 | 0.33596 | 0.32752 | 0.34298 | 0.4198 | 0.32642 | 122.3532 | 122.2375 | 122.2267 | 122.1263 | 0.02534 | 0.073575 | 0.003136 | 0.042605 | 122.3279 | 122.3501 | 122.2014 | 122.2236
3560.2656 | 122.4289 | -0.07782 | 122.2321 | 0.17221 | 0.31205 | 0.30392 | 0.30006 | 0.30636 | 0.39691 | 0.29438 | 122.3212 | 122.1917 | 122.1809 | 122.0943 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.25003 | 0.38987 | 0.38174 | 0.37788 | 0.38418 | 0.47473 | 0.3722 | 122.3624 | 122.2329 | 122.2221 | 122.1355 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3325 | 122.3501 | 122.1922 | 122.2098
3562.0156 | 122.4152 | -0.07782 | 122.2412 | 0.17679 | 0.30289 | 0.28561 | 0.28632 | 0.29721 | 0.3786 | 0.28065 | 122.3166 | 122.2009 | 122.1809 | 122.0943 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.25461 | 0.38071 | 0.36343 | 0.36414 | 0.37503 | 0.45642 | 0.35847 | 122.3578 | 122.2421 | 122.2221 | 122.1355 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3279 | 122.3455 | 122.1922 | 122.2098
3563.7812 | 122.3373 | -0.11902 | 122.2778 | 0.17679 | 0.30289 | 0.29935 | 0.28632 | 0.30636 | 0.38318 | 0.28065 | 122.3212 | 122.2009 | 122.1901 | 122.0988 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.29581 | 0.42191 | 0.41836 | 0.40534 | 0.42538 | 0.5022 | 0.39966 | 122.3624 | 122.2421 | 122.2313 | 122.14 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3371 | 122.3593 | 122.2059 | 122.2282
3565.4844 | 122.3877 | -0.086975 | 122.2549 | 0.18137 | 0.31663 | 0.3085 | 0.30006 | 0.3201 | 0.38776 | 0.29438 | 122.3166 | 122.1963 | 122.1901 | 122.0943 | -0.020437 | 0.02322 | -0.024328 | 0.001406 | 0.26835 | 0.4036 | 0.39548 | 0.38703 | 0.40707 | 0.47473 | 0.38135 | 122.3578 | 122.2375 | 122.2313 | 122.1355 | 0.020762 | 0.064419 | 0.016871 | 0.042605 | 122.3371 | 122.341 | 122.2105 | 122.2144
3567.25 | 122.4335 | -0.054932 | 122.2183 | 0.17679 | 0.31663 | 0.30392 | 0.30463 | 0.31552 | 0.39233 | 0.2898 | 122.3166 | 122.2054 | 122.1947 | 122.0988 | -0.011281 | 0.02322 | -0.024328 | -0.00775 | 0.23172 | 0.37156 | 0.35886 | 0.35957 | 0.37045 | 0.44727 | 0.34473 | 122.3578 | 122.2466 | 122.2359 | 122.14 | 0.029918 | 0.064419 | 0.016871 | 0.033449 | 122.3279 | 122.341 | 122.2059 | 122.219
3569 | 122.4426 | -0.050354 | 122.2595 | 0.17679 | 0.32121 | 0.31308 | 0.30921 | 0.31094 | 0.38776 | 0.29896 | 122.3166 | 122.1963 | 122.1855 | 122.0897 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.22715 | 0.37156 | 0.36344 | 0.35957 | 0.3613 | 0.43811 | 0.34931 | 122.3578 | 122.2375 | 122.2267 | 122.1309 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3325 | 122.3501 | 122.2014 | 122.219
3570.7031 | 122.3328 | -0.091553 | 122.2595 | 0.17679 | 0.33036 | 0.32682 | 0.31837 | 0.33383 | 0.39691 | 0.30812 | 122.312 | 122.2054 | 122.1855 | 122.0943 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.26835 | 0.42192 | 0.41837 | 0.40992 | 0.42539 | 0.48847 | 0.39967 | 122.3532 | 122.2466 | 122.2267 | 122.1355 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3233 | 122.3455 | 122.1968 | 122.219
3572.4688 | 122.4609 | -0.059509 | 122.2458 | 0.18595 | 0.32578 | 0.32224 | 0.31379 | 0.33383 | 0.39691 | 0.30812 | 122.3166 | 122.1963 | 122.1901 | 122.0988 | -0.015859 | 0.027798 | -0.024328 | 0.001406 | 0.24546 | 0.38529 | 0.38175 | 0.3733 | 0.39334 | 0.45642 | 0.36762 | 122.3578 | 122.2375 | 122.2313 | 122.14 | 0.02534 | 0.068997 | 0.016871 | 0.042605 | 122.3325 | 122.341 | 122.2059 | 122.2144
3574.1719 | 122.4701 | -0.041199 | 122.2458 | 0.18595 | 0.33036 | 0.32682 | 0.32295 | 0.32925 | 0.41065 | 0.30812 | 122.312 | 122.2054 | 122.1901 | 122.0943 | -0.025015 | 0.032376 | -0.038063 | 0.001406 | 0.22715 | 0.37156 | 0.36802 | 0.36415 | 0.37045 | 0.45185 | 0.34931 | 122.3532 | 122.2466 | 122.2313 | 122.1355 | 0.016184 | 0.073575 | 0.003136 | 0.042605 | 122.3371 | 122.3501 | 122.2151 | 122.2282
3575.9375 | 122.4701 | -0.036621 | 122.2778 | 0.18595 | 0.33494 | 0.32682 | 0.32753 | 0.33841 | 0.41523 | 0.31269 | 122.3166 | 122.2054 | 122.1855 | 122.0897 | -0.020437 | 0.032376 | -0.033484 | -0.012328 | 0.22257 | 0.37156 | 0.36344 | 0.36415 | 0.37503 | 0.45185 | 0.34931 | 122.3578 | 122.2466 | 122.2267 | 122.1309 | 0.020762 | 0.073575 | 0.007715 | 0.028871 | 122.3371 | 122.3501 | 122.2059 | 122.219
3577.625 | 122.3328 | -0.091553 | 122.287 | 0.19053 | 0.33952 | 0.34055 | 0.33668 | 0.34757 | 0.4198 | 0.32185 | 122.3212 | 122.2054 | 122.1855 | 122.0943 | -0.025015 | 0.027798 | -0.033484 | 0.001406 | 0.28208 | 0.43107 | 0.43211 | 0.42824 | 0.43912 | 0.51136 | 0.4134 | 122.3624 | 122.2466 | 122.2267 | 122.1355 | 0.016184 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.3547 | 122.2105 | 122.219
3579.375 | 122.3602 | -0.086975 | 122.2458 | 0.18137 | 0.34868 | 0.34513 | 0.33668 | 0.34299 | 0.42438 | 0.33558 | 122.3075 | 122.2054 | 122.1809 | 122.0943 | -0.015859 | 0.027798 | -0.033484 | -0.00775 | 0.26835 | 0.43565 | 0.43211 | 0.42366 | 0.42996 | 0.51136 | 0.42256 | 122.3487 | 122.2466 | 122.2221 | 122.1355 | 0.02534 | 0.068997 | 0.007715 | 0.033449 | 122.3233 | 122.341 | 122.1968 | 122.2144
3581.1406 | 122.4289 | -0.068665 | 122.2549 | 0.19053 | 0.3441 | 0.34513 | 0.33668 | 0.34757 | 0.42438 | 0.33558 | 122.3212 | 122.2009 | 122.1855 | 122.0988 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 0.25919 | 0.41277 | 0.4138 | 0.40535 | 0.41623 | 0.49305 | 0.40425 | 122.3624 | 122.2421 | 122.2267 | 122.14 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 122.3279 | 122.3501 | 122.1922 | 122.2144
3582.8594 | 122.3557 | -0.10071 | 122.2824 | 0.19968 | 0.35326 | 0.34513 | 0.34584 | 0.35672 | 0.4198 | 0.33101 | 122.3166 | 122.2054 | 122.1947 | 122.0943 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.30039 | 0.45397 | 0.44584 | 0.44655 | 0.45743 | 0.52051 | 0.43171 | 122.3578 | 122.2466 | 122.2359 | 122.1355 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3455 | 122.2105 | 122.2236
3584.6406 | 122.4472 | -0.050354 | 122.2275 | 0.17221 | 0.29831 | 0.28561 | 0.28632 | 0.29721 | 0.36944 | 0.28065 | 122.3166 | 122.1963 | 122.1855 | 122.0943 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.22257 | 0.34867 | 0.33596 | 0.33668 | 0.34756 | 0.4198 | 0.331 | 122.3578 | 122.2375 | 122.2267 | 122.1355 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.3279 | 122.3455 | 122.1968 | 122.2144
3586.3906 | 122.3465 | -0.09613 | 122.2778 | 0.16306 | 0.25252 | 0.23525 | 0.23138 | 0.25143 | 0.32824 | 0.23029 | 122.312 | 122.2009 | 122.1901 | 122.0988 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.25919 | 0.34865 | 0.33137 | 0.32751 | 0.34756 | 0.42437 | 0.32642 | 122.3532 | 122.2421 | 122.2313 | 122.14 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3279 | 122.3455 | 122.2059 | 122.2236
3588.1562 | 122.4884 | -0.064087 | 122.2321 | 0.16764 | 0.24337 | 0.22609 | 0.23138 | 0.24685 | 0.32366 | 0.22571 | 122.312 | 122.2009 | 122.1855 | 122.0943 | -0.020437 | 0.02322 | -0.038063 | 0.005985 | 0.23172 | 0.30745 | 0.29018 | 0.29547 | 0.31094 | 0.38775 | 0.2898 | 122.3532 | 122.2421 | 122.2267 | 122.1355 | 0.020762 | 0.064419 | 0.003136 | 0.047184 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3589.8594 | 122.3328 | -0.10071 | 122.2733 | 0.16306 | 0.24337 | 0.23525 | 0.23138 | 0.24685 | 0.3145 | 0.22113 | 122.312 | 122.2009 | 122.1901 | 122.0943 | -0.025015 | 0.032376 | -0.028906 | -0.003172 | 0.26377 | 0.34407 | 0.33595 | 0.33209 | 0.34756 | 0.41521 | 0.32184 | 122.3532 | 122.2421 | 122.2313 | 122.1355 | 0.016184 | 0.073575 | 0.012293 | 0.038027 | 122.3371 | 122.341 | 122.2151 | 122.219
3591.6094 | 122.3877 | -0.068665 | 122.2641 | 0.16764 | 0.24337 | 0.23525 | 0.23596 | 0.24685 | 0.32824 | 0.23029 | 122.3166 | 122.21 | 122.1901 | 122.0943 | -0.015859 | 0.02322 | -0.033484 | 0.010563 | 0.2363 | 0.31203 | 0.30391 | 0.30462 | 0.31552 | 0.3969 | 0.29895 | 122.3578 | 122.2512 | 122.2313 | 122.1355 | 0.02534 | 0.064419 | 0.007715 | 0.051762 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3593.375 | 122.3831 | -0.082397 | 122.2595 | 0.16306 | 0.23879 | 0.23982 | 0.2268 | 0.23769 | 0.3145 | 0.21655 | 122.3166 | 122.21 | 122.1947 | 122.0943 | -0.015859 | 0.027798 | -0.024328 | -0.00775 | 0.24545 | 0.32118 | 0.32222 | 0.3092 | 0.32009 | 0.3969 | 0.29895 | 122.3578 | 122.2512 | 122.2359 | 122.1355 | 0.02534 | 0.068997 | 0.016871 | 0.033449 | 122.3325 | 122.341 | 122.2105 | 122.219
3595.1406 | 122.4243 | -0.054932 | 122.2321 | 0.1539 | 0.22047 | 0.20319 | 0.20391 | 0.21023 | 0.28703 | 0.19824 | 122.3258 | 122.1963 | 122.1901 | 122.0897 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.20883 | 0.2754 | 0.25813 | 0.25884 | 0.26516 | 0.34196 | 0.25317 | 122.367 | 122.2375 | 122.2313 | 122.1309 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3593 | 122.2014 | 122.2236
3596.9062 | 122.3373 | -0.10529 | 122.2733 | 0.1539 | 0.20674 | 0.20777 | 0.20391 | 0.2148 | 0.29619 | 0.19824 | 122.3166 | 122.1963 | 122.1947 | 122.0988 | -0.020437 | 0.02322 | -0.024328 | -0.003172 | 0.25919 | 0.31202 | 0.31306 | 0.30919 | 0.32009 | 0.40147 | 0.30352 | 122.3578 | 122.2375 | 122.2359 | 122.14 | 0.020762 | 0.064419 | 0.016871 | 0.038027 | 122.3371 | 122.341 | 122.2151 | 122.219
3598.6094 | 122.4976 | -0.054932 | 122.2458 | 0.15848 | 0.22047 | 0.20777 | 0.19933 | 0.21938 | 0.29161 | 0.19824 | 122.312 | 122.2054 | 122.1855 | 122.1034 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.21341 | 0.2754 | 0.26271 | 0.25426 | 0.27431 | 0.34654 | 0.25317 | 122.3532 | 122.2466 | 122.2267 | 122.1446 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3279 | 122.3455 | 122.2014 | 122.219
3600.3594 | 122.3511 | -0.07782 | 122.2778 | 0.15848 | 0.22505 | 0.21235 | 0.21307 | 0.23312 | 0.30535 | 0.21197 | 122.3212 | 122.1963 | 122.1855 | 122.0943 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.2363 | 0.30287 | 0.29017 | 0.29089 | 0.31094 | 0.38317 | 0.28979 | 122.3624 | 122.2375 | 122.2267 | 122.1355 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3371 | 122.3547 | 122.2014 | 122.219
3602.125 | 122.3877 | -0.09613 | 122.287 | 0.16764 | 0.22963 | 0.23067 | 0.2268 | 0.23312 | 0.30992 | 0.21197 | 122.3166 | 122.2009 | 122.1947 | 122.108 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.26377 | 0.32576 | 0.3268 | 0.32293 | 0.32925 | 0.40605 | 0.3081 | 122.3578 | 122.2421 | 122.2359 | 122.1492 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3371 | 122.3455 | 122.2151 | 122.2236
3603.8906 | 122.4976 | -0.064087 | 122.2366 | 0.16306 | 0.23879 | 0.22609 | 0.2268 | 0.23769 | 0.30077 | 0.21197 | 122.3166 | 122.1963 | 122.1992 | 122.0897 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.22714 | 0.30287 | 0.29018 | 0.29089 | 0.30178 | 0.36485 | 0.27606 | 122.3578 | 122.2375 | 122.2404 | 122.1309 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3501 | 122.2197 | 122.2327
3605.6406 | 122.4792 | -0.059509 | 122.2595 | 0.16306 | 0.22963 | 0.22609 | 0.22222 | 0.23769 | 0.29619 | 0.21197 | 122.312 | 122.2054 | 122.1809 | 122.0988 | -0.015859 | 0.018642 | -0.038063 | 0.005985 | 0.22257 | 0.28914 | 0.2856 | 0.28173 | 0.2972 | 0.3557 | 0.27148 | 122.3532 | 122.2466 | 122.2221 | 122.14 | 0.02534 | 0.059841 | 0.003136 | 0.047184 | 122.3279 | 122.3501 | 122.1968 | 122.219
3607.4062 | 122.3465 | -0.10986 | 122.287 | 0.16764 | 0.23879 | 0.23067 | 0.2268 | 0.24227 | 0.31908 | 0.22113 | 122.3166 | 122.2009 | 122.1901 | 122.1034 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.2775 | 0.34865 | 0.34053 | 0.33666 | 0.35214 | 0.42894 | 0.33099 | 122.3578 | 122.2421 | 122.2313 | 122.1446 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3609.1094 | 122.4335 | -0.050354 | 122.2412 | 0.17221 | 0.24794 | 0.23067 | 0.23138 | 0.25143 | 0.32366 | 0.23029 | 122.3212 | 122.1963 | 122.1901 | 122.0988 | -0.015859 | 0.02322 | -0.042641 | 0.001406 | 0.22257 | 0.2983 | 0.28102 | 0.28173 | 0.30178 | 0.37401 | 0.28064 | 122.3624 | 122.2375 | 122.2313 | 122.14 | 0.02534 | 0.064419 | -0.001442 | 0.042605 | 122.3371 | 122.3638 | 122.2059 | 122.2327
3610.8594 | 122.4792 | -0.050354 | 122.2549 | 0.18137 | 0.2571 | 0.25356 | 0.25427 | 0.26059 | 0.33739 | 0.24402 | 122.3166 | 122.2009 | 122.1901 | 122.0988 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.23172 | 0.30746 | 0.30391 | 0.30463 | 0.31094 | 0.38775 | 0.29437 | 122.3578 | 122.2421 | 122.2313 | 122.14 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3279 | 122.3501 | 122.2014 | 122.2236
3612.6094 | 122.3923 | -0.11444 | 122.2504 | 0.18137 | 0.27084 | 0.25814 | 0.25885 | 0.26516 | 0.35571 | 0.25318 | 122.3212 | 122.2054 | 122.1901 | 122.0943 | -0.020437 | 0.018642 | -0.033484 | 0.001406 | 0.29581 | 0.38528 | 0.37258 | 0.37329 | 0.3796 | 0.47015 | 0.36762 | 122.3624 | 122.2466 | 122.2313 | 122.1355 | 0.020762 | 0.059841 | 0.007715 | 0.042605 | 122.3416 | 122.3547 | 122.2105 | 122.2236
3614.3125 | 122.4701 | -0.045776 | 122.2412 | 0.18595 | 0.28458 | 0.27187 | 0.26801 | 0.27432 | 0.35113 | 0.26233 | 122.3166 | 122.2009 | 122.1901 | 122.0897 | -0.020437 | 0.02322 | -0.038063 | -0.003172 | 0.23172 | 0.33035 | 0.31765 | 0.31378 | 0.32009 | 0.39691 | 0.30811 | 122.3578 | 122.2421 | 122.2313 | 122.1309 | 0.020762 | 0.064419 | 0.003136 | 0.038027 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3616.0781 | 122.3877 | -0.086975 | 122.2687 | 0.20884 | 0.33952 | 0.34513 | 0.33211 | 0.33841 | 0.42438 | 0.33101 | 122.3258 | 122.2054 | 122.1901 | 122.0988 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.29581 | 0.4265 | 0.43211 | 0.41908 | 0.42539 | 0.51136 | 0.41798 | 122.367 | 122.2466 | 122.2313 | 122.14 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3416 | 122.3638 | 122.2059 | 122.2282
3617.8281 | 122.3969 | -0.068665 | 122.2458 | 0.18137 | 0.26626 | 0.26272 | 0.25427 | 0.26516 | 0.34655 | 0.2486 | 122.3166 | 122.2054 | 122.1947 | 122.1034 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.25004 | 0.33493 | 0.33138 | 0.32294 | 0.33383 | 0.41522 | 0.31726 | 122.3578 | 122.2466 | 122.2359 | 122.1446 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3325 | 122.3455 | 122.2105 | 122.2236
3619.5938 | 122.4609 | -0.041199 | 122.2412 | 0.17679 | 0.27084 | 0.25356 | 0.25885 | 0.27432 | 0.33739 | 0.23944 | 122.3258 | 122.2009 | 122.1901 | 122.1034 | -0.025015 | 0.02322 | -0.033484 | -0.00775 | 0.21799 | 0.31204 | 0.29476 | 0.30005 | 0.31552 | 0.37859 | 0.28064 | 122.367 | 122.2421 | 122.2313 | 122.1446 | 0.016184 | 0.064419 | 0.007715 | 0.033449 | 122.3508 | 122.3593 | 122.2151 | 122.2236
3621.3594 | 122.4335 | -0.059509 | 122.2412 | 0.18595 | 0.26168 | 0.25814 | 0.25427 | 0.26974 | 0.35113 | 0.26233 | 122.312 | 122.21 | 122.1901 | 122.0988 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.24546 | 0.32119 | 0.31765 | 0.31378 | 0.32925 | 0.41064 | 0.32184 | 122.3532 | 122.2512 | 122.2313 | 122.14 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3279 | 122.341 | 122.2059 | 122.219
3623.125 | 122.3511 | -0.086975 | 122.2916 | 0.18595 | 0.27542 | 0.2673 | 0.26343 | 0.2789 | 0.34655 | 0.25318 | 122.3212 | 122.2054 | 122.1855 | 122.0988 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.27292 | 0.36239 | 0.35427 | 0.3504 | 0.36587 | 0.43353 | 0.34015 | 122.3624 | 122.2466 | 122.2267 | 122.14 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.2014 | 122.219
3624.8281 | 122.4197 | -0.050354 | 122.2641 | 0.18595 | 0.26626 | 0.25814 | 0.25885 | 0.26974 | 0.33739 | 0.2486 | 122.3166 | 122.2009 | 122.1901 | 122.0943 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.2363 | 0.31661 | 0.30849 | 0.3092 | 0.3201 | 0.38775 | 0.29895 | 122.3578 | 122.2421 | 122.2313 | 122.1355 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3626.5781 | 122.4701 | -0.041199 | 122.2458 | 0.17679 | 0.27084 | 0.25356 | 0.26343 | 0.27432 | 0.33282 | 0.2486 | 122.3212 | 122.2009 | 122.1901 | 122.0988 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.21799 | 0.31204 | 0.29476 | 0.30463 | 0.31552 | 0.37401 | 0.2898 | 122.3624 | 122.2421 | 122.2313 | 122.14 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3628.3281 | 122.4655 | -0.064087 | 122.2458 | 0.19968 | 0.28915 | 0.28561 | 0.27259 | 0.29721 | 0.36486 | 0.27149 | 122.3212 | 122.2009 | 122.1947 | 122.0943 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.26377 | 0.35324 | 0.3497 | 0.33667 | 0.3613 | 0.42895 | 0.33558 | 122.3624 | 122.2421 | 122.2359 | 122.1355 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3630.0938 | 122.3465 | -0.091553 | 122.2641 | 0.19053 | 0.30747 | 0.29477 | 0.28632 | 0.30179 | 0.3786 | 0.27607 | 122.3212 | 122.2009 | 122.1992 | 122.108 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.28208 | 0.39902 | 0.38632 | 0.37787 | 0.39334 | 0.47015 | 0.36762 | 122.3624 | 122.2421 | 122.2404 | 122.1492 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.3371 | 122.3547 | 122.2151 | 122.2327
3631.7969 | 122.3969 | -0.10529 | 122.2687 | 0.19968 | 0.30747 | 0.29477 | 0.29548 | 0.31094 | 0.38776 | 0.2898 | 122.3166 | 122.2054 | 122.1855 | 122.0988 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.30497 | 0.41275 | 0.40005 | 0.40076 | 0.41623 | 0.49304 | 0.39509 | 122.3578 | 122.2466 | 122.2267 | 122.14 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.3325 | 122.3455 | 122.2014 | 122.2144
3633.5625 | 122.3831 | -0.073242 | 122.2824 | 0.19968 | 0.31205 | 0.30392 | 0.30006 | 0.31094 | 0.38318 | 0.28522 | 122.3212 | 122.21 | 122.1947 | 122.0988 | -0.020437 | 0.027798 | -0.038063 | -0.003172 | 0.27293 | 0.38529 | 0.37717 | 0.3733 | 0.38418 | 0.45642 | 0.35847 | 122.3624 | 122.2512 | 122.2359 | 122.14 | 0.020762 | 0.068997 | 0.003136 | 0.038027 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3635.3281 | 122.3694 | -0.10071 | 122.3007 | 0.19968 | 0.30289 | 0.29935 | 0.2909 | 0.30636 | 0.39233 | 0.28522 | 122.3212 | 122.2054 | 122.1992 | 122.1034 | -0.015859 | 0.02322 | -0.038063 | -0.00775 | 0.30039 | 0.4036 | 0.40005 | 0.39161 | 0.40707 | 0.49304 | 0.38593 | 122.3624 | 122.2466 | 122.2404 | 122.1446 | 0.02534 | 0.064419 | 0.003136 | 0.033449 | 122.3371 | 122.3593 | 122.2151 | 122.2373
3637.0781 | 122.4655 | -0.068665 | 122.2137 | 0.19968 | 0.29831 | 0.29019 | 0.28632 | 0.29721 | 0.37402 | 0.28065 | 122.312 | 122.2009 | 122.1947 | 122.0988 | -0.015859 | 0.018642 | -0.028906 | 0.001406 | 0.26835 | 0.36698 | 0.35885 | 0.35499 | 0.36587 | 0.44269 | 0.34931 | 122.3532 | 122.2421 | 122.2359 | 122.14 | 0.02534 | 0.059841 | 0.012293 | 0.042605 | 122.3279 | 122.341 | 122.2105 | 122.2236
3638.8281 | 122.4518 | -0.050354 | 122.2687 | 0.20884 | 0.33036 | 0.3314 | 0.32753 | 0.33841 | 0.41065 | 0.31727 | 122.3166 | 122.1963 | 122.1855 | 122.0943 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 0.25919 | 0.38072 | 0.38175 | 0.37788 | 0.38876 | 0.461 | 0.36763 | 122.3578 | 122.2375 | 122.2267 | 122.1355 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 122.3325 | 122.3547 | 122.2014 | 122.2236
3640.5938 | 122.4335 | -0.054932 | 122.2412 | 0.20426 | 0.32578 | 0.31308 | 0.30463 | 0.31094 | 0.39233 | 0.29438 | 122.3212 | 122.2009 | 122.1901 | 122.0988 | -0.015859 | 0.02322 | -0.042641 | 0.001406 | 0.25919 | 0.38072 | 0.36801 | 0.35957 | 0.36587 | 0.44727 | 0.34931 | 122.3624 | 122.2421 | 122.2313 | 122.14 | 0.02534 | 0.064419 | -0.001442 | 0.042605 | 122.3371 | 122.3638 | 122.2059 | 122.2327
3642.2812 | 122.3557 | -0.082397 | 122.2916 | 0.20884 | 0.31663 | 0.31766 | 0.31379 | 0.31552 | 0.39691 | 0.29896 | 122.3075 | 122.1963 | 122.1855 | 122.1034 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.29124 | 0.39902 | 0.40006 | 0.39619 | 0.39792 | 0.47931 | 0.38135 | 122.3487 | 122.2375 | 122.2267 | 122.1446 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3233 | 122.3455 | 122.2014 | 122.2236
3644.0469 | 122.3831 | -0.07782 | 122.2824 | 0.218 | 0.3441 | 0.32682 | 0.33211 | 0.33841 | 0.4198 | 0.32185 | 122.3166 | 122.2009 | 122.1901 | 122.0988 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.29582 | 0.42192 | 0.40464 | 0.40993 | 0.41623 | 0.49762 | 0.39967 | 122.3578 | 122.2421 | 122.2313 | 122.14 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3645.8125 | 122.4747 | -0.022888 | 122.2595 | 0.22715 | 0.36699 | 0.35887 | 0.35958 | 0.37046 | 0.43812 | 0.34932 | 122.3212 | 122.2009 | 122.1947 | 122.1034 | -0.025015 | 0.032376 | -0.033484 | -0.003172 | 0.25004 | 0.38988 | 0.38176 | 0.38246 | 0.39334 | 0.46101 | 0.37221 | 122.3624 | 122.2421 | 122.2359 | 122.1446 | 0.016184 | 0.073575 | 0.007715 | 0.038027 | 122.3462 | 122.3547 | 122.2197 | 122.2282
3647.5156 | 122.4289 | -0.045776 | 122.2641 | 0.22258 | 0.35784 | 0.35429 | 0.34584 | 0.35672 | 0.42896 | 0.33101 | 122.3166 | 122.21 | 122.1901 | 122.1034 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.26835 | 0.40361 | 0.40007 | 0.39162 | 0.4025 | 0.47474 | 0.37678 | 122.3578 | 122.2512 | 122.2313 | 122.1446 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3455 | 122.2059 | 122.219
3649.2812 | 122.4518 | -0.050354 | 122.2321 | 0.23173 | 0.37157 | 0.37718 | 0.35958 | 0.37961 | 0.45185 | 0.35847 | 122.3258 | 122.2009 | 122.1855 | 122.0988 | -0.025015 | 0.02322 | -0.042641 | 0.005985 | 0.28209 | 0.42193 | 0.42754 | 0.40993 | 0.42997 | 0.50221 | 0.40883 | 122.367 | 122.2421 | 122.2267 | 122.14 | 0.016184 | 0.064419 | -0.001442 | 0.047184 | 122.3508 | 122.3684 | 122.2105 | 122.2282
3651.0469 | 122.4518 | -0.059509 | 122.2504 | 0.25005 | 0.4082 | 0.40923 | 0.3962 | 0.4025 | 0.47932 | 0.3951 | 122.3166 | 122.2009 | 122.1901 | 122.0943 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 0.30955 | 0.46771 | 0.46874 | 0.45571 | 0.46201 | 0.53883 | 0.45461 | 122.3578 | 122.2421 | 122.2313 | 122.1355 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 122.3279 | 122.3547 | 122.2014 | 122.2282
3652.8125 | 122.4884 | -0.045776 | 122.2458 | 0.23631 | 0.38073 | 0.37718 | 0.37789 | 0.38877 | 0.46101 | 0.37221 | 122.3212 | 122.21 | 122.1992 | 122.0943 | -0.020437 | 0.02322 | -0.028906 | 0.005985 | 0.28209 | 0.42651 | 0.42296 | 0.42367 | 0.43454 | 0.50679 | 0.41798 | 122.3624 | 122.2512 | 122.2404 | 122.1355 | 0.020762 | 0.064419 | 0.012293 | 0.047184 | 122.3416 | 122.3501 | 122.2197 | 122.2282
3654.5781 | 122.3511 | -0.09613 | 122.2824 | 0.26378 | 0.44483 | 0.4367 | 0.43741 | 0.4437 | 0.52053 | 0.41799 | 122.3166 | 122.2009 | 122.1901 | 122.1034 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.35991 | 0.54096 | 0.53283 | 0.53354 | 0.53983 | 0.61666 | 0.51412 | 122.3578 | 122.2421 | 122.2313 | 122.1446 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3656.2812 | 122.4289 | -0.059509 | 122.2687 | 0.25005 | 0.4082 | 0.40008 | 0.3962 | 0.40708 | 0.47017 | 0.38137 | 122.3304 | 122.2009 | 122.1855 | 122.0988 | -0.025015 | 0.027798 | -0.033484 | 0.005985 | 0.30955 | 0.46771 | 0.45958 | 0.45571 | 0.46659 | 0.52968 | 0.44087 | 122.3716 | 122.2421 | 122.2267 | 122.14 | 0.016184 | 0.068997 | 0.007715 | 0.047184 | 122.3554 | 122.3638 | 122.2105 | 122.219
3658.0469 | 122.5067 | -0.059509 | 122.2412 | 0.26836 | 0.46773 | 0.47333 | 0.46488 | 0.47117 | 0.54342 | 0.45462 | 122.3258 | 122.1963 | 122.1901 | 122.1034 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.32787 | 0.52724 | 0.53284 | 0.52439 | 0.53068 | 0.60293 | 0.51413 | 122.367 | 122.2375 | 122.2313 | 122.1446 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2059 | 122.2236
3659.75 | 122.4472 | -0.045776 | 122.2412 | 0.28209 | 0.48604 | 0.49165 | 0.48778 | 0.49406 | 0.56631 | 0.47293 | 122.3166 | 122.2054 | 122.1901 | 122.0943 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.32787 | 0.53182 | 0.53742 | 0.53355 | 0.53984 | 0.61209 | 0.5187 | 122.3578 | 122.2466 | 122.2313 | 122.1355 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3661.5156 | 122.4609 | -0.041199 | 122.2275 | 0.29583 | 0.49978 | 0.50538 | 0.48778 | 0.50322 | 0.57089 | 0.47293 | 122.3166 | 122.2009 | 122.1855 | 122.0988 | -0.011281 | 0.02322 | -0.038063 | 0.005985 | 0.33703 | 0.54098 | 0.54658 | 0.52897 | 0.54442 | 0.61209 | 0.51413 | 122.3578 | 122.2421 | 122.2267 | 122.14 | 0.029918 | 0.064419 | 0.003136 | 0.047184 | 122.3279 | 122.3547 | 122.1968 | 122.2236
3663.2812 | 122.3557 | -0.10529 | 122.2916 | 0.30041 | 0.52267 | 0.5237 | 0.51067 | 0.53068 | 0.59836 | 0.50498 | 122.3258 | 122.1963 | 122.1901 | 122.0943 | -0.020437 | 0.027798 | -0.038063 | 0.005985 | 0.40569 | 0.62796 | 0.62898 | 0.61595 | 0.63597 | 0.70365 | 0.61026 | 122.367 | 122.2375 | 122.2313 | 122.1355 | 0.020762 | 0.068997 | 0.003136 | 0.047184 | 122.3462 | 122.3638 | 122.2105 | 122.2282
3665.0469 | 122.3831 | -0.07782 | 122.2549 | 0.30041 | 0.51809 | 0.5237 | 0.50609 | 0.52611 | 0.59378 | 0.5004 | 122.3212 | 122.2054 | 122.1901 | 122.1034 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.37823 | 0.59591 | 0.60152 | 0.58391 | 0.60393 | 0.6716 | 0.57822 | 122.3624 | 122.2466 | 122.2313 | 122.1446 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.3325 | 122.3593 | 122.2014 | 122.2282
3666.8125 | 122.3648 | -0.11444 | 122.2916 | 0.30956 | 0.53641 | 0.53743 | 0.51982 | 0.53526 | 0.60752 | 0.51871 | 122.3166 | 122.2054 | 122.1901 | 122.0988 | -0.011281 | 0.02322 | -0.038063 | 0.001406 | 0.42401 | 0.65085 | 0.65187 | 0.63426 | 0.6497 | 0.72196 | 0.63315 | 122.3578 | 122.2466 | 122.2313 | 122.14 | 0.029918 | 0.064419 | 0.003136 | 0.042605 | 122.3279 | 122.3547 | 122.2014 | 122.2282
3668.5156 | 122.4747 | -0.054932 | 122.2321 | 0.3233 | 0.55473 | 0.5649 | 0.55187 | 0.56273 | 0.63499 | 0.54618 | 122.3258 | 122.2009 | 122.1855 | 122.1034 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.37823 | 0.60966 | 0.61984 | 0.6068 | 0.61766 | 0.68992 | 0.60111 | 122.367 | 122.2421 | 122.2267 | 122.1446 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3416 | 122.3547 | 122.2014 | 122.2144
3670.2812 | 122.3969 | -0.10071 | 122.2733 | 0.30956 | 0.52267 | 0.53285 | 0.51982 | 0.52611 | 0.6121 | 0.50955 | 122.3212 | 122.2054 | 122.1947 | 122.0988 | -0.015859 | 0.032376 | -0.033484 | -0.00775 | 0.41027 | 0.62338 | 0.63356 | 0.62053 | 0.62681 | 0.71281 | 0.61026 | 122.3624 | 122.2466 | 122.2359 | 122.14 | 0.02534 | 0.073575 | 0.007715 | 0.033449 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3672.0312 | 122.4014 | -0.086975 | 122.2687 | 0.30499 | 0.50894 | 0.50538 | 0.50609 | 0.51695 | 0.58921 | 0.48666 | 122.3258 | 122.1963 | 122.1947 | 122.0988 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.39196 | 0.59591 | 0.59236 | 0.59306 | 0.60393 | 0.67618 | 0.57364 | 122.367 | 122.2375 | 122.2359 | 122.14 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3416 | 122.3638 | 122.2105 | 122.2327
3673.7969 | 122.3923 | -0.068665 | 122.2687 | 0.30956 | 0.52267 | 0.52828 | 0.50609 | 0.52153 | 0.60294 | 0.50498 | 122.3258 | 122.2009 | 122.1947 | 122.0988 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.37823 | 0.59134 | 0.59694 | 0.57475 | 0.59019 | 0.67161 | 0.57364 | 122.367 | 122.2421 | 122.2359 | 122.14 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3675.5625 | 122.4289 | -0.050354 | 122.2412 | 0.30499 | 0.51352 | 0.50996 | 0.49693 | 0.50322 | 0.58005 | 0.48666 | 122.3212 | 122.2009 | 122.1901 | 122.108 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 0.35534 | 0.56387 | 0.56032 | 0.54729 | 0.55357 | 0.6304 | 0.53702 | 122.3624 | 122.2421 | 122.2313 | 122.1492 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.3416 | 122.3501 | 122.2105 | 122.219
3677.3281 | 122.4838 | -0.054932 | 122.2321 | 0.30956 | 0.53183 | 0.53743 | 0.51525 | 0.53526 | 0.6121 | 0.51871 | 122.3212 | 122.2009 | 122.1947 | 122.0988 | -0.011281 | 0.027798 | -0.038063 | 0.005985 | 0.3645 | 0.58676 | 0.59237 | 0.57018 | 0.59019 | 0.66703 | 0.57364 | 122.3624 | 122.2421 | 122.2359 | 122.14 | 0.029918 | 0.068997 | 0.003136 | 0.047184 | 122.3325 | 122.3593 | 122.2059 | 122.2327
3679.0312 | 122.4747 | -0.050354 | 122.2458 | 0.32788 | 0.55015 | 0.55117 | 0.53814 | 0.549 | 0.62583 | 0.52329 | 122.3212 | 122.1963 | 122.1947 | 122.1034 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.37823 | 0.6005 | 0.60152 | 0.58849 | 0.59935 | 0.67619 | 0.57364 | 122.3624 | 122.2375 | 122.2359 | 122.1446 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3547 | 122.2151 | 122.2282
3680.7969 | 122.4014 | -0.082397 | 122.2916 | 0.33703 | 0.57304 | 0.58322 | 0.57019 | 0.57189 | 0.6533 | 0.55991 | 122.3212 | 122.1963 | 122.1901 | 122.0988 | -0.015859 | 0.018642 | -0.033484 | -0.00775 | 0.41943 | 0.65544 | 0.66562 | 0.65258 | 0.65428 | 0.7357 | 0.64231 | 122.3624 | 122.2375 | 122.2313 | 122.14 | 0.02534 | 0.059841 | 0.007715 | 0.033449 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3682.5 | 122.4792 | -0.045776 | 122.2229 | 0.36451 | 0.60509 | 0.62443 | 0.59766 | 0.61767 | 0.68077 | 0.59196 | 122.3258 | 122.1963 | 122.1901 | 122.108 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.41028 | 0.65087 | 0.6702 | 0.64343 | 0.66344 | 0.72655 | 0.63774 | 122.367 | 122.2375 | 122.2313 | 122.1492 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2059 | 122.2236
3684.2656 | 122.3648 | -0.091553 | 122.2824 | 0.35535 | 0.60967 | 0.61985 | 0.60681 | 0.61767 | 0.69451 | 0.59654 | 122.3212 | 122.2009 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 0.4469 | 0.70122 | 0.7114 | 0.69837 | 0.70922 | 0.78606 | 0.68809 | 122.3624 | 122.2421 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 122.3325 | 122.3593 | 122.2059 | 122.2327
3686.0156 | 122.374 | -0.09613 | 122.2824 | 0.37366 | 0.62341 | 0.62901 | 0.61597 | 0.62682 | 0.69909 | 0.59654 | 122.3166 | 122.2009 | 122.1901 | 122.1034 | -0.015859 | 0.027798 | -0.042641 | 0.001406 | 0.46979 | 0.71954 | 0.72514 | 0.7121 | 0.72295 | 0.79522 | 0.69267 | 122.3578 | 122.2421 | 122.2313 | 122.1446 | 0.02534 | 0.068997 | -0.001442 | 0.042605 | 122.3325 | 122.3593 | 122.2059 | 122.2327
3687.7656 | 122.3282 | -0.091553 | 122.2733 | 0.36908 | 0.61883 | 0.62901 | 0.61139 | 0.6314 | 0.69451 | 0.60112 | 122.3166 | 122.2054 | 122.1901 | 122.1034 | -0.015859 | 0.027798 | -0.033484 | 0.005985 | 0.46064 | 0.71038 | 0.72056 | 0.70295 | 0.72295 | 0.78606 | 0.69267 | 122.3578 | 122.2466 | 122.2313 | 122.1446 | 0.02534 | 0.068997 | 0.007715 | 0.047184 | 122.3325 | 122.3501 | 122.2059 | 122.2236
3689.4688 | 122.4884 | -0.050354 | 122.2229 | 0.37366 | 0.62341 | 0.63358 | 0.62055 | 0.62682 | 0.69909 | 0.6057 | 122.3212 | 122.21 | 122.1947 | 122.108 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.42402 | 0.67376 | 0.68394 | 0.6709 | 0.67717 | 0.74944 | 0.65605 | 122.3624 | 122.2512 | 122.2359 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3325 | 122.3547 | 122.2059 | 122.2282
3691.2344 | 122.4701 | -0.032043 | 122.2412 | 0.37824 | 0.62799 | 0.63816 | 0.62513 | 0.6314 | 0.70824 | 0.61027 | 122.3166 | 122.1963 | 122.1947 | 122.1034 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.41028 | 0.66003 | 0.67021 | 0.65717 | 0.66344 | 0.74029 | 0.64232 | 122.3578 | 122.2375 | 122.2359 | 122.1446 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.3279 | 122.3501 | 122.2059 | 122.2282
3693 | 122.4197 | -0.068665 | 122.2687 | 0.3874 | 0.65088 | 0.66563 | 0.64802 | 0.65429 | 0.73114 | 0.63774 | 122.3212 | 122.2009 | 122.1947 | 122.1034 | -0.015859 | 0.018642 | -0.038063 | -0.003172 | 0.45606 | 0.71955 | 0.7343 | 0.71669 | 0.72295 | 0.7998 | 0.70641 | 122.3624 | 122.2421 | 122.2359 | 122.1446 | 0.02534 | 0.059841 | 0.003136 | 0.038027 | 122.3371 | 122.3593 | 122.2105 | 122.2327
3694.7812 | 122.3831 | -0.082397 | 122.2733 | 0.39655 | 0.6463 | 0.66105 | 0.64802 | 0.65887 | 0.73571 | 0.63316 | 122.3258 | 122.2009 | 122.1901 | 122.108 | -0.015859 | 0.018642 | -0.033484 | 0.010563 | 0.47895 | 0.7287 | 0.74345 | 0.73042 | 0.74126 | 0.81811 | 0.71556 | 122.367 | 122.2421 | 122.2313 | 122.1492 | 0.02534 | 0.059841 | 0.007715 | 0.051762 | 122.3416 | 122.3593 | 122.2059 | 122.2236
3696.5625 | 122.4701 | -0.041199 | 122.2458 | 0.40113 | 0.66004 | 0.67937 | 0.66176 | 0.6726 | 0.74487 | 0.65148 | 122.3258 | 122.1963 | 122.1901 | 122.1126 | -0.011281 | 0.02322 | -0.024328 | 0.001406 | 0.44233 | 0.70124 | 0.72057 | 0.70296 | 0.7138 | 0.78607 | 0.69268 | 122.367 | 122.2375 | 122.2313 | 122.1538 | 0.029918 | 0.064419 | 0.016871 | 0.042605 | 122.3371 | 122.3501 | 122.2014 | 122.2144
3698.25 | 122.3373 | -0.10529 | 122.2687 | 0.39655 | 0.6463 | 0.66563 | 0.64802 | 0.66344 | 0.73571 | 0.63316 | 122.3304 | 122.1963 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.50184 | 0.75159 | 0.77092 | 0.75331 | 0.76873 | 0.841 | 0.73845 | 122.3716 | 122.2375 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3462 | 122.3638 | 122.2105 | 122.2282
3699.9375 | 122.4838 | -0.018311 | 122.2321 | 0.40113 | 0.66462 | 0.67479 | 0.66176 | 0.6726 | 0.74029 | 0.6469 | 122.3212 | 122.2009 | 122.1992 | 122.1034 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.41944 | 0.68293 | 0.6931 | 0.68007 | 0.69091 | 0.7586 | 0.66521 | 122.3624 | 122.2421 | 122.2404 | 122.1446 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3325 | 122.3501 | 122.2105 | 122.2282
3701.7188 | 122.4609 | -0.059509 | 122.2504 | 0.40113 | 0.65088 | 0.66105 | 0.64344 | 0.65887 | 0.73571 | 0.63774 | 122.312 | 122.2009 | 122.1901 | 122.1034 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.46064 | 0.71039 | 0.72056 | 0.70295 | 0.71838 | 0.79522 | 0.69725 | 122.3532 | 122.2421 | 122.2313 | 122.1446 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3279 | 122.3455 | 122.2059 | 122.2236
3703.4844 | 122.4792 | -0.059509 | 122.2504 | 0.41487 | 0.6692 | 0.67937 | 0.67091 | 0.6726 | 0.75403 | 0.65606 | 122.3166 | 122.2009 | 122.1947 | 122.1034 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.47438 | 0.72871 | 0.73888 | 0.73042 | 0.73211 | 0.81354 | 0.71557 | 122.3578 | 122.2421 | 122.2359 | 122.1446 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.3279 | 122.3501 | 122.2059 | 122.2282
3705.25 | 122.4792 | -0.032043 | 122.2504 | 0.41487 | 0.67378 | 0.68853 | 0.68007 | 0.67718 | 0.75861 | 0.65606 | 122.3212 | 122.2054 | 122.1901 | 122.108 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.44691 | 0.70582 | 0.72057 | 0.71211 | 0.70922 | 0.79065 | 0.6881 | 122.3624 | 122.2466 | 122.2313 | 122.1492 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3706.9531 | 122.4747 | -0.045776 | 122.2412 | 0.41487 | 0.67378 | 0.6931 | 0.68465 | 0.68176 | 0.76318 | 0.66521 | 122.3212 | 122.2009 | 122.1992 | 122.1034 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.46064 | 0.71955 | 0.73888 | 0.73043 | 0.72753 | 0.80896 | 0.71099 | 122.3624 | 122.2421 | 122.2404 | 122.1446 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3416 | 122.3547 | 122.2197 | 122.2327
3708.7188 | 122.3511 | -0.10071 | 122.2824 | 0.43776 | 0.70125 | 0.72515 | 0.71212 | 0.72296 | 0.79065 | 0.69726 | 122.3166 | 122.2054 | 122.1992 | 122.108 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.53847 | 0.80196 | 0.82586 | 0.81283 | 0.82367 | 0.89136 | 0.79797 | 122.3578 | 122.2466 | 122.2404 | 122.1492 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3371 | 122.3501 | 122.2197 | 122.2327
3710.4844 | 122.3328 | -0.10071 | 122.287 | 0.43776 | 0.70583 | 0.72058 | 0.70296 | 0.72754 | 0.79523 | 0.69726 | 122.3212 | 122.2009 | 122.1855 | 122.1034 | -0.020437 | 0.02322 | -0.038063 | -0.003172 | 0.53847 | 0.80654 | 0.82129 | 0.80367 | 0.82825 | 0.89594 | 0.79797 | 122.3624 | 122.2421 | 122.2267 | 122.1446 | 0.020762 | 0.064419 | 0.003136 | 0.038027 | 122.3416 | 122.3593 | 122.2059 | 122.2236
3712.25 | 122.3923 | -0.07782 | 122.2687 | 0.45607 | 0.7333 | 0.74347 | 0.72586 | 0.73669 | 0.80897 | 0.72473 | 122.3212 | 122.1963 | 122.1947 | 122.1126 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.53389 | 0.81112 | 0.82129 | 0.80368 | 0.81451 | 0.88679 | 0.80255 | 122.3624 | 122.2375 | 122.2359 | 122.1538 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3713.9531 | 122.4655 | -0.064087 | 122.2321 | 0.45607 | 0.74704 | 0.75263 | 0.73043 | 0.74127 | 0.82728 | 0.73389 | 122.3212 | 122.2054 | 122.1947 | 122.1034 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.52016 | 0.81112 | 0.81671 | 0.79452 | 0.80536 | 0.89137 | 0.79797 | 122.3624 | 122.2466 | 122.2359 | 122.1446 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3325 | 122.3547 | 122.2059 | 122.2282
3715.7188 | 122.4655 | -0.045776 | 122.2321 | 0.46523 | 0.75162 | 0.75721 | 0.74875 | 0.755 | 0.8227 | 0.72931 | 122.3304 | 122.2009 | 122.1901 | 122.108 | -0.015859 | 0.027798 | -0.038063 | -0.003172 | 0.51101 | 0.79739 | 0.80298 | 0.79453 | 0.80078 | 0.86848 | 0.77508 | 122.3716 | 122.2421 | 122.2313 | 122.1492 | 0.02534 | 0.068997 | 0.003136 | 0.038027 | 122.3462 | 122.3684 | 122.2059 | 122.2282
3717.4219 | 122.3419 | -0.11902 | 122.287 | 0.47439 | 0.75619 | 0.77094 | 0.75333 | 0.76416 | 0.83644 | 0.7522 | 122.3166 | 122.2009 | 122.1947 | 122.1126 | -0.015859 | 0.018642 | -0.038063 | -0.003172 | 0.59341 | 0.87521 | 0.88996 | 0.87235 | 0.88318 | 0.95546 | 0.87122 | 122.3578 | 122.2421 | 122.2359 | 122.1538 | 0.02534 | 0.059841 | 0.003136 | 0.038027 | 122.3325 | 122.3547 | 122.2105 | 122.2327
3719.1875 | 122.4976 | -0.036621 | 122.2275 | 0.46523 | 0.73788 | 0.74347 | 0.73043 | 0.74127 | 0.80897 | 0.70642 | 122.3258 | 122.2009 | 122.1992 | 122.1034 | -0.020437 | 0.02322 | -0.028906 | -0.003172 | 0.50185 | 0.7745 | 0.78009 | 0.76706 | 0.77789 | 0.84559 | 0.74304 | 122.367 | 122.2421 | 122.2404 | 122.1446 | 0.020762 | 0.064419 | 0.012293 | 0.038027 | 122.3462 | 122.3547 | 122.2197 | 122.2282
3720.9531 | 122.4243 | -0.064087 | 122.2366 | 0.47439 | 0.74246 | 0.75263 | 0.74417 | 0.75043 | 0.81812 | 0.72473 | 122.3258 | 122.2054 | 122.1901 | 122.1034 | -0.020437 | 0.02322 | -0.033484 | -0.00775 | 0.53847 | 0.80654 | 0.81671 | 0.80826 | 0.81451 | 0.88221 | 0.78882 | 122.367 | 122.2466 | 122.2313 | 122.1446 | 0.020762 | 0.064419 | 0.007715 | 0.033449 | 122.3462 | 122.3593 | 122.2105 | 122.2236
3722.6562 | 122.3877 | -0.068665 | 122.2687 | 0.48354 | 0.76077 | 0.76178 | 0.74875 | 0.75958 | 0.83644 | 0.74762 | 122.3212 | 122.2009 | 122.1947 | 122.1034 | -0.015859 | 0.027798 | -0.028906 | -0.00775 | 0.55221 | 0.82944 | 0.83045 | 0.81741 | 0.82825 | 0.9051 | 0.81628 | 122.3624 | 122.2421 | 122.2359 | 122.1446 | 0.02534 | 0.068997 | 0.012293 | 0.033449 | 122.3371 | 122.3501 | 122.2105 | 122.2236
3724.4219 | 122.3877 | -0.082397 | 122.2504 | 0.48812 | 0.75619 | 0.76178 | 0.75333 | 0.76416 | 0.83186 | 0.74304 | 122.3258 | 122.2054 | 122.1992 | 122.108 | -0.020437 | 0.02322 | -0.033484 | 0.005985 | 0.57052 | 0.83859 | 0.84418 | 0.83572 | 0.84656 | 0.91426 | 0.82544 | 122.367 | 122.2466 | 122.2404 | 122.1492 | 0.020762 | 0.064419 | 0.007715 | 0.047184 | 122.3462 | 122.3593 | 122.2197 | 122.2327
3726.125 | 122.3465 | -0.10529 | 122.2778 | 0.47439 | 0.73788 | 0.75721 | 0.73959 | 0.74585 | 0.8227 | 0.72015 | 122.3212 | 122.2054 | 122.1947 | 122.108 | -0.020437 | 0.018642 | -0.033484 | -0.003172 | 0.57967 | 0.84316 | 0.86249 | 0.84488 | 0.85113 | 0.92799 | 0.82544 | 122.3624 | 122.2466 | 122.2359 | 122.1492 | 0.020762 | 0.059841 | 0.007715 | 0.038027 | 122.3416 | 122.3547 | 122.2151 | 122.2282
3727.8906 | 122.406 | -0.091553 | 122.2778 | 0.4927 | 0.75162 | 0.77094 | 0.75333 | 0.76874 | 0.84102 | 0.74762 | 122.3166 | 122.2054 | 122.1947 | 122.1126 | -0.015859 | 0.02322 | -0.038063 | -0.00775 | 0.58425 | 0.84317 | 0.86249 | 0.84488 | 0.86029 | 0.93257 | 0.83917 | 122.3578 | 122.2466 | 122.2359 | 122.1538 | 0.02534 | 0.064419 | 0.003136 | 0.033449 | 122.3325 | 122.3547 | 122.2105 | 122.2327
3729.6406 | 122.3419 | -0.10529 | 122.287 | 0.49728 | 0.76077 | 0.77552 | 0.75791 | 0.76874 | 0.84102 | 0.74762 | 122.3212 | 122.2009 | 122.1855 | 122.1034 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.60257 | 0.86606 | 0.88081 | 0.86319 | 0.87402 | 0.9463 | 0.85291 | 122.3624 | 122.2421 | 122.2267 | 122.1446 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.3371 | 122.3501 | 122.2014 | 122.2144
3731.4062 | 122.3282 | -0.10529 | 122.287 | 0.50186 | 0.76077 | 0.78468 | 0.76248 | 0.77332 | 0.84559 | 0.7522 | 122.3349 | 122.21 | 122.1901 | 122.1126 | -0.015859 | 0.02322 | -0.038063 | -0.00775 | 0.60714 | 0.86606 | 0.88996 | 0.86777 | 0.8786 | 0.95088 | 0.85748 | 122.3761 | 122.2512 | 122.2313 | 122.1538 | 0.02534 | 0.064419 | 0.003136 | 0.033449 | 122.3508 | 122.373 | 122.2059 | 122.2282
3733.1094 | 122.4838 | -0.059509 | 122.2412 | 0.50644 | 0.76535 | 0.77094 | 0.75791 | 0.75958 | 0.84559 | 0.74304 | 122.3258 | 122.2009 | 122.1992 | 122.1034 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.56595 | 0.82486 | 0.83045 | 0.81742 | 0.81909 | 0.9051 | 0.80255 | 122.367 | 122.2421 | 122.2404 | 122.1446 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.3416 | 122.3638 | 122.2151 | 122.2373
3734.8906 | 122.3785 | -0.086975 | 122.2504 | 0.50644 | 0.76993 | 0.7801 | 0.76706 | 0.77332 | 0.85017 | 0.74762 | 122.3212 | 122.2009 | 122.1947 | 122.1034 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.59341 | 0.85691 | 0.86707 | 0.85404 | 0.86029 | 0.93715 | 0.83459 | 122.3624 | 122.2421 | 122.2359 | 122.1446 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3371 | 122.3593 | 122.2105 | 122.2327
3736.6562 | 122.493 | -0.050354 | 122.2458 | 0.50644 | 0.76993 | 0.78926 | 0.76248 | 0.77332 | 0.85017 | 0.76135 | 122.3258 | 122.2009 | 122.2038 | 122.1126 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.55679 | 0.82028 | 0.83961 | 0.81284 | 0.82367 | 0.90053 | 0.81171 | 122.367 | 122.2421 | 122.245 | 122.1538 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.3416 | 122.3501 | 122.2197 | 122.2282
3738.4062 | 122.4472 | -0.050354 | 122.2412 | 0.52017 | 0.76535 | 0.77552 | 0.76706 | 0.77789 | 0.84559 | 0.75678 | 122.3258 | 122.2054 | 122.1992 | 122.0988 | -0.015859 | 0.027798 | -0.038063 | -0.00775 | 0.57053 | 0.81571 | 0.82587 | 0.81742 | 0.82825 | 0.89595 | 0.80713 | 122.367 | 122.2466 | 122.2404 | 122.14 | 0.02534 | 0.068997 | 0.003136 | 0.033449 | 122.3416 | 122.3638 | 122.2151 | 122.2373
3740.1719 | 122.4335 | -0.059509 | 122.2321 | 0.52475 | 0.78367 | 0.78926 | 0.7808 | 0.79163 | 0.86391 | 0.76135 | 122.3166 | 122.1963 | 122.1947 | 122.108 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.58426 | 0.84318 | 0.84876 | 0.84031 | 0.85114 | 0.92342 | 0.82086 | 122.3578 | 122.2375 | 122.2359 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3279 | 122.3501 | 122.2059 | 122.2282
3741.875 | 122.319 | -0.10071 | 122.287 | 0.52933 | 0.78367 | 0.79841 | 0.78995 | 0.79621 | 0.86391 | 0.77509 | 122.3212 | 122.2009 | 122.1947 | 122.1034 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.63004 | 0.88437 | 0.89912 | 0.89066 | 0.89691 | 0.96462 | 0.8758 | 122.3624 | 122.2421 | 122.2359 | 122.1446 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3371 | 122.3593 | 122.2105 | 122.2327
3743.6406 | 122.374 | -0.10529 | 122.2778 | 0.54306 | 0.80198 | 0.81215 | 0.79911 | 0.80078 | 0.87764 | 0.78424 | 122.3258 | 122.2054 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.64835 | 0.90727 | 0.91744 | 0.9044 | 0.90607 | 0.98293 | 0.88953 | 122.367 | 122.2466 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3745.3438 | 122.4289 | -0.054932 | 122.2458 | 0.54764 | 0.80198 | 0.81673 | 0.79911 | 0.80994 | 0.8868 | 0.78882 | 122.3258 | 122.2009 | 122.1947 | 122.108 | -0.025015 | 0.027798 | -0.038063 | -0.003172 | 0.60257 | 0.85691 | 0.87166 | 0.85404 | 0.86487 | 0.94173 | 0.84376 | 122.367 | 122.2421 | 122.2359 | 122.1492 | 0.016184 | 0.068997 | 0.003136 | 0.038027 | 122.3508 | 122.3638 | 122.2197 | 122.2327
3747.1094 | 122.438 | -0.068665 | 122.2549 | 0.5568 | 0.80198 | 0.81673 | 0.80827 | 0.8191 | 0.88222 | 0.7934 | 122.3258 | 122.2054 | 122.1901 | 122.1034 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.62546 | 0.87065 | 0.88539 | 0.87693 | 0.88776 | 0.95089 | 0.86207 | 122.367 | 122.2466 | 122.2313 | 122.1446 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.3325 | 122.3547 | 122.1968 | 122.219
3748.875 | 122.3877 | -0.064087 | 122.2687 | 0.57969 | 0.83861 | 0.84878 | 0.83574 | 0.84198 | 0.91885 | 0.82545 | 122.3258 | 122.2009 | 122.1947 | 122.108 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.64378 | 0.9027 | 0.91287 | 0.89983 | 0.90607 | 0.98294 | 0.88953 | 122.367 | 122.2421 | 122.2359 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3750.6406 | 122.3602 | -0.09613 | 122.2916 | 0.57053 | 0.82946 | 0.8442 | 0.82658 | 0.83741 | 0.91427 | 0.82087 | 122.3258 | 122.2054 | 122.1947 | 122.1034 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.66666 | 0.92559 | 0.94033 | 0.92271 | 0.93354 | 1.0104 | 0.917 | 122.367 | 122.2466 | 122.2359 | 122.1446 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3752.3281 | 122.3419 | -0.11444 | 122.3053 | 0.59342 | 0.84777 | 0.86251 | 0.84948 | 0.85572 | 0.93258 | 0.83461 | 122.3258 | 122.2009 | 122.1947 | 122.1172 | -0.020437 | 0.018642 | -0.042641 | 0.001406 | 0.70787 | 0.96221 | 0.97695 | 0.96392 | 0.97016 | 1.047 | 0.94905 | 122.367 | 122.2421 | 122.2359 | 122.1584 | 0.020762 | 0.059841 | -0.001442 | 0.042605 | 122.3462 | 122.3684 | 122.2151 | 122.2373
3754.0938 | 122.4747 | -0.045776 | 122.2137 | 0.61174 | 0.86151 | 0.87625 | 0.86321 | 0.87861 | 0.94632 | 0.8575 | 122.3304 | 122.1963 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.65752 | 0.90728 | 0.92202 | 0.90899 | 0.92439 | 0.9921 | 0.90327 | 122.3716 | 122.2375 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3462 | 122.3638 | 122.2105 | 122.2282
3755.7969 | 122.4197 | -0.059509 | 122.2687 | 0.598 | 0.84777 | 0.85794 | 0.84948 | 0.85572 | 0.91885 | 0.83461 | 122.3258 | 122.2009 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.65751 | 0.90728 | 0.91744 | 0.90899 | 0.91523 | 0.97836 | 0.89411 | 122.367 | 122.2421 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3757.5469 | 122.4106 | -0.064087 | 122.2321 | 0.67584 | 0.97598 | 0.98614 | 0.9731 | 0.97475 | 1.047 | 0.95364 | 122.3166 | 122.1963 | 122.1901 | 122.108 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.73992 | 1.0401 | 1.0502 | 1.0372 | 1.0388 | 1.1111 | 1.0177 | 122.3578 | 122.2375 | 122.2313 | 122.1492 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.3325 | 122.3455 | 122.2059 | 122.219
3759.3125 | 122.3602 | -0.091553 | 122.287 | 0.64837 | 0.92103 | 0.94035 | 0.92273 | 0.92439 | 1.0058 | 0.90785 | 122.3304 | 122.2054 | 122.1855 | 122.108 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 0.73992 | 1.0126 | 1.0319 | 1.0143 | 1.0159 | 1.0974 | 0.99941 | 122.3716 | 122.2466 | 122.2267 | 122.1492 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 122.3416 | 122.3684 | 122.1968 | 122.2236
3761.0781 | 122.4335 | -0.045776 | 122.2595 | 0.67584 | 0.9485 | 0.96324 | 0.95478 | 0.95186 | 1.0287 | 0.94448 | 122.3258 | 122.2054 | 122.1947 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.72161 | 0.99428 | 1.009 | 1.0006 | 0.99763 | 1.0745 | 0.99026 | 122.367 | 122.2466 | 122.2359 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3371 | 122.3547 | 122.2059 | 122.2236
3762.7969 | 122.4289 | -0.041199 | 122.2412 | 0.6621 | 0.93019 | 0.94035 | 0.92273 | 0.93354 | 1.0058 | 0.92617 | 122.3258 | 122.2009 | 122.1947 | 122.108 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.7033 | 0.97139 | 0.98155 | 0.96393 | 0.97474 | 1.047 | 0.96737 | 122.367 | 122.2421 | 122.2359 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3764.5625 | 122.4243 | -0.059509 | 122.2733 | 0.68499 | 0.9485 | 0.95866 | 0.94105 | 0.95643 | 1.0242 | 0.94448 | 122.3258 | 122.21 | 122.1947 | 122.108 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.7445 | 1.008 | 1.0182 | 1.0006 | 1.0159 | 1.0837 | 1.004 | 122.367 | 122.2512 | 122.2359 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3593 | 122.2059 | 122.2282
3766.3125 | 122.4701 | -0.032043 | 122.2595 | 0.63921 | 0.87982 | 0.88541 | 0.88153 | 0.88319 | 0.96005 | 0.8575 | 122.3258 | 122.1963 | 122.1947 | 122.108 | -0.020437 | 0.027798 | -0.033484 | 0.001406 | 0.67125 | 0.91187 | 0.91745 | 0.91357 | 0.91523 | 0.9921 | 0.88954 | 122.367 | 122.2375 | 122.2359 | 122.1492 | 0.020762 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.3593 | 122.2151 | 122.2282
3768.0781 | 122.438 | -0.050354 | 122.2504 | 0.64379 | 0.86608 | 0.88083 | 0.86321 | 0.86945 | 0.93716 | 0.85292 | 122.3258 | 122.2054 | 122.1901 | 122.108 | -0.015859 | 0.02322 | -0.033484 | -0.00775 | 0.69414 | 0.91644 | 0.93118 | 0.91356 | 0.91981 | 0.98752 | 0.90327 | 122.367 | 122.2466 | 122.2313 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.033449 | 122.3416 | 122.3593 | 122.2059 | 122.2236
3769.8438 | 122.4152 | -0.073242 | 122.2458 | 0.63005 | 0.85693 | 0.86251 | 0.85405 | 0.85572 | 0.93258 | 0.83461 | 122.3258 | 122.2009 | 122.1947 | 122.1034 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.70329 | 0.93017 | 0.93576 | 0.9273 | 0.92896 | 1.0058 | 0.90785 | 122.367 | 122.2421 | 122.2359 | 122.1446 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3593 | 122.2151 | 122.2282
3771.5469 | 122.3923 | -0.086975 | 122.2595 | 0.66668 | 0.90729 | 0.91288 | 0.89984 | 0.9015 | 0.97837 | 0.88954 | 122.3258 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.75365 | 0.99427 | 0.99985 | 0.98681 | 0.98847 | 1.0653 | 0.97652 | 122.367 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3773.2969 | 122.3419 | -0.10529 | 122.2916 | 0.67584 | 0.90272 | 0.91288 | 0.90442 | 0.90608 | 0.97379 | 0.89412 | 122.3212 | 122.2009 | 122.1855 | 122.1172 | -0.015859 | 0.018642 | -0.028906 | 0.001406 | 0.78112 | 1.008 | 1.0182 | 1.0097 | 1.0114 | 1.0791 | 0.99941 | 122.3624 | 122.2421 | 122.2267 | 122.1584 | 0.02534 | 0.059841 | 0.012293 | 0.042605 | 122.3371 | 122.3501 | 122.2014 | 122.2144
3775.0469 | 122.4289 | -0.068665 | 122.2321 | 0.68499 | 0.91187 | 0.92204 | 0.909 | 0.91981 | 0.9921 | 0.89412 | 122.312 | 122.1963 | 122.2038 | 122.108 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.75366 | 0.98054 | 0.9907 | 0.97766 | 0.98848 | 1.0608 | 0.96279 | 122.3532 | 122.2375 | 122.245 | 122.1492 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3325 | 122.341 | 122.2243 | 122.2327
3776.75 | 122.4518 | -0.050354 | 122.2641 | 0.69873 | 0.93019 | 0.94493 | 0.92731 | 0.93812 | 1.0104 | 0.91243 | 122.3166 | 122.2054 | 122.1947 | 122.108 | -0.020437 | 0.032376 | -0.028906 | -0.00775 | 0.74908 | 0.98054 | 0.99528 | 0.97766 | 0.98848 | 1.0608 | 0.96279 | 122.3578 | 122.2466 | 122.2359 | 122.1492 | 0.020762 | 0.073575 | 0.012293 | 0.033449 | 122.3371 | 122.3455 | 122.2151 | 122.2236
3778.5 | 122.3923 | -0.09613 | 122.2778 | 0.67126 | 0.88898 | 0.89914 | 0.89068 | 0.89234 | 0.96463 | 0.86665 | 122.3212 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.76739 | 0.98511 | 0.99527 | 0.98681 | 0.98847 | 1.0608 | 0.96278 | 122.3624 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3780.2656 | 122.4106 | -0.082397 | 122.3007 | 0.68957 | 0.89814 | 0.91746 | 0.91358 | 0.91523 | 0.98295 | 0.89412 | 122.3212 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.042641 | -0.00775 | 0.77197 | 0.98053 | 0.99985 | 0.99597 | 0.99763 | 1.0653 | 0.97652 | 122.3624 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | -0.001442 | 0.033449 | 122.3325 | 122.3638 | 122.2105 | 122.2419
3781.9844 | 122.3785 | -0.10529 | 122.287 | 0.71246 | 0.92103 | 0.94035 | 0.92273 | 0.92897 | 1.0058 | 0.90785 | 122.3304 | 122.2054 | 122.1992 | 122.1172 | -0.020437 | 0.02322 | -0.038063 | 0.001406 | 0.81775 | 1.0263 | 1.0456 | 1.028 | 1.0343 | 1.1111 | 1.0131 | 122.3716 | 122.2466 | 122.2404 | 122.1584 | 0.020762 | 0.064419 | 0.003136 | 0.042605 | 122.3508 | 122.3684 | 122.2197 | 122.2373
3783.75 | 122.3282 | -0.091553 | 122.3053 | 0.69873 | 0.90272 | 0.91746 | 0.89526 | 0.91065 | 0.98295 | 0.89412 | 122.3166 | 122.2009 | 122.1992 | 122.108 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.79028 | 0.99427 | 1.009 | 0.98681 | 1.0022 | 1.0745 | 0.98567 | 122.3578 | 122.2421 | 122.2404 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3325 | 122.3501 | 122.2151 | 122.2327
3785.5312 | 122.4655 | -0.054932 | 122.2641 | 0.70331 | 0.8844 | 0.9083 | 0.89068 | 0.88777 | 0.96463 | 0.88039 | 122.3349 | 122.2054 | 122.1947 | 122.1126 | -0.025015 | 0.027798 | -0.028906 | 0.001406 | 0.75824 | 0.93933 | 0.96323 | 0.94561 | 0.9427 | 1.0196 | 0.93532 | 122.3761 | 122.2466 | 122.2359 | 122.1538 | 0.016184 | 0.068997 | 0.012293 | 0.042605 | 122.36 | 122.3638 | 122.2197 | 122.2236
3787.2812 | 122.4701 | -0.045776 | 122.2733 | 0.72162 | 0.90729 | 0.93119 | 0.91358 | 0.92439 | 0.98752 | 0.8987 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.006702 | 0.02322 | -0.042641 | -0.003172 | 0.7674 | 0.95307 | 0.97697 | 0.95935 | 0.97017 | 1.0333 | 0.94448 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.034497 | 0.064419 | -0.001442 | 0.038027 | 122.3371 | 122.373 | 122.2059 | 122.2419
3788.9844 | 122.4014 | -0.068665 | 122.2549 | 0.72162 | 0.91645 | 0.92661 | 0.91815 | 0.91981 | 0.99668 | 0.90785 | 122.3166 | 122.21 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.79029 | 0.98512 | 0.99528 | 0.98682 | 0.98848 | 1.0653 | 0.97652 | 122.3578 | 122.2512 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3279 | 122.3501 | 122.2059 | 122.2282
3790.75 | 122.3511 | -0.10071 | 122.2916 | 0.76282 | 0.96682 | 0.98156 | 0.96852 | 0.97475 | 1.047 | 0.95364 | 122.3212 | 122.21 | 122.2038 | 122.1172 | -0.015859 | 0.018642 | -0.028906 | -0.003172 | 0.86353 | 1.0675 | 1.0823 | 1.0692 | 1.0755 | 1.1478 | 1.0543 | 122.3624 | 122.2512 | 122.245 | 122.1584 | 0.02534 | 0.059841 | 0.012293 | 0.038027 | 122.3371 | 122.3501 | 122.2197 | 122.2327
3792.4531 | 122.3511 | -0.086975 | 122.2961 | 0.74909 | 0.95308 | 0.95866 | 0.95478 | 0.95643 | 1.0287 | 0.93075 | 122.3212 | 122.2054 | 122.1992 | 122.1034 | -0.025015 | 0.027798 | -0.033484 | -0.00775 | 0.83607 | 1.0401 | 1.0456 | 1.0418 | 1.0434 | 1.1157 | 1.0177 | 122.3624 | 122.2466 | 122.2404 | 122.1446 | 0.016184 | 0.068997 | 0.007715 | 0.033449 | 122.3462 | 122.3547 | 122.2243 | 122.2327
3794.2031 | 122.3419 | -0.10529 | 122.2778 | 0.75367 | 0.93935 | 0.94493 | 0.93189 | 0.9427 | 1.015 | 0.92617 | 122.3258 | 122.21 | 122.2084 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.85896 | 1.0446 | 1.0502 | 1.0372 | 1.048 | 1.1203 | 1.0315 | 122.367 | 122.2512 | 122.2496 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3371 | 122.3547 | 122.2197 | 122.2373
3795.9531 | 122.3373 | -0.091553 | 122.3007 | 0.78114 | 0.97598 | 0.99987 | 0.97767 | 0.97932 | 1.0654 | 0.96737 | 122.3258 | 122.2009 | 122.1992 | 122.1034 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.87269 | 1.0675 | 1.0914 | 1.0692 | 1.0709 | 1.1569 | 1.0589 | 122.367 | 122.2421 | 122.2404 | 122.1446 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3797.7031 | 122.3511 | -0.10986 | 122.2778 | 0.79487 | 0.98056 | 0.99071 | 0.97767 | 0.99306 | 1.0608 | 0.96279 | 122.3258 | 122.1963 | 122.1992 | 122.108 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.90474 | 1.0904 | 1.1006 | 1.0875 | 1.1029 | 1.1706 | 1.0727 | 122.367 | 122.2375 | 122.2404 | 122.1492 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.3371 | 122.3547 | 122.2105 | 122.2282
3799.3906 | 122.4152 | -0.059509 | 122.2458 | 0.83608 | 1.0309 | 1.0502 | 1.028 | 1.0343 | 1.1066 | 1.0177 | 122.3258 | 122.1963 | 122.1992 | 122.108 | -0.015859 | 0.032376 | -0.033484 | -0.00775 | 0.89559 | 1.0904 | 1.1097 | 1.0875 | 1.0938 | 1.1661 | 1.0772 | 122.367 | 122.2375 | 122.2404 | 122.1492 | 0.02534 | 0.073575 | 0.007715 | 0.033449 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3801.1562 | 122.3557 | -0.11902 | 122.287 | 0.80861 | 0.98513 | 1.0045 | 0.98225 | 0.99306 | 1.0699 | 0.98111 | 122.3258 | 122.2009 | 122.1947 | 122.1217 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.92763 | 1.1042 | 1.1235 | 1.1013 | 1.1121 | 1.189 | 1.1001 | 122.367 | 122.2421 | 122.2359 | 122.1629 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3802.9219 | 122.3694 | -0.082397 | 122.287 | 0.82692 | 1.0126 | 1.0182 | 1.0097 | 1.0205 | 1.0928 | 1.004 | 122.3166 | 122.21 | 122.1992 | 122.108 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.90932 | 1.095 | 1.1006 | 1.0921 | 1.1029 | 1.1752 | 1.0864 | 122.3578 | 122.2512 | 122.2404 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3325 | 122.3501 | 122.2151 | 122.2327
3804.6875 | 122.4197 | -0.068665 | 122.2321 | 0.85897 | 1.0447 | 1.0594 | 1.0418 | 1.048 | 1.1203 | 1.0223 | 122.3304 | 122.2054 | 122.1901 | 122.108 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.92764 | 1.1133 | 1.1281 | 1.1104 | 1.1167 | 1.189 | 1.091 | 122.3716 | 122.2466 | 122.2313 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.3638 | 122.2059 | 122.2236
3806.4531 | 122.4701 | -0.045776 | 122.2275 | 0.87728 | 1.0492 | 1.0686 | 1.0464 | 1.0572 | 1.1203 | 1.036 | 122.3212 | 122.2054 | 122.1992 | 122.108 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 0.92306 | 1.095 | 1.1143 | 1.0921 | 1.1029 | 1.1661 | 1.0818 | 122.3624 | 122.2466 | 122.2404 | 122.1492 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 122.3279 | 122.3547 | 122.2059 | 122.2327
3808.2188 | 122.438 | -0.068665 | 122.2549 | 0.87728 | 1.0584 | 1.0777 | 1.0601 | 1.0572 | 1.1432 | 1.0544 | 122.3258 | 122.2009 | 122.1992 | 122.1034 | -0.015859 | 0.036954 | -0.033484 | -0.003172 | 0.94595 | 1.1271 | 1.1464 | 1.1288 | 1.1258 | 1.2119 | 1.123 | 122.367 | 122.2421 | 122.2404 | 122.1446 | 0.02534 | 0.078153 | 0.007715 | 0.038027 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3809.9219 | 122.3602 | -0.086975 | 122.3053 | 0.90018 | 1.0859 | 1.1006 | 1.0784 | 1.0846 | 1.1661 | 1.0772 | 122.3212 | 122.1963 | 122.1992 | 122.108 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.98715 | 1.1728 | 1.1876 | 1.1654 | 1.1716 | 1.2531 | 1.1642 | 122.3624 | 122.2375 | 122.2404 | 122.1492 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3547 | 122.2197 | 122.2327
3811.6875 | 122.4289 | -0.059509 | 122.2229 | 0.90475 | 1.0767 | 1.096 | 1.0738 | 1.08 | 1.1523 | 1.0589 | 122.3258 | 122.2009 | 122.1992 | 122.1034 | -0.020437 | 0.027798 | -0.038063 | 0.005985 | 0.96426 | 1.1362 | 1.1555 | 1.1333 | 1.1395 | 1.2119 | 1.1184 | 122.367 | 122.2421 | 122.2404 | 122.1446 | 0.020762 | 0.068997 | 0.003136 | 0.047184 | 122.3462 | 122.3638 | 122.2197 | 122.2373
3813.4531 | 122.4701 | -0.059509 | 122.2321 | 0.94138 | 1.1179 | 1.1281 | 1.1104 | 1.1212 | 1.189 | 1.1001 | 122.3212 | 122.2009 | 122.1992 | 122.108 | -0.020437 | 0.027798 | -0.038063 | 0.001406 | 1.0009 | 1.1774 | 1.1876 | 1.17 | 1.1807 | 1.2485 | 1.1596 | 122.3624 | 122.2421 | 122.2404 | 122.1492 | 0.020762 | 0.068997 | 0.003136 | 0.042605 | 122.3416 | 122.3593 | 122.2197 | 122.2373
3815.1562 | 122.3648 | -0.073242 | 122.2961 | 0.9597 | 1.1271 | 1.1372 | 1.1288 | 1.1304 | 1.2119 | 1.1185 | 122.3304 | 122.21 | 122.1992 | 122.1172 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 1.0329 | 1.2003 | 1.2105 | 1.202 | 1.2036 | 1.2851 | 1.1917 | 122.3716 | 122.2512 | 122.2404 | 122.1584 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2151 | 122.2327
3816.9219 | 122.4838 | -0.064087 | 122.2321 | 0.96885 | 1.1408 | 1.1601 | 1.1379 | 1.1533 | 1.221 | 1.1322 | 122.3258 | 122.2054 | 122.1992 | 122.1172 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 1.0329 | 1.2049 | 1.2242 | 1.202 | 1.2174 | 1.2851 | 1.1963 | 122.367 | 122.2466 | 122.2404 | 122.1584 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3416 | 122.3638 | 122.2151 | 122.2373
3818.6875 | 122.3648 | -0.091553 | 122.287 | 0.99632 | 1.1774 | 1.183 | 1.1654 | 1.1624 | 1.2439 | 1.1642 | 122.3212 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 1.0879 | 1.269 | 1.2746 | 1.2569 | 1.254 | 1.3355 | 1.2558 | 122.3624 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3371 | 122.3593 | 122.2151 | 122.2373
3820.3906 | 122.3511 | -0.10071 | 122.2916 | 0.99632 | 1.1546 | 1.1693 | 1.1562 | 1.167 | 1.2348 | 1.1413 | 122.3212 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.018642 | -0.038063 | -0.00775 | 1.097 | 1.2553 | 1.27 | 1.2569 | 1.2677 | 1.3355 | 1.2421 | 122.3624 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.059841 | 0.003136 | 0.033449 | 122.3371 | 122.3593 | 122.2105 | 122.2327
3822.1719 | 122.3328 | -0.082397 | 122.2733 | 1.0238 | 1.182 | 1.1922 | 1.1745 | 1.1853 | 1.2622 | 1.1642 | 122.3212 | 122.2146 | 122.1901 | 122.108 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 1.1062 | 1.2644 | 1.2746 | 1.2569 | 1.2677 | 1.3446 | 1.2466 | 122.3624 | 122.2558 | 122.2313 | 122.1492 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 122.3279 | 122.3547 | 122.1968 | 122.2236
3823.9375 | 122.3923 | -0.091553 | 122.2641 | 1.0284 | 1.1866 | 1.2013 | 1.1883 | 1.1899 | 1.2576 | 1.1734 | 122.3258 | 122.21 | 122.1992 | 122.1172 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 1.1199 | 1.2782 | 1.2929 | 1.2798 | 1.2815 | 1.3492 | 1.2649 | 122.367 | 122.2512 | 122.2404 | 122.1584 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.3371 | 122.3593 | 122.2105 | 122.2327
3825.7031 | 122.3557 | -0.10529 | 122.2687 | 1.0146 | 1.1591 | 1.1739 | 1.1517 | 1.1624 | 1.2348 | 1.1459 | 122.3212 | 122.2009 | 122.1992 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 1.1199 | 1.2644 | 1.2791 | 1.2569 | 1.2677 | 1.34 | 1.2512 | 122.3624 | 122.2421 | 122.2404 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3371 | 122.3501 | 122.2151 | 122.2282
3827.4219 | 122.4106 | -0.07782 | 122.2916 | 1.033 | 1.1774 | 1.1922 | 1.1745 | 1.1762 | 1.2531 | 1.1688 | 122.3258 | 122.2054 | 122.1947 | 122.1126 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 1.1108 | 1.2553 | 1.27 | 1.2524 | 1.254 | 1.3309 | 1.2466 | 122.367 | 122.2466 | 122.2359 | 122.1538 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 122.3371 | 122.3638 | 122.2059 | 122.2327
3829.1875 | 122.3831 | -0.086975 | 122.2778 | 1.0192 | 1.1454 | 1.1647 | 1.1425 | 1.1487 | 1.2302 | 1.1413 | 122.3212 | 122.21 | 122.1992 | 122.1172 | -0.020437 | 0.018642 | -0.028906 | -0.003172 | 1.1062 | 1.2324 | 1.2517 | 1.2295 | 1.2357 | 1.3172 | 1.2283 | 122.3624 | 122.2512 | 122.2404 | 122.1584 | 0.020762 | 0.059841 | 0.012293 | 0.038027 | 122.3416 | 122.3501 | 122.2197 | 122.2282
3830.9531 | 122.3969 | -0.082397 | 122.2733 | 1.0192 | 1.1454 | 1.1555 | 1.1379 | 1.1533 | 1.2164 | 1.1413 | 122.3304 | 122.2054 | 122.2038 | 122.1172 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 1.1016 | 1.2278 | 1.2379 | 1.2203 | 1.2357 | 1.2988 | 1.2237 | 122.3716 | 122.2466 | 122.245 | 122.1584 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2197 | 122.2373
3832.7344 | 122.4197 | -0.059509 | 122.2549 | 1.0421 | 1.1591 | 1.1647 | 1.1471 | 1.1579 | 1.2393 | 1.1505 | 122.3258 | 122.1963 | 122.2038 | 122.1126 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 1.1016 | 1.2186 | 1.2242 | 1.2066 | 1.2174 | 1.2988 | 1.21 | 122.367 | 122.2375 | 122.245 | 122.1538 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3547 | 122.2243 | 122.2327
3834.5 | 122.3511 | -0.10071 | 122.2733 | 1.0696 | 1.182 | 1.2013 | 1.1791 | 1.1853 | 1.2576 | 1.1734 | 122.3304 | 122.2054 | 122.1992 | 122.108 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 1.1703 | 1.2827 | 1.302 | 1.2798 | 1.286 | 1.3584 | 1.2741 | 122.3716 | 122.2466 | 122.2404 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2151 | 122.2327
3836.2656 | 122.3328 | -0.082397 | 122.2641 | 1.0467 | 1.1591 | 1.1739 | 1.1517 | 1.1579 | 1.2302 | 1.1505 | 122.3212 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 1.1291 | 1.2415 | 1.2563 | 1.2341 | 1.2403 | 1.3126 | 1.2329 | 122.3624 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3371 | 122.3501 | 122.2105 | 122.2236
3838.0312 | 122.5021 | -0.054932 | 122.2595 | 1.0833 | 1.1912 | 1.2059 | 1.1791 | 1.1945 | 1.2576 | 1.178 | 122.3258 | 122.2054 | 122.1992 | 122.108 | -0.020437 | 0.02322 | -0.028906 | 0.005985 | 1.1382 | 1.2461 | 1.2608 | 1.2341 | 1.2494 | 1.3126 | 1.2329 | 122.367 | 122.2466 | 122.2404 | 122.1492 | 0.020762 | 0.064419 | 0.012293 | 0.047184 | 122.3462 | 122.3547 | 122.2197 | 122.2282
3839.7344 | 122.4747 | -0.045776 | 122.2412 | 1.0925 | 1.1912 | 1.2151 | 1.1929 | 1.1945 | 1.2714 | 1.178 | 122.3304 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 1.1382 | 1.237 | 1.2608 | 1.2386 | 1.2403 | 1.3172 | 1.2237 | 122.3716 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2105 | 122.2327
3841.4844 | 122.4243 | -0.068665 | 122.2458 | 1.0925 | 1.1866 | 1.2059 | 1.1837 | 1.1899 | 1.2622 | 1.1734 | 122.3304 | 122.2054 | 122.1947 | 122.1034 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 1.1611 | 1.2553 | 1.2746 | 1.2524 | 1.2586 | 1.3309 | 1.2421 | 122.3716 | 122.2466 | 122.2359 | 122.1446 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3462 | 122.3684 | 122.2105 | 122.2327
3843.25 | 122.4335 | -0.064087 | 122.2275 | 1.0742 | 1.1637 | 1.1739 | 1.1517 | 1.1579 | 1.2256 | 1.1459 | 122.3304 | 122.2054 | 122.1901 | 122.1126 | -0.011281 | 0.014064 | -0.033484 | 0.001406 | 1.1382 | 1.2278 | 1.2379 | 1.2157 | 1.222 | 1.2897 | 1.21 | 122.3716 | 122.2466 | 122.2313 | 122.1538 | 0.029918 | 0.055263 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2014 | 122.2236
3845.0156 | 122.3923 | -0.07782 | 122.2687 | 1.0925 | 1.1729 | 1.1876 | 1.1654 | 1.1716 | 1.2439 | 1.1597 | 122.3304 | 122.21 | 122.2038 | 122.1217 | -0.025015 | 0.02322 | -0.038063 | 0.001406 | 1.1703 | 1.2507 | 1.2654 | 1.2432 | 1.2494 | 1.3217 | 1.2375 | 122.3716 | 122.2512 | 122.245 | 122.1629 | 0.016184 | 0.064419 | 0.003136 | 0.042605 | 122.3554 | 122.3684 | 122.2288 | 122.2419
3846.7188 | 122.3877 | -0.091553 | 122.2824 | 1.097 | 1.1637 | 1.1739 | 1.1608 | 1.1624 | 1.2393 | 1.1459 | 122.3258 | 122.21 | 122.2038 | 122.1217 | -0.015859 | 0.032376 | -0.033484 | 0.005985 | 1.1886 | 1.2553 | 1.2654 | 1.2524 | 1.254 | 1.3309 | 1.2375 | 122.367 | 122.2512 | 122.245 | 122.1629 | 0.02534 | 0.073575 | 0.007715 | 0.047184 | 122.3416 | 122.3593 | 122.2197 | 122.2373
3848.4844 | 122.4472 | -0.059509 | 122.2778 | 1.1291 | 1.1958 | 1.2059 | 1.1929 | 1.1991 | 1.2714 | 1.1825 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 1.1886 | 1.2553 | 1.2654 | 1.2524 | 1.2586 | 1.3309 | 1.2421 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2151 | 122.2282
3850.1719 | 122.3602 | -0.10071 | 122.2916 | 1.1154 | 1.1729 | 1.1968 | 1.1791 | 1.1808 | 1.2485 | 1.1642 | 122.3349 | 122.2054 | 122.1992 | 122.108 | -0.011281 | 0.02322 | -0.024328 | 0.001406 | 1.2161 | 1.2736 | 1.2975 | 1.2798 | 1.2815 | 1.3492 | 1.2649 | 122.3761 | 122.2466 | 122.2404 | 122.1492 | 0.029918 | 0.064419 | 0.016871 | 0.042605 | 122.3462 | 122.3593 | 122.2105 | 122.2236
3851.9375 | 122.3923 | -0.091553 | 122.2916 | 1.1428 | 1.1958 | 1.2105 | 1.1929 | 1.2036 | 1.2714 | 1.1871 | 122.3258 | 122.2054 | 122.2038 | 122.108 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 1.2344 | 1.2873 | 1.302 | 1.2844 | 1.2952 | 1.3629 | 1.2787 | 122.367 | 122.2466 | 122.245 | 122.1492 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3462 | 122.3593 | 122.2243 | 122.2373
3853.7031 | 122.438 | -0.068665 | 122.2824 | 1.1428 | 1.2049 | 1.2105 | 1.202 | 1.1991 | 1.2714 | 1.1917 | 122.3304 | 122.2009 | 122.1947 | 122.1126 | -0.015859 | 0.027798 | -0.028906 | -0.00775 | 1.2115 | 1.2736 | 1.2792 | 1.2707 | 1.2677 | 1.34 | 1.2604 | 122.3716 | 122.2421 | 122.2359 | 122.1538 | 0.02534 | 0.068997 | 0.012293 | 0.033449 | 122.3462 | 122.3593 | 122.2105 | 122.2236
3855.4531 | 122.3923 | -0.09613 | 122.2687 | 1.1657 | 1.2095 | 1.2288 | 1.202 | 1.2128 | 1.2897 | 1.2009 | 122.3304 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 1.2619 | 1.3056 | 1.3249 | 1.2982 | 1.3089 | 1.3858 | 1.297 | 122.3716 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3857.1719 | 122.3831 | -0.086975 | 122.2824 | 1.1795 | 1.2187 | 1.2334 | 1.2158 | 1.2174 | 1.2943 | 1.21 | 122.3258 | 122.2054 | 122.1947 | 122.1217 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 1.2664 | 1.3056 | 1.3204 | 1.3027 | 1.3044 | 1.3813 | 1.297 | 122.367 | 122.2466 | 122.2359 | 122.1629 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3371 | 122.3593 | 122.2059 | 122.2282
3858.9375 | 122.4289 | -0.064087 | 122.2366 | 1.1749 | 1.2095 | 1.2288 | 1.2066 | 1.2128 | 1.2897 | 1.1871 | 122.3349 | 122.2146 | 122.1947 | 122.1172 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 1.239 | 1.2736 | 1.2929 | 1.2707 | 1.2769 | 1.3538 | 1.2512 | 122.3761 | 122.2558 | 122.2359 | 122.1584 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 122.3416 | 122.3684 | 122.2014 | 122.2282
3860.6875 | 122.4518 | -0.054932 | 122.2549 | 1.152 | 1.1866 | 1.1968 | 1.1745 | 1.1808 | 1.2531 | 1.1688 | 122.3304 | 122.2009 | 122.1992 | 122.1034 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 1.2069 | 1.2415 | 1.2517 | 1.2295 | 1.2357 | 1.308 | 1.2237 | 122.3716 | 122.2421 | 122.2404 | 122.1446 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3462 | 122.3593 | 122.2151 | 122.2282
3862.3906 | 122.3511 | -0.11444 | 122.2778 | 1.1611 | 1.1866 | 1.2013 | 1.1745 | 1.1808 | 1.2622 | 1.178 | 122.3304 | 122.21 | 122.1947 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 1.2756 | 1.301 | 1.3158 | 1.289 | 1.2952 | 1.3767 | 1.2924 | 122.3716 | 122.2512 | 122.2359 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2059 | 122.2282
3864.1562 | 122.319 | -0.11902 | 122.2641 | 1.152 | 1.1774 | 1.1784 | 1.1562 | 1.1624 | 1.2439 | 1.1642 | 122.3212 | 122.2009 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.042641 | -0.003172 | 1.271 | 1.2965 | 1.2975 | 1.2753 | 1.2815 | 1.3629 | 1.2833 | 122.3624 | 122.2421 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | -0.001442 | 0.038027 | 122.3325 | 122.3638 | 122.2105 | 122.2419
3865.8594 | 122.4197 | -0.068665 | 122.2549 | 1.1474 | 1.1546 | 1.1647 | 1.1425 | 1.1533 | 1.2302 | 1.1459 | 122.3212 | 122.2054 | 122.1947 | 122.1126 | -0.020437 | 0.018642 | -0.028906 | 0.001406 | 1.2161 | 1.2232 | 1.2334 | 1.2112 | 1.222 | 1.2988 | 1.2146 | 122.3624 | 122.2466 | 122.2359 | 122.1538 | 0.020762 | 0.059841 | 0.012293 | 0.042605 | 122.3416 | 122.3501 | 122.2151 | 122.2236
3867.6406 | 122.4518 | -0.064087 | 122.2412 | 1.1474 | 1.15 | 1.1601 | 1.1333 | 1.1441 | 1.221 | 1.1368 | 122.3349 | 122.2054 | 122.2038 | 122.1126 | -0.020437 | 0.02322 | -0.028906 | -0.003172 | 1.2115 | 1.2141 | 1.2242 | 1.1974 | 1.2082 | 1.2851 | 1.2009 | 122.3761 | 122.2466 | 122.245 | 122.1538 | 0.020762 | 0.064419 | 0.012293 | 0.038027 | 122.3554 | 122.3638 | 122.2243 | 122.2327
3869.4219 | 122.3465 | -0.10529 | 122.2687 | 1.1337 | 1.1271 | 1.1281 | 1.1059 | 1.1121 | 1.189 | 1.1047 | 122.3258 | 122.2009 | 122.2038 | 122.1126 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 1.239 | 1.2324 | 1.2334 | 1.2112 | 1.2174 | 1.2943 | 1.21 | 122.367 | 122.2421 | 122.245 | 122.1538 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3416 | 122.3547 | 122.2197 | 122.2327
3871.1875 | 122.4289 | -0.082397 | 122.2687 | 1.1245 | 1.1133 | 1.1143 | 1.0921 | 1.1029 | 1.1752 | 1.1047 | 122.3304 | 122.2054 | 122.1947 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 1.2069 | 1.1957 | 1.1967 | 1.1745 | 1.1853 | 1.2576 | 1.1871 | 122.3716 | 122.2466 | 122.2359 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2059 | 122.2282
3872.8906 | 122.3419 | -0.09613 | 122.2778 | 1.0879 | 1.063 | 1.0594 | 1.0372 | 1.048 | 1.1295 | 1.0498 | 122.3304 | 122.21 | 122.2084 | 122.1172 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 1.184 | 1.1591 | 1.1555 | 1.1333 | 1.1441 | 1.2256 | 1.1459 | 122.3716 | 122.2512 | 122.2496 | 122.1584 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2197 | 122.2373
3874.6406 | 122.3511 | -0.086975 | 122.2824 | 1.1016 | 1.0721 | 1.0823 | 1.0601 | 1.0663 | 1.1386 | 1.0681 | 122.3258 | 122.2054 | 122.2038 | 122.1172 | -0.006702 | 0.02322 | -0.038063 | -0.00775 | 1.1886 | 1.1591 | 1.1693 | 1.1471 | 1.1533 | 1.2256 | 1.1551 | 122.367 | 122.2466 | 122.245 | 122.1584 | 0.034497 | 0.064419 | 0.003136 | 0.033449 | 122.3325 | 122.3638 | 122.2105 | 122.2419
3876.3281 | 122.4152 | -0.059509 | 122.2321 | 1.1062 | 1.0676 | 1.0777 | 1.0509 | 1.0617 | 1.134 | 1.0498 | 122.3304 | 122.1963 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 1.1657 | 1.1271 | 1.1372 | 1.1104 | 1.1212 | 1.1935 | 1.1093 | 122.3716 | 122.2375 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2059 | 122.2282
3878.0938 | 122.4564 | -0.07782 | 122.2458 | 1.097 | 1.0584 | 1.0686 | 1.0509 | 1.0572 | 1.1249 | 1.0589 | 122.3212 | 122.21 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 1.1749 | 1.1362 | 1.1464 | 1.1287 | 1.135 | 1.2027 | 1.1368 | 122.3624 | 122.2512 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 122.3325 | 122.3593 | 122.2059 | 122.2327
3879.8438 | 122.4701 | -0.045776 | 122.2366 | 1.0558 | 1.0126 | 1.009 | 1.0006 | 0.99764 | 1.0791 | 0.99484 | 122.3212 | 122.2009 | 122.1992 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 1.1016 | 1.0584 | 1.0548 | 1.0463 | 1.0434 | 1.1249 | 1.0406 | 122.3624 | 122.2421 | 122.2404 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3501 | 122.2105 | 122.2282
3881.5938 | 122.4655 | -0.059509 | 122.2366 | 1.065 | 1.0172 | 1.0273 | 1.0006 | 1.0068 | 1.0791 | 1.004 | 122.3212 | 122.2054 | 122.1992 | 122.108 | -0.015859 | 0.02322 | -0.033484 | -0.012328 | 1.1245 | 1.0767 | 1.0869 | 1.0601 | 1.0663 | 1.1386 | 1.0635 | 122.3624 | 122.2466 | 122.2404 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.028871 | 122.3371 | 122.3547 | 122.2151 | 122.2327
3883.2969 | 122.4197 | -0.041199 | 122.2229 | 1.0238 | 0.9714 | 0.97698 | 0.94562 | 0.95643 | 1.0333 | 0.96279 | 122.3304 | 122.2009 | 122.2038 | 122.108 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 1.065 | 1.0126 | 1.0182 | 0.98682 | 0.99763 | 1.0745 | 1.004 | 122.3716 | 122.2421 | 122.245 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2197 | 122.2373
3885.0469 | 122.3648 | -0.091553 | 122.2733 | 1.065 | 1.008 | 1.0182 | 0.98683 | 1.0022 | 1.0791 | 0.99484 | 122.3258 | 122.21 | 122.2084 | 122.1126 | -0.020437 | 0.027798 | -0.038063 | 0.005985 | 1.1566 | 1.0996 | 1.1097 | 1.0784 | 1.0938 | 1.1706 | 1.0864 | 122.367 | 122.2512 | 122.2496 | 122.1538 | 0.020762 | 0.068997 | 0.003136 | 0.047184 | 122.3462 | 122.3638 | 122.2288 | 122.2465
3886.8125 | 122.3282 | -0.10071 | 122.2778 | 1.0238 | 0.96224 | 0.9724 | 0.94562 | 0.96559 | 1.0333 | 0.95822 | 122.3258 | 122.2009 | 122.2084 | 122.1126 | -0.006702 | 0.02322 | -0.028906 | -0.003172 | 1.1245 | 1.0629 | 1.0731 | 1.0463 | 1.0663 | 1.134 | 1.0589 | 122.367 | 122.2421 | 122.2496 | 122.1538 | 0.034497 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3547 | 122.2151 | 122.2373
3888.5781 | 122.3465 | -0.11444 | 122.2504 | 1.0375 | 0.98513 | 0.98614 | 0.95936 | 0.97475 | 1.047 | 0.97195 | 122.3258 | 122.2054 | 122.2038 | 122.108 | -0.015859 | 0.014064 | -0.033484 | 0.001406 | 1.152 | 1.0996 | 1.1006 | 1.0738 | 1.0892 | 1.1615 | 1.0864 | 122.367 | 122.2466 | 122.245 | 122.1492 | 0.02534 | 0.055263 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2197 | 122.2373
3890.3438 | 122.4747 | -0.032043 | 122.2137 | 1.0284 | 0.95766 | 0.96782 | 0.93647 | 0.94728 | 1.0287 | 0.94906 | 122.3304 | 122.2054 | 122.2038 | 122.108 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 1.0604 | 0.9897 | 0.99986 | 0.96851 | 0.97932 | 1.0608 | 0.9811 | 122.3716 | 122.2466 | 122.245 | 122.1492 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.3508 | 122.3593 | 122.2243 | 122.2327
3892.0469 | 122.4518 | -0.068665 | 122.2229 | 1.0467 | 0.98056 | 0.98156 | 0.9502 | 0.95643 | 1.0379 | 0.96279 | 122.3349 | 122.21 | 122.1947 | 122.1172 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 1.1154 | 1.0492 | 1.0502 | 1.0189 | 1.0251 | 1.1066 | 1.0315 | 122.3761 | 122.2512 | 122.2359 | 122.1584 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3462 | 122.3684 | 122.2059 | 122.2282
3893.75 | 122.438 | -0.068665 | 122.2366 | 1.0513 | 0.98971 | 0.99529 | 0.96852 | 0.97932 | 1.047 | 0.96737 | 122.3304 | 122.2054 | 122.1947 | 122.108 | -0.011281 | 0.018642 | -0.033484 | 0.010563 | 1.1199 | 1.0584 | 1.064 | 1.0372 | 1.048 | 1.1157 | 1.036 | 122.3716 | 122.2466 | 122.2359 | 122.1492 | 0.029918 | 0.059841 | 0.007715 | 0.051762 | 122.3416 | 122.3638 | 122.2059 | 122.2282
3895.5 | 122.3511 | -0.086975 | 122.2549 | 1.033 | 0.96682 | 0.9724 | 0.9502 | 0.95643 | 1.0242 | 0.95364 | 122.3304 | 122.2054 | 122.1992 | 122.1172 | -0.020437 | 0.032376 | -0.042641 | -0.003172 | 1.1199 | 1.0538 | 1.0594 | 1.0372 | 1.0434 | 1.1111 | 1.0406 | 122.3716 | 122.2466 | 122.2404 | 122.1584 | 0.020762 | 0.073575 | -0.001442 | 0.038027 | 122.3508 | 122.373 | 122.2197 | 122.2419
3897.25 | 122.3694 | -0.086975 | 122.2504 | 1.0375 | 0.96682 | 0.96782 | 0.9502 | 0.94728 | 1.0333 | 0.95364 | 122.3304 | 122.21 | 122.2038 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 1.1245 | 1.0538 | 1.0548 | 1.0372 | 1.0343 | 1.1203 | 1.0406 | 122.3716 | 122.2512 | 122.245 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3899.0156 | 122.3969 | -0.082397 | 122.2641 | 1.0558 | 0.98056 | 0.98614 | 0.96852 | 0.97017 | 1.047 | 0.97195 | 122.3304 | 122.21 | 122.2038 | 122.1217 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 1.1382 | 1.063 | 1.0685 | 1.0509 | 1.0526 | 1.1294 | 1.0543 | 122.3716 | 122.2512 | 122.245 | 122.1629 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3508 | 122.3593 | 122.2243 | 122.2327
3900.7656 | 122.3831 | -0.086975 | 122.2549 | 1.065 | 0.98513 | 0.99987 | 0.96852 | 0.97017 | 1.0516 | 0.97195 | 122.3212 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 1.152 | 1.0721 | 1.0868 | 1.0555 | 1.0571 | 1.1386 | 1.0589 | 122.3624 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3325 | 122.3501 | 122.2105 | 122.2282
3902.5312 | 122.4197 | -0.050354 | 122.2733 | 1.0513 | 0.97598 | 0.98156 | 0.94562 | 0.95643 | 1.0333 | 0.95364 | 122.3304 | 122.2146 | 122.1992 | 122.1126 | -0.015859 | 0.014064 | -0.028906 | -0.00775 | 1.1016 | 1.0263 | 1.0319 | 0.99598 | 1.0068 | 1.0837 | 1.004 | 122.3716 | 122.2558 | 122.2404 | 122.1538 | 0.02534 | 0.055263 | 0.012293 | 0.033449 | 122.3462 | 122.3593 | 122.2151 | 122.2282
3904.2344 | 122.4655 | -0.041199 | 122.2549 | 1.0192 | 0.94393 | 0.94951 | 0.91815 | 0.92439 | 1.0058 | 0.92617 | 122.3349 | 122.21 | 122.1947 | 122.1126 | -0.015859 | 0.018642 | -0.033484 | -0.003172 | 1.0604 | 0.98512 | 0.99071 | 0.95935 | 0.96559 | 1.047 | 0.96737 | 122.3761 | 122.2512 | 122.2359 | 122.1538 | 0.02534 | 0.059841 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2105 | 122.2282
3906 | 122.438 | -0.064087 | 122.2504 | 1.0146 | 0.93935 | 0.94493 | 0.91815 | 0.91523 | 0.99668 | 0.91243 | 122.3304 | 122.2054 | 122.2038 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 1.0787 | 1.0034 | 1.009 | 0.98224 | 0.97932 | 1.0608 | 0.97652 | 122.3716 | 122.2466 | 122.245 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3462 | 122.3638 | 122.2197 | 122.2373
3907.7656 | 122.3511 | -0.10986 | 122.3007 | 1.0055 | 0.93019 | 0.92661 | 0.89526 | 0.89692 | 0.97837 | 0.90785 | 122.3258 | 122.2054 | 122.2038 | 122.1172 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 1.1153 | 1.0401 | 1.0365 | 1.0051 | 1.0068 | 1.0882 | 1.0177 | 122.367 | 122.2466 | 122.245 | 122.1584 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.3371 | 122.3593 | 122.2151 | 122.2373
3909.4688 | 122.4289 | -0.050354 | 122.2641 | 1.0101 | 0.93019 | 0.93577 | 0.90442 | 0.91065 | 0.98295 | 0.91701 | 122.3258 | 122.2054 | 122.1947 | 122.1126 | -0.015859 | 0.018642 | -0.038063 | -0.003172 | 1.0604 | 0.98054 | 0.98613 | 0.95477 | 0.96101 | 1.0333 | 0.96737 | 122.367 | 122.2466 | 122.2359 | 122.1538 | 0.02534 | 0.059841 | 0.003136 | 0.038027 | 122.3416 | 122.3638 | 122.2105 | 122.2327
3911.2188 | 122.4197 | -0.068665 | 122.2504 | 1.0055 | 0.93019 | 0.92661 | 0.89984 | 0.9015 | 0.97837 | 0.90328 | 122.3258 | 122.21 | 122.1992 | 122.1126 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 1.0741 | 0.99885 | 0.99528 | 0.9685 | 0.97016 | 1.047 | 0.97194 | 122.367 | 122.2512 | 122.2404 | 122.1538 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.3325 | 122.3593 | 122.2059 | 122.2327
3912.9219 | 122.4701 | -0.041199 | 122.2412 | 0.96885 | 0.8844 | 0.89914 | 0.86321 | 0.86945 | 0.94632 | 0.87123 | 122.3212 | 122.2054 | 122.2038 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 1.0101 | 0.9256 | 0.94034 | 0.90441 | 0.91065 | 0.98752 | 0.91243 | 122.3624 | 122.2466 | 122.245 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3371 | 122.3547 | 122.2197 | 122.2373
3914.6875 | 122.3511 | -0.10529 | 122.2961 | 0.98259 | 0.90272 | 0.9083 | 0.87695 | 0.88319 | 0.95548 | 0.89412 | 122.3304 | 122.2009 | 122.1992 | 122.1172 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 1.0879 | 1.008 | 1.0136 | 0.98223 | 0.98847 | 1.0608 | 0.99941 | 122.3716 | 122.2421 | 122.2404 | 122.1584 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.3462 | 122.3638 | 122.2151 | 122.2327
3916.3906 | 122.4426 | -0.073242 | 122.2458 | 0.97801 | 0.8844 | 0.89456 | 0.85863 | 0.87403 | 0.9509 | 0.87123 | 122.3258 | 122.2009 | 122.1947 | 122.1034 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 1.0513 | 0.95764 | 0.96781 | 0.93188 | 0.94727 | 1.0241 | 0.94447 | 122.367 | 122.2421 | 122.2359 | 122.1446 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.3371 | 122.3638 | 122.2059 | 122.2327
3918.1562 | 122.3694 | -0.09613 | 122.2595 | 1.0101 | 0.93019 | 0.93119 | 0.89526 | 0.91065 | 0.98295 | 0.90785 | 122.3304 | 122.2009 | 122.1992 | 122.108 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 1.1062 | 1.0263 | 1.0273 | 0.99139 | 1.0068 | 1.0791 | 1.004 | 122.3716 | 122.2421 | 122.2404 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.3638 | 122.2151 | 122.2327
3919.9062 | 122.4197 | -0.073242 | 122.2458 | 0.98259 | 0.89814 | 0.9083 | 0.87695 | 0.87403 | 0.9509 | 0.87581 | 122.3258 | 122.2054 | 122.1992 | 122.1217 | -0.015859 | 0.027798 | -0.033484 | -0.00775 | 1.0558 | 0.97138 | 0.98154 | 0.95019 | 0.94727 | 1.0241 | 0.94905 | 122.367 | 122.2466 | 122.2404 | 122.1629 | 0.02534 | 0.068997 | 0.007715 | 0.033449 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3921.6719 | 122.4472 | -0.054932 | 122.2366 | 0.98259 | 0.89356 | 0.89914 | 0.86779 | 0.87403 | 0.95548 | 0.88039 | 122.3258 | 122.21 | 122.1992 | 122.1172 | -0.006702 | 0.02322 | -0.028906 | 0.001406 | 1.0375 | 0.94849 | 0.95407 | 0.92272 | 0.92896 | 1.0104 | 0.93532 | 122.367 | 122.2512 | 122.2404 | 122.1584 | 0.034497 | 0.064419 | 0.012293 | 0.042605 | 122.3325 | 122.3547 | 122.2059 | 122.2282
3923.375 | 122.3785 | -0.10071 | 122.2687 | 0.97801 | 0.89356 | 0.89456 | 0.86321 | 0.86945 | 0.9509 | 0.88497 | 122.3304 | 122.2009 | 122.2084 | 122.1126 | -0.011281 | 0.027798 | -0.038063 | -0.012328 | 1.0787 | 0.99427 | 0.99527 | 0.96392 | 0.97016 | 1.0516 | 0.98567 | 122.3716 | 122.2421 | 122.2496 | 122.1538 | 0.029918 | 0.068997 | 0.003136 | 0.028871 | 122.3416 | 122.3684 | 122.2197 | 122.2465
3925.1406 | 122.3465 | -0.09613 | 122.2778 | 0.93223 | 0.84777 | 0.8442 | 0.81743 | 0.82367 | 0.90969 | 0.83461 | 122.3258 | 122.21 | 122.2084 | 122.1126 | -0.025015 | 0.02322 | -0.038063 | 0.001406 | 1.0284 | 0.9439 | 0.94033 | 0.91356 | 0.9198 | 1.0058 | 0.93074 | 122.367 | 122.2512 | 122.2496 | 122.1538 | 0.016184 | 0.064419 | 0.003136 | 0.042605 | 122.3508 | 122.3638 | 122.2334 | 122.2465
3926.875 | 122.4792 | -0.050354 | 122.2412 | 0.93223 | 0.84319 | 0.84878 | 0.81743 | 0.82367 | 0.90969 | 0.83003 | 122.3304 | 122.21 | 122.2038 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.98258 | 0.89355 | 0.89913 | 0.86778 | 0.87403 | 0.96005 | 0.88038 | 122.3716 | 122.2512 | 122.245 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3928.625 | 122.4747 | -0.041199 | 122.2549 | 0.92307 | 0.83403 | 0.8442 | 0.80369 | 0.80994 | 0.89596 | 0.82087 | 122.3304 | 122.2054 | 122.2038 | 122.1217 | -0.020437 | 0.02322 | -0.028906 | -0.003172 | 0.96427 | 0.87523 | 0.8854 | 0.84489 | 0.85114 | 0.93716 | 0.86207 | 122.3716 | 122.2466 | 122.245 | 122.1629 | 0.020762 | 0.064419 | 0.012293 | 0.038027 | 122.3508 | 122.3593 | 122.2243 | 122.2327
3930.3906 | 122.4655 | -0.041199 | 122.2549 | 0.91849 | 0.83861 | 0.83962 | 0.80827 | 0.81452 | 0.90511 | 0.81171 | 122.3212 | 122.2054 | 122.2038 | 122.1126 | -0.020437 | 0.018642 | -0.033484 | -0.003172 | 0.95969 | 0.87981 | 0.88082 | 0.84947 | 0.85572 | 0.94631 | 0.85291 | 122.3624 | 122.2466 | 122.245 | 122.1538 | 0.020762 | 0.059841 | 0.007715 | 0.038027 | 122.3416 | 122.3547 | 122.2243 | 122.2373
3932.1562 | 122.4152 | -0.059509 | 122.2549 | 0.90475 | 0.8203 | 0.83046 | 0.79911 | 0.80078 | 0.8868 | 0.80714 | 122.3258 | 122.21 | 122.1947 | 122.1126 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 0.96426 | 0.87981 | 0.88997 | 0.85862 | 0.86029 | 0.94631 | 0.86664 | 122.367 | 122.2512 | 122.2359 | 122.1538 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2105 | 122.2282
3933.8594 | 122.5067 | -0.041199 | 122.2641 | 0.90475 | 0.82946 | 0.82131 | 0.79911 | 0.80536 | 0.89138 | 0.81171 | 122.3258 | 122.2009 | 122.2038 | 122.108 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.94595 | 0.87065 | 0.8625 | 0.84031 | 0.84656 | 0.93258 | 0.85291 | 122.367 | 122.2421 | 122.245 | 122.1492 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.3371 | 122.3547 | 122.2151 | 122.2327
3935.6094 | 122.3557 | -0.10529 | 122.2824 | 0.91391 | 0.82488 | 0.83504 | 0.79911 | 0.80994 | 0.88222 | 0.81629 | 122.3304 | 122.2054 | 122.2084 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 1.0192 | 0.93016 | 0.94033 | 0.9044 | 0.91523 | 0.98751 | 0.92158 | 122.3716 | 122.2466 | 122.2496 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2197 | 122.2373
3937.375 | 122.4701 | -0.036621 | 122.2321 | 0.90933 | 0.82488 | 0.83504 | 0.79453 | 0.80078 | 0.89138 | 0.81629 | 122.3304 | 122.2054 | 122.2038 | 122.1126 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.94595 | 0.8615 | 0.87166 | 0.83115 | 0.83741 | 0.928 | 0.85291 | 122.3716 | 122.2466 | 122.245 | 122.1538 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3462 | 122.3684 | 122.2197 | 122.2419
3939.1562 | 122.4792 | -0.050354 | 122.2366 | 0.90018 | 0.81114 | 0.82131 | 0.78995 | 0.79163 | 0.88222 | 0.79798 | 122.3304 | 122.2054 | 122.2038 | 122.1126 | -0.020437 | 0.027798 | -0.038063 | -0.003172 | 0.95053 | 0.86149 | 0.87166 | 0.84031 | 0.84198 | 0.93258 | 0.84833 | 122.3716 | 122.2466 | 122.245 | 122.1538 | 0.020762 | 0.068997 | 0.003136 | 0.038027 | 122.3508 | 122.3684 | 122.2243 | 122.2419
3940.8594 | 122.3969 | -0.082397 | 122.2824 | 0.90475 | 0.83403 | 0.83046 | 0.79911 | 0.80994 | 0.89596 | 0.82087 | 122.3258 | 122.21 | 122.1992 | 122.1172 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.98715 | 0.91643 | 0.91286 | 0.88151 | 0.89234 | 0.97836 | 0.90327 | 122.367 | 122.2512 | 122.2404 | 122.1584 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3942.625 | 122.4701 | -0.045776 | 122.2412 | 0.89102 | 0.81572 | 0.81673 | 0.78538 | 0.78705 | 0.87307 | 0.80256 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.9368 | 0.86149 | 0.8625 | 0.83115 | 0.83283 | 0.91884 | 0.84833 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2151 | 122.2327
3944.3438 | 122.438 | -0.068665 | 122.2504 | 0.90018 | 0.8203 | 0.81673 | 0.7808 | 0.79163 | 0.8868 | 0.80256 | 122.3395 | 122.2009 | 122.1992 | 122.1126 | -0.015859 | 0.02322 | -0.033484 | 0.005985 | 0.96884 | 0.88896 | 0.88539 | 0.84946 | 0.86029 | 0.95547 | 0.87122 | 122.3807 | 122.2421 | 122.2404 | 122.1538 | 0.02534 | 0.064419 | 0.007715 | 0.047184 | 122.3554 | 122.373 | 122.2151 | 122.2327
3946.1094 | 122.4426 | -0.054932 | 122.2137 | 0.86355 | 0.78824 | 0.78926 | 0.74875 | 0.75958 | 0.84559 | 0.77051 | 122.3304 | 122.2054 | 122.1947 | 122.1172 | -0.006702 | 0.02322 | -0.033484 | 0.005985 | 0.91848 | 0.84318 | 0.84419 | 0.80368 | 0.81451 | 0.90053 | 0.82544 | 122.3716 | 122.2466 | 122.2359 | 122.1584 | 0.034497 | 0.064419 | 0.007715 | 0.047184 | 122.3371 | 122.3638 | 122.2014 | 122.2282
3947.8594 | 122.4609 | -0.036621 | 122.2092 | 0.87271 | 0.78824 | 0.79383 | 0.76248 | 0.76874 | 0.84559 | 0.78424 | 122.3304 | 122.2054 | 122.2038 | 122.1172 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.90933 | 0.82487 | 0.83046 | 0.79911 | 0.80536 | 0.88222 | 0.82087 | 122.3716 | 122.2466 | 122.245 | 122.1584 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3462 | 122.3593 | 122.2197 | 122.2327
3949.6406 | 122.4701 | -0.045776 | 122.2321 | 0.87271 | 0.78824 | 0.80299 | 0.76248 | 0.75958 | 0.85017 | 0.77967 | 122.3349 | 122.2054 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.91848 | 0.83402 | 0.84877 | 0.80826 | 0.80536 | 0.89595 | 0.82544 | 122.3761 | 122.2466 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3638 | 122.2105 | 122.2282
3951.3438 | 122.3557 | -0.09613 | 122.2824 | 0.88186 | 0.80656 | 0.80299 | 0.77164 | 0.76874 | 0.86391 | 0.78882 | 122.3304 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 0.97799 | 0.90269 | 0.89912 | 0.86777 | 0.86487 | 0.96004 | 0.88495 | 122.3716 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2151 | 122.2373
3953.1094 | 122.438 | -0.032043 | 122.2366 | 0.88186 | 0.81114 | 0.80757 | 0.76706 | 0.77332 | 0.86391 | 0.79798 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.020437 | 0.018642 | -0.033484 | 0.001406 | 0.91391 | 0.84318 | 0.83961 | 0.79911 | 0.80536 | 0.89595 | 0.83002 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.020762 | 0.059841 | 0.007715 | 0.042605 | 122.3508 | 122.3638 | 122.2197 | 122.2327
3954.8125 | 122.3831 | -0.091553 | 122.2458 | 0.84066 | 0.76993 | 0.76178 | 0.73043 | 0.73211 | 0.81812 | 0.74762 | 122.3304 | 122.21 | 122.1992 | 122.1172 | -0.015859 | 0.02322 | -0.038063 | 0.005985 | 0.93221 | 0.86148 | 0.85334 | 0.82199 | 0.82367 | 0.90968 | 0.83917 | 122.3716 | 122.2512 | 122.2404 | 122.1584 | 0.02534 | 0.064419 | 0.003136 | 0.047184 | 122.3462 | 122.3684 | 122.2151 | 122.2373
3956.5156 | 122.3373 | -0.11444 | 122.2733 | 0.82234 | 0.74246 | 0.74347 | 0.70754 | 0.70922 | 0.79523 | 0.72015 | 122.3349 | 122.21 | 122.2084 | 122.1126 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 0.93678 | 0.8569 | 0.85791 | 0.82198 | 0.82367 | 0.90967 | 0.83459 | 122.3761 | 122.2512 | 122.2496 | 122.1538 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 122.3416 | 122.3638 | 122.2151 | 122.2373
3958.2812 | 122.4243 | -0.068665 | 122.2733 | 0.82234 | 0.75619 | 0.74805 | 0.70754 | 0.72296 | 0.80439 | 0.72931 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 0.89101 | 0.82486 | 0.81671 | 0.77621 | 0.79162 | 0.87306 | 0.79797 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 122.3371 | 122.3638 | 122.2059 | 122.2327
3959.9844 | 122.3511 | -0.082397 | 122.2824 | 0.80403 | 0.7333 | 0.72973 | 0.69839 | 0.70007 | 0.79065 | 0.72015 | 122.3258 | 122.2054 | 122.1947 | 122.1126 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.88643 | 0.8157 | 0.81213 | 0.78078 | 0.78247 | 0.87305 | 0.80255 | 122.367 | 122.2466 | 122.2359 | 122.1538 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.3325 | 122.3547 | 122.2014 | 122.2236
3961.75 | 122.406 | -0.068665 | 122.287 | 0.79945 | 0.72414 | 0.72973 | 0.68007 | 0.69549 | 0.77692 | 0.70642 | 122.3304 | 122.2009 | 122.1947 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.86812 | 0.79281 | 0.7984 | 0.74874 | 0.76416 | 0.84558 | 0.77508 | 122.3716 | 122.2421 | 122.2359 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2059 | 122.2282
3963.5156 | 122.3282 | -0.09613 | 122.2824 | 0.78572 | 0.70583 | 0.70684 | 0.67549 | 0.67718 | 0.75861 | 0.69726 | 122.3349 | 122.2054 | 122.1992 | 122.1172 | -0.015859 | 0.027798 | -0.024328 | 0.001406 | 0.88185 | 0.80196 | 0.80297 | 0.77162 | 0.77331 | 0.85474 | 0.79339 | 122.3761 | 122.2466 | 122.2404 | 122.1584 | 0.02534 | 0.068997 | 0.016871 | 0.042605 | 122.3508 | 122.3593 | 122.2151 | 122.2236
3965.2812 | 122.3557 | -0.082397 | 122.2595 | 0.79487 | 0.71956 | 0.72058 | 0.68007 | 0.68634 | 0.77234 | 0.70184 | 122.3258 | 122.2054 | 122.1901 | 122.108 | -0.015859 | 0.027798 | -0.028906 | -0.00775 | 0.87727 | 0.80196 | 0.80297 | 0.76247 | 0.76873 | 0.85474 | 0.78424 | 122.367 | 122.2466 | 122.2313 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.033449 | 122.3416 | 122.3547 | 122.2059 | 122.219
3966.9844 | 122.3511 | -0.10071 | 122.2733 | 0.7674 | 0.69209 | 0.6931 | 0.6526 | 0.66344 | 0.74487 | 0.68353 | 122.3304 | 122.21 | 122.1992 | 122.1172 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.86811 | 0.7928 | 0.79381 | 0.75331 | 0.76415 | 0.84558 | 0.78423 | 122.3716 | 122.2512 | 122.2404 | 122.1584 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2105 | 122.2327
3968.75 | 122.3511 | -0.09613 | 122.2733 | 0.75367 | 0.68751 | 0.68395 | 0.64802 | 0.65429 | 0.74029 | 0.66979 | 122.3304 | 122.21 | 122.1992 | 122.1126 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.8498 | 0.78364 | 0.78008 | 0.74415 | 0.75042 | 0.83642 | 0.76592 | 122.3716 | 122.2512 | 122.2404 | 122.1538 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3508 | 122.3638 | 122.2197 | 122.2327
3970.5156 | 122.3785 | -0.07782 | 122.2687 | 0.75825 | 0.67378 | 0.67479 | 0.63429 | 0.64055 | 0.73571 | 0.66063 | 122.3258 | 122.2054 | 122.2084 | 122.108 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.83607 | 0.7516 | 0.75261 | 0.71211 | 0.71837 | 0.81353 | 0.73845 | 122.367 | 122.2466 | 122.2496 | 122.1492 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.3416 | 122.3638 | 122.2243 | 122.2465
3972.2812 | 122.3877 | -0.09613 | 122.319 | 0.74451 | 0.66462 | 0.65648 | 0.62513 | 0.64055 | 0.72656 | 0.6469 | 122.3304 | 122.2146 | 122.2038 | 122.1034 | -0.015859 | 0.027798 | -0.024328 | 0.001406 | 0.84064 | 0.76075 | 0.75261 | 0.72126 | 0.73669 | 0.82269 | 0.74303 | 122.3716 | 122.2558 | 122.245 | 122.1446 | 0.02534 | 0.068997 | 0.016871 | 0.042605 | 122.3462 | 122.3547 | 122.2197 | 122.2282
3973.9844 | 122.3969 | -0.09613 | 122.2961 | 0.71246 | 0.63257 | 0.62901 | 0.59308 | 0.59935 | 0.69451 | 0.62401 | 122.3304 | 122.2192 | 122.1992 | 122.1172 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.80859 | 0.7287 | 0.72514 | 0.68921 | 0.69548 | 0.79064 | 0.72014 | 122.3716 | 122.2604 | 122.2404 | 122.1584 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.3371 | 122.3638 | 122.2059 | 122.2327
3975.7344 | 122.4014 | -0.086975 | 122.2916 | 0.69873 | 0.62799 | 0.61985 | 0.58392 | 0.59478 | 0.68993 | 0.60112 | 122.3304 | 122.2146 | 122.1992 | 122.1172 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 0.7857 | 0.71496 | 0.70682 | 0.6709 | 0.68175 | 0.77691 | 0.68809 | 122.3716 | 122.2558 | 122.2404 | 122.1584 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.3508 | 122.3593 | 122.2197 | 122.2282
3977.4844 | 122.3282 | -0.09613 | 122.2595 | 0.69415 | 0.61883 | 0.61069 | 0.57477 | 0.5902 | 0.67162 | 0.60112 | 122.3304 | 122.21 | 122.2038 | 122.1217 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.79028 | 0.71496 | 0.70682 | 0.6709 | 0.68633 | 0.76775 | 0.69725 | 122.3716 | 122.2512 | 122.245 | 122.1629 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2197 | 122.2327
3979.25 | 122.319 | -0.086975 | 122.2916 | 0.69415 | 0.62341 | 0.61527 | 0.57934 | 0.59478 | 0.67619 | 0.61485 | 122.3258 | 122.21 | 122.2084 | 122.1126 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.78113 | 0.71038 | 0.70224 | 0.66632 | 0.68175 | 0.76317 | 0.70183 | 122.367 | 122.2512 | 122.2496 | 122.1538 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3416 | 122.3638 | 122.2243 | 122.2465
3980.9531 | 122.4655 | -0.054932 | 122.2641 | 0.68499 | 0.60967 | 0.59696 | 0.57477 | 0.58562 | 0.67619 | 0.59196 | 122.3258 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.014064 | -0.033484 | 0.001406 | 0.73992 | 0.6646 | 0.65189 | 0.6297 | 0.64055 | 0.73113 | 0.64689 | 122.367 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.055263 | 0.007715 | 0.042605 | 122.3416 | 122.3593 | 122.2151 | 122.2327
3982.7188 | 122.4289 | -0.045776 | 122.2733 | 0.66668 | 0.60051 | 0.59696 | 0.56103 | 0.56731 | 0.65788 | 0.58281 | 122.3349 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.71246 | 0.64629 | 0.64273 | 0.60681 | 0.61308 | 0.70366 | 0.62858 | 122.3761 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3638 | 122.2105 | 122.2282
3984.5 | 122.3419 | -0.091553 | 122.3007 | 0.67126 | 0.59136 | 0.5878 | 0.55645 | 0.55815 | 0.6533 | 0.57823 | 122.3304 | 122.21 | 122.2038 | 122.1172 | -0.011281 | 0.018642 | -0.033484 | -0.003172 | 0.76281 | 0.68291 | 0.67935 | 0.648 | 0.6497 | 0.74486 | 0.66978 | 122.3716 | 122.2512 | 122.245 | 122.1584 | 0.029918 | 0.059841 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2151 | 122.2373
3986.2031 | 122.4976 | -0.050354 | 122.2641 | 0.65752 | 0.5822 | 0.57864 | 0.54729 | 0.56273 | 0.6533 | 0.57823 | 122.3395 | 122.2146 | 122.213 | 122.108 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.70788 | 0.63255 | 0.62899 | 0.59765 | 0.61308 | 0.70366 | 0.62858 | 122.3807 | 122.2558 | 122.2542 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.3508 | 122.3684 | 122.2243 | 122.2419
3987.9688 | 122.3602 | -0.082397 | 122.2824 | 0.67584 | 0.59593 | 0.5878 | 0.56103 | 0.57189 | 0.6533 | 0.57823 | 122.3304 | 122.2192 | 122.2084 | 122.1126 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.75823 | 0.67833 | 0.67019 | 0.64343 | 0.65428 | 0.7357 | 0.66062 | 122.3716 | 122.2604 | 122.2496 | 122.1538 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3508 | 122.3593 | 122.2288 | 122.2373
3989.6562 | 122.4655 | -0.059509 | 122.2778 | 0.67126 | 0.60051 | 0.59696 | 0.55187 | 0.57646 | 0.66246 | 0.58738 | 122.3258 | 122.2054 | 122.2038 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.73077 | 0.66002 | 0.65646 | 0.61138 | 0.63597 | 0.72197 | 0.64689 | 122.367 | 122.2466 | 122.245 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3416 | 122.3547 | 122.2197 | 122.2327
3991.4062 | 122.4747 | -0.064087 | 122.2504 | 0.65752 | 0.58678 | 0.56948 | 0.54272 | 0.55815 | 0.63957 | 0.56907 | 122.3349 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.72161 | 0.65086 | 0.63357 | 0.6068 | 0.62224 | 0.70366 | 0.63316 | 122.3761 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3638 | 122.2105 | 122.2282
3993.1094 | 122.4701 | -0.045776 | 122.2412 | 0.65752 | 0.58678 | 0.58322 | 0.55187 | 0.55815 | 0.6533 | 0.57823 | 122.3304 | 122.2146 | 122.1947 | 122.1172 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 0.7033 | 0.63255 | 0.629 | 0.59765 | 0.60393 | 0.69908 | 0.624 | 122.3716 | 122.2558 | 122.2359 | 122.1584 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 122.3416 | 122.3684 | 122.2059 | 122.2327
3994.8281 | 122.3419 | -0.086975 | 122.2687 | 0.65752 | 0.58678 | 0.57864 | 0.54729 | 0.56273 | 0.65788 | 0.57823 | 122.3349 | 122.2146 | 122.2038 | 122.108 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.7445 | 0.67375 | 0.66562 | 0.63427 | 0.6497 | 0.74486 | 0.6652 | 122.3761 | 122.2558 | 122.245 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.3508 | 122.3638 | 122.2197 | 122.2327
3996.5938 | 122.3419 | -0.09613 | 122.2733 | 0.66668 | 0.59136 | 0.57864 | 0.54729 | 0.55815 | 0.66246 | 0.57823 | 122.3258 | 122.2054 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.76281 | 0.68749 | 0.67477 | 0.64342 | 0.65428 | 0.75859 | 0.67436 | 122.367 | 122.2466 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3371 | 122.3593 | 122.2105 | 122.2327
3998.3438 | 122.374 | -0.086975 | 122.2733 | 0.64837 | 0.58678 | 0.57864 | 0.53814 | 0.549 | 0.64415 | 0.56449 | 122.3349 | 122.2146 | 122.2038 | 122.1172 | -0.015859 | 0.032376 | -0.038063 | -0.003172 | 0.73534 | 0.67375 | 0.66562 | 0.62511 | 0.63597 | 0.73112 | 0.65147 | 122.3761 | 122.2558 | 122.245 | 122.1584 | 0.02534 | 0.073575 | 0.003136 | 0.038027 | 122.3508 | 122.373 | 122.2197 | 122.2419
4000.0469 | 122.3373 | -0.10071 | 122.2961 | 0.65294 | 0.57762 | 0.57406 | 0.52898 | 0.549 | 0.63499 | 0.56449 | 122.3349 | 122.2054 | 122.2038 | 122.1217 | -0.011281 | 0.02322 | -0.038063 | 0.005985 | 0.75365 | 0.67833 | 0.67477 | 0.62969 | 0.6497 | 0.7357 | 0.6652 | 122.3761 | 122.2466 | 122.245 | 122.1629 | 0.029918 | 0.064419 | 0.003136 | 0.047184 | 122.3462 | 122.373 | 122.2151 | 122.2419
4001.75 | 122.4335 | -0.059509 | 122.2458 | 0.64379 | 0.57304 | 0.56033 | 0.5244 | 0.54442 | 0.63041 | 0.55534 | 122.3304 | 122.21 | 122.2038 | 122.1172 | -0.020437 | 0.02322 | -0.028906 | 0.001406 | 0.7033 | 0.63255 | 0.61984 | 0.58391 | 0.60393 | 0.68992 | 0.61485 | 122.3716 | 122.2512 | 122.245 | 122.1584 | 0.020762 | 0.064419 | 0.012293 | 0.042605 | 122.3508 | 122.3593 | 122.2243 | 122.2327
4003.4531 | 122.3831 | -0.09613 | 122.2595 | 0.63463 | 0.56846 | 0.55575 | 0.5244 | 0.53068 | 0.62583 | 0.54618 | 122.3258 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.73076 | 0.66459 | 0.65188 | 0.62053 | 0.62681 | 0.72196 | 0.64231 | 122.367 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3371 | 122.3593 | 122.2151 | 122.2373
4005.2188 | 122.3785 | -0.086975 | 122.2641 | 0.65294 | 0.58678 | 0.5649 | 0.53814 | 0.53984 | 0.63041 | 0.56907 | 122.3349 | 122.2146 | 122.2038 | 122.1172 | -0.020437 | 0.027798 | -0.028906 | 0.001406 | 0.73992 | 0.67375 | 0.65188 | 0.62511 | 0.62682 | 0.71739 | 0.65605 | 122.3761 | 122.2558 | 122.245 | 122.1584 | 0.020762 | 0.068997 | 0.012293 | 0.042605 | 122.3554 | 122.3638 | 122.2243 | 122.2327
4006.9844 | 122.4197 | -0.073242 | 122.2412 | 0.63005 | 0.56388 | 0.54659 | 0.51067 | 0.52153 | 0.6121 | 0.54618 | 122.3349 | 122.2009 | 122.2038 | 122.1126 | -0.015859 | 0.02322 | -0.042641 | -0.003172 | 0.70329 | 0.63713 | 0.61983 | 0.58391 | 0.59477 | 0.68534 | 0.61942 | 122.3761 | 122.2421 | 122.245 | 122.1538 | 0.02534 | 0.064419 | -0.001442 | 0.038027 | 122.3508 | 122.3776 | 122.2197 | 122.2465
4008.7344 | 122.4335 | -0.054932 | 122.2504 | 0.62089 | 0.55015 | 0.54201 | 0.51067 | 0.51237 | 0.60294 | 0.53244 | 122.3395 | 122.21 | 122.2038 | 122.108 | -0.015859 | 0.02322 | -0.038063 | -0.00775 | 0.67583 | 0.60508 | 0.59694 | 0.5656 | 0.5673 | 0.65787 | 0.58738 | 122.3807 | 122.2512 | 122.245 | 122.1492 | 0.02534 | 0.064419 | 0.003136 | 0.033449 | 122.3554 | 122.3776 | 122.2197 | 122.2419
4011.7656 | 122.438 | -0.064087 | 122.2549 | 0.598 | 0.53641 | 0.52828 | 0.49235 | 0.50779 | 0.58921 | 0.51413 | 122.3304 | 122.2054 | 122.1992 | 122.108 | -0.020437 | 0.027798 | -0.038063 | -0.003172 | 0.66209 | 0.6005 | 0.59236 | 0.55644 | 0.57188 | 0.65329 | 0.57822 | 122.3716 | 122.2466 | 122.2404 | 122.1492 | 0.020762 | 0.068997 | 0.003136 | 0.038027 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4014.4531 | 122.3785 | -0.086975 | 122.2595 | 0.598 | 0.52725 | 0.50996 | 0.48778 | 0.49406 | 0.58463 | 0.50498 | 122.3304 | 122.2146 | 122.2038 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.68498 | 0.61423 | 0.59694 | 0.57475 | 0.58104 | 0.6716 | 0.59195 | 122.3716 | 122.2558 | 122.245 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2151 | 122.2373
4018.125 | 122.3602 | -0.086975 | 122.287 | 0.58885 | 0.52267 | 0.5237 | 0.4832 | 0.49406 | 0.57547 | 0.50498 | 122.3258 | 122.2146 | 122.1992 | 122.1126 | -0.011281 | 0.018642 | -0.024328 | 0.001406 | 0.67582 | 0.60965 | 0.61067 | 0.57017 | 0.58104 | 0.66245 | 0.59195 | 122.367 | 122.2558 | 122.2404 | 122.1538 | 0.029918 | 0.059841 | 0.016871 | 0.042605 | 122.3371 | 122.3501 | 122.2105 | 122.2236
4023.4375 | 122.3419 | -0.086975 | 122.2595 | 0.57969 | 0.50894 | 0.50538 | 0.47404 | 0.49406 | 0.57547 | 0.49124 | 122.3395 | 122.21 | 122.1992 | 122.1126 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.66667 | 0.59591 | 0.59236 | 0.56101 | 0.58104 | 0.66245 | 0.57822 | 122.3807 | 122.2512 | 122.2404 | 122.1538 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.373 | 122.2059 | 122.2327
4025.2188 | 122.4472 | -0.068665 | 122.2366 | 0.56138 | 0.48604 | 0.49623 | 0.46488 | 0.47575 | 0.55258 | 0.46835 | 122.3304 | 122.2146 | 122.1992 | 122.1172 | -0.011281 | 0.02322 | -0.038063 | -0.00775 | 0.63004 | 0.55471 | 0.56489 | 0.53355 | 0.54441 | 0.62124 | 0.53702 | 122.3716 | 122.2558 | 122.2404 | 122.1584 | 0.029918 | 0.064419 | 0.003136 | 0.033449 | 122.3416 | 122.3684 | 122.2105 | 122.2373
4026.9219 | 122.438 | -0.054932 | 122.2733 | 0.54764 | 0.49062 | 0.48707 | 0.44199 | 0.45744 | 0.53884 | 0.46835 | 122.3349 | 122.2146 | 122.1947 | 122.1172 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.60257 | 0.54555 | 0.542 | 0.49692 | 0.51237 | 0.59377 | 0.52328 | 122.3761 | 122.2558 | 122.2359 | 122.1584 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.3416 | 122.3638 | 122.2014 | 122.2236
4028.6719 | 122.4106 | -0.07782 | 122.2778 | 0.56595 | 0.50436 | 0.49623 | 0.4603 | 0.47117 | 0.548 | 0.47751 | 122.3258 | 122.2054 | 122.1947 | 122.1172 | -0.020437 | 0.027798 | -0.038063 | -0.00775 | 0.64377 | 0.58218 | 0.57405 | 0.53812 | 0.54899 | 0.62582 | 0.55533 | 122.367 | 122.2466 | 122.2359 | 122.1584 | 0.020762 | 0.068997 | 0.003136 | 0.033449 | 122.3462 | 122.3638 | 122.2151 | 122.2327
4030.4375 | 122.3785 | -0.068665 | 122.2778 | 0.5568 | 0.4952 | 0.48707 | 0.45572 | 0.45286 | 0.54342 | 0.47293 | 122.3304 | 122.2146 | 122.1947 | 122.1217 | -0.020437 | 0.018642 | -0.028906 | -0.003172 | 0.62546 | 0.56387 | 0.55573 | 0.52439 | 0.52152 | 0.61209 | 0.54159 | 122.3716 | 122.2558 | 122.2359 | 122.1629 | 0.020762 | 0.059841 | 0.012293 | 0.038027 | 122.3508 | 122.3593 | 122.2151 | 122.2236
4032.2188 | 122.3511 | -0.086975 | 122.2778 | 0.55222 | 0.4952 | 0.48707 | 0.45115 | 0.45744 | 0.54342 | 0.45919 | 122.3304 | 122.21 | 122.2038 | 122.1172 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.6392 | 0.58218 | 0.57404 | 0.53812 | 0.54441 | 0.6304 | 0.54617 | 122.3716 | 122.2512 | 122.245 | 122.1584 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3462 | 122.3593 | 122.2197 | 122.2327
4033.9219 | 122.4701 | -0.054932 | 122.2549 | 0.54306 | 0.47689 | 0.47333 | 0.44657 | 0.4437 | 0.53884 | 0.45004 | 122.3212 | 122.21 | 122.1992 | 122.1217 | -0.006702 | 0.027798 | -0.028906 | 0.005985 | 0.59799 | 0.53182 | 0.52826 | 0.5015 | 0.49863 | 0.59377 | 0.50497 | 122.3624 | 122.2512 | 122.2404 | 122.1629 | 0.034497 | 0.068997 | 0.012293 | 0.047184 | 122.3279 | 122.3501 | 122.2059 | 122.2282
4035.6094 | 122.3923 | -0.07782 | 122.2641 | 0.53391 | 0.47231 | 0.46418 | 0.42368 | 0.43912 | 0.52053 | 0.4363 | 122.3304 | 122.21 | 122.1992 | 122.1126 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.61173 | 0.55013 | 0.542 | 0.5015 | 0.51694 | 0.59835 | 0.51412 | 122.3716 | 122.2512 | 122.2404 | 122.1538 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2151 | 122.2282
4037.375 | 122.3969 | -0.073242 | 122.2733 | 0.53391 | 0.48146 | 0.46875 | 0.44199 | 0.44828 | 0.53426 | 0.44546 | 122.3304 | 122.2237 | 122.2038 | 122.1126 | -0.015859 | 0.02322 | -0.038063 | -0.00775 | 0.60715 | 0.55471 | 0.542 | 0.51523 | 0.52152 | 0.60751 | 0.5187 | 122.3716 | 122.2649 | 122.245 | 122.1538 | 0.02534 | 0.064419 | 0.003136 | 0.033449 | 122.3462 | 122.3684 | 122.2197 | 122.2419
4039.1562 | 122.438 | -0.045776 | 122.2549 | 0.52017 | 0.45857 | 0.45044 | 0.41452 | 0.42539 | 0.51595 | 0.42715 | 122.3349 | 122.2146 | 122.1901 | 122.1172 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 0.56595 | 0.50435 | 0.49621 | 0.4603 | 0.47117 | 0.56173 | 0.47292 | 122.3761 | 122.2558 | 122.2313 | 122.1584 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 122.3462 | 122.373 | 122.2014 | 122.2282
4040.875 | 122.3694 | -0.10529 | 122.2824 | 0.49728 | 0.43568 | 0.42297 | 0.40078 | 0.40708 | 0.4839 | 0.39968 | 122.3349 | 122.2146 | 122.1992 | 122.1172 | -0.011281 | 0.02322 | -0.038063 | 0.001406 | 0.60257 | 0.54096 | 0.52825 | 0.50607 | 0.51237 | 0.58919 | 0.50496 | 122.3761 | 122.2558 | 122.2404 | 122.1584 | 0.029918 | 0.064419 | 0.003136 | 0.042605 | 122.3462 | 122.373 | 122.2105 | 122.2373
4042.6406 | 122.3465 | -0.10071 | 122.2824 | 0.47896 | 0.41736 | 0.41381 | 0.38705 | 0.38419 | 0.46101 | 0.38594 | 122.3304 | 122.2192 | 122.2038 | 122.1126 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.57967 | 0.51807 | 0.51452 | 0.48776 | 0.4849 | 0.56172 | 0.48665 | 122.3716 | 122.2604 | 122.245 | 122.1538 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2197 | 122.2327
4044.3438 | 122.4655 | -0.045776 | 122.2687 | 0.49728 | 0.42652 | 0.42755 | 0.38705 | 0.39335 | 0.47932 | 0.3951 | 122.3349 | 122.2009 | 122.2038 | 122.1172 | -0.015859 | 0.018642 | -0.038063 | -0.003172 | 0.54306 | 0.47229 | 0.47332 | 0.43282 | 0.43912 | 0.5251 | 0.44088 | 122.3761 | 122.2421 | 122.245 | 122.1584 | 0.02534 | 0.059841 | 0.003136 | 0.038027 | 122.3508 | 122.373 | 122.2197 | 122.2419
4046.1094 | 122.4335 | -0.068665 | 122.2641 | 0.48354 | 0.42194 | 0.40008 | 0.37789 | 0.38419 | 0.46559 | 0.38137 | 122.3349 | 122.2192 | 122.2084 | 122.1126 | -0.025015 | 0.02322 | -0.033484 | -0.003172 | 0.55221 | 0.4906 | 0.46874 | 0.44656 | 0.45286 | 0.53425 | 0.45003 | 122.3761 | 122.2604 | 122.2496 | 122.1538 | 0.016184 | 0.064419 | 0.007715 | 0.038027 | 122.36 | 122.3684 | 122.2334 | 122.2419
4047.7969 | 122.3969 | -0.07782 | 122.2549 | 0.45607 | 0.40363 | 0.3955 | 0.36416 | 0.36588 | 0.44728 | 0.37221 | 122.3258 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.53389 | 0.48145 | 0.47332 | 0.44198 | 0.4437 | 0.5251 | 0.45003 | 122.367 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.3371 | 122.3547 | 122.2105 | 122.2282
4049.5625 | 122.3282 | -0.091553 | 122.2961 | 0.45149 | 0.39447 | 0.38634 | 0.355 | 0.3613 | 0.4427 | 0.36305 | 122.3304 | 122.2146 | 122.2084 | 122.1126 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.54305 | 0.48602 | 0.47789 | 0.44655 | 0.45285 | 0.53425 | 0.45461 | 122.3716 | 122.2558 | 122.2496 | 122.1538 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3462 | 122.3638 | 122.2243 | 122.2419
4051.3281 | 122.3602 | -0.10071 | 122.2778 | 0.44692 | 0.38531 | 0.38176 | 0.34584 | 0.35672 | 0.43812 | 0.35847 | 122.3349 | 122.2054 | 122.2038 | 122.1172 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 0.54763 | 0.48602 | 0.48247 | 0.44655 | 0.45743 | 0.53883 | 0.45918 | 122.3761 | 122.2466 | 122.245 | 122.1584 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 122.3462 | 122.373 | 122.2151 | 122.2419
4053.0938 | 122.4609 | -0.054932 | 122.2824 | 0.46981 | 0.4082 | 0.40008 | 0.36416 | 0.37503 | 0.45185 | 0.36305 | 122.3304 | 122.21 | 122.2038 | 122.1034 | -0.006702 | 0.02322 | -0.033484 | -0.003172 | 0.52474 | 0.46313 | 0.45501 | 0.41909 | 0.42997 | 0.50679 | 0.41798 | 122.3716 | 122.2512 | 122.245 | 122.1446 | 0.034497 | 0.064419 | 0.007715 | 0.038027 | 122.3371 | 122.3638 | 122.2105 | 122.2373
4054.7812 | 122.3511 | -0.082397 | 122.2778 | 0.44692 | 0.39447 | 0.38634 | 0.35958 | 0.37503 | 0.4427 | 0.3539 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.018642 | -0.038063 | -0.00775 | 0.52931 | 0.47686 | 0.46874 | 0.44197 | 0.45743 | 0.52509 | 0.43629 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.059841 | 0.003136 | 0.033449 | 122.3416 | 122.3684 | 122.2105 | 122.2373
4056.5625 | 122.4197 | -0.064087 | 122.2595 | 0.43318 | 0.38073 | 0.36345 | 0.33668 | 0.35214 | 0.42896 | 0.34474 | 122.3304 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.49727 | 0.44482 | 0.42753 | 0.40077 | 0.41623 | 0.49305 | 0.40883 | 122.3716 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.3462 | 122.3593 | 122.2151 | 122.2282
4058.3281 | 122.4792 | -0.045776 | 122.2321 | 0.42402 | 0.38073 | 0.36345 | 0.34584 | 0.35214 | 0.43812 | 0.34932 | 122.3349 | 122.2146 | 122.1992 | 122.1126 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 0.4698 | 0.42651 | 0.40922 | 0.39162 | 0.39792 | 0.48389 | 0.39509 | 122.3761 | 122.2558 | 122.2404 | 122.1538 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 122.3462 | 122.373 | 122.2105 | 122.2373
4060.0938 | 122.3557 | -0.086975 | 122.319 | 0.42402 | 0.37157 | 0.36345 | 0.33211 | 0.35214 | 0.43354 | 0.34474 | 122.3258 | 122.2054 | 122.2038 | 122.1217 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 0.511 | 0.45855 | 0.45042 | 0.41908 | 0.43912 | 0.52051 | 0.43171 | 122.367 | 122.2466 | 122.245 | 122.1629 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.3462 | 122.3547 | 122.2243 | 122.2327
4061.7969 | 122.4884 | -0.07782 | 122.2504 | 0.42402 | 0.37157 | 0.36345 | 0.32753 | 0.34757 | 0.42438 | 0.34016 | 122.3349 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | -0.003172 | 0.50184 | 0.44939 | 0.44127 | 0.40535 | 0.42539 | 0.5022 | 0.41798 | 122.3761 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2105 | 122.2282
4063.5938 | 122.4106 | -0.068665 | 122.2504 | 0.42402 | 0.36241 | 0.35429 | 0.33668 | 0.34299 | 0.4198 | 0.33101 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.015859 | 0.036954 | -0.033484 | -0.003172 | 0.49269 | 0.43108 | 0.42295 | 0.40535 | 0.41165 | 0.48847 | 0.39967 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.02534 | 0.078153 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4065.3906 | 122.4014 | -0.041199 | 122.2549 | 0.41945 | 0.36241 | 0.35429 | 0.33211 | 0.35214 | 0.41523 | 0.32643 | 122.3304 | 122.21 | 122.1992 | 122.1126 | -0.015859 | 0.032376 | -0.038063 | -0.003172 | 0.46064 | 0.40361 | 0.39549 | 0.3733 | 0.39334 | 0.45643 | 0.36763 | 122.3716 | 122.2512 | 122.2404 | 122.1538 | 0.02534 | 0.073575 | 0.003136 | 0.038027 | 122.3462 | 122.3684 | 122.2151 | 122.2373
4067.1406 | 122.3602 | -0.10529 | 122.2961 | 0.41487 | 0.36699 | 0.34513 | 0.32753 | 0.34299 | 0.4198 | 0.33101 | 122.3304 | 122.21 | 122.2084 | 122.1172 | -0.006702 | 0.02322 | -0.028906 | -0.003172 | 0.52015 | 0.47228 | 0.45042 | 0.43281 | 0.44827 | 0.52509 | 0.43629 | 122.3716 | 122.2512 | 122.2496 | 122.1584 | 0.034497 | 0.064419 | 0.012293 | 0.038027 | 122.3371 | 122.3593 | 122.2151 | 122.2373
4068.8438 | 122.4243 | -0.050354 | 122.2549 | 0.41029 | 0.35784 | 0.34971 | 0.31379 | 0.33383 | 0.40607 | 0.32643 | 122.3304 | 122.2054 | 122.1992 | 122.1172 | -0.020437 | 0.027798 | -0.038063 | 0.005985 | 0.46064 | 0.40819 | 0.40006 | 0.36415 | 0.38419 | 0.45642 | 0.37678 | 122.3716 | 122.2466 | 122.2404 | 122.1584 | 0.020762 | 0.068997 | 0.003136 | 0.047184 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4070.6094 | 122.4701 | -0.054932 | 122.2549 | 0.40113 | 0.34868 | 0.34513 | 0.31379 | 0.3201 | 0.40607 | 0.32185 | 122.3349 | 122.2146 | 122.1947 | 122.108 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.45606 | 0.40361 | 0.40006 | 0.36872 | 0.37503 | 0.461 | 0.37678 | 122.3761 | 122.2558 | 122.2359 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3508 | 122.3638 | 122.2105 | 122.2236
4072.375 | 122.3969 | -0.073242 | 122.2687 | 0.40113 | 0.34868 | 0.34971 | 0.30463 | 0.32925 | 0.40607 | 0.31727 | 122.3304 | 122.2146 | 122.2084 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.47437 | 0.42192 | 0.42295 | 0.37788 | 0.4025 | 0.47931 | 0.39051 | 122.3716 | 122.2558 | 122.2496 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3462 | 122.3593 | 122.2243 | 122.2373
4074.1562 | 122.3648 | -0.082397 | 122.2549 | 0.38282 | 0.33494 | 0.32682 | 0.31837 | 0.32925 | 0.40607 | 0.31269 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 0.46522 | 0.41734 | 0.40921 | 0.40077 | 0.41165 | 0.48847 | 0.39509 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 122.3416 | 122.373 | 122.2105 | 122.2419
4075.8594 | 122.493 | -0.064087 | 122.2412 | 0.37366 | 0.32578 | 0.31308 | 0.29548 | 0.31094 | 0.38318 | 0.30354 | 122.3395 | 122.2146 | 122.1992 | 122.1126 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 0.43775 | 0.38987 | 0.37717 | 0.35957 | 0.37503 | 0.44727 | 0.36762 | 122.3807 | 122.2558 | 122.2404 | 122.1538 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 122.3554 | 122.3684 | 122.2151 | 122.2282
4077.625 | 122.3557 | -0.09613 | 122.2778 | 0.38282 | 0.32578 | 0.32224 | 0.29548 | 0.31094 | 0.39233 | 0.30354 | 122.3304 | 122.2146 | 122.2038 | 122.1172 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.47895 | 0.42191 | 0.41837 | 0.39161 | 0.40707 | 0.48846 | 0.39967 | 122.3716 | 122.2558 | 122.245 | 122.1584 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3462 | 122.3593 | 122.2197 | 122.2327
4079.3906 | 122.3465 | -0.10529 | 122.2595 | 0.36908 | 0.30747 | 0.30392 | 0.28632 | 0.29721 | 0.3786 | 0.28065 | 122.3304 | 122.2146 | 122.2084 | 122.1172 | -0.015859 | 0.018642 | -0.028906 | -0.003172 | 0.47437 | 0.41275 | 0.40921 | 0.39161 | 0.40249 | 0.48389 | 0.38593 | 122.3716 | 122.2558 | 122.2496 | 122.1584 | 0.02534 | 0.059841 | 0.012293 | 0.038027 | 122.3462 | 122.3593 | 122.2243 | 122.2373
4081.2031 | 122.4747 | -0.045776 | 122.2275 | 0.35535 | 0.29831 | 0.29477 | 0.27259 | 0.28347 | 0.36486 | 0.27149 | 122.3349 | 122.21 | 122.2038 | 122.1172 | -0.015859 | 0.02322 | -0.028906 | -0.003172 | 0.40113 | 0.34409 | 0.34054 | 0.31836 | 0.32925 | 0.41064 | 0.31726 | 122.3761 | 122.2512 | 122.245 | 122.1584 | 0.02534 | 0.064419 | 0.012293 | 0.038027 | 122.3508 | 122.3638 | 122.2197 | 122.2327
4082.9844 | 122.3282 | -0.091553 | 122.2916 | 0.36451 | 0.31663 | 0.30392 | 0.28632 | 0.30179 | 0.3786 | 0.29438 | 122.3304 | 122.21 | 122.1992 | 122.1034 | -0.020437 | 0.027798 | -0.028906 | -0.003172 | 0.45606 | 0.40818 | 0.39548 | 0.37787 | 0.39334 | 0.47015 | 0.38593 | 122.3716 | 122.2512 | 122.2404 | 122.1446 | 0.020762 | 0.068997 | 0.012293 | 0.038027 | 122.3508 | 122.3593 | 122.2197 | 122.2282
4084.7031 | 122.4289 | -0.054932 | 122.2733 | 0.35535 | 0.29831 | 0.30392 | 0.27259 | 0.29263 | 0.37402 | 0.2898 | 122.3349 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.018642 | -0.038063 | 0.001406 | 0.41028 | 0.35324 | 0.35886 | 0.32752 | 0.34756 | 0.42895 | 0.34473 | 122.3761 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.059841 | 0.003136 | 0.042605 | 122.3508 | 122.373 | 122.2105 | 122.2327
4086.4219 | 122.3923 | -0.11902 | 122.2733 | 0.36908 | 0.31663 | 0.3085 | 0.2909 | 0.30179 | 0.3786 | 0.2898 | 122.3258 | 122.21 | 122.2038 | 122.1172 | -0.020437 | 0.018642 | -0.033484 | 0.005985 | 0.4881 | 0.43565 | 0.42752 | 0.40992 | 0.4208 | 0.49762 | 0.40882 | 122.367 | 122.2512 | 122.245 | 122.1584 | 0.020762 | 0.059841 | 0.007715 | 0.047184 | 122.3462 | 122.3593 | 122.2243 | 122.2373
4088.1719 | 122.4747 | -0.054932 | 122.1954 | 0.35077 | 0.30289 | 0.30392 | 0.26801 | 0.28805 | 0.36944 | 0.27607 | 122.3304 | 122.21 | 122.1992 | 122.1172 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.4057 | 0.35782 | 0.35886 | 0.32294 | 0.34298 | 0.42438 | 0.331 | 122.3716 | 122.2512 | 122.2404 | 122.1584 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3508 | 122.3638 | 122.2197 | 122.2327
4089.875 | 122.438 | -0.07782 | 122.2412 | 0.35535 | 0.29831 | 0.29019 | 0.27716 | 0.29263 | 0.36944 | 0.28065 | 122.3349 | 122.21 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.43317 | 0.37613 | 0.36801 | 0.35498 | 0.37045 | 0.44726 | 0.35847 | 122.3761 | 122.2512 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3462 | 122.3638 | 122.2105 | 122.2282
4091.625 | 122.3877 | -0.082397 | 122.2824 | 0.35535 | 0.29373 | 0.28561 | 0.27259 | 0.28805 | 0.36486 | 0.28065 | 122.3304 | 122.21 | 122.2084 | 122.1172 | -0.020437 | 0.032376 | -0.033484 | -0.003172 | 0.43775 | 0.37613 | 0.36801 | 0.35498 | 0.37045 | 0.44726 | 0.36304 | 122.3716 | 122.2512 | 122.2496 | 122.1584 | 0.020762 | 0.073575 | 0.007715 | 0.038027 | 122.3508 | 122.3638 | 122.2288 | 122.2419
4093.3281 | 122.3877 | -0.10071 | 122.2687 | 0.33703 | 0.28915 | 0.28103 | 0.26801 | 0.28347 | 0.36029 | 0.27149 | 122.3349 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 0.43774 | 0.38986 | 0.38174 | 0.36872 | 0.38418 | 0.46099 | 0.3722 | 122.3761 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 122.3462 | 122.373 | 122.2105 | 122.2373
4095.0312 | 122.4426 | -0.059509 | 122.2916 | 0.34619 | 0.29373 | 0.28103 | 0.26801 | 0.28347 | 0.36486 | 0.27149 | 122.3349 | 122.21 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.4057 | 0.35324 | 0.34054 | 0.32752 | 0.34298 | 0.42437 | 0.331 | 122.3761 | 122.2512 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4096.7188 | 122.3602 | -0.10529 | 122.2733 | 0.33703 | 0.29373 | 0.27187 | 0.25885 | 0.27432 | 0.35571 | 0.27149 | 122.3349 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.44232 | 0.39902 | 0.37716 | 0.36414 | 0.3796 | 0.46099 | 0.37677 | 122.3761 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4098.4219 | 122.4838 | -0.068665 | 122.2504 | 0.34161 | 0.29373 | 0.29019 | 0.25885 | 0.2789 | 0.34655 | 0.27149 | 122.3349 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.41028 | 0.3624 | 0.35885 | 0.32752 | 0.34756 | 0.41522 | 0.34015 | 122.3761 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.3508 | 122.3684 | 122.2105 | 122.2282
4100.125 | 122.374 | -0.086975 | 122.287 | 0.33246 | 0.29373 | 0.28561 | 0.25427 | 0.2789 | 0.34655 | 0.27149 | 122.3349 | 122.2192 | 122.1992 | 122.1126 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.41943 | 0.38071 | 0.37258 | 0.34125 | 0.36587 | 0.43353 | 0.35846 | 122.3761 | 122.2604 | 122.2404 | 122.1538 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 122.3416 | 122.3684 | 122.2059 | 122.2327
4101.8281 | 122.4838 | -0.050354 | 122.2504 | 0.32788 | 0.27084 | 0.27187 | 0.24511 | 0.26059 | 0.33739 | 0.25318 | 122.3304 | 122.2054 | 122.2038 | 122.1034 | -0.025015 | 0.02322 | -0.033484 | -0.003172 | 0.37823 | 0.32119 | 0.32223 | 0.29547 | 0.31094 | 0.38775 | 0.30353 | 122.3716 | 122.2466 | 122.245 | 122.1446 | 0.016184 | 0.064419 | 0.007715 | 0.038027 | 122.3554 | 122.3638 | 122.2288 | 122.2373
4103.5781 | 122.4518 | -0.050354 | 122.2458 | 0.3233 | 0.27542 | 0.2673 | 0.24969 | 0.26059 | 0.33739 | 0.25318 | 122.3258 | 122.2054 | 122.1992 | 122.1172 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.37365 | 0.32577 | 0.31765 | 0.30005 | 0.31094 | 0.38775 | 0.30353 | 122.367 | 122.2466 | 122.2404 | 122.1584 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.3325 | 122.3593 | 122.2059 | 122.2327
4105.2812 | 122.3648 | -0.09613 | 122.2733 | 0.31872 | 0.27542 | 0.2673 | 0.24054 | 0.26516 | 0.32366 | 0.24402 | 122.3304 | 122.21 | 122.2038 | 122.1172 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 0.41485 | 0.37155 | 0.36342 | 0.33667 | 0.36129 | 0.41979 | 0.34015 | 122.3716 | 122.2512 | 122.245 | 122.1584 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 122.3416 | 122.3684 | 122.2151 | 122.2419
4106.9844 | 122.4609 | -0.045776 | 122.2549 | 0.31872 | 0.27084 | 0.26272 | 0.23596 | 0.25143 | 0.32824 | 0.24402 | 122.3349 | 122.21 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.3645 | 0.31661 | 0.30849 | 0.28173 | 0.2972 | 0.37401 | 0.2898 | 122.3761 | 122.2512 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4108.6875 | 122.3511 | -0.09613 | 122.2687 | 0.31414 | 0.27542 | 0.26272 | 0.23138 | 0.25143 | 0.33282 | 0.24402 | 122.3349 | 122.2146 | 122.1947 | 122.1126 | -0.015859 | 0.027798 | -0.042641 | -0.003172 | 0.41027 | 0.37155 | 0.35885 | 0.32751 | 0.34756 | 0.42895 | 0.34015 | 122.3761 | 122.2558 | 122.2359 | 122.1538 | 0.02534 | 0.068997 | -0.001442 | 0.038027 | 122.3508 | 122.3776 | 122.2105 | 122.2373
4110.375 | 122.4564 | -0.054932 | 122.2458 | 0.30499 | 0.25252 | 0.25814 | 0.23138 | 0.23769 | 0.32366 | 0.23486 | 122.3304 | 122.2146 | 122.1992 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.35992 | 0.30746 | 0.31307 | 0.28631 | 0.29263 | 0.37859 | 0.2898 | 122.3716 | 122.2558 | 122.2404 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2105 | 122.2327
4112.0781 | 122.4014 | -0.10986 | 122.287 | 0.30499 | 0.26626 | 0.25356 | 0.23596 | 0.24227 | 0.32366 | 0.23486 | 122.3304 | 122.2146 | 122.2038 | 122.1172 | -0.020437 | 0.032376 | -0.033484 | 0.001406 | 0.41485 | 0.37612 | 0.36342 | 0.34582 | 0.35214 | 0.43352 | 0.34473 | 122.3716 | 122.2558 | 122.245 | 122.1584 | 0.020762 | 0.073575 | 0.007715 | 0.042605 | 122.3508 | 122.3638 | 122.2243 | 122.2373
4113.7812 | 122.4655 | -0.045776 | 122.2183 | 0.29583 | 0.24794 | 0.2444 | 0.22222 | 0.23769 | 0.30992 | 0.21655 | 122.3349 | 122.21 | 122.1992 | 122.1172 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.34161 | 0.29372 | 0.29018 | 0.268 | 0.28347 | 0.3557 | 0.26233 | 122.3761 | 122.2512 | 122.2404 | 122.1584 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3508 | 122.3638 | 122.2151 | 122.2282
4115.5312 | 122.4152 | -0.068665 | 122.2412 | 0.30041 | 0.25252 | 0.23982 | 0.22222 | 0.24227 | 0.3145 | 0.23029 | 122.3304 | 122.2146 | 122.2038 | 122.1172 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.36907 | 0.32119 | 0.30849 | 0.29089 | 0.31094 | 0.38317 | 0.29895 | 122.3716 | 122.2558 | 122.245 | 122.1584 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2151 | 122.2373
4117.2344 | 122.4747 | -0.054932 | 122.2641 | 0.29583 | 0.2571 | 0.25356 | 0.2268 | 0.23769 | 0.31908 | 0.23029 | 122.3395 | 122.2146 | 122.2038 | 122.1126 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 0.35076 | 0.31203 | 0.30849 | 0.28173 | 0.29263 | 0.37401 | 0.28522 | 122.3807 | 122.2558 | 122.245 | 122.1538 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 122.3508 | 122.3776 | 122.2151 | 122.2419
4118.9375 | 122.3419 | -0.10529 | 122.2641 | 0.30041 | 0.25252 | 0.24898 | 0.22222 | 0.23769 | 0.31908 | 0.23029 | 122.3304 | 122.2054 | 122.1992 | 122.108 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.40569 | 0.35781 | 0.35427 | 0.32751 | 0.34298 | 0.42437 | 0.33557 | 122.3716 | 122.2466 | 122.2404 | 122.1492 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2151 | 122.2327
4120.6406 | 122.4426 | -0.054932 | 122.2229 | 0.29583 | 0.24794 | 0.24898 | 0.21307 | 0.23769 | 0.30992 | 0.22113 | 122.3304 | 122.21 | 122.2038 | 122.1172 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.35076 | 0.30288 | 0.30391 | 0.268 | 0.29263 | 0.36486 | 0.27606 | 122.3716 | 122.2512 | 122.245 | 122.1584 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2197 | 122.2373
4122.3281 | 122.3923 | -0.086975 | 122.2824 | 0.30041 | 0.2571 | 0.25356 | 0.2268 | 0.23769 | 0.31908 | 0.23029 | 122.3395 | 122.2054 | 122.2084 | 122.1126 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.38738 | 0.34408 | 0.34053 | 0.31378 | 0.32467 | 0.40606 | 0.31726 | 122.3807 | 122.2466 | 122.2496 | 122.1538 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3554 | 122.3684 | 122.2243 | 122.2373
4124.0312 | 122.4609 | -0.050354 | 122.2412 | 0.30041 | 0.25252 | 0.24898 | 0.21764 | 0.23769 | 0.30992 | 0.23029 | 122.3258 | 122.2054 | 122.2084 | 122.1034 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.35076 | 0.30288 | 0.29934 | 0.268 | 0.28805 | 0.36028 | 0.28064 | 122.367 | 122.2466 | 122.2496 | 122.1446 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.3416 | 122.3547 | 122.2243 | 122.2373
4125.75 | 122.4747 | -0.050354 | 122.2275 | 0.29583 | 0.26168 | 0.2444 | 0.22222 | 0.23312 | 0.3145 | 0.22571 | 122.3304 | 122.21 | 122.1992 | 122.1126 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.34618 | 0.31204 | 0.29476 | 0.27258 | 0.28347 | 0.36486 | 0.27606 | 122.3716 | 122.2512 | 122.2404 | 122.1538 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.3462 | 122.3638 | 122.2151 | 122.2327
4127.4375 | 122.3969 | -0.064087 | 122.2549 | 0.29583 | 0.25252 | 0.24898 | 0.22222 | 0.24227 | 0.30535 | 0.22113 | 122.3349 | 122.21 | 122.2084 | 122.108 | -0.006702 | 0.027798 | -0.028906 | 0.005985 | 0.35992 | 0.31661 | 0.31307 | 0.28631 | 0.30636 | 0.36943 | 0.28522 | 122.3761 | 122.2512 | 122.2496 | 122.1492 | 0.034497 | 0.068997 | 0.012293 | 0.047184 | 122.3416 | 122.3638 | 122.2151 | 122.2373
4129.1406 | 122.4197 | -0.068665 | 122.2412 | 0.28667 | 0.2571 | 0.24898 | 0.21764 | 0.22854 | 0.30992 | 0.22113 | 122.3349 | 122.2009 | 122.1992 | 122.1126 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.35534 | 0.32577 | 0.31765 | 0.28631 | 0.2972 | 0.37859 | 0.28979 | 122.3761 | 122.2421 | 122.2404 | 122.1538 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4130.8281 | 122.374 | -0.11444 | 122.2733 | 0.29583 | 0.2571 | 0.2444 | 0.21307 | 0.23769 | 0.30992 | 0.22571 | 122.3258 | 122.2054 | 122.1992 | 122.1172 | -0.015859 | 0.027798 | -0.033484 | -0.00775 | 0.41027 | 0.37154 | 0.35884 | 0.32751 | 0.35214 | 0.42436 | 0.34015 | 122.367 | 122.2466 | 122.2404 | 122.1584 | 0.02534 | 0.068997 | 0.007715 | 0.033449 | 122.3416 | 122.3593 | 122.2151 | 122.2327
4132.5312 | 122.3923 | -0.07782 | 122.2504 | 0.28667 | 0.25252 | 0.24898 | 0.21764 | 0.23312 | 0.29619 | 0.21655 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.36449 | 0.33034 | 0.3268 | 0.29546 | 0.31094 | 0.37401 | 0.29437 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.3684 | 122.2151 | 122.2373
4134.25 | 122.3923 | -0.09613 | 122.2733 | 0.28209 | 0.25252 | 0.23982 | 0.21764 | 0.21938 | 0.29619 | 0.21197 | 122.3349 | 122.2146 | 122.1992 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.37822 | 0.34865 | 0.33595 | 0.31377 | 0.31551 | 0.39232 | 0.3081 | 122.3761 | 122.2558 | 122.2404 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3508 | 122.3638 | 122.2151 | 122.2282
4135.9375 | 122.4518 | -0.045776 | 122.2275 | 0.29125 | 0.24794 | 0.23067 | 0.20849 | 0.22396 | 0.30077 | 0.21655 | 122.3349 | 122.21 | 122.1992 | 122.1126 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.33703 | 0.29372 | 0.27644 | 0.25426 | 0.26974 | 0.34654 | 0.26233 | 122.3761 | 122.2512 | 122.2404 | 122.1538 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.3462 | 122.3638 | 122.2105 | 122.2282
4137.6406 | 122.4609 | -0.07782 | 122.2504 | 0.28667 | 0.25252 | 0.2444 | 0.21764 | 0.22854 | 0.30077 | 0.21655 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.36449 | 0.33034 | 0.32222 | 0.29546 | 0.30636 | 0.37859 | 0.29437 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3462 | 122.3684 | 122.2151 | 122.2373
4139.3438 | 122.3328 | -0.10529 | 122.2824 | 0.28667 | 0.24337 | 0.23067 | 0.21307 | 0.21938 | 0.30535 | 0.21197 | 122.3349 | 122.2054 | 122.1992 | 122.108 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.39196 | 0.34865 | 0.33595 | 0.31835 | 0.32467 | 0.41063 | 0.31726 | 122.3761 | 122.2466 | 122.2404 | 122.1492 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4141.1094 | 122.4335 | -0.045776 | 122.2504 | 0.29583 | 0.24337 | 0.2444 | 0.21307 | 0.22396 | 0.29619 | 0.21197 | 122.3349 | 122.21 | 122.1947 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.34161 | 0.28914 | 0.29018 | 0.25884 | 0.26974 | 0.34196 | 0.25775 | 122.3761 | 122.2512 | 122.2359 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3462 | 122.3684 | 122.2059 | 122.2282
4142.7969 | 122.3648 | -0.091553 | 122.2961 | 0.28209 | 0.24794 | 0.23525 | 0.21307 | 0.21938 | 0.30535 | 0.21197 | 122.3349 | 122.21 | 122.1992 | 122.1126 | -0.015859 | 0.02322 | -0.033484 | -0.00775 | 0.37365 | 0.3395 | 0.3268 | 0.30462 | 0.31094 | 0.3969 | 0.30353 | 122.3761 | 122.2512 | 122.2404 | 122.1538 | 0.02534 | 0.064419 | 0.007715 | 0.033449 | 122.3508 | 122.3684 | 122.2151 | 122.2327
4144.4844 | 122.4655 | -0.054932 | 122.2458 | 0.27752 | 0.23879 | 0.23067 | 0.21307 | 0.21938 | 0.30077 | 0.21197 | 122.3258 | 122.2146 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.33245 | 0.29372 | 0.2856 | 0.268 | 0.27431 | 0.3557 | 0.26691 | 122.367 | 122.2558 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.3371 | 122.3593 | 122.2105 | 122.2327
4146.1875 | 122.4701 | -0.054932 | 122.2366 | 0.28209 | 0.24337 | 0.23982 | 0.20849 | 0.21938 | 0.29619 | 0.20739 | 122.3304 | 122.21 | 122.1992 | 122.1126 | -0.015859 | 0.027798 | -0.019749 | 0.005985 | 0.33703 | 0.2983 | 0.29476 | 0.26342 | 0.27431 | 0.35112 | 0.26233 | 122.3716 | 122.2512 | 122.2404 | 122.1538 | 0.02534 | 0.068997 | 0.02145 | 0.047184 | 122.3462 | 122.3501 | 122.2151 | 122.219
4147.8906 | 122.3969 | -0.086975 | 122.2778 | 0.26836 | 0.23879 | 0.21693 | 0.20391 | 0.21023 | 0.29161 | 0.20282 | 122.3258 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.35533 | 0.32576 | 0.30391 | 0.29088 | 0.2972 | 0.37858 | 0.28979 | 122.367 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.3371 | 122.3593 | 122.2151 | 122.2373
4149.6094 | 122.3557 | -0.086975 | 122.2733 | 0.27752 | 0.23879 | 0.23067 | 0.20849 | 0.21023 | 0.29161 | 0.20739 | 122.3349 | 122.2146 | 122.2038 | 122.1126 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 0.36449 | 0.32576 | 0.31764 | 0.29546 | 0.2972 | 0.37858 | 0.29437 | 122.3761 | 122.2558 | 122.245 | 122.1538 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 122.3416 | 122.3684 | 122.2105 | 122.2373
4151.3125 | 122.4609 | -0.041199 | 122.2412 | 0.28209 | 0.23421 | 0.22609 | 0.20391 | 0.2148 | 0.28703 | 0.20739 | 122.3304 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.32329 | 0.27541 | 0.26729 | 0.24511 | 0.256 | 0.32823 | 0.24859 | 122.3716 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.3416 | 122.3638 | 122.2105 | 122.2327
4153.0781 | 122.4976 | -0.036621 | 122.2412 | 0.28209 | 0.23879 | 0.23067 | 0.20849 | 0.22854 | 0.29619 | 0.20739 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.032376 | -0.024328 | 0.005985 | 0.31872 | 0.27541 | 0.26729 | 0.24511 | 0.26516 | 0.33281 | 0.24402 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.073575 | 0.016871 | 0.047184 | 122.3462 | 122.3593 | 122.2151 | 122.2282
4154.7812 | 122.3785 | -0.09613 | 122.2733 | 0.28209 | 0.24794 | 0.23067 | 0.21764 | 0.22854 | 0.30077 | 0.21197 | 122.3304 | 122.21 | 122.2084 | 122.1126 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 0.37822 | 0.34408 | 0.3268 | 0.31377 | 0.32467 | 0.3969 | 0.3081 | 122.3716 | 122.2512 | 122.2496 | 122.1538 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 122.3508 | 122.3638 | 122.2288 | 122.2419
4156.5312 | 122.3877 | -0.086975 | 122.3007 | 0.28667 | 0.24337 | 0.22609 | 0.20391 | 0.21938 | 0.29619 | 0.19824 | 122.3304 | 122.2146 | 122.2038 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.37365 | 0.33034 | 0.31306 | 0.29088 | 0.30636 | 0.38316 | 0.28521 | 122.3716 | 122.2558 | 122.245 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2151 | 122.2327
4158.2344 | 122.4106 | -0.059509 | 122.2412 | 0.28667 | 0.23879 | 0.22609 | 0.21764 | 0.21938 | 0.30077 | 0.21197 | 122.3349 | 122.2146 | 122.2084 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.34618 | 0.2983 | 0.2856 | 0.27715 | 0.27889 | 0.36028 | 0.27148 | 122.3761 | 122.2558 | 122.2496 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3508 | 122.3684 | 122.2243 | 122.2419
4159.9375 | 122.374 | -0.086975 | 122.2687 | 0.28209 | 0.24794 | 0.23067 | 0.21764 | 0.22396 | 0.30535 | 0.21655 | 122.3349 | 122.2146 | 122.2038 | 122.1126 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.36907 | 0.33492 | 0.31764 | 0.30462 | 0.31094 | 0.39232 | 0.30353 | 122.3761 | 122.2558 | 122.245 | 122.1538 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.3508 | 122.3638 | 122.2197 | 122.2327
4161.625 | 122.4747 | -0.068665 | 122.2641 | 0.28209 | 0.23879 | 0.21693 | 0.20849 | 0.22396 | 0.29619 | 0.20739 | 122.3304 | 122.21 | 122.2038 | 122.1172 | -0.011281 | 0.027798 | -0.024328 | 0.001406 | 0.35076 | 0.30745 | 0.2856 | 0.27715 | 0.29263 | 0.36485 | 0.27606 | 122.3716 | 122.2512 | 122.245 | 122.1584 | 0.029918 | 0.068997 | 0.016871 | 0.042605 | 122.3416 | 122.3547 | 122.2151 | 122.2282
4163.3438 | 122.3465 | -0.11444 | 122.3007 | 0.27294 | 0.23879 | 0.22151 | 0.21307 | 0.22396 | 0.30077 | 0.20739 | 122.3349 | 122.2146 | 122.2038 | 122.1217 | -0.006702 | 0.027798 | -0.024328 | 0.005985 | 0.38738 | 0.35323 | 0.33595 | 0.32751 | 0.3384 | 0.41521 | 0.32184 | 122.3761 | 122.2558 | 122.245 | 122.1629 | 0.034497 | 0.068997 | 0.016871 | 0.047184 | 122.3416 | 122.3593 | 122.2105 | 122.2282
4165.0469 | 122.3831 | -0.073242 | 122.2916 | 0.27752 | 0.23879 | 0.22609 | 0.20391 | 0.22396 | 0.29619 | 0.21197 | 122.3349 | 122.2054 | 122.1992 | 122.1126 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.35076 | 0.31203 | 0.29933 | 0.27715 | 0.2972 | 0.36943 | 0.28521 | 122.3761 | 122.2466 | 122.2404 | 122.1538 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.3554 | 122.3684 | 122.2197 | 122.2327
4166.75 | 122.3511 | -0.10071 | 122.2916 | 0.28667 | 0.23879 | 0.22609 | 0.20849 | 0.22396 | 0.29619 | 0.21655 | 122.3395 | 122.2146 | 122.2038 | 122.1172 | -0.011281 | 0.032376 | -0.033484 | 0.010563 | 0.38738 | 0.33949 | 0.3268 | 0.30919 | 0.32467 | 0.3969 | 0.31726 | 122.3807 | 122.2558 | 122.245 | 122.1584 | 0.029918 | 0.073575 | 0.007715 | 0.051762 | 122.3508 | 122.373 | 122.2151 | 122.2373
4168.4375 | 122.4609 | -0.032043 | 122.2504 | 0.27752 | 0.24337 | 0.22151 | 0.20391 | 0.22396 | 0.29619 | 0.21197 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.30956 | 0.27541 | 0.25355 | 0.23595 | 0.256 | 0.32823 | 0.24402 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4170.1406 | 122.4655 | -0.054932 | 122.2366 | 0.28667 | 0.25252 | 0.23525 | 0.21307 | 0.22854 | 0.29619 | 0.21655 | 122.3304 | 122.2146 | 122.1992 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.3416 | 0.30746 | 0.29018 | 0.268 | 0.28347 | 0.35112 | 0.27148 | 122.3716 | 122.2558 | 122.2404 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.3416 | 122.3593 | 122.2105 | 122.2282
4171.8438 | 122.3328 | -0.09613 | 122.2824 | 0.28209 | 0.25252 | 0.23067 | 0.20849 | 0.21938 | 0.30077 | 0.21655 | 122.3304 | 122.21 | 122.2038 | 122.1126 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.37822 | 0.34865 | 0.3268 | 0.30462 | 0.31551 | 0.3969 | 0.31268 | 122.3716 | 122.2512 | 122.245 | 122.1538 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2197 | 122.2327
4173.5938 | 122.3602 | -0.10529 | 122.2778 | 0.28667 | 0.24794 | 0.22609 | 0.21764 | 0.22396 | 0.30535 | 0.22571 | 122.3349 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.39196 | 0.35323 | 0.33137 | 0.32293 | 0.32925 | 0.41063 | 0.33099 | 122.3761 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4175.2969 | 122.3557 | -0.082397 | 122.287 | 0.28209 | 0.24794 | 0.22609 | 0.21764 | 0.22854 | 0.29619 | 0.21655 | 122.3304 | 122.2146 | 122.2038 | 122.1172 | -0.002124 | 0.027798 | -0.028906 | -0.003172 | 0.36449 | 0.33034 | 0.30849 | 0.30004 | 0.31094 | 0.37859 | 0.29895 | 122.3716 | 122.2558 | 122.245 | 122.1584 | 0.039075 | 0.068997 | 0.012293 | 0.038027 | 122.3325 | 122.3593 | 122.2059 | 122.2327
4177.0625 | 122.3831 | -0.10071 | 122.2641 | 0.28209 | 0.24794 | 0.23525 | 0.2268 | 0.22396 | 0.29619 | 0.22113 | 122.3212 | 122.2146 | 122.1992 | 122.1172 | -0.015859 | 0.02322 | -0.038063 | -0.003172 | 0.3828 | 0.34865 | 0.33595 | 0.32751 | 0.32467 | 0.3969 | 0.32184 | 122.3624 | 122.2558 | 122.2404 | 122.1584 | 0.02534 | 0.064419 | 0.003136 | 0.038027 | 122.3371 | 122.3593 | 122.2151 | 122.2373
4178.7656 | 122.4197 | -0.068665 | 122.2595 | 0.29125 | 0.24794 | 0.23067 | 0.21307 | 0.22854 | 0.30077 | 0.21655 | 122.3304 | 122.2054 | 122.2038 | 122.108 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.35992 | 0.31661 | 0.29933 | 0.28173 | 0.2972 | 0.36943 | 0.28522 | 122.3716 | 122.2466 | 122.245 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2197 | 122.2327
4180.4688 | 122.438 | -0.064087 | 122.2687 | 0.28667 | 0.24794 | 0.23525 | 0.21764 | 0.22854 | 0.30535 | 0.21197 | 122.3304 | 122.2054 | 122.2084 | 122.108 | -0.015859 | 0.027798 | -0.028906 | 0.001406 | 0.35076 | 0.31203 | 0.29933 | 0.28173 | 0.29263 | 0.36943 | 0.27606 | 122.3716 | 122.2466 | 122.2496 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2243 | 122.2373
4182.1875 | 122.4518 | -0.036621 | 122.2504 | 0.29125 | 0.24337 | 0.23525 | 0.22222 | 0.22396 | 0.30077 | 0.22571 | 122.3349 | 122.21 | 122.2038 | 122.108 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.32787 | 0.27999 | 0.27187 | 0.25884 | 0.26058 | 0.33739 | 0.26233 | 122.3761 | 122.2512 | 122.245 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.3462 | 122.3638 | 122.2151 | 122.2327
4183.8906 | 122.3419 | -0.10529 | 122.3007 | 0.30041 | 0.25252 | 0.23067 | 0.23138 | 0.23769 | 0.3145 | 0.22571 | 122.3395 | 122.2054 | 122.2038 | 122.1172 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.40569 | 0.35781 | 0.33595 | 0.33666 | 0.34298 | 0.41979 | 0.33099 | 122.3807 | 122.2466 | 122.245 | 122.1584 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.3508 | 122.373 | 122.2151 | 122.2373
4185.625 | 122.4335 | -0.059509 | 122.2504 | 0.30041 | 0.25252 | 0.2444 | 0.23596 | 0.24227 | 0.30992 | 0.23029 | 122.3349 | 122.21 | 122.2038 | 122.1172 | -0.020437 | 0.02322 | -0.033484 | 0.001406 | 0.35992 | 0.31203 | 0.30391 | 0.29547 | 0.30178 | 0.36943 | 0.28979 | 122.3761 | 122.2512 | 122.245 | 122.1584 | 0.020762 | 0.064419 | 0.007715 | 0.042605 | 122.3554 | 122.3684 | 122.2243 | 122.2373
4187.3281 | 122.3282 | -0.10071 | 122.2824 | 0.29125 | 0.26168 | 0.23525 | 0.22222 | 0.23769 | 0.30992 | 0.22571 | 122.3349 | 122.2192 | 122.2038 | 122.1126 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.39196 | 0.36239 | 0.33595 | 0.32293 | 0.3384 | 0.41063 | 0.32642 | 122.3761 | 122.2604 | 122.245 | 122.1538 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4189.0781 | 122.4564 | -0.050354 | 122.2046 | 0.34619 | 0.26168 | 0.23525 | 0.2268 | 0.23312 | 0.30535 | 0.22571 | 122.3349 | 122.21 | 122.2038 | 122.1126 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.39655 | 0.31204 | 0.2856 | 0.27715 | 0.28347 | 0.3557 | 0.27606 | 122.3761 | 122.2512 | 122.245 | 122.1538 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4190.7969 | 122.4152 | -0.064087 | 122.2549 | 0.35077 | 0.2571 | 0.25356 | 0.24054 | 0.24227 | 0.31908 | 0.23486 | 122.3258 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.41486 | 0.32119 | 0.31765 | 0.30462 | 0.30636 | 0.38317 | 0.29895 | 122.367 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.3371 | 122.3547 | 122.2151 | 122.2327
4192.5469 | 122.4609 | -0.045776 | 122.2229 | 0.34161 | 0.26168 | 0.24898 | 0.23596 | 0.24227 | 0.3145 | 0.23029 | 122.3304 | 122.2054 | 122.2038 | 122.108 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.38739 | 0.30746 | 0.29476 | 0.28173 | 0.28805 | 0.36028 | 0.27606 | 122.3716 | 122.2466 | 122.245 | 122.1492 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.3416 | 122.3684 | 122.2151 | 122.2419
4194.25 | 122.3511 | -0.11444 | 122.287 | 0.34619 | 0.26168 | 0.2444 | 0.2268 | 0.24227 | 0.32366 | 0.22571 | 122.3304 | 122.21 | 122.213 | 122.1172 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.46063 | 0.37612 | 0.35884 | 0.34124 | 0.35671 | 0.4381 | 0.34015 | 122.3716 | 122.2512 | 122.2542 | 122.1584 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2243 | 122.2465
4195.9375 | 122.4335 | -0.050354 | 122.2549 | 0.34161 | 0.25252 | 0.24898 | 0.23596 | 0.24227 | 0.31908 | 0.22571 | 122.3304 | 122.21 | 122.1992 | 122.1126 | -0.006702 | 0.02322 | -0.033484 | -0.003172 | 0.39197 | 0.30288 | 0.29934 | 0.28631 | 0.29263 | 0.36944 | 0.27606 | 122.3716 | 122.2512 | 122.2404 | 122.1538 | 0.034497 | 0.064419 | 0.007715 | 0.038027 | 122.3371 | 122.3638 | 122.2059 | 122.2327
4197.6562 | 122.374 | -0.082397 | 122.2549 | 0.34619 | 0.26626 | 0.24898 | 0.23138 | 0.24227 | 0.31908 | 0.22113 | 122.3349 | 122.2146 | 122.2038 | 122.1126 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.42859 | 0.34866 | 0.33138 | 0.31378 | 0.32467 | 0.40148 | 0.30353 | 122.3761 | 122.2558 | 122.245 | 122.1538 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.3416 | 122.3684 | 122.2105 | 122.2373
4199.3594 | 122.4747 | -0.054932 | 122.2275 | 0.34161 | 0.26168 | 0.24898 | 0.23138 | 0.25143 | 0.32824 | 0.23029 | 122.3304 | 122.2054 | 122.2038 | 122.1034 | -0.020437 | 0.027798 | -0.028906 | 0.005985 | 0.39655 | 0.31661 | 0.30391 | 0.28631 | 0.30636 | 0.38317 | 0.28522 | 122.3716 | 122.2466 | 122.245 | 122.1446 | 0.020762 | 0.068997 | 0.012293 | 0.047184 | 122.3508 | 122.3593 | 122.2243 | 122.2327
4201.0781 | 122.4243 | -0.050354 | 122.2412 | 0.33703 | 0.2571 | 0.25356 | 0.23138 | 0.23769 | 0.3145 | 0.22571 | 122.3304 | 122.2192 | 122.2084 | 122.1126 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.38739 | 0.30746 | 0.30391 | 0.28173 | 0.28805 | 0.36486 | 0.27606 | 122.3716 | 122.2604 | 122.2496 | 122.1538 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.3416 | 122.3638 | 122.2197 | 122.2419
4202.7812 | 122.3969 | -0.091553 | 122.2549 | 0.34619 | 0.26626 | 0.25356 | 0.24511 | 0.25601 | 0.32366 | 0.23486 | 122.3395 | 122.21 | 122.1992 | 122.1217 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.43774 | 0.35781 | 0.34511 | 0.33667 | 0.34756 | 0.41521 | 0.32642 | 122.3807 | 122.2512 | 122.2404 | 122.1629 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3508 | 122.373 | 122.2105 | 122.2327
4204.4688 | 122.4243 | -0.059509 | 122.2641 | 0.35535 | 0.27084 | 0.25814 | 0.25427 | 0.25143 | 0.32824 | 0.23029 | 122.3304 | 122.2054 | 122.2038 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.41486 | 0.33035 | 0.31765 | 0.31378 | 0.31094 | 0.38775 | 0.28979 | 122.3716 | 122.2466 | 122.245 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.3462 | 122.3593 | 122.2197 | 122.2327
4206.1875 | 122.3465 | -0.10986 | 122.2961 | 0.35993 | 0.27542 | 0.27187 | 0.24969 | 0.25143 | 0.33739 | 0.23486 | 122.3349 | 122.2054 | 122.1992 | 122.1217 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.46979 | 0.38528 | 0.38174 | 0.35956 | 0.36129 | 0.44726 | 0.34473 | 122.3761 | 122.2466 | 122.2404 | 122.1629 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3462 | 122.3684 | 122.2105 | 122.2327
4207.8906 | 122.4518 | -0.050354 | 122.2229 | 0.35993 | 0.28458 | 0.26272 | 0.25885 | 0.25601 | 0.34655 | 0.24402 | 122.3349 | 122.2054 | 122.2038 | 122.1126 | -0.011281 | 0.032376 | -0.024328 | 0.001406 | 0.41028 | 0.33493 | 0.31307 | 0.3092 | 0.30636 | 0.39691 | 0.29437 | 122.3761 | 122.2466 | 122.245 | 122.1538 | 0.029918 | 0.073575 | 0.016871 | 0.042605 | 122.3462 | 122.3593 | 122.2151 | 122.2282
4209.6406 | 122.3465 | -0.10529 | 122.3053 | 0.36908 | 0.28915 | 0.26272 | 0.26343 | 0.26059 | 0.34655 | 0.25318 | 122.3349 | 122.21 | 122.2084 | 122.1217 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.47437 | 0.39444 | 0.368 | 0.36871 | 0.36587 | 0.45184 | 0.35846 | 122.3761 | 122.2512 | 122.2496 | 122.1629 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2243 | 122.2419
4211.3438 | 122.3373 | -0.091553 | 122.2595 | 0.37366 | 0.28458 | 0.27187 | 0.26343 | 0.27432 | 0.34655 | 0.24402 | 122.3349 | 122.2146 | 122.2038 | 122.108 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.46521 | 0.37613 | 0.36343 | 0.35498 | 0.36587 | 0.4381 | 0.33557 | 122.3761 | 122.2558 | 122.245 | 122.1492 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.3508 | 122.3684 | 122.2197 | 122.2373
4213.0469 | 122.3419 | -0.086975 | 122.3053 | 0.37366 | 0.28915 | 0.27645 | 0.25885 | 0.26974 | 0.34197 | 0.25318 | 122.3258 | 122.2054 | 122.1992 | 122.1126 | -0.006702 | 0.02322 | -0.028906 | 0.001406 | 0.46064 | 0.37613 | 0.36343 | 0.34583 | 0.35672 | 0.42895 | 0.34015 | 122.367 | 122.2466 | 122.2404 | 122.1538 | 0.034497 | 0.064419 | 0.012293 | 0.042605 | 122.3325 | 122.3547 | 122.2059 | 122.2282
4214.7344 | 122.4335 | -0.054932 | 122.2412 | 0.36908 | 0.28458 | 0.27187 | 0.25427 | 0.27432 | 0.35113 | 0.25776 | 122.3304 | 122.21 | 122.2084 | 122.108 | -0.015859 | 0.027798 | -0.028906 | 0.005985 | 0.42402 | 0.33951 | 0.32681 | 0.3092 | 0.32925 | 0.40606 | 0.31269 | 122.3716 | 122.2512 | 122.2496 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.047184 | 122.3462 | 122.3593 | 122.2243 | 122.2373
4216.4375 | 122.3465 | -0.09613 | 122.2778 | 0.37366 | 0.29831 | 0.27645 | 0.26343 | 0.2789 | 0.35571 | 0.25776 | 122.3349 | 122.21 | 122.2084 | 122.1126 | -0.006702 | 0.02322 | -0.028906 | 0.005985 | 0.46979 | 0.39444 | 0.37258 | 0.35956 | 0.37503 | 0.45184 | 0.35389 | 122.3761 | 122.2512 | 122.2496 | 122.1538 | 0.034497 | 0.064419 | 0.012293 | 0.047184 | 122.3416 | 122.3638 | 122.2151 | 122.2373
4218.1406 | 122.4243 | -0.050354 | 122.2412 | 0.37366 | 0.29373 | 0.28103 | 0.26801 | 0.28347 | 0.35571 | 0.25318 | 122.3304 | 122.21 | 122.2038 | 122.1034 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.42402 | 0.34409 | 0.33138 | 0.31836 | 0.33383 | 0.40606 | 0.30353 | 122.3716 | 122.2512 | 122.245 | 122.1446 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.3462 | 122.3638 | 122.2197 | 122.2373
4219.8281 | 122.3602 | -0.10986 | 122.287 | 0.38282 | 0.29373 | 0.28561 | 0.27259 | 0.28347 | 0.36029 | 0.27149 | 122.3258 | 122.21 | 122.1992 | 122.1172 | -0.015859 | 0.032376 | -0.038063 | -0.003172 | 0.49268 | 0.4036 | 0.39547 | 0.38245 | 0.39334 | 0.47015 | 0.38135 | 122.367 | 122.2512 | 122.2404 | 122.1584 | 0.02534 | 0.073575 | 0.003136 | 0.038027 | 122.3416 | 122.3638 | 122.2151 | 122.2373
4221.5781 | 122.3465 | -0.10071 | 122.2641 | 0.38282 | 0.29831 | 0.28561 | 0.26801 | 0.28347 | 0.36029 | 0.26691 | 122.3304 | 122.2009 | 122.1947 | 122.108 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.48353 | 0.39902 | 0.38632 | 0.36872 | 0.38418 | 0.46099 | 0.36762 | 122.3716 | 122.2421 | 122.2359 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.3416 | 122.3638 | 122.2059 | 122.2282
4223.2812 | 122.3602 | -0.082397 | 122.2595 | 0.3874 | 0.28915 | 0.29477 | 0.28174 | 0.29721 | 0.36486 | 0.26233 | 122.3395 | 122.21 | 122.1947 | 122.1126 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.4698 | 0.37155 | 0.37716 | 0.36414 | 0.37961 | 0.44726 | 0.34473 | 122.3807 | 122.2512 | 122.2359 | 122.1538 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.3508 | 122.373 | 122.2059 | 122.2282
4224.9844 | 122.4518 | -0.059509 | 122.2687 | 0.3874 | 0.29373 | 0.29477 | 0.28632 | 0.29721 | 0.36029 | 0.27149 | 122.3349 | 122.2054 | 122.1992 | 122.108 | -0.015859 | 0.032376 | -0.028906 | 0.001406 | 0.44691 | 0.35324 | 0.35428 | 0.34583 | 0.35672 | 0.41979 | 0.331 | 122.3761 | 122.2466 | 122.2404 | 122.1492 | 0.02534 | 0.073575 | 0.012293 | 0.042605 | 122.3508 | 122.3638 | 122.2151 | 122.2282
4226.6875 | 122.4152 | -0.050354 | 122.2733 | 0.3874 | 0.29373 | 0.29477 | 0.27716 | 0.28347 | 0.37402 | 0.27607 | 122.3304 | 122.2146 | 122.1992 | 122.1172 | -0.006702 | 0.018642 | -0.024328 | 0.001406 | 0.43775 | 0.34409 | 0.34512 | 0.32752 | 0.33383 | 0.42438 | 0.32642 | 122.3716 | 122.2558 | 122.2404 | 122.1584 | 0.034497 | 0.059841 | 0.016871 | 0.042605 | 122.3371 | 122.3547 | 122.2059 | 122.2236
4228.3906 | 122.3831 | -0.082397 | 122.2412 | 0.39198 | 0.28458 | 0.29477 | 0.28632 | 0.29263 | 0.37402 | 0.27607 | 122.3304 | 122.2146 | 122.1992 | 122.108 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.47437 | 0.36697 | 0.37716 | 0.36872 | 0.37503 | 0.45642 | 0.35846 | 122.3716 | 122.2558 | 122.2404 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.3416 | 122.3593 | 122.2105 | 122.2282
4230.0938 | 122.4197 | -0.059509 | 122.2321 | 0.3874 | 0.29373 | 0.29019 | 0.2909 | 0.28805 | 0.36944 | 0.27607 | 122.3349 | 122.2146 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.44691 | 0.35324 | 0.3497 | 0.35041 | 0.34756 | 0.42895 | 0.33558 | 122.3761 | 122.2558 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.3508 | 122.3684 | 122.2105 | 122.2282
4231.7969 | 122.3282 | -0.09613 | 122.2916 | 0.3874 | 0.28 | 0.28561 | 0.27716 | 0.28347 | 0.36944 | 0.27149 | 122.3349 | 122.21 | 122.2038 | 122.108 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.48353 | 0.37613 | 0.38174 | 0.37329 | 0.3796 | 0.46557 | 0.36762 | 122.3761 | 122.2512 | 122.245 | 122.1492 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.3462 | 122.3684 | 122.2151 | 122.2373
4233.5 | 122.4564 | -0.041199 | 122.2275 | 0.37824 | 0.28 | 0.28103 | 0.27259 | 0.28347 | 0.36486 | 0.26233 | 122.3212 | 122.21 | 122.2038 | 122.108 | -0.020437 | 0.027798 | -0.033484 | 0.005985 | 0.41944 | 0.3212 | 0.32223 | 0.31378 | 0.32467 | 0.40606 | 0.30353 | 122.3624 | 122.2512 | 122.245 | 122.1492 | 0.020762 | 0.068997 | 0.007715 | 0.047184 | 122.3416 | 122.3547 | 122.2243 | 122.2373
4235.2188 | 122.4289 | -0.036621 | 122.2137 | 0.37366 | 0.26626 | 0.27187 | 0.26801 | 0.26974 | 0.34197 | 0.26233 | 122.3349 | 122.2054 | 122.1947 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.005985 | 0.41028 | 0.30288 | 0.3085 | 0.30463 | 0.30636 | 0.37859 | 0.29895 | 122.3761 | 122.2466 | 122.2359 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.047184 | 122.3508 | 122.3638 | 122.2105 | 122.2236
4236.9219 | 122.3419 | -0.12817 | 122.2778 | 0.37824 | 0.28 | 0.28103 | 0.27259 | 0.28347 | 0.36029 | 0.26691 | 122.3441 | 122.2146 | 122.2038 | 122.1126 | -0.006702 | 0.027798 | -0.024328 | -0.003172 | 0.50642 | 0.40817 | 0.4092 | 0.40076 | 0.41165 | 0.48846 | 0.39509 | 122.3853 | 122.2558 | 122.245 | 122.1538 | 0.034497 | 0.068997 | 0.016871 | 0.038027 | 122.3508 | 122.3684 | 122.2105 | 122.2282
4238.625 | 122.4426 | -0.045776 | 122.2183 | 0.37824 | 0.27542 | 0.28103 | 0.26801 | 0.28347 | 0.36029 | 0.26233 | 122.3304 | 122.2054 | 122.2038 | 122.1126 | -0.011281 | 0.027798 | -0.033484 | 0.005985 | 0.42402 | 0.32119 | 0.32681 | 0.31378 | 0.32925 | 0.40606 | 0.30811 | 122.3716 | 122.2466 | 122.245 | 122.1538 | 0.029918 | 0.068997 | 0.007715 | 0.047184 | 122.3416 | 122.3638 | 122.2151 | 122.2373
4240.3438 | 122.3419 | -0.11444 | 122.2778 | 0.37366 | 0.28458 | 0.28561 | 0.27716 | 0.2789 | 0.36486 | 0.26233 | 122.3349 | 122.2146 | 122.2038 | 122.1126 | -0.011281 | 0.018642 | -0.028906 | 0.010563 | 0.4881 | 0.39902 | 0.40005 | 0.39161 | 0.39334 | 0.47931 | 0.37677 | 122.3761 | 122.2558 | 122.245 | 122.1538 | 0.029918 | 0.059841 | 0.012293 | 0.051762 | 122.3462 | 122.3638 | 122.2151 | 122.2327
4242.0469 | 122.3831 | -0.10529 | 122.2778 | 0.38282 | 0.28 | 0.28561 | 0.27259 | 0.28805 | 0.36486 | 0.27149 | 122.3304 | 122.2054 | 122.2038 | 122.108 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.48811 | 0.38528 | 0.3909 | 0.37787 | 0.39334 | 0.47015 | 0.37677 | 122.3716 | 122.2466 | 122.245 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.3416 | 122.3593 | 122.2151 | 122.2327
4243.7656 | 122.3923 | -0.082397 | 122.2641 | 0.37366 | 0.27542 | 0.27645 | 0.26343 | 0.2789 | 0.36029 | 0.26691 | 122.2708 | 122.21 | 122.2038 | 122.1172 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.45606 | 0.35781 | 0.35885 | 0.34582 | 0.36129 | 0.44268 | 0.34931 | 122.312 | 122.2512 | 122.245 | 122.1584 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.2775 | 122.3043 | 122.2105 | 122.2373
4245.4531 | 122.3557 | -0.10986 | 122.2916 | 0.37824 | 0.28 | 0.27645 | 0.27259 | 0.2789 | 0.36029 | 0.26233 | 122.2754 | 122.2054 | 122.1947 | 122.1034 | -0.011281 | 0.02322 | -0.038063 | 0.001406 | 0.4881 | 0.38986 | 0.38631 | 0.38245 | 0.38876 | 0.47015 | 0.3722 | 122.3166 | 122.2466 | 122.2359 | 122.1446 | 0.029918 | 0.064419 | 0.003136 | 0.042605 | 122.2867 | 122.3135 | 122.2059 | 122.2327
4247.1562 | 122.374 | -0.086975 | 122.2733 | 0.3874 | 0.27542 | 0.28561 | 0.27259 | 0.28347 | 0.35571 | 0.26233 | 122.2754 | 122.2192 | 122.1947 | 122.108 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.47437 | 0.36239 | 0.37258 | 0.35956 | 0.37045 | 0.44268 | 0.34931 | 122.3166 | 122.2604 | 122.2359 | 122.1492 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2867 | 122.3089 | 122.2059 | 122.2282
4248.875 | 122.4243 | -0.068665 | 122.2504 | 0.37366 | 0.28 | 0.28103 | 0.27716 | 0.2789 | 0.35113 | 0.26691 | 122.28 | 122.2009 | 122.1992 | 122.1172 | -0.011281 | 0.027798 | -0.019749 | 0.005985 | 0.44233 | 0.34866 | 0.3497 | 0.34583 | 0.34756 | 0.41979 | 0.33558 | 122.3212 | 122.2421 | 122.2404 | 122.1584 | 0.029918 | 0.068997 | 0.02145 | 0.047184 | 122.2913 | 122.2997 | 122.2105 | 122.219
4250.625 | 122.4747 | -0.059509 | 122.1909 | 0.38282 | 0.27084 | 0.28103 | 0.27259 | 0.2789 | 0.36029 | 0.26233 | 122.2754 | 122.21 | 122.2038 | 122.1126 | -0.015859 | 0.018642 | -0.038063 | 0.001406 | 0.44233 | 0.33035 | 0.34054 | 0.33209 | 0.33841 | 0.41979 | 0.32184 | 122.3166 | 122.2512 | 122.245 | 122.1538 | 0.02534 | 0.059841 | 0.003136 | 0.042605 | 122.2913 | 122.3135 | 122.2197 | 122.2419
4252.3281 | 122.3694 | -0.086975 | 122.2641 | 0.3874 | 0.29373 | 0.29477 | 0.27716 | 0.28805 | 0.35571 | 0.27149 | 122.2663 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.47437 | 0.38071 | 0.38174 | 0.36414 | 0.37503 | 0.44268 | 0.35846 | 122.3075 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2775 | 122.2997 | 122.2151 | 122.2373
4254.0312 | 122.4152 | -0.059509 | 122.2412 | 0.37366 | 0.28915 | 0.28561 | 0.27259 | 0.2789 | 0.36029 | 0.26691 | 122.2754 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.018642 | -0.028906 | 0.005985 | 0.43317 | 0.34866 | 0.34512 | 0.33209 | 0.33841 | 0.41979 | 0.32642 | 122.3166 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.059841 | 0.012293 | 0.047184 | 122.2913 | 122.3043 | 122.2151 | 122.2282
4255.7188 | 122.3282 | -0.11902 | 122.2961 | 0.39655 | 0.29831 | 0.30392 | 0.2909 | 0.30179 | 0.3786 | 0.28065 | 122.2754 | 122.2146 | 122.1992 | 122.1126 | -0.020437 | 0.027798 | -0.038063 | -0.003172 | 0.51557 | 0.41733 | 0.42294 | 0.40992 | 0.4208 | 0.49762 | 0.39966 | 122.3166 | 122.2558 | 122.2404 | 122.1538 | 0.020762 | 0.068997 | 0.003136 | 0.038027 | 122.2959 | 122.3135 | 122.2197 | 122.2373
4257.4531 | 122.3557 | -0.10529 | 122.2504 | 0.40571 | 0.30289 | 0.29477 | 0.30006 | 0.30179 | 0.37402 | 0.28522 | 122.28 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.014064 | -0.028906 | 0.001406 | 0.511 | 0.40818 | 0.40005 | 0.40534 | 0.40707 | 0.47931 | 0.39051 | 122.3212 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.055263 | 0.012293 | 0.042605 | 122.2913 | 122.3089 | 122.2151 | 122.2327
4259.1406 | 122.4152 | -0.073242 | 122.2458 | 0.41029 | 0.30747 | 0.32224 | 0.30006 | 0.31094 | 0.39233 | 0.2898 | 122.2708 | 122.2054 | 122.2038 | 122.1126 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.48353 | 0.38071 | 0.39548 | 0.3733 | 0.38418 | 0.46558 | 0.36304 | 122.312 | 122.2466 | 122.245 | 122.1538 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.2775 | 122.2997 | 122.2105 | 122.2327
4260.8594 | 122.4106 | -0.064087 | 122.2458 | 0.40571 | 0.30747 | 0.3085 | 0.29548 | 0.30636 | 0.38776 | 0.29438 | 122.2754 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.4698 | 0.37156 | 0.37259 | 0.35957 | 0.37045 | 0.45184 | 0.35847 | 122.3166 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.2867 | 122.3043 | 122.2105 | 122.2282
4262.6094 | 122.4655 | -0.041199 | 122.2321 | 0.41029 | 0.30747 | 0.31766 | 0.30463 | 0.3201 | 0.39233 | 0.29896 | 122.2708 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 0.45149 | 0.34867 | 0.35886 | 0.34583 | 0.3613 | 0.43353 | 0.34016 | 122.312 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 122.2821 | 122.3089 | 122.2105 | 122.2373
4264.2969 | 122.374 | -0.10071 | 122.2687 | 0.41945 | 0.31205 | 0.32682 | 0.30921 | 0.32468 | 0.39691 | 0.29438 | 122.2754 | 122.2009 | 122.1992 | 122.1172 | -0.011281 | 0.02322 | -0.028906 | 0.001406 | 0.52015 | 0.41276 | 0.42753 | 0.40992 | 0.42538 | 0.49762 | 0.39509 | 122.3166 | 122.2421 | 122.2404 | 122.1584 | 0.029918 | 0.064419 | 0.012293 | 0.042605 | 122.2867 | 122.3043 | 122.2105 | 122.2282
4266 | 122.4609 | -0.050354 | 122.2229 | 0.41487 | 0.31205 | 0.31308 | 0.31379 | 0.31552 | 0.39233 | 0.2898 | 122.2708 | 122.2054 | 122.2038 | 122.108 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.46522 | 0.3624 | 0.36344 | 0.36415 | 0.36587 | 0.44269 | 0.34016 | 122.312 | 122.2466 | 122.245 | 122.1492 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2867 | 122.2997 | 122.2197 | 122.2327
4267.7031 | 122.3877 | -0.10071 | 122.2687 | 0.41945 | 0.32578 | 0.32682 | 0.31379 | 0.32925 | 0.40149 | 0.30812 | 122.2754 | 122.21 | 122.2038 | 122.108 | -0.006702 | 0.036954 | -0.033484 | 0.001406 | 0.52015 | 0.42649 | 0.42753 | 0.4145 | 0.42996 | 0.5022 | 0.40882 | 122.3166 | 122.2512 | 122.245 | 122.1492 | 0.034497 | 0.078153 | 0.007715 | 0.042605 | 122.2821 | 122.3089 | 122.2105 | 122.2373
4269.3906 | 122.4472 | -0.059509 | 122.2504 | 0.41487 | 0.30289 | 0.31766 | 0.30921 | 0.30636 | 0.39233 | 0.29896 | 122.2754 | 122.2054 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.47438 | 0.3624 | 0.37717 | 0.36872 | 0.36587 | 0.45184 | 0.35847 | 122.3166 | 122.2466 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.2867 | 122.3089 | 122.2059 | 122.2282
4271.0938 | 122.3831 | -0.082397 | 122.2504 | 0.41487 | 0.31205 | 0.31766 | 0.31379 | 0.3201 | 0.39691 | 0.29438 | 122.2708 | 122.21 | 122.2084 | 122.108 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 0.49727 | 0.39444 | 0.40006 | 0.39619 | 0.40249 | 0.47931 | 0.37678 | 122.312 | 122.2512 | 122.2496 | 122.1492 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 122.2775 | 122.3043 | 122.2151 | 122.2419
4272.7969 | 122.4747 | -0.054932 | 122.2137 | 0.41029 | 0.31205 | 0.31766 | 0.30463 | 0.3201 | 0.39233 | 0.29438 | 122.2663 | 122.2054 | 122.1947 | 122.108 | -0.011281 | 0.02322 | -0.028906 | 0.005985 | 0.46522 | 0.36698 | 0.37259 | 0.35957 | 0.37503 | 0.44727 | 0.34931 | 122.3075 | 122.2466 | 122.2359 | 122.1492 | 0.029918 | 0.064419 | 0.012293 | 0.047184 | 122.2775 | 122.2952 | 122.2059 | 122.2236
4274.5312 | 122.3923 | -0.086975 | 122.2778 | 0.41945 | 0.32121 | 0.32224 | 0.30463 | 0.3201 | 0.39691 | 0.30354 | 122.2754 | 122.2054 | 122.2038 | 122.1126 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 0.50642 | 0.40818 | 0.40921 | 0.39161 | 0.40707 | 0.48389 | 0.39051 | 122.3166 | 122.2466 | 122.245 | 122.1538 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 122.2821 | 122.3089 | 122.2105 | 122.2373
4276.2344 | 122.4106 | -0.07782 | 122.2229 | 0.42402 | 0.31205 | 0.32682 | 0.31379 | 0.3201 | 0.39691 | 0.29896 | 122.2754 | 122.21 | 122.1947 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 0.50184 | 0.38987 | 0.40464 | 0.39161 | 0.39792 | 0.47473 | 0.37678 | 122.3166 | 122.2512 | 122.2359 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 122.2867 | 122.3043 | 122.2059 | 122.2236
4277.9531 | 122.4518 | -0.064087 | 122.2458 | 0.41945 | 0.32578 | 0.32224 | 0.31837 | 0.3201 | 0.39233 | 0.30812 | 122.28 | 122.2054 | 122.2038 | 122.1126 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 0.48353 | 0.38987 | 0.38633 | 0.38246 | 0.38418 | 0.45642 | 0.3722 | 122.3212 | 122.2466 | 122.245 | 122.1538 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 122.2959 | 122.3135 | 122.2197 | 122.2373
4279.6719 | 122.4564 | -0.054932 | 122.2504 | 0.42402 | 0.31663 | 0.3314 | 0.32295 | 0.32468 | 0.40149 | 0.31269 | 122.2754 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.028906 | 0.010563 | 0.47896 | 0.37156 | 0.38633 | 0.37788 | 0.37961 | 0.45642 | 0.36762 | 122.3166 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.012293 | 0.051762 | 122.2913 | 122.3043 | 122.2105 | 122.2236
4281.3594 | 122.3694 | -0.091553 | 122.2778 | 0.4286 | 0.32578 | 0.34055 | 0.32295 | 0.32925 | 0.41065 | 0.31727 | 122.2754 | 122.21 | 122.2038 | 122.108 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.52016 | 0.41734 | 0.43211 | 0.4145 | 0.42081 | 0.5022 | 0.40882 | 122.3166 | 122.2512 | 122.245 | 122.1492 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.2821 | 122.3043 | 122.2105 | 122.2327
4283.0781 | 122.3785 | -0.064087 | 122.2641 | 0.43318 | 0.33952 | 0.34055 | 0.33211 | 0.34299 | 0.41065 | 0.31269 | 122.2708 | 122.2192 | 122.2038 | 122.108 | -0.002124 | 0.027798 | -0.042641 | 0.010563 | 0.49727 | 0.40361 | 0.40464 | 0.39619 | 0.40708 | 0.47474 | 0.37678 | 122.312 | 122.2604 | 122.245 | 122.1492 | 0.039075 | 0.068997 | -0.001442 | 0.051762 | 122.273 | 122.3135 | 122.2059 | 122.2465
4284.7812 | 122.3557 | -0.10529 | 122.2641 | 0.45149 | 0.35326 | 0.35429 | 0.34126 | 0.35214 | 0.42438 | 0.33558 | 122.28 | 122.21 | 122.1992 | 122.1034 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.55678 | 0.45854 | 0.45958 | 0.44655 | 0.45743 | 0.52967 | 0.44087 | 122.3212 | 122.2512 | 122.2404 | 122.1446 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.2867 | 122.3089 | 122.2059 | 122.2282
4286.4688 | 122.4564 | -0.068665 | 122.2366 | 0.45607 | 0.34868 | 0.35887 | 0.35042 | 0.35672 | 0.42438 | 0.33558 | 122.2708 | 122.2146 | 122.2038 | 122.108 | -0.006702 | 0.027798 | -0.038063 | 0.005985 | 0.52474 | 0.41734 | 0.42753 | 0.41909 | 0.42539 | 0.49305 | 0.40425 | 122.312 | 122.2558 | 122.245 | 122.1492 | 0.034497 | 0.068997 | 0.003136 | 0.047184 | 122.2775 | 122.3089 | 122.2105 | 122.2419
4288.1719 | 122.3419 | -0.10529 | 122.287 | 0.45607 | 0.35326 | 0.35887 | 0.34126 | 0.35214 | 0.42896 | 0.33558 | 122.2754 | 122.2054 | 122.2038 | 122.108 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.56136 | 0.45854 | 0.46415 | 0.44655 | 0.45743 | 0.53425 | 0.44087 | 122.3166 | 122.2466 | 122.245 | 122.1492 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.2867 | 122.2997 | 122.2151 | 122.2282
4289.8906 | 122.4976 | -0.054932 | 122.2412 | 0.43776 | 0.33494 | 0.34971 | 0.33211 | 0.33841 | 0.41523 | 0.32643 | 122.2754 | 122.21 | 122.1855 | 122.108 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.49269 | 0.38987 | 0.40464 | 0.38704 | 0.39334 | 0.47016 | 0.38136 | 122.3166 | 122.2512 | 122.2267 | 122.1492 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2867 | 122.3043 | 122.1968 | 122.2144
4291.6406 | 122.3923 | -0.09613 | 122.2595 | 0.46981 | 0.35784 | 0.37718 | 0.35958 | 0.36588 | 0.45185 | 0.34932 | 122.28 | 122.2146 | 122.1947 | 122.1217 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.56594 | 0.45397 | 0.47331 | 0.45571 | 0.46201 | 0.54798 | 0.44545 | 122.3212 | 122.2558 | 122.2359 | 122.1629 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.2913 | 122.3089 | 122.2059 | 122.2236
4293.3438 | 122.4609 | -0.045776 | 122.2412 | 0.46981 | 0.37157 | 0.3726 | 0.36416 | 0.37046 | 0.44728 | 0.35847 | 122.2754 | 122.2054 | 122.1947 | 122.1172 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.51558 | 0.41735 | 0.41838 | 0.40993 | 0.41623 | 0.49305 | 0.40425 | 122.3166 | 122.2466 | 122.2359 | 122.1584 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2867 | 122.3043 | 122.2059 | 122.2236
4295.0469 | 122.3282 | -0.10529 | 122.2687 | 0.46523 | 0.36699 | 0.3726 | 0.35958 | 0.36588 | 0.4427 | 0.34932 | 122.2754 | 122.21 | 122.1992 | 122.108 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 0.57052 | 0.47228 | 0.47789 | 0.46486 | 0.47116 | 0.54798 | 0.4546 | 122.3166 | 122.2512 | 122.2404 | 122.1492 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 122.2867 | 122.3043 | 122.2105 | 122.2282
4296.7344 | 122.4197 | -0.07782 | 122.2366 | 0.46523 | 0.35784 | 0.3726 | 0.36416 | 0.36588 | 0.44728 | 0.3539 | 122.2708 | 122.1963 | 122.1947 | 122.1126 | -0.015859 | 0.02322 | -0.028906 | 0.001406 | 0.54305 | 0.43566 | 0.45042 | 0.44198 | 0.4437 | 0.5251 | 0.43172 | 122.312 | 122.2375 | 122.2359 | 122.1538 | 0.02534 | 0.064419 | 0.012293 | 0.042605 | 122.2867 | 122.2997 | 122.2105 | 122.2236
4298.4375 | 122.3877 | -0.086975 | 122.2595 | 0.47439 | 0.38073 | 0.38634 | 0.36873 | 0.38419 | 0.45643 | 0.36305 | 122.28 | 122.2054 | 122.1992 | 122.1126 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.56136 | 0.46771 | 0.47331 | 0.45571 | 0.47116 | 0.54341 | 0.45003 | 122.3212 | 122.2466 | 122.2404 | 122.1538 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.2959 | 122.3181 | 122.2151 | 122.2373
4300.1875 | 122.3328 | -0.11444 | 122.2687 | 0.47439 | 0.37157 | 0.38634 | 0.37789 | 0.37961 | 0.45643 | 0.35847 | 122.2754 | 122.21 | 122.213 | 122.1126 | -0.015859 | 0.027798 | -0.033484 | -0.003172 | 0.58883 | 0.48601 | 0.50078 | 0.49233 | 0.49405 | 0.57087 | 0.47292 | 122.3166 | 122.2512 | 122.2542 | 122.1538 | 0.02534 | 0.068997 | 0.007715 | 0.038027 | 122.2913 | 122.3089 | 122.2288 | 122.2465
4301.8906 | 122.4747 | -0.059509 | 122.2229 | 0.47439 | 0.37157 | 0.38176 | 0.36873 | 0.37046 | 0.45185 | 0.35847 | 122.2708 | 122.2054 | 122.1992 | 122.1034 | -0.006702 | 0.02322 | -0.028906 | 0.005985 | 0.5339 | 0.43108 | 0.44127 | 0.42824 | 0.42996 | 0.51136 | 0.41798 | 122.312 | 122.2466 | 122.2404 | 122.1446 | 0.034497 | 0.064419 | 0.012293 | 0.047184 | 122.2775 | 122.2997 | 122.2059 | 122.2282
4303.6406 | 122.3969 | -0.10071 | 122.2504 | 0.48354 | 0.38531 | 0.39092 | 0.37789 | 0.37961 | 0.46559 | 0.36305 | 122.2708 | 122.21 | 122.2084 | 122.1034 | -0.006702 | 0.018642 | -0.028906 | 0.005985 | 0.58425 | 0.48602 | 0.49163 | 0.4786 | 0.48032 | 0.5663 | 0.46376 | 122.312 | 122.2512 | 122.2496 | 122.1446 | 0.034497 | 0.059841 | 0.012293 | 0.047184 | 122.2775 | 122.2997 | 122.2151 | 122.2373
4305.375 | 122.3511 | -0.10071 | 122.2778 | 0.4927 | 0.39447 | 0.3955 | 0.38247 | 0.38877 | 0.47017 | 0.36763 | 122.2708 | 122.2054 | 122.1992 | 122.108 | -0.015859 | 0.02322 | -0.028906 | 0.010563 | 0.59341 | 0.49518 | 0.4962 | 0.48318 | 0.48948 | 0.57088 | 0.46834 | 122.312 | 122.2466 | 122.2404 | 122.1492 | 0.02534 | 0.064419 | 0.012293 | 0.051762 | 122.2867 | 122.2997 | 122.2151 | 122.2282
4307.0781 | 122.4335 | -0.082397 | 122.2275 | 0.48812 | 0.38989 | 0.3955 | 0.37331 | 0.39335 | 0.46559 | 0.36763 | 122.2708 | 122.2054 | 122.1992 | 122.0988 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.57052 | 0.47229 | 0.47789 | 0.45571 | 0.47574 | 0.54799 | 0.45003 | 122.312 | 122.2466 | 122.2404 | 122.14 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.2775 | 122.2997 | 122.2059 | 122.2282
4308.8125 | 122.3877 | -0.073242 | 122.2961 | 0.48354 | 0.37615 | 0.3955 | 0.37789 | 0.38877 | 0.46101 | 0.35847 | 122.2754 | 122.2054 | 122.1992 | 122.1126 | -0.020437 | 0.02322 | -0.033484 | -0.003172 | 0.55679 | 0.44939 | 0.46874 | 0.45113 | 0.46201 | 0.53425 | 0.43172 | 122.3166 | 122.2466 | 122.2404 | 122.1538 | 0.020762 | 0.064419 | 0.007715 | 0.038027 | 122.2959 | 122.3089 | 122.2197 | 122.2327
4310.6094 | 122.3511 | -0.086975 | 122.2733 | 0.48812 | 0.38531 | 0.39092 | 0.37789 | 0.38419 | 0.46101 | 0.36305 | 122.2708 | 122.21 | 122.1992 | 122.1034 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 0.5751 | 0.47228 | 0.47789 | 0.46487 | 0.47116 | 0.54799 | 0.45003 | 122.312 | 122.2512 | 122.2404 | 122.1446 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 122.2775 | 122.3089 | 122.2059 | 122.2373
4312.3906 | 122.3282 | -0.082397 | 122.287 | 0.50186 | 0.38989 | 0.3955 | 0.38705 | 0.39792 | 0.47017 | 0.37679 | 122.2708 | 122.2146 | 122.2038 | 122.1126 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.58425 | 0.47229 | 0.47789 | 0.46945 | 0.48032 | 0.55256 | 0.45918 | 122.312 | 122.2558 | 122.245 | 122.1538 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.2867 | 122.3043 | 122.2197 | 122.2373
4314.125 | 122.3557 | -0.10986 | 122.2824 | 0.51101 | 0.41278 | 0.42297 | 0.40994 | 0.41624 | 0.48848 | 0.39052 | 122.2708 | 122.21 | 122.2038 | 122.108 | -0.011281 | 0.02322 | -0.024328 | 0.001406 | 0.62088 | 0.52265 | 0.53283 | 0.5198 | 0.5261 | 0.59834 | 0.50038 | 122.312 | 122.2512 | 122.245 | 122.1492 | 0.029918 | 0.064419 | 0.016871 | 0.042605 | 122.2821 | 122.2952 | 122.2151 | 122.2282
4315.8906 | 122.438 | -0.059509 | 122.2366 | 0.51101 | 0.41278 | 0.42755 | 0.40994 | 0.41166 | 0.48848 | 0.3951 | 122.2754 | 122.2146 | 122.1947 | 122.1034 | -0.006702 | 0.02322 | -0.028906 | -0.00775 | 0.57052 | 0.47229 | 0.48705 | 0.46945 | 0.47117 | 0.54799 | 0.45461 | 122.3166 | 122.2558 | 122.2359 | 122.1446 | 0.034497 | 0.064419 | 0.012293 | 0.033449 | 122.2821 | 122.3043 | 122.2014 | 122.2236
4317.6562 | 122.3602 | -0.10071 | 122.2824 | 0.51559 | 0.41278 | 0.42755 | 0.40536 | 0.41624 | 0.49306 | 0.39968 | 122.2754 | 122.21 | 122.1947 | 122.1172 | -0.011281 | 0.027798 | -0.028906 | 0.010563 | 0.6163 | 0.51349 | 0.52825 | 0.50607 | 0.51694 | 0.59377 | 0.50039 | 122.3166 | 122.2512 | 122.2359 | 122.1584 | 0.029918 | 0.068997 | 0.012293 | 0.051762 | 122.2867 | 122.3043 | 122.2059 | 122.2236
4319.3594 | 122.4884 | -0.045776 | 122.2366 | 0.51101 | 0.4082 | 0.41381 | 0.40078 | 0.40708 | 0.48848 | 0.39052 | 122.2708 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.55679 | 0.45398 | 0.45959 | 0.44656 | 0.45286 | 0.53426 | 0.4363 | 122.312 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.2821 | 122.2997 | 122.2151 | 122.2327
4321.125 | 122.4289 | -0.073242 | 122.2549 | 0.51559 | 0.4082 | 0.41839 | 0.40994 | 0.41166 | 0.49306 | 0.3951 | 122.2708 | 122.21 | 122.2038 | 122.1126 | -0.011281 | 0.032376 | -0.038063 | 0.001406 | 0.58883 | 0.48145 | 0.49163 | 0.48318 | 0.4849 | 0.5663 | 0.46834 | 122.312 | 122.2512 | 122.245 | 122.1538 | 0.029918 | 0.073575 | 0.003136 | 0.042605 | 122.2821 | 122.3089 | 122.2151 | 122.2419
4322.8125 | 122.3648 | -0.10071 | 122.2687 | 0.52017 | 0.41736 | 0.42755 | 0.42368 | 0.42539 | 0.50222 | 0.40884 | 122.2663 | 122.2146 | 122.1992 | 122.1126 | -0.006702 | 0.02322 | -0.033484 | -0.003172 | 0.62088 | 0.51807 | 0.52825 | 0.52438 | 0.5261 | 0.60292 | 0.50954 | 122.3075 | 122.2558 | 122.2404 | 122.1538 | 0.034497 | 0.064419 | 0.007715 | 0.038027 | 122.273 | 122.2997 | 122.2059 | 122.2327
4324.5781 | 122.3511 | -0.082397 | 122.2778 | 0.52933 | 0.4311 | 0.4367 | 0.42825 | 0.42997 | 0.50222 | 0.40884 | 122.2754 | 122.21 | 122.1992 | 122.108 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.61173 | 0.51349 | 0.5191 | 0.51065 | 0.51237 | 0.58461 | 0.49123 | 122.3166 | 122.2512 | 122.2404 | 122.1492 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 122.2821 | 122.3089 | 122.2059 | 122.2327
4326.3438 | 122.4106 | -0.091553 | 122.2641 | 0.53391 | 0.42194 | 0.4367 | 0.41452 | 0.42539 | 0.50222 | 0.40884 | 122.2754 | 122.21 | 122.1947 | 122.1126 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 0.62546 | 0.51349 | 0.52826 | 0.50607 | 0.51694 | 0.59377 | 0.50039 | 122.3166 | 122.2512 | 122.2359 | 122.1538 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 122.2821 | 122.3135 | 122.2014 | 122.2327
4328.1094 | 122.3328 | -0.10071 | 122.2641 | 0.54764 | 0.44483 | 0.44586 | 0.43741 | 0.4437 | 0.51595 | 0.43173 | 122.2708 | 122.21 | 122.1901 | 122.108 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.64835 | 0.54554 | 0.54657 | 0.53812 | 0.54441 | 0.61666 | 0.53243 | 122.312 | 122.2512 | 122.2313 | 122.1492 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2821 | 122.3043 | 122.2014 | 122.2236
4329.8125 | 122.3282 | -0.10986 | 122.2687 | 0.53848 | 0.42652 | 0.45502 | 0.43283 | 0.43455 | 0.51595 | 0.42715 | 122.2754 | 122.21 | 122.1992 | 122.108 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.64835 | 0.53638 | 0.56488 | 0.5427 | 0.54441 | 0.62581 | 0.53701 | 122.3166 | 122.2512 | 122.2404 | 122.1492 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.2821 | 122.3089 | 122.2059 | 122.2327
4331.5781 | 122.4197 | -0.054932 | 122.2687 | 0.55222 | 0.44483 | 0.45502 | 0.44199 | 0.44828 | 0.52053 | 0.4363 | 122.2663 | 122.2146 | 122.1947 | 122.108 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.60715 | 0.49977 | 0.50995 | 0.49692 | 0.50321 | 0.57546 | 0.49124 | 122.3075 | 122.2558 | 122.2359 | 122.1492 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2775 | 122.2952 | 122.2059 | 122.2236
4333.3281 | 122.4197 | -0.064087 | 122.2549 | 0.53391 | 0.43568 | 0.44586 | 0.42825 | 0.43455 | 0.51137 | 0.41799 | 122.2708 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.59799 | 0.49976 | 0.50995 | 0.49234 | 0.49863 | 0.57546 | 0.48208 | 122.312 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.2867 | 122.3043 | 122.2105 | 122.2282
4335.0938 | 122.3373 | -0.10071 | 122.2778 | 0.54306 | 0.44941 | 0.45502 | 0.44199 | 0.43912 | 0.52053 | 0.42715 | 122.2754 | 122.2054 | 122.1992 | 122.1034 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.64377 | 0.55012 | 0.55573 | 0.5427 | 0.53983 | 0.62124 | 0.52785 | 122.3166 | 122.2466 | 122.2404 | 122.1446 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2867 | 122.3089 | 122.2105 | 122.2327
4336.8125 | 122.4426 | -0.064087 | 122.2412 | 0.56595 | 0.45857 | 0.4596 | 0.45115 | 0.44828 | 0.52511 | 0.44088 | 122.2708 | 122.2009 | 122.1992 | 122.1034 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.63004 | 0.52266 | 0.52368 | 0.51523 | 0.51237 | 0.5892 | 0.50497 | 122.312 | 122.2421 | 122.2404 | 122.1446 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2821 | 122.2997 | 122.2105 | 122.2282
4338.5625 | 122.4564 | -0.059509 | 122.2412 | 0.56595 | 0.46315 | 0.47333 | 0.4603 | 0.46202 | 0.54342 | 0.45004 | 122.2754 | 122.2054 | 122.1901 | 122.1034 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.62546 | 0.52266 | 0.53284 | 0.51981 | 0.52152 | 0.60293 | 0.50955 | 122.3166 | 122.2466 | 122.2313 | 122.1446 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2867 | 122.3089 | 122.2014 | 122.2236
4340.3281 | 122.3785 | -0.10071 | 122.2733 | 0.58885 | 0.48146 | 0.49623 | 0.4832 | 0.48948 | 0.56173 | 0.46377 | 122.2708 | 122.21 | 122.1947 | 122.1034 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.68956 | 0.58217 | 0.59693 | 0.5839 | 0.59019 | 0.66244 | 0.56448 | 122.312 | 122.2512 | 122.2359 | 122.1446 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2821 | 122.3043 | 122.2059 | 122.2282
4342.0938 | 122.4564 | -0.045776 | 122.2321 | 0.57053 | 0.46315 | 0.48249 | 0.46488 | 0.46659 | 0.53426 | 0.45462 | 122.2708 | 122.21 | 122.1901 | 122.108 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.61631 | 0.50892 | 0.52826 | 0.51066 | 0.51237 | 0.58004 | 0.50039 | 122.312 | 122.2512 | 122.2313 | 122.1492 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.2867 | 122.2997 | 122.2059 | 122.219
4343.7969 | 122.4701 | -0.054932 | 122.2321 | 0.57511 | 0.47231 | 0.47791 | 0.46488 | 0.47117 | 0.54342 | 0.45462 | 122.2754 | 122.2146 | 122.1992 | 122.108 | -0.015859 | 0.036954 | -0.019749 | -0.003172 | 0.63004 | 0.52724 | 0.53284 | 0.51981 | 0.5261 | 0.59835 | 0.50955 | 122.3166 | 122.2558 | 122.2404 | 122.1492 | 0.02534 | 0.078153 | 0.02145 | 0.038027 | 122.2913 | 122.2952 | 122.2151 | 122.219
4345.5625 | 122.3236 | -0.10986 | 122.2916 | 0.56138 | 0.45399 | 0.46418 | 0.45115 | 0.45286 | 0.52511 | 0.44546 | 122.2754 | 122.2009 | 122.1992 | 122.1126 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 0.67124 | 0.56385 | 0.57404 | 0.56101 | 0.56272 | 0.63497 | 0.55532 | 122.3166 | 122.2421 | 122.2404 | 122.1538 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 122.2867 | 122.3043 | 122.2105 | 122.2282
4347.3281 | 122.3328 | -0.091553 | 122.2687 | 0.54306 | 0.44483 | 0.44586 | 0.43283 | 0.43455 | 0.51137 | 0.41799 | 122.2754 | 122.2054 | 122.2084 | 122.1126 | -0.015859 | 0.032376 | -0.033484 | 0.001406 | 0.63462 | 0.53639 | 0.53741 | 0.52439 | 0.5261 | 0.60293 | 0.50954 | 122.3166 | 122.2466 | 122.2496 | 122.1538 | 0.02534 | 0.073575 | 0.007715 | 0.042605 | 122.2913 | 122.3089 | 122.2243 | 122.2419
4349.0312 | 122.3877 | -0.10529 | 122.2824 | 0.54764 | 0.44026 | 0.45502 | 0.43741 | 0.42997 | 0.51137 | 0.43173 | 122.28 | 122.2009 | 122.1992 | 122.1126 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 0.65293 | 0.54554 | 0.5603 | 0.5427 | 0.53526 | 0.61666 | 0.53701 | 122.3212 | 122.2421 | 122.2404 | 122.1538 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 122.2867 | 122.3135 | 122.2059 | 122.2327
4350.7969 | 122.3557 | -0.082397 | 122.2549 | 0.54764 | 0.43568 | 0.45502 | 0.44199 | 0.43455 | 0.50679 | 0.42715 | 122.2708 | 122.1963 | 122.1947 | 122.1034 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.63004 | 0.51807 | 0.53741 | 0.52439 | 0.51694 | 0.58919 | 0.50954 | 122.312 | 122.2375 | 122.2359 | 122.1446 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.2821 | 122.2997 | 122.2059 | 122.2236
4352.5781 | 122.3373 | -0.10529 | 122.2733 | 0.54764 | 0.44941 | 0.46418 | 0.44199 | 0.43455 | 0.51137 | 0.4363 | 122.2663 | 122.2054 | 122.1992 | 122.1172 | -0.002124 | 0.032376 | -0.024328 | 0.005985 | 0.65293 | 0.5547 | 0.56946 | 0.54728 | 0.53983 | 0.61666 | 0.54159 | 122.3075 | 122.2466 | 122.2404 | 122.1584 | 0.039075 | 0.073575 | 0.016871 | 0.047184 | 122.2684 | 122.2906 | 122.2014 | 122.2236
4354.2812 | 122.4518 | -0.045776 | 122.2 | 0.54764 | 0.44483 | 0.4596 | 0.43283 | 0.43912 | 0.51137 | 0.43173 | 122.2663 | 122.21 | 122.1901 | 122.1126 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.59342 | 0.49061 | 0.50537 | 0.47861 | 0.4849 | 0.55715 | 0.4775 | 122.3075 | 122.2512 | 122.2313 | 122.1538 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.273 | 122.2952 | 122.1968 | 122.219
4356.0469 | 122.3465 | -0.09613 | 122.2412 | 0.56138 | 0.46315 | 0.46875 | 0.45115 | 0.44828 | 0.52511 | 0.44546 | 122.2708 | 122.2009 | 122.1947 | 122.1034 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.65751 | 0.55928 | 0.56488 | 0.54728 | 0.54441 | 0.62124 | 0.54159 | 122.312 | 122.2421 | 122.2359 | 122.1446 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.2867 | 122.2997 | 122.2105 | 122.2236
4357.8125 | 122.374 | -0.086975 | 122.2504 | 0.57053 | 0.46315 | 0.47791 | 0.46488 | 0.44828 | 0.53426 | 0.44546 | 122.2663 | 122.21 | 122.1947 | 122.1034 | -0.011281 | 0.02322 | -0.024328 | 0.001406 | 0.65751 | 0.55012 | 0.56489 | 0.55186 | 0.53526 | 0.62124 | 0.53243 | 122.3075 | 122.2512 | 122.2359 | 122.1446 | 0.029918 | 0.064419 | 0.016871 | 0.042605 | 122.2775 | 122.2906 | 122.2059 | 122.219
4359.5781 | 122.4152 | -0.064087 | 122.2549 | 0.5568 | 0.44483 | 0.46418 | 0.44657 | 0.43912 | 0.52511 | 0.43173 | 122.2708 | 122.2146 | 122.1947 | 122.108 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 0.62089 | 0.50892 | 0.52826 | 0.51066 | 0.50321 | 0.5892 | 0.49581 | 122.312 | 122.2558 | 122.2359 | 122.1492 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 122.2821 | 122.3089 | 122.2059 | 122.2327
4361.3438 | 122.3831 | -0.10529 | 122.2504 | 0.55222 | 0.44941 | 0.45502 | 0.44199 | 0.43912 | 0.51595 | 0.42715 | 122.2663 | 122.2009 | 122.1901 | 122.0988 | -0.002124 | 0.027798 | -0.033484 | 0.005985 | 0.65751 | 0.5547 | 0.5603 | 0.54728 | 0.54441 | 0.62124 | 0.53243 | 122.3075 | 122.2421 | 122.2313 | 122.14 | 0.039075 | 0.068997 | 0.007715 | 0.047184 | 122.2684 | 122.2997 | 122.1922 | 122.2236
4363.125 | 122.4426 | -0.041199 | 122.2549 | 0.58427 | 0.47689 | 0.49623 | 0.47404 | 0.47117 | 0.54342 | 0.45919 | 122.28 | 122.2054 | 122.1947 | 122.108 | -0.006702 | 0.032376 | -0.038063 | 0.001406 | 0.62547 | 0.51809 | 0.53742 | 0.51524 | 0.51237 | 0.58462 | 0.50039 | 122.3212 | 122.2466 | 122.2359 | 122.1492 | 0.034497 | 0.073575 | 0.003136 | 0.042605 | 122.2867 | 122.3181 | 122.2014 | 122.2327
4364.8281 | 122.4655 | -0.054932 | 122.2183 | 0.56595 | 0.46315 | 0.47333 | 0.45572 | 0.45744 | 0.52969 | 0.44546 | 122.2663 | 122.2054 | 122.2038 | 122.1034 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.62089 | 0.51808 | 0.52826 | 0.51066 | 0.51237 | 0.58462 | 0.50039 | 122.3075 | 122.2466 | 122.245 | 122.1446 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2775 | 122.2952 | 122.2151 | 122.2327
4366.5938 | 122.4564 | -0.054932 | 122.2321 | 0.57053 | 0.45857 | 0.47333 | 0.45572 | 0.44828 | 0.52969 | 0.45004 | 122.2708 | 122.2054 | 122.1947 | 122.1034 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.62546 | 0.5135 | 0.52826 | 0.51066 | 0.50321 | 0.58462 | 0.50497 | 122.312 | 122.2466 | 122.2359 | 122.1446 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2821 | 122.3043 | 122.2059 | 122.2282
4368.3438 | 122.3557 | -0.10529 | 122.2549 | 0.58427 | 0.47231 | 0.49165 | 0.46946 | 0.46659 | 0.54342 | 0.45004 | 122.2708 | 122.2054 | 122.2038 | 122.1034 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.68955 | 0.57759 | 0.59693 | 0.57475 | 0.57188 | 0.64871 | 0.55532 | 122.312 | 122.2466 | 122.245 | 122.1446 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2821 | 122.3043 | 122.2151 | 122.2373
4370.0469 | 122.4655 | -0.059509 | 122.2092 | 0.57969 | 0.47231 | 0.48249 | 0.46488 | 0.45744 | 0.52969 | 0.45004 | 122.2754 | 122.2009 | 122.2038 | 122.0988 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 0.6392 | 0.53182 | 0.542 | 0.52439 | 0.51695 | 0.5892 | 0.50955 | 122.3166 | 122.2421 | 122.245 | 122.14 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 122.2867 | 122.3043 | 122.2151 | 122.2327
4371.8281 | 122.3419 | -0.07782 | 122.2595 | 0.58885 | 0.47689 | 0.49165 | 0.47404 | 0.45744 | 0.54342 | 0.45462 | 122.2663 | 122.21 | 122.1901 | 122.1034 | -0.015859 | 0.032376 | -0.028906 | -0.00775 | 0.66667 | 0.55471 | 0.56947 | 0.55186 | 0.53526 | 0.62124 | 0.53244 | 122.3075 | 122.2512 | 122.2313 | 122.1446 | 0.02534 | 0.073575 | 0.012293 | 0.033449 | 122.2821 | 122.2952 | 122.2059 | 122.219
4373.5938 | 122.4838 | -0.050354 | 122.2595 | 0.57053 | 0.46773 | 0.47333 | 0.46488 | 0.45286 | 0.53426 | 0.45004 | 122.2708 | 122.2009 | 122.1901 | 122.108 | -0.011281 | 0.032376 | -0.019749 | 0.001406 | 0.62089 | 0.51808 | 0.52369 | 0.51524 | 0.50321 | 0.58462 | 0.50039 | 122.312 | 122.2421 | 122.2313 | 122.1492 | 0.029918 | 0.073575 | 0.02145 | 0.042605 | 122.2821 | 122.2906 | 122.2014 | 122.2098
4375.3438 | 122.3465 | -0.10529 | 122.2687 | 0.56595 | 0.44941 | 0.46875 | 0.45572 | 0.4437 | 0.52053 | 0.44546 | 122.2708 | 122.1963 | 122.1947 | 122.1126 | -0.002124 | 0.027798 | -0.024328 | 0.005985 | 0.67124 | 0.5547 | 0.57404 | 0.56101 | 0.54899 | 0.62582 | 0.55075 | 122.312 | 122.2375 | 122.2359 | 122.1538 | 0.039075 | 0.068997 | 0.016871 | 0.047184 | 122.273 | 122.2952 | 122.1968 | 122.219
4377.0469 | 122.4518 | -0.054932 | 122.2641 | 0.56595 | 0.45399 | 0.47791 | 0.45115 | 0.45744 | 0.52053 | 0.44546 | 122.2708 | 122.2009 | 122.1947 | 122.1034 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.62089 | 0.50892 | 0.53284 | 0.50608 | 0.51237 | 0.57546 | 0.50039 | 122.312 | 122.2421 | 122.2359 | 122.1446 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.2775 | 122.2997 | 122.2014 | 122.2236
4378.8125 | 122.3236 | -0.09613 | 122.2458 | 0.56595 | 0.45399 | 0.47333 | 0.44199 | 0.4437 | 0.51137 | 0.44546 | 122.2754 | 122.2054 | 122.1992 | 122.0988 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.66209 | 0.55012 | 0.56946 | 0.53812 | 0.53983 | 0.6075 | 0.54159 | 122.3166 | 122.2466 | 122.2404 | 122.14 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2867 | 122.3089 | 122.2105 | 122.2327
4380.5156 | 122.374 | -0.10071 | 122.2549 | 0.5568 | 0.45857 | 0.46875 | 0.45572 | 0.45286 | 0.53426 | 0.45004 | 122.2708 | 122.2054 | 122.1947 | 122.108 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.65751 | 0.55928 | 0.56946 | 0.55643 | 0.55357 | 0.63497 | 0.55075 | 122.312 | 122.2466 | 122.2359 | 122.1492 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2821 | 122.3043 | 122.2059 | 122.2282
4382.2812 | 122.4106 | -0.054932 | 122.2412 | 0.57053 | 0.46315 | 0.48249 | 0.4603 | 0.45286 | 0.52511 | 0.45462 | 122.2708 | 122.2054 | 122.1992 | 122.108 | -0.006702 | 0.036954 | -0.024328 | 0.001406 | 0.62546 | 0.51808 | 0.53742 | 0.51524 | 0.50779 | 0.58004 | 0.50955 | 122.312 | 122.2466 | 122.2404 | 122.1492 | 0.034497 | 0.078153 | 0.016871 | 0.042605 | 122.2775 | 122.2952 | 122.2059 | 122.2236
4383.9844 | 122.3419 | -0.10529 | 122.2641 | 0.57053 | 0.47689 | 0.47791 | 0.4603 | 0.45286 | 0.53884 | 0.45462 | 122.2708 | 122.2054 | 122.1992 | 122.1034 | -0.006702 | 0.027798 | -0.028906 | 0.005985 | 0.67582 | 0.58217 | 0.5832 | 0.56559 | 0.55815 | 0.64413 | 0.5599 | 122.312 | 122.2466 | 122.2404 | 122.1446 | 0.034497 | 0.068997 | 0.012293 | 0.047184 | 122.2775 | 122.2997 | 122.2059 | 122.2282
4385.75 | 122.406 | -0.068665 | 122.2275 | 0.57969 | 0.47231 | 0.48707 | 0.46946 | 0.46202 | 0.53884 | 0.45462 | 122.2617 | 122.2009 | 122.1947 | 122.1034 | -0.011281 | 0.027798 | -0.024328 | 0.005985 | 0.64836 | 0.54097 | 0.55573 | 0.53813 | 0.53068 | 0.60751 | 0.52328 | 122.3029 | 122.2421 | 122.2359 | 122.1446 | 0.029918 | 0.068997 | 0.016871 | 0.047184 | 122.273 | 122.286 | 122.2059 | 122.219
4387.5469 | 122.4655 | -0.050354 | 122.2458 | 0.56595 | 0.46315 | 0.47791 | 0.4603 | 0.46202 | 0.52969 | 0.45004 | 122.2708 | 122.1963 | 122.1992 | 122.1126 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.61631 | 0.5135 | 0.52826 | 0.51066 | 0.51237 | 0.58004 | 0.50039 | 122.312 | 122.2375 | 122.2404 | 122.1538 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2821 | 122.3043 | 122.2105 | 122.2327
4389.25 | 122.3511 | -0.11902 | 122.2641 | 0.57511 | 0.46773 | 0.48249 | 0.4603 | 0.44828 | 0.53426 | 0.44546 | 122.2754 | 122.2009 | 122.1947 | 122.1034 | -0.006702 | 0.041532 | -0.024328 | 0.005985 | 0.69413 | 0.58675 | 0.60151 | 0.57932 | 0.5673 | 0.65328 | 0.56448 | 122.3166 | 122.2421 | 122.2359 | 122.1446 | 0.034497 | 0.082731 | 0.016871 | 0.047184 | 122.2821 | 122.2997 | 122.2014 | 122.219
4391 | 122.374 | -0.064087 | 122.2687 | 0.57969 | 0.46773 | 0.48249 | 0.46946 | 0.47117 | 0.54342 | 0.45462 | 122.2663 | 122.2054 | 122.1992 | 122.1126 | -0.011281 | 0.027798 | -0.028906 | 0.010563 | 0.64378 | 0.53181 | 0.54658 | 0.53355 | 0.53526 | 0.60751 | 0.5187 | 122.3075 | 122.2466 | 122.2404 | 122.1538 | 0.029918 | 0.068997 | 0.012293 | 0.051762 | 122.2775 | 122.2952 | 122.2105 | 122.2282
4392.7656 | 122.3785 | -0.091553 | 122.2641 | 0.57511 | 0.46773 | 0.47791 | 0.45572 | 0.47575 | 0.54342 | 0.45004 | 122.2663 | 122.2009 | 122.1992 | 122.1126 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.66666 | 0.55928 | 0.56946 | 0.54728 | 0.5673 | 0.63497 | 0.54159 | 122.3075 | 122.2421 | 122.2404 | 122.1538 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.273 | 122.2952 | 122.2059 | 122.2282
4394.4688 | 122.374 | -0.082397 | 122.2687 | 0.598 | 0.48604 | 0.5008 | 0.48778 | 0.48033 | 0.56173 | 0.46835 | 122.2708 | 122.1963 | 122.1992 | 122.1034 | -0.006702 | 0.027798 | -0.028906 | 0.005985 | 0.6804 | 0.56844 | 0.5832 | 0.57017 | 0.56272 | 0.64413 | 0.55075 | 122.312 | 122.2375 | 122.2404 | 122.1446 | 0.034497 | 0.068997 | 0.012293 | 0.047184 | 122.2775 | 122.2997 | 122.2059 | 122.2282
4396.2188 | 122.3785 | -0.068665 | 122.2687 | 0.58885 | 0.47689 | 0.49623 | 0.47404 | 0.48033 | 0.55716 | 0.45919 | 122.2663 | 122.21 | 122.1992 | 122.1126 | -0.011281 | 0.036954 | -0.028906 | 0.005985 | 0.65751 | 0.54555 | 0.56489 | 0.5427 | 0.54899 | 0.62582 | 0.52786 | 122.3075 | 122.2512 | 122.2404 | 122.1538 | 0.029918 | 0.078153 | 0.012293 | 0.047184 | 122.2775 | 122.2952 | 122.2105 | 122.2282
4397.9844 | 122.4609 | -0.054932 | 122.2366 | 0.59342 | 0.49062 | 0.5008 | 0.47404 | 0.48033 | 0.56631 | 0.46377 | 122.2663 | 122.2009 | 122.1947 | 122.0988 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.64836 | 0.54555 | 0.55574 | 0.52897 | 0.53526 | 0.62125 | 0.5187 | 122.3075 | 122.2421 | 122.2359 | 122.14 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.2775 | 122.2952 | 122.2059 | 122.2236
4399.75 | 122.4609 | -0.041199 | 122.2321 | 0.56595 | 0.45857 | 0.47791 | 0.45572 | 0.46202 | 0.53426 | 0.4363 | 122.2663 | 122.2054 | 122.1947 | 122.108 | -0.015859 | 0.02322 | -0.033484 | 0.001406 | 0.60715 | 0.49977 | 0.51911 | 0.49692 | 0.50321 | 0.57546 | 0.4775 | 122.3075 | 122.2466 | 122.2359 | 122.1492 | 0.02534 | 0.064419 | 0.007715 | 0.042605 | 122.2821 | 122.2997 | 122.2105 | 122.2282
4401.5156 | 122.4518 | -0.068665 | 122.2321 | 0.57511 | 0.46773 | 0.47333 | 0.45115 | 0.45744 | 0.53884 | 0.45004 | 122.2663 | 122.2054 | 122.1947 | 122.1034 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.64378 | 0.53639 | 0.542 | 0.51981 | 0.5261 | 0.60751 | 0.5187 | 122.3075 | 122.2466 | 122.2359 | 122.1446 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.2821 | 122.2906 | 122.2105 | 122.219
4403.2031 | 122.3923 | -0.086975 | 122.2641 | 0.56595 | 0.46315 | 0.47791 | 0.46946 | 0.46202 | 0.548 | 0.45919 | 122.2708 | 122.2009 | 122.1947 | 122.108 | -0.015859 | 0.027798 | -0.024328 | 0.005985 | 0.65293 | 0.55012 | 0.56489 | 0.55644 | 0.54899 | 0.63498 | 0.54617 | 122.312 | 122.2421 | 122.2359 | 122.1492 | 0.02534 | 0.068997 | 0.016871 | 0.047184 | 122.2867 | 122.2952 | 122.2105 | 122.219
4404.9688 | 122.4609 | -0.059509 | 122.2183 | 0.59342 | 0.48146 | 0.49165 | 0.47404 | 0.47117 | 0.56173 | 0.45919 | 122.2708 | 122.2009 | 122.1855 | 122.0988 | -0.002124 | 0.027798 | -0.033484 | 0.001406 | 0.65293 | 0.54097 | 0.55116 | 0.53355 | 0.53068 | 0.62124 | 0.5187 | 122.312 | 122.2421 | 122.2267 | 122.14 | 0.039075 | 0.068997 | 0.007715 | 0.042605 | 122.273 | 122.3043 | 122.1876 | 122.219
4406.6875 | 122.4792 | -0.050354 | 122.2183 | 0.598 | 0.4952 | 0.50996 | 0.49235 | 0.49406 | 0.57547 | 0.47751 | 122.2754 | 122.2009 | 122.1901 | 122.1034 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.64836 | 0.54556 | 0.56032 | 0.54271 | 0.54441 | 0.62582 | 0.52786 | 122.3166 | 122.2421 | 122.2313 | 122.1446 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2867 | 122.3043 | 122.2014 | 122.219
4408.4375 | 122.3511 | -0.086975 | 122.2595 | 0.57969 | 0.48146 | 0.49165 | 0.47862 | 0.48033 | 0.548 | 0.46377 | 122.2663 | 122.2009 | 122.1947 | 122.0988 | -0.006702 | 0.02322 | -0.024328 | 0.001406 | 0.66667 | 0.56844 | 0.57862 | 0.56559 | 0.5673 | 0.63498 | 0.55075 | 122.3075 | 122.2421 | 122.2359 | 122.14 | 0.034497 | 0.064419 | 0.016871 | 0.042605 | 122.273 | 122.2906 | 122.2014 | 122.219
4410.1406 | 122.3465 | -0.10529 | 122.2412 | 0.57053 | 0.46315 | 0.48249 | 0.4603 | 0.47117 | 0.548 | 0.45462 | 122.2617 | 122.2054 | 122.1855 | 122.1034 | -0.011281 | 0.027798 | -0.024328 | 0.001406 | 0.67582 | 0.56844 | 0.58778 | 0.56559 | 0.57646 | 0.65329 | 0.5599 | 122.3029 | 122.2466 | 122.2267 | 122.1446 | 0.029918 | 0.068997 | 0.016871 | 0.042605 | 122.273 | 122.286 | 122.1968 | 122.2098
4411.9062 | 122.3602 | -0.064087 | 122.2733 | 0.58427 | 0.47689 | 0.49165 | 0.47862 | 0.47117 | 0.55716 | 0.47293 | 122.2663 | 122.2054 | 122.1901 | 122.1034 | -0.006702 | 0.02322 | -0.024328 | 0.005985 | 0.64836 | 0.54097 | 0.55573 | 0.5427 | 0.53526 | 0.62124 | 0.53702 | 122.3075 | 122.2466 | 122.2313 | 122.1446 | 0.034497 | 0.064419 | 0.016871 | 0.047184 | 122.273 | 122.2906 | 122.1968 | 122.2144
4413.6562 | 122.3557 | -0.073242 | 122.2733 | 0.56595 | 0.47231 | 0.47791 | 0.46488 | 0.46202 | 0.54342 | 0.45004 | 122.2708 | 122.2009 | 122.1947 | 122.1034 | -0.006702 | 0.032376 | -0.024328 | 0.005985 | 0.6392 | 0.54555 | 0.55115 | 0.53812 | 0.53526 | 0.61666 | 0.52328 | 122.312 | 122.2421 | 122.2359 | 122.1446 | 0.034497 | 0.073575 | 0.016871 | 0.047184 | 122.2775 | 122.2952 | 122.2014 | 122.219
4415.3594 | 122.3282 | -0.073242 | 122.3236 | 0.57969 | 0.47689 | 0.49165 | 0.47404 | 0.46659 | 0.548 | 0.46377 | 122.2663 | 122.1963 | 122.1901 | 122.1034 | -0.006702 | 0.032376 | -0.033484 | 0.005985 | 0.65293 | 0.55013 | 0.56489 | 0.54728 | 0.53983 | 0.62124 | 0.53702 | 122.3075 | 122.2375 | 122.2313 | 122.1446 | 0.034497 | 0.073575 | 0.007715 | 0.047184 | 122.273 | 122.2997 | 122.1968 | 122.2236
4417.125 | 122.4701 | -0.07782 | 122.2137 | 0.60258 | 0.49062 | 0.50538 | 0.48778 | 0.4849 | 0.55716 | 0.47293 | 122.2754 | 122.2054 | 122.1947 | 122.0943 | -0.002124 | 0.032376 | -0.028906 | 0.001406 | 0.6804 | 0.56844 | 0.5832 | 0.5656 | 0.56272 | 0.63498 | 0.55075 | 122.3166 | 122.2466 | 122.2359 | 122.1355 | 0.039075 | 0.073575 | 0.012293 | 0.042605 | 122.2775 | 122.3043 | 122.1968 | 122.2236
4418.8906 | 122.3145 | -0.11444 | 122.2778 | 0.60258 | 0.48604 | 0.50996 | 0.48778 | 0.4849 | 0.57547 | 0.47293 | 122.2571 | 122.1963 | 122.1947 | 122.1034 | -0.006702 | 0.032376 | -0.019749 | 0.005985 | 0.71702 | 0.60048 | 0.6244 | 0.60222 | 0.59935 | 0.68991 | 0.58737 | 122.2983 | 122.2375 | 122.2359 | 122.1446 | 0.034497 | 0.073575 | 0.02145 | 0.047184 | 122.2638 | 122.2769 | 122.2014 | 122.2144
4420.5938 | 122.4655 | -0.027466 | 122.2778 | 0.58885 | 0.48604 | 0.50538 | 0.48778 | 0.4849 | 0.56631 | 0.46835 | 122.2708 | 122.2009 | 122.1947 | 122.0988 | -0.006702 | 0.027798 | -0.024328 | 0.001406 | 0.61631 | 0.51351 | 0.53285 | 0.51524 | 0.51237 | 0.59378 | 0.49582 | 122.312 | 122.2421 | 122.2359 | 122.14 | 0.034497 | 0.068997 | 0.016871 | 0.042605 | 122.2775 | 122.2952 | 122.2014 | 122.219
4422.375 | 122.406 | -0.09613 | 122.2183 | 0.598 | 0.48604 | 0.50538 | 0.48778 | 0.4849 | 0.57547 | 0.46835 | 122.2663 | 122.1963 | 122.1855 | 122.0988 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 0.69413 | 0.58217 | 0.60151 | 0.58391 | 0.58103 | 0.6716 | 0.56448 | 122.3075 | 122.2375 | 122.2267 | 122.14 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 122.273 | 122.2952 | 122.1922 | 122.2144
4424.1562 | 122.4243 | -0.059509 | 122.2778 | 0.60258 | 0.50894 | 0.50996 | 0.49693 | 0.50322 | 0.57547 | 0.48666 | 122.2663 | 122.1963 | 122.1947 | 122.0988 | 0.002454 | 0.041532 | -0.019749 | 0.005985 | 0.66209 | 0.56845 | 0.56947 | 0.55644 | 0.56273 | 0.63498 | 0.54617 | 122.3075 | 122.2375 | 122.2359 | 122.14 | 0.043653 | 0.082731 | 0.02145 | 0.047184 | 122.2638 | 122.286 | 122.1922 | 122.2144
4425.8438 | 122.4564 | -0.054932 | 122.2321 | 0.60716 | 0.4952 | 0.50538 | 0.49235 | 0.4849 | 0.57089 | 0.48208 | 122.2708 | 122.1963 | 122.1901 | 122.0988 | -0.006702 | 0.032376 | -0.019749 | 0.010563 | 0.66209 | 0.55013 | 0.56031 | 0.54729 | 0.53984 | 0.62582 | 0.53702 | 122.312 | 122.2375 | 122.2313 | 122.14 | 0.034497 | 0.073575 | 0.02145 | 0.051762 | 122.2775 | 122.2906 | 122.1968 | 122.2098
4427.6094 | 122.3282 | -0.10071 | 122.2412 | 0.60258 | 0.4952 | 0.50538 | 0.4832 | 0.4849 | 0.57089 | 0.47751 | 122.2663 | 122.2009 | 122.1901 | 122.0943 | -0.002124 | 0.032376 | -0.024328 | 0.001406 | 0.70329 | 0.59591 | 0.60609 | 0.5839 | 0.58561 | 0.6716 | 0.57822 | 122.3075 | 122.2421 | 122.2313 | 122.1355 | 0.039075 | 0.073575 | 0.016871 | 0.042605 | 122.2684 | 122.2906 | 122.1922 | 122.2144
4429.3125 | 122.4838 | -0.064087 | 122.2595 | 0.59342 | 0.49062 | 0.49623 | 0.48778 | 0.47575 | 0.56631 | 0.47293 | 122.2617 | 122.1963 | 122.1855 | 122.0943 | -0.011281 | 0.032376 | -0.038063 | 0.010563 | 0.65751 | 0.55471 | 0.56031 | 0.55186 | 0.53984 | 0.6304 | 0.53702 | 122.3029 | 122.2375 | 122.2267 | 122.1355 | 0.029918 | 0.073575 | 0.003136 | 0.051762 | 122.273 | 122.2997 | 122.1968 | 122.2236
4431.0781 | 122.3694 | -0.091553 | 122.2321 | 0.59342 | 0.48604 | 0.50538 | 0.47862 | 0.4849 | 0.56631 | 0.47293 | 122.2663 | 122.21 | 122.1901 | 122.0988 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.68498 | 0.5776 | 0.59693 | 0.57017 | 0.57646 | 0.65787 | 0.56448 | 122.3075 | 122.2512 | 122.2313 | 122.14 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2775 | 122.2997 | 122.2014 | 122.2236
4432.7812 | 122.3236 | -0.10071 | 122.2549 | 0.58885 | 0.49062 | 0.50538 | 0.49235 | 0.49406 | 0.56631 | 0.47293 | 122.2754 | 122.1963 | 122.1947 | 122.0988 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.68956 | 0.59133 | 0.60609 | 0.59306 | 0.59477 | 0.66702 | 0.57364 | 122.3166 | 122.2375 | 122.2359 | 122.14 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.2867 | 122.3043 | 122.2059 | 122.2236
4434.5312 | 122.4335 | -0.050354 | 122.2321 | 0.62089 | 0.50436 | 0.5237 | 0.49693 | 0.50779 | 0.58463 | 0.49124 | 122.2663 | 122.2054 | 122.1901 | 122.0988 | -0.002124 | 0.027798 | -0.024328 | -0.003172 | 0.67125 | 0.55471 | 0.57405 | 0.54729 | 0.55815 | 0.63498 | 0.5416 | 122.3075 | 122.2466 | 122.2313 | 122.14 | 0.039075 | 0.068997 | 0.016871 | 0.038027 | 122.2684 | 122.2906 | 122.1922 | 122.2144
4436.2969 | 122.4335 | -0.073242 | 122.2137 | 0.60258 | 0.50436 | 0.51454 | 0.49235 | 0.50779 | 0.56631 | 0.48666 | 122.2617 | 122.1917 | 122.1901 | 122.0988 | -0.002124 | 0.027798 | -0.033484 | 0.005985 | 0.67582 | 0.5776 | 0.58778 | 0.56559 | 0.58104 | 0.63956 | 0.5599 | 122.3029 | 122.2329 | 122.2313 | 122.14 | 0.039075 | 0.068997 | 0.007715 | 0.047184 | 122.2638 | 122.2952 | 122.1922 | 122.2236
4438.0625 | 122.4243 | -0.091553 | 122.2321 | 0.598 | 0.49062 | 0.50996 | 0.48778 | 0.4849 | 0.57547 | 0.47293 | 122.2708 | 122.1963 | 122.1855 | 122.0943 | -0.006702 | 0.036954 | -0.038063 | -0.003172 | 0.68956 | 0.58217 | 0.60151 | 0.57933 | 0.57646 | 0.66702 | 0.56448 | 122.312 | 122.2375 | 122.2267 | 122.1355 | 0.034497 | 0.078153 | 0.003136 | 0.038027 | 122.2775 | 122.3089 | 122.1922 | 122.2236
4439.8125 | 122.4335 | -0.068665 | 122.2183 | 0.60258 | 0.49978 | 0.51454 | 0.49693 | 0.48948 | 0.57547 | 0.48666 | 122.2663 | 122.1963 | 122.1855 | 122.0943 | -0.006702 | 0.032376 | -0.024328 | 0.001406 | 0.67125 | 0.56844 | 0.5832 | 0.5656 | 0.55815 | 0.64414 | 0.55533 | 122.3075 | 122.2375 | 122.2267 | 122.1355 | 0.034497 | 0.073575 | 0.016871 | 0.042605 | 122.273 | 122.2906 | 122.1922 | 122.2098
4441.5156 | 122.4289 | -0.07782 | 122.2458 | 0.63463 | 0.52267 | 0.54201 | 0.51982 | 0.51237 | 0.60294 | 0.50498 | 122.2617 | 122.1917 | 122.1855 | 122.0988 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.71245 | 0.60049 | 0.61983 | 0.59764 | 0.59019 | 0.68076 | 0.5828 | 122.3029 | 122.2329 | 122.2267 | 122.14 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.273 | 122.2952 | 122.1968 | 122.219
4443.2812 | 122.4197 | -0.054932 | 122.2733 | 0.63005 | 0.51809 | 0.53743 | 0.51525 | 0.51695 | 0.60294 | 0.50498 | 122.2663 | 122.2009 | 122.1901 | 122.0943 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.68498 | 0.57303 | 0.59237 | 0.57018 | 0.57188 | 0.65787 | 0.55991 | 122.3075 | 122.2421 | 122.2313 | 122.1355 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.273 | 122.2952 | 122.1968 | 122.219
4444.9844 | 122.4838 | -0.041199 | 122.2275 | 0.63463 | 0.52267 | 0.53285 | 0.51525 | 0.51237 | 0.59836 | 0.50498 | 122.2663 | 122.1917 | 122.1901 | 122.0943 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.67583 | 0.56387 | 0.57405 | 0.55644 | 0.55357 | 0.63956 | 0.54617 | 122.3075 | 122.2329 | 122.2313 | 122.1355 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.2775 | 122.2997 | 122.2014 | 122.2236
4446.75 | 122.4609 | -0.054932 | 122.1954 | 0.63921 | 0.53641 | 0.55575 | 0.52898 | 0.52611 | 0.60752 | 0.50498 | 122.2617 | 122.1963 | 122.1855 | 122.0943 | -0.006702 | 0.032376 | -0.033484 | 0.005985 | 0.69414 | 0.59134 | 0.61068 | 0.58391 | 0.58104 | 0.66245 | 0.55991 | 122.3029 | 122.2375 | 122.2267 | 122.1355 | 0.034497 | 0.073575 | 0.007715 | 0.047184 | 122.2684 | 122.2952 | 122.1922 | 122.219
4448.4531 | 122.4014 | -0.07782 | 122.2549 | 0.63463 | 0.53183 | 0.54201 | 0.51982 | 0.51695 | 0.60752 | 0.51413 | 122.2663 | 122.1917 | 122.1901 | 122.0943 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 0.71245 | 0.60965 | 0.61983 | 0.59764 | 0.59477 | 0.68534 | 0.59195 | 122.3075 | 122.2329 | 122.2313 | 122.1355 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 122.2775 | 122.2997 | 122.2014 | 122.2236
4450.2031 | 122.3602 | -0.082397 | 122.2595 | 0.63005 | 0.53641 | 0.55117 | 0.52898 | 0.51695 | 0.60752 | 0.50955 | 122.2663 | 122.1917 | 122.1901 | 122.0988 | -0.002124 | 0.027798 | -0.033484 | -0.003172 | 0.71245 | 0.61881 | 0.63357 | 0.61138 | 0.59935 | 0.68992 | 0.59195 | 122.3075 | 122.2329 | 122.2313 | 122.14 | 0.039075 | 0.068997 | 0.007715 | 0.038027 | 122.2684 | 122.2997 | 122.1922 | 122.2236
4451.9844 | 122.3648 | -0.07782 | 122.2595 | 0.63921 | 0.53183 | 0.54201 | 0.52898 | 0.51237 | 0.60294 | 0.51413 | 122.2663 | 122.2009 | 122.1992 | 122.0988 | -0.011281 | 0.032376 | -0.019749 | 0.001406 | 0.71703 | 0.60965 | 0.61983 | 0.6068 | 0.59019 | 0.68076 | 0.59195 | 122.3075 | 122.2421 | 122.2404 | 122.14 | 0.029918 | 0.073575 | 0.02145 | 0.042605 | 122.2775 | 122.286 | 122.2105 | 122.219
4453.7031 | 122.3511 | -0.073242 | 122.2504 | 0.62089 | 0.50894 | 0.52828 | 0.51982 | 0.49406 | 0.58921 | 0.5004 | 122.2617 | 122.1963 | 122.1809 | 122.0897 | -0.006702 | 0.027798 | -0.028906 | -0.00775 | 0.69414 | 0.58218 | 0.60152 | 0.59307 | 0.5673 | 0.66245 | 0.57364 | 122.3029 | 122.2375 | 122.2221 | 122.1309 | 0.034497 | 0.068997 | 0.012293 | 0.033449 | 122.2684 | 122.2906 | 122.1876 | 122.2098
4455.4688 | 122.4106 | -0.064087 | 122.2275 | 0.64379 | 0.52267 | 0.54659 | 0.52898 | 0.51695 | 0.60752 | 0.51413 | 122.2617 | 122.1963 | 122.1855 | 122.0988 | -0.002124 | 0.032376 | -0.033484 | -0.00775 | 0.70787 | 0.58676 | 0.61068 | 0.59307 | 0.58104 | 0.67161 | 0.57822 | 122.3029 | 122.2375 | 122.2267 | 122.14 | 0.039075 | 0.073575 | 0.007715 | 0.033449 | 122.2638 | 122.2952 | 122.1876 | 122.219
4457.1719 | 122.3648 | -0.07782 | 122.2412 | 0.64379 | 0.53641 | 0.55575 | 0.54272 | 0.53526 | 0.62125 | 0.52787 | 122.2571 | 122.1917 | 122.1855 | 122.0943 | -0.006702 | 0.036954 | -0.024328 | 0.001406 | 0.72161 | 0.61423 | 0.63357 | 0.62054 | 0.61308 | 0.69907 | 0.60569 | 122.2983 | 122.2329 | 122.2267 | 122.1355 | 0.034497 | 0.078153 | 0.016871 | 0.042605 | 122.2638 | 122.2814 | 122.1922 | 122.2098
4458.9375 | 122.3282 | -0.10986 | 122.2595 | 0.63463 | 0.52725 | 0.54201 | 0.52898 | 0.52611 | 0.60752 | 0.52329 | 122.2617 | 122.1917 | 122.1901 | 122.0988 | -0.002124 | 0.032376 | -0.028906 | 0.005985 | 0.74449 | 0.63712 | 0.65187 | 0.63884 | 0.63597 | 0.71738 | 0.63315 | 122.3029 | 122.2329 | 122.2313 | 122.14 | 0.039075 | 0.073575 | 0.012293 | 0.047184 | 122.2638 | 122.2906 | 122.1922 | 122.219
4460.7031 | 122.3602 | -0.059509 | 122.2687 | 0.64837 | 0.53641 | 0.54659 | 0.5244 | 0.53526 | 0.60294 | 0.51413 | 122.2663 | 122.1963 | 122.1855 | 122.0988 | -0.015859 | 0.027798 | -0.038063 | 0.001406 | 0.70788 | 0.59592 | 0.6061 | 0.58391 | 0.59477 | 0.66245 | 0.57364 | 122.3075 | 122.2375 | 122.2267 | 122.14 | 0.02534 | 0.068997 | 0.003136 | 0.042605 | 122.2821 | 122.3043 | 122.2014 | 122.2236
4462.4062 | 122.3511 | -0.091553 | 122.2549 | 0.64837 | 0.55015 | 0.5649 | 0.54729 | 0.54442 | 0.62583 | 0.53244 | 122.2617 | 122.1917 | 122.1809 | 122.0988 | -0.006702 | 0.036954 | -0.028906 | 0.005985 | 0.73992 | 0.6417 | 0.65646 | 0.63885 | 0.63597 | 0.71739 | 0.624 | 122.3029 | 122.2329 | 122.2221 | 122.14 | 0.034497 | 0.078153 | 0.012293 | 0.047184 | 122.2684 | 122.2906 | 122.1876 | 122.2098
4464.1719 | 122.319 | -0.10529 | 122.2641 | 0.6621 | 0.55473 | 0.56033 | 0.55187 | 0.549 | 0.63499 | 0.52787 | 122.2617 | 122.1963 | 122.1855 | 122.0897 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 0.76739 | 0.66001 | 0.66561 | 0.65716 | 0.65428 | 0.74028 | 0.63315 | 122.3029 | 122.2375 | 122.2267 | 122.1309 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 122.2684 | 122.2952 | 122.1922 | 122.219
4465.8906 | 122.438 | -0.09613 | 122.2137 | 0.6621 | 0.55015 | 0.5649 | 0.55187 | 0.549 | 0.63041 | 0.5416 | 122.2617 | 122.1917 | 122.1809 | 122.0988 | -0.006702 | 0.032376 | -0.024328 | 0.001406 | 0.75823 | 0.64628 | 0.66103 | 0.648 | 0.64513 | 0.72654 | 0.63773 | 122.3029 | 122.2329 | 122.2221 | 122.14 | 0.034497 | 0.073575 | 0.016871 | 0.042605 | 122.2684 | 122.286 | 122.1876 | 122.2053
4467.6562 | 122.374 | -0.086975 | 122.2412 | 0.64837 | 0.54557 | 0.55575 | 0.53814 | 0.53526 | 0.61668 | 0.52787 | 122.2617 | 122.1871 | 122.1855 | 122.0943 | -0.006702 | 0.032376 | -0.033484 | 0.005985 | 0.73534 | 0.63254 | 0.64272 | 0.62511 | 0.62224 | 0.70365 | 0.61484 | 122.3029 | 122.2283 | 122.2267 | 122.1355 | 0.034497 | 0.073575 | 0.007715 | 0.047184 | 122.2684 | 122.2952 | 122.1922 | 122.219
4469.4219 | 122.3236 | -0.082397 | 122.2549 | 0.66668 | 0.56846 | 0.57864 | 0.56561 | 0.55815 | 0.63957 | 0.54618 | 122.2571 | 122.2009 | 122.1855 | 122.0943 | -0.006702 | 0.036954 | -0.033484 | 0.001406 | 0.74908 | 0.65086 | 0.66104 | 0.64801 | 0.64055 | 0.72196 | 0.62858 | 122.2983 | 122.2421 | 122.2267 | 122.1355 | 0.034497 | 0.078153 | 0.007715 | 0.042605 | 122.2638 | 122.2906 | 122.1922 | 122.219
4471.1875 | 122.3557 | -0.091553 | 122.2687 | 0.68041 | 0.57762 | 0.59238 | 0.57019 | 0.57189 | 0.65788 | 0.56449 | 122.2663 | 122.1917 | 122.1809 | 122.0943 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.77197 | 0.66917 | 0.68393 | 0.66174 | 0.66344 | 0.74943 | 0.65604 | 122.3075 | 122.2329 | 122.2221 | 122.1355 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.2775 | 122.2997 | 122.1922 | 122.2144
4472.8906 | 122.3557 | -0.086975 | 122.2458 | 0.69415 | 0.59593 | 0.59696 | 0.58392 | 0.5902 | 0.66704 | 0.57823 | 122.2617 | 122.1871 | 122.1809 | 122.0897 | -0.006702 | 0.032376 | -0.024328 | 0.001406 | 0.78113 | 0.68291 | 0.68393 | 0.6709 | 0.67717 | 0.75401 | 0.6652 | 122.3029 | 122.2283 | 122.2221 | 122.1309 | 0.034497 | 0.073575 | 0.016871 | 0.042605 | 122.2684 | 122.286 | 122.1876 | 122.2053
4474.6562 | 122.3419 | -0.082397 | 122.2366 | 0.72162 | 0.61425 | 0.63358 | 0.61139 | 0.61767 | 0.68535 | 0.59654 | 122.2571 | 122.1871 | 122.1809 | 122.0805 | -0.002124 | 0.032376 | -0.033484 | 0.001406 | 0.80402 | 0.69665 | 0.71598 | 0.69379 | 0.70006 | 0.76775 | 0.67894 | 122.2983 | 122.2283 | 122.2221 | 122.1217 | 0.039075 | 0.073575 | 0.007715 | 0.042605 | 122.2592 | 122.2906 | 122.1831 | 122.2144
4476.4219 | 122.4701 | -0.064087 | 122.2321 | 0.72162 | 0.61425 | 0.63816 | 0.61597 | 0.62224 | 0.69451 | 0.6057 | 122.2571 | 122.1871 | 122.1901 | 122.0851 | -0.011281 | 0.041532 | -0.028906 | 0.001406 | 0.78571 | 0.67834 | 0.70225 | 0.68006 | 0.68633 | 0.7586 | 0.66978 | 122.2983 | 122.2283 | 122.2313 | 122.1263 | 0.029918 | 0.082731 | 0.012293 | 0.042605 | 122.2684 | 122.286 | 122.2014 | 122.219
4478.125 | 122.4197 | -0.073242 | 122.2412 | 0.7262 | 0.61883 | 0.62443 | 0.61597 | 0.62682 | 0.68535 | 0.60112 | 122.2617 | 122.1917 | 122.1764 | 122.0851 | -0.006702 | 0.032376 | -0.033484 | 0.005985 | 0.79944 | 0.69207 | 0.69767 | 0.68921 | 0.70006 | 0.75859 | 0.67436 | 122.3029 | 122.2329 | 122.2176 | 122.1263 | 0.034497 | 0.073575 | 0.007715 | 0.047184 | 122.2684 | 122.2952 | 122.1831 | 122.2098
4479.8906 | 122.4014 | -0.068665 | 122.2366 | 0.74909 | 0.63257 | 0.65648 | 0.62971 | 0.64055 | 0.7174 | 0.62401 | 122.2571 | 122.1917 | 122.1901 | 122.0897 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.81776 | 0.70123 | 0.72514 | 0.69837 | 0.70922 | 0.78607 | 0.69267 | 122.2983 | 122.2329 | 122.2313 | 122.1309 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.2638 | 122.286 | 122.1968 | 122.219
4481.5938 | 122.3969 | -0.050354 | 122.2321 | 0.7262 | 0.62341 | 0.63816 | 0.61139 | 0.63598 | 0.69909 | 0.61485 | 122.2571 | 122.178 | 122.1855 | 122.0851 | 0.002454 | 0.032376 | -0.033484 | 0.001406 | 0.77655 | 0.67376 | 0.68852 | 0.66175 | 0.68633 | 0.74944 | 0.66521 | 122.2983 | 122.2192 | 122.2267 | 122.1263 | 0.043653 | 0.073575 | 0.007715 | 0.042605 | 122.2546 | 122.2906 | 122.1831 | 122.219
4483.375 | 122.4014 | -0.059509 | 122.2229 | 0.74451 | 0.63257 | 0.64732 | 0.62971 | 0.64513 | 0.71282 | 0.62401 | 122.2617 | 122.1871 | 122.1855 | 122.0897 | -0.002124 | 0.032376 | -0.019749 | 0.005985 | 0.80402 | 0.69207 | 0.70683 | 0.68922 | 0.70464 | 0.77233 | 0.68352 | 122.3029 | 122.2283 | 122.2267 | 122.1309 | 0.039075 | 0.073575 | 0.02145 | 0.047184 | 122.2638 | 122.2814 | 122.1876 | 122.2053
4485.0625 | 122.406 | -0.064087 | 122.2046 | 0.73993 | 0.62799 | 0.6519 | 0.63429 | 0.64513 | 0.7174 | 0.61943 | 122.2525 | 122.1825 | 122.1809 | 122.0897 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 0.80402 | 0.69207 | 0.71598 | 0.69837 | 0.70922 | 0.78149 | 0.68352 | 122.2937 | 122.2237 | 122.2221 | 122.1309 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 122.2592 | 122.286 | 122.1876 | 122.2144
4486.8281 | 122.3648 | -0.091553 | 122.2412 | 0.74909 | 0.63257 | 0.64274 | 0.62513 | 0.64055 | 0.71282 | 0.62401 | 122.2617 | 122.1917 | 122.1718 | 122.0897 | -0.011281 | 0.027798 | -0.028906 | 0.005985 | 0.84064 | 0.72412 | 0.73429 | 0.71668 | 0.73211 | 0.80437 | 0.71556 | 122.3029 | 122.2329 | 122.213 | 122.1309 | 0.029918 | 0.068997 | 0.012293 | 0.047184 | 122.273 | 122.2906 | 122.1831 | 122.2007
4488.6094 | 122.3923 | -0.07782 | 122.2412 | 0.76282 | 0.66004 | 0.67021 | 0.6526 | 0.66344 | 0.73571 | 0.63774 | 122.2525 | 122.1825 | 122.1764 | 122.0851 | 0.002454 | 0.027798 | -0.028906 | -0.003172 | 0.84064 | 0.73786 | 0.74803 | 0.73042 | 0.74126 | 0.81353 | 0.71556 | 122.2937 | 122.2237 | 122.2176 | 122.1263 | 0.043653 | 0.068997 | 0.012293 | 0.038027 | 122.2501 | 122.2814 | 122.1739 | 122.2053
4490.3125 | 122.4609 | -0.054932 | 122.2 | 0.7674 | 0.65546 | 0.67479 | 0.66176 | 0.65887 | 0.73571 | 0.6469 | 122.2525 | 122.178 | 122.1718 | 122.0805 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 0.82234 | 0.71039 | 0.72972 | 0.71669 | 0.7138 | 0.79065 | 0.70183 | 122.2937 | 122.2192 | 122.213 | 122.1217 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 122.2592 | 122.2814 | 122.1785 | 122.2007
4492.0938 | 122.4014 | -0.073242 | 122.2275 | 0.78572 | 0.6692 | 0.68395 | 0.67091 | 0.68176 | 0.74945 | 0.65606 | 122.2525 | 122.1825 | 122.1764 | 122.0851 | -0.006702 | 0.036954 | -0.024328 | 0.010563 | 0.85896 | 0.74244 | 0.75719 | 0.74416 | 0.755 | 0.82269 | 0.7293 | 122.2937 | 122.2237 | 122.2176 | 122.1263 | 0.034497 | 0.078153 | 0.016871 | 0.051762 | 122.2592 | 122.2769 | 122.1831 | 122.2007
4493.875 | 122.4335 | -0.036621 | 122.2137 | 0.78114 | 0.67835 | 0.6931 | 0.66634 | 0.68634 | 0.75861 | 0.66063 | 122.2571 | 122.1871 | 122.1718 | 122.0851 | -0.006702 | 0.032376 | -0.028906 | 0.010563 | 0.81776 | 0.71498 | 0.72973 | 0.70296 | 0.72296 | 0.79523 | 0.69726 | 122.2983 | 122.2283 | 122.213 | 122.1263 | 0.034497 | 0.073575 | 0.012293 | 0.051762 | 122.2638 | 122.286 | 122.1785 | 122.2007
4495.5781 | 122.4472 | -0.059509 | 122.2046 | 0.75825 | 0.6463 | 0.67479 | 0.64344 | 0.65429 | 0.72656 | 0.63316 | 122.2479 | 122.1871 | 122.1809 | 122.0851 | -0.002124 | 0.032376 | -0.028906 | -0.00775 | 0.81776 | 0.70581 | 0.7343 | 0.70295 | 0.7138 | 0.78607 | 0.69267 | 122.2891 | 122.2283 | 122.2221 | 122.1263 | 0.039075 | 0.073575 | 0.012293 | 0.033449 | 122.2501 | 122.2769 | 122.1831 | 122.2098
4497.3438 | 122.319 | -0.10529 | 122.2687 | 0.78572 | 0.67835 | 0.68853 | 0.67549 | 0.69091 | 0.75861 | 0.66521 | 122.2479 | 122.1917 | 122.1809 | 122.0897 | -0.002124 | 0.032376 | -0.028906 | 0.005985 | 0.891 | 0.78364 | 0.79381 | 0.78078 | 0.7962 | 0.86389 | 0.7705 | 122.2891 | 122.2329 | 122.2221 | 122.1309 | 0.039075 | 0.073575 | 0.012293 | 0.047184 | 122.2501 | 122.2769 | 122.1831 | 122.2098
4499.125 | 122.3419 | -0.09613 | 122.2504 | 0.7903 | 0.67835 | 0.6931 | 0.68007 | 0.68634 | 0.75861 | 0.66521 | 122.2479 | 122.1917 | 122.1764 | 122.0759 | -0.002124 | 0.036954 | -0.028906 | 0.001406 | 0.88643 | 0.77448 | 0.78923 | 0.7762 | 0.78246 | 0.85474 | 0.76134 | 122.2891 | 122.2329 | 122.2176 | 122.1171 | 0.039075 | 0.078153 | 0.012293 | 0.042605 | 122.2501 | 122.2769 | 122.1785 | 122.2053
4500.8281 | 122.4518 | -0.054932 | 122.2229 | 0.83608 | 0.72414 | 0.74347 | 0.73043 | 0.73211 | 0.80439 | 0.71557 | 122.2525 | 122.1871 | 122.1764 | 122.0851 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 0.89101 | 0.77907 | 0.7984 | 0.78537 | 0.78705 | 0.85932 | 0.7705 | 122.2937 | 122.2283 | 122.2176 | 122.1263 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 122.2638 | 122.2814 | 122.1876 | 122.2053
4502.5938 | 122.3511 | -0.11444 | 122.2641 | 0.84524 | 0.7333 | 0.74347 | 0.73959 | 0.74127 | 0.81355 | 0.72931 | 122.2479 | 122.1825 | 122.1855 | 122.0714 | 0.002454 | 0.027798 | -0.024328 | 0.001406 | 0.95968 | 0.84774 | 0.85791 | 0.85403 | 0.85571 | 0.92799 | 0.84375 | 122.2891 | 122.2237 | 122.2267 | 122.1126 | 0.043653 | 0.068997 | 0.016871 | 0.042605 | 122.2455 | 122.2723 | 122.1831 | 122.2098
4504.3438 | 122.319 | -0.10071 | 122.2321 | 0.86355 | 0.74704 | 0.77094 | 0.76248 | 0.76874 | 0.83644 | 0.74304 | 122.2479 | 122.1871 | 122.1764 | 122.0851 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.96426 | 0.84774 | 0.87165 | 0.86319 | 0.86945 | 0.93715 | 0.84375 | 122.2891 | 122.2283 | 122.2176 | 122.1263 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.2638 | 122.2814 | 122.1922 | 122.2098
4506.1094 | 122.3236 | -0.10071 | 122.2366 | 0.91391 | 0.7974 | 0.82588 | 0.80369 | 0.80994 | 0.88222 | 0.78882 | 122.2479 | 122.1825 | 122.1718 | 122.0759 | -0.006702 | 0.041532 | -0.019749 | 0.010563 | 1.0146 | 0.89811 | 0.92659 | 0.9044 | 0.91065 | 0.98293 | 0.88953 | 122.2891 | 122.2237 | 122.213 | 122.1171 | 0.034497 | 0.082731 | 0.02145 | 0.051762 | 122.2546 | 122.2677 | 122.1785 | 122.1915
4507.875 | 122.3328 | -0.10529 | 122.2321 | 0.94596 | 0.83403 | 0.8442 | 0.82658 | 0.84656 | 0.90969 | 0.81629 | 122.2479 | 122.1825 | 122.1718 | 122.0759 | 0.002454 | 0.032376 | -0.033484 | -0.003172 | 1.0512 | 0.93932 | 0.94949 | 0.93187 | 0.95185 | 1.015 | 0.92158 | 122.2891 | 122.2237 | 122.213 | 122.1171 | 0.043653 | 0.073575 | 0.007715 | 0.038027 | 122.2455 | 122.2814 | 122.1693 | 122.2053
4509.6406 | 122.3557 | -0.09613 | 122.2321 | 0.94596 | 0.83403 | 0.85794 | 0.83574 | 0.85114 | 0.91885 | 0.82545 | 122.2525 | 122.178 | 122.1718 | 122.0759 | -0.006702 | 0.036954 | -0.024328 | -0.003172 | 1.0421 | 0.93016 | 0.95406 | 0.93187 | 0.94727 | 1.015 | 0.92158 | 122.2937 | 122.2192 | 122.213 | 122.1171 | 0.034497 | 0.078153 | 0.016871 | 0.038027 | 122.2592 | 122.2769 | 122.1785 | 122.1961
4511.4062 | 122.4426 | -0.064087 | 122.2183 | 0.95512 | 0.84777 | 0.85794 | 0.85405 | 0.85114 | 0.91885 | 0.83461 | 122.2434 | 122.178 | 122.158 | 122.0805 | 0.002454 | 0.032376 | -0.019749 | 0.005985 | 1.0192 | 0.91186 | 0.92202 | 0.91814 | 0.91523 | 0.98294 | 0.89869 | 122.2846 | 122.2192 | 122.1992 | 122.1217 | 0.043653 | 0.073575 | 0.02145 | 0.047184 | 122.2409 | 122.2631 | 122.1556 | 122.1778
4513.1719 | 122.3007 | -0.10986 | 122.2275 | 0.9368 | 0.8203 | 0.83504 | 0.822 | 0.83741 | 0.90511 | 0.80714 | 122.2479 | 122.1642 | 122.1626 | 122.0668 | -0.002124 | 0.036954 | -0.024328 | 0.001406 | 1.0467 | 0.93016 | 0.9449 | 0.93187 | 0.94727 | 1.015 | 0.917 | 122.2891 | 122.2054 | 122.2038 | 122.108 | 0.039075 | 0.078153 | 0.016871 | 0.042605 | 122.2501 | 122.2723 | 122.1647 | 122.1869
4514.875 | 122.1222 | -0.39825 | 121.7514 | 0.96427 | 0.84777 | 0.86709 | 0.84948 | 0.8603 | 0.92801 | 0.83918 | 121.8176 | 121.7475 | 121.6224 | 121.5265 | 0.24968 | 0.28875 | 0.14507 | 0.18911 | 1.3625 | 1.246 | 1.2653 | 1.2477 | 1.2586 | 1.3263 | 1.2374 | 121.8588 | 121.7887 | 121.6636 | 121.5677 | 0.29087 | 0.32995 | 0.18627 | 0.23031 | 121.5679 | 121.6725 | 121.3727 | 121.4773
4516.6406 | 122.1542 | -0.07782 | 122.0444 | 0.19968 | 0.069371 | 0.065837 | 0.066553 | 0.086622 | 0.14968 | 0.07005 | 122.0373 | 121.9719 | 0.28421 | 0.19127 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 0.2775 | 0.14719 | 0.14366 | 0.14437 | 0.16444 | 0.2275 | 0.14787 | 122.0785 | 122.0131 | 0.32541 | 0.23247 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 122.044 | 122.0708 | 0.29091 | 0.3177
4518.4062 | 122.2916 | -0.054932 | 122.0398 | 0.19968 | 0.07395 | 0.065837 | 0.066553 | 0.082044 | 0.15426 | 0.056315 | 122.1014 | 122.036 | 0.2659 | 0.17296 | -0.006702 | 0.02322 | -0.033484 | 0.010563 | 0.25462 | 0.12888 | 0.12077 | 0.12149 | 0.13698 | 0.20919 | 0.11125 | 122.1426 | 122.0772 | 0.3071 | 0.21415 | 0.034497 | 0.064419 | 0.007715 | 0.051762 | 122.1081 | 122.1349 | 0.2726 | 0.29938
4520.0938 | 122.2046 | -0.086975 | 122.1085 | 0.19053 | 0.078529 | 0.065837 | 0.066553 | 0.072888 | 0.15884 | 0.060893 | 122.1243 | 122.0635 | 0.26132 | 0.17753 | -0.002124 | 0.036954 | -0.033484 | 0.001406 | 0.2775 | 0.1655 | 0.15281 | 0.15353 | 0.15986 | 0.24581 | 0.14787 | 122.1655 | 122.1047 | 0.30252 | 0.21873 | 0.039075 | 0.078153 | 0.007715 | 0.042605 | 122.1265 | 122.1578 | 0.26345 | 0.29481
4521.8594 | 122.3282 | -0.050354 | 122.0901 | 0.19511 | 0.07395 | 0.065837 | 0.066553 | 0.082044 | 0.15884 | 0.056315 | 122.1381 | 122.0681 | 0.24301 | 0.17753 | -0.011281 | 0.02322 | -0.038063 | 0.001406 | 0.24546 | 0.1243 | 0.11619 | 0.11691 | 0.1324 | 0.20919 | 0.10667 | 122.1793 | 122.1093 | 0.28421 | 0.21873 | 0.029918 | 0.064419 | 0.003136 | 0.042605 | 122.1493 | 122.1761 | 0.25429 | 0.28107
4523.625 | 122.3602 | -0.036621 | 122.1039 | 0.19511 | 0.07395 | 0.070415 | 0.066553 | 0.072888 | 0.14968 | 0.056315 | 122.1518 | 122.0818 | 0.25216 | 0.20959 | -0.011281 | 0.02322 | -0.033484 | 0.005985 | 0.23173 | 0.11057 | 0.10704 | 0.10317 | 0.10951 | 0.1863 | 0.092936 | 122.193 | 122.123 | 0.29336 | 0.25079 | 0.029918 | 0.064419 | 0.007715 | 0.047184 | 122.1631 | 122.1853 | 0.26344 | 0.28565
4525.3125 | 122.2092 | -0.10529 | 122.1634 | 0.19511 | 0.064792 | 0.061258 | 0.066553 | 0.077466 | 0.15426 | 0.056315 | 122.1564 | 122.0955 | 0.27963 | 0.2279 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.30039 | 0.17008 | 0.16654 | 0.17184 | 0.18275 | 0.25955 | 0.1616 | 122.1976 | 122.1367 | 0.32083 | 0.2691 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 122.1631 | 122.1899 | 0.28634 | 0.31312
4527.0781 | 122.2504 | -0.082397 | 122.1497 | 0.218 | 0.096844 | 0.093308 | 0.084867 | 0.10493 | 0.17715 | 0.079206 | 122.1655 | 122.1001 | 4.7343 | 4.6421 | -0.015859 | 0.032376 | -0.024328 | -0.00775 | 0.30039 | 0.17924 | 0.17571 | 0.16726 | 0.18733 | 0.25955 | 0.1616 | 122.2067 | 122.1413 | 4.7755 | 4.6833 | 0.02534 | 0.073575 | 0.016871 | 0.033449 | 122.1814 | 122.1899 | 4.7502 | 4.7586
4528.8438 | 122.2504 | -0.068665 | 122.1817 | 0.218 | 0.087686 | 0.084151 | 0.084867 | 0.10036 | 0.16799 | 0.083784 | 122.1747 | 122.1047 | 4.6931 | 4.5917 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.28666 | 0.15635 | 0.15282 | 0.15353 | 0.16902 | 0.23666 | 0.15245 | 122.2159 | 122.1459 | 4.7343 | 4.6329 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.186 | 122.2082 | 4.7044 | 4.7266
4530.5938 | 122.2687 | -0.082397 | 122.1771 | 0.218 | 0.10142 | 0.084151 | 0.084867 | 0.095778 | 0.17257 | 0.079206 | 122.1701 | 122.1184 | 4.7114 | 4.6284 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 0.30039 | 0.18382 | 0.16655 | 0.16726 | 0.17818 | 0.25497 | 0.1616 | 122.2113 | 122.1596 | 4.7526 | 4.6696 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 122.1814 | 122.2036 | 4.7227 | 4.7449
4532.2969 | 122.3557 | -0.07782 | 122.1497 | 0.218 | 0.10142 | 0.084151 | 0.089445 | 0.095778 | 0.17715 | 0.079206 | 122.1884 | 122.1276 | 4.1712 | 4.0743 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.29582 | 0.17924 | 0.16197 | 0.16726 | 0.1736 | 0.25497 | 0.15703 | 122.2296 | 122.1688 | 4.2124 | 4.1155 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.1997 | 122.2219 | 4.1825 | 4.2047
4534.0156 | 122.3511 | -0.054932 | 122.1725 | 0.20426 | 0.087686 | 0.074994 | 0.071132 | 0.0912 | 0.17257 | 0.074628 | 122.1793 | 122.1184 | 3.4066 | 3.3096 | -0.011281 | 0.027798 | -0.019749 | 0.001406 | 0.25919 | 0.14262 | 0.12993 | 0.12606 | 0.14613 | 0.2275 | 0.12956 | 122.2205 | 122.1596 | 3.4478 | 3.3508 | 0.029918 | 0.068997 | 0.02145 | 0.042605 | 122.1905 | 122.199 | 3.4179 | 3.4263
4535.7969 | 122.3145 | -0.064087 | 122.1451 | 0.218 | 0.092265 | 0.079572 | 0.084867 | 0.10493 | 0.17257 | 0.083784 | 122.1884 | 122.123 | 4.162 | 4.0743 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 0.28208 | 0.15635 | 0.14366 | 0.14895 | 0.16902 | 0.23666 | 0.14787 | 122.2296 | 122.1642 | 4.2032 | 4.1155 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 122.1951 | 122.2219 | 4.1687 | 4.1955
4537.5625 | 122.3373 | -0.064087 | 122.2 | 0.19968 | 0.07395 | 0.065837 | 0.066553 | 0.077466 | 0.15426 | 0.065472 | 122.193 | 122.1276 | 0.27048 | 0.20501 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 0.26377 | 0.13804 | 0.12992 | 0.13064 | 0.14155 | 0.21835 | 0.12956 | 122.2342 | 122.1688 | 0.31168 | 0.24621 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 122.1997 | 122.2265 | 0.27718 | 0.30396
4539.2812 | 122.3602 | -0.059509 | 122.1634 | 0.19511 | 0.07395 | 0.065837 | 0.071132 | 0.086622 | 0.15426 | 0.065472 | 122.1976 | 122.1276 | 0.22927 | 0.15922 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 0.25461 | 0.13346 | 0.12535 | 0.13064 | 0.14613 | 0.21377 | 0.12498 | 122.2388 | 122.1688 | 0.27047 | 0.20042 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 122.2043 | 122.2265 | 0.23597 | 0.25818
4541.0625 | 122.3877 | -0.050354 | 122.1451 | 0.19968 | 0.07395 | 0.061258 | 0.071132 | 0.086622 | 0.15884 | 0.07005 | 122.2022 | 122.1322 | 0.23385 | 0.1638 | -0.002124 | 0.02322 | -0.033484 | 0.001406 | 0.25004 | 0.1243 | 0.11161 | 0.12149 | 0.13698 | 0.20919 | 0.1204 | 122.2434 | 122.1734 | 0.27505 | 0.205 | 0.039075 | 0.064419 | 0.007715 | 0.042605 | 122.2043 | 122.2356 | 0.23597 | 0.26733
4542.7812 | 122.3511 | -0.064087 | 122.168 | 0.19511 | 0.078529 | 0.061258 | 0.066553 | 0.072888 | 0.15884 | 0.056315 | 122.2067 | 122.1367 | 0.24759 | 0.17296 | -0.006702 | 0.027798 | -0.038063 | 0.001406 | 0.25919 | 0.14262 | 0.12535 | 0.13064 | 0.13698 | 0.22292 | 0.1204 | 122.2479 | 122.1779 | 0.28879 | 0.21415 | 0.034497 | 0.068997 | 0.003136 | 0.042605 | 122.2134 | 122.2448 | 0.25429 | 0.28565
4544.5625 | 122.2824 | -0.082397 | 122.2137 | 0.19968 | 0.07395 | 0.065837 | 0.07571 | 0.0912 | 0.16342 | 0.060893 | 122.2022 | 122.1322 | 0.25674 | 0.18211 | -0.006702 | 0.02322 | -0.028906 | 0.001406 | 0.28208 | 0.15635 | 0.14823 | 0.15811 | 0.1736 | 0.24581 | 0.14329 | 122.2434 | 122.1734 | 0.29794 | 0.22331 | 0.034497 | 0.064419 | 0.012293 | 0.042605 | 122.2089 | 122.2311 | 0.26344 | 0.28565
4546.3125 | 122.2916 | -0.10071 | 122.2183 | 0.20426 | 0.083107 | 0.074994 | 0.071132 | 0.082044 | 0.15426 | 0.065472 | 122.2022 | 122.1367 | 0.25674 | 0.20043 | -0.011281 | 0.036954 | -0.038063 | -0.003172 | 0.30497 | 0.18382 | 0.1757 | 0.17184 | 0.18275 | 0.25497 | 0.16618 | 122.2434 | 122.1779 | 0.29794 | 0.24163 | 0.029918 | 0.078153 | 0.003136 | 0.038027 | 122.2134 | 122.2402 | 0.26802 | 0.29481
4548.0781 | 122.406 | -0.054932 | 122.1863 | 0.20884 | 0.078529 | 0.074994 | 0.071132 | 0.086622 | 0.15884 | 0.07005 | 122.2022 | 122.1459 | 0.25216 | 0.16838 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.26377 | 0.13346 | 0.12993 | 0.12606 | 0.14155 | 0.21377 | 0.12498 | 122.2434 | 122.1871 | 0.29336 | 0.20958 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.218 | 122.2311 | 0.26802 | 0.28107
4549.8438 | 122.3969 | -0.045776 | 122.1542 | 0.20884 | 0.078529 | 0.070415 | 0.071132 | 0.0912 | 0.16342 | 0.065472 | 122.2113 | 122.1413 | 0.27963 | 0.19585 | 0.002454 | 0.027798 | -0.033484 | 0.005985 | 0.25462 | 0.1243 | 0.11619 | 0.11691 | 0.13698 | 0.20919 | 0.11125 | 122.2525 | 122.1825 | 0.32083 | 0.23705 | 0.043653 | 0.068997 | 0.007715 | 0.047184 | 122.2089 | 122.2448 | 0.27718 | 0.31312
4551.5469 | 122.2824 | -0.10071 | 122.2 | 0.20426 | 0.078529 | 0.074994 | 0.07571 | 0.086622 | 0.15426 | 0.065472 | 122.2067 | 122.1413 | 0.25216 | 0.18211 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.30497 | 0.17924 | 0.1757 | 0.17642 | 0.18733 | 0.25497 | 0.16618 | 122.2479 | 122.1825 | 0.29336 | 0.22331 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.2134 | 122.2402 | 0.25887 | 0.28565
4553.2969 | 122.3007 | -0.073242 | 122.2275 | 0.19511 | 0.07395 | 0.070415 | 0.066553 | 0.082044 | 0.15884 | 0.074628 | 122.2113 | 122.1505 | 0.25216 | 0.17753 | -0.006702 | 0.02322 | -0.033484 | 0.010563 | 0.26835 | 0.14719 | 0.14366 | 0.1398 | 0.15529 | 0.23208 | 0.14787 | 122.2525 | 122.1917 | 0.29336 | 0.21873 | 0.034497 | 0.064419 | 0.007715 | 0.051762 | 122.218 | 122.2448 | 0.25887 | 0.28565
4555 | 122.3145 | -0.073242 | 122.2046 | 0.19968 | 0.083107 | 0.070415 | 0.07571 | 0.086622 | 0.16342 | 0.065472 | 122.2159 | 122.1505 | 0.27048 | 0.20043 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 0.27293 | 0.15635 | 0.14366 | 0.14895 | 0.15986 | 0.23666 | 0.13871 | 122.2571 | 122.1917 | 0.31168 | 0.24163 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 122.2272 | 122.2494 | 0.28176 | 0.30396
4556.7656 | 122.3511 | -0.07782 | 122.2 | 0.19968 | 0.083107 | 0.074994 | 0.071132 | 0.082044 | 0.14968 | 0.065472 | 122.2113 | 122.1413 | 0.28421 | 0.22332 | -0.002124 | 0.027798 | -0.033484 | 0.005985 | 0.2775 | 0.16093 | 0.15281 | 0.14895 | 0.15986 | 0.2275 | 0.14329 | 122.2525 | 122.1825 | 0.32541 | 0.26452 | 0.039075 | 0.068997 | 0.007715 | 0.047184 | 122.2134 | 122.2448 | 0.28634 | 0.3177
4558.5469 | 122.3969 | -0.050354 | 122.1817 | 0.20426 | 0.078529 | 0.074994 | 0.071132 | 0.082044 | 0.15884 | 0.060893 | 122.2113 | 122.1459 | 0.28421 | 0.20501 | -0.006702 | 0.027798 | -0.033484 | 0.005985 | 0.25462 | 0.12888 | 0.12535 | 0.12149 | 0.1324 | 0.20919 | 0.11125 | 122.2525 | 122.1871 | 0.32541 | 0.24621 | 0.034497 | 0.068997 | 0.007715 | 0.047184 | 122.218 | 122.2448 | 0.29091 | 0.3177
4560.3125 | 122.2733 | -0.10986 | 122.2137 | 0.20426 | 0.078529 | 0.070415 | 0.080288 | 0.086622 | 0.15884 | 0.060893 | 122.2205 | 122.1551 | 0.28421 | 0.21417 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.31412 | 0.18839 | 0.18028 | 0.19015 | 0.19649 | 0.2687 | 0.17076 | 122.2617 | 122.1963 | 0.32541 | 0.25537 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2318 | 122.254 | 0.29549 | 0.3177
4562.0156 | 122.2595 | -0.10071 | 122.2137 | 0.20426 | 0.078529 | 0.074994 | 0.07571 | 0.0912 | 0.15884 | 0.060893 | 122.2205 | 122.1551 | 0.29795 | 0.2279 | -0.006702 | 0.027798 | -0.028906 | -0.00775 | 0.30497 | 0.17924 | 0.1757 | 0.17642 | 0.19191 | 0.25955 | 0.1616 | 122.2617 | 122.1963 | 0.33915 | 0.2691 | 0.034497 | 0.068997 | 0.012293 | 0.033449 | 122.2272 | 122.2494 | 0.30465 | 0.32685
4563.7188 | 122.3282 | -0.07782 | 122.1771 | 0.19968 | 0.083107 | 0.070415 | 0.07571 | 0.086622 | 0.16342 | 0.060893 | 122.2159 | 122.1551 | 0.30252 | 0.2279 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.2775 | 0.16093 | 0.14824 | 0.15353 | 0.16444 | 0.24124 | 0.13871 | 122.2571 | 122.1963 | 0.34372 | 0.2691 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.2226 | 122.2448 | 0.30923 | 0.33143
4565.4844 | 122.3328 | -0.10529 | 122.2183 | 0.19968 | 0.087686 | 0.070415 | 0.07571 | 0.0912 | 0.15884 | 0.074628 | 122.2205 | 122.1505 | 0.31168 | 0.24622 | -0.011281 | 0.027798 | -0.024328 | -0.003172 | 0.30497 | 0.19297 | 0.1757 | 0.181 | 0.19649 | 0.26412 | 0.17991 | 122.2617 | 122.1917 | 0.35288 | 0.28742 | 0.029918 | 0.068997 | 0.016871 | 0.038027 | 122.2318 | 122.2448 | 0.32296 | 0.33601
4567.1719 | 122.374 | -0.068665 | 122.2092 | 0.19968 | 0.07395 | 0.070415 | 0.071132 | 0.0912 | 0.15426 | 0.07005 | 122.2159 | 122.1551 | 0.28879 | 0.22332 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.26835 | 0.14261 | 0.13908 | 0.1398 | 0.15987 | 0.22292 | 0.13872 | 122.2571 | 122.1963 | 0.32999 | 0.26452 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2272 | 122.2448 | 0.30007 | 0.3177
4568.9375 | 122.4106 | -0.032043 | 122.1863 | 0.19968 | 0.07395 | 0.070415 | 0.071132 | 0.077466 | 0.15884 | 0.065472 | 122.2205 | 122.1505 | 0.31626 | 0.24164 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 0.23173 | 0.10599 | 0.10246 | 0.10318 | 0.10951 | 0.19088 | 0.097515 | 122.2617 | 122.1917 | 0.35746 | 0.28284 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 122.2318 | 122.254 | 0.32754 | 0.34974
4570.7188 | 122.3648 | -0.059509 | 122.1725 | 0.19968 | 0.078529 | 0.061258 | 0.071132 | 0.086622 | 0.15884 | 0.060893 | 122.2159 | 122.1551 | 0.30252 | 0.24622 | -0.015859 | 0.036954 | -0.033484 | -0.003172 | 0.25919 | 0.13804 | 0.12077 | 0.13064 | 0.14613 | 0.21835 | 0.1204 | 122.2571 | 122.1963 | 0.34372 | 0.28742 | 0.02534 | 0.078153 | 0.007715 | 0.038027 | 122.2318 | 122.2494 | 0.31838 | 0.33601
4572.4219 | 122.2824 | -0.11902 | 122.2183 | 0.19968 | 0.07395 | 0.070415 | 0.07571 | 0.082044 | 0.16342 | 0.065472 | 122.2159 | 122.1551 | 0.31626 | 0.24164 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.3187 | 0.19297 | 0.18943 | 0.19473 | 0.20106 | 0.28243 | 0.18449 | 122.2571 | 122.1963 | 0.35746 | 0.28284 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.2272 | 122.2448 | 0.32754 | 0.34517
4574.2031 | 122.3694 | -0.068665 | 122.1817 | 0.19053 | 0.078529 | 0.065837 | 0.066553 | 0.077466 | 0.15426 | 0.065472 | 122.2251 | 122.1505 | 0.32542 | 0.25996 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.25919 | 0.14719 | 0.1345 | 0.13522 | 0.14613 | 0.22292 | 0.13414 | 122.2663 | 122.1917 | 0.36662 | 0.30116 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 122.2363 | 122.2585 | 0.3367 | 0.3589
4575.9688 | 122.3648 | -0.073242 | 122.1954 | 0.19968 | 0.07395 | 0.070415 | 0.071132 | 0.082044 | 0.15426 | 0.065472 | 122.2205 | 122.1596 | 0.29337 | 0.22332 | -0.006702 | 0.036954 | -0.028906 | 0.001406 | 0.27293 | 0.14719 | 0.14366 | 0.14437 | 0.15529 | 0.2275 | 0.13871 | 122.2617 | 122.2008 | 0.33457 | 0.26452 | 0.034497 | 0.078153 | 0.012293 | 0.042605 | 122.2272 | 122.2494 | 0.30007 | 0.32227
4577.7344 | 122.4426 | -0.07782 | 122.1634 | 0.20426 | 0.069371 | 0.065837 | 0.066553 | 0.082044 | 0.14968 | 0.07005 | 122.2205 | 122.1551 | 0.27506 | 0.20501 | -0.002124 | 0.032376 | -0.024328 | 0.001406 | 0.28208 | 0.14719 | 0.14366 | 0.14437 | 0.15986 | 0.2275 | 0.14787 | 122.2617 | 122.1963 | 0.31626 | 0.24621 | 0.039075 | 0.073575 | 0.016871 | 0.042605 | 122.2226 | 122.2448 | 0.27718 | 0.29938
4579.4531 | 122.3923 | -0.045776 | 122.1817 | 0.19968 | 0.078529 | 0.065837 | 0.066553 | 0.0912 | 0.16342 | 0.060893 | 122.2251 | 122.1551 | 0.2659 | 0.20501 | -0.015859 | 0.027798 | -0.028906 | -0.003172 | 0.24546 | 0.1243 | 0.11161 | 0.11233 | 0.13698 | 0.20919 | 0.10667 | 122.2663 | 122.1963 | 0.3071 | 0.24621 | 0.02534 | 0.068997 | 0.012293 | 0.038027 | 122.2409 | 122.254 | 0.28176 | 0.2948
4581.2188 | 122.319 | -0.07782 | 122.2137 | 0.19968 | 0.07395 | 0.065837 | 0.066553 | 0.086622 | 0.15884 | 0.065472 | 122.2296 | 122.1551 | 0.31168 | 0.23706 | -0.002124 | 0.027798 | -0.033484 | -0.003172 | 0.2775 | 0.15177 | 0.14366 | 0.14437 | 0.16444 | 0.23666 | 0.14329 | 122.2708 | 122.1963 | 0.35288 | 0.27826 | 0.039075 | 0.068997 | 0.007715 | 0.038027 | 122.2318 | 122.2631 | 0.31381 | 0.34517
4582.9688 | 122.2961 | -0.10529 | 122.1771 | 0.19511 | 0.060213 | 0.061258 | 0.057396 | 0.06831 | 0.14968 | 0.051737 | 122.2113 | 122.1459 | 0.32084 | 0.25538 | -0.002124 | 0.036954 | 0.03977 | 0.065501 | 0.30039 | 0.1655 | 0.16654 | 0.16268 | 0.1736 | 0.25497 | 0.15702 | 122.2525 | 122.1871 | 0.36204 | 0.29658 | 0.039075 | 0.078153 | 0.080969 | 0.1067 | 122.2134 | 122.1715 | 0.32296 | 0.28107
4584.7344 | 122.4152 | 0.42572 | 122.7081 | 0.22258 | 0.083107 | 0.08873 | 0.084867 | 0.10036 | 0.17257 | 0.07005 | 122.2571 | 122.1917 | 0.32542 | 0.24164 | -0.043328 | 0.00033 | 0.09471 | 0.097548 | -0.20314 | -0.34261 | -0.33699 | -0.34085 | -0.32536 | -0.25315 | -0.35567 | 122.2983 | 122.2329 | 0.36662 | 0.28284 | -0.002129 | 0.041529 | 0.13591 | 0.13875 | 122.3004 | 122.1624 | 0.36874 | 0.23071
4586.4375 | 122.4243 | -0.054932 | 122.1588 | 0.22258 | 0.10142 | 0.08873 | 0.089445 | 0.10036 | 0.17715 | 0.083784 | 122.2479 | 122.178 | 0.27963 | 0.21875 | -0.034171 | 0.009486 | 0.003143 | 0.028875 | 0.27751 | 0.15635 | 0.14366 | 0.14438 | 0.15529 | 0.23208 | 0.13872 | 122.2891 | 122.2192 | 0.32083 | 0.25994 | 0.007028 | 0.050685 | 0.044342 | 0.070074 | 122.2821 | 122.2448 | 0.31381 | 0.27649
4588.2031 | 122.4335 | 0.50812 | 122.8363 | 0.21342 | 0.078529 | 0.070415 | 0.080288 | 0.086622 | 0.16799 | 0.060893 | 122.2388 | 122.1596 | 0.25674 | 0.19127 | -0.020437 | 0.018642 | 0.048926 | 0.056344 | -0.2947 | -0.42959 | -0.4377 | -0.42783 | -0.4215 | -0.34012 | -0.44722 | 122.28 | 122.2008 | 0.29794 | 0.23247 | 0.020762 | 0.059841 | 0.090125 | 0.097543 | 122.2592 | 122.1899 | 0.27718 | 0.20782
4589.9844 | 122.2549 | 0.4303 | 122.7814 | 0.18137 | 0.055634 | 0.056679 | 0.052818 | 0.06831 | 0.1451 | 0.051737 | 122.2067 | 122.1367 | 0.22927 | 0.1638 | 0.002454 | 0.04611 | 0.035191 | 0.065501 | -0.24893 | -0.37466 | -0.37362 | -0.37748 | -0.36199 | -0.2852 | -0.37856 | 122.2479 | 122.1779 | 0.27047 | 0.205 | 0.043653 | 0.087309 | 0.07639 | 0.1067 | 122.2043 | 122.1715 | 0.22682 | 0.19408
4591.75 | 122.4014 | -0.45319 | 121.8063 | 0.19053 | 0.069371 | 0.052101 | 0.057396 | 0.06831 | 0.1451 | 0.056315 | 122.2067 | 122.1459 | 0.23385 | 0.17753 | 0.01161 | 0.041532 | 0.007721 | 0.033454 | 0.64371 | 0.52256 | 0.50529 | 0.51058 | 0.5215 | 0.59829 | 0.5095 | 122.2479 | 122.1871 | 0.27505 | 0.21873 | 0.052809 | 0.082731 | 0.04892 | 0.074653 | 122.1951 | 122.199 | 0.22224 | 0.22613
4593.4531 | 122.287 | 0.46234 | 122.8088 | 0.19968 | 0.07395 | 0.074994 | 0.071132 | 0.082044 | 0.15884 | 0.060893 | 122.2296 | 122.1642 | 0.23385 | 0.17296 | -0.011281 | 0.02322 | 0.035191 | 0.04261 | -0.26266 | -0.38839 | -0.38735 | -0.39121 | -0.3803 | -0.3035 | -0.40145 | 122.2708 | 122.2054 | 0.27505 | 0.21415 | 0.029918 | 0.064419 | 0.07639 | 0.083809 | 122.2409 | 122.1944 | 0.24513 | 0.19866
4595.2188 | 122.2549 | 0.63629 | 122.9645 | 0.12185 | -0.008469 | -0.012 | -0.020438 | -0.009515 | 0.067269 | -0.026092 | 122.1472 | 122.0864 | 0.16518 | 0.099691 | 0.066548 | 0.11478 | 0.14507 | 0.1708 | -0.51444 | -0.64476 | -0.64829 | -0.65673 | -0.64581 | -0.56902 | -0.66238 | 122.1884 | 122.1276 | 0.20638 | 0.14089 | 0.10775 | 0.15598 | 0.18627 | 0.212 | 122.0807 | 122.0021 | 0.098629 | 0.020104
4596.9219 | 122.3648 | -0.59967 | 121.7148 | 0.14474 | 0.005267 | 0.010893 | -0.006703 | 0.013375 | 0.085583 | -0.007779 | 122.1701 | 122.1047 | 0.21096 | 0.14548 | 0.043657 | 0.082735 | 0.20917 | 0.20285 | 0.74441 | 0.60494 | 0.61056 | 0.59297 | 0.61305 | 0.68525 | 0.59189 | 122.2113 | 122.1459 | 0.25216 | 0.18668 | 0.084856 | 0.12393 | 0.25037 | 0.24405 | 122.1265 | 121.9609 | 0.1673 | 0.00179
4598.6875 | 122.3007 | -0.10529 | 122.1909 | 0.19053 | 0.078529 | 0.052101 | 0.066553 | 0.077466 | 0.14968 | 0.051737 | 122.2113 | 122.1505 | 0.28879 | 0.23706 | -0.002124 | 0.04611 | -0.024328 | 0.005985 | 0.29581 | 0.18382 | 0.15739 | 0.17184 | 0.18275 | 0.25497 | 0.15702 | 122.2525 | 122.1917 | 0.32999 | 0.27826 | 0.039075 | 0.087309 | 0.016871 | 0.047184 | 122.2134 | 122.2356 | 0.29092 | 0.31312
4600.3906 | 122.4243 | -0.64545 | 121.5958 | 0.17679 | 0.03274 | 0.038365 | 0.034504 | 0.045421 | 0.12679 | 0.024268 | 122.1976 | 122.1276 | 0.26132 | 0.20501 | 0.025345 | 0.059844 | 0.062662 | 0.079235 | 0.82224 | 0.67819 | 0.68381 | 0.67995 | 0.69087 | 0.77224 | 0.66971 | 122.2388 | 122.1688 | 0.30252 | 0.24621 | 0.066544 | 0.10104 | 0.10386 | 0.12043 | 122.1722 | 122.1349 | 0.23598 | 0.19866
4602.1562 | 122.4335 | -0.35706 | 121.8475 | 0.19053 | 0.069371 | 0.061258 | 0.061975 | 0.072888 | 0.14968 | 0.051737 | 122.2205 | 122.1551 | 0.27506 | 0.22332 | -0.002124 | 0.036954 | 0.030613 | 0.051766 | 0.54758 | 0.42643 | 0.41831 | 0.41903 | 0.42994 | 0.50674 | 0.40879 | 122.2617 | 122.1963 | 0.31626 | 0.26452 | 0.039075 | 0.078153 | 0.071812 | 0.092965 | 122.2226 | 122.1899 | 0.27718 | 0.24444
4603.8594 | 122.3785 | -0.054932 | 122.1817 | 0.19511 | 0.07395 | 0.070415 | 0.066553 | 0.077466 | 0.15884 | 0.056315 | 122.2251 | 122.1596 | 0.28421 | 0.2279 | -0.002124 | 0.032376 | -0.028906 | -0.003172 | 0.25004 | 0.12888 | 0.12535 | 0.12149 | 0.1324 | 0.21377 | 0.11125 | 122.2663 | 122.2008 | 0.32541 | 0.2691 | 0.039075 | 0.073575 | 0.012293 | 0.038027 | 122.2272 | 122.254 | 0.28634 | 0.31312
4605.625 | 122.3145 | -0.091553 | 122.2229 | 0.19511 | 0.078529 | 0.065837 | 0.066553 | 0.082044 | 0.14968 | 0.065472 | 122.2296 | 122.1596 | 0.30252 | 0.24164 | -0.002124 | 0.027798 | -0.024328 | 0.001406 | 0.28666 | 0.17008 | 0.15739 | 0.15811 | 0.1736 | 0.24123 | 0.15702 | 122.2708 | 122.2008 | 0.34372 | 0.28284 | 0.039075 | 0.068997 | 0.016871 | 0.042605 | 122.2318 | 122.254 | 0.30465 | 0.32685
4607.3281 | 122.319 | -0.10071 | 122.2458 | 0.19968 | 0.078529 | 0.061258 | 0.071132 | 0.082044 | 0.15884 | 0.065472 | 122.2251 | 122.1551 | 0.29795 | 0.23706 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 0.30039 | 0.17924 | 0.16197 | 0.17184 | 0.18275 | 0.25955 | 0.16618 | 122.2663 | 122.1963 | 0.33915 | 0.27826 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 122.2318 | 122.2585 | 0.30465 | 0.33143
4609.0938 | 122.3969 | -0.073242 | 122.2046 | 0.19968 | 0.069371 | 0.074994 | 0.066553 | 0.077466 | 0.15884 | 0.056315 | 122.2296 | 122.1551 | 0.30252 | 0.2279 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 0.27293 | 0.14261 | 0.14824 | 0.1398 | 0.15071 | 0.23208 | 0.12956 | 122.2708 | 122.1963 | 0.34372 | 0.2691 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 122.2363 | 122.2585 | 0.30923 | 0.33143
4610.7969 | 122.3099 | -0.09613 | 122.2366 | 0.20426 | 0.078529 | 0.070415 | 0.071132 | 0.086622 | 0.15884 | 0.065472 | 122.2251 | 122.1596 | 0.31626 | 0.25538 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 0.30039 | 0.17466 | 0.16654 | 0.16726 | 0.18275 | 0.25497 | 0.1616 | 122.2663 | 122.2008 | 0.35746 | 0.29658 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 122.2409 | 122.2585 | 0.33212 | 0.34974
4612.5625 | 122.287 | -0.10071 | 122.2046 | 0.19968 | 0.078529 | 0.070415 | 0.061975 | 0.077466 | 0.16342 | 0.065472 | 122.2296 | 122.1642 | 0.31168 | 0.25538 | -0.011281 | 0.032376 | -0.028906 | 0.005985 | 0.30039 | 0.17924 | 0.17112 | 0.16268 | 0.17817 | 0.26412 | 0.16618 | 122.2708 | 122.2054 | 0.35288 | 0.29658 | 0.029918 | 0.073575 | 0.012293 | 0.047184 | 122.2409 | 122.2585 | 0.32296 | 0.34059
4614.3281 | 122.2824 | -0.10071 | 122.2046 | 0.19511 | 0.083107 | 0.070415 | 0.080288 | 0.082044 | 0.15884 | 0.056315 | 122.2251 | 122.1551 | 0.3071 | 0.23706 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 0.29581 | 0.18382 | 0.17112 | 0.181 | 0.18275 | 0.25955 | 0.15702 | 122.2663 | 122.1963 | 0.3483 | 0.27826 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 122.2318 | 122.254 | 0.31381 | 0.33601
4616.0469 | 122.2687 | -0.10986 | 122.2137 | 0.19511 | 0.078529 | 0.065837 | 0.066553 | 0.082044 | 0.15884 | 0.065472 | 122.2251 | 122.1505 | 0.30252 | 0.24164 | -0.011281 | 0.027798 | -0.028906 | 0.001406 | 0.30497 | 0.18839 | 0.1757 | 0.17642 | 0.19191 | 0.2687 | 0.17534 | 122.2663 | 122.1917 | 0.34372 | 0.28284 | 0.029918 | 0.068997 | 0.012293 | 0.042605 | 122.2363 | 122.254 | 0.31381 | 0.33143
4617.75 | 122.3419 | -0.082397 | 122.2183 | 0.20426 | 0.078529 | 0.061258 | 0.07571 | 0.086622 | 0.15884 | 0.060893 | 122.2296 | 122.1596 | 0.3071 | 0.23706 | -0.011281 | 0.032376 | -0.033484 | 0.005985 | 0.28666 | 0.16093 | 0.14366 | 0.15811 | 0.16902 | 0.24123 | 0.14329 | 122.2708 | 122.2008 | 0.3483 | 0.27826 | 0.029918 | 0.073575 | 0.007715 | 0.047184 | 122.2409 | 122.2631 | 0.31838 | 0.34059
4619.5 | 122.3099 | -0.086975 | 122.2137 | 0.19968 | 0.078529 | 0.065837 | 0.066553 | 0.086622 | 0.15884 | 0.060893 | 122.2296 | 122.1551 | 0.31168 | 0.24622 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.28666 | 0.1655 | 0.15281 | 0.15353 | 0.1736 | 0.24581 | 0.14787 | 122.2708 | 122.1963 | 0.35288 | 0.28742 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 122.2409 | 122.2631 | 0.32296 | 0.34517
4621.2656 | 122.3373 | -0.082397 | 122.2275 | 0.20426 | 0.083107 | 0.074994 | 0.071132 | 0.086622 | 0.15426 | 0.07005 | 122.2296 | 122.1596 | 0.31168 | 0.25996 | -0.006702 | 0.032376 | -0.024328 | -0.003172 | 0.28666 | 0.1655 | 0.15739 | 0.15353 | 0.16902 | 0.23666 | 0.15245 | 122.2708 | 122.2008 | 0.35288 | 0.30116 | 0.034497 | 0.073575 | 0.016871 | 0.038027 | 122.2363 | 122.254 | 0.31838 | 0.33601
4622.9688 | 122.3557 | -0.068665 | 122.2412 | 0.20426 | 0.083107 | 0.061258 | 0.080288 | 0.082044 | 0.16342 | 0.07005 | 122.2296 | 122.1596 | 0.32999 | 0.26454 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 0.27293 | 0.15177 | 0.12992 | 0.14895 | 0.15071 | 0.23208 | 0.13872 | 122.2708 | 122.2008 | 0.37119 | 0.30573 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 122.2363 | 122.2585 | 0.3367 | 0.3589
4624.7344 | 122.3007 | -0.1236 | 122.2183 | 0.19968 | 0.078529 | 0.070415 | 0.066553 | 0.086622 | 0.15884 | 0.065472 | 122.2251 | 122.1596 | 0.60469 | 0.52554 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.32328 | 0.20212 | 0.19401 | 0.19015 | 0.21022 | 0.28243 | 0.18907 | 122.2663 | 122.2008 | 0.64589 | 0.56674 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.2363 | 122.254 | 0.61597 | 0.6336
4626.4375 | 122.3923 | -0.059509 | 122.1588 | 0.20426 | 0.069371 | 0.070415 | 0.071132 | 0.082044 | 0.15426 | 0.065472 | 122.2159 | 122.1551 | 0.62301 | 0.55302 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 0.26377 | 0.12888 | 0.12992 | 0.13064 | 0.14155 | 0.21377 | 0.12498 | 122.2571 | 122.1963 | 0.6642 | 0.59421 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 122.2272 | 122.2448 | 0.63429 | 0.65191
4628.2031 | 122.3785 | -0.064087 | 122.1817 | 0.20426 | 0.078529 | 0.074994 | 0.07571 | 0.082044 | 0.15426 | 0.065472 | 122.2251 | 122.1505 | 0.59554 | 0.52554 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 0.26835 | 0.14262 | 0.13908 | 0.1398 | 0.14613 | 0.21835 | 0.12956 | 122.2663 | 122.1917 | 0.63673 | 0.56674 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 122.2409 | 122.254 | 0.61139 | 0.62444
4629.9219 | 122.3969 | -0.041199 | 122.1909 | 0.19968 | 0.083107 | 0.070415 | 0.071132 | 0.082044 | 0.14968 | 0.065472 | 122.2296 | 122.1505 | 0.60469 | 0.53012 | -0.002124 | 0.036954 | -0.028906 | 0.001406 | 0.24088 | 0.12431 | 0.11161 | 0.11233 | 0.12324 | 0.19088 | 0.10667 | 122.2708 | 122.1917 | 0.64589 | 0.57132 | 0.039075 | 0.078153 | 0.012293 | 0.042605 | 122.2318 | 122.2585 | 0.60682 | 0.6336
4631.6875 | 122.3419 | -0.082397 | 122.2046 | 0.19968 | 0.083107 | 0.070415 | 0.07571 | 0.086622 | 0.15884 | 0.07005 | 122.2159 | 122.1551 | 0.54975 | 0.48433 | -0.006702 | 0.032376 | -0.024328 | 0.001406 | 0.28208 | 0.1655 | 0.15281 | 0.15811 | 0.16902 | 0.24123 | 0.15245 | 122.2571 | 122.1963 | 0.59095 | 0.52553 | 0.034497 | 0.073575 | 0.016871 | 0.042605 | 122.2226 | 122.2402 | 0.55646 | 0.57408
4633.4375 | 122.3602 | -0.091553 | 122.2137 | 0.20426 | 0.078529 | 0.074994 | 0.071132 | 0.086622 | 0.16342 | 0.060893 | 122.2159 | 122.1551 | 0.59554 | 0.52554 | -0.006702 | 0.032376 | -0.028906 | 0.005985 | 0.29581 | 0.17008 | 0.16655 | 0.16268 | 0.17818 | 0.25497 | 0.15245 | 122.2571 | 122.1963 | 0.63673 | 0.56674 | 0.034497 | 0.073575 | 0.012293 | 0.047184 | 122.2226 | 122.2448 | 0.60224 | 0.62444
4635.2031 | 122.319 | -0.15564 | 122.1405 | 0.21342 | 0.083107 | 0.08873 | 0.080288 | 0.0912 | 0.16799 | 0.074628 | 122.2251 | 122.1596 | 0.74662 | 0.67207 | -0.015859 | 0.027798 | 0.062662 | 0.079235 | 0.36906 | 0.23875 | 0.24437 | 0.23593 | 0.24684 | 0.32363 | 0.23027 | 122.2663 | 122.2008 | 0.78782 | 0.71327 | 0.02534 | 0.068997 | 0.10386 | 0.12043 | 122.2409 | 122.1624 | 0.76248 | 0.68396
4636.9062 | 122.374 | -0.52643 | 121.7468 | 0.17679 | 0.041898 | 0.047522 | 0.048239 | 0.054577 | 0.12221 | 0.024268 | 122.193 | 122.1322 | 0.5818 | 0.50265 | 0.01161 | 0.055266 | 0.15881 | 0.15706 | 0.70322 | 0.56833 | 0.57395 | 0.57467 | 0.581 | 0.64864 | 0.5507 | 122.2342 | 122.1734 | 0.623 | 0.54385 | 0.052809 | 0.096465 | 0.20001 | 0.19826 | 122.1814 | 122.0342 | 0.57019 | 0.42299
4638.6719 | 122.2412 | -0.29755 | 121.9894 | 0.19511 | 0.051056 | 0.070415 | 0.057396 | 0.06831 | 0.13137 | 0.038003 | 122.2067 | 122.1413 | 0.57264 | 0.5118 | 0.002454 | 0.041532 | 0.1817 | 0.16622 | 0.49265 | 0.3486 | 0.36796 | 0.35494 | 0.36586 | 0.42891 | 0.33555 | 122.2479 | 122.1825 | 0.61384 | 0.553 | 0.043653 | 0.082731 | 0.2229 | 0.20742 | 122.2043 | 122.025 | 0.57019 | 0.39094
4640.375 | 122.3923 | -0.78735 | 121.4813 | 0.19511 | 0.041898 | 0.061258 | 0.039082 | 0.054577 | 0.13137 | 0.033424 | 122.2022 | 122.1413 | 0.58638 | 0.52096 | 0.007032 | 0.04611 | 0.1817 | 0.18911 | 0.98246 | 0.82925 | 0.84861 | 0.82644 | 0.84193 | 0.91872 | 0.82078 | 122.2434 | 122.1825 | 0.62758 | 0.56216 | 0.048231 | 0.087309 | 0.2229 | 0.23031 | 122.1951 | 122.0205 | 0.57935 | 0.40468
4642.1406 | 122.4152 | 0.16937 | 122.4564 | 0.18137 | 0.041898 | 0.056679 | 0.043661 | 0.054577 | 0.12221 | 0.024268 | 122.1976 | 122.1322 | 0.65505 | 0.59423 | 0.01161 | 0.055266 | 0.18628 | 0.15706 | 0.011997 | -0.12748 | -0.11269 | -0.12571 | -0.1148 | -0.047163 | -0.1451 | 122.2388 | 122.1734 | 0.69625 | 0.63543 | 0.052809 | 0.096465 | 0.22748 | 0.19826 | 122.186 | 122.0113 | 0.64344 | 0.46877
4643.8438 | 122.3007 | -0.84686 | 121.4447 | 0.20426 | 0.060213 | 0.074994 | 0.057396 | 0.072888 | 0.14052 | 0.042581 | 122.2159 | 122.1551 | 0.62301 | 0.54386 | -0.011281 | 0.027798 | 0.19086 | 0.16622 | 1.0511 | 0.90708 | 0.92186 | 0.90426 | 0.91975 | 0.98739 | 0.88944 | 122.2571 | 122.1963 | 0.6642 | 0.58506 | 0.029918 | 0.068997 | 0.23206 | 0.20742 | 122.2272 | 122.025 | 0.63429 | 0.43215
4645.6094 | 122.2641 | -0.52643 | 121.7056 | 0.218 | 0.069371 | 0.079572 | 0.066553 | 0.077466 | 0.14968 | 0.056315 | 122.2251 | 122.1551 | 0.75577 | 0.69039 | -0.011281 | 0.018642 | 0.19086 | 0.17538 | 0.74443 | 0.5958 | 0.606 | 0.59298 | 0.60389 | 0.67611 | 0.58274 | 122.2663 | 122.1963 | 0.79697 | 0.73159 | 0.029918 | 0.059841 | 0.23206 | 0.21658 | 122.2363 | 122.0342 | 0.76706 | 0.56492
4647.375 | 122.3694 | -0.6958 | 121.5454 | 0.20426 | 0.055634 | 0.074994 | 0.061975 | 0.077466 | 0.14052 | 0.042581 | 122.2205 | 122.1596 | 0.64132 | 0.56675 | -0.011281 | 0.032376 | 0.19086 | 0.15249 | 0.90006 | 0.75143 | 0.7708 | 0.75778 | 0.77327 | 0.83632 | 0.73838 | 122.2617 | 122.2008 | 0.68252 | 0.60795 | 0.029918 | 0.073575 | 0.23206 | 0.19368 | 122.2318 | 122.0296 | 0.6526 | 0.45046
4649.125 | 122.2641 | -0.082397 | 122.2366 | 0.17679 | 0.041898 | 0.042944 | 0.039082 | 0.049999 | 0.12679 | 0.028846 | 122.1747 | 122.123 | 0.70541 | 0.6446 | 0.016188 | 0.055266 | 0.062662 | 0.047188 | 0.25919 | 0.12429 | 0.12534 | 0.12148 | 0.1324 | 0.20919 | 0.11124 | 122.2159 | 122.1642 | 0.74661 | 0.68579 | 0.057387 | 0.096465 | 0.10386 | 0.088387 | 122.1585 | 122.112 | 0.68923 | 0.64275
4650.8438 | 122.319 | 0.3479 | 122.6303 | 0.13101 | -0.00389 | -0.002842 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 122.1381 | 122.0726 | 0.54517 | 0.50265 | 0.06197 | 0.1102 | 0.12218 | 0.09297 | -0.21689 | -0.35179 | -0.35074 | -0.35002 | -0.34368 | -0.26689 | -0.36026 | 122.1793 | 122.1138 | 0.58637 | 0.54385 | 0.10317 | 0.1514 | 0.16338 | 0.13417 | 122.0761 | 122.0159 | 0.4832 | 0.42299
4652.6094 | 122.406 | -0.49896 | 121.6873 | 0.19968 | 0.064792 | 0.065837 | 0.061975 | 0.072888 | 0.14968 | 0.060893 | 122.2113 | 122.1367 | 0.65505 | 0.59881 | -0.002124 | 0.032376 | 0.099289 | 0.024297 | 0.69865 | 0.56375 | 0.5648 | 0.56094 | 0.57185 | 0.64864 | 0.55985 | 122.2525 | 122.1779 | 0.69625 | 0.64 | 0.039075 | 0.073575 | 0.14049 | 0.065496 | 122.2134 | 122.112 | 0.65718 | 0.55576
4654.3594 | 122.4152 | -0.064087 | 122.1359 | 0.16306 | 0.023583 | 0.029208 | 0.029925 | 0.027109 | 0.1039 | 0.015112 | 122.1701 | 122.0955 | 0.56807 | 0.5347 | 0.029923 | 0.069001 | 0.16797 | 0.16622 | 0.22714 | 0.08767 | 0.093295 | 0.094012 | 0.091196 | 0.16798 | 0.079199 | 122.2113 | 122.1367 | 0.60926 | 0.5759 | 0.071122 | 0.1102 | 0.20916 | 0.20742 | 122.1402 | 122.0021 | 0.53814 | 0.4001
4656.0625 | 122.3145 | 0.091553 | 122.3648 | 0.18137 | 0.055634 | 0.056679 | 0.057396 | 0.06831 | 0.14052 | 0.038003 | 122.1884 | 122.123 | 0.72373 | 0.67207 | 0.01161 | 0.055266 | 0.090132 | 0.028875 | 0.089817 | -0.035919 | -0.034874 | -0.034157 | -0.023243 | 0.048971 | -0.05355 | 122.2296 | 122.1642 | 0.76493 | 0.71327 | 0.052809 | 0.096465 | 0.13133 | 0.070074 | 122.1768 | 122.0983 | 0.71212 | 0.6336
4657.8281 | 122.3465 | 0.33417 | 122.5983 | 0.19511 | 0.051056 | 0.061258 | 0.057396 | 0.059155 | 0.13595 | 0.042581 | 122.193 | 122.1367 | 0.60927 | 0.54386 | -0.002124 | 0.04611 | 0.18628 | 0.038032 | -0.13906 | -0.28311 | -0.27291 | -0.27677 | -0.27501 | -0.19822 | -0.29159 | 122.2342 | 122.1779 | 0.65047 | 0.58506 | 0.039075 | 0.087309 | 0.22748 | 0.079231 | 122.1951 | 122.0067 | 0.61139 | 0.42299
4659.5938 | 122.4152 | -0.25177 | 122.0398 | 0.16306 | 0.028162 | 0.029208 | 0.029925 | 0.040843 | 0.11305 | 0.010533 | 122.161 | 122.0955 | 0.61385 | 0.56675 | 0.025345 | 0.069001 | 0.11302 | 0.097548 | 0.41483 | 0.27993 | 0.28098 | 0.28169 | 0.29261 | 0.36482 | 0.2623 | 122.2022 | 122.1367 | 0.65505 | 0.60795 | 0.066544 | 0.1102 | 0.15422 | 0.13875 | 122.1356 | 122.0479 | 0.5885 | 0.50082
4661.2969 | 122.3511 | 0.018311 | 122.2733 | 0.19968 | 0.078529 | 0.070415 | 0.07571 | 0.077466 | 0.16799 | 0.060893 | 122.1976 | 122.1322 | 0.55433 | 0.48433 | -0.020437 | 0.02322 | 0.012299 | 0.015141 | 0.18137 | 0.060218 | 0.052104 | 0.057399 | 0.059155 | 0.14968 | 0.042582 | 122.2388 | 122.1734 | 0.59553 | 0.52553 | 0.020762 | 0.064419 | 0.053498 | 0.05634 | 122.218 | 122.1853 | 0.57477 | 0.54203
4663 | 122.4976 | 0.032043 | 122.2504 | 0.20884 | 0.07395 | 0.074994 | 0.061975 | 0.063733 | 0.15426 | 0.047159 | 122.2067 | 122.1322 | 0.5177 | 0.47517 | -0.011281 | 0.027798 | 0.10845 | 0.088392 | 0.1768 | 0.041907 | 0.042951 | 0.029932 | 0.03169 | 0.12222 | 0.015116 | 122.2479 | 122.1734 | 0.5589 | 0.51637 | 0.029918 | 0.068997 | 0.14965 | 0.12959 | 122.218 | 122.0983 | 0.52899 | 0.40926
4664.7656 | 122.3282 | 0.63629 | 122.937 | 0.20884 | 0.060213 | 0.084151 | 0.066553 | 0.077466 | 0.1451 | 0.047159 | 122.2022 | 122.1459 | 0.55433 | 0.47975 | -0.011281 | 0.02322 | 0.20001 | 0.15249 | -0.42745 | -0.57608 | -0.55214 | -0.56974 | -0.55883 | -0.49119 | -0.58913 | 122.2434 | 122.1871 | 0.59553 | 0.52095 | 0.029918 | 0.064419 | 0.24121 | 0.19368 | 122.2134 | 122.0021 | 0.56561 | 0.35432
4666.5469 | 122.2549 | -0.51727 | 121.7422 | 0.21342 | 0.064792 | 0.084151 | 0.07571 | 0.077466 | 0.15426 | 0.056315 | 122.2067 | 122.1367 | 0.4765 | 0.41564 | -0.002124 | 0.032376 | 0.19543 | 0.14333 | 0.73069 | 0.58206 | 0.60142 | 0.59298 | 0.59474 | 0.67153 | 0.57359 | 122.2479 | 122.1779 | 0.5177 | 0.45684 | 0.039075 | 0.073575 | 0.23663 | 0.18453 | 122.2089 | 122.0113 | 0.47862 | 0.28107
4668.3125 | 122.3145 | 0.7782 | 123.1338 | 0.19053 | 0.051056 | 0.056679 | 0.052818 | 0.063733 | 0.13137 | 0.042581 | 122.193 | 122.123 | 0.44445 | 0.36985 | 0.016188 | 0.050688 | 0.21375 | 0.18911 | -0.58767 | -0.72714 | -0.72152 | -0.72538 | -0.71446 | -0.64683 | -0.73562 | 122.2342 | 122.1642 | 0.48565 | 0.41105 | 0.057387 | 0.091887 | 0.25495 | 0.23031 | 122.1768 | 121.9793 | 0.42826 | 0.2307
4670.0156 | 122.287 | -0.13733 | 122.1725 | 0.17679 | 0.055634 | 0.042944 | 0.048239 | 0.063733 | 0.14052 | 0.038003 | 122.1701 | 122.1093 | 0.42156 | 0.35612 | 0.029923 | 0.073579 | -0.010593 | 0.028875 | 0.31412 | 0.19296 | 0.18027 | 0.18557 | 0.20106 | 0.27785 | 0.17533 | 122.2113 | 122.1505 | 0.46276 | 0.39732 | 0.071122 | 0.11478 | 0.030606 | 0.070074 | 122.1402 | 122.1807 | 0.39164 | 0.43215
4671.7812 | 122.3831 | -0.082397 | 122.1222 | 0.17221 | 0.046477 | 0.047522 | 0.043661 | 0.063733 | 0.13137 | 0.038003 | 122.1655 | 122.1047 | 0.39867 | 0.32864 | 0.020767 | 0.064423 | -0.006014 | 0.019719 | 0.25461 | 0.12887 | 0.12992 | 0.12606 | 0.14613 | 0.21376 | 0.1204 | 122.2067 | 122.1459 | 0.43987 | 0.36984 | 0.061966 | 0.10562 | 0.035185 | 0.060918 | 122.1448 | 122.1715 | 0.3779 | 0.40468
4673.5469 | 122.2595 | -0.13275 | 122.1909 | 0.17679 | 0.051056 | 0.038365 | 0.048239 | 0.054577 | 0.13137 | 0.038003 | 122.1564 | 122.1001 | 0.39409 | 0.3378 | 0.034501 | 0.069001 | -0.010593 | 0.015141 | 0.30954 | 0.18381 | 0.17112 | 0.18099 | 0.18733 | 0.26412 | 0.17075 | 122.1976 | 122.1413 | 0.43529 | 0.379 | 0.0757 | 0.1102 | 0.030606 | 0.05634 | 122.1219 | 122.167 | 0.35959 | 0.40468
4675.25 | 122.4243 | -0.086975 | 122.113 | 0.17221 | 0.051056 | 0.042944 | 0.048239 | 0.059155 | 0.13137 | 0.038003 | 122.161 | 122.1047 | 0.38036 | 0.31491 | 0.029923 | 0.073579 | -0.006014 | 0.019719 | 0.25919 | 0.13803 | 0.12992 | 0.13521 | 0.14613 | 0.21834 | 0.12498 | 122.2022 | 122.1459 | 0.42156 | 0.35611 | 0.071122 | 0.11478 | 0.035185 | 0.060918 | 122.131 | 122.167 | 0.35043 | 0.38637
4676.9688 | 122.3373 | -0.091553 | 122.1497 | 0.18137 | 0.051056 | 0.047522 | 0.043661 | 0.059155 | 0.13595 | 0.033424 | 122.161 | 122.1001 | 0.29337 | 0.23248 | 0.025345 | 0.073579 | -0.010593 | 0.015141 | 0.27292 | 0.14261 | 0.13908 | 0.13521 | 0.15071 | 0.2275 | 0.12498 | 122.2022 | 122.1413 | 0.33457 | 0.27368 | 0.066544 | 0.11478 | 0.030606 | 0.05634 | 122.1356 | 122.1715 | 0.26802 | 0.30396
4678.7344 | 122.3419 | -0.091553 | 122.1405 | 0.17221 | 0.055634 | 0.047522 | 0.052818 | 0.059155 | 0.13137 | 0.038003 | 122.161 | 122.0955 | 0.27963 | 0.21417 | 0.029923 | 0.069001 | -0.006014 | 0.010563 | 0.26377 | 0.14719 | 0.13908 | 0.14437 | 0.15071 | 0.22292 | 0.12956 | 122.2022 | 122.1367 | 0.32083 | 0.25537 | 0.071122 | 0.1102 | 0.035185 | 0.051762 | 122.131 | 122.167 | 0.24971 | 0.28565
4680.5 | 122.3145 | -0.10529 | 122.1634 | 0.17221 | 0.055634 | 0.047522 | 0.052818 | 0.059155 | 0.14052 | 0.033424 | 122.1655 | 122.1047 | 0.27963 | 0.2279 | 0.025345 | 0.069001 | -0.010593 | 0.019719 | 0.2775 | 0.16092 | 0.15281 | 0.1581 | 0.16444 | 0.24581 | 0.13871 | 122.2067 | 122.1459 | 0.32083 | 0.2691 | 0.066544 | 0.1102 | 0.030606 | 0.060918 | 122.1402 | 122.1761 | 0.25429 | 0.29023
4682.2812 | 122.3969 | -0.073242 | 122.1313 | 0.17221 | 0.051056 | 0.047522 | 0.048239 | 0.06831 | 0.12679 | 0.038003 | 122.161 | 122.0955 | 0.27963 | 0.21875 | 0.025345 | 0.078157 | -0.015171 | 0.019719 | 0.24546 | 0.1243 | 0.12076 | 0.12148 | 0.14155 | 0.20003 | 0.11125 | 122.2022 | 122.1367 | 0.32083 | 0.25994 | 0.066544 | 0.11936 | 0.026028 | 0.060918 | 122.1356 | 122.1761 | 0.25429 | 0.2948
4684.0469 | 122.406 | -0.091553 | 122.1359 | 0.18137 | 0.060213 | 0.052101 | 0.052818 | 0.063733 | 0.13595 | 0.047159 | 122.1564 | 122.0955 | 0.28421 | 0.22332 | 0.029923 | 0.064423 | -0.015171 | 0.019719 | 0.27292 | 0.15177 | 0.14365 | 0.14437 | 0.15529 | 0.2275 | 0.13871 | 122.1976 | 122.1367 | 0.32541 | 0.26452 | 0.071122 | 0.10562 | 0.026028 | 0.060918 | 122.1265 | 122.1715 | 0.25429 | 0.29938
4685.7656 | 122.3465 | -0.09613 | 122.1405 | 0.18137 | 0.064792 | 0.042944 | 0.057396 | 0.063733 | 0.13595 | 0.038003 | 122.1655 | 122.0955 | 0.27048 | 0.21417 | 0.025345 | 0.069001 | -0.010593 | 0.019719 | 0.2775 | 0.16092 | 0.13907 | 0.15353 | 0.15986 | 0.23208 | 0.13413 | 122.2067 | 122.1367 | 0.31168 | 0.25537 | 0.066544 | 0.1102 | 0.030606 | 0.060918 | 122.1402 | 122.1761 | 0.24513 | 0.28107
4687.5469 | 122.3465 | -0.11902 | 122.1359 | 0.17679 | 0.060213 | 0.056679 | 0.052818 | 0.063733 | 0.14052 | 0.042581 | 122.1518 | 122.091 | 0.26132 | 0.21417 | 0.029923 | 0.073579 | -0.010593 | 0.028875 | 0.29581 | 0.17923 | 0.1757 | 0.17184 | 0.18275 | 0.25954 | 0.1616 | 122.193 | 122.1322 | 0.30252 | 0.25537 | 0.071122 | 0.11478 | 0.030606 | 0.070074 | 122.1219 | 122.1624 | 0.2314 | 0.27191
4689.3125 | 122.2504 | -0.1236 | 122.1451 | 0.18137 | 0.051056 | 0.056679 | 0.057396 | 0.059155 | 0.1451 | 0.038003 | 122.1518 | 122.091 | 0.27048 | 0.20959 | 0.029923 | 0.069001 | -0.010593 | 0.028875 | 0.30497 | 0.17465 | 0.18027 | 0.18099 | 0.18275 | 0.2687 | 0.1616 | 122.193 | 122.1322 | 0.31168 | 0.25079 | 0.071122 | 0.1102 | 0.030606 | 0.070074 | 122.1219 | 122.1624 | 0.24055 | 0.28107
4691.0156 | 122.3099 | -0.12817 | 122.1588 | 0.18137 | 0.060213 | 0.042944 | 0.057396 | 0.063733 | 0.13595 | 0.047159 | 122.1564 | 122.0955 | 0.26132 | 0.20501 | 0.025345 | 0.073579 | -0.006014 | 0.024297 | 0.30954 | 0.18839 | 0.17112 | 0.18557 | 0.19191 | 0.26412 | 0.17533 | 122.1976 | 122.1367 | 0.30252 | 0.24621 | 0.066544 | 0.11478 | 0.035185 | 0.065496 | 122.131 | 122.1624 | 0.23598 | 0.26734
4692.7812 | 122.3648 | -0.10986 | 122.1313 | 0.18137 | 0.064792 | 0.052101 | 0.052818 | 0.059155 | 0.13137 | 0.038003 | 122.161 | 122.0864 | 0.26132 | 0.19585 | 0.029923 | 0.064423 | -0.010593 | 0.019719 | 0.29123 | 0.17466 | 0.16196 | 0.16268 | 0.16902 | 0.24123 | 0.14787 | 122.2022 | 122.1276 | 0.30252 | 0.23705 | 0.071122 | 0.10562 | 0.030606 | 0.060918 | 122.131 | 122.1715 | 0.2314 | 0.27191
4694.5469 | 122.2366 | -0.14191 | 122.1497 | 0.17679 | 0.060213 | 0.042944 | 0.057396 | 0.063733 | 0.14052 | 0.047159 | 122.1564 | 122.0955 | 0.25216 | 0.19127 | 0.029923 | 0.073579 | -0.015171 | 0.024297 | 0.3187 | 0.20212 | 0.18485 | 0.1993 | 0.20564 | 0.28243 | 0.18907 | 122.1976 | 122.1367 | 0.29336 | 0.23247 | 0.071122 | 0.11478 | 0.026028 | 0.065496 | 122.1265 | 122.1715 | 0.22224 | 0.26733
4696.3125 | 122.3007 | -0.1236 | 122.1451 | 0.18137 | 0.055634 | 0.047522 | 0.052818 | 0.06831 | 0.13595 | 0.047159 | 122.1564 | 122.0955 | 0.25216 | 0.18669 | 0.025345 | 0.059844 | -0.006014 | 0.019719 | 0.30497 | 0.17923 | 0.17112 | 0.17641 | 0.19191 | 0.25954 | 0.17075 | 122.1976 | 122.1367 | 0.29336 | 0.22789 | 0.066544 | 0.10104 | 0.035185 | 0.060918 | 122.131 | 122.1624 | 0.22682 | 0.25818
4698.0781 | 122.2641 | -0.14191 | 122.1588 | 0.18137 | 0.060213 | 0.047522 | 0.052818 | 0.06831 | 0.13595 | 0.047159 | 122.1472 | 122.091 | 0.24301 | 0.18211 | 0.034501 | 0.069001 | -0.006014 | 0.019719 | 0.32328 | 0.20212 | 0.18943 | 0.19473 | 0.21022 | 0.27785 | 0.18907 | 122.1884 | 122.1322 | 0.28421 | 0.22331 | 0.0757 | 0.1102 | 0.035185 | 0.060918 | 122.1127 | 122.1532 | 0.20851 | 0.24902
4699.7812 | 122.3465 | -0.10071 | 122.113 | 0.18595 | 0.055634 | 0.042944 | 0.057396 | 0.063733 | 0.13595 | 0.042581 | 122.1564 | 122.091 | 0.24759 | 0.18669 | 0.029923 | 0.073579 | -0.015171 | 0.019719 | 0.28666 | 0.15634 | 0.14365 | 0.1581 | 0.16444 | 0.23665 | 0.14329 | 122.1976 | 122.1322 | 0.28879 | 0.22789 | 0.071122 | 0.11478 | 0.026028 | 0.060918 | 122.1265 | 122.1715 | 0.21766 | 0.26276
4701.5469 | 122.374 | -0.091553 | 122.1085 | 0.18137 | 0.060213 | 0.047522 | 0.057396 | 0.06831 | 0.13137 | 0.038003 | 122.1564 | 122.0726 | 0.23843 | 0.18669 | 0.034501 | 0.069001 | -0.010593 | 0.019719 | 0.27292 | 0.15177 | 0.13908 | 0.14895 | 0.15986 | 0.22292 | 0.12956 | 122.1976 | 122.1138 | 0.27963 | 0.22789 | 0.0757 | 0.1102 | 0.030606 | 0.060918 | 122.1219 | 122.167 | 0.20393 | 0.24902
4703.3125 | 122.2458 | -0.14191 | 122.1817 | 0.18137 | 0.060213 | 0.052101 | 0.048239 | 0.063733 | 0.14052 | 0.047159 | 122.1518 | 122.0818 | 0.23843 | 0.18211 | 0.029923 | 0.073579 | -0.015171 | 0.024297 | 0.32328 | 0.20212 | 0.19401 | 0.19015 | 0.20564 | 0.28243 | 0.18907 | 122.193 | 122.123 | 0.27963 | 0.22331 | 0.071122 | 0.11478 | 0.026028 | 0.065496 | 122.1219 | 122.167 | 0.20851 | 0.2536
4705.0781 | 122.3053 | -0.11444 | 122.1451 | 0.18137 | 0.064792 | 0.047522 | 0.057396 | 0.06831 | 0.13595 | 0.047159 | 122.1518 | 122.0772 | 0.23843 | 0.18669 | 0.034501 | 0.069001 | -0.010593 | 0.019719 | 0.29581 | 0.17923 | 0.16196 | 0.17184 | 0.18275 | 0.25039 | 0.1616 | 122.193 | 122.1184 | 0.27963 | 0.22789 | 0.0757 | 0.1102 | 0.030606 | 0.060918 | 122.1173 | 122.1624 | 0.20393 | 0.24902
4706.7812 | 122.3511 | -0.086975 | 122.1268 | 0.18137 | 0.060213 | 0.047522 | 0.057396 | 0.059155 | 0.13595 | 0.038003 | 122.1426 | 122.0726 | 0.24301 | 0.18669 | 0.029923 | 0.073579 | -0.006014 | 0.028875 | 0.26835 | 0.14719 | 0.1345 | 0.14437 | 0.14613 | 0.22292 | 0.12498 | 122.1838 | 122.1138 | 0.28421 | 0.22789 | 0.071122 | 0.11478 | 0.035185 | 0.070074 | 122.1127 | 122.1487 | 0.21308 | 0.24902
4708.5469 | 122.3145 | -0.11444 | 122.113 | 0.18137 | 0.060213 | 0.042944 | 0.052818 | 0.059155 | 0.13595 | 0.047159 | 122.1381 | 122.0726 | 0.23843 | 0.17753 | 0.034501 | 0.073579 | -0.010593 | 0.024297 | 0.29581 | 0.17465 | 0.15738 | 0.16726 | 0.1736 | 0.25039 | 0.1616 | 122.1793 | 122.1138 | 0.27963 | 0.21873 | 0.0757 | 0.11478 | 0.030606 | 0.065496 | 122.1036 | 122.1487 | 0.20393 | 0.24902
4710.25 | 122.287 | -0.13275 | 122.1497 | 0.18137 | 0.069371 | 0.052101 | 0.052818 | 0.063733 | 0.13137 | 0.047159 | 122.1426 | 122.0818 | 0.24759 | 0.18669 | 0.029923 | 0.069001 | -0.010593 | 0.024297 | 0.31412 | 0.20212 | 0.18485 | 0.18557 | 0.19648 | 0.26412 | 0.17991 | 122.1838 | 122.123 | 0.28879 | 0.22789 | 0.071122 | 0.1102 | 0.030606 | 0.065496 | 122.1127 | 122.1532 | 0.21766 | 0.25818
4712.0312 | 122.3694 | -0.086975 | 122.1176 | 0.18137 | 0.060213 | 0.047522 | 0.057396 | 0.059155 | 0.13137 | 0.038003 | 122.1426 | 122.0726 | 0.23385 | 0.17753 | 0.029923 | 0.073579 | -0.006014 | 0.028875 | 0.26835 | 0.14719 | 0.1345 | 0.14437 | 0.14613 | 0.21834 | 0.12498 | 122.1838 | 122.1138 | 0.27505 | 0.21873 | 0.071122 | 0.11478 | 0.035185 | 0.070074 | 122.1127 | 122.1487 | 0.20393 | 0.23986
4713.7812 | 122.3785 | -0.11444 | 122.1039 | 0.18137 | 0.060213 | 0.052101 | 0.048239 | 0.059155 | 0.14052 | 0.038003 | 122.1426 | 122.0726 | 0.23843 | 0.18669 | 0.039079 | 0.078157 | -0.006014 | 0.024297 | 0.29581 | 0.17465 | 0.16654 | 0.16268 | 0.1736 | 0.25496 | 0.15244 | 122.1838 | 122.1138 | 0.27963 | 0.22789 | 0.080278 | 0.11936 | 0.035185 | 0.065496 | 122.1036 | 122.1487 | 0.19935 | 0.24444
4715.5469 | 122.2549 | -0.13275 | 122.1359 | 0.18595 | 0.060213 | 0.052101 | 0.052818 | 0.06831 | 0.14052 | 0.051737 | 122.1381 | 122.0818 | 0.24301 | 0.17753 | 0.025345 | 0.064423 | -0.006014 | 0.028875 | 0.3187 | 0.19296 | 0.18485 | 0.18557 | 0.20106 | 0.27328 | 0.18449 | 122.1793 | 122.123 | 0.28421 | 0.21873 | 0.066544 | 0.10562 | 0.035185 | 0.070074 | 122.1127 | 122.1441 | 0.21766 | 0.24902
4717.3438 | 122.3328 | -0.1236 | 122.1176 | 0.18137 | 0.060213 | 0.047522 | 0.057396 | 0.054577 | 0.13137 | 0.051737 | 122.1426 | 122.0681 | 0.23385 | 0.17753 | 0.034501 | 0.069001 | -0.015171 | 0.024297 | 0.30497 | 0.18381 | 0.17112 | 0.18099 | 0.17817 | 0.25496 | 0.17533 | 122.1838 | 122.1093 | 0.27505 | 0.21873 | 0.0757 | 0.1102 | 0.026028 | 0.065496 | 122.1081 | 122.1578 | 0.19935 | 0.24902
4719.1094 | 122.2961 | -0.12817 | 122.113 | 0.19053 | 0.060213 | 0.047522 | 0.057396 | 0.072888 | 0.14052 | 0.047159 | 122.1426 | 122.0681 | 0.23385 | 0.18211 | 0.029923 | 0.069001 | -0.015171 | 0.024297 | 0.3187 | 0.18839 | 0.1757 | 0.18557 | 0.20106 | 0.2687 | 0.17533 | 122.1838 | 122.1093 | 0.27505 | 0.22331 | 0.071122 | 0.1102 | 0.026028 | 0.065496 | 122.1127 | 122.1578 | 0.20393 | 0.24902
4720.8125 | 122.2366 | -0.14648 | 122.1451 | 0.18595 | 0.064792 | 0.052101 | 0.061975 | 0.063733 | 0.1451 | 0.051737 | 122.1335 | 122.0726 | 0.23385 | 0.17296 | 0.029923 | 0.069001 | -0.006014 | 0.019719 | 0.33243 | 0.21128 | 0.19859 | 0.20846 | 0.21022 | 0.29159 | 0.19822 | 122.1747 | 122.1138 | 0.27505 | 0.21415 | 0.071122 | 0.1102 | 0.035185 | 0.060918 | 122.1036 | 122.1395 | 0.20393 | 0.23986
4722.6094 | 122.3648 | -0.10529 | 122.1176 | 0.18137 | 0.060213 | 0.052101 | 0.057396 | 0.072888 | 0.14052 | 0.051737 | 122.1335 | 122.0681 | 0.22927 | 0.17753 | 0.043657 | 0.073579 | -0.001436 | 0.033454 | 0.28666 | 0.1655 | 0.15739 | 0.16268 | 0.17817 | 0.24581 | 0.15702 | 122.1747 | 122.1093 | 0.27047 | 0.21873 | 0.084856 | 0.11478 | 0.039763 | 0.074653 | 122.0898 | 122.1349 | 0.18562 | 0.23071
4724.3125 | 122.3785 | -0.10071 | 122.0901 | 0.18595 | 0.064792 | 0.061258 | 0.061975 | 0.063733 | 0.14052 | 0.051737 | 122.1289 | 122.0681 | 0.22927 | 0.17753 | 0.034501 | 0.073579 | -0.010593 | 0.024297 | 0.28666 | 0.1655 | 0.16197 | 0.16268 | 0.16444 | 0.24123 | 0.15244 | 122.1701 | 122.1093 | 0.27047 | 0.21873 | 0.0757 | 0.11478 | 0.030606 | 0.065496 | 122.0944 | 122.1395 | 0.19477 | 0.23987
4726.0781 | 122.2916 | -0.12817 | 122.113 | 0.18137 | 0.060213 | 0.052101 | 0.057396 | 0.059155 | 0.1451 | 0.047159 | 122.1243 | 122.0589 | 0.23385 | 0.17753 | 0.039079 | 0.078157 | -0.010593 | 0.024297 | 0.30954 | 0.18839 | 0.18028 | 0.18557 | 0.18733 | 0.27328 | 0.17533 | 122.1655 | 122.1001 | 0.27505 | 0.21873 | 0.080278 | 0.11936 | 0.030606 | 0.065496 | 122.0852 | 122.1349 | 0.19477 | 0.24444
4727.8594 | 122.2412 | -0.15106 | 122.1542 | 0.19053 | 0.055634 | 0.056679 | 0.057396 | 0.06831 | 0.14052 | 0.051737 | 122.1197 | 122.0589 | 0.22927 | 0.17753 | 0.029923 | 0.073579 | -0.001436 | 0.028875 | 0.34159 | 0.2067 | 0.20774 | 0.20846 | 0.21937 | 0.29159 | 0.2028 | 122.1609 | 122.1001 | 0.27047 | 0.21873 | 0.071122 | 0.11478 | 0.039763 | 0.070074 | 122.0898 | 122.1212 | 0.19935 | 0.23071
4729.6406 | 122.3236 | -0.10071 | 122.049 | 0.19053 | 0.055634 | 0.061258 | 0.057396 | 0.06831 | 0.14052 | 0.038003 | 122.1243 | 122.0589 | 0.22927 | 0.17753 | 0.039079 | 0.073579 | -0.006014 | 0.024297 | 0.29124 | 0.15634 | 0.16197 | 0.1581 | 0.16902 | 0.24123 | 0.13871 | 122.1655 | 122.1001 | 0.27047 | 0.21873 | 0.080278 | 0.11478 | 0.035185 | 0.065496 | 122.0852 | 122.1303 | 0.19019 | 0.23529
4731.4062 | 122.3053 | -0.1236 | 122.0856 | 0.18595 | 0.069371 | 0.052101 | 0.057396 | 0.072888 | 0.1451 | 0.051737 | 122.1289 | 122.0498 | 0.2247 | 0.16838 | 0.039079 | 0.069001 | -0.006014 | 0.024297 | 0.30954 | 0.19297 | 0.1757 | 0.18099 | 0.19648 | 0.2687 | 0.17533 | 122.1701 | 122.0909 | 0.26589 | 0.20958 | 0.080278 | 0.1102 | 0.035185 | 0.065496 | 122.0898 | 122.1349 | 0.18562 | 0.23071
4733.1094 | 122.3099 | -0.10071 | 122.113 | 0.19053 | 0.064792 | 0.052101 | 0.052818 | 0.06831 | 0.1451 | 0.047159 | 122.1152 | 122.0498 | 0.2247 | 0.17753 | 0.039079 | 0.082735 | -0.010593 | 0.033454 | 0.29124 | 0.1655 | 0.15281 | 0.15353 | 0.16902 | 0.24581 | 0.14787 | 122.1564 | 122.0909 | 0.26589 | 0.21873 | 0.080278 | 0.12393 | 0.030606 | 0.074653 | 122.0761 | 122.1258 | 0.18562 | 0.23529
4734.8125 | 122.3007 | -0.11444 | 122.0764 | 0.17679 | 0.069371 | 0.052101 | 0.057396 | 0.063733 | 0.13595 | 0.042581 | 122.1106 | 122.0543 | 0.22927 | 0.17296 | 0.043657 | 0.069001 | -0.006014 | 0.033454 | 0.29123 | 0.18381 | 0.16654 | 0.17184 | 0.17817 | 0.25039 | 0.15702 | 122.1518 | 122.0955 | 0.27047 | 0.21415 | 0.084856 | 0.1102 | 0.035185 | 0.074653 | 122.0669 | 122.1166 | 0.18562 | 0.23529
4736.5625 | 122.2824 | -0.1236 | 122.113 | 0.17679 | 0.055634 | 0.052101 | 0.057396 | 0.06831 | 0.14052 | 0.042581 | 122.1197 | 122.0452 | 0.2247 | 0.17296 | 0.034501 | 0.078157 | -0.001436 | 0.024297 | 0.30039 | 0.17923 | 0.1757 | 0.18099 | 0.19191 | 0.26412 | 0.16618 | 122.1609 | 122.0864 | 0.26589 | 0.21415 | 0.0757 | 0.11936 | 0.039763 | 0.065496 | 122.0852 | 122.1212 | 0.19019 | 0.22613
4738.3281 | 122.3648 | -0.09613 | 122.0673 | 0.18595 | 0.060213 | 0.047522 | 0.057396 | 0.06831 | 0.14968 | 0.042581 | 122.1106 | 122.0498 | 0.2247 | 0.17296 | 0.043657 | 0.073579 | -0.006014 | 0.024297 | 0.28208 | 0.15634 | 0.14365 | 0.15353 | 0.16444 | 0.24581 | 0.13871 | 122.1518 | 122.0909 | 0.26589 | 0.21415 | 0.084856 | 0.11478 | 0.035185 | 0.065496 | 122.0669 | 122.1166 | 0.18104 | 0.23071
4740.0312 | 122.3648 | -0.10986 | 122.0856 | 0.18137 | 0.064792 | 0.052101 | 0.057396 | 0.063733 | 0.13595 | 0.047159 | 122.1152 | 122.0452 | 0.22927 | 0.17296 | 0.039079 | 0.078157 | -0.001436 | 0.028875 | 0.29123 | 0.17466 | 0.16196 | 0.16726 | 0.1736 | 0.24581 | 0.15702 | 122.1564 | 122.0864 | 0.27047 | 0.21415 | 0.080278 | 0.11936 | 0.039763 | 0.070074 | 122.0761 | 122.1166 | 0.19019 | 0.23071
4741.7812 | 122.2641 | -0.14191 | 122.113 | 0.18137 | 0.060213 | 0.047522 | 0.052818 | 0.072888 | 0.14052 | 0.047159 | 122.1106 | 122.0452 | 0.22927 | 0.17753 | 0.048236 | 0.073579 | -0.006014 | 0.028875 | 0.32328 | 0.20212 | 0.18943 | 0.19473 | 0.2148 | 0.28243 | 0.18907 | 122.1518 | 122.0864 | 0.27047 | 0.21873 | 0.089435 | 0.11478 | 0.035185 | 0.070074 | 122.0624 | 122.1166 | 0.18104 | 0.23529
4743.4844 | 122.2549 | -0.13275 | 122.1313 | 0.17221 | 0.069371 | 0.056679 | 0.057396 | 0.059155 | 0.14968 | 0.051737 | 122.106 | 122.0406 | 0.22927 | 0.1638 | 0.043657 | 0.078157 | -0.006014 | 0.024297 | 0.30496 | 0.20212 | 0.18943 | 0.19015 | 0.19191 | 0.28243 | 0.18449 | 122.1472 | 122.0818 | 0.27047 | 0.205 | 0.084856 | 0.11936 | 0.035185 | 0.065496 | 122.0624 | 122.112 | 0.18562 | 0.23529
4745.25 | 122.2229 | -0.15106 | 122.081 | 0.18137 | 0.064792 | 0.056679 | 0.061975 | 0.063733 | 0.14052 | 0.042581 | 122.1014 | 122.036 | 0.23385 | 0.17753 | 0.039079 | 0.073579 | -0.001436 | 0.033454 | 0.33243 | 0.21585 | 0.20774 | 0.21304 | 0.2148 | 0.29159 | 0.19364 | 122.1426 | 122.0772 | 0.27505 | 0.21873 | 0.080278 | 0.11478 | 0.039763 | 0.074653 | 122.0624 | 122.1029 | 0.19477 | 0.23529
4747.0156 | 122.319 | -0.09613 | 122.0535 | 0.18137 | 0.069371 | 0.052101 | 0.052818 | 0.06831 | 0.14968 | 0.038003 | 122.106 | 122.0314 | 0.2247 | 0.17296 | 0.039079 | 0.087313 | -0.006014 | 0.033454 | 0.2775 | 0.1655 | 0.14823 | 0.14895 | 0.16444 | 0.24581 | 0.13413 | 122.1472 | 122.0726 | 0.26589 | 0.21415 | 0.080278 | 0.12851 | 0.035185 | 0.074653 | 122.0669 | 122.112 | 0.18562 | 0.23071
4748.7969 | 122.2595 | -0.14191 | 122.0993 | 0.18595 | 0.060213 | 0.047522 | 0.057396 | 0.06831 | 0.14052 | 0.047159 | 122.0969 | 122.0406 | 0.22927 | 0.18211 | 0.039079 | 0.082735 | -0.001436 | 0.028875 | 0.32786 | 0.20212 | 0.18943 | 0.1993 | 0.21022 | 0.28243 | 0.18907 | 122.1381 | 122.0818 | 0.27047 | 0.22331 | 0.080278 | 0.12393 | 0.039763 | 0.070074 | 122.0578 | 122.0983 | 0.19019 | 0.23071
4750.5 | 122.2275 | -0.15564 | 122.1359 | 0.18137 | 0.055634 | 0.047522 | 0.061975 | 0.059155 | 0.13595 | 0.047159 | 122.0969 | 122.0314 | 0.23385 | 0.17296 | 0.043657 | 0.082735 | -0.006014 | 0.028875 | 0.33701 | 0.21127 | 0.20316 | 0.21762 | 0.2148 | 0.29158 | 0.2028 | 122.1381 | 122.0726 | 0.27505 | 0.21415 | 0.084856 | 0.12393 | 0.035185 | 0.070074 | 122.0532 | 122.1029 | 0.19019 | 0.23986
4752.2656 | 122.2961 | -0.1236 | 122.0856 | 0.18595 | 0.060213 | 0.042944 | 0.052818 | 0.059155 | 0.13595 | 0.047159 | 122.0923 | 122.0314 | 0.23385 | 0.16838 | 0.048236 | 0.082735 | -0.006014 | 0.024297 | 0.30954 | 0.18381 | 0.16654 | 0.17641 | 0.18275 | 0.25954 | 0.17075 | 122.1335 | 122.0726 | 0.27505 | 0.20958 | 0.089435 | 0.12393 | 0.035185 | 0.065496 | 122.044 | 122.0983 | 0.18562 | 0.23986
4754.0312 | 122.2961 | -0.11902 | 122.0947 | 0.18137 | 0.064792 | 0.056679 | 0.057396 | 0.063733 | 0.14052 | 0.042581 | 122.0923 | 122.036 | 0.24301 | 0.18211 | 0.034501 | 0.082735 | -0.001436 | 0.024297 | 0.30039 | 0.18381 | 0.1757 | 0.17641 | 0.18275 | 0.25954 | 0.1616 | 122.1335 | 122.0772 | 0.28421 | 0.22331 | 0.0757 | 0.12393 | 0.039763 | 0.065496 | 122.0578 | 122.0937 | 0.20851 | 0.24444
4755.7344 | 122.2916 | -0.10986 | 122.0535 | 0.18137 | 0.060213 | 0.047522 | 0.052818 | 0.063733 | 0.13595 | 0.042581 | 122.0923 | 122.0269 | 0.23843 | 0.18211 | 0.043657 | 0.078157 | -0.006014 | 0.024297 | 0.29123 | 0.17008 | 0.15738 | 0.16268 | 0.1736 | 0.24581 | 0.15244 | 122.1335 | 122.0681 | 0.27963 | 0.22331 | 0.084856 | 0.11936 | 0.035185 | 0.065496 | 122.0486 | 122.0983 | 0.19477 | 0.24444
4757.5 | 122.2137 | -0.14191 | 122.0856 | 0.18595 | 0.064792 | 0.047522 | 0.052818 | 0.063733 | 0.1451 | 0.047159 | 122.0877 | 122.0223 | 0.23843 | 0.17296 | 0.034501 | 0.082735 | -0.001436 | 0.033454 | 0.32786 | 0.2067 | 0.18943 | 0.19473 | 0.20564 | 0.28701 | 0.18907 | 122.1289 | 122.0635 | 0.27963 | 0.21415 | 0.0757 | 0.12393 | 0.039763 | 0.074653 | 122.0532 | 122.0891 | 0.20393 | 0.23987
4759.25 | 122.2229 | -0.14648 | 122.0764 | 0.18137 | 0.064792 | 0.052101 | 0.057396 | 0.06831 | 0.14052 | 0.047159 | 122.074 | 122.0131 | 0.22927 | 0.17753 | 0.039079 | 0.078157 | -0.010593 | 0.028875 | 0.32785 | 0.21128 | 0.19859 | 0.20388 | 0.21479 | 0.28701 | 0.19364 | 122.1152 | 122.0543 | 0.27047 | 0.21873 | 0.080278 | 0.11936 | 0.030606 | 0.070074 | 122.0349 | 122.0846 | 0.19019 | 0.23987
4761.0156 | 122.3099 | -0.13275 | 122.0306 | 0.17221 | 0.064792 | 0.052101 | 0.048239 | 0.063733 | 0.13595 | 0.042581 | 122.074 | 122.004 | 0.2247 | 0.18669 | 0.039079 | 0.082735 | -0.010593 | 0.024297 | 0.30496 | 0.19754 | 0.18485 | 0.18099 | 0.19648 | 0.2687 | 0.17533 | 122.1152 | 122.0452 | 0.26589 | 0.22789 | 0.080278 | 0.12393 | 0.030606 | 0.065496 | 122.0349 | 122.0846 | 0.18562 | 0.23529
4762.7969 | 122.1909 | -0.15106 | 122.0581 | 0.18595 | 0.055634 | 0.052101 | 0.057396 | 0.06831 | 0.13137 | 0.047159 | 122.0602 | 121.9994 | 0.23385 | 0.18211 | 0.043657 | 0.078157 | -0.006014 | 0.033454 | 0.33701 | 0.2067 | 0.20316 | 0.20846 | 0.21937 | 0.28243 | 0.19822 | 122.1014 | 122.0406 | 0.27505 | 0.22331 | 0.084856 | 0.11936 | 0.035185 | 0.074653 | 122.0166 | 122.0662 | 0.19019 | 0.23986
4764.5625 | 122.2916 | -0.1236 | 122.0352 | 0.18137 | 0.060213 | 0.052101 | 0.052818 | 0.06831 | 0.13595 | 0.047159 | 122.0648 | 121.9948 | 0.23843 | 0.16838 | 0.043657 | 0.087313 | -0.001436 | 0.033454 | 0.30497 | 0.18381 | 0.1757 | 0.17641 | 0.19191 | 0.25954 | 0.17075 | 122.106 | 122.036 | 0.27963 | 0.20958 | 0.084856 | 0.12851 | 0.039763 | 0.074653 | 122.0211 | 122.0662 | 0.19477 | 0.23987
4766.2656 | 117.9977 | -0.10986 | 117.8375 | 0.18137 | 0.064792 | 0.052101 | 0.052818 | 0.063733 | 0.13595 | 0.047159 | 122.019 | 121.949 | 0.23843 | 0.17296 | 0.052814 | 0.082735 | -0.006014 | 0.019719 | 0.29123 | 0.17466 | 0.16196 | 0.16268 | 0.1736 | 0.24581 | 0.15702 | 122.0602 | 121.9902 | 0.27963 | 0.21415 | 0.094013 | 0.12393 | 0.035185 | 0.060918 | 121.9662 | 122.025 | 0.18562 | 0.24444
4768.0312 | 122.1313 | -0.15564 | 122.049 | 0.18595 | 0.060213 | 0.052101 | 0.057396 | 0.063733 | 0.14052 | 0.047159 | 122.0419 | 121.9719 | 0.2247 | 0.17753 | 0.039079 | 0.078157 | -0.015171 | 0.024297 | 0.34159 | 0.21585 | 0.20774 | 0.21304 | 0.21937 | 0.29616 | 0.2028 | 122.0831 | 122.0131 | 0.26589 | 0.21873 | 0.080278 | 0.11936 | 0.026028 | 0.065496 | 122.0028 | 122.0571 | 0.18562 | 0.23987
4769.8125 | 122.1725 | -0.16022 | 122.0673 | 0.17679 | 0.051056 | 0.052101 | 0.057396 | 0.06831 | 0.1451 | 0.047159 | 122.0465 | 121.9673 | 0.23843 | 0.18669 | 0.043657 | 0.078157 | -0.001436 | 0.028875 | 0.33701 | 0.21127 | 0.21232 | 0.21761 | 0.22853 | 0.30532 | 0.20738 | 122.0877 | 122.0085 | 0.27963 | 0.22789 | 0.084856 | 0.11936 | 0.039763 | 0.070074 | 122.0028 | 122.0479 | 0.19477 | 0.23987
4771.5156 | 122.2137 | -0.13275 | 122.0718 | 0.18137 | 0.055634 | 0.052101 | 0.061975 | 0.072888 | 0.1451 | 0.047159 | 122.0419 | 121.9765 | 0.24301 | 0.17753 | 0.043657 | 0.087313 | -0.001436 | 0.033454 | 0.31412 | 0.18839 | 0.18485 | 0.19473 | 0.20564 | 0.27785 | 0.17991 | 122.0831 | 122.0177 | 0.28421 | 0.21873 | 0.084856 | 0.12851 | 0.039763 | 0.074653 | 121.9983 | 122.0434 | 0.19935 | 0.24444
4773.2812 | 122.2504 | -0.11902 | 122.0306 | 0.18137 | 0.055634 | 0.047522 | 0.052818 | 0.059155 | 0.14052 | 0.042581 | 122.0328 | 121.9719 | 0.23843 | 0.17296 | 0.039079 | 0.087313 | -0.006014 | 0.028875 | 0.30039 | 0.17465 | 0.16654 | 0.17184 | 0.17817 | 0.25954 | 0.1616 | 122.074 | 122.0131 | 0.27963 | 0.21415 | 0.080278 | 0.12851 | 0.035185 | 0.070074 | 121.9937 | 122.0388 | 0.19935 | 0.24444
4775.0625 | 122.1405 | -0.14191 | 122.0306 | 0.18137 | 0.060213 | 0.047522 | 0.057396 | 0.06831 | 0.14968 | 0.051737 | 122.0144 | 121.949 | 0.23843 | 0.18211 | 0.048236 | 0.082735 | -0.010593 | 0.019719 | 0.32328 | 0.20212 | 0.18943 | 0.1993 | 0.21022 | 0.29159 | 0.19364 | 122.0556 | 121.9902 | 0.27963 | 0.22331 | 0.089435 | 0.12393 | 0.030606 | 0.060918 | 121.9662 | 122.025 | 0.19019 | 0.24902
4776.7656 | 122.1634 | -0.13733 | 122.0261 | 0.18137 | 0.060213 | 0.047522 | 0.048239 | 0.06831 | 0.13595 | 0.038003 | 121.9687 | 121.9078 | 0.24301 | 0.18211 | 0.048236 | 0.091891 | -0.024328 | 0.005985 | 0.3187 | 0.19754 | 0.18485 | 0.18557 | 0.20564 | 0.27327 | 0.17533 | 122.0099 | 121.949 | 0.28421 | 0.22331 | 0.089435 | 0.13309 | 0.016871 | 0.047184 | 121.9204 | 121.993 | 0.19477 | 0.26734
4778.5312 | 122.1771 | -0.1236 | 121.9345 | 0.18137 | 0.060213 | 0.047522 | 0.052818 | 0.063733 | 0.14052 | 0.042581 | 121.845 | 121.7796 | 0.22927 | 0.17296 | 0.052814 | 0.082735 | -0.051798 | -0.021484 | 0.30497 | 0.18381 | 0.17112 | 0.17641 | 0.18733 | 0.26412 | 0.16618 | 121.8862 | 121.8208 | 0.27047 | 0.21415 | 0.094013 | 0.12393 | -0.010599 | 0.019715 | 121.7922 | 121.8968 | 0.17646 | 0.28107
4780.2344 | 122.2458 | -0.10986 | 121.9528 | 0.17221 | 0.060213 | 0.042944 | 0.048239 | 0.054577 | 0.13137 | 0.038003 | 121.9824 | 121.9215 | 0.2247 | 0.1638 | 0.039079 | 0.091891 | -0.006014 | 0.028875 | 0.28208 | 0.17008 | 0.15281 | 0.1581 | 0.16444 | 0.24123 | 0.14787 | 122.0236 | 121.9627 | 0.26589 | 0.205 | 0.080278 | 0.13309 | 0.035185 | 0.070074 | 121.9433 | 121.9884 | 0.18562 | 0.23071
4782 | 122.1222 | -0.15564 | 121.994 | 0.17679 | 0.064792 | 0.047522 | 0.052818 | 0.054577 | 0.14052 | 0.047159 | 121.9595 | 121.8895 | 0.23385 | 0.17296 | 0.048236 | 0.087313 | -0.015171 | 0.010563 | 0.33243 | 0.22043 | 0.20316 | 0.20846 | 0.21022 | 0.29616 | 0.2028 | 122.0007 | 121.9307 | 0.27505 | 0.21415 | 0.089435 | 0.12851 | 0.026028 | 0.051762 | 121.9113 | 121.9747 | 0.18562 | 0.24902
4783.7656 | 122.113 | -0.14191 | 121.9391 | 0.18137 | 0.064792 | 0.042944 | 0.048239 | 0.06831 | 0.14052 | 0.047159 | 121.8725 | 121.7933 | 0.23385 | 0.18211 | 0.048236 | 0.082735 | -0.042641 | -0.016906 | 0.32328 | 0.2067 | 0.18485 | 0.19015 | 0.21022 | 0.28243 | 0.18907 | 121.9137 | 121.8345 | 0.27505 | 0.22331 | 0.089435 | 0.12393 | -0.001442 | 0.024293 | 121.8243 | 121.9151 | 0.18562 | 0.27649
4785.4531 | 122.1222 | -0.11444 | 121.8704 | 0.17679 | 0.051056 | 0.052101 | 0.057396 | 0.054577 | 0.14052 | 0.047159 | 121.8176 | 121.7521 | 0.22927 | 0.17296 | 0.048236 | 0.091891 | -0.060955 | -0.026063 | 0.29123 | 0.1655 | 0.16654 | 0.17184 | 0.16902 | 0.25496 | 0.1616 | 121.8588 | 121.7933 | 0.27047 | 0.21415 | 0.089435 | 0.13309 | -0.019756 | 0.015136 | 121.7693 | 121.8785 | 0.18104 | 0.29023
4787.2188 | 121.9391 | -0.1236 | 121.788 | 0.17221 | 0.055634 | 0.047522 | 0.048239 | 0.063733 | 0.1451 | 0.042581 | 121.6344 | 121.569 | 0.23385 | 0.18211 | 0.043657 | 0.082735 | -0.097582 | -0.071844 | 0.29581 | 0.17923 | 0.17112 | 0.17183 | 0.18733 | 0.2687 | 0.16618 | 121.6756 | 121.6102 | 0.27505 | 0.22331 | 0.084856 | 0.12393 | -0.056383 | -0.030645 | 121.5908 | 121.732 | 0.19019 | 0.33143
4788.9219 | 121.9254 | -0.086975 | 121.7377 | 0.17679 | 0.064792 | 0.038365 | 0.052818 | 0.063733 | 0.13137 | 0.047159 | 121.5978 | 121.5323 | 0.22927 | 0.17296 | 0.052814 | 0.096469 | -0.093004 | -0.071844 | 0.26377 | 0.15177 | 0.12534 | 0.13979 | 0.15071 | 0.21834 | 0.13413 | 121.639 | 121.5735 | 0.27047 | 0.21415 | 0.094013 | 0.13767 | -0.051805 | -0.030645 | 121.545 | 121.6908 | 0.17646 | 0.32228
4790.6875 | 121.8384 | -0.091553 | 121.55 | 0.17679 | 0.060213 | 0.052101 | 0.048239 | 0.059155 | 0.13595 | 0.042581 | 121.2498 | 121.1706 | 0.22012 | 0.16838 | 0.048236 | 0.082735 | -0.19373 | -0.19088 | 0.26835 | 0.15177 | 0.14365 | 0.13979 | 0.15071 | 0.2275 | 0.13413 | 121.291 | 121.2118 | 0.26132 | 0.20958 | 0.089435 | 0.12393 | -0.15253 | -0.14968 | 121.2016 | 121.4436 | 0.17188 | 0.41384
4792.4062 | 121.7102 | -0.13733 | 121.4676 | 0.17679 | 0.060213 | 0.042944 | 0.052818 | 0.072888 | 0.13595 | 0.038003 | 121.1628 | 121.1019 | 0.2247 | 0.1638 | 0.034501 | 0.078157 | -0.29445 | -0.28244 | 0.31412 | 0.19754 | 0.18027 | 0.19015 | 0.21022 | 0.27327 | 0.17533 | 121.204 | 121.1431 | 0.26589 | 0.205 | 0.0757 | 0.11936 | -0.25325 | -0.24124 | 121.1283 | 121.4573 | 0.19019 | 0.51915
4794.1719 | 121.8613 | -0.14648 | 121.6736 | 0.18137 | 0.060213 | 0.042944 | 0.057396 | 0.063733 | 0.14052 | 0.042581 | 121.5429 | 121.4774 | 0.22927 | 0.17296 | 0.039079 | 0.087313 | -0.070112 | -0.048953 | 0.32785 | 0.2067 | 0.18943 | 0.20388 | 0.21022 | 0.28701 | 0.18907 | 121.5841 | 121.5186 | 0.27047 | 0.21415 | 0.080278 | 0.12851 | -0.028913 | -0.007754 | 121.5038 | 121.613 | 0.19019 | 0.29939
4795.9375 | 121.9162 | -0.082397 | 121.7102 | 0.098959 | -0.017627 | -0.039471 | -0.029595 | -0.009515 | 0.048956 | -0.03067 | 0.24936 | 0.31732 | 0.059877 | -0.023943 | 0.025345 | 0.059844 | -0.019749 | 0.04261 | 0.18136 | 0.06477 | 0.042926 | 0.052802 | 0.072882 | 0.13135 | 0.051727 | 0.29056 | 0.35851 | 0.10108 | 0.017256 | 0.066544 | 0.10104 | 0.02145 | 0.083809 | 0.22402 | 0.26911 | 0.034532 | 0.079626
4797.6406 | 121.962 | -0.11902 | 121.8109 | 0.098959 | -0.022205 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.021514 | 0.20816 | 0.27611 | 0.069033 | -0.014785 | 0.020767 | 0.059844 | -0.019749 | 0.038032 | 0.21798 | 0.096814 | 0.088705 | 0.098581 | 0.10035 | 0.17713 | 0.097505 | 0.24936 | 0.31731 | 0.11023 | 0.026414 | 0.061966 | 0.10104 | 0.02145 | 0.079231 | 0.18739 | 0.22791 | 0.048266 | 0.088782
4799.4219 | 122.081 | -0.073242 | 121.8246 | 0.10354 | -0.013048 | -0.034893 | -0.025017 | -0.009515 | 0.062691 | -0.03067 | 0.20358 | 0.27153 | 0.059877 | -0.019364 | 0.020767 | 0.059844 | -0.015171 | 0.04261 | 0.17678 | 0.060194 | 0.038349 | 0.048225 | 0.063727 | 0.13593 | 0.042572 | 0.24478 | 0.31273 | 0.10108 | 0.021835 | 0.061966 | 0.10104 | 0.026028 | 0.083809 | 0.18281 | 0.21875 | 0.03911 | 0.075048
4801.1719 | 122.0581 | -0.07782 | 121.8338 | 0.098959 | -0.017627 | -0.039471 | -0.034174 | -0.018671 | 0.053534 | -0.03067 | 0.19442 | 0.26695 | 0.059877 | -0.028522 | 0.01161 | 0.059844 | -0.019749 | 0.047188 | 0.17678 | 0.060193 | 0.038349 | 0.043646 | 0.059149 | 0.13135 | 0.04715 | 0.23562 | 0.30815 | 0.10108 | 0.012677 | 0.052809 | 0.10104 | 0.02145 | 0.088387 | 0.18281 | 0.21417 | 0.048267 | 0.079626
4802.9375 | 122.113 | -0.082397 | 121.8704 | 0.10354 | -0.008469 | -0.034893 | -0.020438 | -0.018671 | 0.062691 | -0.03067 | 0.18984 | 0.26237 | 0.059877 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.051766 | 0.18593 | 0.073928 | 0.047504 | 0.061959 | 0.063726 | 0.14509 | 0.051727 | 0.23104 | 0.30357 | 0.10108 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.092965 | 0.17823 | 0.20501 | 0.048267 | 0.075048
4804.7031 | 122.1176 | -0.07782 | 121.8933 | 0.098959 | -0.017627 | -0.025735 | -0.029595 | -0.014093 | 0.058113 | -0.026092 | 0.17611 | 0.26237 | 0.069033 | -0.019364 | 0.020767 | 0.055266 | -0.019749 | 0.047188 | 0.17678 | 0.060193 | 0.052085 | 0.048225 | 0.063727 | 0.13593 | 0.051728 | 0.21731 | 0.30357 | 0.11023 | 0.021835 | 0.061966 | 0.096465 | 0.02145 | 0.088387 | 0.15534 | 0.19586 | 0.048266 | 0.088782
4806.4062 | 122.0261 | -0.10071 | 121.9208 | 0.089802 | -0.013048 | -0.030314 | -0.01586 | -0.018671 | 0.058113 | -0.03067 | 0.18069 | 0.25779 | 0.064455 | -0.028522 | 0.016188 | 0.055266 | -0.010593 | 0.056344 | 0.19051 | 0.08766 | 0.070394 | 0.084848 | 0.082037 | 0.15882 | 0.070038 | 0.22188 | 0.29899 | 0.10565 | 0.012677 | 0.057387 | 0.096465 | 0.030606 | 0.097543 | 0.1645 | 0.19128 | 0.048267 | 0.075048
4808.1875 | 122.0123 | -0.1236 | 121.9391 | 0.098959 | -0.013048 | -0.030314 | -0.025017 | -0.009515 | 0.062691 | -0.03067 | 0.18069 | 0.24405 | 0.059877 | -0.019364 | 0.007032 | 0.04611 | -0.024328 | 0.04261 | 0.22256 | 0.11055 | 0.093282 | 0.098579 | 0.11408 | 0.18629 | 0.092926 | 0.22188 | 0.28525 | 0.10108 | 0.021835 | 0.048231 | 0.087309 | 0.016871 | 0.083809 | 0.17365 | 0.20501 | 0.052845 | 0.084205
4809.9062 | 122.0764 | -0.10071 | 121.9299 | 0.094381 | -0.017627 | -0.034893 | -0.020438 | -0.014093 | 0.067269 | -0.03067 | 0.17611 | 0.25321 | 0.059877 | -0.019364 | 0.016188 | 0.055266 | -0.019749 | 0.047188 | 0.19509 | 0.083081 | 0.065815 | 0.08027 | 0.086615 | 0.16798 | 0.070038 | 0.21731 | 0.29441 | 0.10108 | 0.021835 | 0.057387 | 0.096465 | 0.02145 | 0.088387 | 0.15992 | 0.19586 | 0.043689 | 0.079626
4811.6719 | 122.1222 | -0.082397 | 121.9299 | 0.098959 | -0.017627 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.03067 | 0.17153 | 0.24863 | 0.064455 | -0.028522 | 0.016188 | 0.059844 | -0.015171 | 0.04261 | 0.18136 | 0.06477 | 0.052083 | 0.061959 | 0.063726 | 0.14051 | 0.051727 | 0.21273 | 0.28983 | 0.10565 | 0.012677 | 0.057387 | 0.10104 | 0.026028 | 0.083809 | 0.15534 | 0.1867 | 0.048267 | 0.079626
4813.375 | 122.0535 | -0.1236 | 121.9666 | 0.094381 | -0.017627 | -0.030314 | -0.029595 | -0.018671 | 0.058113 | -0.026092 | 0.17153 | 0.24863 | 0.059877 | -0.023943 | 0.016188 | 0.055266 | -0.010593 | 0.038032 | 0.21798 | 0.10597 | 0.093282 | 0.094001 | 0.10492 | 0.18171 | 0.097504 | 0.21273 | 0.28983 | 0.10108 | 0.017256 | 0.057387 | 0.096465 | 0.030606 | 0.079231 | 0.15534 | 0.18212 | 0.043689 | 0.07047
4815.1406 | 122.2 | -0.082397 | 121.9208 | 0.094381 | -0.022205 | -0.034893 | -0.029595 | -0.009515 | 0.067269 | -0.026092 | 0.17153 | 0.24863 | 0.069033 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.051766 | 0.17678 | 0.060192 | 0.047504 | 0.052802 | 0.072882 | 0.14967 | 0.056305 | 0.21273 | 0.28983 | 0.11023 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.092965 | 0.15534 | 0.19128 | 0.052845 | 0.088782
4816.9062 | 122.081 | -0.10986 | 122.0032 | 0.094381 | -0.013048 | -0.030314 | -0.025017 | -0.014093 | 0.062691 | -0.03067 | 0.17611 | 0.24863 | 0.064455 | -0.014785 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.20424 | 0.096815 | 0.079549 | 0.084846 | 0.09577 | 0.17255 | 0.079193 | 0.21731 | 0.28983 | 0.10565 | 0.026414 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.15992 | 0.19586 | 0.048267 | 0.084204
4818.6875 | 122.0856 | -0.10986 | 121.9849 | 0.098959 | -0.017627 | -0.030314 | -0.01586 | -0.014093 | 0.062691 | -0.03067 | 0.16237 | 0.2349 | 0.064455 | -0.019364 | 0.01161 | 0.055266 | -0.015171 | 0.047188 | 0.20882 | 0.092236 | 0.079549 | 0.094003 | 0.09577 | 0.17255 | 0.079193 | 0.20357 | 0.2761 | 0.10565 | 0.021835 | 0.052809 | 0.096465 | 0.026028 | 0.088387 | 0.15076 | 0.17754 | 0.052845 | 0.079626
4820.4688 | 122.2183 | -0.07782 | 121.9482 | 0.098959 | -0.017627 | -0.034893 | -0.025017 | -0.009515 | 0.062691 | -0.03067 | 0.17153 | 0.24863 | 0.064455 | -0.023943 | 0.025345 | 0.055266 | -0.015171 | 0.047188 | 0.17678 | 0.060193 | 0.042927 | 0.052803 | 0.068305 | 0.14051 | 0.04715 | 0.21273 | 0.28983 | 0.10565 | 0.017256 | 0.066544 | 0.096465 | 0.026028 | 0.088387 | 0.14618 | 0.1867 | 0.03911 | 0.079626
4822.1875 | 122.1039 | -0.1236 | 121.9757 | 0.10354 | -0.008469 | -0.030314 | -0.020438 | -0.014093 | 0.058113 | -0.026092 | 0.16237 | 0.23948 | 0.059877 | -0.019364 | 0.016188 | 0.050688 | -0.024328 | 0.047188 | 0.22713 | 0.11513 | 0.093282 | 0.10316 | 0.1095 | 0.18171 | 0.097504 | 0.20357 | 0.28068 | 0.10108 | 0.021835 | 0.057387 | 0.091887 | 0.016871 | 0.088387 | 0.14618 | 0.1867 | 0.043689 | 0.084205
4823.9688 | 122.2092 | -0.07782 | 121.9437 | 0.10354 | -0.017627 | -0.034893 | -0.020438 | -0.004937 | 0.058113 | -0.035248 | 0.16237 | 0.24863 | 0.055298 | -0.014785 | 0.020767 | 0.04611 | -0.024328 | 0.051766 | 0.18136 | 0.060193 | 0.042927 | 0.057382 | 0.072883 | 0.13593 | 0.042572 | 0.20357 | 0.28983 | 0.096497 | 0.026414 | 0.061966 | 0.087309 | 0.016871 | 0.092965 | 0.1416 | 0.1867 | 0.034531 | 0.079626
4825.6719 | 122.1588 | -0.07782 | 121.962 | 0.10354 | -0.008469 | -0.034893 | -0.025017 | -0.023249 | 0.053534 | -0.03067 | 0.16695 | 0.24405 | 0.059877 | -0.014785 | 0.016188 | 0.055266 | -0.010593 | 0.04261 | 0.18136 | 0.069351 | 0.042927 | 0.052803 | 0.054571 | 0.13135 | 0.04715 | 0.20815 | 0.28525 | 0.10108 | 0.026414 | 0.057387 | 0.096465 | 0.030606 | 0.083809 | 0.15076 | 0.17754 | 0.043689 | 0.07047
4827.4375 | 122.1176 | -0.11444 | 121.9849 | 0.098959 | -0.008469 | -0.030314 | -0.020438 | -0.009515 | 0.058113 | -0.026092 | 0.16237 | 0.24405 | 0.059877 | -0.019364 | 0.016188 | 0.055266 | -0.015171 | 0.04261 | 0.2134 | 0.10597 | 0.084127 | 0.094003 | 0.10493 | 0.17255 | 0.088349 | 0.20357 | 0.28525 | 0.10108 | 0.021835 | 0.057387 | 0.096465 | 0.026028 | 0.083809 | 0.14618 | 0.17754 | 0.043689 | 0.075048
4829.2188 | 122.2412 | -0.07782 | 121.9757 | 0.10354 | -0.013048 | -0.039471 | -0.025017 | -0.014093 | 0.058113 | -0.03067 | 0.15779 | 0.23948 | 0.069033 | -0.023943 | 0.01161 | 0.050688 | -0.019749 | 0.038032 | 0.18136 | 0.064772 | 0.038349 | 0.052803 | 0.063727 | 0.13593 | 0.04715 | 0.19899 | 0.28068 | 0.11023 | 0.017256 | 0.052809 | 0.091887 | 0.02145 | 0.079231 | 0.14618 | 0.17754 | 0.057423 | 0.088782
4830.9844 | 122.1359 | -0.10071 | 121.994 | 0.098959 | -0.008469 | -0.034893 | -0.020438 | -0.018671 | 0.058113 | -0.03067 | 0.16237 | 0.23948 | 0.064455 | -0.023943 | 0.01161 | 0.055266 | -0.019749 | 0.038032 | 0.19967 | 0.092239 | 0.065815 | 0.08027 | 0.082037 | 0.15882 | 0.070038 | 0.20357 | 0.28068 | 0.10565 | 0.017256 | 0.052809 | 0.096465 | 0.02145 | 0.079231 | 0.15076 | 0.18212 | 0.052845 | 0.084204
4832.6875 | 122.1359 | -0.10071 | 122.0032 | 0.098959 | -0.008469 | -0.030314 | -0.020438 | -0.014093 | 0.071848 | -0.026092 | 0.15779 | 0.24405 | 0.069033 | -0.019364 | 0.01161 | 0.055266 | -0.019749 | 0.04261 | 0.19967 | 0.092239 | 0.070394 | 0.08027 | 0.086615 | 0.17256 | 0.074616 | 0.19899 | 0.28525 | 0.11023 | 0.021835 | 0.052809 | 0.096465 | 0.02145 | 0.083809 | 0.14618 | 0.17754 | 0.057423 | 0.088782
4834.4688 | 122.1542 | -0.09613 | 121.9894 | 0.098959 | -0.008469 | -0.030314 | -0.020438 | -0.014093 | 0.058113 | -0.03067 | 0.15779 | 0.23948 | 0.059877 | -0.023943 | 0.016188 | 0.055266 | -0.024328 | 0.047188 | 0.19509 | 0.087661 | 0.065816 | 0.075692 | 0.082037 | 0.15424 | 0.06546 | 0.19899 | 0.28068 | 0.10108 | 0.017256 | 0.057387 | 0.096465 | 0.016871 | 0.088387 | 0.1416 | 0.18212 | 0.043689 | 0.084205
4836.1562 | 122.1085 | -0.13275 | 122.049 | 0.10354 | -0.013048 | -0.039471 | -0.020438 | -0.009515 | 0.067269 | -0.016936 | 0.16237 | 0.23948 | 0.064455 | -0.019364 | 0.016188 | 0.050688 | -0.015171 | 0.038032 | 0.23629 | 0.1197 | 0.09328 | 0.11231 | 0.12324 | 0.20002 | 0.11582 | 0.20357 | 0.28068 | 0.10565 | 0.021835 | 0.057387 | 0.091887 | 0.026028 | 0.079231 | 0.14618 | 0.17754 | 0.048267 | 0.079626
4837.9219 | 122.1085 | -0.11444 | 122.0215 | 0.10812 | -0.017627 | -0.025735 | -0.025017 | -0.014093 | 0.067269 | -0.026092 | 0.14864 | 0.23948 | 0.059877 | -0.019364 | 0.016188 | 0.050688 | -0.024328 | 0.038032 | 0.22256 | 0.096814 | 0.088706 | 0.089424 | 0.10035 | 0.18171 | 0.088349 | 0.18983 | 0.28068 | 0.10108 | 0.021835 | 0.057387 | 0.091887 | 0.016871 | 0.079231 | 0.13245 | 0.17296 | 0.043689 | 0.084205
4839.6875 | 122.1085 | -0.12817 | 122.0398 | 0.098959 | -0.013048 | -0.034893 | -0.020438 | -0.004937 | 0.062691 | -0.021514 | 0.15321 | 0.23032 | 0.059877 | -0.019364 | 0.01161 | 0.055266 | -0.015171 | 0.04261 | 0.22713 | 0.11513 | 0.093281 | 0.10774 | 0.12324 | 0.19087 | 0.10666 | 0.19441 | 0.27152 | 0.10108 | 0.021835 | 0.052809 | 0.096465 | 0.026028 | 0.083809 | 0.1416 | 0.16839 | 0.048267 | 0.075048
4841.3906 | 122.1359 | -0.09613 | 122.0123 | 0.10812 | -0.008469 | -0.025735 | -0.020438 | -0.023249 | 0.067269 | -0.03067 | 0.15779 | 0.24405 | 0.064455 | -0.023943 | 0.007032 | 0.055266 | -0.015171 | 0.04261 | 0.20425 | 0.087661 | 0.070395 | 0.075692 | 0.072881 | 0.1634 | 0.06546 | 0.19899 | 0.28525 | 0.10565 | 0.017256 | 0.048231 | 0.096465 | 0.026028 | 0.083809 | 0.15076 | 0.17296 | 0.057423 | 0.079626
4843.1562 | 122.2 | -0.09613 | 121.9711 | 0.10354 | -0.017627 | -0.030314 | -0.029595 | -0.014093 | 0.062691 | -0.026092 | 0.15321 | 0.2349 | 0.064455 | -0.019364 | 0.01161 | 0.050688 | -0.019749 | 0.04261 | 0.19967 | 0.078503 | 0.065816 | 0.066535 | 0.082037 | 0.15882 | 0.070038 | 0.19441 | 0.2761 | 0.10565 | 0.021835 | 0.052809 | 0.091887 | 0.02145 | 0.083809 | 0.1416 | 0.17296 | 0.052845 | 0.084204
4844.8594 | 122.1725 | -0.086975 | 122.0078 | 0.098959 | -0.013048 | -0.030314 | -0.025017 | -0.000359 | 0.062691 | -0.03067 | 0.15321 | 0.2349 | 0.064455 | -0.010206 | 0.01161 | 0.055266 | -0.019749 | 0.033454 | 0.18593 | 0.073927 | 0.056661 | 0.061958 | 0.086616 | 0.14967 | 0.056305 | 0.19441 | 0.2761 | 0.10565 | 0.030993 | 0.052809 | 0.096465 | 0.02145 | 0.074653 | 0.1416 | 0.17296 | 0.052845 | 0.084204
4846.625 | 122.2412 | -0.064087 | 121.9803 | 0.094381 | -0.013048 | -0.034893 | -0.025017 | -0.009515 | 0.058113 | -0.026092 | 0.14864 | 0.23948 | 0.064455 | -0.028522 | 0.01161 | 0.04611 | -0.010593 | 0.047188 | 0.15847 | 0.051039 | 0.029194 | 0.03907 | 0.054572 | 0.1222 | 0.037995 | 0.18983 | 0.28068 | 0.10565 | 0.012677 | 0.052809 | 0.087309 | 0.030606 | 0.088387 | 0.13703 | 0.15923 | 0.052845 | 0.075048
4848.3906 | 122.2458 | -0.07782 | 122.0078 | 0.098959 | -0.017627 | -0.034893 | -0.025017 | -0.009515 | 0.067269 | -0.021514 | 0.15321 | 0.2349 | 0.059877 | -0.023943 | 0.007032 | 0.050688 | -0.019749 | 0.047188 | 0.17678 | 0.060193 | 0.042927 | 0.052803 | 0.068305 | 0.14509 | 0.056306 | 0.19441 | 0.2761 | 0.10108 | 0.017256 | 0.048231 | 0.091887 | 0.02145 | 0.088387 | 0.14618 | 0.17296 | 0.052845 | 0.079626
4850.1562 | 122.1588 | -0.09613 | 122.0444 | 0.10354 | -0.008469 | -0.025735 | -0.020438 | -0.009515 | 0.058113 | -0.021514 | 0.14864 | 0.23948 | 0.059877 | -0.014785 | 0.016188 | 0.050688 | -0.024328 | 0.04261 | 0.19967 | 0.087661 | 0.070395 | 0.075692 | 0.086615 | 0.15424 | 0.074616 | 0.18983 | 0.28068 | 0.10108 | 0.026414 | 0.057387 | 0.091887 | 0.016871 | 0.083809 | 0.13245 | 0.17296 | 0.043689 | 0.084205
4851.8594 | 122.1634 | -0.1236 | 122.0398 | 0.098959 | -0.013048 | -0.034893 | -0.01586 | -0.014093 | 0.062691 | -0.026092 | 0.15779 | 0.23032 | 0.064455 | -0.019364 | 0.01161 | 0.050688 | -0.019749 | 0.04261 | 0.22256 | 0.11055 | 0.088703 | 0.10774 | 0.1095 | 0.18629 | 0.097504 | 0.19899 | 0.27152 | 0.10565 | 0.021835 | 0.052809 | 0.091887 | 0.02145 | 0.083809 | 0.14618 | 0.17754 | 0.052845 | 0.084204
4853.625 | 122.1497 | -0.10071 | 122.0215 | 0.098959 | -0.013048 | -0.025735 | -0.020438 | -0.009515 | 0.058113 | -0.026092 | 0.14864 | 0.2349 | 0.055298 | -0.023943 | 0.01161 | 0.055266 | -0.019749 | 0.047188 | 0.19967 | 0.08766 | 0.074973 | 0.08027 | 0.091193 | 0.15882 | 0.074616 | 0.18983 | 0.2761 | 0.096497 | 0.017256 | 0.052809 | 0.096465 | 0.02145 | 0.088387 | 0.13703 | 0.16838 | 0.043688 | 0.075047
4855.3438 | 122.2092 | -0.07782 | 122.0306 | 0.098959 | -0.013048 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.021514 | 0.15779 | 0.24405 | 0.059877 | -0.019364 | 0.01161 | 0.050688 | -0.015171 | 0.051766 | 0.17678 | 0.064772 | 0.047506 | 0.057382 | 0.059149 | 0.13593 | 0.056306 | 0.19899 | 0.28525 | 0.10108 | 0.021835 | 0.052809 | 0.091887 | 0.026028 | 0.092965 | 0.14618 | 0.17296 | 0.048267 | 0.075048
4857.125 | 122.1268 | -0.1236 | 122.0215 | 0.10354 | -0.008469 | -0.030314 | -0.020438 | -0.009515 | 0.071848 | -0.016936 | 0.14864 | 0.23948 | 0.059877 | -0.028522 | 0.01161 | 0.050688 | -0.015171 | 0.038032 | 0.22713 | 0.11513 | 0.093282 | 0.10316 | 0.11408 | 0.19544 | 0.10666 | 0.18983 | 0.28068 | 0.10108 | 0.012677 | 0.052809 | 0.091887 | 0.026028 | 0.079231 | 0.13703 | 0.16381 | 0.048267 | 0.075048
4858.8281 | 122.1222 | -0.11902 | 122.0444 | 0.10812 | -0.008469 | -0.030314 | -0.025017 | -0.009515 | 0.058113 | -0.026092 | 0.15321 | 0.23032 | 0.064455 | -0.019364 | 0.007032 | 0.050688 | -0.024328 | 0.038032 | 0.22714 | 0.11055 | 0.088705 | 0.094002 | 0.1095 | 0.17713 | 0.092927 | 0.19441 | 0.27152 | 0.10565 | 0.021835 | 0.048231 | 0.091887 | 0.016871 | 0.079231 | 0.14618 | 0.17754 | 0.057423 | 0.088783
4860.5938 | 122.1085 | -0.10986 | 122.0627 | 0.098959 | -0.00389 | -0.039471 | -0.020438 | -0.018671 | 0.067269 | -0.021514 | 0.14406 | 0.24405 | 0.059877 | -0.019364 | 0.016188 | 0.055266 | -0.024328 | 0.038032 | 0.20882 | 0.10597 | 0.070392 | 0.089425 | 0.091192 | 0.17713 | 0.088349 | 0.18526 | 0.28525 | 0.10108 | 0.021835 | 0.057387 | 0.096465 | 0.016871 | 0.079231 | 0.12787 | 0.16839 | 0.043689 | 0.084205
4862.3594 | 122.2458 | -0.073242 | 121.9894 | 0.098959 | -0.008469 | -0.039471 | -0.020438 | -0.009515 | 0.067269 | -0.026092 | 0.14406 | 0.2349 | 0.064455 | -0.019364 | 0.016188 | 0.050688 | -0.015171 | 0.038032 | 0.1722 | 0.064773 | 0.033771 | 0.052804 | 0.063727 | 0.14051 | 0.04715 | 0.18526 | 0.2761 | 0.10565 | 0.021835 | 0.057387 | 0.091887 | 0.026028 | 0.079231 | 0.12787 | 0.15923 | 0.048267 | 0.079626
4864.0781 | 122.2366 | -0.091553 | 122.0261 | 0.098959 | -0.017627 | -0.030314 | -0.029595 | -0.009515 | 0.067269 | -0.03067 | 0.14864 | 0.22574 | 0.073611 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.19051 | 0.073926 | 0.061239 | 0.061958 | 0.082038 | 0.15882 | 0.060883 | 0.18983 | 0.26694 | 0.11481 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.13245 | 0.16838 | 0.057423 | 0.09336
4865.8438 | 122.1497 | -0.10071 | 122.0764 | 0.10354 | -0.013048 | -0.030314 | -0.020438 | -0.009515 | 0.062691 | -0.021514 | 0.14864 | 0.23032 | 0.055298 | -0.023943 | 0.01161 | 0.059844 | -0.015171 | 0.038032 | 0.20425 | 0.08766 | 0.070394 | 0.08027 | 0.091193 | 0.1634 | 0.079194 | 0.18983 | 0.27152 | 0.096497 | 0.017256 | 0.052809 | 0.10104 | 0.026028 | 0.079231 | 0.13703 | 0.16381 | 0.043688 | 0.070469
4867.6094 | 122.2458 | -0.068665 | 122.0444 | 0.098959 | -0.017627 | -0.030314 | -0.029595 | -0.009515 | 0.053534 | -0.035248 | 0.14864 | 0.23032 | 0.055298 | -0.023943 | 0.016188 | 0.050688 | -0.015171 | 0.04261 | 0.16762 | 0.051038 | 0.038351 | 0.03907 | 0.05915 | 0.1222 | 0.033417 | 0.18983 | 0.27152 | 0.096497 | 0.017256 | 0.057387 | 0.091887 | 0.026028 | 0.083809 | 0.13245 | 0.16381 | 0.03911 | 0.070469
4869.3281 | 122.2275 | -0.068665 | 122.0032 | 0.10354 | -0.013048 | -0.030314 | -0.025017 | -0.014093 | 0.062691 | -0.03067 | 0.14406 | 0.23032 | 0.059877 | -0.028522 | 0.01161 | 0.04611 | -0.015171 | 0.047188 | 0.1722 | 0.055617 | 0.038351 | 0.043648 | 0.054572 | 0.13136 | 0.037995 | 0.18526 | 0.27152 | 0.10108 | 0.012677 | 0.052809 | 0.087309 | 0.026028 | 0.088387 | 0.13245 | 0.15923 | 0.048267 | 0.075048
4871.0938 | 122.1817 | -0.10071 | 122.0764 | 0.098959 | -0.008469 | -0.030314 | -0.01586 | -0.009515 | 0.062691 | -0.026092 | 0.14864 | 0.22574 | 0.064455 | -0.023943 | 0.016188 | 0.055266 | -0.019749 | 0.04261 | 0.19967 | 0.092239 | 0.070394 | 0.084848 | 0.091193 | 0.1634 | 0.074616 | 0.18983 | 0.26694 | 0.10565 | 0.017256 | 0.057387 | 0.096465 | 0.02145 | 0.083809 | 0.13245 | 0.16838 | 0.048267 | 0.084204
4872.7969 | 122.1725 | -0.11444 | 122.049 | 0.10354 | -0.017627 | -0.034893 | -0.020438 | -0.014093 | 0.067269 | -0.026092 | 0.14406 | 0.2349 | 0.055298 | -0.023943 | 0.007032 | 0.050688 | -0.024328 | 0.04261 | 0.21798 | 0.096814 | 0.079548 | 0.094003 | 0.10035 | 0.18171 | 0.088349 | 0.18526 | 0.2761 | 0.096497 | 0.017256 | 0.048231 | 0.091887 | 0.016871 | 0.083809 | 0.13703 | 0.16839 | 0.048266 | 0.079626
4874.5781 | 122.2641 | -0.091553 | 122.0078 | 0.098959 | -0.017627 | -0.030314 | -0.025017 | -0.014093 | 0.062691 | -0.021514 | 0.14864 | 0.22574 | 0.064455 | -0.019364 | 0.01161 | 0.050688 | -0.015171 | 0.047188 | 0.19051 | 0.073926 | 0.061239 | 0.066536 | 0.07746 | 0.15424 | 0.070039 | 0.18983 | 0.26694 | 0.10565 | 0.021835 | 0.052809 | 0.091887 | 0.026028 | 0.088387 | 0.13703 | 0.16381 | 0.052845 | 0.079626
4876.3438 | 122.2275 | -0.082397 | 121.9986 | 0.094381 | -0.013048 | -0.034893 | -0.01586 | -0.004937 | 0.058113 | -0.026092 | 0.1349 | 0.23032 | 0.059877 | -0.019364 | 0.020767 | 0.050688 | -0.015171 | 0.038032 | 0.17678 | 0.069349 | 0.047504 | 0.066537 | 0.07746 | 0.14051 | 0.056305 | 0.1761 | 0.27152 | 0.10108 | 0.021835 | 0.061966 | 0.091887 | 0.026028 | 0.079231 | 0.11413 | 0.15007 | 0.03911 | 0.075048
4878.1094 | 122.2229 | -0.09613 | 122.049 | 0.098959 | -0.022205 | -0.030314 | -0.029595 | -0.018671 | 0.058113 | -0.03067 | 0.13948 | 0.23032 | 0.055298 | -0.019364 | 0.007032 | 0.04611 | -0.015171 | 0.047188 | 0.19509 | 0.073925 | 0.065816 | 0.066535 | 0.077459 | 0.15424 | 0.06546 | 0.18068 | 0.27152 | 0.096497 | 0.021835 | 0.048231 | 0.087309 | 0.026028 | 0.088387 | 0.13245 | 0.15465 | 0.048266 | 0.070469
4879.8125 | 122.2229 | -0.10986 | 122.0306 | 0.098959 | -0.017627 | -0.034893 | -0.020438 | -0.014093 | 0.058113 | -0.026092 | 0.1349 | 0.22574 | 0.055298 | -0.019364 | 0.016188 | 0.059844 | -0.019749 | 0.04261 | 0.20882 | 0.092236 | 0.07497 | 0.089425 | 0.09577 | 0.16798 | 0.083771 | 0.1761 | 0.26694 | 0.096497 | 0.021835 | 0.057387 | 0.10104 | 0.02145 | 0.083809 | 0.11871 | 0.15465 | 0.03911 | 0.075047
4881.5781 | 122.1863 | -0.091553 | 122.0535 | 0.098959 | -0.013048 | -0.039471 | -0.020438 | -0.009515 | 0.062691 | -0.021514 | 0.1349 | 0.22116 | 0.059877 | -0.023943 | 0.01161 | 0.050688 | -0.015171 | 0.047188 | 0.19051 | 0.078505 | 0.052082 | 0.071115 | 0.082038 | 0.15424 | 0.070039 | 0.1761 | 0.26236 | 0.10108 | 0.017256 | 0.052809 | 0.091887 | 0.026028 | 0.088387 | 0.12329 | 0.15007 | 0.048267 | 0.075048
4883.3281 | 122.2458 | -0.09613 | 122.0261 | 0.10354 | -0.008469 | -0.034893 | -0.029595 | -0.014093 | 0.067269 | -0.026092 | 0.14406 | 0.22574 | 0.059877 | -0.010206 | 0.020767 | 0.055266 | -0.015171 | 0.04261 | 0.19967 | 0.087661 | 0.061237 | 0.066535 | 0.082037 | 0.1634 | 0.070038 | 0.18526 | 0.26694 | 0.10108 | 0.030993 | 0.061966 | 0.096465 | 0.026028 | 0.083809 | 0.12329 | 0.15923 | 0.03911 | 0.075048
4885.0469 | 122.2275 | -0.068665 | 122.0352 | 0.094381 | -0.008469 | -0.039471 | -0.01586 | -0.018671 | 0.062691 | -0.021514 | 0.13948 | 0.23032 | 0.064455 | -0.019364 | 0.020767 | 0.055266 | -0.024328 | 0.047188 | 0.16305 | 0.060196 | 0.029194 | 0.052805 | 0.049994 | 0.13136 | 0.047151 | 0.18068 | 0.27152 | 0.10565 | 0.021835 | 0.061966 | 0.096465 | 0.016871 | 0.088387 | 0.11871 | 0.16381 | 0.043688 | 0.088783
4886.8125 | 122.2 | -0.11902 | 122.0764 | 0.098959 | -0.008469 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.026092 | 0.1349 | 0.22574 | 0.055298 | -0.023943 | 0.01161 | 0.059844 | -0.019749 | 0.047188 | 0.21798 | 0.11055 | 0.088705 | 0.098581 | 0.10035 | 0.17713 | 0.092927 | 0.1761 | 0.26694 | 0.096497 | 0.017256 | 0.052809 | 0.10104 | 0.02145 | 0.088387 | 0.12329 | 0.15465 | 0.043688 | 0.075047
4888.5781 | 122.1542 | -0.11444 | 122.0718 | 0.098959 | -0.008469 | -0.021157 | -0.025017 | -0.014093 | 0.067269 | -0.03067 | 0.1349 | 0.22116 | 0.059877 | -0.014785 | 0.020767 | 0.055266 | -0.024328 | 0.051766 | 0.2134 | 0.10597 | 0.093284 | 0.089424 | 0.10035 | 0.18171 | 0.083771 | 0.1761 | 0.26236 | 0.10108 | 0.026414 | 0.061966 | 0.096465 | 0.016871 | 0.092965 | 0.11413 | 0.15923 | 0.03911 | 0.084205
4890.2812 | 122.168 | -0.12817 | 122.0535 | 0.10354 | -0.00389 | -0.030314 | -0.025017 | -0.014093 | 0.067269 | -0.026092 | 0.14406 | 0.21658 | 0.05072 | -0.019364 | 0.01161 | 0.050688 | -0.024328 | 0.047188 | 0.23171 | 0.12428 | 0.09786 | 0.10316 | 0.11408 | 0.19544 | 0.10208 | 0.18526 | 0.25778 | 0.091919 | 0.021835 | 0.052809 | 0.091887 | 0.016871 | 0.088387 | 0.13245 | 0.16839 | 0.03911 | 0.075048
4892.0469 | 122.2641 | -0.064087 | 122.0169 | 0.098959 | -0.017627 | -0.034893 | -0.034174 | -0.014093 | 0.058113 | -0.026092 | 0.13948 | 0.22574 | 0.055298 | -0.019364 | 0.016188 | 0.059844 | -0.019749 | 0.04261 | 0.16305 | 0.04646 | 0.029194 | 0.029913 | 0.049994 | 0.1222 | 0.037995 | 0.18068 | 0.26694 | 0.096497 | 0.021835 | 0.057387 | 0.10104 | 0.02145 | 0.083809 | 0.12329 | 0.15923 | 0.03911 | 0.075047
4893.75 | 122.1588 | -0.1236 | 122.0718 | 0.10354 | -0.008469 | -0.025735 | -0.025017 | -0.004937 | 0.062691 | -0.026092 | 0.1349 | 0.22574 | 0.059877 | -0.028522 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.22713 | 0.11513 | 0.097861 | 0.098579 | 0.11866 | 0.18629 | 0.097504 | 0.1761 | 0.26694 | 0.10108 | 0.012677 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.11871 | 0.15465 | 0.043689 | 0.079626
4895.5312 | 122.1497 | -0.13275 | 122.0673 | 0.098959 | -0.013048 | -0.034893 | -0.020438 | -0.004937 | 0.062691 | -0.026092 | 0.13032 | 0.22574 | 0.059877 | -0.023943 | 0.016188 | 0.04611 | -0.015171 | 0.047188 | 0.23171 | 0.1197 | 0.097858 | 0.11231 | 0.12781 | 0.19544 | 0.10666 | 0.17152 | 0.26694 | 0.10108 | 0.017256 | 0.057387 | 0.087309 | 0.026028 | 0.088387 | 0.11413 | 0.14549 | 0.043689 | 0.075048
4897.2969 | 122.1542 | -0.11444 | 122.0581 | 0.098959 | -0.017627 | -0.034893 | -0.029595 | -0.004937 | 0.062691 | -0.026092 | 0.13032 | 0.22116 | 0.055298 | -0.023943 | 0.020767 | 0.050688 | -0.015171 | 0.04261 | 0.2134 | 0.096814 | 0.079548 | 0.084846 | 0.1095 | 0.17713 | 0.088349 | 0.17152 | 0.26236 | 0.096497 | 0.017256 | 0.061966 | 0.091887 | 0.026028 | 0.083809 | 0.10955 | 0.14549 | 0.034531 | 0.070469
4899.0625 | 122.1588 | -0.13733 | 122.0856 | 0.10354 | -0.013048 | -0.034893 | -0.020438 | -0.009515 | 0.062691 | -0.026092 | 0.13032 | 0.21658 | 0.059877 | -0.023943 | 0.01161 | 0.04611 | -0.024328 | 0.047188 | 0.24087 | 0.12428 | 0.10244 | 0.11689 | 0.12781 | 0.20002 | 0.11124 | 0.17152 | 0.25778 | 0.10108 | 0.017256 | 0.052809 | 0.087309 | 0.016871 | 0.088387 | 0.11871 | 0.15465 | 0.048267 | 0.084205
4900.8281 | 122.1771 | -0.11444 | 122.0535 | 0.098959 | -0.008469 | -0.025735 | -0.020438 | -0.018671 | 0.067269 | -0.021514 | 0.13032 | 0.22116 | 0.064455 | -0.019364 | 0.020767 | 0.041532 | -0.015171 | 0.051766 | 0.2134 | 0.10597 | 0.088706 | 0.094003 | 0.09577 | 0.18171 | 0.092927 | 0.17152 | 0.26236 | 0.10565 | 0.021835 | 0.061966 | 0.082731 | 0.026028 | 0.092965 | 0.10955 | 0.14549 | 0.043688 | 0.079626
4902.5938 | 122.2412 | -0.073242 | 122.049 | 0.10354 | -0.008469 | -0.030314 | -0.025017 | -0.009515 | 0.067269 | -0.021514 | 0.1349 | 0.22116 | 0.059877 | -0.019364 | 0.016188 | 0.050688 | -0.024328 | 0.047188 | 0.17678 | 0.064773 | 0.042928 | 0.048225 | 0.063727 | 0.14051 | 0.051728 | 0.1761 | 0.26236 | 0.10108 | 0.021835 | 0.057387 | 0.091887 | 0.016871 | 0.088387 | 0.11871 | 0.15923 | 0.043689 | 0.084205
4904.3125 | 122.2412 | -0.064087 | 122.0215 | 0.10354 | -0.013048 | -0.025735 | -0.020438 | -0.018671 | 0.058113 | -0.026092 | 0.13948 | 0.22574 | 0.055298 | -0.028522 | 0.016188 | 0.04611 | -0.019749 | 0.038032 | 0.16762 | 0.051039 | 0.038352 | 0.043649 | 0.045416 | 0.1222 | 0.037995 | 0.18068 | 0.26694 | 0.096497 | 0.012677 | 0.057387 | 0.087309 | 0.02145 | 0.079231 | 0.12329 | 0.15923 | 0.03911 | 0.075047
4906.0781 | 122.287 | -0.064087 | 122.0398 | 0.10354 | -0.017627 | -0.030314 | -0.025017 | -0.004937 | 0.062691 | -0.026092 | 0.1349 | 0.22116 | 0.069033 | -0.028522 | 0.016188 | 0.050688 | -0.019749 | 0.047188 | 0.16762 | 0.04646 | 0.033773 | 0.03907 | 0.05915 | 0.12678 | 0.037995 | 0.1761 | 0.26236 | 0.11023 | 0.012677 | 0.057387 | 0.091887 | 0.02145 | 0.088387 | 0.11871 | 0.15465 | 0.052845 | 0.088782
4907.8438 | 122.1634 | -0.13275 | 122.081 | 0.10354 | -0.013048 | -0.025735 | -0.020438 | -0.004937 | 0.071848 | -0.016936 | 0.1349 | 0.21658 | 0.055298 | -0.028522 | 0.01161 | 0.04611 | -0.024328 | 0.04261 | 0.23629 | 0.1197 | 0.10702 | 0.11231 | 0.12781 | 0.2046 | 0.11582 | 0.1761 | 0.25778 | 0.096497 | 0.012677 | 0.052809 | 0.087309 | 0.016871 | 0.083809 | 0.12329 | 0.15923 | 0.043688 | 0.079626
4909.625 | 122.2366 | -0.086975 | 122.0261 | 0.094381 | -0.017627 | -0.025735 | -0.020438 | -0.009515 | 0.062691 | -0.021514 | 0.1349 | 0.21658 | 0.064455 | -0.023943 | 0.020767 | 0.059844 | -0.015171 | 0.051766 | 0.18136 | 0.069348 | 0.06124 | 0.066537 | 0.07746 | 0.14967 | 0.065461 | 0.1761 | 0.25778 | 0.10565 | 0.017256 | 0.061966 | 0.10104 | 0.026028 | 0.092965 | 0.11413 | 0.15007 | 0.043688 | 0.079626
4911.3438 | 122.2549 | -0.068665 | 122.0123 | 0.10354 | -0.013048 | -0.030314 | -0.020438 | -0.014093 | 0.062691 | -0.03067 | 0.13032 | 0.22574 | 0.055298 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.047188 | 0.1722 | 0.055617 | 0.038351 | 0.048227 | 0.054572 | 0.13136 | 0.037995 | 0.17152 | 0.26694 | 0.096497 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.088387 | 0.11413 | 0.15007 | 0.03911 | 0.075047
4913.1094 | 122.1634 | -0.11444 | 122.0673 | 0.094381 | -0.017627 | -0.039471 | -0.020438 | -0.014093 | 0.067269 | -0.026092 | 0.13032 | 0.22116 | 0.059877 | -0.023943 | 0.007032 | 0.055266 | -0.019749 | 0.04261 | 0.20882 | 0.096814 | 0.07497 | 0.094003 | 0.10035 | 0.18171 | 0.088349 | 0.17152 | 0.26236 | 0.10108 | 0.017256 | 0.048231 | 0.096465 | 0.02145 | 0.083809 | 0.12329 | 0.15007 | 0.052845 | 0.079626
4914.875 | 122.1817 | -0.10071 | 122.049 | 0.098959 | -0.008469 | -0.030314 | -0.025017 | -0.014093 | 0.062691 | -0.021514 | 0.13948 | 0.212 | 0.059877 | -0.023943 | 0.016188 | 0.050688 | -0.015171 | 0.04261 | 0.19967 | 0.092239 | 0.070394 | 0.075691 | 0.086615 | 0.1634 | 0.079194 | 0.18068 | 0.2532 | 0.10108 | 0.017256 | 0.057387 | 0.091887 | 0.026028 | 0.083809 | 0.12329 | 0.15465 | 0.043689 | 0.075048
4916.6562 | 122.2 | -0.11902 | 122.0856 | 0.098959 | -0.017627 | -0.025735 | -0.020438 | -0.009515 | 0.058113 | -0.03067 | 0.13032 | 0.21658 | 0.064455 | -0.023943 | 0.01161 | 0.04611 | -0.015171 | 0.038032 | 0.21798 | 0.10139 | 0.093284 | 0.098581 | 0.1095 | 0.17713 | 0.088349 | 0.17152 | 0.25778 | 0.10565 | 0.017256 | 0.052809 | 0.087309 | 0.026028 | 0.079231 | 0.11871 | 0.14549 | 0.052845 | 0.079626
4918.3594 | 122.2366 | -0.09613 | 122.0352 | 0.098959 | -0.008469 | -0.034893 | -0.020438 | -0.014093 | 0.067269 | -0.021514 | 0.12574 | 0.212 | 0.059877 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.047188 | 0.19509 | 0.087661 | 0.061237 | 0.075692 | 0.082037 | 0.1634 | 0.074616 | 0.16694 | 0.2532 | 0.10108 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.088387 | 0.11413 | 0.14091 | 0.048267 | 0.075048
4920.125 | 122.1405 | -0.12817 | 122.0673 | 0.11727 | -0.013048 | -0.030314 | -0.020438 | -0.014093 | 0.067269 | -0.026092 | 0.13032 | 0.22116 | 0.059877 | -0.019364 | 0.01161 | 0.059844 | -0.015171 | 0.047188 | 0.24545 | 0.11513 | 0.09786 | 0.10774 | 0.11408 | 0.19544 | 0.10208 | 0.17152 | 0.26236 | 0.10108 | 0.021835 | 0.052809 | 0.10104 | 0.026028 | 0.088387 | 0.11871 | 0.14549 | 0.048267 | 0.075048
4921.8281 | 122.2321 | -0.073242 | 122.0444 | 0.10354 | -0.013048 | -0.030314 | -0.025017 | -0.009515 | 0.071848 | -0.021514 | 0.1349 | 0.22574 | 0.064455 | -0.019364 | 0.007032 | 0.050688 | -0.028906 | 0.04261 | 0.17678 | 0.060194 | 0.042928 | 0.048225 | 0.063727 | 0.14509 | 0.051728 | 0.1761 | 0.26694 | 0.10565 | 0.021835 | 0.048231 | 0.091887 | 0.012293 | 0.083809 | 0.12787 | 0.16381 | 0.057423 | 0.093361
4923.5938 | 122.168 | -0.10529 | 122.0764 | 0.098959 | -0.017627 | -0.025735 | -0.025017 | -0.014093 | 0.071848 | -0.026092 | 0.1349 | 0.22116 | 0.055298 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.04261 | 0.20425 | 0.087659 | 0.079551 | 0.080269 | 0.091193 | 0.17713 | 0.079194 | 0.1761 | 0.26236 | 0.096497 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.083809 | 0.12329 | 0.15007 | 0.043688 | 0.070469
4925.3594 | 122.168 | -0.10529 | 122.0947 | 0.10354 | -0.013048 | -0.030314 | -0.025017 | -0.009515 | 0.067269 | -0.016936 | 0.13032 | 0.21658 | 0.059877 | -0.014785 | 0.007032 | 0.04611 | -0.019749 | 0.04261 | 0.20882 | 0.092238 | 0.074972 | 0.080269 | 0.095771 | 0.17256 | 0.08835 | 0.17152 | 0.25778 | 0.10108 | 0.026414 | 0.048231 | 0.087309 | 0.02145 | 0.083809 | 0.12329 | 0.15007 | 0.052845 | 0.079626
4927.0625 | 122.2641 | -0.07782 | 122.049 | 0.10354 | -0.008469 | -0.030314 | -0.025017 | -0.014093 | 0.062691 | -0.026092 | 0.12116 | 0.21658 | 0.059877 | -0.019364 | 0.007032 | 0.055266 | -0.019749 | 0.04261 | 0.18136 | 0.069351 | 0.047506 | 0.052803 | 0.063727 | 0.14051 | 0.051728 | 0.16236 | 0.25778 | 0.10108 | 0.021835 | 0.048231 | 0.096465 | 0.02145 | 0.083809 | 0.11413 | 0.14091 | 0.052845 | 0.079626
4928.8281 | 122.1542 | -0.12817 | 122.0947 | 0.098959 | -0.017627 | -0.030314 | -0.020438 | -0.009515 | 0.062691 | -0.021514 | 0.12116 | 0.21658 | 0.064455 | -0.023943 | 0.01161 | 0.050688 | -0.015171 | 0.04261 | 0.22713 | 0.11055 | 0.09786 | 0.10774 | 0.11866 | 0.19087 | 0.10666 | 0.16236 | 0.25778 | 0.10565 | 0.017256 | 0.052809 | 0.091887 | 0.026028 | 0.083809 | 0.10955 | 0.13634 | 0.052845 | 0.079626
4930.6094 | 122.2 | -0.13275 | 122.0901 | 0.098959 | -0.013048 | -0.034893 | -0.025017 | -0.014093 | 0.071848 | -0.026092 | 0.12574 | 0.212 | 0.059877 | -0.019364 | 0.016188 | 0.041532 | -0.015171 | 0.04261 | 0.23171 | 0.1197 | 0.097858 | 0.10773 | 0.11866 | 0.2046 | 0.10666 | 0.16694 | 0.2532 | 0.10108 | 0.021835 | 0.057387 | 0.082731 | 0.026028 | 0.083809 | 0.10956 | 0.14091 | 0.043689 | 0.075048
4932.375 | 122.2275 | -0.082397 | 122.0398 | 0.098959 | -0.013048 | -0.030314 | -0.029595 | -0.009515 | 0.062691 | -0.03067 | 0.12116 | 0.22116 | 0.055298 | -0.023943 | 0.020767 | 0.055266 | -0.019749 | 0.047188 | 0.18136 | 0.069349 | 0.052083 | 0.052802 | 0.072882 | 0.14509 | 0.051727 | 0.16236 | 0.26236 | 0.096497 | 0.017256 | 0.061966 | 0.096465 | 0.02145 | 0.088387 | 0.1004 | 0.14091 | 0.034531 | 0.075047
4934.0781 | 122.2412 | -0.07782 | 122.0581 | 0.094381 | -0.022205 | -0.034893 | -0.025017 | -0.014093 | 0.058113 | -0.026092 | 0.11659 | 0.21658 | 0.055298 | -0.019364 | 0.016188 | 0.055266 | -0.019749 | 0.04261 | 0.1722 | 0.055615 | 0.042927 | 0.052803 | 0.063727 | 0.13593 | 0.051728 | 0.15779 | 0.25778 | 0.096497 | 0.021835 | 0.057387 | 0.096465 | 0.02145 | 0.083809 | 0.1004 | 0.13634 | 0.03911 | 0.075047
4935.8438 | 122.2549 | -0.086975 | 122.0535 | 0.089802 | -0.017627 | -0.034893 | -0.020438 | -0.014093 | 0.062691 | -0.03067 | 0.12574 | 0.21658 | 0.055298 | -0.028522 | 0.002454 | 0.064423 | -0.019749 | 0.04261 | 0.17678 | 0.069348 | 0.052082 | 0.066537 | 0.072882 | 0.14967 | 0.056305 | 0.16694 | 0.25778 | 0.096497 | 0.012677 | 0.043653 | 0.10562 | 0.02145 | 0.083809 | 0.12329 | 0.14549 | 0.052844 | 0.075047
4937.5469 | 122.2137 | -0.10071 | 122.0764 | 0.10354 | -0.008469 | -0.030314 | -0.029595 | -0.009515 | 0.067269 | -0.03067 | 0.12116 | 0.21658 | 0.055298 | -0.033101 | 0.016188 | 0.059844 | -0.019749 | 0.047188 | 0.20425 | 0.092239 | 0.070394 | 0.071113 | 0.091193 | 0.16798 | 0.070038 | 0.16236 | 0.25778 | 0.096497 | 0.008098 | 0.057387 | 0.10104 | 0.02145 | 0.088387 | 0.10498 | 0.14091 | 0.03911 | 0.075047
4939.3281 | 122.2687 | -0.091553 | 122.0398 | 0.098959 | -0.008469 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.03067 | 0.11659 | 0.22116 | 0.059877 | -0.023943 | 0.016188 | 0.055266 | -0.015171 | 0.047188 | 0.19051 | 0.083084 | 0.061239 | 0.071115 | 0.072882 | 0.14967 | 0.060883 | 0.15779 | 0.26236 | 0.10108 | 0.017256 | 0.057387 | 0.096465 | 0.026028 | 0.088387 | 0.1004 | 0.13176 | 0.043689 | 0.075048
4941.0312 | 122.2824 | -0.082397 | 122.0352 | 0.10354 | -0.008469 | -0.030314 | -0.025017 | -0.014093 | 0.053534 | -0.03067 | 0.12574 | 0.21658 | 0.064455 | -0.023943 | 0.020767 | 0.055266 | -0.019749 | 0.04261 | 0.18593 | 0.073928 | 0.052083 | 0.05738 | 0.068304 | 0.13593 | 0.051727 | 0.16694 | 0.25778 | 0.10565 | 0.017256 | 0.061966 | 0.096465 | 0.02145 | 0.083809 | 0.10498 | 0.14549 | 0.043688 | 0.084204
4942.7344 | 122.2504 | -0.068665 | 122.0123 | 0.10354 | -0.013048 | -0.034893 | -0.025017 | -0.018671 | 0.058113 | -0.026092 | 0.13032 | 0.21658 | 0.055298 | -0.019364 | 0.020767 | 0.059844 | -0.024328 | 0.047188 | 0.1722 | 0.055617 | 0.033772 | 0.043648 | 0.049994 | 0.12678 | 0.042573 | 0.17152 | 0.25778 | 0.096497 | 0.021835 | 0.061966 | 0.10104 | 0.016871 | 0.088387 | 0.10955 | 0.15465 | 0.034531 | 0.079626
4944.5 | 122.1954 | -0.10986 | 122.0673 | 0.098959 | -0.017627 | -0.034893 | -0.034174 | -0.014093 | 0.062691 | -0.026092 | 0.11659 | 0.212 | 0.059877 | -0.028522 | 0.01161 | 0.055266 | -0.024328 | 0.04261 | 0.20882 | 0.092236 | 0.07497 | 0.075689 | 0.09577 | 0.17255 | 0.083771 | 0.15779 | 0.2532 | 0.10108 | 0.012677 | 0.052809 | 0.096465 | 0.016871 | 0.083809 | 0.10498 | 0.14091 | 0.048267 | 0.084205
4946.2188 | 122.2046 | -0.10986 | 122.049 | 0.094381 | -0.008469 | -0.034893 | -0.020438 | -0.009515 | 0.062691 | -0.026092 | 0.13032 | 0.212 | 0.05072 | -0.019364 | 0.007032 | 0.050688 | -0.015171 | 0.038032 | 0.20424 | 0.10139 | 0.07497 | 0.089425 | 0.10035 | 0.17255 | 0.083771 | 0.17152 | 0.2532 | 0.091919 | 0.021835 | 0.048231 | 0.091887 | 0.026028 | 0.079231 | 0.12329 | 0.14549 | 0.043688 | 0.065891
4947.9844 | 122.2687 | -0.091553 | 122.0169 | 0.10812 | -0.013048 | -0.034893 | -0.020438 | -0.014093 | 0.062691 | -0.026092 | 0.12116 | 0.21658 | 0.055298 | -0.019364 | 0.020767 | 0.059844 | -0.024328 | 0.04261 | 0.19967 | 0.078505 | 0.05666 | 0.071115 | 0.07746 | 0.15424 | 0.065461 | 0.16236 | 0.25778 | 0.096497 | 0.021835 | 0.061966 | 0.10104 | 0.016871 | 0.083809 | 0.1004 | 0.14549 | 0.034531 | 0.079626
4949.75 | 122.1725 | -0.11444 | 122.081 | 0.098959 | -0.013048 | -0.025735 | -0.025017 | -0.014093 | 0.058113 | -0.026092 | 0.11659 | 0.22116 | 0.05072 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.04261 | 0.2134 | 0.10139 | 0.088706 | 0.089424 | 0.10035 | 0.17255 | 0.088349 | 0.15779 | 0.26236 | 0.091919 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.083809 | 0.10498 | 0.13176 | 0.03911 | 0.065891
4951.4531 | 122.1588 | -0.1236 | 122.0718 | 0.10354 | -0.013048 | -0.025735 | -0.01586 | -0.009515 | 0.062691 | -0.026092 | 0.12116 | 0.212 | 0.059877 | -0.023943 | 0.01161 | 0.055266 | -0.028906 | 0.04261 | 0.22713 | 0.11055 | 0.097861 | 0.10774 | 0.11408 | 0.18629 | 0.097504 | 0.16236 | 0.2532 | 0.10108 | 0.017256 | 0.052809 | 0.096465 | 0.012293 | 0.083809 | 0.10955 | 0.15007 | 0.048267 | 0.088783
4953.2031 | 122.2046 | -0.10071 | 122.0581 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.03067 | 0.11201 | 0.212 | 0.059877 | -0.019364 | 0.01161 | 0.04611 | -0.024328 | 0.04261 | 0.20882 | 0.08766 | 0.074973 | 0.084848 | 0.091193 | 0.16798 | 0.070038 | 0.15321 | 0.2532 | 0.10108 | 0.021835 | 0.052809 | 0.087309 | 0.016871 | 0.083809 | 0.1004 | 0.13634 | 0.048267 | 0.084205
4954.9062 | 122.1588 | -0.1236 | 122.0856 | 0.10354 | -0.013048 | -0.025735 | -0.01586 | -0.018671 | 0.062691 | -0.026092 | 0.12116 | 0.21658 | 0.064455 | -0.019364 | 0.020767 | 0.04611 | -0.019749 | 0.051766 | 0.22713 | 0.11055 | 0.097861 | 0.10774 | 0.10492 | 0.18629 | 0.097504 | 0.16236 | 0.25778 | 0.10565 | 0.021835 | 0.061966 | 0.087309 | 0.02145 | 0.092965 | 0.1004 | 0.14091 | 0.043688 | 0.084204
4956.6719 | 122.1588 | -0.10986 | 122.0718 | 0.10354 | -0.017627 | -0.030314 | -0.025017 | -0.004937 | 0.058113 | -0.021514 | 0.12116 | 0.21658 | 0.059877 | -0.023943 | 0.007032 | 0.059844 | -0.019749 | 0.051766 | 0.2134 | 0.092236 | 0.079549 | 0.084846 | 0.10493 | 0.16798 | 0.088349 | 0.16236 | 0.25778 | 0.10108 | 0.017256 | 0.048231 | 0.10104 | 0.02145 | 0.092965 | 0.11413 | 0.14091 | 0.052845 | 0.079626
4958.4375 | 122.1954 | -0.1236 | 122.0581 | 0.10354 | -0.00389 | -0.030314 | -0.020438 | -0.014093 | 0.062691 | -0.016936 | 0.12116 | 0.212 | 0.055298 | -0.023943 | 0.020767 | 0.059844 | -0.024328 | 0.04261 | 0.22713 | 0.11971 | 0.093282 | 0.10316 | 0.1095 | 0.18629 | 0.10666 | 0.16236 | 0.2532 | 0.096497 | 0.017256 | 0.061966 | 0.10104 | 0.016871 | 0.083809 | 0.1004 | 0.14549 | 0.034531 | 0.079626
4960.2031 | 122.2321 | -0.086975 | 122.0352 | 0.10812 | -0.013048 | -0.030314 | -0.01586 | -0.004937 | 0.062691 | -0.026092 | 0.12116 | 0.20742 | 0.069033 | -0.019364 | 0.01161 | 0.050688 | -0.015171 | 0.038032 | 0.19509 | 0.073927 | 0.056661 | 0.071115 | 0.082038 | 0.14967 | 0.060883 | 0.16236 | 0.24862 | 0.11023 | 0.021835 | 0.052809 | 0.091887 | 0.026028 | 0.079231 | 0.10955 | 0.13634 | 0.057423 | 0.084204
4961.9062 | 122.2046 | -0.10986 | 122.049 | 0.10812 | -0.00389 | -0.025735 | -0.025017 | -0.018671 | 0.067269 | -0.026092 | 0.12116 | 0.212 | 0.055298 | -0.028522 | 0.01161 | 0.055266 | -0.015171 | 0.04261 | 0.21798 | 0.10597 | 0.084128 | 0.084846 | 0.091192 | 0.17713 | 0.083771 | 0.16236 | 0.2532 | 0.096497 | 0.012677 | 0.052809 | 0.096465 | 0.026028 | 0.083809 | 0.10955 | 0.13634 | 0.043688 | 0.070469
4963.6719 | 122.2046 | -0.10529 | 122.0673 | 0.098959 | -0.00389 | -0.030314 | -0.01586 | -0.014093 | 0.071848 | -0.026092 | 0.11201 | 0.21658 | 0.064455 | -0.023943 | 0.007032 | 0.055266 | -0.024328 | 0.04261 | 0.20425 | 0.1014 | 0.074972 | 0.089426 | 0.091193 | 0.17713 | 0.079194 | 0.15321 | 0.25778 | 0.10565 | 0.017256 | 0.048231 | 0.096465 | 0.016871 | 0.083809 | 0.10498 | 0.13634 | 0.057423 | 0.088783
4965.3594 | 122.2504 | -0.091553 | 122.0261 | 0.10354 | -0.008469 | -0.025735 | -0.029595 | -0.018671 | 0.067269 | -0.03067 | 0.12574 | 0.212 | 0.055298 | -0.010206 | 0.01161 | 0.050688 | -0.010593 | 0.04261 | 0.19509 | 0.083084 | 0.065818 | 0.061958 | 0.072882 | 0.15882 | 0.060883 | 0.16694 | 0.2532 | 0.096497 | 0.030993 | 0.052809 | 0.091887 | 0.030606 | 0.083809 | 0.11413 | 0.13634 | 0.043688 | 0.065891
4967.1406 | 122.2 | -0.11444 | 122.0352 | 0.098959 | -0.013048 | -0.025735 | -0.020438 | -0.009515 | 0.067269 | -0.021514 | 0.12116 | 0.212 | 0.05072 | -0.028522 | 0.016188 | 0.055266 | -0.019749 | 0.04261 | 0.2134 | 0.10139 | 0.088706 | 0.094003 | 0.10493 | 0.18171 | 0.092927 | 0.16236 | 0.2532 | 0.091919 | 0.012677 | 0.057387 | 0.096465 | 0.02145 | 0.083809 | 0.10498 | 0.14091 | 0.034532 | 0.070469
4968.9062 | 122.2687 | -0.068665 | 122.0123 | 0.094381 | -0.008469 | -0.034893 | -0.020438 | -0.009515 | 0.062691 | -0.03067 | 0.11659 | 0.212 | 0.064455 | -0.023943 | 0.01161 | 0.050688 | -0.024328 | 0.047188 | 0.16305 | 0.060196 | 0.033772 | 0.048227 | 0.05915 | 0.13136 | 0.037995 | 0.15779 | 0.2532 | 0.10565 | 0.017256 | 0.052809 | 0.091887 | 0.016871 | 0.088387 | 0.10498 | 0.14091 | 0.052845 | 0.088783
4970.6094 | 122.2778 | -0.068665 | 122.0215 | 0.10354 | -0.022205 | -0.025735 | -0.020438 | -0.009515 | 0.071848 | -0.026092 | 0.11201 | 0.21658 | 0.064455 | -0.023943 | 0.016188 | 0.055266 | -0.019749 | 0.047188 | 0.1722 | 0.04646 | 0.04293 | 0.048227 | 0.05915 | 0.14051 | 0.042573 | 0.15321 | 0.25778 | 0.10565 | 0.017256 | 0.057387 | 0.096465 | 0.02145 | 0.088387 | 0.09582 | 0.13176 | 0.048267 | 0.084204
4972.375 | 122.2961 | -0.073242 | 122.0032 | 0.098959 | -0.013048 | -0.034893 | -0.025017 | -0.014093 | 0.062691 | -0.03067 | 0.11201 | 0.212 | 0.055298 | -0.023943 | -0.025015 | 0.018642 | -0.038063 | 0.005985 | 0.1722 | 0.060194 | 0.038349 | 0.048225 | 0.059149 | 0.13593 | 0.042572 | 0.15321 | 0.2532 | 0.096497 | 0.017256 | 0.016184 | 0.059841 | 0.003136 | 0.047184 | 0.13702 | 0.15007 | 0.080313 | 0.093361
4974.1406 | 122.1313 | -0.11444 | 122.0215 | 0.10354 | -0.013048 | -0.030314 | -0.025017 | -0.009515 | 0.067269 | -0.026092 | 0.12116 | 0.212 | 0.059877 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.21798 | 0.10139 | 0.084127 | 0.089424 | 0.10493 | 0.18171 | 0.088349 | 0.16236 | 0.2532 | 0.10108 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.10498 | 0.14091 | 0.043689 | 0.079626
4975.9062 | 122.2549 | -0.064087 | 122.0032 | 0.10354 | -0.013048 | -0.030314 | -0.020438 | -0.009515 | 0.067269 | -0.03067 | 0.11659 | 0.212 | 0.059877 | -0.019364 | 0.007032 | 0.050688 | -0.024328 | 0.04261 | 0.16762 | 0.051039 | 0.033773 | 0.043649 | 0.054572 | 0.13136 | 0.033417 | 0.15779 | 0.2532 | 0.10108 | 0.021835 | 0.048231 | 0.091887 | 0.016871 | 0.083809 | 0.10955 | 0.14091 | 0.052845 | 0.084205
4977.6875 | 122.1771 | -0.091553 | 122.0444 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.014093 | 0.071848 | -0.016936 | 0.12574 | 0.212 | 0.055298 | -0.014785 | 0.01161 | 0.055266 | -0.028906 | 0.038032 | 0.19967 | 0.078505 | 0.065818 | 0.075693 | 0.07746 | 0.1634 | 0.074617 | 0.16694 | 0.2532 | 0.096497 | 0.026414 | 0.052809 | 0.096465 | 0.012293 | 0.079231 | 0.11413 | 0.15465 | 0.043688 | 0.084204
4979.4531 | 122.2504 | -0.068665 | 122.0078 | 0.10354 | -0.013048 | -0.030314 | -0.01586 | -0.009515 | 0.067269 | -0.026092 | 0.12116 | 0.20742 | 0.055298 | -0.023943 | 0.016188 | 0.050688 | -0.024328 | 0.04261 | 0.1722 | 0.055617 | 0.038351 | 0.052805 | 0.05915 | 0.13593 | 0.042573 | 0.16236 | 0.24862 | 0.096497 | 0.017256 | 0.057387 | 0.091887 | 0.016871 | 0.083809 | 0.10498 | 0.14549 | 0.03911 | 0.079626
4981.1562 | 122.1451 | -0.11444 | 122.0856 | 0.10354 | -0.008469 | -0.021157 | -0.020438 | -0.014093 | 0.067269 | -0.016936 | 0.12116 | 0.212 | 0.064455 | -0.019364 | 0.007032 | 0.050688 | -0.024328 | 0.04261 | 0.21798 | 0.10597 | 0.093284 | 0.094003 | 0.10035 | 0.18171 | 0.097505 | 0.16236 | 0.2532 | 0.10565 | 0.021835 | 0.048231 | 0.091887 | 0.016871 | 0.083809 | 0.11413 | 0.14549 | 0.057423 | 0.088783
4982.8594 | 122.2229 | -0.086975 | 122.0581 | 0.10354 | -0.017627 | -0.030314 | -0.020438 | -0.018671 | 0.067269 | -0.021514 | 0.12116 | 0.21658 | 0.059877 | -0.023943 | 0.016188 | 0.050688 | -0.028906 | 0.04261 | 0.19051 | 0.069348 | 0.056661 | 0.066537 | 0.068304 | 0.15424 | 0.065461 | 0.16236 | 0.25778 | 0.10108 | 0.017256 | 0.057387 | 0.091887 | 0.012293 | 0.083809 | 0.10498 | 0.15007 | 0.043689 | 0.088783
4984.625 | 122.1771 | -0.1236 | 122.0535 | 0.10354 | -0.00389 | -0.030314 | -0.020438 | -0.014093 | 0.062691 | -0.026092 | 0.12116 | 0.212 | 0.059877 | -0.019364 | 0.016188 | 0.055266 | -0.024328 | 0.033454 | 0.22713 | 0.11971 | 0.093282 | 0.10316 | 0.1095 | 0.18629 | 0.097504 | 0.16236 | 0.2532 | 0.10108 | 0.021835 | 0.057387 | 0.096465 | 0.016871 | 0.074653 | 0.10498 | 0.14549 | 0.043689 | 0.084205
4986.3125 | 122.287 | -0.068665 | 122.0444 | 0.11269 | -0.017627 | -0.030314 | -0.025017 | -0.009515 | 0.062691 | -0.021514 | 0.11659 | 0.21658 | 0.059877 | -0.019364 | 0.007032 | 0.055266 | -0.024328 | 0.04261 | 0.18136 | 0.051038 | 0.038351 | 0.043648 | 0.05915 | 0.13136 | 0.047151 | 0.15779 | 0.25778 | 0.10108 | 0.021835 | 0.048231 | 0.096465 | 0.016871 | 0.083809 | 0.10955 | 0.14091 | 0.052845 | 0.084205
4988.0938 | 122.1634 | -0.11444 | 122.1313 | 0.10812 | -0.013048 | -0.025735 | -0.025017 | -0.009515 | 0.067269 | -0.026092 | 0.11659 | 0.20742 | 0.059877 | -0.019364 | 0.007032 | 0.050688 | -0.028906 | 0.04261 | 0.22256 | 0.10139 | 0.088706 | 0.089424 | 0.10493 | 0.18171 | 0.088349 | 0.15779 | 0.24862 | 0.10108 | 0.021835 | 0.048231 | 0.091887 | 0.012293 | 0.083809 | 0.10955 | 0.14549 | 0.052845 | 0.088783
4989.8594 | 122.1725 | -0.10986 | 122.0856 | 0.10354 | -0.00389 | -0.025735 | -0.01586 | -0.000359 | 0.071848 | -0.026092 | 0.12116 | 0.212 | 0.059877 | -0.023943 | 0.01161 | 0.050688 | -0.015171 | 0.047188 | 0.2134 | 0.10597 | 0.084128 | 0.094003 | 0.1095 | 0.18171 | 0.083771 | 0.16236 | 0.2532 | 0.10108 | 0.017256 | 0.052809 | 0.091887 | 0.026028 | 0.088387 | 0.10955 | 0.13634 | 0.048267 | 0.075048
4991.5469 | 122.1954 | -0.10986 | 122.0901 | 0.10812 | -0.013048 | -0.034893 | -0.01586 | -0.000359 | 0.062691 | -0.021514 | 0.11659 | 0.22116 | 0.059877 | -0.019364 | 0.016188 | 0.050688 | -0.015171 | 0.04261 | 0.21798 | 0.096815 | 0.07497 | 0.094003 | 0.1095 | 0.17255 | 0.088349 | 0.15779 | 0.26236 | 0.10108 | 0.021835 | 0.057387 | 0.091887 | 0.026028 | 0.083809 | 0.1004 | 0.13176 | 0.043689 | 0.075048
4993.3125 | 122.3236 | -0.086975 | 122.0535 | 0.098959 | -0.013048 | -0.025735 | -0.020438 | -0.014093 | 0.062691 | -0.03067 | 0.12116 | 0.21658 | 0.064455 | -0.019364 | 0.007032 | 0.04611 | -0.019749 | 0.038032 | 0.18593 | 0.073927 | 0.06124 | 0.066537 | 0.072882 | 0.14967 | 0.056305 | 0.16236 | 0.25778 | 0.10565 | 0.021835 | 0.048231 | 0.087309 | 0.02145 | 0.079231 | 0.11413 | 0.14091 | 0.057423 | 0.084204
4995.0781 | 122.2687 | -0.073242 | 122.0398 | 0.10354 | -0.013048 | -0.034893 | -0.020438 | -0.009515 | 0.067269 | -0.026092 | 0.12116 | 0.212 | 0.059877 | -0.019364 | 0.01161 | 0.055266 | -0.028906 | 0.04261 | 0.17678 | 0.060194 | 0.038349 | 0.052804 | 0.063727 | 0.14051 | 0.04715 | 0.16236 | 0.2532 | 0.10108 | 0.021835 | 0.052809 | 0.096465 | 0.012293 | 0.083809 | 0.10955 | 0.15007 | 0.048267 | 0.088783
4996.8438 | 122.319 | -0.059509 | 122.049 | 0.10354 | -0.008469 | -0.021157 | -0.011281 | -0.004937 | 0.058113 | -0.026092 | 0.12574 | 0.21658 | 0.064455 | -0.023943 | 0.007032 | 0.055266 | -0.019749 | 0.04261 | 0.16305 | 0.05104 | 0.038352 | 0.048228 | 0.054572 | 0.11762 | 0.033417 | 0.16694 | 0.25778 | 0.10565 | 0.017256 | 0.048231 | 0.096465 | 0.02145 | 0.083809 | 0.11871 | 0.14549 | 0.057423 | 0.084204
4998.6094 | 122.168 | -0.12817 | 122.1039 | 0.10354 | -0.008469 | -0.030314 | -0.020438 | -0.014093 | 0.062691 | -0.026092 | 0.12116 | 0.22116 | 0.055298 | -0.023943 | 0.01161 | 0.050688 | -0.024328 | 0.04261 | 0.23171 | 0.11971 | 0.09786 | 0.10774 | 0.11408 | 0.19087 | 0.10208 | 0.16236 | 0.26236 | 0.096497 | 0.017256 | 0.052809 | 0.091887 | 0.016871 | 0.083809 | 0.10955 | 0.14549 | 0.043688 | 0.079626
5000.3125 | 122.2916 | -0.086975 | 122.0856 | 0.10354 | -0.013048 | -0.025735 | -0.025017 | -0.009515 | 0.067269 | -0.03067 | 0.11659 | 0.21658 | 0.055298 | -0.019364 | 0.01161 | 0.04611 | -0.024328 | 0.038032 | 0.19051 | 0.073927 | 0.06124 | 0.061958 | 0.07746 | 0.15424 | 0.056305 | 0.15779 | 0.25778 | 0.096497 | 0.021835 | 0.052809 | 0.087309 | 0.016871 | 0.079231 | 0.10498 | 0.14091 | 0.043688 | 0.079626
5002.0938 | 122.2549 | -0.091553 | 122.0764 | 0.10354 | -0.013048 | -0.030314 | -0.01586 | -0.004937 | 0.062691 | -0.021514 | 0.11659 | 0.212 | 0.05072 | -0.023943 | 0.01161 | 0.050688 | -0.024328 | 0.038032 | 0.19509 | 0.078505 | 0.061239 | 0.075693 | 0.086616 | 0.15424 | 0.070039 | 0.15779 | 0.2532 | 0.091919 | 0.017256 | 0.052809 | 0.091887 | 0.016871 | 0.079231 | 0.10498 | 0.14091 | 0.03911 | 0.075048
5003.8594 | 122.2412 | -0.10986 | 122.1085 | 0.10354 | -0.013048 | -0.021157 | -0.025017 | -0.000359 | 0.067269 | -0.026092 | 0.12116 | 0.20742 | 0.059877 | -0.023943 | 0.016188 | 0.050688 | -0.019749 | 0.038032 | 0.2134 | 0.096815 | 0.088706 | 0.084846 | 0.1095 | 0.17713 | 0.083771 | 0.16236 | 0.24862 | 0.10108 | 0.017256 | 0.057387 | 0.091887 | 0.02145 | 0.079231 | 0.10498 | 0.14091 | 0.043689 | 0.079626
5005.5625 | 122.1771 | -0.1236 | 122.113 | 0.10812 | -0.00389 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.026092 | 0.11201 | 0.20284 | 0.064455 | -0.023943 | 0.01161 | 0.050688 | -0.015171 | 0.047188 | 0.23171 | 0.11971 | 0.097861 | 0.10774 | 0.11408 | 0.19087 | 0.097504 | 0.15321 | 0.24404 | 0.10565 | 0.017256 | 0.052809 | 0.091887 | 0.026028 | 0.088387 | 0.1004 | 0.12718 | 0.052845 | 0.079626
5007.3438 | 122.3236 | -0.064087 | 122.0627 | 0.10354 | -0.008469 | -0.025735 | -0.01586 | -0.009515 | 0.058113 | -0.026092 | 0.11659 | 0.20742 | 0.059877 | -0.023943 | 0.01161 | 0.050688 | -0.019749 | 0.04261 | 0.16762 | 0.055618 | 0.038352 | 0.048227 | 0.054572 | 0.1222 | 0.037995 | 0.15779 | 0.24862 | 0.10108 | 0.017256 | 0.052809 | 0.091887 | 0.02145 | 0.083809 | 0.10498 | 0.13634 | 0.048267 | 0.079626
5009.0469 | 122.3236 | -0.07782 | 122.0673 | 0.10812 | -0.017627 | -0.030314 | -0.020438 | -0.018671 | 0.071848 | -0.026092 | 0.11201 | 0.20742 | 0.055298 | -0.023943 | 0.016188 | 0.055266 | -0.019749 | 0.038032 | 0.18594 | 0.060193 | 0.047506 | 0.057382 | 0.059149 | 0.14967 | 0.051728 | 0.15321 | 0.24862 | 0.096497 | 0.017256 | 0.057387 | 0.096465 | 0.02145 | 0.079231 | 0.09582 | 0.13176 | 0.03911 | 0.075047
5010.75 | 122.2137 | -0.10529 | 122.0718 | 0.10354 | -0.013048 | -0.030314 | -0.020438 | -0.009515 | 0.062691 | -0.03067 | 0.11201 | 0.20284 | 0.059877 | -0.019364 | 0.016188 | 0.04611 | -0.019749 | 0.051766 | 0.20882 | 0.092238 | 0.074972 | 0.084848 | 0.095771 | 0.16798 | 0.074616 | 0.15321 | 0.24404 | 0.10108 | 0.021835 | 0.057387 | 0.087309 | 0.02145 | 0.092965 | 0.09582 | 0.13176 | 0.043689 | 0.079626
5012.5312 | 122.1909 | -0.11444 | 122.0627 | 0.11269 | -0.013048 | -0.025735 | -0.020438 | -0.009515 | 0.076426 | -0.021514 | 0.11659 | 0.20742 | 0.055298 | -0.028522 | 0.007032 | 0.050688 | -0.024328 | 0.038032 | 0.22714 | 0.10139 | 0.088706 | 0.094003 | 0.10493 | 0.19087 | 0.092927 | 0.15779 | 0.24862 | 0.096497 | 0.012677 | 0.048231 | 0.091887 | 0.016871 | 0.079231 | 0.10955 | 0.14091 | 0.048266 | 0.079626
5014.2969 | 122.2137 | -0.10071 | 122.0993 | 0.10812 | -0.013048 | -0.030314 | -0.01586 | -0.009515 | 0.067269 | -0.021514 | 0.11659 | 0.212 | 0.055298 | -0.023943 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.20882 | 0.08766 | 0.070394 | 0.084848 | 0.091193 | 0.16798 | 0.079194 | 0.15779 | 0.2532 | 0.096497 | 0.017256 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.1004 | 0.13634 | 0.03911 | 0.075047
5016.0625 | 122.2687 | -0.073242 | 122.0581 | 0.10812 | -0.008469 | -0.025735 | -0.020438 | -0.009515 | 0.067269 | -0.021514 | 0.11659 | 0.20742 | 0.055298 | -0.023943 | 0.007032 | 0.050688 | -0.019749 | 0.04261 | 0.18136 | 0.064773 | 0.047507 | 0.052804 | 0.063727 | 0.14051 | 0.051728 | 0.15779 | 0.24862 | 0.096497 | 0.017256 | 0.048231 | 0.091887 | 0.02145 | 0.083809 | 0.10955 | 0.13634 | 0.048266 | 0.075047
5017.8281 | 122.3007 | -0.068665 | 122.0627 | 0.10354 | -0.013048 | -0.030314 | -0.020438 | -0.009515 | 0.062691 | -0.026092 | 0.11659 | 0.212 | 0.064455 | -0.019364 | 0.016188 | 0.055266 | -0.024328 | 0.038032 | 0.1722 | 0.055617 | 0.038351 | 0.048227 | 0.05915 | 0.13136 | 0.042573 | 0.15779 | 0.2532 | 0.10565 | 0.021835 | 0.057387 | 0.096465 | 0.016871 | 0.079231 | 0.1004 | 0.14091 | 0.048267 | 0.088783
5019.5938 | 122.2 | -0.1236 | 122.113 | 0.10354 | -0.008469 | -0.030314 | -0.025017 | -0.009515 | 0.067269 | -0.026092 | 0.10743 | 0.20742 | 0.05072 | -0.023943 | 0.016188 | 0.04611 | -0.024328 | 0.04261 | 0.22713 | 0.11513 | 0.093282 | 0.098579 | 0.11408 | 0.19087 | 0.097504 | 0.14863 | 0.24862 | 0.091919 | 0.017256 | 0.057387 | 0.087309 | 0.016871 | 0.083809 | 0.091242 | 0.13176 | 0.034532 | 0.075048
5021.2969 | 122.3236 | -0.082397 | 122.0947 | 0.10354 | -0.008469 | -0.030314 | -0.020438 | -0.009515 | 0.067269 | -0.026092 | 0.11201 | 0.20742 | 0.055298 | -0.023943 | 0.01161 | 0.050688 | -0.028906 | 0.04261 | 0.18593 | 0.073928 | 0.052083 | 0.061959 | 0.072882 | 0.14967 | 0.056305 | 0.15321 | 0.24862 | 0.096497 | 0.017256 | 0.052809 | 0.091887 | 0.012293 | 0.083809 | 0.1004 | 0.14091 | 0.043688 | 0.084204
5023.0625 | 122.3053 | -0.07782 | 122.0444 | 0.098959 | -0.013048 | -0.025735 | -0.011281 | -0.009515 | 0.062691 | -0.03067 | 0.10743 | 0.20742 | 0.059877 | -0.019364 | 0.020767 | 0.050688 | -0.024328 | 0.038032 | 0.17678 | 0.064772 | 0.052085 | 0.066539 | 0.068305 | 0.14051 | 0.04715 | 0.14863 | 0.24862 | 0.10108 | 0.021835 | 0.061966 | 0.091887 | 0.016871 | 0.079231 | 0.086663 | 0.13176 | 0.03911 | 0.084205
5024.8438 | 122.3053 | -0.068665 | 122.0764 | 0.10812 | -0.008469 | -0.030314 | -0.01586 | -0.009515 | 0.058113 | -0.026092 | 0.11201 | 0.19827 | 0.059877 | -0.023943 | 0.01161 | 0.04611 | -0.024328 | 0.047188 | 0.17678 | 0.060196 | 0.038351 | 0.052805 | 0.05915 | 0.12678 | 0.042573 | 0.15321 | 0.23946 | 0.10108 | 0.017256 | 0.052809 | 0.087309 | 0.016871 | 0.088387 | 0.1004 | 0.13634 | 0.048267 | 0.084205
5026.5469 | 122.3282 | -0.082397 | 122.0764 | 0.10354 | -0.017627 | -0.030314 | -0.025017 | -0.014093 | 0.067269 | -0.03067 | 0.12116 | 0.20284 | 0.059877 | -0.023943 | 0.016188 | 0.055266 | -0.010593 | 0.047188 | 0.18593 | 0.06477 | 0.052083 | 0.05738 | 0.068304 | 0.14967 | 0.051727 | 0.16236 | 0.24404 | 0.10108 | 0.017256 | 0.057387 | 0.096465 | 0.030606 | 0.088387 | 0.10498 | 0.13176 | 0.043689 | 0.07047
5028.3125 | 122.3282 | -0.073242 | 122.0856 | 0.094381 | -0.013048 | -0.030314 | -0.020438 | -0.014093 | 0.071848 | -0.021514 | 0.11659 | 0.19827 | 0.055298 | -0.014785 | 0.016188 | 0.055266 | -0.019749 | 0.04261 | 0.16762 | 0.060194 | 0.042928 | 0.052804 | 0.059149 | 0.14509 | 0.051728 | 0.15779 | 0.23946 | 0.096497 | 0.026414 | 0.057387 | 0.096465 | 0.02145 | 0.083809 | 0.1004 | 0.13634 | 0.03911 | 0.075047
5030.0781 | 122.2778 | -0.082397 | 122.0352 | 0.098959 | -0.017627 | -0.025735 | -0.01586 | -0.018671 | 0.062691 | -0.03067 | 0.11201 | 0.20742 | 0.064455 | -0.023943 | 0.01161 | 0.055266 | -0.024328 | 0.04261 | 0.18136 | 0.06477 | 0.056662 | 0.066537 | 0.063726 | 0.14509 | 0.051727 | 0.15321 | 0.24862 | 0.10565 | 0.017256 | 0.052809 | 0.096465 | 0.016871 | 0.083809 | 0.1004 | 0.13634 | 0.052845 | 0.088783
5031.7812 | 122.3328 | -0.082397 | 122.0764 | 0.098959 | -0.017627 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.026092 | 0.10743 | 0.20742 | 0.055298 | -0.019364 | 0.01161 | 0.04611 | -0.019749 | 0.047188 | 0.18136 | 0.06477 | 0.052083 | 0.061959 | 0.063726 | 0.14051 | 0.056305 | 0.14863 | 0.24862 | 0.096497 | 0.021835 | 0.052809 | 0.087309 | 0.02145 | 0.088387 | 0.09582 | 0.12718 | 0.043688 | 0.075047
5033.5469 | 122.3145 | -0.07782 | 122.0764 | 0.10354 | -0.00389 | -0.025735 | -0.025017 | -0.014093 | 0.062691 | -0.026092 | 0.11659 | 0.20284 | 0.055298 | -0.019364 | 0.007032 | 0.050688 | -0.019749 | 0.047188 | 0.18136 | 0.07393 | 0.052085 | 0.052803 | 0.063727 | 0.14051 | 0.051728 | 0.15779 | 0.24404 | 0.096497 | 0.021835 | 0.048231 | 0.091887 | 0.02145 | 0.088387 | 0.10955 | 0.13634 | 0.048266 | 0.075047
5035.2969 | 122.319 | -0.07782 | 122.0764 | 0.10812 | -0.017627 | -0.025735 | -0.020438 | -0.009515 | 0.058113 | -0.026092 | 0.11201 | 0.212 | 0.055298 | -0.023943 | 0.016188 | 0.04611 | -0.028906 | 0.04261 | 0.18594 | 0.060193 | 0.052085 | 0.057382 | 0.068305 | 0.13593 | 0.051728 | 0.15321 | 0.2532 | 0.096497 | 0.017256 | 0.057387 | 0.087309 | 0.012293 | 0.083809 | 0.09582 | 0.14091 | 0.03911 | 0.084204
5037.0781 | 122.3282 | -0.082397 | 122.0718 | 0.10812 | -0.013048 | -0.025735 | -0.025017 | -0.000359 | 0.067269 | -0.021514 | 0.11659 | 0.20284 | 0.055298 | -0.023943 | 0.01161 | 0.050688 | -0.015171 | 0.04261 | 0.19051 | 0.069349 | 0.056662 | 0.05738 | 0.082038 | 0.14967 | 0.060883 | 0.15779 | 0.24404 | 0.096497 | 0.017256 | 0.052809 | 0.091887 | 0.026028 | 0.083809 | 0.10498 | 0.13176 | 0.043688 | 0.070469
5038.7969 | 122.1909 | -0.1236 | 122.0901 | 0.10812 | -0.013048 | -0.025735 | -0.020438 | -0.009515 | 0.067269 | -0.03067 | 0.11659 | 0.20742 | 0.05072 | -0.019364 | 0.007032 | 0.055266 | -0.015171 | 0.038032 | 0.23171 | 0.11055 | 0.097861 | 0.10316 | 0.11408 | 0.19087 | 0.092926 | 0.15779 | 0.24862 | 0.091919 | 0.021835 | 0.048231 | 0.096465 | 0.026028 | 0.079231 | 0.10955 | 0.13176 | 0.043688 | 0.065891
5040.5625 | 122.3236 | -0.064087 | 122.081 | 0.10812 | -0.008469 | -0.025735 | -0.01586 | -0.014093 | 0.071848 | -0.026092 | 0.11659 | 0.20742 | 0.055298 | -0.019364 | 0.016188 | 0.050688 | -0.024328 | 0.038032 | 0.1722 | 0.055618 | 0.038352 | 0.048227 | 0.049994 | 0.13594 | 0.037995 | 0.15779 | 0.24862 | 0.096497 | 0.021835 | 0.057387 | 0.091887 | 0.016871 | 0.079231 | 0.1004 | 0.14091 | 0.03911 | 0.079626
5042.3281 | 122.2046 | -0.13275 | 122.1039 | 0.098959 | -0.008469 | -0.025735 | -0.01586 | -0.004937 | 0.058113 | -0.026092 | 0.11659 | 0.20742 | 0.064455 | -0.019364 | 0.01161 | 0.050688 | -0.019749 | 0.047188 | 0.23171 | 0.12428 | 0.10702 | 0.11689 | 0.12781 | 0.19086 | 0.10666 | 0.15779 | 0.24862 | 0.10565 | 0.021835 | 0.052809 | 0.091887 | 0.02145 | 0.088387 | 0.10498 | 0.13634 | 0.052845 | 0.084204
5044.1094 | 122.2778 | -0.054932 | 122.0901 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.035248 | 0.11659 | 0.212 | 0.055298 | -0.023943 | 0.01161 | 0.04611 | -0.024328 | 0.038032 | 0.16305 | 0.041884 | 0.029197 | 0.039072 | 0.045417 | 0.1222 | 0.019684 | 0.15779 | 0.2532 | 0.096497 | 0.017256 | 0.052809 | 0.087309 | 0.016871 | 0.079231 | 0.10498 | 0.14091 | 0.043688 | 0.079626
5045.8125 | 122.3145 | -0.059509 | 122.0581 | 0.10354 | -0.008469 | -0.025735 | -0.020438 | -0.009515 | 0.058113 | -0.026092 | 0.11201 | 0.20742 | 0.046142 | -0.023943 | 0.016188 | 0.050688 | -0.019749 | 0.047188 | 0.16305 | 0.05104 | 0.033774 | 0.039071 | 0.049994 | 0.11762 | 0.033417 | 0.15321 | 0.24862 | 0.087341 | 0.017256 | 0.057387 | 0.091887 | 0.02145 | 0.088387 | 0.09582 | 0.13176 | 0.029954 | 0.065891
5047.5781 | 122.2778 | -0.082397 | 122.0856 | 0.10812 | -0.013048 | -0.030314 | -0.025017 | -0.009515 | 0.067269 | -0.026092 | 0.10743 | 0.212 | 0.055298 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.19051 | 0.069349 | 0.052083 | 0.05738 | 0.072882 | 0.14967 | 0.056305 | 0.14863 | 0.2532 | 0.096497 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.091242 | 0.12718 | 0.03911 | 0.075047
5049.2812 | 122.2733 | -0.086975 | 122.0764 | 0.10354 | -0.00389 | -0.030314 | -0.020438 | -0.018671 | 0.058113 | -0.026092 | 0.11201 | 0.21658 | 0.059877 | -0.028522 | 0.01161 | 0.04611 | -0.024328 | 0.04261 | 0.19051 | 0.083085 | 0.056661 | 0.066537 | 0.068304 | 0.14509 | 0.060883 | 0.15321 | 0.25778 | 0.10108 | 0.012677 | 0.052809 | 0.087309 | 0.016871 | 0.083809 | 0.1004 | 0.13634 | 0.048267 | 0.084205
5051.0469 | 122.2229 | -0.1236 | 122.113 | 0.10354 | -0.008469 | -0.025735 | -0.020438 | -0.009515 | 0.067269 | -0.021514 | 0.11659 | 0.20284 | 0.059877 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.04261 | 0.22713 | 0.11513 | 0.097861 | 0.10316 | 0.11408 | 0.19087 | 0.10208 | 0.15779 | 0.24404 | 0.10108 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.083809 | 0.10498 | 0.13176 | 0.048267 | 0.075048
5052.8281 | 122.2412 | -0.11444 | 122.1085 | 0.10812 | -0.008469 | -0.030314 | -0.01586 | -0.014093 | 0.067269 | -0.026092 | 0.12116 | 0.212 | 0.055298 | -0.033101 | 0.016188 | 0.050688 | -0.028906 | 0.047188 | 0.22256 | 0.10597 | 0.084127 | 0.098581 | 0.10035 | 0.18171 | 0.088349 | 0.16236 | 0.2532 | 0.096497 | 0.008098 | 0.057387 | 0.091887 | 0.012293 | 0.088387 | 0.10498 | 0.15007 | 0.03911 | 0.084204
5054.6094 | 122.2458 | -0.11902 | 122.1085 | 0.10812 | -0.008469 | -0.025735 | -0.020438 | -0.009515 | 0.067269 | -0.03067 | 0.11659 | 0.212 | 0.059877 | -0.019364 | 0.01161 | 0.050688 | -0.024328 | 0.04261 | 0.22714 | 0.11055 | 0.093284 | 0.098581 | 0.1095 | 0.18629 | 0.088349 | 0.15779 | 0.2532 | 0.10108 | 0.021835 | 0.052809 | 0.091887 | 0.016871 | 0.083809 | 0.10498 | 0.14091 | 0.048267 | 0.084205
5056.3125 | 122.3007 | -0.054932 | 122.0581 | 0.10812 | -0.008469 | -0.025735 | -0.01586 | -0.014093 | 0.062691 | -0.016936 | 0.11201 | 0.20742 | 0.05072 | -0.014785 | 0.01161 | 0.055266 | -0.024328 | 0.04261 | 0.16305 | 0.046463 | 0.029197 | 0.039072 | 0.040839 | 0.11762 | 0.037996 | 0.15321 | 0.24862 | 0.091919 | 0.026414 | 0.052809 | 0.096465 | 0.016871 | 0.083809 | 0.1004 | 0.13634 | 0.03911 | 0.075048
5058.0781 | 122.2824 | -0.068665 | 122.0627 | 0.098959 | -0.013048 | -0.025735 | -0.011281 | -0.014093 | 0.062691 | -0.026092 | 0.11659 | 0.20284 | 0.059877 | -0.019364 | 0.016188 | 0.04611 | -0.019749 | 0.04261 | 0.16762 | 0.055617 | 0.04293 | 0.057384 | 0.054572 | 0.13136 | 0.042573 | 0.15779 | 0.24404 | 0.10108 | 0.021835 | 0.057387 | 0.087309 | 0.02145 | 0.083809 | 0.1004 | 0.13634 | 0.043689 | 0.079626
5059.8438 | 122.1863 | -0.1236 | 122.0947 | 0.10812 | -0.008469 | -0.021157 | -0.020438 | -0.004937 | 0.067269 | -0.026092 | 0.12116 | 0.20742 | 0.055298 | -0.023943 | 0.016188 | 0.04611 | -0.019749 | 0.04261 | 0.23171 | 0.11513 | 0.10244 | 0.10316 | 0.11866 | 0.19087 | 0.097504 | 0.16236 | 0.24862 | 0.096497 | 0.017256 | 0.057387 | 0.087309 | 0.02145 | 0.083809 | 0.10498 | 0.14091 | 0.03911 | 0.075047
5061.6094 | 122.3053 | -0.073242 | 122.0856 | 0.10354 | -0.013048 | -0.030314 | -0.01586 | -0.009515 | 0.062691 | -0.026092 | 0.11201 | 0.20742 | 0.055298 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.17678 | 0.060194 | 0.042928 | 0.057382 | 0.063727 | 0.13593 | 0.04715 | 0.15321 | 0.24862 | 0.096497 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.09582 | 0.13176 | 0.03911 | 0.075047
5063.375 | 122.3328 | -0.073242 | 122.0856 | 0.10812 | -0.00389 | -0.034893 | -0.01586 | -0.004937 | 0.067269 | -0.03067 | 0.10743 | 0.20742 | 0.055298 | -0.023943 | 0.016188 | 0.055266 | -0.024328 | 0.04261 | 0.18136 | 0.069352 | 0.038349 | 0.057382 | 0.068305 | 0.14051 | 0.042572 | 0.14863 | 0.24862 | 0.096497 | 0.017256 | 0.057387 | 0.096465 | 0.016871 | 0.083809 | 0.091242 | 0.13176 | 0.03911 | 0.079626
5065.0781 | 122.2229 | -0.1236 | 122.0947 | 0.10354 | -0.013048 | -0.025735 | -0.020438 | -0.014093 | 0.067269 | -0.026092 | 0.11659 | 0.212 | 0.05072 | -0.028522 | 0.007032 | 0.050688 | -0.024328 | 0.051766 | 0.22713 | 0.11055 | 0.097861 | 0.10316 | 0.1095 | 0.19087 | 0.097504 | 0.15779 | 0.2532 | 0.091919 | 0.012677 | 0.048231 | 0.091887 | 0.016871 | 0.092965 | 0.10955 | 0.14091 | 0.043688 | 0.075048
5066.8281 | 122.3099 | -0.054932 | 122.081 | 0.10812 | -0.008469 | -0.030314 | -0.020438 | -0.009515 | 0.071848 | -0.026092 | 0.10743 | 0.20284 | 0.055298 | -0.023943 | 0.020767 | 0.050688 | -0.015171 | 0.04261 | 0.16305 | 0.046463 | 0.024618 | 0.034494 | 0.045417 | 0.12678 | 0.02884 | 0.14863 | 0.24404 | 0.096497 | 0.017256 | 0.061966 | 0.091887 | 0.026028 | 0.083809 | 0.086663 | 0.1226 | 0.034531 | 0.070469
5068.6094 | 122.3145 | -0.068665 | 122.0993 | 0.10812 | -0.008469 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.012357 | 0.10743 | 0.20742 | 0.059877 | -0.023943 | 0.002454 | 0.050688 | -0.024328 | 0.04261 | 0.17678 | 0.060196 | 0.04293 | 0.052805 | 0.05915 | 0.13593 | 0.056308 | 0.14863 | 0.24862 | 0.10108 | 0.017256 | 0.043653 | 0.091887 | 0.016871 | 0.083809 | 0.10498 | 0.13176 | 0.057423 | 0.084205
5070.3125 | 122.3007 | -0.068665 | 122.081 | 0.10812 | -0.013048 | -0.025735 | -0.020438 | -0.009515 | 0.062691 | -0.016936 | 0.11201 | 0.20742 | 0.055298 | -0.019364 | 0.020767 | 0.059844 | -0.024328 | 0.04261 | 0.17678 | 0.055617 | 0.04293 | 0.048227 | 0.05915 | 0.13136 | 0.051729 | 0.15321 | 0.24862 | 0.096497 | 0.021835 | 0.061966 | 0.10104 | 0.016871 | 0.083809 | 0.091241 | 0.13634 | 0.034531 | 0.079626
5072.0938 | 122.2641 | -0.086975 | 122.113 | 0.10354 | -0.013048 | -0.030314 | -0.020438 | -0.018671 | 0.062691 | -0.021514 | 0.11201 | 0.20742 | 0.05072 | -0.023943 | 0.016188 | 0.04611 | -0.024328 | 0.038032 | 0.19051 | 0.073927 | 0.056661 | 0.066537 | 0.068304 | 0.14967 | 0.065461 | 0.15321 | 0.24862 | 0.091919 | 0.017256 | 0.057387 | 0.087309 | 0.016871 | 0.079231 | 0.09582 | 0.13634 | 0.034532 | 0.075048
5073.7969 | 122.2778 | -0.086975 | 122.0901 | 0.10354 | -0.008469 | -0.034893 | -0.020438 | -0.014093 | 0.067269 | -0.026092 | 0.10743 | 0.20284 | 0.046142 | -0.028522 | 0.01161 | 0.059844 | -0.024328 | 0.038032 | 0.19051 | 0.078506 | 0.052082 | 0.066537 | 0.072882 | 0.15424 | 0.060883 | 0.14863 | 0.24404 | 0.087341 | 0.012677 | 0.052809 | 0.10104 | 0.016871 | 0.079231 | 0.09582 | 0.13176 | 0.034532 | 0.07047
5075.5469 | 122.3099 | -0.082397 | 122.0581 | 0.10354 | -0.017627 | -0.025735 | -0.025017 | -0.009515 | 0.067269 | -0.03067 | 0.11201 | 0.20284 | 0.05072 | -0.023943 | 0.016188 | 0.055266 | -0.024328 | 0.051766 | 0.18593 | 0.06477 | 0.056662 | 0.05738 | 0.072882 | 0.14967 | 0.051727 | 0.15321 | 0.24404 | 0.091919 | 0.017256 | 0.057387 | 0.096465 | 0.016871 | 0.092965 | 0.09582 | 0.13634 | 0.034532 | 0.075048
5077.3125 | 122.2092 | -0.11902 | 122.1222 | 0.098959 | -0.013048 | -0.030314 | -0.01586 | -0.009515 | 0.067269 | -0.026092 | 0.11201 | 0.20284 | 0.05072 | -0.023943 | 0.01161 | 0.050688 | -0.024328 | 0.04261 | 0.21798 | 0.10597 | 0.088705 | 0.10316 | 0.1095 | 0.18629 | 0.092927 | 0.15321 | 0.24404 | 0.091919 | 0.017256 | 0.052809 | 0.091887 | 0.016871 | 0.083809 | 0.1004 | 0.13634 | 0.03911 | 0.075048
5079.0312 | 122.2046 | -0.10986 | 122.1313 | 0.10354 | -0.017627 | -0.030314 | -0.020438 | -0.009515 | 0.062691 | -0.026092 | 0.10743 | 0.212 | 0.05072 | -0.028522 | 0.01161 | 0.050688 | -0.019749 | 0.047188 | 0.2134 | 0.092236 | 0.079549 | 0.089425 | 0.10035 | 0.17255 | 0.083771 | 0.14863 | 0.2532 | 0.091919 | 0.012677 | 0.052809 | 0.091887 | 0.02145 | 0.088387 | 0.09582 | 0.12718 | 0.03911 | 0.070469
5080.7969 | 122.3236 | -0.064087 | 122.0627 | 0.10354 | -0.00389 | -0.030314 | -0.01586 | -0.014093 | 0.067269 | -0.026092 | 0.10743 | 0.20284 | 0.05072 | -0.023943 | 0.01161 | 0.04611 | -0.024328 | 0.038032 | 0.16762 | 0.060197 | 0.033773 | 0.048227 | 0.049994 | 0.13136 | 0.037995 | 0.14863 | 0.24404 | 0.091919 | 0.017256 | 0.052809 | 0.087309 | 0.016871 | 0.079231 | 0.09582 | 0.13176 | 0.03911 | 0.075048
5082.5625 | 122.2137 | -0.10986 | 122.0901 | 0.10354 | -0.013048 | -0.025735 | -0.020438 | -0.014093 | 0.067269 | -0.021514 | 0.10743 | 0.19827 | 0.05072 | -0.028522 | 0.016188 | 0.050688 | -0.019749 | 0.038032 | 0.2134 | 0.096815 | 0.084128 | 0.089425 | 0.09577 | 0.17713 | 0.088349 | 0.14863 | 0.23946 | 0.091919 | 0.012677 | 0.057387 | 0.091887 | 0.02145 | 0.079231 | 0.091242 | 0.12718 | 0.034532 | 0.070469
5084.3281 | 122.3328 | -0.082397 | 122.0581 | 0.098959 | -0.013048 | -0.025735 | -0.01586 | -0.004937 | 0.062691 | -0.026092 | 0.10743 | 0.20284 | 0.05072 | -0.019364 | 0.007032 | 0.04611 | -0.010593 | 0.038032 | 0.18136 | 0.069349 | 0.056662 | 0.066537 | 0.07746 | 0.14509 | 0.056305 | 0.14863 | 0.24404 | 0.091919 | 0.021835 | 0.048231 | 0.087309 | 0.030606 | 0.079231 | 0.1004 | 0.11802 | 0.043688 | 0.061313
5086.0312 | 122.1954 | -0.1236 | 122.0764 | 0.11269 | -0.00389 | -0.016578 | -0.020438 | -0.004937 | 0.067269 | -0.021514 | 0.11201 | 0.20742 | 0.059877 | -0.019364 | 0.01161 | 0.04611 | -0.019749 | 0.04261 | 0.23629 | 0.11971 | 0.10702 | 0.10316 | 0.11866 | 0.19087 | 0.10208 | 0.15321 | 0.24862 | 0.10108 | 0.021835 | 0.052809 | 0.087309 | 0.02145 | 0.083809 | 0.1004 | 0.13176 | 0.048267 | 0.079626
5087.7969 | 122.3099 | -0.086975 | 122.0947 | 0.10812 | -0.013048 | -0.030314 | -0.020438 | -0.014093 | 0.067269 | -0.026092 | 0.10743 | 0.20284 | 0.05072 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.047188 | 0.19509 | 0.073927 | 0.056661 | 0.066537 | 0.072882 | 0.15424 | 0.060883 | 0.14863 | 0.24404 | 0.091919 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.088387 | 0.09582 | 0.1226 | 0.03911 | 0.065891
5089.5781 | 122.3236 | -0.068665 | 122.0718 | 0.11269 | -0.013048 | -0.030314 | -0.01586 | -0.009515 | 0.062691 | -0.026092 | 0.10743 | 0.20284 | 0.059877 | -0.019364 | 0.01161 | 0.04611 | -0.019749 | 0.04261 | 0.18136 | 0.055617 | 0.038351 | 0.052805 | 0.05915 | 0.13136 | 0.042573 | 0.14863 | 0.24404 | 0.10108 | 0.021835 | 0.052809 | 0.087309 | 0.02145 | 0.083809 | 0.09582 | 0.12718 | 0.048267 | 0.079626
5091.3438 | 122.2595 | -0.10071 | 122.1176 | 0.098959 | -0.013048 | -0.030314 | -0.01586 | -0.009515 | 0.067269 | -0.026092 | 0.11201 | 0.19369 | 0.059877 | -0.028522 | 0.016188 | 0.050688 | -0.028906 | 0.04261 | 0.19967 | 0.08766 | 0.070394 | 0.084848 | 0.091193 | 0.16798 | 0.074616 | 0.15321 | 0.23489 | 0.10108 | 0.012677 | 0.057387 | 0.091887 | 0.012293 | 0.083809 | 0.09582 | 0.14091 | 0.043689 | 0.088783
5093.0469 | 122.2 | -0.10986 | 122.1268 | 0.10812 | -0.013048 | -0.025735 | -0.020438 | -0.014093 | 0.062691 | -0.03067 | 0.10743 | 0.19369 | 0.055298 | -0.023943 | 0.01161 | 0.055266 | -0.015171 | 0.04261 | 0.21798 | 0.096815 | 0.084128 | 0.089425 | 0.09577 | 0.17255 | 0.079193 | 0.14863 | 0.23489 | 0.096497 | 0.017256 | 0.052809 | 0.096465 | 0.026028 | 0.083809 | 0.09582 | 0.1226 | 0.043688 | 0.070469
5094.8281 | 122.2275 | -0.10529 | 122.113 | 0.10354 | -0.013048 | -0.030314 | -0.01586 | -0.000359 | 0.062691 | -0.026092 | 0.10285 | 0.20742 | 0.055298 | -0.023943 | 0.016188 | 0.041532 | -0.019749 | 0.038032 | 0.20882 | 0.092238 | 0.074972 | 0.089426 | 0.10493 | 0.16798 | 0.079194 | 0.14405 | 0.24862 | 0.096497 | 0.017256 | 0.057387 | 0.082731 | 0.02145 | 0.079231 | 0.086663 | 0.1226 | 0.03911 | 0.075047
5096.6094 | 122.2092 | -0.13275 | 122.1085 | 0.10812 | -0.008469 | -0.025735 | -0.01586 | -0.014093 | 0.062691 | -0.012357 | 0.10285 | 0.20284 | 0.059877 | -0.023943 | 0.007032 | 0.04611 | -0.019749 | 0.038032 | 0.24087 | 0.12428 | 0.10702 | 0.11689 | 0.11866 | 0.19544 | 0.12039 | 0.14405 | 0.24404 | 0.10108 | 0.017256 | 0.048231 | 0.087309 | 0.02145 | 0.079231 | 0.095819 | 0.1226 | 0.052845 | 0.079626
5098.375 | 122.3053 | -0.068665 | 122.0718 | 0.10812 | -0.017627 | -0.034893 | -0.025017 | -0.009515 | 0.062691 | -0.026092 | 0.10743 | 0.19827 | 0.05072 | -0.033101 | 0.007032 | 0.050688 | -0.028906 | 0.04261 | 0.17678 | 0.051038 | 0.033772 | 0.043648 | 0.05915 | 0.13136 | 0.042573 | 0.14863 | 0.23946 | 0.091919 | 0.008098 | 0.048231 | 0.091887 | 0.012293 | 0.083809 | 0.1004 | 0.13634 | 0.043688 | 0.079626
5100.0781 | 122.2778 | -0.091553 | 122.0856 | 0.10354 | -0.008469 | -0.021157 | -0.020438 | -0.009515 | 0.062691 | -0.026092 | 0.10743 | 0.20284 | 0.059877 | -0.028522 | 0.007032 | 0.059844 | -0.019749 | 0.038032 | 0.19509 | 0.083084 | 0.070396 | 0.071115 | 0.082038 | 0.15424 | 0.065461 | 0.14863 | 0.24404 | 0.10108 | 0.012677 | 0.048231 | 0.10104 | 0.02145 | 0.079231 | 0.1004 | 0.12718 | 0.052845 | 0.079626
5101.8438 | 122.2183 | -0.10529 | 122.1176 | 0.10812 | -0.013048 | -0.025735 | -0.011281 | -0.004937 | 0.067269 | -0.026092 | 0.10285 | 0.20284 | 0.055298 | -0.019364 | 0.01161 | 0.050688 | -0.024328 | 0.04261 | 0.2134 | 0.092238 | 0.079551 | 0.094005 | 0.10035 | 0.17256 | 0.079194 | 0.14405 | 0.24404 | 0.096497 | 0.021835 | 0.052809 | 0.091887 | 0.016871 | 0.083809 | 0.091241 | 0.12718 | 0.043688 | 0.079626
5103.625 | 122.2733 | -0.09613 | 122.0627 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.021514 | 0.10285 | 0.20284 | 0.05072 | -0.028522 | 0.020767 | 0.055266 | -0.024328 | 0.047188 | 0.20425 | 0.083082 | 0.070395 | 0.08027 | 0.086615 | 0.1634 | 0.074616 | 0.14405 | 0.24404 | 0.091919 | 0.012677 | 0.061966 | 0.096465 | 0.016871 | 0.088387 | 0.082084 | 0.12718 | 0.029953 | 0.075048
5105.3281 | 122.2366 | -0.10071 | 122.0856 | 0.10354 | -0.017627 | -0.021157 | -0.020438 | -0.014093 | 0.071848 | -0.026092 | 0.10285 | 0.20284 | 0.055298 | -0.028522 | 0.01161 | 0.050688 | -0.019749 | 0.04261 | 0.20425 | 0.083081 | 0.079551 | 0.08027 | 0.086615 | 0.17256 | 0.074616 | 0.14405 | 0.24404 | 0.096497 | 0.012677 | 0.052809 | 0.091887 | 0.02145 | 0.083809 | 0.091241 | 0.1226 | 0.043688 | 0.075047
5107.0938 | 122.1634 | -0.1236 | 122.113 | 0.10812 | -0.013048 | -0.021157 | -0.020438 | -0.009515 | 0.071848 | -0.026092 | 0.10743 | 0.20284 | 0.055298 | -0.019364 | 0.016188 | 0.050688 | -0.015171 | 0.033454 | 0.23171 | 0.11055 | 0.10244 | 0.10316 | 0.11408 | 0.19544 | 0.097504 | 0.14863 | 0.24404 | 0.096497 | 0.021835 | 0.057387 | 0.091887 | 0.026028 | 0.074653 | 0.091242 | 0.1226 | 0.03911 | 0.070469
5108.8594 | 122.2961 | -0.064087 | 122.0535 | 0.098959 | -0.008469 | -0.030314 | -0.011281 | -0.004937 | 0.062691 | -0.026092 | 0.10285 | 0.19827 | 0.055298 | -0.028522 | 0.016188 | 0.050688 | -0.019749 | 0.038032 | 0.16305 | 0.055618 | 0.033773 | 0.052806 | 0.05915 | 0.12678 | 0.037995 | 0.14405 | 0.23946 | 0.096497 | 0.012677 | 0.057387 | 0.091887 | 0.02145 | 0.079231 | 0.086663 | 0.1226 | 0.03911 | 0.075047
5110.6406 | 122.2687 | -0.086975 | 122.0581 | 0.10354 | -0.00389 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.021514 | 0.11201 | 0.20284 | 0.055298 | -0.023943 | 0.016188 | 0.050688 | -0.019749 | 0.038032 | 0.19051 | 0.083085 | 0.06124 | 0.071115 | 0.07746 | 0.15424 | 0.065461 | 0.15321 | 0.24404 | 0.096497 | 0.017256 | 0.057387 | 0.091887 | 0.02145 | 0.079231 | 0.09582 | 0.13176 | 0.03911 | 0.075047
5112.4062 | 122.2412 | -0.10071 | 122.081 | 0.11269 | -0.013048 | -0.025735 | -0.01586 | -0.009515 | 0.067269 | -0.026092 | 0.098273 | 0.19369 | 0.055298 | -0.019364 | 0.016188 | 0.04611 | -0.019749 | 0.038032 | 0.2134 | 0.08766 | 0.074973 | 0.084848 | 0.091193 | 0.16798 | 0.074616 | 0.13947 | 0.23489 | 0.096497 | 0.021835 | 0.057387 | 0.087309 | 0.02145 | 0.079231 | 0.082085 | 0.11802 | 0.03911 | 0.075047
5114.1094 | 122.2687 | -0.086975 | 122.0673 | 0.10812 | -0.008469 | -0.034893 | -0.011281 | -0.014093 | 0.067269 | -0.03067 | 0.10285 | 0.20284 | 0.055298 | -0.019364 | 0.016188 | 0.059844 | -0.019749 | 0.04261 | 0.19509 | 0.078506 | 0.052082 | 0.075694 | 0.072882 | 0.15424 | 0.056305 | 0.14405 | 0.24404 | 0.096497 | 0.021835 | 0.057387 | 0.10104 | 0.02145 | 0.083809 | 0.086663 | 0.1226 | 0.03911 | 0.075047
5115.875 | 122.2046 | -0.11444 | 122.0947 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.004937 | 0.071848 | -0.021514 | 0.10743 | 0.19827 | 0.05072 | -0.019364 | 0.007032 | 0.041532 | -0.019749 | 0.047188 | 0.22256 | 0.10139 | 0.088706 | 0.098581 | 0.1095 | 0.18629 | 0.092927 | 0.14863 | 0.23946 | 0.091919 | 0.021835 | 0.048231 | 0.082731 | 0.02145 | 0.088387 | 0.1004 | 0.12718 | 0.043688 | 0.070469
5117.6406 | 122.2046 | -0.11902 | 122.1039 | 0.10354 | -0.00389 | -0.025735 | -0.020438 | -0.009515 | 0.058113 | -0.016936 | 0.10285 | 0.18911 | 0.055298 | -0.019364 | 0.016188 | 0.050688 | -0.019749 | 0.04261 | 0.22256 | 0.11513 | 0.093284 | 0.098581 | 0.1095 | 0.17713 | 0.10208 | 0.14405 | 0.23031 | 0.096497 | 0.021835 | 0.057387 | 0.091887 | 0.02145 | 0.083809 | 0.086663 | 0.1226 | 0.03911 | 0.075047
5119.3594 | 122.3053 | -0.073242 | 122.0627 | 0.10354 | -0.013048 | -0.021157 | -0.020438 | -0.009515 | 0.071848 | -0.016936 | 0.10285 | 0.20284 | 0.055298 | -0.023943 | 0.016188 | 0.041532 | -0.019749 | 0.038032 | 0.17678 | 0.060194 | 0.052085 | 0.052804 | 0.063727 | 0.14509 | 0.056306 | 0.14405 | 0.24404 | 0.096497 | 0.017256 | 0.057387 | 0.082731 | 0.02145 | 0.079231 | 0.086663 | 0.1226 | 0.03911 | 0.075047
5121.125 | 122.2733 | -0.091553 | 122.0581 | 0.098959 | -0.017627 | -0.030314 | -0.01586 | -0.004937 | 0.071848 | -0.016936 | 0.10285 | 0.20742 | 0.055298 | -0.023943 | 0.01161 | 0.050688 | -0.019749 | 0.047188 | 0.19051 | 0.073926 | 0.061239 | 0.075693 | 0.086616 | 0.1634 | 0.074617 | 0.14405 | 0.24862 | 0.096497 | 0.017256 | 0.052809 | 0.091887 | 0.02145 | 0.088387 | 0.091241 | 0.1226 | 0.043688 | 0.075047
5122.8281 | 122.3145 | -0.082397 | 122.0444 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.004937 | 0.062691 | -0.016936 | 0.10285 | 0.19827 | 0.064455 | -0.028522 | 0.01161 | 0.055266 | -0.019749 | 0.038032 | 0.19051 | 0.069349 | 0.056662 | 0.066537 | 0.07746 | 0.14509 | 0.065461 | 0.14405 | 0.23946 | 0.10565 | 0.012677 | 0.052809 | 0.096465 | 0.02145 | 0.079231 | 0.091241 | 0.1226 | 0.052845 | 0.084204
5124.5938 | 122.2092 | -0.11902 | 122.0856 | 0.10354 | -0.013048 | -0.030314 | -0.011281 | -0.004937 | 0.062691 | -0.021514 | 0.10285 | 0.19369 | 0.055298 | -0.023943 | 0.002454 | 0.050688 | -0.019749 | 0.04261 | 0.22256 | 0.10597 | 0.088705 | 0.10774 | 0.11408 | 0.18171 | 0.097505 | 0.14405 | 0.23489 | 0.096497 | 0.017256 | 0.043653 | 0.091887 | 0.02145 | 0.083809 | 0.1004 | 0.1226 | 0.052844 | 0.075047
5126.3594 | 122.1725 | -0.12817 | 122.1176 | 0.098959 | -0.008469 | -0.021157 | -0.01586 | -0.009515 | 0.067269 | -0.016936 | 0.093694 | 0.19827 | 0.05072 | -0.023943 | 0.016188 | 0.050688 | -0.019749 | 0.038032 | 0.22713 | 0.11971 | 0.10702 | 0.11231 | 0.11866 | 0.19544 | 0.11124 | 0.13489 | 0.23946 | 0.091919 | 0.017256 | 0.057387 | 0.091887 | 0.02145 | 0.079231 | 0.077506 | 0.11344 | 0.034532 | 0.070469
5128.0625 | 122.2916 | -0.068665 | 122.0673 | 0.11269 | -0.00389 | -0.021157 | -0.025017 | -0.004937 | 0.067269 | -0.021514 | 0.098273 | 0.20284 | 0.05072 | -0.028522 | 0.002454 | 0.04611 | -0.019749 | 0.038032 | 0.18136 | 0.064775 | 0.047508 | 0.043648 | 0.063728 | 0.13593 | 0.047151 | 0.13947 | 0.24404 | 0.091919 | 0.012677 | 0.043653 | 0.087309 | 0.02145 | 0.079231 | 0.095819 | 0.11802 | 0.048266 | 0.070469
5129.7812 | 122.168 | -0.11444 | 122.0856 | 0.11269 | -0.008469 | -0.021157 | -0.011281 | -0.004937 | 0.058113 | -0.026092 | 0.098273 | 0.19827 | 0.046142 | -0.019364 | 0.01161 | 0.050688 | -0.024328 | 0.038032 | 0.22714 | 0.10597 | 0.093284 | 0.10316 | 0.1095 | 0.17255 | 0.088349 | 0.13947 | 0.23946 | 0.087341 | 0.021835 | 0.052809 | 0.091887 | 0.016871 | 0.079231 | 0.086663 | 0.1226 | 0.034532 | 0.07047
5131.5469 | 122.1817 | -0.10986 | 122.0901 | 0.098959 | -0.013048 | -0.016578 | -0.01586 | -0.004937 | 0.071848 | -0.021514 | 0.10743 | 0.19827 | 0.055298 | -0.028522 | 0.002454 | 0.050688 | -0.028906 | 0.047188 | 0.20882 | 0.096815 | 0.093285 | 0.094003 | 0.10493 | 0.18171 | 0.088349 | 0.14863 | 0.23946 | 0.096497 | 0.012677 | 0.043653 | 0.091887 | 0.012293 | 0.088387 | 0.10498 | 0.13634 | 0.052844 | 0.084204
5133.3281 | 122.1863 | -0.1236 | 122.113 | 0.10812 | -0.013048 | -0.025735 | -0.011281 | -0.009515 | 0.071848 | -0.021514 | 0.098273 | 0.19369 | 0.05072 | -0.028522 | 0.020767 | 0.04611 | -0.028906 | 0.047188 | 0.23171 | 0.11055 | 0.097861 | 0.11231 | 0.11408 | 0.19544 | 0.10208 | 0.13947 | 0.23489 | 0.091919 | 0.012677 | 0.061966 | 0.087309 | 0.012293 | 0.088387 | 0.077506 | 0.12718 | 0.029953 | 0.079626
5135.1094 | 122.3053 | -0.082397 | 122.081 | 0.10812 | -0.008469 | -0.025735 | -0.011281 | -0.009515 | 0.071848 | -0.016936 | 0.098273 | 0.19827 | 0.055298 | -0.028522 | 0.016188 | 0.050688 | -0.024328 | 0.038032 | 0.19051 | 0.073928 | 0.056662 | 0.071116 | 0.072882 | 0.15424 | 0.065461 | 0.13947 | 0.23946 | 0.096497 | 0.012677 | 0.057387 | 0.091887 | 0.016871 | 0.079231 | 0.082085 | 0.1226 | 0.03911 | 0.079626
5136.8281 | 122.287 | -0.064087 | 122.0627 | 0.10812 | -0.008469 | -0.025735 | -0.006703 | -0.014093 | 0.076426 | -0.016936 | 0.098273 | 0.19827 | 0.05072 | -0.033101 | 0.016188 | 0.04611 | -0.024328 | 0.033454 | 0.1722 | 0.055618 | 0.038352 | 0.057384 | 0.049994 | 0.14051 | 0.047151 | 0.13947 | 0.23946 | 0.091919 | 0.008098 | 0.057387 | 0.087309 | 0.016871 | 0.074653 | 0.082085 | 0.1226 | 0.034532 | 0.075048
5138.5938 | 122.3007 | -0.050354 | 122.0627 | 0.10354 | -0.00389 | -0.025735 | -0.01586 | -0.009515 | 0.071848 | -0.021514 | 0.098273 | 0.19369 | 0.05072 | -0.023943 | 0.01161 | 0.041532 | -0.015171 | 0.038032 | 0.15389 | 0.046464 | 0.024619 | 0.034494 | 0.040839 | 0.1222 | 0.02884 | 0.13947 | 0.23489 | 0.091919 | 0.017256 | 0.052809 | 0.082731 | 0.026028 | 0.079231 | 0.086663 | 0.11344 | 0.03911 | 0.065891
5140.3594 | 122.2824 | -0.086975 | 122.0581 | 0.11269 | -0.008469 | -0.025735 | -0.01586 | -0.004937 | 0.067269 | -0.021514 | 0.11201 | 0.19369 | 0.041563 | -0.028522 | 0.01161 | 0.050688 | -0.024328 | 0.038032 | 0.19967 | 0.078506 | 0.06124 | 0.071115 | 0.082038 | 0.15424 | 0.065461 | 0.15321 | 0.23489 | 0.082762 | 0.012677 | 0.052809 | 0.091887 | 0.016871 | 0.079231 | 0.1004 | 0.13634 | 0.029953 | 0.065891
5142.0625 | 122.2824 | -0.073242 | 122.0673 | 0.10812 | -0.008469 | -0.030314 | -0.006703 | -0.004937 | 0.067269 | -0.016936 | 0.093694 | 0.19827 | 0.055298 | -0.023943 | 0.01161 | 0.050688 | -0.019749 | 0.038032 | 0.18136 | 0.064773 | 0.042928 | 0.066539 | 0.068305 | 0.14051 | 0.056306 | 0.13489 | 0.23946 | 0.096497 | 0.017256 | 0.052809 | 0.091887 | 0.02145 | 0.079231 | 0.082084 | 0.11344 | 0.043688 | 0.075047
5143.8281 | 122.168 | -0.11444 | 122.1039 | 0.10812 | 0.000689 | -0.021157 | -0.006703 | -0.004937 | 0.071848 | -0.016936 | 0.098273 | 0.20284 | 0.055298 | -0.019364 | 0.007032 | 0.050688 | -0.028906 | 0.047188 | 0.22256 | 0.11513 | 0.093284 | 0.10774 | 0.1095 | 0.18629 | 0.097505 | 0.13947 | 0.24404 | 0.096497 | 0.021835 | 0.048231 | 0.091887 | 0.012293 | 0.088387 | 0.091241 | 0.12718 | 0.048266 | 0.084204
5145.6094 | 122.2092 | -0.12817 | 122.1268 | 0.10812 | -0.00389 | -0.025735 | -0.020438 | -0.000359 | 0.076426 | -0.016936 | 0.098273 | 0.19827 | 0.05072 | -0.019364 | 0.007032 | 0.050688 | -0.019749 | 0.038032 | 0.23629 | 0.12428 | 0.10244 | 0.10774 | 0.12782 | 0.2046 | 0.11124 | 0.13947 | 0.23946 | 0.091919 | 0.021835 | 0.048231 | 0.091887 | 0.02145 | 0.079231 | 0.091241 | 0.11802 | 0.043688 | 0.070469
5147.3281 | 122.2733 | -0.091553 | 122.0718 | 0.10812 | 0.000689 | -0.025735 | -0.020438 | -0.009515 | 0.062691 | -0.026092 | 0.10285 | 0.18911 | 0.055298 | -0.014785 | 0.01161 | 0.050688 | -0.019749 | 0.033454 | 0.19967 | 0.092242 | 0.065818 | 0.071115 | 0.082038 | 0.15424 | 0.065461 | 0.14405 | 0.23031 | 0.096497 | 0.026414 | 0.052809 | 0.091887 | 0.02145 | 0.074653 | 0.091241 | 0.1226 | 0.043688 | 0.075047
5149.0938 | 122.2458 | -0.082397 | 122.0764 | 0.10812 | -0.013048 | -0.025735 | -0.01586 | -0.000359 | 0.062691 | -0.03067 | 0.10743 | 0.212 | 0.046142 | -0.023943 | 0.016188 | 0.050688 | -0.024328 | 0.04261 | 0.19051 | 0.069349 | 0.056662 | 0.066537 | 0.082038 | 0.14509 | 0.051727 | 0.14863 | 0.2532 | 0.087341 | 0.017256 | 0.057387 | 0.091887 | 0.016871 | 0.083809 | 0.091242 | 0.13176 | 0.029954 | 0.07047
5150.8594 | 122.2183 | -0.10529 | 122.1039 | 0.10354 | -0.00389 | -0.021157 | -0.020438 | -0.009515 | 0.071848 | -0.021514 | 0.10285 | 0.19827 | 0.064455 | -0.014785 | 0.002454 | 0.04611 | -0.024328 | 0.047188 | 0.20882 | 0.1014 | 0.084129 | 0.084848 | 0.095771 | 0.17713 | 0.083772 | 0.14405 | 0.23946 | 0.10565 | 0.026414 | 0.043653 | 0.087309 | 0.016871 | 0.088387 | 0.1004 | 0.12718 | 0.062001 | 0.088783
5152.6406 | 122.2504 | -0.086975 | 122.0627 | 0.10812 | -0.008469 | -0.025735 | -0.011281 | -0.000359 | 0.062691 | -0.021514 | 0.10285 | 0.20284 | 0.055298 | -0.023943 | 0.01161 | 0.055266 | -0.019749 | 0.033454 | 0.19509 | 0.078506 | 0.06124 | 0.075694 | 0.086616 | 0.14967 | 0.065461 | 0.14405 | 0.24404 | 0.096497 | 0.017256 | 0.052809 | 0.096465 | 0.02145 | 0.074653 | 0.091241 | 0.1226 | 0.043688 | 0.075047
5154.4219 | 122.3053 | -0.07782 | 122.0581 | 0.10354 | -0.013048 | -0.025735 | -0.011281 | -0.000359 | 0.067269 | -0.021514 | 0.10285 | 0.19369 | 0.055298 | -0.023943 | 0.016188 | 0.04611 | -0.019749 | 0.038032 | 0.18136 | 0.064772 | 0.052085 | 0.066539 | 0.077461 | 0.14509 | 0.056306 | 0.14405 | 0.23489 | 0.096497 | 0.017256 | 0.057387 | 0.087309 | 0.02145 | 0.079231 | 0.086663 | 0.1226 | 0.03911 | 0.075047
5156.125 | 122.2641 | -0.073242 | 122.0673 | 0.10812 | -0.013048 | -0.025735 | -0.011281 | -0.004937 | 0.071848 | -0.016936 | 0.11201 | 0.20284 | 0.05072 | -0.028522 | 0.01161 | 0.055266 | -0.019749 | 0.038032 | 0.18136 | 0.060194 | 0.047507 | 0.061961 | 0.068305 | 0.14509 | 0.056306 | 0.15321 | 0.24404 | 0.091919 | 0.012677 | 0.052809 | 0.096465 | 0.02145 | 0.079231 | 0.1004 | 0.13176 | 0.03911 | 0.070469
5157.8906 | 122.1588 | -0.12817 | 122.1085 | 0.10812 | -0.013048 | -0.034893 | -0.01586 | 0.004219 | 0.071848 | -0.021514 | 0.10743 | 0.19369 | 0.059877 | -0.014785 | 0.01161 | 0.041532 | -0.015171 | 0.04261 | 0.23629 | 0.11513 | 0.093281 | 0.11231 | 0.13239 | 0.20002 | 0.10666 | 0.14863 | 0.23489 | 0.10108 | 0.026414 | 0.052809 | 0.082731 | 0.026028 | 0.083809 | 0.09582 | 0.1226 | 0.048267 | 0.075048
5159.6562 | 122.2824 | -0.064087 | 122.0398 | 0.10812 | -0.008469 | -0.021157 | -0.011281 | -0.000359 | 0.067269 | -0.016936 | 0.098273 | 0.20742 | 0.055298 | -0.023943 | 0.016188 | 0.041532 | -0.024328 | 0.04261 | 0.1722 | 0.055618 | 0.04293 | 0.052806 | 0.063728 | 0.13136 | 0.047151 | 0.13947 | 0.24862 | 0.096497 | 0.017256 | 0.057387 | 0.082731 | 0.016871 | 0.083809 | 0.082085 | 0.1226 | 0.03911 | 0.079626
5161.4219 | 122.3053 | -0.054932 | 122.0398 | 0.10812 | -0.013048 | -0.025735 | -0.020438 | -0.000359 | 0.071848 | -0.012357 | 0.10743 | 0.20284 | 0.055298 | -0.023943 | 0.016188 | 0.04611 | -0.024328 | 0.04261 | 0.16305 | 0.041884 | 0.029197 | 0.034494 | 0.054573 | 0.12678 | 0.042575 | 0.14863 | 0.24404 | 0.096497 | 0.017256 | 0.057387 | 0.087309 | 0.016871 | 0.083809 | 0.091242 | 0.13176 | 0.03911 | 0.079626
5163.125 | 122.2366 | -0.086975 | 122.0627 | 0.11269 | -0.00389 | -0.025735 | -0.006703 | 0.004219 | 0.062691 | -0.021514 | 0.098273 | 0.19369 | 0.055298 | -0.023943 | 0.016188 | 0.04611 | -0.024328 | 0.038032 | 0.19967 | 0.083085 | 0.06124 | 0.080272 | 0.091194 | 0.14967 | 0.065461 | 0.13947 | 0.23489 | 0.096497 | 0.017256 | 0.057387 | 0.087309 | 0.016871 | 0.079231 | 0.082085 | 0.1226 | 0.03911 | 0.079626
5164.8906 | 122.2595 | -0.064087 | 122.0535 | 0.11269 | -0.008469 | -0.025735 | -0.006703 | -0.000359 | 0.076426 | -0.012357 | 0.098273 | 0.20284 | 0.055298 | -0.019364 | 0.016188 | 0.055266 | -0.028906 | 0.04261 | 0.17678 | 0.055618 | 0.038352 | 0.057384 | 0.063728 | 0.14051 | 0.05173 | 0.13947 | 0.24404 | 0.096497 | 0.021835 | 0.057387 | 0.096465 | 0.012293 | 0.083809 | 0.082085 | 0.12718 | 0.03911 | 0.084204
5166.6562 | 122.3007 | -0.073242 | 122.0535 | 0.10812 | -0.00389 | -0.025735 | -0.011281 | -0.004937 | 0.076426 | -0.021514 | 0.10743 | 0.19827 | 0.059877 | -0.028522 | 0.007032 | 0.055266 | -0.019749 | 0.038032 | 0.18136 | 0.069352 | 0.047507 | 0.061961 | 0.068305 | 0.14967 | 0.051728 | 0.14863 | 0.23946 | 0.10108 | 0.012677 | 0.048231 | 0.096465 | 0.02145 | 0.079231 | 0.1004 | 0.12718 | 0.052845 | 0.079626
5168.4219 | 122.2961 | -0.07782 | 122.0444 | 0.10812 | -0.008469 | -0.016578 | -0.011281 | -0.000359 | 0.067269 | -0.026092 | 0.10743 | 0.19827 | 0.055298 | -0.023943 | 0.01161 | 0.050688 | -0.028906 | 0.047188 | 0.18594 | 0.069351 | 0.061242 | 0.066539 | 0.077461 | 0.14509 | 0.051728 | 0.14863 | 0.23946 | 0.096497 | 0.017256 | 0.052809 | 0.091887 | 0.012293 | 0.088387 | 0.09582 | 0.13634 | 0.043688 | 0.084204
5170.1406 | 122.1863 | -0.10986 | 122.0718 | 0.10812 | -0.00389 | -0.016578 | -0.020438 | -0.004937 | 0.076426 | -0.016936 | 0.10285 | 0.20284 | 0.059877 | -0.028522 | 0.016188 | 0.059844 | -0.019749 | 0.04261 | 0.21798 | 0.10597 | 0.093285 | 0.089425 | 0.10493 | 0.18629 | 0.092927 | 0.14405 | 0.24404 | 0.10108 | 0.012677 | 0.057387 | 0.10104 | 0.02145 | 0.083809 | 0.086663 | 0.1226 | 0.043689 | 0.079626
5171.9219 | 122.2687 | -0.064087 | 122.0627 | 0.11727 | -0.008469 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.003201 | 0.10743 | 0.19827 | 0.059877 | -0.028522 | 0.002454 | 0.04611 | -0.028906 | 0.038032 | 0.18136 | 0.055618 | 0.04293 | 0.057384 | 0.072884 | 0.14509 | 0.060886 | 0.14863 | 0.23946 | 0.10108 | 0.012677 | 0.043653 | 0.087309 | 0.012293 | 0.079231 | 0.10498 | 0.13634 | 0.057423 | 0.088783
5173.6875 | 122.2504 | -0.059509 | 122.0535 | 0.11269 | 0.000689 | -0.012 | -0.011281 | 0.004219 | 0.076426 | -0.007779 | 0.10743 | 0.20742 | 0.059877 | -0.019364 | 0.002454 | 0.041532 | -0.028906 | 0.038032 | 0.1722 | 0.060198 | 0.047509 | 0.048228 | 0.063728 | 0.13594 | 0.05173 | 0.14863 | 0.24862 | 0.10108 | 0.021835 | 0.043653 | 0.082731 | 0.012293 | 0.079231 | 0.10498 | 0.13634 | 0.057423 | 0.088783
5175.4531 | 122.1451 | -0.10529 | 122.081 | 0.11269 | 0.005267 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.016936 | 0.10743 | 0.20742 | 0.064455 | -0.014785 | 0.007032 | 0.04611 | -0.028906 | 0.033454 | 0.21798 | 0.11055 | 0.088708 | 0.10316 | 0.10493 | 0.18171 | 0.08835 | 0.14863 | 0.24862 | 0.10565 | 0.026414 | 0.048231 | 0.087309 | 0.012293 | 0.074653 | 0.1004 | 0.13634 | 0.057423 | 0.093361
5177.1562 | 122.2275 | -0.07782 | 122.0627 | 0.11269 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.016936 | 0.11201 | 0.20284 | 0.05072 | -0.014785 | 0.007032 | 0.036954 | -0.028906 | 0.028875 | 0.19051 | 0.07393 | 0.06582 | 0.075696 | 0.082039 | 0.15425 | 0.060884 | 0.15321 | 0.24404 | 0.091919 | 0.026414 | 0.048231 | 0.078153 | 0.012293 | 0.070074 | 0.10498 | 0.14091 | 0.043688 | 0.079626
5178.9219 | 122.1817 | -0.09613 | 122.0535 | 0.12185 | -0.00389 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.016936 | 0.11201 | 0.20742 | 0.064455 | -0.028522 | 0.01161 | 0.036954 | -0.024328 | 0.033454 | 0.21798 | 0.09224 | 0.079552 | 0.098584 | 0.10035 | 0.17713 | 0.079194 | 0.15321 | 0.24862 | 0.10565 | 0.012677 | 0.052809 | 0.078153 | 0.016871 | 0.074653 | 0.1004 | 0.13634 | 0.052845 | 0.088783
5180.7031 | 122.2458 | -0.064087 | 122.0581 | 0.11727 | 0.000689 | -0.012 | -0.002124 | -0.000359 | 0.071848 | -0.012357 | 0.11201 | 0.212 | 0.059877 | -0.019364 | 0.01161 | 0.04611 | -0.024328 | 0.028875 | 0.18136 | 0.064776 | 0.052087 | 0.061963 | 0.063728 | 0.13594 | 0.05173 | 0.15321 | 0.2532 | 0.10108 | 0.021835 | 0.052809 | 0.087309 | 0.016871 | 0.070074 | 0.1004 | 0.13634 | 0.048267 | 0.084205
5182.4219 | 122.2961 | -0.064087 | 122.0261 | 0.11269 | 0.000689 | -0.012 | -0.006703 | -0.000359 | 0.071848 | -0.012357 | 0.11201 | 0.212 | 0.059877 | -0.010206 | 0.002454 | 0.036954 | -0.028906 | 0.028875 | 0.17678 | 0.064776 | 0.052087 | 0.057384 | 0.063728 | 0.13594 | 0.05173 | 0.15321 | 0.2532 | 0.10108 | 0.030993 | 0.043653 | 0.078153 | 0.012293 | 0.070074 | 0.10955 | 0.14091 | 0.057423 | 0.088783
5184.1875 | 122.1725 | -0.09613 | 122.0627 | 0.12185 | 0.005267 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.012357 | 0.11659 | 0.20742 | 0.059877 | -0.023943 | 0.002454 | 0.036954 | -0.028906 | 0.033454 | 0.21798 | 0.1014 | 0.088709 | 0.094006 | 0.10035 | 0.18171 | 0.083773 | 0.15779 | 0.24862 | 0.10108 | 0.017256 | 0.043653 | 0.078153 | 0.012293 | 0.074653 | 0.11413 | 0.14549 | 0.057423 | 0.088783
5185.9531 | 122.1451 | -0.13733 | 122.0444 | 0.11727 | 0.005267 | -0.007421 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 0.11201 | 0.212 | 0.059877 | -0.019364 | -0.002124 | 0.04611 | -0.033484 | 0.033454 | 0.2546 | 0.1426 | 0.12991 | 0.13063 | 0.14155 | 0.21833 | 0.12497 | 0.15321 | 0.2532 | 0.10108 | 0.021835 | 0.039075 | 0.087309 | 0.007715 | 0.074653 | 0.11413 | 0.14549 | 0.062001 | 0.093361
5187.7188 | 122.1542 | -0.09613 | 122.0306 | 0.11727 | 0.000689 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.012357 | 0.11659 | 0.21658 | 0.059877 | -0.014785 | 0.007032 | 0.04611 | -0.028906 | 0.033454 | 0.2134 | 0.096819 | 0.08413 | 0.089427 | 0.10035 | 0.17256 | 0.083773 | 0.15779 | 0.25778 | 0.10108 | 0.026414 | 0.048231 | 0.087309 | 0.012293 | 0.074653 | 0.10955 | 0.14549 | 0.052845 | 0.088783
5189.4219 | 122.1222 | -0.13275 | 122.0535 | 0.11269 | 0.005267 | -0.021157 | 0.002454 | -0.000359 | 0.071848 | -0.016936 | 0.10743 | 0.20284 | 0.059877 | -0.023943 | -0.002124 | 0.036954 | -0.024328 | 0.033454 | 0.24545 | 0.13802 | 0.11159 | 0.13521 | 0.13239 | 0.2046 | 0.11582 | 0.14863 | 0.24404 | 0.10108 | 0.017256 | 0.039075 | 0.078153 | 0.016871 | 0.074653 | 0.10955 | 0.13176 | 0.062001 | 0.084205
5191.2031 | 122.2366 | -0.054932 | 122.0169 | 0.11727 | -0.00389 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.016936 | 0.11201 | 0.212 | 0.059877 | -0.014785 | 0.007032 | 0.04611 | -0.028906 | 0.028875 | 0.1722 | 0.051042 | 0.038354 | 0.052808 | 0.063729 | 0.13136 | 0.037996 | 0.15321 | 0.2532 | 0.10108 | 0.026414 | 0.048231 | 0.087309 | 0.012293 | 0.070074 | 0.10498 | 0.14091 | 0.052845 | 0.088783
5192.9688 | 122.1313 | -0.1236 | 122.0444 | 0.11727 | 0.000689 | -0.025735 | -0.002124 | -0.000359 | 0.081005 | -0.007779 | 0.11201 | 0.212 | 0.064455 | -0.023943 | 0.002454 | 0.032376 | -0.024328 | 0.028875 | 0.24087 | 0.12428 | 0.097861 | 0.12147 | 0.12324 | 0.2046 | 0.11582 | 0.15321 | 0.2532 | 0.10565 | 0.017256 | 0.043653 | 0.073575 | 0.016871 | 0.070074 | 0.10955 | 0.13634 | 0.062001 | 0.088783
5194.7344 | 122.2641 | -0.068665 | 122.0078 | 0.11269 | -0.00389 | -0.016578 | -0.006703 | -0.000359 | 0.067269 | -0.007779 | 0.10743 | 0.21658 | 0.059877 | -0.019364 | 0.007032 | 0.04611 | -0.024328 | 0.028875 | 0.18136 | 0.064775 | 0.052087 | 0.061962 | 0.068306 | 0.13593 | 0.060886 | 0.14863 | 0.25778 | 0.10108 | 0.021835 | 0.048231 | 0.087309 | 0.016871 | 0.070074 | 0.1004 | 0.13176 | 0.052845 | 0.084205
5196.4531 | 122.1405 | -0.10986 | 122.0535 | 0.11727 | 0.005267 | -0.012 | 0.002454 | -0.000359 | 0.071848 | -0.012357 | 0.11201 | 0.20742 | 0.069033 | -0.019364 | -0.002124 | 0.041532 | -0.019749 | 0.024297 | 0.22714 | 0.11513 | 0.097863 | 0.11232 | 0.1095 | 0.18171 | 0.097506 | 0.15321 | 0.24862 | 0.11023 | 0.021835 | 0.039075 | 0.082731 | 0.02145 | 0.065496 | 0.11413 | 0.13176 | 0.071157 | 0.088782
5198.2188 | 122.1909 | -0.082397 | 122.0215 | 0.12185 | -0.00389 | -0.016578 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.11659 | 0.20742 | 0.059877 | -0.014785 | 0.002454 | 0.036954 | -0.028906 | 0.028875 | 0.20425 | 0.078507 | 0.065819 | 0.075694 | 0.082038 | 0.1634 | 0.074618 | 0.15779 | 0.24862 | 0.10108 | 0.026414 | 0.043653 | 0.078153 | 0.012293 | 0.070074 | 0.11413 | 0.14549 | 0.057423 | 0.088783
5199.9844 | 122.2504 | -0.045776 | 122.0306 | 0.11727 | 0.000689 | -0.012 | -0.006703 | -0.000359 | 0.085583 | -0.007779 | 0.10743 | 0.21658 | 0.055298 | -0.005627 | -0.002124 | 0.041532 | -0.024328 | 0.038032 | 0.16305 | 0.046465 | 0.033776 | 0.039073 | 0.045417 | 0.13136 | 0.037997 | 0.14863 | 0.25778 | 0.096497 | 0.035572 | 0.039075 | 0.082731 | 0.016871 | 0.079231 | 0.10955 | 0.13176 | 0.057422 | 0.079626
5201.7031 | 122.2504 | -0.064087 | 121.9986 | 0.11269 | -0.008469 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.11659 | 0.20742 | 0.069033 | -0.019364 | 0.002454 | 0.050688 | -0.019749 | 0.033454 | 0.17678 | 0.055618 | 0.047509 | 0.061963 | 0.068306 | 0.14051 | 0.056308 | 0.15779 | 0.24862 | 0.11023 | 0.021835 | 0.043653 | 0.091887 | 0.02145 | 0.074653 | 0.11413 | 0.13634 | 0.066579 | 0.088782
5203.4688 | 122.1451 | -0.10529 | 122.0627 | 0.12643 | -0.008469 | -0.016578 | -0.006703 | -0.004937 | 0.085583 | -0.016936 | 0.11201 | 0.212 | 0.059877 | -0.014785 | 0.002454 | 0.041532 | -0.033484 | 0.028875 | 0.23172 | 0.096817 | 0.088708 | 0.098583 | 0.10035 | 0.19087 | 0.08835 | 0.15321 | 0.2532 | 0.10108 | 0.026414 | 0.043653 | 0.082731 | 0.007715 | 0.070074 | 0.10955 | 0.14549 | 0.057423 | 0.093361
5205.1719 | 122.2183 | -0.068665 | 122.0215 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.016936 | 0.11201 | 0.212 | 0.059877 | -0.014785 | -0.002124 | 0.041532 | -0.024328 | 0.028875 | 0.19509 | 0.064775 | 0.056665 | 0.066541 | 0.072884 | 0.14967 | 0.051729 | 0.15321 | 0.2532 | 0.10108 | 0.026414 | 0.039075 | 0.082731 | 0.016871 | 0.070074 | 0.11413 | 0.13634 | 0.062001 | 0.084205
5206.9375 | 122.2504 | -0.045776 | 121.9986 | 0.12185 | -0.013048 | -0.007421 | -0.002124 | -0.000359 | 0.076426 | -0.012357 | 0.10743 | 0.20742 | 0.05072 | -0.019364 | 0.002454 | 0.041532 | -0.024328 | 0.028875 | 0.16763 | 0.032728 | 0.038355 | 0.043652 | 0.045417 | 0.1222 | 0.033419 | 0.14863 | 0.24862 | 0.091919 | 0.021835 | 0.043653 | 0.082731 | 0.016871 | 0.070074 | 0.10498 | 0.13176 | 0.048266 | 0.075048
5208.7031 | 122.2412 | -0.064087 | 122.0261 | 0.11727 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.090161 | -0.016936 | 0.11659 | 0.20284 | 0.059877 | -0.019364 | 0.002454 | 0.036954 | -0.024328 | 0.033454 | 0.18136 | 0.060197 | 0.047509 | 0.057384 | 0.072884 | 0.15425 | 0.047151 | 0.15779 | 0.24404 | 0.10108 | 0.021835 | 0.043653 | 0.078153 | 0.016871 | 0.074653 | 0.11413 | 0.14091 | 0.057423 | 0.084205
5210.5781 | 122.2 | -0.073242 | 121.9711 | 0.12643 | -0.00389 | -0.007421 | 0.007033 | 0.004219 | 0.081005 | -0.012357 | 0.10743 | 0.212 | 0.064455 | -0.023943 | 0.002454 | 0.041532 | -0.019749 | 0.033454 | 0.19967 | 0.069352 | 0.065821 | 0.080275 | 0.077461 | 0.15425 | 0.060885 | 0.14863 | 0.2532 | 0.10565 | 0.017256 | 0.043653 | 0.082731 | 0.02145 | 0.074653 | 0.10498 | 0.12718 | 0.062001 | 0.084204
5212.375 | 122.0993 | -0.11902 | 122.0169 | 0.12185 | -0.00389 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.012357 | 0.11201 | 0.20284 | 0.064455 | -0.023943 | -0.002124 | 0.041532 | -0.024328 | 0.033454 | 0.24087 | 0.11513 | 0.1116 | 0.11689 | 0.12782 | 0.19544 | 0.10666 | 0.15321 | 0.24404 | 0.10565 | 0.017256 | 0.039075 | 0.082731 | 0.016871 | 0.074653 | 0.11413 | 0.13634 | 0.066579 | 0.088783
5214.0938 | 122.0947 | -0.11444 | 122.0306 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.11201 | 0.20742 | 0.059877 | -0.019364 | 0.002454 | 0.041532 | -0.024328 | 0.028875 | 0.23171 | 0.11513 | 0.097863 | 0.10774 | 0.12324 | 0.19545 | 0.10208 | 0.15321 | 0.24862 | 0.10108 | 0.021835 | 0.043653 | 0.082731 | 0.016871 | 0.070074 | 0.10955 | 0.13634 | 0.057423 | 0.084205
5215.7969 | 122.1405 | -0.07782 | 122.0169 | 0.11269 | 0.000689 | -0.021157 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.11201 | 0.212 | 0.069033 | -0.019364 | 0.002454 | 0.04611 | -0.028906 | 0.038032 | 0.19051 | 0.078509 | 0.056663 | 0.075696 | 0.086617 | 0.1634 | 0.070041 | 0.15321 | 0.2532 | 0.11023 | 0.021835 | 0.043653 | 0.087309 | 0.012293 | 0.079231 | 0.10955 | 0.14091 | 0.066579 | 0.097939
5217.5312 | 122.1863 | -0.059509 | 121.9711 | 0.11727 | 0.005267 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.021514 | 0.10743 | 0.20742 | 0.064455 | -0.019364 | 0.007032 | 0.041532 | -0.024328 | 0.033454 | 0.17678 | 0.064776 | 0.042931 | 0.061963 | 0.063728 | 0.14051 | 0.037995 | 0.14863 | 0.24862 | 0.10565 | 0.021835 | 0.048231 | 0.082731 | 0.016871 | 0.074653 | 0.1004 | 0.13176 | 0.057423 | 0.088783
5219.3594 | 122.2275 | -0.073242 | 121.9574 | 0.11727 | 0.005267 | -0.016578 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.10285 | 0.20742 | 0.064455 | -0.019364 | 0.007032 | 0.050688 | -0.024328 | 0.033454 | 0.19051 | 0.078509 | 0.056664 | 0.066539 | 0.072883 | 0.15425 | 0.065463 | 0.14405 | 0.24862 | 0.10565 | 0.021835 | 0.048231 | 0.091887 | 0.016871 | 0.074653 | 0.095819 | 0.12718 | 0.057423 | 0.088783
5221.1094 | 122.1451 | -0.064087 | 121.994 | 0.11727 | -0.00389 | -0.016578 | 0.007033 | -0.000359 | 0.071848 | -0.016936 | 0.10743 | 0.20284 | 0.059877 | -0.014785 | 0.01161 | 0.041532 | -0.028906 | 0.033454 | 0.18136 | 0.060197 | 0.047509 | 0.07112 | 0.063728 | 0.13594 | 0.047151 | 0.14863 | 0.24404 | 0.10108 | 0.026414 | 0.052809 | 0.082731 | 0.012293 | 0.074653 | 0.09582 | 0.13634 | 0.048267 | 0.088783
5222.875 | 122.0947 | -0.10529 | 122.0123 | 0.11269 | 0.005267 | -0.021157 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.10743 | 0.212 | 0.059877 | -0.010206 | 0.002454 | 0.036954 | -0.028906 | 0.038032 | 0.21798 | 0.11055 | 0.084129 | 0.10316 | 0.11408 | 0.18171 | 0.10209 | 0.14863 | 0.2532 | 0.10108 | 0.030993 | 0.043653 | 0.078153 | 0.012293 | 0.079231 | 0.10498 | 0.13634 | 0.057423 | 0.088783
5224.7031 | 122.1634 | -0.091553 | 121.9574 | 0.11727 | -0.00389 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.012357 | 0.10285 | 0.212 | 0.069033 | -0.014785 | 0.007032 | 0.041532 | -0.028906 | 0.038032 | 0.20883 | 0.087663 | 0.074975 | 0.08485 | 0.095772 | 0.1634 | 0.079196 | 0.14405 | 0.2532 | 0.11023 | 0.026414 | 0.048231 | 0.082731 | 0.012293 | 0.079231 | 0.095819 | 0.13176 | 0.062001 | 0.097939
5226.5 | 122.0764 | -0.11444 | 121.9711 | 0.11727 | -0.00389 | -0.016578 | -0.006703 | 0.004219 | 0.085583 | -0.012357 | 0.11201 | 0.20742 | 0.059877 | -0.010206 | 0.002454 | 0.04611 | -0.033484 | 0.024297 | 0.23171 | 0.11055 | 0.097863 | 0.10774 | 0.11866 | 0.20002 | 0.10208 | 0.15321 | 0.24862 | 0.10108 | 0.030993 | 0.043653 | 0.087309 | 0.007715 | 0.065496 | 0.10955 | 0.14549 | 0.057423 | 0.093361
5228.2969 | 121.0098 | -0.064087 | 120.7901 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.081005 | -0.012357 | 0.11201 | 0.19827 | 0.064455 | -0.019364 | 0.016188 | 0.055266 | -0.019749 | 0.04261 | 0.18136 | 0.064776 | 0.047509 | 0.061963 | 0.063728 | 0.14509 | 0.05173 | 0.15321 | 0.23946 | 0.10565 | 0.021835 | 0.057387 | 0.096465 | 0.02145 | 0.083809 | 0.09582 | 0.13176 | 0.048267 | 0.084204
5230.0156 | 121.8475 | -0.073242 | 121.6461 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.012357 | 0.10285 | 0.20742 | 0.059877 | -0.019364 | 0.007032 | 0.041532 | -0.028906 | 0.024297 | 0.19509 | 0.073931 | 0.056664 | 0.066539 | 0.082039 | 0.14967 | 0.060885 | 0.14405 | 0.24862 | 0.10108 | 0.021835 | 0.048231 | 0.082731 | 0.012293 | 0.065496 | 0.095819 | 0.13176 | 0.052845 | 0.088783
5231.8125 | 121.9482 | -0.07782 | 121.7194 | 0.12185 | -0.00389 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.098273 | 0.20284 | 0.059877 | -0.019364 | 0.016188 | 0.055266 | -0.019749 | 0.028875 | 0.19967 | 0.07393 | 0.061242 | 0.075696 | 0.082039 | 0.15882 | 0.070041 | 0.13947 | 0.24404 | 0.10108 | 0.021835 | 0.057387 | 0.096465 | 0.02145 | 0.070074 | 0.082085 | 0.11802 | 0.043689 | 0.079626
5233.6094 | 121.9254 | -0.11444 | 121.6095 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.10285 | 0.20284 | 0.055298 | -0.010206 | 0.034501 | 0.078157 | -0.001436 | 0.070079 | 0.23629 | 0.11513 | 0.097863 | 0.11232 | 0.11866 | 0.19545 | 0.10208 | 0.14405 | 0.24404 | 0.096497 | 0.030993 | 0.0757 | 0.11936 | 0.039763 | 0.11128 | 0.06835 | 0.10429 | 0.020797 | 0.056734
5235.375 | 121.8475 | -0.13275 | 121.6599 | 0.12185 | -0.008469 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.10285 | 0.20284 | 0.064455 | -0.014785 | 0.057392 | 0.10105 | 0.021456 | 0.09297 | 0.2546 | 0.12428 | 0.12075 | 0.12605 | 0.13697 | 0.21376 | 0.12497 | 0.14405 | 0.24404 | 0.10565 | 0.026414 | 0.098591 | 0.14225 | 0.062655 | 0.13417 | 0.045459 | 0.081395 | 0.007063 | 0.042999
5237.125 | 121.8246 | -0.10986 | 121.7194 | 0.12185 | -0.00389 | -0.016578 | -0.002124 | 0.008797 | 0.071848 | -0.012357 | 0.10285 | 0.20284 | 0.064455 | -0.014785 | 0.025345 | 0.050688 | -0.015171 | 0.051766 | 0.23171 | 0.10597 | 0.093285 | 0.10774 | 0.11866 | 0.18171 | 0.097506 | 0.14405 | 0.24404 | 0.10565 | 0.026414 | 0.066544 | 0.091887 | 0.026028 | 0.092965 | 0.077506 | 0.11802 | 0.03911 | 0.079626
5238.9688 | 121.962 | -0.086975 | 121.6965 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | -0.009515 | 0.076426 | -0.016936 | 0.11201 | 0.20284 | 0.064455 | -0.023943 | 0.025345 | 0.055266 | -0.024328 | 0.056344 | 0.20883 | 0.092242 | 0.070397 | 0.084851 | 0.07746 | 0.1634 | 0.070039 | 0.15321 | 0.24404 | 0.10565 | 0.017256 | 0.066544 | 0.096465 | 0.016871 | 0.097543 | 0.086663 | 0.13634 | 0.03911 | 0.088783
5240.7031 | 121.8201 | -0.31586 | 121.5317 | 0.12185 | -0.008469 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | -0.016936 | 0.093694 | 0.19369 | 0.059877 | -0.019364 | 0.24052 | 0.28417 | 0.14507 | 0.2761 | 0.43771 | 0.30739 | 0.30844 | 0.31373 | 0.32008 | 0.39228 | 0.29892 | 0.13489 | 0.23489 | 0.10108 | 0.021835 | 0.28172 | 0.32537 | 0.18627 | 0.3173 | -0.14683 | -0.051379 | -0.18064 | -0.085196
5242.4219 | 117.0181 | -0.1236 | 116.7114 | 0.12185 | 0.005267 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.016936 | 0.10743 | 0.20284 | 0.059877 | -0.019364 | 0.043657 | 0.078157 | -0.015171 | 0.070079 | 0.24545 | 0.12886 | 0.1116 | 0.11689 | 0.12324 | 0.2046 | 0.10666 | 0.14863 | 0.24404 | 0.10108 | 0.021835 | 0.084856 | 0.11936 | 0.026028 | 0.11128 | 0.063773 | 0.1226 | 0.01622 | 0.075048
5244.1719 | 121.5591 | -0.07782 | 121.3577 | 0.11269 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 0.10285 | 0.20284 | 0.064455 | -0.014785 | 0.016188 | 0.050688 | -0.024328 | 0.033454 | 0.19051 | 0.07393 | 0.061242 | 0.071117 | 0.086617 | 0.1634 | 0.060884 | 0.14405 | 0.24404 | 0.10565 | 0.026414 | 0.057387 | 0.091887 | 0.016871 | 0.074653 | 0.086663 | 0.12718 | 0.048267 | 0.088783
5245.9062 | 121.6873 | -0.068665 | 121.463 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | 0.008797 | 0.085583 | -0.012357 | 0.10743 | 0.20284 | 0.064455 | -0.014785 | 0.007032 | 0.04611 | -0.028906 | 0.033454 | 0.19052 | 0.069354 | 0.047508 | 0.066541 | 0.077462 | 0.15425 | 0.056308 | 0.14863 | 0.24404 | 0.10565 | 0.026414 | 0.048231 | 0.087309 | 0.012293 | 0.074653 | 0.1004 | 0.13634 | 0.057423 | 0.093361
5247.625 | 121.6141 | -0.10986 | 121.5637 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.10285 | 0.20284 | 0.064455 | -0.019364 | 0.002454 | 0.041532 | -0.028906 | 0.033454 | 0.23171 | 0.11055 | 0.10244 | 0.10774 | 0.11408 | 0.18629 | 0.097506 | 0.14405 | 0.24404 | 0.10565 | 0.021835 | 0.043653 | 0.082731 | 0.012293 | 0.074653 | 0.1004 | 0.13176 | 0.062001 | 0.093361
5249.3594 | 121.7239 | -0.064087 | 121.5271 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.012357 | 0.10285 | 0.20742 | 0.069033 | -0.019364 | 0.002454 | 0.04611 | -0.028906 | 0.028875 | 0.18594 | 0.064776 | 0.047509 | 0.061963 | 0.063728 | 0.14051 | 0.05173 | 0.14405 | 0.24862 | 0.11023 | 0.021835 | 0.043653 | 0.087309 | 0.012293 | 0.070074 | 0.1004 | 0.13176 | 0.066579 | 0.097939
5251.1562 | 121.7239 | -0.059509 | 121.6141 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | -0.000359 | 0.076426 | -0.012357 | 0.11201 | 0.212 | 0.064455 | -0.019364 | -0.006702 | 0.036954 | -0.028906 | 0.028875 | 0.18136 | 0.060198 | 0.052088 | 0.057385 | 0.05915 | 0.13594 | 0.047152 | 0.15321 | 0.2532 | 0.10565 | 0.021835 | 0.034497 | 0.078153 | 0.012293 | 0.070074 | 0.11871 | 0.14091 | 0.071157 | 0.093361
5252.8594 | 121.7651 | -0.054932 | 121.637 | 0.11727 | 0.000689 | -0.007421 | -0.006703 | 0.004219 | 0.081005 | -0.003201 | 0.11201 | 0.20284 | 0.064455 | -0.019364 | -0.002124 | 0.036954 | -0.033484 | 0.024297 | 0.1722 | 0.055621 | 0.047511 | 0.048229 | 0.059151 | 0.13594 | 0.051731 | 0.15321 | 0.24404 | 0.10565 | 0.021835 | 0.039075 | 0.078153 | 0.007715 | 0.065496 | 0.11413 | 0.14549 | 0.066579 | 0.097939
5254.5625 | 121.7743 | -0.064087 | 121.6187 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.071848 | -0.016936 | 0.11201 | 0.212 | 0.064455 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | 0.024297 | 0.18136 | 0.064776 | 0.047509 | 0.066541 | 0.068306 | 0.13594 | 0.047151 | 0.15321 | 0.2532 | 0.10565 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.065496 | 0.11871 | 0.14549 | 0.071157 | 0.097939
5256.3281 | 121.7606 | -0.068665 | 121.5729 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.016936 | 0.10743 | 0.20742 | 0.069033 | -0.014785 | -0.002124 | 0.032376 | -0.038063 | 0.024297 | 0.18594 | 0.069354 | 0.052087 | 0.066541 | 0.068306 | 0.14509 | 0.051729 | 0.14863 | 0.24862 | 0.11023 | 0.026414 | 0.039075 | 0.073575 | 0.003136 | 0.065496 | 0.10955 | 0.14549 | 0.071157 | 0.1071
5258.1094 | 121.7789 | -0.10986 | 121.6461 | 0.11727 | 0.005267 | -0.021157 | 0.002454 | -0.000359 | 0.085583 | -0.012357 | 0.10743 | 0.20742 | 0.064455 | -0.019364 | 0.052814 | 0.078157 | 0.003143 | 0.074657 | 0.22714 | 0.11513 | 0.088706 | 0.11232 | 0.1095 | 0.19545 | 0.097506 | 0.14863 | 0.24862 | 0.10565 | 0.021835 | 0.094013 | 0.11936 | 0.044342 | 0.11586 | 0.054616 | 0.10429 | 0.011641 | 0.061312
5259.875 | 121.8018 | -0.09613 | 121.6461 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | -0.004937 | 0.085583 | -0.007779 | 0.10285 | 0.20284 | 0.059877 | -0.014785 | 0.016188 | 0.055266 | -0.010593 | 0.033454 | 0.21798 | 0.096819 | 0.074973 | 0.094006 | 0.091193 | 0.18171 | 0.088351 | 0.14405 | 0.24404 | 0.10108 | 0.026414 | 0.057387 | 0.096465 | 0.030606 | 0.074653 | 0.086663 | 0.11344 | 0.043689 | 0.07047
5261.6562 | 121.756 | -0.11902 | 121.6278 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | 0.004219 | 0.071848 | -0.012357 | 0.11201 | 0.20284 | 0.059877 | -0.019364 | 0.016188 | 0.04611 | -0.019749 | 0.038032 | 0.24087 | 0.11971 | 0.097862 | 0.11689 | 0.12324 | 0.19087 | 0.10666 | 0.15321 | 0.24404 | 0.10108 | 0.021835 | 0.057387 | 0.087309 | 0.02145 | 0.079231 | 0.09582 | 0.13176 | 0.043689 | 0.079626
5263.4062 | 121.7056 | -0.12817 | 121.6324 | 0.11269 | -0.00389 | -0.016578 | -0.002124 | -0.000359 | 0.081005 | -0.016936 | 0.10743 | 0.212 | 0.064455 | -0.019364 | 0.048236 | 0.096469 | 0.007721 | 0.079235 | 0.24087 | 0.12428 | 0.1116 | 0.12605 | 0.12782 | 0.20918 | 0.11124 | 0.14863 | 0.2532 | 0.10565 | 0.021835 | 0.089435 | 0.13767 | 0.04892 | 0.12043 | 0.059194 | 0.099709 | 0.016219 | 0.056734
5265.1719 | 121.7285 | -0.56763 | 121.0464 | 0.11269 | 0.000689 | -0.021157 | -0.006703 | -0.000359 | 0.076426 | -0.007779 | 0.10285 | 0.18911 | 0.055298 | -0.023943 | 0.23136 | 0.26128 | 0.12218 | 0.25321 | 0.68032 | 0.56832 | 0.54647 | 0.56092 | 0.56727 | 0.64405 | 0.55985 | 0.14405 | 0.23031 | 0.096497 | 0.017256 | 0.27256 | 0.30248 | 0.16338 | 0.2944 | -0.12851 | -0.01933 | -0.17607 | -0.066883
5266.9219 | 121.7331 | -0.18768 | 121.5042 | 0.11269 | -0.00389 | -0.012 | -0.006703 | 0.004219 | 0.071848 | -0.012357 | 0.098273 | 0.19827 | 0.064455 | -0.014785 | 0.12607 | 0.16056 | 0.044348 | 0.15249 | 0.30038 | 0.18379 | 0.17568 | 0.18098 | 0.1919 | 0.25953 | 0.17533 | 0.13947 | 0.23946 | 0.10565 | 0.026414 | 0.16726 | 0.20176 | 0.085547 | 0.19368 | -0.027792 | 0.053925 | -0.06161 | 0.020107
5268.625 | 121.3028 | -0.10529 | 121.2067 | 0.12185 | 0.000689 | -0.016578 | 0.002454 | -0.000359 | 0.076426 | -0.007779 | 0.098273 | 0.20742 | 0.055298 | -0.010206 | 0.01161 | 0.059844 | -0.015171 | 0.047188 | 0.22714 | 0.10597 | 0.088708 | 0.10774 | 0.10493 | 0.18171 | 0.097507 | 0.13947 | 0.24862 | 0.096497 | 0.030993 | 0.052809 | 0.10104 | 0.026028 | 0.088387 | 0.086663 | 0.11344 | 0.043688 | 0.070469
5270.375 | 121.4859 | -0.068665 | 121.2936 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | -0.000359 | 0.081005 | -0.012357 | 0.098273 | 0.20284 | 0.064455 | -0.010206 | -0.002124 | 0.04611 | -0.033484 | 0.033454 | 0.19052 | 0.069354 | 0.052087 | 0.061962 | 0.068306 | 0.14967 | 0.056308 | 0.13947 | 0.24404 | 0.10565 | 0.030993 | 0.039075 | 0.087309 | 0.007715 | 0.074653 | 0.1004 | 0.13176 | 0.066579 | 0.097939
5272.1562 | 121.582 | -0.054932 | 121.3669 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.008797 | 0.071848 | -0.012357 | 0.11201 | 0.20742 | 0.059877 | -0.019364 | 0.002454 | 0.04611 | -0.028906 | 0.028875 | 0.17678 | 0.060199 | 0.042932 | 0.048229 | 0.063729 | 0.12678 | 0.042575 | 0.15321 | 0.24862 | 0.10108 | 0.021835 | 0.043653 | 0.087309 | 0.012293 | 0.070074 | 0.10955 | 0.14091 | 0.057423 | 0.088783
5273.8594 | 121.5317 | -0.082397 | 121.4584 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.10285 | 0.20742 | 0.064455 | -0.023943 | -0.002124 | 0.036954 | -0.033484 | 0.028875 | 0.19967 | 0.083086 | 0.065819 | 0.075694 | 0.091194 | 0.15882 | 0.074618 | 0.14405 | 0.24862 | 0.10565 | 0.017256 | 0.039075 | 0.078153 | 0.007715 | 0.070074 | 0.10497 | 0.13633 | 0.066579 | 0.097939
5275.625 | 120.9915 | -0.068665 | 120.7993 | 0.12643 | 0.000689 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.10743 | 0.20742 | 0.064455 | -0.019364 | 0.016188 | 0.059844 | -0.015171 | 0.047188 | 0.19509 | 0.069354 | 0.056665 | 0.061962 | 0.068306 | 0.14967 | 0.060886 | 0.14863 | 0.24862 | 0.10565 | 0.021835 | 0.057387 | 0.10104 | 0.026028 | 0.088387 | 0.091242 | 0.1226 | 0.048267 | 0.079626
5277.3906 | 121.1334 | -0.15564 | 120.9229 | 0.11727 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.10285 | 0.19827 | 0.055298 | -0.019364 | 0.048236 | 0.091891 | 0.007721 | 0.074657 | 0.27291 | 0.15633 | 0.14364 | 0.14894 | 0.16444 | 0.23664 | 0.14328 | 0.14405 | 0.23946 | 0.096497 | 0.021835 | 0.089435 | 0.13309 | 0.04892 | 0.11586 | 0.054615 | 0.09513 | 0.007062 | 0.047577
5279.0938 | 121.1975 | -0.2655 | 120.8359 | 0.11269 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.071848 | -0.007779 | 0.098273 | 0.19827 | 0.055298 | 0.035585 | 0.16727 | 0.20634 | 0.080975 | 0.19827 | 0.3782 | 0.26619 | 0.24892 | 0.26338 | 0.26514 | 0.33735 | 0.25772 | 0.13947 | 0.23946 | 0.096497 | 0.076784 | 0.20847 | 0.24754 | 0.12217 | 0.23947 | -0.068995 | 0.017298 | -0.11197 | -0.025677
5280.7812 | 121.2387 | -0.36163 | 120.7535 | 0.12185 | -0.00389 | -0.021157 | -0.006703 | -0.000359 | 0.067269 | -0.007779 | 0.089116 | 0.18453 | 0.046142 | 0.031006 | 0.23594 | 0.27959 | 0.13134 | 0.27152 | 0.48348 | 0.35774 | 0.34048 | 0.35493 | 0.36127 | 0.4289 | 0.35385 | 0.13032 | 0.22573 | 0.087341 | 0.072205 | 0.27714 | 0.32079 | 0.17254 | 0.31272 | -0.14683 | -0.042221 | -0.1898 | -0.085195
5282.5469 | 121.1792 | -0.37537 | 120.7901 | 0.10812 | -0.008469 | -0.012 | -0.006703 | -0.004937 | 0.071848 | -0.016936 | 0.098273 | 0.18453 | 0.055298 | 0.026427 | 0.26341 | 0.2979 | 0.14507 | 0.29899 | 0.48348 | 0.3669 | 0.36337 | 0.36866 | 0.37043 | 0.44721 | 0.35843 | 0.13947 | 0.22573 | 0.096497 | 0.067626 | 0.30461 | 0.3391 | 0.18627 | 0.34019 | -0.16514 | -0.0468 | -0.20811 | -0.089775
5284.3125 | 117.7002 | -0.17853 | 117.4805 | 0.11727 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 0.098273 | 0.19369 | 0.055298 | 0.035585 | 0.14896 | 0.19719 | 0.076397 | 0.17538 | 0.2958 | 0.17464 | 0.16195 | 0.17183 | 0.18732 | 0.26411 | 0.17075 | 0.13947 | 0.23489 | 0.096497 | 0.076784 | 0.19015 | 0.23839 | 0.1176 | 0.21658 | -0.050682 | 0.021876 | -0.093657 | -0.021099
5286.0781 | 120.9686 | -0.10529 | 120.7718 | 0.12185 | -0.00389 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.016936 | 0.098273 | 0.18911 | 0.055298 | 0.031006 | 0.057392 | 0.10105 | 0.003143 | 0.083814 | 0.22714 | 0.1014 | 0.088708 | 0.10316 | 0.10951 | 0.18171 | 0.08835 | 0.13947 | 0.23031 | 0.096497 | 0.072205 | 0.098591 | 0.14225 | 0.044342 | 0.12501 | 0.040881 | 0.09513 | -0.002094 | 0.052155
5287.7812 | 121.2158 | -0.31128 | 120.5795 | 0.12185 | -0.00389 | -0.016578 | -0.006703 | -0.004937 | 0.071848 | -0.016936 | 0.084537 | 0.17537 | 0.05072 | 0.031006 | 0.33666 | 0.36657 | 0.19543 | 0.36308 | 0.43313 | 0.30739 | 0.2947 | 0.30458 | 0.30634 | 0.38313 | 0.29434 | 0.12574 | 0.21657 | 0.091919 | 0.072205 | 0.37786 | 0.40777 | 0.23663 | 0.40428 | -0.25212 | -0.1109 | -0.28594 | -0.14471
5289.5312 | 121.1746 | -0.20599 | 120.7489 | 0.11727 | -0.008469 | -0.021157 | -0.006703 | -0.004937 | 0.076426 | -0.007779 | 0.098273 | 0.19827 | 0.064455 | -0.019364 | 0.17642 | 0.22008 | 0.080975 | 0.20285 | 0.32327 | 0.19753 | 0.18484 | 0.19929 | 0.20106 | 0.28242 | 0.19822 | 0.13947 | 0.23946 | 0.10565 | 0.021835 | 0.21762 | 0.26128 | 0.12217 | 0.24405 | -0.078151 | 0.017298 | -0.11197 | -0.01652
5291.2812 | 121.1014 | -0.21057 | 120.8359 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.012357 | 0.093694 | 0.19369 | 0.055298 | -0.014785 | 0.16269 | 0.20176 | 0.085554 | 0.19369 | 0.32784 | 0.21126 | 0.19399 | 0.20387 | 0.21479 | 0.28242 | 0.19821 | 0.13489 | 0.23489 | 0.096497 | 0.026414 | 0.20389 | 0.24296 | 0.12675 | 0.23489 | -0.068996 | 0.00814 | -0.10739 | -0.030256
5292.9844 | 121.1517 | -0.20142 | 120.9 | 0.11269 | 0.000689 | -0.012 | -0.002124 | -0.004937 | 0.081005 | -0.012357 | 0.089116 | 0.19827 | 0.055298 | -0.023943 | 0.15353 | 0.18803 | 0.076397 | 0.17996 | 0.31411 | 0.20211 | 0.18942 | 0.19929 | 0.19648 | 0.28242 | 0.18906 | 0.13032 | 0.23946 | 0.096497 | 0.017256 | 0.19473 | 0.22923 | 0.1176 | 0.22115 | -0.064418 | 0.012719 | -0.098236 | -0.021099
5294.7344 | 121.2387 | -0.1831 | 120.8771 | 0.11269 | -0.00389 | -0.021157 | -0.002124 | 0.008797 | 0.085583 | -0.016936 | 0.093694 | 0.18911 | 0.055298 | -0.019364 | 0.12607 | 0.16056 | 0.044348 | 0.15249 | 0.2958 | 0.17921 | 0.16195 | 0.18098 | 0.1919 | 0.26869 | 0.16617 | 0.13489 | 0.23031 | 0.096497 | 0.021835 | 0.16726 | 0.20176 | 0.085547 | 0.19368 | -0.032371 | 0.049346 | -0.070767 | 0.01095
5296.5 | 121.1472 | -0.21057 | 120.9412 | 0.11727 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.084537 | 0.19827 | 0.059877 | -0.019364 | 0.14896 | 0.18345 | 0.058083 | 0.1708 | 0.32784 | 0.21126 | 0.20315 | 0.21303 | 0.21937 | 0.287 | 0.20279 | 0.12574 | 0.23946 | 0.10108 | 0.021835 | 0.19015 | 0.22465 | 0.099282 | 0.212 | -0.064418 | 0.026454 | -0.089078 | 0.001794
5298.2188 | 121.1426 | -0.42114 | 120.7077 | 0.11269 | -0.008469 | -0.012 | -0.011281 | -0.000359 | 0.076426 | -0.012357 | 0.089116 | 0.18911 | 0.055298 | -0.019364 | 0.28172 | 0.31622 | 0.15881 | 0.30814 | 0.53384 | 0.41267 | 0.40914 | 0.40986 | 0.42078 | 0.49757 | 0.40879 | 0.13032 | 0.23031 | 0.096497 | 0.021835 | 0.32292 | 0.35741 | 0.20001 | 0.34934 | -0.19261 | -0.069692 | -0.22642 | -0.10351
5299.9844 | 121.1975 | -0.48981 | 120.5246 | 0.12185 | -0.00389 | -0.016578 | -0.01586 | -0.000359 | 0.076426 | -0.012357 | 0.093694 | 0.18911 | 0.055298 | -0.023943 | 0.3916 | 0.43982 | 0.23206 | 0.42718 | 0.61166 | 0.48592 | 0.47323 | 0.47395 | 0.48945 | 0.56623 | 0.47745 | 0.13489 | 0.23031 | 0.096497 | 0.017256 | 0.4328 | 0.48102 | 0.27326 | 0.46838 | -0.2979 | -0.13837 | -0.3363 | -0.17676
5301.75 | 121.0968 | -0.46234 | 120.6299 | 0.11727 | -0.013048 | -0.012 | -0.002124 | -0.004937 | 0.081005 | -0.016936 | 0.089116 | 0.18453 | 0.059877 | -0.019364 | 0.33666 | 0.38031 | 0.20459 | 0.36766 | 0.57961 | 0.44929 | 0.45034 | 0.46022 | 0.4574 | 0.54335 | 0.4454 | 0.13032 | 0.22573 | 0.10108 | 0.021835 | 0.37786 | 0.42151 | 0.24579 | 0.40886 | -0.24754 | -0.11548 | -0.27678 | -0.14471
5303.4531 | 121.1472 | -0.59967 | 120.3598 | 0.11269 | -0.013048 | -0.025735 | -0.01586 | -0.000359 | 0.071848 | -0.021514 | 0.079959 | 0.17995 | 0.055298 | -0.023943 | 0.61593 | 0.64584 | 0.42893 | 0.64235 | 0.71236 | 0.58662 | 0.57394 | 0.58381 | 0.59931 | 0.67152 | 0.57816 | 0.12116 | 0.22115 | 0.096497 | 0.017256 | 0.65713 | 0.68704 | 0.47013 | 0.68355 | -0.53597 | -0.34897 | -0.56063 | -0.37363
5305.2188 | 120.9457 | -1.1581 | 119.6732 | 0.10354 | -0.008469 | -0.016578 | -0.025017 | -0.014093 | 0.067269 | -0.026092 | 0.061645 | 0.16164 | 0.046142 | -0.019364 | 0.92267 | 0.95715 | 0.74942 | 0.95367 | 1.2617 | 1.1497 | 1.1416 | 1.1331 | 1.144 | 1.2254 | 1.1321 | 0.10284 | 0.20283 | 0.087341 | 0.021835 | 0.96387 | 0.99834 | 0.79062 | 0.99486 | -0.86102 | -0.68778 | -0.87652 | -0.70328
5306.9375 | 120.7901 | -120.0302 | 0.36163 | 0.12185 | -0.008469 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.11659 | 0.212 | 0.059877 | -0.010206 | -0.011281 | 0.027798 | -0.006014 | 0.019719 | 120.1521 | 120.0217 | 120.0182 | 120.0327 | 120.039 | 120.1112 | 120.0224 | 0.15779 | 0.2532 | 0.10108 | 0.030993 | 0.029918 | 0.068997 | 0.035185 | 0.060918 | 0.12787 | 0.1226 | 0.071158 | 0.065891
5308.7031 | 120.8908 | -120.3094 | 0.40741 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.10285 | 0.212 | 0.064455 | -0.010206 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 120.4313 | 120.3101 | 120.302 | 120.3073 | 120.3182 | 120.395 | 120.3017 | 0.14405 | 0.2532 | 0.10565 | 0.030993 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 0.11413 | 0.14091 | 0.075736 | 0.10252
5310.4688 | 120.8038 | -120.1492 | 0.4303 | 0.12643 | 0.000689 | -0.002842 | 0.002454 | 0.017953 | 0.085583 | 0.001377 | 0.11201 | 0.20284 | 0.069033 | -0.014785 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 120.2757 | 120.1499 | 120.1464 | 120.1517 | 120.1672 | 120.2348 | 120.1506 | 0.15321 | 0.24404 | 0.11023 | 0.026414 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.15007 | 0.080314 | 0.1071
5312.2344 | 120.9503 | -120.2499 | 0.4715 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.090161 | -0.003201 | 0.10743 | 0.21658 | 0.059877 | -0.014785 | -0.015859 | 0.014064 | -0.033484 | -0.012328 | 120.3764 | 120.2552 | 120.2379 | 120.2524 | 120.2587 | 120.3401 | 120.2467 | 0.14863 | 0.25778 | 0.10108 | 0.026414 | 0.02534 | 0.055263 | 0.007715 | 0.028871 | 0.12329 | 0.14091 | 0.075736 | 0.093361
5313.9375 | 121.0007 | -120.2591 | 0.50354 | 0.13101 | 0.009846 | -0.002842 | 0.007033 | 0.004219 | 0.081005 | -0.007779 | 0.11201 | 0.212 | 0.069033 | -0.019364 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 120.3901 | 120.2689 | 120.2563 | 120.2661 | 120.2633 | 120.3401 | 120.2513 | 0.15321 | 0.2532 | 0.11023 | 0.021835 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.12329 | 0.15007 | 0.080314 | 0.1071
5315.6875 | 121.1105 | -120.3094 | 0.50812 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.013375 | 0.085583 | -0.003201 | 0.11201 | 0.212 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 120.4313 | 120.3101 | 120.302 | 120.3119 | 120.3228 | 120.395 | 120.3062 | 0.15321 | 0.2532 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.11871 | 0.15007 | 0.062 | 0.093361
5317.4375 | 121.1105 | -120.3461 | 0.49439 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.090161 | -0.007779 | 0.10743 | 0.212 | 0.069033 | -0.019364 | -0.006702 | 0.02322 | -0.033484 | -0.00775 | 120.4679 | 120.3468 | 120.3386 | 120.3439 | 120.3549 | 120.4362 | 120.3383 | 0.14863 | 0.2532 | 0.11023 | 0.021835 | 0.034497 | 0.064419 | 0.007715 | 0.033449 | 0.11413 | 0.14091 | 0.075735 | 0.10252
5319.1562 | 121.0876 | -120.3827 | 0.52643 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.012357 | 0.10743 | 0.20742 | 0.064455 | -0.014785 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 120.5091 | 120.3834 | 120.3707 | 120.3851 | 120.3915 | 120.4683 | 120.3703 | 0.14863 | 0.24862 | 0.10565 | 0.026414 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.11413 | 0.14091 | 0.071157 | 0.097939
5320.8594 | 120.6253 | -3.2364 | 117.3248 | 0.12185 | -0.00389 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.012357 | 0.10285 | 0.19827 | 0.059877 | -0.014785 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 3.3582 | 3.2325 | 3.2198 | 3.2343 | 3.2452 | 3.3128 | 3.224 | 0.14405 | 0.23946 | 0.10108 | 0.026414 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.14091 | 0.071158 | 0.09794
5322.625 | 120.7352 | -104.9927 | 15.2435 | 0.11727 | -0.00389 | -0.012 | 0.002454 | 0.017953 | 0.076426 | -0.003201 | 0.10285 | 0.19369 | 0.073611 | -0.014785 | -0.015859 | 0.018642 | -0.033484 | 0.001406 | 105.1099 | 104.9888 | 104.9807 | 104.9951 | 105.0106 | 105.0691 | 104.9895 | 0.14405 | 0.23489 | 0.11481 | 0.026414 | 0.02534 | 0.059841 | 0.007715 | 0.042605 | 0.11871 | 0.13633 | 0.08947 | 0.10709
5324.3906 | 120.9045 | -105.2948 | 15.1932 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.076426 | -0.012357 | 0.098273 | 0.20284 | 0.064455 | -0.010206 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 105.4212 | 105.2955 | 105.2874 | 105.2973 | 105.3036 | 105.3712 | 105.2824 | 0.13947 | 0.24404 | 0.10565 | 0.030993 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.10497 | 0.13176 | 0.071157 | 0.097939
5326.1562 | 116.4551 | -80.4382 | 35.1379 | 0.12643 | 0.009846 | -0.002842 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.10743 | 0.20284 | 0.059877 | -0.019364 | -0.006702 | 0.014064 | -0.038063 | -0.00775 | 80.5647 | 80.4481 | 80.4354 | 80.4407 | 80.4516 | 80.5147 | 80.4305 | 0.14863 | 0.24404 | 0.10108 | 0.021835 | 0.034497 | 0.055263 | 0.003136 | 0.033449 | 0.11413 | 0.14549 | 0.066579 | 0.09794
5327.8594 | 120.726 | -105.2124 | 15.0101 | 0.12643 | -0.00389 | -0.007421 | -0.006703 | 0.004219 | 0.090161 | -0.007779 | 0.10743 | 0.20742 | 0.064455 | -0.014785 | -0.011281 | 0.032376 | -0.028906 | -0.00775 | 105.3388 | 105.2085 | 105.205 | 105.2057 | 105.2166 | 105.3026 | 105.2046 | 0.14863 | 0.24862 | 0.10565 | 0.026414 | 0.029918 | 0.073575 | 0.012293 | 0.033449 | 0.11871 | 0.13634 | 0.075736 | 0.093361
5329.6094 | 120.7489 | -105.3772 | 15.1245 | 0.12643 | 0.000689 | -0.002842 | 0.002454 | 0.013375 | 0.085583 | -0.003201 | 0.10285 | 0.20742 | 0.055298 | -0.010206 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 105.5036 | 105.3779 | 105.3744 | 105.3797 | 105.3906 | 105.4628 | 105.374 | 0.14405 | 0.24862 | 0.096497 | 0.030993 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 0.11413 | 0.14091 | 0.066579 | 0.093361
5331.3125 | 120.8359 | -105.9631 | 14.6622 | 0.12643 | 0.005267 | -0.007421 | 0.007033 | 0.013375 | 0.085583 | -0.007779 | 0.11659 | 0.20284 | 0.064455 | -0.019364 | -0.015859 | 0.02322 | -0.042641 | -0.00775 | 106.0896 | 105.9684 | 105.9557 | 105.9702 | 105.9765 | 106.0487 | 105.9554 | 0.15779 | 0.24404 | 0.10565 | 0.021835 | 0.02534 | 0.064419 | -0.001442 | 0.033449 | 0.13245 | 0.15923 | 0.080314 | 0.1071
5333.0938 | 120.9091 | -105.661 | 15.0146 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.004219 | 0.085583 | -0.007779 | 0.11201 | 0.20742 | 0.064455 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 105.7829 | 105.6617 | 105.6536 | 105.6635 | 105.6652 | 105.7466 | 105.6532 | 0.15321 | 0.24862 | 0.10565 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.11871 | 0.14549 | 0.071157 | 0.097939
5334.7969 | 120.9961 | -105.1209 | 15.6006 | 0.12643 | 0.000689 | -0.002842 | 0.007033 | 0.013375 | 0.076426 | -0.007779 | 0.11201 | 0.212 | 0.069033 | -0.014785 | -0.011281 | 0.018642 | -0.033484 | -0.00775 | 105.2473 | 105.1215 | 105.118 | 105.1279 | 105.1342 | 105.1973 | 105.1131 | 0.15321 | 0.2532 | 0.11023 | 0.026414 | 0.029918 | 0.059841 | 0.007715 | 0.033449 | 0.12329 | 0.14549 | 0.080314 | 0.10252
5336.5469 | 120.5658 | -105.5054 | 14.6805 | 0.12185 | -0.008469 | -0.007421 | 0.007033 | 0.004219 | 0.085583 | -0.003201 | 0.10285 | 0.21658 | 0.064455 | -0.014785 | -0.011281 | 0.032376 | -0.038063 | -0.012328 | 105.6272 | 105.4969 | 105.498 | 105.5124 | 105.5096 | 105.591 | 105.5022 | 0.14405 | 0.25778 | 0.10565 | 0.026414 | 0.029918 | 0.073575 | 0.003136 | 0.028871 | 0.11413 | 0.14091 | 0.075736 | 0.10252
5338.3125 | 120.9229 | -106.0272 | 14.534 | 0.12643 | 0.005267 | -0.012 | 0.007033 | 0.013375 | 0.09474 | -0.007779 | 0.10743 | 0.20284 | 0.064455 | -0.019364 | -0.015859 | 0.02322 | -0.038063 | 0.001406 | 106.1537 | 106.0325 | 106.0152 | 106.0343 | 106.0406 | 106.122 | 106.0194 | 0.14863 | 0.24404 | 0.10565 | 0.021835 | 0.02534 | 0.064419 | 0.003136 | 0.042605 | 0.12329 | 0.14549 | 0.080314 | 0.10252
5340.0312 | 120.9457 | -106.2653 | 14.4424 | 0.13101 | 0.005267 | -0.007421 | 0.002454 | 0.004219 | 0.090161 | -0.007779 | 0.10285 | 0.20742 | 0.064455 | -0.014785 | -0.015859 | 0.027798 | -0.038063 | -0.00775 | 106.3963 | 106.2705 | 106.2578 | 106.2677 | 106.2695 | 106.3554 | 106.2575 | 0.14405 | 0.24862 | 0.10565 | 0.026414 | 0.02534 | 0.068997 | 0.003136 | 0.033449 | 0.11871 | 0.14091 | 0.080314 | 0.10252
5341.7969 | 120.9641 | -106.1874 | 14.6027 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.10285 | 0.20284 | 0.064455 | -0.014785 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 106.3093 | 106.1927 | 106.1754 | 106.1807 | 106.1917 | 106.2639 | 106.1797 | 0.14405 | 0.24404 | 0.10565 | 0.026414 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.14091 | 0.071157 | 0.10252
5343.5625 | 120.9961 | -106.2241 | 14.6484 | 0.11727 | 0.005267 | -0.012 | 0.011611 | 0.013375 | 0.09474 | -0.007779 | 0.10743 | 0.19827 | 0.059877 | -0.014785 | -0.002124 | 0.02322 | -0.033484 | -0.012328 | 106.3413 | 106.2293 | 106.2121 | 106.2357 | 106.2374 | 106.3188 | 106.2163 | 0.14863 | 0.23946 | 0.10108 | 0.026414 | 0.039075 | 0.064419 | 0.007715 | 0.028871 | 0.10955 | 0.14091 | 0.062001 | 0.093361
5345.3281 | 120.3827 | -5.1956 | 115.7547 | 0.12643 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.081005 | -0.003201 | 0.10285 | 0.19827 | 0.064455 | -0.010206 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 5.322 | 5.1963 | 5.1836 | 5.1889 | 5.2044 | 5.2766 | 5.1924 | 0.14405 | 0.23946 | 0.10565 | 0.030993 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 0.10955 | 0.13633 | 0.071157 | 0.097939
5347.0312 | 120.4788 | -4.8203 | 116.1438 | 0.11727 | 0.000689 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.016936 | 0.093694 | 0.19827 | 0.059877 | -0.019364 | -0.002124 | 0.036954 | -0.038063 | -0.003172 | 4.9375 | 4.8209 | 4.7991 | 4.8135 | 4.8245 | 4.9013 | 4.8033 | 0.13489 | 0.23946 | 0.10108 | 0.021835 | 0.039075 | 0.078153 | 0.003136 | 0.038027 | 0.095818 | 0.13176 | 0.062001 | 0.09794
5348.7969 | 120.9641 | -4.5547 | 116.4825 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.012357 | 0.10743 | 0.20284 | 0.059877 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.003172 | 4.672 | 4.5554 | 4.5382 | 4.5526 | 4.5544 | 4.6312 | 4.5424 | 0.14863 | 0.24404 | 0.10108 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.038027 | 0.10955 | 0.14091 | 0.062001 | 0.093361
5350.4844 | 120.3003 | -2.7786 | 118.2083 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | -0.000359 | 0.081005 | -0.016936 | 0.093694 | 0.19369 | 0.059877 | -0.019364 | -0.011281 | 0.02322 | -0.024328 | -0.003172 | 2.9005 | 2.7793 | 2.7575 | 2.7765 | 2.7783 | 2.8596 | 2.7617 | 0.13489 | 0.23489 | 0.10108 | 0.021835 | 0.029918 | 0.064419 | 0.016871 | 0.038027 | 0.10497 | 0.11802 | 0.071158 | 0.084205
5352.2344 | 121.0098 | -2.7008 | 118.3182 | 0.12185 | -0.00389 | -0.012 | -0.006703 | -0.000359 | 0.085583 | -0.007779 | 0.10285 | 0.20284 | 0.064455 | -0.014785 | -0.006702 | 0.036954 | -0.028906 | -0.003172 | 2.8227 | 2.6969 | 2.6888 | 2.6941 | 2.7004 | 2.7864 | 2.693 | 0.14405 | 0.24404 | 0.10565 | 0.026414 | 0.034497 | 0.078153 | 0.012293 | 0.038027 | 0.10955 | 0.13176 | 0.071157 | 0.093361
5354 | 120.607 | -71.5073 | 47.7448 | 0.13101 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.10743 | 0.19827 | 0.064455 | -0.019364 | -0.006702 | 0.036954 | -0.033484 | -0.00775 | 71.6383 | 71.5034 | 71.4953 | 71.5051 | 71.5115 | 71.5928 | 71.4995 | 0.14863 | 0.23946 | 0.10565 | 0.021835 | 0.034497 | 0.078153 | 0.007715 | 0.033449 | 0.11413 | 0.14091 | 0.071157 | 0.097939
5355.7031 | 120.8588 | -7.1228 | 113.5712 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | -0.000359 | 0.081005 | -0.003201 | 0.098273 | 0.19827 | 0.064455 | -0.019364 | -0.002124 | 0.027798 | -0.028906 | 0.001406 | 7.2447 | 7.1235 | 7.1154 | 7.1207 | 7.1224 | 7.2038 | 7.1196 | 0.13947 | 0.23946 | 0.10565 | 0.021835 | 0.039075 | 0.068997 | 0.012293 | 0.042605 | 0.1004 | 0.12718 | 0.066579 | 0.093361
5357.4688 | 120.8862 | -6.546 | 114.2395 | 0.12185 | 0.005267 | -0.021157 | -0.006703 | 0.004219 | 0.076426 | -0.016936 | 0.093694 | 0.20284 | 0.059877 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | 0.005985 | 6.6679 | 6.5513 | 6.5249 | 6.5393 | 6.5502 | 6.6224 | 6.5291 | 0.13489 | 0.24404 | 0.10108 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.047184 | 0.10497 | 0.13176 | 0.071158 | 0.09794
5359.2344 | 120.8862 | -5.7175 | 115.21 | 0.11269 | 0.000689 | -0.012 | -0.002124 | -0.004937 | 0.081005 | -0.007779 | 0.10285 | 0.19827 | 0.059877 | -0.014785 | -0.006702 | 0.036954 | -0.028906 | -0.003172 | 5.8302 | 5.7182 | 5.7055 | 5.7153 | 5.7125 | 5.7985 | 5.7097 | 0.14405 | 0.23946 | 0.10108 | 0.026414 | 0.034497 | 0.078153 | 0.012293 | 0.038027 | 0.10955 | 0.13176 | 0.066579 | 0.088783
5360.9375 | 121.0236 | -4.7653 | 116.1163 | 0.11727 | -0.00389 | -0.012 | -0.002124 | -0.000359 | 0.081005 | -0.016936 | 0.098273 | 0.19827 | 0.059877 | -0.014785 | -0.002124 | 0.032376 | -0.038063 | -0.012328 | 4.8826 | 4.7614 | 4.7533 | 4.7632 | 4.765 | 4.8463 | 4.7484 | 0.13947 | 0.23946 | 0.10108 | 0.026414 | 0.039075 | 0.073575 | 0.003136 | 0.028871 | 0.1004 | 0.13634 | 0.062001 | 0.09794
5362.7031 | 121.0098 | -4.7333 | 116.2628 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | -0.000359 | 0.081005 | -0.003201 | 0.10285 | 0.20284 | 0.059877 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.003172 | 4.8551 | 4.7385 | 4.7167 | 4.7266 | 4.7329 | 4.8143 | 4.7301 | 0.14405 | 0.24404 | 0.10108 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.13633 | 0.062001 | 0.093361
5364.4688 | 121.0602 | -4.6829 | 116.2949 | 0.12185 | -0.00389 | -0.012 | 0.002454 | 0.004219 | 0.085583 | -0.007779 | 0.098273 | 0.19827 | 0.055298 | -0.010206 | -0.006702 | 0.02322 | -0.028906 | -0.012328 | 4.8048 | 4.679 | 4.6709 | 4.6854 | 4.6871 | 4.7685 | 4.6751 | 0.13947 | 0.23946 | 0.096497 | 0.030993 | 0.034497 | 0.064419 | 0.012293 | 0.028871 | 0.10497 | 0.12718 | 0.062 | 0.084204
5366.2344 | 121.0739 | -4.715 | 116.3177 | 0.12643 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 0.10285 | 0.19827 | 0.064455 | -0.014785 | -0.002124 | 0.027798 | -0.033484 | 0.001406 | 4.8414 | 4.7111 | 4.6984 | 4.7083 | 4.7238 | 4.796 | 4.7072 | 0.14405 | 0.23946 | 0.10565 | 0.026414 | 0.039075 | 0.068997 | 0.007715 | 0.042605 | 0.10497 | 0.13633 | 0.066579 | 0.097939
5367.9375 | 121.0693 | -4.4632 | 116.6428 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.098273 | 0.19827 | 0.055298 | -0.014785 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 4.585 | 4.4639 | 4.4512 | 4.4611 | 4.472 | 4.5396 | 4.4554 | 0.13947 | 0.23946 | 0.096497 | 0.026414 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 0.10497 | 0.12718 | 0.062 | 0.084204
5369.7031 | 121.1884 | -4.3488 | 116.6611 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.098273 | 0.19827 | 0.059877 | -0.019364 | -0.006702 | 0.036954 | -0.033484 | -0.00775 | 4.4706 | 4.354 | 4.3322 | 4.3466 | 4.3576 | 4.4343 | 4.341 | 0.13947 | 0.23946 | 0.10108 | 0.021835 | 0.034497 | 0.078153 | 0.007715 | 0.033449 | 0.10497 | 0.13176 | 0.066579 | 0.093361
5371.4062 | 121.2204 | -4.4861 | 116.5924 | 0.11727 | 0.000689 | -0.012 | -0.006703 | -0.000359 | 0.076426 | -0.012357 | 0.098273 | 0.19827 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 4.6034 | 4.4868 | 4.4741 | 4.4794 | 4.4857 | 4.5625 | 4.4737 | 0.13947 | 0.23946 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 0.10955 | 0.12718 | 0.066579 | 0.084204
5373.1719 | 121.1746 | -4.5502 | 116.6382 | 0.12643 | -0.008469 | -0.016578 | 0.002454 | 0.004219 | 0.085583 | -0.012357 | 0.098273 | 0.20284 | 0.059877 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 4.6766 | 4.5417 | 4.5336 | 4.5526 | 4.5544 | 4.6358 | 4.5378 | 0.13947 | 0.24404 | 0.10108 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.10497 | 0.13176 | 0.066579 | 0.093361
5374.875 | 121.1334 | -4.4449 | 116.6885 | 0.11727 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.098273 | 0.19827 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 4.5622 | 4.4456 | 4.4329 | 4.4428 | 4.4537 | 4.5259 | 4.4325 | 0.13947 | 0.23946 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.10497 | 0.13176 | 0.057422 | 0.084204
5376.6406 | 121.1792 | -3.8635 | 117.3157 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.093694 | 0.19827 | 0.064455 | -0.019364 | 0.002454 | 0.032376 | -0.038063 | -0.003172 | 3.9854 | 3.8642 | 3.8469 | 3.8568 | 3.8723 | 3.9445 | 3.8512 | 0.13489 | 0.23946 | 0.10565 | 0.021835 | 0.043653 | 0.073575 | 0.003136 | 0.038027 | 0.09124 | 0.13176 | 0.062001 | 0.10252
5378.3906 | 120.4285 | -82.1915 | 38.1546 | 0.12185 | 0.000689 | -0.002842 | 0.007033 | 0.008797 | 0.085583 | -0.003201 | 0.10285 | 0.20284 | 0.064455 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 82.3133 | 82.1922 | 82.1886 | 82.1985 | 82.2003 | 82.2771 | 82.1883 | 0.14405 | 0.24404 | 0.10565 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.10955 | 0.13633 | 0.071157 | 0.097939
5380.1719 | 120.2316 | -10.7208 | 109.7992 | 0.11727 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.098273 | 0.19369 | 0.059877 | -0.033101 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 10.8381 | 10.7169 | 10.7088 | 10.7187 | 10.725 | 10.7973 | 10.713 | 0.13947 | 0.23489 | 0.10108 | 0.008098 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.10497 | 0.13176 | 0.066579 | 0.093361
5381.8594 | 120.9732 | -111.0214 | 9.4254 | 0.12643 | -0.00389 | -0.007421 | 0.002454 | 0.008797 | 0.076426 | -0.003201 | 0.10285 | 0.19827 | 0.064455 | -0.014785 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 111.1479 | 111.0175 | 111.014 | 111.0239 | 111.0302 | 111.0978 | 111.0182 | 0.14405 | 0.23946 | 0.10565 | 0.026414 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.11413 | 0.13633 | 0.075736 | 0.097939
5383.6094 | 121.0144 | -119.1605 | 1.4923 | 0.13101 | 0.005267 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.098273 | 0.20284 | 0.073611 | -0.014785 | -0.020437 | 0.027798 | -0.033484 | -0.00775 | 119.2915 | 119.1657 | 119.1485 | 119.1538 | 119.1647 | 119.2415 | 119.1527 | 0.13947 | 0.24404 | 0.11481 | 0.026414 | 0.020762 | 0.068997 | 0.007715 | 0.033449 | 0.11871 | 0.13176 | 0.094048 | 0.10709
5385.375 | 121.1014 | -119.696 | 0.99792 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.003201 | 0.098273 | 0.20284 | 0.055298 | -0.019364 | -0.011281 | 0.027798 | -0.042641 | -0.003172 | 119.8179 | 119.6967 | 119.6795 | 119.6893 | 119.7048 | 119.7725 | 119.6928 | 0.13947 | 0.24404 | 0.096497 | 0.021835 | 0.029918 | 0.068997 | -0.001442 | 0.038027 | 0.10955 | 0.14091 | 0.066579 | 0.097939
5387.125 | 120.9961 | -0.40741 | 120.5566 | 0.12643 | -0.00389 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.098273 | 0.19369 | 0.059877 | -0.014785 | -0.011281 | 0.041532 | -0.033484 | 0.001406 | 0.53384 | 0.40352 | 0.39999 | 0.40529 | 0.41163 | 0.48384 | 0.39505 | 0.13947 | 0.23489 | 0.10108 | 0.026414 | 0.029918 | 0.082731 | 0.007715 | 0.042605 | 0.10955 | 0.13176 | 0.071158 | 0.093361
5388.8281 | 121.0556 | -0.3891 | 120.575 | 0.12185 | 0.005267 | -0.012 | -0.006703 | -0.000359 | 0.076426 | -0.016936 | 0.093694 | 0.19369 | 0.055298 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | 0.001406 | 0.51095 | 0.39437 | 0.3771 | 0.3824 | 0.38874 | 0.46552 | 0.37216 | 0.13489 | 0.23489 | 0.096497 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.042605 | 0.095818 | 0.12718 | 0.057422 | 0.088782
5390.5781 | 121.1151 | -0.38452 | 120.6436 | 0.11727 | -0.00389 | -0.007421 | -0.006703 | 0.008797 | 0.085583 | -0.016936 | 0.098273 | 0.18453 | 0.055298 | -0.023943 | -0.002124 | 0.036954 | -0.024328 | 0.001406 | 0.50179 | 0.38063 | 0.3771 | 0.37782 | 0.39332 | 0.4701 | 0.36758 | 0.13947 | 0.22573 | 0.096497 | 0.017256 | 0.039075 | 0.078153 | 0.016871 | 0.042605 | 0.1004 | 0.1226 | 0.057422 | 0.079626
5392.3281 | 121.1426 | -0.38452 | 120.6619 | 0.12185 | -0.008469 | -0.012 | -0.002124 | -0.000359 | 0.071848 | -0.007779 | 0.093694 | 0.19827 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 0.50637 | 0.37605 | 0.37252 | 0.3824 | 0.38416 | 0.45637 | 0.37674 | 0.13489 | 0.23946 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.10497 | 0.13176 | 0.066579 | 0.093361
5394.0312 | 121.0922 | -0.4303 | 120.7169 | 0.12185 | -0.00389 | -0.002842 | -0.011281 | 0.004219 | 0.081005 | -0.007779 | 0.098273 | 0.19827 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | 0.005985 | 0.55215 | 0.42641 | 0.42746 | 0.41902 | 0.43452 | 0.5113 | 0.42252 | 0.13947 | 0.23946 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.047184 | 0.10497 | 0.13176 | 0.062 | 0.088782
5395.7812 | 121.2067 | -0.36621 | 120.7031 | 0.12643 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.071848 | -0.007779 | 0.093694 | 0.19827 | 0.05072 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | 0.001406 | 0.49264 | 0.36232 | 0.34963 | 0.35951 | 0.37501 | 0.43806 | 0.35843 | 0.13489 | 0.23946 | 0.091919 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.042605 | 0.1004 | 0.13176 | 0.057422 | 0.088783
5397.5312 | 121.1563 | -0.41657 | 120.7535 | 0.12185 | 0.005267 | -0.007421 | -0.006703 | 0.004219 | 0.085583 | -0.007779 | 0.098273 | 0.19369 | 0.059877 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.00775 | 0.53842 | 0.42183 | 0.40914 | 0.40986 | 0.42078 | 0.50215 | 0.40879 | 0.13947 | 0.23489 | 0.10108 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.033449 | 0.10497 | 0.12718 | 0.066579 | 0.088783
5399.2969 | 120.3506 | -0.37079 | 119.8334 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.007779 | 0.093694 | 0.19827 | 0.059877 | -0.014785 | -0.006702 | 0.036954 | -0.028906 | -0.00775 | 0.48806 | 0.37148 | 0.35421 | 0.36409 | 0.37501 | 0.44264 | 0.36301 | 0.13489 | 0.23946 | 0.10108 | 0.026414 | 0.034497 | 0.078153 | 0.012293 | 0.033449 | 0.1004 | 0.1226 | 0.066579 | 0.088783
5401 | 120.6802 | -0.38452 | 120.2637 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.093694 | 0.20284 | 0.059877 | -0.014785 | -0.002124 | 0.02322 | -0.033484 | -0.00775 | 0.50637 | 0.38979 | 0.36794 | 0.3824 | 0.38874 | 0.4701 | 0.37674 | 0.13489 | 0.24404 | 0.10108 | 0.026414 | 0.039075 | 0.064419 | 0.007715 | 0.033449 | 0.095818 | 0.12718 | 0.062001 | 0.093361
5402.7656 | 120.7993 | -0.40283 | 120.3781 | 0.12643 | 0.000689 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.093694 | 0.19369 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | 0.001406 | 0.52926 | 0.40352 | 0.39083 | 0.39613 | 0.40705 | 0.48384 | 0.39505 | 0.13489 | 0.23489 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.042605 | 0.10497 | 0.12718 | 0.062001 | 0.084204
5404.5312 | 120.8725 | -0.39825 | 120.4559 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.10285 | 0.18911 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 0.52468 | 0.39894 | 0.38625 | 0.39613 | 0.40705 | 0.47926 | 0.3859 | 0.14405 | 0.23031 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.13633 | 0.066579 | 0.088782
5406.2969 | 120.8633 | -0.41657 | 120.5246 | 0.12185 | 0.005267 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.012357 | 0.098273 | 0.19827 | 0.05072 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.00775 | 0.53842 | 0.42183 | 0.40457 | 0.40986 | 0.41621 | 0.49757 | 0.40421 | 0.13947 | 0.23946 | 0.091919 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.033449 | 0.1004 | 0.13176 | 0.052844 | 0.084204
5408.0469 | 120.9778 | -0.37994 | 120.5658 | 0.11269 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.085583 | -0.007779 | 0.098273 | 0.19369 | 0.059877 | -0.019364 | -0.002124 | 0.036954 | -0.033484 | -0.003172 | 0.49264 | 0.38063 | 0.36337 | 0.3824 | 0.38416 | 0.46553 | 0.37217 | 0.13947 | 0.23489 | 0.10108 | 0.021835 | 0.039075 | 0.078153 | 0.007715 | 0.038027 | 0.1004 | 0.13176 | 0.062001 | 0.093361
5409.75 | 121.0876 | -0.36163 | 120.6116 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | -0.000359 | 0.076426 | -0.016936 | 0.10285 | 0.19369 | 0.059877 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.003172 | 0.47891 | 0.36232 | 0.34506 | 0.35493 | 0.36127 | 0.43806 | 0.3447 | 0.14405 | 0.23489 | 0.10108 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.038027 | 0.10497 | 0.13633 | 0.062001 | 0.093361
5411.5156 | 121.1288 | -0.3891 | 120.6436 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.093694 | 0.19827 | 0.059877 | -0.019364 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 0.50637 | 0.38979 | 0.37252 | 0.38697 | 0.39332 | 0.46552 | 0.37674 | 0.13489 | 0.23946 | 0.10108 | 0.021835 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.10497 | 0.13176 | 0.071158 | 0.09794
5413.2812 | 121.2204 | -0.35706 | 120.6573 | 0.12185 | 0.000689 | -0.007421 | -0.006703 | 0.004219 | 0.081005 | -0.016936 | 0.089116 | 0.18911 | 0.05072 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.003172 | 0.47891 | 0.35774 | 0.34963 | 0.35035 | 0.36127 | 0.43806 | 0.34012 | 0.13032 | 0.23031 | 0.091919 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.038027 | 0.09124 | 0.1226 | 0.052844 | 0.084204
5415 | 121.1334 | -0.40741 | 120.7443 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 0.098273 | 0.19827 | 0.059877 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 0.52926 | 0.41268 | 0.39541 | 0.40071 | 0.41621 | 0.49299 | 0.39505 | 0.13947 | 0.23946 | 0.10108 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.13176 | 0.066579 | 0.093361
5416.75 | 121.1746 | -0.39825 | 120.7123 | 0.11727 | 0.005267 | -0.016578 | -0.006703 | -0.000359 | 0.081005 | -0.012357 | 0.089116 | 0.18911 | 0.055298 | -0.028522 | -0.002124 | 0.027798 | -0.038063 | -0.003172 | 0.51553 | 0.40352 | 0.38168 | 0.39155 | 0.39789 | 0.47926 | 0.3859 | 0.13032 | 0.23031 | 0.096497 | 0.012677 | 0.039075 | 0.068997 | 0.003136 | 0.038027 | 0.09124 | 0.12718 | 0.057422 | 0.093361
5418.5 | 121.2341 | -0.39825 | 120.7535 | 0.11727 | -0.00389 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.093694 | 0.19369 | 0.059877 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.51553 | 0.39436 | 0.3771 | 0.39155 | 0.40247 | 0.47926 | 0.39048 | 0.13489 | 0.23489 | 0.10108 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.066579 | 0.093361
5420.2812 | 121.2708 | -0.37079 | 120.7352 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.10285 | 0.19827 | 0.046142 | -0.023943 | -0.002124 | 0.036954 | -0.033484 | -0.00775 | 0.49722 | 0.3669 | 0.35879 | 0.36866 | 0.37501 | 0.45179 | 0.35843 | 0.14405 | 0.23946 | 0.087341 | 0.017256 | 0.039075 | 0.078153 | 0.007715 | 0.033449 | 0.10497 | 0.13633 | 0.048266 | 0.079626
5422.0469 | 121.225 | -0.40283 | 120.7947 | 0.11269 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.098273 | 0.20284 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.024328 | 0.001406 | 0.51553 | 0.40352 | 0.38625 | 0.40529 | 0.40705 | 0.48384 | 0.39505 | 0.13947 | 0.24404 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | 0.016871 | 0.042605 | 0.10955 | 0.1226 | 0.066579 | 0.079626
5423.75 | 121.312 | -0.3891 | 120.7764 | 0.12185 | -0.00389 | -0.021157 | -0.006703 | 0.008797 | 0.076426 | -0.012357 | 0.093694 | 0.19369 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 0.51095 | 0.38521 | 0.36794 | 0.3824 | 0.3979 | 0.46552 | 0.37674 | 0.13489 | 0.23489 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.1004 | 0.12718 | 0.062 | 0.088782
5425.5156 | 121.3531 | -0.37079 | 120.7855 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 0.093694 | 0.19827 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 0.49264 | 0.37606 | 0.35421 | 0.36409 | 0.37501 | 0.45179 | 0.35843 | 0.13489 | 0.23946 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.062 | 0.088782
5427.2812 | 121.2479 | -0.4303 | 120.8405 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.089116 | 0.19369 | 0.059877 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.55673 | 0.43099 | 0.4183 | 0.42817 | 0.4391 | 0.50672 | 0.42252 | 0.13032 | 0.23489 | 0.10108 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5429.0312 | 121.3028 | -0.42114 | 120.8633 | 0.12643 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.071848 | -0.012357 | 0.093694 | 0.19827 | 0.059877 | -0.023943 | -0.015859 | 0.027798 | -0.042641 | -0.003172 | 0.54757 | 0.42183 | 0.40457 | 0.41902 | 0.42078 | 0.49299 | 0.40879 | 0.13489 | 0.23946 | 0.10108 | 0.017256 | 0.02534 | 0.068997 | -0.001442 | 0.038027 | 0.10955 | 0.13633 | 0.075736 | 0.10252
5430.7344 | 121.3348 | -0.4303 | 120.8817 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.093694 | 0.19369 | 0.064455 | -0.019364 | -0.002124 | 0.041532 | -0.033484 | -0.00775 | 0.55215 | 0.43099 | 0.40914 | 0.42817 | 0.4391 | 0.5113 | 0.41794 | 0.13489 | 0.23489 | 0.10565 | 0.021835 | 0.039075 | 0.082731 | 0.007715 | 0.033449 | 0.095818 | 0.12718 | 0.066579 | 0.097939
5432.4844 | 121.344 | -0.42572 | 120.8908 | 0.11727 | 0.005267 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 0.098273 | 0.18911 | 0.059877 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 0.54299 | 0.43099 | 0.40914 | 0.41902 | 0.43452 | 0.50672 | 0.41794 | 0.13947 | 0.23031 | 0.10108 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.10497 | 0.13176 | 0.066579 | 0.093361
5434.1875 | 121.4035 | -0.39825 | 120.8862 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.098273 | 0.19827 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 0.52011 | 0.39894 | 0.38168 | 0.39155 | 0.40705 | 0.47468 | 0.39048 | 0.13947 | 0.23946 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.13634 | 0.057422 | 0.088783
5435.9531 | 121.4035 | -0.44403 | 120.8633 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 0.098273 | 0.19369 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 0.56588 | 0.44472 | 0.42745 | 0.43733 | 0.45283 | 0.52504 | 0.43625 | 0.13947 | 0.23489 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 0.10497 | 0.13634 | 0.062 | 0.093361
5437.7188 | 121.3852 | -0.44403 | 120.9366 | 0.12185 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 0.093694 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 0.56588 | 0.44014 | 0.42745 | 0.43733 | 0.45283 | 0.52961 | 0.43625 | 0.13489 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.1004 | 0.13176 | 0.062 | 0.093361
5439.4062 | 121.4172 | -0.43945 | 120.9412 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.089116 | 0.19369 | 0.055298 | -0.019364 | -0.002124 | 0.032376 | -0.038063 | -0.012328 | 0.55673 | 0.44014 | 0.42288 | 0.43275 | 0.43909 | 0.52046 | 0.43167 | 0.13032 | 0.23489 | 0.096497 | 0.021835 | 0.039075 | 0.073575 | 0.003136 | 0.028871 | 0.09124 | 0.12718 | 0.057422 | 0.093361
5441.1719 | 121.4539 | -0.41199 | 120.9457 | 0.12643 | -0.00389 | -0.016578 | -0.011281 | 0.004219 | 0.081005 | -0.012357 | 0.093694 | 0.19369 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.53842 | 0.4081 | 0.39541 | 0.40071 | 0.41621 | 0.49299 | 0.39963 | 0.13489 | 0.23489 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.062 | 0.088782
5442.9375 | 121.3989 | -0.44861 | 120.9686 | 0.11727 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.093694 | 0.19827 | 0.055298 | -0.014785 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 0.56588 | 0.4493 | 0.43661 | 0.44648 | 0.46198 | 0.52961 | 0.44083 | 0.13489 | 0.23946 | 0.096497 | 0.026414 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.062 | 0.088782
5444.7188 | 121.4264 | -0.45776 | 120.9732 | 0.11727 | -0.00389 | -0.012 | -0.011281 | 0.004219 | 0.081005 | -0.016936 | 0.098273 | 0.19369 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 0.57504 | 0.45387 | 0.44576 | 0.44648 | 0.46198 | 0.53877 | 0.44083 | 0.13947 | 0.23489 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 0.10497 | 0.13634 | 0.062 | 0.093361
5446.4844 | 121.5546 | -0.40283 | 120.9549 | 0.11727 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.016936 | 0.089116 | 0.18911 | 0.059877 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 0.52011 | 0.39894 | 0.39083 | 0.40071 | 0.40705 | 0.48384 | 0.3859 | 0.13032 | 0.23031 | 0.10108 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5448.1875 | 120.5429 | -119.2291 | 0.86517 | 0.13101 | 0.005267 | -0.007421 | 0.002454 | 0.004219 | 0.090161 | -0.007779 | 0.098273 | 0.20284 | 0.064455 | -0.010206 | -0.002124 | 0.027798 | -0.038063 | -0.003172 | 119.3601 | 119.2344 | 119.2217 | 119.2316 | 119.2333 | 119.3193 | 119.2213 | 0.13947 | 0.24404 | 0.10565 | 0.030993 | 0.039075 | 0.068997 | 0.003136 | 0.038027 | 0.1004 | 0.13634 | 0.066579 | 0.10252
5449.8906 | 121.0876 | -120.1447 | 0.72784 | 0.12643 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 0.098273 | 0.19827 | 0.059877 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.016906 | 120.2711 | 120.1499 | 120.1372 | 120.1471 | 120.1535 | 120.2302 | 120.1369 | 0.13947 | 0.23946 | 0.10108 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.024293 | 0.10955 | 0.13634 | 0.071158 | 0.09794
5451.6406 | 121.1792 | -120.369 | 0.6546 | 0.12643 | 0.005267 | 0.001736 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.10743 | 0.19369 | 0.059877 | -0.023943 | -0.020437 | 0.027798 | -0.038063 | -0.00775 | 120.4954 | 120.3742 | 120.3707 | 120.3668 | 120.3778 | 120.45 | 120.3612 | 0.14863 | 0.23489 | 0.10108 | 0.017256 | 0.020762 | 0.068997 | 0.003136 | 0.033449 | 0.12787 | 0.14549 | 0.080314 | 0.09794
5453.4062 | 121.3577 | -120.4102 | 0.6134 | 0.12643 | -0.00389 | -0.007421 | -0.011281 | 0.004219 | 0.081005 | -0.007779 | 0.098273 | 0.20284 | 0.064455 | -0.023943 | -0.011281 | 0.02322 | -0.042641 | -0.003172 | 120.5366 | 120.4063 | 120.4027 | 120.3989 | 120.4144 | 120.4912 | 120.4024 | 0.13947 | 0.24404 | 0.10565 | 0.017256 | 0.029918 | 0.064419 | -0.001442 | 0.038027 | 0.10955 | 0.14091 | 0.075736 | 0.1071
5455.1875 | 121.3806 | -120.1218 | 0.9613 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.090161 | -0.007779 | 0.098273 | 0.20284 | 0.059877 | -0.010206 | -0.006702 | 0.02322 | -0.028906 | -0.00775 | 120.2436 | 120.127 | 120.1143 | 120.1242 | 120.1306 | 120.2119 | 120.114 | 0.13947 | 0.24404 | 0.10108 | 0.030993 | 0.034497 | 0.064419 | 0.012293 | 0.033449 | 0.10497 | 0.12718 | 0.066579 | 0.088783
5456.8906 | 121.2982 | -120.1035 | 1.0574 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.013375 | 0.085583 | -0.003201 | 0.10285 | 0.20742 | 0.059877 | -0.014785 | -0.011281 | 0.027798 | -0.033484 | -0.012328 | 120.2299 | 120.1041 | 120.0915 | 120.1059 | 120.1168 | 120.189 | 120.1003 | 0.14405 | 0.24862 | 0.10108 | 0.026414 | 0.029918 | 0.068997 | 0.007715 | 0.028871 | 0.11413 | 0.13633 | 0.071158 | 0.093361
5458.6406 | 121.4447 | -120.4834 | 0.66834 | 0.12185 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.098273 | 0.20284 | 0.069033 | -0.023943 | -0.002124 | 0.02322 | -0.033484 | -0.00775 | 120.6052 | 120.4932 | 120.476 | 120.4859 | 120.4922 | 120.5644 | 120.4802 | 0.13947 | 0.24404 | 0.11023 | 0.017256 | 0.039075 | 0.064419 | 0.007715 | 0.033449 | 0.1004 | 0.13176 | 0.071157 | 0.10252
5460.3438 | 121.3852 | -120.5658 | 0.69122 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 0.093694 | 0.18911 | 0.05072 | -0.014785 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 120.6876 | 120.5711 | 120.5492 | 120.5591 | 120.5746 | 120.6514 | 120.558 | 0.13489 | 0.23031 | 0.091919 | 0.026414 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 0.10497 | 0.1226 | 0.062001 | 0.079626
5462.125 | 121.4676 | -120.5429 | 0.66376 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.093694 | 0.19827 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 120.6693 | 120.5482 | 120.5355 | 120.5408 | 120.5563 | 120.6239 | 120.5397 | 0.13489 | 0.23946 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.062 | 0.088782
5463.8281 | 121.4081 | -120.5338 | 0.737 | 0.12185 | 0.005267 | -0.007421 | 0.007033 | 0.013375 | 0.085583 | -0.003201 | 0.089116 | 0.19827 | 0.069033 | -0.014785 | -0.011281 | 0.02322 | -0.033484 | -0.00775 | 120.6556 | 120.539 | 120.5263 | 120.5408 | 120.5471 | 120.6193 | 120.5306 | 0.13032 | 0.23946 | 0.11023 | 0.026414 | 0.029918 | 0.064419 | 0.007715 | 0.033449 | 0.1004 | 0.1226 | 0.080314 | 0.10252
5465.5938 | 121.5271 | -120.6116 | 0.61798 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 0.089116 | 0.19827 | 0.059877 | -0.019364 | -0.011281 | 0.027798 | -0.042641 | -0.012328 | 120.7334 | 120.6168 | 120.5996 | 120.6049 | 120.6204 | 120.6926 | 120.6038 | 0.13032 | 0.23946 | 0.10108 | 0.021835 | 0.029918 | 0.068997 | -0.001442 | 0.028871 | 0.1004 | 0.13176 | 0.071158 | 0.10252
5467.2969 | 121.4722 | -120.6345 | 0.65002 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.093694 | 0.19369 | 0.064455 | -0.014785 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 120.7609 | 120.6397 | 120.627 | 120.6323 | 120.6433 | 120.7109 | 120.6267 | 0.13489 | 0.23489 | 0.10565 | 0.026414 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.071157 | 0.097939
5469.0625 | 120.9915 | -102.8915 | 17.5964 | 0.12643 | 0.005267 | -0.012 | -0.002124 | -0.000359 | 0.081005 | -0.007779 | 0.098273 | 0.19827 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 103.018 | 102.8968 | 102.8795 | 102.8894 | 102.8912 | 102.9725 | 102.8838 | 0.13947 | 0.23946 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.10497 | 0.13634 | 0.062 | 0.093361
5470.8281 | 121.2891 | -105.1987 | 15.7516 | 0.13101 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.093694 | 0.19827 | 0.069033 | -0.014785 | -0.006702 | 0.032376 | -0.042641 | -0.012328 | 105.3297 | 105.1994 | 105.1867 | 105.1965 | 105.2075 | 105.2797 | 105.1955 | 0.13489 | 0.23946 | 0.11023 | 0.026414 | 0.034497 | 0.073575 | -0.001442 | 0.028871 | 0.1004 | 0.13633 | 0.075735 | 0.11167
5472.5938 | 121.3943 | -104.6906 | 16.3239 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.016936 | 0.093694 | 0.19369 | 0.064455 | -0.014785 | -0.011281 | 0.032376 | -0.042641 | -0.003172 | 104.8124 | 104.6958 | 104.6831 | 104.693 | 104.6993 | 104.7716 | 104.6736 | 0.13489 | 0.23489 | 0.10565 | 0.026414 | 0.029918 | 0.073575 | -0.001442 | 0.038027 | 0.10497 | 0.13633 | 0.075736 | 0.1071
5474.3594 | 121.4813 | -104.1275 | 16.9373 | 0.11727 | 0.000689 | -0.012 | 0.002454 | -0.000359 | 0.081005 | -0.012357 | 0.098273 | 0.19369 | 0.059877 | -0.023943 | -0.020437 | 0.027798 | -0.038063 | -0.003172 | 104.2448 | 104.1282 | 104.1155 | 104.13 | 104.1271 | 104.2085 | 104.1151 | 0.13947 | 0.23489 | 0.10108 | 0.017256 | 0.020762 | 0.068997 | 0.003136 | 0.038027 | 0.11871 | 0.13634 | 0.080314 | 0.09794
5476.125 | 121.4035 | -104.6173 | 16.571 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.093694 | 0.19827 | 0.064455 | -0.019364 | -0.006702 | 0.02322 | -0.033484 | -0.00775 | 104.7437 | 104.6226 | 104.6099 | 104.6152 | 104.6261 | 104.6983 | 104.6095 | 0.13489 | 0.23946 | 0.10565 | 0.021835 | 0.034497 | 0.064419 | 0.007715 | 0.033449 | 0.1004 | 0.12718 | 0.071157 | 0.097939
5477.8438 | 121.5225 | -105.0659 | 16.0629 | 0.12643 | 0.009846 | -0.007421 | 0.007033 | 0.004219 | 0.085583 | -0.007779 | 0.089116 | 0.20284 | 0.064455 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 105.1923 | 105.0758 | 105.0585 | 105.073 | 105.0701 | 105.1515 | 105.0581 | 0.13032 | 0.24404 | 0.10565 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.1004 | 0.12718 | 0.075736 | 0.10252
5479.6094 | 121.5637 | -105.5923 | 15.6006 | 0.12643 | -0.00389 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.098273 | 0.19369 | 0.059877 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 105.7188 | 105.5885 | 105.5803 | 105.5856 | 105.592 | 105.6734 | 105.5846 | 0.13947 | 0.23489 | 0.10108 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.10955 | 0.13176 | 0.071158 | 0.093361
5481.375 | 121.463 | -104.9561 | 16.3055 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.089116 | 0.19827 | 0.055298 | -0.014785 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 105.0779 | 104.9659 | 104.9395 | 104.9585 | 104.9649 | 105.0371 | 104.9483 | 0.13032 | 0.23946 | 0.096497 | 0.026414 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.095818 | 0.12718 | 0.062 | 0.093361
5483.1562 | 121.582 | -104.1 | 17.1249 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.004219 | 0.090161 | -0.007779 | 0.093694 | 0.19369 | 0.059877 | -0.019364 | -0.011281 | 0.032376 | -0.042641 | -0.003172 | 104.2265 | 104.1053 | 104.0926 | 104.0979 | 104.1043 | 104.1902 | 104.0923 | 0.13489 | 0.23489 | 0.10108 | 0.021835 | 0.029918 | 0.073575 | -0.001442 | 0.038027 | 0.10497 | 0.13633 | 0.071158 | 0.10252
5484.8594 | 121.55 | -102.626 | 18.5852 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.016936 | 0.089116 | 0.18911 | 0.064455 | -0.023943 | -0.011281 | 0.02322 | -0.028906 | -0.012328 | 102.7479 | 102.6313 | 102.6095 | 102.6239 | 102.6348 | 102.707 | 102.6091 | 0.13032 | 0.23031 | 0.10565 | 0.017256 | 0.029918 | 0.064419 | 0.012293 | 0.028871 | 0.1004 | 0.11802 | 0.075736 | 0.093361
5486.625 | 121.2021 | -16.9327 | 104.5166 | 0.12185 | 0.005267 | -0.016578 | -0.011281 | 0.013375 | 0.081005 | -0.012357 | 0.093694 | 0.19827 | 0.064455 | -0.019364 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 17.0545 | 16.9379 | 16.9161 | 16.9214 | 16.9461 | 17.0137 | 16.9203 | 0.13489 | 0.23946 | 0.10565 | 0.021835 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 0.10497 | 0.12718 | 0.075736 | 0.097939
5488.3906 | 120.9183 | -10.6064 | 110.8383 | 0.13101 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.016936 | 0.084537 | 0.18911 | 0.059877 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 10.7374 | 10.6071 | 10.599 | 10.6043 | 10.6152 | 10.6828 | 10.5894 | 0.12574 | 0.23031 | 0.10108 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.066579 | 0.093361
5490.1562 | 121.3394 | -9.4849 | 111.9278 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.19369 | 0.059877 | -0.010206 | -0.011281 | 0.027798 | -0.033484 | -0.012328 | 9.6021 | 9.4856 | 9.4683 | 9.4827 | 9.4891 | 9.5613 | 9.4771 | 0.12574 | 0.23489 | 0.10108 | 0.030993 | 0.029918 | 0.068997 | 0.007715 | 0.028871 | 0.095818 | 0.11802 | 0.071158 | 0.093361
5491.8594 | 121.4996 | -9.0775 | 112.3718 | 0.12643 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.089116 | 0.18911 | 0.055298 | -0.019364 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 9.2039 | 9.0781 | 9.0609 | 9.0753 | 9.0817 | 9.1585 | 9.0651 | 0.13032 | 0.23031 | 0.096497 | 0.021835 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.1004 | 0.1226 | 0.066579 | 0.088782
5493.6094 | 121.4722 | -8.7891 | 112.6785 | 0.12643 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.076426 | -0.012357 | 0.084537 | 0.19369 | 0.059877 | -0.023943 | -0.015859 | 0.02322 | -0.038063 | -0.012328 | 8.9155 | 8.7943 | 8.7725 | 8.7824 | 8.7933 | 8.8655 | 8.7767 | 0.12574 | 0.23489 | 0.10108 | 0.017256 | 0.02534 | 0.064419 | 0.003136 | 0.028871 | 0.1004 | 0.1226 | 0.075736 | 0.09794
5495.3906 | 121.5958 | -9.4711 | 111.9598 | 0.13101 | 0.005267 | -0.016578 | -0.011281 | -0.000359 | 0.081005 | -0.021514 | 0.089116 | 0.19369 | 0.064455 | -0.028522 | -0.002124 | 0.032376 | -0.033484 | -0.003172 | 9.6021 | 9.4764 | 9.4546 | 9.4598 | 9.4708 | 9.5521 | 9.4496 | 0.13032 | 0.23489 | 0.10565 | 0.012677 | 0.039075 | 0.073575 | 0.007715 | 0.038027 | 0.09124 | 0.1226 | 0.066579 | 0.097939
5497.0938 | 121.5912 | -8.8028 | 112.619 | 0.13101 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.089116 | 0.20284 | 0.055298 | -0.019364 | -0.011281 | 0.036954 | -0.033484 | 0.001406 | 8.9338 | 8.8035 | 8.7862 | 8.7961 | 8.8116 | 8.8838 | 8.7904 | 0.13032 | 0.24404 | 0.096497 | 0.021835 | 0.029918 | 0.078153 | 0.007715 | 0.042605 | 0.1004 | 0.1226 | 0.066579 | 0.088782
5498.8594 | 121.582 | -8.67 | 112.793 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.016936 | 0.089116 | 0.18911 | 0.05072 | -0.028522 | -0.006702 | 0.027798 | -0.028906 | -0.012328 | 8.7965 | 8.6753 | 8.658 | 8.6725 | 8.6788 | 8.7419 | 8.6531 | 0.13032 | 0.23031 | 0.091919 | 0.012677 | 0.034497 | 0.068997 | 0.012293 | 0.028871 | 0.095818 | 0.11802 | 0.057422 | 0.079626
5500.625 | 121.6507 | -8.4274 | 113.0127 | 0.11269 | 0.009846 | -0.012 | -0.002124 | 0.004219 | 0.071848 | -0.007779 | 0.093694 | 0.19369 | 0.055298 | -0.028522 | -0.006702 | 0.032376 | -0.042641 | -0.003172 | 8.5401 | 8.4373 | 8.4154 | 8.4253 | 8.4316 | 8.4993 | 8.4197 | 0.13489 | 0.23489 | 0.096497 | 0.012677 | 0.034497 | 0.073575 | -0.001442 | 0.038027 | 0.1004 | 0.13633 | 0.062 | 0.097939
5502.3906 | 121.6324 | -8.4503 | 112.999 | 0.12185 | 0.005267 | -0.012 | -0.002124 | -0.000359 | 0.071848 | -0.016936 | 0.093694 | 0.18911 | 0.059877 | -0.023943 | -0.011281 | 0.036954 | -0.038063 | -0.003172 | 8.5722 | 8.4556 | 8.4383 | 8.4482 | 8.45 | 8.5222 | 8.4334 | 0.13489 | 0.23031 | 0.10108 | 0.017256 | 0.029918 | 0.078153 | 0.003136 | 0.038027 | 0.10497 | 0.13176 | 0.071158 | 0.09794
5504.1562 | 121.582 | -8.1894 | 113.3469 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.089116 | 0.19369 | 0.059877 | -0.019364 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 8.3112 | 8.1901 | 8.1728 | 8.1873 | 8.1936 | 8.2658 | 8.177 | 0.13032 | 0.23489 | 0.10108 | 0.021835 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 0.1004 | 0.11802 | 0.071158 | 0.088783
5505.8594 | 121.7056 | -8.1345 | 113.3194 | 0.11269 | 0.000689 | -0.021157 | -0.006703 | 0.013375 | 0.081005 | -0.007779 | 0.093694 | 0.19369 | 0.059877 | -0.023943 | -0.006702 | 0.02322 | -0.038063 | 0.001406 | 8.2472 | 8.1351 | 8.1133 | 8.1278 | 8.1478 | 8.2155 | 8.1267 | 0.13489 | 0.23489 | 0.10108 | 0.017256 | 0.034497 | 0.064419 | 0.003136 | 0.042605 | 0.1004 | 0.13176 | 0.066579 | 0.09794
5507.625 | 121.5958 | -7.9376 | 113.5849 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.089116 | 0.19827 | 0.059877 | -0.014785 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 8.0595 | 7.9383 | 7.9256 | 7.9355 | 7.9418 | 8.014 | 7.9298 | 0.13032 | 0.23946 | 0.10108 | 0.026414 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.095818 | 0.12718 | 0.066579 | 0.09794
5509.3281 | 121.6095 | -7.8049 | 113.7497 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.012357 | 0.084537 | 0.18911 | 0.059877 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 7.9267 | 7.8101 | 7.7883 | 7.8027 | 7.8137 | 7.8813 | 7.7925 | 0.12574 | 0.23031 | 0.10108 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.091239 | 0.11802 | 0.066579 | 0.093361
5511.1094 | 121.6003 | -7.7408 | 113.8687 | 0.10812 | 0.005267 | -0.016578 | -0.006703 | -0.004937 | 0.081005 | -0.012357 | 0.084537 | 0.18911 | 0.046142 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 7.8489 | 7.7461 | 7.7242 | 7.7341 | 7.7358 | 7.8218 | 7.7284 | 0.12574 | 0.23031 | 0.087341 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.091239 | 0.11802 | 0.052844 | 0.079626
5512.8125 | 121.7514 | -7.6859 | 113.7955 | 0.13101 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.021514 | 0.089116 | 0.19369 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 7.8169 | 7.6865 | 7.6693 | 7.6837 | 7.6901 | 7.7623 | 7.6643 | 0.13032 | 0.23489 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.1004 | 0.12718 | 0.062001 | 0.088783
5514.5781 | 121.6324 | -7.5943 | 114.0335 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.089116 | 0.18911 | 0.05072 | -0.010206 | -0.006702 | 0.02322 | -0.028906 | 0.001406 | 7.7162 | 7.595 | 7.5777 | 7.5922 | 7.6031 | 7.6753 | 7.5819 | 0.13032 | 0.23031 | 0.091919 | 0.030993 | 0.034497 | 0.064419 | 0.012293 | 0.042605 | 0.095818 | 0.11802 | 0.057422 | 0.079626
5516.3438 | 121.637 | -7.4799 | 114.1113 | 0.11727 | -0.00389 | -0.012 | -0.006703 | -0.000359 | 0.076426 | -0.012357 | 0.093694 | 0.19369 | 0.046142 | -0.023943 | -0.011281 | 0.032376 | -0.042641 | -0.003172 | 7.5971 | 7.476 | 7.4679 | 7.4732 | 7.4795 | 7.5563 | 7.4675 | 0.13489 | 0.23489 | 0.087341 | 0.017256 | 0.029918 | 0.073575 | -0.001442 | 0.038027 | 0.10497 | 0.13633 | 0.057423 | 0.088783
5518.1094 | 121.6965 | -7.4158 | 114.1251 | 0.11727 | 0.009846 | -0.007421 | -0.006703 | 0.004219 | 0.076426 | -0.016936 | 0.084537 | 0.18453 | 0.055298 | -0.014785 | -0.002124 | 0.036954 | -0.028906 | -0.003172 | 7.533 | 7.4256 | 7.4084 | 7.4091 | 7.42 | 7.4922 | 7.3988 | 0.12574 | 0.22573 | 0.096497 | 0.026414 | 0.039075 | 0.078153 | 0.012293 | 0.038027 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5519.875 | 121.6919 | -7.3975 | 114.2075 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | -0.000359 | 0.076426 | -0.012357 | 0.089116 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 7.5193 | 7.4027 | 7.3809 | 7.3908 | 7.3971 | 7.4739 | 7.3851 | 0.13032 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.095818 | 0.1226 | 0.057422 | 0.084204
5521.6562 | 121.0968 | -5.0446 | 115.9241 | 0.12185 | 0.009846 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.016936 | 0.089116 | 0.19369 | 0.059877 | -0.023943 | -0.006702 | 0.02322 | -0.033484 | -0.003172 | 5.1664 | 5.0544 | 5.028 | 5.0424 | 5.0442 | 5.121 | 5.0276 | 0.13032 | 0.23489 | 0.10108 | 0.017256 | 0.034497 | 0.064419 | 0.007715 | 0.038027 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5523.4219 | 121.3486 | -3.772 | 117.4118 | 0.12185 | 0.009846 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.089116 | 0.18911 | 0.055298 | -0.019364 | -0.002124 | 0.036954 | -0.033484 | 0.001406 | 3.8938 | 3.7818 | 3.76 | 3.7698 | 3.7762 | 3.8484 | 3.7642 | 0.13032 | 0.23031 | 0.096497 | 0.021835 | 0.039075 | 0.078153 | 0.007715 | 0.042605 | 0.09124 | 0.1226 | 0.057422 | 0.088782
5525.1875 | 121.3577 | -3.7537 | 117.5858 | 0.12185 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.067269 | -0.012357 | 0.098273 | 0.18911 | 0.059877 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 3.8755 | 3.7544 | 3.7371 | 3.7561 | 3.7625 | 3.8209 | 3.7413 | 0.13947 | 0.23031 | 0.10108 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.10955 | 0.13176 | 0.071158 | 0.093361
5526.9531 | 121.4584 | -4.2709 | 117.0731 | 0.12643 | 0.005267 | -0.016578 | -0.006703 | -0.000359 | 0.076426 | -0.007779 | 0.089116 | 0.19369 | 0.05072 | -0.028522 | -0.006702 | 0.02322 | -0.038063 | -0.00775 | 4.3974 | 4.2762 | 4.2544 | 4.2642 | 4.2706 | 4.3474 | 4.2632 | 0.13032 | 0.23489 | 0.091919 | 0.012677 | 0.034497 | 0.064419 | 0.003136 | 0.033449 | 0.095818 | 0.12718 | 0.057422 | 0.088783
5528.6562 | 121.4035 | -4.0237 | 117.4393 | 0.11727 | 0.005267 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.089116 | 0.19369 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.012328 | 4.141 | 4.029 | 4.0117 | 4.017 | 4.028 | 4.1002 | 4.016 | 0.13032 | 0.23489 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.028871 | 0.1004 | 0.1226 | 0.066579 | 0.088782
5530.4062 | 121.5454 | -3.7949 | 117.5949 | 0.12643 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.19369 | 0.059877 | -0.033101 | -0.002124 | 0.032376 | -0.028906 | -0.003172 | 3.9213 | 3.8001 | 3.7783 | 3.7882 | 3.7991 | 3.8713 | 3.7871 | 0.12574 | 0.23489 | 0.10108 | 0.008098 | 0.039075 | 0.073575 | 0.012293 | 0.038027 | 0.086661 | 0.11344 | 0.062001 | 0.088783
5532.1719 | 121.6278 | -3.392 | 118.0161 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.004219 | 0.085583 | -0.012357 | 0.089116 | 0.19369 | 0.059877 | -0.019364 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 3.5139 | 3.3973 | 3.38 | 3.3853 | 3.3962 | 3.4776 | 3.3797 | 0.13032 | 0.23489 | 0.10108 | 0.021835 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 0.1004 | 0.11802 | 0.071158 | 0.088783
5533.9375 | 121.5454 | -3.3829 | 118.1213 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.18911 | 0.059877 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 3.5001 | 3.3836 | 3.3663 | 3.3853 | 3.3871 | 3.4593 | 3.3751 | 0.12574 | 0.23031 | 0.10108 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.095818 | 0.1226 | 0.071158 | 0.09794
5535.6875 | 121.5088 | -3.2913 | 118.2678 | 0.12643 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.089116 | 0.19369 | 0.059877 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | -0.00775 | 3.4177 | 3.292 | 3.2747 | 3.2892 | 3.2955 | 3.3723 | 3.2835 | 0.13032 | 0.23489 | 0.10108 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.033449 | 0.095818 | 0.12718 | 0.066579 | 0.09794
5537.3906 | 121.637 | -3.2364 | 118.277 | 0.12185 | 0.005267 | -0.021157 | -0.002124 | -0.004937 | 0.076426 | -0.012357 | 0.089116 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.036954 | -0.033484 | -0.00775 | 3.3582 | 3.2417 | 3.2152 | 3.2343 | 3.2315 | 3.3128 | 3.224 | 0.13032 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.078153 | 0.007715 | 0.033449 | 0.095818 | 0.1226 | 0.062 | 0.088782
5539.1562 | 121.5637 | -3.1952 | 118.3502 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.004219 | 0.076426 | -0.007779 | 0.089116 | 0.19369 | 0.055298 | -0.028522 | -0.002124 | 0.032376 | -0.033484 | -0.00775 | 3.317 | 3.2005 | 3.1832 | 3.1976 | 3.1994 | 3.2716 | 3.1874 | 0.13032 | 0.23489 | 0.096497 | 0.012677 | 0.039075 | 0.073575 | 0.007715 | 0.033449 | 0.09124 | 0.1226 | 0.057422 | 0.088782
5540.8594 | 121.7239 | -3.1448 | 118.3456 | 0.12185 | 0.000689 | -0.016578 | -0.011281 | 0.004219 | 0.076426 | -0.016936 | 0.089116 | 0.18911 | 0.055298 | -0.028522 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 3.2667 | 3.1455 | 3.1283 | 3.1336 | 3.1491 | 3.2213 | 3.1279 | 0.13032 | 0.23031 | 0.096497 | 0.012677 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.095818 | 0.1226 | 0.062 | 0.088782
5542.6562 | 121.6599 | -3.3646 | 118.19 | 0.12643 | 0.000689 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.007779 | 0.093694 | 0.18911 | 0.05072 | -0.019364 | -0.002124 | 0.036954 | -0.038063 | -0.003172 | 3.491 | 3.3653 | 3.348 | 3.3579 | 3.3688 | 3.4364 | 3.3568 | 0.13489 | 0.23031 | 0.091919 | 0.021835 | 0.039075 | 0.078153 | 0.003136 | 0.038027 | 0.095818 | 0.13176 | 0.052844 | 0.088783
5544.3594 | 121.6232 | -3.4012 | 118.2083 | 0.11269 | 0.009846 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.089116 | 0.19369 | 0.05072 | -0.014785 | -0.002124 | 0.041532 | -0.038063 | -0.003172 | 3.5139 | 3.411 | 3.3892 | 3.3991 | 3.41 | 3.4822 | 3.3888 | 0.13032 | 0.23489 | 0.091919 | 0.026414 | 0.039075 | 0.082731 | 0.003136 | 0.038027 | 0.09124 | 0.12718 | 0.052844 | 0.088783
5546.125 | 121.6415 | -3.392 | 118.2404 | 0.12185 | 0.000689 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.093694 | 0.19827 | 0.059877 | -0.019364 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 3.5139 | 3.3927 | 3.38 | 3.3853 | 3.3962 | 3.4685 | 3.3842 | 0.13489 | 0.23946 | 0.10108 | 0.021835 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.12718 | 0.071158 | 0.093361
5547.8906 | 121.6919 | -3.392 | 118.2312 | 0.12185 | 0.000689 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.089116 | 0.18911 | 0.059877 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.012328 | 3.5139 | 3.3927 | 3.38 | 3.3853 | 3.3962 | 3.4685 | 3.3842 | 0.13032 | 0.23031 | 0.10108 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.028871 | 0.09124 | 0.1226 | 0.062001 | 0.093361
5549.6406 | 121.6507 | -3.3966 | 118.2541 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.089116 | 0.19369 | 0.055298 | -0.028522 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 3.5139 | 3.3973 | 3.38 | 3.3945 | 3.4008 | 3.473 | 3.3842 | 0.13032 | 0.23489 | 0.096497 | 0.012677 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.095818 | 0.1226 | 0.062 | 0.088782
5551.4062 | 121.7926 | -3.3325 | 118.2587 | 0.11727 | -0.00389 | -0.016578 | -0.002124 | 0.004219 | 0.085583 | -0.012357 | 0.084537 | 0.18911 | 0.055298 | -0.023943 | -0.002124 | 0.027798 | -0.033484 | 0.001406 | 3.4498 | 3.3286 | 3.3159 | 3.3304 | 3.3367 | 3.4181 | 3.3202 | 0.12574 | 0.23031 | 0.096497 | 0.017256 | 0.039075 | 0.068997 | 0.007715 | 0.042605 | 0.086661 | 0.11802 | 0.057422 | 0.088782
5553.1875 | 121.6827 | -3.3737 | 118.2953 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.090161 | -0.012357 | 0.089116 | 0.18911 | 0.05072 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 3.4956 | 3.3744 | 3.3663 | 3.3716 | 3.3825 | 3.4639 | 3.3614 | 0.13032 | 0.23031 | 0.091919 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.095818 | 0.11802 | 0.057422 | 0.079626
5554.9531 | 121.7834 | -3.2135 | 118.364 | 0.11727 | 0.005267 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.084537 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 3.3308 | 3.2188 | 3.1969 | 3.216 | 3.2177 | 3.2945 | 3.2057 | 0.12574 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 0.091239 | 0.11802 | 0.057422 | 0.084204
5556.6562 | 121.6827 | -3.2547 | 118.4189 | 0.12185 | 0.005267 | -0.021157 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 0.089116 | 0.18911 | 0.046142 | -0.023943 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 3.3766 | 3.26 | 3.2335 | 3.248 | 3.2635 | 3.3403 | 3.2469 | 0.13032 | 0.23031 | 0.087341 | 0.017256 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.095818 | 0.12718 | 0.052844 | 0.084205
5558.4062 | 121.6599 | -3.1998 | 118.5059 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.089116 | 0.18911 | 0.046142 | -0.023943 | -0.002124 | 0.032376 | -0.028906 | -0.00775 | 3.3262 | 3.2005 | 3.1832 | 3.2022 | 3.204 | 3.2808 | 3.192 | 0.13032 | 0.23031 | 0.087341 | 0.017256 | 0.039075 | 0.073575 | 0.012293 | 0.033449 | 0.09124 | 0.11802 | 0.048266 | 0.075048
5560.1719 | 121.7422 | -3.1631 | 118.515 | 0.11727 | 0.005267 | -0.012 | 0.002454 | -0.000359 | 0.076426 | -0.007779 | 0.084537 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 3.2804 | 3.1684 | 3.1511 | 3.1656 | 3.1628 | 3.2396 | 3.1554 | 0.12574 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.095818 | 0.11802 | 0.062001 | 0.084204
5561.875 | 121.7194 | -3.1998 | 118.5287 | 0.12643 | 0.005267 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.089116 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.038063 | -0.00775 | 3.3262 | 3.205 | 3.1878 | 3.1931 | 3.1994 | 3.2808 | 3.192 | 0.13032 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.003136 | 0.033449 | 0.095818 | 0.12718 | 0.062 | 0.093361
5563.625 | 121.7056 | -3.1311 | 118.5791 | 0.12643 | -0.00389 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.016936 | 0.084537 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 3.2575 | 3.1272 | 3.1145 | 3.1336 | 3.1353 | 3.2121 | 3.1142 | 0.12574 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.095818 | 0.1226 | 0.062001 | 0.088783
5565.3438 | 121.8155 | -3.0991 | 118.5699 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.013375 | 0.076426 | -0.012357 | 0.084537 | 0.19369 | 0.059877 | -0.019364 | -0.002124 | 0.036954 | -0.038063 | -0.003172 | 3.2163 | 3.0997 | 3.0825 | 3.0969 | 3.1124 | 3.1755 | 3.0867 | 0.12574 | 0.23489 | 0.10108 | 0.021835 | 0.039075 | 0.078153 | 0.003136 | 0.038027 | 0.086661 | 0.1226 | 0.062001 | 0.09794
5567.1094 | 121.756 | -3.1128 | 118.6066 | 0.11727 | -0.00389 | -0.025735 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.084537 | 0.18453 | 0.055298 | -0.023943 | 0.002454 | 0.032376 | -0.033484 | -0.00775 | 3.2301 | 3.1089 | 3.0871 | 3.1061 | 3.1124 | 3.1938 | 3.105 | 0.12574 | 0.22573 | 0.096497 | 0.017256 | 0.043653 | 0.073575 | 0.007715 | 0.033449 | 0.082083 | 0.11802 | 0.052844 | 0.088782
5568.8594 | 121.7743 | -3.0991 | 118.6203 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.071848 | -0.012357 | 0.089116 | 0.19827 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 3.2209 | 3.0997 | 3.0871 | 3.0969 | 3.1033 | 3.1709 | 3.0867 | 0.13032 | 0.23946 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.095818 | 0.1226 | 0.062 | 0.088782
5570.625 | 121.788 | -3.1219 | 118.5928 | 0.11727 | 0.000689 | -0.016578 | -0.011281 | 0.004219 | 0.076426 | -0.016936 | 0.084537 | 0.19369 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.012328 | 3.2392 | 3.1226 | 3.1054 | 3.1107 | 3.1262 | 3.1984 | 3.105 | 0.12574 | 0.23489 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.028871 | 0.091239 | 0.1226 | 0.057422 | 0.088783
5572.3281 | 121.8842 | -3.1952 | 118.4738 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.016936 | 0.084537 | 0.18453 | 0.046142 | -0.023943 | -0.002124 | 0.027798 | -0.033484 | 0.001406 | 3.317 | 3.2005 | 3.1786 | 3.1885 | 3.1994 | 3.267 | 3.1783 | 0.12574 | 0.22573 | 0.087341 | 0.017256 | 0.039075 | 0.068997 | 0.007715 | 0.042605 | 0.086661 | 0.11802 | 0.048266 | 0.079626
5574.1094 | 121.8246 | -3.2272 | 118.4921 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.008797 | 0.071848 | -0.016936 | 0.079959 | 0.18911 | 0.046142 | -0.028522 | -0.006702 | 0.032376 | -0.028906 | -0.00775 | 3.3491 | 3.2325 | 3.2152 | 3.2205 | 3.236 | 3.2991 | 3.2103 | 0.12116 | 0.23031 | 0.087341 | 0.012677 | 0.034497 | 0.073575 | 0.012293 | 0.033449 | 0.086661 | 0.10887 | 0.052844 | 0.075048
5575.8125 | 121.7697 | -3.2318 | 118.5471 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.084537 | 0.18911 | 0.059877 | -0.028522 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 3.3537 | 3.2371 | 3.2198 | 3.2343 | 3.2406 | 3.3128 | 3.224 | 0.12574 | 0.23031 | 0.10108 | 0.012677 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 0.095818 | 0.11344 | 0.071158 | 0.088783
5577.5781 | 121.8567 | -3.1815 | 118.4921 | 0.10812 | 0.009846 | -0.012 | -0.006703 | -0.000359 | 0.076426 | -0.016936 | 0.089116 | 0.17995 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 3.2896 | 3.1913 | 3.1695 | 3.1748 | 3.1811 | 3.2579 | 3.1645 | 0.13032 | 0.22115 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.095818 | 0.1226 | 0.062 | 0.088782
5579.2812 | 121.8246 | -3.2043 | 118.5242 | 0.12185 | 0.005267 | -0.012 | -0.011281 | 0.004219 | 0.081005 | -0.012357 | 0.093694 | 0.18911 | 0.055298 | -0.028522 | -0.002124 | 0.032376 | -0.038063 | -0.003172 | 3.3262 | 3.2096 | 3.1923 | 3.1931 | 3.2086 | 3.2854 | 3.192 | 0.13489 | 0.23031 | 0.096497 | 0.012677 | 0.039075 | 0.073575 | 0.003136 | 0.038027 | 0.095818 | 0.13176 | 0.057422 | 0.093361
5581.0312 | 121.8979 | -3.1815 | 118.5379 | 0.11269 | 0.005267 | -0.016578 | -0.006703 | -0.004937 | 0.071848 | -0.016936 | 0.084537 | 0.18911 | 0.055298 | -0.023943 | -0.002124 | 0.027798 | -0.033484 | -0.00775 | 3.2942 | 3.1867 | 3.1649 | 3.1748 | 3.1765 | 3.2533 | 3.1645 | 0.12574 | 0.23031 | 0.096497 | 0.017256 | 0.039075 | 0.068997 | 0.007715 | 0.033449 | 0.086661 | 0.11802 | 0.057422 | 0.088782
5582.7969 | 121.843 | -3.2135 | 118.5471 | 0.11727 | 0.009846 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.084537 | 0.19369 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | -0.00775 | 3.3308 | 3.2233 | 3.2015 | 3.2114 | 3.2177 | 3.2945 | 3.2057 | 0.12574 | 0.23489 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.033449 | 0.091239 | 0.11344 | 0.057422 | 0.079626
5584.5625 | 121.8933 | -3.1952 | 118.5699 | 0.12185 | -0.008469 | -0.012 | -0.006703 | 0.004219 | 0.067269 | -0.012357 | 0.084537 | 0.18911 | 0.055298 | -0.028522 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 3.317 | 3.1867 | 3.1832 | 3.1885 | 3.1994 | 3.2625 | 3.1828 | 0.12574 | 0.23031 | 0.096497 | 0.012677 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5586.2656 | 121.8018 | -3.1952 | 118.5928 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.081005 | -0.012357 | 0.084537 | 0.18911 | 0.055298 | -0.023943 | -0.002124 | 0.032376 | -0.033484 | -0.00775 | 3.317 | 3.1959 | 3.1786 | 3.1931 | 3.1948 | 3.2762 | 3.1828 | 0.12574 | 0.23031 | 0.096497 | 0.017256 | 0.039075 | 0.073575 | 0.007715 | 0.033449 | 0.086661 | 0.11802 | 0.057422 | 0.088782
5588.0312 | 121.8521 | -3.2135 | 118.5837 | 0.11727 | -0.00389 | -0.016578 | -0.006703 | -0.000359 | 0.071848 | -0.007779 | 0.084537 | 0.18453 | 0.055298 | -0.023943 | -0.002124 | 0.032376 | -0.033484 | -0.003172 | 3.3308 | 3.2096 | 3.1969 | 3.2068 | 3.2131 | 3.2853 | 3.2057 | 0.12574 | 0.22573 | 0.096497 | 0.017256 | 0.039075 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11802 | 0.057422 | 0.088782
5589.7969 | 121.9437 | -3.1906 | 118.5379 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.089116 | 0.18453 | 0.05072 | -0.023943 | -0.002124 | 0.032376 | -0.028906 | -0.003172 | 3.3125 | 3.1913 | 3.174 | 3.1885 | 3.1948 | 3.2716 | 3.1783 | 0.13032 | 0.22573 | 0.091919 | 0.017256 | 0.039075 | 0.073575 | 0.012293 | 0.038027 | 0.09124 | 0.11802 | 0.052844 | 0.079626
5591.5 | 121.9208 | -3.2227 | 118.5425 | 0.12185 | -0.00389 | -0.016578 | -0.006703 | -0.004937 | 0.076426 | -0.012357 | 0.084537 | 0.18911 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 3.3445 | 3.2188 | 3.2061 | 3.216 | 3.2177 | 3.2991 | 3.2103 | 0.12574 | 0.23031 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.095818 | 0.1226 | 0.062001 | 0.088783
5593.2656 | 121.8567 | -3.273 | 118.5333 | 0.12185 | 0.005267 | -0.021157 | -0.011281 | 0.004219 | 0.081005 | -0.016936 | 0.089116 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 3.3949 | 3.2783 | 3.2519 | 3.2617 | 3.2772 | 3.354 | 3.2561 | 0.13032 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.1004 | 0.12718 | 0.062001 | 0.088783
5595.0312 | 121.9666 | -3.2684 | 118.4875 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.084537 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.012328 | 3.3857 | 3.2691 | 3.2519 | 3.2663 | 3.2772 | 3.3494 | 3.2561 | 0.12574 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.028871 | 0.091239 | 0.11802 | 0.057422 | 0.084204
5596.7812 | 121.8887 | -3.3875 | 118.4555 | 0.11269 | 0.014425 | -0.007421 | -0.006703 | -0.000359 | 0.071848 | -0.003201 | 0.089116 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 3.5001 | 3.4019 | 3.38 | 3.3807 | 3.3871 | 3.4593 | 3.3843 | 0.13032 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.1004 | 0.1226 | 0.066579 | 0.088782
5598.5469 | 121.8796 | -3.392 | 118.4555 | 0.12185 | 0.000689 | -0.012 | -0.002124 | -0.000359 | 0.081005 | -0.007779 | 0.093694 | 0.17995 | 0.055298 | -0.028522 | -0.015859 | 0.041532 | -0.038063 | -0.00775 | 3.5139 | 3.3927 | 3.38 | 3.3899 | 3.3917 | 3.473 | 3.3842 | 0.13489 | 0.22115 | 0.096497 | 0.012677 | 0.02534 | 0.082731 | 0.003136 | 0.033449 | 0.10955 | 0.13176 | 0.071157 | 0.093361
5600.3125 | 121.843 | -3.4058 | 118.4555 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.003201 | 0.089116 | 0.18911 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.024328 | -0.00775 | 3.5276 | 3.411 | 3.3892 | 3.4036 | 3.41 | 3.4822 | 3.4026 | 0.13032 | 0.23031 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.016871 | 0.033449 | 0.095818 | 0.11344 | 0.062 | 0.079626
5602.0156 | 121.8567 | -3.3829 | 118.483 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | -0.000359 | 0.071848 | -0.012357 | 0.084537 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.036954 | -0.028906 | -0.00775 | 3.5001 | 3.3836 | 3.3663 | 3.3853 | 3.3825 | 3.4547 | 3.3705 | 0.12574 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.078153 | 0.012293 | 0.033449 | 0.091239 | 0.11344 | 0.057422 | 0.079626
5603.7812 | 121.9437 | -3.3188 | 118.4509 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.084537 | 0.18911 | 0.055298 | -0.023943 | -0.006702 | 0.036954 | -0.028906 | 0.001406 | 3.4406 | 3.3195 | 3.3022 | 3.3167 | 3.323 | 3.3952 | 3.3064 | 0.12574 | 0.23031 | 0.096497 | 0.017256 | 0.034497 | 0.078153 | 0.012293 | 0.042605 | 0.091239 | 0.11344 | 0.062 | 0.084204
5605.4844 | 121.9986 | -3.3096 | 118.5013 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.071848 | -0.012357 | 0.079959 | 0.18453 | 0.055298 | -0.019364 | -0.011281 | 0.036954 | -0.033484 | -0.00775 | 3.4269 | 3.3103 | 3.2931 | 3.3121 | 3.3138 | 3.3815 | 3.2973 | 0.12116 | 0.22573 | 0.096497 | 0.021835 | 0.029918 | 0.078153 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5607.25 | 121.9208 | -3.3234 | 118.5196 | 0.12185 | 0.000689 | -0.012 | -0.011281 | 0.004219 | 0.076426 | -0.012357 | 0.084537 | 0.18453 | 0.059877 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 3.4452 | 3.3241 | 3.3114 | 3.3121 | 3.3276 | 3.3998 | 3.311 | 0.12574 | 0.22573 | 0.10108 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.095818 | 0.11802 | 0.071158 | 0.093361
5609.0156 | 122.0032 | -3.3051 | 118.5104 | 0.11727 | 0.009846 | -0.016578 | -0.002124 | 0.004219 | 0.071848 | -0.012357 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 3.4223 | 3.3149 | 3.2885 | 3.3029 | 3.3093 | 3.3769 | 3.2927 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5610.7188 | 122.0215 | -3.3005 | 118.5196 | 0.12185 | 0.005267 | -0.012 | -0.002124 | -0.004937 | 0.076426 | -0.003201 | 0.084537 | 0.18453 | 0.046142 | -0.028522 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 3.4223 | 3.3057 | 3.2885 | 3.2984 | 3.2955 | 3.3769 | 3.2973 | 0.12574 | 0.22573 | 0.087341 | 0.012677 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.052844 | 0.079626
5612.4844 | 121.9757 | -3.3508 | 118.4647 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.076426 | -0.012357 | 0.084537 | 0.19369 | 0.059877 | -0.023943 | -0.006702 | 0.036954 | -0.033484 | -0.00775 | 3.4773 | 3.3515 | 3.3388 | 3.3487 | 3.3642 | 3.4273 | 3.3385 | 0.12574 | 0.23489 | 0.10108 | 0.017256 | 0.034497 | 0.078153 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.066579 | 0.093361
5614.1875 | 121.962 | -3.4378 | 118.3823 | 0.11269 | 0.005267 | -0.021157 | -0.006703 | 0.008797 | 0.081005 | -0.016936 | 0.089116 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.032376 | -0.028906 | -0.00775 | 3.5505 | 3.4431 | 3.4166 | 3.4311 | 3.4466 | 3.5188 | 3.4209 | 0.13032 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.073575 | 0.012293 | 0.033449 | 0.1004 | 0.11802 | 0.062001 | 0.079626
5615.9531 | 121.9849 | -3.4195 | 118.4189 | 0.12185 | 0.005267 | -0.021157 | -0.002124 | 0.004219 | 0.081005 | 0.001377 | 0.084537 | 0.19369 | 0.059877 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 3.5413 | 3.4248 | 3.3983 | 3.4174 | 3.4237 | 3.5005 | 3.4209 | 0.12574 | 0.23489 | 0.10108 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.095818 | 0.11802 | 0.071158 | 0.093361
5617.6719 | 122.0581 | -3.479 | 118.3319 | 0.11727 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.002124 | 0.027798 | -0.028906 | 0.001406 | 3.5963 | 3.4751 | 3.467 | 3.4769 | 3.4832 | 3.56 | 3.4666 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.039075 | 0.068997 | 0.012293 | 0.042605 | 0.082083 | 0.10887 | 0.052844 | 0.079626
5619.4375 | 122.0535 | -3.479 | 118.3685 | 0.11727 | 0.000689 | -0.021157 | 0.002454 | 0.008797 | 0.071848 | -0.012357 | 0.079959 | 0.19369 | 0.05072 | -0.019364 | 0.002454 | 0.036954 | -0.033484 | 0.005985 | 3.5963 | 3.4797 | 3.4578 | 3.4815 | 3.4878 | 3.5509 | 3.4666 | 0.12116 | 0.23489 | 0.091919 | 0.021835 | 0.043653 | 0.078153 | 0.007715 | 0.047184 | 0.077505 | 0.11344 | 0.048266 | 0.084204
5621.1406 | 121.9437 | -3.4973 | 118.3914 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.016936 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 3.6237 | 3.498 | 3.4853 | 3.4952 | 3.5015 | 3.5783 | 3.4804 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5622.9062 | 121.9116 | -3.511 | 118.4235 | 0.10812 | -0.00389 | -0.007421 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.084537 | 0.18453 | 0.059877 | -0.019364 | -0.011281 | 0.02322 | -0.033484 | -0.003172 | 3.6192 | 3.5072 | 3.5036 | 3.5043 | 3.5198 | 3.5921 | 3.4987 | 0.12574 | 0.22573 | 0.10108 | 0.021835 | 0.029918 | 0.064419 | 0.007715 | 0.038027 | 0.095818 | 0.11802 | 0.071158 | 0.093361
5624.6719 | 121.9025 | -3.4744 | 118.428 | 0.11727 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.18453 | 0.05072 | -0.023943 | -0.020437 | 0.027798 | -0.033484 | -0.003172 | 3.5917 | 3.4751 | 3.4624 | 3.4723 | 3.4786 | 3.5509 | 3.4666 | 0.12574 | 0.22573 | 0.091919 | 0.017256 | 0.020762 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.11802 | 0.071157 | 0.084204
5626.4375 | 122.0764 | -3.4195 | 118.4235 | 0.12185 | 0.005267 | -0.021157 | -0.006703 | -0.000359 | 0.067269 | -0.007779 | 0.084537 | 0.17995 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 3.5413 | 3.4248 | 3.3983 | 3.4128 | 3.4191 | 3.4868 | 3.4117 | 0.12574 | 0.22115 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.091239 | 0.11344 | 0.062 | 0.084204
5628.1562 | 121.907 | -3.4744 | 118.4601 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.084537 | 0.18453 | 0.046142 | -0.014785 | -0.002124 | 0.036954 | -0.038063 | -0.003172 | 3.6009 | 3.4797 | 3.4624 | 3.4723 | 3.4786 | 3.5554 | 3.4621 | 0.12574 | 0.22573 | 0.087341 | 0.026414 | 0.039075 | 0.078153 | 0.003136 | 0.038027 | 0.086661 | 0.1226 | 0.048266 | 0.084205
5629.9219 | 122.0627 | -3.4195 | 118.4372 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | -0.000359 | 0.076426 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 3.5413 | 3.4248 | 3.4029 | 3.4128 | 3.4191 | 3.4959 | 3.4117 | 0.12116 | 0.23031 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 0.09124 | 0.10887 | 0.066579 | 0.084204
5631.625 | 121.9894 | -3.4378 | 118.4647 | 0.11727 | 0.000689 | -0.016578 | 0.007033 | 0.008797 | 0.071848 | -0.012357 | 0.07538 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 3.5551 | 3.4385 | 3.4212 | 3.4448 | 3.4466 | 3.5097 | 3.4254 | 0.11658 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.10886 | 0.066579 | 0.088782
5633.3906 | 122.0261 | -3.4149 | 118.4235 | 0.12185 | -0.00389 | -0.012 | -0.006703 | -0.004937 | 0.081005 | -0.012357 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.018642 | -0.038063 | -0.012328 | 3.5368 | 3.411 | 3.4029 | 3.4082 | 3.41 | 3.4959 | 3.4026 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.059841 | 0.003136 | 0.028871 | 0.086661 | 0.11802 | 0.057422 | 0.088783
5635.1562 | 122.0764 | -3.392 | 118.4326 | 0.11269 | 0.005267 | -0.016578 | 0.002454 | -0.000359 | 0.076426 | -0.012357 | 0.084537 | 0.17995 | 0.059877 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 3.5047 | 3.3973 | 3.3755 | 3.3945 | 3.3917 | 3.4685 | 3.3797 | 0.12574 | 0.22115 | 0.10108 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.091239 | 0.11802 | 0.066579 | 0.093361
5636.8594 | 121.9986 | -3.4653 | 118.4601 | 0.11727 | 0.005267 | -0.016578 | -0.002124 | -0.000359 | 0.071848 | -0.012357 | 0.084537 | 0.19369 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 3.5825 | 3.4705 | 3.4487 | 3.4631 | 3.4649 | 3.5371 | 3.4529 | 0.12574 | 0.23489 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.091239 | 0.11344 | 0.062 | 0.084204
5638.6406 | 121.9986 | -3.4515 | 118.4509 | 0.11727 | -0.00389 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | 0.001377 | 0.079959 | 0.19369 | 0.055298 | -0.023943 | -0.002124 | 0.02322 | -0.028906 | -0.003172 | 3.5688 | 3.4476 | 3.435 | 3.4448 | 3.4558 | 3.5325 | 3.4529 | 0.12116 | 0.23489 | 0.096497 | 0.017256 | 0.039075 | 0.064419 | 0.012293 | 0.038027 | 0.082083 | 0.10887 | 0.057422 | 0.084204
5640.4219 | 122.0535 | -3.4607 | 118.428 | 0.12185 | -0.008469 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.012357 | 0.084537 | 0.18453 | 0.055298 | -0.023943 | -0.002124 | 0.027798 | -0.028906 | -0.003172 | 3.5825 | 3.4522 | 3.4441 | 3.454 | 3.4649 | 3.5325 | 3.4483 | 0.12574 | 0.22573 | 0.096497 | 0.017256 | 0.039075 | 0.068997 | 0.012293 | 0.038027 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5642.1875 | 122.0901 | -3.4378 | 118.4555 | 0.11269 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.016936 | 0.084537 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 3.5505 | 3.4431 | 3.4212 | 3.4357 | 3.442 | 3.5142 | 3.4209 | 0.12574 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.095818 | 0.11802 | 0.066579 | 0.088782
5643.9062 | 122.0444 | -3.4424 | 118.4692 | 0.11269 | -0.008469 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.016936 | 0.079959 | 0.17995 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 3.5551 | 3.4339 | 3.4304 | 3.4403 | 3.4466 | 3.5188 | 3.4254 | 0.12116 | 0.22115 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 0.09124 | 0.10887 | 0.066579 | 0.084204
5645.6719 | 121.9757 | -3.4653 | 118.5059 | 0.12185 | 0.005267 | -0.012 | -0.002124 | -0.000359 | 0.076426 | -0.021514 | 0.084537 | 0.18453 | 0.05072 | -0.023943 | -0.015859 | 0.032376 | -0.028906 | 0.005985 | 3.5871 | 3.4705 | 3.4533 | 3.4631 | 3.4649 | 3.5417 | 3.4438 | 0.12574 | 0.22573 | 0.091919 | 0.017256 | 0.02534 | 0.073575 | 0.012293 | 0.047184 | 0.1004 | 0.11344 | 0.066579 | 0.079626
5647.4375 | 121.994 | -3.4561 | 118.483 | 0.11727 | 0.009846 | -0.016578 | 0.007033 | 0.008797 | 0.076426 | -0.003201 | 0.079959 | 0.18453 | 0.055298 | -0.014785 | 0.007032 | 0.036954 | -0.033484 | -0.003172 | 3.5734 | 3.466 | 3.4395 | 3.4631 | 3.4649 | 3.5325 | 3.4529 | 0.12116 | 0.22573 | 0.096497 | 0.026414 | 0.048231 | 0.078153 | 0.007715 | 0.038027 | 0.072927 | 0.11344 | 0.048266 | 0.088782
5649.1406 | 122.1039 | -3.4241 | 118.4555 | 0.11269 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.18453 | 0.055298 | -0.023943 | -0.002124 | 0.032376 | -0.028906 | -0.00775 | 3.5368 | 3.4293 | 3.4075 | 3.4174 | 3.4283 | 3.5005 | 3.4163 | 0.12574 | 0.22573 | 0.096497 | 0.017256 | 0.039075 | 0.073575 | 0.012293 | 0.033449 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5650.9062 | 122.0627 | -3.4149 | 118.4692 | 0.11727 | 0.000689 | -0.012 | -0.002124 | -0.000359 | 0.067269 | -0.012357 | 0.084537 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.038063 | -0.012328 | 3.5322 | 3.4156 | 3.4029 | 3.4128 | 3.4146 | 3.4822 | 3.4026 | 0.12574 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.003136 | 0.028871 | 0.091239 | 0.1226 | 0.057422 | 0.088783
5652.6094 | 121.9849 | -3.5065 | 118.5013 | 0.11269 | 0.005267 | -0.021157 | -0.006703 | 0.004219 | 0.076426 | -0.012357 | 0.084537 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 3.6192 | 3.5117 | 3.4853 | 3.4998 | 3.5107 | 3.5829 | 3.4941 | 0.12574 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.091239 | 0.1226 | 0.062 | 0.093361
5654.375 | 122.0901 | -3.4241 | 118.5287 | 0.11727 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.067269 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.023943 | -0.011281 | 0.02322 | -0.033484 | -0.00775 | 3.5413 | 3.4293 | 3.4075 | 3.4174 | 3.4283 | 3.4913 | 3.4163 | 0.12116 | 0.23031 | 0.096497 | 0.017256 | 0.029918 | 0.064419 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5656.125 | 122.0718 | -3.4149 | 118.5013 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.071848 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.014785 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 3.5322 | 3.4156 | 3.3983 | 3.4174 | 3.4191 | 3.4868 | 3.4071 | 0.12116 | 0.22115 | 0.096497 | 0.026414 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5657.8906 | 122.113 | -3.3875 | 118.5287 | 0.11727 | 0.014425 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.079959 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | 0.001406 | 3.5047 | 3.4019 | 3.3755 | 3.3853 | 3.3962 | 3.4639 | 3.3843 | 0.12116 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.042605 | 0.086661 | 0.11344 | 0.062 | 0.088782
5659.6562 | 121.9986 | -3.392 | 118.5883 | 0.11727 | -0.00389 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.084537 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 3.5093 | 3.3881 | 3.38 | 3.3853 | 3.3962 | 3.473 | 3.3842 | 0.12574 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 0.091239 | 0.11344 | 0.057422 | 0.079626
5661.3594 | 122.049 | -3.3875 | 118.5791 | 0.11727 | -0.00389 | -0.007421 | -0.002124 | 0.013375 | 0.076426 | -0.016936 | 0.084537 | 0.18911 | 0.046142 | -0.028522 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 3.5047 | 3.3836 | 3.38 | 3.3853 | 3.4008 | 3.4639 | 3.3705 | 0.12574 | 0.23031 | 0.087341 | 0.012677 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 0.091239 | 0.11802 | 0.052844 | 0.079626
5663.1406 | 122.1268 | -3.3325 | 118.5699 | 0.11727 | -0.00389 | -0.016578 | -0.011281 | 0.008797 | 0.081005 | -0.012357 | 0.089116 | 0.19369 | 0.055298 | -0.014785 | -0.002124 | 0.032376 | -0.033484 | 0.001406 | 3.4498 | 3.3286 | 3.3159 | 3.3212 | 3.3413 | 3.4135 | 3.3202 | 0.13032 | 0.23489 | 0.096497 | 0.026414 | 0.039075 | 0.073575 | 0.007715 | 0.042605 | 0.09124 | 0.1226 | 0.057422 | 0.088782
5664.9219 | 122.1634 | -3.3096 | 118.6111 | 0.11269 | -0.00389 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 0.084537 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.036954 | -0.033484 | -0.00775 | 3.4223 | 3.3057 | 3.2885 | 3.3029 | 3.3138 | 3.3906 | 3.2973 | 0.12574 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.078153 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.052844 | 0.079626
5666.6406 | 122.1588 | -3.3051 | 118.6386 | 0.12185 | 0.005267 | -0.021157 | -0.006703 | -0.000359 | 0.081005 | -0.016936 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | 0.002454 | 0.036954 | -0.028906 | -0.003172 | 3.4269 | 3.3103 | 3.2839 | 3.2984 | 3.3047 | 3.3861 | 3.2881 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.043653 | 0.078153 | 0.012293 | 0.038027 | 0.072926 | 0.10429 | 0.048266 | 0.079626
5668.4062 | 122.1359 | -3.2913 | 118.6478 | 0.12643 | -0.00389 | -0.007421 | -0.006703 | 0.008797 | 0.071848 | -0.016936 | 0.084537 | 0.17537 | 0.041563 | -0.023943 | -0.002124 | 0.036954 | -0.033484 | -0.003172 | 3.4177 | 3.2874 | 3.2839 | 3.2846 | 3.3001 | 3.3632 | 3.2744 | 0.12574 | 0.21657 | 0.082762 | 0.017256 | 0.039075 | 0.078153 | 0.007715 | 0.038027 | 0.086661 | 0.11802 | 0.043687 | 0.075047
5670.1719 | 122.0261 | -3.4103 | 118.6249 | 0.12185 | 0.005267 | -0.012 | -0.011281 | -0.000359 | 0.076426 | -0.012357 | 0.07538 | 0.18453 | 0.055298 | -0.028522 | -0.002124 | 0.036954 | -0.038063 | -0.00775 | 3.5322 | 3.4156 | 3.3983 | 3.3991 | 3.41 | 3.4868 | 3.398 | 0.11658 | 0.22573 | 0.096497 | 0.012677 | 0.039075 | 0.078153 | 0.003136 | 0.033449 | 0.077504 | 0.11344 | 0.057422 | 0.093361
5671.9219 | 122.0444 | -3.3463 | 118.6935 | 0.11727 | 0.000689 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.003201 | 0.084537 | 0.18911 | 0.041563 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 3.4635 | 3.3469 | 3.3251 | 3.3395 | 3.3505 | 3.4273 | 3.3431 | 0.12574 | 0.23031 | 0.082762 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.091239 | 0.11344 | 0.048265 | 0.070469
5673.625 | 122.081 | -3.3279 | 118.6386 | 0.11727 | -0.00389 | -0.012 | -0.002124 | -0.000359 | 0.071848 | -0.016936 | 0.079959 | 0.18911 | 0.055298 | -0.028522 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 3.4452 | 3.3241 | 3.3159 | 3.3258 | 3.3276 | 3.3998 | 3.311 | 0.12116 | 0.23031 | 0.096497 | 0.012677 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5675.3906 | 122.1588 | -3.3188 | 118.6478 | 0.11269 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.079959 | 0.19369 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.00775 | 3.4315 | 3.3195 | 3.3068 | 3.3167 | 3.323 | 3.3952 | 3.311 | 0.12116 | 0.23489 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.033449 | 0.086661 | 0.10887 | 0.062 | 0.084204
5677.1406 | 122.0444 | -3.2135 | 118.8217 | 0.12185 | -0.00389 | -0.007421 | 0.002454 | 0.004219 | 0.076426 | -0.012357 | 0.070802 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 3.3354 | 3.2096 | 3.2061 | 3.216 | 3.2177 | 3.2899 | 3.2011 | 0.112 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.077504 | 0.10887 | 0.057422 | 0.088783
5678.9062 | 122.1634 | -3.1677 | 118.7805 | 0.11727 | 0.000689 | -0.012 | -0.006703 | -0.000359 | 0.076426 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.019364 | 0.007032 | 0.027798 | -0.024328 | -0.003172 | 3.285 | 3.1684 | 3.1557 | 3.161 | 3.1674 | 3.2442 | 3.1599 | 0.12116 | 0.23031 | 0.096497 | 0.021835 | 0.048231 | 0.068997 | 0.016871 | 0.038027 | 0.072927 | 0.10429 | 0.048266 | 0.079626
5680.6719 | 122.081 | -3.2227 | 118.8034 | 0.12185 | 0.005267 | -0.012 | -0.006703 | -0.000359 | 0.081005 | -0.007779 | 0.084537 | 0.17537 | 0.055298 | -0.023943 | 0.002454 | 0.032376 | -0.038063 | -0.00775 | 3.3445 | 3.2279 | 3.2107 | 3.216 | 3.2223 | 3.3037 | 3.2149 | 0.12574 | 0.21657 | 0.096497 | 0.017256 | 0.043653 | 0.073575 | 0.003136 | 0.033449 | 0.082083 | 0.1226 | 0.052844 | 0.093361
5682.4375 | 122.1176 | -3.2043 | 118.7988 | 0.11269 | 0.000689 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.079959 | 0.18911 | 0.059877 | -0.028522 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 3.317 | 3.205 | 3.1969 | 3.2022 | 3.2086 | 3.2808 | 3.1966 | 0.12116 | 0.23031 | 0.10108 | 0.012677 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 0.086661 | 0.10887 | 0.066579 | 0.088783
5684.1562 | 122.0947 | -3.2318 | 118.8171 | 0.12185 | -0.00389 | -0.016578 | -0.006703 | -0.000359 | 0.076426 | -0.007779 | 0.079959 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 3.3537 | 3.2279 | 3.2152 | 3.2251 | 3.2315 | 3.3082 | 3.224 | 0.12116 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.062 | 0.088782
5685.9062 | 122.0993 | -3.2181 | 118.8263 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.003201 | 0.084537 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 3.3399 | 3.2233 | 3.2061 | 3.216 | 3.2223 | 3.2945 | 3.2149 | 0.12574 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 0.091239 | 0.11802 | 0.062 | 0.088782
5687.6719 | 122.1451 | -3.1906 | 118.8217 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | -0.000359 | 0.071848 | -0.012357 | 0.07538 | 0.18453 | 0.046142 | -0.023943 | -0.011281 | 0.032376 | -0.028906 | -0.003172 | 3.3125 | 3.1913 | 3.1695 | 3.1885 | 3.1903 | 3.2625 | 3.1783 | 0.11658 | 0.22573 | 0.087341 | 0.017256 | 0.029918 | 0.073575 | 0.012293 | 0.038027 | 0.086661 | 0.10429 | 0.057423 | 0.075048
5689.375 | 122.1222 | -3.1815 | 118.8309 | 0.11727 | 0.000689 | -0.021157 | -0.002124 | 0.008797 | 0.076426 | -0.016936 | 0.079959 | 0.18453 | 0.05072 | -0.028522 | 0.002454 | 0.027798 | -0.033484 | -0.00775 | 3.2987 | 3.1821 | 3.1603 | 3.1793 | 3.1903 | 3.2579 | 3.1645 | 0.12116 | 0.22573 | 0.091919 | 0.012677 | 0.043653 | 0.068997 | 0.007715 | 0.033449 | 0.077505 | 0.11344 | 0.048266 | 0.084204
5691.1406 | 122.1222 | -3.3005 | 118.7759 | 0.11269 | 0.005267 | -0.016578 | -0.006703 | 0.008797 | 0.071848 | -0.007779 | 0.07538 | 0.17537 | 0.046142 | -0.014785 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 3.4132 | 3.3057 | 3.2839 | 3.2938 | 3.3093 | 3.3723 | 3.2927 | 0.11658 | 0.21657 | 0.087341 | 0.026414 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.082082 | 0.11344 | 0.052844 | 0.084205
5692.8438 | 122.081 | -3.2867 | 118.7897 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.085583 | -0.007779 | 0.079959 | 0.17995 | 0.05072 | -0.019364 | -0.006702 | 0.027798 | -0.042641 | -0.003172 | 3.404 | 3.2874 | 3.2702 | 3.2846 | 3.2864 | 3.3723 | 3.279 | 0.12116 | 0.22115 | 0.091919 | 0.021835 | 0.034497 | 0.068997 | -0.001442 | 0.038027 | 0.086661 | 0.1226 | 0.057422 | 0.093361
5694.6094 | 122.1542 | -3.2272 | 118.7988 | 0.11269 | 0.000689 | -0.016578 | -0.006703 | 0.004219 | 0.071848 | -0.007779 | 0.084537 | 0.17995 | 0.05072 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 3.3399 | 3.2279 | 3.2107 | 3.2205 | 3.2315 | 3.2991 | 3.2195 | 0.12574 | 0.22115 | 0.091919 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.057422 | 0.084204
5696.375 | 122.1588 | -3.2181 | 118.8263 | 0.10812 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.084537 | 0.18453 | 0.055298 | -0.028522 | -0.002124 | 0.032376 | -0.038063 | -0.00775 | 3.3262 | 3.2233 | 3.2061 | 3.216 | 3.2269 | 3.2945 | 3.2103 | 0.12574 | 0.22573 | 0.096497 | 0.012677 | 0.039075 | 0.073575 | 0.003136 | 0.033449 | 0.086661 | 0.1226 | 0.057422 | 0.093361
5698.1562 | 122.2229 | -3.1906 | 118.8126 | 0.12185 | 0.000689 | -0.021157 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 0.084537 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 3.3125 | 3.1913 | 3.1695 | 3.1839 | 3.1948 | 3.2716 | 3.1783 | 0.12574 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 0.091239 | 0.1226 | 0.052844 | 0.084205
5699.875 | 122.1085 | -3.2364 | 118.8538 | 0.12185 | 0.005267 | -0.021157 | -0.002124 | -0.000359 | 0.071848 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 3.3582 | 3.2417 | 3.2152 | 3.2343 | 3.236 | 3.3082 | 3.2286 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 0.086661 | 0.10429 | 0.062001 | 0.079626
5701.6406 | 122.2275 | -3.1128 | 118.9041 | 0.11727 | -0.00389 | -0.012 | -0.002124 | -0.000359 | 0.081005 | -0.012357 | 0.079959 | 0.17995 | 0.046142 | -0.019364 | -0.011281 | 0.036954 | -0.028906 | -0.012328 | 3.2301 | 3.1089 | 3.1008 | 3.1107 | 3.1124 | 3.1938 | 3.1004 | 0.12116 | 0.22115 | 0.087341 | 0.021835 | 0.029918 | 0.078153 | 0.012293 | 0.028871 | 0.09124 | 0.10887 | 0.057423 | 0.075048
5703.4062 | 122.1405 | -3.1815 | 118.8721 | 0.11727 | 0.005267 | -0.012 | 0.002454 | -0.000359 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 3.2987 | 3.1867 | 3.1695 | 3.1839 | 3.1811 | 3.2579 | 3.1737 | 0.112 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.077504 | 0.10429 | 0.057422 | 0.084204
5705.1094 | 122.081 | -3.1586 | 118.9453 | 0.12185 | 0.000689 | -0.016578 | 0.007033 | 0.013375 | 0.085583 | -0.007779 | 0.084537 | 0.17995 | 0.05072 | -0.028522 | -0.006702 | 0.032376 | -0.038063 | 0.005985 | 3.2804 | 3.1593 | 3.142 | 3.1656 | 3.1719 | 3.2442 | 3.1508 | 0.12574 | 0.22115 | 0.091919 | 0.012677 | 0.034497 | 0.073575 | 0.003136 | 0.047184 | 0.091239 | 0.1226 | 0.057422 | 0.088783
5706.875 | 122.1497 | -3.1586 | 118.9133 | 0.11727 | 0.000689 | -0.021157 | -0.002124 | -0.004937 | 0.071848 | -0.016936 | 0.079959 | 0.18453 | 0.055298 | -0.028522 | -0.006702 | 0.032376 | -0.024328 | -0.012328 | 3.2758 | 3.1593 | 3.1374 | 3.1564 | 3.1536 | 3.2304 | 3.1416 | 0.12116 | 0.22573 | 0.096497 | 0.012677 | 0.034497 | 0.073575 | 0.016871 | 0.028871 | 0.086661 | 0.10429 | 0.062 | 0.079626
5708.5781 | 122.0993 | -3.1677 | 118.927 | 0.11727 | 0.005267 | -0.002842 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.003172 | 3.285 | 3.173 | 3.1649 | 3.1702 | 3.1765 | 3.2396 | 3.1645 | 0.12116 | 0.22115 | 0.091919 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.038027 | 0.082083 | 0.11344 | 0.052844 | 0.084204
5710.3438 | 122.1039 | -3.1586 | 118.9362 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 0.084537 | 0.17995 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 3.2804 | 3.1593 | 3.142 | 3.1519 | 3.1674 | 3.2396 | 3.1508 | 0.12574 | 0.22115 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.095818 | 0.11802 | 0.062001 | 0.084204
5712.0469 | 122.1542 | -3.1769 | 118.9041 | 0.12185 | 0.005267 | -0.007421 | -0.011281 | -0.000359 | 0.081005 | 0.001377 | 0.079959 | 0.18911 | 0.055298 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.003172 | 3.2987 | 3.1821 | 3.1695 | 3.1656 | 3.1765 | 3.2579 | 3.1783 | 0.12116 | 0.23031 | 0.096497 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.038027 | 0.082083 | 0.11344 | 0.057422 | 0.088782
5713.7969 | 122.1085 | -3.2043 | 118.8995 | 0.11269 | -0.00389 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.012357 | 0.079959 | 0.19369 | 0.059877 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 3.317 | 3.2005 | 3.1878 | 3.1976 | 3.2131 | 3.2808 | 3.192 | 0.12116 | 0.23489 | 0.10108 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.071158 | 0.093361
5715.5781 | 122.1588 | -3.2364 | 118.84 | 0.10812 | -0.00389 | -0.016578 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.084537 | 0.18453 | 0.05072 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | 0.005985 | 3.3445 | 3.2325 | 3.2198 | 3.2388 | 3.2452 | 3.3128 | 3.2286 | 0.12574 | 0.22573 | 0.091919 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.047184 | 0.091239 | 0.11802 | 0.057422 | 0.084204
5717.2812 | 122.2229 | -3.2089 | 118.8217 | 0.11727 | -0.00389 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.055298 | -0.028522 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 3.3262 | 3.205 | 3.1923 | 3.2068 | 3.2177 | 3.2853 | 3.2011 | 0.11658 | 0.22115 | 0.096497 | 0.012677 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.082082 | 0.11344 | 0.062 | 0.093361
5719.0469 | 122.2458 | -3.2181 | 118.8263 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.007779 | 0.07538 | 0.17537 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.028906 | -0.003172 | 3.3399 | 3.2188 | 3.2015 | 3.216 | 3.2177 | 3.2945 | 3.2103 | 0.11658 | 0.21657 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.012293 | 0.038027 | 0.082082 | 0.10429 | 0.062 | 0.084204
5720.75 | 122.2321 | -3.2135 | 118.84 | 0.11727 | -0.00389 | -0.012 | 0.002454 | 0.004219 | 0.076426 | -0.012357 | 0.079959 | 0.18453 | 0.046142 | -0.023943 | -0.002124 | 0.032376 | -0.038063 | -0.003172 | 3.3308 | 3.2096 | 3.2015 | 3.216 | 3.2177 | 3.2899 | 3.2011 | 0.12116 | 0.22573 | 0.087341 | 0.017256 | 0.039075 | 0.073575 | 0.003136 | 0.038027 | 0.082083 | 0.11802 | 0.048266 | 0.084205
5722.5156 | 121.3577 | -39.6149 | 80.8685 | 0.12185 | -0.00389 | -0.021157 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 39.7367 | 39.611 | 39.5937 | 39.6127 | 39.6191 | 39.6959 | 39.6071 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 0.09124 | 0.11802 | 0.062001 | 0.088783
5724.2188 | 120.7123 | -11.6592 | 109.7397 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 11.7811 | 11.6645 | 11.6472 | 11.6571 | 11.668 | 11.7357 | 11.6515 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5725.9844 | 121.6049 | -10.3317 | 111.1633 | 0.12185 | 0.005267 | -0.021157 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.07538 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.012328 | 10.4536 | 10.337 | 10.3106 | 10.3296 | 10.3405 | 10.4127 | 10.3194 | 0.11658 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.028871 | 0.082082 | 0.10429 | 0.062 | 0.084204
5727.6875 | 121.6049 | -9.819 | 111.6074 | 0.12185 | 0.000689 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.003201 | 0.084537 | 0.17995 | 0.041563 | -0.023943 | -0.015859 | 0.032376 | -0.042641 | -0.003172 | 9.9409 | 9.8197 | 9.807 | 9.8123 | 9.8233 | 9.8955 | 9.8158 | 0.12574 | 0.22115 | 0.082762 | 0.017256 | 0.02534 | 0.073575 | -0.001442 | 0.038027 | 0.1004 | 0.12718 | 0.057422 | 0.084204
5729.4531 | 121.7377 | -11.0046 | 110.5453 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | -0.003201 | 0.089116 | 0.18453 | 0.046142 | -0.023943 | -0.002124 | 0.032376 | -0.038063 | -0.003172 | 11.1265 | 11.0099 | 10.9881 | 10.9979 | 11.0089 | 11.0856 | 11.0014 | 0.13032 | 0.22573 | 0.087341 | 0.017256 | 0.039075 | 0.073575 | 0.003136 | 0.038027 | 0.09124 | 0.12718 | 0.048266 | 0.084205
5731.1562 | 121.0922 | -19.6152 | 102.475 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 19.737 | 19.6204 | 19.5986 | 19.613 | 19.6194 | 19.6962 | 19.612 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.09124 | 0.11802 | 0.062001 | 0.088783
5732.9219 | 121.3989 | -14.2914 | 107.4371 | 0.11727 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.071848 | -0.007779 | 0.07538 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.038063 | 0.001406 | 14.4087 | 14.2921 | 14.2794 | 14.2893 | 14.2956 | 14.3632 | 14.2836 | 0.11658 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.003136 | 0.042605 | 0.082082 | 0.11344 | 0.062 | 0.093361
5734.6406 | 121.8246 | -10.3226 | 111.3007 | 0.11727 | 0.005267 | -0.021157 | -0.002124 | -0.000359 | 0.085583 | -0.007779 | 0.079959 | 0.17537 | 0.05072 | -0.019364 | -0.011281 | 0.032376 | -0.038063 | 0.001406 | 10.4398 | 10.3278 | 10.3014 | 10.3204 | 10.3222 | 10.4082 | 10.3148 | 0.12116 | 0.21657 | 0.091919 | 0.021835 | 0.029918 | 0.073575 | 0.003136 | 0.042605 | 0.09124 | 0.11802 | 0.062001 | 0.088783
5736.4062 | 121.669 | -10.5698 | 111.1084 | 0.12185 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.071848 | -0.007779 | 0.079959 | 0.19369 | 0.046142 | -0.023943 | -0.015859 | 0.032376 | -0.038063 | -0.00775 | 10.6916 | 10.5659 | 10.5578 | 10.5676 | 10.574 | 10.6416 | 10.562 | 0.12116 | 0.23489 | 0.087341 | 0.017256 | 0.02534 | 0.073575 | 0.003136 | 0.033449 | 0.095818 | 0.11802 | 0.062001 | 0.084205
5738.1719 | 121.843 | -25.6531 | 95.9244 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 25.7749 | 25.6583 | 25.6365 | 25.6464 | 25.6619 | 25.7295 | 25.6453 | 0.12116 | 0.22115 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5739.9375 | 121.7972 | -26.0422 | 95.549 | 0.12185 | -0.00389 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.003201 | 0.070802 | 0.19369 | 0.046142 | -0.028522 | -0.011281 | 0.027798 | -0.033484 | 0.001406 | 26.164 | 26.0383 | 26.0348 | 26.0401 | 26.0464 | 26.1278 | 26.039 | 0.112 | 0.23489 | 0.087341 | 0.012677 | 0.029918 | 0.068997 | 0.007715 | 0.042605 | 0.082083 | 0.10429 | 0.057423 | 0.079626
5741.7031 | 121.8613 | -17.7017 | 103.9856 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.028522 | -0.002124 | 0.032376 | -0.038063 | -0.00775 | 17.8282 | 17.7024 | 17.6897 | 17.6996 | 17.7105 | 17.7827 | 17.6939 | 0.12116 | 0.22573 | 0.087341 | 0.012677 | 0.039075 | 0.073575 | 0.003136 | 0.033449 | 0.082083 | 0.11802 | 0.048266 | 0.084205
5743.4062 | 121.17 | -13.9389 | 107.7942 | 0.12185 | 0.009846 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.089116 | 0.17995 | 0.046142 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | -0.00775 | 14.0608 | 13.9488 | 13.9269 | 13.9322 | 13.9431 | 14.0153 | 13.9311 | 0.13032 | 0.22115 | 0.087341 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.033449 | 0.095818 | 0.12718 | 0.052844 | 0.084205
5745.2188 | 121.7148 | -14.2181 | 107.5424 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.17995 | 0.055298 | -0.033101 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 14.34 | 14.2188 | 14.2016 | 14.216 | 14.2224 | 14.2946 | 14.2104 | 0.12574 | 0.22115 | 0.096497 | 0.008098 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5746.9375 | 121.9391 | -17.6514 | 103.8437 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.013375 | 0.067269 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 17.7686 | 17.6521 | 17.6348 | 17.6492 | 17.6647 | 17.7186 | 17.6436 | 0.12116 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.052844 | 0.079626
5748.7031 | 121.9482 | -23.5886 | 98.0621 | 0.11727 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.016936 | 0.079959 | 0.18453 | 0.05072 | -0.028522 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 23.7058 | 23.5893 | 23.572 | 23.5819 | 23.5974 | 23.6696 | 23.5716 | 0.12116 | 0.22573 | 0.091919 | 0.012677 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.086661 | 0.11802 | 0.057422 | 0.088783
5750.4375 | 121.9025 | -31.1234 | 90.5319 | 0.11269 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.028522 | -0.002124 | 0.032376 | -0.038063 | 0.001406 | 31.236 | 31.1286 | 31.1068 | 31.1258 | 31.1321 | 31.1998 | 31.1156 | 0.12116 | 0.22115 | 0.096497 | 0.012677 | 0.039075 | 0.073575 | 0.003136 | 0.042605 | 0.082083 | 0.11802 | 0.057422 | 0.093361
5752.2031 | 121.9025 | -28.0289 | 93.6356 | 0.12185 | 0.000689 | -0.016578 | -0.011281 | 0.004219 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 28.1507 | 28.0296 | 28.0123 | 28.0176 | 28.0331 | 28.1099 | 28.0165 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 0.086661 | 0.11344 | 0.057423 | 0.084205
5753.9688 | 121.9391 | -28.2669 | 93.4708 | 0.12185 | 0.000689 | -0.016578 | -0.002124 | -0.000359 | 0.076426 | -0.012357 | 0.079959 | 0.17995 | 0.05072 | -0.033101 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 28.3888 | 28.2676 | 28.2503 | 28.2648 | 28.2665 | 28.3433 | 28.2545 | 0.12116 | 0.22115 | 0.091919 | 0.008098 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5755.75 | 121.312 | -43.7119 | 84.6542 | 0.11727 | 0.009846 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.084537 | 0.17995 | 0.046142 | -0.023943 | -0.015859 | 0.027798 | -0.028906 | -0.012328 | 43.8291 | 43.7217 | 43.6999 | 43.7097 | 43.7206 | 43.7929 | 43.7087 | 0.12574 | 0.22115 | 0.087341 | 0.017256 | 0.02534 | 0.068997 | 0.012293 | 0.028871 | 0.1004 | 0.11344 | 0.062001 | 0.075048
5757.5156 | 122.0856 | -118.364 | 3.2272 | 0.12185 | 0.009846 | -0.012 | -0.002124 | -0.004937 | 0.071848 | -0.007779 | 0.084537 | 0.19369 | 0.046142 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 118.4858 | 118.3738 | 118.352 | 118.3618 | 118.359 | 118.4358 | 118.3562 | 0.12574 | 0.23489 | 0.087341 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.095818 | 0.1226 | 0.057423 | 0.084205
5759.2812 | 122.1497 | -119.6915 | 1.9913 | 0.12643 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 0.084537 | 0.18911 | 0.059877 | -0.014785 | -0.002124 | 0.018642 | -0.033484 | -0.00775 | 119.8179 | 119.6922 | 119.6749 | 119.6848 | 119.7003 | 119.7771 | 119.6837 | 0.12574 | 0.23031 | 0.10108 | 0.026414 | 0.039075 | 0.059841 | 0.007715 | 0.033449 | 0.086661 | 0.11802 | 0.062001 | 0.093361
5760.9844 | 122.0627 | -118.0298 | 3.6758 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.071848 | -0.012357 | 0.084537 | 0.18911 | 0.059877 | -0.023943 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 118.1516 | 118.0351 | 118.0178 | 118.0277 | 118.0386 | 118.1016 | 118.0174 | 0.12574 | 0.23031 | 0.10108 | 0.017256 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.091239 | 0.1226 | 0.066579 | 0.09794
5762.75 | 122.1451 | -118.428 | 3.2547 | 0.12643 | 0.000689 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 0.079959 | 0.18453 | 0.046142 | -0.028522 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 118.5545 | 118.4287 | 118.4115 | 118.4213 | 118.4323 | 118.509 | 118.4157 | 0.12116 | 0.22573 | 0.087341 | 0.012677 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.057423 | 0.079626
5764.5156 | 122.0123 | -118.7027 | 3.1357 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.084537 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 118.8245 | 118.7034 | 118.6907 | 118.7006 | 118.7069 | 118.7837 | 118.6903 | 0.12574 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.091239 | 0.1226 | 0.052844 | 0.084205
5766.2812 | 122.168 | -120.6299 | 1.0986 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.004219 | 0.076426 | -0.003201 | 0.084537 | 0.18911 | 0.046142 | -0.019364 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 120.7517 | 120.6397 | 120.6179 | 120.6323 | 120.6341 | 120.7063 | 120.6267 | 0.12574 | 0.23031 | 0.087341 | 0.021835 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 0.095818 | 0.11344 | 0.057423 | 0.075048
5767.9844 | 122.0627 | -120.6985 | 1.1444 | 0.12185 | 0.009846 | -0.012 | -0.006703 | 0.008797 | 0.090161 | -0.007779 | 0.079959 | 0.18453 | 0.055298 | -0.023943 | -0.015859 | 0.027798 | -0.038063 | -0.00775 | 120.8204 | 120.7084 | 120.6865 | 120.6918 | 120.7073 | 120.7887 | 120.6908 | 0.12116 | 0.22573 | 0.096497 | 0.017256 | 0.02534 | 0.068997 | 0.003136 | 0.033449 | 0.095818 | 0.11802 | 0.071157 | 0.093361
5769.75 | 122.0261 | -120.7077 | 1.181 | 0.12185 | 0.005267 | -0.007421 | -0.011281 | 0.008797 | 0.085583 | -0.012357 | 0.079959 | 0.18453 | 0.059877 | -0.023943 | -0.002124 | 0.027798 | -0.038063 | -0.00775 | 120.8296 | 120.713 | 120.7003 | 120.6964 | 120.7165 | 120.7933 | 120.6953 | 0.12116 | 0.22573 | 0.10108 | 0.017256 | 0.039075 | 0.068997 | 0.003136 | 0.033449 | 0.082083 | 0.11802 | 0.062001 | 0.09794
5771.5156 | 122.1085 | -120.7077 | 1.149 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.079959 | 0.18911 | 0.059877 | -0.023943 | -0.015859 | 0.032376 | -0.028906 | -0.003172 | 120.825 | 120.7084 | 120.6911 | 120.7056 | 120.7211 | 120.7887 | 120.6999 | 0.12116 | 0.23031 | 0.10108 | 0.017256 | 0.02534 | 0.073575 | 0.012293 | 0.038027 | 0.095818 | 0.10887 | 0.075736 | 0.088783
5773.2188 | 122.0993 | -120.5795 | 1.1673 | 0.12185 | 0.009846 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.003201 | 0.084537 | 0.17995 | 0.046142 | -0.023943 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 120.7014 | 120.5894 | 120.5721 | 120.5774 | 120.5837 | 120.6651 | 120.5763 | 0.12574 | 0.22115 | 0.087341 | 0.017256 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.091239 | 0.1226 | 0.052844 | 0.084205
5774.9844 | 122.0352 | -120.3964 | 1.4923 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.18911 | 0.055298 | -0.019364 | -0.015859 | 0.036954 | -0.038063 | -0.00775 | 120.5183 | 120.3971 | 120.3844 | 120.3943 | 120.4052 | 120.4774 | 120.3886 | 0.11658 | 0.23031 | 0.096497 | 0.021835 | 0.02534 | 0.078153 | 0.003136 | 0.033449 | 0.091239 | 0.11344 | 0.071157 | 0.093361
5776.75 | 122.1359 | -120.2637 | 1.5884 | 0.13101 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.079959 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.036954 | -0.033484 | -0.003172 | 120.3947 | 120.2644 | 120.2517 | 120.2615 | 120.2725 | 120.3493 | 120.2559 | 0.12116 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.078153 | 0.007715 | 0.038027 | 0.09124 | 0.11344 | 0.062001 | 0.084204
5778.5156 | 121.9986 | -120.1721 | 1.7441 | 0.11727 | -0.00389 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.019364 | -0.006702 | 0.018642 | -0.038063 | -0.012328 | 120.2894 | 120.1682 | 120.1601 | 120.17 | 120.1855 | 120.2531 | 120.1689 | 0.12116 | 0.22573 | 0.091919 | 0.021835 | 0.034497 | 0.059841 | 0.003136 | 0.028871 | 0.086661 | 0.11802 | 0.057422 | 0.088783
5780.2812 | 122.049 | -120.1263 | 1.7853 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.079959 | 0.18453 | 0.05072 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.00775 | 120.2482 | 120.127 | 120.1143 | 120.1242 | 120.1351 | 120.2073 | 120.1277 | 0.12116 | 0.22573 | 0.091919 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.033449 | 0.082083 | 0.11344 | 0.052844 | 0.084204
5781.9844 | 122.2412 | -117.0593 | 4.6097 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.076426 | 0.001377 | 0.084537 | 0.18453 | 0.059877 | -0.028522 | -0.015859 | 0.02322 | -0.042641 | -0.012328 | 117.1858 | 117.06 | 117.0427 | 117.0618 | 117.0635 | 117.1358 | 117.0607 | 0.12574 | 0.22573 | 0.10108 | 0.012677 | 0.02534 | 0.064419 | -0.001442 | 0.028871 | 0.1004 | 0.12718 | 0.075736 | 0.10252
5783.75 | 122.1725 | -116.6382 | 5.1407 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.085583 | -0.003201 | 0.084537 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 116.7646 | 116.6389 | 116.6262 | 116.6406 | 116.6424 | 116.7238 | 116.635 | 0.12574 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.095818 | 0.1226 | 0.062001 | 0.088783
5785.5156 | 122.1542 | -119.0323 | 2.8152 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.010206 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 119.1541 | 119.0376 | 119.0203 | 119.0347 | 119.0411 | 119.1179 | 119.0245 | 0.12116 | 0.22115 | 0.096497 | 0.030993 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5787.2812 | 122.1497 | -119.7464 | 2.1286 | 0.12643 | 0.000689 | -0.012 | -0.006703 | 0.013375 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | -0.00775 | 119.8728 | 119.7471 | 119.7344 | 119.7397 | 119.7598 | 119.8274 | 119.7386 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.033449 | 0.086661 | 0.11802 | 0.057422 | 0.088783
5789 | 122.1222 | -119.7876 | 2.1286 | 0.13101 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.023943 | -0.015859 | 0.027798 | -0.038063 | -0.012328 | 119.9186 | 119.7929 | 119.7756 | 119.7855 | 119.7964 | 119.8686 | 119.7798 | 0.12116 | 0.23031 | 0.096497 | 0.017256 | 0.02534 | 0.068997 | 0.003136 | 0.028871 | 0.095818 | 0.11802 | 0.071157 | 0.093361
5790.7656 | 122.2687 | -119.2108 | 2.6093 | 0.11727 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.012357 | 0.079959 | 0.17995 | 0.046142 | -0.023943 | -0.006702 | 0.02322 | -0.028906 | -0.012328 | 119.3281 | 119.2115 | 119.1988 | 119.2087 | 119.2196 | 119.2872 | 119.1985 | 0.12116 | 0.22115 | 0.087341 | 0.017256 | 0.034497 | 0.064419 | 0.012293 | 0.028871 | 0.086661 | 0.10887 | 0.052844 | 0.075048
5792.5312 | 122.2458 | -119.3893 | 2.4307 | 0.12185 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.085583 | -0.007779 | 0.084537 | 0.18911 | 0.055298 | -0.028522 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 119.5112 | 119.39 | 119.3773 | 119.3918 | 119.3936 | 119.4749 | 119.3816 | 0.12574 | 0.23031 | 0.096497 | 0.012677 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.095818 | 0.11802 | 0.066579 | 0.088782
5794.2344 | 122.1588 | -119.5129 | 2.3849 | 0.13101 | 0.005267 | -0.007421 | 0.007033 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.023943 | -0.011281 | 0.02322 | -0.042641 | -0.012328 | 119.6439 | 119.5182 | 119.5055 | 119.52 | 119.5217 | 119.5894 | 119.5052 | 0.12116 | 0.23031 | 0.096497 | 0.017256 | 0.029918 | 0.064419 | -0.001442 | 0.028871 | 0.09124 | 0.1226 | 0.066579 | 0.097939
5796 | 122.0947 | -119.9387 | 2.0142 | 0.12643 | 0.009846 | -0.016578 | 0.007033 | 0.008797 | 0.076426 | -0.003201 | 0.084537 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 120.0651 | 119.9485 | 119.9221 | 119.9457 | 119.9475 | 120.0151 | 119.9355 | 0.12574 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.062 | 0.088782
5797.7031 | 122.0947 | -120.5154 | 1.4648 | 0.12185 | 0.009846 | -0.016578 | -0.002124 | 0.008797 | 0.085583 | -0.003201 | 0.079959 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.02322 | -0.028906 | -0.003172 | 120.6373 | 120.5253 | 120.4989 | 120.5133 | 120.5242 | 120.601 | 120.5122 | 0.12116 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.064419 | 0.012293 | 0.038027 | 0.086661 | 0.10887 | 0.062 | 0.084204
5799.4531 | 122.1817 | -117.3981 | 4.5181 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.084537 | 0.18911 | 0.055298 | -0.014785 | -0.011281 | 0.027798 | -0.028906 | -0.012328 | 117.5199 | 117.4079 | 117.3815 | 117.4005 | 117.4114 | 117.4791 | 117.3994 | 0.12574 | 0.23031 | 0.096497 | 0.026414 | 0.029918 | 0.068997 | 0.012293 | 0.028871 | 0.095818 | 0.11344 | 0.066579 | 0.084204
5801.1562 | 122.1954 | -120.5887 | 1.2909 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.02322 | -0.033484 | 0.001406 | 120.7105 | 120.594 | 120.5767 | 120.5911 | 120.6021 | 120.6651 | 120.5809 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.064419 | 0.007715 | 0.042605 | 0.086661 | 0.10886 | 0.062001 | 0.084204
5802.9219 | 122.1451 | -120.8221 | 1.1261 | 0.12643 | 0.005267 | -0.016578 | 0.007033 | 0.008797 | 0.076426 | -0.003201 | 0.079959 | 0.17995 | 0.059877 | -0.014785 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 120.9486 | 120.8274 | 120.8056 | 120.8292 | 120.8309 | 120.8986 | 120.8189 | 0.12116 | 0.22115 | 0.10108 | 0.026414 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.09124 | 0.11344 | 0.071158 | 0.093361
5804.6875 | 122.1725 | -120.9091 | 1.0712 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.014785 | -0.011281 | 0.02322 | -0.042641 | -0.00775 | 121.031 | 120.919 | 120.8971 | 120.9116 | 120.9179 | 120.981 | 120.9013 | 0.12116 | 0.23031 | 0.096497 | 0.026414 | 0.029918 | 0.064419 | -0.001442 | 0.033449 | 0.09124 | 0.1226 | 0.066579 | 0.097939
5806.3906 | 122.0901 | -120.0531 | 1.9455 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.084537 | 0.18453 | 0.059877 | -0.023943 | -0.011281 | 0.027798 | -0.042641 | -0.00775 | 120.175 | 120.0538 | 120.0319 | 120.051 | 120.0619 | 120.1387 | 120.0453 | 0.12574 | 0.22573 | 0.10108 | 0.017256 | 0.029918 | 0.068997 | -0.001442 | 0.033449 | 0.095818 | 0.12718 | 0.071158 | 0.10252
5808.1719 | 122.1863 | -118.895 | 3.1952 | 0.13559 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.084537 | 0.18911 | 0.05072 | -0.014785 | -0.011281 | 0.027798 | -0.033484 | -0.012328 | 119.0305 | 118.9002 | 118.8875 | 118.8928 | 118.9038 | 118.9714 | 118.8872 | 0.12574 | 0.23031 | 0.091919 | 0.026414 | 0.029918 | 0.068997 | 0.007715 | 0.028871 | 0.095818 | 0.11802 | 0.062001 | 0.084204
5809.875 | 122.2549 | -120.8817 | 1.03 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.012357 | 0.079959 | 0.18453 | 0.055298 | -0.028522 | -0.011281 | 0.027798 | -0.033484 | -0.012328 | 121.0081 | 120.8869 | 120.8697 | 120.8795 | 120.8859 | 120.9672 | 120.8693 | 0.12116 | 0.22573 | 0.096497 | 0.012677 | 0.029918 | 0.068997 | 0.007715 | 0.028871 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5811.6406 | 122.1039 | -120.9045 | 1.0849 | 0.13101 | 0.005267 | -0.016578 | -0.006703 | 0.013375 | 0.071848 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 121.0355 | 120.9098 | 120.888 | 120.8978 | 120.9179 | 120.9764 | 120.9013 | 0.12116 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 0.09124 | 0.10887 | 0.062001 | 0.079626
5813.3281 | 122.1542 | -120.8221 | 1.1627 | 0.12185 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.046142 | -0.023943 | -0.011281 | 0.02322 | -0.033484 | -0.00775 | 120.944 | 120.8274 | 120.8147 | 120.82 | 120.8355 | 120.9031 | 120.8189 | 0.12116 | 0.22573 | 0.087341 | 0.017256 | 0.029918 | 0.064419 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.057423 | 0.079626
5815.1094 | 122.1542 | -120.8267 | 1.1581 | 0.12643 | 0.005267 | -0.012 | -0.006703 | 0.013375 | 0.071848 | -0.003201 | 0.079959 | 0.19369 | 0.05072 | -0.019364 | -0.006702 | 0.036954 | -0.033484 | 0.001406 | 120.9532 | 120.832 | 120.8147 | 120.82 | 120.8401 | 120.8986 | 120.8235 | 0.12116 | 0.23489 | 0.091919 | 0.021835 | 0.034497 | 0.078153 | 0.007715 | 0.042605 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5816.8281 | 122.1268 | -120.8588 | 1.1307 | 0.12185 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.9806 | 120.8595 | 120.8468 | 120.8521 | 120.8676 | 120.9352 | 120.851 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.062001 | 0.084204
5818.5938 | 122.1451 | -120.9366 | 1.0529 | 0.11727 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.028522 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 121.0539 | 120.9419 | 120.92 | 120.9345 | 120.9454 | 121.013 | 120.9334 | 0.11658 | 0.22573 | 0.091919 | 0.012677 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5820.2969 | 122.1725 | -120.9366 | 1.0666 | 0.12643 | 0.009846 | -0.002842 | -0.002124 | 0.013375 | 0.076426 | -0.007779 | 0.079959 | 0.18453 | 0.05072 | -0.019364 | 0.002454 | 0.032376 | -0.04722 | -0.003172 | 121.063 | 120.9464 | 120.9337 | 120.9345 | 120.95 | 121.013 | 120.9288 | 0.12116 | 0.22573 | 0.091919 | 0.021835 | 0.043653 | 0.073575 | -0.006021 | 0.038027 | 0.077505 | 0.12718 | 0.048266 | 0.09794
5822.0625 | 122.2549 | -120.9274 | 1.0208 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 121.0493 | 120.9327 | 120.9109 | 120.9253 | 120.9316 | 121.0084 | 120.9242 | 0.12116 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.09124 | 0.11344 | 0.062001 | 0.084204
5823.75 | 122.2504 | -120.8496 | 1.0712 | 0.11727 | 0.000689 | -0.007421 | -0.006703 | 0.004219 | 0.076426 | 0.001377 | 0.079959 | 0.18911 | 0.05072 | -0.028522 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.9669 | 120.8503 | 120.8422 | 120.8429 | 120.8538 | 120.926 | 120.851 | 0.12116 | 0.23031 | 0.091919 | 0.012677 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.062001 | 0.084204
5825.5156 | 122.168 | -120.9 | 1.1124 | 0.12185 | 0.014425 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.07538 | 0.19369 | 0.064455 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 121.0218 | 120.9144 | 120.888 | 120.8978 | 120.9133 | 120.981 | 120.8968 | 0.11658 | 0.23489 | 0.10565 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.071157 | 0.097939
5827.2812 | 122.1817 | -120.8862 | 1.1078 | 0.12643 | 0.005267 | -0.002842 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.079959 | 0.17995 | 0.05072 | -0.019364 | -0.011281 | 0.02322 | -0.033484 | -0.00775 | 121.0127 | 120.8915 | 120.8834 | 120.8841 | 120.895 | 120.9672 | 120.8785 | 0.12116 | 0.22115 | 0.091919 | 0.021835 | 0.029918 | 0.064419 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.062001 | 0.084204
5829.0469 | 122.1909 | -120.9137 | 1.1078 | 0.12643 | 0.005267 | -0.012 | -0.006703 | 0.013375 | 0.076426 | -0.007779 | 0.089116 | 0.18453 | 0.055298 | -0.023943 | -0.015859 | 0.032376 | -0.028906 | -0.00775 | 121.0401 | 120.919 | 120.9017 | 120.907 | 120.9271 | 120.9901 | 120.9059 | 0.13032 | 0.22573 | 0.096497 | 0.017256 | 0.02534 | 0.073575 | 0.012293 | 0.033449 | 0.10497 | 0.11802 | 0.071157 | 0.084204
5830.75 | 122.1451 | -120.9229 | 1.1398 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.18453 | 0.055298 | -0.014785 | -0.006702 | 0.02322 | -0.038063 | -0.003172 | 121.0447 | 120.9327 | 120.9109 | 120.9253 | 120.9271 | 120.9993 | 120.9151 | 0.12574 | 0.22573 | 0.096497 | 0.026414 | 0.034497 | 0.064419 | 0.003136 | 0.038027 | 0.091239 | 0.1226 | 0.062 | 0.093361
5832.5312 | 122.2733 | -120.8954 | 1.062 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | -0.016936 | 0.070802 | 0.17995 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | -0.00775 | 121.0218 | 120.9007 | 120.888 | 120.8933 | 120.8996 | 120.9718 | 120.8785 | 0.112 | 0.22115 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.033449 | 0.077504 | 0.099708 | 0.062 | 0.084204
5834.2969 | 122.1863 | -120.9457 | 1.1032 | 0.12643 | 0.009846 | -0.002842 | -0.002124 | 0.008797 | 0.076426 | 0.001377 | 0.07538 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.033484 | -0.012328 | 121.0722 | 120.9556 | 120.9429 | 120.9436 | 120.9545 | 121.0222 | 120.9471 | 0.11658 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.007715 | 0.028871 | 0.082082 | 0.10886 | 0.062 | 0.088782
5836.0625 | 122.2321 | -120.9183 | 1.0391 | 0.11727 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.046142 | -0.028522 | -0.011281 | 0.02322 | -0.033484 | -0.00775 | 121.0355 | 120.9235 | 120.9063 | 120.9162 | 120.9271 | 120.9947 | 120.9105 | 0.12116 | 0.22115 | 0.087341 | 0.012677 | 0.029918 | 0.064419 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.057423 | 0.079626
5837.8438 | 122.2778 | -120.9412 | 1.0483 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.013375 | 0.085583 | 0.001377 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.02322 | -0.033484 | 0.001406 | 121.0676 | 120.9419 | 120.9292 | 120.9436 | 120.9545 | 121.0267 | 120.9425 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.064419 | 0.007715 | 0.042605 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5839.6094 | 122.1909 | -120.9641 | 1.0574 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.093694 | 0.18911 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 121.0859 | 120.9693 | 120.9475 | 120.9619 | 120.9728 | 121.0405 | 120.9563 | 0.13489 | 0.23031 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.1004 | 0.12718 | 0.062 | 0.088782
5841.3125 | 122.1863 | -120.9824 | 1.0666 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.017953 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.028522 | -0.006702 | 0.027798 | -0.024328 | -0.012328 | 121.1088 | 120.9876 | 120.9704 | 120.9802 | 121.0003 | 121.0634 | 120.9792 | 0.11658 | 0.22573 | 0.096497 | 0.012677 | 0.034497 | 0.068997 | 0.016871 | 0.028871 | 0.082082 | 0.099708 | 0.062 | 0.079626
5843.1094 | 122.2733 | -120.9412 | 1.0483 | 0.11727 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.084537 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.038063 | -0.012328 | 121.0584 | 120.9464 | 120.9292 | 120.939 | 120.9454 | 121.0267 | 120.9334 | 0.12574 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.003136 | 0.028871 | 0.091239 | 0.1226 | 0.062 | 0.093361
5844.875 | 122.2916 | -120.9641 | 1.0345 | 0.11727 | 0.005267 | -0.007421 | -0.006703 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 121.0813 | 120.9693 | 120.9566 | 120.9573 | 120.9774 | 121.0451 | 120.9563 | 0.11658 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.062 | 0.088782
5846.6562 | 122.168 | -120.9915 | 1.0849 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.07538 | 0.18453 | 0.046142 | -0.014785 | -0.002124 | 0.02322 | -0.033484 | 0.001406 | 121.1134 | 120.9968 | 120.9795 | 120.9894 | 121.0003 | 121.0679 | 120.9837 | 0.11658 | 0.22573 | 0.087341 | 0.026414 | 0.039075 | 0.064419 | 0.007715 | 0.042605 | 0.077504 | 0.10886 | 0.048266 | 0.079626
5848.3594 | 122.2275 | -120.9824 | 1.0803 | 0.11727 | 0.009846 | -0.007421 | 0.002454 | 0.013375 | 0.090161 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 121.0996 | 120.9922 | 120.9749 | 120.9848 | 120.9957 | 121.0725 | 120.9792 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.09124 | 0.11802 | 0.062001 | 0.088783
5850.0625 | 122.1817 | -121.0098 | 1.0895 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.059877 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 121.1363 | 121.0151 | 120.9932 | 121.0123 | 121.014 | 121.0908 | 121.0066 | 0.11658 | 0.22573 | 0.10108 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.066579 | 0.093361
5851.7812 | 122.2321 | -120.9641 | 1.0986 | 0.12185 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.012357 | 0.079959 | 0.18911 | 0.064455 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 121.0859 | 120.9693 | 120.9475 | 120.9665 | 120.9728 | 121.0496 | 120.9517 | 0.12116 | 0.23031 | 0.10565 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.071157 | 0.097939
5853.5312 | 122.3145 | -120.9137 | 1.0941 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.084537 | 0.18911 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.042641 | -0.003172 | 121.0401 | 120.919 | 120.9017 | 120.9116 | 120.9179 | 120.9993 | 120.9059 | 0.12574 | 0.23031 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | -0.001442 | 0.038027 | 0.095818 | 0.12718 | 0.066579 | 0.097939
5855.2344 | 122.1725 | -120.9778 | 1.1398 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.18911 | 0.059877 | -0.014785 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 121.0996 | 120.9785 | 120.9704 | 120.9757 | 120.9866 | 121.0542 | 120.97 | 0.12116 | 0.23031 | 0.10108 | 0.026414 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.09124 | 0.11344 | 0.071158 | 0.093361
5856.9375 | 122.2504 | -120.932 | 1.1215 | 0.12643 | 0.005267 | -0.007421 | -0.006703 | 0.013375 | 0.076426 | -0.012357 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.015859 | 0.032376 | -0.033484 | -0.00775 | 121.0584 | 120.9373 | 120.9246 | 120.9253 | 120.9454 | 121.0084 | 120.9197 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.02534 | 0.073575 | 0.007715 | 0.033449 | 0.095818 | 0.11344 | 0.066579 | 0.084204
5858.6719 | 122.3145 | -120.8908 | 1.1078 | 0.12185 | 0.014425 | -0.016578 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.012328 | 121.0127 | 120.9052 | 120.8742 | 120.8841 | 120.8996 | 120.9672 | 120.883 | 0.12116 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.028871 | 0.09124 | 0.11802 | 0.066579 | 0.093361
5860.3594 | 122.2504 | -120.9137 | 1.1536 | 0.12185 | 0.009846 | -0.012 | 0.011611 | 0.008797 | 0.081005 | 0.001377 | 0.07538 | 0.18453 | 0.059877 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 121.0355 | 120.9235 | 120.9017 | 120.9253 | 120.9225 | 120.9947 | 120.9151 | 0.11658 | 0.22573 | 0.10108 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.066579 | 0.093361
5862.0781 | 122.2275 | -120.9091 | 1.1993 | 0.12643 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.084537 | 0.17995 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | 0.001406 | 121.0355 | 120.919 | 120.9017 | 120.9116 | 120.9179 | 120.9901 | 120.9059 | 0.12574 | 0.22115 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.042605 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5863.7812 | 122.2733 | -120.7855 | 1.2314 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.002124 | 0.032376 | -0.038063 | -0.012328 | 120.912 | 120.7908 | 120.7689 | 120.788 | 120.7943 | 120.8665 | 120.7732 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.039075 | 0.073575 | 0.003136 | 0.028871 | 0.082083 | 0.11802 | 0.052844 | 0.088783
5865.5938 | 122.3099 | -120.7489 | 1.2543 | 0.12643 | 0.009846 | -0.002842 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.079959 | 0.18453 | 0.059877 | -0.019364 | -0.011281 | 0.027798 | -0.024328 | -0.003172 | 120.8753 | 120.7587 | 120.7461 | 120.7468 | 120.7531 | 120.8345 | 120.7411 | 0.12116 | 0.22573 | 0.10108 | 0.021835 | 0.029918 | 0.068997 | 0.016871 | 0.038027 | 0.09124 | 0.10429 | 0.071158 | 0.084205
5867.2969 | 122.2321 | -120.7764 | 1.3458 | 0.12643 | 0.019004 | -0.002842 | 0.002454 | 0.008797 | 0.076426 | 0.001377 | 0.084537 | 0.19369 | 0.05072 | -0.019364 | -0.011281 | 0.02322 | -0.028906 | -0.012328 | 120.9028 | 120.7954 | 120.7735 | 120.7788 | 120.7852 | 120.8528 | 120.7777 | 0.12574 | 0.23489 | 0.091919 | 0.021835 | 0.029918 | 0.064419 | 0.012293 | 0.028871 | 0.095818 | 0.11344 | 0.062001 | 0.079626
5869 | 122.3419 | -120.7031 | 1.3321 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.067269 | -0.003201 | 0.089116 | 0.18453 | 0.055298 | -0.023943 | -0.002124 | 0.036954 | -0.033484 | 0.001406 | 120.825 | 120.7084 | 120.6865 | 120.701 | 120.7119 | 120.7704 | 120.6999 | 0.13032 | 0.22573 | 0.096497 | 0.017256 | 0.039075 | 0.078153 | 0.007715 | 0.042605 | 0.09124 | 0.1226 | 0.057422 | 0.088782
5870.7031 | 122.3328 | -120.6619 | 1.355 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.004219 | 0.076426 | -0.003201 | 0.084537 | 0.17995 | 0.055298 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.012328 | 120.7838 | 120.6672 | 120.6545 | 120.6644 | 120.6661 | 120.7384 | 120.6587 | 0.12574 | 0.22115 | 0.096497 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.028871 | 0.091239 | 0.11802 | 0.062 | 0.088782
5872.3906 | 122.2687 | -120.6802 | 1.4191 | 0.13559 | 0.009846 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.046142 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.00775 | 120.8158 | 120.6901 | 120.6728 | 120.6781 | 120.6936 | 120.7612 | 120.677 | 0.11658 | 0.22573 | 0.087341 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.033449 | 0.077504 | 0.10886 | 0.048266 | 0.079626
5874.1406 | 122.2229 | -120.7581 | 1.355 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.013375 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.05072 | -0.028522 | -0.015859 | 0.027798 | -0.042641 | -0.003172 | 120.8799 | 120.7633 | 120.7415 | 120.7559 | 120.7714 | 120.8345 | 120.7503 | 0.12116 | 0.22115 | 0.091919 | 0.012677 | 0.02534 | 0.068997 | -0.001442 | 0.038027 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5875.8594 | 122.3328 | -120.7718 | 1.2863 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.066223 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.8936 | 120.7771 | 120.7598 | 120.7742 | 120.776 | 120.8528 | 120.764 | 0.10742 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.077504 | 0.099707 | 0.062001 | 0.084204
5877.625 | 122.3099 | -120.7672 | 1.3 | 0.13101 | 0.009846 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.07538 | 0.19369 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 120.8982 | 120.7771 | 120.7552 | 120.7605 | 120.7714 | 120.8482 | 120.7594 | 0.11658 | 0.23489 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 0.086661 | 0.10429 | 0.066579 | 0.084204
5879.3438 | 122.2641 | -120.8221 | 1.2772 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.079959 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 120.944 | 120.8274 | 120.8101 | 120.8246 | 120.8309 | 120.9031 | 120.8098 | 0.12116 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.086661 | 0.11802 | 0.062 | 0.093361
5881.0781 | 122.319 | -120.7947 | 1.268 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.016936 | 0.07538 | 0.18911 | 0.055298 | -0.028522 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 120.9211 | 120.7999 | 120.7873 | 120.7926 | 120.7989 | 120.8803 | 120.7777 | 0.11658 | 0.23031 | 0.096497 | 0.012677 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.086661 | 0.11344 | 0.066579 | 0.093361
5882.7969 | 122.2321 | -120.8588 | 1.2955 | 0.12185 | 0.009846 | -0.012 | -0.002124 | -0.000359 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.019364 | -0.006702 | 0.032376 | -0.028906 | 0.001406 | 120.9806 | 120.8686 | 120.8468 | 120.8566 | 120.8584 | 120.9398 | 120.851 | 0.12116 | 0.22573 | 0.087341 | 0.021835 | 0.034497 | 0.073575 | 0.012293 | 0.042605 | 0.086661 | 0.10887 | 0.052844 | 0.075048
5884.5 | 122.3557 | -120.7993 | 1.2497 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.07538 | 0.19369 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.012328 | 120.9257 | 120.7999 | 120.7918 | 120.7971 | 120.8081 | 120.8803 | 120.8006 | 0.11658 | 0.23489 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.028871 | 0.086661 | 0.10886 | 0.062001 | 0.084204
5886.25 | 122.2824 | -120.8496 | 1.2863 | 0.12185 | 0.014425 | -0.007421 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.014785 | -0.006702 | 0.018642 | -0.028906 | -0.00775 | 120.9715 | 120.864 | 120.8422 | 120.8521 | 120.8538 | 120.9306 | 120.8464 | 0.11658 | 0.22573 | 0.091919 | 0.026414 | 0.034497 | 0.059841 | 0.012293 | 0.033449 | 0.082082 | 0.10429 | 0.057422 | 0.079626
5887.9844 | 122.2549 | -120.8405 | 1.2817 | 0.12185 | 0.005267 | -0.002842 | -0.002124 | 0.008797 | 0.071848 | -0.007779 | 0.079959 | 0.18453 | 0.055298 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.9623 | 120.8457 | 120.8376 | 120.8383 | 120.8493 | 120.9123 | 120.8327 | 0.12116 | 0.22573 | 0.096497 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.066579 | 0.088782
5889.7344 | 122.319 | -120.8633 | 1.2405 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.004219 | 0.076426 | -0.007779 | 0.084537 | 0.18911 | 0.055298 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 120.9898 | 120.8686 | 120.8468 | 120.8658 | 120.8676 | 120.9398 | 120.8556 | 0.12574 | 0.23031 | 0.096497 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 0.095818 | 0.1226 | 0.066579 | 0.093361
5891.4219 | 122.2458 | -120.8725 | 1.2589 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.18911 | 0.055298 | -0.023943 | -0.015859 | 0.02322 | -0.028906 | -0.012328 | 120.9943 | 120.8778 | 120.8605 | 120.875 | 120.8813 | 120.9489 | 120.8693 | 0.11658 | 0.23031 | 0.096497 | 0.017256 | 0.02534 | 0.064419 | 0.012293 | 0.028871 | 0.091239 | 0.10429 | 0.071157 | 0.084204
5893.125 | 122.3419 | -120.9045 | 1.2039 | 0.11269 | 0.005267 | -0.007421 | -0.006703 | 0.008797 | 0.085583 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.014785 | -0.015859 | 0.032376 | -0.028906 | -0.00775 | 121.0172 | 120.9098 | 120.8971 | 120.8978 | 120.9133 | 120.9901 | 120.8968 | 0.12116 | 0.22115 | 0.096497 | 0.026414 | 0.02534 | 0.073575 | 0.012293 | 0.033449 | 0.095818 | 0.10887 | 0.071157 | 0.084204
5894.8281 | 122.2412 | -120.7672 | 1.3824 | 0.12643 | 0.009846 | -0.002842 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.02322 | -0.038063 | -0.003172 | 120.8936 | 120.7771 | 120.7644 | 120.7697 | 120.7714 | 120.8482 | 120.7594 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.064419 | 0.003136 | 0.038027 | 0.086661 | 0.11802 | 0.057422 | 0.088783
5896.5938 | 122.3969 | -120.6802 | 1.3733 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | -0.000359 | 0.081005 | -0.007779 | 0.07538 | 0.18911 | 0.046142 | -0.028522 | -0.002124 | 0.027798 | -0.042641 | -0.00775 | 120.8067 | 120.6855 | 120.6728 | 120.6781 | 120.6799 | 120.7612 | 120.6725 | 0.11658 | 0.23031 | 0.087341 | 0.012677 | 0.039075 | 0.068997 | -0.001442 | 0.033449 | 0.077504 | 0.11802 | 0.048266 | 0.088783
5898.3125 | 122.3007 | -119.5999 | 2.536 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.017953 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | -0.012328 | 119.7263 | 119.6098 | 119.5925 | 119.5978 | 119.6179 | 119.6809 | 119.5921 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.028871 | 0.077504 | 0.099708 | 0.062 | 0.084204
5900.0469 | 122.3877 | -120.7947 | 1.2772 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.18453 | 0.046142 | -0.019364 | -0.015859 | 0.032376 | -0.033484 | -0.00775 | 120.9165 | 120.7999 | 120.7781 | 120.7926 | 120.8081 | 120.8757 | 120.7869 | 0.11658 | 0.22573 | 0.087341 | 0.021835 | 0.02534 | 0.073575 | 0.007715 | 0.033449 | 0.091239 | 0.10886 | 0.062001 | 0.079626
5901.7812 | 122.4014 | -120.7855 | 1.3229 | 0.11727 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.071848 | -0.007779 | 0.084537 | 0.19369 | 0.05072 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.003172 | 120.9028 | 120.7862 | 120.7735 | 120.7788 | 120.7943 | 120.8574 | 120.7777 | 0.12574 | 0.23489 | 0.091919 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11802 | 0.052844 | 0.084204
5903.5156 | 122.2687 | -120.8038 | 1.355 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.07538 | 0.17995 | 0.046142 | -0.019364 | -0.002124 | 0.032376 | -0.038063 | -0.003172 | 120.9257 | 120.8045 | 120.7964 | 120.8017 | 120.8081 | 120.8894 | 120.7961 | 0.11658 | 0.22115 | 0.087341 | 0.021835 | 0.039075 | 0.073575 | 0.003136 | 0.038027 | 0.077504 | 0.11344 | 0.048266 | 0.084205
5905.25 | 122.2733 | -120.8221 | 1.3687 | 0.12185 | -0.00389 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.084537 | 0.18911 | 0.059877 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 120.944 | 120.8183 | 120.8101 | 120.8246 | 120.8309 | 120.9031 | 120.8144 | 0.12574 | 0.23031 | 0.10108 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.091239 | 0.11802 | 0.066579 | 0.093361
5906.9844 | 122.374 | -120.7489 | 1.3641 | 0.12643 | 0.005267 | -0.007421 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.02322 | -0.033484 | -0.003172 | 120.8753 | 120.7542 | 120.7415 | 120.7559 | 120.7577 | 120.8299 | 120.7457 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.064419 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5908.7188 | 122.3419 | -120.7489 | 1.3824 | 0.12643 | 0.005267 | -0.016578 | -0.006703 | 0.008797 | 0.085583 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 120.8753 | 120.7542 | 120.7323 | 120.7422 | 120.7577 | 120.8345 | 120.7457 | 0.12116 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5910.4688 | 122.287 | -120.7489 | 1.4191 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.07538 | 0.17995 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.033484 | -0.00775 | 120.8753 | 120.7587 | 120.7415 | 120.7468 | 120.7577 | 120.8345 | 120.7411 | 0.11658 | 0.22115 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.062 | 0.088782
5912.1875 | 122.3969 | -120.6848 | 1.4328 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.19369 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 120.8112 | 120.6855 | 120.6728 | 120.6873 | 120.6936 | 120.7658 | 120.677 | 0.11658 | 0.23489 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.082082 | 0.10429 | 0.057422 | 0.079626
5913.9062 | 122.2824 | -120.7123 | 1.4694 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.013375 | 0.071848 | -0.003201 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.002124 | 0.02322 | -0.038063 | -0.00775 | 120.8387 | 120.7084 | 120.7003 | 120.7102 | 120.7257 | 120.7841 | 120.7091 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.039075 | 0.064419 | 0.003136 | 0.033449 | 0.082083 | 0.11802 | 0.052844 | 0.088783
5915.6406 | 122.3007 | -120.6802 | 1.4877 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.013375 | 0.09474 | -0.003201 | 0.070802 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.02322 | -0.042641 | -0.00775 | 120.8067 | 120.6855 | 120.6682 | 120.6781 | 120.6936 | 120.775 | 120.677 | 0.112 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.064419 | -0.001442 | 0.033449 | 0.077504 | 0.11344 | 0.052844 | 0.088783
5917.375 | 122.3969 | -120.6116 | 1.474 | 0.13101 | 0.009846 | -0.007421 | -0.006703 | 0.004219 | 0.085583 | -0.012357 | 0.079959 | 0.18453 | 0.046142 | -0.028522 | -0.002124 | 0.027798 | -0.038063 | -0.012328 | 120.7426 | 120.6214 | 120.6042 | 120.6049 | 120.6158 | 120.6972 | 120.5992 | 0.12116 | 0.22573 | 0.087341 | 0.012677 | 0.039075 | 0.068997 | 0.003136 | 0.028871 | 0.082083 | 0.11802 | 0.048266 | 0.084205
5919.1094 | 122.4472 | -120.607 | 1.4969 | 0.12643 | -0.00389 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.019364 | -0.006702 | 0.02322 | -0.038063 | -0.012328 | 120.7334 | 120.6031 | 120.5996 | 120.6049 | 120.6112 | 120.6834 | 120.5992 | 0.12116 | 0.22573 | 0.087341 | 0.021835 | 0.034497 | 0.064419 | 0.003136 | 0.028871 | 0.086661 | 0.11802 | 0.052844 | 0.084205
5920.8438 | 122.4289 | -120.5795 | 1.5106 | 0.12643 | 0.005267 | -0.016578 | -0.002124 | -0.000359 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | 0.001406 | 120.706 | 120.5848 | 120.563 | 120.5774 | 120.5792 | 120.6605 | 120.5763 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.042605 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5922.625 | 122.4106 | -120.5612 | 1.561 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.017953 | 0.081005 | -0.012357 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 120.6876 | 120.5665 | 120.5492 | 120.5591 | 120.5792 | 120.6422 | 120.5489 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.086661 | 0.11802 | 0.057422 | 0.088783
5924.3438 | 122.4152 | -120.575 | 1.5289 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.079959 | 0.19369 | 0.055298 | -0.023943 | -0.011281 | 0.036954 | -0.04722 | -0.012328 | 120.7014 | 120.5802 | 120.5584 | 120.5774 | 120.5837 | 120.656 | 120.5717 | 0.12116 | 0.23489 | 0.096497 | 0.017256 | 0.029918 | 0.078153 | -0.006021 | 0.028871 | 0.09124 | 0.12718 | 0.066579 | 0.10252
5926.0781 | 122.2961 | -120.5246 | 1.6663 | 0.11269 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | -0.00775 | 120.6373 | 120.5299 | 120.5126 | 120.5271 | 120.5334 | 120.6056 | 120.5214 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.033449 | 0.077504 | 0.10887 | 0.062 | 0.093361
5927.7812 | 122.3969 | -120.0714 | 2.0691 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.079959 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 120.1978 | 120.0721 | 120.064 | 120.0693 | 120.0756 | 120.1524 | 120.0636 | 0.12116 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5929.5 | 122.438 | -120.1813 | 1.9089 | 0.12643 | 0.000689 | -0.007421 | -0.006703 | 0.013375 | 0.076426 | 0.001377 | 0.070802 | 0.18453 | 0.046142 | -0.028522 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 120.3077 | 120.182 | 120.1739 | 120.1746 | 120.1946 | 120.2577 | 120.1827 | 0.112 | 0.22573 | 0.087341 | 0.012677 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.077504 | 0.10429 | 0.052844 | 0.079626
5931.2031 | 122.3373 | -120.0439 | 2.1332 | 0.12185 | 0.009846 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.07538 | 0.19369 | 0.05072 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.00775 | 120.1658 | 120.0538 | 120.0319 | 120.0418 | 120.0482 | 120.1249 | 120.0362 | 0.11658 | 0.23489 | 0.091919 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.033449 | 0.077504 | 0.10886 | 0.052844 | 0.084204
5932.9375 | 122.4426 | -120.2591 | 1.886 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 0.079959 | 0.17995 | 0.046142 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 120.3809 | 120.2689 | 120.2471 | 120.2615 | 120.2679 | 120.3447 | 120.2513 | 0.12116 | 0.22115 | 0.087341 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.057423 | 0.079626
5934.6875 | 122.3602 | -120.3598 | 1.8356 | 0.12643 | 0.009846 | -0.016578 | 0.007033 | 0.013375 | 0.085583 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 120.4862 | 120.3696 | 120.3432 | 120.3668 | 120.3732 | 120.4454 | 120.352 | 0.112 | 0.22115 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.082083 | 0.10429 | 0.062001 | 0.084204
5936.4219 | 122.3282 | -120.108 | 2.0828 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.2299 | 120.1133 | 120.096 | 120.1105 | 120.1123 | 120.189 | 120.1048 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.086661 | 0.10886 | 0.062001 | 0.084204
5938.1406 | 122.3419 | -120.0989 | 2.092 | 0.13559 | 0.009846 | -0.012 | -0.006703 | 0.013375 | 0.081005 | -0.003201 | 0.066223 | 0.17537 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 120.2345 | 120.1087 | 120.0869 | 120.0922 | 120.1123 | 120.1799 | 120.0957 | 0.10742 | 0.21657 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.077504 | 0.099707 | 0.066579 | 0.088782
5939.8906 | 122.2733 | -119.4855 | 2.6917 | 0.13559 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.079959 | 0.17537 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.028906 | -0.00775 | 119.6211 | 119.4907 | 119.4735 | 119.4879 | 119.4988 | 119.5665 | 119.4777 | 0.12116 | 0.21657 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.012293 | 0.033449 | 0.086661 | 0.10887 | 0.062 | 0.084204
5941.6406 | 122.3969 | -118.2266 | 3.8864 | 0.11727 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 118.3439 | 118.2319 | 118.2146 | 118.2291 | 118.2354 | 118.2985 | 118.2234 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5943.3594 | 122.3511 | -119.5633 | 2.6184 | 0.12643 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | 0.001377 | 0.07538 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.02322 | -0.042641 | -0.003172 | 119.6897 | 119.5686 | 119.5467 | 119.5612 | 119.5675 | 119.6443 | 119.5647 | 0.11658 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.064419 | -0.001442 | 0.038027 | 0.082082 | 0.11802 | 0.062 | 0.097939
5945.0625 | 122.4106 | -120.5154 | 1.6571 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.016936 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 120.6373 | 120.5161 | 120.508 | 120.5179 | 120.5242 | 120.5964 | 120.4985 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.086661 | 0.11344 | 0.062001 | 0.088783
5946.7812 | 122.3465 | -120.3278 | 1.8356 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.028522 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 120.4496 | 120.3376 | 120.3158 | 120.3302 | 120.3366 | 120.3996 | 120.3246 | 0.11658 | 0.22573 | 0.096497 | 0.012677 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.082082 | 0.10429 | 0.062 | 0.084204
5948.5781 | 122.4197 | -120.6253 | 1.5381 | 0.12643 | 0.005267 | -0.021157 | 0.002454 | 0.013375 | 0.076426 | 0.001377 | 0.07538 | 0.17995 | 0.046142 | -0.010206 | -0.006702 | 0.027798 | -0.038063 | -0.00775 | 120.7517 | 120.6306 | 120.6041 | 120.6278 | 120.6387 | 120.7017 | 120.6267 | 0.11658 | 0.22115 | 0.087341 | 0.030993 | 0.034497 | 0.068997 | 0.003136 | 0.033449 | 0.082082 | 0.11344 | 0.052844 | 0.084205
5950.2969 | 122.4426 | -120.5887 | 1.5518 | 0.11727 | 0.000689 | -0.021157 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.079959 | 0.18911 | 0.046142 | -0.019364 | 0.002454 | 0.032376 | -0.028906 | -0.00775 | 120.706 | 120.5894 | 120.5675 | 120.5866 | 120.5929 | 120.6697 | 120.5809 | 0.12116 | 0.23031 | 0.087341 | 0.021835 | 0.043653 | 0.073575 | 0.012293 | 0.033449 | 0.077505 | 0.10887 | 0.043688 | 0.075048
5952.0781 | 122.4701 | -120.4605 | 1.6479 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.090161 | 0.005955 | 0.084537 | 0.18453 | 0.055298 | -0.028522 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 120.5869 | 120.4658 | 120.4485 | 120.463 | 120.4693 | 120.5507 | 120.4665 | 0.12574 | 0.22573 | 0.096497 | 0.012677 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.062 | 0.088782
5953.7812 | 122.3419 | -120.5154 | 1.7075 | 0.12643 | 0.005267 | -0.016578 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 120.6419 | 120.5207 | 120.4989 | 120.5225 | 120.5242 | 120.5964 | 120.5122 | 0.11658 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5955.5156 | 122.3602 | -120.4559 | 1.7578 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.046142 | -0.019364 | -0.011281 | 0.02322 | -0.042641 | -0.003172 | 120.5778 | 120.4658 | 120.4394 | 120.4584 | 120.4647 | 120.5324 | 120.4482 | 0.12116 | 0.22115 | 0.087341 | 0.021835 | 0.029918 | 0.064419 | -0.001442 | 0.038027 | 0.09124 | 0.1226 | 0.057423 | 0.088783
5957.2188 | 122.374 | -120.4239 | 1.799 | 0.13559 | 0.000689 | -0.012 | 0.007033 | 0.008797 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 120.5595 | 120.4246 | 120.4119 | 120.4309 | 120.4327 | 120.5003 | 120.4161 | 0.12116 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.086661 | 0.11344 | 0.057422 | 0.084204
5958.9219 | 122.4655 | -120.314 | 1.886 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | -0.000359 | 0.076426 | -0.012357 | 0.079959 | 0.18911 | 0.046142 | -0.019364 | -0.006702 | 0.02322 | -0.038063 | -0.012328 | 120.4313 | 120.3147 | 120.2974 | 120.3165 | 120.3137 | 120.3905 | 120.3017 | 0.12116 | 0.23031 | 0.087341 | 0.021835 | 0.034497 | 0.064419 | 0.003136 | 0.028871 | 0.086661 | 0.11802 | 0.052844 | 0.084205
5960.6406 | 122.3511 | -119.8654 | 2.3987 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.079959 | 0.18453 | 0.064455 | -0.019364 | -0.002124 | 0.027798 | -0.033484 | -0.00775 | 119.9827 | 119.8661 | 119.8488 | 119.8679 | 119.8788 | 119.9464 | 119.8668 | 0.12116 | 0.22573 | 0.10565 | 0.021835 | 0.039075 | 0.068997 | 0.007715 | 0.033449 | 0.082083 | 0.11344 | 0.066579 | 0.097939
5962.3438 | 122.4564 | -120.0943 | 2.0645 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.004219 | 0.076426 | 0.001377 | 0.070802 | 0.18453 | 0.046142 | -0.023943 | -0.011281 | 0.02322 | -0.038063 | -0.003172 | 120.2207 | 120.095 | 120.0869 | 120.0922 | 120.0985 | 120.1707 | 120.0957 | 0.112 | 0.22573 | 0.087341 | 0.017256 | 0.029918 | 0.064419 | 0.003136 | 0.038027 | 0.082083 | 0.10887 | 0.057423 | 0.084205
5964.0469 | 122.3969 | -119.5267 | 2.6962 | 0.11727 | 0.000689 | -0.012 | 0.002454 | 0.013375 | 0.085583 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.014785 | 0.002454 | 0.032376 | -0.033484 | -0.003172 | 119.6439 | 119.5274 | 119.5147 | 119.5291 | 119.54 | 119.6123 | 119.5189 | 0.12116 | 0.23031 | 0.096497 | 0.026414 | 0.043653 | 0.073575 | 0.007715 | 0.038027 | 0.077505 | 0.11344 | 0.052844 | 0.088782
5965.75 | 122.4838 | -119.0643 | 3.0716 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.066223 | 0.17995 | 0.05072 | -0.028522 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 119.1908 | 119.065 | 119.0523 | 119.0622 | 119.0777 | 119.1453 | 119.0566 | 0.10742 | 0.22115 | 0.091919 | 0.012677 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 0.077504 | 0.095129 | 0.062001 | 0.079626
5967.5469 | 122.4335 | -119.0598 | 3.1265 | 0.12185 | -0.00389 | -0.002842 | -0.006703 | 0.004219 | 0.081005 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.002124 | 0.027798 | -0.038063 | -0.003172 | 119.1816 | 119.0559 | 119.0569 | 119.053 | 119.064 | 119.1408 | 119.052 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.039075 | 0.068997 | 0.003136 | 0.038027 | 0.077504 | 0.11344 | 0.052844 | 0.088783
5969.2812 | 122.4472 | -118.1213 | 4.01 | 0.12643 | 0.005267 | -0.007421 | -0.011281 | 0.013375 | 0.076426 | -0.012357 | 0.070802 | 0.17995 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.04722 | -0.00775 | 118.2478 | 118.1266 | 118.1139 | 118.1101 | 118.1347 | 118.1978 | 118.109 | 0.112 | 0.22115 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | -0.006021 | 0.033449 | 0.077504 | 0.11802 | 0.062 | 0.10252
5970.9844 | 122.3694 | -120.2179 | 2.0096 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.028522 | -0.002124 | 0.027798 | -0.042641 | -0.00775 | 120.3397 | 120.2232 | 120.2059 | 120.2158 | 120.2221 | 120.2943 | 120.2101 | 0.12116 | 0.22115 | 0.096497 | 0.012677 | 0.039075 | 0.068997 | -0.001442 | 0.033449 | 0.082083 | 0.1226 | 0.057422 | 0.097939
5972.7188 | 122.4838 | -120.1355 | 2.0142 | 0.13101 | 0.005267 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.012357 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 120.2665 | 120.1408 | 120.1235 | 120.1334 | 120.1489 | 120.2211 | 120.1231 | 0.112 | 0.22115 | 0.091919 | 0.012677 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.077504 | 0.10429 | 0.057422 | 0.084204
5974.4219 | 122.3923 | -119.6732 | 2.5131 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.033101 | -0.006702 | 0.032376 | -0.033484 | -0.00775 | 119.795 | 119.683 | 119.6566 | 119.6756 | 119.682 | 119.7496 | 119.67 | 0.11658 | 0.21657 | 0.091919 | 0.008098 | 0.034497 | 0.073575 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.057422 | 0.084204
5976.125 | 122.3694 | -119.1238 | 3.1174 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.019364 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 119.2457 | 119.1245 | 119.1164 | 119.1263 | 119.1326 | 119.2048 | 119.1161 | 0.112 | 0.22573 | 0.096497 | 0.021835 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.082083 | 0.10429 | 0.066579 | 0.088782
5977.8594 | 122.3648 | -119.9295 | 2.2888 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.071848 | 0.001377 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.003172 | 120.0514 | 119.9302 | 119.9221 | 119.932 | 119.9383 | 120.0014 | 119.9309 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.038027 | 0.086661 | 0.10886 | 0.062001 | 0.084204
5979.5625 | 122.3648 | -119.4763 | 2.7603 | 0.11727 | 0.000689 | -0.007421 | -0.006703 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.18911 | 0.05072 | -0.019364 | -0.011281 | 0.02322 | -0.038063 | -0.00775 | 119.5936 | 119.477 | 119.4689 | 119.4696 | 119.4897 | 119.5573 | 119.4731 | 0.112 | 0.23031 | 0.091919 | 0.021835 | 0.029918 | 0.064419 | 0.003136 | 0.033449 | 0.082083 | 0.10887 | 0.062001 | 0.088783
5981.2812 | 122.3602 | -119.1284 | 3.1265 | 0.12185 | 0.000689 | -0.012 | 0.007033 | 0.013375 | 0.076426 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.028906 | -0.012328 | 119.2503 | 119.1291 | 119.1164 | 119.1355 | 119.1418 | 119.2048 | 119.1252 | 0.11658 | 0.22115 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.012293 | 0.028871 | 0.086661 | 0.10429 | 0.062001 | 0.079626
5982.9844 | 122.4701 | -119.3069 | 2.8336 | 0.11727 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.011281 | 0.02322 | -0.038063 | -0.00775 | 119.4242 | 119.3076 | 119.2904 | 119.3094 | 119.3157 | 119.388 | 119.2946 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.029918 | 0.064419 | 0.003136 | 0.033449 | 0.086661 | 0.11344 | 0.062001 | 0.088783
5984.7188 | 122.4838 | -119.2703 | 2.9022 | 0.12643 | -0.00389 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.046142 | -0.019364 | -0.015859 | 0.032376 | -0.033484 | -0.003172 | 119.3968 | 119.2664 | 119.2629 | 119.2728 | 119.2791 | 119.3513 | 119.2671 | 0.12116 | 0.22573 | 0.087341 | 0.021835 | 0.02534 | 0.073575 | 0.007715 | 0.038027 | 0.095818 | 0.11344 | 0.062001 | 0.079626
5986.4219 | 122.4014 | -119.5175 | 2.7191 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.084537 | 0.18911 | 0.055298 | -0.028522 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 119.6439 | 119.5274 | 119.5101 | 119.5154 | 119.5263 | 119.5985 | 119.5097 | 0.12574 | 0.23031 | 0.096497 | 0.012677 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.091239 | 0.1226 | 0.062 | 0.093361
5988.1562 | 122.5113 | -119.6091 | 2.5772 | 0.12643 | -0.00389 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.18911 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 119.7355 | 119.6052 | 119.5971 | 119.6115 | 119.6179 | 119.6901 | 119.6059 | 0.11658 | 0.23031 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.086661 | 0.10886 | 0.062001 | 0.084204
5989.8594 | 122.374 | -117.4393 | 4.7333 | 0.13101 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.046142 | -0.019364 | -0.006702 | 0.02322 | -0.038063 | -0.00775 | 117.5703 | 117.44 | 117.4273 | 117.4371 | 117.4435 | 117.5157 | 117.4315 | 0.112 | 0.22573 | 0.087341 | 0.021835 | 0.034497 | 0.064419 | 0.003136 | 0.033449 | 0.077504 | 0.10887 | 0.052844 | 0.084205
5991.6094 | 122.438 | -119.3802 | 2.7695 | 0.11727 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | 0.001406 | 119.4975 | 119.3809 | 119.3682 | 119.3735 | 119.389 | 119.4566 | 119.377 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.042605 | 0.086661 | 0.11344 | 0.062001 | 0.088783
5993.2969 | 122.4152 | -119.5541 | 2.6871 | 0.11727 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.012357 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 119.6714 | 119.564 | 119.5376 | 119.5566 | 119.5629 | 119.6397 | 119.5418 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 0.082083 | 0.099708 | 0.066579 | 0.084204
5995.0312 | 122.3557 | -119.5908 | 2.6779 | 0.11727 | 0.005267 | -0.012 | -0.006703 | 0.004219 | 0.076426 | -0.003201 | 0.070802 | 0.17537 | 0.046142 | -0.019364 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 119.708 | 119.596 | 119.5788 | 119.5841 | 119.595 | 119.6672 | 119.5876 | 0.112 | 0.21657 | 0.087341 | 0.021835 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 0.082083 | 0.099708 | 0.057423 | 0.075048
5996.7812 | 122.3831 | -119.2841 | 2.98 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.046142 | -0.023943 | -0.011281 | 0.027798 | -0.028906 | -0.003172 | 119.4105 | 119.2847 | 119.2766 | 119.2865 | 119.2929 | 119.3651 | 119.2809 | 0.11658 | 0.22573 | 0.087341 | 0.017256 | 0.029918 | 0.068997 | 0.012293 | 0.038027 | 0.086661 | 0.10429 | 0.057423 | 0.075048
5998.4844 | 122.406 | -119.5633 | 2.6642 | 0.13101 | -0.00389 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.079959 | 0.17995 | 0.046142 | -0.028522 | -0.002124 | 0.027798 | -0.042641 | -0.012328 | 119.6943 | 119.5594 | 119.5467 | 119.5657 | 119.5675 | 119.6443 | 119.5555 | 0.12116 | 0.22115 | 0.087341 | 0.012677 | 0.039075 | 0.068997 | -0.001442 | 0.028871 | 0.082083 | 0.1226 | 0.048266 | 0.088783
6000.1875 | 122.4792 | -119.8196 | 2.3483 | 0.13101 | 0.005267 | -0.002842 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.079959 | 0.18911 | 0.05072 | -0.019364 | -0.006702 | 0.02322 | -0.028906 | -0.00775 | 119.9506 | 119.8249 | 119.8168 | 119.8221 | 119.8239 | 119.9006 | 119.8164 | 0.12116 | 0.23031 | 0.091919 | 0.021835 | 0.034497 | 0.064419 | 0.012293 | 0.033449 | 0.086661 | 0.10887 | 0.057422 | 0.079626
6001.8906 | 122.4152 | -120.0119 | 2.2705 | 0.12185 | 0.000689 | -0.012 | 0.007033 | 0.004219 | 0.081005 | -0.012357 | 0.061645 | 0.18453 | 0.046142 | -0.014785 | -0.011281 | 0.018642 | -0.033484 | 0.001406 | 120.1338 | 120.0126 | 119.9999 | 120.0189 | 120.0161 | 120.0929 | 119.9995 | 0.10284 | 0.22573 | 0.087341 | 0.026414 | 0.029918 | 0.059841 | 0.007715 | 0.042605 | 0.072926 | 0.095129 | 0.057423 | 0.079626
6003.6406 | 122.3877 | -119.8563 | 2.4307 | 0.12643 | 0.000689 | -0.007421 | 0.011611 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.028906 | 0.001406 | 119.9827 | 119.857 | 119.8488 | 119.8679 | 119.8651 | 119.9373 | 119.8531 | 0.11658 | 0.21657 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.012293 | 0.042605 | 0.082082 | 0.10429 | 0.057422 | 0.079626
6005.3438 | 122.4655 | -119.4122 | 2.7969 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.002124 | 0.02322 | -0.033484 | -0.003172 | 119.5387 | 119.4129 | 119.4002 | 119.4101 | 119.4256 | 119.4932 | 119.4045 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.039075 | 0.064419 | 0.007715 | 0.038027 | 0.077504 | 0.10886 | 0.052844 | 0.084204
6007.0469 | 122.4335 | -119.5496 | 2.7237 | 0.11727 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.07538 | 0.17537 | 0.046142 | -0.023943 | -0.006702 | 0.02322 | -0.038063 | -0.003172 | 119.6668 | 119.5548 | 119.533 | 119.5474 | 119.5538 | 119.6306 | 119.5372 | 0.11658 | 0.21657 | 0.087341 | 0.017256 | 0.034497 | 0.064419 | 0.003136 | 0.038027 | 0.082082 | 0.11344 | 0.052844 | 0.084205
6008.75 | 122.438 | -119.7418 | 2.449 | 0.12643 | 0.000689 | -0.007421 | 0.007033 | 0.008797 | 0.076426 | -0.003201 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 119.8683 | 119.7425 | 119.7344 | 119.7489 | 119.7506 | 119.8182 | 119.7386 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.082083 | 0.10429 | 0.066579 | 0.088782
6010.4844 | 122.4243 | -119.8334 | 2.3941 | 0.12643 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.019364 | -0.006702 | 0.027798 | -0.038063 | -0.012328 | 119.9598 | 119.8432 | 119.8214 | 119.8358 | 119.8422 | 119.9144 | 119.8302 | 0.112 | 0.22573 | 0.091919 | 0.021835 | 0.034497 | 0.068997 | 0.003136 | 0.028871 | 0.077504 | 0.10887 | 0.057422 | 0.088783
6012.1875 | 122.5204 | -120.0302 | 2.1835 | 0.12185 | 0.005267 | -0.007421 | 0.007033 | 0.017953 | 0.085583 | -0.003201 | 0.079959 | 0.17995 | 0.046142 | -0.019364 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 120.1521 | 120.0355 | 120.0228 | 120.0372 | 120.0482 | 120.1158 | 120.027 | 0.12116 | 0.22115 | 0.087341 | 0.021835 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.086661 | 0.11802 | 0.052844 | 0.084205
6013.8906 | 122.4152 | -119.9799 | 2.3071 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.059877 | -0.023943 | -0.011281 | 0.036954 | -0.028906 | -0.00775 | 120.1017 | 119.9805 | 119.9679 | 119.9777 | 119.9932 | 120.0609 | 119.9767 | 0.112 | 0.22573 | 0.10108 | 0.017256 | 0.029918 | 0.078153 | 0.012293 | 0.033449 | 0.082083 | 0.099708 | 0.071158 | 0.088783
6015.6406 | 122.438 | -119.8059 | 2.3895 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.028522 | -0.006702 | 0.02322 | -0.038063 | -0.00775 | 119.9278 | 119.8112 | 119.7985 | 119.8084 | 119.8147 | 119.8915 | 119.8027 | 0.11658 | 0.22115 | 0.087341 | 0.012677 | 0.034497 | 0.064419 | 0.003136 | 0.033449 | 0.082082 | 0.11344 | 0.052844 | 0.084205
6017.3438 | 122.438 | -119.9432 | 2.3346 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.090161 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.019364 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 120.0651 | 119.9485 | 119.9312 | 119.9411 | 119.952 | 120.0334 | 119.9355 | 0.11658 | 0.22115 | 0.091919 | 0.021835 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.057422 | 0.084204
6019.0781 | 122.5571 | -119.9112 | 2.3026 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.084537 | 0.17995 | 0.055298 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | -0.00775 | 120.033 | 119.9119 | 119.8992 | 119.9091 | 119.92 | 119.9968 | 119.9034 | 0.12574 | 0.22115 | 0.096497 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.033449 | 0.091239 | 0.1226 | 0.062 | 0.093361
6020.7812 | 122.525 | -119.8791 | 2.3712 | 0.12643 | 0.005267 | -0.016578 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.059877 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 120.0056 | 119.8844 | 119.8626 | 119.877 | 119.8925 | 119.9602 | 119.8714 | 0.12116 | 0.22573 | 0.10108 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.086661 | 0.11344 | 0.066579 | 0.093361
6022.4844 | 122.406 | -119.8151 | 2.4857 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.079959 | 0.17537 | 0.05072 | -0.028522 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 119.9369 | 119.8158 | 119.8076 | 119.8129 | 119.8239 | 119.8915 | 119.8119 | 0.12116 | 0.21657 | 0.091919 | 0.012677 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.057422 | 0.084204
6024.2188 | 122.4472 | -120.1401 | 2.1103 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.055298 | -0.019364 | -0.011281 | 0.02322 | -0.033484 | -0.00775 | 120.2619 | 120.1453 | 120.1281 | 120.1425 | 120.1489 | 120.2211 | 120.1323 | 0.112 | 0.22115 | 0.096497 | 0.021835 | 0.029918 | 0.064419 | 0.007715 | 0.033449 | 0.082083 | 0.10429 | 0.066579 | 0.088782
6025.9219 | 122.5067 | -119.9295 | 2.2751 | 0.13101 | 0.000689 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.028522 | -0.006702 | 0.032376 | -0.038063 | -0.00775 | 120.0605 | 119.9302 | 119.9175 | 119.932 | 119.9429 | 120.0105 | 119.9217 | 0.112 | 0.22115 | 0.087341 | 0.012677 | 0.034497 | 0.073575 | 0.003136 | 0.033449 | 0.077504 | 0.10887 | 0.052844 | 0.084205
6027.625 | 122.5159 | -119.7784 | 2.449 | 0.12185 | 0.009846 | -0.002842 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.028522 | -0.011281 | 0.032376 | -0.028906 | 0.001406 | 119.9003 | 119.7883 | 119.7756 | 119.7809 | 119.7872 | 119.864 | 119.7707 | 0.11658 | 0.22115 | 0.091919 | 0.012677 | 0.029918 | 0.073575 | 0.012293 | 0.042605 | 0.086661 | 0.10429 | 0.062001 | 0.079626
6029.3438 | 122.3969 | -119.6548 | 2.6505 | 0.11727 | 0.009846 | -0.012 | 0.007033 | 0.017953 | 0.085583 | -0.007779 | 0.07538 | 0.18911 | 0.055298 | -0.019364 | -0.002124 | 0.032376 | -0.038063 | -0.003172 | 119.7721 | 119.6647 | 119.6428 | 119.6619 | 119.6728 | 119.7404 | 119.6471 | 0.11658 | 0.23031 | 0.096497 | 0.021835 | 0.039075 | 0.073575 | 0.003136 | 0.038027 | 0.077504 | 0.11344 | 0.057422 | 0.093361
6031.0781 | 122.4335 | -119.5633 | 2.7191 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.090161 | -0.007779 | 0.07538 | 0.17995 | 0.055298 | -0.023943 | -0.002124 | 0.032376 | -0.028906 | -0.003172 | 119.6897 | 119.5686 | 119.5559 | 119.5612 | 119.5721 | 119.6535 | 119.5555 | 0.11658 | 0.22115 | 0.096497 | 0.017256 | 0.039075 | 0.073575 | 0.012293 | 0.038027 | 0.077504 | 0.10429 | 0.057422 | 0.084204
6032.7969 | 122.3831 | -119.4168 | 2.8931 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.003172 | 119.5432 | 119.4175 | 119.4048 | 119.4147 | 119.4256 | 119.4887 | 119.4136 | 0.11658 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.038027 | 0.082082 | 0.10429 | 0.062 | 0.084204
6034.5625 | 122.4197 | -120.3781 | 1.9135 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.084537 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 120.5045 | 120.3834 | 120.3661 | 120.3806 | 120.3869 | 120.45 | 120.3749 | 0.12574 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.091239 | 0.11802 | 0.062 | 0.088782
6036.2656 | 122.493 | -120.2408 | 2.0142 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.066223 | 0.17995 | 0.046142 | -0.028522 | -0.011281 | 0.027798 | -0.038063 | 0.001406 | 120.3672 | 120.2461 | 120.2288 | 120.2387 | 120.2496 | 120.3218 | 120.2284 | 0.10742 | 0.22115 | 0.087341 | 0.012677 | 0.029918 | 0.068997 | 0.003136 | 0.042605 | 0.077504 | 0.10429 | 0.057423 | 0.084205
6037.9688 | 122.4518 | -120.2591 | 2.0325 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | 0.001377 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.015859 | 0.027798 | -0.033484 | 0.001406 | 120.3855 | 120.2644 | 120.2471 | 120.257 | 120.2679 | 120.3355 | 120.2605 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.02534 | 0.068997 | 0.007715 | 0.042605 | 0.091239 | 0.10886 | 0.066579 | 0.084204
6039.7031 | 122.4335 | -120.2728 | 2.0325 | 0.13559 | 0.009846 | -0.007421 | 0.011611 | 0.017953 | 0.081005 | -0.003201 | 0.079959 | 0.17995 | 0.055298 | -0.028522 | -0.002124 | 0.02322 | -0.038063 | -0.003172 | 120.4084 | 120.2827 | 120.2654 | 120.2844 | 120.2908 | 120.3538 | 120.2696 | 0.12116 | 0.22115 | 0.096497 | 0.012677 | 0.039075 | 0.064419 | 0.003136 | 0.038027 | 0.082083 | 0.11802 | 0.057422 | 0.093361
6041.4062 | 122.4976 | -120.108 | 2.1378 | 0.11727 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.079959 | 0.18911 | 0.055298 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 120.2253 | 120.1133 | 120.096 | 120.1059 | 120.1168 | 120.1845 | 120.1048 | 0.12116 | 0.23031 | 0.096497 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 0.09124 | 0.11802 | 0.066579 | 0.093361
6043.1406 | 122.438 | -120.108 | 2.179 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.070802 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.038063 | -0.003172 | 120.2299 | 120.1179 | 120.096 | 120.1105 | 120.1168 | 120.189 | 120.0957 | 0.112 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.003136 | 0.038027 | 0.077504 | 0.10887 | 0.062 | 0.093361
6044.8438 | 122.4609 | -119.9707 | 2.3254 | 0.12643 | 0.005267 | -0.007421 | 0.007033 | 0.004219 | 0.081005 | -0.007779 | 0.079959 | 0.18911 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 120.0971 | 119.976 | 119.9633 | 119.9777 | 119.9749 | 120.0517 | 119.9629 | 0.12116 | 0.23031 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.062 | 0.088782
6046.5469 | 122.5571 | -119.9158 | 2.33 | 0.12643 | -0.00389 | -0.012 | 0.002454 | -0.000359 | 0.085583 | -0.012357 | 0.07538 | 0.18911 | 0.046142 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 120.0422 | 119.9119 | 119.9038 | 119.9182 | 119.9154 | 120.0014 | 119.9034 | 0.11658 | 0.23031 | 0.087341 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.082082 | 0.10886 | 0.052844 | 0.079626
6048.2656 | 122.5662 | -119.7601 | 2.4902 | 0.12185 | 0.014425 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.007779 | 0.07538 | 0.18453 | 0.041563 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.012328 | 119.882 | 119.7746 | 119.7481 | 119.758 | 119.7644 | 119.8411 | 119.7524 | 0.11658 | 0.22573 | 0.082762 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.028871 | 0.086661 | 0.11344 | 0.052844 | 0.079626
6049.9688 | 122.4243 | -120.2225 | 2.0828 | 0.12643 | 0.009846 | -0.012 | -0.006703 | 0.013375 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.012328 | 120.3489 | 120.2323 | 120.2105 | 120.2158 | 120.2358 | 120.3035 | 120.2147 | 0.12116 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.028871 | 0.09124 | 0.11802 | 0.066579 | 0.093361
6051.6719 | 122.4518 | -120.076 | 2.2339 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.090161 | -0.003201 | 0.070802 | 0.18911 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.033484 | -0.003172 | 120.1978 | 120.0813 | 120.064 | 120.0739 | 120.0802 | 120.1662 | 120.0728 | 0.112 | 0.23031 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.007715 | 0.038027 | 0.077504 | 0.10429 | 0.062 | 0.088782
6053.3906 | 122.4472 | -119.8837 | 2.3849 | 0.12185 | -0.00389 | -0.012 | -0.002124 | 0.008797 | 0.076426 | 0.001377 | 0.070802 | 0.17995 | 0.05072 | -0.019364 | 0.002454 | 0.027798 | -0.038063 | -0.003172 | 120.0056 | 119.8798 | 119.8717 | 119.8816 | 119.8925 | 119.9602 | 119.8851 | 0.112 | 0.22115 | 0.091919 | 0.021835 | 0.043653 | 0.068997 | 0.003136 | 0.038027 | 0.068348 | 0.10887 | 0.048266 | 0.088783
6055.0938 | 122.4289 | -119.9387 | 2.3804 | 0.12185 | 0.009846 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.084537 | 0.18911 | 0.055298 | -0.028522 | -0.011281 | 0.027798 | -0.028906 | -0.00775 | 120.0605 | 119.9485 | 119.9267 | 119.9365 | 119.952 | 120.0197 | 119.9309 | 0.12574 | 0.23031 | 0.096497 | 0.012677 | 0.029918 | 0.068997 | 0.012293 | 0.033449 | 0.095818 | 0.11344 | 0.066579 | 0.084204
6056.8125 | 122.5754 | -119.6045 | 2.6276 | 0.12185 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.019364 | -0.015859 | 0.02322 | -0.033484 | -0.00775 | 119.7263 | 119.6052 | 119.5925 | 119.6069 | 119.6087 | 119.6855 | 119.6013 | 0.11658 | 0.21657 | 0.091919 | 0.021835 | 0.02534 | 0.064419 | 0.007715 | 0.033449 | 0.091239 | 0.10886 | 0.066579 | 0.084204
6058.5781 | 122.4197 | -119.5862 | 2.7649 | 0.12185 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 119.708 | 119.596 | 119.5788 | 119.5841 | 119.595 | 119.6672 | 119.5784 | 0.112 | 0.22115 | 0.091919 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.082083 | 0.10887 | 0.062001 | 0.088783
6060.2812 | 122.493 | -119.3069 | 2.9388 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.076426 | -0.012357 | 0.07538 | 0.18453 | 0.05072 | -0.028522 | -0.011281 | 0.032376 | -0.042641 | -0.003172 | 119.4334 | 119.3122 | 119.2904 | 119.3094 | 119.3157 | 119.3834 | 119.2946 | 0.11658 | 0.22573 | 0.091919 | 0.012677 | 0.029918 | 0.073575 | -0.001442 | 0.038027 | 0.086661 | 0.11802 | 0.062001 | 0.093361
6062 | 122.5067 | -119.8105 | 2.449 | 0.12185 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.015859 | 0.032376 | -0.042641 | -0.003172 | 119.9323 | 119.8158 | 119.7985 | 119.8084 | 119.8193 | 119.8869 | 119.8027 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | 0.02534 | 0.073575 | -0.001442 | 0.038027 | 0.082082 | 0.10886 | 0.062001 | 0.088783
6063.6875 | 122.4243 | -119.6915 | 2.623 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.028522 | -0.002124 | 0.032376 | -0.042641 | -0.003172 | 119.8179 | 119.6876 | 119.6795 | 119.6893 | 119.7048 | 119.7771 | 119.6837 | 0.11658 | 0.22573 | 0.091919 | 0.012677 | 0.039075 | 0.073575 | -0.001442 | 0.038027 | 0.077504 | 0.11802 | 0.052844 | 0.093361
6065.3906 | 122.5204 | -119.8196 | 2.4719 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.079959 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 119.9415 | 119.8249 | 119.8076 | 119.8129 | 119.8284 | 119.9006 | 119.8073 | 0.12116 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.09124 | 0.11344 | 0.062001 | 0.084204
6067.0938 | 122.4472 | -119.5038 | 2.7969 | 0.12185 | 0.005267 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | -0.012357 | 0.070802 | 0.18453 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.012328 | 119.6256 | 119.5091 | 119.4872 | 119.4971 | 119.5126 | 119.5848 | 119.4914 | 0.112 | 0.22573 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.028871 | 0.082083 | 0.10887 | 0.062001 | 0.088783
6068.7969 | 122.4518 | -119.8563 | 2.4399 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.18911 | 0.05072 | -0.028522 | -0.002124 | 0.032376 | -0.038063 | 0.001406 | 119.9781 | 119.8615 | 119.8397 | 119.8541 | 119.8651 | 119.9373 | 119.8531 | 0.10742 | 0.23031 | 0.091919 | 0.012677 | 0.039075 | 0.073575 | 0.003136 | 0.042605 | 0.068347 | 0.10429 | 0.052844 | 0.088783
6070.5625 | 122.5113 | -119.4672 | 2.8152 | 0.13101 | 0.005267 | -0.016578 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.028522 | -0.011281 | 0.027798 | -0.042641 | -0.003172 | 119.5982 | 119.4724 | 119.4506 | 119.4742 | 119.476 | 119.5482 | 119.464 | 0.11658 | 0.22115 | 0.087341 | 0.012677 | 0.029918 | 0.068997 | -0.001442 | 0.038027 | 0.086661 | 0.11802 | 0.057423 | 0.088783
6072.2656 | 122.5159 | -119.9936 | 2.2659 | 0.12185 | 0.000689 | -0.012 | 0.007033 | -0.000359 | 0.076426 | -0.003201 | 0.07538 | 0.17537 | 0.041563 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.1154 | 119.9943 | 119.9816 | 120.0006 | 119.9932 | 120.07 | 119.9904 | 0.11658 | 0.21657 | 0.082762 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.086661 | 0.10886 | 0.052844 | 0.075047
6073.9688 | 122.5204 | -119.7739 | 2.5131 | 0.13101 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.046142 | -0.019364 | -0.015859 | 0.032376 | -0.028906 | -0.012328 | 119.9049 | 119.7791 | 119.7619 | 119.7717 | 119.7781 | 119.8503 | 119.7661 | 0.11658 | 0.22115 | 0.087341 | 0.021835 | 0.02534 | 0.073575 | 0.012293 | 0.028871 | 0.091239 | 0.10429 | 0.062001 | 0.075048
6075.6719 | 122.493 | -119.6045 | 2.7191 | 0.12185 | 0.009846 | -0.012 | 0.002454 | -0.000359 | 0.090161 | -0.003201 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 119.7263 | 119.6143 | 119.5925 | 119.6069 | 119.6041 | 119.6947 | 119.6013 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.082083 | 0.10429 | 0.066579 | 0.088782
6077.3906 | 122.493 | -119.4855 | 2.8152 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 119.6119 | 119.4862 | 119.4735 | 119.4879 | 119.4988 | 119.5619 | 119.4823 | 0.11658 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.086661 | 0.10886 | 0.066579 | 0.088782
6079.1094 | 122.4243 | -119.8425 | 2.4948 | 0.11727 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.011281 | 0.036954 | -0.038063 | -0.003172 | 119.9598 | 119.8478 | 119.8351 | 119.845 | 119.8513 | 119.9235 | 119.8347 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.029918 | 0.078153 | 0.003136 | 0.038027 | 0.086661 | 0.11344 | 0.062001 | 0.088783
6080.8125 | 122.438 | -120.369 | 1.9958 | 0.12185 | 0.009846 | -0.002842 | -0.002124 | -0.000359 | 0.081005 | 0.001377 | 0.07538 | 0.18453 | 0.046142 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.00775 | 120.4908 | 120.3788 | 120.3661 | 120.3668 | 120.3686 | 120.45 | 120.3703 | 0.11658 | 0.22573 | 0.087341 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.033449 | 0.086661 | 0.10886 | 0.057423 | 0.079626
6082.5156 | 122.5525 | -119.751 | 2.5223 | 0.12185 | 0.009846 | -0.007421 | 0.002454 | 0.017953 | 0.081005 | -0.007779 | 0.079959 | 0.17995 | 0.046142 | -0.019364 | -0.011281 | 0.041532 | -0.038063 | -0.003172 | 119.8728 | 119.7608 | 119.7436 | 119.7534 | 119.7689 | 119.832 | 119.7432 | 0.12116 | 0.22115 | 0.087341 | 0.021835 | 0.029918 | 0.082731 | 0.003136 | 0.038027 | 0.09124 | 0.11802 | 0.057423 | 0.084205
6084.2188 | 122.4472 | -119.8563 | 2.4948 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.017953 | 0.085583 | -0.003201 | 0.079959 | 0.17995 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.028906 | -0.012328 | 119.9827 | 119.8615 | 119.8443 | 119.8587 | 119.8742 | 119.9418 | 119.8531 | 0.12116 | 0.22115 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.012293 | 0.028871 | 0.086661 | 0.10887 | 0.062 | 0.084204
6085.9375 | 122.4655 | -119.8471 | 2.4994 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.18911 | 0.055298 | -0.019364 | -0.011281 | 0.02322 | -0.028906 | -0.003172 | 119.9735 | 119.857 | 119.8397 | 119.845 | 119.8605 | 119.9281 | 119.8439 | 0.112 | 0.23031 | 0.096497 | 0.021835 | 0.029918 | 0.064419 | 0.012293 | 0.038027 | 0.082083 | 0.099708 | 0.066579 | 0.084204
6087.6562 | 122.5662 | -119.6869 | 2.536 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.071848 | -0.007779 | 0.07538 | 0.18453 | 0.041563 | -0.019364 | -0.011281 | 0.032376 | -0.033484 | -0.003172 | 119.8133 | 119.6876 | 119.6749 | 119.6848 | 119.6911 | 119.7587 | 119.6791 | 0.11658 | 0.22573 | 0.082762 | 0.021835 | 0.029918 | 0.073575 | 0.007715 | 0.038027 | 0.086661 | 0.10886 | 0.052844 | 0.075047
6089.3594 | 122.5708 | -119.6732 | 2.5955 | 0.11727 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.036954 | -0.038063 | -0.00775 | 119.7904 | 119.6784 | 119.6612 | 119.6756 | 119.682 | 119.7542 | 119.67 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.078153 | 0.003136 | 0.033449 | 0.082082 | 0.11344 | 0.057422 | 0.088783
6091.0625 | 122.5616 | -119.3985 | 2.8427 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.006702 | 0.027798 | -0.042641 | -0.00775 | 119.5249 | 119.3946 | 119.3865 | 119.3964 | 119.4027 | 119.4841 | 119.3907 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.034497 | 0.068997 | -0.001442 | 0.033449 | 0.082082 | 0.11802 | 0.057422 | 0.093361
6092.7656 | 122.5067 | -119.8013 | 2.4948 | 0.11727 | 0.000689 | -0.012 | 0.002454 | 0.017953 | 0.076426 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 119.9186 | 119.802 | 119.7893 | 119.8038 | 119.8193 | 119.8778 | 119.7936 | 0.112 | 0.22115 | 0.087341 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 0.082083 | 0.10887 | 0.057423 | 0.084205
6094.4844 | 122.4564 | -119.7922 | 2.5589 | 0.12185 | -0.00389 | -0.012 | -0.006703 | 0.004219 | 0.081005 | 0.005955 | 0.079959 | 0.18453 | 0.055298 | -0.023943 | -0.011281 | 0.02322 | -0.042641 | -0.003172 | 119.914 | 119.7883 | 119.7802 | 119.7855 | 119.7964 | 119.8732 | 119.7981 | 0.12116 | 0.22573 | 0.096497 | 0.017256 | 0.029918 | 0.064419 | -0.001442 | 0.038027 | 0.09124 | 0.1226 | 0.066579 | 0.097939
6096.1875 | 121.8338 | -118.9362 | 2.1286 | 0.12185 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.070802 | 0.17537 | 0.046142 | -0.028522 | -0.020437 | 0.02322 | -0.038063 | -0.012328 | 119.058 | 118.9368 | 118.9242 | 118.9386 | 118.9404 | 119.0172 | 118.9284 | 0.112 | 0.21657 | 0.087341 | 0.012677 | 0.020762 | 0.064419 | 0.003136 | 0.028871 | 0.091239 | 0.10887 | 0.066579 | 0.084205
6097.8906 | 122.0901 | -108.9157 | 12.8677 | 0.12185 | 0.005267 | -0.016578 | 0.007033 | -0.000359 | 0.085583 | -0.007779 | 0.07538 | 0.17995 | 0.055298 | -0.023943 | -0.002124 | 0.036954 | -0.042641 | -0.003172 | 109.0376 | 108.921 | 108.8991 | 108.9227 | 108.9154 | 109.0013 | 108.9079 | 0.11658 | 0.22115 | 0.096497 | 0.017256 | 0.039075 | 0.078153 | -0.001442 | 0.038027 | 0.077504 | 0.11802 | 0.057422 | 0.097939
6099.6406 | 122.3145 | -120.4788 | 1.3779 | 0.13101 | 0.000689 | -0.007421 | -0.002124 | -0.000359 | 0.085583 | -0.007779 | 0.07538 | 0.18453 | 0.055298 | -0.019364 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 120.6098 | 120.4795 | 120.4714 | 120.4767 | 120.4785 | 120.5644 | 120.471 | 0.11658 | 0.22573 | 0.096497 | 0.021835 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.062 | 0.088782
6101.3438 | 122.2183 | -120.5612 | 1.4374 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.17079 | 0.036985 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 120.6876 | 120.5619 | 120.5492 | 120.5591 | 120.57 | 120.6376 | 120.558 | 0.11658 | 0.21199 | 0.078184 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.082082 | 0.10886 | 0.043687 | 0.070469
6103.0625 | 122.2458 | -120.6345 | 1.442 | 0.12643 | -0.00389 | -0.002842 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.02322 | -0.038063 | -0.003172 | 120.7609 | 120.6306 | 120.6316 | 120.6323 | 120.6387 | 120.7155 | 120.6313 | 0.12116 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.064419 | 0.003136 | 0.038027 | 0.086661 | 0.11802 | 0.052844 | 0.084205
6104.7656 | 122.3694 | -120.6024 | 1.442 | 0.12185 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.011281 | 0.036954 | -0.038063 | -0.00775 | 120.7243 | 120.6031 | 120.5904 | 120.5957 | 120.6112 | 120.6788 | 120.5946 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.029918 | 0.078153 | 0.003136 | 0.033449 | 0.086661 | 0.11344 | 0.062001 | 0.088783
6106.5 | 122.2916 | -118.5791 | 3.5202 | 0.11727 | 0.009846 | -0.002842 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 118.6964 | 118.5889 | 118.5763 | 118.5816 | 118.5879 | 118.6647 | 118.5759 | 0.11658 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 0.082082 | 0.10429 | 0.052844 | 0.075048
6108.2031 | 122.3602 | -94.3588 | 27.5116 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.004219 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.041563 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | -0.003172 | 94.4807 | 94.3687 | 94.3422 | 94.3613 | 94.363 | 94.4353 | 94.351 | 0.112 | 0.22573 | 0.082762 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.038027 | 0.077504 | 0.10887 | 0.048265 | 0.079626
6109.9219 | 122.3419 | -120.6253 | 1.4923 | 0.12643 | 0.000689 | -0.007421 | 0.007033 | 0.013375 | 0.081005 | 0.001377 | 0.07538 | 0.18911 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.012328 | 120.7517 | 120.626 | 120.6179 | 120.6323 | 120.6387 | 120.7063 | 120.6267 | 0.11658 | 0.23031 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.028871 | 0.082082 | 0.10886 | 0.057422 | 0.084204
6111.6406 | 122.3511 | -113.7634 | 8.2535 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.006702 | 0.032376 | -0.038063 | 0.001406 | 113.8899 | 113.7687 | 113.7514 | 113.7659 | 113.7768 | 113.8444 | 113.7511 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | 0.034497 | 0.073575 | 0.003136 | 0.042605 | 0.082082 | 0.11344 | 0.052844 | 0.084205
6113.3438 | 122.3465 | -120.6207 | 1.5198 | 0.11727 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.046142 | -0.028522 | -0.011281 | 0.027798 | -0.033484 | -0.00775 | 120.738 | 120.626 | 120.6133 | 120.6186 | 120.6341 | 120.7017 | 120.6129 | 0.112 | 0.22573 | 0.087341 | 0.012677 | 0.029918 | 0.068997 | 0.007715 | 0.033449 | 0.082083 | 0.10429 | 0.057423 | 0.079626
6115.0469 | 122.438 | -120.5933 | 1.5198 | 0.12185 | 0.014425 | -0.012 | -0.002124 | 0.013375 | 0.076426 | -0.007779 | 0.07538 | 0.18911 | 0.046142 | -0.014785 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 120.7151 | 120.6077 | 120.5813 | 120.5911 | 120.6066 | 120.6697 | 120.5855 | 0.11658 | 0.23031 | 0.087341 | 0.026414 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.086661 | 0.11344 | 0.057423 | 0.084205
6116.75 | 122.3877 | -120.5704 | 1.5564 | 0.11727 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.076426 | 0.001377 | 0.070802 | 0.18453 | 0.05072 | -0.014785 | -0.015859 | 0.027798 | -0.033484 | -0.00775 | 120.6876 | 120.5711 | 120.5584 | 120.5728 | 120.5792 | 120.6468 | 120.5718 | 0.112 | 0.22573 | 0.091919 | 0.026414 | 0.02534 | 0.068997 | 0.007715 | 0.033449 | 0.086661 | 0.10429 | 0.066579 | 0.084204
6118.4688 | 122.406 | -120.5475 | 1.5381 | 0.12185 | 0.000689 | -0.002842 | 0.002454 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.002124 | 0.032376 | -0.033484 | -0.012328 | 120.6693 | 120.5482 | 120.5446 | 120.5499 | 120.5563 | 120.6239 | 120.5443 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.039075 | 0.073575 | 0.007715 | 0.028871 | 0.077504 | 0.10886 | 0.052844 | 0.084204
6120.1719 | 122.3236 | -120.5933 | 1.5793 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 0.070802 | 0.18453 | 0.059877 | -0.019364 | -0.002124 | 0.032376 | -0.038063 | -0.00775 | 120.7243 | 120.5985 | 120.5813 | 120.5957 | 120.6021 | 120.6788 | 120.5855 | 0.112 | 0.22573 | 0.10108 | 0.021835 | 0.039075 | 0.073575 | 0.003136 | 0.033449 | 0.072926 | 0.10887 | 0.062001 | 0.09794
6121.8906 | 122.438 | -120.5475 | 1.5656 | 0.12643 | -0.00389 | -0.007421 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.003172 | 120.6739 | 120.5436 | 120.5401 | 120.5499 | 120.5609 | 120.6239 | 120.5397 | 0.12116 | 0.22573 | 0.087341 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.038027 | 0.086661 | 0.11344 | 0.052844 | 0.079626
6123.6406 | 122.3877 | -120.2682 | 1.8951 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.012357 | 0.084537 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.036954 | -0.033484 | -0.00775 | 120.3947 | 120.2644 | 120.2562 | 120.2661 | 120.277 | 120.3447 | 120.2559 | 0.12574 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.078153 | 0.007715 | 0.033449 | 0.091239 | 0.11802 | 0.057422 | 0.084204
6125.3281 | 122.3053 | -120.2911 | 1.9226 | 0.12643 | 0.000689 | -0.016578 | -0.006703 | 0.008797 | 0.081005 | 0.001377 | 0.07538 | 0.18453 | 0.055298 | -0.023943 | -0.015859 | 0.032376 | -0.042641 | -0.003172 | 120.4176 | 120.2918 | 120.2746 | 120.2844 | 120.2999 | 120.3721 | 120.2925 | 0.11658 | 0.22573 | 0.096497 | 0.017256 | 0.02534 | 0.073575 | -0.001442 | 0.038027 | 0.091239 | 0.11802 | 0.071157 | 0.097939
6127.0312 | 122.4197 | -120.2728 | 1.8768 | 0.12185 | 0.009846 | -0.012 | 0.002454 | 0.013375 | 0.071848 | -0.012357 | 0.079959 | 0.17995 | 0.05072 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.003172 | 120.3947 | 120.2827 | 120.2608 | 120.2753 | 120.2862 | 120.3447 | 120.2605 | 0.12116 | 0.22115 | 0.091919 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.038027 | 0.09124 | 0.11802 | 0.062001 | 0.088783
6128.75 | 122.3053 | -120.3003 | 1.9089 | 0.12643 | -0.00389 | -0.002842 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.070802 | 0.17537 | 0.055298 | -0.028522 | -0.002124 | 0.032376 | -0.038063 | -0.003172 | 120.4267 | 120.2964 | 120.2975 | 120.2982 | 120.3045 | 120.3859 | 120.2925 | 0.112 | 0.21657 | 0.096497 | 0.012677 | 0.039075 | 0.073575 | 0.003136 | 0.038027 | 0.072926 | 0.10887 | 0.057422 | 0.093361
6130.4531 | 122.4609 | -120.4559 | 1.6891 | 0.12185 | -0.00389 | -0.012 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17537 | 0.046142 | -0.023943 | -0.011281 | 0.036954 | -0.033484 | -0.003172 | 120.5778 | 120.452 | 120.4439 | 120.463 | 120.4647 | 120.5369 | 120.4527 | 0.11658 | 0.21657 | 0.087341 | 0.017256 | 0.029918 | 0.078153 | 0.007715 | 0.038027 | 0.086661 | 0.10886 | 0.057423 | 0.079626
6132.1562 | 122.2824 | -120.4147 | 1.7807 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | -0.000359 | 0.076426 | -0.007779 | 0.07538 | 0.17537 | 0.055298 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.012328 | 120.5412 | 120.4246 | 120.4073 | 120.4126 | 120.4144 | 120.4912 | 120.407 | 0.11658 | 0.21657 | 0.096497 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.028871 | 0.086661 | 0.11344 | 0.066579 | 0.093361
6133.8906 | 122.3236 | -120.282 | 1.9363 | 0.12185 | 0.009846 | -0.007421 | 0.002454 | 0.004219 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.046142 | -0.023943 | -0.011281 | 0.027798 | -0.038063 | -0.003172 | 120.4038 | 120.2918 | 120.2746 | 120.2844 | 120.2862 | 120.363 | 120.2742 | 0.112 | 0.22573 | 0.087341 | 0.017256 | 0.029918 | 0.068997 | 0.003136 | 0.038027 | 0.082083 | 0.10887 | 0.057423 | 0.084205
6135.6406 | 122.3785 | -120.4971 | 1.6937 | 0.12643 | 0.005267 | -0.007421 | -0.006703 | 0.013375 | 0.076426 | -0.003201 | 0.070802 | 0.18453 | 0.046142 | -0.019364 | -0.002124 | 0.032376 | -0.042641 | -0.012328 | 120.6236 | 120.5024 | 120.4897 | 120.4904 | 120.5105 | 120.5736 | 120.4939 | 0.112 | 0.22573 | 0.087341 | 0.021835 | 0.039075 | 0.073575 | -0.001442 | 0.028871 | 0.072926 | 0.11344 | 0.048266 | 0.088783
6137.3906 | 122.3785 | -120.5017 | 1.7029 | 0.13101 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.084537 | 0.18453 | 0.046142 | -0.023943 | -0.011281 | 0.032376 | -0.033484 | -0.012328 | 120.6327 | 120.507 | 120.4943 | 120.4996 | 120.5105 | 120.5873 | 120.4939 | 0.12574 | 0.22573 | 0.087341 | 0.017256 | 0.029918 | 0.073575 | 0.007715 | 0.028871 | 0.095818 | 0.11802 | 0.057423 | 0.079626
6139.0938 | 122.3877 | -98.2086 | 23.9227 | 0.12185 | 0.000689 | -0.016578 | 0.002454 | 0.004219 | 0.071848 | -0.007779 | 0.066223 | 0.18453 | 0.046142 | -0.019364 | -0.011281 | 0.027798 | -0.038063 | -0.00775 | 98.3305 | 98.2093 | 98.192 | 98.2111 | 98.2128 | 98.2805 | 98.2008 | 0.10742 | 0.22573 | 0.087341 | 0.021835 | 0.029918 | 0.068997 | 0.003136 | 0.033449 | 0.077504 | 0.10429 | 0.057423 | 0.084205
6140.7969 | 122.3877 | -120.5704 | 1.6022 | 0.13101 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.019364 | -0.011281 | 0.032376 | -0.038063 | -0.00775 | 120.7014 | 120.5756 | 120.563 | 120.5683 | 120.5837 | 120.656 | 120.5672 | 0.12116 | 0.22115 | 0.091919 | 0.021835 | 0.029918 | 0.073575 | 0.003136 | 0.033449 | 0.09124 | 0.11802 | 0.062001 | 0.088783
6142.5625 | 122.5113 | -120.5658 | 1.5701 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.079959 | 0.17995 | 0.055298 | -0.019364 | -0.006702 | 0.02322 | -0.028906 | 0.001406 | 120.6922 | 120.5665 | 120.5492 | 120.5683 | 120.5746 | 120.6468 | 120.558 | 0.12116 | 0.22115 | 0.096497 | 0.021835 | 0.034497 | 0.064419 | 0.012293 | 0.042605 | 0.086661 | 0.10887 | 0.062 | 0.084204
6144.2656 | 122.4335 | -120.6162 | 1.5884 | 0.12643 | 0.005267 | -0.021157 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.006702 | 0.032376 | -0.028906 | -0.003172 | 120.7426 | 120.6214 | 120.595 | 120.614 | 120.6295 | 120.6972 | 120.6129 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.034497 | 0.073575 | 0.012293 | 0.038027 | 0.077504 | 0.099708 | 0.062 | 0.084204
6145.9844 | 122.4747 | -120.6024 | 1.5656 | 0.12185 | 0.000689 | -0.007421 | -0.006703 | 0.013375 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.006702 | 0.027798 | -0.033484 | -0.00775 | 120.7243 | 120.6031 | 120.595 | 120.5957 | 120.6158 | 120.6788 | 120.5946 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.034497 | 0.068997 | 0.007715 | 0.033449 | 0.082082 | 0.10886 | 0.057422 | 0.084204
6147.6875 | 121.7834 | -107.7026 | 13.9664 | 0.12185 | 0.005267 | -0.012 | 0.007033 | 0.004219 | 0.071848 | -0.007779 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.002124 | 0.032376 | -0.033484 | -0.00775 | 107.8245 | 107.7079 | 107.6906 | 107.7097 | 107.7069 | 107.7745 | 107.6949 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | 0.039075 | 0.073575 | 0.007715 | 0.033449 | 0.068347 | 0.099707 | 0.048266 | 0.079626
6149.375 | 122.0261 | -65.5151 | 56.1584 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.012357 | 0.066223 | 0.17995 | 0.05072 | -0.019364 | -0.006702 | 0.027798 | -0.038063 | 0.001406 | 65.6416 | 65.5204 | 65.5077 | 65.513 | 65.5239 | 65.5916 | 65.5028 | 0.10742 | 0.22115 | 0.091919 | 0.021835 | 0.034497 | 0.068997 | 0.003136 | 0.042605 | 0.072925 | 0.10429 | 0.057422 | 0.088783
6151.0938 | 121.7606 | -12.0712 | 109.8953 | 0.11727 | 0.000689 | -0.025735 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.17995 | 0.041563 | -0.023943 | -0.011281 | 0.032376 | -0.038063 | -0.012328 | 12.1885 | 12.0719 | 12.0455 | 12.0691 | 12.08 | 12.1477 | 12.0634 | 0.112 | 0.22115 | 0.082762 | 0.017256 | 0.029918 | 0.073575 | 0.003136 | 0.028871 | 0.082083 | 0.10887 | 0.052844 | 0.079626
6152.8125 | 122.1039 | -10.112 | 111.113 | 0.12185 | 0.000689 | -0.021157 | -0.002124 | -0.000359 | 0.076426 | -0.007779 | 0.070802 | 0.17537 | 0.046142 | -0.028522 | 0.002454 | 0.036954 | -0.038063 | -0.003172 | 10.2339 | 10.1127 | 10.0908 | 10.1099 | 10.1116 | 10.1884 | 10.1042 | 0.112 | 0.21657 | 0.087341 | 0.012677 | 0.043653 | 0.078153 | 0.003136 | 0.038027 | 0.068348 | 0.10887 | 0.043688 | 0.084205
6154.5 | 108.0002 | -12.1902 | 95.6268 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.012357 | 0.066223 | 0.18453 | 0.046142 | -0.033101 | -0.03875 | 0.032376 | -0.038063 | -0.00775 | 12.3121 | 12.1955 | 12.1737 | 12.1881 | 12.1945 | 12.2667 | 12.1779 | 0.10742 | 0.22573 | 0.087341 | 0.008098 | 0.002449 | 0.073575 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.084892 | 0.084205
6156.2031 | 91.2827 | -13.2202 | 80.8228 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.071848 | -0.012357 | 0.07538 | 0.17995 | 0.041563 | -0.03768 | -0.043328 | 0.036954 | -0.028906 | -0.00775 | 13.3466 | 13.2209 | 13.2082 | 13.2181 | 13.2244 | 13.2921 | 13.2079 | 0.11658 | 0.22115 | 0.082762 | 0.003519 | -0.002129 | 0.078153 | 0.012293 | 0.033449 | 0.11871 | 0.10429 | 0.084891 | 0.070469
6157.9062 | 121.7468 | -12.1857 | 109.584 | 0.13101 | 0.000689 | -0.012 | -0.006703 | 0.008797 | 0.076426 | -0.007779 | 0.066223 | 0.17537 | 0.05072 | -0.028522 | -0.03875 | 0.036954 | -0.038063 | -0.00775 | 12.3167 | 12.1864 | 12.1737 | 12.179 | 12.1945 | 12.2621 | 12.1779 | 0.10742 | 0.21657 | 0.091919 | 0.012677 | 0.002449 | 0.078153 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.08947 | 0.088783
6159.6094 | 122.3373 | -107.1671 | 14.653 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.071848 | -0.012357 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.024328 | 0.001406 | 107.2935 | 107.1723 | 107.1551 | 107.1649 | 107.1758 | 107.2389 | 107.1547 | 0.112 | 0.22115 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.016871 | 0.042605 | 0.11413 | 0.09513 | 0.094048 | 0.075048
6161.3281 | 122.3373 | -113.0447 | 8.8852 | 0.12185 | -0.00389 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | -0.012357 | 0.070802 | 0.18911 | 0.046142 | -0.028522 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 113.1666 | 113.0408 | 113.0373 | 113.0426 | 113.0535 | 113.1303 | 113.0324 | 0.112 | 0.23031 | 0.087341 | 0.012677 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.11871 | 0.10429 | 0.094048 | 0.079626
6163.0312 | 122.3557 | -105.954 | 15.889 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.070802 | 0.17995 | 0.055298 | -0.019364 | -0.03875 | 0.02322 | -0.033484 | -0.00775 | 106.0804 | 105.9547 | 105.942 | 105.9564 | 105.9628 | 106.0396 | 105.9508 | 0.112 | 0.22115 | 0.096497 | 0.021835 | 0.002449 | 0.064419 | 0.007715 | 0.033449 | 0.10955 | 0.10429 | 0.094048 | 0.088782
6164.7656 | 122.2824 | -121.0556 | 0.94757 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.028522 | -0.03875 | 0.032376 | -0.042641 | -0.00775 | 121.182 | 121.0609 | 121.0436 | 121.0581 | 121.0644 | 121.1366 | 121.0524 | 0.112 | 0.22573 | 0.091919 | 0.012677 | 0.002449 | 0.073575 | -0.001442 | 0.033449 | 0.10955 | 0.11344 | 0.08947 | 0.093361
6166.5312 | 122.2504 | -115.8966 | 6.0974 | 0.13101 | 0.000689 | -0.007421 | 0.007033 | 0.008797 | 0.085583 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.023943 | -0.047906 | 0.027798 | -0.033484 | -0.003172 | 116.0276 | 115.8973 | 115.8892 | 115.9036 | 115.9054 | 115.9822 | 115.8888 | 0.12116 | 0.22573 | 0.087341 | 0.017256 | -0.006707 | 0.068997 | 0.007715 | 0.038027 | 0.12787 | 0.11344 | 0.094048 | 0.079626
6168.2344 | 122.1954 | -112.4634 | 9.4894 | 0.12643 | 0.014425 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.019364 | -0.034171 | 0.032376 | -0.033484 | -0.003172 | 112.5898 | 112.4778 | 112.456 | 112.4613 | 112.4722 | 112.5444 | 112.4602 | 0.11658 | 0.22115 | 0.087341 | 0.021835 | 0.007028 | 0.073575 | 0.007715 | 0.038027 | 0.10955 | 0.10886 | 0.080313 | 0.079626
6169.9375 | 122.3419 | -121.1243 | 0.88348 | 0.13101 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.023943 | -0.03875 | 0.032376 | -0.042641 | -0.012328 | 121.2553 | 121.125 | 121.1077 | 121.1221 | 121.1285 | 121.2053 | 121.1211 | 0.11658 | 0.22573 | 0.096497 | 0.017256 | 0.002449 | 0.073575 | -0.001442 | 0.028871 | 0.11413 | 0.11802 | 0.094048 | 0.097939
6171.6562 | 122.2183 | -121.1838 | 0.90637 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.18911 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.028906 | -0.00775 | 121.3102 | 121.1845 | 121.1672 | 121.1862 | 121.1926 | 121.2694 | 121.1806 | 0.11658 | 0.23031 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.012293 | 0.033449 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6173.3438 | 122.3236 | -121.1792 | 0.85602 | 0.11727 | 0.014425 | -0.016578 | -0.002124 | 0.013375 | 0.085583 | -0.012357 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.034171 | 0.032376 | -0.033484 | -0.00775 | 121.2965 | 121.1936 | 121.1626 | 121.1771 | 121.1926 | 121.2648 | 121.1668 | 0.112 | 0.22115 | 0.091919 | 0.017256 | 0.007028 | 0.073575 | 0.007715 | 0.033449 | 0.10497 | 0.10429 | 0.084891 | 0.084204
6175.0625 | 122.3236 | -121.1929 | 0.8606 | 0.11727 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.034171 | 0.032376 | -0.038063 | 0.001406 | 121.3102 | 121.1982 | 121.1809 | 121.1954 | 121.2063 | 121.2739 | 121.1852 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.007028 | 0.073575 | 0.003136 | 0.042605 | 0.10955 | 0.11344 | 0.084891 | 0.088783
6176.7656 | 122.3053 | -121.1884 | 0.86975 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.017953 | 0.085583 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.018642 | -0.038063 | -0.003172 | 121.3148 | 121.189 | 121.1809 | 121.1862 | 121.2063 | 121.2739 | 121.1852 | 0.112 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.059841 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6178.4688 | 122.2549 | -121.1975 | 0.91095 | 0.12643 | 0.009846 | -0.002842 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.3239 | 121.2074 | 121.1947 | 121.1954 | 121.2063 | 121.2785 | 121.1943 | 0.112 | 0.22115 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6180.1719 | 122.3602 | -121.1975 | 0.89264 | 0.12643 | 0.009846 | -0.007421 | -0.006703 | -0.000359 | 0.081005 | -0.012357 | 0.070802 | 0.18453 | 0.055298 | -0.028522 | -0.03875 | 0.032376 | -0.038063 | -0.00775 | 121.3239 | 121.2074 | 121.1901 | 121.1908 | 121.1972 | 121.2785 | 121.1852 | 0.112 | 0.22573 | 0.096497 | 0.012677 | 0.002449 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10887 | 0.094048 | 0.093361
6181.8906 | 122.3785 | -121.1746 | 0.86975 | 0.12185 | 0.000689 | -0.007421 | 0.007033 | 0.013375 | 0.076426 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.2965 | 121.1753 | 121.1672 | 121.1817 | 121.188 | 121.251 | 121.1714 | 0.11658 | 0.21657 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6183.6406 | 122.3328 | -121.2067 | 0.86975 | 0.12185 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.016936 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.043328 | 0.036954 | -0.033484 | -0.00775 | 121.3285 | 121.2074 | 121.1901 | 121.2091 | 121.2155 | 121.2877 | 121.1897 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | -0.002129 | 0.078153 | 0.007715 | 0.033449 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6185.3906 | 122.2961 | -121.2479 | 0.87891 | 0.12185 | 0.005267 | -0.016578 | 0.007033 | -0.000359 | 0.081005 | -0.007779 | 0.070802 | 0.17537 | 0.059877 | -0.028522 | -0.03875 | 0.032376 | -0.028906 | -0.003172 | 121.3697 | 121.2531 | 121.2313 | 121.2549 | 121.2475 | 121.3289 | 121.2401 | 0.112 | 0.21657 | 0.10108 | 0.012677 | 0.002449 | 0.073575 | 0.012293 | 0.038027 | 0.10955 | 0.099708 | 0.098627 | 0.088783
6187.0938 | 122.3785 | -121.225 | 0.86975 | 0.11727 | 0.000689 | -0.012 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.028522 | -0.03875 | 0.032376 | -0.033484 | -0.00775 | 121.3422 | 121.2257 | 121.213 | 121.232 | 121.2338 | 121.306 | 121.2218 | 0.11658 | 0.22115 | 0.087341 | 0.012677 | 0.002449 | 0.073575 | 0.007715 | 0.033449 | 0.11413 | 0.10886 | 0.084892 | 0.079626
6188.7969 | 122.3785 | -121.225 | 0.86517 | 0.12185 | 0.009846 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.070802 | 0.17537 | 0.055298 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.3468 | 121.2348 | 121.2084 | 121.2229 | 121.2292 | 121.3014 | 121.2172 | 0.112 | 0.21657 | 0.096497 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.098626 | 0.088782
6190.5625 | 122.3419 | -121.2341 | 0.87891 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.012357 | 0.070802 | 0.17995 | 0.055298 | -0.028522 | -0.034171 | 0.027798 | -0.038063 | -0.00775 | 121.3606 | 121.2394 | 121.2221 | 121.2366 | 121.2475 | 121.3106 | 121.2218 | 0.112 | 0.22115 | 0.096497 | 0.012677 | 0.007028 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.10887 | 0.089469 | 0.093361
6192.2656 | 122.2504 | -121.2479 | 0.89722 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.071848 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.028522 | -0.03875 | 0.032376 | -0.028906 | -0.00775 | 121.3743 | 121.2486 | 121.2359 | 121.2503 | 121.2521 | 121.3197 | 121.2401 | 0.112 | 0.22573 | 0.096497 | 0.012677 | 0.002449 | 0.073575 | 0.012293 | 0.033449 | 0.10955 | 0.099708 | 0.094048 | 0.084204
6193.9844 | 122.3785 | -121.2204 | 0.85602 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.041563 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.3468 | 121.2257 | 121.2084 | 121.2229 | 121.2338 | 121.2968 | 121.2126 | 0.11658 | 0.22115 | 0.082762 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.11871 | 0.10886 | 0.084891 | 0.075047
6195.6875 | 122.319 | -121.2662 | 0.88806 | 0.12643 | 0.000689 | -0.007421 | 0.007033 | 0.017953 | 0.085583 | -0.003201 | 0.070802 | 0.17995 | 0.041563 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.012328 | 121.3926 | 121.2669 | 121.2588 | 121.2732 | 121.2841 | 121.3518 | 121.263 | 0.112 | 0.22115 | 0.082762 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.028871 | 0.11413 | 0.10429 | 0.084891 | 0.075047
6197.4219 | 122.3969 | -121.2662 | 0.8606 | 0.11727 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.003172 | 121.3834 | 121.2669 | 121.2542 | 121.2641 | 121.2795 | 121.3472 | 121.2584 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.11344 | 0.084892 | 0.084205
6199.1406 | 122.2824 | -121.2067 | 0.94757 | 0.11727 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.047906 | 0.032376 | -0.033484 | -0.003172 | 121.3239 | 121.2165 | 121.1947 | 121.2091 | 121.2155 | 121.2831 | 121.1989 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | -0.006707 | 0.073575 | 0.007715 | 0.038027 | 0.12329 | 0.10886 | 0.098626 | 0.084204
6200.8438 | 122.2778 | -121.2708 | 0.92926 | 0.13101 | 0.009846 | -0.012 | 0.011611 | 0.008797 | 0.085583 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.019364 | -0.047906 | 0.027798 | -0.028906 | -0.003172 | 121.4018 | 121.2806 | 121.2588 | 121.2824 | 121.2795 | 121.3563 | 121.263 | 0.112 | 0.22115 | 0.087341 | 0.021835 | -0.006707 | 0.068997 | 0.012293 | 0.038027 | 0.11871 | 0.099708 | 0.094048 | 0.075048
6202.5469 | 122.2916 | -121.2708 | 0.9201 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.013375 | 0.085583 | 0.001377 | 0.07538 | 0.17537 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.033484 | -0.00775 | 121.3972 | 121.276 | 121.2542 | 121.2732 | 121.2841 | 121.3563 | 121.2721 | 0.11658 | 0.21657 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.007715 | 0.033449 | 0.11413 | 0.10886 | 0.08947 | 0.084204
6204.2812 | 122.2504 | -121.2662 | 0.9201 | 0.12643 | 0.009846 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.019364 | -0.047906 | 0.036954 | -0.042641 | -0.00775 | 121.3926 | 121.276 | 121.2542 | 121.2686 | 121.2704 | 121.3472 | 121.263 | 0.11658 | 0.22115 | 0.087341 | 0.021835 | -0.006707 | 0.078153 | -0.001442 | 0.033449 | 0.12329 | 0.11802 | 0.094048 | 0.088783
6206.0156 | 122.2961 | -121.2524 | 0.92926 | 0.13101 | 0.005267 | -0.007421 | 0.002454 | 0.013375 | 0.085583 | -0.007779 | 0.070802 | 0.17995 | 0.055298 | -0.023943 | -0.043328 | 0.036954 | -0.038063 | -0.003172 | 121.3834 | 121.2577 | 121.245 | 121.2549 | 121.2658 | 121.338 | 121.2447 | 0.112 | 0.22115 | 0.096497 | 0.017256 | -0.002129 | 0.078153 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.098626 | 0.093361
6207.7188 | 122.4014 | -121.225 | 0.89264 | 0.13101 | 0.000689 | -0.016578 | 0.007033 | 0.013375 | 0.076426 | -0.003201 | 0.07538 | 0.17995 | 0.059877 | -0.019364 | -0.03875 | 0.036954 | -0.038063 | -0.012328 | 121.356 | 121.2257 | 121.2084 | 121.232 | 121.2384 | 121.3014 | 121.2218 | 0.11658 | 0.22115 | 0.10108 | 0.021835 | 0.002449 | 0.078153 | 0.003136 | 0.028871 | 0.11413 | 0.11344 | 0.098627 | 0.09794
6209.4219 | 122.2824 | -121.2708 | 0.93842 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.014785 | -0.03875 | 0.032376 | -0.042641 | -0.012328 | 121.3926 | 121.2714 | 121.2633 | 121.2732 | 121.2795 | 121.3426 | 121.2676 | 0.11658 | 0.22115 | 0.091919 | 0.026414 | 0.002449 | 0.073575 | -0.001442 | 0.028871 | 0.11413 | 0.11802 | 0.08947 | 0.093361
6211.1562 | 122.3923 | -121.2662 | 0.87891 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.079959 | 0.18453 | 0.046142 | -0.033101 | -0.03875 | 0.041532 | -0.038063 | -0.003172 | 121.3972 | 121.2714 | 121.2542 | 121.2686 | 121.2795 | 121.3472 | 121.2584 | 0.12116 | 0.22573 | 0.087341 | 0.008098 | 0.002449 | 0.082731 | 0.003136 | 0.038027 | 0.11871 | 0.11802 | 0.084892 | 0.084205
6212.8594 | 122.3465 | -121.2753 | 0.90179 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.027798 | -0.038063 | -0.00775 | 121.4018 | 121.2852 | 121.2679 | 121.2732 | 121.2887 | 121.3518 | 121.2721 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.068997 | 0.003136 | 0.033449 | 0.12329 | 0.11344 | 0.094048 | 0.084205
6214.6094 | 122.3099 | -121.2753 | 0.89722 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.02322 | -0.033484 | -0.012328 | 121.4018 | 121.2806 | 121.2679 | 121.2732 | 121.2887 | 121.3609 | 121.2721 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.064419 | 0.007715 | 0.028871 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6216.3125 | 122.3969 | -121.225 | 0.90179 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.3514 | 121.2257 | 121.213 | 121.2229 | 121.2384 | 121.306 | 121.2218 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.094048 | 0.079626
6218.0469 | 122.3236 | -121.2753 | 0.91095 | 0.12643 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.17537 | 0.055298 | -0.023943 | -0.034171 | 0.032376 | -0.028906 | -0.012328 | 121.4018 | 121.2852 | 121.2633 | 121.2778 | 121.2841 | 121.3518 | 121.2676 | 0.112 | 0.21657 | 0.096497 | 0.017256 | 0.007028 | 0.073575 | 0.012293 | 0.028871 | 0.10497 | 0.099708 | 0.089469 | 0.084204
6219.7656 | 122.2961 | -121.2891 | 0.9201 | 0.12185 | 0.000689 | -0.002842 | 0.002454 | 0.004219 | 0.076426 | 0.001377 | 0.070802 | 0.17995 | 0.055298 | -0.023943 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.4109 | 121.2898 | 121.2862 | 121.2915 | 121.2933 | 121.3655 | 121.2904 | 0.112 | 0.22115 | 0.096497 | 0.017256 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.098626 | 0.088782
6221.4688 | 122.3923 | -121.257 | 0.90179 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.004219 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.3834 | 121.2577 | 121.2496 | 121.2595 | 121.2612 | 121.338 | 121.2447 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.11344 | 0.098626 | 0.088783
6223.1719 | 122.319 | -121.2936 | 0.94757 | 0.11727 | 0.005267 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.034171 | 0.032376 | -0.042641 | -0.003172 | 121.4109 | 121.2989 | 121.2816 | 121.2915 | 121.2979 | 121.3792 | 121.2904 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.007028 | 0.073575 | -0.001442 | 0.038027 | 0.10955 | 0.11802 | 0.084891 | 0.093361
6224.9062 | 122.4243 | -121.2662 | 0.89264 | 0.12643 | 0.005267 | -0.021157 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.019364 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.3926 | 121.2714 | 121.245 | 121.2686 | 121.275 | 121.3426 | 121.2584 | 0.112 | 0.22573 | 0.096497 | 0.021835 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.11871 | 0.10429 | 0.1032 | 0.088782
6226.6094 | 122.3465 | -121.3211 | 0.89722 | 0.12185 | 0.000689 | -0.021157 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | 0.001406 | 121.443 | 121.3218 | 121.2999 | 121.3236 | 121.3299 | 121.4021 | 121.3087 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.042605 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6228.2969 | 122.3648 | -121.2799 | 0.90179 | 0.12185 | 0.005267 | -0.007421 | -0.002124 | 0.017953 | 0.076426 | -0.012357 | 0.07538 | 0.18453 | 0.055298 | -0.019364 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.4018 | 121.2852 | 121.2725 | 121.2778 | 121.2979 | 121.3563 | 121.2675 | 0.11658 | 0.22573 | 0.096497 | 0.021835 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.11344 | 0.1032 | 0.093361
6230.0156 | 122.319 | -121.3074 | 0.90179 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.03875 | 0.027798 | -0.033484 | -0.012328 | 121.4338 | 121.3126 | 121.2954 | 121.3052 | 121.3207 | 121.3884 | 121.3042 | 0.112 | 0.22115 | 0.091919 | 0.012677 | 0.002449 | 0.068997 | 0.007715 | 0.028871 | 0.10955 | 0.10429 | 0.08947 | 0.084204
6231.7188 | 122.3648 | -121.3028 | 0.90179 | 0.12643 | 0.005267 | -0.016578 | 0.007033 | 0.008797 | 0.071848 | -0.007779 | 0.079959 | 0.17537 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.033484 | -0.00775 | 121.4292 | 121.3081 | 121.2862 | 121.3098 | 121.3116 | 121.3746 | 121.295 | 0.12116 | 0.21657 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.007715 | 0.033449 | 0.12329 | 0.11344 | 0.094048 | 0.084204
6233.4062 | 122.4426 | -121.2616 | 0.87433 | 0.13101 | 0.005267 | -0.012 | 0.007033 | 0.004219 | 0.071848 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.027798 | -0.033484 | -0.003172 | 121.3926 | 121.2669 | 121.2496 | 121.2686 | 121.2658 | 121.3334 | 121.2584 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.068997 | 0.007715 | 0.038027 | 0.12329 | 0.10886 | 0.094048 | 0.079626
6235.1406 | 122.3785 | -121.312 | 0.90179 | 0.12643 | 0.009846 | -0.007421 | 0.007033 | 0.008797 | 0.081005 | -0.007779 | 0.066223 | 0.17995 | 0.055298 | -0.023943 | -0.03875 | 0.027798 | -0.028906 | 0.001406 | 121.4384 | 121.3218 | 121.3045 | 121.319 | 121.3207 | 121.393 | 121.3042 | 0.10742 | 0.22115 | 0.096497 | 0.017256 | 0.002449 | 0.068997 | 0.012293 | 0.042605 | 0.10497 | 0.095129 | 0.094048 | 0.084204
6236.8438 | 122.438 | -121.2616 | 0.88348 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.004219 | 0.085583 | -0.012357 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.388 | 121.2669 | 121.2496 | 121.2641 | 121.2658 | 121.3472 | 121.2492 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.094048 | 0.079626
6238.6094 | 122.4426 | -121.2708 | 0.88806 | 0.12643 | -0.00389 | -0.016578 | 0.002454 | 0.013375 | 0.081005 | -0.012357 | 0.066223 | 0.17537 | 0.046142 | -0.028522 | -0.043328 | 0.036954 | -0.042641 | -0.00775 | 121.3972 | 121.2669 | 121.2542 | 121.2732 | 121.2841 | 121.3518 | 121.2584 | 0.10742 | 0.21657 | 0.087341 | 0.012677 | -0.002129 | 0.078153 | -0.001442 | 0.033449 | 0.10955 | 0.10886 | 0.08947 | 0.088783
6240.2969 | 122.4152 | -121.312 | 0.90179 | 0.13101 | -0.00389 | -0.007421 | -0.002124 | 0.017953 | 0.081005 | -0.007779 | 0.070802 | 0.18911 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.443 | 121.3081 | 121.3045 | 121.3098 | 121.3299 | 121.393 | 121.3042 | 0.112 | 0.23031 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6242.0625 | 122.406 | -121.3257 | 0.87433 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.061645 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.4521 | 121.3264 | 121.3137 | 121.3236 | 121.3345 | 121.4021 | 121.3179 | 0.10284 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.099708 | 0.08947 | 0.084205
6243.7656 | 122.3648 | -121.3623 | 0.89722 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.090161 | -0.007779 | 0.079959 | 0.17537 | 0.05072 | -0.019364 | -0.03875 | 0.027798 | -0.028906 | -0.003172 | 121.4887 | 121.3676 | 121.3503 | 121.3648 | 121.3757 | 121.4525 | 121.3545 | 0.12116 | 0.21657 | 0.091919 | 0.021835 | 0.002449 | 0.068997 | 0.012293 | 0.038027 | 0.11871 | 0.10887 | 0.08947 | 0.079626
6245.5 | 122.3328 | -121.3394 | 0.90179 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.046142 | -0.033101 | -0.043328 | 0.032376 | -0.033484 | -0.00775 | 121.4613 | 121.3447 | 121.332 | 121.3419 | 121.3482 | 121.4204 | 121.3316 | 0.11658 | 0.22115 | 0.087341 | 0.008098 | -0.002129 | 0.073575 | 0.007715 | 0.033449 | 0.11871 | 0.10886 | 0.08947 | 0.079626
6247.2188 | 122.4792 | -121.3348 | 0.85602 | 0.13101 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.4658 | 121.3401 | 121.3183 | 121.3327 | 121.3436 | 121.4113 | 121.3316 | 0.12116 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.12329 | 0.11802 | 0.094048 | 0.088783
6248.9219 | 122.3923 | -121.3165 | 0.87891 | 0.12643 | 0.009846 | -0.007421 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.079959 | 0.17537 | 0.055298 | -0.023943 | -0.03875 | 0.027798 | -0.038063 | -0.003172 | 121.443 | 121.3264 | 121.3091 | 121.3236 | 121.3253 | 121.3975 | 121.3133 | 0.12116 | 0.21657 | 0.096497 | 0.017256 | 0.002449 | 0.068997 | 0.003136 | 0.038027 | 0.11871 | 0.11802 | 0.094048 | 0.093361
6250.6562 | 122.406 | -121.3531 | 0.89722 | 0.13101 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.066223 | 0.17537 | 0.046142 | -0.023943 | -0.03875 | 0.027798 | -0.033484 | -0.012328 | 121.4842 | 121.3584 | 121.3411 | 121.351 | 121.3619 | 121.4342 | 121.3454 | 0.10742 | 0.21657 | 0.087341 | 0.017256 | 0.002449 | 0.068997 | 0.007715 | 0.028871 | 0.10497 | 0.099707 | 0.084892 | 0.079626
6252.3438 | 122.4472 | -121.312 | 0.86975 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17079 | 0.041563 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.4384 | 121.3172 | 121.2954 | 121.3144 | 121.3207 | 121.393 | 121.3088 | 0.11658 | 0.21199 | 0.082762 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.11871 | 0.11344 | 0.084891 | 0.079626
6254.0469 | 122.3648 | -121.3531 | 0.89722 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.070802 | 0.17995 | 0.055298 | -0.028522 | -0.047906 | 0.02322 | -0.028906 | -0.012328 | 121.4796 | 121.3538 | 121.3457 | 121.351 | 121.3574 | 121.4387 | 121.3454 | 0.112 | 0.22115 | 0.096497 | 0.012677 | -0.006707 | 0.064419 | 0.012293 | 0.028871 | 0.11871 | 0.099708 | 0.1032 | 0.084204
6255.7656 | 122.4792 | -121.3165 | 0.86975 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.013375 | 0.090161 | -0.003201 | 0.066223 | 0.18911 | 0.041563 | -0.019364 | -0.043328 | 0.02322 | -0.042641 | -0.003172 | 121.4384 | 121.3172 | 121.3091 | 121.3144 | 121.3299 | 121.4067 | 121.3133 | 0.10742 | 0.23031 | 0.082762 | 0.021835 | -0.002129 | 0.064419 | -0.001442 | 0.038027 | 0.10955 | 0.10886 | 0.084891 | 0.084204
6257.4688 | 122.3831 | -121.344 | 0.8606 | 0.13101 | 0.000689 | -0.012 | 0.007033 | 0.013375 | 0.076426 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.475 | 121.3447 | 121.332 | 121.351 | 121.3574 | 121.4204 | 121.3408 | 0.12116 | 0.22115 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.12329 | 0.11802 | 0.094048 | 0.088783
6259.1719 | 122.493 | -121.3303 | 0.86975 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.032376 | -0.042641 | 0.001406 | 121.4567 | 121.3309 | 121.3183 | 121.3281 | 121.3391 | 121.4113 | 121.3271 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.073575 | -0.001442 | 0.042605 | 0.10955 | 0.10886 | 0.08947 | 0.088783
6260.8906 | 122.5159 | -121.3303 | 0.8606 | 0.13559 | 0.009846 | -0.012 | 0.007033 | 0.013375 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.012328 | 121.4658 | 121.3401 | 121.3183 | 121.3373 | 121.3436 | 121.4067 | 121.3225 | 0.112 | 0.22573 | 0.096497 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.028871 | 0.10955 | 0.10887 | 0.094048 | 0.093361
6262.5781 | 122.5113 | -121.3165 | 0.8606 | 0.11727 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.4338 | 121.3172 | 121.3091 | 121.319 | 121.3253 | 121.3975 | 121.3042 | 0.112 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6264.2812 | 122.4106 | -121.376 | 0.87891 | 0.12643 | 0.005267 | -0.007421 | -0.006703 | 0.008797 | 0.081005 | -0.007779 | 0.066223 | 0.18453 | 0.05072 | -0.019364 | -0.043328 | 0.036954 | -0.028906 | -0.003172 | 121.5025 | 121.3813 | 121.3686 | 121.3693 | 121.3848 | 121.457 | 121.3683 | 0.10742 | 0.22573 | 0.091919 | 0.021835 | -0.002129 | 0.078153 | 0.012293 | 0.038027 | 0.10955 | 0.095129 | 0.094048 | 0.079626
6266.0156 | 122.5067 | -121.3669 | 0.84686 | 0.12185 | 0.005267 | -0.007421 | -0.002124 | 0.017953 | 0.076426 | -0.007779 | 0.070802 | 0.17537 | 0.041563 | -0.019364 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.4887 | 121.3721 | 121.3595 | 121.3648 | 121.3848 | 121.4433 | 121.3591 | 0.112 | 0.21657 | 0.082762 | 0.021835 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.084891 | 0.075047
6267.7188 | 122.4655 | -121.3669 | 0.85602 | 0.13559 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.071848 | -0.012357 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.052484 | 0.027798 | -0.033484 | -0.00775 | 121.5025 | 121.3676 | 121.3595 | 121.3648 | 121.3757 | 121.4387 | 121.3545 | 0.112 | 0.22115 | 0.091919 | 0.012677 | -0.011285 | 0.068997 | 0.007715 | 0.033449 | 0.12329 | 0.10429 | 0.1032 | 0.084204
6269.4219 | 122.5021 | -121.3486 | 0.83313 | 0.13101 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.066223 | 0.17995 | 0.05072 | -0.023943 | -0.047906 | 0.02322 | -0.038063 | -0.003172 | 121.4796 | 121.3584 | 121.332 | 121.351 | 121.3574 | 121.4342 | 121.3454 | 0.10742 | 0.22115 | 0.091919 | 0.017256 | -0.006707 | 0.064419 | 0.003136 | 0.038027 | 0.11413 | 0.10429 | 0.098626 | 0.088783
6271.1406 | 122.4289 | -121.3531 | 0.87433 | 0.13101 | 0.009846 | -0.007421 | 0.002454 | 0.004219 | 0.085583 | 0.001377 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.034171 | 0.027798 | -0.033484 | -0.003172 | 121.4842 | 121.363 | 121.3457 | 121.3556 | 121.3574 | 121.4387 | 121.3545 | 0.112 | 0.22115 | 0.087341 | 0.017256 | 0.007028 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.10429 | 0.080313 | 0.079626
6272.8438 | 122.4747 | -121.3531 | 0.85602 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.034171 | 0.027798 | -0.038063 | -0.012328 | 121.4796 | 121.3584 | 121.3411 | 121.3556 | 121.3619 | 121.425 | 121.3499 | 0.112 | 0.22115 | 0.091919 | 0.017256 | 0.007028 | 0.068997 | 0.003136 | 0.028871 | 0.10497 | 0.10887 | 0.084891 | 0.088783
6274.5469 | 122.5021 | -121.3348 | 0.86517 | 0.12643 | 0.009846 | -0.002842 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.07538 | 0.18453 | 0.046142 | -0.028522 | -0.047906 | 0.027798 | -0.038063 | -0.00775 | 121.4613 | 121.3447 | 121.332 | 121.3373 | 121.3436 | 121.4113 | 121.3271 | 0.11658 | 0.22573 | 0.087341 | 0.012677 | -0.006707 | 0.068997 | 0.003136 | 0.033449 | 0.12329 | 0.11344 | 0.094048 | 0.084205
6276.2812 | 122.5159 | -121.3486 | 0.85602 | 0.12185 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.028522 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.4704 | 121.3493 | 121.332 | 121.351 | 121.3574 | 121.4204 | 121.3454 | 0.11658 | 0.22573 | 0.096497 | 0.012677 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.1032 | 0.088782
6277.9844 | 122.3511 | -121.3898 | 0.89264 | 0.12643 | 0.014425 | -0.012 | 0.002454 | 0.017953 | 0.085583 | 0.001377 | 0.066223 | 0.18453 | 0.046142 | -0.028522 | -0.03875 | 0.027798 | -0.038063 | 0.001406 | 121.5162 | 121.4042 | 121.3778 | 121.3922 | 121.4077 | 121.4754 | 121.3911 | 0.10742 | 0.22573 | 0.087341 | 0.012677 | 0.002449 | 0.068997 | 0.003136 | 0.042605 | 0.10497 | 0.10429 | 0.084892 | 0.084205
6279.7031 | 122.5342 | -121.3715 | 0.83771 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.055298 | -0.033101 | -0.047906 | 0.027798 | -0.033484 | -0.003172 | 121.4979 | 121.3721 | 121.3595 | 121.3739 | 121.3757 | 121.4525 | 121.3683 | 0.112 | 0.21657 | 0.096497 | 0.008098 | -0.006707 | 0.068997 | 0.007715 | 0.038027 | 0.11871 | 0.10429 | 0.1032 | 0.088782
6281.4062 | 122.4335 | -121.4035 | 0.89264 | 0.12643 | -0.00389 | -0.007421 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.066223 | 0.18453 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.5299 | 121.3996 | 121.3961 | 121.406 | 121.4123 | 121.4891 | 121.4003 | 0.10742 | 0.22573 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.10955 | 0.099707 | 0.094048 | 0.084204
6283.1406 | 122.5113 | -121.3531 | 0.84228 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.17537 | 0.041563 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.4796 | 121.3584 | 121.3411 | 121.3556 | 121.3619 | 121.4342 | 121.3454 | 0.11658 | 0.21657 | 0.082762 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.11871 | 0.11344 | 0.084891 | 0.079626
6284.8438 | 122.3694 | -121.3898 | 0.87891 | 0.12185 | -0.00389 | -0.012 | -0.006703 | 0.013375 | 0.085583 | -0.012357 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.047906 | 0.032376 | -0.028906 | -0.00775 | 121.5116 | 121.3859 | 121.3778 | 121.3831 | 121.4031 | 121.4754 | 121.3774 | 0.112 | 0.22115 | 0.091919 | 0.012677 | -0.006707 | 0.073575 | 0.012293 | 0.033449 | 0.11871 | 0.099708 | 0.098626 | 0.079626
6286.5625 | 122.4747 | -121.3577 | 0.86517 | 0.12185 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.05072 | -0.019364 | -0.047906 | 0.036954 | -0.033484 | -0.00775 | 121.4796 | 121.363 | 121.3411 | 121.3602 | 121.3665 | 121.4387 | 121.3454 | 0.11658 | 0.22115 | 0.091919 | 0.021835 | -0.006707 | 0.078153 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.098626 | 0.084204
6288.2656 | 122.4518 | -121.3943 | 0.8194 | 0.12643 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.05072 | -0.023943 | -0.03875 | 0.036954 | -0.033484 | -0.00775 | 121.5208 | 121.3996 | 121.3778 | 121.3922 | 121.4031 | 121.4754 | 121.3866 | 0.112 | 0.22573 | 0.091919 | 0.017256 | 0.002449 | 0.078153 | 0.007715 | 0.033449 | 0.10955 | 0.10429 | 0.08947 | 0.084204
6289.9688 | 122.4655 | -121.4035 | 0.85144 | 0.12643 | 0.005267 | -0.007421 | 0.002454 | 0.013375 | 0.071848 | -0.007779 | 0.061645 | 0.18453 | 0.046142 | -0.019364 | -0.034171 | 0.032376 | -0.038063 | -0.00775 | 121.5299 | 121.4088 | 121.3961 | 121.406 | 121.4169 | 121.4754 | 121.3957 | 0.10284 | 0.22573 | 0.087341 | 0.021835 | 0.007028 | 0.073575 | 0.003136 | 0.033449 | 0.095816 | 0.099708 | 0.080313 | 0.084205
6291.6875 | 122.493 | -121.4218 | 0.82855 | 0.11727 | 0.005267 | -0.021157 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | 0.001406 | 121.5391 | 121.4271 | 121.4007 | 121.4243 | 121.4352 | 121.5028 | 121.414 | 0.112 | 0.22573 | 0.096497 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.042605 | 0.11413 | 0.10887 | 0.098626 | 0.093361
6293.3906 | 122.5204 | -121.3943 | 0.82398 | 0.12185 | 0.000689 | -0.012 | 0.007033 | 0.004219 | 0.085583 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.019364 | -0.047906 | 0.027798 | -0.033484 | -0.003172 | 121.5162 | 121.395 | 121.3823 | 121.4014 | 121.3986 | 121.4799 | 121.3911 | 0.11658 | 0.21657 | 0.091919 | 0.021835 | -0.006707 | 0.068997 | 0.007715 | 0.038027 | 0.12329 | 0.10886 | 0.098626 | 0.084204
6295.1406 | 122.4426 | -121.4355 | 0.84686 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.017953 | 0.085583 | -0.003201 | 0.066223 | 0.17537 | 0.055298 | -0.019364 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.562 | 121.4362 | 121.4281 | 121.438 | 121.4535 | 121.5211 | 121.4323 | 0.10742 | 0.21657 | 0.096497 | 0.021835 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.094048 | 0.093361
6296.8438 | 122.4243 | -121.4401 | 0.83771 | 0.12643 | 0.000689 | -0.012 | 0.002454 | -0.000359 | 0.071848 | -0.003201 | 0.07538 | 0.17537 | 0.046142 | -0.028522 | -0.03875 | 0.027798 | -0.033484 | 0.001406 | 121.5666 | 121.4408 | 121.4281 | 121.4426 | 121.4398 | 121.512 | 121.4369 | 0.11658 | 0.21657 | 0.087341 | 0.012677 | 0.002449 | 0.068997 | 0.007715 | 0.042605 | 0.11413 | 0.10886 | 0.084892 | 0.079626
6298.5625 | 122.5204 | -121.3989 | 0.82398 | 0.12643 | -0.00389 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.032376 | -0.033484 | -0.003172 | 121.5254 | 121.395 | 121.3823 | 121.3968 | 121.4077 | 121.4799 | 121.3911 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10886 | 0.084892 | 0.079626
6300.2656 | 122.4518 | -121.4447 | 0.85602 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.061645 | 0.17995 | 0.05072 | -0.019364 | -0.03875 | 0.027798 | -0.033484 | -0.012328 | 121.5711 | 121.4454 | 121.4373 | 121.4472 | 121.4581 | 121.5257 | 121.4461 | 0.10284 | 0.22115 | 0.091919 | 0.021835 | 0.002449 | 0.068997 | 0.007715 | 0.028871 | 0.10039 | 0.095129 | 0.08947 | 0.084204
6302 | 122.493 | -121.4401 | 0.83771 | 0.12185 | 0.000689 | -0.007421 | 0.007033 | 0.008797 | 0.076426 | -0.012357 | 0.066223 | 0.18453 | 0.041563 | -0.028522 | -0.043328 | 0.027798 | -0.028906 | -0.003172 | 121.562 | 121.4408 | 121.4327 | 121.4472 | 121.4489 | 121.5166 | 121.4278 | 0.10742 | 0.22573 | 0.082762 | 0.012677 | -0.002129 | 0.068997 | 0.012293 | 0.038027 | 0.10955 | 0.095129 | 0.084891 | 0.070469
6303.7344 | 122.4152 | -121.4813 | 0.88348 | 0.13101 | 0.005267 | -0.012 | 0.011611 | 0.008797 | 0.085583 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.03875 | 0.032376 | -0.038063 | -0.012328 | 121.6123 | 121.4866 | 121.4693 | 121.4929 | 121.4901 | 121.5669 | 121.4735 | 0.112 | 0.22115 | 0.091919 | 0.012677 | 0.002449 | 0.073575 | 0.003136 | 0.028871 | 0.10955 | 0.10887 | 0.08947 | 0.088783
6305.4375 | 122.4609 | -121.4493 | 0.8194 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.017953 | 0.085583 | -0.003201 | 0.070802 | 0.17079 | 0.046142 | -0.014785 | -0.047906 | 0.032376 | -0.038063 | -0.00775 | 121.5711 | 121.4545 | 121.4373 | 121.4517 | 121.4672 | 121.5349 | 121.4461 | 0.112 | 0.21199 | 0.087341 | 0.026414 | -0.006707 | 0.073575 | 0.003136 | 0.033449 | 0.11871 | 0.10887 | 0.094048 | 0.084205
6307.1406 | 122.4518 | -121.4447 | 0.82398 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.066223 | 0.18453 | 0.055298 | -0.019364 | -0.03875 | 0.027798 | -0.038063 | -0.003172 | 121.5666 | 121.4545 | 121.4281 | 121.4472 | 121.4581 | 121.5257 | 121.4461 | 0.10742 | 0.22573 | 0.096497 | 0.021835 | 0.002449 | 0.068997 | 0.003136 | 0.038027 | 0.10497 | 0.10429 | 0.094048 | 0.093361
6308.8594 | 122.4197 | -121.4722 | 0.82855 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | -0.012328 | 121.5986 | 121.4729 | 121.4647 | 121.47 | 121.4855 | 121.5532 | 121.4644 | 0.112 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.028871 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6310.6094 | 122.4289 | -121.4676 | 0.85144 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.017953 | 0.076426 | 0.005955 | 0.07538 | 0.18453 | 0.041563 | -0.019364 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.594 | 121.4683 | 121.451 | 121.47 | 121.4855 | 121.544 | 121.4735 | 0.11658 | 0.22573 | 0.082762 | 0.021835 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.11871 | 0.11344 | 0.084891 | 0.079626
6312.2969 | 122.5296 | -121.4355 | 0.82398 | 0.12185 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.016936 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.047906 | 0.027798 | -0.028906 | -0.00775 | 121.5574 | 121.4362 | 121.4235 | 121.438 | 121.4443 | 121.5211 | 121.4186 | 0.112 | 0.22115 | 0.091919 | 0.012677 | -0.006707 | 0.068997 | 0.012293 | 0.033449 | 0.11871 | 0.099708 | 0.098626 | 0.079626
6314 | 122.5662 | -121.4218 | 0.80109 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.034171 | 0.027798 | -0.038063 | -0.00775 | 121.5482 | 121.4225 | 121.4098 | 121.4197 | 121.4306 | 121.5028 | 121.4232 | 0.112 | 0.21657 | 0.091919 | 0.017256 | 0.007028 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.10887 | 0.084891 | 0.088783
6315.7031 | 122.4335 | -121.4722 | 0.81482 | 0.13101 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.066223 | 0.18453 | 0.05072 | -0.019364 | -0.047906 | 0.032376 | -0.038063 | -0.00775 | 121.6032 | 121.482 | 121.4647 | 121.4746 | 121.481 | 121.5532 | 121.4735 | 0.10742 | 0.22573 | 0.091919 | 0.021835 | -0.006707 | 0.073575 | 0.003136 | 0.033449 | 0.11413 | 0.10429 | 0.098626 | 0.088783
6317.4062 | 122.3969 | -121.4493 | 0.84228 | 0.13101 | 0.000689 | -0.007421 | -0.006703 | -0.000359 | 0.076426 | 0.001377 | 0.07538 | 0.17995 | 0.05072 | -0.019364 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.5803 | 121.45 | 121.4419 | 121.4426 | 121.4489 | 121.5257 | 121.4507 | 0.11658 | 0.22115 | 0.091919 | 0.021835 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.098626 | 0.084204
6319.125 | 122.5525 | -121.4539 | 0.82398 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | 0.001377 | 0.070802 | 0.17995 | 0.046142 | -0.019364 | -0.03875 | 0.032376 | -0.028906 | 0.001406 | 121.5803 | 121.4591 | 121.4464 | 121.4517 | 121.4672 | 121.5349 | 121.4552 | 0.112 | 0.22115 | 0.087341 | 0.021835 | 0.002449 | 0.073575 | 0.012293 | 0.042605 | 0.10955 | 0.099708 | 0.084892 | 0.075048
6320.8281 | 122.5433 | -121.4172 | 0.78278 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.07538 | 0.17995 | 0.041563 | -0.023943 | -0.043328 | 0.032376 | -0.028906 | -0.00775 | 121.5437 | 121.4179 | 121.4052 | 121.4151 | 121.4215 | 121.5028 | 121.4095 | 0.11658 | 0.22115 | 0.082762 | 0.017256 | -0.002129 | 0.073575 | 0.012293 | 0.033449 | 0.11871 | 0.10429 | 0.084891 | 0.070469
6322.5469 | 122.4564 | -121.4905 | 0.8194 | 0.12643 | -0.00389 | -0.007421 | 0.002454 | 0.004219 | 0.085583 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.03875 | 0.027798 | -0.033484 | -0.016906 | 121.6169 | 121.4866 | 121.4831 | 121.4929 | 121.4947 | 121.5761 | 121.4873 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.002449 | 0.068997 | 0.007715 | 0.024293 | 0.11413 | 0.10886 | 0.08947 | 0.084204
6324.25 | 122.5662 | -121.4584 | 0.81024 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.013375 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.033101 | -0.03875 | 0.032376 | -0.028906 | -0.003172 | 121.5849 | 121.4545 | 121.4464 | 121.4563 | 121.4718 | 121.5349 | 121.4507 | 0.11658 | 0.22115 | 0.091919 | 0.008098 | 0.002449 | 0.073575 | 0.012293 | 0.038027 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6325.9531 | 122.5342 | -121.4676 | 0.78278 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.066223 | 0.18911 | 0.046142 | -0.023943 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.594 | 121.4637 | 121.4556 | 121.4655 | 121.4764 | 121.5486 | 121.4598 | 0.10742 | 0.23031 | 0.087341 | 0.017256 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.084892 | 0.084205
6327.6562 | 122.58 | -121.4355 | 0.80109 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.047906 | 0.027798 | -0.038063 | -0.003172 | 121.5666 | 121.4408 | 121.4235 | 121.438 | 121.4443 | 121.512 | 121.4278 | 0.112 | 0.21657 | 0.091919 | 0.017256 | -0.006707 | 0.068997 | 0.003136 | 0.038027 | 0.11871 | 0.10887 | 0.098626 | 0.088783
6329.3906 | 122.5662 | -121.463 | 0.80109 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.076426 | -0.003201 | 0.061645 | 0.17995 | 0.046142 | -0.028522 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.5894 | 121.4683 | 121.451 | 121.4655 | 121.4718 | 121.5394 | 121.4598 | 0.10284 | 0.22115 | 0.087341 | 0.012677 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.10955 | 0.095129 | 0.094048 | 0.079626
6331.0938 | 122.5067 | -121.4584 | 0.81482 | 0.12185 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.066223 | 0.17537 | 0.046142 | -0.028522 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.5803 | 121.4591 | 121.4464 | 121.4609 | 121.4672 | 121.5394 | 121.4507 | 0.10742 | 0.21657 | 0.087341 | 0.012677 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6332.7969 | 122.4243 | -121.4859 | 0.83771 | 0.13101 | 0.005267 | -0.012 | 0.011611 | 0.013375 | 0.081005 | -0.003201 | 0.079959 | 0.17537 | 0.055298 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.6169 | 121.4912 | 121.4739 | 121.4975 | 121.4993 | 121.5669 | 121.4827 | 0.12116 | 0.21657 | 0.096497 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.11802 | 0.098626 | 0.093361
6334.5156 | 122.5571 | -121.4493 | 0.80109 | 0.13101 | 0.000689 | -0.016578 | -0.002124 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.18453 | 0.046142 | -0.028522 | -0.03875 | 0.027798 | -0.042641 | -0.012328 | 121.5803 | 121.45 | 121.4327 | 121.4472 | 121.4581 | 121.5211 | 121.4461 | 0.11658 | 0.22573 | 0.087341 | 0.012677 | 0.002449 | 0.068997 | -0.001442 | 0.028871 | 0.11413 | 0.11802 | 0.084892 | 0.088783
6336.2188 | 122.4289 | -121.4813 | 0.81024 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.090161 | -0.003201 | 0.066223 | 0.18911 | 0.05072 | -0.033101 | -0.047906 | 0.032376 | -0.033484 | -0.003172 | 121.6123 | 121.4866 | 121.4693 | 121.4838 | 121.4901 | 121.5715 | 121.4781 | 0.10742 | 0.23031 | 0.091919 | 0.008098 | -0.006707 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.099707 | 0.098626 | 0.084204
6337.9375 | 122.3969 | -121.4996 | 0.82855 | 0.12643 | 0.005267 | -0.007421 | 0.007033 | 0.008797 | 0.081005 | -0.007779 | 0.066223 | 0.18453 | 0.046142 | -0.028522 | -0.047906 | 0.027798 | -0.038063 | -0.003172 | 121.6261 | 121.5049 | 121.4922 | 121.5067 | 121.5084 | 121.5806 | 121.4919 | 0.10742 | 0.22573 | 0.087341 | 0.012677 | -0.006707 | 0.068997 | 0.003136 | 0.038027 | 0.11413 | 0.10429 | 0.094048 | 0.084205
6339.6562 | 122.5388 | -121.4767 | 0.7782 | 0.13101 | 0.005267 | 0.001736 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.033101 | -0.03875 | 0.032376 | -0.033484 | -0.003172 | 121.6078 | 121.482 | 121.4785 | 121.4746 | 121.4901 | 121.5623 | 121.4735 | 0.11658 | 0.22115 | 0.091919 | 0.008098 | 0.002449 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10886 | 0.08947 | 0.084204
6341.3594 | 122.4747 | -121.5179 | 0.80566 | 0.12643 | 0.009846 | -0.002842 | -0.002124 | 0.013375 | 0.085583 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.03875 | 0.032376 | -0.033484 | -0.00775 | 121.6444 | 121.5278 | 121.5151 | 121.5158 | 121.5313 | 121.6035 | 121.5193 | 0.112 | 0.21657 | 0.091919 | 0.017256 | 0.002449 | 0.073575 | 0.007715 | 0.033449 | 0.10955 | 0.10429 | 0.08947 | 0.084204
6343.0625 | 122.5845 | -121.4722 | 0.80109 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.6032 | 121.4774 | 121.4602 | 121.4746 | 121.481 | 121.5532 | 121.4644 | 0.112 | 0.22115 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6344.7656 | 122.5296 | -121.4722 | 0.78278 | 0.12643 | 0.009846 | -0.012 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.043328 | 0.02322 | -0.042641 | -0.00775 | 121.5986 | 121.482 | 121.4602 | 121.4746 | 121.4855 | 121.5532 | 121.4735 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.002129 | 0.064419 | -0.001442 | 0.033449 | 0.11413 | 0.11344 | 0.094048 | 0.093361
6346.5 | 122.5708 | -121.4767 | 0.80566 | 0.13101 | 0.009846 | -0.016578 | -0.002124 | 0.008797 | 0.071848 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.028522 | -0.043328 | 0.027798 | -0.028906 | -0.003172 | 121.6078 | 121.4866 | 121.4602 | 121.4746 | 121.4855 | 121.5486 | 121.4735 | 0.11658 | 0.22573 | 0.096497 | 0.012677 | -0.002129 | 0.068997 | 0.012293 | 0.038027 | 0.11871 | 0.10429 | 0.098626 | 0.084204
6348.2188 | 122.4655 | -121.5042 | 0.8194 | 0.13101 | 0.005267 | -0.012 | -0.006703 | -0.000359 | 0.076426 | 0.001377 | 0.070802 | 0.17537 | 0.055298 | -0.019364 | -0.034171 | 0.02322 | -0.033484 | -0.003172 | 121.6352 | 121.5095 | 121.4922 | 121.4975 | 121.5039 | 121.5806 | 121.5056 | 0.112 | 0.21657 | 0.096497 | 0.021835 | 0.007028 | 0.064419 | 0.007715 | 0.038027 | 0.10497 | 0.10429 | 0.089469 | 0.088782
6349.9219 | 122.5662 | -121.4722 | 0.80109 | 0.12643 | 0.005267 | -0.007421 | -0.006703 | 0.004219 | 0.076426 | -0.007779 | 0.066223 | 0.17995 | 0.05072 | -0.014785 | -0.047906 | 0.032376 | -0.038063 | -0.012328 | 121.5986 | 121.4774 | 121.4647 | 121.4655 | 121.4764 | 121.5486 | 121.4644 | 0.10742 | 0.22115 | 0.091919 | 0.026414 | -0.006707 | 0.073575 | 0.003136 | 0.028871 | 0.11413 | 0.10429 | 0.098626 | 0.088783
6351.6406 | 122.4884 | -121.5088 | 0.82398 | 0.13101 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | 0.005955 | 0.061645 | 0.18911 | 0.046142 | -0.023943 | -0.043328 | 0.032376 | -0.033484 | -0.012328 | 121.6398 | 121.5095 | 121.5014 | 121.5067 | 121.5176 | 121.5852 | 121.5147 | 0.10284 | 0.23031 | 0.087341 | 0.017256 | -0.002129 | 0.073575 | 0.007715 | 0.028871 | 0.10497 | 0.095129 | 0.08947 | 0.079626
6353.3438 | 122.5662 | -121.4767 | 0.81482 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.013375 | 0.076426 | 0.001377 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.6032 | 121.482 | 121.4647 | 121.4746 | 121.4901 | 121.5532 | 121.4781 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.094048 | 0.079626
6355.0469 | 122.5433 | -121.4584 | 0.79651 | 0.13101 | 0.000689 | -0.007421 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.028522 | -0.043328 | 0.036954 | -0.038063 | -0.012328 | 121.5894 | 121.4591 | 121.451 | 121.4563 | 121.4718 | 121.5349 | 121.4552 | 0.12116 | 0.22573 | 0.091919 | 0.012677 | -0.002129 | 0.078153 | 0.003136 | 0.028871 | 0.12329 | 0.11802 | 0.094048 | 0.088783
6356.7812 | 122.4518 | -121.5408 | 0.8194 | 0.12643 | 0.000689 | -0.002842 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.046142 | -0.019364 | -0.043328 | 0.02322 | -0.033484 | -0.003172 | 121.6673 | 121.5415 | 121.538 | 121.5433 | 121.5496 | 121.6173 | 121.5331 | 0.112 | 0.22573 | 0.087341 | 0.021835 | -0.002129 | 0.064419 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6358.5312 | 122.58 | -121.4722 | 0.77362 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.02322 | -0.038063 | -0.012328 | 121.5986 | 121.4774 | 121.4602 | 121.4746 | 121.4855 | 121.5532 | 121.469 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.064419 | 0.003136 | 0.028871 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6360.2344 | 122.4564 | -121.5317 | 0.81482 | 0.13101 | 0.009846 | -0.016578 | 0.002454 | 0.013375 | 0.071848 | -0.007779 | 0.070802 | 0.17537 | 0.055298 | -0.023943 | -0.047906 | 0.027798 | -0.028906 | -0.00775 | 121.6627 | 121.5415 | 121.5151 | 121.5341 | 121.5451 | 121.6035 | 121.5239 | 0.112 | 0.21657 | 0.096497 | 0.017256 | -0.006707 | 0.068997 | 0.012293 | 0.033449 | 0.11871 | 0.099708 | 0.1032 | 0.084204
6361.9531 | 122.5845 | -121.4859 | 0.80109 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.019364 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.6123 | 121.4957 | 121.4785 | 121.4838 | 121.4947 | 121.5715 | 121.4827 | 0.11658 | 0.22115 | 0.087341 | 0.021835 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.11413 | 0.11344 | 0.084892 | 0.084205
6363.6719 | 122.5067 | -121.5271 | 0.82398 | 0.13101 | 0.005267 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.066223 | 0.17537 | 0.055298 | -0.019364 | -0.043328 | 0.02322 | -0.033484 | -0.00775 | 121.6581 | 121.5324 | 121.5151 | 121.525 | 121.5405 | 121.6127 | 121.5239 | 0.10742 | 0.21657 | 0.096497 | 0.021835 | -0.002129 | 0.064419 | 0.007715 | 0.033449 | 0.10955 | 0.099707 | 0.098626 | 0.088782
6365.375 | 122.5433 | -121.5179 | 0.78735 | 0.13101 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.090161 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.649 | 121.5232 | 121.5105 | 121.5204 | 121.5267 | 121.6081 | 121.5147 | 0.112 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6367.1094 | 122.5021 | -121.5225 | 0.80566 | 0.12643 | 0.009846 | -0.007421 | 0.007033 | 0.004219 | 0.076426 | -0.003201 | 0.070802 | 0.17537 | 0.046142 | -0.028522 | -0.03875 | 0.027798 | -0.038063 | 0.001406 | 121.649 | 121.5324 | 121.5151 | 121.5296 | 121.5267 | 121.5989 | 121.5193 | 0.112 | 0.21657 | 0.087341 | 0.012677 | 0.002449 | 0.068997 | 0.003136 | 0.042605 | 0.10955 | 0.10887 | 0.084892 | 0.084205
6368.8125 | 122.4884 | -121.5317 | 0.81482 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.18453 | 0.05072 | -0.028522 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.6581 | 121.5369 | 121.5243 | 121.5296 | 121.5405 | 121.6127 | 121.5331 | 0.112 | 0.22573 | 0.091919 | 0.012677 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6370.5625 | 122.4884 | -121.5408 | 0.82398 | 0.13101 | 0.000689 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.6718 | 121.5415 | 121.5334 | 121.5387 | 121.5542 | 121.6218 | 121.5376 | 0.12116 | 0.22573 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.12329 | 0.11802 | 0.094048 | 0.088783
6372.2656 | 122.493 | -121.5454 | 0.81024 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.022531 | 0.085583 | -0.003201 | 0.07538 | 0.18911 | 0.046142 | -0.023943 | -0.03875 | 0.027798 | -0.028906 | -0.003172 | 121.6718 | 121.5461 | 121.5334 | 121.5479 | 121.5679 | 121.631 | 121.5422 | 0.11658 | 0.23031 | 0.087341 | 0.017256 | 0.002449 | 0.068997 | 0.012293 | 0.038027 | 0.11413 | 0.10429 | 0.084892 | 0.075048
6373.9688 | 122.6028 | -121.4996 | 0.76446 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17079 | 0.046142 | -0.023943 | -0.03875 | 0.036954 | -0.028906 | -0.00775 | 121.6261 | 121.5003 | 121.4876 | 121.5021 | 121.5084 | 121.5806 | 121.4919 | 0.112 | 0.21199 | 0.087341 | 0.017256 | 0.002449 | 0.078153 | 0.012293 | 0.033449 | 0.10955 | 0.099708 | 0.084892 | 0.075048
6375.6719 | 122.5891 | -121.4859 | 0.78735 | 0.12185 | 0.005267 | -0.012 | 0.011611 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.028522 | -0.029593 | 0.02322 | -0.038063 | 0.001406 | 121.6078 | 121.4912 | 121.4739 | 121.4975 | 121.4947 | 121.5669 | 121.4827 | 0.10742 | 0.22115 | 0.087341 | 0.012677 | 0.011606 | 0.064419 | 0.003136 | 0.042605 | 0.095816 | 0.10429 | 0.075735 | 0.084205
6377.375 | 122.58 | -121.5042 | 0.78735 | 0.11727 | 0.005267 | -0.002842 | 0.002454 | 0.013375 | 0.071848 | -0.007779 | 0.07538 | 0.17995 | 0.041563 | -0.014785 | -0.043328 | 0.02322 | -0.042641 | -0.00775 | 121.6215 | 121.5095 | 121.5014 | 121.5067 | 121.5176 | 121.5761 | 121.4964 | 0.11658 | 0.22115 | 0.082762 | 0.026414 | -0.002129 | 0.064419 | -0.001442 | 0.033449 | 0.11871 | 0.11802 | 0.084891 | 0.084204
6379.125 | 122.493 | -121.5408 | 0.80109 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.076426 | 0.001377 | 0.066223 | 0.17995 | 0.05072 | -0.014785 | -0.03875 | 0.027798 | -0.038063 | -0.003172 | 121.6627 | 121.5461 | 121.5288 | 121.5433 | 121.5496 | 121.6173 | 121.5422 | 0.10742 | 0.22115 | 0.091919 | 0.026414 | 0.002449 | 0.068997 | 0.003136 | 0.038027 | 0.10497 | 0.10429 | 0.08947 | 0.088783
6380.8281 | 122.5983 | -121.5042 | 0.7782 | 0.12643 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.055298 | -0.019364 | -0.03875 | 0.032376 | -0.033484 | -0.003172 | 121.6306 | 121.5141 | 121.4876 | 121.5067 | 121.513 | 121.5898 | 121.501 | 0.11658 | 0.22115 | 0.096497 | 0.021835 | 0.002449 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10886 | 0.094048 | 0.088782
6382.5938 | 122.5754 | -121.5454 | 0.79193 | 0.12185 | -0.00389 | -0.012 | 0.011611 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.041563 | -0.023943 | -0.043328 | 0.027798 | -0.028906 | -0.00775 | 121.6673 | 121.5415 | 121.5334 | 121.557 | 121.5588 | 121.6264 | 121.5376 | 0.11658 | 0.22115 | 0.082762 | 0.017256 | -0.002129 | 0.068997 | 0.012293 | 0.033449 | 0.11871 | 0.10429 | 0.084891 | 0.070469
6384.3438 | 122.5479 | -121.5363 | 0.78278 | 0.12185 | 0.005267 | -0.002842 | 0.011611 | 0.017953 | 0.085583 | 0.001377 | 0.070802 | 0.18911 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.6581 | 121.5415 | 121.5334 | 121.5479 | 121.5542 | 121.6218 | 121.5376 | 0.112 | 0.23031 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6386.0469 | 122.5845 | -121.4996 | 0.76904 | 0.13101 | 0.005267 | -0.007421 | 0.007033 | 0.013375 | 0.076426 | -0.003201 | 0.066223 | 0.17995 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.033484 | -0.003172 | 121.6306 | 121.5049 | 121.4922 | 121.5067 | 121.513 | 121.5761 | 121.4964 | 0.10742 | 0.22115 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.099707 | 0.08947 | 0.084204
6387.7344 | 122.5845 | -121.5363 | 0.78278 | 0.12643 | 0.000689 | -0.012 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.079959 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.6627 | 121.5369 | 121.5243 | 121.5341 | 121.5496 | 121.6127 | 121.5331 | 0.12116 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.12329 | 0.11344 | 0.08947 | 0.079626
6389.4531 | 122.58 | -121.5179 | 0.76904 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.17079 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.6444 | 121.5232 | 121.5105 | 121.5158 | 121.5267 | 121.6035 | 121.5147 | 0.11658 | 0.21199 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6391.1719 | 122.5204 | -121.5454 | 0.78735 | 0.13101 | -0.00389 | -0.012 | 0.007033 | 0.008797 | 0.085583 | 0.001377 | 0.079959 | 0.17537 | 0.041563 | -0.028522 | -0.043328 | 0.02322 | -0.038063 | -0.00775 | 121.6764 | 121.5415 | 121.5334 | 121.5524 | 121.5542 | 121.631 | 121.5468 | 0.12116 | 0.21657 | 0.082762 | 0.012677 | -0.002129 | 0.064419 | 0.003136 | 0.033449 | 0.12329 | 0.11802 | 0.084891 | 0.079626
6392.875 | 122.5983 | -121.4905 | 0.7782 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.046142 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.012328 | 121.6123 | 121.4957 | 121.4831 | 121.4929 | 121.4947 | 121.5715 | 121.4873 | 0.112 | 0.21657 | 0.087341 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.028871 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6394.5938 | 122.5571 | -121.5225 | 0.79651 | 0.13101 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.066223 | 0.17537 | 0.046142 | -0.028522 | -0.043328 | 0.02322 | -0.033484 | -0.003172 | 121.6535 | 121.5278 | 121.5105 | 121.5204 | 121.5313 | 121.5989 | 121.5193 | 0.10742 | 0.21657 | 0.087341 | 0.012677 | -0.002129 | 0.064419 | 0.007715 | 0.038027 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6396.2969 | 122.5983 | -121.5042 | 0.7782 | 0.13101 | 0.009846 | -0.016578 | 0.007033 | 0.017953 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.033101 | -0.043328 | 0.032376 | -0.038063 | -0.012328 | 121.6352 | 121.5141 | 121.4876 | 121.5112 | 121.5222 | 121.5852 | 121.501 | 0.112 | 0.22115 | 0.091919 | 0.008098 | -0.002129 | 0.073575 | 0.003136 | 0.028871 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6398.0156 | 122.5983 | -121.5225 | 0.78735 | 0.13101 | -0.00389 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.041563 | -0.023943 | -0.043328 | 0.02322 | -0.04722 | -0.00775 | 121.6535 | 121.5186 | 121.5151 | 121.5204 | 121.5359 | 121.6035 | 121.5147 | 0.112 | 0.22573 | 0.082762 | 0.017256 | -0.002129 | 0.064419 | -0.006021 | 0.033449 | 0.11413 | 0.11802 | 0.084891 | 0.088783
6399.7188 | 122.5479 | -121.5271 | 0.7782 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.649 | 121.5324 | 121.5105 | 121.525 | 121.5359 | 121.6081 | 121.5147 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.11344 | 0.094048 | 0.084205
6401.4375 | 122.6166 | -121.5225 | 0.77362 | 0.12643 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.05072 | -0.019364 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.649 | 121.5278 | 121.5059 | 121.5204 | 121.5313 | 121.6035 | 121.5193 | 0.10742 | 0.22115 | 0.091919 | 0.021835 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.08947 | 0.088783
6403.1406 | 122.5708 | -121.5179 | 0.78278 | 0.13101 | 0.009846 | -0.007421 | -0.002124 | 0.004219 | 0.081005 | -0.012357 | 0.070802 | 0.17995 | 0.046142 | -0.028522 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.649 | 121.5278 | 121.5105 | 121.5158 | 121.5222 | 121.5989 | 121.5056 | 0.112 | 0.22115 | 0.087341 | 0.012677 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.11871 | 0.10429 | 0.094048 | 0.079626
6404.8438 | 122.5571 | -121.5363 | 0.79193 | 0.13101 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.6673 | 121.5369 | 121.5288 | 121.5387 | 121.5451 | 121.6173 | 121.5285 | 0.112 | 0.22115 | 0.091919 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.11871 | 0.10887 | 0.098626 | 0.088783
6406.6094 | 122.5479 | -121.5363 | 0.80109 | 0.12643 | 0.005267 | -0.002842 | 0.002454 | 0.008797 | 0.081005 | 0.005955 | 0.07538 | 0.17537 | 0.055298 | -0.028522 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.6627 | 121.5415 | 121.5334 | 121.5387 | 121.5451 | 121.6173 | 121.5422 | 0.11658 | 0.21657 | 0.096497 | 0.012677 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.1032 | 0.088782
6408.3594 | 122.525 | -121.5591 | 0.80109 | 0.13101 | 0.005267 | -0.007421 | -0.002124 | -0.000359 | 0.081005 | -0.007779 | 0.07538 | 0.17537 | 0.046142 | -0.019364 | -0.03875 | 0.027798 | -0.042641 | -0.003172 | 121.6902 | 121.5644 | 121.5517 | 121.557 | 121.5588 | 121.6401 | 121.5514 | 0.11658 | 0.21657 | 0.087341 | 0.021835 | 0.002449 | 0.068997 | -0.001442 | 0.038027 | 0.11413 | 0.11802 | 0.084892 | 0.088783
6410.0625 | 122.5662 | -121.5683 | 0.78735 | 0.13101 | -0.00389 | -0.002842 | -0.006703 | 0.008797 | 0.085583 | 0.001377 | 0.066223 | 0.18453 | 0.055298 | -0.023943 | -0.03875 | 0.027798 | -0.033484 | 0.001406 | 121.6993 | 121.5644 | 121.5655 | 121.5616 | 121.5771 | 121.6539 | 121.5697 | 0.10742 | 0.22573 | 0.096497 | 0.017256 | 0.002449 | 0.068997 | 0.007715 | 0.042605 | 0.10497 | 0.099707 | 0.094048 | 0.088782
6411.7656 | 122.5342 | -121.5454 | 0.79651 | 0.13101 | 0.005267 | -0.016578 | -0.002124 | 0.013375 | 0.081005 | 0.001377 | 0.070802 | 0.17079 | 0.05072 | -0.028522 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.6764 | 121.5507 | 121.5288 | 121.5433 | 121.5588 | 121.6264 | 121.5468 | 0.112 | 0.21199 | 0.091919 | 0.012677 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6413.4688 | 122.5754 | -121.5179 | 0.78278 | 0.12643 | 0.000689 | -0.012 | 0.007033 | 0.013375 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.055298 | -0.023943 | -0.03875 | 0.036954 | -0.033484 | -0.00775 | 121.6444 | 121.5186 | 121.5059 | 121.525 | 121.5313 | 121.5989 | 121.5056 | 0.11658 | 0.22115 | 0.096497 | 0.017256 | 0.002449 | 0.078153 | 0.007715 | 0.033449 | 0.11413 | 0.10886 | 0.094048 | 0.088782
6415.1719 | 122.4976 | -121.5591 | 0.8194 | 0.12643 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.066223 | 0.17995 | 0.041563 | -0.019364 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.6856 | 121.5644 | 121.5517 | 121.5616 | 121.5679 | 121.6401 | 121.5605 | 0.10742 | 0.22115 | 0.082762 | 0.021835 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.11413 | 0.099707 | 0.089469 | 0.075047
6416.875 | 122.5204 | -121.5775 | 0.81024 | 0.13101 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.079959 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.02322 | -0.038063 | -0.012328 | 121.7085 | 121.5873 | 121.57 | 121.5799 | 121.5863 | 121.6585 | 121.5743 | 0.12116 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.064419 | 0.003136 | 0.028871 | 0.12787 | 0.11802 | 0.094048 | 0.084205
6418.5938 | 122.6166 | -121.5225 | 0.78735 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.007779 | 0.070802 | 0.17537 | 0.055298 | -0.033101 | -0.043328 | 0.032376 | -0.042641 | -0.00775 | 121.6444 | 121.5278 | 121.5105 | 121.525 | 121.5313 | 121.6081 | 121.5147 | 0.112 | 0.21657 | 0.096497 | 0.008098 | -0.002129 | 0.073575 | -0.001442 | 0.033449 | 0.11413 | 0.11344 | 0.098626 | 0.097939
6420.2969 | 122.6166 | -121.5179 | 0.76904 | 0.13101 | -0.00389 | -0.007421 | -0.006703 | 0.008797 | 0.085583 | -0.012357 | 0.070802 | 0.17995 | 0.041563 | -0.023943 | -0.03875 | 0.027798 | -0.028906 | -0.012328 | 121.649 | 121.5141 | 121.5105 | 121.5112 | 121.5267 | 121.6035 | 121.5056 | 0.112 | 0.22115 | 0.082762 | 0.017256 | 0.002449 | 0.068997 | 0.012293 | 0.028871 | 0.10955 | 0.099708 | 0.080313 | 0.070469
6422 | 122.5342 | -121.5591 | 0.80566 | 0.13101 | 0.000689 | -0.012 | 0.007033 | 0.008797 | 0.085583 | -0.007779 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.038063 | -0.012328 | 121.6902 | 121.5598 | 121.5471 | 121.5662 | 121.5679 | 121.6447 | 121.5514 | 0.112 | 0.21657 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.003136 | 0.028871 | 0.10955 | 0.10887 | 0.08947 | 0.088783
6423.7031 | 122.6212 | -121.5454 | 0.76446 | 0.12643 | 0.000689 | -0.012 | 0.007033 | 0.004219 | 0.090161 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.028522 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.6718 | 121.5461 | 121.5334 | 121.5524 | 121.5496 | 121.6356 | 121.5376 | 0.112 | 0.22115 | 0.087341 | 0.012677 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.11871 | 0.10887 | 0.094048 | 0.084205
6425.4062 | 122.493 | -121.55 | 0.82855 | 0.13101 | 0.005267 | -0.007421 | 0.007033 | 0.013375 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.05072 | -0.023943 | -0.047906 | 0.027798 | -0.033484 | -0.003172 | 121.681 | 121.5553 | 121.5426 | 121.557 | 121.5634 | 121.631 | 121.5468 | 0.10742 | 0.22115 | 0.091919 | 0.017256 | -0.006707 | 0.068997 | 0.007715 | 0.038027 | 0.11413 | 0.099707 | 0.098626 | 0.084204
6427.1094 | 122.5388 | -121.5363 | 0.82398 | 0.12643 | 0.009846 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.066223 | 0.17537 | 0.041563 | -0.023943 | -0.03875 | 0.032376 | -0.033484 | -0.00775 | 121.6627 | 121.5461 | 121.5243 | 121.5341 | 121.5496 | 121.6218 | 121.5331 | 0.10742 | 0.21657 | 0.082762 | 0.017256 | 0.002449 | 0.073575 | 0.007715 | 0.033449 | 0.10497 | 0.099707 | 0.080313 | 0.075047
6428.8125 | 122.5616 | -121.5271 | 0.81024 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.02322 | -0.038063 | -0.012328 | 121.649 | 121.5278 | 121.5197 | 121.5296 | 121.5359 | 121.6035 | 121.5193 | 0.112 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.064419 | 0.003136 | 0.028871 | 0.10955 | 0.10887 | 0.084892 | 0.084205
6430.5625 | 122.5433 | -121.5408 | 0.82855 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.061645 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.02322 | -0.033484 | -0.003172 | 121.6673 | 121.5415 | 121.5288 | 121.5433 | 121.5496 | 121.6218 | 121.5331 | 0.10284 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.064419 | 0.007715 | 0.038027 | 0.10497 | 0.095129 | 0.094048 | 0.084204
6432.2656 | 122.5708 | -121.5363 | 0.79651 | 0.11727 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.079959 | 0.18453 | 0.046142 | -0.019364 | -0.047906 | 0.02322 | -0.038063 | -0.003172 | 121.6535 | 121.5415 | 121.5288 | 121.5341 | 121.5496 | 121.6218 | 121.5331 | 0.12116 | 0.22573 | 0.087341 | 0.021835 | -0.006707 | 0.064419 | 0.003136 | 0.038027 | 0.12787 | 0.11802 | 0.094048 | 0.084205
6433.9688 | 122.5845 | -121.5134 | 0.80566 | 0.11727 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.028522 | -0.043328 | 0.02322 | -0.033484 | -0.003172 | 121.6306 | 121.5186 | 121.5014 | 121.5158 | 121.5267 | 121.5944 | 121.5102 | 0.11658 | 0.22573 | 0.096497 | 0.012677 | -0.002129 | 0.064419 | 0.007715 | 0.038027 | 0.11871 | 0.10886 | 0.098626 | 0.088782
6435.6875 | 122.5388 | -121.5271 | 0.82398 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.013375 | 0.071848 | 0.001377 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.043328 | 0.032376 | -0.033484 | 0.001406 | 121.6535 | 121.5278 | 121.5197 | 121.5296 | 121.5405 | 121.5989 | 121.5285 | 0.112 | 0.22115 | 0.091919 | 0.012677 | -0.002129 | 0.073575 | 0.007715 | 0.042605 | 0.11413 | 0.10429 | 0.094048 | 0.084204
6437.3906 | 122.6303 | -121.5042 | 0.78735 | 0.12643 | 0.000689 | -0.002842 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.066223 | 0.17079 | 0.059877 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.6306 | 121.5049 | 121.5014 | 121.5021 | 121.5176 | 121.5852 | 121.501 | 0.10742 | 0.21199 | 0.10108 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10429 | 0.1032 | 0.09794
6439.1406 | 122.5021 | -121.5591 | 0.81482 | 0.12185 | 0.000689 | -0.012 | -0.002124 | 0.017953 | 0.076426 | 0.005955 | 0.066223 | 0.18453 | 0.046142 | -0.019364 | -0.047906 | 0.032376 | -0.038063 | -0.00775 | 121.681 | 121.5598 | 121.5471 | 121.557 | 121.5771 | 121.6356 | 121.5651 | 0.10742 | 0.22573 | 0.087341 | 0.021835 | -0.006707 | 0.073575 | 0.003136 | 0.033449 | 0.11413 | 0.10429 | 0.094048 | 0.084205
6440.8438 | 122.5067 | -121.5775 | 0.81482 | 0.12185 | 0.014425 | 0.001736 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.6993 | 121.5919 | 121.5792 | 121.5753 | 121.5908 | 121.663 | 121.5743 | 0.112 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.11871 | 0.10887 | 0.094048 | 0.084205
6442.5625 | 122.493 | -121.5729 | 0.82398 | 0.12185 | 0.005267 | -0.016578 | 0.007033 | 0.013375 | 0.076426 | 0.001377 | 0.070802 | 0.18911 | 0.046142 | -0.014785 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.6947 | 121.5781 | 121.5563 | 121.5799 | 121.5863 | 121.6493 | 121.5743 | 0.112 | 0.23031 | 0.087341 | 0.026414 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.11871 | 0.10429 | 0.094048 | 0.079626
6444.2656 | 122.5067 | -121.5866 | 0.83771 | 0.12185 | 0.005267 | -0.016578 | 0.007033 | 0.013375 | 0.081005 | -0.007779 | 0.07538 | 0.17995 | 0.041563 | -0.028522 | -0.043328 | 0.02322 | -0.033484 | -0.012328 | 121.7085 | 121.5919 | 121.57 | 121.5936 | 121.6 | 121.6676 | 121.5788 | 0.11658 | 0.22115 | 0.082762 | 0.012677 | -0.002129 | 0.064419 | 0.007715 | 0.028871 | 0.11871 | 0.10886 | 0.084891 | 0.075047
6445.9844 | 122.6257 | -121.5225 | 0.79193 | 0.12185 | 0.005267 | -0.012 | -0.006703 | 0.013375 | 0.085583 | 0.001377 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.047906 | 0.02322 | -0.038063 | -0.00775 | 121.6444 | 121.5278 | 121.5105 | 121.5158 | 121.5359 | 121.6081 | 121.5239 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | -0.006707 | 0.064419 | 0.003136 | 0.033449 | 0.12329 | 0.11344 | 0.098626 | 0.088783
6447.7031 | 122.6212 | -121.4996 | 0.79651 | 0.12643 | 0.009846 | -0.012 | -0.002124 | 0.017953 | 0.076426 | -0.003201 | 0.061645 | 0.17995 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.6261 | 121.5095 | 121.4876 | 121.4975 | 121.5176 | 121.5761 | 121.4964 | 0.10284 | 0.22115 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10039 | 0.099708 | 0.08947 | 0.088783
6449.4062 | 122.58 | -121.5363 | 0.80566 | 0.13101 | 0.000689 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.007779 | 0.066223 | 0.17079 | 0.05072 | -0.028522 | -0.052484 | 0.032376 | -0.028906 | -0.00775 | 121.6673 | 121.5369 | 121.5243 | 121.5341 | 121.5451 | 121.6127 | 121.5285 | 0.10742 | 0.21199 | 0.091919 | 0.012677 | -0.011285 | 0.073575 | 0.012293 | 0.033449 | 0.11871 | 0.095129 | 0.1032 | 0.079626
6451.1094 | 122.644 | -121.4996 | 0.79651 | 0.11727 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.05072 | -0.028522 | -0.03875 | 0.02322 | -0.033484 | -0.00775 | 121.6169 | 121.5049 | 121.4922 | 121.5021 | 121.5084 | 121.5806 | 121.4964 | 0.10742 | 0.22115 | 0.091919 | 0.012677 | 0.002449 | 0.064419 | 0.007715 | 0.033449 | 0.10497 | 0.099707 | 0.08947 | 0.084204
6452.8125 | 122.5388 | -121.5729 | 0.84686 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.017953 | 0.085583 | 0.001377 | 0.066223 | 0.17995 | 0.046142 | -0.019364 | -0.047906 | 0.02322 | -0.038063 | -0.012328 | 121.6993 | 121.5736 | 121.5609 | 121.5753 | 121.5908 | 121.6585 | 121.5743 | 0.10742 | 0.22115 | 0.087341 | 0.021835 | -0.006707 | 0.064419 | 0.003136 | 0.028871 | 0.11413 | 0.10429 | 0.094048 | 0.084205
6454.5312 | 122.5571 | -121.5729 | 0.79651 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.017953 | 0.076426 | -0.012357 | 0.07538 | 0.17995 | 0.055298 | -0.028522 | -0.047906 | 0.032376 | -0.038063 | -0.00775 | 121.6993 | 121.5736 | 121.5655 | 121.5708 | 121.5908 | 121.6493 | 121.5605 | 0.11658 | 0.22115 | 0.096497 | 0.012677 | -0.006707 | 0.073575 | 0.003136 | 0.033449 | 0.12329 | 0.11344 | 0.1032 | 0.093361
6456.2812 | 122.5204 | -121.5454 | 0.83771 | 0.13559 | 0.009846 | -0.002842 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.043328 | 0.032376 | -0.033484 | -0.012328 | 121.681 | 121.5553 | 121.5426 | 121.5479 | 121.5588 | 121.6264 | 121.5422 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.002129 | 0.073575 | 0.007715 | 0.028871 | 0.11413 | 0.10429 | 0.094048 | 0.084204
6458.0469 | 122.5113 | -121.5775 | 0.83771 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.012328 | 121.7039 | 121.5827 | 121.5655 | 121.5799 | 121.5908 | 121.6585 | 121.5697 | 0.112 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.028871 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6459.75 | 122.644 | -121.5134 | 0.80109 | 0.12185 | 0.000689 | -0.007421 | -0.006703 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.6352 | 121.5141 | 121.5059 | 121.5067 | 121.5222 | 121.5944 | 121.5102 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.11871 | 0.11344 | 0.094048 | 0.088783
6461.4531 | 122.5113 | -121.5591 | 0.85144 | 0.13559 | -0.00389 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.024328 | -0.00775 | 121.6947 | 121.5553 | 121.5471 | 121.5616 | 121.5725 | 121.6356 | 121.5514 | 0.112 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | 0.016871 | 0.033449 | 0.11413 | 0.09513 | 0.08947 | 0.07047
6463.1562 | 122.6669 | -121.5271 | 0.80566 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.066223 | 0.17995 | 0.036985 | -0.019364 | -0.043328 | 0.027798 | -0.042641 | -0.00775 | 121.6535 | 121.5278 | 121.5197 | 121.525 | 121.5405 | 121.6035 | 121.5239 | 0.10742 | 0.22115 | 0.078184 | 0.021835 | -0.002129 | 0.068997 | -0.001442 | 0.033449 | 0.10955 | 0.10886 | 0.080313 | 0.079626
6464.8594 | 122.5891 | -121.5363 | 0.80566 | 0.12643 | 0.005267 | 0.001736 | -0.002124 | -0.000359 | 0.085583 | -0.003201 | 0.07538 | 0.18911 | 0.055298 | -0.033101 | -0.043328 | 0.032376 | -0.028906 | -0.00775 | 121.6627 | 121.5415 | 121.538 | 121.5341 | 121.5359 | 121.6218 | 121.5331 | 0.11658 | 0.23031 | 0.096497 | 0.008098 | -0.002129 | 0.073575 | 0.012293 | 0.033449 | 0.11871 | 0.10429 | 0.098626 | 0.084204
6466.6094 | 122.5525 | -121.6095 | 0.79193 | 0.13101 | 0.005267 | -0.002842 | 0.002454 | 0.013375 | 0.081005 | -0.012357 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.7405 | 121.6148 | 121.6067 | 121.612 | 121.6229 | 121.6905 | 121.5971 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.094048 | 0.084204
6468.2969 | 122.644 | -121.5775 | 0.75531 | 0.12643 | 0.009846 | -0.007421 | -0.006703 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.019364 | -0.03875 | 0.036954 | -0.042641 | -0.00775 | 121.7039 | 121.5873 | 121.57 | 121.5708 | 121.5863 | 121.6585 | 121.5743 | 0.10742 | 0.22115 | 0.087341 | 0.021835 | 0.002449 | 0.078153 | -0.001442 | 0.033449 | 0.10497 | 0.10886 | 0.084892 | 0.088783
6470 | 122.5891 | -121.5958 | 0.75989 | 0.12643 | 0.000689 | -0.016578 | -0.002124 | 0.004219 | 0.076426 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.028906 | -0.003172 | 121.7222 | 121.5965 | 121.5792 | 121.5936 | 121.6 | 121.6722 | 121.588 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.012293 | 0.038027 | 0.11871 | 0.10429 | 0.094048 | 0.079626
6471.7188 | 122.525 | -121.6232 | 0.78278 | 0.12185 | 0.005267 | -0.012 | 0.007033 | 0.013375 | 0.081005 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.019364 | -0.043328 | 0.036954 | -0.038063 | -0.016906 | 121.7451 | 121.6285 | 121.6112 | 121.6303 | 121.6366 | 121.7042 | 121.6246 | 0.112 | 0.21657 | 0.091919 | 0.021835 | -0.002129 | 0.078153 | 0.003136 | 0.024293 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6473.4219 | 122.5021 | -121.6278 | 0.78278 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.085583 | -0.012357 | 0.066223 | 0.18453 | 0.046142 | -0.023943 | -0.043328 | 0.036954 | -0.033484 | -0.012328 | 121.7588 | 121.6331 | 121.6158 | 121.6303 | 121.6412 | 121.7134 | 121.6155 | 0.10742 | 0.22573 | 0.087341 | 0.017256 | -0.002129 | 0.078153 | 0.007715 | 0.028871 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6475.125 | 122.5891 | -121.5866 | 0.77362 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.034171 | 0.02322 | -0.038063 | -0.00775 | 121.7085 | 121.5919 | 121.5746 | 121.5891 | 121.5908 | 121.6676 | 121.5834 | 0.112 | 0.22115 | 0.087341 | 0.017256 | 0.007028 | 0.064419 | 0.003136 | 0.033449 | 0.10497 | 0.10887 | 0.080313 | 0.084205
6476.8281 | 122.6166 | -121.5912 | 0.75989 | 0.13101 | 0.000689 | -0.007421 | -0.006703 | 0.004219 | 0.081005 | -0.012357 | 0.066223 | 0.17995 | 0.055298 | -0.019364 | -0.043328 | 0.027798 | -0.042641 | -0.003172 | 121.7222 | 121.5919 | 121.5838 | 121.5845 | 121.5954 | 121.6722 | 121.5788 | 0.10742 | 0.22115 | 0.096497 | 0.021835 | -0.002129 | 0.068997 | -0.001442 | 0.038027 | 0.10955 | 0.10886 | 0.098626 | 0.097939
6478.5938 | 122.644 | -121.5866 | 0.74158 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.012357 | 0.070802 | 0.17995 | 0.055298 | -0.023943 | -0.047906 | 0.027798 | -0.038063 | -0.003172 | 121.7085 | 121.5919 | 121.5746 | 121.5891 | 121.6 | 121.663 | 121.5743 | 0.112 | 0.22115 | 0.096497 | 0.017256 | -0.006707 | 0.068997 | 0.003136 | 0.038027 | 0.11871 | 0.10887 | 0.1032 | 0.093361
6480.2969 | 122.612 | -121.5546 | 0.75989 | 0.13101 | 0.009846 | -0.007421 | 0.007033 | 0.004219 | 0.081005 | 0.001377 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.02322 | -0.038063 | -0.00775 | 121.6856 | 121.5644 | 121.5471 | 121.5616 | 121.5588 | 121.6356 | 121.5559 | 0.112 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.064419 | 0.003136 | 0.033449 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6482 | 122.5662 | -121.6095 | 0.75531 | 0.12185 | 0.005267 | -0.016578 | 0.002454 | 0.017953 | 0.085583 | -0.003201 | 0.066223 | 0.18911 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.7313 | 121.6148 | 121.5929 | 121.612 | 121.6275 | 121.6951 | 121.6063 | 0.10742 | 0.23031 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6483.75 | 122.5754 | -121.6232 | 0.75989 | 0.13101 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.061645 | 0.17995 | 0.05072 | -0.023943 | -0.03875 | 0.02322 | -0.038063 | -0.00775 | 121.7542 | 121.6285 | 121.6158 | 121.6211 | 121.6366 | 121.6997 | 121.62 | 0.10284 | 0.22115 | 0.091919 | 0.017256 | 0.002449 | 0.064419 | 0.003136 | 0.033449 | 0.10039 | 0.099708 | 0.08947 | 0.088783
6485.4531 | 122.5662 | -121.6049 | 0.75989 | 0.11727 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.028906 | -0.012328 | 121.7222 | 121.6148 | 121.5975 | 121.6074 | 121.6137 | 121.6905 | 121.6017 | 0.112 | 0.22573 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.012293 | 0.028871 | 0.10955 | 0.099708 | 0.08947 | 0.079626
6487.1562 | 122.5296 | -121.6507 | 0.7782 | 0.13101 | 0.009846 | -0.012 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.07538 | 0.17995 | 0.05072 | -0.019364 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.7817 | 121.6605 | 121.6387 | 121.6486 | 121.6595 | 121.7317 | 121.6521 | 0.11658 | 0.22115 | 0.091919 | 0.021835 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.11871 | 0.11344 | 0.094048 | 0.088783
6488.8594 | 122.6395 | -121.6278 | 0.74158 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.7542 | 121.6285 | 121.6112 | 121.6303 | 121.6366 | 121.7088 | 121.6246 | 0.11658 | 0.22115 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6490.625 | 122.6395 | -121.5912 | 0.75073 | 0.12185 | 0.009846 | -0.016578 | 0.011611 | 0.008797 | 0.071848 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.713 | 121.601 | 121.5746 | 121.6028 | 121.6 | 121.663 | 121.5834 | 0.112 | 0.22115 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6492.3281 | 122.5296 | -121.6507 | 0.75531 | 0.13101 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.18911 | 0.055298 | -0.023943 | -0.03875 | 0.02322 | -0.033484 | -0.003172 | 121.7817 | 121.656 | 121.6433 | 121.6486 | 121.6595 | 121.7317 | 121.6429 | 0.112 | 0.23031 | 0.096497 | 0.017256 | 0.002449 | 0.064419 | 0.007715 | 0.038027 | 0.10955 | 0.10429 | 0.094048 | 0.088782
6494.0312 | 122.6578 | -121.6095 | 0.71869 | 0.13559 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.023943 | -0.043328 | 0.027798 | -0.028906 | -0.00775 | 121.7451 | 121.6102 | 121.6021 | 121.612 | 121.6183 | 121.6859 | 121.6017 | 0.112 | 0.22573 | 0.096497 | 0.017256 | -0.002129 | 0.068997 | 0.012293 | 0.033449 | 0.11413 | 0.099708 | 0.098626 | 0.084204
6495.7344 | 122.6303 | -121.6187 | 0.73242 | 0.12185 | -0.00389 | -0.016578 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.070802 | 0.18453 | 0.046142 | -0.028522 | -0.03875 | 0.02322 | -0.033484 | -0.003172 | 121.7405 | 121.6148 | 121.6021 | 121.6165 | 121.632 | 121.6951 | 121.6155 | 0.112 | 0.22573 | 0.087341 | 0.012677 | 0.002449 | 0.064419 | 0.007715 | 0.038027 | 0.10955 | 0.10429 | 0.084892 | 0.079626
6497.4375 | 122.5296 | -121.6461 | 0.76446 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.023943 | -0.03875 | 0.036954 | -0.033484 | -0.00775 | 121.7771 | 121.6514 | 121.6341 | 121.6486 | 121.6549 | 121.7317 | 121.6429 | 0.12116 | 0.22115 | 0.091919 | 0.017256 | 0.002449 | 0.078153 | 0.007715 | 0.033449 | 0.11871 | 0.11344 | 0.08947 | 0.084204
6499.1875 | 122.5479 | -121.6324 | 0.77362 | 0.12185 | 0.014425 | -0.007421 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.079959 | 0.17995 | 0.05072 | -0.033101 | -0.03875 | 0.02322 | -0.038063 | -0.003172 | 121.7542 | 121.6468 | 121.625 | 121.6303 | 121.6458 | 121.718 | 121.6292 | 0.12116 | 0.22115 | 0.091919 | 0.008098 | 0.002449 | 0.064419 | 0.003136 | 0.038027 | 0.11871 | 0.11802 | 0.08947 | 0.088783
6500.8906 | 122.58 | -121.6553 | 0.75531 | 0.12643 | 0.005267 | -0.021157 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.18453 | 0.05072 | -0.028522 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.7817 | 121.6605 | 121.6341 | 121.6577 | 121.6641 | 121.7363 | 121.6566 | 0.112 | 0.22573 | 0.091919 | 0.012677 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.11871 | 0.10429 | 0.098626 | 0.084204
6502.6406 | 122.6715 | -121.6461 | 0.72327 | 0.12643 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.18453 | 0.05072 | -0.028522 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.7725 | 121.656 | 121.6387 | 121.6486 | 121.6549 | 121.7271 | 121.6475 | 0.112 | 0.22573 | 0.091919 | 0.012677 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10955 | 0.10887 | 0.08947 | 0.088783
6504.3281 | 122.6532 | -121.637 | 0.72784 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.18911 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.042641 | -0.00775 | 121.7588 | 121.6422 | 121.6204 | 121.6348 | 121.6458 | 121.718 | 121.6338 | 0.112 | 0.23031 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | -0.001442 | 0.033449 | 0.11413 | 0.11344 | 0.08947 | 0.088783
6506.0469 | 122.6212 | -121.6324 | 0.72327 | 0.13559 | 0.000689 | -0.002842 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.768 | 121.6331 | 121.6295 | 121.6348 | 121.6458 | 121.7088 | 121.6246 | 0.112 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6507.75 | 122.6349 | -121.6095 | 0.72327 | 0.13101 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.076426 | -0.003201 | 0.070802 | 0.17995 | 0.055298 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.012328 | 121.7405 | 121.6102 | 121.5975 | 121.612 | 121.6183 | 121.6859 | 121.6063 | 0.112 | 0.22115 | 0.096497 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.028871 | 0.11413 | 0.10887 | 0.098626 | 0.093361
6509.4688 | 122.6486 | -121.6278 | 0.72784 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.17995 | 0.055298 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.00775 | 121.7542 | 121.6331 | 121.6158 | 121.6257 | 121.6366 | 121.7088 | 121.6292 | 0.112 | 0.22115 | 0.096497 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10887 | 0.094048 | 0.093361
6511.1875 | 122.58 | -121.6507 | 0.75531 | 0.12643 | 0.014425 | -0.007421 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.05072 | -0.023943 | -0.034171 | 0.032376 | -0.038063 | -0.00775 | 121.7771 | 121.6651 | 121.6433 | 121.6531 | 121.6595 | 121.7363 | 121.6475 | 0.11658 | 0.22115 | 0.091919 | 0.017256 | 0.007028 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.11344 | 0.084891 | 0.088783
6512.8906 | 122.5388 | -121.669 | 0.75989 | 0.12185 | 0.005267 | -0.012 | 0.007033 | 0.013375 | 0.081005 | -0.007779 | 0.061645 | 0.18453 | 0.055298 | -0.023943 | -0.03875 | 0.018642 | -0.028906 | -0.00775 | 121.7909 | 121.6743 | 121.657 | 121.676 | 121.6824 | 121.75 | 121.6612 | 0.10284 | 0.22573 | 0.096497 | 0.017256 | 0.002449 | 0.059841 | 0.012293 | 0.033449 | 0.10039 | 0.090551 | 0.094048 | 0.084204
6514.6406 | 122.5296 | -121.6782 | 0.75989 | 0.12185 | 0.009846 | -0.007421 | -0.006703 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.043328 | 0.027798 | -0.042641 | -0.003172 | 121.8 | 121.688 | 121.6707 | 121.6715 | 121.687 | 121.7546 | 121.675 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | -0.002129 | 0.068997 | -0.001442 | 0.038027 | 0.11871 | 0.11802 | 0.094048 | 0.093361
6516.3438 | 122.6395 | -121.6278 | 0.71869 | 0.13101 | 0.014425 | -0.012 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.028522 | -0.052484 | 0.032376 | -0.033484 | -0.00775 | 121.7588 | 121.6422 | 121.6158 | 121.6257 | 121.6366 | 121.7042 | 121.6246 | 0.112 | 0.22573 | 0.091919 | 0.012677 | -0.011285 | 0.073575 | 0.007715 | 0.033449 | 0.12329 | 0.10429 | 0.1032 | 0.084204
6518.0469 | 122.5388 | -121.6644 | 0.78735 | 0.12643 | 0.014425 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.055298 | -0.019364 | -0.047906 | 0.032376 | -0.033484 | -0.003172 | 121.7909 | 121.6789 | 121.657 | 121.6623 | 121.6778 | 121.7454 | 121.6612 | 0.112 | 0.22115 | 0.096497 | 0.021835 | -0.006707 | 0.073575 | 0.007715 | 0.038027 | 0.11871 | 0.10429 | 0.1032 | 0.088782
6519.7656 | 122.6212 | -121.6415 | 0.72784 | 0.13101 | 0.000689 | -0.007421 | 0.002454 | 0.013375 | 0.071848 | -0.007779 | 0.070802 | 0.18453 | 0.041563 | -0.023943 | -0.043328 | 0.032376 | -0.042641 | -0.00775 | 121.7725 | 121.6422 | 121.6341 | 121.644 | 121.6549 | 121.7134 | 121.6338 | 0.112 | 0.22573 | 0.082762 | 0.017256 | -0.002129 | 0.073575 | -0.001442 | 0.033449 | 0.11413 | 0.11344 | 0.084891 | 0.084204
6521.4688 | 122.5891 | -121.6827 | 0.74158 | 0.13101 | 0.005267 | -0.012 | 0.007033 | 0.013375 | 0.090161 | 0.001377 | 0.066223 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.012328 | 121.8137 | 121.688 | 121.6707 | 121.6898 | 121.6961 | 121.7729 | 121.6841 | 0.10742 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.028871 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6523.1719 | 122.5388 | -121.6827 | 0.75989 | 0.12643 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.066223 | 0.17537 | 0.046142 | -0.019364 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.8092 | 121.6926 | 121.6662 | 121.6852 | 121.6915 | 121.7683 | 121.6795 | 0.10742 | 0.21657 | 0.087341 | 0.021835 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.084892 | 0.084205
6524.9062 | 122.5754 | -121.6965 | 0.75531 | 0.12643 | 0.009846 | -0.016578 | 0.007033 | 0.017953 | 0.071848 | 0.001377 | 0.07538 | 0.18453 | 0.05072 | -0.019364 | -0.03875 | 0.02322 | -0.038063 | -0.012328 | 121.8229 | 121.7063 | 121.6799 | 121.7035 | 121.7144 | 121.7683 | 121.6978 | 0.11658 | 0.22573 | 0.091919 | 0.021835 | 0.002449 | 0.064419 | 0.003136 | 0.028871 | 0.11413 | 0.11344 | 0.08947 | 0.088783
6526.6094 | 122.5616 | -121.6827 | 0.75531 | 0.12185 | 0.014425 | -0.007421 | 0.002454 | 0.017953 | 0.081005 | -0.012357 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.03875 | 0.032376 | -0.033484 | -0.003172 | 121.8046 | 121.6972 | 121.6753 | 121.6852 | 121.7007 | 121.7637 | 121.6704 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | 0.002449 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10886 | 0.08947 | 0.084204
6528.3281 | 122.6395 | -121.6278 | 0.71869 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.017953 | 0.081005 | -0.007779 | 0.061645 | 0.18911 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.7542 | 121.6331 | 121.6204 | 121.6257 | 121.6458 | 121.7088 | 121.62 | 0.10284 | 0.23031 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.10955 | 0.099708 | 0.094048 | 0.084205
6530.0781 | 122.5342 | -121.6461 | 0.74616 | 0.12185 | 0.005267 | -0.002842 | -0.002124 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.18453 | 0.055298 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.768 | 121.6514 | 121.6433 | 121.644 | 121.6595 | 121.7271 | 121.6383 | 0.112 | 0.22573 | 0.096497 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.11413 | 0.10429 | 0.098626 | 0.088782
6531.7812 | 122.5662 | -121.7056 | 0.75073 | 0.12643 | -0.00389 | -0.016578 | 0.002454 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.034171 | 0.027798 | -0.033484 | -0.003172 | 121.8321 | 121.7017 | 121.689 | 121.7081 | 121.7098 | 121.7866 | 121.7024 | 0.112 | 0.22115 | 0.091919 | 0.017256 | 0.007028 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.10429 | 0.084891 | 0.084204
6533.5469 | 122.6532 | -121.6507 | 0.70038 | 0.13101 | 0.005267 | -0.007421 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.066223 | 0.17537 | 0.05072 | -0.010206 | -0.03875 | 0.027798 | -0.028906 | -0.003172 | 121.7817 | 121.656 | 121.6433 | 121.6531 | 121.6595 | 121.7225 | 121.6475 | 0.10742 | 0.21657 | 0.091919 | 0.030993 | 0.002449 | 0.068997 | 0.012293 | 0.038027 | 0.10497 | 0.095129 | 0.08947 | 0.079626
6535.2969 | 122.6761 | -121.6278 | 0.70953 | 0.12185 | 0.000689 | -0.007421 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.18911 | 0.046142 | -0.023943 | -0.043328 | 0.036954 | -0.038063 | -0.012328 | 121.7497 | 121.6285 | 121.6204 | 121.6348 | 121.6366 | 121.7088 | 121.6246 | 0.112 | 0.23031 | 0.087341 | 0.017256 | -0.002129 | 0.078153 | 0.003136 | 0.028871 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6537.0312 | 122.6669 | -121.6507 | 0.69122 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.013375 | 0.081005 | -0.007779 | 0.061645 | 0.17995 | 0.041563 | -0.019364 | -0.043328 | 0.032376 | -0.038063 | -0.012328 | 121.7771 | 121.656 | 121.6341 | 121.6531 | 121.6641 | 121.7317 | 121.6429 | 0.10284 | 0.22115 | 0.082762 | 0.021835 | -0.002129 | 0.073575 | 0.003136 | 0.028871 | 0.10497 | 0.099708 | 0.084891 | 0.079626
6538.7344 | 122.5845 | -121.6919 | 0.75531 | 0.13101 | 0.014425 | -0.002842 | 0.002454 | 0.008797 | 0.085583 | -0.003201 | 0.066223 | 0.18453 | 0.055298 | -0.028522 | -0.052484 | 0.032376 | -0.033484 | -0.003172 | 121.8229 | 121.7063 | 121.6891 | 121.6943 | 121.7007 | 121.7775 | 121.6887 | 0.10742 | 0.22573 | 0.096497 | 0.012677 | -0.011285 | 0.073575 | 0.007715 | 0.038027 | 0.11871 | 0.099707 | 0.10778 | 0.088782
6540.4688 | 122.6578 | -121.6507 | 0.72784 | 0.13101 | 0.005267 | -0.007421 | 0.007033 | 0.013375 | 0.085583 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.7817 | 121.656 | 121.6433 | 121.6577 | 121.6641 | 121.7363 | 121.6475 | 0.112 | 0.22573 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.11413 | 0.10429 | 0.094048 | 0.084204
6542.1719 | 122.7081 | -121.6415 | 0.73242 | 0.11727 | 0.000689 | -0.012 | 0.002454 | 0.004219 | 0.085583 | -0.012357 | 0.070802 | 0.18453 | 0.041563 | -0.019364 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.7588 | 121.6422 | 121.6295 | 121.644 | 121.6458 | 121.7271 | 121.6292 | 0.112 | 0.22573 | 0.082762 | 0.021835 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.084891 | 0.075047
6543.875 | 122.6715 | -121.6507 | 0.70038 | 0.12643 | 0.005267 | -0.012 | 0.007033 | 0.008797 | 0.081005 | -0.007779 | 0.061645 | 0.18453 | 0.046142 | -0.023943 | -0.043328 | 0.036954 | -0.038063 | -0.016906 | 121.7771 | 121.656 | 121.6387 | 121.6577 | 121.6595 | 121.7317 | 121.6429 | 0.10284 | 0.22573 | 0.087341 | 0.017256 | -0.002129 | 0.078153 | 0.003136 | 0.024293 | 0.10497 | 0.099708 | 0.08947 | 0.084205
6545.5781 | 122.5525 | -121.7102 | 0.74158 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.090161 | -0.003201 | 0.070802 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.02322 | -0.038063 | -0.003172 | 121.8366 | 121.7155 | 121.6982 | 121.7127 | 121.719 | 121.8004 | 121.707 | 0.112 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.064419 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.08947 | 0.084205
6547.2812 | 122.5616 | -121.6965 | 0.72784 | 0.12643 | 0.005267 | -0.012 | -0.006703 | 0.013375 | 0.081005 | 0.001377 | 0.066223 | 0.17537 | 0.055298 | -0.028522 | -0.047906 | 0.032376 | -0.028906 | -0.00775 | 121.8229 | 121.7017 | 121.6845 | 121.6898 | 121.7098 | 121.7775 | 121.6978 | 0.10742 | 0.21657 | 0.096497 | 0.012677 | -0.006707 | 0.073575 | 0.012293 | 0.033449 | 0.11413 | 0.095129 | 0.1032 | 0.084204
6548.9844 | 122.58 | -121.701 | 0.72327 | 0.12185 | 0.014425 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.066223 | 0.17537 | 0.046142 | -0.028522 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.8229 | 121.7155 | 121.6936 | 121.6989 | 121.7098 | 121.7821 | 121.7024 | 0.10742 | 0.21657 | 0.087341 | 0.012677 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6550.7188 | 122.6669 | -121.6507 | 0.70953 | 0.13101 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.18453 | 0.046142 | -0.023943 | -0.043328 | 0.032376 | -0.042641 | -0.00775 | 121.7817 | 121.6605 | 121.6387 | 121.6531 | 121.6595 | 121.7317 | 121.6521 | 0.112 | 0.22573 | 0.087341 | 0.017256 | -0.002129 | 0.073575 | -0.001442 | 0.033449 | 0.11413 | 0.11344 | 0.08947 | 0.088783
6552.4062 | 122.5937 | -121.6873 | 0.70496 | 0.12185 | 0.005267 | -0.002842 | -0.002124 | 0.008797 | 0.085583 | -0.003201 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.043328 | 0.02322 | -0.042641 | -0.00775 | 121.8092 | 121.6926 | 121.6845 | 121.6852 | 121.6961 | 121.7729 | 121.6841 | 0.112 | 0.21657 | 0.091919 | 0.017256 | -0.002129 | 0.064419 | -0.001442 | 0.033449 | 0.11413 | 0.11344 | 0.094048 | 0.093361
6554.1094 | 122.5662 | -121.7239 | 0.72327 | 0.12185 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.085583 | -0.007779 | 0.07538 | 0.17995 | 0.05072 | -0.014785 | -0.03875 | 0.032376 | -0.033484 | -0.003172 | 121.8458 | 121.7292 | 121.7074 | 121.7218 | 121.7327 | 121.8095 | 121.7162 | 0.11658 | 0.22115 | 0.091919 | 0.026414 | 0.002449 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10886 | 0.08947 | 0.084204
6555.8125 | 122.6212 | -121.6782 | 0.71869 | 0.11727 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.07538 | 0.17537 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.7954 | 121.6834 | 121.6662 | 121.6806 | 121.687 | 121.7592 | 121.675 | 0.11658 | 0.21657 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.11871 | 0.11344 | 0.08947 | 0.084205
6557.5156 | 122.6852 | -121.6644 | 0.71869 | 0.12643 | 0.009846 | -0.012 | -0.006703 | 0.004219 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.032376 | -0.038063 | -0.012328 | 121.7909 | 121.6743 | 121.6524 | 121.6577 | 121.6686 | 121.7454 | 121.6612 | 0.10742 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.073575 | 0.003136 | 0.028871 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6559.2344 | 122.6807 | -121.669 | 0.68665 | 0.13101 | 0.009846 | -0.012 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.07538 | 0.18453 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | -0.016906 | 121.8 | 121.6789 | 121.657 | 121.6715 | 121.6778 | 121.75 | 121.6704 | 0.11658 | 0.22573 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.024293 | 0.11871 | 0.10886 | 0.08947 | 0.079626
6560.9375 | 122.6578 | -121.6873 | 0.71869 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.17537 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.8137 | 121.688 | 121.6799 | 121.6898 | 121.6961 | 121.7683 | 121.6795 | 0.11658 | 0.21657 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6562.6406 | 122.6852 | -121.637 | 0.70496 | 0.12185 | 0.005267 | -0.012 | -0.002124 | -0.000359 | 0.076426 | -0.007779 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.047906 | 0.032376 | -0.033484 | -0.003172 | 121.7588 | 121.6422 | 121.625 | 121.6348 | 121.6366 | 121.7134 | 121.6292 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.006707 | 0.073575 | 0.007715 | 0.038027 | 0.11871 | 0.10429 | 0.098626 | 0.084204
6564.3281 | 122.6761 | -121.6736 | 0.70038 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.012357 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.018642 | -0.042641 | -0.003172 | 121.7954 | 121.6789 | 121.6616 | 121.676 | 121.6824 | 121.7546 | 121.6612 | 0.112 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.059841 | -0.001442 | 0.038027 | 0.11871 | 0.11344 | 0.094048 | 0.088783
6566.0938 | 122.6669 | -121.6782 | 0.70038 | 0.12643 | 0.000689 | -0.002842 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.066223 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.032376 | -0.033484 | -0.00775 | 121.8046 | 121.6789 | 121.6753 | 121.6806 | 121.687 | 121.7546 | 121.6704 | 0.10742 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.073575 | 0.007715 | 0.033449 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6567.7969 | 122.6807 | -121.6736 | 0.70496 | 0.12643 | 0.005267 | -0.021157 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.043328 | 0.027798 | -0.033484 | -0.012328 | 121.8 | 121.6789 | 121.6524 | 121.676 | 121.687 | 121.7546 | 121.6704 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.002129 | 0.068997 | 0.007715 | 0.028871 | 0.11413 | 0.10429 | 0.094048 | 0.084204
6569.5156 | 122.6761 | -121.6782 | 0.68207 | 0.12643 | 0.000689 | -0.007421 | -0.002124 | 0.017953 | 0.076426 | -0.003201 | 0.061645 | 0.17995 | 0.055298 | -0.033101 | -0.047906 | 0.032376 | -0.038063 | -0.00775 | 121.8046 | 121.6789 | 121.6707 | 121.676 | 121.6961 | 121.7546 | 121.675 | 0.10284 | 0.22115 | 0.096497 | 0.008098 | -0.006707 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.099708 | 0.1032 | 0.093361
6571.2188 | 122.6486 | -121.6873 | 0.70953 | 0.13101 | 0.005267 | -0.007421 | 0.007033 | 0.017953 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.052484 | 0.027798 | -0.033484 | -0.003172 | 121.8183 | 121.6926 | 121.6799 | 121.6944 | 121.7053 | 121.7683 | 121.6841 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.011285 | 0.068997 | 0.007715 | 0.038027 | 0.12329 | 0.10429 | 0.1032 | 0.084204
6572.9375 | 122.6944 | -121.6553 | 0.70496 | 0.12185 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.066223 | 0.17537 | 0.05072 | -0.033101 | -0.03875 | 0.027798 | -0.033484 | -0.003172 | 121.7771 | 121.6651 | 121.6479 | 121.6577 | 121.6641 | 121.7271 | 121.6521 | 0.10742 | 0.21657 | 0.091919 | 0.008098 | 0.002449 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.099707 | 0.08947 | 0.084204
6574.6719 | 122.5525 | -121.7102 | 0.73242 | 0.12643 | 0.009846 | -0.007421 | 0.011611 | 0.013375 | 0.076426 | -0.012357 | 0.066223 | 0.17995 | 0.046142 | -0.028522 | -0.03875 | 0.032376 | -0.028906 | -0.003172 | 121.8366 | 121.7201 | 121.7028 | 121.7218 | 121.7236 | 121.7866 | 121.6978 | 0.10742 | 0.22115 | 0.087341 | 0.012677 | 0.002449 | 0.073575 | 0.012293 | 0.038027 | 0.10497 | 0.095129 | 0.084892 | 0.075048
6576.375 | 122.5891 | -121.7194 | 0.72784 | 0.13101 | 0.005267 | -0.016578 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.07538 | 0.18453 | 0.055298 | -0.019364 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.8504 | 121.7246 | 121.7028 | 121.7218 | 121.7327 | 121.8004 | 121.7162 | 0.11658 | 0.22573 | 0.096497 | 0.021835 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.11871 | 0.11344 | 0.098626 | 0.093361
6578.0781 | 122.5571 | -121.7606 | 0.73242 | 0.12643 | 0.000689 | -0.016578 | -0.002124 | 0.017953 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.003172 | 121.887 | 121.7612 | 121.744 | 121.7584 | 121.7785 | 121.8416 | 121.7574 | 0.112 | 0.21657 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6579.7812 | 122.6303 | -121.7102 | 0.68665 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.041563 | -0.033101 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.8366 | 121.7155 | 121.6982 | 121.7081 | 121.719 | 121.7912 | 121.707 | 0.10742 | 0.22115 | 0.082762 | 0.008098 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.10955 | 0.10429 | 0.084891 | 0.079626
6581.4844 | 122.5845 | -121.7194 | 0.72784 | 0.12643 | 0.000689 | -0.012 | 0.011611 | 0.013375 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.059877 | -0.019364 | -0.043328 | 0.036954 | -0.033484 | 0.001406 | 121.8458 | 121.72 | 121.7074 | 121.731 | 121.7327 | 121.8004 | 121.7162 | 0.112 | 0.22115 | 0.10108 | 0.021835 | -0.002129 | 0.078153 | 0.007715 | 0.042605 | 0.11413 | 0.10429 | 0.1032 | 0.093361
6583.1875 | 122.6715 | -121.6644 | 0.69122 | 0.12643 | 0.009846 | -0.012 | -0.002124 | 0.013375 | 0.085583 | -0.003201 | 0.07538 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.00775 | 121.7909 | 121.6743 | 121.6524 | 121.6623 | 121.6778 | 121.75 | 121.6612 | 0.11658 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.033449 | 0.11413 | 0.11344 | 0.084892 | 0.084205
6584.8906 | 122.5525 | -121.7422 | 0.72327 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.013375 | 0.090161 | 0.001377 | 0.066223 | 0.17537 | 0.05072 | -0.033101 | -0.043328 | 0.027798 | -0.038063 | 0.001406 | 121.8641 | 121.7475 | 121.7348 | 121.7447 | 121.7556 | 121.8324 | 121.7436 | 0.10742 | 0.21657 | 0.091919 | 0.008098 | -0.002129 | 0.068997 | 0.003136 | 0.042605 | 0.10955 | 0.10429 | 0.094048 | 0.088783
6586.625 | 122.6028 | -121.7056 | 0.73242 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.013375 | 0.081005 | -0.003201 | 0.07538 | 0.17537 | 0.055298 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.003172 | 121.8321 | 121.7155 | 121.6982 | 121.7035 | 121.719 | 121.7866 | 121.7024 | 0.11658 | 0.21657 | 0.096497 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.11344 | 0.094048 | 0.093361
6588.3281 | 122.7036 | -121.701 | 0.66834 | 0.12185 | 0.005267 | -0.016578 | 0.002454 | 0.017953 | 0.076426 | -0.003201 | 0.066223 | 0.17079 | 0.055298 | -0.028522 | -0.03875 | 0.02322 | -0.038063 | -0.003172 | 121.8229 | 121.7063 | 121.6845 | 121.7035 | 121.719 | 121.7775 | 121.6978 | 0.10742 | 0.21199 | 0.096497 | 0.012677 | 0.002449 | 0.064419 | 0.003136 | 0.038027 | 0.10497 | 0.10429 | 0.094048 | 0.093361
6590.0312 | 122.6532 | -121.6782 | 0.69122 | 0.12185 | 0.005267 | -0.007421 | 0.002454 | 0.013375 | 0.085583 | -0.007779 | 0.070802 | 0.18453 | 0.046142 | -0.028522 | -0.043328 | 0.027798 | -0.033484 | 0.001406 | 121.8 | 121.6834 | 121.6707 | 121.6806 | 121.6915 | 121.7637 | 121.6704 | 0.112 | 0.22573 | 0.087341 | 0.012677 | -0.002129 | 0.068997 | 0.007715 | 0.042605 | 0.11413 | 0.10429 | 0.08947 | 0.079626
6591.7344 | 122.6898 | -121.6782 | 0.6958 | 0.12643 | 0.000689 | -0.016578 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.034171 | 0.027798 | -0.038063 | -0.00775 | 121.8046 | 121.6789 | 121.6616 | 121.6806 | 121.687 | 121.75 | 121.675 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | 0.007028 | 0.068997 | 0.003136 | 0.033449 | 0.10039 | 0.10429 | 0.080313 | 0.084205
6593.4531 | 122.6715 | -121.6965 | 0.70038 | 0.12185 | 0.005267 | -0.007421 | 0.007033 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.17995 | 0.041563 | -0.033101 | -0.047906 | 0.032376 | -0.042641 | -0.00775 | 121.8183 | 121.7017 | 121.6891 | 121.7035 | 121.7007 | 121.7775 | 121.6933 | 0.11658 | 0.22115 | 0.082762 | 0.008098 | -0.006707 | 0.073575 | -0.001442 | 0.033449 | 0.12329 | 0.11802 | 0.089469 | 0.084204
6595.1562 | 122.6852 | -121.701 | 0.68665 | 0.12643 | 0.000689 | -0.012 | 0.011611 | 0.004219 | 0.071848 | 0.001377 | 0.066223 | 0.18453 | 0.046142 | -0.028522 | -0.047906 | 0.032376 | -0.033484 | -0.003172 | 121.8275 | 121.7017 | 121.689 | 121.7127 | 121.7053 | 121.7729 | 121.7024 | 0.10742 | 0.22573 | 0.087341 | 0.012677 | -0.006707 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.099707 | 0.094048 | 0.079626
6596.8594 | 122.6898 | -121.6827 | 0.6958 | 0.12643 | 0.005267 | -0.016578 | -0.002124 | 0.013375 | 0.076426 | -0.003201 | 0.061645 | 0.17537 | 0.055298 | -0.023943 | -0.043328 | 0.014064 | -0.038063 | -0.003172 | 121.8092 | 121.688 | 121.6662 | 121.6806 | 121.6961 | 121.7592 | 121.6795 | 0.10284 | 0.21657 | 0.096497 | 0.017256 | -0.002129 | 0.055263 | 0.003136 | 0.038027 | 0.10497 | 0.099708 | 0.098626 | 0.093361
6598.6094 | 122.5845 | -121.7377 | 0.73242 | 0.12643 | 0.009846 | -0.002842 | -0.006703 | 0.008797 | 0.081005 | 0.001377 | 0.066223 | 0.17995 | 0.041563 | -0.019364 | -0.043328 | 0.02322 | -0.04722 | -0.012328 | 121.8641 | 121.7475 | 121.7348 | 121.731 | 121.7465 | 121.8187 | 121.739 | 0.10742 | 0.22115 | 0.082762 | 0.021835 | -0.002129 | 0.064419 | -0.006021 | 0.028871 | 0.10955 | 0.11344 | 0.084891 | 0.088783
6600.3125 | 122.7036 | -121.6919 | 0.67291 | 0.12643 | 0.005267 | -0.012 | -0.002124 | 0.013375 | 0.076426 | -0.007779 | 0.07538 | 0.17537 | 0.05072 | -0.019364 | -0.029593 | 0.02322 | -0.033484 | -0.012328 | 121.8183 | 121.6972 | 121.6799 | 121.6898 | 121.7053 | 121.7683 | 121.6841 | 0.11658 | 0.21657 | 0.091919 | 0.021835 | 0.011606 | 0.064419 | 0.007715 | 0.028871 | 0.10497 | 0.10886 | 0.080313 | 0.084204
6602.0156 | 122.6898 | -121.6553 | 0.67291 | 0.13101 | 0.005267 | -0.002842 | -0.002124 | 0.013375 | 0.085583 | 0.001377 | 0.066223 | 0.17995 | 0.046142 | -0.03768 | -0.03875 | 0.032376 | -0.033484 | -0.003172 | 121.7863 | 121.6605 | 121.6524 | 121.6531 | 121.6686 | 121.7409 | 121.6566 | 0.10742 | 0.22115 | 0.087341 | 0.003519 | 0.002449 | 0.073575 | 0.007715 | 0.038027 | 0.10497 | 0.099707 | 0.084892 | 0.079626
6603.7188 | 122.5937 | -121.7422 | 0.72327 | 0.14017 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.05072 | -0.019364 | -0.043328 | 0.02322 | -0.033484 | -0.00775 | 121.8824 | 121.7475 | 121.7348 | 121.7401 | 121.751 | 121.8233 | 121.739 | 0.112 | 0.22115 | 0.091919 | 0.021835 | -0.002129 | 0.064419 | 0.007715 | 0.033449 | 0.11413 | 0.10429 | 0.094048 | 0.084204
6605.4062 | 122.6532 | -121.6873 | 0.69122 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.013375 | 0.076426 | -0.003201 | 0.07538 | 0.18453 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.8137 | 121.6926 | 121.6707 | 121.6898 | 121.7007 | 121.7637 | 121.6841 | 0.11658 | 0.22573 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.12329 | 0.10886 | 0.094048 | 0.079626
6607.1406 | 122.6166 | -121.7377 | 0.71869 | 0.12643 | 0.014425 | -0.002842 | 0.007033 | 0.017953 | 0.085583 | -0.007779 | 0.070802 | 0.17537 | 0.041563 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.00775 | 121.8641 | 121.7521 | 121.7348 | 121.7447 | 121.7556 | 121.8233 | 121.7299 | 0.112 | 0.21657 | 0.082762 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10887 | 0.080313 | 0.079626
6608.8438 | 122.5662 | -121.7377 | 0.73242 | 0.13101 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.076426 | 0.001377 | 0.070802 | 0.17995 | 0.046142 | -0.014785 | -0.047906 | 0.032376 | -0.028906 | -0.012328 | 121.8687 | 121.7429 | 121.7211 | 121.7401 | 121.7465 | 121.8141 | 121.739 | 0.112 | 0.22115 | 0.087341 | 0.026414 | -0.006707 | 0.073575 | 0.012293 | 0.028871 | 0.11871 | 0.099708 | 0.094048 | 0.075048
6610.6094 | 122.5983 | -121.7239 | 0.70496 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.076426 | 0.001377 | 0.066223 | 0.18453 | 0.05072 | -0.028522 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.8549 | 121.7292 | 121.7119 | 121.7264 | 121.7327 | 121.8004 | 121.7253 | 0.10742 | 0.22573 | 0.091919 | 0.012677 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10429 | 0.094048 | 0.088783
6612.3281 | 122.6898 | -121.6873 | 0.69122 | 0.12185 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.066223 | 0.18453 | 0.05072 | -0.019364 | -0.034171 | 0.02322 | -0.04722 | -0.00775 | 121.8092 | 121.6926 | 121.6753 | 121.6898 | 121.7007 | 121.7683 | 121.6841 | 0.10742 | 0.22573 | 0.091919 | 0.021835 | 0.007028 | 0.064419 | -0.006021 | 0.033449 | 0.10039 | 0.11344 | 0.084891 | 0.09794
6614.0781 | 122.5937 | -121.7422 | 0.72327 | 0.12643 | 0.005267 | -0.002842 | -0.002124 | 0.008797 | 0.076426 | 0.001377 | 0.066223 | 0.17995 | 0.046142 | -0.019364 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.8687 | 121.7475 | 121.7394 | 121.7401 | 121.751 | 121.8187 | 121.7436 | 0.10742 | 0.22115 | 0.087341 | 0.021835 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6615.7812 | 122.6944 | -121.6919 | 0.70038 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.076426 | -0.007779 | 0.070802 | 0.18453 | 0.046142 | -0.019364 | -0.043328 | 0.036954 | -0.042641 | -0.003172 | 121.8183 | 121.6972 | 121.6799 | 121.6943 | 121.7053 | 121.7683 | 121.6841 | 0.112 | 0.22573 | 0.087341 | 0.021835 | -0.002129 | 0.078153 | -0.001442 | 0.038027 | 0.11413 | 0.11344 | 0.08947 | 0.088783
6617.5156 | 122.6624 | -121.7148 | 0.70496 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.079959 | 0.17537 | 0.05072 | -0.023943 | -0.047906 | 0.027798 | -0.033484 | -0.00775 | 121.8412 | 121.7155 | 121.7074 | 121.7172 | 121.7236 | 121.7958 | 121.707 | 0.12116 | 0.21657 | 0.091919 | 0.017256 | -0.006707 | 0.068997 | 0.007715 | 0.033449 | 0.12787 | 0.11344 | 0.098626 | 0.084204
6619.2188 | 122.6349 | -121.7239 | 0.72784 | 0.12643 | 0.014425 | -0.021157 | 0.007033 | 0.013375 | 0.081005 | -0.007779 | 0.061645 | 0.17995 | 0.05072 | -0.028522 | -0.047906 | 0.027798 | -0.038063 | 0.001406 | 121.8504 | 121.7384 | 121.7028 | 121.731 | 121.7373 | 121.8049 | 121.7162 | 0.10284 | 0.22115 | 0.091919 | 0.012677 | -0.006707 | 0.068997 | 0.003136 | 0.042605 | 0.10955 | 0.099708 | 0.098626 | 0.088783
6620.9219 | 122.5983 | -121.7422 | 0.73242 | 0.12643 | 0.005267 | -0.007421 | 0.011611 | 0.013375 | 0.071848 | 0.001377 | 0.070802 | 0.17537 | 0.046142 | -0.019364 | -0.03875 | 0.027798 | -0.038063 | -0.003172 | 121.8687 | 121.7475 | 121.7348 | 121.7539 | 121.7556 | 121.8141 | 121.7436 | 0.112 | 0.21657 | 0.087341 | 0.021835 | 0.002449 | 0.068997 | 0.003136 | 0.038027 | 0.10955 | 0.10887 | 0.084892 | 0.084205
6622.6562 | 122.6166 | -121.7102 | 0.73242 | 0.12643 | 0.009846 | -0.012 | 0.007033 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.055298 | -0.028522 | -0.03875 | 0.027798 | -0.028906 | -0.00775 | 121.8366 | 121.7201 | 121.6982 | 121.7172 | 121.7144 | 121.7912 | 121.707 | 0.112 | 0.22115 | 0.096497 | 0.012677 | 0.002449 | 0.068997 | 0.012293 | 0.033449 | 0.10955 | 0.099708 | 0.094048 | 0.084204
6624.3594 | 122.5845 | -121.7468 | 0.73242 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.017953 | 0.081005 | 0.001377 | 0.066223 | 0.17995 | 0.05072 | -0.023943 | -0.047906 | 0.02322 | -0.033484 | -0.00775 | 121.8733 | 121.7567 | 121.7394 | 121.7447 | 121.7648 | 121.8278 | 121.7482 | 0.10742 | 0.22115 | 0.091919 | 0.017256 | -0.006707 | 0.064419 | 0.007715 | 0.033449 | 0.11413 | 0.099707 | 0.098626 | 0.084204
6626.0625 | 122.6852 | -121.7056 | 0.70496 | 0.11727 | 0.000689 | -0.007421 | 0.007033 | 0.013375 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.00775 | 121.8229 | 121.7063 | 121.6982 | 121.7127 | 121.719 | 121.7866 | 121.6978 | 0.112 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10887 | 0.084892 | 0.084205
6627.7812 | 122.699 | -121.6919 | 0.69122 | 0.12643 | 0.009846 | -0.021157 | -0.002124 | 0.013375 | 0.081005 | 0.001377 | 0.070802 | 0.17995 | 0.055298 | -0.023943 | -0.043328 | 0.02322 | -0.033484 | -0.012328 | 121.8183 | 121.7017 | 121.6707 | 121.6898 | 121.7053 | 121.7729 | 121.6933 | 0.112 | 0.22115 | 0.096497 | 0.017256 | -0.002129 | 0.064419 | 0.007715 | 0.028871 | 0.11413 | 0.10429 | 0.098626 | 0.088782
6629.5469 | 122.5937 | -121.7239 | 0.72784 | 0.12643 | 0.000689 | -0.007421 | -0.011281 | 0.013375 | 0.081005 | -0.012357 | 0.07538 | 0.17995 | 0.041563 | -0.028522 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.8504 | 121.7246 | 121.7165 | 121.7127 | 121.7373 | 121.8049 | 121.7116 | 0.11658 | 0.22115 | 0.082762 | 0.012677 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.11871 | 0.10886 | 0.084891 | 0.075047
6631.2656 | 122.699 | -121.6782 | 0.70953 | 0.12643 | 0.000689 | -0.012 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.032376 | -0.033484 | -0.012328 | 121.8046 | 121.6789 | 121.6662 | 121.6806 | 121.687 | 121.7592 | 121.6704 | 0.112 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.073575 | 0.007715 | 0.028871 | 0.10955 | 0.10429 | 0.084892 | 0.079626
6633.0312 | 122.5891 | -121.7285 | 0.72327 | 0.13101 | 0.000689 | -0.012 | 0.007033 | 0.008797 | 0.085583 | 0.001377 | 0.070802 | 0.17995 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.012328 | 121.8595 | 121.7292 | 121.7165 | 121.7355 | 121.7373 | 121.8141 | 121.7299 | 0.112 | 0.22115 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.028871 | 0.11871 | 0.10887 | 0.094048 | 0.084205
6634.7344 | 122.5845 | -121.7468 | 0.72784 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.013375 | 0.085583 | -0.007779 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.052484 | 0.032376 | -0.038063 | -0.003172 | 121.8733 | 121.7521 | 121.7394 | 121.7447 | 121.7602 | 121.8324 | 121.739 | 0.112 | 0.21657 | 0.091919 | 0.017256 | -0.011285 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.10887 | 0.1032 | 0.088783
6636.4531 | 122.5891 | -121.7285 | 0.73242 | 0.12185 | 0.000689 | -0.016578 | 0.011611 | 0.004219 | 0.090161 | 0.001377 | 0.07538 | 0.17537 | 0.05072 | -0.033101 | -0.043328 | 0.027798 | -0.042641 | -0.00775 | 121.8504 | 121.7292 | 121.7119 | 121.7401 | 121.7327 | 121.8187 | 121.7299 | 0.11658 | 0.21657 | 0.091919 | 0.008098 | -0.002129 | 0.068997 | -0.001442 | 0.033449 | 0.11871 | 0.11802 | 0.094048 | 0.093361
6638.1562 | 122.7173 | -121.6919 | 0.70038 | 0.12185 | 0.009846 | -0.016578 | 0.007033 | 0.008797 | 0.081005 | -0.007779 | 0.061645 | 0.17995 | 0.041563 | -0.023943 | -0.03875 | 0.032376 | -0.033484 | -0.00775 | 121.8137 | 121.7017 | 121.6753 | 121.6989 | 121.7007 | 121.7729 | 121.6841 | 0.10284 | 0.22115 | 0.082762 | 0.017256 | 0.002449 | 0.073575 | 0.007715 | 0.033449 | 0.10039 | 0.095129 | 0.080313 | 0.075047
6639.8594 | 122.731 | -121.7102 | 0.68665 | 0.12643 | 0.005267 | -0.012 | 0.007033 | 0.013375 | 0.085583 | 0.001377 | 0.070802 | 0.17537 | 0.041563 | -0.023943 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.8366 | 121.7155 | 121.6982 | 121.7172 | 121.7236 | 121.7958 | 121.7116 | 0.112 | 0.21657 | 0.082762 | 0.017256 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.11871 | 0.10429 | 0.089469 | 0.075047
6641.6094 | 122.5845 | -121.7239 | 0.74158 | 0.13101 | 0.005267 | -0.016578 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.03875 | 0.027798 | -0.042641 | -0.012328 | 121.8549 | 121.7292 | 121.7074 | 121.7218 | 121.7282 | 121.8049 | 121.7207 | 0.112 | 0.21657 | 0.091919 | 0.012677 | 0.002449 | 0.068997 | -0.001442 | 0.028871 | 0.10955 | 0.11344 | 0.08947 | 0.093361
6643.3125 | 122.6944 | -121.7102 | 0.69122 | 0.13101 | 0.005267 | -0.012 | 0.002454 | 0.008797 | 0.071848 | -0.003201 | 0.066223 | 0.18911 | 0.05072 | -0.028522 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.8412 | 121.7155 | 121.6982 | 121.7127 | 121.719 | 121.7821 | 121.707 | 0.10742 | 0.23031 | 0.091919 | 0.012677 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.11413 | 0.099707 | 0.098626 | 0.084204
6645.0938 | 122.58 | -121.7468 | 0.74616 | 0.12643 | 0.005267 | -0.012 | 0.002454 | 0.013375 | 0.085583 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.03875 | 0.02322 | -0.038063 | -0.00775 | 121.8733 | 121.7521 | 121.7348 | 121.7493 | 121.7602 | 121.8324 | 121.7436 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | 0.002449 | 0.064419 | 0.003136 | 0.033449 | 0.10497 | 0.10429 | 0.084892 | 0.084205
6646.7969 | 122.6715 | -121.7194 | 0.68207 | 0.12185 | 0.000689 | -0.007421 | 0.007033 | 0.008797 | 0.076426 | -0.003201 | 0.066223 | 0.18453 | 0.046142 | -0.028522 | -0.03875 | 0.027798 | -0.033484 | -0.00775 | 121.8412 | 121.72 | 121.7119 | 121.7264 | 121.7282 | 121.7958 | 121.7162 | 0.10742 | 0.22573 | 0.087341 | 0.012677 | 0.002449 | 0.068997 | 0.007715 | 0.033449 | 0.10497 | 0.099707 | 0.084892 | 0.079626
6648.5156 | 122.6303 | -121.7285 | 0.72784 | 0.13101 | 0.005267 | -0.016578 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.17537 | 0.055298 | -0.023943 | -0.043328 | 0.027798 | -0.04722 | -0.003172 | 121.8595 | 121.7338 | 121.7119 | 121.7264 | 121.7373 | 121.8049 | 121.7253 | 0.11658 | 0.21657 | 0.096497 | 0.017256 | -0.002129 | 0.068997 | -0.006021 | 0.038027 | 0.11871 | 0.1226 | 0.098626 | 0.10252
6650.2188 | 122.7036 | -121.7239 | 0.70496 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.085583 | 0.001377 | 0.07538 | 0.18453 | 0.05072 | -0.023943 | -0.047906 | 0.032376 | -0.038063 | -0.003172 | 121.8504 | 121.7338 | 121.7165 | 121.7218 | 121.7327 | 121.8095 | 121.7253 | 0.11658 | 0.22573 | 0.091919 | 0.017256 | -0.006707 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.11344 | 0.098626 | 0.088783
6651.9375 | 122.7219 | -121.701 | 0.66834 | 0.12185 | 0.000689 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.17995 | 0.055298 | -0.023943 | -0.03875 | 0.02322 | -0.038063 | -0.012328 | 121.8229 | 121.7017 | 121.6936 | 121.6989 | 121.7098 | 121.7775 | 121.6978 | 0.11658 | 0.22115 | 0.096497 | 0.017256 | 0.002449 | 0.064419 | 0.003136 | 0.028871 | 0.11413 | 0.11344 | 0.094048 | 0.093361
6653.7031 | 122.7173 | -121.7331 | 0.68207 | 0.12643 | 0.000689 | -0.007421 | 0.002454 | 0.013375 | 0.081005 | 0.005955 | 0.066223 | 0.17537 | 0.05072 | -0.023943 | -0.03875 | 0.036954 | -0.042641 | -0.003172 | 121.8595 | 121.7338 | 121.7257 | 121.7355 | 121.7465 | 121.8141 | 121.739 | 0.10742 | 0.21657 | 0.091919 | 0.017256 | 0.002449 | 0.078153 | -0.001442 | 0.038027 | 0.10497 | 0.10886 | 0.08947 | 0.093361
6655.4062 | 122.6852 | -121.7102 | 0.70038 | 0.12185 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.066223 | 0.17995 | 0.05072 | -0.033101 | -0.043328 | 0.027798 | -0.033484 | 0.001406 | 121.8321 | 121.7155 | 121.6936 | 121.7127 | 121.719 | 121.7912 | 121.7116 | 0.10742 | 0.22115 | 0.091919 | 0.008098 | -0.002129 | 0.068997 | 0.007715 | 0.042605 | 0.10955 | 0.099707 | 0.094048 | 0.084204
6657.1094 | 122.6898 | -121.7285 | 0.70953 | 0.12643 | 0.000689 | -0.016578 | -0.002124 | 0.008797 | 0.071848 | 0.001377 | 0.066223 | 0.18453 | 0.046142 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.00775 | 121.8549 | 121.7292 | 121.7119 | 121.7264 | 121.7373 | 121.8004 | 121.7299 | 0.10742 | 0.22573 | 0.087341 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.033449 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6658.8125 | 122.6212 | -121.7422 | 0.71411 | 0.12643 | 0.009846 | -0.007421 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.066223 | 0.17537 | 0.041563 | -0.023943 | -0.047906 | 0.02322 | -0.033484 | -0.00775 | 121.8687 | 121.7521 | 121.7348 | 121.7447 | 121.7556 | 121.8233 | 121.7436 | 0.10742 | 0.21657 | 0.082762 | 0.017256 | -0.006707 | 0.064419 | 0.007715 | 0.033449 | 0.11413 | 0.099707 | 0.089469 | 0.075047
6660.5625 | 122.5891 | -121.7468 | 0.70496 | 0.12643 | -0.00389 | -0.012 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.023943 | -0.043328 | 0.027798 | -0.042641 | -0.00775 | 121.8733 | 121.7429 | 121.7348 | 121.7447 | 121.751 | 121.8278 | 121.7436 | 0.11658 | 0.21657 | 0.091919 | 0.017256 | -0.002129 | 0.068997 | -0.001442 | 0.033449 | 0.11871 | 0.11802 | 0.094048 | 0.093361
6662.2656 | 122.699 | -121.7102 | 0.66834 | 0.12185 | 0.009846 | -0.016578 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.079959 | 0.18453 | 0.055298 | -0.019364 | -0.03875 | 0.036954 | -0.038063 | -0.003172 | 121.8321 | 121.7201 | 121.6936 | 121.7127 | 121.719 | 121.7912 | 121.707 | 0.12116 | 0.22573 | 0.096497 | 0.021835 | 0.002449 | 0.078153 | 0.003136 | 0.038027 | 0.11871 | 0.11802 | 0.094048 | 0.093361
6664.0781 | 122.6028 | -121.7468 | 0.73242 | 0.12643 | 0.005267 | -0.007421 | -0.002124 | 0.004219 | 0.085583 | -0.007779 | 0.066223 | 0.18453 | 0.046142 | -0.028522 | -0.043328 | 0.02322 | -0.038063 | -0.00775 | 121.8733 | 121.7521 | 121.7394 | 121.7447 | 121.751 | 121.8324 | 121.739 | 0.10742 | 0.22573 | 0.087341 | 0.012677 | -0.002129 | 0.064419 | 0.003136 | 0.033449 | 0.10955 | 0.10429 | 0.08947 | 0.084205
6665.8438 | 122.699 | -121.7422 | 0.66376 | 0.12643 | 0.005267 | -0.016578 | 0.002454 | 0.008797 | 0.085583 | -0.012357 | 0.070802 | 0.18453 | 0.046142 | -0.019364 | -0.043328 | 0.032376 | -0.028906 | -0.00775 | 121.8687 | 121.7475 | 121.7257 | 121.7447 | 121.751 | 121.8278 | 121.7299 | 0.112 | 0.22573 | 0.087341 | 0.021835 | -0.002129 | 0.073575 | 0.012293 | 0.033449 | 0.11413 | 0.099708 | 0.08947 | 0.075048
6667.625 | 122.6349 | -121.7606 | 0.72784 | 0.12185 | 0.000689 | -0.012 | 0.002454 | 0.017953 | 0.076426 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.028906 | -0.003172 | 121.8824 | 121.7612 | 121.7486 | 121.763 | 121.7785 | 121.837 | 121.7574 | 0.112 | 0.22573 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.012293 | 0.038027 | 0.11413 | 0.099708 | 0.094048 | 0.079626
6669.4062 | 122.5891 | -121.7651 | 0.71869 | 0.12185 | 0.000689 | -0.012 | 0.007033 | 0.017953 | 0.076426 | 0.001377 | 0.070802 | 0.18453 | 0.05072 | -0.028522 | -0.03875 | 0.027798 | -0.038063 | -0.00775 | 121.887 | 121.7658 | 121.7531 | 121.7722 | 121.7831 | 121.8416 | 121.7665 | 0.112 | 0.22573 | 0.091919 | 0.012677 | 0.002449 | 0.068997 | 0.003136 | 0.033449 | 0.10955 | 0.10887 | 0.08947 | 0.088783
6671.1094 | 122.6166 | -121.7377 | 0.74616 | 0.12643 | 0.014425 | -0.007421 | 0.002454 | 0.017953 | 0.085583 | -0.003201 | 0.070802 | 0.17995 | 0.041563 | -0.019364 | -0.043328 | 0.027798 | -0.033484 | -0.003172 | 121.8641 | 121.7521 | 121.7303 | 121.7401 | 121.7556 | 121.8233 | 121.7345 | 0.112 | 0.22115 | 0.082762 | 0.021835 | -0.002129 | 0.068997 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.084891 | 0.075047
6672.875 | 122.7173 | -121.6965 | 0.6958 | 0.12185 | 0.000689 | -0.016578 | -0.006703 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.05072 | -0.023943 | -0.043328 | 0.027798 | -0.028906 | -0.00775 | 121.8183 | 121.6972 | 121.6799 | 121.6898 | 121.7007 | 121.7775 | 121.6933 | 0.112 | 0.22573 | 0.091919 | 0.017256 | -0.002129 | 0.068997 | 0.012293 | 0.033449 | 0.11413 | 0.099708 | 0.094048 | 0.079626
6674.6719 | 122.6303 | -121.7514 | 0.72327 | 0.13101 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.041563 | -0.033101 | -0.047906 | 0.036954 | -0.042641 | -0.00775 | 121.8824 | 121.7613 | 121.744 | 121.7539 | 121.7602 | 121.8324 | 121.7482 | 0.112 | 0.22115 | 0.082762 | 0.008098 | -0.006707 | 0.078153 | -0.001442 | 0.033449 | 0.11871 | 0.11344 | 0.089469 | 0.084204
6676.3906 | 122.6486 | -121.7331 | 0.70953 | 0.12643 | 0.014425 | -0.007421 | 0.002454 | 0.013375 | 0.081005 | -0.003201 | 0.066223 | 0.17995 | 0.046142 | -0.023943 | -0.043328 | 0.027798 | -0.033484 | -0.00775 | 121.8595 | 121.7475 | 121.7257 | 121.7355 | 121.7465 | 121.8141 | 121.7299 | 0.10742 | 0.22115 | 0.087341 | 0.017256 | -0.002129 | 0.068997 | 0.007715 | 0.033449 | 0.10955 | 0.099707 | 0.08947 | 0.079626
6678.1562 | 122.6212 | -121.7239 | 0.74158 | 0.13101 | 0.009846 | -0.012 | 0.011611 | 0.008797 | 0.071848 | -0.012357 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.00775 | 121.8549 | 121.7338 | 121.7119 | 121.7355 | 121.7327 | 121.7958 | 121.7116 | 0.112 | 0.22115 | 0.091919 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.033449 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6679.9219 | 122.5891 | -121.7789 | 0.737 | 0.12643 | 0.009846 | 0.001736 | 0.002454 | 0.013375 | 0.076426 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.043328 | 0.036954 | -0.038063 | -0.003172 | 121.9053 | 121.7887 | 121.7806 | 121.7813 | 121.7922 | 121.8553 | 121.7802 | 0.112 | 0.21657 | 0.091919 | 0.017256 | -0.002129 | 0.078153 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.094048 | 0.088783
6681.7031 | 122.6257 | -121.7468 | 0.73242 | 0.13101 | 0.014425 | -0.007421 | 0.007033 | 0.008797 | 0.076426 | -0.003201 | 0.07538 | 0.17537 | 0.05072 | -0.023943 | -0.034171 | 0.027798 | -0.028906 | -0.003172 | 121.8778 | 121.7613 | 121.7394 | 121.7539 | 121.7556 | 121.8233 | 121.7436 | 0.11658 | 0.21657 | 0.091919 | 0.017256 | 0.007028 | 0.068997 | 0.012293 | 0.038027 | 0.10955 | 0.10429 | 0.084891 | 0.079626
6683.4688 | 122.6898 | -121.7194 | 0.70953 | 0.12643 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | -0.003201 | 0.070802 | 0.17995 | 0.041563 | -0.023943 | -0.043328 | 0.027798 | -0.038063 | -0.012328 | 121.8458 | 121.7292 | 121.7119 | 121.7172 | 121.7282 | 121.7958 | 121.7162 | 0.112 | 0.22115 | 0.082762 | 0.017256 | -0.002129 | 0.068997 | 0.003136 | 0.028871 | 0.11413 | 0.10887 | 0.084891 | 0.079626
6685.1719 | 122.6532 | -121.7422 | 0.70496 | 0.13101 | 0.005267 | -0.012 | 0.007033 | 0.008797 | 0.076426 | 0.005955 | 0.061645 | 0.18453 | 0.046142 | -0.023943 | -0.047906 | 0.032376 | -0.033484 | -0.00775 | 121.8733 | 121.7475 | 121.7302 | 121.7493 | 121.751 | 121.8187 | 121.7482 | 0.10284 | 0.22573 | 0.087341 | 0.017256 | -0.006707 | 0.073575 | 0.007715 | 0.033449 | 0.10955 | 0.095129 | 0.094048 | 0.079626
6686.9375 | 122.6486 | -121.7285 | 0.71869 | 0.11727 | 0.009846 | -0.007421 | 0.007033 | 0.008797 | 0.085583 | -0.003201 | 0.07538 | 0.17079 | 0.055298 | -0.033101 | -0.052484 | 0.036954 | -0.042641 | -0.012328 | 121.8458 | 121.7384 | 121.7211 | 121.7355 | 121.7373 | 121.8141 | 121.7253 | 0.11658 | 0.21199 | 0.096497 | 0.008098 | -0.011285 | 0.078153 | -0.001442 | 0.028871 | 0.12786 | 0.11802 | 0.10778 | 0.097939
6688.7031 | 122.6852 | -121.6965 | 0.70038 | 0.12643 | 0.005267 | -0.021157 | 0.002454 | 0.008797 | 0.076426 | -0.007779 | 0.070802 | 0.17995 | 0.046142 | -0.028522 | -0.043328 | 0.036954 | -0.042641 | -0.012328 | 121.8229 | 121.7017 | 121.6753 | 121.6989 | 121.7053 | 121.7729 | 121.6887 | 0.112 | 0.22115 | 0.087341 | 0.012677 | -0.002129 | 0.078153 | -0.001442 | 0.028871 | 0.11413 | 0.11344 | 0.08947 | 0.088783
6690.4062 | 122.6578 | -121.7285 | 0.71869 | 0.12185 | 0.000689 | -0.012 | 0.007033 | 0.013375 | 0.071848 | -0.007779 | 0.061645 | 0.17537 | 0.041563 | -0.023943 | -0.03875 | 0.02322 | -0.024328 | -0.012328 | 121.8504 | 121.7292 | 121.7165 | 121.7355 | 121.7419 | 121.8004 | 121.7207 | 0.10284 | 0.21657 | 0.082762 | 0.017256 | 0.002449 | 0.064419 | 0.016871 | 0.028871 | 0.10039 | 0.085973 | 0.080313 | 0.065891
6692.1719 | 122.7219 | -121.7285 | 0.70496 | 0.12185 | 0.000689 | -0.002842 | -0.002124 | 0.008797 | 0.081005 | -0.007779 | 0.07538 | 0.17537 | 0.05072 | -0.028522 | -0.03875 | 0.036954 | -0.038063 | -0.00775 | 121.8504 | 121.7292 | 121.7257 | 121.7264 | 121.7373 | 121.8095 | 121.7207 | 0.11658 | 0.21657 | 0.091919 | 0.012677 | 0.002449 | 0.078153 | 0.003136 | 0.033449 | 0.11413 | 0.11344 | 0.08947 | 0.088783
6693.9375 | 122.5891 | -121.7651 | 0.73242 | 0.12643 | 0.009846 | -0.002842 | -0.002124 | 0.004219 | 0.081005 | -0.003201 | 0.066223 | 0.17079 | 0.05072 | -0.023943 | -0.03875 | 0.032376 | -0.038063 | -0.003172 | 121.8916 | 121.775 | 121.7623 | 121.763 | 121.7694 | 121.8461 | 121.7619 | 0.10742 | 0.21199 | 0.091919 | 0.017256 | 0.002449 | 0.073575 | 0.003136 | 0.038027 | 0.10497 | 0.10429 | 0.08947 | 0.088783
6695.7188 | 122.7127 | -121.7056 | 0.67749 | 0.13101 | 0.009846 | -0.012 | 0.007033 | 0.004219 | 0.081005 | -0.003201 | 0.070802 | 0.17995 | 0.055298 | -0.019364 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.8366 | 121.7155 | 121.6936 | 121.7127 | 121.7098 | 121.7866 | 121.7024 | 0.112 | 0.22115 | 0.096497 | 0.021835 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11413 | 0.10429 | 0.098626 | 0.088782
6697.4062 | 122.6578 | -121.7422 | 0.71411 | 0.12185 | 0.000689 | -0.002842 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.17995 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.028906 | -0.00775 | 121.8641 | 121.7429 | 121.7394 | 121.7447 | 121.751 | 121.8233 | 121.7436 | 0.112 | 0.22115 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.012293 | 0.033449 | 0.10955 | 0.099708 | 0.08947 | 0.079626
6699.1719 | 122.6898 | -121.7239 | 0.68207 | 0.12185 | 0.009846 | -0.007421 | -0.002124 | 0.008797 | 0.081005 | 0.001377 | 0.066223 | 0.18453 | 0.05072 | -0.023943 | -0.047906 | 0.027798 | -0.028906 | -0.012328 | 121.8458 | 121.7338 | 121.7165 | 121.7218 | 121.7327 | 121.8049 | 121.7253 | 0.10742 | 0.22573 | 0.091919 | 0.017256 | -0.006707 | 0.068997 | 0.012293 | 0.028871 | 0.11413 | 0.095129 | 0.098626 | 0.079626
6700.9531 | 122.6578 | -121.7377 | 0.72327 | 0.12643 | 0.009846 | -0.007421 | 0.007033 | 0.022531 | 0.076426 | 0.001377 | 0.066223 | 0.17537 | 0.05072 | -0.014785 | -0.03875 | 0.032376 | -0.038063 | -0.003172 | 121.8641 | 121.7475 | 121.7303 | 121.7447 | 121.7602 | 121.8141 | 121.739 | 0.10742 | 0.21657 | 0.091919 | 0.026414 | 0.002449 | 0.073575 | 0.003136 | 0.038027 | 0.10497 | 0.10429 | 0.08947 | 0.088783
6702.7188 | 122.7219 | -121.7148 | 0.70496 | 0.11727 | 0.000689 | -0.016578 | -0.002124 | 0.008797 | 0.071848 | -0.012357 | 0.066223 | 0.17537 | 0.059877 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.8321 | 121.7155 | 121.6982 | 121.7127 | 121.7236 | 121.7866 | 121.7024 | 0.10742 | 0.21657 | 0.10108 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.10955 | 0.10429 | 0.1032 | 0.09794
6704.4219 | 122.7219 | -121.7102 | 0.69122 | 0.13101 | 0.000689 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | -0.007779 | 0.070802 | 0.17995 | 0.05072 | -0.019364 | -0.043328 | 0.027798 | -0.028906 | -0.003172 | 121.8412 | 121.7109 | 121.7028 | 121.7127 | 121.719 | 121.7912 | 121.7024 | 0.112 | 0.22115 | 0.091919 | 0.021835 | -0.002129 | 0.068997 | 0.012293 | 0.038027 | 0.11413 | 0.099708 | 0.094048 | 0.079626
6706.1875 | 122.7219 | -121.7422 | 0.6958 | 0.13101 | 0.005267 | -0.002842 | 0.002454 | -0.000359 | 0.071848 | 0.001377 | 0.07538 | 0.17537 | 0.05072 | -0.023943 | -0.043328 | 0.032376 | -0.033484 | -0.003172 | 121.8733 | 121.7475 | 121.7394 | 121.7447 | 121.7419 | 121.8141 | 121.7436 | 0.11658 | 0.21657 | 0.091919 | 0.017256 | -0.002129 | 0.073575 | 0.007715 | 0.038027 | 0.11871 | 0.10886 | 0.094048 | 0.084204
6707.8906 | 122.6898 | -121.7514 | 0.71411 | 0.12185 | 0.000689 | -0.007421 | 0.002454 | 0.017953 | 0.081005 | -0.003201 | 0.066223 | 0.18453 | 0.046142 | -0.028522 | -0.03875 | 0.027798 | -0.033484 | -0.003172 | 121.8733 | 121.7521 | 121.744 | 121.7539 | 121.7694 | 121.8324 | 121.7482 | 0.10742 | 0.22573 | 0.087341 | 0.012677 | 0.002449 | 0.068997 | 0.007715 | 0.038027 | 0.10497 | 0.099707 | 0.084892 | 0.079626
6709.6719 | 122.6028 | -121.8018 | 0.73242 | 0.12185 | 0.000689 | -0.007421 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.061645 | 0.18911 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.033484 | -0.012328 | 121.9236 | 121.8024 | 121.7943 | 121.8088 | 121.8106 | 121.8828 | 121.7986 | 0.10284 | 0.23031 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | 0.007715 | 0.028871 | 0.10039 | 0.095129 | 0.08947 | 0.084204
6711.4375 | 122.5983 | -121.7972 | 0.71411 | 0.13101 | 0.005267 | -0.007421 | -0.002124 | 0.008797 | 0.076426 | 0.001377 | 0.070802 | 0.17995 | 0.05072 | -0.028522 | -0.03875 | 0.032376 | -0.038063 | -0.012328 | 121.9282 | 121.8024 | 121.7898 | 121.7951 | 121.806 | 121.8736 | 121.7986 | 0.112 | 0.22115 | 0.091919 | 0.012677 | 0.002449 | 0.073575 | 0.003136 | 0.028871 | 0.10955 | 0.10887 | 0.08947 | 0.088783
6713.1562 | 122.5891 | -121.7743 | 0.70038 | 0.13101 | 0.000689 | -0.007421 | 0.002454 | 0.013375 | 0.081005 | 0.001377 | 0.07538 | 0.18453 | 0.046142 | -0.023943 | -0.052484 | 0.032376 | -0.042641 | -0.012328 | 121.9053 | 121.775 | 121.7669 | 121.7767 | 121.7877 | 121.8553 | 121.7757 | 0.11658 | 0.22573 | 0.087341 | 0.017256 | -0.011285 | 0.073575 | -0.001442 | 0.028871 | 0.12786 | 0.11802 | 0.098626 | 0.088783
6714.9375 | 122.6532 | -121.756 | 0.72784 | 0.12643 | 0.000689 | -0.012 | 0.007033 | 0.004219 | 0.076426 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.028522 | -0.052484 | 0.032376 | -0.038063 | -0.003172 | 121.8824 | 121.7567 | 121.744 | 121.763 | 121.7602 | 121.8324 | 121.7574 | 0.112 | 0.21657 | 0.091919 | 0.012677 | -0.011285 | 0.073575 | 0.003136 | 0.038027 | 0.12329 | 0.10887 | 0.1032 | 0.088783
6716.7031 | 122.7402 | -121.7422 | 0.68665 | 0.12643 | 0.000689 | -0.012 | 0.007033 | 0.008797 | 0.081005 | -0.003201 | 0.070802 | 0.18453 | 0.055298 | -0.028522 | -0.03875 | 0.02322 | -0.042641 | -0.003172 | 121.8687 | 121.7429 | 121.7302 | 121.7493 | 121.751 | 121.8233 | 121.739 | 0.112 | 0.22573 | 0.096497 | 0.012677 | 0.002449 | 0.064419 | -0.001442 | 0.038027 | 0.10955 | 0.11344 | 0.094048 | 0.097939
6718.4688 | 122.731 | -121.7102 | 0.68207 | 0.13101 | 0.009846 | -0.007421 | 0.002454 | 0.008797 | 0.081005 | 0.001377 | 0.070802 | 0.17537 | 0.05072 | -0.023943 | -0.03875 | 0.027798 | -0.042641 | -0.012328 | 121.8412 | 121.7201 | 121.7028 | 121.7127 | 121.719 | 121.7912 | 121.7116 | 0.112 | 0.21657 | 0.091919 | 0.017256 | 0.002449 | 0.068997 | -0.001442 | 0.028871 | 0.10955 | 0.11344 | 0.08947 | 0.093361
6720.1719 | 122.7448 | -121.7285 | 0.68665 | 0.13101 | 0.005267 | -0.012 | 0.011611 | 0.013375 | 0.076426 | -0.012357 | 0.070802 | 0.17995 | 0.041563 | -0.023943 | -0.043328 | 0.032376 | -0.038063 | -0.003172 | 121.8595 | 121.7338 | 121.7165 | 121.7401 | 121.7419 | 121.8049 | 121.7162 | 0.112 | 0.22115 | 0.082762 | 0.017256 | -0.002129 | 0.073575 | 0.003136 | 0.038027 | 0.11413 | 0.10887 | 0.084891 | 0.079626

## Thermal Data
Fire Time | B Position - Middle
-0.824 | 14.6403
0.176 | 14.6458
1.176 | 14.6488
2.176 | 14.6532
3.176 | 14.6676
4.176 | 14.739
5.176 | 16.8651
6.176 | 19.6475
7.176 | 25.385
8.176 | 31.9947
9.176 | 38.2823
10.176 | 47.7526
11.176 | 59.017
12.176 | 68.3233
13.176 | 79.2357
14.176 | 89.4143
15.176 | 99.5164
16.176 | 108.6348
17.176 | 117.7363
18.176 | 125.8469
19.176 | 134.8542
20.1917 | 139.1662
21.176 | 143.1879
22.176 | 145.9599
23.176 | 147.1687
24.176 | 146.8651
25.176 | 144.9948
26.176 | 143.7164
27.176 | 141.116
28.176 | 138.0992
29.176 | 135.3484
30.176 | 132.8397
31.176 | 130.6076
32.176 | 128.1382
33.176 | 126.6626
34.176 | 125.0491
35.176 | 123.1483
36.176 | 121.2155
37.176 | 119.3996
38.176 | 117.9362
39.176 | 116.2214
40.176 | 114.3483
41.176 | 112.5712
42.176 | 111.122
43.176 | 110.1706
44.176 | 109.1411
45.176 | 108.1691
46.176 | 106.9483
47.176 | 105.5901
48.176 | 104.6352
49.176 | 103.8919
50.1917 | 103.0403
51.176 | 101.8375
52.176 | 100.9867
53.176 | 100.1988
54.176 | 99.3179
55.176 | 98.5752
56.176 | 97.695
57.176 | 96.6825
58.176 | 95.9993
59.176 | 95.4517
60.176 | 95.0146
61.176 | 94.257
62.176 | 93.5249
63.176 | 92.8287
64.176 | 91.892
65.176 | 91.0941
66.176 | 90.1909
67.176 | 89.615
68.176 | 89.092
69.176 | 88.3898
70.176 | 88.225
71.176 | 87.9494
72.176 | 87.2556
73.176 | 86.4792
74.176 | 86.0783
75.176 | 86.0086
76.176 | 85.6489
77.176 | 85.2209
78.176 | 85.4387
79.176 | 84.8609
80.176 | 84.8175
81.176 | 84.9864
82.176 | 85.0852
83.176 | 85.4285
84.176 | 85.7768
85.176 | 86.3372
86.176 | 86.6344
87.176 | 86.8468
88.176 | 87.6008
89.176 | 88.2083
90.176 | 88.8508
91.176 | 89.5585
92.176 | 89.4817
93.176 | 89.8692
94.176 | 90.595
95.176 | 91.7649
96.176 | 92.9744
97.176 | 93.4291
98.176 | 94.0751
99.176 | 94.5534
100.176 | 95.3329
101.176 | 95.837
102.176 | 95.8059
103.176 | 96.2634
104.176 | 97.1018
105.176 | 98.124
106.176 | 98.9238
107.176 | 99.6119
108.176 | 100.0782
109.176 | 100.8776
110.176 | 101.4398
111.176 | 101.7931
112.176 | 102.4273
113.176 | 102.7137
114.176 | 103.1326
115.176 | 103.4117
116.176 | 103.244
117.176 | 103.4895
118.176 | 103.5636
119.176 | 103.2883
120.176 | 103.5415
121.176 | 104.3837
122.176 | 104.6305
123.176 | 104.9853
124.176 | 106.013
125.176 | 106.9772
126.176 | 107.1261
127.176 | 107.5691
128.176 | 107.9829
129.176 | 108.2405
130.176 | 108.7233
131.176 | 109.0254
132.176 | 109.3754
133.176 | 109.7517
134.176 | 110.2512
135.176 | 110.6319
136.176 | 110.4927
137.176 | 110.1424
138.176 | 109.2524
139.176 | 109.3509
140.176 | 109.6059
141.176 | 109.3055
142.176 | 109.7253
143.176 | 109.3077
144.176 | 109.3307
145.176 | 108.9885
146.176 | 108.7095
147.176 | 108.9983
148.176 | 108.9789
149.176 | 108.4177
150.176 | 108.0066
151.176 | 107.9863
152.176 | 108.3184
153.176 | 108.2315
154.176 | 108.7595
155.176 | 108.9145
156.176 | 109.4584
157.176 | 109.307
158.176 | 109.1834
159.176 | 108.8058
160.176 | 109.6381
161.176 | 109.8089
162.176 | 110.4829
163.176 | 110.6877
164.176 | 110.5558
165.176 | 110.2429
166.176 | 110.6819
167.176 | 110.4526
168.176 | 109.7988
169.176 | 109.8559
170.176 | 109.9789
171.176 | 110.341
172.176 | 110.0102
173.176 | 109.6182
174.176 | 109.1417
175.176 | 109.1768
176.176 | 109.1175
177.176 | 109.5838
178.176 | 109.3848
179.176 | 108.8011
180.176 | 108.8717
181.176 | 108.9084
182.176 | 109.7348
183.176 | 110.6525
184.176 | 109.6971
185.176 | 109.342
186.176 | 109.3427
187.176 | 109.0199
188.176 | 109.3387
189.176 | 110.2082
190.176 | 110.7617
191.176 | 111.4928
192.176 | 112.8824
193.176 | 113.464
194.176 | 113.7053
195.176 | 114.7859
196.176 | 115.1522
197.176 | 115.8797
198.176 | 115.8943
199.176 | 116.3601
200.1917 | 116.6599
201.176 | 117.0645
202.176 | 117.1973
203.176 | 117.7463
204.176 | 118.312
205.176 | 119.1839
206.176 | 119.7983
207.176 | 120.1971
208.176 | 120.6209
209.176 | 121.2011
210.176 | 121.3794
211.176 | 122.0232
212.176 | 122.4215
213.176 | 122.7842
214.176 | 122.7675
215.176 | 122.5343
216.176 | 122.341
217.176 | 122.6807
218.176 | 122.6115
219.176 | 122.6821
220.176 | 123.7277
221.176 | 124.3162
222.176 | 124.3363
223.176 | 124.533
224.176 | 124.4436
225.176 | 124.8066
226.176 | 124.6545
227.176 | 124.7514
228.176 | 123.8298
229.176 | 123.6263
230.176 | 123.5941
231.176 | 123.4175
232.176 | 122.4079
233.176 | 122.2046
234.176 | 122.5704
235.176 | 122.7781
236.176 | 123.0704
237.176 | 122.4845
238.176 | 122.4156
239.176 | 121.8316
240.176 | 121.2589
241.176 | 120.9013
242.176 | 120.473
243.176 | 120.3078
244.176 | 119.7964
245.176 | 119.6335
246.176 | 119.2883
247.176 | 119.4959
248.176 | 120.1102
249.176 | 120.5696
250.176 | 120.6924
251.176 | 120.9663
252.176 | 121.4131
253.176 | 120.8391
254.176 | 121.536
255.176 | 121.196
256.176 | 121.3029
257.176 | 121.033
258.176 | 121.1176
259.176 | 120.4827
260.176 | 120.6568
261.176 | 120.2688
262.176 | 119.9155
263.176 | 120.0859
264.176 | 120.1804
265.176 | 120.1177
266.176 | 119.8338
267.176 | 118.9161
268.176 | 119.7347
269.176 | 120.4397
270.176 | 121.1806
271.176 | 121.6994
272.176 | 122.3807
273.176 | 123.0536
274.176 | 122.8961
275.176 | 122.6165
276.176 | 122.2286
277.176 | 121.8968
278.176 | 121.7249
279.176 | 121.9659
280.176 | 122.0514
281.176 | 122.027
282.176 | 121.8121
283.176 | 121.9017
284.176 | 122.5639
285.176 | 123.0598
286.176 | 123.6084
287.176 | 123.8653
288.176 | 123.8151
289.176 | 123.4599
290.176 | 123.4412
291.176 | 123.8705
292.176 | 124.0597
293.176 | 123.6532
294.176 | 123.748
295.176 | 124.0864
296.176 | 124.0764
297.176 | 124.1926
298.176 | 124.2887
299.176 | 123.9108
300.176 | 123.6534
301.176 | 122.957
302.176 | 122.3241
303.176 | 122.2972
304.176 | 122.3013
305.176 | 121.8398
306.176 | 122.2338
307.176 | 121.9906
308.176 | 121.7781
309.176 | 122.6484
310.176 | 123.114
311.176 | 122.7795
312.176 | 123.4491
313.176 | 122.937
314.176 | 122.947
315.176 | 122.7167
316.176 | 122.2401
317.176 | 122.1919
318.176 | 122.4422
319.176 | 122.2291
320.176 | 122.0142
321.176 | 122.1068
322.176 | 121.8063
323.176 | 122.6311
324.176 | 123.837
325.176 | 124.1792
326.176 | 124.2708
327.176 | 124.8065
328.176 | 124.3643
329.176 | 124.2587
330.176 | 124.7435
331.176 | 124.3489
332.176 | 124.7976
333.176 | 125.3595
334.176 | 125.2519
335.176 | 125.3306
336.176 | 125.7778
337.176 | 126.6076
338.176 | 126.4112
339.176 | 126.9631
340.176 | 126.5284
341.176 | 125.7645
342.176 | 126.3687
343.176 | 126.072
344.176 | 126.3581
345.176 | 126.3771
346.176 | 126.1003
347.176 | 126.1603
348.176 | 126.1368
349.176 | 126.5821
350.176 | 127.0656
351.176 | 127.2262
352.176 | 126.4042
353.176 | 126.6256
354.176 | 126.5055
355.176 | 126.9037
356.176 | 126.3403
357.176 | 126.7453
358.176 | 127.1257
359.176 | 127.0823
360.176 | 127.4021
361.176 | 127.306
362.176 | 127.306
363.176 | 127.4962
364.176 | 127.8726
365.176 | 128.0157
366.176 | 127.173
367.176 | 127.4136
368.176 | 127.3381
369.176 | 126.656
370.176 | 126.2939
371.176 | 126.1794
372.176 | 126.3371
373.176 | 126.9424
374.176 | 127.4807
375.176 | 128.0892
376.176 | 129.08
377.176 | 129.4994
378.176 | 130.2295
379.176 | 130.163
380.176 | 129.6864
381.176 | 129.9271
382.176 | 129.5403
383.176 | 129.955
384.176 | 130.3811
385.176 | 130.7759
386.176 | 131.0846
387.176 | 131.2317
388.176 | 130.7354
389.176 | 129.3396
390.176 | 129.8371
391.176 | 130.3927
392.176 | 130.8214
393.176 | 131.236
394.176 | 131.0758
395.176 | 130.6011
396.176 | 130.4409
397.176 | 131.3889
398.176 | 131.2248
399.176 | 131.4678
400.176 | 131.8845
401.176 | 131.7484
402.176 | 131.4337
403.176 | 130.6507
404.176 | 129.948
405.176 | 130.2119
406.176 | 129.6107
407.176 | 130.2711
408.176 | 130.6086
409.176 | 130.8577
410.176 | 131.2703
411.176 | 130.7202
412.176 | 130.2649
413.176 | 130.5809
414.176 | 130.8617
415.176 | 131.4054
416.176 | 132.0798
417.1917 | 132.3795
418.176 | 133.0507
419.176 | 133.0419
420.1917 | 132.9612
421.176 | 133.3091
422.176 | 133.4188
423.1917 | 133.6898
424.1917 | 134.4277
425.176 | 134.5841
426.176 | 134.2377
427.176 | 133.473
428.176 | 133.0349
429.176 | 133.367
430.176 | 133.7229
431.176 | 133.8522
432.176 | 133.8416
433.176 | 134.1096
434.176 | 133.5954
435.176 | 133.2394
436.176 | 132.2584
437.1917 | 131.8976
438.176 | 131.8822
439.176 | 132.0981
440.176 | 132.8802
441.176 | 132.1145
442.176 | 132.3065
443.176 | 132.5061
444.176 | 133.1787
445.176 | 133.5687
446.176 | 133.3944
447.176 | 133.5668
448.176 | 134.3228
449.176 | 134.6603
450.176 | 134.7026
451.176 | 134.7272
452.176 | 133.7714
453.176 | 133.6935
454.176 | 133.8576
455.176 | 133.7713
456.176 | 134.2951
457.176 | 134.761
458.176 | 135.3229
459.176 | 135.6509
460.176 | 135.3274
461.176 | 135.379
462.176 | 135.3643
463.176 | 135.4451
464.176 | 135.049
465.176 | 135.0753
466.176 | 135.3227
467.176 | 135.6812
468.176 | 136.0194
469.176 | 136.5299
470.176 | 137.3497
471.176 | 137.5058
472.176 | 137.775
473.176 | 137.7015
474.176 | 138.0143
475.1917 | 138.1036
476.176 | 138.5298
477.176 | 139.2014
478.176 | 137.8413
479.176 | 138.5954
480.1917 | 139.0009
481.1917 | 139.4347
482.176 | 139.6082
483.176 | 139.2906
484.176 | 138.7839
485.176 | 138.1722
486.176 | 138.3292
487.176 | 138.7512
488.176 | 139.2781
489.176 | 139.7269
490.176 | 140.514
491.176 | 140.8784
492.176 | 141.4258
493.176 | 141.8933
494.176 | 141.9058
495.176 | 141.4391
496.176 | 141.2255
497.176 | 141.1365
498.176 | 140.4635
499.176 | 139.819
500.176 | 139.7514
501.176 | 139.6132
502.176 | 139.6949
503.176 | 139.3254
504.176 | 138.8752
505.176 | 139.2585
506.176 | 139.674
507.176 | 140.251
508.176 | 140.7874
509.176 | 140.5355
510.176 | 140.9376
511.176 | 140.3666
512.176 | 140.2221
513.176 | 140.2023
514.176 | 140.4987
515.176 | 140.6083
516.176 | 140.5352
517.176 | 140.3812
518.176 | 140.5946
519.176 | 140.1994
520.176 | 140.7064
521.176 | 140.5378
522.176 | 140.1534
523.176 | 140.0137
524.176 | 140.2614
525.176 | 139.8713
526.176 | 139.1965
527.176 | 139.0927
528.176 | 138.8777
529.176 | 138.8784
530.176 | 138.9341
531.176 | 138.7806
532.176 | 138.8738
533.176 | 138.8579
534.176 | 138.784
535.176 | 138.5369
536.176 | 138.259
537.176 | 138.1911
538.176 | 138.3882
539.176 | 138.0487
540.176 | 138.2386
541.176 | 137.7766
542.176 | 137.6348
543.176 | 137.9874
544.176 | 138.5282
545.176 | 138.9842
546.176 | 138.8633
547.176 | 139.3586
548.176 | 138.5307
549.176 | 138.3659
550.176 | 138.3655
551.176 | 138.6178
552.176 | 138.4549
553.176 | 138.5307
554.176 | 138.9116
555.176 | 138.6917
556.176 | 138.2826
557.176 | 138.6888
558.176 | 138.998
559.176 | 139.2009
560.176 | 138.9747
561.176 | 139.1641
562.176 | 139.4976
563.176 | 139.9167
564.176 | 140.4968
565.176 | 140.6857
566.176 | 140.3954
567.176 | 140.0331
568.176 | 140.178
569.176 | 140.6842
570.176 | 140.7511
571.176 | 140.5591
572.176 | 140.4434
573.176 | 140.6737
574.176 | 139.9336
575.176 | 139.6221
576.176 | 139.6384
577.176 | 139.1724
578.176 | 139.6168
579.176 | 140.0052
580.176 | 140.4237
581.176 | 140.5678
582.176 | 140.4367
583.176 | 141.114
584.176 | 141.7888
585.176 | 141.7104
586.176 | 141.5246
587.176 | 141.854
588.176 | 142.5502
589.176 | 142.3822
590.176 | 142.4592
591.176 | 142.8088
592.176 | 142.5371
593.176 | 142.2093
594.176 | 142.2759
595.176 | 142.3306
596.176 | 142.126
597.176 | 142.1042
598.176 | 142.0327
599.176 | 142.049
600.176 | 142.4287
601.176 | 141.7585
602.176 | 141.4254
603.176 | 140.9602
604.176 | 141.2346
605.176 | 141.2751
606.176 | 141.5809
607.176 | 141.956
608.176 | 142.0746
609.176 | 141.7951
610.176 | 142.2367
611.176 | 142.4967
612.176 | 142.882
613.176 | 143.087
614.176 | 142.8851
615.176 | 143.084
616.176 | 142.9506
617.176 | 142.8676
618.176 | 142.8414
619.176 | 142.3559
620.176 | 141.8117
621.176 | 141.8554
622.176 | 141.7345
623.176 | 142.0394
624.176 | 141.6696
625.176 | 141.3484
626.176 | 141.3377
627.176 | 141.7366
628.176 | 141.9654
629.176 | 142.3862
630.176 | 142.4945
631.176 | 142.0218
632.176 | 141.6066
633.176 | 141.9483
634.176 | 142.5294
635.176 | 142.5075
636.176 | 142.5906
637.176 | 142.3445
638.176 | 142.9397
639.176 | 142.6334
640.176 | 142.5657
641.176 | 142.6493
642.176 | 142.8026
643.176 | 142.8342
644.176 | 143.1063
645.1917 | 143.1552
646.176 | 143.2606
647.176 | 143.0844
648.176 | 142.8446
649.176 | 142.9906
650.176 | 143.0334
651.176 | 143.3523
652.176 | 142.9945
653.176 | 143.0376
654.176 | 143.371
655.176 | 143.4987
656.176 | 143.4288
657.176 | 143.4767
658.176 | 143.5591
659.176 | 143.5985
660.176 | 143.8536
661.176 | 143.4801
662.176 | 143.8344
663.176 | 144.5025
664.176 | 145.0846
665.176 | 145.7821
666.176 | 145.3082
667.176 | 144.9422
668.176 | 144.5225
669.176 | 144.308
670.176 | 143.759
671.176 | 143.5761
672.176 | 143.7867
673.176 | 143.6871
674.176 | 143.7481
675.176 | 143.8887
676.176 | 144.1438
677.176 | 144.2548
678.176 | 144.4547
679.176 | 144.2274
680.176 | 144.0537
681.176 | 144.1955
682.176 | 143.9462
683.176 | 144.1013
684.176 | 144.29
685.176 | 144.4037
686.176 | 144.5283
687.176 | 144.6104
688.176 | 144.3845
689.176 | 144.37
690.176 | 144.5847
691.176 | 144.2535
692.176 | 143.9745
693.176 | 144.5509
694.176 | 144.5547
695.176 | 144.491
696.176 | 144.3966
697.176 | 144.9654
698.176 | 145.3229
699.176 | 144.9621
700.176 | 145.4242
701.176 | 145.7254
702.176 | 145.4027
703.176 | 146.8854
704.176 | 146.8702
705.176 | 147.0852
706.176 | 146.8516
707.176 | 146.74
708.176 | 146.7044
709.176 | 146.7234
710.176 | 146.6725
711.176 | 147.0708
712.176 | 146.7994
713.176 | 146.4316
714.176 | 147.2488
715.176 | 147.686
716.176 | 147.878
717.176 | 148.1911
718.176 | 148.529
719.176 | 148.5743
720.176 | 148.4755
721.176 | 148.2488
722.176 | 148.2689
723.176 | 148.5469
724.176 | 148.6378
725.176 | 148.6866
726.176 | 149.1709
727.176 | 148.9596
728.176 | 148.5417
729.176 | 148.6085
730.176 | 148.8763
731.176 | 148.9927
732.176 | 149.0158
733.176 | 148.8626
734.176 | 148.9463
735.176 | 149.2793
736.176 | 149.1321
737.176 | 149.1498
738.176 | 148.9294
739.176 | 148.8414
740.176 | 148.9504
741.176 | 148.8984
742.176 | 148.7334
743.176 | 148.7197
744.176 | 149.4057
745.176 | 150.1023
746.176 | 150.5172
747.176 | 150.4788
748.176 | 150.6683
749.176 | 151.2001
750.176 | 151.4102
751.176 | 151.8376
752.176 | 151.3283
753.176 | 151.1879
754.176 | 151.6045
755.176 | 151.5904
756.176 | 151.1462
757.176 | 151.0852
758.176 | 151.0374
759.176 | 150.948
760.176 | 151.811
761.176 | 152.2876
762.176 | 152.3894
763.176 | 152.309
764.176 | 153.1592
765.176 | 153.3048
766.176 | 153.096
767.176 | 152.8476
768.176 | 152.8251
769.176 | 153.0468
770.176 | 152.9836
771.176 | 153.0663
772.176 | 153.2066
773.176 | 153.1595
774.176 | 153.2186
775.176 | 153.3899
776.176 | 153.6064
777.176 | 154.0357
778.176 | 154.3905
779.176 | 154.4046
780.176 | 154.5143
781.176 | 154.6018
782.176 | 154.521
783.176 | 154.4079
784.176 | 154.4124
785.176 | 154.4372
786.176 | 154.2971
787.176 | 154.198
788.176 | 154.2314
789.176 | 154.2366
790.176 | 154.1037
791.176 | 153.9467
792.176 | 153.8845
793.176 | 153.7019
794.176 | 153.8027
795.176 | 154.4271
796.176 | 154.4923
797.176 | 154.7441
798.176 | 154.7322
799.176 | 154.8848
800.176 | 154.9737
801.176 | 154.7419
802.176 | 154.9145
803.176 | 154.5134
804.176 | 154.6006
805.176 | 154.741
806.176 | 154.2745
807.176 | 154.0905
808.176 | 154.565
809.176 | 155.2099
810.176 | 156.1712
811.176 | 157.071
812.176 | 156.7849
813.176 | 156.5785
814.176 | 156.6912
815.176 | 156.7257
816.176 | 156.4683
817.176 | 156.1495
818.176 | 155.7063
819.176 | 156.1319
820.176 | 156.2241
821.176 | 155.5395
822.176 | 155.4056
823.176 | 155.6262
824.176 | 155.8395
825.176 | 155.9177
826.176 | 155.5798
827.176 | 155.2334
828.176 | 155.3447
829.176 | 155.8099
830.176 | 156.3506
831.176 | 156.9206
832.176 | 157.8252
833.176 | 158.2681
834.176 | 158.4099
835.176 | 158.8488
836.176 | 159.0942
837.176 | 159.4245
838.176 | 160.1712
839.176 | 160.7819
840.176 | 160.9275
841.176 | 160.5223
842.176 | 160.2262
843.176 | 160.3017
844.176 | 160.3457
845.176 | 160.7797
846.176 | 160.4979
847.176 | 161.5244
848.176 | 161.6015
849.176 | 161.922
850.176 | 161.8738
851.176 | 161.9494
852.176 | 161.9512
853.176 | 162.0074
854.176 | 161.9886
855.176 | 161.6253
856.176 | 161.3125
857.176 | 161.1512
858.176 | 160.9153
859.176 | 160.9751
860.176 | 161.6684
861.176 | 162.0841
862.176 | 162.4161
863.176 | 162.3711
864.176 | 162.7233
865.176 | 162.3741
866.176 | 162.1971
867.176 | 161.7615
868.176 | 161.2175
869.176 | 161.1179
870.176 | 160.7894
871.176 | 160.9474
872.176 | 161.147
873.176 | 161.3442
874.176 | 161.4366
875.176 | 161.5032
876.176 | 161.5575
877.176 | 161.707
878.176 | 162.3598
879.176 | 162.5552
880.176 | 162.3983
881.176 | 162.3452
882.176 | 162.4175
883.176 | 162.2552
884.176 | 162.2818
885.176 | 162.5687
886.176 | 162.7942
887.176 | 162.6463
888.176 | 162.87
889.176 | 162.4935
890.176 | 162.4071
891.176 | 162.6413
892.176 | 162.6805
893.176 | 162.9104
894.176 | 163.7208
895.176 | 163.9985
896.176 | 164.5231
897.176 | 164.5159
898.176 | 164.4609
899.176 | 164.4294
900.176 | 164.2897
901.176 | 164.4887
902.176 | 164.9606
903.176 | 164.6705
904.176 | 164.7104
905.176 | 165.1464
906.176 | 165.3863
907.176 | 165.1322
908.176 | 165.6103
909.176 | 165.7074
910.176 | 166.3876
911.176 | 166.2987
912.176 | 166.3923
913.176 | 166.6116
914.176 | 166.7954
915.176 | 166.7048
916.176 | 166.5564
917.176 | 166.4649
918.176 | 166.3424
919.176 | 166.0423
920.176 | 166.3269
921.176 | 166.827
922.176 | 167.482
923.176 | 167.7148
924.176 | 167.9517
925.176 | 168.3473
926.176 | 168.5051
927.176 | 168.2163
928.176 | 167.7479
929.176 | 167.8332
930.176 | 167.9064
931.176 | 168.1277
932.176 | 168.1128
933.176 | 167.3653
934.176 | 168.1035
935.176 | 168.1785
936.176 | 168.6092
937.176 | 169.6228
938.176 | 170.2887
939.176 | 170.2752
940.176 | 170.5162
941.176 | 170.6727
942.176 | 170.247
943.176 | 169.9489
944.176 | 169.6595
945.176 | 170.4514
946.176 | 170.2036
947.176 | 170.0964
948.176 | 170.6954
949.176 | 171.3242
950.176 | 170.8737
951.176 | 171.3667
952.176 | 171.0882
953.176 | 171.8602
954.176 | 171.8129
955.176 | 171.7932
956.176 | 172.1774
957.176 | 172.4667
958.176 | 173.6066
959.176 | 173.8064
960.176 | 174.7454
961.176 | 175.0401
962.176 | 175.2993
963.176 | 175.9554
964.176 | 175.3348
965.176 | 175.6494
966.176 | 176.1007
967.176 | 176.4639
968.176 | 176.5752
969.176 | 176.6439
970.176 | 175.6802
971.176 | 175.5507
972.176 | 175.7637
973.176 | 175.6931
974.176 | 175.5677
975.176 | 175.8519
976.176 | 176.0054
977.176 | 176.1722
978.176 | 175.856
979.176 | 176.1923
980.176 | 175.9448
981.176 | 175.8322
982.176 | 175.4521
983.176 | 175.7721
984.176 | 175.7287
985.176 | 176.3231
986.176 | 176.7511
987.176 | 177.0774
988.176 | 177.178
989.176 | 177.0531
990.176 | 176.7629
991.176 | 176.7281
992.176 | 176.5455
993.176 | 176.5255
994.176 | 176.4791
995.176 | 176.737
996.176 | 177.0521
997.176 | 177.0817
998.176 | 177.4567
999.176 | 177.3348
1000.176 | 177.1769
1001.176 | 177.0278
1002.176 | 177.4176
1003.176 | 177.7096
1004.176 | 178.1039
1005.176 | 178.2029
1006.176 | 178.4215
1007.176 | 178.2735
1008.176 | 178.5322
1009.176 | 178.925
1010.176 | 178.9162
1011.176 | 179.1565
1012.176 | 178.8139
1013.176 | 178.926
1014.176 | 178.8352
1015.176 | 178.6584
1016.176 | 178.9994
1017.176 | 178.7755
1018.176 | 178.7219
1019.176 | 178.1818
1020.176 | 177.7379
1021.176 | 177.8115
1022.176 | 177.8254
1023.176 | 177.9627
1024.176 | 177.5118
1025.176 | 177.3488
1026.176 | 177.3802
1027.176 | 177.4648
1028.176 | 177.5798
1029.176 | 178.245
1030.176 | 178.4148
1031.176 | 178.596
1032.176 | 179.0871
1033.176 | 179.8446
1034.176 | 179.9418
1035.176 | 179.8556
1036.176 | 180.1273
1037.176 | 180.5346
1038.176 | 180.4969
1039.176 | 180.4037
1040.176 | 181.015
1041.176 | 181.0117
1042.176 | 181.0637
1043.176 | 181.6227
1044.176 | 181.8353
1045.176 | 181.9155
1046.176 | 182.017
1047.176 | 181.8577
1048.176 | 181.7533
1049.176 | 181.9794
1050.176 | 182.1534
1051.176 | 182.1664
1052.176 | 182.2736
1053.176 | 182.2943
1054.176 | 182.3131
1055.176 | 182.2566
1056.176 | 181.8571
1057.176 | 181.673
1058.176 | 181.5223
1059.176 | 181.0601
1060.176 | 181.1563
1061.176 | 181.2355
1062.176 | 181.2272
1063.176 | 181.5346
1064.176 | 182.0849
1065.176 | 183.1097
1066.176 | 183.7402
1067.176 | 184.396
1068.176 | 185.2422
1069.176 | 184.8213
1070.176 | 185.0661
1071.1917 | 184.7299
1072.176 | 184.5685
1073.176 | 185.2633
1074.176 | 185.5576
1075.176 | 185.6378
1076.176 | 185.589
1077.176 | 185.5783
1078.176 | 185.3101
1079.176 | 186.2403
1080.176 | 186.185
1081.176 | 186.214
1082.176 | 186.4125
1083.176 | 186.3558
1084.176 | 186.2787
1085.176 | 186.2436
1086.176 | 185.6785
1087.176 | 186.3246
1088.176 | 186.593
1089.176 | 187.254
1090.176 | 186.9753
1091.176 | 186.9895
1092.176 | 187.3526
1093.176 | 186.9567
1094.176 | 186.9137
1095.176 | 186.6551
1096.176 | 186.0653
1097.176 | 185.97
1098.176 | 185.8619
1099.176 | 185.6425
1100.176 | 185.9895
1101.1917 | 186.0243
1102.176 | 186.161
1103.176 | 186.5097
1104.176 | 186.3204
1105.176 | 186.4151
1106.176 | 186.3215
1107.176 | 185.9077
1108.176 | 186.1919
1109.176 | 186.3915
1110.176 | 186.7371
1111.176 | 186.5682
1112.176 | 186.4655
1113.176 | 186.2995
1114.176 | 186.6675
1115.176 | 186.8522
1116.176 | 187.1426
1117.176 | 187.9012
1118.176 | 189.2302
1119.176 | 188.9845
1120.176 | 188.8158
1121.176 | 188.7708
1122.176 | 188.7736
1123.176 | 188.869
1124.176 | 189.6217
1125.176 | 190.2814
1126.176 | 190.436
1127.176 | 190.9701
1128.176 | 191.1736
1129.176 | 191.811
1130.176 | 191.9319
1131.176 | 191.9904
1132.176 | 192.4154
1133.176 | 192.2395
1134.176 | 192.3965
1135.176 | 192.4837
1136.176 | 192.9846
1137.176 | 193.4643
1138.176 | 193.5953
1139.176 | 193.7401
1140.176 | 193.2208
1141.176 | 193.1959
1142.176 | 192.9328
1143.176 | 193.2132
1144.176 | 193.0429
1145.176 | 192.9499
1146.176 | 193.0398
1147.176 | 193.2509
1148.176 | 192.9591
1149.176 | 193.8697
1150.176 | 193.8947
1151.176 | 194.1332
1152.176 | 194.3786
1153.176 | 194.6922
1154.176 | 194.9765
1155.176 | 194.5203
1156.176 | 194.3371
1157.176 | 194.6632
1158.176 | 194.045
1159.176 | 194.0287
1160.176 | 193.9192
1161.176 | 193.8894
1162.176 | 194.2074
1163.176 | 193.9585
1164.176 | 194.0002
1165.176 | 193.481
1166.176 | 193.1175
1167.176 | 193.0557
1168.176 | 193.2997
1169.176 | 193.6984
1170.176 | 193.7176
1171.176 | 193.7979
1172.176 | 194.0005
1173.176 | 194.5251
1174.176 | 194.3896
1175.176 | 194.6688
1176.176 | 194.5163
1177.176 | 194.3801
1178.176 | 194.0264
1179.176 | 194.065
1180.176 | 193.6188
1181.176 | 193.9189
1182.176 | 195.0765
1183.176 | 195.8374
1184.176 | 195.6099
1185.176 | 195.298
1186.176 | 195.1397
1187.176 | 195.3246
1188.176 | 195.0343
1189.176 | 195.1462
1190.176 | 195.1478
1191.1917 | 195.2741
1192.176 | 195.1569
1193.176 | 195.9149
1194.176 | 195.5772
1195.176 | 195.4098
1196.176 | 195.8272
1197.176 | 196.0982
1198.176 | 196.5538
1199.176 | 196.5721
1200.176 | 196.0284
1201.176 | 196.0548
1202.176 | 196.1849
1203.176 | 196.5992
1204.176 | 196.8225
1205.176 | 196.9329
1206.176 | 196.7704
1207.176 | 197.5596
1208.176 | 198.1774
1209.176 | 198.6391
1210.176 | 199.4231
1211.176 | 199.6404
1212.176 | 200.1447
1213.176 | 199.6865
1214.176 | 199.9504
1215.176 | 199.9537
1216.176 | 199.3912
1217.176 | 198.9905
1218.176 | 198.7016
1219.176 | 198.4154
1220.176 | 198.832
1221.176 | 199.0203
1222.176 | 198.3493
1223.176 | 198.2389
1224.176 | 198.2811
1225.176 | 198.0057
1226.176 | 198.019
1227.176 | 197.346
1228.176 | 197.2553
1229.176 | 197.6098
1230.176 | 197.6575
1231.176 | 198.06
1232.176 | 198.2963
1233.176 | 198.2701
1234.176 | 198.4405
1235.176 | 197.8186
1236.176 | 197.9241
1237.176 | 198.6128
1238.176 | 199.1728
1239.176 | 199.7387
1240.176 | 200.415
1241.176 | 201.7457
1242.176 | 201.8289
1243.176 | 202.0835
1244.176 | 201.995
1245.176 | 202.098
1246.176 | 202.0867
1247.176 | 202.6432
1248.176 | 202.6522
1249.176 | 203.1787
1250.176 | 203.3423
1251.176 | 202.9366
1252.176 | 202.7125
1253.176 | 202.2491
1254.176 | 202.0678
1255.176 | 201.8801
1256.176 | 202.2834
1257.176 | 201.9007
1258.176 | 201.2195
1259.176 | 201.0934
1260.176 | 200.9393
1261.176 | 201.1341
1262.176 | 201.3207
1263.176 | 200.477
1264.176 | 200.2407
1265.176 | 200.3039
1266.176 | 200.6167
1267.176 | 200.9217
1268.176 | 200.861
1269.176 | 200.9645
1270.176 | 200.3123
1271.176 | 200.3662
1272.176 | 200.5629
1273.176 | 200.5581
1274.176 | 200.5878
1275.176 | 200.3048
1276.176 | 200.1354
1277.176 | 200.577
1278.176 | 201.2984
1279.176 | 201.3835
1280.176 | 201.1741
1281.176 | 201.5806
1282.176 | 201.589
1283.176 | 201.4956
1284.176 | 201.4944
1285.176 | 201.4026
1286.176 | 201.3255
1287.176 | 200.9976
1288.176 | 201.5553
1289.176 | 201.3656
1290.176 | 201.9598
1291.176 | 202.1195
1292.176 | 201.8694
1293.176 | 201.7962
1294.176 | 202.2257
1295.176 | 201.798
1296.176 | 201.9779
1297.176 | 201.3199
1298.176 | 201.4516
1299.176 | 202.7994
1300.176 | 203.4403
1301.176 | 204.8131
1302.176 | 205.6984
1303.176 | 205.534
1304.176 | 205.3436
1305.176 | 204.793
1306.176 | 205.0241
1307.176 | 205.6095
1308.176 | 206.0896
1309.176 | 205.9462
1310.176 | 205.5601
1311.176 | 204.3482
1312.176 | 203.7164
1313.176 | 203.8431
1314.176 | 204.1422
1315.176 | 204.5654
1316.176 | 204.7959
1317.176 | 204.5494
1318.176 | 204.1863
1319.176 | 204.5306
1320.176 | 204.5634
1321.176 | 204.5241
1322.176 | 204.1449
1323.176 | 204.2171
1324.176 | 204.7243
1325.176 | 204.0381
1326.176 | 204.2546
1327.176 | 205.488
1328.176 | 206.1491
1329.176 | 205.8916
1330.176 | 206.4618
1331.176 | 206.3521
1332.176 | 206.4142
1333.176 | 206.7498
1334.176 | 206.4795
1335.176 | 206.5493
1336.176 | 206.7547
1337.176 | 207.2781
1338.176 | 207.73
1339.176 | 208.4941
1340.176 | 208.6998
1341.176 | 208.84
1342.176 | 209.2737
1343.176 | 209.4303
1344.176 | 209.3198
1345.176 | 209.3848
1346.176 | 209.2494
1347.176 | 209.4005
1348.176 | 209.1183
1349.176 | 209.2101
1350.176 | 208.7635
1351.176 | 208.9218
1352.176 | 209.0837
1353.176 | 208.0526
1354.176 | 207.8807
1355.176 | 208.0747
1356.176 | 208.4589
1357.176 | 208.5752
1358.176 | 209.607
1359.176 | 210.5275
1360.176 | 209.9361
1361.176 | 209.6728
1362.176 | 209.4263
1363.176 | 209.113
1364.176 | 208.9348
1365.176 | 208.5788
1366.176 | 208.398
1367.176 | 208.7436
1368.176 | 208.2498
1369.176 | 208.1134
1370.176 | 207.9684
1371.176 | 207.6326
1372.176 | 208.1113
1373.176 | 208.0913
1374.176 | 207.4489
1375.176 | 207.0405
1376.176 | 206.6073
1377.176 | 206.662
1378.176 | 206.4386
1379.176 | 206.6445
1380.176 | 206.5884
1381.176 | 206.9516
1382.176 | 207.013
1383.176 | 207.1433
1384.176 | 206.8439
1385.176 | 206.8844
1386.176 | 206.7441
1387.176 | 207.2693
1388.176 | 207.3741
1389.176 | 207.5641
1390.176 | 207.4515
1391.176 | 207.5153
1392.176 | 207.0808
1393.176 | 206.7036
1394.176 | 206.7929
1395.176 | 206.1841
1396.176 | 205.6972
1397.176 | 205.3447
1398.176 | 205.4706
1399.176 | 205.6155
1400.176 | 205.7948
1401.176 | 205.7639
1402.176 | 205.8176
1403.176 | 205.6339
1404.176 | 205.7868
1405.176 | 205.5914
1406.176 | 205.6907
1407.176 | 205.4486
1408.176 | 204.9865
1409.176 | 204.8006
1410.176 | 205.2806
1411.176 | 205.5456
1412.176 | 205.653
1413.176 | 205.5425
1414.176 | 205.253
1415.176 | 204.8807
1416.176 | 204.9707
1417.176 | 205.0259
1418.176 | 205.3641
1419.176 | 205.4255
1420.176 | 205.5291
1421.176 | 205.033
1422.176 | 205.0063
1423.176 | 204.8059
1424.176 | 205.0879
1425.176 | 205.1431
1426.176 | 205.0349
1427.176 | 204.9883
1428.176 | 205.0785
1429.176 | 204.9509
1430.176 | 205.2766
1431.176 | 205.0022
1432.176 | 204.9692
1433.176 | 204.9222
1434.176 | 204.5735
1435.176 | 204.6152
1436.176 | 204.3476
1437.176 | 204.0809
1438.176 | 204.4361
1439.176 | 204.9046
1440.176 | 204.6782
1441.176 | 204.2522
1442.1917 | 204.1078
1443.176 | 204.4747
1444.176 | 203.9669
1445.176 | 204.5394
1446.176 | 204.5052
1447.176 | 205.1242
1448.176 | 204.9658
1449.176 | 205.0942
1450.176 | 205.1054
1451.176 | 205.2333
1452.176 | 205.1104
1453.176 | 205.3751
1454.176 | 205.7941
1455.176 | 205.9253
1456.176 | 206.5093
1457.176 | 206.1419
1458.176 | 206.8826
1459.176 | 206.8644
1460.176 | 206.4725
1461.176 | 206.0738
1462.176 | 205.9651
1463.176 | 206.1494
1464.176 | 206.3584
1465.176 | 206.4551
1466.176 | 206.5208
1467.176 | 207.0347
1468.176 | 207.1441
1469.176 | 207.4703
1470.176 | 206.8827
1471.176 | 206.5574
1472.176 | 206.2638
1473.176 | 206.2509
1474.176 | 206.3692
1475.176 | 206.1172
1476.176 | 206.1385
1477.176 | 205.908
1478.176 | 206.4105
1479.176 | 206.6261
1480.176 | 206.4746
1481.176 | 206.3768
1482.176 | 206.1095
1483.176 | 205.867
1484.176 | 205.8003
1485.176 | 205.8742
1486.176 | 205.9957
1487.176 | 206.6668
1488.176 | 207.0421
1489.176 | 207.1358
1490.176 | 206.9183
1491.176 | 207.0113
1492.176 | 206.797
1493.176 | 206.8655
1494.176 | 207.234
1495.176 | 207.3628
1496.176 | 207.8673
1497.176 | 208.0178
1498.176 | 207.8275
1499.176 | 208.2334
1500.176 | 208.7608
1501.176 | 209.0642
1502.176 | 209.5406
1503.176 | 209.6869
1504.176 | 209.9423
1505.176 | 210.4111
1506.176 | 210.4321
1507.176 | 210.2361
1508.176 | 210.7632
1509.176 | 210.7217
1510.176 | 210.847
1511.176 | 210.7072
1512.176 | 211.2156
1513.176 | 211.9843
1514.176 | 212.6464
1515.176 | 213.6344
1516.176 | 214.4242
1517.176 | 214.5455
1518.176 | 214.5974
1519.176 | 214.671
1520.176 | 214.8605
1521.176 | 214.423
1522.176 | 214.6499
1523.176 | 215.3245
1524.176 | 215.3441
1525.176 | 215.2245
1526.176 | 215.3958
1527.176 | 214.8734
1528.176 | 215.3445
1529.176 | 216.0388
1530.176 | 216.2089
1531.176 | 217.0067
1532.176 | 217.9769
1533.176 | 217.7215
1534.176 | 217.6703
1535.176 | 218.3161
1536.176 | 217.8641
1537.176 | 217.7348
1538.176 | 217.1871
1539.176 | 217.16
1540.176 | 217.9795
1541.176 | 217.9345
1542.176 | 217.6528
1543.176 | 218.3625
1544.176 | 219.1824
1545.176 | 220.1749
1546.176 | 221.0856
1547.176 | 221.5093
1548.176 | 221.6609
1549.176 | 221.7294
1550.176 | 221.8978
1551.176 | 222.0581
1552.176 | 222.9476
1553.176 | 223.3116
1554.176 | 223.1157
1555.176 | 223.0744
1556.176 | 222.7213
1557.176 | 222.3946
1558.176 | 222.0944
1559.1917 | 222.0547
1560.176 | 221.944
1561.176 | 221.7946
1562.176 | 221.8129
1563.176 | 221.8143
1564.176 | 221.8932
1565.176 | 222.4048
1566.176 | 222.487
1567.176 | 222.8282
1568.176 | 223.1481
1569.176 | 223.0842
1570.176 | 222.9196
1571.176 | 222.7991
1572.176 | 222.9175
1573.176 | 223.1181
1574.176 | 223.0104
1575.176 | 222.5826
1576.176 | 222.7546
1577.176 | 222.816
1578.176 | 222.9986
1579.176 | 223.3329
1580.176 | 223.1734
1581.176 | 223.3042
1582.176 | 222.9393
1583.176 | 222.9206
1584.176 | 222.4512
1585.176 | 222.8232
1586.176 | 223.4659
1587.176 | 223.7848
1588.176 | 223.4559
1589.176 | 223.7542
1590.176 | 223.7047
1591.176 | 223.5308
1592.176 | 223.4469
1593.176 | 224.3537
1594.176 | 224.536
1595.176 | 224.6625
1596.176 | 225.227
1597.176 | 225.1431
1598.176 | 225.4634
1599.176 | 225.4087
1600.176 | 225.2229
1601.176 | 225.2307
1602.176 | 224.7513
1603.176 | 224.6641
1604.176 | 225.1217
1605.176 | 225.3499
1606.176 | 225.4021
1607.176 | 226.132
1608.176 | 226.706
1609.176 | 226.2243
1610.176 | 225.7896
1611.176 | 226.272
1612.176 | 226.1741
1613.176 | 226.2373
1614.176 | 226.0951
1615.176 | 225.9744
1616.176 | 225.6347
1617.176 | 225.3827
1618.176 | 225.4033
1619.176 | 225.3254
1620.176 | 225.6567
1621.176 | 225.9799
1622.176 | 225.7386
1623.176 | 226.1123
1624.176 | 226.2487
1625.176 | 225.9336
1626.176 | 226.3524
1627.176 | 225.8601
1628.176 | 226.0404
1629.176 | 226.0178
1630.176 | 226.0321
1631.176 | 226.1547
1632.176 | 226.2639
1633.176 | 226.9778
1634.176 | 227.4865
1635.176 | 227.5414
1636.176 | 228.473
1637.176 | 228.7421
1638.176 | 228.6744
1639.176 | 228.3838
1640.176 | 228.4118
1641.176 | 228.0848
1642.176 | 228.5935
1643.176 | 228.9902
1644.176 | 229.2234
1645.176 | 229.6755
1646.176 | 229.4856
1647.176 | 228.9781
1648.176 | 229.1796
1649.176 | 230.0029
1650.176 | 230.0172
1651.176 | 230.6188
1652.176 | 230.6229
1653.176 | 231.0322
1654.176 | 231.053
1655.176 | 231.3019
1656.176 | 230.9673
1657.176 | 230.7571
1658.176 | 231.5927
1659.176 | 231.1816
1660.176 | 231.0245
1661.176 | 231.1113
1662.176 | 231.5415
1663.176 | 231.1404
1664.176 | 230.8683
1665.176 | 231.0817
1666.176 | 230.8821
1667.176 | 230.9528
1668.176 | 230.8631
1669.176 | 230.0678
1670.176 | 229.6788
1671.176 | 229.3817
1672.176 | 229.4719
1673.176 | 229.3218
1674.176 | 229.0573
1675.176 | 229.121
1676.176 | 228.5764
1677.176 | 229.3022
1678.176 | 229.2099
1679.176 | 229.33
1680.176 | 230.343
1681.176 | 230.6035
1682.176 | 230.8781
1683.176 | 230.9834
1684.176 | 230.9994
1685.176 | 230.626
1686.176 | 229.9721
1687.176 | 229.6652
1688.176 | 229.3594
1689.176 | 228.7038
1690.176 | 228.7038
1691.176 | 228.5439
1692.176 | 228.1934
1693.176 | 227.9539
1694.176 | 227.9459
1695.176 | 227.6838
1696.176 | 227.5255
1697.176 | 227.4238
1698.176 | 227.7247
1699.176 | 227.6298
1700.176 | 227.3018
1701.176 | 227.0789
1702.176 | 227.1315
1703.176 | 226.9564
1704.176 | 226.65
1705.176 | 226.5785
1706.176 | 226.4786
1707.176 | 226.3522
1708.176 | 226.7302
1709.176 | 227.1146
1710.176 | 227.5523
1711.176 | 227.2878
1712.176 | 227.0601
1713.176 | 227.0594
1714.176 | 226.728
1715.176 | 226.2099
1716.176 | 226.3064
1717.176 | 226.7407
1718.176 | 226.3473
1719.176 | 226.5801
1720.176 | 226.3212
1721.176 | 226.3061
1722.176 | 226.9858
1723.176 | 226.4676
1724.176 | 226.459
1725.176 | 226.6088
1726.176 | 226.3758
1727.176 | 226.7577
1728.176 | 227.2648
1729.176 | 227.744
1730.176 | 227.6963
1731.176 | 228.0142
1732.176 | 228.0802
1733.176 | 228.2243
1734.176 | 228.5923
1735.176 | 228.563
1736.176 | 228.563
1737.176 | 228.5957
1738.176 | 228.7229
1739.176 | 228.5817
1740.176 | 228.0089
1741.176 | 227.446
1742.176 | 226.708
1743.176 | 226.1728
1744.176 | 225.7956
1745.176 | 225.6023
1746.176 | 225.5475
1747.176 | 225.7249
1748.176 | 226.1175
1749.176 | 226.5086
1750.176 | 227.2785
1751.176 | 226.8082
1752.176 | 226.6375
1753.176 | 226.4596
1754.176 | 226.7056
1755.176 | 226.915
1756.176 | 226.4558
1757.176 | 226.2999
1758.176 | 226.0432
1759.176 | 225.4542
1760.176 | 225.5452
1761.176 | 225.3617
1762.176 | 225.2696
1763.176 | 225.5557
1764.176 | 225.6023
1765.176 | 225.24
1766.176 | 225.5538
1767.176 | 225.4967
1768.176 | 225.1923
1769.176 | 225.3742
1770.176 | 225.2962
1771.176 | 225.3854
1772.176 | 225.3193
1773.176 | 225.7332
1774.176 | 225.7186
1775.176 | 225.6389
1776.176 | 225.3696
1777.176 | 225.456
1778.176 | 225.2135
1779.176 | 225.2909
1780.176 | 225.4421
1781.176 | 225.3976
1782.176 | 225.0841
1783.176 | 225.0189
1784.176 | 224.8202
1785.176 | 224.3428
1786.176 | 224.328
1787.176 | 224.5911
1788.176 | 224.506
1789.176 | 224.832
1790.176 | 224.7344
1791.176 | 225.2106
1792.176 | 225.2285
1793.176 | 225.3886
1794.176 | 225.5879
1795.176 | 225.6499
1796.176 | 226.2419
1797.176 | 227.0551
1798.176 | 227.4383
1799.176 | 228.5026
1800.176 | 228.0017
1801.176 | 227.9348
1802.1917 | 227.8492
1803.176 | 227.5122
1804.176 | 227.0564
1805.176 | 226.8455
1806.176 | 226.4697
1807.176 | 226.0329
1808.176 | 225.8632
1809.176 | 226.1063
1810.176 | 226.3296
1811.176 | 226.4776
1812.176 | 226.2153
1813.176 | 225.8982
1814.176 | 225.9949
1815.176 | 226.1686
1816.176 | 226.2678
1817.176 | 226.7913
1818.176 | 226.7931
1819.176 | 226.315
1820.176 | 226.0824
1821.176 | 226.5742
1822.176 | 226.4546
1823.176 | 226.2779
1824.176 | 226.1805
1825.176 | 226.1868
1826.176 | 226.5557
1827.176 | 226.6509
1828.176 | 226.195
1829.176 | 225.9198
1830.176 | 226.0264
1831.176 | 226.0456
1832.176 | 225.8832
1833.176 | 225.7222
1834.176 | 225.2954
1835.176 | 225.5671
1836.176 | 225.7982
1837.176 | 225.2388
1838.176 | 225.2193
1839.176 | 225.069
1840.176 | 224.6609
1841.176 | 224.5146
1842.176 | 224.3235
1843.176 | 224.2556
1844.176 | 224.6991
1845.176 | 224.47
1846.176 | 224.2511
1847.176 | 224.427
1848.176 | 224.6404
1849.176 | 224.5831
1850.176 | 225.1716
1851.176 | 225.0221
1852.176 | 224.9819
1853.176 | 224.5902
1854.176 | 224.3263
1855.176 | 224.5871
1856.176 | 224.3368
1857.176 | 224.2378
1858.176 | 224.4047
1859.176 | 224.1775
1860.176 | 224.0241
1861.176 | 223.9388
1862.176 | 223.8942
1863.176 | 224.148
1864.176 | 224.6313
1865.176 | 224.4809
1866.176 | 224.3628
1867.176 | 224.2998
1868.176 | 224.1298
1869.176 | 224.1265
1870.176 | 224.7894
1871.176 | 225.2718
1872.176 | 225.4744
1873.176 | 225.8383
1874.176 | 226.4761
1875.176 | 226.8262
1876.176 | 227.0126
1877.176 | 227.2249
1878.176 | 227.9891
1879.176 | 228.3794
1880.176 | 228.2293
1881.176 | 227.9736
1882.176 | 227.9075
1883.176 | 227.8049
1884.176 | 227.6601
1885.176 | 227.5557
1886.176 | 227.5849
1887.176 | 227.4599
1888.176 | 227.0678
1889.176 | 227.0059
1890.176 | 227.4561
1891.176 | 227.7904
1892.176 | 228.0999
1893.176 | 227.8835
1894.176 | 227.9617
1895.176 | 228.6186
1896.176 | 228.7301
1897.176 | 228.7318
1898.176 | 228.6518
1899.176 | 228.6211
1900.176 | 228.5266
1901.176 | 228.2253
1902.176 | 228.3711
1903.176 | 228.3982
1904.176 | 228.2334
1905.176 | 228.2042
1906.176 | 228.7139
1907.176 | 228.6674
1908.176 | 228.8362
1909.176 | 229.5558
1910.176 | 229.349
1911.176 | 229.725
1912.176 | 230.309
1913.176 | 229.9498
1914.176 | 230.1981
1915.176 | 230.3738
1916.176 | 230.2952
1917.176 | 229.9423
1918.176 | 229.5495
1919.176 | 229.5673
1920.176 | 229.5195
1921.176 | 228.7752
1922.1917 | 228.523
1923.176 | 228.1118
1924.176 | 228.0157
1925.176 | 228.1644
1926.176 | 228.1453
1927.176 | 228.9214
1928.176 | 229.0557
1929.176 | 229.4356
1930.176 | 228.9301
1931.176 | 228.8207
1932.176 | 228.9603
1933.176 | 228.9389
1934.176 | 229.2349
1935.176 | 228.8372
1936.176 | 229.0569
1937.176 | 229.4712
1938.176 | 229.8309
1939.176 | 229.4954
1940.176 | 229.2302
1941.176 | 228.9659
1942.176 | 228.7499
1943.176 | 229.1
1944.176 | 229.7045
1945.176 | 230.3603
1946.176 | 230.7991
1947.176 | 231.2428
1948.176 | 230.9247
1949.176 | 230.6764
1950.176 | 230.2396
1951.176 | 229.7351
1952.176 | 229.5145
1953.176 | 228.9899
1954.176 | 228.8615
1955.176 | 228.987
1956.176 | 229.3355
1957.176 | 229.6135
1958.176 | 229.1332
1959.176 | 228.7907
1960.176 | 229.0322
1961.176 | 229.7874
1962.176 | 229.6703
1963.176 | 229.7387
1964.176 | 229.7135
1965.176 | 230.109
1966.176 | 230.3809
1967.176 | 230.873
1968.176 | 230.427
1969.176 | 229.9447
1970.176 | 229.9916
1971.176 | 229.954
1972.176 | 229.9005
1973.176 | 229.7285
1974.176 | 230.4472
1975.176 | 230.1195
1976.176 | 230.158
1977.176 | 230.2592
1978.176 | 230.2921
1979.176 | 230.1942
1980.176 | 230.152
1981.176 | 229.742
1982.176 | 229.7041
1983.176 | 229.4652
1984.176 | 229.4288
1985.176 | 229.3014
1986.176 | 229.4848
1987.176 | 229.1722
1988.176 | 229.0291
1989.176 | 228.6454
1990.176 | 228.1805
1991.176 | 227.9675
1992.176 | 227.9094
1993.176 | 227.6806
1994.176 | 227.4679
1995.176 | 227.1971
1996.176 | 227.1501
1997.176 | 226.8779
1998.176 | 226.7743
1999.176 | 227.0688
2000.176 | 227.1597
2001.176 | 227.0569
2002.176 | 227.2504
2003.176 | 227.6092
2004.176 | 227.7344
2005.176 | 227.6935
2006.176 | 227.5781
2007.176 | 227.772
2008.176 | 228.3655
2009.176 | 228.8321
2010.176 | 228.5601
2011.176 | 228.5501
2012.176 | 228.262
2013.176 | 228.9729
2014.176 | 228.9929
2015.176 | 228.9616
2016.176 | 228.9766
2017.176 | 228.9868
2018.176 | 229.054
2019.176 | 228.6655
2020.176 | 228.7203
2021.176 | 228.3903
2022.176 | 228.5321
2023.176 | 228.4157
2024.176 | 228.2128
2025.176 | 228.2222
2026.176 | 228.3197
2027.176 | 228.4428
2028.176 | 228.717
2029.176 | 228.8818
2030.176 | 228.9112
2031.176 | 228.9085
2032.176 | 228.8887
2033.176 | 229.0925
2034.176 | 229.4843
2035.176 | 229.1172
2036.176 | 229.0165
2037.176 | 229.0782
2038.176 | 228.7776
2039.176 | 228.6194
2040.176 | 228.4911
2041.176 | 228.7586
2042.176 | 228.6271
2043.176 | 229.0997
2044.176 | 228.7432
2045.176 | 228.5221
2046.176 | 228.4252
2047.176 | 228.9046
2048.176 | 229.2636
2049.176 | 229.4708
2050.176 | 229.5354
2051.176 | 229.942
2052.176 | 229.8996
2053.176 | 229.7933
2054.176 | 229.7231
2055.176 | 229.4351
2056.176 | 229.0441
2057.176 | 228.7182
2058.176 | 228.7284
2059.176 | 228.4321
2060.176 | 228.2488
2061.176 | 228.4031
2062.1917 | 228.558
2063.176 | 228.5012
2064.176 | 228.4618
2065.176 | 229.0995
2066.176 | 229.2371
2067.176 | 229.2263
2068.176 | 228.7774
2069.176 | 228.8443
2070.176 | 228.9111
2071.176 | 229.1064
2072.176 | 229.2115
2073.176 | 229.1197
2074.176 | 229.1358
2075.176 | 228.8911
2076.176 | 228.9853
2077.176 | 229.028
2078.176 | 229.319
2079.176 | 229.3678
2080.176 | 229.8393
2081.176 | 229.8766
2082.176 | 229.7856
2083.176 | 229.743
2084.176 | 229.6731
2085.176 | 230.1382
2086.176 | 230.8429
2087.176 | 231.0925
2088.176 | 231.3385
2089.176 | 231.4586
2090.176 | 231.3528
2091.176 | 231.3308
2092.176 | 230.9853
2093.176 | 230.79
2094.176 | 230.6052
2095.176 | 230.2249
2096.176 | 230.0231
2097.176 | 229.9081
2098.176 | 229.6686
2099.176 | 229.2702
2100.176 | 229.8095
2101.176 | 229.717
2102.176 | 230.0231
2103.176 | 230.5663
2104.176 | 230.5234
2105.176 | 230.7561
2106.176 | 231.0434
2107.176 | 231.2685
2108.176 | 230.984
2109.176 | 230.9475
2110.176 | 231.1328
2111.176 | 231.5307
2112.176 | 231.9072
2113.176 | 232.1093
2114.176 | 232.2138
2115.176 | 232.4733
2116.176 | 233.0484
2117.176 | 233.5883
2118.176 | 233.208
2119.176 | 233.2823
2120.176 | 233.1871
2121.176 | 232.9233
2122.176 | 233.0526
2123.176 | 232.912
2124.176 | 233.0345
2125.176 | 233.0079
2126.176 | 233.1102
2127.176 | 233.1609
2128.176 | 232.8065
2129.176 | 232.6379
2130.176 | 232.3938
2131.176 | 231.9777
2132.176 | 231.5763
2133.176 | 231.8448
2134.176 | 231.2799
2135.176 | 231.6409
2136.176 | 232.2776
2137.176 | 232.6333
2138.176 | 232.7782
2139.176 | 232.8538
2140.176 | 233.1326
2141.176 | 233.2216
2142.176 | 232.8218
2143.176 | 232.4371
2144.176 | 232.2409
2145.176 | 232.0876
2146.176 | 231.9754
2147.176 | 231.7821
2148.176 | 231.7928
2149.176 | 232.0341
2150.176 | 231.5997
2151.176 | 231.4681
2152.176 | 230.9811
2153.176 | 230.9806
2154.176 | 230.5487
2155.176 | 230.3431
2156.176 | 230.1471
2157.176 | 229.9286
2158.176 | 229.6421
2159.176 | 229.5284
2160.176 | 229.5071
2161.176 | 229.2421
2162.176 | 229.021
2163.176 | 229.0727
2164.176 | 229.3253
2165.176 | 229.3767
2166.176 | 229.0837
2167.176 | 229.0154
2168.176 | 228.9701
2169.176 | 228.5695
2170.176 | 228.1922
2171.176 | 228.1343
2172.176 | 227.9556
2173.176 | 227.834
2174.176 | 228.0195
2175.176 | 228.2292
2176.176 | 228.0742
2177.176 | 227.9095
2178.176 | 227.7225
2179.176 | 227.8967
2180.176 | 227.9
2181.176 | 227.6733
2182.176 | 227.6207
2183.176 | 227.5859
2184.176 | 227.8541
2185.176 | 228.2528
2186.176 | 228.3089
2187.176 | 228.3893
2188.176 | 228.3694
2189.176 | 228.6368
2190.176 | 228.8725
2191.176 | 229.1874
2192.176 | 229.3008
2193.176 | 229.6968
2194.176 | 229.6864
2195.176 | 229.9984
2196.176 | 230.9504
2197.176 | 230.6585
2198.176 | 230.5383
2199.176 | 230.2892
2200.176 | 230.248
2201.176 | 230.0563
2202.176 | 229.9254
2203.176 | 229.5978
2204.176 | 229.3058
2205.176 | 229.564
2206.176 | 229.5871
2207.176 | 229.7261
2208.176 | 229.7094
2209.176 | 230.0096
2210.176 | 229.9197
2211.176 | 230.4873
2212.1917 | 230.6388
2213.176 | 230.5868
2214.176 | 230.3739
2215.176 | 229.9867
2216.176 | 229.6631
2217.176 | 229.253
2218.176 | 228.9145
2219.176 | 228.6658
2220.176 | 228.2977
2221.176 | 228.112
2222.176 | 227.758
2223.176 | 227.8224
2224.176 | 228.0203
2225.176 | 228.1357
2226.176 | 228.1672
2227.176 | 228.0117
2228.176 | 227.8074
2229.176 | 227.2589
2230.176 | 227.4292
2231.176 | 227.3276
2232.176 | 227.6554
2233.176 | 227.7957
2234.176 | 227.6622
2235.176 | 228.0557
2236.176 | 228.1562
2237.176 | 228.0125
2238.176 | 227.8122
2239.176 | 227.8926
2240.176 | 227.9823
2241.176 | 228.0315
2242.176 | 227.7849
2243.176 | 228.1403
2244.176 | 228.387
2245.176 | 228.4498
2246.176 | 228.6456
2247.176 | 228.4934
2248.176 | 228.1369
2249.176 | 228.1843
2250.176 | 228.0412
2251.176 | 227.7252
2252.176 | 227.664
2253.176 | 227.6738
2254.176 | 227.7151
2255.176 | 227.6882
2256.176 | 227.8281
2257.176 | 227.4773
2258.176 | 227.239
2259.176 | 227.6808
2260.176 | 227.7056
2261.176 | 227.4847
2262.176 | 227.6222
2263.176 | 227.5612
2264.176 | 227.3798
2265.176 | 227.2319
2266.176 | 227.673
2267.176 | 227.8114
2268.176 | 227.8167
2269.176 | 227.8132
2270.176 | 227.9146
2271.176 | 228.0964
2272.1917 | 228.1123
2273.176 | 228.0334
2274.176 | 227.7233
2275.176 | 227.3979
2276.176 | 227.4133
2277.176 | 227.6692
2278.176 | 227.5104
2279.176 | 227.4878
2280.176 | 227.4085
2281.176 | 227.5955
2282.176 | 227.4149
2283.176 | 227.5572
2284.176 | 227.6431
2285.176 | 227.4686
2286.176 | 227.2864
2287.176 | 227.181
2288.176 | 227.3005
2289.176 | 227.5916
2290.176 | 227.7848
2291.176 | 227.8692
2292.176 | 227.6785
2293.176 | 227.8255
2294.176 | 228.0081
2295.176 | 228.281
2296.176 | 228.2744
2297.176 | 228.1228
2298.176 | 227.9051
2299.176 | 228.0137
2300.176 | 228.3255
2301.176 | 228.542
2302.176 | 228.6052
2303.176 | 228.6177
2304.176 | 228.262
2305.176 | 228.7663
2306.176 | 229.0246
2307.176 | 229.206
2308.176 | 229.3088
2309.176 | 229.3705
2310.176 | 229.4978
2311.176 | 229.6077
2312.176 | 229.3349
2313.176 | 229.0823
2314.176 | 229.0032
2315.176 | 229.2953
2316.176 | 229.2427
2317.176 | 229.383
2318.176 | 229.4312
2319.176 | 229.4407
2320.176 | 229.4914
2321.176 | 229.2817
2322.176 | 229.0708
2323.176 | 229.0904
2324.176 | 229.0767
2325.176 | 228.969
2326.176 | 228.925
2327.176 | 228.9657
2328.176 | 228.8507
2329.176 | 228.9199
2330.176 | 228.7305
2331.176 | 228.7298
2332.176 | 228.8093
2333.176 | 228.8052
2334.176 | 228.5168
2335.176 | 228.1353
2336.176 | 228.0873
2337.176 | 227.8532
2338.176 | 227.9442
2339.176 | 228.0935
2340.176 | 227.7178
2341.176 | 227.3327
2342.176 | 226.9644
2343.176 | 227.0359
2344.176 | 227.015
2345.176 | 226.945
2346.1917 | 226.7332
2347.1917 | 226.9742
2348.176 | 227.1627
2349.176 | 227.331
2350.176 | 227.1685
2351.176 | 227.6834
2352.176 | 228.4354
2353.176 | 228.5118
2354.176 | 228.4411
2355.176 | 228.4089
2356.176 | 228.0126
2357.176 | 227.8995
2358.176 | 227.8465
2359.176 | 227.4121
2360.176 | 227.3904
2361.176 | 227.4725
2362.176 | 227.5474
2363.176 | 227.7148
2364.176 | 227.6384
2365.176 | 227.4492
2366.176 | 227.3504
2367.176 | 227.5245
2368.176 | 227.7889
2369.176 | 228.3071
2370.176 | 228.1765
2371.176 | 227.601
2372.176 | 227.6372
2373.176 | 227.7642
2374.176 | 228.4579
2375.176 | 228.5276
2376.176 | 228.8002
2377.176 | 228.6779
2378.176 | 228.6686
2379.176 | 228.5256
2380.176 | 228.4432
2381.176 | 228.611
2382.176 | 228.8133
2383.176 | 229.0403
2384.176 | 229.0164
2385.176 | 228.8525
2386.176 | 228.5269
2387.176 | 228.5012
2388.176 | 228.4836
2389.176 | 228.3316
2390.176 | 228.3599
2391.176 | 228.2909
2392.176 | 228.8461
2393.176 | 229.4021
2394.176 | 229.1278
2395.176 | 229.1676
2396.176 | 228.928
2397.176 | 228.7443
2398.176 | 228.6854
2399.176 | 228.6985
2400.176 | 228.6389
2401.176 | 228.4498
2402.176 | 228.5286
2403.176 | 228.4303
2404.176 | 228.2454
2405.176 | 227.7469
2406.176 | 227.6355
2407.176 | 227.2997
2408.176 | 227.0146
2409.176 | 226.8556
2410.176 | 226.5973
2411.176 | 226.3879
2412.176 | 226.2971
2413.176 | 226.6018
2414.176 | 226.6303
2415.176 | 226.7412
2416.176 | 226.9577
2417.176 | 226.6769
2418.176 | 226.3823
2419.176 | 226.353
2420.176 | 226.3791
2421.176 | 226.4142
2422.176 | 226.3473
2423.176 | 226.8078
2424.176 | 226.7874
2425.176 | 227.6358
2426.176 | 227.6703
2427.176 | 227.9626
2428.176 | 228.085
2429.176 | 228.0858
2430.176 | 227.8246
2431.176 | 227.8891
2432.176 | 227.9585
2433.176 | 228.1855
2434.176 | 228.7485
2435.176 | 228.6869
2436.176 | 228.9183
2437.176 | 228.644
2438.176 | 228.3019
2439.176 | 228.1237
2440.176 | 227.6018
2441.176 | 227.5828
2442.176 | 227.3998
2443.176 | 227.1939
2444.176 | 226.999
2445.176 | 226.7707
2446.176 | 226.67
2447.176 | 226.3996
2448.176 | 226.291
2449.176 | 226.4255
2450.176 | 226.6422
2451.176 | 227.2392
2452.176 | 227.2717
2453.176 | 227.4102
2454.176 | 227.918
2455.176 | 228.3009
2456.176 | 228.4143
2457.176 | 228.6274
2458.176 | 229.1185
2459.176 | 229.3687
2460.176 | 229.7896
2461.176 | 230.2704
2462.176 | 230.564
2463.176 | 230.458
2464.176 | 230.6327
2465.176 | 230.6773
2466.176 | 231.1944
2467.176 | 231.1555
2468.176 | 230.97
2469.176 | 230.8878
2470.176 | 230.7367
2471.176 | 230.8111
2472.176 | 230.5754
2473.176 | 230.2704
2474.176 | 230.1128
2475.176 | 230.0589
2476.176 | 229.6387
2477.176 | 229.4321
2478.176 | 229.2157
2479.176 | 229.0358
2480.176 | 229.0634
2481.176 | 228.8408
2482.176 | 228.8635
2483.176 | 229.0652
2484.176 | 229.1471
2485.176 | 229.0804
2486.176 | 229.3253
2487.176 | 229.9031
2488.176 | 229.5599
2489.176 | 229.5384
2490.176 | 229.4877
2491.176 | 229.6437
2492.176 | 229.5533
2493.176 | 229.6058
2494.176 | 229.4782
2495.176 | 229.2978
2496.176 | 229.2909
2497.176 | 229.3115
2498.176 | 229.1796
2499.176 | 229.2603
2500.176 | 229.3029
2501.176 | 229.368
2502.176 | 229.2288
2503.176 | 229.5582
2504.176 | 229.2351
2505.176 | 229.2724
2506.176 | 229.4168
2507.176 | 229.2643
2508.176 | 229.0808
2509.176 | 229.1407
2510.176 | 229.1348
2511.176 | 229.1406
2512.176 | 229.3823
2513.176 | 229.9352
2514.176 | 230.0304
2515.176 | 229.8566
2516.176 | 229.5441
2517.176 | 229.2267
2518.176 | 228.9263
2519.176 | 229.0399
2520.176 | 229.0743
2521.176 | 229.213
2522.176 | 229.1674
2523.176 | 229.0274
2524.176 | 229.0465
2525.176 | 229.1463
2526.176 | 228.9259
2527.176 | 229.0936
2528.176 | 229.1185
2529.176 | 229.4276
2530.176 | 229.6206
2531.176 | 229.457
2532.176 | 229.181
2533.176 | 229.016
2534.176 | 229.0491
2535.176 | 229.0581
2536.176 | 229.174
2537.176 | 229.0992
2538.176 | 229.0198
2539.176 | 228.8848
2540.176 | 228.7543
2541.176 | 228.6917
2542.176 | 228.5853
2543.176 | 228.5868
2544.176 | 228.8363
2545.176 | 229.1616
2546.176 | 229.0715
2547.176 | 229.3268
2548.176 | 229.7059
2549.176 | 230.7897
2550.176 | 230.861
2551.176 | 231.079
2552.176 | 230.8903
2553.176 | 230.5134
2554.176 | 230.7044
2555.176 | 230.6373
2556.176 | 230.6552
2557.176 | 230.6134
2558.176 | 230.6995
2559.176 | 230.75
2560.176 | 230.7553
2561.176 | 230.9356
2562.176 | 231.3898
2563.176 | 231.3254
2564.176 | 231.7882
2565.176 | 231.9614
2566.176 | 231.771
2567.176 | 231.6975
2568.176 | 231.6316
2569.176 | 231.565
2570.176 | 231.366
2571.176 | 231.2513
2572.176 | 231.2879
2573.176 | 231.0539
2574.176 | 230.9904
2575.176 | 231.2505
2576.176 | 230.9566
2577.176 | 230.8392
2578.176 | 230.6831
2579.176 | 230.6693
2580.176 | 230.6446
2581.176 | 230.7665
2582.176 | 230.6969
2583.176 | 230.8939
2584.176 | 231.0152
2585.176 | 231.1748
2586.176 | 231.2125
2587.176 | 231.0425
2588.176 | 231.1093
2589.176 | 231.0953
2590.176 | 231.2167
2591.176 | 231.5235
2592.176 | 231.3975
2593.176 | 231.4101
2594.176 | 231.5249
2595.176 | 231.3668
2596.176 | 231.0673
2597.176 | 230.6395
2598.176 | 230.4525
2599.176 | 230.4071
2600.176 | 230.1193
2601.176 | 230.0274
2602.176 | 229.9193
2603.176 | 230.0392
2604.176 | 229.8152
2605.176 | 229.5932
2606.176 | 229.4265
2607.176 | 229.2626
2608.176 | 229.0266
2609.176 | 228.9892
2610.176 | 228.8489
2611.176 | 228.6684
2612.176 | 228.7625
2613.176 | 228.9171
2614.176 | 228.9004
2615.176 | 228.9591
2616.176 | 228.8991
2617.176 | 228.8169
2618.176 | 229.1091
2619.176 | 229.2829
2620.176 | 229.1278
2621.176 | 229.1257
2622.176 | 229.2322
2623.176 | 229.2275
2624.176 | 229.3047
2625.176 | 229.3801
2626.176 | 229.2678
2627.176 | 229.636
2628.176 | 229.6421
2629.176 | 229.6113
2630.176 | 229.709
2631.176 | 229.4416
2632.176 | 229.3897
2633.176 | 229.3253
2634.176 | 229.8211
2635.176 | 230.0117
2636.176 | 229.9059
2637.176 | 229.7739
2638.176 | 229.8616
2639.176 | 229.7239
2640.176 | 229.6899
2641.176 | 229.7762
2642.176 | 230.5007
2643.176 | 230.468
2644.176 | 230.5632
2645.176 | 230.5966
2646.176 | 230.3315
2647.176 | 230.4466
2648.176 | 230.339
2649.176 | 230.5259
2650.176 | 230.7362
2651.176 | 230.9029
2652.176 | 231.1894
2653.176 | 231.3311
2654.176 | 231.1944
2655.176 | 231.144
2656.176 | 230.9829
2657.176 | 230.85
2658.176 | 230.6563
2659.176 | 230.5374
2660.176 | 230.4574
2661.176 | 230.1658
2662.176 | 230.0836
2663.176 | 229.8302
2664.176 | 229.6344
2665.176 | 229.677
2666.176 | 229.8455
2667.176 | 229.9087
2668.176 | 229.7003
2669.176 | 229.6089
2670.176 | 229.5775
2671.176 | 229.5064
2672.176 | 229.4288
2673.176 | 229.2929
2674.176 | 229.2334
2675.176 | 229.0194
2676.176 | 228.9546
2677.176 | 229.131
2678.176 | 229.1919
2679.176 | 228.9272
2680.176 | 228.5105
2681.176 | 228.0633
2682.176 | 227.9287
2683.176 | 228.0749
2684.176 | 228.0747
2685.176 | 228.1066
2686.176 | 228.163
2687.176 | 228.1952
2688.176 | 228.0838
2689.176 | 228.0187
2690.176 | 227.7362
2691.176 | 227.2281
2692.176 | 226.8318
2693.176 | 226.9848
2694.176 | 227.3497
2695.176 | 227.2785
2696.176 | 227.3331
2697.176 | 227.4544
2698.176 | 227.602
2699.176 | 228.1833
2700.176 | 228.176
2701.176 | 228.1689
2702.176 | 228.4808
2703.176 | 228.6143
2704.176 | 228.743
2705.176 | 228.8246
2706.176 | 229.0577
2707.176 | 228.778
2708.176 | 228.6337
2709.176 | 228.617
2710.176 | 228.9907
2711.176 | 229.0292
2712.176 | 229.038
2713.176 | 228.7546
2714.176 | 228.8968
2715.176 | 229.0193
2716.176 | 229.4534
2717.176 | 229.403
2718.176 | 229.4611
2719.176 | 229.3935
2720.176 | 229.1774
2721.176 | 229.1468
2722.176 | 229.058
2723.176 | 229.079
2724.176 | 229.4403
2725.176 | 229.5415
2726.176 | 229.6524
2727.176 | 229.266
2728.176 | 229.0859
2729.176 | 228.9279
2730.176 | 228.9751
2731.176 | 229.268
2732.176 | 229.3504
2733.176 | 229.2159
2734.176 | 229.1529
2735.176 | 229.0992
2736.176 | 229.1477
2737.176 | 229.2215
2738.176 | 229.1628
2739.176 | 229.1255
2740.176 | 228.9745
2741.176 | 229.1152
2742.176 | 229.1387
2743.176 | 229.0995
2744.176 | 229.1992
2745.176 | 229.3284
2746.176 | 229.6434
2747.176 | 229.7625
2748.176 | 229.9075
2749.176 | 229.9898
2750.176 | 229.9309
2751.176 | 229.8509
2752.176 | 230.0888
2753.176 | 229.8561
2754.176 | 229.9039
2755.176 | 229.9101
2756.176 | 229.9394
2757.176 | 230.1509
2758.176 | 230.05
2759.176 | 229.6704
2760.176 | 229.5842
2761.176 | 229.5088
2762.176 | 229.291
2763.176 | 229.1743
2764.176 | 229.2327
2765.176 | 229.3792
2766.176 | 229.4198
2767.176 | 229.2728
2768.176 | 229.4019
2769.176 | 229.5945
2770.176 | 229.3882
2771.176 | 229.1
2772.176 | 229.1865
2773.176 | 229.4803
2774.176 | 229.5664
2775.176 | 229.5222
2776.176 | 229.5721
2777.176 | 229.5715
2778.176 | 230.172
2779.176 | 230.5889
2780.176 | 230.6593
2781.176 | 230.8296
2782.176 | 230.669
2783.176 | 230.0832
2784.176 | 230.1144
2785.176 | 230.0215
2786.176 | 230.146
2787.176 | 230.0742
2788.176 | 229.8935
2789.176 | 230.1703
2790.176 | 230.2801
2791.176 | 230.2699
2792.176 | 230.1672
2793.176 | 230.1641
2794.176 | 230.112
2795.176 | 230.2432
2796.176 | 230.378
2797.176 | 230.5774
2798.176 | 230.8376
2799.176 | 231.1298
2800.176 | 231.3871
2801.176 | 231.5321
2802.176 | 231.4932
2803.176 | 231.518
2804.176 | 231.4891
2805.176 | 231.5606
2806.176 | 231.6605
2807.176 | 231.6225
2808.176 | 231.3375
2809.176 | 231.2224
2810.176 | 231.3512
2811.176 | 231.8248
2812.176 | 231.9875
2813.176 | 232.0789
2814.176 | 232.1049
2815.176 | 231.6608
2816.176 | 231.5191
2817.176 | 231.5139
2818.176 | 231.5763
2819.176 | 231.533
2820.176 | 231.6081
2821.176 | 231.6526
2822.176 | 231.6583
2823.176 | 231.6178
2824.176 | 231.6082
2825.176 | 231.715
2826.176 | 232.0541
2827.176 | 232.3032
2828.176 | 232.7274
2829.176 | 233.1993
2830.176 | 233.5196
2831.176 | 233.4203
2832.176 | 233.3005
2833.176 | 233.4259
2834.176 | 233.4489
2835.176 | 233.3773
2836.176 | 233.7288
2837.176 | 234.0615
2838.176 | 234.6461
2839.176 | 234.992
2840.176 | 235.485
2841.176 | 235.7028
2842.176 | 235.7273
2843.176 | 235.8627
2844.176 | 235.7332
2845.176 | 235.2678
2846.176 | 235.1204
2847.176 | 235.1325
2848.176 | 235.0492
2849.176 | 234.8275
2850.176 | 234.3749
2851.176 | 234.2628
2852.176 | 234.6358
2853.176 | 234.8806
2854.176 | 234.6152
2855.176 | 234.343
2856.176 | 233.9234
2857.176 | 233.5477
2858.176 | 233.3499
2859.176 | 233.1309
2860.176 | 233.0053
2861.176 | 232.4948
2862.176 | 232.5876
2863.176 | 232.482
2864.176 | 232.7671
2865.176 | 232.906
2866.176 | 233.3266
2867.176 | 233.3902
2868.176 | 233.3119
2869.176 | 233.3051
2870.176 | 233.9233
2871.176 | 233.9388
2872.176 | 233.7782
2873.176 | 233.2938
2874.176 | 232.7158
2875.176 | 232.3236
2876.176 | 232.5274
2877.176 | 232.497
2878.176 | 232.4732
2879.176 | 232.5111
2880.176 | 232.8989
2881.176 | 232.9765
2882.176 | 233.1221
2883.176 | 233.2849
2884.176 | 233.9735
2885.176 | 233.9204
2886.176 | 234.2858
2887.176 | 234.4376
2888.176 | 234.4218
2889.176 | 234.1081
2890.176 | 234.2232
2891.176 | 234.1817
2892.176 | 233.9696
2893.176 | 233.748
2894.176 | 233.7034
2895.176 | 233.4715
2896.176 | 233.3456
2897.176 | 233.3531
2898.176 | 233.4605
2899.176 | 233.6146
2900.176 | 233.7762
2901.176 | 233.8202
2902.176 | 233.6378
2903.176 | 233.7409
2904.176 | 234.0657
2905.176 | 234.13
2906.176 | 234.3458
2907.176 | 234.7935
2908.176 | 234.9287
2909.176 | 234.7388
2910.176 | 234.5216
2911.176 | 234.7181
2912.176 | 234.8167
2913.176 | 235.0258
2914.176 | 235.0873
2915.176 | 234.9418
2916.176 | 234.9455
2917.176 | 235.107
2918.176 | 235.3619
2919.176 | 235.5159
2920.176 | 235.5938
2921.176 | 235.4081
2922.176 | 235.4004
2923.176 | 235.4711
2924.176 | 235.2114
2925.176 | 235.0111
2926.176 | 235.5236
2927.176 | 235.2535
2928.176 | 234.9997
2929.176 | 234.8898
2930.176 | 234.852
2931.176 | 234.6789
2932.176 | 234.5937
2933.176 | 234.4923
2934.176 | 234.4777
2935.176 | 234.4584
2936.176 | 234.4137
2937.176 | 234.2271
2938.176 | 234.316
2939.176 | 234.2581
2940.176 | 234.383
2941.176 | 234.0024
2942.176 | 233.7833
2943.176 | 233.8172
2944.176 | 233.618
2945.176 | 233.4465
2946.176 | 233.4075
2947.176 | 233.4558
2948.176 | 233.5086
2949.176 | 233.5928
2950.176 | 233.6806
2951.176 | 233.4425
2952.176 | 233.2836
2953.176 | 233.725
2954.176 | 234.1718
2955.176 | 234.0469
2956.176 | 233.7962
2957.176 | 233.7104
2958.176 | 233.6477
2959.176 | 233.5664
2960.176 | 232.906
2961.176 | 232.8365
2962.176 | 232.4692
2963.176 | 232.6126
2964.176 | 232.598
2965.176 | 232.527
2966.176 | 232.6855
2967.176 | 233.1257
2968.176 | 233.441
2969.176 | 233.3584
2970.176 | 233.3074
2971.176 | 233.2086
2972.176 | 233.0488
2973.176 | 232.8466
2974.176 | 232.7638
2975.1917 | 232.9027
2976.1917 | 233.8636
2977.176 | 234.3291
2978.176 | 234.9248
2979.176 | 234.8019
2980.176 | 234.7095
2981.176 | 234.7997
2982.176 | 234.8403
2983.1917 | 234.6814
2984.1917 | 234.5216
2985.1917 | 234.2742
2986.176 | 234.1199
2987.176 | 234.1569
2988.176 | 234.0318
2989.176 | 233.9282
2990.176 | 233.7525
2991.176 | 233.3814
2992.176 | 233.3389
2993.176 | 232.8988
2994.176 | 232.432
2995.176 | 232.276
2996.176 | 232.291
2997.176 | 232.3844
2998.176 | 232.356
2999.176 | 232.3312
3000.176 | 232.518
3001.176 | 232.5493
3002.176 | 232.4721
3003.176 | 232.4737
3004.176 | 232.4843
3005.176 | 232.4566
3006.176 | 232.446
3007.176 | 232.2681
3008.176 | 232.192
3009.176 | 232.301
3010.176 | 232.3192
3011.176 | 232.32
3012.176 | 232.3427
3013.176 | 232.5925
3014.176 | 232.6499
3015.176 | 232.7588
3016.176 | 232.5368
3017.176 | 232.5931
3018.176 | 232.9417
3019.176 | 233.3537
3020.176 | 233.3836
3021.176 | 233.3963
3022.176 | 233.5345
3023.176 | 233.5965
3024.176 | 233.814
3025.176 | 233.6788
3026.176 | 233.6935
3027.176 | 233.6768
3028.176 | 233.8712
3029.176 | 234.0603
3030.176 | 233.9811
3031.176 | 233.5564
3032.176 | 233.5653
3033.176 | 233.824
3034.176 | 233.7513
3035.176 | 233.7637
3036.176 | 233.5925
3037.176 | 233.6699
3038.176 | 233.5352
3039.176 | 233.5456
3040.176 | 233.549
3041.176 | 233.7171
3042.176 | 233.5803
3043.176 | 233.6273
3044.176 | 233.4553
3045.176 | 233.2821
3046.176 | 233.324
3047.176 | 233.5575
3048.176 | 233.7385
3049.176 | 233.6846
3050.176 | 233.59
3051.176 | 233.6379
3052.176 | 233.8745
3053.176 | 233.9444
3054.176 | 233.9551
3055.176 | 233.8668
3056.176 | 233.8883
3057.176 | 233.909
3058.176 | 233.9193
3059.176 | 233.9382
3060.176 | 234.0622
3061.176 | 233.8692
3062.176 | 233.6843
3063.176 | 233.5086
3064.176 | 233.5655
3065.176 | 233.5986
3066.176 | 233.6678
3067.176 | 233.6935
3068.176 | 233.731
3069.176 | 233.7728
3070.176 | 233.7015
3071.176 | 233.4965
3072.176 | 233.6539
3073.176 | 233.513
3074.176 | 233.5998
3075.176 | 233.768
3076.176 | 233.8241
3077.176 | 234.0176
3078.176 | 234.3248
3079.176 | 234.4996
3080.176 | 234.8843
3081.176 | 235.0979
3082.176 | 235.3666
3083.176 | 235.3831
3084.176 | 235.6023
3085.176 | 235.9542
3086.176 | 236.1479
3087.176 | 236.1118
3088.176 | 235.9403
3089.176 | 235.7951
3090.176 | 235.6792
3091.176 | 235.887
3092.176 | 235.8287
3093.176 | 235.6476
3094.176 | 235.3309
3095.176 | 235.3342
3096.176 | 235.2988
3097.176 | 235.4099
3098.176 | 235.324
3099.176 | 235.2339
3100.176 | 234.9501
3101.176 | 234.8878
3102.176 | 234.8615
3103.176 | 234.8429
3104.176 | 234.9827
3105.176 | 235.0555
3106.176 | 234.8567
3107.176 | 234.9207
3108.176 | 234.9701
3109.176 | 235.0369
3110.176 | 235.1785
3111.176 | 235.4224
3112.176 | 235.347
3113.176 | 235.3787
3114.176 | 235.2599
3115.176 | 235.0945
3116.176 | 235.6077
3117.176 | 235.952
3118.176 | 235.4268
3119.176 | 235.5667
3120.176 | 235.3116
3121.176 | 234.9473
3122.176 | 234.7723
3123.176 | 234.6831
3124.176 | 234.581
3125.176 | 234.469
3126.176 | 234.3774
3127.176 | 234.7005
3128.176 | 234.6412
3129.176 | 234.9818
3130.176 | 235.1608
3131.176 | 235.5023
3132.176 | 235.3499
3133.176 | 235.1428
3134.176 | 235.1038
3135.176 | 235.1883
3136.176 | 235.1076
3137.176 | 235.0398
3138.176 | 234.7788
3139.176 | 234.9087
3140.176 | 234.8435
3141.176 | 234.5834
3142.176 | 234.181
3143.1917 | 234.2686
3144.176 | 234.1528
3145.176 | 234.1237
3146.176 | 233.9488
3147.176 | 233.494
3148.176 | 233.3526
3149.176 | 233.817
3150.176 | 233.716
3151.176 | 233.7615
3152.176 | 233.7417
3153.176 | 233.5637
3154.176 | 233.4657
3155.176 | 233.4073
3156.176 | 233.1834
3157.176 | 233.2574
3158.176 | 233.2384
3159.176 | 233.4209
3160.176 | 233.4777
3161.176 | 233.6351
3162.176 | 233.81
3163.176 | 234.0477
3164.176 | 234.3383
3165.176 | 234.8455
3166.176 | 234.9224
3167.176 | 234.8303
3168.176 | 234.7381
3169.176 | 234.5425
3170.176 | 234.4767
3171.176 | 234.4922
3172.176 | 234.384
3173.1917 | 233.916
3174.176 | 234.1529
3175.176 | 234.0883
3176.176 | 234.4436
3177.176 | 234.3839
3178.176 | 234.1057
3179.176 | 233.6026
3180.176 | 233.5748
3181.176 | 233.0798
3182.176 | 232.8593
3183.176 | 232.4917
3184.176 | 232.327
3185.176 | 232.5372
3186.176 | 232.8711
3187.176 | 233.1654
3188.176 | 233.4752
3189.176 | 233.468
3190.176 | 233.2603
3191.176 | 233.3666
3192.176 | 233.1826
3193.176 | 233.2395
3194.176 | 233.3027
3195.176 | 233.3394
3196.176 | 233.4436
3197.176 | 233.6545
3198.176 | 233.6128
3199.176 | 233.6732
3200.176 | 233.7156
3201.176 | 233.9827
3202.176 | 234.1205
3203.1917 | 234.1139
3204.176 | 234.0597
3205.176 | 233.8034
3206.176 | 233.8459
3207.176 | 233.7027
3208.176 | 233.186
3209.176 | 232.7702
3210.176 | 232.6686
3211.176 | 232.5532
3212.176 | 232.1219
3213.176 | 232.3898
3214.176 | 232.3349
3215.176 | 232.3059
3216.176 | 232.4051
3217.176 | 232.5473
3218.176 | 232.4614
3219.176 | 232.418
3220.176 | 232.3809
3221.176 | 232.3773
3222.176 | 232.372
3223.176 | 232.4648
3224.176 | 232.6615
3225.176 | 232.5481
3226.2229 | 232.7234
3227.176 | 232.5782
3228.176 | 232.5302
3229.176 | 232.4767
3230.176 | 232.3975
3231.176 | 232.474
3232.176 | 232.4987
3233.1917 | 232.6155
3234.176 | 232.6181
3235.176 | 232.7725
3236.176 | 233.3004
3237.176 | 233.3598
3238.176 | 233.4699
3239.176 | 233.392
3240.176 | 233.3775
3241.176 | 233.3016
3242.176 | 233.2563
3243.176 | 233.2035
3244.176 | 233.4892
3245.176 | 233.4417
3246.176 | 233.505
3247.176 | 233.4416
3248.176 | 233.4638
3249.176 | 233.3332
3250.176 | 233.1546
3251.176 | 232.8093
3252.176 | 232.8416
3253.176 | 232.9795
3254.176 | 232.4682
3255.176 | 232.1769
3256.176 | 231.7115
3257.176 | 231.3922
3258.176 | 231.3861
3259.176 | 231.5145
3260.176 | 231.3515
3261.176 | 231.086
3262.176 | 231.0978
3263.176 | 231.1434
3264.176 | 231.2515
3265.176 | 231.4257
3266.176 | 231.6174
3267.176 | 231.9497
3268.176 | 231.9751
3269.176 | 231.8821
3270.176 | 231.9864
3271.1917 | 231.8978
3272.176 | 232.0232
3273.176 | 231.9822
3274.1917 | 232.2351
3275.1917 | 232.3262
3276.176 | 232.5263
3277.176 | 232.8165
3278.176 | 232.8631
3279.176 | 232.9022
3280.176 | 232.991
3281.176 | 233.1772
3282.176 | 233.5397
3283.176 | 233.5916
3284.176 | 233.9321
3285.176 | 234.1636
3286.176 | 234.1922
3287.176 | 234.2601
3288.176 | 234.2391
3289.176 | 234.5674
3290.176 | 234.6181
3291.176 | 234.951
3292.176 | 235.1254
3293.1917 | 235.3736
3294.176 | 235.5358
3295.176 | 235.6487
3296.176 | 235.8686
3297.176 | 235.7951
3298.176 | 237.024
3299.176 | 237.2261
3300.176 | 237.1146
3301.176 | 237.202
3302.176 | 236.9745
3303.176 | 236.6666
3304.176 | 236.3258
3305.176 | 236.1112
3306.176 | 236.173
3307.176 | 236.0078
3308.176 | 235.8885
3309.176 | 235.7349
3310.176 | 235.6711
3311.176 | 235.6983
3312.176 | 235.9305
3313.176 | 236.5669
3314.176 | 237.2791
3315.176 | 237.699
3316.176 | 238.6157
3317.176 | 239.372
3318.176 | 239.8146
3319.176 | 240.2759
3320.176 | 240.6537
3321.176 | 241.4133
3322.176 | 242.1288
3323.176 | 243.0361
3324.176 | 243.4647
3325.176 | 243.7011
3326.176 | 244.8345
3327.176 | 245.7078
3328.176 | 246.5501
3329.176 | 247.2607
3330.176 | 247.5498
3331.176 | 248.496
3332.176 | 249.4931
3333.176 | 249.9551
3334.176 | 250.1312
3335.176 | 250.3562
3336.176 | 250.789
3337.176 | 252.0541
3338.176 | 252.5301
3339.176 | 252.5071
3340.176 | 252.548
3341.176 | 252.8108
3342.176 | 253.1114
3343.176 | 253.6692
3344.176 | 253.871
3345.176 | 254.0879
3346.176 | 254.3632
3347.176 | 254.4258
3348.176 | 254.848
3349.176 | 255.0269
3350.176 | 255.1199
3351.176 | 255.406
3352.176 | 255.8436
3353.176 | 256.0497
3354.176 | 256.1506
3355.176 | 256.556
3356.176 | 256.4837
3357.176 | 257.1868
3358.176 | 257.682
3359.176 | 258.4071
3360.176 | 258.7119
3361.176 | 259.242
3362.176 | 259.4803
3363.176 | 259.7203
3364.176 | 260.2474
3365.176 | 260.637
3366.176 | 261.0505
3367.176 | 261.0818
3368.176 | 261.6809
3369.176 | 262.4601
3370.176 | 262.9959
3371.176 | 262.9952
3372.176 | 263.2567
3373.176 | 263.3753
3374.176 | 263.729
3375.176 | 263.6382
3376.176 | 263.8358
3377.176 | 264.5289
3378.176 | 264.6157
3379.176 | 264.868
3380.176 | 265.48
3381.176 | 266.4383
3382.176 | 267.4333
3383.176 | 267.936
3384.176 | 268.3755
3385.176 | 268.4469
3386.176 | 268.5971
3387.176 | 270.8129
3388.176 | 271.8087
3389.176 | 273.1356
3390.176 | 274.6085
3391.176 | 275.6281
3392.176 | 276.0657
3393.176 | 276.4899
3394.176 | 278.0204
3395.176 | 280.0989
3396.176 | 281.2376
3397.176 | 282.5454
3398.176 | 283.9874
3399.176 | 286.3881
3400.176 | 288.7939
3401.176 | 289.7297
3402.176 | 290.0212
3403.176 | 290.7118
3404.176 | 291.4784
3405.176 | 292.1869
3406.176 | 293.1222
3407.176 | 293.7233
3408.176 | 294.2772
3409.176 | 296.286
3410.176 | 298.4798
3411.176 | 299.49
3412.176 | 300.2764
3413.176 | 300.2651
3414.176 | 300.7088
3415.176 | 300.8175
3416.176 | 300.4913
3417.176 | 300.9499
3418.176 | 300.5749
3419.176 | 300.3383
3420.176 | 300.9912
3421.176 | 301.4547
3422.176 | 301.4146
3423.176 | 302.1683
3424.176 | 302.8361
3425.176 | 303.3425
3426.176 | 303.6689
3427.176 | 303.5759
3428.176 | 304.28
3429.176 | 305.3186
3430.176 | 306.1164
3431.176 | 305.7354
3432.176 | 305.6506
3433.176 | 305.6977
3434.176 | 305.3889
3435.176 | 305.0361
3436.176 | 306.0435
3437.176 | 306.9721
3438.176 | 308.3554
3439.176 | 309.6532
3440.176 | 311.5309
3441.176 | 311.9291
3442.176 | 312.1105
3443.176 | 312.3455
3444.176 | 313.3891
3445.176 | 315.0294
3446.176 | 315.4235
3447.176 | 314.9949
3448.176 | 315.1474
3449.176 | 316.5425
3450.176 | 316.9788
3451.176 | 318.3538
3452.176 | 318.407
3453.176 | 319.7859
3454.176 | 320.5095
3455.176 | 321.5705
3456.1917 | 322.0349
3457.1917 | 321.9419
3458.1917 | 321.8052
3459.176 | 322.9803
3460.176 | 323.9174
3461.176 | 323.6388
3462.176 | 324.6322
3463.176 | 325.756
3464.176 | 326.2056
3465.176 | 326.6186
3466.176 | 327.4015
3467.176 | 328.4731
3468.176 | 329.0919
3469.176 | 329.1163
3470.176 | 329.4752
3471.176 | 330.0995
3472.176 | 330.2086
3473.176 | 330.9044
3474.176 | 331.2318
3475.176 | 332.34
3476.176 | 333.0497
3477.176 | 334.0905
3478.176 | 335.6125
3479.176 | 336.6793
3480.176 | 337.3742
3481.176 | 338.402
3482.176 | 338.7152
3483.176 | 338.8073
3484.176 | 338.5428
3485.176 | 339.0551
3486.176 | 339.8099
3487.176 | 341.1764
3488.176 | 342.0376
3489.176 | 342.9716
3490.176 | 343.2063
3491.176 | 343.3058
3492.176 | 342.5645
3493.176 | 342.3565
3494.176 | 341.4467
3495.176 | 341.788
3496.176 | 343.5309
3497.176 | 344.8249
3498.176 | 345.423
3499.176 | 345.3982
3500.176 | 345.7377
3501.176 | 346.7852
3502.176 | 346.7632
3503.176 | 346.5328
3504.176 | 346.3495
3505.176 | 346.5593
3506.176 | 347.4331
3507.176 | 348.2646
3508.176 | 349.4292
3509.176 | 349.3206
3510.176 | 348.9516
3511.176 | 349.8648
3512.176 | 349.8692
3513.176 | 350.9497
3514.176 | 351.0404
3515.176 | 350.8462
3516.176 | 351.2184
3517.176 | 352.0176
3518.176 | 353.0962
3519.176 | 354.6601
3520.176 | 355.2654
3521.176 | 354.5297
3522.176 | 354.6011
3523.176 | 354.1348
3524.176 | 353.9098
3525.176 | 353.9627
3526.176 | 353.7858
3527.176 | 352.9636
3528.176 | 352.4905
3529.176 | 352.9243
3530.176 | 352.9454
3531.176 | 354.0053
3532.176 | 354.8165
3533.176 | 354.4017
3534.176 | 354.7062
3535.176 | 355.1568
3536.176 | 356.2926
3537.176 | 357.2122
3538.176 | 358.1151
3539.176 | 359.7803
3540.176 | 360.1368
3541.176 | 360.8061
3542.176 | 361.5849
3543.176 | 362.2686
3544.176 | 362.5635
3545.176 | 362.7557
3546.176 | 362.6277
3547.176 | 363.7432
3548.176 | 364.5982
3549.176 | 365.0941
3550.176 | 366.5534
3551.176 | 368.7852
3552.176 | 369.701
3553.176 | 370.8443
3554.176 | 374.1175
3555.176 | 378.9738
3556.176 | 380.3954
3557.176 | 379.7638
3558.176 | 379.6349
3559.176 | 379.4934
3560.176 | 378.9408
3561.176 | 378.2348
3562.176 | 377.8341
3563.176 | 379.3627
3564.176 | 379.6185
3565.176 | 382.6808
3566.176 | 381.2227
3567.176 | 382.0755
3568.176 | 382.3301
3569.176 | 381.4679
3570.176 | 380.4925
3571.176 | 381.1427
3572.176 | 381.4702
3573.176 | 383.7216
3574.176 | 385.7405
3575.176 | 389.7145
3576.176 | 391.0837
3577.176 | 393.1216
3578.176 | 395.3619
3579.176 | 396.7687
3580.176 | 396.9625
3581.176 | 397.569
3582.176 | 397.8475
3583.176 | 399.135
3584.176 | 398.7899
3585.176 | 399.3495
3586.176 | 400.4517
3587.176 | 400.8298
3588.176 | 400.999
3589.176 | 402.9972
3590.176 | 404.3582
3591.176 | 403.8818
3592.176 | 402.9203
3593.176 | 403.0174
3594.176 | 403.8241
3595.176 | 404.6916
3596.176 | 408.0008
3597.176 | 410.1569
3598.176 | 411.1002
3599.176 | 412.4826
3600.176 | 414.6897
3601.176 | 418.7499
3602.176 | 424.8701
3603.176 | 429.0737
3604.176 | 430.2141
3605.176 | 430.0869
3606.176 | 431.7648
3607.176 | 434.1623
3608.176 | 434.7128
3609.176 | 434.5431
3610.176 | 436.1736
3611.176 | 437.4863
3612.176 | 437.2204
3613.176 | 439.4851
3614.176 | 437.6433
3615.176 | 437.0429
3616.176 | 434.627
3617.176 | 432.3732
3618.176 | 431.4575
3619.176 | 431.43
3620.176 | 431.9112
3621.176 | 432.7347
3622.176 | 436.7057
3623.176 | 437.6749
3624.176 | 437.455
3625.176 | 439.5882
3626.176 | 441.9642
3627.176 | 442.4467
3628.176 | 440.3732
3629.176 | 438.5391
3630.176 | 438.0441
3631.176 | 437.7798
3632.176 | 437.7517
3633.176 | 439.8323
3634.176 | 444.4344
3635.176 | 444.4628
3636.176 | 443.4387
3637.176 | 446.7301
3638.176 | 449.2972
3639.176 | 449.7008
3640.176 | 452.2977
3641.176 | 450.1594
3642.176 | 447.5486
3643.176 | 444.8644
3644.176 | 445.4111
3645.176 | 445.6603
3646.176 | 445.7247
3647.176 | 443.8706
3648.176 | 442.1793
3649.176 | 439.9891
3650.176 | 438.7744
3651.176 | 436.2155
3652.176 | 435.2898
3653.176 | 439.5521
3654.176 | 444.226
3655.176 | 443.8429
3656.176 | 443.4256
3657.176 | 443.8854
3658.176 | 445.7375
3659.176 | 446.0987
3660.176 | 450.2781
3661.176 | 455.5712
3662.176 | 464.2524
3663.176 | 469.4068
3664.176 | 470.3889
3665.176 | 472.811
3666.176 | 470.522
3667.176 | 469.4318
3668.176 | 469.8528
3669.176 | 474.5678
3670.176 | 475.9244
3671.176 | 478.1747
3672.176 | 480.0462
3673.176 | 480.6569
3674.176 | 481.8769
3675.176 | 481.8561
3676.176 | 485.317
3677.176 | 485.0916
3678.176 | 484.5471
3679.176 | 485.6242
3680.176 | 481.9678
3681.176 | 483.1273
3682.176 | 486.815
3683.176 | 485.3043
3684.176 | 481.9177
3685.176 | 485.9635
3686.176 | 494.1046
3687.176 | 494.7419
3688.176 | 498.3054
3689.176 | 499.2091
3690.176 | 502.5019
3691.176 | 503.1194
3692.176 | 508.0573
3693.176 | 511.9634
3694.176 | 510.4651
3695.176 | 509.9336
3696.176 | 511.4061
3697.176 | 511.5028
3698.176 | 515.2483
3699.176 | 516.022
3700.176 | 513.7766
3701.176 | 515.6455
3702.176 | 527.6698
3703.176 | 526.9301
3704.176 | 524.5878
3705.176 | 529.5085
3706.176 | 532.2406
3707.176 | 528.6964
3708.176 | 528.9408
3709.176 | 527.9757
3710.176 | 530.4551
3711.176 | 535.4469
3712.176 | 543.5012
3713.176 | 541.4113
3714.176 | 554.1214
3715.176 | 559.3547
3716.176 | 556.7844
3717.176 | 562.5681
3718.176 | 565.3844
3719.176 | 565.6596
3720.176 | 561.9154
3721.176 | 566.3417
3722.176 | 566.7708
3723.176 | 570.015
3724.176 | 579.5355
3725.176 | 582.3944
3726.176 | 581.3864
3727.176 | 578.3113
3728.176 | 580.1326
3729.176 | 581.7762
3730.176 | 586.2847
3731.176 | 590.8947
3732.176 | 593.463
3733.176 | 592.7303
3734.176 | 592.3969
3735.176 | 589.2286
3736.176 | 588.0554
3737.176 | 586.5369
3738.176 | 589.6552
3739.176 | 588.8512
3740.176 | 588.8135
3741.176 | 585.703
3742.176 | 585.991
3743.176 | 585.326
3744.176 | 588.1995
3745.176 | 584.815
3746.176 | 584.4215
3747.176 | 586.3018
3748.176 | 583.1662
3749.176 | 576.7518
3750.176 | 579.467
3751.176 | 580.6882
3752.176 | 581.5584
3753.176 | 576.9296
3754.176 | 574.785
3755.176 | 573.8105
3756.176 | 570.6759
3757.176 | 571.6029
3758.176 | 570.0129
3759.176 | 569.2122
3760.176 | 565.336
3761.176 | 564.7509
3762.176 | 563.7136
3763.176 | 563.4553
3764.176 | 564.6226
3765.176 | 564.7681
3766.176 | 565.6448
3767.176 | 573.3634
3768.176 | 573.842
3769.176 | 568.8298
3770.176 | 568.9553
3771.176 | 572.4327
3772.176 | 571.1882
3773.176 | 571.214
3774.176 | 566.903
3775.176 | 567.946
3776.176 | 568.5927
3777.176 | 571.5072
3778.176 | 573.6895
3779.176 | 581.245
3780.176 | 584.2064
3781.176 | 587.658
3782.176 | 588.8949
3783.176 | 591.8389
3784.176 | 598.172
3785.176 | 602.5761
3786.176 | 599.9844
3787.176 | 602.2138
3788.176 | 599.6963
3789.176 | 595.8505
3790.176 | 595.4039
3791.176 | 592.2498
3792.176 | 589.1831
3793.176 | 585.7341
3794.176 | 584.9145
3795.176 | 583.4799
3796.176 | 579.9894
3797.176 | 578.1099
3798.176 | 574.9971
3799.176 | 574.0968
3800.176 | 572.2526
3801.176 | 573.4642
3802.176 | 571.9771
3803.176 | 574.4266
3804.176 | 577.8061
3805.176 | 579.4654
3806.176 | 579.2291
3807.176 | 575.863
3808.176 | 574.7703
3809.176 | 577.0042
3810.176 | 580.8643
3811.176 | 581.2598
3812.176 | 582.2015
3813.176 | 579.9594
3814.176 | 578.4623
3815.176 | 577.2744
3816.176 | 575.6451
3817.176 | 576.2274
3818.176 | 577.4871
3819.176 | 576.6577
3820.176 | 572.5357
3821.176 | 572.5799
3822.176 | 570.8517
3823.176 | 572.845
3824.176 | 574.2278
3825.176 | 572.9423
3826.176 | 575.5764
3827.176 | 579.3923
3828.176 | 579.7476
3829.176 | 580.3185
3830.176 | 583.6278
3831.176 | 582.806
3832.176 | 584.1308
3833.176 | 581.3323
3834.176 | 583.5583
3835.176 | 580.3981
3836.176 | 579.5248
3837.176 | 579.5582
3838.176 | 579.0944
3839.176 | 580.0597
3840.176 | 576.8585
3841.176 | 578.1266
3842.176 | 578.5788
3843.176 | 580.7289
3844.176 | 584.2063
3845.176 | 585.2491
3846.176 | 583.8561
3847.176 | 586.5238
3848.176 | 589.9255
3849.176 | 590.7425
3850.176 | 593.5828
3851.176 | 592.4933
3852.176 | 596.1717
3853.176 | 594.9648
3854.176 | 597.359
3855.176 | 598.1082
3856.176 | 596.1837
3857.176 | 597.3228
3858.176 | 597.4785
3859.176 | 596.8712
3860.176 | 599.8689
3861.176 | 602.307
3862.176 | 603.9454
3863.176 | 603.5034
3864.176 | 602.5733
3865.176 | 602.4578
3866.176 | 607.6901
3867.176 | 607.4738
3868.176 | 607.7212
3869.176 | 607.6363
3870.176 | 611.688
3871.176 | 610.9108
3872.176 | 609.5045
3873.176 | 609.5783
3874.176 | 608.8512
3875.176 | 606.6599
3876.176 | 609.1949
3877.176 | 611.1243
3878.176 | 613.7512
3879.176 | 612.7537
3880.176 | 610.5102
3881.176 | 612.744
3882.176 | 614.8668
3883.176 | 618.1073
3884.176 | 620.5224
3885.176 | 619.1707
3886.176 | 617.7274
3887.176 | 616.8818
3888.176 | 618.8292
3889.176 | 611.5988
3890.176 | 619.4823
3891.176 | 629.2574
3892.176 | 628.2177
3893.176 | 638.8143
3894.176 | 642.9227
3895.176 | 645.0686
3896.176 | 641.8228
3897.176 | 641.6128
3898.176 | 636.1423
3899.176 | 633.9962
3900.176 | 629.4237
3901.176 | 623.7685
3902.176 | 618.906
3903.176 | 621.0087
3904.176 | 623.9712
3905.176 | 625.7916
3906.176 | 623.8029
3907.176 | 620.1957
3908.176 | 618.3188
3909.176 | 617.0237
3910.176 | 616.4365
3911.176 | 616.0138
3912.176 | 614.8732
3913.176 | 621.266
3914.176 | 621.6849
3915.176 | 619.9128
3916.176 | 621.0103
3917.176 | 622.2594
3918.176 | 623.9728
3919.176 | 624.8578
3920.176 | 626.8305
3921.176 | 630.1509
3922.176 | 630.3552
3923.176 | 637.9395
3924.176 | 641.5562
3925.176 | 641.7597
3926.176 | 640.3366
3927.176 | 643.5926
3928.176 | 641.6842
3929.176 | 638.2057
3930.176 | 633.7982
3931.176 | 635.7575
3932.176 | 635.2844
3933.176 | 638.0628
3934.176 | 637.6381
3935.176 | 640.4502
3936.176 | 643.8357
3937.176 | 649.238
3938.176 | 647.6278
3939.176 | 648.9574
3940.176 | 648.4858
3941.176 | 643.9419
3942.176 | 637.9915
3943.176 | 633.9231
3944.176 | 634.3094
3945.176 | 632.4556
3946.176 | 634.5531
3947.176 | 635.9702
3948.176 | 634.4741
3949.176 | 635.9384
3950.176 | 635.8315
3951.176 | 634.5022
3952.176 | 635.5223
3953.176 | 635.0766
3954.176 | 639.2084
3955.176 | 640.2029
3956.176 | 639.4021
3957.176 | 634.733
3958.176 | 637.0737
3959.176 | 634.9881
3960.176 | 630.9935
3961.176 | 628.5757
3962.176 | 626.622
3963.176 | 624.5954
3964.176 | 625.7992
3965.176 | 627.1102
3966.176 | 630.8612
3967.176 | 633.468
3968.176 | 632.2749
3969.176 | 635.7691
3970.176 | 640.8716
3971.176 | 643.8946
3972.176 | 643.7006
3973.176 | 638.3311
3974.176 | 636.0109
3975.176 | 634.1331
3976.176 | 631.6071
3977.176 | 631.74
3978.176 | 635.6579
3979.176 | 633.7429
3980.176 | 629.6893
3981.176 | 628.825
3982.176 | 626.6719
3983.176 | 628.9429
3984.176 | 637.2464
3985.176 | 635.9498
3986.176 | 637.9166
3987.176 | 641.1449
3988.176 | 642.1912
3989.176 | 647.2716
3990.176 | 643.9784
3991.176 | 645.5513
3992.176 | 640.8749
3993.176 | 636.1446
3994.176 | 631.5901
3995.176 | 629.5022
3996.176 | 630.9327
3997.176 | 631.0344
3998.176 | 633.8073
3999.176 | 637.9915
4000.176 | 635.4759
4001.176 | 635.8596
4002.176 | 636.2736
4003.176 | 639.5769
4004.176 | 639.8612
4005.176 | 637.3934
4006.176 | 634.6373
4007.176 | 632.4541
4008.176 | 631.0841
4009.176 | 634.0089
4010.176 | 637.9852
4011.176 | 640.8176
4012.176 | 641.3992
4013.176 | 641.3844
4014.176 | 645.1178
4015.176 | 645.6316
4016.176 | 645.1199
4017.176 | 648.7149
4018.176 | 650.9889
4019.176 | 647.9581
4020.176 | 646.1907
4021.176 | 646.132
4022.176 | 643.8494
4023.176 | 638.7369
4024.176 | 636.6812
4025.176 | 634.9173
4026.176 | 636.6508
4027.176 | 639.5432
4028.176 | 638.2433
4029.176 | 637.7199
4030.176 | 637.915
4031.176 | 637.8442
4032.176 | 637.6907
4033.176 | 636.9323
4034.176 | 636.4311
4035.176 | 633.999
4036.176 | 634.1323
4037.176 | 631.117
4038.176 | 629.27
4039.176 | 628.0033
4040.176 | 625.9138
4041.176 | 626.0251
4042.176 | 623.0998
4043.176 | 620.0145
4044.176 | 621.3962
4045.176 | 623.3126
4046.176 | 629.2674
4047.176 | 629.3361
4048.176 | 630.2519
4049.176 | 628.1825
4050.176 | 629.8397
4051.176 | 630.5128
4052.176 | 631.6304
4053.176 | 635.737
4054.176 | 641.8702
4055.176 | 645.6147
4056.176 | 645.4256
4057.176 | 644.4526
4058.176 | 645.5988
4059.176 | 649.1839
4060.176 | 652.8066
4061.176 | 649.6288
4062.176 | 646.3536
4063.176 | 644.5235
4064.176 | 646.946
4065.176 | 646.2207
4066.176 | 647.6451
4067.176 | 648.0467
4068.176 | 647.8059
4069.176 | 651.5562
4070.176 | 648.3864
4071.176 | 646.5973
4072.176 | 643.7157
4073.176 | 641.9193
4074.176 | 642.6267
4075.176 | 641.8853
4076.176 | 640.4812
4077.176 | 642.7271
4078.176 | 645.3745
4079.176 | 647.8481
4080.176 | 651.7264
4081.176 | 649.2118
4082.176 | 648.9283
4083.176 | 648.0341
4084.176 | 648.5671
4085.176 | 650.547
4086.176 | 653.1789
4087.176 | 653.9563
4088.176 | 658.861
4089.176 | 661.2242
4090.176 | 663.0759
4091.176 | 658.4616
4092.176 | 655.5027
4093.176 | 654.8209
4094.176 | 654.21
4095.176 | 655.9739
4096.176 | 654.6833
4097.176 | 650.9223
4098.176 | 656.3434
4099.176 | 664.8192
4100.176 | 666.3263
4101.176 | 666.9723
4102.176 | 663.8675
4103.176 | 664.0058
4104.176 | 657.8047
4105.176 | 655.0157
4106.176 | 658.0103
4107.176 | 658.9108
4108.176 | 658.583
4109.176 | 657.905
4110.176 | 659.0873
4111.176 | 657.4217
4112.176 | 657.2042
4113.176 | 657.4191
4114.176 | 660.9469
4115.176 | 658.2012
4116.176 | 655.3343
4117.176 | 657.9651
4118.176 | 664.2127
4119.176 | 665.8564
4120.176 | 669.2731
4121.176 | 670.6174
4122.176 | 670.5692
4123.176 | 673.7961
4124.176 | 674.9046
4125.176 | 672.4663
4126.176 | 674.752
4127.176 | 677.565
4128.176 | 683.6984
4129.176 | 684.765
4130.176 | 686.0586
4131.176 | 681.9581
4132.176 | 677.0953
4133.176 | 679.2118
4134.176 | 680.2394
4135.176 | 682.4625
4136.176 | 685.7452
4137.176 | 682.2296
4138.176 | 687.8058
4139.176 | 689.5171
4140.176 | 683.4762
4141.176 | 689.1771
4142.176 | 683.3972
4143.176 | 682.3748
4144.176 | 679.8157
4145.176 | 678.9459
4146.176 | 676.9958
4147.176 | 671.4238
4148.176 | 666.2422
4149.176 | 664.8581
4150.176 | 661.3019
4151.176 | 661.6391
4152.176 | 659.374
4153.176 | 658.1154
4154.176 | 655.4785
4155.176 | 655.6282
4156.176 | 656.1921
4157.176 | 658.9835
4158.176 | 660.6482
4159.176 | 658.9733
4160.176 | 661.2166
4161.176 | 661.8282
4162.176 | 666.1849
4163.176 | 667.7018
4164.176 | 666.6956
4165.176 | 671.9613
4166.176 | 674.2109
4167.176 | 673.9732
4168.176 | 676.5323
4169.176 | 673.2651
4170.176 | 676.537
4171.176 | 673.1987
4172.176 | 669.8186
4173.176 | 666.7482
4174.176 | 664.5762
4175.176 | 668.3451
4176.176 | 665.2662
4177.176 | 662.675
4178.176 | 662.9216
4179.176 | 665.3463
4180.176 | 667.2005
4181.176 | 670.2227
4182.176 | 670.4074
4183.176 | 674.0898
4184.176 | 674.4812
4185.176 | 676.4894
4186.176 | 681.7915
4187.176 | 689.1288
4188.176 | 693.6912
4189.176 | 693.9349
4190.176 | 689.5398
4191.176 | 695.4641
4192.176 | 693.8419
4193.176 | 692.687
4194.176 | 690.509
4195.176 | 688.1819
4196.176 | 691.1303
4197.176 | 696.4553
4198.176 | 697.1678
4199.176 | 697.6919
4200.176 | 695.0416
4201.176 | 694.3384
4202.176 | 696.1345
4203.1917 | 702.7625
4204.176 | 699.255
4205.176 | 693.7924
4206.176 | 695.2893
4207.176 | 689.1727
4208.176 | 690.7728
4209.176 | 691.4063
4210.176 | 693.055
4211.176 | 695.0655
4212.176 | 700.396
4213.176 | 706.2686
4214.176 | 705.5214
4215.176 | 703.0517
4216.176 | 707.6545
4217.176 | 708.3854
4218.176 | 712.0426
4219.176 | 712.4998
4220.176 | 708.46
4221.176 | 707.5357
4222.176 | 704.0259
4223.176 | 698.7858
4224.176 | 691.1755
4225.176 | 693.4323
4226.176 | 689.8959
4227.176 | 691.5436
4228.176 | 696.0448
4229.176 | 696.7422
4230.176 | 697.1731
4231.176 | 694.3554
4232.176 | 696.6615
4233.176 | 698.791
4234.176 | 697.734
4235.176 | 698.2827
4236.176 | 699.6595
4237.176 | 702.1129
4238.176 | 700.6367
4239.176 | 697.7018
4240.176 | 695.987
4241.176 | 695.2694
4242.176 | 694.0035
4243.176 | 698.2628
4244.176 | 696.5311
4245.176 | 695.1562
4246.176 | 693.4117
4247.176 | 690.1317
4248.176 | 690.7129
4249.176 | 694.6392
4250.176 | 694.014
4251.176 | 696.1051
4252.176 | 694.1344
4253.176 | 701.5724
4254.176 | 699.6835
4255.176 | 698.9845
4256.176 | 700.9313
4257.176 | 703.9771
4258.176 | 701.1601
4259.176 | 703.622
4260.176 | 704.7713
4261.176 | 705.213
4262.1917 | 706.6907
4263.1917 | 707.4018
4264.176 | 709.2554
4265.176 | 708.7653
4266.176 | 708.4072
4267.176 | 704.87
4268.176 | 705.6062
4269.176 | 709.8421
4270.176 | 708.0601
4271.176 | 703.9005
4272.176 | 703.1136
4273.176 | 700.8638
4274.176 | 699.5644
4275.176 | 697.5609
4276.176 | 697.3576
4277.176 | 693.2935
4278.176 | 691.3696
4279.176 | 690.4892
4280.176 | 690.563
4281.176 | 687.7736
4282.176 | 689.3095
4283.176 | 690.6615
4284.176 | 690.1916
4285.176 | 688.7003
4286.176 | 687.9356
4287.176 | 687.9459
4288.176 | 693.743
4289.176 | 695.2756
4290.176 | 698.2143
4291.176 | 702.7209
4292.176 | 702.8272
4293.176 | 705.5259
4294.176 | 710.6103
4295.176 | 711.772
4296.176 | 712.3484
4297.176 | 712.0796
4298.176 | 714.8823
4299.176 | 712.5298
4300.176 | 711.0954
4301.176 | 715.4988
4302.176 | 712.3177
4303.176 | 710.2596
4304.176 | 703.2319
4305.176 | 706.0611
4306.176 | 704.6074
4307.176 | 707.8006
4308.176 | 709.1751
4309.176 | 707.554
4310.176 | 708.2452
4311.176 | 707.7788
4312.176 | 705.9757
4313.176 | 703.4399
4314.176 | 704.3774
4315.176 | 703.9927
4316.176 | 700.6623
4317.176 | 698.7042
4318.176 | 696.4125
4319.176 | 694.3194
4320.176 | 693.3992
4321.176 | 696.9794
4322.176 | 698.3773
4323.176 | 699.3983
4324.176 | 700.0862
4325.176 | 701.1944
4326.176 | 703.192
4327.176 | 704.7918
4328.176 | 705.6328
4329.176 | 705.8414
4330.176 | 704.7324
4331.176 | 704.38
4332.176 | 702.6303
4333.176 | 702.4979
4334.176 | 706.5586
4335.176 | 708.8158
4336.176 | 709.8782
4337.176 | 711.1815
4338.176 | 711.2066
4339.176 | 712.0774
4340.176 | 713.4881
4341.176 | 716.2077
4342.176 | 712.0701
4343.176 | 707.9286
4344.176 | 706.1712
4345.176 | 706.5326
4346.176 | 706.5248
4347.176 | 704.0782
4348.176 | 704.6459
4349.176 | 707.584
4350.176 | 712.5768
4351.176 | 716.0029
4352.176 | 715.7114
4353.176 | 714.9139
4354.176 | 715.5398
4355.176 | 712.0924
4356.176 | 710.03
4357.176 | 710.7587
4358.176 | 707.5783
4359.176 | 706.6995
4360.176 | 706.055
4361.176 | 710.2945
4362.176 | 709.921
4363.176 | 711.9819
4364.176 | 712.197
4365.176 | 712.393
4366.176 | 711.3379
4367.176 | 709.9824
4368.176 | 710.1974
4369.176 | 712.1794
4370.176 | 711.9365
4371.176 | 710.8267
4372.176 | 715.0995
4373.176 | 714.2319
4374.176 | 712.6782
4375.176 | 712.9206
4376.176 | 716.0221
4377.176 | 717.2962
4378.176 | 717.8641
4379.176 | 720.7561
4380.176 | 719.3615
4381.176 | 718.6445
4382.176 | 719.7495
4383.176 | 721.7549
4384.176 | 721.9368
4385.176 | 720.8587
4386.176 | 719.8455
4387.176 | 716.7575
4388.176 | 714.5264
4389.176 | 709.6164
4390.176 | 708.8548
4391.176 | 708.3408
4392.176 | 709.4798
4393.176 | 711.0592
4394.176 | 710.6247
4395.176 | 709.9257
4396.176 | 713.0804
4397.176 | 714.5623
4398.176 | 715.198
4399.176 | 710.8692
4400.176 | 712.6116
4401.176 | 713.3625
4402.176 | 715.6981
4403.176 | 717.6169
4404.176 | 719.3515
4405.176 | 717.6121
4406.176 | 714.165
4407.176 | 713.4489
4408.176 | 712.4915
4409.176 | 715.5494
4410.176 | 712.986
4411.176 | 713.8938
4412.176 | 712.4445
4413.176 | 715.9004
4414.176 | 718.2451
4415.176 | 718.1927
4416.176 | 717.9763
4417.176 | 715.0135
4418.176 | 714.9873
4419.176 | 715.1557
4420.176 | 717.2017
4421.176 | 717.8905
4422.176 | 715.1582
4423.176 | 711.7891
4424.176 | 711.8769
4425.176 | 710.253
4426.176 | 709.5858
4427.176 | 711.4294
4428.176 | 714.131
4429.176 | 711.916
4430.176 | 708.0146
4431.176 | 709.2553
4432.176 | 710.553
4433.176 | 710.5759
4434.1917 | 711.536
4435.176 | 716.386
4436.176 | 719.8993
4437.176 | 720.9037
4438.176 | 722.4919
4439.176 | 726.4088
4440.176 | 726.5224
4441.176 | 724.0577
4442.176 | 723.0437
4443.176 | 723.1445
4444.176 | 721.7623
4445.176 | 720.1505
4446.176 | 719.5122
4447.176 | 719.4828
4448.176 | 722.049
4449.176 | 724.2205
4450.176 | 725.3591
4451.176 | 726.8322
4452.176 | 724.5872
4453.176 | 721.5802
4454.176 | 721.4526
4455.176 | 723.4867
4456.176 | 723.1611
4457.176 | 721.1307
4458.176 | 722.6374
4459.176 | 726.9576
4460.176 | 727.7576
4461.176 | 728.6076
4462.176 | 729.8444
4463.176 | 731.4268
4464.176 | 730.8783
4465.176 | 730.7996
4466.176 | 729.3475
4467.176 | 730.594
4468.176 | 728.3429
4469.176 | 727.2249
4470.176 | 725.999
4471.176 | 727.0852
4472.176 | 726.2341
4473.176 | 723.1139
4474.176 | 722.825
4475.176 | 723.74
4476.176 | 722.542
4477.176 | 721.7921
4478.1917 | 720.1907
4479.176 | 722.938
4480.176 | 725.0788
4481.176 | 728.0047
4482.176 | 726.4887
4483.176 | 724.7375
4484.176 | 727.3274
4485.176 | 727.9066
4486.176 | 728.1824
4487.176 | 730.288
4488.176 | 729.3435
4489.176 | 728.3472
4490.176 | 729.403
4491.176 | 730.0823
4492.176 | 727.7767
4493.176 | 723.6924
4494.176 | 721.1687
4495.176 | 720.1679
4496.176 | 716.5301
4497.176 | 715.2044
4498.176 | 713.9794
4499.176 | 715.6467
4500.176 | 715.6439
4501.176 | 713.5
4502.176 | 711.2712
4503.176 | 712.507
4504.176 | 713.0417
4505.176 | 715.752
4506.176 | 717.4933
4507.176 | 718.6207
4508.176 | 718.7723
4509.176 | 720.0903
4510.176 | 718.698
4511.176 | 715.814
4512.176 | 713.3829
4513.176 | 710.0087
4514.176 | 711.2212
4515.176 | 709.2794
4516.176 | 711.1773
4517.176 | 711.7907
4518.176 | 712.2672
4519.176 | 712.9426
4520.176 | 717.4895
4521.176 | 721.0853
4522.176 | 722.126
4523.176 | 719.7275
4524.176 | 720.3473
4525.176 | 723.3756
4526.176 | 724.9258
4527.176 | 727.3941
4528.176 | 727.0712
4529.176 | 725.5436
4530.176 | 726.4519
4531.176 | 726.1968
4532.176 | 726.6021
4533.176 | 729.207
4534.176 | 730.7232
4535.176 | 731.0805
4536.176 | 727.3971
4537.176 | 725.5142
4538.176 | 724.6936
4539.176 | 722.3165
4540.176 | 720.6425
4541.176 | 722.4482
4542.176 | 722.0205
4543.176 | 720.4355
4544.176 | 721.2124
4545.176 | 717.9462
4546.176 | 718.6978
4547.176 | 721.4309
4548.176 | 721.3683
4549.176 | 722.794
4550.176 | 721.7068
4551.176 | 723.2422
4552.176 | 722.6477
4553.176 | 723.2295
4554.176 | 721.9033
4555.176 | 720.2367
4556.176 | 718.7418
4557.176 | 717.8815
4558.176 | 717.612
4559.176 | 717.9266
4560.176 | 716.6652
4561.176 | 719.5178
4562.176 | 720.0746
4563.1917 | 719.8704
4564.176 | 718.3028
4565.176 | 716.8946
4566.176 | 717.2134
4567.176 | 719.0039
4568.176 | 717.4894
4569.176 | 719.1749
4570.176 | 720.2528
4571.176 | 721.3935
4572.176 | 720.9213
4573.176 | 718.9105
4574.176 | 718.0361
4575.176 | 718.221
4576.176 | 717.9753
4577.176 | 717.1119
4578.176 | 717.3919
4579.176 | 717.5428
4580.176 | 716.5881
4581.176 | 714.1618
4582.176 | 713.7442
4583.176 | 714.4792
4584.176 | 712.7781
4585.176 | 712.0519
4586.176 | 708.9583
4587.176 | 707.2871
4588.176 | 707.1788
4589.176 | 708.9053
4590.176 | 709.584
4591.176 | 707.2776
4592.176 | 704.6923
4593.176 | 704.2097
4594.176 | 702.2566
4595.176 | 703.3554
4596.176 | 702.9936
4597.176 | 701.8029
4598.176 | 700.6318
4599.176 | 700.2552
4600.176 | 702.4607
4601.176 | 703.9371
4602.176 | 707.239
4603.176 | 707.6219
4604.176 | 706.9881
4605.176 | 707.7363
4606.176 | 707.997
4607.176 | 709.3462
4608.176 | 710.9215
4609.176 | 713.6714
4610.176 | 715.9267
4611.176 | 719.3066
4612.176 | 722.7678
4613.176 | 725.8545
4614.176 | 726.9412
4615.176 | 727.9564
4616.176 | 727.7829
4617.176 | 723.774
4618.176 | 719.4295
4619.176 | 716.47
4620.176 | 716.654
4621.176 | 714.8654
4622.176 | 713.6664
4623.1917 | 711.7782
4624.176 | 714.0297
4625.176 | 715.818
4626.176 | 716.7884
4627.176 | 715.1237
4628.176 | 717.4186
4629.176 | 716.7744
4630.176 | 716.0059
4631.176 | 714.7524
4632.176 | 718.2222
4633.176 | 720.9043
4634.176 | 722.2303
4635.176 | 720.0024
4636.176 | 719.5603
4637.176 | 720.3505
4638.176 | 721.5369
4639.176 | 722.3252
4640.176 | 719.8858
4641.176 | 719.4342
4642.176 | 718.7042
4643.176 | 717.0616
4644.176 | 716.1822
4645.176 | 717.1483
4646.176 | 717.2779
4647.176 | 715.7155
4648.176 | 717.1565
4649.176 | 718.1894
4650.176 | 715.4886
4651.176 | 712.3076
4652.176 | 710.6969
4653.176 | 711.2457
4654.176 | 711.4896
4655.176 | 711.5526
4656.176 | 708.5115
4657.176 | 709.5952
4658.176 | 712.8285
4659.176 | 710.6886
4660.176 | 708.9636
4661.176 | 707.1278
4662.176 | 707.0553
4663.176 | 706.1444
4664.176 | 705.7378
4665.176 | 705.8832
4666.176 | 704.5634
4667.176 | 704.2295
4668.176 | 702.8756
4669.176 | 702.6286
4670.176 | 703.6877
4671.176 | 703.5505
4672.176 | 705.0899
4673.176 | 708.3272
4674.176 | 711.3137
4675.176 | 711.4227
4676.176 | 711.7394
4677.176 | 713.6151
4678.176 | 713.7282
4679.176 | 713.8085
4680.176 | 712.6832
4681.176 | 713.9489
4682.176 | 712.9437
4683.176 | 710.7579
4684.176 | 710.5343
4685.176 | 708.168
4686.176 | 706.4766
4687.176 | 708.753
4688.176 | 708.9275
4689.176 | 707.7365
4690.176 | 708.9167
4691.176 | 706.9542
4692.176 | 707.6503
4693.176 | 709.9109
4694.176 | 711.7671
4695.176 | 711.723
4696.176 | 709.3954
4697.176 | 709.0591
4698.176 | 706.2142
4699.176 | 701.7056
4700.176 | 699.6672
4701.176 | 699.8091
4702.176 | 700.2993
4703.176 | 699.5595
4704.176 | 697.3316
4705.176 | 695.5882
4706.176 | 695.5956
4707.176 | 698.725
4708.176 | 698.5971
4709.176 | 700.8574
4710.176 | 701.8887
4711.176 | 703.9487
4712.176 | 706.528
4713.176 | 704.1797
4714.176 | 704.9588
4715.176 | 703.6104
4716.176 | 702.8204
4717.176 | 702.1668
4718.176 | 699.963
4719.176 | 699.5556
4720.176 | 703.3852
4721.176 | 702.1628
4722.176 | 706.8145
4723.176 | 707.8981
4724.176 | 706.4454
4725.176 | 704.5288
4726.176 | 701.7275
4727.176 | 700.7986
4728.176 | 698.8216
4729.176 | 696.8592
4730.176 | 700.1601
4731.176 | 700.1232
4732.176 | 703.503
4733.176 | 705.6555
4734.176 | 707.3939
4735.176 | 710.3334
4736.176 | 711.3855
4737.176 | 709.5331
4738.176 | 707.1788
4739.176 | 705.8605
4740.176 | 705.626
4741.176 | 704.9301
4742.176 | 706.2682
4743.176 | 708.8843
4744.176 | 708.9413
4745.176 | 709.6313
4746.176 | 713.2532
4747.176 | 713.3169
4748.176 | 710.0147
4749.176 | 708.4188
4750.176 | 707.4883
4751.176 | 704.8025
4752.176 | 704.077
4753.176 | 701.7645
4754.176 | 702.0447
4755.176 | 699.6951
4756.176 | 697.51
4757.176 | 698.1878
4758.176 | 702.3116
4759.176 | 702.8326
4760.176 | 700.3926
4761.176 | 702.9564
4762.176 | 703.3204
4763.176 | 702.8203
4764.176 | 700.2278
4765.176 | 700.0899
4766.176 | 700.9726
4767.176 | 703.2333
4768.176 | 701.5452
4769.176 | 703.9047
4770.176 | 702.7329
4771.176 | 702.6351
4772.176 | 706.6223
4773.176 | 714.0183
4774.176 | 718.0174
4775.176 | 719.2726
4776.176 | 717.4694
4777.176 | 713.6382
4778.176 | 707.557
4779.176 | 701.6982
4780.176 | 699.2357
4781.176 | 695.29
4782.176 | 691.9881
4783.176 | 697.8201
4784.176 | 697.544
4785.176 | 692.5279
4786.176 | 694.8604
4787.176 | 694.9084
4788.176 | 690.9266
4789.176 | 692.4263
4790.176 | 695.2155
4791.176 | 696.878
4792.176 | 697.008
4793.176 | 698.1774
4794.176 | 697.2785
4795.176 | 698.9143
4796.176 | 697.3319
4797.176 | 700.7463
4798.176 | 703.1747
4799.176 | 709.1341
4800.176 | 713.5958
4801.176 | 713.7149
4802.176 | 716.5229
4803.176 | 715.3042
4804.176 | 717.7598
4805.176 | 711.8673
4806.176 | 711.0546
4807.176 | 714.4601
4808.176 | 711.8215
4809.176 | 709.0099
4810.176 | 707.6734
4811.176 | 708.7371
4812.176 | 708.5659
4813.176 | 714.2657
4814.176 | 718.752
4815.176 | 722.4523
4816.176 | 725.6601
4817.176 | 718.6212
4818.176 | 719.9888
4819.176 | 722.3455
4820.176 | 720.5547
4821.176 | 716.5151
4822.176 | 713.0849
4823.176 | 711.366
4824.176 | 713.6383
4825.176 | 718.102
4826.176 | 718.5932
4827.176 | 715.3949
4828.176 | 712.9196
4829.176 | 712.0786
4830.176 | 712.7549
4831.176 | 714.942
4832.176 | 719.7543
4833.176 | 722.3337
4834.176 | 721.5207
4835.176 | 722.2698
4836.176 | 720.6278
4837.176 | 719.8322
4838.176 | 722.0899
4839.176 | 724.4863
4840.176 | 728.869
4841.176 | 725.2149
4842.176 | 720.5419
4843.176 | 722.1776
4844.176 | 727.529
4845.176 | 726.7428
4846.176 | 728.3594
4847.176 | 732.0607
4848.176 | 737.6917
4849.176 | 733.6451
4850.176 | 735.1253
4851.176 | 741.5011
4852.176 | 742.0115
4853.176 | 742.446
4854.176 | 742.2338
4855.176 | 743.7486
4856.176 | 745.497
4857.176 | 741.9719
4858.176 | 739.2396
4859.176 | 742.2753
4860.176 | 741.8969
4861.176 | 741.1603
4862.176 | 739.7849
4863.176 | 729.9139
4864.176 | 728.0387
4865.176 | 733.3724
4866.176 | 732.8472
4867.176 | 731.1499
4868.176 | 725.4383
4869.176 | 726.8891
4870.176 | 722.6716
4871.176 | 725.6218
4872.176 | 729.6217
4873.176 | 730.8581
4874.176 | 733.703
4875.176 | 737.7555
4876.176 | 735.3575
4877.176 | 737.4414
4878.176 | 734.9518
4879.176 | 738.8493
4880.176 | 737.7543
4881.176 | 738.6502
4882.176 | 740.8179
4883.176 | 735.7653
4884.176 | 741.7325
4885.176 | 746.8962
4886.176 | 751.2827
4887.176 | 744.7059
4888.176 | 742.4814
4889.176 | 741.2349
4890.176 | 747.2484
4891.176 | 750.0179
4892.176 | 752.4208
4893.176 | 754.6214
4894.176 | 749.174
4895.176 | 746.4199
4896.176 | 738.6331
4897.176 | 730.2213
4898.176 | 731.7558
4899.176 | 733.1014
4900.176 | 732.8075
4901.176 | 736.2137
4902.176 | 734.5179
4903.176 | 739.733
4904.176 | 738.5119
4905.176 | 743.1657
4906.176 | 740.6904
4907.176 | 744.6759
4908.176 | 739.9585
4909.176 | 738.9719
4910.176 | 744.62
4911.176 | 739.3816
4912.176 | 731.3241
4913.176 | 728.7608
4914.176 | 734.6018
4915.176 | 740.5114
4916.176 | 737.7938
4917.176 | 734.9992
4918.176 | 730.1592
4919.176 | 726.2715
4920.176 | 730.9338
4921.176 | 747.5935
4922.176 | 748.6968
4923.176 | 759.0696
4924.176 | 764.8225
4925.176 | 765.0004
4926.176 | 762.4945
4927.176 | 754.0833
4928.176 | 752.2467
4929.176 | 747.1604
4930.176 | 749.1347
4931.176 | 752.4087
4932.176 | 761.4511
4933.176 | 748.1171
4934.176 | 756.6838
4935.176 | 759.8612
4936.176 | 754.4146
4937.176 | 752.4285
4938.176 | 753.9377
4939.176 | 756.6813
4940.176 | 755.2016
4941.176 | 771.3874
4942.176 | 773.2022
4943.176 | 766.0053
4944.176 | 771.174
4945.176 | 761.1672
4946.176 | 754.0377
4947.176 | 758.7261
4948.176 | 765.9481
4949.176 | 756.2588
4950.176 | 756.4586
4951.176 | 760.1346
4952.176 | 756.3728
4953.176 | 766.8426
4954.176 | 762.4872
4955.176 | 755.7648
4956.176 | 752.4295
4957.176 | 744.2741
4958.176 | 736.6505
4959.176 | 734.7655
4960.176 | 745.4682
4961.176 | 751.9719
4962.176 | 749.2488
4963.176 | 760.6685
4964.176 | 763.7018
4965.176 | 762.5217
4966.176 | 761.5265
4967.176 | 760.2652
4968.176 | 754.9167
4969.176 | 756.3776
4970.176 | 758.9614
4971.176 | 755.9098
4972.176 | 751.5906
4973.176 | 749.4116
4974.176 | 750.8521
4975.176 | 747.125
4976.176 | 751.4402
4977.176 | 754.1086
4978.176 | 755.3118
4979.176 | 753.8922
4980.176 | 747.0035
4981.176 | 741.7293
4982.176 | 730.6502
4983.176 | 729.3275
4984.176 | 725.3083
4985.176 | 722.5968
4986.176 | 725.2349
4987.176 | 729.3468
4988.176 | 732.9513
4989.176 | 732.1457
4990.176 | 744.8239
4991.176 | 752.1195
4992.176 | 756.0024
4993.176 | 751.2079
4994.176 | 751.505
4995.176 | 748.6996
4996.176 | 743.351
4997.176 | 736.8298
4998.176 | 744.4444
4999.176 | 752.7413
5000.176 | 758.0327
5001.176 | 755.7534
5002.176 | 755.0427
5003.176 | 760.466
5004.176 | 766.1495
5005.176 | 764.5302
5006.176 | 769.0072
5007.176 | 770.9869
5008.176 | 756.8545
5009.176 | 745.2512
5010.176 | 744.1904
5011.176 | 740.4583
5012.176 | 742.6309
5013.176 | 738.6519
5014.176 | 732.394
5015.176 | 748.7097
5016.176 | 749.3121
5017.176 | 749.0747
5018.176 | 753.7738
5019.176 | 749.5639
5020.176 | 742.1989
5021.176 | 734.6557
5022.176 | 729.0591
5023.176 | 735.5443
5024.176 | 733.958
5025.176 | 736.3324
5026.176 | 740.5764
5027.176 | 747.2462
5028.176 | 754.4929
5029.176 | 750.4882
5030.176 | 753.2338
5031.176 | 750.2949
5032.176 | 749.9811
5033.176 | 746.6852
5034.176 | 751.5526
5035.176 | 743.12
5036.176 | 739.9056
5037.176 | 745.8325
5038.176 | 745.2605
5039.176 | 746.7344
5040.176 | 743.3704
5041.176 | 739.5032
5042.176 | 736.1779
5043.176 | 738.2813
5044.176 | 750.1686
5045.176 | 743.1934
5046.176 | 743.0185
5047.176 | 742.4452
5048.176 | 753.4882
5049.176 | 758.0963
5050.176 | 749.6108
5051.176 | 751.5645
5052.176 | 763.0545
5053.176 | 754.0623
5054.176 | 744.3054
5055.176 | 750.2943
5056.176 | 746.1823
5057.176 | 736.9221
5058.176 | 734.6057
5059.176 | 739.1136
5060.176 | 750.5199
5061.176 | 758.0908
5062.176 | 765.7455
5063.176 | 749.779
5064.176 | 737.9363
5065.176 | 733.5303
5066.176 | 745.0404
5067.176 | 745.9067
5068.176 | 753.0646
5069.176 | 759.3651
5070.176 | 754.9832
5071.176 | 754.5195
5072.176 | 766.566
5073.176 | 759.1168
5074.176 | 760.209
5075.176 | 755.9113
5076.176 | 751.3095
5077.176 | 744.5238
5078.176 | 748.5152
5079.176 | 755.4084
5080.176 | 747.0351
5081.176 | 751.3527
5082.176 | 755.6425
5083.176 | 758.2277
5084.176 | 753.8502
5085.176 | 759.1317
5086.176 | 765.523
5087.176 | 757.1381
5088.176 | 753.6527
5089.176 | 760.1086
5090.176 | 755.4202
5091.176 | 763.1641
5092.176 | 759.9021
5093.176 | 750.9425
5094.176 | 756.1667
5095.176 | 756.0919
5096.176 | 762.9278
5097.176 | 755.0772
5098.176 | 750.6896
5099.176 | 741.6671
5100.176 | 749.4571
5101.176 | 751.6239
5102.176 | 756.1854
5103.176 | 761.6673
5104.176 | 762.5497
5105.176 | 758.081
5106.176 | 762.7987
5107.176 | 759.7335
5108.176 | 755.1314
5109.176 | 750.2554
5110.176 | 748.3028
5111.176 | 739.9758
5112.176 | 730.5782
5113.176 | 720.5393
5114.176 | 723.9097
5115.176 | 721.1864
5116.176 | 725.3126
5117.176 | 718.0837
5118.176 | 726.9232
5119.176 | 723.9237
5120.176 | 723.8171
5121.176 | 718.5234
5122.176 | 725.3009
5123.176 | 726.6093
5124.176 | 718.114
5125.176 | 713.0295
5126.176 | 713.8973
5127.176 | 719.4425
5128.176 | 724.4733
5129.1917 | 725.4814
5130.176 | 721.6644
5131.176 | 723.9347
5132.176 | 717.5627
5133.176 | 714.3365
5134.1917 | 708.5074
5135.1917 | 702.6339
5136.176 | 696.1722
5137.176 | 696.6447
5138.176 | 699.4291
5139.176 | 704.1855
5140.176 | 712.2658
5141.176 | 702.726
5142.176 | 709.9646
5143.176 | 713.2018
5144.176 | 712.445
5145.176 | 709.15
5146.176 | 702.2554
5147.176 | 698.8573
5148.176 | 706.5163
5149.176 | 718.7164
5150.176 | 706.9737
5151.176 | 696.7519
5152.176 | 695.3139
5153.176 | 702.4681
5154.176 | 708.4127
5155.176 | 706.9603
5156.176 | 713.2258
5157.176 | 722.9557
5158.176 | 723.1171
5159.176 | 724.7338
5160.176 | 715.9761
5161.176 | 713.2603
5162.176 | 706.4339
5163.176 | 702.5098
5164.176 | 704.9827
5165.176 | 709.6085
5166.176 | 704.5217
5167.176 | 701.6186
5168.176 | 703.5392
5169.176 | 699.8107
5170.176 | 701.8834
5171.176 | 712.3053
5172.176 | 713.4265
5173.176 | 708.5592
5174.176 | 699.3508
5175.176 | 700.3558
5176.176 | 704.0625
5177.176 | 702.8446
5178.176 | 703.6709
5179.176 | 701.2108
5180.176 | 701.407
5181.176 | 714.6499
5182.176 | 714.0175
5183.176 | 716.0426
5184.176 | 722.8413
5185.176 | 717.822
5186.176 | 714.1686
5187.176 | 720.1969
5188.176 | 725.3298
5189.176 | 728.0754
5190.176 | 729.3412
5191.176 | 730.6815
5192.176 | 732.1673
5193.176 | 728.1744
5194.176 | 720.1222
5195.176 | 715.4055
5196.176 | 721.0411
5197.176 | 726.6208
5198.176 | 720.4926
5199.176 | 721.8526
5200.176 | 731.1214
5201.176 | 728.7692
5202.176 | 727.9865
5203.176 | 727.4148
5204.176 | 724.659
5205.176 | 732.4831
5206.176 | 728.9708
5207.176 | 727.4009
5208.176 | 732.0215
5209.176 | 731.1011
5210.176 | 721.1992
5211.176 | 709.1529
5212.176 | 712.7188
5213.176 | 709.4597
5214.176 | 714.2836
5215.176 | 718.3372
5216.176 | 718.2349
5217.176 | 712.127
5218.176 | 707.7873
5219.176 | 705.8902
5220.176 | 705.1023
5221.176 | 713.4211
5222.176 | 706.3588
5223.176 | 705.9629
5224.176 | 709.5157
5225.176 | 708.489
5226.176 | 710.2425
5227.176 | 700.48
5228.176 | 694.1045
5229.176 | 700.6033
5230.176 | 704.6684
5231.176 | 711.7172
5232.176 | 715.1401
5233.176 | 712.1514
5234.176 | 703.8907
5235.176 | 694.6704
5236.176 | 700.0607
5237.176 | 702.4481
5238.176 | 706.9251
5239.176 | 702.5159
5240.176 | 700.2271
5241.176 | 695.8244
5242.176 | 701.0972
5243.176 | 697.0896
5244.176 | 689.3851
5245.176 | 689.1008
5246.176 | 685.8644
5247.176 | 680.9621
5248.176 | 684.6076
5249.176 | 686.65
5250.176 | 686.6158
5251.176 | 686.253
5252.176 | 687.7429
5253.176 | 689.8746
5254.176 | 684.3357
5255.176 | 680.0097
5256.176 | 680.7031
5257.176 | 675.9838
5258.176 | 670.7613
5259.176 | 664.88
5260.176 | 661.3881
5261.176 | 660.0565
5262.176 | 656.2259
5263.176 | 657.8778
5264.176 | 655.7322
5265.176 | 658.0751
5266.176 | 662.3903
5267.176 | 671.0371
5268.176 | 684.1108
5269.176 | 692.2408
5270.176 | 698.1269
5271.176 | 695.054
5272.176 | 702.2013
5273.176 | 705.0109
5274.176 | 717.4545
5275.176 | 721.3073
5276.176 | 717.5314
5277.176 | 719.7173
5278.176 | 730.1953
5279.176 | 733.0541
5280.176 | 725.1369
5281.176 | 724.1598
5282.176 | 736.1771
5283.176 | 730.6856
5284.176 | 725.1661
5285.176 | 724.7024
5286.176 | 718.0958
5287.176 | 716.7475
5288.176 | 712.2176
5289.176 | 710.815
5290.176 | 700.9558
5291.176 | 696.1098
5292.176 | 701.0762
5293.176 | 704.8058
5294.176 | 694.5166
5295.176 | 684.4701
5296.176 | 677.6183
5297.176 | 681.6343
5298.176 | 680.1293
5299.176 | 674.8616
5300.176 | 676.0341
5301.176 | 671.1245
5302.176 | 666.5719
5303.176 | 658.6232
5304.176 | 658.5219
5305.1917 | 652.6406
5306.176 | 651.0164
5307.176 | 664.1425
5308.176 | 670.3617
5309.176 | 678.4569
5310.176 | 678.4971
5311.176 | 684.3793
5312.176 | 682.799
5313.176 | 682.733
5314.176 | 684.826
5315.176 | 684.9119
5316.176 | 680.7475
5317.176 | 677.7535
5318.176 | 681.8602
5319.176 | 676.9717
5320.176 | 675.9318
5321.176 | 671.6169
5322.176 | 670.9785
5323.176 | 679.154
5324.176 | 684.4003
5325.176 | 680.028
5326.176 | 675.2274
5327.176 | 676.4434
5328.176 | 681.5888
5329.176 | 676.4248
5330.176 | 675.1613
5331.176 | 676.2236
5332.176 | 673.9118
5333.176 | 674.3557
5334.176 | 678.2214
5335.1917 | 678.1397
5336.176 | 679.0424
5337.176 | 673.9485
5338.176 | 669.6292
5339.176 | 666.7466
5340.176 | 665.5951
5341.176 | 663.3651
5342.176 | 665.2752
5343.176 | 665.848
5344.176 | 667.6908
5345.176 | 668.162
5346.176 | 668.515
5347.176 | 666.3827
5348.176 | 664.7628
5349.176 | 666.6849
5350.176 | 669.4247
5351.176 | 673.866
5352.176 | 676.7149
5353.176 | 675.455
5354.176 | 674.6423
5355.176 | 675.3136
5356.176 | 676.6812
5357.176 | 674.5165
5358.176 | 683.841
5359.176 | 684.8474
5360.176 | 686.2646
5361.176 | 684.9521
5362.176 | 682.0092
5363.176 | 680.1218
5364.176 | 677.642
5365.176 | 685.2483
5366.176 | 685.9855
5367.176 | 684.2016
5368.176 | 690.1421
5369.176 | 679.4115
5370.176 | 671.2248
5371.176 | 667.6099
5372.176 | 663.3695
5373.176 | 660.1727
5374.176 | 655.9303
5375.176 | 652.498
5376.176 | 665.6254
5377.176 | 664.5298
5378.176 | 660.1514
5379.176 | 655.2246
5380.176 | 651.8583
5381.176 | 647.9013
5382.176 | 646.684
5383.176 | 645.8521
5384.176 | 647.6275
5385.176 | 652.4593
5386.176 | 657.7735
5387.176 | 656.4718
5388.176 | 654.9173
5389.176 | 652.021
5390.176 | 646.7803
5391.176 | 642.2566
5392.176 | 636.855
5393.176 | 629.9676
5394.176 | 628.164
5395.1917 | 626.7738
5396.176 | 624.3854
5397.176 | 624.2422
5398.176 | 625.5476
5399.176 | 625.5018
5400.176 | 628.4
5401.176 | 633.2912
5402.176 | 633.3644
5403.176 | 633.4641
5404.176 | 631.9876
5405.176 | 633.5908
5406.176 | 637.0304
5407.176 | 640.4693
5408.176 | 641.0646
5409.176 | 640.3291
5410.176 | 638.3274
5411.176 | 634.5724
5412.176 | 632.5591
5413.176 | 630.6505
5414.176 | 628.9552
5415.176 | 625.9515
5416.176 | 626.8648
5417.176 | 631.7137
5418.176 | 631.1735
5419.176 | 631.1484
5420.176 | 629.6862
5421.176 | 629.6859
5422.176 | 631.7513
5423.176 | 634.2264
5424.176 | 640.2845
5425.1917 | 642.2722
5426.176 | 642.6729
5427.176 | 653.3245
5428.176 | 658.8434
5429.176 | 655.3326
5430.176 | 655.3263
5431.176 | 654.627
5432.176 | 650.1833
5433.176 | 653.9769
5434.176 | 647.2271
5435.176 | 641.8753
5436.176 | 641.575
5437.176 | 640.3332
5438.176 | 643.4809
5439.176 | 647.528
5440.176 | 646.585
5441.176 | 644.4074
5442.176 | 648.6572
5443.176 | 657.2143
5444.176 | 665.8608
5445.176 | 664.974
5446.176 | 662.9013
5447.176 | 665.1479
5448.176 | 662.5998
5449.176 | 660.9311
5450.176 | 661.7591
5451.176 | 668.5756
5452.176 | 668.652
5453.176 | 680.9253
5454.176 | 680.5855
5455.176 | 676.5141
5456.176 | 672.562
5457.176 | 667.8987
5458.176 | 665.0449
5459.176 | 661.9349
5460.176 | 658.2914
5461.176 | 662.2206
5462.176 | 665.5998
5463.176 | 664.3011
5464.176 | 660.1254
5465.176 | 656.5579
5466.176 | 655.3632
5467.176 | 651.664
5468.176 | 654.9963
5469.176 | 659.3556
5470.176 | 656.8216
5471.176 | 653.7619
5472.176 | 658.9807
5473.176 | 658.2926
5474.176 | 654.4849
5475.176 | 651.1385
5476.176 | 651.1859
5477.176 | 655.4201
5478.176 | 659.6572
5479.176 | 660.3134
5480.176 | 659.3155
5481.176 | 661.7354
5482.176 | 661.1002
5483.176 | 655.9703
5484.176 | 654.5084
5485.176 | 660.4887
5486.176 | 662.7884
5487.176 | 666.2564
5488.176 | 668.5325
5489.176 | 664.7829
5490.176 | 665.6354
5491.176 | 662.5175
5492.176 | 659.8835
5493.176 | 662.745
5494.176 | 662.5361
5495.176 | 653.3028
5496.176 | 646.0009
5497.176 | 642.7997
5498.176 | 651.0724
5499.176 | 643.6708
5500.176 | 638.8525
5501.176 | 635.1769
5502.176 | 630.6913
5503.176 | 626.701
5504.176 | 627.3417
5505.176 | 632.3659
5506.176 | 633.8808
5507.176 | 632.984
5508.176 | 632.7714
5509.176 | 633.2112
5510.176 | 635.7376
5511.176 | 638.4007
5512.176 | 638.1257
5513.176 | 637.4939
5514.176 | 640.6681
5515.176 | 642.6113
5516.176 | 643.4326
5517.176 | 642.8609
5518.176 | 641.7596
5519.176 | 646.437
5520.176 | 646.638
5521.176 | 649.729
5522.176 | 651.0604
5523.176 | 646.8253
5524.176 | 648.4302
5525.176 | 660.387
5526.176 | 666.4384
5527.176 | 661.2042
5528.176 | 660.4977
5529.176 | 663.3155
5530.176 | 662.1492
5531.176 | 658.2068
5532.176 | 652.7015
5533.176 | 649.9526
5534.176 | 646.5635
5535.176 | 651.8024
5536.176 | 652.4315
5537.176 | 646.0952
5538.176 | 639.438
5539.176 | 634.963
5540.176 | 632.2548
5541.176 | 631.4449
5542.176 | 629.7567
5543.176 | 625.3687
5544.176 | 620.9136
5545.176 | 617.2072
5546.176 | 614.8253
5547.176 | 611.1087
5548.176 | 609.0769
5549.176 | 606.7013
5550.176 | 605.4764
5551.176 | 604.975
5552.176 | 602.5136
5553.176 | 600.5179
5554.176 | 599.5544
5555.176 | 596.2482
5556.176 | 595.1318
5557.176 | 594.4679
5558.176 | 595.0902
5559.176 | 594.7701
5560.176 | 593.258
5561.176 | 592.3446
5562.176 | 592.7333
5563.176 | 595.3957
5564.176 | 597.8141
5565.176 | 597.5821
5566.176 | 599.5638
5567.176 | 601.1098
5568.176 | 601.4755
5569.176 | 603.2016
5570.176 | 605.7952
5571.176 | 608.9438
5572.176 | 611.9234
5573.176 | 612.0817
5574.176 | 609.0327
5575.176 | 606.3247
5576.176 | 604.0385
5577.176 | 604.7374
5578.176 | 603.7641
5579.176 | 604.8791
5580.176 | 608.1698
5581.176 | 610.3795
5582.176 | 614.4594
5583.176 | 620.7066
5584.176 | 622.315
5585.176 | 621.7136
5586.176 | 619.079
5587.176 | 615.3989
5588.176 | 611.6797
5589.176 | 608.2758
5590.176 | 608.4192
5591.176 | 608.2119
5592.176 | 606.0395
5593.176 | 605.0791
5594.176 | 603.5525
5595.176 | 602.6941
5596.176 | 602.5175
5597.176 | 603.0985
5598.176 | 603.0247
5599.176 | 604.8499
5600.176 | 606.098
5601.176 | 608.4845
5602.176 | 609.3729
5603.176 | 608.5918
5604.176 | 609.9774
5605.176 | 608.6784
5606.176 | 608.1523
5607.176 | 608.8619
5608.176 | 608.4911
5609.176 | 608.2882
5610.176 | 607.8757
5611.176 | 605.9325
5612.176 | 607.4081
5613.176 | 605.9248
5614.176 | 605.0902
5615.176 | 605.8575
5616.176 | 603.949
5617.176 | 601.2089
5618.176 | 601.4867
5619.176 | 603.9064
5620.176 | 603.4928
5621.176 | 603.3086
5622.176 | 602.0193
5623.176 | 603.815
5624.176 | 609.0102
5625.176 | 609.9762
5626.176 | 611.3094
5627.2073 | 610.0857
5628.176 | 605.8199
5629.176 | 603.3023
5630.176 | 601.6701
5631.176 | 599.2214
5632.176 | 597.702
5633.176 | 598.3581
5634.176 | 597.2804
5635.176 | 596.2708
5636.176 | 594.8609
5637.176 | 595.8014
5638.176 | 594.9478
5639.176 | 592.9868
5640.176 | 590.9855
5641.176 | 592.3437
5642.176 | 590.2478
5643.176 | 588.4708
5644.176 | 589.9795
5645.176 | 590.52
5646.176 | 591.5945
5647.176 | 591.2283
5648.176 | 588.4864
5649.176 | 585.5551
5650.176 | 588.1345
5651.176 | 589.1462
5652.176 | 588.8142
5653.176 | 588.9618
5654.176 | 592.1314
5655.176 | 596.527
5656.176 | 598.9525
5657.176 | 601.038
5658.176 | 599.826
5659.176 | 598.1286
5660.176 | 597.8892
5661.176 | 599.878
5662.176 | 601.1849
5663.176 | 600.6964
5664.176 | 601.0993
5665.176 | 597.9475
5666.176 | 595.5131
5667.176 | 593.6305
5668.176 | 593.4736
5669.176 | 592.9331
5670.176 | 595.6819
5671.176 | 596.3231
5672.176 | 597.0534
5673.176 | 597.5751
5674.176 | 598.0698
5675.176 | 597.085
5676.176 | 595.9031
5677.176 | 596.0134
5678.176 | 596.6126
5679.176 | 596.3579
5680.176 | 594.6464
5681.176 | 594.7521
5682.176 | 592.1495
5683.176 | 589.9955
5684.176 | 588.283
5685.176 | 587.7329
5686.176 | 584.5782
5687.176 | 582.3841
5688.176 | 582.5705
5689.176 | 583.2355
5690.176 | 585.695
5691.176 | 584.6158
5692.176 | 585.8051
5693.176 | 584.7822
5694.176 | 584.2973
5695.176 | 584.5862
5696.176 | 584.5266
5697.176 | 582.4243
5698.176 | 582.7408
5699.176 | 583.2726
5700.176 | 582.6414
5701.176 | 581.1859
5702.176 | 581.8143
5703.176 | 580.3423
5704.176 | 577.9236
5705.176 | 578.5098
5706.176 | 577.5692
5707.176 | 576.4753
5708.176 | 575.4357
5709.176 | 575.5634
5710.176 | 576.3179
5711.176 | 577.5387
5712.176 | 576.0191
5713.176 | 573.6166
5714.176 | 574.3365
5715.176 | 575.3575
5716.176 | 577.214
5717.176 | 577.1481
5718.176 | 579.6397
5719.176 | 583.9079
5720.176 | 587.4244
5721.176 | 585.5754
5722.176 | 583.8637
5723.176 | 581.45
5724.176 | 581.5635
5725.176 | 582.7797
5726.176 | 587.7842
5727.176 | 586.5306
5728.176 | 584.0139
5729.176 | 583.2454
5730.176 | 580.2661
5731.176 | 581.7263
5732.176 | 583.8635
5733.176 | 587.6169
5734.176 | 588.6988
5735.176 | 589.8237
5736.176 | 589.4633
5737.176 | 589.6408
5738.176 | 589.424
5739.176 | 589.3962
5740.176 | 589.2656
5741.176 | 592.1664
5742.176 | 593.9743
5743.176 | 593.0752
5744.176 | 590.3456
5745.176 | 589.7431
5746.176 | 590.5413
5747.176 | 589.9881
5748.176 | 588.024
5749.176 | 586.7447
5750.176 | 587.3138
5751.176 | 587.3562
5752.176 | 587.3843
5753.176 | 585.8701
5754.176 | 582.3081
5755.176 | 579.2836
5756.176 | 576.0368
5757.176 | 575.2002
5758.176 | 572.2318
5759.176 | 572.0945
5760.176 | 571.6411
5761.176 | 571.9731
5762.176 | 570.3157
5763.176 | 572.2166
5764.176 | 572.3042
5765.176 | 577.0733
5766.176 | 578.5873
5767.176 | 581.1496
5768.176 | 583.9693
5769.176 | 589.3841
5770.176 | 592.5465
5771.176 | 594.4051
5772.176 | 592.5914
5773.176 | 592.6128
5774.176 | 592.0156
5775.176 | 594.0959
5776.176 | 596.2682
5777.176 | 596.7726
5778.176 | 595.8945
5779.176 | 590.6917
5780.176 | 586.9545
5781.176 | 586.3831
5782.176 | 584.8339
5783.176 | 583.8804
5784.176 | 580.7551
5785.176 | 578.8928
5786.176 | 576.4396
5787.176 | 577.3112
5788.176 | 575.1845
5789.176 | 574.2417
5790.176 | 574.5281
5791.176 | 572.7727
5792.176 | 573.3928
5793.176 | 572.6507
5794.176 | 570.2077
5795.176 | 570.1978
5796.176 | 570.5301
5797.176 | 568.0462
5798.176 | 566.7758
5799.176 | 567.8883
5800.176 | 567.5786
5801.176 | 566.021
5802.176 | 565.0007
5803.176 | 565.6787
5804.176 | 565.4521
5805.176 | 565.4989
5806.176 | 567.145
5807.176 | 566.1618
5808.176 | 567.1209
5809.176 | 567.8367
5810.176 | 569.1864
5811.176 | 567.6543
5812.176 | 568.4282
5813.176 | 569.5321
5814.176 | 574.24
5815.176 | 576.0906
5816.176 | 577.1097
5817.176 | 575.4479
5818.176 | 575.5546
5819.176 | 575.4486
5820.176 | 573.1911
5821.176 | 576.1667
5822.176 | 579.5074
5823.176 | 581.1594
5824.176 | 581.7257
5825.176 | 581.1376
5826.176 | 584.002
5827.176 | 583.3755
5828.176 | 581.7119
5829.176 | 580.3669
5830.176 | 581.3627
5831.176 | 582.9099
5832.176 | 582.7572
5833.176 | 582.8819
5834.176 | 583.4292
5835.176 | 584.7485
5836.176 | 587.8804
5837.176 | 588.4972
5838.176 | 587.4878
5839.176 | 583.0351
5840.176 | 583.3359
5841.176 | 584.935
5842.176 | 587.3289
5843.176 | 585.521
5844.176 | 583.6576
5845.176 | 582.4102
5846.176 | 580.7543
5847.176 | 580.3975
5848.176 | 579.4217
5849.176 | 575.9739
5850.176 | 572.2608
5851.176 | 570.8922
5852.176 | 572.8104
5853.176 | 571.0763
5854.176 | 570.002
5855.176 | 569.2085
5856.176 | 568.728
5857.176 | 568.5675
5858.176 | 568.6901
5859.176 | 568.2565
5860.176 | 567.2581
5861.176 | 567.3574
5862.176 | 567.2929
5863.176 | 566.4644
5864.176 | 567.7534
5865.176 | 568.2634
5866.176 | 568.846
5867.176 | 566.9703
5868.176 | 565.8309
5869.176 | 566.558
5870.176 | 567.3952
5871.176 | 566.9009
5872.176 | 567.408
5873.176 | 568.3889
5874.176 | 567.5641
5875.176 | 567.0333
5876.176 | 568.7848
5877.176 | 570.3124
5878.176 | 571.6255
5879.176 | 572.2108
5880.176 | 573.086
5881.176 | 573.1089
5882.176 | 576.0422
5883.176 | 572.7238
5884.176 | 571.0165
5885.176 | 569.7705
5886.176 | 570.7597
5887.176 | 571.9938
5888.176 | 571.0308
5889.176 | 569.6791
5890.176 | 569.7581
5891.176 | 570.7416
5892.176 | 573.9049
5893.176 | 574.8354
5894.176 | 576.63
5895.176 | 575.5569
5896.176 | 574.8072
5897.176 | 573.6927
5898.176 | 572.9785
5899.176 | 572.5837
5900.176 | 570.4431
5901.176 | 569.1709
5902.176 | 569.6455
5903.176 | 568.3669
5904.176 | 567.1783
5905.176 | 566.3745
5906.176 | 566.7212
5907.176 | 566.0068
5908.176 | 564.136
5909.176 | 563.1366
5910.176 | 562.5234
5911.176 | 561.457
5912.176 | 560.4004
5913.176 | 559.7369
5914.176 | 558.0716
5915.176 | 556.839
5916.176 | 555.7377
5917.176 | 556.0153
5918.176 | 556.0926
5919.176 | 555.8794
5920.176 | 555.2386
5921.176 | 554.1103
5922.176 | 554.5118
5923.176 | 554.186
5924.176 | 551.3175
5925.176 | 550.2284
5926.176 | 550.9256
5927.176 | 551.4948
5928.176 | 552.7091
5929.176 | 553.5354
5930.176 | 550.8188
5931.176 | 551.6236
5932.176 | 551.7657
5933.176 | 552.3872
5934.176 | 552.0994
5935.176 | 551.9443
5936.176 | 552.4281
5937.176 | 554.1596
5938.176 | 555.6467
5939.176 | 558.2275
5940.176 | 560.7425
5941.176 | 563.1249
5942.176 | 562.0127
5943.176 | 562.2011
5944.176 | 563.9763
5945.176 | 564.5574
5946.176 | 563.7111
5947.176 | 561.5339
5948.176 | 560.1058
5949.176 | 559.4197
5950.176 | 561.5804
5951.176 | 562.1855
5952.176 | 560.8128
5953.176 | 558.9102
5954.176 | 557.4253
5955.176 | 555.9607
5956.176 | 554.4685
5957.176 | 553.7857
5958.176 | 554.7096
5959.176 | 556.4168
5960.176 | 559.2348
5961.176 | 560.375
5962.176 | 560.0928
5963.176 | 559.3915
5964.176 | 561.104
5965.176 | 563.0005
5966.176 | 562.7371
5967.176 | 562.4633
5968.176 | 561.1938
5969.176 | 560.4382
5970.176 | 559.2599
5971.176 | 559.6979
5972.176 | 559.3813
5973.176 | 558.8416
5974.176 | 557.1464
5975.176 | 556.0677
5976.176 | 556.3101
5977.176 | 555.7457
5978.176 | 556.1517
5979.176 | 557.2982
5980.176 | 557.6681
5981.176 | 556.4484
5982.176 | 557.0793
5983.176 | 558.0903
5984.176 | 559.0111
5985.176 | 559.8614
5986.176 | 560.3197
5987.176 | 558.996
5988.176 | 558.9716
5989.176 | 558.5617
5990.176 | 559.3354
5991.176 | 557.9599
5992.176 | 557.6794
5993.176 | 560.4002
5994.176 | 562.6438
5995.176 | 562.8874
5996.176 | 564.6928
5997.176 | 566.121
5998.176 | 566.6551
5999.176 | 566.8221
6000.1917 | 567.5122
6001.176 | 563.735
6002.176 | 563.4433
6003.176 | 562.4202
6004.176 | 561.7052
6005.176 | 558.8905
6006.176 | 559.4121
6007.176 | 559.1898
6008.176 | 559.257
6009.176 | 558.7024
6010.176 | 558.6201
6011.176 | 558.3603
6012.176 | 558.3686
6013.176 | 558.7782
6014.176 | 558.8593
6015.176 | 560.4518
6016.176 | 560.9959
6017.176 | 561.3329
6018.176 | 563.3967
6019.176 | 564.5219
6020.176 | 565.6381
6021.176 | 564.8835
6022.176 | 563.7778
6023.176 | 562.0157
6024.176 | 558.773
6025.176 | 558.1242
6026.176 | 556.6726
6027.176 | 557.0106
6028.176 | 557.8688
6029.176 | 557.5742
6030.176 | 557.2472
6031.176 | 557.0294
6032.176 | 557.2869
6033.176 | 558.0193
6034.176 | 555.7542
6035.176 | 554.4981
6036.176 | 554.7367
6037.176 | 555.7604
6038.176 | 555.6179
6039.176 | 554.2558
6040.176 | 552.8821
6041.176 | 552.3065
6042.176 | 551.5034
6043.176 | 551.3527
6044.176 | 552.3809
6045.176 | 554.8613
6046.176 | 555.776
6047.176 | 554.3028
6048.176 | 554.6844
6049.176 | 556.8571
6050.176 | 557.0758
6051.176 | 554.4247
6052.176 | 552.84
6053.176 | 553.8261
6054.176 | 555.3142
6055.176 | 555.9217
6056.176 | 555.8742
6057.176 | 554.8741
6058.176 | 555.6571
6059.176 | 556.7848
6060.176 | 557.8083
6061.176 | 558.2417
6062.176 | 557.6734
6063.176 | 556.7474
6064.176 | 555.8249
6065.176 | 553.7191
6066.176 | 552.3729
6067.176 | 550.4143
6068.176 | 547.2636
6069.176 | 545.896
6070.176 | 543.5745
6071.176 | 541.8485
6072.176 | 541.9492
6073.176 | 540.6125
6074.176 | 542.4257
6075.176 | 544.4649
6076.176 | 546.2142
6077.176 | 547.4258
6078.176 | 548.0823
6079.176 | 546.756
6080.176 | 545.4494
6081.176 | 546.4676
6082.176 | 547.7316
6083.176 | 546.4669
6084.176 | 548.0226
6085.176 | 547.7978
6086.176 | 546.6979
6087.176 | 546.5711
6088.176 | 547.3349
6089.176 | 547.2302
6090.176 | 546.9635
6091.176 | 546.7064
6092.176 | 549.2122
6093.176 | 551.09
6094.176 | 551.8114
6095.176 | 551.7104
6096.176 | 551.7508
6097.176 | 549.0524
6098.176 | 546.9051
6099.176 | 546.5094
6100.176 | 547.2098
6101.176 | 547.4034
6102.176 | 546.5223
6103.176 | 545.9271
6104.176 | 544.6784
6105.176 | 544.9988
6106.176 | 543.8077
6107.176 | 542.6378
6108.176 | 542.0928
6109.176 | 541.3171
6110.176 | 539.9963
6111.176 | 541.1584
6112.176 | 541.6616
6113.176 | 541.5569
6114.176 | 542.116
6115.176 | 544.6223
6116.176 | 546.5033
6117.176 | 546.1793
6118.176 | 544.5484
6119.176 | 543.6661
6120.176 | 543.2542
6121.176 | 541.6674
6122.176 | 540.2616
6123.176 | 540.7482
6124.176 | 541.635
6125.176 | 543.5266
6126.176 | 545.1653
6127.176 | 545.9298
6128.176 | 546.3925
6129.176 | 548.2926
6130.176 | 551.18
6131.176 | 551.4296
6132.176 | 552.6468
6133.176 | 553.3569
6134.176 | 553.4352
6135.176 | 552.1275
6136.176 | 551.3021
6137.1917 | 550.7713
6138.176 | 551.0279
6139.176 | 552.4651
6140.176 | 554.9209
6141.176 | 556.4001
6142.176 | 557.0499
6143.176 | 557.3005
6144.176 | 554.9233
6145.176 | 552.9857
6146.176 | 552.2193
6147.176 | 551.62
6148.176 | 548.1785
6149.176 | 548.1484
6150.176 | 548.7558
6151.176 | 548.0522
6152.176 | 547.7233
6153.176 | 545.6389
6154.176 | 542.3451
6155.176 | 540.1552
6156.176 | 540.1238
6157.176 | 538.9842
6158.176 | 540.0352
6159.176 | 540.2723
6160.176 | 538.7462
6161.176 | 538.1512
6162.176 | 537.7339
6163.176 | 536.9712
6164.176 | 536.3622
6165.176 | 536.184
6166.176 | 534.9614
6167.176 | 533.5512
6168.176 | 532.866
6169.176 | 532.5947
6170.176 | 532.6151
6171.176 | 532.9441
6172.176 | 533.8645
6173.176 | 534.7469
6174.176 | 535.6983
6175.176 | 535.6294
6176.176 | 535.2257
6177.176 | 536.3171
6178.176 | 535.3698
6179.176 | 534.9522
6180.176 | 533.9335
6181.176 | 533.2579
6182.176 | 532.2578
6183.176 | 532.4676
6184.176 | 531.8839
6185.176 | 532.2706
6186.176 | 532.5015
6187.176 | 532.4915
6188.176 | 531.6047
6189.176 | 530.2083
6190.176 | 529.8543
6191.176 | 529.9859
6192.176 | 532.1557
6193.176 | 535.066
6194.176 | 537.8346
6195.176 | 540.102
6196.176 | 538.3028
6197.176 | 537.8529
6198.176 | 537.3888
6199.176 | 537.3226
6200.176 | 538.7003
6201.176 | 538.951
6202.176 | 538.1461
6203.176 | 538.5141
6204.176 | 539.7993
6205.176 | 540.6956
6206.176 | 540.6882
6207.176 | 540.7946
6208.176 | 540.0149
6209.176 | 537.9627
6210.176 | 538.0534
6211.176 | 540.7363
6212.176 | 540.9272
6213.176 | 540.8765
6214.176 | 541.8532
6215.176 | 542.3607
6216.176 | 540.7105
6217.176 | 539.8558
6218.176 | 538.9937
6219.176 | 537.0722
6220.176 | 538.8305
6221.176 | 538.6074
6222.176 | 536.9391
6223.176 | 536.3002
6224.176 | 534.8122
6225.176 | 533.8934
6226.176 | 534.3093
6227.2073 | 537.0852
6228.176 | 537.8204
6229.176 | 537.7881
6230.176 | 537.9088
6231.176 | 537.243
6232.176 | 538.0203
6233.176 | 538.5402
6234.176 | 537.8717
6235.176 | 537.2809
6236.176 | 538.7199
6237.176 | 540.9713
6238.176 | 541.2928
6239.176 | 541.062
6240.176 | 542.0484
6241.176 | 540.2929
6242.176 | 538.4773
6243.176 | 538.1272
6244.176 | 538.1755
6245.176 | 538.4957
6246.176 | 538.4909
6247.176 | 538.0815
6248.176 | 538.8836
6249.176 | 539.1245
6250.176 | 540.2338
6251.176 | 538.8593
6252.176 | 537.3537
6253.176 | 536.0184
6254.176 | 535.7323
6255.176 | 535.0964
6256.176 | 535.0631
6257.176 | 534.1646
6258.176 | 534.792
6259.176 | 535.2216
6260.176 | 533.6056
6261.176 | 534.0616
6262.176 | 533.9813
6263.176 | 533.4192
6264.176 | 532.3717
6265.176 | 532.4844
6266.176 | 533.5372
6267.176 | 534.0553
6268.176 | 533.6522
6269.176 | 533.2077
6270.176 | 531.3856
6271.176 | 529.9979
6272.176 | 528.5362
6273.176 | 528.4266
6274.176 | 529.2298
6275.176 | 527.6527
6276.176 | 527.9145
6277.176 | 526.6298
6278.176 | 527.5972
6279.176 | 527.5113
6280.176 | 528.3156
6281.176 | 530.9653
6282.176 | 533.676
6283.176 | 535.5074
6284.176 | 536.2301
6285.176 | 536.7085
6286.176 | 535.8842
6287.176 | 535.1358
6288.176 | 534.9608
6289.176 | 535.1464
6290.176 | 535.5834
6291.176 | 532.7637
6292.176 | 532.2531
6293.176 | 532.4448
6294.176 | 531.7974
6295.176 | 531.4378
6296.1917 | 530.2525
6297.176 | 530.15
6298.176 | 529.4821
6299.176 | 530.5197
6300.176 | 531.6157
6301.176 | 531.7946
6302.176 | 532.2842
6303.176 | 530.9325
6304.176 | 531.9081
6305.176 | 534.447
6306.176 | 534.9514
6307.176 | 534.3181
6308.176 | 534.8645
6309.176 | 534.178
6310.176 | 533.7034
6311.176 | 533.8131
6312.176 | 531.946
6313.176 | 530.0337
6314.176 | 530.0265
6315.176 | 530.1557
6316.176 | 532.8694
6317.176 | 534.0933
6318.176 | 534.5323
6319.176 | 535.2575
6320.176 | 535.2237
6321.176 | 532.4858
6322.176 | 529.1372
6323.176 | 528.511
6324.176 | 527.255
6325.176 | 528.6695
6326.1917 | 530.9125
6327.176 | 530.5969
6328.176 | 529.1361
6329.176 | 528.2475
6330.176 | 529.9028
6331.176 | 531.7539
6332.176 | 532.9439
6333.176 | 534.1958
6334.176 | 536.9996
6335.176 | 538.0306
6336.176 | 539.4316
6337.176 | 541.4999
6338.176 | 541.1501
6339.176 | 539.7685
6340.176 | 538.7383
6341.176 | 537.2557
6342.176 | 535.6853
6343.176 | 533.0006
6344.176 | 532.9177
6345.176 | 533.7138
6346.176 | 532.9995
6347.176 | 533.6952
6348.176 | 532.7844
6349.176 | 531.698
6350.176 | 530.306
6351.176 | 529.562
6352.176 | 530.6601
6353.176 | 531.4601
6354.176 | 533.233
6355.176 | 533.7566
6356.176 | 533.2171
6357.176 | 533.192
6358.176 | 532.7207
6359.176 | 532.8692
6360.176 | 532.9919
6361.176 | 533.6096
6362.176 | 534.5104
6363.176 | 534.2767
6364.176 | 534.4168
6365.176 | 532.6682
6366.176 | 530.5367
6367.176 | 529.9983
6368.176 | 529.2859
6369.176 | 528.6278
6370.176 | 526.8159
6371.176 | 526.5844
6372.176 | 526.5235
6373.176 | 527.0452
6374.176 | 527.246
6375.176 | 527.8727
6376.176 | 529.2962
6377.176 | 530.2351
6378.176 | 530.1368
6379.176 | 530.7127
6380.176 | 529.7176
6381.176 | 530.8325
6382.176 | 532.4745
6383.176 | 535.6262
6384.176 | 535.9419
6385.176 | 536.1775
6386.176 | 536.4444
6387.176 | 534.6202
6388.176 | 534.5322
6389.176 | 536.7231
6390.176 | 538.0587
6391.176 | 537.0797
6392.176 | 536.5222
6393.176 | 535.2208
6394.176 | 533.4168
6395.176 | 532.1665
6396.176 | 531.7458
6397.176 | 530.0427
6398.176 | 529.0295
6399.176 | 528.2865
6400.176 | 528.6315
6401.176 | 528.398
6402.176 | 527.1606
6403.176 | 526.8547
6404.176 | 526.4792
6405.176 | 526.2081
6406.176 | 526.4048
6407.176 | 527.1437
6408.176 | 526.9951
6409.176 | 528.163
6410.176 | 528.6845
6411.176 | 530.2077
6412.176 | 533.5569
6413.176 | 536.3952
6414.176 | 538.1436
6415.176 | 537.0133
6416.176 | 535.8535
6417.176 | 534.8326
6418.176 | 534.0162
6419.176 | 533.1904
6420.176 | 532.405
6421.176 | 533.07
6422.176 | 534.5674
6423.176 | 534.3043
6424.176 | 533.7256
6425.176 | 533.4011
6426.176 | 533.557
6427.176 | 533.4645
6428.176 | 533.6519
6429.176 | 533.2905
6430.176 | 532.8814
6431.176 | 532.9236
6432.176 | 532.8138
6433.176 | 532.377
6434.176 | 532.8275
6435.176 | 533.1727
6436.176 | 532.5562
6437.176 | 531.9124
6438.176 | 530.2034
6439.176 | 528.8508
6440.176 | 529.193
6441.176 | 528.4571
6442.176 | 527.5032
6443.176 | 526.2101
6444.176 | 526.331
6445.176 | 526.7615
6446.176 | 527.108
6447.176 | 527.0251
6448.176 | 526.912
6449.176 | 526.0428
6450.176 | 527.5166
6451.176 | 529.4528
6452.176 | 528.7696
6453.176 | 527.9529
6454.176 | 529.181
6455.176 | 530.737
6456.176 | 530.2833
6457.176 | 529.9336
6458.176 | 530.4974
6459.176 | 531.4194
6460.176 | 532.6871
6461.176 | 531.7597
6462.176 | 528.1568
6463.176 | 526.2145
6464.176 | 525.2199
6465.176 | 526.5337
6466.176 | 525.1675
6467.176 | 525.0487
6468.176 | 526.0024
6469.176 | 527.7607
6470.176 | 526.5123
6471.176 | 524.3525
6472.176 | 523.5718
6473.176 | 523.1742
6474.176 | 522.925
6475.176 | 520.465
6476.1917 | 520.3063
6477.176 | 517.9736
6478.176 | 516.3021
6479.176 | 515.7442
6480.176 | 517.4551
6481.176 | 518.0172
6482.176 | 518.9546
6483.176 | 519.2706
6484.176 | 519.1927
6485.176 | 520.2407
6486.176 | 519.9725
6487.176 | 518.4257
6488.176 | 517.1743
6489.176 | 517.3906
6490.176 | 518.4743
6491.176 | 519.5035
6492.176 | 520.3688
6493.176 | 520.899
6494.176 | 520.6236
6495.176 | 522.2774
6496.176 | 524.1516
6497.176 | 523.9693
6498.176 | 524.4415
6499.176 | 523.751
6500.176 | 523.0337
6501.176 | 521.9761
6502.176 | 521.0137
6503.176 | 520.898
6504.176 | 521.146
6505.176 | 521.3107
6506.176 | 521.653
6507.176 | 521.2029
6508.176 | 521.4514
6509.176 | 521.3694
6510.176 | 521.5281
6511.176 | 521.6899
6512.176 | 520.0278
6513.176 | 520.2914
6514.176 | 520.8862
6515.176 | 518.5399
6516.176 | 519.1255
6517.176 | 517.9009
6518.176 | 516.006
6519.176 | 515.5842
6520.176 | 515.7538
6521.176 | 515.8316
6522.176 | 515.8563
6523.176 | 516.3335
6524.176 | 517.0318
6525.176 | 516.7438
6526.176 | 517.5661
6527.176 | 516.8814
6528.176 | 517.3569
6529.176 | 517.4669
6530.176 | 516.2307
6531.176 | 515.3656
6532.176 | 514.3021
6533.176 | 514.2048
6534.176 | 515.0184
6535.176 | 515.1036
6536.176 | 515.3252
6537.176 | 515.7542
6538.176 | 514.9435
6539.176 | 514.1703
6540.176 | 512.9062
6541.176 | 513.9484
6542.176 | 514.1339
6543.176 | 514.9849
6544.176 | 514.1977
6545.176 | 514.1057
6546.176 | 515.193
6547.176 | 515.4718
6548.176 | 515.8624
6549.176 | 515.7055
6550.176 | 514.3447
6551.176 | 515.0494
6552.176 | 514.8991
6553.176 | 515.2561
6554.176 | 514.8088
6555.176 | 512.5498
6556.176 | 511.022
6557.176 | 512.3884
6558.176 | 513.2989
6559.176 | 512.9877
6560.176 | 515.4892
6561.176 | 514.5936
6562.176 | 515.8942
6563.176 | 515.8434
6564.176 | 516.5668
6565.176 | 515.3357
6566.176 | 514.7785
6567.176 | 514.608
6568.176 | 513.8568
6569.176 | 514.138
6570.176 | 513.9678
6571.176 | 513.9049
6572.176 | 514.7732
6573.176 | 517.2276
6574.176 | 517.9879
6575.176 | 517.6536
6576.176 | 516.4953
6577.176 | 515.6371
6578.176 | 514.4049
6579.176 | 513.4998
6580.176 | 512.4002
6581.176 | 513.6419
6582.176 | 514.128
6583.176 | 512.1552
6584.176 | 512.9409
6585.176 | 513.8
6586.176 | 513.2496
6587.176 | 513.1977
6588.176 | 514.7329
6589.176 | 516.9301
6590.176 | 518.7807
6591.176 | 520.1991
6592.176 | 520.2178
6593.176 | 521.0585
6594.176 | 520.9802
6595.176 | 521.5007
6596.176 | 521.1881
6597.176 | 521.3872
6598.176 | 521.1155
6599.176 | 519.5112
6600.176 | 518.0994
6601.176 | 517.1452
6602.176 | 516.0938
6603.176 | 515.7294
6604.176 | 517.5249
6605.176 | 518.8361
6606.176 | 519.4185
6607.176 | 518.523
6608.176 | 517.9334
6609.176 | 516.5168
6610.176 | 516.1465
6611.176 | 516.8916
6612.176 | 516.978
6613.176 | 517.3656
6614.176 | 517.0017
6615.176 | 515.7134
6616.176 | 515.2253
6617.176 | 514.4384
6618.176 | 513.8657
6619.176 | 512.5249
6620.176 | 513.5882
6621.176 | 514.1851
6622.176 | 515.3002
6623.176 | 517.6317
6624.176 | 517.1592
6625.176 | 518.1011
6626.176 | 519.5794
6627.176 | 519.8987
6628.176 | 520.3078
6629.176 | 521.729
6630.176 | 522.8007
6631.176 | 522.8239
6632.176 | 523.0267
6633.176 | 523.8697
6634.176 | 524.0031
6635.176 | 523.5765
6636.176 | 522.0612
6637.176 | 521.6882
6638.176 | 521.9642
6639.176 | 520.5261
6640.176 | 519.4442
6641.176 | 518.1755
6642.176 | 516.8626
6643.176 | 516.8472
6644.176 | 516.4999
6645.176 | 515.4184
6646.176 | 515.4676
6647.176 | 515.3331
6648.176 | 515.9755
6649.176 | 517.36
6650.176 | 518.7072
6651.176 | 518.8441
6652.176 | 518.5182
6653.176 | 516.85
6654.176 | 516.3023
6655.176 | 517.1379
6656.176 | 518.4904
6657.176 | 516.5565
6658.176 | 516.5445
6659.176 | 517.0479
6660.176 | 517.1465
6661.176 | 516.6052
6662.176 | 517.6378
6663.176 | 518.6637
6664.176 | 518.4959
6665.176 | 518.8931
6666.176 | 519.1652
6667.176 | 520.621
6668.176 | 520.4059
6669.176 | 521.4687
6670.176 | 521.6681
6671.176 | 523.8199
6672.176 | 524.5989
6673.176 | 523.9965
6674.176 | 523.9583
6675.176 | 523.174
6676.176 | 523.1855
6677.176 | 523.9971
6678.176 | 523.6502
6679.176 | 523.9246
6680.176 | 524.9859
6681.176 | 524.3024
6682.176 | 523.4829
6683.176 | 524.572
6684.176 | 524.9172
6685.176 | 523.7855
6686.176 | 521.9521
6687.176 | 521.7251
6688.176 | 522.0248
6689.176 | 521.2834
6690.176 | 520.9281
6691.176 | 520.4025
6692.176 | 521.38
6693.176 | 522.7663
6694.176 | 523.2369
6695.176 | 522.7354
6696.176 | 522.5562
6697.176 | 523.2289
6698.176 | 523.279
6699.176 | 522.2636
6700.176 | 521.8437
6701.176 | 521.2873
6702.176 | 521.8489
6703.176 | 522.0854
6704.176 | 521.5429
6705.176 | 521.8928
6706.176 | 521.3363
6707.176 | 522.5416
6708.176 | 520.8246
6709.176 | 520.5041
6710.176 | 519.4826
6711.176 | 518.2077
6712.176 | 517.3379
6713.176 | 518.2789
6714.176 | 519.2984
6715.176 | 520.9973
6716.1917 | 520.8516
6717.176 | 521.1251
6718.176 | 519.3595
6719.176 | 518.5555
6720.176 | 517.225