## Test Conditions
DESIREE-FIRE Intermediate Scale Test Number 4 - Circuit Simulator Data Only
Test Date: | 2009-11-12
DCSim DAQ Start Time | 10:31
DCSim Time for Synchronization | 10:32
Heat Source Synchronization | 0:55 | minutes:seconds
Heat Source DAQ Start Time | 10:31
Heat Source Start Time | 11:20
DCSim Offset | 0:49 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2940 | seconds
Heat Source Offset | 0:49 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 2935 | seconds
Heat Source Stop Time | 13:12
Test Duration | 1:52 | minutes:seconds
| 6720 | seconds
CT500 Turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the cable tray located in E-Position. These are labeled as "E Position - 3'", "E Position - Middle", "E Position - 7'", respectively.
SWGR Trip | XLPE/CSPE, 7c, 12AWG |  | Cable thermocouples were not used for this test. | Channel 8, 9, and 10 represents the air temperature 3', 5', and 7' down the cable tray located in E-Position. These are labeled as "E Position - 3'", "E Position - Middle", "E Position - 7'", respectively.
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.90625 | 121.8338 | -61.2488 | 60.3333 | -0.25902 | 0.015182 | 0.0056075 | 0.0033582 | 0.053959 | -0.0073316 | 0.068398 | -61.2717 | 60.1959 | -61.2167 | -61.2991 | 60.1273 | 0.29297 | 0.23804 | 0.22888 | 60.3058 | -61.322 | 0.032043 | -0.13733 | -0.022888 | -0.050354 | -0.20599 | -0.073242 | -0.027466 | -0.054931 | 61.4868 | 61.4777 | 121.376 | 121.4447 | -0.022888 | 121.5546 | 61.5417 | -0.073242 | 121.4447 | -0.022888 | 61.5417 | 121.376 | 121.5546 | -121.55 | -121.6553
0.78125 | 121.9116 | -61.1664 | 60.3561 | 0.12245 | 0.018387 | 0.0043259 | 0.0050672 | 0.0546 | -0.0096814 | 0.06733 | -61.3037 | 60.1135 | -61.2762 | -61.322 | 60.0952 | 0.13733 | -0.14648 | 0.068665 | 60.26 | -61.3495 | -0.10986 | -0.24262 | -0.13733 | -0.15564 | -0.26093 | -0.18311 | -0.09613 | -0.027466 | 61.0199 | 61.235 | 121.2616 | 121.2799 | -0.13733 | 121.4264 | 61.3037 | -0.18311 | 121.2799 | -0.13733 | 61.3037 | 121.2616 | 121.4264 | -121.6324 | -121.7056
2.5312 | 121.9208 | -61.2762 | 60.2692 | 0.10719 | 0.019241 | 0.0079575 | 0.0097668 | 0.053959 | -0.0079724 | 0.066689 | -61.4182 | 60.141 | -61.3632 | -61.441 | 59.9854 | -0.004578 | -0.14191 | -0.17853 | 60.2371 | -61.4502 | -0.086975 | -0.12817 | -0.14191 | -0.16479 | -0.28381 | -0.17395 | -0.032043 | -0.054932 | 61.1343 | 61.0977 | 121.2616 | 121.4172 | -0.14191 | 121.5134 | 61.2717 | -0.17395 | 121.4172 | -0.14191 | 61.2717 | 121.2616 | 121.5134 | -121.6324 | -121.7194
4.2188 | 121.9208 | -61.171 | 60.3882 | 0.12245 | 0.016464 | 0.0047531 | 0.0054944 | 0.053746 | -0.0073316 | 0.06733 | -61.3174 | 60.1181 | -61.2762 | -61.3266 | 60.1044 | 0.12817 | -0.12817 | 0.064087 | 60.2325 | -61.3815 | -0.10529 | -0.27008 | -0.14648 | -0.15564 | -0.28381 | -0.21057 | -0.15564 | -0.041199 | 61.0428 | 61.235 | 121.2753 | 121.2891 | -0.14648 | 121.4035 | 61.2991 | -0.21057 | 121.2891 | -0.14648 | 61.2991 | 121.2753 | 121.4035 | -121.6644 | -121.7697
5.9688 | 121.7697 | -61.3037 | 60.3195 | -0.12169 | 0.017318 | 0.0068893 | 0.0078442 | 0.055882 | -0.010963 | 0.068611 | -61.322 | 60.1639 | -61.3174 | -61.3358 | 60.0861 | 0.19684 | 0.041199 | 0.082397 | 60.2554 | -61.377 | -0.013733 | -0.15564 | -0.01831 | -0.032043 | -0.23346 | -0.073242 | -0.064087 | -0.004577 | 61.3449 | 61.3861 | 121.3898 | 121.4676 | -0.01831 | 121.5591 | 61.5005 | -0.073242 | 121.4676 | -0.01831 | 61.5005 | 121.3898 | 121.5591 | -121.637 | -121.6965
7.7188 | 121.8796 | -61.2167 | 60.3149 | 0.17586 | 0.014114 | 0.0041123 | 0.0046398 | 0.055241 | -0.0077588 | 0.069252 | -61.322 | 60.0357 | -61.3403 | -61.3403 | 60.0998 | 0.11444 | -0.31128 | 0 | 60.1639 | -61.3678 | -0.1236 | -0.27923 | -0.10529 | -0.1236 | -0.21515 | -0.15106 | -0.15106 | 0.018311 | 60.9055 | 61.2167 | 121.3165 | 121.2524 | -0.10529 | 121.3806 | 61.3312 | -0.15106 | 121.2524 | -0.10529 | 61.3312 | 121.3165 | 121.3806 | -121.6553 | -121.6827
9.3906 | 121.9299 | -61.1526 | 60.3745 | 0.01564 | 0.014755 | 0.0028305 | 0.0016492 | 0.051396 | -0.008186 | 0.067757 | -61.2991 | 60.1685 | -61.2488 | -61.3358 | 60.0952 | 0.17395 | -0.004578 | 0.10986 | 60.2188 | -61.3632 | -0.09613 | -0.20599 | -0.14648 | -0.18311 | -0.27924 | -0.21057 | -0.15564 | -0.050354 | 61.1481 | 61.2625 | 121.2479 | 121.3211 | -0.14648 | 121.3715 | 61.3266 | -0.21057 | 121.3211 | -0.14648 | 61.3266 | 121.2479 | 121.3715 | -121.6232 | -121.7377
11.1406 | 121.8979 | -61.2808 | 60.2463 | 0.10719 | 0.016464 | 0.0051803 | 0.010194 | 0.0546 | -0.011604 | 0.066902 | -61.4502 | 60.1044 | -61.3632 | -61.4594 | 59.9487 | 0.004578 | -0.1236 | -0.17395 | 60.2234 | -61.4136 | -0.082397 | -0.14191 | -0.16937 | -0.17853 | -0.29755 | -0.13275 | -0.022888 | -0.086975 | 61.1572 | 61.1069 | 121.2296 | 121.3852 | -0.16937 | 121.5042 | 61.2854 | -0.13275 | 121.3852 | -0.16937 | 61.2854 | 121.2296 | 121.5042 | -121.6095 | -121.6599
12.8281 | 121.8842 | -61.235 | 60.3378 | 0.16823 | 0.015823 | 0.0058211 | 0.0072034 | 0.054173 | -0.0077588 | 0.068611 | -61.3495 | 60.0815 | -61.322 | -61.3541 | 60.0723 | 0.091553 | -0.26093 | -0.032043 | 60.1868 | -61.377 | -0.086975 | -0.25635 | -0.11444 | -0.11902 | -0.2655 | -0.14191 | -0.15106 | -0.027466 | 60.9741 | 61.203 | 121.3074 | 121.3165 | -0.11444 | 121.4218 | 61.3266 | -0.14191 | 121.3165 | -0.11444 | 61.3266 | 121.3074 | 121.4218 | -121.6599 | -121.7148
14.5625 | 121.8658 | -61.2076 | 60.347 | 0.18349 | 0.015182 | 0.0034713 | 0.0063488 | 0.055668 | -0.0083996 | 0.066689 | -61.3174 | 60.0632 | -61.3174 | -61.3358 | 60.1089 | 0.10986 | -0.29297 | 0.009155 | 60.173 | -61.3815 | -0.10986 | -0.28381 | -0.10986 | -0.12817 | -0.23804 | -0.17395 | -0.17395 | 0 | 60.9146 | 61.2167 | 121.3165 | 121.2708 | -0.10986 | 121.3806 | 61.3174 | -0.17395 | 121.2708 | -0.10986 | 61.3174 | 121.3165 | 121.3806 | -121.6644 | -121.7285
16.2969 | 121.8246 | -61.29 | 60.3012 | -0.014877 | 0.015182 | 0.0085983 | 0.010408 | 0.055882 | -0.010322 | 0.066475 | -61.3632 | 60.0861 | -61.3358 | -61.4044 | 60.0128 | 0.07782 | -0.059509 | -0.091553 | 60.2554 | -61.3998 | -0.045776 | -0.21515 | -0.073242 | -0.11444 | -0.28839 | -0.10986 | -0.045776 | -0.027466 | 61.2305 | 61.1984 | 121.3028 | 121.376 | -0.073242 | 121.5454 | 61.3678 | -0.10986 | 121.376 | -0.073242 | 61.3678 | 121.3028 | 121.5454 | -121.637 | -121.701
18.0625 | 121.8979 | -61.2167 | 60.3424 | 0.099564 | 0.013687 | 0.00048074 | 0.003999 | 0.055882 | -0.0073316 | 0.069252 | -61.29 | 60.0861 | -61.2946 | -61.322 | 60.1135 | 0.11902 | -0.2243 | 0.027466 | 60.2142 | -61.3678 | -0.07782 | -0.25635 | -0.073242 | -0.10529 | -0.22888 | -0.15106 | -0.12817 | 0.004578 | 60.9924 | 61.2442 | 121.3303 | 121.3028 | -0.073242 | 121.431 | 61.3358 | -0.15106 | 121.3028 | -0.073242 | 61.3358 | 121.3303 | 121.431 | -121.637 | -121.7102
19.7344 | 121.8384 | -61.2717 | 60.3058 | -0.2285 | 0.015823 | 0.0049667 | 0.0052808 | 0.052891 | -0.0077588 | 0.067543 | -61.322 | 60.2188 | -61.2717 | -61.3449 | 60.0677 | 0.24261 | 0.25177 | 0.15106 | 60.3104 | -61.3495 | 0 | -0.086975 | -0.050354 | -0.073243 | -0.23804 | -0.07782 | 0.004578 | -0.050354 | 61.5234 | 61.4227 | 121.3394 | 121.4905 | -0.050354 | 121.582 | 61.5143 | -0.07782 | 121.4905 | -0.050354 | 61.5143 | 121.3394 | 121.582 | -121.5775 | -121.6553
21.4688 | 121.8842 | -61.203 | 60.3699 | 0.10719 | 0.017532 | 0.0053939 | 0.00229 | 0.054814 | -0.0073316 | 0.068184 | -61.2991 | 60.1181 | -61.2762 | -61.3312 | 60.1044 | 0.12817 | -0.21973 | 0.036621 | 60.1868 | -61.3907 | -0.073242 | -0.25177 | -0.09613 | -0.12817 | -0.2655 | -0.18768 | -0.1831 | -0.022888 | 60.9833 | 61.2396 | 121.3074 | 121.3211 | -0.09613 | 121.3898 | 61.3312 | -0.18768 | 121.3211 | -0.09613 | 61.3312 | 121.3074 | 121.3898 | -121.6461 | -121.7606
23.2344 | 121.7926 | -61.3266 | 60.3195 | -0.083542 | 0.018387 | 0.0036849 | 0.010621 | 0.053532 | -0.010322 | 0.067757 | -61.3403 | 60.1044 | -61.3541 | -61.3449 | 60.0494 | 0.14648 | -0.036621 | 0.022888 | 60.2463 | -61.3678 | -0.027466 | -0.21515 | -0.013733 | -0.018311 | -0.27008 | -0.041199 | -0.073242 | 0.013733 | 61.29 | 61.3495 | 121.376 | 121.431 | -0.013733 | 121.5729 | 61.4731 | -0.041199 | 121.431 | -0.013733 | 61.4731 | 121.376 | 121.5729 | -121.6736 | -121.6873
24.9688 | 121.7926 | -61.3266 | 60.3012 | -0.068283 | 0.016464 | 0.0049667 | 0.0078442 | 0.056309 | -0.009895 | 0.068825 | -61.3174 | 60.1273 | -61.3358 | -61.3449 | 60.0677 | 0.15564 | -0.032043 | 0.009155 | 60.2692 | -61.3678 | -0.009155 | -0.17395 | 0.009155 | -0.018311 | -0.23346 | -0.041199 | -0.032043 | 0.01831 | 61.2946 | 61.3358 | 121.3943 | 121.4539 | 0.009155 | 121.5958 | 61.4822 | -0.041199 | 121.4539 | 0.009155 | 61.4822 | 121.3943 | 121.5958 | -121.637 | -121.669
26.7031 | 121.7834 | -61.3129 | 60.3149 | -0.17509 | 0.018387 | 0.0043259 | 0.0067762 | 0.055668 | -0.010109 | 0.066262 | -61.3358 | 60.1959 | -61.2854 | -61.3495 | 60.0723 | 0.21515 | 0.11444 | 0.10986 | 60.2737 | -61.3724 | 0.027466 | -0.11902 | -0.022888 | -0.036621 | -0.24261 | -0.059509 | -0.041198 | -0.050354 | 61.4273 | 61.4227 | 121.3852 | 121.5088 | -0.022888 | 121.5866 | 61.528 | -0.059509 | 121.5088 | -0.022888 | 61.528 | 121.3852 | 121.5866 | -121.6003 | -121.6873
28.4531 | 121.907 | -61.2717 | 60.2829 | 0.11482 | 0.014969 | 0.0053939 | 0.0067762 | 0.055668 | -0.0077588 | 0.06797 | -61.4182 | 60.1273 | -61.3495 | -61.4777 | 59.9762 | -0.004578 | -0.13275 | -0.17853 | 60.2142 | -61.4502 | -0.07782 | -0.15564 | -0.14648 | -0.20599 | -0.3067 | -0.17853 | -0.068665 | -0.068665 | 61.1389 | 61.0931 | 121.2479 | 121.3989 | -0.14648 | 121.4859 | 61.2671 | -0.17853 | 121.3989 | -0.14648 | 61.2671 | 121.2479 | 121.4859 | -121.6324 | -121.7331
30.2031 | 121.8887 | -61.2396 | 60.347 | 0.099564 | 0.015823 | 0.0045395 | 0.0059216 | 0.056309 | -0.0079724 | 0.065834 | -61.29 | 60.1181 | -61.2762 | -61.3403 | 60.1181 | 0.13275 | -0.23804 | 0.027466 | 60.1822 | -61.3724 | -0.036621 | -0.22888 | -0.050354 | -0.10071 | -0.22888 | -0.13275 | -0.16479 | -0.013733 | 61.0016 | 61.2671 | 121.3577 | 121.3577 | -0.050354 | 121.4218 | 61.3724 | -0.13275 | 121.3577 | -0.050354 | 61.3724 | 121.3577 | 121.4218 | -121.6232 | -121.7194
31.8906 | 121.8521 | -61.2579 | 60.3378 | -0.24376 | 0.017318 | 0.0062485 | 0.0052808 | 0.053318 | -0.0096814 | 0.066475 | -61.3312 | 60.2325 | -61.2625 | -61.3403 | 60.0861 | 0.23804 | 0.23804 | 0.14191 | 60.3378 | -61.3586 | -0.004577 | -0.10529 | -0.073242 | -0.082397 | -0.25177 | -0.10071 | 0 | -0.068665 | 61.496 | 61.3998 | 121.344 | 121.4905 | -0.073242 | 121.5958 | 61.496 | -0.10071 | 121.4905 | -0.073242 | 61.496 | 121.344 | 121.5958 | -121.6003 | -121.6965
33.6406 | 121.8979 | -61.2625 | 60.2921 | 0.099564 | 0.016037 | 0.0053939 | 0.0078442 | 0.055027 | -0.0069042 | 0.068398 | -61.3907 | 60.1044 | -61.3449 | -61.4456 | 59.9991 | 0.004578 | -0.20599 | -0.15564 | 60.2051 | -61.409 | -0.082398 | -0.18768 | -0.12817 | -0.18311 | -0.29297 | -0.14648 | -0.086975 | -0.045776 | 61.0565 | 61.1069 | 121.2616 | 121.3669 | -0.12817 | 121.4676 | 61.2671 | -0.14648 | 121.3669 | -0.12817 | 61.2671 | 121.2616 | 121.4676 | -121.637 | -121.7011
35.3281 | 121.907 | -61.1984 | 60.3607 | 0.099564 | 0.014114 | 0.0056075 | 0.0035718 | 0.052677 | -0.0069042 | 0.067116 | -61.3083 | 60.1318 | -61.29 | -61.3586 | 60.1089 | 0.13733 | -0.17853 | 0.050354 | 60.1913 | -61.3861 | -0.091553 | -0.22888 | -0.10986 | -0.16022 | -0.25177 | -0.18768 | -0.16937 | -0.018311 | 61.0199 | 61.2488 | 121.3074 | 121.3303 | -0.10986 | 121.3898 | 61.3358 | -0.18768 | 121.3303 | -0.10986 | 61.3358 | 121.3074 | 121.3898 | -121.6507 | -121.7468
37.0625 | 121.8887 | -61.203 | 60.3516 | 0.091934 | 0.015609 | 0.0034713 | 0.0037854 | 0.053105 | -0.007118 | 0.06733 | -61.3083 | 60.0906 | -61.2946 | -61.3449 | 60.0998 | 0.1236 | -0.19226 | 0.032043 | 60.1776 | -61.3953 | -0.091553 | -0.26093 | -0.10529 | -0.14191 | -0.25177 | -0.19226 | -0.17395 | -0.013733 | 61.0107 | 61.235 | 121.3028 | 121.2936 | -0.10529 | 121.3806 | 61.3266 | -0.19226 | 121.2936 | -0.10529 | 61.3266 | 121.3028 | 121.3806 | -121.6461 | -121.7468
38.8125 | 121.8475 | -61.2579 | 60.347 | -0.2285 | 0.016678 | 0.0032577 | 0.0052808 | 0.053105 | -0.0075452 | 0.065407 | -61.2946 | 60.1959 | -61.2396 | -61.3129 | 60.1089 | 0.2655 | 0.24261 | 0.21057 | 60.3241 | -61.3541 | 0.018311 | -0.15106 | -0.036621 | -0.054931 | -0.23804 | -0.09613 | -0.022888 | -0.054932 | 61.5006 | 61.4685 | 121.3669 | 121.4539 | -0.036621 | 121.582 | 61.5234 | -0.09613 | 121.4539 | -0.036621 | 61.5234 | 121.3669 | 121.582 | -121.5866 | -121.701
40.5625 | 121.7834 | -61.2442 | 60.4019 | -0.20561 | 0.014114 | 0.0051803 | 0.0050672 | 0.053532 | -0.008827 | 0.06797 | -61.2122 | 60.1593 | -61.2122 | -61.2076 | 60.2234 | 0.37079 | 0.10986 | 0.32044 | 60.2921 | -61.2808 | 0.032044 | -0.24262 | 0.032044 | 0.036621 | -0.17853 | -0.036621 | -0.10986 | 0 | 61.3541 | 61.5646 | 121.4676 | 121.4035 | 0.032044 | 121.5363 | 61.615 | -0.036621 | 121.4035 | 0.032044 | 61.615 | 121.4676 | 121.5363 | -121.6141 | -121.6827
42.25 | 121.788 | -61.2991 | 60.2783 | -0.091171 | 0.016037 | 0.0051803 | 0.01233 | 0.056523 | -0.0094678 | 0.068398 | -61.3312 | 60.1318 | -61.3312 | -61.3403 | 60.0632 | 0.16479 | 0.009155 | 0.054932 | 60.2692 | -61.3724 | -0.032044 | -0.14648 | -0.032044 | -0.041199 | -0.21515 | -0.073242 | -0.009155 | 0 | 61.3083 | 61.3541 | 121.3623 | 121.431 | -0.032044 | 121.5683 | 61.4639 | -0.073242 | 121.431 | -0.032044 | 61.4639 | 121.3623 | 121.5683 | -121.6095 | -121.6507
44 | 121.907 | -61.1938 | 60.3836 | 0.12245 | 0.016464 | 0.0034713 | 0.0050672 | 0.0546 | -0.01075 | 0.067116 | -61.3083 | 60.1044 | -61.2808 | -61.3495 | 60.1089 | 0.12817 | -0.13733 | 0.064087 | 60.2554 | -61.3541 | -0.086975 | -0.27924 | -0.11444 | -0.15564 | -0.27466 | -0.16022 | -0.12817 | -0.027466 | 61.0565 | 61.2579 | 121.3028 | 121.2982 | -0.11444 | 121.4493 | 61.322 | -0.16022 | 121.2982 | -0.11444 | 61.322 | 121.3028 | 121.4493 | -121.6644 | -121.7377
45.7344 | 121.9116 | -61.1755 | 60.3516 | 0.084305 | 0.016678 | -0.00016026 | 0.005708 | 0.054173 | -0.0086132 | 0.06733 | -61.3037 | 60.1181 | -61.2396 | -61.3358 | 60.1044 | 0.13275 | -0.10986 | 0.068665 | 60.26 | -61.377 | -0.064087 | -0.23346 | -0.12817 | -0.16022 | -0.24719 | -0.20142 | -0.091552 | -0.064087 | 61.0657 | 61.2442 | 121.2799 | 121.2936 | -0.12817 | 121.4355 | 61.3083 | -0.20142 | 121.2936 | -0.12817 | 61.3083 | 121.2799 | 121.4355 | -121.5912 | -121.7285
47.4062 | 121.9162 | -61.1847 | 60.347 | 0.00038159 | 0.014114 | 0.0021895 | 0.0052808 | 0.05225 | -0.0060498 | 0.06733 | -61.3083 | 60.1593 | -61.2579 | -61.2991 | 60.1364 | 0.21515 | -0.009155 | 0.17395 | 60.2554 | -61.3312 | -0.073243 | -0.18768 | -0.1236 | -0.11444 | -0.21057 | -0.14648 | -0.091553 | -0.050354 | 61.1755 | 61.3586 | 121.3211 | 121.344 | -0.1236 | 121.4401 | 61.3998 | -0.14648 | 121.344 | -0.1236 | 61.3998 | 121.3211 | 121.4401 | -121.6049 | -121.6782
49.1406 | 121.8338 | -61.2625 | 60.3195 | -0.2285 | 0.015609 | 0.0026169 | 0.010621 | 0.052891 | -0.007118 | 0.065621 | -61.3174 | 60.2325 | -61.2717 | -61.3586 | 60.0632 | 0.2243 | 0.22888 | 0.1236 | 60.3104 | -61.3495 | -0.009155 | -0.086975 | -0.054932 | -0.096131 | -0.25635 | -0.086975 | -0.009155 | -0.045777 | 61.4914 | 61.3861 | 121.3257 | 121.4951 | -0.054932 | 121.5729 | 61.4868 | -0.086975 | 121.4951 | -0.054932 | 61.4868 | 121.3257 | 121.5729 | -121.5912 | -121.669
50.8281 | 121.9162 | -61.1801 | 60.379 | -0.0072479 | 0.016678 | 0.0041123 | 0.0037854 | 0.052037 | -0.007118 | 0.065407 | -61.2946 | 60.1776 | -61.2579 | -61.2991 | 60.1364 | 0.20142 | 0 | 0.16937 | 60.2783 | -61.3403 | -0.07782 | -0.20142 | -0.11444 | -0.11902 | -0.24261 | -0.16022 | -0.10071 | -0.036621 | 61.1801 | 61.3495 | 121.3165 | 121.3577 | -0.11444 | 121.4584 | 61.3815 | -0.16022 | 121.3577 | -0.11444 | 61.3815 | 121.3165 | 121.4584 | -121.637 | -121.7194
52.5781 | 121.9345 | -61.1618 | 60.379 | 0.0080111 | 0.013473 | 0.00069434 | 0.0063488 | 0.052677 | -0.010109 | 0.066902 | -61.322 | 60.1181 | -61.2762 | -61.3312 | 60.1044 | 0.1831 | -0.004578 | 0.13733 | 60.2554 | -61.3449 | -0.11444 | -0.26093 | -0.16022 | -0.16937 | -0.27466 | -0.18311 | -0.1236 | -0.045776 | 61.1572 | 61.2991 | 121.2662 | 121.2799 | -0.16022 | 121.4172 | 61.3449 | -0.18311 | 121.2799 | -0.16022 | 61.3449 | 121.2662 | 121.4172 | -121.6553 | -121.7239
54.3281 | 121.843 | -61.2579 | 60.3378 | -0.25902 | 0.015823 | 0.0028305 | 0.0076306 | 0.051823 | -0.0079724 | 0.067116 | -61.3174 | 60.228 | -61.2717 | -61.322 | 60.0861 | 0.24261 | 0.26093 | 0.16022 | 60.3104 | -61.3495 | -0.013732 | -0.10986 | -0.059509 | -0.064086 | -0.25177 | -0.091552 | -0.027466 | -0.045777 | 61.5189 | 61.4182 | 121.344 | 121.4859 | -0.059509 | 121.5683 | 61.5006 | -0.091552 | 121.4859 | -0.059509 | 61.5006 | 121.344 | 121.5683 | -121.6095 | -121.6873
56.0625 | 121.9254 | -61.2488 | 60.2554 | 0.076676 | 0.015823 | 0.0088119 | 0.012117 | 0.055241 | -0.0094678 | 0.066689 | -61.4456 | 60.0998 | -61.3907 | -61.4548 | 59.9487 | -0.004578 | -0.12817 | -0.16479 | 60.2051 | -61.4456 | -0.14191 | -0.15564 | -0.19684 | -0.20599 | -0.3067 | -0.19684 | -0.050354 | -0.054932 | 61.1206 | 61.084 | 121.1975 | 121.3486 | -0.19684 | 121.4539 | 61.2442 | -0.19684 | 121.3486 | -0.19684 | 61.2442 | 121.1975 | 121.4539 | -121.6461 | -121.7011
57.8125 | 121.9162 | -61.171 | 60.3561 | 0.10719 | 0.014969 | 0.0056075 | 0.0042126 | 0.054173 | -0.007118 | 0.068184 | -61.2991 | 60.1318 | -61.2717 | -61.3358 | 60.1135 | 0.12817 | -0.17395 | 0.059509 | 60.2234 | -61.3861 | -0.10071 | -0.2243 | -0.12817 | -0.16479 | -0.24262 | -0.21515 | -0.13275 | -0.027466 | 60.997 | 61.2305 | 121.2845 | 121.3028 | -0.12817 | 121.3943 | 61.2991 | -0.21515 | 121.3028 | -0.12817 | 61.2991 | 121.2845 | 121.3943 | -121.6278 | -121.7422
59.5625 | 121.8063 | -61.2762 | 60.3195 | -0.17509 | 0.016464 | 0.0034713 | 0.0086988 | 0.053959 | -0.01075 | 0.065407 | -61.3266 | 60.1959 | -61.2946 | -61.3358 | 60.0815 | 0.21515 | 0.16479 | 0.12817 | 60.3149 | -61.3495 | -0.018311 | -0.1236 | -0.050354 | -0.059509 | -0.23804 | -0.073242 | -0.004578 | -0.032043 | 61.441 | 61.4044 | 121.3577 | 121.4722 | -0.050354 | 121.5912 | 61.4914 | -0.073242 | 121.4722 | -0.050354 | 61.4914 | 121.3577 | 121.5912 | -121.6141 | -121.669
61.2344 | 121.8979 | -61.2122 | 60.3561 | 0.13008 | 0.015182 | 0.0064621 | 0.0042126 | 0.055668 | -0.0083996 | 0.06797 | -61.2991 | 60.0677 | -61.3129 | -61.322 | 60.1044 | 0.11902 | -0.24719 | 0.041199 | 60.1959 | -61.3907 | -0.10071 | -0.28839 | -0.086975 | -0.10986 | -0.25177 | -0.17853 | -0.16022 | 0.013733 | 60.965 | 61.2534 | 121.3165 | 121.2799 | -0.086975 | 121.4081 | 61.3312 | -0.17853 | 121.2799 | -0.086975 | 61.3312 | 121.3165 | 121.4081 | -121.669 | -121.7468
62.9844 | 121.9208 | -61.1435 | 60.3699 | 0.00038159 | 0.014114 | 0.010094 | 0.0042126 | 0.053959 | -0.0073316 | 0.066475 | -61.2946 | 60.1639 | -61.2396 | -61.3449 | 60.1089 | 0.17395 | 0.013733 | 0.10986 | 60.228 | -61.3861 | -0.09613 | -0.20599 | -0.15106 | -0.20142 | -0.26093 | -0.24261 | -0.14191 | -0.054932 | 61.1572 | 61.2534 | 121.2524 | 121.3074 | -0.15106 | 121.3715 | 61.3174 | -0.24261 | 121.3074 | -0.15106 | 61.3174 | 121.2524 | 121.3715 | -121.6095 | -121.756
64.7344 | 121.7972 | -61.2213 | 60.4202 | -0.15221 | 0.014969 | 0.0068893 | 0.003999 | 0.050541 | -0.008186 | 0.067757 | -61.2076 | 60.1822 | -61.2213 | -61.2167 | 60.2142 | 0.3479 | 0.064087 | 0.33875 | 60.2875 | -61.3037 | 0 | -0.23804 | 0.013732 | 0.004577 | -0.20599 | -0.082398 | -0.13275 | 0.013732 | 61.2854 | 61.5601 | 121.4355 | 121.4035 | 0.013732 | 121.5088 | 61.5692 | -0.082398 | 121.4035 | 0.013732 | 61.5692 | 121.4355 | 121.5088 | -121.6415 | -121.7239
66.4219 | 121.7834 | -61.322 | 60.3104 | -0.12932 | 0.014328 | 0.0021895 | 0.012117 | 0.0546 | -0.012031 | 0.06498 | -61.3174 | 60.173 | -61.3312 | -61.3266 | 60.0815 | 0.19684 | 0.064087 | 0.091553 | 60.2737 | -61.3449 | -0.009156 | -0.13733 | 0.004577 | -0.004578 | -0.22888 | -0.022889 | -0.036621 | 0.013733 | 61.3861 | 61.4136 | 121.4035 | 121.4951 | 0.004577 | 121.5958 | 61.5189 | -0.022889 | 121.4951 | 0.004577 | 61.5189 | 121.4035 | 121.5958 | -121.6415 | -121.6553
68.1719 | 121.8201 | -61.2808 | 60.3241 | -0.16747 | 0.013046 | 0.0015487 | 0.0076306 | 0.053318 | -0.0092542 | 0.067757 | -61.3358 | 60.173 | -61.29 | -61.3358 | 60.0815 | 0.21057 | 0.17395 | 0.10529 | 60.2875 | -61.3678 | -0.009155 | -0.15106 | -0.054931 | -0.054931 | -0.24262 | -0.086975 | -0.036621 | -0.045776 | 61.4548 | 61.3861 | 121.3623 | 121.4539 | -0.054931 | 121.5683 | 61.4914 | -0.086975 | 121.4539 | -0.054931 | 61.4914 | 121.3623 | 121.5683 | -121.6141 | -121.6919
69.9219 | 121.9162 | -61.1755 | 60.3378 | 0.061417 | 0.015182 | 0.0053939 | 0.0029308 | 0.052891 | -0.0086132 | 0.06797 | -61.3174 | 60.1593 | -61.2488 | -61.3403 | 60.1135 | 0.15106 | -0.10986 | 0.073242 | 60.2325 | -61.3815 | -0.073242 | -0.17853 | -0.14191 | -0.16479 | -0.2243 | -0.20599 | -0.10529 | -0.068665 | 61.0657 | 61.2488 | 121.2891 | 121.3348 | -0.14191 | 121.4081 | 61.3266 | -0.20599 | 121.3348 | -0.14191 | 61.3266 | 121.2891 | 121.4081 | -121.5866 | -121.7194
71.5938 | 121.875 | -61.2122 | 60.3287 | 0.15297 | 0.016037 | 0.0060349 | 0.0080578 | 0.053105 | -0.0083996 | 0.06797 | -61.3037 | 60.0815 | -61.3083 | -61.3449 | 60.0906 | 0.10529 | -0.3067 | -0.032043 | 60.1776 | -61.4227 | -0.096131 | -0.24719 | -0.091553 | -0.13275 | -0.23804 | -0.21057 | -0.15106 | 0.004578 | 60.9055 | 61.1801 | 121.3028 | 121.2936 | -0.091553 | 121.3898 | 61.3174 | -0.21057 | 121.2936 | -0.091553 | 61.3174 | 121.3028 | 121.3898 | -121.637 | -121.7514
73.3438 | 121.9299 | -61.2808 | 60.2783 | 0.099564 | 0.017105 | 0.0071029 | 0.010835 | 0.054386 | -0.0094678 | 0.066902 | -61.4273 | 60.1227 | -61.377 | -61.4685 | 59.9487 | -0.018311 | -0.14648 | -0.1831 | 60.2417 | -61.4548 | -0.09613 | -0.15564 | -0.14648 | -0.18768 | -0.32959 | -0.17395 | -0.036621 | -0.050354 | 61.1343 | 61.0977 | 121.2296 | 121.4035 | -0.14648 | 121.5225 | 61.2625 | -0.17395 | 121.4035 | -0.14648 | 61.2625 | 121.2296 | 121.5225 | -121.6553 | -121.7331
75.0938 | 121.8292 | -61.2762 | 60.3333 | -0.14458 | 0.014755 | 0.0038985 | 0.0076306 | 0.055455 | -0.011604 | 0.066902 | -61.322 | 60.2005 | -61.2762 | -61.3495 | 60.0815 | 0.23346 | 0.19226 | 0.11902 | 60.3241 | -61.3586 | 0 | -0.13275 | -0.045776 | -0.073242 | -0.25177 | -0.082398 | -0.009155 | -0.045776 | 61.4685 | 61.3953 | 121.3577 | 121.4767 | -0.045776 | 121.6003 | 61.5097 | -0.082398 | 121.4767 | -0.045776 | 61.5097 | 121.3577 | 121.6003 | -121.6095 | -121.6919
76.7812 | 121.9025 | -61.2213 | 60.3012 | 0.1606 | 0.016464 | 0.0077437 | 0.0065624 | 0.056736 | -0.0077588 | 0.066048 | -61.3632 | 60.1181 | -61.3266 | -61.3724 | 60.0632 | 0.068665 | -0.24261 | -0.068665 | 60.1959 | -61.4273 | -0.10529 | -0.18311 | -0.14191 | -0.15106 | -0.23804 | -0.20599 | -0.10529 | -0.036621 | 60.9787 | 61.1526 | 121.2845 | 121.3394 | -0.14191 | 121.4172 | 61.29 | -0.20599 | 121.3394 | -0.14191 | 61.29 | 121.2845 | 121.4172 | -121.6278 | -121.7285
78.5312 | 121.9574 | -61.1572 | 60.3561 | 0.01564 | 0.01625 | 0.00069434 | 0.0035718 | 0.053959 | -0.0073316 | 0.066475 | -61.3083 | 60.1593 | -61.2488 | -61.3312 | 60.1181 | 0.16479 | -0.041199 | 0.09613 | 60.2692 | -61.3632 | -0.091552 | -0.19684 | -0.15106 | -0.17395 | -0.23804 | -0.20599 | -0.086975 | -0.05951 | 61.116 | 61.2534 | 121.2753 | 121.3165 | -0.15106 | 121.4264 | 61.322 | -0.20599 | 121.3165 | -0.15106 | 61.322 | 121.2753 | 121.4264 | -121.6049 | -121.7194
80.2656 | 121.8979 | -61.2579 | 60.26 | 0.061417 | 0.018387 | 0.0094527 | 0.0097668 | 0.055241 | -0.01139 | 0.069039 | -61.4182 | 60.1318 | -61.377 | -61.4456 | 59.9442 | -0.013733 | -0.07782 | -0.16937 | 60.2554 | -61.4227 | -0.11902 | -0.12817 | -0.16022 | -0.18768 | -0.31586 | -0.16479 | -0.004578 | -0.041199 | 61.1801 | 61.0886 | 121.2021 | 121.3898 | -0.16022 | 121.5134 | 61.2442 | -0.16479 | 121.3898 | -0.16022 | 61.2442 | 121.2021 | 121.5134 | -121.637 | -121.6827
81.9531 | 121.9528 | -61.1893 | 60.3653 | 0.00038159 | 0.01625 | 0.0038985 | 0.0033582 | 0.054386 | -0.008827 | 0.066475 | -61.2946 | 60.173 | -61.2488 | -61.3358 | 60.1135 | 0.16937 | -0.009155 | 0.10071 | 60.2783 | -61.3678 | -0.059509 | -0.19226 | -0.10529 | -0.14648 | -0.25177 | -0.17853 | -0.086975 | -0.045777 | 61.1801 | 61.29 | 121.3028 | 121.3623 | -0.10529 | 121.4676 | 61.3586 | -0.17853 | 121.3623 | -0.10529 | 61.3586 | 121.3028 | 121.4676 | -121.6141 | -121.7331
83.7031 | 121.7789 | -61.3083 | 60.3012 | -0.091171 | 0.017318 | 0.0077437 | 0.010408 | 0.055027 | -0.008186 | 0.068825 | -61.2991 | 60.2005 | -61.3129 | -61.3358 | 60.0861 | 0.1831 | 0 | 0.068665 | 60.2646 | -61.4227 | -0.004577 | -0.10071 | 0.009156 | -0.027465 | -0.21515 | -0.11444 | -0.036621 | 0.013733 | 61.3083 | 61.377 | 121.3943 | 121.5088 | 0.009156 | 121.5729 | 61.4914 | -0.11444 | 121.5088 | 0.009156 | 61.4914 | 121.3943 | 121.5729 | -121.6141 | -121.7239
85.4375 | 121.8384 | -61.2488 | 60.3699 | -0.25902 | 0.01625 | 0.00090794 | 0.003999 | 0.053959 | -0.0086132 | 0.067757 | -61.2625 | 60.1959 | -61.2488 | -61.3083 | 60.1227 | 0.28381 | 0.21515 | 0.21515 | 60.3058 | -61.3312 | 0 | -0.17395 | -0.013733 | -0.05951 | -0.24719 | -0.082398 | -0.064087 | -0.013733 | 61.4639 | 61.4639 | 121.3715 | 121.4447 | -0.013733 | 121.5546 | 61.5326 | -0.082398 | 121.4447 | -0.013733 | 61.5326 | 121.3715 | 121.5546 | -121.6187 | -121.701
87.125 | 121.8109 | -61.3083 | 60.3058 | -0.083542 | 0.014969 | 0.0047531 | 0.010621 | 0.05695 | -0.012031 | 0.068184 | -61.3174 | 60.1135 | -61.3358 | -61.3403 | 60.0723 | 0.16479 | -0.032043 | 0.032043 | 60.2692 | -61.3724 | -0.027465 | -0.19226 | -0.009155 | -0.032043 | -0.23346 | -0.064086 | -0.036621 | 0.01831 | 61.2762 | 61.3403 | 121.3806 | 121.4218 | -0.009155 | 121.5775 | 61.4731 | -0.064086 | 121.4218 | -0.009155 | 61.4731 | 121.3806 | 121.5775 | -121.6415 | -121.6782
88.875 | 121.8887 | -61.2762 | 60.2692 | 0.061417 | 0.015823 | 0.0060349 | 0.0095532 | 0.057377 | -0.010322 | 0.067757 | -61.409 | 60.1181 | -61.3678 | -61.4548 | 59.9854 | 0.032043 | -0.068665 | -0.12817 | 60.2417 | -61.4044 | -0.091553 | -0.15106 | -0.13275 | -0.17853 | -0.28381 | -0.12817 | -0.027466 | -0.041199 | 61.2076 | 61.1481 | 121.2616 | 121.3943 | -0.13275 | 121.5179 | 61.3083 | -0.12817 | 121.3943 | -0.13275 | 61.3083 | 121.2616 | 121.5179 | -121.637 | -121.6736
90.625 | 121.8475 | -61.1847 | 60.4019 | -0.13695 | 0.014328 | 0.0066757 | 0.0016492 | 0.05225 | -0.005409 | 0.069039 | -61.2167 | 60.2142 | -61.1755 | -61.2442 | 60.1959 | 0.32959 | 0.027466 | 0.28381 | 60.2509 | -61.3358 | 0.009155 | -0.18768 | -0.032044 | -0.05951 | -0.20599 | -0.15106 | -0.15106 | -0.041199 | 61.2122 | 61.4685 | 121.3806 | 121.3989 | -0.032044 | 121.4355 | 61.5143 | -0.15106 | 121.3989 | -0.032044 | 61.5143 | 121.3806 | 121.4355 | -121.5775 | -121.7377
92.2969 | 121.9208 | -61.1984 | 60.3653 | -0.0072479 | 0.014328 | 0.0036849 | 0.0035718 | 0.054173 | -0.0079724 | 0.067757 | -61.3083 | 60.173 | -61.2579 | -61.3358 | 60.1273 | 0.20142 | 0 | 0.15106 | 60.2417 | -61.3266 | -0.05951 | -0.19226 | -0.10986 | -0.13733 | -0.23804 | -0.12817 | -0.1236 | -0.050354 | 61.1984 | 61.3495 | 121.3257 | 121.3715 | -0.10986 | 121.4401 | 61.3998 | -0.12817 | 121.3715 | -0.10986 | 61.3998 | 121.3257 | 121.4401 | -121.6232 | -121.6919
94.0312 | 121.8155 | -61.2854 | 60.3195 | -0.17509 | 0.016037 | 0.0083847 | 0.0097668 | 0.053318 | -0.0083996 | 0.066048 | -61.3312 | 60.2097 | -61.2991 | -61.3541 | 60.0677 | 0.21515 | 0.13733 | 0.10529 | 60.2692 | -61.3907 | -0.013733 | -0.10986 | -0.045777 | -0.068665 | -0.25177 | -0.10529 | -0.050354 | -0.032044 | 61.4227 | 61.3907 | 121.3531 | 121.4951 | -0.045777 | 121.5546 | 61.5005 | -0.10529 | 121.4951 | -0.045777 | 61.5005 | 121.3531 | 121.5546 | -121.6187 | -121.7102
95.7188 | 121.9116 | -61.1801 | 60.3653 | -0.0072479 | 0.015182 | 0.0036849 | 0.0033582 | 0.0546 | -0.008186 | 0.069039 | -61.3129 | 60.1593 | -61.2579 | -61.3358 | 60.1044 | 0.1831 | -0.009155 | 0.14191 | 60.26 | -61.3495 | -0.07782 | -0.20599 | -0.13275 | -0.15564 | -0.26093 | -0.16937 | -0.10529 | -0.054931 | 61.171 | 61.322 | 121.2845 | 121.3394 | -0.13275 | 121.4401 | 61.3632 | -0.16937 | 121.3394 | -0.13275 | 61.3632 | 121.2845 | 121.4401 | -121.6232 | -121.7148
97.4531 | 121.9299 | -61.2534 | 60.2737 | 0.099564 | 0.016891 | 0.0043259 | 0.010194 | 0.057163 | -0.01139 | 0.067116 | -61.4227 | 60.1089 | -61.3861 | -61.4685 | 59.967 | -0.009155 | -0.13275 | -0.15564 | 60.2417 | -61.4182 | -0.13275 | -0.1648 | -0.16937 | -0.21515 | -0.3067 | -0.16479 | -0.032044 | -0.036621 | 61.1206 | 61.0977 | 121.2204 | 121.3623 | -0.16937 | 121.4951 | 61.2442 | -0.16479 | 121.3623 | -0.16937 | 61.2442 | 121.2204 | 121.4951 | -121.6599 | -121.6919
99.2031 | 121.7834 | -61.2305 | 60.4111 | -0.18272 | 0.012619 | 0.0049667 | 0.0031446 | 0.056736 | -0.0086132 | 0.067116 | -61.2305 | 60.173 | -61.2213 | -61.2396 | 60.2051 | 0.33875 | 0.10986 | 0.32959 | 60.2875 | -61.3358 | 0.009156 | -0.23804 | 0 | -0.009155 | -0.20599 | -0.10529 | -0.1236 | -0.009156 | 61.3403 | 61.5601 | 121.4355 | 121.4035 | 0 | 121.5179 | 61.5692 | -0.10529 | 121.4035 | 0 | 61.5692 | 121.4355 | 121.5179 | -121.6324 | -121.7468
100.8906 | 121.8567 | -61.2488 | 60.3653 | -0.24376 | 0.015396 | 0.0075301 | 0.0078442 | 0.053746 | -0.010109 | 0.066475 | -61.2808 | 60.173 | -61.2396 | -61.3129 | 60.1181 | 0.27008 | 0.21973 | 0.20599 | 60.3287 | -61.322 | 0.009155 | -0.19226 | -0.032044 | -0.064087 | -0.24719 | -0.073242 | -0.036621 | -0.041199 | 61.4685 | 61.4548 | 121.3669 | 121.4218 | -0.032044 | 121.5775 | 61.5189 | -0.073242 | 121.4218 | -0.032044 | 61.5189 | 121.3669 | 121.5775 | -121.6049 | -121.6873
102.6406 | 121.8063 | -61.2442 | 60.379 | -0.13695 | 0.014969 | 5.3338e-05 | 0.0050672 | 0.052677 | -0.0083996 | 0.065407 | -61.2076 | 60.1547 | -61.1938 | -61.2076 | 60.2188 | 0.3479 | 0.054932 | 0.31128 | 60.2783 | -61.322 | 0.050354 | -0.2243 | 0.036621 | 0.036621 | -0.16022 | -0.077819 | -0.10071 | -0.013733 | 61.2991 | 61.5555 | 121.463 | 121.3989 | 0.036621 | 121.5225 | 61.5921 | -0.077819 | 121.3989 | 0.036621 | 61.5921 | 121.463 | 121.5225 | -121.5729 | -121.701
104.3906 | 121.9254 | -61.2671 | 60.2509 | 0.13008 | 0.015609 | 0.0041123 | 0.013398 | 0.055027 | -0.010322 | 0.069252 | -61.4319 | 60.0906 | -61.3815 | -61.4502 | 59.9579 | -0.004578 | -0.13275 | -0.15564 | 60.2142 | -61.441 | -0.11444 | -0.16022 | -0.16479 | -0.1831 | -0.29297 | -0.17395 | -0.036621 | -0.050354 | 61.1343 | 61.1115 | 121.225 | 121.3577 | -0.16479 | 121.4813 | 61.2625 | -0.17395 | 121.3577 | -0.16479 | 61.2625 | 121.225 | 121.4813 | -121.6324 | -121.6919
106.0625 | 121.9391 | -61.1847 | 60.3653 | 0.01564 | 0.015823 | 0.0049667 | 0.003999 | 0.052677 | -0.0083996 | 0.066262 | -61.3266 | 60.1639 | -61.2259 | -61.3449 | 60.1135 | 0.15564 | -0.036621 | 0.10071 | 60.26 | -61.377 | -0.041199 | -0.20142 | -0.14191 | -0.16022 | -0.25177 | -0.19226 | -0.10529 | -0.10071 | 61.1481 | 61.2854 | 121.2982 | 121.3486 | -0.14191 | 121.4447 | 61.3403 | -0.19226 | 121.3486 | -0.14191 | 61.3403 | 121.2982 | 121.4447 | -121.5912 | -121.7422
107.7969 | 121.8338 | -61.2579 | 60.3836 | -0.37346 | 0.015396 | 0.0056075 | 0.0078442 | 0.054173 | -0.0079724 | 0.067116 | -61.3037 | 60.2463 | -61.2671 | -61.3312 | 60.0906 | 0.25177 | 0.26093 | 0.19226 | 60.3424 | -61.3358 | -0.009155 | -0.13733 | -0.045776 | -0.073242 | -0.29297 | -0.077819 | -0.041199 | -0.036621 | 61.5189 | 61.4502 | 121.3486 | 121.5042 | -0.045776 | 121.6003 | 61.5097 | -0.077819 | 121.5042 | -0.045776 | 61.5097 | 121.3486 | 121.6003 | -121.6507 | -121.7194
109.5625 | 121.8567 | -61.2579 | 60.3149 | -0.23613 | 0.015182 | 0.0030441 | 0.0093396 | 0.052891 | -0.0096814 | 0.064553 | -61.3449 | 60.2142 | -61.2808 | -61.3449 | 60.0906 | 0.23346 | 0.2655 | 0.16022 | 60.3104 | -61.3403 | -0.022888 | -0.10071 | -0.086975 | -0.086975 | -0.2243 | -0.082397 | -0.004577 | -0.064087 | 61.5234 | 61.4182 | 121.3486 | 121.4722 | -0.086975 | 121.5683 | 61.4914 | -0.082397 | 121.4722 | -0.086975 | 61.4914 | 121.3486 | 121.5683 | -121.5958 | -121.6553
111.2344 | 121.8384 | -61.3037 | 60.2829 | 0.00038159 | 0.017318 | 0.0049667 | 0.0089124 | 0.056095 | -0.012245 | 0.069252 | -61.377 | 60.1181 | -61.3541 | -61.409 | 59.9899 | 0.054932 | -0.07782 | -0.10529 | 60.2234 | -61.441 | -0.050354 | -0.1648 | -0.073242 | -0.10529 | -0.29297 | -0.13733 | -0.059509 | -0.022888 | 61.2259 | 61.1984 | 121.2936 | 121.4218 | -0.073242 | 121.5271 | 61.3586 | -0.13733 | 121.4218 | -0.073242 | 61.3586 | 121.2936 | 121.5271 | -121.637 | -121.7239
112.9844 | 121.8384 | -61.2305 | 60.3882 | -0.26665 | 0.015396 | 0.0047531 | 0.0042126 | 0.052464 | -0.0075452 | 0.068825 | -61.2396 | 60.2097 | -61.2122 | -61.2946 | 60.1501 | 0.31128 | 0.20142 | 0.26093 | 60.3333 | -61.322 | 0.018311 | -0.17853 | -0.009155 | -0.064087 | -0.23804 | -0.091552 | -0.054932 | -0.027466 | 61.4319 | 61.4914 | 121.3806 | 121.4401 | -0.009155 | 121.5637 | 61.5417 | -0.091552 | 121.4401 | -0.009155 | 61.5417 | 121.3806 | 121.5637 | -121.6003 | -121.7102
114.7188 | 121.843 | -61.2625 | 60.3836 | -0.25139 | 0.016464 | 0.0026169 | 0.0059216 | 0.052037 | -0.010536 | 0.066262 | -61.2625 | 60.1959 | -61.2442 | -61.2946 | 60.1318 | 0.27924 | 0.2243 | 0.21515 | 60.3104 | -61.3266 | 0.01831 | -0.18768 | 0 | -0.032044 | -0.25177 | -0.064087 | -0.073242 | -0.01831 | 61.4868 | 61.4777 | 121.3943 | 121.4584 | 0 | 121.5729 | 61.5417 | -0.064087 | 121.4584 | 0 | 61.5417 | 121.3943 | 121.5729 | -121.6278 | -121.7102
116.4531 | 121.8201 | -61.2671 | 60.3241 | -0.17509 | 0.01625 | 0.0071029 | 0.009126 | 0.053959 | -0.0094678 | 0.066262 | -61.3266 | 60.1959 | -61.2991 | -61.3541 | 60.0815 | 0.22888 | 0.19684 | 0.1236 | 60.3378 | -61.3586 | -0.032043 | -0.12817 | -0.059509 | -0.086975 | -0.24262 | -0.091553 | 0.013733 | -0.027466 | 61.4639 | 61.3907 | 121.3486 | 121.463 | -0.059509 | 121.6049 | 61.496 | -0.091553 | 121.463 | -0.059509 | 61.496 | 121.3486 | 121.6049 | -121.6232 | -121.6827
118.2031 | 121.9208 | -61.2579 | 60.2737 | 0.12245 | 0.018173 | 0.0064621 | 0.0086988 | 0.055882 | -0.0092542 | 0.066689 | -61.4227 | 60.1501 | -61.3632 | -61.4685 | 59.9533 | -0.018311 | -0.13275 | -0.18768 | 60.2417 | -61.4319 | -0.10528 | -0.1236 | -0.16479 | -0.21057 | -0.32044 | -0.17395 | -0.032044 | -0.059509 | 61.1252 | 61.0703 | 121.2112 | 121.4081 | -0.16479 | 121.4996 | 61.2396 | -0.17395 | 121.4081 | -0.16479 | 61.2396 | 121.2112 | 121.4996 | -121.637 | -121.7056
119.8906 | 121.7972 | -61.2122 | 60.4065 | -0.17509 | 0.01625 | -0.0012283 | 0.0018628 | 0.053746 | -0.007118 | 0.06498 | -61.1893 | 60.1822 | -61.1984 | -61.2167 | 60.2325 | 0.36163 | 0.091553 | 0.34332 | 60.2783 | -61.3174 | 0.013733 | -0.2243 | 0.022888 | -0.004578 | -0.17395 | -0.10529 | -0.12817 | 0.009155 | 61.3037 | 61.5555 | 121.4447 | 121.3943 | 0.022888 | 121.4905 | 61.5738 | -0.10529 | 121.3943 | 0.022888 | 61.5738 | 121.4447 | 121.4905 | -121.6049 | -121.7239
121.6406 | 121.8796 | -61.2167 | 60.3561 | 0.11482 | 0.01625 | 0.0026169 | 0.0044262 | 0.055241 | -0.0066906 | 0.067543 | -61.2946 | 60.1089 | -61.2946 | -61.3174 | 60.0998 | 0.12817 | -0.22888 | 0.036621 | 60.1959 | -61.3998 | -0.07782 | -0.24719 | -0.07782 | -0.10071 | -0.25635 | -0.18311 | -0.16022 | 0 | 60.9879 | 61.2534 | 121.3165 | 121.3257 | -0.07782 | 121.4127 | 61.3449 | -0.18311 | 121.3257 | -0.07782 | 61.3449 | 121.3165 | 121.4127 | -121.6507 | -121.756
123.3906 | 121.9025 | -61.203 | 60.3653 | 0.10719 | 0.014541 | 0.0024033 | 0.0052808 | 0.054173 | -0.0073316 | 0.067116 | -61.3129 | 60.141 | -61.2808 | -61.3266 | 60.1044 | 0.12817 | -0.18768 | 0.054932 | 60.2188 | -61.3632 | -0.07782 | -0.2243 | -0.10986 | -0.1236 | -0.26093 | -0.16022 | -0.14648 | -0.032043 | 61.0153 | 61.2579 | 121.3074 | 121.344 | -0.10986 | 121.4218 | 61.3312 | -0.16022 | 121.344 | -0.10986 | 61.3312 | 121.3074 | 121.4218 | -121.6461 | -121.7285
125.0781 | 121.8796 | -61.2167 | 60.3424 | 0.17586 | 0.017105 | 0.0051803 | 0.0069898 | 0.055455 | -0.0092542 | 0.06733 | -61.3129 | 60.0723 | -61.3174 | -61.3312 | 60.1135 | 0.11444 | -0.28839 | 0.013733 | 60.1913 | -61.409 | -0.10071 | -0.27008 | -0.09613 | -0.11444 | -0.22888 | -0.19226 | -0.15106 | 0.004578 | 60.9283 | 61.2305 | 121.3303 | 121.2891 | -0.09613 | 121.4081 | 61.3312 | -0.19226 | 121.2891 | -0.09613 | 61.3312 | 121.3303 | 121.4081 | -121.6599 | -121.7514
126.8125 | 121.8887 | -61.1847 | 60.4111 | -0.098801 | 0.014328 | 0.0038985 | 0.0029308 | 0.053105 | -0.0056226 | 0.065407 | -61.2488 | 60.1868 | -61.2396 | -61.2442 | 60.2005 | 0.28839 | 0.050354 | 0.27466 | 60.2783 | -61.3129 | -0.054932 | -0.2243 | -0.064087 | -0.05951 | -0.21057 | -0.12817 | -0.13275 | -0.009155 | 61.235 | 61.4594 | 121.3852 | 121.3715 | -0.064087 | 121.463 | 61.4731 | -0.12817 | 121.3715 | -0.064087 | 61.4731 | 121.3852 | 121.463 | -121.6507 | -121.7239
128.5625 | 121.8201 | -61.2808 | 60.3333 | -0.18272 | 0.015182 | 0.0041123 | 0.010835 | 0.053532 | -0.012458 | 0.065193 | -61.3266 | 60.1959 | -61.3266 | -61.3403 | 60.0861 | 0.2243 | 0.16479 | 0.11444 | 60.3333 | -61.3403 | -0.045776 | -0.13733 | -0.045776 | -0.059509 | -0.24719 | -0.059509 | 0 | 0 | 61.4456 | 61.3953 | 121.3669 | 121.4767 | -0.045776 | 121.6141 | 61.5051 | -0.059509 | 121.4767 | -0.045776 | 61.5051 | 121.3669 | 121.6141 | -121.6599 | -121.6736
130.3125 | 121.8887 | -61.2305 | 60.2921 | 0.15297 | 0.01625 | 0.0034713 | 0.0076306 | 0.054173 | -0.0086132 | 0.066262 | -61.3861 | 60.1044 | -61.3586 | -61.3998 | 60.0403 | 0.045776 | -0.24261 | -0.10071 | 60.2188 | -61.3998 | -0.12817 | -0.18768 | -0.15564 | -0.16937 | -0.25177 | -0.16937 | -0.073242 | -0.027465 | 60.9879 | 61.1298 | 121.2708 | 121.3348 | -0.15564 | 121.4493 | 61.2762 | -0.16937 | 121.3348 | -0.15564 | 61.2762 | 121.2708 | 121.4493 | -121.6507 | -121.6919
131.9844 | 121.875 | -61.1893 | 60.4156 | -0.091171 | 0.013473 | 0.0068893 | 0.00229 | 0.052891 | -0.0096814 | 0.066689 | -61.2305 | 60.2005 | -61.2076 | -61.2213 | 60.2005 | 0.31586 | 0.027466 | 0.27924 | 60.2783 | -61.3266 | -0.018311 | -0.21515 | -0.041199 | -0.032043 | -0.21515 | -0.13733 | -0.13733 | -0.022888 | 61.2167 | 61.4685 | 121.3898 | 121.3898 | -0.041199 | 121.4676 | 61.5051 | -0.13733 | 121.3898 | -0.041199 | 61.5051 | 121.3898 | 121.4676 | -121.6232 | -121.7422
133.7188 | 121.8292 | -61.2396 | 60.3699 | -0.26665 | 0.015396 | 0.0036849 | 0.0046398 | 0.053746 | -0.008186 | 0.065407 | -61.2534 | 60.1913 | -61.2534 | -61.29 | 60.141 | 0.29755 | 0.2243 | 0.24719 | 60.3058 | -61.3586 | -0.013733 | -0.17853 | -0.013733 | -0.050354 | -0.22888 | -0.11902 | -0.064087 | 0 | 61.4639 | 61.4868 | 121.3806 | 121.431 | -0.013733 | 121.5454 | 61.5372 | -0.11902 | 121.431 | -0.013733 | 61.5372 | 121.3806 | 121.5454 | -121.6232 | -121.7285
135.3906 | 121.9345 | -61.2579 | 60.2692 | 0.10719 | 0.017532 | 0.0036849 | 0.0093396 | 0.056523 | -0.010963 | 0.068398 | -61.4227 | 60.1089 | -61.3678 | -61.4731 | 59.967 | -0.013733 | -0.1236 | -0.1831 | 60.2417 | -61.4502 | -0.10986 | -0.16022 | -0.16479 | -0.21515 | -0.30212 | -0.19226 | -0.027466 | -0.054931 | 61.1343 | 61.0748 | 121.225 | 121.3669 | -0.16479 | 121.4996 | 61.2442 | -0.19226 | 121.3669 | -0.16479 | 61.2442 | 121.225 | 121.4996 | -121.637 | -121.7194
137.1406 | 121.9208 | -61.2442 | 60.3149 | 0.13008 | 0.0186 | 0.0066757 | 0.0078442 | 0.055241 | -0.0066906 | 0.067757 | -61.3953 | 60.1501 | -61.3815 | -61.4319 | 59.9899 | 0.022888 | -0.20599 | -0.13733 | 60.1868 | -61.4548 | -0.13733 | -0.16479 | -0.15106 | -0.18768 | -0.32501 | -0.21057 | -0.12817 | -0.013733 | 61.0382 | 61.1069 | 121.2341 | 121.3943 | -0.15106 | 121.431 | 61.2671 | -0.21057 | 121.3943 | -0.15106 | 61.2671 | 121.2341 | 121.431 | -121.6965 | -121.7697
138.8281 | 121.8155 | -61.2762 | 60.3882 | -0.17509 | 0.0139 | 5.3338e-05 | 0.0063488 | 0.052891 | -0.009895 | 0.068398 | -61.2488 | 60.1822 | -61.2534 | -61.2442 | 60.2005 | 0.33417 | 0.14191 | 0.32044 | 60.2875 | -61.3266 | 0.022888 | -0.20599 | 0.027466 | 0.032043 | -0.18768 | -0.050354 | -0.10071 | 0.004578 | 61.4182 | 61.5967 | 121.4767 | 121.4584 | 0.027466 | 121.5637 | 61.6104 | -0.050354 | 121.4584 | 0.027466 | 61.6104 | 121.4767 | 121.5637 | -121.6415 | -121.7148
140.5938 | 121.9254 | -61.1847 | 60.3607 | 0.10719 | 0.016464 | 0.0088119 | 0.0042126 | 0.052464 | -0.0073316 | 0.067543 | -61.3129 | 60.1364 | -61.3037 | -61.3403 | 60.0952 | 0.14191 | -0.16479 | 0.054932 | 60.1913 | -61.3953 | -0.11902 | -0.2243 | -0.12817 | -0.15564 | -0.2655 | -0.21057 | -0.16937 | -0.009155 | 61.0199 | 61.2396 | 121.2799 | 121.3211 | -0.12817 | 121.376 | 61.3266 | -0.21057 | 121.3211 | -0.12817 | 61.3266 | 121.2799 | 121.376 | -121.6644 | -121.756
142.3281 | 121.8887 | -61.2488 | 60.347 | 0.16823 | 0.014328 | 0.0060349 | 0.0076306 | 0.053746 | -0.0096814 | 0.069466 | -61.3129 | 60.0952 | -61.3358 | -61.3449 | 60.0952 | 0.10986 | -0.27924 | 0.018311 | 60.1547 | -61.409 | -0.086975 | -0.25177 | -0.064087 | -0.096131 | -0.25177 | -0.16022 | -0.19226 | 0.022888 | 60.9695 | 61.2671 | 121.344 | 121.344 | -0.064087 | 121.4035 | 61.3586 | -0.16022 | 121.344 | -0.064087 | 61.3586 | 121.344 | 121.4035 | -121.6827 | -121.756
144.0156 | 121.9208 | -61.1938 | 60.3928 | -0.014877 | 0.014755 | -0.00080106 | 0.0042126 | 0.050968 | -0.0069042 | 0.069466 | -61.3174 | 60.1776 | -61.2442 | -61.3083 | 60.1273 | 0.21057 | 0 | 0.16479 | 60.2371 | -61.3632 | -0.050354 | -0.21515 | -0.1236 | -0.11444 | -0.2655 | -0.16937 | -0.15564 | -0.073242 | 61.1938 | 61.3586 | 121.3211 | 121.3715 | -0.1236 | 121.431 | 61.4044 | -0.16937 | 121.3715 | -0.1236 | 61.4044 | 121.3211 | 121.431 | -121.637 | -121.756
145.7656 | 121.8933 | -61.2213 | 60.3287 | 0.10719 | 0.016037 | 0.0062485 | 0.0052808 | 0.053959 | -0.0096814 | 0.067543 | -61.3129 | 60.1135 | -61.3266 | -61.3266 | 60.0998 | 0.11902 | -0.23804 | 0.032043 | 60.2005 | -61.3815 | -0.10529 | -0.21515 | -0.091553 | -0.10529 | -0.22888 | -0.16022 | -0.12817 | 0.013733 | 60.9833 | 61.2534 | 121.3211 | 121.3348 | -0.091553 | 121.4218 | 61.3403 | -0.16022 | 121.3348 | -0.091553 | 61.3403 | 121.3211 | 121.4218 | -121.6553 | -121.7102
147.4375 | 121.9345 | -61.1847 | 60.3195 | 0.084305 | 0.012191 | -0.00080106 | 0.0067762 | 0.052037 | -0.0083996 | 0.065407 | -61.3174 | 60.1456 | -61.3037 | -61.3403 | 60.0861 | 0.13733 | -0.10986 | 0.059509 | 60.2142 | -61.377 | -0.11902 | -0.17395 | -0.13275 | -0.15564 | -0.23346 | -0.19226 | -0.10529 | -0.013733 | 61.0748 | 61.2442 | 121.2708 | 121.3303 | -0.13275 | 121.3989 | 61.322 | -0.19226 | 121.3303 | -0.13275 | 61.322 | 121.2708 | 121.3989 | -121.6232 | -121.6965
149.1719 | 121.8704 | -61.2259 | 60.3287 | 0.099564 | 0.017532 | 0.014153 | 0.011049 | 0.053746 | -0.008186 | 0.067116 | -61.3403 | 60.0998 | -61.3358 | -61.3403 | 60.0815 | 0.11444 | -0.28381 | -0.032043 | 60.1913 | -61.3953 | -0.10986 | -0.22888 | -0.11444 | -0.11444 | -0.24719 | -0.16937 | -0.13733 | -0.004578 | 60.9421 | 61.1938 | 121.3074 | 121.3257 | -0.11444 | 121.4172 | 61.3403 | -0.16937 | 121.3257 | -0.11444 | 61.3403 | 121.3074 | 121.4172 | -121.6644 | -121.7239
150.9375 | 121.7926 | -61.3266 | 60.3241 | -0.10643 | 0.013046 | 0.0094527 | 0.012758 | 0.052677 | -0.0083996 | 0.068398 | -61.3312 | 60.1501 | -61.3358 | -61.3403 | 60.0723 | 0.1831 | 0 | 0.068665 | 60.2417 | -61.3907 | -0.009155 | -0.17395 | -0.004578 | -0.013733 | -0.25177 | -0.064087 | -0.082398 | 0.004577 | 61.3266 | 61.3953 | 121.3989 | 121.4767 | -0.004578 | 121.5683 | 61.5097 | -0.064087 | 121.4767 | -0.004578 | 61.5097 | 121.3989 | 121.5683 | -121.6599 | -121.7148
152.6875 | 121.8155 | -61.2854 | 60.3058 | -0.16747 | 0.016464 | 0.0032577 | 0.009126 | 0.053746 | -0.0090406 | 0.066475 | -61.3312 | 60.2325 | -61.29 | -61.3403 | 60.0815 | 0.21515 | 0.15564 | 0.11444 | 60.3058 | -61.3724 | -0.004578 | -0.073242 | -0.045777 | -0.054932 | -0.2243 | -0.086975 | 0 | -0.041199 | 61.441 | 61.3998 | 121.3669 | 121.5179 | -0.045777 | 121.5912 | 61.5005 | -0.086975 | 121.5179 | -0.045777 | 61.5005 | 121.3669 | 121.5912 | -121.5958 | -121.6782
154.4219 | 121.7926 | -61.3037 | 60.3012 | -0.18272 | 0.014541 | 0.0073165 | 0.0093396 | 0.055455 | -0.010322 | 0.065834 | -61.3129 | 60.228 | -61.29 | -61.3449 | 60.0861 | 0.21057 | 0.10529 | 0.091553 | 60.2966 | -61.3907 | 0.013733 | -0.073242 | -0.009155 | -0.041199 | -0.21515 | -0.086975 | -0.004577 | -0.022888 | 61.409 | 61.3953 | 121.3898 | 121.5317 | -0.009155 | 121.6003 | 61.5143 | -0.086975 | 121.5317 | -0.009155 | 61.5143 | 121.3898 | 121.6003 | -121.5912 | -121.6919
156.125 | 121.9025 | -61.203 | 60.3607 | 0.061417 | 0.015396 | 0.0045395 | 0.0025036 | 0.054173 | -0.0073316 | 0.067543 | -61.3129 | 60.1639 | -61.2808 | -61.3403 | 60.1089 | 0.13733 | -0.09613 | 0.068665 | 60.2325 | -61.3907 | -0.07782 | -0.19684 | -0.10986 | -0.13733 | -0.25177 | -0.18768 | -0.12817 | -0.032043 | 61.1069 | 61.2717 | 121.312 | 121.3669 | -0.10986 | 121.4355 | 61.3403 | -0.18768 | 121.3669 | -0.10986 | 61.3403 | 121.312 | 121.4355 | -121.6415 | -121.7514
157.8125 | 121.8796 | -61.2213 | 60.3241 | 0.1606 | 0.015396 | 0.0011215 | 0.0078442 | 0.0546 | -0.0083996 | 0.067757 | -61.3724 | 60.0861 | -61.3632 | -61.3678 | 60.0632 | 0.082397 | -0.27466 | -0.041199 | 60.1868 | -61.3861 | -0.14191 | -0.23804 | -0.15106 | -0.14648 | -0.26093 | -0.16479 | -0.13733 | -0.009155 | 60.9467 | 61.1801 | 121.2845 | 121.3074 | -0.15106 | 121.4081 | 61.3037 | -0.16479 | 121.3074 | -0.15106 | 61.3037 | 121.2845 | 121.4081 | -121.6873 | -121.7102
159.5469 | 121.8063 | -61.235 | 60.3836 | -0.17509 | 0.014969 | 0.0032577 | 0.0048534 | 0.054386 | -0.010963 | 0.066262 | -61.2259 | 60.1685 | -61.2122 | -61.2488 | 60.1913 | 0.35706 | 0.11902 | 0.3067 | 60.3058 | -61.3312 | 0.022888 | -0.21515 | 0.009155 | -0.013733 | -0.19226 | -0.096131 | -0.07782 | -0.013733 | 61.3541 | 61.5417 | 121.4264 | 121.4035 | 0.009155 | 121.5408 | 61.5921 | -0.096131 | 121.4035 | 0.009155 | 61.5921 | 121.4264 | 121.5408 | -121.5958 | -121.7148
161.3125 | 121.907 | -61.203 | 60.379 | 0.12245 | 0.012832 | 0.0053939 | 0.0067762 | 0.052037 | -0.0073316 | 0.067543 | -61.3129 | 60.1181 | -61.3037 | -61.3403 | 60.1135 | 0.14191 | -0.15564 | 0.054932 | 60.1822 | -61.377 | -0.10071 | -0.26093 | -0.10986 | -0.13733 | -0.2655 | -0.17395 | -0.19684 | -0.009155 | 61.0474 | 61.2579 | 121.3165 | 121.3211 | -0.10986 | 121.3852 | 61.3449 | -0.17395 | 121.3211 | -0.10986 | 61.3449 | 121.3165 | 121.3852 | -121.6827 | -121.756
163 | 121.7743 | -61.3174 | 60.2875 | -0.091171 | 0.015182 | 0.0038985 | 0.01233 | 0.0546 | -0.010963 | 0.068825 | -61.3312 | 60.1776 | -61.3358 | -61.3449 | 60.0677 | 0.1831 | 0.013733 | 0.068665 | 60.2509 | -61.3815 | -0.01831 | -0.10986 | -0.013733 | -0.027466 | -0.21973 | -0.064087 | -0.036622 | 0.004577 | 61.3312 | 61.3861 | 121.3852 | 121.4951 | -0.013733 | 121.5683 | 61.5005 | -0.064087 | 121.4951 | -0.013733 | 61.5005 | 121.3852 | 121.5683 | -121.6232 | -121.669
164.75 | 121.9528 | -61.1755 | 60.3836 | 0.046158 | 0.014755 | 0.0051803 | 0.0027172 | 0.053105 | -0.008827 | 0.068611 | -61.3129 | 60.1501 | -61.2717 | -61.3449 | 60.0998 | 0.17395 | -0.041199 | 0.10071 | 60.2783 | -61.3724 | -0.09613 | -0.23346 | -0.13733 | -0.16937 | -0.28381 | -0.19684 | -0.10529 | -0.041199 | 61.1343 | 61.2762 | 121.2753 | 121.3257 | -0.13733 | 121.4539 | 61.3495 | -0.19684 | 121.3257 | -0.13733 | 61.3495 | 121.2753 | 121.4539 | -121.6553 | -121.756
166.4844 | 121.875 | -61.2305 | 60.3561 | 0.16823 | 0.014541 | 0.0047531 | 0.009126 | 0.053959 | -0.008186 | 0.069252 | -61.3174 | 60.0494 | -61.3403 | -61.3449 | 60.0906 | 0.10529 | -0.30212 | 0.004578 | 60.2051 | -61.377 | -0.10986 | -0.3067 | -0.086975 | -0.11444 | -0.2655 | -0.14648 | -0.15106 | 0.022888 | 60.9283 | 61.235 | 121.3211 | 121.2799 | -0.086975 | 121.4355 | 61.3358 | -0.14648 | 121.2799 | -0.086975 | 61.3358 | 121.3211 | 121.4355 | -121.6965 | -121.7331
168.2188 | 121.8933 | -61.235 | 60.3378 | 0.15297 | 0.014114 | 0.0060349 | 0.0080578 | 0.052677 | -0.0094678 | 0.066048 | -61.3129 | 60.0769 | -61.322 | -61.3449 | 60.0861 | 0.10529 | -0.29755 | -0.018311 | 60.2051 | -61.4182 | -0.086975 | -0.26093 | -0.07782 | -0.10986 | -0.25177 | -0.18311 | -0.13275 | 0.009155 | 60.9375 | 61.2167 | 121.3211 | 121.3119 | -0.07782 | 121.4401 | 61.3403 | -0.18311 | 121.3119 | -0.07782 | 61.3403 | 121.3211 | 121.4401 | -121.6599 | -121.756
169.9062 | 121.7697 | -61.3174 | 60.3012 | -0.075912 | 0.014114 | 0.0026169 | 0.0093396 | 0.053318 | -0.0086132 | 0.068184 | -61.3358 | 60.1318 | -61.3129 | -61.3312 | 60.0586 | 0.17853 | 0 | 0.059509 | 60.2509 | -61.3907 | 0.004578 | -0.16937 | -0.01831 | -0.013733 | -0.24261 | -0.073242 | -0.050354 | -0.022888 | 61.3174 | 61.377 | 121.376 | 121.4493 | -0.01831 | 121.5683 | 61.496 | -0.073242 | 121.4493 | -0.01831 | 61.496 | 121.376 | 121.5683 | -121.6141 | -121.6919
171.6562 | 121.9208 | -61.2946 | 60.2417 | 0.091934 | 0.015396 | 0.0032577 | 0.0078442 | 0.054173 | -0.01075 | 0.067116 | -61.4273 | 60.1089 | -61.3953 | -61.4731 | 59.9625 | -0.009155 | -0.12817 | -0.17853 | 60.228 | -61.4365 | -0.10071 | -0.13275 | -0.13275 | -0.17853 | -0.27924 | -0.14191 | -0.013733 | -0.032043 | 61.1664 | 61.116 | 121.257 | 121.4035 | -0.13275 | 121.5225 | 61.2854 | -0.14191 | 121.4035 | -0.13275 | 61.2854 | 121.257 | 121.5225 | -121.637 | -121.6782
173.4062 | 121.8796 | -61.2259 | 60.3516 | 0.13771 | 0.014969 | 0.0068893 | 0.0052808 | 0.054173 | -0.008186 | 0.06797 | -61.29 | 60.1227 | -61.29 | -61.3449 | 60.0952 | 0.10529 | -0.30212 | -0.009155 | 60.1822 | -61.4227 | -0.064087 | -0.22888 | -0.064087 | -0.11902 | -0.25635 | -0.19684 | -0.16937 | 0 | 60.9238 | 61.2167 | 121.3211 | 121.3486 | -0.064087 | 121.4081 | 61.3312 | -0.19684 | 121.3486 | -0.064087 | 61.3312 | 121.3211 | 121.4081 | -121.6415 | -121.7743
175.1562 | 121.8658 | -61.2122 | 60.4019 | -0.14458 | 0.015823 | 0.0026169 | 0.0020764 | 0.050755 | -0.0077588 | 0.067116 | -61.235 | 60.1959 | -61.235 | -61.235 | 60.2142 | 0.32501 | 0.036621 | 0.29755 | 60.2509 | -61.3312 | -0.022888 | -0.20599 | -0.022888 | -0.022888 | -0.18768 | -0.11902 | -0.15106 | 0 | 61.2488 | 61.5097 | 121.4264 | 121.4081 | -0.022888 | 121.463 | 61.5372 | -0.11902 | 121.4081 | -0.022888 | 61.5372 | 121.4264 | 121.463 | -121.637 | -121.7331
176.8281 | 121.9208 | -61.2442 | 60.3012 | 0.091934 | 0.015182 | 0.0062485 | 0.010194 | 0.053318 | -0.01139 | 0.069039 | -61.3953 | 60.141 | -61.3678 | -61.4319 | 59.9762 | 0.013733 | -0.15564 | -0.14648 | 60.2646 | -61.4227 | -0.1236 | -0.16022 | -0.15106 | -0.18768 | -0.32501 | -0.17853 | -0.036621 | -0.027466 | 61.0886 | 61.0977 | 121.2204 | 121.3852 | -0.15106 | 121.5088 | 61.2579 | -0.17853 | 121.3852 | -0.15106 | 61.2579 | 121.2204 | 121.5088 | -121.669 | -121.7239
178.5625 | 121.9116 | -61.2671 | 60.2829 | 0.069046 | 0.015396 | 0.0024033 | 0.0089124 | 0.056095 | -0.012245 | 0.068398 | -61.4182 | 60.141 | -61.3678 | -61.4685 | 59.9533 | -0.004578 | -0.082397 | -0.16937 | 60.2692 | -61.4319 | -0.10071 | -0.14191 | -0.15106 | -0.20142 | -0.32959 | -0.16479 | -0.013733 | -0.050354 | 61.1847 | 61.0977 | 121.2204 | 121.4081 | -0.15106 | 121.5363 | 61.2625 | -0.16479 | 121.4081 | -0.15106 | 61.2625 | 121.2204 | 121.5363 | -121.6507 | -121.7148
180.2344 | 121.9162 | -61.1847 | 60.3745 | -0.045395 | 0.017105 | 0.0024033 | 0.0050672 | 0.052891 | -0.0079724 | 0.067543 | -61.2946 | 60.1913 | -61.2442 | -61.2762 | 60.1776 | 0.27008 | 0.036621 | 0.22888 | 60.2921 | -61.3266 | -0.05951 | -0.18311 | -0.10986 | -0.091553 | -0.19684 | -0.14191 | -0.082398 | -0.050354 | 61.2213 | 61.4136 | 121.3623 | 121.376 | -0.10986 | 121.4767 | 61.4548 | -0.14191 | 121.376 | -0.10986 | 61.4548 | 121.3623 | 121.4767 | -121.6187 | -121.7011
181.9844 | 121.8384 | -61.2854 | 60.3653 | -0.2285 | 0.015396 | 0.00026694 | 0.0065624 | 0.051609 | -0.010322 | 0.066475 | -61.3358 | 60.1959 | -61.2671 | -61.3312 | 60.1044 | 0.27008 | 0.24719 | 0.19226 | 60.3424 | -61.3495 | 0.01831 | -0.16937 | -0.050354 | -0.045777 | -0.26093 | -0.064087 | -0.022888 | -0.068664 | 61.5326 | 61.4777 | 121.3898 | 121.4813 | -0.050354 | 121.6278 | 61.5555 | -0.064087 | 121.4813 | -0.050354 | 61.5555 | 121.3898 | 121.6278 | -121.6324 | -121.7148
183.7188 | 121.9482 | -61.1893 | 60.3516 | 0.046158 | 0.015609 | 0.0049667 | 0.0063488 | 0.052464 | -0.008827 | 0.066902 | -61.3129 | 60.1501 | -61.2717 | -61.3312 | 60.1089 | 0.16022 | -0.045776 | 0.09613 | 60.2554 | -61.3724 | -0.082397 | -0.20142 | -0.1236 | -0.14191 | -0.24261 | -0.1831 | -0.09613 | -0.041199 | 61.1435 | 61.2854 | 121.2982 | 121.3394 | -0.1236 | 121.4447 | 61.3495 | -0.1831 | 121.3394 | -0.1236 | 61.3495 | 121.2982 | 121.4447 | -121.6232 | -121.7239
185.4531 | 121.788 | -61.2305 | 60.4477 | -0.17509 | 0.015609 | 0.0045395 | 0.007417 | 0.052037 | -0.0090406 | 0.067757 | -61.2076 | 60.2188 | -61.1893 | -61.2122 | 60.2234 | 0.36621 | 0.10071 | 0.33875 | 60.2646 | -61.3449 | 0.041199 | -0.22888 | 0.022888 | 0.018311 | -0.2243 | -0.11444 | -0.18311 | -0.018311 | 61.3312 | 61.5692 | 121.4539 | 121.4493 | 0.022888 | 121.4951 | 61.5967 | -0.11444 | 121.4493 | 0.022888 | 61.5967 | 121.4539 | 121.4951 | -121.637 | -121.7926
187.1406 | 121.8796 | -61.2305 | 60.3195 | 0.13771 | 0.015823 | 0.0028305 | 0.0065624 | 0.055027 | -0.0066906 | 0.065407 | -61.3037 | 60.1044 | -61.322 | -61.3358 | 60.0861 | 0.11444 | -0.29755 | -0.022888 | 60.1913 | -61.4136 | -0.091552 | -0.21515 | -0.073242 | -0.10529 | -0.23346 | -0.1831 | -0.12817 | 0.01831 | 60.9329 | 61.2076 | 121.3165 | 121.3348 | -0.073242 | 121.4218 | 61.3449 | -0.1831 | 121.3348 | -0.073242 | 61.3449 | 121.3165 | 121.4218 | -121.6415 | -121.7331
188.8906 | 121.8887 | -61.2305 | 60.3287 | 0.39711 | 0.014755 | 0.0090255 | 0.0097668 | 0.057163 | -0.009895 | 0.06733 | -61.3129 | 60.0861 | -61.3358 | -61.3358 | 60.0769 | 0.11444 | -0.29297 | -0.022888 | 60.1776 | -61.3998 | -0.10529 | -0.24261 | -0.082397 | -0.10529 | -0.25177 | -0.16937 | -0.15106 | 0.022888 | 60.9375 | 61.2076 | 121.3074 | 121.3165 | -0.082397 | 121.4081 | 61.3449 | -0.16937 | 121.3165 | -0.082397 | 61.3449 | 121.3074 | 121.4081 | -121.6644 | -121.7285
190.5781 | 121.8109 | -61.2488 | 60.3973 | -0.20561 | 0.014114 | 5.3338e-05 | 0.005708 | 0.052891 | -0.0079724 | 0.066048 | -61.2442 | 60.1913 | -61.235 | -61.235 | 60.1868 | 0.33875 | 0.18768 | 0.31128 | 60.2875 | -61.3312 | 0.013733 | -0.20599 | 0.004577 | 0.013733 | -0.21057 | -0.082398 | -0.10986 | -0.009156 | 61.4365 | 61.5601 | 121.4355 | 121.4401 | 0.004577 | 121.5363 | 61.5875 | -0.082398 | 121.4401 | 0.004577 | 61.5875 | 121.4355 | 121.5363 | -121.6324 | -121.7285
192.3281 | 121.8018 | -61.2259 | 60.4019 | -0.19035 | 0.014328 | 0.0058211 | 0.0046398 | 0.052891 | -0.0096814 | 0.066262 | -61.2396 | 60.2005 | -61.2396 | -61.2488 | 60.1913 | 0.3479 | 0.12817 | 0.32501 | 60.2829 | -61.3449 | -0.013733 | -0.20142 | -0.013733 | -0.022888 | -0.21057 | -0.11902 | -0.11902 | 0 | 61.3541 | 61.5509 | 121.4172 | 121.4264 | -0.013733 | 121.5088 | 61.5738 | -0.11902 | 121.4264 | -0.013733 | 61.5738 | 121.4172 | 121.5088 | -121.6415 | -121.7468
194.0781 | 121.8979 | -61.2076 | 60.3653 | 0.091934 | 0.0139 | 0.0085983 | 0.0065624 | 0.052891 | -0.0060498 | 0.067543 | -61.3037 | 60.1501 | -61.2854 | -61.3174 | 60.0998 | 0.12817 | -0.21973 | 0.045776 | 60.1776 | -61.4227 | -0.077819 | -0.21515 | -0.09613 | -0.10986 | -0.2655 | -0.21515 | -0.18768 | -0.018311 | 60.9879 | 61.2534 | 121.3074 | 121.3577 | -0.09613 | 121.3852 | 61.3358 | -0.21515 | 121.3577 | -0.09613 | 61.3358 | 121.3074 | 121.3852 | -121.6507 | -121.788
195.8281 | 121.8063 | -61.2991 | 60.3287 | -0.083542 | 0.014969 | 0.0011215 | 0.0097668 | 0.054173 | -0.009895 | 0.068398 | -61.3312 | 60.1364 | -61.3632 | -61.3312 | 60.0723 | 0.16937 | -0.041199 | 0.045776 | 60.2509 | -61.4044 | -0.064087 | -0.19226 | -0.032044 | -0.032044 | -0.25635 | -0.10529 | -0.07782 | 0.032043 | 61.2579 | 61.3449 | 121.3715 | 121.4355 | -0.032044 | 121.55 | 61.4685 | -0.10529 | 121.4355 | -0.032044 | 61.4685 | 121.3715 | 121.55 | -121.6919 | -121.7331
197.5625 | 121.875 | -61.2122 | 60.3195 | 0.1606 | 0.013473 | 0.0013351 | 0.0082714 | 0.054386 | -0.0090406 | 0.068184 | -61.3083 | 60.0861 | -61.3266 | -61.3403 | 60.0952 | 0.10071 | -0.3067 | -0.013733 | 60.1913 | -61.4044 | -0.11444 | -0.23346 | -0.096131 | -0.12817 | -0.2243 | -0.19226 | -0.12817 | 0.01831 | 60.9055 | 61.1984 | 121.3074 | 121.2982 | -0.096131 | 121.4035 | 61.3129 | -0.19226 | 121.2982 | -0.096131 | 61.3129 | 121.3074 | 121.4035 | -121.6461 | -121.7239
199.2344 | 121.8292 | -61.2122 | 60.4065 | -0.15221 | 0.015609 | 0.0028305 | 0.0016492 | 0.053318 | -0.0058362 | 0.068611 | -61.2259 | 60.2005 | -61.2442 | -61.235 | 60.2051 | 0.32044 | 0.018311 | 0.30212 | 60.3058 | -61.3266 | -0.032044 | -0.20599 | -0.013733 | -0.022888 | -0.20142 | -0.11444 | -0.10071 | 0.018311 | 61.2305 | 61.5143 | 121.4172 | 121.4127 | -0.013733 | 121.5179 | 61.5326 | -0.11444 | 121.4127 | -0.013733 | 61.5326 | 121.4172 | 121.5179 | -121.6507 | -121.7331
200.9844 | 121.8384 | -61.2625 | 60.3745 | -0.23613 | 0.01326 | -0.0010147 | 0.007417 | 0.051396 | -0.0096814 | 0.065407 | -61.2625 | 60.1913 | -61.2305 | -61.2808 | 60.1318 | 0.28839 | 0.24261 | 0.2243 | 60.3104 | -61.3449 | 0.032043 | -0.18311 | 0 | -0.018311 | -0.24262 | -0.082398 | -0.064087 | -0.032043 | 61.5051 | 61.4868 | 121.3943 | 121.4539 | 0 | 121.5729 | 61.5509 | -0.082398 | 121.4539 | 0 | 61.5509 | 121.3943 | 121.5729 | -121.6049 | -121.7194
202.7344 | 121.843 | -61.2671 | 60.347 | -0.37346 | 0.0186 | 0.0058211 | 0.0078442 | 0.050541 | -0.0079724 | 0.066902 | -61.3129 | 60.2325 | -61.2762 | -61.3266 | 60.0906 | 0.26093 | 0.25635 | 0.19226 | 60.3104 | -61.3678 | -0.009155 | -0.11444 | -0.045776 | -0.059509 | -0.25635 | -0.10071 | -0.036621 | -0.036621 | 61.5234 | 61.4594 | 121.3577 | 121.4996 | -0.045776 | 121.5775 | 61.528 | -0.10071 | 121.4996 | -0.045776 | 61.528 | 121.3577 | 121.5775 | -121.6232 | -121.7148
204.4219 | 121.9254 | -61.29 | 60.2509 | 0.10719 | 0.014969 | 0.0058211 | 0.0095532 | 0.053532 | -0.0094678 | 0.066048 | -61.4273 | 60.1456 | -61.3861 | -61.4685 | 59.9487 | -0.009155 | -0.13275 | -0.1831 | 60.2188 | -61.4456 | -0.09613 | -0.10528 | -0.13733 | -0.17853 | -0.30212 | -0.15564 | -0.032043 | -0.041199 | 61.1572 | 61.1069 | 121.2387 | 121.4355 | -0.13733 | 121.5088 | 61.2808 | -0.15564 | 121.4355 | -0.13733 | 61.2808 | 121.2387 | 121.5088 | -121.637 | -121.6965
206.1875 | 121.8018 | -61.3037 | 60.3333 | -0.11406 | 0.01625 | 0.0060349 | 0.008485 | 0.055241 | -0.009895 | 0.065834 | -61.3403 | 60.1364 | -61.3449 | -61.3403 | 60.0769 | 0.19226 | 0.032043 | 0.086975 | 60.2875 | -61.3678 | -0.041199 | -0.19684 | -0.036621 | -0.036621 | -0.25635 | -0.064087 | -0.045776 | 0.004578 | 61.3358 | 61.3907 | 121.3806 | 121.4401 | -0.036621 | 121.5912 | 61.496 | -0.064087 | 121.4401 | -0.036621 | 61.496 | 121.3806 | 121.5912 | -121.6782 | -121.7011
207.9375 | 121.8109 | -61.3037 | 60.3104 | -0.060654 | 0.014541 | 0.0053939 | 0.0099804 | 0.053532 | -0.012031 | 0.068184 | -61.3266 | 60.1364 | -61.3358 | -61.3815 | 60.0449 | 0.13733 | -0.041199 | -0.009155 | 60.2829 | -61.3953 | -0.032043 | -0.17395 | -0.022888 | -0.07782 | -0.2655 | -0.091553 | -0.027466 | 0.009155 | 61.2625 | 61.2946 | 121.3486 | 121.4401 | -0.022888 | 121.5866 | 61.441 | -0.091553 | 121.4401 | -0.022888 | 61.441 | 121.3486 | 121.5866 | -121.6461 | -121.7056
209.6719 | 121.8063 | -61.2305 | 60.4202 | -0.19035 | 0.015823 | 0.0049667 | 0.0025036 | 0.053959 | -0.0079724 | 0.06733 | -61.2167 | 60.2142 | -61.1984 | -61.2488 | 60.2005 | 0.35706 | 0.09613 | 0.33875 | 60.26 | -61.3449 | 0.032044 | -0.20599 | 0.013733 | -0.01831 | -0.21973 | -0.11444 | -0.16022 | -0.018311 | 61.3266 | 61.5692 | 121.431 | 121.4447 | 0.013733 | 121.4905 | 61.5875 | -0.11444 | 121.4447 | 0.013733 | 61.5875 | 121.431 | 121.4905 | -121.6187 | -121.7651
211.3594 | 121.9345 | -61.2625 | 60.2646 | 0.12245 | 0.017532 | 0.0038985 | 0.0082714 | 0.056095 | -0.010322 | 0.067116 | -61.441 | 60.0861 | -61.4044 | -61.4731 | 59.9579 | 0.009155 | -0.14648 | -0.16022 | 60.2646 | -61.4639 | -0.14191 | -0.17853 | -0.17853 | -0.21057 | -0.3067 | -0.20142 | 0 | -0.036621 | 61.116 | 61.1023 | 121.2204 | 121.3486 | -0.17853 | 121.5271 | 61.2717 | -0.20142 | 121.3486 | -0.17853 | 61.2717 | 121.2204 | 121.5271 | -121.669 | -121.7285
213.125 | 121.8201 | -61.3129 | 60.2966 | -0.060654 | 0.015823 | 0.0051803 | 0.0097668 | 0.055027 | -0.0090406 | 0.069252 | -61.3312 | 60.1456 | -61.3358 | -61.3586 | 60.0723 | 0.15106 | -0.045776 | 0.009155 | 60.2554 | -61.4136 | -0.022888 | -0.15106 | -0.018311 | -0.045777 | -0.2243 | -0.10071 | -0.041199 | 0.004577 | 61.2671 | 61.322 | 121.3852 | 121.4584 | -0.018311 | 121.5683 | 61.4639 | -0.10071 | 121.4584 | -0.018311 | 61.4639 | 121.3852 | 121.5683 | -121.6324 | -121.7102
214.8125 | 121.8887 | -61.2396 | 60.3333 | 0.15297 | 0.014114 | 0.0056075 | 0.0065624 | 0.056523 | -0.008827 | 0.069252 | -61.3358 | 60.1044 | -61.3358 | -61.3678 | 60.0815 | 0.10529 | -0.28839 | -0.027466 | 60.2005 | -61.4182 | -0.09613 | -0.22888 | -0.09613 | -0.12817 | -0.25177 | -0.17853 | -0.13275 | 0 | 60.9512 | 61.2122 | 121.3211 | 121.344 | -0.09613 | 121.4401 | 61.3449 | -0.17853 | 121.344 | -0.09613 | 61.3449 | 121.3211 | 121.4401 | -121.669 | -121.7514
216.5625 | 121.8155 | -61.2991 | 60.3241 | -0.022507 | 0.014969 | 0.00090794 | 0.010621 | 0.055668 | -0.011177 | 0.065193 | -61.3632 | 60.1318 | -61.3678 | -61.4273 | 60.0082 | 0.082397 | -0.064087 | -0.068665 | 60.2417 | -61.4319 | -0.068665 | -0.19226 | -0.064087 | -0.12817 | -0.31586 | -0.13275 | -0.082398 | 0.004578 | 61.235 | 61.2305 | 121.3074 | 121.431 | -0.064087 | 121.5408 | 61.3815 | -0.13275 | 121.431 | -0.064087 | 61.3815 | 121.3074 | 121.5408 | -121.6919 | -121.756
218.25 | 121.8201 | -61.1847 | 60.3973 | -0.11406 | 0.015609 | 0.0028305 | 0.0014356 | 0.054386 | -0.0086132 | 0.066902 | -61.2122 | 60.1913 | -61.2305 | -61.235 | 60.2325 | 0.3479 | 0.036621 | 0.31128 | 60.2875 | -61.3266 | -0.045777 | -0.20599 | -0.027466 | -0.050354 | -0.1648 | -0.14191 | -0.10986 | 0.018311 | 61.2213 | 61.496 | 121.4172 | 121.376 | -0.027466 | 121.4722 | 61.5326 | -0.14191 | 121.376 | -0.027466 | 61.5326 | 121.4172 | 121.4722 | -121.6278 | -121.7239
219.9844 | 121.8933 | -61.2213 | 60.3699 | 0.13771 | 0.01625 | 0.0058211 | 0.0059216 | 0.055241 | -0.008827 | 0.066475 | -61.3129 | 60.0769 | -61.3312 | -61.3266 | 60.0998 | 0.13733 | -0.23804 | 0.054932 | 60.2509 | -61.3953 | -0.10986 | -0.29297 | -0.091553 | -0.10529 | -0.27008 | -0.17395 | -0.11902 | 0.018311 | 60.9833 | 61.2762 | 121.3211 | 121.2982 | -0.091553 | 121.4722 | 61.3586 | -0.17395 | 121.2982 | -0.091553 | 61.3586 | 121.3211 | 121.4722 | -121.701 | -121.7651
221.7344 | 121.8979 | -61.1984 | 60.4202 | -0.075912 | 0.014114 | 0.0064621 | 0.0044262 | 0.053105 | -0.0077588 | 0.067116 | -61.2717 | 60.1822 | -61.2442 | -61.2762 | 60.173 | 0.29297 | 0.036621 | 0.27008 | 60.2829 | -61.3312 | -0.045777 | -0.23804 | -0.073242 | -0.07782 | -0.24719 | -0.13275 | -0.13733 | -0.027465 | 61.235 | 61.4685 | 121.3715 | 121.3806 | -0.073242 | 121.4813 | 61.4914 | -0.13275 | 121.3806 | -0.073242 | 61.4914 | 121.3715 | 121.4813 | -121.6644 | -121.7514
223.4844 | 121.7834 | -61.3266 | 60.3104 | -0.060654 | 0.017105 | 0.0036849 | 0.011476 | 0.053105 | -0.010109 | 0.066689 | -61.3358 | 60.1456 | -61.3495 | -61.3358 | 60.0677 | 0.19684 | 0 | 0.064087 | 60.2325 | -61.3861 | -0.022888 | -0.16479 | -0.009155 | -0.009155 | -0.24262 | -0.059509 | -0.07782 | 0.013733 | 61.3266 | 61.3907 | 121.3943 | 121.4722 | -0.009155 | 121.5591 | 61.5234 | -0.059509 | 121.4722 | -0.009155 | 61.5234 | 121.3943 | 121.5591 | -121.6599 | -121.6965
225.2188 | 121.9345 | -61.2854 | 60.2737 | 0.1606 | 0.015396 | 0.0013351 | 0.0099804 | 0.054814 | -0.011604 | 0.068611 | -61.441 | 60.1044 | -61.3953 | -61.4639 | 59.9762 | -0.013733 | -0.13275 | -0.16479 | 60.228 | -61.4182 | -0.10986 | -0.16937 | -0.15564 | -0.17853 | -0.29755 | -0.13275 | -0.045777 | -0.045776 | 61.1526 | 61.1206 | 121.2616 | 121.3898 | -0.15564 | 121.5134 | 61.2717 | -0.13275 | 121.3898 | -0.15564 | 61.2717 | 121.2616 | 121.5134 | -121.669 | -121.6919
226.9062 | 121.9299 | -61.2625 | 60.2783 | 0.15297 | 0.015609 | 0.0062485 | 0.0089124 | 0.055882 | -0.008827 | 0.068825 | -61.4182 | 60.1227 | -61.3678 | -61.4685 | 59.9716 | 0 | -0.13275 | -0.17853 | 60.26 | -61.4182 | -0.10529 | -0.15564 | -0.15564 | -0.20599 | -0.3067 | -0.15564 | -0.01831 | -0.050354 | 61.1298 | 61.084 | 121.2341 | 121.3852 | -0.15564 | 121.5225 | 61.2625 | -0.15564 | 121.3852 | -0.15564 | 61.2625 | 121.2341 | 121.5225 | -121.6461 | -121.6965
228.6406 | 121.7926 | -61.2991 | 60.3424 | -0.13695 | 0.015182 | 0.0026169 | 0.009126 | 0.055668 | -0.010963 | 0.067757 | -61.3129 | 60.1776 | -61.322 | -61.3449 | 60.0861 | 0.20142 | 0.054932 | 0.091553 | 60.3195 | -61.3495 | -0.022888 | -0.16479 | -0.013733 | -0.045777 | -0.25635 | -0.050354 | -0.022888 | 0.009155 | 61.3541 | 61.3907 | 121.3852 | 121.4767 | -0.013733 | 121.6187 | 61.5005 | -0.050354 | 121.4767 | -0.013733 | 61.5005 | 121.3852 | 121.6187 | -121.6644 | -121.6919
230.3125 | 121.8521 | -61.2579 | 60.3287 | -0.20561 | 0.014969 | 0.0047531 | 0.0044262 | 0.054386 | -0.0090406 | 0.066689 | -61.3266 | 60.2509 | -61.2808 | -61.3632 | 60.0723 | 0.22888 | 0.21515 | 0.13275 | 60.3333 | -61.3861 | -0.022888 | -0.07782 | -0.068664 | -0.10528 | -0.25635 | -0.12817 | 0.004578 | -0.045776 | 61.4731 | 61.3907 | 121.3303 | 121.5088 | -0.068664 | 121.5912 | 61.4868 | -0.12817 | 121.5088 | -0.068664 | 61.4868 | 121.3303 | 121.5912 | -121.6095 | -121.7148
232.0625 | 121.8887 | -61.203 | 60.4111 | -0.15984 | 0.016891 | 0.0024033 | 0.00015382 | 0.052677 | -0.0083996 | 0.067543 | -61.2122 | 60.2188 | -61.2305 | -61.2488 | 60.2005 | 0.3067 | 0.027466 | 0.28839 | 60.3058 | -61.3129 | -0.027466 | -0.19226 | -0.009155 | -0.045776 | -0.21057 | -0.10986 | -0.10529 | 0.018311 | 61.2305 | 61.4914 | 121.4035 | 121.4218 | -0.009155 | 121.5088 | 61.5097 | -0.10986 | 121.4218 | -0.009155 | 61.5097 | 121.4035 | 121.5088 | -121.6415 | -121.7239
233.7969 | 121.9208 | -61.1847 | 60.3836 | -0.030136 | 0.014114 | -0.00058746 | 0.0033582 | 0.053746 | -0.0058362 | 0.063912 | -61.2946 | 60.2005 | -61.2671 | -61.322 | 60.1181 | 0.21973 | 0 | 0.17395 | 60.2829 | -61.3724 | -0.082398 | -0.18311 | -0.10986 | -0.13733 | -0.2655 | -0.18768 | -0.10071 | -0.027466 | 61.1847 | 61.3586 | 121.3028 | 121.3852 | -0.10986 | 121.4676 | 61.4044 | -0.18768 | 121.3852 | -0.10986 | 61.4044 | 121.3028 | 121.4676 | -121.6507 | -121.756
235.4688 | 121.8887 | -61.2259 | 60.347 | 0.12245 | 0.015182 | 0.0036849 | 0.0099804 | 0.052677 | -0.011177 | 0.066262 | -61.3037 | 60.0906 | -61.3174 | -61.3403 | 60.0906 | 0.10986 | -0.29297 | -0.009155 | 60.1959 | -61.4319 | -0.091553 | -0.25635 | -0.07782 | -0.11444 | -0.25635 | -0.20599 | -0.15106 | 0.013733 | 60.9329 | 61.2167 | 121.3165 | 121.3165 | -0.07782 | 121.4218 | 61.3358 | -0.20599 | 121.3165 | -0.07782 | 61.3358 | 121.3165 | 121.4218 | -121.6644 | -121.7789
237.2188 | 121.8567 | -61.2534 | 60.3149 | -0.2285 | 0.015823 | 0.0043259 | 0.0080578 | 0.054386 | -0.010109 | 0.069252 | -61.3358 | 60.228 | -61.2946 | -61.3403 | 60.0769 | 0.23804 | 0.24261 | 0.16937 | 60.3561 | -61.3724 | -0.041199 | -0.086975 | -0.082397 | -0.086975 | -0.23804 | -0.11902 | 0.041199 | -0.041198 | 61.496 | 61.4227 | 121.3303 | 121.4813 | -0.082397 | 121.6095 | 61.4914 | -0.11902 | 121.4813 | -0.082397 | 61.4914 | 121.3303 | 121.6095 | -121.6095 | -121.6873
238.8906 | 121.8842 | -61.2396 | 60.3333 | 0.1606 | 0.013473 | 0.0049667 | 0.007417 | 0.055455 | -0.010963 | 0.06797 | -61.3632 | 60.0861 | -61.3495 | -61.3632 | 60.054 | 0.086975 | -0.27924 | -0.045776 | 60.2325 | -61.4044 | -0.10986 | -0.24719 | -0.1236 | -0.1236 | -0.27924 | -0.16479 | -0.10071 | -0.013733 | 60.9604 | 61.1938 | 121.2936 | 121.3257 | -0.1236 | 121.4722 | 61.3266 | -0.16479 | 121.3257 | -0.1236 | 61.3266 | 121.2936 | 121.4722 | -121.6827 | -121.7377
240.6406 | 121.8658 | -61.1984 | 60.4019 | -0.10643 | 0.015182 | 0.0038985 | 0.0031446 | 0.052037 | -0.0066906 | 0.067116 | -61.235 | 60.1593 | -61.2122 | -61.2396 | 60.2142 | 0.31128 | 0.041199 | 0.29297 | 60.3058 | -61.3129 | -0.013733 | -0.24262 | -0.036621 | -0.041199 | -0.18768 | -0.11444 | -0.096131 | -0.022888 | 61.2396 | 61.4914 | 121.4127 | 121.3577 | -0.036621 | 121.5042 | 61.5097 | -0.11444 | 121.3577 | -0.036621 | 61.5097 | 121.4127 | 121.5042 | -121.6141 | -121.7148
242.375 | 121.9254 | -61.1755 | 60.3699 | -0.022507 | 0.015396 | 0.0064621 | 0.0025036 | 0.053318 | -0.008186 | 0.066689 | -61.2991 | 60.173 | -61.2625 | -61.3129 | 60.1318 | 0.23804 | 0.013733 | 0.19226 | 60.2692 | -61.3815 | -0.086975 | -0.19684 | -0.1236 | -0.13733 | -0.23804 | -0.20599 | -0.10071 | -0.036621 | 61.1893 | 61.3678 | 121.3074 | 121.3486 | -0.1236 | 121.4447 | 61.4136 | -0.20599 | 121.3486 | -0.1236 | 61.4136 | 121.3074 | 121.4447 | -121.6324 | -121.7514
244.1094 | 121.9208 | -61.1801 | 60.379 | -0.053024 | 0.014969 | 0.0011215 | 0.003999 | 0.052891 | -0.0079724 | 0.066048 | -61.2808 | 60.1776 | -61.2854 | -61.29 | 60.1456 | 0.23804 | 0.022888 | 0.20599 | 60.2966 | -61.3449 | -0.10529 | -0.20142 | -0.10071 | -0.10986 | -0.23346 | -0.16479 | -0.082397 | 0.004577 | 61.203 | 61.3861 | 121.3257 | 121.3577 | -0.10071 | 121.4767 | 61.4182 | -0.16479 | 121.3577 | -0.10071 | 61.4182 | 121.3257 | 121.4767 | -121.6644 | -121.7239
245.7969 | 121.9391 | -61.2488 | 60.2875 | 0.099564 | 0.013687 | 0.0036849 | 0.010408 | 0.053318 | -0.0094678 | 0.069039 | -61.4044 | 60.0952 | -61.3998 | -61.4365 | 59.9945 | 0 | -0.19684 | -0.13275 | 60.228 | -61.4456 | -0.15106 | -0.19226 | -0.15564 | -0.18768 | -0.29297 | -0.19684 | -0.05951 | -0.004578 | 61.0519 | 61.116 | 121.2433 | 121.344 | -0.15564 | 121.4767 | 61.2488 | -0.19684 | 121.344 | -0.15564 | 61.2488 | 121.2433 | 121.4767 | -121.6873 | -121.7331
247.5469 | 121.8063 | -61.203 | 60.4294 | -0.17509 | 0.014541 | 0.0041123 | 0.0065624 | 0.05225 | -0.0094678 | 0.06733 | -61.203 | 60.2554 | -61.1984 | -61.203 | 60.2188 | 0.35706 | 0.09613 | 0.35706 | 60.3104 | -61.3312 | 0.004578 | -0.17395 | 0 | 0 | -0.21057 | -0.12817 | -0.11902 | -0.004578 | 61.2991 | 61.5601 | 121.4218 | 121.4584 | 0 | 121.5134 | 61.5601 | -0.12817 | 121.4584 | 0 | 61.5601 | 121.4218 | 121.5134 | -121.6278 | -121.7606
249.2812 | 121.8292 | -61.2396 | 60.3882 | -0.2285 | 0.014541 | 0.0047531 | 0.0059216 | 0.052891 | -0.0075452 | 0.067116 | -61.2305 | 60.2234 | -61.2305 | -61.2488 | 60.1776 | 0.32959 | 0.19226 | 0.29297 | 60.3195 | -61.3541 | 0.009155 | -0.1648 | 0.009155 | -0.009155 | -0.21057 | -0.11444 | -0.068665 | 0 | 61.4319 | 61.5326 | 121.4172 | 121.463 | 0.009155 | 121.5591 | 61.5692 | -0.11444 | 121.463 | 0.009155 | 61.5692 | 121.4172 | 121.5591 | -121.6187 | -121.7422
250.9688 | 121.843 | -61.2671 | 60.3561 | -0.26665 | 0.015823 | 0.00069434 | 0.007417 | 0.054386 | -0.0079724 | 0.067757 | -61.235 | 60.228 | -61.2762 | -61.2762 | 60.1364 | 0.30212 | 0.22888 | 0.23804 | 60.3653 | -61.3586 | -0.009155 | -0.12817 | 0.032044 | -0.009155 | -0.21973 | -0.091553 | 0.009155 | 0.041199 | 61.496 | 61.5051 | 121.4035 | 121.4951 | 0.032044 | 121.6324 | 61.5692 | -0.091553 | 121.4951 | 0.032044 | 61.5692 | 121.4035 | 121.6324 | -121.6324 | -121.7148
252.7031 | 121.8979 | -61.235 | 60.3516 | 0.099564 | 0.012619 | 0.0049667 | 0.0093396 | 0.053959 | -0.0079724 | 0.06797 | -61.3129 | 60.1181 | -61.3403 | -61.322 | 60.1089 | 0.11444 | -0.23804 | 0.032043 | 60.2005 | -61.4136 | -0.10529 | -0.23346 | -0.07782 | -0.086975 | -0.24261 | -0.17853 | -0.15106 | 0.027466 | 60.997 | 61.2671 | 121.344 | 121.3531 | -0.07782 | 121.4355 | 61.3495 | -0.17853 | 121.3531 | -0.07782 | 61.3495 | 121.344 | 121.4355 | -121.6919 | -121.7651
254.375 | 121.9574 | -61.1526 | 60.379 | 0.00038159 | 0.014969 | 0.0049667 | 0.0044262 | 0.05225 | -0.0058362 | 0.066262 | -61.3037 | 60.1776 | -61.29 | -61.3312 | 60.0998 | 0.1831 | 0 | 0.12817 | 60.26 | -61.3632 | -0.13733 | -0.20142 | -0.15106 | -0.17853 | -0.27924 | -0.21057 | -0.11902 | -0.013733 | 61.1526 | 61.2808 | 121.2524 | 121.3303 | -0.15106 | 121.4127 | 61.3358 | -0.21057 | 121.3303 | -0.15106 | 61.3358 | 121.2524 | 121.4127 | -121.669 | -121.7422
256.125 | 121.907 | -61.2625 | 60.2692 | 0.069046 | 0.01326 | -0.0018693 | 0.010408 | 0.055455 | -0.0092542 | 0.067757 | -61.4456 | 60.1318 | -61.4044 | -61.4777 | 59.9487 | 0.009155 | -0.11444 | -0.15564 | 60.228 | -61.441 | -0.14191 | -0.13733 | -0.18311 | -0.21515 | -0.32044 | -0.17853 | -0.041199 | -0.041199 | 61.1481 | 61.1069 | 121.2112 | 121.3943 | -0.18311 | 121.4905 | 61.2717 | -0.17853 | 121.3943 | -0.18311 | 61.2717 | 121.2112 | 121.4905 | -121.6736 | -121.7102
257.7969 | 121.8292 | -61.2396 | 60.3882 | -0.24376 | 0.014755 | 0.00026694 | 0.0054944 | 0.052464 | -0.0094678 | 0.067757 | -61.2442 | 60.2188 | -61.2122 | -61.2717 | 60.1639 | 0.31586 | 0.19684 | 0.27924 | 60.3195 | -61.3632 | 0.027466 | -0.16937 | -0.004578 | -0.032043 | -0.22431 | -0.1236 | -0.068665 | -0.032044 | 61.4365 | 61.5189 | 121.4035 | 121.4584 | -0.004578 | 121.5591 | 61.5555 | -0.1236 | 121.4584 | -0.004578 | 61.5555 | 121.4035 | 121.5591 | -121.6003 | -121.7514
259.5312 | 121.962 | -61.171 | 60.3882 | -0.022507 | 0.013687 | -0.00016026 | 0.0046398 | 0.051396 | -0.0051954 | 0.06797 | -61.3266 | 60.1593 | -61.2808 | -61.3312 | 60.1181 | 0.1831 | -0.045776 | 0.091553 | 60.2509 | -61.3724 | -0.10986 | -0.22888 | -0.15564 | -0.16022 | -0.27008 | -0.20142 | -0.13733 | -0.045776 | 61.1252 | 61.2625 | 121.2891 | 121.3303 | -0.15564 | 121.4218 | 61.3541 | -0.20142 | 121.3303 | -0.15564 | 61.3541 | 121.2891 | 121.4218 | -121.669 | -121.7606
261.2812 | 121.907 | -61.2717 | 60.2692 | 0.069046 | 0.016464 | 0.0030441 | 0.011262 | 0.0546 | -0.0090406 | 0.069893 | -61.4365 | 60.1181 | -61.3815 | -61.441 | 59.9762 | 0.032043 | -0.082397 | -0.15564 | 60.2509 | -61.4365 | -0.10986 | -0.15106 | -0.16479 | -0.16937 | -0.29297 | -0.16479 | -0.018311 | -0.054931 | 61.1893 | 61.116 | 121.2479 | 121.3898 | -0.16479 | 121.5225 | 61.3037 | -0.16479 | 121.3898 | -0.16479 | 61.3037 | 121.2479 | 121.5225 | -121.6507 | -121.7056
262.9688 | 121.9437 | -61.1572 | 60.3836 | 0.0080111 | 0.015396 | 0.0019759 | 0.0037854 | 0.053105 | -0.0075452 | 0.065621 | -61.3083 | 60.1913 | -61.2534 | -61.3358 | 60.0998 | 0.17853 | -0.022888 | 0.11902 | 60.2371 | -61.3861 | -0.09613 | -0.19226 | -0.15106 | -0.17853 | -0.28381 | -0.22888 | -0.14648 | -0.054932 | 61.1343 | 61.2762 | 121.257 | 121.3486 | -0.15106 | 121.3943 | 61.3358 | -0.22888 | 121.3486 | -0.15106 | 61.3358 | 121.257 | 121.3943 | -121.637 | -121.7697
264.7188 | 121.9299 | -61.171 | 60.3836 | 0.076676 | 0.016037 | 0.0019759 | 0.0031446 | 0.052464 | -0.0056226 | 0.065407 | -61.3083 | 60.1501 | -61.2808 | -61.3449 | 60.1089 | 0.15564 | -0.11444 | 0.07782 | 60.2188 | -61.3815 | -0.10986 | -0.23346 | -0.13733 | -0.17395 | -0.27466 | -0.21057 | -0.16479 | -0.027466 | 61.0565 | 61.2488 | 121.2799 | 121.3211 | -0.13733 | 121.3898 | 61.3266 | -0.21057 | 121.3211 | -0.13733 | 61.3266 | 121.2799 | 121.3898 | -121.6644 | -121.7651
266.4062 | 121.8979 | -61.2259 | 60.347 | 0.15297 | 0.014114 | 0.0068893 | 0.0086988 | 0.05225 | -0.010536 | 0.066048 | -61.3174 | 60.054 | -61.3358 | -61.3266 | 60.0952 | 0.11902 | -0.30212 | 0.013733 | 60.1959 | -61.4182 | -0.10986 | -0.29297 | -0.091553 | -0.10071 | -0.25177 | -0.19226 | -0.15106 | 0.01831 | 60.9238 | 61.2396 | 121.3211 | 121.2799 | -0.091553 | 121.4218 | 61.3449 | -0.19226 | 121.2799 | -0.091553 | 61.3449 | 121.3211 | 121.4218 | -121.6827 | -121.7651
268.1562 | 121.843 | -61.2259 | 60.3973 | -0.21324 | 0.014328 | 0.0043259 | 0.0065624 | 0.053318 | -0.0096814 | 0.066902 | -61.2488 | 60.1959 | -61.2488 | -61.2488 | 60.173 | 0.34332 | 0.17853 | 0.30212 | 60.3424 | -61.3358 | -0.022888 | -0.20142 | -0.022888 | -0.022888 | -0.2243 | -0.10986 | -0.054932 | 0 | 61.4044 | 61.528 | 121.3989 | 121.4218 | -0.022888 | 121.5683 | 61.5692 | -0.10986 | 121.4218 | -0.022888 | 61.5692 | 121.3989 | 121.5683 | -121.6461 | -121.7331
269.9062 | 121.8246 | -61.2122 | 60.3836 | -0.17509 | 0.012405 | 0.0013351 | 0.0065624 | 0.052464 | -0.009895 | 0.065834 | -61.2305 | 60.1685 | -61.2579 | -61.235 | 60.1959 | 0.35248 | 0.16022 | 0.31586 | 60.3195 | -61.3312 | -0.045777 | -0.21515 | -0.018311 | -0.022888 | -0.18768 | -0.11902 | -0.064087 | 0.027466 | 61.3724 | 61.528 | 121.4081 | 121.3806 | -0.018311 | 121.5317 | 61.5646 | -0.11902 | 121.3806 | -0.018311 | 61.5646 | 121.4081 | 121.5317 | -121.6415 | -121.7148
271.5938 | 121.9254 | -61.2717 | 60.2921 | 0.099564 | 0.017318 | 0.0024033 | 0.009126 | 0.055241 | -0.010536 | 0.06797 | -61.409 | 60.1364 | -61.377 | -61.4365 | 59.9899 | 0.027466 | -0.16937 | -0.13733 | 60.228 | -61.4456 | -0.10529 | -0.15564 | -0.13733 | -0.16479 | -0.30212 | -0.17395 | -0.064087 | -0.032044 | 61.1023 | 61.1343 | 121.2616 | 121.4081 | -0.13733 | 121.4996 | 61.2991 | -0.17395 | 121.4081 | -0.13733 | 61.2991 | 121.2616 | 121.4996 | -121.669 | -121.7377
273.3281 | 121.8475 | -61.2625 | 60.3149 | -0.24376 | 0.01326 | 0.0047531 | 0.005708 | 0.054173 | -0.009895 | 0.06733 | -61.3129 | 60.2142 | -61.2717 | -61.3358 | 60.0861 | 0.23804 | 0.25635 | 0.15564 | 60.3607 | -61.3403 | -0.009155 | -0.10071 | -0.050354 | -0.073242 | -0.22888 | -0.07782 | 0.045777 | -0.041199 | 61.5189 | 61.4182 | 121.3486 | 121.4767 | -0.050354 | 121.6232 | 61.5005 | -0.07782 | 121.4767 | -0.050354 | 61.5005 | 121.3486 | 121.6232 | -121.5866 | -121.6553
275.0781 | 121.8796 | -61.2305 | 60.3241 | 0.02327 | 0.014328 | 0.0043259 | 0.007417 | 0.055882 | -0.0090406 | 0.067543 | -61.3266 | 60.0815 | -61.3358 | -61.3266 | 60.0769 | 0.11902 | -0.28381 | -0.022888 | 60.2097 | -61.4182 | -0.10529 | -0.24262 | -0.09613 | -0.09613 | -0.24719 | -0.18768 | -0.11444 | 0.009155 | 60.9467 | 61.2076 | 121.3074 | 121.312 | -0.09613 | 121.4401 | 61.3495 | -0.18768 | 121.312 | -0.09613 | 61.3495 | 121.3074 | 121.4401 | -121.6599 | -121.7422
276.8125 | 121.8384 | -61.2534 | 60.347 | -0.28191 | 0.016891 | 0.0015487 | 0.007417 | 0.052891 | -0.0096814 | 0.065834 | -61.3129 | 60.2463 | -61.2625 | -61.3403 | 60.1044 | 0.25177 | 0.2655 | 0.19226 | 60.3378 | -61.3541 | -0.009155 | -0.10071 | -0.059509 | -0.086975 | -0.24261 | -0.10071 | -0.009155 | -0.050354 | 61.5189 | 61.4456 | 121.3577 | 121.4996 | -0.059509 | 121.5912 | 61.5051 | -0.10071 | 121.4996 | -0.059509 | 61.5051 | 121.3577 | 121.5912 | -121.6095 | -121.701
278.5625 | 121.8155 | -61.2213 | 60.4111 | -0.17509 | 0.0139 | 0.00069434 | 0.0048534 | 0.053746 | -0.0092542 | 0.06797 | -61.2305 | 60.2142 | -61.2625 | -61.2579 | 60.1913 | 0.34332 | 0.15106 | 0.3067 | 60.3058 | -61.3312 | -0.041199 | -0.19684 | -0.009156 | -0.036622 | -0.21973 | -0.10986 | -0.10529 | 0.032043 | 61.3724 | 61.528 | 121.4127 | 121.4355 | -0.009156 | 121.5271 | 61.5646 | -0.10986 | 121.4355 | -0.009156 | 61.5646 | 121.4127 | 121.5271 | -121.6736 | -121.7422
280.2969 | 121.8338 | -61.2396 | 60.379 | -0.23613 | 0.015396 | 0.0021895 | 0.007417 | 0.053318 | -0.0077588 | 0.066689 | -61.2396 | 60.2097 | -61.2579 | -61.2717 | 60.1501 | 0.31128 | 0.20599 | 0.27466 | 60.3516 | -61.3358 | -0.018311 | -0.16937 | 0 | -0.032043 | -0.22888 | -0.09613 | -0.027466 | 0.018311 | 61.4456 | 61.5143 | 121.3898 | 121.4493 | 0 | 121.5912 | 61.5509 | -0.09613 | 121.4493 | 0 | 61.5509 | 121.3898 | 121.5912 | -121.637 | -121.7148
282.0469 | 121.8384 | -61.2579 | 60.3241 | -0.23613 | 0.016037 | 0.0051803 | 0.0089124 | 0.052891 | -0.0094678 | 0.067757 | -61.322 | 60.2463 | -61.3129 | -61.3632 | 60.0906 | 0.23346 | 0.22888 | 0.16022 | 60.3561 | -61.3632 | -0.054931 | -0.07782 | -0.064086 | -0.10528 | -0.23346 | -0.10528 | 0.032043 | -0.009155 | 61.4868 | 61.4182 | 121.3486 | 121.5042 | -0.064086 | 121.6141 | 61.4914 | -0.10528 | 121.5042 | -0.064086 | 61.4914 | 121.3486 | 121.6141 | -121.637 | -121.6873
283.7344 | 121.9208 | -61.2625 | 60.3058 | 0.16823 | 0.016464 | 0.00026694 | 0.0093396 | 0.053959 | -0.0094678 | 0.068398 | -61.3861 | 60.1318 | -61.3632 | -61.4182 | 60.0174 | 0.050354 | -0.23804 | -0.10071 | 60.2371 | -61.4319 | -0.10071 | -0.17395 | -0.1236 | -0.15564 | -0.28839 | -0.16937 | -0.068664 | -0.022888 | 61.0245 | 61.1618 | 121.2799 | 121.3943 | -0.1236 | 121.4996 | 61.3129 | -0.16937 | 121.3943 | -0.1236 | 61.3129 | 121.2799 | 121.4996 | -121.669 | -121.7377
285.4844 | 121.875 | -61.2488 | 60.3378 | 0.084305 | 0.013473 | 0.0041123 | 0.0063488 | 0.057163 | -0.0094678 | 0.067116 | -61.3174 | 60.1135 | -61.3358 | -61.3449 | 60.0815 | 0.11902 | -0.28839 | -0.022888 | 60.1913 | -61.3907 | -0.086975 | -0.2243 | -0.068665 | -0.096131 | -0.25635 | -0.14191 | -0.14648 | 0.01831 | 60.9604 | 61.2259 | 121.3303 | 121.3623 | -0.068665 | 121.4401 | 61.3678 | -0.14191 | 121.3623 | -0.068665 | 61.3678 | 121.3303 | 121.4401 | -121.6736 | -121.7285
287.1719 | 121.9437 | -61.2579 | 60.2646 | 0.069046 | 0.015182 | 0.0036849 | 0.0080578 | 0.056095 | -0.01075 | 0.067543 | -61.4044 | 60.1364 | -61.377 | -61.4548 | 59.9991 | 0.022888 | -0.13733 | -0.13733 | 60.2737 | -61.4227 | -0.11902 | -0.12817 | -0.14648 | -0.19684 | -0.2655 | -0.16479 | 0.009156 | -0.027466 | 61.1206 | 61.1206 | 121.257 | 121.3943 | -0.14648 | 121.5317 | 61.2808 | -0.16479 | 121.3943 | -0.14648 | 61.2808 | 121.257 | 121.5317 | -121.6415 | -121.6873
288.9219 | 121.9482 | -61.1938 | 60.3836 | 0.076676 | 0.012619 | 0.0028305 | 0.0052808 | 0.052464 | -0.0058362 | 0.064766 | -61.3129 | 60.1318 | -61.2671 | -61.3449 | 60.1135 | 0.14648 | -0.10986 | 0.073242 | 60.2463 | -61.3953 | -0.073242 | -0.25177 | -0.11902 | -0.15106 | -0.27008 | -0.20142 | -0.13733 | -0.045776 | 61.084 | 61.2671 | 121.3074 | 121.3257 | -0.11902 | 121.4401 | 61.3403 | -0.20142 | 121.3257 | -0.11902 | 61.3403 | 121.3074 | 121.4401 | -121.6507 | -121.7789
290.6719 | 121.8155 | -61.2305 | 60.4202 | -0.19035 | 0.014755 | 0.00026694 | 0.0033582 | 0.051182 | -0.0077588 | 0.06733 | -61.2076 | 60.2005 | -61.2213 | -61.2167 | 60.2188 | 0.36621 | 0.091553 | 0.33875 | 60.2921 | -61.3358 | 0.009156 | -0.21973 | 0.022888 | 0.013733 | -0.20142 | -0.10529 | -0.12817 | 0.013732 | 61.322 | 61.5692 | 121.4493 | 121.431 | 0.022888 | 121.5225 | 61.5967 | -0.10529 | 121.431 | 0.022888 | 61.5967 | 121.4493 | 121.5225 | -121.6415 | -121.756
292.3594 | 121.9162 | -61.171 | 60.4019 | -0.060654 | 0.015823 | -0.0022965 | 0.00229 | 0.052677 | -0.006477 | 0.066902 | -61.2717 | 60.1913 | -61.2534 | -61.2671 | 60.1776 | 0.29297 | 0.032043 | 0.2655 | 60.2875 | -61.3312 | -0.082398 | -0.21057 | -0.10071 | -0.096131 | -0.2243 | -0.16022 | -0.11444 | -0.01831 | 61.203 | 61.4365 | 121.3486 | 121.3623 | -0.10071 | 121.4584 | 61.4639 | -0.16022 | 121.3623 | -0.10071 | 61.4639 | 121.3486 | 121.4584 | -121.6553 | -121.7331
294.1094 | 121.8704 | -61.2717 | 60.3516 | -0.12932 | 0.013687 | 0.00090794 | 0.008485 | 0.049687 | -0.0086132 | 0.067543 | -61.322 | 60.2188 | -61.2854 | -61.3358 | 60.0952 | 0.26093 | 0.25177 | 0.20142 | 60.347 | -61.3724 | -0.013733 | -0.13275 | -0.050354 | -0.064087 | -0.25635 | -0.10071 | -0.004577 | -0.036621 | 61.5234 | 61.4731 | 121.3669 | 121.4905 | -0.050354 | 121.6187 | 61.5326 | -0.10071 | 121.4905 | -0.050354 | 61.5326 | 121.3669 | 121.6187 | -121.637 | -121.7239
295.7969 | 121.9574 | -61.1755 | 60.3653 | 0.038529 | 0.014541 | 0.0056075 | 0.0048534 | 0.052891 | -0.0075452 | 0.065407 | -61.3083 | 60.1593 | -61.29 | -61.3449 | 60.1044 | 0.18768 | -0.045776 | 0.10986 | 60.2463 | -61.3586 | -0.11444 | -0.20599 | -0.13275 | -0.16937 | -0.26093 | -0.18311 | -0.11902 | -0.018311 | 61.1298 | 61.2854 | 121.2799 | 121.3348 | -0.13275 | 121.4218 | 61.3632 | -0.18311 | 121.3348 | -0.13275 | 61.3632 | 121.2799 | 121.4218 | -121.6553 | -121.7239
297.5312 | 121.9025 | -61.235 | 60.3378 | 0.099564 | 0.016037 | 0.0017623 | 0.011476 | 0.053318 | -0.0096814 | 0.068611 | -61.3129 | 60.1227 | -61.3403 | -61.3403 | 60.0906 | 0.10986 | -0.28839 | -0.004578 | 60.1913 | -61.4319 | -0.10529 | -0.21515 | -0.07782 | -0.10529 | -0.24719 | -0.19684 | -0.14648 | 0.027466 | 60.9467 | 61.2305 | 121.3257 | 121.3577 | -0.07782 | 121.4264 | 61.3449 | -0.19684 | 121.3577 | -0.07782 | 61.3449 | 121.3257 | 121.4264 | -121.6782 | -121.7697
299.2812 | 121.8338 | -61.2854 | 60.3973 | -0.25902 | 0.013687 | 0.0017623 | 0.0069898 | 0.051609 | -0.0083996 | 0.068611 | -61.2488 | 60.2234 | -61.2717 | -61.2808 | 60.1456 | 0.31586 | 0.21515 | 0.2655 | 60.3424 | -61.3495 | 0.013733 | -0.17395 | 0.036621 | 0.004577 | -0.25177 | -0.064087 | -0.054932 | 0.022888 | 61.5005 | 61.5509 | 121.431 | 121.5088 | 0.036621 | 121.6278 | 61.6013 | -0.064087 | 121.5088 | 0.036621 | 61.6013 | 121.431 | 121.6278 | -121.669 | -121.7468
300.9688 | 121.9299 | -61.1618 | 60.379 | 0.01564 | 0.014328 | 0.00090794 | 0.0054944 | 0.052464 | -0.0075452 | 0.066262 | -61.3129 | 60.2005 | -61.2854 | -61.3358 | 60.1318 | 0.19226 | -0.009155 | 0.12817 | 60.2921 | -61.3541 | -0.1236 | -0.17853 | -0.15106 | -0.17395 | -0.24719 | -0.19226 | -0.086975 | -0.027466 | 61.1526 | 61.29 | 121.2936 | 121.3623 | -0.15106 | 121.4539 | 61.3541 | -0.19226 | 121.3623 | -0.15106 | 61.3541 | 121.2936 | 121.4539 | -121.6644 | -121.7331
302.7188 | 121.8201 | -61.2946 | 60.3287 | -0.075912 | 0.014114 | 0.0021895 | 0.011689 | 0.053318 | -0.011604 | 0.067116 | -61.3083 | 60.1547 | -61.3541 | -61.3541 | 60.0586 | 0.15106 | -0.032043 | 0.018311 | 60.2966 | -61.4044 | -0.059509 | -0.17395 | -0.013733 | -0.059509 | -0.27008 | -0.10986 | -0.032043 | 0.045776 | 61.2625 | 61.3129 | 121.3531 | 121.4493 | -0.013733 | 121.5912 | 61.4456 | -0.10986 | 121.4493 | -0.013733 | 61.4456 | 121.3531 | 121.5912 | -121.6827 | -121.7331
304.4531 | 121.9162 | -61.235 | 60.3333 | 0.19875 | 0.014755 | -0.00080106 | 0.0093396 | 0.052464 | -0.010536 | 0.06733 | -61.3953 | 60.1227 | -61.3953 | -61.3815 | 60.0311 | 0.050354 | -0.24719 | -0.07782 | 60.2142 | -61.4182 | -0.16022 | -0.21057 | -0.16022 | -0.14649 | -0.30212 | -0.18311 | -0.11902 | 0 | 60.9879 | 61.1572 | 121.2662 | 121.3577 | -0.16022 | 121.4493 | 61.2854 | -0.18311 | 121.3577 | -0.16022 | 61.2854 | 121.2662 | 121.4493 | -121.7285 | -121.7514
306.2031 | 121.9208 | -61.2808 | 60.3149 | 0.061417 | 0.015396 | 0.0056075 | 0.011049 | 0.057163 | -0.0096814 | 0.06797 | -61.4273 | 60.1501 | -61.3907 | -61.4639 | 59.9442 | 0 | -0.064087 | -0.15106 | 60.2371 | -61.4502 | -0.10986 | -0.16479 | -0.14648 | -0.18311 | -0.37079 | -0.16937 | -0.077819 | -0.036621 | 61.2167 | 61.1298 | 121.225 | 121.431 | -0.14648 | 121.5179 | 61.2808 | -0.16937 | 121.431 | -0.14648 | 61.2808 | 121.225 | 121.5179 | -121.7056 | -121.7651
307.9375 | 121.8613 | -61.2579 | 60.3378 | -0.25139 | 0.012832 | 0.0015487 | 0.0065624 | 0.050968 | -0.0073316 | 0.067116 | -61.322 | 60.2325 | -61.2946 | -61.3495 | 60.0906 | 0.24719 | 0.27466 | 0.16937 | 60.3424 | -61.3724 | -0.036621 | -0.10529 | -0.064086 | -0.091552 | -0.24719 | -0.11444 | 0.004577 | -0.027465 | 61.5326 | 61.4273 | 121.3486 | 121.4905 | -0.064086 | 121.6003 | 61.5051 | -0.11444 | 121.4905 | -0.064086 | 61.5051 | 121.3486 | 121.6003 | -121.6324 | -121.7102
309.625 | 121.8109 | -61.3129 | 60.2875 | -0.083542 | 0.014541 | 0.0053939 | 0.0095532 | 0.056523 | -0.010536 | 0.068825 | -61.322 | 60.1547 | -61.3312 | -61.3632 | 60.0769 | 0.19226 | -0.009155 | 0.073242 | 60.2737 | -61.3953 | -0.018311 | -0.13275 | -0.009155 | -0.050354 | -0.21057 | -0.082398 | -0.013733 | 0.009156 | 61.3037 | 61.3861 | 121.3898 | 121.4676 | -0.009155 | 121.5866 | 61.5051 | -0.082398 | 121.4676 | -0.009155 | 61.5051 | 121.3898 | 121.5866 | -121.6187 | -121.6827
311.3594 | 121.8201 | -61.2534 | 60.379 | -0.17509 | 0.017532 | 0.0034713 | 0.0029308 | 0.053746 | -0.010109 | 0.065193 | -61.2534 | 60.1822 | -61.2122 | -61.2488 | 60.2051 | 0.34332 | 0.16022 | 0.32044 | 60.3378 | -61.3403 | 0.041199 | -0.19684 | 0 | 0.004578 | -0.17395 | -0.086975 | -0.041198 | -0.041199 | 61.4136 | 61.5738 | 121.4584 | 121.4355 | 0 | 121.5912 | 61.5967 | -0.086975 | 121.4355 | 0 | 61.5967 | 121.4584 | 121.5912 | -121.5912 | -121.7194
313.1094 | 121.9437 | -61.1801 | 60.379 | 0.053787 | 0.014969 | 0.0038985 | 0.0031446 | 0.051823 | -0.0079724 | 0.068184 | -61.3083 | 60.1547 | -61.2762 | -61.3541 | 60.0952 | 0.15106 | -0.1236 | 0.07782 | 60.2325 | -61.3907 | -0.09613 | -0.2243 | -0.12817 | -0.17395 | -0.28381 | -0.21057 | -0.14648 | -0.032044 | 61.0565 | 61.2579 | 121.2753 | 121.3348 | -0.12817 | 121.4127 | 61.3312 | -0.21057 | 121.3348 | -0.12817 | 61.3312 | 121.2753 | 121.4127 | -121.6553 | -121.7697
314.7812 | 121.8201 | -61.2991 | 60.3195 | -0.045395 | 0.016891 | 0.0021895 | 0.012758 | 0.0546 | -0.01139 | 0.066689 | -61.3312 | 60.141 | -61.3586 | -61.4044 | 60.0403 | 0.11444 | -0.059509 | -0.041199 | 60.26 | -61.4227 | -0.05951 | -0.17853 | -0.032044 | -0.10529 | -0.27924 | -0.1236 | -0.059509 | 0.027466 | 61.2396 | 61.2579 | 121.3394 | 121.4401 | -0.032044 | 121.5591 | 61.4136 | -0.1236 | 121.4401 | -0.032044 | 61.4136 | 121.3394 | 121.5591 | -121.6782 | -121.7422
316.5312 | 121.9666 | -61.1755 | 60.3882 | 0.0080111 | 0.014328 | 0.0064621 | 0.0037854 | 0.052037 | -0.008186 | 0.068611 | -61.322 | 60.1913 | -61.2717 | -61.3586 | 60.1089 | 0.17853 | -0.022888 | 0.11902 | 60.2692 | -61.3861 | -0.09613 | -0.19684 | -0.14648 | -0.18311 | -0.27924 | -0.21057 | -0.11902 | -0.050354 | 61.1526 | 61.2946 | 121.2845 | 121.3669 | -0.14648 | 121.4447 | 61.3541 | -0.21057 | 121.3669 | -0.14648 | 61.3541 | 121.2845 | 121.4447 | -121.6599 | -121.7743
318.2969 | 121.9391 | -61.2534 | 60.2783 | 0.10719 | 0.016464 | 0.0021895 | 0.0089124 | 0.053746 | -0.0086132 | 0.068184 | -61.4044 | 60.141 | -61.3724 | -61.4502 | 59.9899 | 0.004578 | -0.14648 | -0.14191 | 60.2509 | -61.4365 | -0.11902 | -0.13733 | -0.15106 | -0.19684 | -0.28839 | -0.1831 | -0.027466 | -0.032044 | 61.1069 | 61.1114 | 121.2433 | 121.3943 | -0.15106 | 121.5042 | 61.2579 | -0.1831 | 121.3943 | -0.15106 | 61.2579 | 121.2433 | 121.5042 | -121.6507 | -121.7148
319.9844 | 121.8292 | -61.2122 | 60.4111 | -0.12169 | 0.015396 | 0.0047531 | 0.0042126 | 0.052464 | -0.0083996 | 0.069039 | -61.2259 | 60.1776 | -61.2625 | -61.2396 | 60.2142 | 0.3479 | 0.032043 | 0.33417 | 60.2966 | -61.3403 | -0.050354 | -0.23346 | -0.013733 | -0.027466 | -0.19684 | -0.12817 | -0.11444 | 0.036621 | 61.2442 | 61.5463 | 121.4264 | 121.3898 | -0.013733 | 121.5088 | 61.5601 | -0.12817 | 121.3898 | -0.013733 | 61.5601 | 121.4264 | 121.5088 | -121.6736 | -121.7514
321.7344 | 121.9025 | -61.1847 | 60.4065 | -0.060654 | 0.013687 | -0.0016557 | 0.0052808 | 0.053532 | -0.0075452 | 0.06733 | -61.2762 | 60.1959 | -61.2442 | -61.2854 | 60.1685 | 0.28839 | 0.009155 | 0.25177 | 60.3104 | -61.322 | -0.05951 | -0.21057 | -0.091553 | -0.10071 | -0.23804 | -0.13733 | -0.09613 | -0.032043 | 61.1938 | 61.4365 | 121.3531 | 121.3806 | -0.091553 | 121.4951 | 61.4731 | -0.13733 | 121.3806 | -0.091553 | 61.4731 | 121.3531 | 121.4951 | -121.6507 | -121.7285
323.5 | 121.9162 | -61.1847 | 60.3699 | 0.13008 | 0.015823 | 0.0036849 | 0.008485 | 0.053318 | -0.0077588 | 0.066048 | -61.3037 | 60.1456 | -61.3266 | -61.3266 | 60.1044 | 0.12817 | -0.16479 | 0.068665 | 60.2463 | -61.3998 | -0.14191 | -0.2243 | -0.11902 | -0.14191 | -0.2655 | -0.21515 | -0.1236 | 0.022888 | 61.0199 | 61.2534 | 121.2891 | 121.3303 | -0.11902 | 121.431 | 61.3129 | -0.21515 | 121.3303 | -0.11902 | 61.3129 | 121.2891 | 121.431 | -121.6965 | -121.7697
325.25 | 121.907 | -61.2762 | 60.2783 | 0.061417 | 0.01625 | 0.0015487 | 0.012971 | 0.055241 | -0.010109 | 0.066902 | -61.409 | 60.1181 | -61.4136 | -61.4456 | 59.9716 | 0.050354 | -0.050354 | -0.10071 | 60.2966 | -61.4319 | -0.13733 | -0.16022 | -0.13275 | -0.16937 | -0.3067 | -0.15564 | 0.018311 | 0.004577 | 61.2259 | 61.1755 | 121.2479 | 121.3943 | -0.13275 | 121.5729 | 61.3266 | -0.15564 | 121.3943 | -0.13275 | 61.3266 | 121.2479 | 121.5729 | -121.6919 | -121.7102
326.9375 | 121.8567 | -61.2442 | 60.3928 | -0.25139 | 0.016464 | -0.0027237 | 0.0061352 | 0.053105 | -0.0075452 | 0.066689 | -61.2488 | 60.2463 | -61.2625 | -61.29 | 60.1593 | 0.31586 | 0.19684 | 0.27466 | 60.3378 | -61.3449 | -0.01831 | -0.14648 | -0.004577 | -0.045776 | -0.23346 | -0.10071 | -0.054931 | 0.013733 | 61.441 | 61.5189 | 121.4035 | 121.4905 | -0.004577 | 121.582 | 61.5601 | -0.10071 | 121.4905 | -0.004577 | 61.5601 | 121.4035 | 121.582 | -121.6553 | -121.7377
328.6875 | 121.843 | -61.3083 | 60.3287 | -0.053024 | 0.015182 | 0.0062485 | 0.0099804 | 0.053746 | -0.009895 | 0.066689 | -61.3358 | 60.1501 | -61.3449 | -61.3953 | 60.0449 | 0.12817 | -0.054932 | -0.022888 | 60.2921 | -61.4136 | -0.036621 | -0.17853 | -0.027465 | -0.086975 | -0.28381 | -0.10528 | -0.036621 | 0.009156 | 61.2534 | 61.2854 | 121.3531 | 121.4584 | -0.027465 | 121.6003 | 61.4365 | -0.10528 | 121.4584 | -0.027465 | 61.4365 | 121.3531 | 121.6003 | -121.6736 | -121.7422
330.4375 | 121.9391 | -61.1847 | 60.4019 | 0.01564 | 0.014541 | 5.3338e-05 | 0.0027172 | 0.052677 | -0.0083996 | 0.067757 | -61.3129 | 60.1822 | -61.2442 | -61.3449 | 60.1227 | 0.20142 | 0 | 0.14648 | 60.3058 | -61.3586 | -0.05951 | -0.21973 | -0.12817 | -0.16022 | -0.27924 | -0.17395 | -0.096131 | -0.068664 | 61.1847 | 61.3312 | 121.3074 | 121.3669 | -0.12817 | 121.4905 | 61.3861 | -0.17395 | 121.3669 | -0.12817 | 61.3861 | 121.3074 | 121.4905 | -121.6461 | -121.7606
332.1875 | 121.8292 | -61.2946 | 60.3104 | -0.030136 | 0.017532 | 0.0045395 | 0.012971 | 0.055668 | -0.011818 | 0.067543 | -61.3358 | 60.1547 | -61.3861 | -61.409 | 60.0266 | 0.11902 | -0.054932 | -0.032043 | 60.26 | -61.4273 | -0.091552 | -0.15564 | -0.041198 | -0.11444 | -0.28381 | -0.13275 | -0.050354 | 0.050354 | 61.2396 | 61.2625 | 121.3211 | 121.4493 | -0.041198 | 121.5546 | 61.4136 | -0.13275 | 121.4493 | -0.041198 | 61.4136 | 121.3211 | 121.5546 | -121.6965 | -121.7377
333.875 | 121.8613 | -61.2396 | 60.3653 | -0.16747 | 0.016891 | 0.0017623 | 0.0065624 | 0.053959 | -0.0086132 | 0.068825 | -61.322 | 60.2554 | -61.2762 | -61.3403 | 60.1135 | 0.25635 | 0.2655 | 0.19684 | 60.3607 | -61.3907 | -0.036621 | -0.10986 | -0.082397 | -0.10071 | -0.25177 | -0.15106 | -0.004577 | -0.045776 | 61.5051 | 61.4365 | 121.3531 | 121.4951 | -0.082397 | 121.6003 | 61.496 | -0.15106 | 121.4951 | -0.082397 | 61.496 | 121.3531 | 121.6003 | -121.6415 | -121.756
335.6094 | 121.7972 | -61.3129 | 60.3241 | -0.098801 | 0.0139 | 0.0032577 | 0.011903 | 0.053532 | -0.010109 | 0.066262 | -61.3174 | 60.1593 | -61.3403 | -61.3541 | 60.0815 | 0.19226 | 0.013733 | 0.086975 | 60.2921 | -61.3907 | -0.027466 | -0.1648 | -0.004578 | -0.041199 | -0.24262 | -0.07782 | -0.032044 | 0.022888 | 61.3266 | 61.3998 | 121.3943 | 121.4722 | -0.004578 | 121.6049 | 61.5051 | -0.07782 | 121.4722 | -0.004578 | 61.5051 | 121.3943 | 121.6049 | -121.6644 | -121.7148
337.3594 | 121.8521 | -61.2396 | 60.4111 | -0.20561 | 0.0139 | 0.00048074 | 0.0025036 | 0.050755 | -0.0083996 | 0.067543 | -61.2396 | 60.228 | -61.2122 | -61.2808 | 60.173 | 0.33417 | 0.20599 | 0.31128 | 60.3241 | -61.3495 | 0.027466 | -0.18311 | 0 | -0.041199 | -0.23804 | -0.10986 | -0.086975 | -0.027466 | 61.4456 | 61.5509 | 121.4127 | 121.4676 | 0 | 121.5637 | 61.5738 | -0.10986 | 121.4676 | 0 | 61.5738 | 121.4127 | 121.5637 | -121.6232 | -121.7606
339.1094 | 121.9162 | -61.2167 | 60.3653 | 0.11482 | 0.015396 | 0.0062485 | 0.0054944 | 0.05225 | -0.006477 | 0.066689 | -61.3083 | 60.1318 | -61.3037 | -61.3541 | 60.0906 | 0.14191 | -0.20142 | 0.068665 | 60.2325 | -61.4044 | -0.086975 | -0.23346 | -0.091553 | -0.13733 | -0.27466 | -0.18768 | -0.13275 | -0.004578 | 61.0153 | 61.2854 | 121.3074 | 121.3486 | -0.091553 | 121.4493 | 61.3586 | -0.18768 | 121.3486 | -0.091553 | 61.3586 | 121.3074 | 121.4493 | -121.669 | -121.7697
340.7969 | 121.9299 | -61.2808 | 60.2783 | 0.091934 | 0.014114 | 0.0028305 | 0.012117 | 0.055027 | -0.0096814 | 0.06733 | -61.4548 | 60.1318 | -61.4136 | -61.4639 | 59.9716 | 0.013733 | -0.11444 | -0.16937 | 60.2417 | -61.4365 | -0.13275 | -0.14648 | -0.17395 | -0.18311 | -0.3067 | -0.15564 | -0.036621 | -0.041199 | 61.1664 | 61.1114 | 121.2524 | 121.4127 | -0.17395 | 121.5225 | 61.2946 | -0.15564 | 121.4127 | -0.17395 | 61.2946 | 121.2524 | 121.5225 | -121.6919 | -121.7148
342.5469 | 121.7972 | -61.2259 | 60.4065 | -0.22087 | 0.014114 | 0.0062485 | 0.0054944 | 0.050968 | -0.0083996 | 0.066475 | -61.2167 | 60.2097 | -61.235 | -61.2579 | 60.2188 | 0.35706 | 0.10986 | 0.34332 | 60.3149 | -61.3312 | -0.009155 | -0.19684 | 0.009155 | -0.032044 | -0.18768 | -0.10529 | -0.091553 | 0.01831 | 61.3358 | 61.5692 | 121.4447 | 121.4355 | 0.009155 | 121.5408 | 61.5829 | -0.10529 | 121.4355 | 0.009155 | 61.5829 | 121.4447 | 121.5408 | -121.6415 | -121.7377
344.2969 | 121.907 | -61.2076 | 60.3928 | -0.098801 | 0.013046 | 0.0019759 | 0.0035718 | 0.05225 | -0.0086132 | 0.066689 | -61.2579 | 60.2234 | -61.2396 | -61.2625 | 60.1822 | 0.29755 | 0.041199 | 0.28381 | 60.3104 | -61.3358 | -0.032043 | -0.16937 | -0.050354 | -0.054931 | -0.21057 | -0.12817 | -0.082397 | -0.018311 | 61.2488 | 61.4914 | 121.3898 | 121.431 | -0.050354 | 121.5179 | 61.5051 | -0.12817 | 121.431 | -0.050354 | 61.5051 | 121.3898 | 121.5179 | -121.6324 | -121.7285
345.9844 | 121.8384 | -61.3312 | 60.3149 | -0.060654 | 0.013687 | 0.0062485 | 0.01233 | 0.055668 | -0.009895 | 0.066689 | -61.3358 | 60.1227 | -61.377 | -61.3907 | 60.0357 | 0.12817 | -0.045776 | 0 | 60.2646 | -61.4182 | -0.045776 | -0.19226 | -0.004577 | -0.059509 | -0.27923 | -0.086975 | -0.050354 | 0.041199 | 61.2854 | 61.3312 | 121.3669 | 121.4539 | -0.004577 | 121.5958 | 61.4594 | -0.086975 | 121.4539 | -0.004577 | 61.4594 | 121.3669 | 121.5958 | -121.6919 | -121.7331
347.7344 | 121.8933 | -61.2396 | 60.3241 | 0.17586 | 0.012832 | 0.0051803 | 0.0065624 | 0.05225 | -0.009895 | 0.066262 | -61.3266 | 60.0861 | -61.3174 | -61.3449 | 60.1044 | 0.12817 | -0.29755 | 0.032043 | 60.2005 | -61.409 | -0.07782 | -0.23804 | -0.086975 | -0.10529 | -0.21973 | -0.16937 | -0.1236 | -0.009155 | 60.9421 | 61.2717 | 121.344 | 121.3257 | -0.086975 | 121.4401 | 61.3678 | -0.16937 | 121.3257 | -0.086975 | 61.3678 | 121.344 | 121.4401 | -121.6415 | -121.7331
349.4688 | 121.9528 | -61.1755 | 60.3607 | 0.0080111 | 0.012405 | 0.0038985 | 0.0046398 | 0.051609 | -0.0096814 | 0.066262 | -61.3129 | 60.1913 | -61.2625 | -61.3403 | 60.1089 | 0.19684 | -0.004578 | 0.15106 | 60.2921 | -61.3724 | -0.086975 | -0.16937 | -0.13733 | -0.16479 | -0.25177 | -0.19684 | -0.068665 | -0.050354 | 61.171 | 61.3266 | 121.2845 | 121.3669 | -0.13733 | 121.4676 | 61.3724 | -0.19684 | 121.3669 | -0.13733 | 61.3724 | 121.2845 | 121.4676 | -121.6232 | -121.7331
351.1562 | 121.8842 | -61.2442 | 60.3516 | 0.18349 | 0.015823 | 0.0047531 | 0.010621 | 0.053959 | -0.009895 | 0.06733 | -61.2991 | 60.0952 | -61.322 | -61.3358 | 60.0906 | 0.13275 | -0.29755 | 0.027466 | 60.228 | -61.4182 | -0.077819 | -0.25635 | -0.054931 | -0.091552 | -0.26093 | -0.17395 | -0.1236 | 0.022888 | 60.9467 | 61.2717 | 121.3348 | 121.3394 | -0.054931 | 121.4722 | 61.377 | -0.17395 | 121.3394 | -0.054931 | 61.377 | 121.3348 | 121.4722 | -121.6736 | -121.7697
352.8438 | 121.907 | -61.2488 | 60.3333 | 0.17586 | 0.016891 | 0.0019759 | 0.0086988 | 0.052464 | -0.012886 | 0.068184 | -61.3678 | 60.0998 | -61.3724 | -61.3953 | 60.0403 | 0.068665 | -0.27008 | -0.045776 | 60.2005 | -61.4182 | -0.1236 | -0.23346 | -0.11902 | -0.14648 | -0.29297 | -0.16937 | -0.13275 | 0.004577 | 60.9787 | 61.203 | 121.2891 | 121.3486 | -0.11902 | 121.4493 | 61.3174 | -0.16937 | 121.3486 | -0.11902 | 61.3174 | 121.2891 | 121.4493 | -121.7056 | -121.7514
354.5938 | 121.8246 | -61.3129 | 60.3195 | -0.18272 | 0.01625 | 0.0013351 | 0.0076306 | 0.054173 | -0.011604 | 0.065193 | -61.3266 | 60.2417 | -61.322 | -61.3403 | 60.0815 | 0.2243 | 0.15106 | 0.13275 | 60.3104 | -61.4044 | -0.009155 | -0.07782 | -0.013733 | -0.027466 | -0.23804 | -0.091553 | -0.009155 | -0.004578 | 61.4639 | 61.4456 | 121.3943 | 121.5546 | -0.013733 | 121.6232 | 61.5372 | -0.091553 | 121.5546 | -0.013733 | 61.5372 | 121.3943 | 121.6232 | -121.6415 | -121.7239
356.3125 | 121.9528 | -61.1755 | 60.3882 | 0.00038159 | 0.012832 | 0.0066757 | 0.0033582 | 0.053532 | -0.0077588 | 0.067116 | -61.3129 | 60.1913 | -61.2762 | -61.3358 | 60.1227 | 0.21057 | -0.013733 | 0.15106 | 60.2921 | -61.3907 | -0.10071 | -0.19684 | -0.13733 | -0.16022 | -0.2655 | -0.21515 | -0.096131 | -0.036621 | 61.1618 | 61.3266 | 121.2982 | 121.3669 | -0.13733 | 121.4676 | 61.3861 | -0.21515 | 121.3669 | -0.13733 | 61.3861 | 121.2982 | 121.4676 | -121.6644 | -121.7789
358 | 121.9299 | -61.203 | 60.3607 | -0.014877 | 0.018387 | 0.0028305 | 0.003999 | 0.054173 | -0.0086132 | 0.066475 | -61.3037 | 60.1913 | -61.2671 | -61.3312 | 60.141 | 0.23804 | 0 | 0.19226 | 60.2921 | -61.3815 | -0.064087 | -0.16937 | -0.10071 | -0.12817 | -0.21973 | -0.17853 | -0.068665 | -0.036621 | 61.203 | 61.3953 | 121.344 | 121.3943 | -0.10071 | 121.4951 | 61.441 | -0.17853 | 121.3943 | -0.10071 | 61.441 | 121.344 | 121.4951 | -121.6278 | -121.7422
359.7344 | 121.9437 | -61.1801 | 60.3882 | 0.0080111 | 0.013687 | 0.0015487 | 0.0046398 | 0.052037 | -0.01075 | 0.066475 | -61.3129 | 60.1959 | -61.2762 | -61.3449 | 60.0952 | 0.19226 | -0.004578 | 0.13733 | 60.3058 | -61.3678 | -0.09613 | -0.19226 | -0.13275 | -0.16479 | -0.29297 | -0.18768 | -0.082398 | -0.036621 | 61.1755 | 61.3174 | 121.2753 | 121.376 | -0.13275 | 121.4859 | 61.3724 | -0.18768 | 121.376 | -0.13275 | 61.3724 | 121.2753 | 121.4859 | -121.6644 | -121.756
361.4062 | 121.9574 | -61.203 | 60.3607 | 0.01564 | 0.015823 | 0.0073165 | 0.0076306 | 0.052037 | -0.010109 | 0.066262 | -61.3312 | 60.141 | -61.3083 | -61.3495 | 60.0906 | 0.15564 | -0.07782 | 0.09613 | 60.2783 | -61.377 | -0.10529 | -0.21973 | -0.12817 | -0.14648 | -0.27008 | -0.17395 | -0.082398 | -0.022888 | 61.1252 | 61.2991 | 121.2936 | 121.344 | -0.12817 | 121.4813 | 61.3586 | -0.17395 | 121.344 | -0.12817 | 61.3586 | 121.2936 | 121.4813 | -121.669 | -121.7377
363.1719 | 121.8338 | -61.29 | 60.3104 | -0.18272 | 0.017746 | 0.0028305 | 0.01233 | 0.052464 | -0.010536 | 0.068611 | -61.3358 | 60.1959 | -61.3495 | -61.3358 | 60.0952 | 0.22888 | 0.14648 | 0.14191 | 60.3607 | -61.3678 | -0.059509 | -0.11444 | -0.045776 | -0.045776 | -0.21515 | -0.07782 | 0.050354 | 0.013733 | 61.4365 | 61.4319 | 121.3852 | 121.4859 | -0.045776 | 121.6507 | 61.5189 | -0.07782 | 121.4859 | -0.045776 | 61.5189 | 121.3852 | 121.6507 | -121.6599 | -121.6782
364.9219 | 121.9254 | -61.171 | 60.3653 | 0.11482 | 0.01625 | 0.0066757 | 0.0067762 | 0.053746 | -0.008827 | 0.067757 | -61.3083 | 60.1273 | -61.3174 | -61.3312 | 60.1044 | 0.14191 | -0.15564 | 0.068665 | 60.26 | -61.3907 | -0.14648 | -0.23804 | -0.13733 | -0.16022 | -0.26093 | -0.21973 | -0.10529 | 0.009155 | 61.0153 | 61.2396 | 121.2753 | 121.2982 | -0.13733 | 121.431 | 61.3129 | -0.21973 | 121.2982 | -0.13733 | 61.3129 | 121.2753 | 121.431 | -121.6827 | -121.756
366.6094 | 121.9162 | -61.1893 | 60.3699 | -0.037765 | 0.01326 | 0.0028305 | 0.003999 | 0.052891 | -0.0094678 | 0.065621 | -61.3037 | 60.1685 | -61.2671 | -61.2991 | 60.1501 | 0.24261 | 0.027466 | 0.21057 | 60.2875 | -61.3495 | -0.07782 | -0.20142 | -0.11444 | -0.10986 | -0.21973 | -0.16022 | -0.082397 | -0.036621 | 61.2167 | 61.3998 | 121.3394 | 121.3577 | -0.11444 | 121.4767 | 61.4319 | -0.16022 | 121.3577 | -0.11444 | 61.4319 | 121.3394 | 121.4767 | -121.637 | -121.7194
368.375 | 121.8933 | -61.2396 | 60.3561 | 0.13771 | 0.015609 | 0.0060349 | 0.010835 | 0.0546 | -0.009895 | 0.068398 | -61.2991 | 60.1135 | -61.3266 | -61.3403 | 60.0861 | 0.10529 | -0.29755 | -0.009155 | 60.228 | -61.409 | -0.086975 | -0.24262 | -0.059509 | -0.10071 | -0.27008 | -0.16937 | -0.12817 | 0.027466 | 60.9421 | 61.2305 | 121.3257 | 121.3531 | -0.059509 | 121.4676 | 61.3449 | -0.16937 | 121.3531 | -0.059509 | 61.3449 | 121.3257 | 121.4676 | -121.6827 | -121.7651
370.0625 | 121.9391 | -61.1664 | 60.3516 | 0.069046 | 0.013473 | -0.00037386 | 0.0046398 | 0.053105 | -0.0079724 | 0.067116 | -61.3174 | 60.1639 | -61.2991 | -61.3586 | 60.1044 | 0.14648 | -0.10529 | 0.09613 | 60.26 | -61.3998 | -0.13275 | -0.18768 | -0.15106 | -0.19226 | -0.24719 | -0.23346 | -0.091552 | -0.018311 | 61.0611 | 61.2625 | 121.2708 | 121.3303 | -0.15106 | 121.4264 | 61.3129 | -0.23346 | 121.3303 | -0.15106 | 61.3129 | 121.2708 | 121.4264 | -121.6507 | -121.7514
371.8125 | 121.8201 | -61.235 | 60.4477 | -0.19798 | 0.011337 | 0.00069434 | 0.0061352 | 0.050541 | -0.0069042 | 0.066262 | -61.2259 | 60.1959 | -61.2396 | -61.2167 | 60.2371 | 0.37079 | 0.091553 | 0.33875 | 60.3058 | -61.3174 | -0.004578 | -0.25177 | 0.009155 | 0.01831 | -0.21057 | -0.082398 | -0.14191 | 0.013733 | 61.3266 | 61.5738 | 121.4722 | 121.431 | 0.009155 | 121.5408 | 61.6058 | -0.082398 | 121.431 | 0.009155 | 61.6058 | 121.4722 | 121.5408 | -121.6873 | -121.7651
373.5938 | 121.8796 | -61.2122 | 60.3745 | 0.16823 | 0.015823 | 0.0075301 | 0.010621 | 0.052464 | -0.0096814 | 0.066689 | -61.3037 | 60.0952 | -61.3358 | -61.3495 | 60.0906 | 0.12817 | -0.3067 | 0.013733 | 60.1776 | -61.4136 | -0.1236 | -0.27924 | -0.091553 | -0.13733 | -0.28381 | -0.20142 | -0.19684 | 0.032043 | 60.9055 | 61.2259 | 121.3028 | 121.3074 | -0.091553 | 121.3898 | 61.3403 | -0.20142 | 121.3074 | -0.091553 | 61.3403 | 121.3028 | 121.3898 | -121.7102 | -121.788
375.3438 | 121.8613 | -61.2808 | 60.3241 | -0.16747 | 0.014755 | 0.0049667 | 0.011903 | 0.053318 | -0.0079724 | 0.06797 | -61.3449 | 60.1868 | -61.3403 | -61.3403 | 60.0861 | 0.24719 | 0.17853 | 0.14191 | 60.3378 | -61.3724 | -0.059509 | -0.13733 | -0.064087 | -0.059509 | -0.23804 | -0.091552 | 0.013733 | -0.004578 | 61.4594 | 61.4227 | 121.3669 | 121.4676 | -0.064087 | 121.6187 | 61.528 | -0.091552 | 121.4676 | -0.064087 | 61.528 | 121.3669 | 121.6187 | -121.6644 | -121.6965
377.0156 | 121.8109 | -61.2854 | 60.3241 | -0.16747 | 0.011978 | 0.0021895 | 0.012544 | 0.054814 | -0.010322 | 0.066902 | -61.3266 | 60.1959 | -61.3449 | -61.3495 | 60.0952 | 0.2243 | 0.09613 | 0.12817 | 60.3424 | -61.3815 | -0.05951 | -0.12817 | -0.041199 | -0.064087 | -0.22888 | -0.096131 | 0.01831 | 0.018311 | 61.3815 | 61.4136 | 121.3806 | 121.4813 | -0.041199 | 121.6278 | 61.5097 | -0.096131 | 121.4813 | -0.041199 | 61.5097 | 121.3806 | 121.6278 | -121.669 | -121.7056
378.7812 | 121.9345 | -61.1755 | 60.3607 | 0.00038159 | 0.013473 | 0.0058211 | -0.00048698 | 0.052037 | -0.0066906 | 0.065193 | -61.3083 | 60.1959 | -61.2579 | -61.3358 | 60.1364 | 0.19226 | -0.009155 | 0.14648 | 60.3149 | -61.377 | -0.082398 | -0.16479 | -0.13275 | -0.16022 | -0.2243 | -0.20142 | -0.045777 | -0.050354 | 61.1664 | 61.322 | 121.312 | 121.3715 | -0.13275 | 121.4905 | 61.3678 | -0.20142 | 121.3715 | -0.13275 | 61.3678 | 121.312 | 121.4905 | -121.6187 | -121.7377
380.4688 | 121.7926 | -61.3266 | 60.3195 | -0.098801 | 0.016037 | 0.0038985 | 0.011476 | 0.054386 | -0.012245 | 0.068184 | -61.3266 | 60.1685 | -61.3358 | -61.3449 | 60.0815 | 0.20599 | 0.018311 | 0.086975 | 60.2783 | -61.377 | -0.009155 | -0.15106 | 0 | -0.018311 | -0.23804 | -0.050354 | -0.041199 | 0.009155 | 61.3449 | 61.4136 | 121.4081 | 121.4951 | 0 | 121.6049 | 61.5326 | -0.050354 | 121.4951 | 0 | 61.5326 | 121.4081 | 121.6049 | -121.6553 | -121.6965
382.2188 | 121.8979 | -61.2213 | 60.3607 | 0.17586 | 0.014969 | 0.0041123 | 0.0067762 | 0.0546 | -0.0096814 | 0.067757 | -61.3037 | 60.0861 | -61.3495 | -61.3403 | 60.1089 | 0.1236 | -0.27924 | 0.036621 | 60.2142 | -61.4182 | -0.12817 | -0.27466 | -0.082398 | -0.11902 | -0.25177 | -0.19684 | -0.14648 | 0.045776 | 60.9421 | 61.2579 | 121.3303 | 121.3074 | -0.082398 | 121.4355 | 61.3449 | -0.19684 | 121.3074 | -0.082398 | 61.3449 | 121.3303 | 121.4355 | -121.7102 | -121.7789
383.9688 | 121.9025 | -61.2167 | 60.3653 | 0.099564 | 0.0139 | 0.0051803 | 0.0061352 | 0.053959 | -0.01075 | 0.068398 | -61.3266 | 60.0769 | -61.3037 | -61.3541 | 60.1044 | 0.12817 | -0.21057 | 0.050354 | 60.2692 | -61.3586 | -0.086975 | -0.28839 | -0.10986 | -0.13733 | -0.26093 | -0.14191 | -0.09613 | -0.022888 | 61.0062 | 61.2671 | 121.3211 | 121.2936 | -0.10986 | 121.4859 | 61.3449 | -0.14191 | 121.2936 | -0.10986 | 61.3449 | 121.3211 | 121.4859 | -121.669 | -121.7239
385.6406 | 121.8613 | -61.2488 | 60.347 | -0.18272 | 0.010482 | 5.3338e-05 | 0.0095532 | 0.0499 | -0.0094678 | 0.068825 | -61.3312 | 60.2509 | -61.3174 | -61.3678 | 60.0815 | 0.2243 | 0.20599 | 0.14191 | 60.3424 | -61.3861 | -0.068665 | -0.096131 | -0.082398 | -0.11902 | -0.2655 | -0.13733 | -0.004578 | -0.013733 | 61.4548 | 61.3907 | 121.3303 | 121.4996 | -0.082398 | 121.5912 | 61.4731 | -0.13733 | 121.4996 | -0.082398 | 61.4731 | 121.3303 | 121.5912 | -121.6644 | -121.7331
387.375 | 121.8018 | -61.322 | 60.3149 | -0.075912 | 0.016891 | 0.0038985 | 0.012117 | 0.055027 | -0.012031 | 0.067116 | -61.322 | 60.1456 | -61.3495 | -61.3541 | 60.0723 | 0.17853 | -0.041199 | 0.045776 | 60.2783 | -61.4044 | -0.027466 | -0.16937 | 0 | -0.032044 | -0.24261 | -0.082398 | -0.036621 | 0.027466 | 61.2808 | 61.3678 | 121.3943 | 121.4676 | 0 | 121.6003 | 61.5005 | -0.082398 | 121.4676 | 0 | 61.5005 | 121.3943 | 121.6003 | -121.6644 | -121.7194
389.125 | 121.8338 | -61.2396 | 60.3836 | -0.23613 | 0.01326 | 0.0011215 | 0.0063488 | 0.051823 | -0.0092542 | 0.069039 | -61.2396 | 60.2371 | -61.2579 | -61.2762 | 60.1959 | 0.34332 | 0.19684 | 0.3067 | 60.3333 | -61.3403 | -0.018311 | -0.14648 | 0 | -0.036621 | -0.18768 | -0.10071 | -0.050354 | 0.018311 | 61.4365 | 61.5463 | 121.4355 | 121.4767 | 0 | 121.5729 | 61.5829 | -0.10071 | 121.4767 | 0 | 61.5829 | 121.4355 | 121.5729 | -121.6415 | -121.7239
390.8594 | 121.8201 | -61.2946 | 60.3058 | -0.030136 | 0.015396 | 0.0058211 | 0.011689 | 0.055027 | -0.012245 | 0.066902 | -61.3358 | 60.1501 | -61.3449 | -61.3953 | 60.0357 | 0.1236 | -0.054932 | -0.009155 | 60.2966 | -61.4182 | -0.050354 | -0.15564 | -0.041198 | -0.10071 | -0.27008 | -0.1236 | -0.009155 | 0.009156 | 61.2396 | 61.2854 | 121.3303 | 121.4447 | -0.041198 | 121.5912 | 61.4182 | -0.1236 | 121.4447 | -0.041198 | 61.4182 | 121.3303 | 121.5912 | -121.6507 | -121.7239
392.6094 | 121.9391 | -61.1893 | 60.347 | 0.076676 | 0.01091 | 0.0021895 | 0.0048534 | 0.052677 | -0.010536 | 0.066902 | -61.3174 | 60.1868 | -61.2671 | -61.3678 | 60.1273 | 0.15564 | -0.10986 | 0.091553 | 60.26 | -61.3815 | -0.07782 | -0.16022 | -0.12817 | -0.17853 | -0.21973 | -0.19226 | -0.086975 | -0.050354 | 61.0794 | 61.2808 | 121.3165 | 121.376 | -0.12817 | 121.4493 | 61.3449 | -0.19226 | 121.376 | -0.12817 | 61.3449 | 121.3165 | 121.4493 | -121.6141 | -121.7285
394.2969 | 121.9025 | -61.235 | 60.347 | 0.12245 | 0.0139 | 0.0062485 | 0.0086988 | 0.053318 | -0.01075 | 0.069679 | -61.322 | 60.1273 | -61.3541 | -61.3358 | 60.1044 | 0.13275 | -0.28839 | -0.004578 | 60.2417 | -61.409 | -0.11902 | -0.21973 | -0.086975 | -0.10071 | -0.24261 | -0.17395 | -0.10529 | 0.032044 | 60.9467 | 61.2305 | 121.3394 | 121.3623 | -0.086975 | 121.4767 | 61.3678 | -0.17395 | 121.3623 | -0.086975 | 61.3678 | 121.3394 | 121.4767 | -121.701 | -121.756
395.9844 | 121.8109 | -61.3129 | 60.3333 | -0.068283 | 0.014114 | 0.0053939 | 0.0095532 | 0.0546 | -0.010322 | 0.069252 | -61.322 | 60.1456 | -61.3495 | -61.3632 | 60.0815 | 0.16022 | -0.009155 | 0.027466 | 60.2783 | -61.4044 | -0.036621 | -0.18768 | -0.009155 | -0.050354 | -0.25177 | -0.091553 | -0.054932 | 0.027466 | 61.3037 | 61.3403 | 121.3943 | 121.4584 | -0.009155 | 121.5912 | 61.4731 | -0.091553 | 121.4584 | -0.009155 | 61.4731 | 121.3943 | 121.5912 | -121.6827 | -121.7377
397.7344 | 121.788 | -61.3129 | 60.3241 | -0.083542 | 0.015609 | 0.0019759 | 0.0097668 | 0.052037 | -0.010109 | 0.067543 | -61.3403 | 60.1685 | -61.3312 | -61.3632 | 60.0861 | 0.21057 | 0.004578 | 0.07782 | 60.2829 | -61.4227 | -0.018311 | -0.15564 | -0.027466 | -0.050354 | -0.23804 | -0.10986 | -0.041199 | -0.009155 | 61.3174 | 61.3907 | 121.3989 | 121.4813 | -0.027466 | 121.5958 | 61.5234 | -0.10986 | 121.4813 | -0.027466 | 61.5234 | 121.3989 | 121.5958 | -121.6553 | -121.7468
399.5 | 121.8475 | -61.2854 | 60.3516 | -0.23613 | 0.015823 | -0.0033647 | 0.0050672 | 0.053959 | -0.0079724 | 0.06733 | -61.2854 | 60.2325 | -61.2854 | -61.322 | 60.1181 | 0.28381 | 0.24261 | 0.25177 | 60.3836 | -61.3449 | 0 | -0.11902 | 0 | -0.036621 | -0.23346 | -0.05951 | 0.032044 | 0 | 61.528 | 61.5372 | 121.4035 | 121.5179 | 0 | 121.669 | 61.5692 | -0.05951 | 121.5179 | 0 | 61.5692 | 121.4035 | 121.669 | -121.637 | -121.6965
401.1875 | 121.8338 | -61.3037 | 60.3195 | -0.030136 | 0.016037 | 0.00026694 | 0.011476 | 0.054814 | -0.011604 | 0.068184 | -61.3449 | 60.1318 | -61.3632 | -61.4136 | 60.0266 | 0.10071 | -0.054932 | -0.032043 | 60.2921 | -61.4182 | -0.059509 | -0.18768 | -0.041199 | -0.10986 | -0.29297 | -0.11444 | -0.027466 | 0.01831 | 61.2488 | 61.2717 | 121.3303 | 121.4355 | -0.041199 | 121.5958 | 61.4044 | -0.11444 | 121.4355 | -0.041199 | 61.4044 | 121.3303 | 121.5958 | -121.6827 | -121.7377
402.9531 | 121.8704 | -61.2808 | 60.3104 | -0.23613 | 0.017105 | -0.0022965 | 0.0069898 | 0.05225 | -0.0083996 | 0.068184 | -61.3358 | 60.2875 | -61.2854 | -61.377 | 60.0815 | 0.25177 | 0.25177 | 0.16937 | 60.3516 | -61.3861 | -0.004577 | -0.022888 | -0.054931 | -0.09613 | -0.22888 | -0.10529 | 0.041198 | -0.050354 | 61.5326 | 61.4502 | 121.3623 | 121.5683 | -0.054931 | 121.6324 | 61.5326 | -0.10529 | 121.5683 | -0.054931 | 61.5326 | 121.3623 | 121.6324 | -121.5958 | -121.6965
404.7031 | 121.8613 | -61.2762 | 60.3653 | -0.15984 | 0.014969 | 0.0013351 | 0.005708 | 0.053959 | -0.012886 | 0.066262 | -61.3266 | 60.2371 | -61.2808 | -61.3678 | 60.0998 | 0.27924 | 0.24261 | 0.20142 | 60.4065 | -61.3541 | -0.004578 | -0.12817 | -0.050354 | -0.091553 | -0.2655 | -0.07782 | 0.041199 | -0.045776 | 61.5189 | 61.4777 | 121.376 | 121.5134 | -0.050354 | 121.6827 | 61.5555 | -0.07782 | 121.5134 | -0.050354 | 61.5555 | 121.376 | 121.6827 | -121.6461 | -121.7194
406.3906 | 121.7972 | -61.3129 | 60.3516 | -0.11406 | 0.015396 | 0.0036849 | 0.0080578 | 0.052891 | -0.011604 | 0.066689 | -61.3129 | 60.1913 | -61.3449 | -61.3632 | 60.0677 | 0.20142 | 0.022888 | 0.07782 | 60.3104 | -61.409 | -0.032044 | -0.16022 | 0 | -0.050354 | -0.28381 | -0.096131 | -0.041198 | 0.032044 | 61.3358 | 61.3907 | 121.3806 | 121.5042 | 0 | 121.6232 | 61.5143 | -0.096131 | 121.5042 | 0 | 61.5143 | 121.3806 | 121.6232 | -121.6965 | -121.7606
408.1562 | 121.8475 | -61.2808 | 60.3561 | -0.19798 | 0.015182 | -0.00016026 | 0.0050672 | 0.053318 | -0.01139 | 0.07032 | -61.3358 | 60.2325 | -61.3083 | -61.3632 | 60.1135 | 0.25177 | 0.27924 | 0.20599 | 60.4065 | -61.3495 | -0.027466 | -0.1236 | -0.054931 | -0.082397 | -0.24262 | -0.068664 | 0.050354 | -0.027465 | 61.5601 | 61.4868 | 121.3943 | 121.5134 | -0.054931 | 121.6873 | 61.5326 | -0.068664 | 121.5134 | -0.054931 | 61.5326 | 121.3943 | 121.6873 | -121.6644 | -121.7056
410.125 | 121.8979 | -61.235 | 60.3607 | 0.15297 | 0.0139 | 0.0043259 | 0.0050672 | 0.054814 | -0.009895 | 0.066048 | -61.3083 | 60.0952 | -61.3724 | -61.3678 | 60.1181 | 0.13733 | -0.28381 | 0.036621 | 60.2142 | -61.3907 | -0.13733 | -0.2655 | -0.073243 | -0.13275 | -0.24262 | -0.15564 | -0.14648 | 0.064086 | 60.9512 | 61.2717 | 121.3531 | 121.3303 | -0.073243 | 121.4493 | 61.3724 | -0.15564 | 121.3303 | -0.073243 | 61.3724 | 121.3531 | 121.4493 | -121.7331 | -121.7514
413.9219 | 121.8567 | -61.1938 | 60.3928 | -0.12169 | 0.012405 | 0.0034713 | 0.0037854 | 0.05225 | -0.0096814 | 0.06733 | -61.2396 | 60.1639 | -61.2625 | -61.2488 | 60.1868 | 0.32501 | 0.027466 | 0.32501 | 60.3195 | -61.3174 | -0.068664 | -0.22888 | -0.045776 | -0.054931 | -0.20599 | -0.1236 | -0.073242 | 0.022888 | 61.2213 | 61.5189 | 121.3806 | 121.3577 | -0.045776 | 121.5134 | 61.5189 | -0.1236 | 121.3577 | -0.045776 | 61.5189 | 121.3806 | 121.5134 | -121.6553 | -121.7102
417.2656 | 121.8979 | -61.2305 | 60.3516 | 0.14534 | 0.014969 | 0.0056075 | 0.010835 | 0.0546 | -0.011177 | 0.066048 | -61.322 | 60.1227 | -61.3495 | -61.3632 | 60.0861 | 0.10986 | -0.27466 | -0.018311 | 60.2509 | -61.4136 | -0.11902 | -0.22888 | -0.091552 | -0.13275 | -0.2655 | -0.1831 | -0.10071 | 0.027466 | 60.9558 | 61.2122 | 121.3165 | 121.3531 | -0.091552 | 121.4813 | 61.3403 | -0.1831 | 121.3531 | -0.091552 | 61.3403 | 121.3165 | 121.4813 | -121.701 | -121.7651
422.9375 | 121.9299 | -61.1755 | 60.3973 | -0.022507 | 0.017959 | 0.0026169 | 0.0046398 | 0.05225 | -0.006477 | 0.066689 | -61.2946 | 60.1593 | -61.2488 | -61.3083 | 60.1547 | 0.24719 | 0.027466 | 0.21515 | 60.3012 | -61.3541 | -0.073242 | -0.23804 | -0.11902 | -0.13275 | -0.24262 | -0.17853 | -0.096131 | -0.045777 | 61.203 | 61.3907 | 121.3303 | 121.3348 | -0.11902 | 121.4767 | 61.4227 | -0.17853 | 121.3348 | -0.11902 | 61.4227 | 121.3303 | 121.4767 | -121.6461 | -121.7514
424.7031 | 121.8063 | -61.235 | 60.434 | -0.18272 | 0.01326 | 5.3338e-05 | 0.0067762 | 0.050755 | -0.0069042 | 0.068184 | -61.203 | 60.1959 | -61.235 | -61.2122 | 60.2234 | 0.36621 | 0.09613 | 0.35706 | 60.347 | -61.322 | 0 | -0.23804 | 0.032043 | 0.022888 | -0.21057 | -0.086975 | -0.086975 | 0.032043 | 61.3312 | 61.5921 | 121.4584 | 121.431 | 0.032043 | 121.582 | 61.6013 | -0.086975 | 121.431 | 0.032043 | 61.6013 | 121.4584 | 121.582 | -121.669 | -121.756
426.4531 | 121.907 | -61.235 | 60.347 | 0.16823 | 0.014328 | -0.00037386 | 0.010621 | 0.055241 | -0.010109 | 0.06797 | -61.3495 | 60.0861 | -61.3724 | -61.3724 | 60.0677 | 0.10986 | -0.30212 | -0.027466 | 60.2509 | -61.3998 | -0.13733 | -0.26092 | -0.11444 | -0.13733 | -0.27924 | -0.1648 | -0.096131 | 0.022888 | 60.9329 | 61.2076 | 121.3028 | 121.3211 | -0.11444 | 121.4859 | 61.3449 | -0.1648 | 121.3211 | -0.11444 | 61.3449 | 121.3028 | 121.4859 | -121.7194 | -121.7468
428.2031 | 121.843 | -61.3129 | 60.347 | 0.00038159 | 0.013473 | 0.0058211 | 0.010194 | 0.055455 | -0.010536 | 0.067757 | -61.3678 | 60.1501 | -61.3815 | -61.409 | 60.0082 | 0.073242 | -0.068665 | -0.059509 | 60.2783 | -61.4456 | -0.068665 | -0.19684 | -0.054932 | -0.096131 | -0.33874 | -0.13275 | -0.068665 | 0.013733 | 61.2442 | 61.2534 | 121.3211 | 121.463 | -0.054932 | 121.5912 | 61.3861 | -0.13275 | 121.463 | -0.054932 | 61.3861 | 121.3211 | 121.5912 | -121.7285 | -121.7926
429.9375 | 121.9482 | -61.1984 | 60.3516 | 0.038529 | 0.015396 | -0.0018693 | 0.0050672 | 0.051823 | -0.0096814 | 0.067116 | -61.3129 | 60.1501 | -61.3037 | -61.3541 | 60.0998 | 0.16022 | -0.082397 | 0.091553 | 60.2737 | -61.4044 | -0.10529 | -0.20142 | -0.11444 | -0.15564 | -0.25177 | -0.20599 | -0.077819 | -0.009155 | 61.116 | 61.29 | 121.2982 | 121.3486 | -0.11444 | 121.4722 | 61.3586 | -0.20599 | 121.3486 | -0.11444 | 61.3586 | 121.2982 | 121.4722 | -121.6553 | -121.756
431.6094 | 121.8338 | -61.2259 | 60.3973 | -0.12932 | 0.013687 | 0.00069434 | 0.0054944 | 0.050755 | -0.0096814 | 0.068398 | -61.2305 | 60.2142 | -61.2442 | -61.2213 | 60.2188 | 0.36163 | 0.041199 | 0.34332 | 60.2966 | -61.3495 | -0.018311 | -0.18311 | -0.004578 | 0.004578 | -0.17853 | -0.1236 | -0.10071 | 0.013733 | 61.2671 | 61.5692 | 121.4447 | 121.4401 | -0.004578 | 121.5225 | 61.5875 | -0.1236 | 121.4401 | -0.004578 | 61.5875 | 121.4447 | 121.5225 | -121.6415 | -121.7468
433.3594 | 121.9254 | -61.2762 | 60.2783 | 0.069046 | 0.015182 | 0.0036849 | 0.013826 | 0.055027 | -0.012245 | 0.068184 | -61.4182 | 60.1364 | -61.409 | -61.4639 | 59.9579 | 0.013733 | -0.07782 | -0.14191 | 60.26 | -61.4548 | -0.13275 | -0.14191 | -0.14191 | -0.18768 | -0.32043 | -0.17853 | -0.01831 | -0.009155 | 61.1984 | 61.1343 | 121.2341 | 121.4127 | -0.14191 | 121.5363 | 61.29 | -0.17853 | 121.4127 | -0.14191 | 61.29 | 121.2341 | 121.5363 | -121.6873 | -121.7331
435.0312 | 121.8521 | -61.2671 | 60.347 | -0.22087 | 0.013473 | 0.0030441 | 0.0048534 | 0.051823 | -0.0075452 | 0.068611 | -61.2991 | 60.2554 | -61.2854 | -61.3449 | 60.0998 | 0.25635 | 0.23346 | 0.21515 | 60.3653 | -61.3998 | -0.01831 | -0.091553 | -0.032043 | -0.07782 | -0.24719 | -0.13275 | 0.01831 | -0.013733 | 61.5005 | 61.4822 | 121.3669 | 121.5225 | -0.032043 | 121.6324 | 61.5234 | -0.13275 | 121.5225 | -0.032043 | 61.5234 | 121.3669 | 121.6324 | -121.6324 | -121.7468
436.7188 | 121.9528 | -61.2625 | 60.2692 | 0.10719 | 0.015609 | 0.0056075 | 0.009126 | 0.055241 | -0.012245 | 0.066902 | -61.4273 | 60.1273 | -61.4273 | -61.4914 | 59.967 | 0.004578 | -0.13733 | -0.16937 | 60.2783 | -61.4822 | -0.16479 | -0.14191 | -0.16479 | -0.22888 | -0.30212 | -0.21973 | 0.009155 | 0 | 61.1252 | 61.0931 | 121.2296 | 121.3898 | -0.16479 | 121.5408 | 61.2671 | -0.21973 | 121.3898 | -0.16479 | 61.2671 | 121.2296 | 121.5408 | -121.6965 | -121.7514
438.4688 | 121.9025 | -61.2213 | 60.3516 | 0.14534 | 0.012191 | 0.0015487 | 0.0059216 | 0.051823 | -0.0092542 | 0.066048 | -61.322 | 60.1227 | -61.3083 | -61.3358 | 60.1089 | 0.14648 | -0.25177 | 0.045776 | 60.228 | -61.4182 | -0.086976 | -0.22888 | -0.10071 | -0.11444 | -0.24261 | -0.19684 | -0.1236 | -0.013732 | 60.9695 | 61.2671 | 121.3303 | 121.344 | -0.10071 | 121.4493 | 61.3678 | -0.19684 | 121.344 | -0.10071 | 61.3678 | 121.3303 | 121.4493 | -121.6599 | -121.7697
440.1719 | 121.9254 | -61.2534 | 60.3058 | 0.11482 | 0.012619 | 0.0045395 | 0.0095532 | 0.053532 | -0.010536 | 0.068184 | -61.4136 | 60.141 | -61.4044 | -61.4548 | 59.9945 | 0.027466 | -0.18768 | -0.1236 | 60.228 | -61.4594 | -0.15106 | -0.16479 | -0.16022 | -0.20142 | -0.31128 | -0.20599 | -0.07782 | -0.009155 | 61.0657 | 61.1298 | 121.2479 | 121.3943 | -0.16022 | 121.4813 | 61.2808 | -0.20599 | 121.3943 | -0.16022 | 61.2808 | 121.2479 | 121.4813 | -121.7102 | -121.7651
441.9062 | 121.9482 | -61.2671 | 60.2829 | 0.15297 | 0.016464 | 0.0021895 | 0.0095532 | 0.053532 | -0.0062634 | 0.069893 | -61.4456 | 60.1501 | -61.4044 | -61.4822 | 59.9716 | 0 | -0.15564 | -0.16022 | 60.2463 | -61.4777 | -0.13733 | -0.13275 | -0.17853 | -0.21515 | -0.31128 | -0.21057 | -0.036621 | -0.041199 | 61.1115 | 61.1069 | 121.2387 | 121.4172 | -0.17853 | 121.5134 | 61.2671 | -0.21057 | 121.4172 | -0.17853 | 61.2671 | 121.2387 | 121.5134 | -121.6873 | -121.7606
443.5781 | 121.8796 | -61.2167 | 60.3973 | 0.16823 | 0.014114 | 0.0096665 | 0.0048534 | 0.052677 | -0.009895 | 0.067757 | -61.3312 | 60.1135 | -61.3358 | -61.3449 | 60.0906 | 0.11902 | -0.31128 | 0.009155 | 60.2371 | -61.441 | -0.11902 | -0.28381 | -0.11444 | -0.12817 | -0.3067 | -0.2243 | -0.16022 | 0.004577 | 60.9055 | 61.2259 | 121.3074 | 121.3303 | -0.11444 | 121.4539 | 61.3358 | -0.2243 | 121.3303 | -0.11444 | 61.3358 | 121.3074 | 121.4539 | -121.7331 | -121.8384
445.3125 | 121.9116 | -61.1938 | 60.4019 | -0.091171 | 0.016891 | 0.0032577 | 0.0020764 | 0.050755 | -0.0077588 | 0.066475 | -61.2717 | 60.2097 | -61.2625 | -61.2762 | 60.1913 | 0.28839 | 0.041199 | 0.27008 | 60.3149 | -61.3449 | -0.068664 | -0.19226 | -0.077819 | -0.082397 | -0.21057 | -0.15106 | -0.086976 | -0.009155 | 61.235 | 61.4639 | 121.3852 | 121.4035 | -0.077819 | 121.5088 | 61.4822 | -0.15106 | 121.4035 | -0.077819 | 61.4822 | 121.3852 | 121.5088 | -121.6644 | -121.7468
446.9844 | 121.8292 | -61.2854 | 60.3104 | -0.19798 | 0.014755 | 0.0047531 | 0.012117 | 0.052677 | -0.01075 | 0.06733 | -61.3129 | 60.228 | -61.3037 | -61.3586 | 60.0861 | 0.22888 | 0.10529 | 0.11444 | 60.3424 | -61.3907 | -0.018311 | -0.082398 | -0.027466 | -0.073243 | -0.2243 | -0.10529 | 0.032043 | -0.009155 | 61.3907 | 61.3998 | 121.3715 | 121.5134 | -0.027466 | 121.6278 | 61.5143 | -0.10529 | 121.5134 | -0.027466 | 61.5143 | 121.3715 | 121.6278 | -121.6141 | -121.7011
448.7344 | 121.7972 | -61.3449 | 60.3012 | -0.075912 | 0.014114 | 0.0038985 | 0.010835 | 0.056095 | -0.010536 | 0.068398 | -61.3449 | 60.1822 | -61.3541 | -61.3632 | 60.0723 | 0.19684 | -0.022888 | 0.064087 | 60.2921 | -61.3998 | -0.009155 | -0.11902 | 0 | -0.01831 | -0.22888 | -0.054931 | -0.009155 | 0.009155 | 61.322 | 61.409 | 121.4172 | 121.5271 | 0 | 121.637 | 61.5417 | -0.054931 | 121.5271 | 0 | 61.5417 | 121.4172 | 121.637 | -121.6553 | -121.701
450.5 | 121.8567 | -61.2534 | 60.347 | -0.19035 | 0.016891 | 0.0030441 | 0.0072034 | 0.054386 | -0.010963 | 0.069252 | -61.3358 | 60.1913 | -61.3037 | -61.3678 | 60.0998 | 0.2655 | 0.27008 | 0.20599 | 60.3836 | -61.3678 | -0.050354 | -0.15564 | -0.082397 | -0.11444 | -0.24719 | -0.11444 | 0.036621 | -0.032043 | 61.5234 | 61.4594 | 121.3531 | 121.4447 | -0.082397 | 121.637 | 61.5189 | -0.11444 | 121.4447 | -0.082397 | 61.5189 | 121.3531 | 121.637 | -121.6507 | -121.7148
452.1719 | 121.9345 | -61.2946 | 60.26 | 0.099564 | 0.014114 | 0.00090794 | 0.010408 | 0.054173 | -0.01139 | 0.068611 | -61.4456 | 60.141 | -61.3953 | -61.4868 | 59.967 | 0.027466 | -0.12817 | -0.14191 | 60.2692 | -61.4273 | -0.10071 | -0.11902 | -0.15106 | -0.19226 | -0.29297 | -0.13275 | 0.009155 | -0.050354 | 61.1664 | 61.1526 | 121.2616 | 121.4355 | -0.15106 | 121.5637 | 61.322 | -0.13275 | 121.4355 | -0.15106 | 61.322 | 121.2616 | 121.5637 | -121.6553 | -121.6873
453.9062 | 121.8018 | -61.3266 | 60.3058 | -0.091171 | 0.014114 | 0.0015487 | 0.011689 | 0.053959 | -0.010963 | 0.067543 | -61.3358 | 60.1547 | -61.3586 | -61.3495 | 60.0906 | 0.19226 | -0.018311 | 0.068665 | 60.3241 | -61.4273 | -0.032044 | -0.15106 | -0.009155 | -0.022888 | -0.21515 | -0.10071 | 0.018311 | 0.022889 | 61.3083 | 61.3953 | 121.4172 | 121.4813 | -0.009155 | 121.6507 | 61.5189 | -0.10071 | 121.4813 | -0.009155 | 61.5189 | 121.4172 | 121.6507 | -121.6644 | -121.7331
455.6562 | 121.9116 | -61.2213 | 60.3653 | 0.091934 | 0.014969 | 0.00026694 | 0.0033582 | 0.053532 | -0.010109 | 0.06797 | -61.3129 | 60.1181 | -61.2991 | -61.3586 | 60.1181 | 0.13733 | -0.21515 | 0.045776 | 60.26 | -61.3907 | -0.07782 | -0.24719 | -0.091553 | -0.13733 | -0.24719 | -0.16937 | -0.10529 | -0.013733 | 61.0062 | 61.2671 | 121.3394 | 121.3394 | -0.091553 | 121.4813 | 61.3586 | -0.16937 | 121.3394 | -0.091553 | 61.3586 | 121.3394 | 121.4813 | -121.6644 | -121.756
457.4062 | 121.8613 | -61.2808 | 60.3516 | -0.17509 | 0.013687 | -0.00037386 | 0.0076306 | 0.051823 | -0.0090406 | 0.068825 | -61.3449 | 60.2509 | -61.3266 | -61.3586 | 60.0906 | 0.23804 | 0.18768 | 0.13733 | 60.347 | -61.3815 | -0.045776 | -0.10071 | -0.064087 | -0.07782 | -0.26093 | -0.10071 | -0.004577 | -0.018311 | 61.4685 | 61.4182 | 121.3715 | 121.5317 | -0.064087 | 121.6278 | 61.5189 | -0.10071 | 121.5317 | -0.064087 | 61.5189 | 121.3715 | 121.6278 | -121.6782 | -121.7331
459.1562 | 121.9666 | -61.1801 | 60.3928 | 0.00038159 | 0.013473 | 0.0019759 | 0.0050672 | 0.052037 | -0.0058362 | 0.066475 | -61.3129 | 60.1959 | -61.2854 | -61.3541 | 60.1044 | 0.1831 | -0.032043 | 0.10986 | 60.2966 | -61.3998 | -0.10529 | -0.19684 | -0.13275 | -0.17395 | -0.28839 | -0.21973 | -0.09613 | -0.027466 | 61.1481 | 61.29 | 121.2845 | 121.376 | -0.13275 | 121.4767 | 61.3632 | -0.21973 | 121.376 | -0.13275 | 61.3632 | 121.2845 | 121.4767 | -121.6782 | -121.7926
460.8438 | 121.8201 | -61.3037 | 60.3287 | -0.060654 | 0.014328 | 0.0011215 | 0.011049 | 0.055668 | -0.010109 | 0.06733 | -61.3403 | 60.1639 | -61.3495 | -61.3815 | 60.0494 | 0.15106 | -0.041199 | 0.013733 | 60.2829 | -61.4136 | -0.045776 | -0.16479 | -0.036621 | -0.07782 | -0.27924 | -0.10986 | -0.045776 | 0.009155 | 61.2625 | 61.3174 | 121.3531 | 121.4676 | -0.036621 | 121.5866 | 61.4548 | -0.10986 | 121.4676 | -0.036621 | 61.4548 | 121.3531 | 121.5866 | -121.6782 | -121.7422
462.5938 | 121.9391 | -61.2671 | 60.2875 | 0.10719 | 0.014114 | 0.0028305 | 0.010621 | 0.053318 | -0.011818 | 0.065834 | -61.4502 | 60.141 | -61.4044 | -61.496 | 59.9854 | 0.013733 | -0.11902 | -0.16479 | 60.2509 | -61.4731 | -0.13733 | -0.14648 | -0.1831 | -0.22888 | -0.30212 | -0.20599 | -0.036622 | -0.045776 | 61.1481 | 61.1023 | 121.2524 | 121.4081 | -0.1831 | 121.5179 | 61.2808 | -0.20599 | 121.4081 | -0.1831 | 61.2808 | 121.2524 | 121.5179 | -121.6919 | -121.7606
464.2656 | 121.8567 | -61.203 | 60.4294 | -0.15221 | 0.010696 | 0.0021895 | 0.0031446 | 0.052037 | -0.0094678 | 0.065193 | -61.235 | 60.2554 | -61.2305 | -61.2579 | 60.2005 | 0.3479 | 0.022888 | 0.31128 | 60.3012 | -61.3815 | -0.027466 | -0.17395 | -0.032043 | -0.054932 | -0.22888 | -0.17853 | -0.12817 | -0.004577 | 61.2259 | 61.5143 | 121.4035 | 121.4584 | -0.032043 | 121.5042 | 61.5509 | -0.17853 | 121.4584 | -0.032043 | 61.5509 | 121.4035 | 121.5042 | -121.6599 | -121.8109
466.0156 | 121.8658 | -61.3083 | 60.2966 | 0.053787 | 0.014114 | -0.0010147 | 0.010408 | 0.055668 | -0.010322 | 0.067757 | -61.3953 | 60.1364 | -61.4044 | -61.4594 | 59.9762 | 0.064087 | -0.07782 | -0.09613 | 60.3058 | -61.4639 | -0.09613 | -0.16022 | -0.086975 | -0.15106 | -0.32043 | -0.15564 | 0.009155 | 0.009155 | 61.2305 | 61.2122 | 121.2845 | 121.4447 | -0.086975 | 121.6141 | 61.3724 | -0.15564 | 121.4447 | -0.086975 | 61.3724 | 121.2845 | 121.6141 | -121.701 | -121.7606
467.7031 | 121.9437 | -61.1618 | 60.379 | 0.00038159 | 0.014541 | -0.00080106 | 0.0037854 | 0.052464 | -0.0083996 | 0.06733 | -61.3266 | 60.173 | -61.3129 | -61.3586 | 60.1227 | 0.20142 | 0 | 0.13733 | 60.3012 | -61.3586 | -0.15106 | -0.20599 | -0.1648 | -0.19684 | -0.25635 | -0.19684 | -0.07782 | -0.013733 | 61.1618 | 61.2991 | 121.2845 | 121.3348 | -0.1648 | 121.463 | 61.3632 | -0.19684 | 121.3348 | -0.1648 | 61.3632 | 121.2845 | 121.463 | -121.6919 | -121.7377
469.4531 | 121.9574 | -61.2762 | 60.2875 | 0.12245 | 0.014969 | 0.0028305 | 0.010835 | 0.054814 | -0.010322 | 0.068611 | -61.4365 | 60.1593 | -61.3953 | -61.4868 | 59.9487 | 0.013733 | -0.12817 | -0.16479 | 60.2829 | -61.4548 | -0.11902 | -0.12817 | -0.16022 | -0.21057 | -0.33875 | -0.17853 | -0.004578 | -0.041198 | 61.1481 | 61.1115 | 121.225 | 121.4355 | -0.16022 | 121.5591 | 61.29 | -0.17853 | 121.4355 | -0.16022 | 61.29 | 121.225 | 121.5591 | -121.6827 | -121.7422
471.2031 | 121.907 | -61.2259 | 60.3561 | 0.11482 | 0.013687 | 0.0066757 | 0.0078442 | 0.053532 | -0.010963 | 0.06797 | -61.3129 | 60.0998 | -61.3403 | -61.3586 | 60.0861 | 0.1236 | -0.27466 | -0.009155 | 60.2325 | -61.4273 | -0.11444 | -0.25635 | -0.086975 | -0.13275 | -0.27008 | -0.20142 | -0.1236 | 0.027466 | 60.9512 | 61.2167 | 121.312 | 121.3257 | -0.086975 | 121.4584 | 61.3495 | -0.20142 | 121.3257 | -0.086975 | 61.3495 | 121.312 | 121.4584 | -121.6965 | -121.7834
472.9375 | 121.9345 | -61.2625 | 60.2966 | 0.12245 | 0.014541 | 0.0041123 | 0.0099804 | 0.054173 | -0.01075 | 0.068398 | -61.4044 | 60.1593 | -61.3907 | -61.4456 | 59.9899 | 0.036621 | -0.20142 | -0.12817 | 60.26 | -61.4273 | -0.12817 | -0.13733 | -0.14191 | -0.18311 | -0.3067 | -0.16479 | -0.036621 | -0.013733 | 61.0611 | 61.1343 | 121.2524 | 121.4218 | -0.14191 | 121.5225 | 61.2991 | -0.16479 | 121.4218 | -0.14191 | 61.2991 | 121.2524 | 121.5225 | -121.6873 | -121.7239
474.6719 | 121.9208 | -61.29 | 60.3104 | 0.053787 | 0.012191 | 0.0064621 | 0.010621 | 0.054386 | -0.013527 | 0.066902 | -61.4136 | 60.141 | -61.3998 | -61.4639 | 59.9854 | 0.045776 | -0.054932 | -0.10529 | 60.3104 | -61.409 | -0.10986 | -0.16937 | -0.1236 | -0.17395 | -0.32501 | -0.11902 | 0 | -0.013733 | 61.235 | 61.1847 | 121.2753 | 121.431 | -0.1236 | 121.6003 | 61.3358 | -0.11902 | 121.431 | -0.1236 | 61.3358 | 121.2753 | 121.6003 | -121.7102 | -121.7194
476.3594 | 121.8567 | -61.2579 | 60.347 | -0.23613 | 0.016037 | 0.0028305 | 0.0063488 | 0.053105 | -0.0077588 | 0.067116 | -61.3312 | 60.2646 | -61.3037 | -61.3586 | 60.0952 | 0.26093 | 0.27008 | 0.19684 | 60.3607 | -61.3724 | -0.045776 | -0.082398 | -0.073242 | -0.10071 | -0.25177 | -0.11444 | 0.013733 | -0.027466 | 61.528 | 61.4548 | 121.3531 | 121.5225 | -0.073242 | 121.6187 | 61.5189 | -0.11444 | 121.5225 | -0.073242 | 61.5189 | 121.3531 | 121.6187 | -121.6507 | -121.7194
478.1094 | 121.8109 | -61.322 | 60.3287 | -0.11406 | 0.012832 | 0.0038985 | 0.0095532 | 0.052464 | -0.008827 | 0.069039 | -61.3266 | 60.1868 | -61.3403 | -61.3541 | 60.0906 | 0.21515 | 0.032043 | 0.10986 | 60.2829 | -61.4319 | -0.018311 | -0.14191 | -0.004578 | -0.032044 | -0.23804 | -0.10986 | -0.045776 | 0.013733 | 61.3541 | 61.4319 | 121.4127 | 121.5088 | -0.004578 | 121.6049 | 61.5372 | -0.10986 | 121.5088 | -0.004578 | 61.5372 | 121.4127 | 121.6049 | -121.669 | -121.7606
479.8594 | 121.9528 | -61.1755 | 60.3928 | -0.0072479 | 0.015182 | 0.0019759 | 0.0027172 | 0.052677 | -0.008186 | 0.068611 | -61.3358 | 60.2051 | -61.2534 | -61.3541 | 60.1135 | 0.18768 | -0.013733 | 0.12817 | 60.2829 | -61.3953 | -0.07782 | -0.18768 | -0.16022 | -0.17853 | -0.27924 | -0.21973 | -0.10986 | -0.082397 | 61.1618 | 61.3037 | 121.2891 | 121.3806 | -0.16022 | 121.4584 | 61.3632 | -0.21973 | 121.3806 | -0.16022 | 61.3632 | 121.2891 | 121.4584 | -121.6461 | -121.788
481.5469 | 121.9254 | -61.2579 | 60.2875 | 0.11482 | 0.014328 | 0.0058211 | 0.012544 | 0.053105 | -0.009895 | 0.066902 | -61.4548 | 60.1547 | -61.4136 | -61.4685 | 59.9579 | 0.004578 | -0.12817 | -0.15564 | 60.2737 | -61.441 | -0.15564 | -0.13275 | -0.19684 | -0.21057 | -0.32959 | -0.1831 | -0.013733 | -0.041199 | 61.1298 | 61.1023 | 121.2158 | 121.4127 | -0.19684 | 121.5317 | 61.2625 | -0.1831 | 121.4127 | -0.19684 | 61.2625 | 121.2158 | 121.5317 | -121.701 | -121.7285
483.2969 | 121.8338 | -61.3083 | 60.3104 | -0.037765 | 0.01625 | 0.00026694 | 0.011476 | 0.054814 | -0.011818 | 0.067116 | -61.3449 | 60.1547 | -61.3678 | -61.3861 | 60.0449 | 0.13733 | -0.045776 | 0.018311 | 60.2966 | -61.3953 | -0.059509 | -0.15564 | -0.036621 | -0.077819 | -0.2655 | -0.086975 | -0.013733 | 0.022888 | 61.2625 | 61.3266 | 121.3531 | 121.463 | -0.036621 | 121.6049 | 61.4456 | -0.086975 | 121.463 | -0.036621 | 61.4456 | 121.3531 | 121.6049 | -121.6782 | -121.7056
485.0469 | 121.8613 | -61.2488 | 60.3836 | -0.25139 | 0.017318 | 0.0015487 | 0.0050672 | 0.052464 | -0.0092542 | 0.066048 | -61.2488 | 60.2554 | -61.2534 | -61.3037 | 60.1685 | 0.32959 | 0.20599 | 0.27466 | 60.3653 | -61.3815 | -0.004578 | -0.12817 | 0 | -0.054932 | -0.21515 | -0.13275 | -0.018311 | 0.004578 | 61.4548 | 61.5234 | 121.4172 | 121.5042 | 0 | 121.6141 | 61.5784 | -0.13275 | 121.5042 | 0 | 61.5784 | 121.4172 | 121.6141 | -121.637 | -121.7651
486.7344 | 121.9437 | -61.1618 | 60.4019 | 0.01564 | 0.016464 | -0.0033647 | 0.0033582 | 0.051609 | -0.0075452 | 0.064766 | -61.3266 | 60.2142 | -61.29 | -61.3495 | 60.1227 | 0.20599 | -0.004578 | 0.15106 | 60.3104 | -61.3998 | -0.12817 | -0.18768 | -0.1648 | -0.18768 | -0.27924 | -0.23804 | -0.091553 | -0.036621 | 61.1572 | 61.3129 | 121.2845 | 121.376 | -0.1648 | 121.4722 | 61.3678 | -0.23804 | 121.376 | -0.1648 | 61.3678 | 121.2845 | 121.4722 | -121.6919 | -121.8018
488.4844 | 121.8109 | -61.2396 | 60.434 | -0.14458 | 0.013687 | 0.0030441 | 0.0048534 | 0.051823 | -0.0079724 | 0.066902 | -61.2167 | 60.2188 | -61.2488 | -61.2167 | 60.2234 | 0.35706 | 0.073242 | 0.36163 | 60.3058 | -61.3586 | -0.009155 | -0.21515 | 0.022888 | 0.022888 | -0.21057 | -0.11902 | -0.12817 | 0.032043 | 61.3129 | 61.6013 | 121.463 | 121.4584 | 0.022888 | 121.5454 | 61.5967 | -0.11902 | 121.4584 | 0.022888 | 61.5967 | 121.463 | 121.5454 | -121.6827 | -121.7926
490.25 | 121.9345 | -61.1938 | 60.4202 | 0.10719 | 0.0139 | 0.0030441 | 0.003999 | 0.050541 | -0.0075452 | 0.06797 | -61.3174 | 60.1501 | -61.3174 | -61.3541 | 60.1089 | 0.16479 | -0.11902 | 0.082397 | 60.2737 | -61.4044 | -0.1236 | -0.27008 | -0.1236 | -0.16022 | -0.31128 | -0.21057 | -0.14648 | 0 | 61.0748 | 61.2762 | 121.3028 | 121.344 | -0.1236 | 121.4676 | 61.3586 | -0.21057 | 121.344 | -0.1236 | 61.3586 | 121.3028 | 121.4676 | -121.7377 | -121.8246
492 | 121.8613 | -61.2076 | 60.4248 | -0.12169 | 0.015396 | 0.0017623 | 0.0052808 | 0.051609 | -0.0094678 | 0.065621 | -61.2305 | 60.2097 | -61.2442 | -61.2442 | 60.1913 | 0.33417 | 0.022888 | 0.31128 | 60.3104 | -61.3678 | -0.036621 | -0.21515 | -0.022888 | -0.036621 | -0.23346 | -0.16022 | -0.11444 | 0.013733 | 61.2305 | 61.5189 | 121.3989 | 121.4172 | -0.022888 | 121.5179 | 61.5417 | -0.16022 | 121.4172 | -0.022888 | 61.5417 | 121.3989 | 121.5179 | -121.669 | -121.7926
493.75 | 121.8384 | -61.2122 | 60.3973 | -0.13695 | 0.015396 | 0.0032577 | 0.0059216 | 0.051396 | -0.0077588 | 0.066048 | -61.235 | 60.228 | -61.2762 | -61.2442 | 60.1959 | 0.33417 | 0.018311 | 0.32959 | 60.3241 | -61.3541 | -0.064087 | -0.16937 | -0.022888 | -0.032044 | -0.20142 | -0.14191 | -0.073242 | 0.041199 | 61.2305 | 61.5417 | 121.4081 | 121.4401 | -0.022888 | 121.5363 | 61.5463 | -0.14191 | 121.4401 | -0.022888 | 61.5463 | 121.4081 | 121.5363 | -121.6736 | -121.7514
495.5 | 121.8109 | -61.3449 | 60.3058 | -0.083542 | 0.016891 | 0.0013351 | 0.012971 | 0.053532 | -0.010322 | 0.069679 | -61.3266 | 60.1547 | -61.3586 | -61.3678 | 60.0723 | 0.17395 | -0.027466 | 0.041199 | 60.3104 | -61.4044 | -0.013733 | -0.15106 | 0.018311 | -0.022888 | -0.23346 | -0.059509 | 0.004578 | 0.032044 | 61.3174 | 61.3861 | 121.4172 | 121.4996 | 0.018311 | 121.6553 | 61.5189 | -0.059509 | 121.4996 | 0.018311 | 61.5189 | 121.4172 | 121.6553 | -121.6644 | -121.7102
497.1875 | 121.8658 | -61.2671 | 60.347 | -0.23613 | 0.014755 | -0.0022965 | 0.0072034 | 0.052037 | -0.0094678 | 0.066689 | -61.3358 | 60.26 | -61.2991 | -61.3541 | 60.1044 | 0.24261 | 0.26093 | 0.17395 | 60.379 | -61.3678 | -0.032043 | -0.086975 | -0.068664 | -0.086975 | -0.24261 | -0.10071 | 0.032043 | -0.036621 | 61.528 | 61.441 | 121.3715 | 121.5271 | -0.068664 | 121.6461 | 61.5097 | -0.10071 | 121.5271 | -0.068664 | 61.5097 | 121.3715 | 121.6461 | -121.6461 | -121.7148
498.9219 | 121.8109 | -61.2213 | 60.3973 | -0.18272 | 0.0139 | 0.0013351 | 0.0050672 | 0.050755 | -0.008186 | 0.066262 | -61.2442 | 60.228 | -61.2442 | -61.235 | 60.2097 | 0.36621 | 0.11444 | 0.33875 | 60.3104 | -61.3815 | -0.022889 | -0.16937 | -0.022889 | -0.013733 | -0.18768 | -0.16022 | -0.086975 | 0 | 61.3358 | 61.5601 | 121.431 | 121.4493 | -0.022889 | 121.5317 | 61.5875 | -0.16022 | 121.4493 | -0.022889 | 61.5875 | 121.431 | 121.5317 | -121.6415 | -121.7789
500.6719 | 121.9528 | -61.1847 | 60.3699 | 0.00038159 | 0.014114 | 0.0024033 | 0.0065624 | 0.053532 | -0.0083996 | 0.066902 | -61.322 | 60.2097 | -61.2808 | -61.3495 | 60.1273 | 0.19226 | -0.013733 | 0.15564 | 60.2966 | -61.3907 | -0.096131 | -0.16022 | -0.13733 | -0.1648 | -0.24262 | -0.20599 | -0.073242 | -0.041198 | 61.171 | 61.3403 | 121.3119 | 121.3943 | -0.13733 | 121.4813 | 61.377 | -0.20599 | 121.3943 | -0.13733 | 61.377 | 121.3119 | 121.4813 | -121.6507 | -121.7606
502.3594 | 121.8887 | -61.2396 | 60.3561 | 0.15297 | 0.015396 | 0.0030441 | 0.0089124 | 0.051609 | -0.009895 | 0.068184 | -61.3174 | 60.1364 | -61.3678 | -61.3266 | 60.1044 | 0.14191 | -0.27924 | 0.050354 | 60.2325 | -61.4273 | -0.12817 | -0.21973 | -0.07782 | -0.086975 | -0.25177 | -0.18768 | -0.1236 | 0.050354 | 60.9604 | 61.29 | 121.344 | 121.376 | -0.07782 | 121.4722 | 61.3815 | -0.18768 | 121.376 | -0.07782 | 61.3815 | 121.344 | 121.4722 | -121.7239 | -121.7834
504.125 | 121.7926 | -61.3037 | 60.3333 | -0.10643 | 0.01326 | 0.0021895 | 0.013398 | 0.051609 | -0.01075 | 0.069252 | -61.3312 | 60.1822 | -61.3586 | -61.3449 | 60.0769 | 0.21973 | 0.045776 | 0.10529 | 60.2875 | -61.3953 | -0.054932 | -0.15106 | -0.027466 | -0.041199 | -0.25635 | -0.091553 | -0.045776 | 0.027466 | 61.3495 | 61.409 | 121.3806 | 121.4859 | -0.027466 | 121.5912 | 61.5234 | -0.091553 | 121.4859 | -0.027466 | 61.5234 | 121.3806 | 121.5912 | -121.6919 | -121.7285
505.8125 | 121.9025 | -61.2259 | 60.3607 | 0.14534 | 0.011764 | 5.3338e-05 | 0.0065624 | 0.052677 | -0.0090406 | 0.068184 | -61.3083 | 60.1364 | -61.3632 | -61.3358 | 60.1089 | 0.13275 | -0.27466 | 0.032043 | 60.2234 | -61.4365 | -0.13733 | -0.2243 | -0.082398 | -0.10986 | -0.25177 | -0.21057 | -0.13733 | 0.054931 | 60.9512 | 61.2579 | 121.3348 | 121.3623 | -0.082398 | 121.4493 | 61.3586 | -0.21057 | 121.3623 | -0.082398 | 61.3586 | 121.3348 | 121.4493 | -121.7239 | -121.7972
507.5625 | 121.8109 | -61.3403 | 60.3287 | -0.083542 | 0.013473 | 0.00090794 | 0.011689 | 0.052677 | -0.011604 | 0.06797 | -61.3312 | 60.1685 | -61.3678 | -61.3449 | 60.0815 | 0.19684 | -0.027466 | 0.082397 | 60.2829 | -61.4044 | -0.027466 | -0.16022 | 0.009155 | -0.004578 | -0.24719 | -0.064087 | -0.045776 | 0.036621 | 61.3129 | 61.4227 | 121.4218 | 121.5088 | 0.009155 | 121.6232 | 61.5372 | -0.064087 | 121.5088 | 0.009155 | 61.5372 | 121.4218 | 121.6232 | -121.6965 | -121.7331
509.2344 | 121.962 | -61.1618 | 60.3882 | 0.02327 | 0.013473 | 0.0019759 | 0.0031446 | 0.053746 | -0.0077588 | 0.06733 | -61.3266 | 60.2005 | -61.2808 | -61.3586 | 60.1181 | 0.19684 | -0.009155 | 0.12817 | 60.2875 | -61.4044 | -0.11902 | -0.18768 | -0.1648 | -0.19684 | -0.27008 | -0.24262 | -0.10071 | -0.045776 | 61.1526 | 61.29 | 121.2799 | 121.3623 | -0.1648 | 121.4493 | 61.3586 | -0.24262 | 121.3623 | -0.1648 | 61.3586 | 121.2799 | 121.4493 | -121.669 | -121.7926
510.9844 | 121.8475 | -61.2579 | 60.3699 | -0.23613 | 0.011337 | 0.0024033 | 0.0078442 | 0.051823 | -0.010109 | 0.065834 | -61.3495 | 60.228 | -61.3174 | -61.3541 | 60.1181 | 0.2655 | 0.25635 | 0.21515 | 60.3745 | -61.3724 | -0.059509 | -0.14191 | -0.091552 | -0.09613 | -0.25177 | -0.11444 | 0.004578 | -0.032043 | 61.5143 | 61.4731 | 121.376 | 121.4859 | -0.091552 | 121.6324 | 61.5234 | -0.11444 | 121.4859 | -0.091552 | 61.5234 | 121.376 | 121.6324 | -121.6873 | -121.7422
512.75 | 121.8155 | -61.2305 | 60.4111 | -0.17509 | 0.0139 | -0.0014419 | 0.007417 | 0.050968 | -0.009895 | 0.066262 | -61.235 | 60.2051 | -61.2442 | -61.235 | 60.2142 | 0.36163 | 0.10071 | 0.33875 | 60.3287 | -61.3586 | -0.013733 | -0.20599 | -0.004577 | -0.004577 | -0.19684 | -0.12817 | -0.082398 | 0.009156 | 61.3312 | 61.5692 | 121.4447 | 121.4355 | -0.004577 | 121.5591 | 61.5921 | -0.12817 | 121.4355 | -0.004577 | 61.5921 | 121.4447 | 121.5591 | -121.6553 | -121.7697
514.4375 | 121.8292 | -61.3174 | 60.3104 | -0.19798 | 0.014541 | 0.0024033 | 0.013185 | 0.050968 | -0.011818 | 0.06733 | -61.3266 | 60.2234 | -61.3541 | -61.3495 | 60.0815 | 0.2243 | 0.10986 | 0.12817 | 60.3607 | -61.3861 | -0.036621 | -0.086975 | -0.009155 | -0.032043 | -0.22888 | -0.068664 | 0.050354 | 0.027466 | 61.4273 | 61.4456 | 121.3989 | 121.5408 | -0.009155 | 121.6782 | 61.5417 | -0.068664 | 121.5408 | -0.009155 | 61.5417 | 121.3989 | 121.6782 | -121.6644 | -121.6965
516.1875 | 121.8658 | -61.3037 | 60.2737 | 0.02327 | 0.016464 | 0.0030441 | 0.011903 | 0.054173 | -0.011818 | 0.066475 | -61.3998 | 60.1547 | -61.3998 | -61.4456 | 59.9945 | 0.054932 | -0.064087 | -0.086975 | 60.2783 | -61.4731 | -0.09613 | -0.11902 | -0.09613 | -0.14191 | -0.27924 | -0.16937 | 0.004577 | 0 | 61.2396 | 61.2167 | 121.2982 | 121.4584 | -0.09613 | 121.582 | 61.3586 | -0.16937 | 121.4584 | -0.09613 | 61.3586 | 121.2982 | 121.582 | -121.6736 | -121.7468
517.9375 | 121.9391 | -61.2579 | 60.2692 | 0.13008 | 0.014541 | 0.0036849 | 0.010621 | 0.055027 | -0.0092542 | 0.067116 | -61.4273 | 60.1639 | -61.3861 | -61.4594 | 59.9991 | 0.022888 | -0.13733 | -0.13733 | 60.2921 | -61.4548 | -0.12817 | -0.10529 | -0.16937 | -0.20142 | -0.27008 | -0.19684 | 0.022888 | -0.041199 | 61.1206 | 61.1206 | 121.257 | 121.4218 | -0.16937 | 121.55 | 61.2808 | -0.19684 | 121.4218 | -0.16937 | 61.2808 | 121.257 | 121.55 | -121.6553 | -121.7239
519.6875 | 121.8613 | -61.2808 | 60.3607 | -0.23613 | 0.016037 | 0.0034713 | 0.007417 | 0.050328 | -0.008186 | 0.067116 | -61.3312 | 60.2737 | -61.2671 | -61.3586 | 60.1044 | 0.2655 | 0.27466 | 0.20142 | 60.3928 | -61.3632 | 0.013733 | -0.086975 | -0.050354 | -0.07782 | -0.25635 | -0.082397 | 0.032043 | -0.064087 | 61.5555 | 61.4822 | 121.3852 | 121.5546 | -0.050354 | 121.6736 | 61.5463 | -0.082397 | 121.5546 | -0.050354 | 61.5463 | 121.3852 | 121.6736 | -121.6278 | -121.7239
521.375 | 121.9299 | -61.2213 | 60.379 | 0.10719 | 0.015182 | 0.00026694 | 0.0037854 | 0.052891 | -0.0083996 | 0.064766 | -61.322 | 60.1456 | -61.3266 | -61.3495 | 60.1135 | 0.15106 | -0.19226 | 0.068665 | 60.2509 | -61.409 | -0.10529 | -0.23346 | -0.10071 | -0.12817 | -0.2655 | -0.18768 | -0.12817 | 0.004578 | 61.0291 | 61.29 | 121.3348 | 121.3669 | -0.10071 | 121.4722 | 61.3724 | -0.18768 | 121.3669 | -0.10071 | 61.3724 | 121.3348 | 121.4722 | -121.7056 | -121.788
523.125 | 121.8658 | -61.2762 | 60.347 | -0.22087 | 0.016678 | 0.0024033 | 0.0080578 | 0.052677 | -0.010109 | 0.067757 | -61.3403 | 60.2737 | -61.3129 | -61.3724 | 60.0861 | 0.24261 | 0.22888 | 0.15564 | 60.3836 | -61.3586 | -0.036621 | -0.073242 | -0.064087 | -0.09613 | -0.26092 | -0.082398 | 0.036621 | -0.027466 | 61.5051 | 61.4319 | 121.3623 | 121.55 | -0.064087 | 121.6599 | 61.5189 | -0.082398 | 121.55 | -0.064087 | 61.5189 | 121.3623 | 121.6599 | -121.6599 | -121.7056
524.8125 | 121.9528 | -61.171 | 60.4065 | 0.0080111 | 0.014541 | 0.0024033 | 0.0044262 | 0.054386 | -0.0092542 | 0.068184 | -61.3266 | 60.1959 | -61.2671 | -61.3632 | 60.1227 | 0.20142 | -0.009155 | 0.14648 | 60.3424 | -61.3586 | -0.096131 | -0.21057 | -0.15564 | -0.19226 | -0.28381 | -0.18768 | -0.064087 | -0.059509 | 61.1618 | 61.3174 | 121.2936 | 121.3669 | -0.15564 | 121.5134 | 61.3724 | -0.18768 | 121.3669 | -0.15564 | 61.3724 | 121.2936 | 121.5134 | -121.6736 | -121.7651
526.5625 | 121.8018 | -61.2991 | 60.3195 | -0.068283 | 0.016678 | 0.0019759 | 0.011903 | 0.0546 | -0.012672 | 0.067757 | -61.3312 | 60.1639 | -61.3541 | -61.3678 | 60.0586 | 0.16937 | -0.032043 | 0.045776 | 60.2921 | -61.3998 | -0.054932 | -0.15564 | -0.032044 | -0.068665 | -0.26093 | -0.10071 | -0.027466 | 0.022888 | 61.2671 | 61.3449 | 121.3577 | 121.463 | -0.032044 | 121.5912 | 61.4685 | -0.10071 | 121.463 | -0.032044 | 61.4685 | 121.3577 | 121.5912 | -121.6736 | -121.7194
528.2969 | 121.9345 | -61.2717 | 60.26 | 0.11482 | 0.013473 | 0.0051803 | 0.0099804 | 0.053746 | -0.010536 | 0.066902 | -61.4273 | 60.1456 | -61.3998 | -61.4639 | 59.9899 | 0.036621 | -0.13733 | -0.11902 | 60.3012 | -61.4731 | -0.12817 | -0.11444 | -0.15564 | -0.19226 | -0.27008 | -0.20142 | 0.041198 | -0.027466 | 61.1343 | 61.1526 | 121.2616 | 121.4172 | -0.15564 | 121.5729 | 61.3083 | -0.20142 | 121.4172 | -0.15564 | 61.3083 | 121.2616 | 121.5729 | -121.6599 | -121.7331
529.9688 | 121.8292 | -61.2305 | 60.4431 | -0.16747 | 0.012619 | 0.0028305 | 0.00229 | 0.051823 | -0.0086132 | 0.066048 | -61.1984 | 60.2371 | -61.235 | -61.2396 | 60.228 | 0.37994 | 0.091553 | 0.36621 | 60.3287 | -61.3174 | -0.004577 | -0.20599 | 0.032044 | -0.009155 | -0.21515 | -0.086975 | -0.11444 | 0.036621 | 61.322 | 61.5967 | 121.4584 | 121.4676 | 0.032044 | 121.5591 | 61.6104 | -0.086975 | 121.4676 | 0.032044 | 61.6104 | 121.4584 | 121.5591 | -121.6782 | -121.7606
531.7188 | 121.8979 | -61.2259 | 60.3516 | 0.16823 | 0.015823 | 0.0041123 | 0.0054944 | 0.052891 | -0.0096814 | 0.06498 | -61.3266 | 60.1181 | -61.3495 | -61.3449 | 60.0952 | 0.14648 | -0.27924 | 0.041199 | 60.2554 | -61.3998 | -0.1236 | -0.23346 | -0.10071 | -0.11902 | -0.25635 | -0.17395 | -0.09613 | 0.022888 | 60.9467 | 61.2671 | 121.3211 | 121.344 | -0.10071 | 121.4813 | 61.3724 | -0.17395 | 121.344 | -0.10071 | 61.3724 | 121.3211 | 121.4813 | -121.701 | -121.7514
533.4531 | 121.9254 | -61.3037 | 60.2829 | 0.076676 | 0.013473 | 0.0058211 | 0.010835 | 0.053746 | -0.010322 | 0.06733 | -61.4319 | 60.1547 | -61.4044 | -61.4822 | 59.9579 | 0.022888 | -0.073242 | -0.14191 | 60.2829 | -61.4685 | -0.10071 | -0.12817 | -0.12817 | -0.17853 | -0.32501 | -0.16479 | 0 | -0.027466 | 61.2305 | 61.1618 | 121.2616 | 121.4584 | -0.12817 | 121.5866 | 61.3266 | -0.16479 | 121.4584 | -0.12817 | 61.3266 | 121.2616 | 121.5866 | -121.6873 | -121.7514
535.2031 | 121.8658 | -61.2671 | 60.347 | -0.2285 | 0.013473 | 0.0056075 | 0.0067762 | 0.050755 | -0.009895 | 0.066902 | -61.3358 | 60.2875 | -61.2991 | -61.3541 | 60.1089 | 0.26093 | 0.27008 | 0.1831 | 60.3653 | -61.3861 | -0.032043 | -0.059509 | -0.068664 | -0.086975 | -0.23804 | -0.11902 | 0.01831 | -0.036621 | 61.5372 | 61.4502 | 121.376 | 121.5546 | -0.068664 | 121.6324 | 61.528 | -0.11902 | 121.5546 | -0.068664 | 61.528 | 121.376 | 121.6324 | -121.6461 | -121.7331
536.8906 | 121.9162 | -61.1847 | 60.3973 | 0.13008 | 0.015182 | 0.0019759 | 0.0050672 | 0.051182 | -0.006477 | 0.069039 | -61.3449 | 60.1456 | -61.3312 | -61.3632 | 60.0952 | 0.14648 | -0.15564 | 0.082397 | 60.2554 | -61.409 | -0.14648 | -0.25177 | -0.16022 | -0.17853 | -0.30212 | -0.22431 | -0.14191 | -0.013733 | 61.0291 | 61.2671 | 121.2799 | 121.3303 | -0.16022 | 121.4401 | 61.3312 | -0.22431 | 121.3303 | -0.16022 | 61.3312 | 121.2799 | 121.4401 | -121.7285 | -121.8063
538.6406 | 121.9437 | -61.1847 | 60.4156 | -0.030136 | 0.012619 | -0.0018693 | 0.0046398 | 0.049046 | -0.008186 | 0.06733 | -61.3266 | 60.2142 | -61.3174 | -61.3495 | 60.1273 | 0.21973 | -0.004578 | 0.1831 | 60.3058 | -61.377 | -0.13275 | -0.20142 | -0.14191 | -0.1648 | -0.28839 | -0.19226 | -0.10986 | -0.009155 | 61.1801 | 61.3678 | 121.3119 | 121.3989 | -0.14191 | 121.4905 | 61.4044 | -0.19226 | 121.3989 | -0.14191 | 61.4044 | 121.3119 | 121.4905 | -121.7331 | -121.7926
540.3906 | 121.8979 | -61.1938 | 60.4156 | -0.098801 | 0.014755 | -0.0031509 | 0.0042126 | 0.051609 | -0.0079724 | 0.068184 | -61.2396 | 60.2371 | -61.2671 | -61.2671 | 60.1913 | 0.33417 | 0.036621 | 0.3067 | 60.3058 | -61.3541 | -0.073242 | -0.17853 | -0.045776 | -0.073242 | -0.2243 | -0.16022 | -0.10986 | 0.027466 | 61.2305 | 61.5006 | 121.3852 | 121.431 | -0.045776 | 121.4996 | 61.528 | -0.16022 | 121.431 | -0.045776 | 61.528 | 121.3852 | 121.4996 | -121.6827 | -121.7697
542.0938 | 121.9528 | -61.1938 | 60.3928 | -0.0072479 | 0.013046 | -0.0037919 | 0.0054944 | 0.052037 | -0.0092542 | 0.066689 | -61.322 | 60.2051 | -61.29 | -61.3449 | 60.1181 | 0.2243 | -0.004578 | 0.16479 | 60.3149 | -61.3907 | -0.09613 | -0.18768 | -0.12817 | -0.15106 | -0.27466 | -0.19684 | -0.07782 | -0.032043 | 61.1893 | 61.3586 | 121.312 | 121.3989 | -0.12817 | 121.5088 | 61.4182 | -0.19684 | 121.3989 | -0.12817 | 61.4182 | 121.312 | 121.5088 | -121.6827 | -121.7834
543.8438 | 121.8201 | -61.2167 | 60.3928 | -0.17509 | 0.013046 | 0.0017623 | 0.0080578 | 0.050968 | -0.0086132 | 0.066048 | -61.2488 | 60.2051 | -61.2625 | -61.2442 | 60.2005 | 0.36621 | 0.11902 | 0.33875 | 60.3195 | -61.3541 | -0.045776 | -0.18768 | -0.032043 | -0.027466 | -0.19226 | -0.13733 | -0.073242 | 0.013733 | 61.3358 | 61.5555 | 121.4172 | 121.4218 | -0.032043 | 121.5363 | 61.5829 | -0.13733 | 121.4218 | -0.032043 | 61.5829 | 121.4172 | 121.5363 | -121.6553 | -121.7468
545.5938 | 121.7926 | -61.3037 | 60.3012 | -0.10643 | 0.014328 | 0.0017623 | 0.012117 | 0.052891 | -0.012245 | 0.067543 | -61.3358 | 60.1913 | -61.3541 | -61.3403 | 60.0769 | 0.19684 | 0.013733 | 0.09613 | 60.3333 | -61.4044 | -0.050354 | -0.10986 | -0.032043 | -0.036621 | -0.2243 | -0.10071 | 0.032044 | 0.018311 | 61.3174 | 61.3998 | 121.3806 | 121.4951 | -0.032043 | 121.637 | 61.5005 | -0.10071 | 121.4951 | -0.032043 | 61.5005 | 121.3806 | 121.637 | -121.6553 | -121.7056
547.3438 | 121.8567 | -61.2854 | 60.3378 | -0.2285 | 0.014328 | -0.0020829 | 0.0080578 | 0.052677 | -0.0086132 | 0.06797 | -61.3495 | 60.2554 | -61.2991 | -61.3632 | 60.0769 | 0.24261 | 0.25177 | 0.17395 | 60.3653 | -61.3953 | -0.013733 | -0.082398 | -0.064087 | -0.07782 | -0.26093 | -0.10986 | 0.027465 | -0.050354 | 61.5372 | 61.4594 | 121.3623 | 121.5408 | -0.064087 | 121.6507 | 61.528 | -0.10986 | 121.5408 | -0.064087 | 61.528 | 121.3623 | 121.6507 | -121.637 | -121.7331
549.0938 | 121.9391 | -61.2579 | 60.26 | 0.11482 | 0.013687 | 0.0030441 | 0.0089124 | 0.054173 | -0.011177 | 0.067543 | -61.4319 | 60.1364 | -61.409 | -61.4868 | 59.9716 | 0.004578 | -0.13275 | -0.14648 | 60.2692 | -61.4548 | -0.15106 | -0.1236 | -0.17395 | -0.22888 | -0.28839 | -0.19684 | 0.009155 | -0.022888 | 61.1252 | 61.1115 | 121.2296 | 121.3943 | -0.17395 | 121.5271 | 61.2625 | -0.19684 | 121.3943 | -0.17395 | 61.2625 | 121.2296 | 121.5271 | -121.669 | -121.7148
550.7656 | 121.9437 | -61.1755 | 60.4111 | -0.0072479 | 0.013473 | -0.0012283 | 0.0037854 | 0.050328 | -0.0069042 | 0.068398 | -61.3266 | 60.1913 | -61.29 | -61.3495 | 60.1227 | 0.21973 | -0.004578 | 0.16479 | 60.2921 | -61.3861 | -0.11444 | -0.21973 | -0.15106 | -0.17395 | -0.28839 | -0.21057 | -0.11902 | -0.036621 | 61.171 | 61.3403 | 121.2982 | 121.3669 | -0.15106 | 121.4676 | 61.3953 | -0.21057 | 121.3669 | -0.15106 | 61.3953 | 121.2982 | 121.4676 | -121.701 | -121.7972
552.5156 | 121.8521 | -61.29 | 60.3195 | -0.22087 | 0.0139 | 0.0015487 | 0.010835 | 0.0499 | -0.010536 | 0.067116 | -61.3541 | 60.2463 | -61.3358 | -61.3724 | 60.0815 | 0.23804 | 0.21515 | 0.15564 | 60.347 | -61.3861 | -0.045776 | -0.073242 | -0.064087 | -0.082397 | -0.23804 | -0.09613 | 0.027466 | -0.018311 | 61.5051 | 61.4456 | 121.3715 | 121.5363 | -0.064087 | 121.637 | 61.528 | -0.09613 | 121.5363 | -0.064087 | 61.528 | 121.3715 | 121.637 | -121.6553 | -121.7056
554.2656 | 121.8109 | -61.322 | 60.3333 | -0.12932 | 0.012832 | 0.0036849 | 0.011903 | 0.053959 | -0.011177 | 0.066902 | -61.3312 | 60.1959 | -61.3541 | -61.3586 | 60.0815 | 0.22888 | 0.036621 | 0.10986 | 60.3195 | -61.409 | -0.032044 | -0.13733 | -0.009156 | -0.036622 | -0.25177 | -0.086976 | -0.013733 | 0.022888 | 61.3586 | 61.4319 | 121.4035 | 121.5179 | -0.009156 | 121.6415 | 61.5509 | -0.086976 | 121.5179 | -0.009156 | 61.5509 | 121.4035 | 121.6415 | -121.6873 | -121.7422
555.9531 | 121.9437 | -61.2534 | 60.2737 | 0.11482 | 0.013687 | 0.0049667 | 0.011476 | 0.053959 | -0.0096814 | 0.066262 | -61.4456 | 60.1639 | -61.3907 | -61.4822 | 59.9716 | 0.009155 | -0.13275 | -0.16479 | 60.3012 | -61.4548 | -0.13733 | -0.10986 | -0.19226 | -0.22888 | -0.30212 | -0.20142 | 0.027465 | -0.054932 | 61.1206 | 61.0886 | 121.225 | 121.4172 | -0.19226 | 121.5546 | 61.2625 | -0.20142 | 121.4172 | -0.19226 | 61.2625 | 121.225 | 121.5546 | -121.6644 | -121.7285
557.7031 | 121.9116 | -61.2579 | 60.347 | 0.13771 | 0.012191 | 0.0030441 | 0.0059216 | 0.055455 | -0.01139 | 0.066475 | -61.3312 | 60.0906 | -61.3403 | -61.3632 | 60.0952 | 0.14191 | -0.3067 | -0.004578 | 60.2234 | -61.4044 | -0.082397 | -0.25635 | -0.073242 | -0.10528 | -0.25177 | -0.14648 | -0.1236 | 0.009155 | 60.9512 | 61.2534 | 121.3531 | 121.3486 | -0.073242 | 121.4813 | 61.3998 | -0.14648 | 121.3486 | -0.073242 | 61.3998 | 121.3531 | 121.4813 | -121.6873 | -121.7514
559.3906 | 121.962 | -61.1664 | 60.3607 | 0.046158 | 0.013687 | 0.0030441 | 0.0037854 | 0.051609 | -0.0062634 | 0.066262 | -61.322 | 60.1868 | -61.2717 | -61.3724 | 60.0952 | 0.17395 | -0.09613 | 0.10071 | 60.2554 | -61.4044 | -0.10529 | -0.17395 | -0.15564 | -0.20599 | -0.2655 | -0.23804 | -0.10529 | -0.050354 | 61.0703 | 61.2671 | 121.2616 | 121.3531 | -0.15564 | 121.4218 | 61.3403 | -0.23804 | 121.3531 | -0.15564 | 61.3403 | 121.2616 | 121.4218 | -121.6324 | -121.7651
561.1406 | 121.8796 | -61.2534 | 60.3561 | -0.22087 | 0.015182 | 0.0038985 | 0.0078442 | 0.054386 | -0.0079724 | 0.06797 | -61.3312 | 60.2554 | -61.2717 | -61.3358 | 60.0861 | 0.27008 | 0.27924 | 0.19226 | 60.3653 | -61.3861 | -0.01831 | -0.10071 | -0.07782 | -0.082397 | -0.27008 | -0.13275 | 0.009155 | -0.05951 | 61.5326 | 61.4456 | 121.3394 | 121.5088 | -0.07782 | 121.6187 | 61.5234 | -0.13275 | 121.5088 | -0.07782 | 61.5234 | 121.3394 | 121.6187 | -121.6278 | -121.7422
562.875 | 121.8018 | -61.3083 | 60.3104 | -0.12169 | 0.015396 | 0.0015487 | 0.011262 | 0.052464 | -0.010536 | 0.066475 | -61.3358 | 60.2142 | -61.3449 | -61.3632 | 60.0906 | 0.21973 | 0.045776 | 0.11444 | 60.3241 | -61.409 | -0.036621 | -0.096131 | -0.027465 | -0.054931 | -0.21973 | -0.10071 | 0.013733 | 0.009156 | 61.3541 | 61.4227 | 121.3989 | 121.5225 | -0.027465 | 121.6324 | 61.528 | -0.10071 | 121.5225 | -0.027465 | 61.528 | 121.3989 | 121.6324 | -121.6553 | -121.7194
564.625 | 121.8292 | -61.3174 | 60.3195 | -0.053024 | 0.013046 | 0.00069434 | 0.010408 | 0.052891 | -0.012031 | 0.067757 | -61.3495 | 60.1685 | -61.3953 | -61.3861 | 60.0586 | 0.14191 | -0.036621 | -0.004578 | 60.2875 | -61.4319 | -0.07782 | -0.15106 | -0.032043 | -0.068664 | -0.26093 | -0.11444 | -0.032043 | 0.045777 | 61.2808 | 61.3129 | 121.376 | 121.4859 | -0.032043 | 121.6049 | 61.4594 | -0.11444 | 121.4859 | -0.032043 | 61.4594 | 121.376 | 121.6049 | -121.7148 | -121.7514
566.375 | 121.9528 | -61.1893 | 60.3607 | 0.046158 | 0.01326 | 0.0015487 | 0.0016492 | 0.051182 | -0.008186 | 0.069252 | -61.3312 | 60.173 | -61.29 | -61.3678 | 60.1044 | 0.16022 | -0.091553 | 0.082397 | 60.3058 | -61.409 | -0.10071 | -0.18768 | -0.14191 | -0.17853 | -0.25635 | -0.21973 | -0.054932 | -0.041199 | 61.0977 | 61.2717 | 121.2936 | 121.3623 | -0.14191 | 121.4951 | 61.3495 | -0.21973 | 121.3623 | -0.14191 | 61.3495 | 121.2936 | 121.4951 | -121.6507 | -121.7697
568.0625 | 121.8292 | -61.3174 | 60.3287 | -0.068283 | 0.012191 | 0.0062485 | 0.011689 | 0.056095 | -0.0086132 | 0.066048 | -61.3632 | 60.1868 | -61.3632 | -61.4044 | 60.0403 | 0.14648 | -0.036621 | -0.004578 | 60.3058 | -61.4136 | -0.045776 | -0.14191 | -0.045776 | -0.086975 | -0.28839 | -0.09613 | -0.022888 | 0 | 61.2808 | 61.3129 | 121.3577 | 121.5042 | -0.045776 | 121.6232 | 61.4639 | -0.09613 | 121.5042 | -0.045776 | 61.4639 | 121.3577 | 121.6232 | -121.6919 | -121.7422
569.75 | 121.8384 | -61.2442 | 60.4111 | -0.25139 | 0.011978 | 0.00048074 | 0.0031446 | 0.054173 | -0.011604 | 0.066475 | -61.2488 | 60.2234 | -61.2717 | -61.2762 | 60.1959 | 0.35248 | 0.19226 | 0.32959 | 60.347 | -61.3541 | -0.027465 | -0.18768 | -0.004577 | -0.032043 | -0.21515 | -0.10986 | -0.064087 | 0.022888 | 61.4365 | 61.5738 | 121.4401 | 121.4676 | -0.004577 | 121.5912 | 61.5967 | -0.10986 | 121.4676 | -0.004577 | 61.5967 | 121.4401 | 121.5912 | -121.6827 | -121.7651
571.5 | 121.8292 | -61.2991 | 60.2966 | -0.068283 | 0.012619 | 0.0021895 | 0.012117 | 0.053746 | -0.010109 | 0.067757 | -61.3541 | 60.1501 | -61.3815 | -61.3632 | 60.0815 | 0.17395 | -0.027466 | 0.041199 | 60.3012 | -61.4227 | -0.082398 | -0.14648 | -0.054932 | -0.064087 | -0.21515 | -0.1236 | 0.004577 | 0.027466 | 61.2717 | 61.3403 | 121.3806 | 121.4493 | -0.054932 | 121.6003 | 61.4731 | -0.1236 | 121.4493 | -0.054932 | 61.4731 | 121.3806 | 121.6003 | -121.6782 | -121.7194
573.25 | 121.8567 | -61.3266 | 60.2783 | 0.02327 | 0.014328 | 0.0019759 | 0.011476 | 0.054173 | -0.01139 | 0.069679 | -61.4044 | 60.1593 | -61.3953 | -61.4502 | 59.9899 | 0.082397 | -0.073242 | -0.07782 | 60.2646 | -61.4639 | -0.068665 | -0.11902 | -0.07782 | -0.1236 | -0.28839 | -0.13733 | -0.013733 | -0.009155 | 61.2534 | 61.2488 | 121.3165 | 121.4859 | -0.07782 | 121.5912 | 61.409 | -0.13733 | 121.4859 | -0.07782 | 61.409 | 121.3165 | 121.5912 | -121.6736 | -121.7422
575 | 121.9391 | -61.171 | 60.3699 | -0.022507 | 0.012191 | -0.0016557 | 0.0027172 | 0.053959 | -0.0066906 | 0.064766 | -61.3129 | 60.2142 | -61.2717 | -61.3449 | 60.141 | 0.22888 | 0.009155 | 0.17853 | 60.347 | -61.3815 | -0.10071 | -0.15564 | -0.14191 | -0.17395 | -0.22888 | -0.21057 | -0.022888 | -0.041199 | 61.1801 | 61.3495 | 121.3119 | 121.3852 | -0.14191 | 121.5179 | 61.3998 | -0.21057 | 121.3852 | -0.14191 | 61.3998 | 121.3119 | 121.5179 | -121.6415 | -121.7514
576.75 | 121.8521 | -61.2534 | 60.3699 | -0.2285 | 0.012191 | -0.0020829 | 0.0069898 | 0.051396 | -0.010322 | 0.066475 | -61.3129 | 60.2371 | -61.2854 | -61.3403 | 60.1044 | 0.27466 | 0.23804 | 0.22888 | 60.3653 | -61.377 | -0.032043 | -0.13275 | -0.059509 | -0.086975 | -0.2655 | -0.1236 | -0.004578 | -0.027466 | 61.4914 | 61.4822 | 121.3577 | 121.4905 | -0.059509 | 121.6187 | 61.528 | -0.1236 | 121.4905 | -0.059509 | 61.528 | 121.3577 | 121.6187 | -121.6553 | -121.7468
578.4375 | 121.8933 | -61.2213 | 60.3653 | 0.12245 | 0.015182 | 0.0049667 | 0.0076306 | 0.052891 | -0.0092542 | 0.067757 | -61.3083 | 60.1456 | -61.3632 | -61.3449 | 60.1181 | 0.16022 | -0.25635 | 0.054932 | 60.2417 | -61.4227 | -0.14191 | -0.21973 | -0.086976 | -0.1236 | -0.24719 | -0.20142 | -0.1236 | 0.054931 | 60.965 | 61.2762 | 121.3394 | 121.3669 | -0.086976 | 121.463 | 61.3815 | -0.20142 | 121.3669 | -0.086976 | 61.3815 | 121.3394 | 121.463 | -121.7285 | -121.788
580.1875 | 121.8704 | -61.2625 | 60.3653 | -0.23613 | 0.0139 | -0.0022965 | 0.0067762 | 0.052037 | -0.0094678 | 0.067116 | -61.3266 | 60.2646 | -61.322 | -61.3632 | 60.0906 | 0.26093 | 0.2655 | 0.17853 | 60.3882 | -61.3724 | -0.059509 | -0.10071 | -0.064087 | -0.10071 | -0.27466 | -0.10986 | 0.022889 | -0.004578 | 61.528 | 61.441 | 121.3531 | 121.5271 | -0.064087 | 121.6507 | 61.5234 | -0.10986 | 121.5271 | -0.064087 | 61.5234 | 121.3531 | 121.6507 | -121.6873 | -121.7377
581.9375 | 121.843 | -61.3174 | 60.3104 | 0.01564 | 0.015182 | 0.0034713 | 0.010621 | 0.053318 | -0.012458 | 0.067116 | -61.4182 | 60.1593 | -61.4044 | -61.4548 | 59.9854 | 0.073242 | -0.082397 | -0.082397 | 60.2646 | -61.4456 | -0.086975 | -0.15106 | -0.10071 | -0.13733 | -0.32501 | -0.12817 | -0.045777 | -0.013733 | 61.235 | 61.235 | 121.3028 | 121.4767 | -0.10071 | 121.582 | 61.3907 | -0.12817 | 121.4767 | -0.10071 | 61.3907 | 121.3028 | 121.582 | -121.7148 | -121.756
583.6875 | 121.8658 | -61.2122 | 60.4065 | -0.15221 | 0.01326 | -0.00080106 | 0.0025036 | 0.050755 | -0.010109 | 0.066262 | -61.2396 | 60.2097 | -61.2625 | -61.2579 | 60.2142 | 0.33417 | 0.027466 | 0.31586 | 60.3333 | -61.3312 | -0.050354 | -0.19684 | -0.027466 | -0.045777 | -0.19226 | -0.11902 | -0.073242 | 0.022888 | 61.2396 | 61.528 | 121.4264 | 121.4218 | -0.027466 | 121.5454 | 61.5463 | -0.11902 | 121.4218 | -0.027466 | 61.5463 | 121.4264 | 121.5454 | -121.669 | -121.7377
585.3594 | 121.8292 | -61.2991 | 60.2921 | -0.045395 | 0.014969 | 0.0026169 | 0.012758 | 0.053532 | -0.010109 | 0.067116 | -61.3449 | 60.1501 | -61.3953 | -61.3998 | 60.0311 | 0.10986 | -0.054932 | -0.013733 | 60.26 | -61.4319 | -0.096131 | -0.14191 | -0.045777 | -0.10071 | -0.26093 | -0.13275 | -0.032043 | 0.050354 | 61.2442 | 61.2854 | 121.3303 | 121.4493 | -0.045777 | 121.5591 | 61.409 | -0.13275 | 121.4493 | -0.045777 | 61.409 | 121.3303 | 121.5591 | -121.6873 | -121.7239
587.1094 | 121.9299 | -61.203 | 60.3745 | 0.099564 | 0.014969 | 0.00069434 | 0.0025036 | 0.05225 | -0.0077588 | 0.065834 | -61.3266 | 60.1501 | -61.3174 | -61.3541 | 60.1089 | 0.16479 | -0.13733 | 0.082397 | 60.2692 | -61.409 | -0.11444 | -0.22431 | -0.1236 | -0.15106 | -0.2655 | -0.20599 | -0.10529 | -0.009155 | 61.0657 | 61.2854 | 121.312 | 121.3531 | -0.1236 | 121.4722 | 61.3678 | -0.20599 | 121.3531 | -0.1236 | 61.3678 | 121.312 | 121.4722 | -121.6919 | -121.7834
588.8438 | 121.9391 | -61.2717 | 60.2966 | 0.10719 | 0.015823 | -0.00080106 | 0.010621 | 0.053959 | -0.011818 | 0.067757 | -61.4182 | 60.1593 | -61.4136 | -61.4502 | 59.9945 | 0.036621 | -0.17853 | -0.11444 | 60.2692 | -61.4731 | -0.14191 | -0.13733 | -0.14648 | -0.17853 | -0.30212 | -0.20142 | -0.027466 | -0.004578 | 61.0931 | 61.1572 | 121.2662 | 121.431 | -0.14648 | 121.5408 | 61.3083 | -0.20142 | 121.431 | -0.14648 | 61.3083 | 121.2662 | 121.5408 | -121.7102 | -121.7697
590.5781 | 121.962 | -61.1847 | 60.3745 | 0.046158 | 0.012191 | 0.00026694 | 0.0061352 | 0.051396 | -0.0077588 | 0.066689 | -61.3403 | 60.1822 | -61.2946 | -61.3586 | 60.1044 | 0.16022 | -0.10071 | 0.09613 | 60.2783 | -61.4182 | -0.10986 | -0.19226 | -0.15564 | -0.17395 | -0.27008 | -0.23346 | -0.096131 | -0.045776 | 61.084 | 61.2808 | 121.2891 | 121.3669 | -0.15564 | 121.463 | 61.3449 | -0.23346 | 121.3669 | -0.15564 | 61.3449 | 121.2891 | 121.463 | -121.669 | -121.7926
592.3281 | 121.9574 | -61.2579 | 60.2783 | 0.099564 | 0.013473 | -0.00058746 | 0.0099804 | 0.052037 | -0.0094678 | 0.067116 | -61.4365 | 60.141 | -61.409 | -61.4777 | 59.9808 | 0.032043 | -0.14648 | -0.12817 | 60.2371 | -61.4731 | -0.15106 | -0.13733 | -0.17853 | -0.21973 | -0.29755 | -0.21515 | -0.041198 | -0.027465 | 61.1115 | 61.1298 | 121.2387 | 121.3989 | -0.17853 | 121.4951 | 61.29 | -0.21515 | 121.3989 | -0.17853 | 61.29 | 121.2387 | 121.4951 | -121.6873 | -121.7514
594 | 121.8384 | -61.2122 | 60.434 | -0.12169 | 0.013046 | -0.00037386 | 0.0020764 | 0.049046 | -0.009895 | 0.066689 | -61.235 | 60.2188 | -61.2488 | -61.2259 | 60.2371 | 0.36163 | 0.068665 | 0.33417 | 60.3333 | -61.3541 | -0.036621 | -0.21515 | -0.022888 | -0.013733 | -0.19684 | -0.14191 | -0.10071 | 0.013733 | 61.2808 | 61.5463 | 121.4493 | 121.431 | -0.022888 | 121.5454 | 61.5738 | -0.14191 | 121.431 | -0.022888 | 61.5738 | 121.4493 | 121.5454 | -121.6827 | -121.788
595.7344 | 121.8613 | -61.2671 | 60.3836 | -0.22087 | 0.0139 | 0.0026169 | 0.0065624 | 0.049259 | -0.008827 | 0.066689 | -61.322 | 60.2646 | -61.3037 | -61.3495 | 60.0998 | 0.27008 | 0.24261 | 0.22888 | 60.3699 | -61.3953 | -0.036621 | -0.11902 | -0.054931 | -0.082397 | -0.28381 | -0.12817 | -0.013733 | -0.01831 | 61.5097 | 61.496 | 121.3669 | 121.5317 | -0.054931 | 121.637 | 61.5372 | -0.12817 | 121.5317 | -0.054931 | 61.5372 | 121.3669 | 121.637 | -121.6873 | -121.7789
597.4219 | 121.8704 | -61.2671 | 60.3653 | -0.22087 | 0.01625 | -0.00037386 | 0.008485 | 0.051182 | -0.0083996 | 0.068398 | -61.3449 | 60.26 | -61.29 | -61.3541 | 60.0906 | 0.27466 | 0.27466 | 0.20142 | 60.3836 | -61.3815 | -0.022888 | -0.10529 | -0.07782 | -0.086975 | -0.27466 | -0.11444 | 0.018311 | -0.054932 | 61.5417 | 61.4685 | 121.3577 | 121.5271 | -0.07782 | 121.6507 | 61.5417 | -0.11444 | 121.5271 | -0.07782 | 61.5417 | 121.3577 | 121.6507 | -121.6553 | -121.7468
599.1562 | 121.8018 | -61.3312 | 60.3149 | -0.098801 | 0.01625 | 0.0032577 | 0.010408 | 0.055027 | -0.009895 | 0.06797 | -61.3358 | 60.1868 | -61.3586 | -61.3495 | 60.0815 | 0.19226 | 0.013733 | 0.10529 | 60.3058 | -61.3998 | -0.027466 | -0.12817 | -0.004577 | -0.01831 | -0.23346 | -0.068664 | -0.009155 | 0.022889 | 61.3449 | 61.4365 | 121.4127 | 121.5179 | -0.004577 | 121.637 | 61.5234 | -0.068664 | 121.5179 | -0.004577 | 61.5234 | 121.4127 | 121.637 | -121.6736 | -121.7148
600.9062 | 121.8842 | -61.2213 | 60.3516 | 0.17586 | 0.014328 | 0.0034713 | 0.0080578 | 0.05225 | -0.0090406 | 0.067543 | -61.3403 | 60.1181 | -61.377 | -61.3632 | 60.0998 | 0.12817 | -0.29755 | 0.004578 | 60.2005 | -61.4777 | -0.15564 | -0.23346 | -0.11902 | -0.14191 | -0.25177 | -0.25635 | -0.15106 | 0.036621 | 60.9238 | 61.2259 | 121.3211 | 121.3394 | -0.11902 | 121.4218 | 61.3495 | -0.25635 | 121.3394 | -0.11902 | 61.3495 | 121.3211 | 121.4218 | -121.7285 | -121.8292
602.5938 | 121.8796 | -61.2396 | 60.4111 | -0.14458 | 0.015182 | 0.0015487 | 0.0050672 | 0.052464 | -0.010322 | 0.067116 | -61.2259 | 60.2234 | -61.2625 | -61.2579 | 60.2051 | 0.3479 | 0.027466 | 0.3067 | 60.3149 | -61.3541 | -0.022888 | -0.18768 | 0.013733 | -0.018311 | -0.20599 | -0.11444 | -0.096131 | 0.036621 | 61.2671 | 61.5463 | 121.4447 | 121.463 | 0.013733 | 121.5546 | 61.5875 | -0.11444 | 121.463 | 0.013733 | 61.5875 | 121.4447 | 121.5546 | -121.6736 | -121.7651
604.3281 | 121.9162 | -61.2076 | 60.379 | 0.084305 | 0.01326 | 0.0019759 | 0.0065624 | 0.052464 | -0.008827 | 0.068825 | -61.3129 | 60.1593 | -61.3495 | -61.3632 | 60.1044 | 0.15106 | -0.21515 | 0.050354 | 60.2509 | -61.409 | -0.14191 | -0.21973 | -0.10529 | -0.15564 | -0.27466 | -0.20142 | -0.12817 | 0.036621 | 60.9924 | 61.2579 | 121.312 | 121.3669 | -0.10529 | 121.4584 | 61.3586 | -0.20142 | 121.3669 | -0.10529 | 61.3586 | 121.312 | 121.4584 | -121.7285 | -121.788
606 | 121.8201 | -61.2442 | 60.434 | -0.17509 | 0.013473 | 0.0011215 | 0.0063488 | 0.049687 | -0.0079724 | 0.067116 | -61.235 | 60.228 | -61.2717 | -61.2625 | 60.1959 | 0.37537 | 0.10986 | 0.34332 | 60.3104 | -61.3678 | -0.027465 | -0.20599 | 0.009156 | -0.01831 | -0.23804 | -0.1236 | -0.1236 | 0.036621 | 61.3541 | 61.5875 | 121.4401 | 121.4722 | 0.009156 | 121.5546 | 61.6196 | -0.1236 | 121.4722 | 0.009156 | 61.6196 | 121.4401 | 121.5546 | -121.7056 | -121.8018
607.75 | 121.9528 | -61.2579 | 60.2829 | 0.14534 | 0.014969 | 0.00026694 | 0.01233 | 0.053318 | -0.012031 | 0.066689 | -61.4456 | 60.1364 | -61.4456 | -61.4731 | 59.9808 | 0.022888 | -0.11902 | -0.13733 | 60.2783 | -61.4822 | -0.18768 | -0.14648 | -0.18768 | -0.21515 | -0.30212 | -0.2243 | -0.004578 | 0 | 61.1389 | 61.1206 | 121.2387 | 121.3943 | -0.18768 | 121.5363 | 61.2808 | -0.2243 | 121.3943 | -0.18768 | 61.2808 | 121.2387 | 121.5363 | -121.7285 | -121.7651
609.5 | 121.9299 | -61.2717 | 60.3012 | 0.13008 | 0.017105 | 0.0043259 | 0.0099804 | 0.051823 | -0.011818 | 0.06797 | -61.4182 | 60.1685 | -61.3998 | -61.4456 | 60.0082 | 0.045776 | -0.21515 | -0.09613 | 60.2554 | -61.4685 | -0.12817 | -0.13275 | -0.14648 | -0.17395 | -0.29297 | -0.19684 | -0.045776 | -0.018311 | 61.0565 | 61.1755 | 121.2799 | 121.4401 | -0.14648 | 121.5271 | 61.3174 | -0.19684 | 121.4401 | -0.14648 | 61.3174 | 121.2799 | 121.5271 | -121.701 | -121.7697
611.1875 | 121.8109 | -61.3266 | 60.3058 | -0.098801 | 0.01625 | -0.0018693 | 0.0097668 | 0.052464 | -0.0094678 | 0.067757 | -61.3312 | 60.2188 | -61.3403 | -61.3678 | 60.0815 | 0.20142 | 0.013733 | 0.10071 | 60.2737 | -61.4502 | -0.013733 | -0.086975 | -0.004578 | -0.041199 | -0.2243 | -0.1236 | -0.032043 | 0.009155 | 61.3403 | 61.4273 | 121.4081 | 121.5454 | -0.004578 | 121.6003 | 61.528 | -0.1236 | 121.5454 | -0.004578 | 61.528 | 121.4081 | 121.6003 | -121.6461 | -121.756
612.9375 | 121.907 | -61.2259 | 60.3745 | 0.13771 | 0.015823 | 0.0043259 | 0.0059216 | 0.055668 | -0.008186 | 0.06733 | -61.322 | 60.1547 | -61.3403 | -61.3632 | 60.1044 | 0.13275 | -0.30212 | 0.018311 | 60.2188 | -61.4502 | -0.11444 | -0.21973 | -0.09613 | -0.13733 | -0.27008 | -0.2243 | -0.15564 | 0.018311 | 60.9238 | 61.2442 | 121.3303 | 121.3806 | -0.09613 | 121.4447 | 61.3586 | -0.2243 | 121.3806 | -0.09613 | 61.3586 | 121.3303 | 121.4447 | -121.7148 | -121.8246
614.6875 | 121.875 | -61.2076 | 60.4065 | -0.17509 | 0.012191 | -0.0046463 | 0.0031446 | 0.052464 | -0.0090406 | 0.066902 | -61.2488 | 60.2325 | -61.2717 | -61.2625 | 60.228 | 0.34332 | 0.027466 | 0.31586 | 60.3058 | -61.3632 | -0.064086 | -0.17395 | -0.041198 | -0.054931 | -0.17853 | -0.15564 | -0.10071 | 0.022888 | 61.235 | 61.5234 | 121.4355 | 121.4401 | -0.041198 | 121.5134 | 61.5509 | -0.15564 | 121.4401 | -0.041198 | 61.5509 | 121.4355 | 121.5134 | -121.6782 | -121.7697
616.375 | 121.8658 | -61.3129 | 60.2783 | 0.01564 | 0.013473 | -0.0029373 | 0.011049 | 0.052891 | -0.010109 | 0.066902 | -61.3998 | 60.1456 | -61.4273 | -61.4456 | 59.9854 | 0.064087 | -0.073242 | -0.09613 | 60.26 | -61.4685 | -0.11444 | -0.13275 | -0.086975 | -0.13275 | -0.29297 | -0.15564 | -0.01831 | 0.027466 | 61.2396 | 61.2167 | 121.2982 | 121.4584 | -0.086975 | 121.5729 | 61.377 | -0.15564 | 121.4584 | -0.086975 | 61.377 | 121.2982 | 121.5729 | -121.7056 | -121.7468
618.125 | 121.9345 | -61.1755 | 60.3836 | -0.030136 | 0.011978 | 0.00090794 | 0.0035718 | 0.052037 | -0.008186 | 0.064553 | -61.3174 | 60.228 | -61.29 | -61.3312 | 60.1456 | 0.25635 | 0.013733 | 0.2243 | 60.3287 | -61.4044 | -0.11444 | -0.15564 | -0.14191 | -0.15564 | -0.23804 | -0.22888 | -0.054932 | -0.027466 | 61.1893 | 61.3998 | 121.3211 | 121.4035 | -0.14191 | 121.5042 | 61.4319 | -0.22888 | 121.4035 | -0.14191 | 61.4319 | 121.3211 | 121.5042 | -121.6736 | -121.788
619.8125 | 121.907 | -61.2213 | 60.3516 | 0.16823 | 0.014328 | 0.0036849 | 0.0082714 | 0.052891 | -0.010322 | 0.066902 | -61.3312 | 60.0906 | -61.3907 | -61.3358 | 60.1089 | 0.13733 | -0.30212 | 0.027466 | 60.2097 | -61.4365 | -0.16937 | -0.26093 | -0.10986 | -0.11444 | -0.24261 | -0.21515 | -0.14191 | 0.059509 | 60.9192 | 61.2488 | 121.3303 | 121.3119 | -0.10986 | 121.431 | 61.3586 | -0.21515 | 121.3119 | -0.10986 | 61.3586 | 121.3303 | 121.431 | -121.7422 | -121.788
621.5625 | 121.8018 | -61.3449 | 60.3149 | -0.068283 | 0.0139 | 0.0038985 | 0.011689 | 0.053318 | -0.0092542 | 0.066902 | -61.3403 | 60.173 | -61.377 | -61.3724 | 60.0815 | 0.16479 | -0.036621 | 0.032043 | 60.3058 | -61.409 | -0.032043 | -0.14191 | 0.004578 | -0.027465 | -0.23346 | -0.064087 | -0.009155 | 0.036621 | 61.3083 | 61.377 | 121.4264 | 121.5179 | 0.004578 | 121.6507 | 61.5097 | -0.064087 | 121.5179 | 0.004578 | 61.5097 | 121.4264 | 121.6507 | -121.6919 | -121.7239
623.25 | 121.7972 | -61.3358 | 60.3149 | -0.083542 | 0.016891 | 0.0036849 | 0.0089124 | 0.052891 | -0.011604 | 0.065621 | -61.3312 | 60.1822 | -61.3632 | -61.3495 | 60.0815 | 0.19684 | -0.013733 | 0.09613 | 60.3012 | -61.4044 | -0.027466 | -0.13275 | 0.004577 | -0.013733 | -0.23346 | -0.068665 | -0.013733 | 0.032043 | 61.322 | 61.4319 | 121.4172 | 121.5179 | 0.004577 | 121.637 | 61.5326 | -0.068665 | 121.5179 | 0.004577 | 61.5326 | 121.4172 | 121.637 | -121.6782 | -121.7194
624.9375 | 121.962 | -61.203 | 60.3836 | 0.10719 | 0.014755 | 0.0045395 | 0.0046398 | 0.052677 | -0.0094678 | 0.068184 | -61.322 | 60.1639 | -61.3037 | -61.3586 | 60.1135 | 0.16022 | -0.11444 | 0.10071 | 60.2921 | -61.3998 | -0.10071 | -0.21973 | -0.11902 | -0.15564 | -0.27008 | -0.19684 | -0.091553 | -0.01831 | 61.0886 | 61.3037 | 121.3165 | 121.3669 | -0.11902 | 121.4951 | 61.3632 | -0.19684 | 121.3669 | -0.11902 | 61.3632 | 121.3165 | 121.4951 | -121.6873 | -121.7834
626.6875 | 121.9391 | -61.1893 | 60.3928 | 0.099564 | 0.014328 | 0.00090794 | 0.0061352 | 0.051396 | -0.008186 | 0.066048 | -61.322 | 60.1547 | -61.3358 | -61.3586 | 60.1227 | 0.16479 | -0.18768 | 0.07782 | 60.2509 | -61.4319 | -0.14648 | -0.23804 | -0.13275 | -0.16937 | -0.27008 | -0.24262 | -0.14191 | 0.013733 | 61.0016 | 61.2671 | 121.312 | 121.344 | -0.13275 | 121.4401 | 61.3541 | -0.24262 | 121.344 | -0.13275 | 61.3541 | 121.312 | 121.4401 | -121.7285 | -121.8246
628.375 | 121.9208 | -61.2488 | 60.3241 | 0.17586 | 0.014328 | 0.0036849 | 0.010194 | 0.053318 | -0.010322 | 0.067543 | -61.4227 | 60.1456 | -61.4044 | -61.4182 | 60.022 | 0.064087 | -0.24261 | -0.07782 | 60.2463 | -61.441 | -0.15564 | -0.17853 | -0.17395 | -0.16937 | -0.30212 | -0.19226 | -0.07782 | -0.01831 | 61.0062 | 61.171 | 121.2708 | 121.3943 | -0.17395 | 121.4951 | 61.3129 | -0.19226 | 121.3943 | -0.17395 | 61.3129 | 121.2708 | 121.4951 | -121.7285 | -121.7651
630.125 | 121.9482 | -61.171 | 60.3836 | 0.0080111 | 0.014114 | 0.0030441 | 0.005708 | 0.050114 | -0.008827 | 0.066475 | -61.3495 | 60.2005 | -61.2808 | -61.3449 | 60.1181 | 0.2243 | -0.004578 | 0.16937 | 60.2966 | -61.4044 | -0.10986 | -0.18311 | -0.17853 | -0.17395 | -0.2655 | -0.23346 | -0.086975 | -0.068664 | 61.1664 | 61.3403 | 121.2891 | 121.3715 | -0.17853 | 121.4676 | 61.3953 | -0.23346 | 121.3715 | -0.17853 | 61.3953 | 121.2891 | 121.4676 | -121.6644 | -121.788
631.8125 | 121.8109 | -61.322 | 60.3378 | -0.10643 | 0.0139 | -0.0016557 | 0.013398 | 0.051182 | -0.011604 | 0.06797 | -61.3312 | 60.1868 | -61.377 | -61.3632 | 60.0769 | 0.19684 | 0.018311 | 0.09613 | 60.2921 | -61.4182 | -0.054932 | -0.15106 | -0.009156 | -0.041199 | -0.26093 | -0.096131 | -0.045777 | 0.045776 | 61.3403 | 61.4182 | 121.3989 | 121.5088 | -0.009156 | 121.6141 | 61.5189 | -0.096131 | 121.5088 | -0.009156 | 61.5189 | 121.3989 | 121.6141 | -121.7148 | -121.756
633.5625 | 121.8155 | -61.3174 | 60.3378 | -0.11406 | 0.016464 | 0.0024033 | 0.011262 | 0.054814 | -0.011818 | 0.067116 | -61.322 | 60.2142 | -61.3632 | -61.3541 | 60.0769 | 0.23346 | 0.045776 | 0.11902 | 60.3149 | -61.4273 | -0.045776 | -0.1236 | -0.004577 | -0.036621 | -0.26093 | -0.10986 | -0.022889 | 0.041199 | 61.3632 | 61.4365 | 121.3943 | 121.5317 | -0.004577 | 121.6324 | 61.5509 | -0.10986 | 121.5317 | -0.004577 | 61.5509 | 121.3943 | 121.6324 | -121.701 | -121.7651
635.25 | 121.8933 | -61.235 | 60.3699 | 0.16823 | 0.012832 | 0.00026694 | 0.0059216 | 0.054814 | -0.0079724 | 0.064766 | -61.3083 | 60.1273 | -61.3449 | -61.3586 | 60.0998 | 0.12817 | -0.31128 | 0.027466 | 60.2188 | -61.441 | -0.10986 | -0.24262 | -0.073243 | -0.1236 | -0.27008 | -0.20599 | -0.15106 | 0.036621 | 60.9238 | 61.2625 | 121.3348 | 121.3623 | -0.073243 | 121.4539 | 61.3632 | -0.20599 | 121.3623 | -0.073243 | 61.3632 | 121.3348 | 121.4539 | -121.7148 | -121.8109
637 | 121.9116 | -61.2488 | 60.3104 | 0.17586 | 0.014328 | 0.0038985 | 0.011476 | 0.053105 | -0.010109 | 0.067757 | -61.409 | 60.1685 | -61.3586 | -61.4365 | 60.022 | 0.059509 | -0.23346 | -0.09613 | 60.2692 | -61.4731 | -0.10986 | -0.14191 | -0.16022 | -0.18768 | -0.28839 | -0.2243 | -0.041199 | -0.050354 | 61.0153 | 61.1526 | 121.2708 | 121.4172 | -0.16022 | 121.5179 | 61.3083 | -0.2243 | 121.4172 | -0.16022 | 61.3083 | 121.2708 | 121.5179 | -121.669 | -121.7834
638.7656 | 121.875 | -61.2854 | 60.347 | -0.16747 | 0.014328 | 0.0021895 | 0.0093396 | 0.05225 | -0.010109 | 0.066475 | -61.3586 | 60.2417 | -61.3632 | -61.3724 | 60.0952 | 0.23804 | 0.20142 | 0.16937 | 60.3333 | -61.3815 | -0.07782 | -0.10529 | -0.073243 | -0.086975 | -0.25177 | -0.096131 | -0.013733 | 0.004577 | 61.4868 | 61.4548 | 121.3806 | 121.5271 | -0.073243 | 121.6187 | 61.5234 | -0.096131 | 121.5271 | -0.073243 | 61.5234 | 121.3806 | 121.6187 | -121.7102 | -121.7285
640.4375 | 121.9345 | -61.2762 | 60.2783 | 0.061417 | 0.013473 | 0.0011215 | 0.011262 | 0.054814 | -0.012031 | 0.067543 | -61.4182 | 60.1868 | -61.409 | -61.4868 | 59.9808 | 0.027466 | -0.059509 | -0.13733 | 60.2783 | -61.4822 | -0.13275 | -0.091552 | -0.14191 | -0.21057 | -0.29755 | -0.20599 | 0 | -0.009155 | 61.2167 | 61.1389 | 121.257 | 121.463 | -0.14191 | 121.5546 | 61.3037 | -0.20599 | 121.463 | -0.14191 | 61.3037 | 121.257 | 121.5546 | -121.6873 | -121.7606
642.1875 | 121.907 | -61.2213 | 60.3241 | 0.17586 | 0.011764 | -0.0012283 | 0.007417 | 0.054386 | -0.01139 | 0.068184 | -61.3678 | 60.1227 | -61.409 | -61.3861 | 60.0632 | 0.09613 | -0.27466 | -0.018311 | 60.2509 | -61.4044 | -0.18768 | -0.20142 | -0.14648 | -0.16479 | -0.26093 | -0.18311 | -0.073243 | 0.041199 | 60.9467 | 61.203 | 121.2845 | 121.344 | -0.14648 | 121.4722 | 61.3174 | -0.18311 | 121.344 | -0.14648 | 61.3174 | 121.2845 | 121.4722 | -121.7331 | -121.7285
643.875 | 121.8796 | -61.2854 | 60.3836 | -0.25139 | 0.012619 | 0.0043259 | 0.0048534 | 0.050755 | -0.010963 | 0.066475 | -61.2808 | 60.2325 | -61.2762 | -61.322 | 60.1685 | 0.32501 | 0.2243 | 0.27924 | 60.3607 | -61.3358 | 0.009155 | -0.15106 | 0.004577 | -0.036621 | -0.21515 | -0.050354 | -0.022888 | -0.004578 | 61.5097 | 61.5646 | 121.4539 | 121.5179 | 0.004577 | 121.6461 | 61.6104 | -0.050354 | 121.5179 | 0.004577 | 61.6104 | 121.4539 | 121.6461 | -121.6599 | -121.7194
645.625 | 121.8338 | -61.2534 | 60.3973 | -0.16747 | 0.015823 | 0.0019759 | 0.0063488 | 0.049046 | -0.0090406 | 0.069039 | -61.2762 | 60.2234 | -61.2534 | -61.2625 | 60.2142 | 0.36621 | 0.16022 | 0.34332 | 60.3424 | -61.3586 | 0 | -0.17395 | -0.022888 | -0.009155 | -0.18311 | -0.10529 | -0.054932 | -0.022888 | 61.4136 | 61.5967 | 121.4676 | 121.4767 | -0.022888 | 121.5958 | 61.6196 | -0.10529 | 121.4767 | -0.022888 | 61.6196 | 121.4676 | 121.5958 | -121.6507 | -121.756
647.3125 | 121.8887 | -61.2122 | 60.4202 | -0.15984 | 0.012405 | -0.00080106 | 0.005708 | 0.051609 | -0.0079724 | 0.068184 | -61.2305 | 60.2051 | -61.2579 | -61.2534 | 60.2142 | 0.34332 | 0.027466 | 0.31586 | 60.3287 | -61.3495 | -0.045777 | -0.21515 | -0.018311 | -0.041199 | -0.20599 | -0.13733 | -0.091553 | 0.027466 | 61.2396 | 61.528 | 121.4264 | 121.4172 | -0.018311 | 121.5408 | 61.5555 | -0.13733 | 121.4172 | -0.018311 | 61.5555 | 121.4264 | 121.5408 | -121.6782 | -121.7697
649.0625 | 121.7926 | -61.3266 | 60.3012 | -0.068283 | 0.014755 | 0.0030441 | 0.011689 | 0.053746 | -0.013313 | 0.066902 | -61.322 | 60.173 | -61.3586 | -61.3541 | 60.0815 | 0.18768 | -0.004578 | 0.086975 | 60.3058 | -61.4044 | -0.032044 | -0.12817 | 0.004578 | -0.027466 | -0.21973 | -0.07782 | 0.004578 | 0.036622 | 61.322 | 61.4136 | 121.4081 | 121.4996 | 0.004578 | 121.6324 | 61.5143 | -0.07782 | 121.4996 | 0.004578 | 61.5143 | 121.4081 | 121.6324 | -121.6599 | -121.7056
650.8125 | 121.8018 | -61.2991 | 60.3287 | -0.11406 | 0.015182 | 0.0013351 | 0.013185 | 0.053959 | -0.01374 | 0.067543 | -61.3358 | 60.1822 | -61.3724 | -61.3541 | 60.0952 | 0.2243 | 0.059509 | 0.1236 | 60.3241 | -61.3953 | -0.073242 | -0.14648 | -0.036621 | -0.054932 | -0.23346 | -0.096131 | -0.004577 | 0.036621 | 61.3586 | 61.4227 | 121.3943 | 121.4813 | -0.036621 | 121.6232 | 61.5234 | -0.096131 | 121.4813 | -0.036621 | 61.5234 | 121.3943 | 121.6232 | -121.701 | -121.7239
652.5156 | 121.9025 | -61.2305 | 60.347 | 0.13771 | 0.015609 | 5.3338e-05 | 0.0069898 | 0.055455 | -0.0083996 | 0.067116 | -61.3129 | 60.1181 | -61.3358 | -61.3632 | 60.1089 | 0.15564 | -0.23804 | 0.068665 | 60.2417 | -61.4136 | -0.10529 | -0.22888 | -0.082397 | -0.13275 | -0.23804 | -0.1831 | -0.10529 | 0.022888 | 60.9924 | 61.2991 | 121.3394 | 121.3486 | -0.082397 | 121.4722 | 61.3861 | -0.1831 | 121.3486 | -0.082397 | 61.3861 | 121.3394 | 121.4722 | -121.6827 | -121.7606
654.25 | 121.962 | -61.1984 | 60.3973 | 0.02327 | 0.0139 | 0.0013351 | 0.0027172 | 0.051823 | -0.0083996 | 0.067116 | -61.3174 | 60.2142 | -61.29 | -61.3541 | 60.1227 | 0.20142 | -0.018311 | 0.14191 | 60.3104 | -61.3861 | -0.091553 | -0.18311 | -0.11902 | -0.15564 | -0.27466 | -0.18768 | -0.086975 | -0.027466 | 61.1801 | 61.3403 | 121.3211 | 121.4127 | -0.11902 | 121.5088 | 61.3998 | -0.18768 | 121.4127 | -0.11902 | 61.3998 | 121.3211 | 121.5088 | -121.6873 | -121.7834
655.9219 | 121.8567 | -61.2579 | 60.3424 | -0.19035 | 0.014969 | -0.0010147 | 0.010835 | 0.051609 | -0.010109 | 0.064766 | -61.3129 | 60.2509 | -61.3083 | -61.3586 | 60.0998 | 0.28381 | 0.25635 | 0.21973 | 60.3561 | -61.3861 | -0.050354 | -0.091553 | -0.054931 | -0.10071 | -0.24262 | -0.12817 | 0.013733 | -0.004577 | 61.5143 | 61.4777 | 121.3577 | 121.5088 | -0.054931 | 121.6141 | 61.5417 | -0.12817 | 121.5088 | -0.054931 | 61.5417 | 121.3577 | 121.6141 | -121.6507 | -121.7285
657.6562 | 121.7972 | -61.3174 | 60.3149 | -0.098801 | 0.014328 | 0.0034713 | 0.014253 | 0.050328 | -0.01139 | 0.066902 | -61.3266 | 60.173 | -61.3678 | -61.3632 | 60.0632 | 0.20142 | -0.004578 | 0.09613 | 60.2829 | -61.4319 | -0.050354 | -0.14191 | -0.009155 | -0.045776 | -0.25177 | -0.11444 | -0.032043 | 0.041199 | 61.3129 | 61.4136 | 121.3806 | 121.4905 | -0.009155 | 121.6003 | 61.5189 | -0.11444 | 121.4905 | -0.009155 | 61.5189 | 121.3806 | 121.6003 | -121.6827 | -121.7468
659.3438 | 121.8933 | -61.2442 | 60.3745 | 0.1606 | 0.013687 | 0.0028305 | 0.0080578 | 0.053746 | -0.0086132 | 0.068398 | -61.3083 | 60.141 | -61.3312 | -61.3449 | 60.1089 | 0.15106 | -0.28381 | 0.041199 | 60.2371 | -61.4365 | -0.086975 | -0.23346 | -0.064087 | -0.10071 | -0.2655 | -0.19226 | -0.13733 | 0.022888 | 60.9604 | 61.2854 | 121.3531 | 121.3852 | -0.064087 | 121.4813 | 61.3953 | -0.19226 | 121.3852 | -0.064087 | 61.3953 | 121.3531 | 121.4813 | -121.7056 | -121.8109
661.0781 | 121.9162 | -61.2488 | 60.3745 | 0.076676 | 0.014541 | -0.00058746 | 0.010194 | 0.052891 | -0.012245 | 0.069466 | -61.3312 | 60.1364 | -61.3449 | -61.3724 | 60.0815 | 0.12817 | -0.28381 | 0.009155 | 60.2463 | -61.4273 | -0.096131 | -0.23804 | -0.082398 | -0.1236 | -0.29297 | -0.17853 | -0.12817 | 0.013733 | 60.965 | 61.2579 | 121.3303 | 121.3852 | -0.082398 | 121.4951 | 61.377 | -0.17853 | 121.3852 | -0.082398 | 61.377 | 121.3303 | 121.4951 | -121.7194 | -121.8018
662.8438 | 121.8246 | -61.3358 | 60.3058 | -0.16747 | 0.013687 | 0.00048074 | 0.011476 | 0.050114 | -0.010322 | 0.067116 | -61.3495 | 60.2005 | -61.3495 | -61.3586 | 60.0861 | 0.22888 | 0.086975 | 0.13733 | 60.3149 | -61.4365 | -0.013733 | -0.10529 | -0.013733 | -0.022889 | -0.21973 | -0.10071 | 0.009155 | 0 | 61.4227 | 61.4731 | 121.4218 | 121.5363 | -0.013733 | 121.6507 | 61.5646 | -0.10071 | 121.5363 | -0.013733 | 61.5646 | 121.4218 | 121.6507 | -121.6553 | -121.7422
664.5156 | 121.962 | -61.2122 | 60.4019 | 0.038529 | 0.014114 | 0.0019759 | 0.0046398 | 0.05225 | -0.0069042 | 0.068184 | -61.3495 | 60.1913 | -61.2991 | -61.3632 | 60.1181 | 0.16479 | -0.064087 | 0.11902 | 60.3058 | -61.4273 | -0.086975 | -0.21057 | -0.13733 | -0.15106 | -0.28381 | -0.21515 | -0.096131 | -0.050354 | 61.1481 | 61.3312 | 121.3303 | 121.4035 | -0.13733 | 121.5179 | 61.377 | -0.21515 | 121.4035 | -0.13733 | 61.377 | 121.3303 | 121.5179 | -121.701 | -121.8292
666.25 | 121.8842 | -61.203 | 60.4019 | -0.098801 | 0.014969 | -0.0010147 | 0.0054944 | 0.051182 | -0.01075 | 0.064766 | -61.2442 | 60.228 | -61.2396 | -61.2671 | 60.2142 | 0.32959 | 0.027466 | 0.31128 | 60.3378 | -61.3586 | -0.036621 | -0.17395 | -0.041199 | -0.064087 | -0.18768 | -0.15564 | -0.064087 | -0.004578 | 61.2305 | 61.5143 | 121.4172 | 121.431 | -0.041199 | 121.5408 | 61.5326 | -0.15564 | 121.431 | -0.041199 | 61.5326 | 121.4172 | 121.5408 | -121.6415 | -121.7606
667.9375 | 121.8384 | -61.235 | 60.3928 | -0.19798 | 0.014541 | -0.0035783 | 0.0093396 | 0.051182 | -0.0096814 | 0.067543 | -61.2579 | 60.2417 | -61.2625 | -61.2579 | 60.1913 | 0.37537 | 0.17853 | 0.33875 | 60.3561 | -61.3678 | -0.027466 | -0.15106 | -0.022889 | -0.022889 | -0.20142 | -0.13275 | -0.036621 | 0.004577 | 61.4136 | 61.5738 | 121.4264 | 121.4767 | -0.022889 | 121.5912 | 61.6104 | -0.13275 | 121.4767 | -0.022889 | 61.6104 | 121.4264 | 121.5912 | -121.6553 | -121.7606
669.6719 | 121.8704 | -61.2625 | 60.3607 | -0.21324 | 0.015396 | 0.0011215 | 0.0089124 | 0.050114 | -0.0083996 | 0.065834 | -61.3358 | 60.2554 | -61.2808 | -61.3449 | 60.0952 | 0.2655 | 0.25177 | 0.21973 | 60.379 | -61.3998 | -0.018311 | -0.10529 | -0.073242 | -0.082398 | -0.2655 | -0.13733 | 0.01831 | -0.054931 | 61.5143 | 61.4822 | 121.3577 | 121.5179 | -0.073242 | 121.6415 | 61.528 | -0.13733 | 121.5179 | -0.073242 | 61.528 | 121.3577 | 121.6415 | -121.6415 | -121.7606
671.3438 | 121.9482 | -61.2671 | 60.2737 | 0.13008 | 0.015823 | 0.0043259 | 0.011689 | 0.053532 | -0.008827 | 0.069466 | -61.4548 | 60.1318 | -61.4319 | -61.4685 | 59.967 | 0.004578 | -0.13275 | -0.14648 | 60.2737 | -61.4639 | -0.16479 | -0.14191 | -0.18768 | -0.20142 | -0.3067 | -0.19684 | 0 | -0.022888 | 61.1343 | 61.1206 | 121.2341 | 121.3989 | -0.18768 | 121.5408 | 61.2717 | -0.19684 | 121.3989 | -0.18768 | 61.2717 | 121.2341 | 121.5408 | -121.7056 | -121.7377
673.0938 | 121.9528 | -61.2717 | 60.26 | 0.10719 | 0.012191 | 5.3338e-05 | 0.010408 | 0.053318 | -0.011818 | 0.06498 | -61.4594 | 60.1501 | -61.441 | -61.4914 | 59.9716 | 0.032043 | -0.11902 | -0.13275 | 60.2737 | -61.4914 | -0.16937 | -0.10986 | -0.18768 | -0.21973 | -0.28839 | -0.21973 | 0.013733 | -0.018311 | 61.1526 | 61.1389 | 121.2433 | 121.4218 | -0.18768 | 121.5454 | 61.3037 | -0.21973 | 121.4218 | -0.18768 | 61.3037 | 121.2433 | 121.5454 | -121.7011 | -121.7514
674.7812 | 121.8521 | -61.2625 | 60.3333 | -0.16747 | 0.015182 | 0.0017623 | 0.0076306 | 0.052037 | -0.011818 | 0.065407 | -61.3541 | 60.2371 | -61.3403 | -61.377 | 60.0815 | 0.24719 | 0.20599 | 0.16022 | 60.3287 | -61.3998 | -0.07782 | -0.09613 | -0.091553 | -0.11444 | -0.25177 | -0.13733 | -0.004578 | -0.013733 | 61.4685 | 61.4227 | 121.344 | 121.4996 | -0.091553 | 121.5912 | 61.5097 | -0.13733 | 121.4996 | -0.091553 | 61.5097 | 121.344 | 121.5912 | -121.6736 | -121.7331
676.5312 | 121.9437 | -61.2808 | 60.2829 | 0.11482 | 0.011978 | 0.0036849 | 0.0089124 | 0.053746 | -0.0094678 | 0.069039 | -61.4365 | 60.1776 | -61.4044 | -61.4639 | 59.9899 | 0.036621 | -0.13733 | -0.1236 | 60.3058 | -61.4319 | -0.1236 | -0.10529 | -0.15564 | -0.18311 | -0.29297 | -0.15106 | 0.022888 | -0.032043 | 61.1435 | 61.1572 | 121.2708 | 121.4584 | -0.15564 | 121.5866 | 61.3174 | -0.15106 | 121.4584 | -0.15564 | 61.3174 | 121.2708 | 121.5866 | -121.6873 | -121.7148
678.2812 | 121.9437 | -61.2534 | 60.3058 | 0.12245 | 0.013473 | 0.0015487 | 0.0095532 | 0.053746 | -0.0075452 | 0.068611 | -61.4227 | 60.1776 | -61.409 | -61.4639 | 59.9945 | 0.045776 | -0.19684 | -0.1236 | 60.2554 | -61.4502 | -0.15564 | -0.12817 | -0.16937 | -0.21057 | -0.31128 | -0.19684 | -0.050354 | -0.013732 | 61.0565 | 61.1298 | 121.2479 | 121.431 | -0.16937 | 121.5088 | 61.2991 | -0.19684 | 121.431 | -0.16937 | 61.2991 | 121.2479 | 121.5088 | -121.7148 | -121.756
680.0312 | 121.8521 | -61.2213 | 60.4431 | -0.13695 | 0.011764 | -0.0022965 | 0.0037854 | 0.050328 | -0.0096814 | 0.06733 | -61.2534 | 60.2234 | -61.2671 | -61.2625 | 60.2234 | 0.36621 | 0.027466 | 0.3479 | 60.3241 | -61.3586 | -0.045777 | -0.21973 | -0.032044 | -0.041199 | -0.21973 | -0.13733 | -0.11902 | 0.013733 | 61.2488 | 61.5692 | 121.4447 | 121.4447 | -0.032044 | 121.5454 | 61.5875 | -0.13733 | 121.4447 | -0.032044 | 61.5875 | 121.4447 | 121.5454 | -121.7102 | -121.8018
681.7188 | 121.8155 | -61.3266 | 60.3195 | -0.17509 | 0.018173 | -0.0010147 | 0.011049 | 0.053318 | -0.0092542 | 0.066689 | -61.3174 | 60.2417 | -61.3312 | -61.3632 | 60.0815 | 0.23346 | 0.086975 | 0.1236 | 60.3195 | -61.4319 | -0.004578 | -0.07782 | 0.009155 | -0.036621 | -0.23804 | -0.10529 | 0 | 0.013733 | 61.4136 | 61.4502 | 121.4081 | 121.5683 | 0.009155 | 121.6461 | 61.5601 | -0.10529 | 121.5683 | 0.009155 | 61.5601 | 121.4081 | 121.6461 | -121.6507 | -121.7514
683.4688 | 121.8338 | -61.3129 | 60.3012 | -0.083542 | 0.012405 | 0.0034713 | 0.010621 | 0.0546 | -0.01075 | 0.066262 | -61.3358 | 60.1456 | -61.3861 | -61.3724 | 60.0769 | 0.18768 | -0.013733 | 0.064087 | 60.3104 | -61.4044 | -0.073242 | -0.15564 | -0.022888 | -0.059509 | -0.2243 | -0.091553 | 0.009156 | 0.050354 | 61.2991 | 61.377 | 121.3898 | 121.4584 | -0.022888 | 121.6232 | 61.5005 | -0.091553 | 121.4584 | -0.022888 | 61.5005 | 121.3898 | 121.6232 | -121.6873 | -121.7056
685.2344 | 121.8246 | -61.2488 | 60.4202 | -0.17509 | 0.011978 | -0.0018693 | 0.0046398 | 0.053105 | -0.0094678 | 0.067757 | -61.2396 | 60.228 | -61.2442 | -61.2717 | 60.2142 | 0.37994 | 0.10529 | 0.34332 | 60.3241 | -61.3678 | 0.004577 | -0.19226 | 0.009155 | -0.022888 | -0.20599 | -0.11902 | -0.09613 | 0.004578 | 61.3541 | 61.5921 | 121.463 | 121.4767 | 0.009155 | 121.5729 | 61.6287 | -0.11902 | 121.4767 | 0.009155 | 61.6287 | 121.463 | 121.5729 | -121.6644 | -121.788
686.9844 | 121.9345 | -61.2854 | 60.3058 | 0.038529 | 0.01326 | -0.0018693 | 0.013185 | 0.053532 | -0.011177 | 0.067543 | -61.4227 | 60.2005 | -61.3998 | -61.496 | 59.9579 | 0.027466 | -0.059509 | -0.1236 | 60.2875 | -61.4822 | -0.11444 | -0.10529 | -0.13733 | -0.21057 | -0.3479 | -0.19684 | -0.01831 | -0.022888 | 61.2259 | 61.1618 | 121.2433 | 121.4859 | -0.13733 | 121.5729 | 61.3129 | -0.19684 | 121.4859 | -0.13733 | 61.3129 | 121.2433 | 121.5729 | -121.7056 | -121.788
688.6719 | 121.8246 | -61.3174 | 60.3241 | -0.19035 | 0.014969 | 0.0047531 | 0.0076306 | 0.055241 | -0.012458 | 0.066689 | -61.3403 | 60.2142 | -61.3403 | -61.3724 | 60.0906 | 0.22888 | 0.10529 | 0.12817 | 60.3561 | -61.4044 | -0.022888 | -0.10986 | -0.022888 | -0.054931 | -0.23346 | -0.086975 | 0.032043 | 0 | 61.4227 | 61.4456 | 121.4081 | 121.5317 | -0.022888 | 121.6736 | 61.5463 | -0.086975 | 121.5317 | -0.022888 | 61.5463 | 121.4081 | 121.6736 | -121.6644 | -121.7285
690.4062 | 121.875 | -61.2717 | 60.3287 | -0.20561 | 0.01326 | 0.0030441 | 0.007417 | 0.052037 | -0.0090406 | 0.066689 | -61.3403 | 60.2692 | -61.3174 | -61.3907 | 60.0998 | 0.27008 | 0.2243 | 0.16479 | 60.347 | -61.409 | -0.045777 | -0.059509 | -0.068665 | -0.11902 | -0.22888 | -0.13733 | 0.018311 | -0.022888 | 61.496 | 61.4365 | 121.3715 | 121.5408 | -0.068665 | 121.6187 | 61.5417 | -0.13733 | 121.5408 | -0.068665 | 61.5417 | 121.3715 | 121.6187 | -121.6461 | -121.7377
692.1562 | 121.8567 | -61.3312 | 60.2966 | 0.0080111 | 0.014114 | 0.00090794 | 0.009126 | 0.055882 | -0.011818 | 0.066689 | -61.4044 | 60.1685 | -61.3953 | -61.4548 | 60.0128 | 0.07782 | -0.073242 | -0.064087 | 60.2829 | -61.4548 | -0.064087 | -0.12817 | -0.073242 | -0.1236 | -0.28381 | -0.1236 | -0.013733 | -0.009155 | 61.2579 | 61.2671 | 121.344 | 121.4996 | -0.073242 | 121.6141 | 61.409 | -0.1236 | 121.4996 | -0.073242 | 61.409 | 121.344 | 121.6141 | -121.6919 | -121.7514
693.8438 | 121.7972 | -61.3129 | 60.3195 | -0.10643 | 0.012619 | 0.0028305 | 0.0099804 | 0.053318 | -0.010963 | 0.066262 | -61.3358 | 60.1868 | -61.3678 | -61.3724 | 60.0861 | 0.22888 | 0.013733 | 0.082397 | 60.3287 | -61.4273 | -0.054932 | -0.13275 | -0.022888 | -0.059509 | -0.23346 | -0.11444 | 0.009155 | 0.032044 | 61.3266 | 61.3953 | 121.3989 | 121.4996 | -0.022888 | 121.6415 | 61.5417 | -0.11444 | 121.4996 | -0.022888 | 61.5417 | 121.3989 | 121.6415 | -121.6873 | -121.7468
695.5781 | 121.8109 | -61.2213 | 60.4202 | -0.20561 | 0.011978 | 5.3338e-05 | 0.0016492 | 0.052037 | -0.0083996 | 0.066262 | -61.235 | 60.2463 | -61.2076 | -61.2579 | 60.2234 | 0.38452 | 0.09613 | 0.35248 | 60.3149 | -61.3815 | 0.013732 | -0.17395 | -0.013733 | -0.036622 | -0.19684 | -0.16022 | -0.10529 | -0.027465 | 61.3174 | 61.5738 | 121.4447 | 121.4676 | -0.013733 | 121.5363 | 61.6058 | -0.16022 | 121.4676 | -0.013733 | 61.6058 | 121.4447 | 121.5363 | -121.6278 | -121.8018
697.3125 | 121.875 | -61.203 | 60.4202 | -0.12169 | 0.01326 | -0.0022965 | 0.0033582 | 0.050755 | -0.0092542 | 0.069893 | -61.2396 | 60.228 | -61.2625 | -61.2579 | 60.2142 | 0.34332 | 0.036621 | 0.32501 | 60.3287 | -61.377 | -0.059509 | -0.19226 | -0.036621 | -0.054932 | -0.20599 | -0.17395 | -0.091553 | 0.022888 | 61.2396 | 61.528 | 121.4172 | 121.431 | -0.036621 | 121.5317 | 61.5463 | -0.17395 | 121.431 | -0.036621 | 61.5463 | 121.4172 | 121.5317 | -121.6827 | -121.7972
699.0781 | 121.9574 | -61.1755 | 60.3973 | 0.02327 | 0.014969 | 0.00026694 | 0.0063488 | 0.051182 | -0.0092542 | 0.067116 | -61.3449 | 60.1959 | -61.3129 | -61.3632 | 60.1181 | 0.19684 | -0.045776 | 0.11902 | 60.3058 | -61.4319 | -0.13733 | -0.20142 | -0.16937 | -0.18768 | -0.27924 | -0.25635 | -0.091553 | -0.032044 | 61.1298 | 61.2946 | 121.2936 | 121.3715 | -0.16937 | 121.4813 | 61.3724 | -0.25635 | 121.3715 | -0.16937 | 61.3724 | 121.2936 | 121.4813 | -121.7102 | -121.8292
700.7656 | 121.8063 | -61.3083 | 60.3287 | -0.11406 | 0.012619 | 0.00026694 | 0.010621 | 0.052891 | -0.01075 | 0.068184 | -61.3403 | 60.2142 | -61.3724 | -61.3541 | 60.1044 | 0.23346 | 0.059509 | 0.13275 | 60.3149 | -61.409 | -0.064086 | -0.11444 | -0.032043 | -0.045776 | -0.2243 | -0.10071 | -0.013733 | 0.032043 | 61.3678 | 61.441 | 121.4127 | 121.5225 | -0.032043 | 121.6232 | 61.5417 | -0.10071 | 121.5225 | -0.032043 | 61.5417 | 121.4127 | 121.6232 | -121.701 | -121.7377
702.5 | 121.9528 | -61.2717 | 60.2966 | 0.099564 | 0.015182 | 0.0021895 | 0.011689 | 0.052037 | -0.010963 | 0.066902 | -61.4365 | 60.1501 | -61.4227 | -61.4639 | 60.0082 | 0.032043 | -0.15564 | -0.11444 | 60.2966 | -61.4685 | -0.15106 | -0.14648 | -0.16479 | -0.19226 | -0.28839 | -0.19684 | 0 | -0.013733 | 61.116 | 61.1572 | 121.2799 | 121.4218 | -0.16479 | 121.5683 | 61.3037 | -0.19684 | 121.4218 | -0.16479 | 61.3037 | 121.2799 | 121.5683 | -121.7194 | -121.7651
704.25 | 121.9666 | -61.2991 | 60.2875 | 0.11482 | 0.014969 | -0.0010147 | 0.010835 | 0.0546 | -0.01075 | 0.067543 | -61.4502 | 60.1318 | -61.409 | -61.4777 | 59.9808 | 0.009155 | -0.1236 | -0.12817 | 60.3149 | -61.4731 | -0.10986 | -0.15564 | -0.15106 | -0.17853 | -0.3067 | -0.17395 | 0.027465 | -0.041198 | 61.1755 | 61.171 | 121.2799 | 121.431 | -0.15106 | 121.6141 | 61.3083 | -0.17395 | 121.431 | -0.15106 | 61.3083 | 121.2799 | 121.6141 | -121.6965 | -121.7606
705.9219 | 121.8933 | -61.1664 | 60.4065 | -0.14458 | 0.013473 | -0.00058746 | 0.003999 | 0.052464 | -0.0090406 | 0.066689 | -61.235 | 60.2371 | -61.2442 | -61.2625 | 60.2097 | 0.33875 | 0.041199 | 0.31128 | 60.3195 | -61.3861 | -0.07782 | -0.16937 | -0.068664 | -0.09613 | -0.19684 | -0.21973 | -0.086975 | 0.009156 | 61.2076 | 61.4777 | 121.376 | 121.4035 | -0.068664 | 121.4859 | 61.5051 | -0.21973 | 121.4035 | -0.068664 | 61.5051 | 121.376 | 121.4859 | -121.6507 | -121.7926
707.6719 | 121.962 | -61.1847 | 60.3882 | 0.030899 | 0.011551 | 0.0017623 | 0.0048534 | 0.051823 | -0.010536 | 0.067116 | -61.3632 | 60.1318 | -61.3358 | -61.3449 | 60.1044 | 0.17395 | -0.073242 | 0.12817 | 60.3058 | -61.3998 | -0.15106 | -0.25635 | -0.17853 | -0.16022 | -0.28381 | -0.21515 | -0.082398 | -0.027466 | 61.1114 | 61.3129 | 121.2891 | 121.3165 | -0.17853 | 121.4905 | 61.3586 | -0.21515 | 121.3165 | -0.17853 | 61.3586 | 121.2891 | 121.4905 | -121.7239 | -121.788
709.4219 | 121.843 | -61.235 | 60.3973 | -0.2285 | 0.012619 | 0.00069434 | 0.0089124 | 0.050755 | -0.01139 | 0.067543 | -61.2534 | 60.2188 | -61.2579 | -61.2717 | 60.1959 | 0.35248 | 0.20142 | 0.29755 | 60.3607 | -61.377 | -0.022889 | -0.17853 | -0.018311 | -0.036621 | -0.20142 | -0.14191 | -0.036621 | 0.004578 | 61.4365 | 61.5326 | 121.431 | 121.4539 | -0.018311 | 121.5958 | 61.5875 | -0.14191 | 121.4539 | -0.018311 | 61.5875 | 121.431 | 121.5958 | -121.6553 | -121.7743
711.1719 | 121.8796 | -61.2625 | 60.347 | -0.25902 | 0.013687 | -0.0033647 | 0.008485 | 0.052677 | -0.013099 | 0.066689 | -61.3495 | 60.2646 | -61.3174 | -61.3724 | 60.0906 | 0.26093 | 0.25635 | 0.18768 | 60.3745 | -61.3724 | -0.054932 | -0.082398 | -0.086975 | -0.10986 | -0.25635 | -0.10986 | 0.027466 | -0.032043 | 61.5189 | 61.4502 | 121.3531 | 121.5271 | -0.086975 | 121.637 | 61.5234 | -0.10986 | 121.5271 | -0.086975 | 61.5234 | 121.3531 | 121.637 | -121.6644 | -121.7194
712.8594 | 121.8292 | -61.2396 | 60.4294 | -0.21324 | 0.014541 | -0.00058746 | 0.0059216 | 0.053318 | -0.0096814 | 0.066262 | -61.2167 | 60.2463 | -61.2625 | -61.2396 | 60.2097 | 0.37079 | 0.10529 | 0.37079 | 60.3561 | -61.3541 | -0.022888 | -0.1831 | 0.022888 | 0 | -0.21973 | -0.11444 | -0.073242 | 0.045776 | 61.3449 | 61.6104 | 121.4493 | 121.4859 | 0.022888 | 121.5958 | 61.6104 | -0.11444 | 121.4859 | 0.022888 | 61.6104 | 121.4493 | 121.5958 | -121.6919 | -121.7834
714.6094 | 121.9437 | -61.235 | 60.2966 | 0.099564 | 0.014969 | -0.00016026 | 0.011049 | 0.054814 | -0.011604 | 0.06797 | -61.409 | 60.1547 | -61.4227 | -61.4639 | 60.0037 | 0.036621 | -0.15106 | -0.1236 | 60.3012 | -61.4502 | -0.18768 | -0.14191 | -0.17395 | -0.22888 | -0.29297 | -0.21515 | 0.004577 | 0.013732 | 61.084 | 61.1114 | 121.2387 | 121.3898 | -0.17395 | 121.5363 | 61.2717 | -0.21515 | 121.3898 | -0.17395 | 61.2717 | 121.2387 | 121.5363 | -121.7194 | -121.7468
716.3594 | 121.8246 | -61.2167 | 60.4156 | -0.19035 | 0.01091 | 0.0024033 | 0.0059216 | 0.053105 | -0.008186 | 0.068184 | -61.2167 | 60.2509 | -61.2396 | -61.2167 | 60.2417 | 0.37079 | 0.10071 | 0.37079 | 60.3516 | -61.3724 | -0.022888 | -0.1648 | 0 | 0 | -0.17395 | -0.15564 | -0.064087 | 0.022888 | 61.3174 | 61.5875 | 121.4584 | 121.4676 | 0 | 121.5683 | 61.5875 | -0.15564 | 121.4676 | 0 | 61.5875 | 121.4584 | 121.5683 | -121.6553 | -121.788
718.0938 | 121.8018 | -61.3358 | 60.3012 | -0.068283 | 0.014969 | 0.0011215 | 0.012117 | 0.0546 | -0.011604 | 0.067116 | -61.3312 | 60.1593 | -61.3678 | -61.3586 | 60.0906 | 0.20142 | -0.004578 | 0.086975 | 60.3149 | -61.4136 | -0.032044 | -0.14191 | 0.004577 | -0.022889 | -0.21057 | -0.07782 | 0.013733 | 0.036621 | 61.3312 | 61.4227 | 121.4264 | 121.4951 | 0.004577 | 121.6507 | 61.5372 | -0.07782 | 121.4951 | 0.004577 | 61.5372 | 121.4264 | 121.6507 | -121.669 | -121.7148
719.7812 | 121.8521 | -61.2167 | 60.434 | -0.12169 | 0.014114 | -0.0010147 | 0.003999 | 0.050541 | -0.010322 | 0.066262 | -61.235 | 60.2417 | -61.2671 | -61.2488 | 60.2188 | 0.3479 | 0.013733 | 0.32959 | 60.3333 | -61.3861 | -0.050354 | -0.19226 | -0.01831 | -0.032043 | -0.21515 | -0.16937 | -0.10071 | 0.032044 | 61.2305 | 61.5463 | 121.4355 | 121.4584 | -0.01831 | 121.55 | 61.5646 | -0.16937 | 121.4584 | -0.01831 | 61.5646 | 121.4355 | 121.55 | -121.7011 | -121.8201
721.5156 | 121.9025 | -61.2488 | 60.3653 | 0.18349 | 0.011978 | 0.0026169 | 0.0095532 | 0.053318 | -0.009895 | 0.068825 | -61.322 | 60.0952 | -61.3678 | -61.3449 | 60.1135 | 0.14648 | -0.29755 | 0.027466 | 60.2463 | -61.441 | -0.11902 | -0.27008 | -0.073242 | -0.096131 | -0.25177 | -0.19226 | -0.11902 | 0.045777 | 60.9512 | 61.2762 | 121.3623 | 121.344 | -0.073242 | 121.4951 | 61.3953 | -0.19226 | 121.344 | -0.073242 | 61.3953 | 121.3623 | 121.4951 | -121.7331 | -121.8063
723.2656 | 121.8979 | -61.2167 | 60.3607 | 0.16823 | 0.012405 | 0.0053939 | 0.0097668 | 0.053105 | -0.010963 | 0.067116 | -61.3312 | 60.0723 | -61.3815 | -61.3449 | 60.1089 | 0.13275 | -0.30212 | 0.041199 | 60.2509 | -61.4227 | -0.1648 | -0.28839 | -0.11444 | -0.12817 | -0.25177 | -0.20599 | -0.10986 | 0.050354 | 60.9146 | 61.2579 | 121.3257 | 121.2891 | -0.11444 | 121.4676 | 61.3495 | -0.20599 | 121.2891 | -0.11444 | 61.3495 | 121.3257 | 121.4676 | -121.7422 | -121.7834
724.9531 | 121.8155 | -61.3449 | 60.3149 | -0.091171 | 0.013473 | 0.0019759 | 0.012971 | 0.052891 | -0.012886 | 0.066475 | -61.3403 | 60.2142 | -61.3815 | -61.3541 | 60.0861 | 0.20599 | 0.013733 | 0.10071 | 60.2921 | -61.4227 | -0.036621 | -0.10071 | 0.004578 | -0.009155 | -0.22888 | -0.077819 | -0.022888 | 0.041199 | 61.3586 | 61.4456 | 121.431 | 121.5591 | 0.004578 | 121.637 | 61.5509 | -0.077819 | 121.5591 | 0.004578 | 61.5509 | 121.431 | 121.637 | -121.6965 | -121.7377
726.7031 | 121.962 | -61.2717 | 60.2737 | 0.12245 | 0.016464 | -0.0018693 | 0.012544 | 0.054173 | -0.011604 | 0.066475 | -61.441 | 60.1547 | -61.3998 | -61.4685 | 60.0037 | 0.041199 | -0.14648 | -0.13733 | 60.3287 | -61.4502 | -0.12817 | -0.11902 | -0.16937 | -0.19684 | -0.27008 | -0.17853 | 0.054931 | -0.041199 | 61.1252 | 61.1343 | 121.2753 | 121.4264 | -0.16937 | 121.6003 | 61.3129 | -0.17853 | 121.4264 | -0.16937 | 61.3129 | 121.2753 | 121.6003 | -121.6736 | -121.7239
728.4531 | 121.8338 | -61.3083 | 60.3104 | -0.19035 | 0.01326 | -0.0014419 | 0.0082714 | 0.052464 | -0.013099 | 0.068611 | -61.3403 | 60.2509 | -61.3449 | -61.3632 | 60.0861 | 0.23804 | 0.11444 | 0.14191 | 60.3241 | -61.4227 | -0.036621 | -0.05951 | -0.032043 | -0.054931 | -0.2243 | -0.11444 | 0.013733 | 0.004578 | 61.4227 | 61.4502 | 121.3943 | 121.5591 | -0.032043 | 121.6324 | 61.5463 | -0.11444 | 121.5591 | -0.032043 | 61.5463 | 121.3943 | 121.6324 | -121.6553 | -121.7331
730.1562 | 121.8292 | -61.3174 | 60.3378 | -0.20561 | 0.014328 | 0.0030441 | 0.010408 | 0.051182 | -0.012245 | 0.066048 | -61.3495 | 60.2234 | -61.3312 | -61.3586 | 60.0906 | 0.24719 | 0.09613 | 0.13733 | 60.347 | -61.4273 | -0.013733 | -0.11444 | -0.032043 | -0.041199 | -0.24719 | -0.10986 | 0.009155 | -0.01831 | 61.4136 | 61.4548 | 121.4081 | 121.5408 | -0.032043 | 121.6644 | 61.5646 | -0.10986 | 121.5408 | -0.032043 | 61.5646 | 121.4081 | 121.6644 | -121.669 | -121.7651
731.8906 | 121.843 | -61.3037 | 60.3058 | -0.16747 | 0.014328 | -0.00058746 | 0.0095532 | 0.052037 | -0.011177 | 0.066475 | -61.3449 | 60.2509 | -61.3174 | -61.3541 | 60.0998 | 0.24719 | 0.15564 | 0.13733 | 60.3607 | -61.3953 | -0.013733 | -0.054932 | -0.041199 | -0.050354 | -0.20599 | -0.091553 | 0.054932 | -0.027466 | 61.4594 | 61.441 | 121.4035 | 121.5546 | -0.041199 | 121.6644 | 61.5509 | -0.091553 | 121.5546 | -0.041199 | 61.5509 | 121.4035 | 121.6644 | -121.6232 | -121.701
733.6406 | 121.9254 | -61.235 | 60.3424 | 0.17586 | 0.014328 | -0.0020829 | 0.0086988 | 0.054386 | -0.010109 | 0.065193 | -61.3815 | 60.1456 | -61.3815 | -61.3998 | 60.0723 | 0.10529 | -0.2655 | -0.045776 | 60.26 | -61.4548 | -0.14649 | -0.19684 | -0.14649 | -0.1648 | -0.27008 | -0.21973 | -0.082397 | 0 | 60.9695 | 61.1893 | 121.3074 | 121.3806 | -0.14649 | 121.4951 | 61.3403 | -0.21973 | 121.3806 | -0.14649 | 61.3403 | 121.3074 | 121.4951 | -121.7239 | -121.7972
735.3906 | 121.907 | -61.2305 | 60.379 | 0.1606 | 0.012405 | 5.3338e-05 | 0.0067762 | 0.052891 | -0.0092542 | 0.067543 | -61.3266 | 60.1273 | -61.3449 | -61.3678 | 60.1044 | 0.13733 | -0.31128 | 0.013733 | 60.2005 | -61.441 | -0.11444 | -0.25177 | -0.09613 | -0.13733 | -0.27466 | -0.21057 | -0.17853 | 0.018311 | 60.9192 | 61.2442 | 121.3348 | 121.3577 | -0.09613 | 121.431 | 61.3678 | -0.21057 | 121.3577 | -0.09613 | 61.3678 | 121.3348 | 121.431 | -121.7239 | -121.8201
737.1406 | 121.875 | -61.2762 | 60.347 | -0.25902 | 0.014541 | 0.0013351 | 0.008485 | 0.049046 | -0.008186 | 0.067116 | -61.3403 | 60.2875 | -61.3129 | -61.3632 | 60.0998 | 0.27466 | 0.27008 | 0.18768 | 60.4019 | -61.4182 | -0.036621 | -0.059509 | -0.064087 | -0.086975 | -0.24719 | -0.14191 | 0.054932 | -0.027466 | 61.5463 | 61.4639 | 121.376 | 121.5637 | -0.064087 | 121.6782 | 61.5509 | -0.14191 | 121.5637 | -0.064087 | 61.5509 | 121.376 | 121.6782 | -121.6599 | -121.7651
738.8281 | 121.9345 | -61.2442 | 60.3012 | 0.13008 | 0.015396 | -0.0042191 | 0.0099804 | 0.053318 | -0.011177 | 0.06797 | -61.4182 | 60.1273 | -61.4182 | -61.4456 | 60.0082 | 0.050354 | -0.21057 | -0.10071 | 60.2646 | -61.4273 | -0.17395 | -0.17395 | -0.17395 | -0.20142 | -0.29297 | -0.1831 | -0.036621 | 0 | 61.0336 | 61.1435 | 121.2524 | 121.3715 | -0.17395 | 121.5088 | 61.2946 | -0.1831 | 121.3715 | -0.17395 | 61.2946 | 121.2524 | 121.5088 | -121.7194 | -121.7285
740.5625 | 121.9116 | -61.2305 | 60.3424 | 0.16823 | 0.0139 | 0.0024033 | 0.0095532 | 0.055241 | -0.010963 | 0.06797 | -61.377 | 60.1547 | -61.3861 | -61.3907 | 60.0861 | 0.11902 | -0.2655 | -0.022888 | 60.2737 | -61.4319 | -0.15564 | -0.18768 | -0.14648 | -0.16022 | -0.25635 | -0.20142 | -0.068664 | 0.009155 | 60.965 | 61.2076 | 121.3165 | 121.3852 | -0.14648 | 121.5042 | 61.3495 | -0.20142 | 121.3852 | -0.14648 | 61.3495 | 121.3165 | 121.5042 | -121.7285 | -121.7743
742.2969 | 121.9299 | -61.29 | 60.2829 | 0.069046 | 0.012832 | 0.0032577 | 0.012544 | 0.053959 | -0.009895 | 0.064766 | -61.4273 | 60.1959 | -61.4227 | -61.4639 | 59.9945 | 0.041199 | -0.073242 | -0.1236 | 60.3058 | -61.4685 | -0.13275 | -0.086975 | -0.13733 | -0.17395 | -0.28839 | -0.17853 | 0.022888 | -0.004578 | 61.2167 | 61.1664 | 121.2845 | 121.4859 | -0.13733 | 121.5958 | 61.3312 | -0.17853 | 121.4859 | -0.13733 | 61.3312 | 121.2845 | 121.5958 | -121.7056 | -121.7514
743.9844 | 121.8658 | -61.29 | 60.347 | -0.19798 | 0.014755 | -0.00016026 | 0.0076306 | 0.051396 | -0.011604 | 0.069466 | -61.3495 | 60.2692 | -61.3541 | -61.3815 | 60.0815 | 0.25177 | 0.21515 | 0.16479 | 60.3836 | -61.3953 | -0.064087 | -0.07782 | -0.059509 | -0.091553 | -0.2655 | -0.10529 | 0.036621 | 0.004578 | 61.5051 | 61.4548 | 121.3715 | 121.5591 | -0.059509 | 121.6736 | 61.5417 | -0.10529 | 121.5591 | -0.059509 | 61.5417 | 121.3715 | 121.6736 | -121.701 | -121.7422
745.7344 | 121.8567 | -61.2167 | 60.4202 | -0.14458 | 0.013473 | 0.0011215 | 0.0027172 | 0.048832 | -0.0090406 | 0.069893 | -61.2534 | 60.2142 | -61.2762 | -61.2488 | 60.228 | 0.3479 | 0.036621 | 0.34332 | 60.3058 | -61.3586 | -0.059509 | -0.20599 | -0.036621 | -0.032043 | -0.19226 | -0.14191 | -0.11444 | 0.022888 | 61.2534 | 61.5601 | 121.4447 | 121.431 | -0.036621 | 121.5225 | 61.5646 | -0.14191 | 121.431 | -0.036621 | 61.5646 | 121.4447 | 121.5225 | -121.6965 | -121.7789
747.4844 | 121.8475 | -61.2991 | 60.3333 | -0.19035 | 0.012191 | 0.0011215 | 0.011262 | 0.051823 | -0.01075 | 0.068398 | -61.3541 | 60.228 | -61.3495 | -61.3678 | 60.0998 | 0.23346 | 0.15106 | 0.13733 | 60.3287 | -61.4227 | -0.050354 | -0.10529 | -0.054932 | -0.068665 | -0.23346 | -0.1236 | -0.004578 | -0.004578 | 61.4502 | 61.4365 | 121.3989 | 121.5271 | -0.054932 | 121.6278 | 61.5326 | -0.1236 | 121.5271 | -0.054932 | 61.5326 | 121.3989 | 121.6278 | -121.6827 | -121.756
749.1719 | 121.8613 | -61.2671 | 60.347 | -0.22087 | 0.012832 | 0.0011215 | 0.0050672 | 0.050968 | -0.0096814 | 0.068611 | -61.3632 | 60.2646 | -61.3129 | -61.3632 | 60.1227 | 0.27466 | 0.27924 | 0.2243 | 60.379 | -61.4044 | -0.045776 | -0.082398 | -0.09613 | -0.09613 | -0.2243 | -0.13733 | 0.032043 | -0.050354 | 61.5463 | 61.4914 | 121.3898 | 121.5317 | -0.09613 | 121.6461 | 61.5417 | -0.13733 | 121.5317 | -0.09613 | 61.5417 | 121.3898 | 121.6461 | -121.6599 | -121.7514
750.9219 | 121.8475 | -61.322 | 60.3241 | -0.20561 | 0.013687 | 0.0013351 | 0.011476 | 0.053105 | -0.01139 | 0.066689 | -61.3541 | 60.2463 | -61.3678 | -61.3678 | 60.0906 | 0.24719 | 0.10071 | 0.12817 | 60.3058 | -61.4365 | -0.045777 | -0.07782 | -0.032044 | -0.045777 | -0.23346 | -0.11444 | -0.018311 | 0.013733 | 61.4227 | 61.4502 | 121.4127 | 121.5683 | -0.032044 | 121.6278 | 61.5692 | -0.11444 | 121.5683 | -0.032044 | 61.5692 | 121.4127 | 121.6278 | -121.6919 | -121.7606
752.6719 | 121.9437 | -61.2762 | 60.2875 | 0.053787 | 0.012619 | -0.0022965 | 0.0095532 | 0.051823 | -0.0077588 | 0.068825 | -61.4456 | 60.1685 | -61.4044 | -61.5051 | 59.9625 | 0.036621 | -0.10986 | -0.1236 | 60.2646 | -61.5005 | -0.12817 | -0.11902 | -0.16937 | -0.22888 | -0.32501 | -0.2243 | -0.022889 | -0.041199 | 61.1664 | 61.1526 | 121.2387 | 121.4447 | -0.16937 | 121.5408 | 61.3129 | -0.2243 | 121.4447 | -0.16937 | 61.3129 | 121.2387 | 121.5408 | -121.6919 | -121.788
754.3594 | 121.8933 | -61.29 | 60.3516 | -0.23613 | 0.015182 | -0.0025101 | 0.0067762 | 0.051182 | -0.006477 | 0.06733 | -61.3495 | 60.2875 | -61.2854 | -61.3907 | 60.0906 | 0.2655 | 0.23346 | 0.17853 | 60.3745 | -61.3861 | 0.004578 | -0.064086 | -0.059509 | -0.10071 | -0.26093 | -0.09613 | 0.022889 | -0.064087 | 61.5234 | 61.4685 | 121.3806 | 121.5775 | -0.059509 | 121.6644 | 61.5555 | -0.09613 | 121.5775 | -0.059509 | 61.5555 | 121.3806 | 121.6644 | -121.637 | -121.7377
756.0938 | 121.9482 | -61.203 | 60.3882 | 0.00038159 | 0.013687 | -0.0016557 | 0.0029308 | 0.050328 | -0.008827 | 0.068825 | -61.3403 | 60.2234 | -61.3037 | -61.3586 | 60.1318 | 0.23804 | 0.004578 | 0.17395 | 60.2692 | -61.4319 | -0.10071 | -0.1648 | -0.13733 | -0.15564 | -0.25635 | -0.22888 | -0.11902 | -0.036621 | 61.2076 | 61.377 | 121.3348 | 121.4264 | -0.13733 | 121.4722 | 61.441 | -0.22888 | 121.4264 | -0.13733 | 61.441 | 121.3348 | 121.4722 | -121.6919 | -121.8201
757.8594 | 121.9666 | -61.2808 | 60.2783 | 0.12245 | 0.015823 | 0.0047531 | 0.012758 | 0.053746 | -0.010322 | 0.06733 | -61.441 | 60.1913 | -61.4182 | -61.4868 | 59.9716 | 0.018311 | -0.13733 | -0.13733 | 60.2783 | -61.4777 | -0.13733 | -0.086975 | -0.16022 | -0.20599 | -0.3067 | -0.19684 | 0 | -0.022888 | 61.1435 | 61.1435 | 121.2524 | 121.4722 | -0.16022 | 121.5591 | 61.2991 | -0.19684 | 121.4722 | -0.16022 | 61.2991 | 121.2524 | 121.5591 | -121.6965 | -121.756
759.5469 | 121.9574 | -61.2762 | 60.2783 | 0.099564 | 0.013687 | -0.00037386 | 0.011262 | 0.054386 | -0.012031 | 0.069466 | -61.4456 | 60.1456 | -61.4365 | -61.5051 | 59.9808 | 0.018311 | -0.12817 | -0.14191 | 60.3058 | -61.4822 | -0.16022 | -0.13275 | -0.16937 | -0.22888 | -0.29755 | -0.20599 | 0.027466 | -0.009156 | 61.1481 | 61.1343 | 121.257 | 121.4218 | -0.16937 | 121.582 | 61.2946 | -0.20599 | 121.4218 | -0.16937 | 61.2946 | 121.257 | 121.582 | -121.7148 | -121.7606
761.2812 | 121.9437 | -61.2946 | 60.2875 | 0.13771 | 0.013046 | -0.00080106 | 0.0097668 | 0.054386 | -0.011604 | 0.069466 | -61.4502 | 60.1639 | -61.4182 | -61.496 | 59.9899 | 0.032043 | -0.14191 | -0.15106 | 60.2921 | -61.4685 | -0.1236 | -0.1236 | -0.15564 | -0.20142 | -0.29755 | -0.17395 | 0.004577 | -0.032043 | 61.1526 | 61.1435 | 121.2845 | 121.4584 | -0.15564 | 121.5866 | 61.3266 | -0.17395 | 121.4584 | -0.15564 | 61.3266 | 121.2845 | 121.5866 | -121.7056 | -121.756
763.0469 | 121.9711 | -61.2122 | 60.3699 | 0.046158 | 0.014114 | -0.0012283 | 0.003999 | 0.050328 | -0.010536 | 0.065193 | -61.3449 | 60.2142 | -61.2946 | -61.3586 | 60.1089 | 0.17853 | -0.082397 | 0.12817 | 60.2875 | -61.4319 | -0.082398 | -0.15564 | -0.13275 | -0.14648 | -0.26093 | -0.21973 | -0.082397 | -0.050354 | 61.1298 | 61.3403 | 121.3211 | 121.4264 | -0.13275 | 121.4996 | 61.3907 | -0.21973 | 121.4264 | -0.13275 | 61.3907 | 121.3211 | 121.4996 | -121.6644 | -121.8018
764.7344 | 121.9299 | -61.1847 | 60.3882 | -0.014877 | 0.015609 | 0.0026169 | 0.005708 | 0.052891 | -0.0092542 | 0.066048 | -61.322 | 60.2417 | -61.3037 | -61.3495 | 60.1227 | 0.22888 | 0.009155 | 0.16022 | 60.3104 | -61.4227 | -0.11902 | -0.14649 | -0.13733 | -0.1648 | -0.2655 | -0.23804 | -0.07782 | -0.01831 | 61.1938 | 61.3449 | 121.3074 | 121.4264 | -0.13733 | 121.4951 | 61.4136 | -0.23804 | 121.4264 | -0.13733 | 61.4136 | 121.3074 | 121.4951 | -121.6919 | -121.8109
766.4688 | 121.9299 | -61.2076 | 60.3745 | 0.10719 | 0.012832 | 0.0024033 | 0.0078442 | 0.052464 | -0.011818 | 0.066902 | -61.322 | 60.1273 | -61.3541 | -61.3495 | 60.1318 | 0.16479 | -0.16479 | 0.091553 | 60.3058 | -61.409 | -0.14648 | -0.24719 | -0.11444 | -0.14191 | -0.24262 | -0.20142 | -0.068665 | 0.032044 | 61.0428 | 61.2991 | 121.3394 | 121.3348 | -0.11444 | 121.5134 | 61.3724 | -0.20142 | 121.3348 | -0.11444 | 61.3724 | 121.3394 | 121.5134 | -121.7285 | -121.7834
768.2031 | 121.907 | -61.203 | 60.4111 | -0.11406 | 0.011978 | -0.0022965 | 0.0050672 | 0.051823 | -0.0086132 | 0.065193 | -61.2442 | 60.2554 | -61.2854 | -61.2579 | 60.2051 | 0.35248 | 0.041199 | 0.31586 | 60.3333 | -61.3724 | -0.082397 | -0.15564 | -0.041199 | -0.054932 | -0.20599 | -0.16937 | -0.07782 | 0.041198 | 61.2442 | 61.5189 | 121.4081 | 121.4584 | -0.041199 | 121.5363 | 61.5555 | -0.16937 | 121.4584 | -0.041199 | 61.5555 | 121.4081 | 121.5363 | -121.6965 | -121.7834
769.9531 | 121.9254 | -61.2488 | 60.3241 | 0.19875 | 0.015182 | 0.00048074 | 0.014039 | 0.053318 | -0.011177 | 0.065834 | -61.3998 | 60.173 | -61.3907 | -61.3953 | 60.0357 | 0.07782 | -0.25635 | -0.050354 | 60.2646 | -61.4868 | -0.14191 | -0.15106 | -0.15106 | -0.14648 | -0.28839 | -0.23804 | -0.05951 | -0.009155 | 60.9924 | 61.1984 | 121.2845 | 121.4218 | -0.15106 | 121.5134 | 61.3266 | -0.23804 | 121.4218 | -0.15106 | 61.3266 | 121.2845 | 121.5134 | -121.7148 | -121.8109
771.625 | 121.9666 | -61.2625 | 60.3012 | 0.13008 | 0.014541 | -0.0018693 | 0.013185 | 0.05225 | -0.009895 | 0.067116 | -61.4319 | 60.1913 | -61.4456 | -61.4594 | 59.9991 | 0.032043 | -0.12817 | -0.11902 | 60.2829 | -61.496 | -0.18311 | -0.10986 | -0.16937 | -0.19684 | -0.30212 | -0.23346 | -0.01831 | 0.013733 | 61.1343 | 61.1435 | 121.2616 | 121.4539 | -0.16937 | 121.5454 | 61.2946 | -0.23346 | 121.4539 | -0.16937 | 61.2946 | 121.2616 | 121.5454 | -121.7468 | -121.7972
773.375 | 121.9437 | -61.2762 | 60.3012 | 0.099564 | 0.015609 | 0.0034713 | 0.01233 | 0.05225 | -0.010536 | 0.069252 | -61.4227 | 60.173 | -61.4227 | -61.4456 | 60.0037 | 0.036621 | -0.15106 | -0.10986 | 60.2783 | -61.4868 | -0.14648 | -0.12817 | -0.14648 | -0.16937 | -0.29755 | -0.21057 | -0.022888 | 0 | 61.1252 | 61.1664 | 121.2799 | 121.4493 | -0.14648 | 121.5546 | 61.3129 | -0.21057 | 121.4493 | -0.14648 | 61.3129 | 121.2799 | 121.5546 | -121.7239 | -121.788
775.125 | 121.8887 | -61.2488 | 60.3516 | -0.19798 | 0.015609 | -0.0016557 | 0.0067762 | 0.051823 | -0.0092542 | 0.067543 | -61.3358 | 60.2646 | -61.3358 | -61.3586 | 60.1135 | 0.2655 | 0.26093 | 0.21057 | 60.4156 | -61.4044 | -0.086975 | -0.086975 | -0.086975 | -0.10986 | -0.23804 | -0.15564 | 0.064087 | 0 | 61.5097 | 61.4594 | 121.3623 | 121.5134 | -0.086975 | 121.6644 | 61.5143 | -0.15564 | 121.5134 | -0.086975 | 61.5143 | 121.3623 | 121.6644 | -121.6873 | -121.756
776.8125 | 121.9162 | -61.2305 | 60.3378 | 0.11482 | 0.014969 | 0.0019759 | 0.0093396 | 0.0546 | -0.012458 | 0.066048 | -61.3449 | 60.1456 | -61.3907 | -61.3541 | 60.1181 | 0.12817 | -0.28839 | 0.009155 | 60.2371 | -61.4502 | -0.16022 | -0.19226 | -0.11444 | -0.1236 | -0.21973 | -0.21973 | -0.10071 | 0.045776 | 60.9421 | 61.2396 | 121.3486 | 121.376 | -0.11444 | 121.4676 | 61.3586 | -0.21973 | 121.376 | -0.11444 | 61.3586 | 121.3486 | 121.4676 | -121.7285 | -121.788
778.5625 | 121.9162 | -61.2488 | 60.3699 | 0.13008 | 0.013687 | 0.0038985 | 0.0069898 | 0.053746 | -0.010322 | 0.06797 | -61.2991 | 60.1456 | -61.3495 | -61.3358 | 60.1273 | 0.16479 | -0.24261 | 0.054932 | 60.2737 | -61.441 | -0.10071 | -0.2243 | -0.050354 | -0.086975 | -0.24262 | -0.19226 | -0.09613 | 0.050354 | 61.0062 | 61.3037 | 121.376 | 121.3943 | -0.050354 | 121.5225 | 61.4136 | -0.19226 | 121.3943 | -0.050354 | 61.4136 | 121.376 | 121.5225 | -121.7194 | -121.8109
780.3281 | 121.8475 | -61.2946 | 60.3241 | -0.014877 | 0.013473 | -0.0018693 | 0.012117 | 0.051823 | -0.012245 | 0.068398 | -61.3678 | 60.1913 | -61.4044 | -61.4182 | 60.0311 | 0.11902 | -0.07782 | -0.018311 | 60.2875 | -61.4731 | -0.10986 | -0.13275 | -0.073242 | -0.1236 | -0.29297 | -0.17853 | -0.036621 | 0.036621 | 61.2167 | 61.2762 | 121.3257 | 121.4859 | -0.073242 | 121.582 | 61.4136 | -0.17853 | 121.4859 | -0.073242 | 61.4136 | 121.3257 | 121.582 | -121.7285 | -121.7972
782.0156 | 121.9208 | -61.2442 | 60.3333 | 0.14534 | 0.015182 | -0.0014419 | 0.0095532 | 0.053105 | -0.011818 | 0.06797 | -61.3174 | 60.1456 | -61.3586 | -61.3632 | 60.0998 | 0.14648 | -0.31586 | 0.022888 | 60.2325 | -61.441 | -0.11444 | -0.18768 | -0.073242 | -0.11902 | -0.23346 | -0.19684 | -0.10071 | 0.041199 | 60.9283 | 61.2671 | 121.344 | 121.3898 | -0.073242 | 121.4767 | 61.3907 | -0.19684 | 121.3898 | -0.073242 | 61.3907 | 121.344 | 121.4767 | -121.6919 | -121.7743
783.7656 | 121.9162 | -61.2488 | 60.3607 | 0.16823 | 0.014541 | 0.0021895 | 0.009126 | 0.054386 | -0.010963 | 0.069252 | -61.3266 | 60.1364 | -61.3541 | -61.3495 | 60.1181 | 0.14648 | -0.28381 | 0.041199 | 60.26 | -61.4273 | -0.10529 | -0.2243 | -0.07782 | -0.10071 | -0.24262 | -0.17853 | -0.10071 | 0.027466 | 60.965 | 61.29 | 121.3669 | 121.3852 | -0.07782 | 121.5088 | 61.3953 | -0.17853 | 121.3852 | -0.07782 | 61.3953 | 121.3669 | 121.5088 | -121.7148 | -121.788
785.5156 | 121.9482 | -61.1664 | 60.3973 | 0.00038159 | 0.012832 | 0.0028305 | 0.0050672 | 0.052037 | -0.011177 | 0.064766 | -61.3312 | 60.2234 | -61.3037 | -61.3495 | 60.1227 | 0.20142 | -0.004578 | 0.16022 | 60.3195 | -61.409 | -0.13733 | -0.17395 | -0.16479 | -0.18311 | -0.27466 | -0.24262 | -0.07782 | -0.027466 | 61.1618 | 61.3266 | 121.2891 | 121.3898 | -0.16479 | 121.4859 | 61.3678 | -0.24262 | 121.3898 | -0.16479 | 61.3678 | 121.2891 | 121.4859 | -121.7011 | -121.8063
787.2031 | 121.8246 | -61.2488 | 60.4202 | -0.17509 | 0.011978 | 0.0013351 | 0.0059216 | 0.050328 | -0.010109 | 0.066902 | -61.2442 | 60.2051 | -61.29 | -61.2625 | 60.2051 | 0.36621 | 0.10986 | 0.3479 | 60.3333 | -61.3541 | -0.041199 | -0.21515 | 0.004577 | -0.013733 | -0.21515 | -0.10529 | -0.086975 | 0.045776 | 61.3586 | 61.5967 | 121.4539 | 121.4539 | 0.004577 | 121.582 | 61.615 | -0.10529 | 121.4539 | 0.004577 | 61.615 | 121.4539 | 121.582 | -121.7102 | -121.7743
788.9688 | 121.8933 | -61.2534 | 60.347 | 0.1606 | 0.012405 | -0.0014419 | 0.011262 | 0.052464 | -0.010536 | 0.070107 | -61.3174 | 60.141 | -61.377 | -61.3449 | 60.1044 | 0.16022 | -0.28381 | 0.050354 | 60.228 | -61.4731 | -0.1236 | -0.20599 | -0.064087 | -0.091553 | -0.24261 | -0.21973 | -0.11902 | 0.059509 | 60.9695 | 61.3037 | 121.3577 | 121.3943 | -0.064087 | 121.4813 | 61.4136 | -0.21973 | 121.3943 | -0.064087 | 61.4136 | 121.3577 | 121.4813 | -121.7239 | -121.8201
790.7188 | 121.8933 | -61.2167 | 60.3561 | 0.17586 | 0.015823 | 0.0045395 | 0.010835 | 0.055241 | -0.0090406 | 0.068184 | -61.322 | 60.141 | -61.3541 | -61.3358 | 60.0952 | 0.15106 | -0.29297 | 0.045776 | 60.2417 | -61.4502 | -0.13733 | -0.21515 | -0.10529 | -0.11902 | -0.26093 | -0.23346 | -0.11444 | 0.032044 | 60.9238 | 61.2625 | 121.312 | 121.3577 | -0.10529 | 121.4584 | 61.3678 | -0.23346 | 121.3577 | -0.10529 | 61.3678 | 121.312 | 121.4584 | -121.7102 | -121.8063
792.4062 | 121.9482 | -61.2808 | 60.2783 | 0.13771 | 0.013473 | 0.0013351 | 0.012117 | 0.051609 | -0.010536 | 0.069252 | -61.4502 | 60.1593 | -61.4365 | -61.4548 | 59.9991 | 0.032043 | -0.13275 | -0.11902 | 60.2829 | -61.4777 | -0.15564 | -0.11902 | -0.16937 | -0.17395 | -0.27924 | -0.19684 | 0.004578 | -0.013733 | 61.1481 | 61.1618 | 121.2799 | 121.4401 | -0.16937 | 121.5637 | 61.3129 | -0.19684 | 121.4401 | -0.16937 | 61.3129 | 121.2799 | 121.5637 | -121.7148 | -121.756
794.1562 | 121.8658 | -61.2167 | 60.4111 | -0.12932 | 0.013687 | 0.0043259 | 0.0048534 | 0.050968 | -0.0090406 | 0.06733 | -61.2305 | 60.2463 | -61.2534 | -61.2534 | 60.2097 | 0.34332 | 0.036621 | 0.32044 | 60.3195 | -61.3724 | -0.036621 | -0.16479 | -0.013733 | -0.036621 | -0.20142 | -0.15564 | -0.091553 | 0.022888 | 61.2534 | 61.5372 | 121.4264 | 121.463 | -0.013733 | 121.5363 | 61.5601 | -0.15564 | 121.463 | -0.013733 | 61.5601 | 121.4264 | 121.5363 | -121.6644 | -121.7834
795.9062 | 121.8338 | -61.2259 | 60.4202 | -0.16747 | 0.014328 | -0.00037386 | 0.007417 | 0.050328 | -0.010322 | 0.066048 | -61.2122 | 60.2325 | -61.2625 | -61.2167 | 60.2234 | 0.3891 | 0.082397 | 0.39368 | 60.3333 | -61.3403 | -0.036621 | -0.18768 | 0.013733 | 0.009155 | -0.19684 | -0.11444 | -0.086975 | 0.050354 | 61.3083 | 61.6196 | 121.4493 | 121.4584 | 0.013733 | 121.5591 | 61.615 | -0.11444 | 121.4584 | 0.013733 | 61.615 | 121.4493 | 121.5591 | -121.6827 | -121.7606
797.5938 | 121.8979 | -61.3129 | 60.2829 | 0.061417 | 0.011978 | -0.00080106 | 0.014253 | 0.053746 | -0.011818 | 0.066475 | -61.4182 | 60.1776 | -61.4182 | -61.4548 | 59.9991 | 0.054932 | -0.068665 | -0.091553 | 60.3104 | -61.4639 | -0.10529 | -0.10529 | -0.10529 | -0.14191 | -0.28381 | -0.15106 | 0.027466 | 0 | 61.2442 | 61.2213 | 121.3119 | 121.4905 | -0.10529 | 121.6232 | 61.3678 | -0.15106 | 121.4905 | -0.10529 | 61.3678 | 121.3119 | 121.6232 | -121.7011 | -121.7468
799.3438 | 121.8704 | -61.2167 | 60.4019 | -0.13695 | 0.01326 | 0.0015487 | 0.0046398 | 0.052464 | -0.01075 | 0.06797 | -61.2396 | 60.2097 | -61.2671 | -61.2442 | 60.2234 | 0.36621 | 0.018311 | 0.33417 | 60.3333 | -61.3495 | -0.050354 | -0.19226 | -0.022888 | -0.027466 | -0.17853 | -0.13275 | -0.068665 | 0.027466 | 61.235 | 61.5509 | 121.4401 | 121.4264 | -0.022888 | 121.55 | 61.5829 | -0.13275 | 121.4264 | -0.022888 | 61.5829 | 121.4401 | 121.55 | -121.669 | -121.7514
801.0781 | 121.8613 | -61.2442 | 60.3836 | -0.24376 | 0.012405 | 0.0015487 | 0.0086988 | 0.051182 | -0.010322 | 0.065193 | -61.2854 | 60.2646 | -61.3174 | -61.322 | 60.1501 | 0.29297 | 0.22888 | 0.27924 | 60.3516 | -61.3953 | -0.073242 | -0.11902 | -0.041198 | -0.077819 | -0.23346 | -0.15106 | -0.032044 | 0.032044 | 61.4731 | 61.5234 | 121.3943 | 121.5088 | -0.041198 | 121.5958 | 61.5372 | -0.15106 | 121.5088 | -0.041198 | 61.5372 | 121.3943 | 121.5958 | -121.7011 | -121.7789
802.8125 | 121.8155 | -61.3403 | 60.3195 | -0.10643 | 0.014541 | 0.00026694 | 0.014039 | 0.050541 | -0.010322 | 0.069252 | -61.3449 | 60.1776 | -61.3815 | -61.3541 | 60.0815 | 0.21057 | -0.013733 | 0.10529 | 60.2829 | -61.4136 | -0.041199 | -0.14191 | -0.004578 | -0.013733 | -0.23804 | -0.073242 | -0.036621 | 0.036621 | 61.3266 | 61.4456 | 121.4218 | 121.5179 | -0.004578 | 121.6232 | 61.5509 | -0.073242 | 121.5179 | -0.004578 | 61.5509 | 121.4218 | 121.6232 | -121.7011 | -121.7331
804.5625 | 121.8155 | -61.3129 | 60.3424 | -0.12169 | 0.013473 | -0.00058746 | 0.011262 | 0.050968 | -0.01139 | 0.069252 | -61.3358 | 60.2142 | -61.3998 | -61.3678 | 60.0906 | 0.21515 | -0.004578 | 0.086975 | 60.3149 | -61.4502 | -0.086975 | -0.12817 | -0.022888 | -0.054932 | -0.25177 | -0.13733 | -0.027466 | 0.064087 | 61.3083 | 61.3998 | 121.4035 | 121.5271 | -0.022888 | 121.6278 | 61.528 | -0.13733 | 121.5271 | -0.022888 | 61.528 | 121.4035 | 121.6278 | -121.7422 | -121.7926
806.2344 | 121.962 | -61.2762 | 60.2966 | 0.10719 | 0.015609 | -0.0016557 | 0.0093396 | 0.053746 | -0.010536 | 0.068398 | -61.441 | 60.1639 | -61.4319 | -61.496 | 59.9945 | 0.032043 | -0.14191 | -0.13733 | 60.3104 | -61.4685 | -0.15564 | -0.13275 | -0.16479 | -0.21973 | -0.30212 | -0.19226 | 0.013733 | -0.009155 | 61.1343 | 61.1389 | 121.2708 | 121.4401 | -0.16479 | 121.5866 | 61.3083 | -0.19226 | 121.4401 | -0.16479 | 61.3083 | 121.2708 | 121.5866 | -121.7285 | -121.7651
807.9219 | 121.8613 | -61.2762 | 60.3424 | -0.18272 | 0.012619 | 0.0034713 | 0.0080578 | 0.051609 | -0.01139 | 0.066262 | -61.3541 | 60.2737 | -61.3174 | -61.3861 | 60.0861 | 0.25635 | 0.19684 | 0.16479 | 60.3882 | -61.3815 | -0.041199 | -0.068664 | -0.07782 | -0.10986 | -0.25635 | -0.10529 | 0.045777 | -0.036621 | 61.4731 | 61.441 | 121.3623 | 121.55 | -0.07782 | 121.6644 | 61.5326 | -0.10529 | 121.55 | -0.07782 | 61.5326 | 121.3623 | 121.6644 | -121.6599 | -121.7239
809.6719 | 121.843 | -61.2488 | 60.434 | -0.15984 | 0.01326 | -0.0031509 | 0.0044262 | 0.052677 | -0.0079724 | 0.066262 | -61.2396 | 60.2097 | -61.2579 | -61.235 | 60.2554 | 0.37537 | 0.068665 | 0.36621 | 60.3561 | -61.3358 | -0.009156 | -0.2243 | 0.009155 | 0.013733 | -0.17853 | -0.086975 | -0.07782 | 0.018311 | 61.3174 | 61.615 | 121.5042 | 121.4584 | 0.009155 | 121.6049 | 61.6241 | -0.086975 | 121.4584 | 0.009155 | 61.6241 | 121.5042 | 121.6049 | -121.6919 | -121.7697
811.3438 | 121.8384 | -61.235 | 60.4294 | -0.15984 | 0.015396 | 0.0024033 | 0.0078442 | 0.049473 | -0.0073316 | 0.06733 | -61.2534 | 60.2463 | -61.2717 | -61.2625 | 60.2142 | 0.37994 | 0.1236 | 0.35706 | 60.3287 | -61.3586 | -0.036621 | -0.1831 | -0.018311 | -0.027466 | -0.21515 | -0.1236 | -0.10071 | 0.01831 | 61.3586 | 61.5921 | 121.4493 | 121.4813 | -0.018311 | 121.5637 | 61.615 | -0.1236 | 121.4813 | -0.018311 | 61.615 | 121.4493 | 121.5637 | -121.701 | -121.788
813.1094 | 121.9528 | -61.2808 | 60.26 | 0.091934 | 0.013473 | -0.0031509 | 0.013185 | 0.053532 | -0.010322 | 0.06797 | -61.4639 | 60.1639 | -61.4182 | -61.4777 | 59.9808 | 0.022888 | -0.1236 | -0.13275 | 60.3012 | -61.4777 | -0.13733 | -0.096131 | -0.18311 | -0.19684 | -0.27924 | -0.19684 | 0.041198 | -0.045776 | 61.1572 | 61.1481 | 121.2616 | 121.4447 | -0.18311 | 121.582 | 61.3037 | -0.19684 | 121.4447 | -0.18311 | 61.3037 | 121.2616 | 121.582 | -121.6782 | -121.7377
814.7969 | 121.9528 | -61.2625 | 60.2829 | 0.12245 | 0.014969 | 0.0026169 | 0.0099804 | 0.053746 | -0.011604 | 0.067757 | -61.4548 | 60.1501 | -61.4548 | -61.4731 | 59.9945 | 0.027466 | -0.13275 | -0.1236 | 60.2783 | -61.4685 | -0.19226 | -0.13275 | -0.19226 | -0.21057 | -0.28839 | -0.20599 | -0.004578 | 0 | 61.1298 | 61.1389 | 121.257 | 121.4127 | -0.19226 | 121.5408 | 61.29 | -0.20599 | 121.4127 | -0.19226 | 61.29 | 121.257 | 121.5408 | -121.7377 | -121.7514
816.5312 | 121.9116 | -61.2808 | 60.2966 | 0.061417 | 0.013473 | -0.0035783 | 0.011476 | 0.054814 | -0.010963 | 0.067116 | -61.4182 | 60.1685 | -61.4182 | -61.4685 | 59.9945 | 0.064087 | -0.064087 | -0.086975 | 60.3058 | -61.4685 | -0.13733 | -0.12817 | -0.13733 | -0.18768 | -0.30212 | -0.18768 | 0.009155 | 0 | 61.2167 | 61.1938 | 121.2753 | 121.4493 | -0.13733 | 121.5866 | 61.3449 | -0.18768 | 121.4493 | -0.13733 | 61.3449 | 121.2753 | 121.5866 | -121.7148 | -121.7651
818.2656 | 121.9574 | -61.2808 | 60.2875 | 0.053787 | 0.013687 | 0.0045395 | 0.011903 | 0.050968 | -0.0092542 | 0.06797 | -61.4456 | 60.1868 | -61.3998 | -61.5005 | 59.967 | 0.050354 | -0.091553 | -0.12817 | 60.2875 | -61.4731 | -0.11902 | -0.10071 | -0.1648 | -0.21973 | -0.32043 | -0.19226 | 0 | -0.045777 | 61.1893 | 61.1526 | 121.2479 | 121.4676 | -0.1648 | 121.5683 | 61.3312 | -0.19226 | 121.4676 | -0.1648 | 61.3312 | 121.2479 | 121.5683 | -121.6873 | -121.7606
820.0156 | 121.8704 | -61.3129 | 60.3104 | -0.022507 | 0.012405 | 0.0058211 | 0.0097668 | 0.052464 | -0.0094678 | 0.068398 | -61.3861 | 60.1822 | -61.3724 | -61.441 | 60.0266 | 0.11444 | -0.07782 | -0.036621 | 60.2875 | -61.4548 | -0.059509 | -0.12817 | -0.073242 | -0.12817 | -0.28381 | -0.14191 | -0.022888 | -0.013733 | 61.235 | 61.2762 | 121.3394 | 121.4951 | -0.073242 | 121.6003 | 61.4273 | -0.14191 | 121.4951 | -0.073242 | 61.4273 | 121.3394 | 121.6003 | -121.6827 | -121.7651
821.75 | 121.8979 | -61.2991 | 60.2921 | 0.046158 | 0.011337 | -0.00037386 | 0.008485 | 0.053532 | -0.0083996 | 0.067757 | -61.441 | 60.173 | -61.4319 | -61.4685 | 59.9945 | 0.07782 | -0.073242 | -0.091553 | 60.2966 | -61.4594 | -0.13275 | -0.11902 | -0.14191 | -0.16937 | -0.29755 | -0.16022 | 0.004578 | -0.009155 | 61.2259 | 61.2076 | 121.2936 | 121.4722 | -0.14191 | 121.5958 | 61.377 | -0.16022 | 121.4722 | -0.14191 | 61.377 | 121.2936 | 121.5958 | -121.7239 | -121.7514
823.4844 | 121.9345 | -61.2213 | 60.3745 | 0.1606 | 0.014541 | 0.00069434 | 0.0054944 | 0.052677 | -0.0086132 | 0.067757 | -61.3266 | 60.1273 | -61.322 | -61.3495 | 60.1318 | 0.16937 | -0.25177 | 0.064087 | 60.2234 | -61.4456 | -0.10071 | -0.24719 | -0.10529 | -0.12817 | -0.24262 | -0.22431 | -0.15106 | -0.004578 | 60.9695 | 61.2854 | 121.3531 | 121.3486 | -0.10529 | 121.4447 | 61.3907 | -0.22431 | 121.3486 | -0.10529 | 61.3907 | 121.3531 | 121.4447 | -121.6965 | -121.8201
825.2344 | 121.8704 | -61.2625 | 60.3928 | -0.25902 | 0.013473 | 0.00026694 | 0.0078442 | 0.051396 | -0.008827 | 0.063912 | -61.2946 | 60.2646 | -61.3083 | -61.3541 | 60.1318 | 0.30212 | 0.24719 | 0.2655 | 60.3745 | -61.3861 | -0.045777 | -0.12817 | -0.032044 | -0.091553 | -0.26093 | -0.1236 | -0.01831 | 0.013733 | 61.5097 | 61.528 | 121.3943 | 121.5271 | -0.032044 | 121.637 | 61.5646 | -0.1236 | 121.5271 | -0.032044 | 61.5646 | 121.3943 | 121.637 | -121.7011 | -121.7789
826.9219 | 121.9116 | -61.2442 | 60.347 | 0.19112 | 0.014328 | 0.0030441 | 0.0099804 | 0.055668 | -0.01139 | 0.066902 | -61.3861 | 60.1501 | -61.3998 | -61.4182 | 60.0632 | 0.091553 | -0.27008 | -0.045776 | 60.2737 | -61.4227 | -0.15564 | -0.19684 | -0.14191 | -0.17395 | -0.28381 | -0.17853 | -0.073242 | 0.013733 | 60.9741 | 61.1984 | 121.3074 | 121.3943 | -0.14191 | 121.5179 | 61.3358 | -0.17853 | 121.3943 | -0.14191 | 61.3358 | 121.3074 | 121.5179 | -121.7468 | -121.7697
828.6562 | 121.8979 | -61.2167 | 60.3882 | 0.1606 | 0.012832 | 0.0049667 | 0.0080578 | 0.051823 | -0.0083996 | 0.066902 | -61.3449 | 60.1181 | -61.3678 | -61.3449 | 60.1135 | 0.15564 | -0.28381 | 0.054932 | 60.2371 | -61.4548 | -0.15106 | -0.27008 | -0.12817 | -0.12817 | -0.27466 | -0.23804 | -0.15106 | 0.022888 | 60.9329 | 61.2717 | 121.3303 | 121.3348 | -0.12817 | 121.4539 | 61.3724 | -0.23804 | 121.3348 | -0.12817 | 61.3724 | 121.3303 | 121.4539 | -121.756 | -121.843
830.4062 | 121.9299 | -61.29 | 60.2875 | 0.038529 | 0.012619 | -0.0010147 | 0.012544 | 0.053105 | -0.012458 | 0.066048 | -61.4319 | 60.1822 | -61.4365 | -61.4639 | 59.9808 | 0.045776 | -0.086975 | -0.11444 | 60.3104 | -61.4594 | -0.14648 | -0.10529 | -0.14191 | -0.17395 | -0.3067 | -0.16937 | 0.022888 | 0.004577 | 61.203 | 61.1755 | 121.2708 | 121.4722 | -0.14191 | 121.6003 | 61.3358 | -0.16937 | 121.4722 | -0.14191 | 61.3358 | 121.2708 | 121.6003 | -121.7239 | -121.7468
832.1562 | 121.962 | -61.2946 | 60.2875 | 0.13771 | 0.014755 | 0.0032577 | 0.011903 | 0.053318 | -0.010536 | 0.067116 | -61.441 | 60.1913 | -61.3998 | -61.496 | 59.9808 | 0.018311 | -0.13733 | -0.14648 | 60.3058 | -61.4868 | -0.10529 | -0.096131 | -0.14648 | -0.20142 | -0.3067 | -0.19226 | 0.01831 | -0.041199 | 61.1572 | 61.1481 | 121.2753 | 121.4859 | -0.14648 | 121.6003 | 61.3129 | -0.19226 | 121.4859 | -0.14648 | 61.3129 | 121.2753 | 121.6003 | -121.6873 | -121.7743
833.8438 | 121.8475 | -61.29 | 60.3333 | -0.17509 | 0.013046 | 0.00069434 | 0.011262 | 0.050541 | -0.011604 | 0.066475 | -61.3403 | 60.2509 | -61.3495 | -61.3495 | 60.0952 | 0.25177 | 0.15106 | 0.15564 | 60.3653 | -61.4182 | -0.059509 | -0.082398 | -0.050354 | -0.059509 | -0.23804 | -0.12817 | 0.032043 | 0.009155 | 61.441 | 61.4456 | 121.3852 | 121.5408 | -0.050354 | 121.6553 | 61.5417 | -0.12817 | 121.5408 | -0.050354 | 61.5417 | 121.3852 | 121.6553 | -121.6827 | -121.7514
835.5938 | 121.8292 | -61.2167 | 60.4385 | -0.19035 | 0.012832 | -0.00016026 | 0.0037854 | 0.050541 | -0.009895 | 0.068184 | -61.2213 | 60.2692 | -61.2717 | -61.235 | 60.2463 | 0.39825 | 0.086975 | 0.37537 | 60.3561 | -61.3358 | -0.054931 | -0.16937 | -0.004577 | -0.01831 | -0.19226 | -0.11902 | -0.082398 | 0.050354 | 61.3037 | 61.5921 | 121.463 | 121.4859 | -0.004577 | 121.5729 | 61.615 | -0.11902 | 121.4859 | -0.004577 | 61.615 | 121.463 | 121.5729 | -121.7102 | -121.7743
837.3281 | 121.8933 | -61.2625 | 60.3424 | -0.20561 | 0.015396 | -0.00016026 | 0.010194 | 0.050968 | -0.0092542 | 0.068184 | -61.3495 | 60.2646 | -61.3312 | -61.3724 | 60.0861 | 0.24719 | 0.20599 | 0.16937 | 60.347 | -61.4227 | -0.068665 | -0.07782 | -0.086975 | -0.10986 | -0.25635 | -0.16022 | 0.004578 | -0.01831 | 61.4685 | 61.4319 | 121.3486 | 121.5271 | -0.086975 | 121.6095 | 61.5097 | -0.16022 | 121.5271 | -0.086975 | 61.5097 | 121.3486 | 121.6095 | -121.6736 | -121.7651
839.0781 | 121.907 | -61.2534 | 60.3424 | 0.13008 | 0.01326 | 0.00026694 | 0.0086988 | 0.050968 | -0.01075 | 0.068825 | -61.3541 | 60.1547 | -61.3541 | -61.3632 | 60.1044 | 0.14648 | -0.28381 | 0.004578 | 60.2417 | -61.4456 | -0.10071 | -0.18768 | -0.10071 | -0.10986 | -0.23804 | -0.19226 | -0.10071 | 0 | 60.9695 | 61.2579 | 121.3577 | 121.4081 | -0.10071 | 121.4951 | 61.3998 | -0.19226 | 121.4081 | -0.10071 | 61.3998 | 121.3577 | 121.4951 | -121.6965 | -121.788
840.7656 | 121.9116 | -61.2167 | 60.3607 | 0.099564 | 0.011337 | 5.3338e-05 | 0.0065624 | 0.050328 | -0.0086132 | 0.066902 | -61.322 | 60.1318 | -61.3724 | -61.3541 | 60.1318 | 0.16022 | -0.21973 | 0.073242 | 60.2921 | -61.4273 | -0.15564 | -0.22888 | -0.10529 | -0.13733 | -0.22888 | -0.21057 | -0.068665 | 0.050354 | 60.997 | 61.29 | 121.3486 | 121.3486 | -0.10529 | 121.5088 | 61.377 | -0.21057 | 121.3486 | -0.10529 | 61.377 | 121.3486 | 121.5088 | -121.7331 | -121.788
842.5156 | 121.9437 | -61.1984 | 60.4065 | -0.045395 | 0.014328 | -0.0027237 | 0.0059216 | 0.047978 | -0.0079724 | 0.067543 | -61.3129 | 60.2325 | -61.29 | -61.3129 | 60.1685 | 0.28839 | 0.032043 | 0.26093 | 60.347 | -61.3586 | -0.091553 | -0.17395 | -0.11444 | -0.11444 | -0.23804 | -0.16022 | -0.059509 | -0.022888 | 61.2305 | 61.4594 | 121.3669 | 121.431 | -0.11444 | 121.5454 | 61.4868 | -0.16022 | 121.431 | -0.11444 | 61.4868 | 121.3669 | 121.5454 | -121.6965 | -121.7651
844.2656 | 121.8704 | -61.3174 | 60.3287 | 0.0080111 | 0.012405 | -0.00080106 | 0.012758 | 0.051823 | -0.01374 | 0.06733 | -61.3632 | 60.173 | -61.409 | -61.4227 | 60.0082 | 0.10529 | -0.068665 | -0.036621 | 60.2829 | -61.4548 | -0.091553 | -0.15564 | -0.045776 | -0.10528 | -0.32043 | -0.13733 | -0.045776 | 0.045777 | 61.2488 | 61.2808 | 121.3257 | 121.4905 | -0.045776 | 121.6003 | 61.4227 | -0.13733 | 121.4905 | -0.045776 | 61.4227 | 121.3257 | 121.6003 | -121.7377 | -121.7834
845.9531 | 121.9803 | -61.1893 | 60.3745 | 0.061417 | 0.014541 | -0.0029373 | 0.003999 | 0.052464 | -0.0079724 | 0.068825 | -61.3495 | 60.2051 | -61.3266 | -61.3678 | 60.1318 | 0.1831 | -0.059509 | 0.10986 | 60.2783 | -61.441 | -0.13733 | -0.16937 | -0.16022 | -0.17853 | -0.24262 | -0.25177 | -0.096131 | -0.022888 | 61.1298 | 61.2991 | 121.3211 | 121.3943 | -0.16022 | 121.4676 | 61.3724 | -0.25177 | 121.3943 | -0.16022 | 61.3724 | 121.3211 | 121.4676 | -121.7011 | -121.8155
847.7031 | 121.8475 | -61.3037 | 60.3378 | -0.053024 | 0.013473 | 0.0013351 | 0.014253 | 0.05225 | -0.01139 | 0.067116 | -61.3449 | 60.2188 | -61.3998 | -61.3861 | 60.0586 | 0.16022 | -0.027466 | 0.041199 | 60.3333 | -61.4319 | -0.09613 | -0.11902 | -0.041199 | -0.082397 | -0.27924 | -0.12817 | -0.004578 | 0.054931 | 61.2762 | 61.3449 | 121.3623 | 121.5225 | -0.041199 | 121.637 | 61.4639 | -0.12817 | 121.5225 | -0.041199 | 61.4639 | 121.3623 | 121.637 | -121.7377 | -121.7697
849.4531 | 121.8338 | -61.3312 | 60.3378 | -0.10643 | 0.015396 | -0.0055009 | 0.012117 | 0.055241 | -0.015022 | 0.067116 | -61.3403 | 60.2234 | -61.3861 | -61.3724 | 60.0998 | 0.22888 | 0.004578 | 0.11444 | 60.3287 | -61.4273 | -0.054931 | -0.11444 | -0.009155 | -0.041198 | -0.23804 | -0.09613 | -0.009156 | 0.045776 | 61.3358 | 61.4456 | 121.431 | 121.5546 | -0.009155 | 121.6599 | 61.5601 | -0.09613 | 121.5546 | -0.009155 | 61.5601 | 121.431 | 121.6599 | -121.7239 | -121.7651
851.2188 | 121.8796 | -61.2534 | 60.3607 | -0.15221 | 0.011978 | 0.0032577 | 0.0065624 | 0.051823 | -0.01075 | 0.066902 | -61.322 | 60.2692 | -61.3312 | -61.3678 | 60.1181 | 0.27924 | 0.24719 | 0.22888 | 60.3836 | -61.3861 | -0.07782 | -0.091553 | -0.068664 | -0.11444 | -0.24262 | -0.13275 | 0.022888 | 0.009156 | 61.5005 | 61.4822 | 121.3715 | 121.5225 | -0.068664 | 121.637 | 61.5326 | -0.13275 | 121.5225 | -0.068664 | 61.5326 | 121.3715 | 121.637 | -121.6919 | -121.7468
852.9688 | 121.9437 | -61.2488 | 60.2829 | 0.10719 | 0.014328 | -0.00058746 | 0.0093396 | 0.054386 | -0.0090406 | 0.06797 | -61.409 | 60.2234 | -61.4182 | -61.4594 | 60.0174 | 0.054932 | -0.20599 | -0.10529 | 60.2829 | -61.4914 | -0.16937 | -0.059509 | -0.16022 | -0.21057 | -0.2655 | -0.24262 | 0 | 0.009155 | 61.0428 | 61.1435 | 121.2662 | 121.4722 | -0.16022 | 121.5317 | 61.3037 | -0.24262 | 121.4722 | -0.16022 | 61.3037 | 121.2662 | 121.5317 | -121.7011 | -121.7743
854.6406 | 121.8704 | -61.2534 | 60.3699 | -0.23613 | 0.012619 | 0.00090794 | 0.005708 | 0.05225 | -0.01075 | 0.068398 | -61.3083 | 60.2646 | -61.2946 | -61.3449 | 60.1501 | 0.31586 | 0.23346 | 0.27466 | 60.3745 | -61.3907 | -0.041199 | -0.10529 | -0.054932 | -0.091553 | -0.21973 | -0.13733 | 0.004578 | -0.013733 | 61.4868 | 61.528 | 121.4035 | 121.5179 | -0.054932 | 121.6278 | 61.5692 | -0.13733 | 121.5179 | -0.054932 | 61.5692 | 121.4035 | 121.6278 | -121.6644 | -121.7606
856.3906 | 121.9299 | -61.2076 | 60.4202 | -0.075912 | 0.012619 | -0.0029373 | 0.0044262 | 0.050755 | -0.010109 | 0.068184 | -61.29 | 60.2188 | -61.2717 | -61.2854 | 60.2051 | 0.32959 | 0.036621 | 0.3067 | 60.3516 | -61.3586 | -0.064086 | -0.20142 | -0.082397 | -0.077819 | -0.21515 | -0.15106 | -0.068665 | -0.018311 | 61.2442 | 61.5143 | 121.4127 | 121.4264 | -0.082397 | 121.5591 | 61.5372 | -0.15106 | 121.4264 | -0.082397 | 61.5372 | 121.4127 | 121.5591 | -121.6919 | -121.7789
858.1406 | 121.8796 | -61.2671 | 60.3928 | -0.2285 | 0.015182 | -0.0016557 | 0.0095532 | 0.050541 | -0.010963 | 0.067116 | -61.3403 | 60.2737 | -61.3312 | -61.3541 | 60.1089 | 0.27924 | 0.24719 | 0.24261 | 60.4019 | -61.4044 | -0.064087 | -0.11902 | -0.073242 | -0.086975 | -0.28381 | -0.13733 | 0.009156 | -0.009155 | 61.5143 | 61.5097 | 121.376 | 121.5408 | -0.073242 | 121.669 | 61.5463 | -0.13733 | 121.5408 | -0.073242 | 61.5463 | 121.376 | 121.669 | -121.7239 | -121.7972
859.8281 | 121.962 | -61.1984 | 60.3882 | 0.10719 | 0.012832 | -0.0033647 | 0.0063488 | 0.050755 | -0.01075 | 0.066262 | -61.3312 | 60.1501 | -61.3815 | -61.3495 | 60.1227 | 0.17853 | -0.14191 | 0.09613 | 60.2875 | -61.4044 | -0.18311 | -0.23804 | -0.13275 | -0.15106 | -0.2655 | -0.20599 | -0.10071 | 0.050354 | 61.0565 | 61.2946 | 121.3211 | 121.3486 | -0.13275 | 121.4859 | 61.377 | -0.20599 | 121.3486 | -0.13275 | 61.377 | 121.3211 | 121.4859 | -121.7697 | -121.7926
861.5781 | 121.8246 | -61.2213 | 60.4202 | -0.21324 | 0.012832 | 0.00026694 | 0.0061352 | 0.0499 | -0.0062634 | 0.068611 | -61.2305 | 60.2325 | -61.2396 | -61.2259 | 60.2234 | 0.37994 | 0.10071 | 0.38452 | 60.3241 | -61.3907 | -0.018311 | -0.18768 | -0.009156 | -0.004578 | -0.19684 | -0.16937 | -0.09613 | 0.009155 | 61.322 | 61.6058 | 121.4447 | 121.4539 | -0.009156 | 121.5454 | 61.6013 | -0.16937 | 121.4539 | -0.009156 | 61.6013 | 121.4447 | 121.5454 | -121.6599 | -121.8109
863.3125 | 121.9437 | -61.1755 | 60.3745 | -0.0072479 | 0.011764 | -0.0033647 | 0.0067762 | 0.049687 | -0.008827 | 0.066475 | -61.3266 | 60.2234 | -61.322 | -61.3266 | 60.1273 | 0.24719 | 0 | 0.19684 | 60.347 | -61.3724 | -0.14648 | -0.15106 | -0.15106 | -0.15106 | -0.24719 | -0.19684 | -0.027466 | -0.004578 | 61.1755 | 61.3724 | 121.3028 | 121.3989 | -0.15106 | 121.5225 | 61.4227 | -0.19684 | 121.3989 | -0.15106 | 61.4227 | 121.3028 | 121.5225 | -121.6965 | -121.7468
865.0781 | 121.843 | -61.235 | 60.4019 | -0.16747 | 0.011978 | -0.0029373 | 0.0086988 | 0.053105 | -0.0090406 | 0.066048 | -61.235 | 60.2325 | -61.2579 | -61.2396 | 60.2142 | 0.39368 | 0.10529 | 0.3479 | 60.3561 | -61.3632 | -0.022889 | -0.16937 | 0 | -0.004578 | -0.18768 | -0.12817 | -0.045777 | 0.022889 | 61.3403 | 61.5829 | 121.4493 | 121.4676 | 0 | 121.5912 | 61.6287 | -0.12817 | 121.4676 | 0 | 61.6287 | 121.4493 | 121.5912 | -121.6599 | -121.7651
866.75 | 121.9574 | -61.203 | 60.3745 | 0.099564 | 0.011551 | -0.0020829 | 0.0078442 | 0.050328 | -0.012031 | 0.067116 | -61.3266 | 60.1456 | -61.3449 | -61.3541 | 60.1181 | 0.17853 | -0.13275 | 0.10529 | 60.3058 | -61.3815 | -0.14191 | -0.22888 | -0.1236 | -0.15106 | -0.25635 | -0.17853 | -0.068665 | 0.018311 | 61.0703 | 61.3083 | 121.3211 | 121.3486 | -0.1236 | 121.5088 | 61.3815 | -0.17853 | 121.3486 | -0.1236 | 61.3815 | 121.3211 | 121.5088 | -121.7194 | -121.756
868.5 | 121.875 | -61.2534 | 60.3745 | -0.25902 | 0.013687 | -0.0010147 | 0.010194 | 0.050755 | -0.011604 | 0.06733 | -61.3312 | 60.2417 | -61.3495 | -61.3541 | 60.1044 | 0.27466 | 0.2655 | 0.21515 | 60.4202 | -61.3907 | -0.09613 | -0.13275 | -0.07782 | -0.10071 | -0.27008 | -0.13733 | 0.045776 | 0.01831 | 61.5189 | 61.4685 | 121.3577 | 121.4951 | -0.07782 | 121.6736 | 61.528 | -0.13733 | 121.4951 | -0.07782 | 61.528 | 121.3577 | 121.6736 | -121.7239 | -121.7651
870.2656 | 121.9574 | -61.1847 | 60.3745 | 0.038529 | 0.011764 | 0.0045395 | 0.007417 | 0.051823 | -0.0094678 | 0.066902 | -61.3174 | 60.1913 | -61.3129 | -61.3495 | 60.1273 | 0.19684 | -0.064087 | 0.13275 | 60.3333 | -61.3907 | -0.12817 | -0.18311 | -0.13275 | -0.1648 | -0.24719 | -0.20599 | -0.041199 | -0.004578 | 61.1206 | 61.3174 | 121.3119 | 121.376 | -0.13275 | 121.5179 | 61.3815 | -0.20599 | 121.376 | -0.13275 | 61.3815 | 121.3119 | 121.5179 | -121.6873 | -121.7651
871.9531 | 121.8887 | -61.2854 | 60.347 | -0.23613 | 0.011978 | -0.0010147 | 0.011476 | 0.050541 | -0.010322 | 0.065834 | -61.3495 | 60.2737 | -61.3403 | -61.3632 | 60.1044 | 0.25635 | 0.24719 | 0.18768 | 60.3745 | -61.377 | -0.054932 | -0.073242 | -0.064087 | -0.07782 | -0.24261 | -0.091553 | 0.027466 | -0.009155 | 61.5326 | 61.4731 | 121.3898 | 121.5591 | -0.064087 | 121.6599 | 61.5417 | -0.091553 | 121.5591 | -0.064087 | 61.5417 | 121.3898 | 121.6599 | -121.6873 | -121.7239
873.7031 | 121.9711 | -61.2808 | 60.2875 | 0.12245 | 0.014114 | 0.00048074 | 0.012117 | 0.051182 | -0.010536 | 0.068184 | -61.4502 | 60.1501 | -61.4456 | -61.4777 | 59.9762 | 0.036621 | -0.13733 | -0.12817 | 60.26 | -61.528 | -0.1648 | -0.13733 | -0.16937 | -0.19684 | -0.31128 | -0.24719 | -0.027466 | -0.004577 | 61.1435 | 61.1526 | 121.257 | 121.431 | -0.16937 | 121.5408 | 61.3174 | -0.24719 | 121.431 | -0.16937 | 61.3174 | 121.257 | 121.5408 | -121.7331 | -121.8155
875.4531 | 121.8384 | -61.203 | 60.4294 | -0.19798 | 0.010482 | 0.0047531 | 0.0072034 | 0.052464 | -0.009895 | 0.066048 | -61.235 | 60.2554 | -61.2671 | -61.235 | 60.2371 | 0.39825 | 0.091553 | 0.37537 | 60.3287 | -61.3266 | -0.064087 | -0.17395 | -0.032043 | -0.032043 | -0.19226 | -0.1236 | -0.10071 | 0.032044 | 61.2946 | 61.5784 | 121.4401 | 121.4584 | -0.032043 | 121.5317 | 61.6013 | -0.1236 | 121.4584 | -0.032043 | 61.6013 | 121.4401 | 121.5317 | -121.6965 | -121.756
877.2031 | 121.9803 | -61.1847 | 60.3928 | 0.0080111 | 0.012405 | 0.0013351 | 0.005708 | 0.051396 | -0.0090406 | 0.065407 | -61.3403 | 60.2005 | -61.3129 | -61.3541 | 60.141 | 0.20142 | -0.045776 | 0.13733 | 60.3378 | -61.3815 | -0.12817 | -0.19226 | -0.15564 | -0.16937 | -0.25177 | -0.19684 | -0.054931 | -0.027466 | 61.1389 | 61.322 | 121.3257 | 121.3852 | -0.15564 | 121.5225 | 61.3861 | -0.19684 | 121.3852 | -0.15564 | 61.3861 | 121.3257 | 121.5225 | -121.7056 | -121.7743
878.9531 | 121.9345 | -61.2488 | 60.347 | 0.16823 | 0.014969 | 0.0024033 | 0.011049 | 0.051182 | -0.010536 | 0.069039 | -61.322 | 60.1318 | -61.3586 | -61.3495 | 60.0998 | 0.14191 | -0.31128 | 0.032043 | 60.2463 | -61.4456 | -0.10986 | -0.21515 | -0.073242 | -0.10071 | -0.24719 | -0.19684 | -0.10071 | 0.036622 | 60.9375 | 61.2808 | 121.3486 | 121.3806 | -0.073242 | 121.4951 | 61.3907 | -0.19684 | 121.3806 | -0.073242 | 61.3907 | 121.3486 | 121.4951 | -121.7056 | -121.7926
880.6406 | 121.8338 | -61.203 | 60.4248 | -0.12932 | 0.01326 | -0.0020829 | 0.0067762 | 0.049046 | -0.0092542 | 0.067757 | -61.2259 | 60.2509 | -61.2671 | -61.2213 | 60.2371 | 0.36163 | 0.073242 | 0.37079 | 60.3561 | -61.377 | -0.064087 | -0.17395 | -0.022888 | -0.01831 | -0.18768 | -0.17395 | -0.068665 | 0.041199 | 61.2762 | 61.5738 | 121.4401 | 121.4539 | -0.022888 | 121.5591 | 61.5646 | -0.17395 | 121.4539 | -0.022888 | 61.5646 | 121.4401 | 121.5591 | -121.6919 | -121.8018
882.375 | 121.8292 | -61.2625 | 60.4111 | -0.16747 | 0.013473 | 0.00048074 | 0.0093396 | 0.053105 | -0.010536 | 0.065834 | -61.2442 | 60.2325 | -61.2946 | -61.2534 | 60.2142 | 0.37994 | 0.14648 | 0.36163 | 60.3653 | -61.3632 | -0.032044 | -0.17853 | 0.01831 | 0.009155 | -0.19684 | -0.10071 | -0.045777 | 0.050354 | 61.409 | 61.6241 | 121.4767 | 121.4951 | 0.01831 | 121.6278 | 61.6425 | -0.10071 | 121.4951 | 0.01831 | 61.6425 | 121.4767 | 121.6278 | -121.7056 | -121.7743
884.125 | 121.8338 | -61.2396 | 60.4294 | -0.17509 | 0.012619 | -0.0010147 | 0.0089124 | 0.051823 | -0.010963 | 0.066262 | -61.2167 | 60.2417 | -61.2854 | -61.2396 | 60.2417 | 0.39368 | 0.082397 | 0.37079 | 60.3561 | -61.3495 | -0.045776 | -0.18768 | 0.022888 | 0 | -0.18768 | -0.10986 | -0.073242 | 0.068664 | 61.322 | 61.6104 | 121.4813 | 121.4813 | 0.022888 | 121.5958 | 61.6333 | -0.10986 | 121.4813 | 0.022888 | 61.6333 | 121.4813 | 121.5958 | -121.7148 | -121.7789
885.8125 | 121.8842 | -61.2808 | 60.3424 | -0.21324 | 0.013046 | 0.0034713 | 0.0095532 | 0.050114 | -0.010322 | 0.068611 | -61.3403 | 60.2737 | -61.3724 | -61.3678 | 60.1089 | 0.26093 | 0.23346 | 0.18768 | 60.3699 | -61.3998 | -0.091552 | -0.068664 | -0.059509 | -0.086975 | -0.23346 | -0.11902 | 0.027466 | 0.032043 | 61.5143 | 61.4685 | 121.3898 | 121.5546 | -0.059509 | 121.6507 | 61.5417 | -0.11902 | 121.5546 | -0.059509 | 61.5417 | 121.3898 | 121.6507 | -121.7148 | -121.7422
887.5469 | 121.8018 | -61.2991 | 60.3607 | -0.14458 | 0.014755 | -0.00058746 | 0.010194 | 0.051609 | -0.011604 | 0.065834 | -61.3266 | 60.2325 | -61.3861 | -61.3449 | 60.0998 | 0.25177 | 0.064087 | 0.14191 | 60.3287 | -61.4319 | -0.086975 | -0.12817 | -0.027466 | -0.045777 | -0.26093 | -0.13275 | -0.032044 | 0.059509 | 61.3632 | 61.441 | 121.3989 | 121.5317 | -0.027466 | 121.6278 | 61.5509 | -0.13275 | 121.5317 | -0.027466 | 61.5509 | 121.3989 | 121.6278 | -121.7468 | -121.7926
889.2969 | 121.8979 | -61.235 | 60.3699 | 0.16823 | 0.011551 | -0.00016026 | 0.009126 | 0.052464 | -0.008827 | 0.065407 | -61.3266 | 60.1547 | -61.3861 | -61.3632 | 60.1135 | 0.16479 | -0.28839 | 0.059509 | 60.2554 | -61.4548 | -0.15106 | -0.21515 | -0.091553 | -0.12817 | -0.25635 | -0.21973 | -0.11444 | 0.059509 | 60.9467 | 61.2946 | 121.3486 | 121.3898 | -0.091553 | 121.4905 | 61.3998 | -0.21973 | 121.3898 | -0.091553 | 61.3998 | 121.3486 | 121.4905 | -121.756 | -121.8246
890.9844 | 121.9711 | -61.1938 | 60.3973 | 0.038529 | 0.013473 | -0.0052873 | 0.0078442 | 0.050968 | -0.0086132 | 0.066689 | -61.3266 | 60.2051 | -61.322 | -61.3678 | 60.1044 | 0.17853 | -0.091553 | 0.10986 | 60.3104 | -61.409 | -0.12817 | -0.19226 | -0.13275 | -0.17395 | -0.29297 | -0.21515 | -0.086975 | -0.004578 | 61.1023 | 61.3037 | 121.2982 | 121.3989 | -0.13275 | 121.5042 | 61.3724 | -0.21515 | 121.3989 | -0.13275 | 61.3724 | 121.2982 | 121.5042 | -121.7194 | -121.8063
892.7188 | 121.9254 | -61.2167 | 60.3745 | 0.13771 | 0.011978 | 0.0032577 | 0.0093396 | 0.053318 | -0.010963 | 0.066902 | -61.3312 | 60.141 | -61.3861 | -61.3495 | 60.1181 | 0.16479 | -0.24719 | 0.073242 | 60.2463 | -61.4273 | -0.16937 | -0.23346 | -0.11444 | -0.13275 | -0.25635 | -0.21057 | -0.12817 | 0.054931 | 60.9695 | 61.29 | 121.3348 | 121.3577 | -0.11444 | 121.463 | 61.3815 | -0.21057 | 121.3577 | -0.11444 | 61.3815 | 121.3348 | 121.463 | -121.7606 | -121.8018
894.4688 | 121.8384 | -61.2534 | 60.3973 | -0.16747 | 0.0139 | -0.00058746 | 0.0097668 | 0.049259 | -0.008827 | 0.066689 | -61.2534 | 60.2463 | -61.2854 | -61.2488 | 60.2051 | 0.38452 | 0.15106 | 0.36163 | 60.3836 | -61.3724 | -0.032043 | -0.15106 | 0 | 0.004578 | -0.19226 | -0.11902 | -0.013733 | 0.032043 | 61.4044 | 61.615 | 121.4584 | 121.4996 | 0 | 121.637 | 61.6379 | -0.11902 | 121.4996 | 0 | 61.6379 | 121.4584 | 121.637 | -121.6827 | -121.7697
896.2344 | 121.8567 | -61.322 | 60.3012 | 0.030899 | 0.013046 | -0.0014419 | 0.015748 | 0.053105 | -0.012886 | 0.067116 | -61.3861 | 60.1639 | -61.4273 | -61.4365 | 59.9991 | 0.10529 | -0.07782 | -0.068665 | 60.2875 | -61.4639 | -0.10529 | -0.13733 | -0.064087 | -0.11444 | -0.30212 | -0.14191 | -0.013732 | 0.041199 | 61.2442 | 61.2534 | 121.3211 | 121.4859 | -0.064087 | 121.6095 | 61.4273 | -0.14191 | 121.4859 | -0.064087 | 61.4273 | 121.3211 | 121.6095 | -121.7285 | -121.7651
897.9062 | 121.843 | -61.2396 | 60.434 | -0.12932 | 0.013687 | -0.00016026 | 0.0048534 | 0.050968 | -0.0096814 | 0.067116 | -61.2167 | 60.228 | -61.2579 | -61.2213 | 60.26 | 0.35706 | 0.073242 | 0.37079 | 60.3516 | -61.377 | -0.018311 | -0.20599 | 0.022888 | 0.018311 | -0.17395 | -0.13733 | -0.082398 | 0.041199 | 61.3129 | 61.6104 | 121.4996 | 121.4676 | 0.022888 | 121.5912 | 61.5967 | -0.13733 | 121.4676 | 0.022888 | 61.5967 | 121.4996 | 121.5912 | -121.6919 | -121.8109
899.6406 | 121.8613 | -61.2442 | 60.4248 | -0.20561 | 0.0139 | -0.0022965 | 0.0097668 | 0.050755 | -0.0086132 | 0.065621 | -61.2579 | 60.26 | -61.2991 | -61.2671 | 60.2051 | 0.38452 | 0.16479 | 0.34332 | 60.3653 | -61.3724 | -0.054931 | -0.16479 | -0.013733 | -0.022888 | -0.21973 | -0.12817 | -0.05951 | 0.041198 | 61.409 | 61.5875 | 121.4493 | 121.5042 | -0.013733 | 121.6095 | 61.6287 | -0.12817 | 121.5042 | -0.013733 | 61.6287 | 121.4493 | 121.6095 | -121.7239 | -121.7972
901.3906 | 121.8292 | -61.2442 | 60.4202 | -0.19798 | 0.014755 | -0.0016557 | 0.0095532 | 0.050968 | -0.012031 | 0.064553 | -61.2396 | 60.2554 | -61.2625 | -61.2396 | 60.2463 | 0.3891 | 0.10071 | 0.38452 | 60.3195 | -61.3815 | -0.01831 | -0.16479 | 0.004578 | 0.004578 | -0.17395 | -0.13733 | -0.10071 | 0.022888 | 61.3449 | 61.6287 | 121.4905 | 121.4996 | 0.004578 | 121.5637 | 61.6333 | -0.13733 | 121.4996 | 0.004578 | 61.6333 | 121.4905 | 121.5637 | -121.6827 | -121.8018
903.0781 | 121.9116 | -61.235 | 60.3607 | 0.15297 | 0.013687 | 0.0024033 | 0.012758 | 0.055027 | -0.012672 | 0.06733 | -61.3312 | 60.1501 | -61.3953 | -61.3586 | 60.0906 | 0.15564 | -0.29755 | 0.027466 | 60.2554 | -61.4548 | -0.16022 | -0.21057 | -0.096131 | -0.1236 | -0.27008 | -0.21973 | -0.10529 | 0.064087 | 60.9375 | 61.2625 | 121.3257 | 121.3852 | -0.096131 | 121.4905 | 61.3907 | -0.21973 | 121.3852 | -0.096131 | 61.3907 | 121.3257 | 121.4905 | -121.756 | -121.8155
904.8281 | 121.8842 | -61.2717 | 60.3287 | -0.25139 | 0.012191 | 0.0015487 | 0.01233 | 0.051609 | -0.009895 | 0.066475 | -61.3358 | 60.2737 | -61.322 | -61.3449 | 60.0998 | 0.2655 | 0.2655 | 0.20142 | 60.4065 | -61.3815 | -0.050354 | -0.054931 | -0.064087 | -0.073243 | -0.22888 | -0.10986 | 0.07782 | -0.013733 | 61.5372 | 61.4731 | 121.3715 | 121.5454 | -0.064087 | 121.6782 | 61.5372 | -0.10986 | 121.5454 | -0.064087 | 61.5372 | 121.3715 | 121.6782 | -121.6507 | -121.7102
906.5781 | 121.8521 | -61.235 | 60.4248 | -0.12932 | 0.011978 | -0.0027237 | 0.005708 | 0.050328 | -0.0092542 | 0.066475 | -61.2534 | 60.2417 | -61.2854 | -61.2442 | 60.2234 | 0.35248 | 0.022888 | 0.35706 | 60.3104 | -61.3998 | -0.050354 | -0.18311 | -0.018311 | -0.009156 | -0.20142 | -0.1648 | -0.11444 | 0.032043 | 61.2579 | 61.5921 | 121.4584 | 121.4767 | -0.018311 | 121.5454 | 61.5875 | -0.1648 | 121.4767 | -0.018311 | 61.5875 | 121.4584 | 121.5454 | -121.7102 | -121.8246
908.3281 | 121.8567 | -61.3312 | 60.3149 | 0.01564 | 0.010696 | 0.0030441 | 0.014467 | 0.052464 | -0.011177 | 0.069252 | -61.4044 | 60.1593 | -61.4136 | -61.4365 | 60.0082 | 0.082397 | -0.07782 | -0.054932 | 60.2737 | -61.4777 | -0.082397 | -0.15564 | -0.073242 | -0.10529 | -0.3067 | -0.14648 | -0.041198 | 0.009155 | 61.2534 | 61.2762 | 121.3394 | 121.4905 | -0.073242 | 121.6049 | 61.4136 | -0.14648 | 121.4905 | -0.073242 | 61.4136 | 121.3394 | 121.6049 | -121.7285 | -121.7926
910.0312 | 121.9299 | -61.1938 | 60.3928 | -0.030136 | 0.014328 | 0.0013351 | 0.007417 | 0.049687 | -0.008827 | 0.067543 | -61.3174 | 60.2325 | -61.2991 | -61.322 | 60.1593 | 0.27008 | 0.022888 | 0.23804 | 60.3653 | -61.4136 | -0.10528 | -0.16022 | -0.1236 | -0.12817 | -0.23346 | -0.21973 | -0.027466 | -0.018311 | 61.2167 | 61.4319 | 121.3531 | 121.4264 | -0.1236 | 121.5591 | 61.4639 | -0.21973 | 121.4264 | -0.1236 | 61.4639 | 121.3531 | 121.5591 | -121.6919 | -121.8063
911.7812 | 121.8567 | -61.2946 | 60.3333 | -0.030136 | 0.012832 | -0.0016557 | 0.012544 | 0.052677 | -0.011177 | 0.066902 | -61.3724 | 60.2097 | -61.4136 | -61.4227 | 60.0128 | 0.13275 | -0.086975 | -0.018311 | 60.2966 | -61.4594 | -0.11902 | -0.1236 | -0.077819 | -0.12817 | -0.32044 | -0.16479 | -0.036621 | 0.041199 | 61.2076 | 61.2762 | 121.3074 | 121.5042 | -0.077819 | 121.5912 | 61.4273 | -0.16479 | 121.5042 | -0.077819 | 61.4273 | 121.3074 | 121.5912 | -121.7468 | -121.7926
913.5156 | 121.9116 | -61.2396 | 60.3287 | 0.1606 | 0.012191 | -0.00080106 | 0.011689 | 0.052891 | -0.010963 | 0.067116 | -61.3815 | 60.141 | -61.3998 | -61.377 | 60.0677 | 0.12817 | -0.27008 | -0.004578 | 60.228 | -61.4456 | -0.16022 | -0.18768 | -0.14191 | -0.13733 | -0.26093 | -0.20599 | -0.10071 | 0.01831 | 60.9695 | 61.235 | 121.3074 | 121.3806 | -0.14191 | 121.4676 | 61.3678 | -0.20599 | 121.3806 | -0.14191 | 61.3678 | 121.3074 | 121.4676 | -121.7285 | -121.7743
915.25 | 121.9849 | -61.1618 | 60.379 | 0.030899 | 0.012832 | -0.0020829 | 0.007417 | 0.050114 | -0.0075452 | 0.066262 | -61.3358 | 60.2234 | -61.3129 | -61.3541 | 60.1227 | 0.20142 | -0.027466 | 0.14648 | 60.3012 | -61.3953 | -0.15106 | -0.15564 | -0.17395 | -0.19226 | -0.25635 | -0.23346 | -0.07782 | -0.022888 | 61.1343 | 61.3083 | 121.2845 | 121.3852 | -0.17395 | 121.463 | 61.3632 | -0.23346 | 121.3852 | -0.17395 | 61.3632 | 121.2845 | 121.463 | -121.6919 | -121.7743
916.9375 | 121.8384 | -61.2213 | 60.4294 | -0.13695 | 0.014755 | -0.00016026 | 0.0063488 | 0.049473 | -0.0096814 | 0.065834 | -61.2442 | 60.2142 | -61.2854 | -61.2259 | 60.2325 | 0.37994 | 0.036621 | 0.36163 | 60.3561 | -61.3632 | -0.064087 | -0.21515 | -0.022889 | -0.004578 | -0.19684 | -0.14191 | -0.073242 | 0.041198 | 61.2579 | 61.5829 | 121.4539 | 121.4355 | -0.022889 | 121.5775 | 61.6013 | -0.14191 | 121.4355 | -0.022889 | 61.6013 | 121.4539 | 121.5775 | -121.7148 | -121.7926
918.625 | 121.9482 | -61.2808 | 60.2829 | 0.046158 | 0.014969 | -0.0010147 | 0.013826 | 0.053959 | -0.012245 | 0.068611 | -61.4227 | 60.1822 | -61.4136 | -61.4914 | 59.9579 | 0.054932 | -0.10986 | -0.11444 | 60.3104 | -61.4685 | -0.13275 | -0.10071 | -0.14191 | -0.21057 | -0.32501 | -0.18768 | 0.027466 | -0.009155 | 61.171 | 61.1664 | 121.2387 | 121.463 | -0.14191 | 121.5912 | 61.3358 | -0.18768 | 121.463 | -0.14191 | 61.3358 | 121.2387 | 121.5912 | -121.6965 | -121.7514
920.375 | 121.9666 | -61.2625 | 60.3104 | 0.11482 | 0.013687 | -0.0014419 | 0.011476 | 0.052677 | -0.011818 | 0.067116 | -61.4502 | 60.173 | -61.4182 | -61.4822 | 59.9808 | 0.041199 | -0.14191 | -0.11444 | 60.3058 | -61.4685 | -0.15564 | -0.13733 | -0.18768 | -0.21973 | -0.32959 | -0.20599 | -0.004578 | -0.032043 | 61.1206 | 61.1481 | 121.2433 | 121.4355 | -0.18768 | 121.5683 | 61.3037 | -0.20599 | 121.4355 | -0.18768 | 61.3037 | 121.2433 | 121.5683 | -121.7285 | -121.7789
922.125 | 121.8796 | -61.2854 | 60.3836 | -0.22087 | 0.011551 | -0.00058746 | 0.010835 | 0.051609 | -0.010963 | 0.068398 | -61.3541 | 60.2875 | -61.3312 | -61.3678 | 60.0998 | 0.26093 | 0.22888 | 0.18768 | 60.3516 | -61.4182 | -0.045777 | -0.09613 | -0.068665 | -0.082398 | -0.28381 | -0.13275 | -0.032044 | -0.022888 | 61.5143 | 61.4731 | 121.3852 | 121.5729 | -0.068665 | 121.637 | 61.5463 | -0.13275 | 121.5729 | -0.068665 | 61.5463 | 121.3852 | 121.637 | -121.7148 | -121.8018
923.7969 | 121.9574 | -61.29 | 60.2921 | 0.10719 | 0.013687 | -0.00058746 | 0.0099804 | 0.05225 | -0.011604 | 0.06797 | -61.4456 | 60.173 | -61.4227 | -61.4914 | 59.9762 | 0.045776 | -0.1236 | -0.13733 | 60.3241 | -61.4868 | -0.13275 | -0.11902 | -0.15564 | -0.20142 | -0.31586 | -0.19684 | 0.032044 | -0.022889 | 61.1664 | 61.1526 | 121.2662 | 121.463 | -0.15564 | 121.6141 | 61.3358 | -0.19684 | 121.463 | -0.15564 | 61.3358 | 121.2662 | 121.6141 | -121.7148 | -121.7789
925.5469 | 121.9299 | -61.1755 | 60.4202 | -0.075912 | 0.011337 | -0.0016557 | 0.0050672 | 0.050114 | -0.0075452 | 0.065834 | -61.2946 | 60.2554 | -61.2762 | -61.2717 | 60.2051 | 0.31128 | 0.041199 | 0.3067 | 60.347 | -61.3678 | -0.10071 | -0.16479 | -0.11902 | -0.09613 | -0.21515 | -0.19226 | -0.073242 | -0.018311 | 61.2167 | 61.4822 | 121.3806 | 121.431 | -0.11902 | 121.5225 | 61.4868 | -0.19226 | 121.431 | -0.11902 | 61.4868 | 121.3806 | 121.5225 | -121.6965 | -121.788
927.2969 | 121.9345 | -61.235 | 60.3836 | 0.13771 | 0.011123 | 0.0013351 | 0.0069898 | 0.0499 | -0.0094678 | 0.069466 | -61.3449 | 60.1364 | -61.3815 | -61.3495 | 60.1227 | 0.16022 | -0.23804 | 0.082397 | 60.2646 | -61.4227 | -0.14649 | -0.24719 | -0.10986 | -0.11444 | -0.26093 | -0.18768 | -0.11902 | 0.036621 | 60.997 | 61.3174 | 121.3577 | 121.3715 | -0.10986 | 121.4996 | 61.3953 | -0.18768 | 121.3715 | -0.10986 | 61.3953 | 121.3577 | 121.4996 | -121.7651 | -121.8063
928.9844 | 121.8292 | -61.3358 | 60.3104 | -0.12932 | 0.015396 | 0.0015487 | 0.01233 | 0.053105 | -0.014167 | 0.068184 | -61.3449 | 60.2325 | -61.377 | -61.3678 | 60.0861 | 0.24261 | 0.064087 | 0.15106 | 60.3333 | -61.441 | -0.041199 | -0.07782 | -0.009156 | -0.032044 | -0.2243 | -0.10529 | 0.022888 | 0.032043 | 61.3998 | 61.4868 | 121.4218 | 121.5683 | -0.009156 | 121.669 | 61.5784 | -0.10529 | 121.5683 | -0.009156 | 61.5784 | 121.4218 | 121.669 | -121.6873 | -121.7514
930.7344 | 121.9254 | -61.2122 | 60.3607 | 0.10719 | 0.012619 | 0.00048074 | 0.0052808 | 0.0546 | -0.008827 | 0.06797 | -61.3174 | 60.1593 | -61.3403 | -61.3449 | 60.1044 | 0.15106 | -0.22888 | 0.09613 | 60.2737 | -61.4227 | -0.12817 | -0.20142 | -0.10529 | -0.13275 | -0.25635 | -0.21057 | -0.086975 | 0.022888 | 60.9833 | 61.3083 | 121.3165 | 121.3715 | -0.10529 | 121.4859 | 61.3632 | -0.21057 | 121.3715 | -0.10529 | 61.3632 | 121.3165 | 121.4859 | -121.701 | -121.7834
932.4844 | 121.9711 | -61.1938 | 60.4019 | 0.10719 | 0.0139 | -0.0012283 | 0.0072034 | 0.050541 | -0.01139 | 0.06733 | -61.3403 | 60.1135 | -61.3541 | -61.3678 | 60.1135 | 0.1831 | -0.12817 | 0.10986 | 60.3333 | -61.3907 | -0.16022 | -0.28839 | -0.14648 | -0.17395 | -0.28839 | -0.19684 | -0.068665 | 0.013733 | 61.0657 | 61.3037 | 121.3074 | 121.3074 | -0.14648 | 121.5271 | 61.377 | -0.19684 | 121.3074 | -0.14648 | 61.377 | 121.3074 | 121.5271 | -121.756 | -121.7926
934.1719 | 121.8155 | -61.3495 | 60.3195 | -0.075912 | 0.013473 | 0.0019759 | 0.015107 | 0.050968 | -0.013954 | 0.067116 | -61.3403 | 60.1913 | -61.3815 | -61.3632 | 60.0815 | 0.20599 | -0.004578 | 0.10529 | 60.3195 | -61.4548 | -0.032044 | -0.12817 | 0.009155 | -0.013733 | -0.23804 | -0.10529 | 0 | 0.041199 | 61.3449 | 61.4548 | 121.431 | 121.5408 | 0.009155 | 121.669 | 61.5555 | -0.10529 | 121.5408 | 0.009155 | 61.5555 | 121.431 | 121.669 | -121.7011 | -121.7743
935.875 | 121.8292 | -61.3083 | 60.3149 | -0.068283 | 0.014755 | 0.00090794 | 0.013398 | 0.052891 | -0.01075 | 0.066048 | -61.3129 | 60.2234 | -61.3495 | -61.3678 | 60.0815 | 0.18768 | -0.022888 | 0.064087 | 60.3287 | -61.4685 | -0.041198 | -0.091552 | -0.004577 | -0.059509 | -0.23346 | -0.16022 | 0.013733 | 0.036621 | 61.2854 | 61.3724 | 121.3898 | 121.5317 | -0.004577 | 121.637 | 61.496 | -0.16022 | 121.5317 | -0.004577 | 61.496 | 121.3898 | 121.637 | -121.6644 | -121.7834
937.6094 | 121.8658 | -61.2854 | 60.3424 | -0.21324 | 0.012619 | -0.0031509 | 0.0076306 | 0.051396 | -0.0092542 | 0.067543 | -61.3541 | 60.2737 | -61.3312 | -61.3632 | 60.0952 | 0.2655 | 0.20142 | 0.18768 | 60.3607 | -61.409 | -0.045777 | -0.068664 | -0.068665 | -0.07782 | -0.24719 | -0.1236 | 0.018311 | -0.022888 | 61.4868 | 61.4731 | 121.3806 | 121.5591 | -0.068665 | 121.6461 | 61.5509 | -0.1236 | 121.5591 | -0.068665 | 61.5509 | 121.3806 | 121.6461 | -121.6736 | -121.7514
939.3438 | 121.8521 | -61.2946 | 60.3378 | -0.17509 | 0.014328 | -0.0016557 | 0.0099804 | 0.050968 | -0.012031 | 0.06797 | -61.3541 | 60.2692 | -61.3449 | -61.3586 | 60.0906 | 0.26093 | 0.17395 | 0.17395 | 60.3699 | -61.441 | -0.050354 | -0.068665 | -0.059509 | -0.064087 | -0.24719 | -0.14648 | 0.032043 | -0.009155 | 61.4685 | 61.4685 | 121.3852 | 121.5637 | -0.059509 | 121.6644 | 61.5555 | -0.14648 | 121.5637 | -0.059509 | 61.5555 | 121.3852 | 121.6644 | -121.6827 | -121.7789
941.1094 | 121.9299 | -61.2808 | 60.3424 | 0.16823 | 0.013473 | -0.0016557 | 0.010194 | 0.054814 | -0.009895 | 0.069466 | -61.4182 | 60.1685 | -61.4227 | -61.4227 | 60.0586 | 0.09613 | -0.25177 | -0.050354 | 60.2554 | -61.4639 | -0.14191 | -0.17395 | -0.13733 | -0.14191 | -0.28381 | -0.18311 | -0.086975 | 0.004577 | 61.0291 | 61.2305 | 121.3394 | 121.4493 | -0.13733 | 121.5363 | 61.377 | -0.18311 | 121.4493 | -0.13733 | 61.377 | 121.3394 | 121.5363 | -121.7651 | -121.8063
942.7969 | 121.9666 | -61.2122 | 60.3653 | 0.046158 | 0.014328 | -0.0029373 | 0.005708 | 0.0499 | -0.0079724 | 0.06797 | -61.3495 | 60.2325 | -61.322 | -61.3724 | 60.1089 | 0.19684 | -0.073242 | 0.13275 | 60.2966 | -61.4319 | -0.10986 | -0.13275 | -0.13733 | -0.16022 | -0.25635 | -0.21973 | -0.068664 | -0.027466 | 61.1389 | 61.3449 | 121.3211 | 121.4447 | -0.13733 | 121.5088 | 61.409 | -0.21973 | 121.4447 | -0.13733 | 61.409 | 121.3211 | 121.5088 | -121.6873 | -121.7972
944.5312 | 121.9711 | -61.1938 | 60.4156 | 0.12245 | 0.01326 | 0.00026694 | 0.0059216 | 0.049687 | -0.010322 | 0.066048 | -61.322 | 60.1776 | -61.322 | -61.3449 | 60.1227 | 0.18768 | -0.13733 | 0.10986 | 60.3104 | -61.409 | -0.12817 | -0.23804 | -0.12817 | -0.15106 | -0.29297 | -0.21515 | -0.10529 | 0 | 61.0565 | 61.3037 | 121.3165 | 121.3715 | -0.12817 | 121.5042 | 61.3815 | -0.21515 | 121.3715 | -0.12817 | 61.3815 | 121.3165 | 121.5042 | -121.7377 | -121.8246
946.2344 | 121.9345 | -61.1984 | 60.4065 | 0.099564 | 0.013046 | -0.0029373 | 0.007417 | 0.050755 | -0.010109 | 0.068184 | -61.3449 | 60.173 | -61.3678 | -61.3495 | 60.1135 | 0.16937 | -0.15564 | 0.10529 | 60.3058 | -61.4319 | -0.16937 | -0.23346 | -0.14648 | -0.15106 | -0.29297 | -0.23346 | -0.10071 | 0.022888 | 61.0428 | 61.3037 | 121.3119 | 121.3715 | -0.14648 | 121.5042 | 61.3678 | -0.23346 | 121.3715 | -0.14648 | 61.3678 | 121.3119 | 121.5042 | -121.7743 | -121.8384
947.9688 | 121.8567 | -61.2305 | 60.4156 | -0.13695 | 0.01326 | -0.0018693 | 0.0072034 | 0.049687 | -0.01075 | 0.066475 | -61.2305 | 60.2554 | -61.2946 | -61.2396 | 60.2325 | 0.3891 | 0.045776 | 0.37079 | 60.3195 | -61.377 | -0.064087 | -0.16022 | 0 | -0.009155 | -0.18311 | -0.14648 | -0.09613 | 0.064087 | 61.2762 | 61.6013 | 121.463 | 121.4859 | 0 | 121.55 | 61.6196 | -0.14648 | 121.4859 | 0 | 61.6196 | 121.463 | 121.55 | -121.7102 | -121.7926
949.7188 | 121.8796 | -61.2717 | 60.3516 | -0.2285 | 0.015609 | -0.0031509 | 0.011049 | 0.049259 | -0.010109 | 0.066475 | -61.3449 | 60.3058 | -61.3495 | -61.3586 | 60.0906 | 0.2655 | 0.21057 | 0.19226 | 60.3882 | -61.4182 | -0.07782 | -0.045776 | -0.073243 | -0.086976 | -0.26093 | -0.14648 | 0.036622 | 0.004577 | 61.4822 | 61.4639 | 121.3623 | 121.5775 | -0.073243 | 121.6599 | 61.5372 | -0.14648 | 121.5775 | -0.073243 | 61.5372 | 121.3623 | 121.6599 | -121.701 | -121.7697
951.4062 | 121.8979 | -61.1938 | 60.4202 | -0.12169 | 0.011978 | -0.0046463 | 0.0059216 | 0.051823 | -0.0079724 | 0.066048 | -61.2442 | 60.2417 | -61.2717 | -61.2396 | 60.2188 | 0.34332 | 0.013733 | 0.33875 | 60.3378 | -61.3678 | -0.077819 | -0.17853 | -0.050354 | -0.045776 | -0.20142 | -0.17395 | -0.082397 | 0.027465 | 61.2076 | 61.5326 | 121.4127 | 121.4355 | -0.050354 | 121.5317 | 61.5372 | -0.17395 | 121.4355 | -0.050354 | 61.5372 | 121.4127 | 121.5317 | -121.6919 | -121.788
953.1562 | 121.8887 | -61.3083 | 60.2966 | 0.061417 | 0.013473 | 5.3338e-05 | 0.015107 | 0.050755 | -0.012458 | 0.067757 | -61.4319 | 60.1639 | -61.4594 | -61.4456 | 59.9899 | 0.064087 | -0.086975 | -0.064087 | 60.2966 | -61.4777 | -0.15106 | -0.13275 | -0.1236 | -0.13733 | -0.3067 | -0.16937 | 0 | 0.027466 | 61.2213 | 61.2442 | 121.2982 | 121.4722 | -0.1236 | 121.6049 | 61.3724 | -0.16937 | 121.4722 | -0.1236 | 61.3724 | 121.2982 | 121.6049 | -121.756 | -121.7743
954.8438 | 121.8658 | -61.2305 | 60.4111 | -0.16747 | 0.015182 | -0.0048599 | 0.0059216 | 0.049473 | -0.008186 | 0.067116 | -61.2625 | 60.2646 | -61.2854 | -61.2442 | 60.2142 | 0.35706 | 0.027466 | 0.34332 | 60.3012 | -61.3907 | -0.054931 | -0.14648 | -0.032043 | -0.013733 | -0.19684 | -0.16022 | -0.10986 | 0.022888 | 61.2579 | 61.5738 | 121.4447 | 121.4951 | -0.032043 | 121.5317 | 61.5875 | -0.16022 | 121.4951 | -0.032043 | 61.5875 | 121.4447 | 121.5317 | -121.6965 | -121.8018
956.5938 | 121.9482 | -61.1893 | 60.4202 | -0.045395 | 0.013687 | -0.0033647 | 0.0061352 | 0.050114 | -0.010322 | 0.067543 | -61.3174 | 60.2234 | -61.322 | -61.3129 | 60.1685 | 0.29755 | 0.022888 | 0.26093 | 60.3333 | -61.4182 | -0.13275 | -0.19684 | -0.12817 | -0.1236 | -0.25177 | -0.22888 | -0.086975 | 0.004577 | 61.2122 | 61.4502 | 121.3577 | 121.4127 | -0.12817 | 121.5225 | 61.4868 | -0.22888 | 121.4127 | -0.12817 | 61.4868 | 121.3577 | 121.5225 | -121.7422 | -121.8384
958.2812 | 121.8567 | -61.322 | 60.3424 | -0.037765 | 0.013473 | 0.00026694 | 0.012758 | 0.051182 | -0.012886 | 0.066689 | -61.3678 | 60.1776 | -61.4136 | -61.409 | 60.0403 | 0.12817 | -0.068665 | -0.004578 | 60.26 | -61.4914 | -0.091553 | -0.16479 | -0.045777 | -0.086976 | -0.30212 | -0.16937 | -0.082397 | 0.045776 | 61.2534 | 61.3174 | 121.3623 | 121.4996 | -0.045777 | 121.582 | 61.4502 | -0.16937 | 121.4996 | -0.045777 | 61.4502 | 121.3623 | 121.582 | -121.756 | -121.8338
960.0312 | 121.9666 | -61.1893 | 60.379 | -0.014877 | 0.012619 | -0.0031509 | 0.003999 | 0.052464 | -0.0092542 | 0.064553 | -61.3266 | 60.2371 | -61.3129 | -61.3358 | 60.1456 | 0.2655 | -0.009155 | 0.20142 | 60.3149 | -61.4136 | -0.1236 | -0.14191 | -0.13733 | -0.14648 | -0.23346 | -0.2243 | -0.064087 | -0.013733 | 61.1801 | 61.3907 | 121.3348 | 121.4264 | -0.13733 | 121.5042 | 61.4548 | -0.2243 | 121.4264 | -0.13733 | 61.4548 | 121.3348 | 121.5042 | -121.6919 | -121.7926
961.7344 | 121.8521 | -61.3083 | 60.3424 | -0.19035 | 0.013687 | -0.00016026 | 0.01233 | 0.049687 | -0.010322 | 0.067543 | -61.3678 | 60.2463 | -61.3998 | -61.3586 | 60.1044 | 0.24261 | 0.13275 | 0.15564 | 60.3516 | -61.4456 | -0.091552 | -0.09613 | -0.059509 | -0.050354 | -0.23804 | -0.13733 | 0.009155 | 0.032043 | 61.441 | 61.4639 | 121.4127 | 121.5546 | -0.059509 | 121.6599 | 61.5509 | -0.13733 | 121.5546 | -0.059509 | 61.5509 | 121.4127 | 121.6599 | -121.7422 | -121.788
963.4688 | 121.8613 | -61.3037 | 60.3516 | -0.16747 | 0.014541 | 0.0028305 | 0.0097668 | 0.050328 | -0.009895 | 0.065407 | -61.3403 | 60.2737 | -61.3678 | -61.3586 | 60.1044 | 0.23804 | 0.1831 | 0.19226 | 60.3516 | -61.4273 | -0.064087 | -0.077819 | -0.036621 | -0.054932 | -0.24719 | -0.1236 | 0 | 0.027466 | 61.4868 | 61.496 | 121.4081 | 121.5775 | -0.036621 | 121.6553 | 61.5417 | -0.1236 | 121.5775 | -0.036621 | 61.5417 | 121.4081 | 121.6553 | -121.7194 | -121.7789
965.2188 | 121.8521 | -61.2305 | 60.4477 | -0.17509 | 0.012405 | 0.00090794 | 0.0048534 | 0.049046 | -0.0094678 | 0.066475 | -61.2122 | 60.2875 | -61.2671 | -61.2259 | 60.2371 | 0.3891 | 0.073242 | 0.38452 | 60.3561 | -61.3586 | -0.036621 | -0.16022 | 0.018311 | 0.004578 | -0.21057 | -0.12817 | -0.091553 | 0.054932 | 61.3037 | 61.615 | 121.4676 | 121.5179 | 0.018311 | 121.5866 | 61.6196 | -0.12817 | 121.5179 | 0.018311 | 61.6196 | 121.4676 | 121.5866 | -121.7148 | -121.8063
966.9062 | 121.907 | -61.2259 | 60.3699 | 0.15297 | 0.012191 | 0.0036849 | 0.009126 | 0.054173 | -0.009895 | 0.066689 | -61.3129 | 60.1501 | -61.3586 | -61.3358 | 60.1135 | 0.16479 | -0.27924 | 0.064087 | 60.2829 | -61.4273 | -0.13275 | -0.21973 | -0.086975 | -0.10986 | -0.25635 | -0.20142 | -0.086975 | 0.045777 | 60.9467 | 61.29 | 121.3394 | 121.376 | -0.086975 | 121.5088 | 61.3907 | -0.20142 | 121.376 | -0.086975 | 61.3907 | 121.3394 | 121.5088 | -121.7285 | -121.7972
968.6562 | 121.9666 | -61.1938 | 60.4019 | -0.014877 | 0.011551 | -0.0012283 | 0.0072034 | 0.052464 | -0.0083996 | 0.065407 | -61.3312 | 60.2463 | -61.3129 | -61.3403 | 60.1318 | 0.24719 | 0.004578 | 0.21515 | 60.3195 | -61.3861 | -0.11902 | -0.15564 | -0.13733 | -0.14648 | -0.27008 | -0.19226 | -0.082398 | -0.018311 | 61.1984 | 61.409 | 121.3257 | 121.4401 | -0.13733 | 121.5134 | 61.441 | -0.19226 | 121.4401 | -0.13733 | 61.441 | 121.3257 | 121.5134 | -121.7148 | -121.788
970.3438 | 121.8887 | -61.3037 | 60.2692 | 0.030899 | 0.012832 | 0.00048074 | 0.015748 | 0.052677 | -0.011604 | 0.069039 | -61.4227 | 60.1822 | -61.441 | -61.4639 | 60.0037 | 0.07782 | -0.07782 | -0.054932 | 60.2966 | -61.4685 | -0.13733 | -0.086975 | -0.11902 | -0.16022 | -0.2655 | -0.16479 | 0.027466 | 0.018311 | 61.2259 | 61.2488 | 121.3074 | 121.4859 | -0.11902 | 121.6003 | 61.3815 | -0.16479 | 121.4859 | -0.11902 | 61.3815 | 121.3074 | 121.6003 | -121.7102 | -121.7377
972.0781 | 121.9116 | -61.2396 | 60.3699 | 0.10719 | 0.013473 | -0.0012283 | 0.009126 | 0.055668 | -0.011604 | 0.066902 | -61.3312 | 60.141 | -61.3861 | -61.3632 | 60.0861 | 0.14191 | -0.28839 | 0.032043 | 60.2463 | -61.4502 | -0.14648 | -0.22888 | -0.091553 | -0.1236 | -0.28381 | -0.21057 | -0.1236 | 0.054931 | 60.9512 | 61.2717 | 121.3257 | 121.3806 | -0.091553 | 121.4859 | 61.3815 | -0.21057 | 121.3806 | -0.091553 | 61.3815 | 121.3257 | 121.4859 | -121.756 | -121.8201
973.8125 | 121.9803 | -61.2076 | 60.3836 | 0.053787 | 0.0139 | -0.00058746 | 0.005708 | 0.05225 | -0.008827 | 0.06797 | -61.3312 | 60.2142 | -61.3403 | -61.3632 | 60.1089 | 0.20142 | -0.073242 | 0.12817 | 60.3241 | -61.4044 | -0.13275 | -0.16937 | -0.1236 | -0.15564 | -0.27466 | -0.19684 | -0.059509 | 0.009155 | 61.1343 | 61.3358 | 121.3165 | 121.4218 | -0.1236 | 121.5317 | 61.409 | -0.19684 | 121.4218 | -0.1236 | 61.409 | 121.3165 | 121.5317 | -121.7239 | -121.788
975.5625 | 121.8521 | -61.2442 | 60.4111 | -0.20561 | 0.0139 | -0.0010147 | 0.0076306 | 0.051182 | -0.009895 | 0.066048 | -61.2305 | 60.2646 | -61.2534 | -61.2442 | 60.2097 | 0.39368 | 0.091553 | 0.37994 | 60.3378 | -61.4044 | -0.009155 | -0.14648 | 0.013733 | 0 | -0.20142 | -0.16022 | -0.073242 | 0.022888 | 61.3358 | 61.6241 | 121.4539 | 121.5088 | 0.013733 | 121.582 | 61.6379 | -0.16022 | 121.5088 | 0.013733 | 61.6379 | 121.4539 | 121.582 | -121.6644 | -121.8155
977.25 | 121.875 | -61.2076 | 60.4156 | -0.11406 | 0.012832 | 0.0013351 | 0.0072034 | 0.05225 | -0.0096814 | 0.066475 | -61.2488 | 60.2463 | -61.2991 | -61.2488 | 60.2234 | 0.3479 | 0.027466 | 0.35248 | 60.3195 | -61.3815 | -0.091552 | -0.16937 | -0.041198 | -0.041198 | -0.19226 | -0.17395 | -0.09613 | 0.050354 | 61.235 | 61.5601 | 121.431 | 121.4539 | -0.041198 | 121.5271 | 61.5555 | -0.17395 | 121.4539 | -0.041198 | 61.5555 | 121.431 | 121.5271 | -121.7148 | -121.7972
979 | 121.8246 | -61.3129 | 60.3424 | -0.12169 | 0.012191 | -0.0016557 | 0.015535 | 0.051823 | -0.012672 | 0.069039 | -61.3449 | 60.1913 | -61.3998 | -61.3632 | 60.0906 | 0.22888 | 0.027466 | 0.1236 | 60.3378 | -61.4548 | -0.086975 | -0.15106 | -0.032044 | -0.050354 | -0.25177 | -0.14191 | -0.004577 | 0.054931 | 61.3403 | 61.4365 | 121.4035 | 121.5042 | -0.032044 | 121.6507 | 61.5417 | -0.14191 | 121.5042 | -0.032044 | 61.5417 | 121.4035 | 121.6507 | -121.7422 | -121.7972
980.75 | 121.9711 | -61.2808 | 60.2737 | 0.10719 | 0.013046 | -0.0014419 | 0.012758 | 0.051823 | -0.011177 | 0.068611 | -61.4365 | 60.1593 | -61.4502 | -61.4731 | 59.9854 | 0.045776 | -0.14191 | -0.10071 | 60.3149 | -61.5234 | -0.16937 | -0.11444 | -0.15564 | -0.19226 | -0.28839 | -0.24261 | 0.041198 | 0.013733 | 61.1389 | 61.1801 | 121.2662 | 121.4401 | -0.15564 | 121.5958 | 61.3266 | -0.24261 | 121.4401 | -0.15564 | 61.3266 | 121.2662 | 121.5958 | -121.7239 | -121.7972
982.4375 | 121.9391 | -61.2946 | 60.2966 | 0.053787 | 0.015396 | -0.00058746 | 0.012758 | 0.055027 | -0.010963 | 0.065407 | -61.4227 | 60.173 | -61.4365 | -61.4685 | 59.9945 | 0.059509 | -0.064087 | -0.10071 | 60.3424 | -61.4456 | -0.14191 | -0.1236 | -0.12817 | -0.17395 | -0.30212 | -0.15106 | 0.045776 | 0.013733 | 61.2305 | 61.1938 | 121.2891 | 121.4676 | -0.12817 | 121.637 | 61.3541 | -0.15106 | 121.4676 | -0.12817 | 61.3541 | 121.2891 | 121.637 | -121.7331 | -121.7422
984.1875 | 121.9482 | -61.2671 | 60.2875 | 0.11482 | 0.014541 | 0.00069434 | 0.009126 | 0.053105 | -0.011818 | 0.067116 | -61.409 | 60.1868 | -61.3953 | -61.4594 | 60.022 | 0.059509 | -0.2243 | -0.082397 | 60.2966 | -61.4822 | -0.12817 | -0.10071 | -0.14191 | -0.19226 | -0.2655 | -0.21515 | 0.009155 | -0.013733 | 61.0428 | 61.1847 | 121.2891 | 121.4539 | -0.14191 | 121.5637 | 61.3266 | -0.21515 | 121.4539 | -0.14191 | 61.3266 | 121.2891 | 121.5637 | -121.6827 | -121.7697
985.9375 | 121.8384 | -61.3312 | 60.3149 | -0.098801 | 0.012832 | 0.0026169 | 0.010621 | 0.052891 | -0.012672 | 0.06797 | -61.3495 | 60.2325 | -61.377 | -61.3632 | 60.0952 | 0.23346 | -0.004578 | 0.11902 | 60.3424 | -61.4731 | -0.045776 | -0.082397 | -0.01831 | -0.032043 | -0.21973 | -0.14191 | 0.027466 | 0.027466 | 61.3266 | 61.4502 | 121.4264 | 121.5637 | -0.01831 | 121.6736 | 61.5646 | -0.14191 | 121.5637 | -0.01831 | 61.5646 | 121.4264 | 121.6736 | -121.6919 | -121.788
987.625 | 121.8384 | -61.2259 | 60.4065 | -0.19798 | 0.011764 | 5.3338e-05 | 0.0052808 | 0.050755 | -0.008186 | 0.066689 | -61.2488 | 60.26 | -61.2762 | -61.2625 | 60.2234 | 0.39368 | 0.10529 | 0.36163 | 60.347 | -61.3678 | -0.050354 | -0.14648 | -0.022888 | -0.036621 | -0.18311 | -0.14191 | -0.059509 | 0.027466 | 61.3312 | 61.5875 | 121.4493 | 121.4859 | -0.022888 | 121.5729 | 61.6196 | -0.14191 | 121.4859 | -0.022888 | 61.6196 | 121.4493 | 121.5729 | -121.6827 | -121.7743
989.375 | 121.8567 | -61.235 | 60.4385 | -0.12169 | 0.0139 | 0.00026694 | 0.003999 | 0.049473 | -0.0083996 | 0.067116 | -61.2488 | 60.2463 | -61.29 | -61.2305 | 60.2509 | 0.3891 | 0.036621 | 0.36163 | 60.347 | -61.3907 | -0.054932 | -0.19226 | -0.013733 | 0.004577 | -0.18768 | -0.15564 | -0.091553 | 0.041199 | 61.2717 | 61.5967 | 121.4859 | 121.4813 | -0.013733 | 121.582 | 61.6241 | -0.15564 | 121.4813 | -0.013733 | 61.6241 | 121.4859 | 121.582 | -121.7285 | -121.8292
991.125 | 121.8292 | -61.235 | 60.434 | -0.19798 | 0.012191 | 0.0013351 | 0.0082714 | 0.048405 | -0.0090406 | 0.065407 | -61.235 | 60.2783 | -61.2762 | -61.2534 | 60.2234 | 0.38452 | 0.10529 | 0.37537 | 60.3516 | -61.3724 | -0.041199 | -0.15564 | 0 | -0.018311 | -0.21057 | -0.13733 | -0.082398 | 0.041199 | 61.3403 | 61.6104 | 121.4584 | 121.5134 | 0 | 121.5866 | 61.6196 | -0.13733 | 121.5134 | 0 | 61.6196 | 121.4584 | 121.5866 | -121.7102 | -121.8063
992.875 | 121.8521 | -61.3495 | 60.3104 | -0.060654 | 0.012191 | 0.0030441 | 0.01468 | 0.052464 | -0.012886 | 0.065193 | -61.3358 | 60.1776 | -61.4182 | -61.3724 | 60.0861 | 0.21057 | -0.027466 | 0.082397 | 60.347 | -61.4319 | -0.068665 | -0.13275 | 0.013733 | -0.022888 | -0.2243 | -0.082398 | 0.036621 | 0.082398 | 61.322 | 61.4319 | 121.4355 | 121.5271 | 0.013733 | 121.6965 | 61.5601 | -0.082398 | 121.5271 | 0.013733 | 61.5601 | 121.4355 | 121.6965 | -121.7285 | -121.7422
994.625 | 121.8613 | -61.2762 | 60.4248 | -0.25139 | 0.011978 | -0.0052873 | 0.0061352 | 0.050328 | -0.01139 | 0.06797 | -61.2671 | 60.2371 | -61.2991 | -61.2808 | 60.1913 | 0.36621 | 0.20142 | 0.33875 | 60.379 | -61.3586 | -0.022888 | -0.18768 | 0.009155 | -0.004578 | -0.23346 | -0.082398 | -0.045777 | 0.032043 | 61.4777 | 61.615 | 121.4676 | 121.5134 | 0.009155 | 121.6553 | 61.6425 | -0.082398 | 121.5134 | 0.009155 | 61.6425 | 121.4676 | 121.6553 | -121.7239 | -121.7834
996.3125 | 121.8521 | -61.322 | 60.3378 | -0.16747 | 0.014541 | 0.0013351 | 0.012544 | 0.053105 | -0.012245 | 0.065834 | -61.3632 | 60.2371 | -61.3724 | -61.3678 | 60.1044 | 0.25177 | 0.16937 | 0.16479 | 60.3836 | -61.3861 | -0.050354 | -0.10071 | -0.041199 | -0.045777 | -0.23346 | -0.064087 | 0.045776 | 0.009155 | 61.4914 | 61.4868 | 121.4264 | 121.5591 | -0.041199 | 121.7056 | 61.5738 | -0.064087 | 121.5591 | -0.041199 | 61.5738 | 121.4264 | 121.7056 | -121.7102 | -121.7239
998.0625 | 121.9574 | -61.2259 | 60.3928 | 0.11482 | 0.013687 | 0.0013351 | 0.0065624 | 0.050114 | -0.007118 | 0.06797 | -61.3083 | 60.1639 | -61.3678 | -61.3632 | 60.1089 | 0.19226 | -0.15106 | 0.10529 | 60.3195 | -61.4136 | -0.14191 | -0.22888 | -0.082398 | -0.13733 | -0.28381 | -0.18768 | -0.073242 | 0.059509 | 61.0748 | 61.3312 | 121.3348 | 121.3898 | -0.082398 | 121.5454 | 61.4182 | -0.18768 | 121.3898 | -0.082398 | 61.4182 | 121.3348 | 121.5454 | -121.7606 | -121.8063
999.8125 | 121.8842 | -61.2946 | 60.3516 | -0.23613 | 0.012619 | 0.00048074 | 0.011049 | 0.049687 | -0.01139 | 0.067543 | -61.3495 | 60.26 | -61.3266 | -61.3495 | 60.1227 | 0.27924 | 0.27466 | 0.23804 | 60.4156 | -61.3815 | -0.032043 | -0.091552 | -0.054931 | -0.054931 | -0.22888 | -0.086975 | 0.064087 | -0.022888 | 61.5692 | 61.5326 | 121.4172 | 121.5546 | -0.054931 | 121.7102 | 61.5738 | -0.086975 | 121.5546 | -0.054931 | 61.5738 | 121.4172 | 121.7102 | -121.6782 | -121.7331
1001.5625 | 121.9345 | -61.2396 | 60.3882 | 0.11482 | 0.012619 | 0.0015487 | 0.0082714 | 0.052891 | -0.0086132 | 0.067116 | -61.3358 | 60.1501 | -61.3632 | -61.3632 | 60.1135 | 0.17853 | -0.21973 | 0.068665 | 60.3012 | -61.4273 | -0.1236 | -0.23804 | -0.09613 | -0.1236 | -0.27466 | -0.18768 | -0.086976 | 0.027466 | 61.0199 | 61.3083 | 121.3531 | 121.3898 | -0.09613 | 121.5408 | 61.4182 | -0.18768 | 121.3898 | -0.09613 | 61.4182 | 121.3531 | 121.5408 | -121.7514 | -121.8155
1003.25 | 121.9574 | -61.2579 | 60.2966 | 0.076676 | 0.014328 | -0.0031509 | 0.01233 | 0.053318 | -0.008827 | 0.068611 | -61.4273 | 60.1776 | -61.4273 | -61.4594 | 59.9991 | 0.059509 | -0.13733 | -0.10071 | 60.3378 | -61.4777 | -0.16937 | -0.11902 | -0.16937 | -0.20142 | -0.29755 | -0.21973 | 0.041199 | 0 | 61.1206 | 61.1572 | 121.257 | 121.4355 | -0.16937 | 121.5958 | 61.3174 | -0.21973 | 121.4355 | -0.16937 | 61.3174 | 121.257 | 121.5958 | -121.7239 | -121.7743
1005 | 121.9803 | -61.1801 | 60.4111 | 0.00038159 | 0.013046 | -0.00080106 | 0.0037854 | 0.0499 | -0.0083996 | 0.065193 | -61.3403 | 60.2554 | -61.322 | -61.3358 | 60.141 | 0.23804 | -0.004578 | 0.18768 | 60.3424 | -61.409 | -0.14191 | -0.15564 | -0.16022 | -0.15564 | -0.27008 | -0.22888 | -0.068665 | -0.018311 | 61.1755 | 61.3678 | 121.3211 | 121.4355 | -0.16022 | 121.5225 | 61.4182 | -0.22888 | 121.4355 | -0.16022 | 61.4182 | 121.3211 | 121.5225 | -121.7331 | -121.8201
1006.7344 | 121.8658 | -61.203 | 60.4294 | -0.13695 | 0.01326 | -0.0057145 | 0.0067762 | 0.049259 | -0.008827 | 0.067757 | -61.2442 | 60.2554 | -61.2854 | -61.2579 | 60.2234 | 0.37079 | 0.004578 | 0.33875 | 60.3287 | -61.3815 | -0.082397 | -0.17395 | -0.041199 | -0.054932 | -0.20599 | -0.17853 | -0.10071 | 0.041198 | 61.2076 | 61.5417 | 121.4264 | 121.4584 | -0.041199 | 121.5317 | 61.5738 | -0.17853 | 121.4584 | -0.041199 | 61.5738 | 121.4264 | 121.5317 | -121.7148 | -121.8109
1008.4844 | 121.9162 | -61.2122 | 60.4294 | -0.098801 | 0.0092008 | -0.00058746 | 0.0067762 | 0.048619 | -0.0066906 | 0.066475 | -61.2579 | 60.2509 | -61.29 | -61.2534 | 60.2097 | 0.36163 | 0.013733 | 0.33417 | 60.3378 | -61.377 | -0.07782 | -0.17853 | -0.045777 | -0.041199 | -0.21973 | -0.16479 | -0.091552 | 0.032043 | 61.2259 | 61.5463 | 121.4218 | 121.463 | -0.045777 | 121.55 | 61.5738 | -0.16479 | 121.463 | -0.045777 | 61.5738 | 121.4218 | 121.55 | -121.7194 | -121.8063
1010.1562 | 121.9803 | -61.2717 | 60.2921 | 0.10719 | 0.012619 | -0.0016557 | 0.015535 | 0.049687 | -0.01075 | 0.066262 | -61.4365 | 60.141 | -61.4502 | -61.4685 | 59.9899 | 0.045776 | -0.13275 | -0.10071 | 60.2737 | -61.4685 | -0.17853 | -0.15106 | -0.16479 | -0.19684 | -0.30212 | -0.19684 | -0.01831 | 0.013733 | 61.1389 | 61.171 | 121.2616 | 121.4127 | -0.16479 | 121.5454 | 61.3174 | -0.19684 | 121.4127 | -0.16479 | 61.3174 | 121.2616 | 121.5454 | -121.7422 | -121.7606
1011.9062 | 121.9299 | -61.2442 | 60.3607 | 0.35133 | 0.013046 | -0.0018693 | 0.010835 | 0.052464 | -0.011604 | 0.066048 | -61.3449 | 60.1181 | -61.3815 | -61.3495 | 60.0952 | 0.13733 | -0.28839 | 0.032043 | 60.2554 | -61.4639 | -0.13733 | -0.24262 | -0.10071 | -0.10529 | -0.2655 | -0.21973 | -0.10529 | 0.036621 | 60.9558 | 61.2762 | 121.3394 | 121.3623 | -0.10071 | 121.4996 | 61.3815 | -0.21973 | 121.3623 | -0.10071 | 61.3815 | 121.3394 | 121.4996 | -121.7422 | -121.8246
1013.5781 | 121.9482 | -61.2122 | 60.4156 | 0.10719 | 0.013046 | 0.0011215 | 0.0078442 | 0.050328 | -0.0092542 | 0.066475 | -61.3266 | 60.1456 | -61.3678 | -61.3495 | 60.1181 | 0.16937 | -0.16937 | 0.10986 | 60.2875 | -61.4273 | -0.15564 | -0.27008 | -0.11444 | -0.13733 | -0.29755 | -0.21515 | -0.12817 | 0.041199 | 61.0428 | 61.322 | 121.3303 | 121.3577 | -0.11444 | 121.4996 | 61.3815 | -0.21515 | 121.3577 | -0.11444 | 61.3815 | 121.3303 | 121.4996 | -121.7834 | -121.843
1015.3125 | 122.0032 | -61.1938 | 60.4111 | -0.0072479 | 0.012832 | -0.0035783 | 0.005708 | 0.049473 | -0.0090406 | 0.066689 | -61.3358 | 60.228 | -61.322 | -61.3678 | 60.1044 | 0.21515 | -0.018311 | 0.16022 | 60.3149 | -61.409 | -0.12817 | -0.18311 | -0.14191 | -0.17395 | -0.3067 | -0.21515 | -0.096131 | -0.013733 | 61.1755 | 61.3541 | 121.2982 | 121.4218 | -0.14191 | 121.5088 | 61.409 | -0.21515 | 121.4218 | -0.14191 | 61.409 | 121.2982 | 121.5088 | -121.7331 | -121.8201
1017.0625 | 121.9482 | -61.2762 | 60.3104 | 0.10719 | 0.015823 | 0.0026169 | 0.013826 | 0.050114 | -0.010536 | 0.066475 | -61.3998 | 60.1639 | -61.4456 | -61.4456 | 59.9945 | 0.050354 | -0.21057 | -0.09613 | 60.2921 | -61.4868 | -0.16937 | -0.14648 | -0.1236 | -0.16937 | -0.31586 | -0.21057 | -0.018311 | 0.045777 | 61.0657 | 61.1801 | 121.2708 | 121.4401 | -0.1236 | 121.5683 | 61.3266 | -0.21057 | 121.4401 | -0.1236 | 61.3266 | 121.2708 | 121.5683 | -121.756 | -121.7972
1018.7344 | 121.8338 | -61.3449 | 60.3424 | -0.083542 | 0.012405 | -0.0025101 | 0.012758 | 0.050114 | -0.01075 | 0.067543 | -61.3403 | 60.2005 | -61.3953 | -61.3724 | 60.0723 | 0.21515 | -0.041199 | 0.082397 | 60.3104 | -61.4639 | -0.050354 | -0.14191 | 0.004578 | -0.027465 | -0.27008 | -0.11902 | -0.032043 | 0.054932 | 61.3037 | 61.4273 | 121.4172 | 121.5454 | 0.004578 | 121.6553 | 61.5601 | -0.11902 | 121.5454 | 0.004578 | 61.5601 | 121.4172 | 121.6553 | -121.7377 | -121.8063
1020.4844 | 121.9116 | -61.235 | 60.3745 | 0.14534 | 0.013046 | 0.0015487 | 0.010835 | 0.050328 | -0.012031 | 0.067116 | -61.3266 | 60.1776 | -61.3678 | -61.3449 | 60.1135 | 0.16937 | -0.27924 | 0.073242 | 60.2463 | -61.4548 | -0.13275 | -0.19684 | -0.091553 | -0.10986 | -0.26093 | -0.21973 | -0.12817 | 0.041199 | 60.9558 | 61.3083 | 121.3486 | 121.4127 | -0.091553 | 121.4813 | 61.4044 | -0.21973 | 121.4127 | -0.091553 | 61.4044 | 121.3486 | 121.4813 | -121.7422 | -121.8292
1022.25 | 121.8887 | -61.3266 | 60.3104 | 0.01564 | 0.013687 | 5.3338e-05 | 0.013826 | 0.050968 | -0.012031 | 0.068184 | -61.3953 | 60.1868 | -61.4227 | -61.4502 | 60.0128 | 0.086975 | -0.07782 | -0.054932 | 60.2875 | -61.4914 | -0.09613 | -0.1236 | -0.068665 | -0.1236 | -0.29755 | -0.16479 | -0.022888 | 0.027465 | 61.2488 | 61.2717 | 121.3394 | 121.5134 | -0.068665 | 121.6141 | 61.4136 | -0.16479 | 121.5134 | -0.068665 | 61.4136 | 121.3394 | 121.6141 | -121.7331 | -121.8018
1023.9375 | 121.8842 | -61.2762 | 60.3516 | -0.21324 | 0.014114 | 0.0011215 | 0.007417 | 0.051396 | -0.01139 | 0.068825 | -61.3312 | 60.3012 | -61.3266 | -61.3586 | 60.1318 | 0.29297 | 0.26093 | 0.24261 | 60.4019 | -61.409 | -0.050354 | -0.050354 | -0.054932 | -0.082398 | -0.21973 | -0.13275 | 0.050355 | -0.004578 | 61.5372 | 61.5189 | 121.4081 | 121.5775 | -0.054932 | 121.6782 | 61.5692 | -0.13275 | 121.5775 | -0.054932 | 61.5692 | 121.4081 | 121.6782 | -121.6782 | -121.7606
1025.6719 | 121.8613 | -61.322 | 60.3195 | -0.053024 | 0.014969 | -0.00016026 | 0.013826 | 0.053318 | -0.010536 | 0.068184 | -61.3358 | 60.2509 | -61.3998 | -61.3724 | 60.0906 | 0.1831 | -0.036621 | 0.064087 | 60.347 | -61.4548 | -0.07782 | -0.068665 | -0.013733 | -0.050354 | -0.22888 | -0.13275 | 0.027466 | 0.064087 | 61.2854 | 61.3861 | 121.4127 | 121.5729 | -0.013733 | 121.669 | 61.5051 | -0.13275 | 121.5729 | -0.013733 | 61.5051 | 121.4127 | 121.669 | -121.7194 | -121.7743
1027.4219 | 121.8292 | -61.2213 | 60.4385 | -0.19035 | 0.010482 | 0.0017623 | 0.0063488 | 0.049687 | -0.011818 | 0.065407 | -61.2442 | 60.26 | -61.2854 | -61.2579 | 60.2234 | 0.40283 | 0.10529 | 0.35706 | 60.3516 | -61.3724 | -0.064087 | -0.17853 | -0.022889 | -0.036622 | -0.21515 | -0.15106 | -0.086976 | 0.041198 | 61.3266 | 61.5784 | 121.4447 | 121.4813 | -0.022889 | 121.5729 | 61.6241 | -0.15106 | 121.4813 | -0.022889 | 61.6241 | 121.4447 | 121.5729 | -121.7239 | -121.8109
1029.1875 | 121.8796 | -61.2717 | 60.3516 | -0.2285 | 0.014755 | -0.0020829 | 0.0095532 | 0.053959 | -0.010963 | 0.066048 | -61.3403 | 60.3012 | -61.3358 | -61.3541 | 60.1181 | 0.28839 | 0.25635 | 0.22888 | 60.4248 | -61.3953 | -0.064087 | -0.050354 | -0.068665 | -0.082398 | -0.23346 | -0.1236 | 0.073243 | -0.004578 | 61.528 | 61.5005 | 121.3898 | 121.5729 | -0.068665 | 121.6965 | 61.5601 | -0.1236 | 121.5729 | -0.068665 | 61.5601 | 121.3898 | 121.6965 | -121.6873 | -121.7468
1030.875 | 121.8658 | -61.29 | 60.3653 | -0.19035 | 0.012832 | 0.0021895 | 0.012117 | 0.051823 | -0.014595 | 0.067757 | -61.3678 | 60.26 | -61.3861 | -61.3632 | 60.0861 | 0.26093 | 0.18768 | 0.17853 | 60.3928 | -61.3953 | -0.09613 | -0.10529 | -0.07782 | -0.073242 | -0.27923 | -0.10529 | 0.027466 | 0.01831 | 61.4777 | 61.4685 | 121.376 | 121.55 | -0.07782 | 121.6827 | 61.5509 | -0.10529 | 121.55 | -0.07782 | 61.5509 | 121.376 | 121.6827 | -121.7514 | -121.7606
1032.6406 | 121.8842 | -61.2534 | 60.3745 | -0.10643 | 0.011764 | -0.0046463 | 0.0078442 | 0.050968 | -0.010322 | 0.067543 | -61.3586 | 60.2692 | -61.3174 | -61.3541 | 60.1273 | 0.29755 | 0.2655 | 0.24719 | 60.3973 | -61.3815 | -0.064087 | -0.10529 | -0.10529 | -0.10071 | -0.24719 | -0.12817 | 0.022888 | -0.041199 | 61.5189 | 61.5005 | 121.3806 | 121.5225 | -0.10529 | 121.6507 | 61.5509 | -0.12817 | 121.5225 | -0.10529 | 61.5509 | 121.3806 | 121.6507 | -121.6919 | -121.756
1034.3281 | 121.907 | -61.2396 | 60.3424 | 0.11482 | 0.013473 | 5.3338e-05 | 0.0089124 | 0.052677 | -0.012031 | 0.066902 | -61.3129 | 60.1547 | -61.3907 | -61.3678 | 60.1089 | 0.16022 | -0.29297 | 0.022888 | 60.2737 | -61.441 | -0.15106 | -0.18768 | -0.073242 | -0.12817 | -0.23346 | -0.20142 | -0.068664 | 0.07782 | 60.9467 | 61.2625 | 121.3486 | 121.3943 | -0.073242 | 121.5134 | 61.3998 | -0.20142 | 121.3943 | -0.073242 | 61.3998 | 121.3486 | 121.5134 | -121.7331 | -121.7834
1036.0625 | 121.8384 | -61.2579 | 60.4156 | -0.15221 | 0.012405 | 0.0011215 | 0.0069898 | 0.0499 | -0.010322 | 0.065834 | -61.2442 | 60.2554 | -61.2671 | -61.2671 | 60.2097 | 0.38452 | 0.13733 | 0.36163 | 60.379 | -61.3632 | -0.009155 | -0.16022 | 0.013733 | -0.009155 | -0.20599 | -0.10528 | -0.036621 | 0.022888 | 61.3953 | 61.6196 | 121.4676 | 121.5134 | 0.013733 | 121.637 | 61.6425 | -0.10528 | 121.5134 | 0.013733 | 61.6425 | 121.4676 | 121.637 | -121.6827 | -121.7789
1037.75 | 121.8796 | -61.2854 | 60.3745 | -0.25902 | 0.013473 | 0.0026169 | 0.0093396 | 0.048832 | -0.0096814 | 0.064766 | -61.2854 | 60.2875 | -61.3129 | -61.3358 | 60.1364 | 0.32959 | 0.23346 | 0.27466 | 60.4111 | -61.3861 | -0.027466 | -0.086975 | 0 | -0.050354 | -0.23804 | -0.10071 | 0.036621 | 0.027466 | 61.5189 | 61.5601 | 121.4218 | 121.5729 | 0 | 121.6965 | 61.615 | -0.10071 | 121.5729 | 0 | 61.615 | 121.4218 | 121.6965 | -121.6873 | -121.7606
1039.4844 | 121.8338 | -61.3037 | 60.3104 | -0.12932 | 0.016037 | -0.0027237 | 0.012544 | 0.050968 | -0.013313 | 0.066262 | -61.3358 | 60.2371 | -61.3861 | -61.3495 | 60.0906 | 0.24719 | 0.064087 | 0.14648 | 60.3195 | -61.4227 | -0.082397 | -0.073242 | -0.032043 | -0.045776 | -0.21973 | -0.11902 | 0.009155 | 0.050354 | 61.3678 | 61.4502 | 121.3943 | 121.5408 | -0.032043 | 121.6232 | 61.5509 | -0.11902 | 121.5408 | -0.032043 | 61.5509 | 121.3943 | 121.6232 | -121.6965 | -121.7331
1041.2344 | 121.9482 | -61.2717 | 60.3012 | 0.13771 | 0.014328 | -0.00037386 | 0.012117 | 0.052677 | -0.010322 | 0.069039 | -61.4365 | 60.1913 | -61.4136 | -61.4639 | 59.9899 | 0.045776 | -0.12817 | -0.091553 | 60.3104 | -61.4777 | -0.14191 | -0.10986 | -0.16479 | -0.19226 | -0.31128 | -0.20599 | 0.009156 | -0.022888 | 61.1435 | 61.1801 | 121.2616 | 121.463 | -0.16479 | 121.582 | 61.3174 | -0.20599 | 121.463 | -0.16479 | 61.3174 | 121.2616 | 121.582 | -121.7148 | -121.7789
1042.9844 | 121.9574 | -61.1893 | 60.3973 | -0.022507 | 0.012832 | -0.0016557 | 0.0029308 | 0.052037 | -0.0079724 | 0.065834 | -61.3266 | 60.26 | -61.3266 | -61.322 | 60.1456 | 0.28381 | 0.013733 | 0.23804 | 60.3241 | -61.4136 | -0.13733 | -0.13733 | -0.13733 | -0.13275 | -0.25177 | -0.2243 | -0.073242 | 0 | 61.203 | 61.4273 | 121.3348 | 121.4493 | -0.13733 | 121.5134 | 61.4731 | -0.2243 | 121.4493 | -0.13733 | 61.4731 | 121.3348 | 121.5134 | -121.7239 | -121.8109
1044.6719 | 121.9574 | -61.2442 | 60.3195 | 0.10719 | 0.011123 | -0.0029373 | 0.012544 | 0.053105 | -0.012886 | 0.069252 | -61.409 | 60.2005 | -61.4365 | -61.4548 | 59.9945 | 0.059509 | -0.20142 | -0.10529 | 60.2875 | -61.4685 | -0.19226 | -0.11902 | -0.16479 | -0.21057 | -0.32501 | -0.2243 | -0.032043 | 0.027465 | 61.0428 | 61.1389 | 121.2387 | 121.4447 | -0.16479 | 121.5317 | 61.3037 | -0.2243 | 121.4447 | -0.16479 | 61.3037 | 121.2387 | 121.5317 | -121.756 | -121.788
1046.4062 | 121.9528 | -61.2534 | 60.3104 | 0.099564 | 0.012191 | -0.0057145 | 0.011689 | 0.053318 | -0.012031 | 0.067116 | -61.4365 | 60.1639 | -61.4227 | -61.4594 | 59.9991 | 0.050354 | -0.13275 | -0.09613 | 60.3287 | -61.4548 | -0.16937 | -0.14648 | -0.1831 | -0.20599 | -0.31128 | -0.20142 | 0.01831 | -0.013733 | 61.1206 | 61.1572 | 121.2524 | 121.4172 | -0.1831 | 121.582 | 61.3037 | -0.20142 | 121.4172 | -0.1831 | 61.3037 | 121.2524 | 121.582 | -121.7331 | -121.7651
1048.1562 | 121.9757 | -61.2122 | 60.3745 | 0.069046 | 0.011337 | 5.3338e-05 | 0.0042126 | 0.050755 | -0.010109 | 0.068184 | -61.3266 | 60.1959 | -61.3358 | -61.3632 | 60.1089 | 0.1831 | -0.10529 | 0.11444 | 60.3241 | -61.4227 | -0.1236 | -0.17853 | -0.11444 | -0.15106 | -0.2655 | -0.21057 | -0.050354 | 0.009155 | 61.1069 | 61.3266 | 121.3211 | 121.4081 | -0.11444 | 121.5363 | 61.3953 | -0.21057 | 121.4081 | -0.11444 | 61.3953 | 121.3211 | 121.5363 | -121.7102 | -121.7972
1049.8281 | 121.843 | -61.322 | 60.347 | -0.18272 | 0.011337 | 0.0024033 | 0.012544 | 0.052037 | -0.01075 | 0.06733 | -61.3403 | 60.2463 | -61.377 | -61.3678 | 60.0906 | 0.25635 | 0.082397 | 0.16479 | 60.3287 | -61.4365 | -0.054932 | -0.10071 | -0.018311 | -0.045777 | -0.25635 | -0.11444 | -0.018311 | 0.036621 | 61.4044 | 61.4868 | 121.4127 | 121.5683 | -0.018311 | 121.6507 | 61.5784 | -0.11444 | 121.5683 | -0.018311 | 61.5784 | 121.4127 | 121.6507 | -121.7239 | -121.7834
1051.5781 | 121.8567 | -61.3266 | 60.3424 | -0.083542 | 0.013687 | -0.0022965 | 0.010621 | 0.0546 | -0.012886 | 0.067757 | -61.3266 | 60.2005 | -61.4044 | -61.377 | 60.0632 | 0.18768 | -0.032043 | 0.073242 | 60.3424 | -61.4365 | -0.07782 | -0.14191 | 0 | -0.050354 | -0.27924 | -0.10986 | 0 | 0.07782 | 61.2946 | 61.3998 | 121.3898 | 121.5271 | 0 | 121.669 | 61.5143 | -0.10986 | 121.5271 | 0 | 61.5143 | 121.3898 | 121.669 | -121.7468 | -121.7789
1053.3281 | 121.8933 | -61.2534 | 60.3561 | -0.24376 | 0.012191 | -0.0014419 | 0.0069898 | 0.050968 | -0.0092542 | 0.066048 | -61.3312 | 60.3149 | -61.3037 | -61.3815 | 60.0998 | 0.27924 | 0.25635 | 0.21973 | 60.4248 | -61.3998 | -0.050354 | -0.041199 | -0.07782 | -0.12817 | -0.25635 | -0.14648 | 0.068665 | -0.027466 | 61.5097 | 61.4731 | 121.3531 | 121.5683 | -0.07782 | 121.6782 | 61.5326 | -0.14648 | 121.5683 | -0.07782 | 61.5326 | 121.3531 | 121.6782 | -121.6599 | -121.756
1055.0625 | 121.8384 | -61.2991 | 60.3424 | -0.15221 | 0.014541 | -0.0014419 | 0.0097668 | 0.051823 | -0.012031 | 0.065193 | -61.3495 | 60.2188 | -61.3632 | -61.3724 | 60.0998 | 0.2655 | 0.091553 | 0.15106 | 60.3516 | -61.4044 | -0.064087 | -0.1236 | -0.050354 | -0.073242 | -0.24262 | -0.10529 | 0.009155 | 0.013733 | 61.3907 | 61.4502 | 121.3989 | 121.5179 | -0.050354 | 121.6507 | 61.5646 | -0.10529 | 121.5179 | -0.050354 | 61.5646 | 121.3989 | 121.6507 | -121.7056 | -121.7468
1056.75 | 121.8933 | -61.29 | 60.3882 | -0.21324 | 0.0139 | -0.0029373 | 0.005708 | 0.050328 | -0.012031 | 0.066689 | -61.3266 | 60.2966 | -61.3174 | -61.3449 | 60.1227 | 0.30212 | 0.22888 | 0.25635 | 60.4019 | -61.4319 | -0.027466 | -0.091553 | -0.036621 | -0.054932 | -0.2655 | -0.14191 | 0.013733 | -0.009155 | 61.5189 | 61.5463 | 121.4127 | 121.5866 | -0.036621 | 121.6919 | 61.5921 | -0.14191 | 121.5866 | -0.036621 | 61.5921 | 121.4127 | 121.6919 | -121.7056 | -121.8201
1058.4844 | 121.9803 | -61.2946 | 60.2692 | 0.13771 | 0.011551 | -0.0016557 | 0.010621 | 0.053105 | -0.01075 | 0.068611 | -61.4456 | 60.1593 | -61.4548 | -61.5143 | 59.9762 | 0.036621 | -0.15564 | -0.1236 | 60.3058 | -61.4777 | -0.16022 | -0.10986 | -0.15106 | -0.21973 | -0.29297 | -0.1831 | 0.036621 | 0.009155 | 61.1389 | 61.171 | 121.2708 | 121.4539 | -0.15106 | 121.6003 | 61.3312 | -0.1831 | 121.4539 | -0.15106 | 61.3312 | 121.2708 | 121.6003 | -121.7239 | -121.7468
1060.2344 | 121.8338 | -61.2534 | 60.4294 | -0.16747 | 0.012191 | -0.0018693 | 0.0067762 | 0.049473 | -0.0092542 | 0.06797 | -61.2396 | 60.2417 | -61.2808 | -61.2625 | 60.2097 | 0.3891 | 0.09613 | 0.36163 | 60.3607 | -61.3998 | -0.027466 | -0.18768 | 0.013733 | -0.009155 | -0.21973 | -0.14648 | -0.068664 | 0.041199 | 61.3495 | 61.615 | 121.463 | 121.4951 | 0.013733 | 121.6141 | 61.6425 | -0.14648 | 121.4951 | 0.013733 | 61.6425 | 121.463 | 121.6141 | -121.7102 | -121.8292
1061.9844 | 121.8384 | -61.3083 | 60.347 | -0.045395 | 0.011337 | -0.0012283 | 0.011476 | 0.054386 | -0.010322 | 0.067543 | -61.3541 | 60.1868 | -61.4136 | -61.377 | 60.0723 | 0.19226 | -0.032043 | 0.086975 | 60.347 | -61.4594 | -0.10528 | -0.16022 | -0.045776 | -0.068664 | -0.27466 | -0.15106 | 0 | 0.059509 | 61.2762 | 61.3953 | 121.3806 | 121.4951 | -0.045776 | 121.6553 | 61.5006 | -0.15106 | 121.4951 | -0.045776 | 61.5006 | 121.3806 | 121.6553 | -121.7606 | -121.8063
1063.7344 | 121.9757 | -61.1755 | 60.3882 | 0.0080111 | 0.011764 | -0.00080106 | 0.0035718 | 0.051609 | -0.0069042 | 0.065834 | -61.322 | 60.2371 | -61.3037 | -61.3632 | 60.1273 | 0.23804 | -0.009155 | 0.18768 | 60.347 | -61.409 | -0.12817 | -0.15106 | -0.14648 | -0.18768 | -0.26093 | -0.23346 | -0.041199 | -0.01831 | 61.1664 | 61.3632 | 121.3028 | 121.4127 | -0.14648 | 121.5225 | 61.4136 | -0.23346 | 121.4127 | -0.14648 | 61.4136 | 121.3028 | 121.5225 | -121.6919 | -121.7972
1065.4219 | 121.8933 | -61.2396 | 60.3882 | -0.21324 | 0.010482 | -0.0029373 | 0.0082714 | 0.050541 | -0.01139 | 0.06797 | -61.3266 | 60.2646 | -61.322 | -61.3495 | 60.1181 | 0.29755 | 0.23346 | 0.24719 | 60.3928 | -61.3861 | -0.082397 | -0.1236 | -0.086975 | -0.10986 | -0.27008 | -0.14648 | 0.004577 | -0.004578 | 61.4731 | 61.4868 | 121.3577 | 121.5042 | -0.086975 | 121.6324 | 61.5372 | -0.14648 | 121.5042 | -0.086975 | 61.5372 | 121.3577 | 121.6324 | -121.7102 | -121.7743
1067.1719 | 121.9757 | -61.1938 | 60.3928 | 0.13008 | 0.012405 | 0.00026694 | 0.0061352 | 0.051182 | -0.010322 | 0.066475 | -61.3174 | 60.1685 | -61.3312 | -61.3541 | 60.1227 | 0.20142 | -0.13275 | 0.11902 | 60.3241 | -61.409 | -0.13733 | -0.2243 | -0.1236 | -0.16022 | -0.27008 | -0.21515 | -0.068664 | 0.013733 | 61.0611 | 61.3129 | 121.3165 | 121.3623 | -0.1236 | 121.5179 | 61.3953 | -0.21515 | 121.3623 | -0.1236 | 61.3953 | 121.3165 | 121.5179 | -121.7239 | -121.8018
1068.8594 | 121.843 | -61.2167 | 60.434 | -0.15984 | 0.012619 | -0.00037386 | 0.0080578 | 0.051396 | -0.01139 | 0.064553 | -61.2076 | 60.2417 | -61.2854 | -61.235 | 60.2325 | 0.39368 | 0.073242 | 0.37994 | 60.3973 | -61.3495 | -0.068664 | -0.19226 | 0.009155 | -0.01831 | -0.20142 | -0.13275 | -0.036621 | 0.077819 | 61.29 | 61.5967 | 121.4493 | 121.4584 | 0.009155 | 121.6141 | 61.6104 | -0.13275 | 121.4584 | 0.009155 | 61.6104 | 121.4493 | 121.6141 | -121.7194 | -121.7834
1070.6094 | 121.9299 | -61.2579 | 60.3058 | 0.14534 | 0.014541 | -0.0046463 | 0.013185 | 0.052891 | -0.012031 | 0.066689 | -61.3998 | 60.173 | -61.4365 | -61.441 | 60.0174 | 0.07782 | -0.23804 | -0.073242 | 60.2921 | -61.4731 | -0.17853 | -0.13275 | -0.14191 | -0.1831 | -0.28839 | -0.21515 | -0.013733 | 0.036621 | 61.0199 | 61.1847 | 121.2753 | 121.431 | -0.14191 | 121.55 | 61.3358 | -0.21515 | 121.431 | -0.14191 | 61.3358 | 121.2753 | 121.55 | -121.7422 | -121.7789
1072.3594 | 121.9803 | -61.1755 | 60.4248 | -0.014877 | 0.015823 | -0.0063553 | 0.0063488 | 0.050114 | -0.0077588 | 0.067116 | -61.3266 | 60.2417 | -61.3312 | -61.3541 | 60.1181 | 0.21973 | -0.009155 | 0.18768 | 60.3424 | -61.4182 | -0.15564 | -0.18311 | -0.15106 | -0.17853 | -0.3067 | -0.24262 | -0.082398 | 0.004578 | 61.1664 | 61.3632 | 121.2936 | 121.4172 | -0.15106 | 121.5179 | 61.3953 | -0.24262 | 121.4172 | -0.15106 | 61.3953 | 121.2936 | 121.5179 | -121.756 | -121.843
1074.0469 | 121.9345 | -61.1618 | 60.4294 | -0.075912 | 0.011123 | -0.0044327 | 0.009126 | 0.051396 | -0.0086132 | 0.068184 | -61.2717 | 60.2554 | -61.2808 | -61.2625 | 60.2097 | 0.35248 | 0.041199 | 0.32044 | 60.3882 | -61.3815 | -0.11902 | -0.17395 | -0.10986 | -0.10071 | -0.21973 | -0.21973 | -0.041198 | 0.009156 | 61.203 | 61.4822 | 121.3715 | 121.4172 | -0.10986 | 121.55 | 61.5143 | -0.21973 | 121.4172 | -0.10986 | 61.5143 | 121.3715 | 121.55 | -121.7102 | -121.8109
1075.8125 | 121.9299 | -61.2625 | 60.3104 | 0.069046 | 0.013473 | 0.0041123 | 0.013612 | 0.050755 | -0.012886 | 0.067757 | -61.4227 | 60.1868 | -61.4639 | -61.4548 | 59.9625 | 0.068665 | -0.068665 | -0.07782 | 60.3424 | -61.4914 | -0.20142 | -0.1236 | -0.16022 | -0.19226 | -0.3479 | -0.22888 | 0.032043 | 0.041199 | 61.1938 | 61.1847 | 121.225 | 121.4493 | -0.16022 | 121.6049 | 61.3312 | -0.22888 | 121.4493 | -0.16022 | 61.3312 | 121.225 | 121.6049 | -121.7743 | -121.8018
1077.5469 | 121.962 | -61.2671 | 60.2921 | 0.091934 | 0.014328 | 0.0024033 | 0.012544 | 0.054173 | -0.011818 | 0.069039 | -61.4639 | 60.1547 | -61.4365 | -61.4777 | 59.9808 | 0.045776 | -0.13275 | -0.12817 | 60.3104 | -61.4914 | -0.16937 | -0.13733 | -0.19684 | -0.21057 | -0.31128 | -0.2243 | 0.018311 | -0.027466 | 61.1343 | 61.1389 | 121.2479 | 121.4218 | -0.19684 | 121.5775 | 61.3129 | -0.2243 | 121.4218 | -0.19684 | 61.3129 | 121.2479 | 121.5775 | -121.7285 | -121.7834
1079.2969 | 121.8567 | -61.322 | 60.3424 | -0.060654 | 0.012191 | -0.0057145 | 0.011903 | 0.05225 | -0.010963 | 0.06797 | -61.3449 | 60.2188 | -61.3998 | -61.3632 | 60.0815 | 0.19684 | -0.041199 | 0.064087 | 60.3699 | -61.4365 | -0.07782 | -0.1236 | -0.022889 | -0.041199 | -0.26093 | -0.11444 | 0.027466 | 0.054931 | 61.2808 | 61.3861 | 121.4035 | 121.5408 | -0.022889 | 121.6919 | 61.5189 | -0.11444 | 121.5408 | -0.022889 | 61.5189 | 121.4035 | 121.6919 | -121.7422 | -121.7789
1080.9844 | 121.8842 | -61.2717 | 60.3516 | -0.2285 | 0.012619 | -0.0042191 | 0.0089124 | 0.051609 | -0.0096814 | 0.066475 | -61.3586 | 60.2966 | -61.322 | -61.3632 | 60.1044 | 0.28381 | 0.22888 | 0.19684 | 60.4248 | -61.3907 | -0.050354 | -0.054931 | -0.086976 | -0.091553 | -0.24719 | -0.11902 | 0.073243 | -0.036622 | 61.5005 | 61.4685 | 121.376 | 121.5683 | -0.086976 | 121.6965 | 61.5555 | -0.11902 | 121.5683 | -0.086976 | 61.5555 | 121.376 | 121.6965 | -121.6736 | -121.7422
1082.7344 | 121.9254 | -61.2625 | 60.3699 | 0.16823 | 0.013046 | -0.0010147 | 0.0089124 | 0.050968 | -0.012031 | 0.067116 | -61.3083 | 60.1135 | -61.3998 | -61.377 | 60.1135 | 0.15564 | -0.31128 | 0.036621 | 60.2509 | -61.4548 | -0.13733 | -0.25635 | -0.045777 | -0.11444 | -0.25635 | -0.19226 | -0.11902 | 0.091552 | 60.9512 | 61.2991 | 121.376 | 121.376 | -0.045777 | 121.5134 | 61.4182 | -0.19226 | 121.376 | -0.045777 | 61.4182 | 121.376 | 121.5134 | -121.7697 | -121.8246
1084.4688 | 121.9894 | -61.171 | 60.3973 | 0.01564 | 0.01091 | -0.0059281 | 0.0050672 | 0.048405 | -0.0069042 | 0.066689 | -61.322 | 60.2234 | -61.2946 | -61.3495 | 60.1227 | 0.21973 | -0.018311 | 0.16022 | 60.3424 | -61.4136 | -0.1236 | -0.17395 | -0.15106 | -0.17853 | -0.27466 | -0.24261 | -0.054932 | -0.027465 | 61.1526 | 61.3312 | 121.2936 | 121.3943 | -0.15106 | 121.5134 | 61.3907 | -0.24261 | 121.3943 | -0.15106 | 61.3907 | 121.2936 | 121.5134 | -121.6919 | -121.8109
1086.2188 | 121.9666 | -61.2671 | 60.3012 | 0.099564 | 0.014755 | 0.0038985 | 0.012758 | 0.052464 | -0.01139 | 0.066902 | -61.4319 | 60.1868 | -61.4502 | -61.4594 | 59.9899 | 0.050354 | -0.14191 | -0.09613 | 60.3104 | -61.4639 | -0.1831 | -0.11444 | -0.16479 | -0.19226 | -0.31128 | -0.19684 | 0.009156 | 0.01831 | 61.1252 | 61.171 | 121.257 | 121.4539 | -0.16479 | 121.5775 | 61.3174 | -0.19684 | 121.4539 | -0.16479 | 61.3174 | 121.257 | 121.5775 | -121.7514 | -121.7651
1087.9062 | 121.8292 | -61.322 | 60.347 | -0.10643 | 0.011764 | 0.0047531 | 0.013398 | 0.05225 | -0.011818 | 0.067757 | -61.3312 | 60.2188 | -61.3632 | -61.3586 | 60.0998 | 0.23346 | 0.013733 | 0.13275 | 60.3333 | -61.4456 | -0.041199 | -0.12817 | -0.009156 | -0.036622 | -0.24719 | -0.1236 | -0.013733 | 0.032043 | 61.3358 | 61.4548 | 121.4218 | 121.5408 | -0.009156 | 121.6553 | 61.5555 | -0.1236 | 121.5408 | -0.009156 | 61.5555 | 121.4218 | 121.6553 | -121.7102 | -121.7926
1089.6562 | 121.9666 | -61.29 | 60.3058 | 0.099564 | 0.014755 | 0.0028305 | 0.011049 | 0.051823 | -0.0094678 | 0.067543 | -61.4639 | 60.1776 | -61.4273 | -61.496 | 59.9762 | 0.045776 | -0.11902 | -0.12817 | 60.3241 | -61.496 | -0.13733 | -0.12817 | -0.17395 | -0.20599 | -0.32959 | -0.20599 | 0.018311 | -0.036621 | 61.171 | 61.1618 | 121.2662 | 121.4676 | -0.17395 | 121.6141 | 61.3358 | -0.20599 | 121.4676 | -0.17395 | 61.3358 | 121.2662 | 121.6141 | -121.7331 | -121.8018
1091.4219 | 121.8704 | -61.2991 | 60.3424 | -0.030136 | 0.012832 | -0.0029373 | 0.011262 | 0.053105 | -0.012672 | 0.068611 | -61.3907 | 60.2097 | -61.3998 | -61.4365 | 60.0357 | 0.13275 | -0.073242 | -0.018311 | 60.3287 | -61.4639 | -0.10071 | -0.13275 | -0.091553 | -0.13733 | -0.3067 | -0.1648 | -0.013733 | 0.009155 | 61.2259 | 61.2808 | 121.3348 | 121.5088 | -0.091553 | 121.6278 | 61.4319 | -0.1648 | 121.5088 | -0.091553 | 61.4319 | 121.3348 | 121.6278 | -121.7422 | -121.8063
1093.1875 | 121.8567 | -61.3129 | 60.3378 | -0.16747 | 0.0139 | -0.0010147 | 0.008485 | 0.052677 | -0.011177 | 0.065834 | -61.3449 | 60.26 | -61.3632 | -61.3815 | 60.0952 | 0.26093 | 0.13733 | 0.17853 | 60.3836 | -61.4136 | -0.050354 | -0.07782 | -0.032044 | -0.068665 | -0.24261 | -0.10071 | 0.045776 | 0.01831 | 61.4502 | 61.4914 | 121.4081 | 121.5729 | -0.032044 | 121.6965 | 61.5738 | -0.10071 | 121.5729 | -0.032044 | 61.5738 | 121.4081 | 121.6965 | -121.701 | -121.7514
1094.875 | 121.9666 | -61.1801 | 60.4202 | 0.091934 | 0.011978 | 0.00026694 | 0.0059216 | 0.050541 | -0.0060498 | 0.067543 | -61.3174 | 60.2142 | -61.322 | -61.3632 | 60.1181 | 0.18768 | -0.11444 | 0.11444 | 60.3424 | -61.4227 | -0.14191 | -0.20599 | -0.13733 | -0.1831 | -0.30212 | -0.24261 | -0.07782 | 0.004577 | 61.0657 | 61.2946 | 121.2982 | 121.3943 | -0.13733 | 121.5225 | 61.3678 | -0.24261 | 121.3943 | -0.13733 | 61.3678 | 121.2982 | 121.5225 | -121.7422 | -121.843
1096.625 | 121.9345 | -61.235 | 60.379 | 0.15297 | 0.010055 | 0.0021895 | 0.0093396 | 0.051182 | -0.0077588 | 0.069466 | -61.3174 | 60.1822 | -61.3815 | -61.3449 | 60.1181 | 0.17395 | -0.27466 | 0.068665 | 60.2875 | -61.4365 | -0.14649 | -0.19684 | -0.082398 | -0.10986 | -0.26093 | -0.20142 | -0.091552 | 0.064087 | 60.9604 | 61.3037 | 121.3531 | 121.4172 | -0.082398 | 121.5225 | 61.409 | -0.20142 | 121.4172 | -0.082398 | 61.409 | 121.3531 | 121.5225 | -121.7606 | -121.8155
1098.3281 | 121.907 | -61.2213 | 60.3836 | 0.16823 | 0.011551 | 0.00069434 | 0.0086988 | 0.052037 | -0.0094678 | 0.069252 | -61.3174 | 60.1776 | -61.3861 | -61.377 | 60.1135 | 0.17853 | -0.28839 | 0.068665 | 60.2509 | -61.4822 | -0.16479 | -0.20599 | -0.096131 | -0.15564 | -0.27008 | -0.26093 | -0.13275 | 0.068664 | 60.9329 | 61.29 | 121.3348 | 121.3989 | -0.096131 | 121.4722 | 61.3998 | -0.26093 | 121.3989 | -0.096131 | 61.3998 | 121.3348 | 121.4722 | -121.7697 | -121.8658
1100.0781 | 121.8567 | -61.322 | 60.3241 | -0.075912 | 0.01326 | -0.0014419 | 0.01233 | 0.051182 | -0.012031 | 0.06733 | -61.3495 | 60.1959 | -61.4044 | -61.3724 | 60.0815 | 0.18768 | -0.036621 | 0.064087 | 60.3424 | -61.4502 | -0.082398 | -0.12817 | -0.027466 | -0.050354 | -0.24262 | -0.12817 | 0.01831 | 0.054932 | 61.2854 | 61.3861 | 121.4035 | 121.5179 | -0.027466 | 121.6644 | 61.5097 | -0.12817 | 121.5179 | -0.027466 | 61.5097 | 121.4035 | 121.6644 | -121.7285 | -121.7743
1101.8281 | 121.9391 | -61.2167 | 60.379 | 0.10719 | 0.011337 | -0.0031509 | 0.007417 | 0.051823 | -0.012031 | 0.066902 | -61.3129 | 60.1639 | -61.3632 | -61.3495 | 60.1273 | 0.16022 | -0.2243 | 0.07782 | 60.3104 | -61.4319 | -0.14648 | -0.21515 | -0.09613 | -0.13275 | -0.25177 | -0.21515 | -0.068664 | 0.050354 | 60.9924 | 61.2946 | 121.344 | 121.3806 | -0.09613 | 121.5271 | 61.377 | -0.21515 | 121.3806 | -0.09613 | 61.377 | 121.344 | 121.5271 | -121.7422 | -121.8109
1103.5781 | 121.9711 | -61.2946 | 60.2829 | 0.13008 | 0.013687 | -0.0018693 | 0.010835 | 0.052677 | -0.011177 | 0.06797 | -61.4594 | 60.173 | -61.4502 | -61.4777 | 59.9762 | 0.036621 | -0.13275 | -0.10986 | 60.3333 | -61.4731 | -0.15564 | -0.10986 | -0.16479 | -0.1831 | -0.3067 | -0.17853 | 0.050354 | -0.009156 | 61.1618 | 61.1847 | 121.2708 | 121.4676 | -0.16479 | 121.6278 | 61.3312 | -0.17853 | 121.4676 | -0.16479 | 61.3312 | 121.2708 | 121.6278 | -121.7331 | -121.756
1105.3281 | 121.962 | -61.203 | 60.4065 | -0.022507 | 0.013473 | -0.0037919 | 0.0048534 | 0.048405 | -0.0075452 | 0.065407 | -61.3266 | 60.2509 | -61.3174 | -61.3541 | 60.1318 | 0.24261 | -0.027466 | 0.19684 | 60.3378 | -61.4182 | -0.11444 | -0.15564 | -0.1236 | -0.15106 | -0.27466 | -0.21515 | -0.068664 | -0.009155 | 61.1755 | 61.3998 | 121.3348 | 121.4539 | -0.1236 | 121.5408 | 61.4456 | -0.21515 | 121.4539 | -0.1236 | 61.4456 | 121.3348 | 121.5408 | -121.7239 | -121.8246
1107.0156 | 121.9437 | -61.2305 | 60.3516 | 0.14534 | 0.0139 | 0.0011215 | 0.0080578 | 0.049687 | -0.012031 | 0.066262 | -61.3266 | 60.1639 | -61.3953 | -61.3449 | 60.1318 | 0.18768 | -0.22888 | 0.091553 | 60.2921 | -61.4273 | -0.16479 | -0.18768 | -0.09613 | -0.11444 | -0.21973 | -0.19684 | -0.059509 | 0.068665 | 61.0016 | 61.322 | 121.3623 | 121.3943 | -0.09613 | 121.5225 | 61.4182 | -0.19684 | 121.3943 | -0.09613 | 61.4182 | 121.3623 | 121.5225 | -121.7468 | -121.7789
1108.7656 | 122.0032 | -61.1664 | 60.4065 | 0.030899 | 0.011551 | -0.0018693 | 0.0059216 | 0.052891 | -0.010322 | 0.067543 | -61.3083 | 60.2371 | -61.3312 | -61.3449 | 60.1227 | 0.21057 | -0.041199 | 0.15564 | 60.3424 | -61.4044 | -0.16479 | -0.16937 | -0.14191 | -0.17853 | -0.28381 | -0.23804 | -0.064087 | 0.022888 | 61.1252 | 61.322 | 121.2891 | 121.4035 | -0.14191 | 121.5088 | 61.377 | -0.23804 | 121.4035 | -0.14191 | 61.377 | 121.2891 | 121.5088 | -121.7377 | -121.8109
1110.5 | 121.9437 | -61.1847 | 60.4019 | -0.053024 | 0.010482 | -0.00037386 | 0.0067762 | 0.050968 | -0.0092542 | 0.064553 | -61.29 | 60.2325 | -61.322 | -61.3083 | 60.1685 | 0.3067 | 0.022888 | 0.2655 | 60.3699 | -61.4044 | -0.13733 | -0.16937 | -0.10529 | -0.1236 | -0.23346 | -0.21973 | -0.032044 | 0.032043 | 61.2076 | 61.4502 | 121.3531 | 121.4172 | -0.10529 | 121.5546 | 61.4914 | -0.21973 | 121.4172 | -0.10529 | 61.4914 | 121.3531 | 121.5546 | -121.7239 | -121.8063
1112.1875 | 121.9574 | -61.2762 | 60.2875 | 0.099564 | 0.012832 | -0.0018693 | 0.015535 | 0.050755 | -0.011604 | 0.068611 | -61.441 | 60.1593 | -61.4594 | -61.4639 | 59.9945 | 0.027466 | -0.15106 | -0.10986 | 60.347 | -61.496 | -0.18311 | -0.12817 | -0.16479 | -0.18768 | -0.29297 | -0.21973 | 0.059509 | 0.018311 | 61.1252 | 61.1664 | 121.2708 | 121.4355 | -0.16479 | 121.6232 | 61.3037 | -0.21973 | 121.4355 | -0.16479 | 61.3037 | 121.2708 | 121.6232 | -121.7468 | -121.7834
1113.9531 | 121.8979 | -61.2717 | 60.3378 | -0.19798 | 0.011764 | 5.3338e-05 | 0.0095532 | 0.050328 | -0.010536 | 0.068398 | -61.3449 | 60.2692 | -61.3678 | -61.3724 | 60.0906 | 0.27008 | 0.20142 | 0.18768 | 60.3882 | -61.4227 | -0.096131 | -0.068665 | -0.073243 | -0.10071 | -0.24719 | -0.15106 | 0.050354 | 0.022888 | 61.4731 | 61.4594 | 121.3623 | 121.5408 | -0.073243 | 121.6599 | 61.5417 | -0.15106 | 121.5408 | -0.073243 | 61.5417 | 121.3623 | 121.6599 | -121.7056 | -121.7606
1115.7031 | 121.8384 | -61.3403 | 60.3333 | -0.053024 | 0.0139 | 0.0013351 | 0.014894 | 0.051823 | -0.0090406 | 0.068398 | -61.3266 | 60.2554 | -61.3541 | -61.3861 | 60.0815 | 0.19684 | -0.032043 | 0.073242 | 60.3378 | -61.496 | -0.013733 | -0.07782 | 0.013733 | -0.045776 | -0.25177 | -0.15564 | 0.004578 | 0.027466 | 61.3083 | 61.4136 | 121.4218 | 121.5958 | 0.013733 | 121.6782 | 61.5372 | -0.15564 | 121.5958 | 0.013733 | 61.5372 | 121.4218 | 121.6782 | -121.6873 | -121.8292
1117.3906 | 121.9528 | -61.1938 | 60.3882 | 0.11482 | 0.011551 | 0.00048074 | 0.0052808 | 0.051182 | -0.010109 | 0.069039 | -61.3312 | 60.1959 | -61.3266 | -61.3586 | 60.1181 | 0.1831 | -0.15564 | 0.091553 | 60.3241 | -61.3861 | -0.13275 | -0.19226 | -0.13733 | -0.16479 | -0.27008 | -0.19226 | -0.064087 | -0.004578 | 61.0382 | 61.2854 | 121.312 | 121.3898 | -0.13733 | 121.5179 | 61.377 | -0.19226 | 121.3898 | -0.13733 | 61.377 | 121.312 | 121.5179 | -121.7148 | -121.7743
1119.1719 | 121.8613 | -61.3129 | 60.3241 | -0.022507 | 0.0139 | 0.00090794 | 0.015107 | 0.055882 | -0.011177 | 0.06797 | -61.3815 | 60.2097 | -61.3998 | -61.4319 | 60.0174 | 0.1236 | -0.073242 | -0.036621 | 60.3516 | -61.4639 | -0.086975 | -0.11444 | -0.068665 | -0.11902 | -0.3067 | -0.15106 | 0.027465 | 0.01831 | 61.2396 | 61.2762 | 121.3303 | 121.5225 | -0.068665 | 121.6644 | 61.4365 | -0.15106 | 121.5225 | -0.068665 | 61.4365 | 121.3303 | 121.6644 | -121.7239 | -121.788
1120.8594 | 121.843 | -61.3266 | 60.3378 | -0.060654 | 0.015609 | -0.00080106 | 0.011689 | 0.051823 | -0.011818 | 0.068398 | -61.3266 | 60.2051 | -61.3907 | -61.3678 | 60.0861 | 0.19226 | -0.036621 | 0.068665 | 60.3653 | -61.4456 | -0.064087 | -0.13275 | 0 | -0.041199 | -0.25177 | -0.11902 | 0.027465 | 0.064087 | 61.29 | 61.3953 | 121.4127 | 121.5317 | 0 | 121.6919 | 61.5189 | -0.11902 | 121.5317 | 0 | 61.5189 | 121.4127 | 121.6919 | -121.7285 | -121.7834
1122.5938 | 121.8338 | -61.3174 | 60.347 | -0.17509 | 0.014328 | -0.0018693 | 0.0099804 | 0.053959 | -0.010963 | 0.068825 | -61.3358 | 60.2463 | -61.3495 | -61.377 | 60.1089 | 0.27008 | 0.07782 | 0.15106 | 60.3882 | -61.4548 | -0.032043 | -0.10071 | -0.01831 | -0.059509 | -0.23804 | -0.13733 | 0.041199 | 0.013733 | 61.3953 | 61.4685 | 121.4264 | 121.5637 | -0.01831 | 121.7056 | 61.5875 | -0.13733 | 121.5637 | -0.01831 | 61.5875 | 121.4264 | 121.7056 | -121.6965 | -121.8018
1124.3438 | 121.9208 | -61.1847 | 60.3973 | -0.091171 | 0.011764 | 0.00069434 | 0.0037854 | 0.050541 | -0.010109 | 0.069252 | -61.2854 | 60.2463 | -61.2854 | -61.29 | 60.2142 | 0.34332 | 0.036621 | 0.31128 | 60.3882 | -61.3495 | -0.10071 | -0.15106 | -0.10071 | -0.10529 | -0.18311 | -0.1648 | -0.009155 | 0 | 61.2213 | 61.496 | 121.3989 | 121.431 | -0.10071 | 121.5729 | 61.528 | -0.1648 | 121.431 | -0.10071 | 61.528 | 121.3989 | 121.5729 | -121.6827 | -121.7468
1126.0938 | 121.8613 | -61.3358 | 60.3012 | 0.01564 | 0.014328 | 5.3338e-05 | 0.013398 | 0.051396 | -0.010963 | 0.06733 | -61.3998 | 60.1959 | -61.4182 | -61.4456 | 59.9991 | 0.09613 | -0.082397 | -0.059509 | 60.3195 | -61.4594 | -0.082398 | -0.10529 | -0.064087 | -0.10986 | -0.30212 | -0.1236 | 0.018311 | 0.018311 | 61.2534 | 61.2762 | 121.3348 | 121.5317 | -0.064087 | 121.6553 | 61.4319 | -0.1236 | 121.5317 | -0.064087 | 61.4319 | 121.3348 | 121.6553 | -121.7194 | -121.7606
1127.7812 | 121.8475 | -61.2167 | 60.4294 | -0.13695 | 0.0089872 | -0.0022965 | 0.0042126 | 0.052464 | -0.012031 | 0.065834 | -61.2122 | 60.26 | -61.2717 | -61.2396 | 60.2417 | 0.39825 | 0.068665 | 0.40283 | 60.3745 | -61.3541 | -0.054931 | -0.16937 | 0.004578 | -0.022888 | -0.18768 | -0.13733 | -0.054931 | 0.059509 | 61.2854 | 61.6196 | 121.4584 | 121.4767 | 0.004578 | 121.5912 | 61.615 | -0.13733 | 121.4767 | 0.004578 | 61.615 | 121.4584 | 121.5912 | -121.701 | -121.7834
1129.5469 | 121.8201 | -61.3449 | 60.3378 | -0.091171 | 0.011978 | -0.0016557 | 0.013398 | 0.051823 | -0.012458 | 0.067116 | -61.3449 | 60.2417 | -61.3953 | -61.3724 | 60.0861 | 0.22888 | -0.013733 | 0.11444 | 60.3561 | -61.4273 | -0.050354 | -0.096131 | 0 | -0.027465 | -0.25177 | -0.082397 | 0.01831 | 0.050354 | 61.3312 | 61.4594 | 121.431 | 121.5866 | 0 | 121.7011 | 61.5738 | -0.082397 | 121.5866 | 0 | 61.5738 | 121.431 | 121.7011 | -121.7331 | -121.7651
1131.2344 | 121.8658 | -61.2625 | 60.4248 | -0.18272 | 0.012619 | -0.0018693 | 0.0061352 | 0.050541 | -0.010322 | 0.065193 | -61.2717 | 60.2325 | -61.2762 | -61.2808 | 60.2142 | 0.39368 | 0.1831 | 0.37079 | 60.4294 | -61.3449 | -0.013733 | -0.19226 | -0.009155 | -0.018311 | -0.21057 | -0.082398 | 0.004577 | 0.004578 | 61.4456 | 61.6333 | 121.4767 | 121.4951 | -0.009155 | 121.6919 | 61.6562 | -0.082398 | 121.4951 | -0.009155 | 61.6562 | 121.4767 | 121.6919 | -121.7011 | -121.7697
1133 | 121.8887 | -61.2579 | 60.3699 | -0.19035 | 0.012619 | -0.0012283 | 0.0072034 | 0.050968 | -0.010536 | 0.06733 | -61.3358 | 60.2554 | -61.3266 | -61.3495 | 60.1181 | 0.29297 | 0.24719 | 0.24719 | 60.4156 | -61.3678 | -0.068664 | -0.11444 | -0.077819 | -0.091552 | -0.25177 | -0.10986 | 0.045776 | -0.009155 | 61.5051 | 61.5051 | 121.376 | 121.5134 | -0.077819 | 121.6736 | 61.5509 | -0.10986 | 121.5134 | -0.077819 | 61.5509 | 121.376 | 121.6736 | -121.6965 | -121.7377
1134.75 | 121.8842 | -61.2854 | 60.3607 | -0.19035 | 0.0139 | 0.0021895 | 0.01233 | 0.051396 | -0.012031 | 0.068825 | -61.3312 | 60.2966 | -61.3403 | -61.3586 | 60.1044 | 0.28381 | 0.18768 | 0.17395 | 60.4156 | -61.409 | -0.054932 | -0.064087 | -0.045777 | -0.073243 | -0.25635 | -0.1236 | 0.054931 | 0.009155 | 61.4731 | 61.4594 | 121.3898 | 121.582 | -0.045777 | 121.701 | 61.5692 | -0.1236 | 121.582 | -0.045777 | 61.5692 | 121.3898 | 121.701 | -121.701 | -121.7697
1136.4531 | 121.8887 | -61.2762 | 60.4294 | -0.26665 | 0.012619 | 0.00048074 | 0.0063488 | 0.050968 | -0.0090406 | 0.06733 | -61.2717 | 60.2737 | -61.3037 | -61.2991 | 60.1593 | 0.36163 | 0.20599 | 0.32044 | 60.4065 | -61.3815 | -0.027466 | -0.15564 | 0.004578 | -0.022888 | -0.27008 | -0.10529 | -0.022888 | 0.032044 | 61.4822 | 61.5967 | 121.4355 | 121.55 | 0.004578 | 121.6827 | 61.6379 | -0.10529 | 121.55 | 0.004578 | 61.6379 | 121.4355 | 121.6827 | -121.7331 | -121.8109
1138.2031 | 121.9299 | -61.2305 | 60.3241 | 0.19112 | 0.015609 | 0.0013351 | 0.011476 | 0.053959 | -0.013527 | 0.068611 | -61.3953 | 60.173 | -61.4227 | -61.4182 | 60.0494 | 0.09613 | -0.23346 | -0.050354 | 60.3241 | -61.441 | -0.19226 | -0.15106 | -0.16479 | -0.18768 | -0.27466 | -0.21057 | 0 | 0.027465 | 60.997 | 61.1801 | 121.2799 | 121.4035 | -0.16479 | 121.5546 | 61.3266 | -0.21057 | 121.4035 | -0.16479 | 61.3266 | 121.2799 | 121.5546 | -121.7468 | -121.7651
1139.8906 | 121.9254 | -61.2122 | 60.3516 | 0.15297 | 0.013046 | -0.0050735 | 0.0093396 | 0.053959 | -0.011177 | 0.06733 | -61.3495 | 60.173 | -61.3815 | -61.377 | 60.0815 | 0.14648 | -0.28381 | 0.022888 | 60.2921 | -61.4594 | -0.16937 | -0.17853 | -0.13733 | -0.16479 | -0.27008 | -0.24719 | -0.059509 | 0.032044 | 60.9283 | 61.235 | 121.2936 | 121.3852 | -0.13733 | 121.5042 | 61.3586 | -0.24719 | 121.3852 | -0.13733 | 61.3586 | 121.2936 | 121.5042 | -121.7331 | -121.8109
1141.6406 | 121.9711 | -61.2671 | 60.3012 | 0.11482 | 0.011123 | -0.0044327 | 0.011903 | 0.05225 | -0.01075 | 0.067116 | -61.4136 | 60.1913 | -61.4273 | -61.4594 | 59.9899 | 0.064087 | -0.15106 | -0.10529 | 60.347 | -61.4685 | -0.16022 | -0.10986 | -0.14648 | -0.19226 | -0.31128 | -0.20142 | 0.045777 | 0.013733 | 61.116 | 61.1618 | 121.257 | 121.4584 | -0.14648 | 121.6141 | 61.3312 | -0.20142 | 121.4584 | -0.14648 | 61.3312 | 121.257 | 121.6141 | -121.7285 | -121.7697
1143.3906 | 121.9711 | -61.2534 | 60.2829 | 0.084305 | 0.012191 | -0.0035783 | 0.010835 | 0.053746 | -0.009895 | 0.066262 | -61.4365 | 60.2142 | -61.4502 | -61.4914 | 59.9808 | 0.054932 | -0.1236 | -0.1236 | 60.3241 | -61.5143 | -0.19684 | -0.068665 | -0.1831 | -0.23804 | -0.30212 | -0.26093 | 0.041199 | 0.013733 | 61.1298 | 61.1298 | 121.2341 | 121.4676 | -0.1831 | 121.5775 | 61.3083 | -0.26093 | 121.4676 | -0.1831 | 61.3083 | 121.2341 | 121.5775 | -121.7331 | -121.7972
1145.1562 | 121.8933 | -61.3037 | 60.3745 | -0.25139 | 0.013046 | 0.00069434 | 0.008485 | 0.050114 | -0.009895 | 0.066689 | -61.3403 | 60.2875 | -61.322 | -61.3815 | 60.0998 | 0.28381 | 0.23346 | 0.20599 | 60.4065 | -61.3953 | -0.01831 | -0.086975 | -0.036621 | -0.07782 | -0.27466 | -0.091553 | 0.032043 | -0.018311 | 61.5372 | 61.5097 | 121.4035 | 121.5912 | -0.036621 | 121.7102 | 61.5875 | -0.091553 | 121.5912 | -0.036621 | 61.5875 | 121.4035 | 121.7102 | -121.6965 | -121.7697
1146.8438 | 121.8704 | -61.2076 | 60.4385 | -0.15221 | 0.012405 | -0.0029373 | 0.0042126 | 0.050328 | -0.0092542 | 0.068184 | -61.2305 | 60.2692 | -61.2442 | -61.2625 | 60.2692 | 0.39368 | 0.036621 | 0.37537 | 60.3836 | -61.3724 | -0.036621 | -0.16937 | -0.022888 | -0.054931 | -0.16937 | -0.16479 | -0.054932 | 0.013733 | 61.2442 | 61.5829 | 121.4767 | 121.4767 | -0.022888 | 121.5912 | 61.6013 | -0.16479 | 121.4767 | -0.022888 | 61.6013 | 121.4767 | 121.5912 | -121.6827 | -121.8109
1148.5938 | 121.8475 | -61.3312 | 60.3241 | -0.068283 | 0.012405 | -0.0022965 | 0.013185 | 0.050755 | -0.012886 | 0.067116 | -61.3358 | 60.2188 | -61.3907 | -61.3495 | 60.0861 | 0.2243 | -0.027466 | 0.091553 | 60.3424 | -61.441 | -0.059509 | -0.10529 | -0.004577 | -0.01831 | -0.23804 | -0.10986 | 0.01831 | 0.054932 | 61.3037 | 61.4227 | 121.4172 | 121.55 | -0.004577 | 121.6736 | 61.5555 | -0.10986 | 121.55 | -0.004577 | 61.5555 | 121.4172 | 121.6736 | -121.7148 | -121.7651
1150.3281 | 121.8842 | -61.2625 | 60.4019 | -0.2285 | 0.011978 | -0.0018693 | 0.0061352 | 0.049687 | -0.01139 | 0.066689 | -61.3129 | 60.3333 | -61.322 | -61.3632 | 60.1135 | 0.31128 | 0.23346 | 0.26093 | 60.3973 | -61.4182 | -0.059509 | -0.068665 | -0.050354 | -0.10071 | -0.28839 | -0.15564 | -0.004578 | 0.009155 | 61.496 | 61.5234 | 121.376 | 121.5958 | -0.050354 | 121.6599 | 61.5738 | -0.15564 | 121.5958 | -0.050354 | 61.5738 | 121.376 | 121.6599 | -121.7239 | -121.8201
1152.0781 | 121.8475 | -61.2991 | 60.3378 | -0.15221 | 0.014328 | -0.00037386 | 0.011903 | 0.051396 | -0.011604 | 0.067757 | -61.3495 | 60.2646 | -61.3724 | -61.377 | 60.0998 | 0.25635 | 0.091553 | 0.15564 | 60.4019 | -61.409 | -0.073242 | -0.073243 | -0.050354 | -0.07782 | -0.23804 | -0.10986 | 0.064087 | 0.022888 | 61.3907 | 61.4548 | 121.3989 | 121.5637 | -0.050354 | 121.701 | 61.5555 | -0.10986 | 121.5637 | -0.050354 | 61.5555 | 121.3989 | 121.701 | -121.7102 | -121.7468
1153.7656 | 121.9803 | -61.2671 | 60.2921 | 0.12245 | 0.014755 | -0.0031509 | 0.011689 | 0.053105 | -0.012672 | 0.067757 | -61.4182 | 60.1639 | -61.4365 | -61.4822 | 59.9854 | 0.045776 | -0.12817 | -0.10071 | 60.3333 | -61.4548 | -0.16937 | -0.12817 | -0.15106 | -0.21515 | -0.3067 | -0.18768 | 0.041199 | 0.01831 | 61.1389 | 61.1664 | 121.2524 | 121.431 | -0.15106 | 121.6003 | 61.3129 | -0.18768 | 121.431 | -0.15106 | 61.3129 | 121.2524 | 121.6003 | -121.7285 | -121.7468
1155.5156 | 121.9208 | -61.2213 | 60.3607 | 0.13771 | 0.014755 | -0.0018693 | 0.010408 | 0.052464 | -0.012031 | 0.068184 | -61.3495 | 60.1868 | -61.3953 | -61.4044 | 60.0723 | 0.12817 | -0.27466 | 0.009155 | 60.2829 | -61.441 | -0.17395 | -0.17395 | -0.12817 | -0.18311 | -0.28839 | -0.21973 | -0.07782 | 0.045777 | 60.9467 | 61.2305 | 121.2936 | 121.4081 | -0.12817 | 121.5042 | 61.3495 | -0.21973 | 121.4081 | -0.12817 | 61.3495 | 121.2936 | 121.5042 | -121.756 | -121.8018
1157.2656 | 121.8384 | -61.3083 | 60.3745 | -0.10643 | 0.012832 | 5.3338e-05 | 0.0097668 | 0.053318 | -0.010963 | 0.06797 | -61.3266 | 60.26 | -61.3724 | -61.3586 | 60.1181 | 0.23804 | 0.054932 | 0.14191 | 60.3699 | -61.4365 | -0.064086 | -0.11444 | -0.01831 | -0.050354 | -0.25635 | -0.12817 | -0.004578 | 0.045776 | 61.3632 | 61.4502 | 121.4264 | 121.5683 | -0.01831 | 121.6782 | 61.5463 | -0.12817 | 121.5683 | -0.01831 | 61.5463 | 121.4264 | 121.6782 | -121.7468 | -121.8109
1159.0156 | 121.907 | -61.1938 | 60.4385 | -0.060654 | 0.014755 | -0.0029373 | 0.0025036 | 0.050968 | -0.0090406 | 0.06797 | -61.235 | 60.2737 | -61.2488 | -61.2671 | 60.2325 | 0.37537 | 0.041199 | 0.32959 | 60.3882 | -61.3953 | -0.054931 | -0.16479 | -0.041198 | -0.073242 | -0.20599 | -0.20142 | -0.050354 | 0.013733 | 61.235 | 61.5234 | 121.4264 | 121.4676 | -0.041198 | 121.582 | 61.5692 | -0.20142 | 121.4676 | -0.041198 | 61.5692 | 121.4264 | 121.582 | -121.6873 | -121.8338
1160.7031 | 121.9345 | -61.2122 | 60.3561 | 0.1606 | 0.011764 | 0.00048074 | 0.010194 | 0.053532 | -0.014167 | 0.066689 | -61.3129 | 60.1501 | -61.3861 | -61.3678 | 60.0998 | 0.15106 | -0.30212 | 0.032043 | 60.2692 | -61.4227 | -0.17395 | -0.20599 | -0.10071 | -0.15564 | -0.25635 | -0.21057 | -0.086975 | 0.073242 | 60.91 | 61.2442 | 121.3119 | 121.3623 | -0.10071 | 121.4813 | 61.3632 | -0.21057 | 121.3623 | -0.10071 | 61.3632 | 121.3119 | 121.4813 | -121.7422 | -121.7789
1162.4375 | 121.9803 | -61.1847 | 60.4019 | 0.038529 | 0.014969 | -0.0010147 | 0.0054944 | 0.050968 | -0.010322 | 0.065621 | -61.3358 | 60.2234 | -61.3632 | -61.3541 | 60.1181 | 0.21515 | -0.054932 | 0.14191 | 60.3607 | -61.3953 | -0.17853 | -0.17853 | -0.15106 | -0.16937 | -0.28381 | -0.21057 | -0.041199 | 0.027466 | 61.1298 | 61.3266 | 121.3028 | 121.4081 | -0.15106 | 121.5454 | 61.3998 | -0.21057 | 121.4081 | -0.15106 | 61.3998 | 121.3028 | 121.5454 | -121.7651 | -121.7972
1164.1875 | 121.8567 | -61.2122 | 60.4431 | -0.14458 | 0.01326 | -0.0016557 | 0.0065624 | 0.049046 | -0.010322 | 0.06498 | -61.203 | 60.2417 | -61.2808 | -61.2167 | 60.2692 | 0.41199 | 0.064087 | 0.39368 | 60.3973 | -61.3678 | -0.068665 | -0.20142 | 0.009155 | -0.004578 | -0.17395 | -0.15564 | -0.045776 | 0.07782 | 61.2762 | 61.6058 | 121.4813 | 121.4539 | 0.009155 | 121.6095 | 61.6241 | -0.15564 | 121.4539 | 0.009155 | 61.6241 | 121.4813 | 121.6095 | -121.7239 | -121.8109
1165.875 | 121.9757 | -61.2762 | 60.2921 | 0.12245 | 0.013473 | 0.00048074 | 0.012758 | 0.05225 | -0.012031 | 0.066689 | -61.4502 | 60.2005 | -61.441 | -61.4777 | 59.9716 | 0.050354 | -0.12817 | -0.1236 | 60.3241 | -61.496 | -0.16479 | -0.091553 | -0.17395 | -0.20142 | -0.32043 | -0.21973 | 0.032044 | -0.009155 | 61.1481 | 61.1526 | 121.2479 | 121.4767 | -0.17395 | 121.6003 | 61.3266 | -0.21973 | 121.4767 | -0.17395 | 61.3266 | 121.2479 | 121.6003 | -121.7331 | -121.788
1167.625 | 121.9666 | -61.2625 | 60.3287 | 0.099564 | 0.01326 | 0.00069434 | 0.012117 | 0.05225 | -0.008827 | 0.067543 | -61.4182 | 60.2097 | -61.4136 | -61.4548 | 60.0082 | 0.064087 | -0.15564 | -0.091553 | 60.3149 | -61.4868 | -0.15106 | -0.11902 | -0.15564 | -0.19226 | -0.32043 | -0.2243 | -0.013733 | -0.004578 | 61.1069 | 61.171 | 121.2708 | 121.4722 | -0.15564 | 121.5775 | 61.3266 | -0.2243 | 121.4722 | -0.15564 | 61.3266 | 121.2708 | 121.5775 | -121.7422 | -121.8155
1169.3906 | 121.8521 | -61.3129 | 60.3745 | -0.060654 | 0.012832 | 0.00048074 | 0.012971 | 0.051609 | -0.010322 | 0.066048 | -61.3449 | 60.2325 | -61.3861 | -61.3907 | 60.0632 | 0.19226 | -0.059509 | 0.041199 | 60.3424 | -61.4639 | -0.073242 | -0.14191 | -0.032044 | -0.07782 | -0.31128 | -0.15106 | -0.032044 | 0.041198 | 61.2534 | 61.3541 | 121.376 | 121.5454 | -0.032044 | 121.6553 | 61.5051 | -0.15106 | 121.5454 | -0.032044 | 61.5051 | 121.376 | 121.6553 | -121.7606 | -121.8384
1171.1406 | 121.9025 | -61.2442 | 60.4019 | -0.22087 | 0.011764 | -0.0048599 | 0.005708 | 0.049687 | -0.0090406 | 0.067116 | -61.3541 | 60.3241 | -61.3174 | -61.3632 | 60.1181 | 0.29297 | 0.2655 | 0.24719 | 60.4111 | -61.4182 | -0.073242 | -0.07782 | -0.10986 | -0.11902 | -0.28381 | -0.17395 | 0.009155 | -0.036621 | 61.5097 | 61.4914 | 121.3623 | 121.5683 | -0.10986 | 121.6553 | 61.5372 | -0.17395 | 121.5683 | -0.10986 | 61.5372 | 121.3623 | 121.6553 | -121.7194 | -121.8201
1172.8281 | 121.8933 | -61.3129 | 60.3149 | 0.01564 | 0.0139 | -0.0022965 | 0.012758 | 0.051609 | -0.011818 | 0.068611 | -61.409 | 60.2188 | -61.4502 | -61.4685 | 60.022 | 0.10071 | -0.07782 | -0.054932 | 60.3333 | -61.4914 | -0.13733 | -0.09613 | -0.096131 | -0.15564 | -0.29297 | -0.17853 | 0.018311 | 0.041198 | 61.235 | 61.2579 | 121.3348 | 121.5317 | -0.096131 | 121.6461 | 61.4136 | -0.17853 | 121.5317 | -0.096131 | 61.4136 | 121.3348 | 121.6461 | -121.7651 | -121.8063
1174.5781 | 121.9757 | -61.1435 | 60.4019 | 0.01564 | 0.011551 | -0.0016557 | 0.0035718 | 0.049259 | -0.0075452 | 0.069252 | -61.3312 | 60.2554 | -61.3266 | -61.3586 | 60.1318 | 0.23346 | -0.004578 | 0.17395 | 60.3516 | -61.4136 | -0.18311 | -0.14648 | -0.18768 | -0.21515 | -0.27008 | -0.27008 | -0.050355 | -0.004578 | 61.1389 | 61.3174 | 121.2753 | 121.3989 | -0.18768 | 121.4951 | 61.377 | -0.27008 | 121.3989 | -0.18768 | 61.377 | 121.2753 | 121.4951 | -121.7285 | -121.8155
1176.2812 | 121.9254 | -61.2167 | 60.3653 | 0.10719 | 0.010482 | -0.0031509 | 0.0080578 | 0.050968 | -0.011818 | 0.066902 | -61.3174 | 60.1913 | -61.377 | -61.3495 | 60.141 | 0.19226 | -0.23346 | 0.091553 | 60.2692 | -61.4594 | -0.16022 | -0.17395 | -0.10071 | -0.13275 | -0.2243 | -0.24262 | -0.09613 | 0.059509 | 60.9833 | 61.3083 | 121.3577 | 121.4081 | -0.10071 | 121.4859 | 61.409 | -0.24262 | 121.4081 | -0.10071 | 61.409 | 121.3577 | 121.4859 | -121.7422 | -121.8246
1178.0312 | 122.0123 | -61.1984 | 60.3928 | 0.053787 | 0.014755 | 0.0011215 | 0.0086988 | 0.049259 | -0.0086132 | 0.067116 | -61.3312 | 60.228 | -61.3174 | -61.3586 | 60.1135 | 0.19684 | -0.11902 | 0.12817 | 60.3149 | -61.4273 | -0.11902 | -0.16479 | -0.13275 | -0.16022 | -0.27924 | -0.22888 | -0.07782 | -0.013733 | 61.0794 | 61.3266 | 121.3119 | 121.4264 | -0.13275 | 121.5134 | 61.3953 | -0.22888 | 121.4264 | -0.13275 | 61.3953 | 121.3119 | 121.5134 | -121.7102 | -121.8201
1179.7344 | 121.8338 | -61.2259 | 60.4431 | -0.21324 | 0.0139 | -0.0012283 | 0.0065624 | 0.050114 | -0.010536 | 0.064766 | -61.2213 | 60.2875 | -61.29 | -61.2305 | 60.2417 | 0.39825 | 0.09613 | 0.40283 | 60.3699 | -61.3632 | -0.064087 | -0.15564 | 0.004578 | -0.004578 | -0.20142 | -0.13733 | -0.073242 | 0.068665 | 61.322 | 61.6287 | 121.4676 | 121.5134 | 0.004578 | 121.5958 | 61.6241 | -0.13733 | 121.5134 | 0.004578 | 61.6241 | 121.4676 | 121.5958 | -121.7331 | -121.8063
1181.4844 | 121.8704 | -61.2122 | 60.4568 | -0.13695 | 0.013046 | -0.00058746 | 0.0067762 | 0.048832 | -0.006477 | 0.06733 | -61.235 | 60.2646 | -61.2946 | -61.2396 | 60.2142 | 0.37079 | 0.036621 | 0.36621 | 60.3561 | -61.3724 | -0.082398 | -0.19226 | -0.022888 | -0.027466 | -0.24262 | -0.16022 | -0.10071 | 0.05951 | 61.2488 | 61.5784 | 121.4264 | 121.4767 | -0.022888 | 121.5683 | 61.5829 | -0.16022 | 121.4767 | -0.022888 | 61.5829 | 121.4264 | 121.5683 | -121.7514 | -121.8292
1183.1719 | 121.9757 | -61.1847 | 60.4202 | 0.12245 | 0.011764 | -0.0029373 | 0.008485 | 0.050755 | -0.011604 | 0.067757 | -61.3174 | 60.1685 | -61.3312 | -61.3403 | 60.1273 | 0.18768 | -0.15106 | 0.10529 | 60.3699 | -61.409 | -0.14648 | -0.25177 | -0.13275 | -0.15564 | -0.29297 | -0.22431 | -0.050354 | 0.013733 | 61.0336 | 61.29 | 121.3119 | 121.3531 | -0.13275 | 121.5546 | 61.3724 | -0.22431 | 121.3531 | -0.13275 | 61.3724 | 121.3119 | 121.5546 | -121.7514 | -121.8292
1184.9062 | 121.8796 | -61.2717 | 60.3882 | -0.21324 | 0.012191 | -0.0018693 | 0.011262 | 0.051609 | -0.011818 | 0.066475 | -61.3312 | 60.3012 | -61.3403 | -61.3449 | 60.0952 | 0.2655 | 0.19684 | 0.18768 | 60.3836 | -61.4044 | -0.068665 | -0.086976 | -0.05951 | -0.073243 | -0.29297 | -0.13275 | -0.004578 | 0.009155 | 61.4685 | 61.4594 | 121.3669 | 121.5729 | -0.05951 | 121.6553 | 61.5372 | -0.13275 | 121.5729 | -0.05951 | 61.5372 | 121.3669 | 121.6553 | -121.7285 | -121.7926
1186.6562 | 121.9299 | -61.2122 | 60.3653 | 0.053787 | 0.011978 | 0.0013351 | 0.010835 | 0.051609 | -0.0075452 | 0.066262 | -61.3037 | 60.1959 | -61.3815 | -61.3312 | 60.1227 | 0.16022 | -0.29297 | 0.032043 | 60.2692 | -61.4548 | -0.16937 | -0.16937 | -0.091553 | -0.11902 | -0.24261 | -0.24262 | -0.09613 | 0.07782 | 60.9192 | 61.2442 | 121.3348 | 121.4081 | -0.091553 | 121.4813 | 61.3724 | -0.24262 | 121.4081 | -0.091553 | 61.3724 | 121.3348 | 121.4813 | -121.7468 | -121.8201
1188.3438 | 121.8246 | -61.322 | 60.3424 | -0.10643 | 0.013046 | -0.0033647 | 0.014039 | 0.051182 | -0.011818 | 0.065621 | -61.322 | 60.228 | -61.3907 | -61.3449 | 60.0906 | 0.23804 | 0.013733 | 0.12817 | 60.347 | -61.4365 | -0.068665 | -0.11444 | 0 | -0.022889 | -0.25177 | -0.11444 | 0.004578 | 0.068665 | 61.3358 | 61.4502 | 121.4127 | 121.55 | 0 | 121.669 | 61.5601 | -0.11444 | 121.55 | 0 | 61.5601 | 121.4127 | 121.669 | -121.7331 | -121.7789
1190.0938 | 121.8933 | -61.2946 | 60.347 | 0.030899 | 0.013046 | -0.0016557 | 0.012117 | 0.05225 | -0.012672 | 0.06797 | -61.3998 | 60.2234 | -61.4227 | -61.4456 | 60.022 | 0.091553 | -0.086975 | -0.045776 | 60.3424 | -61.4731 | -0.12817 | -0.1236 | -0.10529 | -0.15106 | -0.32501 | -0.17853 | -0.004578 | 0.022888 | 61.2076 | 61.2488 | 121.3165 | 121.5179 | -0.10529 | 121.637 | 61.3861 | -0.17853 | 121.5179 | -0.10529 | 61.3861 | 121.3165 | 121.637 | -121.7697 | -121.8201
1191.7812 | 121.9757 | -61.1526 | 60.4202 | -0.022507 | 0.012405 | -0.00016026 | 0.0048534 | 0.050541 | -0.010109 | 0.067116 | -61.3174 | 60.2829 | -61.29 | -61.322 | 60.1501 | 0.25177 | -0.009155 | 0.21057 | 60.3836 | -61.3815 | -0.13733 | -0.13733 | -0.1648 | -0.16937 | -0.27008 | -0.22888 | -0.036621 | -0.027466 | 61.1435 | 61.3632 | 121.3028 | 121.4355 | -0.1648 | 121.5363 | 61.4044 | -0.22888 | 121.4355 | -0.1648 | 61.4044 | 121.3028 | 121.5363 | -121.7102 | -121.8018
1193.5312 | 121.843 | -61.2122 | 60.4706 | -0.15984 | 0.011978 | -0.0059281 | 0.007417 | 0.049259 | -0.0090406 | 0.065834 | -61.2213 | 60.2829 | -61.2671 | -61.2442 | 60.2417 | 0.39825 | 0.09613 | 0.36163 | 60.4111 | -61.3678 | -0.054932 | -0.18768 | -0.009155 | -0.032044 | -0.22888 | -0.15564 | -0.059509 | 0.045777 | 61.3083 | 61.5738 | 121.4539 | 121.4951 | -0.009155 | 121.6232 | 61.6104 | -0.15564 | 121.4951 | -0.009155 | 61.6104 | 121.4539 | 121.6232 | -121.7377 | -121.8384
1195.2188 | 121.8704 | -61.1938 | 60.4614 | -0.19798 | 0.012619 | -0.0046463 | 0.0089124 | 0.048832 | -0.0092542 | 0.066689 | -61.2305 | 60.3104 | -61.2808 | -61.2442 | 60.2188 | 0.38452 | 0.18768 | 0.36621 | 60.3882 | -61.3541 | -0.086975 | -0.15106 | -0.036621 | -0.050354 | -0.24262 | -0.16022 | -0.073242 | 0.050354 | 61.3815 | 61.5601 | 121.4127 | 121.5042 | -0.036621 | 121.582 | 61.5784 | -0.16022 | 121.5042 | -0.036621 | 61.5784 | 121.4127 | 121.582 | -121.7422 | -121.8155
1196.9688 | 121.9208 | -61.203 | 60.3973 | 0.13771 | 0.012405 | -0.0037919 | 0.0082714 | 0.0499 | -0.011177 | 0.065834 | -61.2946 | 60.1776 | -61.3678 | -61.3174 | 60.141 | 0.17395 | -0.24719 | 0.091553 | 60.3287 | -61.3998 | -0.16479 | -0.21973 | -0.091553 | -0.11444 | -0.25635 | -0.19684 | -0.068665 | 0.073242 | 60.9558 | 61.2946 | 121.344 | 121.3806 | -0.091553 | 121.5317 | 61.377 | -0.19684 | 121.3806 | -0.091553 | 61.377 | 121.344 | 121.5317 | -121.7651 | -121.7972
1198.6562 | 121.8567 | -61.2717 | 60.3561 | -0.030136 | 0.016037 | -0.0069961 | 0.013612 | 0.051182 | -0.010536 | 0.069466 | -61.3266 | 60.2325 | -61.3724 | -61.3632 | 60.0632 | 0.16022 | -0.059509 | 0.022888 | 60.3653 | -61.4365 | -0.10071 | -0.1236 | -0.054932 | -0.091553 | -0.29297 | -0.16479 | 0.009155 | 0.045776 | 61.2122 | 61.2946 | 121.3348 | 121.5042 | -0.054932 | 121.637 | 61.4319 | -0.16479 | 121.5042 | -0.054932 | 61.4319 | 121.3348 | 121.637 | -121.7285 | -121.7926
1200.4062 | 121.8979 | -61.2579 | 60.3607 | -0.22087 | 0.0139 | -0.0027237 | 0.0082714 | 0.050755 | -0.01075 | 0.064339 | -61.3174 | 60.3561 | -61.322 | -61.3266 | 60.1273 | 0.29297 | 0.22888 | 0.19684 | 60.4431 | -61.3907 | -0.064086 | -0.004578 | -0.059509 | -0.068664 | -0.23346 | -0.13275 | 0.082397 | 0.004577 | 61.4868 | 61.4548 | 121.3852 | 121.6141 | -0.059509 | 121.7011 | 61.5509 | -0.13275 | 121.6141 | -0.059509 | 61.5509 | 121.3852 | 121.7011 | -121.6827 | -121.7514
1202.1562 | 121.907 | -61.2991 | 60.3378 | 0.046158 | 0.012405 | 0.0028305 | 0.013185 | 0.050968 | -0.0086132 | 0.066262 | -61.3861 | 60.2234 | -61.4044 | -61.4319 | 60.0357 | 0.09613 | -0.068665 | -0.045776 | 60.3653 | -61.4685 | -0.10529 | -0.11444 | -0.086975 | -0.13275 | -0.30212 | -0.16937 | 0.027465 | 0.018311 | 61.2305 | 61.2534 | 121.3348 | 121.5225 | -0.086975 | 121.6644 | 61.3953 | -0.16937 | 121.5225 | -0.086975 | 61.3953 | 121.3348 | 121.6644 | -121.7422 | -121.8063
1203.9062 | 121.9254 | -61.1755 | 60.4065 | 0.091934 | 0.011123 | -0.0020829 | 0.0076306 | 0.050114 | -0.0083996 | 0.065621 | -61.2808 | 60.2051 | -61.3174 | -61.3174 | 60.1501 | 0.17395 | -0.23346 | 0.086975 | 60.3287 | -61.4273 | -0.14191 | -0.20142 | -0.10529 | -0.14191 | -0.25635 | -0.25177 | -0.07782 | 0.036621 | 60.9421 | 61.2625 | 121.3257 | 121.3806 | -0.10529 | 121.5042 | 61.3495 | -0.25177 | 121.3806 | -0.10529 | 61.3495 | 121.3257 | 121.5042 | -121.7239 | -121.8338
1205.6562 | 121.843 | -61.1893 | 60.4614 | -0.15221 | 0.011978 | -0.0018693 | 0.0052808 | 0.048619 | -0.008827 | 0.068184 | -61.1847 | 60.3104 | -61.235 | -61.2076 | 60.2783 | 0.40741 | 0.068665 | 0.39368 | 60.3928 | -61.3586 | -0.045776 | -0.15106 | 0.004578 | -0.018311 | -0.18311 | -0.16937 | -0.068665 | 0.050354 | 61.2579 | 61.5829 | 121.4676 | 121.4996 | 0.004578 | 121.582 | 61.5967 | -0.16937 | 121.4996 | 0.004578 | 61.5967 | 121.4676 | 121.582 | -121.6965 | -121.8201
1207.3906 | 121.8475 | -61.29 | 60.3882 | -0.075912 | 0.012619 | 0.00026694 | 0.015107 | 0.05225 | -0.011818 | 0.068611 | -61.2946 | 60.2463 | -61.3724 | -61.3358 | 60.1135 | 0.20599 | -0.041199 | 0.07782 | 60.4065 | -61.3907 | -0.082397 | -0.14191 | -0.004578 | -0.045776 | -0.27466 | -0.10071 | 0.01831 | 0.077819 | 61.2488 | 61.3678 | 121.4035 | 121.5363 | -0.004578 | 121.6965 | 61.496 | -0.10071 | 121.5363 | -0.004578 | 61.496 | 121.4035 | 121.6965 | -121.7606 | -121.7789
1209.0938 | 121.9849 | -61.1481 | 60.4477 | 0.0080111 | 0.013473 | -0.00058746 | 0.0050672 | 0.051182 | -0.0094678 | 0.065621 | -61.2854 | 60.2737 | -61.2854 | -61.3358 | 60.1639 | 0.21973 | -0.027466 | 0.16022 | 60.3699 | -61.3815 | -0.13733 | -0.17395 | -0.13733 | -0.18768 | -0.28381 | -0.23346 | -0.07782 | 0 | 61.1206 | 61.3083 | 121.3119 | 121.4218 | -0.13733 | 121.5179 | 61.3678 | -0.23346 | 121.4218 | -0.13733 | 61.3678 | 121.3119 | 121.5179 | -121.7331 | -121.8292
1210.8438 | 121.9299 | -61.2762 | 60.3424 | 0.053787 | 0.013046 | 0.00026694 | 0.013826 | 0.050968 | -0.010322 | 0.068611 | -61.3815 | 60.2371 | -61.4044 | -61.4182 | 60.0403 | 0.082397 | -0.068665 | -0.068665 | 60.3561 | -61.4456 | -0.12817 | -0.10529 | -0.10529 | -0.14191 | -0.30212 | -0.16937 | 0.013733 | 0.022888 | 61.2076 | 61.2076 | 121.3165 | 121.5134 | -0.10529 | 121.6324 | 61.3586 | -0.16937 | 121.5134 | -0.10529 | 61.3586 | 121.3165 | 121.6324 | -121.7468 | -121.788
1212.5938 | 121.9986 | -61.1572 | 60.4294 | 0.01564 | 0.012832 | -0.00080106 | 0.0044262 | 0.048832 | -0.008827 | 0.066689 | -61.2991 | 60.3012 | -61.2946 | -61.322 | 60.1593 | 0.2243 | -0.018311 | 0.16479 | 60.3607 | -61.3861 | -0.13733 | -0.12817 | -0.14191 | -0.16479 | -0.27008 | -0.22888 | -0.068664 | -0.004577 | 61.1389 | 61.322 | 121.3165 | 121.4584 | -0.14191 | 121.5179 | 61.3815 | -0.22888 | 121.4584 | -0.14191 | 61.3815 | 121.3165 | 121.5179 | -121.7239 | -121.8155
1214.3438 | 121.9482 | -61.2259 | 60.3653 | 0.11482 | 0.015823 | -0.0010147 | 0.011903 | 0.051396 | -0.01075 | 0.066475 | -61.3815 | 60.2463 | -61.377 | -61.4182 | 60.0403 | 0.064087 | -0.18768 | -0.09613 | 60.347 | -61.4685 | -0.15106 | -0.11902 | -0.15564 | -0.19226 | -0.32501 | -0.24262 | -0.01831 | -0.004578 | 61.0382 | 61.1298 | 121.2662 | 121.4722 | -0.15564 | 121.5729 | 61.29 | -0.24262 | 121.4722 | -0.15564 | 61.29 | 121.2662 | 121.5729 | -121.7422 | -121.8338
1216.0312 | 121.9757 | -61.2488 | 60.347 | 0.10719 | 0.011337 | -0.0014419 | 0.011903 | 0.052037 | -0.01139 | 0.067543 | -61.4182 | 60.1959 | -61.4273 | -61.4594 | 60.0082 | 0.050354 | -0.14191 | -0.11902 | 60.3653 | -61.4685 | -0.17853 | -0.15106 | -0.16937 | -0.21057 | -0.33874 | -0.21973 | 0.01831 | 0.009155 | 61.1069 | 61.1298 | 121.257 | 121.4447 | -0.16937 | 121.6141 | 61.2991 | -0.21973 | 121.4447 | -0.16937 | 61.2991 | 121.257 | 121.6141 | -121.7743 | -121.8155
1217.7812 | 121.875 | -61.1572 | 60.4935 | -0.13695 | 0.013046 | -0.0035783 | 0.005708 | 0.051182 | -0.008186 | 0.069039 | -61.2213 | 60.2966 | -61.2488 | -61.2213 | 60.2646 | 0.3891 | 0.027466 | 0.36621 | 60.3928 | -61.3678 | -0.091552 | -0.19684 | -0.064086 | -0.064086 | -0.22888 | -0.21057 | -0.10071 | 0.027466 | 61.1847 | 61.5234 | 121.4218 | 121.4539 | -0.064086 | 121.55 | 61.5463 | -0.21057 | 121.4539 | -0.064086 | 61.5463 | 121.4218 | 121.55 | -121.7422 | -121.8613
1219.4844 | 121.9757 | -61.1343 | 60.4202 | -0.014877 | 0.011123 | -0.0031509 | 0.003999 | 0.046696 | -0.010963 | 0.066689 | -61.3083 | 60.2325 | -61.3037 | -61.322 | 60.1685 | 0.24719 | 0 | 0.20599 | 60.3882 | -61.3632 | -0.16937 | -0.18768 | -0.17395 | -0.18768 | -0.25177 | -0.22888 | -0.032043 | -0.004578 | 61.1343 | 61.3403 | 121.3028 | 121.3669 | -0.17395 | 121.5225 | 61.3815 | -0.22888 | 121.3669 | -0.17395 | 61.3815 | 121.3028 | 121.5225 | -121.7239 | -121.7834
1221.2344 | 121.8613 | -61.2122 | 60.4568 | -0.25139 | 0.010482 | -0.0052873 | 0.008485 | 0.046696 | -0.0086132 | 0.067116 | -61.2122 | 60.3104 | -61.2625 | -61.2442 | 60.2097 | 0.36621 | 0.20599 | 0.33417 | 60.4248 | -61.3541 | -0.050354 | -0.14648 | 0 | -0.032044 | -0.24719 | -0.14191 | -0.032043 | 0.050354 | 61.4182 | 61.5463 | 121.4218 | 121.5225 | 0 | 121.637 | 61.5784 | -0.14191 | 121.5225 | 0 | 61.5784 | 121.4218 | 121.637 | -121.7194 | -121.8109
1222.9844 | 121.9482 | -61.2625 | 60.3516 | 0.046158 | 0.014541 | -0.0031509 | 0.012758 | 0.051823 | -0.011818 | 0.067757 | -61.3861 | 60.2188 | -61.3998 | -61.4456 | 59.9991 | 0.050354 | -0.082397 | -0.10529 | 60.3333 | -61.4594 | -0.13733 | -0.13275 | -0.1236 | -0.18311 | -0.35248 | -0.19684 | -0.01831 | 0.013733 | 61.1801 | 61.1572 | 121.2616 | 121.4813 | -0.1236 | 121.5958 | 61.3129 | -0.19684 | 121.4813 | -0.1236 | 61.3129 | 121.2616 | 121.5958 | -121.7514 | -121.8109
1224.7344 | 121.8475 | -61.1893 | 60.466 | -0.17509 | 0.010696 | -0.0027237 | 0.0048534 | 0.051182 | -0.010536 | 0.065834 | -61.203 | 60.2875 | -61.2396 | -61.2259 | 60.2325 | 0.40741 | 0.091553 | 0.36621 | 60.4019 | -61.322 | -0.050354 | -0.17853 | -0.013733 | -0.036621 | -0.23346 | -0.13275 | -0.064086 | 0.036621 | 61.2808 | 61.5555 | 121.4218 | 121.4767 | -0.013733 | 121.5912 | 61.5967 | -0.13275 | 121.4767 | -0.013733 | 61.5967 | 121.4218 | 121.5912 | -121.7056 | -121.788
1226.5 | 121.8384 | -61.2122 | 60.4523 | -0.19035 | 0.013473 | -0.0052873 | 0.0072034 | 0.051823 | -0.011818 | 0.06498 | -61.1938 | 60.2966 | -61.2625 | -61.2167 | 60.2509 | 0.40741 | 0.10071 | 0.38452 | 60.4202 | -61.3358 | -0.050354 | -0.15564 | 0.01831 | -0.004578 | -0.20142 | -0.1236 | -0.032044 | 0.068664 | 61.3129 | 61.5967 | 121.463 | 121.5088 | 0.01831 | 121.6324 | 61.6196 | -0.1236 | 121.5088 | 0.01831 | 61.6196 | 121.463 | 121.6324 | -121.7148 | -121.788
1228.1875 | 121.9482 | -61.1481 | 60.4752 | -0.098801 | 0.0139 | -0.0040055 | 0.005708 | 0.049046 | -0.0094678 | 0.066262 | -61.2122 | 60.2966 | -61.2762 | -61.235 | 60.2371 | 0.36163 | 0.036621 | 0.33875 | 60.4156 | -61.3541 | -0.12817 | -0.17853 | -0.064087 | -0.086975 | -0.23804 | -0.20599 | -0.05951 | 0.064087 | 61.1847 | 61.4868 | 121.3852 | 121.4447 | -0.064087 | 121.5637 | 61.5097 | -0.20599 | 121.4447 | -0.064087 | 61.5097 | 121.3852 | 121.5637 | -121.7514 | -121.8292
1229.9375 | 121.9345 | -61.2076 | 60.3882 | 0.11482 | 0.0087734 | -0.0025101 | 0.011689 | 0.05225 | -0.01139 | 0.067757 | -61.2854 | 60.1547 | -61.3586 | -61.3266 | 60.1181 | 0.15564 | -0.3067 | 0.027466 | 60.2875 | -61.3953 | -0.15106 | -0.23346 | -0.077819 | -0.11902 | -0.27008 | -0.18768 | -0.10071 | 0.073243 | 60.9009 | 61.235 | 121.3257 | 121.3623 | -0.077819 | 121.4951 | 61.3632 | -0.18768 | 121.3623 | -0.077819 | 61.3632 | 121.3257 | 121.4951 | -121.7468 | -121.7834
1231.6719 | 121.9757 | -61.1481 | 60.4614 | 0.0080111 | 0.012619 | -0.0012283 | 0.0050672 | 0.051396 | -0.012886 | 0.067757 | -61.3083 | 60.2097 | -61.3174 | -61.3174 | 60.1547 | 0.23804 | -0.022888 | 0.17395 | 60.3836 | -61.3678 | -0.16937 | -0.25177 | -0.16022 | -0.16937 | -0.3067 | -0.21973 | -0.07782 | 0.009155 | 61.1252 | 61.322 | 121.3028 | 121.3577 | -0.16022 | 121.5317 | 61.3861 | -0.21973 | 121.3577 | -0.16022 | 61.3861 | 121.3028 | 121.5317 | -121.7789 | -121.8292
1233.3438 | 121.843 | -61.1893 | 60.4843 | -0.17509 | 0.010696 | -0.0010147 | 0.0078442 | 0.048832 | -0.010536 | 0.066475 | -61.1893 | 60.2875 | -61.2259 | -61.1984 | 60.26 | 0.41199 | 0.091553 | 0.40283 | 60.3973 | -61.3449 | -0.036621 | -0.19684 | 0 | -0.009155 | -0.2243 | -0.15564 | -0.086975 | 0.036621 | 61.2808 | 61.5921 | 121.4493 | 121.4767 | 0 | 121.5866 | 61.6013 | -0.15564 | 121.4767 | 0 | 61.6013 | 121.4493 | 121.5866 | -121.7102 | -121.8292
1235.0938 | 121.8567 | -61.2259 | 60.4614 | -0.20561 | 0.012191 | 0.00090794 | 0.011476 | 0.047764 | -0.008827 | 0.064766 | -61.2167 | 60.2966 | -61.2671 | -61.2167 | 60.2463 | 0.40283 | 0.091553 | 0.3891 | 60.3973 | -61.3449 | -0.041199 | -0.1648 | 0.009155 | 0.009155 | -0.21515 | -0.11902 | -0.064087 | 0.050354 | 61.3174 | 61.615 | 121.4722 | 121.5225 | 0.009155 | 121.6232 | 61.6287 | -0.11902 | 121.5225 | 0.009155 | 61.6287 | 121.4722 | 121.6232 | -121.7285 | -121.8063
1236.7812 | 121.9025 | -61.2167 | 60.3653 | 0.12245 | 0.011337 | 0.0028305 | 0.013612 | 0.050968 | -0.012031 | 0.067757 | -61.2991 | 60.1913 | -61.3953 | -61.3403 | 60.1227 | 0.15564 | -0.28839 | 0.022888 | 60.3333 | -61.4548 | -0.17853 | -0.17395 | -0.082397 | -0.1236 | -0.24261 | -0.23804 | -0.032043 | 0.096131 | 60.9283 | 61.2396 | 121.3394 | 121.4081 | -0.082397 | 121.55 | 61.3724 | -0.23804 | 121.4081 | -0.082397 | 61.3724 | 121.3394 | 121.55 | -121.7606 | -121.8201
1238.5469 | 121.8567 | -61.2991 | 60.3333 | -0.19035 | 0.013473 | -0.0042191 | 0.014039 | 0.052464 | -0.01139 | 0.067116 | -61.3174 | 60.2966 | -61.3724 | -61.3312 | 60.1227 | 0.24719 | 0.086975 | 0.16022 | 60.3882 | -61.4273 | -0.073242 | -0.036621 | -0.018311 | -0.032044 | -0.21057 | -0.12817 | 0.054932 | 0.054931 | 61.3861 | 61.4594 | 121.4218 | 121.5958 | -0.018311 | 121.6873 | 61.5463 | -0.12817 | 121.5958 | -0.018311 | 61.5463 | 121.4218 | 121.6873 | -121.7056 | -121.7606
1240.2344 | 121.9482 | -61.2396 | 60.3561 | 0.10719 | 0.01091 | -0.0012283 | 0.011262 | 0.051609 | -0.012886 | 0.06797 | -61.4136 | 60.2005 | -61.4227 | -61.4319 | 60.0449 | 0.073242 | -0.21973 | -0.086975 | 60.3058 | -61.4639 | -0.1831 | -0.15564 | -0.17395 | -0.19226 | -0.31128 | -0.2243 | -0.050354 | 0.009155 | 61.0199 | 61.1526 | 121.2845 | 121.4401 | -0.17395 | 121.5454 | 61.3129 | -0.2243 | 121.4401 | -0.17395 | 61.3129 | 121.2845 | 121.5454 | -121.7789 | -121.8201
1241.9844 | 121.9711 | -61.1618 | 60.4202 | 0.0080111 | 0.011978 | -0.0010147 | 0.005708 | 0.050328 | -0.0090406 | 0.065407 | -61.2991 | 60.2737 | -61.3174 | -61.3266 | 60.1639 | 0.2243 | 0 | 0.17853 | 60.3745 | -61.3861 | -0.15564 | -0.14648 | -0.13733 | -0.1648 | -0.25635 | -0.2243 | -0.045776 | 0.018311 | 61.1618 | 61.3403 | 121.3257 | 121.4355 | -0.13733 | 121.5363 | 61.3861 | -0.2243 | 121.4355 | -0.13733 | 61.3861 | 121.3257 | 121.5363 | -121.7377 | -121.8063
1243.7344 | 121.8521 | -61.235 | 60.4797 | -0.17509 | 0.0094144 | -0.0048599 | 0.0086988 | 0.051609 | -0.0079724 | 0.066262 | -61.203 | 60.2829 | -61.2717 | -61.2076 | 60.26 | 0.41199 | 0.086975 | 0.40741 | 60.3973 | -61.3449 | -0.036621 | -0.19684 | 0.032043 | 0.027465 | -0.21973 | -0.10986 | -0.082397 | 0.068664 | 61.322 | 61.6425 | 121.4951 | 121.5179 | 0.032043 | 121.6324 | 61.647 | -0.10986 | 121.5179 | 0.032043 | 61.647 | 121.4951 | 121.6324 | -121.7514 | -121.8246
1245.4219 | 121.8475 | -61.2808 | 60.3516 | -0.19035 | 0.012619 | -0.0016557 | 0.013612 | 0.051396 | -0.01374 | 0.06797 | -61.3403 | 60.2509 | -61.3907 | -61.3495 | 60.1135 | 0.26093 | 0.10529 | 0.16479 | 60.3973 | -61.4044 | -0.10986 | -0.10071 | -0.059509 | -0.068664 | -0.23804 | -0.1236 | 0.045777 | 0.050354 | 61.3861 | 61.4456 | 121.3943 | 121.5317 | -0.059509 | 121.6782 | 61.5417 | -0.1236 | 121.5317 | -0.059509 | 61.5417 | 121.3943 | 121.6782 | -121.7422 | -121.756
1247.1719 | 121.8384 | -61.3083 | 60.3653 | -0.12932 | 0.011764 | -0.00037386 | 0.012117 | 0.053105 | -0.011604 | 0.067543 | -61.3266 | 60.2509 | -61.3724 | -61.3495 | 60.141 | 0.25635 | 0.054932 | 0.15564 | 60.3653 | -61.409 | -0.064086 | -0.11444 | -0.01831 | -0.041198 | -0.2243 | -0.10071 | 0 | 0.045776 | 61.3632 | 61.4639 | 121.4493 | 121.5591 | -0.01831 | 121.6736 | 61.5646 | -0.10071 | 121.5591 | -0.01831 | 61.5646 | 121.4493 | 121.6736 | -121.7377 | -121.7743
1248.9219 | 121.9345 | -61.235 | 60.3699 | 0.18349 | 0.012832 | -0.0037919 | 0.007417 | 0.052677 | -0.010322 | 0.066475 | -61.3174 | 60.1639 | -61.3815 | -61.3495 | 60.1273 | 0.16937 | -0.30212 | 0.050354 | 60.3012 | -61.4456 | -0.14649 | -0.20599 | -0.082398 | -0.11444 | -0.24262 | -0.21057 | -0.068665 | 0.064087 | 60.9329 | 61.2854 | 121.3623 | 121.3989 | -0.082398 | 121.5363 | 61.4044 | -0.21057 | 121.3989 | -0.082398 | 61.4044 | 121.3623 | 121.5363 | -121.7514 | -121.8155
1250.6719 | 121.8155 | -61.3129 | 60.3561 | -0.11406 | 0.014755 | -0.0018693 | 0.012544 | 0.050328 | -0.011604 | 0.066689 | -61.3312 | 60.2463 | -61.3953 | -61.3495 | 60.1135 | 0.24261 | 0.018311 | 0.13733 | 60.3653 | -61.4227 | -0.082398 | -0.10986 | -0.018311 | -0.036621 | -0.24262 | -0.10986 | 0.009155 | 0.064087 | 61.3312 | 61.4502 | 121.4264 | 121.5591 | -0.018311 | 121.6782 | 61.5555 | -0.10986 | 121.5591 | -0.018311 | 61.5555 | 121.4264 | 121.6782 | -121.7514 | -121.7789
1252.3594 | 121.8887 | -61.2625 | 60.3928 | -0.21324 | 0.014969 | -0.0035783 | 0.0072034 | 0.050114 | -0.008827 | 0.065834 | -61.3129 | 60.3424 | -61.3358 | -61.3358 | 60.1273 | 0.3067 | 0.27924 | 0.23804 | 60.4294 | -61.3953 | -0.073242 | -0.050354 | -0.050354 | -0.073242 | -0.2655 | -0.13275 | 0.036621 | 0.022888 | 61.5417 | 61.5005 | 121.3898 | 121.6049 | -0.050354 | 121.6919 | 61.5692 | -0.13275 | 121.6049 | -0.050354 | 61.5692 | 121.3898 | 121.6919 | -121.7285 | -121.788
1254.1094 | 121.8887 | -61.1893 | 60.4477 | -0.12932 | 0.0139 | 5.3338e-05 | 0.0044262 | 0.050968 | -0.0092542 | 0.067116 | -61.2122 | 60.2554 | -61.2671 | -61.235 | 60.2371 | 0.37537 | 0.036621 | 0.35248 | 60.3836 | -61.377 | -0.07782 | -0.19226 | -0.022888 | -0.045776 | -0.21057 | -0.18768 | -0.064087 | 0.054932 | 61.2259 | 61.5417 | 121.4264 | 121.4447 | -0.022888 | 121.5729 | 61.5646 | -0.18768 | 121.4447 | -0.022888 | 61.5646 | 121.4264 | 121.5729 | -121.7148 | -121.8246
1255.7969 | 121.8613 | -61.2213 | 60.4385 | -0.24376 | 0.01091 | -0.0018693 | 0.0089124 | 0.049687 | -0.01139 | 0.067543 | -61.2442 | 60.3104 | -61.2854 | -61.2625 | 60.2051 | 0.37537 | 0.19226 | 0.34332 | 60.4385 | -61.3678 | -0.064087 | -0.12817 | -0.022889 | -0.041199 | -0.23346 | -0.14648 | 0 | 0.041198 | 61.4136 | 61.5646 | 121.4264 | 121.5317 | -0.022889 | 121.6599 | 61.5967 | -0.14648 | 121.5317 | -0.022889 | 61.5967 | 121.4264 | 121.6599 | -121.7239 | -121.8063
1257.5469 | 121.9711 | -61.2579 | 60.2829 | 0.13771 | 0.013046 | 0.0019759 | 0.012117 | 0.053746 | -0.011604 | 0.066689 | -61.409 | 60.2188 | -61.441 | -61.4502 | 60.0082 | 0.073242 | -0.13275 | -0.09613 | 60.3424 | -61.4548 | -0.1831 | -0.064087 | -0.15106 | -0.19226 | -0.27466 | -0.19684 | 0.059509 | 0.032043 | 61.1252 | 61.1618 | 121.2662 | 121.4767 | -0.15106 | 121.6003 | 61.3312 | -0.19684 | 121.4767 | -0.15106 | 61.3312 | 121.2662 | 121.6003 | -121.7239 | -121.7377
1259.2344 | 121.8796 | -61.2808 | 60.3607 | -0.16747 | 0.014114 | -0.0025101 | 0.0097668 | 0.051823 | -0.01139 | 0.067543 | -61.3312 | 60.3104 | -61.3632 | -61.3495 | 60.1089 | 0.27924 | 0.17853 | 0.16479 | 60.3745 | -61.4227 | -0.082397 | -0.050354 | -0.050354 | -0.068664 | -0.25177 | -0.14191 | 0.013733 | 0.032043 | 61.4594 | 61.4456 | 121.3898 | 121.5912 | -0.050354 | 121.6553 | 61.5601 | -0.14191 | 121.5912 | -0.050354 | 61.5601 | 121.3898 | 121.6553 | -121.7239 | -121.7834
1260.9844 | 121.8933 | -61.2488 | 60.379 | -0.2285 | 0.011337 | -0.00016026 | 0.008485 | 0.050968 | -0.010963 | 0.067757 | -61.3403 | 60.3287 | -61.3174 | -61.3724 | 60.1089 | 0.29297 | 0.23346 | 0.21515 | 60.4294 | -61.4182 | -0.068665 | -0.050354 | -0.091553 | -0.1236 | -0.27008 | -0.16937 | 0.050354 | -0.022888 | 61.4822 | 61.4639 | 121.3577 | 121.5775 | -0.091553 | 121.6782 | 61.5417 | -0.16937 | 121.5775 | -0.091553 | 61.5417 | 121.3577 | 121.6782 | -121.6965 | -121.7972
1262.7344 | 121.9437 | -61.2534 | 60.3195 | 0.13771 | 0.012619 | -0.0016557 | 0.010408 | 0.052037 | -0.0090406 | 0.067116 | -61.4273 | 60.1959 | -61.4319 | -61.4548 | 60.0082 | 0.082397 | -0.22888 | -0.059509 | 60.2692 | -61.5005 | -0.17853 | -0.1236 | -0.17395 | -0.20142 | -0.31128 | -0.24719 | -0.050354 | 0.004578 | 61.0245 | 61.1938 | 121.2616 | 121.4493 | -0.17395 | 121.5225 | 61.3358 | -0.24719 | 121.4493 | -0.17395 | 61.3358 | 121.2616 | 121.5225 | -121.7514 | -121.8201
1264.4219 | 121.8613 | -61.2579 | 60.4019 | -0.16747 | 0.010482 | 0.0011215 | 0.0061352 | 0.051609 | -0.011604 | 0.066048 | -61.29 | 60.2325 | -61.3083 | -61.29 | 60.1959 | 0.3891 | 0.17853 | 0.35248 | 60.3745 | -61.3907 | -0.050354 | -0.16937 | -0.032043 | -0.032043 | -0.20599 | -0.13275 | -0.027466 | 0.018311 | 61.4365 | 61.6104 | 121.4539 | 121.4905 | -0.032043 | 121.6324 | 61.647 | -0.13275 | 121.4905 | -0.032043 | 61.647 | 121.4539 | 121.6324 | -121.7102 | -121.7926
1266.1875 | 121.9574 | -61.2076 | 60.3882 | -0.014877 | 0.011551 | -0.0014419 | 0.0052808 | 0.047337 | -0.0073316 | 0.066262 | -61.3266 | 60.2371 | -61.3312 | -61.3632 | 60.1364 | 0.25177 | 0 | 0.21515 | 60.3424 | -61.4182 | -0.1236 | -0.15106 | -0.11902 | -0.15564 | -0.25177 | -0.21057 | -0.045777 | 0.004578 | 61.2076 | 61.4227 | 121.344 | 121.4447 | -0.11902 | 121.55 | 61.4594 | -0.21057 | 121.4447 | -0.11902 | 61.4594 | 121.344 | 121.55 | -121.7194 | -121.8063
1267.9375 | 121.9574 | -61.1984 | 60.4019 | 0.00038159 | 0.011551 | 5.3338e-05 | 0.0067762 | 0.0499 | -0.010109 | 0.066475 | -61.3358 | 60.2325 | -61.3449 | -61.3678 | 60.1273 | 0.22888 | -0.013733 | 0.16937 | 60.3424 | -61.4044 | -0.14648 | -0.16937 | -0.13733 | -0.16937 | -0.27466 | -0.20599 | -0.05951 | 0.009156 | 61.1847 | 61.3678 | 121.3257 | 121.431 | -0.13733 | 121.5408 | 61.4273 | -0.20599 | 121.431 | -0.13733 | 61.4273 | 121.3257 | 121.5408 | -121.7468 | -121.8063
1269.6875 | 121.8567 | -61.2534 | 60.4477 | -0.16747 | 0.012191 | -0.0027237 | 0.0080578 | 0.0499 | -0.0096814 | 0.064553 | -61.2259 | 60.2509 | -61.3129 | -61.2442 | 60.2188 | 0.41657 | 0.086975 | 0.39825 | 60.3882 | -61.3907 | -0.059509 | -0.19684 | 0.027466 | 0.009155 | -0.22888 | -0.13733 | -0.059509 | 0.086975 | 61.3403 | 61.6516 | 121.4722 | 121.5042 | 0.027466 | 121.6415 | 61.6699 | -0.13733 | 121.5042 | 0.027466 | 61.6699 | 121.4722 | 121.6415 | -121.7606 | -121.8384
1271.375 | 121.9025 | -61.2259 | 60.3516 | 0.1606 | 0.012191 | -0.0022965 | 0.011903 | 0.050755 | -0.011177 | 0.067757 | -61.3541 | 60.1318 | -61.4548 | -61.3678 | 60.0769 | 0.1831 | -0.28381 | 0.086975 | 60.2509 | -61.4777 | -0.22888 | -0.21973 | -0.12817 | -0.14191 | -0.27466 | -0.25177 | -0.10071 | 0.10071 | 60.9421 | 61.3129 | 121.3028 | 121.3577 | -0.12817 | 121.4767 | 61.409 | -0.25177 | 121.3577 | -0.12817 | 61.409 | 121.3028 | 121.4767 | -121.8063 | -121.8292
1273.125 | 121.9391 | -61.2488 | 60.3745 | 0.11482 | 0.011123 | -0.00016026 | 0.010194 | 0.051823 | -0.008827 | 0.067116 | -61.3449 | 60.1685 | -61.3861 | -61.377 | 60.0952 | 0.18768 | -0.22888 | 0.091553 | 60.2875 | -61.4731 | -0.13733 | -0.20599 | -0.096131 | -0.12817 | -0.27924 | -0.2243 | -0.086975 | 0.041198 | 61.0199 | 61.3403 | 121.344 | 121.4172 | -0.096131 | 121.5363 | 61.4365 | -0.2243 | 121.4172 | -0.096131 | 61.4365 | 121.344 | 121.5363 | -121.7606 | -121.8475
1274.875 | 121.9116 | -61.2213 | 60.3836 | -0.12932 | 0.012832 | -0.0022965 | 0.007417 | 0.050328 | -0.0092542 | 0.066048 | -61.2808 | 60.2463 | -61.3403 | -61.2946 | 60.1959 | 0.37079 | 0.027466 | 0.33875 | 60.3241 | -61.4227 | -0.11902 | -0.13733 | -0.05951 | -0.073243 | -0.18768 | -0.20142 | -0.059509 | 0.059509 | 61.2488 | 61.5601 | 121.4172 | 121.4676 | -0.05951 | 121.5454 | 61.5921 | -0.20142 | 121.4676 | -0.05951 | 61.5921 | 121.4172 | 121.5454 | -121.7239 | -121.8063
1276.5625 | 121.962 | -61.2213 | 60.3836 | -0.022507 | 0.011978 | -0.0033647 | 0.0069898 | 0.050114 | -0.0077588 | 0.06733 | -61.3586 | 60.2142 | -61.377 | -61.3632 | 60.1273 | 0.27008 | -0.004578 | 0.23804 | 60.3104 | -61.4548 | -0.15564 | -0.16937 | -0.13733 | -0.14191 | -0.25635 | -0.23346 | -0.073242 | 0.01831 | 61.2167 | 61.4594 | 121.3486 | 121.4355 | -0.13733 | 121.5317 | 61.4914 | -0.23346 | 121.4355 | -0.13733 | 61.4914 | 121.3486 | 121.5317 | -121.7606 | -121.8384
1278.2969 | 121.8979 | -61.29 | 60.3287 | -0.21324 | 0.015396 | -0.0025101 | 0.01468 | 0.048619 | -0.010322 | 0.065834 | -61.3678 | 60.2737 | -61.3815 | -61.3907 | 60.0769 | 0.29755 | 0.25635 | 0.25635 | 60.4019 | -61.4594 | -0.091553 | -0.054931 | -0.07782 | -0.10071 | -0.25177 | -0.16937 | 0.073243 | 0.013733 | 61.5463 | 61.5463 | 121.3669 | 121.5637 | -0.07782 | 121.6919 | 61.5875 | -0.16937 | 121.5637 | -0.07782 | 61.5875 | 121.3669 | 121.6919 | -121.7102 | -121.788
1280.0469 | 121.907 | -61.3174 | 60.3241 | -0.23613 | 0.011764 | -0.0027237 | 0.010835 | 0.0499 | -0.011604 | 0.065834 | -61.3998 | 60.2554 | -61.3953 | -61.3815 | 60.0494 | 0.27466 | 0.24719 | 0.21973 | 60.379 | -61.441 | -0.07782 | -0.068665 | -0.082397 | -0.064087 | -0.27466 | -0.1236 | 0.054931 | -0.004577 | 61.5646 | 61.5372 | 121.3669 | 121.5729 | -0.082397 | 121.6965 | 61.5921 | -0.1236 | 121.5729 | -0.082397 | 61.5921 | 121.3669 | 121.6965 | -121.7194 | -121.7651
1281.7969 | 121.9803 | -61.2305 | 60.3333 | 0.046158 | 0.0139 | -0.0012283 | 0.0063488 | 0.052037 | -0.0083996 | 0.06733 | -61.3815 | 60.1959 | -61.3907 | -61.3998 | 60.0861 | 0.21057 | -0.059509 | 0.14191 | 60.3104 | -61.4594 | -0.16022 | -0.13733 | -0.15106 | -0.16937 | -0.24719 | -0.22888 | -0.022888 | 0.009155 | 61.171 | 61.3724 | 121.3165 | 121.4264 | -0.15106 | 121.5408 | 61.441 | -0.22888 | 121.4264 | -0.15106 | 61.441 | 121.3165 | 121.5408 | -121.7239 | -121.7926
1283.5625 | 121.8796 | -61.3678 | 60.2783 | 0.01564 | 0.013687 | -0.0022965 | 0.015107 | 0.051823 | -0.012672 | 0.065834 | -61.4456 | 60.1593 | -61.5051 | -61.4868 | 59.9579 | 0.10529 | -0.086975 | -0.036621 | 60.2783 | -61.5509 | -0.13733 | -0.11902 | -0.07782 | -0.11902 | -0.32043 | -0.1831 | 0 | 0.059509 | 61.2808 | 61.3312 | 121.3257 | 121.5271 | -0.07782 | 121.6461 | 61.4731 | -0.1831 | 121.5271 | -0.07782 | 61.4731 | 121.3257 | 121.6461 | -121.7834 | -121.8292
1285.25 | 121.9803 | -61.2946 | 60.2509 | 0.10719 | 0.012619 | -0.0020829 | 0.010194 | 0.051823 | -0.010109 | 0.067116 | -61.4731 | 60.1364 | -61.4914 | -61.5051 | 59.9533 | 0.064087 | -0.21057 | -0.068665 | 60.2371 | -61.5646 | -0.19684 | -0.11444 | -0.17853 | -0.21057 | -0.29755 | -0.27008 | -0.013732 | 0.018311 | 61.084 | 61.2259 | 121.2479 | 121.431 | -0.17853 | 121.5317 | 61.3586 | -0.27008 | 121.431 | -0.17853 | 61.3586 | 121.2479 | 121.5317 | -121.7422 | -121.8155
1287 | 121.8658 | -61.2946 | 60.3836 | -0.11406 | 0.013046 | -0.0046463 | 0.003999 | 0.046269 | -0.008827 | 0.065834 | -61.2946 | 60.2417 | -61.3403 | -61.2762 | 60.2005 | 0.40741 | 0.036621 | 0.3891 | 60.3012 | -61.4502 | -0.045776 | -0.14191 | 0 | 0.018311 | -0.18311 | -0.15564 | -0.082398 | 0.045776 | 61.3312 | 61.6837 | 121.4951 | 121.5363 | 0 | 121.5958 | 61.702 | -0.15564 | 121.5363 | 0 | 61.702 | 121.4951 | 121.5958 | -121.7239 | -121.8338
1288.6719 | 121.9254 | -61.29 | 60.3149 | 0.13771 | 0.011337 | 0.0011215 | 0.0095532 | 0.050114 | -0.008827 | 0.065621 | -61.377 | 60.1044 | -61.4456 | -61.4044 | 60.0586 | 0.19226 | -0.23804 | 0.082397 | 60.2829 | -61.4914 | -0.15564 | -0.21057 | -0.086975 | -0.11444 | -0.25635 | -0.20142 | -0.032043 | 0.068665 | 61.0519 | 61.3724 | 121.3486 | 121.3943 | -0.086975 | 121.5729 | 61.4822 | -0.20142 | 121.3943 | -0.086975 | 61.4822 | 121.3486 | 121.5729 | -121.7606 | -121.8063
1290.4219 | 121.875 | -61.29 | 60.3653 | -0.19798 | 0.010482 | -0.00080106 | 0.007417 | 0.048832 | -0.01075 | 0.066689 | -61.3266 | 60.2142 | -61.3541 | -61.3266 | 60.1364 | 0.38452 | 0.18768 | 0.35706 | 60.3424 | -61.4502 | -0.064087 | -0.15106 | -0.036621 | -0.036621 | -0.22888 | -0.16022 | -0.022888 | 0.027466 | 61.4777 | 61.647 | 121.4264 | 121.5042 | -0.036621 | 121.6324 | 61.6745 | -0.16022 | 121.5042 | -0.036621 | 61.6745 | 121.4264 | 121.6324 | -121.7194 | -121.8155
1292.1094 | 121.8887 | -61.2579 | 60.3607 | -0.13695 | 0.013687 | -0.0078507 | 0.005708 | 0.049687 | -0.0069042 | 0.066689 | -61.3037 | 60.2188 | -61.3449 | -61.322 | 60.1639 | 0.38452 | 0.022888 | 0.35706 | 60.3195 | -61.4639 | -0.086975 | -0.14191 | -0.045776 | -0.064086 | -0.19684 | -0.20599 | -0.041199 | 0.041199 | 61.2808 | 61.615 | 121.4218 | 121.4767 | -0.045776 | 121.5775 | 61.6425 | -0.20599 | 121.4767 | -0.045776 | 61.6425 | 121.4218 | 121.5775 | -121.7056 | -121.8246
1293.8594 | 121.9803 | -61.2717 | 60.3195 | 0.00038159 | 0.0139 | -0.0020829 | 0.0076306 | 0.049687 | -0.010109 | 0.06733 | -61.3861 | 60.173 | -61.3998 | -61.4136 | 60.0632 | 0.23346 | -0.009155 | 0.18768 | 60.2966 | -61.4731 | -0.12817 | -0.14648 | -0.11444 | -0.14191 | -0.25635 | -0.20142 | -0.022888 | 0.013733 | 61.2625 | 61.4594 | 121.3348 | 121.4447 | -0.11444 | 121.5683 | 61.5051 | -0.20142 | 121.4447 | -0.11444 | 61.5051 | 121.3348 | 121.5683 | -121.7194 | -121.7926
1295.6094 | 121.9894 | -61.2213 | 60.3561 | -0.0072479 | 0.01091 | -0.0010147 | 0.010621 | 0.049687 | -0.0092542 | 0.067543 | -61.4044 | 60.2005 | -61.4182 | -61.4044 | 60.0632 | 0.21515 | -0.013733 | 0.16937 | 60.2921 | -61.5005 | -0.19684 | -0.15564 | -0.18311 | -0.18311 | -0.29297 | -0.27924 | -0.064087 | 0.013733 | 61.2076 | 61.3907 | 121.2845 | 121.4218 | -0.18311 | 121.5134 | 61.4365 | -0.27924 | 121.4218 | -0.18311 | 61.4365 | 121.2845 | 121.5134 | -121.7743 | -121.8567
1297.2812 | 121.8658 | -61.409 | 60.2463 | -0.075912 | 0.012405 | -0.0033647 | 0.017884 | 0.049259 | -0.0096814 | 0.066902 | -61.3998 | 60.1547 | -61.4868 | -61.4365 | 60.0082 | 0.21973 | -0.032043 | 0.10529 | 60.2737 | -61.5372 | -0.077819 | -0.091553 | 0.009156 | -0.027465 | -0.23804 | -0.12817 | 0.027466 | 0.086975 | 61.377 | 61.5143 | 121.4172 | 121.5637 | 0.009156 | 121.6827 | 61.6287 | -0.12817 | 121.5637 | 0.009156 | 61.6287 | 121.4172 | 121.6827 | -121.7331 | -121.7834
1299.0469 | 121.9574 | -61.3449 | 60.2051 | 0.12245 | 0.014114 | 0.00090794 | 0.012758 | 0.050755 | -0.010322 | 0.067116 | -61.5143 | 60.1364 | -61.528 | -61.5601 | 59.8938 | 0.050354 | -0.13275 | -0.10529 | 60.2325 | -61.6058 | -0.18311 | -0.068664 | -0.16937 | -0.21515 | -0.31128 | -0.26093 | 0.027466 | 0.013733 | 61.2122 | 61.2396 | 121.2387 | 121.4813 | -0.16937 | 121.5775 | 61.3953 | -0.26093 | 121.4813 | -0.16937 | 61.3953 | 121.2387 | 121.5775 | -121.7331 | -121.8109
1300.8125 | 121.8292 | -61.3953 | 60.2966 | -0.12169 | 0.010482 | -0.0065689 | 0.011903 | 0.050755 | -0.012886 | 0.067116 | -61.4227 | 60.141 | -61.4685 | -61.4502 | 60.0266 | 0.24719 | 0.059509 | 0.15564 | 60.2783 | -61.5005 | -0.073242 | -0.15564 | -0.027465 | -0.054931 | -0.27008 | -0.10529 | -0.018311 | 0.045777 | 61.4548 | 61.5509 | 121.4218 | 121.5363 | -0.027465 | 121.6736 | 61.6425 | -0.10529 | 121.5363 | -0.027465 | 61.6425 | 121.4218 | 121.6736 | -121.7651 | -121.7972
1302.5625 | 121.875 | -61.3541 | 60.2783 | -0.19035 | 0.014969 | -0.0046463 | 0.009126 | 0.050541 | -0.0092542 | 0.066475 | -61.4456 | 60.2234 | -61.4365 | -61.4502 | 60.0311 | 0.27466 | 0.18768 | 0.1831 | 60.3104 | -61.5189 | -0.082397 | -0.054931 | -0.091553 | -0.09613 | -0.24719 | -0.16479 | 0.032044 | -0.009156 | 61.5417 | 61.5372 | 121.3852 | 121.5775 | -0.091553 | 121.6644 | 61.6287 | -0.16479 | 121.5775 | -0.091553 | 61.6287 | 121.3852 | 121.6644 | -121.7148 | -121.7972
1304.25 | 121.9666 | -61.2625 | 60.3241 | 0.00038159 | 0.014114 | 0.0021895 | 0.0042126 | 0.051182 | -0.0083996 | 0.064766 | -61.4044 | 60.2005 | -61.3907 | -61.441 | 60.0586 | 0.26093 | -0.018311 | 0.20142 | 60.2737 | -61.5143 | -0.12817 | -0.1236 | -0.14191 | -0.17853 | -0.2655 | -0.25177 | -0.050354 | -0.013733 | 61.2442 | 61.4639 | 121.3211 | 121.463 | -0.14191 | 121.5363 | 61.5234 | -0.25177 | 121.463 | -0.14191 | 61.5234 | 121.3211 | 121.5363 | -121.7148 | -121.8384
1306 | 121.9254 | -61.3632 | 60.2325 | 0.099564 | 0.011764 | -0.0046463 | 0.012971 | 0.051823 | -0.012245 | 0.065834 | -61.5005 | 60.1089 | -61.5463 | -61.5463 | 59.9121 | 0.09613 | -0.064087 | -0.068665 | 60.26 | -61.5738 | -0.18311 | -0.1236 | -0.13733 | -0.18311 | -0.32043 | -0.21057 | 0.027466 | 0.045777 | 61.2991 | 61.2946 | 121.2753 | 121.4722 | -0.13733 | 121.6232 | 61.4594 | -0.21057 | 121.4722 | -0.13733 | 61.4594 | 121.2753 | 121.6232 | -121.7789 | -121.8063
1307.75 | 121.9803 | -61.2717 | 60.3104 | 0.046158 | 0.011123 | -0.0042191 | 0.0050672 | 0.050114 | -0.010109 | 0.064766 | -61.4136 | 60.1456 | -61.4182 | -61.4365 | 60.022 | 0.20142 | -0.091553 | 0.13275 | 60.26 | -61.5143 | -0.14648 | -0.16479 | -0.14191 | -0.16479 | -0.28839 | -0.24262 | -0.050354 | 0.004578 | 61.1801 | 61.4044 | 121.2936 | 121.4172 | -0.14191 | 121.5317 | 61.4731 | -0.24262 | 121.4172 | -0.14191 | 61.4731 | 121.2936 | 121.5317 | -121.7285 | -121.8246
1309.5 | 121.9482 | -61.3861 | 60.2097 | 0.053787 | 0.013046 | -0.0031509 | 0.01233 | 0.051396 | -0.01139 | 0.066048 | -61.528 | 60.1227 | -61.5417 | -61.5646 | 59.9121 | 0.082397 | -0.073242 | -0.091553 | 60.2371 | -61.5784 | -0.15564 | -0.086975 | -0.14191 | -0.17853 | -0.29755 | -0.19226 | 0.027466 | 0.013733 | 61.3129 | 61.2946 | 121.2982 | 121.5088 | -0.14191 | 121.6232 | 61.4685 | -0.19226 | 121.5088 | -0.14191 | 61.4685 | 121.2982 | 121.6232 | -121.7514 | -121.788
1311.1875 | 121.9711 | -61.3678 | 60.2509 | 0.13771 | 0.011337 | -0.0025101 | 0.012544 | 0.049473 | -0.011604 | 0.068825 | -61.5463 | 60.1135 | -61.5372 | -61.5646 | 59.9075 | 0.068665 | -0.13275 | -0.10529 | 60.2051 | -61.5829 | -0.16937 | -0.13733 | -0.17853 | -0.19684 | -0.34332 | -0.21515 | -0.045776 | -0.009156 | 61.235 | 61.2625 | 121.2753 | 121.4813 | -0.17853 | 121.5729 | 61.4365 | -0.21515 | 121.4813 | -0.17853 | 61.4365 | 121.2753 | 121.5729 | -121.788 | -121.8338
1312.9375 | 121.9254 | -61.2808 | 60.3378 | -0.075912 | 0.012832 | -0.0037919 | 0.0052808 | 0.0499 | -0.0083996 | 0.068825 | -61.3724 | 60.1685 | -61.3861 | -61.3678 | 60.1135 | 0.36163 | 0.036621 | 0.34332 | 60.2921 | -61.4822 | -0.10529 | -0.16937 | -0.091552 | -0.086975 | -0.2243 | -0.20142 | -0.045777 | 0.013733 | 61.3174 | 61.6241 | 121.3943 | 121.4493 | -0.091552 | 121.5729 | 61.6425 | -0.20142 | 121.4493 | -0.091552 | 61.6425 | 121.3943 | 121.5729 | -121.7239 | -121.8201
1314.625 | 121.907 | -61.3358 | 60.2829 | 0.17586 | 0.013687 | -0.0048599 | 0.010408 | 0.051396 | -0.0090406 | 0.065621 | -61.4227 | 60.0632 | -61.4731 | -61.4594 | 60.0037 | 0.17853 | -0.28839 | 0.064087 | 60.2051 | -61.5143 | -0.13733 | -0.21973 | -0.086975 | -0.1236 | -0.27924 | -0.17853 | -0.07782 | 0.050354 | 61.0474 | 61.3998 | 121.3394 | 121.3989 | -0.086975 | 121.5408 | 61.5143 | -0.17853 | 121.3989 | -0.086975 | 61.5143 | 121.3394 | 121.5408 | -121.756 | -121.7972
1316.375 | 121.962 | -61.2854 | 60.3058 | 0.061417 | 0.0098416 | -0.0044327 | 0.005708 | 0.048191 | -0.011177 | 0.065834 | -61.4227 | 60.1044 | -61.4456 | -61.4548 | 60.0357 | 0.20599 | -0.10986 | 0.13275 | 60.228 | -61.5189 | -0.16022 | -0.20142 | -0.13733 | -0.16937 | -0.27008 | -0.23346 | -0.07782 | 0.022889 | 61.1755 | 61.4182 | 121.3211 | 121.3898 | -0.13733 | 121.5134 | 61.4914 | -0.23346 | 121.3898 | -0.13733 | 61.4914 | 121.3211 | 121.5134 | -121.7514 | -121.8246
1318.125 | 121.9666 | -61.3495 | 60.228 | 0.10719 | 0.012191 | -0.00080106 | 0.011903 | 0.052464 | -0.010536 | 0.067757 | -61.5234 | 60.1089 | -61.5463 | -61.5372 | 59.9075 | 0.068665 | -0.17853 | -0.091553 | 60.2463 | -61.5601 | -0.19684 | -0.11902 | -0.17395 | -0.18768 | -0.32043 | -0.21057 | 0.018311 | 0.022889 | 61.171 | 61.2579 | 121.257 | 121.4584 | -0.17395 | 121.5958 | 61.4182 | -0.21057 | 121.4584 | -0.17395 | 61.4182 | 121.257 | 121.5958 | -121.7743 | -121.788
1319.8594 | 121.9803 | -61.2854 | 60.3012 | 0.00038159 | 0.011978 | 0.0013351 | 0.0054944 | 0.049259 | -0.0086132 | 0.06733 | -61.4227 | 60.1685 | -61.3998 | -61.4548 | 60.0174 | 0.24719 | -0.013733 | 0.19684 | 60.2417 | -61.528 | -0.11444 | -0.13275 | -0.13733 | -0.16937 | -0.28381 | -0.24262 | -0.059509 | -0.022888 | 61.2717 | 61.4822 | 121.3028 | 121.4539 | -0.13733 | 121.5271 | 61.5326 | -0.24262 | 121.4539 | -0.13733 | 61.5326 | 121.3028 | 121.5271 | -121.701 | -121.8292
1321.5469 | 121.8658 | -61.3083 | 60.3607 | -0.15984 | 0.011764 | -0.0044327 | 0.0089124 | 0.051396 | -0.010536 | 0.065407 | -61.3037 | 60.1776 | -61.377 | -61.3083 | 60.141 | 0.39825 | 0.07782 | 0.3891 | 60.3195 | -61.4548 | -0.068664 | -0.18311 | 0.004578 | 0 | -0.21973 | -0.14648 | -0.041199 | 0.073242 | 61.3861 | 61.6974 | 121.4493 | 121.4859 | 0.004578 | 121.6278 | 61.7065 | -0.14648 | 121.4859 | 0.004578 | 61.7065 | 121.4493 | 121.6278 | -121.7377 | -121.8155
1323.2969 | 122.0078 | -61.2762 | 60.3058 | 0.02327 | 0.0092008 | -0.0025101 | 0.008485 | 0.050114 | -0.0086132 | 0.068611 | -61.409 | 60.1456 | -61.4319 | -61.4365 | 60.0449 | 0.2243 | -0.050354 | 0.15106 | 60.2463 | -61.5005 | -0.15564 | -0.16022 | -0.13275 | -0.16022 | -0.26093 | -0.2243 | -0.059509 | 0.022888 | 61.2259 | 61.4273 | 121.3211 | 121.4218 | -0.13275 | 121.5225 | 61.5005 | -0.2243 | 121.4218 | -0.13275 | 61.5005 | 121.3211 | 121.5225 | -121.7377 | -121.8063
1325.0312 | 121.8933 | -61.3586 | 60.2646 | -0.25139 | 0.011123 | -0.0072099 | 0.01233 | 0.050968 | -0.011177 | 0.06498 | -61.4182 | 60.2325 | -61.4319 | -61.4319 | 60.022 | 0.30212 | 0.25177 | 0.23346 | 60.3287 | -61.496 | -0.073242 | -0.032043 | -0.059509 | -0.073242 | -0.24261 | -0.13733 | 0.064087 | 0.013733 | 61.6104 | 61.5921 | 121.3806 | 121.5912 | -0.059509 | 121.6873 | 61.6608 | -0.13733 | 121.5912 | -0.059509 | 61.6608 | 121.3806 | 121.6873 | -121.6965 | -121.7606
1326.7812 | 121.9528 | -61.2946 | 60.3149 | -0.037765 | 0.012832 | -0.0065689 | 0.0078442 | 0.047764 | -0.01075 | 0.066689 | -61.4044 | 60.1913 | -61.4044 | -61.4044 | 60.0769 | 0.3067 | 0.013733 | 0.27924 | 60.2737 | -61.4685 | -0.10986 | -0.1236 | -0.10986 | -0.10986 | -0.23804 | -0.17395 | -0.041198 | 0 | 61.3083 | 61.5738 | 121.3715 | 121.4859 | -0.10986 | 121.5683 | 61.6013 | -0.17395 | 121.4859 | -0.10986 | 61.6013 | 121.3715 | 121.5683 | -121.7194 | -121.7834
1328.5469 | 121.8842 | -61.3861 | 60.2921 | -0.17509 | 0.011551 | -0.0029373 | 0.01233 | 0.051182 | -0.011604 | 0.066689 | -61.4319 | 60.1913 | -61.4685 | -61.4273 | 60.0266 | 0.27924 | 0.17395 | 0.20142 | 60.3287 | -61.4777 | -0.082398 | -0.10071 | -0.045777 | -0.041199 | -0.2655 | -0.091553 | 0.036621 | 0.036621 | 61.5601 | 61.5875 | 121.4127 | 121.5775 | -0.045777 | 121.7148 | 61.6653 | -0.091553 | 121.5775 | -0.045777 | 61.6653 | 121.4127 | 121.7148 | -121.7606 | -121.7697
1330.2344 | 121.9391 | -61.29 | 60.2783 | 0.14534 | 0.01625 | 0.0013351 | 0.0099804 | 0.053105 | -0.012458 | 0.064553 | -61.377 | 60.1135 | -61.4548 | -61.4365 | 60.0311 | 0.16479 | -0.3067 | 0.036621 | 60.2188 | -61.5417 | -0.1648 | -0.16479 | -0.086975 | -0.14648 | -0.24719 | -0.25177 | -0.059509 | 0.07782 | 60.9833 | 61.3266 | 121.3211 | 121.4035 | -0.086975 | 121.5088 | 61.4548 | -0.25177 | 121.4035 | -0.086975 | 61.4548 | 121.3211 | 121.5088 | -121.7331 | -121.8201
1331.9844 | 121.8338 | -61.3815 | 60.26 | -0.098801 | 0.010482 | -0.0014419 | 0.012117 | 0.051823 | -0.012031 | 0.067543 | -61.4044 | 60.1547 | -61.496 | -61.441 | 60.0037 | 0.25177 | 0.018311 | 0.13733 | 60.2921 | -61.5097 | -0.11444 | -0.10529 | -0.022888 | -0.059509 | -0.25635 | -0.12817 | 0.032043 | 0.091553 | 61.3998 | 61.5189 | 121.3852 | 121.5363 | -0.022888 | 121.6736 | 61.6333 | -0.12817 | 121.5363 | -0.022888 | 61.6333 | 121.3852 | 121.6736 | -121.756 | -121.7697
1333.6719 | 121.875 | -61.3174 | 60.347 | -0.11406 | 0.012832 | -0.0048599 | 0.0046398 | 0.051396 | -0.0079724 | 0.066262 | -61.3312 | 60.1868 | -61.3998 | -61.3083 | 60.1776 | 0.42114 | 0.054932 | 0.38452 | 60.3149 | -61.4548 | -0.082397 | -0.16022 | -0.013733 | 0.009155 | -0.16937 | -0.13733 | -0.032044 | 0.068664 | 61.3724 | 61.702 | 121.4951 | 121.5042 | -0.013733 | 121.6324 | 61.7386 | -0.13733 | 121.5042 | -0.013733 | 61.7386 | 121.4951 | 121.6324 | -121.7468 | -121.8018
1335.4219 | 121.843 | -61.3129 | 60.3653 | -0.18272 | 0.011337 | -0.00016026 | 0.0069898 | 0.050114 | -0.011177 | 0.066902 | -61.2946 | 60.1776 | -61.3815 | -61.3266 | 60.1501 | 0.41657 | 0.091553 | 0.40283 | 60.2783 | -61.4548 | -0.068665 | -0.18768 | 0.01831 | -0.013733 | -0.21515 | -0.14191 | -0.086975 | 0.086975 | 61.4044 | 61.7157 | 121.463 | 121.4905 | 0.01831 | 121.5912 | 61.7294 | -0.14191 | 121.4905 | 0.01831 | 61.7294 | 121.463 | 121.5912 | -121.7468 | -121.8201
1337.1875 | 121.9803 | -61.2305 | 60.3424 | -0.0072479 | 0.011551 | -0.0029373 | 0.0076306 | 0.048832 | -0.0086132 | 0.066902 | -61.409 | 60.1501 | -61.4365 | -61.4273 | 60.054 | 0.25635 | -0.018311 | 0.19226 | 60.2875 | -61.496 | -0.20599 | -0.19226 | -0.17853 | -0.19684 | -0.28839 | -0.2655 | -0.054931 | 0.027465 | 61.2122 | 61.4227 | 121.2845 | 121.3806 | -0.17853 | 121.5179 | 61.4868 | -0.2655 | 121.3806 | -0.17853 | 61.4868 | 121.2845 | 121.5179 | -121.7789 | -121.8384
1338.9688 | 121.9803 | -61.3586 | 60.2417 | 0.10719 | 0.012832 | -0.0010147 | 0.013398 | 0.05225 | -0.012031 | 0.06733 | -61.5005 | 60.1181 | -61.5417 | -61.5417 | 59.9258 | 0.07782 | -0.20142 | -0.086975 | 60.2417 | -61.5646 | -0.1831 | -0.1236 | -0.14191 | -0.1831 | -0.31586 | -0.20599 | 0 | 0.041199 | 61.1572 | 61.2717 | 121.2845 | 121.4767 | -0.14191 | 121.6003 | 61.4365 | -0.20599 | 121.4767 | -0.14191 | 61.4365 | 121.2845 | 121.6003 | -121.7834 | -121.8063
1340.7188 | 121.9025 | -61.3678 | 60.2646 | -0.24376 | 0.013046 | -0.0035783 | 0.0095532 | 0.052037 | -0.009895 | 0.06733 | -61.4319 | 60.2463 | -61.4365 | -61.4548 | 60.0174 | 0.29755 | 0.25635 | 0.23804 | 60.3333 | -61.496 | -0.068664 | -0.01831 | -0.064087 | -0.086975 | -0.24719 | -0.12817 | 0.068665 | 0.004577 | 61.6241 | 61.6058 | 121.3852 | 121.6141 | -0.064087 | 121.7011 | 61.6653 | -0.12817 | 121.6141 | -0.064087 | 61.6653 | 121.3852 | 121.7011 | -121.701 | -121.7606
1342.4062 | 121.8658 | -61.4044 | 60.2692 | -0.19798 | 0.01326 | -0.0020829 | 0.013185 | 0.049687 | -0.012458 | 0.06733 | -61.4273 | 60.1913 | -61.4456 | -61.4502 | 59.9945 | 0.26093 | 0.13275 | 0.17853 | 60.2875 | -61.5463 | -0.041199 | -0.07782 | -0.022888 | -0.045776 | -0.27466 | -0.14191 | 0.018311 | 0.018311 | 61.5372 | 61.5829 | 121.3989 | 121.5958 | -0.022888 | 121.6919 | 61.6653 | -0.14191 | 121.5958 | -0.022888 | 61.6653 | 121.3989 | 121.6919 | -121.7148 | -121.8155
1344.1562 | 121.962 | -61.2946 | 60.3058 | -0.030136 | 0.011764 | -0.0025101 | 0.0033582 | 0.050968 | -0.0096814 | 0.065193 | -61.4182 | 60.173 | -61.4639 | -61.4365 | 60.0586 | 0.28381 | 0.004578 | 0.24261 | 60.2692 | -61.4868 | -0.16937 | -0.13275 | -0.1236 | -0.14191 | -0.24719 | -0.19226 | -0.036621 | 0.045776 | 61.2991 | 61.5372 | 121.3531 | 121.4676 | -0.1236 | 121.5637 | 61.5784 | -0.19226 | 121.4676 | -0.1236 | 61.5784 | 121.3531 | 121.5637 | -121.7697 | -121.7926
1345.9062 | 121.8521 | -61.4227 | 60.2646 | -0.075912 | 0.012405 | -0.0010147 | 0.012758 | 0.052677 | -0.012672 | 0.068184 | -61.4685 | 60.1135 | -61.5326 | -61.4868 | 59.9716 | 0.19684 | -0.041199 | 0.073242 | 60.2234 | -61.5372 | -0.10986 | -0.15106 | -0.045777 | -0.064087 | -0.29297 | -0.11444 | -0.041198 | 0.064087 | 61.3815 | 61.496 | 121.3943 | 121.5363 | -0.045777 | 121.6461 | 61.6196 | -0.11444 | 121.5363 | -0.045777 | 61.6196 | 121.3943 | 121.6461 | -121.7972 | -121.8018
1347.6562 | 121.8292 | -61.4456 | 60.2188 | -0.083542 | 0.014328 | 5.3338e-05 | 0.013185 | 0.052891 | -0.012031 | 0.06797 | -61.4548 | 60.1044 | -61.5509 | -61.5005 | 59.967 | 0.21973 | -0.027466 | 0.10529 | 60.2234 | -61.5646 | -0.10528 | -0.11444 | -0.009155 | -0.054931 | -0.25177 | -0.11902 | 0.004578 | 0.09613 | 61.4182 | 61.5509 | 121.4127 | 121.55 | -0.009155 | 121.669 | 61.6653 | -0.11902 | 121.55 | -0.009155 | 61.6653 | 121.4127 | 121.669 | -121.7697 | -121.7834
1349.3438 | 121.9803 | -61.2991 | 60.3012 | 0.00038159 | 0.0098416 | -0.0055009 | 0.0037854 | 0.051182 | -0.0092542 | 0.065621 | -61.4456 | 60.1456 | -61.4777 | -61.4731 | 60.0082 | 0.25177 | -0.004578 | 0.19684 | 60.2463 | -61.5234 | -0.17853 | -0.15564 | -0.14649 | -0.17395 | -0.29297 | -0.2243 | -0.054931 | 0.032043 | 61.2946 | 61.496 | 121.3074 | 121.4447 | -0.14649 | 121.5454 | 61.5509 | -0.2243 | 121.4447 | -0.14649 | 61.5509 | 121.3074 | 121.5454 | -121.7789 | -121.8246
1351.1094 | 121.9391 | -61.3586 | 60.2463 | 0.1606 | 0.01326 | 0.0024033 | 0.010835 | 0.054386 | -0.008827 | 0.066902 | -61.4456 | 60.0677 | -61.5143 | -61.4822 | 59.9625 | 0.16937 | -0.31128 | 0.059509 | 60.1456 | -61.6104 | -0.15564 | -0.17853 | -0.086975 | -0.1236 | -0.28381 | -0.25177 | -0.10071 | 0.068664 | 61.0474 | 61.4182 | 121.3211 | 121.4264 | -0.086975 | 121.5042 | 61.528 | -0.25177 | 121.4264 | -0.086975 | 61.528 | 121.3211 | 121.5042 | -121.7606 | -121.8567
1352.8594 | 121.9666 | -61.3953 | 60.1501 | 0.11482 | 0.011978 | -0.0031509 | 0.012758 | 0.05225 | -0.012245 | 0.067543 | -61.5784 | 60.0357 | -61.5875 | -61.615 | 59.8572 | 0.059509 | -0.1236 | -0.091553 | 60.2005 | -61.6241 | -0.19226 | -0.11444 | -0.18311 | -0.21973 | -0.29297 | -0.22888 | 0.050354 | 0.009155 | 61.2717 | 61.3037 | 121.2524 | 121.431 | -0.18311 | 121.5958 | 61.4548 | -0.22888 | 121.431 | -0.18311 | 61.4548 | 121.2524 | 121.5958 | -121.7377 | -121.7743
1354.6094 | 121.8475 | -61.4639 | 60.2188 | -0.091171 | 0.01091 | -0.00016026 | 0.011689 | 0.051182 | -0.012458 | 0.06733 | -61.4822 | 60.0906 | -61.5372 | -61.5189 | 59.9442 | 0.24719 | 0.013733 | 0.15106 | 60.2005 | -61.6058 | -0.073242 | -0.12817 | -0.018311 | -0.054932 | -0.27466 | -0.14191 | -0.018311 | 0.054931 | 61.4777 | 61.615 | 121.4081 | 121.5546 | -0.018311 | 121.6644 | 61.7111 | -0.14191 | 121.5546 | -0.018311 | 61.7111 | 121.4081 | 121.6644 | -121.756 | -121.8246
1356.2969 | 121.8933 | -61.4273 | 60.2371 | -0.17509 | 0.012405 | -0.0050735 | 0.0086988 | 0.052464 | -0.010322 | 0.067116 | -61.5051 | 60.1364 | -61.5097 | -61.5326 | 59.9487 | 0.27466 | 0.20142 | 0.20142 | 60.2692 | -61.5372 | -0.082398 | -0.10071 | -0.07782 | -0.10529 | -0.28839 | -0.10986 | 0.032043 | 0.004578 | 61.6287 | 61.6287 | 121.376 | 121.5637 | -0.07782 | 121.6965 | 61.702 | -0.10986 | 121.5637 | -0.07782 | 61.702 | 121.376 | 121.6965 | -121.7468 | -121.7743
1358.0469 | 121.9482 | -61.409 | 60.1822 | 0.17586 | 0.012405 | -0.0031509 | 0.0080578 | 0.051609 | -0.011604 | 0.066262 | -61.5601 | 60.0494 | -61.5738 | -61.5875 | 59.9121 | 0.11902 | -0.23346 | -0.032043 | 60.1639 | -61.6608 | -0.16479 | -0.13275 | -0.15106 | -0.17853 | -0.27008 | -0.25177 | -0.018311 | 0.013733 | 61.1755 | 61.377 | 121.3211 | 121.4584 | -0.15106 | 121.5729 | 61.528 | -0.25177 | 121.4584 | -0.15106 | 61.528 | 121.3211 | 121.5729 | -121.756 | -121.843
1359.7969 | 121.8521 | -61.4548 | 60.1959 | -0.16747 | 0.01091 | -0.0048599 | 0.0078442 | 0.049473 | -0.010109 | 0.06733 | -61.5051 | 60.1044 | -61.528 | -61.5143 | 59.9625 | 0.2655 | 0.086975 | 0.16937 | 60.2097 | -61.5829 | -0.073242 | -0.091553 | -0.050354 | -0.059509 | -0.23346 | -0.12817 | 0.013733 | 0.022888 | 61.5417 | 61.6241 | 121.4172 | 121.5591 | -0.050354 | 121.6644 | 61.7203 | -0.12817 | 121.5591 | -0.050354 | 61.7203 | 121.4172 | 121.6644 | -121.7239 | -121.7789
1361.5625 | 121.8613 | -61.3815 | 60.2646 | -0.15221 | 0.011337 | -0.0018693 | 0.0050672 | 0.050968 | -0.0075452 | 0.068825 | -61.4182 | 60.1044 | -61.4594 | -61.4365 | 60.0723 | 0.40741 | 0.027466 | 0.37994 | 60.2371 | -61.5189 | -0.07782 | -0.16022 | -0.036621 | -0.054931 | -0.19226 | -0.13733 | -0.027465 | 0.041199 | 61.409 | 61.7615 | 121.4539 | 121.4859 | -0.036621 | 121.6187 | 61.7889 | -0.13733 | 121.4859 | -0.036621 | 61.7889 | 121.4539 | 121.6187 | -121.7239 | -121.7834
1363.25 | 121.9894 | -61.3861 | 60.2097 | 0.053787 | 0.012832 | -0.00037386 | 0.0054944 | 0.050541 | -0.0096814 | 0.067757 | -61.5005 | 60.0266 | -61.5234 | -61.5463 | 59.9442 | 0.20599 | -0.082397 | 0.13733 | 60.1959 | -61.6013 | -0.13733 | -0.18311 | -0.11444 | -0.16022 | -0.2655 | -0.21515 | -0.013733 | 0.022888 | 61.3037 | 61.5234 | 121.3303 | 121.4127 | -0.11444 | 121.582 | 61.5921 | -0.21515 | 121.4127 | -0.11444 | 61.5921 | 121.3303 | 121.582 | -121.7331 | -121.8109
1364.9844 | 121.843 | -61.5051 | 60.1776 | -0.12932 | 0.012191 | -0.00080106 | 0.0069898 | 0.049046 | -0.0090406 | 0.065407 | -61.4868 | 60.0174 | -61.5738 | -61.496 | 59.9945 | 0.39368 | 0.064087 | 0.39368 | 60.1181 | -61.6608 | -0.068665 | -0.16022 | 0.018311 | 0.009155 | -0.18311 | -0.15564 | -0.059509 | 0.086976 | 61.5692 | 61.8988 | 121.4996 | 121.5225 | 0.018311 | 121.6232 | 61.8988 | -0.15564 | 121.5225 | 0.018311 | 61.8988 | 121.4996 | 121.6232 | -121.7514 | -121.8384
1366.7344 | 121.8475 | -62.3062 | 59.3491 | -0.068283 | 0.01091 | -0.00037386 | 0.014253 | 0.048619 | -0.013099 | 0.065834 | -62.3657 | 59.1934 | -62.4527 | -62.3978 | 59.0561 | 0.16479 | -0.059509 | 0.086975 | 59.3216 | -62.4527 | -0.14648 | -0.15564 | -0.05951 | -0.091553 | -0.29297 | -0.14648 | -0.027466 | 0.086975 | 62.2467 | 62.3932 | 121.3623 | 121.4996 | -0.05951 | 121.6278 | 62.471 | -0.14648 | 121.4996 | -0.05951 | 62.471 | 121.3623 | 121.6278 | -121.8018 | -121.8018
1368.4844 | 121.9849 | -62.8784 | 58.7448 | 0.01564 | 0.012619 | 0.00026694 | 0.0061352 | 0.049473 | -0.0075452 | 0.068611 | -63.0157 | 58.5526 | -63.0157 | -63.0295 | 58.461 | 0.14648 | -0.027466 | 0.16479 | 58.6716 | -63.1073 | -0.13733 | -0.19226 | -0.13733 | -0.15106 | -0.28381 | -0.22888 | -0.073242 | 0 | 62.851 | 63.0432 | 121.3394 | 121.431 | -0.13733 | 121.55 | 63.0249 | -0.22888 | 121.431 | -0.13733 | 63.0249 | 121.3394 | 121.55 | -121.7606 | -121.8521
1370.1719 | 121.9482 | -62.1689 | 59.4452 | 0.061417 | 0.0139 | 0.0017623 | 0.01468 | 0.050114 | -0.01139 | 0.067116 | -62.3108 | 59.3399 | -62.3154 | -62.3383 | 59.111 | 0.073242 | -0.045776 | -0.050354 | 59.4543 | -62.384 | -0.14648 | -0.10528 | -0.14191 | -0.16937 | -0.33417 | -0.21515 | 0.009156 | 0.004578 | 62.1231 | 62.1185 | 121.2799 | 121.5088 | -0.14191 | 121.6232 | 62.2421 | -0.21515 | 121.5088 | -0.14191 | 62.2421 | 121.2799 | 121.6232 | -121.7606 | -121.8292
1371.9219 | 121.8887 | -62.0041 | 59.6558 | -0.2285 | 0.013046 | -0.0063553 | 0.0093396 | 0.049473 | -0.009895 | 0.067543 | -62.0316 | 59.5688 | -62.0636 | -62.0728 | 59.3948 | 0.27924 | 0.23804 | 0.2655 | 59.7015 | -62.1552 | -0.05951 | -0.086975 | -0.027466 | -0.068665 | -0.26093 | -0.15106 | 0.045776 | 0.032044 | 62.2421 | 62.2696 | 121.3989 | 121.5729 | -0.027466 | 121.7056 | 62.2833 | -0.15106 | 121.5729 | -0.027466 | 62.2833 | 121.3989 | 121.7056 | -121.7194 | -121.8109
1373.6719 | 121.8979 | -62.0087 | 59.6649 | -0.22087 | 0.015182 | -0.0057145 | 0.0099804 | 0.049687 | -0.012245 | 0.066689 | -62.059 | 59.5734 | -62.0819 | -62.0865 | 59.4086 | 0.2655 | 0.24261 | 0.21057 | 59.7244 | -62.1231 | -0.073242 | -0.091553 | -0.050354 | -0.07782 | -0.25635 | -0.11444 | 0.059509 | 0.022888 | 62.2513 | 62.2192 | 121.4172 | 121.582 | -0.050354 | 121.7331 | 62.2742 | -0.11444 | 121.582 | -0.050354 | 62.2742 | 121.4172 | 121.7331 | -121.7468 | -121.788
1375.3594 | 121.9711 | -62.0041 | 59.5688 | 0.084305 | 0.012191 | -0.0016557 | 0.010194 | 0.052464 | -0.01139 | 0.06797 | -62.1506 | 59.4727 | -62.1735 | -62.1872 | 59.2804 | 0.059509 | -0.14648 | -0.07782 | 59.6237 | -62.2284 | -0.16937 | -0.096131 | -0.14648 | -0.18311 | -0.28839 | -0.22431 | 0.054931 | 0.022888 | 61.8576 | 61.9263 | 121.2845 | 121.4767 | -0.14648 | 121.6278 | 62.0636 | -0.22431 | 121.4767 | -0.14648 | 62.0636 | 121.2845 | 121.6278 | -121.7422 | -121.7972
1377.125 | 121.8979 | -62.1094 | 59.5322 | -0.0072479 | 0.01326 | 0.00090794 | 0.011903 | 0.05225 | -0.012886 | 0.066262 | -62.1826 | 59.4223 | -62.2147 | -62.2238 | 59.2163 | 0.13275 | -0.064087 | -0.009155 | 59.5322 | -62.2787 | -0.10529 | -0.10986 | -0.073242 | -0.11444 | -0.31586 | -0.16937 | 0 | 0.032044 | 62.0453 | 62.1002 | 121.3257 | 121.5317 | -0.073242 | 121.6415 | 62.2421 | -0.16937 | 121.5317 | -0.073242 | 62.2421 | 121.3257 | 121.6415 | -121.7468 | -121.8109
1378.8594 | 121.8475 | -62.2055 | 59.4589 | -0.075912 | 0.012832 | 0.0024033 | 0.012544 | 0.052037 | -0.012031 | 0.067116 | -62.2055 | 59.3582 | -62.2742 | -62.2421 | 59.2346 | 0.22888 | -0.022888 | 0.11444 | 59.4864 | -62.3428 | -0.068665 | -0.10071 | 0 | -0.036621 | -0.2243 | -0.13733 | 0.027466 | 0.068665 | 62.1826 | 62.3199 | 121.4401 | 121.5637 | 0 | 121.6919 | 62.4344 | -0.13733 | 121.5637 | 0 | 62.4344 | 121.4401 | 121.6919 | -121.7331 | -121.8018
1380.625 | 121.9757 | -62.1506 | 59.4452 | 0.01564 | 0.013046 | -0.0050735 | 0.0025036 | 0.050541 | -0.0092542 | 0.065834 | -62.3062 | 59.2712 | -62.2925 | -62.3428 | 59.1476 | 0.21973 | -0.022888 | 0.16479 | 59.3994 | -62.4069 | -0.14191 | -0.17395 | -0.15564 | -0.19226 | -0.29755 | -0.25635 | -0.045776 | -0.013733 | 62.1277 | 62.3154 | 121.2982 | 121.4218 | -0.15564 | 121.55 | 62.3703 | -0.25635 | 121.4218 | -0.15564 | 62.3703 | 121.2982 | 121.55 | -121.7377 | -121.8521
1382.3125 | 121.9391 | -62.2925 | 59.3124 | 0.17586 | 0.012619 | -0.0022965 | 0.0097668 | 0.052464 | -0.008827 | 0.067116 | -62.3657 | 59.1431 | -62.4344 | -62.4115 | 59.0698 | 0.14648 | -0.31586 | 0.07782 | 59.2392 | -62.5031 | -0.14191 | -0.16937 | -0.073243 | -0.11902 | -0.24262 | -0.21057 | -0.073242 | 0.068664 | 61.9766 | 62.3703 | 121.3623 | 121.4355 | -0.073243 | 121.5317 | 62.439 | -0.21057 | 121.4355 | -0.073243 | 62.439 | 121.3623 | 121.5317 | -121.7468 | -121.8155
1384.0625 | 121.9666 | -62.4023 | 59.1934 | 0.11482 | 0.013687 | -0.00058746 | 0.013185 | 0.053532 | -0.010963 | 0.068184 | -62.5259 | 59.0836 | -62.5626 | -62.5717 | 58.8867 | 0.059509 | -0.21515 | -0.07782 | 59.2163 | -62.6221 | -0.16022 | -0.10986 | -0.1236 | -0.16937 | -0.3067 | -0.21973 | 0.022889 | 0.036621 | 62.1872 | 62.3245 | 121.2891 | 121.4859 | -0.1236 | 121.6187 | 62.4619 | -0.21973 | 121.4859 | -0.1236 | 62.4619 | 121.2891 | 121.6187 | -121.756 | -121.8155
1385.8125 | 121.8475 | -62.5305 | 59.1751 | -0.17509 | 0.011551 | -0.0046463 | 0.0086988 | 0.050755 | -0.011177 | 0.066475 | -62.5214 | 59.024 | -62.5992 | -62.5442 | 58.9325 | 0.37537 | 0.11444 | 0.37537 | 59.0973 | -62.645 | -0.068664 | -0.15106 | 0.009156 | -0.013732 | -0.24261 | -0.11444 | -0.07782 | 0.07782 | 62.645 | 62.9059 | 121.463 | 121.5546 | 0.009156 | 121.6278 | 62.9059 | -0.11444 | 121.5546 | 0.009156 | 62.9059 | 121.463 | 121.6278 | -121.7743 | -121.8201
1387.4844 | 121.962 | -64.5035 | 57.0923 | 0.15297 | 0.011337 | -0.0022965 | 0.005708 | 0.050541 | -0.012245 | 0.06797 | -64.7919 | 56.7032 | -64.8468 | -64.8148 | 56.6803 | 0.064087 | -0.12817 | 0.13733 | 56.8817 | -64.8743 | -0.34332 | -0.3891 | -0.28839 | -0.31128 | -0.41199 | -0.37079 | -0.21057 | 0.054932 | 64.3753 | 64.6408 | 121.1838 | 121.2067 | -0.28839 | 121.3852 | 64.5676 | -0.37079 | 121.2067 | -0.28839 | 64.5676 | 121.1838 | 121.3852 | -121.9391 | -121.9666
1389.25 | 121.9574 | -62.677 | 58.905 | 0.10719 | 0.011551 | -0.0029373 | 0.0089124 | 0.050968 | -0.0075452 | 0.066689 | -62.8098 | 58.7219 | -62.8601 | -62.8418 | 58.6349 | 0.15564 | -0.17853 | 0.10986 | 58.8364 | -62.9105 | -0.1831 | -0.1831 | -0.13275 | -0.16479 | -0.27008 | -0.23346 | -0.068664 | 0.050354 | 62.4985 | 62.7869 | 121.312 | 121.3989 | -0.13275 | 121.5134 | 62.8326 | -0.23346 | 121.3989 | -0.13275 | 62.8326 | 121.312 | 121.5134 | -121.7651 | -121.8155
1391 | 121.9666 | -62.6678 | 58.9417 | -0.037765 | 0.01326 | 0.0028305 | 0.0086988 | 0.048832 | -0.010963 | 0.06498 | -62.7777 | 58.7723 | -62.7914 | -62.7777 | 58.6853 | 0.27924 | 0.018311 | 0.27924 | 58.8959 | -62.8967 | -0.1236 | -0.16937 | -0.10986 | -0.10986 | -0.25635 | -0.22888 | -0.045776 | 0.013733 | 62.6862 | 62.9471 | 121.3531 | 121.4401 | -0.10986 | 121.5637 | 62.9471 | -0.22888 | 121.4401 | -0.10986 | 62.9471 | 121.3531 | 121.5637 | -121.7331 | -121.8384
1392.7031 | 121.8567 | -63.2172 | 58.4564 | -0.15984 | 0.0094144 | -0.0022965 | 0.0086988 | 0.050541 | -0.010322 | 0.066689 | -63.2172 | 58.2687 | -63.2858 | -63.2309 | 58.2321 | 0.35248 | 0.10529 | 0.37994 | 58.429 | -63.3682 | -0.068665 | -0.18768 | 0 | -0.013733 | -0.2243 | -0.15106 | -0.027466 | 0.068665 | 63.3224 | 63.5971 | 121.4493 | 121.4859 | 0 | 121.6461 | 63.5696 | -0.15106 | 121.4859 | 0 | 63.5696 | 121.4493 | 121.6461 | -121.7422 | -121.8246
1394.4531 | 121.994 | -63.1302 | 58.4518 | 0.030899 | 0.011764 | -0.0022965 | 0.0082714 | 0.050541 | -0.010109 | 0.065834 | -63.2492 | 58.2779 | -63.295 | -63.2858 | 58.2047 | 0.16937 | -0.082397 | 0.13275 | 58.4381 | -63.3408 | -0.1648 | -0.17395 | -0.11902 | -0.15564 | -0.24719 | -0.21057 | -0.013733 | 0.045776 | 63.0478 | 63.2629 | 121.3348 | 121.4081 | -0.11902 | 121.5683 | 63.2996 | -0.21057 | 121.4081 | -0.11902 | 63.2996 | 121.3348 | 121.5683 | -121.7468 | -121.7926
1396.2031 | 121.875 | -63.3545 | 58.2458 | -0.19035 | 0.010696 | -0.0016557 | 0.013826 | 0.0499 | -0.011177 | 0.066902 | -63.4094 | 58.1635 | -63.4918 | -63.4369 | 58.0032 | 0.21973 | 0.10529 | 0.16479 | 58.3054 | -63.5376 | -0.13733 | -0.082398 | -0.054932 | -0.082398 | -0.24262 | -0.18311 | 0.059509 | 0.082397 | 63.4598 | 63.5193 | 121.3577 | 121.5179 | -0.054932 | 121.6599 | 63.5742 | -0.18311 | 121.5179 | -0.054932 | 63.5742 | 121.3577 | 121.6599 | -121.7377 | -121.7834
1397.9688 | 121.843 | -65.5884 | 56.0669 | -0.17509 | 0.0083462 | -0.0035783 | 0.009126 | 0.050328 | -0.010536 | 0.06797 | -65.9088 | 55.632 | -65.9866 | -65.8997 | 55.6366 | 0.31128 | 0.009155 | 0.31128 | 55.7373 | -66.0049 | -0.39825 | -0.43488 | -0.32043 | -0.31128 | -0.4303 | -0.41656 | -0.32959 | 0.07782 | 65.5975 | 65.8997 | 121.225 | 121.2204 | -0.32043 | 121.3257 | 65.8997 | -0.41656 | 121.2204 | -0.32043 | 65.8997 | 121.225 | 121.3257 | -122.0535 | -122.0718
1399.6562 | 121.8796 | -63.7848 | 57.8888 | -0.15984 | 0.0139 | -0.0040055 | 0.013826 | 0.049473 | -0.010536 | 0.064766 | -63.8168 | 57.8064 | -63.8351 | -63.8443 | 57.6141 | 0.23346 | 0.17853 | 0.20142 | 57.9208 | -63.9404 | -0.050354 | -0.082398 | -0.032043 | -0.059509 | -0.27466 | -0.15564 | 0.032043 | 0.018311 | 63.9633 | 63.9862 | 121.3989 | 121.5912 | -0.032043 | 121.7056 | 64.0182 | -0.15564 | 121.5912 | -0.032043 | 64.0182 | 121.3989 | 121.7056 | -121.7239 | -121.8292
1401.4062 | 121.8613 | -63.8809 | 57.7744 | -0.20561 | 0.010269 | -0.0042191 | 0.0065624 | 0.049687 | -0.010963 | 0.066262 | -63.8763 | 57.6324 | -63.9542 | -63.8901 | 57.5775 | 0.45319 | 0.10071 | 0.39368 | 57.7103 | -63.9999 | -0.073243 | -0.14191 | 0.004577 | -0.009156 | -0.19684 | -0.11902 | -0.064087 | 0.07782 | 63.9816 | 64.2746 | 121.4584 | 121.5134 | 0.004577 | 121.5912 | 64.3341 | -0.11902 | 121.5134 | 0.004577 | 64.3341 | 121.4584 | 121.5912 | -121.7285 | -121.7743
1403.1094 | 121.9666 | -70.079 | 51.4664 | 0.14534 | 0.015609 | -0.00080106 | 0.011476 | 0.050541 | -0.01139 | 0.06733 | -70.1797 | 51.3428 | -70.2896 | -70.2026 | 51.2878 | -0.71869 | -0.3891 | -0.064087 | 51.416 | -70.3354 | -0.21057 | -0.1236 | -0.10071 | -0.1236 | -0.17853 | -0.25635 | -0.050354 | 0.10986 | 69.6899 | 70.015 | 121.3669 | 121.4218 | -0.10071 | 121.4951 | 69.3604 | -0.25635 | 121.4218 | -0.10071 | 69.3604 | 121.3669 | 121.4951 | -121.756 | -121.8018
1404.8125 | 121.9849 | -64.2105 | 57.399 | 0.10719 | 0.013687 | -0.0020829 | 0.012758 | 0.051823 | -0.0096814 | 0.069679 | -64.3158 | 57.3257 | -64.3478 | -64.3478 | 57.1152 | 0.10529 | -0.14191 | -0.07782 | 57.399 | -64.4073 | -0.13733 | -0.073242 | -0.10529 | -0.13733 | -0.28381 | -0.19684 | 0 | 0.032043 | 64.0686 | 64.1327 | 121.3257 | 121.5363 | -0.10529 | 121.6095 | 64.3158 | -0.19684 | 121.5363 | -0.10529 | 64.3158 | 121.3257 | 121.6095 | -121.7468 | -121.8063
1406.5625 | 121.9208 | -71.2784 | 50.3036 | 0.15297 | 0.012619 | -0.0014419 | 0.0080578 | 0.051396 | -0.0096814 | 0.065834 | -71.4066 | 50.0565 | -71.5256 | -71.4478 | 50.0336 | -0.67749 | -0.36621 | -0.022888 | 50.1434 | -71.6217 | -0.24719 | -0.24719 | -0.12817 | -0.16937 | -0.27008 | -0.34332 | -0.16022 | 0.11902 | 70.9122 | 71.2555 | 121.3119 | 121.3348 | -0.12817 | 121.4218 | 70.6009 | -0.34332 | 121.3348 | -0.12817 | 70.6009 | 121.3119 | 121.4218 | -121.8292 | -121.9254
1408.3125 | 121.875 | -66.5039 | 55.2017 | -0.24376 | 0.012191 | -0.0010147 | 0.009126 | 0.048405 | -0.011818 | 0.066902 | -65.8676 | 55.7007 | -65.9317 | -65.8951 | 55.5634 | 0.56305 | 0.26093 | 0.36621 | 55.8151 | -66.0141 | 0.5722 | 0.49896 | 0.63629 | 0.60882 | 0.36163 | 0.48981 | 0.6134 | 0.064087 | 66.7648 | 66.8701 | 122.0673 | 122.2046 | 0.63629 | 122.319 | 67.067 | 0.48981 | 122.2046 | 0.63629 | 67.067 | 122.0673 | 122.319 | -121.1334 | -121.2158
1409.9844 | 121.9437 | -66.4627 | 55.1285 | 0.1606 | 0.01326 | 0.00069434 | 0.0078442 | 0.051396 | -0.010322 | 0.065834 | -66.4032 | 55.0415 | -66.5039 | -66.4398 | 55.0369 | 0.38452 | -0.20142 | 0.16022 | 55.1788 | -66.5451 | -0.041198 | -0.086975 | 0.05951 | 0.022889 | -0.091553 | -0.082397 | 0.050354 | 0.10071 | 66.2613 | 66.6229 | 121.4996 | 121.5042 | 0.05951 | 121.6415 | 66.8472 | -0.082397 | 121.5042 | 0.05951 | 66.8472 | 121.4996 | 121.6415 | -121.6324 | -121.6736
1411.7344 | 121.8842 | -66.5863 | 55.0735 | -0.23613 | 0.011764 | -0.00080106 | 0.009126 | 0.050114 | -0.009895 | 0.066048 | -66.5314 | 55.0323 | -66.5909 | -66.5909 | 54.8904 | 0.62714 | 0.23346 | 0.31128 | 55.1514 | -66.655 | -0.004577 | -0.041198 | 0.054932 | -0.004577 | -0.1831 | -0.068664 | 0.07782 | 0.059509 | 66.8198 | 66.8976 | 121.4767 | 121.6187 | 0.054932 | 121.7377 | 67.2134 | -0.068664 | 121.6187 | 0.054932 | 67.2134 | 121.4767 | 121.7377 | -121.6644 | -121.7285
1413.4375 | 121.9391 | -67.6071 | 53.9795 | -0.091171 | 0.01091 | -0.0050735 | 0.0080578 | 0.048619 | -0.008186 | 0.066902 | -66.9846 | 54.5471 | -67.0303 | -67.0029 | 54.4968 | -0.53101 | -0.19684 | 0.09613 | 54.6112 | -67.1768 | 0.57678 | 0.56763 | 0.62256 | 0.60425 | 0.51727 | 0.4303 | 0.63171 | 0.045776 | 67.4103 | 67.7032 | 122.1039 | 122.1542 | 0.62256 | 122.2183 | 67.0761 | 0.4303 | 122.1542 | 0.62256 | 67.0761 | 122.1039 | 122.2183 | -121.0098 | -121.1563
1415.1875 | 121.8567 | -66.4124 | 55.2887 | -0.16747 | 0.011764 | -0.0031509 | 0.013826 | 0.049687 | -0.011177 | 0.065834 | -66.3986 | 55.188 | -66.4536 | -66.4124 | 55.0186 | 0.16937 | 0.064087 | 0.17853 | 55.2933 | -66.5085 | -0.041198 | -0.10071 | 0.013733 | 0 | -0.27008 | -0.09613 | 0.004578 | 0.054931 | 66.4764 | 66.5909 | 121.431 | 121.6003 | 0.013733 | 121.7056 | 66.5817 | -0.09613 | 121.6003 | 0.013733 | 66.5817 | 121.431 | 121.7056 | -121.7422 | -121.7972
1416.9375 | 121.9482 | -66.5817 | 54.9911 | 0.17586 | 0.011764 | 0.0021895 | 0.012544 | 0.052037 | -0.01075 | 0.069252 | -66.6916 | 54.8538 | -66.7557 | -66.7191 | 54.7531 | 0.013733 | -0.2655 | -0.036621 | 54.9774 | -66.774 | -0.17395 | -0.13733 | -0.10986 | -0.13733 | -0.23804 | -0.19226 | -0.013733 | 0.064087 | 66.3162 | 66.5451 | 121.3348 | 121.4355 | -0.10986 | 121.5591 | 66.5955 | -0.19226 | 121.4355 | -0.10986 | 66.5955 | 121.3348 | 121.5591 | -121.7468 | -121.7651
1418.6875 | 121.8613 | -66.6595 | 55.0049 | -0.18272 | 0.011551 | -0.0057145 | 0.0080578 | 0.050968 | -0.010536 | 0.068825 | -66.7007 | 54.776 | -66.7511 | -66.6321 | 54.8584 | 0.27008 | 0.10071 | 0.33417 | 54.9774 | -66.7648 | -0.091553 | -0.22888 | -0.041199 | 0.027466 | -0.14648 | -0.10529 | -0.027466 | 0.050354 | 66.7603 | 66.9937 | 121.5179 | 121.4355 | -0.041199 | 121.637 | 66.9296 | -0.10529 | 121.4355 | -0.041199 | 66.9296 | 121.5179 | 121.637 | -121.756 | -121.7697
1420.3906 | 121.8292 | -68.1839 | 53.4714 | -0.12932 | 0.012405 | -0.0027237 | 0.01468 | 0.051823 | -0.011604 | 0.064339 | -68.1702 | 53.3936 | -68.248 | -68.2022 | 53.2608 | 0.52185 | 0.13733 | 0.2655 | 53.4897 | -68.3075 | -0.064087 | -0.07782 | 0.013733 | -0.01831 | -0.21057 | -0.1236 | 0.01831 | 0.07782 | 68.3212 | 68.4494 | 121.4447 | 121.5775 | 0.013733 | 121.6736 | 68.7057 | -0.1236 | 121.5775 | 0.013733 | 68.7057 | 121.4447 | 121.6736 | -121.7194 | -121.7789
1422.1406 | 121.8384 | -68.1015 | 53.5629 | -0.20561 | 0.010482 | -0.0059281 | 0.0072034 | 0.049687 | -0.012031 | 0.065407 | -68.1061 | 53.334 | -68.2205 | -68.1244 | 53.3707 | 0.2243 | 0.068665 | 0.36621 | 53.4988 | -68.2434 | -0.11902 | -0.22888 | -0.004578 | -0.022889 | -0.19226 | -0.14191 | -0.064087 | 0.11444 | 68.1702 | 68.4677 | 121.4722 | 121.4355 | -0.004578 | 121.6003 | 68.3258 | -0.14191 | 121.4355 | -0.004578 | 68.3258 | 121.4722 | 121.6003 | -121.7834 | -121.8063
1423.8281 | 121.962 | -69.5297 | 52.0203 | 0.091934 | 0.011337 | -0.0029373 | 0.014253 | 0.050114 | -0.013099 | 0.065834 | -69.6625 | 51.9333 | -69.6991 | -69.7128 | 51.7548 | -0.13275 | -0.20599 | -0.10529 | 52.0157 | -69.7723 | -0.16937 | -0.086975 | -0.13275 | -0.18311 | -0.2655 | -0.24262 | -0.004578 | 0.036621 | 69.3237 | 69.4244 | 121.2845 | 121.463 | -0.13275 | 121.5454 | 69.397 | -0.24262 | 121.463 | -0.13275 | 69.397 | 121.2845 | 121.5454 | -121.7194 | -121.7926
1425.5781 | 121.907 | -69.9188 | 51.7044 | -0.15221 | 0.012405 | -0.0040055 | 0.012117 | 0.0499 | -0.010322 | 0.068825 | -69.9829 | 51.59 | -70.0607 | -70.0241 | 51.4664 | 0.10071 | 0.22888 | 0.24261 | 51.6678 | -70.1797 | -0.14191 | -0.11444 | -0.064087 | -0.10529 | -0.23804 | -0.26093 | -0.036621 | 0.07782 | 70.1477 | 70.1614 | 121.3852 | 121.5088 | -0.064087 | 121.5866 | 70.0195 | -0.26093 | 121.5088 | -0.064087 | 70.0195 | 121.3852 | 121.5866 | -121.7651 | -121.8842
1427.2656 | 121.8384 | -70.2209 | 51.4343 | -0.091171 | 0.011337 | 0.00026694 | 0.01233 | 0.053959 | -0.014595 | 0.066689 | -70.1706 | 51.3474 | -70.285 | -70.2164 | 51.2512 | 0.022888 | -0.050354 | 0.09613 | 51.4938 | -70.3125 | -0.064087 | -0.086975 | 0.050354 | 0.004577 | -0.1831 | -0.091553 | 0.059509 | 0.11444 | 70.1706 | 70.3171 | 121.4722 | 121.5683 | 0.050354 | 121.7148 | 70.2438 | -0.091553 | 121.5683 | 0.050354 | 70.2438 | 121.4722 | 121.7148 | -121.7194 | -121.7468
1429.0156 | 121.9254 | -70.5231 | 51.0635 | 0.17586 | 0.011337 | -0.00058746 | 0.0095532 | 0.051182 | -0.0083996 | 0.068184 | -70.5414 | 50.9216 | -70.6421 | -70.5872 | 50.9125 | -0.032043 | -0.31128 | 0.059509 | 51.0361 | -70.7245 | -0.11902 | -0.14191 | -0.018311 | -0.064087 | -0.15106 | -0.20142 | -0.027466 | 0.10071 | 70.2118 | 70.5826 | 121.4355 | 121.4447 | -0.018311 | 121.5591 | 70.491 | -0.20142 | 121.4447 | -0.018311 | 70.491 | 121.4355 | 121.5591 | -121.7056 | -121.788
1430.7031 | 121.9803 | -71.0678 | 50.5142 | -0.0072479 | 0.010696 | 0.0021895 | 0.0069898 | 0.049046 | -0.0086132 | 0.066475 | -71.1639 | 50.4044 | -71.2189 | -71.2097 | 50.3174 | -0.004578 | -0.050354 | 0.14648 | 50.4822 | -71.3196 | -0.15106 | -0.10986 | -0.09613 | -0.14191 | -0.19684 | -0.25177 | -0.032043 | 0.054932 | 71.0175 | 71.2143 | 121.3852 | 121.4722 | -0.09613 | 121.55 | 71.0632 | -0.25177 | 121.4722 | -0.09613 | 71.0632 | 121.3852 | 121.55 | -121.7331 | -121.8338
1432.4531 | 121.9482 | -72.5464 | 49.0448 | 0.17586 | 0.01091 | -0.0037919 | 0.011476 | 0.052677 | -0.012458 | 0.06797 | -72.5555 | 48.9029 | -72.6746 | -72.5555 | 48.912 | -0.091553 | -0.31128 | -0.027466 | 49.0128 | -72.7478 | -0.12817 | -0.14191 | -0.009155 | -0.009155 | -0.13275 | -0.20142 | -0.032044 | 0.11902 | 72.2351 | 72.5189 | 121.4584 | 121.4493 | -0.009155 | 121.5591 | 72.4548 | -0.20142 | 121.4493 | -0.009155 | 72.4548 | 121.4584 | 121.5591 | -121.7194 | -121.7926
1434.1875 | 121.8384 | -71.2234 | 50.4639 | -0.21324 | 0.011764 | -0.0035783 | 0.0061352 | 0.050755 | -0.010322 | 0.067543 | -71.196 | 50.2487 | -71.2967 | -71.2189 | 50.2762 | 0.16022 | 0.064087 | 0.38452 | 50.3815 | -71.4249 | -0.073242 | -0.21515 | 0.027466 | 0.004578 | -0.18768 | -0.20142 | -0.082397 | 0.10071 | 71.2875 | 71.608 | 121.4996 | 121.4722 | 0.027466 | 121.6049 | 71.3837 | -0.20142 | 121.4722 | 0.027466 | 71.3837 | 121.4996 | 121.6049 | -121.7606 | -121.8887
1435.9375 | 121.8887 | -71.9421 | 49.7177 | -0.32768 | 0.013046 | -0.0037919 | 0.010194 | 0.049687 | -0.0094678 | 0.066475 | -71.489 | 50.0381 | -71.5622 | -71.6766 | 49.7314 | 0.20142 | 0.2655 | 0.30212 | 50.0015 | -71.846 | 0.37994 | 0.32044 | 0.45319 | 0.2655 | 0.013733 | 0.096131 | 0.28381 | 0.073242 | 72.2076 | 72.2443 | 121.6736 | 121.9803 | 0.45319 | 121.9437 | 72.1436 | 0.096131 | 121.9803 | 0.45319 | 72.1436 | 121.6736 | 121.9437 | -121.2799 | -121.5637
1437.7031 | 121.8613 | -71.4249 | 50.2121 | -0.022507 | 0.013687 | 5.3338e-05 | 0.014253 | 0.051609 | -0.0094678 | 0.066689 | -71.3242 | 50.235 | -71.4157 | -71.2967 | 50.1526 | -0.064087 | -0.091553 | 0.022888 | 50.3723 | -71.4523 | 0.009156 | 0.022888 | 0.10071 | 0.12817 | -0.059509 | -0.027466 | 0.16022 | 0.091552 | 71.3333 | 71.4478 | 121.5775 | 121.6599 | 0.10071 | 121.7972 | 71.3608 | -0.027466 | 121.6599 | 0.10071 | 71.3608 | 121.5775 | 121.7972 | -121.6278 | -121.6644
1439.3906 | 121.843 | -71.4523 | 50.2121 | -0.21324 | 0.011551 | -0.0046463 | 0.0069898 | 0.050755 | -0.010109 | 0.063912 | -71.4157 | 50.0748 | -71.5027 | -71.4478 | 50.0519 | 0.11444 | 0.041199 | 0.35248 | 50.1663 | -71.608 | -0.050354 | -0.13733 | 0.036622 | 0.004578 | -0.16022 | -0.15564 | -0.045776 | 0.086976 | 71.4935 | 71.8048 | 121.5042 | 121.5271 | 0.036622 | 121.6187 | 71.5668 | -0.15564 | 121.5271 | 0.036622 | 71.5668 | 121.5042 | 121.6187 | -121.7148 | -121.8201
1441.1406 | 121.8658 | -72.5784 | 49.0768 | -0.060654 | 0.0139 | -0.0020829 | 0.014253 | 0.051609 | -0.012031 | 0.067543 | -72.496 | 48.9853 | -72.6517 | -72.5372 | 48.9624 | 0.073242 | 0.004578 | 0.14191 | 49.1776 | -72.6242 | -0.073242 | -0.091552 | 0.082397 | 0.041199 | -0.11444 | -0.045777 | 0.10071 | 0.15564 | 72.583 | 72.7203 | 121.5408 | 121.5637 | 0.082397 | 121.756 | 72.6517 | -0.045777 | 121.5637 | 0.082397 | 72.6517 | 121.5408 | 121.756 | -121.7285 | -121.701
1442.8438 | 121.9437 | -72.8165 | 48.7518 | 0.19112 | 0.013473 | -0.0014419 | 0.0097668 | 0.052891 | -0.0075452 | 0.068184 | -73.0453 | 48.468 | -73.1506 | -72.9904 | 48.4955 | -0.045776 | -0.26093 | 0.027466 | 48.6511 | -73.1369 | -0.33417 | -0.28381 | -0.22888 | -0.17395 | -0.25635 | -0.32044 | -0.10071 | 0.10529 | 72.5555 | 72.8439 | 121.3119 | 121.2845 | -0.22888 | 121.4676 | 72.7707 | -0.32044 | 121.2845 | -0.22888 | 72.7707 | 121.3119 | 121.4676 | -121.9025 | -121.8887
1444.6094 | 121.9757 | -72.7844 | 48.8113 | 0.10719 | 0.0139 | -0.0035783 | 0.012117 | 0.052464 | -0.009895 | 0.068398 | -72.8897 | 48.7061 | -72.9538 | -72.9401 | 48.5504 | -0.15106 | -0.13733 | -0.10071 | 48.8159 | -73.0133 | -0.16937 | -0.10529 | -0.10528 | -0.15564 | -0.26093 | -0.22888 | 0.004578 | 0.064087 | 72.6471 | 72.6837 | 121.3348 | 121.4905 | -0.10528 | 121.6003 | 72.6334 | -0.22888 | 121.4905 | -0.10528 | 72.6334 | 121.3348 | 121.6003 | -121.7651 | -121.8246
1446.3594 | 121.8567 | -73.1003 | 48.5596 | -0.2285 | 0.012405 | -0.0031509 | 0.0052808 | 0.051396 | -0.0096814 | 0.068398 | -73.32 | 48.1796 | -73.3841 | -73.3017 | 48.1705 | -0.064087 | -0.013733 | 0.28839 | 48.262 | -73.4894 | -0.28381 | -0.37994 | -0.21973 | -0.20142 | -0.3891 | -0.3891 | -0.29755 | 0.064087 | 73.0865 | 73.3887 | 121.2708 | 121.2799 | -0.21973 | 121.3623 | 73.0362 | -0.3891 | 121.2799 | -0.21973 | 73.0362 | 121.2708 | 121.3623 | -121.9437 | -122.0489
1448.0469 | 121.9757 | -73.8007 | 47.7859 | 0.076676 | 0.014541 | -0.0048599 | 0.012117 | 0.050114 | -0.009895 | 0.06797 | -73.9746 | 47.6303 | -74.0524 | -73.97 | 47.5388 | -0.19226 | -0.12817 | -0.082397 | 47.8226 | -73.9563 | -0.25177 | -0.15564 | -0.17395 | -0.16937 | -0.24719 | -0.15564 | 0.036621 | 0.07782 | 73.6725 | 73.7183 | 121.3394 | 121.431 | -0.17395 | 121.6232 | 73.6084 | -0.15564 | 121.431 | -0.17395 | 73.6084 | 121.3394 | 121.6232 | -121.8384 | -121.7422
1449.7812 | 121.9208 | -74.1531 | 47.4426 | 0.16823 | 0.0098416 | -0.0027237 | 0.007417 | 0.05225 | -0.008186 | 0.068825 | -74.4049 | 47.0764 | -74.4781 | -74.3729 | 47.0078 | -0.44861 | -0.59967 | -0.21057 | 47.0901 | -74.7162 | -0.32501 | -0.36621 | -0.25177 | -0.21973 | -0.43488 | -0.56305 | -0.35248 | 0.073242 | 73.5535 | 73.9426 | 121.1609 | 121.2296 | -0.25177 | 121.2433 | 73.7045 | -0.56305 | 121.2296 | -0.25177 | 73.7045 | 121.1609 | 121.2433 | -121.9208 | -122.1588
1451.5312 | 121.9757 | -74.8077 | 46.756 | -0.0072479 | 0.011764 | -0.0020829 | 0.0052808 | 0.050328 | -0.0077588 | 0.065834 | -74.8581 | 46.637 | -74.9359 | -74.9313 | 46.6003 | -0.09613 | -0.082397 | 0.14648 | 46.7194 | -75.0412 | -0.12817 | -0.11902 | -0.050354 | -0.1236 | -0.15564 | -0.23346 | -0.036621 | 0.07782 | 74.7253 | 74.9542 | 121.4081 | 121.4447 | -0.050354 | 121.5271 | 74.7116 | -0.23346 | 121.4447 | -0.050354 | 74.7116 | 121.4081 | 121.5271 | -121.6919 | -121.7972
1453.2344 | 121.8292 | -75.9567 | 45.694 | -0.091171 | 0.012832 | 0.0019759 | 0.012544 | 0.050328 | -0.01139 | 0.066048 | -75.9659 | 45.5429 | -76.0941 | -75.9933 | 45.4834 | -0.13733 | -0.082397 | 0.091553 | 45.6482 | -76.1627 | -0.13733 | -0.15106 | -0.009155 | -0.036621 | -0.21057 | -0.20599 | -0.045777 | 0.12817 | 75.8743 | 76.0483 | 121.4401 | 121.4996 | -0.009155 | 121.6049 | 75.8194 | -0.20599 | 121.4996 | -0.009155 | 75.8194 | 121.4401 | 121.6049 | -121.788 | -121.8567
1454.9844 | 121.9437 | -76.0483 | 45.5521 | -0.053024 | 0.013046 | -0.0063553 | 0.0031446 | 0.04755 | -0.0094678 | 0.067116 | -76.1536 | 45.3323 | -76.2222 | -76.1948 | 45.3003 | -0.068665 | -0.027466 | 0.24261 | 45.4285 | -76.3321 | -0.17395 | -0.21973 | -0.10529 | -0.14648 | -0.25177 | -0.28381 | -0.1236 | 0.068665 | 76.0208 | 76.2909 | 121.3486 | 121.3806 | -0.10529 | 121.4767 | 75.9796 | -0.28381 | 121.3806 | -0.10529 | 75.9796 | 121.3486 | 121.4767 | -121.7743 | -121.8842
1456.7344 | 121.8613 | -76.712 | 44.8975 | -0.20561 | 0.014328 | 5.3338e-05 | 0.012971 | 0.049473 | -0.013313 | 0.066262 | -76.9226 | 44.6136 | -77.0599 | -76.9867 | 44.5084 | -0.16937 | -0.036621 | 0.045776 | 44.6915 | -77.1515 | -0.3479 | -0.28381 | -0.21057 | -0.27466 | -0.3891 | -0.43945 | -0.20599 | 0.13733 | 76.6754 | 76.7578 | 121.2204 | 121.3257 | -0.21057 | 121.4035 | 76.5427 | -0.43945 | 121.3257 | -0.21057 | 76.5427 | 121.2204 | 121.4035 | -121.9574 | -122.0489
1458.4688 | 121.9711 | -77.1973 | 44.3802 | 0.038529 | 0.011337 | -0.0018693 | 0.0069898 | 0.050114 | -0.011604 | 0.065193 | -77.2568 | 44.2383 | -77.3254 | -77.2934 | 44.22 | -0.19226 | -0.14648 | 0.086975 | 44.3573 | -77.4033 | -0.12817 | -0.14191 | -0.059509 | -0.09613 | -0.16022 | -0.20599 | -0.022888 | 0.068664 | 77.0508 | 77.2842 | 121.4172 | 121.4355 | -0.059509 | 121.5546 | 77.005 | -0.20599 | 121.4355 | -0.059509 | 77.005 | 121.4172 | 121.5546 | -121.7056 | -121.7834
1460.1719 | 121.8887 | -76.4053 | 45.2454 | -0.2285 | 0.012619 | -0.0035783 | 0.012117 | 0.050968 | -0.0090406 | 0.066689 | -76.442 | 45.1355 | -76.5289 | -76.4832 | 45.0027 | -0.091553 | 0.16022 | 0.16479 | 45.2545 | -76.5427 | -0.1236 | -0.10986 | -0.036622 | -0.07782 | -0.24261 | -0.13733 | 0.009156 | 0.086975 | 76.5656 | 76.5701 | 121.4081 | 121.5408 | -0.036622 | 121.6599 | 76.3138 | -0.13733 | 121.5408 | -0.036622 | 76.3138 | 121.4081 | 121.6599 | -121.7743 | -121.788
1461.875 | 121.9254 | -78.4882 | 43.0573 | -0.15221 | 0.01091 | -0.0052873 | 0.0089124 | 0.050968 | -0.011818 | 0.066689 | -77.5497 | 43.9545 | -77.7008 | -77.7054 | 43.6935 | -0.1831 | 0.21057 | 0.21515 | 44.0048 | -77.8473 | 0.78735 | 0.89722 | 0.93841 | 0.78278 | 0.63629 | 0.64087 | 0.94757 | 0.15106 | 78.6987 | 78.7033 | 122.1817 | 122.4426 | 0.93841 | 122.493 | 78.3051 | 0.64087 | 122.4426 | 0.93841 | 78.3051 | 122.1817 | 122.493 | -120.7581 | -120.9045
1463.6406 | 121.8979 | -77.33 | 44.2841 | -0.25139 | 0.011978 | -0.0048599 | 0.011903 | 0.049687 | -0.011177 | 0.06733 | -77.3895 | 44.1742 | -77.4994 | -77.4261 | 44.046 | -0.10529 | 0.18768 | 0.19684 | 44.3298 | -77.5223 | -0.16937 | -0.10986 | -0.059509 | -0.09613 | -0.23804 | -0.19226 | 0.045776 | 0.10986 | 77.5177 | 77.5269 | 121.376 | 121.5042 | -0.059509 | 121.6599 | 77.2247 | -0.19226 | 121.5042 | -0.059509 | 77.2247 | 121.376 | 121.6599 | -121.7834 | -121.8063
1465.3438 | 121.9849 | -77.9205 | 43.6203 | 0.046158 | 0.011123 | -0.0040055 | 0.011476 | 0.053532 | -0.01139 | 0.069466 | -77.9572 | 43.5928 | -78.0579 | -78.0853 | 43.4235 | -0.29755 | -0.14648 | -0.11902 | 43.6935 | -78.1357 | -0.13733 | -0.027466 | -0.036621 | -0.1648 | -0.19684 | -0.21515 | 0.073242 | 0.10071 | 77.774 | 77.8015 | 121.344 | 121.5134 | -0.036621 | 121.6141 | 77.623 | -0.21515 | 121.5134 | -0.036621 | 77.623 | 121.344 | 121.6141 | -121.6782 | -121.756
1467.0781 | 121.8201 | -78.1082 | 43.5425 | -0.098801 | 0.012405 | -0.00080106 | 0.014039 | 0.052891 | -0.012245 | 0.066475 | -78.0853 | 43.4097 | -78.241 | -78.1265 | 43.3548 | -0.064087 | -0.036621 | 0.10529 | 43.5562 | -78.2776 | -0.13275 | -0.13275 | 0.022888 | -0.018311 | -0.18768 | -0.16937 | 0.013733 | 0.15564 | 78.0716 | 78.2135 | 121.463 | 121.5179 | 0.022888 | 121.6644 | 78.0441 | -0.16937 | 121.5179 | 0.022888 | 78.0441 | 121.463 | 121.6644 | -121.7834 | -121.8201
1468.7656 | 121.9025 | -78.273 | 43.3594 | -0.24376 | 0.01326 | -0.0031509 | 0.0072034 | 0.051396 | -0.010109 | 0.070107 | -78.3096 | 43.2678 | -78.4149 | -78.3554 | 43.1534 | -0.12817 | 0.1831 | 0.16937 | 43.3594 | -78.4561 | -0.14191 | -0.091553 | -0.036621 | -0.082398 | -0.20599 | -0.18311 | 0 | 0.10529 | 78.4561 | 78.4424 | 121.4264 | 121.5408 | -0.036621 | 121.6324 | 78.1448 | -0.18311 | 121.5408 | -0.036621 | 78.1448 | 121.4264 | 121.6324 | -121.7743 | -121.8155
1470.4844 | 121.8246 | -78.3829 | 43.2724 | -0.21324 | 0.011978 | -0.0044327 | 0.0065624 | 0.050114 | -0.011177 | 0.066689 | -78.2776 | 43.158 | -78.3875 | -78.3188 | 43.2037 | -0.022888 | 0.032043 | 0.33417 | 43.2587 | -78.479 | -0.004577 | -0.11444 | 0.10529 | 0.064087 | -0.068665 | -0.09613 | -0.013733 | 0.10986 | 78.4149 | 78.717 | 121.5866 | 121.5408 | 0.10529 | 121.6415 | 78.36 | -0.09613 | 121.5408 | 0.10529 | 78.36 | 121.5866 | 121.6415 | -121.6599 | -121.7514
1472.2031 | 121.843 | -77.124 | 44.5541 | -0.11406 | 0.01326 | -0.0055009 | 0.013398 | 0.050328 | -0.01075 | 0.066048 | -77.3254 | 44.2062 | -77.3941 | -77.4765 | 43.9728 | 0.032043 | 0.004578 | 0.1831 | 44.2337 | -77.5314 | -0.27008 | -0.3479 | -0.20142 | -0.35248 | -0.58136 | -0.40741 | -0.32043 | 0.068665 | 77.1286 | 77.3071 | 121.0968 | 121.3303 | -0.20142 | 121.3577 | 77.1561 | -0.40741 | 121.3303 | -0.20142 | 77.1561 | 121.0968 | 121.3577 | -121.9482 | -122.0856
1473.9219 | 121.8384 | -77.9572 | 43.6844 | -0.19798 | 0.012405 | 0.00048074 | 0.0061352 | 0.049473 | -0.008186 | 0.067757 | -77.8931 | 43.5333 | -78.0396 | -77.9388 | 43.5791 | -0.054932 | -0.018311 | 0.30212 | 43.5837 | -78.1677 | -0.082398 | -0.15106 | 0.064087 | 0.01831 | -0.10529 | -0.21057 | -0.10071 | 0.14648 | 77.9388 | 78.2593 | 121.5363 | 121.4905 | 0.064087 | 121.5408 | 77.9022 | -0.21057 | 121.4905 | 0.064087 | 77.9022 | 121.5363 | 121.5408 | -121.7239 | -121.8521
1475.6562 | 121.9528 | -78.1586 | 43.4052 | 0.13008 | 0.012832 | 0.0026169 | 0.011689 | 0.051609 | -0.0083996 | 0.066902 | -78.2684 | 43.2861 | -78.3554 | -78.3371 | 43.1671 | -0.32044 | -0.27924 | -0.10986 | 43.3685 | -78.4561 | -0.19684 | -0.11902 | -0.10986 | -0.17853 | -0.23804 | -0.29755 | -0.036621 | 0.086975 | 77.8793 | 78.0487 | 121.3257 | 121.4447 | -0.10986 | 121.5271 | 77.8381 | -0.29755 | 121.4447 | -0.10986 | 77.8381 | 121.3257 | 121.5271 | -121.7606 | -121.8613
1477.3594 | 121.875 | -77.5452 | 44.1101 | -0.25139 | 0.012191 | -0.0067825 | 0.0076306 | 0.049473 | -0.010536 | 0.067116 | -77.8473 | 43.6707 | -77.948 | -77.8748 | 43.6249 | -0.086975 | 0.14191 | 0.28381 | 43.7759 | -78.0441 | -0.40283 | -0.43945 | -0.30212 | -0.32959 | -0.48523 | -0.49896 | -0.33417 | 0.10071 | 77.6871 | 77.829 | 121.17 | 121.2158 | -0.30212 | 121.3211 | 77.4582 | -0.49896 | 121.2158 | -0.30212 | 77.4582 | 121.17 | 121.3211 | -122.0581 | -122.1542
1479.0625 | 121.9757 | -77.124 | 44.4626 | 0.00038159 | 0.013687 | -0.0010147 | 0.0059216 | 0.051182 | -0.010109 | 0.065193 | -77.298 | 44.2245 | -77.3254 | -77.298 | 44.2703 | -0.13275 | -0.073242 | 0.15106 | 44.3985 | -77.3575 | -0.20142 | -0.23804 | -0.17395 | -0.17395 | -0.19226 | -0.23346 | -0.064086 | 0.027465 | 77.0508 | 77.2751 | 121.3943 | 121.3486 | -0.17395 | 121.5225 | 76.9913 | -0.23346 | 121.3486 | -0.17395 | 76.9913 | 121.3943 | 121.5225 | -121.788 | -121.8201
1480.8125 | 121.8246 | -76.3412 | 45.3461 | -0.12169 | 0.010482 | -0.0059281 | 0.008485 | 0.0499 | -0.010963 | 0.066048 | -76.2314 | 45.2087 | -76.3641 | -76.2497 | 45.2454 | -0.004578 | -0.009155 | 0.32501 | 45.314 | -76.4877 | -0.022888 | -0.13733 | 0.10986 | 0.091553 | -0.10071 | -0.14648 | -0.032043 | 0.13275 | 76.3321 | 76.6663 | 121.5866 | 121.55 | 0.10986 | 121.6553 | 76.3367 | -0.14648 | 121.55 | 0.10986 | 76.3367 | 121.5866 | 121.6553 | -121.7102 | -121.8338
1482.5938 | 121.8796 | -76.8723 | 44.7281 | 0.00038159 | 0.012191 | -0.0020829 | 0.015748 | 0.051609 | -0.01374 | 0.06797 | -76.918 | 44.5908 | -77.0782 | -76.8402 | 44.5587 | -0.48065 | -0.25635 | -0.16022 | 44.7922 | -77.0233 | -0.20599 | -0.13733 | -0.045777 | 0.032043 | -0.16937 | -0.15106 | 0.064087 | 0.16022 | 76.6159 | 76.712 | 121.431 | 121.463 | -0.045777 | 121.6644 | 76.3916 | -0.15106 | 121.463 | -0.045777 | 76.3916 | 121.431 | 121.6644 | -121.8063 | -121.7514
1484.2969 | 121.8933 | -76.918 | 44.6777 | -0.15984 | 0.011123 | -0.0018693 | 0.0059216 | 0.050755 | -0.01139 | 0.067543 | -76.886 | 44.5587 | -77.0187 | -76.9089 | 44.5862 | 0.064087 | -0.036621 | 0.32501 | 44.6915 | -77.1011 | -0.10071 | -0.11902 | 0.032044 | 0.009155 | -0.091552 | -0.1831 | 0.013733 | 0.13275 | 76.8814 | 77.243 | 121.5042 | 121.4767 | 0.032044 | 121.6095 | 76.9821 | -0.1831 | 121.4767 | 0.032044 | 76.9821 | 121.5042 | 121.6095 | -121.6965 | -121.7789
1486.0469 | 121.8842 | -77.3209 | 44.2841 | -0.23613 | 0.011337 | -0.00058746 | 0.012117 | 0.048832 | -0.012886 | 0.068398 | -77.3392 | 44.2062 | -77.4124 | -77.3941 | 44.101 | -0.20142 | 0.1236 | 0.10986 | 44.3665 | -77.4719 | -0.091553 | -0.07782 | -0.01831 | -0.073242 | -0.18311 | -0.15106 | 0.082397 | 0.073243 | 77.4445 | 77.4307 | 121.4218 | 121.5271 | -0.01831 | 121.6873 | 77.1194 | -0.15106 | 121.5271 | -0.01831 | 77.1194 | 121.4218 | 121.6873 | -121.6965 | -121.756
1487.7344 | 121.962 | -77.1103 | 44.4489 | 0.046158 | 0.012405 | -0.00016026 | 0.0065624 | 0.052037 | -0.0090406 | 0.06797 | -76.8173 | 44.6732 | -76.8951 | -76.9272 | 44.6091 | -0.20142 | -0.16479 | 0.073242 | 44.7784 | -77.0096 | 0.21515 | 0.2243 | 0.29297 | 0.18311 | 0.16022 | 0.10071 | 0.32959 | 0.07782 | 76.9455 | 77.1835 | 121.7194 | 121.7834 | 0.29297 | 121.8887 | 76.9089 | 0.10071 | 121.7834 | 0.29297 | 76.9089 | 121.7194 | 121.8887 | -121.344 | -121.4584
1489.4062 | 121.8567 | -77.2797 | 44.3481 | -0.022507 | 0.014114 | -0.00037386 | 0.013826 | 0.052891 | -0.014381 | 0.066048 | -77.2888 | 44.2108 | -77.4399 | -77.3575 | 44.1101 | -0.19684 | -0.10529 | -0.004578 | 44.3481 | -77.4811 | -0.16022 | -0.13733 | -0.009155 | -0.07782 | -0.23804 | -0.20142 | 0 | 0.15106 | 77.1744 | 77.2751 | 121.3898 | 121.4905 | -0.009155 | 121.6278 | 77.0828 | -0.20142 | 121.4905 | -0.009155 | 77.0828 | 121.3898 | 121.6278 | -121.788 | -121.8292
1491.0938 | 121.8796 | -77.0462 | 44.5908 | -0.21324 | 0.014114 | -0.0042191 | 0.0099804 | 0.0499 | -0.011604 | 0.06733 | -77.0645 | 44.5129 | -77.1652 | -77.1286 | 44.3573 | -0.09613 | 0.19226 | 0.18768 | 44.5724 | -77.243 | -0.11902 | -0.07782 | -0.01831 | -0.082397 | -0.23346 | -0.19684 | -0.01831 | 0.10071 | 77.2385 | 77.2339 | 121.4035 | 121.5591 | -0.01831 | 121.6187 | 76.9501 | -0.19684 | 121.5591 | -0.01831 | 76.9501 | 121.4035 | 121.6187 | -121.756 | -121.8338
1492.7656 | 121.843 | -76.918 | 44.7418 | -0.15221 | 0.014755 | -0.0040055 | 0.0050672 | 0.050755 | -0.011177 | 0.065193 | -76.8723 | 44.5541 | -77.005 | -76.9043 | 44.5908 | 0.004578 | 0 | 0.3479 | 44.6503 | -77.124 | -0.086975 | -0.18768 | 0.045777 | 0.013733 | -0.15106 | -0.20599 | -0.091552 | 0.13275 | 76.918 | 77.2659 | 121.5088 | 121.4722 | 0.045777 | 121.5683 | 76.9226 | -0.20599 | 121.4722 | 0.045777 | 76.9226 | 121.5088 | 121.5683 | -121.7468 | -121.8658
1494.4531 | 121.962 | -75.4349 | 46.1792 | 0.076676 | 0.011551 | -0.0048599 | 0.013612 | 0.052677 | -0.01139 | 0.067757 | -75.4898 | 46.0739 | -75.6134 | -75.5493 | 45.932 | -0.25635 | -0.20142 | -0.10529 | 46.1975 | -75.6409 | -0.17853 | -0.10528 | -0.054932 | -0.11444 | -0.24719 | -0.20599 | 0.018311 | 0.1236 | 75.2335 | 75.3296 | 121.3669 | 121.5088 | -0.054932 | 121.6324 | 75.1785 | -0.20599 | 121.5088 | -0.054932 | 75.1785 | 121.3669 | 121.6324 | -121.7926 | -121.8201
1496.1406 | 121.875 | -72.8622 | 48.793 | -0.23613 | 0.012832 | -0.0044327 | 0.0099804 | 0.050541 | -0.010322 | 0.067116 | -72.9172 | 48.7106 | -72.9721 | -72.9218 | 48.5596 | 0.032043 | 0.26093 | 0.25177 | 48.8159 | -73.0041 | -0.10986 | -0.082398 | -0.054931 | -0.059509 | -0.23346 | -0.14191 | 0.022888 | 0.054932 | 73.1232 | 73.114 | 121.4218 | 121.5729 | -0.054931 | 121.6782 | 72.8943 | -0.14191 | 121.5729 | -0.054931 | 72.8943 | 121.4218 | 121.6782 | -121.7651 | -121.7972
1497.8281 | 121.843 | -71.9238 | 49.7314 | -0.2285 | 0.011123 | -0.0048599 | 0.0086988 | 0.049687 | -0.01139 | 0.066048 | -71.8964 | 49.5758 | -72.0016 | -71.9238 | 49.5438 | 0.041199 | 0.13733 | 0.31586 | 49.7223 | -72.0566 | -0.07782 | -0.15564 | 0.027466 | 0 | -0.18768 | -0.13275 | -0.009155 | 0.10529 | 72.0612 | 72.2397 | 121.4676 | 121.4996 | 0.027466 | 121.6461 | 71.965 | -0.13275 | 121.4996 | 0.027466 | 71.965 | 121.4676 | 121.6461 | -121.7331 | -121.788
1499.5781 | 121.8155 | -71.3562 | 50.2625 | -0.13695 | 0.012191 | -0.0025101 | 0.012117 | 0.05225 | -0.013099 | 0.064766 | -71.3287 | 50.1572 | -71.4478 | -71.4111 | 50.0656 | -0.009155 | 0.013733 | 0.13733 | 50.2808 | -71.5393 | -0.091553 | -0.10529 | 0.027466 | -0.054932 | -0.19684 | -0.18311 | 0.018311 | 0.11902 | 71.3699 | 71.4935 | 121.4218 | 121.5134 | 0.027466 | 121.637 | 71.347 | -0.18311 | 121.5134 | 0.027466 | 71.347 | 121.4218 | 121.637 | -121.7102 | -121.8018
1501.2656 | 121.8338 | -71.5988 | 50.0427 | -0.12169 | 0.0098416 | -0.0063553 | 0.0042126 | 0.050114 | -0.012245 | 0.066902 | -71.5897 | 49.8596 | -71.7087 | -71.5988 | 49.8825 | 0.09613 | 0.013733 | 0.33875 | 49.9603 | -71.7819 | -0.10986 | -0.18311 | 0.009155 | 0 | -0.16022 | -0.1831 | -0.082398 | 0.11902 | 71.6125 | 71.9376 | 121.4813 | 121.4584 | 0.009155 | 121.5591 | 71.6949 | -0.1831 | 121.4584 | 0.009155 | 71.6949 | 121.4813 | 121.5591 | -121.7514 | -121.8246
1503.0156 | 121.9116 | -71.1823 | 50.3998 | 0.18349 | 0.012619 | -0.0014419 | 0.012758 | 0.050968 | -0.010109 | 0.068184 | -71.228 | 50.2808 | -71.3104 | -71.2555 | 50.2029 | -0.054932 | -0.28839 | -0.013733 | 50.3677 | -71.3791 | -0.12817 | -0.11902 | -0.045776 | -0.073242 | -0.19684 | -0.19684 | -0.032043 | 0.082398 | 70.8939 | 71.1685 | 121.3852 | 121.463 | -0.045776 | 121.55 | 71.1273 | -0.19684 | 121.463 | -0.045776 | 71.1273 | 121.3852 | 121.55 | -121.7102 | -121.7789
1504.8281 | 121.8338 | -70.3308 | 51.3062 | -0.12932 | 0.012191 | -0.0048599 | 0.0046398 | 0.048405 | -0.0096814 | 0.065834 | -70.2667 | 51.178 | -70.3537 | -70.2759 | 51.1871 | 0.24261 | 0.032043 | 0.37079 | 51.2833 | -70.4636 | -0.022888 | -0.12817 | 0.064087 | 0.054932 | -0.11902 | -0.13275 | -0.022888 | 0.086975 | 70.3629 | 70.7016 | 121.5179 | 121.5088 | 0.064087 | 121.6141 | 70.5734 | -0.13275 | 121.5088 | 0.064087 | 70.5734 | 121.5179 | 121.6141 | -121.6599 | -121.7697
1506.5781 | 121.9208 | -69.1635 | 52.446 | 0.091934 | 0.012191 | -0.0012283 | 0.011903 | 0.050541 | -0.01139 | 0.067116 | -69.0353 | 52.4048 | -69.1589 | -69.1818 | 52.3087 | -0.022888 | -0.32044 | 0.022888 | 52.4551 | -69.2688 | 0.004577 | -0.041199 | 0.12817 | -0.018311 | -0.13733 | -0.10529 | 0.009155 | 0.1236 | 68.8431 | 69.1864 | 121.4722 | 121.5683 | 0.12817 | 121.6187 | 69.1406 | -0.10529 | 121.5683 | 0.12817 | 69.1406 | 121.4722 | 121.6187 | -121.6049 | -121.7148
1508.3438 | 121.9162 | -69.6991 | 51.8921 | 0.099564 | 0.0094144 | -0.0052873 | 0.010621 | 0.050114 | -0.0094678 | 0.068184 | -69.7495 | 51.6953 | -69.8502 | -69.7678 | 51.6861 | -0.004578 | -0.24719 | 0.086975 | 51.8005 | -69.8914 | -0.15106 | -0.19684 | -0.050354 | -0.068664 | -0.20599 | -0.19226 | -0.091553 | 0.10071 | 69.4519 | 69.7861 | 121.3852 | 121.3943 | -0.050354 | 121.4996 | 69.6945 | -0.19226 | 121.3943 | -0.050354 | 69.6945 | 121.3852 | 121.4996 | -121.7422 | -121.7834
1510.0938 | 121.8979 | -69.9326 | 51.6541 | 0.1606 | 0.011551 | -0.0018693 | 0.010621 | 0.048619 | -0.009895 | 0.065621 | -69.9417 | 51.4847 | -70.0562 | -69.9966 | 51.4755 | 0.018311 | -0.32959 | 0.054932 | 51.5762 | -70.1385 | -0.1236 | -0.16937 | -0.009155 | -0.064087 | -0.17853 | -0.20599 | -0.07782 | 0.11444 | 69.603 | 69.9875 | 121.4081 | 121.4172 | -0.009155 | 121.5088 | 69.9509 | -0.20599 | 121.4172 | -0.009155 | 69.9509 | 121.4081 | 121.5088 | -121.7102 | -121.7926
1511.7812 | 121.843 | -68.6188 | 53.0273 | -0.19798 | 0.012619 | -0.0040055 | 0.013398 | 0.048619 | -0.014808 | 0.065834 | -68.6554 | 52.8946 | -68.7149 | -68.6691 | 52.7115 | 0.050354 | 0.07782 | 0.17395 | 52.977 | -68.7973 | -0.096131 | -0.13275 | -0.036622 | -0.050354 | -0.31586 | -0.17853 | -0.050354 | 0.059509 | 68.6966 | 68.7927 | 121.3303 | 121.5134 | -0.036622 | 121.5958 | 68.6691 | -0.17853 | 121.5134 | -0.036622 | 68.6691 | 121.3303 | 121.5958 | -121.7422 | -121.8246
1513.5312 | 121.8979 | -67.2546 | 54.3137 | 0.13771 | 0.010696 | 0.0017623 | 0.0097668 | 0.0499 | -0.011604 | 0.067543 | -67.2775 | 54.1718 | -67.3599 | -67.3096 | 54.1443 | 0.11902 | -0.31586 | 0.064087 | 54.2587 | -67.4377 | -0.10529 | -0.14191 | -0.022888 | -0.054931 | -0.16937 | -0.1831 | -0.054932 | 0.082397 | 66.9388 | 67.3187 | 121.3989 | 121.4264 | -0.022888 | 121.5134 | 67.3737 | -0.1831 | 121.4264 | -0.022888 | 67.3737 | 121.3989 | 121.5134 | -121.6736 | -121.7514
1515.2812 | 122.0078 | -83.6792 | 37.8845 | 0.01564 | 0.01326 | -0.0057145 | 0.0061352 | 0.04691 | -0.008827 | 0.066048 | -82.988 | 38.4888 | -83.0841 | -83.0612 | 38.4293 | -1.2772 | -0.37537 | -0.16937 | 38.5345 | -83.226 | 0.59509 | 0.60425 | 0.69122 | 0.61798 | 0.54474 | 0.45319 | 0.65002 | 0.09613 | 83.3038 | 83.5098 | 122.1085 | 122.168 | 0.69122 | 122.2137 | 82.402 | 0.45319 | 122.168 | 0.69122 | 82.402 | 122.1085 | 122.2137 | -120.9686 | -121.1105
1516.9688 | 121.7743 | -82.0908 | 39.6103 | -0.28954 | 0.011764 | -0.0040055 | 0.0097668 | 0.048619 | -0.0075452 | 0.06498 | -82.4982 | 38.7817 | -82.7271 | -82.576 | 39.1296 | 1.3916 | 0.6546 | 0.55389 | 39.1571 | -82.7133 | -0.63629 | -0.82855 | -0.40741 | -0.48523 | -0.48065 | -0.62256 | -0.45319 | 0.22888 | 82.7454 | 82.6447 | 121.2204 | 120.8725 | -0.40741 | 121.2479 | 83.4824 | -0.62256 | 120.8725 | -0.40741 | 83.4824 | 121.2204 | 121.2479 | -122.3373 | -122.3236
1518.7188 | 121.8201 | -53.4531 | 68.0649 | 0.13008 | 0.013046 | 0.0011215 | 0.010835 | 0.050968 | -0.011818 | 0.06498 | -53.5034 | 67.923 | -53.5767 | -53.5675 | 67.8955 | 1.1673 | -0.16479 | 0.13275 | 67.9733 | -53.6865 | -0.1236 | -0.14191 | -0.050354 | -0.11444 | -0.16937 | -0.23346 | -0.091552 | 0.073242 | 53.2883 | 53.5858 | 121.3486 | 121.376 | -0.050354 | 121.4264 | 54.6204 | -0.23346 | 121.376 | -0.050354 | 54.6204 | 121.3486 | 121.4264 | -121.6415 | -121.7514
1520.4688 | 121.6736 | -64.2517 | 57.1243 | -0.20561 | 0.012832 | 5.3338e-05 | 0.011476 | 0.049473 | -0.0096814 | 0.068184 | -59.2758 | 62.2467 | -59.3857 | -59.4955 | 61.7661 | 0.33875 | 0.26093 | 0.1831 | 62.0865 | -59.61 | 4.866 | 5.1224 | 4.9759 | 4.7562 | 4.6417 | 4.6417 | 4.9622 | 0.10986 | 64.5126 | 64.4348 | 126.0178 | 126.4984 | 4.9759 | 126.3382 | 64.5905 | 4.6417 | 126.4984 | 4.9759 | 64.5905 | 126.0178 | 126.3382 | -116.51 | -116.7343
1522.2188 | 121.4813 | -61.4685 | 60.3378 | -0.13695 | 0.013046 | -0.0063553 | 0.0063488 | 0.050541 | -0.0096814 | 0.06498 | -59.5963 | 61.4273 | -59.8251 | -59.9762 | 61.3174 | 1.3412 | 0.28381 | 0.35706 | 61.3586 | -60.3241 | 1.6434 | 1.0895 | 1.8723 | 1.4923 | 0.97961 | 1.1444 | 1.0208 | 0.22888 | 61.7523 | 61.8256 | 122.7859 | 122.8958 | 1.8723 | 122.8271 | 62.8098 | 1.1444 | 122.8958 | 1.8723 | 62.8098 | 122.7859 | 122.8271 | -120.163 | -120.6619
1523.9062 | 121.5546 | -60.7315 | 60.5118 | -0.12169 | 0.011551 | -0.0012283 | 0.009126 | 0.045628 | -0.008827 | 0.064553 | -62.2238 | 59.7244 | -61.8851 | -62.4115 | 59.4406 | 0.050354 | -0.086975 | -0.29297 | 59.436 | -62.1368 | -1.1536 | -0.78735 | -1.4923 | -1.68 | -1.0712 | -1.4053 | -1.0757 | -0.33874 | 60.6445 | 60.4385 | 120.1721 | 120.4559 | -1.4923 | 120.1675 | 60.7819 | -1.4053 | 120.4559 | -1.4923 | 60.7819 | 120.1721 | 120.1675 | -122.3969 | -122.6486
1525.6406 | 121.5591 | -65.0803 | 56.0349 | 0.084305 | 0.012191 | -0.0044327 | 0.013398 | 0.050114 | -0.010536 | 0.067757 | -66.4627 | 55.1834 | -66.3391 | -66.2109 | 54.9728 | 3.4103 | 1.8951 | 1.6708 | 55.2841 | -66.3574 | -1.2589 | -0.85144 | -1.3824 | -1.1307 | -1.062 | -1.2772 | -0.75073 | -0.1236 | 66.9754 | 66.7511 | 120.0531 | 120.2637 | -1.3824 | 120.3644 | 68.4906 | -1.2772 | 120.2637 | -1.3824 | 68.4906 | 120.0531 | 120.3644 | -122.374 | -122.3923
1527.3281 | 121.5591 | -69.7952 | 51.3474 | 0.11482 | 0.011551 | -0.0037919 | 0.011689 | 0.050755 | -0.009895 | 0.066262 | -66.4902 | 54.8584 | -66.362 | -65.4648 | 54.4098 | 0.23804 | -0.75073 | -1.9135 | 53.8879 | -68.1931 | 3.4332 | 3.511 | 3.3051 | 4.3304 | 3.0624 | 1.6022 | 2.5406 | -0.12817 | 69.0445 | 67.8818 | 124.205 | 124.6536 | 3.3051 | 123.6832 | 70.0333 | 1.6022 | 124.6536 | 3.3051 | 70.0333 | 124.205 | 123.6832 | -117.7094 | -119.5404
1529.0781 | 121.5363 | -62.1231 | 59.0286 | 0.13008 | 0.011551 | -0.0016557 | 0.011476 | 0.051609 | -0.010109 | 0.066262 | -62.3886 | 58.7082 | -62.5305 | -62.6862 | 58.493 | -0.1236 | -0.054932 | -0.068665 | 58.7585 | -62.6175 | -0.40741 | -0.32043 | -0.2655 | -0.56305 | -0.53558 | -0.49439 | -0.27008 | 0.14191 | 62.0682 | 62.0544 | 120.6162 | 120.8313 | -0.2655 | 120.8817 | 61.9995 | -0.49439 | 120.8313 | -0.2655 | 61.9995 | 120.6162 | 120.8817 | -121.5591 | -121.6461
1530.8125 | 121.4035 | -60.1685 | 60.9695 | 0.18349 | 0.012619 | -0.0029373 | 0.0063488 | 0.052464 | -0.011177 | 0.067116 | -59.198 | 62.0819 | -59.1385 | -60.1456 | 60.8643 | -0.62256 | -1.387 | -1.1856 | 61.0931 | -60.2142 | 1.03 | 1.1124 | 0.97046 | 0.022888 | -0.10529 | -0.045776 | 0.1236 | -0.059509 | 58.7814 | 58.9828 | 121.0327 | 122.2504 | 0.97046 | 121.2616 | 59.5459 | -0.045776 | 122.2504 | 0.97046 | 59.5459 | 121.0327 | 121.2616 | -120.108 | -121.1838
1532.5 | 121.5317 | -0.56763 | 120.8908 | 0.091934 | 0.011978 | -0.0057145 | 0.0063488 | 0.049046 | -0.011177 | 0.06733 | -0.43945 | 120.6894 | -0.63629 | -0.37079 | 120.2774 | 2.449 | 0.13733 | 0.43945 | 120.8359 | -0.69122 | -0.068665 | -0.20142 | 0.12817 | 0.19684 | -0.6134 | -0.1236 | -0.054932 | 0.19684 | 0.70496 | 1.0071 | 120.845 | 121.257 | 0.12817 | 121.4035 | 3.0167 | -0.1236 | 121.257 | 0.12817 | 3.0167 | 120.845 | 121.4035 | -121.5271 | -121.582
1534.25 | 121.6919 | -0.51727 | 121.0373 | 0.061417 | 0.0085598 | -0.0050735 | 0.0069898 | 0.047978 | -0.0090406 | 0.066262 | -0.44861 | 120.813 | -0.60883 | -0.36163 | 120.4147 | 2.1057 | 0.15106 | 0.37079 | 121.0281 | -0.64087 | -0.091553 | -0.2243 | 0.068665 | 0.15564 | -0.62256 | -0.1236 | -0.009155 | 0.16022 | 0.66834 | 0.88806 | 120.932 | 121.3303 | 0.068665 | 121.5454 | 2.623 | -0.1236 | 121.3303 | 0.068665 | 2.623 | 120.932 | 121.5454 | -121.6461 | -121.6782
1535.9375 | 121.6095 | -0.65002 | 121.019 | -0.053024 | 0.012191 | -0.0063553 | 0.01468 | 0.049473 | -0.012245 | 0.065407 | -0.54016 | 120.7993 | -0.75531 | -0.46234 | 120.3369 | 2.0325 | 0.25177 | 0.33875 | 121.0052 | -0.76446 | -0.10529 | -0.21973 | 0.10986 | 0.18768 | -0.68207 | -0.11444 | -0.013733 | 0.21515 | 0.90179 | 0.98877 | 120.9869 | 121.4493 | 0.10986 | 121.6553 | 2.6825 | -0.11444 | 121.4493 | 0.10986 | 2.6825 | 120.9869 | 121.6553 | -121.7743 | -121.7834
1537.625 | 121.637 | -0.6546 | 121.0236 | -0.022507 | 0.011123 | -0.0057145 | 0.013398 | 0.050541 | -0.011177 | 0.06797 | -0.56305 | 120.8405 | -0.71869 | -0.48065 | 120.3552 | 1.9592 | 0.23804 | 0.3067 | 121.0556 | -0.77362 | -0.064087 | -0.18311 | 0.091553 | 0.17395 | -0.66833 | -0.11902 | 0.032043 | 0.15564 | 0.89264 | 0.9613 | 121.0098 | 121.4951 | 0.091553 | 121.7102 | 2.6138 | -0.11902 | 121.4951 | 0.091553 | 2.6138 | 121.0098 | 121.7102 | -121.7422 | -121.7972
1539.3906 | 121.7697 | -0.65918 | 120.9549 | 0.038529 | 0.011764 | -0.0044327 | 0.0067762 | 0.050541 | -0.0094678 | 0.065621 | -0.61798 | 120.7809 | -0.77362 | -0.54016 | 120.3415 | 1.9089 | 0.16937 | 0.35706 | 120.9869 | -0.8194 | -0.11444 | -0.17395 | 0.041199 | 0.11902 | -0.6134 | -0.16022 | 0.032043 | 0.15564 | 0.82855 | 1.0162 | 121.0007 | 121.4401 | 0.041199 | 121.6461 | 2.5681 | -0.16022 | 121.4401 | 0.041199 | 2.5681 | 121.0007 | 121.6461 | -121.7285 | -121.7743
1541.1406 | 121.8292 | -5.7495 | 115.6952 | -0.0072479 | 0.011764 | -0.0016557 | 0.005708 | 0.052037 | -0.0083996 | 0.066902 | -5.9692 | 115.3748 | -6.1432 | -5.896 | 114.9902 | 1.8173 | 0.29755 | 0.52185 | 115.6723 | -6.0608 | -0.39368 | -0.32043 | -0.21973 | -0.14648 | -0.70496 | -0.31128 | -0.022888 | 0.17395 | 6.0471 | 6.2714 | 120.7397 | 121.1243 | -0.21973 | 121.4218 | 7.5668 | -0.31128 | 121.1243 | -0.21973 | 7.5668 | 120.7397 | 121.4218 | -121.8384 | -121.756
1542.8438 | 121.8155 | -7.37 | 114.1708 | 0.069046 | 0.014541 | -0.0061417 | 0.0086988 | 0.05225 | -0.010109 | 0.066689 | -7.1503 | 114.3356 | -7.2006 | -7.1182 | 113.7772 | 0.98877 | -0.16479 | 0.032043 | 114.3585 | -7.3746 | 0.16937 | 0.16479 | 0.21973 | 0.25177 | -0.39368 | -0.004578 | 0.18768 | 0.050354 | 7.2052 | 7.402 | 121.1472 | 121.7056 | 0.21973 | 121.7285 | 8.3588 | -0.004578 | 121.7056 | 0.21973 | 8.3588 | 121.1472 | 121.7285 | -121.3715 | -121.5454
1544.6094 | 121.6782 | -1.3962 | 120.2499 | -0.17509 | 0.013046 | -0.0076371 | 0.014894 | 0.049046 | -0.013099 | 0.065834 | -1.4053 | 120.0577 | -1.5656 | -1.2863 | 119.5312 | 1.9867 | 0.43488 | 0.42572 | 120.2454 | -1.5839 | -0.16937 | -0.19226 | -0.009155 | 0.10986 | -0.71869 | -0.18768 | -0.004578 | 0.16022 | 1.8311 | 1.8219 | 120.9274 | 121.4539 | -0.009155 | 121.6415 | 3.3829 | -0.18768 | 121.4539 | -0.009155 | 3.3829 | 120.9274 | 121.6415 | -121.8155 | -121.8338
1546.3438 | 121.7422 | -1.7532 | 119.8654 | 0.11482 | 0.010269 | -0.0027237 | 0.011476 | 0.051182 | -0.013099 | 0.06797 | -1.6205 | 119.7006 | -1.8082 | -1.5198 | 119.3253 | 1.8402 | -0.064087 | 0.25635 | 119.9249 | -1.8265 | -0.054932 | -0.16479 | 0.13275 | 0.23346 | -0.54016 | -0.073242 | 0.05951 | 0.18768 | 1.6891 | 2.0096 | 121.0785 | 121.4539 | 0.13275 | 121.6782 | 3.5934 | -0.073242 | 121.4539 | 0.13275 | 3.5934 | 121.0785 | 121.6782 | -121.6736 | -121.6919
1548.0938 | 121.6141 | -8.812 | 113.8321 | 0.19112 | 0.011551 | -0.0044327 | 0.011262 | 0.051609 | -0.011604 | 0.063698 | -9.3109 | 112.088 | -9.4666 | -8.9951 | 111.5845 | 1.6525 | 0.23804 | 0.46234 | 112.4405 | -9.2651 | -0.6546 | -1.7441 | -0.49896 | -0.1831 | -2.2476 | -0.45319 | -1.3916 | 0.15564 | 9.05 | 9.2743 | 120.3964 | 120.9 | -0.49896 | 121.2524 | 10.4645 | -0.45319 | 120.9 | -0.49896 | 10.4645 | 120.3964 | 121.2524 | -123.2986 | -123.0972
1549.7812 | 121.6599 | -12.0895 | 109.4421 | -0.053024 | 0.0087734 | -0.0074235 | 0.007417 | 0.0499 | -0.0075452 | 0.066689 | -11.1557 | 110.2066 | -11.1694 | -11.3892 | 109.5245 | 0.76904 | -0.68207 | -0.28381 | 110.1608 | -11.3525 | 0.9201 | 0.76447 | 0.93384 | 0.70038 | 0.082397 | 0.737 | 0.71869 | 0.013733 | 11.4075 | 11.8057 | 121.6141 | 122.2961 | 0.93384 | 122.2504 | 12.8586 | 0.737 | 122.2961 | 0.93384 | 12.8586 | 121.6141 | 122.2504 | -120.6116 | -120.7947
1551.5156 | 121.6507 | -1.7258 | 119.7922 | 0.30556 | 0.010696 | -0.0042191 | 0.011476 | 0.05225 | -0.012458 | 0.064125 | -1.6891 | 119.2017 | -2.4811 | -1.5106 | 119.2978 | 2.0004 | 0.14191 | 0.45776 | 119.8517 | -1.7258 | -0.75531 | -0.59051 | 0.036621 | 0.21515 | -0.49438 | 0 | 0.05951 | 0.79193 | 1.8677 | 2.1835 | 121.0236 | 120.9274 | 0.036621 | 121.5775 | 3.7262 | 0 | 120.9274 | 0.036621 | 3.7262 | 121.0236 | 121.5775 | -122.2733 | -121.5179
1553.2656 | 121.6049 | -0.5127 | 121.1288 | -0.21324 | 0.011337 | -0.0059281 | 0.0086988 | 0.049259 | -0.01139 | 0.065193 | -0.61798 | 120.7077 | -0.75531 | -0.87433 | 119.9478 | 1.8036 | 0.39825 | 0.76904 | 120.7855 | -1.0986 | -0.24262 | -0.42114 | -0.10529 | -0.36163 | -1.181 | -0.58594 | -0.34332 | 0.13733 | 0.91095 | 1.2817 | 120.4605 | 121.2204 | -0.10529 | 121.2982 | 2.3163 | -0.58594 | 121.2204 | -0.10529 | 2.3163 | 120.4605 | 121.2982 | -121.8842 | -122.2275
1554.9688 | 121.6232 | -0.48981 | 121.1655 | -0.12169 | 0.012191 | -0.0074235 | 0.015535 | 0.052037 | -0.012886 | 0.066262 | -0.39368 | 121.0236 | -0.59509 | -0.29297 | 120.5154 | 1.973 | 0.29297 | 0.3891 | 121.2067 | -0.59967 | -0.10529 | -0.14191 | 0.09613 | 0.19684 | -0.65002 | -0.10986 | 0.041199 | 0.20142 | 0.78278 | 0.87891 | 121.0052 | 121.5134 | 0.09613 | 121.6965 | 2.4628 | -0.10986 | 121.5134 | 0.09613 | 2.4628 | 121.0052 | 121.6965 | -121.7606 | -121.7651
1556.7188 | 121.6461 | -0.62256 | 121.0236 | -0.10643 | 0.011764 | -0.0046463 | 0.012544 | 0.051609 | -0.01139 | 0.067543 | -0.51727 | 120.9183 | -0.70953 | -0.45776 | 120.3918 | 1.9089 | 0.22888 | 0.3479 | 121.0602 | -0.75073 | -0.086975 | -0.10529 | 0.10529 | 0.16479 | -0.63171 | -0.12817 | 0.036621 | 0.19226 | 0.85144 | 0.97046 | 121.0144 | 121.5408 | 0.10529 | 121.6827 | 2.5314 | -0.12817 | 121.5408 | 0.10529 | 2.5314 | 121.0144 | 121.6827 | -121.7331 | -121.7743
1558.4844 | 121.6599 | -0.64545 | 121.0739 | -0.20561 | 0.011337 | -0.0061417 | 0.0069898 | 0.049046 | -0.010963 | 0.06498 | -0.50354 | 120.8908 | -0.68207 | -0.36163 | 120.4971 | 2.1332 | 0.32044 | 0.6134 | 121.0098 | -0.71869 | -0.036621 | -0.18311 | 0.14191 | 0.28381 | -0.57678 | -0.073242 | -0.064087 | 0.17853 | 0.96588 | 1.2589 | 121.1426 | 121.5363 | 0.14191 | 121.6553 | 2.7786 | -0.073242 | 121.5363 | 0.14191 | 2.7786 | 121.1426 | 121.6553 | -121.756 | -121.7926
1560.25 | 121.6278 | -3.9688 | 117.7917 | -0.15984 | 0.010696 | -0.0016557 | 0.0072034 | 0.0499 | -0.0096814 | 0.067757 | -3.7445 | 117.572 | -4.0283 | -3.7491 | 117.16 | 1.8127 | 0.47607 | 0.7782 | 117.8101 | -3.9688 | -0.059509 | -0.21973 | 0.2243 | 0.21973 | -0.63171 | 0 | 0.018311 | 0.28381 | 4.4449 | 4.747 | 121.1288 | 121.5408 | 0.2243 | 121.7789 | 5.7816 | 0 | 121.5408 | 0.2243 | 5.7816 | 121.1288 | 121.7789 | -121.8201 | -121.7606
1561.9531 | 121.6919 | -3.0029 | 118.5974 | -0.18272 | 0.01091 | -0.0035783 | 0.014039 | 0.050755 | -0.010109 | 0.066475 | -2.9251 | 118.4875 | -3.0441 | -2.9022 | 117.778 | 1.5427 | 0.25177 | 0.32044 | 118.7027 | -3.1403 | -0.041198 | -0.10986 | 0.07782 | 0.10071 | -0.8194 | -0.13733 | 0.10529 | 0.11902 | 3.2547 | 3.3234 | 120.7809 | 121.4905 | 0.07782 | 121.7056 | 4.5456 | -0.13733 | 121.4905 | 0.07782 | 4.5456 | 120.7809 | 121.7056 | -121.6415 | -121.7377
1563.7031 | 121.7056 | -5.4016 | 116.2125 | -0.10643 | 0.013687 | -0.0025101 | 0.015107 | 0.051396 | -0.010322 | 0.066689 | -4.4632 | 116.7252 | -5.0262 | -5.0766 | 116.0065 | 1.7899 | 0.009155 | 0.050354 | 116.6016 | -5.1727 | 0.37537 | 0.5127 | 0.93841 | 0.32501 | -0.20599 | 0.22888 | 0.3891 | 0.56305 | 5.4108 | 5.452 | 121.4081 | 122.1268 | 0.93841 | 122.0032 | 7.1915 | 0.22888 | 122.1268 | 0.93841 | 7.1915 | 121.4081 | 122.0032 | -121.2387 | -121.3852
1565.4688 | 121.6827 | -1.6388 | 120.0348 | -0.13695 | 0.013473 | -0.0052873 | 0.0072034 | 0.047337 | -0.009895 | 0.067757 | -1.8082 | 119.4626 | -2.2842 | -2.2659 | 119.4717 | 2.9663 | 1.2817 | 1.2222 | 120.0577 | -1.9226 | -0.64545 | -0.5722 | -0.16937 | -0.62714 | -0.56305 | -0.28381 | 0.022888 | 0.47607 | 2.9205 | 2.861 | 121.1105 | 121.1014 | -0.16937 | 121.6965 | 4.6051 | -0.28381 | 121.1014 | -0.16937 | 4.6051 | 121.1105 | 121.6965 | -122.319 | -121.9574
1567.2188 | 121.6599 | -16.713 | 104.6539 | 0.13008 | 0.010269 | -0.0040055 | 0.0089124 | 0.053318 | -0.011818 | 0.065621 | -14.9734 | 106.4301 | -14.8636 | -14.4562 | 106.2149 | 1.1032 | -0.27008 | 0.009155 | 106.691 | -14.8453 | 1.8494 | 1.7761 | 1.7395 | 2.2568 | 1.561 | 1.8677 | 2.037 | -0.10986 | 16.4429 | 16.7221 | 122.9279 | 123.143 | 1.7395 | 123.4039 | 17.8162 | 1.8677 | 123.143 | 1.7395 | 17.8162 | 122.9279 | 123.4039 | -119.5175 | -119.4992
1568.9688 | 121.6873 | -3.2043 | 118.4052 | -0.26665 | 0.010482 | -0.0080643 | 0.0082714 | 0.048405 | -0.010536 | 0.063698 | -3.1174 | 118.2587 | -3.241 | -3.0075 | 117.7872 | 1.8494 | 0.46234 | 0.48523 | 118.4784 | -3.2684 | -0.036621 | -0.14648 | 0.086975 | 0.19684 | -0.61798 | -0.064087 | 0.073243 | 0.1236 | 3.6667 | 3.6896 | 120.9915 | 121.463 | 0.086975 | 121.6827 | 5.0537 | -0.064087 | 121.463 | 0.086975 | 5.0537 | 120.9915 | 121.6827 | -121.6461 | -121.6736
1570.6562 | 121.6278 | -5.7999 | 115.741 | -0.15984 | 0.012832 | -0.0080643 | 0.012544 | 0.049473 | -0.011604 | 0.067543 | -5.2963 | 116.1484 | -5.3879 | -5.1819 | 115.6403 | 1.7578 | 0.32044 | 0.38452 | 116.2949 | -5.4245 | 0.41199 | 0.40741 | 0.50354 | 0.61798 | -0.10071 | 0.37537 | 0.55389 | 0.091552 | 6.1203 | 6.1844 | 121.4401 | 121.9482 | 0.50354 | 122.0947 | 7.5577 | 0.37537 | 121.9482 | 0.50354 | 7.5577 | 121.4401 | 122.0947 | -121.1288 | -121.1655
1572.4062 | 121.6507 | -9.1461 | 112.1933 | 0.1606 | 0.015396 | -0.0055009 | 0.010408 | 0.05225 | -0.0094678 | 0.066902 | -8.7708 | 112.5183 | -8.9081 | -8.8898 | 111.7676 | 1.1261 | -0.091553 | 0.12817 | 112.5046 | -9.1141 | 0.23804 | 0.32501 | 0.37537 | 0.25635 | -0.42572 | 0.032043 | 0.31128 | 0.13733 | 9.0546 | 9.2743 | 120.9137 | 121.6644 | 0.37537 | 121.6507 | 10.2722 | 0.032043 | 121.6644 | 0.37537 | 10.2722 | 120.9137 | 121.6507 | -121.1014 | -121.3074
1574.1719 | 121.5775 | -1.6708 | 119.9295 | -0.18272 | 0.012619 | -0.0089189 | 0.011689 | 0.048405 | -0.0086132 | 0.06797 | -1.7487 | 119.6869 | -1.8219 | -1.6846 | 119.1834 | 1.9775 | 0.40741 | 0.34332 | 119.8608 | -1.886 | -0.15106 | -0.24261 | -0.07782 | -0.013733 | -0.74615 | -0.21515 | -0.068664 | 0.073242 | 2.0782 | 2.0142 | 120.8542 | 121.3577 | -0.07782 | 121.5317 | 3.6484 | -0.21515 | 121.3577 | -0.07782 | 3.6484 | 120.8542 | 121.5317 | -121.7514 | -121.8155
1575.8594 | 121.6415 | -1.3367 | 120.2911 | -0.091171 | 0.011123 | -0.0033647 | 0.012544 | 0.050114 | -0.012245 | 0.06733 | -1.1719 | 120.1996 | -1.3687 | -1.1353 | 119.6823 | 2.0554 | 0.28381 | 0.39825 | 120.3598 | -1.3916 | -0.032043 | -0.091553 | 0.1648 | 0.20142 | -0.60883 | -0.054932 | 0.068664 | 0.19684 | 1.6205 | 1.7349 | 121.019 | 121.5363 | 0.1648 | 121.6965 | 3.392 | -0.054932 | 121.5363 | 0.1648 | 3.392 | 121.019 | 121.6965 | -121.6599 | -121.6827
1577.6094 | 121.7194 | -1.0712 | 120.6482 | -0.091171 | 0.0094144 | -0.0067825 | 0.012758 | 0.051823 | -0.010536 | 0.066475 | -1.8356 | 119.545 | -1.9867 | -1.8997 | 118.9728 | 3.0487 | 0.74158 | 0.73242 | 119.7784 | -2.0233 | -0.91553 | -1.1032 | -0.76446 | -0.82855 | -1.6754 | -0.95215 | -0.86975 | 0.15106 | 1.8127 | 1.8036 | 120.0439 | 120.6162 | -0.76446 | 120.8496 | 4.1199 | -0.95215 | 120.6162 | -0.76446 | 4.1199 | 120.0439 | 120.8496 | -122.6349 | -122.6715
1579.3594 | 121.701 | -9.7458 | 111.7355 | 0.25215 | 0.012619 | -0.0035783 | 0.005708 | 0.0499 | -0.012245 | 0.066048 | -9.2651 | 112.0193 | -9.3979 | -9.3704 | 111.4105 | 1.2955 | -0.19684 | 0.11444 | 112.0102 | -9.5947 | 0.3479 | 0.28381 | 0.48065 | 0.37537 | -0.32501 | 0.15106 | 0.27466 | 0.13275 | 9.549 | 9.8602 | 121.1563 | 121.7651 | 0.48065 | 121.756 | 11.0413 | 0.15106 | 121.7651 | 0.48065 | 11.0413 | 121.1563 | 121.756 | -121.1334 | -121.3303
1581.1094 | 121.5866 | -12.8448 | 108.4396 | 0.046158 | 0.011123 | -0.0072099 | 0.01233 | 0.050968 | -0.012886 | 0.06733 | -13.3987 | 108.2748 | -13.0463 | -11.8744 | 108.8287 | 2.4902 | 1.7487 | 1.7303 | 109.9548 | -11.7279 | -0.20142 | -0.16479 | -0.55389 | 0.97046 | 0.3891 | 1.1169 | 1.5152 | -0.35248 | 14.5935 | 14.5752 | 121.6736 | 121.1197 | -0.55389 | 122.7997 | 15.3351 | 1.1169 | 121.1197 | -0.55389 | 15.3351 | 121.6736 | 122.7997 | -121.4859 | -120.1675
1582.7969 | 121.5088 | -13.5132 | 107.9407 | 0.19112 | 0.0089872 | -0.0074235 | 0.009126 | 0.050114 | -0.010536 | 0.067116 | -12.648 | 108.49 | -12.6984 | -12.6846 | 108.2428 | 1.3733 | -0.18768 | 0.54016 | 108.7189 | -12.6984 | 0.81482 | 0.54932 | 0.86517 | 0.82855 | 0.30212 | 0.81482 | 0.7782 | 0.050354 | 13.3255 | 14.0533 | 121.756 | 122.0032 | 0.86517 | 122.2321 | 14.8865 | 0.81482 | 122.0032 | 0.86517 | 14.8865 | 121.756 | 122.2321 | -120.639 | -120.639
1584.5469 | 121.3211 | -20.1553 | 100.9094 | 0.1606 | 0.009628 | -0.0052873 | 0.010194 | 0.049259 | -0.011177 | 0.066475 | -21.5057 | 99.7192 | -21.2631 | -21.2448 | 99.4858 | 2.6001 | 0.10529 | 0.34332 | 99.9664 | -21.2219 | -1.1078 | -1.1902 | -1.3504 | -1.0895 | -1.4236 | -1.0666 | -0.94299 | -0.24261 | 20.2606 | 20.4987 | 119.6411 | 119.8746 | -1.3504 | 120.1218 | 22.7554 | -1.0666 | 119.8746 | -1.3504 | 22.7554 | 119.6411 | 120.1218 | -122.1725 | -122.1313
1586.2969 | 121.1426 | -17.3264 | 103.6606 | 0.038529 | 0.012832 | -0.0057145 | 0.011689 | 0.0499 | -0.009895 | 0.06797 | -18.2556 | 102.9602 | -18.0222 | -17.9306 | 102.5894 | 0.54016 | -0.42114 | -0.3479 | 102.9648 | -18.2053 | -0.6958 | -0.70038 | -0.92926 | -0.60425 | -1.0712 | -0.87891 | -0.6958 | -0.23346 | 16.9052 | 16.9785 | 119.9158 | 120.2866 | -0.92926 | 120.2911 | 17.8665 | -0.87891 | 120.2866 | -0.92926 | 17.8665 | 119.9158 | 120.2911 | -121.6827 | -121.8658
1587.9844 | 121.5088 | -0.19684 | 121.2524 | 0.18349 | 0.011764 | -0.0035783 | 0.0086988 | 0.051396 | -0.0094678 | 0.066902 | -0.059509 | 121.0876 | -0.25635 | 0.027466 | 120.6757 | 2.0233 | -0.041199 | 0.3067 | 121.2433 | -0.29755 | -0.05951 | -0.16479 | 0.13733 | 0.2243 | -0.57678 | -0.10071 | -0.009155 | 0.19684 | 0.15564 | 0.50354 | 120.8725 | 121.2845 | 0.13733 | 121.4401 | 2.2202 | -0.10071 | 121.2845 | 0.13733 | 2.2202 | 120.8725 | 121.4401 | -121.5088 | -121.55
1589.7344 | 121.5546 | -0.21515 | 121.3623 | -0.25139 | 0.011337 | -0.0067825 | 0.008485 | 0.049473 | -0.012031 | 0.068398 | -0.17395 | 121.2112 | -0.29755 | -0.09613 | 120.6436 | 2.0279 | 0.48065 | 0.43945 | 121.3943 | -0.33417 | -0.082397 | -0.15106 | 0.041199 | 0.11902 | -0.71869 | -0.11902 | 0.032043 | 0.1236 | 0.6958 | 0.6546 | 120.8588 | 121.4264 | 0.041199 | 121.6095 | 2.243 | -0.11902 | 121.4264 | 0.041199 | 2.243 | 120.8588 | 121.6095 | -121.6599 | -121.6965
1591.4219 | 121.6141 | -0.20599 | 121.3898 | -0.14458 | 0.013046 | -0.010628 | 0.005708 | 0.050541 | -0.011818 | 0.067116 | -0.082397 | 121.2112 | -0.26093 | 0.022888 | 120.7809 | 2.0416 | 0.23804 | 0.54932 | 121.376 | -0.31128 | -0.054931 | -0.17853 | 0.1236 | 0.22888 | -0.60883 | -0.10528 | -0.013733 | 0.17853 | 0.44403 | 0.75531 | 120.9869 | 121.4172 | 0.1236 | 121.582 | 2.2476 | -0.10528 | 121.4172 | 0.1236 | 2.2476 | 120.9869 | 121.582 | -121.6507 | -121.701
1593.1562 | 121.5958 | -0.22888 | 121.376 | -0.068283 | 0.013687 | -0.0061417 | 0.013612 | 0.050114 | -0.01139 | 0.064766 | -0.11444 | 121.1792 | -0.29755 | -0.045776 | 120.7123 | 1.9363 | 0.2243 | 0.29297 | 121.3852 | -0.3479 | -0.068664 | -0.19684 | 0.11444 | 0.18311 | -0.66376 | -0.11902 | 0.009155 | 0.1831 | 0.45319 | 0.52185 | 120.9412 | 121.4081 | 0.11444 | 121.6141 | 2.1652 | -0.11902 | 121.4081 | 0.11444 | 2.1652 | 120.9412 | 121.6141 | -121.6736 | -121.7239
1594.9062 | 121.5866 | -0.24261 | 121.4172 | -0.11406 | 0.011764 | -0.0040055 | 0.01233 | 0.051609 | -0.010536 | 0.067757 | -0.11902 | 121.2662 | -0.29297 | -0.022888 | 120.7397 | 1.9958 | 0.27008 | 0.3891 | 121.4355 | -0.3479 | -0.050354 | -0.15106 | 0.1236 | 0.21973 | -0.67749 | -0.10528 | 0.018311 | 0.17395 | 0.5127 | 0.63171 | 120.9824 | 121.5088 | 0.1236 | 121.6782 | 2.2385 | -0.10528 | 121.5088 | 0.1236 | 2.2385 | 120.9824 | 121.6782 | -121.7102 | -121.7651
1596.6562 | 121.6553 | -0.23346 | 121.376 | 0.0080111 | 0.011337 | -0.0022965 | 0.01233 | 0.051182 | -0.01075 | 0.06733 | -0.16479 | 121.257 | -0.32044 | -0.07782 | 120.7077 | 1.8723 | 0.19226 | 0.21057 | 121.4401 | -0.35706 | -0.086976 | -0.11902 | 0.068664 | 0.15564 | -0.66833 | -0.1236 | 0.064087 | 0.15564 | 0.42572 | 0.44403 | 120.9412 | 121.4905 | 0.068664 | 121.6736 | 2.1057 | -0.1236 | 121.4905 | 0.068664 | 2.1057 | 120.9412 | 121.6736 | -121.6965 | -121.7331
1598.4062 | 121.6278 | -0.25635 | 121.4218 | -0.17509 | 0.011764 | -0.0050735 | 0.0059216 | 0.050541 | -0.0083996 | 0.065834 | -0.10529 | 121.257 | -0.29297 | -0.004578 | 120.8359 | 2.0737 | 0.32044 | 0.58594 | 121.3852 | -0.33875 | -0.036621 | -0.16479 | 0.15106 | 0.25177 | -0.58594 | -0.082397 | -0.036621 | 0.18768 | 0.57678 | 0.84229 | 121.0922 | 121.5134 | 0.15106 | 121.6415 | 2.33 | -0.082397 | 121.5134 | 0.15106 | 2.33 | 121.0922 | 121.6415 | -121.7148 | -121.7606
1600.1562 | 121.6736 | -0.2243 | 121.431 | -0.25139 | 0.011123 | -0.0042191 | 0.0093396 | 0.049687 | -0.01075 | 0.066475 | -0.11444 | 121.257 | -0.29297 | -0.032043 | 120.7947 | 2.0416 | 0.41199 | 0.54016 | 121.4493 | -0.3479 | -0.068665 | -0.17395 | 0.10986 | 0.19226 | -0.63629 | -0.1236 | 0.018311 | 0.17853 | 0.63629 | 0.76446 | 121.019 | 121.4813 | 0.10986 | 121.6736 | 2.2659 | -0.1236 | 121.4813 | 0.10986 | 2.2659 | 121.019 | 121.6736 | -121.7239 | -121.7789
1601.8438 | 121.7789 | -0.21973 | 121.376 | 0.11482 | 0.012191 | -0.00058746 | 0.0065624 | 0.049259 | -0.0094678 | 0.06797 | -0.1236 | 121.2662 | -0.29755 | -0.059509 | 120.7855 | 1.8723 | 0.068665 | 0.29755 | 121.4127 | -0.35248 | -0.077819 | -0.10986 | 0.096131 | 0.16022 | -0.59052 | -0.13275 | 0.036621 | 0.17395 | 0.28839 | 0.51727 | 121.0052 | 121.4859 | 0.096131 | 121.6324 | 2.092 | -0.13275 | 121.4859 | 0.096131 | 2.092 | 121.0052 | 121.6324 | -121.6736 | -121.7285
1603.5938 | 121.6827 | -0.25635 | 121.4218 | -0.15984 | 0.0094144 | -0.0057145 | 0.0080578 | 0.048405 | -0.010322 | 0.067757 | -0.09613 | 121.2387 | -0.3067 | 0.004578 | 120.8633 | 2.0462 | 0.27466 | 0.58594 | 121.4264 | -0.3479 | -0.050354 | -0.18311 | 0.16022 | 0.26093 | -0.55847 | -0.091552 | 0.004578 | 0.21057 | 0.53101 | 0.84229 | 121.1197 | 121.4951 | 0.16022 | 121.6827 | 2.3026 | -0.091552 | 121.4951 | 0.16022 | 2.3026 | 121.1197 | 121.6827 | -121.7285 | -121.7697
1605.3594 | 121.756 | -0.2243 | 121.4081 | 0.084305 | 0.01326 | -0.0040055 | 0.011689 | 0.050755 | -0.0092542 | 0.065193 | -0.09613 | 121.2936 | -0.29297 | -0.018311 | 120.8084 | 1.8906 | -0.004578 | 0.28839 | 121.4401 | -0.34332 | -0.068665 | -0.11444 | 0.12817 | 0.20599 | -0.59967 | -0.11902 | 0.032044 | 0.19684 | 0.21973 | 0.5127 | 121.0327 | 121.5179 | 0.12817 | 121.6644 | 2.1149 | -0.11902 | 121.5179 | 0.12817 | 2.1149 | 121.0327 | 121.6644 | -121.701 | -121.7514
1607.1094 | 121.6736 | -0.25177 | 121.4584 | -0.12932 | 0.011551 | -0.0069961 | 0.014039 | 0.048832 | -0.011604 | 0.064339 | -0.14191 | 121.2799 | -0.32501 | -0.036621 | 120.7809 | 1.9775 | 0.28381 | 0.39825 | 121.4813 | -0.35248 | -0.073242 | -0.17853 | 0.10986 | 0.21515 | -0.67749 | -0.10071 | 0.022888 | 0.18311 | 0.53558 | 0.65002 | 121.0327 | 121.5317 | 0.10986 | 121.7331 | 2.2293 | -0.10071 | 121.5317 | 0.10986 | 2.2293 | 121.0327 | 121.7331 | -121.7834 | -121.8109
1608.7969 | 121.6644 | -0.27008 | 121.463 | -0.18272 | 0.011337 | -0.0078507 | 0.0093396 | 0.049046 | -0.0094678 | 0.066048 | -0.11444 | 121.2708 | -0.29755 | 0 | 120.8817 | 2.0691 | 0.32044 | 0.58594 | 121.4447 | -0.33875 | -0.027465 | -0.19226 | 0.15564 | 0.27008 | -0.58136 | -0.068664 | -0.018311 | 0.1831 | 0.59052 | 0.85602 | 121.1517 | 121.5408 | 0.15564 | 121.7148 | 2.3392 | -0.068664 | 121.5408 | 0.15564 | 2.3392 | 121.1517 | 121.7148 | -121.7606 | -121.8018
1610.5469 | 121.8109 | -0.21057 | 121.4035 | 0.084305 | 0.011978 | -0.0037919 | 0.015535 | 0.050755 | -0.01075 | 0.066902 | -0.24261 | 121.312 | -0.34332 | -0.11902 | 120.7169 | 1.8265 | 0.12817 | 0.13275 | 121.4905 | -0.37994 | -0.13275 | -0.091552 | -0.032044 | 0.091552 | -0.68664 | -0.16937 | 0.086976 | 0.10071 | 0.33875 | 0.34332 | 120.9274 | 121.5225 | -0.032044 | 121.701 | 2.037 | -0.16937 | 121.5225 | -0.032044 | 2.037 | 120.9274 | 121.701 | -121.7468 | -121.7834
1612.2969 | 121.8475 | -0.21973 | 121.4172 | 0.00038159 | 0.013046 | -0.0046463 | 0.0059216 | 0.049259 | -0.0096814 | 0.06733 | -0.15564 | 121.312 | -0.28839 | -0.082397 | 120.8221 | 1.8997 | 0.16022 | 0.34332 | 121.4401 | -0.37537 | -0.068664 | -0.10529 | 0.064087 | 0.13733 | -0.59509 | -0.15564 | 0.022889 | 0.13275 | 0.37994 | 0.56305 | 121.0419 | 121.5317 | 0.064087 | 121.6599 | 2.1194 | -0.15564 | 121.5317 | 0.064087 | 2.1194 | 121.0419 | 121.6599 | -121.7056 | -121.7926
1614.0469 | 121.7972 | -0.23804 | 121.4401 | 0.030899 | 0.012619 | -0.0022965 | 0.014894 | 0.050968 | -0.012245 | 0.066048 | -0.20599 | 121.3074 | -0.35248 | -0.14648 | 120.7077 | 1.8311 | 0.18768 | 0.15564 | 121.4767 | -0.37994 | -0.11444 | -0.13275 | 0.032043 | 0.091553 | -0.73242 | -0.14191 | 0.036621 | 0.14648 | 0.42572 | 0.39368 | 120.9457 | 121.5454 | 0.032043 | 121.7148 | 2.0691 | -0.14191 | 121.5454 | 0.032043 | 2.0691 | 120.9457 | 121.7148 | -121.7926 | -121.8201
1615.7344 | 121.8063 | -0.24261 | 121.4127 | 0.053787 | 0.0092008 | -0.0063553 | 0.012971 | 0.050541 | -0.011177 | 0.067116 | -0.24261 | 121.3074 | -0.35706 | -0.15106 | 120.7397 | 1.8311 | 0.19226 | 0.16937 | 121.4539 | -0.40283 | -0.11444 | -0.10529 | 0 | 0.091553 | -0.67291 | -0.16022 | 0.041198 | 0.11444 | 0.43488 | 0.41199 | 120.9824 | 121.55 | 0 | 121.6965 | 2.0737 | -0.16022 | 121.55 | 0 | 2.0737 | 120.9824 | 121.6965 | -121.7697 | -121.8155
1617.4844 | 121.701 | -0.34332 | 121.3715 | -0.19035 | 0.011764 | -0.0061417 | 0.0076306 | 0.050968 | -0.0096814 | 0.064339 | -0.17853 | 121.2433 | -0.37537 | -0.07782 | 120.8176 | 2.0691 | 0.3067 | 0.59052 | 121.4035 | -0.42114 | -0.032043 | -0.12817 | 0.16479 | 0.2655 | -0.55389 | -0.07782 | 0.032043 | 0.19684 | 0.65002 | 0.93384 | 121.1609 | 121.5866 | 0.16479 | 121.7468 | 2.4124 | -0.07782 | 121.5866 | 0.16479 | 2.4124 | 121.1609 | 121.7468 | -121.7468 | -121.7926
1619.2344 | 121.8109 | -0.30212 | 121.3852 | -0.068283 | 0.011978 | -0.0031509 | 0.005708 | 0.0499 | -0.0092542 | 0.065407 | -0.21057 | 121.2524 | -0.36621 | -0.11444 | 120.813 | 1.9913 | 0.21057 | 0.46692 | 121.4401 | -0.40741 | -0.064087 | -0.13275 | 0.091553 | 0.18768 | -0.5722 | -0.10529 | 0.054932 | 0.15564 | 0.5127 | 0.76904 | 121.1151 | 121.5546 | 0.091553 | 121.7422 | 2.2934 | -0.10529 | 121.5546 | 0.091553 | 2.2934 | 121.1151 | 121.7422 | -121.7514 | -121.7926
1620.9219 | 121.756 | -0.33417 | 121.4035 | -0.25902 | 0.011337 | -0.0044327 | 0.011903 | 0.048191 | -0.010963 | 0.064125 | -0.2655 | 121.2753 | -0.40741 | -0.17853 | 120.7352 | 1.9958 | 0.46692 | 0.49439 | 121.4493 | -0.43488 | -0.073243 | -0.12817 | 0.068664 | 0.15564 | -0.66833 | -0.10071 | 0.045777 | 0.14191 | 0.80109 | 0.82855 | 121.0693 | 121.6095 | 0.068664 | 121.7834 | 2.33 | -0.10071 | 121.6095 | 0.068664 | 2.33 | 121.0693 | 121.7834 | -121.8109 | -121.8384
1622.6719 | 121.788 | -0.33875 | 121.3806 | -0.13695 | 0.012832 | -0.0042191 | 0.0093396 | 0.050114 | -0.010109 | 0.065407 | -0.19684 | 121.225 | -0.37537 | -0.091553 | 120.8176 | 2.0416 | 0.22888 | 0.53558 | 121.4218 | -0.44403 | -0.036621 | -0.15564 | 0.14191 | 0.24719 | -0.56305 | -0.10529 | 0.041199 | 0.17853 | 0.56763 | 0.87433 | 121.1563 | 121.5637 | 0.14191 | 121.7606 | 2.3804 | -0.10529 | 121.5637 | 0.14191 | 2.3804 | 121.1563 | 121.7606 | -121.756 | -121.8246
1624.4219 | 121.8246 | -0.33875 | 121.3486 | 0.11482 | 0.013046 | -0.0057145 | 0.0097668 | 0.050755 | -0.011604 | 0.065834 | -0.20599 | 121.2204 | -0.40741 | -0.1236 | 120.7901 | 1.9272 | -0.032043 | 0.28839 | 121.3623 | -0.45319 | -0.068665 | -0.12817 | 0.13275 | 0.21515 | -0.55847 | -0.11444 | 0.013733 | 0.20142 | 0.3067 | 0.62714 | 121.1288 | 121.5591 | 0.13275 | 121.7011 | 2.2659 | -0.11444 | 121.5591 | 0.13275 | 2.2659 | 121.1288 | 121.7011 | -121.756 | -121.8018
1626.125 | 121.8292 | -0.33875 | 121.3577 | -0.045395 | 0.009628 | -0.0059281 | 0.0086988 | 0.049687 | -0.0075452 | 0.065407 | -0.26093 | 121.225 | -0.4303 | -0.16022 | 120.7672 | 1.9913 | 0.20599 | 0.46234 | 121.3852 | -0.47607 | -0.091553 | -0.13275 | 0.07782 | 0.17853 | -0.59051 | -0.13733 | 0.027466 | 0.16937 | 0.54474 | 0.80109 | 121.106 | 121.5637 | 0.07782 | 121.7239 | 2.33 | -0.13733 | 121.5637 | 0.07782 | 2.33 | 121.106 | 121.7239 | -121.788 | -121.8338
1627.8906 | 121.788 | -0.36163 | 121.3669 | -0.21324 | 0.013473 | -0.0057145 | 0.014039 | 0.050968 | -0.013527 | 0.064125 | -0.32501 | 121.257 | -0.4715 | -0.21973 | 120.694 | 1.9913 | 0.46692 | 0.42572 | 121.4355 | -0.48523 | -0.10986 | -0.10986 | 0.036621 | 0.14191 | -0.67291 | -0.1236 | 0.068665 | 0.14648 | 0.82855 | 0.78735 | 121.0556 | 121.6187 | 0.036621 | 121.7972 | 2.3529 | -0.1236 | 121.6187 | 0.036621 | 2.3529 | 121.0556 | 121.7972 | -121.8384 | -121.8521
1629.6406 | 121.8063 | -0.3479 | 121.3669 | 0.18349 | 0.01326 | -0.0046463 | 0.010835 | 0.052891 | -0.0092542 | 0.066475 | -0.16937 | 121.2296 | -0.39825 | -0.10071 | 120.8084 | 1.9272 | -0.059509 | 0.28381 | 121.4172 | -0.4303 | -0.050354 | -0.13733 | 0.17853 | 0.24719 | -0.55847 | -0.082398 | 0.050354 | 0.22888 | 0.28839 | 0.63171 | 121.1563 | 121.5775 | 0.17853 | 121.7651 | 2.2751 | -0.082398 | 121.5775 | 0.17853 | 2.2751 | 121.1563 | 121.7651 | -121.7651 | -121.7972
1631.3281 | 121.8567 | -0.32959 | 121.3669 | 0.00038159 | 0.009628 | -0.0069961 | 0.009126 | 0.050328 | -0.009895 | 0.067757 | -0.27008 | 121.2204 | -0.4303 | -0.18768 | 120.7581 | 1.9318 | 0.17853 | 0.37079 | 121.3943 | -0.45776 | -0.10071 | -0.14648 | 0.059509 | 0.14191 | -0.60883 | -0.12817 | 0.027466 | 0.16022 | 0.50812 | 0.70038 | 121.0876 | 121.55 | 0.059509 | 121.7239 | 2.2614 | -0.12817 | 121.55 | 0.059509 | 2.2614 | 121.0876 | 121.7239 | -121.7972 | -121.8246
1633.1094 | 121.8384 | -0.3479 | 121.3531 | 0.13771 | 0.011978 | -0.0046463 | 0.011262 | 0.052464 | -0.0086132 | 0.067116 | -0.19684 | 121.2387 | -0.38452 | -0.1236 | 120.8084 | 1.918 | -0.036621 | 0.29755 | 121.3531 | -0.43945 | -0.036621 | -0.11444 | 0.15106 | 0.2243 | -0.54474 | -0.091553 | 0 | 0.18768 | 0.31128 | 0.64545 | 121.1563 | 121.5866 | 0.15106 | 121.701 | 2.2659 | -0.091553 | 121.5866 | 0.15106 | 2.2659 | 121.1563 | 121.701 | -121.7377 | -121.7926
1634.7969 | 121.8246 | -0.37537 | 121.3211 | 0.16823 | 0.0087734 | -0.0052873 | 0.013612 | 0.052677 | -0.010536 | 0.068611 | -0.25635 | 121.1472 | -0.46692 | -0.17395 | 120.7443 | 1.9272 | -0.073242 | 0.27924 | 121.3165 | -0.48523 | -0.091553 | -0.17395 | 0.11902 | 0.20142 | -0.57678 | -0.10986 | -0.004578 | 0.21057 | 0.30212 | 0.6546 | 121.1197 | 121.5225 | 0.11902 | 121.6919 | 2.3026 | -0.10986 | 121.5225 | 0.11902 | 2.3026 | 121.1197 | 121.6919 | -121.788 | -121.8063
1636.5469 | 121.8246 | -1.0345 | 120.694 | -0.19798 | 0.009628 | -0.0076371 | 0.0082714 | 0.048832 | -0.01075 | 0.063698 | -0.94299 | 120.5475 | -1.1032 | -0.81024 | 120.1309 | 2.037 | 0.24261 | 0.52185 | 120.6665 | -1.1673 | -0.068664 | -0.14648 | 0.091553 | 0.2243 | -0.56305 | -0.13275 | -0.027466 | 0.16022 | 1.2772 | 1.5564 | 121.1655 | 121.582 | 0.091553 | 121.7011 | 3.0716 | -0.13275 | 121.582 | 0.091553 | 3.0716 | 121.1655 | 121.7011 | -121.7972 | -121.8613
1638.2969 | 121.8796 | -0.32044 | 121.376 | 0.12245 | 0.012405 | -0.0063553 | 0.011476 | 0.050114 | -0.0083996 | 0.066048 | -0.16937 | 121.257 | -0.35248 | -0.091553 | 120.8267 | 1.9455 | 0.036621 | 0.30212 | 121.4127 | -0.40283 | -0.032043 | -0.11902 | 0.15106 | 0.22888 | -0.54932 | -0.082397 | 0.036621 | 0.18311 | 0.35706 | 0.62256 | 121.1472 | 121.5775 | 0.15106 | 121.7331 | 2.2659 | -0.082397 | 121.5775 | 0.15106 | 2.2659 | 121.1472 | 121.7331 | -121.7285 | -121.7789
1639.9844 | 121.8658 | -0.29297 | 121.3989 | 0.099564 | 0.011337 | -0.0014419 | 0.014467 | 0.050968 | -0.010536 | 0.06733 | -0.26093 | 121.3211 | -0.3891 | -0.17853 | 120.7397 | 1.8539 | 0.045776 | 0.14648 | 121.4584 | -0.43488 | -0.09613 | -0.07782 | 0.032044 | 0.11444 | -0.65918 | -0.14191 | 0.059509 | 0.12817 | 0.33874 | 0.43945 | 121.0327 | 121.6141 | 0.032044 | 121.7514 | 2.1469 | -0.14191 | 121.6141 | 0.032044 | 2.1469 | 121.0327 | 121.7514 | -121.788 | -121.8338
1641.75 | 121.8887 | -0.30212 | 121.3943 | 0.12245 | 0.010482 | -0.0046463 | 0.010194 | 0.047764 | -0.0096814 | 0.067543 | -0.21057 | 121.2799 | -0.37079 | -0.11902 | 120.8221 | 1.9226 | 0.036621 | 0.29297 | 121.4355 | -0.4303 | -0.068665 | -0.11444 | 0.091553 | 0.18311 | -0.5722 | -0.12817 | 0.041199 | 0.16022 | 0.33875 | 0.59509 | 121.1243 | 121.582 | 0.091553 | 121.7377 | 2.2247 | -0.12817 | 121.582 | 0.091553 | 2.2247 | 121.1243 | 121.7377 | -121.7651 | -121.8246
1643.4844 | 121.7697 | -0.36163 | 121.4493 | -0.18272 | 0.011337 | -0.0093461 | 0.010194 | 0.04755 | -0.011604 | 0.065193 | -0.18768 | 121.2891 | -0.37994 | -0.073242 | 120.8588 | 2.1103 | 0.31128 | 0.59052 | 121.4127 | -0.4303 | -0.018311 | -0.16022 | 0.17395 | 0.28839 | -0.59051 | -0.068665 | -0.036621 | 0.19226 | 0.67291 | 0.95215 | 121.2204 | 121.6507 | 0.17395 | 121.7743 | 2.4719 | -0.068665 | 121.6507 | 0.17395 | 2.4719 | 121.2204 | 121.7743 | -121.8292 | -121.8796
1645.2344 | 121.8613 | -0.33875 | 121.3852 | 0.053787 | 0.011551 | -0.00058746 | 0.016176 | 0.052037 | -0.013313 | 0.066475 | -0.31128 | 121.2891 | -0.43488 | -0.23346 | 120.6985 | 1.8768 | 0.1831 | 0.16022 | 121.4539 | -0.48065 | -0.09613 | -0.096131 | 0.027466 | 0.10529 | -0.68665 | -0.14191 | 0.068664 | 0.1236 | 0.52185 | 0.49896 | 121.0373 | 121.6278 | 0.027466 | 121.7926 | 2.2156 | -0.14191 | 121.6278 | 0.027466 | 2.2156 | 121.0373 | 121.7926 | -121.8201 | -121.8658
1647.0312 | 121.7697 | -0.36163 | 121.4081 | -0.18272 | 0.011764 | -0.0059281 | 0.015107 | 0.051609 | -0.012245 | 0.066262 | -0.29755 | 121.2708 | -0.45319 | -0.20142 | 120.7581 | 2.037 | 0.34332 | 0.39825 | 121.463 | -0.45776 | -0.091553 | -0.13733 | 0.064087 | 0.16022 | -0.65002 | -0.096131 | 0.054932 | 0.15564 | 0.70496 | 0.75989 | 121.1197 | 121.6324 | 0.064087 | 121.8246 | 2.3987 | -0.096131 | 121.6324 | 0.064087 | 2.3987 | 121.1197 | 121.8246 | -121.8613 | -121.8658
1648.7188 | 121.8018 | -0.42572 | 121.376 | -0.23613 | 0.01091 | -0.0076371 | 0.0065624 | 0.048832 | -0.01139 | 0.06733 | -0.35706 | 121.2753 | -0.46692 | -0.27008 | 120.7031 | 2.037 | 0.4715 | 0.48065 | 121.4355 | -0.52643 | -0.041199 | -0.10071 | 0.068664 | 0.15564 | -0.67291 | -0.10071 | 0.059509 | 0.10986 | 0.89722 | 0.90637 | 121.1288 | 121.701 | 0.068664 | 121.8613 | 2.4628 | -0.10071 | 121.701 | 0.068664 | 2.4628 | 121.1288 | 121.8613 | -121.843 | -121.9025
1650.4688 | 121.7834 | -0.4303 | 121.3806 | -0.19035 | 0.01091 | -0.0035783 | 0.007417 | 0.048619 | -0.011604 | 0.066262 | -0.2655 | 121.2204 | -0.46234 | -0.17853 | 120.8084 | 2.1194 | 0.30212 | 0.60425 | 121.3943 | -0.49896 | -0.032043 | -0.16022 | 0.1648 | 0.25177 | -0.5722 | -0.068664 | 0.013733 | 0.19684 | 0.73242 | 1.0345 | 121.2387 | 121.6507 | 0.1648 | 121.8246 | 2.5497 | -0.068664 | 121.6507 | 0.1648 | 2.5497 | 121.2387 | 121.8246 | -121.843 | -121.8796
1652.2188 | 121.8567 | -0.42114 | 121.3074 | 0.15297 | 0.013046 | -0.0065689 | 0.012971 | 0.05225 | -0.011604 | 0.067757 | -0.2655 | 121.1929 | -0.45776 | -0.1831 | 120.7718 | 1.9684 | -0.068665 | 0.2655 | 121.3943 | -0.48981 | -0.036621 | -0.11444 | 0.15564 | 0.23804 | -0.53558 | -0.068664 | 0.086975 | 0.19226 | 0.35248 | 0.68665 | 121.1929 | 121.6141 | 0.15564 | 121.8155 | 2.3895 | -0.068664 | 121.6141 | 0.15564 | 2.3895 | 121.1929 | 121.8155 | -121.7651 | -121.7972
1653.9062 | 121.8704 | -0.39825 | 121.3303 | 0.14534 | 0.010269 | -0.0031509 | 0.011049 | 0.048619 | -0.008827 | 0.066262 | -0.28381 | 121.1838 | -0.44861 | -0.18768 | 120.7672 | 1.9592 | -0.036621 | 0.29297 | 121.312 | -0.5127 | -0.050354 | -0.14648 | 0.11444 | 0.21057 | -0.56305 | -0.11444 | -0.01831 | 0.1648 | 0.36163 | 0.69122 | 121.1655 | 121.582 | 0.11444 | 121.7102 | 2.3575 | -0.11444 | 121.582 | 0.11444 | 2.3575 | 121.1655 | 121.7102 | -121.7789 | -121.843
1655.6719 | 121.7834 | -0.48981 | 121.344 | -0.20561 | 0.010055 | -0.0069961 | 0.0086988 | 0.047978 | -0.009895 | 0.065621 | -0.30212 | 121.1884 | -0.49896 | -0.20599 | 120.7626 | 2.124 | 0.31586 | 0.60425 | 121.312 | -0.54016 | -0.009155 | -0.15564 | 0.18768 | 0.28381 | -0.58136 | -0.050354 | -0.032043 | 0.19684 | 0.80566 | 1.0941 | 121.2524 | 121.6782 | 0.18768 | 121.8018 | 2.6138 | -0.050354 | 121.6782 | 0.18768 | 2.6138 | 121.2524 | 121.8018 | -121.843 | -121.8842
1657.3594 | 121.8521 | -0.93384 | 120.7809 | 0.091934 | 0.0094144 | -0.0031509 | 0.014039 | 0.0499 | -0.010963 | 0.065834 | -0.80566 | 120.6436 | -0.99792 | -0.737 | 120.2362 | 1.9409 | -0.059509 | 0.26093 | 120.813 | -1.0437 | -0.064087 | -0.13733 | 0.12817 | 0.19684 | -0.54474 | -0.10986 | 0.032043 | 0.19226 | 0.87433 | 1.1948 | 121.17 | 121.5775 | 0.12817 | 121.7468 | 2.8748 | -0.10986 | 121.5775 | 0.12817 | 2.8748 | 121.17 | 121.7468 | -121.7789 | -121.8246
1659.1094 | 121.8201 | -2.1881 | 119.5404 | -0.11406 | 0.01091 | -0.0033647 | 0.0080578 | 0.049473 | -0.011604 | 0.068611 | -2.0462 | 119.4626 | -2.2064 | -1.9272 | 119.0094 | 2.0737 | 0.23804 | 0.5127 | 119.577 | -2.2568 | -0.018311 | -0.07782 | 0.14191 | 0.26093 | -0.53101 | -0.068665 | 0.036621 | 0.16022 | 2.4261 | 2.7008 | 121.1975 | 121.6507 | 0.14191 | 121.7651 | 4.2618 | -0.068665 | 121.6507 | 0.14191 | 4.2618 | 121.1975 | 121.7651 | -121.7468 | -121.7972
1660.8125 | 121.9116 | -2.2476 | 119.4489 | -0.030136 | 0.010269 | -0.0042191 | 0.0097668 | 0.048405 | -0.010109 | 0.065834 | -4.0054 | 117.4988 | -4.1382 | -3.9139 | 116.9998 | 1.6342 | 0.31586 | 0.44403 | 117.7277 | -4.1382 | -1.8906 | -1.9501 | -1.7578 | -1.6663 | -2.449 | -1.8906 | -1.7212 | 0.13275 | 2.5635 | 2.6917 | 119.2474 | 119.7464 | -1.7578 | 119.9753 | 3.8818 | -1.8906 | 119.7464 | -1.7578 | 3.8818 | 119.2474 | 119.9753 | -123.587 | -123.587
1662.5625 | 121.8658 | -0.64087 | 121.1014 | 0.053787 | 0.013687 | -0.0044327 | 0.015107 | 0.049259 | -0.012031 | 0.065621 | -0.63171 | 120.9732 | -0.76904 | -0.56305 | 120.3873 | 1.8951 | 0.18768 | 0.16022 | 121.1288 | -0.8194 | -0.12817 | -0.12817 | 0.009155 | 0.07782 | -0.71411 | -0.17853 | 0.027466 | 0.13733 | 0.82855 | 0.80109 | 121.0281 | 121.6141 | 0.009155 | 121.7697 | 2.536 | -0.17853 | 121.6141 | 0.009155 | 2.536 | 121.0281 | 121.7697 | -121.8704 | -121.9208
1664.25 | 121.8384 | -2.1286 | 119.6228 | -0.21324 | 0.0089872 | -0.0074235 | 0.011689 | 0.049687 | -0.01139 | 0.06797 | -2.0645 | 119.5084 | -2.243 | -1.8997 | 118.9911 | 1.7349 | 0.24719 | 0.29297 | 119.6091 | -2.2751 | -0.11444 | -0.11444 | 0.064087 | 0.22888 | -0.63171 | -0.14648 | -0.013733 | 0.17853 | 2.3758 | 2.4216 | 121.1197 | 121.637 | 0.064087 | 121.7377 | 3.8635 | -0.14648 | 121.637 | 0.064087 | 3.8635 | 121.1197 | 121.7377 | -121.8658 | -121.8979
1666.0156 | 121.6965 | -7.7728 | 113.887 | -0.068283 | 0.01091 | -0.0022965 | 0.014253 | 0.051609 | -0.011818 | 0.065834 | -7.7316 | 113.8138 | -7.7866 | -7.5851 | 113.3652 | 1.7624 | 0.23346 | 0.33417 | 113.9511 | -7.8186 | -0.013733 | -0.073242 | 0.041199 | 0.18768 | -0.52185 | -0.045777 | 0.064087 | 0.054932 | 8.0063 | 8.107 | 121.138 | 121.5866 | 0.041199 | 121.7239 | 9.5352 | -0.045777 | 121.5866 | 0.041199 | 9.5352 | 121.138 | 121.7239 | -121.6736 | -121.7056
1667.7656 | 121.669 | -17.7658 | 103.7201 | -0.13695 | 0.013473 | -0.0072099 | 0.0054944 | 0.048191 | -0.011177 | 0.064553 | -16.2827 | 104.8279 | -16.5527 | -16.2277 | 104.7867 | 1.8539 | 0.3891 | 0.69122 | 105.1346 | -16.4658 | 1.2131 | 1.1078 | 1.4832 | 1.5381 | 1.0666 | 1.3 | 1.4145 | 0.27008 | 18.1549 | 18.457 | 122.5525 | 122.5937 | 1.4832 | 122.9004 | 19.6198 | 1.3 | 122.5937 | 1.4832 | 19.6198 | 122.5525 | 122.9004 | -120.2728 | -120.1859
1669.4531 | 120.845 | -75.737 | 44.7601 | -0.13695 | 0.0098416 | -0.0074235 | 0.0082714 | 0.050755 | -0.0079724 | 0.066475 | -75.8377 | 44.5496 | -76.0391 | -75.9705 | 44.4214 | -1.1765 | -0.064087 | 0.23346 | 44.6457 | -76.0345 | -0.30212 | -0.21057 | -0.10071 | -0.23346 | -0.33874 | -0.29755 | -0.11444 | 0.20142 | 75.6729 | 75.9705 | 120.1584 | 120.2866 | -0.10071 | 120.3827 | 74.5605 | -0.29755 | 120.2866 | -0.10071 | 74.5605 | 120.1584 | 120.3827 | -120.7993 | -120.7947
1671.2188 | 121.4447 | -116.185 | 4.9301 | -0.045395 | 0.012405 | -0.0055009 | 0.010408 | 0.049046 | -0.0079724 | 0.066689 | -116.1392 | 4.8111 | -116.3727 | -116.2216 | 4.7653 | -2.4033 | -0.44861 | -0.17395 | 4.8294 | -116.5466 | -0.18768 | -0.11902 | 0.045777 | -0.036621 | -0.16479 | -0.36163 | -0.10071 | 0.23346 | 115.7364 | 116.011 | 120.9503 | 120.9961 | 0.045777 | 121.0144 | 113.7817 | -0.36163 | 120.9961 | 0.045777 | 113.7817 | 120.9503 | 121.0144 | -121.3028 | -121.4767
1672.9375 | 120.8908 | -68.1564 | 52.5558 | -0.0072479 | 0.013473 | -0.0033647 | 0.0080578 | 0.050328 | -0.010536 | 0.067116 | -63.0203 | 58.2275 | -62.7594 | -63.5101 | 56.9824 | -0.71869 | -1.9547 | -1.7349 | 57.1518 | -63.6887 | 5.397 | 5.6717 | 5.1361 | 4.6463 | 4.4266 | 4.4678 | 4.5959 | -0.26093 | 66.2018 | 66.4215 | 125.1389 | 126.384 | 5.1361 | 125.3082 | 67.4377 | 4.4678 | 126.384 | 5.1361 | 67.4377 | 125.1389 | 125.3082 | -115.3152 | -116.2445
1674.7031 | 120.9274 | -0.26093 | 120.9503 | -0.17509 | 0.012405 | -0.0046463 | 0.015748 | 0.050755 | -0.012458 | 0.067116 | -0.18768 | 120.7581 | -0.35248 | -0.09613 | 120.2454 | 2.5085 | 0.49896 | 0.53101 | 120.9686 | -0.35706 | -0.091553 | -0.19226 | 0.073242 | 0.1648 | -0.70496 | -0.096131 | 0.018311 | 0.1648 | 0.75989 | 0.79193 | 120.5063 | 121.019 | 0.073242 | 121.2296 | 2.7695 | -0.096131 | 121.019 | 0.073242 | 2.7695 | 120.5063 | 121.2296 | -121.3028 | -121.3074
1676.3906 | 121.3486 | -0.1831 | 121.0236 | 0.13008 | 0.011551 | -0.0059281 | 0.012544 | 0.048832 | -0.011177 | 0.064766 | -0.15106 | 120.9091 | -0.28381 | -0.082397 | 120.3323 | 2.1149 | 0.17853 | 0.17395 | 121.0556 | -0.32959 | -0.10071 | -0.11444 | 0.032043 | 0.10071 | -0.69122 | -0.14649 | 0.032043 | 0.13275 | 0.36163 | 0.35706 | 120.5154 | 121.0922 | 0.032043 | 121.2387 | 2.298 | -0.14649 | 121.0922 | 0.032043 | 2.298 | 120.5154 | 121.2387 | -121.3074 | -121.3531
1678.1406 | 121.2845 | -0.21515 | 121.1197 | -0.13695 | 0.010696 | -0.0089189 | 0.0080578 | 0.04691 | -0.009895 | 0.065407 | -0.045776 | 120.9274 | -0.24261 | 0.041199 | 120.5475 | 2.2705 | 0.31128 | 0.61798 | 121.0922 | -0.28839 | -0.027466 | -0.19226 | 0.16937 | 0.25635 | -0.57221 | -0.073242 | -0.027466 | 0.19684 | 0.52643 | 0.83313 | 120.7626 | 121.1426 | 0.16937 | 121.3074 | 2.4857 | -0.073242 | 121.1426 | 0.16937 | 2.4857 | 120.7626 | 121.3074 | -121.3623 | -121.4081
1679.8281 | 121.344 | -0.2243 | 121.1197 | -0.15221 | 0.013473 | -0.0067825 | 0.0097668 | 0.04691 | -0.011818 | 0.065193 | -0.07782 | 120.9641 | -0.27924 | 0.032043 | 120.5566 | 2.2202 | 0.26093 | 0.59509 | 121.0922 | -0.32044 | -0.054932 | -0.15564 | 0.14648 | 0.25635 | -0.56305 | -0.096131 | -0.027466 | 0.20142 | 0.48523 | 0.8194 | 120.7809 | 121.1884 | 0.14648 | 121.3165 | 2.4445 | -0.096131 | 121.1884 | 0.14648 | 2.4445 | 120.7809 | 121.3165 | -121.3989 | -121.4401
1681.5781 | 121.4035 | -0.24261 | 121.0968 | -0.17509 | 0.011551 | -0.0046463 | 0.0082714 | 0.04691 | -0.0075452 | 0.064553 | -0.11444 | 120.9686 | -0.29297 | -0.018311 | 120.5429 | 2.1927 | 0.24719 | 0.55847 | 121.1014 | -0.36163 | -0.050354 | -0.12817 | 0.12817 | 0.2243 | -0.55389 | -0.11902 | 0.004577 | 0.17853 | 0.48981 | 0.80109 | 120.7855 | 121.2112 | 0.12817 | 121.344 | 2.4353 | -0.11902 | 121.2112 | 0.12817 | 2.4353 | 120.7855 | 121.344 | -121.3898 | -121.4584
1683.3281 | 121.376 | -0.26093 | 121.1472 | -0.083542 | 0.012191 | -0.0059281 | 0.016603 | 0.049259 | -0.012672 | 0.065834 | -0.16022 | 121.0007 | -0.33417 | -0.054932 | 120.488 | 2.1011 | 0.23346 | 0.36163 | 121.1334 | -0.35706 | -0.073242 | -0.14648 | 0.10071 | 0.20599 | -0.65918 | -0.096131 | -0.013733 | 0.17395 | 0.49438 | 0.62256 | 120.7489 | 121.2616 | 0.10071 | 121.3943 | 2.3621 | -0.096131 | 121.2616 | 0.10071 | 2.3621 | 120.7489 | 121.3943 | -121.4813 | -121.5042
1685.0938 | 121.4035 | -0.28381 | 121.138 | -0.053024 | 0.011764 | -0.0059281 | 0.015748 | 0.050328 | -0.012245 | 0.064553 | -0.17853 | 120.9824 | -0.36163 | -0.073242 | 120.4971 | 2.0782 | 0.22888 | 0.3479 | 121.138 | -0.38452 | -0.07782 | -0.15564 | 0.10528 | 0.21057 | -0.64087 | -0.10071 | 0 | 0.1831 | 0.5127 | 0.63171 | 120.7809 | 121.2662 | 0.10528 | 121.4218 | 2.3621 | -0.10071 | 121.2662 | 0.10528 | 2.3621 | 120.7809 | 121.4218 | -121.4996 | -121.5225
1686.7969 | 121.4172 | -0.32044 | 121.1426 | -0.19035 | 0.012619 | -0.0050735 | 0.0072034 | 0.050541 | -0.010322 | 0.064766 | -0.13275 | 121.0052 | -0.34332 | -0.041199 | 120.5841 | 2.1927 | 0.31586 | 0.59967 | 121.1243 | -0.3891 | -0.022888 | -0.13733 | 0.18768 | 0.27924 | -0.55847 | -0.068664 | -0.01831 | 0.21057 | 0.63629 | 0.92011 | 120.9045 | 121.3257 | 0.18768 | 121.4447 | 2.5131 | -0.068664 | 121.3257 | 0.18768 | 2.5131 | 120.9045 | 121.4447 | -121.4859 | -121.5317
1688.5469 | 121.4355 | -0.31128 | 121.1472 | -0.083542 | 0.012619 | -0.0022965 | 0.014039 | 0.050755 | -0.012458 | 0.066689 | -0.21057 | 121.0281 | -0.39368 | -0.12817 | 120.488 | 2.0874 | 0.23346 | 0.35248 | 121.1655 | -0.42572 | -0.082398 | -0.11902 | 0.10071 | 0.1831 | -0.65918 | -0.11444 | 0.01831 | 0.18311 | 0.54474 | 0.66376 | 120.7993 | 121.3394 | 0.10071 | 121.4767 | 2.3987 | -0.11444 | 121.3394 | 0.10071 | 2.3987 | 120.7993 | 121.4767 | -121.5408 | -121.5729
1690.25 | 121.5637 | -0.2655 | 121.0831 | 0.1606 | 0.013046 | -0.0055009 | 0.012758 | 0.053105 | -0.011604 | 0.068825 | -0.27008 | 121.0098 | -0.39825 | -0.16937 | 120.4651 | 1.9547 | 0.022888 | 0.16479 | 121.138 | -0.43488 | -0.13275 | -0.073242 | -0.004578 | 0.09613 | -0.61798 | -0.16937 | 0.054931 | 0.12817 | 0.28839 | 0.4303 | 120.7306 | 121.2753 | -0.004578 | 121.4035 | 2.2202 | -0.16937 | 121.2753 | -0.004578 | 2.2202 | 120.7306 | 121.4035 | -121.4813 | -121.5179
1692.0625 | 121.582 | -0.28839 | 121.138 | 0.00038159 | 0.009628 | -0.0095597 | 0.0048534 | 0.047764 | -0.0092542 | 0.069252 | -0.27008 | 120.9778 | -0.38452 | -0.16937 | 120.52 | 2.0645 | 0.21057 | 0.40283 | 121.1197 | -0.43488 | -0.09613 | -0.16022 | 0.01831 | 0.11902 | -0.61798 | -0.14648 | -0.01831 | 0.11444 | 0.49896 | 0.69122 | 120.8084 | 121.2662 | 0.01831 | 121.4081 | 2.3529 | -0.14648 | 121.2662 | 0.01831 | 2.3529 | 120.8084 | 121.4081 | -121.5225 | -121.5729
1693.7969 | 121.5363 | -0.32501 | 121.17 | -0.20561 | 0.014755 | -0.0031509 | 0.012758 | 0.050541 | -0.012672 | 0.067116 | -0.28381 | 121.0739 | -0.40283 | -0.20142 | 120.4834 | 2.1011 | 0.45319 | 0.43488 | 121.2387 | -0.46234 | -0.07782 | -0.09613 | 0.041199 | 0.1236 | -0.68665 | -0.13733 | 0.068664 | 0.11902 | 0.7782 | 0.75989 | 120.8084 | 121.3989 | 0.041199 | 121.5637 | 2.4261 | -0.13733 | 121.3989 | 0.041199 | 2.4261 | 120.8084 | 121.5637 | -121.5729 | -121.6324
1695.5312 | 121.582 | -0.31586 | 121.1426 | 0.1606 | 0.012405 | -0.0040055 | 0.01233 | 0.051182 | -0.008186 | 0.066689 | -0.18768 | 121.0373 | -0.36621 | -0.11444 | 120.5887 | 2.0279 | -0.073242 | 0.27924 | 121.1746 | -0.42114 | -0.050354 | -0.10529 | 0.12817 | 0.20142 | -0.55389 | -0.10529 | 0.032044 | 0.17853 | 0.24261 | 0.59509 | 120.9045 | 121.3531 | 0.12817 | 121.4905 | 2.3438 | -0.10529 | 121.3531 | 0.12817 | 2.3438 | 120.9045 | 121.4905 | -121.5088 | -121.5637
1697.2812 | 121.4996 | -0.37079 | 121.1746 | -0.091171 | 0.0092008 | -0.0065689 | 0.014894 | 0.053105 | -0.011604 | 0.065407 | -0.27008 | 121.0098 | -0.45319 | -0.16479 | 120.5292 | 2.1057 | 0.29297 | 0.39368 | 121.2067 | -0.4715 | -0.082397 | -0.16479 | 0.10071 | 0.20599 | -0.64545 | -0.10071 | 0.032043 | 0.1831 | 0.66376 | 0.76447 | 120.9 | 121.3806 | 0.10071 | 121.5775 | 2.4765 | -0.10071 | 121.3806 | 0.10071 | 2.4765 | 120.9 | 121.5775 | -121.6278 | -121.6461
1698.9844 | 121.6553 | -0.32044 | 121.1334 | 0.084305 | 0.012405 | -0.0048599 | 0.01468 | 0.051823 | -0.01374 | 0.065834 | -0.35706 | 121.0876 | -0.45776 | -0.25177 | 120.4285 | 1.9363 | 0.13733 | 0.13733 | 121.2067 | -0.48065 | -0.13733 | -0.045777 | -0.036621 | 0.068665 | -0.70496 | -0.16022 | 0.073242 | 0.10071 | 0.45776 | 0.45776 | 120.7489 | 121.4081 | -0.036621 | 121.5271 | 2.2568 | -0.16022 | 121.4081 | -0.036621 | 2.2568 | 120.7489 | 121.5271 | -121.5912 | -121.6141
1700.7344 | 121.669 | -0.34332 | 121.1243 | 0.099564 | 0.012619 | -0.0027237 | 0.011262 | 0.049687 | -0.010536 | 0.066475 | -0.35248 | 121.0373 | -0.4715 | -0.27008 | 120.4697 | 1.9272 | 0.10071 | 0.14191 | 121.1838 | -0.50812 | -0.12817 | -0.086976 | -0.009155 | 0.073242 | -0.6546 | -0.16479 | 0.059509 | 0.11902 | 0.44403 | 0.48523 | 120.813 | 121.3806 | -0.009155 | 121.5271 | 2.2705 | -0.16479 | 121.3806 | -0.009155 | 2.2705 | 120.813 | 121.5271 | -121.5958 | -121.6324
1702.4531 | 121.637 | -0.37537 | 121.1655 | 0.046158 | 0.010269 | -0.0052873 | 0.01468 | 0.053532 | -0.012458 | 0.065407 | -0.34332 | 121.0373 | -0.48523 | -0.27008 | 120.4559 | 1.9547 | 0.19684 | 0.18768 | 121.2021 | -0.51727 | -0.10986 | -0.12817 | 0.032043 | 0.10528 | -0.70953 | -0.14191 | 0.036621 | 0.14191 | 0.5722 | 0.56305 | 120.8313 | 121.4127 | 0.032043 | 121.5775 | 2.33 | -0.14191 | 121.4127 | 0.032043 | 2.33 | 120.8313 | 121.5775 | -121.6507 | -121.6827
1704.1875 | 121.6782 | -0.37994 | 121.138 | 0.099564 | 0.0139 | -0.0042191 | 0.010408 | 0.052677 | -0.012886 | 0.067757 | -0.38452 | 121.019 | -0.50354 | -0.30212 | 120.4605 | 1.9409 | 0.09613 | 0.15564 | 121.1975 | -0.52643 | -0.1236 | -0.11902 | -0.004577 | 0.07782 | -0.67749 | -0.14648 | 0.05951 | 0.11902 | 0.47607 | 0.53558 | 120.8405 | 121.3989 | -0.004577 | 121.5775 | 2.3209 | -0.14648 | 121.3989 | -0.004577 | 2.3209 | 120.8405 | 121.5775 | -121.6415 | -121.6644
1705.9062 | 121.6324 | -0.43945 | 121.1105 | -0.14458 | 0.011551 | -0.0052873 | 0.005708 | 0.049046 | -0.0075452 | 0.065834 | -0.32959 | 120.9961 | -0.49439 | -0.22888 | 120.5475 | 2.1469 | 0.24261 | 0.54016 | 121.106 | -0.54932 | -0.054932 | -0.11444 | 0.10986 | 0.21057 | -0.56305 | -0.10986 | -0.004578 | 0.1648 | 0.68207 | 0.97961 | 120.9869 | 121.4355 | 0.10986 | 121.5454 | 2.5864 | -0.10986 | 121.4355 | 0.10986 | 2.5864 | 120.9869 | 121.5454 | -121.6049 | -121.6599
1707.6562 | 121.6507 | -0.48523 | 121.0648 | -0.13695 | 0.012191 | -0.0084915 | 0.0059216 | 0.048619 | -0.0079724 | 0.065834 | -0.37994 | 120.9457 | -0.54474 | -0.27924 | 120.5017 | 2.1652 | 0.25177 | 0.53101 | 121.051 | -0.58594 | -0.05951 | -0.11902 | 0.10529 | 0.20599 | -0.56305 | -0.10071 | -0.013733 | 0.16479 | 0.737 | 1.0162 | 120.9869 | 121.431 | 0.10529 | 121.5363 | 2.6505 | -0.10071 | 121.431 | 0.10529 | 2.6505 | 120.9869 | 121.5363 | -121.6095 | -121.6507
1709.375 | 121.6553 | -0.48065 | 121.0419 | 0.091934 | 0.015182 | -0.0016557 | 0.016389 | 0.051396 | -0.011818 | 0.065193 | -0.44403 | 121.0144 | -0.6134 | -0.39368 | 120.3598 | 1.9775 | 0.19684 | 0.17395 | 121.1334 | -0.63629 | -0.13275 | -0.027466 | 0.036621 | 0.086975 | -0.68207 | -0.15564 | 0.091553 | 0.16937 | 0.67749 | 0.6546 | 120.8405 | 121.4951 | 0.036621 | 121.6141 | 2.4582 | -0.15564 | 121.4951 | 0.036621 | 2.4582 | 120.8405 | 121.6141 | -121.6553 | -121.6782
1711.1562 | 121.5912 | -0.52643 | 121.106 | -0.19035 | 0.0089872 | -0.0061417 | 0.0069898 | 0.048832 | -0.010109 | 0.066689 | -0.37537 | 120.9503 | -0.55389 | -0.25177 | 120.5338 | 2.2064 | 0.31128 | 0.61798 | 121.1014 | -0.60883 | -0.027466 | -0.15564 | 0.15106 | 0.27466 | -0.5722 | -0.082398 | -0.004578 | 0.17853 | 0.83771 | 1.1444 | 121.0602 | 121.4767 | 0.15106 | 121.6278 | 2.7328 | -0.082398 | 121.4767 | 0.15106 | 2.7328 | 121.0602 | 121.6278 | -121.6599 | -121.7148
1712.9844 | 121.669 | -0.44403 | 121.106 | 0.1606 | 0.012832 | -0.0074235 | 0.011903 | 0.049473 | -0.011177 | 0.068825 | -0.33417 | 120.9824 | -0.53101 | -0.24719 | 120.5383 | 2.0416 | -0.054932 | 0.29755 | 121.1288 | -0.54474 | -0.086975 | -0.1236 | 0.10986 | 0.19684 | -0.56763 | -0.10071 | 0.022888 | 0.19684 | 0.3891 | 0.74158 | 120.9824 | 121.4264 | 0.10986 | 121.5729 | 2.4857 | -0.10071 | 121.4264 | 0.10986 | 2.4857 | 120.9824 | 121.5729 | -121.637 | -121.6507
1714.6875 | 121.6873 | -0.46234 | 121.0831 | 0.16823 | 0.0098416 | -0.0052873 | 0.012971 | 0.050114 | -0.010963 | 0.066689 | -0.37079 | 120.9641 | -0.53101 | -0.27924 | 120.5154 | 2.0187 | -0.045776 | 0.26093 | 121.1014 | -0.58136 | -0.068665 | -0.11902 | 0.091552 | 0.18311 | -0.56763 | -0.11902 | 0.01831 | 0.16022 | 0.41657 | 0.72327 | 120.9778 | 121.4264 | 0.091552 | 121.5637 | 2.4811 | -0.11902 | 121.4264 | 0.091552 | 2.4811 | 120.9778 | 121.5637 | -121.6141 | -121.6644
1716.4375 | 121.7377 | -0.45319 | 121.1288 | 0.099564 | 0.010269 | -0.0055009 | 0.014039 | 0.052677 | -0.011177 | 0.065621 | -0.45319 | 121.0602 | -0.55389 | -0.37079 | 120.433 | 1.9409 | 0.13275 | 0.13733 | 121.2112 | -0.59052 | -0.10071 | -0.068664 | 0 | 0.082397 | -0.6958 | -0.13733 | 0.082398 | 0.10071 | 0.58594 | 0.59052 | 120.8862 | 121.5134 | 0 | 121.6644 | 2.3941 | -0.13733 | 121.5134 | 0 | 2.3941 | 120.8862 | 121.6644 | -121.6827 | -121.7194
1718.1875 | 121.6187 | -0.5127 | 121.17 | -0.098801 | 0.012619 | -0.0069961 | 0.012117 | 0.05225 | -0.012031 | 0.066475 | -0.3891 | 121.0007 | -0.56305 | -0.30212 | 120.4926 | 2.1103 | 0.25177 | 0.36163 | 121.1792 | -0.59052 | -0.050354 | -0.16937 | 0.1236 | 0.21057 | -0.67749 | -0.07782 | 0.009155 | 0.17395 | 0.76446 | 0.87433 | 121.0052 | 121.5134 | 0.1236 | 121.6919 | 2.623 | -0.07782 | 121.5134 | 0.1236 | 2.623 | 121.0052 | 121.6919 | -121.7331 | -121.7606
1719.8906 | 121.637 | -0.49439 | 121.1334 | -0.030136 | 0.013046 | -0.0072099 | 0.011262 | 0.050968 | -0.014167 | 0.06797 | -0.41657 | 121.0052 | -0.58136 | -0.35248 | 120.4605 | 2.0462 | 0.20599 | 0.26093 | 121.2067 | -0.6134 | -0.086975 | -0.12817 | 0.07782 | 0.14191 | -0.67291 | -0.11902 | 0.073242 | 0.16479 | 0.70038 | 0.75531 | 120.9549 | 121.4996 | 0.07782 | 121.701 | 2.5406 | -0.11902 | 121.4996 | 0.07782 | 2.5406 | 120.9549 | 121.701 | -121.7148 | -121.7468
1721.6562 | 121.6232 | -0.49896 | 121.1472 | -0.11406 | 0.0098416 | -0.0048599 | 0.012544 | 0.051182 | -0.011604 | 0.068398 | -0.39368 | 121.0098 | -0.57678 | -0.32044 | 120.4926 | 2.1469 | 0.29755 | 0.40741 | 121.1929 | -0.60883 | -0.07782 | -0.13733 | 0.10529 | 0.17853 | -0.6546 | -0.10986 | 0.045776 | 0.18311 | 0.79651 | 0.90637 | 120.9915 | 121.5088 | 0.10529 | 121.6919 | 2.6459 | -0.10986 | 121.5088 | 0.10529 | 2.6459 | 120.9915 | 121.6919 | -121.7239 | -121.756
1723.3438 | 121.6415 | -0.50812 | 121.1792 | -0.15984 | 0.013473 | -0.0084915 | 0.0052808 | 0.0499 | -0.0079724 | 0.066475 | -0.36163 | 121.0327 | -0.53101 | -0.26093 | 120.575 | 2.2156 | 0.3479 | 0.58594 | 121.1792 | -0.59509 | -0.022888 | -0.14648 | 0.14648 | 0.24719 | -0.60425 | -0.086975 | 0 | 0.16937 | 0.85602 | 1.0941 | 121.0831 | 121.5408 | 0.14648 | 121.6873 | 2.7237 | -0.086975 | 121.5408 | 0.14648 | 2.7237 | 121.0831 | 121.6873 | -121.7102 | -121.7743
1725.0938 | 121.6873 | -0.49439 | 121.1426 | -0.23613 | 0.011978 | -0.0031509 | 0.008485 | 0.048619 | -0.0096814 | 0.065834 | -0.40283 | 121.0281 | -0.55389 | -0.35706 | 120.5063 | 2.1469 | 0.46234 | 0.51727 | 121.2158 | -0.59967 | -0.059509 | -0.11444 | 0.091553 | 0.13733 | -0.63629 | -0.10529 | 0.073242 | 0.15106 | 0.95673 | 1.0117 | 121.0007 | 121.5225 | 0.091553 | 121.7102 | 2.6413 | -0.10529 | 121.5225 | 0.091553 | 2.6413 | 121.0007 | 121.7102 | -121.6965 | -121.7422
1726.8438 | 121.6827 | -0.4715 | 121.1746 | -0.18272 | 0.011123 | -0.0052873 | 0.010194 | 0.050328 | -0.011818 | 0.066048 | -0.43488 | 121.0968 | -0.55847 | -0.35706 | 120.5109 | 2.1378 | 0.44861 | 0.43945 | 121.225 | -0.61798 | -0.086975 | -0.07782 | 0.036622 | 0.11444 | -0.66376 | -0.14648 | 0.050354 | 0.1236 | 0.9201 | 0.91095 | 120.9824 | 121.5683 | 0.036622 | 121.6965 | 2.6093 | -0.14648 | 121.5683 | 0.036622 | 2.6093 | 120.9824 | 121.6965 | -121.7331 | -121.7926
1728.5938 | 121.7148 | -0.50354 | 121.1609 | -0.24376 | 0.012405 | -0.0084915 | 0.0099804 | 0.047764 | -0.011818 | 0.063912 | -0.48065 | 121.0602 | -0.59967 | -0.37994 | 120.4605 | 2.124 | 0.50354 | 0.45319 | 121.2021 | -0.64545 | -0.09613 | -0.10071 | 0.022888 | 0.1236 | -0.70038 | -0.14191 | 0.041198 | 0.11902 | 1.0071 | 0.95673 | 120.9641 | 121.5637 | 0.022888 | 121.7056 | 2.6276 | -0.14191 | 121.5637 | 0.022888 | 2.6276 | 120.9641 | 121.7056 | -121.7606 | -121.8063
1730.2812 | 121.6644 | -0.52185 | 121.1655 | -0.083542 | 0.011123 | -0.0031509 | 0.01468 | 0.050541 | -0.01139 | 0.067543 | -0.42572 | 121.0144 | -0.59509 | -0.32959 | 120.5246 | 2.1286 | 0.25177 | 0.36621 | 121.2021 | -0.6134 | -0.073242 | -0.15106 | 0.096131 | 0.19226 | -0.64087 | -0.091552 | 0.036621 | 0.16937 | 0.77362 | 0.88806 | 121.0464 | 121.5363 | 0.096131 | 121.7239 | 2.6505 | -0.091552 | 121.5363 | 0.096131 | 2.6505 | 121.0464 | 121.7239 | -121.7606 | -121.7789
1732.0312 | 121.7194 | -0.53558 | 121.1426 | -0.13695 | 0.012405 | -0.0067825 | 0.0044262 | 0.050968 | -0.0079724 | 0.065834 | -0.38452 | 121.0281 | -0.5722 | -0.27924 | 120.5978 | 2.1927 | 0.24261 | 0.5722 | 121.1563 | -0.6134 | -0.036622 | -0.11444 | 0.15106 | 0.25635 | -0.54474 | -0.07782 | 0.013733 | 0.18768 | 0.7782 | 1.1078 | 121.1334 | 121.5637 | 0.15106 | 121.6919 | 2.7283 | -0.07782 | 121.5637 | 0.15106 | 2.7283 | 121.1334 | 121.6919 | -121.7148 | -121.756
1733.7812 | 121.7697 | -0.52185 | 121.1472 | 0.14534 | 0.010055 | -0.0029373 | 0.012117 | 0.051396 | -0.011604 | 0.068184 | -0.38452 | 121.0327 | -0.55389 | -0.27924 | 120.5795 | 2.0782 | -0.059509 | 0.27466 | 121.1334 | -0.59052 | -0.032043 | -0.11444 | 0.13733 | 0.24261 | -0.56763 | -0.068664 | -0.013733 | 0.16937 | 0.46234 | 0.79651 | 121.1014 | 121.5546 | 0.13733 | 121.6553 | 2.6001 | -0.068664 | 121.5546 | 0.13733 | 2.6001 | 121.1014 | 121.6553 | -121.701 | -121.7377
1735.4688 | 121.701 | -0.50812 | 121.1975 | -0.18272 | 0.01091 | -0.0055009 | 0.013398 | 0.050541 | -0.012031 | 0.065407 | -0.46234 | 121.0831 | -0.59052 | -0.35706 | 120.5292 | 2.1561 | 0.3891 | 0.43488 | 121.2204 | -0.62256 | -0.082397 | -0.11444 | 0.045777 | 0.15106 | -0.66833 | -0.11444 | 0.022888 | 0.12817 | 0.89722 | 0.94299 | 121.0373 | 121.5912 | 0.045777 | 121.7285 | 2.6642 | -0.11444 | 121.5912 | 0.045777 | 2.6642 | 121.0373 | 121.7285 | -121.788 | -121.8201
1737.2344 | 121.6827 | -0.50354 | 121.225 | -0.14458 | 0.013473 | -0.0076371 | 0.013612 | 0.049046 | -0.01139 | 0.067116 | -0.42114 | 121.0785 | -0.5722 | -0.34332 | 120.5566 | 2.1515 | 0.34332 | 0.41657 | 121.2296 | -0.61798 | -0.068665 | -0.14648 | 0.082397 | 0.16022 | -0.66833 | -0.11444 | 0.004577 | 0.15106 | 0.84686 | 0.9201 | 121.0602 | 121.582 | 0.082397 | 121.7331 | 2.655 | -0.11444 | 121.582 | 0.082397 | 2.655 | 121.0602 | 121.7331 | -121.7972 | -121.843
1739 | 121.6919 | -0.51727 | 121.2387 | -0.19035 | 0.010482 | -0.0069961 | 0.0065624 | 0.048191 | -0.01075 | 0.068184 | -0.35248 | 121.1014 | -0.52643 | -0.26093 | 120.639 | 2.2385 | 0.31586 | 0.6134 | 121.225 | -0.57678 | -0.009155 | -0.13733 | 0.16479 | 0.25635 | -0.59967 | -0.059509 | -0.013732 | 0.17395 | 0.83313 | 1.1307 | 121.1563 | 121.6187 | 0.16479 | 121.7422 | 2.7557 | -0.059509 | 121.6187 | 0.16479 | 2.7557 | 121.1563 | 121.7422 | -121.7651 | -121.8155
1740.75 | 121.6919 | -0.50812 | 121.2387 | -0.10643 | 0.012191 | -0.0018693 | 0.015321 | 0.050755 | -0.011604 | 0.068184 | -0.41657 | 121.0785 | -0.55847 | -0.32501 | 120.5566 | 2.1606 | 0.29297 | 0.39825 | 121.2479 | -0.60883 | -0.050354 | -0.16022 | 0.091553 | 0.18311 | -0.68207 | -0.10071 | 0.009156 | 0.14191 | 0.80109 | 0.90637 | 121.0648 | 121.5866 | 0.091553 | 121.756 | 2.6688 | -0.10071 | 121.5866 | 0.091553 | 2.6688 | 121.0648 | 121.756 | -121.7972 | -121.8475
1742.4531 | 121.6873 | -0.50354 | 121.2479 | -0.098801 | 0.011123 | -0.0037919 | 0.012758 | 0.050114 | -0.011604 | 0.066689 | -0.40283 | 121.1105 | -0.55847 | -0.31586 | 120.5795 | 2.1606 | 0.27466 | 0.39825 | 121.2662 | -0.59509 | -0.054932 | -0.13733 | 0.10071 | 0.18768 | -0.66834 | -0.091553 | 0.01831 | 0.15564 | 0.7782 | 0.90179 | 121.0831 | 121.6141 | 0.10071 | 121.7697 | 2.6642 | -0.091553 | 121.6141 | 0.10071 | 2.6642 | 121.0831 | 121.7697 | -121.8063 | -121.843
1744.2031 | 121.8018 | -0.46234 | 121.2067 | -0.060654 | 0.010482 | -0.0052873 | 0.0050672 | 0.048619 | -0.0069042 | 0.069039 | -0.38452 | 121.1243 | -0.51727 | -0.27466 | 120.6299 | 2.1698 | 0.23804 | 0.49439 | 121.2341 | -0.59052 | -0.054932 | -0.082397 | 0.07782 | 0.18768 | -0.57678 | -0.12817 | 0.027466 | 0.13275 | 0.70038 | 0.95673 | 121.0922 | 121.5866 | 0.07782 | 121.6965 | 2.6321 | -0.12817 | 121.5866 | 0.07782 | 2.6321 | 121.0922 | 121.6965 | -121.7239 | -121.7972
1745.9531 | 121.8338 | -0.43488 | 121.2112 | 0.0080111 | 0.013046 | -0.0057145 | 0.007417 | 0.047764 | -0.010536 | 0.065621 | -0.40283 | 121.1105 | -0.54016 | -0.32044 | 120.5887 | 2.1057 | 0.20142 | 0.39368 | 121.2341 | -0.58594 | -0.10529 | -0.10071 | 0.032043 | 0.11444 | -0.62256 | -0.15106 | 0.022888 | 0.13733 | 0.63629 | 0.82855 | 121.0236 | 121.5454 | 0.032043 | 121.669 | 2.5406 | -0.15106 | 121.5454 | 0.032043 | 2.5406 | 121.0236 | 121.669 | -121.7514 | -121.7972
1747.7188 | 121.7285 | -0.48065 | 121.2479 | -0.19798 | 0.012191 | -0.0025101 | 0.014467 | 0.049046 | -0.010109 | 0.063271 | -0.42572 | 121.1746 | -0.55389 | -0.32959 | 120.5612 | 2.1515 | 0.42572 | 0.4303 | 121.2845 | -0.59967 | -0.073242 | -0.073242 | 0.054932 | 0.15106 | -0.68665 | -0.11902 | 0.036621 | 0.12817 | 0.90637 | 0.91095 | 121.0419 | 121.6553 | 0.054932 | 121.7651 | 2.6321 | -0.11902 | 121.6553 | 0.054932 | 2.6321 | 121.0419 | 121.7651 | -121.8018 | -121.8475
1749.4688 | 121.8475 | -0.43945 | 121.2067 | 0.099564 | 0.010482 | -0.0050735 | 0.012544 | 0.05225 | -0.012031 | 0.067543 | -0.44403 | 121.1288 | -0.55847 | -0.35706 | 120.5704 | 1.9913 | 0.091553 | 0.15106 | 121.3303 | -0.58136 | -0.11902 | -0.07782 | -0.004578 | 0.082397 | -0.63629 | -0.14191 | 0.1236 | 0.11444 | 0.53101 | 0.59052 | 121.0098 | 121.5683 | -0.004578 | 121.7697 | 2.4307 | -0.14191 | 121.5683 | -0.004578 | 2.4307 | 121.0098 | 121.7697 | -121.7651 | -121.788
1751.1562 | 121.8475 | -0.4303 | 121.2158 | 0.053787 | 0.01091 | -0.0093461 | 0.011476 | 0.050755 | -0.012245 | 0.067543 | -0.44861 | 121.1792 | -0.54474 | -0.3479 | 120.5246 | 2.0142 | 0.16479 | 0.15564 | 121.312 | -0.58594 | -0.11444 | -0.036621 | -0.01831 | 0.082398 | -0.69122 | -0.15564 | 0.096131 | 0.096131 | 0.59509 | 0.58594 | 120.9549 | 121.6095 | -0.01831 | 121.7422 | 2.4445 | -0.15564 | 121.6095 | -0.01831 | 2.4445 | 120.9549 | 121.7422 | -121.7606 | -121.8018
1752.9219 | 121.8704 | -0.41657 | 121.2158 | 0.091934 | 0.01326 | -0.0052873 | 0.01233 | 0.050968 | -0.010963 | 0.06733 | -0.42114 | 121.1792 | -0.53101 | -0.36163 | 120.575 | 1.9867 | 0.12817 | 0.12817 | 121.3531 | -0.58136 | -0.11444 | -0.036621 | -0.004578 | 0.054932 | -0.64087 | -0.16479 | 0.13733 | 0.10986 | 0.54474 | 0.54474 | 120.9915 | 121.5958 | -0.004578 | 121.7697 | 2.4033 | -0.16479 | 121.5958 | -0.004578 | 2.4033 | 120.9915 | 121.7697 | -121.7468 | -121.7972
1754.6094 | 121.756 | -0.46234 | 121.2799 | -0.075912 | 0.011551 | -0.0050735 | 0.011689 | 0.049687 | -0.012458 | 0.068611 | -0.36621 | 121.1655 | -0.53558 | -0.27924 | 120.639 | 2.1286 | 0.2243 | 0.33417 | 121.3257 | -0.57678 | -0.073242 | -0.11444 | 0.09613 | 0.18311 | -0.64087 | -0.11444 | 0.045777 | 0.16937 | 0.68664 | 0.79651 | 121.1014 | 121.6278 | 0.09613 | 121.788 | 2.5909 | -0.11444 | 121.6278 | 0.09613 | 2.5909 | 121.1014 | 121.788 | -121.8155 | -121.8567
1756.3438 | 121.8246 | -0.41657 | 121.2662 | 0.15297 | 0.011764 | -0.0042191 | 0.0059216 | 0.04755 | -0.0094678 | 0.067116 | -0.32044 | 121.1838 | -0.49896 | -0.23346 | 120.7031 | 2.1194 | 0 | 0.31586 | 121.257 | -0.54016 | -0.082397 | -0.082397 | 0.09613 | 0.18311 | -0.56305 | -0.1236 | -0.009155 | 0.17853 | 0.41657 | 0.73242 | 121.1197 | 121.6003 | 0.09613 | 121.6736 | 2.536 | -0.1236 | 121.6003 | 0.09613 | 2.536 | 121.1197 | 121.6736 | -121.7651 | -121.8063
1758.125 | 121.8384 | -0.44403 | 121.3074 | -0.10643 | 0.013473 | -0.0050735 | 0.0054944 | 0.048405 | -0.0077588 | 0.066048 | -0.35248 | 121.1838 | -0.47607 | -0.2243 | 120.7214 | 2.2064 | 0.26093 | 0.52643 | 121.3165 | -0.54016 | -0.032043 | -0.1236 | 0.091553 | 0.21973 | -0.58594 | -0.09613 | 0.009155 | 0.1236 | 0.70496 | 0.97046 | 121.1655 | 121.6278 | 0.091553 | 121.7606 | 2.6505 | -0.09613 | 121.6278 | 0.091553 | 2.6505 | 121.1655 | 121.7606 | -121.7834 | -121.8475
1759.8281 | 121.8796 | -0.3891 | 121.2708 | 0.00038159 | 0.01326 | -0.0087051 | 0.007417 | 0.048405 | -0.0096814 | 0.066048 | -0.36163 | 121.2112 | -0.48981 | -0.27924 | 120.6802 | 2.1057 | 0.21973 | 0.39368 | 121.3211 | -0.54474 | -0.10071 | -0.059509 | 0.027466 | 0.10986 | -0.59051 | -0.15564 | 0.050354 | 0.12817 | 0.60883 | 0.78278 | 121.0693 | 121.6003 | 0.027466 | 121.7102 | 2.4948 | -0.15564 | 121.6003 | 0.027466 | 2.4948 | 121.0693 | 121.7102 | -121.7606 | -121.8155
1761.5625 | 121.8018 | -0.45776 | 121.312 | -0.13695 | 0.011337 | -0.0061417 | 0.0078442 | 0.048619 | -0.012458 | 0.06498 | -0.31128 | 121.1929 | -0.48523 | -0.20142 | 120.7443 | 2.243 | 0.25177 | 0.57678 | 121.3211 | -0.53558 | -0.027465 | -0.11902 | 0.14649 | 0.25635 | -0.56763 | -0.077819 | 0.009155 | 0.17395 | 0.70953 | 1.0345 | 121.2021 | 121.6507 | 0.14649 | 121.7789 | 2.7008 | -0.077819 | 121.6507 | 0.14649 | 2.7008 | 121.2021 | 121.7789 | -121.7972 | -121.8475
1763.25 | 121.7651 | -0.48981 | 121.3669 | -0.20561 | 0.0094144 | -0.0093461 | 0.010621 | 0.049687 | -0.0092542 | 0.066048 | -0.29755 | 121.1838 | -0.4715 | -0.20599 | 120.7397 | 2.2705 | 0.33875 | 0.60883 | 121.3394 | -0.53101 | 0.01831 | -0.1831 | 0.19226 | 0.28381 | -0.62714 | -0.041199 | -0.027465 | 0.17395 | 0.82855 | 1.0986 | 121.2296 | 121.6736 | 0.19226 | 121.8292 | 2.7603 | -0.041199 | 121.6736 | 0.19226 | 2.7603 | 121.2296 | 121.8292 | -121.8384 | -121.8979
1765 | 121.8887 | -0.38452 | 121.3211 | 0.10719 | 0.009628 | -0.0042191 | 0.014467 | 0.0499 | -0.011604 | 0.066262 | -0.37994 | 121.2387 | -0.49896 | -0.27466 | 120.6528 | 2.0096 | 0.10071 | 0.16937 | 121.3806 | -0.53101 | -0.11444 | -0.082398 | 0.004577 | 0.10986 | -0.66833 | -0.14648 | 0.059509 | 0.11902 | 0.48523 | 0.55389 | 121.0373 | 121.6232 | 0.004577 | 121.7651 | 2.3941 | -0.14648 | 121.6232 | 0.004577 | 2.3941 | 121.0373 | 121.7651 | -121.8201 | -121.8521
1766.75 | 121.8796 | -0.3479 | 121.3669 | -0.014877 | 0.009628 | -0.0048599 | 0.005708 | 0.049046 | -0.0092542 | 0.067116 | -0.30212 | 121.2753 | -0.4303 | -0.1831 | 120.7764 | 2.1606 | 0.20599 | 0.42114 | 121.3943 | -0.46234 | -0.082398 | -0.091552 | 0.045776 | 0.16479 | -0.59052 | -0.11444 | 0.027466 | 0.12817 | 0.55389 | 0.76904 | 121.1243 | 121.6232 | 0.045776 | 121.7422 | 2.5085 | -0.11444 | 121.6232 | 0.045776 | 2.5085 | 121.1243 | 121.7422 | -121.7972 | -121.8292
1768.4375 | 121.7697 | -0.39825 | 121.4172 | -0.21324 | 0.011551 | -0.0059281 | 0.0099804 | 0.049046 | -0.011818 | 0.065834 | -0.22888 | 121.2936 | -0.41657 | -0.11902 | 120.8267 | 2.2842 | 0.32959 | 0.62256 | 121.4218 | -0.44403 | -0.018311 | -0.1236 | 0.16937 | 0.27924 | -0.59051 | -0.045777 | 0.004578 | 0.18768 | 0.72784 | 1.0208 | 121.225 | 121.6919 | 0.16937 | 121.8201 | 2.6825 | -0.045777 | 121.6919 | 0.16937 | 2.6825 | 121.225 | 121.8201 | -121.8338 | -121.8613
1770.1875 | 121.8201 | -0.36621 | 121.4401 | 0.030899 | 0.013473 | -0.0042191 | 0.014467 | 0.048191 | -0.012672 | 0.06733 | -0.28381 | 121.3257 | -0.4303 | -0.20599 | 120.7169 | 2.0828 | 0.1831 | 0.21973 | 121.4584 | -0.48981 | -0.064087 | -0.11444 | 0.082398 | 0.16022 | -0.72327 | -0.1236 | 0.01831 | 0.14649 | 0.54932 | 0.58594 | 121.0831 | 121.6919 | 0.082398 | 121.8246 | 2.449 | -0.1236 | 121.6919 | 0.082398 | 2.449 | 121.0831 | 121.8246 | -121.8704 | -121.9299
1771.9375 | 121.8475 | -0.32044 | 121.4035 | 0.14534 | 0.012832 | -0.00037386 | 0.01233 | 0.051609 | -0.0096814 | 0.065621 | -0.19684 | 121.312 | -0.3891 | -0.11444 | 120.8405 | 2.1103 | -0.054932 | 0.27466 | 121.4447 | -0.43488 | -0.068664 | -0.091552 | 0.1236 | 0.20599 | -0.56305 | -0.11444 | 0.041199 | 0.19226 | 0.2655 | 0.59509 | 121.1609 | 121.6324 | 0.1236 | 121.7651 | 2.4307 | -0.11444 | 121.6324 | 0.1236 | 2.4307 | 121.1609 | 121.7651 | -121.7926 | -121.8384
1773.7031 | 121.8201 | -0.31586 | 121.4539 | 0.02327 | 0.013473 | -0.0084915 | 0.013612 | 0.050541 | -0.0094678 | 0.067543 | -0.26093 | 121.3531 | -0.39825 | -0.18768 | 120.7581 | 2.0645 | 0.19684 | 0.21515 | 121.4951 | -0.45319 | -0.082397 | -0.10071 | 0.054932 | 0.12817 | -0.6958 | -0.13733 | 0.041199 | 0.13733 | 0.5127 | 0.53101 | 121.0739 | 121.669 | 0.054932 | 121.8109 | 2.3804 | -0.13733 | 121.669 | 0.054932 | 2.3804 | 121.0739 | 121.8109 | -121.8521 | -121.907
1775.4375 | 121.8155 | -0.29755 | 121.4996 | -0.014877 | 0.011123 | -0.0042191 | 0.013398 | 0.052677 | -0.01139 | 0.066689 | -0.24719 | 121.3623 | -0.3891 | -0.14648 | 120.7993 | 2.1149 | 0.21057 | 0.27466 | 121.5225 | -0.39825 | -0.091553 | -0.13733 | 0.050354 | 0.15106 | -0.70038 | -0.10071 | 0.022888 | 0.14191 | 0.50812 | 0.5722 | 121.0968 | 121.6599 | 0.050354 | 121.8201 | 2.4124 | -0.10071 | 121.6599 | 0.050354 | 2.4124 | 121.0968 | 121.8201 | -121.8887 | -121.8979
1777.125 | 121.875 | -0.26093 | 121.4676 | 0.14534 | 0.010482 | -0.0061417 | 0.0082714 | 0.051609 | -0.010109 | 0.067116 | -0.18768 | 121.3623 | -0.3479 | -0.082397 | 120.8862 | 2.124 | -0.032043 | 0.2655 | 121.5134 | -0.37537 | -0.086975 | -0.10528 | 0.073242 | 0.17853 | -0.58136 | -0.11444 | 0.045777 | 0.16022 | 0.22888 | 0.52643 | 121.1472 | 121.6232 | 0.073242 | 121.7743 | 2.3849 | -0.11444 | 121.6232 | 0.073242 | 2.3849 | 121.1472 | 121.7743 | -121.8155 | -121.843
1778.875 | 121.8018 | -0.31586 | 121.5225 | -0.17509 | 0.0092008 | -0.0052873 | 0.0078442 | 0.049687 | -0.010109 | 0.065193 | -0.16937 | 121.3715 | -0.33417 | -0.068665 | 120.9137 | 2.2888 | 0.33875 | 0.60425 | 121.5179 | -0.39825 | -0.01831 | -0.15106 | 0.14648 | 0.24719 | -0.60883 | -0.082397 | -0.004578 | 0.16479 | 0.6546 | 0.9201 | 121.2296 | 121.6873 | 0.14648 | 121.8338 | 2.6047 | -0.082397 | 121.6873 | 0.14648 | 2.6047 | 121.2296 | 121.8338 | -121.8567 | -121.9208
1780.6406 | 121.9208 | -0.26093 | 121.4767 | -0.022507 | 0.010269 | -0.0052873 | 0.0086988 | 0.049046 | -0.008186 | 0.065621 | -0.20142 | 121.4127 | -0.32959 | -0.10529 | 120.9045 | 2.1881 | 0.22888 | 0.45319 | 121.5317 | -0.39368 | -0.068665 | -0.064087 | 0.059509 | 0.15564 | -0.57221 | -0.13275 | 0.054931 | 0.12817 | 0.48981 | 0.71411 | 121.1655 | 121.6736 | 0.059509 | 121.7926 | 2.449 | -0.13275 | 121.6736 | 0.059509 | 2.449 | 121.1655 | 121.7926 | -121.8063 | -121.8704
1782.3906 | 121.8979 | -0.24719 | 121.4859 | 0.1606 | 0.010696 | -0.0080643 | 0.013826 | 0.047978 | -0.0096814 | 0.065621 | -0.21973 | 121.4127 | -0.36163 | -0.10071 | 120.8588 | 2.0782 | 0.009155 | 0.21973 | 121.5363 | -0.37994 | -0.11444 | -0.073242 | 0.027465 | 0.14648 | -0.62714 | -0.13275 | 0.050354 | 0.14191 | 0.25635 | 0.46692 | 121.106 | 121.6599 | 0.027465 | 121.7834 | 2.3254 | -0.13275 | 121.6599 | 0.027465 | 2.3254 | 121.106 | 121.7834 | -121.8475 | -121.8658
1784.1406 | 121.8338 | -0.27466 | 121.5408 | -0.12169 | 0.010482 | -0.0029373 | 0.0061352 | 0.048405 | -0.010322 | 0.066048 | -0.14648 | 121.3943 | -0.32501 | -0.045776 | 120.9641 | 2.2751 | 0.2655 | 0.58136 | 121.5271 | -0.36163 | -0.050354 | -0.14649 | 0.12817 | 0.22888 | -0.57678 | -0.086975 | -0.013733 | 0.17853 | 0.54016 | 0.85602 | 121.2387 | 121.669 | 0.12817 | 121.8018 | 2.5497 | -0.086975 | 121.669 | 0.12817 | 2.5497 | 121.2387 | 121.8018 | -121.8658 | -121.9025
1785.8438 | 121.7926 | -0.29755 | 121.5271 | -0.20561 | 0.009628 | -0.0059281 | 0.009126 | 0.048191 | -0.012031 | 0.065834 | -0.13275 | 121.4218 | -0.32501 | -0.036621 | 120.9549 | 2.3071 | 0.33875 | 0.6134 | 121.5317 | -0.37079 | -0.027466 | -0.10529 | 0.16479 | 0.26092 | -0.57221 | -0.073243 | 0.004577 | 0.19226 | 0.63629 | 0.91095 | 121.2524 | 121.7194 | 0.16479 | 121.8292 | 2.6047 | -0.073243 | 121.7194 | 0.16479 | 2.6047 | 121.2524 | 121.8292 | -121.8521 | -121.8979
1787.5938 | 121.9391 | -0.24719 | 121.5134 | 0.01564 | 0.011551 | -0.0084915 | 0.0080578 | 0.047123 | -0.0094678 | 0.066475 | -0.18768 | 121.431 | -0.31128 | -0.10529 | 120.8954 | 2.1423 | 0.21057 | 0.39368 | 121.5134 | -0.3891 | -0.064087 | -0.082398 | 0.059509 | 0.14191 | -0.61798 | -0.14191 | 0 | 0.1236 | 0.45776 | 0.64087 | 121.1426 | 121.6782 | 0.059509 | 121.7606 | 2.3895 | -0.14191 | 121.6782 | 0.059509 | 2.3895 | 121.1426 | 121.7606 | -121.8246 | -121.9025
1789.3438 | 121.9025 | -0.25177 | 121.5363 | -0.083542 | 0.01091 | -0.0040055 | 0.007417 | 0.047337 | -0.011177 | 0.066475 | -0.16937 | 121.4218 | -0.33417 | -0.045776 | 120.9595 | 2.2476 | 0.25177 | 0.53558 | 121.5546 | -0.35706 | -0.082397 | -0.11444 | 0.082397 | 0.20599 | -0.57678 | -0.10529 | 0.01831 | 0.16479 | 0.50354 | 0.78735 | 121.2112 | 121.6736 | 0.082397 | 121.8063 | 2.4994 | -0.10529 | 121.6736 | 0.082397 | 2.4994 | 121.2112 | 121.8063 | -121.8704 | -121.8933
1791.125 | 121.8475 | -0.27008 | 121.5546 | -0.12932 | 0.0087734 | -0.0069961 | 0.009126 | 0.04755 | -0.0086132 | 0.064125 | -0.11902 | 121.4081 | -0.30212 | -0.013733 | 120.9824 | 2.2888 | 0.27008 | 0.59967 | 121.5591 | -0.35706 | -0.032043 | -0.14648 | 0.15106 | 0.25635 | -0.5722 | -0.086975 | 0.004578 | 0.18311 | 0.54016 | 0.86975 | 121.2524 | 121.6782 | 0.15106 | 121.8292 | 2.5589 | -0.086975 | 121.6782 | 0.15106 | 2.5589 | 121.2524 | 121.8292 | -121.8567 | -121.9116
1792.8281 | 121.843 | -0.27924 | 121.5179 | -0.045395 | 0.011764 | -0.0033647 | 0.018098 | 0.051182 | -0.01374 | 0.066689 | -0.16479 | 121.4493 | -0.35706 | -0.082397 | 120.8908 | 2.1652 | 0.23804 | 0.32044 | 121.6278 | -0.3891 | -0.07782 | -0.068664 | 0.11444 | 0.19684 | -0.62714 | -0.10986 | 0.10986 | 0.19226 | 0.51727 | 0.59967 | 121.17 | 121.7285 | 0.11444 | 121.907 | 2.4445 | -0.10986 | 121.7285 | 0.11444 | 2.4445 | 121.17 | 121.907 | -121.875 | -121.907
1794.5938 | 121.8704 | -0.27466 | 121.5866 | -0.25902 | 0.009628 | -0.0069961 | 0.0099804 | 0.04755 | -0.011818 | 0.066902 | -0.17853 | 121.4584 | -0.34332 | -0.10071 | 120.9 | 2.2293 | 0.47607 | 0.54016 | 121.5866 | -0.37994 | -0.068665 | -0.12817 | 0.09613 | 0.17395 | -0.68665 | -0.10529 | 0 | 0.16479 | 0.75073 | 0.81482 | 121.1746 | 121.7331 | 0.09613 | 121.8613 | 2.504 | -0.10529 | 121.7331 | 0.09613 | 2.504 | 121.1746 | 121.8613 | -121.9299 | -121.9666
1796.3438 | 121.907 | -0.23346 | 121.5637 | -0.22087 | 0.0098416 | -0.0055009 | 0.0093396 | 0.049687 | -0.0086132 | 0.066048 | -0.13733 | 121.4447 | -0.30212 | -0.022888 | 121.0052 | 2.2614 | 0.24261 | 0.55847 | 121.6003 | -0.3479 | -0.068665 | -0.11902 | 0.09613 | 0.21057 | -0.55847 | -0.11444 | 0.036621 | 0.16479 | 0.47607 | 0.79193 | 121.2387 | 121.6782 | 0.09613 | 121.8338 | 2.4948 | -0.11444 | 121.6782 | 0.09613 | 2.4948 | 121.2387 | 121.8338 | -121.8658 | -121.9116
1798.0469 | 121.9254 | -0.2243 | 121.5363 | 0.053787 | 0.01091 | -0.0078507 | 0.016176 | 0.052891 | -0.011604 | 0.066689 | -0.2243 | 121.4813 | -0.35248 | -0.15106 | 120.8542 | 2.0737 | 0.18768 | 0.16937 | 121.6232 | -0.37994 | -0.12817 | -0.054932 | 0 | 0.073242 | -0.68207 | -0.15564 | 0.086975 | 0.12817 | 0.41199 | 0.39368 | 121.0785 | 121.7056 | 0 | 121.8475 | 2.298 | -0.15564 | 121.7056 | 0 | 2.298 | 121.0785 | 121.8475 | -121.8887 | -121.9162
1799.7969 | 121.8246 | -0.27924 | 121.5866 | -0.19035 | 0.011551 | -0.0089189 | 0.0080578 | 0.048832 | -0.01075 | 0.066048 | -0.10986 | 121.463 | -0.29297 | 0 | 121.019 | 2.3209 | 0.33875 | 0.61798 | 121.582 | -0.34332 | -0.013733 | -0.1236 | 0.16937 | 0.27924 | -0.56763 | -0.064087 | -0.004578 | 0.18311 | 0.61798 | 0.89722 | 121.2982 | 121.7422 | 0.16937 | 121.8613 | 2.6001 | -0.064087 | 121.7422 | 0.16937 | 2.6001 | 121.2982 | 121.8613 | -121.8796 | -121.9299
1801.5469 | 121.9025 | -0.23804 | 121.5408 | 0.12245 | 0.01326 | -0.0035783 | 0.01468 | 0.052037 | -0.011818 | 0.06733 | -0.10529 | 121.4722 | -0.29755 | -0.022888 | 121.0052 | 2.1561 | -0.045776 | 0.27924 | 121.5912 | -0.33875 | -0.059509 | -0.068665 | 0.13275 | 0.21515 | -0.53558 | -0.10071 | 0.050354 | 0.19226 | 0.19226 | 0.51727 | 121.2433 | 121.7102 | 0.13275 | 121.8292 | 2.3941 | -0.10071 | 121.7102 | 0.13275 | 2.3941 | 121.2433 | 121.8292 | -121.8384 | -121.8796
1803.25 | 121.875 | -0.25177 | 121.5729 | -0.19798 | 0.012832 | -0.0093461 | 0.013398 | 0.051182 | -0.011177 | 0.068184 | -0.20599 | 121.5225 | -0.33875 | -0.1236 | 120.9091 | 2.2247 | 0.4715 | 0.44403 | 121.6782 | -0.37994 | -0.086975 | -0.050354 | 0.045776 | 0.12817 | -0.66376 | -0.12817 | 0.10529 | 0.13275 | 0.72327 | 0.6958 | 121.1609 | 121.7743 | 0.045776 | 121.9299 | 2.4765 | -0.12817 | 121.7743 | 0.045776 | 2.4765 | 121.1609 | 121.9299 | -121.9116 | -121.9528
1805 | 121.8979 | -0.22888 | 121.5637 | 0.16823 | 0.011764 | -0.0046463 | 0.011049 | 0.052464 | -0.011818 | 0.065621 | -0.091553 | 121.4813 | -0.27466 | -0.004578 | 121.0144 | 2.1744 | -0.041199 | 0.3067 | 121.6141 | -0.3067 | -0.045776 | -0.082398 | 0.13733 | 0.2243 | -0.54932 | -0.07782 | 0.050354 | 0.18311 | 0.18768 | 0.53558 | 121.2433 | 121.7102 | 0.13733 | 121.843 | 2.4033 | -0.07782 | 121.7102 | 0.13733 | 2.4033 | 121.2433 | 121.843 | -121.8384 | -121.8704
1806.75 | 121.8887 | -0.23804 | 121.6095 | -0.20561 | 0.011551 | -0.0074235 | 0.012117 | 0.050755 | -0.01075 | 0.065834 | -0.21057 | 121.5088 | -0.32959 | -0.10529 | 120.9229 | 2.243 | 0.49439 | 0.48065 | 121.6599 | -0.37537 | -0.091553 | -0.10071 | 0.027466 | 0.13275 | -0.68664 | -0.13733 | 0.050354 | 0.11902 | 0.73242 | 0.71869 | 121.1609 | 121.7468 | 0.027466 | 121.8979 | 2.4811 | -0.13733 | 121.7468 | 0.027466 | 2.4811 | 121.1609 | 121.8979 | -121.9391 | -121.9849
1808.4375 | 121.8887 | -0.23346 | 121.5958 | 0.099564 | 0.012619 | -0.0050735 | 0.014467 | 0.050968 | -0.011604 | 0.068398 | -0.1831 | 121.5134 | -0.32044 | -0.11444 | 120.9091 | 2.124 | 0.20142 | 0.21057 | 121.6415 | -0.35706 | -0.086976 | -0.082397 | 0.050354 | 0.11902 | -0.68664 | -0.1236 | 0.045777 | 0.13733 | 0.43488 | 0.44403 | 121.1426 | 121.7468 | 0.050354 | 121.875 | 2.3575 | -0.1236 | 121.7468 | 0.050354 | 2.3575 | 121.1426 | 121.875 | -121.9162 | -121.9528
1810.1875 | 121.8384 | -0.24261 | 121.6232 | -0.083542 | 0.01326 | -0.0067825 | 0.01233 | 0.051823 | -0.010109 | 0.066262 | -0.15106 | 121.5179 | -0.31586 | -0.054932 | 120.9595 | 2.243 | 0.31128 | 0.40283 | 121.6782 | -0.33417 | -0.073242 | -0.10529 | 0.091553 | 0.18768 | -0.66376 | -0.091552 | 0.054932 | 0.16479 | 0.55389 | 0.64545 | 121.2021 | 121.7606 | 0.091553 | 121.9208 | 2.4857 | -0.091552 | 121.7606 | 0.091553 | 2.4857 | 121.2021 | 121.9208 | -121.9391 | -121.9574
1811.875 | 121.8796 | -0.24261 | 121.6187 | -0.18272 | 0.0092008 | -0.0059281 | 0.0093396 | 0.050755 | -0.009895 | 0.065407 | -0.19226 | 121.5134 | -0.30212 | -0.11444 | 120.9457 | 2.2568 | 0.50812 | 0.49896 | 121.6873 | -0.36163 | -0.059509 | -0.10528 | 0.050354 | 0.12817 | -0.67291 | -0.11902 | 0.068665 | 0.10986 | 0.75073 | 0.74158 | 121.1884 | 121.756 | 0.050354 | 121.9299 | 2.4994 | -0.11902 | 121.756 | 0.050354 | 2.4994 | 121.1884 | 121.9299 | -121.9208 | -121.9803
1813.5781 | 121.8338 | -0.23804 | 121.6324 | -0.10643 | 0.01326 | -0.0040055 | 0.013185 | 0.050328 | -0.012886 | 0.065407 | -0.14648 | 121.5454 | -0.3067 | -0.050354 | 120.9824 | 2.2568 | 0.29755 | 0.41657 | 121.6736 | -0.35248 | -0.068665 | -0.086975 | 0.091553 | 0.18768 | -0.65002 | -0.11444 | 0.041199 | 0.16022 | 0.53558 | 0.6546 | 121.2204 | 121.7834 | 0.091553 | 121.9116 | 2.4948 | -0.11444 | 121.7834 | 0.091553 | 2.4948 | 121.2204 | 121.9116 | -121.9391 | -121.9849
1815.3281 | 121.962 | -0.20599 | 121.5912 | 0.084305 | 0.012619 | -0.0010147 | 0.010621 | 0.051823 | -0.010322 | 0.064766 | -0.18768 | 121.5591 | -0.32959 | -0.10529 | 120.9183 | 2.0874 | 0.11444 | 0.1831 | 121.6827 | -0.33875 | -0.1236 | -0.032044 | 0.018311 | 0.10071 | -0.67291 | -0.13275 | 0.091552 | 0.14191 | 0.32044 | 0.3891 | 121.1243 | 121.7651 | 0.018311 | 121.8887 | 2.2934 | -0.13275 | 121.7651 | 0.018311 | 2.2934 | 121.1243 | 121.8887 | -121.9208 | -121.9299
1817.0938 | 121.8658 | -0.23346 | 121.6232 | -0.18272 | 0.012405 | -0.0102 | 0.01233 | 0.049259 | -0.010109 | 0.066689 | -0.17853 | 121.5408 | -0.32501 | -0.082397 | 120.9824 | 2.2614 | 0.37994 | 0.43488 | 121.6873 | -0.33875 | -0.091553 | -0.082397 | 0.054931 | 0.15106 | -0.64087 | -0.10529 | 0.064087 | 0.14648 | 0.6134 | 0.66833 | 121.2158 | 121.7743 | 0.054931 | 121.9208 | 2.4948 | -0.10529 | 121.7743 | 0.054931 | 2.4948 | 121.2158 | 121.9208 | -121.9482 | -121.962
1818.7969 | 121.9025 | -0.24261 | 121.637 | -0.13695 | 0.011551 | -0.0067825 | 0.0035718 | 0.049687 | -0.01139 | 0.066048 | -0.086975 | 121.5454 | -0.27924 | 0.004578 | 121.0739 | 2.3254 | 0.2655 | 0.59052 | 121.6507 | -0.3067 | -0.036621 | -0.091553 | 0.15564 | 0.24719 | -0.56305 | -0.064087 | 0.013733 | 0.19226 | 0.50812 | 0.83313 | 121.3165 | 121.788 | 0.15564 | 121.8933 | 2.5681 | -0.064087 | 121.788 | 0.15564 | 2.5681 | 121.3165 | 121.8933 | -121.9162 | -121.9437
1820.5469 | 121.9116 | -0.2243 | 121.637 | -0.25139 | 0.012405 | -0.0067825 | 0.011689 | 0.051396 | -0.010963 | 0.063271 | -0.17395 | 121.5866 | -0.31586 | -0.10071 | 120.9366 | 2.2476 | 0.5127 | 0.45776 | 121.7422 | -0.3479 | -0.091553 | -0.050354 | 0.050354 | 0.1236 | -0.70038 | -0.1236 | 0.10529 | 0.14191 | 0.737 | 0.68207 | 121.1609 | 121.8109 | 0.050354 | 121.9666 | 2.4719 | -0.1236 | 121.8109 | 0.050354 | 2.4719 | 121.1609 | 121.9666 | -121.9528 | -121.9849
1822.2969 | 121.875 | -0.24261 | 121.6599 | -0.20561 | 0.010696 | -0.0072099 | 0.0076306 | 0.050114 | -0.012031 | 0.065193 | -0.07782 | 121.5408 | -0.27008 | 0.018311 | 121.0739 | 2.3575 | 0.33875 | 0.61798 | 121.6644 | -0.3067 | -0.027466 | -0.11902 | 0.16479 | 0.26093 | -0.58594 | -0.064087 | 0.004578 | 0.19226 | 0.58136 | 0.8606 | 121.3165 | 121.7834 | 0.16479 | 121.907 | 2.6001 | -0.064087 | 121.7834 | 0.16479 | 2.6001 | 121.3165 | 121.907 | -121.9299 | -121.9666
1823.9844 | 121.962 | -0.19684 | 121.6324 | 0.1606 | 0.011337 | -0.0059281 | 0.013826 | 0.051396 | -0.011604 | 0.065834 | -0.14648 | 121.5637 | -0.29297 | -0.064087 | 120.9961 | 2.124 | 0.032043 | 0.20599 | 121.6965 | -0.31586 | -0.096131 | -0.068664 | 0.050354 | 0.13275 | -0.63629 | -0.11902 | 0.064087 | 0.14648 | 0.22888 | 0.40283 | 121.1929 | 121.7606 | 0.050354 | 121.8933 | 2.3209 | -0.11902 | 121.7606 | 0.050354 | 2.3209 | 121.1929 | 121.8933 | -121.9254 | -121.9482
1825.7344 | 121.8979 | -0.21057 | 121.6599 | 0.00038159 | 0.0094144 | -0.0044327 | 0.015962 | 0.052677 | -0.011177 | 0.066689 | -0.13275 | 121.5271 | -0.28839 | -0.07782 | 120.9595 | 2.1744 | 0.21515 | 0.25635 | 121.7194 | -0.32044 | -0.07782 | -0.13275 | 0.07782 | 0.13275 | -0.70038 | -0.10986 | 0.059509 | 0.15564 | 0.42572 | 0.46692 | 121.17 | 121.7377 | 0.07782 | 121.9299 | 2.3849 | -0.10986 | 121.7377 | 0.07782 | 2.3849 | 121.17 | 121.9299 | -121.9482 | -121.9803
1827.4844 | 121.9894 | -0.18768 | 121.6232 | 0.061417 | 0.014541 | -0.0059281 | 0.0089124 | 0.051396 | -0.008827 | 0.066048 | -0.11444 | 121.5454 | -0.24261 | -0.045776 | 121.0281 | 2.1744 | 0.11902 | 0.34332 | 121.7056 | -0.31586 | -0.054932 | -0.07782 | 0.073242 | 0.14191 | -0.59509 | -0.12817 | 0.082397 | 0.12817 | 0.3067 | 0.53101 | 121.2158 | 121.7331 | 0.073242 | 121.8933 | 2.3621 | -0.12817 | 121.7331 | 0.073242 | 2.3621 | 121.2158 | 121.8933 | -121.8658 | -121.9391
1829.25 | 121.8521 | -0.25635 | 121.6873 | -0.10643 | 0.0139 | -0.0037919 | 0.014467 | 0.051396 | -0.012031 | 0.066262 | -0.12817 | 121.5591 | -0.28839 | -0.027466 | 121.0281 | 2.2568 | 0.28381 | 0.3891 | 121.7422 | -0.32501 | -0.032043 | -0.12817 | 0.12817 | 0.22888 | -0.65918 | -0.068664 | 0.054932 | 0.16022 | 0.54016 | 0.64545 | 121.2845 | 121.8155 | 0.12817 | 121.9986 | 2.5131 | -0.068664 | 121.8155 | 0.12817 | 2.5131 | 121.2845 | 121.9986 | -121.9757 | -122.0123
1830.9375 | 121.9162 | -0.21973 | 121.6599 | -0.25139 | 0.012191 | -0.0097733 | 0.008485 | 0.047764 | -0.0090406 | 0.066048 | -0.11902 | 121.5637 | -0.2655 | -0.050354 | 121.0373 | 2.3209 | 0.45776 | 0.55847 | 121.701 | -0.32959 | -0.045776 | -0.09613 | 0.10071 | 0.16937 | -0.62256 | -0.10986 | 0.041199 | 0.14648 | 0.67749 | 0.7782 | 121.257 | 121.7834 | 0.10071 | 121.9208 | 2.5406 | -0.10986 | 121.7834 | 0.10071 | 2.5406 | 121.257 | 121.9208 | -121.9254 | -121.9894
1832.6875 | 122.0169 | -0.17395 | 121.6324 | 0.046158 | 0.011123 | -0.0072099 | 0.0065624 | 0.0499 | -0.0083996 | 0.06797 | -0.11902 | 121.5637 | -0.25177 | -0.041199 | 121.0373 | 2.1927 | 0.15106 | 0.36621 | 121.7102 | -0.29297 | -0.07782 | -0.068664 | 0.054931 | 0.13275 | -0.59509 | -0.11902 | 0.07782 | 0.13275 | 0.32501 | 0.54016 | 121.2112 | 121.7377 | 0.054931 | 121.8842 | 2.3666 | -0.11902 | 121.7377 | 0.054931 | 2.3666 | 121.2112 | 121.8842 | -121.8842 | -121.9254
1834.4375 | 121.994 | -0.16479 | 121.6415 | 0.076676 | 0.010696 | -0.0052873 | 0.014467 | 0.050114 | -0.013099 | 0.06797 | -0.16479 | 121.5775 | -0.28839 | -0.082397 | 120.9869 | 2.124 | 0.07782 | 0.16937 | 121.7514 | -0.32044 | -0.1236 | -0.064087 | 0 | 0.082398 | -0.6546 | -0.15564 | 0.10986 | 0.1236 | 0.24261 | 0.33417 | 121.1517 | 121.7422 | 0 | 121.9162 | 2.2888 | -0.15564 | 121.7422 | 0 | 2.2888 | 121.1517 | 121.9162 | -121.9299 | -121.962
1836.1875 | 121.9528 | -0.20599 | 121.669 | -0.091171 | 0.010482 | -0.0063553 | 0.0078442 | 0.047978 | -0.0096814 | 0.066048 | -0.091553 | 121.5912 | -0.24261 | 0.013733 | 121.1014 | 2.3209 | 0.26093 | 0.54932 | 121.6827 | -0.31586 | -0.036621 | -0.077819 | 0.11444 | 0.21973 | -0.56763 | -0.10986 | 0.013733 | 0.15106 | 0.46692 | 0.75531 | 121.3074 | 121.7972 | 0.11444 | 121.8887 | 2.5269 | -0.10986 | 121.7972 | 0.11444 | 2.5269 | 121.3074 | 121.8887 | -121.9116 | -121.9849
1837.875 | 121.8887 | -0.20599 | 121.6827 | -0.15984 | 0.014328 | -0.0035783 | 0.013826 | 0.051182 | -0.012031 | 0.063912 | -0.13733 | 121.5775 | -0.28839 | -0.036621 | 121.0144 | 2.3026 | 0.37079 | 0.44861 | 121.7194 | -0.32959 | -0.082397 | -0.10528 | 0.068665 | 0.16937 | -0.66833 | -0.1236 | 0.036621 | 0.15106 | 0.57678 | 0.6546 | 121.2204 | 121.7834 | 0.068665 | 121.9254 | 2.5085 | -0.1236 | 121.7834 | 0.068665 | 2.5085 | 121.2204 | 121.9254 | -121.9711 | -122.0123
1839.625 | 122.0215 | -0.17395 | 121.637 | 0.0080111 | 0.010055 | -0.0046463 | 0.0093396 | 0.047978 | -0.010536 | 0.067116 | -0.1236 | 121.55 | -0.26093 | -0.041199 | 121.0419 | 2.2064 | 0.21973 | 0.3891 | 121.7102 | -0.31128 | -0.086975 | -0.086975 | 0.050354 | 0.13275 | -0.59509 | -0.13733 | 0.073242 | 0.13733 | 0.39368 | 0.56305 | 121.2158 | 121.7239 | 0.050354 | 121.8842 | 2.3804 | -0.13733 | 121.7239 | 0.050354 | 2.3804 | 121.2158 | 121.8842 | -121.8979 | -121.9482
1841.3594 | 121.8796 | -0.21973 | 121.6919 | -0.13695 | 0.011978 | -0.0044327 | 0.012758 | 0.049046 | -0.012886 | 0.066689 | -0.09613 | 121.5958 | -0.26093 | -0.027466 | 121.0327 | 2.2842 | 0.31128 | 0.42572 | 121.7697 | -0.3067 | -0.041198 | -0.096131 | 0.1236 | 0.19226 | -0.65918 | -0.086975 | 0.077819 | 0.1648 | 0.53101 | 0.64545 | 121.2524 | 121.8155 | 0.1236 | 121.9894 | 2.504 | -0.086975 | 121.8155 | 0.1236 | 2.504 | 121.2524 | 121.9894 | -121.9528 | -121.9986
1843.0469 | 122.0352 | -0.17853 | 121.6599 | 0.038529 | 0.0092008 | -0.0061417 | 0.0078442 | 0.048191 | -0.010536 | 0.068825 | -0.15106 | 121.5225 | -0.25635 | -0.036621 | 121.0556 | 2.2064 | 0.16479 | 0.37994 | 121.7422 | -0.28381 | -0.07782 | -0.13733 | 0.027466 | 0.14191 | -0.60425 | -0.10528 | 0.082398 | 0.10529 | 0.34332 | 0.55847 | 121.2341 | 121.701 | 0.027466 | 121.9208 | 2.3849 | -0.10528 | 121.701 | 0.027466 | 2.3849 | 121.2341 | 121.9208 | -121.9162 | -121.9437
1844.75 | 122.0306 | -0.17853 | 121.6599 | 0.069046 | 0.011978 | -0.0095597 | 0.007417 | 0.048832 | -0.0096814 | 0.067543 | -0.10986 | 121.5912 | -0.25177 | -0.027466 | 121.0556 | 2.2064 | 0.16022 | 0.35706 | 121.7194 | -0.30212 | -0.073242 | -0.068664 | 0.068665 | 0.15106 | -0.60425 | -0.1236 | 0.059509 | 0.14191 | 0.33874 | 0.53558 | 121.2341 | 121.7697 | 0.068665 | 121.8979 | 2.3849 | -0.1236 | 121.7697 | 0.068665 | 2.3849 | 121.2341 | 121.8979 | -121.9116 | -121.962
1846.5 | 121.8933 | -0.21515 | 121.7285 | -0.20561 | 0.012191 | -0.0025101 | 0.0099804 | 0.050114 | -0.01139 | 0.066262 | -0.064087 | 121.5912 | -0.23804 | 0.045776 | 121.1197 | 2.3849 | 0.34332 | 0.61798 | 121.7239 | -0.27466 | -0.022888 | -0.13733 | 0.15106 | 0.26093 | -0.60883 | -0.059509 | -0.004578 | 0.17395 | 0.55847 | 0.83313 | 121.3348 | 121.8063 | 0.15106 | 121.9391 | 2.6001 | -0.059509 | 121.8063 | 0.15106 | 2.6001 | 121.3348 | 121.9391 | -121.9666 | -122.0032
1848.2812 | 122.0123 | -0.18768 | 121.6965 | 0.11482 | 0.0092008 | -0.0012283 | 0.011903 | 0.049687 | -0.0094678 | 0.064766 | -0.07782 | 121.6095 | -0.22888 | 0 | 121.0785 | 2.1881 | 0.073242 | 0.34332 | 121.7651 | -0.30212 | -0.041199 | -0.086975 | 0.10986 | 0.18768 | -0.61798 | -0.11444 | 0.068665 | 0.15106 | 0.26092 | 0.53101 | 121.2662 | 121.7972 | 0.10986 | 121.9528 | 2.3758 | -0.11444 | 121.7972 | 0.10986 | 2.3758 | 121.2662 | 121.9528 | -121.9254 | -121.9986
1849.9688 | 121.9757 | -0.1831 | 121.6873 | 0.1606 | 0.0139 | -0.0067825 | 0.015321 | 0.050541 | -0.012458 | 0.065407 | -0.10071 | 121.6095 | -0.2655 | 0.027466 | 121.0739 | 2.1927 | -0.018311 | 0.26093 | 121.7148 | -0.29755 | -0.082398 | -0.07782 | 0.082397 | 0.21057 | -0.6134 | -0.11444 | 0.027466 | 0.16479 | 0.16479 | 0.44403 | 121.257 | 121.7926 | 0.082397 | 121.8979 | 2.3758 | -0.11444 | 121.7926 | 0.082397 | 2.3758 | 121.257 | 121.8979 | -121.9528 | -121.9849
1851.7031 | 121.8933 | -0.21515 | 121.701 | -0.18272 | 0.011764 | -0.0065689 | 0.0076306 | 0.051182 | -0.0086132 | 0.06498 | -0.068665 | 121.5866 | -0.22888 | 0.054932 | 121.138 | 2.3621 | 0.32959 | 0.62256 | 121.7331 | -0.29297 | -0.013733 | -0.11444 | 0.14648 | 0.27008 | -0.56305 | -0.07782 | 0.032043 | 0.16022 | 0.54474 | 0.83771 | 121.3531 | 121.8018 | 0.14648 | 121.9482 | 2.5772 | -0.07782 | 121.8018 | 0.14648 | 2.5772 | 121.3531 | 121.9482 | -121.9299 | -121.994
1853.4531 | 121.9437 | -0.19684 | 121.6827 | 0.0080111 | 0.014755 | -0.0069961 | 0.017457 | 0.052037 | -0.011818 | 0.065621 | -0.14191 | 121.582 | -0.28381 | -0.041199 | 121.0052 | 2.1835 | 0.21057 | 0.25177 | 121.8018 | -0.31128 | -0.086975 | -0.10071 | 0.054931 | 0.15564 | -0.67749 | -0.11444 | 0.11902 | 0.14191 | 0.40741 | 0.44861 | 121.2021 | 121.7789 | 0.054931 | 121.9986 | 2.3804 | -0.11444 | 121.7789 | 0.054931 | 2.3804 | 121.2021 | 121.9986 | -121.9666 | -121.994
1855.2188 | 121.9025 | -0.21515 | 121.7194 | -0.19035 | 0.011551 | -0.0059281 | 0.0076306 | 0.047764 | -0.011177 | 0.066475 | -0.054932 | 121.6095 | -0.23804 | 0.045776 | 121.138 | 2.3895 | 0.34332 | 0.63171 | 121.7468 | -0.2655 | -0.022888 | -0.10986 | 0.16022 | 0.26093 | -0.58136 | -0.050354 | 0.027466 | 0.1831 | 0.55847 | 0.84686 | 121.3531 | 121.8246 | 0.16022 | 121.962 | 2.6047 | -0.050354 | 121.8246 | 0.16022 | 2.6047 | 121.3531 | 121.962 | -121.9574 | -121.9849
1856.9062 | 121.994 | -0.16937 | 121.6324 | -0.0072479 | 0.011337 | -0.0016557 | 0.0095532 | 0.048405 | -0.009895 | 0.065834 | -0.12817 | 121.582 | -0.2655 | -0.036621 | 121.0556 | 2.2522 | 0.21515 | 0.41199 | 121.6965 | -0.29755 | -0.09613 | -0.050354 | 0.041199 | 0.13275 | -0.57678 | -0.12817 | 0.064087 | 0.13733 | 0.38452 | 0.58136 | 121.225 | 121.7514 | 0.041199 | 121.8658 | 2.4216 | -0.12817 | 121.7514 | 0.041199 | 2.4216 | 121.225 | 121.8658 | -121.8979 | -121.9299
1858.6562 | 121.962 | -0.19226 | 121.5958 | 0.01564 | 0.0087734 | -0.0057145 | 0.0078442 | 0.047123 | -0.01139 | 0.065834 | -0.1236 | 121.5408 | -0.24719 | -0.027466 | 121.0052 | 2.2339 | 0.2243 | 0.39825 | 121.637 | -0.31586 | -0.054931 | -0.054931 | 0.068665 | 0.16479 | -0.59051 | -0.1236 | 0.041199 | 0.1236 | 0.41656 | 0.59052 | 121.1975 | 121.7331 | 0.068665 | 121.8292 | 2.4261 | -0.1236 | 121.7331 | 0.068665 | 2.4261 | 121.1975 | 121.8292 | -121.843 | -121.9116
1860.3906 | 121.8018 | -0.21057 | 121.6232 | -0.098801 | 0.011123 | -0.0050735 | 0.013398 | 0.049687 | -0.013313 | 0.06498 | -0.10529 | 121.5317 | -0.29297 | -0.009155 | 120.9686 | 2.3026 | 0.31128 | 0.42114 | 121.6736 | -0.32501 | -0.082398 | -0.091553 | 0.10529 | 0.20142 | -0.6546 | -0.11444 | 0.050354 | 0.18768 | 0.52185 | 0.63171 | 121.1792 | 121.7422 | 0.10529 | 121.8842 | 2.5131 | -0.11444 | 121.7422 | 0.10529 | 2.5131 | 121.1792 | 121.8842 | -121.9162 | -121.9482
1862.1562 | 121.8109 | -0.21057 | 121.6324 | -0.14458 | 0.012191 | -0.0048599 | 0.0061352 | 0.049259 | -0.010322 | 0.06498 | -0.068665 | 121.4951 | -0.23804 | 0.064087 | 121.0419 | 2.3712 | 0.26093 | 0.58136 | 121.6187 | -0.27466 | -0.027466 | -0.13733 | 0.14191 | 0.27466 | -0.59051 | -0.064087 | -0.013733 | 0.16937 | 0.4715 | 0.79193 | 121.2524 | 121.7056 | 0.14191 | 121.8292 | 2.5818 | -0.064087 | 121.7056 | 0.14191 | 2.5818 | 121.2524 | 121.8292 | -121.8704 | -121.907
1863.8438 | 121.9162 | -0.17395 | 121.5637 | 0.13008 | 0.012619 | -0.0078507 | 0.015107 | 0.050114 | -0.012458 | 0.065834 | -0.17853 | 121.4859 | -0.29297 | -0.073242 | 120.8771 | 2.1332 | 0.14648 | 0.15564 | 121.6827 | -0.32044 | -0.11902 | -0.07782 | -0.004578 | 0.10071 | -0.68665 | -0.14649 | 0.11902 | 0.11444 | 0.32043 | 0.32959 | 121.051 | 121.6599 | -0.004578 | 121.8567 | 2.3071 | -0.14649 | 121.6599 | -0.004578 | 2.3071 | 121.051 | 121.8567 | -121.8567 | -121.8842
1865.5938 | 121.8521 | -0.17853 | 121.5454 | 0.099564 | 0.011764 | -0.0048599 | 0.011049 | 0.050968 | -0.012245 | 0.068398 | -0.045776 | 121.5179 | -0.24719 | 0.022888 | 120.9686 | 2.2293 | -0.018311 | 0.27924 | 121.5912 | -0.27466 | -0.068664 | -0.027466 | 0.13275 | 0.20142 | -0.57678 | -0.09613 | 0.045777 | 0.20142 | 0.16022 | 0.45776 | 121.1472 | 121.6965 | 0.13275 | 121.7697 | 2.4078 | -0.09613 | 121.6965 | 0.13275 | 2.4078 | 121.1472 | 121.7697 | -121.7926 | -121.8201
1867.3438 | 121.8338 | -0.19226 | 121.5683 | 0.01564 | 0.011337 | -0.0040055 | 0.015107 | 0.049687 | -0.01374 | 0.067757 | -0.15564 | 121.4813 | -0.29297 | -0.073242 | 120.8771 | 2.1881 | 0.21515 | 0.21057 | 121.6324 | -0.31586 | -0.10071 | -0.086975 | 0.036621 | 0.11902 | -0.69122 | -0.1236 | 0.064087 | 0.13733 | 0.40741 | 0.40283 | 121.0693 | 121.6736 | 0.036621 | 121.8246 | 2.3804 | -0.1236 | 121.6736 | 0.036621 | 2.3804 | 121.0693 | 121.8246 | -121.8613 | -121.8842
1869.1094 | 121.8338 | -0.18768 | 121.5637 | 0.18349 | 0.011337 | -0.0072099 | 0.011049 | 0.050968 | -0.009895 | 0.064553 | -0.059509 | 121.4676 | -0.21515 | 0.045776 | 120.9641 | 2.2659 | -0.036621 | 0.31128 | 121.5683 | -0.28381 | -0.027466 | -0.096131 | 0.12817 | 0.23346 | -0.59967 | -0.09613 | 0.004577 | 0.15564 | 0.15106 | 0.49896 | 121.1517 | 121.6553 | 0.12817 | 121.756 | 2.4536 | -0.09613 | 121.6553 | 0.12817 | 2.4536 | 121.1517 | 121.756 | -121.7789 | -121.8475
1870.7969 | 121.7651 | -0.21057 | 121.5317 | -0.014877 | 0.01326 | -0.0089189 | 0.014467 | 0.050968 | -0.010963 | 0.06733 | -0.13733 | 121.4722 | -0.25177 | -0.050354 | 120.8908 | 2.2385 | 0.2243 | 0.27008 | 121.6324 | -0.31586 | -0.041199 | -0.059509 | 0.073242 | 0.16022 | -0.64087 | -0.10529 | 0.10071 | 0.11444 | 0.43488 | 0.48065 | 121.1014 | 121.6827 | 0.073242 | 121.843 | 2.449 | -0.10529 | 121.6827 | 0.073242 | 2.449 | 121.1014 | 121.843 | -121.7834 | -121.8475
1872.5469 | 121.7606 | -0.20142 | 121.5408 | -0.037765 | 0.012405 | -0.0067825 | 0.01233 | 0.052677 | -0.010109 | 0.069466 | -0.13275 | 121.463 | -0.28381 | -0.045776 | 120.8954 | 2.2568 | 0.22888 | 0.30212 | 121.6003 | -0.3067 | -0.082397 | -0.07782 | 0.068665 | 0.15564 | -0.64545 | -0.10529 | 0.059509 | 0.15106 | 0.4303 | 0.50354 | 121.0968 | 121.6644 | 0.068665 | 121.8018 | 2.4582 | -0.10529 | 121.6644 | 0.068665 | 2.4582 | 121.0968 | 121.8018 | -121.8246 | -121.8475
1874.2969 | 121.7926 | -0.2243 | 121.5317 | -0.23613 | 0.011123 | -0.0082779 | 0.007417 | 0.048832 | -0.0096814 | 0.067543 | -0.12817 | 121.4722 | -0.24719 | -0.045776 | 120.9091 | 2.3575 | 0.4715 | 0.55389 | 121.582 | -0.32044 | -0.022888 | -0.059509 | 0.09613 | 0.17853 | -0.62256 | -0.096131 | 0.050354 | 0.11902 | 0.6958 | 0.7782 | 121.1334 | 121.6965 | 0.09613 | 121.8063 | 2.5818 | -0.096131 | 121.6965 | 0.09613 | 2.5818 | 121.1334 | 121.8063 | -121.7789 | -121.8521
1876 | 121.7834 | -0.20599 | 121.5729 | -0.19798 | 0.010482 | -0.0050735 | 0.010408 | 0.048619 | -0.009895 | 0.066048 | -0.17395 | 121.4813 | -0.28381 | -0.091553 | 120.8496 | 2.3163 | 0.52185 | 0.49896 | 121.6324 | -0.32959 | -0.077819 | -0.091553 | 0.032044 | 0.11444 | -0.72327 | -0.1236 | 0.059509 | 0.10986 | 0.72784 | 0.70496 | 121.0556 | 121.6873 | 0.032044 | 121.8384 | 2.5223 | -0.1236 | 121.6873 | 0.032044 | 2.5223 | 121.0556 | 121.8384 | -121.8567 | -121.9025
1877.75 | 121.875 | -0.19226 | 121.5225 | 0.091934 | 0.009628 | -0.0074235 | 0.0065624 | 0.048619 | -0.0094678 | 0.065621 | -0.10529 | 121.4493 | -0.24719 | -0.013733 | 120.9045 | 2.2339 | 0.10529 | 0.3479 | 121.5591 | -0.29755 | -0.054931 | -0.073242 | 0.086975 | 0.17853 | -0.61798 | -0.10528 | 0.036621 | 0.14191 | 0.29755 | 0.54016 | 121.0968 | 121.6415 | 0.086975 | 121.7514 | 2.4261 | -0.10528 | 121.6415 | 0.086975 | 2.4261 | 121.0968 | 121.7514 | -121.7697 | -121.8201
1879.5156 | 121.7377 | -0.21057 | 121.5317 | -0.19035 | 0.011123 | -0.0089189 | 0.011049 | 0.049473 | -0.0096814 | 0.065834 | -0.086975 | 121.431 | -0.23804 | 0.018311 | 120.9457 | 2.3987 | 0.40741 | 0.60883 | 121.6003 | -0.29755 | -0.027466 | -0.10071 | 0.1236 | 0.22888 | -0.58594 | -0.086975 | 0.068665 | 0.15106 | 0.61798 | 0.8194 | 121.1563 | 121.6415 | 0.1236 | 121.8109 | 2.6093 | -0.086975 | 121.6415 | 0.1236 | 2.6093 | 121.1563 | 121.8109 | -121.7697 | -121.8292
1881.2656 | 121.8109 | -0.1831 | 121.5271 | 0.18349 | 0.010055 | -0.0061417 | 0.012544 | 0.048832 | -0.012458 | 0.067116 | -0.054932 | 121.4127 | -0.22888 | 0.032043 | 120.9412 | 2.2568 | -0.022888 | 0.32044 | 121.5637 | -0.29755 | -0.045777 | -0.11444 | 0.12817 | 0.21515 | -0.58594 | -0.11444 | 0.036621 | 0.17395 | 0.16022 | 0.50354 | 121.1243 | 121.5958 | 0.12817 | 121.7468 | 2.4399 | -0.11444 | 121.5958 | 0.12817 | 2.4399 | 121.1243 | 121.7468 | -121.756 | -121.8246
1882.9531 | 121.843 | -0.19226 | 121.5042 | 0.10719 | 0.012619 | -0.0050735 | 0.0089124 | 0.047978 | -0.012031 | 0.066262 | -0.068665 | 121.4264 | -0.25177 | 0.004578 | 120.9137 | 2.2522 | 0.07782 | 0.32959 | 121.55 | -0.30212 | -0.059509 | -0.077819 | 0.1236 | 0.19684 | -0.59051 | -0.10986 | 0.045777 | 0.1831 | 0.27008 | 0.52185 | 121.106 | 121.6187 | 0.1236 | 121.7422 | 2.4445 | -0.10986 | 121.6187 | 0.1236 | 2.4445 | 121.106 | 121.7422 | -121.756 | -121.8063
1884.7031 | 121.8109 | -0.18768 | 121.4676 | 0.11482 | 0.010482 | -0.0059281 | 0.012971 | 0.049259 | -0.010322 | 0.067757 | -0.059509 | 121.4172 | -0.23346 | 0.013733 | 120.9274 | 2.2614 | 0.013733 | 0.32044 | 121.5546 | -0.27924 | -0.045776 | -0.050354 | 0.12817 | 0.20142 | -0.54016 | -0.091553 | 0.086975 | 0.17395 | 0.20142 | 0.50812 | 121.1151 | 121.6049 | 0.12817 | 121.7422 | 2.449 | -0.091553 | 121.6049 | 0.12817 | 2.449 | 121.1151 | 121.7422 | -121.701 | -121.7468
1886.4531 | 121.7148 | -0.21515 | 121.5454 | -0.18272 | 0.011337 | -0.0063553 | 0.011049 | 0.049473 | -0.010963 | 0.067116 | -0.059509 | 121.4081 | -0.23346 | 0.032043 | 120.9412 | 2.4124 | 0.37537 | 0.63171 | 121.5591 | -0.30212 | -0.01831 | -0.13733 | 0.15564 | 0.24719 | -0.60425 | -0.086975 | 0.013733 | 0.17395 | 0.59052 | 0.84686 | 121.1563 | 121.6232 | 0.15564 | 121.7743 | 2.6276 | -0.086975 | 121.6232 | 0.15564 | 2.6276 | 121.1563 | 121.7743 | -121.7789 | -121.8475
1888.2031 | 121.7148 | -0.23804 | 121.5134 | -0.19798 | 0.012832 | -0.0046463 | 0.010835 | 0.049473 | -0.01139 | 0.067116 | -0.041199 | 121.431 | -0.22888 | 0.050354 | 120.9457 | 2.4261 | 0.34332 | 0.64087 | 121.55 | -0.28839 | 0.009155 | -0.082398 | 0.19684 | 0.28839 | -0.56763 | -0.050354 | 0.036621 | 0.18768 | 0.58136 | 0.87891 | 121.1838 | 121.669 | 0.19684 | 121.788 | 2.6642 | -0.050354 | 121.669 | 0.19684 | 2.6642 | 121.1838 | 121.788 | -121.7422 | -121.8018
1889.8906 | 121.7697 | -0.20142 | 121.4996 | -0.2285 | 0.014328 | -0.0082779 | 0.012544 | 0.049259 | -0.010963 | 0.064553 | -0.16022 | 121.4264 | -0.27466 | -0.059509 | 120.8221 | 2.3346 | 0.49439 | 0.4715 | 121.6141 | -0.32959 | -0.073242 | -0.073242 | 0.041199 | 0.14191 | -0.67749 | -0.12817 | 0.11444 | 0.11444 | 0.6958 | 0.67291 | 121.0236 | 121.6278 | 0.041199 | 121.8155 | 2.536 | -0.12817 | 121.6278 | 0.041199 | 2.536 | 121.0236 | 121.8155 | -121.7743 | -121.8292
1891.6406 | 121.7194 | -0.20599 | 121.5225 | -0.037765 | 0.0092008 | -0.0052873 | 0.015321 | 0.053532 | -0.013313 | 0.066689 | -0.11444 | 121.3943 | -0.27924 | -0.045776 | 120.8405 | 2.2659 | 0.2243 | 0.28839 | 121.6232 | -0.31128 | -0.073242 | -0.12817 | 0.091553 | 0.16022 | -0.68207 | -0.10528 | 0.10071 | 0.16479 | 0.4303 | 0.49439 | 121.0464 | 121.6003 | 0.091553 | 121.8292 | 2.4719 | -0.10528 | 121.6003 | 0.091553 | 2.4719 | 121.0464 | 121.8292 | -121.8018 | -121.8338
1893.4062 | 121.8063 | -0.17853 | 121.4859 | 0.13771 | 0.010055 | -0.0065689 | 0.009126 | 0.048191 | -0.010963 | 0.06797 | -0.07782 | 121.4218 | -0.19684 | 0.018311 | 120.9229 | 2.2659 | 0.032043 | 0.32959 | 121.5546 | -0.27008 | -0.01831 | -0.064087 | 0.10071 | 0.19684 | -0.56305 | -0.091553 | 0.068664 | 0.11902 | 0.21057 | 0.50812 | 121.1014 | 121.6003 | 0.10071 | 121.7331 | 2.4445 | -0.091553 | 121.6003 | 0.10071 | 2.4445 | 121.1014 | 121.7331 | -121.6827 | -121.756
1895.1562 | 121.8338 | -0.14648 | 121.4859 | 0.0080111 | 0.010696 | -0.0091325 | 0.0065624 | 0.049473 | -0.010109 | 0.065834 | -0.10071 | 121.3852 | -0.21057 | -0.004578 | 120.8725 | 2.2842 | 0.18768 | 0.39368 | 121.5317 | -0.27008 | -0.064087 | -0.10071 | 0.045776 | 0.14191 | -0.6134 | -0.1236 | 0.045776 | 0.10986 | 0.33417 | 0.54016 | 121.019 | 121.5317 | 0.045776 | 121.6782 | 2.4307 | -0.1236 | 121.5317 | 0.045776 | 2.4307 | 121.019 | 121.6782 | -121.6965 | -121.756
1896.8438 | 121.843 | -0.16479 | 121.5454 | 0.18349 | 0.010269 | -0.0065689 | 0.015321 | 0.049687 | -0.0092542 | 0.064339 | -0.013733 | 121.4722 | -0.21057 | 0.054932 | 121.0007 | 2.2797 | -0.027466 | 0.32044 | 121.6232 | -0.25635 | -0.045776 | -0.073242 | 0.15106 | 0.21973 | -0.54474 | -0.091553 | 0.07782 | 0.19684 | 0.13733 | 0.48523 | 121.1655 | 121.637 | 0.15106 | 121.788 | 2.4445 | -0.091553 | 121.637 | 0.15106 | 2.4445 | 121.1655 | 121.788 | -121.756 | -121.8018
1898.5938 | 121.8384 | -0.19226 | 121.6141 | -0.24376 | 0.011764 | -0.0055009 | 0.011049 | 0.046055 | -0.008186 | 0.067757 | -0.11444 | 121.5363 | -0.25177 | -0.022888 | 120.9503 | 2.3483 | 0.50354 | 0.51727 | 121.669 | -0.29297 | -0.059509 | -0.07782 | 0.07782 | 0.16937 | -0.66376 | -0.10071 | 0.054931 | 0.13733 | 0.6958 | 0.70953 | 121.1426 | 121.7285 | 0.07782 | 121.8613 | 2.5406 | -0.10071 | 121.7285 | 0.07782 | 2.5406 | 121.1426 | 121.8613 | -121.8658 | -121.907
1900.3594 | 121.875 | -0.16479 | 121.637 | -0.11406 | 0.009628 | -0.0095597 | 0.0080578 | 0.047337 | -0.0083996 | 0.068398 | -0.050354 | 121.5317 | -0.2243 | 0.059509 | 121.0602 | 2.4033 | 0.27008 | 0.57678 | 121.6553 | -0.27466 | -0.059509 | -0.10529 | 0.11444 | 0.2243 | -0.57678 | -0.10986 | 0.01831 | 0.17395 | 0.43488 | 0.74158 | 121.225 | 121.6965 | 0.11444 | 121.8201 | 2.5681 | -0.10986 | 121.6965 | 0.11444 | 2.5681 | 121.225 | 121.8201 | -121.8613 | -121.9116
1902.1094 | 121.8796 | -0.18768 | 121.6507 | -0.2285 | 0.011978 | -0.0022965 | 0.013398 | 0.047123 | -0.010536 | 0.067116 | -0.14191 | 121.5683 | -0.28381 | -0.050354 | 120.9503 | 2.3483 | 0.52185 | 0.49896 | 121.7377 | -0.31586 | -0.09613 | -0.082398 | 0.045776 | 0.13733 | -0.70038 | -0.12817 | 0.086975 | 0.14191 | 0.70953 | 0.68664 | 121.138 | 121.756 | 0.045776 | 121.9254 | 2.536 | -0.12817 | 121.756 | 0.045776 | 2.536 | 121.138 | 121.9254 | -121.9345 | -121.9666
1903.7969 | 121.8246 | -0.17395 | 121.637 | -0.10643 | 0.010055 | -0.0055009 | 0.015107 | 0.051609 | -0.012031 | 0.06797 | -0.086975 | 121.5546 | -0.25177 | 0.009155 | 121.0144 | 2.3483 | 0.32044 | 0.43488 | 121.7422 | -0.28839 | -0.07782 | -0.082398 | 0.086975 | 0.1831 | -0.62256 | -0.11444 | 0.10529 | 0.16479 | 0.49439 | 0.60882 | 121.1884 | 121.7285 | 0.086975 | 121.9162 | 2.5223 | -0.11444 | 121.7285 | 0.086975 | 2.5223 | 121.1884 | 121.9162 | -121.8887 | -121.9254
1905.5469 | 121.8887 | -0.18768 | 121.6827 | -0.23613 | 0.012405 | -0.0057145 | 0.0097668 | 0.047764 | -0.01075 | 0.067543 | -0.11444 | 121.5866 | -0.23346 | -0.018311 | 121.019 | 2.3575 | 0.49896 | 0.53558 | 121.7285 | -0.30212 | -0.045776 | -0.09613 | 0.073242 | 0.16937 | -0.66376 | -0.11444 | 0.045777 | 0.11902 | 0.68664 | 0.72327 | 121.2067 | 121.7743 | 0.073242 | 121.9162 | 2.5452 | -0.11444 | 121.7743 | 0.073242 | 2.5452 | 121.2067 | 121.9162 | -121.9162 | -121.9849
1907.2969 | 121.962 | -0.15564 | 121.6644 | 0.1606 | 0.012191 | -0.0072099 | 0.012544 | 0.050541 | -0.012886 | 0.067116 | -0.11444 | 121.5866 | -0.25635 | -0.013733 | 121.0144 | 2.2202 | 0.032043 | 0.21057 | 121.7651 | -0.2655 | -0.10071 | -0.07782 | 0.041199 | 0.14191 | -0.65002 | -0.10986 | 0.10071 | 0.14191 | 0.18768 | 0.36621 | 121.17 | 121.7422 | 0.041199 | 121.9208 | 2.3758 | -0.10986 | 121.7422 | 0.041199 | 2.3758 | 121.17 | 121.9208 | -121.9208 | -121.9299
1909 | 121.9849 | -0.15564 | 121.6415 | -0.014877 | 0.011337 | -0.0063553 | 0.0067762 | 0.047764 | -0.0086132 | 0.06498 | -0.091553 | 121.6278 | -0.21057 | 0.009155 | 121.0739 | 2.33 | 0.23346 | 0.44403 | 121.701 | -0.27924 | -0.054931 | -0.013733 | 0.064087 | 0.16479 | -0.56763 | -0.1236 | 0.059509 | 0.11902 | 0.3891 | 0.59967 | 121.2296 | 121.7834 | 0.064087 | 121.8567 | 2.4857 | -0.1236 | 121.7834 | 0.064087 | 2.4857 | 121.2296 | 121.8567 | -121.8521 | -121.9208
1910.75 | 121.875 | -0.20142 | 121.6965 | -0.083542 | 0.011551 | -0.0065689 | 0.015321 | 0.051609 | -0.014381 | 0.065407 | -0.10071 | 121.6049 | -0.2655 | -0.004578 | 121.0236 | 2.3163 | 0.26093 | 0.33875 | 121.7834 | -0.28381 | -0.064087 | -0.091553 | 0.10071 | 0.19684 | -0.67291 | -0.082397 | 0.086975 | 0.16479 | 0.46234 | 0.54016 | 121.225 | 121.8063 | 0.10071 | 121.9849 | 2.5177 | -0.082397 | 121.8063 | 0.10071 | 2.5177 | 121.225 | 121.9849 | -121.962 | -121.9803
1912.5 | 121.9482 | -0.16937 | 121.6873 | 0.18349 | 0.011123 | -0.0095597 | 0.0099804 | 0.050541 | -0.009895 | 0.066475 | -0.027466 | 121.6141 | -0.22888 | 0.036621 | 121.1197 | 2.3026 | -0.027466 | 0.31128 | 121.6919 | -0.27008 | -0.059509 | -0.073242 | 0.14191 | 0.20599 | -0.56763 | -0.10071 | 0.004578 | 0.20142 | 0.14191 | 0.48065 | 121.2891 | 121.7834 | 0.14191 | 121.8613 | 2.4719 | -0.10071 | 121.7834 | 0.14191 | 2.4719 | 121.2891 | 121.8613 | -121.9162 | -121.9574
1914.25 | 121.9849 | -0.16479 | 121.6965 | 0.091934 | 0.011764 | -0.0076371 | 0.0097668 | 0.050968 | -0.009895 | 0.067543 | -0.050354 | 121.6049 | -0.21515 | 0.022888 | 121.1151 | 2.2888 | 0.027466 | 0.33417 | 121.7194 | -0.28381 | -0.050354 | -0.091553 | 0.11444 | 0.18768 | -0.58136 | -0.11902 | 0.022888 | 0.16479 | 0.19226 | 0.49896 | 121.2799 | 121.7697 | 0.11444 | 121.8842 | 2.4536 | -0.11902 | 121.7697 | 0.11444 | 2.4536 | 121.2799 | 121.8842 | -121.9116 | -121.9803
1915.9375 | 121.9757 | -0.13733 | 121.6919 | 0.13771 | 0.011551 | -0.0072099 | 0.012758 | 0.049687 | -0.011818 | 0.065407 | -0.054932 | 121.5912 | -0.21057 | 0.045776 | 121.1151 | 2.298 | -0.032043 | 0.28381 | 121.7239 | -0.25177 | -0.073242 | -0.10071 | 0.082397 | 0.18311 | -0.57678 | -0.11444 | 0.032043 | 0.15564 | 0.10529 | 0.42114 | 121.2524 | 121.7285 | 0.082397 | 121.8613 | 2.4353 | -0.11444 | 121.7285 | 0.082397 | 2.4353 | 121.2524 | 121.8613 | -121.9025 | -121.9437
1917.6719 | 121.9025 | -0.20599 | 121.701 | -0.045395 | 0.01091 | -0.0091325 | 0.014039 | 0.050328 | -0.012245 | 0.066262 | -0.073242 | 121.7056 | -0.24719 | -0.009155 | 121.051 | 2.3209 | 0.24719 | 0.32044 | 121.8292 | -0.3067 | -0.041198 | 0.004577 | 0.13275 | 0.19684 | -0.65002 | -0.10071 | 0.12817 | 0.17395 | 0.45319 | 0.52643 | 121.257 | 121.9116 | 0.13275 | 122.0352 | 2.5269 | -0.10071 | 121.9116 | 0.13275 | 2.5269 | 121.257 | 122.0352 | -121.9482 | -122.0078
1919.4375 | 121.8842 | -0.18768 | 121.7422 | -0.12932 | 0.007919 | -0.0046463 | 0.010408 | 0.054386 | -0.012672 | 0.065834 | -0.1236 | 121.6278 | -0.27008 | -0.013733 | 121.0739 | 2.3895 | 0.36621 | 0.44403 | 121.7972 | -0.30212 | -0.082398 | -0.11444 | 0.064087 | 0.17395 | -0.66833 | -0.11444 | 0.054931 | 0.14649 | 0.55389 | 0.63171 | 121.2616 | 121.8155 | 0.064087 | 121.9849 | 2.5772 | -0.11444 | 121.8155 | 0.064087 | 2.5772 | 121.2616 | 121.9849 | -122.0123 | -122.0444
1921.2031 | 121.9254 | -0.20142 | 121.7377 | -0.17509 | 0.010696 | -0.0089189 | 0.0099804 | 0.050328 | -0.013527 | 0.066902 | -0.15106 | 121.6415 | -0.25635 | -0.073242 | 121.0602 | 2.3712 | 0.48065 | 0.46692 | 121.8521 | -0.3067 | -0.054932 | -0.09613 | 0.050354 | 0.12817 | -0.67749 | -0.10529 | 0.11444 | 0.10529 | 0.68207 | 0.66834 | 121.2616 | 121.843 | 0.050354 | 122.0535 | 2.5726 | -0.10529 | 121.843 | 0.050354 | 2.5726 | 121.2616 | 122.0535 | -121.994 | -122.0444
1922.9062 | 121.907 | -0.21057 | 121.7697 | -0.098801 | 0.0098416 | -0.0069961 | 0.01233 | 0.050114 | -0.01374 | 0.06498 | -0.086975 | 121.6507 | -0.27466 | -0.009155 | 121.0922 | 2.3804 | 0.27466 | 0.40741 | 121.8155 | -0.27008 | -0.064087 | -0.11902 | 0.1236 | 0.20142 | -0.67749 | -0.05951 | 0.045777 | 0.18768 | 0.48523 | 0.61798 | 121.3028 | 121.8613 | 0.1236 | 122.0261 | 2.5909 | -0.05951 | 121.8613 | 0.1236 | 2.5909 | 121.3028 | 122.0261 | -122.0444 | -122.0398
1924.6719 | 122.0306 | -0.16479 | 121.7377 | 0.099564 | 0.009628 | -0.0078507 | 0.0054944 | 0.049259 | -0.012458 | 0.066689 | -0.073242 | 121.5683 | -0.23804 | -0.009155 | 121.1197 | 2.2797 | 0.11444 | 0.3479 | 121.788 | -0.27466 | -0.073242 | -0.16937 | 0.091553 | 0.15564 | -0.61798 | -0.10986 | 0.050354 | 0.16479 | 0.27924 | 0.5127 | 121.2845 | 121.7331 | 0.091553 | 121.9528 | 2.4445 | -0.10986 | 121.7331 | 0.091553 | 2.4445 | 121.2845 | 121.9528 | -121.9757 | -122.0123
1926.4219 | 121.9391 | -0.17395 | 121.7514 | -0.17509 | 0.011551 | -0.0035783 | 0.012117 | 0.048832 | -0.010963 | 0.064125 | -0.14191 | 121.6553 | -0.2655 | -0.059509 | 121.0648 | 2.3849 | 0.47607 | 0.4715 | 121.8338 | -0.30212 | -0.091553 | -0.096131 | 0.032043 | 0.11444 | -0.68665 | -0.12817 | 0.082397 | 0.1236 | 0.65002 | 0.64545 | 121.2387 | 121.8292 | 0.032043 | 122.0078 | 2.5589 | -0.12817 | 121.8292 | 0.032043 | 2.5589 | 121.2387 | 122.0078 | -122.0169 | -122.0535
1928.1719 | 121.9345 | -0.19684 | 121.7743 | -0.12932 | 0.010269 | -0.011696 | 0.0059216 | 0.049473 | -0.011177 | 0.065621 | -0.022888 | 121.6553 | -0.21973 | 0.059509 | 121.1975 | 2.4719 | 0.32501 | 0.61798 | 121.8018 | -0.2655 | -0.022889 | -0.11902 | 0.17395 | 0.25635 | -0.57678 | -0.068665 | 0.027466 | 0.19684 | 0.52185 | 0.81482 | 121.3943 | 121.8521 | 0.17395 | 121.9986 | 2.6688 | -0.068665 | 121.8521 | 0.17395 | 2.6688 | 121.3943 | 121.9986 | -121.994 | -122.0398
1929.8594 | 121.9482 | -0.20142 | 121.7606 | -0.19035 | 0.009628 | -0.0059281 | 0.008485 | 0.050541 | -0.011818 | 0.065193 | -0.054932 | 121.6553 | -0.21057 | 0.054932 | 121.17 | 2.4673 | 0.39825 | 0.6134 | 121.8063 | -0.27924 | -0.009155 | -0.10529 | 0.14648 | 0.25635 | -0.59051 | -0.07782 | 0.045776 | 0.15564 | 0.59967 | 0.81482 | 121.3715 | 121.8567 | 0.14648 | 122.0078 | 2.6688 | -0.07782 | 121.8567 | 0.14648 | 2.6688 | 121.3715 | 122.0078 | -121.9711 | -122.0398
1931.5938 | 121.9757 | -0.16937 | 121.7422 | -0.19798 | 0.011551 | -0.010841 | 0.013398 | 0.049259 | -0.010109 | 0.06733 | -0.14191 | 121.6965 | -0.25177 | -0.036621 | 121.0648 | 2.3758 | 0.49439 | 0.4715 | 121.8384 | -0.31128 | -0.082397 | -0.045777 | 0.027466 | 0.13275 | -0.67749 | -0.14191 | 0.09613 | 0.10986 | 0.66376 | 0.64087 | 121.2341 | 121.8658 | 0.027466 | 122.0078 | 2.5452 | -0.14191 | 121.8658 | 0.027466 | 2.5452 | 121.2341 | 122.0078 | -121.994 | -122.0535
1933.3438 | 121.9986 | -0.16022 | 121.7468 | 0.046158 | 0.011764 | -0.0065689 | 0.014894 | 0.050755 | -0.011604 | 0.066689 | -0.13275 | 121.6553 | -0.26093 | -0.059509 | 121.0419 | 2.2705 | 0.2243 | 0.2243 | 121.875 | -0.29755 | -0.10071 | -0.091553 | 0.027466 | 0.10071 | -0.70496 | -0.13733 | 0.12817 | 0.12817 | 0.38452 | 0.38452 | 121.2021 | 121.8155 | 0.027466 | 122.0352 | 2.4307 | -0.13733 | 121.8155 | 0.027466 | 2.4307 | 121.2021 | 122.0352 | -122.0078 | -122.0444
1935.0938 | 121.9711 | -0.1831 | 121.7651 | 0.030899 | 0.011764 | -0.0095597 | 0.014467 | 0.051823 | -0.013313 | 0.065407 | -0.1236 | 121.7102 | -0.25635 | -0.041199 | 121.0739 | 2.2842 | 0.23346 | 0.24719 | 121.8796 | -0.27466 | -0.073243 | -0.054932 | 0.059509 | 0.14191 | -0.69122 | -0.091553 | 0.11444 | 0.13275 | 0.41656 | 0.4303 | 121.257 | 121.8933 | 0.059509 | 122.0627 | 2.4673 | -0.091553 | 121.8933 | 0.059509 | 2.4673 | 121.257 | 122.0627 | -122.0215 | -122.0398
1936.7812 | 122.0261 | -0.16022 | 121.7651 | 0.061417 | 0.011764 | -0.0074235 | 0.0099804 | 0.050541 | -0.014167 | 0.068825 | -0.13275 | 121.6873 | -0.26093 | -0.07782 | 121.051 | 2.2476 | 0.22888 | 0.21515 | 121.8796 | -0.30212 | -0.10071 | -0.07782 | 0.027466 | 0.082397 | -0.71411 | -0.14191 | 0.11444 | 0.12817 | 0.3891 | 0.37537 | 121.2112 | 121.8475 | 0.027466 | 122.0398 | 2.4078 | -0.14191 | 121.8475 | 0.027466 | 2.4078 | 121.2112 | 122.0398 | -122.0261 | -122.0673
1938.5312 | 121.9482 | -0.19226 | 121.7789 | -0.20561 | 0.0092008 | -0.0087051 | 0.0069898 | 0.049473 | -0.01075 | 0.06498 | -0.054932 | 121.6461 | -0.20142 | 0.050354 | 121.1929 | 2.4948 | 0.37537 | 0.64087 | 121.788 | -0.2655 | -0.009155 | -0.13275 | 0.13733 | 0.24261 | -0.58594 | -0.073242 | 0.009155 | 0.14648 | 0.56763 | 0.83313 | 121.3852 | 121.8384 | 0.13733 | 121.9803 | 2.6871 | -0.073242 | 121.8384 | 0.13733 | 2.6871 | 121.3852 | 121.9803 | -121.9803 | -122.0444
1940.2969 | 121.9894 | -0.17395 | 121.7606 | -0.2285 | 0.012191 | -0.0065689 | 0.0099804 | 0.050114 | -0.012031 | 0.064766 | -0.16022 | 121.7331 | -0.25635 | -0.059509 | 121.0693 | 2.417 | 0.51727 | 0.48065 | 121.8842 | -0.30212 | -0.082398 | -0.027466 | 0.013733 | 0.11444 | -0.69122 | -0.12817 | 0.1236 | 0.096131 | 0.69122 | 0.6546 | 121.2433 | 121.907 | 0.013733 | 122.0581 | 2.5909 | -0.12817 | 121.907 | 0.013733 | 2.5909 | 121.2433 | 122.0581 | -122.0169 | -122.0627
1941.9844 | 121.9894 | -0.19226 | 121.7651 | -0.20561 | 0.0089872 | -0.010414 | 0.0076306 | 0.051396 | -0.011818 | 0.06498 | -0.14191 | 121.6965 | -0.26093 | -0.059509 | 121.0876 | 2.417 | 0.51727 | 0.52643 | 121.8842 | -0.28381 | -0.068664 | -0.068665 | 0.050354 | 0.13275 | -0.67749 | -0.091552 | 0.11902 | 0.11902 | 0.70953 | 0.71869 | 121.2799 | 121.8887 | 0.050354 | 122.0764 | 2.6093 | -0.091552 | 121.8887 | 0.050354 | 2.6093 | 121.2799 | 122.0764 | -122.0261 | -122.0489
1943.7344 | 122.0306 | -0.17853 | 121.7743 | 0.053787 | 0.011123 | -0.0097733 | 0.015107 | 0.050328 | -0.012458 | 0.066689 | -0.14191 | 121.7056 | -0.25177 | -0.073242 | 121.0602 | 2.2568 | 0.22888 | 0.21515 | 121.8613 | -0.30212 | -0.073242 | -0.068665 | 0.036621 | 0.10529 | -0.71411 | -0.1236 | 0.086975 | 0.10986 | 0.40741 | 0.39368 | 121.2387 | 121.8842 | 0.036621 | 122.0398 | 2.4353 | -0.1236 | 121.8842 | 0.036621 | 2.4353 | 121.2387 | 122.0398 | -122.0261 | -122.0764
1945.4844 | 122.0581 | -0.16937 | 121.7697 | 0.091934 | 0.010696 | -0.0095597 | 0.0046398 | 0.048405 | -0.012886 | 0.066902 | -0.059509 | 121.6278 | -0.23346 | 0.018311 | 121.1517 | 2.3346 | 0.054932 | 0.3479 | 121.788 | -0.2655 | -0.064086 | -0.14191 | 0.10986 | 0.18768 | -0.61798 | -0.09613 | 0.018311 | 0.17395 | 0.22431 | 0.51727 | 121.3211 | 121.7972 | 0.10986 | 121.9574 | 2.504 | -0.09613 | 121.7972 | 0.10986 | 2.504 | 121.3211 | 121.9574 | -122.0032 | -122.0352
1947.2344 | 122.049 | -0.16479 | 121.7331 | 0.18349 | 0.0077054 | -0.0102 | 0.011262 | 0.049259 | -0.013099 | 0.066262 | -0.082397 | 121.6919 | -0.25635 | 0.018311 | 121.1563 | 2.3254 | 0 | 0.27924 | 121.8521 | -0.27008 | -0.091553 | -0.041198 | 0.082398 | 0.18311 | -0.57678 | -0.10529 | 0.11902 | 0.17395 | 0.16479 | 0.44403 | 121.3211 | 121.8567 | 0.082398 | 122.0169 | 2.4902 | -0.10529 | 121.8567 | 0.082398 | 2.4902 | 121.3211 | 122.0169 | -121.9894 | -122.0032
1948.9844 | 121.9894 | -0.17395 | 121.7743 | -0.19035 | 0.012832 | -0.0072099 | 0.0097668 | 0.049046 | -0.010322 | 0.066475 | -0.13733 | 121.7331 | -0.26093 | -0.073242 | 121.1014 | 2.3941 | 0.53558 | 0.51727 | 121.8704 | -0.31128 | -0.086975 | -0.041199 | 0.036621 | 0.10071 | -0.67291 | -0.13733 | 0.09613 | 0.1236 | 0.70953 | 0.69122 | 121.2753 | 121.907 | 0.036621 | 122.0444 | 2.5681 | -0.13733 | 121.907 | 0.036621 | 2.5681 | 121.2753 | 122.0444 | -122.0352 | -122.0856
1950.6875 | 122.0398 | -0.17395 | 121.7834 | 0.038529 | 0.012619 | -0.0069961 | 0.014894 | 0.050114 | -0.014167 | 0.065834 | -0.13275 | 121.7148 | -0.2655 | -0.064087 | 121.0693 | 2.2797 | 0.23346 | 0.24261 | 121.8567 | -0.32044 | -0.091553 | -0.068664 | 0.041199 | 0.10986 | -0.71411 | -0.14649 | 0.073242 | 0.13275 | 0.40741 | 0.41656 | 121.2433 | 121.8887 | 0.041199 | 122.0306 | 2.4536 | -0.14649 | 121.8887 | 0.041199 | 2.4536 | 121.2433 | 122.0306 | -122.0489 | -122.1039
1952.4375 | 122.0169 | -0.16937 | 121.7834 | -0.14458 | 0.010482 | -0.0050735 | 0.0063488 | 0.048405 | -0.01139 | 0.066475 | -0.032043 | 121.6827 | -0.20599 | 0.059509 | 121.2112 | 2.4765 | 0.28839 | 0.59967 | 121.8658 | -0.2655 | -0.036621 | -0.10071 | 0.13733 | 0.22888 | -0.5722 | -0.09613 | 0.082398 | 0.17395 | 0.45776 | 0.76904 | 121.3806 | 121.8521 | 0.13733 | 122.0352 | 2.6459 | -0.09613 | 121.8521 | 0.13733 | 2.6459 | 121.3806 | 122.0352 | -121.9894 | -122.0489
1954.1875 | 122.0123 | -0.16022 | 121.8063 | -0.25139 | 0.011123 | -0.0091325 | 0.01233 | 0.049687 | -0.013099 | 0.064125 | -0.14648 | 121.7148 | -0.25635 | -0.064087 | 121.0922 | 2.4033 | 0.53101 | 0.49439 | 121.9208 | -0.3067 | -0.096131 | -0.091552 | 0.013733 | 0.09613 | -0.71411 | -0.14648 | 0.11444 | 0.10986 | 0.69122 | 0.6546 | 121.2524 | 121.875 | 0.013733 | 122.081 | 2.5635 | -0.14648 | 121.875 | 0.013733 | 2.5635 | 121.2524 | 122.081 | -122.0627 | -122.113
1955.8906 | 122.0947 | -0.15106 | 121.7743 | 0.061417 | 0.010696 | -0.0076371 | 0.012758 | 0.049046 | -0.013954 | 0.065407 | -0.13733 | 121.7148 | -0.27466 | -0.068665 | 121.0693 | 2.2522 | 0.2243 | 0.19226 | 121.962 | -0.29755 | -0.1236 | -0.059509 | 0.013733 | 0.082397 | -0.70496 | -0.14648 | 0.18768 | 0.13733 | 0.37537 | 0.34332 | 121.2204 | 121.8658 | 0.013733 | 122.113 | 2.4033 | -0.14648 | 121.8658 | 0.013733 | 2.4033 | 121.2204 | 122.113 | -122.049 | -122.0718
1957.6406 | 122.0673 | -0.13733 | 121.7651 | 0.14534 | 0.012619 | -0.0037919 | 0.010835 | 0.051182 | -0.012031 | 0.065193 | -0.10071 | 121.7148 | -0.22888 | -0.027466 | 121.1243 | 2.2659 | 0.054932 | 0.20599 | 121.8933 | -0.28381 | -0.091553 | -0.050354 | 0.036621 | 0.10986 | -0.64087 | -0.14648 | 0.12817 | 0.12817 | 0.19226 | 0.34332 | 121.2616 | 121.8521 | 0.036621 | 122.0306 | 2.4033 | -0.14648 | 121.8521 | 0.036621 | 2.4033 | 121.2616 | 122.0306 | -121.994 | -122.0489
1959.4062 | 121.9666 | -0.18768 | 121.7972 | -0.083542 | 0.011978 | -0.0080643 | 0.013612 | 0.051182 | -0.012672 | 0.064766 | -0.068665 | 121.7102 | -0.24261 | 0.004578 | 121.1517 | 2.3987 | 0.2655 | 0.39368 | 121.9116 | -0.27008 | -0.054932 | -0.086975 | 0.11902 | 0.19226 | -0.64545 | -0.082398 | 0.11444 | 0.17395 | 0.45319 | 0.58136 | 121.3394 | 121.8979 | 0.11902 | 122.0993 | 2.5864 | -0.082398 | 121.8979 | 0.11902 | 2.5864 | 121.3394 | 122.0993 | -122.0398 | -122.0673
1961.1875 | 121.9574 | -0.17853 | 121.8201 | -0.14458 | 0.0083462 | -0.0067825 | 0.011262 | 0.050755 | -0.014808 | 0.069039 | -0.09613 | 121.7148 | -0.26093 | -0.009155 | 121.1563 | 2.4399 | 0.36621 | 0.46692 | 121.907 | -0.2655 | -0.082397 | -0.10529 | 0.082398 | 0.16937 | -0.66376 | -0.086975 | 0.086975 | 0.1648 | 0.54474 | 0.64545 | 121.3348 | 121.8933 | 0.082398 | 122.0856 | 2.6184 | -0.086975 | 121.8933 | 0.082398 | 2.6184 | 121.3348 | 122.0856 | -122.081 | -122.0856
1962.875 | 121.9849 | -0.18768 | 121.8063 | -0.068283 | 0.0092008 | -0.0078507 | 0.012971 | 0.050541 | -0.014381 | 0.068184 | -0.086975 | 121.7194 | -0.25177 | -0.022888 | 121.1472 | 2.3804 | 0.25635 | 0.34332 | 121.9254 | -0.28839 | -0.064087 | -0.086975 | 0.10071 | 0.16479 | -0.65918 | -0.10071 | 0.11902 | 0.16479 | 0.44403 | 0.53101 | 121.3348 | 121.907 | 0.10071 | 122.113 | 2.5681 | -0.10071 | 121.907 | 0.10071 | 2.5681 | 121.3348 | 122.113 | -122.0581 | -122.0947
1964.625 | 122.0856 | -0.13275 | 121.8018 | 0.12245 | 0.011978 | -0.0076371 | 0.010835 | 0.053105 | -0.010536 | 0.064553 | -0.12817 | 121.7606 | -0.24261 | -0.054932 | 121.1334 | 2.2842 | 0.07782 | 0.20599 | 121.9254 | -0.27924 | -0.10986 | -0.041199 | 0.004577 | 0.077819 | -0.66834 | -0.14648 | 0.1236 | 0.11444 | 0.21057 | 0.33875 | 121.2662 | 121.8933 | 0.004577 | 122.0581 | 2.417 | -0.14648 | 121.8933 | 0.004577 | 2.417 | 121.2662 | 122.0581 | -122.0444 | -122.081
1966.375 | 121.9803 | -0.16937 | 121.8246 | -0.091171 | 0.010696 | -0.0046463 | 0.012971 | 0.0499 | -0.01374 | 0.068184 | -0.07782 | 121.7377 | -0.23804 | 0.009155 | 121.1609 | 2.4353 | 0.28381 | 0.39825 | 121.9025 | -0.28839 | -0.068664 | -0.086975 | 0.091553 | 0.17853 | -0.66376 | -0.11902 | 0.07782 | 0.16022 | 0.45319 | 0.56763 | 121.3303 | 121.907 | 0.091553 | 122.0718 | 2.6047 | -0.11902 | 121.907 | 0.091553 | 2.6047 | 121.3303 | 122.0718 | -122.0627 | -122.113
1968.0625 | 121.9666 | -0.15564 | 121.8338 | -0.083542 | 0.012191 | -0.0102 | 0.012544 | 0.053105 | -0.012886 | 0.065407 | -0.086975 | 121.756 | -0.22888 | -0.004578 | 121.1792 | 2.4307 | 0.29755 | 0.42114 | 121.9208 | -0.27924 | -0.073242 | -0.07782 | 0.068665 | 0.15106 | -0.6546 | -0.1236 | 0.086975 | 0.14191 | 0.45319 | 0.57678 | 121.3348 | 121.9116 | 0.068665 | 122.0764 | 2.5864 | -0.1236 | 121.9116 | 0.068665 | 2.5864 | 121.3348 | 122.0764 | -122.0627 | -122.113
1969.8125 | 122.113 | -0.15106 | 121.7972 | -0.0072479 | 0.009628 | -0.0102 | 0.0042126 | 0.048832 | -0.007118 | 0.065407 | -0.09613 | 121.7148 | -0.21973 | -0.018311 | 121.2067 | 2.4261 | 0.25635 | 0.4715 | 121.8933 | -0.27924 | -0.068665 | -0.082397 | 0.054932 | 0.13275 | -0.59051 | -0.12817 | 0.096131 | 0.1236 | 0.40741 | 0.62256 | 121.3577 | 121.8658 | 0.054932 | 122.0444 | 2.5772 | -0.12817 | 121.8658 | 0.054932 | 2.5772 | 121.3577 | 122.0444 | -122.0169 | -122.0764
1971.5625 | 122.0993 | -0.14191 | 121.8063 | 0.13771 | 0.010269 | -0.0069961 | 0.013612 | 0.051609 | -0.013313 | 0.066475 | -0.13733 | 121.7651 | -0.26093 | -0.07782 | 121.1014 | 2.2751 | 0.15106 | 0.1831 | 121.9391 | -0.28839 | -0.11902 | -0.041198 | 0.004578 | 0.064087 | -0.70496 | -0.14648 | 0.13275 | 0.1236 | 0.29297 | 0.32501 | 121.2433 | 121.907 | 0.004578 | 122.081 | 2.417 | -0.14648 | 121.907 | 0.004578 | 2.417 | 121.2433 | 122.081 | -122.0673 | -122.0947
1973.3125 | 122.0993 | -0.14648 | 121.8109 | -0.030136 | 0.010269 | -0.0025101 | 0.0059216 | 0.049687 | -0.010536 | 0.066048 | -0.073242 | 121.7606 | -0.21057 | 0.009155 | 121.2112 | 2.4216 | 0.27466 | 0.49896 | 121.8796 | -0.27008 | -0.064087 | -0.050354 | 0.073242 | 0.15564 | -0.59967 | -0.1236 | 0.068665 | 0.13733 | 0.42114 | 0.64545 | 121.3577 | 121.907 | 0.073242 | 122.0261 | 2.5681 | -0.1236 | 121.907 | 0.073242 | 2.5681 | 121.3577 | 122.0261 | -122.0215 | -122.081
1975.0156 | 122.0352 | -0.1831 | 121.8109 | -0.12932 | 0.0098416 | -0.0072099 | 0.011049 | 0.048619 | -0.01374 | 0.065834 | -0.14648 | 121.7468 | -0.24719 | -0.036621 | 121.1426 | 2.4399 | 0.52185 | 0.52185 | 121.9482 | -0.30212 | -0.064087 | -0.064087 | 0.036621 | 0.14648 | -0.66833 | -0.11902 | 0.13733 | 0.10071 | 0.70496 | 0.70496 | 121.3257 | 121.9299 | 0.036621 | 122.1313 | 2.623 | -0.11902 | 121.9299 | 0.036621 | 2.623 | 121.3257 | 122.1313 | -122.0581 | -122.113
1976.7656 | 121.9711 | -0.19226 | 121.8246 | -0.11406 | 0.010696 | -0.0080643 | 0.014039 | 0.050968 | -0.013099 | 0.063912 | -0.082397 | 121.7422 | -0.25635 | -0.009155 | 121.17 | 2.4536 | 0.31586 | 0.4303 | 121.9208 | -0.29297 | -0.064087 | -0.082397 | 0.10986 | 0.18311 | -0.6546 | -0.10071 | 0.09613 | 0.17395 | 0.50812 | 0.62256 | 121.3623 | 121.9345 | 0.10986 | 122.113 | 2.6459 | -0.10071 | 121.9345 | 0.10986 | 2.6459 | 121.3623 | 122.113 | -122.081 | -122.1176
1978.5312 | 122.1222 | -0.14648 | 121.7834 | 0.099564 | 0.011764 | -0.010628 | 0.010621 | 0.050328 | -0.012031 | 0.066262 | -0.14648 | 121.7514 | -0.24261 | -0.059509 | 121.1426 | 2.2842 | 0.10071 | 0.19226 | 121.9391 | -0.28381 | -0.096131 | -0.032043 | 0 | 0.086975 | -0.64087 | -0.13733 | 0.15564 | 0.096131 | 0.24719 | 0.33874 | 121.2891 | 121.8979 | 0 | 122.0856 | 2.4307 | -0.13733 | 121.8979 | 0 | 2.4307 | 121.2891 | 122.0856 | -122.0261 | -122.0673
1980.2812 | 122.0718 | -0.16937 | 121.8063 | 0.23689 | 0.0092008 | -0.0084915 | 0.013185 | 0.052677 | -0.013099 | 0.068398 | -0.041199 | 121.7148 | -0.23346 | 0.032043 | 121.2296 | 2.3758 | 0 | 0.29297 | 121.8887 | -0.24261 | -0.064086 | -0.091552 | 0.12817 | 0.20142 | -0.57678 | -0.073242 | 0.082398 | 0.19226 | 0.16937 | 0.46234 | 121.3989 | 121.8842 | 0.12817 | 122.0581 | 2.5452 | -0.073242 | 121.8842 | 0.12817 | 2.5452 | 121.3989 | 122.0581 | -122.0398 | -122.049
1981.9688 | 122.1359 | -0.14191 | 121.8018 | 0.046158 | 0.011978 | -0.0091325 | 0.0067762 | 0.04755 | -0.0096814 | 0.066689 | -0.082397 | 121.7422 | -0.21057 | -0.004578 | 121.1929 | 2.3666 | 0.19226 | 0.3891 | 121.8979 | -0.27924 | -0.068664 | -0.059509 | 0.05951 | 0.13733 | -0.60883 | -0.13733 | 0.09613 | 0.12817 | 0.33417 | 0.53101 | 121.3348 | 121.8842 | 0.05951 | 122.0398 | 2.5085 | -0.13733 | 121.8842 | 0.05951 | 2.5085 | 121.3348 | 122.0398 | -122.0123 | -122.081
1983.7188 | 121.994 | -0.19684 | 121.8567 | -0.098801 | 0.015182 | -0.0061417 | 0.012758 | 0.049687 | -0.014381 | 0.065621 | -0.073242 | 121.7972 | -0.23346 | 0.022888 | 121.1929 | 2.4628 | 0.34332 | 0.4303 | 121.9116 | -0.28839 | -0.036621 | -0.059509 | 0.1236 | 0.21973 | -0.66376 | -0.091553 | 0.054932 | 0.16022 | 0.54016 | 0.62714 | 121.3898 | 121.994 | 0.1236 | 122.1085 | 2.6596 | -0.091553 | 121.994 | 0.1236 | 2.6596 | 121.3898 | 122.1085 | -122.0901 | -122.1451
1985.4688 | 122.1497 | -0.13733 | 121.8063 | 0.076676 | 0.010055 | -0.0084915 | 0.014039 | 0.051396 | -0.012886 | 0.066902 | -0.13733 | 121.7651 | -0.25635 | -0.054932 | 121.1334 | 2.2934 | 0.13275 | 0.19226 | 121.962 | -0.28381 | -0.11902 | -0.041198 | 0 | 0.082397 | -0.67291 | -0.14648 | 0.15564 | 0.11902 | 0.27008 | 0.32959 | 121.2708 | 121.9025 | 0 | 122.0993 | 2.4307 | -0.14648 | 121.9025 | 0 | 2.4307 | 121.2708 | 122.0993 | -122.0627 | -122.0901
1987.2188 | 121.9849 | -0.17853 | 121.875 | -0.11406 | 0.011123 | -0.0076371 | 0.01233 | 0.050755 | -0.013099 | 0.068825 | -0.073242 | 121.756 | -0.24719 | -0.004578 | 121.1792 | 2.4445 | 0.31586 | 0.43488 | 121.9482 | -0.28839 | -0.068664 | -0.11902 | 0.10529 | 0.17395 | -0.6958 | -0.10986 | 0.073242 | 0.17395 | 0.49438 | 0.6134 | 121.3577 | 121.9345 | 0.10529 | 122.1268 | 2.623 | -0.10986 | 121.9345 | 0.10529 | 2.623 | 121.3577 | 122.1268 | -122.1222 | -122.1634
1988.9062 | 122.0169 | -0.16022 | 121.843 | -0.17509 | 0.012405 | -0.010414 | 0.011476 | 0.0499 | -0.012458 | 0.064553 | -0.13733 | 121.8201 | -0.23804 | -0.027466 | 121.1746 | 2.4673 | 0.47607 | 0.47607 | 121.9482 | -0.29755 | -0.07782 | -0.022889 | 0.022888 | 0.13275 | -0.66833 | -0.13733 | 0.10528 | 0.10071 | 0.63629 | 0.63629 | 121.3348 | 121.9803 | 0.022888 | 122.1085 | 2.6276 | -0.13733 | 121.9803 | 0.022888 | 2.6276 | 121.3348 | 122.1085 | -122.081 | -122.1405
1990.6562 | 122.0398 | -0.16022 | 121.8475 | 0.046158 | 0.011764 | -0.010841 | 0.012971 | 0.05225 | -0.012245 | 0.067116 | -0.10986 | 121.7377 | -0.24261 | -0.041199 | 121.1563 | 2.3529 | 0.23804 | 0.2655 | 121.9437 | -0.27008 | -0.082398 | -0.10986 | 0.050354 | 0.11902 | -0.69122 | -0.10986 | 0.096131 | 0.13275 | 0.39825 | 0.42572 | 121.3165 | 121.8979 | 0.050354 | 122.1039 | 2.5131 | -0.10986 | 121.8979 | 0.050354 | 2.5131 | 121.3165 | 122.1039 | -122.0901 | -122.1176
1992.3906 | 122.1085 | -0.13733 | 121.8292 | 0.1606 | 0.012405 | -0.0097733 | 0.010621 | 0.052677 | -0.010322 | 0.066048 | -0.10986 | 121.7697 | -0.21057 | -0.022888 | 121.1929 | 2.3346 | 0.059509 | 0.2243 | 121.9437 | -0.27466 | -0.073242 | -0.05951 | 0.027466 | 0.11444 | -0.63629 | -0.13733 | 0.11444 | 0.10071 | 0.19684 | 0.36163 | 121.3303 | 121.907 | 0.027466 | 122.081 | 2.4719 | -0.13733 | 121.907 | 0.027466 | 2.4719 | 121.3303 | 122.081 | -122.0398 | -122.1039
1994.0781 | 122.0169 | -0.17853 | 121.8796 | -0.091171 | 0.012832 | -0.0042191 | 0.011903 | 0.050968 | -0.013313 | 0.066475 | -0.068665 | 121.7697 | -0.21515 | 0.032043 | 121.2067 | 2.4673 | 0.27466 | 0.39825 | 121.9574 | -0.27466 | -0.036621 | -0.10986 | 0.10986 | 0.21057 | -0.67291 | -0.09613 | 0.077819 | 0.14648 | 0.45319 | 0.57678 | 121.3852 | 121.9482 | 0.10986 | 122.1359 | 2.6459 | -0.09613 | 121.9482 | 0.10986 | 2.6459 | 121.3852 | 122.1359 | -122.0947 | -122.1542
1995.7812 | 122.1542 | -0.11902 | 121.8384 | 0.02327 | 0.011337 | -0.010414 | 0.0054944 | 0.049473 | -0.0096814 | 0.068611 | -0.082397 | 121.8018 | -0.20142 | -0.013733 | 121.225 | 2.3895 | 0.21515 | 0.37994 | 121.962 | -0.2655 | -0.082397 | -0.036621 | 0.036622 | 0.10529 | -0.6134 | -0.14648 | 0.1236 | 0.11902 | 0.33417 | 0.49896 | 121.344 | 121.9208 | 0.036622 | 122.081 | 2.5085 | -0.14648 | 121.9208 | 0.036622 | 2.5085 | 121.344 | 122.081 | -122.0398 | -122.1039
1997.5156 | 122.0215 | -0.17853 | 121.8887 | -0.15221 | 0.009628 | -0.0067825 | 0.007417 | 0.048619 | -0.011604 | 0.066475 | -0.009155 | 121.7468 | -0.1831 | 0.07782 | 121.3257 | 2.5452 | 0.32959 | 0.63171 | 121.9528 | -0.23346 | -0.004577 | -0.14191 | 0.16937 | 0.25635 | -0.56305 | -0.054931 | 0.064087 | 0.17395 | 0.50812 | 0.81024 | 121.5042 | 121.9254 | 0.16937 | 122.1313 | 2.7237 | -0.054931 | 121.9254 | 0.16937 | 2.7237 | 121.5042 | 122.1313 | -122.0718 | -122.1222
1999.2656 | 122.1405 | -0.1236 | 121.8475 | 0.046158 | 0.013046 | -0.0080643 | 0.015321 | 0.05225 | -0.013954 | 0.06733 | -0.11902 | 121.8018 | -0.25177 | -0.045776 | 121.1426 | 2.3071 | 0.22888 | 0.20599 | 122.0169 | -0.27924 | -0.12817 | -0.045776 | 0.004577 | 0.07782 | -0.70496 | -0.15564 | 0.16937 | 0.13275 | 0.35248 | 0.32959 | 121.2662 | 121.9254 | 0.004577 | 122.1405 | 2.4307 | -0.15564 | 121.9254 | 0.004577 | 2.4307 | 121.2662 | 122.1405 | -122.0993 | -122.1268
2000.9688 | 122.1451 | -0.13733 | 121.8384 | 0.061417 | 0.010269 | -0.0069961 | 0.014039 | 0.051396 | -0.015876 | 0.065407 | -0.11444 | 121.8109 | -0.2243 | -0.064087 | 121.1472 | 2.3209 | 0.21057 | 0.21057 | 121.9849 | -0.28381 | -0.086975 | -0.027466 | 0.022888 | 0.073242 | -0.69122 | -0.14648 | 0.14648 | 0.10986 | 0.3479 | 0.3479 | 121.2845 | 121.9482 | 0.022888 | 122.1222 | 2.4582 | -0.14648 | 121.9482 | 0.022888 | 2.4582 | 121.2845 | 122.1222 | -122.0627 | -122.1222
2002.7188 | 122.1588 | -0.13275 | 121.8338 | 0.069046 | 0.012191 | -0.012764 | 0.0054944 | 0.050755 | -0.012031 | 0.066262 | -0.059509 | 121.8063 | -0.17853 | 0.018311 | 121.2387 | 2.3758 | 0.16479 | 0.37079 | 121.9757 | -0.25177 | -0.045777 | -0.027466 | 0.073242 | 0.15106 | -0.59509 | -0.11902 | 0.14191 | 0.11902 | 0.29755 | 0.50354 | 121.3715 | 121.9391 | 0.073242 | 122.1085 | 2.5085 | -0.11902 | 121.9391 | 0.073242 | 2.5085 | 121.3715 | 122.1085 | -122.0123 | -122.0856
2004.4844 | 122.1497 | -0.11902 | 121.8292 | 0.12245 | 0.012191 | -0.0087051 | 0.014039 | 0.053746 | -0.0090406 | 0.066048 | -0.11444 | 121.8063 | -0.2243 | -0.059509 | 121.1655 | 2.3117 | 0.16022 | 0.17853 | 122.0078 | -0.27466 | -0.10529 | -0.022889 | 0.004578 | 0.05951 | -0.66376 | -0.15564 | 0.17853 | 0.10986 | 0.27924 | 0.29755 | 121.2845 | 121.9254 | 0.004578 | 122.1268 | 2.4307 | -0.15564 | 121.9254 | 0.004578 | 2.4307 | 121.2845 | 122.1268 | -122.0535 | -122.1039
2006.25 | 122.1634 | -0.09613 | 121.8475 | 0.01564 | 0.010055 | -0.0078507 | 0.0067762 | 0.049259 | -0.011604 | 0.065407 | -0.059509 | 121.7926 | -0.19684 | 0.022888 | 121.2479 | 2.4399 | 0.25635 | 0.42572 | 121.9666 | -0.24261 | -0.10071 | -0.054931 | 0.036621 | 0.11902 | -0.59967 | -0.14649 | 0.11902 | 0.13733 | 0.35248 | 0.52185 | 121.344 | 121.8887 | 0.036621 | 122.0627 | 2.536 | -0.14649 | 121.8887 | 0.036621 | 2.536 | 121.344 | 122.0627 | -122.0444 | -122.0901
2007.9531 | 122.0215 | -0.15564 | 121.8887 | -0.19035 | 0.012405 | -0.0046463 | 0.012971 | 0.049687 | -0.013527 | 0.064125 | -0.07782 | 121.8201 | -0.24261 | 0.027466 | 121.2433 | 2.4948 | 0.39368 | 0.48065 | 121.9849 | -0.27008 | -0.086975 | -0.068665 | 0.07782 | 0.18311 | -0.64545 | -0.11444 | 0.09613 | 0.16479 | 0.54932 | 0.63629 | 121.3989 | 121.9757 | 0.07782 | 122.1405 | 2.6505 | -0.11444 | 121.9757 | 0.07782 | 2.6505 | 121.3989 | 122.1405 | -122.1313 | -122.1588
2009.6875 | 122.1497 | -0.12817 | 121.8384 | 0.038529 | 0.0089872 | -0.0046463 | 0.0065624 | 0.050541 | -0.013099 | 0.066475 | -0.068665 | 121.8063 | -0.1831 | 0.022888 | 121.2616 | 2.4078 | 0.17395 | 0.37537 | 121.9391 | -0.24261 | -0.054931 | -0.032044 | 0.059509 | 0.15106 | -0.57678 | -0.11444 | 0.10071 | 0.11444 | 0.30212 | 0.50354 | 121.3898 | 121.9345 | 0.059509 | 122.0673 | 2.536 | -0.11444 | 121.9345 | 0.059509 | 2.536 | 121.3898 | 122.0673 | -122.0215 | -122.081
2011.4531 | 122.1405 | -0.10529 | 121.8658 | 0.061417 | 0.011764 | -0.011055 | 0.0095532 | 0.049687 | -0.010536 | 0.064553 | -0.036621 | 121.7926 | -0.17395 | 0.032043 | 121.2616 | 2.3941 | 0.13733 | 0.36621 | 121.9894 | -0.25177 | -0.068664 | -0.073242 | 0.068665 | 0.13733 | -0.60425 | -0.14648 | 0.1236 | 0.13733 | 0.24262 | 0.4715 | 121.3669 | 121.8979 | 0.068665 | 122.0947 | 2.4994 | -0.14648 | 121.8979 | 0.068665 | 2.4994 | 121.3669 | 122.0947 | -122.0398 | -122.1176
2013.1406 | 122.0535 | -0.13733 | 121.8842 | -0.12932 | 0.011123 | -0.0067825 | 0.007417 | 0.047123 | -0.010109 | 0.064553 | -0.009155 | 121.8201 | -0.17853 | 0.11902 | 121.3394 | 2.5589 | 0.30212 | 0.61798 | 121.9574 | -0.23804 | -0.041199 | -0.064087 | 0.12817 | 0.25635 | -0.54474 | -0.10071 | 0.073242 | 0.16937 | 0.43945 | 0.75531 | 121.4767 | 121.9574 | 0.12817 | 122.0947 | 2.6962 | -0.10071 | 121.9574 | 0.12817 | 2.6962 | 121.4767 | 122.0947 | -122.0627 | -122.1222
2014.8906 | 122.049 | -0.14648 | 121.9208 | -0.15221 | 0.013473 | -0.0089189 | 0.010621 | 0.046696 | -0.012031 | 0.064766 | 0.032043 | 121.8018 | -0.17395 | 0.10529 | 121.3348 | 2.5772 | 0.32959 | 0.63629 | 121.9986 | -0.23346 | -0.027466 | -0.11902 | 0.17853 | 0.25177 | -0.58594 | -0.086975 | 0.07782 | 0.20599 | 0.47607 | 0.78278 | 121.4813 | 121.9482 | 0.17853 | 122.1451 | 2.7237 | -0.086975 | 121.9482 | 0.17853 | 2.7237 | 121.4813 | 122.1451 | -122.0947 | -122.1542
2016.6406 | 122.1222 | -0.11902 | 121.8704 | 0.15297 | 0.0089872 | -0.0097733 | 0.01233 | 0.049046 | -0.011177 | 0.066902 | 0.009155 | 121.7834 | -0.1831 | 0.10071 | 121.3074 | 2.4353 | 0.009155 | 0.33875 | 121.962 | -0.21515 | -0.064086 | -0.086975 | 0.12817 | 0.21973 | -0.56305 | -0.09613 | 0.091553 | 0.19226 | 0.12817 | 0.45776 | 121.4264 | 121.9025 | 0.12817 | 122.081 | 2.5543 | -0.09613 | 121.9025 | 0.12817 | 2.5543 | 121.4264 | 122.081 | -122.0535 | -122.0856
2018.3906 | 122.0947 | -0.14648 | 121.8933 | -0.21324 | 0.010269 | -0.0102 | 0.013612 | 0.04755 | -0.01374 | 0.067116 | -0.11444 | 121.8018 | -0.21515 | 0 | 121.2158 | 2.4765 | 0.54474 | 0.51727 | 121.9757 | -0.27466 | -0.068665 | -0.091553 | 0.032043 | 0.14648 | -0.67749 | -0.12817 | 0.082397 | 0.10071 | 0.69122 | 0.66376 | 121.3623 | 121.9482 | 0.032043 | 122.1222 | 2.623 | -0.12817 | 121.9482 | 0.032043 | 2.623 | 121.3623 | 122.1222 | -122.1085 | -122.168
2020.0781 | 122.1405 | -0.13733 | 121.8887 | 0.084305 | 0.011551 | -0.0061417 | 0.015535 | 0.0546 | -0.012458 | 0.064766 | -0.09613 | 121.8475 | -0.2243 | -0.027466 | 121.1884 | 2.3575 | 0.23346 | 0.21515 | 122.0352 | -0.2655 | -0.086975 | -0.041199 | 0.041199 | 0.10986 | -0.70038 | -0.12817 | 0.14648 | 0.12817 | 0.37079 | 0.35248 | 121.3257 | 121.9849 | 0.041199 | 122.1725 | 2.4948 | -0.12817 | 121.9849 | 0.041199 | 2.4948 | 121.3257 | 122.1725 | -122.113 | -122.1542
2021.8281 | 122.1497 | -0.086975 | 121.8704 | 0.053787 | 0.011764 | -0.0059281 | 0.014039 | 0.051182 | -0.012886 | 0.066902 | -0.1236 | 121.8658 | -0.21057 | -0.032043 | 121.1792 | 2.33 | 0.23346 | 0.19226 | 121.994 | -0.27466 | -0.1236 | -0.004577 | -0.036621 | 0.054932 | -0.69122 | -0.18768 | 0.1236 | 0.086975 | 0.32043 | 0.27924 | 121.2662 | 121.9528 | -0.036621 | 122.081 | 2.417 | -0.18768 | 121.9528 | -0.036621 | 2.417 | 121.2662 | 122.081 | -122.081 | -122.1451
2023.5781 | 122.0993 | -0.14191 | 121.9391 | -0.26665 | 0.010055 | -0.0084915 | 0.0095532 | 0.045841 | -0.0094678 | 0.067543 | -0.11444 | 121.875 | -0.24261 | -0.009155 | 121.225 | 2.504 | 0.53558 | 0.48523 | 122.0169 | -0.28839 | -0.10071 | -0.064087 | 0.027466 | 0.13275 | -0.71411 | -0.14648 | 0.07782 | 0.12817 | 0.67749 | 0.62714 | 121.3669 | 122.0169 | 0.027466 | 122.1588 | 2.6459 | -0.14648 | 122.0169 | 0.027466 | 2.6459 | 121.3669 | 122.1588 | -122.1817 | -122.2275
2025.3281 | 122.1313 | -0.10986 | 121.8933 | -0.083542 | 0.011978 | -0.0059281 | 0.007417 | 0.047123 | -0.012886 | 0.064766 | -0.032043 | 121.843 | -0.17395 | 0.07782 | 121.3257 | 2.5269 | 0.28381 | 0.5722 | 121.9803 | -0.23804 | -0.064087 | -0.050354 | 0.07782 | 0.18768 | -0.56763 | -0.12817 | 0.086975 | 0.14191 | 0.39368 | 0.68207 | 121.4355 | 121.9528 | 0.07782 | 122.0901 | 2.6367 | -0.12817 | 121.9528 | 0.07782 | 2.6367 | 121.4355 | 122.0901 | -122.0673 | -122.1313
2027.0938 | 122.081 | -0.14648 | 121.9345 | -0.18272 | 0.012405 | -0.0082779 | 0.011049 | 0.048191 | -0.012245 | 0.066475 | -0.09613 | 121.8613 | -0.21057 | 0 | 121.2433 | 2.5131 | 0.48981 | 0.48065 | 122.0261 | -0.27924 | -0.064087 | -0.073242 | 0.050354 | 0.14648 | -0.69122 | -0.13275 | 0.091553 | 0.11444 | 0.63629 | 0.62714 | 121.3898 | 122.0078 | 0.050354 | 122.1725 | 2.6596 | -0.13275 | 122.0078 | 0.050354 | 2.6596 | 121.3898 | 122.1725 | -122.1451 | -122.2137
2028.7812 | 122.049 | -0.15106 | 121.9437 | -0.19035 | 0.0085598 | -0.010628 | 0.0069898 | 0.047337 | -0.010536 | 0.06498 | -0.009155 | 121.8475 | -0.1831 | 0.10529 | 121.3623 | 2.6047 | 0.35706 | 0.66376 | 121.9757 | -0.22888 | -0.032043 | -0.096131 | 0.14191 | 0.25635 | -0.58136 | -0.07782 | 0.032043 | 0.17395 | 0.50812 | 0.81482 | 121.5134 | 121.9986 | 0.14191 | 122.1268 | 2.7557 | -0.07782 | 121.9986 | 0.14191 | 2.7557 | 121.5134 | 122.1268 | -122.1268 | -122.1725
2030.5312 | 122.1771 | -0.10986 | 121.9025 | 0.076676 | 0.010269 | -0.0037919 | 0.015748 | 0.052037 | -0.014595 | 0.067757 | -0.10986 | 121.875 | -0.21515 | -0.050354 | 121.1975 | 2.3438 | 0.23804 | 0.21057 | 122.0123 | -0.25635 | -0.10529 | -0.027466 | 0 | 0.059509 | -0.70496 | -0.14649 | 0.10986 | 0.10529 | 0.3479 | 0.32043 | 121.3074 | 121.9849 | 0 | 122.1222 | 2.4536 | -0.14649 | 121.9849 | 0 | 2.4536 | 121.3074 | 122.1222 | -122.1176 | -122.1588
2032.2812 | 122.0901 | -0.14648 | 121.9025 | -0.19798 | 0.011337 | -0.011269 | 0.0086988 | 0.04691 | -0.010536 | 0.066475 | -0.10986 | 121.8658 | -0.2243 | -0.004578 | 121.2433 | 2.5131 | 0.53558 | 0.5127 | 122.0169 | -0.27008 | -0.07782 | -0.036621 | 0.036621 | 0.14191 | -0.65918 | -0.1236 | 0.11444 | 0.11444 | 0.68207 | 0.65918 | 121.3898 | 122.0123 | 0.036621 | 122.1634 | 2.6596 | -0.1236 | 122.0123 | 0.036621 | 2.6596 | 121.3898 | 122.1634 | -122.1268 | -122.1725
2033.9844 | 122.1176 | -0.11902 | 121.9162 | -0.22087 | 0.0092008 | -0.0099869 | 0.0099804 | 0.047978 | -0.012458 | 0.065834 | -0.1236 | 121.8475 | -0.2243 | -0.013733 | 121.2387 | 2.504 | 0.54016 | 0.52185 | 122.0444 | -0.2655 | -0.10529 | -0.068665 | -0.004577 | 0.10529 | -0.67749 | -0.14648 | 0.12817 | 0.10071 | 0.65918 | 0.64087 | 121.3577 | 121.9666 | -0.004577 | 122.1634 | 2.623 | -0.14648 | 121.9666 | -0.004577 | 2.623 | 121.3577 | 122.1634 | -122.1405 | -122.1817
2035.75 | 122.0581 | -0.16022 | 121.9299 | -0.20561 | 0.010269 | -0.0074235 | 0.0082714 | 0.046055 | -0.0096814 | 0.065407 | 0.004578 | 121.8338 | -0.15106 | 0.10986 | 121.3531 | 2.6138 | 0.36163 | 0.6546 | 121.9757 | -0.2243 | 0.009155 | -0.096131 | 0.16479 | 0.27008 | -0.57678 | -0.064087 | 0.045776 | 0.15564 | 0.52185 | 0.81482 | 121.5134 | 121.994 | 0.16479 | 122.1359 | 2.774 | -0.064087 | 121.994 | 0.16479 | 2.774 | 121.5134 | 122.1359 | -122.081 | -122.1542
2037.5 | 122.1222 | -0.12817 | 121.907 | 0.1606 | 0.0072782 | -0.0080643 | 0.014039 | 0.050114 | -0.012672 | 0.067757 | 0.018311 | 121.8613 | -0.14648 | 0.091553 | 121.3348 | 2.449 | -0.013733 | 0.33417 | 121.9803 | -0.21973 | -0.01831 | -0.045776 | 0.14649 | 0.21973 | -0.5722 | -0.091553 | 0.073243 | 0.16479 | 0.11444 | 0.46234 | 121.463 | 121.9894 | 0.14649 | 122.1085 | 2.5772 | -0.091553 | 121.9894 | 0.14649 | 2.5772 | 121.463 | 122.1085 | -122.0535 | -122.1268
2039.25 | 122.0306 | -0.15564 | 121.9437 | -0.091171 | 0.010055 | -0.0057145 | 0.014894 | 0.049473 | -0.012245 | 0.066262 | -0.045776 | 121.8658 | -0.20142 | 0.059509 | 121.2845 | 2.5177 | 0.29755 | 0.4303 | 122.0306 | -0.22888 | -0.045776 | -0.07782 | 0.10986 | 0.21515 | -0.65918 | -0.073242 | 0.086975 | 0.15564 | 0.45319 | 0.58594 | 121.4401 | 122.0215 | 0.10986 | 122.1863 | 2.6733 | -0.073242 | 122.0215 | 0.10986 | 2.6733 | 121.4401 | 122.1863 | -122.1451 | -122.1725
2040.9531 | 122.1863 | -0.11444 | 121.9254 | -0.014877 | 0.011337 | -0.0076371 | 0.0069898 | 0.04755 | -0.0083996 | 0.067757 | -0.064087 | 121.8979 | -0.16479 | 0.036621 | 121.3165 | 2.4673 | 0.25177 | 0.44861 | 122.0215 | -0.24719 | -0.050354 | -0.027466 | 0.050354 | 0.15106 | -0.60883 | -0.13275 | 0.09613 | 0.10071 | 0.36621 | 0.56305 | 121.431 | 122.0123 | 0.050354 | 122.1359 | 2.5818 | -0.13275 | 122.0123 | 0.050354 | 2.5818 | 121.431 | 122.1359 | -122.0901 | -122.1725
2042.6875 | 122.0398 | -0.14648 | 121.9437 | -0.091171 | 0.011978 | -0.014259 | 0.014467 | 0.047123 | -0.013313 | 0.066048 | -0.041199 | 121.8567 | -0.19226 | 0.064087 | 121.2799 | 2.5223 | 0.3067 | 0.43945 | 122.0261 | -0.24261 | -0.045777 | -0.086976 | 0.10529 | 0.21057 | -0.66376 | -0.096131 | 0.082397 | 0.15106 | 0.45319 | 0.58594 | 121.4264 | 122.0032 | 0.10529 | 122.1725 | 2.6688 | -0.096131 | 122.0032 | 0.10529 | 2.6688 | 121.4264 | 122.1725 | -122.1359 | -122.1863
2044.4375 | 122.1039 | -0.1236 | 121.9574 | -0.2285 | 0.011551 | -0.012123 | 0.010194 | 0.048832 | -0.01139 | 0.066048 | -0.10071 | 121.8842 | -0.20599 | -0.022888 | 121.2479 | 2.5314 | 0.55389 | 0.5127 | 122.0673 | -0.27008 | -0.082398 | -0.073242 | 0.022888 | 0.10071 | -0.70953 | -0.14649 | 0.10986 | 0.10529 | 0.67749 | 0.63629 | 121.3715 | 122.0078 | 0.022888 | 122.1909 | 2.655 | -0.14649 | 122.0078 | 0.022888 | 2.655 | 121.3715 | 122.1909 | -122.1634 | -122.2275
2046.1406 | 122.1542 | -0.1236 | 121.9299 | 0.14534 | 0.0092008 | -0.0087051 | 0.010621 | 0.050114 | -0.011177 | 0.06733 | 0.009155 | 121.8658 | -0.17395 | 0.09613 | 121.344 | 2.4628 | -0.013733 | 0.32044 | 122.0123 | -0.21515 | -0.050354 | -0.064087 | 0.13275 | 0.21973 | -0.58594 | -0.091553 | 0.082397 | 0.1831 | 0.10986 | 0.44403 | 121.4676 | 121.9894 | 0.13275 | 122.1359 | 2.5864 | -0.091553 | 121.9894 | 0.13275 | 2.5864 | 121.4676 | 122.1359 | -122.1039 | -122.1451
2047.8906 | 122.1497 | -0.11444 | 121.9299 | 0.17586 | 0.011551 | -0.0072099 | 0.014253 | 0.050755 | -0.013954 | 0.066475 | -0.041199 | 121.8567 | -0.19684 | 0.068665 | 121.3028 | 2.4353 | 0.036621 | 0.27924 | 122.0306 | -0.21973 | -0.082397 | -0.073243 | 0.073242 | 0.18311 | -0.62714 | -0.10529 | 0.10071 | 0.15564 | 0.15106 | 0.39368 | 121.4172 | 121.9711 | 0.073242 | 122.1451 | 2.5497 | -0.10529 | 121.9711 | 0.073242 | 2.5497 | 121.4172 | 122.1451 | -122.1268 | -122.1497
2049.6406 | 122.1313 | -0.11444 | 121.9208 | 0.18349 | 0.012832 | -0.010628 | 0.0097668 | 0.050968 | -0.011604 | 0.066475 | 0.018311 | 121.8658 | -0.15564 | 0.10529 | 121.3531 | 2.4719 | -0.018311 | 0.33875 | 121.9894 | -0.21515 | -0.041199 | -0.054931 | 0.13275 | 0.21973 | -0.56763 | -0.10071 | 0.068665 | 0.17395 | 0.09613 | 0.45319 | 121.4676 | 121.9803 | 0.13275 | 122.1039 | 2.5864 | -0.10071 | 121.9803 | 0.13275 | 2.5864 | 121.4676 | 122.1039 | -122.0764 | -122.1359
2051.3906 | 122.1451 | -0.10529 | 121.9345 | 0.16823 | 0.0098416 | -0.0044327 | 0.010194 | 0.049046 | -0.0094678 | 0.067116 | 0.004578 | 121.8613 | -0.16022 | 0.10986 | 121.3623 | 2.4719 | 0.004578 | 0.3479 | 122.0078 | -0.20142 | -0.054931 | -0.073242 | 0.10986 | 0.21515 | -0.5722 | -0.09613 | 0.073242 | 0.16479 | 0.10986 | 0.45319 | 121.4676 | 121.9666 | 0.10986 | 122.113 | 2.5772 | -0.09613 | 121.9666 | 0.10986 | 2.5772 | 121.4676 | 122.113 | -122.0947 | -122.1359
2053.1406 | 122.0627 | -0.14191 | 121.9345 | -0.098801 | 0.011764 | -0.0087051 | 0.015107 | 0.050328 | -0.013099 | 0.065407 | -0.022888 | 121.8887 | -0.20142 | 0.059509 | 121.3028 | 2.536 | 0.28381 | 0.40741 | 122.0398 | -0.26093 | -0.059509 | -0.045776 | 0.11902 | 0.20142 | -0.63171 | -0.11902 | 0.10529 | 0.17853 | 0.42572 | 0.54932 | 121.4447 | 122.0306 | 0.11902 | 122.1817 | 2.6779 | -0.11902 | 122.0306 | 0.11902 | 2.6779 | 121.4447 | 122.1817 | -122.1359 | -122.1954
2054.8281 | 122.2 | -0.082397 | 121.9116 | 0.13771 | 0.011764 | -0.0040055 | 0.012971 | 0.049046 | -0.012031 | 0.067116 | -0.10529 | 121.9025 | -0.20142 | -0.018311 | 121.2387 | 2.3712 | 0.16937 | 0.1831 | 122.0352 | -0.24719 | -0.11902 | -0.009155 | -0.022889 | 0.064086 | -0.67291 | -0.16479 | 0.1236 | 0.09613 | 0.25177 | 0.2655 | 121.3211 | 121.9849 | -0.022889 | 122.1176 | 2.4536 | -0.16479 | 121.9849 | -0.022889 | 2.4536 | 121.3211 | 122.1176 | -122.113 | -122.1588
2056.5781 | 122.0993 | -0.12817 | 121.9482 | -0.13695 | 0.010269 | -0.0082779 | 0.0069898 | 0.050114 | -0.008827 | 0.064339 | 0.009155 | 121.8796 | -0.14648 | 0.10529 | 121.3943 | 2.6321 | 0.30212 | 0.63629 | 122.0123 | -0.2243 | -0.01831 | -0.068664 | 0.13733 | 0.23346 | -0.55389 | -0.09613 | 0.064087 | 0.15564 | 0.4303 | 0.76447 | 121.5225 | 122.0078 | 0.13733 | 122.1405 | 2.7603 | -0.09613 | 122.0078 | 0.13733 | 2.7603 | 121.5225 | 122.1405 | -122.0947 | -122.1725
2058.3281 | 122.168 | -0.10986 | 121.9391 | 0.099564 | 0.011978 | -0.0082779 | 0.0093396 | 0.0499 | -0.013954 | 0.065834 | 0.004578 | 121.8475 | -0.16937 | 0.086975 | 121.3257 | 2.4811 | 0.059509 | 0.3479 | 122.0123 | -0.21057 | -0.05951 | -0.091553 | 0.11444 | 0.19684 | -0.6134 | -0.10071 | 0.073242 | 0.17395 | 0.16937 | 0.45776 | 121.4355 | 121.9574 | 0.11444 | 122.1222 | 2.5909 | -0.10071 | 121.9574 | 0.11444 | 2.5909 | 121.4355 | 122.1222 | -122.1085 | -122.1497
2060.0781 | 122.1771 | -0.1236 | 121.9391 | -0.30479 | 0.010482 | -0.0080643 | 0.010194 | 0.046696 | -0.0096814 | 0.065621 | -0.013733 | 121.8933 | -0.17395 | 0.11444 | 121.3852 | 2.5955 | 0.30212 | 0.60883 | 122.0078 | -0.2243 | -0.050354 | -0.045776 | 0.10986 | 0.23804 | -0.55389 | -0.10071 | 0.068664 | 0.16022 | 0.42572 | 0.73242 | 121.5088 | 122.0169 | 0.10986 | 122.1313 | 2.7191 | -0.10071 | 122.0169 | 0.10986 | 2.7191 | 121.5088 | 122.1313 | -122.113 | -122.1634
2061.7656 | 122.0993 | -0.13733 | 121.9711 | -0.19798 | 0.012832 | -0.0097733 | 0.012544 | 0.047764 | -0.013099 | 0.065621 | -0.086975 | 121.907 | -0.2243 | 0.004578 | 121.2799 | 2.5497 | 0.51727 | 0.49896 | 122.0947 | -0.25177 | -0.086975 | -0.064087 | 0.050354 | 0.14191 | -0.69122 | -0.11444 | 0.1236 | 0.13733 | 0.6546 | 0.63629 | 121.4172 | 122.0444 | 0.050354 | 122.2321 | 2.6871 | -0.11444 | 122.0444 | 0.050354 | 2.6871 | 121.4172 | 122.2321 | -122.1954 | -122.2229
2063.5156 | 122.081 | -0.13733 | 121.9757 | -0.13695 | 0.012405 | -0.0072099 | 0.012758 | 0.050328 | -0.012886 | 0.066048 | -0.032043 | 121.8796 | -0.20142 | 0.059509 | 121.2936 | 2.5681 | 0.38452 | 0.45776 | 122.0352 | -0.25177 | -0.064087 | -0.09613 | 0.10529 | 0.19684 | -0.68207 | -0.11444 | 0.059509 | 0.16937 | 0.52185 | 0.59509 | 121.431 | 122.0169 | 0.10529 | 122.1725 | 2.7054 | -0.11444 | 122.0169 | 0.10529 | 2.7054 | 121.431 | 122.1725 | -122.1771 | -122.2275
2065.2656 | 122.2 | -0.082397 | 121.9437 | 0.084305 | 0.011978 | -0.0025101 | 0.014253 | 0.051182 | -0.012886 | 0.066262 | -0.10529 | 121.9025 | -0.21973 | -0.004578 | 121.2387 | 2.4033 | 0.19684 | 0.20599 | 122.081 | -0.26093 | -0.13733 | -0.041199 | -0.022889 | 0.077819 | -0.70496 | -0.17853 | 0.13733 | 0.11444 | 0.27924 | 0.28839 | 121.3211 | 121.9849 | -0.022889 | 122.1634 | 2.4857 | -0.17853 | 121.9849 | -0.022889 | 2.4857 | 121.3211 | 122.1634 | -122.1634 | -122.2046
2066.9531 | 122.1634 | -0.10071 | 121.9437 | 0.13771 | 0.011123 | -0.0087051 | 0.008485 | 0.051823 | -0.012672 | 0.06797 | 0.013733 | 121.8567 | -0.15564 | 0.10529 | 121.3715 | 2.4902 | -0.004578 | 0.32959 | 122.0352 | -0.21515 | -0.054932 | -0.086976 | 0.11444 | 0.20599 | -0.5722 | -0.11444 | 0.091552 | 0.16937 | 0.09613 | 0.4303 | 121.4722 | 121.9574 | 0.11444 | 122.1359 | 2.5909 | -0.11444 | 121.9574 | 0.11444 | 2.5909 | 121.4722 | 122.1359 | -122.0993 | -122.1588
2068.7031 | 122.1313 | -0.11902 | 121.9391 | 0.030899 | 0.014328 | -0.0050735 | 0.013826 | 0.050328 | -0.012031 | 0.065621 | -0.073242 | 121.9162 | -0.19226 | 0.004578 | 121.2662 | 2.4399 | 0.24719 | 0.25635 | 122.0581 | -0.26093 | -0.073242 | -0.022888 | 0.045777 | 0.1236 | -0.67291 | -0.14191 | 0.11902 | 0.11902 | 0.36621 | 0.37537 | 121.3852 | 122.0352 | 0.045777 | 122.1771 | 2.5589 | -0.14191 | 122.0352 | 0.045777 | 2.5589 | 121.3852 | 122.1771 | -122.1313 | -122.2
2070.3906 | 122.1176 | -0.13275 | 121.9666 | -0.22087 | 0.013046 | -0.0080643 | 0.010408 | 0.049473 | -0.013313 | 0.064125 | -0.10986 | 121.9482 | -0.19684 | -0.004578 | 121.2799 | 2.5635 | 0.51727 | 0.49439 | 122.0535 | -0.25635 | -0.064087 | -0.018311 | 0.022888 | 0.12817 | -0.68665 | -0.1236 | 0.086975 | 0.086975 | 0.65002 | 0.62714 | 121.4127 | 122.081 | 0.022888 | 122.1863 | 2.6962 | -0.1236 | 122.081 | 0.022888 | 2.6962 | 121.4127 | 122.1863 | -122.1634 | -122.2229
2072.1406 | 122.081 | -0.14191 | 121.9849 | -0.17509 | 0.010055 | -0.0076371 | 0.0078442 | 0.049046 | -0.010963 | 0.066902 | 0.004578 | 121.9208 | -0.16479 | 0.10986 | 121.3943 | 2.6779 | 0.39825 | 0.63171 | 122.0444 | -0.20599 | -0.022888 | -0.064087 | 0.14649 | 0.25177 | -0.59052 | -0.064087 | 0.05951 | 0.16937 | 0.54016 | 0.77362 | 121.5363 | 122.0627 | 0.14649 | 122.1863 | 2.8198 | -0.064087 | 122.0627 | 0.14649 | 2.8198 | 121.5363 | 122.1863 | -122.1497 | -122.1909
2073.8281 | 122.0856 | -0.15564 | 121.9711 | -0.16747 | 0.0085598 | -0.0095597 | 0.008485 | 0.048832 | -0.012886 | 0.066475 | 0.013733 | 121.8704 | -0.16022 | 0.10529 | 121.3943 | 2.6642 | 0.37994 | 0.64545 | 122.0718 | -0.21057 | -0.004577 | -0.10071 | 0.16937 | 0.26093 | -0.57678 | -0.054931 | 0.10071 | 0.17395 | 0.53558 | 0.80109 | 121.55 | 122.0261 | 0.16937 | 122.2275 | 2.8198 | -0.054931 | 122.0261 | 0.16937 | 2.8198 | 121.55 | 122.2275 | -122.1313 | -122.1817
2075.5625 | 122.0718 | -0.11902 | 121.9803 | -0.12932 | 0.0094144 | -0.0055009 | 0.016816 | 0.050114 | -0.010963 | 0.064125 | -0.027466 | 121.9299 | -0.20599 | 0.045776 | 121.3348 | 2.5818 | 0.37994 | 0.45776 | 122.0673 | -0.23346 | -0.086975 | -0.050354 | 0.091553 | 0.16479 | -0.64545 | -0.11444 | 0.086975 | 0.17853 | 0.49896 | 0.57678 | 121.4539 | 122.049 | 0.091553 | 122.1863 | 2.7008 | -0.11444 | 122.049 | 0.091553 | 2.7008 | 121.4539 | 122.1863 | -122.1863 | -122.2137
2077.25 | 122.168 | -0.11444 | 121.9528 | 0.15297 | 0.011551 | -0.0044327 | 0.0086988 | 0.050541 | -0.011604 | 0.066902 | 0.022888 | 121.8842 | -0.15564 | 0.09613 | 121.3715 | 2.5131 | 0 | 0.35248 | 122.0123 | -0.2243 | -0.041199 | -0.068665 | 0.13733 | 0.21057 | -0.58136 | -0.10986 | 0.059509 | 0.17853 | 0.11444 | 0.46692 | 121.4859 | 121.9986 | 0.13733 | 122.1268 | 2.6276 | -0.10986 | 121.9986 | 0.13733 | 2.6276 | 121.4859 | 122.1268 | -122.1085 | -122.1771
2078.9375 | 122.0947 | -0.12817 | 121.9711 | -0.13695 | 0.011978 | -0.0065689 | 0.012971 | 0.050541 | -0.011818 | 0.066689 | -0.045776 | 121.9025 | -0.21515 | 0.041199 | 121.3257 | 2.5818 | 0.39368 | 0.48065 | 122.0581 | -0.23804 | -0.086975 | -0.068664 | 0.082398 | 0.16937 | -0.64545 | -0.10986 | 0.086975 | 0.16937 | 0.52185 | 0.60883 | 121.4539 | 122.0306 | 0.082398 | 122.1863 | 2.71 | -0.10986 | 122.0306 | 0.082398 | 2.71 | 121.4539 | 122.1863 | -122.1863 | -122.2092
2080.6875 | 122.2092 | -0.1236 | 121.9666 | -0.075912 | 0.011123 | -0.0084915 | 0.0059216 | 0.049046 | -0.010536 | 0.065407 | -0.013733 | 121.9025 | -0.15564 | 0.09613 | 121.3806 | 2.5909 | 0.28839 | 0.5722 | 122.0993 | -0.21515 | -0.032044 | -0.064087 | 0.10986 | 0.21973 | -0.58594 | -0.091553 | 0.13275 | 0.14191 | 0.41199 | 0.6958 | 121.5042 | 122.0261 | 0.10986 | 122.2229 | 2.7145 | -0.091553 | 122.0261 | 0.10986 | 2.7145 | 121.5042 | 122.2229 | -122.1222 | -122.1817
2082.3906 | 122.0718 | -0.14648 | 122.0032 | -0.091171 | 0.010269 | -0.0037919 | 0.014253 | 0.050755 | -0.013954 | 0.066475 | -0.022888 | 121.8933 | -0.19226 | 0.073242 | 121.3074 | 2.5818 | 0.31586 | 0.44403 | 122.0901 | -0.23346 | -0.045777 | -0.10986 | 0.1236 | 0.21973 | -0.6958 | -0.086975 | 0.086975 | 0.16937 | 0.46234 | 0.59052 | 121.4539 | 122.0398 | 0.1236 | 122.2366 | 2.7283 | -0.086975 | 122.0398 | 0.1236 | 2.7283 | 121.4539 | 122.2366 | -122.1954 | -122.2366
2084.1406 | 122.1313 | -0.12817 | 121.9894 | -0.13695 | 0.010482 | -0.0087051 | 0.0069898 | 0.050755 | -0.0090406 | 0.065193 | 0.027466 | 121.907 | -0.16937 | 0.11902 | 121.3943 | 2.6596 | 0.28839 | 0.6134 | 122.049 | -0.21057 | -0.041199 | -0.082398 | 0.15564 | 0.24719 | -0.59509 | -0.082397 | 0.059509 | 0.19684 | 0.41657 | 0.74158 | 121.5225 | 122.0352 | 0.15564 | 122.1771 | 2.7878 | -0.082397 | 122.0352 | 0.15564 | 2.7878 | 121.5225 | 122.1771 | -122.1588 | -122.2
2085.8281 | 122.1451 | -0.14648 | 121.9482 | -0.22087 | 0.013473 | -0.010414 | 0.012544 | 0.050968 | -0.012245 | 0.066048 | -0.086975 | 121.9391 | -0.20599 | -0.009155 | 121.2799 | 2.5818 | 0.54932 | 0.52185 | 122.1039 | -0.26093 | -0.05951 | -0.009155 | 0.059509 | 0.13733 | -0.66833 | -0.11444 | 0.15564 | 0.11902 | 0.6958 | 0.66833 | 121.4264 | 122.0856 | 0.059509 | 122.2504 | 2.7283 | -0.11444 | 122.0856 | 0.059509 | 2.7283 | 121.4264 | 122.2504 | -122.1542 | -122.2092
2087.5781 | 122.168 | -0.082397 | 121.9482 | 0.14534 | 0.0089872 | -0.0082779 | 0.01233 | 0.049687 | -0.012245 | 0.065407 | 0.004578 | 121.9437 | -0.16937 | 0.10071 | 121.3715 | 2.4948 | 0.013733 | 0.29755 | 122.0673 | -0.21973 | -0.086976 | -0.004577 | 0.086975 | 0.18311 | -0.57678 | -0.13733 | 0.11902 | 0.17395 | 0.09613 | 0.37994 | 121.4539 | 122.0261 | 0.086975 | 122.1497 | 2.5772 | -0.13733 | 122.0261 | 0.086975 | 2.5772 | 121.4539 | 122.1497 | -122.1176 | -122.168
2089.2656 | 122.1863 | -0.10986 | 121.9757 | 0.12245 | 0.010269 | -0.0048599 | 0.011689 | 0.051182 | -0.012672 | 0.068398 | 0.013733 | 121.8933 | -0.16479 | 0.09613 | 121.3715 | 2.5177 | -0.004578 | 0.32044 | 122.0398 | -0.21057 | -0.054932 | -0.082397 | 0.1236 | 0.20599 | -0.60425 | -0.10071 | 0.064087 | 0.17853 | 0.10529 | 0.4303 | 121.4813 | 122.0032 | 0.1236 | 122.1497 | 2.6276 | -0.10071 | 122.0032 | 0.1236 | 2.6276 | 121.4813 | 122.1497 | -122.1405 | -122.1863
2091.0156 | 122.1451 | -0.11902 | 121.9803 | -0.2285 | 0.01091 | -0.0057145 | 0.011476 | 0.047123 | -0.013099 | 0.065834 | -0.10071 | 121.9254 | -0.19226 | -0.009155 | 121.2936 | 2.5818 | 0.54016 | 0.48981 | 122.0993 | -0.27008 | -0.073242 | -0.054932 | 0.018311 | 0.10986 | -0.68665 | -0.15106 | 0.11902 | 0.091553 | 0.65918 | 0.60883 | 121.4127 | 122.0444 | 0.018311 | 122.2183 | 2.7008 | -0.15106 | 122.0444 | 0.018311 | 2.7008 | 121.4127 | 122.2183 | -122.1725 | -122.2504
2092.7656 | 122.2321 | -0.082397 | 121.9803 | 0.00038159 | 0.0098416 | -0.011055 | 0.0076306 | 0.049259 | -0.011177 | 0.064339 | -0.027466 | 121.907 | -0.17853 | 0.041199 | 121.3486 | 2.5223 | 0.24261 | 0.43488 | 122.0947 | -0.21973 | -0.096131 | -0.073243 | 0.054931 | 0.1236 | -0.63171 | -0.13733 | 0.11444 | 0.15106 | 0.32501 | 0.51727 | 121.431 | 121.9894 | 0.054931 | 122.1771 | 2.6047 | -0.13733 | 121.9894 | 0.054931 | 2.6047 | 121.431 | 122.1771 | -122.1588 | -122.2
2094.5312 | 122.1954 | -0.11444 | 121.9711 | 0.13008 | 0.011123 | -0.0050735 | 0.01233 | 0.050968 | -0.012672 | 0.065407 | 0.027466 | 121.8933 | -0.14648 | 0.11902 | 121.376 | 2.5223 | -0.004578 | 0.33875 | 122.0856 | -0.21973 | -0.032043 | -0.077819 | 0.14191 | 0.23346 | -0.59509 | -0.10529 | 0.11444 | 0.17395 | 0.10986 | 0.45319 | 121.4905 | 122.0078 | 0.14191 | 122.2 | 2.6367 | -0.10529 | 122.0078 | 0.14191 | 2.6367 | 121.4905 | 122.2 | -122.1176 | -122.1909
2096.2812 | 122.1634 | -0.13733 | 121.9986 | -0.22087 | 0.012191 | -0.0082779 | 0.012544 | 0.050328 | -0.011818 | 0.067543 | -0.091553 | 121.9391 | -0.19684 | 0 | 121.2982 | 2.5864 | 0.51727 | 0.49439 | 122.0856 | -0.25177 | -0.059509 | -0.059509 | 0.045776 | 0.13733 | -0.70038 | -0.11444 | 0.086975 | 0.10529 | 0.6546 | 0.63171 | 121.4355 | 122.0764 | 0.045776 | 122.2229 | 2.7237 | -0.11444 | 122.0764 | 0.045776 | 2.7237 | 121.4355 | 122.2229 | -122.1954 | -122.2504
2097.9688 | 122.2092 | -0.10986 | 121.9803 | 0.084305 | 0.011337 | -0.0067825 | 0.015535 | 0.051182 | -0.012672 | 0.06733 | -0.10071 | 121.9574 | -0.20599 | -0.018311 | 121.2662 | 2.4399 | 0.24719 | 0.22888 | 122.0993 | -0.24261 | -0.096131 | -0.022889 | 0.009155 | 0.091552 | -0.71411 | -0.13275 | 0.11902 | 0.10529 | 0.35706 | 0.33875 | 121.376 | 122.0673 | 0.009155 | 122.2092 | 2.5497 | -0.13275 | 122.0673 | 0.009155 | 2.5497 | 121.376 | 122.2092 | -122.1863 | -122.2229
2099.7188 | 122.1085 | -0.13733 | 122.0032 | -0.13695 | 0.011978 | -0.0057145 | 0.0054944 | 0.050328 | -0.012458 | 0.066262 | 0.027466 | 121.907 | -0.14648 | 0.1236 | 121.4493 | 2.6642 | 0.32501 | 0.6546 | 122.0627 | -0.21057 | -0.009155 | -0.096131 | 0.16479 | 0.26093 | -0.55389 | -0.073242 | 0.059509 | 0.17395 | 0.46234 | 0.79193 | 121.5866 | 122.0444 | 0.16479 | 122.2 | 2.8015 | -0.073242 | 122.0444 | 0.16479 | 2.8015 | 121.5866 | 122.2 | -122.1497 | -122.2137
2101.4062 | 122.1497 | -0.12817 | 121.9757 | -0.16747 | 0.012191 | -0.010628 | 0.013185 | 0.0499 | -0.013313 | 0.066902 | -0.054932 | 121.9666 | -0.20599 | 0.022888 | 121.3165 | 2.5864 | 0.48065 | 0.49896 | 122.1359 | -0.24719 | -0.07782 | -0.009155 | 0.073242 | 0.15106 | -0.65918 | -0.11902 | 0.16022 | 0.15106 | 0.60883 | 0.62714 | 121.4447 | 122.0947 | 0.073242 | 122.2641 | 2.7145 | -0.11902 | 122.0947 | 0.073242 | 2.7145 | 121.4447 | 122.2641 | -122.1817 | -122.2229
2103.1719 | 122.1268 | -0.14648 | 121.9986 | -0.19798 | 0.011551 | -0.011909 | 0.0065624 | 0.050541 | -0.010963 | 0.067543 | 0.009155 | 121.9116 | -0.13733 | 0.09613 | 121.3943 | 2.6917 | 0.42114 | 0.65918 | 122.0764 | -0.21057 | 0.009155 | -0.086975 | 0.15564 | 0.24261 | -0.60425 | -0.064087 | 0.07782 | 0.14648 | 0.56763 | 0.80566 | 121.5408 | 122.0581 | 0.15564 | 122.2229 | 2.8381 | -0.064087 | 122.0581 | 0.15564 | 2.8381 | 121.5408 | 122.2229 | -122.1359 | -122.2092
2104.8594 | 122.1634 | -0.09613 | 121.9849 | -0.19035 | 0.012191 | -0.012978 | 0.0080578 | 0.049046 | -0.013954 | 0.065621 | -0.073242 | 121.9666 | -0.20599 | 0.004578 | 121.3028 | 2.5955 | 0.55389 | 0.53101 | 122.1405 | -0.24261 | -0.10986 | -0.01831 | 0.022888 | 0.10071 | -0.68207 | -0.14649 | 0.15564 | 0.13275 | 0.65002 | 0.62714 | 121.3989 | 122.0627 | 0.022888 | 122.2366 | 2.6917 | -0.14649 | 122.0627 | 0.022888 | 2.6917 | 121.3989 | 122.2366 | -122.1909 | -122.2275
2106.6094 | 122.2321 | -0.10071 | 121.9757 | -0.053024 | 0.010696 | -0.0063553 | 0.0067762 | 0.050541 | -0.010536 | 0.066902 | -0.027466 | 121.9391 | -0.16479 | 0.07782 | 121.3806 | 2.6047 | 0.27924 | 0.52185 | 122.0947 | -0.21515 | -0.064087 | -0.036621 | 0.073242 | 0.17853 | -0.59509 | -0.11444 | 0.11902 | 0.13733 | 0.37994 | 0.62256 | 121.4813 | 122.0398 | 0.073242 | 122.1954 | 2.7054 | -0.11444 | 122.0398 | 0.073242 | 2.7054 | 121.4813 | 122.1954 | -122.1405 | -122.1909
2108.3594 | 122.2275 | -0.07782 | 121.9482 | 0.076676 | 0.010055 | -0.0099869 | 0.015962 | 0.050968 | -0.014381 | 0.065193 | -0.10529 | 121.9437 | -0.19684 | -0.018311 | 121.257 | 2.4536 | 0.21057 | 0.21057 | 122.1405 | -0.23804 | -0.11902 | -0.004577 | -0.027466 | 0.059509 | -0.69122 | -0.16022 | 0.19226 | 0.091552 | 0.28839 | 0.28839 | 121.3348 | 122.0215 | -0.027466 | 122.2183 | 2.5314 | -0.16022 | 122.0215 | -0.027466 | 2.5314 | 121.3348 | 122.2183 | -122.1451 | -122.1863
2110.125 | 122.1359 | -0.12817 | 122.0306 | -0.18272 | 0.0098416 | -0.012123 | 0.015321 | 0.052464 | -0.015022 | 0.064553 | -0.064087 | 121.9437 | -0.18768 | 0.027466 | 121.3394 | 2.6138 | 0.43488 | 0.50354 | 122.1313 | -0.23346 | -0.059509 | -0.086975 | 0.064087 | 0.15564 | -0.69122 | -0.10528 | 0.10071 | 0.1236 | 0.56305 | 0.63171 | 121.4676 | 122.0718 | 0.064087 | 122.2595 | 2.742 | -0.10528 | 122.0718 | 0.064087 | 2.742 | 121.4676 | 122.2595 | -122.2183 | -122.2641
2111.8281 | 122.2412 | -0.082397 | 121.9849 | 0.076676 | 0.011551 | -0.0087051 | 0.015321 | 0.049687 | -0.012245 | 0.068611 | -0.09613 | 121.9482 | -0.20142 | -0.009155 | 121.2753 | 2.4399 | 0.21515 | 0.20599 | 122.1497 | -0.23346 | -0.11902 | -0.036621 | -0.013733 | 0.073242 | -0.70953 | -0.15106 | 0.16479 | 0.10529 | 0.29755 | 0.28839 | 121.3577 | 122.0306 | -0.013733 | 122.2321 | 2.5223 | -0.15106 | 122.0306 | -0.013733 | 2.5223 | 121.3577 | 122.2321 | -122.1863 | -122.2183
2113.5781 | 122.2366 | -0.091553 | 121.9894 | 0.069046 | 0.010696 | -0.0082779 | 0.009126 | 0.050541 | -0.012886 | 0.067757 | -0.004578 | 121.9574 | -0.15564 | 0.059509 | 121.3669 | 2.5314 | 0.15564 | 0.37537 | 122.1039 | -0.20142 | -0.064087 | -0.032044 | 0.086975 | 0.15106 | -0.62256 | -0.10986 | 0.11444 | 0.15106 | 0.24719 | 0.46692 | 121.4584 | 122.049 | 0.086975 | 122.1954 | 2.623 | -0.10986 | 122.049 | 0.086975 | 2.623 | 121.4584 | 122.1954 | -122.1451 | -122.1909
2115.3438 | 122.1176 | -0.13733 | 121.9986 | -0.083542 | 0.010269 | -0.0061417 | 0.01468 | 0.050541 | -0.013527 | 0.06733 | -0.004578 | 121.9345 | -0.21057 | 0.059509 | 121.344 | 2.6047 | 0.29297 | 0.41199 | 122.113 | -0.22888 | -0.073242 | -0.064087 | 0.13275 | 0.19684 | -0.6546 | -0.091553 | 0.11444 | 0.20599 | 0.4303 | 0.54932 | 121.4813 | 122.0718 | 0.13275 | 122.2504 | 2.742 | -0.091553 | 122.0718 | 0.13275 | 2.742 | 121.4813 | 122.2504 | -122.2092 | -122.2275
2117.1094 | 122.1268 | -0.1236 | 122.049 | -0.060654 | 0.01091 | -0.0082779 | 0.012971 | 0.049046 | -0.013099 | 0.067543 | -0.027466 | 121.9299 | -0.17395 | 0.054932 | 121.3486 | 2.5818 | 0.27924 | 0.39368 | 122.1222 | -0.25177 | -0.050354 | -0.11902 | 0.09613 | 0.17853 | -0.70038 | -0.12817 | 0.073242 | 0.14648 | 0.40283 | 0.51727 | 121.4722 | 122.0535 | 0.09613 | 122.2458 | 2.7054 | -0.12817 | 122.0535 | 0.09613 | 2.7054 | 121.4722 | 122.2458 | -122.2229 | -122.3007
2118.7969 | 122.1817 | -0.12817 | 122.0123 | -0.21324 | 0.010482 | -0.0076371 | 0.010621 | 0.048619 | -0.010536 | 0.064553 | -0.091553 | 121.994 | -0.19226 | 0.009155 | 121.3257 | 2.6138 | 0.5127 | 0.49896 | 122.1039 | -0.23804 | -0.064087 | -0.01831 | 0.036621 | 0.13733 | -0.68664 | -0.10986 | 0.091553 | 0.10071 | 0.64087 | 0.62714 | 121.4539 | 122.1222 | 0.036621 | 122.2321 | 2.742 | -0.10986 | 122.1222 | 0.036621 | 2.742 | 121.4539 | 122.2321 | -122.2046 | -122.2504
2120.5469 | 122.2595 | -0.086975 | 121.9711 | 0.10719 | 0.011764 | -0.0055009 | 0.013398 | 0.052037 | -0.014381 | 0.066689 | -0.059509 | 121.9894 | -0.18768 | 0.004578 | 121.3165 | 2.4628 | 0.13275 | 0.20599 | 122.1176 | -0.24261 | -0.10071 | 0.018311 | 0.027466 | 0.091553 | -0.6546 | -0.15564 | 0.14648 | 0.12817 | 0.21973 | 0.29297 | 121.4035 | 122.0764 | 0.027466 | 122.2046 | 2.5497 | -0.15564 | 122.0764 | 0.027466 | 2.5497 | 121.4035 | 122.2046 | -122.1588 | -122.2137
2122.3125 | 122.1451 | -0.11902 | 122.0398 | -0.18272 | 0.010482 | -0.0052873 | 0.010621 | 0.050328 | -0.013099 | 0.067757 | -0.073242 | 121.9711 | -0.18768 | 0.045776 | 121.3623 | 2.6505 | 0.42114 | 0.49896 | 122.1176 | -0.23346 | -0.068664 | -0.068665 | 0.045777 | 0.16479 | -0.67749 | -0.11444 | 0.07782 | 0.11444 | 0.54016 | 0.61798 | 121.4813 | 122.0901 | 0.045777 | 122.2366 | 2.7695 | -0.11444 | 122.0901 | 0.045777 | 2.7695 | 121.4813 | 122.2366 | -122.2275 | -122.2733
2124 | 122.2183 | -0.10986 | 121.994 | 0.1606 | 0.0098416 | -0.0055009 | 0.0099804 | 0.049473 | -0.009895 | 0.067116 | 0.027466 | 121.9116 | -0.13733 | 0.10071 | 121.4172 | 2.5543 | 0.018311 | 0.36163 | 122.0947 | -0.19684 | -0.027466 | -0.082398 | 0.13733 | 0.21057 | -0.57678 | -0.086975 | 0.10071 | 0.16479 | 0.12817 | 0.4715 | 121.5271 | 122.0215 | 0.13733 | 122.2046 | 2.6642 | -0.086975 | 122.0215 | 0.13733 | 2.6642 | 121.5271 | 122.2046 | -122.1313 | -122.1909
2125.75 | 122.2366 | -0.07782 | 122.0078 | 0.091934 | 0.0094144 | -0.0082779 | 0.011262 | 0.050755 | -0.012672 | 0.068398 | -0.09613 | 121.9482 | -0.17853 | -0.004578 | 121.3074 | 2.4765 | 0.12817 | 0.21973 | 122.168 | -0.21057 | -0.10071 | -0.059509 | -0.01831 | 0.073242 | -0.70038 | -0.13275 | 0.16022 | 0.082398 | 0.20599 | 0.29755 | 121.3852 | 122.0261 | -0.01831 | 122.2458 | 2.5543 | -0.13275 | 122.0261 | -0.01831 | 2.5543 | 121.3852 | 122.2458 | -122.1863 | -122.2183
2127.5 | 122.168 | -0.14191 | 122.0398 | -0.17509 | 0.010696 | -0.0099869 | 0.012971 | 0.050968 | -0.012031 | 0.065834 | -0.07782 | 121.9528 | -0.18768 | 0.013733 | 121.3486 | 2.6276 | 0.50354 | 0.49896 | 122.1542 | -0.23346 | -0.045776 | -0.086975 | 0.064087 | 0.15564 | -0.69122 | -0.091552 | 0.11444 | 0.10986 | 0.64545 | 0.64087 | 121.4905 | 122.0947 | 0.064087 | 122.2961 | 2.7695 | -0.091552 | 122.0947 | 0.064087 | 2.7695 | 121.4905 | 122.2961 | -122.2275 | -122.2733
2129.25 | 122.2458 | -0.091553 | 122.0444 | -0.014877 | 0.011337 | -0.0052873 | 0.0059216 | 0.049473 | -0.010536 | 0.066475 | -0.050354 | 121.9528 | -0.15106 | 0.045776 | 121.3898 | 2.5864 | 0.27008 | 0.46234 | 122.1039 | -0.20599 | -0.059509 | -0.091553 | 0.041199 | 0.13733 | -0.6546 | -0.11444 | 0.059509 | 0.10071 | 0.36163 | 0.55389 | 121.4813 | 122.0444 | 0.041199 | 122.1954 | 2.6779 | -0.11444 | 122.0444 | 0.041199 | 2.6779 | 121.4813 | 122.1954 | -122.1954 | -122.2504
2130.9531 | 122.1451 | -0.13275 | 122.0398 | -0.083542 | 0.010269 | -0.0074235 | 0.01468 | 0.052891 | -0.012245 | 0.066902 | -0.018311 | 121.9299 | -0.19684 | 0.07782 | 121.3531 | 2.5955 | 0.3067 | 0.39825 | 122.1588 | -0.2243 | -0.064087 | -0.10986 | 0.11444 | 0.21057 | -0.68665 | -0.091553 | 0.11902 | 0.17853 | 0.43945 | 0.531 | 121.4859 | 122.0627 | 0.11444 | 122.2916 | 2.7283 | -0.091553 | 122.0627 | 0.11444 | 2.7283 | 121.4859 | 122.2916 | -122.2366 | -122.2641
2132.7031 | 122.1222 | -0.13733 | 122.0444 | -0.19035 | 0.0089872 | -0.01255 | 0.007417 | 0.049473 | -0.012031 | 0.066475 | 0.022888 | 121.9208 | -0.15106 | 0.12817 | 121.4447 | 2.7328 | 0.36621 | 0.67291 | 122.1313 | -0.19684 | -0.013733 | -0.1236 | 0.16022 | 0.2655 | -0.59967 | -0.059509 | 0.086975 | 0.17395 | 0.50354 | 0.81024 | 121.582 | 122.0581 | 0.16022 | 122.2687 | 2.8702 | -0.059509 | 122.0581 | 0.16022 | 2.8702 | 121.582 | 122.2687 | -122.1954 | -122.2412
2134.4531 | 122.2824 | -0.086975 | 122.0123 | 0.02327 | 0.0092008 | -0.0040055 | 0.0082714 | 0.050541 | -0.01075 | 0.067757 | -0.018311 | 121.9482 | -0.15106 | 0.054932 | 121.3806 | 2.5497 | 0.1831 | 0.39825 | 122.1222 | -0.23346 | -0.064087 | -0.064087 | 0.068664 | 0.14191 | -0.63171 | -0.14648 | 0.10986 | 0.13275 | 0.27008 | 0.48523 | 121.4676 | 122.0352 | 0.068664 | 122.2092 | 2.6367 | -0.14648 | 122.0352 | 0.068664 | 2.6367 | 121.4676 | 122.2092 | -122.1634 | -122.2458
2136.2188 | 122.1451 | -0.1236 | 122.0261 | -0.068283 | 0.010055 | -0.0102 | 0.013398 | 0.052677 | -0.011177 | 0.066902 | -0.018311 | 121.962 | -0.18768 | 0.064087 | 121.3486 | 2.5909 | 0.27924 | 0.40283 | 122.1359 | -0.25177 | -0.064087 | -0.064087 | 0.10528 | 0.18768 | -0.67749 | -0.12817 | 0.10986 | 0.16937 | 0.40283 | 0.52643 | 121.4722 | 122.0856 | 0.10528 | 122.2595 | 2.7145 | -0.12817 | 122.0856 | 0.10528 | 2.7145 | 121.4722 | 122.2595 | -122.2137 | -122.2778
2137.9062 | 122.2733 | -0.091553 | 121.994 | 0.02327 | 0.010055 | -0.0080643 | 0.0063488 | 0.048405 | -0.011177 | 0.068398 | -0.032043 | 121.9528 | -0.16479 | 0.045776 | 121.3806 | 2.5589 | 0.24261 | 0.42572 | 122.0993 | -0.21515 | -0.073242 | -0.041199 | 0.05951 | 0.13733 | -0.6134 | -0.1236 | 0.10529 | 0.13275 | 0.33417 | 0.51727 | 121.4722 | 122.0444 | 0.05951 | 122.1909 | 2.6505 | -0.1236 | 122.0444 | 0.05951 | 2.6505 | 121.4722 | 122.1909 | -122.1588 | -122.2092
2139.6406 | 122.2412 | -0.10071 | 122.0123 | -0.075912 | 0.009628 | -0.0063553 | 0.0086988 | 0.04755 | -0.01139 | 0.066902 | -0.018311 | 121.9482 | -0.15564 | 0.10986 | 121.4218 | 2.655 | 0.3067 | 0.57678 | 122.1222 | -0.20142 | -0.054932 | -0.064087 | 0.082397 | 0.21057 | -0.59051 | -0.10071 | 0.10986 | 0.13733 | 0.40741 | 0.67749 | 121.5225 | 122.0489 | 0.082397 | 122.2229 | 2.7557 | -0.10071 | 122.0489 | 0.082397 | 2.7557 | 121.5225 | 122.2229 | -122.168 | -122.2137
2141.3906 | 122.1222 | -0.14191 | 122.0398 | -0.18272 | 0.01091 | -0.0069961 | 0.0093396 | 0.047978 | -0.012245 | 0.066262 | 0.036621 | 121.9711 | -0.15106 | 0.13275 | 121.4493 | 2.7328 | 0.37079 | 0.67291 | 122.1085 | -0.19684 | -0.009155 | -0.068665 | 0.17853 | 0.27466 | -0.59051 | -0.054931 | 0.068664 | 0.18768 | 0.5127 | 0.81482 | 121.5912 | 122.113 | 0.17853 | 122.2504 | 2.8748 | -0.054931 | 122.113 | 0.17853 | 2.8748 | 121.5912 | 122.2504 | -122.1909 | -122.2366
2143.1562 | 122.2549 | -0.086975 | 122.0169 | 0.00038159 | 0.011337 | -0.0076371 | 0.010621 | 0.047764 | -0.010322 | 0.066475 | -0.032043 | 121.9666 | -0.14648 | 0.064087 | 121.3806 | 2.5681 | 0.25635 | 0.45319 | 122.1085 | -0.21973 | -0.059509 | -0.050354 | 0.054932 | 0.15106 | -0.63629 | -0.13275 | 0.091552 | 0.11444 | 0.34332 | 0.54016 | 121.4676 | 122.0535 | 0.054932 | 122.1954 | 2.655 | -0.13275 | 122.0535 | 0.054932 | 2.655 | 121.4676 | 122.1954 | -122.1634 | -122.2366
2144.8438 | 122.2778 | -0.07782 | 122.0215 | 0.091934 | 0.013046 | -0.0063553 | 0.016176 | 0.049473 | -0.012245 | 0.065407 | -0.091553 | 122.0123 | -0.20599 | 0 | 121.2936 | 2.4719 | 0.19226 | 0.20142 | 122.1451 | -0.21973 | -0.12817 | -0.009155 | -0.013733 | 0.07782 | -0.72784 | -0.14191 | 0.1236 | 0.11444 | 0.27008 | 0.27924 | 121.3715 | 122.0901 | -0.013733 | 122.2229 | 2.5497 | -0.14191 | 122.0901 | -0.013733 | 2.5497 | 121.3715 | 122.2229 | -122.2275 | -122.2412
2146.6094 | 122.168 | -0.11902 | 122.0444 | -0.12169 | 0.011123 | -0.0076371 | 0.0078442 | 0.047337 | -0.0094678 | 0.064553 | 0.027466 | 121.9757 | -0.13275 | 0.14648 | 121.4767 | 2.7283 | 0.31586 | 0.67291 | 122.0947 | -0.21057 | -0.013732 | -0.068665 | 0.14649 | 0.2655 | -0.56763 | -0.091552 | 0.050354 | 0.16022 | 0.43488 | 0.79193 | 121.5958 | 122.0947 | 0.14649 | 122.2137 | 2.8473 | -0.091552 | 122.0947 | 0.14649 | 2.8473 | 121.5958 | 122.2137 | -122.1771 | -122.2549
2148.375 | 122.2137 | -0.086975 | 122.0398 | -0.083542 | 0.011551 | -0.0097733 | 0.008485 | 0.04691 | -0.012886 | 0.064339 | 0.022888 | 121.962 | -0.15564 | 0.11902 | 121.4447 | 2.6733 | 0.29755 | 0.59052 | 122.1313 | -0.19226 | -0.068665 | -0.07782 | 0.10986 | 0.20599 | -0.59509 | -0.10529 | 0.091553 | 0.17853 | 0.38452 | 0.67749 | 121.5317 | 122.0489 | 0.10986 | 122.2183 | 2.7603 | -0.10529 | 122.0489 | 0.10986 | 2.7603 | 121.5317 | 122.2183 | -122.1954 | -122.2321
2150.0625 | 122.2321 | -0.082397 | 121.9803 | 0.10719 | 0.0085598 | -0.0072099 | 0.013185 | 0.048405 | -0.0092542 | 0.06498 | 0.027466 | 122.0032 | -0.15106 | 0.10529 | 121.4035 | 2.5635 | 0.07782 | 0.37537 | 122.1085 | -0.19684 | -0.068665 | 0.022888 | 0.10986 | 0.18768 | -0.57678 | -0.11444 | 0.12817 | 0.17853 | 0.16022 | 0.45776 | 121.4859 | 122.0856 | 0.10986 | 122.1909 | 2.6459 | -0.11444 | 122.0856 | 0.10986 | 2.6459 | 121.4859 | 122.1909 | -122.1313 | -122.1771
2151.8125 | 122.2046 | -0.10529 | 122.0261 | 0.02327 | 0.013046 | -0.010414 | 0.016176 | 0.0499 | -0.015449 | 0.06733 | -0.045776 | 121.9986 | -0.21515 | 0.027466 | 121.3211 | 2.5177 | 0.24261 | 0.27008 | 122.1588 | -0.21515 | -0.10986 | -0.027466 | 0.05951 | 0.13275 | -0.70496 | -0.10986 | 0.13275 | 0.16937 | 0.3479 | 0.37537 | 121.4264 | 122.1039 | 0.05951 | 122.2641 | 2.623 | -0.10986 | 122.1039 | 0.05951 | 2.623 | 121.4264 | 122.2641 | -122.2412 | -122.2412
2153.5938 | 122.2229 | -0.10071 | 122.0306 | -0.075912 | 0.0092008 | -0.0091325 | 0.0080578 | 0.048191 | -0.010536 | 0.064553 | -0.004578 | 121.994 | -0.16479 | 0.1236 | 121.463 | 2.6825 | 0.31128 | 0.59509 | 122.0993 | -0.23346 | -0.064087 | -0.036621 | 0.09613 | 0.2243 | -0.56763 | -0.13275 | 0.068664 | 0.16022 | 0.41199 | 0.6958 | 121.5637 | 122.0947 | 0.09613 | 122.2 | 2.7832 | -0.13275 | 122.0947 | 0.09613 | 2.7832 | 121.5637 | 122.2 | -122.1954 | -122.2641
2155.2656 | 122.2321 | -0.09613 | 122.0078 | 0.13771 | 0.010482 | -0.0069961 | 0.012117 | 0.051823 | -0.010109 | 0.066048 | 0.027466 | 121.9437 | -0.15564 | 0.12817 | 121.4493 | 2.5726 | -0.022888 | 0.33417 | 122.113 | -0.19684 | -0.05951 | -0.064086 | 0.1236 | 0.2243 | -0.55847 | -0.10071 | 0.10529 | 0.18311 | 0.073242 | 0.4303 | 121.5454 | 122.0398 | 0.1236 | 122.2092 | 2.6688 | -0.10071 | 122.0398 | 0.1236 | 2.6688 | 121.5454 | 122.2092 | -122.1634 | -122.2046
2157.0156 | 122.1771 | -0.10986 | 122.0261 | -0.20561 | 0.011551 | -0.0080643 | 0.013185 | 0.049259 | -0.01374 | 0.066689 | -0.068665 | 122.0169 | -0.20142 | 0.027466 | 121.3486 | 2.6459 | 0.50354 | 0.50354 | 122.1725 | -0.24261 | -0.091553 | -0.009155 | 0.041198 | 0.13733 | -0.67749 | -0.13275 | 0.14648 | 0.13275 | 0.6134 | 0.6134 | 121.4584 | 122.1268 | 0.041198 | 122.2824 | 2.7557 | -0.13275 | 122.1268 | 0.041198 | 2.7557 | 121.4584 | 122.2824 | -122.2275 | -122.2687
2158.7188 | 122.1542 | -0.14191 | 122.0718 | -0.17509 | 0.0094144 | -0.0076371 | 0.008485 | 0.047978 | -0.010536 | 0.065621 | 0.045776 | 121.9574 | -0.14648 | 0.13275 | 121.4859 | 2.7328 | 0.34332 | 0.66376 | 122.1313 | -0.20599 | -0.004577 | -0.11444 | 0.18768 | 0.27466 | -0.58594 | -0.064087 | 0.05951 | 0.19226 | 0.48523 | 0.80566 | 121.6278 | 122.0993 | 0.18768 | 122.2733 | 2.8748 | -0.064087 | 122.0993 | 0.18768 | 2.8748 | 121.6278 | 122.2733 | -122.2183 | -122.2778
2160.4688 | 122.2321 | -0.082397 | 122.0352 | 0.13771 | 0.010482 | -0.010841 | 0.0099804 | 0.050755 | -0.012672 | 0.065834 | 0.022888 | 121.9437 | -0.13733 | 0.11902 | 121.4539 | 2.5955 | -0.018311 | 0.3479 | 122.113 | -0.19684 | -0.054932 | -0.091552 | 0.10528 | 0.20142 | -0.58136 | -0.11444 | 0.07782 | 0.16022 | 0.064086 | 0.4303 | 121.5363 | 122.0261 | 0.10528 | 122.1954 | 2.6779 | -0.11444 | 122.0261 | 0.10528 | 2.6779 | 121.5363 | 122.1954 | -122.1725 | -122.2321
2162.2344 | 122.2458 | -0.091553 | 122.0306 | 0.19875 | 0.010269 | -0.0084915 | 0.012758 | 0.051396 | -0.012245 | 0.066902 | -0.009155 | 121.9574 | -0.16022 | 0.091553 | 121.4264 | 2.5452 | 0.032043 | 0.3067 | 122.1268 | -0.21057 | -0.068664 | -0.073243 | 0.082398 | 0.18311 | -0.60425 | -0.11902 | 0.09613 | 0.15106 | 0.1236 | 0.39825 | 121.5179 | 122.049 | 0.082398 | 122.2183 | 2.6367 | -0.11902 | 122.049 | 0.082398 | 2.6367 | 121.5179 | 122.2183 | -122.1909 | -122.2412
2164 | 122.2824 | -0.07782 | 122.0398 | 0.038529 | 0.011123 | -0.0059281 | 0.0089124 | 0.049473 | -0.0092542 | 0.065407 | -0.013733 | 121.9849 | -0.13733 | 0.064087 | 121.3989 | 2.5818 | 0.1831 | 0.38452 | 122.1222 | -0.19684 | -0.059509 | -0.054932 | 0.064087 | 0.14191 | -0.64087 | -0.11902 | 0.082397 | 0.1236 | 0.26092 | 0.46234 | 121.4767 | 122.0627 | 0.064087 | 122.2 | 2.6596 | -0.11902 | 122.0627 | 0.064087 | 2.6596 | 121.4767 | 122.2 | -122.1771 | -122.2366
2165.7031 | 122.2641 | -0.091553 | 122.0032 | -0.030136 | 0.011123 | -0.0080643 | 0.0082714 | 0.04691 | -0.010322 | 0.064553 | -0.013733 | 121.9574 | -0.15106 | 0.07782 | 121.4447 | 2.6367 | 0.27466 | 0.50354 | 122.1222 | -0.20599 | -0.059509 | -0.045777 | 0.07782 | 0.16937 | -0.55847 | -0.11444 | 0.11902 | 0.13733 | 0.36621 | 0.59509 | 121.5363 | 122.049 | 0.07782 | 122.2137 | 2.7283 | -0.11444 | 122.049 | 0.07782 | 2.7283 | 121.5363 | 122.2137 | -122.1542 | -122.2092
2167.4531 | 122.2916 | -0.068665 | 122.0078 | 0.10719 | 0.010055 | -0.0052873 | 0.016603 | 0.048619 | -0.013527 | 0.067757 | -0.07782 | 122.0032 | -0.18768 | -0.009155 | 121.3394 | 2.504 | 0.17853 | 0.19684 | 122.1359 | -0.23346 | -0.11902 | -0.004577 | -0.009155 | 0.05951 | -0.66833 | -0.16479 | 0.12817 | 0.10986 | 0.24719 | 0.2655 | 121.4081 | 122.0718 | -0.009155 | 122.2046 | 2.5726 | -0.16479 | 122.0718 | -0.009155 | 2.5726 | 121.4081 | 122.2046 | -122.1954 | -122.2412
2169.1406 | 122.1588 | -0.12817 | 122.0627 | -0.075912 | 0.0098416 | -0.0080643 | 0.014894 | 0.049687 | -0.015663 | 0.065834 | -0.004578 | 121.9849 | -0.1831 | 0.086975 | 121.3989 | 2.6505 | 0.28839 | 0.41657 | 122.168 | -0.22888 | -0.054931 | -0.07782 | 0.1236 | 0.21515 | -0.66376 | -0.10071 | 0.10529 | 0.17853 | 0.41657 | 0.54474 | 121.5271 | 122.113 | 0.1236 | 122.2961 | 2.7786 | -0.10071 | 122.113 | 0.1236 | 2.7786 | 121.5271 | 122.2961 | -122.2458 | -122.2916
2170.9062 | 122.2092 | -0.10529 | 122.081 | -0.23613 | 0.012405 | -0.0084915 | 0.011476 | 0.050114 | -0.012245 | 0.068611 | -0.082397 | 122.0261 | -0.20599 | 0.004578 | 121.344 | 2.6642 | 0.56305 | 0.52185 | 122.1817 | -0.24261 | -0.10071 | -0.054932 | 0.022889 | 0.10986 | -0.737 | -0.13733 | 0.10071 | 0.1236 | 0.66834 | 0.62714 | 121.4493 | 122.1313 | 0.022889 | 122.287 | 2.7695 | -0.13733 | 122.1313 | 0.022889 | 2.7695 | 121.4493 | 122.287 | -122.287 | -122.3236
2172.6719 | 122.1405 | -0.1236 | 122.0764 | -0.12169 | 0.011123 | -0.013191 | 0.011476 | 0.050755 | -0.01075 | 0.066048 | -0.032043 | 121.9803 | -0.19684 | 0.068665 | 121.4127 | 2.6871 | 0.38452 | 0.47607 | 122.168 | -0.22888 | -0.073242 | -0.09613 | 0.091553 | 0.19226 | -0.66376 | -0.10529 | 0.091553 | 0.1648 | 0.50812 | 0.59967 | 121.5363 | 122.1039 | 0.091553 | 122.2916 | 2.8107 | -0.10529 | 122.1039 | 0.091553 | 2.8107 | 121.5363 | 122.2916 | -122.2733 | -122.3053
2174.3594 | 122.2092 | -0.091553 | 122.0581 | -0.24376 | 0.010269 | -0.0087051 | 0.0095532 | 0.050328 | -0.012886 | 0.066475 | -0.07782 | 122.0215 | -0.20142 | 0.013733 | 121.3577 | 2.6733 | 0.55389 | 0.50812 | 122.2 | -0.2243 | -0.10986 | -0.036621 | 0.013733 | 0.10529 | -0.70038 | -0.13275 | 0.14191 | 0.1236 | 0.64545 | 0.59967 | 121.4493 | 122.113 | 0.013733 | 122.2916 | 2.7649 | -0.13275 | 122.113 | 0.013733 | 2.7649 | 121.4493 | 122.2916 | -122.2595 | -122.2824
2176.125 | 122.2778 | -0.064087 | 122.0261 | 0.099564 | 0.010482 | -0.0078507 | 0.014253 | 0.051609 | -0.01374 | 0.06733 | -0.091553 | 122.0306 | -0.20142 | 0.009155 | 121.3211 | 2.5131 | 0.20142 | 0.20599 | 122.168 | -0.2243 | -0.13733 | 0.004578 | -0.027466 | 0.073242 | -0.70496 | -0.16022 | 0.14191 | 0.10986 | 0.2655 | 0.27008 | 121.3852 | 122.0947 | -0.027466 | 122.2321 | 2.5772 | -0.16022 | 122.0947 | -0.027466 | 2.5772 | 121.3852 | 122.2321 | -122.2275 | -122.2504
2177.8906 | 122.168 | -0.12817 | 122.0581 | -0.19798 | 0.009628 | -0.0080643 | 0.011476 | 0.048832 | -0.013099 | 0.065407 | -0.059509 | 121.9849 | -0.19684 | 0.041199 | 121.4081 | 2.6917 | 0.46234 | 0.49896 | 122.1725 | -0.21057 | -0.068664 | -0.073242 | 0.068665 | 0.16937 | -0.65002 | -0.082397 | 0.11444 | 0.13733 | 0.59052 | 0.62714 | 121.5363 | 122.113 | 0.068665 | 122.3007 | 2.8198 | -0.082397 | 122.113 | 0.068665 | 2.8198 | 121.5363 | 122.3007 | -122.2549 | -122.2687
2179.6406 | 122.2458 | -0.09613 | 122.0352 | 0.15297 | 0.010055 | -0.010841 | 0.0099804 | 0.050968 | -0.01139 | 0.067543 | 0.045776 | 121.9711 | -0.12817 | 0.11902 | 121.4676 | 2.6047 | 0.022888 | 0.35248 | 122.1313 | -0.19684 | -0.032044 | -0.064087 | 0.14191 | 0.21515 | -0.56763 | -0.10071 | 0.096131 | 0.17395 | 0.11902 | 0.44861 | 121.5637 | 122.0673 | 0.14191 | 122.2275 | 2.7008 | -0.10071 | 122.0673 | 0.14191 | 2.7008 | 121.5637 | 122.2275 | -122.1634 | -122.2321
2181.3281 | 122.2549 | -0.07782 | 122.0444 | 0.14534 | 0.013046 | -0.0078507 | 0.012117 | 0.048832 | -0.01139 | 0.066902 | 0.009155 | 122.0078 | -0.16479 | 0.10071 | 121.4493 | 2.5909 | 0.027466 | 0.32044 | 122.1497 | -0.19226 | -0.086975 | -0.036622 | 0.086975 | 0.17853 | -0.59509 | -0.11444 | 0.10529 | 0.17395 | 0.10529 | 0.39826 | 121.5271 | 122.0856 | 0.086975 | 122.2275 | 2.6688 | -0.11444 | 122.0856 | 0.086975 | 2.6688 | 121.5271 | 122.2275 | -122.2092 | -122.2366
2183.0938 | 122.2687 | -0.073242 | 122.0673 | -0.037765 | 0.009628 | -0.0102 | 0.0048534 | 0.048832 | -0.010536 | 0.065834 | -0.009155 | 121.9894 | -0.15106 | 0.086975 | 121.4447 | 2.6688 | 0.29755 | 0.53101 | 122.1497 | -0.21973 | -0.07782 | -0.07782 | 0.064087 | 0.16022 | -0.62256 | -0.14649 | 0.082397 | 0.14191 | 0.37079 | 0.60425 | 121.5179 | 122.0627 | 0.064087 | 122.2229 | 2.742 | -0.14649 | 122.0627 | 0.064087 | 2.742 | 121.5179 | 122.2229 | -122.2183 | -122.287
2184.8438 | 122.3007 | -0.068665 | 122.0123 | 0.12245 | 0.010269 | -0.0044327 | 0.014253 | 0.051396 | -0.011177 | 0.066902 | -0.059509 | 122.0352 | -0.17853 | 0.013733 | 121.3394 | 2.5223 | 0.16479 | 0.21515 | 122.1634 | -0.24719 | -0.10986 | 0.022888 | 0.009156 | 0.082398 | -0.67291 | -0.17853 | 0.15106 | 0.11902 | 0.23346 | 0.28381 | 121.4081 | 122.1039 | 0.009156 | 122.2321 | 2.5909 | -0.17853 | 122.1039 | 0.009156 | 2.5909 | 121.4081 | 122.2321 | -122.1909 | -122.2595
2186.6094 | 122.2916 | -0.07782 | 122.0352 | -0.030136 | 0.010482 | -0.0063553 | 0.0067762 | 0.047978 | -0.012031 | 0.067543 | -0.018311 | 122.0169 | -0.15564 | 0.064087 | 121.4355 | 2.655 | 0.2655 | 0.4715 | 122.1222 | -0.21515 | -0.07782 | -0.01831 | 0.059509 | 0.14191 | -0.59967 | -0.13733 | 0.086975 | 0.13733 | 0.34332 | 0.54932 | 121.5134 | 122.0947 | 0.059509 | 122.2 | 2.7328 | -0.13733 | 122.0947 | 0.059509 | 2.7328 | 121.5134 | 122.2 | -122.1909 | -122.2504
2188.2969 | 122.1588 | -0.1236 | 122.0535 | -0.045395 | 0.011551 | -0.0048599 | 0.017457 | 0.051182 | -0.014595 | 0.066475 | -0.013733 | 122.0215 | -0.19226 | 0.059509 | 121.3989 | 2.6367 | 0.29297 | 0.37994 | 122.2046 | -0.21973 | -0.068665 | -0.032044 | 0.10986 | 0.1831 | -0.6546 | -0.096131 | 0.15106 | 0.17853 | 0.41656 | 0.50354 | 121.5225 | 122.1451 | 0.10986 | 122.3282 | 2.7603 | -0.096131 | 122.1451 | 0.10986 | 2.7603 | 121.5225 | 122.3282 | -122.2458 | -122.2733
2190.0469 | 122.168 | -0.13275 | 122.0947 | -0.068283 | 0.013046 | -0.0052873 | 0.013826 | 0.050328 | -0.012672 | 0.065621 | -0.013733 | 122.0078 | -0.1831 | 0.073242 | 121.4218 | 2.6505 | 0.29755 | 0.41657 | 122.1588 | -0.20599 | -0.050354 | -0.086976 | 0.11902 | 0.20599 | -0.67291 | -0.073243 | 0.064086 | 0.16937 | 0.4303 | 0.54932 | 121.5546 | 122.1405 | 0.11902 | 122.2916 | 2.7832 | -0.073243 | 122.1405 | 0.11902 | 2.7832 | 121.5546 | 122.2916 | -122.2778 | -122.3007
2191.7344 | 122.1817 | -0.10986 | 122.081 | -0.022507 | 0.011123 | -0.0061417 | 0.014253 | 0.051396 | -0.01139 | 0.068611 | -0.041199 | 121.9986 | -0.17853 | 0.050354 | 121.3852 | 2.6093 | 0.2655 | 0.34332 | 122.168 | -0.21515 | -0.068665 | -0.082398 | 0.068664 | 0.16022 | -0.6958 | -0.10529 | 0.086975 | 0.13733 | 0.37537 | 0.45319 | 121.4951 | 122.1085 | 0.068664 | 122.2778 | 2.7191 | -0.10529 | 122.1085 | 0.068664 | 2.7191 | 121.4951 | 122.2778 | -122.2595 | -122.2961
2193.4844 | 122.2229 | -0.10071 | 122.081 | 0.16823 | 0.009628 | -0.010414 | 0.0076306 | 0.050541 | -0.011177 | 0.066262 | 0.041199 | 121.9666 | -0.13275 | 0.11902 | 121.4676 | 2.6459 | 0.032043 | 0.37537 | 122.1222 | -0.19226 | -0.032043 | -0.11444 | 0.14191 | 0.21973 | -0.6134 | -0.091553 | 0.041198 | 0.17395 | 0.13275 | 0.47607 | 121.5683 | 122.0673 | 0.14191 | 122.2229 | 2.7466 | -0.091553 | 122.0673 | 0.14191 | 2.7466 | 121.5683 | 122.2229 | -122.2137 | -122.2733
2195.2344 | 122.1725 | -0.1236 | 122.0993 | -0.19035 | 0.0087734 | -0.0087051 | 0.0065624 | 0.047764 | -0.010322 | 0.066689 | 0.022888 | 121.9849 | -0.13275 | 0.13733 | 121.5042 | 2.7878 | 0.37537 | 0.66834 | 122.1313 | -0.20599 | -0.009155 | -0.11444 | 0.14648 | 0.26093 | -0.59509 | -0.082398 | 0.032044 | 0.15564 | 0.49896 | 0.79193 | 121.6278 | 122.1085 | 0.14648 | 122.2549 | 2.9114 | -0.082398 | 122.1085 | 0.14648 | 2.9114 | 121.6278 | 122.2549 | -122.2321 | -122.3053
2197 | 122.3053 | -0.082397 | 122.0398 | 0.038529 | 0.010696 | -0.0082779 | 0.0076306 | 0.0499 | -0.0096814 | 0.065834 | -0.009155 | 121.9986 | -0.15106 | 0.054932 | 121.4218 | 2.6001 | 0.21973 | 0.41657 | 122.1725 | -0.19226 | -0.068665 | -0.041199 | 0.073242 | 0.13733 | -0.61798 | -0.10986 | 0.13275 | 0.14191 | 0.30212 | 0.49896 | 121.5042 | 122.081 | 0.073242 | 122.2549 | 2.6825 | -0.10986 | 122.081 | 0.073242 | 2.6825 | 121.5042 | 122.2549 | -122.1909 | -122.2321
2198.7031 | 122.2321 | -0.091553 | 122.0535 | -0.23613 | 0.007919 | -0.0097733 | 0.010194 | 0.046055 | -0.012031 | 0.06733 | -0.091553 | 122.0215 | -0.20142 | 0.018311 | 121.3577 | 2.6871 | 0.56305 | 0.54474 | 122.1863 | -0.24719 | -0.10986 | -0.032044 | 0 | 0.10986 | -0.6958 | -0.15564 | 0.13275 | 0.10986 | 0.6546 | 0.63629 | 121.4493 | 122.113 | 0 | 122.2778 | 2.7786 | -0.15564 | 122.113 | 0 | 2.7786 | 121.4493 | 122.2778 | -122.2549 | -122.3007
2200.4688 | 122.287 | -0.054932 | 122.0306 | 0.10719 | 0.010482 | -0.0074235 | 0.012544 | 0.050114 | -0.013313 | 0.067757 | -0.054932 | 121.9986 | -0.19684 | 0.036621 | 121.3852 | 2.5589 | 0.09613 | 0.22888 | 122.1954 | -0.20599 | -0.14191 | -0.032044 | 0 | 0.091553 | -0.64545 | -0.15106 | 0.16479 | 0.14191 | 0.15106 | 0.28381 | 121.4401 | 122.0535 | 0 | 122.2504 | 2.6138 | -0.15106 | 122.0535 | 0 | 2.6138 | 121.4401 | 122.2504 | -122.2275 | -122.2366
2202.2188 | 122.3145 | -0.073242 | 122.0398 | 0.030899 | 0.012191 | -0.0102 | 0.0089124 | 0.048832 | -0.011177 | 0.064125 | -0.022888 | 122.0123 | -0.13733 | 0.07782 | 121.431 | 2.6184 | 0.21057 | 0.40741 | 122.1634 | -0.21973 | -0.064087 | -0.027466 | 0.050354 | 0.15106 | -0.60883 | -0.14649 | 0.1236 | 0.11444 | 0.28381 | 0.48065 | 121.5042 | 122.0856 | 0.050354 | 122.2366 | 2.6917 | -0.14649 | 122.0856 | 0.050354 | 2.6917 | 121.5042 | 122.2366 | -122.1771 | -122.2595
2203.9219 | 122.1909 | -0.13733 | 122.0673 | -0.16747 | 0.0094144 | -0.012123 | 0.010835 | 0.050541 | -0.012886 | 0.065193 | 0.036621 | 121.9849 | -0.13275 | 0.13275 | 121.4813 | 2.7924 | 0.40283 | 0.66834 | 122.168 | -0.19684 | 0.004578 | -0.082398 | 0.17395 | 0.27008 | -0.58594 | -0.059509 | 0.10071 | 0.16937 | 0.54016 | 0.80566 | 121.6187 | 122.1222 | 0.17395 | 122.3053 | 2.9297 | -0.059509 | 122.1222 | 0.17395 | 2.9297 | 121.6187 | 122.3053 | -122.2 | -122.2641
2205.6719 | 122.1954 | -0.11902 | 122.0993 | -0.12169 | 0.010696 | -0.0080643 | 0.0086988 | 0.047978 | -0.011177 | 0.067757 | 0.036621 | 121.9803 | -0.15106 | 0.14191 | 121.5088 | 2.7878 | 0.32959 | 0.64087 | 122.1359 | -0.20142 | -0.032043 | -0.11902 | 0.15564 | 0.26093 | -0.59052 | -0.082397 | 0.036621 | 0.18768 | 0.44861 | 0.75989 | 121.6278 | 122.0993 | 0.15564 | 122.2549 | 2.9068 | -0.082397 | 122.0993 | 0.15564 | 2.9068 | 121.6278 | 122.2549 | -122.2504 | -122.3007
2207.3594 | 122.287 | -0.07782 | 122.0535 | -0.014877 | 0.010055 | -0.010628 | 0.008485 | 0.046482 | -0.0096814 | 0.065407 | -0.027466 | 122.0215 | -0.14648 | 0.086975 | 121.4447 | 2.6733 | 0.27466 | 0.50354 | 122.1497 | -0.21515 | -0.068664 | -0.032044 | 0.050354 | 0.16479 | -0.60883 | -0.13733 | 0.09613 | 0.11902 | 0.35248 | 0.58136 | 121.5225 | 122.0993 | 0.050354 | 122.2275 | 2.7512 | -0.13733 | 122.0993 | 0.050354 | 2.7512 | 121.5225 | 122.2275 | -122.2 | -122.2687
2209.1094 | 122.2275 | -0.11444 | 122.0718 | -0.25139 | 0.013046 | -0.013191 | 0.012971 | 0.049259 | -0.012031 | 0.067116 | -0.064087 | 122.0398 | -0.17853 | 0.022888 | 121.3669 | 2.6962 | 0.5722 | 0.53101 | 122.2275 | -0.2243 | -0.064087 | -0.032043 | 0.050354 | 0.13733 | -0.70496 | -0.10986 | 0.15564 | 0.11444 | 0.68665 | 0.64545 | 121.4813 | 122.1542 | 0.050354 | 122.3419 | 2.8107 | -0.10986 | 122.1542 | 0.050354 | 2.8107 | 121.4813 | 122.3419 | -122.2504 | -122.2961
2210.7969 | 122.1725 | -0.10529 | 122.113 | -0.098801 | 0.011123 | -0.0080643 | 0.015535 | 0.051182 | -0.015663 | 0.065407 | -0.009155 | 122.0169 | -0.19684 | 0.091553 | 121.4172 | 2.6962 | 0.32959 | 0.46692 | 122.1954 | -0.2243 | -0.091552 | -0.09613 | 0.096131 | 0.19684 | -0.6958 | -0.11902 | 0.082398 | 0.18768 | 0.43488 | 0.5722 | 121.5225 | 122.1222 | 0.096131 | 122.3007 | 2.8015 | -0.11902 | 122.1222 | 0.096131 | 2.8015 | 121.5225 | 122.3007 | -122.3099 | -122.3373
2212.5469 | 122.2824 | -0.068665 | 122.081 | -0.060654 | 0.009628 | -0.0102 | 0.0061352 | 0.051396 | -0.014167 | 0.067757 | 0 | 122.0352 | -0.14191 | 0.10529 | 121.5042 | 2.7054 | 0.29755 | 0.56763 | 122.1405 | -0.22888 | -0.073242 | -0.045777 | 0.068665 | 0.17395 | -0.57678 | -0.16022 | 0.059509 | 0.14191 | 0.36621 | 0.63629 | 121.5729 | 122.1039 | 0.068665 | 122.2092 | 2.774 | -0.16022 | 122.1039 | 0.068665 | 2.774 | 121.5729 | 122.2092 | -122.2229 | -122.3099
2214.25 | 122.1817 | -0.11902 | 122.1039 | -0.12932 | 0.0085598 | -0.0016557 | 0.015962 | 0.051396 | -0.013099 | 0.065834 | -0.018311 | 122.0032 | -0.1831 | 0.082397 | 121.4172 | 2.7191 | 0.37079 | 0.48981 | 122.2046 | -0.21515 | -0.064086 | -0.10071 | 0.10071 | 0.20142 | -0.68665 | -0.09613 | 0.10071 | 0.16479 | 0.48981 | 0.60883 | 121.5363 | 122.1222 | 0.10071 | 122.3236 | 2.8381 | -0.09613 | 122.1222 | 0.10071 | 2.8381 | 121.5363 | 122.3236 | -122.287 | -122.319
2216 | 122.2961 | -0.059509 | 122.0261 | 0.11482 | 0.010055 | -0.0091325 | 0.012758 | 0.051182 | -0.013099 | 0.066048 | -0.068665 | 122.0078 | -0.19684 | 0.013733 | 121.3715 | 2.5406 | 0.18768 | 0.20599 | 122.2092 | -0.22888 | -0.13733 | -0.018311 | -0.009156 | 0.073242 | -0.6546 | -0.16937 | 0.1831 | 0.12817 | 0.24719 | 0.2655 | 121.431 | 122.0673 | -0.009156 | 122.2687 | 2.6001 | -0.16937 | 122.0673 | -0.009156 | 2.6001 | 121.431 | 122.2687 | -122.2229 | -122.2549
2217.6875 | 122.2961 | -0.068665 | 122.0627 | 0.091934 | 0.012619 | -0.0093461 | 0.012544 | 0.050968 | -0.014381 | 0.067116 | -0.07782 | 122.0581 | -0.20599 | 0.009155 | 121.3486 | 2.5589 | 0.21515 | 0.21057 | 122.2137 | -0.23346 | -0.13733 | -0.004578 | -0.009155 | 0.07782 | -0.71411 | -0.16479 | 0.15106 | 0.12817 | 0.28381 | 0.27924 | 121.4172 | 122.1268 | -0.009155 | 122.2824 | 2.6276 | -0.16479 | 122.1268 | -0.009155 | 2.6276 | 121.4172 | 122.2824 | -122.2687 | -122.2961
2219.4375 | 122.1817 | -0.11902 | 122.1268 | -0.11406 | 0.010482 | -0.0044327 | 0.01233 | 0.049687 | -0.012458 | 0.067116 | -0.018311 | 122.0215 | -0.17395 | 0.068665 | 121.4218 | 2.71 | 0.35706 | 0.46234 | 122.2 | -0.21057 | -0.054931 | -0.10529 | 0.10071 | 0.18768 | -0.70496 | -0.091552 | 0.073242 | 0.15564 | 0.47607 | 0.58136 | 121.5408 | 122.1405 | 0.10071 | 122.319 | 2.829 | -0.091552 | 122.1405 | 0.10071 | 2.829 | 121.5408 | 122.319 | -122.3007 | -122.3373
2221.2031 | 122.3465 | -0.059509 | 122.049 | 0.00038159 | 0.0087734 | -0.012337 | 0.0061352 | 0.049046 | -0.01139 | 0.066689 | -0.027466 | 122.0306 | -0.13733 | 0.059509 | 121.4401 | 2.6505 | 0.24261 | 0.4303 | 122.1863 | -0.20599 | -0.07782 | -0.01831 | 0.032043 | 0.11902 | -0.60883 | -0.14649 | 0.13733 | 0.10986 | 0.30212 | 0.48981 | 121.4996 | 122.0901 | 0.032043 | 122.2458 | 2.71 | -0.14649 | 122.0901 | 0.032043 | 2.71 | 121.4996 | 122.2458 | -122.1863 | -122.2549
2222.8906 | 122.3328 | -0.082397 | 122.0306 | 0.046158 | 0.0092008 | -0.0069961 | 0.007417 | 0.051182 | -0.011604 | 0.066902 | -0.013733 | 122.0306 | -0.14648 | 0.064087 | 121.4401 | 2.6367 | 0.19684 | 0.40283 | 122.1817 | -0.20142 | -0.064087 | 0 | 0.068664 | 0.14648 | -0.59052 | -0.11902 | 0.15106 | 0.13275 | 0.27924 | 0.48523 | 121.5225 | 122.113 | 0.068664 | 122.2641 | 2.7191 | -0.11902 | 122.113 | 0.068664 | 2.7191 | 121.5225 | 122.2641 | -122.1771 | -122.2321
2224.6406 | 122.3053 | -0.068665 | 122.0215 | 0.091934 | 0.011764 | -0.0061417 | 0.014253 | 0.049259 | -0.015022 | 0.067116 | -0.059509 | 122.049 | -0.19226 | 0 | 121.3623 | 2.5635 | 0.20599 | 0.20142 | 122.2092 | -0.21515 | -0.1236 | 0.027466 | 0.009156 | 0.068665 | -0.65918 | -0.14648 | 0.18768 | 0.13275 | 0.27466 | 0.27008 | 121.431 | 122.1176 | 0.009156 | 122.2778 | 2.6321 | -0.14648 | 122.1176 | 0.009156 | 2.6321 | 121.431 | 122.2778 | -122.2137 | -122.2366
2226.3281 | 122.1909 | -0.11902 | 122.0856 | -0.083542 | 0.011123 | -0.0055009 | 0.014467 | 0.049687 | -0.014381 | 0.067757 | -0.009155 | 122.0261 | -0.16479 | 0.082397 | 121.431 | 2.7191 | 0.3067 | 0.43488 | 122.2092 | -0.2243 | -0.045776 | -0.059509 | 0.10986 | 0.20142 | -0.6546 | -0.10529 | 0.1236 | 0.15564 | 0.42572 | 0.55389 | 121.55 | 122.1451 | 0.10986 | 122.3282 | 2.8381 | -0.10529 | 122.1451 | 0.10986 | 2.8381 | 121.55 | 122.3282 | -122.2504 | -122.3099
2228.0781 | 122.2412 | -0.10529 | 122.0856 | -0.24376 | 0.013046 | -0.0091325 | 0.010194 | 0.048191 | -0.010322 | 0.066689 | -0.073242 | 122.1039 | -0.18768 | 0.009155 | 121.3898 | 2.7191 | 0.56305 | 0.54016 | 122.2137 | -0.24719 | -0.082397 | 0.018311 | 0.032044 | 0.11444 | -0.6958 | -0.14191 | 0.12817 | 0.11444 | 0.66834 | 0.64545 | 121.4951 | 122.2092 | 0.032044 | 122.319 | 2.8244 | -0.14191 | 122.2092 | 0.032044 | 2.8244 | 121.4951 | 122.319 | -122.2733 | -122.3328
2229.8281 | 122.1771 | -0.13275 | 122.0993 | -0.14458 | 0.013473 | -0.0072099 | 0.0076306 | 0.047764 | -0.010536 | 0.066262 | 0.054932 | 122.0261 | -0.14648 | 0.1236 | 121.5225 | 2.8061 | 0.36163 | 0.67749 | 122.1359 | -0.20142 | -0.013733 | -0.073242 | 0.18768 | 0.25635 | -0.57678 | -0.068665 | 0.036621 | 0.20142 | 0.49438 | 0.81024 | 121.6553 | 122.1588 | 0.18768 | 122.2687 | 2.9388 | -0.068665 | 122.1588 | 0.18768 | 2.9388 | 121.6553 | 122.2687 | -122.2458 | -122.3007
2231.5625 | 122.287 | -0.086975 | 122.0673 | 0.046158 | 0.0098416 | -0.0048599 | 0.015107 | 0.049046 | -0.014808 | 0.06797 | -0.073242 | 122.0078 | -0.19684 | 0 | 121.3669 | 2.5909 | 0.27008 | 0.26093 | 122.2092 | -0.21057 | -0.10986 | -0.05951 | 0.013733 | 0.086975 | -0.70038 | -0.1236 | 0.14191 | 0.1236 | 0.35706 | 0.3479 | 121.4539 | 122.0947 | 0.013733 | 122.2961 | 2.6779 | -0.1236 | 122.0947 | 0.013733 | 2.6779 | 121.4539 | 122.2961 | -122.2641 | -122.2778
2233.3125 | 122.1725 | -0.11444 | 122.0901 | -0.14458 | 0.010482 | -0.0042191 | 0.012971 | 0.047978 | -0.013527 | 0.067543 | -0.036621 | 122.1085 | -0.18768 | 0.068665 | 121.4355 | 2.7328 | 0.40283 | 0.49896 | 122.1909 | -0.23804 | -0.073242 | 0.01831 | 0.07782 | 0.18311 | -0.6546 | -0.1236 | 0.10071 | 0.15106 | 0.51727 | 0.6134 | 121.55 | 122.2229 | 0.07782 | 122.3053 | 2.8473 | -0.1236 | 122.2229 | 0.07782 | 2.8473 | 121.55 | 122.3053 | -122.2778 | -122.3282
2235 | 122.168 | -0.11444 | 122.1176 | -0.083542 | 0.014755 | -0.0076371 | 0.01233 | 0.049687 | -0.011818 | 0.066902 | -0.009155 | 122.0581 | -0.17853 | 0.07782 | 121.4401 | 2.7466 | 0.32501 | 0.45319 | 122.1817 | -0.2243 | -0.064087 | -0.05951 | 0.10529 | 0.19226 | -0.67749 | -0.10986 | 0.064087 | 0.16937 | 0.43945 | 0.56763 | 121.5546 | 122.1725 | 0.10529 | 122.2961 | 2.861 | -0.10986 | 122.1725 | 0.10529 | 2.861 | 121.5546 | 122.2961 | -122.2961 | -122.3419
2236.7344 | 122.3419 | -0.07782 | 122.0581 | 0.053787 | 0.011123 | -0.0084915 | 0.0052808 | 0.04755 | -0.0096814 | 0.06797 | -0.027466 | 122.0261 | -0.13275 | 0.059509 | 121.4676 | 2.6505 | 0.21515 | 0.39825 | 122.2092 | -0.19684 | -0.054931 | -0.032043 | 0.050354 | 0.13733 | -0.59051 | -0.11902 | 0.15106 | 0.10529 | 0.29297 | 0.47607 | 121.5454 | 122.1039 | 0.050354 | 122.287 | 2.7283 | -0.11902 | 122.1039 | 0.050354 | 2.7283 | 121.5454 | 122.287 | -122.1909 | -122.2549
2238.4375 | 122.3053 | -0.064087 | 122.0535 | 0.0080111 | 0.011551 | -0.0099869 | 0.0050672 | 0.048405 | -0.009895 | 0.067116 | -0.027466 | 122.049 | -0.14648 | 0.073242 | 121.4493 | 2.6688 | 0.27466 | 0.46234 | 122.1909 | -0.2243 | -0.082397 | -0.004578 | 0.036621 | 0.13733 | -0.60425 | -0.16022 | 0.13733 | 0.11902 | 0.33875 | 0.52643 | 121.5134 | 122.113 | 0.036621 | 122.2549 | 2.7328 | -0.16022 | 122.113 | 0.036621 | 2.7328 | 121.5134 | 122.2549 | -122.2 | -122.2778
2240.1875 | 122.2458 | -0.10986 | 122.1268 | -0.24376 | 0.009628 | -0.0082779 | 0.011689 | 0.049046 | -0.013527 | 0.066048 | -0.086975 | 122.0398 | -0.18768 | 0.013733 | 121.3852 | 2.7512 | 0.56763 | 0.54932 | 122.2412 | -0.24261 | -0.07782 | -0.086975 | 0.022888 | 0.1236 | -0.74158 | -0.13275 | 0.11444 | 0.10071 | 0.67749 | 0.65918 | 121.4951 | 122.1497 | 0.022888 | 122.3511 | 2.861 | -0.13275 | 122.1497 | 0.022888 | 2.861 | 121.4951 | 122.3511 | -122.3145 | -122.3694
2241.9375 | 122.1817 | -0.13733 | 122.1085 | -0.18272 | 0.0087734 | -0.0087051 | 0.008485 | 0.048191 | -0.01139 | 0.061989 | 0.054932 | 122.0306 | -0.11444 | 0.15106 | 121.5317 | 2.8244 | 0.36621 | 0.68665 | 122.2137 | -0.1831 | 0.022888 | -0.077819 | 0.19226 | 0.28839 | -0.57678 | -0.045776 | 0.10529 | 0.16937 | 0.50354 | 0.82398 | 121.669 | 122.168 | 0.19226 | 122.3511 | 2.9617 | -0.045776 | 122.168 | 0.19226 | 2.9617 | 121.669 | 122.3511 | -122.2229 | -122.2916
2243.6406 | 122.1771 | -0.11444 | 122.1085 | -0.11406 | 0.012832 | -0.0082779 | 0.016389 | 0.051396 | -0.013954 | 0.066048 | -0.009155 | 122.0444 | -0.1831 | 0.07782 | 121.4401 | 2.7466 | 0.37994 | 0.48981 | 122.2458 | -0.2243 | -0.068664 | -0.064086 | 0.10529 | 0.19226 | -0.66833 | -0.10986 | 0.13733 | 0.17395 | 0.49439 | 0.60425 | 121.5546 | 122.1588 | 0.10529 | 122.3602 | 2.861 | -0.10986 | 122.1588 | 0.10529 | 2.861 | 121.5546 | 122.3602 | -122.2916 | -122.3328
2245.3906 | 122.3099 | -0.073242 | 122.0581 | 0.069046 | 0.01091 | -0.0067825 | 0.013826 | 0.050755 | -0.011177 | 0.067543 | -0.07782 | 122.0764 | -0.1831 | 0.009155 | 121.3577 | 2.5818 | 0.21973 | 0.20142 | 122.2458 | -0.2243 | -0.10986 | 0.018311 | -0.004578 | 0.082397 | -0.70038 | -0.15106 | 0.18768 | 0.10528 | 0.29297 | 0.27466 | 121.431 | 122.1497 | -0.004578 | 122.319 | 2.655 | -0.15106 | 122.1497 | -0.004578 | 2.655 | 121.431 | 122.319 | -122.2412 | -122.2824
2247.1406 | 122.2046 | -0.13275 | 122.1085 | -0.16747 | 0.0092008 | -0.0078507 | 0.0086988 | 0.047123 | -0.010536 | 0.065621 | 0.032043 | 122.0581 | -0.15564 | 0.11902 | 121.5042 | 2.8152 | 0.4715 | 0.65918 | 122.168 | -0.20599 | -0.022889 | -0.050354 | 0.16479 | 0.25177 | -0.60425 | -0.073243 | 0.05951 | 0.18768 | 0.60425 | 0.79193 | 121.637 | 122.1909 | 0.16479 | 122.3007 | 2.948 | -0.073243 | 122.1909 | 0.16479 | 2.948 | 121.637 | 122.3007 | -122.2641 | -122.3145
2248.8281 | 122.319 | -0.07782 | 122.0581 | 0.053787 | 0.009628 | -0.010628 | 0.014467 | 0.049687 | -0.015449 | 0.066475 | -0.082397 | 122.0352 | -0.18768 | 0.013733 | 121.3623 | 2.5955 | 0.22888 | 0.23804 | 122.2504 | -0.22888 | -0.10986 | -0.022888 | -0.004577 | 0.091553 | -0.6958 | -0.15106 | 0.19226 | 0.10529 | 0.3067 | 0.31586 | 121.4401 | 122.113 | -0.004577 | 122.3282 | 2.6733 | -0.15106 | 122.113 | -0.004577 | 2.6733 | 121.4401 | 122.3282 | -122.2458 | -122.287
2250.5781 | 122.2092 | -0.10071 | 122.1085 | -0.075912 | 0.0098416 | -0.0080643 | 0.011903 | 0.051823 | -0.012245 | 0.066902 | -0.004578 | 122.0444 | -0.17395 | 0.082397 | 121.4355 | 2.71 | 0.3067 | 0.41199 | 122.2321 | -0.23346 | -0.073242 | -0.064086 | 0.09613 | 0.18311 | -0.67291 | -0.13275 | 0.1236 | 0.16937 | 0.40741 | 0.5127 | 121.5363 | 122.1451 | 0.09613 | 122.3328 | 2.8107 | -0.13275 | 122.1451 | 0.09613 | 2.8107 | 121.5363 | 122.3328 | -122.2824 | -122.3419
2252.2656 | 122.1817 | -0.10986 | 122.1359 | -0.091171 | 0.010055 | -0.0087051 | 0.013612 | 0.050968 | -0.012458 | 0.065193 | -0.027466 | 122.0169 | -0.16479 | 0.07782 | 121.4493 | 2.7512 | 0.33875 | 0.45319 | 122.2504 | -0.21973 | -0.054932 | -0.11902 | 0.082397 | 0.18768 | -0.68664 | -0.10986 | 0.11444 | 0.13733 | 0.44861 | 0.56305 | 121.5591 | 122.1268 | 0.082397 | 122.3602 | 2.861 | -0.10986 | 122.1268 | 0.082397 | 2.861 | 121.5591 | 122.3602 | -122.3007 | -122.3557
2254.0312 | 122.1863 | -0.11444 | 122.0993 | -0.15984 | 0.01091 | -0.0072099 | 0.011476 | 0.049687 | -0.01374 | 0.064766 | -0.022888 | 122.0535 | -0.17395 | 0.068665 | 121.4401 | 2.7695 | 0.41657 | 0.48981 | 122.2458 | -0.21973 | -0.059509 | -0.045776 | 0.091553 | 0.18311 | -0.65918 | -0.10529 | 0.14648 | 0.15106 | 0.53101 | 0.60425 | 121.5546 | 122.168 | 0.091553 | 122.3602 | 2.8839 | -0.10529 | 122.168 | 0.091553 | 2.8839 | 121.5546 | 122.3602 | -122.2733 | -122.319
2255.7812 | 122.287 | -0.091553 | 122.0581 | -0.098801 | 0.010696 | -0.0082779 | 0.005708 | 0.048832 | -0.0092542 | 0.06733 | 0.004578 | 122.0764 | -0.14191 | 0.11902 | 121.5088 | 2.8015 | 0.32501 | 0.6134 | 122.2 | -0.20599 | -0.050354 | 0.018311 | 0.096131 | 0.21057 | -0.54932 | -0.11444 | 0.14191 | 0.14649 | 0.41657 | 0.70496 | 121.6003 | 122.168 | 0.096131 | 122.2916 | 2.8931 | -0.11444 | 122.168 | 0.096131 | 2.8931 | 121.6003 | 122.2916 | -122.2 | -122.2641
2257.4688 | 122.2595 | -0.086975 | 122.0764 | 0.084305 | 0.013046 | -0.0099869 | 0.014253 | 0.049046 | -0.013527 | 0.066475 | -0.050354 | 122.0352 | -0.16937 | 0.009155 | 121.3898 | 2.6276 | 0.27466 | 0.28381 | 122.2412 | -0.23346 | -0.082398 | -0.041199 | 0.036621 | 0.09613 | -0.68664 | -0.14648 | 0.1648 | 0.11902 | 0.36163 | 0.37079 | 121.4767 | 122.1222 | 0.036621 | 122.3282 | 2.7145 | -0.14648 | 122.1222 | 0.036621 | 2.7145 | 121.4767 | 122.3282 | -122.2458 | -122.3099
2259.2344 | 122.2458 | -0.1236 | 122.1222 | -0.19035 | 0.01326 | -0.0082779 | 0.009126 | 0.046696 | -0.01139 | 0.066902 | -0.068665 | 122.0673 | -0.1831 | 0.022888 | 121.4172 | 2.7466 | 0.56763 | 0.54016 | 122.2183 | -0.23804 | -0.059509 | -0.054931 | 0.054931 | 0.14648 | -0.70496 | -0.11444 | 0.096131 | 0.11444 | 0.69122 | 0.66376 | 121.5408 | 122.1909 | 0.054931 | 122.3419 | 2.8702 | -0.11444 | 122.1909 | 0.054931 | 2.8702 | 121.5408 | 122.3419 | -122.3053 | -122.3602
2260.9375 | 122.1817 | -0.1236 | 122.1176 | -0.12169 | 0.01091 | -0.0016557 | 0.012117 | 0.04755 | -0.012672 | 0.06797 | -0.013733 | 122.0535 | -0.17395 | 0.073242 | 121.4447 | 2.7557 | 0.35248 | 0.45776 | 122.2275 | -0.21515 | -0.050354 | -0.064087 | 0.10986 | 0.19684 | -0.67291 | -0.091553 | 0.10986 | 0.16022 | 0.47607 | 0.58136 | 121.5683 | 122.1771 | 0.10986 | 122.3511 | 2.8793 | -0.091553 | 122.1771 | 0.10986 | 2.8793 | 121.5683 | 122.3511 | -122.2916 | -122.3328
2262.6875 | 122.2092 | -0.11444 | 122.1085 | -0.19035 | 0.010482 | -0.0082779 | 0.0076306 | 0.047764 | -0.010536 | 0.065834 | 0.032043 | 122.049 | -0.14648 | 0.10529 | 121.5088 | 2.8336 | 0.44861 | 0.67291 | 122.2137 | -0.21057 | -0.032043 | -0.059509 | 0.14648 | 0.21973 | -0.59967 | -0.09613 | 0.10529 | 0.17853 | 0.56305 | 0.78735 | 121.6232 | 122.1634 | 0.14648 | 122.3282 | 2.948 | -0.09613 | 122.1634 | 0.14648 | 2.948 | 121.6232 | 122.3282 | -122.2549 | -122.319
2264.4375 | 122.1954 | -0.10986 | 122.1222 | -0.14458 | 0.010482 | -0.0076371 | 0.014253 | 0.048832 | -0.01139 | 0.06498 | -0.013733 | 122.0764 | -0.1831 | 0.07782 | 121.4355 | 2.7649 | 0.38452 | 0.48523 | 122.2183 | -0.21515 | -0.073242 | -0.045776 | 0.09613 | 0.18768 | -0.68664 | -0.10529 | 0.096131 | 0.16937 | 0.49438 | 0.59509 | 121.5454 | 122.1863 | 0.09613 | 122.3282 | 2.8748 | -0.10529 | 122.1863 | 0.09613 | 2.8748 | 121.5454 | 122.3282 | -122.3053 | -122.3373
2266.1406 | 122.3236 | -0.073242 | 122.0993 | 0.084305 | 0.010696 | -0.011055 | 0.0072034 | 0.050541 | -0.009895 | 0.067757 | 0.013733 | 122.0306 | -0.12817 | 0.064087 | 121.4539 | 2.6596 | 0.15106 | 0.37537 | 122.1863 | -0.20142 | -0.054932 | -0.068664 | 0.086975 | 0.13733 | -0.64545 | -0.12817 | 0.086975 | 0.14191 | 0.2243 | 0.44861 | 121.5271 | 122.1039 | 0.086975 | 122.2595 | 2.7328 | -0.12817 | 122.1039 | 0.086975 | 2.7328 | 121.5271 | 122.2595 | -122.2275 | -122.3007
2267.8906 | 122.2549 | -0.11444 | 122.1222 | -0.26665 | 0.01091 | -0.011055 | 0.0095532 | 0.049046 | -0.012458 | 0.066475 | -0.013733 | 122.0535 | -0.16022 | 0.082397 | 121.4447 | 2.8061 | 0.53101 | 0.59967 | 122.2458 | -0.21057 | -0.045776 | -0.068664 | 0.10071 | 0.19684 | -0.67749 | -0.09613 | 0.1236 | 0.14648 | 0.64545 | 0.71411 | 121.5591 | 122.168 | 0.10071 | 122.3602 | 2.9205 | -0.09613 | 122.168 | 0.10071 | 2.9205 | 121.5591 | 122.3602 | -122.2824 | -122.3328
2269.6406 | 122.287 | -0.07782 | 122.0627 | 0.15297 | 0.010696 | -0.0044327 | 0.011689 | 0.050968 | -0.009895 | 0.067543 | 0.050354 | 122.0581 | -0.12817 | 0.13275 | 121.5134 | 2.6917 | 0.022888 | 0.37994 | 122.1954 | -0.19226 | -0.050354 | -0.004578 | 0.12817 | 0.21057 | -0.54932 | -0.11444 | 0.13275 | 0.17853 | 0.10071 | 0.45776 | 121.5912 | 122.1359 | 0.12817 | 122.2733 | 2.7695 | -0.11444 | 122.1359 | 0.12817 | 2.7695 | 121.5912 | 122.2733 | -122.1909 | -122.2549
2271.3281 | 122.3007 | -0.082397 | 122.0856 | 0.099564 | 0.0085598 | -0.0082779 | 0.0089124 | 0.049687 | -0.011818 | 0.066902 | 0.032043 | 122.0123 | -0.15564 | 0.10071 | 121.4813 | 2.6871 | 0.073242 | 0.37994 | 122.1863 | -0.19684 | -0.073243 | -0.073242 | 0.11444 | 0.18311 | -0.60425 | -0.11444 | 0.10071 | 0.18768 | 0.15564 | 0.46234 | 121.5637 | 122.0947 | 0.11444 | 122.2687 | 2.7695 | -0.11444 | 122.0947 | 0.11444 | 2.7695 | 121.5637 | 122.2687 | -122.2412 | -122.2824
2273.0781 | 122.2 | -0.12817 | 122.1176 | -0.19035 | 0.0094144 | -0.0067825 | 0.009126 | 0.048405 | -0.012245 | 0.065193 | 0.032043 | 122.0352 | -0.14648 | 0.13275 | 121.5134 | 2.8702 | 0.3891 | 0.68207 | 122.1634 | -0.18768 | -0.01831 | -0.082398 | 0.16022 | 0.26093 | -0.60425 | -0.059509 | 0.045776 | 0.17853 | 0.51727 | 0.81024 | 121.6415 | 122.1634 | 0.16022 | 122.2916 | 2.9984 | -0.059509 | 122.1634 | 0.16022 | 2.9984 | 121.6415 | 122.2916 | -122.2641 | -122.3053
2274.8438 | 122.2504 | -0.11444 | 122.1176 | -0.23613 | 0.010055 | -0.011269 | 0.010835 | 0.049687 | -0.011818 | 0.065193 | 0.004578 | 122.0261 | -0.16022 | 0.09613 | 121.463 | 2.8061 | 0.50812 | 0.63629 | 122.2504 | -0.21973 | -0.045776 | -0.091553 | 0.11902 | 0.21057 | -0.6546 | -0.10529 | 0.13275 | 0.16479 | 0.62256 | 0.75073 | 121.5775 | 122.1405 | 0.11902 | 122.3648 | 2.9205 | -0.10529 | 122.1405 | 0.11902 | 2.9205 | 121.5775 | 122.3648 | -122.2778 | -122.3373
2276.6094 | 122.2 | -0.13733 | 122.1405 | -0.19035 | 0.0098416 | -0.0080643 | 0.011049 | 0.047764 | -0.014167 | 0.06498 | 0.022888 | 122.0215 | -0.15564 | 0.1236 | 121.5179 | 2.8519 | 0.42114 | 0.6958 | 122.1725 | -0.20142 | -0.018311 | -0.11902 | 0.16022 | 0.26093 | -0.62256 | -0.064087 | 0.032043 | 0.17853 | 0.55847 | 0.83313 | 121.6553 | 122.1588 | 0.16022 | 122.3099 | 2.9892 | -0.064087 | 122.1588 | 0.16022 | 2.9892 | 121.6553 | 122.3099 | -122.2961 | -122.3419
2278.375 | 122.2961 | -0.10071 | 122.081 | 0.084305 | 0.010269 | -0.0061417 | 0.012758 | 0.049687 | -0.01075 | 0.067116 | 0.022888 | 122.049 | -0.15564 | 0.11902 | 121.4951 | 2.6962 | 0.013733 | 0.32959 | 122.1909 | -0.1831 | -0.054932 | -0.032044 | 0.1236 | 0.21973 | -0.58594 | -0.082397 | 0.10986 | 0.17853 | 0.11444 | 0.4303 | 121.5958 | 122.1497 | 0.1236 | 122.2916 | 2.7969 | -0.082397 | 122.1497 | 0.1236 | 2.7969 | 121.5958 | 122.2916 | -122.2366 | -122.2641
2280.1406 | 122.2778 | -0.086975 | 122.0718 | 0.25215 | 0.01091 | -0.0076371 | 0.011903 | 0.052464 | -0.010963 | 0.068611 | 0.045776 | 122.0718 | -0.16022 | 0.10986 | 121.5042 | 2.6825 | 0.036621 | 0.33875 | 122.2046 | -0.1831 | -0.073242 | 0 | 0.13275 | 0.19684 | -0.56763 | -0.09613 | 0.13275 | 0.20599 | 0.1236 | 0.42572 | 121.5912 | 122.1588 | 0.13275 | 122.2916 | 2.7695 | -0.09613 | 122.1588 | 0.13275 | 2.7695 | 121.5912 | 122.2916 | -122.2321 | -122.2549
2281.8281 | 122.3328 | -0.073242 | 122.0901 | 0.12245 | 0.011123 | -0.0099869 | 0.012544 | 0.0499 | -0.010536 | 0.066902 | -0.073242 | 122.0627 | -0.18768 | 0.013733 | 121.4035 | 2.5955 | 0.1831 | 0.21515 | 122.2275 | -0.23346 | -0.11444 | -0.027466 | 0 | 0.086975 | -0.68665 | -0.16022 | 0.13733 | 0.11444 | 0.25635 | 0.28839 | 121.4767 | 122.1359 | 0 | 122.3007 | 2.6688 | -0.16022 | 122.1359 | 0 | 2.6688 | 121.4767 | 122.3007 | -122.2778 | -122.3236
2283.5781 | 122.3602 | -0.059509 | 122.0627 | 0.01564 | 0.01091 | -0.0089189 | 0.009126 | 0.050755 | -0.0094678 | 0.065621 | -0.027466 | 122.0673 | -0.1236 | 0.068665 | 121.4722 | 2.7008 | 0.22888 | 0.43488 | 122.2092 | -0.21973 | -0.064087 | 0.004578 | 0.032043 | 0.12817 | -0.59052 | -0.16022 | 0.14648 | 0.09613 | 0.28839 | 0.49438 | 121.5317 | 122.1268 | 0.032043 | 122.2687 | 2.7603 | -0.16022 | 122.1268 | 0.032043 | 2.7603 | 121.5317 | 122.2687 | -122.1863 | -122.2824
2285.3281 | 122.3419 | -0.07782 | 122.081 | 0.11482 | 0.010482 | -0.0076371 | 0.014894 | 0.047978 | -0.010322 | 0.066262 | -0.064087 | 122.0627 | -0.20142 | 0.036621 | 121.4035 | 2.6138 | 0.14191 | 0.24261 | 122.2137 | -0.21973 | -0.1236 | -0.018311 | 0.013733 | 0.11444 | -0.67749 | -0.14191 | 0.13275 | 0.13733 | 0.21973 | 0.32044 | 121.4813 | 122.1405 | 0.013733 | 122.2916 | 2.6917 | -0.14191 | 122.1405 | 0.013733 | 2.6917 | 121.4813 | 122.2916 | -122.2824 | -122.3007
2287.0781 | 122.3419 | -0.10071 | 122.0856 | 0.053787 | 0.010055 | -0.010414 | 0.0093396 | 0.048619 | -0.01075 | 0.066262 | -0.004578 | 122.0306 | -0.14191 | 0.059509 | 121.4539 | 2.6962 | 0.1831 | 0.40283 | 122.1634 | -0.21973 | -0.041199 | -0.054931 | 0.09613 | 0.16022 | -0.63171 | -0.11902 | 0.07782 | 0.13733 | 0.28381 | 0.50354 | 121.5546 | 122.1313 | 0.09613 | 122.2641 | 2.7969 | -0.11902 | 122.1313 | 0.09613 | 2.7969 | 121.5546 | 122.2641 | -122.2275 | -122.3053
2288.8438 | 122.2275 | -0.11444 | 122.113 | -0.19035 | 0.0092008 | -0.0069961 | 0.015321 | 0.048405 | -0.011177 | 0.065621 | -0.07782 | 122.081 | -0.19684 | 0.041199 | 121.4401 | 2.7969 | 0.48065 | 0.51727 | 122.2412 | -0.2243 | -0.082397 | -0.032043 | 0.036621 | 0.15564 | -0.67291 | -0.10986 | 0.12817 | 0.11902 | 0.59509 | 0.63171 | 121.5546 | 122.1954 | 0.036621 | 122.3557 | 2.9114 | -0.10986 | 122.1954 | 0.036621 | 2.9114 | 121.5546 | 122.3557 | -122.3099 | -122.3373
2290.5312 | 122.2275 | -0.10986 | 122.1268 | -0.15984 | 0.010055 | -0.0089189 | 0.011476 | 0.049046 | -0.011177 | 0.067757 | -0.07782 | 122.081 | -0.20142 | 0.022888 | 121.431 | 2.7878 | 0.51727 | 0.53101 | 122.2549 | -0.2243 | -0.091553 | -0.045776 | 0.032043 | 0.13275 | -0.6958 | -0.11444 | 0.12817 | 0.1236 | 0.62714 | 0.64087 | 121.5408 | 122.1909 | 0.032043 | 122.3648 | 2.8976 | -0.11444 | 122.1909 | 0.032043 | 2.8976 | 121.5408 | 122.3648 | -122.3282 | -122.3511
2292.2812 | 122.319 | -0.064087 | 122.081 | -0.0072479 | 0.011337 | -0.0093461 | 0.0063488 | 0.04691 | -0.0077588 | 0.067757 | -0.022888 | 122.0993 | -0.14191 | 0.064087 | 121.4905 | 2.7328 | 0.27466 | 0.49896 | 122.1771 | -0.2243 | -0.07782 | 0.01831 | 0.041199 | 0.12817 | -0.59052 | -0.16022 | 0.09613 | 0.11902 | 0.33875 | 0.56305 | 121.5546 | 122.1634 | 0.041199 | 122.2412 | 2.7969 | -0.16022 | 122.1634 | 0.041199 | 2.7969 | 121.5546 | 122.2412 | -122.2229 | -122.3053
2294.0312 | 122.3145 | -0.086975 | 122.0901 | -0.068283 | 0.010482 | -0.010628 | 0.0089124 | 0.047123 | -0.0079724 | 0.066262 | 0.013733 | 122.049 | -0.15106 | 0.091553 | 121.5088 | 2.8107 | 0.3067 | 0.58136 | 122.1771 | -0.21057 | -0.064087 | -0.041199 | 0.10071 | 0.17853 | -0.58136 | -0.1236 | 0.086975 | 0.16479 | 0.39368 | 0.66834 | 121.5958 | 122.1359 | 0.10071 | 122.2641 | 2.8976 | -0.1236 | 122.1359 | 0.10071 | 2.8976 | 121.5958 | 122.2641 | -122.2412 | -122.3007
2295.7188 | 122.2229 | -0.12817 | 122.1085 | -0.19035 | 0.01091 | -0.0067825 | 0.0099804 | 0.046482 | -0.010536 | 0.065834 | 0.041199 | 122.0627 | -0.13275 | 0.15106 | 121.5363 | 2.8885 | 0.38452 | 0.69122 | 122.1725 | -0.17853 | -0.004577 | -0.045776 | 0.16937 | 0.27924 | -0.5722 | -0.050354 | 0.064087 | 0.17395 | 0.5127 | 0.8194 | 121.6644 | 122.1909 | 0.16937 | 122.3007 | 3.0167 | -0.050354 | 122.1909 | 0.16937 | 3.0167 | 121.6644 | 122.3007 | -122.2412 | -122.287
2297.4688 | 122.2229 | -0.1236 | 122.1039 | -0.091171 | 0.012191 | -0.0076371 | 0.01703 | 0.049687 | -0.01374 | 0.065407 | -0.004578 | 122.0627 | -0.17853 | 0.07782 | 121.4493 | 2.7649 | 0.30212 | 0.41199 | 122.2092 | -0.21515 | -0.054932 | -0.041199 | 0.11902 | 0.20142 | -0.6546 | -0.091553 | 0.10528 | 0.17395 | 0.42572 | 0.53558 | 121.5729 | 122.1863 | 0.11902 | 122.3328 | 2.8885 | -0.091553 | 122.1863 | 0.11902 | 2.8885 | 121.5729 | 122.3328 | -122.2824 | -122.319
2299.2344 | 122.2961 | -0.07782 | 122.1039 | 0.069046 | 0.011764 | -0.0059281 | 0.011903 | 0.049687 | -0.0094678 | 0.068611 | 0.027466 | 122.0718 | -0.15106 | 0.10986 | 121.4996 | 2.7237 | 0.036621 | 0.3479 | 122.1909 | -0.20599 | -0.073242 | -0.032044 | 0.10529 | 0.18768 | -0.60425 | -0.12817 | 0.086975 | 0.17853 | 0.11444 | 0.42572 | 121.5775 | 122.1497 | 0.10529 | 122.2687 | 2.8015 | -0.12817 | 122.1497 | 0.10529 | 2.8015 | 121.5775 | 122.2687 | -122.2549 | -122.3099
2300.9375 | 122.3145 | -0.09613 | 122.081 | 0.053787 | 0.01091 | -0.0074235 | 0.013185 | 0.050328 | -0.011177 | 0.066902 | -0.068665 | 122.081 | -0.18768 | 0.009155 | 121.3989 | 2.6505 | 0.27008 | 0.25177 | 122.2183 | -0.24261 | -0.091553 | 0 | 0.027465 | 0.10528 | -0.68207 | -0.14649 | 0.13733 | 0.11902 | 0.36621 | 0.3479 | 121.4951 | 122.1771 | 0.027465 | 122.3145 | 2.7466 | -0.14649 | 122.1771 | 0.027465 | 2.7466 | 121.4951 | 122.3145 | -122.2687 | -122.3236
2302.6875 | 122.2092 | -0.1236 | 122.1176 | -0.091171 | 0.010482 | -0.0082779 | 0.014039 | 0.050328 | -0.010963 | 0.067757 | -0.018311 | 122.081 | -0.17853 | 0.068665 | 121.4676 | 2.7969 | 0.32959 | 0.44861 | 122.2412 | -0.21515 | -0.054932 | -0.036621 | 0.10528 | 0.19226 | -0.65002 | -0.091553 | 0.1236 | 0.16022 | 0.45319 | 0.5722 | 121.5912 | 122.2046 | 0.10528 | 122.3648 | 2.9205 | -0.091553 | 122.2046 | 0.10528 | 2.9205 | 121.5912 | 122.3648 | -122.2961 | -122.3328
2304.4531 | 122.2092 | -0.13275 | 122.1268 | -0.083542 | 0.010055 | -0.011055 | 0.014039 | 0.052677 | -0.011818 | 0.06733 | 0.004578 | 122.0444 | -0.18768 | 0.073242 | 121.4767 | 2.7878 | 0.31128 | 0.4303 | 122.2458 | -0.23346 | -0.054932 | -0.082397 | 0.13733 | 0.20599 | -0.65002 | -0.10071 | 0.11902 | 0.19226 | 0.44403 | 0.56305 | 121.6095 | 122.1771 | 0.13733 | 122.3785 | 2.9205 | -0.10071 | 122.1771 | 0.13733 | 2.9205 | 121.6095 | 122.3785 | -122.3145 | -122.3602
2306.2031 | 122.2275 | -0.1236 | 122.1313 | -0.068283 | 0.012405 | -0.0074235 | 0.012971 | 0.0499 | -0.013527 | 0.066048 | -0.009155 | 122.0718 | -0.17853 | 0.073242 | 121.463 | 2.774 | 0.3067 | 0.42114 | 122.2504 | -0.21515 | -0.054932 | -0.05951 | 0.11444 | 0.19684 | -0.66833 | -0.091553 | 0.11902 | 0.16937 | 0.4303 | 0.54474 | 121.5866 | 122.1954 | 0.11444 | 122.374 | 2.8976 | -0.091553 | 122.1954 | 0.11444 | 2.8976 | 121.5866 | 122.374 | -122.3099 | -122.3465
2307.9531 | 122.2275 | -0.12817 | 122.1313 | -0.18272 | 0.010269 | -0.0097733 | 0.005708 | 0.050968 | -0.01075 | 0.068184 | 0.027466 | 122.0215 | -0.13733 | 0.09613 | 121.5225 | 2.8976 | 0.45776 | 0.67291 | 122.2046 | -0.21973 | -0.009155 | -0.10986 | 0.15564 | 0.2243 | -0.60883 | -0.091553 | 0.073242 | 0.16479 | 0.58594 | 0.80109 | 121.6507 | 122.1497 | 0.15564 | 122.3328 | 3.0258 | -0.091553 | 122.1497 | 0.15564 | 3.0258 | 121.6507 | 122.3328 | -122.2687 | -122.3511
2309.6406 | 122.2504 | -0.091553 | 122.1268 | -0.15984 | 0.011978 | -0.0082779 | 0.0046398 | 0.050114 | -0.011604 | 0.065193 | 0.032043 | 122.0581 | -0.13733 | 0.13275 | 121.5546 | 2.8702 | 0.32044 | 0.63629 | 122.2092 | -0.21057 | -0.045776 | -0.068665 | 0.1236 | 0.2243 | -0.5722 | -0.11902 | 0.082397 | 0.16937 | 0.41199 | 0.72784 | 121.6461 | 122.1497 | 0.1236 | 122.3007 | 2.9617 | -0.11902 | 122.1497 | 0.1236 | 2.9617 | 121.6461 | 122.3007 | -122.2641 | -122.3373
2311.3906 | 122.3373 | -0.068665 | 122.0718 | 0.030899 | 0.0098416 | -0.0050735 | 0.013826 | 0.051182 | -0.012031 | 0.066048 | -0.07782 | 122.0718 | -0.18768 | -0.022888 | 121.3715 | 2.6459 | 0.24719 | 0.24261 | 122.2641 | -0.21973 | -0.11902 | 0 | -0.009155 | 0.045777 | -0.70038 | -0.15106 | 0.19226 | 0.10986 | 0.31586 | 0.31128 | 121.4401 | 122.1405 | -0.009155 | 122.3328 | 2.7145 | -0.15106 | 122.1405 | -0.009155 | 2.7145 | 121.4401 | 122.3328 | -122.2595 | -122.2916
2313.1406 | 122.2595 | -0.09613 | 122.1313 | -0.27428 | 0.0098416 | -0.011055 | 0.0089124 | 0.047337 | -0.010963 | 0.066902 | -0.068665 | 122.0947 | -0.17853 | 0.018311 | 121.4218 | 2.8061 | 0.5722 | 0.56763 | 122.2275 | -0.25635 | -0.082398 | -0.036621 | 0.027465 | 0.11444 | -0.70953 | -0.16022 | 0.09613 | 0.10986 | 0.66833 | 0.66376 | 121.5179 | 122.1909 | 0.027465 | 122.3236 | 2.9022 | -0.16022 | 122.1909 | 0.027465 | 2.9022 | 121.5179 | 122.3236 | -122.3099 | -122.3877
2314.8438 | 122.2229 | -0.1236 | 122.1268 | -0.19035 | 0.0083462 | -0.0102 | 0.013398 | 0.049473 | -0.012031 | 0.064766 | -0.032043 | 122.0581 | -0.19684 | 0.068665 | 121.4493 | 2.8244 | 0.4303 | 0.50812 | 122.2458 | -0.22888 | -0.073242 | -0.068665 | 0.091553 | 0.19226 | -0.67749 | -0.10529 | 0.11902 | 0.1648 | 0.55389 | 0.63171 | 121.5729 | 122.1817 | 0.091553 | 122.3694 | 2.948 | -0.10529 | 122.1817 | 0.091553 | 2.948 | 121.5729 | 122.3694 | -122.3236 | -122.3557
2316.5938 | 122.3557 | -0.073242 | 122.0718 | 0.01564 | 0.010482 | -0.0069961 | 0.0063488 | 0.050114 | -0.011604 | 0.068184 | -0.009155 | 122.0535 | -0.14648 | 0.068665 | 121.4859 | 2.7237 | 0.21973 | 0.43488 | 122.2046 | -0.21057 | -0.073242 | -0.01831 | 0.064087 | 0.14191 | -0.58594 | -0.13733 | 0.13275 | 0.13733 | 0.29297 | 0.50812 | 121.5591 | 122.1268 | 0.064087 | 122.2778 | 2.7969 | -0.13733 | 122.1268 | 0.064087 | 2.7969 | 121.5591 | 122.2778 | -122.2183 | -122.2824
2318.3438 | 122.2275 | -0.14191 | 122.1313 | -0.19035 | 0.011337 | -0.010628 | 0.0061352 | 0.0499 | -0.01075 | 0.064766 | 0.045776 | 122.0673 | -0.14648 | 0.12817 | 121.5317 | 2.8931 | 0.43488 | 0.68207 | 122.1909 | -0.21057 | -0.004577 | -0.064087 | 0.18768 | 0.27008 | -0.59967 | -0.068664 | 0.059509 | 0.19226 | 0.57678 | 0.82398 | 121.6736 | 122.2092 | 0.18768 | 122.3328 | 3.035 | -0.068664 | 122.2092 | 0.18768 | 3.035 | 121.6736 | 122.3328 | -122.2778 | -122.3419
2320.1094 | 122.2275 | -0.10529 | 122.1176 | -0.045395 | 0.011337 | -0.0093461 | 0.016176 | 0.051609 | -0.013527 | 0.068184 | -0.009155 | 122.0947 | -0.17853 | 0.054932 | 121.4355 | 2.7649 | 0.29297 | 0.37537 | 122.2504 | -0.21973 | -0.073242 | -0.022888 | 0.096131 | 0.16022 | -0.68207 | -0.11444 | 0.13275 | 0.16937 | 0.39825 | 0.48065 | 121.5408 | 122.2 | 0.096131 | 122.3557 | 2.8702 | -0.11444 | 122.2 | 0.096131 | 2.8702 | 121.5408 | 122.3557 | -122.2961 | -122.3373
2321.8125 | 122.2687 | -0.11444 | 122.1176 | -0.23613 | 0.011337 | -0.0084915 | 0.0086988 | 0.050755 | -0.011604 | 0.06498 | -0.091553 | 122.0764 | -0.20142 | 0.018311 | 121.4218 | 2.8107 | 0.58594 | 0.53558 | 122.2687 | -0.23346 | -0.086975 | -0.041199 | 0.022888 | 0.13275 | -0.6958 | -0.11902 | 0.15106 | 0.10986 | 0.70038 | 0.65002 | 121.5363 | 122.1909 | 0.022888 | 122.3831 | 2.9251 | -0.11902 | 122.1909 | 0.022888 | 2.9251 | 121.5363 | 122.3831 | -122.319 | -122.3511
2323.5625 | 122.2275 | -0.11902 | 122.1542 | -0.17509 | 0.011337 | -0.0099869 | 0.0093396 | 0.048832 | -0.010109 | 0.064125 | 0.045776 | 122.0947 | -0.14191 | 0.14191 | 121.5591 | 2.8931 | 0.39825 | 0.70038 | 122.1954 | -0.20142 | -0.022888 | -0.059509 | 0.16479 | 0.26093 | -0.59509 | -0.082397 | 0.041199 | 0.18768 | 0.51727 | 0.8194 | 121.6782 | 122.2137 | 0.16479 | 122.3145 | 3.0121 | -0.082397 | 122.2137 | 0.16479 | 3.0121 | 121.6782 | 122.3145 | -122.2961 | -122.3557
2325.2656 | 122.3557 | -0.068665 | 122.0856 | 0.091934 | 0.011123 | -0.0042191 | 0.01468 | 0.050541 | -0.015022 | 0.066262 | -0.059509 | 122.0856 | -0.18768 | 0.013733 | 121.4035 | 2.655 | 0.21515 | 0.21973 | 122.2321 | -0.23804 | -0.11902 | 0 | 0.009156 | 0.082398 | -0.68207 | -0.16937 | 0.14648 | 0.12817 | 0.28381 | 0.28839 | 121.4722 | 122.1542 | 0.009156 | 122.3007 | 2.7237 | -0.16937 | 122.1542 | 0.009156 | 2.7237 | 121.4722 | 122.3007 | -122.2733 | -122.3236
2327.0156 | 122.2733 | -0.1236 | 122.1405 | -0.21324 | 0.0087734 | -0.0067825 | 0.010621 | 0.050755 | -0.012886 | 0.066689 | -0.064087 | 122.1085 | -0.1831 | 0.018311 | 121.431 | 2.8107 | 0.57678 | 0.54932 | 122.2595 | -0.23804 | -0.059509 | -0.032044 | 0.059509 | 0.14191 | -0.70953 | -0.11444 | 0.11902 | 0.11902 | 0.70038 | 0.67291 | 121.5546 | 122.2321 | 0.059509 | 122.3831 | 2.9343 | -0.11444 | 122.2321 | 0.059509 | 2.9343 | 121.5546 | 122.3831 | -122.3236 | -122.3785
2328.7812 | 122.2275 | -0.12817 | 122.1588 | -0.18272 | 0.0092008 | -0.0102 | 0.0080578 | 0.04691 | -0.010536 | 0.066902 | 0.036621 | 122.0581 | -0.15106 | 0.10529 | 121.5271 | 2.9068 | 0.45319 | 0.66834 | 122.2137 | -0.21057 | -0.022888 | -0.10071 | 0.1648 | 0.23346 | -0.63171 | -0.082397 | 0.054932 | 0.18768 | 0.58136 | 0.79651 | 121.6553 | 122.1863 | 0.1648 | 122.3419 | 3.035 | -0.082397 | 122.1863 | 0.1648 | 3.035 | 121.6553 | 122.3419 | -122.3099 | -122.3694
2330.5312 | 122.2641 | -0.1236 | 122.1451 | -0.13695 | 0.011978 | -0.0087051 | 0.011476 | 0.047764 | -0.011177 | 0.064339 | -0.064087 | 122.1359 | -0.17395 | 0.013733 | 121.431 | 2.829 | 0.5722 | 0.57678 | 122.2504 | -0.23804 | -0.050354 | -0.009156 | 0.059509 | 0.13733 | -0.71411 | -0.11444 | 0.10528 | 0.10986 | 0.6958 | 0.70038 | 121.5546 | 122.2595 | 0.059509 | 122.374 | 2.9526 | -0.11444 | 122.2595 | 0.059509 | 2.9526 | 121.5546 | 122.374 | -122.319 | -122.3831
2332.2812 | 122.3007 | -0.082397 | 122.1085 | 0.15297 | 0.01091 | -0.0052873 | 0.011049 | 0.050541 | -0.010536 | 0.066048 | 0.059509 | 122.0673 | -0.14191 | 0.1236 | 121.5408 | 2.7603 | 0.022888 | 0.37994 | 122.2137 | -0.1831 | -0.05951 | -0.041198 | 0.14191 | 0.20599 | -0.56763 | -0.10071 | 0.10529 | 0.20142 | 0.10528 | 0.46234 | 121.6232 | 122.1497 | 0.14191 | 122.2961 | 2.8427 | -0.10071 | 122.1497 | 0.14191 | 2.8427 | 121.6232 | 122.2961 | -122.2504 | -122.2916
2333.9688 | 122.3053 | -0.064087 | 122.113 | 0.053787 | 0.0094144 | -0.0061417 | 0.012544 | 0.048405 | -0.013954 | 0.066048 | 0.036621 | 122.0627 | -0.14191 | 0.1236 | 121.5179 | 2.7328 | 0.041199 | 0.3479 | 122.1954 | -0.19226 | -0.07782 | -0.050354 | 0.10071 | 0.18768 | -0.59509 | -0.12817 | 0.082398 | 0.17853 | 0.10529 | 0.41199 | 121.582 | 122.1268 | 0.10071 | 122.2595 | 2.7969 | -0.12817 | 122.1268 | 0.10071 | 2.7969 | 121.582 | 122.2595 | -122.2549 | -122.3053
2335.7344 | 122.2458 | -0.12817 | 122.1588 | -0.11406 | 0.011551 | -0.0078507 | 0.007417 | 0.047123 | -0.012031 | 0.065834 | 0.041199 | 122.0901 | -0.14191 | 0.14648 | 121.5683 | 2.9068 | 0.35706 | 0.67291 | 122.1863 | -0.20142 | -0.013733 | -0.068664 | 0.16937 | 0.27466 | -0.59051 | -0.073242 | 0.027466 | 0.18311 | 0.48523 | 0.80109 | 121.6965 | 122.2183 | 0.16937 | 122.3145 | 3.035 | -0.073242 | 122.2183 | 0.16937 | 3.035 | 121.6965 | 122.3145 | -122.3007 | -122.3602
2337.4844 | 122.2961 | -0.09613 | 122.1085 | 0.14534 | 0.009628 | -0.0074235 | 0.011262 | 0.048405 | -0.012458 | 0.065621 | 0.041199 | 122.0627 | -0.14648 | 0.14191 | 121.5179 | 2.7603 | 0.027466 | 0.39368 | 122.1954 | -0.19684 | -0.050354 | -0.045776 | 0.13733 | 0.23804 | -0.59051 | -0.10071 | 0.086976 | 0.18768 | 0.1236 | 0.48981 | 121.6141 | 122.1588 | 0.13733 | 122.2916 | 2.8564 | -0.10071 | 122.1588 | 0.13733 | 2.8564 | 121.6141 | 122.2916 | -122.2549 | -122.3053
2339.2344 | 122.2412 | -0.1236 | 122.1405 | -0.19798 | 0.011764 | -0.0091325 | 0.01468 | 0.047978 | -0.014808 | 0.066048 | -0.036621 | 122.0627 | -0.20142 | 0.068665 | 121.4676 | 2.8336 | 0.44403 | 0.51727 | 122.2549 | -0.22888 | -0.07782 | -0.07782 | 0.086975 | 0.19226 | -0.67291 | -0.10529 | 0.11444 | 0.1648 | 0.56763 | 0.64087 | 121.5912 | 122.1863 | 0.086975 | 122.3785 | 2.9572 | -0.10529 | 122.1863 | 0.086975 | 2.9572 | 121.5912 | 122.3785 | -122.3419 | -122.3694
2340.9375 | 122.2275 | -0.1236 | 122.1222 | -0.19035 | 0.009628 | -0.012337 | 0.0089124 | 0.048619 | -0.0092542 | 0.064339 | 0.041199 | 122.0993 | -0.15106 | 0.1236 | 121.5454 | 2.9297 | 0.41199 | 0.68665 | 122.2229 | -0.20599 | -0.027466 | -0.022888 | 0.16479 | 0.24719 | -0.57678 | -0.082398 | 0.10071 | 0.19226 | 0.53558 | 0.81024 | 121.669 | 122.2229 | 0.16479 | 122.3465 | 3.0533 | -0.082398 | 122.2229 | 0.16479 | 3.0533 | 121.669 | 122.3465 | -122.2733 | -122.3282
2342.6875 | 122.2961 | -0.086975 | 122.1176 | 0.11482 | 0.0098416 | -0.0057145 | 0.008485 | 0.049687 | -0.012458 | 0.064553 | 0.036621 | 122.0581 | -0.14191 | 0.1236 | 121.5225 | 2.7695 | 0.059509 | 0.37994 | 122.2 | -0.21057 | -0.054932 | -0.05951 | 0.1236 | 0.21057 | -0.59509 | -0.1236 | 0.082397 | 0.17853 | 0.14648 | 0.46692 | 121.6095 | 122.1451 | 0.1236 | 122.287 | 2.8564 | -0.1236 | 122.1451 | 0.1236 | 2.8564 | 121.6095 | 122.287 | -122.2595 | -122.3282
2344.4375 | 122.3465 | -0.068665 | 122.081 | 0.11482 | 0.012405 | -0.0078507 | 0.014894 | 0.049046 | -0.012672 | 0.065834 | -0.059509 | 122.113 | -0.19226 | 0.004578 | 121.4218 | 2.6733 | 0.18768 | 0.21515 | 122.2458 | -0.22888 | -0.1236 | 0.032043 | 0.009156 | 0.073243 | -0.65918 | -0.16022 | 0.16479 | 0.13275 | 0.25635 | 0.28381 | 121.4905 | 122.1817 | 0.009156 | 122.3145 | 2.742 | -0.16022 | 122.1817 | 0.009156 | 2.742 | 121.4905 | 122.3145 | -122.2733 | -122.3099
2346.2188 | 122.2733 | -0.1236 | 122.1405 | -0.25902 | 0.010482 | -0.010628 | 0.009126 | 0.048619 | -0.012886 | 0.065193 | -0.009155 | 122.0947 | -0.16022 | 0.091553 | 121.5179 | 2.8885 | 0.51727 | 0.63629 | 122.2366 | -0.2243 | -0.036621 | -0.045776 | 0.11444 | 0.21515 | -0.62256 | -0.10071 | 0.09613 | 0.15106 | 0.64087 | 0.75989 | 121.6415 | 122.2183 | 0.11444 | 122.3602 | 3.0121 | -0.10071 | 122.2183 | 0.11444 | 3.0121 | 121.6415 | 122.3602 | -122.3007 | -122.3648
2347.9062 | 122.2412 | -0.12817 | 122.113 | -0.24376 | 0.010269 | -0.0093461 | 0.0093396 | 0.046055 | -0.011604 | 0.063912 | 0.032043 | 122.0901 | -0.16022 | 0.09613 | 121.5271 | 2.9022 | 0.49896 | 0.6546 | 122.2275 | -0.21515 | -0.032043 | -0.022888 | 0.16022 | 0.2243 | -0.58594 | -0.086975 | 0.11444 | 0.19226 | 0.62714 | 0.78278 | 121.6553 | 122.2183 | 0.16022 | 122.3557 | 3.0304 | -0.086975 | 122.2183 | 0.16022 | 3.0304 | 121.6553 | 122.3557 | -122.2733 | -122.3282
2349.6406 | 122.3602 | -0.054932 | 122.1222 | 0.076676 | 0.012619 | -0.014046 | 0.014039 | 0.050328 | -0.012458 | 0.06797 | -0.059509 | 122.0764 | -0.17853 | 0.027466 | 121.431 | 2.6733 | 0.17853 | 0.25177 | 122.2641 | -0.23346 | -0.1236 | -0.045776 | -0.004577 | 0.082398 | -0.69122 | -0.17853 | 0.14191 | 0.11902 | 0.23346 | 0.3067 | 121.4859 | 122.1313 | -0.004577 | 122.319 | 2.7283 | -0.17853 | 122.1313 | -0.004577 | 2.7283 | 121.4859 | 122.319 | -122.3007 | -122.3557
2351.3906 | 122.2412 | -0.09613 | 122.1359 | -0.060654 | 0.012191 | -0.010414 | 0.016816 | 0.050114 | -0.011818 | 0.067116 | -0.009155 | 122.0901 | -0.1831 | 0.082397 | 121.4676 | 2.7969 | 0.31586 | 0.41657 | 122.2366 | -0.2243 | -0.086975 | -0.045776 | 0.086975 | 0.17853 | -0.66833 | -0.12817 | 0.10071 | 0.17395 | 0.41199 | 0.5127 | 121.5637 | 122.1863 | 0.086975 | 122.3328 | 2.8931 | -0.12817 | 122.1863 | 0.086975 | 2.8931 | 121.5637 | 122.3328 | -122.319 | -122.3602
2353.1406 | 122.3648 | -0.068665 | 122.1176 | -0.0072479 | 0.0077054 | -0.0082779 | 0.0044262 | 0.047337 | -0.012672 | 0.06733 | -0.027466 | 122.1176 | -0.14191 | 0.073242 | 121.4951 | 2.7924 | 0.28839 | 0.49896 | 122.2 | -0.21515 | -0.073242 | 0 | 0.041199 | 0.14191 | -0.62256 | -0.14648 | 0.082397 | 0.11444 | 0.35706 | 0.56763 | 121.5637 | 122.1863 | 0.041199 | 122.2687 | 2.861 | -0.14648 | 122.1863 | 0.041199 | 2.861 | 121.5637 | 122.2687 | -122.2595 | -122.3328
2354.8438 | 122.2321 | -0.1236 | 122.1497 | -0.18272 | 0.0089872 | -0.0065689 | 0.0095532 | 0.046696 | -0.015022 | 0.065193 | 0.022888 | 122.0764 | -0.15564 | 0.13275 | 121.5317 | 2.9388 | 0.43945 | 0.68665 | 122.2275 | -0.19226 | -0.032044 | -0.073242 | 0.14648 | 0.25635 | -0.61798 | -0.068665 | 0.07782 | 0.17853 | 0.56305 | 0.81024 | 121.6553 | 122.2 | 0.14648 | 122.3511 | 3.0624 | -0.068665 | 122.2 | 0.14648 | 3.0624 | 121.6553 | 122.3511 | -122.3053 | -122.3419
2356.5938 | 122.319 | -0.07782 | 122.1176 | 0.14534 | 0.010055 | -0.0097733 | 0.014894 | 0.048832 | -0.011177 | 0.066689 | 0.027466 | 122.0627 | -0.13733 | 0.13733 | 121.5271 | 2.7786 | 0.050354 | 0.39825 | 122.1863 | -0.19226 | -0.059509 | -0.054932 | 0.10529 | 0.21515 | -0.59051 | -0.11444 | 0.068664 | 0.16479 | 0.12817 | 0.47607 | 121.6049 | 122.1405 | 0.10529 | 122.2641 | 2.8564 | -0.11444 | 122.1405 | 0.10529 | 2.8564 | 121.6049 | 122.2641 | -122.2549 | -122.3099
2358.3594 | 122.3236 | -0.082397 | 122.1039 | 0.091934 | 0.010055 | -0.0061417 | 0.010621 | 0.048405 | -0.010536 | 0.067116 | 0.041199 | 122.0993 | -0.12817 | 0.11902 | 121.5179 | 2.7786 | 0.07782 | 0.40741 | 122.2 | -0.20599 | -0.045777 | -0.004578 | 0.1236 | 0.20142 | -0.58594 | -0.1236 | 0.09613 | 0.16937 | 0.16022 | 0.48981 | 121.6003 | 122.1817 | 0.1236 | 122.2824 | 2.861 | -0.1236 | 122.1817 | 0.1236 | 2.861 | 121.6003 | 122.2824 | -122.2321 | -122.3099
2360.125 | 122.3511 | -0.082397 | 122.1039 | 0.10719 | 0.0098416 | -0.0050735 | 0.011049 | 0.047764 | -0.010322 | 0.06797 | 0.013733 | 122.0993 | -0.13733 | 0.09613 | 121.4996 | 2.774 | 0.15106 | 0.41657 | 122.2 | -0.21057 | -0.054932 | -0.004578 | 0.09613 | 0.17853 | -0.60425 | -0.12817 | 0.09613 | 0.15106 | 0.23346 | 0.49896 | 121.582 | 122.1817 | 0.09613 | 122.2824 | 2.8564 | -0.12817 | 122.1817 | 0.09613 | 2.8564 | 121.582 | 122.2824 | -122.2412 | -122.3145
2361.8125 | 122.3648 | -0.073242 | 122.1085 | 0.01564 | 0.013046 | -0.0102 | 0.011049 | 0.046269 | -0.009895 | 0.067116 | -0.009155 | 122.0993 | -0.13275 | 0.07782 | 121.4905 | 2.7603 | 0.22888 | 0.43488 | 122.2183 | -0.19684 | -0.059509 | -0.009155 | 0.064087 | 0.15106 | -0.61798 | -0.1236 | 0.10986 | 0.1236 | 0.30212 | 0.50812 | 121.5637 | 122.1725 | 0.064087 | 122.2916 | 2.8336 | -0.1236 | 122.1725 | 0.064087 | 2.8336 | 121.5637 | 122.2916 | -122.2412 | -122.3053
2363.5625 | 122.2824 | -0.091553 | 122.1634 | -0.24376 | 0.011551 | -0.0089189 | 0.013398 | 0.045628 | -0.012886 | 0.06733 | -0.082397 | 122.0993 | -0.21057 | 0.027466 | 121.431 | 2.8427 | 0.58136 | 0.55389 | 122.2641 | -0.2243 | -0.11902 | -0.064087 | 0.009156 | 0.11902 | -0.73242 | -0.13275 | 0.10071 | 0.12817 | 0.67291 | 0.64545 | 121.5225 | 122.1909 | 0.009156 | 122.3557 | 2.9343 | -0.13275 | 122.1909 | 0.009156 | 2.9343 | 121.5225 | 122.3557 | -122.374 | -122.3877
2365.3281 | 122.3602 | -0.07782 | 122.1176 | 0.00038159 | 0.011337 | -0.0095597 | 0.0078442 | 0.048619 | -0.010963 | 0.066048 | -0.004578 | 122.113 | -0.15106 | 0.073242 | 121.5042 | 2.774 | 0.25177 | 0.45776 | 122.2183 | -0.19684 | -0.073242 | -0.004578 | 0.073242 | 0.15106 | -0.6134 | -0.11902 | 0.10071 | 0.14648 | 0.32959 | 0.53558 | 121.582 | 122.1909 | 0.073242 | 122.2961 | 2.8519 | -0.11902 | 122.1909 | 0.073242 | 2.8519 | 121.582 | 122.2961 | -122.2687 | -122.3145
2367.0781 | 122.3694 | -0.064087 | 122.1039 | 0.0080111 | 0.0083462 | -0.0099869 | 0.010194 | 0.047978 | -0.010536 | 0.063912 | -0.013733 | 122.081 | -0.14191 | 0.07782 | 121.4951 | 2.7969 | 0.28381 | 0.48981 | 122.2183 | -0.19226 | -0.07782 | -0.022888 | 0.050354 | 0.14191 | -0.60883 | -0.12817 | 0.11444 | 0.12817 | 0.3479 | 0.55389 | 121.5591 | 122.1451 | 0.050354 | 122.2824 | 2.861 | -0.12817 | 122.1451 | 0.050354 | 2.861 | 121.5591 | 122.2824 | -122.2458 | -122.2961
2368.7812 | 122.2961 | -0.086975 | 122.1039 | 0.16823 | 0.010269 | -0.0074235 | 0.012758 | 0.049473 | -0.012672 | 0.065407 | 0.059509 | 122.0764 | -0.11902 | 0.13733 | 121.5408 | 2.7878 | 0.032043 | 0.3891 | 122.2412 | -0.1831 | -0.032044 | -0.027466 | 0.14648 | 0.2243 | -0.56305 | -0.09613 | 0.13733 | 0.17853 | 0.11902 | 0.47607 | 121.6278 | 122.1634 | 0.14648 | 122.3282 | 2.8748 | -0.09613 | 122.1634 | 0.14648 | 2.8748 | 121.6278 | 122.3282 | -122.2229 | -122.287
2370.5312 | 122.3465 | -0.045776 | 122.1222 | 0.10719 | 0.011337 | -0.011909 | 0.017244 | 0.0499 | -0.01374 | 0.066689 | -0.050354 | 122.1085 | -0.16937 | 0.032043 | 121.4401 | 2.6779 | 0.18768 | 0.24719 | 122.2504 | -0.21973 | -0.1236 | -0.013733 | -0.004578 | 0.077819 | -0.68207 | -0.17395 | 0.12817 | 0.11902 | 0.23346 | 0.29297 | 121.4859 | 122.1542 | -0.004578 | 122.2961 | 2.7237 | -0.17395 | 122.1542 | -0.004578 | 2.7237 | 121.4859 | 122.2961 | -122.2916 | -122.3419
2372.2188 | 122.2641 | -0.091553 | 122.1268 | 0.01564 | 0.010696 | -0.0102 | 0.016816 | 0.049259 | -0.014167 | 0.065834 | -0.036621 | 122.0901 | -0.19226 | 0.054932 | 121.4264 | 2.7512 | 0.27466 | 0.31128 | 122.2641 | -0.23346 | -0.10071 | -0.036621 | 0.054932 | 0.14649 | -0.70038 | -0.14191 | 0.13733 | 0.15564 | 0.36621 | 0.40283 | 121.5179 | 122.1817 | 0.054932 | 122.3557 | 2.8427 | -0.14191 | 122.1817 | 0.054932 | 2.8427 | 121.5179 | 122.3557 | -122.319 | -122.3602
2373.9688 | 122.2458 | -0.09613 | 122.168 | -0.083542 | 0.01091 | -0.0084915 | 0.015107 | 0.052037 | -0.012886 | 0.06733 | -0.018311 | 122.1085 | -0.17853 | 0.07782 | 121.4813 | 2.8198 | 0.29755 | 0.41199 | 122.2366 | -0.21515 | -0.082398 | -0.05951 | 0.077819 | 0.17395 | -0.68665 | -0.11902 | 0.068664 | 0.16022 | 0.39368 | 0.50812 | 121.5775 | 122.2046 | 0.077819 | 122.3328 | 2.916 | -0.11902 | 122.2046 | 0.077819 | 2.916 | 121.5775 | 122.3328 | -122.3465 | -122.3831
2375.7188 | 122.3465 | -0.059509 | 122.1222 | 0.069046 | 0.010055 | -0.0078507 | 0.013826 | 0.051396 | -0.017158 | 0.065407 | -0.082397 | 122.1039 | -0.20142 | 0.009155 | 121.4081 | 2.7054 | 0.25177 | 0.25177 | 122.287 | -0.20142 | -0.14191 | -0.01831 | -0.022888 | 0.068664 | -0.71411 | -0.14191 | 0.16479 | 0.11902 | 0.31128 | 0.31128 | 121.4676 | 122.1634 | -0.022888 | 122.3465 | 2.7649 | -0.14191 | 122.1634 | -0.022888 | 2.7649 | 121.4676 | 122.3465 | -122.3236 | -122.3236
2377.4688 | 122.2733 | -0.091553 | 122.1497 | -0.15984 | 0.012405 | -0.011482 | 0.0089124 | 0.047764 | -0.010536 | 0.065407 | -0.059509 | 122.1222 | -0.16937 | 0.027466 | 121.4539 | 2.8702 | 0.58594 | 0.5722 | 122.2778 | -0.25635 | -0.07782 | -0.027466 | 0.032044 | 0.11902 | -0.6958 | -0.1648 | 0.12817 | 0.10986 | 0.67749 | 0.66376 | 121.5454 | 122.2137 | 0.032044 | 122.3694 | 2.9617 | -0.1648 | 122.2137 | 0.032044 | 2.9617 | 121.5454 | 122.3694 | -122.319 | -122.406
2379.1562 | 122.3694 | -0.091553 | 122.0856 | 0.030899 | 0.011123 | -0.0080643 | 0.0063488 | 0.050541 | -0.012672 | 0.065407 | 0.004578 | 122.0993 | -0.13275 | 0.064087 | 121.5042 | 2.8152 | 0.23346 | 0.44861 | 122.2549 | -0.19684 | -0.041198 | 0.013733 | 0.096131 | 0.15564 | -0.58136 | -0.10529 | 0.16937 | 0.13733 | 0.32501 | 0.54016 | 121.5958 | 122.1909 | 0.096131 | 122.3465 | 2.9068 | -0.10529 | 122.1909 | 0.096131 | 2.9068 | 121.5958 | 122.3465 | -122.2183 | -122.2824
2380.9219 | 122.3602 | -0.041199 | 122.1039 | 0.13008 | 0.0089872 | -0.0050735 | 0.015962 | 0.050541 | -0.014808 | 0.066048 | -0.050354 | 122.0993 | -0.16937 | 0.018311 | 121.4264 | 2.7054 | 0.21057 | 0.21973 | 122.3007 | -0.21973 | -0.12817 | -0.004578 | -0.009155 | 0.05951 | -0.67749 | -0.17853 | 0.19684 | 0.11902 | 0.25177 | 0.26093 | 121.4676 | 122.1405 | -0.009155 | 122.3419 | 2.7466 | -0.17853 | 122.1405 | -0.009155 | 2.7466 | 121.4676 | 122.3419 | -122.2733 | -122.3236
2382.6094 | 122.3694 | -0.068665 | 122.0993 | 0.13008 | 0.011764 | -0.0040055 | 0.014253 | 0.050541 | -0.012031 | 0.067116 | -0.068665 | 122.1176 | -0.1831 | 0.004578 | 121.4355 | 2.7145 | 0.20599 | 0.22888 | 122.2549 | -0.21515 | -0.11444 | 0.018311 | 0 | 0.073243 | -0.66376 | -0.14648 | 0.15564 | 0.11444 | 0.27466 | 0.29755 | 121.5042 | 122.1863 | 0 | 122.3236 | 2.7832 | -0.14648 | 122.1863 | 0 | 2.7832 | 121.5042 | 122.3236 | -122.2824 | -122.3145
2384.375 | 122.2733 | -0.10529 | 122.1634 | -0.25139 | 0.010055 | -0.010841 | 0.0093396 | 0.049687 | -0.013099 | 0.063912 | -0.073242 | 122.0947 | -0.18768 | 0.027466 | 121.4493 | 2.8748 | 0.59509 | 0.54474 | 122.287 | -0.23346 | -0.082397 | -0.068664 | 0.032044 | 0.13275 | -0.71411 | -0.12817 | 0.1236 | 0.11444 | 0.70038 | 0.65002 | 121.5546 | 122.2 | 0.032044 | 122.3923 | 2.98 | -0.12817 | 122.2 | 0.032044 | 2.98 | 121.5546 | 122.3923 | -122.3511 | -122.3969
2386.0938 | 122.3557 | -0.064087 | 122.1176 | 0.13771 | 0.0087734 | -0.0067825 | 0.013612 | 0.052891 | -0.013527 | 0.067543 | -0.054932 | 122.1405 | -0.16937 | -0.004578 | 121.4355 | 2.7145 | 0.20142 | 0.23346 | 122.2641 | -0.21973 | -0.10529 | 0.022888 | 0.009155 | 0.059509 | -0.68207 | -0.15564 | 0.14648 | 0.11444 | 0.2655 | 0.29755 | 121.4996 | 122.2046 | 0.009155 | 122.3282 | 2.7786 | -0.15564 | 122.2046 | 0.009155 | 2.7786 | 121.4996 | 122.3282 | -122.287 | -122.3373
2387.8438 | 122.2504 | -0.11902 | 122.1542 | -0.19035 | 0.014328 | -0.0084915 | 0.012971 | 0.052037 | -0.013527 | 0.066262 | -0.032043 | 122.1222 | -0.16937 | 0.059509 | 121.4996 | 2.9068 | 0.45319 | 0.52185 | 122.2778 | -0.2243 | -0.050354 | -0.032044 | 0.086976 | 0.17853 | -0.6546 | -0.10529 | 0.1236 | 0.13733 | 0.5722 | 0.64087 | 121.6187 | 122.2412 | 0.086976 | 122.3969 | 3.0258 | -0.10529 | 122.2412 | 0.086976 | 3.0258 | 121.6187 | 122.3969 | -122.3236 | -122.3785
2389.5938 | 122.2458 | -0.12817 | 122.1542 | -0.18272 | 0.0089872 | -0.013191 | 0.0065624 | 0.050968 | -0.010322 | 0.065621 | 0.036621 | 122.1085 | -0.14191 | 0.14191 | 121.5775 | 2.98 | 0.38452 | 0.70953 | 122.2229 | -0.20142 | -0.013733 | -0.045777 | 0.1648 | 0.27008 | -0.57678 | -0.073242 | 0.068664 | 0.17853 | 0.5127 | 0.83771 | 121.7056 | 122.2366 | 0.1648 | 122.3511 | 3.1082 | -0.073242 | 122.2366 | 0.1648 | 3.1082 | 121.7056 | 122.3511 | -122.2961 | -122.3557
2391.2812 | 122.2366 | -0.10071 | 122.1771 | -0.068283 | 0.01091 | -0.0080643 | 0.016603 | 0.049687 | -0.01374 | 0.066262 | -0.013733 | 122.1176 | -0.17853 | 0.073242 | 121.4767 | 2.8519 | 0.32501 | 0.4303 | 122.2733 | -0.21057 | -0.07782 | -0.059509 | 0.086975 | 0.17395 | -0.70038 | -0.10986 | 0.09613 | 0.16479 | 0.42572 | 0.53101 | 121.5775 | 122.2183 | 0.086975 | 122.374 | 2.9526 | -0.10986 | 122.2183 | 0.086975 | 2.9526 | 121.5775 | 122.374 | -122.3557 | -122.3877
2393.0312 | 122.3648 | -0.059509 | 122.1039 | 0.099564 | 0.01091 | -0.0057145 | 0.0086988 | 0.048832 | -0.012886 | 0.068184 | 0.013733 | 122.0947 | -0.12817 | 0.07782 | 121.5088 | 2.7969 | 0.17853 | 0.41657 | 122.2595 | -0.18768 | -0.068665 | -0.009155 | 0.073242 | 0.13733 | -0.59509 | -0.12817 | 0.15564 | 0.14191 | 0.23804 | 0.47607 | 121.5683 | 122.1542 | 0.073242 | 122.319 | 2.8564 | -0.12817 | 122.1542 | 0.073242 | 2.8564 | 121.5683 | 122.319 | -122.2321 | -122.2916
2394.7812 | 122.2961 | -0.07782 | 122.1497 | 0.00038159 | 0.012405 | -0.0046463 | 0.014894 | 0.050328 | -0.01374 | 0.065834 | -0.045776 | 122.1085 | -0.1831 | 0.009155 | 121.4264 | 2.7786 | 0.28839 | 0.28381 | 122.2824 | -0.2243 | -0.10528 | -0.041199 | 0.032044 | 0.086975 | -0.72327 | -0.14648 | 0.13275 | 0.13733 | 0.36621 | 0.36163 | 121.5042 | 122.1863 | 0.032044 | 122.3602 | 2.8564 | -0.14648 | 122.1863 | 0.032044 | 2.8564 | 121.5042 | 122.3602 | -122.3328 | -122.374
2396.4688 | 122.3831 | -0.054932 | 122.1039 | 0.01564 | 0.010269 | -0.0080643 | 0.0076306 | 0.050328 | -0.01139 | 0.066262 | -0.004578 | 122.1176 | -0.13275 | 0.064087 | 121.5088 | 2.8107 | 0.23346 | 0.44403 | 122.2458 | -0.19684 | -0.077819 | 0.013733 | 0.050354 | 0.11902 | -0.59509 | -0.14191 | 0.14191 | 0.12817 | 0.28839 | 0.49896 | 121.5637 | 122.1725 | 0.050354 | 122.3007 | 2.8656 | -0.14191 | 122.1725 | 0.050354 | 2.8656 | 121.5637 | 122.3007 | -122.2366 | -122.3007
2398.2188 | 122.2504 | -0.1236 | 122.1588 | -0.068283 | 0.01091 | -0.011269 | 0.017457 | 0.05225 | -0.016304 | 0.066262 | 0.004578 | 122.0947 | -0.1831 | 0.073242 | 121.4813 | 2.8702 | 0.31128 | 0.43488 | 122.2961 | -0.21973 | -0.059509 | -0.064086 | 0.12817 | 0.19684 | -0.67749 | -0.096131 | 0.13733 | 0.18768 | 0.43487 | 0.55847 | 121.6049 | 122.2183 | 0.12817 | 122.4197 | 2.9938 | -0.096131 | 122.2183 | 0.12817 | 2.9938 | 121.6049 | 122.4197 | -122.3419 | -122.3785
2399.9688 | 122.3831 | -0.059509 | 122.1222 | 0.046158 | 0.011764 | -0.0091325 | 0.0082714 | 0.04691 | -0.01075 | 0.06733 | -0.018311 | 122.1268 | -0.12817 | 0.073242 | 121.5179 | 2.8152 | 0.2243 | 0.4303 | 122.2137 | -0.21973 | -0.068665 | 0.004578 | 0.041198 | 0.13275 | -0.60425 | -0.16022 | 0.091553 | 0.10986 | 0.28381 | 0.48981 | 121.5775 | 122.1863 | 0.041198 | 122.2733 | 2.8748 | -0.16022 | 122.1863 | 0.041198 | 2.8748 | 121.5775 | 122.2733 | -122.2504 | -122.3419
2401.7188 | 122.3282 | -0.068665 | 122.1497 | 0.17586 | 0.009628 | -0.0093461 | 0.012117 | 0.0499 | -0.013099 | 0.066902 | -0.018311 | 122.0993 | -0.16937 | 0.086975 | 121.5179 | 2.8061 | 0.07782 | 0.32959 | 122.2504 | -0.20142 | -0.10071 | -0.050354 | 0.050354 | 0.15564 | -0.63171 | -0.13275 | 0.10071 | 0.15106 | 0.14649 | 0.39826 | 121.5866 | 122.168 | 0.050354 | 122.319 | 2.8748 | -0.13275 | 122.168 | 0.050354 | 2.8748 | 121.5866 | 122.319 | -122.319 | -122.3511
2403.4219 | 122.3465 | -0.068665 | 122.1268 | 0.1606 | 0.010269 | -0.0082779 | 0.010621 | 0.048832 | -0.012672 | 0.066689 | 0.064087 | 122.1222 | -0.12817 | 0.13275 | 121.5546 | 2.8244 | 0.032043 | 0.41657 | 122.2137 | -0.19226 | -0.059509 | -0.004578 | 0.13275 | 0.20142 | -0.5722 | -0.1236 | 0.086975 | 0.19226 | 0.10071 | 0.48523 | 121.6232 | 122.1909 | 0.13275 | 122.2824 | 2.8931 | -0.1236 | 122.1909 | 0.13275 | 2.8931 | 121.6232 | 122.2824 | -122.2549 | -122.319
2405.1719 | 122.2733 | -0.09613 | 122.1405 | 0.01564 | 0.011764 | -0.0067825 | 0.015962 | 0.050755 | -0.012886 | 0.065407 | -0.041199 | 122.1268 | -0.17853 | 0.036621 | 121.4218 | 2.7832 | 0.28839 | 0.32501 | 122.2458 | -0.21057 | -0.082398 | -0.013733 | 0.054931 | 0.13275 | -0.71869 | -0.11444 | 0.10529 | 0.13733 | 0.38452 | 0.42114 | 121.5179 | 122.2229 | 0.054931 | 122.3419 | 2.8793 | -0.11444 | 122.2229 | 0.054931 | 2.8793 | 121.5179 | 122.3419 | -122.319 | -122.3511
2406.875 | 122.3877 | -0.054932 | 122.1268 | 0.038529 | 0.010269 | -0.0082779 | 0.0065624 | 0.048191 | -0.010963 | 0.06733 | -0.013733 | 122.113 | -0.1236 | 0.068665 | 121.4905 | 2.8061 | 0.21973 | 0.43488 | 122.2504 | -0.19684 | -0.068664 | -0.013733 | 0.041199 | 0.1236 | -0.63629 | -0.14191 | 0.1236 | 0.10986 | 0.27466 | 0.48981 | 121.5454 | 122.168 | 0.041199 | 122.3053 | 2.861 | -0.14191 | 122.168 | 0.041199 | 2.861 | 121.5454 | 122.3053 | -122.2504 | -122.3236
2408.625 | 122.3694 | -0.054932 | 122.1405 | 0.12245 | 0.0098416 | -0.0082779 | 0.014253 | 0.052677 | -0.015022 | 0.065193 | -0.064087 | 122.1039 | -0.19226 | 0.018311 | 121.4355 | 2.7374 | 0.20142 | 0.23804 | 122.2824 | -0.2243 | -0.13733 | -0.036621 | -0.009155 | 0.073243 | -0.70496 | -0.16937 | 0.14191 | 0.12817 | 0.25635 | 0.29297 | 121.4905 | 122.1588 | -0.009155 | 122.3373 | 2.7924 | -0.16937 | 122.1588 | -0.009155 | 2.7924 | 121.4905 | 122.3373 | -122.3328 | -122.3648
2410.3125 | 122.2366 | -0.1236 | 122.1588 | -0.18272 | 0.011123 | -0.0097733 | 0.0067762 | 0.048619 | -0.012672 | 0.064553 | 0.032043 | 122.1176 | -0.14191 | 0.13275 | 121.5591 | 2.9892 | 0.45776 | 0.6958 | 122.2458 | -0.21057 | -0.018311 | -0.041198 | 0.15564 | 0.25635 | -0.59967 | -0.086975 | 0.086976 | 0.17395 | 0.58136 | 0.8194 | 121.6827 | 122.2412 | 0.15564 | 122.3694 | 3.1128 | -0.086975 | 122.2412 | 0.15564 | 3.1128 | 121.6827 | 122.3694 | -122.3007 | -122.3694
2412.0156 | 122.3282 | -0.073242 | 122.1313 | 0.15297 | 0.013046 | -0.011909 | 0.012971 | 0.050968 | -0.012245 | 0.066902 | 0.050354 | 122.1588 | -0.14191 | 0.11444 | 121.5454 | 2.8244 | 0.050354 | 0.36163 | 122.2549 | -0.17395 | -0.068665 | 0.027465 | 0.1236 | 0.18768 | -0.58594 | -0.10071 | 0.1236 | 0.19226 | 0.1236 | 0.43488 | 121.6187 | 122.2321 | 0.1236 | 122.3282 | 2.8976 | -0.10071 | 122.2321 | 0.1236 | 2.8976 | 121.6187 | 122.3282 | -122.2733 | -122.3053
2413.7812 | 122.2916 | -0.09613 | 122.1771 | -0.14458 | 0.010055 | -0.0093461 | 0.009126 | 0.048832 | -0.015663 | 0.066902 | -0.041199 | 122.1451 | -0.16937 | 0.045776 | 121.4905 | 2.9068 | 0.5722 | 0.58136 | 122.3053 | -0.2243 | -0.073243 | -0.032043 | 0.054931 | 0.14191 | -0.68665 | -0.12817 | 0.12817 | 0.12817 | 0.66833 | 0.67749 | 121.5866 | 122.2412 | 0.054931 | 122.4014 | 3.0029 | -0.12817 | 122.2412 | 0.054931 | 3.0029 | 121.5866 | 122.4014 | -122.3465 | -122.4014
2415.5625 | 122.3648 | -0.059509 | 122.1542 | 0.13771 | 0.012405 | -0.0052873 | 0.010835 | 0.049473 | -0.012245 | 0.068184 | -0.045776 | 122.1313 | -0.1831 | 0.032043 | 121.4584 | 2.7374 | 0.14648 | 0.26093 | 122.2504 | -0.22888 | -0.1236 | -0.022888 | 0.013733 | 0.091552 | -0.6958 | -0.16937 | 0.09613 | 0.13733 | 0.20599 | 0.32043 | 121.5179 | 122.1909 | 0.013733 | 122.3099 | 2.7969 | -0.16937 | 122.1909 | 0.013733 | 2.7969 | 121.5179 | 122.3099 | -122.3373 | -122.3831
2417.25 | 122.3511 | -0.064087 | 122.1451 | 0.053787 | 0.011978 | -0.0040055 | 0.014467 | 0.050755 | -0.012672 | 0.066475 | -0.07782 | 122.1268 | -0.1831 | 0 | 121.4264 | 2.7512 | 0.28381 | 0.27466 | 122.2595 | -0.23804 | -0.11902 | -0.018311 | -0.013733 | 0.064087 | -0.71869 | -0.17395 | 0.11444 | 0.10528 | 0.3479 | 0.33875 | 121.4905 | 122.1909 | -0.013733 | 122.3236 | 2.8152 | -0.17395 | 122.1909 | -0.013733 | 2.8152 | 121.4905 | 122.3236 | -122.3282 | -122.3831
2419 | 122.2504 | -0.091553 | 122.1588 | -0.19798 | 0.012191 | -0.012337 | 0.012758 | 0.049473 | -0.012458 | 0.068184 | -0.036621 | 122.1268 | -0.16937 | 0.054932 | 121.4951 | 2.9251 | 0.46234 | 0.53101 | 122.287 | -0.22888 | -0.07782 | -0.032043 | 0.054932 | 0.14649 | -0.66376 | -0.13733 | 0.12817 | 0.13275 | 0.55389 | 0.62256 | 121.5866 | 122.2183 | 0.054932 | 122.3785 | 3.0167 | -0.13733 | 122.2183 | 0.054932 | 3.0167 | 121.5866 | 122.3785 | -122.3282 | -122.3877
2420.6875 | 122.3511 | -0.073242 | 122.1222 | 0.046158 | 0.009628 | -0.0033647 | 0.013185 | 0.051396 | -0.013313 | 0.066689 | -0.091553 | 122.1268 | -0.17395 | 0.009155 | 121.431 | 2.774 | 0.27924 | 0.26093 | 122.287 | -0.23804 | -0.10071 | 0.004578 | -0.018311 | 0.082397 | -0.69122 | -0.16479 | 0.16479 | 0.082397 | 0.35248 | 0.33417 | 121.5042 | 122.2 | -0.018311 | 122.3602 | 2.8473 | -0.16479 | 122.2 | -0.018311 | 2.8473 | 121.5042 | 122.3602 | -122.2961 | -122.3602
2422.4219 | 122.287 | -0.086975 | 122.1863 | -0.12932 | 0.010482 | -0.010841 | 0.0050672 | 0.04755 | -0.009895 | 0.065407 | 0.050354 | 122.1497 | -0.14191 | 0.14648 | 121.6003 | 2.98 | 0.33875 | 0.68665 | 122.2275 | -0.17395 | -0.054932 | -0.036621 | 0.13733 | 0.23346 | -0.58594 | -0.086975 | 0.041199 | 0.19226 | 0.42572 | 0.77362 | 121.6873 | 122.2366 | 0.13733 | 122.3145 | 3.067 | -0.086975 | 122.2366 | 0.13733 | 3.067 | 121.6873 | 122.3145 | -122.3282 | -122.3602
2424.1719 | 122.3557 | -0.059509 | 122.1313 | 0.10719 | 0.0085598 | -0.010841 | 0.0080578 | 0.047978 | -0.012886 | 0.067116 | 0.027466 | 122.1085 | -0.14648 | 0.07782 | 121.5317 | 2.8152 | 0.15564 | 0.42572 | 122.2366 | -0.19226 | -0.086975 | -0.022889 | 0.086975 | 0.13733 | -0.59967 | -0.13275 | 0.10528 | 0.17395 | 0.21515 | 0.48523 | 121.5912 | 122.168 | 0.086975 | 122.2961 | 2.8748 | -0.13275 | 122.168 | 0.086975 | 2.8748 | 121.5912 | 122.2961 | -122.2778 | -122.3236
2425.9375 | 122.2733 | -0.09613 | 122.1771 | -0.16747 | 0.011764 | -0.0067825 | 0.012758 | 0.048405 | -0.014808 | 0.064766 | -0.059509 | 122.1222 | -0.19684 | 0.041199 | 121.4859 | 2.9251 | 0.51727 | 0.54474 | 122.2824 | -0.2243 | -0.10071 | -0.054932 | 0.036621 | 0.13733 | -0.69122 | -0.12817 | 0.10529 | 0.13733 | 0.6134 | 0.64087 | 121.582 | 122.2183 | 0.036621 | 122.3785 | 3.0212 | -0.12817 | 122.2183 | 0.036621 | 3.0212 | 121.582 | 122.3785 | -122.374 | -122.4014
2427.6875 | 122.3923 | -0.082397 | 122.1085 | 0.053787 | 0.0068508 | -0.0061417 | 0.0067762 | 0.04691 | -0.010536 | 0.064553 | -0.018311 | 122.0993 | -0.13733 | 0.073242 | 121.5134 | 2.8381 | 0.20599 | 0.43488 | 122.2092 | -0.19684 | -0.054932 | -0.009155 | 0.064086 | 0.15564 | -0.59509 | -0.11444 | 0.10071 | 0.11902 | 0.28839 | 0.51727 | 121.5958 | 122.1817 | 0.064086 | 122.2916 | 2.9205 | -0.11444 | 122.1817 | 0.064086 | 2.9205 | 121.5958 | 122.2916 | -122.2458 | -122.3053
2429.375 | 122.3877 | -0.054932 | 122.1268 | 0.12245 | 0.011123 | -0.0089189 | 0.016603 | 0.0499 | -0.01075 | 0.067116 | -0.050354 | 122.168 | -0.17853 | 0.018311 | 121.4539 | 2.7603 | 0.21057 | 0.24261 | 122.287 | -0.22888 | -0.1236 | 0.041199 | 0.004578 | 0.073243 | -0.67291 | -0.17395 | 0.16022 | 0.12817 | 0.2655 | 0.29755 | 121.5088 | 122.2229 | 0.004578 | 122.3419 | 2.8152 | -0.17395 | 122.2229 | 0.004578 | 2.8152 | 121.5088 | 122.3419 | -122.3053 | -122.3557
2431.1406 | 122.3007 | -0.073242 | 122.1497 | -0.14458 | 0.0092008 | -0.0080643 | 0.0072034 | 0.048405 | -0.010963 | 0.066262 | 0.050354 | 122.1359 | -0.11902 | 0.13275 | 121.582 | 2.9755 | 0.33417 | 0.6546 | 122.2458 | -0.19684 | -0.045777 | -0.013733 | 0.1236 | 0.20599 | -0.56763 | -0.1236 | 0.096131 | 0.16937 | 0.40741 | 0.72784 | 121.6553 | 122.2092 | 0.1236 | 122.319 | 3.0487 | -0.1236 | 122.2092 | 0.1236 | 3.0487 | 121.6553 | 122.319 | -122.2687 | -122.3465
2432.875 | 122.2687 | -0.11444 | 122.1863 | -0.068283 | 0.011551 | -0.0102 | 0.017244 | 0.049046 | -0.013954 | 0.067543 | 0 | 122.1313 | -0.17853 | 0.091553 | 121.4905 | 2.8793 | 0.31128 | 0.4303 | 122.287 | -0.21057 | -0.064087 | -0.054931 | 0.11444 | 0.20599 | -0.6958 | -0.09613 | 0.10071 | 0.17853 | 0.42572 | 0.54474 | 121.6049 | 122.2458 | 0.11444 | 122.4014 | 2.9938 | -0.09613 | 122.2458 | 0.11444 | 2.9938 | 121.6049 | 122.4014 | -122.3648 | -122.3969
2434.625 | 122.2595 | -0.10986 | 122.168 | -0.068283 | 0.011551 | -0.0069961 | 0.011903 | 0.050755 | -0.013954 | 0.067543 | 0.009155 | 122.1222 | -0.16022 | 0.082397 | 121.5042 | 2.8931 | 0.31586 | 0.44861 | 122.2961 | -0.21515 | -0.050354 | -0.045777 | 0.11902 | 0.19226 | -0.66376 | -0.10529 | 0.12817 | 0.16937 | 0.42572 | 0.55847 | 121.6141 | 122.2321 | 0.11902 | 122.406 | 3.0029 | -0.10529 | 122.2321 | 0.11902 | 3.0029 | 121.6141 | 122.406 | -122.3282 | -122.3831
2436.375 | 122.2824 | -0.10529 | 122.1634 | 0.00038159 | 0.012619 | -0.0042191 | 0.013826 | 0.051182 | -0.013099 | 0.065834 | -0.032043 | 122.1176 | -0.16479 | 0.045776 | 121.4859 | 2.8381 | 0.29297 | 0.32959 | 122.2733 | -0.21973 | -0.059509 | -0.045776 | 0.073243 | 0.15106 | -0.67749 | -0.11444 | 0.10986 | 0.13275 | 0.39825 | 0.43488 | 121.5912 | 122.2229 | 0.073243 | 122.3785 | 2.9434 | -0.11444 | 122.2229 | 0.073243 | 2.9434 | 121.5912 | 122.3785 | -122.3282 | -122.3831
2438.125 | 122.2595 | -0.10529 | 122.1634 | -0.15221 | 0.010055 | -0.0089189 | 0.010194 | 0.050541 | -0.0096814 | 0.064339 | -0.018311 | 122.1359 | -0.17853 | 0.059509 | 121.5179 | 2.9434 | 0.43488 | 0.53101 | 122.2687 | -0.21057 | -0.073242 | -0.027466 | 0.086975 | 0.16479 | -0.64545 | -0.10529 | 0.10529 | 0.16022 | 0.54016 | 0.63629 | 121.6232 | 122.2412 | 0.086975 | 122.374 | 3.0487 | -0.10529 | 122.2412 | 0.086975 | 3.0487 | 121.6232 | 122.374 | -122.3419 | -122.374
2439.8125 | 122.3923 | -0.050354 | 122.1497 | 0.13771 | 0.010269 | -0.0063553 | 0.011476 | 0.050755 | -0.013313 | 0.067116 | -0.059509 | 122.1176 | -0.18768 | 0.009155 | 121.4539 | 2.7649 | 0.20599 | 0.24261 | 122.3328 | -0.20599 | -0.13733 | -0.032043 | -0.009155 | 0.059509 | -0.6958 | -0.15564 | 0.18311 | 0.12817 | 0.25635 | 0.29297 | 121.5042 | 122.168 | -0.009155 | 122.3831 | 2.8152 | -0.15564 | 122.168 | -0.009155 | 2.8152 | 121.5042 | 122.3831 | -122.3373 | -122.3557
2441.5781 | 122.3007 | -0.10071 | 122.2046 | -0.16747 | 0.009628 | -0.0095597 | 0.0059216 | 0.047978 | -0.010109 | 0.066689 | 0.036621 | 122.1176 | -0.11444 | 0.14191 | 121.6003 | 3.0121 | 0.33875 | 0.65918 | 122.2183 | -0.19684 | -0.013733 | -0.086975 | 0.13733 | 0.24262 | -0.60425 | -0.09613 | 0.013733 | 0.15106 | 0.43945 | 0.75989 | 121.701 | 122.2183 | 0.13733 | 122.319 | 3.1128 | -0.09613 | 122.2183 | 0.13733 | 3.1128 | 121.701 | 122.319 | -122.319 | -122.4014
2443.2656 | 122.406 | -0.068665 | 122.1313 | 0.00038159 | 0.0089872 | -0.011482 | 0.0061352 | 0.049046 | -0.011177 | 0.065621 | -0.022888 | 122.1268 | -0.12817 | 0.068665 | 121.5225 | 2.8564 | 0.25635 | 0.46692 | 122.2733 | -0.19684 | -0.059509 | -0.004578 | 0.045777 | 0.13733 | -0.60883 | -0.12817 | 0.14191 | 0.10529 | 0.32501 | 0.53558 | 121.5912 | 122.1954 | 0.045777 | 122.3419 | 2.9251 | -0.12817 | 122.1954 | 0.045777 | 2.9251 | 121.5912 | 122.3419 | -122.2595 | -122.3282
2445.0156 | 122.3007 | -0.082397 | 122.1817 | -0.19798 | 0.011551 | -0.014687 | 0.012544 | 0.045628 | -0.013313 | 0.06733 | -0.068665 | 122.1405 | -0.1831 | 0.036621 | 121.463 | 2.9434 | 0.55389 | 0.55389 | 122.287 | -0.23346 | -0.10071 | -0.041199 | 0.013732 | 0.11902 | -0.71869 | -0.15106 | 0.10528 | 0.11444 | 0.63629 | 0.63629 | 121.5454 | 122.2229 | 0.013732 | 122.3694 | 3.0258 | -0.15106 | 122.2229 | 0.013732 | 3.0258 | 121.5454 | 122.3694 | -122.3648 | -122.4152
2446.7812 | 122.3053 | -0.09613 | 122.1634 | -0.045395 | 0.011551 | -0.0102 | 0.015962 | 0.049473 | -0.013313 | 0.06733 | -0.045776 | 122.1497 | -0.17395 | 0.027466 | 121.463 | 2.8198 | 0.28839 | 0.30212 | 122.2824 | -0.21973 | -0.07782 | -0.013733 | 0.050354 | 0.1236 | -0.70038 | -0.1236 | 0.11902 | 0.12817 | 0.38452 | 0.39825 | 121.5591 | 122.2458 | 0.050354 | 122.3785 | 2.916 | -0.1236 | 122.2458 | 0.050354 | 2.916 | 121.5591 | 122.3785 | -122.3373 | -122.3831
2448.4844 | 122.3419 | -0.086975 | 122.1725 | 0.076676 | 0.010482 | -0.010628 | 0.014467 | 0.049046 | -0.012886 | 0.06797 | -0.050354 | 122.1268 | -0.16937 | 0.009155 | 121.4355 | 2.8061 | 0.29297 | 0.29755 | 122.2824 | -0.21973 | -0.082398 | -0.045776 | 0.036621 | 0.09613 | -0.737 | -0.13275 | 0.10986 | 0.11902 | 0.37994 | 0.38452 | 121.5225 | 122.2137 | 0.036621 | 122.3694 | 2.8931 | -0.13275 | 122.2137 | 0.036621 | 2.8931 | 121.5225 | 122.3694 | -122.3419 | -122.3923
2450.2344 | 122.3236 | -0.082397 | 122.1451 | 0.10719 | 0.011123 | -0.0074235 | 0.011049 | 0.050328 | -0.011604 | 0.067543 | 0.045776 | 122.1268 | -0.14648 | 0.1236 | 121.5729 | 2.8793 | 0.050354 | 0.37079 | 122.2412 | -0.1831 | -0.064087 | -0.018311 | 0.12817 | 0.20599 | -0.57221 | -0.10071 | 0.09613 | 0.19226 | 0.13275 | 0.45319 | 121.6553 | 122.2092 | 0.12817 | 122.3236 | 2.9617 | -0.10071 | 122.2092 | 0.12817 | 2.9617 | 121.6553 | 122.3236 | -122.2916 | -122.3282
2451.9844 | 122.3053 | -0.091553 | 122.1771 | 0.01564 | 0.012619 | -0.0087051 | 0.013612 | 0.050968 | -0.013099 | 0.067116 | -0.036621 | 122.1222 | -0.18768 | 0.032043 | 121.463 | 2.8336 | 0.29297 | 0.33875 | 122.2916 | -0.20599 | -0.09613 | -0.054932 | 0.054932 | 0.1236 | -0.71411 | -0.11444 | 0.11444 | 0.15106 | 0.38452 | 0.4303 | 121.5546 | 122.2137 | 0.054932 | 122.3831 | 2.9251 | -0.11444 | 122.2137 | 0.054932 | 2.9251 | 121.5546 | 122.3831 | -122.3648 | -122.3831
2453.7344 | 122.4014 | -0.059509 | 122.1359 | 0.053787 | 0.011337 | -0.0087051 | 0.007417 | 0.048619 | -0.011818 | 0.064125 | -0.013733 | 122.1497 | -0.13733 | 0.073242 | 121.5317 | 2.8702 | 0.2243 | 0.43945 | 122.2366 | -0.19226 | -0.07782 | 0.013733 | 0.045776 | 0.13275 | -0.60425 | -0.13275 | 0.10071 | 0.1236 | 0.28381 | 0.49896 | 121.5912 | 122.2092 | 0.045776 | 122.2961 | 2.9297 | -0.13275 | 122.2092 | 0.045776 | 2.9297 | 121.5912 | 122.2961 | -122.2733 | -122.3282
2455.4219 | 122.3557 | -0.07782 | 122.1359 | 0.17586 | 0.010482 | -0.0046463 | 0.010835 | 0.050114 | -0.012886 | 0.066262 | -0.013733 | 122.1222 | -0.12817 | 0.11444 | 121.5317 | 2.8519 | 0.064087 | 0.34332 | 122.2778 | -0.18768 | -0.050354 | -0.013733 | 0.064087 | 0.19226 | -0.60425 | -0.10986 | 0.14191 | 0.11444 | 0.14191 | 0.42114 | 121.6095 | 122.2 | 0.064087 | 122.3557 | 2.9297 | -0.10986 | 122.2 | 0.064087 | 2.9297 | 121.6095 | 122.3557 | -122.2641 | -122.3236
2457.1875 | 122.2504 | -0.10071 | 122.1863 | -0.083542 | 0.01091 | -0.0080643 | 0.014467 | 0.049473 | -0.012245 | 0.066048 | -0.004578 | 122.1497 | -0.17853 | 0.086975 | 121.5134 | 2.948 | 0.33417 | 0.47607 | 122.2778 | -0.19684 | -0.07782 | -0.036621 | 0.09613 | 0.18768 | -0.67291 | -0.09613 | 0.091553 | 0.17395 | 0.43488 | 0.57678 | 121.6141 | 122.2504 | 0.09613 | 122.3785 | 3.0487 | -0.09613 | 122.2504 | 0.09613 | 3.0487 | 121.6141 | 122.3785 | -122.3648 | -122.3831
2458.9375 | 122.2778 | -0.10986 | 122.2046 | -0.19798 | 0.010055 | -0.014687 | 0.0072034 | 0.048832 | -0.011604 | 0.063912 | 0.059509 | 122.1359 | -0.12817 | 0.13733 | 121.5958 | 3.0396 | 0.41657 | 0.71411 | 122.2504 | -0.19684 | -0.018311 | -0.068665 | 0.16937 | 0.24719 | -0.60883 | -0.086975 | 0.045776 | 0.18768 | 0.52643 | 0.82397 | 121.7056 | 122.2458 | 0.16937 | 122.3602 | 3.1494 | -0.086975 | 122.2458 | 0.16937 | 3.1494 | 121.7056 | 122.3602 | -122.3328 | -122.4014
2460.7031 | 122.2504 | -0.1236 | 122.1542 | -0.18272 | 0.0098416 | -0.012337 | 0.0095532 | 0.048832 | -0.01139 | 0.064125 | 0.045776 | 122.1176 | -0.14648 | 0.14191 | 121.5729 | 3.0533 | 0.43488 | 0.71411 | 122.2778 | -0.20142 | -0.022888 | -0.036621 | 0.16937 | 0.2655 | -0.58136 | -0.07782 | 0.1236 | 0.19226 | 0.55847 | 0.83771 | 121.6965 | 122.2412 | 0.16937 | 122.4014 | 3.1769 | -0.07782 | 122.2412 | 0.16937 | 3.1769 | 121.6965 | 122.4014 | -122.3007 | -122.3557
2462.4219 | 122.2687 | -0.10986 | 122.1863 | -0.16747 | 0.010482 | -0.0102 | 0.0097668 | 0.046696 | -0.011177 | 0.065407 | 0.041199 | 122.1313 | -0.14648 | 0.14191 | 121.55 | 3.035 | 0.45776 | 0.70953 | 122.2595 | -0.19684 | -0.036621 | -0.054931 | 0.15106 | 0.25177 | -0.63629 | -0.086975 | 0.073242 | 0.18768 | 0.56763 | 0.8194 | 121.6599 | 122.2412 | 0.15106 | 122.3694 | 3.1448 | -0.086975 | 122.2412 | 0.15106 | 3.1448 | 121.6599 | 122.3694 | -122.3328 | -122.3831
2464.1719 | 122.406 | -0.054932 | 122.1863 | -0.0072479 | 0.0098416 | -0.012978 | 0.0082714 | 0.047337 | -0.011604 | 0.065834 | -0.013733 | 122.1405 | -0.15564 | 0.073242 | 121.5317 | 2.8793 | 0.2655 | 0.47607 | 122.2504 | -0.21515 | -0.10071 | -0.045776 | 0.041199 | 0.12817 | -0.6546 | -0.16022 | 0.064087 | 0.14191 | 0.32043 | 0.53101 | 121.5866 | 122.1954 | 0.041199 | 122.3053 | 2.9343 | -0.16022 | 122.1954 | 0.041199 | 2.9343 | 121.5866 | 122.3053 | -122.3419 | -122.4014
2465.875 | 122.2458 | -0.10986 | 122.1771 | -0.10643 | 0.011337 | -0.0099869 | 0.015107 | 0.050328 | -0.014167 | 0.066689 | -0.013733 | 122.1039 | -0.17853 | 0.082397 | 121.5088 | 2.948 | 0.37079 | 0.48981 | 122.2412 | -0.21515 | -0.068665 | -0.073242 | 0.09613 | 0.19226 | -0.66834 | -0.10529 | 0.064087 | 0.16479 | 0.48065 | 0.59967 | 121.6187 | 122.2137 | 0.09613 | 122.3511 | 3.0579 | -0.10529 | 122.2137 | 0.09613 | 3.0579 | 121.6187 | 122.3511 | -122.3557 | -122.3923
2467.6406 | 122.2824 | -0.086975 | 122.1909 | -0.022507 | 0.011551 | -0.0025101 | 0.015535 | 0.049259 | -0.012031 | 0.065621 | -0.009155 | 122.1497 | -0.17395 | 0.059509 | 121.4859 | 2.8748 | 0.28381 | 0.37079 | 122.2824 | -0.21973 | -0.086975 | -0.041199 | 0.07782 | 0.14648 | -0.70496 | -0.13275 | 0.091553 | 0.16479 | 0.37079 | 0.45776 | 121.5729 | 122.2366 | 0.07782 | 122.3694 | 2.9617 | -0.13275 | 122.2366 | 0.07782 | 2.9617 | 121.5729 | 122.3694 | -122.3648 | -122.4106
2469.3281 | 122.2458 | -0.10529 | 122.1725 | -0.15221 | 0.012191 | -0.014046 | 0.011049 | 0.048619 | -0.014167 | 0.066262 | -0.027466 | 122.1451 | -0.18768 | 0.068665 | 121.5225 | 2.9617 | 0.44403 | 0.53558 | 122.2778 | -0.22888 | -0.082397 | -0.027465 | 0.07782 | 0.17395 | -0.65002 | -0.1236 | 0.10529 | 0.16022 | 0.54932 | 0.64087 | 121.6278 | 122.2504 | 0.07782 | 122.3831 | 3.067 | -0.1236 | 122.2504 | 0.07782 | 3.067 | 121.6278 | 122.3831 | -122.3602 | -122.4014
2471.0938 | 122.3419 | -0.059509 | 122.1405 | 0.16823 | 0.01091 | -0.0093461 | 0.010835 | 0.051182 | -0.011177 | 0.068398 | 0.064087 | 122.1313 | -0.11444 | 0.13275 | 121.5591 | 2.9022 | 0.018311 | 0.3891 | 122.2687 | -0.17395 | -0.054932 | -0.009155 | 0.1236 | 0.19226 | -0.58136 | -0.11444 | 0.12817 | 0.17853 | 0.07782 | 0.44861 | 121.6187 | 122.1909 | 0.1236 | 122.3282 | 2.9617 | -0.11444 | 122.1909 | 0.1236 | 2.9617 | 121.6187 | 122.3282 | -122.2549 | -122.3145
2472.8594 | 122.2916 | -0.11902 | 122.1863 | -0.12169 | 0.01091 | -0.013618 | 0.0063488 | 0.050114 | -0.010536 | 0.066902 | 0.054932 | 122.1313 | -0.12817 | 0.18768 | 121.6187 | 3.0441 | 0.36163 | 0.69122 | 122.2549 | -0.17395 | -0.009155 | -0.054931 | 0.17395 | 0.3067 | -0.56763 | -0.054931 | 0.068665 | 0.18311 | 0.48065 | 0.81024 | 121.7377 | 122.2504 | 0.17395 | 122.374 | 3.1631 | -0.054931 | 122.2504 | 0.17395 | 3.1631 | 121.7377 | 122.374 | -122.3145 | -122.3602
2474.5469 | 122.2824 | -0.11902 | 122.2046 | -0.053024 | 0.011337 | -0.011055 | 0.018098 | 0.051182 | -0.014381 | 0.065621 | 0 | 122.1222 | -0.17395 | 0.064087 | 121.5042 | 2.9068 | 0.31586 | 0.41199 | 122.3282 | -0.20142 | -0.054931 | -0.082398 | 0.11902 | 0.18311 | -0.70038 | -0.082397 | 0.1236 | 0.17395 | 0.43488 | 0.53101 | 121.6232 | 122.2412 | 0.11902 | 122.4472 | 3.0258 | -0.082397 | 122.2412 | 0.11902 | 3.0258 | 121.6232 | 122.4472 | -122.3785 | -122.406
2476.2969 | 122.2916 | -0.091553 | 122.1725 | -0.14458 | 0.010482 | -0.0063553 | 0.0067762 | 0.050114 | -0.010322 | 0.06263 | 0.059509 | 122.1313 | -0.12817 | 0.15106 | 121.5958 | 3.0212 | 0.33417 | 0.68207 | 122.2641 | -0.20142 | -0.036621 | -0.041198 | 0.15106 | 0.24261 | -0.57678 | -0.10986 | 0.091553 | 0.18768 | 0.42572 | 0.77362 | 121.6873 | 122.2229 | 0.15106 | 122.3557 | 3.1128 | -0.10986 | 122.2229 | 0.15106 | 3.1128 | 121.6873 | 122.3557 | -122.3007 | -122.374
2478.0625 | 122.2641 | -0.1236 | 122.1634 | -0.15984 | 0.010055 | -0.0093461 | 0.0080578 | 0.04755 | -0.013099 | 0.065193 | 0.059509 | 122.1359 | -0.14191 | 0.13733 | 121.6278 | 3.0533 | 0.39368 | 0.71411 | 122.2733 | -0.18768 | -0.018311 | -0.027466 | 0.1831 | 0.26093 | -0.53558 | -0.064087 | 0.10986 | 0.20142 | 0.51727 | 0.83771 | 121.7514 | 122.2595 | 0.1831 | 122.3969 | 3.1769 | -0.064087 | 122.2595 | 0.1831 | 3.1769 | 121.7514 | 122.3969 | -122.3053 | -122.3511
2479.8281 | 122.3511 | -0.07782 | 122.168 | -0.053024 | 0.010269 | -0.0095597 | 0.0095532 | 0.047978 | -0.010322 | 0.066475 | 0.009155 | 122.1359 | -0.13733 | 0.11902 | 121.5591 | 2.98 | 0.32044 | 0.59509 | 122.2778 | -0.19684 | -0.059509 | -0.032044 | 0.086975 | 0.19684 | -0.60883 | -0.11902 | 0.10986 | 0.14648 | 0.39826 | 0.67291 | 121.637 | 122.2137 | 0.086975 | 122.3557 | 3.0579 | -0.11902 | 122.2137 | 0.086975 | 3.0579 | 121.637 | 122.3557 | -122.3053 | -122.3648
2481.5938 | 123.8342 | -0.09613 | 122.1542 | -0.12932 | 0.0094144 | -0.0082779 | 0.0095532 | 0.047337 | -0.011177 | 0.06498 | 0.40741 | 122.1222 | -0.14191 | 0.27924 | 121.8475 | 3.2089 | 0.44403 | 1.0483 | 122.2366 | -0.20142 | -0.045777 | -0.032044 | 0.50354 | 0.37537 | -0.3067 | -0.10529 | 0.082397 | 0.54932 | 0.54016 | 1.1444 | 121.9437 | 122.2183 | 0.50354 | 122.3328 | 3.3051 | -0.10529 | 122.2183 | 0.50354 | 3.3051 | 121.9437 | 122.3328 | -122.2961 | -122.3557
2483.2969 | 122.4976 | -0.091553 | 122.1634 | -0.22087 | 0.0098416 | -0.015541 | 0.01233 | 0.048191 | -0.012031 | 0.064553 | -0.07782 | 122.1176 | -0.17395 | 0.068665 | 121.5912 | 3.0304 | 0.67291 | 0.59967 | 122.319 | -0.21515 | -0.082397 | -0.045776 | 0.013733 | 0.16022 | -0.5722 | -0.1236 | 0.15564 | 0.09613 | 0.76447 | 0.69122 | 121.6827 | 122.2092 | 0.013733 | 122.4106 | 3.1219 | -0.1236 | 122.2092 | 0.013733 | 3.1219 | 121.6827 | 122.4106 | -122.3373 | -122.3785
2485.0469 | 122.5525 | -0.068665 | 122.1588 | 0.19875 | 0.011123 | -0.0084915 | 0.012117 | 0.050328 | -0.012886 | 0.066475 | 0.050354 | 122.1085 | -0.13733 | 0.17395 | 121.8658 | 2.9526 | 0.064087 | 0.31586 | 122.2778 | -0.16022 | -0.068664 | -0.050354 | 0.11902 | 0.24261 | -0.29297 | -0.091552 | 0.11902 | 0.18768 | 0.13275 | 0.38452 | 121.9345 | 122.1771 | 0.11902 | 122.3465 | 3.0212 | -0.091552 | 122.1771 | 0.11902 | 3.0212 | 121.9345 | 122.3465 | -122.2961 | -122.319
2486.8125 | 122.4792 | -0.054932 | 122.1542 | 0.13008 | 0.01091 | -0.0072099 | 0.016389 | 0.0499 | -0.012245 | 0.066475 | 0.11444 | 122.1542 | -0.19684 | 0.15106 | 121.5363 | 2.8198 | 0.25635 | 0.28381 | 122.3007 | -0.22888 | -0.14191 | 0 | 0.16937 | 0.20599 | -0.61798 | -0.17395 | 0.14648 | 0.31128 | 0.31128 | 0.33874 | 121.5912 | 122.2092 | 0.16937 | 122.3557 | 2.8748 | -0.17395 | 122.2092 | 0.16937 | 2.8748 | 121.5912 | 122.3557 | -122.3511 | -122.3831
2488.5 | 122.3557 | -0.09613 | 122.1863 | -0.14458 | 0.011978 | -0.0095597 | 0.0093396 | 0.046696 | -0.010322 | 0.066475 | 0.059509 | 122.1313 | -0.11902 | 0.22888 | 121.756 | 3.1128 | 0.42114 | 0.70953 | 122.2458 | -0.19684 | -0.022889 | -0.054931 | 0.15564 | 0.32501 | -0.4303 | -0.10071 | 0.05951 | 0.17853 | 0.51727 | 0.80566 | 121.8521 | 122.2275 | 0.15564 | 122.3419 | 3.2089 | -0.10071 | 122.2275 | 0.15564 | 3.2089 | 121.8521 | 122.3419 | -122.3053 | -122.3831
2490.25 | 122.4014 | -0.068665 | 122.1634 | 0.046158 | 0.012619 | -0.0059281 | 0.015535 | 0.049046 | -0.012886 | 0.064339 | -0.054932 | 122.1542 | -0.1831 | 0.022888 | 121.4951 | 2.829 | 0.29755 | 0.28381 | 122.3007 | -0.21057 | -0.11444 | -0.009155 | 0.013733 | 0.091553 | -0.66833 | -0.14191 | 0.13733 | 0.12817 | 0.36621 | 0.35248 | 121.5637 | 122.2229 | 0.013733 | 122.3694 | 2.8976 | -0.14191 | 122.2229 | 0.013733 | 2.8976 | 121.5637 | 122.3694 | -122.3465 | -122.374
2492.0156 | 122.3511 | -0.091553 | 122.1497 | 0.1606 | 0.0098416 | -0.0044327 | 0.012971 | 0.049473 | -0.012458 | 0.066048 | 0.059509 | 122.1222 | -0.1236 | 0.16022 | 121.5958 | 2.9297 | 0.045776 | 0.39368 | 122.2504 | -0.19684 | -0.032043 | -0.027466 | 0.15106 | 0.25177 | -0.55389 | -0.10529 | 0.10071 | 0.1831 | 0.13733 | 0.48523 | 121.6873 | 122.2137 | 0.15106 | 122.3419 | 3.0212 | -0.10529 | 122.2137 | 0.15106 | 3.0212 | 121.6873 | 122.3419 | -122.2733 | -122.3465
2493.7031 | 122.374 | -0.07782 | 122.1634 | -0.083542 | 0.0087734 | -0.0082779 | 0.0025036 | 0.046696 | -0.010963 | 0.065621 | 0.004578 | 122.1451 | -0.16479 | 0.1236 | 121.6553 | 3.035 | 0.36163 | 0.64087 | 122.2229 | -0.1831 | -0.086975 | -0.01831 | 0.082398 | 0.20142 | -0.50812 | -0.10528 | 0.059509 | 0.16937 | 0.43945 | 0.71869 | 121.7331 | 122.2229 | 0.082398 | 122.3007 | 3.1128 | -0.10528 | 122.2229 | 0.082398 | 3.1128 | 121.7331 | 122.3007 | -122.3282 | -122.3465
2495.4375 | 122.3923 | -0.09613 | 122.1954 | -0.25139 | 0.0085598 | -0.011482 | 0.011689 | 0.045628 | -0.012245 | 0.068184 | 0.013733 | 122.1542 | -0.15106 | 0.12817 | 121.6461 | 3.0762 | 0.57678 | 0.66834 | 122.2824 | -0.21515 | -0.054932 | -0.041199 | 0.10986 | 0.2243 | -0.54932 | -0.11902 | 0.086975 | 0.16479 | 0.67291 | 0.76446 | 121.7422 | 122.2504 | 0.10986 | 122.3785 | 3.1723 | -0.11902 | 122.2504 | 0.10986 | 3.1723 | 121.7422 | 122.3785 | -122.3465 | -122.4106
2497.1875 | 122.3373 | -0.10529 | 122.2 | -0.17509 | 0.0092008 | -0.012123 | 0.010621 | 0.04691 | -0.010109 | 0.065621 | 0.045776 | 122.1405 | -0.13733 | 0.16022 | 121.6461 | 3.0991 | 0.49439 | 0.71869 | 122.2733 | -0.19684 | -0.032043 | -0.059509 | 0.15106 | 0.2655 | -0.55389 | -0.091552 | 0.073242 | 0.18311 | 0.59967 | 0.82398 | 121.7514 | 122.2458 | 0.15106 | 122.3785 | 3.2043 | -0.091552 | 122.2458 | 0.15106 | 3.2043 | 121.7514 | 122.3785 | -122.3373 | -122.3969
2498.9375 | 122.4518 | -0.050354 | 122.168 | 0.12245 | 0.012832 | -0.0072099 | 0.016816 | 0.051182 | -0.014381 | 0.067116 | -0.054932 | 122.1405 | -0.19226 | 0.054932 | 121.5546 | 2.8748 | 0.26093 | 0.2655 | 122.3282 | -0.2243 | -0.14191 | -0.027466 | -0.004578 | 0.10529 | -0.6134 | -0.17395 | 0.16022 | 0.13733 | 0.31128 | 0.31586 | 121.6049 | 122.1909 | -0.004578 | 122.3785 | 2.9251 | -0.17395 | 122.1909 | -0.004578 | 2.9251 | 121.6049 | 122.3785 | -122.3602 | -122.3923
2500.6406 | 122.319 | -0.10071 | 122.2321 | -0.13695 | 0.011123 | -0.011696 | 0.015748 | 0.0499 | -0.01139 | 0.064339 | 0.013733 | 122.168 | -0.16937 | 0.13275 | 121.637 | 3.0579 | 0.46692 | 0.54016 | 122.3053 | -0.21515 | -0.068665 | -0.064087 | 0.11444 | 0.23346 | -0.59509 | -0.11444 | 0.073242 | 0.18311 | 0.56763 | 0.64087 | 121.7377 | 122.2687 | 0.11444 | 122.406 | 3.1586 | -0.11444 | 122.2687 | 0.11444 | 3.1586 | 121.7377 | 122.406 | -122.4014 | -122.4472
2502.3906 | 122.3465 | -0.11444 | 122.1725 | -0.083542 | 0.011551 | -0.0097733 | 0.015962 | 0.052677 | -0.01139 | 0.06498 | 0.004578 | 122.168 | -0.16937 | 0.13275 | 121.5866 | 2.9984 | 0.35248 | 0.46234 | 122.3053 | -0.2243 | -0.054932 | -0.004577 | 0.11902 | 0.24719 | -0.58594 | -0.10986 | 0.13275 | 0.17395 | 0.46692 | 0.57678 | 121.701 | 122.2824 | 0.11902 | 122.4197 | 3.1128 | -0.10986 | 122.2824 | 0.11902 | 3.1128 | 121.701 | 122.4197 | -122.3419 | -122.3969
2504.1406 | 122.4243 | -0.073242 | 122.1634 | 0.038529 | 0.0083462 | -0.0102 | 0.011476 | 0.049259 | -0.012031 | 0.065834 | -0.059509 | 122.168 | -0.19226 | 0.027466 | 121.5225 | 2.8931 | 0.32501 | 0.3067 | 122.319 | -0.2243 | -0.11902 | 0.004578 | 0.013733 | 0.10071 | -0.64087 | -0.15106 | 0.15564 | 0.13275 | 0.39825 | 0.37994 | 121.5958 | 122.2412 | 0.013733 | 122.3923 | 2.9663 | -0.15106 | 122.2412 | 0.013733 | 2.9663 | 121.5958 | 122.3923 | -122.3557 | -122.3877
2505.8906 | 122.3373 | -0.091553 | 122.1451 | 0.030899 | 0.010696 | -0.0057145 | 0.013398 | 0.052891 | -0.013527 | 0.068825 | -0.027466 | 122.1542 | -0.16022 | 0.073242 | 121.5729 | 2.9572 | 0.33417 | 0.35706 | 122.3282 | -0.21515 | -0.068664 | 0.009155 | 0.064087 | 0.16479 | -0.57221 | -0.1236 | 0.1831 | 0.13275 | 0.42572 | 0.44861 | 121.6644 | 122.2458 | 0.064087 | 122.4197 | 3.0487 | -0.1236 | 122.2458 | 0.064087 | 3.0487 | 121.6644 | 122.4197 | -122.3053 | -122.3602
2507.6406 | 122.4014 | -0.073242 | 122.1451 | 0.099564 | 0.010696 | -0.012123 | 0.005708 | 0.050755 | -0.011818 | 0.066902 | 0.041199 | 122.1405 | -0.1236 | 0.14191 | 121.637 | 2.9617 | 0.15106 | 0.43945 | 122.287 | -0.17395 | -0.050354 | -0.004578 | 0.11444 | 0.21515 | -0.50812 | -0.10071 | 0.14191 | 0.16479 | 0.2243 | 0.5127 | 121.7102 | 122.2137 | 0.11444 | 122.3602 | 3.035 | -0.10071 | 122.2137 | 0.11444 | 3.035 | 121.7102 | 122.3602 | -122.2687 | -122.319
2509.3906 | 122.4289 | -0.064087 | 122.1405 | 0.10719 | 0.011123 | -0.0061417 | 0.0063488 | 0.048405 | -0.012245 | 0.068184 | 0.022888 | 122.1268 | -0.13275 | 0.11902 | 121.6187 | 2.9388 | 0.21515 | 0.42572 | 122.2916 | -0.17853 | -0.068664 | -0.013733 | 0.086975 | 0.18311 | -0.52185 | -0.11444 | 0.15106 | 0.15564 | 0.27924 | 0.48981 | 121.6827 | 122.1909 | 0.086975 | 122.3557 | 3.0029 | -0.11444 | 122.1909 | 0.086975 | 3.0029 | 121.6827 | 122.3557 | -122.2733 | -122.319
2511.0938 | 122.4289 | -0.054932 | 122.1268 | 0.13008 | 0.011337 | -0.011269 | 0.015321 | 0.049259 | -0.012245 | 0.065621 | -0.041199 | 122.1497 | -0.19226 | 0.050354 | 121.5317 | 2.8793 | 0.24719 | 0.24719 | 122.3236 | -0.22888 | -0.13733 | 0.022888 | 0.013733 | 0.10529 | -0.59509 | -0.17395 | 0.19684 | 0.15106 | 0.30212 | 0.30212 | 121.5866 | 122.2046 | 0.013733 | 122.3785 | 2.9343 | -0.17395 | 122.2046 | 0.013733 | 2.9343 | 121.5866 | 122.3785 | -122.319 | -122.3557
2512.8594 | 122.4289 | -0.059509 | 122.1542 | 0.10719 | 0.011551 | -0.0080643 | 0.013826 | 0.049259 | -0.012031 | 0.068825 | -0.027466 | 122.1771 | -0.16022 | 0.068665 | 121.5637 | 2.8748 | 0.21057 | 0.27008 | 122.2961 | -0.21057 | -0.10071 | 0.022888 | 0.032043 | 0.12817 | -0.59051 | -0.15106 | 0.14191 | 0.13275 | 0.27008 | 0.32959 | 121.6232 | 122.2366 | 0.032043 | 122.3557 | 2.9343 | -0.15106 | 122.2366 | 0.032043 | 2.9343 | 121.6232 | 122.3557 | -122.3145 | -122.3648
2514.625 | 122.2778 | -0.10986 | 122.2092 | -0.12932 | 0.011337 | -0.0069961 | 0.01468 | 0.048405 | -0.013527 | 0.068184 | -0.013733 | 122.1497 | -0.17853 | 0.17395 | 121.7468 | 3.1082 | 0.54016 | 0.56763 | 122.3053 | -0.21057 | -0.068665 | -0.059509 | 0.09613 | 0.28381 | -0.46234 | -0.10071 | 0.096131 | 0.16479 | 0.65002 | 0.67749 | 121.8567 | 122.2595 | 0.09613 | 122.4152 | 3.2181 | -0.10071 | 122.2595 | 0.09613 | 3.2181 | 121.8567 | 122.4152 | -122.3877 | -122.4197
2516.3125 | 122.287 | -0.10986 | 122.2046 | -0.12932 | 0.010055 | -0.01255 | 0.0069898 | 0.047337 | -0.01075 | 0.064553 | 0.068665 | 122.1634 | -0.13275 | 0.19226 | 121.7789 | 3.1311 | 0.60425 | 0.75073 | 122.2824 | -0.19684 | -0.022888 | -0.041199 | 0.17853 | 0.30212 | -0.42572 | -0.086975 | 0.07782 | 0.20142 | 0.71411 | 0.86059 | 121.8887 | 122.2733 | 0.17853 | 122.3923 | 3.241 | -0.086975 | 122.2733 | 0.17853 | 3.241 | 121.8887 | 122.3923 | -122.3373 | -122.4014
2518.0625 | 122.319 | -0.082397 | 122.1634 | -0.19798 | 0.0094144 | -0.0069961 | 0.012117 | 0.050114 | -0.014167 | 0.066048 | -0.018311 | 122.1909 | -0.18768 | 0.09613 | 121.7056 | 3.0487 | 0.72784 | 0.61798 | 122.3465 | -0.22888 | -0.10529 | 0.027466 | 0.064086 | 0.17853 | -0.45776 | -0.14649 | 0.18311 | 0.16937 | 0.81024 | 0.70038 | 121.788 | 122.2733 | 0.064086 | 122.4289 | 3.1311 | -0.14649 | 122.2733 | 0.064086 | 3.1311 | 121.788 | 122.4289 | -122.3511 | -122.3923
2519.8125 | 122.3145 | -0.086975 | 122.1863 | -0.19035 | 0.009628 | -0.0091325 | 0.013185 | 0.050755 | -0.014381 | 0.065407 | -0.054932 | 122.1954 | -0.17853 | 0.045776 | 121.4996 | 3.0167 | 0.55847 | 0.56763 | 122.3602 | -0.22888 | -0.091553 | 0.009156 | 0.032043 | 0.13275 | -0.68664 | -0.14191 | 0.17395 | 0.1236 | 0.64545 | 0.6546 | 121.5866 | 122.2824 | 0.032043 | 122.4472 | 3.1036 | -0.14191 | 122.2824 | 0.032043 | 3.1036 | 121.5866 | 122.4472 | -122.3648 | -122.4152
2521.5 | 122.3282 | -0.10529 | 122.1863 | -0.24376 | 0.010055 | -0.0087051 | 0.0067762 | 0.049473 | -0.013099 | 0.065407 | -0.036621 | 122.1725 | -0.17395 | 0.045776 | 121.4951 | 3.0212 | 0.57678 | 0.60883 | 122.3465 | -0.20599 | -0.068664 | -0.013733 | 0.068665 | 0.15106 | -0.69122 | -0.10071 | 0.16022 | 0.13733 | 0.68207 | 0.71411 | 121.6003 | 122.2778 | 0.068665 | 122.4518 | 3.1265 | -0.10071 | 122.2778 | 0.068665 | 3.1265 | 121.6003 | 122.4518 | -122.3602 | -122.3923
2523.2656 | 122.3053 | -0.11902 | 122.1771 | -0.25902 | 0.011551 | -0.0078507 | 0.0095532 | 0.050114 | -0.014381 | 0.06733 | -0.013733 | 122.1497 | -0.14191 | 0.064087 | 121.5363 | 3.0396 | 0.55847 | 0.60425 | 122.3007 | -0.20599 | -0.022888 | -0.027466 | 0.10529 | 0.18311 | -0.64087 | -0.086975 | 0.1236 | 0.12817 | 0.67749 | 0.72327 | 121.6553 | 122.2687 | 0.10529 | 122.4197 | 3.1586 | -0.086975 | 122.2687 | 0.10529 | 3.1586 | 121.6553 | 122.4197 | -122.319 | -122.3831
2525.0312 | 122.3785 | -0.07782 | 122.1542 | 0.099564 | 0.0085598 | -0.0044327 | 0.011476 | 0.049687 | -0.01075 | 0.067543 | 0.041199 | 122.1268 | -0.13733 | 0.10986 | 121.5729 | 2.9388 | 0.09613 | 0.42114 | 122.2733 | -0.1831 | -0.059509 | -0.027466 | 0.11902 | 0.18768 | -0.58136 | -0.10528 | 0.11902 | 0.17853 | 0.17395 | 0.49896 | 121.6507 | 122.2046 | 0.11902 | 122.3511 | 3.0167 | -0.10528 | 122.2046 | 0.11902 | 3.0167 | 121.6507 | 122.3511 | -122.2916 | -122.3373
2526.7812 | 122.3831 | -0.082397 | 122.1542 | 0.11482 | 0.0098416 | -0.013191 | 0.0078442 | 0.049687 | -0.010109 | 0.065834 | 0.041199 | 122.1268 | -0.15564 | 0.10986 | 121.5546 | 2.9297 | 0.14648 | 0.41657 | 122.287 | -0.20599 | -0.073243 | -0.027466 | 0.1236 | 0.19226 | -0.59967 | -0.1236 | 0.13275 | 0.19684 | 0.22888 | 0.49896 | 121.637 | 122.2092 | 0.1236 | 122.3694 | 3.0121 | -0.1236 | 122.2092 | 0.1236 | 3.0121 | 121.637 | 122.3694 | -122.3099 | -122.3602
2528.4844 | 122.3145 | -0.10529 | 122.1863 | -0.24376 | 0.010696 | -0.0093461 | 0.0089124 | 0.04755 | -0.012886 | 0.066902 | -0.059509 | 122.1497 | -0.1831 | 0.032043 | 121.5042 | 3.0029 | 0.58136 | 0.59509 | 122.3145 | -0.21515 | -0.077819 | -0.036621 | 0.045777 | 0.13733 | -0.68207 | -0.10986 | 0.12817 | 0.1236 | 0.68665 | 0.70038 | 121.6095 | 122.2549 | 0.045777 | 122.4197 | 3.1082 | -0.10986 | 122.2549 | 0.045777 | 3.1082 | 121.6095 | 122.4197 | -122.3694 | -122.4014
2530.2344 | 122.3648 | -0.073242 | 122.1725 | 0.1606 | 0.010482 | -0.0093461 | 0.013398 | 0.047764 | -0.013954 | 0.063484 | 0.018311 | 122.1405 | -0.15106 | 0.11902 | 121.5775 | 2.916 | 0.059509 | 0.36621 | 122.2961 | -0.1831 | -0.07782 | -0.032043 | 0.091553 | 0.19226 | -0.59509 | -0.10986 | 0.1236 | 0.16937 | 0.13275 | 0.43945 | 121.6507 | 122.2137 | 0.091553 | 122.3694 | 2.9892 | -0.10986 | 122.2137 | 0.091553 | 2.9892 | 121.6507 | 122.3694 | -122.3236 | -122.3557
2531.9844 | 122.3694 | -0.07782 | 122.1817 | 0.13008 | 0.010055 | -0.01255 | 0.012971 | 0.049046 | -0.011818 | 0.065834 | 0.059509 | 122.1451 | -0.14191 | 0.13275 | 121.5775 | 2.9388 | 0.041199 | 0.37994 | 122.2549 | -0.17853 | -0.064087 | -0.036621 | 0.13733 | 0.21057 | -0.60425 | -0.10071 | 0.073242 | 0.20142 | 0.11902 | 0.45776 | 121.6553 | 122.2229 | 0.13733 | 122.3328 | 3.0167 | -0.10071 | 122.2229 | 0.13733 | 3.0167 | 121.6553 | 122.3328 | -122.3236 | -122.3602
2533.6719 | 122.2733 | -0.10529 | 122.2229 | -0.075912 | 0.0094144 | -0.0074235 | 0.014253 | 0.052464 | -0.012886 | 0.066048 | 0.013733 | 122.1909 | -0.16479 | 0.09613 | 121.5363 | 2.9938 | 0.33875 | 0.48065 | 122.3328 | -0.21515 | -0.059509 | -0.032043 | 0.11902 | 0.20142 | -0.68664 | -0.10986 | 0.10986 | 0.17853 | 0.44403 | 0.58594 | 121.6415 | 122.2961 | 0.11902 | 122.4381 | 3.0991 | -0.10986 | 122.2961 | 0.11902 | 3.0991 | 121.6415 | 122.4381 | -122.3877 | -122.438
2535.4219 | 122.3877 | -0.054932 | 122.1634 | 0.099564 | 0.011978 | -0.0080643 | 0.0061352 | 0.049687 | -0.010322 | 0.067543 | 0.027466 | 122.1542 | -0.12817 | 0.11902 | 121.5729 | 2.9251 | 0.10986 | 0.42572 | 122.2778 | -0.20142 | -0.073242 | -0.009155 | 0.082398 | 0.17395 | -0.59052 | -0.14648 | 0.11444 | 0.15564 | 0.16479 | 0.48065 | 121.6278 | 122.2092 | 0.082398 | 122.3328 | 2.98 | -0.14648 | 122.2092 | 0.082398 | 2.98 | 121.6278 | 122.3328 | -122.2916 | -122.3648
2537.1875 | 122.3236 | -0.091553 | 122.2046 | 0.02327 | 0.010055 | -0.013191 | 0.015748 | 0.049473 | -0.012458 | 0.066262 | -0.036621 | 122.168 | -0.17395 | 0.036621 | 121.4767 | 2.9068 | 0.29297 | 0.33417 | 122.3236 | -0.21515 | -0.082397 | -0.036621 | 0.054932 | 0.12817 | -0.72784 | -0.1236 | 0.11902 | 0.13733 | 0.38452 | 0.42572 | 121.5683 | 122.2595 | 0.054932 | 122.4152 | 2.9984 | -0.1236 | 122.2595 | 0.054932 | 2.9984 | 121.5683 | 122.4152 | -122.3785 | -122.4197
2538.9531 | 122.319 | -0.10986 | 122.1954 | -0.22087 | 0.01091 | -0.0102 | 0.011262 | 0.048832 | -0.012458 | 0.064339 | -0.082397 | 122.1954 | -0.16937 | 0.027466 | 121.4859 | 3.0167 | 0.60425 | 0.59052 | 122.319 | -0.24719 | -0.05951 | 0 | 0.027466 | 0.13733 | -0.70953 | -0.13733 | 0.1236 | 0.086976 | 0.71411 | 0.70038 | 121.5958 | 122.3053 | 0.027466 | 122.4289 | 3.1265 | -0.13733 | 122.3053 | 0.027466 | 3.1265 | 121.5958 | 122.4289 | -122.3648 | -122.4426
2540.7031 | 122.2961 | -0.10071 | 122.2 | -0.18272 | 0.009628 | -0.0074235 | 0.011903 | 0.049473 | -0.011818 | 0.066689 | -0.036621 | 122.1588 | -0.18768 | 0.050354 | 121.5225 | 3.0258 | 0.50812 | 0.55847 | 122.319 | -0.20599 | -0.086975 | -0.041199 | 0.064087 | 0.15106 | -0.67749 | -0.10529 | 0.11902 | 0.15106 | 0.60883 | 0.65918 | 121.6232 | 122.2595 | 0.064087 | 122.4197 | 3.1265 | -0.10529 | 122.2595 | 0.064087 | 3.1265 | 121.6232 | 122.4197 | -122.3877 | -122.406
2542.3906 | 122.3236 | -0.073242 | 122.1817 | 0.02327 | 0.010482 | -0.0065689 | 0.013612 | 0.051396 | -0.013954 | 0.066689 | -0.045776 | 122.1588 | -0.17395 | 0.036621 | 121.4859 | 2.9068 | 0.29755 | 0.32501 | 122.3282 | -0.21515 | -0.10071 | -0.022889 | 0.027466 | 0.10986 | -0.6958 | -0.14191 | 0.14648 | 0.12817 | 0.37079 | 0.39825 | 121.5591 | 122.2321 | 0.027466 | 122.4014 | 2.98 | -0.14191 | 122.2321 | 0.027466 | 2.98 | 121.5591 | 122.4014 | -122.3557 | -122.3969
2544.1406 | 122.3602 | -0.068665 | 122.1634 | 0.1606 | 0.0089872 | -0.012978 | 0.0095532 | 0.048832 | -0.014167 | 0.064553 | 0.032043 | 122.1542 | -0.15564 | 0.11444 | 121.582 | 2.9526 | 0.064087 | 0.36163 | 122.2916 | -0.18768 | -0.086975 | -0.009155 | 0.10071 | 0.18311 | -0.58136 | -0.11902 | 0.12817 | 0.18768 | 0.13275 | 0.4303 | 121.6507 | 122.2229 | 0.10071 | 122.3602 | 3.0212 | -0.11902 | 122.2229 | 0.10071 | 3.0212 | 121.6507 | 122.3602 | -122.319 | -122.3511
2545.8906 | 122.2687 | -0.091553 | 122.2137 | -0.12932 | 0.0094144 | -0.011269 | 0.011476 | 0.049259 | -0.015663 | 0.066902 | -0.018311 | 122.1542 | -0.1831 | 0.068665 | 121.5363 | 3.0441 | 0.44403 | 0.54016 | 122.3282 | -0.20599 | -0.091552 | -0.059509 | 0.073242 | 0.16022 | -0.67749 | -0.11444 | 0.11444 | 0.16479 | 0.53558 | 0.63171 | 121.6278 | 122.2458 | 0.073242 | 122.4197 | 3.1357 | -0.11444 | 122.2458 | 0.073242 | 3.1357 | 121.6278 | 122.4197 | -122.3969 | -122.4197
2547.6406 | 122.3145 | -0.10529 | 122.168 | -0.0072479 | 0.011123 | -0.0095597 | 0.01233 | 0.051823 | -0.013527 | 0.068611 | -0.022888 | 122.1542 | -0.17853 | 0.045776 | 121.4859 | 2.916 | 0.31586 | 0.35248 | 122.3465 | -0.2243 | -0.073242 | -0.013733 | 0.082398 | 0.15106 | -0.68207 | -0.11902 | 0.17853 | 0.15564 | 0.42114 | 0.45776 | 121.5912 | 122.2595 | 0.082398 | 122.4518 | 3.0212 | -0.11902 | 122.2595 | 0.082398 | 3.0212 | 121.5912 | 122.4518 | -122.3465 | -122.3923
2549.3281 | 122.3602 | -0.082397 | 122.1405 | 0.13008 | 0.011551 | -0.0099869 | 0.010835 | 0.049687 | -0.012458 | 0.066902 | 0.045776 | 122.1405 | -0.13733 | 0.1236 | 121.5912 | 2.9572 | 0.054932 | 0.39825 | 122.2778 | -0.16022 | -0.054932 | 0 | 0.12817 | 0.20599 | -0.54932 | -0.07782 | 0.13733 | 0.18311 | 0.13733 | 0.48065 | 121.6736 | 122.2229 | 0.12817 | 122.3602 | 3.0395 | -0.07782 | 122.2229 | 0.12817 | 3.0395 | 121.6736 | 122.3602 | -122.2778 | -122.3007
2551.0938 | 122.3557 | -0.086975 | 122.168 | 0.17586 | 0.011123 | -0.0089189 | 0.010621 | 0.051182 | -0.01139 | 0.067543 | 0.050354 | 122.1405 | -0.12817 | 0.13733 | 121.5866 | 2.9709 | 0.036621 | 0.40283 | 122.2595 | -0.16479 | -0.041199 | -0.027466 | 0.13733 | 0.2243 | -0.58136 | -0.07782 | 0.091552 | 0.17853 | 0.1236 | 0.48981 | 121.6736 | 122.2275 | 0.13733 | 122.3465 | 3.0579 | -0.07782 | 122.2275 | 0.13733 | 3.0579 | 121.6736 | 122.3465 | -122.2961 | -122.3328
2552.7812 | 122.2961 | -0.10071 | 122.2137 | -0.23613 | 0.009628 | -0.014259 | 0.0080578 | 0.046269 | -0.011177 | 0.065407 | 0.032043 | 122.1863 | -0.14648 | 0.10986 | 121.5775 | 3.1128 | 0.53101 | 0.70496 | 122.2733 | -0.21973 | -0.045776 | -0.027466 | 0.13275 | 0.21057 | -0.63629 | -0.11902 | 0.059509 | 0.17853 | 0.63171 | 0.80566 | 121.6782 | 122.287 | 0.13275 | 122.374 | 3.2135 | -0.11902 | 122.287 | 0.13275 | 3.2135 | 121.6782 | 122.374 | -122.3602 | -122.4335
2554.5312 | 122.287 | -0.10071 | 122.1909 | -0.14458 | 0.011123 | -0.0076371 | 0.0065624 | 0.046055 | -0.011177 | 0.067543 | 0.064087 | 122.1725 | -0.14648 | 0.14648 | 121.6187 | 3.1036 | 0.36163 | 0.70496 | 122.3145 | -0.18768 | -0.045776 | -0.018311 | 0.1648 | 0.24719 | -0.5722 | -0.086975 | 0.1236 | 0.21057 | 0.46234 | 0.80566 | 121.7194 | 122.2733 | 0.1648 | 122.4152 | 3.2043 | -0.086975 | 122.2733 | 0.1648 | 3.2043 | 121.7194 | 122.4152 | -122.3373 | -122.3785
2556.2812 | 122.4289 | -0.059509 | 122.1542 | 0.00038159 | 0.0072782 | -0.012764 | 0.009126 | 0.048191 | -0.011818 | 0.066902 | 0.009155 | 122.1588 | -0.14648 | 0.068665 | 121.5454 | 2.9617 | 0.30212 | 0.50354 | 122.319 | -0.20142 | -0.086975 | 0.004577 | 0.068664 | 0.12817 | -0.60883 | -0.14191 | 0.16479 | 0.15564 | 0.36163 | 0.56305 | 121.6049 | 122.2183 | 0.068664 | 122.3785 | 3.0212 | -0.14191 | 122.2183 | 0.068664 | 3.0212 | 121.6049 | 122.3785 | -122.3007 | -122.3557
2558.0312 | 122.3099 | -0.10071 | 122.1817 | -0.25139 | 0.010696 | -0.010628 | 0.011476 | 0.04691 | -0.015236 | 0.065193 | 0.032043 | 122.1634 | -0.15106 | 0.10986 | 121.5591 | 3.0945 | 0.53558 | 0.68665 | 122.2916 | -0.2243 | -0.050354 | -0.018311 | 0.13275 | 0.21057 | -0.62256 | -0.1236 | 0.10986 | 0.18311 | 0.63629 | 0.78735 | 121.6599 | 122.2641 | 0.13275 | 122.3923 | 3.1952 | -0.1236 | 122.2641 | 0.13275 | 3.1952 | 121.6599 | 122.3923 | -122.3328 | -122.406
2559.7188 | 122.3419 | -0.07782 | 122.1725 | 0.0080111 | 0.011764 | -0.0076371 | 0.017244 | 0.051182 | -0.014808 | 0.06498 | -0.027466 | 122.1497 | -0.1831 | 0.054932 | 121.4813 | 2.9205 | 0.3067 | 0.33417 | 122.3511 | -0.20599 | -0.10528 | -0.022888 | 0.050354 | 0.13275 | -0.69122 | -0.12817 | 0.17853 | 0.15564 | 0.38452 | 0.41199 | 121.5591 | 122.2275 | 0.050354 | 122.4289 | 2.9984 | -0.12817 | 122.2275 | 0.050354 | 2.9984 | 121.5591 | 122.4289 | -122.3557 | -122.3785
2561.4688 | 122.2961 | -0.09613 | 122.1954 | -0.15984 | 0.009628 | -0.015114 | 0.007417 | 0.047978 | -0.012672 | 0.065193 | 0.059509 | 122.1405 | -0.15564 | 0.16937 | 121.6187 | 3.1036 | 0.34332 | 0.70496 | 122.3007 | -0.1831 | -0.05951 | -0.054932 | 0.15564 | 0.2655 | -0.57678 | -0.086975 | 0.10528 | 0.21515 | 0.43945 | 0.80109 | 121.7148 | 122.2366 | 0.15564 | 122.3969 | 3.1998 | -0.086975 | 122.2366 | 0.15564 | 3.1998 | 121.7148 | 122.3969 | -122.3511 | -122.3785
2563.2344 | 122.3419 | -0.082397 | 122.1725 | 0.038529 | 0.011337 | -0.010841 | 0.015748 | 0.049687 | -0.014595 | 0.066475 | -0.054932 | 122.168 | -0.18768 | 0.032043 | 121.4813 | 2.9114 | 0.29755 | 0.31586 | 122.3511 | -0.20142 | -0.10529 | -0.004577 | 0.027465 | 0.11444 | -0.69122 | -0.11902 | 0.17853 | 0.13275 | 0.37994 | 0.39825 | 121.5637 | 122.2504 | 0.027465 | 122.4335 | 2.9938 | -0.11902 | 122.2504 | 0.027465 | 2.9938 | 121.5637 | 122.4335 | -122.3602 | -122.374
2564.9844 | 122.2687 | -0.09613 | 122.2229 | -0.10643 | 0.013046 | -0.0102 | 0.015748 | 0.049259 | -0.01374 | 0.06733 | 0.018311 | 122.2092 | -0.16479 | 0.09613 | 121.5454 | 3.0487 | 0.38452 | 0.52643 | 122.287 | -0.21973 | -0.068665 | -0.013733 | 0.11444 | 0.19226 | -0.67749 | -0.1236 | 0.064087 | 0.18311 | 0.48065 | 0.62256 | 121.6415 | 122.3053 | 0.11444 | 122.3831 | 3.1448 | -0.1236 | 122.3053 | 0.11444 | 3.1448 | 121.6415 | 122.3831 | -122.3877 | -122.4426
2566.6719 | 122.319 | -0.082397 | 122.2137 | 0.046158 | 0.0098416 | -0.0099869 | 0.013612 | 0.049259 | -0.01374 | 0.065834 | -0.041199 | 122.1771 | -0.1831 | 0.032043 | 121.4813 | 2.916 | 0.3067 | 0.34332 | 122.3282 | -0.20142 | -0.10071 | -0.036621 | 0.041198 | 0.11444 | -0.73242 | -0.11902 | 0.11444 | 0.14191 | 0.3891 | 0.42572 | 121.5637 | 122.2595 | 0.041198 | 122.4106 | 2.9984 | -0.11902 | 122.2595 | 0.041198 | 2.9984 | 121.5637 | 122.4106 | -122.3969 | -122.4152
2568.4219 | 122.4289 | -0.073242 | 122.1588 | 0.046158 | 0.010055 | -0.011909 | 0.0048534 | 0.049687 | -0.010322 | 0.065621 | 0.004578 | 122.1497 | -0.14191 | 0.091553 | 121.5591 | 2.9526 | 0.22888 | 0.45319 | 122.2961 | -0.1831 | -0.068665 | -0.009155 | 0.07782 | 0.16479 | -0.59967 | -0.10986 | 0.13733 | 0.14649 | 0.30212 | 0.52643 | 121.6324 | 122.2229 | 0.07782 | 122.3694 | 3.0258 | -0.10986 | 122.2229 | 0.07782 | 3.0258 | 121.6324 | 122.3694 | -122.3007 | -122.3419
2570.1719 | 122.3923 | -0.07782 | 122.1817 | 0.099564 | 0.0077054 | -0.0102 | 0.0093396 | 0.049259 | -0.010322 | 0.067757 | 0.050354 | 122.1588 | -0.15106 | 0.12817 | 121.5591 | 2.9709 | 0.10986 | 0.42114 | 122.2916 | -0.19226 | -0.073242 | -0.022889 | 0.12817 | 0.20599 | -0.62256 | -0.11444 | 0.10986 | 0.20142 | 0.18768 | 0.49896 | 121.637 | 122.2366 | 0.12817 | 122.3694 | 3.0487 | -0.11444 | 122.2366 | 0.12817 | 3.0487 | 121.637 | 122.3694 | -122.3328 | -122.374
2571.8594 | 122.3831 | -0.064087 | 122.1909 | -0.075912 | 0.010696 | -0.0074235 | 0.0095532 | 0.047123 | -0.010322 | 0.066689 | 0.027466 | 122.2 | -0.15106 | 0.12817 | 121.6141 | 3.067 | 0.3479 | 0.62256 | 122.2641 | -0.20599 | -0.086975 | 0.009155 | 0.091553 | 0.19226 | -0.57678 | -0.14191 | 0.073242 | 0.17853 | 0.41199 | 0.68665 | 121.6782 | 122.2641 | 0.091553 | 122.3282 | 3.1311 | -0.14191 | 122.2641 | 0.091553 | 3.1311 | 121.6782 | 122.3282 | -122.3419 | -122.3969
2573.625 | 122.2687 | -0.10529 | 122.2046 | -0.083542 | 0.010482 | -0.011269 | 0.017244 | 0.048832 | -0.01374 | 0.065407 | 0.018311 | 122.1497 | -0.16479 | 0.10071 | 121.5454 | 3.0167 | 0.33875 | 0.46234 | 122.287 | -0.20599 | -0.059509 | -0.054932 | 0.1236 | 0.20599 | -0.65918 | -0.10071 | 0.082397 | 0.18311 | 0.44403 | 0.56763 | 121.6507 | 122.2549 | 0.1236 | 122.3923 | 3.1219 | -0.10071 | 122.2549 | 0.1236 | 3.1219 | 121.6507 | 122.3923 | -122.3694 | -122.4106
2575.3906 | 122.2641 | -0.10071 | 122.1909 | -0.14458 | 0.010482 | -0.014473 | 0.013612 | 0.047978 | -0.011604 | 0.067116 | -0.018311 | 122.1863 | -0.17395 | 0.091553 | 121.5454 | 3.0579 | 0.43488 | 0.54474 | 122.2916 | -0.23346 | -0.073242 | -0.004578 | 0.082397 | 0.19226 | -0.64545 | -0.13275 | 0.10071 | 0.15564 | 0.53558 | 0.64545 | 121.6461 | 122.287 | 0.082397 | 122.3923 | 3.1586 | -0.13275 | 122.287 | 0.082397 | 3.1586 | 121.6461 | 122.3923 | -122.3648 | -122.4243
2577.1406 | 122.287 | -0.09613 | 122.1909 | -0.20561 | 0.010482 | -0.011055 | 0.0063488 | 0.046482 | -0.011818 | 0.066262 | 0.050354 | 122.1954 | -0.14191 | 0.15564 | 121.6324 | 3.1494 | 0.42114 | 0.72327 | 122.2549 | -0.19684 | -0.045777 | 0.004578 | 0.14648 | 0.25177 | -0.55847 | -0.10071 | 0.064087 | 0.19226 | 0.51727 | 0.8194 | 121.7285 | 122.2916 | 0.14648 | 122.3511 | 3.2455 | -0.10071 | 122.2916 | 0.14648 | 3.2455 | 121.7285 | 122.3511 | -122.3328 | -122.3877
2578.8594 | 122.4197 | -0.068665 | 122.1954 | -0.0072479 | 0.01091 | -0.0055009 | 0.0072034 | 0.046269 | -0.011818 | 0.066689 | -0.018311 | 122.1725 | -0.14648 | 0.068665 | 121.5591 | 2.9984 | 0.32044 | 0.50812 | 122.3007 | -0.2243 | -0.077819 | -0.022889 | 0.050354 | 0.13733 | -0.63629 | -0.15564 | 0.10528 | 0.12817 | 0.3891 | 0.57678 | 121.6278 | 122.2412 | 0.050354 | 122.3694 | 3.067 | -0.15564 | 122.2412 | 0.050354 | 3.067 | 121.6278 | 122.3694 | -122.3419 | -122.4197
2580.625 | 122.2916 | -0.10529 | 122.2275 | -0.060654 | 0.0098416 | -0.0025101 | 0.015107 | 0.049687 | -0.012672 | 0.065621 | 0.013733 | 122.1634 | -0.16479 | 0.091553 | 121.5317 | 3.0029 | 0.33417 | 0.44861 | 122.3511 | -0.2243 | -0.059509 | -0.064087 | 0.11902 | 0.19684 | -0.6958 | -0.11902 | 0.1236 | 0.17853 | 0.43945 | 0.55389 | 121.637 | 122.2687 | 0.11902 | 122.4564 | 3.1082 | -0.11902 | 122.2687 | 0.11902 | 3.1082 | 121.637 | 122.4564 | -122.3923 | -122.4518
2582.3125 | 122.287 | -0.091553 | 122.2137 | -0.045395 | 0.012832 | -0.0072099 | 0.016176 | 0.050968 | -0.014595 | 0.066262 | -0.004578 | 122.1954 | -0.17853 | 0.064087 | 121.5271 | 2.9892 | 0.32044 | 0.42572 | 122.3419 | -0.23346 | -0.086975 | -0.01831 | 0.086975 | 0.15564 | -0.68664 | -0.14191 | 0.12817 | 0.17395 | 0.41199 | 0.51727 | 121.6187 | 122.287 | 0.086975 | 122.4335 | 3.0808 | -0.14191 | 122.287 | 0.086975 | 3.0808 | 121.6187 | 122.4335 | -122.3923 | -122.4472
2584.0781 | 122.2961 | -0.11444 | 122.2229 | -0.2285 | 0.0085598 | -0.0099869 | 0.0093396 | 0.0499 | -0.013099 | 0.068611 | 0.036621 | 122.1817 | -0.13275 | 0.11444 | 121.5958 | 3.1174 | 0.52643 | 0.6958 | 122.3282 | -0.20599 | -0.01831 | -0.041198 | 0.15106 | 0.22888 | -0.62714 | -0.091553 | 0.10529 | 0.16937 | 0.64087 | 0.81024 | 121.7102 | 122.2961 | 0.15106 | 122.4426 | 3.2318 | -0.091553 | 122.2961 | 0.15106 | 3.2318 | 121.7102 | 122.4426 | -122.3557 | -122.4289
2585.8281 | 122.3282 | -0.09613 | 122.1863 | 0.01564 | 0.0098416 | -0.011055 | 0.014894 | 0.051396 | -0.013954 | 0.065834 | -0.032043 | 122.1634 | -0.16937 | 0.050354 | 121.4996 | 2.9526 | 0.29297 | 0.34332 | 122.3465 | -0.20599 | -0.073243 | -0.022888 | 0.064087 | 0.14648 | -0.68664 | -0.10986 | 0.16022 | 0.13733 | 0.3891 | 0.43945 | 121.5958 | 122.2595 | 0.064087 | 122.4426 | 3.0487 | -0.10986 | 122.2595 | 0.064087 | 3.0487 | 121.5958 | 122.4426 | -122.3557 | -122.3923
2587.5156 | 122.3648 | -0.086975 | 122.1771 | 0.069046 | 0.010269 | -0.0059281 | 0.013185 | 0.053532 | -0.015022 | 0.066262 | -0.050354 | 122.168 | -0.16937 | 0.027466 | 121.4951 | 2.916 | 0.31586 | 0.3067 | 122.3465 | -0.21973 | -0.082398 | -0.009155 | 0.036621 | 0.11444 | -0.68207 | -0.13275 | 0.16937 | 0.11902 | 0.40283 | 0.39368 | 121.582 | 122.2549 | 0.036621 | 122.4335 | 3.0029 | -0.13275 | 122.2549 | 0.036621 | 3.0029 | 121.582 | 122.4335 | -122.3465 | -122.3969
2589.2656 | 122.3877 | -0.068665 | 122.1771 | 0.099564 | 0.0094144 | -0.0072099 | 0.010621 | 0.048832 | -0.0096814 | 0.067116 | 0.041199 | 122.1176 | -0.1236 | 0.11902 | 121.582 | 2.98 | 0.11444 | 0.43945 | 122.2504 | -0.18768 | -0.054931 | -0.059509 | 0.10986 | 0.18768 | -0.59509 | -0.11902 | 0.073242 | 0.16479 | 0.18311 | 0.50812 | 121.6507 | 122.1863 | 0.10986 | 122.319 | 3.0487 | -0.11902 | 122.1863 | 0.10986 | 3.0487 | 121.6507 | 122.319 | -122.3007 | -122.3648
2591.0156 | 122.4289 | -0.054932 | 122.1634 | 0.046158 | 0.0089872 | -0.011482 | 0.0082714 | 0.045841 | -0.010109 | 0.066262 | -0.004578 | 122.168 | -0.16479 | 0.07782 | 121.5729 | 2.9572 | 0.22888 | 0.46692 | 122.2824 | -0.19226 | -0.10986 | 0.004578 | 0.050354 | 0.13275 | -0.59052 | -0.13733 | 0.11902 | 0.16022 | 0.28381 | 0.52185 | 121.6278 | 122.2229 | 0.050354 | 122.3373 | 3.0121 | -0.13733 | 122.2229 | 0.050354 | 3.0121 | 121.6278 | 122.3373 | -122.3282 | -122.3557
2592.7031 | 122.3465 | -0.086975 | 122.1817 | -0.28191 | 0.0089872 | -0.0093461 | 0.0076306 | 0.04755 | -0.013527 | 0.065193 | 0.041199 | 122.1817 | -0.13275 | 0.15106 | 121.6187 | 3.1174 | 0.3479 | 0.67291 | 122.3007 | -0.19226 | -0.045776 | 0 | 0.12817 | 0.23804 | -0.56305 | -0.10529 | 0.11902 | 0.17395 | 0.43488 | 0.75989 | 121.7056 | 122.2687 | 0.12817 | 122.3877 | 3.2043 | -0.10529 | 122.2687 | 0.12817 | 3.2043 | 121.7056 | 122.3877 | -122.3145 | -122.374
2594.4688 | 122.3831 | -0.073242 | 122.1771 | 0.17586 | 0.011978 | -0.0097733 | 0.013185 | 0.048832 | -0.01139 | 0.066262 | -0.004578 | 122.1909 | -0.15106 | 0.10986 | 121.5637 | 2.9617 | 0.091553 | 0.36163 | 122.2824 | -0.1831 | -0.07782 | 0.013733 | 0.068664 | 0.18311 | -0.6134 | -0.10986 | 0.10529 | 0.14648 | 0.16479 | 0.43488 | 121.637 | 122.2641 | 0.068664 | 122.3557 | 3.035 | -0.10986 | 122.2641 | 0.068664 | 3.035 | 121.637 | 122.3557 | -122.3282 | -122.3602
2596.1562 | 122.4014 | -0.032043 | 122.1863 | 0.10719 | 0.010482 | -0.0067825 | 0.014467 | 0.050755 | -0.012886 | 0.06733 | -0.050354 | 122.2046 | -0.18768 | 0.064087 | 121.5042 | 2.9068 | 0.15564 | 0.30212 | 122.3007 | -0.21515 | -0.15564 | 0.018311 | -0.018311 | 0.09613 | -0.68207 | -0.18311 | 0.11444 | 0.13733 | 0.18768 | 0.33417 | 121.5363 | 122.2366 | -0.018311 | 122.3328 | 2.9388 | -0.18311 | 122.2366 | -0.018311 | 2.9388 | 121.5363 | 122.3328 | -122.374 | -122.4014
2597.9062 | 122.2687 | -0.07782 | 122.2412 | -0.11406 | 0.010696 | -0.0044327 | 0.01468 | 0.052037 | -0.014381 | 0.065834 | 0 | 122.1542 | -0.17395 | 0.10529 | 121.5454 | 3.0533 | 0.40741 | 0.52643 | 122.3419 | -0.21057 | -0.09613 | -0.086975 | 0.07782 | 0.18311 | -0.6958 | -0.13275 | 0.10071 | 0.17395 | 0.48523 | 0.60425 | 121.6232 | 122.2321 | 0.07782 | 122.4197 | 3.1311 | -0.13275 | 122.2321 | 0.07782 | 3.1311 | 121.6232 | 122.4197 | -122.4152 | -122.4518
2599.6562 | 122.4106 | -0.054932 | 122.168 | 0.13008 | 0.010696 | -0.012337 | 0.013612 | 0.048191 | -0.014595 | 0.066689 | -0.054932 | 122.1909 | -0.19226 | 0.022888 | 121.4859 | 2.8976 | 0.23346 | 0.25635 | 122.3236 | -0.2243 | -0.13733 | 0.022888 | 0 | 0.07782 | -0.68207 | -0.16937 | 0.15564 | 0.13733 | 0.28839 | 0.31128 | 121.5408 | 122.2458 | 0 | 122.3785 | 2.9526 | -0.16937 | 122.2458 | 0 | 2.9526 | 121.5408 | 122.3785 | -122.3602 | -122.3923
2601.3438 | 122.2961 | -0.09613 | 122.2229 | -0.060654 | 0.009628 | -0.0063553 | 0.013398 | 0.049473 | -0.012031 | 0.06733 | -0.022888 | 122.1954 | -0.14648 | 0.086975 | 121.5363 | 3.0121 | 0.3479 | 0.45319 | 122.3145 | -0.2243 | -0.050354 | -0.027465 | 0.073242 | 0.1831 | -0.68664 | -0.12817 | 0.091553 | 0.1236 | 0.44403 | 0.54932 | 121.6324 | 122.2916 | 0.073242 | 122.4106 | 3.1082 | -0.12817 | 122.2916 | 0.073242 | 3.1082 | 121.6324 | 122.4106 | -122.3694 | -122.4472
2603.1094 | 122.4106 | -0.059509 | 122.1817 | 0.076676 | 0.0098416 | -0.0033647 | 0.0048534 | 0.050755 | -0.010109 | 0.065621 | 0.013733 | 122.1634 | -0.13275 | 0.086975 | 121.5637 | 2.9755 | 0.21057 | 0.43945 | 122.287 | -0.20142 | -0.073242 | -0.018311 | 0.073242 | 0.14648 | -0.61798 | -0.14191 | 0.10528 | 0.14648 | 0.27008 | 0.49896 | 121.6232 | 122.2229 | 0.073242 | 122.3465 | 3.035 | -0.14191 | 122.2229 | 0.073242 | 3.035 | 121.6232 | 122.3465 | -122.3145 | -122.3831
2604.8125 | 122.2687 | -0.10529 | 122.2183 | -0.12932 | 0.010269 | -0.0078507 | 0.012971 | 0.049473 | -0.013313 | 0.066475 | -0.009155 | 122.1725 | -0.17395 | 0.091553 | 121.5408 | 3.0762 | 0.43488 | 0.53558 | 122.3236 | -0.20142 | -0.068664 | -0.045777 | 0.096131 | 0.19684 | -0.67749 | -0.09613 | 0.10528 | 0.16479 | 0.54016 | 0.64087 | 121.6461 | 122.2778 | 0.096131 | 122.4289 | 3.1815 | -0.09613 | 122.2778 | 0.096131 | 3.1815 | 121.6461 | 122.4289 | -122.3923 | -122.4197
2606.5625 | 122.2778 | -0.091553 | 122.2046 | -0.21324 | 0.011123 | -0.0089189 | 0.013185 | 0.050328 | -0.012672 | 0.066689 | -0.036621 | 122.1954 | -0.19226 | 0.059509 | 121.5454 | 3.0853 | 0.48981 | 0.55847 | 122.3511 | -0.2243 | -0.10071 | -0.009155 | 0.054932 | 0.15106 | -0.65918 | -0.13275 | 0.14648 | 0.15564 | 0.58136 | 0.65002 | 121.637 | 122.287 | 0.054932 | 122.4426 | 3.1769 | -0.13275 | 122.287 | 0.054932 | 3.1769 | 121.637 | 122.4426 | -122.3969 | -122.4289
2608.3281 | 122.2824 | -0.10071 | 122.2 | -0.075912 | 0.0092008 | -0.0084915 | 0.012971 | 0.051823 | -0.013527 | 0.068825 | 0.018311 | 122.1863 | -0.16937 | 0.086975 | 121.5454 | 3.0258 | 0.35248 | 0.45319 | 122.3145 | -0.2243 | -0.068665 | -0.013733 | 0.11902 | 0.18768 | -0.6546 | -0.1236 | 0.11444 | 0.18768 | 0.45319 | 0.55389 | 121.6461 | 122.287 | 0.11902 | 122.4152 | 3.1265 | -0.1236 | 122.287 | 0.11902 | 3.1265 | 121.6461 | 122.4152 | -122.3694 | -122.4243
2610.0938 | 122.3923 | -0.064087 | 122.1771 | 0.084305 | 0.010696 | -0.010414 | 0.013826 | 0.051396 | -0.01139 | 0.06498 | -0.054932 | 122.2183 | -0.16479 | 0.018311 | 121.5042 | 2.8885 | 0.20599 | 0.27466 | 122.3282 | -0.2243 | -0.10071 | 0.041199 | 0.009155 | 0.082398 | -0.67291 | -0.16022 | 0.15106 | 0.10986 | 0.27008 | 0.33875 | 121.5683 | 122.2824 | 0.009155 | 122.3923 | 2.9526 | -0.16022 | 122.2824 | 0.009155 | 2.9526 | 121.5683 | 122.3923 | -122.3419 | -122.4014
2611.875 | 122.2778 | -0.10529 | 122.2321 | -0.068283 | 0.011764 | -0.0072099 | 0.014894 | 0.050541 | -0.014381 | 0.066689 | 0.009155 | 122.1863 | -0.1831 | 0.082397 | 121.5271 | 3.0396 | 0.33875 | 0.44861 | 122.3373 | -0.20142 | -0.077819 | -0.045777 | 0.11444 | 0.18768 | -0.70496 | -0.09613 | 0.10528 | 0.19226 | 0.44403 | 0.55389 | 121.6324 | 122.2916 | 0.11444 | 122.4426 | 3.1448 | -0.09613 | 122.2916 | 0.11444 | 3.1448 | 121.6324 | 122.4426 | -122.4152 | -122.4335
2613.5625 | 122.3831 | -0.064087 | 122.1954 | 0.038529 | 0.0087734 | -0.0097733 | 0.013826 | 0.054173 | -0.015236 | 0.068398 | -0.064087 | 122.2046 | -0.16479 | 0.018311 | 121.4996 | 2.9251 | 0.32044 | 0.30212 | 122.3419 | -0.20599 | -0.10071 | 0.009155 | 0 | 0.082398 | -0.6958 | -0.14191 | 0.14648 | 0.10071 | 0.38452 | 0.36621 | 121.5637 | 122.2687 | 0 | 122.406 | 2.9892 | -0.14191 | 122.2687 | 0 | 2.9892 | 121.5637 | 122.406 | -122.3602 | -122.4014
2615.3281 | 122.4106 | -0.059509 | 122.1771 | -0.0072479 | 0.010696 | -0.0102 | 0.0050672 | 0.051396 | -0.0094678 | 0.066262 | -0.013733 | 122.1909 | -0.12817 | 0.07782 | 121.5775 | 3.0396 | 0.32501 | 0.54474 | 122.3373 | -0.19226 | -0.068665 | 0.013733 | 0.045776 | 0.13733 | -0.59967 | -0.13275 | 0.16022 | 0.11444 | 0.38452 | 0.60425 | 121.637 | 122.2504 | 0.045776 | 122.3969 | 3.0991 | -0.13275 | 122.2504 | 0.045776 | 3.0991 | 121.637 | 122.3969 | -122.3053 | -122.3694
2617.0938 | 122.3236 | -0.091553 | 122.2092 | -0.22087 | 0.0092008 | -0.010414 | 0.010194 | 0.047978 | -0.013099 | 0.066475 | -0.064087 | 122.2 | -0.19226 | 0.032043 | 121.5088 | 3.067 | 0.60883 | 0.59509 | 122.3465 | -0.22888 | -0.10071 | -0.009155 | 0.027466 | 0.1236 | -0.70038 | -0.13733 | 0.13733 | 0.12817 | 0.70038 | 0.68665 | 121.6003 | 122.2916 | 0.027466 | 122.4381 | 3.1586 | -0.13733 | 122.2916 | 0.027466 | 3.1586 | 121.6003 | 122.4381 | -122.4014 | -122.438
2618.8594 | 122.3923 | -0.07782 | 122.1909 | 0.046158 | 0.012832 | -0.0050735 | 0.013185 | 0.050328 | -0.011818 | 0.065193 | -0.050354 | 122.2046 | -0.17395 | 0.013733 | 121.4813 | 2.9388 | 0.32501 | 0.28839 | 122.3694 | -0.22888 | -0.09613 | 0.013733 | 0.027466 | 0.091553 | -0.70953 | -0.15106 | 0.17853 | 0.1236 | 0.40283 | 0.36621 | 121.5591 | 122.2824 | 0.027466 | 122.4472 | 3.0167 | -0.15106 | 122.2824 | 0.027466 | 3.0167 | 121.5591 | 122.4472 | -122.3648 | -122.4197
2620.625 | 122.3969 | -0.073242 | 122.1634 | -0.045395 | 0.012619 | -0.012337 | 0.0067762 | 0.049046 | -0.0096814 | 0.065834 | -0.004578 | 122.2046 | -0.1236 | 0.086975 | 121.5912 | 3.067 | 0.33417 | 0.57678 | 122.3007 | -0.20142 | -0.050354 | 0.041199 | 0.068664 | 0.16022 | -0.5722 | -0.12817 | 0.13733 | 0.11902 | 0.40741 | 0.65002 | 121.6644 | 122.2778 | 0.068664 | 122.374 | 3.1403 | -0.12817 | 122.2778 | 0.068664 | 3.1403 | 121.6644 | 122.374 | -122.287 | -122.3648
2622.3281 | 122.4014 | -0.073242 | 122.1863 | 0.12245 | 0.0087734 | -0.0087051 | 0.0093396 | 0.050114 | -0.011177 | 0.066262 | 0.041199 | 122.1909 | -0.12817 | 0.086975 | 121.5775 | 2.9938 | 0.16937 | 0.42572 | 122.2824 | -0.19684 | -0.054932 | 0.004578 | 0.11444 | 0.16022 | -0.60882 | -0.1236 | 0.096131 | 0.16937 | 0.24261 | 0.49896 | 121.6507 | 122.2641 | 0.11444 | 122.3557 | 3.067 | -0.1236 | 122.2641 | 0.11444 | 3.067 | 121.6507 | 122.3557 | -122.3145 | -122.3831
2624.0938 | 122.3785 | -0.068665 | 122.1817 | 0.14534 | 0.0098416 | -0.0099869 | 0.013185 | 0.049473 | -0.012031 | 0.065621 | 0.041199 | 122.1542 | -0.14191 | 0.14191 | 121.5866 | 3.0075 | 0.041199 | 0.39825 | 122.2916 | -0.17395 | -0.073242 | -0.027466 | 0.10986 | 0.21057 | -0.59509 | -0.10528 | 0.10986 | 0.18311 | 0.10986 | 0.46692 | 121.6553 | 122.2229 | 0.10986 | 122.3602 | 3.0762 | -0.10528 | 122.2229 | 0.10986 | 3.0762 | 121.6553 | 122.3602 | -122.3236 | -122.3557
2625.7812 | 122.3785 | -0.086975 | 122.2046 | 0.12245 | 0.0068508 | -0.0046463 | 0.011049 | 0.048619 | -0.0090406 | 0.065834 | 0.032043 | 122.1542 | -0.1236 | 0.14191 | 121.5958 | 3.0121 | 0.086975 | 0.42114 | 122.2733 | -0.17853 | -0.036621 | -0.050354 | 0.11902 | 0.22888 | -0.60883 | -0.091553 | 0.068664 | 0.15564 | 0.17395 | 0.50812 | 121.6827 | 122.2412 | 0.11902 | 122.3602 | 3.0991 | -0.091553 | 122.2412 | 0.11902 | 3.0991 | 121.6827 | 122.3602 | -122.3282 | -122.3831
2627.5312 | 122.2916 | -0.11444 | 122.2275 | -0.083542 | 0.0098416 | -0.0084915 | 0.015107 | 0.048191 | -0.015876 | 0.066262 | 0.018311 | 122.2 | -0.18768 | 0.10986 | 121.5454 | 3.067 | 0.33417 | 0.48065 | 122.3282 | -0.21515 | -0.073242 | -0.027466 | 0.13275 | 0.2243 | -0.68207 | -0.10071 | 0.10071 | 0.20599 | 0.44861 | 0.59509 | 121.6599 | 122.3145 | 0.13275 | 122.4426 | 3.1815 | -0.10071 | 122.3145 | 0.13275 | 3.1815 | 121.6599 | 122.4426 | -122.4152 | -122.4426
2629.2344 | 122.3099 | -0.086975 | 122.2275 | -0.12932 | 0.012832 | -0.011696 | 0.0089124 | 0.045628 | -0.013313 | 0.068398 | 0.059509 | 122.1909 | -0.14191 | 0.16479 | 121.6324 | 3.1631 | 0.3479 | 0.70038 | 122.287 | -0.17853 | -0.054932 | -0.036621 | 0.14648 | 0.25177 | -0.59509 | -0.091553 | 0.059509 | 0.20142 | 0.43488 | 0.78735 | 121.7194 | 122.2778 | 0.14648 | 122.374 | 3.2501 | -0.091553 | 122.2778 | 0.14648 | 3.2501 | 121.7194 | 122.374 | -122.3694 | -122.406
2630.9844 | 122.3602 | -0.082397 | 122.2 | -0.2285 | 0.0094144 | -0.0082779 | 0.0076306 | 0.046696 | -0.010963 | 0.06498 | 0.036621 | 122.1909 | -0.15106 | 0.14648 | 121.6324 | 3.1311 | 0.35248 | 0.67749 | 122.2916 | -0.18768 | -0.068665 | -0.009155 | 0.11902 | 0.22888 | -0.56763 | -0.10529 | 0.091553 | 0.18768 | 0.43488 | 0.75989 | 121.7148 | 122.2733 | 0.11902 | 122.374 | 3.2135 | -0.10529 | 122.2733 | 0.11902 | 3.2135 | 121.7148 | 122.374 | -122.3511 | -122.3877
2632.7344 | 122.3053 | -0.10529 | 122.2092 | -0.15221 | 0.011123 | -0.011909 | 0.007417 | 0.046696 | -0.011177 | 0.064553 | 0.064087 | 122.2 | -0.11902 | 0.1831 | 121.6324 | 3.1631 | 0.33875 | 0.72327 | 122.2916 | -0.19684 | -0.013733 | -0.009155 | 0.16937 | 0.28839 | -0.57678 | -0.091552 | 0.082398 | 0.18311 | 0.44403 | 0.82855 | 121.7377 | 122.3053 | 0.16937 | 122.3969 | 3.2684 | -0.091552 | 122.3053 | 0.16937 | 3.2684 | 121.7377 | 122.3969 | -122.3282 | -122.406
2634.4219 | 122.3648 | -0.064087 | 122.2 | 0.19112 | 0.0094144 | -0.0093461 | 0.013826 | 0.051396 | -0.014595 | 0.06733 | 0.059509 | 122.1085 | -0.13275 | 0.15106 | 121.6095 | 3.0167 | 0.054932 | 0.39825 | 122.3007 | -0.19226 | -0.068664 | -0.091553 | 0.1236 | 0.21515 | -0.59051 | -0.12817 | 0.10071 | 0.19226 | 0.11902 | 0.46234 | 121.6736 | 122.1725 | 0.1236 | 122.3648 | 3.0808 | -0.12817 | 122.1725 | 0.1236 | 3.0808 | 121.6736 | 122.3648 | -122.3328 | -122.3923
2636.1719 | 122.3785 | -0.045776 | 122.1909 | 0.1606 | 0.011337 | -0.0074235 | 0.012971 | 0.048832 | -0.013527 | 0.067757 | 0.022888 | 122.1542 | -0.15564 | 0.1236 | 121.5683 | 2.9938 | 0.059509 | 0.36621 | 122.3145 | -0.18768 | -0.10986 | -0.036621 | 0.068664 | 0.16937 | -0.62256 | -0.14191 | 0.1236 | 0.17853 | 0.10528 | 0.41199 | 121.6141 | 122.2 | 0.068664 | 122.3602 | 3.0396 | -0.14191 | 122.2 | 0.068664 | 3.0396 | 121.6141 | 122.3602 | -122.3465 | -122.3785
2637.8594 | 122.374 | -0.07782 | 122.1909 | -0.10643 | 0.01091 | -0.015114 | 0.0063488 | 0.046269 | -0.009895 | 0.066689 | 0.022888 | 122.1954 | -0.13275 | 0.14191 | 121.6095 | 3.1082 | 0.35706 | 0.6546 | 122.2961 | -0.21057 | -0.054931 | 0.004578 | 0.10071 | 0.21973 | -0.58136 | -0.13275 | 0.10529 | 0.15564 | 0.43488 | 0.73242 | 121.6873 | 122.2733 | 0.10071 | 122.374 | 3.186 | -0.13275 | 122.2733 | 0.10071 | 3.186 | 121.6873 | 122.374 | -122.3236 | -122.4014
2639.625 | 122.3923 | -0.050354 | 122.2046 | 0.15297 | 0.0085598 | -0.0102 | 0.014039 | 0.048405 | -0.013954 | 0.065193 | 0.027466 | 122.1634 | -0.14648 | 0.13733 | 121.5866 | 2.9938 | 0.07782 | 0.36621 | 122.2961 | -0.17853 | -0.09613 | -0.041199 | 0.07782 | 0.18768 | -0.61798 | -0.12817 | 0.091553 | 0.17395 | 0.12817 | 0.41657 | 121.637 | 122.2137 | 0.07782 | 122.3465 | 3.0441 | -0.12817 | 122.2137 | 0.07782 | 3.0441 | 121.637 | 122.3465 | -122.3511 | -122.3831
2641.375 | 122.2824 | -0.10529 | 122.2366 | -0.12169 | 0.010055 | -0.010628 | 0.013826 | 0.049259 | -0.015236 | 0.065834 | -0.004578 | 122.1817 | -0.17853 | 0.11444 | 121.55 | 3.0899 | 0.39825 | 0.5127 | 122.3145 | -0.20599 | -0.073242 | -0.054931 | 0.10071 | 0.21973 | -0.68664 | -0.10071 | 0.07782 | 0.17395 | 0.50354 | 0.61798 | 121.6553 | 122.287 | 0.10071 | 122.4197 | 3.1952 | -0.10071 | 122.287 | 0.10071 | 3.1952 | 121.6553 | 122.4197 | -122.4152 | -122.4426
2643.0781 | 122.4152 | -0.054932 | 122.1909 | 0.10719 | 0.012832 | -0.010414 | 0.013398 | 0.04755 | -0.012672 | 0.065621 | -0.059509 | 122.2183 | -0.16479 | 0.032043 | 121.5042 | 2.9343 | 0.21515 | 0.26093 | 122.3465 | -0.23346 | -0.10986 | 0.027466 | -0.004577 | 0.086975 | -0.68665 | -0.17853 | 0.15564 | 0.10529 | 0.27008 | 0.31586 | 121.5591 | 122.2733 | -0.004577 | 122.4014 | 2.9892 | -0.17853 | 122.2733 | -0.004577 | 2.9892 | 121.5591 | 122.4014 | -122.3557 | -122.4243
2644.8438 | 122.3785 | -0.068665 | 122.2137 | 0.15297 | 0.01091 | -0.0057145 | 0.011049 | 0.047337 | -0.011177 | 0.066902 | 0.059509 | 122.2092 | -0.11444 | 0.15106 | 121.6095 | 3.0167 | 0.068665 | 0.41657 | 122.2687 | -0.19226 | -0.045776 | -0.004578 | 0.12817 | 0.21973 | -0.60425 | -0.1236 | 0.054932 | 0.17395 | 0.13733 | 0.48523 | 121.6782 | 122.2778 | 0.12817 | 122.3373 | 3.0853 | -0.1236 | 122.2778 | 0.12817 | 3.0853 | 121.6782 | 122.3373 | -122.3282 | -122.406
2646.6094 | 122.3831 | -0.07782 | 122.1954 | 0.13008 | 0.0094144 | -0.0084915 | 0.010621 | 0.0499 | -0.011177 | 0.066689 | 0.050354 | 122.2 | -0.14191 | 0.12817 | 121.5958 | 3.0167 | 0.064087 | 0.37994 | 122.2916 | -0.19226 | -0.064087 | 0.004577 | 0.12817 | 0.20599 | -0.59967 | -0.11444 | 0.09613 | 0.19226 | 0.14191 | 0.45776 | 121.6736 | 122.2778 | 0.12817 | 122.3694 | 3.0945 | -0.11444 | 122.2778 | 0.12817 | 3.0945 | 121.6736 | 122.3694 | -122.3373 | -122.3877
2648.375 | 122.2778 | -0.10986 | 122.2412 | -0.083542 | 0.009628 | -0.0095597 | 0.013185 | 0.047978 | -0.013954 | 0.066689 | -0.022888 | 122.2046 | -0.17853 | 0.086975 | 121.5591 | 3.0945 | 0.37079 | 0.50812 | 122.3328 | -0.21973 | -0.068665 | -0.036621 | 0.086975 | 0.19684 | -0.68207 | -0.10986 | 0.091553 | 0.15564 | 0.48065 | 0.61798 | 121.669 | 122.3145 | 0.086975 | 122.4426 | 3.2043 | -0.10986 | 122.3145 | 0.086975 | 3.2043 | 121.669 | 122.4426 | -122.4197 | -122.4609
2650.0781 | 122.3511 | -0.073242 | 122.2046 | -0.045395 | 0.0085598 | -0.0089189 | 0.012117 | 0.049473 | -0.013313 | 0.067757 | -0.041199 | 122.2046 | -0.1831 | 0.036621 | 121.4859 | 2.9755 | 0.31586 | 0.3479 | 122.3373 | -0.22888 | -0.10986 | 0 | 0.032043 | 0.10986 | -0.71869 | -0.15564 | 0.13275 | 0.14191 | 0.3891 | 0.42114 | 121.5591 | 122.2778 | 0.032043 | 122.4106 | 3.0487 | -0.15564 | 122.2778 | 0.032043 | 3.0487 | 121.5591 | 122.4106 | -122.3877 | -122.4335
2651.8281 | 122.406 | -0.050354 | 122.1588 | 0.13008 | 0.010055 | -0.0093461 | 0.01233 | 0.049259 | -0.011177 | 0.063484 | -0.050354 | 122.1817 | -0.16937 | 0.009155 | 121.5088 | 2.9297 | 0.22888 | 0.27008 | 122.3877 | -0.21973 | -0.11902 | 0.022889 | 0 | 0.059509 | -0.65002 | -0.16937 | 0.22888 | 0.11902 | 0.27924 | 0.32044 | 121.5591 | 122.2321 | 0 | 122.438 | 2.98 | -0.16937 | 122.2321 | 0 | 2.98 | 121.5591 | 122.438 | -122.3282 | -122.3785
2653.5781 | 122.2961 | -0.10071 | 122.2137 | -0.20561 | 0.010696 | -0.0093461 | 0.011476 | 0.051396 | -0.014808 | 0.065193 | -0.036621 | 122.2046 | -0.1831 | 0.082397 | 121.5408 | 3.1174 | 0.49439 | 0.55847 | 122.3602 | -0.20599 | -0.082397 | -0.009155 | 0.064087 | 0.18311 | -0.67291 | -0.10529 | 0.14648 | 0.14648 | 0.59509 | 0.65918 | 121.6415 | 122.3053 | 0.064087 | 122.4609 | 3.2181 | -0.10529 | 122.3053 | 0.064087 | 3.2181 | 121.6415 | 122.4609 | -122.3969 | -122.4197
2655.2656 | 122.374 | -0.073242 | 122.1954 | 0.10719 | 0.010696 | -0.0087051 | 0.011262 | 0.047764 | -0.012672 | 0.067757 | 0.032043 | 122.1497 | -0.12817 | 0.1236 | 121.6003 | 3.035 | 0.082397 | 0.37994 | 122.287 | -0.19226 | -0.054932 | -0.045777 | 0.10529 | 0.19684 | -0.59509 | -0.11902 | 0.091552 | 0.16022 | 0.15564 | 0.45319 | 121.6736 | 122.2229 | 0.10529 | 122.3602 | 3.1082 | -0.11902 | 122.2229 | 0.10529 | 3.1082 | 121.6736 | 122.3602 | -122.3236 | -122.3877
2657.0156 | 122.3282 | -0.086975 | 122.2137 | -0.12169 | 0.0083462 | -0.010841 | 0.0059216 | 0.045841 | -0.013099 | 0.06498 | 0.073242 | 122.1817 | -0.13733 | 0.16937 | 121.6232 | 3.1723 | 0.36163 | 0.69122 | 122.287 | -0.20599 | -0.050354 | -0.032043 | 0.16022 | 0.25635 | -0.59051 | -0.11902 | 0.073242 | 0.21057 | 0.44861 | 0.7782 | 121.7102 | 122.2687 | 0.16022 | 122.374 | 3.2593 | -0.11902 | 122.2687 | 0.16022 | 3.2593 | 121.7102 | 122.374 | -122.3511 | -122.4197
2658.7031 | 122.3419 | -0.082397 | 122.1954 | -0.23613 | 0.010269 | -0.011482 | 0.012758 | 0.050328 | -0.012031 | 0.064339 | -0.068665 | 122.2229 | -0.17853 | 0.041199 | 121.5042 | 3.1036 | 0.59509 | 0.59052 | 122.374 | -0.23346 | -0.096131 | 0.027465 | 0.013732 | 0.1236 | -0.69122 | -0.15106 | 0.17853 | 0.10986 | 0.67749 | 0.67291 | 121.5866 | 122.3053 | 0.013732 | 122.4564 | 3.186 | -0.15106 | 122.3053 | 0.013732 | 3.186 | 121.5866 | 122.4564 | -122.374 | -122.4289
2660.4688 | 122.3969 | -0.050354 | 122.1863 | 0.069046 | 0.010055 | -0.010628 | 0.015107 | 0.048832 | -0.014167 | 0.066475 | -0.064087 | 122.2229 | -0.17395 | 0.027466 | 121.4722 | 2.9572 | 0.27008 | 0.28381 | 122.3511 | -0.24261 | -0.1236 | 0.036621 | -0.013733 | 0.07782 | -0.71411 | -0.19226 | 0.16479 | 0.10986 | 0.32044 | 0.33417 | 121.5225 | 122.2733 | -0.013733 | 122.4014 | 3.0075 | -0.19226 | 122.2733 | -0.013733 | 3.0075 | 121.5225 | 122.4014 | -122.3602 | -122.4289
2662.1562 | 122.4014 | -0.050354 | 122.2 | 0.053787 | 0.0092008 | -0.012764 | 0.012544 | 0.0499 | -0.015236 | 0.066048 | -0.073242 | 122.1863 | -0.18768 | 0.018311 | 121.4767 | 2.9663 | 0.27008 | 0.29297 | 122.3373 | -0.21973 | -0.13733 | -0.013733 | -0.022888 | 0.068665 | -0.72327 | -0.16937 | 0.13733 | 0.11444 | 0.32044 | 0.34332 | 121.5271 | 122.2366 | -0.022888 | 122.3877 | 3.0167 | -0.16937 | 122.2366 | -0.022888 | 3.0167 | 121.5271 | 122.3877 | -122.3877 | -122.4197
2663.9219 | 122.3877 | -0.064087 | 122.2 | 0.046158 | 0.011551 | -0.0097733 | 0.01468 | 0.052037 | -0.01374 | 0.064553 | -0.036621 | 122.2092 | -0.16022 | 0.013733 | 121.4905 | 2.9663 | 0.32044 | 0.31586 | 122.3694 | -0.2243 | -0.09613 | 0.009155 | 0.027466 | 0.07782 | -0.70953 | -0.16022 | 0.16937 | 0.1236 | 0.38452 | 0.37994 | 121.5546 | 122.2733 | 0.027466 | 122.4335 | 3.0304 | -0.16022 | 122.2733 | 0.027466 | 3.0304 | 121.5546 | 122.4335 | -122.3602 | -122.4243
2665.6719 | 122.374 | -0.073242 | 122.1863 | 0.15297 | 0.0070646 | -0.0093461 | 0.0067762 | 0.050328 | -0.012458 | 0.066048 | 0.036621 | 122.1359 | -0.14191 | 0.13275 | 121.6141 | 3.0441 | 0.091553 | 0.4303 | 122.3099 | -0.17853 | -0.068665 | -0.050354 | 0.10986 | 0.20599 | -0.5722 | -0.10529 | 0.1236 | 0.17853 | 0.16479 | 0.50354 | 121.6873 | 122.2092 | 0.10986 | 122.3831 | 3.1174 | -0.10529 | 122.2092 | 0.10986 | 3.1174 | 121.6873 | 122.3831 | -122.3282 | -122.3648
2667.3594 | 122.3969 | -0.059509 | 122.1771 | 0.17586 | 0.0089872 | -0.011055 | 0.011903 | 0.048832 | -0.012886 | 0.066262 | -0.027466 | 122.1771 | -0.17853 | 0.064087 | 121.55 | 2.98 | 0.13275 | 0.31586 | 122.3145 | -0.20142 | -0.11902 | 0 | 0.032043 | 0.1236 | -0.62714 | -0.14191 | 0.13733 | 0.15106 | 0.19226 | 0.37537 | 121.6095 | 122.2366 | 0.032043 | 122.374 | 3.0396 | -0.14191 | 122.2366 | 0.032043 | 3.0396 | 121.6095 | 122.374 | -122.3557 | -122.3785
2669.1094 | 122.4335 | -0.064087 | 122.1954 | 0.0080111 | 0.0081326 | -0.0089189 | 0.0059216 | 0.047978 | -0.011177 | 0.067543 | 0 | 122.1817 | -0.14648 | 0.082397 | 121.5683 | 3.0533 | 0.31586 | 0.50354 | 122.2961 | -0.22888 | -0.082397 | -0.013733 | 0.064087 | 0.14648 | -0.62714 | -0.16479 | 0.10071 | 0.14648 | 0.37994 | 0.56763 | 121.6324 | 122.2458 | 0.064087 | 122.3602 | 3.1174 | -0.16479 | 122.2458 | 0.064087 | 3.1174 | 121.6324 | 122.3602 | -122.3419 | -122.4243
2670.8125 | 122.3785 | -0.07782 | 122.2046 | -0.11406 | 0.0089872 | -0.010628 | 0.007417 | 0.048832 | -0.012245 | 0.066048 | 0.022888 | 122.1863 | -0.15106 | 0.12817 | 121.6141 | 3.1448 | 0.36621 | 0.65918 | 122.319 | -0.20599 | -0.073242 | -0.018311 | 0.10071 | 0.20599 | -0.59051 | -0.12817 | 0.11444 | 0.17395 | 0.44403 | 0.737 | 121.6919 | 122.2641 | 0.10071 | 122.3969 | 3.2227 | -0.12817 | 122.2641 | 0.10071 | 3.2227 | 121.6919 | 122.3969 | -122.3557 | -122.4106
2672.5625 | 122.3007 | -0.11902 | 122.2046 | -0.18272 | 0.01091 | -0.010841 | 0.011689 | 0.047337 | -0.013099 | 0.065193 | 0.041199 | 122.1954 | -0.13275 | 0.15106 | 121.6049 | 3.2043 | 0.48065 | 0.72327 | 122.3099 | -0.18768 | -0.013732 | -0.009155 | 0.16022 | 0.27008 | -0.59967 | -0.068664 | 0.10529 | 0.17395 | 0.59967 | 0.84229 | 121.7239 | 122.3145 | 0.16022 | 122.4289 | 3.3234 | -0.068664 | 122.3145 | 0.16022 | 3.3234 | 121.7239 | 122.4289 | -122.3373 | -122.3923
2674.3125 | 122.3053 | -0.1236 | 122.2046 | -0.20561 | 0.0092008 | -0.011482 | 0.011049 | 0.046482 | -0.012245 | 0.066475 | 0.032043 | 122.1588 | -0.12817 | 0.14191 | 121.5866 | 3.1998 | 0.52643 | 0.70953 | 122.3099 | -0.21057 | -0.004578 | -0.045777 | 0.15564 | 0.2655 | -0.61798 | -0.086975 | 0.10529 | 0.16022 | 0.65002 | 0.83313 | 121.7102 | 122.2824 | 0.15564 | 122.4335 | 3.3234 | -0.086975 | 122.2824 | 0.15564 | 3.3234 | 121.7102 | 122.4335 | -122.3328 | -122.4152
2676.0625 | 122.4106 | -0.036621 | 122.2 | 0.02327 | 0.0098416 | -0.0080643 | 0.0089124 | 0.046696 | -0.011177 | 0.066262 | -0.004578 | 122.1909 | -0.13275 | 0.09613 | 121.5637 | 3.067 | 0.33417 | 0.52185 | 122.3099 | -0.20599 | -0.09613 | -0.009155 | 0.032043 | 0.13275 | -0.63629 | -0.16937 | 0.10986 | 0.12817 | 0.37079 | 0.55847 | 121.6003 | 122.2275 | 0.032043 | 122.3465 | 3.1036 | -0.16937 | 122.2275 | 0.032043 | 3.1036 | 121.6003 | 122.3465 | -122.3328 | -122.406
2677.8125 | 122.3053 | -0.10986 | 122.2321 | -0.18272 | 0.0094144 | -0.011909 | 0.010194 | 0.048191 | -0.011818 | 0.064766 | 0.041199 | 122.1634 | -0.14648 | 0.16022 | 121.6049 | 3.2135 | 0.46234 | 0.74158 | 122.2916 | -0.21057 | -0.036621 | -0.068665 | 0.15106 | 0.27008 | -0.62714 | -0.10071 | 0.059509 | 0.18768 | 0.5722 | 0.85144 | 121.7148 | 122.2733 | 0.15106 | 122.4014 | 3.3234 | -0.10071 | 122.2733 | 0.15106 | 3.3234 | 121.7148 | 122.4014 | -122.3785 | -122.4426
2679.5781 | 122.2824 | -0.091553 | 122.2183 | -0.13695 | 0.012191 | -0.013191 | 0.016389 | 0.048191 | -0.014808 | 0.066475 | -0.013733 | 122.1863 | -0.17853 | 0.09613 | 121.55 | 3.1448 | 0.45776 | 0.5722 | 122.3557 | -0.2243 | -0.086975 | -0.032044 | 0.07782 | 0.18768 | -0.66833 | -0.13275 | 0.13733 | 0.16479 | 0.54932 | 0.66376 | 121.6415 | 122.2778 | 0.07782 | 122.4472 | 3.2364 | -0.13275 | 122.2778 | 0.07782 | 3.2364 | 121.6415 | 122.4472 | -122.3969 | -122.4426
2681.2812 | 122.406 | -0.054932 | 122.1909 | 0.16823 | 0.012832 | -0.0076371 | 0.013612 | 0.047978 | -0.010963 | 0.065834 | -0.022888 | 122.2137 | -0.16479 | 0.10071 | 121.55 | 3.0029 | 0.09613 | 0.36163 | 122.3053 | -0.19226 | -0.10986 | 0.022888 | 0.032044 | 0.15564 | -0.64087 | -0.13733 | 0.11444 | 0.14191 | 0.15106 | 0.41656 | 121.6049 | 122.2687 | 0.032044 | 122.3602 | 3.0579 | -0.13733 | 122.2687 | 0.032044 | 3.0579 | 121.6049 | 122.3602 | -122.3557 | -122.3831
2682.9844 | 122.3831 | -0.064087 | 122.1771 | 0.12245 | 0.0089872 | -0.0093461 | 0.013826 | 0.050968 | -0.011177 | 0.06498 | 0.050354 | 122.2183 | -0.15106 | 0.13275 | 121.6003 | 3.0579 | 0.091553 | 0.37994 | 122.3282 | -0.18768 | -0.086975 | 0.041199 | 0.11444 | 0.19684 | -0.57678 | -0.1236 | 0.15106 | 0.20142 | 0.15564 | 0.44403 | 121.6644 | 122.2824 | 0.11444 | 122.3923 | 3.1219 | -0.1236 | 122.2824 | 0.11444 | 3.1219 | 121.6644 | 122.3923 | -122.3282 | -122.3648
2684.7344 | 122.2916 | -0.10071 | 122.2366 | -0.075912 | 0.0089872 | -0.013832 | 0.015321 | 0.050541 | -0.017799 | 0.067543 | 0 | 122.1954 | -0.17853 | 0.10529 | 121.55 | 3.1128 | 0.36621 | 0.48981 | 122.3969 | -0.21515 | -0.07782 | -0.041198 | 0.10071 | 0.20599 | -0.68664 | -0.11444 | 0.16022 | 0.17853 | 0.46692 | 0.59052 | 121.6507 | 122.2961 | 0.10071 | 122.4976 | 3.2135 | -0.11444 | 122.2961 | 0.10071 | 3.2135 | 121.6507 | 122.4976 | -122.4152 | -122.4518
2686.4844 | 122.3785 | -0.068665 | 122.1863 | 0.14534 | 0.009628 | -0.0095597 | 0.011689 | 0.049259 | -0.013527 | 0.066475 | 0.018311 | 122.1817 | -0.16022 | 0.13275 | 121.6003 | 3.0624 | 0.091553 | 0.39368 | 122.3053 | -0.17395 | -0.091552 | -0.004577 | 0.086976 | 0.20142 | -0.58594 | -0.10528 | 0.11902 | 0.17853 | 0.16022 | 0.46234 | 121.669 | 122.2504 | 0.086976 | 122.374 | 3.1311 | -0.10528 | 122.2504 | 0.086976 | 3.1311 | 121.669 | 122.374 | -122.3465 | -122.3602
2688.1719 | 122.4014 | -0.059509 | 122.2046 | 0.12245 | 0.01091 | -0.014687 | 0.0063488 | 0.048832 | -0.01139 | 0.068398 | 0.036621 | 122.2 | -0.12817 | 0.10071 | 121.5729 | 3.0441 | 0.16022 | 0.43488 | 122.3099 | -0.19684 | -0.068665 | -0.004578 | 0.09613 | 0.16022 | -0.63171 | -0.13733 | 0.10529 | 0.1648 | 0.21973 | 0.49438 | 121.6324 | 122.2595 | 0.09613 | 122.3694 | 3.1036 | -0.13733 | 122.2595 | 0.09613 | 3.1036 | 121.6324 | 122.3694 | -122.3328 | -122.4014
2689.9375 | 122.3877 | -0.054932 | 122.1954 | 0.13771 | 0.0085598 | -0.010628 | 0.013185 | 0.048191 | -0.01374 | 0.066475 | 0.022888 | 122.1771 | -0.15564 | 0.13733 | 121.5958 | 3.0441 | 0.091553 | 0.3891 | 122.3099 | -0.20599 | -0.10071 | -0.018311 | 0.07782 | 0.19226 | -0.59967 | -0.15106 | 0.11444 | 0.17853 | 0.14649 | 0.44403 | 121.6507 | 122.2321 | 0.07782 | 122.3648 | 3.0991 | -0.15106 | 122.2321 | 0.07782 | 3.0991 | 121.6507 | 122.3648 | -122.3511 | -122.4014
2691.6875 | 122.3236 | -0.091553 | 122.2092 | -0.19798 | 0.012832 | -0.014473 | 0.012758 | 0.049259 | -0.012886 | 0.06498 | -0.027466 | 122.2412 | -0.17395 | 0.064087 | 121.5637 | 3.1448 | 0.53101 | 0.57678 | 122.3785 | -0.21973 | -0.082397 | 0.032044 | 0.064087 | 0.15564 | -0.64545 | -0.12817 | 0.16937 | 0.14648 | 0.62256 | 0.66834 | 121.6553 | 122.3328 | 0.064087 | 122.4701 | 3.2364 | -0.12817 | 122.3328 | 0.064087 | 3.2364 | 121.6553 | 122.4701 | -122.3831 | -122.4289
2693.375 | 122.3007 | -0.091553 | 122.2 | -0.18272 | 0.011123 | -0.0093461 | 0.015535 | 0.050541 | -0.014808 | 0.064553 | -0.018311 | 122.2229 | -0.17853 | 0.073242 | 121.5591 | 3.1586 | 0.51727 | 0.5722 | 122.3831 | -0.21515 | -0.086975 | 0.022888 | 0.073242 | 0.16479 | -0.64087 | -0.1236 | 0.18311 | 0.16022 | 0.60883 | 0.66376 | 121.6507 | 122.3145 | 0.073242 | 122.4747 | 3.2501 | -0.1236 | 122.3145 | 0.073242 | 3.2501 | 121.6507 | 122.4747 | -122.3785 | -122.4152
2695.1406 | 122.287 | -0.11444 | 122.2412 | -0.17509 | 0.0098416 | -0.010628 | 0.007417 | 0.047337 | -0.01139 | 0.06797 | 0.050354 | 122.1909 | -0.14648 | 0.16479 | 121.637 | 3.2455 | 0.42114 | 0.737 | 122.3099 | -0.1831 | -0.032043 | -0.050354 | 0.16479 | 0.27924 | -0.60425 | -0.068664 | 0.068664 | 0.19684 | 0.53558 | 0.85144 | 121.7514 | 122.3053 | 0.16479 | 122.4243 | 3.36 | -0.068664 | 122.3053 | 0.16479 | 3.36 | 121.7514 | 122.4243 | -122.3877 | -122.4243
2696.8281 | 122.3511 | -0.09613 | 122.2137 | -0.25139 | 0.0083462 | -0.011269 | 0.012971 | 0.050114 | -0.013954 | 0.065193 | -0.064087 | 122.2229 | -0.1831 | 0.041199 | 121.5134 | 3.1311 | 0.6134 | 0.59052 | 122.4014 | -0.23804 | -0.086975 | 0.009155 | 0.032043 | 0.13733 | -0.70038 | -0.14191 | 0.18768 | 0.11902 | 0.70953 | 0.68664 | 121.6095 | 122.319 | 0.032043 | 122.4976 | 3.2272 | -0.14191 | 122.319 | 0.032043 | 3.2272 | 121.6095 | 122.4976 | -122.3969 | -122.4518
2698.5781 | 122.3877 | -0.059509 | 122.2137 | -0.098801 | 0.0092008 | -0.0084915 | 0.0076306 | 0.049259 | -0.012031 | 0.066902 | 0.022888 | 122.1909 | -0.12817 | 0.14648 | 121.6278 | 3.1769 | 0.36621 | 0.65002 | 122.2961 | -0.19684 | -0.068665 | -0.022888 | 0.082397 | 0.20599 | -0.58594 | -0.13733 | 0.082398 | 0.15106 | 0.42572 | 0.70953 | 121.6873 | 122.2504 | 0.082397 | 122.3557 | 3.2364 | -0.13733 | 122.2504 | 0.082397 | 3.2364 | 121.6873 | 122.3557 | -122.3419 | -122.4106
2700.3281 | 122.3969 | -0.064087 | 122.2046 | 0.053787 | 0.010482 | -0.0087051 | 0.013398 | 0.050541 | -0.013313 | 0.067543 | -0.045776 | 122.2137 | -0.1831 | 0.018311 | 121.4859 | 2.98 | 0.31128 | 0.29755 | 122.3694 | -0.23804 | -0.11902 | 0.009155 | 0.018311 | 0.082398 | -0.71869 | -0.17395 | 0.16479 | 0.13733 | 0.37537 | 0.36163 | 121.55 | 122.2778 | 0.018311 | 122.4335 | 3.0441 | -0.17395 | 122.2778 | 0.018311 | 3.0441 | 121.55 | 122.4335 | -122.3877 | -122.4426
2702.0938 | 122.3831 | -0.068665 | 122.1909 | -0.098801 | 0.009628 | -0.0095597 | 0.0059216 | 0.046482 | -0.011604 | 0.065621 | 0.022888 | 122.2 | -0.13275 | 0.14191 | 121.6415 | 3.1998 | 0.36163 | 0.6546 | 122.2916 | -0.19226 | -0.064086 | 0.009155 | 0.091553 | 0.21057 | -0.54932 | -0.1236 | 0.10071 | 0.15564 | 0.4303 | 0.72327 | 121.7102 | 122.2687 | 0.091553 | 122.3602 | 3.2684 | -0.1236 | 122.2687 | 0.091553 | 3.2684 | 121.7102 | 122.3602 | -122.3236 | -122.3831
2703.8594 | 122.4289 | -0.068665 | 122.1817 | 0.053787 | 0.012832 | -0.0080643 | 0.010835 | 0.04755 | -0.01075 | 0.065407 | 0.013733 | 122.2092 | -0.13275 | 0.10071 | 121.5637 | 3.0716 | 0.23804 | 0.45319 | 122.3053 | -0.20599 | -0.064086 | 0.027465 | 0.082398 | 0.16937 | -0.61798 | -0.13733 | 0.1236 | 0.14648 | 0.3067 | 0.52185 | 121.6324 | 122.2778 | 0.082398 | 122.374 | 3.1403 | -0.13733 | 122.2778 | 0.082398 | 3.1403 | 121.6324 | 122.374 | -122.3145 | -122.3877
2705.625 | 122.4289 | -0.059509 | 122.1771 | 0.10719 | 0.0083462 | -0.0080643 | 0.011262 | 0.049046 | -0.010536 | 0.064766 | 0.036621 | 122.1771 | -0.13275 | 0.10529 | 121.582 | 3.0487 | 0.18768 | 0.44403 | 122.3328 | -0.20599 | -0.073242 | 0 | 0.09613 | 0.16479 | -0.59509 | -0.14649 | 0.15564 | 0.16937 | 0.24719 | 0.50354 | 121.6415 | 122.2366 | 0.09613 | 122.3923 | 3.1082 | -0.14649 | 122.2366 | 0.09613 | 3.1082 | 121.6415 | 122.3923 | -122.3099 | -122.3831
2707.375 | 122.3831 | -0.054932 | 122.2092 | 0.18349 | 0.010269 | -0.0033647 | 0.015962 | 0.049687 | -0.012672 | 0.066262 | -0.022888 | 122.168 | -0.16479 | 0.086975 | 121.5546 | 3.0396 | 0.10529 | 0.33417 | 122.3145 | -0.19684 | -0.10986 | -0.041198 | 0.032044 | 0.14191 | -0.6546 | -0.14191 | 0.10529 | 0.14191 | 0.16022 | 0.3891 | 121.6095 | 122.2229 | 0.032044 | 122.3694 | 3.0945 | -0.14191 | 122.2229 | 0.032044 | 3.0945 | 121.6095 | 122.3694 | -122.374 | -122.406
2709.125 | 122.319 | -0.086975 | 122.2321 | -0.19798 | 0.010696 | -0.011269 | 0.01233 | 0.047337 | -0.014595 | 0.065834 | -0.027466 | 122.2229 | -0.1831 | 0.082397 | 121.5454 | 3.1677 | 0.54016 | 0.57678 | 122.3373 | -0.22888 | -0.09613 | -0.009156 | 0.059509 | 0.16937 | -0.68665 | -0.14191 | 0.10528 | 0.15564 | 0.62714 | 0.66376 | 121.6324 | 122.3099 | 0.059509 | 122.4243 | 3.2547 | -0.14191 | 122.3099 | 0.059509 | 3.2547 | 121.6324 | 122.4243 | -122.4152 | -122.4609
2710.8125 | 122.4014 | -0.050354 | 122.1909 | 0.16823 | 0.010055 | -0.0093461 | 0.014039 | 0.049687 | -0.012031 | 0.066262 | 0 | 122.2229 | -0.16022 | 0.10986 | 121.582 | 3.0624 | 0.10529 | 0.37994 | 122.319 | -0.18768 | -0.10986 | 0.032043 | 0.050354 | 0.16022 | -0.60883 | -0.13733 | 0.12817 | 0.16022 | 0.15564 | 0.4303 | 121.6324 | 122.2733 | 0.050354 | 122.3694 | 3.1128 | -0.13733 | 122.2733 | 0.050354 | 3.1128 | 121.6324 | 122.3694 | -122.3511 | -122.3785
2712.5625 | 122.2916 | -0.09613 | 122.2183 | -0.12932 | 0.012619 | -0.0076371 | 0.014253 | 0.048191 | -0.014381 | 0.066475 | -0.013733 | 122.2 | -0.16937 | 0.10071 | 121.5729 | 3.154 | 0.44861 | 0.55389 | 122.3602 | -0.2243 | -0.073243 | -0.018311 | 0.082397 | 0.19684 | -0.64545 | -0.12817 | 0.14191 | 0.15564 | 0.54474 | 0.65002 | 121.669 | 122.2961 | 0.082397 | 122.4564 | 3.2501 | -0.12817 | 122.2961 | 0.082397 | 3.2501 | 121.669 | 122.4564 | -122.3877 | -122.4426
2714.3125 | 122.3969 | -0.050354 | 122.2183 | 0.16823 | 0.011123 | -0.012978 | 0.012971 | 0.050114 | -0.014167 | 0.069466 | -0.027466 | 122.1725 | -0.16479 | 0.064087 | 121.5546 | 3.0167 | 0.15564 | 0.32501 | 122.3099 | -0.21057 | -0.11444 | -0.045777 | 0.022888 | 0.11444 | -0.66376 | -0.16022 | 0.091552 | 0.13733 | 0.20599 | 0.37537 | 121.6049 | 122.2229 | 0.022888 | 122.3602 | 3.067 | -0.16022 | 122.2229 | 0.022888 | 3.067 | 121.6049 | 122.3602 | -122.3831 | -122.4289
2716 | 122.3145 | -0.082397 | 122.2275 | -0.17509 | 0.0094144 | -0.0087051 | 0.011476 | 0.049259 | -0.012672 | 0.066048 | -0.050354 | 122.2275 | -0.17395 | 0.064087 | 121.5408 | 3.154 | 0.54474 | 0.5722 | 122.3465 | -0.22888 | -0.091553 | 0 | 0.032043 | 0.14648 | -0.68664 | -0.14649 | 0.11902 | 0.1236 | 0.62714 | 0.6546 | 121.6232 | 122.3099 | 0.032043 | 122.4289 | 3.2364 | -0.14649 | 122.3099 | 0.032043 | 3.2364 | 121.6232 | 122.4289 | -122.4014 | -122.4564
2717.75 | 122.3694 | -0.082397 | 122.2 | 0.16823 | 0.0087734 | -0.0091325 | 0.0093396 | 0.048619 | -0.012458 | 0.065621 | 0.059509 | 122.2092 | -0.13275 | 0.13733 | 121.6278 | 3.1036 | 0.073242 | 0.42114 | 122.3007 | -0.17853 | -0.050354 | 0.009155 | 0.14191 | 0.21973 | -0.5722 | -0.096131 | 0.10071 | 0.19226 | 0.15564 | 0.50354 | 121.7102 | 122.2916 | 0.14191 | 122.3831 | 3.186 | -0.096131 | 122.2916 | 0.14191 | 3.186 | 121.7102 | 122.3831 | -122.3328 | -122.3785
2719.4531 | 122.3785 | -0.064087 | 122.1954 | 0.14534 | 0.0098416 | -0.0055009 | 0.012117 | 0.049259 | -0.010322 | 0.065834 | 0.064087 | 122.2229 | -0.12817 | 0.14191 | 121.6095 | 3.0899 | 0.059509 | 0.40283 | 122.2916 | -0.20599 | -0.064087 | 0.027465 | 0.12817 | 0.20599 | -0.58594 | -0.14191 | 0.09613 | 0.19226 | 0.1236 | 0.46692 | 121.6736 | 122.287 | 0.12817 | 122.3557 | 3.154 | -0.14191 | 122.287 | 0.12817 | 3.154 | 121.6736 | 122.3557 | -122.3236 | -122.4014
2721.2188 | 122.3328 | -0.10986 | 122.2412 | -0.26665 | 0.009628 | -0.0076371 | 0.0076306 | 0.04691 | -0.012886 | 0.06498 | 0.022888 | 122.2137 | -0.14191 | 0.09613 | 121.582 | 3.2181 | 0.55847 | 0.68665 | 122.3831 | -0.20142 | -0.032044 | -0.027466 | 0.13275 | 0.20599 | -0.65918 | -0.091553 | 0.14191 | 0.16479 | 0.66834 | 0.79651 | 121.6919 | 122.3236 | 0.13275 | 122.493 | 3.3279 | -0.091553 | 122.3236 | 0.13275 | 3.3279 | 121.6919 | 122.493 | -122.3831 | -122.4426
2722.9688 | 122.4289 | -0.073242 | 122.2046 | -0.0072479 | 0.0098416 | -0.0076371 | 0.009126 | 0.047337 | -0.0096814 | 0.066475 | -0.004578 | 122.2 | -0.15106 | 0.091553 | 121.5683 | 3.0991 | 0.31128 | 0.50354 | 122.3145 | -0.18768 | -0.07782 | -0.004578 | 0.068664 | 0.16479 | -0.63629 | -0.11444 | 0.10986 | 0.14648 | 0.38452 | 0.57678 | 121.6415 | 122.2733 | 0.068664 | 122.3877 | 3.1723 | -0.11444 | 122.2733 | 0.068664 | 3.1723 | 121.6415 | 122.3877 | -122.3557 | -122.3923
2724.7344 | 122.374 | -0.059509 | 122.1863 | 0.038529 | 0.011978 | -0.0087051 | 0.013612 | 0.04755 | -0.013099 | 0.06733 | 0.036621 | 122.1909 | -0.14648 | 0.15106 | 121.6049 | 3.0991 | 0.068665 | 0.40283 | 122.2961 | -0.20142 | -0.086975 | 0.004578 | 0.09613 | 0.21057 | -0.58136 | -0.14191 | 0.10986 | 0.18311 | 0.12817 | 0.46234 | 121.6644 | 122.2504 | 0.09613 | 122.3557 | 3.1586 | -0.14191 | 122.2504 | 0.09613 | 3.1586 | 121.6644 | 122.3557 | -122.3328 | -122.3877
2726.4375 | 122.3373 | -0.10071 | 122.2412 | -0.26665 | 0.01091 | -0.011269 | 0.010408 | 0.04755 | -0.01075 | 0.065621 | 0.013733 | 122.2092 | -0.13733 | 0.10986 | 121.5912 | 3.2135 | 0.56305 | 0.6958 | 122.3694 | -0.21057 | -0.036621 | -0.032044 | 0.11444 | 0.21057 | -0.65002 | -0.10986 | 0.12817 | 0.15106 | 0.66376 | 0.79651 | 121.6919 | 122.3099 | 0.11444 | 122.4701 | 3.3142 | -0.10986 | 122.3099 | 0.11444 | 3.3142 | 121.6919 | 122.4701 | -122.3785 | -122.4518
2728.1875 | 122.4701 | -0.068665 | 122.2092 | 0.01564 | 0.0083462 | -0.0055009 | 0.0099804 | 0.047764 | -0.012458 | 0.066262 | 0.004578 | 122.2137 | -0.1236 | 0.09613 | 121.5637 | 3.1036 | 0.29297 | 0.48981 | 122.3236 | -0.21057 | -0.054931 | 0.004578 | 0.073243 | 0.16479 | -0.64545 | -0.14191 | 0.11444 | 0.12817 | 0.36163 | 0.55847 | 121.6324 | 122.2824 | 0.073243 | 122.3923 | 3.1723 | -0.14191 | 122.2824 | 0.073243 | 3.1723 | 121.6324 | 122.3923 | -122.3328 | -122.4197
2729.9531 | 122.4518 | -0.073242 | 122.2229 | 0.00038159 | 0.0077054 | -0.010414 | 0.0067762 | 0.047337 | -0.012245 | 0.06733 | -0.032043 | 122.1405 | -0.14648 | 0.091553 | 121.5729 | 3.0945 | 0.28839 | 0.48981 | 122.319 | -0.17853 | -0.073242 | -0.082397 | 0.041199 | 0.16479 | -0.65002 | -0.10529 | 0.096131 | 0.11444 | 0.36163 | 0.56305 | 121.6461 | 122.2137 | 0.041199 | 122.3923 | 3.1677 | -0.10529 | 122.2137 | 0.041199 | 3.1677 | 121.6461 | 122.3923 | -122.3694 | -122.4014
2731.7188 | 122.3007 | -0.09613 | 122.2412 | -0.17509 | 0.007919 | -0.011482 | 0.011262 | 0.04691 | -0.011177 | 0.066689 | 0.07782 | 122.2 | -0.13733 | 0.17853 | 121.637 | 3.2639 | 0.41657 | 0.737 | 122.3419 | -0.18768 | -0.041199 | -0.041199 | 0.17395 | 0.27466 | -0.60425 | -0.091553 | 0.10071 | 0.21515 | 0.5127 | 0.83313 | 121.7331 | 122.2961 | 0.17395 | 122.438 | 3.36 | -0.091553 | 122.2961 | 0.17395 | 3.36 | 121.7331 | 122.438 | -122.3785 | -122.4289
2733.4062 | 122.4197 | -0.068665 | 122.1817 | 0.084305 | 0.011337 | -0.013405 | 0.01233 | 0.049473 | -0.01139 | 0.06733 | 0.027466 | 122.1909 | -0.13733 | 0.10529 | 121.5866 | 3.0899 | 0.19684 | 0.45319 | 122.3236 | -0.19684 | -0.068664 | 0.009155 | 0.096131 | 0.17395 | -0.59509 | -0.12817 | 0.14191 | 0.16479 | 0.2655 | 0.52185 | 121.6553 | 122.2595 | 0.096131 | 122.3923 | 3.1586 | -0.12817 | 122.2595 | 0.096131 | 3.1586 | 121.6553 | 122.3923 | -122.319 | -122.3785
2735.1562 | 122.3053 | -0.10986 | 122.2458 | -0.17509 | 0.010696 | -0.011696 | 0.010621 | 0.045201 | -0.011177 | 0.063057 | 0.045776 | 122.1817 | -0.14648 | 0.16022 | 121.6095 | 3.2684 | 0.45776 | 0.74616 | 122.3145 | -0.19226 | -0.036621 | -0.064087 | 0.15564 | 0.27008 | -0.63629 | -0.082398 | 0.068664 | 0.19226 | 0.56763 | 0.85602 | 121.7194 | 122.2916 | 0.15564 | 122.4243 | 3.3783 | -0.082398 | 122.2916 | 0.15564 | 3.3783 | 121.7194 | 122.4243 | -122.3923 | -122.4381
2736.9062 | 122.3282 | -0.09613 | 122.2595 | -0.2285 | 0.0094144 | -0.013405 | 0.011689 | 0.047337 | -0.01374 | 0.066262 | 0.045776 | 122.2321 | -0.15564 | 0.11444 | 121.5912 | 3.2364 | 0.54474 | 0.70953 | 122.3373 | -0.21057 | -0.05951 | -0.027465 | 0.14191 | 0.21057 | -0.66833 | -0.11444 | 0.07782 | 0.20142 | 0.64087 | 0.80566 | 121.6873 | 122.3282 | 0.14191 | 122.4335 | 3.3325 | -0.11444 | 122.3282 | 0.14191 | 3.3325 | 121.6873 | 122.4335 | -122.4152 | -122.4701
2738.6562 | 122.3465 | -0.10071 | 122.2183 | -0.2285 | 0.0098416 | -0.0099869 | 0.012971 | 0.047123 | -0.011818 | 0.066689 | -0.027466 | 122.2092 | -0.17395 | 0.073242 | 121.5546 | 3.1906 | 0.58136 | 0.63171 | 122.3831 | -0.23346 | -0.073242 | -0.009156 | 0.073242 | 0.17395 | -0.66376 | -0.13275 | 0.16479 | 0.14648 | 0.68207 | 0.73242 | 121.6553 | 122.3099 | 0.073242 | 122.4838 | 3.2913 | -0.13275 | 122.3099 | 0.073242 | 3.2913 | 121.6553 | 122.4838 | -122.3923 | -122.4518
2740.3438 | 122.3602 | -0.086975 | 122.1863 | 0.038529 | 0.009628 | -0.010628 | 0.018525 | 0.049259 | -0.01374 | 0.067116 | -0.041199 | 122.2275 | -0.17395 | 0.032043 | 121.5088 | 3.0441 | 0.31128 | 0.33417 | 122.374 | -0.20599 | -0.086975 | 0.041199 | 0.045776 | 0.11902 | -0.67749 | -0.11902 | 0.18768 | 0.13275 | 0.39825 | 0.42114 | 121.5958 | 122.3145 | 0.045776 | 122.4609 | 3.1311 | -0.11902 | 122.3145 | 0.045776 | 3.1311 | 121.5958 | 122.4609 | -122.3602 | -122.3923
2742.1094 | 122.4472 | -0.054932 | 122.1771 | 0.038529 | 0.011337 | -0.01255 | 0.0099804 | 0.04755 | -0.011818 | 0.064339 | 0.018311 | 122.2137 | -0.13275 | 0.086975 | 121.582 | 3.0945 | 0.24261 | 0.4715 | 122.3053 | -0.19684 | -0.077819 | 0.036621 | 0.073243 | 0.14191 | -0.59509 | -0.14191 | 0.12817 | 0.15106 | 0.29755 | 0.52643 | 121.637 | 122.2687 | 0.073243 | 122.3602 | 3.1494 | -0.14191 | 122.2687 | 0.073243 | 3.1494 | 121.637 | 122.3602 | -122.3099 | -122.374
2743.8594 | 122.3877 | -0.064087 | 122.2092 | 0.16823 | 0.011551 | -0.011055 | 0.015107 | 0.049687 | -0.013527 | 0.067116 | -0.013733 | 122.1909 | -0.16479 | 0.10071 | 121.5637 | 3.0579 | 0.1236 | 0.32501 | 122.3602 | -0.20142 | -0.10071 | -0.01831 | 0.050354 | 0.1648 | -0.64545 | -0.13733 | 0.15106 | 0.15106 | 0.18768 | 0.3891 | 121.6278 | 122.2549 | 0.050354 | 122.4243 | 3.1219 | -0.13733 | 122.2549 | 0.050354 | 3.1219 | 121.6278 | 122.4243 | -122.374 | -122.4106
2745.625 | 122.3419 | -0.091553 | 122.2595 | -0.25139 | 0.0083462 | -0.0093461 | 0.0095532 | 0.047123 | -0.012886 | 0.066475 | 0.004578 | 122.2321 | -0.14191 | 0.086975 | 121.5637 | 3.2135 | 0.5722 | 0.65002 | 122.3465 | -0.22888 | -0.050354 | -0.027465 | 0.096131 | 0.17853 | -0.6958 | -0.13733 | 0.086976 | 0.14649 | 0.66376 | 0.74158 | 121.6553 | 122.3236 | 0.096131 | 122.4381 | 3.3051 | -0.13733 | 122.3236 | 0.096131 | 3.3051 | 121.6553 | 122.4381 | -122.4014 | -122.4884
2747.3125 | 122.319 | -0.10529 | 122.2595 | -0.18272 | 0.010482 | -0.0087051 | 0.013826 | 0.050755 | -0.013954 | 0.063912 | -0.041199 | 122.2458 | -0.17395 | 0.091553 | 121.55 | 3.2043 | 0.50812 | 0.58136 | 122.3557 | -0.21973 | -0.068664 | -0.013732 | 0.064087 | 0.19684 | -0.70953 | -0.11444 | 0.096131 | 0.13275 | 0.6134 | 0.68665 | 121.6553 | 122.3511 | 0.064087 | 122.4609 | 3.3096 | -0.11444 | 122.3511 | 0.064087 | 3.3096 | 121.6553 | 122.4609 | -122.4335 | -122.4792
2749.0781 | 122.3511 | -0.086975 | 122.2183 | -0.25139 | 0.010269 | -0.0093461 | 0.011689 | 0.048832 | -0.015663 | 0.06498 | -0.068665 | 122.2275 | -0.17395 | 0.045776 | 121.5408 | 3.1769 | 0.62714 | 0.59509 | 122.3877 | -0.22888 | -0.086975 | 0.009155 | 0.01831 | 0.13275 | -0.67749 | -0.14191 | 0.16937 | 0.10528 | 0.71411 | 0.68207 | 121.6278 | 122.3145 | 0.01831 | 122.4747 | 3.2639 | -0.14191 | 122.3145 | 0.01831 | 3.2639 | 121.6278 | 122.4747 | -122.3923 | -122.4472
2750.8438 | 122.438 | -0.045776 | 122.1909 | 0.10719 | 0.007919 | -0.0091325 | 0.012758 | 0.050114 | -0.01374 | 0.065193 | -0.027466 | 122.2412 | -0.17853 | 0.050354 | 121.5271 | 3.035 | 0.20599 | 0.28381 | 122.3785 | -0.2243 | -0.13275 | 0.050354 | 0.01831 | 0.09613 | -0.66376 | -0.17853 | 0.18768 | 0.15106 | 0.25177 | 0.32959 | 121.5729 | 122.287 | 0.01831 | 122.4243 | 3.0807 | -0.17853 | 122.287 | 0.01831 | 3.0807 | 121.5729 | 122.4243 | -122.3694 | -122.4152
2752.5312 | 122.3694 | -0.073242 | 122.2046 | 0.16823 | 0.009628 | -0.0072099 | 0.009126 | 0.047978 | -0.013954 | 0.067543 | 0.050354 | 122.1909 | -0.14191 | 0.15564 | 121.637 | 3.1311 | 0.064087 | 0.42572 | 122.3099 | -0.1831 | -0.068665 | -0.013733 | 0.1236 | 0.22888 | -0.56763 | -0.10986 | 0.10529 | 0.19226 | 0.13733 | 0.49896 | 121.7102 | 122.2641 | 0.1236 | 122.3831 | 3.2043 | -0.10986 | 122.2641 | 0.1236 | 3.2043 | 121.7102 | 122.3831 | -122.3465 | -122.3877
2754.2812 | 122.3145 | -0.09613 | 122.2275 | -0.091171 | 0.011337 | -0.010628 | 0.014039 | 0.052464 | -0.015022 | 0.065621 | 0.013733 | 122.1863 | -0.16937 | 0.10529 | 121.5729 | 3.1952 | 0.37537 | 0.49896 | 122.3648 | -0.19684 | -0.073243 | -0.041199 | 0.10986 | 0.20142 | -0.6546 | -0.10071 | 0.13733 | 0.18311 | 0.4715 | 0.59509 | 121.669 | 122.2824 | 0.10986 | 122.4609 | 3.2913 | -0.10071 | 122.2824 | 0.10986 | 3.2913 | 121.669 | 122.4609 | -122.3969 | -122.4243
2755.9844 | 122.3007 | -0.10071 | 122.2366 | -0.16747 | 0.011551 | -0.0093461 | 0.013398 | 0.051396 | -0.012672 | 0.065407 | -0.013733 | 122.2275 | -0.18768 | 0.086975 | 121.5637 | 3.2089 | 0.48523 | 0.58136 | 122.374 | -0.21057 | -0.086975 | -0.009155 | 0.086975 | 0.18768 | -0.67291 | -0.10986 | 0.13733 | 0.17395 | 0.58594 | 0.68207 | 121.6644 | 122.3282 | 0.086975 | 122.4747 | 3.3096 | -0.10986 | 122.3282 | 0.086975 | 3.3096 | 121.6644 | 122.4747 | -122.4243 | -122.4472
2757.7344 | 122.3099 | -0.1236 | 122.2 | -0.15984 | 0.010482 | -0.013618 | 0.0063488 | 0.047123 | -0.011818 | 0.065834 | 0.050354 | 122.2092 | -0.1236 | 0.14648 | 121.6644 | 3.3051 | 0.44403 | 0.74616 | 122.3053 | -0.19226 | 0 | 0.009155 | 0.17395 | 0.27008 | -0.53558 | -0.068665 | 0.10529 | 0.17395 | 0.56763 | 0.86975 | 121.788 | 122.3328 | 0.17395 | 122.4289 | 3.4287 | -0.068665 | 122.3328 | 0.17395 | 3.4287 | 121.788 | 122.4289 | -122.3236 | -122.3923
2759.4219 | 122.4197 | -0.059509 | 122.2092 | 0.0080111 | 0.011551 | -0.0069961 | 0.0097668 | 0.047764 | -0.0096814 | 0.066475 | -0.013733 | 122.2 | -0.13733 | 0.082397 | 121.5866 | 3.1357 | 0.32501 | 0.52643 | 122.3145 | -0.1831 | -0.07782 | -0.009155 | 0.045776 | 0.14191 | -0.62256 | -0.1236 | 0.10529 | 0.1236 | 0.38452 | 0.58594 | 121.6461 | 122.2595 | 0.045776 | 122.374 | 3.1952 | -0.1236 | 122.2595 | 0.045776 | 3.1952 | 121.6461 | 122.374 | -122.3465 | -122.3923
2761.1875 | 122.3236 | -0.086975 | 122.2229 | -0.15221 | 0.009628 | -0.0097733 | 0.013185 | 0.050968 | -0.013313 | 0.063912 | -0.041199 | 122.2183 | -0.17853 | 0.068665 | 121.5454 | 3.2043 | 0.56763 | 0.5722 | 122.4106 | -0.2243 | -0.091553 | -0.004577 | 0.045776 | 0.15564 | -0.67749 | -0.13733 | 0.18768 | 0.13733 | 0.6546 | 0.65918 | 121.6324 | 122.3053 | 0.045776 | 122.4976 | 3.2913 | -0.13733 | 122.3053 | 0.045776 | 3.2913 | 121.6324 | 122.4976 | -122.4014 | -122.4472
2762.9375 | 122.4243 | -0.054932 | 122.2092 | 0.12245 | 0.009628 | -0.0080643 | 0.015107 | 0.048619 | -0.011818 | 0.06797 | -0.036621 | 122.2275 | -0.17395 | 0.041199 | 121.5408 | 3.0441 | 0.1831 | 0.3067 | 122.3694 | -0.20599 | -0.11902 | 0.018311 | 0.018311 | 0.096131 | -0.66833 | -0.15106 | 0.16022 | 0.13733 | 0.23804 | 0.36163 | 121.5958 | 122.2824 | 0.018311 | 122.4243 | 3.0991 | -0.15106 | 122.2824 | 0.018311 | 3.0991 | 121.5958 | 122.4243 | -122.3831 | -122.4152
2764.6875 | 122.4289 | -0.054932 | 122.1909 | 0.10719 | 0.01091 | -0.013191 | 0.01233 | 0.050755 | -0.012672 | 0.068184 | -0.064087 | 122.2275 | -0.19684 | 0.022888 | 121.5088 | 3.0487 | 0.23346 | 0.27924 | 122.4014 | -0.21515 | -0.14191 | 0.036621 | -0.009155 | 0.07782 | -0.68207 | -0.16022 | 0.21057 | 0.13275 | 0.28839 | 0.33417 | 121.5637 | 122.2824 | -0.009155 | 122.4564 | 3.1036 | -0.16022 | 122.2824 | -0.009155 | 3.1036 | 121.5637 | 122.4564 | -122.3877 | -122.406
2766.375 | 122.438 | -0.064087 | 122.1954 | 0.061417 | 0.0085598 | -0.011269 | 0.0052808 | 0.047764 | -0.012245 | 0.066475 | 0.004578 | 122.1771 | -0.14191 | 0.091553 | 121.6003 | 3.1219 | 0.23346 | 0.46692 | 122.3373 | -0.18768 | -0.07782 | -0.018311 | 0.068665 | 0.15564 | -0.59509 | -0.1236 | 0.14191 | 0.14649 | 0.29755 | 0.53101 | 121.6644 | 122.2412 | 0.068665 | 122.4014 | 3.186 | -0.1236 | 122.2412 | 0.068665 | 3.186 | 121.6644 | 122.4014 | -122.3373 | -122.3831
2768.125 | 122.406 | -0.059509 | 122.2046 | 0.13008 | 0.009628 | -0.0072099 | 0.010835 | 0.049687 | -0.012031 | 0.066902 | 0.036621 | 122.1771 | -0.1236 | 0.12817 | 121.582 | 3.1311 | 0.16937 | 0.45319 | 122.3328 | -0.19684 | -0.064087 | -0.027466 | 0.09613 | 0.18768 | -0.62256 | -0.13733 | 0.12817 | 0.16022 | 0.22888 | 0.5127 | 121.6415 | 122.2366 | 0.09613 | 122.3923 | 3.1906 | -0.13733 | 122.2366 | 0.09613 | 3.1906 | 121.6415 | 122.3923 | -122.3282 | -122.4014
2769.8125 | 122.3511 | -0.091553 | 122.2504 | -0.25139 | 0.0089872 | -0.014259 | 0.013612 | 0.046055 | -0.013954 | 0.065193 | -0.009155 | 122.2412 | -0.14191 | 0.07782 | 121.55 | 3.2364 | 0.59509 | 0.64545 | 122.3511 | -0.22888 | -0.050354 | -0.009155 | 0.082398 | 0.16937 | -0.70038 | -0.13733 | 0.10071 | 0.13275 | 0.68665 | 0.737 | 121.6415 | 122.3328 | 0.082398 | 122.4426 | 3.3279 | -0.13733 | 122.3328 | 0.082398 | 3.3279 | 121.6415 | 122.4426 | -122.3923 | -122.4792
2771.5625 | 122.3694 | -0.068665 | 122.2137 | 0.02327 | 0.0085598 | -0.010841 | 0.015107 | 0.0499 | -0.013313 | 0.066902 | -0.045776 | 122.2046 | -0.1831 | 0.045776 | 121.5088 | 3.0853 | 0.32959 | 0.33417 | 122.3648 | -0.21973 | -0.11444 | -0.009155 | 0.022889 | 0.11444 | -0.70496 | -0.15106 | 0.15106 | 0.13733 | 0.39826 | 0.40283 | 121.5775 | 122.2733 | 0.022889 | 122.4335 | 3.154 | -0.15106 | 122.2733 | 0.022889 | 3.154 | 121.5775 | 122.4335 | -122.3969 | -122.4335
2773.25 | 122.3785 | -0.073242 | 122.2092 | 0.16823 | 0.010269 | -0.0091325 | 0.011903 | 0.048619 | -0.011818 | 0.066048 | 0.022888 | 122.2183 | -0.15106 | 0.12817 | 121.6095 | 3.1219 | 0.10529 | 0.39825 | 122.3236 | -0.19684 | -0.07782 | 0.009156 | 0.09613 | 0.20142 | -0.59967 | -0.1236 | 0.11444 | 0.17395 | 0.17853 | 0.4715 | 121.6827 | 122.2916 | 0.09613 | 122.3968 | 3.1952 | -0.1236 | 122.2916 | 0.09613 | 3.1952 | 121.6827 | 122.3968 | -122.3602 | -122.406
2775 | 122.406 | -0.064087 | 122.1863 | 0.15297 | 0.01091 | -0.012337 | 0.012117 | 0.050755 | -0.014595 | 0.066475 | -0.032043 | 122.2137 | -0.16022 | 0.068665 | 121.55 | 3.0579 | 0.15106 | 0.32959 | 122.3373 | -0.21515 | -0.09613 | 0.027466 | 0.032044 | 0.13275 | -0.63629 | -0.15106 | 0.15106 | 0.12817 | 0.21515 | 0.39368 | 121.6141 | 122.2778 | 0.032044 | 122.4014 | 3.1219 | -0.15106 | 122.2778 | 0.032044 | 3.1219 | 121.6141 | 122.4014 | -122.3465 | -122.4014
2776.7656 | 122.4243 | -0.068665 | 122.1909 | 0.099564 | 0.0085598 | -0.0076371 | 0.0086988 | 0.049473 | -0.010109 | 0.066689 | 0.045776 | 122.2412 | -0.13733 | 0.13275 | 121.5912 | 3.1311 | 0.14648 | 0.44403 | 122.3099 | -0.20599 | -0.068664 | 0.050354 | 0.11444 | 0.20142 | -0.59967 | -0.13733 | 0.11902 | 0.18311 | 0.21515 | 0.5127 | 121.6599 | 122.3099 | 0.11444 | 122.3785 | 3.1998 | -0.13733 | 122.3099 | 0.11444 | 3.1998 | 121.6599 | 122.3785 | -122.3282 | -122.3969
2778.4531 | 122.3785 | -0.054932 | 122.2046 | 0.1606 | 0.011764 | -0.011482 | 0.012117 | 0.049046 | -0.010322 | 0.067543 | 0.059509 | 122.2092 | -0.1236 | 0.15106 | 121.6187 | 3.154 | 0.064087 | 0.43945 | 122.3145 | -0.18768 | -0.068664 | 0.004577 | 0.11444 | 0.20599 | -0.58594 | -0.13275 | 0.10986 | 0.1831 | 0.11902 | 0.49438 | 121.6736 | 122.2641 | 0.11444 | 122.3694 | 3.2089 | -0.13275 | 122.2641 | 0.11444 | 3.2089 | 121.6736 | 122.3694 | -122.3282 | -122.3923
2780.2031 | 122.3877 | -0.068665 | 122.2092 | 0.1606 | 0.01091 | -0.014473 | 0.011476 | 0.0499 | -0.01139 | 0.066475 | 0.054932 | 122.1771 | -0.13275 | 0.14191 | 121.6187 | 3.154 | 0.09613 | 0.4303 | 122.3465 | -0.17853 | -0.064086 | -0.032043 | 0.1236 | 0.21057 | -0.59051 | -0.10986 | 0.13733 | 0.18768 | 0.16479 | 0.49896 | 121.6873 | 122.2458 | 0.1236 | 122.4152 | 3.2227 | -0.10986 | 122.2458 | 0.1236 | 3.2227 | 121.6873 | 122.4152 | -122.3419 | -122.3877
2781.9688 | 122.3602 | -0.086975 | 122.2137 | -0.24376 | 0.010696 | -0.010414 | 0.011476 | 0.048405 | -0.015876 | 0.064766 | -0.064087 | 122.2275 | -0.1831 | 0.045776 | 121.5042 | 3.1906 | 0.63171 | 0.59509 | 122.3923 | -0.23804 | -0.09613 | 0.013733 | 0.022888 | 0.13275 | -0.70953 | -0.15106 | 0.17853 | 0.11902 | 0.71869 | 0.68207 | 121.5912 | 122.3145 | 0.022888 | 122.4792 | 3.2776 | -0.15106 | 122.3145 | 0.022888 | 3.2776 | 121.5912 | 122.4792 | -122.3969 | -122.4518
2783.7344 | 122.4289 | -0.050354 | 122.2092 | 0.12245 | 0.012405 | -0.013618 | 0.013398 | 0.049259 | -0.013527 | 0.068611 | -0.050354 | 122.2092 | -0.17395 | 0.041199 | 121.5317 | 3.067 | 0.17853 | 0.30212 | 122.3831 | -0.21057 | -0.1236 | 0 | 0 | 0.091553 | -0.67749 | -0.16022 | 0.17395 | 0.1236 | 0.22888 | 0.35248 | 121.582 | 122.2595 | 0 | 122.4335 | 3.1174 | -0.16022 | 122.2595 | 0 | 3.1174 | 121.582 | 122.4335 | -122.3831 | -122.4197
2785.4219 | 122.3328 | -0.07782 | 122.2366 | 0.0080111 | 0.0098416 | -0.0102 | 0.014039 | 0.050968 | -0.013313 | 0.06797 | -0.009155 | 122.2092 | -0.17395 | 0.045776 | 121.5134 | 3.1219 | 0.32501 | 0.38452 | 122.3923 | -0.2243 | -0.09613 | -0.027466 | 0.068665 | 0.1236 | -0.72327 | -0.14648 | 0.15564 | 0.16479 | 0.40283 | 0.46234 | 121.5912 | 122.287 | 0.068665 | 122.4701 | 3.1998 | -0.14648 | 122.287 | 0.068665 | 3.1998 | 121.5912 | 122.4701 | -122.4106 | -122.4609
2787.1875 | 122.3145 | -0.1236 | 122.2275 | -0.16747 | 0.009628 | -0.015541 | 0.0061352 | 0.047123 | -0.01075 | 0.066689 | 0.064087 | 122.2092 | -0.1236 | 0.15106 | 121.6599 | 3.3005 | 0.42572 | 0.74158 | 122.3145 | -0.20142 | 0 | -0.018311 | 0.18768 | 0.27466 | -0.56763 | -0.07782 | 0.086975 | 0.18768 | 0.54932 | 0.86517 | 121.7834 | 122.3328 | 0.18768 | 122.438 | 3.4241 | -0.07782 | 122.3328 | 0.18768 | 3.4241 | 121.7834 | 122.438 | -122.3511 | -122.4289
2788.875 | 122.3236 | -0.10071 | 122.2137 | -0.17509 | 0.0092008 | -0.0093461 | 0.015107 | 0.048832 | -0.01374 | 0.065193 | -0.059509 | 122.2321 | -0.21057 | 0.064087 | 121.55 | 3.2135 | 0.56305 | 0.57678 | 122.3831 | -0.21057 | -0.10986 | 0.018311 | 0.041199 | 0.1648 | -0.66376 | -0.10986 | 0.16937 | 0.15106 | 0.66376 | 0.67749 | 121.6507 | 122.3328 | 0.041199 | 122.4838 | 3.3142 | -0.10986 | 122.3328 | 0.041199 | 3.3142 | 121.6507 | 122.4838 | -122.4243 | -122.4243
2790.625 | 122.3923 | -0.059509 | 122.2137 | 0.061417 | 0.014541 | -0.0057145 | 0.014894 | 0.050328 | -0.013313 | 0.064553 | -0.041199 | 122.2275 | -0.19226 | 0.022888 | 121.5088 | 3.0853 | 0.32501 | 0.33417 | 122.3969 | -0.20142 | -0.13275 | 0.013733 | 0.01831 | 0.082397 | -0.70496 | -0.14191 | 0.18311 | 0.15106 | 0.38452 | 0.39368 | 121.5683 | 122.287 | 0.01831 | 122.4564 | 3.1448 | -0.14191 | 122.287 | 0.01831 | 3.1448 | 121.5683 | 122.4564 | -122.406 | -122.4152
2792.3125 | 122.4197 | -0.064087 | 122.2275 | 0.11482 | 0.012619 | -0.012123 | 0.0080578 | 0.048191 | -0.011818 | 0.066689 | 0.018311 | 122.2092 | -0.13275 | 0.10071 | 121.582 | 3.1403 | 0.21057 | 0.44403 | 122.3328 | -0.20142 | -0.068664 | -0.018311 | 0.082398 | 0.1648 | -0.64545 | -0.13733 | 0.10529 | 0.15106 | 0.27466 | 0.50812 | 121.6461 | 122.2733 | 0.082398 | 122.3969 | 3.2043 | -0.13733 | 122.2733 | 0.082398 | 3.2043 | 121.6461 | 122.3969 | -122.3602 | -122.4289
2794.0625 | 122.3923 | -0.064087 | 122.2183 | -0.098801 | 0.010696 | -0.012337 | 0.008485 | 0.042423 | -0.010963 | 0.064766 | 0.027466 | 122.2275 | -0.13733 | 0.11444 | 121.6278 | 3.2593 | 0.37079 | 0.65918 | 122.3465 | -0.17853 | -0.073242 | 0.009155 | 0.091553 | 0.17853 | -0.59051 | -0.11444 | 0.12817 | 0.16479 | 0.43488 | 0.72327 | 121.6919 | 122.2916 | 0.091553 | 122.4106 | 3.3234 | -0.11444 | 122.2916 | 0.091553 | 3.3234 | 121.6919 | 122.4106 | -122.3557 | -122.3969
2795.8125 | 122.438 | -0.059509 | 122.1817 | -0.037765 | 0.0092008 | -0.011909 | 0.0082714 | 0.047337 | -0.010536 | 0.066048 | 0.004578 | 122.2229 | -0.12817 | 0.10986 | 121.6049 | 3.1998 | 0.34332 | 0.59509 | 122.374 | -0.19684 | -0.068665 | 0.041198 | 0.064087 | 0.16937 | -0.57678 | -0.13733 | 0.19226 | 0.13275 | 0.40283 | 0.6546 | 121.6644 | 122.2824 | 0.064087 | 122.4335 | 3.2593 | -0.13733 | 122.2824 | 0.064087 | 3.2593 | 121.6644 | 122.4335 | -122.3099 | -122.3785
2797.5 | 122.3373 | -0.09613 | 122.2229 | -0.13695 | 0.0087734 | -0.0089189 | 0.010408 | 0.047337 | -0.010963 | 0.064339 | 0.064087 | 122.1954 | -0.16479 | 0.16937 | 121.669 | 3.3005 | 0.37079 | 0.737 | 122.3465 | -0.18768 | -0.068665 | -0.027465 | 0.16022 | 0.2655 | -0.55389 | -0.091553 | 0.1236 | 0.22888 | 0.46692 | 0.83313 | 121.7651 | 122.2916 | 0.16022 | 122.4426 | 3.3966 | -0.091553 | 122.2916 | 0.16022 | 3.3966 | 121.7651 | 122.4426 | -122.3877 | -122.4106
2799.2656 | 122.3419 | -0.073242 | 122.2321 | -0.053024 | 0.010055 | -0.0084915 | 0.017884 | 0.048405 | -0.01374 | 0.067116 | 0.004578 | 122.2183 | -0.1831 | 0.10986 | 121.5408 | 3.1677 | 0.35706 | 0.45776 | 122.374 | -0.20142 | -0.10986 | -0.013733 | 0.07782 | 0.18311 | -0.69122 | -0.12817 | 0.14191 | 0.18768 | 0.4303 | 0.53101 | 121.6141 | 122.2916 | 0.07782 | 122.4472 | 3.241 | -0.12817 | 122.2916 | 0.07782 | 3.241 | 121.6141 | 122.4472 | -122.4152 | -122.4335
2801.0312 | 122.3007 | -0.10986 | 122.2321 | -0.18272 | 0.0094144 | -0.0072099 | 0.008485 | 0.046482 | -0.012886 | 0.066902 | 0.050354 | 122.2046 | -0.13733 | 0.16022 | 121.637 | 3.3325 | 0.45319 | 0.75531 | 122.3511 | -0.17853 | -0.027466 | -0.027466 | 0.16022 | 0.27008 | -0.59509 | -0.068665 | 0.11902 | 0.18768 | 0.56305 | 0.86517 | 121.7468 | 122.3145 | 0.16022 | 122.4609 | 3.4424 | -0.068665 | 122.3145 | 0.16022 | 3.4424 | 121.7468 | 122.4609 | -122.3694 | -122.4106
2802.7812 | 122.3511 | -0.086975 | 122.2229 | -0.12169 | 0.0092008 | -0.011055 | 0.008485 | 0.048832 | -0.0092542 | 0.065193 | 0.050354 | 122.168 | -0.1236 | 0.16479 | 121.6507 | 3.3051 | 0.37079 | 0.72327 | 122.3145 | -0.19226 | -0.036621 | -0.054931 | 0.13733 | 0.25177 | -0.5722 | -0.10529 | 0.091553 | 0.17395 | 0.45776 | 0.81024 | 121.7377 | 122.2549 | 0.13733 | 122.4014 | 3.392 | -0.10529 | 122.2549 | 0.13733 | 3.392 | 121.7377 | 122.4014 | -122.3465 | -122.4152
2804.5312 | 122.3465 | -0.086975 | 122.2641 | -0.25139 | 0.010269 | -0.013191 | 0.013398 | 0.047337 | -0.014808 | 0.064766 | -0.018311 | 122.2229 | -0.16022 | 0.068665 | 121.5591 | 3.2501 | 0.59967 | 0.65002 | 122.3785 | -0.21515 | -0.073242 | -0.041199 | 0.068664 | 0.15564 | -0.70496 | -0.12817 | 0.11444 | 0.14191 | 0.68665 | 0.737 | 121.6461 | 122.3099 | 0.068664 | 122.4655 | 3.3371 | -0.12817 | 122.3099 | 0.068664 | 3.3371 | 121.6461 | 122.4655 | -122.4243 | -122.4792
2806.2969 | 122.4152 | -0.054932 | 122.1954 | 0.076676 | 0.011123 | -0.0095597 | 0.014039 | 0.050114 | -0.015236 | 0.067116 | -0.07782 | 122.2183 | -0.18768 | 0.050354 | 121.4859 | 3.0945 | 0.29755 | 0.29755 | 122.3877 | -0.21057 | -0.13275 | 0.022888 | -0.022888 | 0.10529 | -0.70953 | -0.15564 | 0.19226 | 0.10986 | 0.35248 | 0.35248 | 121.5408 | 122.2733 | -0.022888 | 122.4426 | 3.1494 | -0.15564 | 122.2733 | -0.022888 | 3.1494 | 121.5408 | 122.4426 | -122.3831 | -122.406
2808 | 122.3831 | -0.041199 | 122.1863 | 0.15297 | 0.0094144 | -0.0091325 | 0.012117 | 0.051609 | -0.015022 | 0.06498 | 0.07782 | 122.2412 | -0.12817 | 0.14191 | 121.6324 | 3.1448 | 0.082397 | 0.41657 | 122.3465 | -0.16937 | -0.086975 | 0.054932 | 0.11902 | 0.18311 | -0.55389 | -0.12817 | 0.16022 | 0.20599 | 0.1236 | 0.45776 | 121.6736 | 122.2824 | 0.11902 | 122.3877 | 3.186 | -0.12817 | 122.2824 | 0.11902 | 3.186 | 121.6736 | 122.3877 | -122.3145 | -122.3557
2809.6875 | 122.3145 | -0.10071 | 122.2641 | -0.20561 | 0.0077054 | -0.015114 | 0.0089124 | 0.04691 | -0.012031 | 0.069679 | 0.045776 | 122.1909 | -0.15106 | 0.16937 | 121.6507 | 3.3325 | 0.44861 | 0.75989 | 122.3236 | -0.20142 | -0.050354 | -0.073242 | 0.14648 | 0.27008 | -0.6134 | -0.10071 | 0.059509 | 0.19684 | 0.54932 | 0.8606 | 121.7514 | 122.2916 | 0.14648 | 122.4243 | 3.4332 | -0.10071 | 122.2916 | 0.14648 | 3.4332 | 121.7514 | 122.4243 | -122.4152 | -122.4655
2811.4375 | 122.4701 | -0.054932 | 122.2183 | 0.01564 | 0.0072782 | -0.010628 | 0.0082714 | 0.048405 | -0.012458 | 0.064339 | 0.009155 | 122.2046 | -0.14191 | 0.086975 | 121.6049 | 3.154 | 0.28839 | 0.50354 | 122.3511 | -0.20599 | -0.086975 | -0.013733 | 0.064087 | 0.14191 | -0.6134 | -0.15106 | 0.13275 | 0.15106 | 0.34332 | 0.55847 | 121.6599 | 122.2595 | 0.064087 | 122.406 | 3.2089 | -0.15106 | 122.2595 | 0.064087 | 3.2089 | 121.6599 | 122.406 | -122.3602 | -122.4243
2813.1875 | 122.3145 | -0.09613 | 122.2321 | -0.16747 | 0.009628 | -0.011909 | 0.010835 | 0.047337 | -0.012031 | 0.066262 | 0.050354 | 122.1954 | -0.13275 | 0.16022 | 121.6324 | 3.3371 | 0.46692 | 0.75073 | 122.3465 | -0.1831 | -0.036621 | -0.036621 | 0.14648 | 0.25635 | -0.59967 | -0.086975 | 0.11444 | 0.18311 | 0.56305 | 0.84686 | 121.7285 | 122.2916 | 0.14648 | 122.4426 | 3.4332 | -0.086975 | 122.2916 | 0.14648 | 3.4332 | 121.7285 | 122.4426 | -122.3648 | -122.4152
2814.9375 | 122.3236 | -0.091553 | 122.2458 | -0.12932 | 0.0089872 | -0.0084915 | 0.0093396 | 0.04691 | -0.012672 | 0.064339 | 0.045776 | 122.168 | -0.14191 | 0.17395 | 121.669 | 3.3234 | 0.37537 | 0.75073 | 122.3557 | -0.19226 | -0.050354 | -0.07782 | 0.13733 | 0.2655 | -0.57678 | -0.10071 | 0.10986 | 0.18768 | 0.46692 | 0.84228 | 121.7606 | 122.2595 | 0.13733 | 122.4472 | 3.4149 | -0.10071 | 122.2595 | 0.13733 | 3.4149 | 121.7606 | 122.4472 | -122.3877 | -122.4381
2816.6406 | 122.4197 | -0.054932 | 122.2046 | 0.091934 | 0.011551 | -0.01255 | 0.016389 | 0.051823 | -0.014167 | 0.066475 | -0.032043 | 122.2275 | -0.1831 | 0.050354 | 121.5225 | 3.0853 | 0.21973 | 0.28839 | 122.3923 | -0.19684 | -0.12817 | 0.022888 | 0.022889 | 0.10529 | -0.68207 | -0.14191 | 0.18768 | 0.15106 | 0.27466 | 0.34332 | 121.5775 | 122.2824 | 0.022889 | 122.4472 | 3.1403 | -0.14191 | 122.2824 | 0.022889 | 3.1403 | 121.5775 | 122.4472 | -122.3877 | -122.4014
2818.3906 | 122.3465 | -0.086975 | 122.2275 | 0.00038159 | 0.0085598 | -0.0087051 | 0.016816 | 0.049259 | -0.014167 | 0.066475 | -0.032043 | 122.2137 | -0.17853 | 0.059509 | 121.5225 | 3.1311 | 0.32959 | 0.35706 | 122.374 | -0.21973 | -0.091553 | -0.013733 | 0.054932 | 0.14648 | -0.70496 | -0.13275 | 0.14648 | 0.14648 | 0.41656 | 0.44403 | 121.6095 | 122.3007 | 0.054932 | 122.4609 | 3.2181 | -0.13275 | 122.3007 | 0.054932 | 3.2181 | 121.6095 | 122.4609 | -122.406 | -122.4472
2820.0938 | 122.4564 | -0.045776 | 122.2137 | 0.053787 | 0.010055 | -0.0087051 | 0.0095532 | 0.049473 | -0.012245 | 0.066902 | 0.018311 | 122.2275 | -0.15106 | 0.09613 | 121.5958 | 3.154 | 0.21515 | 0.4715 | 122.3557 | -0.21057 | -0.10529 | 0.013733 | 0.064087 | 0.14191 | -0.61798 | -0.1648 | 0.14191 | 0.16937 | 0.26093 | 0.51727 | 121.6415 | 122.2733 | 0.064087 | 122.4014 | 3.1998 | -0.1648 | 122.2733 | 0.064087 | 3.1998 | 121.6415 | 122.4014 | -122.3648 | -122.4243
2821.8594 | 122.3007 | -0.09613 | 122.2321 | -0.091171 | 0.010055 | -0.01255 | 0.01703 | 0.049259 | -0.01609 | 0.067116 | 0.013733 | 122.2412 | -0.15106 | 0.10071 | 121.5775 | 3.241 | 0.39825 | 0.54474 | 122.4152 | -0.19226 | -0.054932 | 0.009155 | 0.10986 | 0.19684 | -0.6546 | -0.096131 | 0.1831 | 0.16479 | 0.49438 | 0.64087 | 121.6736 | 122.3373 | 0.10986 | 122.5113 | 3.3371 | -0.096131 | 122.3373 | 0.10986 | 3.3371 | 121.6736 | 122.5113 | -122.3831 | -122.4243
2823.6094 | 122.438 | -0.050354 | 122.2137 | 0.10719 | 0.011123 | -0.011269 | 0.015107 | 0.049687 | -0.013954 | 0.068398 | -0.032043 | 122.2824 | -0.17853 | 0.027466 | 121.5088 | 3.0899 | 0.28381 | 0.29297 | 122.4289 | -0.2243 | -0.12817 | 0.068665 | 0.018311 | 0.07782 | -0.70496 | -0.17395 | 0.21515 | 0.14648 | 0.33417 | 0.34332 | 121.5591 | 122.3328 | 0.018311 | 122.4792 | 3.1403 | -0.17395 | 122.3328 | 0.018311 | 3.1403 | 121.5591 | 122.4792 | -122.3923 | -122.438
2825.3594 | 122.374 | -0.059509 | 122.2183 | 0.16823 | 0.0098416 | -0.011696 | 0.0089124 | 0.04755 | -0.011604 | 0.066902 | 0.059509 | 122.2 | -0.1236 | 0.15106 | 121.6324 | 3.1769 | 0.073242 | 0.43488 | 122.3373 | -0.17395 | -0.064087 | -0.018311 | 0.11902 | 0.21057 | -0.58594 | -0.11444 | 0.11902 | 0.1831 | 0.13275 | 0.49438 | 121.6919 | 122.2595 | 0.11902 | 122.3969 | 3.2364 | -0.11444 | 122.2595 | 0.11902 | 3.2364 | 121.6919 | 122.3969 | -122.3419 | -122.3923
2827.0625 | 122.3145 | -0.09613 | 122.2412 | -0.14458 | 0.0092008 | -0.0149 | 0.014467 | 0.049259 | -0.017158 | 0.065407 | -0.009155 | 122.2366 | -0.1831 | 0.091553 | 121.5729 | 3.273 | 0.4715 | 0.57678 | 122.374 | -0.2243 | -0.086975 | -0.004578 | 0.086975 | 0.18768 | -0.66834 | -0.12817 | 0.13275 | 0.17395 | 0.56763 | 0.67291 | 121.669 | 122.3328 | 0.086975 | 122.4701 | 3.3691 | -0.12817 | 122.3328 | 0.086975 | 3.3691 | 121.669 | 122.4701 | -122.4243 | -122.4655
2828.8281 | 122.4335 | -0.036621 | 122.2321 | 0.053787 | 0.012619 | -0.0076371 | 0.013185 | 0.049046 | -0.012886 | 0.067757 | -0.054932 | 122.2687 | -0.17853 | 0.018311 | 121.4905 | 3.1128 | 0.3067 | 0.32044 | 122.3694 | -0.21973 | -0.14191 | 0.036621 | -0.018311 | 0.054932 | -0.74158 | -0.18311 | 0.13733 | 0.1236 | 0.34332 | 0.35706 | 121.5271 | 122.3053 | -0.018311 | 122.406 | 3.1494 | -0.18311 | 122.3053 | -0.018311 | 3.1494 | 121.5271 | 122.406 | -122.4106 | -122.4518
2830.5156 | 122.3969 | -0.068665 | 122.2229 | 0.053787 | 0.011551 | -0.0089189 | 0.01468 | 0.050541 | -0.013527 | 0.067116 | -0.059509 | 122.2275 | -0.1831 | 0.018311 | 121.4905 | 3.1219 | 0.32959 | 0.32959 | 122.3785 | -0.24261 | -0.11444 | 0.004578 | 0.009156 | 0.086976 | -0.73242 | -0.17395 | 0.15564 | 0.1236 | 0.39826 | 0.39826 | 121.5591 | 122.2961 | 0.009156 | 122.4472 | 3.1906 | -0.17395 | 122.2961 | 0.009156 | 3.1906 | 121.5591 | 122.4472 | -122.406 | -122.4655
2832.2812 | 122.4289 | -0.059509 | 122.2092 | 0.01564 | 0.010482 | -0.011909 | 0.0050672 | 0.04691 | -0.011177 | 0.065834 | -0.009155 | 122.2275 | -0.13275 | 0.064087 | 121.6049 | 3.1906 | 0.32501 | 0.5127 | 122.3328 | -0.20142 | -0.073242 | 0.018311 | 0.050354 | 0.1236 | -0.60425 | -0.14191 | 0.1236 | 0.1236 | 0.38452 | 0.5722 | 121.6644 | 122.287 | 0.050354 | 122.3923 | 3.2501 | -0.14191 | 122.287 | 0.050354 | 3.2501 | 121.6644 | 122.3923 | -122.3419 | -122.4106
2834.0469 | 122.4335 | -0.064087 | 122.2275 | -0.0072479 | 0.0098416 | -0.0069961 | 0.007417 | 0.048405 | -0.010109 | 0.066048 | -0.009155 | 122.2412 | -0.15106 | 0.07782 | 121.5912 | 3.2089 | 0.32501 | 0.54474 | 122.3602 | -0.20142 | -0.086975 | 0.013733 | 0.054932 | 0.14191 | -0.63629 | -0.13733 | 0.13275 | 0.14191 | 0.3891 | 0.60883 | 121.6553 | 122.3053 | 0.054932 | 122.4243 | 3.273 | -0.13733 | 122.3053 | 0.054932 | 3.273 | 121.6553 | 122.4243 | -122.3785 | -122.4289
2835.7969 | 122.438 | -0.045776 | 122.2137 | 0.10719 | 0.0089872 | -0.010628 | 0.014894 | 0.047764 | -0.014808 | 0.06797 | -0.050354 | 122.2183 | -0.17395 | 0.032043 | 121.5225 | 3.1036 | 0.21057 | 0.31586 | 122.3877 | -0.21515 | -0.12817 | 0.004578 | -0.004578 | 0.077819 | -0.69122 | -0.16937 | 0.17395 | 0.1236 | 0.25635 | 0.36163 | 121.5683 | 122.2641 | -0.004578 | 122.4335 | 3.1494 | -0.16937 | 122.2641 | -0.004578 | 3.1494 | 121.5683 | 122.4335 | -122.3877 | -122.4289
2837.5469 | 122.3145 | -0.082397 | 122.2504 | -0.060654 | 0.0094144 | -0.011482 | 0.01468 | 0.051182 | -0.013313 | 0.065621 | 0.004578 | 122.2275 | -0.16022 | 0.091553 | 121.5591 | 3.2135 | 0.37994 | 0.48065 | 122.3923 | -0.21515 | -0.07782 | -0.022888 | 0.086975 | 0.17395 | -0.69122 | -0.13275 | 0.14191 | 0.16479 | 0.46234 | 0.56305 | 121.6415 | 122.3099 | 0.086975 | 122.4747 | 3.2959 | -0.13275 | 122.3099 | 0.086975 | 3.2959 | 121.6415 | 122.4747 | -122.4106 | -122.4655
2839.25 | 122.319 | -0.086975 | 122.2458 | -0.17509 | 0.011551 | -0.011269 | 0.01233 | 0.049687 | -0.014167 | 0.06733 | -0.032043 | 122.2183 | -0.17853 | 0.073242 | 121.5637 | 3.273 | 0.49896 | 0.59052 | 122.3831 | -0.21973 | -0.091553 | -0.027466 | 0.054932 | 0.16022 | -0.68207 | -0.13275 | 0.13733 | 0.14648 | 0.58594 | 0.67749 | 121.6507 | 122.3053 | 0.054932 | 122.4701 | 3.36 | -0.13275 | 122.3053 | 0.054932 | 3.36 | 121.6507 | 122.4701 | -122.4243 | -122.4655
2841 | 122.3145 | -0.10529 | 122.2504 | -0.20561 | 0.011764 | -0.0093461 | 0.0082714 | 0.048832 | -0.009895 | 0.064766 | 0.050354 | 122.2 | -0.13733 | 0.17395 | 121.6507 | 3.3554 | 0.45319 | 0.75989 | 122.3602 | -0.19684 | -0.032043 | -0.050354 | 0.15564 | 0.27924 | -0.59967 | -0.091552 | 0.10986 | 0.18768 | 0.55847 | 0.86517 | 121.756 | 122.3053 | 0.15564 | 122.4655 | 3.4607 | -0.091552 | 122.3053 | 0.15564 | 3.4607 | 121.756 | 122.4655 | -122.3877 | -122.4472
2842.75 | 122.3328 | -0.09613 | 122.2549 | -0.20561 | 0.0085598 | -0.01255 | 0.0099804 | 0.049046 | -0.011177 | 0.065193 | 0.064087 | 122.2229 | -0.13275 | 0.16022 | 121.6415 | 3.3508 | 0.45319 | 0.77362 | 122.3785 | -0.19226 | -0.036621 | -0.032044 | 0.16022 | 0.25635 | -0.6134 | -0.096131 | 0.1236 | 0.19684 | 0.54932 | 0.86975 | 121.7377 | 122.319 | 0.16022 | 122.4747 | 3.447 | -0.096131 | 122.319 | 0.16022 | 3.447 | 121.7377 | 122.4747 | -122.3877 | -122.4472
2844.5 | 122.4564 | -0.054932 | 122.1863 | 0.01564 | 0.0094144 | -0.011055 | 0.009126 | 0.049473 | -0.012458 | 0.06498 | 0.009155 | 122.2321 | -0.15106 | 0.09613 | 121.582 | 3.1906 | 0.28381 | 0.50812 | 122.3969 | -0.19684 | -0.09613 | 0.045777 | 0.064087 | 0.15106 | -0.60425 | -0.14191 | 0.21057 | 0.16022 | 0.33874 | 0.56305 | 121.637 | 122.287 | 0.064087 | 122.4518 | 3.2455 | -0.14191 | 122.287 | 0.064087 | 3.2455 | 121.637 | 122.4518 | -122.3373 | -122.3831
2846.1875 | 122.319 | -0.11902 | 122.2321 | -0.19035 | 0.011123 | -0.0084915 | 0.010835 | 0.046055 | -0.010322 | 0.063698 | 0.050354 | 122.2183 | -0.14648 | 0.14191 | 121.6187 | 3.3463 | 0.52185 | 0.73242 | 122.3282 | -0.21057 | -0.027465 | -0.013733 | 0.16937 | 0.26093 | -0.6134 | -0.091552 | 0.09613 | 0.19684 | 0.64087 | 0.85144 | 121.7377 | 122.3373 | 0.16937 | 122.4472 | 3.4653 | -0.091552 | 122.3373 | 0.16937 | 3.4653 | 121.7377 | 122.4472 | -122.3785 | -122.4426
2847.9375 | 122.3099 | -0.091553 | 122.2687 | -0.12169 | 0.0098416 | -0.0089189 | 0.015748 | 0.050541 | -0.013954 | 0.065621 | 0 | 122.2183 | -0.17395 | 0.11902 | 121.5637 | 3.273 | 0.46234 | 0.5722 | 122.3877 | -0.21057 | -0.082397 | -0.050354 | 0.091553 | 0.21057 | -0.70496 | -0.11902 | 0.11902 | 0.17395 | 0.55389 | 0.66376 | 121.6553 | 122.3099 | 0.091553 | 122.4792 | 3.3646 | -0.11902 | 122.3099 | 0.091553 | 3.3646 | 121.6553 | 122.4792 | -122.4426 | -122.4792
2849.6875 | 122.2916 | -0.10986 | 122.2275 | -0.12169 | 0.0098416 | -0.0091325 | 0.015748 | 0.047764 | -0.013099 | 0.066262 | 0.018311 | 122.2687 | -0.1831 | 0.10071 | 121.5683 | 3.2547 | 0.39825 | 0.54016 | 122.374 | -0.22888 | -0.073242 | 0.041199 | 0.12817 | 0.21057 | -0.65918 | -0.11902 | 0.14648 | 0.20142 | 0.50812 | 0.65002 | 121.6782 | 122.3785 | 0.12817 | 122.4838 | 3.3646 | -0.11902 | 122.3785 | 0.12817 | 3.3646 | 121.6782 | 122.4838 | -122.4106 | -122.4564
2851.3906 | 122.4472 | -0.068665 | 122.1909 | 0.076676 | 0.011978 | -0.0097733 | 0.0078442 | 0.048619 | -0.01139 | 0.066689 | 0.022888 | 122.2137 | -0.1236 | 0.09613 | 121.6049 | 3.1906 | 0.2243 | 0.47607 | 122.3373 | -0.18768 | -0.054931 | 0.022888 | 0.091553 | 0.16479 | -0.58594 | -0.11902 | 0.14648 | 0.14648 | 0.29297 | 0.54474 | 121.6736 | 122.2824 | 0.091553 | 122.406 | 3.2593 | -0.11902 | 122.2824 | 0.091553 | 3.2593 | 121.6736 | 122.406 | -122.3145 | -122.3785
2853.1562 | 122.3511 | -0.10986 | 122.2458 | -0.24376 | 0.0081326 | -0.0102 | 0.011049 | 0.047123 | -0.015236 | 0.064125 | -0.018311 | 122.2137 | -0.15106 | 0.068665 | 121.5591 | 3.2913 | 0.6134 | 0.65918 | 122.4106 | -0.22888 | -0.041199 | -0.032044 | 0.091552 | 0.17853 | -0.68665 | -0.11902 | 0.16479 | 0.13275 | 0.72327 | 0.76904 | 121.669 | 122.3236 | 0.091552 | 122.5204 | 3.4012 | -0.11902 | 122.3236 | 0.091552 | 3.4012 | 121.669 | 122.5204 | -122.3969 | -122.4747
2854.8594 | 122.3511 | -0.082397 | 122.2366 | -0.23613 | 0.011123 | -0.013618 | 0.014253 | 0.048619 | -0.013527 | 0.066262 | -0.059509 | 122.2412 | -0.19684 | 0.045776 | 121.5271 | 3.2684 | 0.62256 | 0.60425 | 122.4152 | -0.22888 | -0.11444 | 0.004578 | 0.022888 | 0.12817 | -0.70953 | -0.14649 | 0.17853 | 0.13733 | 0.70496 | 0.68664 | 121.6095 | 122.3236 | 0.022888 | 122.4976 | 3.3508 | -0.14649 | 122.3236 | 0.022888 | 3.3508 | 121.6095 | 122.4976 | -122.4335 | -122.4655
2856.625 | 122.3053 | -0.10529 | 122.2549 | -0.11406 | 0.009628 | -0.012337 | 0.012758 | 0.051609 | -0.015236 | 0.063912 | 0.004578 | 122.2183 | -0.17395 | 0.10529 | 121.5775 | 3.2822 | 0.43945 | 0.55847 | 122.3969 | -0.21973 | -0.068664 | -0.036621 | 0.10986 | 0.21057 | -0.67749 | -0.11444 | 0.14191 | 0.17853 | 0.54474 | 0.66376 | 121.6827 | 122.3236 | 0.10986 | 122.5021 | 3.3875 | -0.11444 | 122.3236 | 0.10986 | 3.3875 | 121.6827 | 122.5021 | -122.4289 | -122.4747
2858.375 | 122.3236 | -0.11444 | 122.2595 | -0.13695 | 0.0094144 | -0.012978 | 0.0067762 | 0.049046 | -0.0086132 | 0.065407 | 0.073242 | 122.2046 | -0.12817 | 0.17395 | 121.669 | 3.3554 | 0.37994 | 0.75531 | 122.3465 | -0.18768 | -0.013733 | -0.054931 | 0.18768 | 0.28839 | -0.59052 | -0.073242 | 0.086976 | 0.20142 | 0.49439 | 0.86975 | 121.7834 | 122.319 | 0.18768 | 122.4609 | 3.4698 | -0.073242 | 122.319 | 0.18768 | 3.4698 | 121.7834 | 122.4609 | -122.3877 | -122.4472
2860.0625 | 122.3511 | -0.091553 | 122.2412 | -0.21324 | 0.009628 | -0.0080643 | 0.014039 | 0.048191 | -0.013954 | 0.06733 | -0.036621 | 122.2778 | -0.20142 | 0.045776 | 121.5408 | 3.2639 | 0.59509 | 0.60425 | 122.374 | -0.22888 | -0.10986 | 0.036621 | 0.054932 | 0.13733 | -0.70038 | -0.13733 | 0.13275 | 0.1648 | 0.68665 | 0.6958 | 121.6324 | 122.3694 | 0.054932 | 122.4655 | 3.3554 | -0.13733 | 122.3694 | 0.054932 | 3.3554 | 121.6324 | 122.4655 | -122.4426 | -122.4701
2861.7656 | 122.4289 | -0.059509 | 122.2229 | -0.075912 | 0.0085598 | -0.011909 | 0.0080578 | 0.046696 | -0.010109 | 0.065193 | 0.013733 | 122.2321 | -0.14191 | 0.10071 | 121.6278 | 3.2822 | 0.36163 | 0.61798 | 122.3557 | -0.19226 | -0.082398 | 0.009156 | 0.073242 | 0.16022 | -0.59509 | -0.13275 | 0.13275 | 0.15564 | 0.42114 | 0.67749 | 121.6873 | 122.2916 | 0.073242 | 122.4152 | 3.3417 | -0.13275 | 122.2916 | 0.073242 | 3.3417 | 121.6873 | 122.4152 | -122.3648 | -122.4152
2863.5312 | 122.4426 | -0.045776 | 122.2092 | 0.091934 | 0.010269 | -0.015114 | 0.010621 | 0.048405 | -0.0086132 | 0.066048 | 0.027466 | 122.2229 | -0.14648 | 0.10529 | 121.5958 | 3.1723 | 0.22888 | 0.48065 | 122.3511 | -0.18768 | -0.10071 | 0.013733 | 0.073242 | 0.15106 | -0.6134 | -0.14191 | 0.14191 | 0.17395 | 0.27466 | 0.52643 | 121.6415 | 122.2687 | 0.073242 | 122.3969 | 3.2181 | -0.14191 | 122.2687 | 0.073242 | 3.2181 | 121.6415 | 122.3969 | -122.3557 | -122.3969
2865.2969 | 122.438 | -0.054932 | 122.2 | 0.13008 | 0.013473 | -0.0084915 | 0.015535 | 0.047978 | -0.012672 | 0.067543 | -0.032043 | 122.2687 | -0.19684 | 0.045776 | 121.5134 | 3.1082 | 0.25635 | 0.28839 | 122.3877 | -0.23804 | -0.14191 | 0.068665 | 0.022889 | 0.10071 | -0.68664 | -0.1831 | 0.18768 | 0.1648 | 0.31128 | 0.34332 | 121.5683 | 122.3236 | 0.022889 | 122.4426 | 3.1631 | -0.1831 | 122.3236 | 0.022889 | 3.1631 | 121.5683 | 122.4426 | -122.3969 | -122.438
2867 | 122.3419 | -0.091553 | 122.2458 | -0.19798 | 0.011123 | -0.014687 | 0.015962 | 0.047978 | -0.012886 | 0.064339 | -0.036621 | 122.2595 | -0.18768 | 0.073242 | 121.5729 | 3.3005 | 0.52643 | 0.59052 | 122.3923 | -0.23346 | -0.09613 | 0.013732 | 0.054932 | 0.16479 | -0.67291 | -0.14191 | 0.14648 | 0.15106 | 0.61798 | 0.68207 | 121.6644 | 122.3511 | 0.054932 | 122.4838 | 3.392 | -0.14191 | 122.3511 | 0.054932 | 3.392 | 121.6644 | 122.4838 | -122.4335 | -122.4792
2868.75 | 122.4197 | -0.064087 | 122.2183 | -0.030136 | 0.010482 | -0.011696 | 0.0080578 | 0.046482 | -0.010536 | 0.066262 | -0.018311 | 122.2321 | -0.14648 | 0.09613 | 121.6232 | 3.2639 | 0.35248 | 0.59967 | 122.3465 | -0.20599 | -0.082397 | 0.013733 | 0.045776 | 0.16022 | -0.59509 | -0.14191 | 0.12817 | 0.12817 | 0.41657 | 0.66376 | 121.6873 | 122.2961 | 0.045776 | 122.4106 | 3.3279 | -0.14191 | 122.2961 | 0.045776 | 3.3279 | 121.6873 | 122.4106 | -122.3648 | -122.4243
2870.4531 | 122.3236 | -0.10529 | 122.2275 | -0.15221 | 0.010055 | -0.0087051 | 0.010194 | 0.047978 | -0.013099 | 0.066048 | 0.068665 | 122.2 | -0.15106 | 0.16022 | 121.6644 | 3.36 | 0.41657 | 0.75073 | 122.3648 | -0.20142 | -0.045776 | -0.027466 | 0.17395 | 0.2655 | -0.56305 | -0.09613 | 0.13733 | 0.21973 | 0.52185 | 0.85602 | 121.7697 | 122.3053 | 0.17395 | 122.4701 | 3.4653 | -0.09613 | 122.3053 | 0.17395 | 3.4653 | 121.7697 | 122.4701 | -122.3785 | -122.4289
2872.2188 | 122.3694 | -0.086975 | 122.2549 | -0.21324 | 0.0081326 | -0.010628 | 0.011049 | 0.04755 | -0.012886 | 0.064553 | -0.064087 | 122.2183 | -0.19684 | 0.059509 | 121.5454 | 3.2822 | 0.63629 | 0.64087 | 122.4335 | -0.21057 | -0.10986 | -0.036621 | 0.022888 | 0.14648 | -0.70953 | -0.1236 | 0.17853 | 0.13275 | 0.72327 | 0.72784 | 121.6324 | 122.3053 | 0.022888 | 122.5204 | 3.3691 | -0.1236 | 122.3053 | 0.022888 | 3.3691 | 121.6324 | 122.5204 | -122.4518 | -122.4655
2873.9219 | 122.319 | -0.11444 | 122.2412 | -0.075912 | 0.0089872 | -0.0089189 | 0.015107 | 0.049046 | -0.015663 | 0.067543 | 0.013733 | 122.2504 | -0.16937 | 0.11444 | 121.5683 | 3.2501 | 0.35706 | 0.50354 | 122.4289 | -0.21057 | -0.054932 | 0.009155 | 0.12817 | 0.22888 | -0.67291 | -0.09613 | 0.18768 | 0.18311 | 0.4715 | 0.61798 | 121.6827 | 122.3648 | 0.12817 | 122.5433 | 3.3646 | -0.09613 | 122.3648 | 0.12817 | 3.3646 | 121.6827 | 122.5433 | -122.4106 | -122.4518
2875.6719 | 122.3511 | -0.073242 | 122.2275 | -0.18272 | 0.01091 | -0.0102 | 0.014039 | 0.048191 | -0.012031 | 0.065407 | -0.027466 | 122.287 | -0.16937 | 0.045776 | 121.5408 | 3.2867 | 0.58594 | 0.60425 | 122.4152 | -0.23804 | -0.096131 | 0.059509 | 0.045776 | 0.11902 | -0.68664 | -0.16479 | 0.18768 | 0.14191 | 0.65918 | 0.67749 | 121.6141 | 122.3602 | 0.045776 | 122.4884 | 3.36 | -0.16479 | 122.3602 | 0.045776 | 3.36 | 121.6141 | 122.4884 | -122.3969 | -122.4655
2877.3594 | 122.3557 | -0.091553 | 122.2092 | 0.01564 | 0.009628 | -0.011269 | 0.014253 | 0.049473 | -0.015663 | 0.065621 | -0.022888 | 122.2275 | -0.17853 | 0.050354 | 121.5363 | 3.1998 | 0.3479 | 0.39825 | 122.4197 | -0.21515 | -0.086975 | 0.018311 | 0.068665 | 0.14191 | -0.67291 | -0.1236 | 0.21057 | 0.15564 | 0.43945 | 0.48981 | 121.6278 | 122.319 | 0.068665 | 122.5113 | 3.2913 | -0.1236 | 122.319 | 0.068665 | 3.2913 | 121.6278 | 122.5113 | -122.3877 | -122.4243
2879.1094 | 122.3877 | -0.073242 | 122.1909 | 0.053787 | 0.009628 | -0.011909 | 0.013826 | 0.0499 | -0.012245 | 0.065621 | -0.07782 | 122.2275 | -0.1831 | 0.032043 | 121.5271 | 3.154 | 0.33875 | 0.33875 | 122.3923 | -0.23346 | -0.10986 | 0.036621 | -0.004578 | 0.10529 | -0.66376 | -0.16022 | 0.20142 | 0.10528 | 0.41199 | 0.41199 | 121.6003 | 122.3007 | -0.004578 | 122.4655 | 3.2272 | -0.16022 | 122.3007 | -0.004578 | 3.2272 | 121.6003 | 122.4655 | -122.374 | -122.4243
2880.875 | 122.3877 | -0.068665 | 122.2046 | 0.17586 | 0.011978 | -0.0093461 | 0.010194 | 0.050968 | -0.012886 | 0.066262 | 0.064087 | 122.2321 | -0.11902 | 0.14191 | 121.637 | 3.2227 | 0.082397 | 0.43488 | 122.3282 | -0.17853 | -0.050354 | 0.027466 | 0.13275 | 0.21057 | -0.56763 | -0.10986 | 0.1236 | 0.18311 | 0.15106 | 0.50354 | 121.7056 | 122.3007 | 0.13275 | 122.3969 | 3.2913 | -0.10986 | 122.3007 | 0.13275 | 3.2913 | 121.7056 | 122.3969 | -122.3236 | -122.3831
2882.5781 | 122.3145 | -0.09613 | 122.2504 | -0.083542 | 0.0094144 | -0.011696 | 0.014467 | 0.048619 | -0.015022 | 0.067543 | 0.018311 | 122.2092 | -0.16022 | 0.10529 | 121.5775 | 3.273 | 0.39368 | 0.5127 | 122.3877 | -0.19684 | -0.064087 | -0.041199 | 0.11444 | 0.20142 | -0.67291 | -0.10071 | 0.13733 | 0.17853 | 0.48981 | 0.60882 | 121.6736 | 122.3053 | 0.11444 | 122.4838 | 3.3691 | -0.10071 | 122.3053 | 0.11444 | 3.3691 | 121.6736 | 122.4838 | -122.4106 | -122.4472
2884.3281 | 122.3831 | -0.07782 | 122.2 | 0.19112 | 0.010696 | -0.0078507 | 0.0099804 | 0.048405 | -0.010536 | 0.064766 | 0.064087 | 122.2321 | -0.11902 | 0.14191 | 121.6553 | 3.2547 | 0.086975 | 0.44403 | 122.3602 | -0.17853 | -0.041199 | 0.032044 | 0.14191 | 0.21973 | -0.54474 | -0.10071 | 0.16022 | 0.18311 | 0.16479 | 0.52185 | 121.7331 | 122.3099 | 0.14191 | 122.438 | 3.3325 | -0.10071 | 122.3099 | 0.14191 | 3.3325 | 121.7331 | 122.438 | -122.319 | -122.3785
2886.0781 | 122.4243 | -0.045776 | 122.2275 | 0.069046 | 0.012405 | -0.0080643 | 0.012758 | 0.050328 | -0.015022 | 0.066689 | -0.073242 | 122.2458 | -0.1831 | 0.027466 | 121.4905 | 3.1448 | 0.31128 | 0.3067 | 122.4289 | -0.21515 | -0.13733 | 0.018311 | -0.027466 | 0.073242 | -0.737 | -0.16937 | 0.20142 | 0.10986 | 0.35705 | 0.35248 | 121.5363 | 122.2916 | -0.027466 | 122.4747 | 3.1906 | -0.16937 | 122.2916 | -0.027466 | 3.1906 | 121.5363 | 122.4747 | -122.4106 | -122.4426
2887.8438 | 122.3373 | -0.082397 | 122.2595 | -0.13695 | 0.01091 | -0.011696 | 0.009126 | 0.048405 | -0.011604 | 0.06498 | 0.054932 | 122.2229 | -0.12817 | 0.15564 | 121.6644 | 3.3646 | 0.38452 | 0.737 | 122.3328 | -0.19684 | -0.045777 | -0.036621 | 0.13733 | 0.23804 | -0.59509 | -0.11444 | 0.073243 | 0.18311 | 0.46692 | 0.8194 | 121.7468 | 122.3053 | 0.13733 | 122.4152 | 3.447 | -0.11444 | 122.3053 | 0.13733 | 3.447 | 121.7468 | 122.4152 | -122.3877 | -122.4564
2889.5312 | 122.3282 | -0.10986 | 122.2412 | -0.12169 | 0.012619 | -0.01255 | 0.0082714 | 0.04755 | -0.011818 | 0.066048 | 0.068665 | 122.2046 | -0.16479 | 0.16937 | 121.6644 | 3.3783 | 0.39368 | 0.75073 | 122.3785 | -0.19226 | -0.054932 | -0.036621 | 0.17853 | 0.27924 | -0.57678 | -0.082398 | 0.13733 | 0.23346 | 0.50354 | 0.86059 | 121.7743 | 122.3145 | 0.17853 | 122.4884 | 3.4882 | -0.082398 | 122.3145 | 0.17853 | 3.4882 | 121.7743 | 122.4884 | -122.406 | -122.4335
2891.2812 | 122.4518 | -0.059509 | 122.2092 | 0.11482 | 0.009628 | -0.0093461 | 0.014253 | 0.048832 | -0.011177 | 0.065193 | -0.027466 | 122.2641 | -0.17853 | 0.027466 | 121.5179 | 3.1265 | 0.23804 | 0.29755 | 122.3877 | -0.21973 | -0.11902 | 0.054932 | 0.032043 | 0.086975 | -0.69122 | -0.16022 | 0.17853 | 0.15106 | 0.29755 | 0.35705 | 121.5775 | 122.3236 | 0.032043 | 122.4472 | 3.186 | -0.16022 | 122.3236 | 0.032043 | 3.186 | 121.5775 | 122.4472 | -122.3877 | -122.4289
2893.0469 | 122.438 | -0.068665 | 122.2137 | -0.022507 | 0.0059964 | -0.0078507 | 0.0078442 | 0.046696 | -0.010322 | 0.065407 | -0.009155 | 122.2733 | -0.15106 | 0.086975 | 121.5866 | 3.2684 | 0.3479 | 0.56763 | 122.3419 | -0.20599 | -0.082397 | 0.059509 | 0.05951 | 0.15564 | -0.62714 | -0.13733 | 0.12817 | 0.14191 | 0.41656 | 0.63629 | 121.6553 | 122.3419 | 0.05951 | 122.4106 | 3.3371 | -0.13733 | 122.3419 | 0.05951 | 3.3371 | 121.6553 | 122.4106 | -122.3648 | -122.4197
2894.7344 | 122.3557 | -0.082397 | 122.2275 | -0.068283 | 0.010055 | -0.0059281 | 0.018098 | 0.050968 | -0.014381 | 0.066048 | -0.022888 | 122.2549 | -0.16937 | 0.036621 | 121.4951 | 3.186 | 0.33875 | 0.37537 | 122.3969 | -0.21973 | -0.086976 | 0.027466 | 0.059509 | 0.11902 | -0.73242 | -0.13733 | 0.16937 | 0.14649 | 0.42114 | 0.45776 | 121.5775 | 122.3373 | 0.059509 | 122.4792 | 3.2684 | -0.13733 | 122.3373 | 0.059509 | 3.2684 | 121.5775 | 122.4792 | -122.3969 | -122.4472
2896.4844 | 122.3282 | -0.10071 | 122.2549 | -0.083542 | 0.010269 | -0.0072099 | 0.014467 | 0.050541 | -0.014595 | 0.065407 | 0.013733 | 122.2458 | -0.16937 | 0.10529 | 121.5775 | 3.2959 | 0.38452 | 0.53101 | 122.4243 | -0.21515 | -0.068665 | -0.009155 | 0.11444 | 0.20599 | -0.67749 | -0.11444 | 0.16937 | 0.18311 | 0.48523 | 0.63171 | 121.6782 | 122.3465 | 0.11444 | 122.525 | 3.3966 | -0.11444 | 122.3465 | 0.11444 | 3.3966 | 121.6782 | 122.525 | -122.4243 | -122.4701
2898.2344 | 122.4289 | -0.032043 | 122.1725 | 0.12245 | 0.010269 | -0.0061417 | 0.014253 | 0.050541 | -0.013954 | 0.065834 | -0.059509 | 122.2275 | -0.1831 | 0.022888 | 121.5179 | 3.1265 | 0.27008 | 0.29755 | 122.4152 | -0.21973 | -0.15106 | 0.054932 | -0.027466 | 0.054931 | -0.6546 | -0.18768 | 0.24262 | 0.1236 | 0.30212 | 0.32959 | 121.55 | 122.2595 | -0.027466 | 122.4472 | 3.1586 | -0.18768 | 122.2595 | -0.027466 | 3.1586 | 121.55 | 122.4472 | -122.3557 | -122.3923
2899.9219 | 122.3557 | -0.086975 | 122.2504 | -0.12932 | 0.011551 | -0.010414 | 0.0059216 | 0.049259 | -0.012458 | 0.06498 | 0.041199 | 122.2412 | -0.12817 | 0.13275 | 121.6599 | 3.3875 | 0.38452 | 0.72784 | 122.3373 | -0.20142 | -0.041199 | -0.009155 | 0.12817 | 0.21973 | -0.59051 | -0.11444 | 0.086975 | 0.16937 | 0.4715 | 0.81482 | 121.7468 | 122.3282 | 0.12817 | 122.4243 | 3.4744 | -0.11444 | 122.3282 | 0.12817 | 3.4744 | 121.7468 | 122.4243 | -122.3785 | -122.4518
2901.6719 | 122.3648 | -0.082397 | 122.2458 | -0.23613 | 0.013687 | -0.0091325 | 0.010408 | 0.046482 | -0.012886 | 0.064766 | -0.041199 | 122.2778 | -0.16937 | 0.036621 | 121.5271 | 3.3096 | 0.65002 | 0.63171 | 122.3923 | -0.24719 | -0.086976 | 0.032043 | 0.041198 | 0.11902 | -0.71869 | -0.16479 | 0.14648 | 0.12817 | 0.73242 | 0.71411 | 121.6095 | 122.3602 | 0.041198 | 122.4747 | 3.392 | -0.16479 | 122.3602 | 0.041198 | 3.392 | 121.6095 | 122.4747 | -122.4152 | -122.493
2903.375 | 122.3877 | -0.059509 | 122.2458 | 0.084305 | 0.0094144 | -0.0102 | 0.014894 | 0.0499 | -0.014167 | 0.066475 | -0.045776 | 122.2549 | -0.17395 | 0.027466 | 121.5088 | 3.1586 | 0.34332 | 0.34332 | 122.406 | -0.20599 | -0.11444 | 0.009155 | 0.013733 | 0.086975 | -0.737 | -0.14649 | 0.16022 | 0.12817 | 0.40283 | 0.40283 | 121.5683 | 122.3145 | 0.013733 | 122.4655 | 3.2181 | -0.14649 | 122.3145 | 0.013733 | 3.2181 | 121.5683 | 122.4655 | -122.4197 | -122.4518
2905.1406 | 122.319 | -0.091553 | 122.2321 | -0.18272 | 0.010269 | -0.0093461 | 0.01233 | 0.050114 | -0.013099 | 0.066262 | -0.027466 | 122.2366 | -0.17853 | 0.07782 | 121.5775 | 3.3234 | 0.48981 | 0.59052 | 122.4197 | -0.20142 | -0.086975 | 0.004577 | 0.064087 | 0.16937 | -0.6546 | -0.10986 | 0.18768 | 0.15106 | 0.58136 | 0.68207 | 121.669 | 122.3282 | 0.064087 | 122.5113 | 3.4149 | -0.10986 | 122.3282 | 0.064087 | 3.4149 | 121.669 | 122.5113 | -122.4106 | -122.4335
2906.9062 | 122.3145 | -0.10986 | 122.2641 | -0.16747 | 0.010269 | -0.011055 | 0.012971 | 0.048405 | -0.013313 | 0.066902 | -0.027466 | 122.2504 | -0.17853 | 0.068665 | 121.582 | 3.3142 | 0.50812 | 0.58136 | 122.4152 | -0.2243 | -0.068665 | -0.013733 | 0.082397 | 0.17853 | -0.68207 | -0.11444 | 0.15106 | 0.15106 | 0.61798 | 0.69122 | 121.6919 | 122.3602 | 0.082397 | 122.525 | 3.4241 | -0.11444 | 122.3602 | 0.082397 | 3.4241 | 121.6919 | 122.525 | -122.4426 | -122.4884
2908.6094 | 122.2961 | -0.10529 | 122.2641 | -0.22087 | 0.0094144 | -0.012764 | 0.005708 | 0.048191 | -0.008827 | 0.066262 | 0.054932 | 122.2137 | -0.1236 | 0.15564 | 121.6415 | 3.4195 | 0.44861 | 0.76446 | 122.3602 | -0.18768 | -0.01831 | -0.050354 | 0.16022 | 0.26093 | -0.62256 | -0.082397 | 0.09613 | 0.17853 | 0.55389 | 0.86975 | 121.7468 | 122.319 | 0.16022 | 122.4655 | 3.5248 | -0.082397 | 122.319 | 0.16022 | 3.5248 | 121.7468 | 122.4655 | -122.3877 | -122.4518
2910.3594 | 122.3007 | -0.11444 | 122.2504 | -0.068283 | 0.01091 | -0.0059281 | 0.013826 | 0.048405 | -0.015022 | 0.066048 | 0.009155 | 122.2458 | -0.16937 | 0.09613 | 121.5775 | 3.2959 | 0.37994 | 0.52643 | 122.3923 | -0.21057 | -0.054932 | -0.004577 | 0.1236 | 0.21057 | -0.67291 | -0.09613 | 0.14191 | 0.17853 | 0.49439 | 0.64087 | 121.6919 | 122.3602 | 0.1236 | 122.5067 | 3.4103 | -0.09613 | 122.3602 | 0.1236 | 3.4103 | 121.6919 | 122.5067 | -122.4197 | -122.4609
2912.125 | 122.3419 | -0.09613 | 122.2733 | -0.022507 | 0.0098416 | -0.011269 | 0.013612 | 0.051823 | -0.015022 | 0.06733 | -0.009155 | 122.2229 | -0.15564 | 0.068665 | 121.5454 | 3.2455 | 0.36621 | 0.41657 | 122.4289 | -0.21057 | -0.05951 | -0.050354 | 0.086975 | 0.16479 | -0.72784 | -0.11444 | 0.15564 | 0.14649 | 0.46234 | 0.5127 | 121.6415 | 122.319 | 0.086975 | 122.525 | 3.3417 | -0.11444 | 122.319 | 0.086975 | 3.3417 | 121.6415 | 122.525 | -122.4289 | -122.4838
2913.8281 | 122.3511 | -0.10071 | 122.2641 | -0.23613 | 0.011978 | -0.0102 | 0.0082714 | 0.046269 | -0.013954 | 0.065621 | 0 | 122.2504 | -0.15106 | 0.068665 | 121.5866 | 3.3463 | 0.60425 | 0.69122 | 122.3923 | -0.20599 | -0.050354 | -0.013733 | 0.10071 | 0.16937 | -0.67749 | -0.10529 | 0.12817 | 0.15106 | 0.70496 | 0.79193 | 121.6873 | 122.3511 | 0.10071 | 122.493 | 3.447 | -0.10529 | 122.3511 | 0.10071 | 3.447 | 121.6873 | 122.493 | -122.4152 | -122.4701
2915.5781 | 122.4701 | -0.068665 | 122.2229 | 0.0080111 | 0.009628 | -0.012978 | 0.0072034 | 0.045841 | -0.012886 | 0.065193 | -0.018311 | 122.2687 | -0.14191 | 0.082397 | 121.5958 | 3.2501 | 0.35248 | 0.53558 | 122.3648 | -0.21973 | -0.073242 | 0.045777 | 0.050354 | 0.15106 | -0.62714 | -0.15106 | 0.14191 | 0.1236 | 0.42114 | 0.60425 | 121.6644 | 122.3373 | 0.050354 | 122.4335 | 3.3188 | -0.15106 | 122.3373 | 0.050354 | 3.3188 | 121.6644 | 122.4335 | -122.3648 | -122.4426
2917.3281 | 122.3923 | -0.064087 | 122.2366 | 0.1606 | 0.0092008 | -0.0102 | 0.014253 | 0.049046 | -0.01374 | 0.064766 | 0.041199 | 122.2321 | -0.15564 | 0.12817 | 121.6232 | 3.241 | 0.091553 | 0.42114 | 122.3419 | -0.19684 | -0.091553 | -0.004577 | 0.10529 | 0.19226 | -0.6134 | -0.13275 | 0.10529 | 0.19684 | 0.15564 | 0.48523 | 121.6873 | 122.2961 | 0.10529 | 122.406 | 3.3051 | -0.13275 | 122.2961 | 0.10529 | 3.3051 | 121.6873 | 122.406 | -122.3923 | -122.4335
2919.0938 | 122.4014 | -0.07782 | 122.2321 | 0.1606 | 0.0094144 | -0.0076371 | 0.0099804 | 0.049259 | -0.012245 | 0.066262 | 0.050354 | 122.2046 | -0.1236 | 0.14648 | 121.6278 | 3.2593 | 0.10529 | 0.45319 | 122.3877 | -0.16479 | -0.045776 | -0.027466 | 0.12817 | 0.2243 | -0.60425 | -0.086975 | 0.15564 | 0.17395 | 0.18311 | 0.53101 | 121.7056 | 122.2824 | 0.12817 | 122.4655 | 3.3371 | -0.086975 | 122.2824 | 0.12817 | 3.3371 | 121.7056 | 122.4655 | -122.3557 | -122.3969
2920.7969 | 122.3648 | -0.09613 | 122.2137 | -0.21324 | 0.01091 | -0.014473 | 0.01233 | 0.04755 | -0.014167 | 0.065193 | -0.050354 | 122.287 | -0.17395 | 0.032043 | 121.5317 | 3.3279 | 0.6546 | 0.65002 | 122.4014 | -0.22888 | -0.07782 | 0.073242 | 0.045776 | 0.12817 | -0.68207 | -0.13275 | 0.18768 | 0.1236 | 0.75073 | 0.74615 | 121.6278 | 122.3831 | 0.045776 | 122.4976 | 3.4241 | -0.13275 | 122.3831 | 0.045776 | 3.4241 | 121.6278 | 122.4976 | -122.3877 | -122.4426
2922.5625 | 122.319 | -0.073242 | 122.2824 | -0.15221 | 0.0085598 | -0.0102 | 0.014467 | 0.049259 | -0.01609 | 0.067116 | -0.013733 | 122.2321 | -0.18768 | 0.10071 | 121.5866 | 3.3371 | 0.47607 | 0.59967 | 122.4106 | -0.21973 | -0.11444 | -0.050354 | 0.059509 | 0.17395 | -0.6958 | -0.14649 | 0.12817 | 0.17395 | 0.54932 | 0.67291 | 121.6599 | 122.3053 | 0.059509 | 122.4838 | 3.4103 | -0.14649 | 122.3053 | 0.059509 | 3.4103 | 121.6599 | 122.4838 | -122.4701 | -122.5021
2924.2812 | 122.3557 | -0.082397 | 122.2275 | -0.20561 | 0.009628 | -0.012764 | 0.012117 | 0.048619 | -0.012245 | 0.067116 | -0.059509 | 122.2458 | -0.19226 | 0.036621 | 121.5317 | 3.3142 | 0.60425 | 0.60883 | 122.3877 | -0.24261 | -0.10986 | 0.018311 | 0.022888 | 0.11902 | -0.6958 | -0.16022 | 0.16022 | 0.13275 | 0.68664 | 0.69122 | 121.6141 | 122.3282 | 0.022888 | 122.4701 | 3.3966 | -0.16022 | 122.3282 | 0.022888 | 3.3966 | 121.6141 | 122.4701 | -122.4197 | -122.4701
2926.0312 | 122.4289 | -0.045776 | 122.2092 | -0.053024 | 0.0085598 | -0.0102 | 0.0069898 | 0.047978 | -0.009895 | 0.06733 | 0.013733 | 122.2412 | -0.15106 | 0.11444 | 121.6324 | 3.3279 | 0.36163 | 0.63171 | 122.3511 | -0.20599 | -0.10529 | 0.032044 | 0.059509 | 0.16022 | -0.57678 | -0.16022 | 0.14191 | 0.16479 | 0.40741 | 0.67749 | 121.6782 | 122.287 | 0.059509 | 122.3969 | 3.3737 | -0.16022 | 122.287 | 0.059509 | 3.3737 | 121.6782 | 122.3969 | -122.3602 | -122.4152
2927.7812 | 122.3007 | -0.10071 | 122.2641 | -0.11406 | 0.0092008 | -0.0069961 | 0.013826 | 0.048832 | -0.012031 | 0.065834 | 0.013733 | 122.2366 | -0.17395 | 0.10529 | 121.5683 | 3.3463 | 0.45776 | 0.57678 | 122.4289 | -0.21973 | -0.073242 | -0.027466 | 0.11444 | 0.20599 | -0.6958 | -0.11902 | 0.16479 | 0.18768 | 0.55847 | 0.67749 | 121.669 | 122.3373 | 0.11444 | 122.5296 | 3.447 | -0.11902 | 122.3373 | 0.11444 | 3.447 | 121.669 | 122.5296 | -122.438 | -122.4838
2929.5469 | 122.3328 | -0.11444 | 122.2458 | -0.18272 | 0.0098416 | -0.0087051 | 0.0076306 | 0.046269 | -0.01075 | 0.067116 | 0.036621 | 122.2458 | -0.15564 | 0.15106 | 121.6461 | 3.4149 | 0.48523 | 0.75531 | 122.3419 | -0.18768 | -0.041199 | 0 | 0.15106 | 0.2655 | -0.59967 | -0.073242 | 0.09613 | 0.19226 | 0.59967 | 0.86975 | 121.7606 | 122.3602 | 0.15106 | 122.4564 | 3.5294 | -0.073242 | 122.3602 | 0.15106 | 3.5294 | 121.7606 | 122.4564 | -122.4014 | -122.4335
2931.2969 | 122.3145 | -0.068665 | 122.2595 | -0.16747 | 0.0092008 | -0.0089189 | 0.014467 | 0.049046 | -0.014595 | 0.065193 | -0.027466 | 122.2733 | -0.18768 | 0.082397 | 121.5775 | 3.36 | 0.50354 | 0.59509 | 122.4243 | -0.20599 | -0.11902 | 0.013733 | 0.041199 | 0.15106 | -0.68207 | -0.13733 | 0.16479 | 0.16022 | 0.5722 | 0.66376 | 121.6461 | 122.3419 | 0.041199 | 122.493 | 3.4287 | -0.13733 | 122.3419 | 0.041199 | 3.4287 | 121.6461 | 122.493 | -122.4472 | -122.4655
2933.0469 | 122.3419 | -0.086975 | 122.2412 | 0.02327 | 0.0089872 | -0.0065689 | 0.014467 | 0.050755 | -0.015236 | 0.065621 | -0.018311 | 122.2412 | -0.20142 | 0.059509 | 121.5271 | 3.2364 | 0.33417 | 0.37994 | 122.4243 | -0.21057 | -0.11444 | 0 | 0.068664 | 0.14648 | -0.71411 | -0.1236 | 0.1831 | 0.18311 | 0.42114 | 0.46692 | 121.6141 | 122.3282 | 0.068664 | 122.5113 | 3.3234 | -0.1236 | 122.3282 | 0.068664 | 3.3234 | 121.6141 | 122.5113 | -122.4426 | -122.4518
2934.7344 | 122.4518 | -0.032043 | 122.2183 | 0.084305 | 0.010482 | -0.0097733 | 0.012117 | 0.049046 | -0.012031 | 0.066689 | -0.054932 | 122.2321 | -0.16022 | 0.036621 | 121.5408 | 3.1769 | 0.24261 | 0.30212 | 122.3785 | -0.2243 | -0.12817 | 0.013733 | -0.022889 | 0.068664 | -0.67749 | -0.19226 | 0.16022 | 0.10528 | 0.27466 | 0.33417 | 121.5729 | 122.2641 | -0.022889 | 122.4106 | 3.2089 | -0.19226 | 122.2641 | -0.022889 | 3.2089 | 121.5729 | 122.4106 | -122.3785 | -122.4426
2936.4844 | 122.4243 | -0.059509 | 122.2366 | 0.061417 | 0.011551 | -0.0065689 | 0.013398 | 0.050968 | -0.015663 | 0.067543 | -0.036621 | 122.2504 | -0.16937 | 0.022888 | 121.5088 | 3.1815 | 0.35248 | 0.32959 | 122.4289 | -0.2243 | -0.10986 | 0.013733 | 0.022888 | 0.082397 | -0.72784 | -0.16479 | 0.19226 | 0.13275 | 0.41199 | 0.3891 | 121.5683 | 122.3099 | 0.022888 | 122.4884 | 3.241 | -0.16479 | 122.3099 | 0.022888 | 3.241 | 121.5683 | 122.4884 | -122.406 | -122.4609
2938.2344 | 122.4564 | -0.064087 | 122.2046 | 0.00038159 | 0.011123 | -0.010841 | 0.0069898 | 0.048832 | -0.012886 | 0.065834 | -0.027466 | 122.2229 | -0.13733 | 0.064087 | 121.5912 | 3.2776 | 0.35248 | 0.55847 | 122.3785 | -0.19684 | -0.073242 | 0.01831 | 0.036621 | 0.12817 | -0.6134 | -0.13275 | 0.17395 | 0.10986 | 0.41657 | 0.62256 | 121.6553 | 122.287 | 0.036621 | 122.4426 | 3.3417 | -0.13275 | 122.287 | 0.036621 | 3.3417 | 121.6553 | 122.4426 | -122.3419 | -122.4014
2939.9375 | 122.3785 | -0.073242 | 122.2412 | -0.25902 | 0.0098416 | -0.012764 | 0.01233 | 0.048191 | -0.012886 | 0.06733 | -0.07782 | 122.2366 | -0.18768 | 0.036621 | 121.5271 | 3.3188 | 0.64545 | 0.61798 | 122.4014 | -0.24261 | -0.11444 | -0.004578 | -0.004578 | 0.10986 | -0.71411 | -0.16937 | 0.16022 | 0.10986 | 0.71869 | 0.69122 | 121.6003 | 122.3099 | -0.004578 | 122.4747 | 3.392 | -0.16937 | 122.3099 | -0.004578 | 3.392 | 121.6003 | 122.4747 | -122.4289 | -122.4838
2941.7031 | 122.3099 | -0.082397 | 122.2504 | -0.12169 | 0.011764 | -0.0097733 | 0.015748 | 0.048405 | -0.012886 | 0.065193 | 0.009155 | 122.2824 | -0.16022 | 0.091553 | 121.5683 | 3.3463 | 0.45319 | 0.56763 | 122.374 | -0.2243 | -0.07782 | 0.032044 | 0.091552 | 0.17395 | -0.68207 | -0.14191 | 0.1236 | 0.16937 | 0.53558 | 0.65002 | 121.6507 | 122.3648 | 0.091552 | 122.4564 | 3.4286 | -0.14191 | 122.3648 | 0.091552 | 3.4286 | 121.6507 | 122.4564 | -122.4106 | -122.4747
2943.4062 | 122.4518 | -0.045776 | 122.2137 | 0.02327 | 0.010269 | -0.011269 | 0.0061352 | 0.050328 | -0.009895 | 0.066048 | -0.022888 | 122.2595 | -0.13733 | 0.068665 | 121.5912 | 3.2867 | 0.35248 | 0.55847 | 122.406 | -0.20599 | -0.091553 | 0.045776 | 0.022888 | 0.11444 | -0.62256 | -0.16022 | 0.19226 | 0.11444 | 0.39825 | 0.60425 | 121.637 | 122.3053 | 0.022888 | 122.4518 | 3.3325 | -0.16022 | 122.3053 | 0.022888 | 3.3325 | 121.637 | 122.4518 | -122.3511 | -122.4197
2945.1562 | 122.438 | -0.050354 | 122.1954 | 0.076676 | 0.012405 | -0.010841 | 0.013398 | 0.046696 | -0.01139 | 0.068825 | -0.064087 | 122.319 | -0.17853 | 0.022888 | 121.4996 | 3.2043 | 0.29755 | 0.31586 | 122.3923 | -0.24719 | -0.12817 | 0.1236 | -0.013733 | 0.073242 | -0.6958 | -0.19684 | 0.19684 | 0.11444 | 0.3479 | 0.36621 | 121.55 | 122.3694 | -0.013733 | 122.4426 | 3.2547 | -0.19684 | 122.3694 | -0.013733 | 3.2547 | 121.55 | 122.4426 | -122.374 | -122.4426
2946.9219 | 122.3602 | -0.10071 | 122.2183 | 0.030899 | 0.010482 | -0.010841 | 0.016816 | 0.052037 | -0.014595 | 0.066475 | -0.022888 | 122.2458 | -0.17395 | 0.050354 | 121.5271 | 3.2318 | 0.3479 | 0.37537 | 122.4106 | -0.21973 | -0.073242 | 0.027466 | 0.07782 | 0.15106 | -0.69122 | -0.11902 | 0.19226 | 0.15106 | 0.44861 | 0.47607 | 121.6278 | 122.3465 | 0.07782 | 122.5113 | 3.3325 | -0.11902 | 122.3465 | 0.07782 | 3.3325 | 121.6278 | 122.5113 | -122.3923 | -122.4381
2948.6719 | 122.3053 | -0.091553 | 122.2595 | -0.12932 | 0.0089872 | -0.014046 | 0.013826 | 0.048405 | -0.012672 | 0.067116 | -0.004578 | 122.2595 | -0.17853 | 0.091553 | 121.5775 | 3.3554 | 0.48065 | 0.59509 | 122.4152 | -0.21515 | -0.086975 | 0 | 0.086975 | 0.18311 | -0.68207 | -0.1236 | 0.15564 | 0.17395 | 0.57221 | 0.68665 | 121.669 | 122.3511 | 0.086975 | 122.5067 | 3.447 | -0.1236 | 122.3511 | 0.086975 | 3.447 | 121.669 | 122.5067 | -122.438 | -122.4747
2950.3594 | 122.4152 | -0.073242 | 122.2229 | 0.14534 | 0.010269 | -0.0078507 | 0.010194 | 0.050114 | -0.015876 | 0.065834 | 0.013733 | 122.2275 | -0.13733 | 0.11444 | 121.6141 | 3.2593 | 0.14191 | 0.39825 | 122.3969 | -0.19226 | -0.064087 | 0.004578 | 0.086975 | 0.18768 | -0.60882 | -0.11902 | 0.17395 | 0.15106 | 0.21515 | 0.4715 | 121.6873 | 122.3007 | 0.086975 | 122.4701 | 3.3325 | -0.11902 | 122.3007 | 0.086975 | 3.3325 | 121.6873 | 122.4701 | -122.3602 | -122.4152
2952.125 | 122.319 | -0.10529 | 122.2595 | -0.22087 | 0.0085598 | -0.013832 | 0.0069898 | 0.048832 | -0.013099 | 0.066689 | 0.059509 | 122.2229 | -0.14648 | 0.15106 | 121.669 | 3.4561 | 0.47607 | 0.78735 | 122.3969 | -0.1831 | -0.041198 | -0.036621 | 0.16479 | 0.25635 | -0.59052 | -0.077819 | 0.13733 | 0.20599 | 0.58136 | 0.89264 | 121.7743 | 122.3282 | 0.16479 | 122.5021 | 3.5614 | -0.077819 | 122.3282 | 0.16479 | 3.5614 | 121.7743 | 122.5021 | -122.406 | -122.4426
2953.9062 | 122.438 | -0.059509 | 122.2 | 0.11482 | 0.010482 | -0.013405 | 0.0093396 | 0.050114 | -0.01075 | 0.067116 | 0.054932 | 122.2229 | -0.12817 | 0.11902 | 121.6095 | 3.2639 | 0.18768 | 0.48523 | 122.3694 | -0.20142 | -0.068665 | 0.022888 | 0.11444 | 0.17853 | -0.59051 | -0.14191 | 0.16937 | 0.18311 | 0.24719 | 0.54474 | 121.669 | 122.2824 | 0.11444 | 122.4289 | 3.3234 | -0.14191 | 122.2824 | 0.11444 | 3.3234 | 121.669 | 122.4289 | -122.3282 | -122.4014
2955.6562 | 122.3282 | -0.10529 | 122.287 | -0.068283 | 0.010055 | -0.0082779 | 0.016176 | 0.048832 | -0.014381 | 0.065621 | 0.013733 | 122.2504 | -0.17395 | 0.091553 | 121.5729 | 3.3371 | 0.38452 | 0.52185 | 122.4152 | -0.21057 | -0.068664 | -0.036621 | 0.11902 | 0.19684 | -0.71411 | -0.10529 | 0.12817 | 0.18768 | 0.48981 | 0.62714 | 121.6782 | 122.3557 | 0.11902 | 122.5204 | 3.4424 | -0.10529 | 122.3557 | 0.11902 | 3.4424 | 121.6782 | 122.5204 | -122.4609 | -122.4976
2957.3438 | 122.4197 | -0.064087 | 122.2275 | 0.091934 | 0.011123 | -0.011482 | 0.0093396 | 0.049687 | -0.013099 | 0.063912 | 0.036621 | 122.2183 | -0.1236 | 0.12817 | 121.6187 | 3.2867 | 0.15106 | 0.46234 | 122.3785 | -0.17853 | -0.059509 | -0.009155 | 0.10071 | 0.19226 | -0.60883 | -0.11444 | 0.15106 | 0.16022 | 0.21515 | 0.52643 | 121.6827 | 122.2824 | 0.10071 | 122.4426 | 3.3508 | -0.11444 | 122.2824 | 0.10071 | 3.3508 | 121.6827 | 122.4426 | -122.3511 | -122.406
2959.1094 | 122.4335 | -0.054932 | 122.2321 | -0.045395 | 0.01091 | -0.010414 | 0.007417 | 0.047764 | -0.010322 | 0.067757 | 0.004578 | 122.2504 | -0.13733 | 0.11902 | 121.637 | 3.3554 | 0.38452 | 0.64545 | 122.3831 | -0.20142 | -0.082397 | 0.01831 | 0.05951 | 0.17395 | -0.59509 | -0.14648 | 0.15106 | 0.14191 | 0.43945 | 0.70038 | 121.6919 | 122.3053 | 0.05951 | 122.438 | 3.4103 | -0.14648 | 122.3053 | 0.05951 | 3.4103 | 121.6919 | 122.438 | -122.3694 | -122.4335
2960.7969 | 122.374 | -0.10071 | 122.2504 | -0.23613 | 0.011551 | -0.013618 | 0.014039 | 0.04755 | -0.013527 | 0.066902 | -0.050354 | 122.2549 | -0.16479 | 0.041199 | 121.5408 | 3.36 | 0.63629 | 0.64545 | 122.406 | -0.23346 | -0.064087 | 0.004578 | 0.050354 | 0.14191 | -0.70953 | -0.13275 | 0.15564 | 0.11444 | 0.737 | 0.74616 | 121.6415 | 122.3557 | 0.050354 | 122.5067 | 3.4607 | -0.13275 | 122.3557 | 0.050354 | 3.4607 | 121.6415 | 122.5067 | -122.4152 | -122.4838
2962.5469 | 122.3831 | -0.07782 | 122.2229 | -0.10643 | 0.009628 | -0.0076371 | 0.0086988 | 0.046269 | -0.010536 | 0.067543 | 0.045776 | 122.2458 | -0.13275 | 0.15106 | 121.6553 | 3.4012 | 0.37994 | 0.70496 | 122.3511 | -0.17395 | -0.054931 | 0.022889 | 0.1236 | 0.22888 | -0.56763 | -0.09613 | 0.12817 | 0.17853 | 0.45776 | 0.78278 | 121.7331 | 122.3236 | 0.1236 | 122.4289 | 3.479 | -0.09613 | 122.3236 | 0.1236 | 3.479 | 121.7331 | 122.4289 | -122.3557 | -122.3969
2964.3125 | 122.3282 | -0.10071 | 122.2549 | -0.13695 | 0.0066372 | -0.012337 | 0.010621 | 0.046269 | -0.012458 | 0.065621 | 0.073242 | 122.2275 | -0.16022 | 0.15564 | 121.6736 | 3.447 | 0.4303 | 0.76446 | 122.3694 | -0.20142 | -0.059509 | -0.027466 | 0.17395 | 0.25635 | -0.58136 | -0.10071 | 0.11444 | 0.23346 | 0.53101 | 0.86517 | 121.7743 | 122.3282 | 0.17395 | 122.4701 | 3.5477 | -0.10071 | 122.3282 | 0.17395 | 3.5477 | 121.7743 | 122.4701 | -122.4152 | -122.4564
2966 | 122.3648 | -0.086975 | 122.2549 | -0.26665 | 0.0089872 | -0.0099869 | 0.013826 | 0.046055 | -0.013954 | 0.065834 | -0.064087 | 122.2641 | -0.19684 | 0.041199 | 121.5363 | 3.3463 | 0.65002 | 0.63171 | 122.4197 | -0.24261 | -0.10986 | 0.009155 | 0.022888 | 0.12817 | -0.71869 | -0.15564 | 0.1648 | 0.13275 | 0.737 | 0.71869 | 121.6232 | 122.3511 | 0.022888 | 122.5067 | 3.4332 | -0.15564 | 122.3511 | 0.022888 | 3.4332 | 121.6232 | 122.5067 | -122.4518 | -122.4976
2967.75 | 122.4243 | -0.064087 | 122.2687 | 0.10719 | 0.010055 | -0.010841 | 0.011049 | 0.047978 | -0.01075 | 0.068611 | 0.064087 | 122.2504 | -0.13275 | 0.14191 | 121.6187 | 3.2913 | 0.15564 | 0.47607 | 122.374 | -0.19226 | -0.068664 | -0.018311 | 0.12817 | 0.20599 | -0.65002 | -0.12817 | 0.10529 | 0.19684 | 0.21973 | 0.54016 | 121.6827 | 122.3145 | 0.12817 | 122.438 | 3.3554 | -0.12817 | 122.3145 | 0.12817 | 3.3554 | 121.6827 | 122.438 | -122.4014 | -122.4609
2969.4531 | 122.406 | -0.073242 | 122.1954 | 0.13008 | 0.010696 | -0.0087051 | 0.010835 | 0.049259 | -0.010963 | 0.066262 | 0.054932 | 122.2366 | -0.15564 | 0.15564 | 121.6278 | 3.3005 | 0.1236 | 0.47607 | 122.3694 | -0.16479 | -0.082398 | 0.041198 | 0.12817 | 0.22888 | -0.56763 | -0.091553 | 0.17395 | 0.21057 | 0.19684 | 0.54932 | 121.701 | 122.3099 | 0.12817 | 122.4426 | 3.3737 | -0.091553 | 122.3099 | 0.12817 | 3.3737 | 121.701 | 122.4426 | -122.3511 | -122.3602
2971.2031 | 122.3694 | -0.10071 | 122.2321 | -0.24376 | 0.0098416 | -0.011269 | 0.012971 | 0.048619 | -0.014381 | 0.066689 | -0.07782 | 122.2504 | -0.19226 | 0.045776 | 121.5591 | 3.3417 | 0.65002 | 0.64545 | 122.4197 | -0.23346 | -0.091553 | 0.01831 | 0.022888 | 0.14648 | -0.67291 | -0.13275 | 0.18768 | 0.11444 | 0.75073 | 0.74616 | 121.6599 | 122.3511 | 0.022888 | 122.5204 | 3.4424 | -0.13275 | 122.3511 | 0.022888 | 3.4424 | 121.6599 | 122.5204 | -122.4243 | -122.4655
2972.9688 | 122.4243 | -0.064087 | 122.2092 | 0.11482 | 0.0070646 | -0.012337 | 0.0095532 | 0.048619 | -0.011818 | 0.065621 | 0.027466 | 122.2229 | -0.15564 | 0.11444 | 121.6141 | 3.2867 | 0.17395 | 0.46692 | 122.3557 | -0.16937 | -0.091553 | 0.013733 | 0.091553 | 0.17853 | -0.59509 | -0.10529 | 0.14649 | 0.18311 | 0.23804 | 0.53101 | 121.6782 | 122.287 | 0.091553 | 122.4197 | 3.3508 | -0.10529 | 122.287 | 0.091553 | 3.3508 | 121.6782 | 122.4197 | -122.3648 | -122.3785
2974.6562 | 122.3785 | -0.073242 | 122.2549 | -0.23613 | 0.011551 | -0.017891 | 0.012971 | 0.0499 | -0.014167 | 0.065407 | -0.050354 | 122.2366 | -0.1831 | 0.045776 | 121.5317 | 3.3554 | 0.65002 | 0.62256 | 122.4426 | -0.2243 | -0.10986 | -0.018311 | 0.022888 | 0.11902 | -0.72327 | -0.15106 | 0.18768 | 0.13275 | 0.72327 | 0.6958 | 121.6049 | 122.3099 | 0.022888 | 122.5159 | 3.4287 | -0.15106 | 122.3099 | 0.022888 | 3.4287 | 121.6049 | 122.5159 | -122.438 | -122.4792
2976.4062 | 122.374 | -0.10071 | 122.2412 | -0.24376 | 0.010696 | -0.013191 | 0.011903 | 0.047337 | -0.012886 | 0.06498 | 0.004578 | 122.2687 | -0.17395 | 0.07782 | 121.5775 | 3.3737 | 0.62714 | 0.67749 | 122.4335 | -0.21057 | -0.073242 | 0.027466 | 0.10529 | 0.17853 | -0.66376 | -0.10986 | 0.19226 | 0.17853 | 0.72784 | 0.7782 | 121.6782 | 122.3694 | 0.10529 | 122.5342 | 3.4744 | -0.10986 | 122.3694 | 0.10529 | 3.4744 | 121.6782 | 122.5342 | -122.4152 | -122.4518
2978.0938 | 122.374 | -0.086975 | 122.2275 | 0.046158 | 0.010482 | -0.0095597 | 0.015748 | 0.049687 | -0.01609 | 0.064125 | -0.027466 | 122.2229 | -0.1831 | 0.041199 | 121.5225 | 3.2547 | 0.33875 | 0.37079 | 122.4243 | -0.21515 | -0.09613 | -0.004578 | 0.059509 | 0.12817 | -0.70496 | -0.12817 | 0.19684 | 0.15564 | 0.42572 | 0.45776 | 121.6095 | 122.3099 | 0.059509 | 122.5113 | 3.3417 | -0.12817 | 122.3099 | 0.059509 | 3.3417 | 121.6095 | 122.5113 | -122.4106 | -122.4426
2979.8438 | 122.3511 | -0.10529 | 122.2275 | -0.014877 | 0.0094144 | -0.013191 | 0.015321 | 0.050755 | -0.015663 | 0.067116 | -0.013733 | 122.2229 | -0.17853 | 0.054932 | 121.5546 | 3.2913 | 0.35248 | 0.43945 | 122.4243 | -0.21515 | -0.073242 | -0.004578 | 0.091553 | 0.16022 | -0.67291 | -0.10986 | 0.19684 | 0.16479 | 0.45776 | 0.54474 | 121.6599 | 122.3282 | 0.091553 | 122.5296 | 3.3966 | -0.10986 | 122.3282 | 0.091553 | 3.3966 | 121.6599 | 122.5296 | -122.406 | -122.4426
2981.6094 | 122.438 | -0.050354 | 122.2046 | -0.022507 | 0.010269 | -0.0099869 | 0.0042126 | 0.049046 | -0.011818 | 0.06498 | 0.013733 | 122.2504 | -0.15106 | 0.10986 | 121.6278 | 3.3417 | 0.3479 | 0.60425 | 122.3831 | -0.21973 | -0.10071 | 0.045776 | 0.064087 | 0.16022 | -0.57678 | -0.16937 | 0.17853 | 0.16479 | 0.39825 | 0.6546 | 121.6782 | 122.3007 | 0.064087 | 122.4335 | 3.392 | -0.16937 | 122.3007 | 0.064087 | 3.392 | 121.6782 | 122.4335 | -122.3557 | -122.4243
2983.3125 | 122.3373 | -0.091553 | 122.2504 | -0.15221 | 0.010055 | -0.0069961 | 0.010621 | 0.047123 | -0.011818 | 0.066689 | 0.068665 | 122.1817 | -0.14191 | 0.16022 | 121.6873 | 3.4653 | 0.41657 | 0.74158 | 122.3648 | -0.20142 | -0.050354 | -0.068664 | 0.16022 | 0.25177 | -0.56305 | -0.10986 | 0.11444 | 0.21057 | 0.50812 | 0.83313 | 121.7789 | 122.2733 | 0.16022 | 122.4564 | 3.5568 | -0.10986 | 122.2733 | 0.16022 | 3.5568 | 121.7789 | 122.4564 | -122.3923 | -122.4518
2985.0781 | 122.3236 | -0.10529 | 122.2641 | -0.060654 | 0.011551 | -0.010628 | 0.016816 | 0.049046 | -0.013313 | 0.065621 | 0.013733 | 122.2366 | -0.19226 | 0.11444 | 121.5683 | 3.3508 | 0.37537 | 0.50354 | 122.4014 | -0.2243 | -0.086975 | -0.027466 | 0.11902 | 0.21973 | -0.6958 | -0.11902 | 0.13733 | 0.20599 | 0.48065 | 0.60883 | 121.6736 | 122.3419 | 0.11902 | 122.5067 | 3.4561 | -0.11902 | 122.3419 | 0.11902 | 3.4561 | 121.6736 | 122.5067 | -122.4564 | -122.4884
2986.7656 | 122.3328 | -0.10529 | 122.2687 | -0.16747 | 0.0081326 | -0.0078507 | 0.005708 | 0.046482 | -0.012458 | 0.06733 | 0.059509 | 122.2321 | -0.13733 | 0.15564 | 121.6736 | 3.4698 | 0.44403 | 0.76904 | 122.3465 | -0.20599 | -0.032043 | -0.036621 | 0.16479 | 0.26093 | -0.59509 | -0.10071 | 0.07782 | 0.19684 | 0.54932 | 0.87433 | 121.7789 | 122.3373 | 0.16479 | 122.4518 | 3.5751 | -0.10071 | 122.3373 | 0.16479 | 3.5751 | 121.7789 | 122.4518 | -122.406 | -122.4747
2988.5156 | 122.4106 | -0.073242 | 122.2412 | 0.099564 | 0.0094144 | -0.0067825 | 0.010408 | 0.047337 | -0.012672 | 0.066902 | 0.050354 | 122.2229 | -0.14648 | 0.13275 | 121.6324 | 3.3142 | 0.13733 | 0.47607 | 122.3557 | -0.19226 | -0.073242 | -0.018311 | 0.1236 | 0.20599 | -0.60883 | -0.11902 | 0.11444 | 0.19684 | 0.21057 | 0.54932 | 121.7056 | 122.2961 | 0.1236 | 122.4289 | 3.3875 | -0.11902 | 122.2961 | 0.1236 | 3.3875 | 121.7056 | 122.4289 | -122.3877 | -122.4335
2990.2031 | 122.3602 | -0.068665 | 122.2504 | -0.19798 | 0.010482 | -0.011696 | 0.013398 | 0.04691 | -0.013954 | 0.065407 | -0.041199 | 122.2916 | -0.1831 | 0.050354 | 121.55 | 3.3829 | 0.60883 | 0.61798 | 122.4243 | -0.24261 | -0.11444 | 0.041199 | 0.027466 | 0.11902 | -0.70038 | -0.17395 | 0.17395 | 0.14191 | 0.67749 | 0.68665 | 121.6187 | 122.3602 | 0.027466 | 122.493 | 3.4515 | -0.17395 | 122.3602 | 0.027466 | 3.4515 | 121.6187 | 122.493 | -122.4335 | -122.493
2991.9688 | 122.406 | -0.050354 | 122.2275 | 0.27504 | 0.0098416 | -0.011909 | 0.011903 | 0.048619 | -0.012031 | 0.06498 | 0.059509 | 122.2275 | -0.15106 | 0.14191 | 121.6278 | 3.3051 | 0.10986 | 0.43488 | 122.374 | -0.17395 | -0.10071 | 0 | 0.10986 | 0.19226 | -0.59967 | -0.1236 | 0.14648 | 0.21057 | 0.16022 | 0.48523 | 121.6782 | 122.2778 | 0.10986 | 122.4243 | 3.3554 | -0.1236 | 122.2778 | 0.10986 | 3.3554 | 121.6782 | 122.4243 | -122.3785 | -122.4014
2993.7344 | 122.4335 | -0.059509 | 122.2366 | 0.10719 | 0.012405 | -0.011696 | 0.014039 | 0.050541 | -0.012245 | 0.065407 | -0.027466 | 122.2687 | -0.16022 | 0.045776 | 121.5454 | 3.2455 | 0.21057 | 0.33417 | 122.4197 | -0.21057 | -0.10071 | 0.032044 | 0.032043 | 0.10528 | -0.69122 | -0.15106 | 0.18311 | 0.13275 | 0.27008 | 0.39368 | 121.6049 | 122.3282 | 0.032043 | 122.4792 | 3.3051 | -0.15106 | 122.3282 | 0.032043 | 3.3051 | 121.6049 | 122.4792 | -122.3969 | -122.4472
2995.4844 | 122.3145 | -0.10071 | 122.2778 | -0.098801 | 0.011337 | -0.0087051 | 0.015748 | 0.04691 | -0.012886 | 0.066475 | 0.018311 | 122.2549 | -0.18768 | 0.10986 | 121.5775 | 3.36 | 0.3891 | 0.52185 | 122.3969 | -0.21515 | -0.086975 | -0.022888 | 0.11902 | 0.21057 | -0.70038 | -0.11444 | 0.11902 | 0.20599 | 0.48981 | 0.62256 | 121.6782 | 122.3557 | 0.11902 | 122.4976 | 3.4607 | -0.11444 | 122.3557 | 0.11902 | 3.4607 | 121.6782 | 122.4976 | -122.4655 | -122.493
2997.1875 | 122.3602 | -0.086975 | 122.2549 | -0.25139 | 0.0092008 | -0.011269 | 0.0065624 | 0.04755 | -0.013099 | 0.065407 | -0.013733 | 122.2458 | -0.16937 | 0.064087 | 121.5729 | 3.4149 | 0.63629 | 0.68665 | 122.406 | -0.21515 | -0.082398 | -0.009155 | 0.073242 | 0.15106 | -0.68207 | -0.12817 | 0.15106 | 0.15564 | 0.72327 | 0.77362 | 121.6599 | 122.3328 | 0.073242 | 122.493 | 3.5019 | -0.12817 | 122.3328 | 0.073242 | 3.5019 | 121.6599 | 122.493 | -122.4243 | -122.4701
2998.9531 | 122.4197 | -0.064087 | 122.2549 | 0.099564 | 0.0081326 | -0.0093461 | 0.010621 | 0.049473 | -0.012672 | 0.066689 | 0.045776 | 122.2229 | -0.13275 | 0.12817 | 121.6324 | 3.3188 | 0.16479 | 0.4715 | 122.3557 | -0.20599 | -0.068664 | -0.032044 | 0.10986 | 0.19226 | -0.62256 | -0.14191 | 0.10071 | 0.17853 | 0.22888 | 0.53558 | 121.6965 | 122.287 | 0.10986 | 122.4197 | 3.3829 | -0.14191 | 122.287 | 0.10986 | 3.3829 | 121.6965 | 122.4197 | -122.3877 | -122.4609
3000.7188 | 122.4197 | -0.041199 | 122.2275 | 0.10719 | 0.0072782 | -0.011909 | 0.0095532 | 0.046482 | -0.011177 | 0.067116 | 0.050354 | 122.2595 | -0.12817 | 0.14648 | 121.6415 | 3.3234 | 0.13733 | 0.4715 | 122.3282 | -0.20599 | -0.086975 | 0.032043 | 0.091553 | 0.18768 | -0.58594 | -0.1648 | 0.10071 | 0.17853 | 0.17853 | 0.5127 | 121.6827 | 122.3007 | 0.091553 | 122.3694 | 3.3646 | -0.1648 | 122.3007 | 0.091553 | 3.3646 | 121.6827 | 122.3694 | -122.3557 | -122.4335
3002.4844 | 122.4609 | -0.054932 | 122.2 | 0.084305 | 0.010055 | -0.0097733 | 0.011689 | 0.047123 | -0.01139 | 0.067116 | 0.013733 | 122.2504 | -0.14648 | 0.10986 | 121.6003 | 3.3096 | 0.23346 | 0.48981 | 122.3877 | -0.21973 | -0.091552 | 0.050354 | 0.068665 | 0.16479 | -0.59967 | -0.16479 | 0.18768 | 0.16022 | 0.28839 | 0.54474 | 121.6553 | 122.3053 | 0.068665 | 122.4426 | 3.3646 | -0.16479 | 122.3053 | 0.068665 | 3.3646 | 121.6553 | 122.4426 | -122.3465 | -122.4197
3004.1875 | 122.4518 | -0.036621 | 122.2366 | 0.01564 | 0.010269 | -0.0080643 | 0.0080578 | 0.046482 | -0.01139 | 0.066689 | -0.018311 | 122.2641 | -0.16022 | 0.082397 | 121.5912 | 3.3371 | 0.36163 | 0.56763 | 122.3648 | -0.21057 | -0.1236 | 0.027466 | 0.01831 | 0.11902 | -0.64545 | -0.17395 | 0.12817 | 0.14191 | 0.39825 | 0.60425 | 121.6278 | 122.3007 | 0.01831 | 122.4014 | 3.3737 | -0.17395 | 122.3007 | 0.01831 | 3.3737 | 121.6278 | 122.4014 | -122.3969 | -122.4472
3005.9375 | 122.4472 | -0.054932 | 122.2412 | 0.10719 | 0.0094144 | -0.0087051 | 0.011476 | 0.045201 | -0.010322 | 0.066262 | 0.036621 | 122.2321 | -0.15106 | 0.10529 | 121.6141 | 3.3005 | 0.2243 | 0.49439 | 122.3557 | -0.21057 | -0.09613 | -0.009155 | 0.091553 | 0.16022 | -0.62714 | -0.15564 | 0.11444 | 0.18768 | 0.27924 | 0.54932 | 121.669 | 122.287 | 0.091553 | 122.4106 | 3.3554 | -0.15564 | 122.287 | 0.091553 | 3.3554 | 121.669 | 122.4106 | -122.3923 | -122.4518
3007.6875 | 122.3785 | -0.054932 | 122.2366 | 0.15297 | 0.0089872 | -0.0059281 | 0.01468 | 0.050328 | -0.013099 | 0.065407 | 0.027466 | 122.2046 | -0.15564 | 0.13275 | 121.6049 | 3.3005 | 0.10529 | 0.42572 | 122.3831 | -0.17853 | -0.10071 | -0.032043 | 0.082398 | 0.18768 | -0.63171 | -0.1236 | 0.14648 | 0.18311 | 0.16022 | 0.48065 | 121.6599 | 122.2595 | 0.082398 | 122.438 | 3.3554 | -0.1236 | 122.2595 | 0.082398 | 3.3554 | 121.6599 | 122.438 | -122.3923 | -122.4152
3009.4531 | 122.3145 | -0.10529 | 122.2687 | -0.19798 | 0.0072782 | -0.011696 | 0.010621 | 0.048832 | -0.01139 | 0.065621 | 0.054932 | 122.2549 | -0.13275 | 0.16022 | 121.669 | 3.4882 | 0.48065 | 0.79651 | 122.3602 | -0.20142 | -0.027465 | -0.013733 | 0.16022 | 0.2655 | -0.59967 | -0.09613 | 0.091552 | 0.18768 | 0.58594 | 0.9018 | 121.7743 | 122.3602 | 0.16022 | 122.4655 | 3.5934 | -0.09613 | 122.3602 | 0.16022 | 3.5934 | 121.7743 | 122.4655 | -122.4014 | -122.4701
3011.1562 | 122.3328 | -0.10071 | 122.2595 | -0.060654 | 0.0089872 | -0.0099869 | 0.017884 | 0.0499 | -0.014381 | 0.066048 | 0.018311 | 122.2458 | -0.17853 | 0.10529 | 121.5591 | 3.3554 | 0.37994 | 0.50354 | 122.406 | -0.21515 | -0.07782 | -0.013732 | 0.11902 | 0.20599 | -0.70038 | -0.11444 | 0.14648 | 0.19684 | 0.48065 | 0.60425 | 121.6599 | 122.3465 | 0.11902 | 122.5067 | 3.4561 | -0.11444 | 122.3465 | 0.11902 | 3.4561 | 121.6599 | 122.5067 | -122.438 | -122.4747
3012.9062 | 122.3694 | -0.07782 | 122.2321 | -0.25139 | 0.009628 | -0.0099869 | 0.012758 | 0.048405 | -0.01374 | 0.064766 | -0.050354 | 122.2641 | -0.19684 | 0.041199 | 121.5546 | 3.3875 | 0.64545 | 0.63629 | 122.438 | -0.2243 | -0.11902 | 0.032043 | 0.027466 | 0.11902 | -0.67749 | -0.14648 | 0.20599 | 0.14648 | 0.72327 | 0.71411 | 121.6324 | 122.3419 | 0.027466 | 122.5159 | 3.4653 | -0.14648 | 122.3419 | 0.027466 | 3.4653 | 121.6324 | 122.5159 | -122.4289 | -122.4564
3014.6719 | 122.4792 | -0.050354 | 122.2321 | 0.02327 | 0.0087734 | -0.0074235 | 0.0063488 | 0.048405 | -0.012886 | 0.066902 | 0 | 122.2458 | -0.14191 | 0.07782 | 121.6049 | 3.3325 | 0.32044 | 0.52185 | 122.4014 | -0.19226 | -0.091553 | 0.013733 | 0.050354 | 0.12817 | -0.62714 | -0.14191 | 0.16937 | 0.14191 | 0.37079 | 0.5722 | 121.6553 | 122.2961 | 0.050354 | 122.4518 | 3.3829 | -0.14191 | 122.2961 | 0.050354 | 3.3829 | 121.6553 | 122.4518 | -122.374 | -122.4243
3016.4219 | 122.406 | -0.064087 | 122.2549 | 0.19112 | 0.010269 | -0.011482 | 0.013612 | 0.048405 | -0.012458 | 0.06733 | -0.013733 | 122.2687 | -0.16937 | 0.09613 | 121.582 | 3.273 | 0.13733 | 0.37994 | 122.3694 | -0.19684 | -0.10529 | 0.013733 | 0.050354 | 0.16022 | -0.67291 | -0.13275 | 0.11444 | 0.15564 | 0.20142 | 0.44403 | 121.6461 | 122.3328 | 0.050354 | 122.4335 | 3.3371 | -0.13275 | 122.3328 | 0.050354 | 3.3371 | 121.6461 | 122.4335 | -122.4243 | -122.4518
3018.125 | 122.4747 | -0.045776 | 122.2458 | 0.01564 | 0.011764 | -0.011909 | 0.008485 | 0.04755 | -0.0083996 | 0.065834 | 0.009155 | 122.2687 | -0.15106 | 0.091553 | 121.6095 | 3.3188 | 0.32044 | 0.53558 | 122.3602 | -0.20599 | -0.10529 | 0.022888 | 0.054931 | 0.13733 | -0.63629 | -0.16022 | 0.11444 | 0.16022 | 0.36621 | 0.58136 | 121.6553 | 122.3145 | 0.054931 | 122.406 | 3.3646 | -0.16022 | 122.3145 | 0.054931 | 3.3646 | 121.6553 | 122.406 | -122.3969 | -122.4518
3019.8906 | 122.3694 | -0.086975 | 122.2504 | -0.23613 | 0.0092008 | -0.014473 | 0.012117 | 0.047123 | -0.012458 | 0.065621 | -0.059509 | 122.3007 | -0.19226 | 0.054932 | 121.5546 | 3.3966 | 0.66376 | 0.63629 | 122.4014 | -0.24261 | -0.10529 | 0.050354 | 0.027466 | 0.14191 | -0.6958 | -0.15564 | 0.15106 | 0.13275 | 0.75073 | 0.72327 | 121.6415 | 122.3877 | 0.027466 | 122.4884 | 3.4836 | -0.15564 | 122.3877 | 0.027466 | 3.4836 | 121.6415 | 122.4884 | -122.4426 | -122.493
3021.6406 | 122.3648 | -0.086975 | 122.2458 | -0.2285 | 0.01091 | -0.012978 | 0.014467 | 0.04755 | -0.013954 | 0.064553 | -0.054932 | 122.287 | -0.18768 | 0.059509 | 121.55 | 3.3966 | 0.63171 | 0.61798 | 122.4243 | -0.2243 | -0.10071 | 0.041198 | 0.032043 | 0.14648 | -0.6958 | -0.13733 | 0.17853 | 0.13275 | 0.71869 | 0.70496 | 121.637 | 122.374 | 0.032043 | 122.5113 | 3.4836 | -0.13733 | 122.374 | 0.032043 | 3.4836 | 121.637 | 122.5113 | -122.4335 | -122.4701
3023.3281 | 122.319 | -0.11444 | 122.2549 | -0.053024 | 0.0094144 | -0.012764 | 0.016816 | 0.050328 | -0.014167 | 0.066689 | 0.009155 | 122.2321 | -0.17395 | 0.10529 | 121.582 | 3.3875 | 0.3891 | 0.52643 | 122.3923 | -0.21515 | -0.059509 | -0.022888 | 0.1236 | 0.21973 | -0.67291 | -0.10071 | 0.13733 | 0.1831 | 0.50354 | 0.64087 | 121.6965 | 122.3465 | 0.1236 | 122.5067 | 3.5019 | -0.10071 | 122.3465 | 0.1236 | 3.5019 | 121.6965 | 122.5067 | -122.4289 | -122.4701
3025.1094 | 122.3465 | -0.091553 | 122.2412 | -0.22087 | 0.009628 | -0.013191 | 0.010194 | 0.046696 | -0.012886 | 0.066902 | 0.018311 | 122.2275 | -0.13275 | 0.11444 | 121.6461 | 3.479 | 0.57678 | 0.75989 | 122.3877 | -0.19684 | -0.041198 | -0.013733 | 0.10986 | 0.20599 | -0.59509 | -0.10529 | 0.14648 | 0.15106 | 0.66834 | 0.85144 | 121.7377 | 122.319 | 0.10986 | 122.4792 | 3.5706 | -0.10529 | 122.319 | 0.10986 | 3.5706 | 121.7377 | 122.4792 | -122.374 | -122.438
3026.875 | 122.3373 | -0.1236 | 122.2366 | -0.19798 | 0.0081326 | -0.0095597 | 0.0078442 | 0.047978 | -0.010536 | 0.067543 | 0.054932 | 122.2183 | -0.14648 | 0.1831 | 121.6644 | 3.5065 | 0.4715 | 0.78278 | 122.3877 | -0.20142 | -0.022888 | -0.01831 | 0.17853 | 0.3067 | -0.5722 | -0.07782 | 0.15106 | 0.20142 | 0.59509 | 0.90637 | 121.788 | 122.3419 | 0.17853 | 122.5113 | 3.6301 | -0.07782 | 122.3419 | 0.17853 | 3.6301 | 121.788 | 122.5113 | -122.3831 | -122.438
3028.6406 | 122.4289 | -0.064087 | 122.2092 | 0.053787 | 0.01091 | -0.0102 | 0.015748 | 0.051609 | -0.013313 | 0.066475 | -0.050354 | 122.2595 | -0.19226 | 0.018311 | 121.4905 | 3.2593 | 0.31128 | 0.33875 | 122.438 | -0.21973 | -0.12817 | 0.050354 | 0.013733 | 0.082398 | -0.71869 | -0.15564 | 0.22888 | 0.14191 | 0.37537 | 0.40283 | 121.5546 | 122.3236 | 0.013733 | 122.5021 | 3.3234 | -0.15564 | 122.3236 | 0.013733 | 3.3234 | 121.5546 | 122.5021 | -122.4014 | -122.4289
3030.3281 | 122.4197 | -0.082397 | 122.2275 | 0.084305 | 0.0070646 | -0.011482 | 0.007417 | 0.048191 | -0.009895 | 0.06797 | 0.041199 | 122.2549 | -0.13275 | 0.1236 | 121.6187 | 3.3417 | 0.14648 | 0.4715 | 122.3419 | -0.21057 | -0.050354 | 0.027466 | 0.1236 | 0.20599 | -0.60883 | -0.12817 | 0.11444 | 0.17395 | 0.22888 | 0.55389 | 121.701 | 122.3373 | 0.1236 | 122.4243 | 3.4241 | -0.12817 | 122.3373 | 0.1236 | 3.4241 | 121.701 | 122.4243 | -122.3602 | -122.438
3032.0938 | 122.3373 | -0.10529 | 122.2504 | -0.14458 | 0.011551 | -0.013618 | 0.0097668 | 0.04691 | -0.010963 | 0.063912 | 0.082397 | 122.2366 | -0.12817 | 0.16479 | 121.6736 | 3.5156 | 0.40741 | 0.737 | 122.3328 | -0.19684 | -0.022888 | -0.013733 | 0.18768 | 0.27008 | -0.57678 | -0.091552 | 0.082398 | 0.21057 | 0.5127 | 0.84229 | 121.7789 | 122.3419 | 0.18768 | 122.4381 | 3.6209 | -0.091552 | 122.3419 | 0.18768 | 3.6209 | 121.7789 | 122.4381 | -122.3785 | -122.4472
3033.7812 | 122.3099 | -0.082397 | 122.2321 | -0.091171 | 0.011764 | -0.011269 | 0.017457 | 0.047978 | -0.01139 | 0.067543 | 0.004578 | 122.2458 | -0.17853 | 0.10986 | 121.5958 | 3.4058 | 0.39825 | 0.54932 | 122.406 | -0.20599 | -0.096131 | 0.013733 | 0.086975 | 0.19226 | -0.63629 | -0.1236 | 0.17395 | 0.18311 | 0.48065 | 0.63171 | 121.6782 | 122.3282 | 0.086975 | 122.4884 | 3.4882 | -0.1236 | 122.3282 | 0.086975 | 3.4882 | 121.6782 | 122.4884 | -122.4106 | -122.4381
3035.5469 | 122.3373 | -0.10529 | 122.2595 | -0.12932 | 0.010269 | -0.0093461 | 0.009126 | 0.045201 | -0.012245 | 0.065407 | 0.054932 | 122.2595 | -0.12817 | 0.15564 | 121.6873 | 3.4882 | 0.43945 | 0.75989 | 122.3419 | -0.20142 | -0.022888 | 0 | 0.16022 | 0.26093 | -0.5722 | -0.09613 | 0.082398 | 0.18311 | 0.54474 | 0.86517 | 121.7926 | 122.3648 | 0.16022 | 122.4472 | 3.5934 | -0.09613 | 122.3648 | 0.16022 | 3.5934 | 121.7926 | 122.4472 | -122.3877 | -122.4609
3037.2969 | 122.4106 | -0.050354 | 122.2275 | 0.1606 | 0.0094144 | -0.0095597 | 0.014253 | 0.049046 | -0.010322 | 0.067757 | 0.032043 | 122.2916 | -0.15106 | 0.12817 | 121.6232 | 3.3142 | 0.11902 | 0.42114 | 122.3557 | -0.1831 | -0.10071 | 0.064087 | 0.082397 | 0.17853 | -0.60425 | -0.13275 | 0.12817 | 0.18311 | 0.16937 | 0.4715 | 121.6736 | 122.3419 | 0.082397 | 122.406 | 3.3646 | -0.13275 | 122.3419 | 0.082397 | 3.3646 | 121.6736 | 122.406 | -122.3785 | -122.4106
3039.0625 | 122.406 | -0.054932 | 122.2183 | 0.17586 | 0.011551 | -0.0097733 | 0.013185 | 0.046055 | -0.012672 | 0.066262 | 0.064087 | 122.2458 | -0.13733 | 0.16022 | 121.637 | 3.3508 | 0.091553 | 0.45776 | 122.3236 | -0.19226 | -0.082397 | 0.027466 | 0.11902 | 0.21515 | -0.58136 | -0.13733 | 0.10528 | 0.20142 | 0.14649 | 0.5127 | 121.6919 | 122.3007 | 0.11902 | 122.3785 | 3.4058 | -0.13733 | 122.3007 | 0.11902 | 3.4058 | 121.6919 | 122.3785 | -122.3557 | -122.4106
3040.7656 | 122.3099 | -0.10986 | 122.2504 | -0.15984 | 0.0098416 | -0.0069961 | 0.013826 | 0.04755 | -0.010109 | 0.065621 | -0.022888 | 122.2687 | -0.19226 | 0.11444 | 121.5775 | 3.4424 | 0.49896 | 0.6134 | 122.4197 | -0.20599 | -0.082398 | 0.018311 | 0.086975 | 0.2243 | -0.67291 | -0.096131 | 0.16937 | 0.16937 | 0.60883 | 0.72327 | 121.6873 | 122.3785 | 0.086975 | 122.5296 | 3.5522 | -0.096131 | 122.3785 | 0.086975 | 3.5522 | 121.6873 | 122.5296 | -122.4426 | -122.4564
3042.5156 | 122.4289 | -0.064087 | 122.2183 | 0.061417 | 0.011551 | -0.011909 | 0.013826 | 0.050328 | -0.015449 | 0.064553 | -0.068665 | 122.2549 | -0.20142 | 0.027466 | 121.5042 | 3.273 | 0.31128 | 0.33875 | 122.3877 | -0.23346 | -0.13733 | 0.036621 | -0.004578 | 0.091553 | -0.71411 | -0.16937 | 0.16937 | 0.13275 | 0.37537 | 0.40283 | 121.5683 | 122.319 | -0.004578 | 122.4518 | 3.3371 | -0.16937 | 122.319 | -0.004578 | 3.3371 | 121.5683 | 122.4518 | -122.4197 | -122.4518
3044.2031 | 122.3145 | -0.091553 | 122.2733 | -0.18272 | 0.010696 | -0.011909 | 0.0089124 | 0.04755 | -0.011177 | 0.066262 | 0.07782 | 122.2595 | -0.1236 | 0.15106 | 121.6644 | 3.5202 | 0.47607 | 0.78278 | 122.374 | -0.21973 | -0.032043 | -0.013733 | 0.16937 | 0.24261 | -0.60882 | -0.12817 | 0.10071 | 0.20142 | 0.56763 | 0.87433 | 121.756 | 122.3511 | 0.16937 | 122.4655 | 3.6118 | -0.12817 | 122.3511 | 0.16937 | 3.6118 | 121.756 | 122.4655 | -122.3969 | -122.493
3045.9688 | 122.3328 | -0.091553 | 122.2824 | -0.068283 | 0.009628 | -0.011696 | 0.015962 | 0.050328 | -0.013099 | 0.065407 | -0.004578 | 122.2641 | -0.17395 | 0.09613 | 121.5591 | 3.3737 | 0.3891 | 0.49896 | 122.4243 | -0.21057 | -0.082397 | -0.018311 | 0.086975 | 0.18768 | -0.72327 | -0.11902 | 0.14191 | 0.16937 | 0.48065 | 0.59052 | 121.6507 | 122.3557 | 0.086975 | 122.5159 | 3.4653 | -0.11902 | 122.3557 | 0.086975 | 3.4653 | 121.6507 | 122.5159 | -122.4564 | -122.493
3047.6562 | 122.3373 | -0.10529 | 122.2733 | -0.15221 | 0.0081326 | -0.0149 | 0.012758 | 0.050541 | -0.014381 | 0.064125 | -0.018311 | 122.2504 | -0.19684 | 0.09613 | 121.5912 | 3.4378 | 0.5127 | 0.59967 | 122.4106 | -0.21973 | -0.091552 | -0.022888 | 0.086975 | 0.20142 | -0.68207 | -0.11444 | 0.13733 | 0.17853 | 0.61798 | 0.70496 | 121.6965 | 122.3557 | 0.086975 | 122.5159 | 3.5431 | -0.11444 | 122.3557 | 0.086975 | 3.5431 | 121.6965 | 122.5159 | -122.4701 | -122.493
3049.4062 | 122.3145 | -0.10986 | 122.2412 | -0.12932 | 0.0092008 | -0.0099869 | 0.012758 | 0.051609 | -0.013099 | 0.065621 | 0.004578 | 122.2458 | -0.19684 | 0.086975 | 121.6049 | 3.447 | 0.4715 | 0.59052 | 122.438 | -0.21057 | -0.086975 | 0.004578 | 0.11444 | 0.19684 | -0.63629 | -0.10071 | 0.19684 | 0.20142 | 0.58136 | 0.70038 | 121.7148 | 122.3557 | 0.11444 | 122.5479 | 3.5568 | -0.10071 | 122.3557 | 0.11444 | 3.5568 | 121.7148 | 122.5479 | -122.438 | -122.4518
3051.1719 | 122.3099 | -0.086975 | 122.2778 | -0.083542 | 0.010696 | -0.010414 | 0.011689 | 0.050541 | -0.01374 | 0.065407 | 0.009155 | 122.2504 | -0.1831 | 0.10071 | 121.5958 | 3.4195 | 0.39825 | 0.54474 | 122.4655 | -0.19684 | -0.09613 | -0.027466 | 0.09613 | 0.18768 | -0.68207 | -0.10986 | 0.18768 | 0.19226 | 0.48523 | 0.63171 | 121.6827 | 122.3373 | 0.09613 | 122.5525 | 3.5065 | -0.10986 | 122.3373 | 0.09613 | 3.5065 | 121.6827 | 122.5525 | -122.4609 | -122.4747
3052.9219 | 122.3145 | -0.091553 | 122.2641 | -0.19798 | 0.010696 | -0.013618 | 0.007417 | 0.048619 | -0.0092542 | 0.06498 | 0.059509 | 122.2412 | -0.15106 | 0.15564 | 121.6827 | 3.5202 | 0.48065 | 0.79651 | 122.3831 | -0.1831 | -0.059509 | -0.022888 | 0.15106 | 0.24719 | -0.58136 | -0.091552 | 0.11902 | 0.21057 | 0.57221 | 0.88806 | 121.7743 | 122.3328 | 0.15106 | 122.4747 | 3.6118 | -0.091552 | 122.3328 | 0.15106 | 3.6118 | 121.7743 | 122.4747 | -122.4152 | -122.4472
3054.6875 | 122.3694 | -0.091553 | 122.2733 | -0.15984 | 0.011123 | -0.013618 | 0.0080578 | 0.049046 | -0.011604 | 0.064766 | 0.059509 | 122.2412 | -0.13733 | 0.14648 | 121.6873 | 3.4973 | 0.39368 | 0.73242 | 122.3923 | -0.20142 | -0.045776 | -0.032043 | 0.15106 | 0.23804 | -0.58594 | -0.10986 | 0.11902 | 0.19684 | 0.48523 | 0.82398 | 121.7789 | 122.3328 | 0.15106 | 122.4838 | 3.5889 | -0.10986 | 122.3328 | 0.15106 | 3.5889 | 121.7789 | 122.4838 | -122.4106 | -122.4747
3056.375 | 122.3694 | -0.086975 | 122.2504 | -0.23613 | 0.010482 | -0.015114 | 0.012544 | 0.047764 | -0.013527 | 0.064553 | -0.050354 | 122.2778 | -0.17853 | 0.045776 | 121.5454 | 3.4287 | 0.6546 | 0.63171 | 122.438 | -0.21973 | -0.091553 | 0.027466 | 0.036621 | 0.13275 | -0.70496 | -0.13275 | 0.18768 | 0.12817 | 0.74158 | 0.71869 | 121.6324 | 122.3648 | 0.036621 | 122.525 | 3.5156 | -0.13275 | 122.3648 | 0.036621 | 3.5156 | 121.6324 | 122.525 | -122.4289 | -122.4701
3058.125 | 122.3373 | -0.12817 | 122.2778 | -0.19798 | 0.0083462 | -0.012337 | 0.0095532 | 0.049046 | -0.010963 | 0.066262 | 0.050354 | 122.2229 | -0.13733 | 0.16937 | 121.6644 | 3.5339 | 0.47607 | 0.79651 | 122.3785 | -0.18768 | -0.009155 | -0.054932 | 0.17853 | 0.29755 | -0.6134 | -0.059509 | 0.10071 | 0.18768 | 0.60425 | 0.92468 | 121.7926 | 122.3511 | 0.17853 | 122.5067 | 3.6621 | -0.059509 | 122.3511 | 0.17853 | 3.6621 | 121.7926 | 122.5067 | -122.4152 | -122.4655
3059.8281 | 122.4655 | -0.027466 | 122.2321 | 0.099564 | 0.0089872 | -0.011696 | 0.015535 | 0.049259 | -0.015449 | 0.066689 | -0.045776 | 122.2504 | -0.17853 | 0.032043 | 121.5271 | 3.2684 | 0.26093 | 0.33875 | 122.4472 | -0.21973 | -0.15106 | 0.01831 | -0.01831 | 0.059509 | -0.70496 | -0.19226 | 0.21515 | 0.13275 | 0.28839 | 0.36621 | 121.5546 | 122.2778 | -0.01831 | 122.4747 | 3.2959 | -0.19226 | 122.2778 | -0.01831 | 3.2959 | 121.5546 | 122.4747 | -122.4106 | -122.4518
3061.5781 | 122.4426 | -0.050354 | 122.2137 | -0.0072479 | 0.0083462 | -0.011055 | 0.0063488 | 0.047764 | -0.0096814 | 0.066475 | -0.013733 | 122.2687 | -0.14648 | 0.10071 | 121.6141 | 3.4012 | 0.35248 | 0.59967 | 122.3511 | -0.21515 | -0.09613 | 0.054932 | 0.036621 | 0.15106 | -0.59967 | -0.16479 | 0.13733 | 0.13275 | 0.40283 | 0.65002 | 121.6644 | 122.319 | 0.036621 | 122.4014 | 3.4515 | -0.16479 | 122.319 | 0.036621 | 3.4515 | 121.6644 | 122.4014 | -122.3602 | -122.4289
3063.3438 | 122.3053 | -0.09613 | 122.2641 | -0.083542 | 0.010482 | -0.011696 | 0.015748 | 0.049259 | -0.013099 | 0.065407 | 0.018311 | 122.2275 | -0.18768 | 0.10986 | 121.582 | 3.4332 | 0.40283 | 0.55389 | 122.4335 | -0.21057 | -0.091553 | -0.036621 | 0.11444 | 0.20599 | -0.68207 | -0.11444 | 0.16937 | 0.20599 | 0.49896 | 0.65002 | 121.6782 | 122.3236 | 0.11444 | 122.5296 | 3.5294 | -0.11444 | 122.3236 | 0.11444 | 3.5294 | 121.6782 | 122.5296 | -122.4518 | -122.4747
3065.0469 | 122.4426 | -0.059509 | 122.2412 | -0.037765 | 0.010696 | -0.011482 | 0.0080578 | 0.046269 | -0.010322 | 0.065834 | 0.009155 | 122.2595 | -0.13275 | 0.10986 | 121.6278 | 3.447 | 0.37994 | 0.64545 | 122.3877 | -0.21057 | -0.073242 | 0.01831 | 0.068664 | 0.16937 | -0.6134 | -0.15106 | 0.14648 | 0.14191 | 0.43945 | 0.70496 | 121.6873 | 122.319 | 0.068664 | 122.4472 | 3.5065 | -0.15106 | 122.319 | 0.068664 | 3.5065 | 121.6873 | 122.4472 | -122.374 | -122.4518
3066.7969 | 122.374 | -0.07782 | 122.2321 | -0.12932 | 0.009628 | -0.013618 | 0.0080578 | 0.045841 | -0.010963 | 0.064553 | 0.041199 | 122.2458 | -0.13275 | 0.17853 | 121.6644 | 3.5065 | 0.39825 | 0.72327 | 122.3465 | -0.19684 | -0.054931 | 0.013733 | 0.11902 | 0.25635 | -0.56763 | -0.11902 | 0.11444 | 0.17395 | 0.47607 | 0.80109 | 121.7422 | 122.3236 | 0.11902 | 122.4243 | 3.5843 | -0.11902 | 122.3236 | 0.11902 | 3.5843 | 121.7422 | 122.4243 | -122.3648 | -122.4289
3068.5625 | 122.3099 | -0.09613 | 122.3007 | -0.12169 | 0.0098416 | -0.010841 | 0.017457 | 0.051396 | -0.012672 | 0.066689 | 0.004578 | 122.2366 | -0.19226 | 0.11444 | 121.5866 | 3.4515 | 0.45319 | 0.59509 | 122.4289 | -0.20142 | -0.096131 | -0.064087 | 0.10071 | 0.21057 | -0.71411 | -0.10529 | 0.12817 | 0.19684 | 0.54932 | 0.69122 | 121.6827 | 122.3328 | 0.10071 | 122.525 | 3.5477 | -0.10529 | 122.3328 | 0.10071 | 3.5477 | 121.6827 | 122.525 | -122.493 | -122.5021
3070.3281 | 122.3511 | -0.10986 | 122.2641 | -0.18272 | 0.0098416 | -0.013405 | 0.008485 | 0.046482 | -0.013527 | 0.066048 | 0.050354 | 122.2412 | -0.12817 | 0.13733 | 121.637 | 3.5065 | 0.56305 | 0.76446 | 122.4014 | -0.21057 | -0.018311 | -0.022888 | 0.16022 | 0.24719 | -0.62714 | -0.10071 | 0.13733 | 0.17853 | 0.67291 | 0.87433 | 121.7468 | 122.3511 | 0.16022 | 122.5113 | 3.6163 | -0.10071 | 122.3511 | 0.16022 | 3.6163 | 121.7468 | 122.5113 | -122.3923 | -122.4747
3072.0156 | 122.4289 | -0.050354 | 122.2092 | 0.15297 | 0.011764 | -0.010628 | 0.016176 | 0.050328 | -0.014381 | 0.06797 | -0.032043 | 122.2275 | -0.18768 | 0.073242 | 121.582 | 3.3051 | 0.17853 | 0.35706 | 122.3877 | -0.19684 | -0.13733 | 0.018311 | 0.018311 | 0.1236 | -0.62714 | -0.14648 | 0.17853 | 0.15564 | 0.22888 | 0.40741 | 121.6324 | 122.2778 | 0.018311 | 122.438 | 3.3554 | -0.14648 | 122.2778 | 0.018311 | 3.3554 | 121.6324 | 122.438 | -122.3969 | -122.406
3073.7656 | 122.3923 | -0.050354 | 122.2366 | 0.214 | 0.010269 | -0.01255 | 0.015107 | 0.051609 | -0.013099 | 0.066475 | 0.064087 | 122.2137 | -0.13733 | 0.14191 | 121.637 | 3.3691 | 0.1236 | 0.44403 | 122.3694 | -0.19226 | -0.086975 | -0.022888 | 0.11444 | 0.19226 | -0.59967 | -0.14191 | 0.13275 | 0.20142 | 0.17395 | 0.49439 | 121.6873 | 122.2641 | 0.11444 | 122.4197 | 3.4195 | -0.14191 | 122.2641 | 0.11444 | 3.4195 | 121.6873 | 122.4197 | -122.374 | -122.4289
3075.5312 | 122.3648 | -0.082397 | 122.2916 | -0.19035 | 0.01091 | -0.0089189 | 0.014467 | 0.047978 | -0.01374 | 0.066262 | -0.036621 | 122.2961 | -0.19226 | 0.050354 | 121.55 | 3.4424 | 0.59509 | 0.63171 | 122.4152 | -0.23804 | -0.10986 | 0.004578 | 0.045776 | 0.13275 | -0.74158 | -0.15564 | 0.1236 | 0.15564 | 0.67749 | 0.71411 | 121.6324 | 122.3785 | 0.045776 | 122.4976 | 3.5248 | -0.15564 | 122.3785 | 0.045776 | 3.5248 | 121.6324 | 122.4976 | -122.4838 | -122.5296
3077.2188 | 122.2916 | -0.10529 | 122.2641 | -0.068283 | 0.0098416 | -0.0072099 | 0.014894 | 0.052037 | -0.013527 | 0.066475 | 0.004578 | 122.2183 | -0.16937 | 0.10529 | 121.582 | 3.4515 | 0.42572 | 0.5722 | 122.3969 | -0.20142 | -0.064087 | -0.045776 | 0.10986 | 0.21057 | -0.68207 | -0.09613 | 0.13275 | 0.17395 | 0.53101 | 0.67749 | 121.6873 | 122.3236 | 0.10986 | 122.5021 | 3.5568 | -0.09613 | 122.3236 | 0.10986 | 3.5568 | 121.6873 | 122.5021 | -122.4335 | -122.4655
3078.9844 | 122.3282 | -0.086975 | 122.2961 | -0.14458 | 0.0098416 | -0.011269 | 0.015535 | 0.050114 | -0.013954 | 0.065834 | -0.013733 | 122.2458 | -0.1831 | 0.082397 | 121.5912 | 3.4607 | 0.49896 | 0.59967 | 122.4426 | -0.21515 | -0.09613 | -0.050354 | 0.073242 | 0.16937 | -0.70496 | -0.12817 | 0.14648 | 0.16937 | 0.58594 | 0.68665 | 121.6782 | 122.3328 | 0.073242 | 122.5296 | 3.5477 | -0.12817 | 122.3328 | 0.073242 | 3.5477 | 121.6782 | 122.5296 | -122.4792 | -122.5113
3080.75 | 122.4289 | -0.059509 | 122.2275 | 0.084305 | 0.01091 | -0.011482 | 0.0069898 | 0.049687 | -0.0094678 | 0.066048 | 0.036621 | 122.2412 | -0.12817 | 0.10986 | 121.637 | 3.3783 | 0.16937 | 0.48523 | 122.3557 | -0.19684 | -0.068665 | 0.013733 | 0.09613 | 0.16937 | -0.59052 | -0.13733 | 0.12817 | 0.1648 | 0.22888 | 0.54474 | 121.6965 | 122.3007 | 0.09613 | 122.4152 | 3.4378 | -0.13733 | 122.3007 | 0.09613 | 3.4378 | 121.6965 | 122.4152 | -122.3557 | -122.4243
3082.4375 | 122.3328 | -0.10529 | 122.2504 | -0.15984 | 0.0087734 | -0.01255 | 0.010835 | 0.047337 | -0.010963 | 0.063912 | 0.036621 | 122.2412 | -0.14648 | 0.15106 | 121.6415 | 3.5477 | 0.50812 | 0.77362 | 122.374 | -0.19226 | -0.041198 | -0.009155 | 0.14191 | 0.25635 | -0.60882 | -0.086975 | 0.1236 | 0.18311 | 0.6134 | 0.87891 | 121.7468 | 122.3465 | 0.14191 | 122.4792 | 3.653 | -0.086975 | 122.3465 | 0.14191 | 3.653 | 121.7468 | 122.4792 | -122.3969 | -122.4426
3084.1875 | 122.4335 | -0.07782 | 122.2412 | -0.075912 | 0.010269 | -0.012123 | 0.0086988 | 0.046696 | -0.0094678 | 0.069039 | 0.027466 | 122.2916 | -0.16479 | 0.12817 | 121.6553 | 3.4698 | 0.39825 | 0.68665 | 122.3511 | -0.2243 | -0.086975 | 0.050354 | 0.10529 | 0.20599 | -0.58594 | -0.14648 | 0.10986 | 0.19226 | 0.47607 | 0.76447 | 121.7331 | 122.3694 | 0.10529 | 122.4289 | 3.5477 | -0.14648 | 122.3694 | 0.10529 | 3.5477 | 121.7331 | 122.4289 | -122.406 | -122.4655
3085.8906 | 122.4472 | -0.036621 | 122.2137 | 0.069046 | 0.011978 | -0.0093461 | 0.013826 | 0.048405 | -0.012458 | 0.066048 | -0.036621 | 122.2778 | -0.17853 | 0.064087 | 121.5271 | 3.2776 | 0.25635 | 0.34332 | 122.4106 | -0.22888 | -0.14191 | 0.064087 | 0 | 0.10071 | -0.68664 | -0.19226 | 0.19684 | 0.14191 | 0.29297 | 0.37994 | 121.5637 | 122.3145 | 0 | 122.4472 | 3.3142 | -0.19226 | 122.3145 | 0 | 3.3142 | 121.5637 | 122.4472 | -122.3923 | -122.4426
3087.6562 | 122.4289 | -0.064087 | 122.2504 | 0.084305 | 0.0083462 | -0.0099869 | 0.01233 | 0.047123 | -0.012672 | 0.06498 | 0.032043 | 122.2275 | -0.14648 | 0.12817 | 121.6324 | 3.3783 | 0.15564 | 0.48523 | 122.3511 | -0.19684 | -0.082397 | -0.022888 | 0.09613 | 0.19226 | -0.61798 | -0.13275 | 0.10071 | 0.17853 | 0.21973 | 0.54932 | 121.6965 | 122.2916 | 0.09613 | 122.4152 | 3.4424 | -0.13275 | 122.2916 | 0.09613 | 3.4424 | 121.6965 | 122.4152 | -122.3969 | -122.4472
3089.3594 | 122.4335 | -0.041199 | 122.2321 | 0.13008 | 0.0087734 | -0.011055 | 0.0069898 | 0.045628 | -0.010536 | 0.066689 | 0.036621 | 122.2733 | -0.13275 | 0.09613 | 121.6095 | 3.3554 | 0.23346 | 0.48981 | 122.3557 | -0.21057 | -0.091552 | 0.041198 | 0.07782 | 0.13733 | -0.62256 | -0.16937 | 0.1236 | 0.16937 | 0.27466 | 0.53101 | 121.6507 | 122.3145 | 0.07782 | 122.3969 | 3.3966 | -0.16937 | 122.3145 | 0.07782 | 3.3966 | 121.6507 | 122.3969 | -122.3648 | -122.4426
3091.125 | 122.4838 | -0.050354 | 122.2229 | 0.038529 | 0.0083462 | -0.015327 | 0.0093396 | 0.04755 | -0.011177 | 0.06498 | 0.009155 | 122.2595 | -0.15564 | 0.091553 | 121.6049 | 3.3875 | 0.3067 | 0.53558 | 122.3785 | -0.21515 | -0.10529 | 0.036621 | 0.059509 | 0.14191 | -0.61798 | -0.16479 | 0.15564 | 0.16479 | 0.35706 | 0.58594 | 121.6553 | 122.3099 | 0.059509 | 122.4289 | 3.4378 | -0.16479 | 122.3099 | 0.059509 | 3.4378 | 121.6553 | 122.4289 | -122.3785 | -122.438
3092.8906 | 122.4335 | -0.064087 | 122.2412 | 0.091934 | 0.010482 | -0.013191 | 0.012544 | 0.047978 | -0.012458 | 0.067543 | 0.045776 | 122.2321 | -0.11444 | 0.14191 | 121.6095 | 3.4103 | 0.1831 | 0.48981 | 122.3602 | -0.17853 | -0.050354 | -0.009155 | 0.10986 | 0.20599 | -0.63171 | -0.11444 | 0.11902 | 0.16022 | 0.24719 | 0.55389 | 121.6736 | 122.2961 | 0.10986 | 122.4243 | 3.4744 | -0.11444 | 122.2961 | 0.10986 | 3.4744 | 121.6736 | 122.4243 | -122.3557 | -122.4197
3094.6875 | 122.4106 | -0.059509 | 122.2366 | 0.16823 | 0.011337 | -0.010414 | 0.015321 | 0.044987 | -0.011604 | 0.066475 | 0.11444 | 122.2916 | -0.17395 | 0.29297 | 122.3236 | 3.6301 | 0.35248 | 0.43488 | 122.3969 | -0.20599 | -0.11444 | 0.054932 | 0.17395 | 0.35248 | 0.086975 | -0.14649 | 0.16022 | 0.28839 | 0.41199 | 0.49438 | 122.3831 | 122.3511 | 0.17395 | 122.4564 | 3.6896 | -0.14649 | 122.3511 | 0.17395 | 3.6896 | 122.3831 | 122.4564 | -122.4106 | -122.4426
3096.3906 | 122.3419 | -0.09613 | 122.2366 | -0.053024 | 0.011123 | -0.0095597 | 0.016389 | 0.051609 | -0.014595 | 0.066689 | 0.009155 | 122.2321 | -0.17395 | 0.091553 | 121.5683 | 3.4287 | 0.39368 | 0.50354 | 122.4243 | -0.21515 | -0.07782 | -0.004577 | 0.10528 | 0.18768 | -0.66833 | -0.11902 | 0.18768 | 0.1831 | 0.48981 | 0.59967 | 121.6644 | 122.3282 | 0.10528 | 122.5204 | 3.5248 | -0.11902 | 122.3282 | 0.10528 | 3.5248 | 121.6644 | 122.5204 | -122.4106 | -122.4518
3098.1562 | 122.4655 | -0.064087 | 122.2229 | 0.053787 | 0.009628 | -0.0087051 | 0.0089124 | 0.047978 | -0.010536 | 0.066475 | -0.004578 | 122.2824 | -0.14648 | 0.10071 | 121.6187 | 3.3691 | 0.27008 | 0.50812 | 122.3785 | -0.20599 | -0.082397 | 0.05951 | 0.059509 | 0.1648 | -0.60425 | -0.14191 | 0.15564 | 0.14191 | 0.33417 | 0.5722 | 121.6827 | 122.3465 | 0.059509 | 122.4426 | 3.4332 | -0.14191 | 122.3465 | 0.059509 | 3.4332 | 121.6827 | 122.4426 | -122.3694 | -122.4289
3099.8438 | 122.374 | -0.10071 | 122.2549 | -0.24376 | 0.0092008 | -0.012123 | 0.011689 | 0.046055 | -0.010963 | 0.065834 | 0.004578 | 122.2916 | -0.16022 | 0.091553 | 121.6003 | 3.4882 | 0.60425 | 0.70953 | 122.3831 | -0.23804 | -0.059509 | 0.036621 | 0.10529 | 0.19226 | -0.6546 | -0.13733 | 0.12817 | 0.16479 | 0.70496 | 0.81024 | 121.701 | 122.3923 | 0.10529 | 122.4838 | 3.5889 | -0.13733 | 122.3923 | 0.10529 | 3.5889 | 121.701 | 122.4838 | -122.4152 | -122.493
3101.625 | 122.4289 | -0.059509 | 122.2137 | 0.10719 | 0.0085598 | -0.012978 | 0.014039 | 0.050114 | -0.011818 | 0.065834 | -0.041199 | 122.2275 | -0.1831 | 0.064087 | 121.5546 | 3.3279 | 0.21515 | 0.34332 | 122.3969 | -0.20599 | -0.1236 | 0.013733 | 0.01831 | 0.1236 | -0.65918 | -0.14649 | 0.18311 | 0.14191 | 0.27466 | 0.40283 | 121.6141 | 122.287 | 0.01831 | 122.4564 | 3.3875 | -0.14649 | 122.287 | 0.01831 | 3.3875 | 121.6141 | 122.4564 | -122.3969 | -122.4197
3103.3125 | 122.4472 | -0.054932 | 122.2366 | -0.014877 | 0.0085598 | -0.010414 | 0.007417 | 0.04755 | -0.0079724 | 0.066262 | -0.009155 | 122.2733 | -0.16479 | 0.10529 | 121.6232 | 3.4287 | 0.38452 | 0.62714 | 122.3694 | -0.20599 | -0.10986 | 0.036621 | 0.045777 | 0.16022 | -0.6134 | -0.15106 | 0.13275 | 0.15564 | 0.43945 | 0.68207 | 121.6782 | 122.3282 | 0.045777 | 122.4243 | 3.4836 | -0.15106 | 122.3282 | 0.045777 | 3.4836 | 121.6782 | 122.4243 | -122.4014 | -122.4426
3105.0625 | 122.3557 | -0.091553 | 122.2504 | -0.20561 | 0.010055 | -0.017677 | 0.014894 | 0.049046 | -0.013313 | 0.067116 | -0.059509 | 122.287 | -0.19684 | 0.059509 | 121.5591 | 3.4653 | 0.62256 | 0.62256 | 122.4152 | -0.23804 | -0.10529 | 0.036621 | 0.032044 | 0.15106 | -0.69122 | -0.14648 | 0.16479 | 0.13733 | 0.71411 | 0.71411 | 121.6507 | 122.3785 | 0.032044 | 122.5067 | 3.5568 | -0.14648 | 122.3785 | 0.032044 | 3.5568 | 121.6507 | 122.5067 | -122.4472 | -122.4884
3106.7656 | 122.3648 | -0.091553 | 122.2412 | -0.15984 | 0.010482 | -0.010628 | 0.0082714 | 0.046696 | -0.012672 | 0.066689 | -0.018311 | 122.2824 | -0.17853 | 0.050354 | 121.5683 | 3.4561 | 0.64087 | 0.66376 | 122.406 | -0.2243 | -0.086975 | 0.041199 | 0.073242 | 0.14191 | -0.67291 | -0.13275 | 0.16479 | 0.16022 | 0.73242 | 0.75531 | 121.6599 | 122.374 | 0.073242 | 122.4976 | 3.5477 | -0.13275 | 122.374 | 0.073242 | 3.5477 | 121.6599 | 122.4976 | -122.4197 | -122.4655
3108.5156 | 122.3282 | -0.10071 | 122.2595 | -0.20561 | 0.0092008 | -0.013405 | 0.0080578 | 0.046269 | -0.009895 | 0.067543 | 0.050354 | 122.2366 | -0.15106 | 0.16022 | 121.6736 | 3.5568 | 0.46692 | 0.78735 | 122.3694 | -0.21057 | -0.050354 | -0.022888 | 0.15106 | 0.26093 | -0.58594 | -0.10986 | 0.10986 | 0.20142 | 0.56763 | 0.88806 | 121.7743 | 122.3373 | 0.15106 | 122.4701 | 3.6575 | -0.10986 | 122.3373 | 0.15106 | 3.6575 | 121.7743 | 122.4701 | -122.4106 | -122.4701
3110.2812 | 122.3465 | -0.10529 | 122.2412 | -0.037765 | 0.0094144 | -0.013405 | 0.018953 | 0.051823 | -0.013313 | 0.067116 | 0 | 122.2504 | -0.20599 | 0.09613 | 121.5546 | 3.3966 | 0.37537 | 0.4715 | 122.4472 | -0.21057 | -0.10071 | 0.009155 | 0.10529 | 0.20142 | -0.68665 | -0.10529 | 0.20599 | 0.20599 | 0.48065 | 0.57678 | 121.6599 | 122.3557 | 0.10529 | 122.5525 | 3.5019 | -0.10529 | 122.3557 | 0.10529 | 3.5019 | 121.6599 | 122.5525 | -122.4472 | -122.4518
3112.0469 | 122.3923 | -0.086975 | 122.2687 | -0.13695 | 0.0094144 | -0.0099869 | 0.0063488 | 0.047764 | -0.012031 | 0.066262 | 0.036621 | 122.2641 | -0.1236 | 0.16479 | 121.6782 | 3.5339 | 0.40283 | 0.73242 | 122.3831 | -0.20599 | -0.036621 | -0.004578 | 0.1236 | 0.25177 | -0.59051 | -0.11902 | 0.11444 | 0.16022 | 0.48981 | 0.8194 | 121.7651 | 122.3511 | 0.1236 | 122.4701 | 3.6209 | -0.11902 | 122.3511 | 0.1236 | 3.6209 | 121.7651 | 122.4701 | -122.3923 | -122.4747
3113.75 | 122.4243 | -0.054932 | 122.2412 | -0.083542 | 0.0085598 | -0.0097733 | 0.0076306 | 0.047764 | -0.01075 | 0.064553 | 0.022888 | 122.2687 | -0.14648 | 0.1236 | 121.6553 | 3.4973 | 0.40283 | 0.69122 | 122.3557 | -0.20142 | -0.091552 | 0.027466 | 0.07782 | 0.17853 | -0.58594 | -0.14648 | 0.11444 | 0.16937 | 0.45776 | 0.74616 | 121.7102 | 122.3236 | 0.07782 | 122.4106 | 3.5522 | -0.14648 | 122.3236 | 0.07782 | 3.5522 | 121.7102 | 122.4106 | -122.3877 | -122.4426
3115.5156 | 122.3785 | -0.10529 | 122.2595 | -0.22087 | 0.011764 | -0.0099869 | 0.013398 | 0.047123 | -0.012031 | 0.065834 | -0.041199 | 122.3007 | -0.17395 | 0.050354 | 121.5591 | 3.4653 | 0.66376 | 0.66376 | 122.4197 | -0.25177 | -0.068664 | 0.041199 | 0.064087 | 0.15564 | -0.70038 | -0.14648 | 0.16022 | 0.13275 | 0.76904 | 0.76904 | 121.6644 | 122.406 | 0.064087 | 122.525 | 3.5706 | -0.14648 | 122.406 | 0.064087 | 3.5706 | 121.6644 | 122.525 | -122.4335 | -122.5113
3117.2656 | 122.4609 | -0.068665 | 122.2092 | 0.01564 | 0.0077054 | -0.011909 | 0.0089124 | 0.047123 | -0.009895 | 0.064125 | -0.009155 | 122.2778 | -0.14191 | 0.091553 | 121.6049 | 3.4195 | 0.36621 | 0.56763 | 122.3602 | -0.21057 | -0.073242 | 0.068665 | 0.05951 | 0.16022 | -0.60425 | -0.14191 | 0.15106 | 0.13275 | 0.43488 | 0.63629 | 121.6736 | 122.3465 | 0.05951 | 122.4289 | 3.4882 | -0.14191 | 122.3465 | 0.05951 | 3.4882 | 121.6736 | 122.4289 | -122.3511 | -122.4197
3119.0156 | 122.4243 | -0.045776 | 122.2321 | -0.060654 | 0.0094144 | -0.012978 | 0.008485 | 0.047978 | -0.010322 | 0.064553 | 0.004578 | 122.2549 | -0.16022 | 0.11444 | 121.6278 | 3.4744 | 0.37994 | 0.6546 | 122.3969 | -0.21057 | -0.11444 | 0.022888 | 0.050354 | 0.16022 | -0.60425 | -0.1648 | 0.16479 | 0.16479 | 0.42572 | 0.70038 | 121.6736 | 122.3007 | 0.050354 | 122.4426 | 3.5202 | -0.1648 | 122.3007 | 0.050354 | 3.5202 | 121.6736 | 122.4426 | -122.3923 | -122.4426
3120.7812 | 122.4106 | -0.059509 | 122.2321 | 0.18349 | 0.010055 | -0.0063553 | 0.01468 | 0.047764 | -0.012031 | 0.066689 | 0.009155 | 122.2229 | -0.17395 | 0.13275 | 121.6324 | 3.3783 | 0.1236 | 0.42114 | 122.3785 | -0.19226 | -0.11444 | -0.009156 | 0.068664 | 0.19226 | -0.59967 | -0.13275 | 0.14648 | 0.1831 | 0.1831 | 0.48065 | 121.6919 | 122.2824 | 0.068664 | 122.438 | 3.4378 | -0.13275 | 122.2824 | 0.068664 | 3.4378 | 121.6919 | 122.438 | -122.406 | -122.4243
3122.4688 | 122.3831 | -0.09613 | 122.2595 | -0.24376 | 0.011337 | -0.01255 | 0.010835 | 0.046055 | -0.012031 | 0.064766 | -0.032043 | 122.2824 | -0.16479 | 0.068665 | 121.5729 | 3.479 | 0.64087 | 0.68207 | 122.4289 | -0.23804 | -0.068665 | 0.022889 | 0.064087 | 0.16479 | -0.68665 | -0.14191 | 0.16937 | 0.13275 | 0.737 | 0.7782 | 121.669 | 122.3785 | 0.064087 | 122.525 | 3.5751 | -0.14191 | 122.3785 | 0.064087 | 3.5751 | 121.669 | 122.525 | -122.4243 | -122.4976
3124.2344 | 122.2916 | -0.10071 | 122.2733 | -0.11406 | 0.011123 | -0.012337 | 0.016603 | 0.045201 | -0.014167 | 0.065834 | 0 | 122.2595 | -0.17853 | 0.10071 | 121.5775 | 3.4882 | 0.44861 | 0.57678 | 122.3831 | -0.21515 | -0.07782 | -0.013733 | 0.10071 | 0.20142 | -0.6958 | -0.11444 | 0.10986 | 0.17853 | 0.54932 | 0.67749 | 121.6782 | 122.3602 | 0.10071 | 122.4838 | 3.5889 | -0.11444 | 122.3602 | 0.10071 | 3.5889 | 121.6782 | 122.4838 | -122.4518 | -122.4884
3126 | 122.4701 | -0.032043 | 122.2137 | 0.12245 | 0.010482 | -0.0084915 | 0.014467 | 0.048832 | -0.014381 | 0.066048 | -0.050354 | 122.2961 | -0.16937 | 0.041199 | 121.5179 | 3.3279 | 0.30212 | 0.33875 | 122.4289 | -0.21973 | -0.13733 | 0.082398 | -0.018311 | 0.073242 | -0.6958 | -0.18768 | 0.21515 | 0.11902 | 0.33417 | 0.37079 | 121.55 | 122.3282 | -0.018311 | 122.4609 | 3.36 | -0.18768 | 122.3282 | -0.018311 | 3.36 | 121.55 | 122.4609 | -122.3831 | -122.4335
3127.7031 | 122.4243 | -0.059509 | 122.2549 | 0.18349 | 0.0085598 | -0.014046 | 0.009126 | 0.050328 | -0.013527 | 0.066475 | 0.045776 | 122.1954 | -0.15106 | 0.14648 | 121.637 | 3.4241 | 0.10071 | 0.46234 | 122.3877 | -0.17395 | -0.091553 | -0.059509 | 0.10528 | 0.20599 | -0.61798 | -0.11444 | 0.13275 | 0.19684 | 0.16022 | 0.52185 | 121.6965 | 122.2549 | 0.10528 | 122.4472 | 3.4836 | -0.11444 | 122.2549 | 0.10528 | 3.4836 | 121.6965 | 122.4472 | -122.406 | -122.4289
3129.4531 | 122.4106 | -0.064087 | 122.2321 | 0.16823 | 0.0087734 | -0.0089189 | 0.012971 | 0.049687 | -0.012672 | 0.067116 | 0.068665 | 122.2504 | -0.14191 | 0.13275 | 121.637 | 3.4195 | 0.10529 | 0.46234 | 122.4106 | -0.17395 | -0.07782 | 0.01831 | 0.13275 | 0.19684 | -0.59509 | -0.10986 | 0.17853 | 0.21057 | 0.16937 | 0.52643 | 121.701 | 122.3145 | 0.13275 | 122.4747 | 3.4836 | -0.10986 | 122.3145 | 0.13275 | 3.4836 | 121.701 | 122.4747 | -122.374 | -122.406
3131.2188 | 122.3282 | -0.10986 | 122.2549 | -0.19035 | 0.010055 | -0.01255 | 0.008485 | 0.046482 | -0.011818 | 0.066048 | 0.054932 | 122.2641 | -0.14191 | 0.16937 | 121.6782 | 3.5843 | 0.48981 | 0.79651 | 122.3648 | -0.20142 | -0.032044 | 0.009155 | 0.16479 | 0.27924 | -0.57678 | -0.091553 | 0.10986 | 0.19684 | 0.59967 | 0.90637 | 121.788 | 122.374 | 0.16479 | 122.4747 | 3.6942 | -0.091553 | 122.374 | 0.16479 | 3.6942 | 121.788 | 122.4747 | -122.3969 | -122.4564
3132.9844 | 122.319 | -0.09613 | 122.2595 | -0.22087 | 0.0092008 | -0.010841 | 0.0080578 | 0.046696 | -0.0096814 | 0.064553 | 0.064087 | 122.2504 | -0.15564 | 0.16937 | 121.669 | 3.5843 | 0.48981 | 0.79193 | 122.3511 | -0.1831 | -0.05951 | -0.009155 | 0.16022 | 0.2655 | -0.59052 | -0.086975 | 0.091553 | 0.21973 | 0.58594 | 0.88806 | 121.7651 | 122.3465 | 0.16022 | 122.4472 | 3.6804 | -0.086975 | 122.3465 | 0.16022 | 3.6804 | 121.7651 | 122.4472 | -122.4152 | -122.4426
3134.75 | 122.4335 | -0.07782 | 122.2321 | 0.091934 | 0.0089872 | -0.012764 | 0.012117 | 0.048832 | -0.01139 | 0.066048 | 0.050354 | 122.2412 | -0.13733 | 0.15564 | 121.6232 | 3.4195 | 0.16479 | 0.49439 | 122.3557 | -0.19684 | -0.059509 | 0.009155 | 0.12817 | 0.23346 | -0.60883 | -0.11902 | 0.1236 | 0.18768 | 0.24261 | 0.57221 | 121.7011 | 122.319 | 0.12817 | 122.4335 | 3.4973 | -0.11902 | 122.319 | 0.12817 | 3.4973 | 121.7011 | 122.4335 | -122.3694 | -122.4289
3136.5156 | 122.3236 | -0.10071 | 122.2733 | -0.12169 | 0.010055 | -0.013191 | 0.016603 | 0.049473 | -0.015449 | 0.067116 | 0.013733 | 122.2595 | -0.18768 | 0.11444 | 121.6049 | 3.4744 | 0.43488 | 0.59052 | 122.3831 | -0.21973 | -0.086975 | -0.013733 | 0.11444 | 0.21515 | -0.66833 | -0.11902 | 0.10986 | 0.20142 | 0.53558 | 0.69122 | 121.7056 | 122.3602 | 0.11444 | 122.4838 | 3.5751 | -0.11902 | 122.3602 | 0.11444 | 3.5751 | 121.7056 | 122.4838 | -122.4609 | -122.493
3138.2031 | 122.4564 | -0.036621 | 122.2092 | 0.11482 | 0.011551 | -0.0091325 | 0.014039 | 0.049473 | -0.013313 | 0.065834 | -0.054932 | 122.2687 | -0.18768 | 0.032043 | 121.5408 | 3.3417 | 0.28839 | 0.32044 | 122.4564 | -0.21515 | -0.15106 | 0.05951 | -0.018311 | 0.068664 | -0.66833 | -0.17853 | 0.24719 | 0.13275 | 0.32501 | 0.35706 | 121.5775 | 122.3053 | -0.018311 | 122.493 | 3.3783 | -0.17853 | 122.3053 | -0.018311 | 3.3783 | 121.5775 | 122.493 | -122.3969 | -122.4243
3139.9531 | 122.3557 | -0.073242 | 122.2504 | -0.16747 | 0.009628 | -0.015541 | 0.014894 | 0.048832 | -0.01374 | 0.064766 | -0.059509 | 122.2549 | -0.18768 | 0.045776 | 121.5683 | 3.5019 | 0.6134 | 0.63629 | 122.4655 | -0.2243 | -0.11444 | 0.004578 | 0.013733 | 0.11902 | -0.68207 | -0.15106 | 0.21515 | 0.12817 | 0.68665 | 0.70953 | 121.6415 | 122.3282 | 0.013733 | 122.5388 | 3.5751 | -0.15106 | 122.3282 | 0.013733 | 3.5751 | 121.6415 | 122.5388 | -122.438 | -122.4747
3141.7188 | 122.493 | -0.045776 | 122.2137 | 0.00038159 | 0.0081326 | -0.016609 | 0.0069898 | 0.047978 | -0.012886 | 0.066902 | 0.004578 | 122.2687 | -0.15106 | 0.086975 | 121.6141 | 3.4332 | 0.33875 | 0.52643 | 122.3923 | -0.19684 | -0.10529 | 0.054932 | 0.050354 | 0.13275 | -0.59967 | -0.15106 | 0.17853 | 0.15564 | 0.38452 | 0.5722 | 121.6599 | 122.3145 | 0.050354 | 122.438 | 3.479 | -0.15106 | 122.3145 | 0.050354 | 3.479 | 121.6599 | 122.438 | -122.3648 | -122.4106
3143.4062 | 122.3694 | -0.09613 | 122.2458 | -0.22087 | 0.010269 | -0.010841 | 0.010194 | 0.047764 | -0.011604 | 0.065193 | 0.022888 | 122.2412 | -0.14191 | 0.11444 | 121.6278 | 3.5568 | 0.59967 | 0.75531 | 122.3831 | -0.21973 | -0.045777 | -0.004578 | 0.11902 | 0.21057 | -0.61798 | -0.1236 | 0.13733 | 0.16479 | 0.6958 | 0.85144 | 121.7239 | 122.3373 | 0.11902 | 122.4792 | 3.653 | -0.1236 | 122.3373 | 0.11902 | 3.653 | 121.7239 | 122.4792 | -122.3877 | -122.4655
3145.1562 | 122.3282 | -0.10986 | 122.2595 | -0.20561 | 0.0094144 | -0.0069961 | 0.011476 | 0.04691 | -0.011177 | 0.064553 | 0.032043 | 122.2778 | -0.14648 | 0.13733 | 121.6415 | 3.5751 | 0.56305 | 0.77362 | 122.3557 | -0.21515 | -0.036621 | 0.018311 | 0.14191 | 0.24719 | -0.61798 | -0.10529 | 0.096131 | 0.17853 | 0.67291 | 0.88348 | 121.7514 | 122.3877 | 0.14191 | 122.4655 | 3.685 | -0.10529 | 122.3877 | 0.14191 | 3.685 | 121.7514 | 122.4655 | -122.406 | -122.4747
3146.9062 | 122.3877 | -0.064087 | 122.2458 | -0.17509 | 0.010696 | -0.010841 | 0.0095532 | 0.046482 | -0.01139 | 0.066475 | 0.050354 | 122.2595 | -0.14648 | 0.15564 | 121.669 | 3.5614 | 0.40741 | 0.74616 | 122.3328 | -0.18768 | -0.082397 | 0.013732 | 0.11444 | 0.21973 | -0.57678 | -0.1236 | 0.086975 | 0.19684 | 0.4715 | 0.81024 | 121.7331 | 122.3236 | 0.11444 | 122.3969 | 3.6255 | -0.1236 | 122.3236 | 0.11444 | 3.6255 | 121.7331 | 122.3969 | -122.3923 | -122.4335
3148.6094 | 122.4014 | -0.073242 | 122.2275 | 0.16823 | 0.0085598 | -0.0063553 | 0.013185 | 0.047978 | -0.014167 | 0.066262 | 0.059509 | 122.2137 | -0.14648 | 0.16479 | 121.6324 | 3.4332 | 0.1236 | 0.49896 | 122.3648 | -0.1831 | -0.073242 | -0.013733 | 0.13275 | 0.23804 | -0.59509 | -0.10986 | 0.13733 | 0.20599 | 0.19684 | 0.5722 | 121.7056 | 122.287 | 0.13275 | 122.438 | 3.5065 | -0.10986 | 122.287 | 0.13275 | 3.5065 | 121.7056 | 122.438 | -122.374 | -122.4106
3150.375 | 122.4152 | -0.064087 | 122.2366 | 0.1606 | 0.0087734 | -0.011055 | 0.013398 | 0.047978 | -0.013527 | 0.066475 | 0.064087 | 122.2549 | -0.12817 | 0.15106 | 121.6461 | 3.4332 | 0.13733 | 0.47607 | 122.374 | -0.17853 | -0.064087 | 0.018311 | 0.12817 | 0.21515 | -0.59051 | -0.11444 | 0.13733 | 0.19226 | 0.20142 | 0.54016 | 121.7102 | 122.319 | 0.12817 | 122.438 | 3.4973 | -0.11444 | 122.319 | 0.12817 | 3.4973 | 121.7102 | 122.438 | -122.3648 | -122.4152
3152.1562 | 122.4152 | -0.054932 | 122.2321 | 0.17586 | 0.012405 | -0.011696 | 0.01468 | 0.047978 | -0.012245 | 0.066262 | 0.009155 | 122.2641 | -0.16937 | 0.12817 | 121.6049 | 3.4103 | 0.16022 | 0.42572 | 122.4014 | -0.20142 | -0.11444 | 0.032043 | 0.064087 | 0.18311 | -0.62714 | -0.14648 | 0.16937 | 0.17853 | 0.21515 | 0.48065 | 121.6599 | 122.319 | 0.064087 | 122.4564 | 3.4653 | -0.14648 | 122.319 | 0.064087 | 3.4653 | 121.6599 | 122.4564 | -122.4014 | -122.4335
3153.8438 | 122.4518 | -0.050354 | 122.2321 | -0.0072479 | 0.010482 | -0.0093461 | 0.0076306 | 0.04755 | -0.011818 | 0.065834 | -0.009155 | 122.287 | -0.15564 | 0.10986 | 121.6187 | 3.4698 | 0.37537 | 0.59509 | 122.3831 | -0.20599 | -0.10529 | 0.054931 | 0.041199 | 0.16022 | -0.6134 | -0.15564 | 0.15106 | 0.14649 | 0.42572 | 0.64545 | 121.669 | 122.3373 | 0.041199 | 122.4335 | 3.5202 | -0.15564 | 122.3373 | 0.041199 | 3.5202 | 121.669 | 122.4335 | -122.3877 | -122.4381
3155.5938 | 122.3373 | -0.082397 | 122.2549 | -0.14458 | 0.011978 | -0.014687 | 0.01233 | 0.047764 | -0.010322 | 0.065621 | 0.082397 | 122.2092 | -0.15106 | 0.19226 | 121.6736 | 3.5934 | 0.42114 | 0.78278 | 122.3877 | -0.20599 | -0.068665 | -0.045777 | 0.16479 | 0.27466 | -0.58136 | -0.1236 | 0.13275 | 0.23346 | 0.50354 | 0.86517 | 121.756 | 122.2916 | 0.16479 | 122.4701 | 3.6758 | -0.1236 | 122.2916 | 0.16479 | 3.6758 | 121.756 | 122.4701 | -122.406 | -122.4609
3157.3594 | 122.3099 | -0.10529 | 122.2641 | -0.091171 | 0.0087734 | -0.011269 | 0.017671 | 0.048405 | -0.013527 | 0.065621 | 0.009155 | 122.2595 | -0.21057 | 0.13733 | 121.5912 | 3.511 | 0.44861 | 0.58594 | 122.3923 | -0.22888 | -0.10529 | -0.004578 | 0.11444 | 0.24262 | -0.67291 | -0.1236 | 0.12817 | 0.21973 | 0.55389 | 0.69122 | 121.6965 | 122.3648 | 0.11444 | 122.4976 | 3.6163 | -0.1236 | 122.3648 | 0.11444 | 3.6163 | 121.6965 | 122.4976 | -122.4747 | -122.493
3159.0625 | 122.4289 | -0.054932 | 122.2458 | 0.19112 | 0.0083462 | -0.0078507 | 0.013826 | 0.050114 | -0.013954 | 0.066262 | 0.009155 | 122.2733 | -0.15564 | 0.10529 | 121.6095 | 3.3966 | 0.15106 | 0.41199 | 122.3557 | -0.20142 | -0.10071 | 0.027465 | 0.064087 | 0.16022 | -0.63629 | -0.14648 | 0.10986 | 0.16479 | 0.20599 | 0.46692 | 121.6644 | 122.3282 | 0.064087 | 122.4106 | 3.4515 | -0.14648 | 122.3282 | 0.064087 | 3.4515 | 121.6644 | 122.4106 | -122.4014 | -122.4472
3160.8281 | 122.3145 | -0.09613 | 122.2778 | -0.12169 | 0.010482 | -0.010414 | 0.014467 | 0.050328 | -0.012031 | 0.064553 | 0.009155 | 122.2733 | -0.16937 | 0.11902 | 121.5912 | 3.5248 | 0.48065 | 0.59052 | 122.4106 | -0.21515 | -0.073243 | -0.004578 | 0.10528 | 0.21515 | -0.68664 | -0.11902 | 0.13275 | 0.17853 | 0.57678 | 0.68664 | 121.6873 | 122.3694 | 0.10528 | 122.5067 | 3.6209 | -0.11902 | 122.3694 | 0.10528 | 3.6209 | 121.6873 | 122.5067 | -122.4472 | -122.493
3162.5938 | 122.3328 | -0.10529 | 122.2778 | -0.17509 | 0.012405 | -0.0102 | 0.0093396 | 0.047978 | -0.010322 | 0.064766 | 0.059509 | 122.2641 | -0.14648 | 0.13733 | 121.669 | 3.598 | 0.54474 | 0.7782 | 122.406 | -0.21057 | -0.041198 | -0.013733 | 0.16479 | 0.24262 | -0.60883 | -0.10529 | 0.12817 | 0.20599 | 0.65002 | 0.88348 | 121.7743 | 122.3694 | 0.16479 | 122.5113 | 3.7033 | -0.10529 | 122.3694 | 0.16479 | 3.7033 | 121.7743 | 122.5113 | -122.4243 | -122.4884
3164.3594 | 122.3236 | -0.10529 | 122.2412 | -0.10643 | 0.010055 | -0.0084915 | 0.013185 | 0.050114 | -0.015449 | 0.06498 | 0.013733 | 122.2275 | -0.17395 | 0.10529 | 121.6003 | 3.5248 | 0.4715 | 0.59967 | 122.4655 | -0.21973 | -0.068664 | -0.013733 | 0.11902 | 0.21057 | -0.64087 | -0.11444 | 0.2243 | 0.18768 | 0.57678 | 0.70496 | 121.7056 | 122.3328 | 0.11902 | 122.5708 | 3.6301 | -0.11444 | 122.3328 | 0.11902 | 3.6301 | 121.7056 | 122.5708 | -122.4152 | -122.4609
3166.1094 | 122.3373 | -0.10986 | 122.2549 | -0.15221 | 0.010269 | -0.013191 | 0.0076306 | 0.048405 | -0.012245 | 0.065407 | 0.07782 | 122.2549 | -0.12817 | 0.15564 | 121.701 | 3.5843 | 0.43945 | 0.7782 | 122.3694 | -0.18768 | -0.018311 | 0 | 0.18768 | 0.2655 | -0.55389 | -0.07782 | 0.11444 | 0.20599 | 0.54932 | 0.88806 | 121.8109 | 122.3648 | 0.18768 | 122.4792 | 3.6942 | -0.07782 | 122.3648 | 0.18768 | 3.6942 | 121.8109 | 122.4792 | -122.3831 | -122.4426
3167.8125 | 122.4152 | -0.054932 | 122.2321 | 0.14534 | 0.009628 | -0.010628 | 0.015321 | 0.049687 | -0.012245 | 0.066902 | 0.045776 | 122.2595 | -0.14648 | 0.12817 | 121.6187 | 3.4332 | 0.13733 | 0.45319 | 122.3923 | -0.19226 | -0.091552 | 0.027465 | 0.10071 | 0.18311 | -0.6134 | -0.13733 | 0.16022 | 0.19226 | 0.19226 | 0.50812 | 121.6736 | 122.3145 | 0.10071 | 122.4472 | 3.4882 | -0.13733 | 122.3145 | 0.10071 | 3.4882 | 121.6736 | 122.4472 | -122.3785 | -122.4243
3169.5781 | 122.4152 | -0.082397 | 122.2366 | 0.19112 | 0.0085598 | -0.0091325 | 0.012117 | 0.048191 | -0.012886 | 0.065621 | 0.059509 | 122.2504 | -0.14648 | 0.15106 | 121.637 | 3.4515 | 0.1236 | 0.48065 | 122.3877 | -0.1831 | -0.064087 | 0.013733 | 0.14191 | 0.23346 | -0.59967 | -0.10071 | 0.15106 | 0.20599 | 0.20599 | 0.56305 | 121.7194 | 122.3328 | 0.14191 | 122.4701 | 3.5339 | -0.10071 | 122.3328 | 0.14191 | 3.5339 | 121.7194 | 122.4701 | -122.3831 | -122.4197
3171.3438 | 122.374 | -0.068665 | 122.2458 | -0.22087 | 0.01091 | -0.011696 | 0.014039 | 0.047764 | -0.012031 | 0.064553 | -0.041199 | 122.3053 | -0.19684 | 0.036621 | 121.55 | 3.5202 | 0.62714 | 0.62714 | 122.4243 | -0.23804 | -0.12817 | 0.059509 | 0.027466 | 0.10529 | -0.6958 | -0.16937 | 0.17853 | 0.15564 | 0.6958 | 0.6958 | 121.6187 | 122.374 | 0.027466 | 122.493 | 3.5889 | -0.16937 | 122.374 | 0.027466 | 3.5889 | 121.6187 | 122.493 | -122.4426 | -122.4838
3173.1094 | 122.4197 | -0.050354 | 122.2183 | 0.038529 | 0.011551 | -0.0078507 | 0.013185 | 0.050328 | -0.013954 | 0.066475 | -0.054932 | 122.2595 | -0.18768 | 0.027466 | 121.5317 | 3.3691 | 0.35248 | 0.37079 | 122.4426 | -0.23804 | -0.13733 | 0.041198 | -0.004578 | 0.07782 | -0.68665 | -0.18768 | 0.2243 | 0.13275 | 0.40283 | 0.42114 | 121.582 | 122.3099 | -0.004578 | 122.493 | 3.4195 | -0.18768 | 122.3099 | -0.004578 | 3.4195 | 121.582 | 122.493 | -122.406 | -122.4564
3174.7969 | 122.4609 | -0.054932 | 122.2412 | 0.069046 | 0.0070646 | -0.010628 | 0.0054944 | 0.048832 | -0.01075 | 0.065407 | 0.004578 | 122.2458 | -0.14191 | 0.09613 | 121.6049 | 3.4287 | 0.25635 | 0.51727 | 122.3557 | -0.1831 | -0.086975 | 0.004578 | 0.05951 | 0.15106 | -0.63629 | -0.12817 | 0.11444 | 0.14649 | 0.31128 | 0.5722 | 121.6599 | 122.3007 | 0.05951 | 122.4106 | 3.4836 | -0.12817 | 122.3007 | 0.05951 | 3.4836 | 121.6599 | 122.4106 | -122.3831 | -122.4243
3176.5625 | 122.3602 | -0.09613 | 122.2595 | -0.12932 | 0.007919 | -0.013832 | 0.0095532 | 0.049046 | -0.011818 | 0.065834 | 0.059509 | 122.2275 | -0.11902 | 0.16479 | 121.6782 | 3.598 | 0.42114 | 0.75073 | 122.3923 | -0.21057 | -0.022889 | -0.032043 | 0.15564 | 0.26092 | -0.58136 | -0.11444 | 0.13275 | 0.17853 | 0.51727 | 0.84686 | 121.7743 | 122.3236 | 0.15564 | 122.4884 | 3.6942 | -0.11444 | 122.3236 | 0.15564 | 3.6942 | 121.7743 | 122.4884 | -122.3785 | -122.4701
3178.2656 | 122.3419 | -0.10529 | 122.2687 | -0.068283 | 0.01091 | -0.011909 | 0.016816 | 0.049046 | -0.014595 | 0.066902 | 0.009155 | 122.2549 | -0.18768 | 0.11902 | 121.582 | 3.4973 | 0.40283 | 0.55389 | 122.406 | -0.21973 | -0.082397 | -0.013733 | 0.11444 | 0.22431 | -0.68665 | -0.11444 | 0.13733 | 0.19684 | 0.50812 | 0.65918 | 121.6873 | 122.3602 | 0.11444 | 122.5113 | 3.6026 | -0.11444 | 122.3602 | 0.11444 | 3.6026 | 121.6873 | 122.5113 | -122.4564 | -122.4884
3180.0312 | 122.4976 | -0.091553 | 122.2321 | -0.17509 | 0.0087734 | -0.01725 | 0.0086988 | 0.047337 | -0.014381 | 0.065834 | 0.018311 | 122.2824 | -0.1831 | 0.11444 | 121.6232 | 3.5614 | 0.67291 | 0.72784 | 122.4106 | -0.23804 | -0.091552 | 0.050354 | 0.10986 | 0.20599 | -0.60883 | -0.14648 | 0.17853 | 0.20142 | 0.76447 | 0.8194 | 121.7148 | 122.374 | 0.10986 | 122.5021 | 3.653 | -0.14648 | 122.374 | 0.10986 | 3.653 | 121.7148 | 122.5021 | -122.4152 | -122.4701
3181.7969 | 122.4518 | -0.10986 | 122.2687 | -0.068283 | 0.010055 | -0.012123 | 0.015107 | 0.047337 | -0.01374 | 0.067116 | 0.064087 | 122.2733 | -0.17853 | 0.16479 | 121.6599 | 3.5248 | 0.41657 | 0.55847 | 122.4243 | -0.2243 | -0.068665 | 0.004577 | 0.17395 | 0.27466 | -0.60883 | -0.11444 | 0.15564 | 0.24261 | 0.52643 | 0.66834 | 121.7697 | 122.3831 | 0.17395 | 122.5342 | 3.6346 | -0.11444 | 122.3831 | 0.17395 | 3.6346 | 121.7697 | 122.5342 | -122.4472 | -122.493
3183.5 | 122.374 | -0.09613 | 122.2641 | -0.24376 | 0.0085598 | -0.011909 | 0.007417 | 0.046055 | -0.010322 | 0.065407 | -0.018311 | 122.2916 | -0.15106 | 0.054932 | 121.5775 | 3.5522 | 0.63629 | 0.6958 | 122.4197 | -0.23346 | -0.054932 | 0.027466 | 0.077819 | 0.15106 | -0.68664 | -0.13733 | 0.15564 | 0.13275 | 0.73242 | 0.79193 | 121.6736 | 122.3877 | 0.077819 | 122.5159 | 3.6484 | -0.13733 | 122.3877 | 0.077819 | 3.6484 | 121.6736 | 122.5159 | -122.4152 | -122.4976
3185.2656 | 122.3419 | -0.091553 | 122.2687 | -0.16747 | 0.010696 | -0.0093461 | 0.012544 | 0.048619 | -0.013954 | 0.064766 | -0.045776 | 122.287 | -0.20142 | 0.073242 | 121.5591 | 3.5294 | 0.59509 | 0.63629 | 122.4564 | -0.23346 | -0.10986 | 0.01831 | 0.045777 | 0.16479 | -0.70953 | -0.14191 | 0.18768 | 0.15564 | 0.68665 | 0.72784 | 121.6507 | 122.3785 | 0.045777 | 122.5479 | 3.6209 | -0.14191 | 122.3785 | 0.045777 | 3.6209 | 121.6507 | 122.5479 | -122.4701 | -122.5021
3186.9688 | 122.3785 | -0.10071 | 122.2824 | -0.24376 | 0.011551 | -0.012123 | 0.010621 | 0.049259 | -0.012031 | 0.06498 | -0.041199 | 122.3099 | -0.20142 | 0.041199 | 121.5683 | 3.5202 | 0.68207 | 0.67291 | 122.4335 | -0.23804 | -0.10071 | 0.027465 | 0.059509 | 0.14191 | -0.71411 | -0.13733 | 0.15106 | 0.16022 | 0.78278 | 0.77362 | 121.669 | 122.4106 | 0.059509 | 122.5342 | 3.6209 | -0.13733 | 122.4106 | 0.059509 | 3.6209 | 121.669 | 122.5342 | -122.4838 | -122.5204
3188.7188 | 122.3236 | -0.09613 | 122.2824 | -0.10643 | 0.0098416 | -0.011696 | 0.015962 | 0.049687 | -0.012031 | 0.067116 | 0 | 122.2733 | -0.16479 | 0.10071 | 121.5866 | 3.5294 | 0.45319 | 0.60883 | 122.4335 | -0.21515 | -0.068665 | -0.009156 | 0.09613 | 0.19684 | -0.6958 | -0.11902 | 0.15106 | 0.16479 | 0.54932 | 0.70496 | 121.6827 | 122.3694 | 0.09613 | 122.5296 | 3.6255 | -0.11902 | 122.3694 | 0.09613 | 3.6255 | 121.6827 | 122.5296 | -122.4472 | -122.4976
3190.4688 | 122.4243 | -0.045776 | 122.2366 | 0.18349 | 0.0089872 | -0.010841 | 0.010621 | 0.048191 | -0.012886 | 0.067116 | -0.027466 | 122.2641 | -0.16937 | 0.091553 | 121.582 | 3.4103 | 0.16937 | 0.39368 | 122.4106 | -0.20142 | -0.1236 | 0.027466 | 0.01831 | 0.13733 | -0.6546 | -0.15564 | 0.17395 | 0.14191 | 0.21515 | 0.43945 | 121.6278 | 122.3099 | 0.01831 | 122.4564 | 3.4561 | -0.15564 | 122.3099 | 0.01831 | 3.4561 | 121.6278 | 122.4564 | -122.406 | -122.438
3192.1875 | 122.3511 | -0.11902 | 122.2778 | -0.22087 | 0.0077054 | -0.0082779 | 0.0093396 | 0.047123 | -0.012458 | 0.06498 | 0.013733 | 122.2641 | -0.15106 | 0.1236 | 121.6553 | 3.6118 | 0.57678 | 0.78278 | 122.3831 | -0.20599 | -0.032043 | -0.013733 | 0.13275 | 0.24261 | -0.62256 | -0.086975 | 0.10529 | 0.16479 | 0.6958 | 0.9018 | 121.7743 | 122.3831 | 0.13275 | 122.5021 | 3.7308 | -0.086975 | 122.3831 | 0.13275 | 3.7308 | 121.7743 | 122.5021 | -122.4289 | -122.4838
3193.9531 | 122.4792 | -0.059509 | 122.2412 | -0.014877 | 0.010269 | -0.0087051 | 0.0072034 | 0.043919 | -0.0096814 | 0.066475 | 0 | 122.2733 | -0.13733 | 0.082397 | 121.5958 | 3.4698 | 0.36163 | 0.55847 | 122.3831 | -0.20142 | -0.07782 | 0.032043 | 0.059509 | 0.14191 | -0.64545 | -0.14191 | 0.14191 | 0.13733 | 0.42114 | 0.61798 | 121.6553 | 122.3328 | 0.059509 | 122.4426 | 3.5294 | -0.14191 | 122.3328 | 0.059509 | 3.5294 | 121.6553 | 122.4426 | -122.3785 | -122.4426
3195.7031 | 122.493 | -0.045776 | 122.2366 | 0.01564 | 0.010055 | -0.011696 | 0.0078442 | 0.044132 | -0.013099 | 0.068184 | -0.027466 | 122.2229 | -0.16022 | 0.07782 | 121.5958 | 3.4607 | 0.33875 | 0.56305 | 122.374 | -0.20142 | -0.11444 | -0.013733 | 0.01831 | 0.1236 | -0.64087 | -0.15564 | 0.13733 | 0.13275 | 0.38452 | 0.60883 | 121.6415 | 122.2687 | 0.01831 | 122.4197 | 3.5065 | -0.15564 | 122.2687 | 0.01831 | 3.5065 | 121.6415 | 122.4197 | -122.3969 | -122.438
3197.4688 | 122.3419 | -0.10986 | 122.2778 | -0.19798 | 0.0083462 | -0.0089189 | 0.011262 | 0.046055 | -0.012245 | 0.063912 | 0.054932 | 122.2412 | -0.15106 | 0.17853 | 121.6507 | 3.6301 | 0.48981 | 0.80566 | 122.3785 | -0.18768 | -0.041199 | -0.036621 | 0.16479 | 0.28839 | -0.62714 | -0.07782 | 0.10071 | 0.20599 | 0.59967 | 0.91553 | 121.7606 | 122.3511 | 0.16479 | 122.4884 | 3.7399 | -0.07782 | 122.3511 | 0.16479 | 3.7399 | 121.7606 | 122.4884 | -122.4289 | -122.4655
3199.2344 | 122.3694 | -0.086975 | 122.2549 | -0.15984 | 0.01091 | -0.012764 | 0.01233 | 0.046696 | -0.01374 | 0.066475 | -0.050354 | 122.2504 | -0.1831 | 0.068665 | 121.5408 | 3.5339 | 0.6546 | 0.67749 | 122.438 | -0.21973 | -0.09613 | -0.004578 | 0.036621 | 0.15564 | -0.71411 | -0.13275 | 0.18311 | 0.13275 | 0.74158 | 0.76447 | 121.6278 | 122.3373 | 0.036621 | 122.525 | 3.6209 | -0.13275 | 122.3373 | 0.036621 | 3.6209 | 121.6278 | 122.525 | -122.438 | -122.4747
3200.9375 | 122.3145 | -0.09613 | 122.2916 | -0.15221 | 0.0092008 | -0.012764 | 0.014894 | 0.049473 | -0.01374 | 0.066048 | 0.013733 | 122.2687 | -0.17853 | 0.10071 | 121.5775 | 3.5477 | 0.48981 | 0.6134 | 122.4335 | -0.21515 | -0.082398 | -0.022888 | 0.10986 | 0.19684 | -0.71411 | -0.11902 | 0.14191 | 0.19226 | 0.58594 | 0.70953 | 121.6736 | 122.3648 | 0.10986 | 122.5296 | 3.6438 | -0.11902 | 122.3648 | 0.10986 | 3.6438 | 121.6736 | 122.5296 | -122.4701 | -122.5067
3202.6406 | 122.3831 | -0.091553 | 122.2595 | -0.20561 | 0.009628 | -0.012123 | 0.011262 | 0.048405 | -0.012672 | 0.064339 | -0.041199 | 122.287 | -0.20142 | 0.054932 | 121.5546 | 3.5385 | 0.65918 | 0.67291 | 122.4289 | -0.24261 | -0.10986 | 0.027466 | 0.050354 | 0.14649 | -0.70496 | -0.15106 | 0.16937 | 0.16022 | 0.75073 | 0.76447 | 121.6461 | 122.3785 | 0.050354 | 122.5204 | 3.6301 | -0.15106 | 122.3785 | 0.050354 | 3.6301 | 121.6461 | 122.5204 | -122.4609 | -122.5021
3204.3906 | 122.3465 | -0.10529 | 122.2412 | -0.068283 | 0.0094144 | -0.010841 | 0.015748 | 0.048191 | -0.015022 | 0.064766 | 0 | 122.2549 | -0.1831 | 0.11444 | 121.5958 | 3.5156 | 0.40283 | 0.52185 | 122.4243 | -0.21515 | -0.077819 | 0.013733 | 0.10529 | 0.21973 | -0.64545 | -0.10986 | 0.1831 | 0.1831 | 0.50812 | 0.62714 | 121.7011 | 122.3602 | 0.10529 | 122.5296 | 3.6209 | -0.10986 | 122.3602 | 0.10529 | 3.6209 | 121.7011 | 122.5296 | -122.4243 | -122.4564
3206.1562 | 122.3465 | -0.10529 | 122.2687 | -0.068283 | 0.009628 | -0.012123 | 0.014039 | 0.050114 | -0.013313 | 0.065193 | 0.009155 | 122.2687 | -0.17395 | 0.10529 | 121.5912 | 3.511 | 0.39825 | 0.54016 | 122.4609 | -0.21057 | -0.068664 | 0 | 0.11444 | 0.21057 | -0.67749 | -0.10529 | 0.19226 | 0.1831 | 0.50354 | 0.64545 | 121.6965 | 122.374 | 0.11444 | 122.5662 | 3.6163 | -0.10529 | 122.374 | 0.11444 | 3.6163 | 121.6965 | 122.5662 | -122.4426 | -122.4792
3207.8594 | 122.4701 | -0.068665 | 122.2366 | -0.014877 | 0.0087734 | -0.015114 | 0.0054944 | 0.047337 | -0.010963 | 0.063698 | -0.009155 | 122.287 | -0.15106 | 0.091553 | 121.637 | 3.5248 | 0.38452 | 0.63629 | 122.3969 | -0.20142 | -0.082397 | 0.050354 | 0.05951 | 0.16022 | -0.59967 | -0.13275 | 0.16022 | 0.14191 | 0.45319 | 0.70496 | 121.7056 | 122.3557 | 0.05951 | 122.4655 | 3.5934 | -0.13275 | 122.3557 | 0.05951 | 3.5934 | 121.7056 | 122.4655 | -122.3877 | -122.438
3209.625 | 122.4747 | -0.068665 | 122.2137 | 0.038529 | 0.0094144 | -0.0078507 | 0.0086988 | 0.048191 | -0.01075 | 0.06797 | 0.013733 | 122.2733 | -0.14648 | 0.082397 | 121.6141 | 3.4744 | 0.32044 | 0.54474 | 122.3785 | -0.20142 | -0.077819 | 0.059509 | 0.082398 | 0.15106 | -0.59967 | -0.13275 | 0.16479 | 0.16022 | 0.3891 | 0.6134 | 121.6827 | 122.3419 | 0.082398 | 122.4472 | 3.5431 | -0.13275 | 122.3419 | 0.082398 | 3.5431 | 121.6827 | 122.4472 | -122.3602 | -122.4152
3211.3906 | 122.4518 | -0.054932 | 122.2229 | 0.076676 | 0.010696 | -0.010841 | 0.016816 | 0.048832 | -0.014808 | 0.065834 | -0.059509 | 122.2916 | -0.17395 | 0.027466 | 121.5317 | 3.3875 | 0.3067 | 0.32959 | 122.438 | -0.22888 | -0.11902 | 0.068665 | -0.004577 | 0.082398 | -0.69122 | -0.17395 | 0.21515 | 0.11444 | 0.36163 | 0.38452 | 121.5866 | 122.3465 | -0.004577 | 122.493 | 3.4424 | -0.17395 | 122.3465 | -0.004577 | 3.4424 | 121.5866 | 122.493 | -122.3969 | -122.4518
3213.0938 | 122.3236 | -0.09613 | 122.2321 | -0.21324 | 0.0057828 | -0.012337 | 0.0086988 | 0.048405 | -0.009895 | 0.065621 | 0.050354 | 122.2824 | -0.14191 | 0.16022 | 121.6782 | 3.6209 | 0.48523 | 0.8194 | 122.406 | -0.19684 | -0.045777 | 0.050354 | 0.14648 | 0.25635 | -0.55389 | -0.10071 | 0.17395 | 0.19226 | 0.58136 | 0.91553 | 121.7743 | 122.3785 | 0.14648 | 122.5021 | 3.717 | -0.10071 | 122.3785 | 0.14648 | 3.717 | 121.7743 | 122.5021 | -122.374 | -122.4289
3214.8594 | 122.3511 | -0.10529 | 122.2733 | -0.19798 | 0.0077054 | -0.0082779 | 0.0099804 | 0.048832 | -0.013527 | 0.06498 | 0.045776 | 122.2092 | -0.14648 | 0.15564 | 121.6553 | 3.6346 | 0.52643 | 0.79193 | 122.3969 | -0.1831 | -0.041198 | -0.064087 | 0.15106 | 0.26093 | -0.61798 | -0.077819 | 0.1236 | 0.19226 | 0.63171 | 0.89722 | 121.7606 | 122.3145 | 0.15106 | 122.5021 | 3.7399 | -0.077819 | 122.3145 | 0.15106 | 3.7399 | 121.7606 | 122.5021 | -122.4197 | -122.4564
3216.6406 | 122.3282 | -0.10986 | 122.2641 | -0.20561 | 0.010696 | -0.013832 | 0.011262 | 0.047978 | -0.012458 | 0.066689 | 0.054932 | 122.2321 | -0.14648 | 0.16937 | 121.6736 | 3.6346 | 0.48065 | 0.81024 | 122.4152 | -0.20142 | -0.036621 | -0.032043 | 0.16479 | 0.27924 | -0.59051 | -0.091553 | 0.15106 | 0.20142 | 0.59052 | 0.92011 | 121.7834 | 122.3419 | 0.16479 | 122.525 | 3.7445 | -0.091553 | 122.3419 | 0.16479 | 3.7445 | 121.7834 | 122.525 | -122.4106 | -122.4655
3218.4062 | 122.3282 | -0.10986 | 122.2778 | -0.075912 | 0.0085598 | -0.0084915 | 0.017457 | 0.050114 | -0.014595 | 0.06733 | 0.018311 | 122.2778 | -0.19684 | 0.10529 | 121.5912 | 3.5294 | 0.40741 | 0.54932 | 122.438 | -0.20599 | -0.086975 | 0 | 0.12817 | 0.21515 | -0.68664 | -0.096131 | 0.16022 | 0.21515 | 0.51727 | 0.65918 | 121.7011 | 122.3877 | 0.12817 | 122.5479 | 3.6392 | -0.096131 | 122.3877 | 0.12817 | 3.6392 | 121.7011 | 122.5479 | -122.4747 | -122.4838
3220.1562 | 122.3328 | -0.082397 | 122.2733 | -0.060654 | 0.01091 | -0.010841 | 0.016816 | 0.048619 | -0.014595 | 0.067543 | 0.018311 | 122.2824 | -0.1831 | 0.091553 | 121.5683 | 3.5065 | 0.40283 | 0.51727 | 122.4472 | -0.21057 | -0.10071 | 0.009156 | 0.10071 | 0.17395 | -0.70496 | -0.12817 | 0.17395 | 0.20142 | 0.48523 | 0.59967 | 121.6507 | 122.3648 | 0.10071 | 122.5296 | 3.5889 | -0.12817 | 122.3648 | 0.10071 | 3.5889 | 121.6507 | 122.5296 | -122.4564 | -122.4838
3221.8594 | 122.3602 | -0.091553 | 122.2595 | -0.2285 | 0.010696 | -0.0097733 | 0.0099804 | 0.049046 | -0.012672 | 0.065834 | -0.041199 | 122.2687 | -0.17853 | 0.059509 | 121.5683 | 3.5614 | 0.65918 | 0.70038 | 122.4106 | -0.24261 | -0.086975 | 0.009156 | 0.050354 | 0.15106 | -0.69122 | -0.15106 | 0.15106 | 0.13733 | 0.75073 | 0.79193 | 121.6599 | 122.3602 | 0.050354 | 122.5021 | 3.653 | -0.15106 | 122.3602 | 0.050354 | 3.653 | 121.6599 | 122.5021 | -122.438 | -122.5021
3223.625 | 122.3419 | -0.10529 | 122.2961 | -0.19035 | 0.009628 | -0.0082779 | 0.010194 | 0.046482 | -0.013313 | 0.063271 | 0.027466 | 122.2366 | -0.16022 | 0.14191 | 121.6461 | 3.6484 | 0.54016 | 0.78735 | 122.3969 | -0.21057 | -0.054931 | -0.05951 | 0.13275 | 0.24719 | -0.65002 | -0.10529 | 0.10071 | 0.18768 | 0.64545 | 0.89264 | 121.7514 | 122.3419 | 0.13275 | 122.5021 | 3.7537 | -0.10529 | 122.3419 | 0.13275 | 3.7537 | 121.7514 | 122.5021 | -122.4564 | -122.5067
3225.3281 | 122.4197 | -0.064087 | 122.2504 | 0.13008 | 0.011551 | -0.011909 | 0.015748 | 0.049473 | -0.015022 | 0.066475 | -0.041199 | 122.2687 | -0.1831 | 0.032043 | 121.5179 | 3.4195 | 0.37537 | 0.37537 | 122.4564 | -0.22888 | -0.11902 | 0.018311 | 0.022888 | 0.09613 | -0.73242 | -0.16479 | 0.20599 | 0.14191 | 0.43945 | 0.43945 | 121.582 | 122.3328 | 0.022888 | 122.5204 | 3.4836 | -0.16479 | 122.3328 | 0.022888 | 3.4836 | 121.582 | 122.5204 | -122.4335 | -122.4792
3227.0938 | 122.4609 | -0.050354 | 122.2412 | 0.099564 | 0.009628 | -0.0091325 | 0.0069898 | 0.046482 | -0.0096814 | 0.066048 | 0.004578 | 122.2458 | -0.15106 | 0.091553 | 121.6049 | 3.4515 | 0.25177 | 0.5127 | 122.3694 | -0.20599 | -0.10071 | 0.004578 | 0.054932 | 0.14191 | -0.63629 | -0.15564 | 0.12817 | 0.15564 | 0.30212 | 0.56305 | 121.6553 | 122.2961 | 0.054932 | 122.4197 | 3.5019 | -0.15564 | 122.2961 | 0.054932 | 3.5019 | 121.6553 | 122.4197 | -122.3923 | -122.4472
3228.7812 | 122.3145 | -0.10529 | 122.2778 | -0.098801 | 0.011551 | -0.013832 | 0.01468 | 0.047764 | -0.014167 | 0.066689 | 0.004578 | 122.2733 | -0.18768 | 0.11444 | 121.5958 | 3.5706 | 0.44861 | 0.59052 | 122.4289 | -0.21515 | -0.082397 | -0.004578 | 0.10986 | 0.21973 | -0.68207 | -0.10986 | 0.15106 | 0.19226 | 0.55389 | 0.6958 | 121.7011 | 122.3785 | 0.10986 | 122.5342 | 3.6758 | -0.10986 | 122.3785 | 0.10986 | 3.6758 | 121.7011 | 122.5342 | -122.4655 | -122.493
3230.5312 | 122.3282 | -0.10071 | 122.2778 | -0.14458 | 0.010055 | -0.011055 | 0.014253 | 0.0499 | -0.015449 | 0.065621 | -0.004578 | 122.2778 | -0.16937 | 0.09613 | 121.5775 | 3.566 | 0.5127 | 0.61798 | 122.4472 | -0.21515 | -0.068665 | 0 | 0.09613 | 0.19684 | -0.70038 | -0.11444 | 0.16937 | 0.16479 | 0.6134 | 0.71869 | 121.6782 | 122.3785 | 0.09613 | 122.5479 | 3.6667 | -0.11444 | 122.3785 | 0.09613 | 3.6667 | 121.6782 | 122.5479 | -122.4472 | -122.493
3232.2812 | 122.3557 | -0.091553 | 122.2412 | 0.0080111 | 0.0083462 | -0.016823 | 0.013826 | 0.049687 | -0.013527 | 0.066902 | -0.041199 | 122.2641 | -0.19684 | 0.050354 | 121.5317 | 3.4424 | 0.37537 | 0.41657 | 122.4472 | -0.21515 | -0.10529 | 0.022888 | 0.050354 | 0.14191 | -0.70953 | -0.1236 | 0.20599 | 0.15564 | 0.46692 | 0.50812 | 121.6232 | 122.3557 | 0.050354 | 122.5388 | 3.5339 | -0.1236 | 122.3557 | 0.050354 | 3.5339 | 121.6232 | 122.5388 | -122.438 | -122.4564
3234.0469 | 122.3282 | -0.11444 | 122.2641 | -0.19035 | 0.010269 | -0.012337 | 0.0052808 | 0.048832 | -0.012031 | 0.066262 | 0.050354 | 122.2916 | -0.13733 | 0.15106 | 121.669 | 3.6621 | 0.5127 | 0.79193 | 122.3923 | -0.19226 | -0.022888 | 0.027466 | 0.16479 | 0.2655 | -0.59509 | -0.07782 | 0.12817 | 0.18768 | 0.62714 | 0.90637 | 121.7834 | 122.406 | 0.16479 | 122.5067 | 3.7765 | -0.07782 | 122.406 | 0.16479 | 3.7765 | 121.7834 | 122.5067 | -122.4014 | -122.4564
3235.7344 | 122.4518 | -0.07782 | 122.2275 | 0.14534 | 0.011764 | -0.012764 | 0.0065624 | 0.047764 | -0.013313 | 0.066048 | 0.045776 | 122.2549 | -0.15106 | 0.091553 | 121.6232 | 3.479 | 0.21973 | 0.52643 | 122.4106 | -0.20142 | -0.073242 | 0.027466 | 0.1236 | 0.16937 | -0.60425 | -0.1236 | 0.1831 | 0.19684 | 0.29755 | 0.60425 | 121.7011 | 122.3328 | 0.1236 | 122.4884 | 3.5568 | -0.1236 | 122.3328 | 0.1236 | 3.5568 | 121.7011 | 122.4884 | -122.3785 | -122.4289
3237.5 | 122.3282 | -0.10529 | 122.2733 | -0.21324 | 0.0083462 | -0.0076371 | 0.0089124 | 0.04755 | -0.012031 | 0.066689 | 0.036621 | 122.2549 | -0.16022 | 0.16479 | 121.6553 | 3.6575 | 0.48981 | 0.80566 | 122.3923 | -0.19226 | -0.054931 | -0.01831 | 0.14191 | 0.27008 | -0.61798 | -0.086975 | 0.11902 | 0.19684 | 0.59509 | 0.91095 | 121.7606 | 122.3602 | 0.14191 | 122.4976 | 3.7628 | -0.086975 | 122.3602 | 0.14191 | 3.7628 | 121.7606 | 122.4976 | -122.4335 | -122.4655
3239.2656 | 122.3923 | -0.082397 | 122.2595 | -0.12169 | 0.011551 | -0.013405 | 0.008485 | 0.046482 | -0.011818 | 0.066902 | 0.036621 | 122.2504 | -0.16479 | 0.16022 | 121.6644 | 3.6255 | 0.39825 | 0.75531 | 122.3602 | -0.21057 | -0.082398 | -0.009155 | 0.11902 | 0.24261 | -0.59509 | -0.12817 | 0.10071 | 0.20142 | 0.48065 | 0.83771 | 121.7468 | 122.3328 | 0.11902 | 122.4426 | 3.7079 | -0.12817 | 122.3328 | 0.11902 | 3.7079 | 121.7468 | 122.4426 | -122.4243 | -122.4701
3241.0312 | 122.4838 | -0.050354 | 122.2275 | 0.030899 | 0.010269 | -0.0102 | 0.0086988 | 0.046055 | -0.0079724 | 0.066475 | -0.013733 | 122.2549 | -0.16022 | 0.086975 | 121.5958 | 3.4836 | 0.31586 | 0.53558 | 122.3694 | -0.19226 | -0.10986 | 0.027466 | 0.036621 | 0.13733 | -0.63171 | -0.14191 | 0.14191 | 0.14648 | 0.36621 | 0.58594 | 121.6461 | 122.3053 | 0.036621 | 122.4197 | 3.5339 | -0.14191 | 122.3053 | 0.036621 | 3.5339 | 121.6461 | 122.4197 | -122.3877 | -122.4197
3242.7969 | 122.4701 | -0.032043 | 122.2458 | 0.084305 | 0.011551 | -0.012123 | 0.016816 | 0.048191 | -0.012458 | 0.066048 | -0.022888 | 122.2595 | -0.19226 | 0.059509 | 121.5408 | 3.4012 | 0.26093 | 0.36163 | 122.4335 | -0.21973 | -0.16022 | 0.013732 | 0.009155 | 0.091552 | -0.70496 | -0.18768 | 0.18768 | 0.16937 | 0.29297 | 0.39368 | 121.5729 | 122.2916 | 0.009155 | 122.4655 | 3.4332 | -0.18768 | 122.2916 | 0.009155 | 3.4332 | 121.5729 | 122.4655 | -122.4381 | -122.4655
3244.5 | 122.3923 | -0.073242 | 122.2549 | -0.12932 | 0.0094144 | -0.011055 | 0.0082714 | 0.04456 | -0.0073316 | 0.065621 | 0.036621 | 122.2733 | -0.14191 | 0.15106 | 121.669 | 3.6072 | 0.41199 | 0.74616 | 122.3694 | -0.18768 | -0.068665 | 0.01831 | 0.10986 | 0.2243 | -0.58594 | -0.11444 | 0.11444 | 0.17853 | 0.48523 | 0.8194 | 121.7422 | 122.3465 | 0.10986 | 122.4426 | 3.6804 | -0.11444 | 122.3465 | 0.10986 | 3.6804 | 121.7422 | 122.4426 | -122.3969 | -122.4426
3246.2656 | 122.3419 | -0.09613 | 122.2824 | -0.16747 | 0.0085598 | -0.010841 | 0.010621 | 0.045201 | -0.013954 | 0.065621 | 0.032043 | 122.2549 | -0.14191 | 0.16022 | 121.6507 | 3.6758 | 0.50354 | 0.80566 | 122.3511 | -0.21973 | -0.045777 | -0.027466 | 0.12817 | 0.25635 | -0.63171 | -0.1236 | 0.068664 | 0.17395 | 0.59967 | 0.90179 | 121.7468 | 122.3511 | 0.12817 | 122.4472 | 3.772 | -0.1236 | 122.3511 | 0.12817 | 3.772 | 121.7468 | 122.4472 | -122.4243 | -122.5021
3248.0312 | 122.3282 | -0.07782 | 122.2778 | -0.053024 | 0.0092008 | -0.012337 | 0.017671 | 0.048405 | -0.014381 | 0.067116 | 0.009155 | 122.2824 | -0.16937 | 0.09613 | 121.5683 | 3.5385 | 0.40741 | 0.54474 | 122.406 | -0.21515 | -0.091553 | 0.004578 | 0.086975 | 0.17395 | -0.70953 | -0.13733 | 0.12817 | 0.17853 | 0.48523 | 0.62256 | 121.6461 | 122.3602 | 0.086975 | 122.4838 | 3.6163 | -0.13733 | 122.3602 | 0.086975 | 3.6163 | 121.6461 | 122.4838 | -122.4472 | -122.493
3249.7344 | 122.3785 | -0.086975 | 122.2504 | -0.14458 | 0.010055 | -0.016182 | 0.010835 | 0.044346 | -0.013954 | 0.066048 | -0.054932 | 122.2916 | -0.19226 | 0.054932 | 121.5546 | 3.566 | 0.66376 | 0.67749 | 122.4014 | -0.2243 | -0.10529 | 0.041199 | 0.032043 | 0.14191 | -0.6958 | -0.13733 | 0.15106 | 0.13733 | 0.75073 | 0.76447 | 121.6415 | 122.3785 | 0.032043 | 122.4884 | 3.653 | -0.13733 | 122.3785 | 0.032043 | 3.653 | 121.6415 | 122.4884 | -122.4426 | -122.4747
3251.4844 | 122.4152 | -0.086975 | 122.2549 | -0.098801 | 0.01091 | -0.0095597 | 0.0069898 | 0.046696 | -0.011818 | 0.066902 | 0.036621 | 122.2824 | -0.16022 | 0.16937 | 121.6782 | 3.6163 | 0.42572 | 0.74616 | 122.374 | -0.20142 | -0.073242 | 0.027466 | 0.1236 | 0.25635 | -0.57678 | -0.11444 | 0.11902 | 0.19684 | 0.5127 | 0.83313 | 121.7651 | 122.3694 | 0.1236 | 122.4609 | 3.7033 | -0.11444 | 122.3694 | 0.1236 | 3.7033 | 121.7651 | 122.4609 | -122.4152 | -122.4564
3253.2344 | 122.3602 | -0.091553 | 122.2412 | -0.25902 | 0.0094144 | -0.012337 | 0.010835 | 0.047978 | -0.012886 | 0.066262 | 0.027466 | 122.2916 | -0.16937 | 0.10986 | 121.6232 | 3.6346 | 0.60883 | 0.76446 | 122.3923 | -0.21973 | -0.07782 | 0.050354 | 0.11902 | 0.20142 | -0.61798 | -0.12817 | 0.15106 | 0.19684 | 0.70038 | 0.85602 | 121.7148 | 122.3831 | 0.11902 | 122.4838 | 3.7262 | -0.12817 | 122.3831 | 0.11902 | 3.7262 | 121.7148 | 122.4838 | -122.4106 | -122.4609
3255 | 122.3465 | -0.10986 | 122.2824 | -0.068283 | 0.0098416 | -0.011482 | 0.016816 | 0.050114 | -0.012245 | 0.066902 | 0.004578 | 122.2595 | -0.17395 | 0.09613 | 121.5683 | 3.5339 | 0.40283 | 0.54016 | 122.4472 | -0.21057 | -0.064087 | -0.022889 | 0.11444 | 0.20599 | -0.71411 | -0.10071 | 0.16479 | 0.17853 | 0.5127 | 0.65002 | 121.6782 | 122.3694 | 0.11444 | 122.5571 | 3.6438 | -0.10071 | 122.3694 | 0.11444 | 3.6438 | 121.6782 | 122.5571 | -122.4564 | -122.493
3256.7031 | 122.3419 | -0.10071 | 122.2733 | -0.16747 | 0.0087734 | -0.011909 | 0.009126 | 0.046269 | -0.012886 | 0.065193 | 0.032043 | 122.2687 | -0.14191 | 0.15564 | 121.6507 | 3.6621 | 0.51727 | 0.81482 | 122.3877 | -0.19684 | -0.041199 | -0.004577 | 0.13275 | 0.25635 | -0.62256 | -0.09613 | 0.11444 | 0.17395 | 0.61798 | 0.91553 | 121.7514 | 122.3694 | 0.13275 | 122.4884 | 3.7628 | -0.09613 | 122.3694 | 0.13275 | 3.7628 | 121.7514 | 122.4884 | -122.4152 | -122.4701
3258.4688 | 122.4152 | -0.068665 | 122.2549 | 0.17586 | 0.011764 | -0.011482 | 0.014467 | 0.048619 | -0.010963 | 0.066475 | 0.059509 | 122.2778 | -0.13275 | 0.15564 | 121.6599 | 3.4973 | 0.11902 | 0.49896 | 122.3373 | -0.18768 | -0.064086 | 0.022888 | 0.12817 | 0.22431 | -0.59509 | -0.11902 | 0.082397 | 0.19226 | 0.18768 | 0.56763 | 121.7285 | 122.3465 | 0.12817 | 122.406 | 3.566 | -0.11902 | 122.3465 | 0.12817 | 3.566 | 121.7285 | 122.406 | -122.3877 | -122.4426
3260.1719 | 122.3511 | -0.09613 | 122.2687 | -0.037765 | 0.009628 | -0.0087051 | 0.016816 | 0.045841 | -0.011177 | 0.066475 | 0.004578 | 122.287 | -0.17853 | 0.086975 | 121.5775 | 3.5202 | 0.3891 | 0.49439 | 122.4014 | -0.21973 | -0.082398 | 0.01831 | 0.10071 | 0.1831 | -0.69122 | -0.1236 | 0.13275 | 0.18311 | 0.48523 | 0.59052 | 121.6736 | 122.3831 | 0.10071 | 122.4976 | 3.6163 | -0.1236 | 122.3831 | 0.10071 | 3.6163 | 121.6736 | 122.4976 | -122.4472 | -122.4884
3261.9375 | 122.4472 | -0.045776 | 122.2229 | 0.091934 | 0.0083462 | -0.01255 | 0.015321 | 0.049046 | -0.01374 | 0.06733 | -0.050354 | 122.287 | -0.19226 | 0.036621 | 121.5637 | 3.4195 | 0.27924 | 0.35706 | 122.4426 | -0.24261 | -0.14648 | 0.064087 | -0.004578 | 0.082397 | -0.65918 | -0.19684 | 0.21973 | 0.14191 | 0.32501 | 0.40283 | 121.6095 | 122.3328 | -0.004578 | 122.4884 | 3.4653 | -0.19684 | 122.3328 | -0.004578 | 3.4653 | 121.6095 | 122.4884 | -122.4152 | -122.4655
3263.7031 | 122.3373 | -0.086975 | 122.2504 | -0.15221 | 0.011123 | -0.011696 | 0.01468 | 0.047764 | -0.01374 | 0.064339 | -0.022888 | 122.3007 | -0.17853 | 0.07782 | 121.5958 | 3.6072 | 0.53558 | 0.63629 | 122.4426 | -0.24261 | -0.091553 | 0.050354 | 0.064087 | 0.16479 | -0.6546 | -0.15564 | 0.19226 | 0.15564 | 0.62256 | 0.72327 | 121.6827 | 122.3877 | 0.064087 | 122.5296 | 3.6942 | -0.15564 | 122.3877 | 0.064087 | 3.6942 | 121.6827 | 122.5296 | -122.4289 | -122.493
3265.3906 | 122.4701 | -0.064087 | 122.2412 | 0.11482 | 0.01091 | -0.0091325 | 0.014894 | 0.050541 | -0.013954 | 0.066048 | -0.059509 | 122.2916 | -0.17395 | 0.022888 | 121.5363 | 3.4287 | 0.3067 | 0.33417 | 122.4472 | -0.23804 | -0.10986 | 0.050354 | 0.004578 | 0.086975 | -0.70496 | -0.17395 | 0.20599 | 0.11444 | 0.37079 | 0.39825 | 121.6003 | 122.3557 | 0.004578 | 122.5113 | 3.4927 | -0.17395 | 122.3557 | 0.004578 | 3.4927 | 121.6003 | 122.5113 | -122.4152 | -122.4792
3267.1562 | 122.3465 | -0.10529 | 122.287 | -0.19035 | 0.0089872 | -0.0078507 | 0.0097668 | 0.048191 | -0.01374 | 0.065621 | 0.036621 | 122.2549 | -0.14648 | 0.13733 | 121.6507 | 3.6621 | 0.5722 | 0.79651 | 122.4106 | -0.20142 | -0.041198 | -0.032043 | 0.14191 | 0.24262 | -0.63629 | -0.09613 | 0.1236 | 0.18311 | 0.67749 | 0.9018 | 121.756 | 122.3602 | 0.14191 | 122.5159 | 3.7674 | -0.09613 | 122.3602 | 0.14191 | 3.7674 | 121.756 | 122.5159 | -122.4335 | -122.4884
3268.9219 | 122.4609 | -0.059509 | 122.2275 | 0.084305 | 0.010482 | -0.0102 | 0.014894 | 0.047978 | -0.014595 | 0.067757 | -0.068665 | 122.287 | -0.1831 | 0.022888 | 121.5225 | 3.4378 | 0.32501 | 0.35248 | 122.4335 | -0.22888 | -0.1236 | 0.059509 | -0.009156 | 0.082397 | -0.70496 | -0.16937 | 0.20599 | 0.11444 | 0.38452 | 0.41199 | 121.582 | 122.3465 | -0.009156 | 122.493 | 3.4973 | -0.16937 | 122.3465 | -0.009156 | 3.4973 | 121.582 | 122.493 | -122.4106 | -122.4564
3270.6719 | 122.4335 | -0.054932 | 122.2229 | 0.15297 | 0.0085598 | -0.0074235 | 0.010408 | 0.050328 | -0.012245 | 0.06498 | 0.022888 | 122.2504 | -0.16937 | 0.11444 | 121.6278 | 3.511 | 0.15106 | 0.45319 | 122.3831 | -0.19226 | -0.11444 | 0.027466 | 0.07782 | 0.16937 | -0.59509 | -0.13733 | 0.16022 | 0.19226 | 0.20599 | 0.50812 | 121.6827 | 122.3053 | 0.07782 | 122.438 | 3.566 | -0.13733 | 122.3053 | 0.07782 | 3.566 | 121.6827 | 122.438 | -122.3923 | -122.4152
3272.375 | 122.3557 | -0.091553 | 122.2778 | -0.19798 | 0.010055 | -0.011482 | 0.007417 | 0.047978 | -0.012245 | 0.067543 | 0.032043 | 122.2549 | -0.13733 | 0.15564 | 121.669 | 3.6804 | 0.5127 | 0.8194 | 122.3923 | -0.21973 | -0.045776 | -0.022888 | 0.1236 | 0.24719 | -0.60883 | -0.12817 | 0.11444 | 0.16937 | 0.60425 | 0.91095 | 121.7606 | 122.3465 | 0.1236 | 122.4838 | 3.772 | -0.12817 | 122.3465 | 0.1236 | 3.772 | 121.7606 | 122.4838 | -122.4152 | -122.4976
3274.1406 | 122.4472 | -0.045776 | 122.2366 | 0.046158 | 0.010482 | -0.013832 | 0.017244 | 0.050114 | -0.013313 | 0.066262 | -0.064087 | 122.3053 | -0.1831 | 0.027466 | 121.5225 | 3.4378 | 0.37537 | 0.3479 | 122.438 | -0.21515 | -0.13733 | 0.068665 | -0.018311 | 0.073242 | -0.71411 | -0.16937 | 0.20142 | 0.11902 | 0.42114 | 0.39368 | 121.5683 | 122.3511 | -0.018311 | 122.4838 | 3.4836 | -0.16937 | 122.3511 | -0.018311 | 3.4836 | 121.5683 | 122.4838 | -122.4197 | -122.4518
3275.875 | 122.3373 | -0.10986 | 122.2641 | -0.19035 | 0.0081326 | -0.011696 | 0.008485 | 0.045201 | -0.010322 | 0.066689 | 0.050354 | 122.2824 | -0.13733 | 0.15564 | 121.669 | 3.6758 | 0.48981 | 0.81024 | 122.3648 | -0.20599 | -0.027466 | 0.018311 | 0.16022 | 0.2655 | -0.59509 | -0.096131 | 0.10071 | 0.18768 | 0.59967 | 0.92011 | 121.7789 | 122.3923 | 0.16022 | 122.4747 | 3.7857 | -0.096131 | 122.3923 | 0.16022 | 3.7857 | 121.7789 | 122.4747 | -122.4014 | -122.4701
3277.6406 | 122.319 | -0.086975 | 122.2504 | -0.083542 | 0.0094144 | -0.013832 | 0.013826 | 0.048832 | -0.014381 | 0.065193 | 0 | 122.2549 | -0.19226 | 0.11444 | 121.5912 | 3.5934 | 0.44861 | 0.59967 | 122.4289 | -0.21515 | -0.10529 | 0.004578 | 0.086975 | 0.20142 | -0.65918 | -0.12817 | 0.17853 | 0.19226 | 0.53558 | 0.68665 | 121.6782 | 122.3419 | 0.086975 | 122.5159 | 3.6804 | -0.12817 | 122.3419 | 0.086975 | 3.6804 | 121.6782 | 122.5159 | -122.4426 | -122.4655
3279.4219 | 122.4884 | -0.050354 | 122.2 | 0.01564 | 0.0089872 | -0.011696 | 0.0080578 | 0.046269 | -0.012672 | 0.065621 | 0 | 122.2641 | -0.14191 | 0.082397 | 121.6278 | 3.5294 | 0.36163 | 0.55847 | 122.4014 | -0.20142 | -0.091553 | 0.064087 | 0.050354 | 0.13275 | -0.5722 | -0.15106 | 0.20142 | 0.14191 | 0.41199 | 0.60883 | 121.6782 | 122.3145 | 0.050354 | 122.4518 | 3.5797 | -0.15106 | 122.3145 | 0.050354 | 3.5797 | 121.6782 | 122.4518 | -122.3419 | -122.4014
3281.125 | 122.3648 | -0.09613 | 122.2321 | -0.12169 | 0.0098416 | -0.011055 | 0.010408 | 0.045841 | -0.015449 | 0.065621 | -0.050354 | 122.2916 | -0.18768 | 0.054932 | 121.5546 | 3.5934 | 0.67749 | 0.69122 | 122.4335 | -0.21973 | -0.091553 | 0.059509 | 0.045776 | 0.15106 | -0.67749 | -0.1236 | 0.20142 | 0.13733 | 0.77362 | 0.78735 | 121.6507 | 122.3877 | 0.045776 | 122.5296 | 3.6896 | -0.1236 | 122.3877 | 0.045776 | 3.6896 | 121.6507 | 122.5296 | -122.4197 | -122.4518
3282.875 | 122.3511 | -0.09613 | 122.2595 | -0.13695 | 0.0081326 | -0.0089189 | 0.0078442 | 0.047764 | -0.010322 | 0.066689 | 0.045776 | 122.2733 | -0.14648 | 0.15564 | 121.6782 | 3.653 | 0.42572 | 0.7782 | 122.374 | -0.20142 | -0.050354 | 0.013733 | 0.14191 | 0.25177 | -0.58136 | -0.10529 | 0.11444 | 0.19226 | 0.52185 | 0.87433 | 121.7743 | 122.3694 | 0.14191 | 122.4701 | 3.7491 | -0.10529 | 122.3694 | 0.14191 | 3.7491 | 121.7743 | 122.4701 | -122.406 | -122.4609
3284.6406 | 122.4838 | -0.032043 | 122.2183 | 0.030899 | 0.0072782 | -0.0149 | 0.0097668 | 0.047764 | -0.010963 | 0.064766 | 0 | 122.2595 | -0.15106 | 0.091553 | 121.6095 | 3.5156 | 0.32501 | 0.54932 | 122.374 | -0.20599 | -0.11902 | 0.041198 | 0.032043 | 0.1236 | -0.60883 | -0.17395 | 0.15564 | 0.15106 | 0.35706 | 0.58136 | 121.6415 | 122.2916 | 0.032043 | 122.406 | 3.5477 | -0.17395 | 122.2916 | 0.032043 | 3.5477 | 121.6415 | 122.406 | -122.3694 | -122.4243
3286.3906 | 122.438 | -0.036621 | 122.2137 | 0.10719 | 0.010696 | -0.0082779 | 0.017244 | 0.045628 | -0.011604 | 0.065193 | -0.041199 | 122.287 | -0.18768 | 0.059509 | 121.5454 | 3.4378 | 0.21973 | 0.35706 | 122.4243 | -0.23346 | -0.15106 | 0.073242 | -0.004578 | 0.09613 | -0.66833 | -0.19684 | 0.21057 | 0.14648 | 0.25635 | 0.39368 | 121.582 | 122.3236 | -0.004578 | 122.4609 | 3.4744 | -0.19684 | 122.3236 | -0.004578 | 3.4744 | 121.582 | 122.4609 | -122.4014 | -122.4472
3288.0781 | 122.3648 | -0.09613 | 122.2778 | -0.19798 | 0.011764 | -0.012764 | 0.013398 | 0.047978 | -0.012245 | 0.067116 | -0.054932 | 122.3282 | -0.20599 | 0.059509 | 121.5454 | 3.5889 | 0.64087 | 0.6546 | 122.4152 | -0.22888 | -0.10986 | 0.050354 | 0.041198 | 0.15564 | -0.73242 | -0.13275 | 0.13733 | 0.15106 | 0.737 | 0.75073 | 121.6415 | 122.4243 | 0.041198 | 122.5113 | 3.685 | -0.13275 | 122.4243 | 0.041198 | 3.685 | 121.6415 | 122.5113 | -122.4838 | -122.5067
3289.8438 | 122.4426 | -0.054932 | 122.2321 | 0.18349 | 0.01091 | -0.011482 | 0.013826 | 0.049473 | -0.01374 | 0.06733 | -0.004578 | 122.2733 | -0.16937 | 0.09613 | 121.5958 | 3.4744 | 0.16022 | 0.41657 | 122.3694 | -0.21973 | -0.11444 | 0.041198 | 0.050354 | 0.15106 | -0.63629 | -0.16479 | 0.13733 | 0.16479 | 0.21515 | 0.4715 | 121.6507 | 122.3282 | 0.050354 | 122.4243 | 3.5294 | -0.16479 | 122.3282 | 0.050354 | 3.5294 | 121.6507 | 122.4243 | -122.4014 | -122.4518
3291.6094 | 122.3602 | -0.07782 | 122.2824 | -0.14458 | 0.0098416 | -0.013191 | 0.0069898 | 0.049046 | -0.009895 | 0.065407 | 0.050354 | 122.2595 | -0.15106 | 0.16479 | 121.6827 | 3.6713 | 0.41657 | 0.75989 | 122.3785 | -0.18768 | -0.073242 | -0.022889 | 0.12817 | 0.24261 | -0.59967 | -0.10986 | 0.09613 | 0.20142 | 0.49439 | 0.83771 | 121.7606 | 122.3373 | 0.12817 | 122.4564 | 3.7491 | -0.10986 | 122.3373 | 0.12817 | 3.7491 | 121.7606 | 122.4564 | -122.4335 | -122.4701
3293.375 | 122.3511 | -0.068665 | 122.2549 | -0.045395 | 0.010055 | -0.014259 | 0.016816 | 0.047337 | -0.014595 | 0.066262 | 0.004578 | 122.2687 | -0.17395 | 0.082397 | 121.5591 | 3.5339 | 0.37994 | 0.49439 | 122.438 | -0.21515 | -0.10528 | 0.013733 | 0.073243 | 0.15106 | -0.6958 | -0.14648 | 0.18311 | 0.17853 | 0.44861 | 0.56305 | 121.6278 | 122.3373 | 0.073243 | 122.5067 | 3.6026 | -0.14648 | 122.3373 | 0.073243 | 3.6026 | 121.6278 | 122.5067 | -122.4289 | -122.4701
3295.0781 | 122.4426 | -0.032043 | 122.2412 | 0.10719 | 0.011764 | -0.011482 | 0.014894 | 0.051182 | -0.014381 | 0.067543 | -0.041199 | 122.2961 | -0.17395 | 0.059509 | 121.5683 | 3.447 | 0.2243 | 0.36163 | 122.4243 | -0.21057 | -0.14191 | 0.054932 | -0.009156 | 0.091552 | -0.67291 | -0.17853 | 0.1831 | 0.13275 | 0.25635 | 0.39368 | 121.6003 | 122.3282 | -0.009156 | 122.4564 | 3.479 | -0.17853 | 122.3282 | -0.009156 | 3.479 | 121.6003 | 122.4564 | -122.4152 | -122.4518
3296.8594 | 122.3236 | -0.10529 | 122.2504 | -0.10643 | 0.011764 | -0.011269 | 0.013185 | 0.049259 | -0.014167 | 0.066689 | -0.004578 | 122.2824 | -0.18768 | 0.10986 | 121.5912 | 3.598 | 0.46234 | 0.6134 | 122.4518 | -0.22888 | -0.082397 | 0.032044 | 0.10071 | 0.21515 | -0.65918 | -0.1236 | 0.20142 | 0.1831 | 0.56763 | 0.71869 | 121.6965 | 122.3877 | 0.10071 | 122.5571 | 3.7033 | -0.1236 | 122.3877 | 0.10071 | 3.7033 | 121.6965 | 122.5571 | -122.438 | -122.4792
3298.5625 | 122.4518 | -0.050354 | 122.2183 | 0.01564 | 0.0092008 | -0.012337 | 0.0076306 | 0.04755 | -0.010322 | 0.06797 | -0.009155 | 122.287 | -0.15564 | 0.086975 | 121.6049 | 3.5339 | 0.38452 | 0.58594 | 122.3969 | -0.2243 | -0.10529 | 0.068664 | 0.041199 | 0.13733 | -0.6134 | -0.17395 | 0.17853 | 0.14649 | 0.43488 | 0.63629 | 121.6553 | 122.3373 | 0.041199 | 122.4472 | 3.5843 | -0.17395 | 122.3373 | 0.041199 | 3.5843 | 121.6553 | 122.4472 | -122.374 | -122.4426
3300.3281 | 122.4197 | -0.064087 | 122.2366 | 0.053787 | 0.011764 | -0.0089189 | 0.015962 | 0.0499 | -0.014167 | 0.066689 | -0.036621 | 122.287 | -0.18768 | 0.032043 | 121.5271 | 3.4653 | 0.37079 | 0.40283 | 122.4655 | -0.21973 | -0.1236 | 0.050354 | 0.027466 | 0.09613 | -0.70953 | -0.15564 | 0.22888 | 0.15106 | 0.43488 | 0.46692 | 121.5912 | 122.3511 | 0.027466 | 122.5296 | 3.5294 | -0.15564 | 122.3511 | 0.027466 | 3.5294 | 121.5912 | 122.5296 | -122.4243 | -122.4564
3302.1094 | 122.4014 | -0.07782 | 122.2504 | 0.17586 | 0.0087734 | -0.0087051 | 0.014253 | 0.050755 | -0.012886 | 0.065834 | 0.004578 | 122.2961 | -0.17395 | 0.11444 | 121.6141 | 3.5019 | 0.16937 | 0.44403 | 122.4014 | -0.20599 | -0.09613 | 0.045777 | 0.082398 | 0.19226 | -0.63629 | -0.12817 | 0.15106 | 0.17853 | 0.24719 | 0.52185 | 121.6919 | 122.374 | 0.082398 | 122.4792 | 3.5797 | -0.12817 | 122.374 | 0.082398 | 3.5797 | 121.6919 | 122.4792 | -122.4243 | -122.4564
3303.8125 | 122.3785 | -0.091553 | 122.287 | -0.21324 | 0.009628 | -0.016182 | 0.0099804 | 0.046055 | -0.01139 | 0.06498 | -0.032043 | 122.3007 | -0.16937 | 0.054932 | 121.5591 | 3.598 | 0.6546 | 0.70038 | 122.4197 | -0.2243 | -0.07782 | 0.013733 | 0.05951 | 0.14649 | -0.72784 | -0.13275 | 0.13275 | 0.13733 | 0.74616 | 0.79193 | 121.6507 | 122.3923 | 0.05951 | 122.5113 | 3.6896 | -0.13275 | 122.3923 | 0.05951 | 3.6896 | 121.6507 | 122.5113 | -122.4564 | -122.5113
3305.5625 | 122.4655 | -0.050354 | 122.2321 | 0.00038159 | 0.0092008 | -0.010841 | 0.0069898 | 0.04755 | -0.010536 | 0.06498 | -0.013733 | 122.2733 | -0.16022 | 0.09613 | 121.6232 | 3.5431 | 0.37537 | 0.59509 | 122.3694 | -0.20599 | -0.10986 | 0.041198 | 0.036621 | 0.14648 | -0.60883 | -0.15564 | 0.13733 | 0.14648 | 0.42572 | 0.64545 | 121.6736 | 122.3236 | 0.036621 | 122.4197 | 3.5934 | -0.15564 | 122.3236 | 0.036621 | 3.5934 | 121.6736 | 122.4197 | -122.3923 | -122.4381
3307.3125 | 122.3877 | -0.073242 | 122.2504 | 0.11482 | 0.007919 | -0.011696 | 0.017671 | 0.049473 | -0.015236 | 0.06797 | -0.036621 | 122.2778 | -0.19684 | 0.045776 | 121.5225 | 3.4882 | 0.37537 | 0.42114 | 122.4564 | -0.2243 | -0.1236 | 0.027466 | 0.036621 | 0.11902 | -0.72784 | -0.15106 | 0.20599 | 0.16022 | 0.44861 | 0.49438 | 121.5958 | 122.3511 | 0.036621 | 122.5296 | 3.5614 | -0.15106 | 122.3511 | 0.036621 | 3.5614 | 121.5958 | 122.5296 | -122.4472 | -122.4747
3309.0781 | 122.3419 | -0.09613 | 122.2687 | -0.22087 | 0.0089872 | -0.012123 | 0.0099804 | 0.045841 | -0.012458 | 0.064553 | 0.050354 | 122.2916 | -0.15564 | 0.16479 | 121.6736 | 3.6942 | 0.50354 | 0.8194 | 122.3694 | -0.20142 | -0.05951 | 0.022888 | 0.14648 | 0.26092 | -0.59509 | -0.10529 | 0.10071 | 0.20599 | 0.59967 | 0.91553 | 121.7697 | 122.3877 | 0.14648 | 122.4655 | 3.7903 | -0.10529 | 122.3877 | 0.14648 | 3.7903 | 121.7697 | 122.4655 | -122.4243 | -122.4701
3310.7812 | 122.406 | -0.059509 | 122.2458 | 0.16823 | 0.0098416 | -0.0082779 | 0.010835 | 0.048619 | -0.01139 | 0.065193 | 0.068665 | 122.2641 | -0.13275 | 0.16022 | 121.6507 | 3.5431 | 0.13275 | 0.50354 | 122.3877 | -0.20142 | -0.073242 | 0.01831 | 0.12817 | 0.21973 | -0.59509 | -0.14191 | 0.14191 | 0.20142 | 0.19226 | 0.56305 | 121.7102 | 122.3236 | 0.12817 | 122.4472 | 3.6026 | -0.14191 | 122.3236 | 0.12817 | 3.6026 | 121.7102 | 122.4472 | -122.3785 | -122.4472
3312.5312 | 122.4243 | -0.059509 | 122.2458 | 0.14534 | 0.009628 | -0.011482 | 0.016389 | 0.04755 | -0.014381 | 0.066262 | 0.041199 | 122.2641 | -0.16479 | 0.13275 | 121.6415 | 3.5248 | 0.14648 | 0.45776 | 122.4014 | -0.1831 | -0.10529 | 0.01831 | 0.10071 | 0.19226 | -0.60425 | -0.1236 | 0.15564 | 0.20599 | 0.20599 | 0.51727 | 121.7011 | 122.3236 | 0.10071 | 122.4609 | 3.5843 | -0.1236 | 122.3236 | 0.10071 | 3.5843 | 121.7011 | 122.4609 | -122.4106 | -122.4289
3314.2812 | 122.406 | -0.064087 | 122.2412 | 0.14534 | 0.0085598 | -0.012764 | 0.012971 | 0.050114 | -0.013313 | 0.06498 | 0.022888 | 122.2595 | -0.15564 | 0.13275 | 121.6324 | 3.5294 | 0.15106 | 0.46234 | 122.4014 | -0.18768 | -0.091553 | 0.01831 | 0.086975 | 0.19684 | -0.60883 | -0.1236 | 0.16022 | 0.17853 | 0.21515 | 0.52643 | 121.6965 | 122.3236 | 0.086975 | 122.4655 | 3.5934 | -0.1236 | 122.3236 | 0.086975 | 3.5934 | 121.6965 | 122.4655 | -122.3969 | -122.4289
3316.0312 | 122.4518 | -0.041199 | 122.2595 | 0.10719 | 0.0085598 | -0.012764 | 0.015962 | 0.051396 | -0.014595 | 0.065834 | -0.068665 | 122.3007 | -0.19226 | 0.036621 | 121.5179 | 3.4653 | 0.32501 | 0.36621 | 122.4564 | -0.22888 | -0.15106 | 0.041199 | -0.027466 | 0.07782 | -0.74158 | -0.18768 | 0.19684 | 0.1236 | 0.36621 | 0.40741 | 121.5591 | 122.3419 | -0.027466 | 122.4976 | 3.5065 | -0.18768 | 122.3419 | -0.027466 | 3.5065 | 121.5591 | 122.4976 | -122.4518 | -122.4884
3317.7812 | 122.4243 | -0.082397 | 122.2229 | 0.099564 | 0.011123 | -0.010414 | 0.009126 | 0.04691 | -0.011177 | 0.066262 | 0.059509 | 122.2733 | -0.14191 | 0.13275 | 121.6507 | 3.5568 | 0.17395 | 0.52185 | 122.3557 | -0.1831 | -0.05951 | 0.050354 | 0.14191 | 0.21515 | -0.5722 | -0.10071 | 0.13275 | 0.20142 | 0.25635 | 0.60425 | 121.7331 | 122.3557 | 0.14191 | 122.438 | 3.6392 | -0.10071 | 122.3557 | 0.14191 | 3.6392 | 121.7331 | 122.438 | -122.3648 | -122.406
3319.4844 | 122.4152 | -0.082397 | 122.2137 | 0.18349 | 0.0068508 | -0.0074235 | 0.013826 | 0.049473 | -0.014381 | 0.064553 | 0.004578 | 122.2824 | -0.15106 | 0.10529 | 121.6003 | 3.5202 | 0.16479 | 0.44403 | 122.4014 | -0.19226 | -0.068665 | 0.068665 | 0.086975 | 0.18768 | -0.6134 | -0.10986 | 0.18768 | 0.15564 | 0.24719 | 0.52643 | 121.6827 | 122.3648 | 0.086975 | 122.4838 | 3.6026 | -0.10986 | 122.3648 | 0.086975 | 3.6026 | 121.6827 | 122.4838 | -122.3648 | -122.406
3321.2344 | 122.406 | -0.064087 | 122.2092 | 0.15297 | 0.0085598 | -0.012337 | 0.012117 | 0.049046 | -0.011818 | 0.066902 | 0.073242 | 122.2321 | -0.13733 | 0.14191 | 121.6461 | 3.5522 | 0.10529 | 0.48523 | 122.3923 | -0.19684 | -0.073242 | 0.022889 | 0.13733 | 0.20599 | -0.56305 | -0.13275 | 0.18311 | 0.21057 | 0.16937 | 0.54932 | 121.7102 | 122.2961 | 0.13733 | 122.4564 | 3.6163 | -0.13275 | 122.2961 | 0.13733 | 3.6163 | 121.7102 | 122.4564 | -122.3465 | -122.406
3322.9219 | 122.3923 | -0.082397 | 122.2366 | -0.15984 | 0.0053556 | -0.0063553 | 0.013185 | 0.048619 | -0.01075 | 0.067116 | -0.027466 | 122.2916 | -0.16937 | 0.045776 | 121.5775 | 3.6255 | 0.66834 | 0.70038 | 122.4106 | -0.24719 | -0.086976 | 0.054932 | 0.054931 | 0.12817 | -0.65918 | -0.16479 | 0.17395 | 0.14191 | 0.75073 | 0.78277 | 121.6599 | 122.374 | 0.054931 | 122.493 | 3.7079 | -0.16479 | 122.374 | 0.054931 | 3.7079 | 121.6599 | 122.493 | -122.406 | -122.4838
3324.6875 | 122.3419 | -0.091553 | 122.2778 | -0.21324 | 0.01091 | -0.012978 | 0.0089124 | 0.04755 | -0.011818 | 0.066262 | 0.059509 | 122.2641 | -0.13733 | 0.15106 | 121.6736 | 3.7216 | 0.5127 | 0.82398 | 122.3923 | -0.19684 | -0.045776 | -0.013733 | 0.15106 | 0.24261 | -0.60425 | -0.10529 | 0.11444 | 0.19684 | 0.60425 | 0.91553 | 121.7651 | 122.3557 | 0.15106 | 122.4838 | 3.8132 | -0.10529 | 122.3557 | 0.15106 | 3.8132 | 121.7651 | 122.4838 | -122.4152 | -122.4747
3326.4375 | 122.3282 | -0.10529 | 122.2778 | -0.19035 | 0.0077054 | -0.011482 | 0.0099804 | 0.047337 | -0.01374 | 0.065621 | 0.045776 | 122.2687 | -0.15106 | 0.15564 | 121.6644 | 3.717 | 0.51727 | 0.81482 | 122.3923 | -0.20142 | -0.045776 | -0.009155 | 0.15106 | 0.26093 | -0.6134 | -0.09613 | 0.11444 | 0.19684 | 0.62256 | 0.9201 | 121.7697 | 122.374 | 0.15106 | 122.4976 | 3.8223 | -0.09613 | 122.374 | 0.15106 | 3.8223 | 121.7697 | 122.4976 | -122.4289 | -122.4792
3328.125 | 122.3602 | -0.10529 | 122.2595 | -0.060654 | 0.010055 | -0.011909 | 0.015321 | 0.048832 | -0.014381 | 0.066048 | 0.009155 | 122.2504 | -0.1831 | 0.10071 | 121.5866 | 3.5934 | 0.41199 | 0.52643 | 122.4655 | -0.21057 | -0.077819 | -0.009155 | 0.11444 | 0.20599 | -0.67291 | -0.10529 | 0.20599 | 0.19226 | 0.51727 | 0.63171 | 121.6919 | 122.3557 | 0.11444 | 122.5708 | 3.6987 | -0.10529 | 122.3557 | 0.11444 | 3.6987 | 121.6919 | 122.5708 | -122.4426 | -122.4701
3329.9062 | 122.4472 | -0.054932 | 122.2321 | -0.022507 | 0.01091 | -0.012764 | 0.0078442 | 0.048832 | -0.01139 | 0.065193 | 0.004578 | 122.287 | -0.15564 | 0.10529 | 121.6232 | 3.6026 | 0.39825 | 0.64545 | 122.406 | -0.20142 | -0.10071 | 0.054931 | 0.05951 | 0.16022 | -0.60883 | -0.14648 | 0.17395 | 0.16022 | 0.45319 | 0.70038 | 121.6782 | 122.3419 | 0.05951 | 122.4609 | 3.6575 | -0.14648 | 122.3419 | 0.05951 | 3.6575 | 121.6782 | 122.4609 | -122.3877 | -122.4335
3331.6562 | 122.3465 | -0.10529 | 122.2961 | -0.18272 | 0.0087734 | -0.015541 | 0.010408 | 0.04691 | -0.012672 | 0.064339 | 0.054932 | 122.2366 | -0.15564 | 0.15106 | 121.6553 | 3.717 | 0.54932 | 0.81482 | 122.4106 | -0.20142 | -0.050354 | -0.05951 | 0.16022 | 0.25635 | -0.64087 | -0.09613 | 0.11444 | 0.21057 | 0.6546 | 0.9201 | 121.7606 | 122.3419 | 0.16022 | 122.5159 | 3.8223 | -0.09613 | 122.3419 | 0.16022 | 3.8223 | 121.7606 | 122.5159 | -122.4518 | -122.4976
3333.4062 | 122.4564 | -0.054932 | 122.2183 | 0.076676 | 0.011337 | -0.0074235 | 0.010194 | 0.047764 | -0.012245 | 0.065407 | 0.032043 | 122.2778 | -0.14648 | 0.11444 | 121.6278 | 3.5477 | 0.27008 | 0.52643 | 122.4335 | -0.20142 | -0.091552 | 0.059509 | 0.086975 | 0.16937 | -0.59051 | -0.14648 | 0.21515 | 0.17853 | 0.32501 | 0.58136 | 121.6827 | 122.3328 | 0.086975 | 122.4884 | 3.6026 | -0.14648 | 122.3328 | 0.086975 | 3.6026 | 121.6827 | 122.4884 | -122.3648 | -122.4197
3335.1719 | 122.4609 | -0.054932 | 122.2275 | -0.022507 | 0.0083462 | -0.0099869 | 0.012117 | 0.04755 | -0.011818 | 0.065834 | -0.009155 | 122.2916 | -0.16937 | 0.10986 | 121.637 | 3.6026 | 0.39368 | 0.61798 | 122.4197 | -0.20142 | -0.11444 | 0.064087 | 0.045777 | 0.16479 | -0.59052 | -0.14648 | 0.19226 | 0.16022 | 0.44861 | 0.67291 | 121.6919 | 122.3465 | 0.045777 | 122.4747 | 3.6575 | -0.14648 | 122.3465 | 0.045777 | 3.6575 | 121.6919 | 122.4747 | -122.3969 | -122.4289
3336.875 | 122.4426 | -0.045776 | 122.2183 | 0.10719 | 0.010269 | -0.0084915 | 0.018312 | 0.046696 | -0.014381 | 0.06733 | -0.013733 | 122.3053 | -0.19226 | 0.054932 | 121.5683 | 3.4882 | 0.23804 | 0.37079 | 122.4426 | -0.21515 | -0.14648 | 0.086975 | 0.032043 | 0.10071 | -0.65002 | -0.16937 | 0.2243 | 0.17853 | 0.28381 | 0.41656 | 121.6141 | 122.3511 | 0.032043 | 122.4884 | 3.5339 | -0.16937 | 122.3511 | 0.032043 | 3.5339 | 121.6141 | 122.4884 | -122.4106 | -122.4335
3338.6406 | 122.4243 | -0.059509 | 122.2595 | 0.18349 | 0.0098416 | -0.013405 | 0.013185 | 0.047764 | -0.012245 | 0.066475 | 0.07782 | 122.2549 | -0.13275 | 0.17853 | 121.669 | 3.5797 | 0.1236 | 0.49439 | 122.3785 | -0.17853 | -0.073242 | -0.004577 | 0.13733 | 0.23804 | -0.59052 | -0.11902 | 0.11902 | 0.21057 | 0.1831 | 0.55389 | 121.7285 | 122.3145 | 0.13733 | 122.438 | 3.6392 | -0.11902 | 122.3145 | 0.13733 | 3.6392 | 121.7285 | 122.438 | -122.3923 | -122.438
3340.4062 | 122.438 | -0.059509 | 122.2321 | 0.10719 | 0.007919 | -0.0099869 | 0.013185 | 0.049473 | -0.012458 | 0.066262 | 0.059509 | 122.2641 | -0.15564 | 0.14191 | 121.6187 | 3.5889 | 0.18768 | 0.52185 | 122.3877 | -0.19684 | -0.096131 | 0.032043 | 0.11902 | 0.20142 | -0.6134 | -0.13733 | 0.15564 | 0.21515 | 0.24719 | 0.58136 | 121.6782 | 122.3236 | 0.11902 | 122.4472 | 3.6484 | -0.13733 | 122.3236 | 0.11902 | 3.6484 | 121.6782 | 122.4472 | -122.3877 | -122.4289
3342.1875 | 122.4426 | -0.041199 | 122.2183 | 0.11482 | 0.013687 | -0.010628 | 0.013612 | 0.048619 | -0.012245 | 0.067116 | -0.032043 | 122.2595 | -0.18768 | 0.068665 | 121.5637 | 3.5019 | 0.23804 | 0.35706 | 122.4014 | -0.21515 | -0.14648 | 0.041198 | 0.009156 | 0.10986 | -0.6546 | -0.17395 | 0.1831 | 0.15564 | 0.27924 | 0.39825 | 121.6049 | 122.3007 | 0.009156 | 122.4426 | 3.5431 | -0.17395 | 122.3007 | 0.009156 | 3.5431 | 121.6049 | 122.4426 | -122.406 | -122.4335
3343.9531 | 122.4792 | -0.050354 | 122.2183 | 0.0080111 | 0.010055 | -0.0102 | 0.0086988 | 0.047123 | -0.012672 | 0.066048 | 0.009155 | 122.2733 | -0.15564 | 0.091553 | 121.6187 | 3.5751 | 0.36621 | 0.5722 | 122.4152 | -0.21515 | -0.10529 | 0.054931 | 0.059509 | 0.14191 | -0.59967 | -0.16479 | 0.19684 | 0.16479 | 0.41657 | 0.62256 | 121.669 | 122.3236 | 0.059509 | 122.4655 | 3.6255 | -0.16479 | 122.3236 | 0.059509 | 3.6255 | 121.669 | 122.4655 | -122.374 | -122.4335
3345.6406 | 122.4472 | -0.054932 | 122.2366 | -0.037765 | 0.0087734 | -0.014046 | 0.0089124 | 0.045841 | -0.013313 | 0.065834 | -0.009155 | 122.2641 | -0.15106 | 0.11902 | 121.6461 | 3.6438 | 0.39825 | 0.66834 | 122.3785 | -0.20599 | -0.09613 | 0.027466 | 0.045777 | 0.17395 | -0.59051 | -0.15106 | 0.14191 | 0.14191 | 0.45319 | 0.72327 | 121.701 | 122.319 | 0.045777 | 122.4335 | 3.6987 | -0.15106 | 122.319 | 0.045777 | 3.6987 | 121.701 | 122.4335 | -122.3877 | -122.4426
3347.3281 | 122.4701 | -0.054932 | 122.2183 | -0.0072479 | 0.0094144 | -0.014687 | 0.010194 | 0.046055 | -0.01139 | 0.066262 | -0.022888 | 122.2824 | -0.15106 | 0.10529 | 121.6141 | 3.6072 | 0.38452 | 0.62256 | 122.3694 | -0.2243 | -0.09613 | 0.064087 | 0.032044 | 0.16022 | -0.60425 | -0.16937 | 0.15106 | 0.12817 | 0.43945 | 0.67749 | 121.669 | 122.3373 | 0.032044 | 122.4243 | 3.6621 | -0.16937 | 122.3373 | 0.032044 | 3.6621 | 121.669 | 122.4243 | -122.3694 | -122.4426
3349.0938 | 122.3602 | -0.086975 | 122.2504 | -0.0072479 | 0.0098416 | -0.013832 | 0.017884 | 0.048191 | -0.014808 | 0.068611 | -0.013733 | 122.2641 | -0.20599 | 0.07782 | 121.4905 | 3.5797 | 0.3891 | 0.45319 | 122.4152 | -0.23804 | -0.11902 | 0.013733 | 0.073242 | 0.16479 | -0.75989 | -0.15106 | 0.16479 | 0.19226 | 0.47607 | 0.54016 | 121.5775 | 122.3511 | 0.073242 | 122.5021 | 3.6667 | -0.15106 | 122.3511 | 0.073242 | 3.6667 | 121.5775 | 122.5021 | -122.4564 | -122.4884
3350.7812 | 122.4152 | -0.068665 | 122.2321 | 0.12245 | 0.0085598 | -0.012337 | 0.012758 | 0.048191 | -0.011177 | 0.067116 | 0.045776 | 122.2321 | -0.14648 | 0.15106 | 121.6599 | 3.6026 | 0.14648 | 0.51727 | 122.3785 | -0.17853 | -0.077819 | 0 | 0.11444 | 0.21973 | -0.5722 | -0.10986 | 0.14648 | 0.19226 | 0.21515 | 0.58594 | 121.7285 | 122.3007 | 0.11444 | 122.4472 | 3.6713 | -0.10986 | 122.3007 | 0.11444 | 3.6713 | 121.7285 | 122.4472 | -122.3785 | -122.4106
3352.5469 | 122.3877 | -0.082397 | 122.2549 | -0.23613 | 0.012405 | -0.011909 | 0.014253 | 0.047337 | -0.011604 | 0.065407 | -0.064087 | 122.319 | -0.19684 | 0.059509 | 121.5683 | 3.6758 | 0.67291 | 0.67291 | 122.4289 | -0.24261 | -0.11444 | 0.064087 | 0.01831 | 0.14191 | -0.68665 | -0.16022 | 0.17395 | 0.13275 | 0.75531 | 0.75531 | 121.6507 | 122.4014 | 0.01831 | 122.5113 | 3.7582 | -0.16022 | 122.4014 | 0.01831 | 3.7582 | 121.6507 | 122.5113 | -122.4518 | -122.4976
3354.3125 | 122.438 | -0.064087 | 122.2275 | -0.022507 | 0.009628 | -0.012764 | 0.0086988 | 0.046055 | -0.011818 | 0.065621 | 0.004578 | 122.2504 | -0.13733 | 0.10529 | 121.6278 | 3.6575 | 0.39368 | 0.65002 | 122.3969 | -0.21057 | -0.073242 | 0.022888 | 0.068665 | 0.16937 | -0.59967 | -0.14648 | 0.16937 | 0.14191 | 0.45776 | 0.71411 | 121.6919 | 122.3145 | 0.068665 | 122.4609 | 3.7216 | -0.14648 | 122.3145 | 0.068665 | 3.7216 | 121.6919 | 122.4609 | -122.3648 | -122.438
3356.0781 | 122.3831 | -0.082397 | 122.2549 | -0.24376 | 0.011337 | -0.016823 | 0.014467 | 0.046055 | -0.012672 | 0.066475 | -0.050354 | 122.3099 | -0.20142 | 0.045776 | 121.5408 | 3.6758 | 0.68665 | 0.67291 | 122.4564 | -0.23804 | -0.11902 | 0.054931 | 0.032043 | 0.12817 | -0.71411 | -0.15564 | 0.20142 | 0.15106 | 0.76904 | 0.75531 | 121.6232 | 122.3923 | 0.032043 | 122.5388 | 3.7582 | -0.15564 | 122.3923 | 0.032043 | 3.7582 | 121.6232 | 122.5388 | -122.4564 | -122.493
3357.7656 | 122.4243 | -0.050354 | 122.2504 | 0.17586 | 0.0089872 | -0.012337 | 0.015321 | 0.049473 | -0.012458 | 0.067543 | -0.013733 | 122.2733 | -0.17853 | 0.09613 | 121.6003 | 3.5797 | 0.18768 | 0.40741 | 122.4106 | -0.18768 | -0.12817 | 0.022888 | 0.036621 | 0.14648 | -0.65002 | -0.13733 | 0.16022 | 0.16479 | 0.23804 | 0.45776 | 121.6507 | 122.3236 | 0.036621 | 122.4609 | 3.6301 | -0.13733 | 122.3236 | 0.036621 | 3.6301 | 121.6507 | 122.4609 | -122.4289 | -122.438
3359.5312 | 122.406 | -0.059509 | 122.2046 | 0.18349 | 0.010696 | -0.0102 | 0.014039 | 0.0499 | -0.012245 | 0.066475 | 0.064087 | 122.2824 | -0.13275 | 0.14648 | 121.6599 | 3.6209 | 0.11902 | 0.50812 | 122.3969 | -0.19226 | -0.073242 | 0.07782 | 0.1236 | 0.20599 | -0.54474 | -0.13275 | 0.19226 | 0.19684 | 0.17853 | 0.56763 | 121.7194 | 122.3419 | 0.1236 | 122.4564 | 3.6804 | -0.13275 | 122.3419 | 0.1236 | 3.6804 | 121.7194 | 122.4564 | -122.3373 | -122.3969
3361.2969 | 122.4701 | -0.045776 | 122.2366 | 0.13008 | 0.010482 | -0.013618 | 0.013398 | 0.048405 | -0.012672 | 0.06733 | -0.032043 | 122.2733 | -0.19684 | 0.032043 | 121.55 | 3.5202 | 0.28839 | 0.35706 | 122.4289 | -0.23346 | -0.15106 | 0.036621 | 0.013733 | 0.077819 | -0.68664 | -0.18768 | 0.19226 | 0.1648 | 0.33417 | 0.40283 | 121.5958 | 122.319 | 0.013733 | 122.4747 | 3.566 | -0.18768 | 122.319 | 0.013733 | 3.566 | 121.5958 | 122.4747 | -122.4335 | -122.4701
3362.9844 | 122.4106 | -0.082397 | 122.2504 | 0.12245 | 0.0077054 | -0.011909 | 0.011476 | 0.048405 | -0.013527 | 0.067543 | 0.059509 | 122.2549 | -0.15106 | 0.14191 | 121.6599 | 3.6392 | 0.13275 | 0.47607 | 122.3694 | -0.19684 | -0.068665 | 0.004578 | 0.14191 | 0.2243 | -0.59051 | -0.11444 | 0.11902 | 0.21057 | 0.21515 | 0.55847 | 121.7422 | 122.3373 | 0.14191 | 122.4518 | 3.7216 | -0.11444 | 122.3373 | 0.14191 | 3.7216 | 121.7422 | 122.4518 | -122.4014 | -122.4472
3364.75 | 122.319 | -0.10529 | 122.2504 | -0.075912 | 0.0092008 | -0.013405 | 0.017244 | 0.049473 | -0.011604 | 0.066262 | 0.004578 | 122.2961 | -0.18768 | 0.10986 | 121.5958 | 3.7033 | 0.45776 | 0.61798 | 122.4243 | -0.23804 | -0.082397 | 0.045777 | 0.10986 | 0.21515 | -0.6546 | -0.13275 | 0.17395 | 0.19226 | 0.56305 | 0.72327 | 121.7011 | 122.4014 | 0.10986 | 122.5296 | 3.8086 | -0.13275 | 122.4014 | 0.10986 | 3.8086 | 121.7011 | 122.5296 | -122.438 | -122.4884
3366.5 | 122.3465 | -0.10071 | 122.2778 | -0.037765 | 0.0087734 | -0.0084915 | 0.013185 | 0.048405 | -0.011604 | 0.066048 | 0 | 122.3053 | -0.18768 | 0.07782 | 121.5683 | 3.653 | 0.41657 | 0.50812 | 122.4289 | -0.22888 | -0.086975 | 0.027466 | 0.10071 | 0.17853 | -0.70953 | -0.12817 | 0.15106 | 0.18768 | 0.51727 | 0.60883 | 121.669 | 122.406 | 0.10071 | 122.5296 | 3.7537 | -0.12817 | 122.406 | 0.10071 | 3.7537 | 121.669 | 122.5296 | -122.4655 | -122.5067
3368.2656 | 122.4014 | -0.073242 | 122.2366 | -0.0072479 | 0.0077054 | -0.015327 | 0.014039 | 0.0499 | -0.013527 | 0.065834 | -0.036621 | 122.3007 | -0.19226 | 0.045776 | 121.5363 | 3.6026 | 0.37994 | 0.4303 | 122.4152 | -0.21973 | -0.11902 | 0.064087 | 0.036621 | 0.11902 | -0.70038 | -0.14649 | 0.17853 | 0.15564 | 0.45319 | 0.50354 | 121.6095 | 122.374 | 0.036621 | 122.4884 | 3.6758 | -0.14649 | 122.374 | 0.036621 | 3.6758 | 121.6095 | 122.4884 | -122.4289 | -122.4564
3369.9688 | 122.4747 | -0.059509 | 122.2549 | -0.0072479 | 0.010269 | -0.0069961 | 0.0054944 | 0.046482 | -0.010536 | 0.066262 | -0.027466 | 122.2916 | -0.16022 | 0.082397 | 121.637 | 3.6667 | 0.41657 | 0.64087 | 122.3969 | -0.20599 | -0.10071 | 0.036621 | 0.032043 | 0.14191 | -0.61798 | -0.14649 | 0.14191 | 0.13275 | 0.47607 | 0.70038 | 121.6965 | 122.3511 | 0.032043 | 122.4564 | 3.7262 | -0.14649 | 122.3511 | 0.032043 | 3.7262 | 121.6965 | 122.4564 | -122.4152 | -122.4609
3371.7344 | 122.3877 | -0.082397 | 122.2687 | -0.23613 | 0.011551 | -0.011696 | 0.011476 | 0.047337 | -0.011818 | 0.064553 | -0.064087 | 122.3236 | -0.21057 | 0.041199 | 121.55 | 3.717 | 0.68665 | 0.66376 | 122.406 | -0.25177 | -0.12817 | 0.054931 | 0.01831 | 0.1236 | -0.71869 | -0.16937 | 0.13733 | 0.14648 | 0.76904 | 0.74615 | 121.6324 | 122.406 | 0.01831 | 122.4884 | 3.7994 | -0.16937 | 122.406 | 0.01831 | 3.7994 | 121.6324 | 122.4884 | -122.4792 | -122.5204
3373.4844 | 122.4564 | -0.059509 | 122.2321 | 0.091934 | 0.0087734 | -0.013191 | 0.0097668 | 0.04755 | -0.0096814 | 0.066689 | 0.022888 | 122.2961 | -0.13733 | 0.09613 | 121.637 | 3.6301 | 0.27466 | 0.53558 | 122.3923 | -0.20142 | -0.07782 | 0.064087 | 0.082397 | 0.15564 | -0.59509 | -0.14191 | 0.16022 | 0.16022 | 0.33417 | 0.59509 | 121.6965 | 122.3557 | 0.082397 | 122.4518 | 3.6896 | -0.14191 | 122.3557 | 0.082397 | 3.6896 | 121.6965 | 122.4518 | -122.3694 | -122.4335
3375.2656 | 122.406 | -0.054932 | 122.2412 | 0.13771 | 0.01091 | -0.014473 | 0.013826 | 0.050114 | -0.01374 | 0.066475 | 0.054932 | 122.2641 | -0.15564 | 0.15564 | 121.6553 | 3.653 | 0.1236 | 0.50812 | 122.3785 | -0.19226 | -0.10071 | 0.022888 | 0.10986 | 0.21057 | -0.58594 | -0.13733 | 0.13733 | 0.21057 | 0.17853 | 0.56305 | 121.7102 | 122.319 | 0.10986 | 122.4335 | 3.7079 | -0.13733 | 122.319 | 0.10986 | 3.7079 | 121.7102 | 122.4335 | -122.3969 | -122.4335
3376.9688 | 122.374 | -0.07782 | 122.2229 | -0.17509 | 0.0098416 | -0.01255 | 0.016389 | 0.048619 | -0.01075 | 0.065407 | -0.050354 | 122.2961 | -0.19684 | 0.050354 | 121.5683 | 3.7125 | 0.63629 | 0.67291 | 122.4243 | -0.23804 | -0.11902 | 0.073243 | 0.027466 | 0.12817 | -0.6546 | -0.16022 | 0.20142 | 0.14648 | 0.71411 | 0.75073 | 121.6461 | 122.374 | 0.027466 | 122.5021 | 3.7903 | -0.16022 | 122.374 | 0.027466 | 3.7903 | 121.6461 | 122.5021 | -122.4197 | -122.4609
3378.7188 | 122.406 | -0.082397 | 122.2412 | -0.23613 | 0.0081326 | -0.015114 | 0.0080578 | 0.047337 | -0.010536 | 0.067116 | 0.032043 | 122.3099 | -0.14191 | 0.15106 | 121.6919 | 3.7674 | 0.43488 | 0.75989 | 122.3877 | -0.19684 | -0.05951 | 0.068664 | 0.11444 | 0.23346 | -0.54932 | -0.11444 | 0.14648 | 0.17395 | 0.51727 | 0.84228 | 121.7743 | 122.3923 | 0.11444 | 122.4701 | 3.8498 | -0.11444 | 122.3923 | 0.11444 | 3.8498 | 121.7743 | 122.4701 | -122.3831 | -122.438
3380.4844 | 122.374 | -0.082397 | 122.2687 | -0.21324 | 0.0081326 | -0.011696 | 0.013398 | 0.045201 | -0.011818 | 0.066048 | -0.045776 | 122.3511 | -0.1831 | 0.059509 | 121.5591 | 3.7262 | 0.65002 | 0.67291 | 122.4518 | -0.24719 | -0.10071 | 0.082397 | 0.036621 | 0.14191 | -0.70953 | -0.16479 | 0.1831 | 0.13733 | 0.73242 | 0.75531 | 121.6415 | 122.4335 | 0.036621 | 122.5342 | 3.8086 | -0.16479 | 122.4335 | 0.036621 | 3.8086 | 121.6415 | 122.5342 | -122.4518 | -122.5159
3382.25 | 122.4106 | -0.082397 | 122.2275 | 0.15297 | 0.0085598 | -0.013618 | 0.012971 | 0.049259 | -0.011604 | 0.067116 | 0.073242 | 122.2733 | -0.15106 | 0.15564 | 121.6553 | 3.685 | 0.13733 | 0.52643 | 122.3969 | -0.1831 | -0.068665 | 0.045776 | 0.15564 | 0.23804 | -0.57221 | -0.10071 | 0.16937 | 0.2243 | 0.21973 | 0.60882 | 121.7377 | 122.3557 | 0.15564 | 122.4792 | 3.7674 | -0.10071 | 122.3557 | 0.15564 | 3.7674 | 121.7377 | 122.4792 | -122.3785 | -122.4106
3384.0156 | 122.3328 | -0.11444 | 122.2733 | -0.091171 | 0.0092008 | -0.012764 | 0.016603 | 0.052037 | -0.014167 | 0.066902 | 0.004578 | 122.2778 | -0.19684 | 0.10986 | 121.5958 | 3.7537 | 0.44861 | 0.59967 | 122.4335 | -0.21515 | -0.082397 | 0.004578 | 0.11902 | 0.2243 | -0.67749 | -0.10071 | 0.16022 | 0.20142 | 0.56305 | 0.71411 | 121.7102 | 122.3923 | 0.11902 | 122.5479 | 3.8681 | -0.10071 | 122.3923 | 0.11902 | 3.8681 | 121.7102 | 122.5479 | -122.4701 | -122.4884
3385.7188 | 122.3602 | -0.09613 | 122.2549 | -0.21324 | 0.010269 | -0.014259 | 0.013398 | 0.049687 | -0.013313 | 0.065834 | -0.032043 | 122.3145 | -0.19684 | 0.07782 | 121.6049 | 3.7674 | 0.55847 | 0.67291 | 122.4335 | -0.22888 | -0.10071 | 0.059509 | 0.064087 | 0.17395 | -0.65002 | -0.13275 | 0.17853 | 0.1648 | 0.6546 | 0.76904 | 121.701 | 122.4106 | 0.064087 | 122.5296 | 3.8635 | -0.13275 | 122.4106 | 0.064087 | 3.8635 | 121.701 | 122.5296 | -122.4518 | -122.4838
3387.4688 | 122.4106 | -0.064087 | 122.2321 | 0.1606 | 0.0083462 | -0.013832 | 0.01233 | 0.049046 | -0.012245 | 0.066475 | 0.041199 | 122.2733 | -0.14648 | 0.14191 | 121.6553 | 3.7033 | 0.13275 | 0.50354 | 122.3785 | -0.1831 | -0.082397 | 0.041198 | 0.10529 | 0.20599 | -0.57678 | -0.11902 | 0.14648 | 0.18768 | 0.19684 | 0.56763 | 121.7194 | 122.3373 | 0.10529 | 122.4426 | 3.7674 | -0.11902 | 122.3373 | 0.10529 | 3.7674 | 121.7194 | 122.4426 | -122.3785 | -122.4152
3389.2344 | 122.4243 | -0.059509 | 122.2458 | 0.20638 | 0.0085598 | -0.014473 | 0.013826 | 0.049046 | -0.012031 | 0.067116 | -0.022888 | 122.2733 | -0.19226 | 0.09613 | 121.5958 | 3.6484 | 0.17395 | 0.4303 | 122.4014 | -0.21515 | -0.13275 | 0.027465 | 0.036621 | 0.15564 | -0.65002 | -0.15564 | 0.15564 | 0.16937 | 0.23346 | 0.48981 | 121.6553 | 122.3328 | 0.036621 | 122.4609 | 3.7079 | -0.15564 | 122.3328 | 0.036621 | 3.7079 | 121.6553 | 122.4609 | -122.4381 | -122.4609
3391 | 122.4243 | -0.054932 | 122.2229 | 0.12245 | 0.010696 | -0.0149 | 0.013826 | 0.049473 | -0.01374 | 0.065834 | 0.054932 | 122.2824 | -0.13275 | 0.13275 | 121.6507 | 3.6987 | 0.13733 | 0.50812 | 122.4243 | -0.19684 | -0.077819 | 0.05951 | 0.10986 | 0.18768 | -0.5722 | -0.14191 | 0.20142 | 0.18768 | 0.19226 | 0.56305 | 121.7056 | 122.3373 | 0.10986 | 122.4792 | 3.7537 | -0.14191 | 122.3373 | 0.10986 | 3.7537 | 121.7056 | 122.4792 | -122.3557 | -122.4197
3392.7031 | 122.4838 | -0.059509 | 122.2229 | 0.030899 | 0.010055 | -0.012978 | 0.0097668 | 0.04755 | -0.012245 | 0.064339 | -0.004578 | 122.2824 | -0.15106 | 0.082397 | 121.6141 | 3.7125 | 0.32959 | 0.56763 | 122.3831 | -0.21515 | -0.091553 | 0.05951 | 0.054931 | 0.14191 | -0.60882 | -0.15564 | 0.16022 | 0.14648 | 0.3891 | 0.62714 | 121.6736 | 122.3419 | 0.054931 | 122.4426 | 3.772 | -0.15564 | 122.3419 | 0.054931 | 3.772 | 121.6736 | 122.4426 | -122.374 | -122.438
3394.4688 | 122.3694 | -0.11444 | 122.2595 | -0.2285 | 0.0085598 | -0.015114 | 0.01233 | 0.046696 | -0.012672 | 0.064766 | 0.027466 | 122.2778 | -0.16022 | 0.13275 | 121.6232 | 3.8406 | 0.62256 | 0.80109 | 122.4152 | -0.21515 | -0.045776 | 0.018311 | 0.14191 | 0.24719 | -0.63629 | -0.10071 | 0.15564 | 0.18768 | 0.737 | 0.91553 | 121.7377 | 122.3923 | 0.14191 | 122.5296 | 3.9551 | -0.10071 | 122.3923 | 0.14191 | 3.9551 | 121.7377 | 122.5296 | -122.4197 | -122.4747
3396.1562 | 122.4106 | -0.082397 | 122.2504 | 0.214 | 0.0089872 | -0.010628 | 0.011049 | 0.048405 | -0.015663 | 0.066475 | 0.050354 | 122.2458 | -0.14648 | 0.13733 | 121.6461 | 3.7079 | 0.14191 | 0.48523 | 122.438 | -0.17853 | -0.064087 | -0.004577 | 0.13275 | 0.21973 | -0.60425 | -0.096131 | 0.18768 | 0.19684 | 0.2243 | 0.56763 | 121.7285 | 122.3282 | 0.13275 | 122.5204 | 3.7903 | -0.096131 | 122.3282 | 0.13275 | 3.7903 | 121.7285 | 122.5204 | -122.3969 | -122.4289
3397.9062 | 122.4197 | -0.064087 | 122.2458 | 0.19112 | 0.0098416 | -0.01255 | 0.012758 | 0.0499 | -0.01139 | 0.066262 | 0.064087 | 122.2458 | -0.15106 | 0.16022 | 121.6599 | 3.7308 | 0.13275 | 0.50812 | 122.3831 | -0.20599 | -0.086975 | 0 | 0.12817 | 0.2243 | -0.58594 | -0.14191 | 0.13733 | 0.21515 | 0.19684 | 0.5722 | 121.7239 | 122.3099 | 0.12817 | 122.4472 | 3.7949 | -0.14191 | 122.3099 | 0.12817 | 3.7949 | 121.7239 | 122.4472 | -122.3969 | -122.4518
3399.6094 | 122.4426 | -0.036621 | 122.2458 | 0.046158 | 0.01091 | -0.010414 | 0.014467 | 0.048832 | -0.01139 | 0.06797 | -0.045776 | 122.3557 | -0.18768 | 0.018311 | 121.5225 | 3.6438 | 0.36621 | 0.39825 | 122.4243 | -0.24719 | -0.15106 | 0.10986 | -0.009155 | 0.054932 | -0.72327 | -0.21057 | 0.17853 | 0.14191 | 0.40283 | 0.43488 | 121.5591 | 122.3923 | -0.009155 | 122.4609 | 3.6804 | -0.21057 | 122.3923 | -0.009155 | 3.6804 | 121.5591 | 122.4609 | -122.4335 | -122.493
3401.3594 | 122.4518 | -0.064087 | 122.2183 | 0.099564 | 0.011337 | -0.0078507 | 0.012117 | 0.049046 | -0.013954 | 0.065834 | -0.045776 | 122.3007 | -0.17395 | 0.050354 | 121.5546 | 3.6438 | 0.25177 | 0.37994 | 122.438 | -0.21057 | -0.10986 | 0.082397 | 0.018311 | 0.11444 | -0.66376 | -0.14648 | 0.21973 | 0.12817 | 0.31586 | 0.44403 | 121.6187 | 122.3648 | 0.018311 | 122.5021 | 3.7079 | -0.14648 | 122.3648 | 0.018311 | 3.7079 | 121.6187 | 122.5021 | -122.3923 | -122.4289
3403.1094 | 122.4655 | -0.050354 | 122.2321 | 0.046158 | 0.0085598 | -0.0097733 | 0.013612 | 0.050114 | -0.013313 | 0.066475 | -0.064087 | 122.2961 | -0.1831 | 0.032043 | 121.5179 | 3.6621 | 0.35248 | 0.37994 | 122.4609 | -0.24719 | -0.13275 | 0.064087 | -0.013733 | 0.082397 | -0.71411 | -0.19684 | 0.22888 | 0.11902 | 0.40283 | 0.4303 | 121.5683 | 122.3465 | -0.013733 | 122.5113 | 3.7125 | -0.19684 | 122.3465 | -0.013733 | 3.7125 | 121.5683 | 122.5113 | -122.4152 | -122.4792
3404.875 | 122.3877 | -0.091553 | 122.2641 | -0.15221 | 0.0085598 | -0.015327 | 0.010194 | 0.048191 | -0.014808 | 0.065834 | -0.045776 | 122.2641 | -0.19226 | 0.054932 | 121.5683 | 3.8315 | 0.68665 | 0.70953 | 122.5067 | -0.23346 | -0.10071 | 0 | 0.045777 | 0.14649 | -0.6958 | -0.14191 | 0.24262 | 0.14648 | 0.7782 | 0.80109 | 121.6599 | 122.3557 | 0.045777 | 122.5983 | 3.923 | -0.14191 | 122.3557 | 0.045777 | 3.923 | 121.6599 | 122.5983 | -122.4564 | -122.4976
3406.6562 | 122.4335 | -0.064087 | 122.2641 | 0.15297 | 0.012191 | -0.0097733 | 0.0093396 | 0.049046 | -0.01139 | 0.064766 | 0.07782 | 122.2733 | -0.12817 | 0.15106 | 121.6553 | 3.7582 | 0.12817 | 0.50354 | 122.406 | -0.17853 | -0.064087 | 0.009155 | 0.14191 | 0.21515 | -0.60883 | -0.11444 | 0.14191 | 0.20599 | 0.19226 | 0.56763 | 121.7194 | 122.3373 | 0.14191 | 122.4701 | 3.8223 | -0.11444 | 122.3373 | 0.14191 | 3.8223 | 121.7194 | 122.4701 | -122.3923 | -122.4426
3408.3438 | 122.3969 | -0.059509 | 122.2549 | 0.17586 | 0.0092008 | -0.0099869 | 0.010835 | 0.050114 | -0.010963 | 0.064553 | 0.064087 | 122.2641 | -0.16937 | 0.16479 | 121.6507 | 3.7674 | 0.14191 | 0.50812 | 122.3785 | -0.17395 | -0.10986 | 0.009155 | 0.1236 | 0.2243 | -0.60425 | -0.11444 | 0.1236 | 0.23346 | 0.20142 | 0.56763 | 121.7102 | 122.3236 | 0.1236 | 122.438 | 3.8269 | -0.11444 | 122.3236 | 0.1236 | 3.8269 | 121.7102 | 122.438 | -122.4243 | -122.4289
3410.1094 | 122.3511 | -0.10071 | 122.2961 | -0.16747 | 0.0064236 | -0.014473 | 0.0089124 | 0.04755 | -0.011818 | 0.066475 | 0.068665 | 122.287 | -0.15106 | 0.15564 | 121.7102 | 3.9276 | 0.48981 | 0.82855 | 122.3648 | -0.21515 | -0.050354 | -0.009156 | 0.16937 | 0.25635 | -0.58594 | -0.11444 | 0.068664 | 0.21973 | 0.59052 | 0.92926 | 121.8109 | 122.3877 | 0.16937 | 122.4655 | 4.0283 | -0.11444 | 122.3877 | 0.16937 | 4.0283 | 121.8109 | 122.4655 | -122.4472 | -122.5113
3411.8125 | 122.3145 | -0.10071 | 122.2641 | -0.098801 | 0.0074918 | -0.014473 | 0.016603 | 0.048191 | -0.012245 | 0.065621 | 0 | 122.2412 | -0.1831 | 0.10986 | 121.5912 | 3.8544 | 0.4715 | 0.6134 | 122.4747 | -0.21057 | -0.082397 | -0.022888 | 0.10071 | 0.21057 | -0.67291 | -0.10986 | 0.21057 | 0.1831 | 0.5722 | 0.71411 | 121.6919 | 122.3419 | 0.10071 | 122.5754 | 3.9551 | -0.10986 | 122.3419 | 0.10071 | 3.9551 | 121.6919 | 122.5754 | -122.4472 | -122.4747
3413.5781 | 122.3373 | -0.10986 | 122.2412 | -0.21324 | 0.007919 | -0.011696 | 0.0093396 | 0.04755 | -0.012672 | 0.066048 | 0.041199 | 122.2687 | -0.14191 | 0.16022 | 121.6827 | 3.9642 | 0.51727 | 0.85144 | 122.3831 | -0.19684 | -0.032044 | 0.027466 | 0.15106 | 0.27008 | -0.55847 | -0.086975 | 0.14191 | 0.18311 | 0.62714 | 0.9613 | 121.7926 | 122.3785 | 0.15106 | 122.493 | 4.0741 | -0.086975 | 122.3785 | 0.15106 | 4.0741 | 121.7926 | 122.493 | -122.3831 | -122.438
3415.3438 | 122.3373 | -0.10071 | 122.2778 | -0.2285 | 0.012405 | -0.014046 | 0.0082714 | 0.046696 | -0.011604 | 0.066048 | 0.054932 | 122.2595 | -0.14648 | 0.17853 | 121.6782 | 3.9642 | 0.52185 | 0.83313 | 122.3831 | -0.19684 | -0.045776 | -0.018311 | 0.15564 | 0.27924 | -0.59967 | -0.09613 | 0.10529 | 0.20142 | 0.62256 | 0.93384 | 121.7789 | 122.3602 | 0.15564 | 122.4838 | 4.0649 | -0.09613 | 122.3602 | 0.15564 | 4.0649 | 121.7789 | 122.4838 | -122.4243 | -122.4747
3417.1094 | 122.374 | -0.091553 | 122.2778 | -0.22087 | 0.0081326 | -0.0093461 | 0.015535 | 0.045414 | -0.014381 | 0.066475 | -0.050354 | 122.2824 | -0.20599 | 0.041199 | 121.5683 | 3.8727 | 0.65002 | 0.68665 | 122.4426 | -0.23346 | -0.11444 | 0.004578 | 0.041199 | 0.13275 | -0.70953 | -0.14191 | 0.16479 | 0.15564 | 0.74158 | 0.7782 | 121.6599 | 122.374 | 0.041199 | 122.5342 | 3.9642 | -0.14191 | 122.374 | 0.041199 | 3.9642 | 121.6599 | 122.5342 | -122.4838 | -122.5113
3418.8125 | 122.4564 | -0.050354 | 122.2366 | 0.099564 | 0.01091 | -0.015114 | 0.014467 | 0.047978 | -0.013954 | 0.064125 | -0.050354 | 122.2824 | -0.18768 | 0.050354 | 121.5408 | 3.7125 | 0.29755 | 0.37079 | 122.4472 | -0.23346 | -0.13733 | 0.045777 | 0 | 0.10071 | -0.6958 | -0.1831 | 0.21057 | 0.13733 | 0.3479 | 0.42114 | 121.5912 | 122.3328 | 0 | 122.4976 | 3.7628 | -0.1831 | 122.3328 | 0 | 3.7628 | 121.5912 | 122.4976 | -122.4243 | -122.4701
3420.5781 | 122.3694 | -0.10529 | 122.287 | -0.13695 | 0.010269 | -0.0102 | 0.0065624 | 0.045628 | -0.01139 | 0.06733 | 0.059509 | 122.2824 | -0.15564 | 0.16479 | 121.6827 | 3.9597 | 0.43945 | 0.81482 | 122.3923 | -0.20142 | -0.050354 | -0.004577 | 0.16479 | 0.27008 | -0.60425 | -0.09613 | 0.10529 | 0.21515 | 0.54474 | 0.9201 | 121.788 | 122.3877 | 0.16479 | 122.4976 | 4.0649 | -0.09613 | 122.3877 | 0.16479 | 4.0649 | 121.788 | 122.4976 | -122.4426 | -122.4884
3422.3281 | 122.319 | -0.091553 | 122.2824 | -0.12169 | 0.0087734 | -0.013405 | 0.016816 | 0.047123 | -0.014808 | 0.066475 | 0 | 122.2733 | -0.19226 | 0.10986 | 121.6003 | 3.9185 | 0.49439 | 0.64087 | 122.4747 | -0.23346 | -0.10071 | -0.009156 | 0.091553 | 0.20142 | -0.68207 | -0.14191 | 0.19226 | 0.19226 | 0.58594 | 0.73242 | 121.6919 | 122.3648 | 0.091553 | 122.5662 | 4.01 | -0.14191 | 122.3648 | 0.091553 | 4.01 | 121.6919 | 122.5662 | -122.4747 | -122.5159
3424.0938 | 122.3373 | -0.10529 | 122.2595 | -0.18272 | 0.0094144 | -0.01255 | 0.0097668 | 0.044773 | -0.011177 | 0.066048 | 0.032043 | 122.2458 | -0.15564 | 0.17395 | 121.6736 | 3.9917 | 0.50354 | 0.83771 | 122.3831 | -0.19684 | -0.050354 | -0.013732 | 0.13733 | 0.27924 | -0.58594 | -0.091552 | 0.1236 | 0.18768 | 0.60883 | 0.94299 | 121.7789 | 122.3511 | 0.13733 | 122.4884 | 4.097 | -0.091552 | 122.3511 | 0.13733 | 4.097 | 121.7789 | 122.4884 | -122.4152 | -122.4564
3425.8594 | 122.4426 | -0.059509 | 122.2275 | 0.10719 | 0.010269 | -0.011909 | 0.014253 | 0.048832 | -0.013954 | 0.065193 | -0.022888 | 122.2778 | -0.17395 | 0.054932 | 121.55 | 3.7811 | 0.24261 | 0.39825 | 122.4426 | -0.20142 | -0.11444 | 0.050354 | 0.036621 | 0.11444 | -0.67749 | -0.14191 | 0.21515 | 0.15106 | 0.30212 | 0.45776 | 121.6095 | 122.3373 | 0.036621 | 122.5021 | 3.8406 | -0.14191 | 122.3373 | 0.036621 | 3.8406 | 121.6095 | 122.5021 | -122.4014 | -122.4289
3427.625 | 122.3419 | -0.10986 | 122.2824 | -0.15984 | 0.0098416 | -0.013191 | 0.0097668 | 0.043492 | -0.012458 | 0.064339 | 0.068665 | 122.2687 | -0.15106 | 0.17853 | 121.6965 | 4.0054 | 0.48065 | 0.83313 | 122.3831 | -0.19684 | -0.041199 | -0.013733 | 0.17853 | 0.28839 | -0.58594 | -0.086975 | 0.10071 | 0.21973 | 0.59052 | 0.94299 | 121.8063 | 122.3785 | 0.17853 | 122.493 | 4.1153 | -0.086975 | 122.3785 | 0.17853 | 4.1153 | 121.8063 | 122.493 | -122.4335 | -122.4792
3429.3281 | 122.3602 | -0.073242 | 122.2824 | -0.20561 | 0.010482 | -0.011055 | 0.015321 | 0.049259 | -0.014808 | 0.06733 | -0.013733 | 122.2641 | -0.21057 | 0.086975 | 121.5775 | 3.9413 | 0.56763 | 0.68207 | 122.4747 | -0.21973 | -0.13733 | -0.018311 | 0.059509 | 0.16022 | -0.70496 | -0.14649 | 0.19226 | 0.19684 | 0.64087 | 0.75531 | 121.6507 | 122.3373 | 0.059509 | 122.5479 | 4.0146 | -0.14649 | 122.3373 | 0.059509 | 4.0146 | 121.6507 | 122.5479 | -122.493 | -122.5021
3431.1094 | 122.4609 | -0.068665 | 122.2229 | 0.00038159 | 0.0072782 | -0.016396 | 0.0086988 | 0.048191 | -0.011604 | 0.064766 | 0 | 122.2824 | -0.16022 | 0.091553 | 121.6324 | 3.8818 | 0.39825 | 0.61798 | 122.3923 | -0.2243 | -0.091552 | 0.05951 | 0.068665 | 0.16022 | -0.59051 | -0.15564 | 0.16937 | 0.16022 | 0.46692 | 0.68665 | 121.701 | 122.3511 | 0.068665 | 122.4609 | 3.9505 | -0.15564 | 122.3511 | 0.068665 | 3.9505 | 121.701 | 122.4609 | -122.3831 | -122.4472
3432.8125 | 122.3877 | -0.073242 | 122.2778 | -0.25139 | 0.0068508 | -0.014046 | 0.015748 | 0.04691 | -0.015449 | 0.065407 | -0.073242 | 122.287 | -0.20599 | 0.036621 | 121.5546 | 3.9368 | 0.6958 | 0.69122 | 122.4289 | -0.23346 | -0.13275 | 0.009155 | 0 | 0.10986 | -0.72327 | -0.16022 | 0.15106 | 0.13275 | 0.76904 | 0.76447 | 121.6278 | 122.3602 | 0 | 122.5021 | 4.01 | -0.16022 | 122.3602 | 0 | 4.01 | 121.6278 | 122.5021 | -122.4838 | -122.5113
3434.5781 | 122.3419 | -0.10071 | 122.2641 | -0.030136 | 0.010055 | -0.0099869 | 0.014253 | 0.046482 | -0.01374 | 0.066475 | -0.009155 | 122.2778 | -0.19684 | 0.082397 | 121.5546 | 3.8727 | 0.41199 | 0.49896 | 122.4289 | -0.21973 | -0.09613 | 0.013733 | 0.091553 | 0.18311 | -0.70953 | -0.11902 | 0.16479 | 0.18768 | 0.5127 | 0.59967 | 121.6553 | 122.3785 | 0.091553 | 122.5296 | 3.9734 | -0.11902 | 122.3785 | 0.091553 | 3.9734 | 121.6553 | 122.5296 | -122.4609 | -122.4838
3436.3281 | 122.4472 | -0.073242 | 122.2366 | 0.091934 | 0.0089872 | -0.014046 | 0.0095532 | 0.04755 | -0.012031 | 0.066048 | 0.054932 | 122.2733 | -0.13733 | 0.13275 | 121.637 | 3.8864 | 0.20599 | 0.54474 | 122.406 | -0.21057 | -0.064087 | 0.036621 | 0.12817 | 0.20599 | -0.59967 | -0.13733 | 0.16937 | 0.19226 | 0.27924 | 0.61798 | 121.7102 | 122.3465 | 0.12817 | 122.4792 | 3.9597 | -0.13733 | 122.3465 | 0.12817 | 3.9597 | 121.7102 | 122.4792 | -122.374 | -122.4472
3438.0781 | 122.4472 | -0.054932 | 122.2412 | 0.053787 | 0.0066372 | -0.010628 | 0.015107 | 0.050968 | -0.014381 | 0.066048 | -0.050354 | 122.2641 | -0.20599 | 0.036621 | 121.5179 | 3.8223 | 0.38452 | 0.3891 | 122.4564 | -0.21515 | -0.15106 | 0.022888 | 0.004578 | 0.091553 | -0.72327 | -0.16022 | 0.21515 | 0.15564 | 0.43945 | 0.44403 | 121.5729 | 122.319 | 0.004578 | 122.5113 | 3.8773 | -0.16022 | 122.319 | 0.004578 | 3.8773 | 121.5729 | 122.5113 | -122.4472 | -122.4564
3439.8438 | 122.4152 | -0.064087 | 122.2549 | 0.13771 | 0.0087734 | -0.012978 | 0.011049 | 0.048405 | -0.013313 | 0.068184 | 0.059509 | 122.2549 | -0.14191 | 0.13733 | 121.669 | 3.9093 | 0.16937 | 0.53101 | 122.3877 | -0.18768 | -0.07782 | 0 | 0.1236 | 0.20142 | -0.58594 | -0.1236 | 0.13275 | 0.20142 | 0.23346 | 0.59509 | 121.7331 | 122.319 | 0.1236 | 122.4518 | 3.9734 | -0.1236 | 122.319 | 0.1236 | 3.9734 | 121.7331 | 122.4518 | -122.3969 | -122.4426
3441.6094 | 122.4564 | -0.041199 | 122.2275 | 0.10719 | 0.012832 | -0.010841 | 0.013398 | 0.048405 | -0.013527 | 0.066475 | -0.032043 | 122.2366 | -0.17853 | 0.050354 | 121.5591 | 3.8452 | 0.26093 | 0.38452 | 122.4335 | -0.20142 | -0.13733 | 0.009155 | 0.009156 | 0.091553 | -0.66833 | -0.16022 | 0.20599 | 0.14648 | 0.30212 | 0.42572 | 121.6003 | 122.2778 | 0.009156 | 122.4747 | 3.8864 | -0.16022 | 122.2778 | 0.009156 | 3.8864 | 121.6003 | 122.4747 | -122.406 | -122.4289
3443.3594 | 122.4701 | -0.064087 | 122.2458 | 0.13008 | 0.0089872 | -0.010414 | 0.014467 | 0.048405 | -0.013527 | 0.065621 | -0.059509 | 122.2916 | -0.20599 | 0.027466 | 121.5591 | 3.8406 | 0.31128 | 0.38452 | 122.4335 | -0.24719 | -0.14191 | 0.045776 | 0.004578 | 0.091553 | -0.68665 | -0.1831 | 0.18768 | 0.14649 | 0.37537 | 0.44861 | 121.6232 | 122.3557 | 0.004578 | 122.4976 | 3.9047 | -0.1831 | 122.3557 | 0.004578 | 3.9047 | 121.6232 | 122.4976 | -122.4518 | -122.493
3445.1094 | 122.4152 | -0.07782 | 122.2412 | 0.18349 | 0.0074918 | -0.0102 | 0.0099804 | 0.048619 | -0.013099 | 0.065193 | 0.059509 | 122.2458 | -0.15106 | 0.15564 | 121.6553 | 3.9459 | 0.15106 | 0.51727 | 122.3602 | -0.20142 | -0.073242 | 0.004578 | 0.13733 | 0.23346 | -0.58594 | -0.1236 | 0.11902 | 0.21057 | 0.22888 | 0.59509 | 121.7331 | 122.3236 | 0.13733 | 122.438 | 4.0237 | -0.1236 | 122.3236 | 0.13733 | 4.0237 | 121.7331 | 122.438 | -122.3923 | -122.4426
3446.8125 | 122.4655 | -0.064087 | 122.2595 | 0.11482 | 0.0083462 | -0.0091325 | 0.009126 | 0.049259 | -0.0096814 | 0.065621 | 0.050354 | 122.2549 | -0.16479 | 0.10071 | 121.637 | 3.923 | 0.27008 | 0.55389 | 122.4106 | -0.21057 | -0.10071 | -0.004577 | 0.11444 | 0.1648 | -0.62256 | -0.14648 | 0.15106 | 0.21515 | 0.33417 | 0.61798 | 121.701 | 122.319 | 0.11444 | 122.4747 | 3.9871 | -0.14648 | 122.319 | 0.11444 | 3.9871 | 121.701 | 122.4747 | -122.4243 | -122.4701
3448.5625 | 122.4609 | -0.054932 | 122.2366 | 0.053787 | 0.0077054 | -0.0087051 | 0.0097668 | 0.048405 | -0.010322 | 0.066262 | 0.022888 | 122.287 | -0.13275 | 0.10986 | 121.6187 | 3.9505 | 0.32044 | 0.56763 | 122.3785 | -0.21973 | -0.077819 | 0.050354 | 0.07782 | 0.16479 | -0.61798 | -0.16479 | 0.14191 | 0.15564 | 0.37537 | 0.62256 | 121.6736 | 122.3419 | 0.07782 | 122.4335 | 4.0054 | -0.16479 | 122.3419 | 0.07782 | 4.0054 | 121.6736 | 122.4335 | -122.3694 | -122.4564
3450.3281 | 122.4106 | -0.07782 | 122.2366 | 0.14534 | 0.010696 | -0.011482 | 0.012758 | 0.047978 | -0.010963 | 0.066475 | 0.064087 | 122.2733 | -0.14191 | 0.16479 | 121.6461 | 3.9917 | 0.15564 | 0.53558 | 122.3785 | -0.18768 | -0.064087 | 0.036621 | 0.14191 | 0.24261 | -0.59051 | -0.10986 | 0.14191 | 0.20599 | 0.23346 | 0.6134 | 121.7239 | 122.3511 | 0.14191 | 122.4564 | 4.0695 | -0.10986 | 122.3511 | 0.14191 | 4.0695 | 121.7239 | 122.4564 | -122.3785 | -122.4243
3452.0312 | 122.4197 | -0.07782 | 122.2366 | 0.15297 | 0.0087734 | -0.014473 | 0.01233 | 0.047764 | -0.014808 | 0.066902 | 0.059509 | 122.2595 | -0.15564 | 0.15106 | 121.6507 | 3.9871 | 0.13275 | 0.52185 | 122.3969 | -0.17395 | -0.07782 | 0.022888 | 0.13733 | 0.22888 | -0.58594 | -0.09613 | 0.16022 | 0.21515 | 0.21057 | 0.59967 | 121.7285 | 122.3373 | 0.13733 | 122.4747 | 4.0649 | -0.09613 | 122.3373 | 0.13733 | 4.0649 | 121.7285 | 122.4747 | -122.3923 | -122.4106
3453.7812 | 122.4655 | -0.054932 | 122.2504 | -0.022507 | 0.0072782 | -0.010841 | 0.007417 | 0.044987 | -0.011818 | 0.064766 | -0.013733 | 122.2961 | -0.16022 | 0.11444 | 121.6187 | 4.0237 | 0.42572 | 0.67749 | 122.3969 | -0.22888 | -0.10528 | 0.045777 | 0.041199 | 0.16937 | -0.63171 | -0.17395 | 0.14648 | 0.14648 | 0.48065 | 0.73242 | 121.6736 | 122.3511 | 0.041199 | 122.4518 | 4.0787 | -0.17395 | 122.3511 | 0.041199 | 4.0787 | 121.6736 | 122.4518 | -122.4106 | -122.4792
3455.5469 | 122.4747 | -0.050354 | 122.2092 | 0.038529 | 0.0087734 | -0.017036 | 0.010621 | 0.044773 | -0.014381 | 0.066902 | -0.018311 | 122.2229 | -0.16937 | 0.086975 | 121.6187 | 3.9917 | 0.35248 | 0.59052 | 122.4197 | -0.20142 | -0.11902 | 0.013733 | 0.032043 | 0.13733 | -0.59051 | -0.15106 | 0.21057 | 0.15106 | 0.40283 | 0.64087 | 121.669 | 122.2733 | 0.032043 | 122.4701 | 4.0421 | -0.15106 | 122.2733 | 0.032043 | 4.0421 | 121.669 | 122.4701 | -122.3785 | -122.4106
3457.3125 | 122.4747 | -0.036621 | 122.2504 | 0.00038159 | 0.011551 | -0.014259 | 0.0099804 | 0.045201 | -0.013099 | 0.064339 | 0.004578 | 122.287 | -0.16479 | 0.091553 | 121.6141 | 4.0192 | 0.41657 | 0.62256 | 122.4197 | -0.20142 | -0.12817 | 0.036621 | 0.041199 | 0.12817 | -0.63629 | -0.1648 | 0.16937 | 0.16937 | 0.45319 | 0.65918 | 121.6507 | 122.3236 | 0.041199 | 122.4564 | 4.0558 | -0.1648 | 122.3236 | 0.041199 | 4.0558 | 121.6507 | 122.4564 | -122.4152 | -122.4518
3459.0156 | 122.3877 | -0.10071 | 122.2412 | -0.23613 | 0.0087734 | -0.0093461 | 0.014253 | 0.047123 | -0.012886 | 0.065407 | -0.054932 | 122.2733 | -0.20599 | 0.041199 | 121.5591 | 4.0833 | 0.72784 | 0.71411 | 122.4838 | -0.23346 | -0.10529 | 0.032043 | 0.045776 | 0.14191 | -0.68207 | -0.13275 | 0.24261 | 0.15106 | 0.82855 | 0.81482 | 121.6599 | 122.374 | 0.045776 | 122.5845 | 4.184 | -0.13275 | 122.374 | 0.045776 | 4.184 | 121.6599 | 122.5845 | -122.4472 | -122.4747
3460.7969 | 122.4564 | -0.045776 | 122.2504 | 0.0080111 | 0.0092008 | -0.011055 | 0.0095532 | 0.048619 | -0.011177 | 0.065407 | 0 | 122.287 | -0.13733 | 0.10071 | 121.6278 | 4.0512 | 0.40741 | 0.6546 | 122.4106 | -0.19684 | -0.091553 | 0.036621 | 0.045776 | 0.14648 | -0.62256 | -0.15106 | 0.16022 | 0.13733 | 0.45319 | 0.70038 | 121.6736 | 122.3328 | 0.045776 | 122.4564 | 4.097 | -0.15106 | 122.3328 | 0.045776 | 4.097 | 121.6736 | 122.4564 | -122.3877 | -122.4472
3462.5625 | 122.374 | -0.086975 | 122.2549 | 0.26741 | 0.0083462 | -0.010628 | 0.017671 | 0.049046 | -0.01609 | 0.063698 | -0.032043 | 122.3007 | -0.18768 | 0.050354 | 121.5363 | 3.9917 | 0.41199 | 0.45319 | 122.4426 | -0.22888 | -0.10071 | 0.045776 | 0.054932 | 0.13733 | -0.71869 | -0.14191 | 0.18768 | 0.15564 | 0.49896 | 0.54016 | 121.6232 | 122.3877 | 0.054932 | 122.5296 | 4.0787 | -0.14191 | 122.3877 | 0.054932 | 4.0787 | 121.6232 | 122.5296 | -122.4426 | -122.4838
3464.3125 | 122.3419 | -0.086975 | 122.2778 | -0.045395 | 0.011764 | -0.013832 | 0.01703 | 0.0499 | -0.015022 | 0.06498 | 0.027466 | 122.3236 | -0.18768 | 0.091553 | 121.5729 | 4.0741 | 0.44403 | 0.54932 | 122.4655 | -0.2243 | -0.10071 | 0.045776 | 0.11444 | 0.17853 | -0.70496 | -0.13733 | 0.18768 | 0.21515 | 0.53101 | 0.63629 | 121.6599 | 122.4106 | 0.11444 | 122.5525 | 4.1611 | -0.13733 | 122.4106 | 0.11444 | 4.1611 | 121.6599 | 122.5525 | -122.4655 | -122.5021
3466 | 122.493 | -0.059509 | 122.2321 | 0.02327 | 0.0087734 | -0.013832 | 0.0078442 | 0.047978 | -0.012672 | 0.066689 | -0.013733 | 122.287 | -0.16937 | 0.09613 | 121.6141 | 4.0604 | 0.37994 | 0.60883 | 122.4152 | -0.20599 | -0.10986 | 0.054931 | 0.045776 | 0.15564 | -0.61798 | -0.14649 | 0.1831 | 0.15564 | 0.43945 | 0.66834 | 121.6736 | 122.3465 | 0.045776 | 122.4747 | 4.1199 | -0.14649 | 122.3465 | 0.045776 | 4.1199 | 121.6736 | 122.4747 | -122.4014 | -122.4381
3467.75 | 122.4106 | -0.064087 | 122.2504 | 0.16823 | 0.0087734 | -0.012123 | 0.014467 | 0.050114 | -0.014167 | 0.065193 | 0.068665 | 122.2595 | -0.15106 | 0.16937 | 121.6507 | 4.0741 | 0.14191 | 0.52643 | 122.4243 | -0.20142 | -0.086975 | 0.009155 | 0.13275 | 0.23346 | -0.59967 | -0.13733 | 0.17395 | 0.21973 | 0.20599 | 0.59052 | 121.7148 | 122.3236 | 0.13275 | 122.4884 | 4.1382 | -0.13733 | 122.3236 | 0.13275 | 4.1382 | 121.7148 | 122.4884 | -122.4014 | -122.4518
3469.5156 | 122.3785 | -0.082397 | 122.2366 | -0.19798 | 0.0081326 | -0.010841 | 0.010408 | 0.047337 | -0.012672 | 0.066902 | -0.054932 | 122.3053 | -0.21515 | 0.054932 | 121.5637 | 4.1565 | 0.6958 | 0.72784 | 122.4197 | -0.23346 | -0.13275 | 0.068665 | 0.027465 | 0.13733 | -0.67291 | -0.15106 | 0.18311 | 0.16022 | 0.7782 | 0.81024 | 121.6461 | 122.3877 | 0.027465 | 122.5021 | 4.2389 | -0.15106 | 122.3877 | 0.027465 | 4.2389 | 121.6461 | 122.5021 | -122.4518 | -122.4701
3471.2344 | 122.4609 | -0.054932 | 122.2366 | -0.014877 | 0.0092008 | -0.012978 | 0.009126 | 0.046482 | -0.01139 | 0.065193 | 0 | 122.2824 | -0.15564 | 0.10529 | 121.6278 | 4.1428 | 0.41657 | 0.69122 | 122.4289 | -0.21515 | -0.10071 | 0.045777 | 0.054932 | 0.16022 | -0.60882 | -0.16022 | 0.19226 | 0.15564 | 0.4715 | 0.74616 | 121.6827 | 122.3373 | 0.054932 | 122.4838 | 4.1977 | -0.16022 | 122.3373 | 0.054932 | 4.1977 | 121.6827 | 122.4838 | -122.3923 | -122.4518
3472.9844 | 122.4426 | -0.073242 | 122.2412 | 0.091934 | 0.010055 | -0.011696 | 0.012758 | 0.047764 | -0.013313 | 0.06733 | 0.032043 | 122.2778 | -0.15564 | 0.12817 | 121.6141 | 4.1153 | 0.20599 | 0.55389 | 122.3785 | -0.20142 | -0.082398 | 0.036621 | 0.10529 | 0.20142 | -0.62714 | -0.12817 | 0.13733 | 0.18768 | 0.27924 | 0.62714 | 121.6873 | 122.3511 | 0.10529 | 122.4518 | 4.1885 | -0.12817 | 122.3511 | 0.10529 | 4.1885 | 121.6873 | 122.4518 | -122.3969 | -122.4426
3474.7344 | 122.4152 | -0.068665 | 122.2549 | 0.13771 | 0.0066372 | -0.010414 | 0.012758 | 0.047337 | -0.014808 | 0.065621 | 0.054932 | 122.2641 | -0.15564 | 0.16022 | 121.6461 | 4.1245 | 0.17853 | 0.55847 | 122.3969 | -0.19684 | -0.086975 | 0.009155 | 0.1236 | 0.22888 | -0.60883 | -0.12817 | 0.14191 | 0.21057 | 0.24719 | 0.62714 | 121.7148 | 122.3328 | 0.1236 | 122.4655 | 4.1931 | -0.12817 | 122.3328 | 0.1236 | 4.1931 | 121.7148 | 122.4655 | -122.4106 | -122.4518
3476.5 | 122.3602 | -0.10986 | 122.2824 | -0.18272 | 0.009628 | -0.015114 | 0.009126 | 0.046269 | -0.012245 | 0.063057 | 0.054932 | 122.2687 | -0.14191 | 0.13733 | 121.6461 | 4.2801 | 0.56763 | 0.84686 | 122.4335 | -0.19684 | -0.032044 | -0.013733 | 0.16479 | 0.24719 | -0.63629 | -0.086975 | 0.15106 | 0.19684 | 0.67749 | 0.95673 | 121.756 | 122.3785 | 0.16479 | 122.5433 | 4.39 | -0.086975 | 122.3785 | 0.16479 | 4.39 | 121.756 | 122.5433 | -122.4243 | -122.4792
3478.2031 | 122.3282 | -0.091553 | 122.2687 | -0.14458 | 0.0089872 | -0.015327 | 0.015535 | 0.050328 | -0.012672 | 0.065407 | -0.022888 | 122.2778 | -0.21973 | 0.10529 | 121.5912 | 4.2206 | 0.56763 | 0.68207 | 122.4701 | -0.20599 | -0.12817 | 0.009155 | 0.068665 | 0.19684 | -0.67749 | -0.11444 | 0.20142 | 0.19684 | 0.65918 | 0.77362 | 121.6827 | 122.3694 | 0.068665 | 122.5616 | 4.3121 | -0.11444 | 122.3694 | 0.068665 | 4.3121 | 121.6827 | 122.5616 | -122.4884 | -122.4747
3479.9844 | 122.4106 | -0.086975 | 122.2733 | -0.022507 | 0.0087734 | -0.011055 | 0.0086988 | 0.048191 | -0.011818 | 0.066262 | 0.045776 | 122.2961 | -0.15106 | 0.16937 | 121.6782 | 4.2847 | 0.45776 | 0.79193 | 122.3969 | -0.20142 | -0.064087 | 0.022889 | 0.13275 | 0.25635 | -0.59509 | -0.11444 | 0.1236 | 0.19684 | 0.54474 | 0.87891 | 121.7651 | 122.3831 | 0.13275 | 122.4838 | 4.3716 | -0.11444 | 122.3831 | 0.13275 | 4.3716 | 121.7651 | 122.4838 | -122.4243 | -122.4747
3481.6875 | 122.4335 | -0.068665 | 122.2366 | 0.076676 | 0.0074918 | -0.0091325 | 0.010835 | 0.047337 | -0.01374 | 0.067757 | 0.041199 | 122.1909 | -0.16022 | 0.1236 | 121.6324 | 4.1565 | 0.21973 | 0.54474 | 122.4197 | -0.19226 | -0.091552 | -0.045776 | 0.10986 | 0.19226 | -0.60425 | -0.1236 | 0.18311 | 0.20142 | 0.28839 | 0.6134 | 121.701 | 122.2595 | 0.10986 | 122.4884 | 4.2252 | -0.1236 | 122.2595 | 0.10986 | 4.2252 | 121.701 | 122.4884 | -122.3969 | -122.4289
3483.4375 | 122.319 | -0.09613 | 122.2961 | -0.10643 | 0.011551 | -0.014473 | 0.017457 | 0.0499 | -0.015236 | 0.065407 | 0.022888 | 122.2778 | -0.18768 | 0.10529 | 121.5912 | 4.2435 | 0.48981 | 0.64545 | 122.4655 | -0.20599 | -0.091553 | -0.018311 | 0.11902 | 0.20142 | -0.70496 | -0.10986 | 0.16937 | 0.21057 | 0.58594 | 0.74158 | 121.6873 | 122.374 | 0.11902 | 122.5616 | 4.3396 | -0.10986 | 122.374 | 0.11902 | 4.3396 | 121.6873 | 122.5616 | -122.4838 | -122.5021
3485.2031 | 122.4609 | -0.032043 | 122.2321 | 0.084305 | 0.011764 | -0.011269 | 0.014894 | 0.04691 | -0.015236 | 0.069252 | -0.032043 | 122.3145 | -0.1831 | 0.032043 | 121.55 | 4.0924 | 0.32044 | 0.40741 | 122.4472 | -0.2243 | -0.15106 | 0.082397 | 0 | 0.064086 | -0.68207 | -0.19226 | 0.21515 | 0.15106 | 0.35248 | 0.43945 | 121.582 | 122.3465 | 0 | 122.4792 | 4.1244 | -0.19226 | 122.3465 | 0 | 4.1244 | 121.582 | 122.4792 | -122.4152 | -122.4564
3486.9688 | 122.3877 | -0.086975 | 122.2504 | -0.21324 | 0.01091 | -0.013405 | 0.012758 | 0.0499 | -0.015022 | 0.065407 | -0.027466 | 122.3282 | -0.19226 | 0.045776 | 121.5591 | 4.2526 | 0.68665 | 0.71411 | 122.4655 | -0.23346 | -0.10529 | 0.07782 | 0.059509 | 0.13275 | -0.69122 | -0.14648 | 0.21515 | 0.16479 | 0.77362 | 0.80109 | 121.6461 | 122.4152 | 0.059509 | 122.5525 | 4.3396 | -0.14648 | 122.4152 | 0.059509 | 4.3396 | 121.6461 | 122.5525 | -122.4426 | -122.4838
3488.6719 | 122.4747 | -0.059509 | 122.2229 | 0.084305 | 0.010269 | -0.016396 | 0.0095532 | 0.04691 | -0.012245 | 0.066689 | 0.022888 | 122.2778 | -0.14648 | 0.10071 | 121.6232 | 4.1885 | 0.32044 | 0.56763 | 122.3969 | -0.19226 | -0.086975 | 0.054932 | 0.082397 | 0.16022 | -0.59967 | -0.13275 | 0.17395 | 0.16937 | 0.37994 | 0.62714 | 121.6827 | 122.3373 | 0.082397 | 122.4564 | 4.248 | -0.13275 | 122.3373 | 0.082397 | 4.248 | 121.6827 | 122.4564 | -122.3694 | -122.4152
3490.4219 | 122.4976 | -0.045776 | 122.2549 | 0.02327 | 0.010055 | -0.0089189 | 0.007417 | 0.044987 | -0.011177 | 0.066902 | -0.004578 | 122.287 | -0.16937 | 0.10529 | 121.6049 | 4.2206 | 0.37994 | 0.6134 | 122.3877 | -0.21515 | -0.1236 | 0.032043 | 0.041198 | 0.15106 | -0.65002 | -0.16937 | 0.13275 | 0.16479 | 0.42572 | 0.65918 | 121.6507 | 122.3328 | 0.041198 | 122.4335 | 4.2664 | -0.16937 | 122.3328 | 0.041198 | 4.2664 | 121.6507 | 122.4335 | -122.4243 | -122.4701
3492.1875 | 122.4106 | -0.064087 | 122.2504 | 0.099564 | 0.0087734 | -0.011482 | 0.015535 | 0.048191 | -0.012031 | 0.066048 | 0.045776 | 122.2733 | -0.16022 | 0.15564 | 121.6461 | 4.2389 | 0.14648 | 0.53558 | 122.374 | -0.18768 | -0.09613 | 0.022888 | 0.10986 | 0.21973 | -0.60425 | -0.1236 | 0.1236 | 0.20599 | 0.21057 | 0.59967 | 121.7102 | 122.3373 | 0.10986 | 122.438 | 4.303 | -0.1236 | 122.3373 | 0.10986 | 4.303 | 121.7102 | 122.438 | -122.4106 | -122.438
3493.9375 | 122.4472 | -0.064087 | 122.2321 | 0.12245 | 0.009628 | -0.0080643 | 0.017671 | 0.049046 | -0.014808 | 0.067116 | -0.041199 | 122.2824 | -0.18768 | 0.064087 | 121.5637 | 4.1565 | 0.25635 | 0.42114 | 122.4289 | -0.2243 | -0.1236 | 0.050354 | 0.022888 | 0.12817 | -0.66833 | -0.16022 | 0.19684 | 0.14648 | 0.32044 | 0.48523 | 121.6278 | 122.3465 | 0.022888 | 122.493 | 4.2206 | -0.16022 | 122.3465 | 0.022888 | 4.2206 | 121.6278 | 122.493 | -122.4197 | -122.4564
3495.6875 | 122.4152 | -0.045776 | 122.2458 | 0.15297 | 0.010482 | -0.011269 | 0.013185 | 0.050968 | -0.013527 | 0.066048 | 0.022888 | 122.2687 | -0.14648 | 0.14648 | 121.637 | 4.2435 | 0.1831 | 0.49896 | 122.4197 | -0.18768 | -0.10071 | 0.022888 | 0.068664 | 0.19226 | -0.60883 | -0.14191 | 0.17395 | 0.16937 | 0.22888 | 0.54474 | 121.6827 | 122.3145 | 0.068664 | 122.4655 | 4.2892 | -0.14191 | 122.3145 | 0.068664 | 4.2892 | 121.6827 | 122.4655 | -122.3923 | -122.4335
3497.4531 | 122.4609 | -0.050354 | 122.2366 | 0.00038159 | 0.0098416 | -0.011482 | 0.007417 | 0.047123 | -0.010963 | 0.06498 | 0 | 122.287 | -0.15564 | 0.10071 | 121.6415 | 4.2847 | 0.42114 | 0.66834 | 122.438 | -0.22888 | -0.10529 | 0.050354 | 0.050354 | 0.15106 | -0.59509 | -0.17853 | 0.20142 | 0.15564 | 0.4715 | 0.71869 | 121.6919 | 122.3373 | 0.050354 | 122.4884 | 4.335 | -0.17853 | 122.3373 | 0.050354 | 4.335 | 121.6919 | 122.4884 | -122.3923 | -122.4655
3499.1562 | 122.3969 | -0.091553 | 122.2595 | -0.25902 | 0.0094144 | -0.0091325 | 0.013398 | 0.047337 | -0.014381 | 0.065407 | -0.059509 | 122.2778 | -0.21973 | 0.041199 | 121.5546 | 4.3396 | 0.73242 | 0.72327 | 122.4472 | -0.23346 | -0.12817 | 0.018311 | 0.032044 | 0.13275 | -0.70496 | -0.14191 | 0.18768 | 0.16022 | 0.82398 | 0.81482 | 121.6461 | 122.3694 | 0.032044 | 122.5388 | 4.4312 | -0.14191 | 122.3694 | 0.032044 | 4.4312 | 121.6461 | 122.5388 | -122.4792 | -122.493
3500.9219 | 122.3877 | -0.086975 | 122.2595 | 0.046158 | 0.011123 | -0.0061417 | 0.016389 | 0.050968 | -0.014381 | 0.063698 | -0.022888 | 122.3007 | -0.19226 | 0.059509 | 121.5363 | 4.2252 | 0.41657 | 0.46692 | 122.4747 | -0.21057 | -0.10529 | 0.041199 | 0.064087 | 0.14648 | -0.72327 | -0.1236 | 0.21515 | 0.16937 | 0.50354 | 0.55389 | 121.6232 | 122.3877 | 0.064087 | 122.5616 | 4.3121 | -0.1236 | 122.3877 | 0.064087 | 4.3121 | 121.6232 | 122.5616 | -122.4518 | -122.4701
3502.6875 | 122.4701 | -0.050354 | 122.2458 | 0.030899 | 0.009628 | -0.0084915 | 0.0089124 | 0.048405 | -0.013527 | 0.066475 | 0.009155 | 122.3099 | -0.16022 | 0.091553 | 121.6095 | 4.2847 | 0.3479 | 0.57678 | 122.406 | -0.20142 | -0.10986 | 0.064086 | 0.059509 | 0.14191 | -0.63629 | -0.15106 | 0.16022 | 0.16937 | 0.39825 | 0.62714 | 121.6599 | 122.3602 | 0.059509 | 122.4564 | 4.335 | -0.15106 | 122.3602 | 0.059509 | 4.335 | 121.6599 | 122.4564 | -122.406 | -122.4472
3504.3906 | 122.3328 | -0.086975 | 122.2733 | -0.17509 | 0.011551 | -0.0095597 | 0.015107 | 0.048619 | -0.012886 | 0.063698 | -0.018311 | 122.2778 | -0.19226 | 0.086975 | 121.5683 | 4.3945 | 0.57678 | 0.70038 | 122.4335 | -0.22888 | -0.10529 | 0.004578 | 0.068664 | 0.17395 | -0.70496 | -0.14191 | 0.16022 | 0.17395 | 0.66376 | 0.78735 | 121.6553 | 122.3648 | 0.068664 | 122.5204 | 4.4815 | -0.14191 | 122.3648 | 0.068664 | 4.4815 | 121.6553 | 122.5204 | -122.4655 | -122.5021
3506.1406 | 122.3602 | -0.09613 | 122.2961 | -0.15221 | 0.01091 | -0.011055 | 0.0076306 | 0.044987 | -0.011818 | 0.064766 | 0.059509 | 122.2778 | -0.15106 | 0.16479 | 121.6782 | 4.4586 | 0.48523 | 0.83313 | 122.3877 | -0.20142 | -0.054932 | -0.018311 | 0.15564 | 0.26092 | -0.61798 | -0.10529 | 0.091552 | 0.21057 | 0.58136 | 0.92926 | 121.7743 | 122.374 | 0.15564 | 122.4838 | 4.5547 | -0.10529 | 122.374 | 0.15564 | 4.5547 | 121.7743 | 122.4838 | -122.4472 | -122.4976
3507.9062 | 122.374 | -0.07782 | 122.2687 | -0.21324 | 0.0083462 | -0.011482 | 0.01468 | 0.046269 | -0.013099 | 0.066048 | -0.050354 | 122.3099 | -0.20142 | 0.059509 | 121.5637 | 4.3808 | 0.68207 | 0.70038 | 122.438 | -0.2243 | -0.1236 | 0.041198 | 0.027466 | 0.13733 | -0.70496 | -0.14648 | 0.16937 | 0.15106 | 0.75989 | 0.7782 | 121.6415 | 122.3877 | 0.027466 | 122.5159 | 4.4586 | -0.14648 | 122.3877 | 0.027466 | 4.4586 | 121.6415 | 122.5159 | -122.4701 | -122.493
3509.6562 | 122.4518 | -0.073242 | 122.2504 | -0.068283 | 0.011337 | -0.0099869 | 0.0076306 | 0.044987 | -0.0083996 | 0.065834 | 0.004578 | 122.287 | -0.16022 | 0.13275 | 121.6644 | 4.4357 | 0.44861 | 0.75073 | 122.374 | -0.22888 | -0.086975 | 0.036621 | 0.07782 | 0.20599 | -0.58594 | -0.15564 | 0.1236 | 0.16479 | 0.52185 | 0.82397 | 121.7377 | 122.3602 | 0.07782 | 122.4472 | 4.509 | -0.15564 | 122.3602 | 0.07782 | 4.509 | 121.7377 | 122.4472 | -122.4106 | -122.4792
3511.3438 | 122.4564 | -0.041199 | 122.2458 | 0.046158 | 0.010269 | -0.012123 | 0.015748 | 0.049259 | -0.015022 | 0.065621 | -0.054932 | 122.3053 | -0.20599 | 0.027466 | 121.5134 | 4.2664 | 0.37537 | 0.4303 | 122.4838 | -0.24719 | -0.1648 | 0.059509 | -0.013733 | 0.068665 | -0.73242 | -0.20599 | 0.23804 | 0.15106 | 0.41656 | 0.4715 | 121.5546 | 122.3465 | -0.013733 | 122.525 | 4.3076 | -0.20599 | 122.3465 | -0.013733 | 4.3076 | 121.5546 | 122.525 | -122.4518 | -122.493
3513.1094 | 122.3648 | -0.091553 | 122.2733 | -0.18272 | 0.0098416 | -0.011482 | 0.01233 | 0.048191 | -0.014167 | 0.067116 | -0.045776 | 122.3053 | -0.19226 | 0.064087 | 121.5912 | 4.4312 | 0.64545 | 0.71869 | 122.4655 | -0.23346 | -0.10071 | 0.032044 | 0.045777 | 0.15564 | -0.68207 | -0.14191 | 0.19226 | 0.14648 | 0.737 | 0.81024 | 121.6827 | 122.3969 | 0.045777 | 122.5571 | 4.5227 | -0.14191 | 122.3969 | 0.045777 | 4.5227 | 121.6827 | 122.5571 | -122.4655 | -122.5067
3514.8125 | 122.3831 | -0.10071 | 122.2778 | -0.24376 | 0.010269 | -0.016182 | 0.010408 | 0.048832 | -0.012458 | 0.066689 | 0.004578 | 122.319 | -0.1831 | 0.082397 | 121.5866 | 4.4586 | 0.71869 | 0.76446 | 122.438 | -0.25177 | -0.082397 | 0.041199 | 0.10529 | 0.18311 | -0.69122 | -0.15106 | 0.16022 | 0.18768 | 0.8194 | 0.86517 | 121.6873 | 122.4197 | 0.10529 | 122.5388 | 4.5593 | -0.15106 | 122.4197 | 0.10529 | 4.5593 | 121.6873 | 122.5388 | -122.4609 | -122.5296
3516.5781 | 122.4106 | -0.073242 | 122.2321 | 0.12245 | 0.010482 | -0.012337 | 0.012758 | 0.049473 | -0.013527 | 0.064553 | 0.054932 | 122.2595 | -0.1236 | 0.15106 | 121.6507 | 4.39 | 0.17395 | 0.53558 | 122.4335 | -0.1831 | -0.050354 | 0.027465 | 0.12817 | 0.2243 | -0.58136 | -0.10986 | 0.20142 | 0.17853 | 0.24719 | 0.60883 | 121.7239 | 122.3328 | 0.12817 | 122.5067 | 4.4632 | -0.10986 | 122.3328 | 0.12817 | 4.4632 | 121.7239 | 122.5067 | -122.3557 | -122.4152
3518.3438 | 122.4884 | -0.064087 | 122.2366 | 0.0080111 | 0.010269 | -0.012978 | 0.010408 | 0.047123 | -0.012245 | 0.066902 | -0.009155 | 122.2824 | -0.16479 | 0.09613 | 121.6141 | 4.3991 | 0.39368 | 0.63629 | 122.4152 | -0.20599 | -0.10071 | 0.045777 | 0.054932 | 0.16022 | -0.62256 | -0.14191 | 0.17853 | 0.15564 | 0.45776 | 0.70038 | 121.6782 | 122.3465 | 0.054932 | 122.4792 | 4.4632 | -0.14191 | 122.3465 | 0.054932 | 4.4632 | 121.6782 | 122.4792 | -122.4014 | -122.4426
3520.0625 | 122.3877 | -0.082397 | 122.2778 | -0.12932 | 0.007919 | -0.010414 | 0.0099804 | 0.044987 | -0.010109 | 0.065407 | 0.050354 | 122.2824 | -0.16479 | 0.16022 | 121.6782 | 4.5456 | 0.48523 | 0.82398 | 122.374 | -0.19684 | -0.082398 | 0.004578 | 0.13275 | 0.24261 | -0.59967 | -0.11444 | 0.09613 | 0.21515 | 0.56763 | 0.90637 | 121.7606 | 122.3648 | 0.13275 | 122.4564 | 4.628 | -0.11444 | 122.3648 | 0.13275 | 4.628 | 121.7606 | 122.4564 | -122.4426 | -122.4747
3521.8438 | 122.4609 | -0.050354 | 122.2366 | 0.076676 | 0.009628 | -0.011909 | 0.016603 | 0.048405 | -0.014167 | 0.064553 | -0.064087 | 122.3236 | -0.18768 | 0.045776 | 121.4996 | 4.3304 | 0.3891 | 0.4303 | 122.4472 | -0.23804 | -0.13733 | 0.086975 | -0.013733 | 0.09613 | -0.737 | -0.18768 | 0.21057 | 0.1236 | 0.43945 | 0.48065 | 121.55 | 122.374 | -0.013733 | 122.4976 | 4.3808 | -0.18768 | 122.374 | -0.013733 | 4.3808 | 121.55 | 122.4976 | -122.4243 | -122.4747
3523.6094 | 122.438 | -0.050354 | 122.2412 | 0.17586 | 0.011978 | -0.0080643 | 0.014894 | 0.049259 | -0.012245 | 0.068398 | 0.004578 | 122.3282 | -0.17395 | 0.10529 | 121.6049 | 4.39 | 0.21057 | 0.4715 | 122.4197 | -0.21057 | -0.1236 | 0.086975 | 0.054932 | 0.15564 | -0.63629 | -0.16022 | 0.17853 | 0.17853 | 0.26093 | 0.52185 | 121.6553 | 122.3785 | 0.054932 | 122.4701 | 4.4403 | -0.16022 | 122.3785 | 0.054932 | 4.4403 | 121.6553 | 122.4701 | -122.4152 | -122.4518
3525.375 | 122.3328 | -0.10071 | 122.2778 | -0.098801 | 0.010055 | -0.013832 | 0.016389 | 0.047978 | -0.013527 | 0.066475 | 0.013733 | 122.2641 | -0.19684 | 0.11444 | 121.5866 | 4.5044 | 0.47607 | 0.61798 | 122.4335 | -0.21057 | -0.09613 | -0.013733 | 0.11444 | 0.21515 | -0.69122 | -0.10986 | 0.15564 | 0.21057 | 0.57678 | 0.71869 | 121.6873 | 122.3648 | 0.11444 | 122.5342 | 4.6051 | -0.10986 | 122.3648 | 0.11444 | 4.6051 | 121.6873 | 122.5342 | -122.4747 | -122.4884
3527.0938 | 122.525 | -0.054932 | 122.2549 | 0.10719 | 0.009628 | -0.0095597 | 0.0095532 | 0.047764 | -0.011177 | 0.066902 | 0.032043 | 122.3053 | -0.14191 | 0.11444 | 121.6095 | 4.4449 | 0.29297 | 0.60425 | 122.3831 | -0.21057 | -0.086975 | 0.050354 | 0.086975 | 0.16937 | -0.64545 | -0.15564 | 0.12817 | 0.17395 | 0.3479 | 0.65918 | 121.6644 | 122.3602 | 0.086975 | 122.438 | 4.4998 | -0.15564 | 122.3602 | 0.086975 | 4.4998 | 121.6644 | 122.438 | -122.3969 | -122.4655
3528.8594 | 122.4472 | -0.050354 | 122.2183 | 0.099564 | 0.010696 | -0.0095597 | 0.012544 | 0.050114 | -0.014381 | 0.066262 | -0.022888 | 122.3282 | -0.1831 | 0.068665 | 121.55 | 4.3854 | 0.28381 | 0.43945 | 122.4197 | -0.21057 | -0.13275 | 0.10986 | 0.027466 | 0.11902 | -0.66833 | -0.16022 | 0.20142 | 0.16022 | 0.33417 | 0.48981 | 121.6003 | 122.3785 | 0.027466 | 122.4701 | 4.4357 | -0.16022 | 122.3785 | 0.027466 | 4.4357 | 121.6003 | 122.4701 | -122.4014 | -122.4289
3530.625 | 122.4701 | -0.036621 | 122.2366 | 0.046158 | 0.0087734 | -0.011055 | 0.0076306 | 0.047123 | -0.01374 | 0.067757 | 0.018311 | 122.287 | -0.15564 | 0.10529 | 121.6141 | 4.4769 | 0.32959 | 0.59052 | 122.374 | -0.21057 | -0.11902 | 0.050354 | 0.054932 | 0.14191 | -0.62256 | -0.17395 | 0.13733 | 0.17395 | 0.36621 | 0.62714 | 121.6507 | 122.3236 | 0.054932 | 122.4106 | 4.5136 | -0.17395 | 122.3236 | 0.054932 | 4.5136 | 121.6507 | 122.4106 | -122.3923 | -122.4472
3532.3281 | 122.3465 | -0.10529 | 122.2687 | -0.19798 | 0.0092008 | -0.012978 | 0.009126 | 0.046269 | -0.012672 | 0.065407 | 0.032043 | 122.2961 | -0.14191 | 0.16022 | 121.6599 | 4.6555 | 0.58136 | 0.86517 | 122.3923 | -0.21057 | -0.036621 | 0.027466 | 0.13733 | 0.2655 | -0.60883 | -0.10529 | 0.1236 | 0.17395 | 0.68665 | 0.97046 | 121.7651 | 122.4014 | 0.13733 | 122.4976 | 4.7607 | -0.10529 | 122.4014 | 0.13733 | 4.7607 | 121.7651 | 122.4976 | -122.4106 | -122.4792
3534.1406 | 122.4655 | -0.068665 | 122.2549 | 0.099564 | 0.009628 | -0.010628 | 0.010408 | 0.046269 | -0.010109 | 0.066475 | 0.036621 | 122.2824 | -0.15564 | 0.1236 | 121.6232 | 4.4907 | 0.27466 | 0.57678 | 122.3923 | -0.20142 | -0.086975 | 0.027466 | 0.10529 | 0.19226 | -0.63171 | -0.13275 | 0.13733 | 0.19226 | 0.34332 | 0.64545 | 121.6919 | 122.3511 | 0.10529 | 122.4609 | 4.5593 | -0.13275 | 122.3511 | 0.10529 | 4.5593 | 121.6919 | 122.4609 | -122.4106 | -122.4564
3535.8438 | 122.3373 | -0.09613 | 122.2549 | -0.17509 | 0.011337 | -0.010841 | 0.016603 | 0.048832 | -0.015236 | 0.065621 | -0.013733 | 122.3007 | -0.18768 | 0.09613 | 121.5866 | 4.5959 | 0.58136 | 0.70496 | 122.493 | -0.23346 | -0.091553 | 0.045776 | 0.082397 | 0.19226 | -0.66833 | -0.13733 | 0.23804 | 0.17395 | 0.67749 | 0.80109 | 121.6827 | 122.3969 | 0.082397 | 122.5891 | 4.6921 | -0.13733 | 122.3969 | 0.082397 | 4.6921 | 121.6827 | 122.5891 | -122.4426 | -122.4884
3537.5781 | 122.4335 | -0.064087 | 122.2275 | 0.13771 | 0.0081326 | -0.016396 | 0.011049 | 0.050114 | -0.01374 | 0.06498 | 0.064087 | 122.287 | -0.13275 | 0.16022 | 121.6507 | 4.5319 | 0.21057 | 0.58136 | 122.4518 | -0.20142 | -0.068664 | 0.059509 | 0.12817 | 0.2243 | -0.57678 | -0.13733 | 0.2243 | 0.19684 | 0.27466 | 0.64545 | 121.7148 | 122.3511 | 0.12817 | 122.5159 | 4.5959 | -0.13733 | 122.3511 | 0.12817 | 4.5959 | 121.7148 | 122.5159 | -122.3602 | -122.4289
3539.3594 | 122.4747 | -0.041199 | 122.2549 | 0.11482 | 0.0089872 | -0.013618 | 0.017671 | 0.051396 | -0.014381 | 0.065621 | -0.054932 | 122.3099 | -0.19226 | 0.027466 | 121.5225 | 4.4403 | 0.36163 | 0.40741 | 122.4792 | -0.22888 | -0.15106 | 0.054931 | -0.013733 | 0.068665 | -0.73242 | -0.18768 | 0.2243 | 0.13733 | 0.40283 | 0.44861 | 121.5637 | 122.3511 | -0.013733 | 122.5204 | 4.4815 | -0.18768 | 122.3511 | -0.013733 | 4.4815 | 121.5637 | 122.5204 | -122.4472 | -122.4838
3541.0781 | 122.3511 | -0.11444 | 122.2641 | -0.091171 | 0.0094144 | -0.0149 | 0.016176 | 0.047764 | -0.017372 | 0.067543 | 0.009155 | 122.3053 | -0.19684 | 0.10529 | 121.6049 | 4.6143 | 0.49896 | 0.6546 | 122.4884 | -0.21515 | -0.082397 | 0.041199 | 0.1236 | 0.21973 | -0.65918 | -0.10071 | 0.2243 | 0.20599 | 0.6134 | 0.76904 | 121.7194 | 122.4197 | 0.1236 | 122.6028 | 4.7287 | -0.10071 | 122.4197 | 0.1236 | 4.7287 | 121.7194 | 122.6028 | -122.4609 | -122.4792
3542.8594 | 122.3969 | -0.064087 | 122.2229 | 0.069046 | 0.0094144 | -0.010628 | 0.013826 | 0.050755 | -0.015449 | 0.068184 | -0.022888 | 122.2824 | -0.19226 | 0.036621 | 121.5317 | 4.509 | 0.43488 | 0.46234 | 122.4701 | -0.22888 | -0.12817 | 0.05951 | 0.041199 | 0.10071 | -0.69122 | -0.16479 | 0.24719 | 0.16937 | 0.49896 | 0.52643 | 121.5958 | 122.3465 | 0.041199 | 122.5342 | 4.5731 | -0.16479 | 122.3465 | 0.041199 | 4.5731 | 121.5958 | 122.5342 | -122.4152 | -122.4518
3544.6406 | 122.4838 | -0.064087 | 122.2458 | 0.01564 | 0.0098416 | -0.014473 | 0.0037854 | 0.04755 | -0.013313 | 0.06797 | 0 | 122.3007 | -0.14648 | 0.086975 | 121.6095 | 4.5776 | 0.39825 | 0.62256 | 122.4014 | -0.20599 | -0.082397 | 0.054931 | 0.064087 | 0.15106 | -0.63629 | -0.14191 | 0.15564 | 0.14648 | 0.46234 | 0.68665 | 121.6736 | 122.3648 | 0.064087 | 122.4655 | 4.6417 | -0.14191 | 122.3648 | 0.064087 | 4.6417 | 121.6736 | 122.4655 | -122.3923 | -122.4518
3546.3281 | 122.493 | -0.054932 | 122.2366 | 0.046158 | 0.0072782 | -0.01255 | 0.0080578 | 0.046055 | -0.010322 | 0.066048 | 0 | 122.2916 | -0.14648 | 0.09613 | 121.6049 | 4.5822 | 0.38452 | 0.61798 | 122.3831 | -0.21057 | -0.091552 | 0.054932 | 0.054932 | 0.15106 | -0.63171 | -0.15564 | 0.14648 | 0.14648 | 0.43945 | 0.67291 | 121.6599 | 122.3465 | 0.054932 | 122.438 | 4.6371 | -0.15564 | 122.3465 | 0.054932 | 4.6371 | 121.6599 | 122.438 | -122.3831 | -122.4472
3548.0938 | 122.3373 | -0.091553 | 122.2824 | -0.15221 | 0.0083462 | -0.013832 | 0.010835 | 0.046269 | -0.012245 | 0.065834 | 0.041199 | 122.287 | -0.14191 | 0.16937 | 121.6461 | 4.7516 | 0.58136 | 0.87433 | 122.3923 | -0.21057 | -0.050354 | 0.004577 | 0.13275 | 0.26093 | -0.63629 | -0.11902 | 0.10986 | 0.18311 | 0.67291 | 0.96588 | 121.7377 | 122.3785 | 0.13275 | 122.4838 | 4.8431 | -0.11902 | 122.3785 | 0.13275 | 4.8431 | 121.7377 | 122.4838 | -122.4243 | -122.493
3549.8438 | 122.3923 | -0.11444 | 122.2824 | -0.25902 | 0.0087734 | -0.012764 | 0.01233 | 0.046055 | -0.012672 | 0.065621 | 0.013733 | 122.3145 | -0.16022 | 0.07782 | 121.5866 | 4.715 | 0.6958 | 0.80109 | 122.4518 | -0.21515 | -0.045776 | 0.032043 | 0.12817 | 0.19226 | -0.6958 | -0.10071 | 0.16937 | 0.17395 | 0.81024 | 0.91553 | 121.701 | 122.4289 | 0.12817 | 122.5662 | 4.8294 | -0.10071 | 122.4289 | 0.12817 | 4.8294 | 121.701 | 122.5662 | -122.4426 | -122.4976
3551.5938 | 122.3648 | -0.10986 | 122.2641 | -0.18272 | 0.010269 | -0.014473 | 0.011476 | 0.046696 | -0.013313 | 0.066475 | 0.050354 | 122.2778 | -0.15564 | 0.15106 | 121.6644 | 4.7928 | 0.58136 | 0.87891 | 122.4335 | -0.2243 | -0.045777 | 0.013733 | 0.16022 | 0.26093 | -0.59967 | -0.11444 | 0.16937 | 0.20599 | 0.69122 | 0.98877 | 121.7743 | 122.3877 | 0.16022 | 122.5433 | 4.9026 | -0.11444 | 122.3877 | 0.16022 | 4.9026 | 121.7743 | 122.5433 | -122.4197 | -122.4884
3553.2812 | 122.4701 | -0.050354 | 122.2458 | 0.14534 | 0.0098416 | -0.0082779 | 0.016816 | 0.047123 | -0.013954 | 0.067543 | -0.050354 | 122.3145 | -0.20599 | 0.032043 | 121.5408 | 4.5319 | 0.36621 | 0.41199 | 122.4426 | -0.2243 | -0.15564 | 0.068664 | 0 | 0.082397 | -0.70496 | -0.17395 | 0.19684 | 0.15564 | 0.41657 | 0.46234 | 121.5912 | 122.3648 | 0 | 122.493 | 4.5822 | -0.17395 | 122.3648 | 0 | 4.5822 | 121.5912 | 122.493 | -122.4518 | -122.4701
3555.0469 | 122.4335 | -0.059509 | 122.2412 | 0.13771 | 0.011764 | -0.01255 | 0.013612 | 0.049687 | -0.01374 | 0.065834 | 0.082397 | 122.3236 | -0.14648 | 0.15564 | 121.6461 | 4.6555 | 0.17395 | 0.55847 | 122.4014 | -0.19684 | -0.086975 | 0.082397 | 0.14191 | 0.21515 | -0.59509 | -0.13733 | 0.16022 | 0.22888 | 0.23346 | 0.61798 | 121.7056 | 122.3831 | 0.14191 | 122.4609 | 4.715 | -0.13733 | 122.3831 | 0.14191 | 4.715 | 121.7056 | 122.4609 | -122.3877 | -122.438
3556.75 | 122.3923 | -0.09613 | 122.2504 | -0.2285 | 0.010055 | -0.014259 | 0.012971 | 0.04691 | -0.012245 | 0.064766 | -0.068665 | 122.3053 | -0.19226 | 0.041199 | 121.5591 | 4.7195 | 0.71411 | 0.737 | 122.4564 | -0.23804 | -0.096131 | 0.054932 | 0.027465 | 0.13733 | -0.69122 | -0.14191 | 0.20599 | 0.1236 | 0.81024 | 0.83313 | 121.6553 | 122.4014 | 0.027465 | 122.5525 | 4.8157 | -0.14191 | 122.4014 | 0.027465 | 4.8157 | 121.6553 | 122.5525 | -122.4426 | -122.4884
3558.5156 | 122.4701 | -0.050354 | 122.2321 | 0.099564 | 0.010696 | -0.0046463 | 0.015535 | 0.050541 | -0.012886 | 0.068398 | -0.064087 | 122.3007 | -0.18768 | 0.027466 | 121.5363 | 4.5776 | 0.37079 | 0.40741 | 122.4518 | -0.23804 | -0.13733 | 0.068664 | -0.013733 | 0.07782 | -0.6958 | -0.18768 | 0.21973 | 0.1236 | 0.42114 | 0.45776 | 121.5866 | 122.3511 | -0.013733 | 122.5021 | 4.628 | -0.18768 | 122.3511 | -0.013733 | 4.628 | 121.5866 | 122.5021 | -122.4197 | -122.4701
3560.2656 | 122.4289 | -0.07782 | 122.2321 | 0.061417 | 0.011337 | -0.0149 | 0.014467 | 0.050968 | -0.015876 | 0.064339 | -0.050354 | 122.2824 | -0.19226 | 0.027466 | 121.5363 | 4.6234 | 0.43945 | 0.4715 | 122.4655 | -0.22888 | -0.11444 | 0.050354 | 0.027466 | 0.10529 | -0.6958 | -0.15106 | 0.23346 | 0.14191 | 0.51727 | 0.54932 | 121.6141 | 122.3602 | 0.027466 | 122.5433 | 4.7012 | -0.15106 | 122.3602 | 0.027466 | 4.7012 | 121.6141 | 122.5433 | -122.4243 | -122.4609
3562.0156 | 122.4152 | -0.07782 | 122.2412 | 0.1606 | 0.0068508 | -0.020454 | 0.012544 | 0.047978 | -0.0094678 | 0.066262 | 0.045776 | 122.2824 | -0.16022 | 0.13733 | 121.6415 | 4.7058 | 0.18768 | 0.54932 | 122.4106 | -0.19684 | -0.082397 | 0.041199 | 0.1236 | 0.21515 | -0.59967 | -0.11902 | 0.16937 | 0.20599 | 0.2655 | 0.62714 | 121.7194 | 122.3602 | 0.1236 | 122.4884 | 4.7836 | -0.11902 | 122.3602 | 0.1236 | 4.7836 | 121.7194 | 122.4884 | -122.4014 | -122.438
3563.7812 | 122.3373 | -0.11902 | 122.2778 | -0.21324 | 0.0098416 | -0.013618 | 0.007417 | 0.045414 | -0.01139 | 0.064766 | 0.054932 | 122.2916 | -0.15564 | 0.15564 | 121.669 | 4.8798 | 0.56763 | 0.89264 | 122.3877 | -0.20599 | -0.036621 | 0.013733 | 0.17395 | 0.27466 | -0.60883 | -0.086975 | 0.10986 | 0.21057 | 0.68665 | 1.0117 | 121.788 | 122.4106 | 0.17395 | 122.5067 | 4.9988 | -0.086975 | 122.4106 | 0.17395 | 4.9988 | 121.788 | 122.5067 | -122.4335 | -122.4838
3565.4844 | 122.3877 | -0.086975 | 122.2549 | -0.25902 | 0.0087734 | -0.012337 | 0.011476 | 0.045841 | -0.010963 | 0.06733 | -0.059509 | 122.2824 | -0.19226 | 0.032043 | 121.5454 | 4.7836 | 0.75531 | 0.77362 | 122.4564 | -0.27008 | -0.10529 | 0.027466 | 0.027466 | 0.11902 | -0.70953 | -0.18311 | 0.20142 | 0.13275 | 0.84229 | 0.8606 | 121.6324 | 122.3694 | 0.027466 | 122.5433 | 4.8706 | -0.18311 | 122.3694 | 0.027466 | 4.8706 | 121.6324 | 122.5433 | -122.4472 | -122.525
3567.25 | 122.4335 | -0.054932 | 122.2183 | 0.17586 | 0.010269 | -0.01255 | 0.014467 | 0.049687 | -0.013954 | 0.063912 | -0.013733 | 122.3053 | -0.17853 | 0.09613 | 121.5866 | 4.6738 | 0.24261 | 0.4715 | 122.438 | -0.21973 | -0.1236 | 0.086975 | 0.041199 | 0.15106 | -0.63171 | -0.16479 | 0.21973 | 0.16479 | 0.29755 | 0.52643 | 121.6415 | 122.3602 | 0.041199 | 122.493 | 4.7287 | -0.16479 | 122.3602 | 0.041199 | 4.7287 | 121.6415 | 122.493 | -122.3969 | -122.4381
3569 | 122.4426 | -0.050354 | 122.2595 | -0.053024 | 0.007919 | -0.014687 | 0.0059216 | 0.046055 | -0.012245 | 0.066048 | 0.009155 | 122.3145 | -0.13733 | 0.12817 | 121.6461 | 4.8111 | 0.46692 | 0.75073 | 122.4014 | -0.21515 | -0.086975 | 0.054932 | 0.059509 | 0.17853 | -0.6134 | -0.16479 | 0.14191 | 0.14648 | 0.51727 | 0.80109 | 121.6965 | 122.3648 | 0.059509 | 122.4518 | 4.8614 | -0.16479 | 122.3648 | 0.059509 | 4.8614 | 121.6965 | 122.4518 | -122.3969 | -122.4747
3570.7031 | 122.3328 | -0.091553 | 122.2595 | -0.083542 | 0.0092008 | -0.014046 | 0.015962 | 0.048619 | -0.015876 | 0.066689 | -0.004578 | 122.3007 | -0.19684 | 0.10986 | 121.582 | 4.8248 | 0.51727 | 0.66834 | 122.4564 | -0.24261 | -0.10529 | 0.041199 | 0.086975 | 0.20142 | -0.67749 | -0.15106 | 0.19684 | 0.19226 | 0.60883 | 0.75989 | 121.6736 | 122.3923 | 0.086975 | 122.5479 | 4.9164 | -0.15106 | 122.3923 | 0.086975 | 4.9164 | 121.6736 | 122.5479 | -122.4564 | -122.5021
3572.4688 | 122.4609 | -0.059509 | 122.2458 | 0.061417 | 0.0098416 | -0.0089189 | 0.015107 | 0.047978 | -0.015663 | 0.066902 | -0.050354 | 122.3099 | -0.19226 | 0.022888 | 121.5225 | 4.6829 | 0.44403 | 0.45319 | 122.5113 | -0.24719 | -0.13275 | 0.064086 | 0.009155 | 0.082397 | -0.72327 | -0.18768 | 0.2655 | 0.14191 | 0.50354 | 0.5127 | 121.582 | 122.3694 | 0.009155 | 122.5708 | 4.7424 | -0.18768 | 122.3694 | 0.009155 | 4.7424 | 121.582 | 122.5708 | -122.4381 | -122.493
3574.1719 | 122.4701 | -0.041199 | 122.2458 | 0.11482 | 0.010482 | -0.013832 | 0.013185 | 0.048832 | -0.011604 | 0.065621 | -0.041199 | 122.3373 | -0.18768 | 0.036621 | 121.5317 | 4.6875 | 0.36163 | 0.42572 | 122.4518 | -0.23346 | -0.14648 | 0.091552 | 0 | 0.07782 | -0.71411 | -0.19226 | 0.20599 | 0.14648 | 0.40283 | 0.46692 | 121.5729 | 122.3785 | 0 | 122.493 | 4.7287 | -0.19226 | 122.3785 | 0 | 4.7287 | 121.5729 | 122.493 | -122.4335 | -122.4792
3575.9375 | 122.4701 | -0.036621 | 122.2778 | -0.030136 | 0.0092008 | -0.014259 | 0.0042126 | 0.046269 | -0.0096814 | 0.067757 | 0.009155 | 122.3053 | -0.16937 | 0.09613 | 121.6232 | 4.8523 | 0.46692 | 0.72327 | 122.4106 | -0.2243 | -0.13275 | 0.027466 | 0.045776 | 0.13275 | -0.6546 | -0.18768 | 0.13275 | 0.17853 | 0.50354 | 0.75989 | 121.6599 | 122.3419 | 0.045776 | 122.4472 | 4.8889 | -0.18768 | 122.3419 | 0.045776 | 4.8889 | 121.6599 | 122.4472 | -122.4472 | -122.5021
3577.625 | 122.3328 | -0.091553 | 122.287 | -0.13695 | 0.0092008 | -0.011909 | 0.016389 | 0.047978 | -0.013527 | 0.067543 | -0.004578 | 122.3099 | -0.20599 | 0.10071 | 121.5866 | 4.8935 | 0.57678 | 0.72784 | 122.438 | -0.23346 | -0.11444 | 0.022888 | 0.086975 | 0.19226 | -0.70038 | -0.14191 | 0.15106 | 0.20142 | 0.66834 | 0.8194 | 121.6782 | 122.4014 | 0.086975 | 122.5296 | 4.985 | -0.14191 | 122.4014 | 0.086975 | 4.985 | 121.6782 | 122.5296 | -122.493 | -122.5204
3579.375 | 122.3602 | -0.086975 | 122.2458 | -0.045395 | 0.0077054 | -0.010628 | 0.016603 | 0.050755 | -0.014381 | 0.066475 | 0.004578 | 122.2916 | -0.1831 | 0.086975 | 121.5637 | 4.8431 | 0.46692 | 0.59052 | 122.4701 | -0.22888 | -0.09613 | 0.045776 | 0.091553 | 0.17395 | -0.68207 | -0.14191 | 0.2243 | 0.18768 | 0.55389 | 0.67749 | 121.6507 | 122.3785 | 0.091553 | 122.5571 | 4.9301 | -0.14191 | 122.3785 | 0.091553 | 4.9301 | 121.6507 | 122.5571 | -122.4289 | -122.4747
3581.1406 | 122.4289 | -0.068665 | 122.2549 | 0.13771 | 0.0081326 | -0.014259 | 0.0095532 | 0.049259 | -0.011818 | 0.066902 | 0.068665 | 122.2961 | -0.13733 | 0.14191 | 121.6507 | 4.8477 | 0.21515 | 0.59052 | 122.4106 | -0.20599 | -0.068664 | 0.041199 | 0.13733 | 0.21057 | -0.60425 | -0.13733 | 0.15564 | 0.20599 | 0.28381 | 0.65918 | 121.7194 | 122.3648 | 0.13733 | 122.4792 | 4.9164 | -0.13733 | 122.3648 | 0.13733 | 4.9164 | 121.7194 | 122.4792 | -122.3923 | -122.4609
3582.8594 | 122.3557 | -0.10071 | 122.2824 | -0.14458 | 0.0085598 | -0.012764 | 0.009126 | 0.047978 | -0.012031 | 0.066262 | 0.045776 | 122.2824 | -0.14648 | 0.17395 | 121.6782 | 4.9896 | 0.5127 | 0.86975 | 122.4197 | -0.19684 | -0.045776 | 0 | 0.14648 | 0.27466 | -0.60425 | -0.09613 | 0.13733 | 0.19226 | 0.6134 | 0.97046 | 121.7789 | 122.3831 | 0.14648 | 122.5204 | 5.0903 | -0.09613 | 122.3831 | 0.14648 | 5.0903 | 121.7789 | 122.5204 | -122.4289 | -122.4792
3584.6406 | 122.4472 | -0.050354 | 122.2275 | 0.15297 | 0.0087734 | -0.011269 | 0.01468 | 0.049687 | -0.013954 | 0.066048 | -0.013733 | 122.3053 | -0.18768 | 0.091553 | 121.5729 | 4.7836 | 0.28381 | 0.4715 | 122.4792 | -0.21973 | -0.13733 | 0.07782 | 0.036621 | 0.14191 | -0.6546 | -0.16937 | 0.25177 | 0.17395 | 0.33417 | 0.52185 | 121.6232 | 122.3557 | 0.036621 | 122.5296 | 4.834 | -0.16937 | 122.3557 | 0.036621 | 4.834 | 121.6232 | 122.5296 | -122.4152 | -122.4472
3586.3906 | 122.3465 | -0.09613 | 122.2778 | -0.075912 | 0.0066372 | -0.01255 | 0.012544 | 0.049046 | -0.013099 | 0.066048 | 0.018311 | 122.2778 | -0.18768 | 0.10986 | 121.5912 | 4.9164 | 0.50354 | 0.65002 | 122.4564 | -0.2243 | -0.091553 | 0 | 0.11444 | 0.20599 | -0.68664 | -0.12817 | 0.17853 | 0.20599 | 0.59967 | 0.74615 | 121.6873 | 122.374 | 0.11444 | 122.5525 | 5.0125 | -0.12817 | 122.374 | 0.11444 | 5.0125 | 121.6873 | 122.5525 | -122.4655 | -122.5021
3588.1562 | 122.4884 | -0.064087 | 122.2321 | 0.02327 | 0.0085598 | -0.011269 | 0.0063488 | 0.047764 | -0.014595 | 0.066689 | 0.018311 | 122.3053 | -0.16937 | 0.10071 | 121.6187 | 4.8798 | 0.3891 | 0.62256 | 122.4335 | -0.19226 | -0.10529 | 0.073242 | 0.082398 | 0.1648 | -0.6134 | -0.12817 | 0.20142 | 0.18768 | 0.45319 | 0.68665 | 121.6827 | 122.3694 | 0.082398 | 122.4976 | 4.9438 | -0.12817 | 122.3694 | 0.082398 | 4.9438 | 121.6827 | 122.4976 | -122.4014 | -122.4243
3589.8594 | 122.3328 | -0.10071 | 122.2733 | -0.091171 | 0.0098416 | -0.013618 | 0.015748 | 0.049687 | -0.012672 | 0.066689 | -0.009155 | 122.2824 | -0.20599 | 0.11444 | 121.5958 | 4.9667 | 0.51727 | 0.67291 | 122.4289 | -0.21515 | -0.10529 | 0.009156 | 0.091553 | 0.21515 | -0.67749 | -0.11444 | 0.15564 | 0.19684 | 0.61798 | 0.77362 | 121.6965 | 122.3831 | 0.091553 | 122.5296 | 5.0674 | -0.11444 | 122.3831 | 0.091553 | 5.0674 | 121.6965 | 122.5296 | -122.4792 | -122.4884
3591.6094 | 122.3877 | -0.068665 | 122.2641 | -0.12932 | 0.0092008 | -0.018104 | 0.0099804 | 0.044987 | -0.011818 | 0.066689 | -0.050354 | 122.3145 | -0.19226 | 0.059509 | 121.5683 | 4.9805 | 0.74158 | 0.78278 | 122.4747 | -0.25177 | -0.1236 | 0.050354 | 0.018311 | 0.12817 | -0.6958 | -0.1831 | 0.21057 | 0.14191 | 0.81024 | 0.85144 | 121.637 | 122.3831 | 0.018311 | 122.5433 | 5.0491 | -0.1831 | 122.3831 | 0.018311 | 5.0491 | 121.637 | 122.5433 | -122.4564 | -122.5159
3593.375 | 122.3831 | -0.082397 | 122.2595 | -0.22087 | 0.0077054 | -0.012337 | 0.01233 | 0.048191 | -0.012031 | 0.065621 | -0.064087 | 122.2961 | -0.2243 | 0.050354 | 121.55 | 4.9896 | 0.76904 | 0.76446 | 122.4884 | -0.22888 | -0.14191 | 0.036622 | 0.01831 | 0.13275 | -0.70953 | -0.14649 | 0.22888 | 0.16022 | 0.85144 | 0.84686 | 121.6324 | 122.3785 | 0.01831 | 122.5708 | 5.072 | -0.14649 | 122.3785 | 0.01831 | 5.072 | 121.6324 | 122.5708 | -122.4838 | -122.4884
3595.1406 | 122.4243 | -0.054932 | 122.2321 | 0.12245 | 0.0092008 | -0.012978 | 0.0086988 | 0.047123 | -0.010322 | 0.066048 | 0.059509 | 122.2916 | -0.14648 | 0.13275 | 121.6415 | 4.9438 | 0.23804 | 0.59509 | 122.4014 | -0.20142 | -0.091552 | 0.059509 | 0.11444 | 0.18768 | -0.59051 | -0.14648 | 0.16937 | 0.20599 | 0.29297 | 0.65002 | 121.6965 | 122.3465 | 0.11444 | 122.4564 | 4.9988 | -0.14648 | 122.3465 | 0.11444 | 4.9988 | 121.6965 | 122.4564 | -122.3785 | -122.4335
3596.9062 | 122.3373 | -0.10529 | 122.2733 | -0.17509 | 0.0068508 | -0.014259 | 0.0099804 | 0.044773 | -0.012886 | 0.067116 | 0.050354 | 122.2916 | -0.15564 | 0.16937 | 121.6599 | 5.0949 | 0.56763 | 0.91095 | 122.4106 | -0.20599 | -0.050354 | 0.018311 | 0.15564 | 0.27466 | -0.6134 | -0.10071 | 0.13733 | 0.20599 | 0.67291 | 1.0162 | 121.7651 | 122.3969 | 0.15564 | 122.5159 | 5.2002 | -0.10071 | 122.3969 | 0.15564 | 5.2002 | 121.7651 | 122.5159 | -122.4289 | -122.4792
3598.6094 | 122.4976 | -0.054932 | 122.2458 | 0.0080111 | 0.010055 | -0.013832 | 0.010408 | 0.046269 | -0.010963 | 0.066048 | 0.004578 | 122.3007 | -0.15106 | 0.10529 | 121.5958 | 4.9667 | 0.42114 | 0.66834 | 122.4014 | -0.20599 | -0.09613 | 0.054931 | 0.05951 | 0.16022 | -0.65002 | -0.15106 | 0.15564 | 0.15564 | 0.47607 | 0.72327 | 121.6507 | 122.3557 | 0.05951 | 122.4564 | 5.0217 | -0.15106 | 122.3557 | 0.05951 | 5.0217 | 121.6507 | 122.4564 | -122.3969 | -122.4518
3600.3594 | 122.3511 | -0.07782 | 122.2778 | -0.14458 | 0.0087734 | -0.012337 | 0.0089124 | 0.044987 | -0.01374 | 0.064553 | 0.059509 | 122.2916 | -0.15106 | 0.16937 | 121.6644 | 5.1132 | 0.48981 | 0.8606 | 122.4289 | -0.21057 | -0.073242 | 0.013733 | 0.13733 | 0.24719 | -0.6134 | -0.13275 | 0.15106 | 0.21057 | 0.56763 | 0.93842 | 121.7422 | 122.3694 | 0.13733 | 122.5067 | 5.191 | -0.13275 | 122.3694 | 0.13733 | 5.191 | 121.7422 | 122.5067 | -122.4289 | -122.4884
3602.125 | 122.3877 | -0.09613 | 122.287 | -0.19035 | 0.0081326 | -0.012764 | 0.014894 | 0.048619 | -0.015663 | 0.065621 | -0.054932 | 122.287 | -0.18768 | 0.068665 | 121.55 | 5.0491 | 0.72784 | 0.75073 | 122.4701 | -0.21973 | -0.091553 | 0 | 0.041198 | 0.16479 | -0.737 | -0.1236 | 0.18311 | 0.13275 | 0.82397 | 0.84686 | 121.6461 | 122.3831 | 0.041198 | 122.5662 | 5.1453 | -0.1236 | 122.3831 | 0.041198 | 5.1453 | 121.6461 | 122.5662 | -122.4747 | -122.5067
3603.8906 | 122.4976 | -0.064087 | 122.2366 | 0.0080111 | 0.011551 | -0.010414 | 0.0097668 | 0.047337 | -0.010322 | 0.067543 | 0 | 122.3007 | -0.15106 | 0.10529 | 121.6095 | 4.9942 | 0.42572 | 0.65918 | 122.4106 | -0.20599 | -0.086975 | 0.064087 | 0.064087 | 0.16937 | -0.62714 | -0.14191 | 0.17395 | 0.15106 | 0.48981 | 0.72327 | 121.6736 | 122.3648 | 0.064087 | 122.4747 | 5.0583 | -0.14191 | 122.3648 | 0.064087 | 5.0583 | 121.6736 | 122.4747 | -122.3877 | -122.4426
3605.6406 | 122.4792 | -0.059509 | 122.2595 | 0.038529 | 0.0094144 | -0.014473 | 0.012117 | 0.045841 | -0.013099 | 0.066902 | 0.018311 | 122.2916 | -0.14191 | 0.12817 | 121.6003 | 4.9942 | 0.34332 | 0.61798 | 122.4014 | -0.2243 | -0.082398 | 0.032044 | 0.07782 | 0.18768 | -0.65918 | -0.16479 | 0.14191 | 0.16022 | 0.40283 | 0.67749 | 121.6599 | 122.3511 | 0.07782 | 122.4609 | 5.0537 | -0.16479 | 122.3511 | 0.07782 | 5.0537 | 121.6599 | 122.4609 | -122.4014 | -122.4838
3607.4062 | 122.3465 | -0.10986 | 122.287 | -0.11406 | 0.0085598 | -0.010414 | 0.011049 | 0.04755 | -0.010109 | 0.066262 | 0.07782 | 122.2824 | -0.13733 | 0.19226 | 121.6827 | 5.1727 | 0.54474 | 0.89722 | 122.4152 | -0.18768 | -0.027466 | -0.004577 | 0.18768 | 0.30212 | -0.60425 | -0.07782 | 0.12817 | 0.21515 | 0.6546 | 1.0071 | 121.7926 | 122.3923 | 0.18768 | 122.525 | 5.2826 | -0.07782 | 122.3923 | 0.18768 | 5.2826 | 121.7926 | 122.525 | -122.4243 | -122.4747
3609.1094 | 122.4335 | -0.050354 | 122.2412 | -0.075912 | 0.0094144 | -0.01725 | 0.010621 | 0.044132 | -0.01075 | 0.065621 | 0.018311 | 122.2733 | -0.16479 | 0.14648 | 121.6415 | 5.127 | 0.49439 | 0.81024 | 122.4289 | -0.21057 | -0.11444 | 0.032043 | 0.068665 | 0.19684 | -0.59967 | -0.16022 | 0.18768 | 0.18311 | 0.54474 | 0.8606 | 121.6919 | 122.3236 | 0.068665 | 122.4792 | 5.1773 | -0.16022 | 122.3236 | 0.068665 | 5.1773 | 121.6919 | 122.4792 | -122.406 | -122.4518
3610.8594 | 122.4792 | -0.050354 | 122.2549 | 0.00038159 | 0.007919 | -0.015968 | 0.011903 | 0.045628 | -0.010109 | 0.065407 | -0.004578 | 122.3145 | -0.17853 | 0.10529 | 121.6049 | 5.0812 | 0.46234 | 0.70496 | 122.4152 | -0.22888 | -0.12817 | 0.059509 | 0.045776 | 0.15564 | -0.65002 | -0.17853 | 0.16022 | 0.17395 | 0.5127 | 0.75531 | 121.6553 | 122.3648 | 0.045776 | 122.4655 | 5.1315 | -0.17853 | 122.3648 | 0.045776 | 5.1315 | 121.6553 | 122.4655 | -122.4335 | -122.4838
3612.6094 | 122.3923 | -0.11444 | 122.2504 | -0.26665 | 0.0092008 | -0.010414 | 0.01468 | 0.047764 | -0.012672 | 0.065621 | 0.032043 | 122.3145 | -0.16022 | 0.11444 | 121.6003 | 5.191 | 0.69122 | 0.84686 | 122.4518 | -0.23346 | -0.045776 | 0.064087 | 0.14648 | 0.22888 | -0.65002 | -0.11902 | 0.20142 | 0.19226 | 0.80566 | 0.9613 | 121.7148 | 122.4289 | 0.14648 | 122.5662 | 5.3055 | -0.11902 | 122.4289 | 0.14648 | 5.3055 | 121.7148 | 122.5662 | -122.4106 | -122.4838
3614.3125 | 122.4701 | -0.045776 | 122.2412 | 0.10719 | 0.0087734 | -0.01255 | 0.016816 | 0.046482 | -0.013527 | 0.06498 | -0.045776 | 122.3053 | -0.19684 | 0.054932 | 121.5179 | 4.9713 | 0.39368 | 0.44861 | 122.4701 | -0.24719 | -0.15106 | 0.064087 | 0 | 0.10071 | -0.72327 | -0.20142 | 0.22888 | 0.15106 | 0.43945 | 0.49438 | 121.5637 | 122.3511 | 0 | 122.5159 | 5.0171 | -0.20142 | 122.3511 | 0 | 5.0171 | 121.5637 | 122.5159 | -122.438 | -122.4884
3616.0781 | 122.3877 | -0.086975 | 122.2687 | -0.2285 | 0.0077054 | -0.015755 | 0.013826 | 0.050114 | -0.015663 | 0.064553 | -0.054932 | 122.3007 | -0.20142 | 0.064087 | 121.55 | 5.159 | 0.737 | 0.75073 | 122.4655 | -0.22888 | -0.11444 | 0.032043 | 0.032043 | 0.15106 | -0.71869 | -0.14191 | 0.19684 | 0.14648 | 0.82398 | 0.83771 | 121.637 | 122.3877 | 0.032043 | 122.5525 | 5.246 | -0.14191 | 122.3877 | 0.032043 | 5.246 | 121.637 | 122.5525 | -122.4701 | -122.4976
3617.8281 | 122.3969 | -0.068665 | 122.2458 | -0.25139 | 0.0089872 | -0.013405 | 0.014039 | 0.046269 | -0.013313 | 0.066902 | -0.059509 | 122.319 | -0.18768 | 0.050354 | 121.5546 | 5.1636 | 0.76446 | 0.7782 | 122.4472 | -0.25635 | -0.11902 | 0.073242 | 0.009156 | 0.11902 | -0.69122 | -0.18768 | 0.20142 | 0.12817 | 0.83313 | 0.84686 | 121.6232 | 122.3877 | 0.009156 | 122.5159 | 5.2322 | -0.18768 | 122.3877 | 0.009156 | 5.2322 | 121.6232 | 122.5159 | -122.4335 | -122.5021
3619.5938 | 122.4609 | -0.041199 | 122.2412 | 0.14534 | 0.011123 | -0.010841 | 0.015748 | 0.046055 | -0.01374 | 0.066048 | -0.045776 | 122.3282 | -0.19226 | 0.041199 | 121.5317 | 5.0217 | 0.37537 | 0.44861 | 122.438 | -0.25177 | -0.15106 | 0.086975 | -0.004577 | 0.082398 | -0.70953 | -0.21057 | 0.19684 | 0.14648 | 0.41656 | 0.48981 | 121.5729 | 122.3694 | -0.004577 | 122.4792 | 5.0629 | -0.21057 | 122.3694 | -0.004577 | 5.0629 | 121.5729 | 122.4792 | -122.4335 | -122.493
3621.3594 | 122.4335 | -0.059509 | 122.2412 | 0.1606 | 0.0085598 | -0.010628 | 0.012544 | 0.049259 | -0.011177 | 0.065407 | 0.018311 | 122.2824 | -0.16479 | 0.13733 | 121.6324 | 5.1315 | 0.23804 | 0.55847 | 122.3969 | -0.20599 | -0.10529 | 0.041199 | 0.07782 | 0.19684 | -0.60883 | -0.14649 | 0.15564 | 0.18311 | 0.29755 | 0.61798 | 121.6919 | 122.3419 | 0.07782 | 122.4564 | 5.191 | -0.14649 | 122.3419 | 0.07782 | 5.191 | 121.6919 | 122.4564 | -122.406 | -122.4472
3623.125 | 122.3511 | -0.086975 | 122.2916 | -0.14458 | 0.0081326 | -0.011269 | 0.01233 | 0.048832 | -0.013954 | 0.064125 | -0.027466 | 122.2824 | -0.20599 | 0.091553 | 121.582 | 5.2414 | 0.62256 | 0.74158 | 122.4289 | -0.23346 | -0.11902 | -0.009155 | 0.059509 | 0.17853 | -0.70953 | -0.14648 | 0.13733 | 0.17853 | 0.70953 | 0.82855 | 121.669 | 122.3694 | 0.059509 | 122.5159 | 5.3284 | -0.14648 | 122.3694 | 0.059509 | 5.3284 | 121.669 | 122.5159 | -122.4976 | -122.525
3624.8281 | 122.4197 | -0.050354 | 122.2641 | 0.13771 | 0.0085598 | -0.013832 | 0.0099804 | 0.048405 | -0.011818 | 0.069039 | 0.050354 | 122.3007 | -0.13733 | 0.15106 | 121.6507 | 5.159 | 0.23804 | 0.59967 | 122.406 | -0.21973 | -0.086975 | 0.036621 | 0.10071 | 0.20142 | -0.6134 | -0.16937 | 0.14191 | 0.18768 | 0.28839 | 0.65002 | 121.701 | 122.3511 | 0.10071 | 122.4564 | 5.2094 | -0.16937 | 122.3511 | 0.10071 | 5.2094 | 121.701 | 122.4564 | -122.4014 | -122.4838
3626.5781 | 122.4701 | -0.041199 | 122.2458 | 0.01564 | 0.011123 | -0.014473 | 0.0069898 | 0.044346 | -0.009895 | 0.066689 | -0.009155 | 122.319 | -0.14648 | 0.086975 | 121.6095 | 5.1865 | 0.47607 | 0.70038 | 122.4289 | -0.20599 | -0.10529 | 0.073242 | 0.032044 | 0.12817 | -0.63629 | -0.1648 | 0.1831 | 0.13733 | 0.51727 | 0.74158 | 121.6507 | 122.3602 | 0.032044 | 122.4701 | 5.2277 | -0.1648 | 122.3602 | 0.032044 | 5.2277 | 121.6507 | 122.4701 | -122.3923 | -122.4518
3628.3281 | 122.4655 | -0.064087 | 122.2458 | 0.10719 | 0.0092008 | -0.013618 | 0.0095532 | 0.046696 | -0.011177 | 0.064125 | 0.032043 | 122.2916 | -0.16479 | 0.1236 | 121.6095 | 5.1727 | 0.35248 | 0.62714 | 122.4289 | -0.20599 | -0.10071 | 0.045776 | 0.09613 | 0.18768 | -0.63629 | -0.14191 | 0.1831 | 0.19684 | 0.41657 | 0.69122 | 121.6736 | 122.3557 | 0.09613 | 122.493 | 5.2368 | -0.14191 | 122.3557 | 0.09613 | 5.2368 | 121.6736 | 122.493 | -122.4106 | -122.4518
3630.0938 | 122.3465 | -0.091553 | 122.2641 | -0.075912 | 0.010055 | -0.012978 | 0.015535 | 0.047337 | -0.013313 | 0.066475 | 0.009155 | 122.2733 | -0.18768 | 0.12817 | 121.5775 | 5.246 | 0.50812 | 0.68207 | 122.438 | -0.21057 | -0.09613 | 0.009155 | 0.10071 | 0.21973 | -0.68664 | -0.11902 | 0.17395 | 0.19684 | 0.59967 | 0.77362 | 121.669 | 122.3648 | 0.10071 | 122.5296 | 5.3375 | -0.11902 | 122.3648 | 0.10071 | 5.3375 | 121.669 | 122.5296 | -122.4518 | -122.4747
3631.7969 | 122.3969 | -0.10529 | 122.2687 | -0.21324 | 0.010055 | -0.010414 | 0.011689 | 0.046696 | -0.012672 | 0.065621 | -0.054932 | 122.3328 | -0.19684 | 0.059509 | 121.55 | 5.2734 | 0.76904 | 0.78278 | 122.4564 | -0.24719 | -0.091552 | 0.064087 | 0.050354 | 0.16479 | -0.71869 | -0.14191 | 0.18768 | 0.14191 | 0.87433 | 0.88806 | 121.6553 | 122.4381 | 0.050354 | 122.5616 | 5.3787 | -0.14191 | 122.4381 | 0.050354 | 5.3787 | 121.6553 | 122.5616 | -122.4655 | -122.5159
3633.5625 | 122.3831 | -0.073242 | 122.2824 | -0.25902 | 0.0074918 | -0.015114 | 0.012117 | 0.047123 | -0.016517 | 0.06498 | -0.068665 | 122.2961 | -0.20142 | 0.050354 | 121.5546 | 5.2917 | 0.78278 | 0.78278 | 122.4609 | -0.26093 | -0.12817 | 0.013733 | 0.004577 | 0.1236 | -0.72785 | -0.18768 | 0.17853 | 0.13275 | 0.85602 | 0.85602 | 121.6278 | 122.3694 | 0.004577 | 122.5342 | 5.365 | -0.18768 | 122.3694 | 0.004577 | 5.365 | 121.6278 | 122.5342 | -122.4838 | -122.5433
3635.3281 | 122.3694 | -0.10071 | 122.3007 | -0.17509 | 0.007919 | -0.013618 | 0.010835 | 0.047123 | -0.01374 | 0.063484 | 0.050354 | 122.2824 | -0.15564 | 0.16022 | 121.6644 | 5.4016 | 0.62256 | 0.90637 | 122.4197 | -0.21057 | -0.054932 | -0.01831 | 0.15106 | 0.26093 | -0.63629 | -0.10986 | 0.11902 | 0.20599 | 0.72327 | 1.0071 | 121.7651 | 122.3831 | 0.15106 | 122.5204 | 5.5023 | -0.10986 | 122.3831 | 0.15106 | 5.5023 | 121.7651 | 122.5204 | -122.4564 | -122.5113
3637.0781 | 122.4655 | -0.068665 | 122.2137 | 0.0080111 | 0.0087734 | -0.0093461 | 0.0080578 | 0.047123 | -0.010536 | 0.065407 | -0.009155 | 122.2961 | -0.16937 | 0.10986 | 121.6141 | 5.2689 | 0.48523 | 0.71869 | 122.4243 | -0.19684 | -0.10071 | 0.082398 | 0.05951 | 0.17853 | -0.59967 | -0.12817 | 0.21057 | 0.16022 | 0.55389 | 0.78735 | 121.6827 | 122.3648 | 0.05951 | 122.493 | 5.3375 | -0.12817 | 122.3648 | 0.05951 | 5.3375 | 121.6827 | 122.493 | -122.3831 | -122.4106
3638.8281 | 122.4518 | -0.050354 | 122.2687 | -0.045395 | 0.0094144 | -0.012764 | 0.0095532 | 0.046696 | -0.0096814 | 0.067116 | 0.022888 | 122.3145 | -0.16937 | 0.12817 | 121.6553 | 5.3284 | 0.5127 | 0.79193 | 122.4335 | -0.2243 | -0.11902 | 0.045776 | 0.073242 | 0.17853 | -0.6134 | -0.17395 | 0.16479 | 0.19226 | 0.56305 | 0.84229 | 121.7056 | 122.3648 | 0.073242 | 122.4838 | 5.3787 | -0.17395 | 122.3648 | 0.073242 | 5.3787 | 121.7056 | 122.4838 | -122.438 | -122.493
3640.5938 | 122.4335 | -0.054932 | 122.2412 | 0.19112 | 0.007919 | -0.012123 | 0.016389 | 0.04755 | -0.013527 | 0.066902 | 0.013733 | 122.2778 | -0.1831 | 0.13275 | 121.6141 | 5.246 | 0.2655 | 0.54016 | 122.4518 | -0.17853 | -0.12817 | 0.036621 | 0.068665 | 0.18768 | -0.62714 | -0.1236 | 0.21057 | 0.19684 | 0.32043 | 0.59509 | 121.669 | 122.3328 | 0.068665 | 122.5067 | 5.3009 | -0.1236 | 122.3328 | 0.068665 | 5.3009 | 121.669 | 122.5067 | -122.4243 | -122.4197
3642.2812 | 122.3557 | -0.082397 | 122.2916 | -0.15984 | 0.0081326 | -0.012123 | 0.010194 | 0.04691 | -0.011604 | 0.066689 | 0.050354 | 122.2641 | -0.15106 | 0.16479 | 121.6599 | 5.4337 | 0.62714 | 0.9201 | 122.406 | -0.21057 | -0.068665 | -0.027466 | 0.13275 | 0.24719 | -0.63171 | -0.12817 | 0.11444 | 0.20142 | 0.70953 | 1.0025 | 121.7422 | 122.3465 | 0.13275 | 122.4884 | 5.5161 | -0.12817 | 122.3465 | 0.13275 | 5.5161 | 121.7422 | 122.4884 | -122.4426 | -122.5021
3644.0469 | 122.3831 | -0.07782 | 122.2824 | 0.01564 | 0.0066372 | -0.010414 | 0.017671 | 0.049473 | -0.012672 | 0.06498 | -0.018311 | 122.2961 | -0.19226 | 0.073242 | 121.5408 | 5.2597 | 0.47607 | 0.56305 | 122.4426 | -0.22888 | -0.11444 | 0.013733 | 0.059509 | 0.15106 | -0.74158 | -0.15106 | 0.16022 | 0.17395 | 0.55389 | 0.64087 | 121.6187 | 122.374 | 0.059509 | 122.5204 | 5.3375 | -0.15106 | 122.374 | 0.059509 | 5.3375 | 121.6187 | 122.5204 | -122.4747 | -122.5113
3645.8125 | 122.4747 | -0.022888 | 122.2595 | 0.10719 | 0.0098416 | -0.010841 | 0.012544 | 0.04755 | -0.01374 | 0.066048 | -0.041199 | 122.3053 | -0.17853 | 0.036621 | 121.5454 | 5.2231 | 0.39368 | 0.46692 | 122.4609 | -0.24261 | -0.15564 | 0.045777 | -0.018311 | 0.059509 | -0.71411 | -0.21973 | 0.20142 | 0.13733 | 0.41657 | 0.48981 | 121.5683 | 122.3282 | -0.018311 | 122.4838 | 5.246 | -0.21973 | 122.3282 | -0.018311 | 5.246 | 121.5683 | 122.4838 | -122.438 | -122.5021
3647.5156 | 122.4289 | -0.045776 | 122.2641 | 0.061417 | 0.0098416 | -0.011269 | 0.014894 | 0.048405 | -0.014167 | 0.066048 | 0.041199 | 122.2733 | -0.15106 | 0.15106 | 121.6415 | 5.3238 | 0.24261 | 0.58136 | 122.4335 | -0.20142 | -0.10529 | 0.009155 | 0.086975 | 0.19684 | -0.62256 | -0.15564 | 0.16937 | 0.19226 | 0.28839 | 0.62714 | 121.6873 | 122.319 | 0.086975 | 122.4792 | 5.3696 | -0.15564 | 122.319 | 0.086975 | 5.3696 | 121.6873 | 122.4792 | -122.4152 | -122.4655
3649.2812 | 122.4518 | -0.050354 | 122.2321 | 0.11482 | 0.010482 | -0.010414 | 0.016603 | 0.049259 | -0.012672 | 0.068398 | -0.027466 | 122.3145 | -0.1831 | 0.068665 | 121.5729 | 5.2597 | 0.31128 | 0.49439 | 122.438 | -0.21057 | -0.13275 | 0.082397 | 0.022888 | 0.11902 | -0.65918 | -0.16022 | 0.20599 | 0.15564 | 0.36163 | 0.54474 | 121.6232 | 122.3648 | 0.022888 | 122.4884 | 5.3101 | -0.16022 | 122.3648 | 0.022888 | 5.3101 | 121.6232 | 122.4884 | -122.4152 | -122.4426
3651.0469 | 122.4518 | -0.059509 | 122.2504 | 0.046158 | 0.0072782 | -0.014046 | 0.013398 | 0.049687 | -0.015236 | 0.06797 | -0.054932 | 122.3236 | -0.19684 | 0.036621 | 121.5225 | 5.2734 | 0.46234 | 0.48065 | 122.4609 | -0.23804 | -0.13733 | 0.073242 | 0.004577 | 0.09613 | -0.72784 | -0.17853 | 0.21057 | 0.14191 | 0.52185 | 0.54016 | 121.582 | 122.3831 | 0.004577 | 122.5204 | 5.3329 | -0.17853 | 122.3831 | 0.004577 | 5.3329 | 121.582 | 122.5204 | -122.4472 | -122.4884
3652.8125 | 122.4884 | -0.045776 | 122.2458 | 0.030899 | 0.009628 | -0.014687 | 0.0082714 | 0.048832 | -0.01075 | 0.065621 | -0.004578 | 122.3099 | -0.16022 | 0.09613 | 121.6278 | 5.3558 | 0.42114 | 0.66376 | 122.4335 | -0.21515 | -0.11444 | 0.064086 | 0.041198 | 0.14191 | -0.61798 | -0.16937 | 0.18768 | 0.15564 | 0.46692 | 0.70953 | 121.6736 | 122.3557 | 0.041198 | 122.4792 | 5.4016 | -0.16937 | 122.3557 | 0.041198 | 5.4016 | 121.6736 | 122.4792 | -122.406 | -122.4609
3654.5781 | 122.3511 | -0.09613 | 122.2824 | -0.12932 | 0.0081326 | -0.01255 | 0.016816 | 0.050968 | -0.014167 | 0.065621 | 0 | 122.2824 | -0.19684 | 0.10529 | 121.582 | 5.4428 | 0.59052 | 0.737 | 122.4609 | -0.20599 | -0.10071 | 0 | 0.09613 | 0.20142 | -0.70038 | -0.10986 | 0.17853 | 0.19684 | 0.68664 | 0.83313 | 121.6782 | 122.3785 | 0.09613 | 122.5571 | 5.5389 | -0.10986 | 122.3785 | 0.09613 | 5.5389 | 121.6782 | 122.5571 | -122.4792 | -122.4884
3656.2812 | 122.4289 | -0.059509 | 122.2687 | 0.15297 | 0.011764 | -0.01255 | 0.012971 | 0.05225 | -0.014167 | 0.066048 | 0.059509 | 122.3236 | -0.16022 | 0.15564 | 121.6507 | 5.397 | 0.2243 | 0.60425 | 122.4335 | -0.20599 | -0.10071 | 0.054931 | 0.11902 | 0.21515 | -0.61798 | -0.14649 | 0.16479 | 0.21973 | 0.28381 | 0.66376 | 121.7102 | 122.3831 | 0.11902 | 122.493 | 5.4565 | -0.14649 | 122.3831 | 0.11902 | 5.4565 | 121.7102 | 122.493 | -122.4289 | -122.4747
3658.0469 | 122.5067 | -0.059509 | 122.2412 | 0.0080111 | 0.0083462 | -0.012123 | 0.0080578 | 0.046055 | -0.012031 | 0.065834 | -0.009155 | 122.2824 | -0.16479 | 0.086975 | 121.5912 | 5.4108 | 0.46234 | 0.68665 | 122.4014 | -0.20599 | -0.10529 | 0.041199 | 0.050354 | 0.14648 | -0.65002 | -0.14649 | 0.16022 | 0.15564 | 0.52185 | 0.74616 | 121.6507 | 122.3419 | 0.050354 | 122.4609 | 5.4703 | -0.14649 | 122.3419 | 0.050354 | 5.4703 | 121.6507 | 122.4609 | -122.406 | -122.4472
3659.75 | 122.4472 | -0.045776 | 122.2412 | 0.099564 | 0.0092008 | -0.0149 | 0.010835 | 0.048191 | -0.013527 | 0.06498 | 0.054932 | 122.3007 | -0.16022 | 0.14191 | 121.6324 | 5.4062 | 0.28381 | 0.63171 | 122.4106 | -0.20599 | -0.11444 | 0.059509 | 0.10071 | 0.18768 | -0.60883 | -0.16022 | 0.16937 | 0.21515 | 0.32959 | 0.67749 | 121.6782 | 122.3465 | 0.10071 | 122.4564 | 5.452 | -0.16022 | 122.3465 | 0.10071 | 5.452 | 121.6782 | 122.4564 | -122.4014 | -122.4472
3661.5156 | 122.4609 | -0.041199 | 122.2275 | 0.10719 | 0.0085598 | -0.0097733 | 0.014253 | 0.048191 | -0.013527 | 0.066902 | -0.041199 | 122.2961 | -0.19684 | 0.068665 | 121.55 | 5.3467 | 0.34332 | 0.49439 | 122.4472 | -0.23346 | -0.15564 | 0.068665 | 0 | 0.10986 | -0.67749 | -0.19226 | 0.21973 | 0.15564 | 0.38452 | 0.53558 | 121.5912 | 122.3373 | 0 | 122.4884 | 5.3879 | -0.19226 | 122.3373 | 0 | 5.3879 | 121.5912 | 122.4884 | -122.4243 | -122.4609
3663.2812 | 122.3557 | -0.10529 | 122.2916 | -0.16747 | 0.011551 | -0.015114 | 0.011262 | 0.048191 | -0.013527 | 0.065621 | 0.054932 | 122.2961 | -0.14648 | 0.15564 | 121.6507 | 5.6168 | 0.62256 | 0.93842 | 122.4335 | -0.21515 | -0.041198 | 0.004578 | 0.16022 | 0.26093 | -0.64087 | -0.10986 | 0.14191 | 0.20142 | 0.72784 | 1.0437 | 121.756 | 122.4014 | 0.16022 | 122.5388 | 5.722 | -0.10986 | 122.4014 | 0.16022 | 5.722 | 121.756 | 122.5388 | -122.438 | -122.5067
3665.0469 | 122.3831 | -0.07782 | 122.2549 | -0.014877 | 0.011337 | -0.0057145 | 0.015962 | 0.050541 | -0.015876 | 0.069039 | 0 | 122.3145 | -0.18768 | 0.068665 | 121.5408 | 5.4199 | 0.49896 | 0.58136 | 122.493 | -0.21973 | -0.10986 | 0.059509 | 0.07782 | 0.14649 | -0.71411 | -0.14191 | 0.23804 | 0.18768 | 0.57678 | 0.65918 | 121.6187 | 122.3923 | 0.07782 | 122.5708 | 5.4977 | -0.14191 | 122.3923 | 0.07782 | 5.4977 | 121.6187 | 122.5708 | -122.4426 | -122.4747
3666.8125 | 122.3648 | -0.11444 | 122.2916 | -0.19035 | 0.011551 | -0.013191 | 0.012117 | 0.047764 | -0.010109 | 0.066902 | 0.036621 | 122.2961 | -0.14648 | 0.15564 | 121.6461 | 5.6076 | 0.68207 | 0.93842 | 122.438 | -0.21973 | -0.032043 | 0.004578 | 0.15106 | 0.27008 | -0.64545 | -0.10529 | 0.14648 | 0.18311 | 0.79651 | 1.0529 | 121.7606 | 122.4106 | 0.15106 | 122.5525 | 5.722 | -0.10529 | 122.4106 | 0.15106 | 5.722 | 121.7606 | 122.5525 | -122.438 | -122.5113
3668.5156 | 122.4747 | -0.054932 | 122.2321 | 0.046158 | 0.0070646 | -0.011909 | 0.0089124 | 0.047764 | -0.01139 | 0.066902 | 0.009155 | 122.2687 | -0.16479 | 0.09613 | 121.6141 | 5.4657 | 0.40283 | 0.65918 | 122.4335 | -0.20599 | -0.10986 | 0.036621 | 0.064087 | 0.15106 | -0.61798 | -0.15106 | 0.20142 | 0.17395 | 0.45776 | 0.71411 | 121.669 | 122.3236 | 0.064087 | 122.4884 | 5.5206 | -0.15106 | 122.3236 | 0.064087 | 5.5206 | 121.669 | 122.4884 | -122.3969 | -122.4381
3670.2812 | 122.3969 | -0.10071 | 122.2733 | -0.2285 | 0.0089872 | -0.013405 | 0.015321 | 0.046696 | -0.012458 | 0.066475 | -0.059509 | 122.3373 | -0.20142 | 0.054932 | 121.55 | 5.5481 | 0.76904 | 0.78735 | 122.438 | -0.25177 | -0.10071 | 0.064087 | 0.041199 | 0.15564 | -0.72327 | -0.15106 | 0.1648 | 0.14191 | 0.86975 | 0.88806 | 121.6507 | 122.438 | 0.041199 | 122.5388 | 5.6488 | -0.15106 | 122.438 | 0.041199 | 5.6488 | 121.6507 | 122.5388 | -122.4747 | -122.525
3672.0312 | 122.4014 | -0.086975 | 122.2687 | -0.25902 | 0.010055 | -0.012337 | 0.012971 | 0.044346 | -0.012886 | 0.065621 | -0.054932 | 122.3282 | -0.21057 | 0.054932 | 121.55 | 5.5664 | 0.80109 | 0.79651 | 122.4655 | -0.24719 | -0.1236 | 0.059509 | 0.032043 | 0.14191 | -0.71869 | -0.16022 | 0.19684 | 0.15564 | 0.88806 | 0.88348 | 121.637 | 122.4152 | 0.032043 | 122.5525 | 5.6534 | -0.16022 | 122.4152 | 0.032043 | 5.6534 | 121.637 | 122.5525 | -122.4792 | -122.5159
3673.7969 | 122.3923 | -0.068665 | 122.2687 | 0.069046 | 0.0092008 | -0.0078507 | 0.018098 | 0.048619 | -0.012031 | 0.068184 | -0.036621 | 122.3236 | -0.19684 | 0.045776 | 121.5271 | 5.4749 | 0.48981 | 0.55389 | 122.4243 | -0.22888 | -0.12817 | 0.054931 | 0.032044 | 0.11444 | -0.74158 | -0.16022 | 0.15564 | 0.16022 | 0.55847 | 0.62256 | 121.5958 | 122.3923 | 0.032044 | 122.493 | 5.5435 | -0.16022 | 122.3923 | 0.032044 | 5.5435 | 121.5958 | 122.493 | -122.4655 | -122.4976
3675.5625 | 122.4289 | -0.050354 | 122.2412 | 0.15297 | 0.012405 | -0.012978 | 0.013398 | 0.049046 | -0.013099 | 0.067116 | 0.027466 | 122.3694 | -0.16937 | 0.14191 | 121.6278 | 5.5161 | 0.27008 | 0.59509 | 122.406 | -0.20142 | -0.11902 | 0.12817 | 0.07782 | 0.19226 | -0.6134 | -0.15106 | 0.16479 | 0.19684 | 0.32044 | 0.64545 | 121.6782 | 122.4197 | 0.07782 | 122.4564 | 5.5664 | -0.15106 | 122.4197 | 0.07782 | 5.5664 | 121.6782 | 122.4564 | -122.4106 | -122.4426
3677.3281 | 122.4838 | -0.054932 | 122.2321 | 0.053787 | 0.009628 | -0.013405 | 0.0078442 | 0.045841 | -0.011818 | 0.068611 | -0.009155 | 122.2824 | -0.14191 | 0.10071 | 121.6003 | 5.5389 | 0.41199 | 0.65918 | 122.4152 | -0.21973 | -0.086975 | 0.050354 | 0.045777 | 0.15564 | -0.63171 | -0.16479 | 0.1831 | 0.13275 | 0.46692 | 0.71411 | 121.6553 | 122.3373 | 0.045777 | 122.4701 | 5.5939 | -0.16479 | 122.3373 | 0.045777 | 5.5939 | 121.6553 | 122.4701 | -122.374 | -122.4518
3679.0312 | 122.4747 | -0.050354 | 122.2458 | 0.099564 | 0.010696 | -0.014046 | 0.016603 | 0.046482 | -0.013954 | 0.066048 | -0.059509 | 122.319 | -0.20599 | 0.045776 | 121.5271 | 5.4565 | 0.44403 | 0.48065 | 122.4792 | -0.24261 | -0.15564 | 0.073242 | -0.009155 | 0.09613 | -0.71869 | -0.19226 | 0.23346 | 0.14649 | 0.49439 | 0.53101 | 121.5775 | 122.3694 | -0.009155 | 122.5296 | 5.5069 | -0.19226 | 122.3694 | -0.009155 | 5.5069 | 121.5775 | 122.5296 | -122.4518 | -122.4884
3680.7969 | 122.4014 | -0.082397 | 122.2916 | 0.046158 | 0.0094144 | -0.013191 | 0.015535 | 0.049259 | -0.014808 | 0.066262 | -0.027466 | 122.3145 | -0.19226 | 0.045776 | 121.5179 | 5.5161 | 0.48981 | 0.53558 | 122.493 | -0.23804 | -0.10986 | 0.022888 | 0.054931 | 0.12817 | -0.77362 | -0.15564 | 0.20142 | 0.16479 | 0.5722 | 0.61798 | 121.6003 | 122.3969 | 0.054931 | 122.5754 | 5.5984 | -0.15564 | 122.3969 | 0.054931 | 5.5984 | 121.6003 | 122.5754 | -122.4838 | -122.5296
3682.5 | 122.4792 | -0.045776 | 122.2229 | 0.053787 | 0.011978 | -0.012764 | 0.0089124 | 0.048191 | -0.010963 | 0.065407 | 0.009155 | 122.3007 | -0.15564 | 0.091553 | 121.6003 | 5.5847 | 0.41199 | 0.65002 | 122.406 | -0.20599 | -0.10986 | 0.07782 | 0.054931 | 0.13733 | -0.62256 | -0.16022 | 0.18311 | 0.16479 | 0.45776 | 0.6958 | 121.6461 | 122.3465 | 0.054931 | 122.4518 | 5.6305 | -0.16022 | 122.3465 | 0.054931 | 5.6305 | 121.6461 | 122.4518 | -122.3785 | -122.4289
3684.2656 | 122.3648 | -0.091553 | 122.2824 | -0.19035 | 0.010055 | -0.012123 | 0.01468 | 0.04755 | -0.013954 | 0.067116 | -0.027466 | 122.3511 | -0.19226 | 0.082397 | 121.5775 | 5.6763 | 0.70496 | 0.78735 | 122.4609 | -0.22888 | -0.10071 | 0.068664 | 0.064087 | 0.17395 | -0.70496 | -0.13733 | 0.17853 | 0.16479 | 0.79651 | 0.87891 | 121.669 | 122.4426 | 0.064087 | 122.5525 | 5.7678 | -0.13733 | 122.4426 | 0.064087 | 5.7678 | 121.669 | 122.5525 | -122.4747 | -122.5113
3686.0156 | 122.374 | -0.09613 | 122.2824 | -0.15221 | 0.010696 | -0.0057145 | 0.012544 | 0.047978 | -0.01139 | 0.06733 | -0.054932 | 122.3282 | -0.1831 | 0.064087 | 121.5775 | 5.6763 | 0.737 | 0.79193 | 122.4564 | -0.24719 | -0.086975 | 0.045776 | 0.041198 | 0.16022 | -0.70496 | -0.15106 | 0.17395 | 0.12817 | 0.83313 | 0.88806 | 121.6736 | 122.4243 | 0.041198 | 122.5525 | 5.7724 | -0.15106 | 122.4243 | 0.041198 | 5.7724 | 121.6736 | 122.5525 | -122.4655 | -122.5296
3687.7656 | 122.3282 | -0.091553 | 122.2733 | -0.13695 | 0.010055 | -0.0099869 | 0.013398 | 0.045841 | -0.013954 | 0.066475 | -0.018311 | 122.3145 | -0.18768 | 0.09613 | 121.582 | 5.7129 | 0.6546 | 0.76904 | 122.4609 | -0.23346 | -0.09613 | 0.041199 | 0.073242 | 0.18768 | -0.69122 | -0.14191 | 0.18768 | 0.16937 | 0.74616 | 0.8606 | 121.6736 | 122.406 | 0.073242 | 122.5525 | 5.8044 | -0.14191 | 122.406 | 0.073242 | 5.8044 | 121.6736 | 122.5525 | -122.4609 | -122.5067
3689.4688 | 122.4884 | -0.050354 | 122.2229 | 0.030899 | 0.011551 | -0.016182 | 0.0086988 | 0.046696 | -0.011177 | 0.067757 | -0.004578 | 122.319 | -0.16937 | 0.09613 | 121.6095 | 5.6534 | 0.42572 | 0.67749 | 122.4289 | -0.20599 | -0.11902 | 0.096131 | 0.045776 | 0.14648 | -0.6134 | -0.15564 | 0.20599 | 0.16479 | 0.47607 | 0.72784 | 121.6599 | 122.3694 | 0.045776 | 122.4792 | 5.7037 | -0.15564 | 122.3694 | 0.045776 | 5.7037 | 121.6599 | 122.4792 | -122.3923 | -122.4289
3691.2344 | 122.4701 | -0.032043 | 122.2412 | 0.0080111 | 0.0087734 | -0.011055 | 0.010408 | 0.047337 | -0.0096814 | 0.06498 | -0.004578 | 122.3099 | -0.15106 | 0.11444 | 121.6187 | 5.6808 | 0.48981 | 0.74158 | 122.4106 | -0.22888 | -0.11902 | 0.068664 | 0.027465 | 0.14648 | -0.62256 | -0.19684 | 0.16937 | 0.14648 | 0.52185 | 0.77362 | 121.6507 | 122.3419 | 0.027465 | 122.4426 | 5.7129 | -0.19684 | 122.3419 | 0.027465 | 5.7129 | 121.6507 | 122.4426 | -122.3923 | -122.4701
3693 | 122.4197 | -0.068665 | 122.2687 | -0.098801 | 0.011978 | -0.0102 | 0.010621 | 0.045414 | -0.011604 | 0.065621 | 0.032043 | 122.3053 | -0.15564 | 0.15106 | 121.6599 | 5.7907 | 0.54474 | 0.89722 | 122.3877 | -0.21057 | -0.086975 | 0.036621 | 0.10071 | 0.21973 | -0.60883 | -0.14191 | 0.11902 | 0.18768 | 0.6134 | 0.96588 | 121.7285 | 122.374 | 0.10071 | 122.4564 | 5.8594 | -0.14191 | 122.374 | 0.10071 | 5.8594 | 121.7285 | 122.4564 | -122.4243 | -122.4792
3694.7812 | 122.3831 | -0.082397 | 122.2733 | -0.0072479 | 0.0092008 | -0.013832 | 0.01938 | 0.048832 | -0.014167 | 0.06797 | -0.022888 | 122.2916 | -0.20599 | 0.073242 | 121.5363 | 5.6488 | 0.50354 | 0.59509 | 122.4564 | -0.22888 | -0.1236 | 0.018311 | 0.059509 | 0.15564 | -0.737 | -0.14649 | 0.18311 | 0.18311 | 0.58594 | 0.67749 | 121.6187 | 122.374 | 0.059509 | 122.5388 | 5.7312 | -0.14649 | 122.374 | 0.059509 | 5.7312 | 121.6187 | 122.5388 | -122.4792 | -122.5021
3696.5625 | 122.4701 | -0.041199 | 122.2458 | -0.0072479 | 0.0059964 | -0.014259 | 0.0086988 | 0.047123 | -0.013954 | 0.068184 | -0.018311 | 122.2778 | -0.15564 | 0.09613 | 121.6141 | 5.7037 | 0.48523 | 0.72784 | 122.4426 | -0.21057 | -0.11444 | 0.032043 | 0.022888 | 0.13733 | -0.63171 | -0.16937 | 0.19684 | 0.13733 | 0.52643 | 0.76904 | 121.6553 | 122.319 | 0.022888 | 122.4838 | 5.7449 | -0.16937 | 122.319 | 0.022888 | 5.7449 | 121.6553 | 122.4838 | -122.4014 | -122.4564
3698.25 | 122.3373 | -0.10529 | 122.2687 | -0.12932 | 0.011123 | -0.0102 | 0.014039 | 0.04755 | -0.013313 | 0.065834 | 0.004578 | 122.3007 | -0.19684 | 0.11444 | 121.5729 | 5.7953 | 0.62714 | 0.76904 | 122.4701 | -0.24719 | -0.091552 | 0.032043 | 0.10986 | 0.21973 | -0.6958 | -0.14191 | 0.20142 | 0.20142 | 0.73242 | 0.87433 | 121.6782 | 122.406 | 0.10986 | 122.5754 | 5.9006 | -0.14191 | 122.406 | 0.10986 | 5.9006 | 121.6782 | 122.5754 | -122.4655 | -122.5159
3699.9375 | 122.4838 | -0.018311 | 122.2321 | 0.038529 | 0.010055 | -0.013832 | 0.007417 | 0.04755 | -0.012031 | 0.067116 | 0.018311 | 122.2778 | -0.13733 | 0.09613 | 121.6095 | 5.7175 | 0.43945 | 0.67749 | 122.4426 | -0.20599 | -0.11902 | 0.045776 | 0.036622 | 0.11444 | -0.62256 | -0.18768 | 0.21057 | 0.15564 | 0.45776 | 0.6958 | 121.6278 | 122.2961 | 0.036622 | 122.4609 | 5.7358 | -0.18768 | 122.2961 | 0.036622 | 5.7358 | 121.6278 | 122.4609 | -122.3694 | -122.4381
3701.7188 | 122.4609 | -0.059509 | 122.2504 | 0.091934 | 0.0098416 | -0.010841 | 0.0099804 | 0.044132 | -0.010109 | 0.065621 | -0.004578 | 122.2549 | -0.16937 | 0.11444 | 121.6232 | 5.7083 | 0.38452 | 0.66376 | 122.4106 | -0.21973 | -0.10986 | 0.004578 | 0.054931 | 0.17395 | -0.62714 | -0.16022 | 0.16022 | 0.16479 | 0.44403 | 0.72327 | 121.6827 | 122.3145 | 0.054931 | 122.4701 | 5.7678 | -0.16022 | 122.3145 | 0.054931 | 5.7678 | 121.6827 | 122.4701 | -122.4197 | -122.4701
3703.4844 | 122.4792 | -0.059509 | 122.2504 | 0.11482 | 0.011551 | -0.011482 | 0.015962 | 0.047337 | -0.01139 | 0.066262 | -0.041199 | 122.3145 | -0.20142 | 0.050354 | 121.5179 | 5.6534 | 0.41199 | 0.50354 | 122.4426 | -0.25635 | -0.14191 | 0.064087 | 0.01831 | 0.10986 | -0.73242 | -0.19684 | 0.19226 | 0.16022 | 0.4715 | 0.56305 | 121.5775 | 122.374 | 0.01831 | 122.5021 | 5.7129 | -0.19684 | 122.374 | 0.01831 | 5.7129 | 121.5775 | 122.5021 | -122.4518 | -122.5067
3705.25 | 122.4792 | -0.032043 | 122.2504 | 0.099564 | 0.0092008 | -0.012978 | 0.016176 | 0.048405 | -0.013313 | 0.066262 | -0.045776 | 122.3053 | -0.20599 | 0.059509 | 121.5363 | 5.6717 | 0.41199 | 0.50354 | 122.4792 | -0.23346 | -0.17395 | 0.054932 | -0.013733 | 0.091552 | -0.71411 | -0.20142 | 0.22888 | 0.16022 | 0.44403 | 0.53558 | 121.5683 | 122.3373 | -0.013733 | 122.5113 | 5.7037 | -0.20142 | 122.3373 | -0.013733 | 5.7037 | 121.5683 | 122.5113 | -122.4564 | -122.4838
3706.9531 | 122.4747 | -0.045776 | 122.2412 | 0.01564 | 0.009628 | -0.017464 | 0.0076306 | 0.046696 | -0.009895 | 0.064339 | -0.004578 | 122.319 | -0.15106 | 0.086975 | 121.6095 | 5.7861 | 0.50354 | 0.72327 | 122.4152 | -0.21973 | -0.10529 | 0.07782 | 0.041198 | 0.13275 | -0.63171 | -0.17395 | 0.17395 | 0.14648 | 0.54932 | 0.76904 | 121.6553 | 122.3648 | 0.041198 | 122.4609 | 5.8319 | -0.17395 | 122.3648 | 0.041198 | 5.8319 | 121.6553 | 122.4609 | -122.3923 | -122.4609
3708.7188 | 122.3511 | -0.10071 | 122.2824 | -0.18272 | 0.00621 | -0.0149 | 0.010835 | 0.045414 | -0.011177 | 0.06498 | 0.054932 | 122.2824 | -0.16022 | 0.16479 | 121.6599 | 5.9555 | 0.62714 | 0.95673 | 122.3831 | -0.20599 | -0.059509 | 0 | 0.15564 | 0.2655 | -0.62256 | -0.10529 | 0.10071 | 0.21515 | 0.72784 | 1.0574 | 121.7606 | 122.3831 | 0.15564 | 122.4838 | 6.0562 | -0.10529 | 122.3831 | 0.15564 | 6.0562 | 121.7606 | 122.4838 | -122.4426 | -122.4884
3710.4844 | 122.3328 | -0.10071 | 122.287 | -0.15984 | 0.0094144 | -0.011055 | 0.016816 | 0.04691 | -0.01374 | 0.066902 | -0.009155 | 122.3099 | -0.20599 | 0.10529 | 121.5729 | 5.8914 | 0.6546 | 0.79193 | 122.4518 | -0.24719 | -0.10529 | 0.022888 | 0.091553 | 0.20599 | -0.71411 | -0.14648 | 0.16479 | 0.19684 | 0.75531 | 0.89264 | 121.6736 | 122.4106 | 0.091553 | 122.5525 | 5.9921 | -0.14648 | 122.4106 | 0.091553 | 5.9921 | 121.6736 | 122.5525 | -122.493 | -122.5342
3712.25 | 122.3923 | -0.07782 | 122.2687 | -0.12169 | 0.010696 | -0.011482 | 0.0080578 | 0.047123 | -0.012672 | 0.065621 | 0.054932 | 122.2824 | -0.14648 | 0.17395 | 121.6644 | 5.9647 | 0.54474 | 0.9201 | 122.4564 | -0.19684 | -0.068664 | 0.013733 | 0.13275 | 0.25177 | -0.60425 | -0.11902 | 0.18768 | 0.20142 | 0.62256 | 0.99792 | 121.7422 | 122.3602 | 0.13275 | 122.5342 | 6.0425 | -0.11902 | 122.3602 | 0.13275 | 6.0425 | 121.7422 | 122.5342 | -122.4152 | -122.4655
3713.9531 | 122.4655 | -0.064087 | 122.2321 | 0.053787 | 0.011123 | -0.017464 | 0.014467 | 0.049259 | -0.012245 | 0.066475 | -0.059509 | 122.3053 | -0.20599 | 0.027466 | 121.5042 | 5.7541 | 0.47607 | 0.52185 | 122.4838 | -0.23346 | -0.14191 | 0.073242 | 0.004578 | 0.091553 | -0.72785 | -0.16937 | 0.25177 | 0.14649 | 0.54016 | 0.58594 | 121.5683 | 122.3694 | 0.004578 | 122.5479 | 5.8182 | -0.16937 | 122.3694 | 0.004578 | 5.8182 | 121.5683 | 122.5479 | -122.4381 | -122.4655
3715.7188 | 122.4655 | -0.045776 | 122.2321 | 0.00038159 | 0.0066372 | -0.016182 | 0.0076306 | 0.04755 | -0.011177 | 0.066262 | -0.009155 | 122.2916 | -0.16479 | 0.086975 | 121.6049 | 5.8731 | 0.51727 | 0.73242 | 122.4152 | -0.21057 | -0.11902 | 0.059509 | 0.036621 | 0.13275 | -0.62714 | -0.1648 | 0.1831 | 0.15564 | 0.56305 | 0.7782 | 121.6507 | 122.3373 | 0.036621 | 122.4609 | 5.9189 | -0.1648 | 122.3373 | 0.036621 | 5.9189 | 121.6507 | 122.4609 | -122.3969 | -122.4426
3717.4219 | 122.3419 | -0.11902 | 122.287 | -0.21324 | 0.010269 | -0.0099869 | 0.011049 | 0.045841 | -0.013099 | 0.066048 | 0.041199 | 122.2961 | -0.15564 | 0.15564 | 121.6553 | 6.0425 | 0.64087 | 0.97046 | 122.4243 | -0.18768 | -0.036621 | 0.009156 | 0.16022 | 0.27466 | -0.63171 | -0.068664 | 0.13733 | 0.19684 | 0.75989 | 1.0895 | 121.7743 | 122.4152 | 0.16022 | 122.5433 | 6.1615 | -0.068664 | 122.4152 | 0.16022 | 6.1615 | 121.7743 | 122.5433 | -122.4426 | -122.4747
3719.1875 | 122.4976 | -0.036621 | 122.2275 | 0.02327 | 0.0066372 | -0.015327 | 0.0095532 | 0.046696 | -0.0094678 | 0.065407 | 0.004578 | 122.2824 | -0.14648 | 0.10071 | 121.6049 | 5.8731 | 0.47607 | 0.71411 | 122.4335 | -0.20142 | -0.10986 | 0.054932 | 0.041199 | 0.13733 | -0.62256 | -0.1648 | 0.20599 | 0.15106 | 0.5127 | 0.75073 | 121.6415 | 122.319 | 0.041199 | 122.4701 | 5.9097 | -0.1648 | 122.319 | 0.041199 | 5.9097 | 121.6415 | 122.4701 | -122.374 | -122.4289
3720.9531 | 122.4243 | -0.064087 | 122.2366 | 0.18349 | 0.0064236 | -0.011055 | 0.016389 | 0.046482 | -0.011818 | 0.066475 | 0.064087 | 122.2687 | -0.16022 | 0.16937 | 121.6324 | 5.9052 | 0.24261 | 0.63171 | 122.4152 | -0.20142 | -0.09613 | 0.032044 | 0.12817 | 0.23346 | -0.60425 | -0.13733 | 0.17853 | 0.2243 | 0.3067 | 0.6958 | 121.6965 | 122.3328 | 0.12817 | 122.4792 | 5.9692 | -0.13733 | 122.3328 | 0.12817 | 5.9692 | 121.6965 | 122.4792 | -122.3969 | -122.438
3722.6562 | 122.3877 | -0.068665 | 122.2687 | -0.21324 | 0.0092008 | -0.012123 | 0.013612 | 0.046269 | -0.012886 | 0.066689 | -0.054932 | 122.3099 | -0.19226 | 0.054932 | 121.5454 | 5.9601 | 0.81024 | 0.85144 | 122.4884 | -0.27008 | -0.1236 | 0.041198 | 0.013733 | 0.1236 | -0.72327 | -0.20142 | 0.21973 | 0.13733 | 0.87891 | 0.9201 | 121.6141 | 122.3785 | 0.013733 | 122.5571 | 6.0287 | -0.20142 | 122.3785 | 0.013733 | 6.0287 | 121.6141 | 122.5571 | -122.4609 | -122.5388
3724.4219 | 122.3877 | -0.082397 | 122.2504 | -0.26665 | 0.0089872 | -0.014687 | 0.012758 | 0.047123 | -0.011818 | 0.066048 | -0.059509 | 122.287 | -0.20142 | 0.059509 | 121.5546 | 5.9738 | 0.80566 | 0.82855 | 122.4792 | -0.24719 | -0.11902 | 0.036621 | 0.022888 | 0.14191 | -0.6958 | -0.16479 | 0.22888 | 0.14191 | 0.88806 | 0.91095 | 121.637 | 122.3694 | 0.022888 | 122.5616 | 6.0562 | -0.16479 | 122.3694 | 0.022888 | 6.0562 | 121.637 | 122.5616 | -122.4518 | -122.4976
3726.125 | 122.3465 | -0.10529 | 122.2778 | -0.19035 | 0.0087734 | -0.01255 | 0.011049 | 0.045628 | -0.012245 | 0.065621 | 0.041199 | 122.3053 | -0.15564 | 0.16022 | 121.6599 | 6.102 | 0.66834 | 0.97504 | 122.4335 | -0.2243 | -0.050354 | 0.027466 | 0.14649 | 0.2655 | -0.61798 | -0.11902 | 0.15564 | 0.19684 | 0.77362 | 1.0803 | 121.7651 | 122.4106 | 0.14649 | 122.5388 | 6.2073 | -0.11902 | 122.4106 | 0.14649 | 6.2073 | 121.7651 | 122.5388 | -122.4335 | -122.5021
3727.8906 | 122.406 | -0.091553 | 122.2778 | -0.21324 | 0.0087734 | -0.015114 | 0.012544 | 0.047978 | -0.01374 | 0.065834 | -0.068665 | 122.3053 | -0.20142 | 0.064087 | 121.55 | 6.0104 | 0.81482 | 0.84686 | 122.4884 | -0.24261 | -0.10986 | 0.027466 | 0.022888 | 0.15564 | -0.72784 | -0.15106 | 0.21057 | 0.13275 | 0.90637 | 0.93842 | 121.6415 | 122.3969 | 0.022888 | 122.58 | 6.102 | -0.15106 | 122.3969 | 0.022888 | 6.102 | 121.6415 | 122.58 | -122.4792 | -122.5204
3729.6406 | 122.3419 | -0.10529 | 122.287 | -0.19035 | 0.0087734 | -0.012337 | 0.010194 | 0.047978 | -0.011177 | 0.064553 | 0.054932 | 122.2961 | -0.15106 | 0.17395 | 121.6599 | 6.134 | 0.63171 | 0.95673 | 122.438 | -0.21057 | -0.045776 | 0.009156 | 0.16022 | 0.27924 | -0.62714 | -0.10529 | 0.15106 | 0.20599 | 0.737 | 1.062 | 121.7651 | 122.4014 | 0.16022 | 122.5433 | 6.2393 | -0.10529 | 122.4014 | 0.16022 | 6.2393 | 121.7651 | 122.5433 | -122.438 | -122.4976
3731.4062 | 122.3282 | -0.10529 | 122.287 | -0.091171 | 0.0092008 | -0.015327 | 0.017244 | 0.04691 | -0.016304 | 0.066475 | -0.009155 | 122.287 | -0.19226 | 0.1236 | 121.5912 | 6.0516 | 0.60883 | 0.7782 | 122.4518 | -0.23346 | -0.086975 | 0 | 0.096131 | 0.22888 | -0.6958 | -0.12817 | 0.16479 | 0.18311 | 0.71411 | 0.88348 | 121.6965 | 122.3923 | 0.096131 | 122.5571 | 6.1569 | -0.12817 | 122.3923 | 0.096131 | 6.1569 | 121.6965 | 122.5571 | -122.4792 | -122.5204
3733.1094 | 122.4838 | -0.059509 | 122.2412 | 0.046158 | 0.0087734 | -0.0149 | 0.0099804 | 0.045841 | -0.01139 | 0.064766 | 0.013733 | 122.3053 | -0.14191 | 0.10986 | 121.5958 | 5.9784 | 0.4303 | 0.70038 | 122.4243 | -0.21515 | -0.082398 | 0.064087 | 0.073242 | 0.16937 | -0.64545 | -0.15564 | 0.1831 | 0.15564 | 0.48981 | 0.75989 | 121.6553 | 122.3648 | 0.073242 | 122.4838 | 6.0379 | -0.15564 | 122.3648 | 0.073242 | 6.0379 | 121.6553 | 122.4838 | -122.3831 | -122.4564
3734.8906 | 122.3785 | -0.086975 | 122.2504 | 0.02327 | 0.011764 | -0.0095597 | 0.017244 | 0.048619 | -0.010322 | 0.064339 | 0.018311 | 122.3465 | -0.20142 | 0.059509 | 121.5363 | 5.9555 | 0.52185 | 0.59509 | 122.4792 | -0.24261 | -0.11444 | 0.096131 | 0.10529 | 0.14648 | -0.71411 | -0.15564 | 0.22888 | 0.21973 | 0.60883 | 0.68207 | 121.6232 | 122.4335 | 0.10529 | 122.5662 | 6.0425 | -0.15564 | 122.4335 | 0.10529 | 6.0425 | 121.6232 | 122.5662 | -122.4518 | -122.493
3736.6562 | 122.493 | -0.050354 | 122.2458 | 0.02327 | 0.010696 | -0.0082779 | 0.009126 | 0.04691 | -0.011818 | 0.066902 | 0.004578 | 122.3145 | -0.17395 | 0.10071 | 121.6003 | 6.0242 | 0.52643 | 0.74616 | 122.4564 | -0.21515 | -0.1236 | 0.068664 | 0.054932 | 0.15106 | -0.64545 | -0.16479 | 0.21057 | 0.17853 | 0.57678 | 0.79651 | 121.6507 | 122.3648 | 0.054932 | 122.5067 | 6.0745 | -0.16479 | 122.3648 | 0.054932 | 6.0745 | 121.6507 | 122.5067 | -122.4197 | -122.4609
3738.4062 | 122.4472 | -0.050354 | 122.2412 | -0.053024 | 0.0089872 | -0.014473 | 0.0082714 | 0.045201 | -0.011177 | 0.066048 | -0.004578 | 122.287 | -0.1831 | 0.14191 | 121.6324 | 6.1066 | 0.54474 | 0.83771 | 122.4243 | -0.20599 | -0.13275 | 0.045776 | 0.045776 | 0.19226 | -0.60883 | -0.15564 | 0.1831 | 0.17853 | 0.59509 | 0.88806 | 121.6827 | 122.3373 | 0.045776 | 122.4747 | 6.1569 | -0.15564 | 122.3373 | 0.045776 | 6.1569 | 121.6827 | 122.4747 | -122.4243 | -122.4472
3740.1719 | 122.4335 | -0.059509 | 122.2321 | 0.046158 | 0.0074918 | -0.010414 | 0.018312 | 0.048405 | -0.014167 | 0.067757 | -0.036621 | 122.3053 | -0.20599 | 0.045776 | 121.5225 | 5.9921 | 0.53558 | 0.56305 | 122.4884 | -0.23804 | -0.14649 | 0.073242 | 0.022888 | 0.10528 | -0.70953 | -0.17853 | 0.25635 | 0.16937 | 0.59509 | 0.62256 | 121.582 | 122.3648 | 0.022888 | 122.5479 | 6.0516 | -0.17853 | 122.3648 | 0.022888 | 6.0516 | 121.582 | 122.5479 | -122.4381 | -122.4701
3741.875 | 122.319 | -0.10071 | 122.287 | -0.098801 | 0.0085598 | -0.018318 | 0.015748 | 0.049259 | -0.015876 | 0.067116 | 0.004578 | 122.3007 | -0.18768 | 0.11444 | 121.5958 | 6.1386 | 0.59509 | 0.76446 | 122.4518 | -0.22888 | -0.086975 | 0.013733 | 0.10529 | 0.21515 | -0.69122 | -0.12817 | 0.16479 | 0.19226 | 0.6958 | 0.86517 | 121.6965 | 122.4014 | 0.10529 | 122.5525 | 6.2393 | -0.12817 | 122.4014 | 0.10529 | 6.2393 | 121.6965 | 122.5525 | -122.4747 | -122.5159
3743.6406 | 122.374 | -0.10529 | 122.2778 | -0.25902 | 0.0083462 | -0.01255 | 0.0097668 | 0.044773 | -0.011177 | 0.064125 | 0.032043 | 122.3328 | -0.18768 | 0.10529 | 121.6187 | 6.2119 | 0.77362 | 0.9201 | 122.4518 | -0.23346 | -0.082397 | 0.054932 | 0.13733 | 0.21057 | -0.65918 | -0.12817 | 0.17395 | 0.21973 | 0.87891 | 1.0254 | 121.7239 | 122.4381 | 0.13733 | 122.5571 | 6.3171 | -0.12817 | 122.4381 | 0.13733 | 6.3171 | 121.7239 | 122.5571 | -122.4655 | -122.5113
3745.3438 | 122.4289 | -0.054932 | 122.2458 | 0.15297 | 0.01091 | -0.011696 | 0.014894 | 0.049687 | -0.014808 | 0.066475 | 0.027466 | 122.3007 | -0.15106 | 0.12817 | 121.6141 | 6.0791 | 0.27924 | 0.60883 | 122.4197 | -0.19226 | -0.09613 | 0.054931 | 0.082398 | 0.18311 | -0.63171 | -0.13733 | 0.17395 | 0.17853 | 0.33417 | 0.66376 | 121.669 | 122.3557 | 0.082398 | 122.4747 | 6.134 | -0.13733 | 122.3557 | 0.082398 | 6.134 | 121.669 | 122.4747 | -122.3969 | -122.4381
3747.1094 | 122.438 | -0.068665 | 122.2549 | 0.084305 | 0.0098416 | -0.012978 | 0.012117 | 0.047978 | -0.01374 | 0.066475 | 0.050354 | 122.3373 | -0.16022 | 0.12817 | 121.6278 | 6.1249 | 0.32044 | 0.67291 | 122.4335 | -0.18768 | -0.091552 | 0.082397 | 0.11902 | 0.19684 | -0.62714 | -0.11902 | 0.17853 | 0.21057 | 0.3891 | 0.74158 | 121.6965 | 122.406 | 0.11902 | 122.5021 | 6.1935 | -0.11902 | 122.406 | 0.11902 | 6.1935 | 121.6965 | 122.5021 | -122.4152 | -122.4426
3748.875 | 122.3877 | -0.064087 | 122.2687 | -0.17509 | 0.0089872 | -0.012978 | 0.011476 | 0.047978 | -0.013527 | 0.066689 | -0.032043 | 122.3328 | -0.19226 | 0.054932 | 121.5546 | 6.1981 | 0.81024 | 0.84228 | 122.4609 | -0.24261 | -0.12817 | 0.064087 | 0.032044 | 0.11902 | -0.71411 | -0.17853 | 0.19226 | 0.16022 | 0.87433 | 0.90637 | 121.6187 | 122.3969 | 0.032044 | 122.525 | 6.2622 | -0.17853 | 122.3969 | 0.032044 | 6.2622 | 121.6187 | 122.525 | -122.4609 | -122.5113
3750.6406 | 122.3602 | -0.09613 | 122.2916 | -0.060654 | 0.010055 | -0.0089189 | 0.016816 | 0.052037 | -0.013527 | 0.066262 | 0.009155 | 122.2961 | -0.1831 | 0.10529 | 121.5683 | 6.1523 | 0.5722 | 0.68207 | 122.4792 | -0.23346 | -0.086975 | 0.004578 | 0.10528 | 0.20142 | -0.72327 | -0.13733 | 0.18768 | 0.19226 | 0.66833 | 0.7782 | 121.6644 | 122.3923 | 0.10528 | 122.5754 | 6.2485 | -0.13733 | 122.3923 | 0.10528 | 6.2485 | 121.6644 | 122.5754 | -122.4747 | -122.525
3752.3281 | 122.3419 | -0.11444 | 122.3053 | -0.083542 | 0.0077054 | -0.0102 | 0.01468 | 0.049046 | -0.014595 | 0.067116 | 0.018311 | 122.3145 | -0.18768 | 0.10986 | 121.5866 | 6.1935 | 0.5722 | 0.74158 | 122.4838 | -0.23346 | -0.073242 | 0.009155 | 0.13275 | 0.2243 | -0.71869 | -0.11902 | 0.17853 | 0.20599 | 0.68665 | 0.85602 | 121.701 | 122.4289 | 0.13275 | 122.5983 | 6.308 | -0.11902 | 122.4289 | 0.13275 | 6.308 | 121.701 | 122.5983 | -122.493 | -122.5388
3754.0938 | 122.4747 | -0.045776 | 122.2137 | 0.0080111 | 0.0064236 | -0.012337 | 0.0065624 | 0.048619 | -0.009895 | 0.067116 | -0.004578 | 122.3236 | -0.17395 | 0.086975 | 121.6003 | 6.1707 | 0.52643 | 0.75531 | 122.4289 | -0.21057 | -0.12817 | 0.10986 | 0.041198 | 0.13275 | -0.6134 | -0.1648 | 0.21515 | 0.16937 | 0.5722 | 0.80109 | 121.6461 | 122.3694 | 0.041198 | 122.4747 | 6.2164 | -0.1648 | 122.3694 | 0.041198 | 6.2164 | 121.6461 | 122.4747 | -122.3877 | -122.4243
3755.7969 | 122.4197 | -0.059509 | 122.2687 | 0.16823 | 0.0072782 | -0.011269 | 0.013612 | 0.047978 | -0.012458 | 0.066902 | 0.064087 | 122.2595 | -0.16479 | 0.15564 | 121.6278 | 6.1844 | 0.27924 | 0.63171 | 122.4014 | -0.19226 | -0.10529 | -0.009156 | 0.1236 | 0.21515 | -0.64087 | -0.13275 | 0.13275 | 0.22888 | 0.33874 | 0.69122 | 121.6873 | 122.319 | 0.1236 | 122.4609 | 6.2439 | -0.13275 | 122.319 | 0.1236 | 6.2439 | 121.6873 | 122.4609 | -122.4335 | -122.4609
3757.5469 | 122.4106 | -0.064087 | 122.2321 | 0.15297 | 0.007919 | -0.011909 | 0.011262 | 0.047764 | -0.015022 | 0.067116 | 0.068665 | 122.2687 | -0.15106 | 0.16022 | 121.6278 | 6.1981 | 0.28381 | 0.66834 | 122.4335 | -0.18768 | -0.086975 | 0.036621 | 0.13275 | 0.2243 | -0.60425 | -0.1236 | 0.20142 | 0.21973 | 0.3479 | 0.73242 | 121.6919 | 122.3328 | 0.13275 | 122.4976 | 6.2622 | -0.1236 | 122.3328 | 0.13275 | 6.2622 | 121.6919 | 122.4976 | -122.3831 | -122.4197
3759.3125 | 122.3602 | -0.091553 | 122.287 | -0.030136 | 0.009628 | -0.0063553 | 0.016176 | 0.048832 | -0.014595 | 0.065834 | 0.004578 | 122.3053 | -0.19226 | 0.086975 | 121.5363 | 6.189 | 0.54016 | 0.63629 | 122.4701 | -0.21515 | -0.10071 | 0.018311 | 0.096131 | 0.17853 | -0.75073 | -0.1236 | 0.18311 | 0.19684 | 0.63171 | 0.72784 | 121.6278 | 122.3969 | 0.096131 | 122.5616 | 6.2805 | -0.1236 | 122.3969 | 0.096131 | 6.2805 | 121.6278 | 122.5616 | -122.4792 | -122.5021
3761.0781 | 122.4335 | -0.045776 | 122.2595 | 0.11482 | 0.0089872 | -0.011482 | 0.0099804 | 0.04691 | -0.012458 | 0.066262 | 0.064087 | 122.3007 | -0.13733 | 0.13275 | 121.6415 | 6.2256 | 0.31586 | 0.67749 | 122.4152 | -0.20142 | -0.091553 | 0.041199 | 0.10986 | 0.17853 | -0.61798 | -0.15564 | 0.15564 | 0.20142 | 0.36163 | 0.72327 | 121.6873 | 122.3465 | 0.10986 | 122.4609 | 6.2714 | -0.15564 | 122.3465 | 0.10986 | 6.2714 | 121.6873 | 122.4609 | -122.3969 | -122.4609
3762.7969 | 122.4289 | -0.041199 | 122.2412 | 0.12245 | 0.010269 | -0.015755 | 0.0097668 | 0.048405 | -0.015022 | 0.066902 | 0.054932 | 122.2824 | -0.14191 | 0.15106 | 121.6461 | 6.2393 | 0.31128 | 0.66834 | 122.4335 | -0.20142 | -0.10071 | 0.041199 | 0.096131 | 0.19226 | -0.59509 | -0.16022 | 0.19226 | 0.19684 | 0.35248 | 0.70953 | 121.6873 | 122.3236 | 0.096131 | 122.4747 | 6.2805 | -0.16022 | 122.3236 | 0.096131 | 6.2805 | 121.6873 | 122.4747 | -122.3831 | -122.4426
3764.5625 | 122.4243 | -0.059509 | 122.2733 | 0.1606 | 0.0081326 | -0.0093461 | 0.013185 | 0.047337 | -0.011818 | 0.065193 | 0.082397 | 122.3328 | -0.15564 | 0.14191 | 121.6278 | 6.2439 | 0.25635 | 0.65002 | 122.4243 | -0.19684 | -0.096131 | 0.05951 | 0.14191 | 0.20142 | -0.64545 | -0.13733 | 0.15106 | 0.23804 | 0.31586 | 0.70953 | 121.6873 | 122.3923 | 0.14191 | 122.4838 | 6.3034 | -0.13733 | 122.3923 | 0.14191 | 6.3034 | 121.6873 | 122.4838 | -122.4289 | -122.4701
3766.3125 | 122.4701 | -0.032043 | 122.2595 | 0.038529 | 0.0087734 | -0.011696 | 0.018953 | 0.047123 | -0.016517 | 0.066689 | -0.050354 | 122.319 | -0.21515 | 0.036621 | 121.4996 | 6.1569 | 0.51727 | 0.55389 | 122.5159 | -0.22888 | -0.18311 | 0.05951 | -0.018311 | 0.068664 | -0.75989 | -0.19684 | 0.25635 | 0.16479 | 0.54932 | 0.58594 | 121.5317 | 122.3511 | -0.018311 | 122.5479 | 6.189 | -0.19684 | 122.3511 | -0.018311 | 6.189 | 121.5317 | 122.5479 | -122.4747 | -122.4884
3768.0781 | 122.438 | -0.050354 | 122.2504 | 0.16823 | 0.0081326 | -0.0097733 | 0.012971 | 0.0499 | -0.014808 | 0.065407 | 0.027466 | 122.2961 | -0.17395 | 0.12817 | 121.6095 | 6.2439 | 0.31586 | 0.63171 | 122.4701 | -0.19684 | -0.1236 | 0.045777 | 0.07782 | 0.17853 | -0.64087 | -0.14648 | 0.21973 | 0.20142 | 0.36621 | 0.68207 | 121.6599 | 122.3465 | 0.07782 | 122.5204 | 6.2942 | -0.14648 | 122.3465 | 0.07782 | 6.2942 | 121.6599 | 122.5204 | -122.4243 | -122.4472
3769.8438 | 122.4152 | -0.073242 | 122.2458 | 0.1606 | 0.0081326 | -0.013405 | 0.0095532 | 0.047978 | -0.0094678 | 0.064339 | 0.054932 | 122.3236 | -0.15564 | 0.16022 | 121.6461 | 6.308 | 0.2655 | 0.66376 | 122.406 | -0.20599 | -0.082398 | 0.077819 | 0.12817 | 0.23346 | -0.59967 | -0.13275 | 0.16022 | 0.21057 | 0.33874 | 0.737 | 121.7194 | 122.3968 | 0.12817 | 122.4792 | 6.3812 | -0.13275 | 122.3968 | 0.12817 | 6.3812 | 121.7194 | 122.4792 | -122.4014 | -122.4518
3771.5469 | 122.3923 | -0.086975 | 122.2595 | -0.022507 | 0.010269 | -0.012978 | 0.015962 | 0.051182 | -0.01609 | 0.066475 | -0.036621 | 122.3145 | -0.1831 | 0.045776 | 121.5271 | 6.2393 | 0.54474 | 0.59509 | 122.4792 | -0.23804 | -0.09613 | 0.054932 | 0.050354 | 0.13275 | -0.73242 | -0.15106 | 0.21973 | 0.14648 | 0.63171 | 0.68207 | 121.6141 | 122.4014 | 0.050354 | 122.5662 | 6.3263 | -0.15106 | 122.4014 | 0.050354 | 6.3263 | 121.6141 | 122.5662 | -122.4426 | -122.4976
3773.2969 | 122.3419 | -0.10529 | 122.2916 | -0.14458 | 0.010482 | -0.013191 | 0.014039 | 0.0499 | -0.013954 | 0.066048 | 0.004578 | 122.3053 | -0.20142 | 0.10529 | 121.582 | 6.3904 | 0.66376 | 0.80109 | 122.4564 | -0.2243 | -0.09613 | 0.013733 | 0.10986 | 0.21057 | -0.70953 | -0.11902 | 0.16479 | 0.20599 | 0.76904 | 0.90637 | 121.6873 | 122.4106 | 0.10986 | 122.5616 | 6.4957 | -0.11902 | 122.4106 | 0.10986 | 6.4957 | 121.6873 | 122.5616 | -122.493 | -122.5159
3775.0469 | 122.4289 | -0.068665 | 122.2321 | 0.11482 | 0.0089872 | -0.012337 | 0.008485 | 0.04755 | -0.01139 | 0.066902 | 0.050354 | 122.3053 | -0.13733 | 0.14191 | 121.637 | 6.3263 | 0.3067 | 0.68207 | 122.4243 | -0.19226 | -0.068664 | 0.073242 | 0.11902 | 0.21057 | -0.59509 | -0.1236 | 0.19226 | 0.18768 | 0.37537 | 0.75073 | 121.7056 | 122.374 | 0.11902 | 122.493 | 6.395 | -0.1236 | 122.374 | 0.11902 | 6.395 | 121.7056 | 122.493 | -122.3694 | -122.4243
3776.75 | 122.4518 | -0.050354 | 122.2641 | 0.14534 | 0.010482 | -0.015327 | 0.015107 | 0.049046 | -0.01374 | 0.065834 | -0.018311 | 122.3145 | -0.17853 | 0.073242 | 121.5683 | 6.2805 | 0.37537 | 0.56305 | 122.4884 | -0.21973 | -0.12817 | 0.050354 | 0.032043 | 0.1236 | -0.6958 | -0.16937 | 0.2243 | 0.16022 | 0.42572 | 0.6134 | 121.6187 | 122.3648 | 0.032043 | 122.5388 | 6.3309 | -0.16937 | 122.3648 | 0.032043 | 6.3309 | 121.6187 | 122.5388 | -122.4426 | -122.4838
3778.5 | 122.3923 | -0.09613 | 122.2778 | -0.2285 | 0.010269 | -0.011055 | 0.0099804 | 0.04755 | -0.014808 | 0.063912 | -0.032043 | 122.287 | -0.1831 | 0.07782 | 121.5729 | 6.4178 | 0.81482 | 0.88348 | 122.4747 | -0.21973 | -0.086975 | 0.009155 | 0.064087 | 0.17395 | -0.70496 | -0.1236 | 0.19684 | 0.15106 | 0.91095 | 0.97961 | 121.669 | 122.3831 | 0.064087 | 122.5708 | 6.514 | -0.1236 | 122.3831 | 0.064087 | 6.514 | 121.669 | 122.5708 | -122.4609 | -122.4976
3780.2656 | 122.4106 | -0.082397 | 122.3007 | -0.23613 | 0.0094144 | -0.015114 | 0.013612 | 0.048832 | -0.014595 | 0.066689 | -0.068665 | 122.3145 | -0.20142 | 0.036621 | 121.5454 | 6.4224 | 0.83313 | 0.85144 | 122.4976 | -0.24261 | -0.11902 | 0.013733 | 0.013732 | 0.11902 | -0.75531 | -0.16022 | 0.19684 | 0.13275 | 0.91553 | 0.93384 | 121.6278 | 122.3969 | 0.013732 | 122.58 | 6.5048 | -0.16022 | 122.3969 | 0.013732 | 6.5048 | 121.6278 | 122.58 | -122.5021 | -122.5433
3781.9844 | 122.3785 | -0.10529 | 122.287 | -0.26665 | 0.0072782 | -0.016396 | 0.012117 | 0.045201 | -0.013313 | 0.066902 | 0.022888 | 122.3007 | -0.16479 | 0.10529 | 121.6049 | 6.4957 | 0.79193 | 0.94299 | 122.4472 | -0.2243 | -0.059509 | 0.013733 | 0.12817 | 0.21057 | -0.68207 | -0.11902 | 0.16022 | 0.18768 | 0.89722 | 1.0483 | 121.7102 | 122.406 | 0.12817 | 122.5525 | 6.601 | -0.11902 | 122.406 | 0.12817 | 6.601 | 121.7102 | 122.5525 | -122.4518 | -122.5113
3783.75 | 122.3282 | -0.091553 | 122.3053 | -0.12169 | 0.0089872 | -0.013832 | 0.016389 | 0.046482 | -0.012245 | 0.065407 | -0.009155 | 122.3099 | -0.21057 | 0.09613 | 121.5729 | 6.4545 | 0.66834 | 0.80566 | 122.4472 | -0.25177 | -0.11902 | 0.004577 | 0.082398 | 0.18768 | -0.73242 | -0.16022 | 0.14191 | 0.20142 | 0.75989 | 0.89722 | 121.6644 | 122.4014 | 0.082398 | 122.5388 | 6.546 | -0.16022 | 122.4014 | 0.082398 | 6.546 | 121.6644 | 122.5388 | -122.5159 | -122.5571
3785.5312 | 122.4655 | -0.054932 | 122.2641 | 0.038529 | 0.0064236 | -0.017677 | 0.007417 | 0.044132 | -0.013527 | 0.066475 | -0.022888 | 122.2595 | -0.17853 | 0.086975 | 121.6095 | 6.3858 | 0.4715 | 0.72327 | 122.4426 | -0.19684 | -0.1236 | -0.004578 | 0.032044 | 0.14191 | -0.6546 | -0.14191 | 0.17853 | 0.15564 | 0.52643 | 0.7782 | 121.6644 | 122.3145 | 0.032044 | 122.4976 | 6.4407 | -0.14191 | 122.3145 | 0.032044 | 6.4407 | 121.6644 | 122.4976 | -122.4426 | -122.4609
3787.2812 | 122.4701 | -0.045776 | 122.2733 | 0.099564 | 0.0087734 | -0.018745 | 0.013826 | 0.047978 | -0.014808 | 0.065407 | -0.027466 | 122.3145 | -0.19684 | 0.064087 | 121.55 | 6.3446 | 0.3891 | 0.55389 | 122.4426 | -0.22888 | -0.15106 | 0.041199 | 0.01831 | 0.10986 | -0.72327 | -0.18311 | 0.16937 | 0.16937 | 0.43487 | 0.59967 | 121.5958 | 122.3602 | 0.01831 | 122.4884 | 6.3904 | -0.18311 | 122.3602 | 0.01831 | 6.3904 | 121.5958 | 122.4884 | -122.4701 | -122.5021
3788.9844 | 122.4014 | -0.068665 | 122.2549 | -0.24376 | 0.0083462 | -0.012337 | 0.012758 | 0.046696 | -0.012886 | 0.06498 | -0.068665 | 122.2916 | -0.21515 | 0.050354 | 121.5363 | 6.4682 | 0.84228 | 0.86975 | 122.4564 | -0.26093 | -0.14648 | 0.036621 | 0 | 0.11902 | -0.71869 | -0.19226 | 0.20142 | 0.14648 | 0.91095 | 0.93842 | 121.6049 | 122.3602 | 0 | 122.525 | 6.5369 | -0.19226 | 122.3602 | 0 | 6.5369 | 121.6049 | 122.525 | -122.4701 | -122.5159
3790.75 | 122.3511 | -0.10071 | 122.2916 | -0.098801 | 0.0087734 | -0.012978 | 0.015107 | 0.047764 | -0.014167 | 0.067543 | 0 | 122.2824 | -0.18768 | 0.10986 | 121.5866 | 6.4865 | 0.59052 | 0.76904 | 122.4609 | -0.21057 | -0.086975 | -0.009155 | 0.10071 | 0.21057 | -0.70496 | -0.10986 | 0.16937 | 0.18768 | 0.69122 | 0.86975 | 121.6873 | 122.3831 | 0.10071 | 122.5616 | 6.5872 | -0.10986 | 122.3831 | 0.10071 | 6.5872 | 121.6873 | 122.5616 | -122.4792 | -122.5021
3792.4531 | 122.3511 | -0.086975 | 122.2961 | -0.20561 | 0.0077054 | -0.01255 | 0.008485 | 0.045628 | -0.014808 | 0.065407 | 0.054932 | 122.3145 | -0.15564 | 0.17395 | 121.6599 | 6.6101 | 0.65002 | 1.0071 | 122.406 | -0.20599 | -0.068665 | 0.01831 | 0.14191 | 0.26092 | -0.63629 | -0.11902 | 0.10986 | 0.21057 | 0.737 | 1.0941 | 121.7468 | 122.4014 | 0.14191 | 122.493 | 6.6971 | -0.11902 | 122.4014 | 0.14191 | 6.6971 | 121.7468 | 122.493 | -122.4518 | -122.5021
3794.2031 | 122.3419 | -0.10529 | 122.2778 | -0.21324 | 0.009628 | -0.013832 | 0.0082714 | 0.046269 | -0.011818 | 0.06733 | 0.050354 | 122.3236 | -0.15106 | 0.17853 | 121.6507 | 6.6284 | 0.67291 | 1.0071 | 122.438 | -0.21057 | -0.045776 | 0.045776 | 0.15564 | 0.28381 | -0.62714 | -0.10529 | 0.16022 | 0.20142 | 0.7782 | 1.1124 | 121.756 | 122.4289 | 0.15564 | 122.5433 | 6.7337 | -0.10529 | 122.4289 | 0.15564 | 6.7337 | 121.756 | 122.5433 | -122.4289 | -122.4884
3795.9531 | 122.3373 | -0.091553 | 122.3007 | -0.068283 | 0.010482 | -0.014046 | 0.017244 | 0.046055 | -0.015236 | 0.065407 | 0.009155 | 122.3145 | -0.21057 | 0.10071 | 121.5683 | 6.5094 | 0.59967 | 0.76446 | 122.4609 | -0.2243 | -0.11902 | 0.013733 | 0.10071 | 0.19226 | -0.73242 | -0.13275 | 0.16022 | 0.21973 | 0.69122 | 0.85602 | 121.6599 | 122.406 | 0.10071 | 122.5525 | 6.601 | -0.13275 | 122.406 | 0.10071 | 6.601 | 121.6599 | 122.5525 | -122.5113 | -122.525
3797.7031 | 122.3511 | -0.10986 | 122.2778 | -0.083542 | 0.0094144 | -0.011909 | 0.01703 | 0.047123 | -0.01075 | 0.066048 | 0.013733 | 122.3602 | -0.18768 | 0.10529 | 121.5683 | 6.5094 | 0.58136 | 0.71869 | 122.4564 | -0.23346 | -0.07782 | 0.082397 | 0.1236 | 0.21515 | -0.70953 | -0.1236 | 0.17853 | 0.20142 | 0.69122 | 0.82855 | 121.6782 | 122.4701 | 0.1236 | 122.5662 | 6.6193 | -0.1236 | 122.4701 | 0.1236 | 6.6193 | 121.6782 | 122.5662 | -122.4655 | -122.5113
3799.3906 | 122.4152 | -0.059509 | 122.2458 | 0.19112 | 0.0072782 | -0.012123 | 0.01233 | 0.047337 | -0.01075 | 0.066475 | 0.064087 | 122.3053 | -0.15106 | 0.15106 | 121.6324 | 6.514 | 0.30212 | 0.69122 | 122.406 | -0.19226 | -0.091553 | 0.059509 | 0.1236 | 0.21057 | -0.6134 | -0.13275 | 0.16022 | 0.21515 | 0.36163 | 0.75073 | 121.6919 | 122.3648 | 0.1236 | 122.4655 | 6.5735 | -0.13275 | 122.3648 | 0.1236 | 6.5735 | 121.6919 | 122.4655 | -122.3969 | -122.4381
3801.1562 | 122.3557 | -0.11902 | 122.287 | -0.22087 | 0.0083462 | -0.013405 | 0.008485 | 0.047123 | -0.013527 | 0.066475 | 0.045776 | 122.287 | -0.16479 | 0.15564 | 121.6415 | 6.6925 | 0.68207 | 1.0162 | 122.4426 | -0.18768 | -0.045776 | 0 | 0.16479 | 0.27466 | -0.64545 | -0.068664 | 0.15564 | 0.21057 | 0.80109 | 1.1353 | 121.7606 | 122.406 | 0.16479 | 122.5616 | 6.8115 | -0.068664 | 122.406 | 0.16479 | 6.8115 | 121.7606 | 122.5616 | -122.4518 | -122.4747
3802.9219 | 122.3694 | -0.082397 | 122.287 | -0.17509 | 0.011551 | -0.014473 | 0.013826 | 0.047764 | -0.013313 | 0.065193 | -0.036621 | 122.3282 | -0.20599 | 0.073242 | 121.5637 | 6.5872 | 0.80566 | 0.84228 | 122.4564 | -0.24261 | -0.1236 | 0.041199 | 0.045776 | 0.15564 | -0.72327 | -0.16022 | 0.16937 | 0.16937 | 0.88806 | 0.92468 | 121.6461 | 122.4106 | 0.045776 | 122.5388 | 6.6696 | -0.16022 | 122.4106 | 0.045776 | 6.6696 | 121.6461 | 122.5388 | -122.493 | -122.5296
3804.6875 | 122.4197 | -0.068665 | 122.2321 | 0.061417 | 0.011551 | -0.0093461 | 0.01233 | 0.048832 | -0.012886 | 0.063912 | 0.054932 | 122.3282 | -0.16022 | 0.13733 | 121.6232 | 6.5369 | 0.3067 | 0.6546 | 122.4152 | -0.20142 | -0.091552 | 0.09613 | 0.1236 | 0.20599 | -0.60883 | -0.13275 | 0.1831 | 0.21515 | 0.37537 | 0.72327 | 121.6919 | 122.3969 | 0.1236 | 122.4838 | 6.6055 | -0.13275 | 122.3969 | 0.1236 | 6.6055 | 121.6919 | 122.4838 | -122.3923 | -122.4335
3806.4531 | 122.4701 | -0.045776 | 122.2275 | 0.10719 | 0.0087734 | -0.014046 | 0.01468 | 0.045414 | -0.014167 | 0.06498 | -0.045776 | 122.3236 | -0.21973 | 0.054932 | 121.5317 | 6.459 | 0.45319 | 0.55847 | 122.4518 | -0.24261 | -0.17395 | 0.09613 | 0 | 0.10071 | -0.6958 | -0.19684 | 0.2243 | 0.17395 | 0.49896 | 0.60425 | 121.5775 | 122.3694 | 0 | 122.4976 | 6.5048 | -0.19684 | 122.3694 | 0 | 6.5048 | 121.5775 | 122.4976 | -122.4472 | -122.4701
3808.2188 | 122.438 | -0.068665 | 122.2549 | 0.12245 | 0.007919 | -0.014687 | 0.011689 | 0.047337 | -0.013099 | 0.067116 | 0.059509 | 122.3145 | -0.15106 | 0.16022 | 121.6187 | 6.5643 | 0.30212 | 0.65918 | 122.4289 | -0.1831 | -0.082397 | 0.059509 | 0.12817 | 0.22888 | -0.63629 | -0.11444 | 0.17395 | 0.21057 | 0.37079 | 0.72784 | 121.6873 | 122.3831 | 0.12817 | 122.4976 | 6.633 | -0.11444 | 122.3831 | 0.12817 | 6.633 | 121.6873 | 122.4976 | -122.406 | -122.438
3809.9219 | 122.3602 | -0.086975 | 122.3053 | -0.18272 | 0.0072782 | -0.01255 | 0.0093396 | 0.045414 | -0.013099 | 0.066689 | 0.032043 | 122.2687 | -0.14648 | 0.12817 | 121.6278 | 6.7108 | 0.75073 | 1.0025 | 122.4335 | -0.22888 | -0.059509 | -0.036621 | 0.11902 | 0.21515 | -0.67749 | -0.14191 | 0.12817 | 0.17853 | 0.83771 | 1.0895 | 121.7148 | 122.3557 | 0.11902 | 122.5204 | 6.7978 | -0.14191 | 122.3557 | 0.11902 | 6.7978 | 121.7148 | 122.5204 | -122.4518 | -122.5342
3811.6875 | 122.4289 | -0.059509 | 122.2229 | 0.091934 | 0.0070646 | -0.0097733 | 0.011689 | 0.045628 | -0.01374 | 0.067116 | 0.022888 | 122.2733 | -0.15106 | 0.13275 | 121.6095 | 6.5918 | 0.35248 | 0.71411 | 122.4152 | -0.21057 | -0.091553 | 0.050354 | 0.082397 | 0.19226 | -0.6134 | -0.15106 | 0.19226 | 0.17395 | 0.41199 | 0.77362 | 121.669 | 122.3328 | 0.082397 | 122.4747 | 6.6513 | -0.15106 | 122.3328 | 0.082397 | 6.6513 | 121.669 | 122.4747 | -122.374 | -122.4335
3813.4531 | 122.4701 | -0.059509 | 122.2321 | 0.10719 | 0.009628 | -0.012978 | 0.010835 | 0.044132 | -0.012458 | 0.065834 | 0.041199 | 122.2961 | -0.15564 | 0.1236 | 121.6003 | 6.5781 | 0.42114 | 0.71869 | 122.4152 | -0.21515 | -0.096131 | 0.064087 | 0.10071 | 0.1831 | -0.63171 | -0.15564 | 0.1831 | 0.19684 | 0.48065 | 0.7782 | 121.6599 | 122.3557 | 0.10071 | 122.4747 | 6.6376 | -0.15564 | 122.3557 | 0.10071 | 6.6376 | 121.6599 | 122.4747 | -122.3877 | -122.4472
3815.1562 | 122.3648 | -0.073242 | 122.2961 | -0.19035 | 0.010482 | -0.015114 | 0.016603 | 0.046055 | -0.015022 | 0.064125 | -0.041199 | 122.3236 | -0.20142 | 0.059509 | 121.5637 | 6.6788 | 0.80109 | 0.85144 | 122.4976 | -0.25177 | -0.12817 | 0.027465 | 0.032043 | 0.13275 | -0.73242 | -0.17853 | 0.20142 | 0.16022 | 0.87433 | 0.92468 | 121.637 | 122.3968 | 0.032043 | 122.5708 | 6.752 | -0.17853 | 122.3968 | 0.032043 | 6.752 | 121.637 | 122.5708 | -122.4976 | -122.5479
3816.9219 | 122.4838 | -0.064087 | 122.2321 | -0.014877 | 0.0092008 | -0.015755 | 0.0078442 | 0.047978 | -0.013099 | 0.06498 | 0.022888 | 122.287 | -0.15106 | 0.11902 | 121.6003 | 6.6238 | 0.53101 | 0.7782 | 122.4518 | -0.20599 | -0.086975 | 0.054931 | 0.086975 | 0.18311 | -0.63171 | -0.14191 | 0.21973 | 0.17395 | 0.59509 | 0.84228 | 121.6644 | 122.3511 | 0.086975 | 122.5159 | 6.6879 | -0.14191 | 122.3511 | 0.086975 | 6.6879 | 121.6644 | 122.5159 | -122.3831 | -122.4381
3818.6875 | 122.3648 | -0.091553 | 122.287 | -0.25902 | 0.0081326 | -0.0087051 | 0.012117 | 0.046055 | -0.013527 | 0.063484 | 0.045776 | 122.3053 | -0.17395 | 0.13733 | 121.6095 | 6.752 | 0.78735 | 0.97961 | 122.4426 | -0.22888 | -0.082397 | 0.018311 | 0.13733 | 0.22888 | -0.67749 | -0.13733 | 0.15564 | 0.21973 | 0.87891 | 1.0712 | 121.7011 | 122.3969 | 0.13733 | 122.5342 | 6.8436 | -0.13733 | 122.3969 | 0.13733 | 6.8436 | 121.7011 | 122.5342 | -122.4609 | -122.5159
3820.3906 | 122.3511 | -0.10071 | 122.2916 | -0.053024 | 0.011337 | -0.0089189 | 0.017457 | 0.04755 | -0.014595 | 0.066475 | 0.013733 | 122.2916 | -0.20142 | 0.10986 | 121.5637 | 6.6696 | 0.60883 | 0.75531 | 122.4609 | -0.23346 | -0.10071 | 0 | 0.11444 | 0.21057 | -0.72784 | -0.13275 | 0.16937 | 0.21515 | 0.70953 | 0.85602 | 121.6644 | 122.3923 | 0.11444 | 122.5616 | 6.7703 | -0.13275 | 122.3923 | 0.11444 | 6.7703 | 121.6644 | 122.5616 | -122.493 | -122.525
3822.1719 | 122.3328 | -0.082397 | 122.2733 | -0.16747 | 0.009628 | -0.014259 | 0.0097668 | 0.04691 | -0.014167 | 0.065193 | 0.073242 | 122.2733 | -0.13733 | 0.16022 | 121.6919 | 6.8024 | 0.65918 | 0.99792 | 122.438 | -0.20599 | -0.054932 | 0 | 0.15564 | 0.24261 | -0.58136 | -0.1236 | 0.1648 | 0.21057 | 0.74158 | 1.0803 | 121.7743 | 122.3557 | 0.15564 | 122.5204 | 6.8848 | -0.1236 | 122.3557 | 0.15564 | 6.8848 | 121.7743 | 122.5204 | -122.4106 | -122.4792
3823.9375 | 122.3923 | -0.091553 | 122.2641 | -0.25902 | 0.0092008 | -0.015541 | 0.013612 | 0.046269 | -0.012458 | 0.065193 | -0.004578 | 122.3007 | -0.17395 | 0.07782 | 121.5591 | 6.7703 | 0.83771 | 0.92468 | 122.4747 | -0.25635 | -0.082397 | 0.036621 | 0.086975 | 0.16937 | -0.70496 | -0.1648 | 0.21057 | 0.16937 | 0.92926 | 1.0162 | 121.6507 | 122.3923 | 0.086975 | 122.5662 | 6.8619 | -0.1648 | 122.3923 | 0.086975 | 6.8619 | 121.6507 | 122.5662 | -122.438 | -122.5204
3825.7031 | 122.3557 | -0.10529 | 122.2687 | -0.18272 | 0.0055692 | -0.016823 | 0.010835 | 0.046696 | -0.011818 | 0.066262 | 0.050354 | 122.2961 | -0.16022 | 0.16022 | 121.6553 | 6.839 | 0.6546 | 1.0254 | 122.4289 | -0.21515 | -0.054931 | 0.027466 | 0.15564 | 0.2655 | -0.6134 | -0.10986 | 0.16022 | 0.21057 | 0.75989 | 1.1307 | 121.7606 | 122.4014 | 0.15564 | 122.5342 | 6.9443 | -0.10986 | 122.4014 | 0.15564 | 6.9443 | 121.7606 | 122.5342 | -122.4289 | -122.4838
3827.4219 | 122.4106 | -0.07782 | 122.2916 | -0.19798 | 0.010055 | -0.012337 | 0.011049 | 0.046482 | -0.012031 | 0.066048 | 0.041199 | 122.2687 | -0.14648 | 0.1831 | 121.6782 | 6.8161 | 0.6134 | 0.97046 | 122.438 | -0.20599 | -0.068664 | -0.022888 | 0.11902 | 0.26092 | -0.6134 | -0.12817 | 0.14648 | 0.18768 | 0.69122 | 1.0483 | 121.756 | 122.3465 | 0.11902 | 122.5159 | 6.8939 | -0.12817 | 122.3465 | 0.11902 | 6.8939 | 121.756 | 122.5159 | -122.438 | -122.4976
3829.1875 | 122.3831 | -0.086975 | 122.2778 | -0.25902 | 0.0098416 | -0.012337 | 0.013826 | 0.045841 | -0.012245 | 0.067757 | -0.064087 | 122.3053 | -0.20142 | 0.054932 | 121.5317 | 6.7566 | 0.86975 | 0.88348 | 122.4792 | -0.24719 | -0.11444 | 0.027466 | 0.022888 | 0.14191 | -0.74616 | -0.16022 | 0.20142 | 0.13733 | 0.95673 | 0.97046 | 121.6187 | 122.3923 | 0.022888 | 122.5662 | 6.8436 | -0.16022 | 122.3923 | 0.022888 | 6.8436 | 121.6187 | 122.5662 | -122.4792 | -122.525
3830.9531 | 122.3969 | -0.082397 | 122.2733 | -0.24376 | 0.01091 | -0.015327 | 0.015962 | 0.04691 | -0.01139 | 0.063484 | -0.064087 | 122.3282 | -0.19684 | 0.045776 | 121.5363 | 6.7703 | 0.8606 | 0.89264 | 122.4655 | -0.25177 | -0.11444 | 0.054932 | 0.01831 | 0.12817 | -0.737 | -0.16937 | 0.19226 | 0.13275 | 0.94299 | 0.97504 | 121.6187 | 122.4106 | 0.01831 | 122.5479 | 6.8527 | -0.16937 | 122.4106 | 0.01831 | 6.8527 | 121.6187 | 122.5479 | -122.4701 | -122.525
3832.7344 | 122.4197 | -0.059509 | 122.2549 | 0.16823 | 0.0074918 | -0.010628 | 0.013185 | 0.049046 | -0.012672 | 0.064553 | 0.082397 | 122.319 | -0.14191 | 0.16479 | 121.6415 | 6.7429 | 0.3067 | 0.70038 | 122.4472 | -0.19226 | -0.082398 | 0.064087 | 0.14191 | 0.2243 | -0.6134 | -0.13275 | 0.19226 | 0.2243 | 0.36621 | 0.75989 | 121.7011 | 122.3785 | 0.14191 | 122.5067 | 6.8024 | -0.13275 | 122.3785 | 0.14191 | 6.8024 | 121.7011 | 122.5067 | -122.3969 | -122.4472
3834.5 | 122.3511 | -0.10071 | 122.2733 | -0.13695 | 0.0098416 | -0.011269 | 0.010194 | 0.04755 | -0.01075 | 0.065407 | 0.07782 | 122.287 | -0.15564 | 0.19226 | 121.6919 | 6.8985 | 0.64545 | 1.0025 | 122.4472 | -0.20599 | -0.054932 | 0.013733 | 0.17853 | 0.29297 | -0.58136 | -0.10529 | 0.17395 | 0.23346 | 0.74616 | 1.1032 | 121.7926 | 122.3877 | 0.17853 | 122.5479 | 6.9992 | -0.10529 | 122.3877 | 0.17853 | 6.9992 | 121.7926 | 122.5479 | -122.4289 | -122.4792
3836.2656 | 122.3328 | -0.082397 | 122.2641 | -0.18272 | 0.0087734 | -0.010841 | 0.016176 | 0.04691 | -0.013954 | 0.065834 | -0.013733 | 122.3328 | -0.20142 | 0.11444 | 121.5683 | 6.839 | 0.737 | 0.8606 | 122.4701 | -0.23804 | -0.11902 | 0.068665 | 0.068664 | 0.19684 | -0.6958 | -0.15564 | 0.20599 | 0.18768 | 0.8194 | 0.94299 | 121.6507 | 122.4152 | 0.068664 | 122.5525 | 6.9214 | -0.15564 | 122.4152 | 0.068664 | 6.9214 | 121.6507 | 122.5525 | -122.4655 | -122.5021
3838.0312 | 122.5021 | -0.054932 | 122.2595 | 0.038529 | 0.0085598 | -0.01255 | 0.009126 | 0.045628 | -0.01075 | 0.063698 | -0.004578 | 122.3145 | -0.17395 | 0.091553 | 121.6095 | 6.7749 | 0.52185 | 0.76446 | 122.4243 | -0.21057 | -0.11902 | 0.054932 | 0.050354 | 0.14649 | -0.65002 | -0.15564 | 0.16479 | 0.16937 | 0.57678 | 0.8194 | 121.6644 | 122.3694 | 0.050354 | 122.4792 | 6.8298 | -0.15564 | 122.3694 | 0.050354 | 6.8298 | 121.6644 | 122.4792 | -122.4335 | -122.4701
3839.7344 | 122.4747 | -0.045776 | 122.2412 | 0.13008 | 0.011337 | -0.0097733 | 0.017244 | 0.044987 | -0.010536 | 0.066902 | -0.054932 | 122.3282 | -0.19684 | 0.027466 | 121.5134 | 6.6879 | 0.48065 | 0.55847 | 122.4655 | -0.23346 | -0.15106 | 0.086975 | -0.009156 | 0.073242 | -0.72784 | -0.18768 | 0.2243 | 0.14191 | 0.52643 | 0.60425 | 121.5591 | 122.374 | -0.009156 | 122.5113 | 6.7337 | -0.18768 | 122.374 | -0.009156 | 6.7337 | 121.5591 | 122.5113 | -122.438 | -122.4747
3841.4844 | 122.4243 | -0.068665 | 122.2458 | 0.13771 | 0.0064236 | -0.014687 | 0.013826 | 0.049473 | -0.014167 | 0.067757 | 0.054932 | 122.2412 | -0.17853 | 0.15564 | 121.637 | 6.7932 | 0.3067 | 0.71411 | 122.4426 | -0.18768 | -0.10986 | -0.004578 | 0.1236 | 0.22431 | -0.60883 | -0.11902 | 0.19684 | 0.23346 | 0.37537 | 0.78278 | 121.7056 | 122.3099 | 0.1236 | 122.5113 | 6.8619 | -0.11902 | 122.3099 | 0.1236 | 6.8619 | 121.7056 | 122.5113 | -122.4243 | -122.4335
3843.25 | 122.4335 | -0.064087 | 122.2275 | 0.16823 | 0.012619 | -0.0097733 | 0.015748 | 0.048405 | -0.013954 | 0.066475 | -0.004578 | 122.3465 | -0.16937 | 0.10529 | 121.5637 | 6.752 | 0.38452 | 0.60425 | 122.493 | -0.21515 | -0.10529 | 0.11902 | 0.059509 | 0.16937 | -0.66376 | -0.15106 | 0.2655 | 0.16479 | 0.44861 | 0.66834 | 121.6278 | 122.4106 | 0.059509 | 122.5571 | 6.8161 | -0.15106 | 122.4106 | 0.059509 | 6.8161 | 121.6278 | 122.5571 | -122.3969 | -122.4426
3845.0156 | 122.3923 | -0.07782 | 122.2687 | -0.22087 | 0.010269 | -0.0149 | 0.011903 | 0.048191 | -0.012672 | 0.06498 | -0.036621 | 122.3373 | -0.19226 | 0.073242 | 121.55 | 6.8848 | 0.84686 | 0.9201 | 122.493 | -0.23804 | -0.11444 | 0.068664 | 0.041199 | 0.15106 | -0.71869 | -0.16022 | 0.2243 | 0.15564 | 0.92468 | 0.99792 | 121.6278 | 122.4152 | 0.041199 | 122.5708 | 6.9626 | -0.16022 | 122.4152 | 0.041199 | 6.9626 | 121.6278 | 122.5708 | -122.4609 | -122.5067
3846.7188 | 122.3877 | -0.091553 | 122.2824 | -0.19798 | 0.0055692 | -0.016823 | 0.011476 | 0.049046 | -0.014167 | 0.064766 | -0.064087 | 122.3099 | -0.20142 | 0.064087 | 121.55 | 6.8893 | 0.86517 | 0.92926 | 122.5021 | -0.23346 | -0.10986 | 0.027465 | 0.027466 | 0.15564 | -0.73242 | -0.14191 | 0.21973 | 0.13733 | 0.95673 | 1.0208 | 121.6415 | 122.4014 | 0.027466 | 122.5937 | 6.9809 | -0.14191 | 122.4014 | 0.027466 | 6.9809 | 121.6415 | 122.5937 | -122.4838 | -122.5159
3848.4844 | 122.4472 | -0.059509 | 122.2778 | 0.099564 | 0.0083462 | -0.013405 | 0.011262 | 0.047337 | -0.011818 | 0.06733 | 0.050354 | 122.3099 | -0.13733 | 0.14191 | 121.6095 | 6.8527 | 0.3891 | 0.737 | 122.3923 | -0.21515 | -0.07782 | 0.032043 | 0.10986 | 0.20142 | -0.66833 | -0.15564 | 0.11444 | 0.18768 | 0.44861 | 0.79651 | 121.669 | 122.3694 | 0.10986 | 122.4518 | 6.9122 | -0.15564 | 122.3694 | 0.10986 | 6.9122 | 121.669 | 122.4518 | -122.4152 | -122.493
3850.1719 | 122.3602 | -0.10071 | 122.2916 | -0.21324 | 0.009628 | -0.012337 | 0.013185 | 0.046269 | -0.011818 | 0.065834 | 0.059509 | 122.3236 | -0.16479 | 0.17853 | 121.6553 | 7.0312 | 0.70038 | 1.0345 | 122.4014 | -0.21057 | -0.064087 | 0.032043 | 0.16022 | 0.27924 | -0.63629 | -0.10986 | 0.10986 | 0.2243 | 0.80109 | 1.1353 | 121.756 | 122.4243 | 0.16022 | 122.5021 | 7.132 | -0.10986 | 122.4243 | 0.16022 | 7.132 | 121.756 | 122.5021 | -122.4564 | -122.5021
3851.9375 | 122.3923 | -0.091553 | 122.2916 | -0.24376 | 0.0085598 | -0.013618 | 0.012544 | 0.045201 | -0.01139 | 0.065834 | -0.050354 | 122.3282 | -0.23346 | 0.045776 | 121.5546 | 6.9443 | 0.88806 | 0.91095 | 122.438 | -0.24261 | -0.14191 | 0.036621 | 0.041199 | 0.13733 | -0.737 | -0.15106 | 0.14648 | 0.1831 | 0.97962 | 1.0025 | 121.6461 | 122.4197 | 0.041199 | 122.5296 | 7.0358 | -0.15106 | 122.4197 | 0.041199 | 7.0358 | 121.6461 | 122.5296 | -122.525 | -122.5342
3853.7031 | 122.438 | -0.068665 | 122.2824 | 0.038529 | 0.0087734 | -0.011696 | 0.015535 | 0.049046 | -0.010322 | 0.066262 | 0.059509 | 122.3145 | -0.17853 | 0.15106 | 121.6187 | 6.8939 | 0.3479 | 0.70038 | 122.4014 | -0.20599 | -0.10986 | 0.032043 | 0.12817 | 0.21973 | -0.66376 | -0.13733 | 0.11902 | 0.23804 | 0.41656 | 0.76904 | 121.6873 | 122.3831 | 0.12817 | 122.4701 | 6.9626 | -0.13733 | 122.3831 | 0.12817 | 6.9626 | 121.6873 | 122.4701 | -122.4609 | -122.4884
3855.4531 | 122.3923 | -0.09613 | 122.2687 | -0.13695 | 0.0085598 | -0.016182 | 0.0099804 | 0.044987 | -0.0094678 | 0.066902 | 0.045776 | 122.3053 | -0.14191 | 0.16022 | 121.669 | 7.0358 | 0.63171 | 0.97504 | 122.3831 | -0.21515 | -0.045777 | 0.036621 | 0.14191 | 0.25635 | -0.59967 | -0.11902 | 0.11444 | 0.18768 | 0.72784 | 1.0712 | 121.7651 | 122.4014 | 0.14191 | 122.4792 | 7.132 | -0.11902 | 122.4014 | 0.14191 | 7.132 | 121.7651 | 122.4792 | -122.4106 | -122.4838
3857.1719 | 122.3831 | -0.086975 | 122.2824 | -0.19798 | 0.0072782 | -0.014046 | 0.01233 | 0.043492 | -0.015022 | 0.065834 | -0.059509 | 122.2961 | -0.18768 | 0.059509 | 121.5408 | 6.9672 | 0.88806 | 0.91095 | 122.4838 | -0.23804 | -0.10071 | 0.013733 | 0.027466 | 0.14648 | -0.74158 | -0.15106 | 0.20142 | 0.12817 | 0.97504 | 0.99793 | 121.6278 | 122.3831 | 0.027466 | 122.5708 | 7.0541 | -0.15106 | 122.3831 | 0.027466 | 7.0541 | 121.6278 | 122.5708 | -122.4701 | -122.5204
3858.9375 | 122.4289 | -0.064087 | 122.2366 | 0.15297 | 0.00621 | -0.011482 | 0.013398 | 0.048191 | -0.013527 | 0.065621 | 0.059509 | 122.3007 | -0.16937 | 0.16022 | 121.6324 | 6.9305 | 0.31586 | 0.72327 | 122.4197 | -0.20142 | -0.10529 | 0.064087 | 0.1236 | 0.2243 | -0.60425 | -0.13733 | 0.18311 | 0.22888 | 0.37994 | 0.78735 | 121.6965 | 122.3648 | 0.1236 | 122.4838 | 6.9946 | -0.13733 | 122.3648 | 0.1236 | 6.9946 | 121.6965 | 122.4838 | -122.406 | -122.438
3860.6875 | 122.4518 | -0.054932 | 122.2549 | 0.13008 | 0.0083462 | -0.0097733 | 0.0097668 | 0.044346 | -0.011604 | 0.065834 | 0.032043 | 122.2687 | -0.16022 | 0.13275 | 121.6049 | 6.9214 | 0.45319 | 0.74158 | 122.4426 | -0.19684 | -0.10528 | 0.013733 | 0.086975 | 0.18768 | -0.65002 | -0.14191 | 0.18768 | 0.19226 | 0.50812 | 0.79651 | 121.6599 | 122.3236 | 0.086975 | 122.4976 | 6.9763 | -0.14191 | 122.3236 | 0.086975 | 6.9763 | 121.6599 | 122.4976 | -122.4152 | -122.4518
3862.3906 | 122.3511 | -0.11444 | 122.2778 | -0.22087 | 0.0085598 | -0.013618 | 0.011903 | 0.043492 | -0.011177 | 0.067757 | 0.050354 | 122.2778 | -0.15106 | 0.17853 | 121.6736 | 7.1136 | 0.6958 | 1.0574 | 122.3831 | -0.21973 | -0.036621 | 0 | 0.16479 | 0.29297 | -0.60425 | -0.10529 | 0.10529 | 0.20142 | 0.81024 | 1.1719 | 121.788 | 122.3923 | 0.16479 | 122.4976 | 7.2281 | -0.10529 | 122.3923 | 0.16479 | 7.2281 | 121.788 | 122.4976 | -122.4289 | -122.4976
3864.1562 | 122.319 | -0.11902 | 122.2641 | -0.091171 | 0.011978 | -0.015114 | 0.017457 | 0.049046 | -0.014595 | 0.063912 | 0.018311 | 122.3007 | -0.19684 | 0.12817 | 121.5775 | 7.0358 | 0.6546 | 0.82855 | 122.4884 | -0.23804 | -0.077819 | 0.036621 | 0.13733 | 0.24719 | -0.68664 | -0.11902 | 0.2243 | 0.21515 | 0.77362 | 0.94757 | 121.6965 | 122.4197 | 0.13733 | 122.6074 | 7.1548 | -0.11902 | 122.4197 | 0.13733 | 7.1548 | 121.6965 | 122.6074 | -122.4609 | -122.5021
3865.8594 | 122.4197 | -0.068665 | 122.2549 | 0.12245 | 0.0094144 | -0.011696 | 0.013185 | 0.048191 | -0.011177 | 0.066689 | 0.059509 | 122.3145 | -0.15106 | 0.16479 | 121.6324 | 6.9855 | 0.36163 | 0.72784 | 122.4426 | -0.21973 | -0.082397 | 0.059509 | 0.12817 | 0.23346 | -0.62256 | -0.15106 | 0.18768 | 0.21057 | 0.4303 | 0.79651 | 121.701 | 122.3831 | 0.12817 | 122.5113 | 7.0541 | -0.15106 | 122.3831 | 0.12817 | 7.0541 | 121.701 | 122.5113 | -122.406 | -122.4747
3867.6406 | 122.4518 | -0.064087 | 122.2412 | 0.061417 | 0.0083462 | -0.013618 | 0.015962 | 0.050968 | -0.015449 | 0.065407 | -0.045776 | 122.3282 | -0.19226 | 0.041199 | 121.5042 | 6.9077 | 0.57678 | 0.59509 | 122.5021 | -0.23804 | -0.12817 | 0.086975 | 0.018311 | 0.10529 | -0.737 | -0.17395 | 0.26092 | 0.14648 | 0.64087 | 0.65918 | 121.5683 | 122.3923 | 0.018311 | 122.5662 | 6.9717 | -0.17395 | 122.3923 | 0.018311 | 6.9717 | 121.5683 | 122.5662 | -122.4335 | -122.4792
3869.4219 | 122.3465 | -0.10529 | 122.2687 | -0.083542 | 0.010055 | -0.012123 | 0.014894 | 0.047978 | -0.016304 | 0.065407 | 0.013733 | 122.2916 | -0.21057 | 0.12817 | 121.5775 | 7.0587 | 0.6546 | 0.8194 | 122.4792 | -0.23804 | -0.10529 | 0.022888 | 0.11902 | 0.23346 | -0.69122 | -0.13275 | 0.21057 | 0.2243 | 0.75989 | 0.92468 | 121.6827 | 122.3969 | 0.11902 | 122.5845 | 7.164 | -0.13275 | 122.3969 | 0.11902 | 7.164 | 121.6827 | 122.5845 | -122.4792 | -122.5067
3871.1875 | 122.4289 | -0.082397 | 122.2687 | 0.02327 | 0.0089872 | -0.011909 | 0.015962 | 0.050114 | -0.013954 | 0.067116 | -0.050354 | 122.3236 | -0.20142 | 0.041199 | 121.5179 | 6.9717 | 0.59052 | 0.63629 | 122.4838 | -0.24719 | -0.11902 | 0.054931 | 0.032043 | 0.1236 | -0.75073 | -0.16479 | 0.21515 | 0.15106 | 0.67291 | 0.71869 | 121.6003 | 122.406 | 0.032043 | 122.5662 | 7.0541 | -0.16479 | 122.406 | 0.032043 | 7.0541 | 121.6003 | 122.5662 | -122.4701 | -122.5159
3872.8906 | 122.3419 | -0.09613 | 122.2778 | -0.14458 | 0.0081326 | -0.012764 | 0.015107 | 0.049046 | -0.013527 | 0.064339 | -0.004578 | 122.3053 | -0.19226 | 0.086975 | 121.582 | 7.132 | 0.737 | 0.86975 | 122.4747 | -0.23804 | -0.096131 | 0.027466 | 0.091552 | 0.1831 | -0.6958 | -0.14191 | 0.19684 | 0.18768 | 0.83313 | 0.96588 | 121.6782 | 122.4014 | 0.091552 | 122.5708 | 7.2281 | -0.14191 | 122.4014 | 0.091552 | 7.2281 | 121.6782 | 122.5708 | -122.4701 | -122.5159
3874.6406 | 122.3511 | -0.086975 | 122.2824 | -0.091171 | 0.0085598 | -0.014259 | 0.013398 | 0.047337 | -0.014808 | 0.066689 | 0.013733 | 122.3099 | -0.19684 | 0.10529 | 121.582 | 7.1091 | 0.65002 | 0.80109 | 122.4609 | -0.21973 | -0.10986 | 0.027465 | 0.10071 | 0.19226 | -0.70038 | -0.13275 | 0.17853 | 0.21057 | 0.737 | 0.88806 | 121.669 | 122.3969 | 0.10071 | 122.5479 | 7.196 | -0.13275 | 122.3969 | 0.10071 | 7.196 | 121.669 | 122.5479 | -122.4792 | -122.5021
3876.3281 | 122.4152 | -0.059509 | 122.2321 | 0.12245 | 0.0087734 | -0.010628 | 0.010194 | 0.047123 | -0.011604 | 0.065621 | 0.054932 | 122.3099 | -0.15564 | 0.15106 | 121.6278 | 7.0587 | 0.37994 | 0.73242 | 122.438 | -0.20142 | -0.096131 | 0.077819 | 0.11444 | 0.21057 | -0.60425 | -0.14191 | 0.20599 | 0.21057 | 0.43945 | 0.79193 | 121.6873 | 122.3694 | 0.11444 | 122.4976 | 7.1182 | -0.14191 | 122.3694 | 0.11444 | 7.1182 | 121.6873 | 122.4976 | -122.3877 | -122.4335
3878.0938 | 122.4564 | -0.07782 | 122.2458 | 0.038529 | 0.0098416 | -0.0084915 | 0.016389 | 0.048191 | -0.015876 | 0.065407 | -0.054932 | 122.3236 | -0.19684 | 0.036621 | 121.5134 | 7.0038 | 0.60425 | 0.63171 | 122.4747 | -0.23804 | -0.11902 | 0.077819 | 0.022888 | 0.11444 | -0.73242 | -0.16022 | 0.22888 | 0.14191 | 0.68207 | 0.70953 | 121.5912 | 122.4014 | 0.022888 | 122.5525 | 7.0816 | -0.16022 | 122.4014 | 0.022888 | 7.0816 | 121.5912 | 122.5525 | -122.4426 | -122.4838
3879.8438 | 122.4701 | -0.045776 | 122.2366 | 0.11482 | 0.0098416 | -0.012764 | 0.014039 | 0.049046 | -0.014167 | 0.066475 | -0.045776 | 122.3053 | -0.20599 | 0.032043 | 121.5225 | 6.9946 | 0.50812 | 0.58594 | 122.4976 | -0.23804 | -0.16022 | 0.068665 | 0 | 0.077819 | -0.71411 | -0.19226 | 0.26093 | 0.16022 | 0.55389 | 0.63171 | 121.5683 | 122.3511 | 0 | 122.5433 | 7.0404 | -0.19226 | 122.3511 | 0 | 7.0404 | 121.5683 | 122.5433 | -122.4426 | -122.4747
3881.5938 | 122.4655 | -0.059509 | 122.2366 | 0.091934 | 0.009628 | -0.014473 | 0.013185 | 0.047764 | -0.013954 | 0.067543 | -0.050354 | 122.3053 | -0.20599 | 0.032043 | 121.5271 | 7.0129 | 0.49896 | 0.59509 | 122.493 | -0.24719 | -0.14649 | 0.068665 | 0.009155 | 0.091552 | -0.70953 | -0.18768 | 0.25635 | 0.15564 | 0.55847 | 0.6546 | 121.5866 | 122.3648 | 0.009155 | 122.5525 | 7.0724 | -0.18768 | 122.3648 | 0.009155 | 7.0724 | 121.5866 | 122.5525 | -122.4426 | -122.4838
3883.2969 | 122.4197 | -0.041199 | 122.2229 | 0.40474 | 0.010269 | -0.010841 | 0.01233 | 0.051396 | -0.015236 | 0.06797 | 0.064087 | 122.2961 | -0.15564 | 0.14191 | 121.6232 | 7.1045 | 0.3479 | 0.70953 | 122.438 | -0.20142 | -0.11444 | 0.073243 | 0.10529 | 0.18311 | -0.59967 | -0.16022 | 0.21515 | 0.21973 | 0.3891 | 0.75073 | 121.6644 | 122.3373 | 0.10529 | 122.4792 | 7.1457 | -0.16022 | 122.3373 | 0.10529 | 7.1457 | 121.6644 | 122.4792 | -122.3785 | -122.4243
3885.0469 | 122.3648 | -0.091553 | 122.2733 | -0.11406 | 0.007919 | -0.0097733 | 0.0082714 | 0.04456 | -0.011818 | 0.065407 | 0.059509 | 122.3099 | -0.14191 | 0.16479 | 121.669 | 7.2784 | 0.64087 | 1.0162 | 122.3923 | -0.23346 | -0.050354 | 0.036621 | 0.15106 | 0.25635 | -0.60425 | -0.14191 | 0.11902 | 0.20142 | 0.73242 | 1.1078 | 121.7606 | 122.4014 | 0.15106 | 122.4838 | 7.37 | -0.14191 | 122.4014 | 0.15106 | 7.37 | 121.7606 | 122.4838 | -122.4152 | -122.5067
3886.8125 | 122.3282 | -0.10071 | 122.2778 | -0.12169 | 0.0070646 | -0.013618 | 0.016176 | 0.046696 | -0.013954 | 0.065834 | -0.013733 | 122.2824 | -0.19226 | 0.09613 | 121.582 | 7.2144 | 0.70953 | 0.86975 | 122.4472 | -0.22888 | -0.091553 | 0.004578 | 0.086975 | 0.19684 | -0.6958 | -0.12817 | 0.16937 | 0.17853 | 0.81024 | 0.97046 | 121.6827 | 122.3831 | 0.086975 | 122.5479 | 7.3151 | -0.12817 | 122.3831 | 0.086975 | 7.3151 | 121.6827 | 122.5479 | -122.4701 | -122.5067
3888.5781 | 122.3465 | -0.11444 | 122.2504 | -0.14458 | 0.009628 | -0.012337 | 0.011476 | 0.045841 | -0.010536 | 0.064553 | 0.073242 | 122.3007 | -0.16022 | 0.16937 | 121.6827 | 7.2922 | 0.68207 | 1.0529 | 122.4197 | -0.21057 | -0.045776 | 0.050354 | 0.18768 | 0.28381 | -0.56763 | -0.09613 | 0.16937 | 0.23346 | 0.79651 | 1.1673 | 121.7972 | 122.4152 | 0.18768 | 122.5342 | 7.4066 | -0.09613 | 122.4152 | 0.18768 | 7.4066 | 121.7972 | 122.5342 | -122.4106 | -122.4609
3890.3438 | 122.4747 | -0.032043 | 122.2137 | 0.099564 | 0.0087734 | -0.013191 | 0.016816 | 0.049473 | -0.012672 | 0.068184 | -0.041199 | 122.3007 | -0.19684 | 0.050354 | 121.5317 | 7.0862 | 0.51727 | 0.60883 | 122.4838 | -0.24261 | -0.1648 | 0.086975 | -0.009156 | 0.082397 | -0.68207 | -0.21057 | 0.27008 | 0.15564 | 0.54932 | 0.64087 | 121.5637 | 122.3328 | -0.009156 | 122.5159 | 7.1182 | -0.21057 | 122.3328 | -0.009156 | 7.1182 | 121.5637 | 122.5159 | -122.4106 | -122.4564
3892.0469 | 122.4518 | -0.068665 | 122.2229 | 0.038529 | 0.0094144 | -0.012337 | 0.017457 | 0.047764 | -0.01374 | 0.066475 | -0.054932 | 122.3328 | -0.19226 | 0.036621 | 121.5042 | 7.077 | 0.59509 | 0.60883 | 122.4747 | -0.23346 | -0.1236 | 0.10986 | 0.013733 | 0.10529 | -0.71869 | -0.16479 | 0.25177 | 0.13733 | 0.66376 | 0.67749 | 121.5729 | 122.4014 | 0.013733 | 122.5433 | 7.1457 | -0.16479 | 122.4014 | 0.013733 | 7.1457 | 121.5729 | 122.5433 | -122.4152 | -122.4564
3893.75 | 122.438 | -0.068665 | 122.2366 | 0.1606 | 0.0089872 | -0.011482 | 0.013826 | 0.048405 | -0.012458 | 0.066902 | -0.004578 | 122.319 | -0.16479 | 0.12817 | 121.6141 | 7.1915 | 0.3479 | 0.68665 | 122.438 | -0.19684 | -0.09613 | 0.082398 | 0.064087 | 0.19684 | -0.62256 | -0.12817 | 0.20142 | 0.16022 | 0.41656 | 0.75531 | 121.6827 | 122.3877 | 0.064087 | 122.5067 | 7.2601 | -0.12817 | 122.3877 | 0.064087 | 7.2601 | 121.6827 | 122.5067 | -122.4014 | -122.4335
3895.5 | 122.3511 | -0.086975 | 122.2549 | -0.053024 | 0.0098416 | -0.011482 | 0.014894 | 0.048191 | -0.013313 | 0.064766 | 0.013733 | 122.2961 | -0.20599 | 0.09613 | 121.5591 | 7.2098 | 0.64087 | 0.76904 | 122.4838 | -0.2243 | -0.11902 | 0.041199 | 0.10071 | 0.1831 | -0.6958 | -0.13733 | 0.22888 | 0.21973 | 0.72784 | 0.85602 | 121.6461 | 122.3831 | 0.10071 | 122.5708 | 7.2968 | -0.13733 | 122.3831 | 0.10071 | 7.2968 | 121.6461 | 122.5708 | -122.4609 | -122.4792
3897.25 | 122.3694 | -0.086975 | 122.2504 | -0.030136 | 0.0072782 | -0.014473 | 0.015748 | 0.050968 | -0.012886 | 0.066475 | -0.013733 | 122.3007 | -0.18768 | 0.068665 | 121.55 | 7.2189 | 0.63171 | 0.70953 | 122.4747 | -0.23346 | -0.10071 | 0.050354 | 0.073242 | 0.15564 | -0.70038 | -0.14648 | 0.2243 | 0.17395 | 0.71869 | 0.79651 | 121.637 | 122.3877 | 0.073242 | 122.5616 | 7.3059 | -0.14648 | 122.3877 | 0.073242 | 7.3059 | 121.637 | 122.5616 | -122.438 | -122.4838
3899.0156 | 122.3969 | -0.082397 | 122.2641 | -0.21324 | 0.0098416 | -0.012764 | 0.0099804 | 0.049259 | -0.012672 | 0.067543 | -0.059509 | 122.3511 | -0.20599 | 0.036621 | 121.55 | 7.2784 | 0.90637 | 0.94757 | 122.4838 | -0.27008 | -0.1236 | 0.086975 | 0.022888 | 0.11902 | -0.71411 | -0.18768 | 0.21973 | 0.14649 | 0.98877 | 1.03 | 121.6324 | 122.4335 | 0.022888 | 122.5662 | 7.3608 | -0.18768 | 122.4335 | 0.022888 | 7.3608 | 121.6324 | 122.5662 | -122.4701 | -122.5342
3900.7656 | 122.3831 | -0.086975 | 122.2549 | -0.22087 | 0.010055 | -0.0102 | 0.01233 | 0.044773 | -0.01139 | 0.066902 | -0.059509 | 122.3648 | -0.21515 | 0.041199 | 121.5363 | 7.3059 | 0.91095 | 0.93842 | 122.4747 | -0.25635 | -0.12817 | 0.10986 | 0.027466 | 0.12817 | -0.71869 | -0.16937 | 0.21973 | 0.15564 | 0.99793 | 1.0254 | 121.6232 | 122.4518 | 0.027466 | 122.5616 | 7.3929 | -0.16937 | 122.4518 | 0.027466 | 7.3929 | 121.6232 | 122.5616 | -122.4701 | -122.5113
3902.5312 | 122.4197 | -0.050354 | 122.2733 | 0.12245 | 0.010482 | -0.014259 | 0.010194 | 0.047123 | -0.013527 | 0.067116 | 0.064087 | 122.3145 | -0.14191 | 0.14648 | 121.6461 | 7.2601 | 0.37537 | 0.75989 | 122.4335 | -0.19226 | -0.091553 | 0.041199 | 0.11444 | 0.19684 | -0.62714 | -0.14191 | 0.16022 | 0.20599 | 0.42572 | 0.81024 | 121.6965 | 122.3648 | 0.11444 | 122.4838 | 7.3105 | -0.14191 | 122.3648 | 0.11444 | 7.3105 | 121.6965 | 122.4838 | -122.4152 | -122.4655
3904.2344 | 122.4655 | -0.041199 | 122.2549 | 0.030899 | 0.0098416 | -0.013618 | 0.01703 | 0.049046 | -0.013527 | 0.065621 | -0.050354 | 122.3419 | -0.20599 | 0.013733 | 121.4951 | 7.1548 | 0.5722 | 0.63171 | 122.493 | -0.24719 | -0.1648 | 0.086975 | -0.009155 | 0.054932 | -0.75989 | -0.20599 | 0.23804 | 0.15564 | 0.6134 | 0.67291 | 121.5363 | 122.3831 | -0.009155 | 122.5342 | 7.196 | -0.20599 | 122.3831 | -0.009155 | 7.196 | 121.5363 | 122.5342 | -122.4609 | -122.5021
3906 | 122.438 | -0.064087 | 122.2504 | 0.091934 | 0.0092008 | -0.012978 | 0.011049 | 0.048191 | -0.011818 | 0.064125 | 0.045776 | 122.3053 | -0.15564 | 0.14648 | 121.6278 | 7.2739 | 0.40283 | 0.76904 | 122.4335 | -0.21057 | -0.091553 | 0.054932 | 0.10986 | 0.21057 | -0.62256 | -0.14648 | 0.18311 | 0.20142 | 0.46692 | 0.83313 | 121.6919 | 122.3694 | 0.10986 | 122.4976 | 7.338 | -0.14648 | 122.3694 | 0.10986 | 7.338 | 121.6919 | 122.4976 | -122.406 | -122.4609
3907.7656 | 122.3511 | -0.10986 | 122.3007 | -0.068283 | 0.0098416 | -0.013405 | 0.015748 | 0.049687 | -0.014381 | 0.065834 | 0.032043 | 122.3145 | -0.21057 | 0.10529 | 121.5729 | 7.3242 | 0.6546 | 0.8194 | 122.4792 | -0.2243 | -0.10071 | 0.013733 | 0.14191 | 0.21515 | -0.72784 | -0.11444 | 0.17853 | 0.24261 | 0.76447 | 0.92926 | 121.6827 | 122.4243 | 0.14191 | 122.5891 | 7.4341 | -0.11444 | 122.4243 | 0.14191 | 7.4341 | 121.6827 | 122.5891 | -122.5113 | -122.525
3909.4688 | 122.4289 | -0.050354 | 122.2641 | 0.10719 | 0.0087734 | -0.013405 | 0.011049 | 0.048405 | -0.013954 | 0.067757 | 0.059509 | 122.319 | -0.15564 | 0.15564 | 121.6232 | 7.2968 | 0.34332 | 0.72784 | 122.4518 | -0.19684 | -0.10529 | 0.054932 | 0.10986 | 0.20599 | -0.64087 | -0.14648 | 0.18768 | 0.21515 | 0.39368 | 0.7782 | 121.6736 | 122.3694 | 0.10986 | 122.5021 | 7.3471 | -0.14648 | 122.3694 | 0.10986 | 7.3471 | 121.6736 | 122.5021 | -122.4197 | -122.4609
3911.2188 | 122.4197 | -0.068665 | 122.2504 | 0.18349 | 0.010055 | -0.0091325 | 0.011476 | 0.048191 | -0.012458 | 0.065621 | 0.059509 | 122.2916 | -0.15106 | 0.14191 | 121.637 | 7.3242 | 0.3479 | 0.75073 | 122.438 | -0.19684 | -0.082397 | 0.041199 | 0.12817 | 0.21057 | -0.6134 | -0.12817 | 0.18768 | 0.21057 | 0.41656 | 0.8194 | 121.7056 | 122.3602 | 0.12817 | 122.5067 | 7.3929 | -0.12817 | 122.3602 | 0.12817 | 7.3929 | 121.7056 | 122.5067 | -122.4014 | -122.4472
3912.9219 | 122.4701 | -0.041199 | 122.2412 | 0.10719 | 0.011123 | -0.011696 | 0.015535 | 0.048405 | -0.013313 | 0.064766 | -0.041199 | 122.2916 | -0.21973 | 0.036621 | 121.5179 | 7.2189 | 0.52185 | 0.61798 | 122.4792 | -0.24261 | -0.17853 | 0.050354 | 0 | 0.07782 | -0.72327 | -0.20142 | 0.23804 | 0.17853 | 0.56305 | 0.65918 | 121.5591 | 122.3328 | 0 | 122.5204 | 7.2601 | -0.20142 | 122.3328 | 0 | 7.2601 | 121.5591 | 122.5204 | -122.4609 | -122.4838
3914.6875 | 122.3511 | -0.10529 | 122.2961 | -0.24376 | 0.0074918 | -0.013832 | 0.0067762 | 0.045628 | -0.010536 | 0.06498 | 0.054932 | 122.319 | -0.15564 | 0.16022 | 121.6599 | 7.5119 | 0.74616 | 1.0895 | 122.4289 | -0.21515 | -0.050354 | 0.022888 | 0.16022 | 0.2655 | -0.63629 | -0.10986 | 0.13275 | 0.21057 | 0.85144 | 1.1948 | 121.7651 | 122.4243 | 0.16022 | 122.5342 | 7.6172 | -0.10986 | 122.4243 | 0.16022 | 7.6172 | 121.7651 | 122.5342 | -122.4518 | -122.5113
3916.3906 | 122.4426 | -0.073242 | 122.2458 | 0.14534 | 0.0087734 | -0.013832 | 0.010835 | 0.047764 | -0.013954 | 0.063484 | 0.050354 | 122.2595 | -0.16937 | 0.15564 | 121.6187 | 7.3563 | 0.36163 | 0.75989 | 122.4289 | -0.21973 | -0.096131 | 0.013732 | 0.1236 | 0.22888 | -0.62714 | -0.14649 | 0.1831 | 0.21973 | 0.43488 | 0.83313 | 121.6919 | 122.3328 | 0.1236 | 122.5021 | 7.4295 | -0.14649 | 122.3328 | 0.1236 | 7.4295 | 121.6919 | 122.5021 | -122.4152 | -122.4655
3918.1562 | 122.3694 | -0.09613 | 122.2595 | -0.17509 | 0.0068508 | -0.012337 | 0.010835 | 0.046696 | -0.014381 | 0.065407 | 0.059509 | 122.287 | -0.15564 | 0.15106 | 121.6324 | 7.5256 | 0.78735 | 1.0712 | 122.4518 | -0.19684 | -0.05951 | 0.027466 | 0.15564 | 0.24719 | -0.62714 | -0.10071 | 0.19226 | 0.21515 | 0.88348 | 1.1673 | 121.7285 | 122.3831 | 0.15564 | 122.5479 | 7.6218 | -0.10071 | 122.3831 | 0.15564 | 7.6218 | 121.7285 | 122.5479 | -122.4152 | -122.4564
3919.9062 | 122.4197 | -0.073242 | 122.2458 | -0.12169 | 0.0089872 | -0.015968 | 0.010835 | 0.046055 | -0.013099 | 0.066262 | 0.032043 | 122.2916 | -0.14191 | 0.16022 | 121.6461 | 7.4799 | 0.66376 | 0.99335 | 122.4609 | -0.20599 | -0.068665 | 0.045776 | 0.10529 | 0.23346 | -0.59967 | -0.13275 | 0.21515 | 0.17395 | 0.737 | 1.0666 | 121.7194 | 122.3648 | 0.10529 | 122.5342 | 7.5531 | -0.13275 | 122.3648 | 0.10529 | 7.5531 | 121.7194 | 122.5342 | -122.3877 | -122.4518
3921.6719 | 122.4472 | -0.054932 | 122.2366 | 0.14534 | 0.0081326 | -0.013832 | 0.01938 | 0.048832 | -0.012672 | 0.066475 | -0.022888 | 122.3099 | -0.21515 | 0.082397 | 121.5363 | 7.3059 | 0.44403 | 0.62714 | 122.4426 | -0.21515 | -0.16022 | 0.073242 | 0.032044 | 0.13733 | -0.70038 | -0.16022 | 0.20599 | 0.19226 | 0.49896 | 0.68207 | 121.5912 | 122.3648 | 0.032044 | 122.4976 | 7.3608 | -0.16022 | 122.3648 | 0.032044 | 7.3608 | 121.5912 | 122.4976 | -122.4518 | -122.4518
3923.375 | 122.3785 | -0.10071 | 122.2687 | -0.25139 | 0.010055 | -0.015114 | 0.011689 | 0.04755 | -0.012245 | 0.068825 | -0.013733 | 122.319 | -0.18768 | 0.068665 | 121.5637 | 7.4799 | 0.90179 | 0.98419 | 122.4792 | -0.24261 | -0.086975 | 0.050354 | 0.086975 | 0.16937 | -0.70496 | -0.14191 | 0.21057 | 0.17395 | 1.0025 | 1.0849 | 121.6644 | 122.4197 | 0.086975 | 122.58 | 7.5806 | -0.14191 | 122.4197 | 0.086975 | 7.5806 | 121.6644 | 122.58 | -122.4564 | -122.5113
3925.1406 | 122.3465 | -0.09613 | 122.2778 | -0.075912 | 0.0085598 | -0.01255 | 0.017457 | 0.048191 | -0.015663 | 0.06733 | 0.027466 | 122.3053 | -0.19226 | 0.11444 | 121.5637 | 7.4524 | 0.66834 | 0.83313 | 122.4701 | -0.2243 | -0.096131 | 0.027466 | 0.1236 | 0.21057 | -0.71411 | -0.12817 | 0.19226 | 0.21973 | 0.76446 | 0.92926 | 121.6599 | 122.4014 | 0.1236 | 122.5662 | 7.5485 | -0.12817 | 122.4014 | 0.1236 | 7.5485 | 121.6599 | 122.5662 | -122.4701 | -122.5021
3926.875 | 122.4792 | -0.050354 | 122.2412 | 0.099564 | 0.0092008 | -0.0097733 | 0.017244 | 0.046696 | -0.01374 | 0.067757 | -0.059509 | 122.3328 | -0.22888 | 0.036621 | 121.4813 | 7.3288 | 0.58136 | 0.63629 | 122.4792 | -0.2243 | -0.17853 | 0.091553 | -0.009155 | 0.086975 | -0.75989 | -0.17395 | 0.23804 | 0.16937 | 0.63171 | 0.68665 | 121.5317 | 122.3831 | -0.009155 | 122.5296 | 7.3791 | -0.17395 | 122.3831 | -0.009155 | 7.3791 | 121.5317 | 122.5296 | -122.4701 | -122.4655
3928.625 | 122.4747 | -0.041199 | 122.2549 | 0.12245 | 0.0072782 | -0.011269 | 0.013612 | 0.048191 | -0.012886 | 0.067116 | -0.041199 | 122.3282 | -0.20599 | 0.041199 | 121.5179 | 7.3471 | 0.53558 | 0.6134 | 122.4609 | -0.2655 | -0.1648 | 0.073242 | 0 | 0.082398 | -0.737 | -0.2243 | 0.20599 | 0.1648 | 0.57678 | 0.6546 | 121.5591 | 122.3694 | 0 | 122.5021 | 7.3883 | -0.2243 | 122.3694 | 0 | 7.3883 | 121.5591 | 122.5021 | -122.4609 | -122.5204
3930.3906 | 122.4655 | -0.041199 | 122.2549 | 0.01564 | 0.0083462 | -0.014687 | 0.0059216 | 0.047978 | -0.013313 | 0.066048 | 0 | 122.287 | -0.15564 | 0.07782 | 121.5866 | 7.4615 | 0.60425 | 0.83771 | 122.4655 | -0.20142 | -0.11444 | 0.032043 | 0.041199 | 0.11902 | -0.66833 | -0.16022 | 0.21057 | 0.15564 | 0.64545 | 0.87891 | 121.6278 | 122.3282 | 0.041199 | 122.5067 | 7.5027 | -0.16022 | 122.3282 | 0.041199 | 7.5027 | 121.6278 | 122.5067 | -122.4106 | -122.4564
3932.1562 | 122.4152 | -0.059509 | 122.2549 | -0.045395 | 0.0087734 | -0.013618 | 0.0082714 | 0.045201 | -0.013527 | 0.065193 | 0.032043 | 122.3236 | -0.17395 | 0.15564 | 121.6507 | 7.5806 | 0.66834 | 1.0162 | 122.4243 | -0.2243 | -0.11444 | 0.068664 | 0.091552 | 0.21515 | -0.60425 | -0.16479 | 0.16937 | 0.20599 | 0.72784 | 1.0757 | 121.7102 | 122.3831 | 0.091552 | 122.4838 | 7.6401 | -0.16479 | 122.3831 | 0.091552 | 7.6401 | 121.7102 | 122.4838 | -122.4289 | -122.4792
3933.8594 | 122.5067 | -0.041199 | 122.2641 | 0.0080111 | 0.0081326 | -0.013832 | 0.010621 | 0.046055 | -0.010536 | 0.065193 | 0.013733 | 122.3053 | -0.16479 | 0.09613 | 121.5775 | 7.4799 | 0.60883 | 0.84686 | 122.4701 | -0.21057 | -0.1236 | 0.041199 | 0.054932 | 0.13733 | -0.68664 | -0.16937 | 0.20599 | 0.17853 | 0.65002 | 0.88806 | 121.6187 | 122.3465 | 0.054932 | 122.5113 | 7.5211 | -0.16937 | 122.3465 | 0.054932 | 7.5211 | 121.6187 | 122.5113 | -122.4289 | -122.4747
3935.6094 | 122.3557 | -0.10529 | 122.2824 | -0.16747 | 0.0064236 | -0.014046 | 0.018953 | 0.047337 | -0.015663 | 0.063698 | -0.004578 | 122.3053 | -0.20599 | 0.10071 | 121.5591 | 7.5714 | 0.79193 | 0.93842 | 122.4884 | -0.24261 | -0.10071 | 0.022888 | 0.10071 | 0.20599 | -0.72327 | -0.13733 | 0.20599 | 0.20142 | 0.89722 | 1.0437 | 121.6644 | 122.4106 | 0.10071 | 122.5937 | 7.6767 | -0.13733 | 122.4106 | 0.10071 | 7.6767 | 121.6644 | 122.5937 | -122.4884 | -122.525
3937.375 | 122.4701 | -0.036621 | 122.2321 | 0.076676 | 0.0098416 | -0.014046 | 0.016389 | 0.048191 | -0.013527 | 0.068184 | -0.050354 | 122.3236 | -0.21973 | 0.054932 | 121.5225 | 7.4158 | 0.54474 | 0.63171 | 122.4655 | -0.23346 | -0.18311 | 0.091552 | -0.013733 | 0.091553 | -0.70953 | -0.19684 | 0.23346 | 0.16937 | 0.58136 | 0.66834 | 121.5591 | 122.3602 | -0.013733 | 122.5021 | 7.4524 | -0.19684 | 122.3602 | -0.013733 | 7.4524 | 121.5591 | 122.5021 | -122.4518 | -122.4655
3939.1562 | 122.4792 | -0.050354 | 122.2366 | 0.099564 | 0.010482 | -0.01255 | 0.015321 | 0.050114 | -0.01374 | 0.066689 | -0.027466 | 122.3602 | -0.2243 | 0.050354 | 121.5271 | 7.4295 | 0.53558 | 0.62714 | 122.4792 | -0.23346 | -0.17395 | 0.1236 | 0.022888 | 0.10071 | -0.70953 | -0.1831 | 0.24262 | 0.19684 | 0.58594 | 0.67749 | 121.5775 | 122.4106 | 0.022888 | 122.5296 | 7.4799 | -0.1831 | 122.4106 | 0.022888 | 7.4799 | 121.5775 | 122.5296 | -122.4609 | -122.4701
3940.8594 | 122.3969 | -0.082397 | 122.2824 | -0.22087 | 0.0092008 | -0.0149 | 0.010835 | 0.04755 | -0.012031 | 0.066048 | -0.059509 | 122.3328 | -0.20599 | 0.064087 | 121.5271 | 7.608 | 0.92926 | 0.97504 | 122.4564 | -0.25177 | -0.1236 | 0.050354 | 0.022888 | 0.14648 | -0.75531 | -0.16937 | 0.17395 | 0.14649 | 1.0117 | 1.0574 | 121.6095 | 122.4152 | 0.022888 | 122.5388 | 7.6904 | -0.16937 | 122.4152 | 0.022888 | 7.6904 | 121.6095 | 122.5388 | -122.4884 | -122.5342
3942.625 | 122.4701 | -0.045776 | 122.2412 | 0.091934 | 0.010269 | -0.010414 | 0.014467 | 0.048191 | -0.010109 | 0.067116 | -0.041199 | 122.3328 | -0.19684 | 0.050354 | 121.5271 | 7.4615 | 0.54016 | 0.64087 | 122.4655 | -0.25177 | -0.15106 | 0.091553 | 0.004577 | 0.09613 | -0.71411 | -0.20599 | 0.2243 | 0.15564 | 0.58594 | 0.68665 | 121.5729 | 122.3785 | 0.004577 | 122.5113 | 7.5073 | -0.20599 | 122.3785 | 0.004577 | 7.5073 | 121.5729 | 122.5113 | -122.438 | -122.493
3944.3438 | 122.438 | -0.068665 | 122.2504 | 0.10719 | 0.0092008 | -0.0089189 | 0.013185 | 0.048619 | -0.013099 | 0.065834 | 0.059509 | 122.319 | -0.14648 | 0.13733 | 121.6187 | 7.5851 | 0.3891 | 0.74158 | 122.4289 | -0.21515 | -0.077819 | 0.068665 | 0.12817 | 0.20599 | -0.63171 | -0.14648 | 0.17853 | 0.20599 | 0.45776 | 0.81024 | 121.6873 | 122.3877 | 0.12817 | 122.4976 | 7.6538 | -0.14648 | 122.3877 | 0.12817 | 7.6538 | 121.6873 | 122.4976 | -122.3969 | -122.4655
3946.1094 | 122.4426 | -0.054932 | 122.2137 | 0.10719 | 0.0089872 | -0.010628 | 0.014039 | 0.047978 | -0.013527 | 0.068825 | -0.022888 | 122.3419 | -0.20142 | 0.068665 | 121.5363 | 7.5027 | 0.48981 | 0.64545 | 122.4792 | -0.21057 | -0.14648 | 0.12817 | 0.032044 | 0.1236 | -0.67749 | -0.15564 | 0.2655 | 0.17853 | 0.54474 | 0.70038 | 121.5912 | 122.3969 | 0.032044 | 122.5342 | 7.5577 | -0.15564 | 122.3969 | 0.032044 | 7.5577 | 121.5912 | 122.5342 | -122.4152 | -122.4243
3947.8594 | 122.4609 | -0.036621 | 122.2092 | 0.11482 | 0.0089872 | -0.016396 | 0.013826 | 0.048405 | -0.015236 | 0.065834 | -0.054932 | 122.3282 | -0.2243 | 0.041199 | 121.5317 | 7.5073 | 0.54474 | 0.62714 | 122.4838 | -0.23346 | -0.18768 | 0.11902 | -0.018311 | 0.07782 | -0.67749 | -0.19684 | 0.27466 | 0.16937 | 0.58136 | 0.66376 | 121.5683 | 122.3648 | -0.018311 | 122.5204 | 7.5439 | -0.19684 | 122.3648 | -0.018311 | 7.5439 | 121.5683 | 122.5204 | -122.4335 | -122.4426
3949.6406 | 122.4701 | -0.045776 | 122.2321 | 0.084305 | 0.0089872 | -0.016823 | 0.008485 | 0.048619 | -0.011177 | 0.065834 | 0.027466 | 122.3328 | -0.16937 | 0.10071 | 121.5958 | 7.6035 | 0.53558 | 0.81024 | 122.4289 | -0.21973 | -0.1236 | 0.10071 | 0.073242 | 0.14648 | -0.63629 | -0.17395 | 0.19684 | 0.19684 | 0.58136 | 0.85602 | 121.6415 | 122.3785 | 0.073242 | 122.4747 | 7.6492 | -0.17395 | 122.3785 | 0.073242 | 7.6492 | 121.6415 | 122.4747 | -122.4014 | -122.4518
3951.3438 | 122.3557 | -0.09613 | 122.2824 | -0.19798 | 0.0089872 | -0.011055 | 0.016176 | 0.048832 | -0.014381 | 0.065834 | -0.041199 | 122.3419 | -0.21057 | 0.086975 | 121.55 | 7.7179 | 0.84686 | 0.93842 | 122.4564 | -0.23346 | -0.11444 | 0.059509 | 0.054931 | 0.1831 | -0.73242 | -0.13733 | 0.17395 | 0.16937 | 0.94299 | 1.0345 | 121.6461 | 122.438 | 0.054931 | 122.5525 | 7.814 | -0.13733 | 122.438 | 0.054931 | 7.814 | 121.6461 | 122.5525 | -122.493 | -122.5159
3953.1094 | 122.438 | -0.032043 | 122.2366 | 0.069046 | 0.0081326 | -0.01255 | 0.016389 | 0.049687 | -0.014167 | 0.066902 | -0.050354 | 122.3236 | -0.20599 | 0.018311 | 121.4996 | 7.5577 | 0.6546 | 0.65002 | 122.5067 | -0.25635 | -0.17395 | 0.086975 | -0.018311 | 0.050354 | -0.737 | -0.22431 | 0.27008 | 0.15564 | 0.68665 | 0.68207 | 121.5317 | 122.3557 | -0.018311 | 122.5388 | 7.5897 | -0.22431 | 122.3557 | -0.018311 | 7.5897 | 121.5317 | 122.5388 | -122.4426 | -122.493
3954.8125 | 122.3831 | -0.091553 | 122.2458 | 0.00038159 | 0.0098416 | -0.011482 | 0.017244 | 0.049473 | -0.01374 | 0.066475 | -0.032043 | 122.319 | -0.20142 | 0.054932 | 121.5134 | 7.6126 | 0.64545 | 0.71869 | 122.5113 | -0.22888 | -0.10986 | 0.073242 | 0.05951 | 0.14649 | -0.73242 | -0.13733 | 0.2655 | 0.16937 | 0.737 | 0.81024 | 121.6049 | 122.4106 | 0.05951 | 122.6028 | 7.7042 | -0.13733 | 122.4106 | 0.05951 | 7.7042 | 121.6049 | 122.6028 | -122.4472 | -122.4747
3956.5156 | 122.3373 | -0.11444 | 122.2733 | -0.19798 | 0.0083462 | -0.015968 | 0.0086988 | 0.047123 | -0.011818 | 0.066475 | 0.045776 | 122.3007 | -0.16479 | 0.15106 | 121.6507 | 7.814 | 0.7782 | 1.0895 | 122.4289 | -0.21515 | -0.050354 | 0.027466 | 0.16022 | 0.2655 | -0.62256 | -0.10071 | 0.15564 | 0.21057 | 0.89264 | 1.2039 | 121.7651 | 122.4152 | 0.16022 | 122.5433 | 7.9285 | -0.10071 | 122.4152 | 0.16022 | 7.9285 | 121.7651 | 122.5433 | -122.438 | -122.4884
3958.2812 | 122.4243 | -0.068665 | 122.2733 | 0.099564 | 0.009628 | -0.014259 | 0.0097668 | 0.046055 | -0.012886 | 0.06797 | 0.041199 | 122.3007 | -0.14648 | 0.13275 | 121.6232 | 7.6813 | 0.42572 | 0.80109 | 122.4152 | -0.21515 | -0.077819 | 0.027466 | 0.10986 | 0.20142 | -0.65002 | -0.14648 | 0.14191 | 0.18768 | 0.49438 | 0.86975 | 121.6919 | 122.3694 | 0.10986 | 122.4838 | 7.7499 | -0.14648 | 122.3694 | 0.10986 | 7.7499 | 121.6919 | 122.4838 | -122.4197 | -122.4884
3959.9844 | 122.3511 | -0.082397 | 122.2824 | -0.15221 | 0.011123 | -0.016182 | 0.015748 | 0.046269 | -0.012672 | 0.064553 | -0.009155 | 122.3099 | -0.21973 | 0.09613 | 121.5591 | 7.7683 | 0.80566 | 0.95215 | 122.4655 | -0.25177 | -0.13733 | 0.027465 | 0.073242 | 0.17853 | -0.72327 | -0.16937 | 0.1831 | 0.21057 | 0.88806 | 1.0345 | 121.6415 | 122.3923 | 0.073242 | 122.5479 | 7.8506 | -0.16937 | 122.3923 | 0.073242 | 7.8506 | 121.6415 | 122.5479 | -122.5021 | -122.5342
3961.75 | 122.406 | -0.068665 | 122.287 | 0.069046 | 0.0092008 | -0.012978 | 0.013826 | 0.049259 | -0.011818 | 0.066048 | -0.027466 | 122.3145 | -0.21057 | 0.050354 | 121.5042 | 7.6584 | 0.64545 | 0.72327 | 122.4747 | -0.24261 | -0.14191 | 0.027466 | 0.041199 | 0.11902 | -0.78278 | -0.17395 | 0.18768 | 0.18311 | 0.71411 | 0.79193 | 121.5729 | 122.3831 | 0.041199 | 122.5433 | 7.7271 | -0.17395 | 122.3831 | 0.041199 | 7.7271 | 121.5729 | 122.5433 | -122.4976 | -122.5296
3963.5156 | 122.3282 | -0.09613 | 122.2824 | -0.15984 | 0.011551 | -0.014259 | 0.0065624 | 0.047123 | -0.013099 | 0.066262 | 0.086975 | 122.3328 | -0.16479 | 0.15564 | 121.6736 | 7.8598 | 0.737 | 1.0803 | 122.4518 | -0.20599 | -0.068665 | 0.050354 | 0.1831 | 0.25177 | -0.60883 | -0.10986 | 0.16937 | 0.25177 | 0.83313 | 1.1765 | 121.7697 | 122.4289 | 0.1831 | 122.5479 | 7.9559 | -0.10986 | 122.4289 | 0.1831 | 7.9559 | 121.7697 | 122.5479 | -122.4472 | -122.4884
3965.2812 | 122.3557 | -0.082397 | 122.2595 | -0.060654 | 0.0087734 | -0.014046 | 0.015748 | 0.048191 | -0.016731 | 0.066689 | 0.013733 | 122.3145 | -0.20142 | 0.09613 | 121.55 | 7.7545 | 0.68665 | 0.84228 | 122.4976 | -0.2243 | -0.11902 | 0.054932 | 0.09613 | 0.17853 | -0.70953 | -0.14191 | 0.23804 | 0.21515 | 0.76904 | 0.92468 | 121.6324 | 122.3969 | 0.09613 | 122.58 | 7.8369 | -0.14191 | 122.3969 | 0.09613 | 7.8369 | 121.6324 | 122.58 | -122.4609 | -122.4838
3966.9844 | 122.3511 | -0.10071 | 122.2733 | -0.083542 | 0.0098416 | -0.0097733 | 0.013185 | 0.049473 | -0.014167 | 0.064553 | 0.009155 | 122.3007 | -0.1831 | 0.082397 | 121.5546 | 7.7637 | 0.68665 | 0.83313 | 122.493 | -0.21973 | -0.082397 | 0.027466 | 0.10986 | 0.18311 | -0.71869 | -0.11902 | 0.21973 | 0.19226 | 0.78735 | 0.93384 | 121.6553 | 122.4014 | 0.10986 | 122.5937 | 7.8644 | -0.11902 | 122.4014 | 0.10986 | 7.8644 | 121.6553 | 122.5937 | -122.4564 | -122.493
3968.75 | 122.3511 | -0.09613 | 122.2733 | -0.18272 | 0.009628 | -0.010841 | 0.007417 | 0.048191 | -0.012245 | 0.067757 | 0.082397 | 122.319 | -0.16022 | 0.16022 | 121.6736 | 7.9102 | 0.74158 | 1.1078 | 122.4472 | -0.21057 | -0.064087 | 0.045777 | 0.17853 | 0.25635 | -0.59967 | -0.11444 | 0.17395 | 0.24261 | 0.83771 | 1.2039 | 121.7697 | 122.4152 | 0.17853 | 122.5433 | 8.0063 | -0.11444 | 122.4152 | 0.17853 | 8.0063 | 121.7697 | 122.5433 | -122.4335 | -122.4838
3970.5156 | 122.3785 | -0.07782 | 122.2687 | 0.046158 | 0.010482 | -0.012764 | 0.015535 | 0.048405 | -0.013954 | 0.067543 | -0.013733 | 122.3328 | -0.21057 | 0.041199 | 121.4951 | 7.7225 | 0.66376 | 0.72327 | 122.4976 | -0.24261 | -0.13275 | 0.064087 | 0.064087 | 0.11902 | -0.77362 | -0.16479 | 0.22888 | 0.19684 | 0.74158 | 0.80109 | 121.5729 | 122.4106 | 0.064087 | 122.5754 | 7.8003 | -0.16479 | 122.4106 | 0.064087 | 7.8003 | 121.5729 | 122.5754 | -122.4792 | -122.5113
3972.2812 | 122.3877 | -0.09613 | 122.319 | -0.28191 | 0.0081326 | -0.016609 | 0.010408 | 0.046696 | -0.013099 | 0.066262 | 0.036621 | 122.3373 | -0.16479 | 0.11444 | 121.6003 | 7.9056 | 0.90179 | 1.0757 | 122.4609 | -0.22888 | -0.068665 | 0.01831 | 0.13275 | 0.21057 | -0.71869 | -0.13275 | 0.14191 | 0.20142 | 0.99792 | 1.1719 | 121.6965 | 122.4335 | 0.13275 | 122.5571 | 8.0017 | -0.13275 | 122.4335 | 0.13275 | 8.0017 | 121.6965 | 122.5571 | -122.4838 | -122.5479
3973.9844 | 122.3969 | -0.09613 | 122.2961 | -0.18272 | 0.009628 | -0.018318 | 0.012544 | 0.046696 | -0.012245 | 0.063271 | -0.022888 | 122.3511 | -0.18768 | 0.036621 | 121.5408 | 7.8506 | 0.95215 | 0.98419 | 122.4747 | -0.24719 | -0.091553 | 0.054931 | 0.073242 | 0.13275 | -0.75531 | -0.15106 | 0.17853 | 0.16479 | 1.0483 | 1.0803 | 121.637 | 122.4472 | 0.073242 | 122.5708 | 7.9468 | -0.15106 | 122.4472 | 0.073242 | 7.9468 | 121.637 | 122.5708 | -122.4838 | -122.5433
3975.7344 | 122.4014 | -0.086975 | 122.2916 | -0.24376 | 0.010269 | -0.014473 | 0.013826 | 0.046269 | -0.011818 | 0.065407 | -0.059509 | 122.3373 | -0.21057 | 0.045776 | 121.5179 | 7.8506 | 0.94757 | 0.97504 | 122.4564 | -0.25635 | -0.1236 | 0.045776 | 0.027466 | 0.13275 | -0.77362 | -0.16937 | 0.16479 | 0.15106 | 1.0345 | 1.062 | 121.6049 | 122.4243 | 0.027466 | 122.5433 | 7.9376 | -0.16937 | 122.4243 | 0.027466 | 7.9376 | 121.6049 | 122.5433 | -122.5021 | -122.5479
3977.4844 | 122.3282 | -0.09613 | 122.2595 | -0.068283 | 0.010696 | -0.0097733 | 0.015748 | 0.048832 | -0.014595 | 0.063912 | 0.022888 | 122.3282 | -0.20142 | 0.09613 | 121.55 | 7.8369 | 0.70038 | 0.85144 | 122.4884 | -0.22888 | -0.10529 | 0.068665 | 0.11902 | 0.19226 | -0.70953 | -0.13275 | 0.22888 | 0.2243 | 0.79651 | 0.94757 | 121.6461 | 122.4243 | 0.11902 | 122.5845 | 7.933 | -0.13275 | 122.4243 | 0.11902 | 7.933 | 121.6461 | 122.5845 | -122.4609 | -122.4884
3979.25 | 122.319 | -0.086975 | 122.2916 | -0.091171 | 0.009628 | -0.011269 | 0.015535 | 0.04755 | -0.014595 | 0.065621 | 0 | 122.3236 | -0.19684 | 0.10986 | 121.582 | 7.8918 | 0.71411 | 0.90179 | 122.4976 | -0.23804 | -0.10986 | 0.032043 | 0.086975 | 0.19684 | -0.70953 | -0.15106 | 0.20599 | 0.19684 | 0.80109 | 0.98877 | 121.669 | 122.4106 | 0.086975 | 122.5845 | 7.9788 | -0.15106 | 122.4106 | 0.086975 | 7.9788 | 121.669 | 122.5845 | -122.4884 | -122.5296
3980.9531 | 122.4655 | -0.054932 | 122.2641 | 0.11482 | 0.0072782 | -0.011269 | 0.0078442 | 0.045841 | -0.010536 | 0.066048 | 0.036621 | 122.3419 | -0.16022 | 0.10986 | 121.5958 | 7.8232 | 0.49439 | 0.8194 | 122.4655 | -0.2243 | -0.10528 | 0.07782 | 0.091553 | 0.16479 | -0.66833 | -0.16937 | 0.20142 | 0.19684 | 0.54932 | 0.87433 | 121.6507 | 122.3969 | 0.091553 | 122.5204 | 7.8781 | -0.16937 | 122.3969 | 0.091553 | 7.8781 | 121.6507 | 122.5204 | -122.4243 | -122.4884
3982.7188 | 122.4289 | -0.045776 | 122.2733 | 0.15297 | 0.0098416 | -0.0102 | 0.013826 | 0.047978 | -0.012245 | 0.066262 | 0.064087 | 122.3236 | -0.16479 | 0.15564 | 121.6232 | 7.8598 | 0.39825 | 0.78278 | 122.4426 | -0.21057 | -0.11902 | 0.050354 | 0.10986 | 0.20142 | -0.65002 | -0.1648 | 0.16937 | 0.22888 | 0.44403 | 0.82855 | 121.669 | 122.3694 | 0.10986 | 122.4884 | 7.9056 | -0.1648 | 122.3694 | 0.10986 | 7.9056 | 121.669 | 122.4884 | -122.438 | -122.4838
3984.5 | 122.3419 | -0.091553 | 122.3007 | -0.16747 | 0.010269 | -0.01255 | 0.01468 | 0.047337 | -0.011818 | 0.066262 | 0.004578 | 122.3053 | -0.20599 | 0.10071 | 121.5729 | 7.9422 | 0.81024 | 0.95215 | 122.5159 | -0.26093 | -0.11444 | 0.004578 | 0.096131 | 0.19226 | -0.72784 | -0.16937 | 0.21515 | 0.21057 | 0.9018 | 1.0437 | 121.6644 | 122.3969 | 0.096131 | 122.6074 | 8.0338 | -0.16937 | 122.3969 | 0.096131 | 8.0338 | 121.6644 | 122.6074 | -122.5067 | -122.5616
3986.2031 | 122.4976 | -0.050354 | 122.2641 | 0.02327 | 0.0092008 | -0.012978 | 0.0069898 | 0.047764 | -0.012886 | 0.065193 | 0.004578 | 122.3328 | -0.16937 | 0.09613 | 121.5866 | 7.8873 | 0.63171 | 0.86975 | 122.4655 | -0.21973 | -0.11902 | 0.068665 | 0.054932 | 0.14648 | -0.67749 | -0.16937 | 0.20142 | 0.17395 | 0.68207 | 0.92011 | 121.637 | 122.3831 | 0.054932 | 122.5159 | 7.9376 | -0.16937 | 122.3831 | 0.054932 | 7.9376 | 121.637 | 122.5159 | -122.4335 | -122.4838
3987.9688 | 122.3602 | -0.082397 | 122.2824 | -0.19035 | 0.0081326 | -0.013405 | 0.014894 | 0.048191 | -0.012031 | 0.065834 | -0.045776 | 122.3373 | -0.21515 | 0.086975 | 121.5546 | 7.9742 | 0.86517 | 0.9613 | 122.4838 | -0.24719 | -0.13275 | 0.054931 | 0.036621 | 0.16937 | -0.72785 | -0.16479 | 0.20142 | 0.16937 | 0.94757 | 1.0437 | 121.637 | 122.4197 | 0.036621 | 122.5662 | 8.0566 | -0.16479 | 122.4197 | 0.036621 | 8.0566 | 121.637 | 122.5662 | -122.4976 | -122.5296
3989.6562 | 122.4655 | -0.059509 | 122.2778 | -0.037765 | 0.0077054 | -0.019173 | 0.0072034 | 0.046269 | -0.011604 | 0.065834 | 0 | 122.3145 | -0.17853 | 0.11444 | 121.6095 | 7.9651 | 0.68665 | 0.98419 | 122.4335 | -0.21973 | -0.11902 | 0.036621 | 0.059509 | 0.17395 | -0.66833 | -0.16022 | 0.15564 | 0.17853 | 0.74616 | 1.0437 | 121.669 | 122.374 | 0.059509 | 122.493 | 8.0246 | -0.16022 | 122.374 | 0.059509 | 8.0246 | 121.669 | 122.493 | -122.4564 | -122.4976
3991.4062 | 122.4747 | -0.064087 | 122.2504 | 0.061417 | 0.0074918 | -0.014473 | 0.008485 | 0.044987 | -0.010536 | 0.066048 | 0.004578 | 122.3053 | -0.18768 | 0.10529 | 121.582 | 7.9056 | 0.55847 | 0.83313 | 122.4106 | -0.2243 | -0.1236 | 0.054932 | 0.068665 | 0.16937 | -0.66833 | -0.16022 | 0.16022 | 0.19226 | 0.62256 | 0.89722 | 121.6461 | 122.3694 | 0.068665 | 122.4747 | 7.9697 | -0.16022 | 122.3694 | 0.068665 | 7.9697 | 121.6461 | 122.4747 | -122.438 | -122.4747
3993.1094 | 122.4701 | -0.045776 | 122.2412 | 0.10719 | 0.011337 | -0.011482 | 0.017671 | 0.049473 | -0.013099 | 0.064553 | -0.032043 | 122.3373 | -0.20142 | 0.045776 | 121.5042 | 7.8278 | 0.60425 | 0.66834 | 122.4884 | -0.25177 | -0.15564 | 0.09613 | 0.013733 | 0.091552 | -0.737 | -0.20599 | 0.24719 | 0.16937 | 0.65002 | 0.71411 | 121.55 | 122.3831 | 0.013733 | 122.5342 | 7.8735 | -0.20599 | 122.3831 | 0.013733 | 7.8735 | 121.55 | 122.5342 | -122.4426 | -122.493
3994.8281 | 122.3419 | -0.086975 | 122.2687 | -0.11406 | 0.010696 | -0.014687 | 0.019593 | 0.048405 | -0.016945 | 0.066262 | 0.013733 | 122.3282 | -0.1831 | 0.1236 | 121.5683 | 8.0017 | 0.72327 | 0.89722 | 122.4884 | -0.23804 | -0.09613 | 0.059509 | 0.10071 | 0.21057 | -0.70038 | -0.15106 | 0.21973 | 0.19684 | 0.81024 | 0.98419 | 121.6553 | 122.4152 | 0.10071 | 122.5754 | 8.0887 | -0.15106 | 122.4152 | 0.10071 | 8.0887 | 121.6553 | 122.5754 | -122.4518 | -122.5067
3996.5938 | 122.3419 | -0.09613 | 122.2733 | -0.060654 | 0.01091 | -0.014259 | 0.01468 | 0.049046 | -0.016304 | 0.065407 | 0.027466 | 122.3053 | -0.19684 | 0.10986 | 121.5637 | 7.9971 | 0.71869 | 0.87891 | 122.493 | -0.21973 | -0.10071 | 0.032044 | 0.1236 | 0.20599 | -0.70953 | -0.1236 | 0.21973 | 0.2243 | 0.81482 | 0.97504 | 121.6599 | 122.4014 | 0.1236 | 122.5891 | 8.0933 | -0.1236 | 122.4014 | 0.1236 | 8.0933 | 121.6599 | 122.5891 | -122.4701 | -122.493
3998.3438 | 122.374 | -0.086975 | 122.2733 | -0.19035 | 0.0094144 | -0.011909 | 0.012544 | 0.048191 | -0.013954 | 0.06498 | -0.036621 | 122.3373 | -0.19684 | 0.064087 | 121.5591 | 8.0292 | 0.88348 | 0.98419 | 122.5067 | -0.23346 | -0.10986 | 0.064087 | 0.050354 | 0.15106 | -0.71411 | -0.14648 | 0.23346 | 0.16022 | 0.97046 | 1.0712 | 121.6461 | 122.4243 | 0.050354 | 122.5937 | 8.1162 | -0.14648 | 122.4243 | 0.050354 | 8.1162 | 121.6461 | 122.5937 | -122.4701 | -122.5067
4000.0469 | 122.3373 | -0.10071 | 122.2961 | -0.11406 | 0.0081326 | -0.013618 | 0.014253 | 0.049046 | -0.014808 | 0.069893 | 0 | 122.3373 | -0.20142 | 0.10529 | 121.5683 | 8.0521 | 0.78735 | 0.94757 | 122.5021 | -0.24719 | -0.10071 | 0.041198 | 0.10071 | 0.20599 | -0.72785 | -0.14648 | 0.20599 | 0.20142 | 0.88806 | 1.0483 | 121.669 | 122.438 | 0.10071 | 122.6028 | 8.1528 | -0.14648 | 122.438 | 0.10071 | 8.1528 | 121.669 | 122.6028 | -122.4976 | -122.5433
4001.75 | 122.4335 | -0.059509 | 122.2458 | 0.16823 | 0.0083462 | -0.011482 | 0.012117 | 0.050114 | -0.013954 | 0.067116 | 0.064087 | 122.3465 | -0.15106 | 0.15106 | 121.6095 | 7.9971 | 0.42114 | 0.79651 | 122.4609 | -0.20599 | -0.091553 | 0.10071 | 0.1236 | 0.21057 | -0.63629 | -0.14649 | 0.21515 | 0.21515 | 0.48065 | 0.85602 | 121.669 | 122.406 | 0.1236 | 122.5204 | 8.0566 | -0.14649 | 122.406 | 0.1236 | 8.0566 | 121.669 | 122.5204 | -122.3969 | -122.4518
4003.4531 | 122.3831 | -0.09613 | 122.2595 | -0.13695 | 0.0094144 | -0.015968 | 0.0078442 | 0.046482 | -0.013313 | 0.066262 | 0.054932 | 122.3053 | -0.16937 | 0.15564 | 121.6644 | 8.1482 | 0.72327 | 1.1032 | 122.4197 | -0.20599 | -0.073243 | 0.045777 | 0.15106 | 0.25177 | -0.59509 | -0.10986 | 0.16022 | 0.22431 | 0.8194 | 1.1993 | 121.7606 | 122.4014 | 0.15106 | 122.5159 | 8.2443 | -0.10986 | 122.4014 | 0.15106 | 8.2443 | 121.7606 | 122.5159 | -122.4289 | -122.4655
4005.2188 | 122.3785 | -0.086975 | 122.2641 | -0.26665 | 0.0085598 | -0.012337 | 0.010621 | 0.046696 | -0.011818 | 0.066902 | 0.022888 | 122.287 | -0.16022 | 0.11902 | 121.5912 | 8.1436 | 0.91553 | 1.1032 | 122.4335 | -0.23346 | -0.073242 | 0.022888 | 0.10986 | 0.20599 | -0.67291 | -0.14648 | 0.16937 | 0.1831 | 1.0025 | 1.1902 | 121.6782 | 122.374 | 0.10986 | 122.5204 | 8.2306 | -0.14648 | 122.374 | 0.10986 | 8.2306 | 121.6782 | 122.5204 | -122.4243 | -122.4976
4006.9844 | 122.4197 | -0.073242 | 122.2412 | 0.17586 | 0.007919 | -0.011696 | 0.014039 | 0.048405 | -0.014381 | 0.065407 | 0.07782 | 122.2961 | -0.14648 | 0.15564 | 121.6232 | 8.0338 | 0.4303 | 0.81482 | 122.4426 | -0.19226 | -0.073242 | 0.054932 | 0.15106 | 0.22888 | -0.61798 | -0.11902 | 0.20142 | 0.2243 | 0.50354 | 0.88806 | 121.6965 | 122.3694 | 0.15106 | 122.5159 | 8.107 | -0.11902 | 122.3694 | 0.15106 | 8.107 | 121.6965 | 122.5159 | -122.3877 | -122.4335
4008.7344 | 122.4335 | -0.054932 | 122.2504 | 0.10719 | 0.0085598 | -0.0082779 | 0.011903 | 0.04755 | -0.012245 | 0.06498 | 0.050354 | 122.287 | -0.17395 | 0.14648 | 121.6049 | 8.0475 | 0.48523 | 0.84686 | 122.4426 | -0.21057 | -0.11902 | 0.036621 | 0.10529 | 0.20142 | -0.64545 | -0.15564 | 0.19226 | 0.2243 | 0.54016 | 0.9018 | 121.6599 | 122.3419 | 0.10529 | 122.4976 | 8.1024 | -0.15564 | 122.3419 | 0.10529 | 8.1024 | 121.6599 | 122.4976 | -122.4243 | -122.4609
4011.7656 | 122.438 | -0.064087 | 122.2549 | 0.13008 | 0.0094144 | -0.0093461 | 0.011476 | 0.047337 | -0.013527 | 0.064553 | 0.050354 | 122.3145 | -0.16937 | 0.13275 | 121.5866 | 8.0612 | 0.52185 | 0.84686 | 122.4152 | -0.2243 | -0.10529 | 0.059509 | 0.11444 | 0.19684 | -0.66833 | -0.16022 | 0.16022 | 0.21973 | 0.58594 | 0.91095 | 121.6507 | 122.3785 | 0.11444 | 122.4792 | 8.1253 | -0.16022 | 122.3785 | 0.11444 | 8.1253 | 121.6507 | 122.4792 | -122.4243 | -122.4792
4014.4531 | 122.3785 | -0.086975 | 122.2595 | 0.0080111 | 0.012191 | -0.0089189 | 0.019593 | 0.0499 | -0.017799 | 0.06498 | 0.018311 | 122.374 | -0.20599 | 0.082397 | 121.5042 | 8.0521 | 0.67749 | 0.7782 | 122.5021 | -0.2655 | -0.11902 | 0.11444 | 0.10529 | 0.16937 | -0.75531 | -0.17853 | 0.24261 | 0.22431 | 0.76447 | 0.86517 | 121.5912 | 122.4609 | 0.10529 | 122.5891 | 8.139 | -0.17853 | 122.4609 | 0.10529 | 8.139 | 121.5912 | 122.5891 | -122.4655 | -122.525
4018.125 | 122.3602 | -0.086975 | 122.287 | -0.19035 | 0.0098416 | -0.016182 | 0.0097668 | 0.04755 | -0.011604 | 0.064766 | 0.036621 | 122.3145 | -0.16022 | 0.13733 | 121.6232 | 8.2535 | 0.88348 | 1.1536 | 122.4426 | -0.23346 | -0.073242 | 0.027466 | 0.1236 | 0.2243 | -0.66376 | -0.14648 | 0.15564 | 0.19684 | 0.97046 | 1.2405 | 121.7102 | 122.4014 | 0.1236 | 122.5296 | 8.3405 | -0.14648 | 122.4014 | 0.1236 | 8.3405 | 121.7102 | 122.5296 | -122.4472 | -122.5204
4023.4375 | 122.3419 | -0.086975 | 122.2595 | -0.12932 | 0.010055 | -0.011909 | 0.017884 | 0.048405 | -0.013527 | 0.065407 | 0.013733 | 122.3328 | -0.21057 | 0.11444 | 121.5637 | 8.226 | 0.82855 | 0.97046 | 122.4701 | -0.23804 | -0.1236 | 0.073243 | 0.10071 | 0.20142 | -0.6958 | -0.15106 | 0.21057 | 0.2243 | 0.91553 | 1.0574 | 121.6507 | 122.4197 | 0.10071 | 122.5571 | 8.313 | -0.15106 | 122.4197 | 0.10071 | 8.313 | 121.6507 | 122.5571 | -122.4701 | -122.4976
4025.2188 | 122.4472 | -0.068665 | 122.2366 | -0.030136 | 0.0081326 | -0.011696 | 0.0072034 | 0.047764 | -0.0086132 | 0.065193 | 0.022888 | 122.3236 | -0.17395 | 0.11444 | 121.6141 | 8.2123 | 0.71869 | 1.0117 | 122.4518 | -0.21057 | -0.10528 | 0.086975 | 0.091553 | 0.18311 | -0.62256 | -0.14191 | 0.21515 | 0.19684 | 0.78735 | 1.0803 | 121.6827 | 122.3923 | 0.091553 | 122.5204 | 8.2809 | -0.14191 | 122.3923 | 0.091553 | 8.2809 | 121.6827 | 122.5204 | -122.4106 | -122.4472
4026.9219 | 122.438 | -0.054932 | 122.2733 | 0.17586 | 0.0068508 | -0.010841 | 0.01233 | 0.048191 | -0.010963 | 0.063912 | 0.073242 | 122.2824 | -0.15564 | 0.16022 | 121.6187 | 8.1711 | 0.43945 | 0.83771 | 122.4655 | -0.18768 | -0.10071 | 0.009156 | 0.12817 | 0.21515 | -0.6546 | -0.13275 | 0.19226 | 0.22888 | 0.49438 | 0.89264 | 121.6736 | 122.3373 | 0.12817 | 122.5204 | 8.226 | -0.13275 | 122.3373 | 0.12817 | 8.226 | 121.6736 | 122.5204 | -122.4289 | -122.4609
4028.6719 | 122.4106 | -0.07782 | 122.2778 | -0.068283 | 0.010269 | -0.011696 | 0.0089124 | 0.046696 | -0.012245 | 0.064339 | 0.041199 | 122.287 | -0.18768 | 0.14191 | 121.6232 | 8.2809 | 0.74158 | 1.0712 | 122.4564 | -0.21973 | -0.10986 | 0.009155 | 0.11902 | 0.21973 | -0.6546 | -0.14191 | 0.17853 | 0.22888 | 0.8194 | 1.149 | 121.7011 | 122.3648 | 0.11902 | 122.5342 | 8.3588 | -0.14191 | 122.3648 | 0.11902 | 8.3588 | 121.7011 | 122.5342 | -122.4655 | -122.4976
4030.4375 | 122.3785 | -0.068665 | 122.2778 | -0.19798 | 0.010269 | -0.010414 | 0.015748 | 0.046696 | -0.014595 | 0.065834 | -0.036621 | 122.3328 | -0.21515 | 0.054932 | 121.5317 | 8.2672 | 0.97961 | 1.0208 | 122.4838 | -0.24719 | -0.14648 | 0.054932 | 0.032044 | 0.1236 | -0.74616 | -0.17853 | 0.20599 | 0.17853 | 1.0483 | 1.0895 | 121.6003 | 122.4014 | 0.032044 | 122.5525 | 8.3359 | -0.17853 | 122.4014 | 0.032044 | 8.3359 | 121.6003 | 122.5525 | -122.493 | -122.525
4032.2188 | 122.3511 | -0.086975 | 122.2778 | -0.18272 | 0.0085598 | -0.015114 | 0.010835 | 0.04456 | -0.012886 | 0.066262 | 0.041199 | 122.2916 | -0.16937 | 0.16022 | 121.6232 | 8.3771 | 0.88348 | 1.1673 | 122.4289 | -0.21515 | -0.082398 | 0.013733 | 0.12817 | 0.24719 | -0.6546 | -0.12817 | 0.15106 | 0.21057 | 0.97046 | 1.2543 | 121.7102 | 122.3785 | 0.12817 | 122.5159 | 8.4641 | -0.12817 | 122.3785 | 0.12817 | 8.4641 | 121.7102 | 122.5159 | -122.4472 | -122.493
4033.9219 | 122.4701 | -0.054932 | 122.2549 | 0.00038159 | 0.0081326 | -0.011269 | 0.0097668 | 0.045841 | -0.010963 | 0.064125 | 0.004578 | 122.3373 | -0.16022 | 0.11444 | 121.5912 | 8.2397 | 0.70953 | 0.97504 | 122.4472 | -0.2243 | -0.10528 | 0.082397 | 0.05951 | 0.16937 | -0.66376 | -0.16937 | 0.19226 | 0.16479 | 0.76447 | 1.03 | 121.6461 | 122.3923 | 0.05951 | 122.5021 | 8.2947 | -0.16937 | 122.3923 | 0.05951 | 8.2947 | 121.6461 | 122.5021 | -122.4152 | -122.4792
4035.6094 | 122.3923 | -0.07782 | 122.2641 | 0.00038159 | 0.0098416 | -0.011909 | 0.018312 | 0.047337 | -0.014167 | 0.066902 | -0.009155 | 122.3557 | -0.19684 | 0.059509 | 121.5042 | 8.1802 | 0.68665 | 0.75531 | 122.4701 | -0.24261 | -0.11902 | 0.091553 | 0.068665 | 0.13733 | -0.75989 | -0.16479 | 0.20599 | 0.18768 | 0.76447 | 0.83313 | 121.582 | 122.4335 | 0.068665 | 122.5479 | 8.2581 | -0.16479 | 122.4335 | 0.068665 | 8.2581 | 121.582 | 122.5479 | -122.4609 | -122.5067
4037.375 | 122.3969 | -0.073242 | 122.2733 | -0.27428 | 0.0087734 | -0.015755 | 0.013185 | 0.045841 | -0.01374 | 0.066262 | -0.050354 | 122.374 | -0.20599 | 0.050354 | 121.5225 | 8.3221 | 0.99792 | 1.03 | 122.4792 | -0.24719 | -0.13275 | 0.10071 | 0.022888 | 0.1236 | -0.75073 | -0.17395 | 0.20599 | 0.15564 | 1.0712 | 1.1032 | 121.5958 | 122.4472 | 0.022888 | 122.5525 | 8.3954 | -0.17395 | 122.4472 | 0.022888 | 8.3954 | 121.5958 | 122.5525 | -122.4792 | -122.5204
4039.1562 | 122.438 | -0.045776 | 122.2549 | 0.061417 | 0.010482 | -0.010628 | 0.015535 | 0.049473 | -0.01374 | 0.066689 | -0.045776 | 122.3328 | -0.20599 | 0.032043 | 121.4951 | 8.1848 | 0.70038 | 0.73242 | 122.4838 | -0.24719 | -0.16022 | 0.07782 | 0 | 0.077819 | -0.75989 | -0.20142 | 0.22888 | 0.16022 | 0.74615 | 0.7782 | 121.5408 | 122.3785 | 0 | 122.5296 | 8.2306 | -0.20142 | 122.3785 | 0 | 8.2306 | 121.5408 | 122.5296 | -122.4609 | -122.5021
4040.875 | 122.3694 | -0.10529 | 122.2824 | -0.022507 | 0.01091 | -0.015755 | 0.015962 | 0.048619 | -0.012458 | 0.06797 | -0.004578 | 122.319 | -0.20142 | 0.07782 | 121.5179 | 8.2535 | 0.71869 | 0.80566 | 122.4655 | -0.23804 | -0.09613 | 0.036621 | 0.10071 | 0.18311 | -0.76447 | -0.13275 | 0.1831 | 0.19684 | 0.82398 | 0.91095 | 121.6232 | 122.4243 | 0.10071 | 122.5708 | 8.3588 | -0.13275 | 122.4243 | 0.10071 | 8.3588 | 121.6232 | 122.5708 | -122.4838 | -122.5204
4042.6406 | 122.3465 | -0.10071 | 122.2824 | -0.091171 | 0.010269 | -0.01255 | 0.015321 | 0.047764 | -0.013954 | 0.067116 | 0.022888 | 122.3328 | -0.19684 | 0.11444 | 121.5546 | 8.345 | 0.76904 | 0.9201 | 122.5021 | -0.21973 | -0.09613 | 0.050354 | 0.1236 | 0.21515 | -0.72785 | -0.11902 | 0.21973 | 0.21973 | 0.86975 | 1.0208 | 121.6553 | 122.4335 | 0.1236 | 122.6028 | 8.4457 | -0.11902 | 122.4335 | 0.1236 | 8.4457 | 121.6553 | 122.6028 | -122.4792 | -122.5021
4044.3438 | 122.4655 | -0.045776 | 122.2687 | -0.014877 | 0.0074918 | -0.016609 | 0.0044262 | 0.04691 | -0.01139 | 0.065193 | -0.013733 | 122.3053 | -0.17395 | 0.10071 | 121.6095 | 8.3359 | 0.71869 | 0.97046 | 122.4335 | -0.23804 | -0.12817 | 0.036621 | 0.032043 | 0.14648 | -0.65918 | -0.19226 | 0.16479 | 0.16022 | 0.76447 | 1.0162 | 121.6553 | 122.3511 | 0.032043 | 122.4792 | 8.3817 | -0.19226 | 122.3511 | 0.032043 | 8.3817 | 121.6553 | 122.4792 | -122.4426 | -122.5067
4046.1094 | 122.4335 | -0.068665 | 122.2641 | -0.098801 | 0.0081326 | -0.012764 | 0.0086988 | 0.045201 | -0.01075 | 0.066475 | 0.036621 | 122.319 | -0.16937 | 0.14191 | 121.637 | 8.432 | 0.77362 | 1.1032 | 122.4289 | -0.22888 | -0.10071 | 0.054932 | 0.10529 | 0.21057 | -0.62714 | -0.16022 | 0.16479 | 0.20599 | 0.84229 | 1.1719 | 121.7056 | 122.3877 | 0.10529 | 122.4976 | 8.5007 | -0.16022 | 122.3877 | 0.10529 | 8.5007 | 121.7056 | 122.4976 | -122.4335 | -122.493
4047.7969 | 122.3969 | -0.07782 | 122.2549 | 0.13008 | 0.0074918 | -0.015968 | 0.017671 | 0.049687 | -0.012245 | 0.066048 | -0.013733 | 122.3328 | -0.21057 | 0.050354 | 121.4996 | 8.2809 | 0.72327 | 0.78278 | 122.4701 | -0.24261 | -0.13275 | 0.07782 | 0.064087 | 0.12817 | -0.75531 | -0.16479 | 0.21515 | 0.19684 | 0.80109 | 0.8606 | 121.5775 | 122.4106 | 0.064087 | 122.5479 | 8.3588 | -0.16479 | 122.4106 | 0.064087 | 8.3588 | 121.5775 | 122.5479 | -122.4655 | -122.4976
4049.5625 | 122.3282 | -0.091553 | 122.2961 | -0.19035 | 0.010482 | -0.014046 | 0.0097668 | 0.046482 | -0.01374 | 0.063698 | 0.050354 | 122.319 | -0.16022 | 0.16937 | 121.637 | 8.5144 | 0.85144 | 1.1902 | 122.4289 | -0.20599 | -0.068664 | 0.022888 | 0.14191 | 0.26093 | -0.65918 | -0.11444 | 0.13275 | 0.21057 | 0.94299 | 1.2817 | 121.7285 | 122.4106 | 0.14191 | 122.5204 | 8.606 | -0.11444 | 122.4106 | 0.14191 | 8.606 | 121.7285 | 122.5204 | -122.4564 | -122.5021
4051.3281 | 122.3602 | -0.10071 | 122.2778 | -0.075912 | 0.009628 | -0.0149 | 0.016176 | 0.050328 | -0.014381 | 0.065834 | 0.027466 | 122.3328 | -0.19684 | 0.10529 | 121.55 | 8.3954 | 0.75531 | 0.9201 | 122.5067 | -0.2243 | -0.09613 | 0.054932 | 0.12817 | 0.20599 | -0.72784 | -0.1236 | 0.22888 | 0.2243 | 0.85602 | 1.0208 | 121.6507 | 122.4335 | 0.12817 | 122.6074 | 8.4961 | -0.1236 | 122.4335 | 0.12817 | 8.4961 | 121.6507 | 122.6074 | -122.4747 | -122.5021
4053.0938 | 122.4609 | -0.054932 | 122.2824 | -0.014877 | 0.0098416 | -0.015541 | 0.0082714 | 0.046482 | -0.012886 | 0.06498 | -0.009155 | 122.3099 | -0.16937 | 0.086975 | 121.6141 | 8.4183 | 0.73242 | 1.0071 | 122.4518 | -0.21057 | -0.11444 | 0.027465 | 0.045777 | 0.14191 | -0.66833 | -0.15564 | 0.16937 | 0.16022 | 0.78735 | 1.062 | 121.669 | 122.3648 | 0.045777 | 122.5067 | 8.4732 | -0.15564 | 122.3648 | 0.045777 | 8.4732 | 121.669 | 122.5067 | -122.4518 | -122.493
4054.7812 | 122.3511 | -0.082397 | 122.2778 | -0.083542 | 0.0094144 | -0.013618 | 0.015962 | 0.048405 | -0.015663 | 0.065834 | 0.018311 | 122.319 | -0.21515 | 0.10071 | 121.5408 | 8.4045 | 0.74158 | 0.90179 | 122.5021 | -0.23346 | -0.13275 | 0.041199 | 0.10071 | 0.18311 | -0.737 | -0.15106 | 0.2243 | 0.23346 | 0.82397 | 0.98419 | 121.6232 | 122.4014 | 0.10071 | 122.5845 | 8.4869 | -0.15106 | 122.4014 | 0.10071 | 8.4869 | 121.6232 | 122.5845 | -122.493 | -122.5113
4056.5625 | 122.4197 | -0.064087 | 122.2595 | 0.15297 | 0.0094144 | -0.012978 | 0.011262 | 0.048619 | -0.01374 | 0.065621 | 0.059509 | 122.2961 | -0.16022 | 0.16479 | 121.6095 | 8.4 | 0.49896 | 0.87891 | 122.438 | -0.21515 | -0.09613 | 0.036622 | 0.1236 | 0.22888 | -0.65002 | -0.15106 | 0.17853 | 0.21973 | 0.56305 | 0.94299 | 121.6736 | 122.3602 | 0.1236 | 122.5021 | 8.4641 | -0.15106 | 122.3602 | 0.1236 | 8.4641 | 121.6736 | 122.5021 | -122.4197 | -122.4747
4058.3281 | 122.4792 | -0.045776 | 122.2321 | 0.10719 | 0.011337 | -0.015968 | 0.017244 | 0.048832 | -0.014167 | 0.065834 | -0.022888 | 122.3282 | -0.20142 | 0.041199 | 121.5042 | 8.3084 | 0.63629 | 0.72327 | 122.5067 | -0.25177 | -0.15564 | 0.09613 | 0.022888 | 0.086975 | -0.72785 | -0.20599 | 0.27466 | 0.17853 | 0.68207 | 0.76904 | 121.55 | 122.374 | 0.022888 | 122.5525 | 8.3542 | -0.20599 | 122.374 | 0.022888 | 8.3542 | 121.55 | 122.5525 | -122.4335 | -122.4838
4060.0938 | 122.3557 | -0.086975 | 122.319 | -0.17509 | 0.0085598 | -0.0072099 | 0.0078442 | 0.046696 | -0.012458 | 0.064766 | 0.064087 | 122.3373 | -0.15564 | 0.15106 | 121.6187 | 8.5785 | 0.86517 | 1.181 | 122.4747 | -0.2243 | -0.068665 | 0.01831 | 0.15106 | 0.23804 | -0.70038 | -0.13733 | 0.15564 | 0.21973 | 0.95215 | 1.268 | 121.7056 | 122.4243 | 0.15106 | 122.5616 | 8.6655 | -0.13733 | 122.4243 | 0.15106 | 8.6655 | 121.7056 | 122.5616 | -122.4747 | -122.5433
4061.7969 | 122.4884 | -0.07782 | 122.2504 | 0.02327 | 0.0098416 | -0.010628 | 0.011049 | 0.04691 | -0.01075 | 0.06498 | 0.018311 | 122.3236 | -0.16022 | 0.091553 | 121.582 | 8.432 | 0.66834 | 0.93842 | 122.4335 | -0.23346 | -0.082397 | 0.073242 | 0.096131 | 0.16937 | -0.66833 | -0.15564 | 0.18311 | 0.17853 | 0.74616 | 1.0162 | 121.6599 | 122.4014 | 0.096131 | 122.5113 | 8.5098 | -0.15564 | 122.4014 | 0.096131 | 8.5098 | 121.6599 | 122.5113 | -122.4106 | -122.4838
4063.5938 | 122.4106 | -0.068665 | 122.2504 | 0.1606 | 0.0089872 | -0.013618 | 0.015321 | 0.04755 | -0.012886 | 0.06733 | 0.086975 | 122.3007 | -0.16937 | 0.17395 | 121.6232 | 8.4686 | 0.48065 | 0.86517 | 122.4289 | -0.21057 | -0.10071 | 0.050354 | 0.15564 | 0.24261 | -0.62714 | -0.14191 | 0.17853 | 0.25635 | 0.54932 | 0.93384 | 121.6919 | 122.3694 | 0.15564 | 122.4976 | 8.5373 | -0.14191 | 122.3694 | 0.15564 | 8.5373 | 121.6919 | 122.4976 | -122.4197 | -122.4609
4065.3906 | 122.4014 | -0.041199 | 122.2549 | 0.12245 | 0.0077054 | -0.011909 | 0.014894 | 0.049687 | -0.014167 | 0.067757 | 0.054932 | 122.3007 | -0.19226 | 0.16022 | 121.6095 | 8.4732 | 0.50812 | 0.85144 | 122.4655 | -0.20599 | -0.15106 | 0.045776 | 0.096131 | 0.20142 | -0.64545 | -0.1648 | 0.21057 | 0.24719 | 0.54932 | 0.89264 | 121.6507 | 122.3419 | 0.096131 | 122.5067 | 8.5144 | -0.1648 | 122.3419 | 0.096131 | 8.5144 | 121.6507 | 122.5067 | -122.4472 | -122.4609
4067.1406 | 122.3602 | -0.10529 | 122.2961 | -0.25139 | 0.0083462 | -0.01725 | 0.014253 | 0.04691 | -0.013099 | 0.065621 | 0.045776 | 122.3282 | -0.17395 | 0.12817 | 121.582 | 8.6105 | 0.93842 | 1.1536 | 122.4838 | -0.2243 | -0.068664 | 0.032043 | 0.15106 | 0.23346 | -0.71411 | -0.11902 | 0.18768 | 0.21973 | 1.0437 | 1.2589 | 121.6873 | 122.4335 | 0.15106 | 122.5891 | 8.7158 | -0.11902 | 122.4335 | 0.15106 | 8.7158 | 121.6873 | 122.5891 | -122.4701 | -122.5204
4068.8438 | 122.4243 | -0.050354 | 122.2549 | 0.13771 | 0.0098416 | -0.0102 | 0.015107 | 0.04755 | -0.013313 | 0.066902 | 0.086975 | 122.3007 | -0.16022 | 0.15564 | 121.6232 | 8.5007 | 0.48065 | 0.86517 | 122.4518 | -0.21057 | -0.10986 | 0.045776 | 0.13733 | 0.20599 | -0.63171 | -0.16022 | 0.19684 | 0.24719 | 0.53101 | 0.91553 | 121.6736 | 122.3511 | 0.13733 | 122.5021 | 8.551 | -0.16022 | 122.3511 | 0.13733 | 8.551 | 121.6736 | 122.5021 | -122.4152 | -122.4655
4070.6094 | 122.4701 | -0.054932 | 122.2549 | 0.00038159 | 0.0094144 | -0.012123 | 0.0097668 | 0.047123 | -0.011604 | 0.067116 | -0.013733 | 122.3053 | -0.17853 | 0.09613 | 121.5866 | 8.5327 | 0.72784 | 0.99792 | 122.4426 | -0.20599 | -0.1236 | 0.050354 | 0.041199 | 0.15106 | -0.66833 | -0.15106 | 0.18768 | 0.16479 | 0.78278 | 1.0529 | 121.6415 | 122.3602 | 0.041199 | 122.4976 | 8.5876 | -0.15106 | 122.3602 | 0.041199 | 8.5876 | 121.6415 | 122.4976 | -122.4335 | -122.4609
4072.375 | 122.3969 | -0.073242 | 122.2687 | -0.24376 | 0.009628 | -0.012764 | 0.014467 | 0.04691 | -0.013099 | 0.066262 | -0.068665 | 122.3419 | -0.21515 | 0.050354 | 121.5179 | 8.5648 | 1.0437 | 1.0574 | 122.4609 | -0.26093 | -0.14191 | 0.073242 | 0.004577 | 0.1236 | -0.75073 | -0.18768 | 0.19226 | 0.14648 | 1.1169 | 1.1307 | 121.5912 | 122.4152 | 0.004577 | 122.5342 | 8.638 | -0.18768 | 122.4152 | 0.004577 | 8.638 | 121.5912 | 122.5342 | -122.4838 | -122.5296
4074.1562 | 122.3648 | -0.082397 | 122.2549 | -0.16747 | 0.01091 | -0.017677 | 0.015962 | 0.045841 | -0.012245 | 0.066689 | -0.032043 | 122.319 | -0.19226 | 0.086975 | 121.5363 | 8.6014 | 0.97961 | 1.0437 | 122.5113 | -0.24719 | -0.10986 | 0.064087 | 0.050354 | 0.16937 | -0.71869 | -0.16479 | 0.25635 | 0.16022 | 1.062 | 1.1261 | 121.6187 | 122.4014 | 0.050354 | 122.5937 | 8.6838 | -0.16479 | 122.4014 | 0.050354 | 8.6838 | 121.6187 | 122.5937 | -122.4472 | -122.5021
4075.8594 | 122.493 | -0.064087 | 122.2412 | 0.046158 | 0.0087734 | -0.013832 | 0.0095532 | 0.048619 | -0.01139 | 0.067116 | 0.009155 | 122.2916 | -0.16479 | 0.09613 | 121.5775 | 8.5419 | 0.65002 | 0.9201 | 122.4289 | -0.2243 | -0.10071 | 0.050354 | 0.073242 | 0.16022 | -0.66376 | -0.16022 | 0.18768 | 0.17395 | 0.71411 | 0.98419 | 121.6415 | 122.3557 | 0.073242 | 122.493 | 8.606 | -0.16022 | 122.3557 | 0.073242 | 8.606 | 121.6415 | 122.493 | -122.406 | -122.4655
4077.625 | 122.3557 | -0.09613 | 122.2778 | -0.17509 | 0.0077054 | -0.010414 | 0.015962 | 0.047978 | -0.015022 | 0.065621 | -0.009155 | 122.3099 | -0.21515 | 0.086975 | 121.5637 | 8.6426 | 0.92468 | 1.0391 | 122.5067 | -0.24261 | -0.11902 | 0.032043 | 0.086975 | 0.1831 | -0.71411 | -0.14649 | 0.22888 | 0.20599 | 1.0208 | 1.1353 | 121.6599 | 122.406 | 0.086975 | 122.6028 | 8.7387 | -0.14649 | 122.406 | 0.086975 | 8.7387 | 121.6599 | 122.6028 | -122.493 | -122.5204
4079.3906 | 122.3465 | -0.10529 | 122.2595 | -0.21324 | 0.009628 | -0.011696 | 0.010621 | 0.047978 | -0.012672 | 0.064553 | 0.059509 | 122.3328 | -0.16479 | 0.16479 | 121.6507 | 8.7387 | 0.85144 | 1.1993 | 122.4564 | -0.2243 | -0.059509 | 0.073243 | 0.16479 | 0.27008 | -0.60883 | -0.11902 | 0.19684 | 0.2243 | 0.95673 | 1.3046 | 121.756 | 122.4381 | 0.16479 | 122.5616 | 8.844 | -0.11902 | 122.4381 | 0.16479 | 8.844 | 121.756 | 122.5616 | -122.4243 | -122.4838
4081.2031 | 122.4747 | -0.045776 | 122.2275 | 0.13008 | 0.0092008 | -0.014259 | 0.015107 | 0.0499 | -0.01374 | 0.066689 | -0.032043 | 122.3328 | -0.20599 | 0.050354 | 121.4951 | 8.4961 | 0.68207 | 0.75073 | 122.4609 | -0.23804 | -0.16022 | 0.10529 | 0.013733 | 0.09613 | -0.73242 | -0.19226 | 0.23346 | 0.17395 | 0.72784 | 0.79651 | 121.5408 | 122.3785 | 0.013733 | 122.5067 | 8.5419 | -0.19226 | 122.3785 | 0.013733 | 8.5419 | 121.5408 | 122.5067 | -122.4335 | -122.4655
4082.9844 | 122.3282 | -0.091553 | 122.2916 | -0.083542 | 0.0085598 | -0.013191 | 0.017671 | 0.046482 | -0.015663 | 0.06733 | 0 | 122.3236 | -0.18768 | 0.10529 | 121.5591 | 8.7021 | 0.87433 | 1.0162 | 122.4792 | -0.24719 | -0.09613 | 0.032043 | 0.091553 | 0.19684 | -0.73242 | -0.15564 | 0.18768 | 0.18768 | 0.96588 | 1.1078 | 121.6507 | 122.4152 | 0.091553 | 122.5708 | 8.7936 | -0.15564 | 122.4152 | 0.091553 | 8.7936 | 121.6507 | 122.5708 | -122.4792 | -122.5388
4084.7031 | 122.4289 | -0.054932 | 122.2733 | 0.13771 | 0.0089872 | -0.014473 | 0.012544 | 0.047978 | -0.012031 | 0.066902 | 0.082397 | 122.3465 | -0.16479 | 0.14648 | 121.6232 | 8.6563 | 0.50354 | 0.89722 | 122.4243 | -0.21057 | -0.10986 | 0.073243 | 0.13733 | 0.20142 | -0.65002 | -0.15564 | 0.15106 | 0.24719 | 0.55847 | 0.95215 | 121.6782 | 122.4014 | 0.13733 | 122.4792 | 8.7112 | -0.15564 | 122.4014 | 0.13733 | 8.7112 | 121.6782 | 122.4792 | -122.438 | -122.4838
4086.4219 | 122.3923 | -0.11902 | 122.2733 | -0.17509 | 0.010269 | -0.015968 | 0.011476 | 0.045201 | -0.012886 | 0.066048 | -0.050354 | 122.3007 | -0.20599 | 0.054932 | 121.5271 | 8.7067 | 1.0574 | 1.1032 | 122.4747 | -0.24719 | -0.086975 | 0.027466 | 0.068665 | 0.17395 | -0.74615 | -0.12817 | 0.20142 | 0.15564 | 1.1765 | 1.2222 | 121.6461 | 122.4197 | 0.068665 | 122.5937 | 8.8257 | -0.12817 | 122.4197 | 0.068665 | 8.8257 | 121.6461 | 122.5937 | -122.4792 | -122.5204
4088.1719 | 122.4747 | -0.054932 | 122.1954 | 0.11482 | 0.010055 | -0.015327 | 0.014467 | 0.048405 | -0.01374 | 0.065834 | -0.054932 | 122.3282 | -0.19684 | 0.022888 | 121.5134 | 8.5739 | 0.70038 | 0.75073 | 122.4655 | -0.24261 | -0.14191 | 0.13275 | 0 | 0.07782 | -0.68207 | -0.18768 | 0.27008 | 0.14191 | 0.75531 | 0.80566 | 121.5683 | 122.3831 | 0 | 122.5204 | 8.6288 | -0.18768 | 122.3831 | 0 | 8.6288 | 121.5683 | 122.5204 | -122.3923 | -122.4381
4089.875 | 122.438 | -0.07782 | 122.2412 | 0.091934 | 0.0072782 | -0.015541 | 0.011476 | 0.046269 | -0.012031 | 0.068825 | 0.059509 | 122.3007 | -0.16022 | 0.13733 | 121.6141 | 8.6792 | 0.54932 | 0.9201 | 122.4472 | -0.20599 | -0.082397 | 0.059509 | 0.13733 | 0.21515 | -0.62714 | -0.12817 | 0.20599 | 0.21973 | 0.62714 | 0.99792 | 121.6919 | 122.3785 | 0.13733 | 122.525 | 8.757 | -0.12817 | 122.3785 | 0.13733 | 8.757 | 121.6919 | 122.525 | -122.4014 | -122.4472
4091.625 | 122.3877 | -0.082397 | 122.2824 | -0.11406 | 0.0074918 | -0.01255 | 0.009126 | 0.044346 | -0.011177 | 0.064766 | 0.054932 | 122.3236 | -0.17395 | 0.17395 | 121.6599 | 8.8165 | 0.79651 | 1.1765 | 122.438 | -0.21515 | -0.091553 | 0.041198 | 0.13733 | 0.25635 | -0.62256 | -0.13275 | 0.15564 | 0.22888 | 0.87891 | 1.2589 | 121.7422 | 122.406 | 0.13733 | 122.5204 | 8.8989 | -0.13275 | 122.406 | 0.13733 | 8.8989 | 121.7422 | 122.5204 | -122.4564 | -122.4976
4093.3281 | 122.3877 | -0.10071 | 122.2687 | -0.014877 | 0.0094144 | -0.012978 | 0.018739 | 0.049046 | -0.018654 | 0.064553 | 0.004578 | 122.3236 | -0.21515 | 0.07782 | 121.5088 | 8.6655 | 0.77362 | 0.87433 | 122.5067 | -0.23346 | -0.11444 | 0.054931 | 0.10529 | 0.17853 | -0.75989 | -0.13275 | 0.23804 | 0.21973 | 0.87433 | 0.97504 | 121.6095 | 122.4243 | 0.10529 | 122.6074 | 8.7662 | -0.13275 | 122.4243 | 0.10529 | 8.7662 | 121.6095 | 122.6074 | -122.4838 | -122.5021
4095.0312 | 122.4426 | -0.059509 | 122.2916 | -0.083542 | 0.0089872 | -0.014046 | 0.0082714 | 0.045628 | -0.0094678 | 0.065407 | 0.018311 | 122.3465 | -0.17395 | 0.13733 | 121.5866 | 8.8028 | 0.80109 | 1.1215 | 122.4472 | -0.22888 | -0.11444 | 0.054932 | 0.07782 | 0.19684 | -0.70496 | -0.16937 | 0.15564 | 0.19226 | 0.86059 | 1.181 | 121.6461 | 122.406 | 0.07782 | 122.5067 | 8.8623 | -0.16937 | 122.406 | 0.07782 | 8.8623 | 121.6461 | 122.5067 | -122.4655 | -122.5204
4096.7188 | 122.3602 | -0.10529 | 122.2733 | 0.0080111 | 0.010269 | -0.014687 | 0.017884 | 0.047764 | -0.015236 | 0.064766 | 0.004578 | 122.3373 | -0.2243 | 0.064087 | 121.5134 | 8.6975 | 0.79651 | 0.86975 | 122.5113 | -0.25177 | -0.11902 | 0.064087 | 0.10986 | 0.16937 | -0.75989 | -0.14648 | 0.23804 | 0.22888 | 0.9018 | 0.97504 | 121.6187 | 122.4426 | 0.10986 | 122.6166 | 8.8028 | -0.14648 | 122.4426 | 0.10986 | 8.8028 | 121.6187 | 122.6166 | -122.4976 | -122.525
4098.4219 | 122.4838 | -0.068665 | 122.2504 | 0.01564 | 0.010055 | -0.014687 | 0.0086988 | 0.047123 | -0.0090406 | 0.066262 | 0 | 122.319 | -0.16022 | 0.10529 | 121.5866 | 8.7341 | 0.73242 | 0.96588 | 122.438 | -0.23804 | -0.091552 | 0.068665 | 0.068665 | 0.17395 | -0.66376 | -0.16937 | 0.18768 | 0.16022 | 0.80109 | 1.0345 | 121.6553 | 122.3877 | 0.068665 | 122.5067 | 8.8028 | -0.16937 | 122.3877 | 0.068665 | 8.8028 | 121.6553 | 122.5067 | -122.4106 | -122.4884
4100.125 | 122.374 | -0.086975 | 122.287 | -0.25902 | 0.0070646 | -0.017464 | 0.015748 | 0.04456 | -0.011818 | 0.067116 | -0.059509 | 122.3145 | -0.20599 | 0.050354 | 121.5179 | 8.7982 | 1.0803 | 1.1078 | 122.4655 | -0.27008 | -0.11902 | 0.027466 | 0.027466 | 0.13733 | -0.76904 | -0.18311 | 0.17853 | 0.14649 | 1.1673 | 1.1948 | 121.6049 | 122.4014 | 0.027466 | 122.5525 | 8.8852 | -0.18311 | 122.4014 | 0.027466 | 8.8852 | 121.6049 | 122.5525 | -122.493 | -122.5571
4101.8281 | 122.4838 | -0.050354 | 122.2504 | 0.0080111 | 0.0083462 | -0.013405 | 0.0093396 | 0.046055 | -0.0092542 | 0.066262 | 0.009155 | 122.3145 | -0.17853 | 0.09613 | 121.5866 | 8.7708 | 0.76904 | 1.0162 | 122.4792 | -0.21973 | -0.12817 | 0.064087 | 0.059509 | 0.14648 | -0.66376 | -0.16937 | 0.22888 | 0.18768 | 0.8194 | 1.0666 | 121.637 | 122.3648 | 0.059509 | 122.5296 | 8.8211 | -0.16937 | 122.3648 | 0.059509 | 8.8211 | 121.637 | 122.5296 | -122.4289 | -122.4701
4103.5781 | 122.4518 | -0.050354 | 122.2458 | 0.091934 | 0.009628 | -0.013405 | 0.015748 | 0.049046 | -0.012245 | 0.065407 | -0.027466 | 122.3373 | -0.20599 | 0.059509 | 121.5179 | 8.6884 | 0.65002 | 0.78278 | 122.4609 | -0.24261 | -0.15564 | 0.091552 | 0.022888 | 0.10986 | -0.72785 | -0.19226 | 0.21515 | 0.17853 | 0.70038 | 0.83313 | 121.5683 | 122.3877 | 0.022888 | 122.5113 | 8.7387 | -0.19226 | 122.3877 | 0.022888 | 8.7387 | 121.5683 | 122.5113 | -122.4518 | -122.4884
4105.2812 | 122.3648 | -0.09613 | 122.2733 | -0.19798 | 0.010055 | -0.01255 | 0.011049 | 0.047337 | -0.013099 | 0.066689 | 0.032043 | 122.3328 | -0.16022 | 0.14191 | 121.5866 | 8.9172 | 0.97961 | 1.1993 | 122.4426 | -0.24261 | -0.064087 | 0.05951 | 0.12817 | 0.23804 | -0.68664 | -0.14649 | 0.16937 | 0.19226 | 1.0757 | 1.2955 | 121.6827 | 122.4289 | 0.12817 | 122.5388 | 9.0134 | -0.14649 | 122.4289 | 0.12817 | 9.0134 | 121.6827 | 122.5388 | -122.4335 | -122.5159
4106.9844 | 122.4609 | -0.045776 | 122.2549 | -0.053024 | 0.0087734 | -0.014046 | 0.0095532 | 0.047123 | -0.011818 | 0.065834 | 0.013733 | 122.3099 | -0.17395 | 0.12817 | 121.6141 | 8.8715 | 0.79193 | 1.1215 | 122.406 | -0.21973 | -0.12817 | 0.054931 | 0.059509 | 0.17395 | -0.64087 | -0.17395 | 0.15106 | 0.18768 | 0.83771 | 1.1673 | 121.6599 | 122.3557 | 0.059509 | 122.4518 | 8.9172 | -0.17395 | 122.3557 | 0.059509 | 8.9172 | 121.6599 | 122.4518 | -122.4289 | -122.4747
4108.6875 | 122.3511 | -0.09613 | 122.2687 | -0.075912 | 0.010482 | -0.013405 | 0.017671 | 0.046269 | -0.014381 | 0.066262 | 0.013733 | 122.3053 | -0.20599 | 0.11902 | 121.5546 | 8.8486 | 0.83313 | 0.99335 | 122.4792 | -0.25177 | -0.10986 | 0.036621 | 0.10986 | 0.21515 | -0.71411 | -0.15564 | 0.21057 | 0.21973 | 0.92926 | 1.0895 | 121.6507 | 122.4014 | 0.10986 | 122.5754 | 8.9447 | -0.15564 | 122.4014 | 0.10986 | 8.9447 | 121.6507 | 122.5754 | -122.4747 | -122.5204
4110.375 | 122.4564 | -0.054932 | 122.2458 | -0.0072479 | 0.0098416 | -0.017036 | 0.010194 | 0.046482 | -0.011604 | 0.066048 | 0.004578 | 122.3373 | -0.17853 | 0.1236 | 121.5958 | 8.844 | 0.7782 | 1.0529 | 122.4609 | -0.21515 | -0.1236 | 0.091552 | 0.05951 | 0.17853 | -0.65002 | -0.16022 | 0.21515 | 0.18311 | 0.83313 | 1.1078 | 121.6507 | 122.3923 | 0.05951 | 122.5159 | 8.8989 | -0.16022 | 122.3923 | 0.05951 | 8.8989 | 121.6507 | 122.5159 | -122.4243 | -122.4609
4112.0781 | 122.4014 | -0.10986 | 122.287 | -0.24376 | 0.010269 | -0.013618 | 0.015962 | 0.046055 | -0.013954 | 0.066902 | -0.054932 | 122.3557 | -0.21973 | 0.059509 | 121.5179 | 8.8898 | 1.0803 | 1.1124 | 122.5067 | -0.25177 | -0.10986 | 0.068665 | 0.054931 | 0.16937 | -0.76904 | -0.14191 | 0.21973 | 0.16479 | 1.1902 | 1.2222 | 121.6278 | 122.4655 | 0.054931 | 122.6166 | 8.9996 | -0.14191 | 122.4655 | 0.054931 | 8.9996 | 121.6278 | 122.6166 | -122.5067 | -122.5388
4113.7812 | 122.4655 | -0.045776 | 122.2183 | 0.14534 | 0.010482 | -0.014473 | 0.015962 | 0.049687 | -0.014808 | 0.065834 | -0.041199 | 122.3465 | -0.21057 | 0.045776 | 121.4996 | 8.7616 | 0.72784 | 0.78735 | 122.4838 | -0.24261 | -0.1648 | 0.12817 | 0.004577 | 0.091552 | -0.71869 | -0.19684 | 0.2655 | 0.16937 | 0.77362 | 0.83313 | 121.5454 | 122.3923 | 0.004577 | 122.5296 | 8.8074 | -0.19684 | 122.3923 | 0.004577 | 8.8074 | 121.5454 | 122.5296 | -122.4289 | -122.4609
4115.5312 | 122.4152 | -0.068665 | 122.2412 | 0.053787 | 0.0092008 | -0.014687 | 0.015535 | 0.049046 | -0.01374 | 0.066902 | -0.041199 | 122.3373 | -0.20599 | 0.050354 | 121.4905 | 8.8074 | 0.80566 | 0.85602 | 122.4884 | -0.23346 | -0.13733 | 0.09613 | 0.027466 | 0.11902 | -0.75073 | -0.16479 | 0.24719 | 0.1648 | 0.87433 | 0.92468 | 121.5591 | 122.406 | 0.027466 | 122.5571 | 8.876 | -0.16479 | 122.406 | 0.027466 | 8.876 | 121.5591 | 122.5571 | -122.4472 | -122.4747
4117.2344 | 122.4747 | -0.054932 | 122.2641 | 0.00038159 | 0.0077054 | -0.017464 | 0.0078442 | 0.047764 | -0.011177 | 0.065834 | 0.004578 | 122.3511 | -0.16479 | 0.10071 | 121.6003 | 8.8943 | 0.79193 | 1.0254 | 122.4426 | -0.23346 | -0.10986 | 0.086975 | 0.05951 | 0.15564 | -0.66376 | -0.17853 | 0.17853 | 0.16937 | 0.84686 | 1.0803 | 121.6553 | 122.406 | 0.05951 | 122.4976 | 8.9493 | -0.17853 | 122.406 | 0.05951 | 8.9493 | 121.6553 | 122.4976 | -122.4289 | -122.4976
4118.9375 | 122.3419 | -0.10529 | 122.2641 | -0.083542 | 0.010269 | -0.012123 | 0.016389 | 0.047123 | -0.015236 | 0.063698 | 0.018311 | 122.3145 | -0.20599 | 0.11902 | 121.5408 | 8.9493 | 0.85144 | 1.0117 | 122.4792 | -0.25177 | -0.10071 | 0.050354 | 0.1236 | 0.22431 | -0.72327 | -0.14648 | 0.21515 | 0.22431 | 0.95673 | 1.1169 | 121.6461 | 122.4197 | 0.1236 | 122.5845 | 9.0546 | -0.14648 | 122.4197 | 0.1236 | 9.0546 | 121.6461 | 122.5845 | -122.4701 | -122.5159
4120.6406 | 122.4426 | -0.054932 | 122.2229 | 0.13008 | 0.010482 | -0.0149 | 0.014039 | 0.049473 | -0.012245 | 0.067543 | -0.009155 | 122.3145 | -0.20142 | 0.073242 | 121.55 | 8.8531 | 0.62714 | 0.82855 | 122.4609 | -0.21973 | -0.14648 | 0.091553 | 0.045777 | 0.12817 | -0.67291 | -0.16479 | 0.23804 | 0.19226 | 0.68207 | 0.88348 | 121.6049 | 122.3694 | 0.045777 | 122.5159 | 8.9081 | -0.16479 | 122.3694 | 0.045777 | 8.9081 | 121.6049 | 122.5159 | -122.4243 | -122.4426
4122.3281 | 122.3923 | -0.086975 | 122.2824 | -0.19798 | 0.0083462 | -0.013618 | 0.0095532 | 0.044132 | -0.010963 | 0.064553 | -0.054932 | 122.3465 | -0.19226 | 0.050354 | 121.5271 | 8.9722 | 1.1032 | 1.1307 | 122.4838 | -0.25177 | -0.10529 | 0.064087 | 0.032043 | 0.13733 | -0.75531 | -0.16479 | 0.20142 | 0.13733 | 1.1902 | 1.2177 | 121.6141 | 122.4335 | 0.032043 | 122.5708 | 9.0591 | -0.16479 | 122.4335 | 0.032043 | 9.0591 | 121.6141 | 122.5708 | -122.4747 | -122.5342
4124.0312 | 122.4609 | -0.050354 | 122.2412 | 0.076676 | 0.0087734 | -0.01255 | 0.013612 | 0.048619 | -0.015876 | 0.064766 | -0.018311 | 122.374 | -0.21515 | 0.045776 | 121.5134 | 8.8577 | 0.71411 | 0.79651 | 122.5113 | -0.24719 | -0.16479 | 0.13275 | 0.032043 | 0.09613 | -0.72784 | -0.19684 | 0.27008 | 0.19684 | 0.76447 | 0.84686 | 121.5637 | 122.4243 | 0.032043 | 122.5616 | 8.9081 | -0.19684 | 122.4243 | 0.032043 | 8.9081 | 121.5637 | 122.5616 | -122.4564 | -122.4884
4125.75 | 122.4747 | -0.050354 | 122.2275 | 0.099564 | 0.010482 | -0.016182 | 0.015107 | 0.049259 | -0.012458 | 0.068184 | -0.050354 | 122.3465 | -0.19684 | 0.027466 | 121.4951 | 8.876 | 0.78735 | 0.80566 | 122.5113 | -0.22888 | -0.14648 | 0.11902 | 0 | 0.07782 | -0.73242 | -0.17853 | 0.28381 | 0.14648 | 0.83771 | 0.85602 | 121.5454 | 122.3969 | 0 | 122.5616 | 8.9264 | -0.17853 | 122.3969 | 0 | 8.9264 | 121.5454 | 122.5616 | -122.4243 | -122.4564
4127.4375 | 122.3969 | -0.064087 | 122.2549 | 0.1606 | 0.0083462 | -0.0078507 | 0.009126 | 0.046055 | -0.011604 | 0.066475 | 0.059509 | 122.3053 | -0.15564 | 0.16022 | 121.6187 | 8.9722 | 0.55389 | 0.93842 | 122.4655 | -0.18768 | -0.091553 | 0.050354 | 0.1236 | 0.2243 | -0.63629 | -0.1236 | 0.21057 | 0.21515 | 0.61798 | 1.0025 | 121.6827 | 122.3694 | 0.1236 | 122.5296 | 9.0363 | -0.1236 | 122.3694 | 0.1236 | 9.0363 | 121.6827 | 122.5296 | -122.4106 | -122.4426
4129.1406 | 122.4197 | -0.068665 | 122.2412 | 0.15297 | 0.0072782 | -0.0095597 | 0.01468 | 0.048619 | -0.014381 | 0.066902 | 0.064087 | 122.3236 | -0.13275 | 0.15564 | 121.6049 | 8.9996 | 0.54932 | 0.94757 | 122.4472 | -0.20599 | -0.064086 | 0.082397 | 0.13275 | 0.22431 | -0.63629 | -0.13733 | 0.20599 | 0.19684 | 0.61798 | 1.0162 | 121.6736 | 122.3923 | 0.13275 | 122.5159 | 9.0683 | -0.13733 | 122.3923 | 0.13275 | 9.0683 | 121.6736 | 122.5159 | -122.374 | -122.4472
4130.8281 | 122.374 | -0.11444 | 122.2733 | -0.23613 | 0.0089872 | -0.015541 | 0.010835 | 0.045414 | -0.01374 | 0.064766 | 0.009155 | 122.3328 | -0.18768 | 0.10529 | 121.5637 | 9.0912 | 1.0666 | 1.1993 | 122.4747 | -0.22888 | -0.073242 | 0.05951 | 0.1236 | 0.21973 | -0.70953 | -0.11444 | 0.20142 | 0.19684 | 1.181 | 1.3138 | 121.6782 | 122.4472 | 0.1236 | 122.5891 | 9.2056 | -0.11444 | 122.4472 | 0.1236 | 9.2056 | 121.6782 | 122.5891 | -122.4609 | -122.5021
4132.5312 | 122.3923 | -0.07782 | 122.2504 | 0.00038159 | 0.0081326 | -0.0102 | 0.01468 | 0.050328 | -0.014381 | 0.065621 | -0.013733 | 122.3328 | -0.21515 | 0.054932 | 121.4859 | 8.9584 | 0.8194 | 0.87891 | 122.5296 | -0.23346 | -0.13733 | 0.082398 | 0.064087 | 0.13275 | -0.76447 | -0.15564 | 0.27924 | 0.20142 | 0.89722 | 0.95673 | 121.5637 | 122.4106 | 0.064087 | 122.6074 | 9.0363 | -0.15564 | 122.4106 | 0.064087 | 9.0363 | 121.5637 | 122.6074 | -122.4655 | -122.4838
4134.25 | 122.3923 | -0.09613 | 122.2733 | -0.47264 | 0.01091 | -0.013191 | 0.010408 | 0.046696 | -0.012031 | 0.067543 | -0.036621 | 122.3602 | -0.1831 | 0.045776 | 121.5179 | 9.0775 | 1.0895 | 1.1536 | 122.4655 | -0.27008 | -0.086975 | 0.086975 | 0.059509 | 0.14191 | -0.75531 | -0.17395 | 0.19226 | 0.14648 | 1.1856 | 1.2497 | 121.6141 | 122.4564 | 0.059509 | 122.5616 | 9.1736 | -0.17395 | 122.4564 | 0.059509 | 9.1736 | 121.6141 | 122.5616 | -122.4564 | -122.5433
4135.9375 | 122.4518 | -0.045776 | 122.2275 | 0.099564 | 0.010269 | -0.01255 | 0.011049 | 0.047764 | -0.013954 | 0.067116 | 0.041199 | 122.3007 | -0.16479 | 0.13733 | 121.5729 | 9.0271 | 0.65002 | 0.95673 | 122.4747 | -0.19684 | -0.11902 | 0.073242 | 0.086975 | 0.18311 | -0.6546 | -0.15106 | 0.24719 | 0.20599 | 0.6958 | 1.0025 | 121.6187 | 122.3465 | 0.086975 | 122.5204 | 9.0729 | -0.15106 | 122.3465 | 0.086975 | 9.0729 | 121.6187 | 122.5204 | -122.3923 | -122.4243
4137.6406 | 122.4609 | -0.07782 | 122.2504 | -0.060654 | 0.0085598 | -0.012764 | 0.0099804 | 0.047764 | -0.012458 | 0.066262 | 0.013733 | 122.3511 | -0.16022 | 0.13733 | 121.6095 | 9.1095 | 0.84686 | 1.1627 | 122.4609 | -0.2243 | -0.082397 | 0.10071 | 0.091553 | 0.21515 | -0.64087 | -0.14648 | 0.21057 | 0.17395 | 0.92468 | 1.2405 | 121.6873 | 122.4289 | 0.091553 | 122.5388 | 9.1873 | -0.14648 | 122.4289 | 0.091553 | 9.1873 | 121.6873 | 122.5388 | -122.4106 | -122.4747
4139.3438 | 122.3328 | -0.10529 | 122.2824 | -0.10643 | 0.012191 | -0.013832 | 0.017671 | 0.047764 | -0.015876 | 0.065621 | 0.022888 | 122.3236 | -0.21057 | 0.1236 | 121.5408 | 9.1461 | 0.93384 | 1.0986 | 122.4976 | -0.22888 | -0.10529 | 0.041198 | 0.12817 | 0.22888 | -0.74158 | -0.1236 | 0.21515 | 0.23346 | 1.0391 | 1.2039 | 121.6461 | 122.4289 | 0.12817 | 122.6028 | 9.2514 | -0.1236 | 122.4289 | 0.12817 | 9.2514 | 121.6461 | 122.6028 | -122.493 | -122.5113
4141.1094 | 122.4335 | -0.045776 | 122.2504 | 0.14534 | 0.011764 | -0.011055 | 0.015962 | 0.050114 | -0.013099 | 0.066902 | -0.022888 | 122.3419 | -0.20599 | 0.086975 | 121.5317 | 9.0134 | 0.6546 | 0.86517 | 122.5113 | -0.22888 | -0.16022 | 0.091553 | 0.022888 | 0.13275 | -0.71869 | -0.18311 | 0.26093 | 0.18311 | 0.70038 | 0.91095 | 121.5775 | 122.3877 | 0.022888 | 122.5571 | 9.0591 | -0.18311 | 122.3877 | 0.022888 | 9.0591 | 121.5775 | 122.5571 | -122.4564 | -122.4792
4142.7969 | 122.3648 | -0.091553 | 122.2961 | -0.19798 | 0.0094144 | -0.014687 | 0.011476 | 0.044132 | -0.013099 | 0.066048 | 0.050354 | 122.3007 | -0.17395 | 0.14648 | 121.5958 | 9.2422 | 1.0391 | 1.2543 | 122.4426 | -0.22888 | -0.082397 | 0.004577 | 0.14191 | 0.23804 | -0.70038 | -0.13733 | 0.14648 | 0.2243 | 1.1307 | 1.3458 | 121.6873 | 122.3923 | 0.14191 | 122.5342 | 9.3338 | -0.13733 | 122.3923 | 0.14191 | 9.3338 | 121.6873 | 122.5342 | -122.4701 | -122.525
4144.4844 | 122.4655 | -0.054932 | 122.2458 | 0.12245 | 0.0092008 | -0.012978 | 0.016176 | 0.049687 | -0.013099 | 0.066902 | -0.054932 | 122.3328 | -0.20142 | 0.036621 | 121.4905 | 9.0042 | 0.75531 | 0.82855 | 122.5113 | -0.24719 | -0.14648 | 0.086975 | 0 | 0.091553 | -0.75531 | -0.19226 | 0.2655 | 0.14648 | 0.81024 | 0.88348 | 121.5454 | 122.3877 | 0 | 122.5662 | 9.0591 | -0.19226 | 122.3877 | 0 | 9.0591 | 121.5454 | 122.5662 | -122.4472 | -122.493
4146.1875 | 122.4701 | -0.054932 | 122.2366 | 0.01564 | 0.0070646 | -0.015755 | 0.0082714 | 0.047337 | -0.01139 | 0.066902 | 0.009155 | 122.3282 | -0.17395 | 0.091553 | 121.5912 | 9.1415 | 0.84228 | 1.0666 | 122.4701 | -0.22888 | -0.11902 | 0.091553 | 0.064087 | 0.14649 | -0.64545 | -0.17395 | 0.23346 | 0.1831 | 0.89722 | 1.1215 | 121.6461 | 122.3831 | 0.064087 | 122.525 | 9.1965 | -0.17395 | 122.3831 | 0.064087 | 9.1965 | 121.6461 | 122.525 | -122.4106 | -122.4655
4147.8906 | 122.3969 | -0.086975 | 122.2778 | -0.17509 | 0.0051418 | -0.0149 | 0.012758 | 0.046696 | -0.013313 | 0.06733 | -0.050354 | 122.3053 | -0.20142 | 0.068665 | 121.5225 | 9.1965 | 1.1261 | 1.1627 | 122.4838 | -0.25635 | -0.11444 | 0.027466 | 0.036621 | 0.15564 | -0.75531 | -0.16937 | 0.20599 | 0.15106 | 1.2131 | 1.2497 | 121.6095 | 122.3923 | 0.036621 | 122.5708 | 9.2834 | -0.16937 | 122.3923 | 0.036621 | 9.2834 | 121.6095 | 122.5708 | -122.4792 | -122.5342
4149.6094 | 122.3557 | -0.086975 | 122.2733 | -0.19798 | 0.0072782 | -0.0099869 | 0.014253 | 0.047978 | -0.014595 | 0.066262 | -0.022888 | 122.2916 | -0.2243 | 0.09613 | 121.5408 | 9.2194 | 1.0117 | 1.1307 | 122.4747 | -0.25177 | -0.13733 | 0.018311 | 0.064087 | 0.1831 | -0.73242 | -0.16479 | 0.20142 | 0.20142 | 1.0986 | 1.2177 | 121.6278 | 122.3785 | 0.064087 | 122.5616 | 9.3063 | -0.16479 | 122.3785 | 0.064087 | 9.3063 | 121.6278 | 122.5616 | -122.4976 | -122.525
4151.3125 | 122.4609 | -0.041199 | 122.2412 | 0.084305 | 0.0098416 | -0.012123 | 0.015535 | 0.049687 | -0.014167 | 0.065621 | -0.050354 | 122.3465 | -0.21515 | 0.022888 | 121.4905 | 9.082 | 0.81482 | 0.8606 | 122.5067 | -0.25177 | -0.17395 | 0.10529 | -0.009155 | 0.064087 | -0.75073 | -0.21057 | 0.2655 | 0.16479 | 0.85602 | 0.9018 | 121.5317 | 122.3877 | -0.009155 | 122.5479 | 9.1232 | -0.21057 | 122.3877 | -0.009155 | 9.1232 | 121.5317 | 122.5479 | -122.4564 | -122.493
4153.0781 | 122.4976 | -0.036621 | 122.2412 | 0.00038159 | 0.010055 | -0.018532 | 0.0082714 | 0.045628 | -0.01139 | 0.064766 | -0.004578 | 122.3373 | -0.16937 | 0.09613 | 121.5775 | 9.1644 | 0.80566 | 1.0529 | 122.438 | -0.22888 | -0.13275 | 0.09613 | 0.032043 | 0.13275 | -0.66376 | -0.19226 | 0.19684 | 0.16479 | 0.84229 | 1.0895 | 121.6141 | 122.374 | 0.032043 | 122.4747 | 9.2011 | -0.19226 | 122.374 | 0.032043 | 9.2011 | 121.6141 | 122.4747 | -122.4106 | -122.4701
4154.7812 | 122.3785 | -0.09613 | 122.2733 | -0.16747 | 0.010055 | -0.013618 | 0.014253 | 0.047337 | -0.012245 | 0.065407 | -0.041199 | 122.3328 | -0.2243 | 0.059509 | 121.5271 | 9.2468 | 1.0941 | 1.1444 | 122.5113 | -0.24261 | -0.12817 | 0.05951 | 0.054931 | 0.15564 | -0.74615 | -0.14649 | 0.23804 | 0.18311 | 1.1902 | 1.2405 | 121.6232 | 122.4289 | 0.054931 | 122.6074 | 9.343 | -0.14649 | 122.4289 | 0.054931 | 9.343 | 121.6232 | 122.6074 | -122.4976 | -122.5159
4156.5312 | 122.3877 | -0.086975 | 122.3007 | -0.2285 | 0.0094144 | -0.0149 | 0.013612 | 0.050968 | -0.013313 | 0.065407 | -0.036621 | 122.3602 | -0.21057 | 0.050354 | 121.5179 | 9.2606 | 1.1124 | 1.149 | 122.5021 | -0.26093 | -0.1236 | 0.059509 | 0.050354 | 0.13733 | -0.78278 | -0.17395 | 0.20142 | 0.17395 | 1.1993 | 1.236 | 121.6049 | 122.4472 | 0.050354 | 122.5891 | 9.3475 | -0.17395 | 122.4472 | 0.050354 | 9.3475 | 121.6049 | 122.5891 | -122.5113 | -122.5616
4158.2344 | 122.4106 | -0.059509 | 122.2412 | 0.14534 | 0.0098416 | -0.014473 | 0.012544 | 0.0499 | -0.012031 | 0.066902 | 0.073242 | 122.3282 | -0.16022 | 0.16022 | 121.6003 | 9.2285 | 0.58594 | 0.97504 | 122.4609 | -0.21057 | -0.10071 | 0.086975 | 0.13275 | 0.21973 | -0.64087 | -0.15106 | 0.21973 | 0.23346 | 0.64545 | 1.0345 | 121.6599 | 122.3877 | 0.13275 | 122.5204 | 9.288 | -0.15106 | 122.3877 | 0.13275 | 9.288 | 121.6599 | 122.5204 | -122.4014 | -122.4518
4159.9375 | 122.374 | -0.086975 | 122.2687 | -0.15221 | 0.0085598 | -0.017891 | 0.0080578 | 0.047337 | -0.012245 | 0.065834 | 0.054932 | 122.3007 | -0.16022 | 0.16937 | 121.6415 | 9.3658 | 0.86975 | 1.2634 | 122.438 | -0.21515 | -0.073242 | 0.032043 | 0.14191 | 0.25635 | -0.62714 | -0.12817 | 0.16937 | 0.21515 | 0.95673 | 1.3504 | 121.7285 | 122.3877 | 0.14191 | 122.525 | 9.4528 | -0.12817 | 122.3877 | 0.14191 | 9.4528 | 121.7285 | 122.525 | -122.4289 | -122.4838
4161.625 | 122.4747 | -0.068665 | 122.2641 | 0.046158 | 0.0077054 | -0.016609 | 0.010835 | 0.045841 | -0.013099 | 0.066689 | 0.013733 | 122.3053 | -0.17395 | 0.10529 | 121.5637 | 9.2422 | 0.76904 | 1.0208 | 122.4518 | -0.23346 | -0.10528 | 0.041199 | 0.082398 | 0.17395 | -0.70038 | -0.16479 | 0.18768 | 0.18768 | 0.83771 | 1.0895 | 121.6324 | 122.374 | 0.082398 | 122.5204 | 9.3109 | -0.16479 | 122.374 | 0.082398 | 9.3109 | 121.6324 | 122.5204 | -122.438 | -122.4976
4163.3438 | 122.3465 | -0.11444 | 122.3007 | -0.19035 | 0.0074918 | -0.014687 | 0.011689 | 0.045628 | -0.012672 | 0.065193 | 0.068665 | 122.3145 | -0.18768 | 0.16937 | 121.6187 | 9.407 | 0.98877 | 1.3184 | 122.4426 | -0.20599 | -0.073242 | 0.013733 | 0.18311 | 0.28381 | -0.68207 | -0.091553 | 0.14191 | 0.25635 | 1.1032 | 1.4328 | 121.7331 | 122.4289 | 0.18311 | 122.5571 | 9.5215 | -0.091553 | 122.4289 | 0.18311 | 9.5215 | 121.7331 | 122.5571 | -122.4884 | -122.5067
4165.0469 | 122.3831 | -0.073242 | 122.2916 | -0.25902 | 0.0089872 | -0.013618 | 0.013612 | 0.044346 | -0.012886 | 0.065621 | -0.032043 | 122.3465 | -0.2243 | 0.068665 | 121.5134 | 9.3338 | 1.1673 | 1.1993 | 122.4518 | -0.25635 | -0.15106 | 0.054932 | 0.041199 | 0.14191 | -0.7782 | -0.18311 | 0.16022 | 0.19226 | 1.2405 | 1.2726 | 121.5866 | 122.4197 | 0.041199 | 122.525 | 9.407 | -0.18311 | 122.4197 | 0.041199 | 9.407 | 121.5866 | 122.525 | -122.5159 | -122.5479
4166.75 | 122.3511 | -0.10071 | 122.2916 | -0.16747 | 0.0087734 | -0.01255 | 0.010621 | 0.045628 | -0.010963 | 0.06498 | 0.027466 | 122.287 | -0.17853 | 0.16937 | 121.6141 | 9.4299 | 1.0071 | 1.3092 | 122.4426 | -0.23346 | -0.07782 | -0.004578 | 0.12817 | 0.27008 | -0.67749 | -0.13275 | 0.15106 | 0.20599 | 1.1078 | 1.4099 | 121.7148 | 122.3877 | 0.12817 | 122.5433 | 9.5306 | -0.13275 | 122.3877 | 0.12817 | 9.5306 | 121.7148 | 122.5433 | -122.4701 | -122.525
4168.4375 | 122.4609 | -0.032043 | 122.2504 | 0.10719 | 0.0083462 | -0.010414 | 0.018739 | 0.04755 | -0.01374 | 0.065834 | -0.018311 | 122.3373 | -0.21515 | 0.064087 | 121.5134 | 9.2148 | 0.75989 | 0.87433 | 122.4976 | -0.23804 | -0.18311 | 0.086975 | 0.013732 | 0.09613 | -0.737 | -0.20599 | 0.24719 | 0.19684 | 0.79193 | 0.90637 | 121.5454 | 122.3694 | 0.013732 | 122.5296 | 9.2468 | -0.20599 | 122.3694 | 0.013732 | 9.2468 | 121.5454 | 122.5296 | -122.4655 | -122.4884
4170.1406 | 122.4655 | -0.054932 | 122.2366 | -0.045395 | 0.0092008 | -0.013832 | 0.009126 | 0.04691 | -0.012458 | 0.065407 | 0.009155 | 122.3373 | -0.16937 | 0.11902 | 121.6003 | 9.3704 | 0.88806 | 1.1719 | 122.4518 | -0.20599 | -0.11444 | 0.10071 | 0.064087 | 0.17395 | -0.63629 | -0.15106 | 0.21515 | 0.17853 | 0.94299 | 1.2268 | 121.6553 | 122.3923 | 0.064087 | 122.5067 | 9.4254 | -0.15106 | 122.3923 | 0.064087 | 9.4254 | 121.6553 | 122.5067 | -122.406 | -122.4426
4171.8438 | 122.3328 | -0.09613 | 122.2824 | -0.098801 | 0.0085598 | -0.014473 | 0.017884 | 0.046696 | -0.014381 | 0.065621 | 0.013733 | 122.3282 | -0.21057 | 0.10986 | 121.5546 | 9.3979 | 0.99792 | 1.1536 | 122.4747 | -0.23346 | -0.11444 | 0.045776 | 0.10986 | 0.20599 | -0.72785 | -0.13733 | 0.19226 | 0.2243 | 1.0941 | 1.2497 | 121.6507 | 122.4243 | 0.10986 | 122.5708 | 9.494 | -0.13733 | 122.4243 | 0.10986 | 9.494 | 121.6507 | 122.5708 | -122.493 | -122.5159
4173.5938 | 122.3602 | -0.10529 | 122.2778 | -0.13695 | 0.0077054 | -0.015541 | 0.0089124 | 0.046482 | -0.012458 | 0.063484 | 0.07782 | 122.3328 | -0.15564 | 0.18768 | 121.6507 | 9.5123 | 0.94299 | 1.3046 | 122.4472 | -0.21057 | -0.050354 | 0.054932 | 0.18311 | 0.29297 | -0.62714 | -0.10529 | 0.16937 | 0.23346 | 1.0483 | 1.4099 | 121.756 | 122.4381 | 0.18311 | 122.5525 | 9.6176 | -0.10529 | 122.4381 | 0.18311 | 9.6176 | 121.756 | 122.5525 | -122.4335 | -122.4884
4175.2969 | 122.3557 | -0.082397 | 122.287 | -0.19035 | 0.0087734 | -0.01255 | 0.016816 | 0.047764 | -0.014595 | 0.06498 | -0.032043 | 122.3099 | -0.22888 | 0.10529 | 121.5408 | 9.4391 | 1.0574 | 1.1673 | 122.5021 | -0.24261 | -0.14649 | 0.022888 | 0.050354 | 0.18768 | -0.74615 | -0.16022 | 0.21515 | 0.19684 | 1.1398 | 1.2497 | 121.6232 | 122.3923 | 0.050354 | 122.5845 | 9.5215 | -0.16022 | 122.3923 | 0.050354 | 9.5215 | 121.6232 | 122.5845 | -122.5159 | -122.5296
4177.0625 | 122.3831 | -0.10071 | 122.2641 | -0.2285 | 0.0072782 | -0.016609 | 0.012971 | 0.045841 | -0.015449 | 0.06733 | -0.050354 | 122.3099 | -0.21515 | 0.059509 | 121.5317 | 9.4116 | 1.1719 | 1.2039 | 122.5021 | -0.25635 | -0.11444 | 0.045776 | 0.050354 | 0.16022 | -0.73242 | -0.15564 | 0.23804 | 0.16479 | 1.2726 | 1.3046 | 121.6324 | 122.4106 | 0.050354 | 122.6028 | 9.5123 | -0.15564 | 122.4106 | 0.050354 | 9.5123 | 121.6324 | 122.6028 | -122.4792 | -122.5204
4178.7656 | 122.4197 | -0.068665 | 122.2595 | 0.084305 | 0.0092008 | -0.011055 | 0.015535 | 0.04755 | -0.016517 | 0.06733 | -0.013733 | 122.3373 | -0.20142 | 0.036621 | 121.4905 | 9.3246 | 0.89722 | 0.93384 | 122.5113 | -0.25635 | -0.13275 | 0.07782 | 0.054932 | 0.10529 | -0.76904 | -0.18768 | 0.25177 | 0.18768 | 0.96588 | 1.0025 | 121.5591 | 122.406 | 0.054932 | 122.58 | 9.3933 | -0.18768 | 122.406 | 0.054932 | 9.3933 | 121.5591 | 122.58 | -122.4609 | -122.5159
4180.4688 | 122.438 | -0.064087 | 122.2687 | -0.083542 | 0.0070646 | -0.015968 | 0.0065624 | 0.046269 | -0.012245 | 0.066048 | 0.027466 | 122.3419 | -0.17395 | 0.13275 | 121.6187 | 9.4986 | 0.91553 | 1.236 | 122.4335 | -0.22888 | -0.10986 | 0.073242 | 0.091553 | 0.19684 | -0.65002 | -0.16479 | 0.16479 | 0.20142 | 0.97961 | 1.3 | 121.6827 | 122.406 | 0.091553 | 122.4976 | 9.5627 | -0.16479 | 122.406 | 0.091553 | 9.5627 | 121.6827 | 122.4976 | -122.4426 | -122.4976
4182.1875 | 122.4518 | -0.036621 | 122.2504 | 0.13008 | 0.0081326 | -0.015327 | 0.015748 | 0.045841 | -0.014381 | 0.066689 | -0.027466 | 122.3145 | -0.20142 | 0.073242 | 121.5363 | 9.3613 | 0.71411 | 0.91095 | 122.4747 | -0.22888 | -0.1648 | 0.064087 | 0.009155 | 0.10986 | -0.71411 | -0.19226 | 0.2243 | 0.17395 | 0.75073 | 0.94757 | 121.5729 | 122.3511 | 0.009155 | 122.5113 | 9.3979 | -0.19226 | 122.3511 | 0.009155 | 9.3979 | 121.5729 | 122.5113 | -122.4518 | -122.4792
4183.8906 | 122.3419 | -0.10529 | 122.3007 | -0.18272 | 0.0092008 | -0.020668 | 0.011049 | 0.048191 | -0.01374 | 0.06733 | 0.059509 | 122.3053 | -0.16022 | 0.15564 | 121.6141 | 9.5718 | 1.0391 | 1.3184 | 122.4335 | -0.21515 | -0.054931 | 0.004578 | 0.16479 | 0.26093 | -0.68664 | -0.10986 | 0.13275 | 0.21973 | 1.1444 | 1.4236 | 121.7194 | 122.4106 | 0.16479 | 122.5388 | 9.6771 | -0.10986 | 122.4106 | 0.16479 | 9.6771 | 121.7194 | 122.5388 | -122.4609 | -122.5159
4185.625 | 122.4335 | -0.059509 | 122.2504 | -0.075912 | 0.0066372 | -0.014046 | 0.0097668 | 0.043919 | -0.012031 | 0.063698 | 0.059509 | 122.3373 | -0.16479 | 0.15564 | 121.637 | 9.5489 | 0.9201 | 1.2543 | 122.4335 | -0.23804 | -0.10529 | 0.086975 | 0.11902 | 0.21515 | -0.6134 | -0.17853 | 0.18311 | 0.2243 | 0.97961 | 1.3138 | 121.6965 | 122.3969 | 0.11902 | 122.493 | 9.6085 | -0.17853 | 122.3969 | 0.11902 | 9.6085 | 121.6965 | 122.493 | -122.4152 | -122.4884
4187.3281 | 122.3282 | -0.10071 | 122.2824 | -0.091171 | 0.0089872 | -0.014259 | 0.016603 | 0.046696 | -0.012886 | 0.066689 | 0.027466 | 122.3282 | -0.21973 | 0.1236 | 121.55 | 9.5215 | 0.95673 | 1.1261 | 122.5113 | -0.23346 | -0.11902 | 0.045776 | 0.12817 | 0.2243 | -0.73242 | -0.13275 | 0.22888 | 0.24719 | 1.0574 | 1.2268 | 121.6507 | 122.4289 | 0.12817 | 122.612 | 9.6222 | -0.13275 | 122.4289 | 0.12817 | 9.6222 | 121.6507 | 122.612 | -122.5021 | -122.5159
4189.0781 | 122.4564 | -0.050354 | 122.2046 | 0.10719 | 0.0094144 | -0.012337 | 0.015321 | 0.049473 | -0.013527 | 0.066048 | -0.036621 | 122.3465 | -0.22888 | 0.041199 | 121.5042 | 9.3796 | 0.83313 | 0.89722 | 122.4792 | -0.23346 | -0.17853 | 0.14191 | 0.013733 | 0.091553 | -0.70038 | -0.1831 | 0.27466 | 0.19226 | 0.88348 | 0.94757 | 121.5546 | 122.3969 | 0.013733 | 122.5296 | 9.4299 | -0.1831 | 122.3969 | 0.013733 | 9.4299 | 121.5546 | 122.5296 | -122.4335 | -122.438
4190.7969 | 122.4152 | -0.064087 | 122.2549 | -0.11406 | 0.0070646 | -0.020882 | 0.0093396 | 0.044987 | -0.01075 | 0.066048 | 0.045776 | 122.3328 | -0.16479 | 0.16022 | 121.6232 | 9.6176 | 0.93842 | 1.2909 | 122.4289 | -0.21057 | -0.10071 | 0.07782 | 0.10986 | 0.2243 | -0.63171 | -0.14648 | 0.17395 | 0.21057 | 1.0025 | 1.355 | 121.6873 | 122.3969 | 0.10986 | 122.493 | 9.6817 | -0.14648 | 122.3969 | 0.10986 | 9.6817 | 121.6873 | 122.493 | -122.4197 | -122.4655
4192.5469 | 122.4609 | -0.045776 | 122.2229 | 0.11482 | 0.0098416 | -0.01255 | 0.016816 | 0.050328 | -0.012672 | 0.06498 | -0.036621 | 122.3648 | -0.21515 | 0.032043 | 121.5134 | 9.4116 | 0.82855 | 0.89722 | 122.5113 | -0.24261 | -0.16937 | 0.14191 | 0.009155 | 0.077819 | -0.70953 | -0.19684 | 0.28839 | 0.17853 | 0.87433 | 0.94299 | 121.5591 | 122.4106 | 0.009155 | 122.5571 | 9.4574 | -0.19684 | 122.4106 | 0.009155 | 9.4574 | 121.5591 | 122.5571 | -122.438 | -122.4655
4194.25 | 122.3511 | -0.11444 | 122.287 | -0.20561 | 0.0077054 | -0.010628 | 0.011049 | 0.047123 | -0.011818 | 0.066475 | 0.064087 | 122.3145 | -0.16479 | 0.17395 | 121.6141 | 9.6817 | 1.03 | 1.3596 | 122.4197 | -0.21973 | -0.050354 | 0.027466 | 0.17853 | 0.28839 | -0.67291 | -0.10529 | 0.13275 | 0.22888 | 1.1444 | 1.474 | 121.7285 | 122.4289 | 0.17853 | 122.5342 | 9.7961 | -0.10529 | 122.4289 | 0.17853 | 9.7961 | 121.7285 | 122.5342 | -122.4518 | -122.5067
4195.9375 | 122.4335 | -0.050354 | 122.2549 | 0.17586 | 0.007919 | -0.011909 | 0.013826 | 0.048619 | -0.014808 | 0.066902 | 0.036621 | 122.319 | -0.16479 | 0.13733 | 121.5683 | 9.5352 | 0.67291 | 0.98877 | 122.4609 | -0.21973 | -0.11444 | 0.064087 | 0.086975 | 0.18768 | -0.68665 | -0.16937 | 0.20599 | 0.20142 | 0.72327 | 1.0391 | 121.6187 | 122.3694 | 0.086975 | 122.5113 | 9.5856 | -0.16937 | 122.3694 | 0.086975 | 9.5856 | 121.6187 | 122.5113 | -122.4197 | -122.4747
4197.6562 | 122.374 | -0.082397 | 122.2549 | -0.19035 | 0.0074918 | -0.011482 | 0.014894 | 0.046696 | -0.014808 | 0.065621 | -0.027466 | 122.3282 | -0.21973 | 0.064087 | 121.5179 | 9.6085 | 1.1536 | 1.2131 | 122.4976 | -0.26093 | -0.13733 | 0.073242 | 0.054931 | 0.14648 | -0.737 | -0.17853 | 0.24262 | 0.19226 | 1.236 | 1.2955 | 121.6003 | 122.4106 | 0.054931 | 122.58 | 9.6909 | -0.17853 | 122.4106 | 0.054931 | 9.6909 | 121.6003 | 122.58 | -122.4747 | -122.5159
4199.3594 | 122.4747 | -0.054932 | 122.2275 | -0.014877 | 0.0070646 | -0.012764 | 0.0078442 | 0.048832 | -0.010963 | 0.064339 | 0.004578 | 122.3419 | -0.1831 | 0.10529 | 121.5866 | 9.5993 | 0.91095 | 1.1581 | 122.4426 | -0.21973 | -0.12817 | 0.11444 | 0.05951 | 0.16022 | -0.64087 | -0.16479 | 0.21515 | 0.18768 | 0.96588 | 1.2131 | 121.6415 | 122.3969 | 0.05951 | 122.4976 | 9.6542 | -0.16479 | 122.3969 | 0.05951 | 9.6542 | 121.6415 | 122.4976 | -122.4106 | -122.4472
4201.0781 | 122.4243 | -0.050354 | 122.2412 | 0.19112 | 0.0083462 | -0.011909 | 0.015107 | 0.050114 | -0.015876 | 0.065407 | 0.018311 | 122.3328 | -0.20599 | 0.11444 | 121.5546 | 9.5535 | 0.70953 | 0.99335 | 122.4838 | -0.21973 | -0.15564 | 0.091553 | 0.068665 | 0.16479 | -0.68665 | -0.16937 | 0.24261 | 0.22431 | 0.75989 | 1.0437 | 121.6049 | 122.3831 | 0.068665 | 122.5342 | 9.6039 | -0.16937 | 122.3831 | 0.068665 | 9.6039 | 121.6049 | 122.5342 | -122.4472 | -122.4609
4202.7812 | 122.3969 | -0.091553 | 122.2549 | -0.2285 | 0.0092008 | -0.015755 | 0.011476 | 0.046696 | -0.012031 | 0.067116 | 0 | 122.3373 | -0.20599 | 0.091553 | 121.5271 | 9.6725 | 1.2039 | 1.2634 | 122.4564 | -0.24719 | -0.11444 | 0.082397 | 0.091553 | 0.18311 | -0.72784 | -0.15564 | 0.20142 | 0.20599 | 1.2955 | 1.355 | 121.6187 | 122.4289 | 0.091553 | 122.5479 | 9.7641 | -0.15564 | 122.4289 | 0.091553 | 9.7641 | 121.6187 | 122.5479 | -122.4609 | -122.5021
4204.4688 | 122.4243 | -0.059509 | 122.2641 | 0.17586 | 0.0081326 | -0.0099869 | 0.012971 | 0.04755 | -0.013313 | 0.066048 | 0.086975 | 122.2824 | -0.16937 | 0.16937 | 121.6003 | 9.613 | 0.66834 | 1.0666 | 122.4335 | -0.20599 | -0.10986 | 0.018311 | 0.14648 | 0.22888 | -0.66376 | -0.14649 | 0.16937 | 0.25635 | 0.72784 | 1.1261 | 121.6599 | 122.3419 | 0.14648 | 122.493 | 9.6725 | -0.14649 | 122.3419 | 0.14648 | 9.6725 | 121.6599 | 122.493 | -122.4335 | -122.4701
4206.1875 | 122.3465 | -0.10986 | 122.2961 | -0.14458 | 0.0049282 | -0.015114 | 0.011049 | 0.046055 | -0.01374 | 0.065621 | 0.032043 | 122.3007 | -0.16479 | 0.16937 | 121.6141 | 9.7824 | 1.0757 | 1.3641 | 122.4655 | -0.2243 | -0.054932 | 0.004577 | 0.14191 | 0.27924 | -0.68207 | -0.11444 | 0.16937 | 0.19684 | 1.1856 | 1.474 | 121.7239 | 122.4106 | 0.14191 | 122.5754 | 9.8923 | -0.11444 | 122.4106 | 0.14191 | 9.8923 | 121.7239 | 122.5754 | -122.4609 | -122.5204
4207.8906 | 122.4518 | -0.050354 | 122.2229 | 0.11482 | 0.009628 | -0.0102 | 0.016603 | 0.04691 | -0.012458 | 0.064125 | -0.018311 | 122.3236 | -0.20599 | 0.064087 | 121.5179 | 9.5627 | 0.76904 | 0.93384 | 122.4884 | -0.22888 | -0.15564 | 0.10071 | 0.032043 | 0.11444 | -0.70496 | -0.17853 | 0.2655 | 0.18768 | 0.8194 | 0.98419 | 121.5683 | 122.374 | 0.032043 | 122.5388 | 9.613 | -0.17853 | 122.374 | 0.032043 | 9.613 | 121.5683 | 122.5388 | -122.4289 | -122.4518
4209.6406 | 122.3465 | -0.10529 | 122.3053 | -0.20561 | 0.0066372 | -0.016182 | 0.0093396 | 0.047978 | -0.013527 | 0.065621 | 0.059509 | 122.3145 | -0.16937 | 0.16937 | 121.6095 | 9.8099 | 1.0574 | 1.3733 | 122.4564 | -0.21515 | -0.064087 | 0.009155 | 0.16479 | 0.27466 | -0.6958 | -0.10986 | 0.15106 | 0.22888 | 1.1627 | 1.4786 | 121.7148 | 122.4197 | 0.16479 | 122.5616 | 9.9152 | -0.10986 | 122.4197 | 0.16479 | 9.9152 | 121.7148 | 122.5616 | -122.4747 | -122.5204
4211.3438 | 122.3373 | -0.091553 | 122.2595 | -0.13695 | 0.0087734 | -0.016182 | 0.015962 | 0.047123 | -0.015449 | 0.065193 | 0.004578 | 122.3007 | -0.20599 | 0.10986 | 121.5454 | 9.7504 | 1.0941 | 1.2222 | 122.4976 | -0.23346 | -0.11444 | 0.041199 | 0.096131 | 0.20142 | -0.71411 | -0.14191 | 0.23804 | 0.21057 | 1.1856 | 1.3138 | 121.637 | 122.3923 | 0.096131 | 122.5891 | 9.8419 | -0.14191 | 122.3923 | 0.096131 | 9.8419 | 121.637 | 122.5891 | -122.4655 | -122.493
4213.0469 | 122.3419 | -0.086975 | 122.3053 | -0.12932 | 0.009628 | -0.015755 | 0.0086988 | 0.047764 | -0.011818 | 0.066262 | 0.086975 | 122.3145 | -0.16022 | 0.17395 | 121.6599 | 9.8373 | 0.98419 | 1.3687 | 122.4335 | -0.23346 | -0.073242 | 0.009155 | 0.17395 | 0.26092 | -0.64545 | -0.14648 | 0.12817 | 0.24719 | 1.0712 | 1.4557 | 121.7468 | 122.4014 | 0.17395 | 122.5204 | 9.9243 | -0.14648 | 122.4014 | 0.17395 | 9.9243 | 121.7468 | 122.5204 | -122.4655 | -122.5388
4214.7344 | 122.4335 | -0.054932 | 122.2412 | 0.19112 | 0.0087734 | -0.014687 | 0.015535 | 0.050541 | -0.015663 | 0.066262 | 0.027466 | 122.3236 | -0.19226 | 0.11902 | 121.5591 | 9.6588 | 0.737 | 0.98419 | 122.4792 | -0.21973 | -0.13733 | 0.082397 | 0.082398 | 0.17395 | -0.68207 | -0.16479 | 0.23804 | 0.21973 | 0.79193 | 1.0391 | 121.6141 | 122.3785 | 0.082398 | 122.5342 | 9.7137 | -0.16479 | 122.3785 | 0.082398 | 9.7137 | 121.6141 | 122.5342 | -122.4335 | -122.4609
4216.4375 | 122.3465 | -0.09613 | 122.2778 | -0.15984 | 0.0083462 | -0.014046 | 0.0089124 | 0.045628 | -0.01374 | 0.065834 | 0.064087 | 122.2778 | -0.17853 | 0.1831 | 121.637 | 9.8785 | 1.0529 | 1.3824 | 122.4197 | -0.22888 | -0.082398 | 0 | 0.16022 | 0.27924 | -0.64087 | -0.13275 | 0.14191 | 0.24261 | 1.149 | 1.4786 | 121.7331 | 122.374 | 0.16022 | 122.5159 | 9.9747 | -0.13275 | 122.374 | 0.16022 | 9.9747 | 121.7331 | 122.5159 | -122.4564 | -122.5067
4218.1406 | 122.4243 | -0.050354 | 122.2412 | 0.1606 | 0.0083462 | -0.012337 | 0.013826 | 0.047978 | -0.012672 | 0.065193 | 0.059509 | 122.2961 | -0.1831 | 0.13733 | 121.582 | 9.7412 | 0.71411 | 1.0391 | 122.4335 | -0.21057 | -0.13275 | 0.054932 | 0.10986 | 0.18768 | -0.65918 | -0.16022 | 0.19226 | 0.24261 | 0.76447 | 1.0895 | 121.6324 | 122.3465 | 0.10986 | 122.4838 | 9.7916 | -0.16022 | 122.3465 | 0.10986 | 9.7916 | 121.6324 | 122.4838 | -122.4243 | -122.4518
4219.8281 | 122.3602 | -0.10986 | 122.287 | -0.19035 | 0.0094144 | -0.013618 | 0.017244 | 0.045628 | -0.012672 | 0.06498 | -0.027466 | 122.3419 | -0.21515 | 0.07782 | 121.5317 | 9.819 | 1.1765 | 1.2543 | 122.4655 | -0.25635 | -0.10529 | 0.054932 | 0.082397 | 0.18768 | -0.75531 | -0.14649 | 0.17853 | 0.18768 | 1.2863 | 1.3641 | 121.6415 | 122.4518 | 0.082397 | 122.5754 | 9.9289 | -0.14649 | 122.4518 | 0.082397 | 9.9289 | 121.6415 | 122.5754 | -122.5021 | -122.5433
4221.5781 | 122.3465 | -0.10071 | 122.2641 | -0.19798 | 0.010055 | -0.01725 | 0.0095532 | 0.046482 | -0.013313 | 0.064125 | 0.073242 | 122.2916 | -0.17395 | 0.17853 | 121.6187 | 9.9106 | 1.0757 | 1.3824 | 122.4609 | -0.2243 | -0.073242 | 0.027466 | 0.17395 | 0.27924 | -0.64545 | -0.1236 | 0.19684 | 0.24719 | 1.1765 | 1.4832 | 121.7194 | 122.3923 | 0.17395 | 122.5616 | 10.0113 | -0.1236 | 122.3923 | 0.17395 | 10.0113 | 121.7194 | 122.5616 | -122.438 | -122.4884
4223.2812 | 122.3602 | -0.082397 | 122.2595 | 0.13008 | 0.010055 | -0.014687 | 0.018525 | 0.049687 | -0.015663 | 0.065193 | -0.004578 | 122.3236 | -0.20599 | 0.068665 | 121.4859 | 9.7412 | 0.9613 | 1.0162 | 122.5113 | -0.24261 | -0.1236 | 0.064087 | 0.077819 | 0.15106 | -0.77362 | -0.16022 | 0.25177 | 0.20142 | 1.0437 | 1.0986 | 121.5683 | 122.406 | 0.077819 | 122.5937 | 9.8236 | -0.16022 | 122.406 | 0.077819 | 9.8236 | 121.5683 | 122.5937 | -122.4655 | -122.5021
4224.9844 | 122.4518 | -0.059509 | 122.2687 | -0.014877 | 0.009628 | -0.017677 | 0.0069898 | 0.045414 | -0.011818 | 0.066689 | 0.009155 | 122.3511 | -0.16022 | 0.10529 | 121.582 | 9.8328 | 0.96588 | 1.2177 | 122.4655 | -0.22888 | -0.10071 | 0.082397 | 0.068664 | 0.16479 | -0.68665 | -0.16937 | 0.19684 | 0.16937 | 1.0254 | 1.2772 | 121.6415 | 122.4106 | 0.068664 | 122.525 | 9.8923 | -0.16937 | 122.4106 | 0.068664 | 9.8923 | 121.6415 | 122.525 | -122.4289 | -122.4976
4226.6875 | 122.4152 | -0.050354 | 122.2733 | 0.16823 | 0.0092008 | -0.013618 | 0.014039 | 0.049259 | -0.014808 | 0.064339 | 0.086975 | 122.319 | -0.15106 | 0.16479 | 121.6049 | 9.8282 | 0.69122 | 1.0849 | 122.4472 | -0.20599 | -0.10071 | 0.045777 | 0.13733 | 0.21515 | -0.66833 | -0.15564 | 0.17395 | 0.23804 | 0.74158 | 1.1353 | 121.6553 | 122.3694 | 0.13733 | 122.4976 | 9.8785 | -0.15564 | 122.3694 | 0.13733 | 9.8785 | 121.6553 | 122.4976 | -122.4243 | -122.4792
4228.3906 | 122.3831 | -0.082397 | 122.2412 | -0.26665 | 0.0092008 | -0.011696 | 0.013398 | 0.044987 | -0.012886 | 0.064766 | -0.045776 | 122.3282 | -0.21515 | 0.059509 | 121.5088 | 9.8602 | 1.268 | 1.2817 | 122.5113 | -0.27466 | -0.13275 | 0.086975 | 0.036621 | 0.14191 | -0.73242 | -0.19226 | 0.27008 | 0.16937 | 1.3504 | 1.3641 | 121.5912 | 122.4106 | 0.036621 | 122.5937 | 9.9426 | -0.19226 | 122.4106 | 0.036621 | 9.9426 | 121.5912 | 122.5937 | -122.4564 | -122.5159
4230.0938 | 122.4197 | -0.059509 | 122.2321 | 0.10719 | 0.0074918 | -0.014687 | 0.012117 | 0.04691 | -0.013313 | 0.066902 | 0.07782 | 122.2961 | -0.16937 | 0.15564 | 121.5912 | 9.8373 | 0.75073 | 1.0986 | 122.4472 | -0.20599 | -0.10986 | 0.064087 | 0.13733 | 0.21515 | -0.64087 | -0.14649 | 0.21515 | 0.24719 | 0.81024 | 1.1581 | 121.6507 | 122.3557 | 0.13733 | 122.5067 | 9.8969 | -0.14649 | 122.3557 | 0.13733 | 9.8969 | 121.6507 | 122.5067 | -122.4014 | -122.4381
4231.7969 | 122.3282 | -0.09613 | 122.2916 | -0.14458 | 0.0064236 | -0.016396 | 0.01468 | 0.047123 | -0.013099 | 0.066048 | 0.022888 | 122.3099 | -0.21057 | 0.10529 | 121.5408 | 9.9197 | 1.1124 | 1.2451 | 122.4609 | -0.23804 | -0.11444 | 0.01831 | 0.11902 | 0.20142 | -0.75073 | -0.14191 | 0.16937 | 0.23346 | 1.2085 | 1.3412 | 121.637 | 122.406 | 0.11902 | 122.5571 | 10.0159 | -0.14191 | 122.406 | 0.11902 | 10.0159 | 121.637 | 122.5571 | -122.5021 | -122.5296
4233.5 | 122.4564 | -0.041199 | 122.2275 | 0.099564 | 0.009628 | -0.016396 | 0.017457 | 0.048619 | -0.01374 | 0.066689 | -0.004578 | 122.3419 | -0.20599 | 0.054932 | 121.4951 | 9.7641 | 0.87433 | 0.97961 | 122.4792 | -0.24719 | -0.1648 | 0.11444 | 0.036621 | 0.096131 | -0.73242 | -0.20599 | 0.25177 | 0.20142 | 0.91553 | 1.0208 | 121.5363 | 122.3831 | 0.036621 | 122.5204 | 9.8053 | -0.20599 | 122.3831 | 0.036621 | 9.8053 | 121.5363 | 122.5204 | -122.4335 | -122.4747
4235.2188 | 122.4289 | -0.036621 | 122.2137 | 0.1606 | 0.0081326 | -0.011696 | 0.012544 | 0.048191 | -0.015236 | 0.06733 | 0.036621 | 122.319 | -0.20142 | 0.10071 | 121.5546 | 9.8282 | 0.77362 | 1.0254 | 122.4655 | -0.23346 | -0.1648 | 0.10529 | 0.073242 | 0.13733 | -0.65918 | -0.19684 | 0.25177 | 0.23804 | 0.81024 | 1.062 | 121.5912 | 122.3557 | 0.073242 | 122.5021 | 9.8648 | -0.19684 | 122.3557 | 0.073242 | 9.8648 | 121.5912 | 122.5021 | -122.4152 | -122.4472
4236.9219 | 122.3419 | -0.12817 | 122.2778 | -0.19035 | 0.0053556 | -0.014259 | 0.0086988 | 0.047123 | -0.010963 | 0.065407 | 0.054932 | 122.3007 | -0.17395 | 0.17395 | 121.6187 | 10.0479 | 1.1124 | 1.4282 | 122.4335 | -0.21515 | -0.045776 | 0.022888 | 0.18311 | 0.30212 | -0.65918 | -0.086975 | 0.15564 | 0.22888 | 1.2405 | 1.5564 | 121.7468 | 122.4289 | 0.18311 | 122.5616 | 10.1761 | -0.086975 | 122.4289 | 0.18311 | 10.1761 | 121.7468 | 122.5616 | -122.4518 | -122.493
4238.625 | 122.4426 | -0.045776 | 122.2183 | 0.15297 | 0.0098416 | -0.010414 | 0.016389 | 0.050328 | -0.016517 | 0.064766 | 0.004578 | 122.3328 | -0.18768 | 0.086975 | 121.5317 | 9.8328 | 0.81024 | 0.99335 | 122.493 | -0.21057 | -0.14191 | 0.11444 | 0.050354 | 0.13275 | -0.68665 | -0.1648 | 0.27466 | 0.19226 | 0.85602 | 1.0391 | 121.5775 | 122.3785 | 0.050354 | 122.5388 | 9.8785 | -0.1648 | 122.3785 | 0.050354 | 9.8785 | 121.5775 | 122.5388 | -122.406 | -122.4289
4240.3438 | 122.3419 | -0.11444 | 122.2778 | -0.19035 | 0.010055 | -0.016609 | 0.008485 | 0.045201 | -0.012245 | 0.066475 | 0.09613 | 122.3053 | -0.17853 | 0.16022 | 121.6415 | 10.0662 | 1.0666 | 1.4191 | 122.406 | -0.19684 | -0.064087 | 0.027466 | 0.21057 | 0.27466 | -0.63629 | -0.082397 | 0.12817 | 0.27466 | 1.181 | 1.5335 | 121.756 | 122.4197 | 0.21057 | 122.5204 | 10.1807 | -0.082397 | 122.4197 | 0.21057 | 10.1807 | 121.756 | 122.5204 | -122.4564 | -122.4747
4242.0469 | 122.3831 | -0.10529 | 122.2778 | -0.27428 | 0.0077054 | -0.016396 | 0.013612 | 0.045841 | -0.012458 | 0.067116 | -0.032043 | 122.3602 | -0.21515 | 0.068665 | 121.5134 | 9.9838 | 1.2772 | 1.3184 | 122.4976 | -0.27008 | -0.10986 | 0.082397 | 0.073243 | 0.17395 | -0.76447 | -0.1648 | 0.21973 | 0.18311 | 1.3824 | 1.4236 | 121.6187 | 122.4655 | 0.073243 | 122.6028 | 10.0891 | -0.1648 | 122.4655 | 0.073243 | 10.0891 | 121.6187 | 122.6028 | -122.493 | -122.5479
4243.7656 | 122.3923 | -0.082397 | 122.2641 | -0.14458 | 0.0074918 | -0.015327 | 0.011262 | 0.04755 | -0.011818 | 0.065407 | 0.07782 | 122.3145 | -0.16937 | 0.16479 | 121.6324 | 10.0754 | 1.0345 | 1.3962 | 122.4518 | -0.20599 | -0.086976 | 0.050354 | 0.16022 | 0.24719 | -0.63171 | -0.1236 | 0.18768 | 0.24719 | 1.1169 | 1.4786 | 121.7148 | 122.3969 | 0.16022 | 122.5342 | 10.1578 | -0.1236 | 122.3969 | 0.16022 | 10.1578 | 121.7148 | 122.5342 | -122.4335 | -122.4701
4245.4531 | 122.3557 | -0.10986 | 122.2916 | -0.068283 | 0.0098416 | -0.012978 | 0.017671 | 0.049687 | -0.014167 | 0.066475 | 0.032043 | 122.3236 | -0.21973 | 0.10071 | 121.5408 | 9.9792 | 1.03 | 1.1536 | 122.4701 | -0.23346 | -0.10986 | 0.032043 | 0.14191 | 0.21057 | -0.75073 | -0.1236 | 0.17853 | 0.25177 | 1.1398 | 1.2634 | 121.6507 | 122.4335 | 0.14191 | 122.58 | 10.0891 | -0.1236 | 122.4335 | 0.14191 | 10.0891 | 121.6507 | 122.58 | -122.5113 | -122.525
4247.1562 | 122.374 | -0.086975 | 122.2733 | -0.15221 | 0.0070646 | -0.018745 | 0.008485 | 0.044132 | -0.013527 | 0.064339 | 0.082397 | 122.319 | -0.17395 | 0.17853 | 121.637 | 10.1074 | 1.0208 | 1.3962 | 122.4289 | -0.21057 | -0.086975 | 0.045777 | 0.16937 | 0.2655 | -0.63629 | -0.1236 | 0.15564 | 0.25635 | 1.1078 | 1.4832 | 121.7239 | 122.406 | 0.16937 | 122.5159 | 10.1944 | -0.1236 | 122.406 | 0.16937 | 10.1944 | 121.7239 | 122.5159 | -122.4472 | -122.4838
4248.875 | 122.4243 | -0.068665 | 122.2504 | 0.14534 | 0.0085598 | -0.0095597 | 0.01233 | 0.045841 | -0.012458 | 0.067543 | 0.07782 | 122.2961 | -0.1831 | 0.15564 | 121.5912 | 9.9976 | 0.7782 | 1.1444 | 122.4564 | -0.20599 | -0.11444 | 0.045777 | 0.14649 | 0.22431 | -0.65918 | -0.13733 | 0.20599 | 0.26092 | 0.84686 | 1.2131 | 121.6599 | 122.3648 | 0.14649 | 122.525 | 10.0662 | -0.13733 | 122.3648 | 0.14649 | 10.0662 | 121.6599 | 122.525 | -122.4335 | -122.4564
4250.625 | 122.4747 | -0.059509 | 122.1909 | 0.01564 | 0.0074918 | -0.014687 | 0.0097668 | 0.047337 | -0.011818 | 0.065834 | 0.022888 | 122.3236 | -0.1831 | 0.11444 | 121.5637 | 10.0067 | 0.94299 | 1.1765 | 122.438 | -0.23804 | -0.1236 | 0.13275 | 0.082397 | 0.17395 | -0.62714 | -0.17853 | 0.24719 | 0.20599 | 1.0025 | 1.236 | 121.6232 | 122.3831 | 0.082397 | 122.4976 | 10.0662 | -0.17853 | 122.3831 | 0.082397 | 10.0662 | 121.6232 | 122.4976 | -122.374 | -122.4289
4252.3281 | 122.3694 | -0.086975 | 122.2641 | -0.25139 | 0.0087734 | -0.014046 | 0.012758 | 0.043278 | -0.014808 | 0.067757 | 0.041199 | 122.3007 | -0.19226 | 0.11902 | 121.5683 | 10.1074 | 1.2451 | 1.387 | 122.4609 | -0.24719 | -0.10529 | 0.036621 | 0.12817 | 0.20599 | -0.6958 | -0.16022 | 0.19684 | 0.23346 | 1.3321 | 1.474 | 121.6553 | 122.3877 | 0.12817 | 122.5479 | 10.1944 | -0.16022 | 122.3877 | 0.12817 | 10.1944 | 121.6553 | 122.5479 | -122.4564 | -122.5113
4254.0312 | 122.4152 | -0.059509 | 122.2412 | 0.11482 | 0.0077054 | -0.013832 | 0.012758 | 0.04755 | -0.014595 | 0.063057 | 0.086975 | 122.2824 | -0.16937 | 0.16022 | 121.5775 | 10.0204 | 0.77362 | 1.1307 | 122.4335 | -0.20142 | -0.10986 | 0.041199 | 0.14648 | 0.21973 | -0.66376 | -0.14191 | 0.19226 | 0.25635 | 0.83313 | 1.1902 | 121.637 | 122.3419 | 0.14648 | 122.493 | 10.08 | -0.14191 | 122.3419 | 0.14648 | 10.08 | 121.637 | 122.493 | -122.4106 | -122.4426
4255.7188 | 122.3282 | -0.11902 | 122.2961 | -0.098801 | 0.0087734 | -0.012764 | 0.017244 | 0.046482 | -0.014808 | 0.066048 | 0.045776 | 122.3236 | -0.21057 | 0.13733 | 121.5179 | 10.0983 | 1.062 | 1.2177 | 122.4701 | -0.22888 | -0.091552 | 0.027465 | 0.16479 | 0.25635 | -0.7782 | -0.10986 | 0.17395 | 0.25635 | 1.181 | 1.3367 | 121.637 | 122.4426 | 0.16479 | 122.5891 | 10.2173 | -0.10986 | 122.4426 | 0.16479 | 10.2173 | 121.637 | 122.5891 | -122.5067 | -122.525
4257.4531 | 122.3557 | -0.10529 | 122.2504 | -0.21324 | 0.0089872 | -0.015968 | 0.0093396 | 0.046696 | -0.011818 | 0.064553 | 0.073242 | 122.3236 | -0.16937 | 0.14191 | 121.5912 | 10.1944 | 1.2314 | 1.4328 | 122.4472 | -0.23346 | -0.064087 | 0.073242 | 0.17853 | 0.24719 | -0.65918 | -0.12817 | 0.19684 | 0.24261 | 1.3367 | 1.5381 | 121.6965 | 122.4289 | 0.17853 | 122.5525 | 10.2997 | -0.12817 | 122.4289 | 0.17853 | 10.2997 | 121.6965 | 122.5525 | -122.4197 | -122.4838
4259.1406 | 122.4152 | -0.073242 | 122.2458 | 0.13771 | 0.0081326 | -0.0149 | 0.01233 | 0.049046 | -0.014595 | 0.064339 | 0.07782 | 122.2961 | -0.15564 | 0.15564 | 121.6003 | 10.0891 | 0.79651 | 1.1536 | 122.4426 | -0.18768 | -0.082398 | 0.050354 | 0.15106 | 0.22888 | -0.64545 | -0.11444 | 0.19684 | 0.23346 | 0.86975 | 1.2268 | 121.6736 | 122.3694 | 0.15106 | 122.5159 | 10.1624 | -0.11444 | 122.3694 | 0.15106 | 10.1624 | 121.6736 | 122.5159 | -122.4014 | -122.4335
4260.8594 | 122.4106 | -0.064087 | 122.2458 | 0.12245 | 0.0081326 | -0.011055 | 0.014253 | 0.050968 | -0.015236 | 0.064553 | 0.086975 | 122.2824 | -0.17853 | 0.16022 | 121.6003 | 10.1166 | 0.75073 | 1.1261 | 122.4426 | -0.19684 | -0.11444 | 0.036621 | 0.15106 | 0.2243 | -0.64545 | -0.13275 | 0.19684 | 0.2655 | 0.81482 | 1.1902 | 121.6644 | 122.3465 | 0.15106 | 122.5067 | 10.1807 | -0.13275 | 122.3465 | 0.15106 | 10.1807 | 121.6644 | 122.5067 | -122.4243 | -122.4426
4262.6094 | 122.4655 | -0.041199 | 122.2321 | 0.046158 | 0.0083462 | -0.016609 | 0.0080578 | 0.04755 | -0.013099 | 0.065407 | 0.036621 | 122.3373 | -0.1831 | 0.10986 | 121.5546 | 10.0983 | 0.94299 | 1.181 | 122.438 | -0.22888 | -0.14191 | 0.10528 | 0.07782 | 0.15106 | -0.67749 | -0.18768 | 0.20599 | 0.21973 | 0.98419 | 1.2222 | 121.5958 | 122.3785 | 0.07782 | 122.4792 | 10.1395 | -0.18768 | 122.3785 | 0.07782 | 10.1395 | 121.5958 | 122.4792 | -122.4152 | -122.4609
4264.2969 | 122.374 | -0.10071 | 122.2687 | -0.2285 | 0.010055 | -0.0097733 | 0.013398 | 0.045414 | -0.011604 | 0.064339 | -0.009155 | 122.3419 | -0.20599 | 0.082397 | 121.5042 | 10.1944 | 1.3 | 1.3687 | 122.4747 | -0.2655 | -0.10529 | 0.073242 | 0.091553 | 0.18311 | -0.76447 | -0.16479 | 0.20599 | 0.19684 | 1.4008 | 1.4694 | 121.6049 | 122.4426 | 0.091553 | 122.5754 | 10.2951 | -0.16479 | 122.4426 | 0.091553 | 10.2951 | 121.6049 | 122.5754 | -122.4747 | -122.5342
4266 | 122.4609 | -0.050354 | 122.2229 | 0.10719 | 0.0087734 | -0.0102 | 0.01703 | 0.048619 | -0.012245 | 0.065621 | -0.004578 | 122.3236 | -0.20142 | 0.050354 | 121.4905 | 10.0388 | 0.94299 | 1.0208 | 122.4884 | -0.25177 | -0.15106 | 0.10071 | 0.045776 | 0.10071 | -0.73242 | -0.20142 | 0.2655 | 0.19684 | 0.99335 | 1.0712 | 121.5408 | 122.374 | 0.045776 | 122.5388 | 10.0891 | -0.20142 | 122.374 | 0.045776 | 10.0891 | 121.5408 | 122.5388 | -122.4243 | -122.4747
4267.7031 | 122.3877 | -0.10071 | 122.2687 | -0.23613 | 0.0098416 | -0.015541 | 0.01233 | 0.046696 | -0.013099 | 0.064766 | 0.009155 | 122.3877 | -0.20599 | 0.07782 | 121.5179 | 10.2173 | 1.3092 | 1.3779 | 122.4655 | -0.25177 | -0.10529 | 0.11902 | 0.10986 | 0.17853 | -0.75073 | -0.15106 | 0.19684 | 0.21515 | 1.4099 | 1.4786 | 121.6187 | 122.4884 | 0.10986 | 122.5662 | 10.318 | -0.15106 | 122.4884 | 0.10986 | 10.318 | 121.6187 | 122.5662 | -122.4747 | -122.5204
4269.3906 | 122.4472 | -0.059509 | 122.2504 | 0.13771 | 0.0098416 | -0.013405 | 0.016389 | 0.04755 | -0.014595 | 0.066475 | 0.009155 | 122.3282 | -0.20599 | 0.082397 | 121.5134 | 10.0754 | 0.86517 | 1.0437 | 122.4792 | -0.23804 | -0.14649 | 0.07782 | 0.068664 | 0.14191 | -0.737 | -0.17853 | 0.22888 | 0.21515 | 0.92468 | 1.1032 | 121.5729 | 122.3877 | 0.068664 | 122.5388 | 10.1349 | -0.17853 | 122.3877 | 0.068664 | 10.1349 | 121.5729 | 122.5388 | -122.4564 | -122.4884
4271.0938 | 122.3831 | -0.082397 | 122.2504 | -0.26665 | 0.0083462 | -0.019386 | 0.010408 | 0.047764 | -0.012886 | 0.066262 | -0.036621 | 122.3328 | -0.22888 | 0.050354 | 121.5042 | 10.2127 | 1.3412 | 1.3412 | 122.4701 | -0.24719 | -0.14649 | 0.082398 | 0.045776 | 0.13275 | -0.74616 | -0.16479 | 0.21973 | 0.19226 | 1.4236 | 1.4236 | 121.5866 | 122.4152 | 0.045776 | 122.5525 | 10.2951 | -0.16479 | 122.4152 | 0.045776 | 10.2951 | 121.5866 | 122.5525 | -122.4792 | -122.4976
4272.7969 | 122.4747 | -0.054932 | 122.2137 | 0.01564 | 0.0083462 | -0.014687 | 0.0086988 | 0.047978 | -0.012031 | 0.063484 | 0.022888 | 122.3145 | -0.18768 | 0.10529 | 121.5775 | 10.1898 | 1.0071 | 1.2405 | 122.4518 | -0.21057 | -0.13275 | 0.10071 | 0.07782 | 0.16022 | -0.63629 | -0.15564 | 0.23804 | 0.21057 | 1.062 | 1.2955 | 121.6324 | 122.3694 | 0.07782 | 122.5067 | 10.2448 | -0.15564 | 122.3694 | 0.07782 | 10.2448 | 121.6324 | 122.5067 | -122.4014 | -122.4243
4274.5312 | 122.3923 | -0.086975 | 122.2778 | -0.23613 | 0.010055 | -0.010628 | 0.013398 | 0.044987 | -0.011818 | 0.06797 | -0.013733 | 122.3602 | -0.21515 | 0.050354 | 121.4951 | 10.2493 | 1.3504 | 1.355 | 122.4792 | -0.25635 | -0.12817 | 0.082397 | 0.073242 | 0.13733 | -0.78278 | -0.16937 | 0.20142 | 0.20142 | 1.4374 | 1.442 | 121.582 | 122.4472 | 0.073242 | 122.5662 | 10.3363 | -0.16937 | 122.4472 | 0.073242 | 10.3363 | 121.582 | 122.5662 | -122.493 | -122.5342
4276.2344 | 122.4106 | -0.07782 | 122.2229 | 0.13771 | 0.010696 | -0.01255 | 0.014253 | 0.049046 | -0.013313 | 0.067116 | 0.091553 | 122.3373 | -0.16937 | 0.16022 | 121.6003 | 10.2081 | 0.80109 | 1.1398 | 122.4564 | -0.21973 | -0.091553 | 0.11444 | 0.16937 | 0.23804 | -0.62256 | -0.14191 | 0.23346 | 0.26093 | 0.87891 | 1.2177 | 121.6782 | 122.4152 | 0.16937 | 122.5342 | 10.2859 | -0.14191 | 122.4152 | 0.16937 | 10.2859 | 121.6782 | 122.5342 | -122.3923 | -122.4426
4277.9531 | 122.4518 | -0.064087 | 122.2458 | -0.053024 | 0.0057828 | -0.01255 | 0.009126 | 0.046055 | -0.0094678 | 0.068184 | 0.032043 | 122.2916 | -0.16937 | 0.13275 | 121.5912 | 10.2905 | 1.0712 | 1.355 | 122.4289 | -0.23346 | -0.10529 | 0.045776 | 0.09613 | 0.19684 | -0.6546 | -0.16937 | 0.1831 | 0.20142 | 1.1353 | 1.4191 | 121.6553 | 122.3557 | 0.09613 | 122.493 | 10.3546 | -0.16937 | 122.3557 | 0.09613 | 10.3546 | 121.6553 | 122.493 | -122.4152 | -122.4792
4279.6719 | 122.4564 | -0.054932 | 122.2504 | 0.00038159 | 0.010269 | -0.013618 | 0.012758 | 0.047123 | -0.013527 | 0.065834 | 0.022888 | 122.3328 | -0.17853 | 0.10071 | 121.55 | 10.2493 | 1.0391 | 1.2863 | 122.4289 | -0.2243 | -0.1236 | 0.082398 | 0.07782 | 0.15564 | -0.70038 | -0.16937 | 0.17853 | 0.20142 | 1.0941 | 1.3412 | 121.6049 | 122.3877 | 0.07782 | 122.4838 | 10.3043 | -0.16937 | 122.3877 | 0.07782 | 10.3043 | 121.6049 | 122.4838 | -122.4289 | -122.4747
4281.3594 | 122.3694 | -0.091553 | 122.2778 | -0.15984 | 0.009628 | -0.012764 | 0.012971 | 0.045201 | -0.010322 | 0.065407 | 0.10071 | 122.3419 | -0.15106 | 0.18768 | 121.6141 | 10.3729 | 1.0895 | 1.4603 | 122.4152 | -0.22888 | -0.059509 | 0.064087 | 0.19226 | 0.27924 | -0.66376 | -0.13733 | 0.13733 | 0.25177 | 1.181 | 1.5518 | 121.7056 | 122.4335 | 0.19226 | 122.5067 | 10.4645 | -0.13733 | 122.4335 | 0.19226 | 10.4645 | 121.7056 | 122.5067 | -122.4289 | -122.5067
4283.0781 | 122.3785 | -0.064087 | 122.2641 | -0.22087 | 0.0092008 | -0.015968 | 0.016603 | 0.046055 | -0.017158 | 0.066689 | -0.018311 | 122.319 | -0.23804 | 0.073242 | 121.4905 | 10.3043 | 1.3458 | 1.3687 | 122.4701 | -0.2655 | -0.17395 | 0.054932 | 0.045776 | 0.13733 | -0.77362 | -0.20142 | 0.20599 | 0.21973 | 1.4099 | 1.4328 | 121.5546 | 122.3831 | 0.045776 | 122.5342 | 10.3683 | -0.20142 | 122.3831 | 0.045776 | 10.3683 | 121.5546 | 122.5342 | -122.5021 | -122.5296
4284.7812 | 122.3557 | -0.10529 | 122.2641 | -0.14458 | 0.007919 | -0.013618 | 0.012117 | 0.045414 | -0.012031 | 0.066262 | 0.10529 | 122.3099 | -0.17853 | 0.20599 | 121.6324 | 10.4233 | 1.0986 | 1.506 | 122.4609 | -0.21515 | -0.073242 | 0.045776 | 0.21057 | 0.31128 | -0.63171 | -0.10986 | 0.19684 | 0.28381 | 1.2039 | 1.6113 | 121.7377 | 122.4152 | 0.21057 | 122.5662 | 10.5286 | -0.10986 | 122.4152 | 0.21057 | 10.5286 | 121.7377 | 122.5662 | -122.4426 | -122.4792
4286.4688 | 122.4564 | -0.068665 | 122.2366 | 0.099564 | 0.0094144 | -0.0089189 | 0.018098 | 0.049473 | -0.015236 | 0.066689 | -0.009155 | 122.3419 | -0.20599 | 0.045776 | 121.4722 | 10.1898 | 1.0254 | 1.062 | 122.5204 | -0.25177 | -0.13733 | 0.10529 | 0.05951 | 0.11444 | -0.76447 | -0.1831 | 0.28381 | 0.19684 | 1.0941 | 1.1307 | 121.5408 | 122.4106 | 0.05951 | 122.5891 | 10.2585 | -0.1831 | 122.4106 | 0.05951 | 10.2585 | 121.5408 | 122.5891 | -122.4426 | -122.4884
4288.1719 | 122.3419 | -0.10529 | 122.287 | -0.21324 | 0.0070646 | -0.017677 | 0.01233 | 0.044346 | -0.012458 | 0.066262 | 0.068665 | 122.2961 | -0.17853 | 0.16022 | 121.5912 | 10.4645 | 1.1948 | 1.5106 | 122.4243 | -0.20599 | -0.073242 | 0.009156 | 0.17395 | 0.2655 | -0.6958 | -0.10071 | 0.13733 | 0.24719 | 1.3 | 1.6159 | 121.6965 | 122.4014 | 0.17395 | 122.5296 | 10.5698 | -0.10071 | 122.4014 | 0.17395 | 10.5698 | 121.6965 | 122.5296 | -122.4655 | -122.493
4289.8906 | 122.4976 | -0.054932 | 122.2412 | 0.02327 | 0.010696 | -0.017464 | 0.010408 | 0.047978 | -0.01139 | 0.06797 | 0.032043 | 122.3145 | -0.17853 | 0.10071 | 121.5637 | 10.3226 | 1.0208 | 1.268 | 122.4701 | -0.2243 | -0.1236 | 0.073242 | 0.086975 | 0.15564 | -0.67749 | -0.16937 | 0.22888 | 0.21057 | 1.0757 | 1.3229 | 121.6187 | 122.3694 | 0.086975 | 122.525 | 10.3775 | -0.16937 | 122.3694 | 0.086975 | 10.3775 | 121.6187 | 122.525 | -122.4197 | -122.4655
4291.6406 | 122.3923 | -0.09613 | 122.2595 | -0.25902 | 0.007919 | -0.013832 | 0.014253 | 0.046269 | -0.013954 | 0.06498 | -0.027466 | 122.3145 | -0.21515 | 0.064087 | 121.4859 | 10.3867 | 1.3733 | 1.3687 | 122.4838 | -0.26093 | -0.11902 | 0.054932 | 0.068664 | 0.16022 | -0.77362 | -0.1648 | 0.2243 | 0.18768 | 1.4694 | 1.4648 | 121.582 | 122.4106 | 0.068664 | 122.58 | 10.4828 | -0.1648 | 122.4106 | 0.068664 | 10.4828 | 121.582 | 122.58 | -122.4747 | -122.5204
4293.3438 | 122.4609 | -0.045776 | 122.2412 | -0.014877 | 0.0094144 | -0.016396 | 0.0082714 | 0.045414 | -0.012672 | 0.065834 | 0.032043 | 122.3419 | -0.15564 | 0.1236 | 121.582 | 10.3958 | 1.0895 | 1.3504 | 122.4838 | -0.21057 | -0.10986 | 0.10071 | 0.077819 | 0.16937 | -0.65918 | -0.1648 | 0.24261 | 0.18768 | 1.1353 | 1.3962 | 121.6278 | 122.3877 | 0.077819 | 122.5296 | 10.4416 | -0.1648 | 122.3877 | 0.077819 | 10.4416 | 121.6278 | 122.5296 | -122.3969 | -122.4518
4295.0469 | 122.3282 | -0.10529 | 122.2687 | -0.17509 | 0.0081326 | -0.012764 | 0.012544 | 0.046269 | -0.012458 | 0.066048 | 0.09613 | 122.3145 | -0.16937 | 0.16022 | 121.5958 | 10.5148 | 1.2634 | 1.5106 | 122.4564 | -0.23346 | -0.064087 | 0.045776 | 0.20142 | 0.2655 | -0.67291 | -0.12817 | 0.18768 | 0.2655 | 1.3687 | 1.6159 | 121.7011 | 122.4197 | 0.20142 | 122.5616 | 10.6201 | -0.12817 | 122.4197 | 0.20142 | 10.6201 | 121.7011 | 122.5616 | -122.438 | -122.5021
4296.7344 | 122.4197 | -0.07782 | 122.2366 | 0.15297 | 0.0083462 | -0.011055 | 0.015535 | 0.047123 | -0.013954 | 0.065407 | 0.10986 | 122.287 | -0.15106 | 0.16022 | 121.6003 | 10.3775 | 0.83771 | 1.2268 | 122.4243 | -0.20599 | -0.073242 | 0.050354 | 0.18768 | 0.23804 | -0.63629 | -0.12817 | 0.18768 | 0.26093 | 0.91553 | 1.3046 | 121.6782 | 122.3648 | 0.18768 | 122.5021 | 10.4553 | -0.12817 | 122.3648 | 0.18768 | 10.4553 | 121.6782 | 122.5021 | -122.3877 | -122.4426
4298.4375 | 122.3877 | -0.086975 | 122.2595 | -0.2285 | 0.01091 | -0.013191 | 0.013398 | 0.046269 | -0.01374 | 0.06733 | -0.018311 | 122.3236 | -0.2243 | 0.064087 | 121.4905 | 10.4324 | 1.3962 | 1.4145 | 122.4792 | -0.25177 | -0.13733 | 0.064087 | 0.068664 | 0.15106 | -0.76904 | -0.16479 | 0.21973 | 0.20599 | 1.4832 | 1.5015 | 121.5775 | 122.4106 | 0.068664 | 122.5662 | 10.5194 | -0.16479 | 122.4106 | 0.068664 | 10.5194 | 121.5775 | 122.5662 | -122.4838 | -122.5113
4300.1875 | 122.3328 | -0.11444 | 122.2687 | -0.21324 | 0.0064236 | -0.015114 | 0.011689 | 0.047764 | -0.012458 | 0.064553 | 0.09613 | 122.3053 | -0.1831 | 0.17395 | 121.6141 | 10.5469 | 1.2039 | 1.5381 | 122.4426 | -0.23346 | -0.068664 | 0.036621 | 0.21057 | 0.28839 | -0.6546 | -0.11902 | 0.17395 | 0.27924 | 1.3184 | 1.6525 | 121.7285 | 122.4197 | 0.21057 | 122.5571 | 10.6613 | -0.11902 | 122.4197 | 0.21057 | 10.6613 | 121.7285 | 122.5571 | -122.4518 | -122.5021
4301.8906 | 122.4747 | -0.059509 | 122.2229 | 0.061417 | 0.0085598 | -0.014687 | 0.0099804 | 0.045201 | -0.013313 | 0.065621 | 0.064087 | 122.2916 | -0.15564 | 0.10986 | 121.5637 | 10.4004 | 0.99335 | 1.236 | 122.4564 | -0.23346 | -0.096131 | 0.068665 | 0.1236 | 0.16937 | -0.65918 | -0.17395 | 0.23346 | 0.21973 | 1.0529 | 1.2955 | 121.6232 | 122.3511 | 0.1236 | 122.5159 | 10.4599 | -0.17395 | 122.3511 | 0.1236 | 10.4599 | 121.6232 | 122.5159 | -122.3785 | -122.4564
4303.6406 | 122.3969 | -0.10071 | 122.2504 | -0.2285 | 0.0072782 | -0.0196 | 0.015321 | 0.045628 | -0.01374 | 0.064553 | -0.004578 | 122.319 | -0.23346 | 0.054932 | 121.5042 | 10.4874 | 1.4099 | 1.4053 | 122.4838 | -0.25177 | -0.13275 | 0.068665 | 0.09613 | 0.15564 | -0.74616 | -0.15106 | 0.23346 | 0.22888 | 1.5106 | 1.506 | 121.6049 | 122.4197 | 0.09613 | 122.5845 | 10.5881 | -0.15106 | 122.4197 | 0.09613 | 10.5881 | 121.6049 | 122.5845 | -122.4838 | -122.5021
4305.375 | 122.3511 | -0.10071 | 122.2778 | -0.20561 | 0.0087734 | -0.010414 | 0.011903 | 0.044987 | -0.011177 | 0.063912 | 0.082397 | 122.3099 | -0.16937 | 0.15564 | 121.582 | 10.5652 | 1.2909 | 1.5289 | 122.4289 | -0.23346 | -0.068665 | 0.032043 | 0.18311 | 0.25635 | -0.6958 | -0.13275 | 0.15106 | 0.25177 | 1.3916 | 1.6296 | 121.6827 | 122.4106 | 0.18311 | 122.5296 | 10.6659 | -0.13275 | 122.4106 | 0.18311 | 10.6659 | 121.6827 | 122.5296 | -122.4472 | -122.5113
4307.0781 | 122.4335 | -0.082397 | 122.2275 | 0.038529 | 0.0089872 | -0.01255 | 0.01703 | 0.048191 | -0.01609 | 0.066902 | -0.004578 | 122.3328 | -0.21515 | 0.027466 | 121.463 | 10.3683 | 1.1032 | 1.1124 | 122.493 | -0.25177 | -0.13275 | 0.10529 | 0.077819 | 0.10986 | -0.76447 | -0.16937 | 0.2655 | 0.21057 | 1.1856 | 1.1948 | 121.5454 | 122.4152 | 0.077819 | 122.5754 | 10.4507 | -0.16937 | 122.4152 | 0.077819 | 10.4507 | 121.5454 | 122.5754 | -122.4426 | -122.4792
4308.8125 | 122.3877 | -0.073242 | 122.2961 | -0.2285 | 0.0085598 | -0.013618 | 0.012117 | 0.046269 | -0.013099 | 0.067116 | 0.032043 | 122.3465 | -0.20142 | 0.073242 | 121.5134 | 10.5377 | 1.4008 | 1.4511 | 122.4609 | -0.24719 | -0.12817 | 0.050354 | 0.10529 | 0.14648 | -0.78278 | -0.17395 | 0.16479 | 0.23346 | 1.474 | 1.5244 | 121.5866 | 122.4197 | 0.10529 | 122.5342 | 10.611 | -0.17395 | 122.4197 | 0.10529 | 10.611 | 121.5866 | 122.5342 | -122.4976 | -122.5433
4310.6094 | 122.3511 | -0.086975 | 122.2733 | -0.045395 | 0.0085598 | -0.015327 | 0.014467 | 0.049259 | -0.01609 | 0.066475 | 0.045776 | 122.3282 | -0.21515 | 0.091553 | 121.5134 | 10.4965 | 1.1581 | 1.2543 | 122.4701 | -0.25177 | -0.12817 | 0.054932 | 0.13275 | 0.17853 | -0.75989 | -0.16479 | 0.19684 | 0.26093 | 1.2451 | 1.3412 | 121.6003 | 122.4152 | 0.13275 | 122.5571 | 10.5835 | -0.16479 | 122.4152 | 0.13275 | 10.5835 | 121.6003 | 122.5571 | -122.4884 | -122.525
4312.3906 | 122.3282 | -0.082397 | 122.287 | -0.14458 | 0.0072782 | -0.015968 | 0.015321 | 0.050114 | -0.014595 | 0.065193 | 0.045776 | 122.3145 | -0.22888 | 0.10986 | 121.5317 | 10.5789 | 1.268 | 1.3824 | 122.5021 | -0.23346 | -0.14649 | 0.027466 | 0.12817 | 0.19226 | -0.75531 | -0.15106 | 0.21515 | 0.27466 | 1.3504 | 1.4648 | 121.6141 | 122.3969 | 0.12817 | 122.5845 | 10.6613 | -0.15106 | 122.3969 | 0.12817 | 10.6613 | 121.6141 | 122.5845 | -122.5159 | -122.5204
4314.125 | 122.3557 | -0.10986 | 122.2824 | -0.18272 | 0.0085598 | -0.017036 | 0.0095532 | 0.047764 | -0.013313 | 0.066902 | 0.10986 | 122.3053 | -0.16479 | 0.16022 | 121.6141 | 10.6567 | 1.2817 | 1.5564 | 122.4609 | -0.21515 | -0.054932 | 0.022888 | 0.21973 | 0.27008 | -0.66833 | -0.10529 | 0.17853 | 0.27466 | 1.3916 | 1.6663 | 121.7239 | 122.4152 | 0.21973 | 122.5708 | 10.7666 | -0.10529 | 122.4152 | 0.21973 | 10.7666 | 121.7239 | 122.5708 | -122.4472 | -122.4976
4315.8906 | 122.438 | -0.059509 | 122.2366 | -0.098801 | 0.0092008 | -0.013618 | 0.0080578 | 0.047764 | -0.01139 | 0.064766 | 0.086975 | 122.2961 | -0.17395 | 0.14191 | 121.6141 | 10.6293 | 1.1536 | 1.4603 | 122.4655 | -0.21973 | -0.11444 | 0.05951 | 0.14648 | 0.20142 | -0.62256 | -0.16022 | 0.22888 | 0.26092 | 1.2131 | 1.5198 | 121.6736 | 122.3557 | 0.14648 | 122.525 | 10.6888 | -0.16022 | 122.3557 | 0.14648 | 10.6888 | 121.6736 | 122.525 | -122.4106 | -122.4564
4317.6562 | 122.3602 | -0.10071 | 122.2824 | -0.24376 | 0.009628 | -0.0095597 | 0.0095532 | 0.044132 | -0.012886 | 0.064125 | 0.10529 | 122.3557 | -0.1831 | 0.14191 | 121.5775 | 10.6659 | 1.3504 | 1.5198 | 122.4518 | -0.23804 | -0.082397 | 0.073242 | 0.20599 | 0.24262 | -0.70496 | -0.13733 | 0.16937 | 0.28839 | 1.4511 | 1.6205 | 121.6782 | 122.4564 | 0.20599 | 122.5525 | 10.7666 | -0.13733 | 122.4564 | 0.20599 | 10.7666 | 121.6782 | 122.5525 | -122.4655 | -122.5204
4319.3594 | 122.4884 | -0.045776 | 122.2366 | -0.0072479 | 0.0087734 | -0.015541 | 0.010835 | 0.044987 | -0.012245 | 0.066689 | 0.064087 | 122.2916 | -0.16022 | 0.09613 | 121.5454 | 10.5469 | 1.0712 | 1.3046 | 122.438 | -0.23346 | -0.11444 | 0.054932 | 0.10986 | 0.14191 | -0.69122 | -0.18768 | 0.20142 | 0.2243 | 1.1169 | 1.3504 | 121.5912 | 122.3373 | 0.10986 | 122.4838 | 10.5927 | -0.18768 | 122.3373 | 0.10986 | 10.5927 | 121.5912 | 122.4838 | -122.3969 | -122.4701
4321.125 | 122.4289 | -0.073242 | 122.2549 | 0.091934 | 0.0085598 | -0.0099869 | 0.013612 | 0.047337 | -0.012886 | 0.066689 | 0.10529 | 122.2961 | -0.16479 | 0.14648 | 121.5729 | 10.5606 | 0.9201 | 1.2634 | 122.4243 | -0.21057 | -0.091553 | 0.041199 | 0.17853 | 0.21973 | -0.68207 | -0.13733 | 0.16937 | 0.27008 | 0.99335 | 1.3367 | 121.6461 | 122.3694 | 0.17853 | 122.4976 | 10.6339 | -0.13733 | 122.3694 | 0.17853 | 10.6339 | 121.6461 | 122.4976 | -122.4197 | -122.4655
4322.8125 | 122.3648 | -0.10071 | 122.2687 | -0.28191 | 0.0092008 | -0.015968 | 0.011262 | 0.045841 | -0.01374 | 0.064339 | 0.07782 | 122.3236 | -0.1831 | 0.13275 | 121.55 | 10.6888 | 1.3733 | 1.5381 | 122.4747 | -0.23804 | -0.082397 | 0.054931 | 0.17853 | 0.23346 | -0.71869 | -0.13733 | 0.20599 | 0.26092 | 1.474 | 1.6388 | 121.6507 | 122.4243 | 0.17853 | 122.5754 | 10.7895 | -0.13733 | 122.4243 | 0.17853 | 10.7895 | 121.6507 | 122.5754 | -122.4518 | -122.5067
4324.5781 | 122.3511 | -0.082397 | 122.2778 | -0.19035 | 0.0074918 | -0.011696 | 0.01703 | 0.04456 | -0.014808 | 0.06733 | 0.018311 | 122.3373 | -0.21057 | 0.091553 | 121.5179 | 10.6613 | 1.3504 | 1.4191 | 122.4701 | -0.23804 | -0.12817 | 0.059509 | 0.10071 | 0.17395 | -0.75989 | -0.15564 | 0.19226 | 0.22888 | 1.4328 | 1.5015 | 121.6003 | 122.4197 | 0.10071 | 122.5525 | 10.7437 | -0.15564 | 122.4197 | 0.10071 | 10.7437 | 121.6003 | 122.5525 | -122.4884 | -122.5159
4326.3438 | 122.4106 | -0.091553 | 122.2641 | 0.1606 | 0.007919 | -0.011482 | 0.011689 | 0.048191 | -0.013313 | 0.065834 | 0.11902 | 122.2961 | -0.1831 | 0.16479 | 121.5912 | 10.6018 | 0.91095 | 1.2589 | 122.4289 | -0.21515 | -0.091552 | 0.032044 | 0.21057 | 0.25635 | -0.67291 | -0.1236 | 0.16479 | 0.30212 | 1.0025 | 1.3504 | 121.6827 | 122.3877 | 0.21057 | 122.5204 | 10.6934 | -0.1236 | 122.3877 | 0.21057 | 10.6934 | 121.6827 | 122.5204 | -122.4472 | -122.4792
4328.1094 | 122.3328 | -0.10071 | 122.2641 | -0.12169 | 0.0074918 | -0.016182 | 0.015962 | 0.046269 | -0.015022 | 0.065834 | 0.054932 | 122.3099 | -0.21973 | 0.10986 | 121.5179 | 10.6888 | 1.2817 | 1.4282 | 122.4701 | -0.23804 | -0.11902 | 0.045776 | 0.15564 | 0.21057 | -0.74616 | -0.13733 | 0.20599 | 0.27466 | 1.3824 | 1.5289 | 121.6187 | 122.4106 | 0.15564 | 122.5708 | 10.7895 | -0.13733 | 122.4106 | 0.15564 | 10.7895 | 121.6187 | 122.5708 | -122.4838 | -122.5021
4329.8125 | 122.3282 | -0.10986 | 122.2687 | -0.20561 | 0.0089872 | -0.014473 | 0.0080578 | 0.046269 | -0.012031 | 0.066048 | 0.10986 | 122.3145 | -0.17395 | 0.1831 | 121.6141 | 10.8032 | 1.2817 | 1.6022 | 122.4701 | -0.22888 | -0.064087 | 0.045776 | 0.21973 | 0.29297 | -0.6546 | -0.11902 | 0.20142 | 0.28381 | 1.3916 | 1.712 | 121.7239 | 122.4243 | 0.21973 | 122.58 | 10.9131 | -0.11902 | 122.4243 | 0.21973 | 10.9131 | 121.7239 | 122.58 | -122.4426 | -122.4976
4331.5781 | 122.4197 | -0.054932 | 122.2687 | 0.10719 | 0.0081326 | -0.012123 | 0.013612 | 0.049473 | -0.015449 | 0.06498 | 0.11444 | 122.3007 | -0.1831 | 0.14191 | 121.582 | 10.6522 | 0.91095 | 1.2451 | 122.4472 | -0.19226 | -0.12817 | 0.032043 | 0.16937 | 0.19684 | -0.68665 | -0.13733 | 0.17853 | 0.29755 | 0.96588 | 1.3 | 121.637 | 122.3557 | 0.16937 | 122.5021 | 10.7071 | -0.13733 | 122.3557 | 0.16937 | 10.7071 | 121.637 | 122.5021 | -122.4518 | -122.4609
4333.3281 | 122.4197 | -0.064087 | 122.2549 | -0.083542 | 0.0089872 | -0.013405 | 0.0080578 | 0.047123 | -0.009895 | 0.064125 | 0.091553 | 122.3465 | -0.16479 | 0.15564 | 121.6187 | 10.7574 | 1.1993 | 1.5106 | 122.4518 | -0.23804 | -0.10071 | 0.091553 | 0.15564 | 0.21973 | -0.63629 | -0.17395 | 0.19684 | 0.25635 | 1.2634 | 1.5747 | 121.6827 | 122.4106 | 0.15564 | 122.5159 | 10.8215 | -0.17395 | 122.4106 | 0.15564 | 10.8215 | 121.6827 | 122.5159 | -122.4197 | -122.493
4335.0938 | 122.3373 | -0.10071 | 122.2778 | -0.068283 | 0.0092008 | -0.010414 | 0.01938 | 0.047337 | -0.014167 | 0.065834 | 0.068665 | 122.3053 | -0.21515 | 0.1236 | 121.5088 | 10.73 | 1.2405 | 1.3779 | 122.4747 | -0.24261 | -0.11444 | 0.027466 | 0.16937 | 0.2243 | -0.76904 | -0.14191 | 0.19684 | 0.28381 | 1.3412 | 1.4786 | 121.6095 | 122.406 | 0.16937 | 122.5754 | 10.8307 | -0.14191 | 122.406 | 0.16937 | 10.8307 | 121.6095 | 122.5754 | -122.493 | -122.5204
4336.8125 | 122.4426 | -0.064087 | 122.2412 | 0.084305 | 0.0087734 | -0.012337 | 0.011262 | 0.048191 | -0.013313 | 0.066689 | 0.10071 | 122.3419 | -0.17395 | 0.13275 | 121.5546 | 10.6659 | 0.97504 | 1.2863 | 122.438 | -0.23346 | -0.10986 | 0.10071 | 0.1648 | 0.19684 | -0.68665 | -0.16937 | 0.19684 | 0.27466 | 1.0391 | 1.3504 | 121.6187 | 122.406 | 0.1648 | 122.5021 | 10.73 | -0.16937 | 122.406 | 0.1648 | 10.73 | 121.6187 | 122.5021 | -122.4152 | -122.4747
4338.5625 | 122.4564 | -0.059509 | 122.2412 | -0.075912 | 0.0092008 | -0.0196 | 0.009126 | 0.045201 | -0.011818 | 0.066048 | 0.068665 | 122.319 | -0.17395 | 0.13733 | 121.582 | 10.7666 | 1.1856 | 1.4832 | 122.406 | -0.21973 | -0.11444 | 0.07782 | 0.12817 | 0.19684 | -0.65918 | -0.16022 | 0.16479 | 0.24261 | 1.2451 | 1.5427 | 121.6415 | 122.3785 | 0.12817 | 122.4655 | 10.8261 | -0.16022 | 122.3785 | 0.12817 | 10.8261 | 121.6415 | 122.4655 | -122.4152 | -122.4609
4340.3281 | 122.3785 | -0.10071 | 122.2733 | -0.2285 | 0.0072782 | -0.015755 | 0.014894 | 0.044346 | -0.014381 | 0.066262 | 0.004578 | 122.2961 | -0.23346 | 0.050354 | 121.4951 | 10.7483 | 1.4832 | 1.4786 | 122.5021 | -0.25635 | -0.13275 | 0.022889 | 0.10529 | 0.15106 | -0.7782 | -0.15564 | 0.22888 | 0.23804 | 1.5839 | 1.5793 | 121.5958 | 122.3969 | 0.10529 | 122.6028 | 10.849 | -0.15564 | 122.3969 | 0.10529 | 10.849 | 121.5958 | 122.6028 | -122.5067 | -122.5296
4342.0938 | 122.4564 | -0.045776 | 122.2321 | 0.01564 | 0.0087734 | -0.0149 | 0.009126 | 0.047337 | -0.012245 | 0.063271 | 0.054932 | 122.319 | -0.1831 | 0.10529 | 121.5546 | 10.7254 | 1.1627 | 1.387 | 122.4564 | -0.22888 | -0.13733 | 0.086975 | 0.10071 | 0.15106 | -0.67749 | -0.18311 | 0.2243 | 0.23804 | 1.2085 | 1.4328 | 121.6003 | 122.3648 | 0.10071 | 122.5021 | 10.7712 | -0.18311 | 122.3648 | 0.10071 | 10.7712 | 121.6003 | 122.5021 | -122.4152 | -122.4609
4343.7969 | 122.4701 | -0.054932 | 122.2321 | 0.0080111 | 0.010055 | -0.011696 | 0.011476 | 0.044132 | -0.012245 | 0.06498 | 0.059509 | 122.3282 | -0.20142 | 0.10071 | 121.5363 | 10.7346 | 1.149 | 1.3687 | 122.4243 | -0.2243 | -0.14648 | 0.09613 | 0.11444 | 0.15564 | -0.6958 | -0.16937 | 0.19226 | 0.26093 | 1.2039 | 1.4236 | 121.5912 | 122.3831 | 0.11444 | 122.4792 | 10.7895 | -0.16937 | 122.3831 | 0.11444 | 10.7895 | 121.5912 | 122.4792 | -122.4335 | -122.4564
4345.5625 | 122.3236 | -0.10986 | 122.2916 | -0.16747 | 0.0094144 | -0.016396 | 0.017671 | 0.045201 | -0.012458 | 0.065407 | 0.050354 | 122.2916 | -0.21057 | 0.11444 | 121.5225 | 10.8124 | 1.3367 | 1.4603 | 122.493 | -0.23804 | -0.10071 | 0 | 0.16022 | 0.2243 | -0.76904 | -0.12817 | 0.20142 | 0.26093 | 1.4465 | 1.5701 | 121.6324 | 122.4014 | 0.16022 | 122.6028 | 10.9222 | -0.12817 | 122.4014 | 0.16022 | 10.9222 | 121.6324 | 122.6028 | -122.5021 | -122.5296
4347.3281 | 122.3328 | -0.091553 | 122.2687 | -0.091171 | 0.011123 | -0.011696 | 0.020021 | 0.04755 | -0.014381 | 0.06498 | 0.10529 | 122.3145 | -0.21973 | 0.11444 | 121.5225 | 10.817 | 1.236 | 1.4008 | 122.4976 | -0.25177 | -0.12817 | 0.045776 | 0.19684 | 0.20599 | -0.74616 | -0.16022 | 0.22888 | 0.32501 | 1.3275 | 1.4923 | 121.6141 | 122.406 | 0.19684 | 122.5891 | 10.9085 | -0.16022 | 122.406 | 0.19684 | 10.9085 | 121.6141 | 122.5891 | -122.4884 | -122.5204
4349.0312 | 122.3877 | -0.10529 | 122.2824 | -0.19035 | 0.010055 | -0.016182 | 0.01233 | 0.045628 | -0.013527 | 0.066048 | 0.013733 | 122.3602 | -0.20599 | 0.050354 | 121.4951 | 10.8215 | 1.5015 | 1.506 | 122.4518 | -0.26093 | -0.10071 | 0.077819 | 0.11902 | 0.15564 | -0.78735 | -0.15564 | 0.16937 | 0.21973 | 1.6068 | 1.6113 | 121.6003 | 122.4655 | 0.11902 | 122.5571 | 10.9268 | -0.15564 | 122.4655 | 0.11902 | 10.9268 | 121.6003 | 122.5571 | -122.4884 | -122.5433
4350.7969 | 122.3557 | -0.082397 | 122.2549 | -0.030136 | 0.0087734 | -0.015114 | 0.016176 | 0.048405 | -0.013527 | 0.065834 | 0.059509 | 122.3236 | -0.20599 | 0.086975 | 121.4996 | 10.762 | 1.2314 | 1.3092 | 122.4701 | -0.24719 | -0.1236 | 0.068664 | 0.14191 | 0.16937 | -0.75531 | -0.16479 | 0.21515 | 0.2655 | 1.3138 | 1.3916 | 121.582 | 122.406 | 0.14191 | 122.5525 | 10.8444 | -0.16479 | 122.406 | 0.14191 | 10.8444 | 121.582 | 122.5525 | -122.4609 | -122.5021
4352.5781 | 122.3373 | -0.10529 | 122.2733 | -0.18272 | 0.0083462 | -0.014687 | 0.010835 | 0.045628 | -0.0096814 | 0.066689 | 0.10071 | 122.3145 | -0.16479 | 0.13275 | 121.5912 | 10.9268 | 1.3824 | 1.6113 | 122.4289 | -0.22888 | -0.059509 | 0.041199 | 0.20599 | 0.23804 | -0.68207 | -0.1236 | 0.15564 | 0.2655 | 1.4877 | 1.7166 | 121.6965 | 122.4197 | 0.20599 | 122.5342 | 11.0321 | -0.1236 | 122.4197 | 0.20599 | 11.0321 | 121.6965 | 122.5342 | -122.438 | -122.5021
4354.2812 | 122.4518 | -0.045776 | 122.2 | 0.10719 | 0.009628 | -0.011269 | 0.012971 | 0.047978 | -0.014167 | 0.065834 | 0.032043 | 122.3328 | -0.21973 | 0.045776 | 121.4722 | 10.6979 | 1.1215 | 1.1673 | 122.493 | -0.2655 | -0.17395 | 0.13275 | 0.077819 | 0.091552 | -0.72784 | -0.21973 | 0.29297 | 0.25177 | 1.1673 | 1.2131 | 121.5179 | 122.3785 | 0.077819 | 122.5388 | 10.7437 | -0.21973 | 122.3785 | 0.077819 | 10.7437 | 121.5179 | 122.5388 | -122.4197 | -122.4655
4356.0469 | 122.3465 | -0.09613 | 122.2412 | -0.14458 | 0.007919 | -0.015327 | 0.0078442 | 0.045628 | -0.012031 | 0.066689 | 0.1236 | 122.319 | -0.1831 | 0.16479 | 121.6232 | 10.9543 | 1.2405 | 1.5884 | 122.4152 | -0.21515 | -0.086975 | 0.07782 | 0.21973 | 0.26092 | -0.61798 | -0.11902 | 0.17395 | 0.3067 | 1.3367 | 1.6846 | 121.7194 | 122.4152 | 0.21973 | 122.5113 | 11.0504 | -0.11902 | 122.4152 | 0.21973 | 11.0504 | 121.7194 | 122.5113 | -122.4243 | -122.4564
4357.8125 | 122.374 | -0.086975 | 122.2504 | -0.20561 | 0.0092008 | -0.013405 | 0.01468 | 0.044773 | -0.015236 | 0.065621 | 0.013733 | 122.319 | -0.22888 | 0.050354 | 121.4951 | 10.8902 | 1.4923 | 1.4786 | 122.4701 | -0.2655 | -0.14191 | 0.068665 | 0.10071 | 0.13733 | -0.75531 | -0.17853 | 0.21973 | 0.24261 | 1.5793 | 1.5656 | 121.582 | 122.406 | 0.10071 | 122.5571 | 10.9772 | -0.17853 | 122.406 | 0.10071 | 10.9772 | 121.582 | 122.5571 | -122.4792 | -122.5159
4359.5781 | 122.4152 | -0.064087 | 122.2549 | 0.19112 | 0.007919 | -0.012764 | 0.014253 | 0.04755 | -0.013313 | 0.065834 | 0.15106 | 122.2916 | -0.18768 | 0.16022 | 121.5866 | 10.8627 | 0.9613 | 1.3275 | 122.406 | -0.20142 | -0.1236 | 0.036621 | 0.21515 | 0.2243 | -0.66833 | -0.13733 | 0.15106 | 0.33874 | 1.0254 | 1.3916 | 121.6507 | 122.3557 | 0.21515 | 122.4701 | 10.9268 | -0.13733 | 122.3557 | 0.21515 | 10.9268 | 121.6507 | 122.4701 | -122.4426 | -122.4564
4361.3438 | 122.3831 | -0.10529 | 122.2504 | 0.00038159 | 0.01091 | -0.012337 | 0.016389 | 0.049259 | -0.014595 | 0.065193 | 0.073242 | 122.3145 | -0.19684 | 0.068665 | 121.4767 | 10.8215 | 1.2177 | 1.2772 | 122.4838 | -0.25177 | -0.091552 | 0.064087 | 0.17853 | 0.17395 | -0.77362 | -0.14648 | 0.23346 | 0.27008 | 1.3229 | 1.3824 | 121.582 | 122.4197 | 0.17853 | 122.5891 | 10.9268 | -0.14648 | 122.4197 | 0.17853 | 10.9268 | 121.582 | 122.5891 | -122.4472 | -122.5021
4363.125 | 122.4426 | -0.041199 | 122.2549 | -0.075912 | 0.0098416 | -0.021736 | 0.0061352 | 0.045841 | -0.010963 | 0.066262 | 0.086975 | 122.3236 | -0.18768 | 0.11902 | 121.5729 | 10.9589 | 1.236 | 1.5289 | 122.4289 | -0.23804 | -0.14648 | 0.068664 | 0.12817 | 0.16022 | -0.68207 | -0.19684 | 0.17395 | 0.27466 | 1.2772 | 1.5701 | 121.6141 | 122.3648 | 0.12817 | 122.4701 | 11.0001 | -0.19684 | 122.3648 | 0.12817 | 11.0001 | 121.6141 | 122.4701 | -122.4426 | -122.493
4364.8281 | 122.4655 | -0.054932 | 122.2183 | 0.0080111 | 0.0092008 | -0.011482 | 0.0078442 | 0.046482 | -0.013099 | 0.064553 | 0.07782 | 122.3282 | -0.19226 | 0.086975 | 121.55 | 10.8856 | 1.1993 | 1.4008 | 122.4564 | -0.23804 | -0.13733 | 0.10986 | 0.13275 | 0.14191 | -0.66833 | -0.1831 | 0.23804 | 0.27008 | 1.2543 | 1.4557 | 121.6049 | 122.3831 | 0.13275 | 122.5113 | 10.9406 | -0.1831 | 122.3831 | 0.13275 | 10.9406 | 121.6049 | 122.5113 | -122.4106 | -122.4564
4366.5938 | 122.4564 | -0.054932 | 122.2321 | 0.053787 | 0.0087734 | -0.013405 | 0.011689 | 0.044773 | -0.012458 | 0.066048 | 0.10529 | 122.3053 | -0.18768 | 0.10529 | 121.5271 | 10.8902 | 1.1169 | 1.3779 | 122.4609 | -0.23804 | -0.13275 | 0.073242 | 0.16022 | 0.16022 | -0.70496 | -0.1831 | 0.22888 | 0.29297 | 1.1719 | 1.4328 | 121.582 | 122.3602 | 0.16022 | 122.5159 | 10.9451 | -0.1831 | 122.3602 | 0.16022 | 10.9451 | 121.582 | 122.5159 | -122.4197 | -122.4701
4368.3438 | 122.3557 | -0.10529 | 122.2549 | -0.18272 | 0.0083462 | -0.010414 | 0.013612 | 0.044987 | -0.012031 | 0.065621 | 0.11444 | 122.287 | -0.16937 | 0.15564 | 121.5729 | 11.055 | 1.4236 | 1.6434 | 122.4426 | -0.2243 | -0.064087 | 0.032043 | 0.21973 | 0.26093 | -0.68207 | -0.11902 | 0.18768 | 0.28381 | 1.5289 | 1.7487 | 121.6782 | 122.3923 | 0.21973 | 122.5479 | 11.1603 | -0.11902 | 122.3923 | 0.21973 | 11.1603 | 121.6782 | 122.5479 | -122.4243 | -122.4792
4370.0469 | 122.4655 | -0.059509 | 122.2092 | 0.12245 | 0.0098416 | -0.0097733 | 0.017457 | 0.049687 | -0.013099 | 0.066902 | 0.054932 | 122.3694 | -0.21973 | 0.036621 | 121.4584 | 10.8215 | 1.1398 | 1.1993 | 122.4976 | -0.25177 | -0.16022 | 0.16022 | 0.11444 | 0.09613 | -0.75073 | -0.19226 | 0.28839 | 0.27466 | 1.1993 | 1.2589 | 121.5179 | 122.4289 | 0.11444 | 122.5571 | 10.881 | -0.19226 | 122.4289 | 0.11444 | 10.881 | 121.5179 | 122.5571 | -122.4289 | -122.4609
4371.8281 | 122.3419 | -0.07782 | 122.2595 | -0.20561 | 0.0081326 | -0.020241 | 0.015321 | 0.046696 | -0.015236 | 0.063698 | 0.041199 | 122.319 | -0.21057 | 0.10529 | 121.5042 | 11.0138 | 1.442 | 1.5198 | 122.5067 | -0.24261 | -0.13275 | 0.05951 | 0.11902 | 0.18311 | -0.75531 | -0.16479 | 0.24719 | 0.25177 | 1.5198 | 1.5976 | 121.582 | 122.3969 | 0.11902 | 122.5845 | 11.0916 | -0.16479 | 122.3969 | 0.11902 | 11.0916 | 121.582 | 122.5845 | -122.4701 | -122.5021
4373.5938 | 122.4838 | -0.050354 | 122.2595 | 0.0080111 | 0.0089872 | -0.016182 | 0.009126 | 0.047764 | -0.013527 | 0.066262 | 0.091553 | 122.3236 | -0.19226 | 0.10071 | 121.55 | 10.968 | 1.2131 | 1.4191 | 122.4655 | -0.2243 | -0.14191 | 0.064087 | 0.14191 | 0.15106 | -0.70953 | -0.17395 | 0.20599 | 0.28381 | 1.2634 | 1.4694 | 121.6003 | 122.374 | 0.14191 | 122.5159 | 11.0184 | -0.17395 | 122.374 | 0.14191 | 11.0184 | 121.6003 | 122.5159 | -122.4518 | -122.4838
4375.3438 | 122.3465 | -0.10529 | 122.2687 | -0.17509 | 0.0092008 | -0.016182 | 0.011049 | 0.044346 | -0.012672 | 0.064766 | 0.16022 | 122.3053 | -0.16479 | 0.17853 | 121.6095 | 11.1099 | 1.3229 | 1.6525 | 122.4426 | -0.21515 | -0.059509 | 0.036621 | 0.2655 | 0.28381 | -0.65918 | -0.10986 | 0.17395 | 0.32501 | 1.4282 | 1.7578 | 121.7148 | 122.4106 | 0.2655 | 122.5479 | 11.2152 | -0.10986 | 122.4106 | 0.2655 | 11.2152 | 121.7148 | 122.5479 | -122.4335 | -122.4838
4377.0469 | 122.4518 | -0.054932 | 122.2641 | -0.030136 | 0.0081326 | -0.014687 | 0.011049 | 0.045201 | -0.013099 | 0.066262 | 0.10529 | 122.3373 | -0.18768 | 0.13733 | 121.5637 | 11.0321 | 1.2497 | 1.5381 | 122.4426 | -0.2243 | -0.13275 | 0.073242 | 0.16022 | 0.19226 | -0.70038 | -0.16937 | 0.17853 | 0.29297 | 1.3046 | 1.593 | 121.6187 | 122.3923 | 0.16022 | 122.4976 | 11.087 | -0.16937 | 122.3923 | 0.16022 | 11.087 | 121.6187 | 122.4976 | -122.4518 | -122.4884
4378.8125 | 122.3236 | -0.09613 | 122.2458 | -0.098801 | 0.0064236 | -0.0149 | 0.018098 | 0.048191 | -0.016517 | 0.065407 | 0.11902 | 122.3007 | -0.21057 | 0.13275 | 121.5179 | 11.0733 | 1.3321 | 1.4786 | 122.4701 | -0.24719 | -0.11444 | 0.054931 | 0.21515 | 0.22888 | -0.72785 | -0.15106 | 0.2243 | 0.32959 | 1.4282 | 1.5747 | 121.6141 | 122.3969 | 0.21515 | 122.5662 | 11.1694 | -0.15106 | 122.3969 | 0.21515 | 11.1694 | 121.6141 | 122.5662 | -122.4564 | -122.493
4380.5156 | 122.374 | -0.10071 | 122.2549 | -0.17509 | 0.0087734 | -0.017036 | 0.014253 | 0.049473 | -0.015663 | 0.064339 | 0.032043 | 122.3465 | -0.22888 | 0.073242 | 121.4905 | 11.0779 | 1.5244 | 1.5518 | 122.4747 | -0.27008 | -0.12817 | 0.091553 | 0.13275 | 0.17395 | -0.76447 | -0.16937 | 0.21973 | 0.26093 | 1.6251 | 1.6525 | 121.5912 | 122.4472 | 0.13275 | 122.5754 | 11.1786 | -0.16937 | 122.4472 | 0.13275 | 11.1786 | 121.5912 | 122.5754 | -122.4838 | -122.525
4382.2812 | 122.4106 | -0.054932 | 122.2412 | 0.046158 | 0.0070646 | -0.011269 | 0.013398 | 0.049259 | -0.013313 | 0.065193 | 0.15564 | 122.3053 | -0.16937 | 0.14191 | 121.5683 | 11.0092 | 0.98877 | 1.3092 | 122.4564 | -0.21515 | -0.11444 | 0.064087 | 0.21057 | 0.19684 | -0.67291 | -0.16022 | 0.21515 | 0.32501 | 1.0437 | 1.3641 | 121.6232 | 122.3602 | 0.21057 | 122.5113 | 11.0641 | -0.16022 | 122.3602 | 0.21057 | 11.0641 | 121.6232 | 122.5113 | -122.4106 | -122.4564
4383.9844 | 122.3419 | -0.10529 | 122.2641 | -0.053024 | 0.0083462 | -0.013832 | 0.015748 | 0.048619 | -0.014167 | 0.066262 | 0.091553 | 122.3465 | -0.21057 | 0.10071 | 121.5179 | 11.0596 | 1.2817 | 1.4053 | 122.4701 | -0.24719 | -0.10529 | 0.082398 | 0.19684 | 0.20599 | -0.74616 | -0.14191 | 0.20599 | 0.30212 | 1.387 | 1.5106 | 121.6232 | 122.4518 | 0.19684 | 122.5754 | 11.1649 | -0.14191 | 122.4518 | 0.19684 | 11.1649 | 121.6232 | 122.5754 | -122.4747 | -122.5113
4385.75 | 122.406 | -0.068665 | 122.2275 | 0.17586 | 0.0089872 | -0.015114 | 0.011689 | 0.048191 | -0.015663 | 0.06797 | 0.10529 | 122.3419 | -0.19684 | 0.11444 | 121.5454 | 11.0229 | 1.0025 | 1.268 | 122.4289 | -0.21973 | -0.12817 | 0.11444 | 0.17395 | 0.18311 | -0.68207 | -0.15106 | 0.20142 | 0.30212 | 1.0712 | 1.3367 | 121.6141 | 122.4106 | 0.17395 | 122.4976 | 11.0916 | -0.15106 | 122.4106 | 0.17395 | 11.0916 | 121.6141 | 122.4976 | -122.4243 | -122.4472
4387.5469 | 122.4655 | -0.050354 | 122.2458 | 0.11482 | 0.011551 | -0.015541 | 0.014894 | 0.047764 | -0.015022 | 0.068184 | 0.054932 | 122.3465 | -0.21515 | 0.027466 | 121.4539 | 10.9634 | 1.1765 | 1.1902 | 122.4655 | -0.27466 | -0.16479 | 0.10071 | 0.10529 | 0.07782 | -0.79193 | -0.2243 | 0.21973 | 0.27008 | 1.2268 | 1.2405 | 121.5042 | 122.3969 | 0.10529 | 122.5159 | 11.0138 | -0.2243 | 122.3969 | 0.10529 | 11.0138 | 121.5042 | 122.5159 | -122.4609 | -122.5204
4389.25 | 122.3511 | -0.11902 | 122.2641 | -0.17509 | 0.0087734 | -0.013832 | 0.0089124 | 0.045201 | -0.013099 | 0.063271 | 0.13733 | 122.3145 | -0.16022 | 0.15564 | 121.5775 | 11.2198 | 1.474 | 1.7212 | 122.4518 | -0.22888 | -0.041198 | 0.050354 | 0.25635 | 0.27466 | -0.68664 | -0.10986 | 0.18768 | 0.29755 | 1.593 | 1.8402 | 121.6965 | 122.4335 | 0.25635 | 122.5708 | 11.3388 | -0.10986 | 122.4335 | 0.25635 | 11.3388 | 121.6965 | 122.5708 | -122.4243 | -122.493
4391 | 122.374 | -0.064087 | 122.2687 | -0.22087 | 0.011337 | -0.014046 | 0.011262 | 0.045414 | -0.015236 | 0.066689 | 0.036621 | 122.3694 | -0.21515 | 0.054932 | 121.4676 | 11.1603 | 1.5976 | 1.5701 | 122.4518 | -0.25177 | -0.15106 | 0.10071 | 0.10071 | 0.11902 | -0.80109 | -0.18768 | 0.1831 | 0.25177 | 1.6617 | 1.6342 | 121.5317 | 122.4335 | 0.10071 | 122.5159 | 11.2244 | -0.18768 | 122.4335 | 0.10071 | 11.2244 | 121.5317 | 122.5159 | -122.4838 | -122.5204
4392.7656 | 122.3785 | -0.091553 | 122.2641 | 0.01564 | 0.0087734 | -0.013405 | 0.018098 | 0.048405 | -0.015449 | 0.066902 | 0.086975 | 122.3328 | -0.21515 | 0.041199 | 121.4447 | 11.0504 | 1.2634 | 1.2955 | 122.4884 | -0.24719 | -0.1236 | 0.068665 | 0.17853 | 0.13275 | -0.8194 | -0.15564 | 0.2243 | 0.30212 | 1.355 | 1.387 | 121.5363 | 122.4243 | 0.17853 | 122.58 | 11.142 | -0.15564 | 122.4243 | 0.17853 | 11.142 | 121.5363 | 122.58 | -122.4792 | -122.5113
4394.4688 | 122.374 | -0.082397 | 122.2687 | -0.15221 | 0.0098416 | -0.012978 | 0.010621 | 0.046055 | -0.015022 | 0.066262 | 0.059509 | 122.3511 | -0.21515 | 0.054932 | 121.4996 | 11.1877 | 1.6022 | 1.6296 | 122.4792 | -0.24261 | -0.13275 | 0.082397 | 0.14191 | 0.13733 | -0.76904 | -0.16022 | 0.21057 | 0.27466 | 1.6846 | 1.712 | 121.582 | 122.4335 | 0.14191 | 122.5616 | 11.2701 | -0.16022 | 122.4335 | 0.14191 | 11.2701 | 121.582 | 122.5616 | -122.4838 | -122.5113
4396.2188 | 122.3785 | -0.068665 | 122.2687 | -0.22087 | 0.010055 | -0.016823 | 0.012971 | 0.047978 | -0.011177 | 0.065193 | 0.054932 | 122.3511 | -0.2243 | 0.059509 | 121.4767 | 11.1923 | 1.6251 | 1.6159 | 122.4792 | -0.25635 | -0.15564 | 0.082397 | 0.1236 | 0.12817 | -0.79193 | -0.18768 | 0.21057 | 0.27924 | 1.6937 | 1.6846 | 121.5454 | 122.4197 | 0.1236 | 122.5479 | 11.261 | -0.18768 | 122.4197 | 0.1236 | 11.261 | 121.5454 | 122.5479 | -122.493 | -122.525
4397.9844 | 122.4609 | -0.054932 | 122.2366 | 0.12245 | 0.009628 | -0.011482 | 0.015962 | 0.047764 | -0.012458 | 0.06797 | 0.073242 | 122.3511 | -0.21973 | 0.041199 | 121.463 | 11.0092 | 1.1719 | 1.2131 | 122.5021 | -0.27008 | -0.16479 | 0.11444 | 0.12817 | 0.096131 | -0.77362 | -0.21515 | 0.2655 | 0.29297 | 1.2268 | 1.268 | 121.5179 | 122.406 | 0.12817 | 122.5571 | 11.0641 | -0.21515 | 122.406 | 0.12817 | 11.0641 | 121.5179 | 122.5571 | -122.4564 | -122.5067
4399.75 | 122.4609 | -0.041199 | 122.2321 | 0.02327 | 0.0094144 | -0.013191 | 0.0078442 | 0.047978 | -0.012886 | 0.066475 | 0.09613 | 122.3465 | -0.19226 | 0.086975 | 121.5363 | 11.1374 | 1.2909 | 1.474 | 122.4701 | -0.23346 | -0.15106 | 0.11444 | 0.13733 | 0.12817 | -0.6958 | -0.19226 | 0.23804 | 0.28839 | 1.3321 | 1.5152 | 121.5775 | 122.3877 | 0.13733 | 122.5113 | 11.1786 | -0.19226 | 122.3877 | 0.13733 | 11.1786 | 121.5775 | 122.5113 | -122.4243 | -122.4655
4401.5156 | 122.4518 | -0.068665 | 122.2321 | 0.11482 | 0.0089872 | -0.013832 | 0.015107 | 0.046055 | -0.010963 | 0.06797 | 0.07782 | 122.2961 | -0.21973 | 0.064087 | 121.4859 | 11.0504 | 1.0941 | 1.236 | 122.4701 | -0.26093 | -0.15106 | 0.064087 | 0.14649 | 0.13275 | -0.74616 | -0.19226 | 0.23804 | 0.29755 | 1.1627 | 1.3046 | 121.5546 | 122.3648 | 0.14649 | 122.5388 | 11.1191 | -0.19226 | 122.3648 | 0.14649 | 11.1191 | 121.5546 | 122.5388 | -122.4518 | -122.493
4403.2031 | 122.3923 | -0.086975 | 122.2641 | -0.2285 | 0.0083462 | -0.018745 | 0.012117 | 0.045628 | -0.012672 | 0.065621 | 0.068665 | 122.3511 | -0.20599 | 0.045776 | 121.4722 | 11.2106 | 1.6388 | 1.6251 | 122.4609 | -0.2655 | -0.11902 | 0.086975 | 0.15564 | 0.13275 | -0.79193 | -0.17853 | 0.19684 | 0.27466 | 1.7258 | 1.712 | 121.5591 | 122.438 | 0.15564 | 122.5479 | 11.2976 | -0.17853 | 122.438 | 0.15564 | 11.2976 | 121.5591 | 122.5479 | -122.4701 | -122.5296
4404.9688 | 122.4609 | -0.059509 | 122.2183 | 0.099564 | 0.010269 | -0.011696 | 0.014039 | 0.050114 | -0.012672 | 0.066902 | 0.064087 | 122.3694 | -0.21973 | 0.022888 | 121.4447 | 11.0596 | 1.2085 | 1.2131 | 122.4838 | -0.24719 | -0.16022 | 0.15106 | 0.1236 | 0.082397 | -0.77362 | -0.18768 | 0.2655 | 0.28381 | 1.268 | 1.2726 | 121.5042 | 122.4289 | 0.1236 | 122.5433 | 11.1191 | -0.18768 | 122.4289 | 0.1236 | 11.1191 | 121.5042 | 122.5433 | -122.4381 | -122.4655
4406.6875 | 122.4792 | -0.050354 | 122.2183 | 0.038529 | 0.0081326 | -0.012764 | 0.008485 | 0.04456 | -0.012886 | 0.065834 | 0.10071 | 122.287 | -0.1831 | 0.07782 | 121.5363 | 11.174 | 1.2634 | 1.442 | 122.4518 | -0.23346 | -0.13275 | 0.068664 | 0.15106 | 0.12817 | -0.68207 | -0.1831 | 0.23346 | 0.28381 | 1.3138 | 1.4923 | 121.5866 | 122.3373 | 0.15106 | 122.5021 | 11.2244 | -0.1831 | 122.3373 | 0.15106 | 11.2244 | 121.5866 | 122.5021 | -122.4014 | -122.4518
4408.4375 | 122.3511 | -0.086975 | 122.2595 | -0.19035 | 0.0083462 | -0.017677 | 0.010194 | 0.044346 | -0.012886 | 0.065193 | 0.17395 | 122.3419 | -0.16937 | 0.14648 | 121.5546 | 11.348 | 1.5335 | 1.7624 | 122.4335 | -0.23346 | -0.082398 | 0.082398 | 0.26092 | 0.23346 | -0.70496 | -0.14648 | 0.17395 | 0.34332 | 1.6205 | 1.8494 | 121.6415 | 122.4289 | 0.26092 | 122.5204 | 11.4349 | -0.14648 | 122.4289 | 0.26092 | 11.4349 | 121.6415 | 122.5204 | -122.4289 | -122.493
4410.1406 | 122.3465 | -0.10529 | 122.2412 | -0.053024 | 0.0087734 | -0.0084915 | 0.018739 | 0.046696 | -0.013313 | 0.066048 | 0.12817 | 122.3145 | -0.21515 | 0.091553 | 121.4905 | 11.2106 | 1.3275 | 1.4099 | 122.4792 | -0.25177 | -0.10986 | 0.073242 | 0.23346 | 0.19684 | -0.75073 | -0.14648 | 0.23804 | 0.34332 | 1.4328 | 1.5152 | 121.5958 | 122.4197 | 0.23346 | 122.5845 | 11.3159 | -0.14648 | 122.4197 | 0.23346 | 11.3159 | 121.5958 | 122.5845 | -122.4564 | -122.493
4411.9062 | 122.3602 | -0.064087 | 122.2733 | -0.15221 | 0.0083462 | -0.014687 | 0.0095532 | 0.045414 | -0.010963 | 0.064766 | 0.16937 | 122.319 | -0.17395 | 0.17395 | 121.6003 | 11.3525 | 1.3916 | 1.712 | 122.4289 | -0.2243 | -0.10986 | 0.045777 | 0.23346 | 0.23804 | -0.67291 | -0.16022 | 0.15564 | 0.34332 | 1.4557 | 1.7761 | 121.6644 | 122.3831 | 0.23346 | 122.493 | 11.4166 | -0.16022 | 122.3831 | 0.23346 | 11.4166 | 121.6644 | 122.493 | -122.4472 | -122.4976
4413.6562 | 122.3557 | -0.073242 | 122.2733 | -0.19035 | 0.009628 | -0.015327 | 0.014039 | 0.045628 | -0.013527 | 0.06733 | 0.091553 | 122.3648 | -0.20142 | 0.07782 | 121.4905 | 11.293 | 1.6022 | 1.6159 | 122.493 | -0.23346 | -0.12817 | 0.091553 | 0.16479 | 0.15106 | -0.78278 | -0.16022 | 0.21973 | 0.29297 | 1.6754 | 1.6891 | 121.5637 | 122.438 | 0.16479 | 122.5662 | 11.3663 | -0.16022 | 122.438 | 0.16479 | 11.3663 | 121.5637 | 122.5662 | -122.4747 | -122.5067
4415.3594 | 122.3282 | -0.073242 | 122.3236 | -0.22087 | 0.0081326 | -0.0102 | 0.0093396 | 0.045414 | -0.015449 | 0.065193 | 0.1831 | 122.3511 | -0.16479 | 0.15106 | 121.582 | 11.4075 | 1.5656 | 1.7624 | 122.4655 | -0.21515 | -0.091553 | 0.027466 | 0.25635 | 0.2243 | -0.74158 | -0.14191 | 0.14191 | 0.3479 | 1.6388 | 1.8356 | 121.6553 | 122.4243 | 0.25635 | 122.5388 | 11.4807 | -0.14191 | 122.4243 | 0.25635 | 11.4807 | 121.6553 | 122.5388 | -122.4884 | -122.5388
4417.125 | 122.4701 | -0.07782 | 122.2137 | 0.10719 | 0.011123 | -0.012123 | 0.017244 | 0.048832 | -0.012672 | 0.066902 | 0.068665 | 122.3328 | -0.21973 | 0.036621 | 121.4355 | 11.1282 | 1.2268 | 1.2314 | 122.4426 | -0.27008 | -0.14191 | 0.11902 | 0.14649 | 0.11444 | -0.7782 | -0.19226 | 0.22888 | 0.28839 | 1.3046 | 1.3092 | 121.5134 | 122.4106 | 0.14649 | 122.5204 | 11.2061 | -0.19226 | 122.4106 | 0.14649 | 11.2061 | 121.5134 | 122.5204 | -122.4335 | -122.4838
4418.8906 | 122.3145 | -0.11444 | 122.2778 | -0.091171 | 0.011123 | -0.014259 | 0.014894 | 0.046696 | -0.012886 | 0.065834 | 0.14648 | 122.3648 | -0.20599 | 0.11444 | 121.5271 | 11.3342 | 1.4236 | 1.5427 | 122.4518 | -0.22888 | -0.091553 | 0.086975 | 0.26093 | 0.22888 | -0.75073 | -0.11444 | 0.17395 | 0.35248 | 1.5381 | 1.6571 | 121.6415 | 122.4792 | 0.26093 | 122.5662 | 11.4487 | -0.11444 | 122.4792 | 0.26093 | 11.4487 | 121.6415 | 122.5662 | -122.4838 | -122.5067
4420.5938 | 122.4655 | -0.027466 | 122.2778 | -0.030136 | 0.0083462 | -0.013832 | 0.0072034 | 0.045628 | -0.012458 | 0.066048 | 0.13733 | 122.3145 | -0.18768 | 0.10071 | 121.55 | 11.3297 | 1.3367 | 1.6067 | 122.4426 | -0.21515 | -0.16022 | 0.036621 | 0.16479 | 0.12817 | -0.72784 | -0.18768 | 0.16479 | 0.32501 | 1.3641 | 1.6342 | 121.5775 | 122.3419 | 0.16479 | 122.4701 | 11.3571 | -0.18768 | 122.3419 | 0.16479 | 11.3571 | 121.5775 | 122.4701 | -122.4655 | -122.493
4422.375 | 122.406 | -0.09613 | 122.2183 | -0.0072479 | 0.009628 | -0.014473 | 0.01468 | 0.046055 | -0.01374 | 0.066048 | 0.10071 | 122.3145 | -0.23346 | 0.041199 | 121.4264 | 11.2061 | 1.3046 | 1.3046 | 122.4747 | -0.27008 | -0.13733 | 0.09613 | 0.19684 | 0.13733 | -0.79193 | -0.17395 | 0.25635 | 0.33417 | 1.4008 | 1.4008 | 121.5225 | 122.4106 | 0.19684 | 122.5708 | 11.3022 | -0.17395 | 122.4106 | 0.19684 | 11.3022 | 121.5225 | 122.5708 | -122.4518 | -122.4884
4424.1562 | 122.4243 | -0.059509 | 122.2778 | -0.098801 | 0.007919 | -0.012123 | 0.0086988 | 0.043919 | -0.012458 | 0.063271 | 0.16479 | 122.3328 | -0.19226 | 0.14648 | 121.582 | 11.4029 | 1.3779 | 1.6617 | 122.4106 | -0.22888 | -0.13275 | 0.054932 | 0.2243 | 0.20599 | -0.6958 | -0.16937 | 0.13275 | 0.35706 | 1.4374 | 1.7212 | 121.6415 | 122.3923 | 0.2243 | 122.4701 | 11.4624 | -0.16937 | 122.3923 | 0.2243 | 11.4624 | 121.6415 | 122.4701 | -122.4701 | -122.5067
4425.8438 | 122.4564 | -0.054932 | 122.2321 | 0.076676 | 0.0081326 | -0.010414 | 0.014253 | 0.046269 | -0.013313 | 0.065834 | 0.082397 | 122.3145 | -0.23804 | 0.041199 | 121.4264 | 11.2061 | 1.2634 | 1.2817 | 122.438 | -0.27466 | -0.1831 | 0.082397 | 0.13733 | 0.096131 | -0.80566 | -0.21973 | 0.20599 | 0.32043 | 1.3184 | 1.3367 | 121.4813 | 122.3694 | 0.13733 | 122.493 | 11.261 | -0.21973 | 122.3694 | 0.13733 | 11.261 | 121.4813 | 122.493 | -122.4701 | -122.5067
4427.6094 | 122.3282 | -0.10071 | 122.2412 | -0.091171 | 0.01091 | -0.015114 | 0.016603 | 0.047123 | -0.014167 | 0.064766 | 0.16022 | 122.2961 | -0.21973 | 0.10529 | 121.5042 | 11.3571 | 1.387 | 1.5015 | 122.4564 | -0.23804 | -0.11902 | 0.054932 | 0.26093 | 0.20599 | -0.737 | -0.13733 | 0.21515 | 0.37994 | 1.4877 | 1.6022 | 121.6049 | 122.3969 | 0.26093 | 122.5571 | 11.4578 | -0.13733 | 122.3969 | 0.26093 | 11.4578 | 121.6049 | 122.5571 | -122.4609 | -122.4792
4429.3125 | 122.4838 | -0.064087 | 122.2595 | -0.0072479 | 0.0094144 | -0.014259 | 0.005708 | 0.045628 | -0.010109 | 0.067757 | 0.13733 | 122.3373 | -0.1831 | 0.09613 | 121.5363 | 11.3342 | 1.3229 | 1.5015 | 122.4426 | -0.23804 | -0.11902 | 0.07782 | 0.20142 | 0.16022 | -0.72327 | -0.17395 | 0.18311 | 0.32043 | 1.387 | 1.5656 | 121.6003 | 122.4014 | 0.20142 | 122.5067 | 11.3983 | -0.17395 | 122.4014 | 0.20142 | 11.3983 | 121.6003 | 122.5067 | -122.4426 | -122.4976
4431.0781 | 122.3694 | -0.091553 | 122.2321 | 0.00038159 | 0.0087734 | -0.016609 | 0.018525 | 0.047978 | -0.015449 | 0.065834 | 0.15106 | 122.3007 | -0.22888 | 0.059509 | 121.431 | 11.3068 | 1.3733 | 1.3962 | 122.493 | -0.24719 | -0.13733 | 0.068664 | 0.24261 | 0.15106 | -0.80109 | -0.15564 | 0.26093 | 0.37994 | 1.4648 | 1.4877 | 121.5225 | 122.3923 | 0.24261 | 122.5845 | 11.3983 | -0.15564 | 122.3923 | 0.24261 | 11.3983 | 121.5225 | 122.5845 | -122.4609 | -122.4792
4432.7812 | 122.3236 | -0.10071 | 122.2549 | -0.091171 | 0.010055 | -0.0099869 | 0.015962 | 0.047978 | -0.015022 | 0.065621 | 0.17853 | 122.319 | -0.19226 | 0.11902 | 121.4996 | 11.3983 | 1.4145 | 1.5381 | 122.4701 | -0.25177 | -0.091553 | 0.064087 | 0.27924 | 0.21973 | -0.75531 | -0.15106 | 0.21515 | 0.37079 | 1.5152 | 1.6388 | 121.6003 | 122.4197 | 0.27924 | 122.5708 | 11.499 | -0.15106 | 122.4197 | 0.27924 | 11.499 | 121.6003 | 122.5708 | -122.4472 | -122.5067
4434.5312 | 122.4335 | -0.050354 | 122.2321 | 0.099564 | 0.011337 | -0.016396 | 0.0067762 | 0.049687 | -0.012886 | 0.066048 | 0.19684 | 122.3007 | -0.16937 | 0.11902 | 121.5271 | 11.3571 | 1.181 | 1.4511 | 122.438 | -0.21515 | -0.11902 | 0.068664 | 0.24719 | 0.16937 | -0.70496 | -0.16479 | 0.20599 | 0.36621 | 1.2314 | 1.5015 | 121.5775 | 122.3511 | 0.24719 | 122.4884 | 11.4075 | -0.16479 | 122.3511 | 0.24719 | 11.4075 | 121.5775 | 122.4884 | -122.4014 | -122.4472
4436.2969 | 122.4335 | -0.073242 | 122.2137 | 0.10719 | 0.009628 | -0.01255 | 0.011476 | 0.046269 | -0.01374 | 0.066475 | 0.22888 | 122.3007 | -0.18768 | 0.12817 | 121.5408 | 11.3663 | 1.1765 | 1.4603 | 122.4747 | -0.21973 | -0.11444 | 0.086975 | 0.30212 | 0.20142 | -0.67291 | -0.14649 | 0.26093 | 0.41656 | 1.2497 | 1.5335 | 121.6141 | 122.374 | 0.30212 | 122.5479 | 11.4395 | -0.14649 | 122.374 | 0.30212 | 11.4395 | 121.6141 | 122.5479 | -122.4014 | -122.4335
4438.0625 | 122.4243 | -0.091553 | 122.2321 | 0.030899 | 0.01091 | -0.011482 | 0.013826 | 0.046696 | -0.013099 | 0.066262 | 0.1236 | 122.3236 | -0.21973 | 0.041199 | 121.431 | 11.3205 | 1.3687 | 1.3412 | 122.4472 | -0.26093 | -0.12817 | 0.091552 | 0.21515 | 0.13275 | -0.80109 | -0.16937 | 0.21515 | 0.34332 | 1.4603 | 1.4328 | 121.5225 | 122.4152 | 0.21515 | 122.5388 | 11.412 | -0.16937 | 122.4152 | 0.21515 | 11.412 | 121.5225 | 122.5388 | -122.4518 | -122.493
4439.8125 | 122.4335 | -0.068665 | 122.2183 | 0.10719 | 0.010055 | -0.015755 | 0.017671 | 0.048619 | -0.01609 | 0.066689 | 0.13733 | 122.3145 | -0.23346 | 0.032043 | 121.4539 | 11.3113 | 1.3138 | 1.3138 | 122.4609 | -0.25177 | -0.16479 | 0.09613 | 0.20599 | 0.10071 | -0.76447 | -0.1831 | 0.24261 | 0.37079 | 1.3824 | 1.3824 | 121.5225 | 122.3831 | 0.20599 | 122.5296 | 11.38 | -0.1831 | 122.3831 | 0.20599 | 11.38 | 121.5225 | 122.5296 | -122.4518 | -122.4701
4441.5156 | 122.4289 | -0.07782 | 122.2458 | 0.14534 | 0.0089872 | -0.013832 | 0.013185 | 0.047978 | -0.013954 | 0.066048 | 0.22888 | 122.287 | -0.16479 | 0.15106 | 121.5729 | 11.4212 | 1.0941 | 1.4465 | 122.438 | -0.19684 | -0.086975 | 0.041198 | 0.3067 | 0.22888 | -0.67291 | -0.11902 | 0.19226 | 0.39368 | 1.1719 | 1.5244 | 121.6507 | 122.3648 | 0.3067 | 122.5159 | 11.499 | -0.11902 | 122.3648 | 0.3067 | 11.499 | 121.6507 | 122.5159 | -122.4106 | -122.4426
4443.2812 | 122.4197 | -0.054932 | 122.2733 | -0.098801 | 0.00621 | -0.015114 | 0.007417 | 0.043278 | -0.012672 | 0.06733 | 0.20142 | 122.319 | -0.1831 | 0.13733 | 121.5729 | 11.5128 | 1.3824 | 1.6663 | 122.4426 | -0.2243 | -0.12817 | 0.045777 | 0.25635 | 0.19226 | -0.70038 | -0.16937 | 0.16937 | 0.38452 | 1.4374 | 1.7212 | 121.6278 | 122.374 | 0.25635 | 122.4976 | 11.5677 | -0.16937 | 122.374 | 0.25635 | 11.5677 | 121.6278 | 122.4976 | -122.4564 | -122.4976
4444.9844 | 122.4838 | -0.041199 | 122.2275 | 0.030899 | 0.010482 | -0.015755 | 0.0097668 | 0.046696 | -0.011604 | 0.066262 | 0.20599 | 122.2916 | -0.19226 | 0.10071 | 121.5179 | 11.4166 | 1.2772 | 1.4694 | 122.4472 | -0.23346 | -0.15106 | 0.064087 | 0.24719 | 0.14191 | -0.70953 | -0.19226 | 0.21973 | 0.39826 | 1.3184 | 1.5106 | 121.5591 | 122.3328 | 0.24719 | 122.4884 | 11.4578 | -0.19226 | 122.3328 | 0.24719 | 11.4578 | 121.5591 | 122.4884 | -122.4197 | -122.4609
4446.75 | 122.4609 | -0.054932 | 122.1954 | 0.13771 | 0.009628 | -0.013832 | 0.016603 | 0.046482 | -0.015022 | 0.066262 | 0.14191 | 122.319 | -0.21515 | 0.041199 | 121.431 | 11.348 | 1.3046 | 1.3138 | 122.4792 | -0.25177 | -0.16022 | 0.1236 | 0.19684 | 0.096131 | -0.76447 | -0.19684 | 0.28381 | 0.35706 | 1.3596 | 1.3687 | 121.4859 | 122.374 | 0.19684 | 122.5342 | 11.4029 | -0.19684 | 122.374 | 0.19684 | 11.4029 | 121.4859 | 122.5342 | -122.4106 | -122.4472
4448.4531 | 122.4014 | -0.07782 | 122.2549 | 0.17586 | 0.011123 | -0.013191 | 0.010835 | 0.048191 | -0.012886 | 0.066262 | 0.25177 | 122.2733 | -0.17395 | 0.16937 | 121.55 | 11.4716 | 1.1307 | 1.4603 | 122.4426 | -0.20599 | -0.09613 | 0.01831 | 0.32959 | 0.24719 | -0.70496 | -0.12817 | 0.18768 | 0.42572 | 1.2085 | 1.5381 | 121.6278 | 122.3511 | 0.32959 | 122.5204 | 11.5494 | -0.12817 | 122.3511 | 0.32959 | 11.5494 | 121.6278 | 122.5204 | -122.4289 | -122.4609
4450.2031 | 122.3602 | -0.082397 | 122.2595 | -0.23613 | 0.011123 | -0.015114 | 0.011049 | 0.04456 | -0.013313 | 0.064339 | 0.24261 | 122.3053 | -0.19226 | 0.11902 | 121.5271 | 11.5677 | 1.593 | 1.7258 | 122.4564 | -0.23346 | -0.10986 | 0.045777 | 0.32501 | 0.20142 | -0.73242 | -0.15106 | 0.19684 | 0.43488 | 1.6754 | 1.8082 | 121.6095 | 122.3877 | 0.32501 | 122.5388 | 11.6501 | -0.15106 | 122.3877 | 0.32501 | 11.6501 | 121.6095 | 122.5388 | -122.4518 | -122.493
4451.9844 | 122.3648 | -0.07782 | 122.2595 | -0.17509 | 0.010055 | -0.012123 | 0.018312 | 0.047337 | -0.014808 | 0.065407 | 0.16479 | 122.3145 | -0.23346 | 0.068665 | 121.4722 | 11.5082 | 1.6159 | 1.6205 | 122.4884 | -0.24261 | -0.15564 | 0.054932 | 0.24261 | 0.14649 | -0.78735 | -0.16479 | 0.22888 | 0.39825 | 1.6937 | 1.6983 | 121.55 | 122.3923 | 0.24261 | 122.5662 | 11.586 | -0.16479 | 122.3923 | 0.24261 | 11.586 | 121.55 | 122.5662 | -122.493 | -122.5021
4453.7031 | 122.3511 | -0.073242 | 122.2504 | -0.0072479 | 0.011978 | -0.011909 | 0.015962 | 0.04755 | -0.012672 | 0.066902 | 0.19226 | 122.319 | -0.21057 | 0.059509 | 121.4584 | 11.4395 | 1.3962 | 1.4236 | 122.4655 | -0.25635 | -0.13733 | 0.068665 | 0.2655 | 0.13275 | -0.79193 | -0.18311 | 0.21515 | 0.40283 | 1.4694 | 1.4969 | 121.5317 | 122.3923 | 0.2655 | 122.5388 | 11.5128 | -0.18311 | 122.3923 | 0.2655 | 11.5128 | 121.5317 | 122.5388 | -122.4609 | -122.5067
4455.4688 | 122.4106 | -0.064087 | 122.2275 | 0.1606 | 0.0066372 | -0.011909 | 0.010408 | 0.049046 | -0.012672 | 0.066902 | 0.27008 | 122.2961 | -0.19684 | 0.14191 | 121.5546 | 11.5036 | 1.1307 | 1.4786 | 122.4106 | -0.21515 | -0.13275 | 0.068665 | 0.33417 | 0.20599 | -0.67291 | -0.15106 | 0.1831 | 0.46692 | 1.1948 | 1.5427 | 121.6187 | 122.3602 | 0.33417 | 122.4747 | 11.5677 | -0.15106 | 122.3602 | 0.33417 | 11.5677 | 121.6187 | 122.4747 | -122.4243 | -122.4426
4457.1719 | 122.3648 | -0.07782 | 122.2412 | -0.19798 | 0.010269 | -0.013191 | 0.014467 | 0.047123 | -0.014808 | 0.065193 | 0.17395 | 122.3053 | -0.21973 | 0.064087 | 121.4539 | 11.5448 | 1.6434 | 1.6342 | 122.493 | -0.26093 | -0.14191 | 0.064087 | 0.25177 | 0.14191 | -0.78735 | -0.18311 | 0.25177 | 0.39368 | 1.7212 | 1.712 | 121.5317 | 122.3831 | 0.25177 | 122.5708 | 11.6226 | -0.18311 | 122.3831 | 0.25177 | 11.6226 | 121.5317 | 122.5708 | -122.4609 | -122.5021
4458.9375 | 122.3282 | -0.10986 | 122.2595 | -0.20561 | 0.010055 | -0.012978 | 0.010194 | 0.048405 | -0.013099 | 0.06498 | 0.29755 | 122.3282 | -0.1831 | 0.15564 | 121.5683 | 11.6638 | 1.4969 | 1.7761 | 122.406 | -0.21515 | -0.073242 | 0.068665 | 0.40741 | 0.2655 | -0.69122 | -0.10529 | 0.14648 | 0.48065 | 1.6068 | 1.886 | 121.6782 | 122.438 | 0.40741 | 122.5159 | 11.7737 | -0.10529 | 122.438 | 0.40741 | 11.7737 | 121.6782 | 122.5159 | -122.4426 | -122.4747
4460.7031 | 122.3602 | -0.059509 | 122.2687 | -0.24376 | 0.011337 | -0.0093461 | 0.013826 | 0.046696 | -0.014808 | 0.066262 | 0.16937 | 122.3145 | -0.23346 | 0.050354 | 121.4584 | 11.5768 | 1.6891 | 1.6434 | 122.5021 | -0.24719 | -0.17395 | 0.045776 | 0.22888 | 0.10986 | -0.81024 | -0.18768 | 0.23346 | 0.40283 | 1.7487 | 1.7029 | 121.5179 | 122.374 | 0.22888 | 122.5616 | 11.6364 | -0.18768 | 122.374 | 0.22888 | 11.6364 | 121.5179 | 122.5616 | -122.5021 | -122.5159
4462.4062 | 122.3511 | -0.091553 | 122.2549 | -0.25902 | 0.0092008 | -0.014473 | 0.010194 | 0.046482 | -0.013099 | 0.066902 | 0.27008 | 122.3099 | -0.19684 | 0.10529 | 121.5271 | 11.6501 | 1.6205 | 1.7258 | 122.4609 | -0.24261 | -0.10529 | 0.054931 | 0.36163 | 0.19684 | -0.72784 | -0.15106 | 0.20599 | 0.46692 | 1.712 | 1.8173 | 121.6187 | 122.4014 | 0.36163 | 122.5525 | 11.7416 | -0.15106 | 122.4014 | 0.36163 | 11.7416 | 121.6187 | 122.5525 | -122.4518 | -122.4976
4464.1719 | 122.319 | -0.10529 | 122.2641 | -0.13695 | 0.0089872 | -0.01255 | 0.010408 | 0.046696 | -0.01075 | 0.064553 | 0.31128 | 122.2687 | -0.17853 | 0.16479 | 121.6003 | 11.6821 | 1.4465 | 1.7487 | 122.4472 | -0.21057 | -0.073242 | 0.004578 | 0.41656 | 0.27008 | -0.66376 | -0.10529 | 0.18311 | 0.48981 | 1.5518 | 1.8539 | 121.7056 | 122.374 | 0.41656 | 122.5525 | 11.7874 | -0.10529 | 122.374 | 0.41656 | 11.7874 | 121.7056 | 122.5525 | -122.4426 | -122.4747
4465.8906 | 122.438 | -0.09613 | 122.2137 | 0.053787 | 0.010055 | -0.015755 | 0.018312 | 0.047978 | -0.015449 | 0.065193 | 0.19684 | 122.3236 | -0.21973 | 0.032043 | 121.4127 | 11.4624 | 1.3962 | 1.3641 | 122.493 | -0.25177 | -0.1236 | 0.10986 | 0.29297 | 0.12817 | -0.80109 | -0.15564 | 0.27924 | 0.41657 | 1.4923 | 1.4603 | 121.5088 | 122.4197 | 0.29297 | 122.5891 | 11.5585 | -0.15564 | 122.4197 | 0.29297 | 11.5585 | 121.5088 | 122.5891 | -122.4335 | -122.4655
4467.6562 | 122.374 | -0.086975 | 122.2412 | -0.26665 | 0.011337 | -0.0149 | 0.012544 | 0.04456 | -0.013954 | 0.066689 | 0.19684 | 122.3602 | -0.22888 | 0.041199 | 121.463 | 11.5906 | 1.6708 | 1.6388 | 122.4655 | -0.2655 | -0.14191 | 0.11902 | 0.28381 | 0.12817 | -0.7782 | -0.17853 | 0.2243 | 0.42572 | 1.7578 | 1.7258 | 121.55 | 122.4472 | 0.28381 | 122.5525 | 11.6776 | -0.17853 | 122.4472 | 0.28381 | 11.6776 | 121.55 | 122.5525 | -122.4701 | -122.5067
4469.4219 | 122.3236 | -0.082397 | 122.2549 | -0.18272 | 0.0083462 | -0.018959 | 0.014467 | 0.047337 | -0.015236 | 0.067757 | 0.23346 | 122.3236 | -0.22888 | 0.07782 | 121.4813 | 11.6318 | 1.6067 | 1.6388 | 122.4701 | -0.25635 | -0.14649 | 0.068664 | 0.31586 | 0.16022 | -0.77362 | -0.17395 | 0.21515 | 0.46234 | 1.6891 | 1.7212 | 121.5637 | 122.406 | 0.31586 | 122.5525 | 11.7142 | -0.17395 | 122.406 | 0.31586 | 11.7142 | 121.5637 | 122.5525 | -122.4838 | -122.5113
4471.1875 | 122.3557 | -0.091553 | 122.2687 | -0.12932 | 0.010482 | -0.013191 | 0.0065624 | 0.046482 | -0.010536 | 0.064553 | 0.33875 | 122.3328 | -0.16479 | 0.15564 | 121.5912 | 11.7142 | 1.4236 | 1.7578 | 122.4152 | -0.23346 | -0.073242 | 0.064087 | 0.4303 | 0.24719 | -0.67749 | -0.14191 | 0.14648 | 0.50354 | 1.5152 | 1.8494 | 121.6827 | 122.4243 | 0.4303 | 122.5067 | 11.8057 | -0.14191 | 122.4243 | 0.4303 | 11.8057 | 121.6827 | 122.5067 | -122.4335 | -122.5021
4472.8906 | 122.3557 | -0.086975 | 122.2458 | -0.27428 | 0.011551 | -0.01255 | 0.01233 | 0.046482 | -0.014167 | 0.065621 | 0.24261 | 122.3511 | -0.2243 | 0.045776 | 121.4493 | 11.6135 | 1.6983 | 1.6434 | 122.493 | -0.27008 | -0.13733 | 0.10528 | 0.32959 | 0.13275 | -0.79651 | -0.18311 | 0.24719 | 0.46692 | 1.7853 | 1.7303 | 121.5363 | 122.438 | 0.32959 | 122.58 | 11.7004 | -0.18311 | 122.438 | 0.32959 | 11.7004 | 121.5363 | 122.58 | -122.4701 | -122.5159
4474.6562 | 122.3419 | -0.082397 | 122.2366 | -0.083542 | 0.010696 | -0.011696 | 0.016603 | 0.049046 | -0.016304 | 0.066475 | 0.29755 | 122.3099 | -0.20599 | 0.09613 | 121.4722 | 11.6318 | 1.442 | 1.5427 | 122.4472 | -0.24719 | -0.1236 | 0.073242 | 0.37994 | 0.17853 | -0.76447 | -0.16479 | 0.21057 | 0.50354 | 1.5244 | 1.6251 | 121.5546 | 122.3923 | 0.37994 | 122.5296 | 11.7142 | -0.16479 | 122.3923 | 0.37994 | 11.7142 | 121.5546 | 122.5296 | -122.4426 | -122.4838
4476.4219 | 122.4701 | -0.064087 | 122.2321 | 0.0080111 | 0.0085598 | -0.016823 | 0.0061352 | 0.04691 | -0.012886 | 0.06797 | 0.27466 | 122.2778 | -0.18768 | 0.082397 | 121.5225 | 11.6135 | 1.3641 | 1.5472 | 122.4655 | -0.21973 | -0.1236 | 0.045776 | 0.33875 | 0.14648 | -0.70953 | -0.15564 | 0.23346 | 0.46234 | 1.4282 | 1.6113 | 121.5866 | 122.3419 | 0.33875 | 122.5296 | 11.6776 | -0.15564 | 122.3419 | 0.33875 | 11.6776 | 121.5866 | 122.5296 | -122.4197 | -122.4518
4478.125 | 122.4197 | -0.073242 | 122.2412 | 0.13008 | 0.0087734 | -0.0099869 | 0.010621 | 0.047764 | -0.011818 | 0.065834 | 0.37079 | 122.3007 | -0.16937 | 0.13275 | 121.5454 | 11.6226 | 1.1765 | 1.4877 | 122.406 | -0.23804 | -0.096131 | 0.059509 | 0.44403 | 0.20599 | -0.6958 | -0.16479 | 0.16479 | 0.54016 | 1.2497 | 1.561 | 121.6187 | 122.374 | 0.44403 | 122.4792 | 11.6959 | -0.16479 | 122.374 | 0.44403 | 11.6959 | 121.6187 | 122.4792 | -122.4106 | -122.4792
4479.8906 | 122.4014 | -0.068665 | 122.2366 | -0.12169 | 0.012191 | -0.012764 | 0.0097668 | 0.045628 | -0.012672 | 0.062416 | 0.36163 | 122.3099 | -0.18768 | 0.17395 | 121.582 | 11.7462 | 1.4374 | 1.7349 | 122.4564 | -0.23346 | -0.11902 | 0.073242 | 0.4303 | 0.24261 | -0.6546 | -0.16479 | 0.21973 | 0.54932 | 1.506 | 1.8036 | 121.6507 | 122.3785 | 0.4303 | 122.525 | 11.8149 | -0.16479 | 122.3785 | 0.4303 | 11.8149 | 121.6507 | 122.525 | -122.4243 | -122.4701
4481.5938 | 122.3969 | -0.050354 | 122.2321 | 0.12245 | 0.011337 | -0.015755 | 0.014467 | 0.048191 | -0.011177 | 0.066048 | 0.38452 | 122.2916 | -0.17395 | 0.14648 | 121.5271 | 11.6409 | 1.1581 | 1.4557 | 122.406 | -0.21973 | -0.1236 | 0.059509 | 0.43488 | 0.19684 | -0.70496 | -0.16937 | 0.17395 | 0.55847 | 1.2085 | 1.506 | 121.5775 | 122.3419 | 0.43488 | 122.4564 | 11.6913 | -0.16937 | 122.3419 | 0.43488 | 11.6913 | 121.5775 | 122.4564 | -122.406 | -122.4518
4483.375 | 122.4014 | -0.059509 | 122.2229 | -0.12169 | 0.0074918 | -0.013191 | 0.012117 | 0.044773 | -0.012672 | 0.065193 | 0.37994 | 122.319 | -0.17395 | 0.16479 | 121.5729 | 11.7554 | 1.4328 | 1.7349 | 122.406 | -0.24719 | -0.11444 | 0.096131 | 0.43945 | 0.2243 | -0.65002 | -0.18768 | 0.18311 | 0.55389 | 1.4923 | 1.7944 | 121.6324 | 122.3785 | 0.43945 | 122.4655 | 11.8149 | -0.18768 | 122.3785 | 0.43945 | 11.8149 | 121.6324 | 122.4655 | -122.3969 | -122.4701
4485.0625 | 122.406 | -0.064087 | 122.2046 | 0.18349 | 0.010482 | -0.0099869 | 0.016389 | 0.047978 | -0.01609 | 0.068398 | 0.36163 | 122.3053 | -0.21057 | 0.13275 | 121.5134 | 11.6226 | 1.1948 | 1.442 | 122.438 | -0.21973 | -0.14648 | 0.10071 | 0.42572 | 0.19684 | -0.69122 | -0.15564 | 0.23346 | 0.5722 | 1.2589 | 1.506 | 121.5775 | 122.3694 | 0.42572 | 122.5021 | 11.6867 | -0.15564 | 122.3694 | 0.42572 | 11.6867 | 121.5775 | 122.5021 | -122.4152 | -122.4243
4486.8281 | 122.3648 | -0.091553 | 122.2412 | -0.15221 | 0.0098416 | -0.015541 | 0.010408 | 0.046482 | -0.012886 | 0.067757 | 0.4303 | 122.287 | -0.17853 | 0.17853 | 121.5866 | 11.7874 | 1.4374 | 1.7578 | 122.4335 | -0.20599 | -0.086975 | 0.045776 | 0.52185 | 0.27008 | -0.6546 | -0.11444 | 0.19226 | 0.60883 | 1.5289 | 1.8494 | 121.6782 | 122.3785 | 0.52185 | 122.525 | 11.879 | -0.11444 | 122.3785 | 0.52185 | 11.879 | 121.6782 | 122.525 | -122.4197 | -122.4472
4488.6094 | 122.3923 | -0.07782 | 122.2412 | 0.030899 | 0.011337 | -0.012978 | 0.017884 | 0.0499 | -0.015236 | 0.067543 | 0.33875 | 122.2916 | -0.21515 | 0.050354 | 121.4218 | 11.5952 | 1.4191 | 1.4145 | 122.4518 | -0.25635 | -0.13733 | 0.050354 | 0.41657 | 0.12817 | -0.8194 | -0.17853 | 0.21057 | 0.55389 | 1.4969 | 1.4923 | 121.4996 | 122.3694 | 0.41657 | 122.5296 | 11.673 | -0.17853 | 122.3694 | 0.41657 | 11.673 | 121.4996 | 122.5296 | -122.4564 | -122.4976
4490.3125 | 122.4609 | -0.054932 | 122.2 | 0.076676 | 0.01091 | -0.0069961 | 0.0089124 | 0.047123 | -0.012031 | 0.065193 | 0.40741 | 122.3007 | -0.16479 | 0.10071 | 121.5179 | 11.6638 | 1.2955 | 1.5106 | 122.4289 | -0.23804 | -0.10986 | 0.10071 | 0.46234 | 0.15564 | -0.68207 | -0.1831 | 0.22888 | 0.5722 | 1.3504 | 1.5656 | 121.5729 | 122.3557 | 0.46234 | 122.4838 | 11.7188 | -0.1831 | 122.3557 | 0.46234 | 11.7188 | 121.5729 | 122.4838 | -122.3648 | -122.438
4492.0938 | 122.4014 | -0.073242 | 122.2275 | 0.1606 | 0.011337 | -0.015327 | 0.01468 | 0.048619 | -0.011818 | 0.065407 | 0.49439 | 122.287 | -0.16022 | 0.16937 | 121.5454 | 11.6959 | 1.1353 | 1.474 | 122.4426 | -0.21057 | -0.086975 | 0.059509 | 0.56763 | 0.24261 | -0.68207 | -0.13733 | 0.21515 | 0.6546 | 1.2085 | 1.5472 | 121.6187 | 122.3602 | 0.56763 | 122.5159 | 11.7691 | -0.13733 | 122.3602 | 0.56763 | 11.7691 | 121.6187 | 122.5159 | -122.3877 | -122.438
4493.875 | 122.4335 | -0.036621 | 122.2137 | 0.099564 | 0.01326 | -0.015327 | 0.016603 | 0.049687 | -0.01374 | 0.066689 | 0.39825 | 122.3328 | -0.21515 | 0.050354 | 121.4218 | 11.5997 | 1.3596 | 1.3596 | 122.4655 | -0.26093 | -0.17853 | 0.11902 | 0.43488 | 0.086975 | -0.79193 | -0.2243 | 0.25177 | 0.6134 | 1.3962 | 1.3962 | 121.4584 | 122.3694 | 0.43488 | 122.5021 | 11.6364 | -0.2243 | 122.3694 | 0.43488 | 11.6364 | 121.4584 | 122.5021 | -122.4289 | -122.4747
4495.5781 | 122.4472 | -0.059509 | 122.2046 | 0.00038159 | 0.013046 | -0.013832 | 0.0099804 | 0.047764 | -0.011604 | 0.066689 | 0.43488 | 122.319 | -0.19226 | 0.09613 | 121.5134 | 11.6959 | 1.3962 | 1.5747 | 122.4106 | -0.22888 | -0.13275 | 0.11444 | 0.49438 | 0.15564 | -0.69122 | -0.16937 | 0.20599 | 0.62714 | 1.4557 | 1.6342 | 121.5729 | 122.3785 | 0.49438 | 122.4701 | 11.7554 | -0.16937 | 122.3785 | 0.49438 | 11.7554 | 121.5729 | 122.4701 | -122.3969 | -122.4335
4497.3438 | 122.319 | -0.10529 | 122.2687 | -0.17509 | 0.0092008 | -0.015968 | 0.0099804 | 0.046269 | -0.014381 | 0.06498 | 0.52643 | 122.3099 | -0.18768 | 0.18768 | 121.5683 | 11.8423 | 1.4969 | 1.8036 | 122.4197 | -0.2243 | -0.082397 | 0.041198 | 0.63171 | 0.29297 | -0.70038 | -0.11902 | 0.15106 | 0.71411 | 1.6022 | 1.9089 | 121.6736 | 122.4152 | 0.63171 | 122.525 | 11.9476 | -0.11902 | 122.4152 | 0.63171 | 11.9476 | 121.6736 | 122.525 | -122.4564 | -122.493
4499.125 | 122.3419 | -0.09613 | 122.2504 | -0.19798 | 0.011123 | -0.011482 | 0.016176 | 0.047978 | -0.014595 | 0.064766 | 0.44861 | 122.3419 | -0.22888 | 0.091553 | 121.4722 | 11.7828 | 1.6205 | 1.6571 | 122.4564 | -0.27008 | -0.13275 | 0.091553 | 0.54474 | 0.18768 | -0.7782 | -0.17395 | 0.20599 | 0.67749 | 1.7166 | 1.7532 | 121.5683 | 122.438 | 0.54474 | 122.5525 | 11.879 | -0.17395 | 122.438 | 0.54474 | 11.879 | 121.5683 | 122.5525 | -122.4792 | -122.5204
4500.8281 | 122.4518 | -0.054932 | 122.2229 | 0.030899 | 0.013687 | -0.014473 | 0.010835 | 0.044773 | -0.012458 | 0.066262 | 0.50812 | 122.3099 | -0.19684 | 0.11902 | 121.5134 | 11.705 | 1.3687 | 1.561 | 122.438 | -0.22888 | -0.14191 | 0.086975 | 0.56305 | 0.17395 | -0.70953 | -0.17395 | 0.21515 | 0.70496 | 1.4236 | 1.6159 | 121.5683 | 122.3648 | 0.56305 | 122.493 | 11.7599 | -0.17395 | 122.3648 | 0.56305 | 11.7599 | 121.5683 | 122.493 | -122.4197 | -122.4518
4502.5938 | 122.3511 | -0.11444 | 122.2641 | -0.26665 | 0.011764 | -0.017036 | 0.011049 | 0.043278 | -0.012886 | 0.066689 | 0.54016 | 122.2961 | -0.19684 | 0.10986 | 121.4905 | 11.8332 | 1.6663 | 1.7578 | 122.4289 | -0.2655 | -0.082397 | 0.032044 | 0.6546 | 0.2243 | -0.77362 | -0.15106 | 0.16479 | 0.737 | 1.7807 | 1.8723 | 121.6049 | 122.4106 | 0.6546 | 122.5433 | 11.9476 | -0.15106 | 122.4106 | 0.6546 | 11.9476 | 121.6049 | 122.5433 | -122.4609 | -122.5296
4504.3438 | 122.319 | -0.10071 | 122.2321 | -0.083542 | 0.011978 | -0.0095597 | 0.017457 | 0.044987 | -0.015663 | 0.067757 | 0.58136 | 122.3007 | -0.21515 | 0.10986 | 121.4722 | 11.7645 | 1.4648 | 1.5656 | 122.4426 | -0.25635 | -0.11444 | 0.068664 | 0.68207 | 0.21057 | -0.75989 | -0.15564 | 0.21057 | 0.79651 | 1.5656 | 1.6663 | 121.5729 | 122.4014 | 0.68207 | 122.5433 | 11.8652 | -0.15564 | 122.4014 | 0.68207 | 11.8652 | 121.5729 | 122.5433 | -122.4472 | -122.4884
4506.1094 | 122.3236 | -0.10071 | 122.2366 | -0.068283 | 0.011123 | -0.0097733 | 0.017884 | 0.048619 | -0.015449 | 0.068611 | 0.58136 | 122.2961 | -0.23804 | 0.10529 | 121.4676 | 11.7691 | 1.4694 | 1.5381 | 122.4518 | -0.26093 | -0.13733 | 0.05951 | 0.68207 | 0.20599 | -0.76904 | -0.16022 | 0.21515 | 0.8194 | 1.5701 | 1.6388 | 121.5683 | 122.3969 | 0.68207 | 122.5525 | 11.8698 | -0.16022 | 122.3969 | 0.68207 | 11.8698 | 121.5683 | 122.5525 | -122.4747 | -122.4976
4507.875 | 122.3328 | -0.10529 | 122.2321 | -0.068283 | 0.011551 | -0.0080643 | 0.014467 | 0.046696 | -0.012672 | 0.066262 | 0.59509 | 122.3145 | -0.21515 | 0.086975 | 121.4676 | 11.7416 | 1.4557 | 1.5244 | 122.4289 | -0.25177 | -0.10986 | 0.082397 | 0.70038 | 0.19226 | -0.76447 | -0.14648 | 0.19684 | 0.81024 | 1.561 | 1.6296 | 121.5729 | 122.4197 | 0.70038 | 122.5342 | 11.8469 | -0.14648 | 122.4197 | 0.70038 | 11.8469 | 121.5729 | 122.5342 | -122.4472 | -122.4838
4509.6406 | 122.3557 | -0.09613 | 122.2321 | -0.19035 | 0.013046 | -0.012764 | 0.010621 | 0.046696 | -0.013099 | 0.067757 | 0.56763 | 122.3557 | -0.2243 | 0.059509 | 121.4539 | 11.7874 | 1.6937 | 1.6663 | 122.4609 | -0.27008 | -0.12817 | 0.1236 | 0.66376 | 0.15564 | -0.7782 | -0.17395 | 0.22888 | 0.79193 | 1.7899 | 1.7624 | 121.55 | 122.4518 | 0.66376 | 122.5571 | 11.8835 | -0.17395 | 122.4518 | 0.66376 | 11.8835 | 121.55 | 122.5571 | -122.4564 | -122.5021
4511.4062 | 122.4426 | -0.064087 | 122.2183 | 0.046158 | 0.011764 | -0.010628 | 0.0069898 | 0.046696 | -0.012245 | 0.066262 | 0.64545 | 122.2824 | -0.20599 | 0.086975 | 121.5042 | 11.7371 | 1.355 | 1.5564 | 122.4243 | -0.23346 | -0.14191 | 0.064087 | 0.70953 | 0.15106 | -0.71411 | -0.16937 | 0.20599 | 0.85144 | 1.4191 | 1.6205 | 121.5683 | 122.3465 | 0.70953 | 122.4884 | 11.8011 | -0.16937 | 122.3465 | 0.70953 | 11.8011 | 121.5683 | 122.4884 | -122.4243 | -122.4518
4513.1719 | 122.3007 | -0.10986 | 122.2275 | -0.083542 | 0.011551 | -0.010628 | 0.017457 | 0.047978 | -0.015022 | 0.066048 | 0.6958 | 122.3007 | -0.23346 | 0.09613 | 121.4767 | 11.7874 | 1.4923 | 1.5884 | 122.4426 | -0.24719 | -0.1236 | 0.073242 | 0.80566 | 0.20599 | -0.75073 | -0.13733 | 0.21515 | 0.92926 | 1.6022 | 1.6983 | 121.5866 | 122.4106 | 0.80566 | 122.5525 | 11.8973 | -0.13733 | 122.4106 | 0.80566 | 11.8973 | 121.5866 | 122.5525 | -122.4609 | -122.4747
4514.875 | 122.1222 | -0.39825 | 121.7514 | -0.14458 | 0.012405 | -0.015327 | 0.0099804 | 0.045201 | -0.0094678 | 0.066262 | 0.43488 | 121.8018 | -0.49439 | -0.13733 | 121.0602 | 11.8103 | 1.4511 | 1.7853 | 121.9025 | -0.54932 | -0.096131 | 0.050354 | 0.83313 | 0.26092 | -0.69122 | -0.15106 | 0.15106 | 0.92926 | 1.8494 | 2.1835 | 121.4584 | 122.2 | 0.83313 | 122.3007 | 12.2086 | -0.15106 | 122.2 | 0.83313 | 12.2086 | 121.4584 | 122.3007 | -122.2458 | -122.3007
4516.6406 | 122.1542 | -0.07782 | 122.0444 | -0.17509 | 0.012619 | -0.015755 | 0.013185 | 0.045628 | -0.01139 | 0.06498 | 0.70038 | 122.1313 | -0.21515 | 0.064087 | 121.2387 | 11.7874 | 1.7349 | 1.6983 | 122.3007 | -0.25635 | -0.13733 | 0.086975 | 0.7782 | 0.14191 | -0.80566 | -0.17853 | 0.25635 | 0.91553 | 1.8127 | 1.7761 | 121.3165 | 122.2092 | 0.7782 | 122.3785 | 11.8652 | -0.17853 | 122.2092 | 0.7782 | 11.8652 | 121.3165 | 122.3785 | -122.2595 | -122.3007
4518.4062 | 122.2916 | -0.054932 | 122.0398 | 0.084305 | 0.011123 | -0.0095597 | 0.0099804 | 0.046482 | -0.01374 | 0.064553 | 0.77362 | 122.1268 | -0.19226 | 0.10986 | 121.3531 | 11.7279 | 1.3412 | 1.5518 | 122.3007 | -0.23346 | -0.13733 | 0.086975 | 0.82855 | 0.16479 | -0.68665 | -0.17853 | 0.26093 | 0.96588 | 1.3962 | 1.6068 | 121.4081 | 122.1817 | 0.82855 | 122.3557 | 11.7828 | -0.17853 | 122.1817 | 0.82855 | 11.7828 | 121.4081 | 122.3557 | -122.2321 | -122.2733
4520.0938 | 122.2046 | -0.086975 | 122.1085 | -0.022507 | 0.014328 | -0.011055 | 0.018098 | 0.046055 | -0.015449 | 0.066689 | 0.80566 | 122.1863 | -0.20599 | 0.073242 | 121.312 | 11.7096 | 1.4603 | 1.506 | 122.3236 | -0.24261 | -0.11902 | 0.07782 | 0.89264 | 0.16022 | -0.79651 | -0.15564 | 0.21515 | 1.0117 | 1.5472 | 1.593 | 121.3989 | 122.2733 | 0.89264 | 122.4106 | 11.7966 | -0.15564 | 122.2733 | 0.89264 | 11.7966 | 121.3989 | 122.4106 | -122.3145 | -122.3511
4521.8594 | 122.3282 | -0.050354 | 122.0901 | 0.0080111 | 0.012832 | -0.0149 | 0.008485 | 0.045414 | -0.011177 | 0.065407 | 0.81482 | 122.2046 | -0.19684 | 0.10529 | 121.3852 | 11.7599 | 1.4191 | 1.6159 | 122.3236 | -0.23804 | -0.14648 | 0.11444 | 0.86517 | 0.15564 | -0.70496 | -0.18768 | 0.23346 | 1.0117 | 1.4694 | 1.6663 | 121.4355 | 122.2549 | 0.86517 | 122.374 | 11.8103 | -0.18768 | 122.2549 | 0.86517 | 11.8103 | 121.4355 | 122.374 | -122.287 | -122.3282
4523.625 | 122.3602 | -0.036621 | 122.1039 | 0.038529 | 0.011978 | -0.010628 | 0.011476 | 0.044346 | -0.011604 | 0.067116 | 0.8606 | 122.2 | -0.1831 | 0.09613 | 121.3943 | 11.7371 | 1.355 | 1.5564 | 122.2916 | -0.24261 | -0.14648 | 0.09613 | 0.89722 | 0.13275 | -0.70953 | -0.20599 | 0.18768 | 1.0437 | 1.3916 | 1.593 | 121.431 | 122.2366 | 0.89722 | 122.3282 | 11.7737 | -0.20599 | 122.2366 | 0.89722 | 11.7737 | 121.431 | 122.3282 | -122.287 | -122.3465
4525.3125 | 122.2092 | -0.10529 | 122.1634 | -0.075912 | 0.015182 | -0.012123 | 0.018739 | 0.047123 | -0.014381 | 0.066475 | 0.91095 | 122.1771 | -0.21973 | 0.1236 | 121.3623 | 11.7874 | 1.4923 | 1.6022 | 122.3373 | -0.24261 | -0.11444 | 0.013733 | 1.0162 | 0.22888 | -0.80109 | -0.13733 | 0.17395 | 1.1307 | 1.5976 | 1.7075 | 121.4676 | 122.2824 | 1.0162 | 122.4426 | 11.8927 | -0.13733 | 122.2824 | 1.0162 | 11.8927 | 121.4676 | 122.4426 | -122.3831 | -122.406
4527.0781 | 122.2504 | -0.082397 | 122.1497 | -0.21324 | 0.015396 | -0.010414 | 0.013826 | 0.050114 | -0.015022 | 0.065193 | 0.88806 | 122.2595 | -0.22888 | 0.068665 | 121.3531 | 11.7828 | 1.6846 | 1.6891 | 122.3969 | -0.25635 | -0.14649 | 0.10986 | 0.97046 | 0.15106 | -0.79651 | -0.17395 | 0.24719 | 1.1169 | 1.767 | 1.7715 | 121.4355 | 122.3419 | 0.97046 | 122.4792 | 11.8652 | -0.17395 | 122.3419 | 0.97046 | 11.8652 | 121.4355 | 122.4792 | -122.3785 | -122.406
4528.8438 | 122.2504 | -0.068665 | 122.1817 | -0.13695 | 0.011978 | -0.011909 | 0.0093396 | 0.04456 | -0.013527 | 0.065834 | 1.0345 | 122.2183 | -0.1831 | 0.20599 | 121.4905 | 11.8835 | 1.4694 | 1.8036 | 122.3373 | -0.21515 | -0.11444 | 0.036621 | 1.1032 | 0.27466 | -0.69122 | -0.14648 | 0.15564 | 1.2177 | 1.5381 | 1.8723 | 121.5591 | 122.287 | 1.1032 | 122.406 | 11.9522 | -0.14648 | 122.287 | 1.1032 | 11.9522 | 121.5591 | 122.406 | -122.3648 | -122.3969
4530.5938 | 122.2687 | -0.082397 | 122.1771 | -0.17509 | 0.014755 | -0.011482 | 0.015748 | 0.047337 | -0.013527 | 0.063484 | 0.95215 | 122.2458 | -0.22888 | 0.082397 | 121.3715 | 11.8149 | 1.6708 | 1.6983 | 122.3969 | -0.25635 | -0.14649 | 0.068665 | 1.0345 | 0.16479 | -0.80566 | -0.17395 | 0.21973 | 1.181 | 1.7532 | 1.7807 | 121.4539 | 122.3282 | 1.0345 | 122.4792 | 11.8973 | -0.17395 | 122.3282 | 1.0345 | 11.8973 | 121.4539 | 122.4792 | -122.406 | -122.4335
4532.2969 | 122.3557 | -0.07782 | 122.1497 | 0.099564 | 0.014328 | -0.013618 | 0.010835 | 0.046269 | -0.014595 | 0.067543 | 1.0849 | 122.2183 | -0.16479 | 0.13275 | 121.431 | 11.7416 | 1.2772 | 1.5564 | 122.3923 | -0.21973 | -0.086975 | 0.068665 | 1.1627 | 0.21057 | -0.71869 | -0.14191 | 0.24262 | 1.2497 | 1.355 | 1.6342 | 121.5088 | 122.2961 | 1.1627 | 122.4701 | 11.8195 | -0.14191 | 122.2961 | 1.1627 | 11.8195 | 121.5088 | 122.4701 | -122.3145 | -122.3694
4534.0156 | 122.3511 | -0.054932 | 122.1725 | -0.083542 | 0.014755 | -0.0080643 | 0.0078442 | 0.045414 | -0.010536 | 0.06498 | 1.0849 | 122.2458 | -0.17853 | 0.15106 | 121.4767 | 11.8423 | 1.4603 | 1.7624 | 122.3602 | -0.21973 | -0.1236 | 0.073243 | 1.1398 | 0.20599 | -0.6958 | -0.16479 | 0.18768 | 1.2634 | 1.5152 | 1.8173 | 121.5317 | 122.3007 | 1.1398 | 122.4152 | 11.8973 | -0.16479 | 122.3007 | 1.1398 | 11.8973 | 121.5317 | 122.4152 | -122.3511 | -122.3923
4535.7969 | 122.3145 | -0.064087 | 122.1451 | 0.076676 | 0.014755 | -0.0087051 | 0.020021 | 0.047764 | -0.013099 | 0.06498 | 1.062 | 122.2458 | -0.2243 | 0.050354 | 121.3348 | 11.6547 | 1.4648 | 1.4786 | 122.4014 | -0.25635 | -0.16022 | 0.10071 | 1.1261 | 0.11444 | -0.81024 | -0.19226 | 0.25635 | 1.2863 | 1.5289 | 1.5427 | 121.3989 | 122.3099 | 1.1261 | 122.4655 | 11.7188 | -0.19226 | 122.3099 | 1.1261 | 11.7188 | 121.3989 | 122.4655 | -122.3694 | -122.4014
4537.5625 | 122.3373 | -0.064087 | 122.2 | 0.15297 | 0.014114 | -0.011269 | 0.013826 | 0.049259 | -0.012031 | 0.065834 | 1.1856 | 122.2412 | -0.16022 | 0.16022 | 121.4722 | 11.7233 | 1.2039 | 1.5518 | 122.3602 | -0.20142 | -0.09613 | 0.041199 | 1.2497 | 0.2243 | -0.72784 | -0.13733 | 0.16022 | 1.3458 | 1.268 | 1.6159 | 121.5363 | 122.3053 | 1.2497 | 122.4243 | 11.7874 | -0.13733 | 122.3053 | 1.2497 | 11.7874 | 121.5363 | 122.4243 | -122.3602 | -122.4014
4539.2812 | 122.3602 | -0.059509 | 122.1634 | 0.11482 | 0.015609 | -0.011909 | 0.012758 | 0.048832 | -0.009895 | 0.065834 | 1.2177 | 122.2412 | -0.17853 | 0.14648 | 121.4584 | 11.7233 | 1.2405 | 1.5701 | 122.3557 | -0.23346 | -0.11902 | 0.07782 | 1.2772 | 0.20599 | -0.70496 | -0.17395 | 0.19226 | 1.3962 | 1.3 | 1.6296 | 121.5179 | 122.3007 | 1.2772 | 122.4152 | 11.7828 | -0.17395 | 122.3007 | 1.2772 | 11.7828 | 121.5179 | 122.4152 | -122.3419 | -122.3969
4541.0625 | 122.3877 | -0.050354 | 122.1451 | 0.053787 | 0.013473 | -0.0037919 | 0.018525 | 0.047123 | -0.014167 | 0.066475 | 1.1444 | 122.2595 | -0.22888 | 0.050354 | 121.3303 | 11.6318 | 1.4603 | 1.4694 | 122.4152 | -0.24719 | -0.17853 | 0.11444 | 1.1948 | 0.10071 | -0.81482 | -0.19684 | 0.27008 | 1.3733 | 1.5106 | 1.5198 | 121.3806 | 122.3099 | 1.1948 | 122.4655 | 11.6821 | -0.19684 | 122.3099 | 1.1948 | 11.6821 | 121.3806 | 122.4655 | -122.374 | -122.3923
4542.7812 | 122.3511 | -0.064087 | 122.168 | 0.10719 | 0.014541 | -0.0102 | 0.01233 | 0.046269 | -0.010963 | 0.068184 | 1.2772 | 122.1954 | -0.16479 | 0.15106 | 121.4722 | 11.7233 | 1.2177 | 1.5747 | 122.319 | -0.21057 | -0.10071 | 0.027466 | 1.3412 | 0.21515 | -0.6958 | -0.14648 | 0.15106 | 1.442 | 1.2817 | 1.6388 | 121.5363 | 122.2595 | 1.3412 | 122.3831 | 11.7874 | -0.14648 | 122.2595 | 1.3412 | 11.7874 | 121.5363 | 122.3831 | -122.3328 | -122.3785
4544.5625 | 122.2824 | -0.082397 | 122.2137 | -0.17509 | 0.016678 | -0.0093461 | 0.012758 | 0.046269 | -0.016304 | 0.064339 | 1.1993 | 122.2641 | -0.21973 | 0.086975 | 121.3943 | 11.7554 | 1.7212 | 1.7532 | 122.4197 | -0.25635 | -0.13733 | 0.050354 | 1.2817 | 0.16937 | -0.8194 | -0.17395 | 0.20599 | 1.4191 | 1.8036 | 1.8356 | 121.4767 | 122.3465 | 1.2817 | 122.5021 | 11.8378 | -0.17395 | 122.3465 | 1.2817 | 11.8378 | 121.4767 | 122.5021 | -122.4335 | -122.4701
4546.3125 | 122.2916 | -0.10071 | 122.2183 | -0.2285 | 0.016037 | -0.012337 | 0.010194 | 0.043492 | -0.01374 | 0.067543 | 1.2817 | 122.2687 | -0.17395 | 0.10529 | 121.4401 | 11.792 | 1.7258 | 1.8631 | 122.3923 | -0.25177 | -0.073242 | 0.050354 | 1.3824 | 0.20599 | -0.7782 | -0.15106 | 0.17395 | 1.4557 | 1.8265 | 1.9638 | 121.5408 | 122.3694 | 1.3824 | 122.493 | 11.8927 | -0.15106 | 122.3694 | 1.3824 | 11.8927 | 121.5408 | 122.493 | -122.3923 | -122.4701
4548.0781 | 122.406 | -0.054932 | 122.1863 | 0.0080111 | 0.015182 | -0.01255 | 0.007417 | 0.044773 | -0.010109 | 0.066475 | 1.2772 | 122.2687 | -0.16937 | 0.10071 | 121.431 | 11.6776 | 1.4923 | 1.7029 | 122.3694 | -0.24719 | -0.11444 | 0.082398 | 1.3321 | 0.15564 | -0.75531 | -0.19226 | 0.18311 | 1.4465 | 1.5472 | 1.7578 | 121.4859 | 122.3236 | 1.3321 | 122.4243 | 11.7325 | -0.19226 | 122.3236 | 1.3321 | 11.7325 | 121.4859 | 122.4243 | -122.3557 | -122.4335
4549.8438 | 122.3969 | -0.045776 | 122.1542 | 0.11482 | 0.019882 | -0.0065689 | 0.016603 | 0.048832 | -0.012458 | 0.064766 | 1.268 | 122.2961 | -0.21973 | 0.041199 | 121.3486 | 11.5402 | 1.4786 | 1.4877 | 122.438 | -0.27924 | -0.17395 | 0.14191 | 1.3138 | 0.086975 | -0.80566 | -0.23346 | 0.28381 | 1.4877 | 1.5244 | 1.5335 | 121.3943 | 122.3419 | 1.3138 | 122.4838 | 11.586 | -0.23346 | 122.3419 | 1.3138 | 11.586 | 121.3943 | 122.4838 | -122.374 | -122.4335
4551.5469 | 122.2824 | -0.10071 | 122.2 | -0.19035 | 0.014969 | -0.0097733 | 0.0089124 | 0.045628 | -0.011604 | 0.065407 | 1.387 | 122.2504 | -0.1831 | 0.16937 | 121.4859 | 11.7966 | 1.6022 | 1.9547 | 122.3877 | -0.2243 | -0.082397 | 0.050354 | 1.4877 | 0.27008 | -0.71411 | -0.1236 | 0.18768 | 1.5701 | 1.7029 | 2.0554 | 121.5866 | 122.3511 | 1.4877 | 122.4884 | 11.8973 | -0.1236 | 122.3511 | 1.4877 | 11.8973 | 121.5866 | 122.4884 | -122.3831 | -122.4243
4553.2969 | 122.3007 | -0.073242 | 122.2275 | -0.19798 | 0.015182 | -0.012337 | 0.015321 | 0.046055 | -0.013313 | 0.066689 | 1.2955 | 122.3007 | -0.2243 | 0.073242 | 121.3577 | 11.6684 | 1.7761 | 1.8127 | 122.406 | -0.24261 | -0.15106 | 0.073242 | 1.3687 | 0.14648 | -0.86975 | -0.16937 | 0.17853 | 1.5198 | 1.8494 | 1.886 | 121.431 | 122.374 | 1.3687 | 122.4792 | 11.7416 | -0.16937 | 122.374 | 1.3687 | 11.7416 | 121.431 | 122.4792 | -122.4518 | -122.4701
4555 | 122.3145 | -0.073242 | 122.2046 | -0.25139 | 0.015823 | -0.0065689 | 0.012758 | 0.046055 | -0.012886 | 0.065621 | 1.3046 | 122.3145 | -0.21973 | 0.059509 | 121.3669 | 11.6318 | 1.8219 | 1.8539 | 122.4106 | -0.27008 | -0.14649 | 0.10986 | 1.3779 | 0.13275 | -0.83771 | -0.19684 | 0.20599 | 1.5244 | 1.8951 | 1.9272 | 121.4401 | 122.3877 | 1.3779 | 122.4838 | 11.705 | -0.19684 | 122.3877 | 1.3779 | 11.705 | 121.4401 | 122.4838 | -122.4243 | -122.4747
4556.7656 | 122.3511 | -0.07782 | 122.2 | 0.18349 | 0.017318 | -0.0089189 | 0.011476 | 0.04755 | -0.011818 | 0.064766 | 1.4511 | 122.2595 | -0.19226 | 0.16479 | 121.4401 | 11.6318 | 1.3092 | 1.7258 | 122.3694 | -0.21515 | -0.11444 | 0.059509 | 1.5289 | 0.24261 | -0.75989 | -0.13733 | 0.16937 | 1.6434 | 1.387 | 1.8036 | 121.5179 | 122.3373 | 1.5289 | 122.4472 | 11.7096 | -0.13733 | 122.3373 | 1.5289 | 11.7096 | 121.5179 | 122.4472 | -122.3923 | -122.4152
4558.5469 | 122.3969 | -0.050354 | 122.1817 | 0.00038159 | 0.019241 | -0.0082779 | 0.010621 | 0.045201 | -0.0096814 | 0.064339 | 1.4099 | 122.287 | -0.17853 | 0.10986 | 121.4172 | 11.6684 | 1.5747 | 1.8631 | 122.3969 | -0.23346 | -0.12817 | 0.10528 | 1.4603 | 0.16022 | -0.76447 | -0.1831 | 0.21515 | 1.5884 | 1.6251 | 1.9135 | 121.4676 | 122.3373 | 1.4603 | 122.4472 | 11.7188 | -0.1831 | 122.3373 | 1.4603 | 11.7188 | 121.4676 | 122.4472 | -122.3602 | -122.4152
4560.3125 | 122.2733 | -0.10986 | 122.2137 | -0.12169 | 0.016891 | -0.0093461 | 0.016389 | 0.047764 | -0.017372 | 0.066262 | 1.442 | 122.2641 | -0.22888 | 0.11444 | 121.3669 | 11.6867 | 1.7349 | 1.9135 | 122.4289 | -0.24719 | -0.11902 | 0.050354 | 1.5518 | 0.2243 | -0.84686 | -0.13733 | 0.21515 | 1.6708 | 1.8448 | 2.0233 | 121.4767 | 122.374 | 1.5518 | 122.5388 | 11.7966 | -0.13733 | 122.374 | 1.5518 | 11.7966 | 121.4767 | 122.5388 | -122.4426 | -122.4609
4562.0156 | 122.2595 | -0.10071 | 122.2137 | -0.083542 | 0.016464 | -0.0080643 | 0.016389 | 0.048405 | -0.015022 | 0.065621 | 1.474 | 122.2733 | -0.21973 | 0.10986 | 121.3852 | 11.705 | 1.6983 | 1.9272 | 122.438 | -0.24719 | -0.11902 | 0.059509 | 1.5747 | 0.21057 | -0.82855 | -0.14648 | 0.2243 | 1.6937 | 1.799 | 2.0279 | 121.4859 | 122.374 | 1.5747 | 122.5388 | 11.8057 | -0.14648 | 122.374 | 1.5747 | 11.8057 | 121.4859 | 122.5388 | -122.4335 | -122.4609
4563.7188 | 122.3282 | -0.07782 | 122.1771 | 0.061417 | 0.02095 | -0.0035783 | 0.015962 | 0.049259 | -0.014595 | 0.065407 | 1.4557 | 122.2595 | -0.21973 | 0.045776 | 121.312 | 11.5997 | 1.6571 | 1.7944 | 122.4335 | -0.24719 | -0.14191 | 0.082397 | 1.5335 | 0.1236 | -0.86517 | -0.16937 | 0.25635 | 1.6754 | 1.7349 | 1.8723 | 121.3898 | 122.3373 | 1.5335 | 122.5113 | 11.6776 | -0.16937 | 122.3373 | 1.5335 | 11.6776 | 121.3898 | 122.5113 | -122.3969 | -122.4243
4565.4844 | 122.3328 | -0.10529 | 122.2183 | -0.26665 | 0.018814 | -0.0099869 | 0.011476 | 0.046482 | -0.011818 | 0.068398 | 1.4603 | 122.3282 | -0.21515 | 0.050354 | 121.344 | 11.7325 | 1.9821 | 2.0645 | 122.4472 | -0.27924 | -0.10986 | 0.10986 | 1.5656 | 0.15564 | -0.87433 | -0.17395 | 0.22888 | 1.6754 | 2.0874 | 2.1698 | 121.4493 | 122.4335 | 1.5656 | 122.5525 | 11.8378 | -0.17395 | 122.4335 | 1.5656 | 11.8378 | 121.4493 | 122.5525 | -122.4335 | -122.4976
4567.1719 | 122.374 | -0.068665 | 122.2092 | 0.17586 | 0.017532 | -0.0078507 | 0.010835 | 0.047123 | -0.014595 | 0.066262 | 1.5884 | 122.2458 | -0.17395 | 0.15106 | 121.4218 | 11.7188 | 1.4648 | 1.9547 | 122.3969 | -0.21973 | -0.10528 | 0.036622 | 1.6571 | 0.21973 | -0.78735 | -0.15106 | 0.18768 | 1.7624 | 1.5335 | 2.0233 | 121.4905 | 122.3145 | 1.6571 | 122.4655 | 11.7874 | -0.15106 | 122.3145 | 1.6571 | 11.7874 | 121.4905 | 122.4655 | -122.3831 | -122.4289
4568.9375 | 122.4106 | -0.032043 | 122.1863 | 0.0080111 | 0.018173 | -0.0067825 | 0.0078442 | 0.04456 | -0.01139 | 0.065193 | 1.5472 | 122.2733 | -0.19226 | 0.07782 | 121.3943 | 11.7874 | 1.7487 | 2.0874 | 122.3969 | -0.23804 | -0.16022 | 0.086975 | 1.5793 | 0.10986 | -0.79193 | -0.20599 | 0.21057 | 1.7395 | 1.7807 | 2.1194 | 121.4264 | 122.3053 | 1.5793 | 122.4289 | 11.8195 | -0.20599 | 122.3053 | 1.5793 | 11.8195 | 121.4264 | 122.4289 | -122.3785 | -122.4243
4570.7188 | 122.3648 | -0.059509 | 122.1725 | 0.16823 | 0.01625 | -0.0020829 | 0.015748 | 0.048832 | -0.011604 | 0.065621 | 1.6251 | 122.3007 | -0.18768 | 0.13275 | 121.3669 | 11.7966 | 1.593 | 2.0462 | 122.4472 | -0.2243 | -0.12817 | 0.12817 | 1.6846 | 0.19226 | -0.80566 | -0.16479 | 0.27466 | 1.8127 | 1.6525 | 2.1057 | 121.4264 | 122.3602 | 1.6846 | 122.5067 | 11.8561 | -0.16479 | 122.3602 | 1.6846 | 11.8561 | 121.4264 | 122.5067 | -122.3602 | -122.3969
4572.4219 | 122.2824 | -0.11902 | 122.2183 | -0.068283 | 0.017746 | -0.0055009 | 0.01703 | 0.047123 | -0.013527 | 0.065621 | 1.6159 | 122.2824 | -0.21973 | 0.11902 | 121.3531 | 11.8652 | 1.8906 | 2.2202 | 122.4472 | -0.24261 | -0.10071 | 0.064087 | 1.7349 | 0.23804 | -0.86517 | -0.1236 | 0.22888 | 1.8356 | 2.0096 | 2.3392 | 121.4722 | 122.4014 | 1.7349 | 122.5662 | 11.9843 | -0.1236 | 122.4014 | 1.7349 | 11.9843 | 121.4722 | 122.5662 | -122.4381 | -122.4609
4574.2031 | 122.3694 | -0.068665 | 122.1817 | 0.13771 | 0.017318 | -0.0061417 | 0.010408 | 0.048405 | -0.013099 | 0.066048 | 1.7029 | 122.2275 | -0.17853 | 0.14191 | 121.3898 | 11.9019 | 1.6479 | 2.2202 | 122.4243 | -0.21057 | -0.10986 | 0.045776 | 1.7715 | 0.21057 | -0.79193 | -0.14191 | 0.24261 | 1.8814 | 1.7166 | 2.2888 | 121.4584 | 122.2961 | 1.7715 | 122.493 | 11.9705 | -0.14191 | 122.2961 | 1.7715 | 11.9705 | 121.4584 | 122.493 | -122.3602 | -122.3923
4575.9688 | 122.3648 | -0.073242 | 122.1954 | 0.13008 | 0.020309 | -0.0057145 | 0.013826 | 0.048832 | -0.013954 | 0.066475 | 1.7395 | 122.2778 | -0.16479 | 0.16022 | 121.3806 | 11.9705 | 1.7303 | 2.2934 | 122.4106 | -0.21515 | -0.091553 | 0.082397 | 1.8127 | 0.23346 | -0.81482 | -0.14191 | 0.21515 | 1.9043 | 1.8036 | 2.3666 | 121.4539 | 122.3511 | 1.8127 | 122.4838 | 12.0438 | -0.14191 | 122.3511 | 1.8127 | 12.0438 | 121.4539 | 122.4838 | -122.3602 | -122.4106
4577.7344 | 122.4426 | -0.07782 | 122.1634 | 0.01564 | 0.018173 | -0.0025101 | 0.008485 | 0.04755 | -0.012031 | 0.066689 | 1.712 | 122.2733 | -0.17853 | 0.10071 | 121.3577 | 12.1078 | 1.9958 | 2.4857 | 122.4197 | -0.23346 | -0.10071 | 0.10986 | 1.7899 | 0.17853 | -0.80566 | -0.15564 | 0.25635 | 1.8906 | 2.0737 | 2.5635 | 121.4355 | 122.3511 | 1.7899 | 122.4976 | 12.1857 | -0.15564 | 122.3511 | 1.7899 | 12.1857 | 121.4355 | 122.4976 | -122.3419 | -122.3969
4579.4531 | 122.3923 | -0.045776 | 122.1817 | 0.12245 | 0.017746 | -0.0082779 | 0.011689 | 0.045841 | -0.012245 | 0.064125 | 1.7578 | 122.2961 | -0.17395 | 0.15106 | 121.3577 | 12.0941 | 1.9272 | 2.536 | 122.3602 | -0.23346 | -0.12817 | 0.11444 | 1.8036 | 0.19684 | -0.82398 | -0.18768 | 0.17853 | 1.9318 | 1.973 | 2.5818 | 121.4035 | 122.3419 | 1.8036 | 122.406 | 12.1399 | -0.18768 | 122.3419 | 1.8036 | 12.1399 | 121.4035 | 122.406 | -122.3557 | -122.4152
4581.2188 | 122.319 | -0.07782 | 122.2137 | -0.23613 | 0.018173 | -0.0046463 | 0.015748 | 0.045628 | -0.013527 | 0.065834 | 1.7166 | 122.319 | -0.2243 | 0.07782 | 121.2799 | 12.236 | 2.4582 | 2.7695 | 122.406 | -0.24261 | -0.14648 | 0.10529 | 1.7944 | 0.15564 | -0.93384 | -0.16479 | 0.19226 | 1.9409 | 2.536 | 2.8473 | 121.3577 | 122.3969 | 1.7944 | 122.4838 | 12.3138 | -0.16479 | 122.3969 | 1.7944 | 12.3138 | 121.3577 | 122.4838 | -122.438 | -122.4564
4582.9688 | 122.2961 | -0.10529 | 122.1771 | -0.022507 | 0.016678 | -0.0042191 | 0.018525 | 0.047337 | -0.012672 | 0.066689 | 1.7807 | 122.2916 | -0.21057 | 0.07782 | 121.2479 | 12.2589 | 2.2659 | 2.6871 | 122.4106 | -0.24719 | -0.10529 | 0.11444 | 1.886 | 0.18311 | -0.92926 | -0.14191 | 0.23346 | 1.9913 | 2.3712 | 2.7924 | 121.3532 | 122.3969 | 1.886 | 122.5159 | 12.3642 | -0.14191 | 122.3969 | 1.886 | 12.3642 | 121.3532 | 122.5159 | -122.3877 | -122.4243
4584.7344 | 122.4152 | 0.42572 | 122.7081 | -0.25902 | 0.019882 | -0.0102 | 0.012758 | 0.048619 | -0.012031 | 0.06498 | 2.2842 | 122.8455 | 0.31128 | 0.60425 | 121.8155 | 12.9639 | 2.9297 | 3.3371 | 123.0331 | 0.30212 | -0.11444 | 0.13733 | 1.8585 | 0.17853 | -0.89264 | -0.1236 | 0.32501 | 1.973 | 2.504 | 2.9114 | 121.3898 | 122.4197 | 1.8585 | 122.6074 | 12.5381 | -0.1236 | 122.4197 | 1.8585 | 12.5381 | 121.3898 | 122.6074 | -122.3969 | -122.406
4586.4375 | 122.4243 | -0.054932 | 122.1588 | 0.030899 | 0.0186 | -0.0050735 | 0.0082714 | 0.046696 | -0.011818 | 0.065834 | 1.7807 | 122.2275 | -0.23346 | 0.027466 | 121.2433 | 12.5107 | 2.3987 | 3.0716 | 122.3328 | -0.28839 | -0.17853 | 0.068665 | 1.8356 | 0.082398 | -0.91553 | -0.23346 | 0.17395 | 2.0142 | 2.4536 | 3.1265 | 121.2982 | 122.2824 | 1.8356 | 122.3877 | 12.5656 | -0.23346 | 122.2824 | 1.8356 | 12.5656 | 121.2982 | 122.3877 | -122.3923 | -122.4472
4588.2031 | 122.4335 | 0.50812 | 122.8363 | 0.02327 | 0.020309 | -0.0061417 | 0.011476 | 0.049259 | -0.012245 | 0.066262 | 1.268 | 121.6736 | -0.80109 | -0.48065 | 120.7214 | 12.2314 | 2.3895 | 3.0716 | 121.8658 | -0.79651 | -1.3092 | -1.1627 | 0.75989 | -0.98877 | -2.1149 | -1.3046 | -0.97046 | 2.0691 | 1.8814 | 2.5635 | 120.2133 | 121.1655 | 0.75989 | 121.3577 | 11.7233 | -1.3046 | 121.1655 | 0.75989 | 11.7233 | 120.2133 | 121.3577 | -123.6374 | -123.6328
4589.9844 | 122.2549 | 0.4303 | 122.7814 | -0.15221 | 0.018814 | -0.0089189 | 0.012758 | 0.044773 | -0.012245 | 0.064125 | 1.9363 | 122.2916 | -0.17853 | 0.16022 | 121.3165 | 12.8586 | 2.7878 | 3.5889 | 122.406 | -0.23346 | -0.60883 | -0.48981 | 1.506 | -0.27008 | -1.4648 | -0.66376 | -0.37537 | 2.1149 | 2.3575 | 3.1586 | 120.8862 | 121.8613 | 1.506 | 121.9757 | 12.4283 | -0.66376 | 121.8613 | 1.506 | 12.4283 | 120.8862 | 121.9757 | -122.9599 | -123.0148
4591.75 | 122.4014 | -0.45319 | 121.8063 | 0.19112 | 0.019027 | -0.0061417 | 0.016816 | 0.047764 | -0.012672 | 0.065834 | 1.6067 | 122.0032 | -0.48523 | -0.21515 | 120.9274 | 12.4374 | 2.3895 | 3.1998 | 122.0856 | -0.55389 | -0.032043 | 0.19684 | 2.0599 | 0.23804 | -0.87891 | -0.10071 | 0.27924 | 2.092 | 2.8427 | 3.653 | 121.3806 | 122.4564 | 2.0599 | 122.5388 | 12.8906 | -0.10071 | 122.4564 | 2.0599 | 12.8906 | 121.3806 | 122.5388 | -122.2916 | -122.3602
4593.4531 | 122.287 | 0.46234 | 122.8088 | -0.19035 | 0.018814 | -0.0059281 | 0.012117 | 0.044132 | -0.012031 | 0.06498 | 2.1378 | 122.4335 | -0.022888 | 0.3067 | 121.4676 | 13.1653 | 3.0441 | 4.01 | 122.5479 | -0.059509 | -0.48523 | -0.37537 | 1.6754 | -0.15564 | -1.3412 | -0.52185 | -0.26093 | 2.1606 | 2.5818 | 3.5477 | 121.0052 | 121.9711 | 1.6754 | 122.0856 | 12.7029 | -0.52185 | 121.9711 | 1.6754 | 12.7029 | 121.0052 | 122.0856 | -122.8317 | -122.8683
4595.2188 | 122.2549 | 0.63629 | 122.9645 | -0.19035 | 0.017959 | -0.0059281 | 0.013826 | 0.048619 | -0.011604 | 0.065834 | 2.092 | 122.3282 | -0.12817 | 0.26093 | 121.3852 | 13.298 | 3.2593 | 4.2068 | 122.5067 | -0.13275 | -0.76447 | -0.63629 | 1.4557 | -0.37537 | -1.5793 | -0.76904 | -0.45776 | 2.2202 | 2.623 | 3.5706 | 120.7489 | 121.6919 | 1.4557 | 121.8704 | 12.6617 | -0.76904 | 121.6919 | 1.4557 | 12.6617 | 120.7489 | 121.8704 | -123.0927 | -123.0972
4596.9219 | 122.3648 | -0.59967 | 121.7148 | 0.1606 | 0.019027 | -0.0061417 | 0.014253 | 0.04691 | -0.012031 | 0.065621 | 1.2589 | 121.4264 | -0.98419 | -0.70038 | 120.3873 | 12.4466 | 2.5497 | 3.6484 | 121.5546 | -1.0849 | -0.38452 | -0.28839 | 1.8585 | -0.10071 | -1.3275 | -0.48523 | -0.16022 | 2.243 | 3.1494 | 4.248 | 120.9869 | 122.0261 | 1.8585 | 122.1542 | 13.0463 | -0.48523 | 122.0261 | 1.8585 | 13.0463 | 120.9869 | 122.1542 | -122.699 | -122.7997
4598.6875 | 122.3007 | -0.10529 | 122.1909 | -0.030136 | 0.020096 | -0.0069961 | 0.018098 | 0.048405 | -0.016304 | 0.063271 | 2.0096 | 122.2458 | -0.21973 | 0.091553 | 121.1792 | 13.1332 | 3.2684 | 4.1107 | 122.4426 | -0.25177 | -0.11444 | 0.054932 | 2.1149 | 0.19684 | -1.0117 | -0.14648 | 0.25177 | 2.2293 | 3.3737 | 4.216 | 121.2845 | 122.3511 | 2.1149 | 122.5479 | 13.2385 | -0.14648 | 122.3511 | 2.1149 | 13.2385 | 121.2845 | 122.5479 | -122.4106 | -122.4426
4600.3906 | 122.4243 | -0.64545 | 121.5958 | 0.12245 | 0.017746 | -0.0052873 | 0.014253 | 0.045841 | -0.012031 | 0.069466 | 1.8173 | 122.081 | -0.42572 | -0.16479 | 120.9503 | 13.0051 | 3.1265 | 4.1061 | 122.168 | -0.47607 | 0.21973 | 0.48523 | 2.4628 | 0.48065 | -0.64545 | 0.16937 | 0.5722 | 2.243 | 3.772 | 4.7516 | 121.5958 | 122.7264 | 2.4628 | 122.8134 | 13.6505 | 0.16937 | 122.7264 | 2.4628 | 13.6505 | 121.5958 | 122.8134 | -122.0215 | -122.0718
4602.1562 | 122.4335 | -0.35706 | 121.8475 | 0.13771 | 0.021164 | -0.0089189 | 0.013612 | 0.046482 | -0.013313 | 0.065193 | 1.8265 | 122.0581 | -0.45319 | -0.20142 | 120.9 | 13.0142 | 3.2776 | 4.1931 | 122.168 | -0.48523 | -0.09613 | 0.21057 | 2.1835 | 0.15564 | -0.94757 | -0.12817 | 0.32044 | 2.2797 | 3.6346 | 4.5502 | 121.257 | 122.4152 | 2.1835 | 122.525 | 13.3713 | -0.12817 | 122.4152 | 2.1835 | 13.3713 | 121.257 | 122.525 | -122.3007 | -122.3328
4603.8594 | 122.3785 | -0.054932 | 122.1817 | 0.053787 | 0.020523 | -0.0050735 | 0.014039 | 0.04691 | -0.015876 | 0.065407 | 2.0645 | 122.3053 | -0.21973 | 0.036621 | 121.1105 | 13.4216 | 3.6575 | 4.5273 | 122.438 | -0.26093 | -0.16479 | 0.1236 | 2.1194 | 0.091553 | -1.0712 | -0.20599 | 0.25635 | 2.2842 | 3.7125 | 4.5822 | 121.1655 | 122.3602 | 2.1194 | 122.493 | 13.4766 | -0.20599 | 122.3602 | 2.1194 | 13.4766 | 121.1655 | 122.493 | -122.4014 | -122.4426
4605.625 | 122.3145 | -0.091553 | 122.2229 | -0.20561 | 0.019882 | -0.0072099 | 0.014039 | 0.046269 | -0.013527 | 0.066902 | 2.092 | 122.2778 | -0.21515 | 0.050354 | 121.1288 | 13.7695 | 4.1702 | 5.0812 | 122.4289 | -0.25177 | -0.1236 | 0.054932 | 2.1835 | 0.14191 | -1.0941 | -0.16022 | 0.20599 | 2.3071 | 4.2618 | 5.1727 | 121.2204 | 122.3694 | 2.1835 | 122.5204 | 13.8611 | -0.16022 | 122.3694 | 2.1835 | 13.8611 | 121.2204 | 122.5204 | -122.438 | -122.4747
4607.3281 | 122.319 | -0.10071 | 122.2458 | -0.28191 | 0.019027 | -0.0072099 | 0.0078442 | 0.044346 | -0.010109 | 0.066475 | 2.2202 | 122.2961 | -0.19226 | 0.1236 | 121.1838 | 13.9847 | 4.3213 | 5.4428 | 122.4243 | -0.22888 | -0.091553 | 0.050354 | 2.3209 | 0.2243 | -1.062 | -0.12817 | 0.17853 | 2.4124 | 4.422 | 5.5435 | 121.2845 | 122.3969 | 2.3209 | 122.525 | 14.0854 | -0.12817 | 122.3969 | 2.3209 | 14.0854 | 121.2845 | 122.525 | -122.4381 | -122.4747
4609.0938 | 122.3969 | -0.073242 | 122.2046 | 0.091934 | 0.019668 | -0.0065689 | 0.011903 | 0.046696 | -0.011818 | 0.065407 | 2.2568 | 122.2504 | -0.18768 | 0.13275 | 121.17 | 13.9526 | 4.0741 | 5.397 | 122.4014 | -0.21515 | -0.11444 | 0.045776 | 2.33 | 0.20599 | -1.0345 | -0.14191 | 0.19684 | 2.4445 | 4.1473 | 5.4703 | 121.2433 | 122.3236 | 2.33 | 122.4747 | 14.0259 | -0.14191 | 122.3236 | 2.33 | 14.0259 | 121.2433 | 122.4747 | -122.3923 | -122.4197
4610.7969 | 122.3099 | -0.09613 | 122.2366 | -0.25139 | 0.022018 | -0.0084915 | 0.013826 | 0.045841 | -0.013099 | 0.06498 | 2.2659 | 122.2961 | -0.21057 | 0.07782 | 121.1014 | 14.2181 | 4.715 | 5.7953 | 122.4243 | -0.27008 | -0.11444 | 0.05951 | 2.3621 | 0.17395 | -1.1353 | -0.17395 | 0.18768 | 2.4765 | 4.8111 | 5.8914 | 121.1975 | 122.3923 | 2.3621 | 122.5204 | 14.3143 | -0.17395 | 122.3923 | 2.3621 | 14.3143 | 121.1975 | 122.5204 | -122.4472 | -122.5067
4612.5625 | 122.287 | -0.10071 | 122.2046 | -0.098801 | 0.021804 | -0.0029373 | 0.016603 | 0.046696 | -0.013313 | 0.064339 | 2.3117 | 122.2778 | -0.2243 | 0.11902 | 121.1014 | 14.3143 | 4.6555 | 5.8777 | 122.4106 | -0.24261 | -0.1236 | 0.073242 | 2.4124 | 0.21973 | -1.1032 | -0.14191 | 0.20599 | 2.536 | 4.7562 | 5.9784 | 121.2021 | 122.3785 | 2.4124 | 122.5113 | 14.415 | -0.14191 | 122.3785 | 2.4124 | 14.415 | 121.2021 | 122.5113 | -122.4289 | -122.4472
4614.3281 | 122.2824 | -0.10071 | 122.2046 | -0.17509 | 0.0233 | -0.0035783 | 0.01468 | 0.047123 | -0.01374 | 0.066048 | 2.3209 | 122.3007 | -0.21057 | 0.10071 | 121.0968 | 14.502 | 4.9484 | 6.1432 | 122.4014 | -0.27466 | -0.10986 | 0.09613 | 2.4216 | 0.20142 | -1.1078 | -0.17395 | 0.19684 | 2.5314 | 5.0491 | 6.2439 | 121.1975 | 122.4014 | 2.4216 | 122.5021 | 14.6027 | -0.17395 | 122.4014 | 2.4216 | 14.6027 | 121.1975 | 122.5021 | -122.4152 | -122.4792
4616.0469 | 122.2687 | -0.10986 | 122.2137 | -0.091171 | 0.021591 | -0.0046463 | 0.016389 | 0.046482 | -0.01609 | 0.066689 | 2.3895 | 122.2824 | -0.19684 | 0.10071 | 121.0693 | 14.6072 | 4.9805 | 6.2805 | 122.4152 | -0.23346 | -0.086975 | 0.068665 | 2.4994 | 0.21057 | -1.1444 | -0.1236 | 0.20142 | 2.5864 | 5.0903 | 6.3904 | 121.1792 | 122.3923 | 2.4994 | 122.525 | 14.7171 | -0.1236 | 122.3923 | 2.4994 | 14.7171 | 121.1792 | 122.525 | -122.4106 | -122.4472
4617.75 | 122.3419 | -0.082397 | 122.2183 | -0.21324 | 0.022445 | -0.0072099 | 0.010621 | 0.046696 | -0.014595 | 0.065407 | 2.3712 | 122.3099 | -0.22888 | 0.054932 | 121.0281 | 14.8132 | 5.4886 | 6.633 | 122.4518 | -0.26093 | -0.14649 | 0.091552 | 2.4536 | 0.13733 | -1.1902 | -0.17853 | 0.23346 | 2.6001 | 5.571 | 6.7154 | 121.1105 | 122.3923 | 2.4536 | 122.5342 | 14.8956 | -0.17853 | 122.3923 | 2.4536 | 14.8956 | 121.1105 | 122.5342 | -122.4472 | -122.4792
4619.5 | 122.3099 | -0.086975 | 122.2137 | -0.17509 | 0.022018 | -0.0020829 | 0.01468 | 0.047337 | -0.013099 | 0.066902 | 2.4078 | 122.3236 | -0.2243 | 0.068665 | 121.0281 | 14.9643 | 5.6168 | 6.8207 | 122.4289 | -0.25635 | -0.13733 | 0.10986 | 2.4948 | 0.15564 | -1.1856 | -0.16937 | 0.21515 | 2.6321 | 5.7037 | 6.9077 | 121.1151 | 122.4106 | 2.4948 | 122.5159 | 15.0513 | -0.16937 | 122.4106 | 2.4948 | 15.0513 | 121.1151 | 122.5159 | -122.438 | -122.4701
4621.2656 | 122.3373 | -0.082397 | 122.2275 | -0.27428 | 0.022445 | -0.0055009 | 0.011262 | 0.043278 | -0.011177 | 0.065834 | 2.449 | 122.3236 | -0.22888 | 0.045776 | 121.0007 | 15.1428 | 5.9372 | 7.0953 | 122.4335 | -0.27466 | -0.14649 | 0.09613 | 2.5314 | 0.12817 | -1.2268 | -0.19226 | 0.20599 | 2.6779 | 6.0196 | 7.1777 | 121.0831 | 122.406 | 2.5314 | 122.5159 | 15.2252 | -0.19226 | 122.406 | 2.5314 | 15.2252 | 121.0831 | 122.5159 | -122.4564 | -122.5021
4622.9688 | 122.3557 | -0.068665 | 122.2412 | -0.12169 | 0.023727 | -0.0084915 | 0.0065624 | 0.045414 | -0.012245 | 0.066048 | 2.5589 | 122.2687 | -0.1831 | 0.14648 | 121.1014 | 15.4312 | 5.9509 | 7.489 | 122.4152 | -0.2243 | -0.11444 | 0.027466 | 2.6276 | 0.21515 | -1.1398 | -0.15564 | 0.17395 | 2.742 | 6.0196 | 7.5577 | 121.17 | 122.3373 | 2.6276 | 122.4838 | 15.4999 | -0.15564 | 122.3373 | 2.6276 | 15.4999 | 121.17 | 122.4838 | -122.4243 | -122.4655
4624.7344 | 122.3007 | -0.1236 | 122.2183 | -0.045395 | 0.022445 | 0.0032577 | 0.016816 | 0.04755 | -0.014167 | 0.066262 | 2.6001 | 122.3007 | -0.2243 | 0.07782 | 120.9686 | 15.39 | 6.0287 | 7.37 | 122.4335 | -0.24719 | -0.10071 | 0.082397 | 2.7237 | 0.20142 | -1.2497 | -0.1236 | 0.21515 | 2.8244 | 6.1523 | 7.4936 | 121.0922 | 122.4243 | 2.7237 | 122.5571 | 15.5136 | -0.1236 | 122.4243 | 2.7237 | 15.5136 | 121.0922 | 122.5571 | -122.4426 | -122.4655
4626.4375 | 122.3923 | -0.059509 | 122.1588 | 0.076676 | 0.025009 | -0.0048599 | 0.014039 | 0.048191 | -0.014595 | 0.066902 | 2.5772 | 122.3007 | -0.2243 | 0.050354 | 120.9366 | 15.4816 | 6.1157 | 7.489 | 122.4564 | -0.2655 | -0.16479 | 0.14191 | 2.6367 | 0.10986 | -1.2222 | -0.20599 | 0.29755 | 2.8015 | 6.1752 | 7.5485 | 120.9961 | 122.3602 | 2.6367 | 122.5159 | 15.5411 | -0.20599 | 122.3602 | 2.6367 | 15.5411 | 120.9961 | 122.5159 | -122.3831 | -122.4243
4628.2031 | 122.3785 | -0.064087 | 122.1817 | 0.084305 | 0.022445 | -0.0059281 | 0.010194 | 0.04755 | -0.011177 | 0.065621 | 2.7283 | 122.2824 | -0.17395 | 0.13275 | 120.9732 | 15.8203 | 6.3263 | 7.9559 | 122.3694 | -0.24261 | -0.10986 | 0.10071 | 2.7924 | 0.19684 | -1.2085 | -0.17853 | 0.18768 | 2.9022 | 6.3904 | 8.02 | 121.0373 | 122.3465 | 2.7924 | 122.4335 | 15.8844 | -0.17853 | 122.3465 | 2.7924 | 15.8844 | 121.0373 | 122.4335 | -122.3557 | -122.4243
4629.9219 | 122.3969 | -0.041199 | 122.1909 | 0.099564 | 0.022659 | -0.0055009 | 0.012758 | 0.047123 | -0.012031 | 0.066902 | 2.7649 | 122.2687 | -0.16937 | 0.13275 | 120.9595 | 16.0309 | 6.601 | 8.2535 | 122.3465 | -0.22888 | -0.12817 | 0.07782 | 2.8061 | 0.17395 | -1.2314 | -0.18768 | 0.15564 | 2.9343 | 6.6422 | 8.2947 | 121.0007 | 122.3099 | 2.8061 | 122.3877 | 16.0721 | -0.18768 | 122.3099 | 2.8061 | 16.0721 | 121.0007 | 122.3877 | -122.3602 | -122.4197
4631.6875 | 122.3419 | -0.082397 | 122.2046 | 0.076676 | 0.022873 | 5.3338e-05 | 0.018739 | 0.046696 | -0.012458 | 0.065407 | 2.742 | 122.2961 | -0.23346 | 0.045776 | 120.8359 | 16.1041 | 6.926 | 8.2901 | 122.4335 | -0.25177 | -0.15106 | 0.091553 | 2.8244 | 0.12817 | -1.3687 | -0.16937 | 0.22888 | 2.9755 | 7.0084 | 8.3725 | 120.9183 | 122.3785 | 2.8244 | 122.5159 | 16.1865 | -0.16937 | 122.3785 | 2.8244 | 16.1865 | 120.9183 | 122.5159 | -122.438 | -122.4564
4633.4375 | 122.3602 | -0.091553 | 122.2137 | 0.0080111 | 0.025222 | 0.00026694 | 0.016389 | 0.049259 | -0.01374 | 0.065621 | 2.7832 | 122.2961 | -0.23346 | 0.045776 | 120.8267 | 16.3101 | 7.1915 | 8.5785 | 122.4518 | -0.24719 | -0.14191 | 0.082398 | 2.8748 | 0.13733 | -1.387 | -0.15564 | 0.23804 | 3.0167 | 7.283 | 8.67 | 120.9183 | 122.3877 | 2.8748 | 122.5433 | 16.4017 | -0.15564 | 122.3877 | 2.8748 | 16.4017 | 120.9183 | 122.5433 | -122.4472 | -122.4609
4635.2031 | 122.319 | -0.15564 | 122.1405 | -0.075912 | 0.024154 | -0.0035783 | 0.015962 | 0.048405 | -0.013954 | 0.064766 | 2.9205 | 122.3099 | -0.19684 | 0.11444 | 120.8588 | 16.5985 | 7.4753 | 8.9493 | 122.4197 | -0.24719 | -0.041198 | 0.16937 | 3.0762 | 0.27008 | -1.2817 | -0.091552 | 0.27924 | 3.1174 | 7.6309 | 9.1049 | 121.0144 | 122.4655 | 3.0762 | 122.5754 | 16.7542 | -0.091552 | 122.4655 | 3.0762 | 16.7542 | 121.0144 | 122.5754 | -122.3373 | -122.3877
4636.9062 | 122.374 | -0.52643 | 121.7468 | 0.10719 | 0.024154 | -0.0029373 | 0.0080578 | 0.046696 | -0.011818 | 0.065193 | 2.3575 | 121.6232 | -0.81024 | -0.49439 | 120.2637 | 16.3651 | 7.2693 | 8.9401 | 121.7377 | -0.85602 | -0.28381 | -0.1236 | 2.8839 | 0.032043 | -1.4832 | -0.32959 | -0.009155 | 3.1677 | 7.7957 | 9.4666 | 120.7901 | 122.1497 | 2.8839 | 122.2641 | 16.8915 | -0.32959 | 122.1497 | 2.8839 | 16.8915 | 120.7901 | 122.2641 | -122.5571 | -122.6028
4638.6719 | 122.2412 | -0.29755 | 121.9894 | -0.083542 | 0.024795 | 0.0021895 | 0.017244 | 0.047978 | -0.014595 | 0.067543 | 3.6118 | 122.9416 | 0.40741 | 0.72327 | 121.4584 | 17.5552 | 8.3496 | 9.8969 | 123.0194 | 0.37537 | 0.70496 | 0.95215 | 3.9093 | 1.0208 | -0.53101 | 0.67291 | 1.03 | 3.2043 | 8.6472 | 10.1944 | 121.756 | 123.2391 | 3.9093 | 123.317 | 17.8528 | 0.67291 | 123.2391 | 3.9093 | 17.8528 | 121.756 | 123.317 | -121.582 | -121.6141
4640.375 | 122.3923 | -0.78735 | 121.4813 | 0.13771 | 0.025863 | -0.0042191 | 0.012971 | 0.049687 | -0.012458 | 0.067757 | 2.3026 | 121.4951 | -0.97046 | -0.65002 | 120.0714 | 16.6031 | 7.5851 | 9.288 | 121.6187 | -0.98419 | -0.1831 | 0.013733 | 3.0899 | 0.13733 | -1.4099 | -0.19684 | 0.13733 | 3.273 | 8.3725 | 10.0754 | 120.8588 | 122.2824 | 3.0899 | 122.406 | 17.3904 | -0.19684 | 122.2824 | 3.0899 | 17.3904 | 120.8588 | 122.406 | -122.4518 | -122.4655
4642.1406 | 122.4152 | 0.16937 | 122.4564 | -0.022507 | 0.024154 | -0.00037386 | 0.010194 | 0.04691 | -0.011818 | 0.067543 | 2.3712 | 121.582 | -0.90637 | -0.59967 | 120.1355 | 17.0609 | 8.2306 | 9.8419 | 121.701 | -0.91553 | -1.0757 | -0.87433 | 2.2018 | -0.76904 | -2.3209 | -1.0849 | -0.75531 | 3.2776 | 8.0612 | 9.6725 | 119.9661 | 121.4127 | 2.2018 | 121.5317 | 16.8915 | -1.0849 | 121.4127 | 2.2018 | 16.8915 | 119.9661 | 121.5317 | -123.3627 | -123.3719
4643.8438 | 122.3007 | -0.84686 | 121.4447 | -0.030136 | 0.025863 | -0.0033647 | 0.018525 | 0.04755 | -0.014167 | 0.066902 | 3.6987 | 122.8317 | 0.32044 | 0.57678 | 121.2067 | 17.9672 | 8.963 | 10.524 | 122.9141 | 0.25177 | 1.1673 | 1.387 | 4.5456 | 1.4236 | -0.23804 | 1.0986 | 1.4694 | 3.3783 | 9.8099 | 11.3709 | 122.0535 | 123.6786 | 4.5456 | 123.761 | 18.8141 | 1.0986 | 123.6786 | 4.5456 | 18.8141 | 122.0535 | 123.761 | -121.1243 | -121.1929
4645.6094 | 122.2641 | -0.52643 | 121.7056 | -0.068283 | 0.025863 | -0.0027237 | 0.015748 | 0.047978 | -0.014167 | 0.064766 | 3.9368 | 122.9965 | 0.50812 | 0.74158 | 121.3898 | 18.4433 | 9.407 | 11.0001 | 123.056 | 0.41199 | 1.0345 | 1.2909 | 4.4632 | 1.268 | -0.31586 | 0.93841 | 1.3504 | 3.4286 | 9.9335 | 11.5265 | 121.9162 | 123.5229 | 4.4632 | 123.5825 | 18.9697 | 0.93841 | 123.5229 | 4.4632 | 18.9697 | 121.9162 | 123.5825 | -121.1975 | -121.2936
4647.375 | 122.3694 | -0.6958 | 121.5454 | 0.084305 | 0.027572 | -0.0016557 | 0.011689 | 0.049046 | -0.015876 | 0.067543 | 2.5223 | 121.4447 | -0.97504 | -0.66376 | 119.9524 | 17.5507 | 8.6929 | 10.4645 | 121.5866 | -1.0162 | -0.27924 | -0.10071 | 3.2181 | 0.032044 | -1.593 | -0.32043 | 0.041199 | 3.4973 | 9.3887 | 11.1603 | 120.6482 | 122.1405 | 3.2181 | 122.2824 | 18.2465 | -0.32043 | 122.1405 | 3.2181 | 18.2465 | 120.6482 | 122.2824 | -122.5204 | -122.5616
4649.125 | 122.2641 | -0.082397 | 122.2366 | -0.15984 | 0.025436 | 0.0017623 | 0.009126 | 0.045201 | -0.010963 | 0.063912 | 3.4058 | 122.2733 | -0.16022 | 0.15564 | 120.7993 | 18.6127 | 9.7549 | 11.5402 | 122.374 | -0.23346 | -0.07782 | 0.036621 | 3.4882 | 0.23804 | -1.4374 | -0.15106 | 0.13733 | 3.566 | 9.8373 | 11.6226 | 120.8817 | 122.3557 | 3.4882 | 122.4564 | 18.6951 | -0.15106 | 122.3557 | 3.4882 | 18.6951 | 120.8817 | 122.4564 | -122.3969 | -122.4701
4650.8438 | 122.319 | 0.3479 | 122.6303 | -0.2285 | 0.02565 | 0.0024033 | 0.012971 | 0.04691 | -0.012458 | 0.063698 | 3.4836 | 122.3602 | -0.10529 | 0.19226 | 120.7809 | 18.8461 | 10.2768 | 11.8011 | 122.5891 | -0.13275 | -0.45319 | -0.27008 | 3.1357 | -0.15564 | -1.8494 | -0.48065 | -0.041199 | 3.5889 | 9.9289 | 11.4532 | 120.433 | 122.0123 | 3.1357 | 122.2412 | 18.4982 | -0.48065 | 122.0123 | 3.1357 | 18.4982 | 120.433 | 122.2412 | -122.7356 | -122.7631
4652.6094 | 122.406 | -0.49896 | 121.6873 | 0.11482 | 0.027359 | -0.00080106 | 0.016176 | 0.047764 | -0.013099 | 0.06498 | 3.0716 | 122.049 | -0.41199 | -0.3067 | 120.2362 | 18.3426 | 9.6634 | 11.3251 | 122.0215 | -0.63629 | 0.086975 | 0.36163 | 3.5706 | 0.19226 | -1.4511 | -0.13733 | 0.33417 | 3.4836 | 10.1624 | 11.824 | 120.7352 | 122.5479 | 3.5706 | 122.5204 | 18.8416 | -0.13733 | 122.5479 | 3.5706 | 18.8416 | 120.7352 | 122.5204 | -122.0993 | -122.3236
4654.3594 | 122.4152 | -0.064087 | 122.1359 | 0.030899 | 0.028427 | 0.00090794 | 0.0080578 | 0.048191 | -0.010109 | 0.066689 | 2.7328 | 121.4539 | -0.98877 | -0.75989 | 119.8105 | 18.4982 | 9.9014 | 11.6043 | 121.5637 | -1.0071 | -0.92468 | -0.68207 | 2.7969 | -0.6958 | -2.3254 | -0.94299 | -0.5722 | 3.7216 | 9.9655 | 11.6684 | 119.8746 | 121.5179 | 2.7969 | 121.6278 | 18.5623 | -0.94299 | 121.5179 | 2.7969 | 18.5623 | 119.8746 | 121.6278 | -123.1247 | -123.143
4656.0625 | 122.3145 | 0.091553 | 122.3648 | -0.15221 | 0.030777 | -0.0037919 | 0.0093396 | 0.044346 | -0.011604 | 0.064553 | 3.6575 | 122.2824 | -0.17853 | 0.18768 | 120.7169 | 19.6381 | 10.8765 | 12.7213 | 122.3877 | -0.20599 | -0.27008 | -0.082397 | 3.566 | 0.09613 | -1.6479 | -0.29755 | 0.022888 | 3.8361 | 10.7849 | 12.6297 | 120.6253 | 122.1909 | 3.566 | 122.2961 | 19.5465 | -0.29755 | 122.1909 | 3.566 | 19.5465 | 120.6253 | 122.2961 | -122.5433 | -122.5708
4657.8281 | 122.3465 | 0.33417 | 122.5983 | -0.28191 | 0.028 | -0.0037919 | 0.014039 | 0.045201 | -0.013954 | 0.066475 | 4.2984 | 123.0011 | 0.48523 | 0.77362 | 121.2616 | 20.1874 | 11.6547 | 13.1836 | 123.1979 | 0.46234 | 0.15106 | 0.40283 | 3.9642 | 0.43945 | -1.3367 | 0.12817 | 0.59967 | 3.8132 | 11.3205 | 12.8494 | 120.9274 | 122.6669 | 3.9642 | 122.8638 | 19.8532 | 0.12817 | 122.6669 | 3.9642 | 19.8532 | 120.9274 | 122.8638 | -122.113 | -122.1359
4659.5938 | 122.4152 | -0.25177 | 122.0398 | 0.076676 | 0.027359 | -0.00080106 | 0.013185 | 0.04691 | -0.011604 | 0.066689 | 3.5934 | 122.0627 | -0.36163 | -0.050354 | 120.4193 | 19.7754 | 11.1465 | 12.9044 | 122.2504 | -0.39368 | -0.10986 | 0.022888 | 3.8452 | 0.20142 | -1.6205 | -0.14191 | 0.21057 | 3.9551 | 11.3983 | 13.1561 | 120.6711 | 122.3145 | 3.8452 | 122.5021 | 20.0272 | -0.14191 | 122.3145 | 3.8452 | 20.0272 | 120.6711 | 122.5021 | -122.4014 | -122.4335
4661.2969 | 122.3511 | 0.018311 | 122.2733 | -0.29716 | 0.029281 | 0.0041123 | 0.011689 | 0.044132 | -0.01374 | 0.065834 | 3.7582 | 122.1771 | -0.2655 | 0.12817 | 120.575 | 20.2606 | 11.6409 | 13.4903 | 122.3694 | -0.27466 | -0.28381 | -0.09613 | 3.7399 | 0.10986 | -1.6983 | -0.29297 | 0.096131 | 4.0237 | 11.6226 | 13.472 | 120.5566 | 122.1588 | 3.7399 | 122.3511 | 20.2423 | -0.29297 | 122.1588 | 3.7399 | 20.2423 | 120.5566 | 122.3511 | -122.5388 | -122.5479
4663 | 122.4976 | 0.032043 | 122.2504 | 0.02327 | 0.02864 | -0.00058746 | 0.011689 | 0.046696 | -0.013954 | 0.065407 | 3.0945 | 121.4218 | -0.97504 | -0.62714 | 119.783 | 19.7891 | 11.4075 | 13.1195 | 121.6599 | -0.99335 | -1.0071 | -0.82855 | 3.0624 | -0.65918 | -2.4673 | -1.0254 | -0.59051 | 4.0695 | 11.3754 | 13.0875 | 119.751 | 121.3898 | 3.0624 | 121.6278 | 19.7571 | -1.0254 | 121.3898 | 3.0624 | 19.7571 | 119.751 | 121.6278 | -123.2254 | -123.2437
4664.7656 | 122.3282 | 0.63629 | 122.937 | -0.2285 | 0.029281 | -0.00037386 | 0.014467 | 0.04456 | -0.014381 | 0.065193 | 4.7745 | 123.1888 | 0.65918 | 0.95673 | 121.3669 | 21.2677 | 12.9044 | 14.4379 | 123.349 | 0.61798 | 0.022888 | 0.25177 | 4.1382 | 0.32043 | -1.5701 | -0.018311 | 0.41199 | 4.1153 | 12.2681 | 13.8016 | 120.7306 | 122.5525 | 4.1382 | 122.7127 | 20.6314 | -0.018311 | 122.5525 | 4.1382 | 20.6314 | 120.7306 | 122.7127 | -122.2778 | -122.319
4666.5469 | 122.2549 | -0.51727 | 121.7422 | -0.14458 | 0.028213 | 0.00090794 | 0.017671 | 0.047764 | -0.013954 | 0.065621 | 4.7928 | 123.0469 | 0.55389 | 0.8606 | 121.2204 | 21.3638 | 12.9044 | 14.5889 | 123.175 | 0.47607 | 1.0712 | 1.3046 | 5.3101 | 1.3779 | -0.52185 | 0.99335 | 1.4328 | 4.2389 | 13.4216 | 15.1062 | 121.7377 | 123.5641 | 5.3101 | 123.6923 | 21.8811 | 0.99335 | 123.5641 | 5.3101 | 21.8811 | 121.7377 | 123.6923 | -121.1884 | -121.2662
4668.3125 | 122.3145 | 0.7782 | 123.1338 | -0.12932 | 0.02864 | 0.00069434 | 0.0080578 | 0.047764 | -0.014381 | 0.067116 | 4.2984 | 122.4518 | -0.004578 | 0.56763 | 120.9503 | 21.7346 | 13.4171 | 15.2481 | 122.9141 | 0.19684 | -0.78278 | -0.68207 | 3.5202 | -0.21057 | -2.1835 | -0.58136 | -0.21973 | 4.303 | 12.6389 | 14.4699 | 120.1721 | 121.6736 | 3.5202 | 122.1359 | 20.9564 | -0.58136 | 121.6736 | 3.5202 | 20.9564 | 120.1721 | 122.1359 | -123.1384 | -122.937
4670.0156 | 122.287 | -0.13733 | 122.1725 | -0.13695 | 0.031204 | -0.00037386 | 0.010194 | 0.045414 | -0.012458 | 0.066048 | 4.1748 | 122.1954 | -0.21057 | 0.16022 | 120.4834 | 21.4462 | 12.9593 | 14.8132 | 122.319 | -0.25635 | -0.073242 | 0.022889 | 4.3121 | 0.29755 | -1.6891 | -0.11902 | 0.14648 | 4.3854 | 13.0966 | 14.9506 | 120.6207 | 122.3328 | 4.3121 | 122.4564 | 21.5836 | -0.11902 | 122.3328 | 4.3121 | 21.5836 | 120.6207 | 122.4564 | -122.3831 | -122.4289
4671.7812 | 122.3831 | -0.082397 | 122.1222 | 0.13771 | 0.03334 | 0.0032577 | 0.016389 | 0.047123 | -0.012672 | 0.065407 | 4.1565 | 122.2458 | -0.27466 | 0.054932 | 120.3323 | 21.5195 | 13.2111 | 14.8727 | 122.3557 | -0.27008 | -0.19226 | 0.1236 | 4.2389 | 0.13733 | -1.7899 | -0.18768 | 0.23346 | 4.4312 | 13.2935 | 14.9551 | 120.4147 | 122.3282 | 4.2389 | 122.438 | 21.6019 | -0.18768 | 122.3282 | 4.2389 | 21.6019 | 120.4147 | 122.438 | -122.3969 | -122.3923
4673.5469 | 122.2595 | -0.13275 | 122.1909 | -0.21324 | 0.032699 | 0.0053939 | 0.010835 | 0.045628 | -0.012672 | 0.065621 | 4.303 | 122.2275 | -0.21973 | 0.12817 | 120.4285 | 21.8811 | 13.4903 | 15.3214 | 122.3602 | -0.27008 | -0.086976 | 0.036621 | 4.4357 | 0.26093 | -1.7624 | -0.13733 | 0.16937 | 4.5227 | 13.623 | 15.4541 | 120.5612 | 122.3602 | 4.4357 | 122.493 | 22.0139 | -0.13733 | 122.3602 | 4.4357 | 22.0139 | 120.5612 | 122.493 | -122.4106 | -122.4609
4675.25 | 122.4243 | -0.086975 | 122.113 | 0.046158 | 0.031418 | 0.0038985 | 0.011262 | 0.046482 | -0.012458 | 0.064766 | 4.3304 | 122.2137 | -0.24261 | 0.07782 | 120.3598 | 22.0825 | 13.7695 | 15.4861 | 122.3557 | -0.27008 | -0.15564 | 0.10071 | 4.4174 | 0.16479 | -1.7532 | -0.18311 | 0.24262 | 4.5731 | 13.8565 | 15.5731 | 120.4468 | 122.3007 | 4.4174 | 122.4426 | 22.1695 | -0.18311 | 122.3007 | 4.4174 | 22.1695 | 120.4468 | 122.4426 | -122.3557 | -122.3831
4676.9688 | 122.3373 | -0.091553 | 122.1497 | 0.19112 | 0.033554 | 0.0077437 | 0.01468 | 0.048405 | -0.010109 | 0.066262 | 4.4678 | 122.2092 | -0.20599 | 0.14191 | 120.3552 | 22.3206 | 13.8931 | 15.7471 | 122.3511 | -0.27466 | -0.11444 | 0.059509 | 4.5593 | 0.23346 | -1.7944 | -0.18311 | 0.20142 | 4.6738 | 13.9847 | 15.8386 | 120.4468 | 122.3007 | 4.5593 | 122.4426 | 22.4121 | -0.18311 | 122.3007 | 4.5593 | 22.4121 | 120.4468 | 122.4426 | -122.3557 | -122.4243
4678.7344 | 122.3419 | -0.091553 | 122.1405 | 0.16823 | 0.032058 | 0.0077437 | 0.016389 | 0.045628 | -0.013099 | 0.066475 | 4.5456 | 122.2275 | -0.21057 | 0.14191 | 120.3323 | 22.5449 | 14.1266 | 15.9943 | 122.3557 | -0.24261 | -0.11902 | 0.086975 | 4.6371 | 0.23346 | -1.8082 | -0.15106 | 0.21515 | 4.7562 | 14.2181 | 16.0858 | 120.4239 | 122.319 | 4.6371 | 122.4472 | 22.6364 | -0.15106 | 122.319 | 4.6371 | 22.6364 | 120.4239 | 122.4472 | -122.3511 | -122.3831
4680.5 | 122.3145 | -0.10529 | 122.1634 | -0.25139 | 0.034195 | 0.0079575 | 0.014467 | 0.046696 | -0.012031 | 0.066262 | 4.4769 | 122.2504 | -0.25635 | 0.018311 | 120.2087 | 22.7005 | 14.7446 | 16.1819 | 122.3831 | -0.29755 | -0.15106 | 0.086975 | 4.5822 | 0.1236 | -1.9547 | -0.19226 | 0.21973 | 4.7333 | 14.8499 | 16.2872 | 120.314 | 122.3557 | 4.5822 | 122.4884 | 22.8058 | -0.19226 | 122.3557 | 4.5822 | 22.8058 | 120.314 | 122.4884 | -122.4197 | -122.4609
4682.2812 | 122.3969 | -0.073242 | 122.1313 | 0.14534 | 0.036758 | 0.0085983 | 0.01938 | 0.047978 | -0.013099 | 0.066902 | 4.5731 | 122.2366 | -0.27008 | 0.009155 | 120.1675 | 22.879 | 14.8544 | 16.3193 | 122.3419 | -0.3067 | -0.19684 | 0.10528 | 4.6463 | 0.082397 | -1.9638 | -0.23346 | 0.21057 | 4.8431 | 14.9277 | 16.3925 | 120.2408 | 122.3099 | 4.6463 | 122.4152 | 22.9523 | -0.23346 | 122.3099 | 4.6463 | 22.9523 | 120.2408 | 122.4152 | -122.4014 | -122.4381
4684.0469 | 122.406 | -0.091553 | 122.1359 | 0.12245 | 0.033554 | 0.0075301 | 0.015321 | 0.048191 | -0.014595 | 0.065621 | 4.66 | 122.2275 | -0.25635 | 0.004578 | 120.1538 | 23.0804 | 15.0558 | 16.5344 | 122.374 | -0.29755 | -0.1648 | 0.091553 | 4.7516 | 0.096131 | -1.9821 | -0.20599 | 0.23804 | 4.9164 | 15.1474 | 16.626 | 120.2454 | 122.319 | 4.7516 | 122.4655 | 23.172 | -0.20599 | 122.319 | 4.7516 | 23.172 | 120.2454 | 122.4655 | -122.3923 | -122.4335
4685.7656 | 122.3465 | -0.09613 | 122.1405 | 0.1606 | 0.033981 | 0.0085983 | 0.015321 | 0.049259 | -0.012458 | 0.066689 | 4.7836 | 122.2275 | -0.21057 | 0.091553 | 120.2179 | 23.4512 | 15.1978 | 16.9006 | 122.3373 | -0.25635 | -0.11444 | 0.086975 | 4.8798 | 0.18768 | -1.9226 | -0.16022 | 0.19684 | 4.9942 | 15.2939 | 16.9968 | 120.314 | 122.3236 | 4.8798 | 122.4335 | 23.5474 | -0.16022 | 122.3236 | 4.8798 | 23.5474 | 120.314 | 122.4335 | -122.3511 | -122.3969
4687.5469 | 122.3465 | -0.11902 | 122.1359 | 0.15297 | 0.034408 | 0.0096665 | 0.01233 | 0.048191 | -0.01139 | 0.06733 | 4.8981 | 122.2229 | -0.20142 | 0.10986 | 120.195 | 23.735 | 15.4175 | 17.1982 | 122.3236 | -0.2655 | -0.082397 | 0.086975 | 5.0171 | 0.22888 | -1.9409 | -0.14648 | 0.18768 | 5.0995 | 15.5365 | 17.3172 | 120.314 | 122.3419 | 5.0171 | 122.4426 | 23.8541 | -0.14648 | 122.3419 | 5.0171 | 23.8541 | 120.314 | 122.4426 | -122.3373 | -122.4014
4689.3125 | 122.2504 | -0.1236 | 122.1451 | -0.12169 | 0.035049 | 0.0092391 | 0.015748 | 0.04755 | -0.014381 | 0.066048 | 4.8843 | 122.2275 | -0.26093 | 0.064087 | 120.1263 | 23.8815 | 15.8844 | 17.3996 | 122.3465 | -0.28381 | -0.13733 | 0.082397 | 5.0079 | 0.18768 | -2.0187 | -0.16022 | 0.20142 | 5.1453 | 16.008 | 17.5232 | 120.2499 | 122.3511 | 5.0079 | 122.4701 | 24.0051 | -0.16022 | 122.3511 | 5.0079 | 24.0051 | 120.2499 | 122.4701 | -122.406 | -122.4289
4691.0156 | 122.3099 | -0.12817 | 122.1588 | -0.25902 | 0.03569 | 0.010094 | 0.010835 | 0.043919 | -0.010536 | 0.065621 | 4.8935 | 122.2687 | -0.26093 | 0.009155 | 120.0714 | 23.996 | 16.1362 | 17.514 | 122.3694 | -0.31128 | -0.13275 | 0.10986 | 5.0217 | 0.13733 | -2.0874 | -0.1831 | 0.21057 | 5.1544 | 16.2643 | 17.6422 | 120.1996 | 122.3969 | 5.0217 | 122.4976 | 24.1241 | -0.1831 | 122.3969 | 5.0217 | 24.1241 | 120.1996 | 122.4976 | -122.4197 | -122.4701
4692.7812 | 122.3648 | -0.10986 | 122.1313 | 0.13008 | 0.036758 | 0.0077437 | 0.008485 | 0.048832 | -0.011177 | 0.066475 | 5.0674 | 122.2229 | -0.21515 | 0.082397 | 120.1218 | 24.202 | 16.0584 | 17.6971 | 122.3282 | -0.26093 | -0.10529 | 0.091552 | 5.1773 | 0.19226 | -2.0096 | -0.15106 | 0.19684 | 5.2826 | 16.1682 | 17.807 | 120.2316 | 122.3328 | 5.1773 | 122.438 | 24.3118 | -0.15106 | 122.3328 | 5.1773 | 24.3118 | 120.2316 | 122.438 | -122.3465 | -122.3923
4694.5469 | 122.2366 | -0.14191 | 122.1497 | -0.098801 | 0.036972 | 0.0064621 | 0.016603 | 0.045841 | -0.012886 | 0.066048 | 5.1086 | 122.1954 | -0.25635 | 0.073242 | 120.0485 | 24.3851 | 16.4291 | 17.9031 | 122.374 | -0.29297 | -0.11444 | 0.045777 | 5.2505 | 0.21515 | -2.1011 | -0.15106 | 0.2243 | 5.365 | 16.571 | 18.045 | 120.1904 | 122.3373 | 5.2505 | 122.5159 | 24.527 | -0.15106 | 122.3373 | 5.2505 | 24.527 | 120.1904 | 122.5159 | -122.406 | -122.4426
4696.3125 | 122.3007 | -0.1236 | 122.1451 | -0.16747 | 0.036758 | 0.0021895 | 0.013826 | 0.046696 | -0.01374 | 0.065193 | 5.1407 | 122.2321 | -0.24719 | 0.009155 | 120.0027 | 24.5041 | 16.6718 | 18.0267 | 122.3923 | -0.3067 | -0.1236 | 0.086975 | 5.2643 | 0.13275 | -2.1423 | -0.18311 | 0.24719 | 5.3879 | 16.7953 | 18.1503 | 120.1263 | 122.3557 | 5.2643 | 122.5159 | 24.6277 | -0.18311 | 122.3557 | 5.2643 | 24.6277 | 120.1263 | 122.5159 | -122.3923 | -122.4518
4698.0781 | 122.2641 | -0.14191 | 122.1588 | -0.17509 | 0.037613 | 0.0060349 | 0.01233 | 0.04691 | -0.012672 | 0.064125 | 5.3329 | 122.2046 | -0.21973 | 0.1236 | 120.0623 | 24.8108 | 16.777 | 18.3334 | 122.3328 | -0.26093 | -0.07782 | 0.045777 | 5.4749 | 0.2655 | -2.0966 | -0.11902 | 0.17395 | 5.5527 | 16.9189 | 18.4753 | 120.2042 | 122.3465 | 5.4749 | 122.4747 | 24.9527 | -0.11902 | 122.3465 | 5.4749 | 24.9527 | 120.2042 | 122.4747 | -122.3785 | -122.4197
4699.7812 | 122.3465 | -0.10071 | 122.113 | -0.098801 | 0.035263 | 0.010735 | 0.010408 | 0.045414 | -0.012245 | 0.06498 | 5.365 | 122.2046 | -0.2243 | 0.10986 | 120.0394 | 24.9664 | 16.9052 | 18.5028 | 122.3511 | -0.26093 | -0.1236 | 0.091553 | 5.4657 | 0.21057 | -2.0737 | -0.16022 | 0.23804 | 5.5893 | 17.0059 | 18.6035 | 120.1401 | 122.3053 | 5.4657 | 122.4518 | 25.0671 | -0.16022 | 122.3053 | 5.4657 | 25.0671 | 120.1401 | 122.4518 | -122.3373 | -122.374
4701.5469 | 122.374 | -0.091553 | 122.1085 | 0.084305 | 0.03804 | 0.0081711 | 0.015748 | 0.050114 | -0.013527 | 0.065407 | 5.3375 | 122.2183 | -0.25177 | 0.013733 | 119.8517 | 24.9435 | 17.1341 | 18.425 | 122.3648 | -0.3067 | -0.16022 | 0.10986 | 5.4291 | 0.10529 | -2.2568 | -0.21515 | 0.25635 | 5.5893 | 17.2256 | 18.5165 | 119.9432 | 122.3099 | 5.4291 | 122.4564 | 25.0351 | -0.21515 | 122.3099 | 5.4291 | 25.0351 | 119.9432 | 122.4564 | -122.3602 | -122.4152
4703.3125 | 122.2458 | -0.14191 | 122.1817 | -0.12932 | 0.037826 | 0.010094 | 0.015321 | 0.046482 | -0.013527 | 0.066475 | 5.4565 | 122.2229 | -0.25177 | 0.059509 | 119.9066 | 25.1541 | 17.3172 | 18.6905 | 122.3602 | -0.29297 | -0.10986 | 0.041198 | 5.5984 | 0.20142 | -2.2751 | -0.15106 | 0.17853 | 5.7083 | 17.4591 | 18.8324 | 120.0485 | 122.3648 | 5.5984 | 122.5021 | 25.296 | -0.15106 | 122.3648 | 5.5984 | 25.296 | 120.0485 | 122.5021 | -122.4335 | -122.4747
4705.0781 | 122.3053 | -0.11444 | 122.1451 | -0.24376 | 0.038894 | 0.01223 | 0.014253 | 0.045628 | -0.013313 | 0.064766 | 5.4611 | 122.2687 | -0.27466 | 0.009155 | 119.8654 | 25.2502 | 17.514 | 18.7546 | 122.3694 | -0.31586 | -0.16022 | 0.1236 | 5.5756 | 0.1236 | -2.2797 | -0.20142 | 0.2243 | 5.7358 | 17.6285 | 18.869 | 119.9799 | 122.3831 | 5.5756 | 122.4838 | 25.3647 | -0.20142 | 122.3831 | 5.5756 | 25.3647 | 119.9799 | 122.4838 | -122.4197 | -122.4609
4706.7812 | 122.3511 | -0.086975 | 122.1268 | 0.17586 | 0.037826 | 0.0092391 | 0.01703 | 0.047764 | -0.011818 | 0.066689 | 5.5344 | 122.1909 | -0.25177 | 0.045776 | 119.838 | 25.4059 | 17.4637 | 18.837 | 122.3465 | -0.27008 | -0.16479 | 0.064087 | 5.6213 | 0.13275 | -2.2888 | -0.18311 | 0.21973 | 5.7861 | 17.5507 | 18.9239 | 119.9249 | 122.2778 | 5.6213 | 122.4335 | 25.4929 | -0.18311 | 122.2778 | 5.6213 | 25.4929 | 119.9249 | 122.4335 | -122.3785 | -122.3969
4708.5469 | 122.3145 | -0.11444 | 122.113 | 0.069046 | 0.040176 | 0.013298 | 0.013826 | 0.048191 | -0.015449 | 0.065407 | 5.5756 | 122.2229 | -0.27466 | 0.009155 | 119.7647 | 25.4562 | 17.6147 | 18.8553 | 122.3511 | -0.30212 | -0.16022 | 0.10986 | 5.69 | 0.1236 | -2.3483 | -0.18768 | 0.23804 | 5.8502 | 17.7292 | 18.9697 | 119.8791 | 122.3373 | 5.69 | 122.4655 | 25.5707 | -0.18768 | 122.3373 | 5.69 | 25.5707 | 119.8791 | 122.4655 | -122.3877 | -122.4152
4710.25 | 122.287 | -0.13275 | 122.1497 | -0.24376 | 0.039535 | 0.0079575 | 0.0097668 | 0.045841 | -0.011818 | 0.066048 | 5.658 | 122.2092 | -0.23346 | 0.036621 | 119.7876 | 25.6348 | 17.7979 | 19.0659 | 122.3831 | -0.28839 | -0.10071 | 0.059509 | 5.7907 | 0.16937 | -2.3621 | -0.15564 | 0.23346 | 5.8914 | 17.9306 | 19.1986 | 119.9203 | 122.3419 | 5.7907 | 122.5159 | 25.7675 | -0.15564 | 122.3419 | 5.7907 | 25.7675 | 119.9203 | 122.5159 | -122.3831 | -122.438
4712.0312 | 122.3694 | -0.086975 | 122.1176 | 0.099564 | 0.039962 | 0.011162 | 0.014467 | 0.049687 | -0.015449 | 0.066048 | 5.7175 | 122.2 | -0.27008 | 0.004578 | 119.7327 | 25.6989 | 17.8345 | 19.075 | 122.3694 | -0.29297 | -0.18311 | 0.082397 | 5.8044 | 0.091553 | -2.3849 | -0.20599 | 0.25177 | 5.9875 | 17.9214 | 19.162 | 119.8196 | 122.287 | 5.8044 | 122.4564 | 25.7858 | -0.20599 | 122.287 | 5.8044 | 25.7858 | 119.8196 | 122.4564 | -122.3877 | -122.4106
4713.7812 | 122.3785 | -0.11444 | 122.1039 | 0.030899 | 0.038253 | 0.013512 | 0.008485 | 0.046269 | -0.009895 | 0.066689 | 5.7999 | 122.1817 | -0.22888 | 0.050354 | 119.751 | 25.9094 | 17.8711 | 19.2535 | 122.3053 | -0.27924 | -0.11444 | 0.07782 | 5.9143 | 0.16479 | -2.3529 | -0.16479 | 0.20142 | 6.0287 | 17.9855 | 19.368 | 119.8654 | 122.2961 | 5.9143 | 122.4197 | 26.0239 | -0.16479 | 122.2961 | 5.9143 | 26.0239 | 119.8654 | 122.4197 | -122.3328 | -122.3831
4715.5469 | 122.2549 | -0.13275 | 122.1359 | -0.15984 | 0.040176 | 0.0096665 | 0.010621 | 0.04691 | -0.011177 | 0.065834 | 5.8685 | 122.1771 | -0.2243 | 0.10986 | 119.7784 | 26.0605 | 17.9855 | 19.4092 | 122.319 | -0.27924 | -0.091553 | 0.041199 | 6.0013 | 0.24261 | -2.3575 | -0.14648 | 0.18311 | 6.0928 | 18.1183 | 19.5419 | 119.9112 | 122.3099 | 6.0013 | 122.4518 | 26.1932 | -0.14648 | 122.3099 | 6.0013 | 26.1932 | 119.9112 | 122.4518 | -122.3602 | -122.4152
4717.3438 | 122.3328 | -0.1236 | 122.1176 | 0.17586 | 0.041244 | 0.013725 | 0.013185 | 0.047978 | -0.011604 | 0.064553 | 5.9418 | 122.1954 | -0.21515 | 0.11444 | 119.7189 | 26.1932 | 17.9718 | 19.4687 | 122.3099 | -0.26093 | -0.091553 | 0.07782 | 6.0654 | 0.23804 | -2.3987 | -0.13733 | 0.19226 | 6.1569 | 18.0954 | 19.5923 | 119.8425 | 122.319 | 6.0654 | 122.4335 | 26.3168 | -0.13733 | 122.319 | 6.0654 | 26.3168 | 119.8425 | 122.4335 | -122.3328 | -122.3785
4719.1094 | 122.2961 | -0.12817 | 122.113 | -0.25139 | 0.041885 | 0.0083847 | 0.015535 | 0.046055 | -0.014595 | 0.065407 | 5.809 | 122.2229 | -0.2655 | 0.004578 | 119.5908 | 26.2344 | 18.3884 | 19.5053 | 122.3557 | -0.31586 | -0.13733 | 0.10986 | 5.9372 | 0.13275 | -2.5223 | -0.18768 | 0.24262 | 6.0745 | 18.5165 | 19.6335 | 119.7189 | 122.3511 | 5.9372 | 122.4838 | 26.3626 | -0.18768 | 122.3511 | 5.9372 | 26.3626 | 119.7189 | 122.4838 | -122.3785 | -122.4289
4720.8125 | 122.2366 | -0.14648 | 122.1451 | -0.21324 | 0.040176 | 0.0088119 | 0.010408 | 0.044773 | -0.011818 | 0.067116 | 5.983 | 122.2 | -0.20599 | 0.1236 | 119.7006 | 26.5091 | 18.3105 | 19.7754 | 122.3373 | -0.24719 | -0.05951 | 0.054931 | 6.1295 | 0.27008 | -2.4445 | -0.10071 | 0.19226 | 6.189 | 18.457 | 19.9219 | 119.8471 | 122.3465 | 6.1295 | 122.4838 | 26.6556 | -0.10071 | 122.3465 | 6.1295 | 26.6556 | 119.8471 | 122.4838 | -122.3511 | -122.3923
4722.6094 | 122.3648 | -0.10529 | 122.1176 | 0.053787 | 0.04274 | 0.011375 | 0.011476 | 0.047337 | -0.012245 | 0.065834 | 5.9875 | 122.1954 | -0.21057 | 0.064087 | 119.6045 | 26.619 | 18.4021 | 19.7617 | 122.2778 | -0.28381 | -0.10529 | 0.07782 | 6.0928 | 0.16937 | -2.5131 | -0.17853 | 0.16022 | 6.1981 | 18.5074 | 19.8669 | 119.7098 | 122.3007 | 6.0928 | 122.3831 | 26.7242 | -0.17853 | 122.3007 | 6.0928 | 26.7242 | 119.7098 | 122.3831 | -122.3282 | -122.4014
4724.3125 | 122.3785 | -0.10071 | 122.0901 | 0.084305 | 0.041885 | 0.0090255 | 0.013612 | 0.048191 | -0.011818 | 0.066689 | 6.0425 | 122.168 | -0.22888 | 0.064087 | 119.5724 | 26.7563 | 18.5303 | 19.8624 | 122.2961 | -0.27924 | -0.12817 | 0.07782 | 6.1432 | 0.1648 | -2.5177 | -0.17853 | 0.20599 | 6.2714 | 18.631 | 19.9631 | 119.6732 | 122.2687 | 6.1432 | 122.3969 | 26.857 | -0.17853 | 122.2687 | 6.1432 | 26.857 | 119.6732 | 122.3969 | -122.319 | -122.3694
4726.0781 | 122.2916 | -0.12817 | 122.113 | -0.25139 | 0.042953 | 0.010735 | 0.014467 | 0.046055 | -0.01374 | 0.064553 | 6.0837 | 122.1863 | -0.27924 | 0.022888 | 119.4626 | 26.8387 | 18.8736 | 19.931 | 122.3419 | -0.32044 | -0.15106 | 0.073242 | 6.2119 | 0.15106 | -2.6505 | -0.19226 | 0.22888 | 6.3629 | 19.0018 | 20.0592 | 119.5908 | 122.3145 | 6.2119 | 122.4701 | 26.9669 | -0.19226 | 122.3145 | 6.2119 | 26.9669 | 119.5908 | 122.4701 | -122.3923 | -122.4335
4727.8594 | 122.2412 | -0.15106 | 122.1542 | -0.19035 | 0.042953 | 0.011803 | 0.013185 | 0.044773 | -0.013527 | 0.065834 | 6.2622 | 122.1817 | -0.2243 | 0.13733 | 119.5587 | 27.1271 | 18.8141 | 20.1874 | 122.2824 | -0.2655 | -0.073242 | 0.027466 | 6.4133 | 0.28839 | -2.5955 | -0.11444 | 0.12817 | 6.4865 | 18.9651 | 20.3384 | 119.7098 | 122.3328 | 6.4133 | 122.4335 | 27.2781 | -0.11444 | 122.3328 | 6.4133 | 27.2781 | 119.7098 | 122.4335 | -122.3785 | -122.4197
4729.6406 | 122.3236 | -0.10071 | 122.049 | 0.15297 | 0.044235 | 0.016502 | 0.017671 | 0.049046 | -0.013527 | 0.066689 | 6.2759 | 122.1725 | -0.24261 | 0.064087 | 119.4534 | 27.2141 | 18.8644 | 20.1828 | 122.3236 | -0.28839 | -0.14191 | 0.1236 | 6.3766 | 0.1648 | -2.5955 | -0.18768 | 0.27466 | 6.5186 | 18.9651 | 20.2835 | 119.5541 | 122.2733 | 6.3766 | 122.4243 | 27.3148 | -0.18768 | 122.2733 | 6.3766 | 27.3148 | 119.5541 | 122.4243 | -122.2916 | -122.3373
4731.4062 | 122.3053 | -0.1236 | 122.0856 | 0.076676 | 0.045944 | 0.016289 | 0.01703 | 0.045414 | -0.014381 | 0.066262 | 6.2622 | 122.1909 | -0.28381 | 0 | 119.3436 | 27.2598 | 19.1299 | 20.1553 | 122.3282 | -0.32044 | -0.16022 | 0.10529 | 6.3858 | 0.1236 | -2.742 | -0.19684 | 0.24262 | 6.546 | 19.2535 | 20.2789 | 119.4672 | 122.3145 | 6.3858 | 122.4518 | 27.3834 | -0.19684 | 122.3145 | 6.3858 | 27.3834 | 119.4672 | 122.4518 | -122.3694 | -122.406
4733.1094 | 122.3099 | -0.10071 | 122.113 | 0.16823 | 0.045303 | 0.014793 | 0.013398 | 0.048405 | -0.012031 | 0.066902 | 6.4041 | 122.1588 | -0.21057 | 0.10986 | 119.4397 | 27.5482 | 19.0247 | 20.3934 | 122.2961 | -0.24719 | -0.10986 | 0.045776 | 6.5048 | 0.21057 | -2.6733 | -0.14648 | 0.18311 | 6.6147 | 19.1254 | 20.4941 | 119.5404 | 122.2595 | 6.5048 | 122.3969 | 27.6489 | -0.14648 | 122.2595 | 6.5048 | 27.6489 | 119.5404 | 122.3969 | -122.3236 | -122.3602
4734.8125 | 122.3007 | -0.11444 | 122.0764 | 0.061417 | 0.045303 | 0.012444 | 0.012117 | 0.046482 | -0.014808 | 0.064125 | 6.4957 | 122.168 | -0.22888 | 0.10071 | 119.3848 | 27.6215 | 19.0933 | 20.3934 | 122.2824 | -0.27924 | -0.11444 | 0.091553 | 6.6101 | 0.21515 | -2.6916 | -0.16479 | 0.20599 | 6.7245 | 19.2078 | 20.5078 | 119.4992 | 122.2824 | 6.6101 | 122.3969 | 27.7359 | -0.16479 | 122.2824 | 6.6101 | 27.7359 | 119.4992 | 122.3969 | -122.3053 | -122.3557
4736.5625 | 122.2824 | -0.1236 | 122.113 | -0.12169 | 0.045517 | 0.015007 | 0.0089124 | 0.046696 | -0.011818 | 0.066475 | 6.5689 | 122.1725 | -0.21515 | 0.11444 | 119.3893 | 27.7908 | 19.2764 | 20.549 | 122.287 | -0.27924 | -0.091553 | 0.059509 | 6.6925 | 0.23804 | -2.7237 | -0.15564 | 0.17395 | 6.7841 | 19.4 | 20.6726 | 119.5129 | 122.2961 | 6.6925 | 122.4106 | 27.9144 | -0.15564 | 122.2961 | 6.6925 | 27.9144 | 119.5129 | 122.4106 | -122.3282 | -122.3923
4738.3281 | 122.3648 | -0.09613 | 122.0673 | 0.0080111 | 0.046158 | 0.014793 | 0.012544 | 0.044132 | -0.010322 | 0.064766 | 6.5964 | 122.168 | -0.21973 | 0.054932 | 119.2841 | 27.8824 | 19.4275 | 20.549 | 122.3282 | -0.28839 | -0.1236 | 0.10071 | 6.6925 | 0.15106 | -2.7832 | -0.19226 | 0.26093 | 6.8161 | 19.5236 | 20.6451 | 119.3802 | 122.2641 | 6.6925 | 122.4243 | 27.9785 | -0.19226 | 122.2641 | 6.6925 | 27.9785 | 119.3802 | 122.4243 | -122.287 | -122.3557
4740.0312 | 122.3648 | -0.10986 | 122.0856 | 0.00038159 | 0.046158 | 0.016502 | 0.012971 | 0.045414 | -0.012672 | 0.065834 | 6.633 | 122.1863 | -0.23804 | 0.064087 | 119.2566 | 28.0289 | 19.5374 | 20.6406 | 122.2824 | -0.29755 | -0.12817 | 0.10071 | 6.7429 | 0.17395 | -2.829 | -0.18768 | 0.19684 | 6.871 | 19.6472 | 20.7504 | 119.3665 | 122.2961 | 6.7429 | 122.3923 | 28.1387 | -0.18768 | 122.2961 | 6.7429 | 28.1387 | 119.3665 | 122.3923 | -122.3236 | -122.3831
4741.7812 | 122.2641 | -0.14191 | 122.113 | -0.25902 | 0.047867 | 0.018639 | 0.015535 | 0.046482 | -0.013099 | 0.065407 | 6.5414 | 122.1954 | -0.25635 | 0.045776 | 119.1834 | 28.0701 | 19.7159 | 20.6589 | 122.3282 | -0.29755 | -0.11444 | 0.082398 | 6.6833 | 0.18768 | -2.9297 | -0.15564 | 0.21515 | 6.7978 | 19.8578 | 20.8008 | 119.3253 | 122.3373 | 6.6833 | 122.4701 | 28.212 | -0.15564 | 122.3373 | 6.6833 | 28.212 | 119.3253 | 122.4701 | -122.3694 | -122.4106
4743.4844 | 122.2549 | -0.13275 | 122.1313 | -0.25139 | 0.047653 | 0.014153 | 0.013185 | 0.042851 | -0.012245 | 0.064125 | 6.5414 | 122.2 | -0.2655 | 0.054932 | 119.1467 | 28.2166 | 19.8532 | 20.7413 | 122.319 | -0.29755 | -0.13275 | 0.068664 | 6.6742 | 0.18768 | -2.9846 | -0.16479 | 0.18768 | 6.8069 | 19.986 | 20.874 | 119.2795 | 122.3328 | 6.6742 | 122.4518 | 28.3493 | -0.16479 | 122.3328 | 6.6742 | 28.3493 | 119.2795 | 122.4518 | -122.3969 | -122.4289
4745.25 | 122.2229 | -0.15106 | 122.081 | -0.075912 | 0.047867 | 0.017784 | 0.018098 | 0.047123 | -0.012245 | 0.065834 | 6.6971 | 122.1634 | -0.27924 | 0.073242 | 119.1101 | 28.4134 | 19.9036 | 20.8466 | 122.3099 | -0.31128 | -0.12817 | 0.082397 | 6.8481 | 0.2243 | -2.9709 | -0.16022 | 0.22888 | 6.9763 | 20.0546 | 20.9976 | 119.2612 | 122.3145 | 6.8481 | 122.4609 | 28.5645 | -0.16022 | 122.3145 | 6.8481 | 28.5645 | 119.2612 | 122.4609 | -122.3602 | -122.3923
4747.0156 | 122.319 | -0.09613 | 122.0535 | 0.1606 | 0.050216 | 0.020775 | 0.016816 | 0.049046 | -0.01139 | 0.06797 | 6.5369 | 122.1909 | -0.27008 | 0.036621 | 119.0689 | 28.537 | 19.899 | 20.8694 | 122.2961 | -0.30212 | -0.17395 | 0.13733 | 6.633 | 0.13275 | -2.9846 | -0.20599 | 0.24262 | 6.8069 | 19.9951 | 20.9656 | 119.165 | 122.287 | 6.633 | 122.3923 | 28.6331 | -0.20599 | 122.287 | 6.633 | 28.6331 | 119.165 | 122.3923 | -122.3236 | -122.3557
4748.7969 | 122.2595 | -0.14191 | 122.0993 | -0.24376 | 0.04808 | 0.017998 | 0.014039 | 0.045628 | -0.014167 | 0.065407 | 6.5826 | 122.2 | -0.27008 | 0 | 119.0048 | 28.7018 | 20.2103 | 20.993 | 122.2916 | -0.33875 | -0.12817 | 0.10071 | 6.7245 | 0.14191 | -3.0945 | -0.19684 | 0.19226 | 6.8527 | 20.3522 | 21.1349 | 119.1467 | 122.3419 | 6.7245 | 122.4335 | 28.8437 | -0.19684 | 122.3419 | 6.7245 | 28.8437 | 119.1467 | 122.4335 | -122.3694 | -122.438
4750.5 | 122.2275 | -0.15564 | 122.1359 | -0.18272 | 0.047439 | 0.012016 | 0.01233 | 0.04691 | -0.010963 | 0.066048 | 6.8024 | 122.1725 | -0.2243 | 0.082397 | 119.0506 | 28.9993 | 20.2469 | 21.2357 | 122.287 | -0.28839 | -0.068664 | 0.036621 | 6.958 | 0.23804 | -3.0853 | -0.13275 | 0.15106 | 7.0267 | 20.4025 | 21.3913 | 119.2062 | 122.3282 | 6.958 | 122.4426 | 29.155 | -0.13275 | 122.3282 | 6.958 | 29.155 | 119.2062 | 122.4426 | -122.3602 | -122.4243
4752.2656 | 122.2961 | -0.1236 | 122.0856 | 0.18349 | 0.051071 | 0.023552 | 0.01468 | 0.04755 | -0.010109 | 0.067543 | 6.9992 | 122.0856 | -0.21973 | 0.09613 | 119.0277 | 29.1687 | 20.1645 | 21.2631 | 122.2595 | -0.26093 | -0.096131 | 0 | 7.1228 | 0.21973 | -3.0579 | -0.13733 | 0.17395 | 7.2189 | 20.2881 | 21.3867 | 119.1513 | 122.2092 | 7.1228 | 122.3831 | 29.2923 | -0.13733 | 122.2092 | 7.1228 | 29.2923 | 119.1513 | 122.3831 | -122.3053 | -122.3465
4754.0312 | 122.2961 | -0.11902 | 122.0947 | -0.091171 | 0.052993 | 0.023125 | 0.0082714 | 0.044987 | -0.012031 | 0.065834 | 7.2556 | 122.1634 | -0.24261 | 0.10986 | 119.0094 | 29.3106 | 20.3064 | 21.3181 | 122.2824 | -0.27924 | -0.1236 | 0.068664 | 7.3746 | 0.22888 | -3.0853 | -0.16022 | 0.18768 | 7.4982 | 20.4254 | 21.4371 | 119.1284 | 122.2824 | 7.3746 | 122.4014 | 29.4296 | -0.16022 | 122.2824 | 7.3746 | 29.4296 | 119.1284 | 122.4014 | -122.3373 | -122.374
4755.7344 | 122.2916 | -0.10986 | 122.0535 | 0.11482 | 0.052353 | 0.024406 | 0.015962 | 0.047123 | -0.010963 | 0.066262 | 6.8527 | 122.1542 | -0.22888 | 0.11444 | 118.9499 | 29.5303 | 20.3842 | 21.3867 | 122.2961 | -0.27008 | -0.11902 | 0.10071 | 6.9626 | 0.2243 | -3.1036 | -0.16022 | 0.24262 | 7.0816 | 20.4941 | 21.4966 | 119.0598 | 122.2641 | 6.9626 | 122.406 | 29.6402 | -0.16022 | 122.2641 | 6.9626 | 29.6402 | 119.0598 | 122.406 | -122.2824 | -122.3236
4757.5 | 122.2137 | -0.14191 | 122.0856 | -0.15984 | 0.052566 | 0.017784 | 0.013398 | 0.046269 | -0.010109 | 0.066902 | 6.8298 | 122.1451 | -0.23804 | 0.1236 | 118.9453 | 29.7638 | 20.5902 | 21.5515 | 122.2687 | -0.29297 | -0.09613 | 0.05951 | 6.9717 | 0.2655 | -3.1403 | -0.15106 | 0.18311 | 7.0679 | 20.7321 | 21.6934 | 119.0872 | 122.287 | 6.9717 | 122.4106 | 29.9057 | -0.15106 | 122.287 | 6.9717 | 29.9057 | 119.0872 | 122.4106 | -122.3236 | -122.3785
4759.25 | 122.2229 | -0.14648 | 122.0764 | -0.27428 | 0.054275 | 0.021843 | 0.01468 | 0.045628 | -0.012458 | 0.064553 | 6.6559 | 122.1497 | -0.23804 | 0.068665 | 118.8492 | 29.8599 | 20.8054 | 21.5744 | 122.2733 | -0.29297 | -0.091553 | 0.073242 | 6.8024 | 0.21515 | -3.2272 | -0.14648 | 0.19684 | 6.8939 | 20.9518 | 21.7209 | 118.9957 | 122.2961 | 6.8024 | 122.4197 | 30.0064 | -0.14648 | 122.2961 | 6.8024 | 30.0064 | 118.9957 | 122.4197 | -122.3145 | -122.3694
4761.0156 | 122.3099 | -0.13275 | 122.0306 | 0.10719 | 0.054702 | 0.018639 | 0.014467 | 0.046482 | -0.0090406 | 0.06498 | 6.6101 | 122.1268 | -0.21973 | 0.073242 | 118.7805 | 30.0476 | 20.7687 | 21.6293 | 122.2458 | -0.28381 | -0.086976 | 0.09613 | 6.7429 | 0.20599 | -3.2501 | -0.15106 | 0.21515 | 6.8298 | 20.9015 | 21.7621 | 118.9133 | 122.2595 | 6.7429 | 122.3785 | 30.1804 | -0.15106 | 122.2595 | 6.7429 | 30.1804 | 118.9133 | 122.3785 | -122.2504 | -122.3145
4762.7969 | 122.1909 | -0.15106 | 122.0581 | -0.060654 | 0.05278 | 0.022698 | 0.018312 | 0.043064 | -0.016731 | 0.06797 | 6.8848 | 122.113 | -0.25635 | 0.054932 | 118.6981 | 30.2353 | 21.0297 | 21.6797 | 122.319 | -0.29755 | -0.10529 | 0.054932 | 7.0358 | 0.20599 | -3.36 | -0.14648 | 0.26093 | 7.1411 | 21.1807 | 21.8307 | 118.8492 | 122.2641 | 7.0358 | 122.4701 | 30.3864 | -0.14648 | 122.2641 | 7.0358 | 30.3864 | 118.8492 | 122.4701 | -122.3145 | -122.3557
4764.5625 | 122.2916 | -0.1236 | 122.0352 | -0.068283 | 0.052139 | 0.023552 | 0.011262 | 0.045201 | -0.0092542 | 0.066048 | 6.9626 | 122.1497 | -0.23346 | 0.091553 | 118.7439 | 30.4413 | 20.993 | 21.8216 | 122.2321 | -0.29755 | -0.10986 | 0.11444 | 7.0862 | 0.21515 | -3.2913 | -0.17395 | 0.19684 | 7.196 | 21.1166 | 21.9452 | 118.8675 | 122.2733 | 7.0862 | 122.3557 | 30.5649 | -0.17395 | 122.2733 | 7.0862 | 30.5649 | 118.8675 | 122.3557 | -122.2687 | -122.3328
4766.2656 | 117.9977 | -0.10986 | 117.8375 | 0.32845 | 7.0207 | 6.977 | 0.017671 | 0.042423 | -0.020576 | 0.067116 | 2.2064 | 105.13 | 2.124 | 0.07782 | 112.912 | 26.7792 | 20.5948 | 21.2219 | 116.4825 | 0.20142 | 2.2339 | -12.7075 | 2.3163 | 0.18768 | -4.9255 | 0.31128 | -1.355 | 0.082398 | 20.7047 | 21.3318 | 113.0219 | 105.2399 | 2.3163 | 116.5924 | 26.889 | 0.31128 | 105.2399 | 2.3163 | 26.889 | 113.0219 | 116.5924 | -115.7135 | -117.6361
4768.0312 | 122.1313 | -0.15564 | 122.049 | -0.091171 | 0.013046 | -0.014046 | 0.018953 | 0.047764 | -0.014167 | 0.06733 | 0.6546 | 0.86517 | 0.48523 | 0.064087 | 118.4875 | 28.6789 | 20.0684 | 20.668 | 122.287 | -0.3067 | 0.64087 | -121.1838 | 0.81024 | 0.21973 | -3.5614 | -0.15106 | 0.23804 | 0.16937 | 20.224 | 20.8237 | 118.6432 | 1.0208 | 0.81024 | 122.4426 | 28.8345 | -0.15106 | 1.0208 | 0.81024 | 28.8345 | 118.6432 | 122.4426 | -121.5637 | -122.3557
4769.8125 | 122.1725 | -0.16022 | 122.0673 | -0.068283 | 0.014541 | -0.014473 | 0.015748 | 0.049687 | -0.01609 | 0.06498 | 0.64545 | 0.8194 | 0.45319 | 0.041199 | 118.4509 | 28.8345 | 20.1324 | 20.7184 | 122.287 | -0.29297 | 0.6134 | -121.2479 | 0.80566 | 0.20142 | -3.6163 | -0.13275 | 0.21973 | 0.19226 | 20.2927 | 20.8786 | 118.6111 | 0.97961 | 0.80566 | 122.4472 | 28.9948 | -0.13275 | 0.97961 | 0.80566 | 28.9948 | 118.6111 | 122.4472 | -121.6141 | -122.3602
4771.5156 | 122.2137 | -0.13275 | 122.0718 | -0.17509 | 0.014541 | -0.018959 | 0.009126 | 0.046696 | -0.012245 | 0.067116 | 0.67749 | 0.79193 | 0.47607 | 0.10071 | 118.4967 | 29.1367 | 20.1324 | 20.9061 | 122.2137 | -0.28839 | 0.60882 | -121.2799 | 0.81024 | 0.23346 | -3.5751 | -0.15564 | 0.14191 | 0.20142 | 20.2652 | 21.0388 | 118.6295 | 0.92468 | 0.81024 | 122.3465 | 29.2694 | -0.15564 | 0.92468 | 0.81024 | 29.2694 | 118.6295 | 122.3465 | -121.5958 | -122.3602
4773.2812 | 122.2504 | -0.11902 | 122.0306 | 0.19112 | 0.016678 | -0.016182 | 0.016603 | 0.047978 | -0.011818 | 0.066475 | 0.61798 | 0.7782 | 0.46234 | 0.073242 | 118.3777 | 29.2648 | 20.2103 | 20.9015 | 122.2183 | -0.27466 | 0.58136 | -121.2524 | 0.737 | 0.19226 | -3.653 | -0.15564 | 0.18768 | 0.15564 | 20.3293 | 21.0205 | 118.4967 | 0.89722 | 0.737 | 122.3373 | 29.3839 | -0.15564 | 0.89722 | 0.737 | 29.3839 | 118.4967 | 122.3373 | -121.5683 | -122.3053
4775.0625 | 122.1405 | -0.14191 | 122.0306 | -0.15984 | 0.015182 | -0.0102 | 0.018312 | 0.047337 | -0.012245 | 0.068398 | 0.60883 | 0.8194 | 0.43945 | 0.032043 | 118.309 | 29.4342 | 20.4117 | 20.9198 | 122.2183 | -0.32501 | 0.58136 | -121.2112 | 0.75073 | 0.17395 | -3.7216 | -0.18311 | 0.18768 | 0.16937 | 20.5536 | 21.0617 | 118.4509 | 0.9613 | 0.75073 | 122.3602 | 29.5761 | -0.18311 | 0.9613 | 0.75073 | 29.5761 | 118.4509 | 122.3602 | -121.5912 | -122.3557
4776.7656 | 122.1634 | -0.13733 | 122.0261 | -0.25139 | 0.015396 | -0.013618 | 0.012758 | 0.04456 | -0.012031 | 0.06797 | 0.66834 | 0.78735 | 0.48523 | 0.073242 | 118.277 | 29.6951 | 20.4803 | 21.0571 | 122.2046 | -0.31586 | 0.62256 | -121.2387 | 0.80566 | 0.21057 | -3.7491 | -0.17853 | 0.17853 | 0.18311 | 20.6177 | 21.1945 | 118.4143 | 0.92468 | 0.80566 | 122.3419 | 29.8325 | -0.17853 | 0.92468 | 0.80566 | 29.8325 | 118.4143 | 122.3419 | -121.5408 | -122.3419
4778.5312 | 122.1771 | -0.1236 | 121.9345 | 0.11482 | 0.012619 | -0.013618 | 0.012117 | 0.047337 | -0.010963 | 0.066475 | 0.63171 | 0.75531 | 0.45776 | 0.068665 | 118.1534 | 29.8691 | 20.3705 | 21.0342 | 122.1405 | -0.25635 | 0.58136 | -121.1792 | 0.75531 | 0.19226 | -3.7811 | -0.13275 | 0.20599 | 0.17395 | 20.4941 | 21.1578 | 118.277 | 0.87891 | 0.75531 | 122.2641 | 29.9927 | -0.13275 | 0.87891 | 0.75531 | 29.9927 | 118.277 | 122.2641 | -121.4767 | -122.1909
4780.2344 | 122.2458 | -0.10986 | 121.9528 | 0.091934 | 0.015182 | -0.013405 | 0.01938 | 0.047978 | -0.01374 | 0.067543 | 0.55389 | 0.81024 | 0.41657 | -0.004578 | 118.0664 | 29.9835 | 20.636 | 21.0114 | 122.2092 | -0.31586 | 0.52643 | -121.1426 | 0.66376 | 0.10529 | -3.8864 | -0.20599 | 0.25635 | 0.13733 | 20.7458 | 21.1212 | 118.1763 | 0.92011 | 0.66376 | 122.319 | 30.0934 | -0.20599 | 0.92011 | 0.66376 | 30.0934 | 118.1763 | 122.319 | -121.5363 | -122.2687
4782 | 122.1222 | -0.15564 | 121.994 | -0.20561 | 0.017318 | -0.014046 | 0.010835 | 0.046482 | -0.012458 | 0.066902 | 0.66376 | 0.74158 | 0.47607 | 0.10071 | 118.1396 | 30.3497 | 20.6589 | 21.2997 | 122.1725 | -0.27008 | 0.63171 | -121.2524 | 0.8194 | 0.25635 | -3.8544 | -0.11444 | 0.17853 | 0.18768 | 20.8145 | 21.4554 | 118.2953 | 0.89722 | 0.8194 | 122.3282 | 30.5054 | -0.11444 | 0.89722 | 0.8194 | 30.5054 | 118.2953 | 122.3282 | -121.5179 | -122.2641
4783.7656 | 122.113 | -0.14191 | 121.9391 | -0.2285 | 0.015182 | -0.0080643 | 0.014894 | 0.045414 | -0.010963 | 0.067543 | 0.56763 | 0.81024 | 0.43945 | 0.009155 | 117.9428 | 30.3864 | 20.8923 | 21.2265 | 122.1909 | -0.34332 | 0.58136 | -121.1288 | 0.70953 | 0.15106 | -3.9963 | -0.20142 | 0.25177 | 0.12817 | 21.0342 | 21.3684 | 118.0847 | 0.95215 | 0.70953 | 122.3328 | 30.5283 | -0.20142 | 0.95215 | 0.70953 | 30.5283 | 118.0847 | 122.3328 | -121.4996 | -122.2824
4785.4531 | 122.1222 | -0.11444 | 121.8704 | 0.18349 | 0.01625 | -0.015541 | 0.015748 | 0.047764 | -0.01374 | 0.06797 | 0.6134 | 0.7782 | 0.44861 | 0.041199 | 117.9108 | 30.6564 | 20.7504 | 21.2723 | 122.1359 | -0.28381 | 0.56305 | -121.0922 | 0.72784 | 0.15564 | -3.9597 | -0.16937 | 0.2655 | 0.1648 | 20.8649 | 21.3867 | 118.0252 | 0.89264 | 0.72784 | 122.2504 | 30.7709 | -0.16937 | 0.89264 | 0.72784 | 30.7709 | 118.0252 | 122.2504 | -121.4218 | -122.1542
4787.2188 | 121.9391 | -0.1236 | 121.788 | -0.18272 | 0.015182 | -0.015327 | 0.014467 | 0.047764 | -0.01374 | 0.066048 | 0.59509 | 0.78278 | 0.43488 | 0.018311 | 117.746 | 30.7846 | 20.9839 | 21.3089 | 122.0673 | -0.3067 | 0.55847 | -121.0052 | 0.71869 | 0.14191 | -4.0421 | -0.18311 | 0.27924 | 0.16022 | 21.1075 | 21.4325 | 117.8696 | 0.90637 | 0.71869 | 122.1909 | 30.9082 | -0.18311 | 0.90637 | 0.71869 | 30.9082 | 117.8696 | 122.1909 | -121.3531 | -122.0947
4788.9219 | 121.9254 | -0.086975 | 121.7377 | 0.14534 | 0.016678 | -0.012337 | 0.015321 | 0.048619 | -0.011818 | 0.06797 | 0.59052 | 0.81024 | 0.4303 | 0.018311 | 117.6498 | 30.9402 | 20.9015 | 21.3318 | 121.9711 | -0.31586 | 0.51727 | -120.9274 | 0.67749 | 0.10529 | -4.0878 | -0.22888 | 0.23346 | 0.16022 | 20.9885 | 21.4188 | 117.7368 | 0.89722 | 0.67749 | 122.0581 | 31.0272 | -0.22888 | 0.89722 | 0.67749 | 31.0272 | 117.7368 | 122.0581 | -121.3074 | -122.0535
4790.6875 | 121.8384 | -0.091553 | 121.55 | -0.0072479 | 0.01625 | -0.012123 | 0.007417 | 0.044987 | -0.0083996 | 0.064125 | 0.61798 | 0.75531 | 0.46234 | 0.054932 | 117.485 | 31.1691 | 20.9015 | 21.3638 | 121.7743 | -0.29297 | 0.55389 | -120.7947 | 0.70953 | 0.14649 | -4.0649 | -0.20142 | 0.2243 | 0.15564 | 20.993 | 21.4554 | 117.5766 | 0.84686 | 0.70953 | 121.8658 | 31.2607 | -0.20142 | 0.84686 | 0.70953 | 31.2607 | 117.5766 | 121.8658 | -121.0876 | -121.843
4792.4062 | 121.7102 | -0.13733 | 121.4676 | 0.0080111 | 0.013473 | -0.012123 | 0.019593 | 0.046055 | -0.014808 | 0.06733 | 0.59967 | 0.77362 | 0.42572 | 0.018311 | 117.2424 | 31.2515 | 21.0663 | 21.3364 | 121.7285 | -0.3067 | 0.56305 | -120.694 | 0.737 | 0.15564 | -4.2252 | -0.16937 | 0.26093 | 0.17395 | 21.2036 | 21.4737 | 117.3798 | 0.91095 | 0.737 | 121.8658 | 31.3889 | -0.16937 | 0.91095 | 0.737 | 31.3889 | 117.3798 | 121.8658 | -121.0419 | -121.7743
4794.1719 | 121.8613 | -0.14648 | 121.6736 | -0.36583 | 0.015609 | -0.015968 | 0.010835 | 0.046269 | -0.011818 | 0.064766 | 0.5722 | 0.80109 | 0.44403 | 0.009155 | 117.3843 | 31.485 | 21.2265 | 21.4783 | 121.9299 | -0.32501 | 0.59052 | -120.8725 | 0.71869 | 0.15564 | -4.2892 | -0.17853 | 0.25635 | 0.12817 | 21.373 | 21.6248 | 117.5308 | 0.94757 | 0.71869 | 122.0764 | 31.6315 | -0.17853 | 0.94757 | 0.71869 | 31.6315 | 117.5308 | 122.0764 | -121.2296 | -121.9986
4795.9375 | 121.9162 | -0.082397 | 121.7102 | 0.12245 | 0.0139 | -0.011269 | 0.013612 | 0.050541 | -0.01139 | 0.065193 | 0.67749 | 0.73242 | 0.45776 | 0.11902 | 117.5079 | 31.8741 | 21.1258 | 21.9727 | 121.9208 | -0.23346 | 0.54016 | -120.9778 | 0.75989 | 0.20142 | -4.2023 | -0.15106 | 0.21057 | 0.21973 | 21.2082 | 22.0551 | 117.5903 | 0.81482 | 0.75989 | 122.0032 | 31.9565 | -0.15106 | 0.81482 | 0.75989 | 31.9565 | 117.5903 | 122.0032 | -121.2524 | -121.9437
4797.6406 | 121.962 | -0.11902 | 121.8109 | -0.25902 | 0.015182 | -0.016182 | 0.012758 | 0.047123 | -0.011818 | 0.066902 | 0.59052 | 0.78735 | 0.43488 | 0.041199 | 117.4622 | 32.0114 | 21.4828 | 22.1191 | 122.0398 | -0.27924 | 0.55389 | -121.0236 | 0.70953 | 0.16022 | -4.3488 | -0.16022 | 0.22888 | 0.15564 | 21.6019 | 22.2382 | 117.5812 | 0.90637 | 0.70953 | 122.1588 | 32.1304 | -0.16022 | 0.90637 | 0.70953 | 32.1304 | 117.5812 | 122.1588 | -121.376 | -122.0901
4799.4219 | 122.081 | -0.073242 | 121.8246 | 0.11482 | 0.016678 | -0.012337 | 0.017671 | 0.048405 | -0.015022 | 0.06797 | 0.55389 | 0.78278 | 0.41199 | 0.013733 | 117.421 | 32.2083 | 21.524 | 22.142 | 122.1222 | -0.2655 | 0.48523 | -121.0419 | 0.62714 | 0.086975 | -4.4037 | -0.19226 | 0.29755 | 0.14191 | 21.5973 | 22.2153 | 117.4942 | 0.85602 | 0.62714 | 122.1954 | 32.2815 | -0.19226 | 0.85602 | 0.62714 | 32.2815 | 117.4942 | 122.1954 | -121.4127 | -122.0901
4801.1719 | 122.0581 | -0.07782 | 121.8338 | 0.11482 | 0.015609 | -0.019813 | 0.016389 | 0.047978 | -0.014808 | 0.066048 | 0.59052 | 0.76446 | 0.41199 | 0.059509 | 117.421 | 32.4738 | 21.524 | 22.2702 | 122.1085 | -0.2655 | 0.48981 | -121.0693 | 0.66834 | 0.13733 | -4.4128 | -0.18768 | 0.27466 | 0.17853 | 21.6019 | 22.348 | 117.4988 | 0.84228 | 0.66834 | 122.1863 | 32.5516 | -0.18768 | 0.84228 | 0.66834 | 32.5516 | 117.4988 | 122.1863 | -121.4218 | -122.0993
4802.9375 | 122.113 | -0.082397 | 121.8704 | 0.091934 | 0.011978 | -0.0089189 | 0.010621 | 0.046055 | -0.010322 | 0.066048 | 0.64545 | 0.72784 | 0.45319 | 0.082397 | 117.4255 | 32.6706 | 21.5881 | 22.3984 | 122.0947 | -0.27008 | 0.53558 | -121.1426 | 0.72784 | 0.16479 | -4.4449 | -0.18768 | 0.22431 | 0.19226 | 21.6705 | 22.4808 | 117.5079 | 0.81024 | 0.72784 | 122.1771 | 32.753 | -0.18768 | 0.81024 | 0.72784 | 32.753 | 117.5079 | 122.1771 | -121.4172 | -122.1405
4804.7031 | 122.1176 | -0.07782 | 121.8933 | 0.061417 | 0.015182 | -0.0102 | 0.01938 | 0.047337 | -0.014808 | 0.066048 | 0.56305 | 0.78278 | 0.41199 | 0.004578 | 117.2745 | 32.8125 | 21.8307 | 22.3755 | 122.1725 | -0.28381 | 0.48981 | -121.1105 | 0.64087 | 0.082398 | -4.6188 | -0.20599 | 0.27923 | 0.15106 | 21.9086 | 22.4533 | 117.3523 | 0.8606 | 0.64087 | 122.2504 | 32.8903 | -0.20599 | 0.8606 | 0.64087 | 32.8903 | 117.3523 | 122.2504 | -121.4813 | -122.1771
4806.4062 | 122.0261 | -0.10071 | 121.9208 | -0.17509 | 0.015609 | -0.013832 | 0.015748 | 0.04755 | -0.012245 | 0.066048 | 0.55847 | 0.78278 | 0.40741 | 0.059509 | 117.3065 | 33.0643 | 21.9772 | 22.5769 | 122.1359 | -0.29297 | 0.50812 | -121.138 | 0.65918 | 0.16022 | -4.6143 | -0.19226 | 0.21515 | 0.15106 | 22.0779 | 22.6776 | 117.4072 | 0.88348 | 0.65918 | 122.2366 | 33.165 | -0.19226 | 0.88348 | 0.65918 | 33.165 | 117.4072 | 122.2366 | -121.5134 | -122.2137
4808.1875 | 122.0123 | -0.1236 | 121.9391 | -0.20561 | 0.016891 | -0.017036 | 0.0089124 | 0.045628 | -0.011177 | 0.06797 | 0.63629 | 0.74616 | 0.45776 | 0.14191 | 117.3523 | 33.4488 | 22.023 | 22.7783 | 122.1085 | -0.25177 | 0.58136 | -121.1929 | 0.75989 | 0.2655 | -4.5868 | -0.12817 | 0.16937 | 0.17853 | 22.1466 | 22.9019 | 117.4759 | 0.86975 | 0.75989 | 122.2321 | 33.5724 | -0.12817 | 0.86975 | 0.75989 | 33.5724 | 117.4759 | 122.2321 | -121.4813 | -122.1909
4809.9062 | 122.0764 | -0.10071 | 121.9299 | -0.21324 | 0.013687 | -0.015114 | 0.015107 | 0.046055 | -0.011604 | 0.06797 | 0.55847 | 0.78278 | 0.4303 | 0.036621 | 117.215 | 33.5632 | 22.3892 | 22.7509 | 122.1771 | -0.28381 | 0.53101 | -121.1472 | 0.65918 | 0.13733 | -4.715 | -0.1831 | 0.24719 | 0.12817 | 22.4899 | 22.8516 | 117.3157 | 0.88348 | 0.65918 | 122.2778 | 33.6639 | -0.1831 | 0.88348 | 0.65918 | 33.6639 | 117.3157 | 122.2778 | -121.4996 | -122.2137
4811.6719 | 122.1222 | -0.082397 | 121.9299 | 0.16823 | 0.013046 | -0.017036 | 0.013612 | 0.045841 | -0.012245 | 0.068398 | 0.63171 | 0.71869 | 0.44861 | 0.13275 | 117.2607 | 33.847 | 22.2748 | 22.934 | 122.113 | -0.24261 | 0.531 | -121.2112 | 0.71411 | 0.21515 | -4.6692 | -0.16022 | 0.18311 | 0.18311 | 22.3572 | 23.0164 | 117.3431 | 0.80109 | 0.71411 | 122.1954 | 33.9294 | -0.16022 | 0.80109 | 0.71411 | 33.9294 | 117.3431 | 122.1954 | -121.4813 | -122.1725
4813.375 | 122.0535 | -0.1236 | 121.9666 | -0.21324 | 0.014328 | -0.017036 | 0.013185 | 0.042637 | -0.011604 | 0.065834 | 0.6546 | 0.72784 | 0.44861 | 0.15564 | 117.2012 | 34.0897 | 22.4533 | 23.053 | 122.1313 | -0.23804 | 0.5722 | -121.2387 | 0.7782 | 0.27924 | -4.7653 | -0.11444 | 0.16479 | 0.20599 | 22.5769 | 23.1766 | 117.3248 | 0.85144 | 0.7782 | 122.2549 | 34.2133 | -0.11444 | 0.85144 | 0.7782 | 34.2133 | 117.3248 | 122.2549 | -121.5179 | -122.2046
4815.1406 | 122.2 | -0.082397 | 121.9208 | -0.014877 | 0.013687 | -0.014259 | 0.01233 | 0.046055 | -0.011604 | 0.066475 | 0.59509 | 0.74158 | 0.45319 | 0.07782 | 117.1097 | 34.2407 | 22.641 | 23.0347 | 122.1497 | -0.26093 | 0.53558 | -121.1792 | 0.67749 | 0.16022 | -4.8111 | -0.17853 | 0.22888 | 0.14191 | 22.7234 | 23.1171 | 117.1921 | 0.82397 | 0.67749 | 122.2321 | 34.3231 | -0.17853 | 0.82397 | 0.67749 | 34.3231 | 117.1921 | 122.2321 | -121.4676 | -122.1817
4816.9062 | 122.081 | -0.10986 | 122.0032 | -0.13695 | 0.011978 | -0.011269 | 0.012544 | 0.04456 | -0.010109 | 0.066262 | 0.66834 | 0.72784 | 0.40741 | 0.15564 | 117.1417 | 34.5978 | 22.4945 | 23.2452 | 122.1451 | -0.27466 | 0.51727 | -121.2753 | 0.7782 | 0.2655 | -4.8615 | -0.1648 | 0.14191 | 0.26093 | 22.6044 | 23.3551 | 117.2516 | 0.83771 | 0.7782 | 122.2549 | 34.7076 | -0.1648 | 0.83771 | 0.7782 | 34.7076 | 117.2516 | 122.2549 | -121.5958 | -122.2778
4818.6875 | 122.0856 | -0.10986 | 121.9849 | -0.20561 | 0.014969 | -0.014687 | 0.013612 | 0.04456 | -0.010963 | 0.066689 | 0.63171 | 0.72327 | 0.43945 | 0.12817 | 117.0273 | 34.8312 | 22.7097 | 23.3093 | 122.1725 | -0.27466 | 0.54932 | -121.2616 | 0.74158 | 0.23804 | -4.9576 | -0.1648 | 0.18768 | 0.19226 | 22.8195 | 23.4192 | 117.1371 | 0.83313 | 0.74158 | 122.2824 | 34.9411 | -0.1648 | 0.83313 | 0.74158 | 34.9411 | 117.1371 | 122.2824 | -121.5454 | -122.2595
4820.4688 | 122.2183 | -0.07782 | 121.9482 | 0.0080111 | 0.016891 | -0.012978 | 0.015748 | 0.047123 | -0.01075 | 0.067543 | 0.58136 | 0.71411 | 0.4303 | 0.09613 | 116.9449 | 35.1517 | 22.7417 | 23.3688 | 122.1863 | -0.24719 | 0.50812 | -121.2341 | 0.65918 | 0.17395 | -5.0034 | -0.16937 | 0.23804 | 0.15106 | 22.8195 | 23.4467 | 117.0227 | 0.79193 | 0.65918 | 122.2641 | 35.2295 | -0.16937 | 0.79193 | 0.65918 | 35.2295 | 117.0227 | 122.2641 | -121.5179 | -122.1954
4822.1875 | 122.1039 | -0.1236 | 121.9757 | -0.0072479 | 0.013473 | -0.0149 | 0.020662 | 0.049259 | -0.01374 | 0.06797 | 0.59509 | 0.77362 | 0.40283 | 0.054932 | 116.7938 | 35.2615 | 22.934 | 23.3414 | 122.1863 | -0.27924 | 0.52643 | -121.2021 | 0.71869 | 0.17853 | -5.1819 | -0.15564 | 0.21057 | 0.19226 | 23.0576 | 23.465 | 116.9174 | 0.89722 | 0.71869 | 122.3099 | 35.3851 | -0.15564 | 0.89722 | 0.71869 | 35.3851 | 116.9174 | 122.3099 | -121.5729 | -122.2549
4823.9688 | 122.2092 | -0.07782 | 121.9437 | -0.022507 | 0.015182 | -0.018532 | 0.011476 | 0.046696 | -0.009895 | 0.066902 | 0.58136 | 0.737 | 0.44403 | 0.09613 | 116.8304 | 35.5637 | 22.8699 | 23.4833 | 122.1771 | -0.2655 | 0.52185 | -121.2067 | 0.65918 | 0.17395 | -5.1132 | -0.18768 | 0.23346 | 0.13733 | 22.9477 | 23.5611 | 116.9083 | 0.81482 | 0.65918 | 122.2549 | 35.6415 | -0.18768 | 0.81482 | 0.65918 | 35.6415 | 116.9083 | 122.2549 | -121.4996 | -122.2092
4825.6719 | 122.1588 | -0.07782 | 121.962 | 0.17586 | 0.016464 | -0.010628 | 0.017457 | 0.047764 | -0.010536 | 0.067757 | 0.61798 | 0.70038 | 0.42114 | 0.14191 | 116.7755 | 35.8383 | 22.847 | 23.5107 | 122.1863 | -0.23804 | 0.49896 | -121.2616 | 0.6958 | 0.21973 | -5.1865 | -0.16022 | 0.2243 | 0.19684 | 22.9248 | 23.5886 | 116.8533 | 0.7782 | 0.6958 | 122.2641 | 35.9161 | -0.16022 | 0.7782 | 0.6958 | 35.9161 | 116.8533 | 122.2641 | -121.5408 | -122.2
4827.4375 | 122.1176 | -0.11444 | 121.9849 | -0.14458 | 0.013046 | -0.017464 | 0.011049 | 0.045841 | -0.0096814 | 0.066475 | 0.63171 | 0.70953 | 0.43488 | 0.16479 | 116.7709 | 36.0672 | 22.9019 | 23.6252 | 122.1588 | -0.24719 | 0.54932 | -121.2753 | 0.74616 | 0.27924 | -5.2139 | -0.13275 | 0.17395 | 0.19684 | 23.0164 | 23.7396 | 116.8854 | 0.82398 | 0.74616 | 122.2733 | 36.1816 | -0.13275 | 0.82398 | 0.74616 | 36.1816 | 116.8854 | 122.2733 | -121.55 | -122.2321
4829.2188 | 122.2412 | -0.07782 | 121.9757 | 0.0080111 | 0.014755 | -0.013405 | 0.013612 | 0.04221 | -0.0083996 | 0.064125 | 0.5722 | 0.70496 | 0.41199 | 0.091553 | 116.6153 | 36.1816 | 22.934 | 23.5107 | 122.1771 | -0.27008 | 0.48981 | -121.2708 | 0.65002 | 0.16937 | -5.3604 | -0.19226 | 0.20142 | 0.16022 | 23.0118 | 23.5886 | 116.6931 | 0.78278 | 0.65002 | 122.2549 | 36.2595 | -0.19226 | 0.78278 | 0.65002 | 36.2595 | 116.6931 | 122.2549 | -121.5637 | -122.2458
4830.9844 | 122.1359 | -0.10071 | 121.994 | 0.076676 | 0.015823 | -0.012337 | 0.018953 | 0.0499 | -0.012458 | 0.065834 | 0.54932 | 0.74616 | 0.39368 | 0.054932 | 116.4825 | 36.3373 | 23.0942 | 23.4375 | 122.2366 | -0.26093 | 0.49439 | -121.2479 | 0.65002 | 0.15564 | -5.5115 | -0.16022 | 0.24261 | 0.15564 | 23.1949 | 23.5382 | 116.5833 | 0.84686 | 0.65002 | 122.3373 | 36.438 | -0.16022 | 0.84686 | 0.65002 | 36.438 | 116.5833 | 122.3373 | -121.6003 | -122.2549
4832.6875 | 122.1359 | -0.10071 | 122.0032 | -0.19798 | 0.014328 | -0.012337 | 0.016389 | 0.045841 | -0.011818 | 0.067116 | 0.5127 | 0.72784 | 0.37079 | 0.045776 | 116.4459 | 36.5662 | 23.2178 | 23.5565 | 122.2092 | -0.26093 | 0.4715 | -121.2753 | 0.6134 | 0.14648 | -5.5573 | -0.16022 | 0.20599 | 0.14191 | 23.3185 | 23.6572 | 116.5466 | 0.82855 | 0.6134 | 122.3099 | 36.6669 | -0.16022 | 0.82855 | 0.6134 | 36.6669 | 116.5466 | 122.3099 | -121.6324 | -122.2641
4834.4688 | 122.1542 | -0.09613 | 121.9894 | 0.01564 | 0.014541 | -0.01725 | 0.018953 | 0.04691 | -0.0096814 | 0.066475 | 0.54932 | 0.75073 | 0.39825 | 0.045776 | 116.3452 | 36.7584 | 23.204 | 23.5107 | 122.1954 | -0.27924 | 0.49438 | -121.2387 | 0.64545 | 0.14191 | -5.6442 | -0.18311 | 0.20599 | 0.15106 | 23.3002 | 23.6069 | 116.4413 | 0.84686 | 0.64545 | 122.2916 | 36.8546 | -0.18311 | 0.84686 | 0.64545 | 36.8546 | 116.4413 | 122.2916 | -121.5912 | -122.2687
4836.1562 | 122.1085 | -0.13275 | 122.049 | -0.20561 | 0.015182 | -0.014046 | 0.010194 | 0.045628 | -0.0086132 | 0.065621 | 0.63629 | 0.75073 | 0.44403 | 0.13733 | 116.391 | 37.0972 | 23.2224 | 23.6847 | 122.1954 | -0.28381 | 0.57678 | -121.2982 | 0.76904 | 0.27008 | -5.658 | -0.15106 | 0.14648 | 0.19226 | 23.3551 | 23.8174 | 116.5237 | 0.88348 | 0.76904 | 122.3282 | 37.2299 | -0.15106 | 0.88348 | 0.76904 | 37.2299 | 116.5237 | 122.3282 | -121.6049 | -122.3328
4837.9219 | 122.1085 | -0.11444 | 122.0215 | -0.15984 | 0.015182 | -0.012764 | 0.016176 | 0.046269 | -0.01374 | 0.066902 | 0.5722 | 0.74616 | 0.41657 | 0.082397 | 116.2537 | 37.3261 | 23.3276 | 23.6618 | 122.2321 | -0.27466 | 0.53101 | -121.2753 | 0.68665 | 0.19684 | -5.7678 | -0.16022 | 0.21057 | 0.15564 | 23.4421 | 23.7762 | 116.3681 | 0.8606 | 0.68665 | 122.3465 | 37.4405 | -0.16022 | 0.8606 | 0.68665 | 37.4405 | 116.3681 | 122.3465 | -121.6049 | -122.2961
4839.6875 | 122.1085 | -0.12817 | 122.0398 | -0.16747 | 0.012832 | -0.01255 | 0.010835 | 0.046055 | -0.0086132 | 0.067757 | 0.66834 | 0.74616 | 0.46234 | 0.15106 | 116.3452 | 37.2299 | 23.1628 | 23.6801 | 122.2 | -0.24719 | 0.59052 | -121.2936 | 0.79651 | 0.27924 | -5.6946 | -0.11902 | 0.16022 | 0.20599 | 23.291 | 23.8083 | 116.4734 | 0.87433 | 0.79651 | 122.3282 | 37.3581 | -0.11902 | 0.87433 | 0.79651 | 37.3581 | 116.4734 | 122.3282 | -121.5775 | -122.287
4841.3906 | 122.1359 | -0.09613 | 122.0123 | -0.022507 | 0.016678 | -0.0072099 | 0.020021 | 0.047337 | -0.010536 | 0.066475 | 0.63629 | 0.78735 | 0.46234 | 0.050354 | 116.1804 | 37.2803 | 23.3002 | 23.5153 | 122.2321 | -0.28839 | 0.55847 | -121.225 | 0.73242 | 0.14648 | -5.8319 | -0.19226 | 0.21973 | 0.17395 | 23.3963 | 23.6114 | 116.2766 | 0.88348 | 0.73242 | 122.3282 | 37.3764 | -0.19226 | 0.88348 | 0.73242 | 37.3764 | 116.2766 | 122.3282 | -121.55 | -122.3007
4843.1562 | 122.2 | -0.09613 | 121.9711 | 0.14534 | 0.014969 | -0.014259 | 0.014039 | 0.047337 | -0.010536 | 0.068611 | 0.67749 | 0.76446 | 0.49896 | 0.15106 | 116.1987 | 37.6328 | 23.1857 | 23.6801 | 122.1817 | -0.24719 | 0.59509 | -121.2067 | 0.77362 | 0.24719 | -5.7724 | -0.15106 | 0.21057 | 0.17853 | 23.2819 | 23.7762 | 116.2949 | 0.86059 | 0.77362 | 122.2778 | 37.7289 | -0.15106 | 0.86059 | 0.77362 | 37.7289 | 116.2949 | 122.2778 | -121.4722 | -122.2183
4844.8594 | 122.1725 | -0.086975 | 122.0078 | -0.12169 | 0.014755 | -0.015327 | 0.011476 | 0.045841 | -0.011177 | 0.06733 | 0.70038 | 0.77362 | 0.51727 | 0.14191 | 116.1667 | 37.9395 | 23.3551 | 23.8312 | 122.2229 | -0.25635 | 0.60425 | -121.2341 | 0.78735 | 0.22888 | -5.8411 | -0.16937 | 0.21515 | 0.1831 | 23.4421 | 23.9182 | 116.2537 | 0.8606 | 0.78735 | 122.3099 | 38.0264 | -0.16937 | 0.8606 | 0.78735 | 38.0264 | 116.2537 | 122.3099 | -121.4905 | -122.2641
4846.625 | 122.2412 | -0.064087 | 121.9803 | 0.084305 | 0.014328 | -0.013405 | 0.017244 | 0.04755 | -0.01139 | 0.067543 | 0.60883 | 0.83313 | 0.47607 | 0.027466 | 115.9561 | 37.9486 | 23.5611 | 23.6252 | 122.2183 | -0.27924 | 0.54016 | -121.1472 | 0.67291 | 0.091553 | -6.0242 | -0.21515 | 0.23804 | 0.13275 | 23.6252 | 23.6893 | 116.0202 | 0.89722 | 0.67291 | 122.2824 | 38.0127 | -0.21515 | 0.89722 | 0.67291 | 38.0127 | 116.0202 | 122.2824 | -121.5042 | -122.2595
4848.3906 | 122.2458 | -0.07782 | 122.0078 | 0.0080111 | 0.011978 | -0.013832 | 0.009126 | 0.04456 | -0.009895 | 0.066475 | 0.6546 | 0.78735 | 0.51727 | 0.073242 | 115.9607 | 38.3194 | 23.5428 | 23.79 | 122.1954 | -0.28839 | 0.59509 | -121.2204 | 0.73242 | 0.15106 | -6.0471 | -0.21057 | 0.18768 | 0.13733 | 23.6206 | 23.8678 | 116.0385 | 0.86517 | 0.73242 | 122.2733 | 38.3972 | -0.21057 | 0.86517 | 0.73242 | 38.3972 | 116.0385 | 122.2733 | -121.4905 | -122.2961
4850.1562 | 122.1588 | -0.09613 | 122.0444 | -0.23613 | 0.014114 | -0.017677 | 0.014894 | 0.045201 | -0.01139 | 0.066689 | 0.60425 | 0.81482 | 0.47607 | 0.032043 | 115.8188 | 38.4705 | 23.7671 | 23.7762 | 122.2778 | -0.29755 | 0.5722 | -121.2296 | 0.70038 | 0.12817 | -6.2256 | -0.20142 | 0.23346 | 0.12817 | 23.8632 | 23.8724 | 115.9149 | 0.91095 | 0.70038 | 122.374 | 38.5666 | -0.20142 | 0.91095 | 0.70038 | 38.5666 | 115.9149 | 122.374 | -121.5683 | -122.3419
4851.8594 | 122.1634 | -0.1236 | 122.0398 | -0.25902 | 0.015609 | -0.014046 | 0.013185 | 0.046055 | -0.0096814 | 0.06498 | 0.68207 | 0.79651 | 0.49896 | 0.10071 | 115.8279 | 38.8046 | 23.7442 | 23.8953 | 122.2366 | -0.2655 | 0.62256 | -121.2433 | 0.80566 | 0.2243 | -6.2119 | -0.14191 | 0.19684 | 0.18311 | 23.8678 | 24.0189 | 115.9515 | 0.92011 | 0.80566 | 122.3602 | 38.9282 | -0.14191 | 0.92011 | 0.80566 | 38.9282 | 115.9515 | 122.3602 | -121.5408 | -122.3053
4853.625 | 122.1497 | -0.10071 | 122.0215 | -0.022507 | 0.016037 | -0.014046 | 0.017884 | 0.043278 | -0.011818 | 0.068611 | 0.6546 | 0.80109 | 0.4715 | 0.068665 | 115.686 | 38.9648 | 23.7717 | 23.8541 | 122.2733 | -0.27466 | 0.5722 | -121.2204 | 0.75531 | 0.16937 | -6.3354 | -0.17395 | 0.25177 | 0.18311 | 23.8724 | 23.9548 | 115.7867 | 0.90179 | 0.75531 | 122.374 | 39.0656 | -0.17395 | 0.90179 | 0.75531 | 39.0656 | 115.7867 | 122.374 | -121.55 | -122.2961
4855.3438 | 122.2092 | -0.07782 | 122.0306 | 0.19112 | 0.018173 | -0.013618 | 0.013398 | 0.049687 | -0.0086132 | 0.068398 | 0.6546 | 0.81482 | 0.48065 | 0.082397 | 115.6448 | 39.2761 | 23.7534 | 23.941 | 122.2549 | -0.27466 | 0.55847 | -121.2158 | 0.73242 | 0.16022 | -6.3858 | -0.19684 | 0.2243 | 0.17395 | 23.8312 | 24.0189 | 115.7227 | 0.89264 | 0.73242 | 122.3328 | 39.3539 | -0.19684 | 0.89264 | 0.73242 | 39.3539 | 115.7227 | 122.3328 | -121.55 | -122.3053
4857.125 | 122.1268 | -0.1236 | 122.0215 | -0.20561 | 0.015396 | -0.015327 | 0.016816 | 0.047978 | -0.010109 | 0.069466 | 0.65002 | 0.83771 | 0.48065 | 0.091553 | 115.6494 | 39.3768 | 23.8815 | 23.9365 | 122.2504 | -0.27466 | 0.60425 | -121.1838 | 0.77362 | 0.21515 | -6.3721 | -0.15106 | 0.22888 | 0.16937 | 24.0051 | 24.0601 | 115.773 | 0.9613 | 0.77362 | 122.374 | 39.5004 | -0.15106 | 0.9613 | 0.77362 | 39.5004 | 115.773 | 122.374 | -121.5408 | -122.2961
4858.8281 | 122.1222 | -0.11902 | 122.0444 | -0.12169 | 0.017105 | -0.014687 | 0.015962 | 0.047123 | -0.012672 | 0.069252 | 0.66834 | 0.81482 | 0.47607 | 0.086975 | 115.5853 | 39.6652 | 23.8953 | 23.9044 | 122.2778 | -0.27924 | 0.59509 | -121.2296 | 0.78735 | 0.20599 | -6.459 | -0.16022 | 0.23346 | 0.19226 | 24.0143 | 24.0234 | 115.7043 | 0.93384 | 0.78735 | 122.3969 | 39.7842 | -0.16022 | 0.93384 | 0.78735 | 39.7842 | 115.7043 | 122.3969 | -121.5683 | -122.3236
4860.5938 | 122.1085 | -0.10986 | 122.0627 | -0.12169 | 0.014755 | -0.014687 | 0.015535 | 0.050114 | -0.010322 | 0.067116 | 0.64545 | 0.78278 | 0.44861 | 0.091553 | 115.5121 | 39.9216 | 23.9639 | 23.9273 | 122.2504 | -0.27008 | 0.55847 | -121.2799 | 0.75531 | 0.20142 | -6.5506 | -0.16022 | 0.18768 | 0.19684 | 24.0738 | 24.0372 | 115.6219 | 0.89264 | 0.75531 | 122.3602 | 40.0314 | -0.16022 | 0.89264 | 0.75531 | 40.0314 | 115.6219 | 122.3602 | -121.6141 | -122.3328
4862.3594 | 122.2458 | -0.073242 | 121.9894 | 0.11482 | 0.014328 | -0.010841 | 0.016389 | 0.049046 | -0.009895 | 0.068825 | 0.60883 | 0.79651 | 0.46692 | 0.022888 | 115.3885 | 40.2832 | 24.0005 | 23.9319 | 122.287 | -0.27466 | 0.54016 | -121.1929 | 0.68207 | 0.09613 | -6.601 | -0.20142 | 0.29755 | 0.14191 | 24.0738 | 24.0051 | 115.4617 | 0.86975 | 0.68207 | 122.3602 | 40.3564 | -0.20142 | 0.86975 | 0.68207 | 40.3564 | 115.4617 | 122.3602 | -121.5225 | -122.2641
4864.0781 | 122.2366 | -0.091553 | 122.0261 | 0.11482 | 0.015609 | -0.015327 | 0.011476 | 0.04691 | -0.0077588 | 0.067757 | 0.6546 | 0.73242 | 0.48523 | 0.10529 | 115.3931 | 40.686 | 23.9822 | 24.115 | 122.2092 | -0.25177 | 0.57678 | -121.2936 | 0.74616 | 0.19684 | -6.633 | -0.16022 | 0.1831 | 0.16937 | 24.0738 | 24.2065 | 115.4846 | 0.82398 | 0.74616 | 122.3007 | 40.7776 | -0.16022 | 0.82398 | 0.74616 | 40.7776 | 115.4846 | 122.3007 | -121.5408 | -122.2778
4865.8438 | 122.1497 | -0.10071 | 122.0764 | -0.053024 | 0.014755 | -0.0097733 | 0.017671 | 0.04755 | -0.013527 | 0.070534 | 0.62714 | 0.7782 | 0.46692 | 0.073242 | 115.2466 | 40.8051 | 24.1608 | 24.0829 | 122.2595 | -0.27924 | 0.56763 | -121.2982 | 0.72784 | 0.17395 | -6.8298 | -0.17853 | 0.18311 | 0.16022 | 24.2615 | 24.1837 | 115.3473 | 0.87891 | 0.72784 | 122.3602 | 40.9058 | -0.17853 | 0.87891 | 0.72784 | 40.9058 | 115.3473 | 122.3602 | -121.6095 | -122.3557
4867.6094 | 122.2458 | -0.068665 | 122.0444 | 0.10719 | 0.015182 | -0.014473 | 0.01233 | 0.047337 | -0.0066906 | 0.069039 | 0.6546 | 0.75989 | 0.50354 | 0.10529 | 115.21 | 41.0156 | 24.0509 | 24.1928 | 122.2183 | -0.25635 | 0.5722 | -121.2845 | 0.72327 | 0.17395 | -6.8344 | -0.18768 | 0.17395 | 0.15106 | 24.1196 | 24.2615 | 115.2786 | 0.82855 | 0.72327 | 122.287 | 41.0843 | -0.18768 | 0.82855 | 0.72327 | 41.0843 | 115.2786 | 122.287 | -121.5408 | -122.3007
4869.3281 | 122.2275 | -0.068665 | 122.0032 | 0.1606 | 0.016891 | -0.012978 | 0.017671 | 0.04755 | -0.0090406 | 0.069039 | 0.59509 | 0.79193 | 0.45319 | 0.059509 | 115.0726 | 41.1896 | 24.1379 | 24.1928 | 122.2504 | -0.24719 | 0.52185 | -121.2112 | 0.66376 | 0.12817 | -6.9305 | -0.17853 | 0.24719 | 0.14191 | 24.2065 | 24.2615 | 115.1413 | 0.8606 | 0.66376 | 122.319 | 41.2582 | -0.17853 | 0.8606 | 0.66376 | 41.2582 | 115.1413 | 122.319 | -121.55 | -122.2504
4871.0938 | 122.1817 | -0.10071 | 122.0764 | -0.19798 | 0.015182 | -0.016823 | 0.016176 | 0.045414 | -0.012245 | 0.068611 | 0.58136 | 0.79651 | 0.4715 | 0.045776 | 114.9628 | 41.3406 | 24.3668 | 24.2661 | 122.2778 | -0.28839 | 0.5722 | -121.2799 | 0.68207 | 0.14648 | -7.1136 | -0.18768 | 0.20142 | 0.10986 | 24.4675 | 24.3668 | 115.0635 | 0.89722 | 0.68207 | 122.3785 | 41.4413 | -0.18768 | 0.89722 | 0.68207 | 41.4413 | 115.0635 | 122.3785 | -121.6049 | -122.3648
4872.7969 | 122.1725 | -0.11444 | 122.049 | -0.20561 | 0.015823 | -0.017464 | 0.012544 | 0.046269 | -0.010536 | 0.068825 | 0.58136 | 0.8194 | 0.46692 | 0.022888 | 114.8712 | 41.5604 | 24.4034 | 24.321 | 122.2687 | -0.29755 | 0.58136 | -121.2296 | 0.6958 | 0.13733 | -7.1777 | -0.1831 | 0.21973 | 0.11444 | 24.5178 | 24.4354 | 114.9857 | 0.93384 | 0.6958 | 122.3831 | 41.6748 | -0.1831 | 0.93384 | 0.6958 | 41.6748 | 114.9857 | 122.3831 | -121.582 | -122.3465
4874.5781 | 122.2641 | -0.091553 | 122.0078 | 0.10719 | 0.013687 | -0.016182 | 0.011262 | 0.044132 | -0.0094678 | 0.068611 | 0.62714 | 0.74616 | 0.48065 | 0.086975 | 114.8071 | 41.7755 | 24.2432 | 24.3759 | 122.2458 | -0.24719 | 0.57221 | -121.2616 | 0.71869 | 0.17853 | -7.2006 | -0.15564 | 0.23804 | 0.14648 | 24.3347 | 24.4675 | 114.8987 | 0.83771 | 0.71869 | 122.3373 | 41.8671 | -0.15564 | 0.83771 | 0.71869 | 41.8671 | 114.8987 | 122.3373 | -121.5271 | -122.2549
4876.3438 | 122.2275 | -0.082397 | 121.9986 | 0.15297 | 0.015182 | -0.015114 | 0.018525 | 0.049687 | -0.0094678 | 0.069252 | 0.65918 | 0.80109 | 0.47607 | 0.064087 | 114.6561 | 41.9632 | 24.3393 | 24.3896 | 122.2733 | -0.25635 | 0.55847 | -121.1975 | 0.74158 | 0.14648 | -7.3425 | -0.17395 | 0.27466 | 0.18311 | 24.4217 | 24.472 | 114.7385 | 0.88348 | 0.74158 | 122.3557 | 42.0456 | -0.17395 | 0.88348 | 0.74158 | 42.0456 | 114.7385 | 122.3557 | -121.5225 | -122.2549
4878.1094 | 122.2229 | -0.09613 | 122.049 | -0.098801 | 0.0139 | -0.017036 | 0.011689 | 0.04691 | -0.0083996 | 0.067543 | 0.68207 | 0.79651 | 0.50354 | 0.13275 | 114.6515 | 42.1463 | 24.3942 | 24.5773 | 122.2595 | -0.26093 | 0.59967 | -121.2524 | 0.7782 | 0.22888 | -7.3975 | -0.1648 | 0.21057 | 0.17853 | 24.4904 | 24.6735 | 114.7476 | 0.89264 | 0.7782 | 122.3557 | 42.2424 | -0.1648 | 0.89264 | 0.7782 | 42.2424 | 114.7476 | 122.3557 | -121.5454 | -122.3099
4879.8125 | 122.2229 | -0.10986 | 122.0306 | -0.15221 | 0.015609 | -0.016823 | 0.012544 | 0.042637 | -0.0096814 | 0.066689 | 0.70038 | 0.76904 | 0.53101 | 0.15106 | 114.5554 | 42.3843 | 24.4583 | 24.646 | 122.2321 | -0.25635 | 0.64087 | -121.2616 | 0.81024 | 0.26093 | -7.4753 | -0.14649 | 0.20142 | 0.16937 | 24.5682 | 24.7559 | 114.6652 | 0.87891 | 0.81024 | 122.3419 | 42.4942 | -0.14649 | 0.87891 | 0.81024 | 42.4942 | 114.6652 | 122.3419 | -121.4996 | -122.287
4881.5781 | 122.1863 | -0.091553 | 122.0535 | -0.23613 | 0.016464 | -0.016823 | 0.017244 | 0.044987 | -0.0090406 | 0.066902 | 0.58594 | 0.80566 | 0.4303 | 0.054932 | 114.3173 | 42.4988 | 24.7559 | 24.6002 | 122.3007 | -0.28381 | 0.52185 | -121.2479 | 0.67749 | 0.14649 | -7.7362 | -0.19226 | 0.24719 | 0.15564 | 24.8474 | 24.6918 | 114.4089 | 0.89722 | 0.67749 | 122.3923 | 42.5903 | -0.19226 | 0.89722 | 0.67749 | 42.5903 | 114.4089 | 122.3923 | -121.6232 | -122.3373
4883.3281 | 122.2458 | -0.09613 | 122.0261 | 0.038529 | 0.015396 | -0.013405 | 0.021516 | 0.045841 | -0.01139 | 0.068398 | 0.58136 | 0.78278 | 0.45319 | 0.027466 | 114.1891 | 42.6636 | 24.7421 | 24.5865 | 122.2687 | -0.28381 | 0.54932 | -121.2433 | 0.67749 | 0.1236 | -7.8369 | -0.18768 | 0.24262 | 0.12817 | 24.8383 | 24.6826 | 114.2853 | 0.87891 | 0.67749 | 122.3648 | 42.7597 | -0.18768 | 0.87891 | 0.67749 | 42.7597 | 114.2853 | 122.3648 | -121.5729 | -122.3099
4885.0469 | 122.2275 | -0.068665 | 122.0352 | 0.11482 | 0.014755 | -0.0078507 | 0.014039 | 0.04755 | -0.010322 | 0.069893 | 0.69122 | 0.737 | 0.4715 | 0.13275 | 114.1983 | 43.0298 | 24.6002 | 24.765 | 122.1771 | -0.25635 | 0.54016 | -121.2982 | 0.75989 | 0.20142 | -7.8369 | -0.18768 | 0.14191 | 0.21973 | 24.6689 | 24.8337 | 114.267 | 0.80566 | 0.75989 | 122.2458 | 43.0984 | -0.18768 | 0.80566 | 0.75989 | 43.0984 | 114.267 | 122.2458 | -121.5637 | -122.2916
4886.8125 | 122.2 | -0.11902 | 122.0764 | -0.26665 | 0.015609 | -0.010414 | 0.015107 | 0.045414 | -0.0069042 | 0.068184 | 0.57678 | 0.81482 | 0.46692 | 0.032043 | 113.9923 | 43.103 | 24.9435 | 24.7879 | 122.2733 | -0.28839 | 0.58594 | -121.2616 | 0.6958 | 0.15106 | -8.0841 | -0.16937 | 0.19684 | 0.10986 | 25.0626 | 24.9069 | 114.1113 | 0.93384 | 0.6958 | 122.3923 | 43.222 | -0.16937 | 0.93384 | 0.6958 | 43.222 | 114.1113 | 122.3923 | -121.6095 | -122.3648
4888.5781 | 122.1542 | -0.11444 | 122.0718 | -0.19798 | 0.014328 | -0.0095597 | 0.01233 | 0.046482 | -0.0094678 | 0.071175 | 0.64545 | 0.73242 | 0.47607 | 0.1236 | 113.974 | 43.4738 | 24.8795 | 24.9619 | 122.2092 | -0.25635 | 0.59052 | -121.3394 | 0.75989 | 0.23804 | -8.0978 | -0.14191 | 0.13733 | 0.16937 | 24.9939 | 25.0763 | 114.0884 | 0.84686 | 0.75989 | 122.3236 | 43.5883 | -0.14191 | 0.84686 | 0.75989 | 43.5883 | 114.0884 | 122.3236 | -121.5958 | -122.3282
4890.2812 | 122.168 | -0.12817 | 122.0535 | -0.20561 | 0.013473 | -0.016823 | 0.012971 | 0.047123 | -0.008827 | 0.071175 | 0.66376 | 0.73242 | 0.46234 | 0.12817 | 113.8412 | 43.6798 | 24.9664 | 25.0351 | 122.2458 | -0.27466 | 0.59052 | -121.3211 | 0.79193 | 0.25635 | -8.2123 | -0.14648 | 0.19226 | 0.20142 | 25.0946 | 25.1633 | 113.9694 | 0.8606 | 0.79193 | 122.374 | 43.808 | -0.14648 | 0.8606 | 0.79193 | 43.808 | 113.9694 | 122.374 | -121.5912 | -122.3282
4892.0469 | 122.2641 | -0.064087 | 122.0169 | 0.13008 | 0.016037 | -0.017036 | 0.019166 | 0.046482 | -0.010109 | 0.069252 | 0.55847 | 0.75531 | 0.39825 | 0.041199 | 113.6307 | 43.7851 | 25.0259 | 24.8886 | 122.2641 | -0.29297 | 0.46234 | -121.2616 | 0.62256 | 0.10529 | -8.3862 | -0.22888 | 0.24719 | 0.16022 | 25.09 | 24.9527 | 113.6948 | 0.8194 | 0.62256 | 122.3282 | 43.8492 | -0.22888 | 0.8194 | 0.62256 | 43.8492 | 113.6948 | 122.3282 | -121.6187 | -122.3099
4893.75 | 122.1588 | -0.1236 | 122.0718 | -0.15984 | 0.0139 | -0.017891 | 0.012544 | 0.045201 | -0.0094678 | 0.068398 | 0.65002 | 0.737 | 0.47607 | 0.13275 | 113.6261 | 44.0643 | 25.0351 | 25.1129 | 122.2458 | -0.25177 | 0.59967 | -121.3348 | 0.77362 | 0.25635 | -8.4457 | -0.12817 | 0.17395 | 0.17395 | 25.1587 | 25.2365 | 113.7497 | 0.8606 | 0.77362 | 122.3694 | 44.1879 | -0.12817 | 0.8606 | 0.77362 | 44.1879 | 113.7497 | 122.3694 | -121.5958 | -122.3236
4895.5312 | 122.1497 | -0.13275 | 122.0673 | -0.19798 | 0.01326 | -0.016182 | 0.012117 | 0.044773 | -0.0075452 | 0.070961 | 0.67291 | 0.71869 | 0.45319 | 0.15564 | 113.4888 | 44.3298 | 25.09 | 25.2228 | 122.2137 | -0.24261 | 0.58594 | -121.3486 | 0.80566 | 0.28839 | -8.5785 | -0.10986 | 0.14648 | 0.21973 | 25.2228 | 25.3555 | 113.6215 | 0.85144 | 0.80566 | 122.3465 | 44.4626 | -0.10986 | 0.85144 | 0.80566 | 44.4626 | 113.6215 | 122.3465 | -121.6141 | -122.3099
4897.2969 | 122.1542 | -0.11444 | 122.0581 | -0.2285 | 0.014328 | -0.017036 | 0.014253 | 0.044346 | -0.0077588 | 0.068184 | 0.66834 | 0.72784 | 0.48065 | 0.15106 | 113.3652 | 44.5816 | 25.2457 | 25.3876 | 122.2183 | -0.24719 | 0.59509 | -121.3303 | 0.78278 | 0.2655 | -8.6929 | -0.13275 | 0.16022 | 0.18768 | 25.3601 | 25.502 | 113.4796 | 0.84229 | 0.78278 | 122.3328 | 44.696 | -0.13275 | 0.84229 | 0.78278 | 44.696 | 113.4796 | 122.3328 | -121.5775 | -122.3053
4899.0625 | 122.1588 | -0.13733 | 122.0856 | -0.053024 | 0.015609 | -0.013832 | 0.022371 | 0.044773 | -0.011177 | 0.068825 | 0.6134 | 0.75531 | 0.41199 | 0.086975 | 113.1592 | 44.6823 | 25.383 | 25.3326 | 122.2595 | -0.27924 | 0.54932 | -121.3303 | 0.75073 | 0.2243 | -8.9264 | -0.14191 | 0.17395 | 0.20142 | 25.5203 | 25.47 | 113.2965 | 0.89264 | 0.75073 | 122.3969 | 44.8196 | -0.14191 | 0.89264 | 0.75073 | 44.8196 | 113.2965 | 122.3969 | -121.6736 | -122.3648
4900.8281 | 122.1771 | -0.11444 | 122.0535 | -0.26665 | 0.014755 | -0.012978 | 0.014467 | 0.045201 | -0.0075452 | 0.069893 | 0.60425 | 0.71869 | 0.42572 | 0.10986 | 113.0585 | 44.9707 | 25.4517 | 25.4837 | 122.2321 | -0.2655 | 0.54016 | -121.3348 | 0.71869 | 0.2243 | -8.9951 | -0.15106 | 0.17853 | 0.17853 | 25.5661 | 25.5981 | 113.1729 | 0.83313 | 0.71869 | 122.3465 | 45.0851 | -0.15106 | 0.83313 | 0.71869 | 45.0851 | 113.1729 | 122.3465 | -121.6278 | -122.319
4902.5938 | 122.2412 | -0.073242 | 122.049 | 0.15297 | 0.016891 | -0.014046 | 0.016816 | 0.047123 | -0.0096814 | 0.069252 | 0.65918 | 0.71869 | 0.45776 | 0.14648 | 112.9211 | 45.2316 | 25.3693 | 25.5844 | 122.2687 | -0.26093 | 0.53101 | -121.3303 | 0.73242 | 0.21973 | -9.1278 | -0.18768 | 0.21973 | 0.20142 | 25.4425 | 25.6577 | 112.9944 | 0.79193 | 0.73242 | 122.3419 | 45.3049 | -0.18768 | 0.79193 | 0.73242 | 45.3049 | 112.9944 | 122.3419 | -121.5912 | -122.3099
4904.3125 | 122.2412 | -0.064087 | 122.0215 | 0.15297 | 0.014541 | -0.011909 | 0.017244 | 0.048405 | -0.0073316 | 0.069039 | 0.66376 | 0.70953 | 0.44403 | 0.14648 | 112.7701 | 45.488 | 25.4608 | 25.7034 | 122.2412 | -0.22888 | 0.50812 | -121.3119 | 0.72784 | 0.21057 | -9.2514 | -0.16479 | 0.21973 | 0.21973 | 25.5249 | 25.7675 | 112.8342 | 0.77362 | 0.72784 | 122.3053 | 45.5521 | -0.16479 | 0.77362 | 0.72784 | 45.5521 | 112.8342 | 122.3053 | -121.5775 | -122.2504
4906.0781 | 122.287 | -0.064087 | 122.0398 | 0.10719 | 0.016037 | -0.0072099 | 0.020662 | 0.048619 | -0.009895 | 0.07267 | 0.50354 | 0.71411 | 0.37537 | 0.032043 | 112.5183 | 45.607 | 25.7629 | 25.6393 | 122.2595 | -0.29755 | 0.43945 | -121.3257 | 0.56763 | 0.09613 | -9.5215 | -0.23346 | 0.21973 | 0.12817 | 25.827 | 25.7034 | 112.5824 | 0.7782 | 0.56763 | 122.3236 | 45.6711 | -0.23346 | 0.7782 | 0.56763 | 45.6711 | 112.5824 | 122.3236 | -121.6644 | -122.3373
4907.8438 | 122.1634 | -0.13275 | 122.081 | -0.15984 | 0.015609 | -0.011482 | 0.014467 | 0.046482 | -0.0086132 | 0.069679 | 0.6134 | 0.69122 | 0.4303 | 0.14191 | 112.4863 | 46.0007 | 25.7675 | 25.9323 | 122.2687 | -0.27008 | 0.56305 | -121.3898 | 0.74615 | 0.27466 | -9.5947 | -0.13733 | 0.18768 | 0.18311 | 25.9003 | 26.0651 | 112.619 | 0.82397 | 0.74615 | 122.4014 | 46.1334 | -0.13733 | 0.82397 | 0.74615 | 46.1334 | 112.619 | 122.4014 | -121.6507 | -122.3511
4909.625 | 122.2366 | -0.086975 | 122.0261 | 0.15297 | 0.015182 | -0.015541 | 0.016603 | 0.048619 | -0.0083996 | 0.069252 | 0.65002 | 0.70496 | 0.44861 | 0.14191 | 112.4359 | 46.3486 | 25.6577 | 25.8865 | 122.2458 | -0.23804 | 0.53558 | -121.3211 | 0.737 | 0.22888 | -9.5901 | -0.15106 | 0.21973 | 0.20142 | 25.7446 | 25.9735 | 112.5229 | 0.79193 | 0.737 | 122.3328 | 46.4355 | -0.15106 | 0.79193 | 0.737 | 46.4355 | 112.5229 | 122.3328 | -121.5775 | -122.2641
4911.3438 | 122.2549 | -0.068665 | 122.0123 | 0.19112 | 0.015182 | -0.015541 | 0.019807 | 0.049687 | -0.0096814 | 0.070961 | 0.55389 | 0.70038 | 0.39368 | 0.082397 | 112.2162 | 46.4951 | 25.8591 | 25.9369 | 122.2687 | -0.27924 | 0.46234 | -121.312 | 0.62256 | 0.15106 | -9.7961 | -0.21057 | 0.25635 | 0.16022 | 25.9277 | 26.0056 | 112.2849 | 0.76904 | 0.62256 | 122.3373 | 46.5637 | -0.21057 | 0.76904 | 0.62256 | 46.5637 | 112.2849 | 122.3373 | -121.6187 | -122.2916
4913.1094 | 122.1634 | -0.11444 | 122.0673 | -0.068283 | 0.016891 | -0.010841 | 0.020234 | 0.047337 | -0.0090406 | 0.071388 | 0.59967 | 0.71411 | 0.41657 | 0.082397 | 112.0239 | 46.7514 | 26.1337 | 26.088 | 122.2824 | -0.2655 | 0.53101 | -121.3531 | 0.71411 | 0.19684 | -10.0433 | -0.15106 | 0.21515 | 0.18311 | 26.2482 | 26.2024 | 112.1384 | 0.82855 | 0.71411 | 122.3969 | 46.8658 | -0.15106 | 0.82855 | 0.71411 | 46.8658 | 112.1384 | 122.3969 | -121.6507 | -122.3328
4914.875 | 122.1817 | -0.10071 | 122.049 | -0.022507 | 0.014328 | -0.0095597 | 0.019593 | 0.046482 | -0.010109 | 0.069893 | 0.55847 | 0.70496 | 0.40283 | 0.07782 | 111.8637 | 47.0718 | 26.3077 | 26.2161 | 122.2687 | -0.27466 | 0.50354 | -121.344 | 0.65918 | 0.17853 | -10.1852 | -0.17395 | 0.21973 | 0.15564 | 26.4084 | 26.3168 | 111.9644 | 0.80566 | 0.65918 | 122.3694 | 47.1725 | -0.17395 | 0.80566 | 0.65918 | 47.1725 | 111.9644 | 122.3694 | -121.6461 | -122.3236
4916.6562 | 122.2 | -0.11902 | 122.0856 | -0.20561 | 0.013687 | -0.012337 | 0.015107 | 0.046482 | -0.0094678 | 0.073525 | 0.49896 | 0.71869 | 0.38452 | 0.027466 | 111.7538 | 47.2916 | 26.564 | 26.3535 | 122.3007 | -0.29755 | 0.50354 | -121.3669 | 0.61798 | 0.14649 | -10.3317 | -0.17853 | 0.21515 | 0.11444 | 26.683 | 26.4725 | 111.8729 | 0.83771 | 0.61798 | 122.4197 | 47.4106 | -0.17853 | 0.83771 | 0.61798 | 47.4106 | 111.8729 | 122.4197 | -121.701 | -122.3831
4918.3594 | 122.2366 | -0.09613 | 122.0352 | 0.16823 | 0.016464 | -0.01255 | 0.015748 | 0.048405 | -0.0083996 | 0.070534 | 0.62256 | 0.6546 | 0.41199 | 0.12817 | 111.7447 | 47.699 | 26.4084 | 26.5869 | 122.2595 | -0.25635 | 0.50812 | -121.3806 | 0.71869 | 0.2243 | -10.2905 | -0.16022 | 0.2243 | 0.21057 | 26.5045 | 26.683 | 111.8408 | 0.75073 | 0.71869 | 122.3557 | 47.7951 | -0.16022 | 0.75073 | 0.71869 | 47.7951 | 111.8408 | 122.3557 | -121.6232 | -122.2916
4920.125 | 122.1405 | -0.12817 | 122.0673 | -0.098801 | 0.013473 | -0.01255 | 0.020662 | 0.047764 | -0.010963 | 0.072243 | 0.55847 | 0.70038 | 0.38452 | 0.09613 | 111.5295 | 47.8867 | 26.7563 | 26.7517 | 122.2733 | -0.2655 | 0.5127 | -121.3669 | 0.68665 | 0.2243 | -10.5377 | -0.13733 | 0.20599 | 0.17395 | 26.8845 | 26.8799 | 111.6577 | 0.82855 | 0.68665 | 122.4014 | 48.0148 | -0.13733 | 0.82855 | 0.68665 | 48.0148 | 111.6577 | 122.4014 | -121.6827 | -122.3328
4921.8281 | 122.2321 | -0.073242 | 122.0444 | 0.14534 | 0.0139 | -0.015755 | 0.014253 | 0.045414 | -0.0069042 | 0.071175 | 0.65918 | 0.72784 | 0.48065 | 0.12817 | 111.4609 | 48.3215 | 26.8112 | 27.0676 | 122.2183 | -0.24719 | 0.55389 | -121.3165 | 0.73242 | 0.20142 | -10.5835 | -0.17395 | 0.17395 | 0.17853 | 26.8845 | 27.1408 | 111.5341 | 0.80109 | 0.73242 | 122.2916 | 48.3948 | -0.17395 | 0.80109 | 0.73242 | 48.3948 | 111.5341 | 122.2916 | -121.5637 | -122.2916
4923.5938 | 122.168 | -0.10529 | 122.0764 | -0.19035 | 0.016464 | -0.012764 | 0.020234 | 0.045414 | -0.006477 | 0.072457 | 0.57678 | 0.79193 | 0.4303 | 0.07782 | 111.319 | 48.761 | 27.2507 | 27.2827 | 122.3053 | -0.27924 | 0.53558 | -121.2845 | 0.68207 | 0.18311 | -10.7574 | -0.17395 | 0.22888 | 0.14648 | 27.356 | 27.388 | 111.4243 | 0.89722 | 0.68207 | 122.4106 | 48.8663 | -0.17395 | 0.89722 | 0.68207 | 48.8663 | 111.4243 | 122.4106 | -121.6461 | -122.3557
4925.3594 | 122.168 | -0.10529 | 122.0947 | -0.21324 | 0.015182 | -0.011696 | 0.014467 | 0.04691 | -0.007118 | 0.070961 | 0.6546 | 0.75531 | 0.49439 | 0.11902 | 111.2457 | 49.0082 | 27.5162 | 27.594 | 122.2504 | -0.28839 | 0.59967 | -121.3394 | 0.75989 | 0.22431 | -10.849 | -0.18311 | 0.15564 | 0.16022 | 27.6215 | 27.6993 | 111.351 | 0.8606 | 0.75989 | 122.3557 | 49.1135 | -0.18311 | 0.8606 | 0.75989 | 49.1135 | 111.351 | 122.3557 | -121.6003 | -122.3831
4927.0625 | 122.2641 | -0.07782 | 122.049 | -0.053024 | 0.015182 | -0.015755 | 0.013612 | 0.041996 | -0.0058362 | 0.073097 | 0.61798 | 0.74616 | 0.46234 | 0.10071 | 111.1221 | 49.3286 | 27.7405 | 27.8915 | 122.2549 | -0.27008 | 0.54016 | -121.3028 | 0.6958 | 0.17853 | -10.9268 | -0.19226 | 0.20599 | 0.15564 | 27.8183 | 27.9694 | 111.2 | 0.82398 | 0.6958 | 122.3328 | 49.4064 | -0.19226 | 0.82398 | 0.6958 | 49.4064 | 111.2 | 122.3328 | -121.5866 | -122.319
4928.8281 | 122.1542 | -0.12817 | 122.0947 | -0.091171 | 0.016891 | -0.0095597 | 0.022584 | 0.045414 | -0.0083996 | 0.074806 | 0.63171 | 0.78278 | 0.43945 | 0.091553 | 110.9253 | 49.5941 | 28.1204 | 28.1616 | 122.2549 | -0.27924 | 0.56763 | -121.312 | 0.75989 | 0.21973 | -11.1694 | -0.15106 | 0.16022 | 0.19226 | 28.2486 | 28.2898 | 111.0535 | 0.91095 | 0.75989 | 122.3831 | 49.7223 | -0.15106 | 0.91095 | 0.75989 | 49.7223 | 111.0535 | 122.3831 | -121.6553 | -122.374
4930.6094 | 122.2 | -0.13275 | 122.0901 | -0.24376 | 0.015182 | -0.011055 | 0.016816 | 0.046482 | -0.0056226 | 0.071175 | 0.65002 | 0.74158 | 0.46692 | 0.11444 | 110.8109 | 50.0107 | 28.5187 | 28.6514 | 122.2458 | -0.2655 | 0.59967 | -121.3486 | 0.78277 | 0.24719 | -11.2793 | -0.13275 | 0.15564 | 0.18311 | 28.6514 | 28.7842 | 110.9436 | 0.87433 | 0.78277 | 122.3785 | 50.1434 | -0.13275 | 0.87433 | 0.78277 | 50.1434 | 110.9436 | 122.3785 | -121.6232 | -122.3557
4932.375 | 122.2275 | -0.082397 | 122.0398 | 0.20638 | 0.013473 | -0.0097733 | 0.01703 | 0.04691 | -0.0086132 | 0.073738 | 0.6546 | 0.6958 | 0.45319 | 0.14648 | 110.6873 | 50.4272 | 28.7796 | 29.1367 | 122.2458 | -0.23804 | 0.53558 | -121.344 | 0.737 | 0.22888 | -11.3525 | -0.15564 | 0.20599 | 0.20142 | 28.862 | 29.2191 | 110.7697 | 0.7782 | 0.737 | 122.3282 | 50.5096 | -0.15564 | 0.7782 | 0.737 | 50.5096 | 110.7697 | 122.3282 | -121.5866 | -122.2778
4934.0781 | 122.2412 | -0.07782 | 122.0581 | 0.17586 | 0.014969 | -0.01255 | 0.019166 | 0.047123 | -0.0090406 | 0.072457 | 0.58594 | 0.70496 | 0.41657 | 0.11444 | 110.527 | 50.7751 | 29.274 | 29.6036 | 122.2229 | -0.25177 | 0.49439 | -121.3531 | 0.66376 | 0.19226 | -11.5311 | -0.17395 | 0.16479 | 0.16937 | 29.3518 | 29.6814 | 110.6049 | 0.78278 | 0.66376 | 122.3007 | 50.853 | -0.17395 | 0.78278 | 0.66376 | 50.853 | 110.6049 | 122.3007 | -121.6415 | -122.3099
4935.8438 | 122.2549 | -0.086975 | 122.0535 | 0.18349 | 0.015396 | -0.013832 | 0.020448 | 0.047123 | -0.0075452 | 0.073311 | 0.62714 | 0.72784 | 0.45319 | 0.11444 | 110.376 | 51.2604 | 29.7318 | 30.098 | 122.2595 | -0.26093 | 0.54016 | -121.3257 | 0.71411 | 0.20142 | -11.6776 | -0.17395 | 0.20599 | 0.17395 | 29.8187 | 30.1849 | 110.463 | 0.81482 | 0.71411 | 122.3465 | 51.3474 | -0.17395 | 0.81482 | 0.71411 | 51.3474 | 110.463 | 122.3465 | -121.6003 | -122.3145
4937.5469 | 122.2137 | -0.10071 | 122.0764 | -0.12169 | 0.014328 | -0.013832 | 0.017671 | 0.044132 | -0.006477 | 0.073952 | 0.56763 | 0.75531 | 0.43488 | 0.036621 | 110.1379 | 51.4847 | 30.4779 | 30.574 | 122.2549 | -0.3067 | 0.53558 | -121.3211 | 0.66834 | 0.13733 | -11.9385 | -0.20599 | 0.17853 | 0.13275 | 30.5786 | 30.6747 | 110.2386 | 0.85602 | 0.66834 | 122.3557 | 51.5854 | -0.20599 | 0.85602 | 0.66834 | 51.5854 | 110.2386 | 122.3557 | -121.6415 | -122.3831
4939.3281 | 122.2687 | -0.091553 | 122.0398 | 0.10719 | 0.014114 | -0.0082779 | 0.018098 | 0.045201 | -0.004768 | 0.075875 | 0.67749 | 0.72784 | 0.48065 | 0.11902 | 110.0464 | 52.002 | 30.8121 | 31.2149 | 122.2183 | -0.27924 | 0.57221 | -121.312 | 0.76904 | 0.21057 | -11.9934 | -0.18768 | 0.17853 | 0.19684 | 30.9036 | 31.3065 | 110.1379 | 0.8194 | 0.76904 | 122.3099 | 52.0935 | -0.18768 | 0.8194 | 0.76904 | 52.0935 | 110.1379 | 122.3099 | -121.5591 | -122.319
4941.0312 | 122.2824 | -0.082397 | 122.0352 | 0.038529 | 0.014328 | -0.017677 | 0.018312 | 0.045414 | -0.0069042 | 0.076515 | 0.61798 | 0.70953 | 0.43945 | 0.091553 | 109.9182 | 52.4643 | 31.3248 | 31.6727 | 122.2321 | -0.27008 | 0.52185 | -121.3257 | 0.70038 | 0.17395 | -12.117 | -0.18768 | 0.19684 | 0.17853 | 31.4072 | 31.7551 | 110.0006 | 0.79193 | 0.70038 | 122.3145 | 52.5467 | -0.18768 | 0.79193 | 0.70038 | 52.5467 | 110.0006 | 122.3145 | -121.5958 | -122.3053
4942.7344 | 122.2504 | -0.068665 | 122.0123 | 0.19112 | 0.015609 | -0.0099869 | 0.023866 | 0.046696 | -0.0077588 | 0.074806 | 0.60883 | 0.74158 | 0.4303 | 0.10071 | 109.7351 | 52.9221 | 31.8878 | 32.2357 | 122.2824 | -0.2655 | 0.49896 | -121.2708 | 0.67749 | 0.16937 | -12.2772 | -0.19684 | 0.27008 | 0.17853 | 31.9565 | 32.3044 | 109.8038 | 0.81024 | 0.67749 | 122.3511 | 52.9907 | -0.19684 | 0.81024 | 0.67749 | 52.9907 | 109.8038 | 122.3511 | -121.582 | -122.2778
4944.5 | 122.1954 | -0.10986 | 122.0673 | -0.26665 | 0.0139 | -0.017036 | 0.01938 | 0.04456 | -0.0073316 | 0.074166 | 0.60425 | 0.70496 | 0.4303 | 0.10529 | 109.6024 | 53.3707 | 32.5928 | 32.8445 | 122.2916 | -0.27466 | 0.54016 | -121.3623 | 0.71411 | 0.21515 | -12.4649 | -0.1648 | 0.2243 | 0.17395 | 32.7026 | 32.9544 | 109.7122 | 0.81482 | 0.71411 | 122.4014 | 53.4805 | -0.1648 | 0.81482 | 0.71411 | 53.4805 | 109.7122 | 122.4014 | -121.637 | -122.3419
4946.2188 | 122.2046 | -0.10986 | 122.049 | -0.22087 | 0.01326 | -0.013832 | 0.023439 | 0.046055 | -0.0056226 | 0.073311 | 0.52643 | 0.72784 | 0.37994 | 0.059509 | 109.3826 | 53.7094 | 33.2062 | 33.2657 | 122.2733 | -0.29297 | 0.48981 | -121.3211 | 0.63629 | 0.16937 | -12.6663 | -0.18311 | 0.2243 | 0.14648 | 33.316 | 33.3755 | 109.4925 | 0.83771 | 0.63629 | 122.3831 | 53.8193 | -0.18311 | 0.83771 | 0.63629 | 53.8193 | 109.4925 | 122.3831 | -121.669 | -122.3419
4947.9844 | 122.2687 | -0.091553 | 122.0169 | 0.091934 | 0.014541 | -0.014473 | 0.019166 | 0.04691 | -0.0056226 | 0.07737 | 0.62714 | 0.6958 | 0.43488 | 0.12817 | 109.3185 | 54.3686 | 33.5587 | 33.9203 | 122.2504 | -0.2655 | 0.52643 | -121.3211 | 0.71869 | 0.21973 | -12.6984 | -0.17395 | 0.23346 | 0.19226 | 33.6502 | 34.0118 | 109.4101 | 0.78735 | 0.71869 | 122.3419 | 54.4601 | -0.17395 | 0.78735 | 0.71869 | 54.4601 | 109.4101 | 122.3419 | -121.582 | -122.2824
4949.75 | 122.1725 | -0.11444 | 122.081 | -0.18272 | 0.014114 | -0.013191 | 0.019807 | 0.042637 | -0.0075452 | 0.076943 | 0.61798 | 0.70496 | 0.44403 | 0.15106 | 109.1858 | 54.9225 | 34.1446 | 34.4788 | 122.2229 | -0.25635 | 0.55847 | -121.376 | 0.73242 | 0.2655 | -12.8952 | -0.14191 | 0.14191 | 0.17395 | 34.259 | 34.5932 | 109.3002 | 0.8194 | 0.73242 | 122.3373 | 55.0369 | -0.14191 | 0.8194 | 0.73242 | 55.0369 | 109.3002 | 122.3373 | -121.637 | -122.3373
4951.4531 | 122.1588 | -0.1236 | 122.0718 | -0.18272 | 0.014755 | -0.014687 | 0.019593 | 0.043705 | -0.006477 | 0.076302 | 0.63629 | 0.68207 | 0.43488 | 0.17395 | 109.0897 | 55.3986 | 34.5749 | 34.996 | 122.2549 | -0.24261 | 0.55847 | -121.3898 | 0.75989 | 0.29755 | -12.9822 | -0.11902 | 0.18311 | 0.20142 | 34.6985 | 35.1196 | 109.2133 | 0.80566 | 0.75989 | 122.3785 | 55.5222 | -0.11902 | 0.80566 | 0.75989 | 55.5222 | 109.2133 | 122.3785 | -121.637 | -122.3145
4953.2031 | 122.2046 | -0.10071 | 122.0581 | -0.22087 | 0.014328 | -0.011055 | 0.022798 | 0.045841 | -0.0049816 | 0.077156 | 0.54932 | 0.72327 | 0.41199 | 0.064087 | 108.7051 | 54.9957 | 34.1904 | 34.4055 | 122.2733 | -0.28839 | 0.5127 | -121.3348 | 0.65002 | 0.1648 | -13.353 | -0.18768 | 0.21515 | 0.13733 | 34.2911 | 34.5062 | 108.8058 | 0.82398 | 0.65002 | 122.374 | 55.0964 | -0.18768 | 0.82398 | 0.65002 | 55.0964 | 108.8058 | 122.374 | -121.6461 | -122.3465
4954.9062 | 122.1588 | -0.1236 | 122.0856 | -0.22087 | 0.015609 | -0.013618 | 0.01938 | 0.044987 | -0.0062634 | 0.075234 | 0.63629 | 0.70038 | 0.41657 | 0.17395 | 108.6044 | 55.2338 | 34.0805 | 34.6161 | 122.2687 | -0.24719 | 0.54016 | -121.3852 | 0.75989 | 0.29755 | -13.4811 | -0.1236 | 0.18311 | 0.21973 | 34.2041 | 34.7397 | 108.728 | 0.82397 | 0.75989 | 122.3923 | 55.3574 | -0.1236 | 0.82397 | 0.75989 | 55.3574 | 108.728 | 122.3923 | -121.669 | -122.3328
4956.6719 | 122.1588 | -0.10986 | 122.0718 | -0.19035 | 0.014328 | -0.013191 | 0.027925 | 0.046696 | -0.0086132 | 0.078865 | 0.55847 | 0.70953 | 0.38452 | 0.10071 | 108.3298 | 55.426 | 34.5108 | 34.8221 | 122.2961 | -0.27924 | 0.49438 | -121.3623 | 0.66834 | 0.21057 | -13.7421 | -0.16937 | 0.22431 | 0.17395 | 34.6207 | 34.9319 | 108.4396 | 0.8194 | 0.66834 | 122.406 | 55.5359 | -0.16937 | 0.8194 | 0.66834 | 55.5359 | 108.4396 | 122.406 | -121.6873 | -122.3511
4958.4375 | 122.1954 | -0.1236 | 122.0581 | -0.27428 | 0.014969 | -0.017891 | 0.020448 | 0.044132 | -0.0062634 | 0.076943 | 0.58136 | 0.71869 | 0.40741 | 0.10071 | 108.1375 | 55.5862 | 34.8633 | 35.2707 | 122.3053 | -0.27924 | 0.53101 | -121.3394 | 0.70496 | 0.2243 | -13.9206 | -0.15564 | 0.24719 | 0.17395 | 34.9869 | 35.3943 | 108.2611 | 0.84229 | 0.70496 | 122.4289 | 55.7098 | -0.15564 | 0.84229 | 0.70496 | 55.7098 | 108.2611 | 122.4289 | -121.6507 | -122.3373
4960.2031 | 122.2321 | -0.086975 | 122.0352 | -0.11406 | 0.014755 | -0.0149 | 0.019807 | 0.047123 | -0.0060498 | 0.078652 | 0.60883 | 0.70038 | 0.43488 | 0.16022 | 108.0139 | 55.9113 | 35.0784 | 35.6552 | 122.2504 | -0.26093 | 0.52185 | -121.3348 | 0.6958 | 0.24719 | -14.0213 | -0.17395 | 0.21515 | 0.17395 | 35.1654 | 35.7422 | 108.1009 | 0.78735 | 0.6958 | 122.3373 | 55.9982 | -0.17395 | 0.78735 | 0.6958 | 55.9982 | 108.1009 | 122.3373 | -121.6003 | -122.2961
4961.9062 | 122.2046 | -0.10986 | 122.049 | -0.24376 | 0.01326 | -0.015755 | 0.023866 | 0.044773 | -0.0069042 | 0.076943 | 0.53101 | 0.74616 | 0.37994 | 0.041199 | 107.7072 | 56.0165 | 35.6735 | 35.907 | 122.3419 | -0.30212 | 0.48981 | -121.3028 | 0.64087 | 0.15106 | -14.3417 | -0.19226 | 0.29297 | 0.15106 | 35.7834 | 36.0168 | 107.8171 | 0.85602 | 0.64087 | 122.4518 | 56.1264 | -0.19226 | 0.85602 | 0.64087 | 56.1264 | 107.8171 | 122.4518 | -121.669 | -122.3511
4963.6719 | 122.2046 | -0.10529 | 122.0673 | -0.25902 | 0.018814 | -0.013405 | 0.026002 | 0.04456 | -0.0045544 | 0.077584 | 0.53558 | 0.74158 | 0.38452 | 0.050354 | 107.5287 | 56.1996 | 35.9802 | 36.2503 | 122.2733 | -0.29755 | 0.48981 | -121.3257 | 0.64087 | 0.15564 | -14.5386 | -0.19226 | 0.20599 | 0.15106 | 36.0855 | 36.3556 | 107.634 | 0.84686 | 0.64087 | 122.3785 | 56.3049 | -0.19226 | 0.84686 | 0.64087 | 56.3049 | 107.634 | 122.3785 | -121.6827 | -122.3648
4965.3594 | 122.2504 | -0.091553 | 122.0261 | 0.16823 | 0.014114 | -0.012337 | 0.02408 | 0.04755 | -0.0060498 | 0.078011 | 0.64087 | 0.68665 | 0.4303 | 0.15564 | 107.4554 | 56.5796 | 36.1313 | 36.7355 | 122.2504 | -0.25177 | 0.52185 | -121.3394 | 0.73242 | 0.24719 | -14.5706 | -0.16022 | 0.2243 | 0.21057 | 36.2228 | 36.8271 | 107.547 | 0.7782 | 0.73242 | 122.3419 | 56.6711 | -0.16022 | 0.7782 | 0.73242 | 56.6711 | 107.547 | 122.3419 | -121.5958 | -122.2778
4967.1406 | 122.2 | -0.11444 | 122.0352 | -0.2285 | 0.016037 | -0.011055 | 0.02408 | 0.047764 | -0.007118 | 0.07972 | 0.57678 | 0.73242 | 0.42572 | 0.054932 | 107.1625 | 56.6528 | 36.6852 | 36.969 | 122.2824 | -0.28839 | 0.54016 | -121.3028 | 0.69122 | 0.16937 | -14.8727 | -0.17395 | 0.24719 | 0.15106 | 36.7996 | 37.0834 | 107.2769 | 0.84686 | 0.69122 | 122.3969 | 56.7673 | -0.17395 | 0.84686 | 0.69122 | 56.7673 | 107.2769 | 122.3969 | -121.6095 | -122.3236
4968.9062 | 122.2687 | -0.068665 | 122.0123 | 0.11482 | 0.014328 | -0.0093461 | 0.027284 | 0.048191 | -0.0066906 | 0.079506 | 0.56763 | 0.72327 | 0.41199 | 0.036621 | 106.9199 | 56.7947 | 36.9919 | 37.2116 | 122.3099 | -0.27466 | 0.48065 | -121.2891 | 0.63629 | 0.10529 | -15.0925 | -0.20599 | 0.29755 | 0.15564 | 37.0605 | 37.2803 | 106.9885 | 0.79193 | 0.63629 | 122.3785 | 56.8634 | -0.20599 | 0.79193 | 0.63629 | 56.8634 | 106.9885 | 122.3785 | -121.6003 | -122.287
4970.6094 | 122.2778 | -0.068665 | 122.0215 | 0.12245 | 0.014328 | -0.0099869 | 0.026429 | 0.048619 | -0.0073316 | 0.082283 | 0.54474 | 0.74158 | 0.40741 | 0.027466 | 106.7459 | 57.0374 | 37.3535 | 37.5504 | 122.2595 | -0.28381 | 0.47608 | -121.2799 | 0.6134 | 0.096131 | -15.2756 | -0.21515 | 0.23804 | 0.13733 | 37.4222 | 37.619 | 106.8146 | 0.81024 | 0.6134 | 122.3282 | 57.106 | -0.21515 | 0.81024 | 0.6134 | 57.106 | 106.8146 | 122.3282 | -121.6141 | -122.3053
4972.375 | 122.2961 | -0.073242 | 122.0032 | 0.01564 | 0.012405 | -0.015327 | 0.01938 | 0.047337 | -0.0062634 | 0.080574 | 0.57678 | 0.69122 | 0.44403 | 0.086975 | 106.6177 | 57.2662 | 37.6053 | 37.9303 | 122.2275 | -0.26093 | 0.51727 | -121.312 | 0.65002 | 0.16022 | -15.3854 | -0.18768 | 0.2243 | 0.13275 | 37.6785 | 38.0035 | 106.691 | 0.76447 | 0.65002 | 122.3007 | 57.3395 | -0.18768 | 0.76447 | 0.65002 | 57.3395 | 106.691 | 122.3007 | -121.5591 | -122.2641
4974.1406 | 122.1313 | -0.11444 | 122.0215 | -0.022507 | 0.012619 | -0.015755 | 0.030061 | 0.047123 | -0.0083996 | 0.083565 | 0.56305 | 0.70496 | 0.37079 | 0.07782 | 106.3202 | 57.3532 | 38.0539 | 38.1683 | 122.2412 | -0.2655 | 0.48523 | -121.3165 | 0.67749 | 0.19226 | -15.7013 | -0.15106 | 0.21973 | 0.19226 | 38.1683 | 38.2828 | 106.4346 | 0.8194 | 0.67749 | 122.3557 | 57.4677 | -0.15106 | 0.8194 | 0.67749 | 57.4677 | 106.4346 | 122.3557 | -121.6507 | -122.287
4975.9062 | 122.2549 | -0.064087 | 122.0032 | 0.091934 | 0.013046 | -0.015755 | 0.026429 | 0.047978 | -0.0069042 | 0.081856 | 0.5127 | 0.72327 | 0.3891 | 0.041199 | 106.1234 | 57.486 | 38.4384 | 38.5483 | 122.2366 | -0.29755 | 0.45319 | -121.2799 | 0.57678 | 0.10529 | -15.8798 | -0.23346 | 0.23346 | 0.1236 | 38.5025 | 38.6124 | 106.1874 | 0.78735 | 0.57678 | 122.3007 | 57.55 | -0.23346 | 0.78735 | 0.57678 | 57.55 | 106.1874 | 122.3007 | -121.6141 | -122.3007
4977.6875 | 122.1771 | -0.091553 | 122.0444 | -0.19798 | 0.017105 | -0.01255 | 0.026429 | 0.046482 | -0.0037 | 0.083138 | 0.52185 | 0.70953 | 0.37079 | 0.050354 | 106.0089 | 57.6324 | 38.9008 | 39.0289 | 122.2275 | -0.29755 | 0.46234 | -121.3348 | 0.6134 | 0.14191 | -16.0355 | -0.20599 | 0.18311 | 0.15106 | 38.9923 | 39.1205 | 106.1005 | 0.80109 | 0.6134 | 122.319 | 57.724 | -0.20599 | 0.80109 | 0.6134 | 57.724 | 106.1005 | 122.319 | -121.6736 | -122.3419
4979.4531 | 122.2504 | -0.068665 | 122.0078 | 0.16823 | 0.016037 | -0.015968 | 0.026643 | 0.050755 | -0.0049816 | 0.083351 | 0.50812 | 0.67749 | 0.35248 | 0.082397 | 105.8212 | 57.843 | 39.1754 | 39.4226 | 122.2687 | -0.2655 | 0.42114 | -121.3303 | 0.57678 | 0.15106 | -16.1865 | -0.19684 | 0.26093 | 0.15564 | 39.2441 | 39.4913 | 105.8899 | 0.74616 | 0.57678 | 122.3373 | 57.9117 | -0.19684 | 0.74616 | 0.57678 | 57.9117 | 105.8899 | 122.3373 | -121.6553 | -122.2733
4981.1562 | 122.1451 | -0.11444 | 122.0856 | -0.083542 | 0.014755 | -0.012337 | 0.029207 | 0.047337 | -0.0056226 | 0.083351 | 0.54016 | 0.66834 | 0.37079 | 0.10071 | 105.6656 | 58.0078 | 39.624 | 39.8575 | 122.2687 | -0.27466 | 0.48523 | -121.4172 | 0.6546 | 0.21515 | -16.42 | -0.16022 | 0.18311 | 0.16937 | 39.7385 | 39.9719 | 105.78 | 0.78278 | 0.6546 | 122.3831 | 58.1223 | -0.16022 | 0.78278 | 0.6546 | 58.1223 | 105.78 | 122.3831 | -121.7148 | -122.3602
4982.8594 | 122.2229 | -0.086975 | 122.0581 | 0.038529 | 0.017959 | -0.012978 | 0.029847 | 0.046696 | -0.0066906 | 0.083351 | 0.48981 | 0.66376 | 0.35248 | 0.022888 | 105.3772 | 58.0994 | 40.0177 | 40.1779 | 122.2961 | -0.28381 | 0.43945 | -121.3943 | 0.57678 | 0.10986 | -16.6809 | -0.19684 | 0.23804 | 0.13733 | 40.1047 | 40.2649 | 105.4642 | 0.75073 | 0.57678 | 122.3831 | 58.1863 | -0.19684 | 0.75073 | 0.57678 | 58.1863 | 105.4642 | 122.3831 | -121.7056 | -122.3419
4984.625 | 122.1771 | -0.1236 | 122.0535 | -0.068283 | 0.014328 | -0.0102 | 0.029207 | 0.049259 | -0.0062634 | 0.084847 | 0.53558 | 0.67291 | 0.37079 | 0.07782 | 105.1804 | 58.2504 | 40.3244 | 40.535 | 122.287 | -0.27924 | 0.49438 | -121.3806 | 0.65918 | 0.20142 | -16.8732 | -0.15564 | 0.23346 | 0.16479 | 40.448 | 40.6586 | 105.304 | 0.79651 | 0.65918 | 122.4106 | 58.374 | -0.15564 | 0.79651 | 0.65918 | 58.374 | 105.304 | 122.4106 | -121.6827 | -122.3328
4986.3125 | 122.287 | -0.068665 | 122.0444 | -0.014877 | 0.014755 | -0.013191 | 0.020875 | 0.045628 | -0.0032728 | 0.083138 | 0.52643 | 0.67291 | 0.37994 | 0.10071 | 105.0339 | 58.4473 | 40.5441 | 40.8875 | 122.2733 | -0.25177 | 0.44861 | -121.3715 | 0.59509 | 0.16937 | -17.0105 | -0.1831 | 0.22888 | 0.14648 | 40.6128 | 40.9561 | 105.1025 | 0.74158 | 0.59509 | 122.3419 | 58.5159 | -0.1831 | 0.74158 | 0.59509 | 58.5159 | 105.1025 | 122.3419 | -121.6644 | -122.2961
4988.0938 | 122.1634 | -0.11444 | 122.1313 | -0.21324 | 0.015182 | -0.014259 | 0.026216 | 0.046482 | -0.0041272 | 0.082924 | 0.60425 | 0.62714 | 0.39825 | 0.16022 | 104.8233 | 58.6075 | 40.8691 | 41.2491 | 122.2778 | -0.23346 | 0.5127 | -121.5042 | 0.71869 | 0.27466 | -17.308 | -0.11902 | 0.14648 | 0.20599 | 40.9836 | 41.3635 | 104.9377 | 0.74158 | 0.71869 | 122.3923 | 58.7219 | -0.11902 | 0.74158 | 0.71869 | 58.7219 | 104.9377 | 122.3923 | -121.7331 | -122.3648
4989.8594 | 122.1725 | -0.10986 | 122.0856 | -0.12169 | 0.017318 | -0.015541 | 0.030702 | 0.047764 | -0.0083996 | 0.085701 | 0.54016 | 0.67749 | 0.35706 | 0.10529 | 104.5029 | 58.5617 | 41.2079 | 41.3956 | 122.3145 | -0.26093 | 0.46692 | -121.4081 | 0.65002 | 0.21515 | -17.5827 | -0.15106 | 0.22888 | 0.18311 | 41.3177 | 41.5054 | 104.6127 | 0.78735 | 0.65002 | 122.4243 | 58.6716 | -0.15106 | 0.78735 | 0.65002 | 58.6716 | 104.6127 | 122.4243 | -121.7285 | -122.3465
4991.5469 | 122.1954 | -0.10986 | 122.0901 | -0.022507 | 0.019241 | -0.012123 | 0.035188 | 0.048405 | -0.004768 | 0.086769 | 0.53101 | 0.66834 | 0.35706 | 0.082397 | 104.2328 | 58.6075 | 41.4642 | 41.5054 | 122.3007 | -0.28381 | 0.46692 | -121.4218 | 0.64087 | 0.19226 | -17.8574 | -0.17395 | 0.21057 | 0.17395 | 41.5741 | 41.6153 | 104.3427 | 0.7782 | 0.64087 | 122.4106 | 58.7173 | -0.17395 | 0.7782 | 0.64087 | 58.7173 | 104.3427 | 122.4106 | -121.7331 | -122.374
4993.3125 | 122.3236 | -0.086975 | 122.0535 | 0.0080111 | 0.017105 | -0.014473 | 0.025575 | 0.047337 | -0.0037 | 0.08506 | 0.54932 | 0.65918 | 0.37994 | 0.091553 | 104.0771 | 58.7448 | 41.5558 | 41.7755 | 122.2961 | -0.24719 | 0.46692 | -121.3943 | 0.63629 | 0.17853 | -17.9764 | -0.16022 | 0.24262 | 0.16937 | 41.6428 | 41.8625 | 104.1641 | 0.74616 | 0.63629 | 122.3831 | 58.8318 | -0.16022 | 0.74616 | 0.63629 | 58.8318 | 104.1641 | 122.3831 | -121.6736 | -122.3007
4995.0781 | 122.2687 | -0.073242 | 122.0398 | 0.15297 | 0.013687 | -0.0091325 | 0.032411 | 0.049473 | -0.0049816 | 0.088051 | 0.53101 | 0.68207 | 0.37079 | 0.082397 | 103.775 | 58.7723 | 41.7847 | 41.8945 | 122.287 | -0.26093 | 0.44403 | -121.3577 | 0.60425 | 0.15564 | -18.2648 | -0.18768 | 0.24719 | 0.16022 | 41.8579 | 41.9678 | 103.8483 | 0.75531 | 0.60425 | 122.3602 | 58.8455 | -0.18768 | 0.75531 | 0.60425 | 58.8455 | 103.8483 | 122.3602 | -121.669 | -122.3007
4996.8438 | 122.319 | -0.059509 | 122.049 | 0.12245 | 0.014969 | -0.016396 | 0.033052 | 0.048832 | -0.006477 | 0.089333 | 0.50354 | 0.67749 | 0.36621 | 0.045776 | 103.4866 | 58.8409 | 42.0776 | 42.0319 | 122.3373 | -0.27924 | 0.42572 | -121.3715 | 0.56305 | 0.10528 | -18.5623 | -0.21973 | 0.28839 | 0.13733 | 42.1371 | 42.0914 | 103.5461 | 0.737 | 0.56305 | 122.3969 | 58.9005 | -0.21973 | 0.737 | 0.56305 | 58.9005 | 103.5461 | 122.3969 | -121.6827 | -122.3282
4998.6094 | 122.168 | -0.12817 | 122.1039 | -0.091171 | 0.014755 | -0.016396 | 0.033479 | 0.04755 | -0.0039136 | 0.089974 | 0.55389 | 0.66834 | 0.35248 | 0.10071 | 103.2806 | 58.9966 | 42.3065 | 42.2836 | 122.3099 | -0.27924 | 0.48065 | -121.4355 | 0.68207 | 0.22888 | -18.8232 | -0.15106 | 0.20599 | 0.20142 | 42.4347 | 42.4118 | 103.4088 | 0.79651 | 0.68207 | 122.438 | 59.1248 | -0.15106 | 0.79651 | 0.68207 | 59.1248 | 103.4088 | 122.438 | -121.7514 | -122.3831
5000.3125 | 122.2916 | -0.086975 | 122.0856 | -0.045395 | 0.014114 | -0.012978 | 0.027284 | 0.046482 | -0.00135 | 0.088906 | 0.5127 | 0.61798 | 0.37079 | 0.11902 | 103.1204 | 59.1522 | 42.4072 | 42.5537 | 122.2824 | -0.26093 | 0.45776 | -121.4676 | 0.59967 | 0.20599 | -18.9651 | -0.17395 | 0.19684 | 0.14191 | 42.4942 | 42.6407 | 103.2074 | 0.70496 | 0.59967 | 122.3694 | 59.2392 | -0.17395 | 0.70496 | 0.59967 | 59.2392 | 103.2074 | 122.3694 | -121.7148 | -122.3465
5002.0938 | 122.2549 | -0.091553 | 122.0764 | 0.15297 | 0.016037 | -0.01255 | 0.031984 | 0.048405 | -0.0032728 | 0.089119 | 0.56763 | 0.59052 | 0.36163 | 0.15106 | 102.832 | 59.2484 | 42.5171 | 42.7277 | 122.2778 | -0.24719 | 0.45319 | -121.4859 | 0.65918 | 0.24261 | -19.2444 | -0.15564 | 0.20142 | 0.20599 | 42.6086 | 42.8192 | 102.9236 | 0.68207 | 0.65918 | 122.3694 | 59.3399 | -0.15564 | 0.68207 | 0.65918 | 59.3399 | 102.9236 | 122.3694 | -121.7148 | -122.3236
5003.8594 | 122.2412 | -0.10986 | 122.1085 | -0.25902 | 0.015396 | -0.014473 | 0.031984 | 0.045841 | -0.0049816 | 0.090187 | 0.42572 | 0.6134 | 0.27924 | 0.050354 | 102.4567 | 59.2163 | 42.952 | 42.8055 | 122.3511 | -0.27924 | 0.3891 | -121.4951 | 0.53558 | 0.16022 | -19.6518 | -0.16937 | 0.24262 | 0.14648 | 43.0618 | 42.9153 | 102.5665 | 0.72327 | 0.53558 | 122.4609 | 59.3262 | -0.16937 | 0.72327 | 0.53558 | 59.3262 | 102.5665 | 122.4609 | -121.8292 | -122.3877
5005.5625 | 122.1771 | -0.1236 | 122.113 | -0.19035 | 0.015182 | -0.015327 | 0.02942 | 0.045841 | -0.0037 | 0.08976 | 0.54474 | 0.58594 | 0.36163 | 0.15106 | 102.3376 | 59.4086 | 42.952 | 43.1625 | 122.2916 | -0.24261 | 0.48523 | -121.5271 | 0.66834 | 0.27466 | -19.7754 | -0.11902 | 0.17853 | 0.18311 | 43.0756 | 43.2861 | 102.4612 | 0.70953 | 0.66834 | 122.4152 | 59.5322 | -0.11902 | 0.70953 | 0.66834 | 59.5322 | 102.4612 | 122.4152 | -121.7514 | -122.3557
5007.3438 | 122.3236 | -0.064087 | 122.0627 | 0.00038159 | 0.015182 | -0.0099869 | 0.033052 | 0.043919 | -0.0009228 | 0.091255 | 0.50812 | 0.60883 | 0.35706 | 0.10529 | 102.0218 | 59.4681 | 43.1625 | 43.2312 | 122.3099 | -0.28381 | 0.42114 | -121.4539 | 0.5722 | 0.16937 | -20.0409 | -0.21973 | 0.24719 | 0.15106 | 43.2266 | 43.2953 | 102.0859 | 0.67291 | 0.5722 | 122.374 | 59.5322 | -0.21973 | 0.67291 | 0.5722 | 59.5322 | 102.0859 | 122.374 | -121.7056 | -122.3465
5009.0469 | 122.3236 | -0.07782 | 122.0673 | 0.091934 | 0.015182 | -0.010841 | 0.033052 | 0.04691 | -0.001991 | 0.091683 | 0.5722 | 0.65918 | 0.40283 | 0.11444 | 101.7609 | 59.6237 | 43.3594 | 43.4692 | 122.287 | -0.23804 | 0.48065 | -121.4081 | 0.65002 | 0.19226 | -20.3064 | -0.16022 | 0.21973 | 0.16937 | 43.4372 | 43.5471 | 101.8387 | 0.737 | 0.65002 | 122.3648 | 59.7015 | -0.16022 | 0.737 | 0.65002 | 59.7015 | 101.8387 | 122.3648 | -121.6644 | -122.3053
5010.75 | 122.2137 | -0.10529 | 122.0718 | 0.0080111 | 0.016678 | -0.012978 | 0.040529 | 0.048191 | -0.0045544 | 0.091896 | 0.54016 | 0.69122 | 0.35706 | 0.07782 | 101.4816 | 59.6466 | 43.6295 | 43.5791 | 122.3373 | -0.27924 | 0.46234 | -121.3806 | 0.64545 | 0.18311 | -20.5902 | -0.17395 | 0.2655 | 0.18311 | 43.7347 | 43.6844 | 101.5869 | 0.79651 | 0.64545 | 122.4426 | 59.7519 | -0.17395 | 0.79651 | 0.64545 | 59.7519 | 101.5869 | 122.4426 | -121.7148 | -122.3511
5012.5312 | 122.1909 | -0.11444 | 122.0627 | -0.19035 | 0.014755 | -0.010628 | 0.039247 | 0.045841 | -0.004768 | 0.093178 | 0.49896 | 0.67749 | 0.33417 | 0.086975 | 101.2756 | 59.8114 | 43.8995 | 43.8629 | 122.3282 | -0.27466 | 0.44861 | -121.3852 | 0.6134 | 0.20142 | -20.787 | -0.16022 | 0.2655 | 0.1648 | 44.014 | 43.9774 | 101.3901 | 0.79193 | 0.6134 | 122.4426 | 59.9258 | -0.16022 | 0.79193 | 0.6134 | 59.9258 | 101.3901 | 122.4426 | -121.7285 | -122.3373
5014.2969 | 122.2137 | -0.10071 | 122.0993 | -0.12932 | 0.014328 | -0.015755 | 0.032411 | 0.04456 | -0.003059 | 0.093178 | 0.59509 | 0.65002 | 0.38452 | 0.16937 | 101.1887 | 60.0677 | 44.0094 | 44.2474 | 122.2595 | -0.25635 | 0.48523 | -121.4493 | 0.6958 | 0.27008 | -20.9106 | -0.15564 | 0.16022 | 0.21057 | 44.1101 | 44.3481 | 101.2894 | 0.75073 | 0.6958 | 122.3602 | 60.1685 | -0.15564 | 0.75073 | 0.6958 | 60.1685 | 101.2894 | 122.3602 | -121.7148 | -122.3557
5016.0625 | 122.2687 | -0.073242 | 122.0581 | 0.13008 | 0.014969 | -0.014259 | 0.038392 | 0.047978 | -0.0051954 | 0.096596 | 0.58136 | 0.63629 | 0.37537 | 0.15564 | 100.8911 | 60.1547 | 44.1925 | 44.4305 | 122.2778 | -0.22888 | 0.44861 | -121.4218 | 0.6546 | 0.22888 | -21.167 | -0.15564 | 0.21973 | 0.20599 | 44.2657 | 44.5038 | 100.9644 | 0.70953 | 0.6546 | 122.3511 | 60.228 | -0.15564 | 0.70953 | 0.6546 | 60.228 | 100.9644 | 122.3511 | -121.6827 | -122.287
5017.8281 | 122.3007 | -0.068665 | 122.0627 | 0.13771 | 0.015823 | -0.012123 | 0.040315 | 0.045628 | -0.0022046 | 0.096382 | 0.50354 | 0.67749 | 0.3479 | 0.086975 | 100.589 | 60.2097 | 44.5358 | 44.5541 | 122.2778 | -0.27466 | 0.41656 | -121.3852 | 0.5722 | 0.15564 | -21.4737 | -0.20599 | 0.21515 | 0.15564 | 44.6045 | 44.6228 | 100.6577 | 0.74616 | 0.5722 | 122.3465 | 60.2783 | -0.20599 | 0.74616 | 0.5722 | 60.2783 | 100.6577 | 122.3465 | -121.7148 | -122.3373
5019.5938 | 122.2 | -0.1236 | 122.113 | -0.19035 | 0.010482 | -0.017891 | 0.032624 | 0.043492 | -0.0024182 | 0.095314 | 0.55847 | 0.64087 | 0.35706 | 0.16022 | 100.4745 | 60.4385 | 44.7189 | 44.7739 | 122.2595 | -0.24719 | 0.48065 | -121.4722 | 0.68207 | 0.28381 | -21.6385 | -0.1236 | 0.14648 | 0.20142 | 44.8425 | 44.8975 | 100.5981 | 0.76447 | 0.68207 | 122.3831 | 60.5621 | -0.1236 | 0.76447 | 0.68207 | 60.5621 | 100.5981 | 122.3831 | -121.756 | -122.3602
5021.2969 | 122.3236 | -0.082397 | 122.0947 | 0.10719 | 0.011764 | -0.0196 | 0.03647 | 0.047978 | -6.8404e-05 | 0.095314 | 0.53101 | 0.6134 | 0.37079 | 0.13275 | 100.1862 | 60.6628 | 44.9661 | 44.3115 | 122.2916 | -0.25177 | 0.45319 | -121.4813 | 0.6134 | 0.21515 | -21.9086 | -0.16937 | 0.19684 | 0.16022 | 45.0485 | 44.3939 | 100.2686 | 0.6958 | 0.6134 | 122.374 | 60.7452 | -0.16937 | 0.6958 | 0.6134 | 60.7452 | 100.2686 | 122.374 | -121.7239 | -122.3465
5023.0625 | 122.3053 | -0.07782 | 122.0444 | 0.10719 | 0.013687 | -0.013832 | 0.039674 | 0.046055 | -0.0024182 | 0.097664 | 0.55847 | 0.61798 | 0.37079 | 0.13275 | 99.9115 | 60.8276 | 45.2271 | 44.7235 | 122.3053 | -0.23346 | 0.44861 | -121.4264 | 0.63629 | 0.21057 | -22.1329 | -0.15564 | 0.26093 | 0.18768 | 45.3049 | 44.8013 | 99.9893 | 0.6958 | 0.63629 | 122.3831 | 60.9055 | -0.15564 | 0.6958 | 0.63629 | 60.9055 | 99.9893 | 122.3831 | -121.6736 | -122.2778
5024.8438 | 122.3053 | -0.068665 | 122.0764 | 0.11482 | 0.014328 | -0.012337 | 0.038392 | 0.045414 | -0.0007092 | 0.09745 | 0.54474 | 0.6134 | 0.33417 | 0.12817 | 99.6597 | 60.9924 | 45.4559 | 44.9295 | 122.2824 | -0.23804 | 0.40283 | -121.463 | 0.6134 | 0.19684 | -22.4167 | -0.16937 | 0.20599 | 0.21057 | 45.5246 | 44.9982 | 99.7284 | 0.68207 | 0.6134 | 122.3511 | 61.0611 | -0.16937 | 0.68207 | 0.6134 | 61.0611 | 99.7284 | 122.3511 | -121.7422 | -122.3145
5026.5469 | 122.3282 | -0.082397 | 122.0764 | 0.061417 | 0.012191 | -0.015968 | 0.040956 | 0.045414 | -0.0007092 | 0.10001 | 0.52643 | 0.59967 | 0.37994 | 0.10986 | 99.4446 | 61.0886 | 45.6711 | 45.1218 | 122.2961 | -0.27008 | 0.46234 | -121.4767 | 0.60882 | 0.19226 | -22.6318 | -0.18768 | 0.21973 | 0.14648 | 45.7535 | 45.2042 | 99.527 | 0.68207 | 0.60882 | 122.3785 | 61.171 | -0.18768 | 0.68207 | 0.60882 | 61.171 | 99.527 | 122.3785 | -121.6965 | -122.3465
5028.3125 | 122.3282 | -0.073242 | 122.0856 | 0.00038159 | 0.014328 | -0.015541 | 0.03946 | 0.045414 | -0.00135 | 0.10001 | 0.50812 | 0.60883 | 0.3479 | 0.11444 | 99.1928 | 61.2167 | 45.9503 | 45.4285 | 122.3053 | -0.2655 | 0.42114 | -121.4767 | 0.58136 | 0.18768 | -22.8928 | -0.19226 | 0.21973 | 0.16022 | 46.0236 | 45.5017 | 99.2661 | 0.68207 | 0.58136 | 122.3785 | 61.29 | -0.19226 | 0.68207 | 0.58136 | 61.29 | 99.2661 | 122.3785 | -121.7377 | -122.3511
5030.0781 | 122.2778 | -0.082397 | 122.0352 | 0.15297 | 0.015182 | -0.012123 | 0.044801 | 0.046269 | -0.00135 | 0.10065 | 0.47607 | 0.62256 | 0.28839 | 0.10529 | 98.9227 | 61.3083 | 46.1838 | 45.6345 | 122.287 | -0.25177 | 0.37079 | -121.4127 | 0.55847 | 0.18768 | -23.1125 | -0.16937 | 0.25177 | 0.18768 | 46.2662 | 45.7169 | 99.0051 | 0.70496 | 0.55847 | 122.3694 | 61.3907 | -0.16937 | 0.70496 | 0.55847 | 61.3907 | 99.0051 | 122.3694 | -121.7468 | -122.287
5031.7812 | 122.3328 | -0.082397 | 122.0764 | 0.038529 | 0.01326 | -0.015541 | 0.039888 | 0.045841 | -0.000282 | 0.10215 | 0.48065 | 0.59509 | 0.3479 | 0.1236 | 98.7488 | 61.4868 | 46.4264 | 45.932 | 122.2641 | -0.2655 | 0.4303 | -121.4813 | 0.56305 | 0.20599 | -23.3276 | -0.18311 | 0.18768 | 0.13275 | 46.5088 | 46.0144 | 98.8312 | 0.67749 | 0.56305 | 122.3465 | 61.5692 | -0.18311 | 0.67749 | 0.56305 | 61.5692 | 98.8312 | 122.3465 | -121.7285 | -122.3419
5033.5469 | 122.3145 | -0.07782 | 122.0764 | 0.091934 | 0.016678 | -0.011482 | 0.047578 | 0.045628 | -0.003059 | 0.10343 | 0.45319 | 0.61798 | 0.3067 | 0.059509 | 98.465 | 61.5692 | 46.756 | 46.17 | 122.2824 | -0.27466 | 0.38452 | -121.4584 | 0.53101 | 0.13733 | -23.6114 | -0.19684 | 0.20599 | 0.14648 | 46.8338 | 46.2479 | 98.5428 | 0.6958 | 0.53101 | 122.3602 | 61.647 | -0.19684 | 0.6958 | 0.53101 | 61.647 | 98.5428 | 122.3602 | -121.7697 | -122.3511
5035.2969 | 122.319 | -0.07782 | 122.0764 | 0.099564 | 0.014328 | -0.014259 | 0.042451 | 0.046696 | 0.0018542 | 0.10322 | 0.52185 | 0.60425 | 0.35248 | 0.13733 | 98.3414 | 61.7249 | 46.9025 | 46.4951 | 122.2916 | -0.26093 | 0.4303 | -121.4722 | 0.59967 | 0.21515 | -23.735 | -0.18311 | 0.21515 | 0.16937 | 46.9803 | 46.5729 | 98.4192 | 0.68207 | 0.59967 | 122.3694 | 61.8027 | -0.18311 | 0.68207 | 0.59967 | 61.8027 | 98.4192 | 122.3694 | -121.7239 | -122.3373
5037.0781 | 122.3282 | -0.082397 | 122.0718 | 0.02327 | 0.012405 | -0.014046 | 0.044374 | 0.046055 | 0.0007862 | 0.10471 | 0.54932 | 0.64087 | 0.39368 | 0.13733 | 98.0942 | 61.8347 | 47.1313 | 46.7422 | 122.3145 | -0.24719 | 0.47607 | -121.431 | 0.63171 | 0.21973 | -23.9777 | -0.16479 | 0.24262 | 0.15564 | 47.2137 | 46.8246 | 98.1766 | 0.72327 | 0.63171 | 122.3969 | 61.9171 | -0.16479 | 0.72327 | 0.63171 | 61.9171 | 98.1766 | 122.3969 | -121.6782 | -122.319
5038.7969 | 122.1909 | -0.1236 | 122.0901 | -0.19798 | 0.013473 | -0.015541 | 0.045442 | 0.043919 | -0.000282 | 0.10514 | 0.58136 | 0.60425 | 0.3479 | 0.18768 | 97.9294 | 62.0087 | 47.406 | 47.1359 | 122.2824 | -0.24719 | 0.4715 | -121.4859 | 0.70496 | 0.31128 | -24.1608 | -0.1236 | 0.19226 | 0.23346 | 47.5296 | 47.2595 | 98.053 | 0.72784 | 0.70496 | 122.406 | 62.1323 | -0.1236 | 0.72784 | 0.70496 | 62.1323 | 98.053 | 122.406 | -121.7422 | -122.3373
5040.5625 | 122.3236 | -0.064087 | 122.081 | 0.084305 | 0.016464 | -0.013405 | 0.05121 | 0.04691 | -0.00135 | 0.10664 | 0.46234 | 0.63629 | 0.32959 | 0.073242 | 97.6089 | 62.0407 | 47.7859 | 47.2366 | 122.3099 | -0.27008 | 0.39368 | -121.4447 | 0.52643 | 0.13733 | -24.472 | -0.20599 | 0.22888 | 0.13275 | 47.85 | 47.3007 | 97.673 | 0.70038 | 0.52643 | 122.374 | 62.1048 | -0.20599 | 0.70038 | 0.52643 | 62.1048 | 97.673 | 122.374 | -121.7514 | -122.3511
5042.3281 | 122.2046 | -0.13275 | 122.1039 | -0.18272 | 0.0139 | -0.012337 | 0.043519 | 0.045201 | -0.0017774 | 0.10471 | 0.54016 | 0.5722 | 0.33875 | 0.1831 | 97.5632 | 62.3566 | 47.9279 | 47.6761 | 122.2961 | -0.25177 | 0.4715 | -121.5317 | 0.67291 | 0.31586 | -24.5407 | -0.11902 | 0.19226 | 0.20142 | 48.0606 | 47.8088 | 97.6959 | 0.70496 | 0.67291 | 122.4289 | 62.4893 | -0.11902 | 0.70496 | 0.67291 | 62.4893 | 97.6959 | 122.4289 | -121.7651 | -122.3557
5044.1094 | 122.2778 | -0.054932 | 122.0901 | 0.17586 | 0.016037 | -0.012978 | 0.049287 | 0.046696 | -0.000282 | 0.106 | 0.52643 | 0.61798 | 0.3479 | 0.14191 | 97.2794 | 62.3932 | 48.1155 | 47.8455 | 122.3007 | -0.24719 | 0.40283 | -121.4722 | 0.58136 | 0.19684 | -24.8108 | -0.19226 | 0.21057 | 0.17853 | 48.1705 | 47.9004 | 97.3343 | 0.67291 | 0.58136 | 122.3557 | 62.4481 | -0.19226 | 0.67291 | 0.58136 | 62.4481 | 97.3343 | 122.3557 | -121.7422 | -122.3373
5045.8125 | 122.3145 | -0.059509 | 122.0581 | 0.099564 | 0.014755 | -0.015327 | 0.052064 | 0.046269 | -0.000282 | 0.10728 | 0.45776 | 0.63629 | 0.29297 | 0.073242 | 97.0322 | 62.4298 | 48.4406 | 48.0057 | 122.3282 | -0.28381 | 0.35248 | -121.4218 | 0.51727 | 0.13275 | -25.0259 | -0.2243 | 0.27008 | 0.1648 | 48.5001 | 48.0652 | 97.0917 | 0.6958 | 0.51727 | 122.3877 | 62.4893 | -0.2243 | 0.6958 | 0.51727 | 62.4893 | 97.0917 | 122.3877 | -121.7651 | -122.3419
5047.5781 | 122.2778 | -0.082397 | 122.0856 | 0.069046 | 0.013046 | -0.016182 | 0.049073 | 0.047337 | -0.0007092 | 0.10749 | 0.54474 | 0.6134 | 0.35248 | 0.16022 | 96.9406 | 62.645 | 48.4726 | 48.3078 | 122.2687 | -0.25177 | 0.43488 | -121.4722 | 0.62714 | 0.24261 | -25.145 | -0.16937 | 0.18311 | 0.19226 | 48.555 | 48.3902 | 97.023 | 0.6958 | 0.62714 | 122.3511 | 62.7274 | -0.16937 | 0.6958 | 0.62714 | 62.7274 | 97.023 | 122.3511 | -121.7331 | -122.3373
5049.2812 | 122.2733 | -0.086975 | 122.0764 | 0.091934 | 0.015609 | -0.01255 | 0.050569 | 0.048619 | 0.0003588 | 0.10899 | 0.56305 | 0.60883 | 0.35248 | 0.16479 | 96.7621 | 62.7594 | 48.6603 | 48.4634 | 122.2733 | -0.23804 | 0.43945 | -121.4676 | 0.65002 | 0.25177 | -25.3143 | -0.15106 | 0.19684 | 0.21057 | 48.7473 | 48.5504 | 96.8491 | 0.6958 | 0.65002 | 122.3602 | 62.8464 | -0.15106 | 0.6958 | 0.65002 | 62.8464 | 96.8491 | 122.3602 | -121.7239 | -122.3145
5051.0469 | 122.2229 | -0.1236 | 122.113 | -0.12932 | 0.016891 | -0.013618 | 0.047364 | 0.046055 | 0.0007862 | 0.11027 | 0.56305 | 0.59967 | 0.35706 | 0.1831 | 96.6156 | 62.8922 | 48.8388 | 48.6786 | 122.2549 | -0.24261 | 0.48065 | -121.5134 | 0.68665 | 0.3067 | -25.4974 | -0.11902 | 0.14191 | 0.20599 | 48.9624 | 48.8022 | 96.7392 | 0.72327 | 0.68665 | 122.3785 | 63.0157 | -0.11902 | 0.72327 | 0.68665 | 63.0157 | 96.7392 | 122.3785 | -121.756 | -122.3557
5052.8281 | 122.2412 | -0.11444 | 122.1085 | -0.24376 | 0.011123 | -0.013618 | 0.053773 | 0.045201 | -0.000282 | 0.11198 | 0.44403 | 0.63171 | 0.30212 | 0.073242 | 96.2769 | 62.8006 | 49.1409 | 48.6511 | 122.3328 | -0.28381 | 0.41657 | -121.4767 | 0.55847 | 0.18768 | -25.8316 | -0.16937 | 0.22431 | 0.14191 | 49.2554 | 48.7656 | 96.3913 | 0.74616 | 0.55847 | 122.4472 | 62.915 | -0.16937 | 0.74616 | 0.55847 | 62.915 | 96.3913 | 122.4472 | -121.8063 | -122.3923
5054.6094 | 122.2458 | -0.11902 | 122.1085 | -0.25139 | 0.014328 | -0.014046 | 0.051851 | 0.043278 | 0.0009998 | 0.10899 | 0.49439 | 0.60883 | 0.34332 | 0.09613 | 96.1075 | 62.9059 | 49.1867 | 48.8434 | 122.319 | -0.28839 | 0.46234 | -121.4996 | 0.6134 | 0.21515 | -26.001 | -0.16937 | 0.21057 | 0.15106 | 49.3057 | 48.9624 | 96.2265 | 0.72784 | 0.6134 | 122.438 | 63.0249 | -0.16937 | 0.72784 | 0.6134 | 63.0249 | 96.2265 | 122.438 | -121.7651 | -122.3969
5056.3125 | 122.3007 | -0.054932 | 122.0581 | 0.099564 | 0.013473 | -0.013191 | 0.050782 | 0.045628 | 0.0018542 | 0.11048 | 0.52643 | 0.59967 | 0.35248 | 0.15564 | 95.9702 | 63.0112 | 49.1364 | 48.9807 | 122.2824 | -0.25177 | 0.40741 | -121.4584 | 0.58136 | 0.21057 | -26.088 | -0.19684 | 0.22431 | 0.17395 | 49.1913 | 49.0356 | 96.0251 | 0.6546 | 0.58136 | 122.3373 | 63.0661 | -0.19684 | 0.6546 | 0.58136 | 63.0661 | 96.0251 | 122.3373 | -121.7056 | -122.3099
5058.0781 | 122.2824 | -0.068665 | 122.0627 | 0.1606 | 0.014969 | -0.011909 | 0.054841 | 0.047978 | -0.0034864 | 0.11219 | 0.53101 | 0.58594 | 0.33417 | 0.1831 | 95.8099 | 63.0981 | 49.1638 | 49.0814 | 122.3007 | -0.21515 | 0.40283 | -121.4767 | 0.59967 | 0.25177 | -26.2527 | -0.14648 | 0.23804 | 0.19684 | 49.2325 | 49.1501 | 95.8786 | 0.6546 | 0.59967 | 122.3694 | 63.1668 | -0.14648 | 0.6546 | 0.59967 | 63.1668 | 95.8786 | 122.3694 | -121.7285 | -122.2778
5059.8438 | 122.1863 | -0.1236 | 122.0947 | -0.19798 | 0.01625 | -0.016823 | 0.052064 | 0.046482 | -0.000282 | 0.11262 | 0.54474 | 0.57678 | 0.33417 | 0.19226 | 95.6406 | 63.2446 | 49.3332 | 49.2599 | 122.319 | -0.24261 | 0.45776 | -121.5179 | 0.66834 | 0.31586 | -26.4542 | -0.11902 | 0.2243 | 0.21057 | 49.4568 | 49.3835 | 95.7642 | 0.70038 | 0.66834 | 122.4426 | 63.3682 | -0.11902 | 0.70038 | 0.66834 | 63.3682 | 95.7642 | 122.4426 | -121.7606 | -122.3373
5061.6094 | 122.3053 | -0.073242 | 122.0856 | 0.030899 | 0.014114 | -0.015755 | 0.058687 | 0.048191 | -0.0015638 | 0.11262 | 0.42114 | 0.60883 | 0.28381 | 0.050354 | 95.3384 | 63.1165 | 49.5209 | 49.1043 | 122.3373 | -0.26093 | 0.35706 | -121.4767 | 0.49438 | 0.1236 | -26.7471 | -0.18768 | 0.25177 | 0.13733 | 49.5941 | 49.1776 | 95.4117 | 0.68207 | 0.49438 | 122.4106 | 63.1897 | -0.18768 | 0.68207 | 0.49438 | 63.1897 | 95.4117 | 122.4106 | -121.8018 | -122.3465
5063.375 | 122.3328 | -0.073242 | 122.0856 | 0.11482 | 0.014328 | -0.015327 | 0.055696 | 0.045628 | 0.0009998 | 0.11668 | 0.4303 | 0.60883 | 0.27008 | 0.050354 | 95.1828 | 63.1393 | 49.4659 | 49.118 | 122.2961 | -0.27924 | 0.34332 | -121.4767 | 0.50354 | 0.1236 | -26.9028 | -0.20599 | 0.21057 | 0.16022 | 49.5392 | 49.1913 | 95.256 | 0.68207 | 0.50354 | 122.3694 | 63.2126 | -0.20599 | 0.68207 | 0.50354 | 63.2126 | 95.256 | 122.3694 | -121.8155 | -122.3648
5065.0781 | 122.2229 | -0.1236 | 122.0947 | -0.030136 | 0.01326 | -0.015755 | 0.058473 | 0.048405 | -0.0009228 | 0.11262 | 0.46692 | 0.59052 | 0.28381 | 0.11444 | 95.0317 | 63.2034 | 49.4476 | 49.1638 | 122.3099 | -0.27008 | 0.40741 | -121.5042 | 0.59052 | 0.23804 | -27.063 | -0.14649 | 0.21515 | 0.18311 | 49.5712 | 49.2874 | 95.1553 | 0.71411 | 0.59052 | 122.4335 | 63.327 | -0.14649 | 0.71411 | 0.59052 | 63.327 | 95.1553 | 122.4335 | -121.8109 | -122.3648
5066.8281 | 122.3099 | -0.054932 | 122.081 | 0.00038159 | 0.015182 | -0.018745 | 0.052491 | 0.046055 | 0.0007862 | 0.11347 | 0.44861 | 0.5722 | 0.32959 | 0.1236 | 94.8853 | 63.2309 | 49.3744 | 49.2233 | 122.287 | -0.27466 | 0.38452 | -121.5088 | 0.50354 | 0.17853 | -27.1957 | -0.21973 | 0.20599 | 0.11902 | 49.4293 | 49.2783 | 94.9402 | 0.62714 | 0.50354 | 122.3419 | 63.2858 | -0.21973 | 0.62714 | 0.50354 | 63.2858 | 94.9402 | 122.3419 | -121.7514 | -122.3557
5068.6094 | 122.3145 | -0.068665 | 122.0993 | -0.022507 | 0.014969 | -0.013191 | 0.05356 | 0.046696 | 0.0024952 | 0.11475 | 0.43945 | 0.58136 | 0.30212 | 0.11902 | 94.7021 | 63.1668 | 49.3652 | 49.2599 | 122.3053 | -0.2655 | 0.37079 | -121.5179 | 0.50812 | 0.18768 | -27.3972 | -0.19684 | 0.20599 | 0.13733 | 49.4339 | 49.3286 | 94.7708 | 0.65002 | 0.50812 | 122.374 | 63.2355 | -0.19684 | 0.65002 | 0.50812 | 63.2355 | 94.7708 | 122.374 | -121.7972 | -122.3648
5070.3125 | 122.3007 | -0.068665 | 122.081 | 0.091934 | 0.016464 | -0.0097733 | 0.060823 | 0.046269 | 0.0003588 | 0.11454 | 0.39825 | 0.58136 | 0.24261 | 0.073242 | 94.4366 | 63.0753 | 49.4614 | 49.205 | 122.3053 | -0.28381 | 0.31128 | -121.4996 | 0.46692 | 0.14191 | -27.6443 | -0.21515 | 0.2243 | 0.15564 | 49.53 | 49.2737 | 94.5053 | 0.65002 | 0.46692 | 122.374 | 63.1439 | -0.21515 | 0.65002 | 0.46692 | 63.1439 | 94.5053 | 122.374 | -121.8384 | -122.3648
5072.0938 | 122.2641 | -0.086975 | 122.113 | 0.046158 | 0.01625 | -0.012337 | 0.061036 | 0.044773 | 0.0001452 | 0.11817 | 0.39825 | 0.56763 | 0.24261 | 0.059509 | 94.2673 | 62.9791 | 49.4385 | 49.2004 | 122.3282 | -0.27924 | 0.32959 | -121.5454 | 0.48523 | 0.14648 | -27.8458 | -0.19226 | 0.21515 | 0.15564 | 49.5255 | 49.2874 | 94.3542 | 0.6546 | 0.48523 | 122.4152 | 63.0661 | -0.19226 | 0.6546 | 0.48523 | 63.0661 | 94.3542 | 122.4152 | -121.8704 | -122.3923
5073.7969 | 122.2778 | -0.086975 | 122.0901 | 0.16823 | 0.013046 | -0.015968 | 0.056978 | 0.04691 | 0.003136 | 0.11817 | 0.48981 | 0.53101 | 0.27924 | 0.17853 | 94.2123 | 63.1393 | 49.2142 | 49.3332 | 122.2504 | -0.23804 | 0.36621 | -121.5591 | 0.57678 | 0.2655 | -27.8778 | -0.15106 | 0.16022 | 0.21057 | 49.3011 | 49.4202 | 94.2993 | 0.61798 | 0.57678 | 122.3373 | 63.2263 | -0.15106 | 0.61798 | 0.57678 | 63.2263 | 94.2993 | 122.3373 | -121.8109 | -122.3282
5075.5469 | 122.3099 | -0.082397 | 122.0581 | 0.11482 | 0.016678 | -0.014473 | 0.055482 | 0.044987 | 0.0022814 | 0.11881 | 0.4303 | 0.52185 | 0.2655 | 0.11902 | 93.9285 | 62.9791 | 49.2233 | 49.324 | 122.3007 | -0.24261 | 0.3479 | -121.5363 | 0.5127 | 0.20142 | -28.1296 | -0.16022 | 0.24262 | 0.1648 | 49.3057 | 49.4064 | 94.0109 | 0.60425 | 0.5127 | 122.3831 | 63.0615 | -0.16022 | 0.60425 | 0.5127 | 63.0615 | 94.0109 | 122.3831 | -121.7926 | -122.3007
5077.3125 | 122.2092 | -0.11902 | 122.1222 | -0.19035 | 0.014969 | -0.016396 | 0.057832 | 0.04456 | -0.000282 | 0.11881 | 0.4715 | 0.50812 | 0.26093 | 0.16479 | 93.782 | 62.8967 | 49.2462 | 49.3378 | 122.2916 | -0.26093 | 0.37994 | -121.6141 | 0.59052 | 0.28381 | -28.3401 | -0.14191 | 0.16937 | 0.21057 | 49.3652 | 49.4568 | 93.9011 | 0.62714 | 0.59052 | 122.4106 | 63.0157 | -0.14191 | 0.62714 | 0.59052 | 63.0157 | 93.9011 | 122.4106 | -121.8613 | -122.3831
5079.0312 | 122.2046 | -0.10986 | 122.1313 | -0.19798 | 0.015182 | -0.013618 | 0.059968 | 0.046055 | 0.0027088 | 0.11839 | 0.44403 | 0.50812 | 0.26093 | 0.16937 | 93.5806 | 62.851 | 49.1821 | 49.205 | 122.287 | -0.2655 | 0.37079 | -121.6232 | 0.55389 | 0.27924 | -28.5507 | -0.15564 | 0.15564 | 0.18311 | 49.292 | 49.3149 | 93.6905 | 0.61798 | 0.55389 | 122.3969 | 62.9608 | -0.15564 | 0.61798 | 0.55389 | 62.9608 | 93.6905 | 122.3969 | -121.8704 | -122.3969
5080.7969 | 122.3236 | -0.064087 | 122.0627 | 0.099564 | 0.014541 | -0.012337 | 0.0636 | 0.044987 | 0.0003588 | 0.12244 | 0.35248 | 0.54932 | 0.21973 | 0.045776 | 93.2602 | 62.6495 | 49.118 | 49.0082 | 122.3053 | -0.27466 | 0.28381 | -121.5134 | 0.41657 | 0.10986 | -28.8025 | -0.21057 | 0.24261 | 0.13275 | 49.1821 | 49.0723 | 93.3243 | 0.6134 | 0.41657 | 122.3694 | 62.7136 | -0.21057 | 0.6134 | 0.41657 | 62.7136 | 93.3243 | 122.3694 | -121.843 | -122.3373
5082.5625 | 122.2137 | -0.10986 | 122.0901 | -0.0072479 | 0.01625 | -0.012978 | 0.0636 | 0.046482 | 0.0003588 | 0.1218 | 0.39825 | 0.53558 | 0.20599 | 0.10071 | 93.0588 | 62.5946 | 49.0952 | 49.0402 | 122.3053 | -0.28839 | 0.31586 | -121.5546 | 0.50812 | 0.21057 | -29.0314 | -0.17853 | 0.21515 | 0.19226 | 49.205 | 49.1501 | 93.1686 | 0.64545 | 0.50812 | 122.4152 | 62.7045 | -0.17853 | 0.64545 | 0.50812 | 62.7045 | 93.1686 | 122.4152 | -121.8842 | -122.3785
5084.3281 | 122.3328 | -0.082397 | 122.0581 | 0.084305 | 0.013473 | -0.016396 | 0.058259 | 0.04691 | 0.0027088 | 0.1233 | 0.42114 | 0.49439 | 0.25635 | 0.13275 | 92.9443 | 62.6358 | 48.9487 | 49.086 | 122.2778 | -0.25177 | 0.33875 | -121.5637 | 0.50354 | 0.21515 | -29.1138 | -0.16937 | 0.21973 | 0.16479 | 49.0311 | 49.1684 | 93.0267 | 0.57678 | 0.50354 | 122.3602 | 62.7182 | -0.16937 | 0.57678 | 0.50354 | 62.7182 | 93.0267 | 122.3602 | -121.8018 | -122.3099
5086.0312 | 122.1954 | -0.1236 | 122.0764 | -0.068283 | 0.014755 | -0.0095597 | 0.067231 | 0.046269 | 0.0027088 | 0.12437 | 0.40283 | 0.5127 | 0.20599 | 0.15106 | 92.6926 | 62.558 | 48.9944 | 49.0356 | 122.3145 | -0.2655 | 0.32959 | -121.5637 | 0.52643 | 0.27466 | -29.3838 | -0.14191 | 0.23804 | 0.19684 | 49.118 | 49.1592 | 92.8162 | 0.63629 | 0.52643 | 122.438 | 62.6816 | -0.14191 | 0.63629 | 0.52643 | 62.6816 | 92.8162 | 122.438 | -121.8704 | -122.3419
5087.7969 | 122.3099 | -0.086975 | 122.0947 | 0.11482 | 0.016037 | -0.010841 | 0.059114 | 0.044773 | 0.0033496 | 0.12437 | 0.42572 | 0.5127 | 0.25635 | 0.1236 | 92.4774 | 62.4664 | 48.8388 | 49.0128 | 122.2733 | -0.23346 | 0.34332 | -121.582 | 0.5127 | 0.21057 | -29.6173 | -0.14648 | 0.17853 | 0.16937 | 48.9258 | 49.0997 | 92.5644 | 0.59967 | 0.5127 | 122.3602 | 62.5534 | -0.14648 | 0.59967 | 0.5127 | 62.5534 | 92.5644 | 122.3602 | -121.8384 | -122.3282
5089.5781 | 122.3236 | -0.068665 | 122.0718 | 0.0080111 | 0.01326 | -0.016182 | 0.061891 | 0.044346 | 0.003136 | 0.12394 | 0.40741 | 0.51727 | 0.25177 | 0.13733 | 92.2623 | 62.384 | 48.8663 | 49.0311 | 122.3007 | -0.2655 | 0.32044 | -121.5546 | 0.47608 | 0.20599 | -29.8096 | -0.19684 | 0.22888 | 0.15564 | 48.9349 | 49.0997 | 92.3309 | 0.58594 | 0.47608 | 122.3694 | 62.4527 | -0.19684 | 0.58594 | 0.47608 | 62.4527 | 92.3309 | 122.3694 | -121.8201 | -122.3373
5091.3438 | 122.2595 | -0.10071 | 122.1176 | 0.091934 | 0.014969 | -0.012337 | 0.071504 | 0.047764 | 0.0001452 | 0.12501 | 0.37537 | 0.52643 | 0.22888 | 0.086975 | 91.9556 | 62.2696 | 48.967 | 48.88 | 122.3465 | -0.2655 | 0.32959 | -121.5912 | 0.47607 | 0.18768 | -30.162 | -0.16479 | 0.22888 | 0.14648 | 49.0677 | 48.9807 | 92.0563 | 0.62714 | 0.47607 | 122.4472 | 62.3703 | -0.16479 | 0.62714 | 0.47607 | 62.3703 | 92.0563 | 122.4472 | -121.8887 | -122.3831
5093.0469 | 122.2 | -0.10986 | 122.1268 | -0.19035 | 0.012832 | -0.016609 | 0.066163 | 0.046269 | 0.001427 | 0.12394 | 0.36621 | 0.53558 | 0.20599 | 0.13733 | 91.8228 | 62.2375 | 48.8937 | 48.9258 | 122.3145 | -0.27924 | 0.31586 | -121.5912 | 0.47607 | 0.24719 | -30.304 | -0.16937 | 0.18768 | 0.16022 | 49.0036 | 49.0356 | 91.9327 | 0.64545 | 0.47607 | 122.4243 | 62.3474 | -0.16937 | 0.64545 | 0.47607 | 62.3474 | 91.9327 | 122.4243 | -121.9208 | -122.406
5094.8281 | 122.2275 | -0.10529 | 122.113 | -0.25902 | 0.011337 | -0.012764 | 0.064027 | 0.043919 | 0.003136 | 0.12608 | 0.37537 | 0.50354 | 0.23346 | 0.10071 | 91.6168 | 62.1643 | 48.7839 | 48.8892 | 122.2916 | -0.28839 | 0.33875 | -121.6095 | 0.48065 | 0.20599 | -30.4962 | -0.18311 | 0.17853 | 0.14191 | 48.8892 | 48.9944 | 91.7221 | 0.60883 | 0.48065 | 122.3969 | 62.2696 | -0.18311 | 0.60883 | 0.48065 | 62.2696 | 91.7221 | 122.3969 | -121.8796 | -122.4014
5096.6094 | 122.2092 | -0.13275 | 122.1085 | -0.12169 | 0.014755 | -0.015968 | 0.062532 | 0.044773 | 0.0044178 | 0.12544 | 0.44403 | 0.4715 | 0.24261 | 0.20599 | 91.4429 | 62.1826 | 48.5641 | 48.9487 | 122.2824 | -0.24719 | 0.37537 | -121.637 | 0.57678 | 0.33875 | -30.6656 | -0.11444 | 0.17395 | 0.20142 | 48.6969 | 49.0814 | 91.5756 | 0.60425 | 0.57678 | 122.4152 | 62.3154 | -0.11444 | 0.60425 | 0.57678 | 62.3154 | 91.5756 | 122.4152 | -121.8658 | -122.3557
5098.375 | 122.3053 | -0.068665 | 122.0718 | 0.076676 | 0.014328 | -0.0102 | 0.070222 | 0.04755 | 0.0029224 | 0.1265 | 0.32044 | 0.4715 | 0.17853 | 0.086975 | 91.1316 | 62.0041 | 48.5962 | 48.7335 | 122.3099 | -0.28381 | 0.24719 | -121.6003 | 0.3891 | 0.15564 | -30.9402 | -0.21515 | 0.23804 | 0.14191 | 48.6649 | 48.8022 | 91.2003 | 0.54016 | 0.3891 | 122.3785 | 62.0728 | -0.21515 | 0.54016 | 0.3891 | 62.0728 | 91.2003 | 122.3785 | -121.8933 | -122.3557
5100.0781 | 122.2778 | -0.091553 | 122.0856 | 0.1606 | 0.013687 | -0.011055 | 0.069368 | 0.046269 | 0.0029224 | 0.12885 | 0.42114 | 0.45319 | 0.21057 | 0.18768 | 91.008 | 62.0132 | 48.381 | 48.8708 | 122.2641 | -0.25177 | 0.30212 | -121.6324 | 0.5127 | 0.27924 | -31.0776 | -0.16022 | 0.17853 | 0.21057 | 48.4726 | 48.9624 | 91.0995 | 0.54474 | 0.5127 | 122.3557 | 62.1048 | -0.16022 | 0.54474 | 0.5127 | 62.1048 | 91.0995 | 122.3557 | -121.875 | -122.3373
5101.8438 | 122.2183 | -0.10529 | 122.1176 | -0.23613 | 0.011764 | -0.015327 | 0.068727 | 0.046269 | 0.0018542 | 0.12779 | 0.3891 | 0.44861 | 0.21057 | 0.15564 | 90.7379 | 61.8347 | 48.4863 | 48.8388 | 122.319 | -0.2655 | 0.31586 | -121.669 | 0.49438 | 0.26093 | -31.3797 | -0.16022 | 0.20142 | 0.17853 | 48.5916 | 48.9441 | 90.8432 | 0.55389 | 0.49438 | 122.4243 | 61.94 | -0.16022 | 0.55389 | 0.49438 | 61.94 | 90.8432 | 122.4243 | -121.907 | -122.3831
5103.625 | 122.2733 | -0.09613 | 122.0627 | 0.15297 | 0.0139 | -0.012337 | 0.070222 | 0.046055 | 0.003136 | 0.1312 | 0.41199 | 0.45319 | 0.21057 | 0.20142 | 90.5502 | 61.8713 | 48.2986 | 48.8113 | 122.287 | -0.22888 | 0.3067 | -121.6095 | 0.50812 | 0.29755 | -31.5125 | -0.13275 | 0.2243 | 0.20142 | 48.3948 | 48.9075 | 90.6464 | 0.54932 | 0.50812 | 122.3831 | 61.9675 | -0.13275 | 0.54932 | 0.50812 | 61.9675 | 90.6464 | 122.3831 | -121.8521 | -122.2916
5105.3281 | 122.2366 | -0.10071 | 122.0856 | 0.053787 | 0.016464 | -0.013618 | 0.075135 | 0.046269 | 0.0009998 | 0.12821 | 0.32959 | 0.48981 | 0.16022 | 0.091553 | 90.2664 | 61.6516 | 48.4772 | 48.7244 | 122.3328 | -0.27924 | 0.26093 | -121.5958 | 0.4303 | 0.19226 | -31.8192 | -0.17853 | 0.24719 | 0.16937 | 48.5779 | 48.8251 | 90.3671 | 0.59052 | 0.4303 | 122.4335 | 61.7523 | -0.17853 | 0.59052 | 0.4303 | 61.7523 | 90.3671 | 122.4335 | -121.9254 | -122.3648
5107.0938 | 122.1634 | -0.1236 | 122.113 | -0.091171 | 0.014541 | -0.014046 | 0.074067 | 0.044132 | 0.004845 | 0.13206 | 0.36163 | 0.46692 | 0.16937 | 0.15106 | 90.1382 | 61.7065 | 48.4222 | 48.848 | 122.3053 | -0.2655 | 0.29297 | -121.6461 | 0.48523 | 0.27466 | -31.9748 | -0.14191 | 0.19226 | 0.19226 | 48.5458 | 48.9716 | 90.2618 | 0.59052 | 0.48523 | 122.4289 | 61.8301 | -0.14191 | 0.59052 | 0.48523 | 61.8301 | 90.2618 | 122.4289 | -121.9437 | -122.3785
5108.8594 | 122.2961 | -0.064087 | 122.0535 | -0.083542 | 0.014969 | -0.015114 | 0.06894 | 0.044773 | 0.005913 | 0.13291 | 0.36163 | 0.43488 | 0.18768 | 0.17853 | 89.946 | 61.6928 | 48.2529 | 48.8663 | 122.2641 | -0.2655 | 0.25177 | -121.6187 | 0.42572 | 0.24261 | -32.1075 | -0.20142 | 0.21057 | 0.17395 | 48.317 | 48.9304 | 90.0101 | 0.49896 | 0.42572 | 122.3282 | 61.7569 | -0.20142 | 0.49896 | 0.42572 | 61.7569 | 90.0101 | 122.3282 | -121.8658 | -122.319
5110.6406 | 122.2687 | -0.086975 | 122.0581 | 0.1606 | 0.017105 | -0.011909 | 0.072358 | 0.048191 | 0.0044178 | 0.13355 | 0.42114 | 0.44403 | 0.19226 | 0.20142 | 89.7446 | 61.6928 | 48.2025 | 48.9304 | 122.2916 | -0.23346 | 0.27924 | -121.6141 | 0.50812 | 0.28839 | -32.3135 | -0.14648 | 0.23346 | 0.22888 | 48.2895 | 49.0173 | 89.8315 | 0.53101 | 0.50812 | 122.3785 | 61.7798 | -0.14648 | 0.53101 | 0.50812 | 61.7798 | 89.8315 | 122.3785 | -121.8658 | -122.2916
5112.4062 | 122.2412 | -0.10071 | 122.081 | -0.24376 | 0.016891 | -0.015755 | 0.074708 | 0.044132 | 0.0044178 | 0.13483 | 0.28839 | 0.46692 | 0.14648 | 0.09613 | 89.3875 | 61.4594 | 48.4406 | 48.8434 | 122.3373 | -0.28839 | 0.24719 | -121.6141 | 0.3891 | 0.19684 | -32.6935 | -0.18768 | 0.25635 | 0.14191 | 48.5413 | 48.9441 | 89.4882 | 0.56763 | 0.3891 | 122.438 | 61.5601 | -0.18768 | 0.56763 | 0.3891 | 61.5601 | 89.4882 | 122.438 | -121.9345 | -122.3694
5114.1094 | 122.2687 | -0.086975 | 122.0673 | 0.099564 | 0.014541 | -0.014473 | 0.076417 | 0.049473 | 0.0035632 | 0.13633 | 0.37537 | 0.43488 | 0.16937 | 0.18768 | 89.1907 | 61.4639 | 48.1842 | 48.8892 | 122.2824 | -0.23346 | 0.25635 | -121.6324 | 0.46234 | 0.27466 | -32.8766 | -0.14648 | 0.21515 | 0.20599 | 48.2712 | 48.9761 | 89.2776 | 0.52185 | 0.46234 | 122.3694 | 61.5509 | -0.14648 | 0.52185 | 0.46234 | 61.5509 | 89.2776 | 122.3694 | -121.8979 | -122.3007
5115.875 | 122.2046 | -0.11444 | 122.0947 | -0.030136 | 0.015182 | -0.015114 | 0.079622 | 0.047764 | 0.003136 | 0.13462 | 0.32959 | 0.4715 | 0.15564 | 0.13275 | 88.9206 | 61.2762 | 48.3215 | 48.848 | 122.3282 | -0.27924 | 0.27008 | -121.6232 | 0.44403 | 0.24719 | -33.1741 | -0.16479 | 0.23346 | 0.17395 | 48.436 | 48.9624 | 89.035 | 0.58594 | 0.44403 | 122.4426 | 61.3907 | -0.16479 | 0.58594 | 0.44403 | 61.3907 | 89.035 | 122.4426 | -121.9391 | -122.374
5117.6406 | 122.2046 | -0.11902 | 122.1039 | -0.022507 | 0.014755 | -0.012123 | 0.078981 | 0.048405 | 0.001427 | 0.13804 | 0.32501 | 0.4303 | 0.14191 | 0.1236 | 88.6642 | 61.2259 | 48.2803 | 48.7564 | 122.3373 | -0.2655 | 0.26093 | -121.6736 | 0.44403 | 0.24261 | -33.4396 | -0.14648 | 0.23346 | 0.18311 | 48.3994 | 48.8754 | 88.7833 | 0.54932 | 0.44403 | 122.4564 | 61.3449 | -0.14648 | 0.54932 | 0.44403 | 61.3449 | 88.7833 | 122.4564 | -121.962 | -122.3694
5119.3594 | 122.3053 | -0.073242 | 122.0627 | 0.099564 | 0.013687 | -0.0102 | 0.072358 | 0.048191 | 0.005913 | 0.1374 | 0.34332 | 0.3891 | 0.16479 | 0.14191 | 88.4354 | 61.2167 | 48.1522 | 48.7656 | 122.2687 | -0.24719 | 0.23804 | -121.6736 | 0.41656 | 0.21515 | -33.6273 | -0.17395 | 0.20599 | 0.17853 | 48.2254 | 48.8388 | 88.5086 | 0.46234 | 0.41656 | 122.3419 | 61.29 | -0.17395 | 0.46234 | 0.41656 | 61.29 | 88.5086 | 122.3419 | -121.8979 | -122.3099
5121.125 | 122.2733 | -0.091553 | 122.0581 | 0.18349 | 0.015823 | -0.01255 | 0.07834 | 0.047337 | 0.0050586 | 0.14018 | 0.28839 | 0.41657 | 0.1236 | 0.1236 | 88.2431 | 61.1389 | 48.175 | 48.7701 | 122.2916 | -0.24719 | 0.21515 | -121.6415 | 0.37994 | 0.21515 | -33.815 | -0.15564 | 0.23346 | 0.1648 | 48.2666 | 48.8617 | 88.3347 | 0.50812 | 0.37994 | 122.3831 | 61.2305 | -0.15564 | 0.50812 | 0.37994 | 61.2305 | 88.3347 | 122.3831 | -121.9345 | -122.3053
5122.8281 | 122.3145 | -0.082397 | 122.0444 | 0.13008 | 0.013687 | -0.0093461 | 0.08069 | 0.045414 | 0.0046314 | 0.13911 | 0.25177 | 0.44403 | 0.1236 | 0.059509 | 87.9501 | 61.0382 | 48.2483 | 48.6649 | 122.2961 | -0.27924 | 0.20599 | -121.6003 | 0.33417 | 0.14191 | -34.0942 | -0.19684 | 0.25177 | 0.12817 | 48.3307 | 48.7473 | 88.0325 | 0.52643 | 0.33417 | 122.3785 | 61.1206 | -0.19684 | 0.52643 | 0.33417 | 61.1206 | 88.0325 | 122.3785 | -121.9208 | -122.3236
5124.5938 | 122.2092 | -0.11902 | 122.0856 | -0.045395 | 0.01326 | -0.015327 | 0.082826 | 0.045414 | 0.0039904 | 0.13847 | 0.31128 | 0.45319 | 0.12817 | 0.11444 | 87.735 | 60.965 | 48.2437 | 48.8571 | 122.3145 | -0.27466 | 0.24719 | -121.6324 | 0.4303 | 0.23346 | -34.3506 | -0.15564 | 0.22888 | 0.1831 | 48.3627 | 48.9761 | 87.854 | 0.5722 | 0.4303 | 122.4335 | 61.084 | -0.15564 | 0.5722 | 0.4303 | 61.084 | 87.854 | 122.4335 | -121.9574 | -122.3602
5126.3594 | 122.1725 | -0.12817 | 122.1176 | -0.20561 | 0.013473 | -0.017464 | 0.075349 | 0.044773 | 0.0052722 | 0.1421 | 0.35248 | 0.38452 | 0.16022 | 0.20142 | 87.2864 | 60.9329 | 48.1339 | 49.0082 | 122.2687 | -0.23804 | 0.28839 | -121.7331 | 0.48065 | 0.32959 | -34.8312 | -0.10986 | 0.15106 | 0.19226 | 48.262 | 49.1364 | 87.4146 | 0.5127 | 0.48065 | 122.3969 | 61.0611 | -0.10986 | 0.5127 | 0.48065 | 61.0611 | 87.4146 | 122.3969 | -121.9574 | -122.3557
5128.0625 | 122.2916 | -0.068665 | 122.0673 | 0.11482 | 0.014541 | -0.015755 | 0.078981 | 0.043705 | 0.005913 | 0.14167 | 0.35248 | 0.38452 | 0.16937 | 0.15564 | 86.9614 | 60.7407 | 48.0972 | 49.0265 | 122.2504 | -0.23804 | 0.23804 | -121.6827 | 0.42114 | 0.22431 | -35.1059 | -0.16937 | 0.1831 | 0.18311 | 48.1659 | 49.0952 | 87.03 | 0.45319 | 0.42114 | 122.319 | 60.8093 | -0.16937 | 0.45319 | 0.42114 | 60.8093 | 87.03 | 122.319 | -121.8979 | -122.3053
5129.7812 | 122.168 | -0.11444 | 122.0856 | -0.083542 | 0.014114 | -0.01725 | 0.086457 | 0.047123 | 0.0029224 | 0.1406 | 0.31128 | 0.42572 | 0.1236 | 0.13275 | 86.9293 | 60.7269 | 48.2574 | 49.0906 | 122.3099 | -0.27008 | 0.23804 | -121.6599 | 0.42572 | 0.24719 | -35.1562 | -0.15564 | 0.2243 | 0.18768 | 48.3719 | 49.205 | 87.0438 | 0.54016 | 0.42572 | 122.4243 | 60.8414 | -0.15564 | 0.54016 | 0.42572 | 60.8414 | 87.0438 | 122.4243 | -121.962 | -122.3557
5131.5469 | 122.1817 | -0.10986 | 122.0901 | -0.083542 | 0.015182 | -0.014473 | 0.087312 | 0.047978 | 0.0039904 | 0.14445 | 0.31586 | 0.41657 | 0.13275 | 0.14191 | 86.4395 | 60.6033 | 48.2483 | 49.0906 | 122.287 | -0.27466 | 0.24261 | -121.6736 | 0.42572 | 0.25177 | -35.6506 | -0.1648 | 0.19684 | 0.18311 | 48.3582 | 49.2004 | 86.5494 | 0.52643 | 0.42572 | 122.3969 | 60.7132 | -0.1648 | 0.52643 | 0.42572 | 60.7132 | 86.5494 | 122.3969 | -121.9574 | -122.3648
5133.3281 | 122.1863 | -0.1236 | 122.113 | -0.19798 | 0.012832 | -0.015968 | 0.079835 | 0.046482 | 0.0061268 | 0.14295 | 0.33875 | 0.39825 | 0.14648 | 0.19226 | 85.5652 | 60.3287 | 48.0652 | 49.0814 | 122.2778 | -0.25635 | 0.27008 | -121.7148 | 0.46234 | 0.31586 | -36.5479 | -0.13275 | 0.16479 | 0.19226 | 48.1888 | 49.205 | 85.6888 | 0.52185 | 0.46234 | 122.4014 | 60.4523 | -0.13275 | 0.52185 | 0.46234 | 60.4523 | 85.6888 | 122.4014 | -121.9666 | -122.3694
5135.1094 | 122.3053 | -0.082397 | 122.081 | -0.022507 | 0.012832 | -0.0093461 | 0.081117 | 0.045414 | 0.0069812 | 0.1453 | 0.30212 | 0.40283 | 0.13275 | 0.15564 | 86.4899 | 60.64 | 48.0789 | 49.0814 | 122.2778 | -0.24719 | 0.21515 | -121.6782 | 0.38452 | 0.23804 | -35.5911 | -0.16479 | 0.19684 | 0.16937 | 48.1613 | 49.1638 | 86.5723 | 0.48523 | 0.38452 | 122.3602 | 60.7224 | -0.16479 | 0.48523 | 0.38452 | 60.7224 | 86.5723 | 122.3602 | -121.9482 | -122.3282
5136.8281 | 122.287 | -0.064087 | 122.0627 | -0.030136 | 0.015609 | -0.015968 | 0.08304 | 0.043278 | 0.0063404 | 0.14616 | 0.30212 | 0.3891 | 0.14648 | 0.16937 | 85.9955 | 60.5255 | 48.056 | 49.0768 | 122.2687 | -0.23804 | 0.21057 | -121.6736 | 0.36621 | 0.23346 | -36.0672 | -0.17395 | 0.20599 | 0.15564 | 48.1201 | 49.1409 | 86.0596 | 0.45319 | 0.36621 | 122.3328 | 60.5896 | -0.17395 | 0.45319 | 0.36621 | 60.5896 | 86.0596 | 122.3328 | -121.9162 | -122.3007
5138.5938 | 122.3007 | -0.050354 | 122.0627 | 0.061417 | 0.015609 | -0.014046 | 0.091371 | 0.047123 | 0.0033496 | 0.14616 | 0.23346 | 0.41657 | 0.10529 | 0.10529 | 85.5011 | 60.2646 | 48.1201 | 48.8983 | 122.3099 | -0.28839 | 0.15564 | -121.6461 | 0.28381 | 0.15564 | -36.5616 | -0.23804 | 0.24719 | 0.12817 | 48.1705 | 48.9487 | 85.5515 | 0.46692 | 0.28381 | 122.3602 | 60.3149 | -0.23804 | 0.46692 | 0.28381 | 60.3149 | 85.5515 | 122.3602 | -121.9574 | -122.3511
5140.3594 | 122.2824 | -0.086975 | 122.0581 | 0.084305 | 0.013046 | -0.017891 | 0.086244 | 0.04691 | 0.006554 | 0.15086 | 0.34332 | 0.38452 | 0.14191 | 0.16937 | 84.6222 | 60.1273 | 47.9324 | 48.9349 | 122.2916 | -0.25177 | 0.22888 | -121.6736 | 0.4303 | 0.25635 | -37.4359 | -0.16479 | 0.23346 | 0.20142 | 48.0194 | 49.0219 | 84.7092 | 0.4715 | 0.4303 | 122.3785 | 60.2142 | -0.16479 | 0.4715 | 0.4303 | 60.2142 | 84.7092 | 122.3785 | -121.9162 | -122.3099
5142.0625 | 122.2824 | -0.073242 | 122.0673 | -0.060654 | 0.015823 | -0.014259 | 0.086885 | 0.046055 | 0.0063404 | 0.14979 | 0.32044 | 0.40741 | 0.14191 | 0.18768 | 84.9884 | 60.2829 | 47.9462 | 48.9716 | 122.2458 | -0.25177 | 0.21515 | -121.6599 | 0.39368 | 0.26092 | -37.0789 | -0.17853 | 0.17853 | 0.17853 | 48.0194 | 49.0448 | 85.0616 | 0.48065 | 0.39368 | 122.319 | 60.3561 | -0.17853 | 0.48065 | 0.39368 | 60.3561 | 85.0616 | 122.319 | -121.9254 | -122.319
5143.8281 | 122.168 | -0.11444 | 122.1039 | -0.15221 | 0.015609 | -0.015541 | 0.093507 | 0.047337 | 0.0046314 | 0.14957 | 0.29755 | 0.43488 | 0.10529 | 0.15564 | 84.8099 | 60.1639 | 48.143 | 49.0448 | 122.3053 | -0.27008 | 0.21973 | -121.669 | 0.41199 | 0.27008 | -37.294 | -0.15564 | 0.20142 | 0.19226 | 48.2574 | 49.1592 | 84.9243 | 0.54932 | 0.41199 | 122.4197 | 60.2783 | -0.15564 | 0.54932 | 0.41199 | 60.2783 | 84.9243 | 122.4197 | -121.9986 | -122.374
5145.6094 | 122.2092 | -0.12817 | 122.1268 | -0.22087 | 0.014969 | -0.013832 | 0.090303 | 0.045414 | 0.006554 | 0.15107 | 0.34332 | 0.41199 | 0.15564 | 0.17853 | 84.874 | 60.2142 | 48.1613 | 49.0814 | 122.2549 | -0.25177 | 0.28381 | -121.7148 | 0.4715 | 0.3067 | -37.2528 | -0.1236 | 0.12817 | 0.18768 | 48.2895 | 49.2096 | 85.0021 | 0.54016 | 0.4715 | 122.3831 | 60.3424 | -0.1236 | 0.54016 | 0.4715 | 60.3424 | 85.0021 | 122.3831 | -121.9711 | -122.3785
5147.3281 | 122.2733 | -0.091553 | 122.0718 | -0.060654 | 0.013473 | -0.0149 | 0.087953 | 0.043705 | 0.0074084 | 0.15427 | 0.32501 | 0.40283 | 0.14191 | 0.18768 | 83.1711 | 59.8114 | 48.0515 | 48.9716 | 122.2733 | -0.25177 | 0.23346 | -121.669 | 0.41657 | 0.27924 | -38.9008 | -0.16022 | 0.20142 | 0.18311 | 48.143 | 49.0631 | 83.2626 | 0.49439 | 0.41657 | 122.3648 | 59.903 | -0.16022 | 0.49439 | 0.41657 | 59.903 | 83.2626 | 122.3648 | -121.9299 | -122.3236
5149.0938 | 122.2458 | -0.082397 | 122.0764 | 0.19112 | 0.0139 | -0.012123 | 0.096071 | 0.043278 | 0.0074084 | 0.15385 | 0.36163 | 0.39368 | 0.15106 | 0.20599 | 83.8669 | 59.9899 | 47.8912 | 48.8205 | 122.2504 | -0.2243 | 0.23346 | -121.6827 | 0.44403 | 0.28839 | -38.2095 | -0.14191 | 0.17395 | 0.21057 | 47.9736 | 48.9029 | 83.9493 | 0.47607 | 0.44403 | 122.3328 | 60.0723 | -0.14191 | 0.47607 | 0.44403 | 60.0723 | 83.9493 | 122.3328 | -121.9254 | -122.3007
5150.8594 | 122.2183 | -0.10529 | 122.1039 | -0.25139 | 0.015823 | -0.014687 | 0.092439 | 0.046055 | 0.0061268 | 0.15684 | 0.27924 | 0.42572 | 0.11444 | 0.1236 | 83.1528 | 59.7565 | 48.0789 | 48.6374 | 122.2916 | -0.27924 | 0.21973 | -121.6782 | 0.38452 | 0.22888 | -38.9511 | -0.17395 | 0.18768 | 0.16479 | 48.1842 | 48.7427 | 83.2581 | 0.53101 | 0.38452 | 122.3969 | 59.8618 | -0.17395 | 0.53101 | 0.38452 | 59.8618 | 83.2581 | 122.3969 | -121.9894 | -122.3831
5152.6406 | 122.2504 | -0.086975 | 122.0627 | 0.18349 | 0.015396 | -0.0093461 | 0.096284 | 0.045841 | 0.007622 | 0.15812 | 0.37537 | 0.39825 | 0.15564 | 0.23346 | 82.4203 | 59.6054 | 47.8638 | 48.7289 | 122.2595 | -0.22888 | 0.24261 | -121.6644 | 0.46234 | 0.32043 | -39.6423 | -0.14191 | 0.19684 | 0.21973 | 47.9507 | 48.8159 | 82.5073 | 0.48523 | 0.46234 | 122.3465 | 59.6924 | -0.14191 | 0.48523 | 0.46234 | 59.6924 | 82.5073 | 122.3465 | -121.907 | -122.2916
5154.4219 | 122.3053 | -0.07782 | 122.0581 | 0.00038159 | 0.016464 | -0.016396 | 0.091371 | 0.046269 | 0.0097582 | 0.1594 | 0.31586 | 0.40283 | 0.14191 | 0.16022 | 82.5027 | 59.6146 | 47.9141 | 48.6099 | 122.2549 | -0.25635 | 0.21973 | -121.6553 | 0.39368 | 0.23804 | -39.5554 | -0.17853 | 0.19684 | 0.17395 | 47.9919 | 48.6877 | 82.5806 | 0.48065 | 0.39368 | 122.3328 | 59.6924 | -0.17853 | 0.48065 | 0.39368 | 59.6924 | 82.5806 | 122.3328 | -121.9162 | -122.3145
5156.125 | 122.2641 | -0.073242 | 122.0673 | 0.15297 | 0.014114 | -0.015327 | 0.096711 | 0.045201 | 0.005913 | 0.15897 | 0.3479 | 0.40741 | 0.15564 | 0.21973 | 82.5439 | 59.6832 | 47.7493 | 48.4817 | 122.2321 | -0.24719 | 0.22888 | -121.6599 | 0.42114 | 0.29297 | -39.5233 | -0.17395 | 0.16479 | 0.19226 | 47.8226 | 48.555 | 82.6172 | 0.48065 | 0.42114 | 122.3053 | 59.7565 | -0.17395 | 0.48065 | 0.42114 | 59.7565 | 82.6172 | 122.3053 | -121.9116 | -122.3145
5157.8906 | 122.1588 | -0.12817 | 122.1085 | -0.098801 | 0.015182 | -0.0089189 | 0.10312 | 0.046055 | 0.005913 | 0.16154 | 0.33417 | 0.44861 | 0.12817 | 0.16937 | 80.5573 | 59.079 | 47.7814 | 48.3536 | 122.3053 | -0.24719 | 0.25635 | -121.6599 | 0.46234 | 0.29755 | -41.5512 | -0.11902 | 0.19684 | 0.20599 | 47.9095 | 48.4818 | 80.6854 | 0.57678 | 0.46234 | 122.4335 | 59.2072 | -0.11902 | 0.57678 | 0.46234 | 59.2072 | 80.6854 | 122.4335 | -121.9803 | -122.3557
5159.6562 | 122.2824 | -0.064087 | 122.0398 | 0.099564 | 0.015182 | -0.017677 | 0.099702 | 0.048832 | 0.0061268 | 0.16624 | 0.2655 | 0.42572 | 0.09613 | 0.13275 | 79.3854 | 58.6441 | 47.438 | 47.4747 | 122.3099 | -0.27008 | 0.16022 | -121.6141 | 0.32959 | 0.19684 | -42.6544 | -0.20599 | 0.27008 | 0.16937 | 47.5021 | 47.5388 | 79.4495 | 0.48981 | 0.32959 | 122.374 | 58.7082 | -0.20599 | 0.48981 | 0.32959 | 58.7082 | 79.4495 | 122.374 | -121.9437 | -122.3099
5161.4219 | 122.3053 | -0.054932 | 122.0398 | 0.01564 | 0.015182 | -0.013618 | 0.093934 | 0.044773 | 0.0069812 | 0.16303 | 0.31586 | 0.40283 | 0.16479 | 0.14191 | 82.3105 | 59.6466 | 47.5845 | 48.0194 | 122.2549 | -0.25177 | 0.21973 | -121.637 | 0.37079 | 0.19684 | -39.7293 | -0.19684 | 0.21515 | 0.15106 | 47.6395 | 48.0743 | 82.3654 | 0.45776 | 0.37079 | 122.3099 | 59.7015 | -0.19684 | 0.45776 | 0.37079 | 59.7015 | 82.3654 | 122.3099 | -121.875 | -122.2916
5163.125 | 122.2366 | -0.086975 | 122.0627 | 0.15297 | 0.015182 | -0.013618 | 0.10291 | 0.04755 | 0.009331 | 0.16389 | 0.37079 | 0.37994 | 0.15564 | 0.21973 | 80.5847 | 59.1888 | 47.2733 | 47.4014 | 122.2412 | -0.25177 | 0.24261 | -121.6827 | 0.45776 | 0.3067 | -41.478 | -0.16479 | 0.17853 | 0.21515 | 47.3602 | 47.4884 | 80.6717 | 0.46692 | 0.45776 | 122.3282 | 59.2758 | -0.16479 | 0.46692 | 0.45776 | 59.2758 | 80.6717 | 122.3282 | -121.907 | -122.3145
5164.8906 | 122.2595 | -0.064087 | 122.0535 | 0.12245 | 0.012619 | -0.012978 | 0.10141 | 0.047978 | 0.0071948 | 0.16859 | 0.3479 | 0.3891 | 0.16022 | 0.21515 | 78.4195 | 58.5983 | 47.1771 | 47.0947 | 122.2321 | -0.22888 | 0.2243 | -121.6644 | 0.41199 | 0.27924 | -43.634 | -0.16479 | 0.17853 | 0.18768 | 47.2412 | 47.1588 | 78.4836 | 0.45319 | 0.41199 | 122.2961 | 58.6624 | -0.16479 | 0.45319 | 0.41199 | 58.6624 | 78.4836 | 122.2961 | -121.8933 | -122.2824
5166.6562 | 122.3007 | -0.073242 | 122.0535 | 0.076676 | 0.016037 | -0.013405 | 0.10846 | 0.049473 | 0.009331 | 0.16816 | 0.26093 | 0.42572 | 0.1236 | 0.11902 | 77.7008 | 58.2596 | 47.3007 | 47.0901 | 122.287 | -0.28381 | 0.19684 | -121.6278 | 0.33417 | 0.19226 | -44.3527 | -0.21057 | 0.23346 | 0.13733 | 47.374 | 47.1634 | 77.774 | 0.49896 | 0.33417 | 122.3602 | 58.3328 | -0.21057 | 0.49896 | 0.33417 | 58.3328 | 77.774 | 122.3602 | -121.9299 | -122.3373
5168.4219 | 122.2961 | -0.07782 | 122.0444 | 0.030899 | 0.015396 | -0.01255 | 0.1012 | 0.044132 | 0.011254 | 0.17136 | 0.31128 | 0.40741 | 0.14648 | 0.17395 | 78.1311 | 58.5068 | 47.1085 | 46.669 | 122.2275 | -0.25177 | 0.2243 | -121.637 | 0.3891 | 0.25177 | -43.9133 | -0.17395 | 0.18311 | 0.16479 | 47.1863 | 46.7468 | 78.2089 | 0.48523 | 0.3891 | 122.3053 | 58.5846 | -0.17395 | 0.48523 | 0.3891 | 58.5846 | 78.2089 | 122.3053 | -121.8979 | -122.2961
5170.1406 | 122.1863 | -0.10986 | 122.0718 | -0.17509 | 0.013046 | -0.014473 | 0.10547 | 0.043492 | 0.0080494 | 0.17201 | 0.36163 | 0.4303 | 0.16937 | 0.21057 | 77.6276 | 58.3145 | 46.6141 | 45.0348 | 122.2412 | -0.27008 | 0.27924 | -121.6415 | 0.4715 | 0.32043 | -44.4443 | -0.16022 | 0.16937 | 0.19226 | 46.7239 | 45.1447 | 77.7374 | 0.54016 | 0.4715 | 122.3511 | 58.4244 | -0.16022 | 0.54016 | 0.4715 | 58.4244 | 77.7374 | 122.3511 | -121.9025 | -122.3419
5171.9219 | 122.2687 | -0.064087 | 122.0627 | 0.099564 | 0.015182 | -0.016823 | 0.10761 | 0.044132 | 0.011254 | 0.17371 | 0.40741 | 0.45776 | 0.19684 | 0.21057 | 76.7715 | 57.9941 | 46.0739 | 44.5724 | 122.2046 | -0.2655 | 0.26093 | -121.6049 | 0.4715 | 0.27466 | -45.2911 | -0.20142 | 0.14191 | 0.21057 | 46.138 | 44.6365 | 76.8356 | 0.52185 | 0.4715 | 122.2687 | 58.0582 | -0.20142 | 0.52185 | 0.4715 | 58.0582 | 76.8356 | 122.2687 | -121.8658 | -122.3282
5173.6875 | 122.2504 | -0.059509 | 122.0535 | 0.1606 | 0.013046 | -0.017036 | 0.11252 | 0.046482 | 0.011467 | 0.17414 | 0.3891 | 0.42114 | 0.19684 | 0.2243 | 75.618 | 57.6645 | 45.5978 | 42.1463 | 122.2275 | -0.21515 | 0.25635 | -121.6324 | 0.44861 | 0.28381 | -46.4355 | -0.15564 | 0.17395 | 0.19226 | 45.6573 | 42.2058 | 75.6775 | 0.48065 | 0.44861 | 122.287 | 57.724 | -0.15564 | 0.48065 | 0.44861 | 57.724 | 75.6775 | 122.287 | -121.8567 | -122.2687
5175.4531 | 122.1451 | -0.10529 | 122.081 | -0.098801 | 0.015396 | -0.015327 | 0.11615 | 0.046055 | 0.0095446 | 0.17756 | 0.3479 | 0.45319 | 0.17395 | 0.19684 | 75.1099 | 57.4539 | 46.1609 | 43.5059 | 122.2733 | -0.2655 | 0.27924 | -121.6278 | 0.45319 | 0.30212 | -46.9711 | -0.16022 | 0.19226 | 0.17395 | 46.2662 | 43.6111 | 75.2151 | 0.55847 | 0.45319 | 122.3785 | 57.5592 | -0.16022 | 0.55847 | 0.45319 | 57.5592 | 75.2151 | 122.3785 | -121.907 | -122.3465
5177.1562 | 122.2275 | -0.07782 | 122.0627 | 0.11482 | 0.013687 | -0.018318 | 0.11102 | 0.047123 | 0.012322 | 0.17884 | 0.37079 | 0.40741 | 0.17853 | 0.22888 | 75.0412 | 57.4905 | 45.8405 | 43.8034 | 122.2092 | -0.2243 | 0.25635 | -121.6553 | 0.44861 | 0.3067 | -47.0215 | -0.14648 | 0.14648 | 0.19226 | 45.9183 | 43.8812 | 75.119 | 0.48523 | 0.44861 | 122.287 | 57.5684 | -0.14648 | 0.48523 | 0.44861 | 57.5684 | 75.119 | 122.287 | -121.8842 | -122.287
5178.9219 | 122.1817 | -0.09613 | 122.0535 | -0.12932 | 0.014328 | -0.012978 | 0.12705 | 0.04456 | 0.047356 | 0.23631 | 0.23346 | 0.29755 | 0.045776 | 0.26093 | 9.1827 | 37.207 | 44.7235 | 41.4642 | 122.2366 | -0.2243 | 0.14191 | -121.756 | 0.32959 | 0.35706 | -112.8708 | -0.12817 | 0.1831 | 0.18768 | 44.8196 | 41.5604 | 9.2789 | 0.39368 | 0.32959 | 122.3328 | 37.3032 | -0.12817 | 0.39368 | 0.32959 | 37.3032 | 9.2789 | 122.3328 | -122.0078 | -122.2778
5180.7031 | 122.2458 | -0.064087 | 122.0581 | 0.11482 | 0.014328 | -0.011482 | 0.13239 | 0.047337 | 0.048638 | 0.23951 | 0.24719 | 0.28839 | 0.050354 | 0.22888 | 7.4844 | 36.7172 | 45.1904 | 41.922 | 122.2504 | -0.2243 | 0.11444 | -121.7697 | 0.31128 | 0.29297 | -114.5737 | -0.16022 | 0.19226 | 0.19684 | 45.2545 | 41.9861 | 7.5485 | 0.35248 | 0.31128 | 122.3145 | 36.7813 | -0.16022 | 0.35248 | 0.31128 | 36.7813 | 7.5485 | 122.3145 | -122.0078 | -122.2824
5182.4219 | 122.2961 | -0.064087 | 122.0261 | -0.014877 | 0.01625 | -0.014473 | 0.13175 | 0.044987 | 0.050347 | 0.24421 | 0.20142 | 0.29297 | 0.041199 | 0.18768 | 7.0358 | 36.644 | 45.4559 | 42.3019 | 122.2458 | -0.23346 | 0.10529 | -121.7331 | 0.2655 | 0.25177 | -114.9902 | -0.16937 | 0.21973 | 0.16022 | 45.52 | 42.366 | 7.0999 | 0.35706 | 0.2655 | 122.3099 | 36.7081 | -0.16937 | 0.35706 | 0.2655 | 36.7081 | 7.0999 | 122.3099 | -121.9849 | -122.2595
5184.1875 | 122.1725 | -0.09613 | 122.0627 | -0.17509 | 0.017318 | -0.013618 | 0.13815 | 0.047337 | 0.045647 | 0.2425 | 0.17853 | 0.33875 | 0.004578 | 0.17853 | 6.6742 | 36.557 | 45.8817 | 43.1671 | 122.2595 | -0.2655 | 0.10071 | -121.7239 | 0.27466 | 0.27466 | -115.3885 | -0.16937 | 0.19684 | 0.17395 | 45.9778 | 43.2632 | 6.7703 | 0.43488 | 0.27466 | 122.3557 | 36.6531 | -0.16937 | 0.43488 | 0.27466 | 36.6531 | 6.7703 | 122.3557 | -122.0581 | -122.3282
5185.9531 | 122.1451 | -0.13733 | 122.0444 | -0.18272 | 0.01326 | -0.012123 | 0.13452 | 0.046482 | 0.049279 | 0.24357 | 0.27466 | 0.27466 | 0.036621 | 0.27008 | 6.5369 | 36.6623 | 45.9 | 43.5608 | 122.2 | -0.22888 | 0.17395 | -121.7697 | 0.41199 | 0.40741 | -115.5075 | -0.091553 | 0.15564 | 0.23804 | 46.0373 | 43.6981 | 6.6742 | 0.41199 | 0.41199 | 122.3373 | 36.7996 | -0.091553 | 0.41199 | 0.41199 | 36.7996 | 6.6742 | 122.3373 | -122.0078 | -122.2733
5187.7188 | 122.1542 | -0.09613 | 122.0306 | -0.030136 | 0.014755 | -0.0149 | 0.14435 | 0.047337 | 0.047142 | 0.24549 | 0.18768 | 0.31586 | 0.022888 | 0.17853 | 6.1935 | 36.4883 | 46.0785 | 43.4143 | 122.2504 | -0.24719 | 0.11902 | -121.7148 | 0.28381 | 0.27466 | -115.8371 | -0.15106 | 0.21973 | 0.16479 | 46.1746 | 43.5104 | 6.2897 | 0.41199 | 0.28381 | 122.3465 | 36.5845 | -0.15106 | 0.41199 | 0.28381 | 36.5845 | 6.2897 | 122.3465 | -122.0078 | -122.2778
5189.4219 | 122.1222 | -0.13275 | 122.0535 | -0.19035 | 0.012405 | -0.015114 | 0.13645 | 0.04221 | 0.045861 | 0.24805 | 0.25177 | 0.30212 | 0.054932 | 0.26093 | 6.1844 | 36.5707 | 45.4239 | 41.7847 | 122.2183 | -0.21057 | 0.18768 | -121.7514 | 0.38452 | 0.39368 | -115.8691 | -0.07782 | 0.16479 | 0.19684 | 45.5566 | 41.9174 | 6.3171 | 0.43488 | 0.38452 | 122.3511 | 36.7035 | -0.07782 | 0.43488 | 0.38452 | 36.7035 | 6.3171 | 122.3511 | -121.9986 | -122.2641
5191.2031 | 122.2366 | -0.054932 | 122.0169 | 0.12245 | 0.015182 | -0.011909 | 0.13986 | 0.047337 | 0.051842 | 0.2504 | 0.24261 | 0.29755 | 0.045776 | 0.21057 | 6.0013 | 36.5524 | 45.3461 | 41.4459 | 122.2366 | -0.20599 | 0.10071 | -121.7194 | 0.29755 | 0.2655 | -116.0156 | -0.15106 | 0.21973 | 0.19684 | 45.401 | 41.5009 | 6.0562 | 0.35248 | 0.29755 | 122.2916 | 36.6074 | -0.15106 | 0.35248 | 0.29755 | 36.6074 | 6.0562 | 122.2916 | -121.9711 | -122.2229
5192.9688 | 122.1313 | -0.1236 | 122.0444 | -0.068283 | 0.015823 | -0.013618 | 0.1467 | 0.048191 | 0.047142 | 0.25147 | 0.21057 | 0.29297 | 0 | 0.21057 | 5.9097 | 36.4975 | 45.5292 | 41.5146 | 122.2412 | -0.24719 | 0.1236 | -121.7514 | 0.33417 | 0.33417 | -116.1346 | -0.1236 | 0.19684 | 0.21057 | 45.6528 | 41.6382 | 6.0333 | 0.41656 | 0.33417 | 122.3648 | 36.6211 | -0.1236 | 0.41656 | 0.33417 | 36.6211 | 6.0333 | 122.3648 | -122.0444 | -122.2916
5194.7344 | 122.2641 | -0.068665 | 122.0078 | 0.053787 | 0.014755 | -0.0149 | 0.1373 | 0.046696 | 0.049706 | 0.25233 | 0.19684 | 0.29297 | 0.041199 | 0.20142 | 5.8456 | 36.5387 | 45.2866 | 40.7959 | 122.2137 | -0.23346 | 0.10986 | -121.7148 | 0.2655 | 0.27008 | -116.1621 | -0.16479 | 0.20599 | 0.15564 | 45.3552 | 40.8646 | 5.9143 | 0.36163 | 0.2655 | 122.2824 | 36.6074 | -0.16479 | 0.36163 | 0.2655 | 36.6074 | 5.9143 | 122.2824 | -121.9666 | -122.2412
5196.4531 | 122.1405 | -0.10986 | 122.0535 | -0.19035 | 0.013046 | -0.015968 | 0.14328 | 0.045414 | 0.050774 | 0.25446 | 0.22888 | 0.27924 | 0.022888 | 0.27466 | 5.8777 | 36.5982 | 44.9524 | 39.8804 | 122.2275 | -0.22888 | 0.13275 | -121.7743 | 0.33875 | 0.38452 | -116.1758 | -0.11902 | 0.17395 | 0.20599 | 45.0623 | 39.9902 | 5.9875 | 0.3891 | 0.33875 | 122.3373 | 36.7081 | -0.11902 | 0.3891 | 0.33875 | 36.7081 | 5.9875 | 122.3373 | -122.0306 | -122.2824
5198.2188 | 122.1909 | -0.082397 | 122.0215 | 0.13771 | 0.012619 | -0.0149 | 0.14606 | 0.04691 | 0.048424 | 0.2581 | 0.23346 | 0.27466 | 0.018311 | 0.24261 | 5.7495 | 36.557 | 44.6732 | 38.9465 | 122.168 | -0.22888 | 0.10071 | -121.7468 | 0.31586 | 0.32501 | -116.272 | -0.14649 | 0.14648 | 0.21515 | 44.7556 | 39.0289 | 5.8319 | 0.35706 | 0.31586 | 122.2504 | 36.6394 | -0.14649 | 0.35706 | 0.31586 | 36.6394 | 5.8319 | 122.2504 | -122.0032 | -122.2504
5199.9844 | 122.2504 | -0.045776 | 122.0306 | 0.00038159 | 0.011978 | -0.011482 | 0.14478 | 0.044987 | 0.050347 | 0.25681 | 0.14648 | 0.27008 | 0.009155 | 0.20599 | 5.6534 | 36.4288 | 45.3369 | 40.1779 | 122.1909 | -0.23346 | 0.054931 | -121.7606 | 0.19226 | 0.25177 | -116.3773 | -0.18768 | 0.16022 | 0.13733 | 45.3827 | 40.2237 | 5.6992 | 0.31586 | 0.19226 | 122.2366 | 36.4746 | -0.18768 | 0.31586 | 0.19226 | 36.4746 | 5.6992 | 122.2366 | -122.0215 | -122.2641
5201.7031 | 122.2504 | -0.064087 | 121.9986 | -0.014877 | 0.014328 | -0.015114 | 0.1452 | 0.043705 | 0.049492 | 0.25852 | 0.16937 | 0.27924 | 0.009155 | 0.19684 | 5.6488 | 36.4014 | 44.5175 | 37.9349 | 122.1817 | -0.23346 | 0.073242 | -121.7194 | 0.23346 | 0.26093 | -116.3498 | -0.16937 | 0.18311 | 0.16022 | 44.5816 | 37.999 | 5.7129 | 0.34332 | 0.23346 | 122.2458 | 36.4655 | -0.16937 | 0.34332 | 0.23346 | 36.4655 | 5.7129 | 122.2458 | -121.9894 | -122.2321
5203.4688 | 122.1451 | -0.10529 | 122.0627 | -0.022507 | 0.015609 | -0.011269 | 0.15503 | 0.045841 | 0.045861 | 0.26002 | 0.16022 | 0.29297 | 0 | 0.17395 | 5.5115 | 36.2503 | 44.6686 | 37.6373 | 122.287 | -0.23804 | 0.10529 | -121.7697 | 0.2655 | 0.27924 | -116.5512 | -0.13275 | 0.2243 | 0.16022 | 44.7739 | 37.7426 | 5.6168 | 0.39825 | 0.2655 | 122.3923 | 36.3556 | -0.13275 | 0.39825 | 0.2655 | 36.3556 | 5.6168 | 122.3923 | -122.0627 | -122.3007
5205.1719 | 122.2183 | -0.068665 | 122.0215 | 0.053787 | 0.012832 | -0.012764 | 0.15546 | 0.04755 | 0.04821 | 0.26215 | 0.11444 | 0.29755 | -0.027466 | 0.11902 | 5.4474 | 36.1679 | 44.3893 | 36.3144 | 122.2321 | -0.24719 | 0.041199 | -121.7239 | 0.18311 | 0.18768 | -116.5741 | -0.17853 | 0.21057 | 0.14191 | 44.458 | 36.3831 | 5.5161 | 0.36621 | 0.18311 | 122.3007 | 36.2366 | -0.17853 | 0.36621 | 0.18311 | 36.2366 | 5.5161 | 122.3007 | -122.049 | -122.2687
5206.9375 | 122.2504 | -0.045776 | 121.9986 | 0.091934 | 0.014755 | -0.013618 | 0.15482 | 0.047764 | 0.049706 | 0.26365 | 0.091553 | 0.29755 | -0.009155 | 0.13733 | 5.4428 | 36.1679 | 44.4489 | 36.47 | 122.2458 | -0.25177 | 0.036621 | -121.7011 | 0.13733 | 0.18311 | -116.5558 | -0.20599 | 0.24719 | 0.10071 | 44.4946 | 36.5158 | 5.4886 | 0.34332 | 0.13733 | 122.2916 | 36.2137 | -0.20599 | 0.34332 | 0.13733 | 36.2137 | 5.4886 | 122.2916 | -122.0078 | -122.2504
5208.7031 | 122.2412 | -0.064087 | 122.0261 | 0.0080111 | 0.014328 | -0.011482 | 0.14862 | 0.046482 | 0.049706 | 0.26301 | 0.15106 | 0.27466 | 0.018311 | 0.18768 | 5.452 | 36.1862 | 44.9249 | 38.2004 | 122.1909 | -0.24719 | 0.082398 | -121.7514 | 0.21515 | 0.25177 | -116.5741 | -0.1831 | 0.16479 | 0.13275 | 44.989 | 38.2645 | 5.5161 | 0.33875 | 0.21515 | 122.2549 | 36.2503 | -0.1831 | 0.33875 | 0.21515 | 36.2503 | 5.5161 | 122.2549 | -122.0078 | -122.2733
5210.5781 | 122.2 | -0.073242 | 121.9711 | 0.16823 | 0.016891 | -0.011055 | 0.15973 | 0.048619 | 0.05056 | 0.26514 | 0.1831 | 0.27466 | -0.013733 | 0.21057 | 5.4153 | 36.1679 | 44.4901 | 36.4975 | 122.2046 | -0.22888 | 0.059509 | -121.6965 | 0.25635 | 0.28381 | -116.5558 | -0.15564 | 0.23346 | 0.19684 | 44.5633 | 36.5707 | 5.4886 | 0.3479 | 0.25635 | 122.2778 | 36.2411 | -0.15564 | 0.3479 | 0.25635 | 36.2411 | 5.4886 | 122.2778 | -121.9849 | -122.2
5212.375 | 122.0993 | -0.11902 | 122.0169 | -0.19798 | 0.012405 | -0.015755 | 0.15183 | 0.045201 | 0.051628 | 0.26258 | 0.21515 | 0.23804 | 0.018311 | 0.2655 | 5.4657 | 36.1862 | 45.0668 | 38.1729 | 122.1909 | -0.25177 | 0.13733 | -121.7789 | 0.33417 | 0.38452 | -116.5512 | -0.13275 | 0.17395 | 0.19684 | 45.1859 | 38.2919 | 5.5847 | 0.35706 | 0.33417 | 122.3099 | 36.3052 | -0.13275 | 0.35706 | 0.33417 | 36.3052 | 5.5847 | 122.3099 | -121.9986 | -122.2687
5214.0938 | 122.0947 | -0.11444 | 122.0306 | -0.17509 | 0.01326 | -0.012764 | 0.15375 | 0.04456 | 0.050774 | 0.26514 | 0.21973 | 0.24261 | 0.009155 | 0.26093 | 5.4794 | 36.113 | 45.0851 | 38.0447 | 122.1725 | -0.23804 | 0.1236 | -121.788 | 0.33417 | 0.37537 | -116.5512 | -0.1236 | 0.14191 | 0.21057 | 45.1996 | 38.1592 | 5.5939 | 0.35706 | 0.33417 | 122.287 | 36.2274 | -0.1236 | 0.35706 | 0.33417 | 36.2274 | 5.5939 | 122.287 | -122.0215 | -122.2687
5215.7969 | 122.1405 | -0.07782 | 122.0169 | -0.26665 | 0.015182 | -0.017036 | 0.15866 | 0.046696 | 0.049279 | 0.26386 | 0.10986 | 0.3067 | -0.022888 | 0.15564 | 5.3375 | 35.9436 | 46.0876 | 40.5899 | 122.2366 | -0.25635 | 0.054932 | -121.7102 | 0.18768 | 0.23346 | -116.6794 | -0.17853 | 0.21973 | 0.13275 | 46.1655 | 40.6677 | 5.4153 | 0.38452 | 0.18768 | 122.3145 | 36.0214 | -0.17853 | 0.38452 | 0.18768 | 36.0214 | 5.4153 | 122.3145 | -122.0398 | -122.2733
5217.5312 | 122.1863 | -0.059509 | 121.9711 | 0.12245 | 0.013046 | -0.0149 | 0.15674 | 0.04691 | 0.051842 | 0.26579 | 0.21515 | 0.27466 | 0.036621 | 0.2243 | 5.4565 | 36.058 | 47.1405 | 43.9499 | 122.1817 | -0.23804 | 0.09613 | -121.6965 | 0.27466 | 0.28381 | -116.5146 | -0.17853 | 0.21057 | 0.17853 | 47.2 | 44.0094 | 5.5161 | 0.33417 | 0.27466 | 122.2412 | 36.1176 | -0.17853 | 0.33417 | 0.27466 | 36.1176 | 5.5161 | 122.2412 | -121.9345 | -122.2092
5219.3594 | 122.2275 | -0.073242 | 121.9574 | 0.076676 | 0.014755 | -0.011909 | 0.16443 | 0.04691 | 0.049919 | 0.26792 | 0.11444 | 0.29297 | -0.009155 | 0.14648 | 5.3787 | 35.9207 | 46.7697 | 41.7068 | 122.2092 | -0.25177 | 0.064087 | -121.6644 | 0.18768 | 0.21973 | -116.5787 | -0.17853 | 0.25177 | 0.1236 | 46.843 | 41.7801 | 5.452 | 0.36621 | 0.18768 | 122.2824 | 35.994 | -0.17853 | 0.36621 | 0.18768 | 35.994 | 5.452 | 122.2824 | -121.9666 | -122.2092
5221.1094 | 122.1451 | -0.064087 | 121.994 | -0.014877 | 0.014328 | -0.01255 | 0.15695 | 0.045414 | 0.050133 | 0.27006 | 0.21057 | 0.27466 | 0.009155 | 0.27008 | 5.452 | 36.0397 | 47.2412 | 43.9316 | 122.1451 | -0.23346 | 0.073242 | -121.7194 | 0.27466 | 0.33417 | -116.5421 | -0.16937 | 0.15106 | 0.20142 | 47.3053 | 43.9957 | 5.5161 | 0.33875 | 0.27466 | 122.2092 | 36.1038 | -0.16937 | 0.33875 | 0.27466 | 36.1038 | 5.5161 | 122.2092 | -121.9849 | -122.2275
5222.875 | 122.0947 | -0.10529 | 122.0123 | -0.17509 | 0.014755 | -0.013405 | 0.16593 | 0.047123 | 0.046715 | 0.27198 | 0.13275 | 0.31586 | -0.004578 | 0.19226 | 5.3879 | 35.939 | 47.6486 | 43.9819 | 122.2046 | -0.25177 | 0.10071 | -121.6965 | 0.23804 | 0.29755 | -116.6245 | -0.14648 | 0.19226 | 0.13733 | 47.7539 | 44.0872 | 5.4932 | 0.42114 | 0.23804 | 122.3099 | 36.0443 | -0.14648 | 0.42114 | 0.23804 | 36.0443 | 5.4932 | 122.3099 | -122.0169 | -122.2641
5224.7031 | 122.1634 | -0.091553 | 121.9574 | 0.17586 | 0.014969 | -0.017036 | 0.16528 | 0.046269 | 0.050133 | 0.27241 | 0.25177 | 0.25177 | 0.018311 | 0.24719 | 5.484 | 36.026 | 47.8271 | 44.6365 | 122.1405 | -0.21973 | 0.10986 | -121.7056 | 0.34332 | 0.33874 | -116.4734 | -0.12817 | 0.18311 | 0.23346 | 47.9187 | 44.7281 | 5.5756 | 0.34332 | 0.34332 | 122.2321 | 36.1176 | -0.12817 | 0.34332 | 0.34332 | 36.1176 | 5.5756 | 122.2321 | -121.9391 | -122.1771
5226.5 | 122.0764 | -0.11444 | 121.9711 | -0.17509 | 0.012191 | -0.014046 | 0.16464 | 0.044773 | 0.048638 | 0.27134 | 0.2243 | 0.27008 | 0.032043 | 0.25635 | 5.484 | 36.0901 | 48.5825 | 46.2341 | 122.1222 | -0.24261 | 0.14648 | -121.701 | 0.33875 | 0.37079 | -116.4871 | -0.12817 | 0.15106 | 0.19226 | 48.6969 | 46.3486 | 5.5985 | 0.38452 | 0.33875 | 122.2366 | 36.2045 | -0.12817 | 0.38452 | 0.33875 | 36.2045 | 5.5985 | 122.2366 | -121.9391 | -122.2137
5228.2969 | 121.0098 | -0.064087 | 120.7901 | 0.16823 | 0.017532 | -0.012764 | 0.057405 | 0.0011941 | 0.0052722 | 0.042763 | 0.74158 | 0.73242 | 0.50812 | 85.112 | 89.6988 | 83.9218 | 80.6671 | 82.3425 | 121.0052 | -0.27466 | 0.5722 | -120.0577 | 0.80566 | 85.1761 | -31.0913 | -0.21057 | 0.21515 | 0.23346 | 80.7312 | 82.4066 | 89.7629 | 0.79651 | 0.80566 | 121.0693 | 83.9859 | -0.21057 | 0.79651 | 0.80566 | 83.9859 | 89.7629 | 121.0693 | -120.282 | -121.0648
5230.0156 | 121.8475 | -0.073242 | 121.6461 | 0.19112 | 0.014541 | -0.012764 | 0.13281 | 0.039433 | 0.049065 | 0.23844 | 0.13275 | 0.21057 | -0.082397 | 10.8902 | 7.6355 | 22.7234 | 22.3938 | 11.1832 | 121.8201 | -0.21973 | -0.009155 | -121.4355 | 0.20599 | 10.9634 | -114.0106 | -0.14649 | 0.17395 | 0.21515 | 22.467 | 11.2564 | 7.7087 | 0.28381 | 0.20599 | 121.8933 | 22.7966 | -0.14649 | 0.28381 | 0.20599 | 22.7966 | 7.7087 | 121.8933 | -121.7285 | -121.8658
5231.8125 | 121.9482 | -0.07782 | 121.7194 | 0.15297 | 0.016678 | -0.011482 | 0.22125 | -0.011196 | -0.0060498 | 0.16688 | 0.81482 | 0.95215 | 0.66834 | 109.7031 | 109.4925 | 102.2141 | 101.5549 | 109.7168 | 121.9528 | -0.26093 | 0.74616 | -120.7672 | 0.89264 | 109.7809 | -12.2269 | -0.18311 | 0.23346 | 0.14648 | 101.6327 | 109.7946 | 109.5703 | 1.03 | 0.89264 | 122.0306 | 102.2919 | -0.18311 | 1.03 | 0.89264 | 102.2919 | 109.5703 | 122.0306 | -121.051 | -121.9803
5233.6094 | 121.9254 | -0.11444 | 121.6095 | -0.075912 | 0.01625 | -0.016182 | 0.18707 | 0.031742 | 0.037743 | 0.041054 | 0.55847 | 0.92926 | 0.68665 | 32.7255 | 23.8815 | 31.6498 | 30.9998 | 21.8765 | 121.8063 | -0.21057 | 0.80109 | -120.6802 | 0.67291 | 32.84 | -97.728 | -0.09613 | 0.19684 | -0.12817 | 31.1142 | 21.991 | 23.996 | 1.0437 | 0.67291 | 121.9208 | 31.7642 | -0.09613 | 1.0437 | 0.67291 | 31.7642 | 23.996 | 121.9208 | -120.9229 | -121.8201
5235.375 | 121.8475 | -0.13275 | 121.6599 | -0.26665 | 0.016037 | -0.015327 | 0.21036 | 0.027256 | 0.037102 | 0.033791 | 0.33875 | 0.50812 | 0.20142 | 32.8445 | 32.9041 | 41.4825 | 34.0897 | 33.4351 | 121.8933 | -0.32044 | 0.33417 | -121.1517 | 0.4715 | 32.9773 | -88.7558 | -0.18768 | 0.23346 | 0.13733 | 34.2224 | 33.5678 | 33.0368 | 0.64087 | 0.4715 | 122.0261 | 41.6153 | -0.18768 | 0.64087 | 0.4715 | 41.6153 | 33.0368 | 122.0261 | -121.4584 | -121.9803
5237.125 | 121.8246 | -0.10986 | 121.7194 | -0.22087 | 0.014755 | -0.013405 | 0.1326 | -0.02145 | -0.013099 | 0.057717 | 1.0254 | 1.0803 | 0.84686 | 121.5729 | 121.376 | 111.8088 | 121.1517 | 121.5088 | 121.8933 | -0.2655 | 0.95673 | -120.639 | 1.1353 | 121.6827 | -0.34332 | -0.15564 | 0.17395 | 0.17853 | 121.2616 | 121.6187 | 121.4859 | 1.1902 | 1.1353 | 122.0032 | 111.9186 | -0.15564 | 1.1902 | 1.1353 | 111.9186 | 121.4859 | 122.0032 | -120.8725 | -121.9849
5238.9688 | 121.962 | -0.086975 | 121.6965 | 0.17586 | 0.014114 | -0.01725 | 0.15225 | -0.019741 | -0.012672 | 0.063912 | 1.0437 | 1.181 | 0.88348 | 121.5134 | 121.2433 | 111.7493 | 121.1472 | 121.3165 | 121.9254 | -0.27008 | 0.97046 | -120.5154 | 1.1307 | 121.6003 | -0.45319 | -0.18311 | 0.22888 | 0.16022 | 121.2341 | 121.4035 | 121.3303 | 1.268 | 1.1307 | 122.0123 | 111.8362 | -0.18311 | 1.268 | 1.1307 | 111.8362 | 121.3303 | 122.0123 | -120.813 | -121.9666
5240.7031 | 121.8201 | -0.31586 | 121.5317 | -0.25902 | 0.011978 | -0.012978 | 1.183 | -0.020809 | -0.012672 | 0.071816 | 1.4694 | 1.5701 | 1.3 | 119.1925 | 119.5541 | 110.1608 | 119.0277 | 119.1376 | 121.6553 | -0.47607 | 1.6159 | -119.9615 | 1.7853 | 119.5084 | -1.9775 | -0.16022 | 0.1236 | 0.16937 | 119.3436 | 119.4534 | 119.87 | 1.886 | 1.7853 | 121.9711 | 110.4767 | -0.16022 | 1.886 | 1.7853 | 110.4767 | 119.87 | 121.9711 | -120.2316 | -122.0078
5242.4219 | 117.0181 | -0.1236 | 116.7114 | 0.084305 | 0.014114 | -0.014473 | 6.9574 | -0.0054281 | 0.003136 | 7.0205 | 0.72784 | 0.84686 | 0.55389 | 69.9921 | 71.0403 | 66.4719 | 70.9213 | 71.0632 | 104.8233 | 8.6517 | 0.67749 | -115.8646 | 0.85144 | 70.1157 | -45.6711 | 8.7753 | -11.8881 | 0.17395 | 71.0449 | 71.1868 | 71.1639 | 0.97046 | 0.85144 | 104.9469 | 66.5955 | 8.7753 | 0.97046 | 0.85144 | 66.5955 | 71.1639 | 104.9469 | -116.1575 | -108.0597
5244.1719 | 121.5591 | -0.07782 | 121.3577 | 0.13008 | 0.014755 | -0.017036 | 0.17191 | 0.045628 | 0.047783 | 0.24421 | 0.13733 | 0.17853 | -0.064087 | 8.0658 | 7.7545 | 8.3725 | 10.144 | 7.8186 | 121.5775 | -0.22888 | 0.013733 | -121.1792 | 0.21515 | 8.1436 | -113.6032 | -0.15106 | 0.21973 | 0.20142 | 10.2219 | 7.8964 | 7.8323 | 0.25635 | 0.21515 | 121.6553 | 8.4503 | -0.15106 | 0.25635 | 0.21515 | 8.4503 | 7.8323 | 121.6553 | -121.4218 | -121.5866
5245.9062 | 121.6873 | -0.068665 | 121.463 | -0.0072479 | 0.015823 | -0.011482 | 0.15994 | 0.044346 | 0.053124 | 0.24784 | 0.045776 | 0.14648 | -0.09613 | 4.3304 | 4.2114 | 4.4815 | 4.0237 | 3.7537 | 121.6278 | -0.25635 | -0.027465 | -121.3165 | 0.11444 | 4.3991 | -117.2516 | -0.18768 | 0.16479 | 0.14191 | 4.0924 | 3.8223 | 4.2801 | 0.21515 | 0.11444 | 121.6965 | 4.5502 | -0.18768 | 0.21515 | 0.11444 | 4.5502 | 4.2801 | 121.6965 | -121.5591 | -121.7194
5247.625 | 121.6141 | -0.10986 | 121.5637 | -0.26665 | 0.013473 | -0.016182 | 0.12854 | 0.043064 | 0.052697 | 0.23417 | 0.045776 | 0.13733 | -0.13275 | 2.33 | 2.2659 | 2.3804 | 2.1927 | 1.9592 | 121.7285 | -0.24261 | -0.022888 | -121.4264 | 0.15564 | 2.4399 | -119.2978 | -0.13275 | 0.16479 | 0.17853 | 2.3026 | 2.0691 | 2.3758 | 0.24719 | 0.15564 | 121.8384 | 2.4902 | -0.13275 | 0.24719 | 0.15564 | 2.4902 | 2.3758 | 121.8384 | -121.6965 | -121.8063
5249.3594 | 121.7239 | -0.064087 | 121.5271 | 0.069046 | 0.014755 | -0.014259 | 0.15076 | 0.047978 | 0.050988 | 0.25275 | -0.004578 | 0.16022 | -0.16937 | 2.4811 | 2.417 | 2.5818 | 2.3575 | 1.918 | 121.7606 | -0.25635 | -0.10529 | -121.3669 | 0.059509 | 2.5452 | -119.1101 | -0.19226 | 0.23346 | 0.16479 | 2.4216 | 1.9821 | 2.4811 | 0.2243 | 0.059509 | 121.8246 | 2.6459 | -0.19226 | 0.2243 | 0.059509 | 2.6459 | 2.4811 | 121.8246 | -121.6965 | -121.7834
5251.1562 | 121.7239 | -0.059509 | 121.6141 | 0.10719 | 0.013473 | -0.016609 | 0.12833 | 0.047123 | 0.053337 | 0.23609 | 0.073242 | 0.10529 | -0.11444 | 1.7441 | 1.6891 | 1.8311 | 1.4145 | 1.4282 | 121.7697 | -0.20599 | -0.054932 | -121.5088 | 0.13275 | 1.8036 | -119.9249 | -0.14649 | 0.15564 | 0.18768 | 1.474 | 1.4877 | 1.7487 | 0.16479 | 0.13275 | 121.8292 | 1.8906 | -0.14649 | 0.16479 | 0.13275 | 1.8906 | 1.7487 | 121.8292 | -121.7285 | -121.8201
5252.8594 | 121.7651 | -0.054932 | 121.637 | -0.15221 | 0.012832 | -0.018318 | 0.23877 | 0.047978 | 0.05291 | 0.27305 | -0.027466 | 0.15106 | -0.17395 | 2.1606 | 2.1011 | 2.5497 | 2.3254 | 1.6342 | 121.8475 | -0.26093 | -0.11902 | -121.4859 | 0.027466 | 2.2156 | -119.5358 | -0.20599 | 0.21057 | 0.14648 | 2.3804 | 1.6891 | 2.1561 | 0.20599 | 0.027466 | 121.9025 | 2.6047 | -0.20599 | 0.20599 | 0.027466 | 2.6047 | 2.1561 | 121.9025 | -121.8109 | -121.8979
5254.5625 | 121.7743 | -0.064087 | 121.6187 | 0.27504 | 0.014114 | -0.012764 | 0.29709 | 0.049259 | 0.051842 | 0.28352 | 0.068665 | 0.15564 | -0.11444 | 2.98 | 2.9343 | 3.067 | 2.5452 | 2.1744 | 121.7926 | -0.19684 | -0.050354 | -121.463 | 0.13275 | 3.0441 | -118.6844 | -0.13275 | 0.17395 | 0.18311 | 2.6093 | 2.2385 | 2.9984 | 0.21973 | 0.13275 | 121.8567 | 3.1311 | -0.13275 | 0.21973 | 0.13275 | 3.1311 | 2.9984 | 121.8567 | -121.7331 | -121.8155
5256.3281 | 121.7606 | -0.068665 | 121.5729 | 0.19112 | 0.017532 | -0.011055 | 0.13922 | 0.047123 | 0.051201 | 0.24613 | 0.004578 | 0.13733 | -0.15106 | 1.9958 | 1.9409 | 2.037 | 1.7899 | 1.5472 | 121.8155 | -0.20599 | -0.082397 | -121.4355 | 0.073243 | 2.0645 | -119.632 | -0.13733 | 0.24262 | 0.15564 | 1.8585 | 1.6159 | 2.0096 | 0.20599 | 0.073243 | 121.8842 | 2.1057 | -0.13733 | 0.20599 | 0.073243 | 2.1057 | 2.0096 | 121.8842 | -121.7239 | -121.7789
5258.1094 | 121.7789 | -0.10986 | 121.6461 | -0.20561 | 0.0139 | -0.015327 | 0.18643 | -0.011837 | -0.0051954 | 0.065621 | 0.92926 | 1.0757 | 0.75531 | 104.3106 | 103.8345 | 104.1687 | 104.1367 | 101.8433 | 121.843 | -0.29755 | 0.86517 | -120.5704 | 1.0391 | 104.4205 | -17.8116 | -0.18768 | 0.19684 | 0.17395 | 104.2465 | 101.9531 | 103.9444 | 1.1856 | 1.0391 | 121.9528 | 104.2786 | -0.18768 | 1.1856 | 1.0391 | 104.2786 | 103.9444 | 121.9528 | -120.8908 | -121.9437
5259.875 | 121.8018 | -0.09613 | 121.6461 | -0.22087 | 0.016464 | -0.014687 | 0.11038 | 0.011021 | 0.018517 | 0.063484 | 0.6134 | 0.71869 | 0.3891 | 64.151 | 64.2334 | 64.3753 | 64.3982 | 64.1785 | 121.9025 | -0.30212 | 0.48523 | -120.9274 | 0.70953 | 64.2471 | -57.4127 | -0.20599 | 0.25635 | 0.2243 | 64.4943 | 64.2746 | 64.3295 | 0.81482 | 0.70953 | 121.9986 | 64.4714 | -0.20599 | 0.81482 | 0.70953 | 64.4714 | 64.3295 | 121.9986 | -121.257 | -121.9482
5261.6562 | 121.756 | -0.11902 | 121.6278 | -0.15984 | 0.011551 | -0.011696 | 0.2565 | -0.020168 | -0.013527 | 0.080361 | 1.5427 | 1.5884 | 1.3458 | 121.2891 | 121.0236 | 121.1243 | 120.8359 | 120.8176 | 121.8475 | 1.0437 | 1.4648 | -120.0394 | 1.6617 | 121.4081 | -0.60425 | 1.1627 | 0.21973 | 0.19684 | 120.9549 | 120.9366 | 121.1426 | 1.7075 | 1.6617 | 121.9666 | 121.2433 | 1.1627 | 1.7075 | 1.6617 | 121.2433 | 121.1426 | 121.9666 | -120.282 | -120.5841
5263.4062 | 121.7056 | -0.12817 | 121.6324 | -0.10643 | 0.018814 | -0.013191 | 0.24667 | -0.016323 | -0.015876 | 0.075234 | 1.2405 | 1.3275 | 1.0254 | 121.3669 | 121.0693 | 121.1151 | 121.0922 | 121.0556 | 121.8567 | -0.25177 | 1.1536 | -120.3049 | 1.3687 | 121.4951 | -0.56305 | -0.1236 | 0.2243 | 0.21515 | 121.2204 | 121.1838 | 121.1975 | 1.4557 | 1.3687 | 121.9849 | 121.2433 | -0.1236 | 1.4557 | 1.3687 | 121.2433 | 121.1975 | 121.9849 | -120.607 | -121.8842
5265.1719 | 121.7285 | -0.56763 | 121.0464 | -0.13695 | 0.0139 | -0.011909 | 3.0289 | -0.019314 | -0.0094678 | 0.07267 | 3.8177 | 3.8818 | 3.6209 | 117.8467 | 117.5537 | 118.1213 | 117.3889 | 117.0959 | 121.0098 | -0.67749 | 4.1885 | -117.1646 | 4.3854 | 118.4143 | -3.4927 | -0.10986 | -0.036621 | 0.19684 | 117.9565 | 117.6636 | 118.1213 | 4.4495 | 4.3854 | 121.5775 | 118.689 | -0.10986 | 4.4495 | 4.3854 | 118.689 | 118.1213 | 121.5775 | -117.4255 | -121.7239
5266.9219 | 121.7331 | -0.18768 | 121.5042 | -0.18272 | 0.018387 | -0.011482 | 0.8226 | -0.019527 | -0.013313 | 0.093392 | 1.8997 | 2.0142 | 1.712 | 119.8471 | 119.5084 | 119.989 | 119.5724 | 117.9474 | 121.7056 | -0.36621 | 1.8997 | -119.4901 | 2.0874 | 120.0348 | -1.9958 | -0.17853 | 0.20142 | 0.18768 | 119.7601 | 118.1351 | 119.696 | 2.2018 | 2.0874 | 121.8933 | 120.1767 | -0.17853 | 2.2018 | 2.0874 | 120.1767 | 119.696 | 121.8933 | -119.7922 | -121.8704
5268.625 | 121.3028 | -0.10529 | 121.2067 | -0.17509 | 0.014969 | -0.015327 | 0.11188 | 0.045628 | 0.048424 | 0.094673 | 0.16479 | 0.32501 | 0.004578 | 8.8715 | 8.8303 | 9.1965 | 8.8943 | 9.0317 | 121.3852 | -0.27466 | 0.10986 | -120.8817 | 0.27008 | 8.9767 | -112.3764 | -0.16937 | 0.17853 | 0.16022 | 8.9996 | 9.137 | 8.9355 | 0.4303 | 0.27008 | 121.4905 | 9.3018 | -0.16937 | 0.4303 | 0.27008 | 9.3018 | 8.9355 | 121.4905 | -121.2021 | -121.4813
5270.375 | 121.4859 | -0.068665 | 121.2936 | 0.18349 | 0.014755 | -0.016182 | 0.11957 | 0.04691 | 0.052697 | 0.19508 | 0.064087 | 0.18768 | -0.082397 | 4.1977 | 4.2114 | 4.3808 | 4.0512 | 4.4128 | 121.4905 | -0.2243 | -0.013732 | -121.106 | 0.13275 | 4.2664 | -117.0822 | -0.15564 | 0.19684 | 0.14648 | 4.1199 | 4.4815 | 4.2801 | 0.25635 | 0.13275 | 121.5591 | 4.4495 | -0.15564 | 0.25635 | 0.13275 | 4.4495 | 4.2801 | 121.5591 | -121.376 | -121.5179
5272.1562 | 121.582 | -0.054932 | 121.3669 | 0.091934 | 0.014755 | -0.015327 | 0.15546 | 0.04691 | 0.049706 | 0.21067 | -0.004578 | 0.19226 | -0.11902 | 4.5502 | 4.4952 | 4.6417 | 4.3945 | 4.4907 | 121.5866 | -0.25177 | -0.064087 | -121.1746 | 0.050354 | 4.6051 | -116.8716 | -0.19684 | 0.21973 | 0.11444 | 4.4495 | 4.5456 | 4.5502 | 0.24719 | 0.050354 | 121.6415 | 4.6967 | -0.19684 | 0.24719 | 0.050354 | 4.6967 | 4.5502 | 121.6415 | -121.4859 | -121.6187
5273.8594 | 121.5317 | -0.082397 | 121.4584 | -0.24376 | 0.016037 | -0.018959 | 0.13666 | 0.045201 | 0.050133 | 0.22413 | -0.009155 | 0.17395 | -0.13275 | 3.1906 | 3.1952 | 3.479 | 3.3142 | 3.2043 | 121.6599 | -0.26093 | -0.050354 | -121.2845 | 0.073242 | 3.273 | -118.2632 | -0.17853 | 0.20142 | 0.1236 | 3.3966 | 3.2867 | 3.2776 | 0.25635 | 0.073242 | 121.7422 | 3.5614 | -0.17853 | 0.25635 | 0.073242 | 3.5614 | 3.2776 | 121.7422 | -121.5912 | -121.7194
5275.625 | 120.9915 | -0.068665 | 120.7993 | 0.1606 | 0.015609 | -0.010628 | 0.12512 | 0.042851 | -0.012031 | 0.042122 | 1.149 | 1.1581 | 0.91553 | 12.941 | 120.6482 | 13.1104 | 12.6572 | 13.147 | 120.9869 | -0.24719 | 0.98419 | -119.6411 | 1.2177 | 13.0096 | -0.15106 | -0.17853 | 0.18768 | 0.23346 | 12.7258 | 13.2156 | 120.7169 | 1.2268 | 1.2177 | 121.0556 | 13.179 | -0.17853 | 1.2268 | 1.2177 | 13.179 | 120.7169 | 121.0556 | -119.8837 | -121.0464
5277.3906 | 121.1334 | -0.15564 | 120.9229 | -0.068283 | 0.0139 | -0.013405 | 0.46265 | 0.02042 | -0.01374 | 0.050026 | 3.8361 | 3.9185 | 3.6209 | 51.8646 | 120.607 | 51.6586 | 51.3565 | 53.5767 | 121.138 | -0.32501 | 3.7766 | -117.0044 | 3.9917 | 52.0203 | -0.31586 | -0.16937 | 0.21515 | 0.21515 | 51.5121 | 53.7323 | 120.7626 | 4.0741 | 3.9917 | 121.2936 | 51.8143 | -0.16937 | 4.0741 | 3.9917 | 51.8143 | 120.7626 | 121.2936 | -117.3019 | -121.2479
5279.0938 | 121.1975 | -0.2655 | 120.8359 | 0.038529 | 0.015182 | -0.011696 | 1.23 | -0.015896 | -0.012031 | 0.058785 | 3.2181 | 3.3463 | 3.0853 | 118.9499 | 120.2316 | 120.1996 | 118.8446 | 118.6569 | 120.9457 | -0.45776 | 3.3508 | -117.4896 | 3.4836 | 119.2154 | -0.60425 | -0.19226 | 0.10986 | 0.13275 | 119.1101 | 118.9224 | 120.4971 | 3.6118 | 3.4836 | 121.2112 | 120.4651 | -0.19226 | 3.6118 | 3.4836 | 120.4651 | 120.4971 | 121.2112 | -117.7505 | -121.2936
5280.7812 | 121.2387 | -0.36163 | 120.7535 | 0.12245 | 0.01326 | -0.010628 | 1.622 | -0.019527 | -0.011818 | 0.058998 | 3.6667 | 3.7308 | 3.4973 | 119.014 | 120.2408 | 120.2454 | 118.5013 | 118.5928 | 120.8221 | -0.48981 | 3.8589 | -117.0227 | 4.0283 | 119.3756 | -0.51269 | -0.12817 | 0.068665 | 0.16937 | 118.8629 | 118.9545 | 120.6024 | 4.0924 | 4.0283 | 121.1838 | 120.607 | -0.12817 | 4.0924 | 4.0283 | 120.607 | 120.6024 | 121.1838 | -117.2562 | -121.2433
5282.5469 | 121.1792 | -0.37537 | 120.7901 | -0.19798 | 0.012619 | -0.015968 | 1.7719 | -0.022732 | -0.015876 | 0.056221 | 3.2593 | 3.4241 | 3.1082 | 119.2474 | 120.108 | 120.0485 | 119.0918 | 118.959 | 120.8817 | -0.58594 | 3.4836 | -117.366 | 3.6346 | 119.6228 | -0.68207 | -0.21057 | 0.091553 | 0.15106 | 119.4672 | 119.3344 | 120.4834 | 3.7994 | 3.6346 | 121.257 | 120.4239 | -0.21057 | 3.7994 | 3.6346 | 120.4239 | 120.4834 | 121.257 | -117.6819 | -121.376
5284.3125 | 117.7002 | -0.17853 | 117.4805 | -0.14458 | 0.014114 | -0.011909 | 6.9574 | -0.010555 | -0.015449 | 7.0205 | 4.454 | 4.4861 | 4.0466 | 105.304 | 105.5878 | 105.7938 | 106.073 | 42.5766 | 115.3976 | 3.2455 | 4.2252 | -112.9944 | 4.6326 | 105.4825 | -11.8927 | 3.4241 | -2.0828 | 0.40741 | 106.2515 | 42.7551 | 105.7663 | 4.6646 | 4.6326 | 115.5762 | 105.9723 | 3.4241 | 4.6646 | 4.6326 | 105.9723 | 105.7663 | 115.5762 | -113.4338 | -114.2349
5286.0781 | 120.9686 | -0.10529 | 120.7718 | 0.16823 | 0.012619 | -0.010841 | 0.35242 | -0.018886 | -0.013954 | 0.048104 | 3.5889 | 3.6713 | 3.4103 | 120.7764 | 120.5063 | 120.6299 | 120.4605 | 3.7216 | 120.9915 | -0.19684 | 3.5156 | -117.1005 | 3.6942 | 120.8817 | -0.2655 | -0.091552 | 0.21973 | 0.17853 | 120.5658 | 3.8269 | 120.6116 | 3.7766 | 3.6942 | 121.0968 | 120.7352 | -0.091552 | 3.7766 | 3.6942 | 120.7352 | 120.6116 | 121.0968 | -117.3615 | -120.9686
5287.7812 | 121.2158 | -0.31128 | 120.5795 | 0.13008 | 0.0139 | -0.016396 | 1.7141 | -0.01675 | -0.012672 | 0.044472 | 5.5801 | 5.6076 | 5.3329 | 120.2133 | 120.0851 | 120.0485 | 119.9661 | 2.9526 | 120.7077 | -0.4715 | 5.6442 | -114.9719 | 5.8914 | 120.5246 | -0.49438 | -0.16022 | 0.12817 | 0.24719 | 120.2774 | 3.2639 | 120.3964 | 5.9189 | 5.8914 | 121.019 | 120.3598 | -0.16022 | 5.9189 | 5.8914 | 120.3598 | 120.3964 | 121.019 | -115.2466 | -121.051
5289.5312 | 121.1746 | -0.20599 | 120.7489 | 0.11482 | 0.015182 | -0.015755 | 0.96723 | -0.018245 | -0.011604 | 0.048317 | 4.0787 | 4.2206 | 3.8864 | 120.5338 | 120.2545 | 120.2408 | 120.3003 | 3.1631 | 120.9045 | -0.43488 | 4.0924 | -116.5283 | 4.2847 | 120.7397 | -0.49438 | -0.22888 | 0.15564 | 0.19226 | 120.5063 | 3.3691 | 120.4605 | 4.4266 | 4.2847 | 121.1105 | 120.4468 | -0.22888 | 4.4266 | 4.2847 | 120.4468 | 120.4605 | 121.1105 | -116.8625 | -121.1838
5291.2812 | 121.1014 | -0.21057 | 120.8359 | -0.11406 | 0.014328 | -0.014473 | 0.76685 | -0.021023 | -0.013313 | 0.047035 | 7.6584 | 7.901 | 7.3334 | 120.8267 | 120.5612 | 120.5429 | 120.3506 | 3.9368 | 120.9503 | -0.35706 | 7.5439 | -112.9349 | 7.869 | 121.0373 | -0.27466 | -0.14648 | 0.11444 | 0.32501 | 120.5612 | 4.1473 | 120.7718 | 8.1116 | 7.869 | 121.1609 | 120.7535 | -0.14648 | 8.1116 | 7.869 | 120.7535 | 120.7718 | 121.1609 | -113.5025 | -121.1929
5292.9844 | 121.1517 | -0.20142 | 120.9 | -0.14458 | 0.014755 | -0.015327 | 0.77924 | -0.020809 | -0.01075 | 0.047249 | 7.4799 | 7.3883 | 6.8527 | 120.8359 | 120.5978 | 120.5978 | 120.3918 | 2.8839 | 121.0327 | -0.36163 | 7.0541 | -113.5117 | 7.6813 | 121.0373 | -0.30212 | -0.16022 | 0.13275 | 0.62714 | 120.5933 | 3.0853 | 120.7993 | 7.5897 | 7.6813 | 121.2341 | 120.7993 | -0.16022 | 7.5897 | 7.6813 | 120.7993 | 120.7993 | 121.2341 | -114.0472 | -121.2616
5294.7344 | 121.2387 | -0.1831 | 120.8771 | 0.13771 | 0.014541 | -0.0097733 | 0.8429 | -0.021663 | -0.012886 | 0.043831 | 7.5668 | 7.6172 | 7.251 | 120.7718 | 120.5429 | 120.6207 | 120.5063 | 7.608 | 121.0419 | -0.36163 | 7.4341 | -113.2599 | 7.7499 | 120.9549 | -0.33417 | -0.17853 | 0.16479 | 0.31586 | 120.6894 | 7.7911 | 120.726 | 7.8003 | 7.7499 | 121.225 | 120.8038 | -0.17853 | 7.8003 | 7.7499 | 120.8038 | 120.726 | 121.225 | -113.6261 | -121.2387
5296.5 | 121.1472 | -0.21057 | 120.9412 | -0.098801 | 0.013687 | -0.013191 | 0.85144 | -0.019741 | -0.015663 | 0.053017 | 8.3771 | 8.3038 | 7.7271 | 120.8176 | 120.4834 | 120.5109 | 120.4834 | 6.0287 | 121.0785 | -0.36163 | 7.9376 | -112.6373 | 8.5876 | 121.0281 | -0.45776 | -0.15106 | 0.13733 | 0.65002 | 120.694 | 6.2393 | 120.694 | 8.5144 | 8.5876 | 121.2891 | 120.7214 | -0.15106 | 8.5144 | 8.5876 | 120.7214 | 120.694 | 121.2891 | -113.2141 | -121.3028
5298.2188 | 121.1426 | -0.42114 | 120.7077 | -0.014877 | 0.014969 | -0.015541 | 1.9473 | -0.020809 | -0.012886 | 0.051522 | 14.0167 | 14.0076 | 9.0179 | 120.2682 | 119.9661 | 119.957 | 119.9936 | 4.9667 | 120.7535 | -0.58136 | 9.4391 | -106.7001 | 14.4379 | 120.6894 | -0.74158 | -0.16022 | 0.045776 | 4.9988 | 120.4147 | 5.3879 | 120.3873 | 14.4287 | 14.4379 | 121.1746 | 120.3781 | -0.16022 | 14.4287 | 14.4379 | 120.3781 | 120.3873 | 121.1746 | -111.6898 | -121.2891
5299.9844 | 121.1975 | -0.48981 | 120.5246 | 0.030899 | 0.014114 | -0.010628 | 2.6228 | -0.020382 | -0.013099 | 0.051735 | 11.554 | 11.6959 | 8.9767 | 119.8837 | 119.6136 | 119.6274 | 119.7327 | 4.6829 | 120.5978 | -0.70953 | 9.4666 | -108.8287 | 12.0438 | 120.3735 | -0.91095 | -0.21973 | 0.073242 | 2.5772 | 120.2225 | 5.1727 | 120.1035 | 12.1857 | 12.0438 | 121.0876 | 120.1172 | -0.21973 | 12.1857 | 12.0438 | 120.1172 | 120.1035 | 121.0876 | -111.5479 | -121.2341
5301.75 | 121.0968 | -0.46234 | 120.6299 | -0.14458 | 0.014755 | -0.017677 | 2.1513 | -0.021236 | -0.012031 | 0.035286 | 3.8132 | 3.8223 | 3.5934 | 120.2728 | 120.0394 | 119.9799 | 119.783 | 110.8978 | 120.6802 | -0.58136 | 4.0558 | -116.8076 | 4.2755 | 120.7352 | -0.59052 | -0.11902 | 0.050354 | 0.21973 | 120.2454 | 111.3602 | 120.5017 | 4.2847 | 4.2755 | 121.1426 | 120.4422 | -0.11902 | 4.2847 | 4.2755 | 120.4422 | 120.5017 | 121.1426 | -117.0364 | -121.2112
5303.4531 | 121.1472 | -0.59967 | 120.3598 | 0.076676 | 0.015396 | -0.012123 | 3.3382 | -0.0191 | -0.014167 | 0.042336 | 7.8415 | 8.0475 | 7.6218 | 119.4763 | 119.22 | 119.2703 | 119.3024 | 10.199 | 120.3186 | -0.82398 | 8.2214 | -112.3123 | 8.4412 | 120.076 | -1.1398 | -0.2243 | -0.041198 | 0.21973 | 119.902 | 10.7986 | 119.8196 | 8.6472 | 8.4412 | 120.9183 | 119.87 | -0.2243 | 8.6472 | 8.4412 | 119.87 | 119.8196 | 120.9183 | -112.738 | -121.1838
5305.2188 | 120.9457 | -1.1581 | 119.6732 | 0.13008 | 0.013046 | -0.011055 | 6.6372 | -0.019527 | -0.012672 | 0.051735 | 14.3051 | 14.2548 | 9.0225 | 118.0618 | 117.7872 | 117.8146 | 117.5766 | 5.0446 | 119.3253 | -1.3687 | 10.1807 | -105.4184 | 15.4633 | 119.22 | -1.886 | -0.21057 | -0.3479 | 5.2826 | 118.7347 | 6.2027 | 118.9453 | 15.4129 | 15.4633 | 120.4834 | 118.9728 | -0.21057 | 15.4129 | 15.4633 | 118.9728 | 118.9453 | 120.4834 | -110.6506 | -121.0419
5306.9375 | 120.7901 | -120.0302 | 0.36163 | 0.10719 | 0.014969 | -0.01255 | 0.093934 | -0.017177 | -0.014595 | 0.056221 | -0.064087 | 0.10071 | -0.21515 | 0.19684 | 0.21057 | 0.21515 | 0.16937 | -112.706 | 0.50812 | -120.3461 | 119.8151 | -0.26092 | 119.9661 | 120.2271 | -0.15106 | -0.31586 | 0.14648 | 0.15106 | 120.1996 | 7.3242 | 120.2408 | 120.1309 | 119.9661 | 120.5383 | 120.2454 | -0.31586 | 120.1309 | 119.9661 | 120.2454 | 120.2408 | 120.5383 | -0.57678 | -120.7077
5308.7031 | 120.8908 | -120.3094 | 0.40741 | -0.075912 | 0.01326 | -0.0093461 | 0.096498 | -0.019314 | -0.012031 | 0.059853 | -0.032043 | 0.07782 | -0.22888 | 0.24261 | 0.2243 | 0.2655 | 0.20142 | -113.0493 | 0.51727 | -120.5154 | 120.0806 | -0.32959 | 120.2774 | 120.5521 | -0.18311 | -0.20599 | 0.10986 | 0.19684 | 120.5109 | 7.2601 | 120.5338 | 120.3873 | 120.2774 | 120.8267 | 120.575 | -0.20599 | 120.3873 | 120.2774 | 120.575 | 120.5338 | 120.8267 | -0.63629 | -120.9229
5310.4688 | 120.8038 | -120.1492 | 0.4303 | 0.13008 | 0.016037 | -0.013191 | 0.068513 | -0.018673 | 0.054833 | 0.1077 | -0.091553 | 0.091553 | -0.23804 | 0.21057 | -120.0211 | 0.2655 | 0.24261 | -1.8265 | 0.58594 | -120.3323 | 119.9112 | -0.33875 | 120.0577 | 120.3598 | -120.4514 | -0.1831 | 0.15564 | 0.14648 | 120.3918 | 118.3228 | 0.12817 | 120.2408 | 120.0577 | 120.7352 | 120.4147 | -0.1831 | 120.2408 | 120.0577 | 120.4147 | 0.12817 | 120.7352 | -0.66834 | -120.7626
5312.2344 | 120.9503 | -120.2499 | 0.4715 | 0.13008 | 0.014328 | -0.014046 | 0.076417 | -0.019741 | 0.053765 | 0.12437 | -0.009155 | 0.045776 | -0.1831 | 0.33875 | -120.0531 | 0.40741 | 0.16937 | -11.8469 | 0.59052 | -120.4422 | 120.0668 | -0.42572 | 120.2408 | 120.5887 | -120.5246 | -0.19226 | 0.11902 | 0.17395 | 120.4193 | 108.403 | 0.19684 | 120.2957 | 120.2408 | 120.8405 | 120.6573 | -0.19226 | 120.2957 | 120.2408 | 120.6573 | 0.19684 | 120.8405 | -0.6546 | -120.9137
5313.9375 | 121.0007 | -120.2591 | 0.50354 | 0.13008 | 0.014969 | -0.011696 | 0.079622 | -0.020168 | 0.052483 | 0.11945 | -0.07782 | 0.064087 | -0.2243 | 0.32044 | -120.1859 | 0.37079 | 0.21515 | -4.3076 | 0.62256 | -120.4971 | 120.0348 | -0.43945 | 120.1813 | 120.5795 | -120.6894 | -0.23804 | 0.11902 | 0.14648 | 120.4742 | 115.9515 | 0.073242 | 120.3232 | 120.1813 | 120.8817 | 120.6299 | -0.23804 | 120.3232 | 120.1813 | 120.6299 | 0.073242 | 120.8817 | -0.72784 | -121.0007
5315.6875 | 121.1105 | -120.3094 | 0.50812 | 0.13008 | 0.015609 | -0.0149 | 0.079622 | -0.018673 | 0.052697 | 0.11625 | -0.086975 | 0.07782 | -0.21973 | 0.29755 | -120.2637 | 0.33417 | 0.29755 | 0.19684 | 0.64087 | -120.5383 | 120.0897 | -0.4303 | 120.2225 | 120.607 | -120.7718 | -0.22888 | 0.13275 | 0.13275 | 120.607 | 120.5063 | 0.045776 | 120.3873 | 120.2225 | 120.9503 | 120.6436 | -0.22888 | 120.3873 | 120.2225 | 120.6436 | 0.045776 | 120.9503 | -0.72784 | -121.0464
5317.4375 | 121.1105 | -120.3461 | 0.49439 | 0.17586 | 0.014755 | -0.014046 | 0.13901 | -0.019741 | 0.052269 | 0.17841 | -0.050354 | 0.073242 | -0.20599 | 0.37079 | -120.2362 | 0.41657 | 0.19226 | 0.3891 | 0.63171 | -120.5429 | 120.1401 | -0.42114 | 120.2957 | 120.7169 | -120.7306 | -0.19684 | 0.13733 | 0.15564 | 120.5383 | 120.7352 | 0.10986 | 120.4193 | 120.2957 | 120.9778 | 120.7626 | -0.19684 | 120.4193 | 120.2957 | 120.7626 | 0.10986 | 120.9778 | -0.70038 | -121.0373
5319.1562 | 121.0876 | -120.3827 | 0.52643 | 0.0080111 | 0.015823 | -0.016396 | 0.087312 | -0.019741 | 0.054406 | 0.13483 | -0.045776 | 0.068665 | -0.19684 | 0.36163 | -120.2225 | 0.43488 | 0.23804 | 0.54474 | 0.63629 | -120.6162 | 120.1859 | -0.45776 | 120.3369 | 120.7443 | -120.7489 | -0.23346 | 0.10986 | 0.15106 | 120.6207 | 120.9274 | 0.16022 | 120.4514 | 120.3369 | 121.019 | 120.8176 | -0.23346 | 120.4514 | 120.3369 | 120.8176 | 0.16022 | 121.019 | -0.72327 | -121.1426
5320.8594 | 120.6253 | -3.2364 | 117.3248 | 0.038529 | 0.014328 | -0.013405 | 0.045655 | 0.048405 | 0.049919 | 0.17542 | 0.07782 | 0.07782 | -0.16022 | -0.12817 | -0.15564 | -0.064087 | -0.41657 | -0.14648 | 117.4667 | -3.3966 | 3.0762 | -117.247 | 3.3142 | 3.1082 | -117.4805 | -0.16022 | 0.14191 | 0.23804 | 2.8198 | 3.0899 | 3.0807 | 3.3142 | 3.3142 | 120.7031 | 3.1723 | -0.16022 | 3.3142 | 3.3142 | 3.1723 | 3.0807 | 120.7031 | -117.485 | -120.7214
5322.625 | 120.7352 | -104.9927 | 15.2435 | 0.01564 | 0.015396 | -0.019386 | 0.026002 | -0.010982 | -0.0041272 | 0.02076 | -0.009155 | 0.091553 | -0.16022 | 0.21973 | 0.25635 | 0.29297 | 0.10986 | 0.39825 | 15.3625 | -105.336 | 104.8325 | -15.152 | 104.9835 | 105.2124 | -14.9872 | -0.34332 | 0.11902 | 0.15106 | 105.1025 | 105.3909 | 105.249 | 105.0842 | 104.9835 | 120.3552 | 105.2856 | -0.34332 | 105.0842 | 104.9835 | 105.2856 | 105.249 | 120.3552 | -15.4037 | -120.5795
5324.3906 | 120.9045 | -105.2948 | 15.1932 | 0.18349 | 0.013046 | -0.012764 | 0.031129 | -0.011623 | -0.0051954 | 0.020119 | 0.036621 | 0.064087 | -0.13733 | 0.28839 | 0.29297 | 0.35248 | 0.027466 | 0.46234 | 15.2802 | -105.5786 | 105.1575 | -15.1291 | 105.3314 | 105.5832 | -14.9002 | -0.28381 | 0.086975 | 0.17395 | 105.3223 | 105.7571 | 105.5878 | 105.3589 | 105.3314 | 120.575 | 105.6473 | -0.28381 | 105.3589 | 105.3314 | 105.6473 | 105.5878 | 120.575 | -15.3305 | -120.7718
5326.1562 | 116.4551 | -80.4382 | 35.1379 | -0.060654 | 0.015396 | -0.017036 | 0.047364 | -0.017605 | -0.0075452 | 0.031655 | 0.013733 | 0.082397 | -0.14648 | 0.3067 | 0.32501 | 0.3479 | 0.13275 | 0.47607 | 8.8898 | -112.1201 | 80.2917 | -35.0555 | 80.452 | 80.7449 | -34.8129 | -31.6818 | -26.2482 | 0.16022 | 80.571 | 80.9143 | 80.7632 | 80.5206 | 80.452 | 89.328 | 80.7861 | -31.6818 | 80.5206 | 80.452 | 80.7861 | 80.7632 | 89.328 | -35.2844 | -147.258
5327.8594 | 120.726 | -105.2124 | 15.0101 | 0.01564 | 0.015609 | -0.014687 | 0.022371 | -0.012478 | -0.0011364 | 0.021187 | -0.009155 | 0.086975 | -0.1831 | 0.22888 | 0.25635 | 0.29297 | 0.11902 | 0.41199 | 15.1291 | -105.5557 | 105.0293 | -14.9231 | 105.2032 | 105.4413 | -14.7537 | -0.34332 | 0.11902 | 0.17395 | 105.3314 | 105.6244 | 105.4688 | 105.2994 | 105.2032 | 120.3415 | 105.5054 | -0.34332 | 105.2994 | 105.2032 | 105.5054 | 105.4688 | 120.3415 | -15.1932 | -120.5658
5329.6094 | 120.7489 | -105.3772 | 15.1245 | -0.13695 | 0.013046 | -0.014259 | 0.02472 | -0.013546 | -0.0011364 | 0.023323 | 0.050354 | 0.086975 | -0.13733 | 0.32501 | 0.32959 | 0.37537 | 0.054932 | 0.5127 | 15.1932 | -105.6427 | 105.2399 | -15.0375 | 105.4276 | 105.7022 | -14.7949 | -0.2655 | 0.068664 | 0.18768 | 105.4321 | 105.8899 | 105.7068 | 105.4642 | 105.4276 | 120.5704 | 105.7526 | -0.2655 | 105.4642 | 105.4276 | 105.7526 | 105.7068 | 120.5704 | -15.2618 | -120.7672
5331.3125 | 120.8359 | -105.9631 | 14.6622 | -0.19798 | 0.014328 | -0.012123 | 0.03412 | -0.012691 | -0.0069042 | 0.019051 | -0.022888 | 0.1236 | -0.20599 | 0.24261 | 0.2243 | 0.24719 | 0.19684 | 0.38452 | 14.7949 | -106.1554 | 105.7571 | -14.5386 | 105.9402 | 106.2057 | -14.4379 | -0.19226 | 0.13275 | 0.18311 | 106.16 | 106.3477 | 106.1874 | 106.0867 | 105.9402 | 120.7581 | 106.2103 | -0.19226 | 106.0867 | 105.9402 | 106.2103 | 106.1874 | 120.7581 | -14.8682 | -120.8176
5333.0938 | 120.9091 | -105.661 | 15.0146 | -0.18272 | 0.014969 | -0.01725 | 0.031984 | -0.01205 | -0.0079724 | 0.023537 | -0.064087 | 0.13275 | -0.20142 | 0.21515 | 0.21973 | 0.21973 | 0.24719 | 0.37537 | 15.0604 | -105.9769 | 105.4596 | -14.8819 | 105.5969 | 105.8762 | -14.7949 | -0.31586 | 0.045777 | 0.13733 | 105.9082 | 106.0364 | 105.8807 | 105.7938 | 105.5969 | 120.7214 | 105.8807 | -0.31586 | 105.7938 | 105.5969 | 105.8807 | 105.8807 | 120.7214 | -15.2161 | -120.9915
5334.7969 | 120.9961 | -105.1209 | 15.6006 | -0.083542 | 0.012619 | -0.018104 | 0.034761 | -0.013118 | -0.0041272 | 0.032082 | 0.018311 | 0.082397 | -0.15564 | 0.31586 | 0.32501 | 0.35706 | 0.10071 | 0.48523 | 15.6738 | -105.368 | 104.9652 | -15.5182 | 105.1392 | 105.4367 | -15.2756 | -0.24719 | 0.073242 | 0.17395 | 105.2216 | 105.6061 | 105.4459 | 105.2032 | 105.1392 | 120.7947 | 105.4779 | -0.24719 | 105.2032 | 105.1392 | 105.4779 | 105.4459 | 120.7947 | -15.7562 | -120.9686
5336.5469 | 120.5658 | -105.5054 | 14.6805 | -0.12932 | 0.015182 | -0.011696 | 0.021943 | -0.01141 | -0.0026318 | 0.017769 | 0.064087 | 0.073242 | -0.15106 | 0.32959 | 0.3479 | 0.37079 | 0.059509 | 0.5127 | 14.8911 | -105.6427 | 105.3543 | -14.6072 | 105.5695 | 105.835 | -14.3326 | -0.13733 | 0.21057 | 0.21515 | 105.5649 | 106.0181 | 105.8533 | 105.5786 | 105.5695 | 120.3964 | 105.8762 | -0.13733 | 105.5786 | 105.5695 | 105.8762 | 105.8533 | 120.3964 | -14.8315 | -120.3232
5338.3125 | 120.9229 | -106.0272 | 14.534 | 0.030899 | 0.012832 | -0.013191 | 0.033693 | -0.013332 | -0.0056226 | 0.019051 | -0.022888 | 0.10071 | -0.20142 | 0.21973 | 0.20142 | 0.23346 | 0.23804 | 0.3479 | 14.6713 | -106.3019 | 105.8258 | -14.4333 | 106.0043 | 106.2469 | -14.3326 | -0.27466 | 0.13733 | 0.17853 | 106.2653 | 106.3751 | 106.2286 | 106.1279 | 106.0043 | 120.6985 | 106.2607 | -0.27466 | 106.1279 | 106.0043 | 106.2607 | 106.2286 | 120.6985 | -14.7354 | -120.8359
5340.0312 | 120.9457 | -106.2653 | 14.4424 | -0.083542 | 0.014755 | -0.011909 | 0.030916 | -0.011196 | -0.008186 | 0.019051 | 0.013733 | 0.09613 | -0.16479 | 0.2655 | 0.27466 | 0.30212 | 0.19226 | 0.39825 | 14.566 | -106.4621 | 106.1005 | -14.3463 | 106.279 | 106.5308 | -14.1678 | -0.19684 | 0.1236 | 0.17853 | 106.4575 | 106.6635 | 106.5399 | 106.3614 | 106.279 | 120.8313 | 106.5674 | -0.19684 | 106.3614 | 106.279 | 106.5674 | 106.5399 | 120.8313 | -14.6072 | -120.9045
5341.7969 | 120.9641 | -106.1874 | 14.6027 | -0.091171 | 0.013046 | -0.014259 | 0.030275 | -0.0092733 | -0.0060498 | 0.019478 | 0.004578 | 0.10529 | -0.19226 | 0.27008 | 0.27924 | 0.29755 | 0.19684 | 0.4303 | 14.7079 | -106.3705 | 105.9952 | -14.4974 | 106.192 | 106.4575 | -14.3234 | -0.1831 | 0.10529 | 0.19684 | 106.3843 | 106.6177 | 106.4667 | 106.2927 | 106.192 | 120.8954 | 106.485 | -0.1831 | 106.2927 | 106.192 | 106.485 | 106.4667 | 120.8954 | -14.7949 | -120.9732
5343.5625 | 120.9961 | -106.2241 | 14.6484 | -0.21324 | 0.016037 | -0.016609 | 0.02408 | -0.012264 | -0.005409 | 0.019692 | 0.059509 | 0.07782 | -0.14191 | 0.31586 | 0.36621 | 0.37537 | 0.12817 | 0.52643 | 14.7079 | -106.4163 | 106.0822 | -14.5706 | 106.2836 | 106.5399 | -14.2822 | -0.19226 | 0.05951 | 0.20142 | 106.3522 | 106.7505 | 106.5903 | 106.3019 | 106.2836 | 120.932 | 106.5994 | -0.19226 | 106.3019 | 106.2836 | 106.5994 | 106.5903 | 120.932 | -14.7903 | -121.0648
5345.3281 | 120.3827 | -5.1956 | 115.7547 | -0.083542 | 0.016464 | -0.015541 | 0.048433 | 0.044346 | 0.050133 | 0.17072 | 0.022888 | 0.10529 | -0.19226 | -0.23804 | -0.21973 | -0.21057 | -0.30212 | -0.12817 | 115.8554 | -5.3467 | 5.0034 | -115.6494 | 5.2185 | 4.9576 | -115.9744 | -0.15106 | 0.10071 | 0.21515 | 4.8935 | 5.0674 | 4.9759 | 5.3009 | 5.2185 | 121.051 | 4.985 | -0.15106 | 5.3009 | 5.2185 | 4.985 | 4.9759 | 121.051 | -115.947 | -121.1014
5347.0312 | 120.4788 | -4.8203 | 116.1438 | -0.23613 | 0.0139 | -0.013405 | 0.047792 | 0.043278 | 0.051415 | 0.17179 | -0.059509 | 0.1236 | -0.20142 | -0.28381 | -0.25635 | -0.26093 | -0.2243 | -0.15106 | 116.3589 | -4.9347 | 4.6188 | -116.0202 | 4.7607 | 4.5364 | -116.4001 | -0.11444 | 0.21515 | 0.14191 | 4.5959 | 4.6692 | 4.5639 | 4.9438 | 4.7607 | 121.1792 | 4.5593 | -0.11444 | 4.9438 | 4.7607 | 4.5593 | 4.5639 | 121.1792 | -116.3452 | -121.0785
5348.7969 | 120.9641 | -4.5547 | 116.4825 | -0.15984 | 0.013046 | -0.016182 | 0.045015 | 0.042637 | 0.051415 | 0.1735 | 0.041199 | 0.068665 | -0.15564 | -0.14648 | -0.12817 | -0.1236 | -0.39368 | 0.013733 | 116.5283 | -4.7241 | 4.3991 | -116.4139 | 4.5959 | 4.4083 | -116.6107 | -0.16937 | 0.045776 | 0.19684 | 4.1611 | 4.5685 | 4.4266 | 4.6234 | 4.5959 | 121.0831 | 4.4312 | -0.16937 | 4.6234 | 4.5959 | 4.4312 | 4.4266 | 121.0831 | -116.6382 | -121.2067
5350.4844 | 120.3003 | -2.7786 | 118.2083 | -0.12169 | 0.014755 | -0.016182 | 0.043733 | 0.047978 | 0.051415 | 0.16709 | 0.018311 | 0.10529 | -0.1831 | -0.23346 | -0.23346 | -0.22888 | -0.3067 | -0.10529 | 118.3502 | -2.9663 | 2.5955 | -118.103 | 2.7969 | 2.5452 | -118.4418 | -0.18768 | 0.14191 | 0.20142 | 2.4719 | 2.6733 | 2.5452 | 2.8839 | 2.7969 | 121.1288 | 2.5497 | -0.18768 | 2.8839 | 2.7969 | 2.5497 | 2.5452 | 121.1288 | -118.3914 | -121.1746
5352.2344 | 121.0098 | -2.7008 | 118.3182 | -0.16747 | 0.014328 | -0.013832 | 0.044374 | 0.046269 | 0.047997 | 0.17008 | -0.045776 | 0.12817 | -0.19226 | -0.27008 | -0.23804 | -0.24719 | -0.25635 | -0.12817 | 118.4052 | -2.9663 | 2.5085 | -118.19 | 2.655 | 2.4307 | -118.5562 | -0.2655 | 0.086975 | 0.14648 | 2.4445 | 2.5726 | 2.4628 | 2.829 | 2.655 | 121.106 | 2.4536 | -0.2655 | 2.829 | 2.655 | 2.4536 | 2.4628 | 121.106 | -118.5104 | -121.2845
5354 | 120.607 | -71.5073 | 47.7448 | 0.0080111 | 0.014328 | -0.016823 | 0.041383 | 0.011021 | 0.020012 | 0.082283 | -0.041199 | 0.1236 | -0.16937 | 0.004578 | 0.059509 | 0.20599 | 0.11444 | 0.34332 | 45.8633 | -82.5256 | 71.3379 | -47.6212 | 71.4661 | 71.5118 | -47.6852 | -11.0184 | -1.8814 | 0.12817 | 71.6217 | 71.8506 | 71.5668 | 71.6309 | 71.4661 | 117.3706 | 71.7133 | -11.0184 | 71.6309 | 71.4661 | 71.7133 | 71.5668 | 117.3706 | -47.9141 | -130.2704
5355.7031 | 120.8588 | -7.1228 | 113.5712 | 0.030899 | 0.013687 | -0.015327 | 0.039033 | 0.040928 | 0.051628 | 0.1656 | -0.022888 | 0.086975 | -0.16022 | -0.21973 | -0.16022 | -0.15564 | -0.34332 | -0.036621 | 113.6993 | -7.3059 | 6.9626 | -113.4842 | 7.0999 | 6.9031 | -113.7314 | -0.1831 | 0.12817 | 0.13733 | 6.7795 | 7.0862 | 6.9626 | 7.2098 | 7.0999 | 120.8221 | 6.9672 | -0.1831 | 7.2098 | 7.0999 | 6.9672 | 6.9626 | 120.8221 | -113.7314 | -120.8771
5357.4688 | 120.8862 | -6.546 | 114.2395 | 0.099564 | 0.013687 | -0.013832 | 0.049287 | 0.041783 | 0.049919 | 0.16581 | 0.054932 | 0.073242 | -0.16022 | -0.14648 | -0.14648 | -0.10986 | -0.4303 | -0.004578 | 114.3402 | -6.7978 | 6.3858 | -114.1663 | 6.601 | 6.3995 | -114.386 | -0.25177 | 0.10071 | 0.21515 | 6.1157 | 6.5414 | 6.3995 | 6.6193 | 6.601 | 120.8862 | 6.4362 | -0.25177 | 6.6193 | 6.601 | 6.4362 | 6.3995 | 120.8862 | -114.3997 | -121.0373
5359.2344 | 120.8862 | -5.7175 | 115.21 | -0.17509 | 0.012405 | -0.01255 | 0.050569 | 0.041996 | 0.049279 | 0.17457 | 0.041199 | 0.064087 | -0.16479 | -0.12817 | -0.11902 | -0.10071 | -0.38452 | 0.036621 | 115.2878 | -5.9006 | 5.5527 | -115.1459 | 5.7587 | 5.5893 | -115.329 | -0.18311 | 0.07782 | 0.20599 | 5.3329 | 5.7541 | 5.5984 | 5.7816 | 5.7587 | 121.0052 | 5.6168 | -0.18311 | 5.7816 | 5.7587 | 5.6168 | 5.5984 | 121.0052 | -115.3748 | -121.1105
5360.9375 | 121.0236 | -4.7653 | 116.1163 | 0.1606 | 0.017318 | -0.011482 | 0.050782 | 0.043919 | 0.048851 | 0.17393 | -0.004578 | 0.09613 | -0.17395 | -0.18768 | -0.18768 | -0.15106 | -0.40283 | -0.054932 | 116.2674 | -4.9713 | 4.5914 | -116.0202 | 4.7607 | 4.5776 | -116.304 | -0.20599 | 0.15106 | 0.16937 | 4.3625 | 4.7104 | 4.5776 | 4.8614 | 4.7607 | 121.0327 | 4.6143 | -0.20599 | 4.8614 | 4.7607 | 4.6143 | 4.5776 | 121.0327 | -116.2903 | -121.0876
5362.7031 | 121.0098 | -4.7333 | 116.2628 | 0.0080111 | 0.014755 | -0.012764 | 0.05356 | 0.045414 | 0.045433 | 0.17265 | -0.004578 | 0.10529 | -0.19226 | -0.23804 | -0.23346 | -0.22888 | -0.28381 | -0.12817 | 116.4551 | -4.9118 | 4.541 | -116.1575 | 4.7287 | 4.4952 | -116.4963 | -0.17853 | 0.19226 | 0.18768 | 4.4495 | 4.6051 | 4.4998 | 4.8386 | 4.7287 | 121.1884 | 4.5044 | -0.17853 | 4.8386 | 4.7287 | 4.5044 | 4.4998 | 121.1884 | -116.4551 | -121.1746
5364.4688 | 121.0602 | -4.6829 | 116.2949 | -0.2285 | 0.016464 | -0.016823 | 0.04886 | 0.043705 | 0.04757 | 0.17457 | -0.045776 | 0.10071 | -0.18768 | -0.24719 | -0.23346 | -0.23346 | -0.1831 | -0.10986 | 116.4917 | -4.9347 | 4.4952 | -116.1942 | 4.6371 | 4.4357 | -116.5283 | -0.25177 | 0.19684 | 0.14191 | 4.4998 | 4.5731 | 4.4495 | 4.7836 | 4.6371 | 121.1746 | 4.4495 | -0.25177 | 4.7836 | 4.6371 | 4.4495 | 4.4495 | 121.1746 | -116.4825 | -121.2296
5366.2344 | 121.0739 | -4.715 | 116.3177 | -0.0072479 | 0.017105 | -0.0093461 | 0.052064 | 0.044987 | 0.047356 | 0.17201 | -0.009155 | 0.10986 | -0.19684 | -0.24719 | -0.26093 | -0.23346 | -0.26093 | -0.11902 | 116.5283 | -4.8843 | 4.5181 | -116.2079 | 4.7058 | 4.4678 | -116.5787 | -0.16937 | 0.21057 | 0.18768 | 4.454 | 4.5959 | 4.454 | 4.8248 | 4.7058 | 121.2433 | 4.4815 | -0.16937 | 4.8248 | 4.7058 | 4.4815 | 4.454 | 121.2433 | -116.5146 | -121.2021
5367.9375 | 121.0693 | -4.4632 | 116.6428 | -0.19798 | 0.013473 | -0.016396 | 0.045655 | 0.041569 | 0.048851 | 0.175 | 0.054932 | 0.068665 | -0.15106 | -0.15564 | -0.11444 | -0.1236 | -0.36621 | 0.032043 | 116.7801 | -4.5959 | 4.3121 | -116.5741 | 4.5181 | 4.3076 | -116.7572 | -0.13275 | 0.13733 | 0.20599 | 4.097 | 4.4952 | 4.3488 | 4.5319 | 4.5181 | 121.2433 | 4.3396 | -0.13275 | 4.5319 | 4.5181 | 4.3396 | 4.3488 | 121.2433 | -116.7938 | -121.2387
5369.7031 | 121.1884 | -4.3488 | 116.6611 | 0.18349 | 0.015396 | -0.012123 | 0.053773 | 0.044132 | 0.050347 | 0.17841 | -0.036621 | 0.10071 | -0.18768 | -0.20599 | -0.19684 | -0.17853 | -0.37079 | -0.073242 | 116.8442 | -4.5319 | 4.1611 | -116.5604 | 4.3121 | 4.1428 | -116.8579 | -0.18311 | 0.1831 | 0.15106 | 3.978 | 4.2755 | 4.1519 | 4.4495 | 4.3121 | 121.1929 | 4.1702 | -0.18311 | 4.4495 | 4.3121 | 4.1702 | 4.1519 | 121.1929 | -116.8488 | -121.1929
5371.4062 | 121.2204 | -4.4861 | 116.5924 | 0.13008 | 0.013046 | -0.017677 | 0.052064 | 0.041355 | 0.051201 | 0.18226 | 0.050354 | 0.064087 | -0.13275 | -0.16937 | -0.13275 | -0.10529 | -0.4303 | -0.022888 | 116.7572 | -4.6188 | 4.3533 | -116.5283 | 4.5364 | 4.3167 | -116.7252 | -0.13275 | 0.1648 | 0.18311 | 4.0558 | 4.4632 | 4.3533 | 4.5502 | 4.5364 | 121.2433 | 4.3808 | -0.13275 | 4.5502 | 4.5364 | 4.3808 | 4.3533 | 121.2433 | -116.7252 | -121.2112
5373.1719 | 121.1746 | -4.5502 | 116.6382 | -0.20561 | 0.017318 | -0.012337 | 0.057832 | 0.042423 | 0.04821 | 0.17991 | -0.041199 | 0.10529 | -0.1831 | -0.24719 | -0.23346 | -0.23346 | -0.21973 | -0.091553 | 116.8121 | -4.7104 | 4.3671 | -116.5329 | 4.509 | 4.303 | -116.8716 | -0.16022 | 0.17395 | 0.14191 | 4.3304 | 4.4586 | 4.3167 | 4.6555 | 4.509 | 121.3623 | 4.3167 | -0.16022 | 4.6555 | 4.509 | 4.3167 | 4.3167 | 121.3623 | -116.8213 | -121.3486
5374.875 | 121.1334 | -4.4449 | 116.6885 | -0.068283 | 0.014755 | -0.017036 | 0.061036 | 0.044346 | 0.047997 | 0.18461 | 0.009155 | 0.11902 | -0.1831 | -0.2243 | -0.20142 | -0.20599 | -0.28839 | -0.07782 | 116.9037 | -4.5731 | 4.2618 | -116.5695 | 4.454 | 4.2206 | -116.89 | -0.12817 | 0.21515 | 0.19226 | 4.1565 | 4.3671 | 4.2435 | 4.5639 | 4.454 | 121.3486 | 4.2389 | -0.12817 | 4.5639 | 4.454 | 4.2389 | 4.2435 | 121.3486 | -116.8716 | -121.2616
5376.6406 | 121.1792 | -3.8635 | 117.3157 | -0.098801 | 0.015396 | -0.0149 | 0.061036 | 0.043492 | 0.048638 | 0.18162 | 0 | 0.10529 | -0.17853 | -0.21515 | -0.19226 | -0.19684 | -0.29297 | -0.064087 | 117.4713 | -4.0421 | 3.685 | -117.2104 | 3.8635 | 3.6484 | -117.5079 | -0.17853 | 0.15564 | 0.17853 | 3.5706 | 3.7994 | 3.6713 | 3.9688 | 3.8635 | 121.3348 | 3.6667 | -0.17853 | 3.9688 | 3.8635 | 3.6667 | 3.6713 | 121.3348 | -117.4942 | -121.3577
5378.3906 | 120.4285 | -82.1915 | 38.1546 | -0.23613 | 0.015182 | -0.015114 | 0.033479 | 0.00012612 | 0.0071948 | 0.057717 | 0.054932 | 0.073242 | -0.12817 | 0.16937 | 0.23804 | 0.24719 | 0.018311 | 0.39368 | 38.2324 | -82.3151 | 82.0633 | -38.0814 | 82.2464 | 82.3608 | -37.9166 | -0.1236 | 0.07782 | 0.18311 | 82.2098 | 82.5851 | 82.4295 | 82.2647 | 82.2464 | 120.4239 | 82.4387 | -0.1236 | 82.2647 | 82.2464 | 82.4387 | 82.4295 | 120.4239 | -38.2828 | -120.4697
5380.1719 | 120.2316 | -10.7208 | 109.7992 | -0.15221 | 0.01625 | -0.011909 | 0.047578 | 0.044987 | 0.045647 | 0.16154 | 0.004578 | 0.11444 | -0.18768 | -0.19226 | -0.18768 | -0.16479 | -0.25177 | -0.045776 | 110.5041 | -10.4416 | 10.5331 | -109.6848 | 10.7254 | 10.5286 | -109.9869 | 0.27924 | 0.70496 | 0.19226 | 10.4691 | 10.675 | 10.5331 | 10.8353 | 10.7254 | 121.225 | 10.556 | 0.27924 | 10.8353 | 10.7254 | 10.556 | 10.5331 | 121.225 | -109.9869 | -120.2408
5381.8594 | 120.9732 | -111.0214 | 9.4254 | -0.014877 | 0.013687 | -0.016823 | 0.52481 | -0.015468 | -0.0077588 | 0.51188 | -0.018311 | 0.10529 | -0.14191 | 0.26093 | 0.32959 | 0.35248 | 0.15564 | 0.45319 | 9.6359 | -111.232 | 110.8795 | -9.3201 | 111.0031 | 111.2823 | -9.0958 | -0.21057 | 0.21057 | 0.1236 | 111.1771 | 111.4746 | 111.351 | 111.1267 | 111.0031 | 120.6573 | 111.3739 | -0.21057 | 111.1267 | 111.0031 | 111.3739 | 111.351 | 120.6573 | -9.5673 | -120.6573
5383.6094 | 121.0144 | -119.1605 | 1.4923 | 0.1606 | 0.012832 | -0.01255 | 0.054628 | -0.017391 | -0.012245 | 0.024605 | 0.07782 | 0.064087 | -0.13275 | 0.35706 | 0.37079 | 0.43488 | 0.086975 | 0.52643 | 1.5839 | -119.3939 | 119.0277 | -1.4282 | 119.2383 | 119.5175 | -1.1215 | -0.23346 | 0.091552 | 0.21057 | 119.2474 | 119.6869 | 119.5312 | 119.2245 | 119.2383 | 120.7443 | 119.5953 | -0.23346 | 119.2245 | 119.2383 | 119.5953 | 119.5312 | 120.7443 | -1.6251 | -120.8862
5385.375 | 121.1014 | -119.696 | 0.99792 | 0.13771 | 0.014114 | -0.015327 | 0.057405 | -0.020382 | -0.015876 | 0.025887 | -0.041199 | 0.11444 | -0.18768 | 0.24719 | 0.26093 | 0.29755 | 0.27008 | 0.39368 | 1.1948 | -119.9799 | 119.5084 | -0.88348 | 119.6548 | 119.9432 | -0.737 | -0.28381 | 0.19684 | 0.14648 | 119.9661 | 120.0897 | 119.957 | 119.8105 | 119.6548 | 120.8908 | 119.9936 | -0.28381 | 119.8105 | 119.6548 | 119.9936 | 119.957 | 120.8908 | -1.1856 | -120.9778
5387.125 | 120.9961 | -0.40741 | 120.5566 | 0.12245 | 0.014755 | -0.0149 | 0.047364 | 0.044987 | 0.054192 | 0.17692 | 0.068665 | 0.073242 | -0.14191 | -0.1831 | -0.16479 | -0.1236 | -0.46234 | -0.027466 | 120.6848 | -0.57678 | 0.2655 | -120.4834 | 0.47608 | 0.22431 | -120.7214 | -0.16937 | 0.12817 | 0.21057 | -0.054931 | 0.37994 | 0.24261 | 0.48065 | 0.47608 | 121.0922 | 0.28381 | -0.16937 | 0.48065 | 0.47608 | 0.28381 | 0.24261 | 121.0922 | -120.6985 | -121.1334
5388.8281 | 121.0556 | -0.3891 | 120.575 | 0.15297 | 0.014541 | -0.01725 | 0.049073 | 0.045414 | 0.051415 | 0.17521 | 0.050354 | 0.068665 | -0.15564 | -0.1831 | -0.15564 | -0.1236 | -0.48065 | -0.022888 | 120.6894 | -0.56305 | 0.23346 | -120.5063 | 0.43945 | 0.20599 | -120.7306 | -0.17395 | 0.11444 | 0.20599 | -0.091553 | 0.36621 | 0.23346 | 0.45776 | 0.43945 | 121.0785 | 0.2655 | -0.17395 | 0.45776 | 0.43945 | 0.2655 | 0.23346 | 121.0785 | -120.7306 | -121.138
5390.5781 | 121.1151 | -0.38452 | 120.6436 | -0.053024 | 0.014755 | -0.016396 | 0.042451 | 0.043064 | 0.054406 | 0.17542 | 0.013733 | 0.091553 | -0.14191 | -0.21057 | -0.16022 | -0.16022 | -0.38452 | -0.018311 | 120.7947 | -0.58136 | 0.24261 | -120.5521 | 0.39825 | 0.17395 | -120.8038 | -0.19684 | 0.15106 | 0.15564 | 0 | 0.36621 | 0.2243 | 0.47607 | 0.39825 | 121.1792 | 0.2243 | -0.19684 | 0.47607 | 0.39825 | 0.2243 | 0.2243 | 121.1792 | -120.7855 | -121.225
5392.3281 | 121.1426 | -0.38452 | 120.6619 | 0.084305 | 0.012191 | -0.014687 | 0.047578 | 0.043919 | 0.052697 | 0.17756 | 0.045776 | 0.068665 | -0.15106 | -0.17395 | -0.16479 | -0.15564 | -0.45776 | -0.045776 | 120.7901 | -0.56305 | 0.23346 | -120.5933 | 0.4303 | 0.21057 | -120.8267 | -0.17853 | 0.12817 | 0.19684 | -0.073243 | 0.33875 | 0.21973 | 0.45319 | 0.4303 | 121.1746 | 0.22888 | -0.17853 | 0.45319 | 0.4303 | 0.22888 | 0.21973 | 121.1746 | -120.813 | -121.225
5394.0312 | 121.0922 | -0.4303 | 120.7169 | -0.13695 | 0.0139 | -0.018532 | 0.046296 | 0.041569 | 0.054619 | 0.17457 | 0.059509 | 0.068665 | -0.15564 | -0.15564 | -0.12817 | -0.10986 | -0.42572 | 0.041199 | 120.8267 | -0.55847 | 0.27466 | -120.6482 | 0.48981 | 0.27466 | -120.845 | -0.12817 | 0.10986 | 0.21515 | 0.004578 | 0.4715 | 0.30212 | 0.49896 | 0.48981 | 121.257 | 0.32044 | -0.12817 | 0.49896 | 0.48981 | 0.32044 | 0.30212 | 121.257 | -120.8725 | -121.2753
5395.7812 | 121.2067 | -0.36621 | 120.7031 | -0.068283 | 0.013473 | -0.014046 | 0.046724 | 0.04456 | 0.052269 | 0.17756 | 0.022888 | 0.09613 | -0.15564 | -0.18768 | -0.17395 | -0.14191 | -0.42572 | -0.004578 | 120.8908 | -0.58136 | 0.21057 | -120.607 | 0.3891 | 0.17853 | -120.8771 | -0.21515 | 0.18768 | 0.17853 | -0.059509 | 0.36163 | 0.19226 | 0.46234 | 0.3891 | 121.257 | 0.2243 | -0.21515 | 0.46234 | 0.3891 | 0.2243 | 0.19226 | 121.257 | -120.8588 | -121.2845
5397.5312 | 121.1563 | -0.41657 | 120.7535 | -0.15221 | 0.0139 | -0.015327 | 0.04651 | 0.043492 | 0.053978 | 0.17628 | 0.054932 | 0.07782 | -0.17853 | -0.14191 | -0.1236 | -0.11444 | -0.4303 | 0.032043 | 120.8862 | -0.55847 | 0.23804 | -120.6757 | 0.4715 | 0.27466 | -120.8771 | -0.14191 | 0.13275 | 0.23346 | -0.013733 | 0.44861 | 0.29297 | 0.49439 | 0.4715 | 121.3028 | 0.30212 | -0.14191 | 0.49439 | 0.4715 | 0.30212 | 0.29297 | 121.3028 | -120.932 | -121.312
5399.2969 | 120.3506 | -0.37079 | 119.8334 | 0.053787 | 0.015396 | -0.015541 | 0.04651 | 0.040928 | 0.053337 | 0.1609 | -0.032043 | 0.10986 | -0.20142 | 16.5344 | -0.28839 | 39.2715 | 0.62256 | 0.70038 | 120.0668 | -0.57678 | 0.16937 | -119.7235 | 0.33875 | 16.9052 | -120.1218 | -0.20599 | 0.23346 | 0.16937 | 0.99335 | 1.0712 | 0.082398 | 0.48065 | 0.33875 | 120.4376 | 39.6423 | -0.20599 | 0.48065 | 0.33875 | 39.6423 | 0.082398 | 120.4376 | -120.0348 | -120.4102
5401 | 120.6802 | -0.38452 | 120.2637 | -0.22087 | 0.014541 | -0.015755 | 0.040101 | 0.03751 | 0.051842 | 0.16346 | -0.045776 | 0.11444 | -0.19684 | 14.3005 | -0.2655 | 40.2328 | 0.59052 | 0.69122 | 120.4697 | -0.59967 | 0.18768 | -120.1492 | 0.33875 | 14.6851 | -120.5292 | -0.21515 | 0.20599 | 0.15106 | 0.97504 | 1.0757 | 0.11902 | 0.49896 | 0.33875 | 120.8542 | 40.6174 | -0.21515 | 0.49896 | 0.33875 | 40.6174 | 0.11902 | 120.8542 | -120.4605 | -120.8633
5402.7656 | 120.7993 | -0.40283 | 120.3781 | -0.25139 | 0.014328 | -0.018104 | 0.042238 | 0.036656 | 0.055687 | 0.16688 | -0.064087 | 0.11444 | -0.20599 | 15.2435 | -0.25177 | 40.9332 | 0.58136 | 0.67291 | 120.5429 | -0.60425 | 0.19684 | -120.2637 | 0.33875 | 15.6464 | -120.6299 | -0.20142 | 0.16479 | 0.14191 | 0.98419 | 1.0757 | 0.15106 | 0.51727 | 0.33875 | 120.9457 | 41.3361 | -0.20142 | 0.51727 | 0.33875 | 41.3361 | 0.15106 | 120.9457 | -120.5841 | -120.9824
5404.5312 | 120.8725 | -0.39825 | 120.4559 | -0.13695 | 0.01326 | -0.010841 | 0.03946 | 0.036015 | 0.053551 | 0.16389 | 0.041199 | 0.09613 | -0.15564 | 16.04 | -0.13733 | 40.8463 | 0.55389 | 0.98877 | 120.6116 | -0.54474 | 0.24261 | -120.3598 | 0.43945 | 16.4383 | -120.5933 | -0.14648 | 0.15564 | 0.19684 | 0.95215 | 1.387 | 0.26092 | 0.49438 | 0.43945 | 121.0098 | 41.2445 | -0.14648 | 0.49438 | 0.43945 | 41.2445 | 0.26092 | 121.0098 | -120.6116 | -121.0007
5406.2969 | 120.8633 | -0.41657 | 120.5246 | -0.10643 | 0.014541 | -0.015755 | 0.048433 | 0.038151 | 0.050347 | 0.16367 | 0.009155 | 0.10986 | -0.18768 | 16.9098 | -0.2243 | 40.2328 | 0.89264 | 1.1124 | 120.7169 | -0.56305 | 0.22888 | -120.4147 | 0.42572 | 17.3264 | -120.7489 | -0.14648 | 0.19226 | 0.19684 | 1.3092 | 1.5289 | 0.19226 | 0.52643 | 0.42572 | 121.1334 | 40.6494 | -0.14648 | 0.52643 | 0.42572 | 40.6494 | 0.19226 | 121.1334 | -120.7123 | -121.0876
5408.0469 | 120.9778 | -0.37994 | 120.5658 | -0.25139 | 0.015609 | -0.013618 | 0.041597 | 0.035588 | 0.053124 | 0.16389 | -0.045776 | 0.11444 | -0.19684 | 16.7679 | -0.2655 | 39.9033 | 1.03 | 1.1032 | 120.7855 | -0.58594 | 0.18311 | -120.4514 | 0.33417 | 17.1478 | -120.8313 | -0.20599 | 0.21973 | 0.15106 | 1.4099 | 1.4832 | 0.11444 | 0.49439 | 0.33417 | 121.1655 | 40.2832 | -0.20599 | 0.49439 | 0.33417 | 40.2832 | 0.11444 | 121.1655 | -120.7626 | -121.1517
5409.75 | 121.0876 | -0.36163 | 120.6116 | -0.068283 | 0.012619 | -0.013405 | 0.03946 | -0.016536 | 0.053978 | 0.10856 | 0.013733 | 0.091553 | -0.15564 | 114.949 | -0.15564 | 63.002 | -0.29755 | 0.086975 | 120.7855 | -0.57678 | 0.20599 | -120.52 | 0.37537 | 115.3107 | -120.7672 | -0.21515 | 0.17395 | 0.16937 | 0.064087 | 0.44861 | 0.20599 | 0.45319 | 0.37537 | 121.1472 | 63.3636 | -0.21515 | 0.45319 | 0.37537 | 63.3636 | 0.20599 | 121.1472 | -120.7672 | -121.1884
5411.5156 | 121.1288 | -0.3891 | 120.6436 | 0.13008 | 0.015823 | -0.012123 | 0.045655 | -0.015255 | 0.051628 | 0.10792 | 0.045776 | 0.09613 | -0.16022 | 115.0681 | -0.16479 | 63.1851 | -0.3479 | 0.045776 | 120.8084 | -0.53558 | 0.22888 | -120.5475 | 0.43487 | 115.4572 | -120.8084 | -0.14648 | 0.1648 | 0.20599 | 0.041199 | 0.43487 | 0.2243 | 0.48523 | 0.43487 | 121.1975 | 63.5742 | -0.14648 | 0.48523 | 0.43487 | 63.5742 | 0.2243 | 121.1975 | -120.8038 | -121.1792
5413.2812 | 121.2204 | -0.35706 | 120.6573 | 0.0080111 | 0.013046 | -0.015541 | 0.038392 | -0.020382 | 0.054619 | 0.10471 | -0.013733 | 0.086975 | -0.14191 | 114.8895 | -0.19684 | 62.9837 | -0.28381 | 0.018311 | 120.7947 | -0.57678 | 0.21515 | -120.5704 | 0.34332 | 115.2466 | -120.8542 | -0.21973 | 0.13733 | 0.12817 | 0.073243 | 0.37537 | 0.16022 | 0.44403 | 0.34332 | 121.1517 | 63.3408 | -0.21973 | 0.44403 | 0.34332 | 63.3408 | 0.16022 | 121.1517 | -120.7993 | -121.2341
5415 | 121.1334 | -0.40741 | 120.7443 | -0.26665 | 0.013687 | -0.012123 | 0.042878 | -0.017605 | 0.05291 | 0.10899 | 0.027466 | 0.082397 | -0.14191 | 114.9078 | -0.21515 | 62.4481 | -0.21973 | 0.036621 | 120.8954 | -0.59052 | 0.2655 | -120.6619 | 0.43488 | 115.3152 | -120.9595 | -0.18311 | 0.15106 | 0.16937 | 0.18768 | 0.44403 | 0.19226 | 0.48981 | 0.43488 | 121.3028 | 62.8555 | -0.18311 | 0.48981 | 0.43488 | 62.8555 | 0.19226 | 121.3028 | -120.8862 | -121.3348
5416.75 | 121.1746 | -0.39825 | 120.7123 | -0.2285 | 0.013046 | -0.012978 | 0.043947 | -0.02145 | 0.053765 | 0.10792 | -0.027466 | 0.11444 | -0.19226 | 114.798 | -0.25635 | 61.908 | -0.17853 | -0.027466 | 120.9137 | -0.59509 | 0.20599 | -120.5978 | 0.37079 | 115.1962 | -120.9686 | -0.19684 | 0.20142 | 0.16479 | 0.21973 | 0.37079 | 0.14191 | 0.5127 | 0.37079 | 121.3119 | 62.3062 | -0.19684 | 0.5127 | 0.37079 | 62.3062 | 0.14191 | 121.3119 | -120.9045 | -121.3074
5418.5 | 121.2341 | -0.39825 | 120.7535 | 0.053787 | 0.014541 | -0.013191 | 0.048219 | 0.02982 | 0.050988 | 0.15513 | -0.054932 | 0.12817 | -0.20599 | 31.517 | -0.30212 | 41.8442 | -0.20142 | -0.10529 | 120.9732 | -0.5722 | 0.19226 | -120.6253 | 0.34332 | 31.9153 | -121.0556 | -0.17395 | 0.21973 | 0.15106 | 0.19684 | 0.29297 | 0.09613 | 0.52643 | 0.34332 | 121.3715 | 42.2424 | -0.17395 | 0.52643 | 0.34332 | 42.2424 | 0.09613 | 121.3715 | -120.9595 | -121.3257
5420.2812 | 121.2708 | -0.37079 | 120.7352 | 0.12245 | 0.014755 | -0.012978 | 0.04651 | 0.030674 | 0.053551 | 0.15791 | -0.027466 | 0.11444 | -0.17853 | 27.9327 | -0.25635 | 41.5237 | -0.28839 | -0.054932 | 120.9229 | -0.58594 | 0.19226 | -120.6207 | 0.34332 | 28.3035 | -120.9915 | -0.21515 | 0.18768 | 0.15106 | 0.082398 | 0.31586 | 0.11444 | 0.48523 | 0.34332 | 121.2936 | 41.8945 | -0.21515 | 0.48523 | 0.34332 | 41.8945 | 0.11444 | 121.2936 | -120.9137 | -121.3211
5422.0469 | 121.225 | -0.40283 | 120.7947 | -0.13695 | 0.016037 | -0.0095597 | 0.039888 | 0.027897 | 0.058464 | 0.15897 | 0.050354 | 0.082397 | -0.16022 | 26.4908 | -0.13733 | 41.2354 | -0.38452 | 0.064087 | 120.9091 | -0.56763 | 0.24262 | -120.7123 | 0.45319 | 26.8936 | -120.932 | -0.16479 | 0.11444 | 0.21057 | 0.018311 | 0.46692 | 0.2655 | 0.48523 | 0.45319 | 121.312 | 41.6382 | -0.16479 | 0.48523 | 0.45319 | 41.6382 | 0.2655 | 121.312 | -120.9549 | -121.3623
5423.75 | 121.312 | -0.3891 | 120.7764 | 0.061417 | 0.014755 | -0.016396 | 0.048433 | 0.034092 | 0.053978 | 0.15855 | -0.045776 | 0.10986 | -0.19684 | 25.2274 | -0.29755 | 40.6586 | -0.21515 | -0.11444 | 121.0327 | -0.60425 | 0.19226 | -120.6665 | 0.34332 | 25.6165 | -121.0739 | -0.21515 | 0.25635 | 0.15106 | 0.17395 | 0.27466 | 0.091553 | 0.49896 | 0.34332 | 121.4218 | 41.0477 | -0.21515 | 0.49896 | 0.34332 | 41.0477 | 0.091553 | 121.4218 | -120.9732 | -121.3806
5425.5156 | 121.3531 | -0.37079 | 120.7855 | 0.084305 | 0.014969 | -0.012978 | 0.044374 | 0.03281 | 0.051628 | 0.1594 | -0.027466 | 0.11902 | -0.19684 | 24.8383 | -0.27466 | 40.6723 | -0.24719 | -0.091553 | 121.0556 | -0.58594 | 0.17395 | -120.6665 | 0.34332 | 25.209 | -121.0602 | -0.21515 | 0.27008 | 0.16937 | 0.1236 | 0.27924 | 0.096131 | 0.48981 | 0.34332 | 121.4264 | 41.0431 | -0.21515 | 0.48981 | 0.34332 | 41.0431 | 0.096131 | 121.4264 | -120.9824 | -121.3715
5427.2812 | 121.2479 | -0.4303 | 120.8405 | -0.16747 | 0.015823 | -0.015541 | 0.039247 | 0.032597 | 0.054619 | 0.1594 | 0.050354 | 0.07782 | -0.15564 | 24.6963 | -0.14191 | 40.3839 | -0.33875 | 0.091553 | 120.9686 | -0.56305 | 0.27466 | -120.7626 | 0.48065 | 25.1266 | -120.9824 | -0.13275 | 0.12817 | 0.20599 | 0.091553 | 0.52185 | 0.28839 | 0.50812 | 0.48065 | 121.3989 | 40.8142 | -0.13275 | 0.50812 | 0.48065 | 40.8142 | 0.28839 | 121.3989 | -120.9961 | -121.4035
5429.0312 | 121.3028 | -0.42114 | 120.8633 | -0.15221 | 0.014541 | -0.013405 | 0.042878 | 0.031956 | 0.053124 | 0.15897 | -0.045776 | 0.10986 | -0.1831 | 24.0509 | -0.27008 | 40.21 | -0.16479 | -0.050354 | 121.0968 | -0.6134 | 0.23804 | -120.7535 | 0.37537 | 24.472 | -121.1334 | -0.19226 | 0.23346 | 0.13733 | 0.25635 | 0.37079 | 0.15106 | 0.53101 | 0.37537 | 121.5179 | 40.6311 | -0.19226 | 0.53101 | 0.37537 | 40.6311 | 0.15106 | 121.5179 | -121.0464 | -121.4767
5430.7344 | 121.3348 | -0.4303 | 120.8817 | -0.25139 | 0.015396 | -0.015327 | 0.042665 | 0.030461 | 0.051628 | 0.16004 | 0.004578 | 0.10071 | -0.17853 | 23.7167 | -0.2243 | 40.1459 | -0.21515 | -0.027466 | 121.0739 | -0.61798 | 0.25177 | -120.7809 | 0.43488 | 24.147 | -121.106 | -0.18768 | 0.19226 | 0.18311 | 0.21515 | 0.40283 | 0.20599 | 0.53101 | 0.43488 | 121.5042 | 40.5762 | -0.18768 | 0.53101 | 0.43488 | 40.5762 | 0.20599 | 121.5042 | -121.0602 | -121.4996
5432.4844 | 121.344 | -0.42572 | 120.8908 | -0.31242 | 0.016037 | -0.016182 | 0.043733 | 0.030461 | 0.052269 | 0.15791 | -0.059509 | 0.1236 | -0.18768 | 23.2498 | -0.25635 | 39.7385 | -0.16937 | -0.036621 | 121.0602 | -0.59967 | 0.23804 | -120.7672 | 0.36621 | 23.6755 | -121.1472 | -0.17395 | 0.16937 | 0.12817 | 0.25635 | 0.3891 | 0.16937 | 0.54932 | 0.36621 | 121.4859 | 40.1642 | -0.17395 | 0.54932 | 0.36621 | 40.1642 | 0.16937 | 121.4859 | -121.0785 | -121.4905
5434.1875 | 121.4035 | -0.39825 | 120.8862 | 0.053787 | 0.016037 | -0.0084915 | 0.043733 | 0.032383 | 0.05291 | 0.16068 | 0.064087 | 0.07782 | -0.16937 | 23.14 | -0.16937 | 40.416 | -0.39368 | 0.027466 | 121.0648 | -0.57678 | 0.22888 | -120.8084 | 0.46234 | 23.5382 | -121.0556 | -0.17853 | 0.17853 | 0.23346 | 0.004577 | 0.42572 | 0.22888 | 0.47607 | 0.46234 | 121.463 | 40.8142 | -0.17853 | 0.47607 | 0.46234 | 40.8142 | 0.22888 | 121.463 | -121.0556 | -121.463
5435.9531 | 121.4035 | -0.44403 | 120.8633 | 0.046158 | 0.013687 | -0.011482 | 0.048433 | 0.034519 | 0.053124 | 0.15961 | -0.036621 | 0.10986 | -0.19226 | 22.8516 | -0.30212 | 40.5167 | -0.21057 | -0.10986 | 121.1243 | -0.62714 | 0.25177 | -120.7535 | 0.40741 | 23.2956 | -121.1655 | -0.18311 | 0.26093 | 0.15564 | 0.23346 | 0.33417 | 0.14191 | 0.55389 | 0.40741 | 121.5683 | 40.9607 | -0.18311 | 0.55389 | 0.40741 | 40.9607 | 0.14191 | 121.5683 | -121.0556 | -121.4905
5437.7188 | 121.3852 | -0.44403 | 120.9366 | -0.12932 | 0.015182 | -0.016823 | 0.039888 | 0.032597 | 0.05291 | 0.1594 | 0.045776 | 0.068665 | -0.15106 | 23.0026 | -0.11902 | 39.7156 | -0.37079 | 0.086975 | 121.0968 | -0.58136 | 0.29297 | -120.8679 | 0.48981 | 23.4467 | -121.0556 | -0.13733 | 0.16022 | 0.19684 | 0.073242 | 0.53101 | 0.32501 | 0.5127 | 0.48981 | 121.5408 | 40.1596 | -0.13733 | 0.5127 | 0.48981 | 40.1596 | 0.32501 | 121.5408 | -121.0876 | -121.5179
5439.4062 | 121.4172 | -0.43945 | 120.9412 | -0.2285 | 0.015823 | -0.012337 | 0.045655 | 0.02982 | 0.052483 | 0.1609 | -0.045776 | 0.12817 | -0.19684 | 22.76 | -0.27466 | 40.1321 | -0.15106 | -0.027466 | 121.138 | -0.63629 | 0.24261 | -120.813 | 0.39368 | 23.1995 | -121.2158 | -0.19684 | 0.19684 | 0.15106 | 0.28839 | 0.41199 | 0.16479 | 0.56763 | 0.39368 | 121.5775 | 40.5716 | -0.19684 | 0.56763 | 0.39368 | 40.5716 | 0.16479 | 121.5775 | -121.138 | -121.5775
5441.1719 | 121.4539 | -0.41199 | 120.9457 | 0.15297 | 0.015182 | -0.015114 | 0.044374 | 0.033879 | 0.054406 | 0.1594 | 0.032043 | 0.07782 | -0.15106 | 22.5815 | -0.21057 | 39.917 | -0.37079 | 0.027466 | 121.1105 | -0.56763 | 0.26092 | -120.8679 | 0.44403 | 22.9935 | -121.1563 | -0.15564 | 0.16479 | 0.18311 | 0.041198 | 0.43945 | 0.20142 | 0.48981 | 0.44403 | 121.5225 | 40.329 | -0.15564 | 0.48981 | 0.44403 | 40.329 | 0.20142 | 121.5225 | -121.0968 | -121.5134
5442.9375 | 121.3989 | -0.44861 | 120.9686 | -0.060654 | 0.013046 | -0.012337 | 0.048219 | 0.032597 | 0.052269 | 0.16132 | 0.004578 | 0.10071 | -0.1831 | 24.8199 | -0.25635 | 40.3381 | -0.20599 | -0.018311 | 121.1517 | -0.59052 | 0.2655 | -120.8679 | 0.45319 | 25.2686 | -121.225 | -0.14191 | 0.1831 | 0.18768 | 0.24261 | 0.4303 | 0.19226 | 0.54932 | 0.45319 | 121.6003 | 40.7867 | -0.14191 | 0.54932 | 0.45319 | 40.7867 | 0.19226 | 121.6003 | -121.1517 | -121.5591
5444.7188 | 121.4264 | -0.45776 | 120.9732 | -0.068283 | 0.015396 | -0.012978 | 0.048646 | 0.031956 | 0.051628 | 0.16068 | -0.009155 | 0.09613 | -0.18768 | 23.3963 | -0.2655 | 40.1367 | -0.23804 | -0.041199 | 121.1746 | -0.6134 | 0.27008 | -120.8771 | 0.44861 | 23.8541 | -121.2387 | -0.15564 | 0.20142 | 0.17853 | 0.21973 | 0.41657 | 0.19226 | 0.55389 | 0.44861 | 121.6324 | 40.5945 | -0.15564 | 0.55389 | 0.44861 | 40.5945 | 0.19226 | 121.6324 | -121.1609 | -121.5866
5446.4844 | 121.5546 | -0.40283 | 120.9549 | 0.11482 | 0.015396 | -0.011482 | 0.04651 | 0.032383 | 0.053765 | 0.16688 | -0.068665 | 0.12817 | -0.1831 | 23.1216 | -0.29755 | 40.2283 | -0.21057 | -0.10529 | 121.1655 | -0.63171 | 0.21973 | -120.8267 | 0.33417 | 23.5245 | -121.2524 | -0.22888 | 0.21057 | 0.11444 | 0.19226 | 0.29755 | 0.10529 | 0.53101 | 0.33417 | 121.5683 | 40.6311 | -0.22888 | 0.53101 | 0.33417 | 40.6311 | 0.10529 | 121.5683 | -121.138 | -121.5866
5448.1875 | 120.5429 | -119.2291 | 0.86517 | 0.091934 | 0.015182 | -0.011696 | 0.054628 | -0.017177 | -0.015876 | 0.020973 | -0.07782 | 0.13275 | -0.21973 | 0.10529 | 0.33875 | 0.8194 | 0.09613 | 0.19684 | 1.0437 | -119.577 | 119.0094 | -0.73242 | 119.1513 | 119.3344 | -0.52643 | -0.3479 | 0.17853 | 0.14191 | 119.3253 | 119.426 | 119.5679 | 119.3619 | 119.1513 | 120.2728 | 120.0485 | -0.3479 | 119.3619 | 119.1513 | 120.0485 | 119.5679 | 120.2728 | -1.0849 | -120.4422
5449.8906 | 121.0876 | -120.1447 | 0.72784 | -0.030136 | 0.014541 | -0.016396 | 0.055696 | -0.017605 | -0.013313 | 0.020546 | -0.027466 | 0.07782 | -0.19226 | 0.27466 | 0.36621 | 0.59967 | 0.27924 | 0.42114 | 0.86517 | -120.3552 | 119.9524 | -0.65002 | 120.1172 | 120.4193 | -0.36163 | -0.21057 | 0.13733 | 0.16479 | 120.4239 | 120.5658 | 120.5109 | 120.2225 | 120.1172 | 121.0098 | 120.7443 | -0.21057 | 120.2225 | 120.1172 | 120.7443 | 120.5109 | 121.0098 | -0.92011 | -121.0831
5451.6406 | 121.1792 | -120.369 | 0.6546 | -0.13695 | 0.012619 | -0.018959 | 0.045228 | -0.023372 | -0.010536 | 0.018837 | 0.032043 | 0.064087 | -0.15564 | 0.41657 | 0.4715 | 0.61798 | 0.21973 | 0.65918 | 0.74158 | -120.5978 | 120.2133 | -0.59052 | 120.401 | 120.7855 | -0.18311 | -0.22888 | 0.086975 | 0.18768 | 120.5887 | 121.0281 | 120.8405 | 120.433 | 120.401 | 121.1105 | 120.9869 | -0.22888 | 120.433 | 120.401 | 120.9869 | 120.8405 | 121.1105 | -0.81024 | -121.2524
5453.4062 | 121.3577 | -120.4102 | 0.6134 | 0.084305 | 0.014328 | -0.0099869 | 0.055055 | -0.019954 | -0.014381 | 0.021187 | -0.068665 | 0.086975 | -0.22888 | 0.31586 | 0.3479 | 0.48981 | 0.31586 | 0.45776 | 0.78278 | -120.639 | 120.1813 | -0.52643 | 120.3415 | 120.726 | -0.2655 | -0.22888 | 0.16937 | 0.16022 | 120.726 | 120.8679 | 120.7581 | 120.4971 | 120.3415 | 121.1929 | 120.9 | -0.22888 | 120.4971 | 120.3415 | 120.9 | 120.7581 | 121.1929 | -0.84229 | -121.2524
5455.1875 | 121.3806 | -120.1218 | 0.9613 | 0.12245 | 0.015823 | -0.015327 | 0.049501 | -0.018886 | -0.010109 | 0.019905 | 0.013733 | 0.073242 | -0.16479 | 0.38452 | 0.42572 | 0.92468 | 0.22888 | 0.5722 | 1.0757 | -120.369 | 119.957 | -0.88806 | 120.1355 | 120.5063 | -0.53558 | -0.24719 | 0.11444 | 0.17853 | 120.3506 | 120.694 | 120.5475 | 120.195 | 120.1355 | 121.1975 | 121.0464 | -0.24719 | 120.195 | 120.1355 | 121.0464 | 120.5475 | 121.1975 | -1.1261 | -121.3303
5456.8906 | 121.2982 | -120.1035 | 1.0574 | -0.068283 | 0.015182 | -0.0149 | 0.058687 | -0.019314 | -0.015236 | 0.020973 | -0.022888 | 0.091553 | -0.21973 | 0.36163 | 0.36163 | 0.90637 | 0.31586 | 0.52185 | 1.181 | -120.3552 | 119.8837 | -0.96588 | 120.0806 | 120.4651 | -0.6958 | -0.25177 | 0.1236 | 0.19684 | 120.4193 | 120.6253 | 120.4651 | 120.195 | 120.0806 | 121.2845 | 121.0098 | -0.25177 | 120.195 | 120.0806 | 121.0098 | 120.4651 | 121.2845 | -1.2772 | -121.4127
5458.6406 | 121.4447 | -120.4834 | 0.66834 | 0.099564 | 0.014328 | -0.012978 | 0.05655 | -0.020595 | -0.013954 | 0.021828 | -0.10071 | 0.091553 | -0.21057 | 0.31128 | 0.3479 | 0.52643 | 0.33417 | 0.46234 | 0.83771 | -120.726 | 120.2728 | -0.57678 | 120.3827 | 120.7947 | -0.32044 | -0.24262 | 0.16937 | 0.10986 | 120.8176 | 120.9457 | 120.8313 | 120.575 | 120.3827 | 121.3211 | 121.0098 | -0.24262 | 120.575 | 120.3827 | 121.0098 | 120.8313 | 121.3211 | -0.87891 | -121.3943
5460.3438 | 121.3852 | -120.5658 | 0.69122 | -0.15221 | 0.013046 | -0.018318 | 0.050142 | -0.022091 | -0.012031 | 0.023323 | 0.004578 | 0.059509 | -0.19226 | 0.40283 | 0.49439 | 0.6546 | 0.13733 | 0.58594 | 0.76904 | -120.7626 | 120.3735 | -0.63171 | 120.5704 | 120.9686 | -0.19684 | -0.19684 | 0.07782 | 0.19684 | 120.7031 | 121.1517 | 121.0602 | 120.6253 | 120.5704 | 121.3348 | 121.2204 | -0.19684 | 120.6253 | 120.5704 | 121.2204 | 121.0602 | 121.3348 | -0.88348 | -121.4539
5462.125 | 121.4676 | -120.5429 | 0.66376 | 0.076676 | 0.013687 | -0.014473 | 0.056978 | -0.024868 | -0.013313 | 0.023964 | 0.027466 | 0.036621 | -0.17395 | -0.027466 | 0.45319 | 0.65918 | -0.28381 | 0.1236 | 0.75989 | -120.7855 | 120.369 | -0.62714 | 120.5704 | 120.5154 | -0.21057 | -0.24261 | 0.096131 | 0.20142 | 120.2591 | 120.6665 | 120.9961 | 120.5795 | 120.5704 | 121.3028 | 121.2021 | -0.24261 | 120.5795 | 120.5704 | 121.2021 | 120.9961 | 121.3028 | -0.83771 | -121.4493
5463.8281 | 121.4081 | -120.5338 | 0.737 | -0.19035 | 0.011764 | -0.010841 | 0.059114 | -0.021877 | -0.016731 | 0.022042 | -0.054932 | 0.10071 | -0.21515 | 0.23804 | 0.36621 | 0.60883 | 0.15106 | 0.32501 | 0.85144 | -120.7581 | 120.3186 | -0.63629 | 120.4788 | 120.7718 | -0.37079 | -0.2243 | 0.11444 | 0.16022 | 120.6848 | 120.8588 | 120.9 | 120.6345 | 120.4788 | 121.3852 | 121.1426 | -0.2243 | 120.6345 | 120.4788 | 121.1426 | 120.9 | 121.3852 | -0.95215 | -121.4951
5465.5938 | 121.5271 | -120.6116 | 0.61798 | 0.099564 | 0.014755 | -0.0097733 | 0.059541 | -0.020382 | -0.014595 | 0.0261 | -0.064087 | 0.10071 | -0.20599 | 0.17853 | 0.34332 | 0.47607 | 0.11902 | 0.25177 | 0.78278 | -120.9 | 120.4056 | -0.51727 | 120.5475 | 120.7901 | -0.27466 | -0.28839 | 0.1648 | 0.14191 | 120.7306 | 120.8633 | 120.9549 | 120.7123 | 120.5475 | 121.3943 | 121.0876 | -0.28839 | 120.7123 | 120.5475 | 121.0876 | 120.9549 | 121.3943 | -0.82398 | -121.5179
5467.2969 | 121.4722 | -120.6345 | 0.65002 | -0.15221 | 0.012619 | -0.014046 | 0.056337 | -0.022945 | -0.011818 | 0.028237 | 0.032043 | 0.073242 | -0.16937 | 0.27466 | 0.4715 | 0.64087 | -0.054932 | 0.3891 | 0.74616 | -120.8817 | 120.4651 | -0.57678 | 120.6665 | 120.9091 | -0.17853 | -0.24719 | 0.096131 | 0.20142 | 120.5795 | 121.0236 | 121.106 | 120.7077 | 120.6665 | 121.3806 | 121.2753 | -0.24719 | 120.7077 | 120.6665 | 121.2753 | 121.106 | 121.3806 | -0.8194 | -121.5317
5469.0625 | 120.9915 | -102.8915 | 17.5964 | 0.18349 | 0.016678 | -0.015755 | 0.032197 | -0.0075643 | -0.0037 | 0.022469 | -0.027466 | 0.07782 | -0.20599 | 0.59967 | 0.27924 | 0.33417 | 0.38452 | 0.65918 | 17.7063 | -103.244 | 102.6855 | -17.5186 | 102.8641 | 103.4912 | -17.3172 | -0.35248 | 0.10986 | 0.17853 | 103.2761 | 103.5507 | 103.1708 | 102.9694 | 102.8641 | 120.5978 | 103.2257 | -0.35248 | 102.9694 | 102.8641 | 103.2257 | 103.1708 | 120.5978 | -17.8024 | -120.8405
5470.8281 | 121.2891 | -105.1987 | 15.7516 | -0.19798 | 0.014541 | -0.016182 | 0.033052 | -0.014187 | -0.0045544 | 0.021401 | -0.045776 | 0.09613 | -0.21973 | 0.39368 | 0.28381 | 0.28839 | 0.28381 | 0.43945 | 15.8661 | -105.5237 | 104.9789 | -15.6555 | 105.1529 | 105.5923 | -15.4678 | -0.32501 | 0.11444 | 0.17395 | 105.4825 | 105.6381 | 105.4825 | 105.2948 | 105.1529 | 121.0648 | 105.4871 | -0.32501 | 105.2948 | 105.1529 | 105.4871 | 105.4825 | 121.0648 | -15.9714 | -121.2753
5472.5938 | 121.3943 | -104.6906 | 16.3239 | 0.13771 | 0.014541 | -0.015541 | 0.028993 | -0.010128 | -0.0037 | 0.021828 | 0.045776 | 0.036621 | -0.14648 | 0.46234 | 0.37994 | 0.42114 | 0.11902 | 0.54474 | 16.42 | -104.9698 | 104.5441 | -16.2872 | 104.7363 | 105.1529 | -15.9439 | -0.27924 | 0.09613 | 0.19226 | 104.8096 | 105.2353 | 105.0705 | 104.7272 | 104.7363 | 121.1105 | 105.1117 | -0.27924 | 104.7272 | 104.7363 | 105.1117 | 105.0705 | 121.1105 | -16.4703 | -121.2936
5474.3594 | 121.4813 | -104.1275 | 16.9373 | 0.091934 | 0.014328 | -0.01255 | 0.030061 | -0.0144 | -0.0017774 | 0.02311 | 0.004578 | 0.050354 | -0.16937 | 0.45776 | 0.36163 | 0.41657 | 0.17395 | 0.5127 | 17.0609 | -104.4388 | 103.9581 | -16.8869 | 104.1321 | 104.5853 | -16.5756 | -0.31128 | 0.1236 | 0.17395 | 104.3015 | 104.6402 | 104.4891 | 104.1779 | 104.1321 | 121.1884 | 104.5441 | -0.31128 | 104.1779 | 104.1321 | 104.5441 | 104.4891 | 121.1884 | -17.1066 | -121.376
5476.125 | 121.4035 | -104.6173 | 16.571 | -0.22087 | 0.012619 | -0.012123 | 0.032197 | -0.013973 | -0.0051954 | 0.022896 | 0.013733 | 0.082397 | -0.1831 | 0.52185 | 0.37994 | 0.40283 | 0.25635 | 0.56763 | 16.6855 | -104.837 | 104.4342 | -16.4886 | 104.631 | 105.1392 | -16.1911 | -0.21973 | 0.11444 | 0.19684 | 104.8737 | 105.1849 | 104.9973 | 104.6997 | 104.631 | 121.3028 | 105.0201 | -0.21973 | 104.6997 | 104.631 | 105.0201 | 104.9973 | 121.3028 | -16.7542 | -121.4081
5477.8438 | 121.5225 | -105.0659 | 16.0629 | -0.014877 | 0.015182 | -0.014046 | 0.02942 | -0.013546 | -0.0041272 | 0.018837 | -0.004578 | 0.091553 | -0.17853 | 0.50354 | 0.3891 | 0.40283 | 0.1831 | 0.54932 | 16.2003 | -105.336 | 104.8874 | -15.9714 | 105.0613 | 105.5695 | -15.6738 | -0.27008 | 0.13733 | 0.17395 | 105.249 | 105.6152 | 105.455 | 105.1575 | 105.0613 | 121.2662 | 105.4688 | -0.27008 | 105.1575 | 105.0613 | 105.4688 | 105.455 | 121.2662 | -16.2415 | -121.3989
5479.6094 | 121.5637 | -105.5923 | 15.6006 | 0.038529 | 0.014755 | -0.016182 | 0.03647 | -0.014614 | -0.0043408 | 0.020119 | -0.004578 | 0.073242 | -0.17395 | 0.49439 | 0.36621 | 0.39825 | 0.18768 | 0.5127 | 15.7059 | -105.8395 | 105.4184 | -15.5273 | 105.5878 | 106.0867 | -15.2344 | -0.24719 | 0.10529 | 0.16937 | 105.78 | 106.105 | 105.9586 | 105.6656 | 105.5878 | 121.2982 | 105.9906 | -0.24719 | 105.6656 | 105.5878 | 105.9906 | 105.9586 | 121.2982 | -15.7745 | -121.4401
5481.375 | 121.463 | -104.9561 | 16.3055 | -0.12169 | 0.014969 | -0.014687 | 0.032624 | -0.014827 | -0.0043408 | 0.02076 | 0.036621 | 0.068665 | -0.16937 | 0.56763 | 0.43945 | 0.46692 | 0.16022 | 0.61798 | 16.3834 | -105.162 | 104.7867 | -16.2369 | 104.9927 | 105.5237 | -15.8661 | -0.20599 | 0.07782 | 0.20599 | 105.1163 | 105.574 | 105.3955 | 105.0247 | 104.9927 | 121.3394 | 105.423 | -0.20599 | 105.0247 | 104.9927 | 105.423 | 105.3955 | 121.3394 | -16.4749 | -121.4676
5483.1562 | 121.582 | -104.1 | 17.1249 | -0.0072479 | 0.014541 | -0.021522 | 0.033052 | -0.013546 | -0.0017774 | 0.022255 | -0.027466 | 0.082397 | -0.18768 | 0.50812 | 0.3891 | 0.39368 | 0.20599 | 0.53101 | 17.2348 | -104.4022 | 103.9124 | -17.0425 | 104.0726 | 104.6082 | -16.7358 | -0.30212 | 0.10986 | 0.16022 | 104.306 | 104.631 | 104.4891 | 104.1824 | 104.0726 | 121.3348 | 104.4937 | -0.30212 | 104.1824 | 104.0726 | 104.4937 | 104.4891 | 121.3348 | -17.3126 | -121.5271
5484.8594 | 121.55 | -102.626 | 18.5852 | 0.18349 | 0.014541 | -0.013832 | 0.038179 | -0.010341 | -0.0039136 | 0.023964 | 0 | 0.086975 | -0.19226 | 0.5127 | 0.37079 | 0.39825 | 0.16022 | 0.48981 | 18.7271 | -102.8503 | 102.4338 | -18.4982 | 102.626 | 103.1387 | -18.2144 | -0.2243 | 0.14191 | 0.19226 | 102.7863 | 103.1158 | 102.9968 | 102.713 | 102.626 | 121.3531 | 103.0243 | -0.2243 | 102.713 | 102.626 | 103.0243 | 102.9968 | 121.3531 | -18.7775 | -121.4355
5486.625 | 121.2021 | -16.9327 | 104.5166 | -0.12932 | 0.012832 | -0.021309 | 0.036683 | 0.031529 | 0.046288 | 0.14274 | 0.041199 | 0.064087 | -0.16479 | 0.71411 | -0.13733 | -0.10529 | -0.40283 | 0.054932 | 104.5212 | -17.0975 | 16.7679 | -104.4525 | 16.9739 | 17.6468 | -104.6539 | -0.1648 | 0.004577 | 0.20599 | 16.5298 | 16.9876 | 16.7953 | 16.9968 | 16.9739 | 121.4539 | 16.8274 | -0.1648 | 16.9968 | 16.9739 | 16.8274 | 16.7953 | 121.4539 | -104.6814 | -121.6141
5488.3906 | 120.9183 | -10.6064 | 110.8383 | -0.17509 | 0.018173 | -0.016823 | 0.044587 | 0.038151 | 0.043724 | 0.15171 | -0.036621 | 0.09613 | -0.20599 | 0.64087 | -0.27924 | -0.27924 | -0.26093 | -0.10986 | 110.9436 | -10.817 | 10.4004 | -110.7422 | 10.5698 | 11.2473 | -111.1176 | -0.21057 | 0.10529 | 0.16937 | 10.3455 | 10.4965 | 10.3271 | 10.7025 | 10.5698 | 121.55 | 10.3271 | -0.21057 | 10.7025 | 10.5698 | 10.3271 | 10.3271 | 121.55 | -111.0443 | -121.6553
5490.1562 | 121.3394 | -9.4849 | 111.9278 | -0.17509 | 0.016037 | -0.0149 | 0.045015 | 0.039433 | 0.048851 | 0.15321 | -0.032043 | 0.1236 | -0.20142 | 0.63171 | -0.28381 | -0.27466 | -0.25635 | -0.11444 | 112.1017 | -9.6954 | 9.2834 | -111.8042 | 9.4528 | 10.1166 | -112.2116 | -0.21057 | 0.17395 | 0.16937 | 9.2285 | 9.3704 | 9.2011 | 9.6085 | 9.4528 | 121.5866 | 9.2102 | -0.21057 | 9.6085 | 9.4528 | 9.2102 | 9.2011 | 121.5866 | -112.1292 | -121.6232
5491.8594 | 121.4996 | -9.0775 | 112.3718 | -0.22087 | 0.012832 | -0.013191 | 0.042238 | 0.038365 | 0.047783 | 0.15449 | -0.068665 | 0.10986 | -0.20599 | 0.62714 | -0.3067 | -0.27924 | -0.22888 | -0.12817 | 112.5183 | -9.288 | 8.8715 | -112.262 | 9.0088 | 9.7046 | -112.6785 | -0.21057 | 0.14648 | 0.13733 | 8.8486 | 8.9493 | 8.7708 | 9.1873 | 9.0088 | 121.5958 | 8.7982 | -0.21057 | 9.1873 | 9.0088 | 8.7982 | 8.7708 | 121.5958 | -112.5778 | -121.6599
5493.6094 | 121.4722 | -8.7891 | 112.6785 | -0.21324 | 0.013687 | -0.015755 | 0.036683 | 0.038578 | 0.048638 | 0.15449 | 0.036621 | 0.073242 | -0.17853 | 0.73242 | -0.1831 | -0.15564 | -0.40283 | -0.004578 | 112.7792 | -8.9447 | 8.6105 | -112.6053 | 8.8257 | 9.5215 | -112.8616 | -0.15564 | 0.10071 | 0.21515 | 8.3862 | 8.7845 | 8.606 | 8.8623 | 8.8257 | 121.5683 | 8.6334 | -0.15564 | 8.8623 | 8.8257 | 8.6334 | 8.606 | 121.5683 | -112.8571 | -121.6232
5495.3906 | 121.5958 | -9.4711 | 111.9598 | 0.10719 | 0.014541 | -0.013832 | 0.042665 | 0.039433 | 0.051415 | 0.15299 | -0.041199 | 0.11444 | -0.19684 | 0.60425 | -0.29755 | -0.27008 | -0.29755 | -0.15106 | 112.1567 | -9.6909 | 9.2743 | -111.8454 | 9.4299 | 10.0754 | -112.2574 | -0.21973 | 0.19684 | 0.15564 | 9.1736 | 9.3201 | 9.1736 | 9.5856 | 9.4299 | 121.6278 | 9.201 | -0.21973 | 9.5856 | 9.4299 | 9.201 | 9.1736 | 121.6278 | -112.1567 | -121.6507
5497.0938 | 121.5912 | -8.8028 | 112.619 | 0.061417 | 0.016891 | -0.015327 | 0.042238 | 0.042423 | 0.045861 | 0.15363 | -0.064087 | 0.10071 | -0.21973 | 0.54474 | -0.32959 | -0.29297 | -0.26093 | -0.18768 | 112.8662 | -9.0225 | 8.5831 | -112.5183 | 8.7387 | 9.3475 | -112.9486 | -0.21973 | 0.24719 | 0.15564 | 8.5419 | 8.6151 | 8.4732 | 8.9035 | 8.7387 | 121.669 | 8.5098 | -0.21973 | 8.9035 | 8.7387 | 8.5098 | 8.4732 | 121.669 | -112.8387 | -121.6415
5498.8594 | 121.582 | -8.67 | 112.793 | 0.27504 | 0.015823 | -0.0084915 | 0.041169 | 0.04221 | 0.05056 | 0.15641 | 0.064087 | 0.091553 | -0.16479 | 0.64087 | -0.20599 | -0.15106 | -0.45776 | -0.045776 | 112.9257 | -8.844 | 8.5052 | -112.7014 | 8.7341 | 9.3109 | -112.999 | -0.17395 | 0.13275 | 0.22888 | 8.2123 | 8.6243 | 8.4641 | 8.7616 | 8.7341 | 121.5958 | 8.519 | -0.17395 | 8.7616 | 8.7341 | 8.519 | 8.4641 | 121.5958 | -112.9578 | -121.637
5500.625 | 121.6507 | -8.4274 | 113.0127 | 0.10719 | 0.015396 | -0.014046 | 0.04651 | 0.043064 | 0.047997 | 0.15769 | -0.059509 | 0.10071 | -0.23346 | 0.54474 | -0.31586 | -0.28381 | -0.29755 | -0.17395 | 113.2233 | -8.67 | 8.194 | -112.912 | 8.3679 | 8.9722 | -113.3286 | -0.24262 | 0.21057 | 0.17395 | 8.1299 | 8.2535 | 8.1116 | 8.5281 | 8.3679 | 121.6507 | 8.1436 | -0.24262 | 8.5281 | 8.3679 | 8.1436 | 8.1116 | 121.6507 | -113.2462 | -121.6827
5502.3906 | 121.6324 | -8.4503 | 112.999 | 0.13771 | 0.014328 | -0.013405 | 0.041169 | 0.041783 | 0.050133 | 0.15855 | 0.022888 | 0.07782 | -0.16479 | 0.6134 | -0.21973 | -0.16937 | -0.44861 | -0.045776 | 113.1729 | -8.6334 | 8.2855 | -112.9211 | 8.4732 | 9.0637 | -113.2187 | -0.18311 | 0.17395 | 0.18768 | 8.0017 | 8.4045 | 8.2306 | 8.5281 | 8.4732 | 121.6232 | 8.2809 | -0.18311 | 8.5281 | 8.4732 | 8.2809 | 8.2306 | 121.6232 | -113.1638 | -121.6324
5504.1562 | 121.582 | -8.1894 | 113.3469 | -0.23613 | 0.015396 | -0.016609 | 0.040101 | 0.03751 | 0.047142 | 0.15855 | 0.004578 | 0.068665 | -0.17395 | 0.58136 | -0.21515 | -0.19684 | -0.31586 | -0.064087 | 113.4842 | -8.3588 | 8.0154 | -113.2782 | 8.194 | 8.7708 | -113.562 | -0.16937 | 0.13733 | 0.17853 | 7.8735 | 8.1253 | 7.9742 | 8.2581 | 8.194 | 121.6736 | 7.9926 | -0.16937 | 8.2581 | 8.194 | 7.9926 | 7.9742 | 121.6736 | -113.5208 | -121.7056
5505.8594 | 121.7056 | -8.1345 | 113.3194 | 0.038529 | 0.014541 | -0.013405 | 0.03946 | 0.03986 | 0.051628 | 0.15876 | 0 | 0.082397 | -0.16937 | 0.50354 | -0.22888 | -0.17395 | -0.40283 | -0.073242 | 113.5071 | -8.3588 | 7.9651 | -113.237 | 8.1345 | 8.638 | -113.5483 | -0.2243 | 0.18768 | 0.16937 | 7.7316 | 8.0612 | 7.9056 | 8.2169 | 8.1345 | 121.6415 | 7.9605 | -0.2243 | 8.2169 | 8.1345 | 7.9605 | 7.9056 | 121.6415 | -113.4888 | -121.6782
5507.625 | 121.5958 | -7.9376 | 113.5849 | -0.083542 | 0.014114 | -0.015968 | 0.047578 | 0.040715 | 0.047142 | 0.15791 | 0.004578 | 0.086975 | -0.20142 | 0.54016 | -0.28839 | -0.23346 | -0.31128 | -0.10071 | 113.7543 | -8.1207 | 7.7362 | -113.4979 | 7.9422 | 8.4778 | -113.8733 | -0.18311 | 0.16937 | 0.20599 | 7.6263 | 7.8369 | 7.6492 | 8.0246 | 7.9422 | 121.6919 | 7.7042 | -0.18311 | 8.0246 | 7.9422 | 7.7042 | 7.6492 | 121.6919 | -113.7863 | -121.7056
5509.3281 | 121.6095 | -7.8049 | 113.7497 | -0.13695 | 0.014969 | -0.015327 | 0.03946 | 0.037724 | 0.050347 | 0.16047 | 0.045776 | 0.082397 | -0.17395 | 0.60425 | -0.17853 | -0.14191 | -0.4303 | 0.018311 | 113.8504 | -7.9834 | 7.6309 | -113.6673 | 7.8506 | 8.4091 | -113.9282 | -0.17853 | 0.10071 | 0.21973 | 7.3746 | 7.8232 | 7.6263 | 7.8873 | 7.8506 | 121.6553 | 7.663 | -0.17853 | 7.8873 | 7.8506 | 7.663 | 7.6263 | 121.6553 | -113.9236 | -121.7331
5511.1094 | 121.6003 | -7.7408 | 113.8687 | -0.15984 | 0.014541 | -0.015968 | 0.041169 | 0.040074 | 0.050133 | 0.1594 | 0.064087 | 0.07782 | -0.16022 | 0.57678 | -0.18768 | -0.15106 | -0.41199 | 0 | 114.0015 | -7.8827 | 7.5806 | -113.7909 | 7.8049 | 8.3176 | -114.0564 | -0.14191 | 0.13275 | 0.2243 | 7.3288 | 7.7408 | 7.5531 | 7.8186 | 7.8049 | 121.7422 | 7.5897 | -0.14191 | 7.8186 | 7.8049 | 7.5897 | 7.5531 | 121.7422 | -114.0289 | -121.7514
5512.8125 | 121.7514 | -7.6859 | 113.7955 | 0.02327 | 0.013473 | -0.01255 | 0.042024 | 0.040074 | 0.050133 | 0.15876 | -0.009155 | 0.07782 | -0.16479 | 0.54932 | -0.23804 | -0.19684 | -0.40283 | -0.054932 | 113.9969 | -7.901 | 7.5211 | -113.7177 | 7.6767 | 8.2352 | -114.0335 | -0.21515 | 0.20142 | 0.15564 | 7.283 | 7.6309 | 7.4478 | 7.7637 | 7.6767 | 121.6827 | 7.489 | -0.21515 | 7.7637 | 7.6767 | 7.489 | 7.4478 | 121.6827 | -113.9603 | -121.6965
5514.5781 | 121.6324 | -7.5943 | 114.0335 | -0.17509 | 0.012191 | -0.017464 | 0.042024 | 0.040715 | 0.052056 | 0.15705 | 0.064087 | 0.086975 | -0.16937 | 0.59052 | -0.18768 | -0.15106 | -0.41199 | 0.018311 | 114.1571 | -7.7133 | 7.4249 | -113.9465 | 7.6584 | 8.1848 | -114.2212 | -0.11902 | 0.1236 | 0.23346 | 7.1823 | 7.6126 | 7.4066 | 7.6813 | 7.6584 | 121.7514 | 7.4432 | -0.11902 | 7.6813 | 7.6584 | 7.4432 | 7.4066 | 121.7514 | -114.2029 | -121.7468
5516.3438 | 121.637 | -7.4799 | 114.1113 | -0.15221 | 0.013687 | -0.014687 | 0.045228 | 0.041783 | 0.046288 | 0.15897 | -0.004578 | 0.10529 | -0.21973 | 0.53101 | -0.2655 | -0.23804 | -0.30212 | -0.091553 | 114.2761 | -7.6584 | 7.2601 | -114.006 | 7.4753 | 8.0109 | -114.3768 | -0.17853 | 0.16479 | 0.21515 | 7.1777 | 7.3883 | 7.2144 | 7.5851 | 7.4753 | 121.756 | 7.2418 | -0.17853 | 7.5851 | 7.4753 | 7.2418 | 7.2144 | 121.756 | -114.3311 | -121.7697
5518.1094 | 121.6965 | -7.4158 | 114.1251 | -0.14458 | 0.013687 | -0.015541 | 0.04181 | 0.040074 | 0.051201 | 0.15961 | 0.041199 | 0.064087 | -0.16937 | 0.58594 | -0.16937 | -0.13275 | -0.42572 | 0.018311 | 114.299 | -7.608 | 7.2464 | -114.061 | 7.457 | 8.0017 | -114.2944 | -0.19226 | 0.17395 | 0.21057 | 6.9901 | 7.4341 | 7.2464 | 7.4799 | 7.457 | 121.7148 | 7.283 | -0.19226 | 7.4799 | 7.457 | 7.283 | 7.2464 | 121.7148 | -114.2944 | -121.7331
5519.875 | 121.6919 | -7.3975 | 114.2075 | -0.15221 | 0.013473 | -0.016396 | 0.039674 | 0.040501 | 0.050347 | 0.1609 | 0.054932 | 0.068665 | -0.14648 | 0.58136 | -0.17395 | -0.14191 | -0.43945 | 0.013733 | 114.3677 | -7.5668 | 7.251 | -114.1388 | 7.4524 | 7.9788 | -114.3814 | -0.16937 | 0.16022 | 0.20142 | 6.958 | 7.4112 | 7.2235 | 7.4661 | 7.4524 | 121.7651 | 7.2556 | -0.16937 | 7.4661 | 7.4524 | 7.2556 | 7.2235 | 121.7651 | -114.3539 | -121.7743
5521.6562 | 121.0968 | -5.0446 | 115.9241 | 0.16823 | 0.016037 | -0.013191 | 0.045655 | 0.044132 | 0.05056 | 0.16602 | 0.027466 | 0.082397 | -0.19684 | 0.19226 | -0.25635 | -0.19684 | -0.45319 | -0.082397 | 116.0568 | -5.2368 | 4.8477 | -115.8417 | 5.072 | 5.2368 | -116.1804 | -0.19226 | 0.13275 | 0.2243 | 4.5914 | 4.9622 | 4.7882 | 5.127 | 5.072 | 121.1014 | 4.8477 | -0.19226 | 5.127 | 5.072 | 4.8477 | 4.7882 | 121.1014 | -116.1209 | -121.1609
5523.4219 | 121.3486 | -3.772 | 117.4118 | 0.10719 | 0.01625 | -0.015755 | 0.047792 | 0.043064 | 0.052483 | 0.17051 | -0.041199 | 0.10529 | -0.20599 | 0.12817 | -0.31586 | -0.28381 | -0.36621 | -0.17853 | 117.5674 | -4.0009 | 3.566 | -117.3065 | 3.7308 | 3.9001 | -117.7277 | -0.22888 | 0.15564 | 0.1648 | 3.4058 | 3.5934 | 3.4561 | 3.8773 | 3.7308 | 121.3394 | 3.4882 | -0.22888 | 3.8773 | 3.7308 | 3.4882 | 3.4561 | 121.3394 | -117.6178 | -121.4127
5525.1875 | 121.3577 | -3.7537 | 117.5858 | -0.18272 | 0.015609 | -0.011696 | 0.04651 | 0.044132 | 0.052697 | 0.16944 | -0.059509 | 0.10529 | -0.21515 | 0.13275 | -0.32044 | -0.3067 | -0.26093 | -0.15106 | 117.7231 | -3.9551 | 3.5385 | -117.4805 | 3.6942 | 3.8864 | -117.9062 | -0.20142 | 0.13733 | 0.15564 | 3.4927 | 3.6026 | 3.4332 | 3.8589 | 3.6942 | 121.4767 | 3.447 | -0.20142 | 3.8589 | 3.6942 | 3.447 | 3.4332 | 121.4767 | -117.8009 | -121.5408
5526.9531 | 121.4584 | -4.2709 | 117.0731 | 0.1606 | 0.014328 | -0.012123 | 0.04651 | 0.043278 | 0.051842 | 0.17094 | 0.050354 | 0.059509 | -0.14648 | 0.21515 | -0.21973 | -0.16022 | -0.50354 | -0.059509 | 117.1783 | -4.4495 | 4.1245 | -117.0135 | 4.3213 | 4.4861 | -117.2928 | -0.17853 | 0.10529 | 0.19684 | 3.7674 | 4.2114 | 4.0512 | 4.3304 | 4.3213 | 121.4493 | 4.1107 | -0.17853 | 4.3304 | 4.3213 | 4.1107 | 4.0512 | 121.4493 | -117.2195 | -121.5225
5528.6562 | 121.4035 | -4.0237 | 117.4393 | -0.15984 | 0.0139 | -0.013618 | 0.048433 | 0.042637 | 0.05056 | 0.16837 | -0.022888 | 0.086975 | -0.21515 | 0.20599 | -0.29755 | -0.25635 | -0.32959 | -0.11902 | 117.54 | -4.184 | 3.8086 | -117.3523 | 4.0009 | 4.2297 | -117.7368 | -0.16022 | 0.10071 | 0.19226 | 3.6942 | 3.9047 | 3.7262 | 4.1107 | 4.0009 | 121.5637 | 3.7674 | -0.16022 | 4.1107 | 4.0009 | 3.7674 | 3.7262 | 121.5637 | -117.6544 | -121.6232
5530.4062 | 121.5454 | -3.7949 | 117.5949 | 0.061417 | 0.015396 | -0.016609 | 0.048219 | 0.044346 | 0.049706 | 0.17158 | -0.073242 | 0.10986 | -0.20599 | 0.18768 | -0.33875 | -0.29755 | -0.27466 | -0.21515 | 117.7963 | -4.0237 | 3.5889 | -117.485 | 3.7216 | 3.9825 | -117.9337 | -0.22888 | 0.20142 | 0.13275 | 3.5202 | 3.5797 | 3.4561 | 3.9047 | 3.7216 | 121.5912 | 3.4973 | -0.22888 | 3.9047 | 3.7216 | 3.4973 | 3.4561 | 121.5912 | -117.8009 | -121.6187
5532.1719 | 121.6278 | -3.392 | 118.0161 | 0.0080111 | 0.011764 | -0.016396 | 0.038179 | 0.04221 | 0.053124 | 0.1703 | -0.022888 | 0.082397 | -0.15106 | 0.2655 | -0.26093 | -0.20599 | -0.3891 | -0.10529 | 118.1992 | -3.6026 | 3.241 | -117.9337 | 3.3691 | 3.6575 | -118.277 | -0.21057 | 0.18311 | 0.12817 | 3.0029 | 3.2867 | 3.1311 | 3.4744 | 3.3691 | 121.5912 | 3.186 | -0.21057 | 3.4744 | 3.3691 | 3.186 | 3.1311 | 121.5912 | -118.1671 | -121.6187
5533.9375 | 121.5454 | -3.3829 | 118.1213 | -0.24376 | 0.015609 | -0.012123 | 0.04651 | 0.041569 | 0.051842 | 0.16923 | -0.018311 | 0.086975 | -0.19226 | 0.27008 | -0.3067 | -0.27924 | -0.26093 | -0.13275 | 118.3044 | -3.5706 | 3.1906 | -118.0344 | 3.3646 | 3.653 | -118.428 | -0.18768 | 0.18311 | 0.17395 | 3.1219 | 3.2501 | 3.0762 | 3.4698 | 3.3646 | 121.6873 | 3.1036 | -0.18768 | 3.4698 | 3.3646 | 3.1036 | 3.0762 | 121.6873 | -118.3136 | -121.6919
5535.6875 | 121.5088 | -3.2913 | 118.2678 | -0.15984 | 0.017318 | -0.013832 | 0.051851 | 0.044132 | 0.052483 | 0.17051 | 0.004578 | 0.11444 | -0.20599 | 0.29755 | -0.28839 | -0.25177 | -0.3067 | -0.10529 | 118.428 | -3.4653 | 3.0853 | -118.1534 | 3.2959 | 3.5889 | -118.5562 | -0.17395 | 0.16022 | 0.21057 | 2.9846 | 3.186 | 3.0029 | 3.4058 | 3.2959 | 121.7194 | 3.0396 | -0.17395 | 3.4058 | 3.2959 | 3.0396 | 3.0029 | 121.7194 | -118.4738 | -121.7331
5537.3906 | 121.637 | -3.2364 | 118.277 | -0.098801 | 0.013687 | -0.016823 | 0.041597 | 0.043278 | 0.054619 | 0.17307 | 0 | 0.07782 | -0.14648 | 0.3479 | -0.20142 | -0.16022 | -0.41657 | -0.018311 | 118.4097 | -3.4103 | 3.0899 | -118.1992 | 3.2364 | 3.5843 | -118.4784 | -0.17395 | 0.13275 | 0.14648 | 2.8198 | 3.2181 | 3.035 | 3.3142 | 3.2364 | 121.6461 | 3.0762 | -0.17395 | 3.3142 | 3.2364 | 3.0762 | 3.035 | 121.6461 | -118.4235 | -121.6873
5539.1562 | 121.5637 | -3.1952 | 118.3502 | -0.10643 | 0.014114 | -0.010841 | 0.051637 | 0.042851 | 0.050347 | 0.17201 | 0.004578 | 0.082397 | -0.20142 | 0.32501 | -0.28381 | -0.25177 | -0.32044 | -0.1236 | 118.515 | -3.4012 | 2.9938 | -118.2678 | 3.1998 | 3.5202 | -118.634 | -0.20599 | 0.1648 | 0.20599 | 2.8748 | 3.0716 | 2.9114 | 3.2776 | 3.1998 | 121.7102 | 2.9434 | -0.20599 | 3.2776 | 3.1998 | 2.9434 | 2.9114 | 121.7102 | -118.5516 | -121.7514
5540.8594 | 121.7239 | -3.1448 | 118.3456 | 0.0080111 | 0.01326 | -0.012123 | 0.042878 | 0.042851 | 0.05526 | 0.17457 | -0.027466 | 0.064087 | -0.16022 | 0.32044 | -0.26093 | -0.20599 | -0.37994 | -0.086975 | 118.5059 | -3.3646 | 2.9846 | -118.2816 | 3.1174 | 3.4653 | -118.6066 | -0.21973 | 0.16022 | 0.13275 | 2.7649 | 3.0579 | 2.8839 | 3.2089 | 3.1174 | 121.6507 | 2.9388 | -0.21973 | 3.2089 | 3.1174 | 2.9388 | 2.8839 | 121.6507 | -118.5059 | -121.7102
5542.6562 | 121.6599 | -3.3646 | 118.19 | 0.10719 | 0.017105 | -0.012764 | 0.052705 | 0.045628 | 0.051415 | 0.17158 | -0.050354 | 0.091553 | -0.20599 | 0.27008 | -0.3479 | -0.31586 | -0.28381 | -0.19226 | 118.4097 | -3.5751 | 3.1586 | -118.0984 | 3.3142 | 3.6346 | -118.5379 | -0.21057 | 0.21973 | 0.15564 | 3.0808 | 3.1723 | 3.0167 | 3.4561 | 3.3142 | 121.7743 | 3.0487 | -0.21057 | 3.4561 | 3.3142 | 3.0487 | 3.0167 | 121.7743 | -118.396 | -121.7651
5544.3594 | 121.6232 | -3.4012 | 118.2083 | -0.21324 | 0.013473 | -0.014259 | 0.040742 | 0.04221 | 0.051201 | 0.16923 | 0.041199 | 0.073242 | -0.16022 | 0.38452 | -0.21057 | -0.15564 | -0.41199 | 0.013733 | 118.3594 | -3.5248 | 3.241 | -118.1351 | 3.4424 | 3.7857 | -118.4189 | -0.1236 | 0.15106 | 0.20142 | 2.9892 | 3.4149 | 3.1906 | 3.4744 | 3.4424 | 121.7606 | 3.2455 | -0.1236 | 3.4744 | 3.4424 | 3.2455 | 3.1906 | 121.7606 | -118.3685 | -121.7331
5546.125 | 121.6415 | -3.392 | 118.2404 | -0.17509 | 0.017318 | -0.0149 | 0.049714 | 0.043278 | 0.049919 | 0.17179 | -0.054932 | 0.1236 | -0.21057 | 0.27924 | -0.32044 | -0.28381 | -0.25635 | -0.11444 | 118.4143 | -3.5751 | 3.1815 | -118.1168 | 3.3371 | 3.6713 | -118.5608 | -0.1831 | 0.17395 | 0.15564 | 3.1357 | 3.2776 | 3.0716 | 3.5156 | 3.3371 | 121.8063 | 3.1082 | -0.1831 | 3.5156 | 3.3371 | 3.1082 | 3.0716 | 121.8063 | -118.4509 | -121.8155
5547.8906 | 121.6919 | -3.392 | 118.2312 | -0.24376 | 0.016037 | -0.019173 | 0.046937 | 0.043492 | 0.050774 | 0.1703 | -0.064087 | 0.10071 | -0.19684 | 0.2655 | -0.32501 | -0.30212 | -0.23346 | -0.15106 | 118.428 | -3.598 | 3.1952 | -118.1305 | 3.3279 | 3.6575 | -118.5562 | -0.20599 | 0.19684 | 0.13275 | 3.1586 | 3.241 | 3.067 | 3.4927 | 3.3279 | 121.8201 | 3.0899 | -0.20599 | 3.4927 | 3.3279 | 3.0899 | 3.067 | 121.8201 | -118.428 | -121.8292
5549.6406 | 121.6507 | -3.3966 | 118.2541 | -0.20561 | 0.015609 | -0.018532 | 0.049714 | 0.044987 | 0.051415 | 0.1703 | -0.027466 | 0.10529 | -0.21515 | 0.3067 | -0.30212 | -0.24719 | -0.28839 | -0.11902 | 118.4418 | -3.5797 | 3.1815 | -118.1488 | 3.3691 | 3.7033 | -118.5562 | -0.18311 | 0.18768 | 0.18768 | 3.1082 | 3.2776 | 3.0945 | 3.5019 | 3.3691 | 121.8384 | 3.1494 | -0.18311 | 3.5019 | 3.3691 | 3.1494 | 3.0945 | 121.8384 | -118.4692 | -121.8338
5551.4062 | 121.7926 | -3.3325 | 118.2587 | 0.076676 | 0.012619 | -0.015968 | 0.048005 | 0.043919 | 0.051628 | 0.17094 | -0.059509 | 0.10529 | -0.20599 | 0.26093 | -0.33417 | -0.29297 | -0.33875 | -0.16937 | 118.4326 | -3.5522 | 3.1265 | -118.1534 | 3.273 | 3.5934 | -118.5928 | -0.21973 | 0.17395 | 0.14649 | 2.9938 | 3.1631 | 2.9984 | 3.4378 | 3.273 | 121.7651 | 3.0396 | -0.21973 | 3.4378 | 3.273 | 3.0396 | 2.9984 | 121.7651 | -118.4647 | -121.8109
5553.1875 | 121.6827 | -3.3737 | 118.2953 | -0.045395 | 0.013687 | -0.014046 | 0.048219 | 0.043064 | 0.051415 | 0.17286 | 0.004578 | 0.086975 | -0.21057 | 0.28839 | -0.31586 | -0.27008 | -0.31128 | -0.14191 | 118.483 | -3.5522 | 3.1631 | -118.2083 | 3.3783 | 3.6621 | -118.6111 | -0.17853 | 0.18768 | 0.21515 | 3.0624 | 3.2318 | 3.0579 | 3.4607 | 3.3783 | 121.8567 | 3.1036 | -0.17853 | 3.4607 | 3.3783 | 3.1036 | 3.0579 | 121.8567 | -118.5059 | -121.8475
5554.9531 | 121.7834 | -3.2135 | 118.364 | -0.060654 | 0.013046 | -0.016182 | 0.03946 | 0.043705 | 0.05526 | 0.17243 | -0.022888 | 0.07782 | -0.16479 | 0.32959 | -0.23346 | -0.18768 | -0.40283 | -0.036621 | 118.5654 | -3.4332 | 3.0487 | -118.2861 | 3.1906 | 3.5431 | -118.5974 | -0.21973 | 0.20142 | 0.14191 | 2.8107 | 3.1769 | 2.98 | 3.2913 | 3.1906 | 121.7789 | 3.0258 | -0.21973 | 3.2913 | 3.1906 | 3.0258 | 2.98 | 121.7789 | -118.5287 | -121.7972
5556.6562 | 121.6827 | -3.2547 | 118.4189 | -0.19035 | 0.014969 | -0.018318 | 0.043519 | 0.044346 | 0.055046 | 0.17051 | 0.07782 | 0.045776 | -0.16479 | 0.3891 | -0.21515 | -0.16479 | -0.42114 | -0.009155 | 118.6157 | -3.3829 | 3.0899 | -118.3731 | 3.3325 | 3.6438 | -118.634 | -0.12817 | 0.19684 | 0.24261 | 2.8336 | 3.2455 | 3.0396 | 3.3005 | 3.3325 | 121.8704 | 3.0899 | -0.12817 | 3.3005 | 3.3325 | 3.0899 | 3.0396 | 121.8704 | -118.5837 | -121.8018
5558.4062 | 121.6599 | -3.1998 | 118.5059 | -0.11406 | 0.013473 | -0.01725 | 0.051637 | 0.043705 | 0.053337 | 0.17201 | 0.009155 | 0.10071 | -0.19684 | 0.34332 | -0.30212 | -0.25635 | -0.32959 | -0.09613 | 118.6752 | -3.3737 | 3.0029 | -118.4052 | 3.2089 | 3.5431 | -118.808 | -0.17395 | 0.16937 | 0.20599 | 2.8702 | 3.1036 | 2.8976 | 3.3005 | 3.2089 | 121.875 | 2.9434 | -0.17395 | 3.3005 | 3.2089 | 2.9434 | 2.8976 | 121.875 | -118.7027 | -121.8796
5560.1719 | 121.7422 | -3.1631 | 118.515 | -0.2285 | 0.012619 | -0.016182 | 0.044374 | 0.041355 | 0.05291 | 0.17094 | -0.032043 | 0.11444 | -0.1831 | 0.30212 | -0.32044 | -0.29755 | -0.25177 | -0.11444 | 118.721 | -3.3646 | 2.98 | -118.4006 | 3.1311 | 3.4653 | -118.8355 | -0.20142 | 0.20599 | 0.15106 | 2.9114 | 3.0487 | 2.8427 | 3.2776 | 3.1311 | 121.8842 | 2.8656 | -0.20142 | 3.2776 | 3.1311 | 2.8656 | 2.8427 | 121.8842 | -118.6981 | -121.8796
5561.875 | 121.7194 | -3.1998 | 118.5287 | -0.14458 | 0.012405 | -0.015541 | 0.044587 | 0.043705 | 0.051415 | 0.16966 | 0.054932 | 0.068665 | -0.15564 | 0.41657 | -0.21057 | -0.13733 | -0.45319 | 0.004578 | 118.6798 | -3.3279 | 3.0441 | -118.4601 | 3.2547 | 3.6163 | -118.7393 | -0.12817 | 0.15106 | 0.21057 | 2.7466 | 3.2043 | 2.9892 | 3.2684 | 3.2547 | 121.8796 | 3.0624 | -0.12817 | 3.2684 | 3.2547 | 3.0624 | 2.9892 | 121.8796 | -118.6844 | -121.8567
5563.625 | 121.7056 | -3.1311 | 118.5791 | -0.15984 | 0.012619 | -0.015114 | 0.045228 | 0.041142 | 0.053551 | 0.16987 | 0.041199 | 0.064087 | -0.16022 | 0.53558 | -0.21515 | -0.16479 | -0.43945 | 0.004578 | 118.7119 | -3.273 | 2.9709 | -118.515 | 3.1723 | 3.6667 | -118.7943 | -0.14191 | 0.13275 | 0.20142 | 2.6917 | 3.1357 | 2.916 | 3.1952 | 3.1723 | 121.843 | 2.9663 | -0.14191 | 3.1952 | 3.1723 | 2.9663 | 2.916 | 121.843 | -118.7393 | -121.8521
5565.3438 | 121.8155 | -3.0991 | 118.5699 | 0.038529 | 0.017532 | -0.0149 | 0.052919 | 0.045628 | 0.051201 | 0.17072 | -0.050354 | 0.10529 | -0.21057 | 0.37537 | -0.36621 | -0.32044 | -0.27924 | -0.20142 | 118.7988 | -3.3051 | 2.8885 | -118.4647 | 3.0487 | 3.4744 | -118.9362 | -0.20599 | 0.22888 | 0.16022 | 2.8198 | 2.8976 | 2.7328 | 3.2043 | 3.0487 | 121.8979 | 2.7786 | -0.20599 | 3.2043 | 3.0487 | 2.7786 | 2.7328 | 121.8979 | -118.7805 | -121.875
5567.1094 | 121.756 | -3.1128 | 118.6066 | -0.14458 | 0.016464 | -0.016396 | 0.043306 | 0.043919 | 0.054192 | 0.17136 | 0.041199 | 0.073242 | -0.16022 | 0.49439 | -0.21057 | -0.15106 | -0.44861 | 0.009155 | 118.7576 | -3.2913 | 2.9526 | -118.5333 | 3.154 | 3.6072 | -118.8171 | -0.17853 | 0.15106 | 0.20142 | 2.6642 | 3.1219 | 2.9022 | 3.186 | 3.154 | 121.8704 | 2.9617 | -0.17853 | 3.186 | 3.154 | 2.9617 | 2.9022 | 121.8704 | -118.7668 | -121.8979
5568.8594 | 121.7743 | -3.0991 | 118.6203 | -0.28191 | 0.012832 | -0.014687 | 0.045228 | 0.043278 | 0.054833 | 0.17158 | 0.009155 | 0.086975 | -0.17395 | 0.44861 | -0.27008 | -0.20599 | -0.31128 | -0.068665 | 118.7759 | -3.2684 | 2.9251 | -118.5333 | 3.1082 | 3.5477 | -118.8904 | -0.16937 | 0.15564 | 0.1831 | 2.7878 | 3.0304 | 2.829 | 3.186 | 3.1082 | 121.875 | 2.8931 | -0.16937 | 3.186 | 3.1082 | 2.8931 | 2.829 | 121.875 | -118.7943 | -121.8887
5570.625 | 121.788 | -3.1219 | 118.5928 | 0.038529 | 0.015609 | -0.015755 | 0.050996 | 0.045414 | 0.050774 | 0.17265 | -0.032043 | 0.10071 | -0.21057 | 0.39825 | -0.35248 | -0.28381 | -0.28839 | -0.16479 | 118.8126 | -3.3051 | 2.9114 | -118.4921 | 3.0899 | 3.5202 | -118.9453 | -0.18311 | 0.21973 | 0.17853 | 2.8336 | 2.9572 | 2.7695 | 3.2227 | 3.0899 | 121.9345 | 2.8381 | -0.18311 | 3.2227 | 3.0899 | 2.8381 | 2.7695 | 121.9345 | -118.8034 | -121.8979
5572.3281 | 121.8842 | -3.1952 | 118.4738 | -0.0072479 | 0.014114 | -0.011909 | 0.040315 | 0.043705 | 0.053124 | 0.17136 | -0.018311 | 0.07782 | -0.17395 | 0.46234 | -0.27008 | -0.16937 | -0.37079 | -0.045776 | 118.6798 | -3.4195 | 3.0212 | -118.396 | 3.1769 | 3.6575 | -118.7439 | -0.2243 | 0.20599 | 0.15564 | 2.8244 | 3.1494 | 2.9251 | 3.273 | 3.1769 | 121.875 | 3.0258 | -0.2243 | 3.273 | 3.1769 | 3.0258 | 2.9251 | 121.875 | -118.6478 | -121.8933
5574.1094 | 121.8246 | -3.2272 | 118.4921 | 0.091934 | 0.012832 | -0.014046 | 0.050142 | 0.04456 | 0.050988 | 0.17051 | -0.041199 | 0.091553 | -0.20142 | 0.33875 | -0.36621 | -0.27008 | -0.26093 | -0.16479 | 118.7073 | -3.4195 | 3.0258 | -118.4006 | 3.186 | 3.566 | -118.8583 | -0.19226 | 0.21515 | 0.16022 | 2.9663 | 3.0624 | 2.861 | 3.3188 | 3.186 | 121.9345 | 2.9572 | -0.19226 | 3.3188 | 3.186 | 2.9572 | 2.861 | 121.9345 | -118.6935 | -121.9116
5575.8125 | 121.7697 | -3.2318 | 118.5471 | -0.19798 | 0.015823 | -0.017464 | 0.045015 | 0.041569 | 0.051201 | 0.17072 | 0.032043 | 0.07782 | -0.17395 | 0.45319 | -0.2243 | -0.13733 | -0.39825 | 0.009155 | 118.6707 | -3.3875 | 3.0579 | -118.4692 | 3.2639 | 3.685 | -118.7714 | -0.15564 | 0.1236 | 0.20599 | 2.8336 | 3.241 | 3.0075 | 3.3096 | 3.2639 | 121.9025 | 3.0945 | -0.15564 | 3.3096 | 3.2639 | 3.0945 | 3.0075 | 121.9025 | -118.721 | -121.9345
5577.5781 | 121.8567 | -3.1815 | 118.4921 | 0.15297 | 0.015182 | -0.014687 | 0.050569 | 0.045201 | 0.053337 | 0.17072 | 0.004578 | 0.09613 | -0.16937 | 0.45319 | -0.25635 | -0.13275 | -0.44861 | -0.045776 | 118.6935 | -3.3875 | 3.0121 | -118.396 | 3.186 | 3.6346 | -118.7485 | -0.20599 | 0.20142 | 0.17395 | 2.7329 | 3.1357 | 2.9251 | 3.2776 | 3.186 | 121.875 | 3.0487 | -0.20599 | 3.2776 | 3.186 | 3.0487 | 2.9251 | 121.875 | -118.6615 | -121.8796
5579.2812 | 121.8246 | -3.2043 | 118.5242 | -0.21324 | 0.014114 | -0.016823 | 0.046937 | 0.041996 | 0.053551 | 0.17051 | -0.064087 | 0.10529 | -0.21057 | 0.37994 | -0.32044 | -0.27466 | -0.23804 | -0.11444 | 118.7439 | -3.4332 | 2.9938 | -118.4189 | 3.1403 | 3.5843 | -118.8446 | -0.22888 | 0.21973 | 0.14648 | 2.9663 | 3.0899 | 2.8839 | 3.3096 | 3.1403 | 121.9482 | 2.9297 | -0.22888 | 3.3096 | 3.1403 | 2.9297 | 2.8839 | 121.9482 | -118.7347 | -121.9574
5581.0312 | 121.8979 | -3.1815 | 118.5379 | 0.046158 | 0.013687 | -0.012764 | 0.049501 | 0.044987 | 0.050988 | 0.17222 | -0.064087 | 0.091553 | -0.20599 | 0.37079 | -0.37537 | -0.27924 | -0.25177 | -0.15564 | 118.7485 | -3.392 | 2.9755 | -118.4463 | 3.1174 | 3.5522 | -118.9133 | -0.21057 | 0.21057 | 0.14191 | 2.9297 | 3.0258 | 2.8061 | 3.273 | 3.1174 | 121.9299 | 2.9022 | -0.21057 | 3.273 | 3.1174 | 2.9022 | 2.8061 | 121.9299 | -118.7439 | -121.9299
5582.7969 | 121.843 | -3.2135 | 118.5471 | -0.2285 | 0.014541 | -0.013618 | 0.044801 | 0.041996 | 0.052697 | 0.17136 | -0.07782 | 0.10529 | -0.21515 | 0.40283 | -0.33875 | -0.27466 | -0.23346 | -0.1236 | 118.7714 | -3.3875 | 2.9984 | -118.4418 | 3.1357 | 3.6163 | -118.8858 | -0.17395 | 0.2243 | 0.13733 | 2.98 | 3.0899 | 2.8748 | 3.3188 | 3.1357 | 121.9849 | 2.9388 | -0.17395 | 3.3188 | 3.1357 | 2.9388 | 2.8748 | 121.9849 | -118.7622 | -121.9345
5584.5625 | 121.8933 | -3.1952 | 118.5699 | 0.099564 | 0.015609 | -0.014473 | 0.043519 | 0.045414 | 0.053765 | 0.17008 | 0.032043 | 0.07782 | -0.13733 | 0.50354 | -0.23804 | -0.15564 | -0.44403 | -0.032043 | 118.7302 | -3.3371 | 3.0579 | -118.4921 | 3.2272 | 3.6987 | -118.808 | -0.14191 | 0.16022 | 0.16937 | 2.7512 | 3.1631 | 2.9572 | 3.273 | 3.2272 | 121.9254 | 3.0396 | -0.14191 | 3.273 | 3.2272 | 3.0396 | 2.9572 | 121.9254 | -118.7073 | -121.907
5586.2656 | 121.8018 | -3.1952 | 118.5928 | -0.083542 | 0.014755 | -0.0149 | 0.050996 | 0.045201 | 0.051415 | 0.17286 | -0.009155 | 0.082397 | -0.21515 | 0.50354 | -0.32501 | -0.23346 | -0.29755 | -0.10986 | 118.7393 | -3.3966 | 2.98 | -118.5104 | 3.186 | 3.6987 | -118.9178 | -0.20142 | 0.14648 | 0.20599 | 2.8976 | 3.0853 | 2.8702 | 3.2776 | 3.186 | 121.9345 | 2.9617 | -0.20142 | 3.2776 | 3.186 | 2.9617 | 2.8702 | 121.9345 | -118.808 | -121.9894
5588.0312 | 121.8521 | -3.2135 | 118.5837 | -0.13695 | 0.014114 | -0.0149 | 0.043306 | 0.042423 | 0.053124 | 0.17222 | 0.041199 | 0.068665 | -0.16479 | 0.60425 | -0.20599 | -0.13733 | -0.40741 | 0.032043 | 118.7347 | -3.3875 | 3.0487 | -118.515 | 3.2547 | 3.8177 | -118.7897 | -0.17395 | 0.15106 | 0.20599 | 2.8061 | 3.2455 | 3.0075 | 3.2822 | 3.2547 | 121.9482 | 3.0762 | -0.17395 | 3.2822 | 3.2547 | 3.0762 | 3.0075 | 121.9482 | -118.7485 | -121.9711
5589.7969 | 121.9437 | -3.1906 | 118.5379 | 0.13008 | 0.016891 | -0.016823 | 0.04886 | 0.042851 | 0.051628 | 0.17243 | -0.073242 | 0.10071 | -0.19684 | 0.45319 | -0.35706 | -0.28381 | -0.28839 | -0.16479 | 118.7439 | -3.4287 | 2.9938 | -118.4372 | 3.1174 | 3.6438 | -118.895 | -0.23804 | 0.20599 | 0.1236 | 2.9022 | 3.0258 | 2.8336 | 3.2913 | 3.1174 | 121.9345 | 2.9068 | -0.23804 | 3.2913 | 3.1174 | 2.9068 | 2.8336 | 121.9345 | -118.7347 | -121.9666
5591.5 | 121.9208 | -3.2227 | 118.5425 | 0.069046 | 0.013046 | -0.013618 | 0.043306 | 0.043278 | 0.05526 | 0.17094 | 0.032043 | 0.07782 | -0.13733 | 0.5722 | -0.23346 | -0.16022 | -0.45319 | -0.032043 | 118.7027 | -3.392 | 3.0853 | -118.4647 | 3.2547 | 3.7949 | -118.7759 | -0.16937 | 0.16022 | 0.16937 | 2.7695 | 3.1906 | 2.9892 | 3.3005 | 3.2547 | 121.9254 | 3.0624 | -0.16937 | 3.3005 | 3.2547 | 3.0624 | 2.9892 | 121.9254 | -118.6798 | -121.9345
5593.2656 | 121.8567 | -3.273 | 118.5333 | 0.0080111 | 0.014755 | -0.0093461 | 0.049501 | 0.044773 | 0.050774 | 0.17265 | -0.027466 | 0.086975 | -0.19226 | 0.50812 | -0.35248 | -0.27008 | -0.29755 | -0.14648 | 118.7164 | -3.4744 | 3.0807 | -118.4464 | 3.2455 | 3.7811 | -118.8858 | -0.20142 | 0.18311 | 0.16479 | 2.9755 | 3.1265 | 2.9205 | 3.36 | 3.2455 | 121.9894 | 3.0029 | -0.20142 | 3.36 | 3.2455 | 3.0029 | 2.9205 | 121.9894 | -118.7256 | -122.0078
5595.0312 | 121.9666 | -3.2684 | 118.4875 | -0.0072479 | 0.014328 | -0.014687 | 0.040742 | 0.041569 | 0.05291 | 0.17201 | -0.032043 | 0.073242 | -0.16937 | 0.5722 | -0.27008 | -0.21057 | -0.37537 | -0.050354 | 118.6707 | -3.4744 | 3.0991 | -118.4143 | 3.2364 | 3.8406 | -118.7576 | -0.20599 | 0.1831 | 0.13733 | 2.8931 | 3.2181 | 2.9984 | 3.3417 | 3.2364 | 121.9391 | 3.0579 | -0.20599 | 3.3417 | 3.2364 | 3.0579 | 2.9984 | 121.9391 | -118.6569 | -121.962
5596.7812 | 121.8887 | -3.3875 | 118.4555 | -0.25139 | 0.012619 | -0.018104 | 0.047364 | 0.041996 | 0.053978 | 0.17072 | -0.013733 | 0.086975 | -0.1831 | 0.55847 | -0.29755 | -0.24261 | -0.28381 | -0.10529 | 118.6203 | -3.5568 | 3.2043 | -118.3685 | 3.3737 | 3.9459 | -118.7531 | -0.16937 | 0.16479 | 0.16937 | 3.1036 | 3.2822 | 3.0899 | 3.4744 | 3.3737 | 122.0078 | 3.1448 | -0.16937 | 3.4744 | 3.3737 | 3.1448 | 3.0899 | 122.0078 | -118.6386 | -122.0123
5598.5469 | 121.8796 | -3.392 | 118.4555 | -0.22087 | 0.01326 | -0.017036 | 0.045015 | 0.04221 | 0.054619 | 0.16987 | 0.027466 | 0.073242 | -0.17395 | 0.59052 | -0.27008 | -0.19226 | -0.32044 | -0.022888 | 118.6066 | -3.5477 | 3.2181 | -118.3823 | 3.4195 | 3.9825 | -118.7256 | -0.15564 | 0.15106 | 0.20142 | 3.0716 | 3.3691 | 3.1219 | 3.4653 | 3.4195 | 121.9986 | 3.1998 | -0.15564 | 3.4653 | 3.4195 | 3.1998 | 3.1219 | 121.9986 | -118.6295 | -122.0032
5600.3125 | 121.843 | -3.4058 | 118.4555 | -0.10643 | 0.011551 | -0.013832 | 0.049928 | 0.045414 | 0.050988 | 0.17115 | -0.013733 | 0.086975 | -0.19684 | 0.55847 | -0.3067 | -0.24261 | -0.31128 | -0.082397 | 118.6478 | -3.5522 | 3.2089 | -118.3685 | 3.392 | 3.9642 | -118.7622 | -0.14648 | 0.19226 | 0.18311 | 3.0945 | 3.3234 | 3.0991 | 3.4927 | 3.392 | 122.0535 | 3.1631 | -0.14648 | 3.4927 | 3.392 | 3.1631 | 3.0991 | 122.0535 | -118.6523 | -122.0078
5602.0156 | 121.8567 | -3.3829 | 118.483 | -0.14458 | 0.013473 | -0.011909 | 0.042238 | 0.044132 | 0.05291 | 0.17136 | 0.054932 | 0.064087 | -0.15106 | 0.62256 | -0.19226 | -0.13275 | -0.40741 | 0.032043 | 118.6386 | -3.5156 | 3.2318 | -118.4189 | 3.4378 | 4.0054 | -118.6752 | -0.13275 | 0.15564 | 0.20599 | 2.9755 | 3.4149 | 3.1906 | 3.447 | 3.4378 | 122.0215 | 3.2501 | -0.13275 | 3.447 | 3.4378 | 3.2501 | 3.1906 | 122.0215 | -118.634 | -121.9986
5603.7812 | 121.9437 | -3.3188 | 118.4509 | 0.076676 | 0.015823 | -0.014259 | 0.052705 | 0.043064 | 0.051842 | 0.17072 | -0.041199 | 0.091553 | -0.21515 | 0.48523 | -0.36163 | -0.28381 | -0.24719 | -0.16937 | 118.6935 | -3.5202 | 3.1036 | -118.3594 | 3.2776 | 3.804 | -118.8126 | -0.20142 | 0.24261 | 0.17395 | 3.0716 | 3.1494 | 2.9572 | 3.4103 | 3.2776 | 122.0123 | 3.035 | -0.20142 | 3.4103 | 3.2776 | 3.035 | 2.9572 | 122.0123 | -118.6661 | -121.9711
5605.4844 | 121.9986 | -3.3096 | 118.5013 | 0.069046 | 0.011978 | -0.017891 | 0.040742 | 0.042851 | 0.053337 | 0.17158 | 0.004578 | 0.064087 | -0.16479 | 0.53101 | -0.2655 | -0.18768 | -0.37994 | -0.054932 | 118.6569 | -3.5019 | 3.1448 | -118.4372 | 3.3142 | 3.8406 | -118.7668 | -0.19226 | 0.15564 | 0.16937 | 2.9297 | 3.2547 | 3.0441 | 3.3737 | 3.3142 | 121.9666 | 3.1219 | -0.19226 | 3.3737 | 3.3142 | 3.1219 | 3.0441 | 121.9666 | -118.6661 | -122.0032
5607.25 | 121.9208 | -3.3234 | 118.5196 | -0.14458 | 0.014114 | -0.018745 | 0.040742 | 0.040074 | 0.054406 | 0.17072 | 0.032043 | 0.07782 | -0.15564 | 0.58136 | -0.20142 | -0.13733 | -0.41657 | 0.018311 | 118.6569 | -3.479 | 3.1677 | -118.4418 | 3.3554 | 3.9047 | -118.721 | -0.15564 | 0.13733 | 0.18768 | 2.9068 | 3.3417 | 3.1219 | 3.4012 | 3.3554 | 121.9803 | 3.186 | -0.15564 | 3.4012 | 3.3554 | 3.186 | 3.1219 | 121.9803 | -118.6752 | -121.9986
5609.0156 | 122.0032 | -3.3051 | 118.5104 | -0.037765 | 0.012619 | -0.019386 | 0.043519 | 0.042851 | 0.053551 | 0.17222 | -0.022888 | 0.059509 | -0.17395 | 0.5127 | -0.24719 | -0.16937 | -0.3891 | -0.032043 | 118.6615 | -3.5156 | 3.1311 | -118.4509 | 3.2822 | 3.8177 | -118.7576 | -0.21057 | 0.15106 | 0.15106 | 2.916 | 3.273 | 3.0579 | 3.3646 | 3.2822 | 121.9666 | 3.1357 | -0.21057 | 3.3646 | 3.2822 | 3.1357 | 3.0579 | 121.9666 | -118.6844 | -122.0261
5610.7188 | 122.0215 | -3.3005 | 118.5196 | 0.091934 | 0.017532 | -0.015541 | 0.049501 | 0.044987 | 0.051201 | 0.17243 | -0.059509 | 0.10529 | -0.19684 | 0.45319 | -0.35248 | -0.27008 | -0.28839 | -0.14648 | 118.7439 | -3.5156 | 3.1036 | -118.4143 | 3.241 | 3.7537 | -118.8721 | -0.21515 | 0.2243 | 0.13733 | 3.0121 | 3.154 | 2.948 | 3.4058 | 3.241 | 122.0444 | 3.0304 | -0.21515 | 3.4058 | 3.241 | 3.0304 | 2.948 | 122.0444 | -118.7164 | -122.0352
5612.4844 | 121.9757 | -3.3508 | 118.4647 | 0.20638 | 0.015182 | -0.017677 | 0.050355 | 0.045628 | 0.050347 | 0.1703 | 0.004578 | 0.082397 | -0.1831 | 0.52643 | -0.25177 | -0.18768 | -0.42114 | -0.073242 | 118.6386 | -3.5614 | 3.1677 | -118.3823 | 3.3554 | 3.8773 | -118.7164 | -0.21057 | 0.17395 | 0.18768 | 2.9297 | 3.2776 | 3.0991 | 3.4332 | 3.3554 | 121.9894 | 3.1631 | -0.21057 | 3.4332 | 3.3554 | 3.1631 | 3.0991 | 121.9894 | -118.6478 | -122.0261
5614.1875 | 121.962 | -3.4378 | 118.3823 | 0.1606 | 0.016464 | -0.013832 | 0.048219 | 0.046482 | 0.05291 | 0.17371 | -0.004578 | 0.086975 | -0.18768 | 0.50354 | -0.27924 | -0.20599 | -0.41199 | -0.059509 | 118.5928 | -3.5889 | 3.2501 | -118.2953 | 3.4332 | 3.9413 | -118.6615 | -0.15106 | 0.21057 | 0.1831 | 3.0258 | 3.3783 | 3.1586 | 3.5248 | 3.4332 | 122.0306 | 3.2318 | -0.15106 | 3.5248 | 3.4332 | 3.2318 | 3.1586 | 122.0306 | -118.5699 | -121.9711
5615.9531 | 121.9849 | -3.4195 | 118.4189 | -0.075912 | 0.01326 | -0.015327 | 0.043519 | 0.040715 | 0.054406 | 0.16966 | 0 | 0.082397 | -0.15564 | 0.53101 | -0.2243 | -0.16479 | -0.37994 | -0.004578 | 118.5654 | -3.6072 | 3.2639 | -118.3365 | 3.4195 | 3.9505 | -118.6432 | -0.18768 | 0.14648 | 0.15564 | 3.0396 | 3.4149 | 3.1952 | 3.5019 | 3.4195 | 121.9849 | 3.2547 | -0.18768 | 3.5019 | 3.4195 | 3.2547 | 3.1952 | 121.9849 | -118.5745 | -122.0261
5617.6719 | 122.0581 | -3.479 | 118.3319 | -0.0072479 | 0.011337 | -0.015541 | 0.042878 | 0.041355 | 0.053337 | 0.17371 | -0.041199 | 0.054932 | -0.18768 | 0.54474 | -0.27924 | -0.15564 | -0.35248 | -0.013733 | 118.5059 | -3.6575 | 3.2913 | -118.277 | 3.4378 | 4.0237 | -118.6111 | -0.17853 | 0.17395 | 0.14648 | 3.1265 | 3.4653 | 3.1998 | 3.5339 | 3.4378 | 121.9849 | 3.3234 | -0.17853 | 3.5339 | 3.4378 | 3.3234 | 3.1998 | 121.9849 | -118.5196 | -121.9894
5619.4375 | 122.0535 | -3.479 | 118.3685 | 0.01564 | 0.014328 | -0.017464 | 0.046083 | 0.04221 | 0.052269 | 0.17008 | -0.018311 | 0.064087 | -0.18768 | 0.53101 | -0.2655 | -0.15564 | -0.32501 | -0.022888 | 118.5287 | -3.6667 | 3.2913 | -118.3044 | 3.4607 | 4.01 | -118.634 | -0.18768 | 0.16022 | 0.16937 | 3.154 | 3.4561 | 3.2135 | 3.5431 | 3.4607 | 122.0078 | 3.3234 | -0.18768 | 3.5431 | 3.4607 | 3.3234 | 3.2135 | 122.0078 | -118.5562 | -122.0352
5621.1406 | 121.9437 | -3.4973 | 118.3914 | -0.014877 | 0.017532 | -0.014687 | 0.055269 | 0.045201 | 0.05056 | 0.17094 | 0.004578 | 0.10529 | -0.20599 | 0.53101 | -0.35248 | -0.21057 | -0.23804 | -0.07782 | 118.6066 | -3.6713 | 3.2913 | -118.2861 | 3.5019 | 4.0283 | -118.7439 | -0.17395 | 0.21515 | 0.21057 | 3.2593 | 3.4195 | 3.1448 | 3.6026 | 3.5019 | 122.1039 | 3.2867 | -0.17395 | 3.6026 | 3.5019 | 3.2867 | 3.1448 | 122.1039 | -118.5974 | -122.0627
5622.9062 | 121.9116 | -3.511 | 118.4235 | -0.12932 | 0.015182 | -0.014687 | 0.049928 | 0.046269 | 0.047997 | 0.17072 | 0.004578 | 0.09613 | -0.19226 | 0.5722 | -0.29755 | -0.1831 | -0.24719 | -0.013733 | 118.6295 | -3.653 | 3.3188 | -118.3273 | 3.5156 | 4.0833 | -118.721 | -0.14191 | 0.20599 | 0.19684 | 3.2639 | 3.4973 | 3.2135 | 3.6072 | 3.5156 | 122.1405 | 3.3279 | -0.14191 | 3.6072 | 3.5156 | 3.3279 | 3.2135 | 122.1405 | -118.6157 | -122.0764
5624.6719 | 121.9025 | -3.4744 | 118.428 | -0.098801 | 0.014969 | -0.01255 | 0.049501 | 0.043492 | 0.052269 | 0.16987 | 0.004578 | 0.086975 | -0.21057 | 0.57678 | -0.28839 | -0.16022 | -0.23346 | 0 | 118.634 | -3.6484 | 3.2639 | -118.3411 | 3.479 | 4.0512 | -118.7164 | -0.17395 | 0.20599 | 0.21515 | 3.241 | 3.4744 | 3.186 | 3.5614 | 3.479 | 122.1085 | 3.3142 | -0.17395 | 3.5614 | 3.479 | 3.3142 | 3.186 | 122.1085 | -118.6386 | -122.0764
5626.4375 | 122.0764 | -3.4195 | 118.4235 | 0.01564 | 0.015396 | -0.018745 | 0.042451 | 0.045414 | 0.053124 | 0.17243 | -0.022888 | 0.073242 | -0.15564 | 0.56305 | -0.25635 | -0.12817 | -0.32959 | -0.013733 | 118.6157 | -3.6301 | 3.2639 | -118.3502 | 3.3966 | 3.9825 | -118.6798 | -0.21057 | 0.19226 | 0.13275 | 3.0899 | 3.4058 | 3.1631 | 3.4927 | 3.3966 | 122.0352 | 3.2913 | -0.21057 | 3.4927 | 3.3966 | 3.2913 | 3.1631 | 122.0352 | -118.5791 | -122.0535
5628.1562 | 121.907 | -3.4744 | 118.4601 | -0.091171 | 0.01326 | -0.011909 | 0.05121 | 0.043278 | 0.049919 | 0.1735 | 0 | 0.073242 | -0.21515 | 0.55847 | -0.30212 | -0.16479 | -0.26093 | -0.032043 | 118.6249 | -3.6484 | 3.2593 | -118.3868 | 3.4744 | 4.0329 | -118.7622 | -0.17395 | 0.16479 | 0.21515 | 3.2135 | 3.4424 | 3.1723 | 3.5477 | 3.4744 | 122.0993 | 3.3096 | -0.17395 | 3.5477 | 3.4744 | 3.3096 | 3.1723 | 122.0993 | -118.6752 | -122.1085
5629.9219 | 122.0627 | -3.4195 | 118.4372 | 0.061417 | 0.0139 | -0.012764 | 0.04416 | 0.042423 | 0.053978 | 0.17307 | -0.009155 | 0.073242 | -0.16479 | 0.5722 | -0.26093 | -0.14191 | -0.33875 | 0 | 118.6157 | -3.6209 | 3.2547 | -118.364 | 3.4103 | 3.9917 | -118.6981 | -0.20142 | 0.17853 | 0.15564 | 3.0808 | 3.4195 | 3.1586 | 3.4927 | 3.4103 | 122.0352 | 3.2776 | -0.20142 | 3.4927 | 3.4103 | 3.2776 | 3.1586 | 122.0352 | -118.602 | -122.0581
5631.625 | 121.9894 | -3.4378 | 118.4647 | -0.2285 | 0.014969 | -0.017464 | 0.046937 | 0.040928 | 0.051415 | 0.17179 | -0.086975 | 0.10529 | -0.20142 | 0.52185 | -0.33875 | -0.21973 | -0.16479 | -0.07782 | 118.6981 | -3.6392 | 3.2364 | -118.3594 | 3.3508 | 3.9597 | -118.8034 | -0.20142 | 0.23346 | 0.11444 | 3.273 | 3.36 | 3.0991 | 3.5431 | 3.3508 | 122.1359 | 3.2181 | -0.20142 | 3.5431 | 3.3508 | 3.2181 | 3.0991 | 122.1359 | -118.6661 | -122.1039
5633.3906 | 122.0261 | -3.4149 | 118.4235 | 0.1606 | 0.015609 | -0.012978 | 0.047578 | 0.043492 | 0.051201 | 0.17371 | -0.018311 | 0.064087 | -0.19226 | 0.57678 | -0.27466 | -0.13733 | -0.35706 | -0.004578 | 118.6295 | -3.6163 | 3.2227 | -118.3594 | 3.3966 | 3.9917 | -118.6981 | -0.20142 | 0.20599 | 0.17395 | 3.0579 | 3.4103 | 3.1403 | 3.479 | 3.3966 | 122.0444 | 3.2776 | -0.20142 | 3.479 | 3.3966 | 3.2776 | 3.1403 | 122.0444 | -118.6157 | -122.0398
5635.1562 | 122.0764 | -3.392 | 118.4326 | 0.084305 | 0.014541 | -0.020668 | 0.047578 | 0.043064 | 0.050988 | 0.17201 | -0.09613 | 0.10529 | -0.20142 | 0.49896 | -0.34332 | -0.24261 | -0.22888 | -0.13275 | 118.6707 | -3.6621 | 3.1906 | -118.3273 | 3.2959 | 3.891 | -118.7759 | -0.27008 | 0.23804 | 0.10529 | 3.1631 | 3.2593 | 3.0487 | 3.4973 | 3.2959 | 122.0627 | 3.1494 | -0.27008 | 3.4973 | 3.2959 | 3.1494 | 3.0487 | 122.0627 | -118.634 | -122.0947
5636.8594 | 121.9986 | -3.4653 | 118.4601 | -0.14458 | 0.0139 | -0.021095 | 0.041597 | 0.040287 | 0.054406 | 0.17307 | 0.009155 | 0.068665 | -0.16479 | 0.62256 | -0.21057 | -0.07782 | -0.35706 | 0.07782 | 118.6295 | -3.6255 | 3.3005 | -118.3914 | 3.4744 | 4.0878 | -118.6707 | -0.16022 | 0.16937 | 0.17395 | 3.1082 | 3.5431 | 3.2547 | 3.5339 | 3.4744 | 122.0947 | 3.3875 | -0.16022 | 3.5339 | 3.4744 | 3.3875 | 3.2547 | 122.0947 | -118.6249 | -122.0856
5638.6406 | 121.9986 | -3.4515 | 118.4509 | -0.17509 | 0.013046 | -0.0149 | 0.043947 | 0.042851 | 0.055687 | 0.17201 | 0.032043 | 0.073242 | -0.16479 | 0.62714 | -0.21515 | -0.082397 | -0.37994 | 0.082397 | 118.634 | -3.6301 | 3.2867 | -118.3777 | 3.4836 | 4.0787 | -118.6661 | -0.17853 | 0.1831 | 0.19684 | 3.0716 | 3.5339 | 3.2364 | 3.5248 | 3.4836 | 122.0856 | 3.3691 | -0.17853 | 3.5248 | 3.4836 | 3.3691 | 3.2364 | 122.0856 | -118.6157 | -122.081
5640.4219 | 122.0535 | -3.4607 | 118.428 | 0.11482 | 0.015396 | -0.010414 | 0.050782 | 0.041996 | 0.053551 | 0.17094 | 0.059509 | 0.059509 | -0.16479 | 0.62714 | -0.25177 | -0.10529 | -0.4303 | 0.013733 | 118.6066 | -3.6255 | 3.2959 | -118.3685 | 3.5202 | 4.0878 | -118.6798 | -0.16479 | 0.17853 | 0.2243 | 3.0304 | 3.4744 | 3.2089 | 3.5202 | 3.5202 | 122.0673 | 3.3554 | -0.16479 | 3.5202 | 3.5202 | 3.3554 | 3.2089 | 122.0673 | -118.5928 | -122.0535
5642.1875 | 122.0901 | -3.4378 | 118.4555 | -0.030136 | 0.0139 | -0.022163 | 0.044374 | 0.040715 | 0.05291 | 0.17222 | -0.036621 | 0.068665 | -0.18768 | 0.55847 | -0.27924 | -0.13733 | -0.32959 | -0.022888 | 118.6111 | -3.6575 | 3.2501 | -118.3868 | 3.4012 | 3.9963 | -118.7347 | -0.21973 | 0.15564 | 0.15106 | 3.1082 | 3.4149 | 3.1586 | 3.5065 | 3.4012 | 122.0489 | 3.3005 | -0.21973 | 3.5065 | 3.4012 | 3.3005 | 3.1586 | 122.0489 | -118.6432 | -122.113
5643.9062 | 122.0444 | -3.4424 | 118.4692 | 0.1606 | 0.014755 | -0.012337 | 0.049714 | 0.043919 | 0.053551 | 0.17307 | 0.059509 | 0.064087 | -0.16479 | 0.62714 | -0.25635 | -0.10529 | -0.43488 | 0.036621 | 118.6752 | -3.6118 | 3.2776 | -118.4052 | 3.5019 | 4.0695 | -118.7256 | -0.16937 | 0.20599 | 0.2243 | 3.0075 | 3.479 | 3.186 | 3.5065 | 3.5019 | 122.1176 | 3.3371 | -0.16937 | 3.5065 | 3.5019 | 3.3371 | 3.186 | 122.1176 | -118.634 | -122.081
5645.6719 | 121.9757 | -3.4653 | 118.5059 | -0.17509 | 0.015182 | -0.014046 | 0.046296 | 0.043064 | 0.051628 | 0.1703 | 0.050354 | 0.068665 | -0.17395 | 0.67291 | -0.2243 | -0.059509 | -0.32044 | 0.10071 | 118.6661 | -3.6209 | 3.2913 | -118.4372 | 3.5156 | 4.1382 | -118.7302 | -0.15564 | 0.16022 | 0.2243 | 3.1448 | 3.566 | 3.241 | 3.5339 | 3.5156 | 122.1313 | 3.4058 | -0.15564 | 3.5339 | 3.5156 | 3.4058 | 3.241 | 122.1313 | -118.6798 | -122.1268
5647.4375 | 121.994 | -3.4561 | 118.483 | -0.18272 | 0.015609 | -0.011269 | 0.053346 | 0.043705 | 0.049492 | 0.17371 | -0.045776 | 0.10986 | -0.20599 | 0.58594 | -0.32959 | -0.20599 | -0.17395 | -0.036621 | 118.6844 | -3.6621 | 3.2501 | -118.3731 | 3.4103 | 4.0421 | -118.8126 | -0.20599 | 0.20142 | 0.16022 | 3.2822 | 3.4195 | 3.1265 | 3.566 | 3.4103 | 122.1405 | 3.2501 | -0.20599 | 3.566 | 3.4103 | 3.2501 | 3.1265 | 122.1405 | -118.689 | -122.1451
5649.1406 | 122.1039 | -3.4241 | 118.4555 | 0.091934 | 0.012405 | -0.01725 | 0.050142 | 0.044773 | 0.048638 | 0.17521 | -0.068665 | 0.09613 | -0.21515 | 0.56305 | -0.36621 | -0.20599 | -0.20599 | -0.09613 | 118.6844 | -3.6484 | 3.2089 | -118.3594 | 3.3554 | 3.9871 | -118.8217 | -0.2243 | 0.22888 | 0.14648 | 3.2181 | 3.3279 | 3.0579 | 3.5202 | 3.3554 | 122.1085 | 3.2181 | -0.2243 | 3.5202 | 3.3554 | 3.2181 | 3.0579 | 122.1085 | -118.6707 | -122.1039
5650.9062 | 122.0627 | -3.4149 | 118.4692 | 0.14534 | 0.012832 | -0.014046 | 0.04886 | 0.045841 | 0.054406 | 0.17179 | 0.050354 | 0.054932 | -0.16479 | 0.64087 | -0.25635 | -0.054932 | -0.39825 | 0.045776 | 118.6386 | -3.6072 | 3.2501 | -118.4143 | 3.4653 | 4.0558 | -118.7256 | -0.19226 | 0.16937 | 0.21515 | 3.0167 | 3.4607 | 3.1586 | 3.4698 | 3.4653 | 122.0535 | 3.36 | -0.19226 | 3.4698 | 3.4653 | 3.36 | 3.1586 | 122.0535 | -118.634 | -122.0764
5652.6094 | 121.9849 | -3.5065 | 118.5013 | -0.091171 | 0.015823 | -0.012337 | 0.052705 | 0.043919 | 0.051201 | 0.17414 | 0 | 0.09613 | -0.21515 | 0.59052 | -0.31586 | -0.16937 | -0.23804 | -0.041199 | 118.6844 | -3.6438 | 3.2913 | -118.4052 | 3.5065 | 4.097 | -118.8171 | -0.13733 | 0.1831 | 0.21515 | 3.2684 | 3.4653 | 3.1906 | 3.6026 | 3.5065 | 122.1909 | 3.3371 | -0.13733 | 3.6026 | 3.5065 | 3.3371 | 3.1906 | 122.1909 | -118.7164 | -122.1451
5654.375 | 122.0901 | -3.4241 | 118.5287 | 0.11482 | 0.01326 | -0.015541 | 0.046083 | 0.043492 | 0.052269 | 0.17222 | 0.041199 | 0.059509 | -0.16022 | 0.65002 | -0.25635 | -0.073242 | -0.38452 | 0.036621 | 118.6752 | -3.598 | 3.2639 | -118.4692 | 3.4653 | 4.0741 | -118.7851 | -0.17395 | 0.14648 | 0.20142 | 3.0396 | 3.4607 | 3.1677 | 3.4836 | 3.4653 | 122.0993 | 3.3508 | -0.17395 | 3.4836 | 3.4653 | 3.3508 | 3.1677 | 122.0993 | -118.689 | -122.1268
5656.125 | 122.0718 | -3.4149 | 118.5013 | 0.17586 | 0.013687 | -0.015541 | 0.049073 | 0.047764 | 0.052269 | 0.17158 | -0.004578 | 0.073242 | -0.19226 | 0.70038 | -0.27008 | -0.082397 | -0.32501 | 0.027466 | 118.7302 | -3.5706 | 3.2227 | -118.428 | 3.4103 | 4.1153 | -118.7714 | -0.15564 | 0.22888 | 0.18768 | 3.0899 | 3.4424 | 3.1448 | 3.4882 | 3.4103 | 122.1451 | 3.3325 | -0.15564 | 3.4882 | 3.4103 | 3.3325 | 3.1448 | 122.1451 | -118.6935 | -122.0718
5657.8906 | 122.113 | -3.3875 | 118.5287 | -0.030136 | 0.014328 | -0.018318 | 0.043092 | 0.043919 | 0.05291 | 0.17371 | -0.013733 | 0.068665 | -0.17853 | 0.66376 | -0.23346 | -0.059509 | -0.28839 | 0.050354 | 118.7347 | -3.5568 | 3.2089 | -118.4601 | 3.3737 | 4.0512 | -118.7622 | -0.16937 | 0.20599 | 0.16479 | 3.0991 | 3.4378 | 3.154 | 3.4561 | 3.3737 | 122.1222 | 3.3279 | -0.16937 | 3.4561 | 3.3737 | 3.3279 | 3.154 | 122.1222 | -118.7073 | -122.0856
5659.6562 | 121.9986 | -3.392 | 118.5883 | -0.091171 | 0.016678 | -0.015541 | 0.053346 | 0.045628 | 0.050133 | 0.17521 | -0.004578 | 0.082397 | -0.20142 | 0.6546 | -0.28381 | -0.14648 | -0.24261 | 0.009155 | 118.7943 | -3.566 | 3.1906 | -118.5059 | 3.3875 | 4.0466 | -118.8721 | -0.17395 | 0.20599 | 0.19684 | 3.1494 | 3.4012 | 3.1082 | 3.4744 | 3.3875 | 122.1863 | 3.2455 | -0.17395 | 3.4744 | 3.3875 | 3.2455 | 3.1082 | 122.1863 | -118.7897 | -122.1542
5661.3594 | 122.049 | -3.3875 | 118.5791 | -0.14458 | 0.014114 | -0.018532 | 0.045015 | 0.042851 | 0.053978 | 0.17158 | 0.032043 | 0.068665 | -0.17395 | 0.71869 | -0.19684 | -0.041199 | -0.34332 | 0.09613 | 118.7622 | -3.5339 | 3.2135 | -118.5104 | 3.4195 | 4.1061 | -118.7759 | -0.14649 | 0.1831 | 0.20599 | 3.0441 | 3.4836 | 3.1906 | 3.4561 | 3.4195 | 122.1497 | 3.3463 | -0.14649 | 3.4561 | 3.4195 | 3.3463 | 3.1906 | 122.1497 | -118.7531 | -122.113
5663.1406 | 122.1268 | -3.3325 | 118.5699 | 0.12245 | 0.016891 | -0.016182 | 0.051851 | 0.044346 | 0.052483 | 0.17478 | -0.045776 | 0.091553 | -0.21973 | 0.58594 | -0.3479 | -0.19226 | -0.21057 | -0.091553 | 118.8171 | -3.5614 | 3.1128 | -118.4784 | 3.2867 | 3.9185 | -118.9178 | -0.22888 | 0.24719 | 0.17395 | 3.1219 | 3.241 | 2.9846 | 3.4241 | 3.2867 | 122.1497 | 3.1403 | -0.22888 | 3.4241 | 3.2867 | 3.1403 | 2.9846 | 122.1497 | -118.7897 | -122.1313
5664.9219 | 122.1634 | -3.3096 | 118.6111 | 0.038529 | 0.0139 | -0.018318 | 0.043947 | 0.041996 | 0.052056 | 0.17542 | -0.004578 | 0.073242 | -0.1831 | 0.6546 | -0.26093 | -0.11444 | -0.31128 | 0.004578 | 118.8263 | -3.5248 | 3.1265 | -118.5379 | 3.3051 | 3.9642 | -118.8721 | -0.21515 | 0.21515 | 0.17853 | 2.9984 | 3.3142 | 3.0487 | 3.3829 | 3.3051 | 122.1359 | 3.1952 | -0.21515 | 3.3829 | 3.3051 | 3.1952 | 3.0487 | 122.1359 | -118.7942 | -122.1359
5666.6406 | 122.1588 | -3.3051 | 118.6386 | 0.13771 | 0.014969 | -0.012337 | 0.056123 | 0.04456 | 0.050988 | 0.17564 | -0.050354 | 0.10071 | -0.21057 | 0.59967 | -0.36163 | -0.19226 | -0.21515 | -0.086975 | 118.8766 | -3.5248 | 3.0945 | -118.5379 | 3.2547 | 3.9047 | -119.0002 | -0.21973 | 0.23804 | 0.16022 | 3.0899 | 3.2181 | 2.9434 | 3.4058 | 3.2547 | 122.1817 | 3.1128 | -0.21973 | 3.4058 | 3.2547 | 3.1128 | 2.9434 | 122.1817 | -118.8492 | -122.1634
5668.4062 | 122.1359 | -3.2913 | 118.6478 | 0.084305 | 0.012405 | -0.012764 | 0.046937 | 0.042637 | 0.05291 | 0.17606 | 0.036621 | 0.041199 | -0.16479 | 0.68665 | -0.23804 | -0.073242 | -0.36163 | 0.036621 | 118.8446 | -3.5019 | 3.1265 | -118.6066 | 3.3279 | 3.978 | -118.8858 | -0.21057 | 0.19684 | 0.20142 | 2.9297 | 3.3279 | 3.0533 | 3.3325 | 3.3279 | 122.1359 | 3.2181 | -0.21057 | 3.3325 | 3.3279 | 3.2181 | 3.0533 | 122.1359 | -118.8126 | -122.1497
5670.1719 | 122.0261 | -3.4103 | 118.6249 | -0.21324 | 0.013473 | -0.014687 | 0.053346 | 0.041569 | 0.053124 | 0.17777 | 0.054932 | 0.068665 | -0.14648 | 0.70953 | -0.21057 | -0.054932 | -0.32044 | 0.09613 | 118.7714 | -3.5522 | 3.2639 | -118.5562 | 3.4653 | 4.1199 | -118.8354 | -0.14191 | 0.14648 | 0.20142 | 3.0899 | 3.5065 | 3.1998 | 3.479 | 3.4653 | 122.1817 | 3.3554 | -0.14191 | 3.479 | 3.4653 | 3.3554 | 3.1998 | 122.1817 | -118.7714 | -122.1771
5671.9219 | 122.0444 | -3.3463 | 118.6935 | -0.13695 | 0.0139 | -0.020241 | 0.047364 | 0.042851 | 0.051628 | 0.17585 | 0.032043 | 0.045776 | -0.18768 | 0.71411 | -0.22888 | -0.045776 | -0.32959 | 0.082397 | 118.84 | -3.5019 | 3.1586 | -118.6478 | 3.3783 | 4.0604 | -118.9224 | -0.15564 | 0.14649 | 0.21973 | 3.0167 | 3.4286 | 3.1174 | 3.392 | 3.3783 | 122.1863 | 3.3005 | -0.15564 | 3.392 | 3.3783 | 3.3005 | 3.1174 | 122.1863 | -118.8812 | -122.1954
5673.625 | 122.081 | -3.3279 | 118.6386 | 0.02327 | 0.014969 | -0.018104 | 0.055696 | 0.044132 | 0.050133 | 0.175 | -0.045776 | 0.086975 | -0.21057 | 0.58136 | -0.35248 | -0.20142 | -0.20142 | -0.09613 | 118.895 | -3.5156 | 3.1174 | -118.5516 | 3.2822 | 3.9093 | -118.9911 | -0.18768 | 0.25635 | 0.1648 | 3.1265 | 3.2318 | 2.9755 | 3.4149 | 3.2822 | 122.2229 | 3.1265 | -0.18768 | 3.4149 | 3.2822 | 3.1265 | 2.9755 | 122.2229 | -118.8492 | -122.1542
5675.3906 | 122.1588 | -3.3188 | 118.6478 | -0.014877 | 0.014114 | -0.019386 | 0.043733 | 0.042423 | 0.053337 | 0.17542 | -0.013733 | 0.073242 | -0.17853 | 0.61798 | -0.27924 | -0.10071 | -0.31586 | 0.018311 | 118.808 | -3.5065 | 3.1403 | -118.5745 | 3.3051 | 3.9368 | -118.927 | -0.18768 | 0.16022 | 0.16479 | 3.0029 | 3.3371 | 3.0396 | 3.392 | 3.3051 | 122.1268 | 3.2181 | -0.18768 | 3.392 | 3.3051 | 3.2181 | 3.0396 | 122.1268 | -118.8263 | -122.1542
5677.1406 | 122.0444 | -3.2135 | 118.8217 | -0.12932 | 0.011764 | -0.014046 | 0.044587 | 0.043064 | 0.052269 | 0.17222 | 0.041199 | 0.050354 | -0.16937 | 0.68207 | -0.19684 | -0.050354 | -0.37079 | 0.082397 | 118.9636 | -3.3737 | 3.0441 | -118.7714 | 3.2547 | 3.8956 | -119.0186 | -0.16022 | 0.14191 | 0.21057 | 2.8427 | 3.2959 | 3.0167 | 3.2639 | 3.2547 | 122.1771 | 3.1631 | -0.16022 | 3.2639 | 3.2547 | 3.1631 | 3.0167 | 122.1771 | -118.9911 | -122.1954
5678.9062 | 122.1634 | -3.1677 | 118.7805 | 0.10719 | 0.014541 | -0.011482 | 0.052064 | 0.04221 | 0.050988 | 0.17307 | -0.073242 | 0.086975 | -0.21057 | 0.55847 | -0.35706 | -0.21057 | -0.23804 | -0.11444 | 118.9865 | -3.3966 | 2.9572 | -118.6935 | 3.0945 | 3.7262 | -119.1376 | -0.22888 | 0.20599 | 0.13733 | 2.9297 | 3.0533 | 2.8107 | 3.2547 | 3.0945 | 122.1542 | 2.9572 | -0.22888 | 3.2547 | 3.0945 | 2.9572 | 2.8107 | 122.1542 | -118.9911 | -122.1771
5680.6719 | 122.081 | -3.2227 | 118.8034 | -0.18272 | 0.017532 | -0.015114 | 0.049501 | 0.040928 | 0.053978 | 0.17393 | -0.064087 | 0.091553 | -0.21057 | 0.5722 | -0.32501 | -0.19684 | -0.17853 | -0.073242 | 118.9865 | -3.4287 | 3.0121 | -118.7119 | 3.1586 | 3.7949 | -119.1284 | -0.20599 | 0.1831 | 0.14648 | 3.0441 | 3.1494 | 2.8976 | 3.3142 | 3.1586 | 122.2092 | 3.0258 | -0.20599 | 3.3142 | 3.1586 | 3.0258 | 2.8976 | 122.2092 | -119.014 | -122.2321
5682.4375 | 122.1176 | -3.2043 | 118.7988 | 0.069046 | 0.0139 | -0.015755 | 0.052491 | 0.044773 | 0.047997 | 0.175 | -0.041199 | 0.091553 | -0.21515 | 0.55389 | -0.35706 | -0.20142 | -0.21515 | -0.10986 | 119.0277 | -3.3875 | 2.9892 | -118.7073 | 3.1631 | 3.7582 | -119.1559 | -0.1831 | 0.22888 | 0.17395 | 2.9892 | 3.0945 | 2.8473 | 3.2959 | 3.1631 | 122.2321 | 3.0029 | -0.1831 | 3.2959 | 3.1631 | 3.0029 | 2.8473 | 122.2321 | -119.014 | -122.1863
5684.1562 | 122.0947 | -3.2318 | 118.8171 | -0.15984 | 0.014969 | -0.015327 | 0.046083 | 0.044346 | 0.05526 | 0.17606 | 0.036621 | 0.064087 | -0.16479 | 0.65002 | -0.20599 | -0.054932 | -0.36621 | 0.07782 | 118.9545 | -3.3737 | 3.067 | -118.7531 | 3.2684 | 3.8818 | -119.0231 | -0.14191 | 0.13733 | 0.20142 | 2.8656 | 3.3096 | 3.0258 | 3.2959 | 3.2684 | 122.1863 | 3.1769 | -0.14191 | 3.2959 | 3.2684 | 3.1769 | 3.0258 | 122.1863 | -118.9819 | -122.1909
5685.9062 | 122.0993 | -3.2181 | 118.8263 | -0.19035 | 0.016037 | -0.0149 | 0.050355 | 0.042637 | 0.053124 | 0.17414 | -0.068665 | 0.10071 | -0.20142 | 0.54932 | -0.31586 | -0.20142 | -0.18768 | -0.059509 | 119.0186 | -3.4149 | 3.0167 | -118.7256 | 3.1494 | 3.7674 | -119.1422 | -0.19684 | 0.19226 | 0.13275 | 3.0304 | 3.1586 | 2.9022 | 3.3188 | 3.1494 | 122.2366 | 3.0167 | -0.19684 | 3.3188 | 3.1494 | 3.0167 | 2.9022 | 122.2366 | -119.0277 | -122.2412
5687.6719 | 122.1451 | -3.1906 | 118.8217 | 0.19112 | 0.014328 | -0.010841 | 0.050569 | 0.042423 | 0.051628 | 0.17713 | 0.018311 | 0.050354 | -0.16022 | 0.63629 | -0.21515 | -0.068665 | -0.42114 | 0.027466 | 118.9407 | -3.3646 | 3.0304 | -118.7714 | 3.2089 | 3.8269 | -119.0369 | -0.17395 | 0.11902 | 0.17853 | 2.7695 | 3.2181 | 2.9755 | 3.241 | 3.2089 | 122.1313 | 3.1219 | -0.17395 | 3.241 | 3.2089 | 3.1219 | 2.9755 | 122.1313 | -118.9819 | -122.1863
5689.375 | 122.1222 | -3.1815 | 118.8309 | 0.046158 | 0.015182 | -0.017891 | 0.052064 | 0.042851 | 0.050988 | 0.17457 | -0.073242 | 0.09613 | -0.21973 | 0.52643 | -0.34332 | -0.19226 | -0.21515 | -0.11902 | 119.0552 | -3.3737 | 2.9617 | -118.7347 | 3.1082 | 3.7079 | -119.1742 | -0.19226 | 0.2243 | 0.14649 | 2.9663 | 3.0624 | 2.8381 | 3.2776 | 3.1082 | 122.2366 | 2.9892 | -0.19226 | 3.2776 | 3.1082 | 2.9892 | 2.8381 | 122.2366 | -119.0506 | -122.2046
5691.1406 | 122.1222 | -3.3005 | 118.7759 | -0.2285 | 0.0139 | -0.0149 | 0.04651 | 0.039433 | 0.053337 | 0.17735 | -0.07782 | 0.10529 | -0.20599 | 0.53101 | -0.32044 | -0.23804 | -0.1831 | -0.07782 | 118.9545 | -3.4927 | 3.0945 | -118.6707 | 3.2227 | 3.8315 | -119.0964 | -0.19226 | 0.17853 | 0.12817 | 3.1174 | 3.2227 | 2.98 | 3.4058 | 3.2227 | 122.2549 | 3.0624 | -0.19226 | 3.4058 | 3.2227 | 3.0624 | 2.98 | 122.2549 | -118.9819 | -122.2687
5692.8438 | 122.081 | -3.2867 | 118.7897 | -0.18272 | 0.014114 | -0.016609 | 0.047578 | 0.04221 | 0.053551 | 0.17692 | 0.018311 | 0.054932 | -0.16937 | 0.62256 | -0.20599 | -0.09613 | -0.32044 | 0.054932 | 118.959 | -3.4378 | 3.1174 | -118.7347 | 3.3051 | 3.9093 | -118.9957 | -0.15106 | 0.16937 | 0.18768 | 2.9663 | 3.3417 | 3.0807 | 3.3417 | 3.3051 | 122.2458 | 3.1906 | -0.15106 | 3.3417 | 3.3051 | 3.1906 | 3.0807 | 122.2458 | -118.959 | -122.2275
5694.6094 | 122.1542 | -3.2272 | 118.7988 | 0.13771 | 0.015609 | -0.012123 | 0.049287 | 0.043705 | 0.054406 | 0.17585 | 0.054932 | 0.054932 | -0.1831 | 0.61798 | -0.23804 | -0.09613 | -0.42114 | 0.018311 | 118.959 | -3.3783 | 3.0441 | -118.7439 | 3.2822 | 3.8452 | -119.0369 | -0.15106 | 0.16022 | 0.23804 | 2.8061 | 3.2455 | 2.9892 | 3.2822 | 3.2822 | 122.1863 | 3.1311 | -0.15106 | 3.2822 | 3.2822 | 3.1311 | 2.9892 | 122.1863 | -118.9819 | -122.1771
5696.375 | 122.1588 | -3.2181 | 118.8263 | 0.091934 | 0.01625 | -0.015114 | 0.049287 | 0.043064 | 0.053124 | 0.17606 | 0.036621 | 0.059509 | -0.17853 | 0.63629 | -0.23346 | -0.09613 | -0.41199 | 0.004578 | 118.9636 | -3.3875 | 3.0396 | -118.7668 | 3.2547 | 3.8544 | -119.0598 | -0.16937 | 0.13733 | 0.21515 | 2.8061 | 3.2227 | 2.9846 | 3.2776 | 3.2547 | 122.1817 | 3.1219 | -0.16937 | 3.2776 | 3.2547 | 3.1219 | 2.9846 | 122.1817 | -119.0048 | -122.2137
5698.1562 | 122.2229 | -3.1906 | 118.8126 | 0.12245 | 0.015182 | -0.016396 | 0.052064 | 0.043278 | 0.053337 | 0.17692 | -0.068665 | 0.09613 | -0.2243 | 0.49439 | -0.36621 | -0.24261 | -0.2655 | -0.10986 | 119.0002 | -3.392 | 2.9663 | -118.7164 | 3.1219 | 3.685 | -119.1788 | -0.20142 | 0.18768 | 0.15564 | 2.9251 | 3.0808 | 2.8244 | 3.2867 | 3.1219 | 122.1909 | 2.948 | -0.20142 | 3.2867 | 3.1219 | 2.948 | 2.8244 | 122.1909 | -119.0369 | -122.2046
5699.875 | 122.1085 | -3.2364 | 118.8538 | -0.037765 | 0.015396 | -0.014259 | 0.054841 | 0.043492 | 0.051628 | 0.17756 | -0.032043 | 0.091553 | -0.21515 | 0.54474 | -0.33417 | -0.21057 | -0.25177 | -0.09613 | 119.0277 | -3.4058 | 3.0212 | -118.7622 | 3.2043 | 3.7811 | -119.1879 | -0.16937 | 0.17395 | 0.18311 | 2.9846 | 3.1403 | 2.9022 | 3.3279 | 3.2043 | 122.2641 | 3.0258 | -0.16937 | 3.3279 | 3.2043 | 3.0258 | 2.9022 | 122.2641 | -119.0689 | -122.2595
5701.6406 | 122.2275 | -3.1128 | 118.9041 | 0.061417 | 0.015396 | -0.016823 | 0.043947 | 0.04221 | 0.052269 | 0.17564 | -0.022888 | 0.050354 | -0.17853 | 0.54474 | -0.27008 | -0.16022 | -0.36621 | -0.036621 | 119.1147 | -3.3142 | 2.9343 | -118.8538 | 3.0899 | 3.6575 | -119.1742 | -0.20142 | 0.21057 | 0.15564 | 2.7466 | 3.0762 | 2.8427 | 3.1631 | 3.0899 | 122.2275 | 2.9526 | -0.20142 | 3.1631 | 3.0899 | 2.9526 | 2.8427 | 122.2275 | -119.0826 | -122.2183
5703.4062 | 122.1405 | -3.1815 | 118.8721 | -0.23613 | 0.015182 | -0.013832 | 0.051637 | 0.04456 | 0.050988 | 0.1767 | -0.07782 | 0.10071 | -0.23804 | 0.49439 | -0.33875 | -0.26093 | -0.19226 | -0.10986 | 119.1147 | -3.3737 | 2.9434 | -118.7714 | 3.1036 | 3.6758 | -119.2108 | -0.19226 | 0.24262 | 0.16022 | 2.9892 | 3.0716 | 2.8427 | 3.2822 | 3.1036 | 122.2961 | 2.9205 | -0.19226 | 3.2822 | 3.1036 | 2.9205 | 2.8427 | 122.2961 | -119.1101 | -122.2458
5705.1094 | 122.081 | -3.1586 | 118.9453 | -0.15221 | 0.015823 | -0.015968 | 0.050782 | 0.044132 | 0.052697 | 0.17542 | -0.041199 | 0.09613 | -0.21057 | 0.54016 | -0.29297 | -0.20599 | -0.25635 | -0.059509 | 119.101 | -3.3417 | 2.948 | -118.8492 | 3.1174 | 3.6987 | -119.2383 | -0.18311 | 0.15564 | 0.16937 | 2.9022 | 3.0991 | 2.8656 | 3.2547 | 3.1174 | 122.2595 | 2.9526 | -0.18311 | 3.2547 | 3.1174 | 2.9526 | 2.8656 | 122.2595 | -119.1559 | -122.287
5706.875 | 122.1497 | -3.1586 | 118.9133 | 0.02327 | 0.014114 | -0.017036 | 0.050996 | 0.045628 | 0.050133 | 0.1767 | -0.045776 | 0.082397 | -0.21973 | 0.45319 | -0.36621 | -0.25635 | -0.23804 | -0.13275 | 119.1284 | -3.3371 | 2.9388 | -118.8309 | 3.1128 | 3.6118 | -119.2795 | -0.17853 | 0.21515 | 0.17395 | 2.9205 | 3.0258 | 2.7924 | 3.241 | 3.1128 | 122.287 | 2.9022 | -0.17853 | 3.241 | 3.1128 | 2.9022 | 2.7924 | 122.287 | -119.133 | -122.2504
5708.5781 | 122.0993 | -3.1677 | 118.927 | -0.20561 | 0.014328 | -0.015968 | 0.045015 | 0.041996 | 0.05526 | 0.17371 | 0.041199 | 0.068665 | -0.16479 | 0.59052 | -0.21057 | -0.11444 | -0.37079 | 0.032043 | 119.0781 | -3.3188 | 3.0029 | -118.8583 | 3.2089 | 3.7582 | -119.1376 | -0.15106 | 0.15106 | 0.20599 | 2.7969 | 3.1998 | 2.9572 | 3.2364 | 3.2089 | 122.2458 | 3.0533 | -0.15106 | 3.2364 | 3.2089 | 3.0533 | 2.9572 | 122.2458 | -119.0918 | -122.2458
5710.3438 | 122.1039 | -3.1586 | 118.9362 | -0.068283 | 0.013473 | -0.014473 | 0.052278 | 0.045414 | 0.051628 | 0.17585 | -0.013733 | 0.068665 | -0.2243 | 0.5127 | -0.31128 | -0.20599 | -0.27924 | -0.059509 | 119.1101 | -3.3279 | 2.9343 | -118.8675 | 3.1448 | 3.6713 | -119.2474 | -0.16937 | 0.17395 | 0.21057 | 2.8793 | 3.0991 | 2.8473 | 3.2272 | 3.1448 | 122.2687 | 2.9526 | -0.16937 | 3.2272 | 3.1448 | 2.9526 | 2.8473 | 122.2687 | -119.1605 | -122.2641
5712.0469 | 122.1542 | -3.1769 | 118.9041 | -0.14458 | 0.014541 | -0.020882 | 0.045442 | 0.043919 | 0.05291 | 0.1767 | 0.032043 | 0.054932 | -0.16479 | 0.57678 | -0.21515 | -0.10529 | -0.3891 | 0.045776 | 119.0689 | -3.3371 | 3.0121 | -118.8492 | 3.2089 | 3.7537 | -119.1193 | -0.16022 | 0.16479 | 0.19684 | 2.7878 | 3.2227 | 2.9617 | 3.2318 | 3.2089 | 122.2458 | 3.0716 | -0.16022 | 3.2318 | 3.2089 | 3.0716 | 2.9617 | 122.2458 | -119.0689 | -122.2412
5713.7969 | 122.1085 | -3.2043 | 118.8995 | -0.19798 | 0.014328 | -0.014046 | 0.053773 | 0.043278 | 0.052056 | 0.17799 | -0.064087 | 0.10071 | -0.24719 | 0.44861 | -0.37994 | -0.28381 | -0.28839 | -0.12817 | 119.0643 | -3.4012 | 2.9572 | -118.7988 | 3.1403 | 3.653 | -119.2795 | -0.19684 | 0.16479 | 0.1831 | 2.916 | 3.0762 | 2.8244 | 3.3051 | 3.1403 | 122.2687 | 2.9205 | -0.19684 | 3.3051 | 3.1403 | 2.9205 | 2.8244 | 122.2687 | -119.1467 | -122.3007
5715.5781 | 122.1588 | -3.2364 | 118.84 | -0.25902 | 0.014114 | -0.016396 | 0.049287 | 0.043705 | 0.051842 | 0.17756 | -0.10071 | 0.086975 | -0.23346 | 0.36163 | -0.43488 | -0.34332 | -0.27008 | -0.19226 | 119.0781 | -3.4378 | 3.0029 | -118.7531 | 3.1357 | 3.598 | -119.2749 | -0.20142 | 0.23804 | 0.13275 | 2.9663 | 3.0441 | 2.8015 | 3.3234 | 3.1357 | 122.3145 | 2.8931 | -0.20142 | 3.3234 | 3.1357 | 2.8931 | 2.8015 | 122.3145 | -119.0735 | -122.2778
5717.2812 | 122.2229 | -3.2089 | 118.8217 | 0.061417 | 0.01625 | -0.010841 | 0.052278 | 0.04456 | 0.050133 | 0.17606 | -0.073242 | 0.082397 | -0.21973 | 0.39368 | -0.43488 | -0.32959 | -0.33417 | -0.23346 | 119.0735 | -3.4241 | 2.9892 | -118.7393 | 3.1357 | 3.6026 | -119.2566 | -0.21515 | 0.25177 | 0.14649 | 2.8748 | 2.9755 | 2.774 | 3.2913 | 3.1357 | 122.2824 | 2.8793 | -0.21515 | 3.2913 | 3.1357 | 2.8793 | 2.774 | 122.2824 | -119.0414 | -122.2458
5719.0469 | 122.2458 | -3.2181 | 118.8263 | 0.038529 | 0.013046 | -0.017677 | 0.048219 | 0.041783 | 0.053551 | 0.17713 | -0.027466 | 0.054932 | -0.18768 | 0.45319 | -0.35248 | -0.2243 | -0.43945 | -0.12817 | 119.0048 | -3.4012 | 3.0304 | -118.7714 | 3.1906 | 3.6713 | -119.1788 | -0.18311 | 0.17853 | 0.16022 | 2.7786 | 3.0899 | 2.8656 | 3.273 | 3.1906 | 122.2229 | 2.9938 | -0.18311 | 3.273 | 3.1906 | 2.9938 | 2.8656 | 122.2229 | -119.014 | -122.2275
5720.75 | 122.2321 | -3.2135 | 118.84 | -0.075912 | 0.012832 | -0.020241 | 0.045442 | 0.044346 | 0.053765 | 0.17585 | -0.004578 | 0.064087 | -0.18768 | 0.4715 | -0.31128 | -0.18768 | -0.43945 | -0.064087 | 119.0277 | -3.4149 | 3.0258 | -118.7759 | 3.2089 | 3.685 | -119.1513 | -0.20142 | 0.18768 | 0.1831 | 2.774 | 3.1494 | 2.9022 | 3.2776 | 3.2089 | 122.2412 | 3.0258 | -0.20142 | 3.2776 | 3.2089 | 3.0258 | 2.9022 | 122.2412 | -119.0277 | -122.2549
5722.5156 | 121.3577 | -39.6149 | 80.8685 | 0.099564 | 0.012191 | -0.015541 | 0.056764 | 0.026615 | 0.029198 | 0.12373 | -0.050354 | 0.10071 | -0.21057 | -0.10071 | -0.16479 | -0.14191 | -0.15106 | -0.004578 | 80.5893 | -40.9378 | 39.4043 | -80.7678 | 39.5645 | 39.5142 | -81.0333 | -1.3229 | -0.27924 | 0.16022 | 39.4638 | 39.6103 | 39.4501 | 39.7156 | 39.5645 | 120.2042 | 39.473 | -1.3229 | 39.7156 | 39.5645 | 39.473 | 39.4501 | 120.2042 | -81.0791 | -121.8063
5724.2188 | 120.7123 | -11.6592 | 109.7397 | -0.19798 | 0.016891 | -0.021309 | 0.053773 | 0.040501 | 0.047356 | 0.16132 | -0.059509 | 0.086975 | -0.19684 | -0.27008 | -0.35248 | -0.34332 | -0.29297 | -0.19226 | 109.2865 | -10.7712 | 11.4624 | -109.6527 | 11.5997 | 11.3892 | -110.0922 | 0.88806 | -0.45319 | 0.13733 | 11.3663 | 11.467 | 11.3068 | 11.7462 | 11.5997 | 120.9457 | 11.3159 | 0.88806 | 11.7462 | 11.5997 | 11.3159 | 11.3068 | 120.9457 | -109.9365 | -120.5109
5725.9844 | 121.6049 | -10.3317 | 111.1633 | -0.10643 | 0.015182 | -0.019386 | 0.049928 | 0.03986 | 0.050133 | 0.17521 | 0.022888 | 0.045776 | -0.17853 | -0.14191 | -0.1831 | -0.2243 | -0.5127 | -0.054932 | 110.7468 | -11.1328 | 10.1532 | -111.1176 | 10.3546 | 10.1898 | -111.3464 | -0.80109 | -0.41657 | 0.20142 | 9.819 | 10.2768 | 10.1486 | 10.3775 | 10.3546 | 121.0785 | 10.1074 | -0.80109 | 10.3775 | 10.3546 | 10.1074 | 10.1486 | 121.0785 | -111.3419 | -122.2961
5727.6875 | 121.6049 | -9.819 | 111.6074 | 0.16823 | 0.01326 | -0.015968 | 0.074495 | 0.041569 | 0.048638 | 0.16666 | 0.045776 | 0.032043 | -0.16479 | -0.19226 | -0.27924 | -0.23804 | -0.54932 | -0.10529 | 111.9553 | -9.906 | 9.6542 | -111.5753 | 9.8648 | 9.6268 | -111.8866 | -0.086975 | 0.3479 | 0.21057 | 9.2697 | 9.7137 | 9.5398 | 9.8511 | 9.8648 | 121.7743 | 9.581 | -0.086975 | 9.8511 | 9.8648 | 9.581 | 9.5398 | 121.7743 | -111.7722 | -121.5134
5729.4531 | 121.7377 | -11.0046 | 110.5453 | 0.099564 | 0.011551 | -0.011269 | 0.056337 | 0.038151 | 0.048638 | 0.18418 | 0 | 0.032043 | -0.20142 | -0.16937 | -0.28839 | -0.23804 | -0.49896 | -0.1236 | 110.8704 | -11.0413 | 10.8032 | -110.5133 | 11.0046 | 10.8353 | -110.8337 | -0.036621 | 0.32501 | 0.20142 | 10.5057 | 10.881 | 10.7162 | 11.0367 | 11.0046 | 121.875 | 10.7666 | -0.036621 | 11.0367 | 11.0046 | 10.7666 | 10.7162 | 121.875 | -110.7468 | -121.5866
5731.1562 | 121.0922 | -19.6152 | 102.475 | -0.11406 | 0.015396 | -0.015114 | 0.0683 | 0.035588 | 0.041161 | 0.17222 | 0 | 0.09613 | -0.21057 | -0.11444 | -0.28381 | -0.25177 | -0.33417 | -0.10986 | 103.2166 | -18.5852 | 19.4046 | -102.3788 | 19.6152 | 19.5007 | -102.7588 | 1.03 | 0.74158 | 0.21057 | 19.281 | 19.5053 | 19.3314 | 19.7113 | 19.6152 | 122.8317 | 19.3634 | 1.03 | 19.7113 | 19.6152 | 19.3634 | 19.3314 | 122.8317 | -102.6855 | -121.0602
5732.9219 | 121.3989 | -14.2914 | 107.4371 | -0.16747 | 0.012619 | -0.018318 | 0.22168 | 0.036656 | 0.047356 | 0.33863 | 0.022888 | 0.059509 | -0.16479 | -0.068665 | -0.21057 | -0.17395 | -0.45319 | -0.027466 | 107.3364 | -14.5157 | 14.1266 | -107.3776 | 14.3143 | 14.2227 | -107.6477 | -0.2243 | -0.10071 | 0.18768 | 13.8382 | 14.2639 | 14.0808 | 14.3509 | 14.3143 | 121.6278 | 14.1174 | -0.2243 | 14.3509 | 14.3143 | 14.1174 | 14.0808 | 121.6278 | -107.6019 | -121.9528
5734.6406 | 121.8246 | -10.3226 | 111.3007 | 0.038529 | 0.014969 | -0.017464 | 0.055269 | 0.040501 | 0.049706 | 0.17542 | -0.018311 | 0.068665 | -0.16937 | -0.15564 | -0.32501 | -0.27466 | -0.46234 | -0.14648 | 111.5479 | -10.4095 | 10.1532 | -111.232 | 10.3043 | 10.1669 | -111.6257 | -0.086975 | 0.24719 | 0.15106 | 9.8602 | 10.1761 | 9.9976 | 10.3912 | 10.3043 | 121.8704 | 10.0479 | -0.086975 | 10.3912 | 10.3043 | 10.0479 | 9.9976 | 121.8704 | -111.47 | -121.7102
5736.4062 | 121.669 | -10.5698 | 111.1084 | -0.16747 | 0.013473 | -0.011055 | 0.076204 | 0.039646 | 0.046929 | 0.18546 | -0.027466 | 0.082397 | -0.23804 | -0.15106 | -0.32959 | -0.31128 | -0.36621 | -0.16022 | 111.2961 | -10.7071 | 10.3317 | -111.026 | 10.5423 | 10.4187 | -111.438 | -0.13733 | 0.18768 | 0.21057 | 10.2036 | 10.4095 | 10.2402 | 10.6522 | 10.5423 | 121.8658 | 10.2585 | -0.13733 | 10.6522 | 10.5423 | 10.2585 | 10.2402 | 121.8658 | -111.3464 | -121.8155
5738.1719 | 121.843 | -25.6531 | 95.9244 | 0.084305 | 0.016464 | -0.016823 | 0.2862 | 0.028111 | 0.041588 | 0.37986 | 0.013733 | 0.059509 | -0.17853 | -0.009155 | -0.17853 | -0.07782 | -0.34332 | 0.036621 | 96.4828 | -25.4242 | 25.4745 | -95.8649 | 25.6668 | 25.6439 | -96.1029 | 0.22888 | 0.55847 | 0.19226 | 25.3098 | 25.6897 | 25.4745 | 25.7126 | 25.6668 | 122.1359 | 25.5753 | 0.22888 | 25.7126 | 25.6668 | 25.5753 | 25.4745 | 122.1359 | -96.1029 | -121.3486
5739.9375 | 121.7972 | -26.0422 | 95.549 | 0.11482 | 0.014755 | -0.012337 | 0.060395 | 0.030888 | 0.037957 | 0.14851 | -0.07782 | 0.091553 | -0.21057 | -0.14648 | -0.2655 | -0.23804 | -0.26093 | -0.13275 | 95.7779 | -26.4313 | 25.8316 | -95.4575 | 25.9644 | 25.8957 | -95.8145 | -0.3891 | 0.22888 | 0.13275 | 25.7812 | 25.9094 | 25.7767 | 26.1337 | 25.9644 | 121.8201 | 25.8041 | -0.3891 | 26.1337 | 25.9644 | 25.8041 | 25.7767 | 121.8201 | -95.7596 | -121.9803
5741.7031 | 121.8613 | -17.7017 | 103.9856 | 0.069046 | 0.012832 | -0.017464 | 0.038179 | 0.038365 | 0.045006 | 0.15043 | -0.018311 | 0.041199 | -0.20599 | -0.13275 | -0.24719 | -0.2243 | -0.42114 | -0.10071 | 104.1321 | -17.8665 | 17.4957 | -103.9444 | 17.6834 | 17.569 | -104.2328 | -0.1648 | 0.14648 | 0.18768 | 17.2806 | 17.601 | 17.4545 | 17.7429 | 17.6834 | 121.8338 | 17.4774 | -0.1648 | 17.7429 | 17.6834 | 17.4774 | 17.4545 | 121.8338 | -104.1916 | -121.8521
5743.4062 | 121.17 | -13.9389 | 107.7942 | -0.15984 | 0.012619 | -0.0149 | 0.048005 | 0.036656 | 0.044792 | 0.15556 | -0.045776 | 0.09613 | -0.2243 | -0.17853 | -0.31586 | -0.31128 | -0.3067 | -0.15564 | 107.8262 | -14.241 | 13.7146 | -107.6981 | 13.8931 | 13.7604 | -108.11 | -0.30212 | 0.032044 | 0.17853 | 13.6322 | 13.7833 | 13.623 | 14.035 | 13.8931 | 121.7651 | 13.6276 | -0.30212 | 14.035 | 13.8931 | 13.6276 | 13.623 | 121.7651 | -108.0185 | -122.0352
5745.2188 | 121.7148 | -14.2181 | 107.5424 | -0.060654 | 0.013473 | -0.011055 | 0.050569 | 0.03751 | 0.045861 | 0.15919 | -0.013733 | 0.07782 | -0.20142 | -0.16937 | -0.31586 | -0.27466 | -0.37994 | -0.16479 | 107.5516 | -14.534 | 14.0167 | -107.4646 | 14.2044 | 14.0488 | -107.8583 | -0.31586 | 0.009156 | 0.18768 | 13.8382 | 14.0533 | 13.9023 | 14.296 | 14.2044 | 121.7697 | 13.9435 | -0.31586 | 14.296 | 14.2044 | 13.9435 | 13.9023 | 121.7697 | -107.7438 | -122.0764
5746.9375 | 121.9391 | -17.6514 | 103.8437 | 0.076676 | 0.017532 | -0.0095597 | 0.052491 | 0.038792 | 0.043297 | 0.16944 | -0.064087 | 0.10986 | -0.20142 | -0.19684 | -0.32044 | -0.32501 | -0.32959 | -0.22888 | 104.9515 | -17.1661 | 17.45 | -103.7338 | 17.5873 | 17.4545 | -104.1641 | 0.48523 | 1.1078 | 0.13733 | 17.3218 | 17.4225 | 17.3309 | 17.7612 | 17.5873 | 122.6028 | 17.3264 | 0.48523 | 17.7612 | 17.5873 | 17.3264 | 17.3309 | 122.6028 | -104.0451 | -121.0098
5748.7031 | 121.9482 | -23.5886 | 98.0621 | 0.0080111 | 0.014541 | -0.015114 | 0.036897 | 0.032597 | 0.042443 | 0.1421 | -0.018311 | 0.054932 | -0.19226 | -0.12817 | -0.18768 | -0.1831 | -0.38452 | -0.068665 | 98.1857 | -23.8403 | 23.3963 | -98.0072 | 23.5703 | 23.4604 | -98.2498 | -0.25177 | 0.1236 | 0.17395 | 23.204 | 23.5199 | 23.4009 | 23.6435 | 23.5703 | 121.7743 | 23.4055 | -0.25177 | 23.6435 | 23.5703 | 23.4055 | 23.4009 | 121.7743 | -98.2544 | -121.9025
5750.4375 | 121.9025 | -31.1234 | 90.5319 | 0.16823 | 0.014114 | -0.012764 | 0.042878 | 0.02747 | 0.036248 | 0.13227 | 0.045776 | 0.045776 | -0.1831 | -0.013733 | -0.10529 | -0.054932 | -0.40283 | 0.032043 | 90.6372 | -31.3431 | 30.9402 | -90.4861 | 31.1691 | 31.1096 | -90.6372 | -0.21973 | 0.10529 | 0.22888 | 30.7205 | 31.1554 | 31.0181 | 31.1691 | 31.1691 | 121.7606 | 31.0684 | -0.21973 | 31.1691 | 31.1691 | 31.0684 | 31.0181 | 121.7606 | -90.715 | -121.875
5752.2031 | 121.9025 | -28.0289 | 93.6356 | 0.084305 | 0.013046 | -0.0149 | 0.039247 | 0.028324 | 0.039238 | 0.13718 | 0.027466 | 0.054932 | -0.17395 | -0.050354 | -0.14648 | -0.10071 | -0.39825 | 0 | 93.7912 | -28.2578 | 27.8549 | -93.5806 | 28.0563 | 27.9785 | -93.782 | -0.22888 | 0.15564 | 0.20142 | 27.6306 | 28.0289 | 27.8824 | 28.0838 | 28.0563 | 121.8201 | 27.9282 | -0.22888 | 28.0838 | 28.0563 | 27.9282 | 27.8824 | 121.8201 | -93.8095 | -121.8933
5753.9688 | 121.9391 | -28.2669 | 93.4708 | 0.00038159 | 0.013473 | -0.017036 | 0.03946 | 0.027043 | 0.038384 | 0.1359 | -0.018311 | 0.064087 | -0.19226 | -0.10071 | -0.16479 | -0.14191 | -0.33875 | -0.027466 | 93.4525 | -28.6102 | 28.0746 | -93.4067 | 28.2486 | 28.1662 | -93.6356 | -0.34332 | -0.01831 | 0.17395 | 27.9282 | 28.2394 | 28.1021 | 28.331 | 28.2486 | 121.7194 | 28.125 | -0.34332 | 28.331 | 28.2486 | 28.125 | 28.1021 | 121.7194 | -93.663 | -122.081
5755.75 | 121.312 | -43.7119 | 84.6542 | 0.18349 | 0.014328 | -0.021309 | 0.52802 | -0.0073507 | 0.0007862 | 0.52918 | -0.050354 | 0.10529 | -0.20142 | 0.34332 | 0.23346 | 0.34332 | 0.32044 | 0.43488 | 29.1641 | -92.5369 | 43.5104 | -84.5489 | 43.6615 | 44.0552 | -84.4208 | -48.8251 | -55.4901 | 0.15106 | 44.0323 | 44.1467 | 43.9453 | 43.8171 | 43.6615 | 72.876 | 44.0552 | -48.8251 | 43.8171 | 43.6615 | 44.0552 | 43.9453 | 72.876 | -84.8557 | -177.1912
5757.5156 | 122.0856 | -118.364 | 3.2272 | 0.16823 | 0.014328 | -0.016396 | 0.049928 | -0.018886 | -0.014167 | 0.020119 | 0.036621 | 0.091553 | -0.15564 | 0.52185 | 0.53558 | 0.57678 | 0.29297 | 0.68665 | 3.3463 | -118.7256 | 118.2083 | -3.1357 | 118.4006 | 118.8858 | -2.6917 | -0.36163 | 0.11902 | 0.19226 | 118.6569 | 119.0506 | 118.8995 | 118.4555 | 118.4006 | 121.7102 | 118.9407 | -0.36163 | 118.4555 | 118.4006 | 118.9407 | 118.8995 | 121.7102 | -3.3829 | -121.9528
5759.2812 | 122.1497 | -119.6915 | 1.9913 | 0.00038159 | 0.013473 | -0.013618 | 0.04886 | -0.023159 | -0.012886 | 0.020333 | -0.018311 | 0.091553 | -0.13733 | 0.47607 | 0.54016 | 0.54932 | 0.37537 | 0.66376 | 2.2797 | -119.9341 | 119.5541 | -1.8997 | 119.6732 | 120.1675 | -1.4511 | -0.24262 | 0.28839 | 0.11902 | 120.0668 | 120.3552 | 120.2316 | 119.783 | 119.6732 | 121.9711 | 120.2408 | -0.24262 | 119.783 | 119.6732 | 120.2408 | 120.2316 | 121.9711 | -2.1286 | -121.9254
5760.9844 | 122.0627 | -118.0298 | 3.6758 | -0.20561 | 0.013046 | -0.018959 | 0.04651 | -0.021023 | -0.012672 | 0.020546 | 0.059509 | 0.082397 | -0.14648 | 0.54932 | 0.55847 | 0.59967 | 0.33417 | 0.737 | 3.7857 | -118.3365 | 117.8833 | -3.5934 | 118.0893 | 118.5791 | -3.1174 | -0.3067 | 0.10986 | 0.20599 | 118.364 | 118.7668 | 118.5883 | 118.1122 | 118.0893 | 121.8155 | 118.6295 | -0.3067 | 118.1122 | 118.0893 | 118.6295 | 118.5883 | 121.8155 | -3.8223 | -122.0123
5762.75 | 122.1451 | -118.428 | 3.2547 | 0.091934 | 0.016678 | -0.014046 | 0.05121 | -0.021877 | -0.014381 | 0.022469 | -0.032043 | 0.11902 | -0.1831 | 0.43488 | 0.45776 | 0.48523 | 0.41657 | 0.59967 | 3.3554 | -118.7897 | 118.2449 | -3.1357 | 118.396 | 118.8629 | -2.7969 | -0.36163 | 0.10071 | 0.15106 | 118.8446 | 119.0277 | 118.8858 | 118.5471 | 118.396 | 121.7834 | 118.9133 | -0.36163 | 118.5471 | 118.396 | 118.9133 | 118.8858 | 121.7834 | -3.4378 | -122.0444
5764.5156 | 122.0123 | -118.7027 | 3.1357 | -0.19035 | 0.014969 | -0.012764 | 0.047151 | -0.021877 | -0.011818 | 0.020119 | 0.059509 | 0.09613 | -0.13275 | 0.55389 | 0.5722 | 0.61798 | 0.33875 | 0.76446 | 3.1998 | -118.9728 | 118.5699 | -3.0396 | 118.7622 | 119.2566 | -2.5635 | -0.27008 | 0.064087 | 0.19226 | 119.0414 | 119.4672 | 119.2749 | 118.7988 | 118.7622 | 121.9025 | 119.3207 | -0.27008 | 118.7988 | 118.7622 | 119.3207 | 119.2749 | 121.9025 | -3.2684 | -122.1085
5766.2812 | 122.168 | -120.6299 | 1.0986 | 0.076676 | 0.011123 | -0.016182 | 0.050996 | -0.023372 | -0.013313 | 0.022255 | 0.036621 | 0.07782 | -0.14191 | 0.54016 | 0.54932 | 0.59967 | 0.31586 | 0.69122 | 1.2039 | -120.9091 | 120.488 | -1.0208 | 120.6665 | 121.17 | -0.54932 | -0.27924 | 0.10529 | 0.17853 | 120.9457 | 121.3211 | 121.1792 | 120.7077 | 120.6665 | 121.8338 | 121.2296 | -0.27924 | 120.7077 | 120.6665 | 121.2296 | 121.1792 | 121.8338 | -1.2405 | -122.0078
5767.9844 | 122.0627 | -120.6985 | 1.1444 | -0.20561 | 0.012191 | -0.016396 | 0.052705 | -0.019741 | -0.014808 | 0.02076 | -0.032043 | 0.12817 | -0.1831 | 0.47607 | 0.49896 | 0.50812 | 0.48523 | 0.64545 | 1.2909 | -120.9412 | 120.5154 | -1.0162 | 120.6665 | 121.1746 | -0.64545 | -0.24262 | 0.14648 | 0.15106 | 121.1838 | 121.344 | 121.1975 | 120.8267 | 120.6665 | 121.9894 | 121.2067 | -0.24262 | 120.8267 | 120.6665 | 121.2067 | 121.1975 | 121.9894 | -1.3275 | -122.0856
5769.75 | 122.0261 | -120.7077 | 1.181 | -0.068283 | 0.012832 | -0.015541 | 0.055482 | -0.020809 | -0.014381 | 0.019264 | 0.018311 | 0.12817 | -0.18768 | 0.52643 | 0.5127 | 0.55847 | 0.44403 | 0.65918 | 1.2863 | -120.9641 | 120.52 | -1.0529 | 120.726 | 121.2341 | -0.66834 | -0.25635 | 0.10529 | 0.20599 | 121.1517 | 121.3669 | 121.2204 | 120.8359 | 120.726 | 121.994 | 121.2662 | -0.25635 | 120.8359 | 120.726 | 121.2662 | 121.2204 | 121.994 | -1.3687 | -122.1451
5771.5156 | 122.1085 | -120.7077 | 1.149 | -0.11406 | 0.012619 | -0.016182 | 0.054628 | -0.022091 | -0.013313 | 0.022682 | 0.041199 | 0.09613 | -0.14648 | 0.54932 | 0.59967 | 0.61798 | 0.36163 | 0.75073 | 1.2863 | -120.9137 | 120.5612 | -1.0529 | 120.7489 | 121.257 | -0.54932 | -0.20599 | 0.13733 | 0.18768 | 121.0693 | 121.4584 | 121.3074 | 120.8038 | 120.7489 | 121.994 | 121.3257 | -0.20599 | 120.8038 | 120.7489 | 121.3257 | 121.3074 | 121.994 | -1.2955 | -122.0627
5773.2188 | 122.0993 | -120.5795 | 1.1673 | -0.0072479 | 0.009628 | -0.016609 | 0.049501 | -0.02145 | -0.011818 | 0.018624 | -0.009155 | 0.086975 | -0.14191 | 0.49439 | 0.53558 | 0.56763 | 0.37079 | 0.67291 | 1.268 | -120.9045 | 120.4376 | -1.0803 | 120.5704 | 121.0739 | -0.63171 | -0.32501 | 0.10071 | 0.13275 | 120.9503 | 121.2524 | 121.1151 | 120.6665 | 120.5704 | 121.8475 | 121.1472 | -0.32501 | 120.6665 | 120.5704 | 121.1472 | 121.1151 | 121.8475 | -1.3092 | -122.0718
5774.9844 | 122.0352 | -120.3964 | 1.4923 | -0.17509 | 0.014541 | -0.015327 | 0.056764 | -0.021236 | -0.013099 | 0.023751 | -0.022888 | 0.12817 | -0.19684 | 0.46692 | 0.47607 | 0.50354 | 0.49896 | 0.61798 | 1.6296 | -120.6207 | 120.1996 | -1.3641 | 120.3735 | 120.8633 | -1.0162 | -0.22431 | 0.13733 | 0.17395 | 120.8954 | 121.0144 | 120.8725 | 120.5246 | 120.3735 | 122.0261 | 120.9 | -0.22431 | 120.5246 | 120.3735 | 120.9 | 120.8725 | 122.0261 | -1.6891 | -122.113
5776.75 | 122.1359 | -120.2637 | 1.5884 | -0.014877 | 0.014114 | -0.020241 | 0.045655 | -0.021236 | -0.013313 | 0.02076 | -0.009155 | 0.11444 | -0.13733 | 0.5127 | 0.54016 | 0.56305 | 0.37994 | 0.68207 | 1.6983 | -120.5109 | 120.1263 | -1.474 | 120.2545 | 120.7764 | -1.0483 | -0.24719 | 0.10986 | 0.12817 | 120.6436 | 120.9457 | 120.8038 | 120.3781 | 120.2545 | 121.962 | 120.8267 | -0.24719 | 120.3781 | 120.2545 | 120.8267 | 120.8038 | 121.962 | -1.7258 | -122.0993
5778.5156 | 121.9986 | -120.1721 | 1.7441 | -0.083542 | 0.015182 | -0.015114 | 0.060823 | -0.020595 | -0.016731 | 0.024178 | 0.022888 | 0.1236 | -0.18768 | 0.5127 | 0.50812 | 0.53558 | 0.42114 | 0.65918 | 1.8951 | -120.3278 | 119.9844 | -1.6205 | 120.195 | 120.6848 | -1.236 | -0.15564 | 0.15106 | 0.21057 | 120.5933 | 120.8313 | 120.6802 | 120.2957 | 120.195 | 122.0673 | 120.7077 | -0.15564 | 120.2957 | 120.195 | 120.7077 | 120.6802 | 122.0673 | -1.9318 | -122.0718
5780.2812 | 122.049 | -120.1263 | 1.7853 | -0.25902 | 0.013687 | -0.016609 | 0.049714 | -0.022732 | -0.016304 | 0.02076 | 0.032043 | 0.086975 | -0.16479 | 0.51727 | 0.52643 | 0.54932 | 0.43945 | 0.70496 | 1.918 | -120.3278 | 119.9615 | -1.6983 | 120.1584 | 120.6436 | -1.2588 | -0.20142 | 0.13275 | 0.19684 | 120.5658 | 120.8313 | 120.6528 | 120.2133 | 120.1584 | 122.0444 | 120.6757 | -0.20142 | 120.2133 | 120.1584 | 120.6757 | 120.6528 | 122.0444 | -1.9501 | -122.113
5781.9844 | 122.2412 | -117.0593 | 4.6097 | 0.076676 | 0.015609 | -0.011482 | 0.05356 | -0.015255 | -0.014381 | 0.019051 | -0.032043 | 0.11444 | -0.17853 | 0.46234 | 0.46234 | 0.48981 | 0.48523 | 0.58594 | 4.7287 | -117.5125 | 116.8808 | -4.4952 | 117.0273 | 117.5217 | -4.1473 | -0.45319 | 0.11902 | 0.14648 | 117.5446 | 117.6453 | 117.5217 | 117.1738 | 117.0273 | 121.788 | 117.5491 | -0.45319 | 117.1738 | 117.0273 | 117.5491 | 117.5217 | 121.788 | -4.7882 | -122.1222
5783.75 | 122.1725 | -116.6382 | 5.1407 | 0.12245 | 0.012832 | -0.015968 | 0.047364 | -0.019527 | -0.012672 | 0.020546 | 0.082397 | 0.091553 | -0.16022 | 0.56305 | 0.58136 | 0.62714 | 0.29297 | 0.70953 | 5.2277 | -116.954 | 116.478 | -5.0491 | 116.7206 | 117.2012 | -4.5593 | -0.31586 | 0.086975 | 0.24261 | 116.9312 | 117.3477 | 117.2195 | 116.7297 | 116.7206 | 121.8658 | 117.2653 | -0.31586 | 116.7297 | 116.7206 | 117.2653 | 117.2195 | 121.8658 | -5.3009 | -122.0947
5785.5156 | 122.1542 | -119.0323 | 2.8152 | -0.25902 | 0.014541 | -0.019813 | 0.055055 | -0.020595 | -0.014381 | 0.031868 | -0.050354 | 0.13275 | -0.1831 | 0.50354 | 0.51727 | 0.51727 | 0.55847 | 0.6546 | 3.1906 | -119.0552 | 118.8492 | -2.6825 | 118.9819 | 119.5358 | -2.298 | -0.022888 | 0.37537 | 0.13275 | 119.5908 | 119.6869 | 119.5496 | 119.165 | 118.9819 | 122.2229 | 119.5496 | -0.022888 | 119.165 | 118.9819 | 119.5496 | 119.5496 | 122.2229 | -2.9984 | -121.8704
5787.2812 | 122.1497 | -119.7464 | 2.1286 | 0.15297 | 0.013687 | -0.015114 | 0.050996 | -0.021023 | -0.01374 | 0.020119 | 0.073242 | 0.086975 | -0.13275 | 0.60883 | 0.62256 | 0.67749 | 0.33417 | 0.7782 | 2.2293 | -119.9615 | 119.6136 | -2.0416 | 119.8196 | 120.3552 | -1.506 | -0.21515 | 0.10071 | 0.20599 | 120.0806 | 120.5246 | 120.369 | 119.8334 | 119.8196 | 121.9757 | 120.4239 | -0.21515 | 119.8334 | 119.8196 | 120.4239 | 120.369 | 121.9757 | -2.2614 | -122.0901
5789 | 122.1222 | -119.7876 | 2.1286 | -0.25902 | 0.013473 | -0.017464 | 0.051637 | -0.022732 | -0.014381 | 0.021614 | -0.045776 | 0.12817 | -0.18768 | 0.50354 | 0.5127 | 0.52643 | 0.59509 | 0.65918 | 2.2842 | -120.0714 | 119.5999 | -2.0004 | 119.7418 | 120.2911 | -1.6159 | -0.28381 | 0.15564 | 0.14191 | 120.3827 | 120.4468 | 120.3003 | 119.9158 | 119.7418 | 122.0718 | 120.314 | -0.28381 | 119.9158 | 119.7418 | 120.314 | 120.3003 | 122.0718 | -2.3163 | -122.2
5790.7656 | 122.2687 | -119.2108 | 2.6093 | 0.14534 | 0.011764 | -0.013191 | 0.054841 | -0.019954 | -0.012458 | 0.02845 | 0.059509 | 0.09613 | -0.15106 | 0.59052 | 0.60883 | 0.65918 | 0.32044 | 0.75989 | 2.9251 | -119.339 | 119.0598 | -2.5131 | 119.2703 | 119.8013 | -2.0004 | -0.12817 | 0.31586 | 0.21057 | 119.5312 | 119.9707 | 119.8196 | 119.3069 | 119.2703 | 122.1359 | 119.87 | -0.12817 | 119.3069 | 119.2703 | 119.87 | 119.8196 | 122.1359 | -2.7603 | -121.9482
5792.5312 | 122.2458 | -119.3893 | 2.4307 | 0.12245 | 0.01326 | -0.015327 | 0.05356 | -0.0191 | -0.014381 | 0.020546 | -0.013733 | 0.11444 | -0.1831 | 0.4715 | 0.4715 | 0.5127 | 0.46234 | 0.59967 | 2.6093 | -119.7006 | 119.2062 | -2.3163 | 119.3756 | 119.8608 | -1.9592 | -0.31128 | 0.17853 | 0.16937 | 119.8517 | 119.989 | 119.8608 | 119.5038 | 119.3756 | 121.9986 | 119.902 | -0.31128 | 119.5038 | 119.3756 | 119.902 | 119.8608 | 121.9986 | -2.6138 | -122.1313
5794.2344 | 122.1588 | -119.5129 | 2.3849 | -0.23613 | 0.014114 | -0.021095 | 0.050142 | -0.020382 | -0.012458 | 0.021187 | -0.045776 | 0.13275 | -0.20599 | 0.48065 | 0.50812 | 0.50812 | 0.56305 | 0.64545 | 2.5497 | -119.7876 | 119.3069 | -2.2522 | 119.4672 | 119.9936 | -1.8768 | -0.27466 | 0.16479 | 0.16022 | 120.076 | 120.1584 | 120.0211 | 119.6457 | 119.4672 | 122.0627 | 120.0211 | -0.27466 | 119.6457 | 119.4672 | 120.0211 | 120.0211 | 122.0627 | -2.5909 | -122.1725
5796 | 122.0947 | -119.9387 | 2.0142 | -0.20561 | 0.015823 | -0.017677 | 0.048005 | -0.020382 | -0.010963 | 0.023537 | 0.073242 | 0.086975 | -0.1236 | 0.6134 | 0.6134 | 0.65002 | 0.3891 | 0.78735 | 2.124 | -120.1401 | 119.8151 | -1.9272 | 120.0119 | 120.5521 | -1.4008 | -0.20142 | 0.10986 | 0.19684 | 120.3278 | 120.726 | 120.5521 | 120.0256 | 120.0119 | 122.0627 | 120.5887 | -0.20142 | 120.0256 | 120.0119 | 120.5887 | 120.5521 | 122.0627 | -2.1378 | -122.1542
5797.7031 | 122.0947 | -120.5154 | 1.4648 | -0.20561 | 0.013046 | -0.016182 | 0.050782 | -0.022732 | -0.01374 | 0.017128 | 0.082397 | 0.086975 | -0.15564 | 0.64087 | 0.64087 | 0.68665 | 0.41657 | 0.8194 | 1.5335 | -120.726 | 120.3598 | -1.3779 | 120.5978 | 121.1563 | -0.82398 | -0.21057 | 0.068664 | 0.23804 | 120.932 | 121.3348 | 121.1563 | 120.6024 | 120.5978 | 122.0489 | 121.2021 | -0.21057 | 120.6024 | 120.5978 | 121.2021 | 121.1563 | 122.0489 | -1.6205 | -122.1909
5799.4531 | 122.1817 | -117.3981 | 4.5181 | -0.037765 | 0.013046 | -0.016182 | 0.21805 | -0.021023 | -0.012886 | 0.18867 | 0.022888 | 0.091553 | -0.15106 | 0.59509 | 0.63171 | 0.64087 | 0.43488 | 0.78735 | 4.3442 | -117.8879 | 117.247 | -4.4266 | 117.421 | 117.9932 | -3.8864 | -0.48981 | -0.17395 | 0.17395 | 117.8329 | 118.1854 | 118.0298 | 117.4896 | 117.421 | 121.7422 | 118.0389 | -0.48981 | 117.4896 | 117.421 | 118.0389 | 118.0298 | 121.7422 | -4.6692 | -122.406
5801.1562 | 122.1954 | -120.5887 | 1.2909 | -0.23613 | 0.014969 | -0.01725 | 0.067231 | -0.021663 | -0.014595 | 0.033364 | -0.032043 | 0.14191 | -0.18768 | 0.59967 | 0.60425 | 0.62256 | 0.6546 | 0.75989 | 1.3916 | -120.932 | 120.401 | -1.149 | 120.5566 | 121.1884 | -0.68665 | -0.34332 | 0.10071 | 0.15564 | 121.2433 | 121.3486 | 121.1929 | 120.7306 | 120.5566 | 121.9803 | 121.2112 | -0.34332 | 120.7306 | 120.5566 | 121.2112 | 121.1929 | 121.9803 | -1.4786 | -122.2229
5802.9219 | 122.1451 | -120.8221 | 1.1261 | -0.19798 | 0.012405 | -0.015755 | 0.053346 | -0.022304 | -0.015022 | 0.022896 | 0.068665 | 0.11902 | -0.14648 | 0.70496 | 0.73242 | 0.73242 | 0.50354 | 0.89722 | 1.2177 | -121.0785 | 120.6757 | -1.0071 | 120.8908 | 121.5271 | -0.39368 | -0.25635 | 0.091552 | 0.21515 | 121.3257 | 121.7194 | 121.5546 | 120.9412 | 120.8908 | 122.0398 | 121.5546 | -0.25635 | 120.9412 | 120.8908 | 121.5546 | 121.5546 | 122.0398 | -1.2726 | -122.2046
5804.6875 | 122.1725 | -120.9091 | 1.0712 | -0.19798 | 0.014541 | -0.011055 | 0.0542 | -0.022518 | -0.015663 | 0.02076 | -0.013733 | 0.13733 | -0.17395 | 0.6134 | 0.6134 | 0.60883 | 0.66376 | 0.75531 | 1.2177 | -121.1838 | 120.7352 | -0.93384 | 120.8954 | 121.5225 | -0.45776 | -0.27466 | 0.14648 | 0.16022 | 121.5729 | 121.6644 | 121.5225 | 121.0464 | 120.8954 | 122.1268 | 121.5179 | -0.27466 | 121.0464 | 120.8954 | 121.5179 | 121.5225 | 122.1268 | -1.2451 | -122.2549
5806.3906 | 122.0901 | -120.0531 | 1.9455 | -0.091171 | 0.014541 | -0.015755 | 0.11551 | -0.0191 | -0.015663 | 0.081215 | 0.045776 | 0.12817 | -0.17853 | 0.64087 | 0.64087 | 0.66376 | 0.56763 | 0.78735 | 2.0554 | -120.2179 | 119.8746 | -1.8173 | 120.0989 | 120.694 | -1.3046 | -0.16479 | 0.10986 | 0.2243 | 120.6207 | 120.8405 | 120.694 | 120.1813 | 120.0989 | 122.1085 | 120.7169 | -0.16479 | 120.1813 | 120.0989 | 120.7169 | 120.694 | 122.1085 | -2.124 | -122.1634
5808.1719 | 122.1863 | -118.895 | 3.1952 | 0.13008 | 0.013687 | -0.016823 | 0.15653 | -0.019314 | -0.014595 | 0.12373 | 0.086975 | 0.10071 | -0.1236 | 0.66834 | 0.70953 | 0.74616 | 0.42114 | 0.82855 | 2.504 | -119.838 | 118.7714 | -3.0945 | 118.9819 | 119.5633 | -2.4857 | -0.94299 | -0.69122 | 0.21057 | 119.3161 | 119.7235 | 119.6045 | 118.9957 | 118.9819 | 121.3989 | 119.6411 | -0.94299 | 118.9957 | 118.9819 | 119.6411 | 119.6045 | 121.3989 | -3.3188 | -123.0331
5809.875 | 122.2549 | -120.8817 | 1.03 | 0.030899 | 0.011337 | -0.017891 | 0.047792 | -0.022304 | -0.013527 | 0.022255 | -0.013733 | 0.091553 | -0.14648 | 0.62714 | 0.67749 | 0.70038 | 0.5127 | 0.8194 | 1.1536 | -121.1517 | 120.7352 | -0.93841 | 120.8679 | 121.5088 | -0.35248 | -0.27008 | 0.1236 | 0.13275 | 121.3943 | 121.701 | 121.5591 | 120.9732 | 120.8679 | 122.0352 | 121.582 | -0.27008 | 120.9732 | 120.8679 | 121.582 | 121.5591 | 122.0352 | -1.1765 | -122.1817
5811.6406 | 122.1039 | -120.9045 | 1.0849 | -0.083542 | 0.016678 | -0.016396 | 0.055055 | -0.0238 | -0.013527 | 0.032082 | 0.050354 | 0.13275 | -0.17395 | 0.6546 | 0.63629 | 0.66834 | 0.58594 | 0.78735 | 1.2131 | -121.1609 | 120.7306 | -0.95215 | 120.9549 | 121.5591 | -0.44861 | -0.25635 | 0.12817 | 0.2243 | 121.4905 | 121.6919 | 121.5408 | 121.0373 | 120.9549 | 122.1176 | 121.5729 | -0.25635 | 121.0373 | 120.9549 | 121.5729 | 121.5408 | 122.1176 | -1.2589 | -122.2458
5813.3281 | 122.1542 | -120.8221 | 1.1627 | -0.18272 | 0.014755 | -0.015968 | 0.047792 | -0.021877 | -0.013099 | 0.02076 | 0.07782 | 0.10071 | -0.12817 | 0.69122 | 0.71411 | 0.74616 | 0.48981 | 0.87891 | 1.236 | -121.0876 | 120.694 | -1.062 | 120.9 | 121.5134 | -0.44861 | -0.2655 | 0.073242 | 0.20599 | 121.312 | 121.701 | 121.5363 | 120.9229 | 120.9 | 122.0581 | 121.5683 | -0.2655 | 120.9229 | 120.9 | 121.5683 | 121.5363 | 122.0581 | -1.2909 | -122.2504
5815.1094 | 122.1542 | -120.8267 | 1.1581 | -0.075912 | 0.013046 | -0.012764 | 0.057405 | -0.019954 | -0.014167 | 0.021828 | 0.032043 | 0.13733 | -0.17395 | 0.60425 | 0.59967 | 0.63171 | 0.57678 | 0.74158 | 1.2589 | -121.0785 | 120.6528 | -1.0208 | 120.8588 | 121.431 | -0.55847 | -0.25177 | 0.10071 | 0.20599 | 121.4035 | 121.5683 | 121.4264 | 120.9641 | 120.8588 | 122.0856 | 121.4584 | -0.25177 | 120.9641 | 120.8588 | 121.4584 | 121.4264 | 122.0856 | -1.3321 | -122.2366
5816.8281 | 122.1268 | -120.8588 | 1.1307 | -0.083542 | 0.015823 | -0.017464 | 0.055482 | -0.022091 | -0.01609 | 0.023537 | 0.054932 | 0.12817 | -0.16479 | 0.65002 | 0.65002 | 0.68665 | 0.58594 | 0.78735 | 1.2497 | -121.106 | 120.694 | -1.0025 | 120.9137 | 121.5088 | -0.48065 | -0.24719 | 0.11902 | 0.21973 | 121.4447 | 121.6461 | 121.5088 | 120.9869 | 120.9137 | 122.1085 | 121.5454 | -0.24719 | 120.9869 | 120.9137 | 121.5454 | 121.5088 | 122.1085 | -1.2955 | -122.2366
5818.5938 | 122.1451 | -120.9366 | 1.0529 | -0.060654 | 0.011764 | -0.012123 | 0.054414 | -0.021236 | -0.013527 | 0.023323 | 0.045776 | 0.12817 | -0.15106 | 0.61798 | 0.62714 | 0.64545 | 0.5722 | 0.75989 | 1.1948 | -121.1884 | 120.7855 | -0.92468 | 120.9824 | 121.5546 | -0.42572 | -0.25177 | 0.14191 | 0.19684 | 121.5088 | 121.6965 | 121.5637 | 121.0648 | 120.9824 | 122.1313 | 121.582 | -0.25177 | 121.0648 | 120.9824 | 121.582 | 121.5637 | 122.1313 | -1.2039 | -122.2412
5820.2969 | 122.1725 | -120.9366 | 1.0666 | -0.22087 | 0.014114 | -0.013618 | 0.050996 | -0.018886 | -0.016304 | 0.021401 | -0.032043 | 0.14191 | -0.16937 | 0.56763 | 0.59967 | 0.60425 | 0.63171 | 0.73242 | 1.2085 | -121.1746 | 120.7672 | -0.92468 | 120.9045 | 121.5042 | -0.46692 | -0.23804 | 0.14191 | 0.13733 | 121.5683 | 121.669 | 121.5363 | 121.0785 | 120.9045 | 122.1451 | 121.5408 | -0.23804 | 121.0785 | 120.9045 | 121.5408 | 121.5363 | 122.1451 | -1.236 | -122.2412
5822.0625 | 122.2549 | -120.9274 | 1.0208 | -0.0072479 | 0.0139 | -0.01725 | 0.046937 | -0.022732 | -0.011177 | 0.022042 | 0.013733 | 0.12817 | -0.12817 | 0.57678 | 0.64545 | 0.66834 | 0.45776 | 0.78278 | 1.149 | -121.2067 | 120.7993 | -0.89264 | 120.9412 | 121.5042 | -0.37537 | -0.27924 | 0.12817 | 0.14191 | 121.3852 | 121.7102 | 121.5729 | 121.0556 | 120.9412 | 122.0764 | 121.5958 | -0.27924 | 121.0556 | 120.9412 | 121.5958 | 121.5729 | 122.0764 | -1.149 | -122.2275
5823.75 | 122.2504 | -120.8496 | 1.0712 | 0.10719 | 0.014114 | -0.013618 | 0.056123 | -0.019954 | -0.014808 | 0.023537 | -0.013733 | 0.15564 | -0.16937 | 0.62714 | 0.65002 | 0.67291 | 0.65002 | 0.7782 | 1.2634 | -121.1563 | 120.6802 | -0.91553 | 120.8359 | 121.4767 | -0.42114 | -0.3067 | 0.19226 | 0.15564 | 121.4996 | 121.6278 | 121.4996 | 121.0052 | 120.8359 | 122.113 | 121.5225 | -0.3067 | 121.0052 | 120.8359 | 121.5225 | 121.4996 | 122.113 | -1.2405 | -122.2275
5825.5156 | 122.168 | -120.9 | 1.1124 | -0.2285 | 0.0139 | -0.019813 | 0.050569 | -0.021877 | -0.015449 | 0.019478 | -0.022888 | 0.15106 | -0.16937 | 0.58136 | 0.60883 | 0.61798 | 0.70038 | 0.75531 | 1.2405 | -121.1517 | 120.7306 | -0.9613 | 120.8771 | 121.4813 | -0.50354 | -0.25177 | 0.12817 | 0.14649 | 121.6003 | 121.6553 | 121.5088 | 121.051 | 120.8771 | 122.1405 | 121.5179 | -0.25177 | 121.051 | 120.8771 | 121.5179 | 121.5088 | 122.1405 | -1.2817 | -122.2641
5827.2812 | 122.1817 | -120.8862 | 1.1078 | -0.25139 | 0.014328 | -0.017677 | 0.049714 | -0.022091 | -0.014381 | 0.022255 | 0.022888 | 0.11444 | -0.16479 | 0.59509 | 0.62256 | 0.65002 | 0.6134 | 0.78278 | 1.2543 | -121.2021 | 120.7214 | -0.99335 | 120.9091 | 121.4813 | -0.48523 | -0.31586 | 0.14648 | 0.18768 | 121.4996 | 121.669 | 121.5088 | 121.0007 | 120.9091 | 122.1405 | 121.5363 | -0.31586 | 121.0007 | 120.9091 | 121.5363 | 121.5088 | 122.1405 | -1.2726 | -122.3099
5829.0469 | 122.1909 | -120.9137 | 1.1078 | -0.24376 | 0.014328 | -0.017891 | 0.052705 | -0.020382 | -0.015449 | 0.021187 | -0.013733 | 0.14648 | -0.15564 | 0.5722 | 0.60883 | 0.59967 | 0.66834 | 0.737 | 1.2497 | -121.2112 | 120.7581 | -0.9613 | 120.9 | 121.4859 | -0.49896 | -0.29755 | 0.14191 | 0.14191 | 121.582 | 121.6507 | 121.5225 | 121.0602 | 120.9 | 122.1634 | 121.5134 | -0.29755 | 121.0602 | 120.9 | 121.5134 | 121.5225 | 122.1634 | -1.2634 | -122.319
5830.75 | 122.1451 | -120.9229 | 1.1398 | -0.12169 | 0.011764 | -0.013832 | 0.048433 | -0.024013 | -0.010963 | 0.022896 | 0.10071 | 0.091553 | -0.13275 | 0.68665 | 0.71869 | 0.75073 | 0.4303 | 0.89264 | 1.1993 | -121.1746 | 120.7901 | -1.0483 | 121.0236 | 121.6095 | -0.42114 | -0.25177 | 0.059509 | 0.23346 | 121.3531 | 121.8155 | 121.6415 | 121.0144 | 121.0236 | 122.1222 | 121.6736 | -0.25177 | 121.0144 | 121.0236 | 121.6736 | 121.6415 | 122.1222 | -1.2726 | -122.3145
5832.5312 | 122.2733 | -120.8954 | 1.062 | 0.11482 | 0.014328 | -0.014687 | 0.050569 | -0.021023 | -0.014167 | 0.020973 | 0.073242 | 0.10529 | -0.12817 | 0.59967 | 0.63171 | 0.67291 | 0.40741 | 0.77362 | 1.1902 | -121.1838 | 120.7672 | -0.95673 | 120.9686 | 121.4951 | -0.4303 | -0.28839 | 0.12817 | 0.20142 | 121.3028 | 121.669 | 121.5271 | 121.0007 | 120.9686 | 122.0856 | 121.5683 | -0.28839 | 121.0007 | 120.9686 | 121.5683 | 121.5271 | 122.0856 | -1.1902 | -122.2458
5834.2969 | 122.1863 | -120.9457 | 1.1032 | -0.25139 | 0.013473 | -0.01725 | 0.053346 | -0.022945 | -0.014595 | 0.020973 | 0.018311 | 0.12817 | -0.15106 | 0.54016 | 0.56763 | 0.58594 | 0.58136 | 0.71411 | 1.2085 | -121.2112 | 120.7947 | -0.97504 | 120.9641 | 121.4859 | -0.53558 | -0.2655 | 0.10529 | 0.16937 | 121.5271 | 121.6599 | 121.5134 | 121.0739 | 120.9641 | 122.1542 | 121.5317 | -0.2655 | 121.0739 | 120.9641 | 121.5317 | 121.5134 | 122.1542 | -1.2543 | -122.3145
5836.0625 | 122.2321 | -120.9183 | 1.0391 | 0.15297 | 0.01326 | -0.017464 | 0.053987 | -0.019741 | -0.015236 | 0.021401 | 0.10529 | 0.09613 | -0.13733 | 0.63171 | 0.61798 | 0.67749 | 0.32501 | 0.78735 | 1.1581 | -121.1884 | 120.7809 | -0.94299 | 121.0236 | 121.55 | -0.42114 | -0.27008 | 0.11902 | 0.24262 | 121.2433 | 121.7056 | 121.5363 | 121.0144 | 121.0236 | 122.0764 | 121.5958 | -0.27008 | 121.0144 | 121.0236 | 121.5958 | 121.5363 | 122.0764 | -1.1765 | -122.2275
5837.8438 | 122.2778 | -120.9412 | 1.0483 | -0.0072479 | 0.014541 | -0.018104 | 0.047792 | -0.021663 | -0.011818 | 0.02076 | 0.022888 | 0.11902 | -0.14648 | 0.56305 | 0.58136 | 0.63629 | 0.42572 | 0.74616 | 1.1765 | -121.2479 | 120.7947 | -0.92926 | 120.9641 | 121.5042 | -0.46692 | -0.3067 | 0.12817 | 0.16937 | 121.3669 | 121.6873 | 121.5225 | 121.0602 | 120.9641 | 122.1176 | 121.5775 | -0.3067 | 121.0602 | 120.9641 | 121.5775 | 121.5225 | 122.1176 | -1.1948 | -122.2961
5839.6094 | 122.1909 | -120.9641 | 1.0574 | -0.0072479 | 0.012619 | -0.012337 | 0.059114 | -0.021877 | -0.015876 | 0.020546 | 0.018311 | 0.12817 | -0.17853 | 0.53101 | 0.52185 | 0.53101 | 0.51727 | 0.6546 | 1.1902 | -121.2479 | 120.7855 | -0.92926 | 120.9824 | 121.4951 | -0.53558 | -0.28381 | 0.13275 | 0.19684 | 121.4813 | 121.6187 | 121.4859 | 121.0922 | 120.9824 | 122.1542 | 121.4951 | -0.28381 | 121.0922 | 120.9824 | 121.4951 | 121.4859 | 122.1542 | -1.236 | -122.3053
5841.3125 | 122.1863 | -120.9824 | 1.0666 | -0.26665 | 0.016037 | -0.014473 | 0.052491 | -0.0238 | -0.010963 | 0.023964 | 0.041199 | 0.1236 | -0.14191 | 0.55847 | 0.56763 | 0.58594 | 0.51727 | 0.74158 | 1.1993 | -121.2616 | 120.8405 | -0.94299 | 121.0236 | 121.5408 | -0.49896 | -0.27924 | 0.13275 | 0.18311 | 121.4996 | 121.7239 | 121.55 | 121.106 | 121.0236 | 122.1817 | 121.5683 | -0.27924 | 121.106 | 121.0236 | 121.5683 | 121.55 | 122.1817 | -1.2085 | -122.3282
5843.1094 | 122.2733 | -120.9412 | 1.0483 | -0.068283 | 0.015609 | -0.016182 | 0.048433 | -0.022304 | -0.01139 | 0.022042 | 0.036621 | 0.11902 | -0.13275 | 0.58594 | 0.62714 | 0.67291 | 0.40283 | 0.78278 | 1.149 | -121.2524 | 120.8084 | -0.92926 | 120.9778 | 121.5271 | -0.42114 | -0.31128 | 0.10071 | 0.16937 | 121.344 | 121.7239 | 121.5683 | 121.0602 | 120.9778 | 122.0901 | 121.6141 | -0.31128 | 121.0602 | 120.9778 | 121.6141 | 121.5683 | 122.0901 | -1.181 | -122.3007
5844.875 | 122.2916 | -120.9641 | 1.0345 | -0.0072479 | 0.012619 | -0.014259 | 0.050782 | -0.022945 | -0.012458 | 0.020333 | 0.018311 | 0.1236 | -0.14191 | 0.55389 | 0.59052 | 0.61798 | 0.41657 | 0.737 | 1.1765 | -121.2387 | 120.8221 | -0.91095 | 120.9824 | 121.5179 | -0.44403 | -0.27466 | 0.14191 | 0.16022 | 121.3806 | 121.701 | 121.5546 | 121.0876 | 120.9824 | 122.1405 | 121.582 | -0.27466 | 121.0876 | 120.9824 | 121.582 | 121.5546 | 122.1405 | -1.1765 | -122.2733
5846.6562 | 122.168 | -120.9915 | 1.0849 | -0.15221 | 0.015609 | -0.014046 | 0.057405 | -0.021023 | -0.017799 | 0.022042 | 0.045776 | 0.14191 | -0.15564 | 0.56305 | 0.55847 | 0.58136 | 0.50354 | 0.71411 | 1.1902 | -121.2524 | 120.8359 | -0.94299 | 121.0373 | 121.5546 | -0.52643 | -0.26093 | 0.10529 | 0.20142 | 121.4951 | 121.7056 | 121.55 | 121.1334 | 121.0373 | 122.1817 | 121.5729 | -0.26093 | 121.1334 | 121.0373 | 121.5729 | 121.55 | 122.1817 | -1.2405 | -122.3373
5848.3594 | 122.2275 | -120.9824 | 1.0803 | -0.24376 | 0.016037 | -0.01725 | 0.053987 | -0.019527 | -0.015449 | 0.020546 | -0.022888 | 0.15106 | -0.18768 | 0.50812 | 0.52643 | 0.53558 | 0.59052 | 0.66376 | 1.2039 | -121.257 | 120.7947 | -0.92926 | 120.9595 | 121.4905 | -0.55389 | -0.27466 | 0.1236 | 0.16479 | 121.5729 | 121.6461 | 121.5088 | 121.1334 | 120.9595 | 122.1863 | 121.5179 | -0.27466 | 121.1334 | 120.9595 | 121.5179 | 121.5088 | 122.1863 | -1.268 | -122.3373
5850.0625 | 122.1817 | -121.0098 | 1.0895 | -0.14458 | 0.0139 | -0.013832 | 0.049073 | -0.022945 | -0.013527 | 0.019692 | 0.11444 | 0.10986 | -0.13275 | 0.62714 | 0.6546 | 0.68665 | 0.41657 | 0.83771 | 1.181 | -121.2204 | 120.8771 | -0.97961 | 121.1243 | 121.637 | -0.43488 | -0.21057 | 0.091552 | 0.24719 | 121.4264 | 121.8475 | 121.6644 | 121.1197 | 121.1243 | 122.1909 | 121.6965 | -0.21057 | 121.1197 | 121.1243 | 121.6965 | 121.6644 | 122.1909 | -1.2222 | -122.3099
5851.7812 | 122.2321 | -120.9641 | 1.0986 | -0.27428 | 0.015396 | -0.017036 | 0.05121 | -0.022304 | -0.015022 | 0.020333 | -0.018311 | 0.14191 | -0.17853 | 0.52185 | 0.53101 | 0.53558 | 0.6134 | 0.68665 | 1.2222 | -121.2662 | 120.7855 | -0.95673 | 120.9457 | 121.4859 | -0.56763 | -0.30212 | 0.1236 | 0.16022 | 121.5775 | 121.6507 | 121.4951 | 121.106 | 120.9457 | 122.1863 | 121.4996 | -0.30212 | 121.106 | 120.9457 | 121.4996 | 121.4951 | 122.1863 | -1.2772 | -122.3648
5853.5312 | 122.3145 | -120.9137 | 1.0941 | 0.11482 | 0.0139 | -0.012123 | 0.056123 | -0.020595 | -0.015449 | 0.020119 | -0.013733 | 0.14648 | -0.16022 | 0.51727 | 0.54016 | 0.57678 | 0.54474 | 0.65002 | 1.2268 | -121.2067 | 120.7535 | -0.94757 | 120.9 | 121.431 | -0.55389 | -0.29297 | 0.13275 | 0.14648 | 121.4584 | 121.5637 | 121.4539 | 121.0602 | 120.9 | 122.1405 | 121.4905 | -0.29297 | 121.0602 | 120.9 | 121.4905 | 121.4539 | 122.1405 | -1.2543 | -122.3007
5855.2344 | 122.1725 | -120.9778 | 1.1398 | -0.19035 | 0.013687 | -0.017036 | 0.048646 | -0.022304 | -0.012672 | 0.022042 | 0.064087 | 0.11902 | -0.12817 | 0.65918 | 0.67749 | 0.71869 | 0.43945 | 0.85602 | 1.2222 | -121.2067 | 120.8496 | -1.0208 | 121.0419 | 121.637 | -0.46234 | -0.22888 | 0.082397 | 0.19226 | 121.4172 | 121.8338 | 121.6553 | 121.0968 | 121.0419 | 122.2 | 121.6965 | -0.22888 | 121.0968 | 121.0419 | 121.6965 | 121.6553 | 122.2 | -1.268 | -122.3465
5856.9375 | 122.2504 | -120.932 | 1.1215 | -0.15221 | 0.011123 | -0.018104 | 0.049287 | -0.023372 | -0.01374 | 0.022042 | 0.07782 | 0.10986 | -0.11902 | 0.66834 | 0.69122 | 0.73242 | 0.43488 | 0.85602 | 1.2268 | -121.225 | 120.813 | -1.0117 | 121.0098 | 121.6003 | -0.4303 | -0.29297 | 0.10529 | 0.19684 | 121.3669 | 121.788 | 121.6232 | 121.0419 | 121.0098 | 122.1588 | 121.6644 | -0.29297 | 121.0419 | 121.0098 | 121.6644 | 121.6232 | 122.1588 | -1.2405 | -122.3465
5858.6719 | 122.3145 | -120.8908 | 1.1078 | 0.084305 | 0.015182 | -0.017036 | 0.055055 | -0.02145 | -0.014381 | 0.022042 | 0.009155 | 0.15106 | -0.16479 | 0.55389 | 0.56763 | 0.59052 | 0.52643 | 0.6958 | 1.2589 | -121.2112 | 120.726 | -0.95673 | 120.9 | 121.4447 | -0.54016 | -0.32043 | 0.15106 | 0.17395 | 121.4172 | 121.5866 | 121.4584 | 121.0419 | 120.9 | 122.1497 | 121.4813 | -0.32043 | 121.0419 | 120.9 | 121.4813 | 121.4584 | 122.1497 | -1.2726 | -122.319
5860.3594 | 122.2504 | -120.9137 | 1.1536 | -0.21324 | 0.013046 | -0.015755 | 0.053346 | -0.02145 | -0.01139 | 0.019905 | -0.018311 | 0.15106 | -0.15564 | 0.56305 | 0.59052 | 0.59967 | 0.65002 | 0.737 | 1.2909 | -121.2112 | 120.7581 | -1.0025 | 120.8954 | 121.4767 | -0.56305 | -0.29755 | 0.13733 | 0.13733 | 121.5637 | 121.6507 | 121.5042 | 121.0648 | 120.8954 | 122.2046 | 121.5134 | -0.29755 | 121.0648 | 120.8954 | 121.5134 | 121.5042 | 122.2046 | -1.3092 | -122.3648
5862.0781 | 122.2275 | -120.9091 | 1.1993 | -0.24376 | 0.013687 | -0.016823 | 0.050142 | -0.0238 | -0.012672 | 0.020973 | 0.073242 | 0.1236 | -0.13733 | 0.6546 | 0.67749 | 0.68207 | 0.5722 | 0.82855 | 1.3092 | -121.1884 | 120.7718 | -1.0757 | 120.9824 | 121.5637 | -0.52185 | -0.27923 | 0.10986 | 0.21057 | 121.4813 | 121.7377 | 121.5866 | 121.0327 | 120.9824 | 122.2183 | 121.5912 | -0.27923 | 121.0327 | 120.9824 | 121.5912 | 121.5866 | 122.2183 | -1.3367 | -122.3877
5863.7812 | 122.2733 | -120.7855 | 1.2314 | 0.1606 | 0.015182 | -0.01725 | 0.057191 | -0.018673 | -0.015236 | 0.023323 | 0.064087 | 0.1236 | -0.12817 | 0.69122 | 0.6958 | 0.75073 | 0.44861 | 0.84228 | 1.3504 | -121.0831 | 120.6573 | -1.1078 | 120.8496 | 121.4767 | -0.53558 | -0.29755 | 0.11902 | 0.19226 | 121.2341 | 121.6278 | 121.4813 | 120.9091 | 120.8496 | 122.1359 | 121.5363 | -0.29755 | 120.9091 | 120.8496 | 121.5363 | 121.4813 | 122.1359 | -1.3596 | -122.3145
5865.5938 | 122.3099 | -120.7489 | 1.2543 | 0.11482 | 0.013046 | -0.014259 | 0.055482 | -0.020168 | -0.015022 | 0.022896 | 0.013733 | 0.16479 | -0.16937 | 0.62714 | 0.64545 | 0.68665 | 0.55389 | 0.76904 | 1.387 | -121.0602 | 120.5795 | -1.0895 | 120.7626 | 121.376 | -0.60883 | -0.31128 | 0.13275 | 0.18311 | 121.3028 | 121.5179 | 121.3943 | 120.9137 | 120.7626 | 122.1359 | 121.4355 | -0.31128 | 120.9137 | 120.7626 | 121.4355 | 121.3943 | 122.1359 | -1.4236 | -122.3145
5867.2969 | 122.2321 | -120.7764 | 1.3458 | -0.23613 | 0.012619 | -0.014473 | 0.050142 | -0.022518 | -0.012458 | 0.022896 | 0.059509 | 0.13275 | -0.1236 | 0.71411 | 0.74158 | 0.74616 | 0.63171 | 0.88348 | 1.4374 | -121.0602 | 120.6528 | -1.2131 | 120.8359 | 121.4905 | -0.60425 | -0.28381 | 0.091553 | 0.1831 | 121.4081 | 121.6599 | 121.5179 | 120.9091 | 120.8359 | 122.2137 | 121.5225 | -0.28381 | 120.9091 | 120.8359 | 121.5225 | 121.5179 | 122.2137 | -1.4694 | -122.406
5869 | 122.3419 | -120.7031 | 1.3321 | 0.053787 | 0.014969 | -0.018745 | 0.049501 | -0.021663 | -0.014595 | 0.021828 | 0.036621 | 0.12817 | -0.11444 | 0.68665 | 0.73242 | 0.7782 | 0.58136 | 0.88806 | 1.4511 | -121.0052 | 120.5887 | -1.2039 | 120.7397 | 121.3898 | -0.59967 | -0.30212 | 0.11902 | 0.15106 | 121.2845 | 121.5912 | 121.4355 | 120.8313 | 120.7397 | 122.1542 | 121.4813 | -0.30212 | 120.8313 | 120.7397 | 121.4813 | 121.4355 | 122.1542 | -1.4465 | -122.3373
5870.7031 | 122.3328 | -120.6619 | 1.355 | 0.091934 | 0.014969 | -0.0069961 | 0.056978 | -0.022518 | -0.017158 | 0.021401 | 0.004578 | 0.15564 | -0.16479 | 0.65918 | 0.68665 | 0.68665 | 0.68207 | 0.80566 | 1.5381 | -120.9824 | 120.4971 | -1.1993 | 120.6665 | 121.3211 | -0.66833 | -0.32044 | 0.18311 | 0.16937 | 121.344 | 121.4676 | 121.3486 | 120.8176 | 120.6665 | 122.2 | 121.3486 | -0.32044 | 120.8176 | 120.6665 | 121.3486 | 121.3486 | 122.2 | -1.5198 | -122.3373
5872.3906 | 122.2687 | -120.6802 | 1.4191 | -0.15984 | 0.013046 | -0.018745 | 0.05356 | -0.023159 | -0.015236 | 0.023323 | -0.004578 | 0.13733 | -0.15564 | 0.70038 | 0.72327 | 0.74616 | 0.75531 | 0.88348 | 1.6434 | -120.8405 | 120.5246 | -1.2817 | 120.6757 | 121.3806 | -0.6958 | -0.16022 | 0.2243 | 0.15106 | 121.4355 | 121.5637 | 121.4035 | 120.8176 | 120.6757 | 122.3236 | 121.4264 | -0.16022 | 120.8176 | 120.6757 | 121.4264 | 121.4035 | 122.3236 | -1.5747 | -122.2595
5874.1406 | 122.2229 | -120.7581 | 1.355 | -0.083542 | 0.016464 | -0.021522 | 0.057618 | -0.02145 | -0.013099 | 0.022682 | 0.064087 | 0.14191 | -0.14648 | 0.73242 | 0.71869 | 0.75073 | 0.6546 | 0.8606 | 1.4786 | -120.9915 | 120.6116 | -1.2131 | 120.8221 | 121.4905 | -0.63629 | -0.23346 | 0.1236 | 0.21057 | 121.4127 | 121.6187 | 121.4767 | 120.9 | 120.8221 | 122.2366 | 121.5088 | -0.23346 | 120.9 | 120.8221 | 121.5088 | 121.4767 | 122.2366 | -1.5015 | -122.3465
5875.8594 | 122.3328 | -120.7718 | 1.2863 | -0.037765 | 0.014969 | -0.01725 | 0.047151 | -0.022732 | -0.013527 | 0.020546 | 0.036621 | 0.1236 | -0.1236 | 0.74616 | 0.78278 | 0.80566 | 0.59052 | 0.93384 | 1.4145 | -121.0693 | 120.6482 | -1.1627 | 120.8084 | 121.5179 | -0.50354 | -0.29755 | 0.12817 | 0.16022 | 121.3623 | 121.7056 | 121.5546 | 120.8954 | 120.8084 | 122.1863 | 121.5775 | -0.29755 | 120.8954 | 120.8084 | 121.5775 | 121.5546 | 122.1863 | -1.4099 | -122.3557
5877.625 | 122.3099 | -120.7672 | 1.3 | 0.1606 | 0.01326 | -0.014687 | 0.053987 | -0.022945 | -0.011818 | 0.022042 | 0.07782 | 0.13275 | -0.12817 | 0.77362 | 0.78735 | 0.82855 | 0.54474 | 0.92926 | 1.3733 | -121.0281 | 120.639 | -1.1673 | 120.845 | 121.5408 | -0.5127 | -0.26093 | 0.073242 | 0.20599 | 121.312 | 121.6965 | 121.5546 | 120.9 | 120.845 | 122.1405 | 121.5958 | -0.26093 | 120.9 | 120.845 | 121.5958 | 121.5546 | 122.1405 | -1.4282 | -122.3282
5879.3438 | 122.2641 | -120.8221 | 1.2772 | -0.19798 | 0.01326 | -0.01255 | 0.054414 | -0.023586 | -0.014167 | 0.02311 | 0 | 0.15564 | -0.16022 | 0.70038 | 0.70496 | 0.71411 | 0.74616 | 0.86517 | 1.4008 | -121.1243 | 120.6619 | -1.1215 | 120.8221 | 121.5225 | -0.5722 | -0.30212 | 0.1236 | 0.16022 | 121.5683 | 121.6873 | 121.5271 | 120.9778 | 120.8221 | 122.2229 | 121.5363 | -0.30212 | 120.9778 | 120.8221 | 121.5363 | 121.5271 | 122.2229 | -1.4374 | -122.4014
5881.0781 | 122.319 | -120.7947 | 1.268 | 0.10719 | 0.015823 | -0.017891 | 0.050569 | -0.022732 | -0.012458 | 0.020546 | 0.09613 | 0.10986 | -0.10529 | 0.76446 | 0.79651 | 0.83313 | 0.54932 | 0.92926 | 1.3733 | -121.0968 | 120.6894 | -1.1581 | 120.8908 | 121.5591 | -0.4715 | -0.30212 | 0.10529 | 0.20142 | 121.344 | 121.7239 | 121.5912 | 120.9045 | 120.8908 | 122.168 | 121.6278 | -0.30212 | 120.9045 | 120.8908 | 121.6278 | 121.5912 | 122.168 | -1.3733 | -122.3648
5882.7969 | 122.2321 | -120.8588 | 1.2955 | -0.12932 | 0.015396 | -0.012978 | 0.052919 | -0.02145 | -0.016304 | 0.020973 | 0.032043 | 0.15106 | -0.14648 | 0.73242 | 0.73242 | 0.76904 | 0.70038 | 0.88348 | 1.4053 | -121.106 | 120.7123 | -1.1444 | 120.8908 | 121.5912 | -0.56305 | -0.24719 | 0.10986 | 0.17853 | 121.5591 | 121.7422 | 121.5912 | 121.0098 | 120.8908 | 122.2641 | 121.6278 | -0.24719 | 121.0098 | 120.8908 | 121.6278 | 121.5912 | 122.2641 | -1.442 | -122.4014
5884.5 | 122.3557 | -120.7993 | 1.2497 | -0.0072479 | 0.012405 | -0.019813 | 0.045228 | -0.021877 | -0.013527 | 0.020973 | 0.022888 | 0.11902 | -0.11902 | 0.74616 | 0.78735 | 0.81482 | 0.60425 | 0.93384 | 1.3687 | -121.0968 | 120.6802 | -1.1307 | 120.8221 | 121.5454 | -0.46234 | -0.29755 | 0.11902 | 0.14191 | 121.4035 | 121.7331 | 121.5866 | 120.9183 | 120.8221 | 122.168 | 121.6141 | -0.29755 | 120.9183 | 120.8221 | 121.6141 | 121.5866 | 122.168 | -1.3687 | -122.3465
5886.25 | 122.2824 | -120.8496 | 1.2863 | -0.24376 | 0.013473 | -0.016396 | 0.051423 | -0.022518 | -0.015236 | 0.019905 | 0.022888 | 0.13733 | -0.15106 | 0.71411 | 0.72327 | 0.737 | 0.72784 | 0.8606 | 1.4236 | -121.1151 | 120.6985 | -1.149 | 120.8725 | 121.5637 | -0.56305 | -0.2655 | 0.13733 | 0.17395 | 121.5775 | 121.7102 | 121.5729 | 120.9869 | 120.8725 | 122.2733 | 121.5866 | -0.2655 | 120.9869 | 120.8725 | 121.5866 | 121.5729 | 122.2733 | -1.4374 | -122.4014
5887.9844 | 122.2549 | -120.8405 | 1.2817 | -0.12932 | 0.0139 | -0.018532 | 0.049287 | -0.023159 | -0.012245 | 0.021614 | 0.10986 | 0.1236 | -0.10986 | 0.81482 | 0.81482 | 0.84686 | 0.55847 | 0.99792 | 1.3733 | -121.1105 | 120.7306 | -1.1581 | 120.9503 | 121.6553 | -0.46692 | -0.27008 | 0.091553 | 0.21973 | 121.3989 | 121.8384 | 121.6553 | 120.9641 | 120.9503 | 122.2137 | 121.6873 | -0.27008 | 120.9641 | 120.9503 | 121.6873 | 121.6553 | 122.2137 | -1.3916 | -122.3923
5889.7344 | 122.319 | -120.8633 | 1.2405 | 0.16823 | 0.015182 | -0.012123 | 0.05356 | -0.022518 | -0.012886 | 0.022042 | 0.10071 | 0.10071 | -0.12817 | 0.78278 | 0.80109 | 0.83313 | 0.49896 | 0.95673 | 1.3184 | -121.1197 | 120.7352 | -1.1398 | 120.9641 | 121.6461 | -0.43945 | -0.25635 | 0.077819 | 0.22888 | 121.3623 | 121.8201 | 121.6644 | 120.9641 | 120.9641 | 122.1817 | 121.6965 | -0.25635 | 120.9641 | 120.9641 | 121.6965 | 121.6644 | 122.1817 | -1.3687 | -122.3602
5891.4219 | 122.2458 | -120.8725 | 1.2589 | -0.18272 | 0.014755 | -0.013191 | 0.051423 | -0.0238 | -0.013527 | 0.02076 | 0.086975 | 0.11902 | -0.091553 | 0.78278 | 0.78735 | 0.82398 | 0.62714 | 0.9613 | 1.3367 | -121.1884 | 120.7809 | -1.1398 | 120.9595 | 121.6553 | -0.4715 | -0.31586 | 0.07782 | 0.17853 | 121.4996 | 121.8338 | 121.6599 | 120.9915 | 120.9595 | 122.2092 | 121.6965 | -0.31586 | 120.9915 | 120.9595 | 121.6965 | 121.6599 | 122.2092 | -1.3504 | -122.4472
5893.125 | 122.3419 | -120.9045 | 1.2039 | 0.13008 | 0.014969 | -0.017036 | 0.052705 | -0.021023 | -0.012886 | 0.021187 | 0.11444 | 0.10529 | -0.10529 | 0.76904 | 0.78735 | 0.8194 | 0.5127 | 0.93384 | 1.3 | -121.1609 | 120.7993 | -1.0986 | 121.019 | 121.6736 | -0.41656 | -0.25635 | 0.096131 | 0.21973 | 121.4172 | 121.8384 | 121.6919 | 121.0098 | 121.019 | 122.2046 | 121.7239 | -0.25635 | 121.0098 | 121.019 | 121.7239 | 121.6919 | 122.2046 | -1.3092 | -122.3648
5894.8281 | 122.2412 | -120.7672 | 1.3824 | -0.083542 | 0.016037 | -0.014687 | 0.064454 | -0.022518 | -0.015876 | 0.028023 | 0.036621 | 0.11902 | -0.16479 | 0.75073 | 0.75531 | 0.77362 | 0.67291 | 0.91095 | 1.4557 | -121.0693 | 120.6024 | -1.2634 | 120.8038 | 121.5179 | -0.62714 | -0.30212 | 0.073242 | 0.20142 | 121.4401 | 121.6782 | 121.5225 | 120.8862 | 120.8038 | 122.2229 | 121.5408 | -0.30212 | 120.8862 | 120.8038 | 121.5408 | 121.5225 | 122.2229 | -1.5472 | -122.4518
5896.5938 | 122.3969 | -120.6802 | 1.3733 | 0.11482 | 0.015823 | -0.016182 | 0.067018 | -0.020168 | -0.015663 | 0.041268 | -0.004578 | 0.15564 | -0.15106 | 0.94757 | 0.96588 | 0.85144 | 0.7782 | 0.9201 | 1.7349 | -120.9595 | 120.5292 | -1.2177 | 120.6757 | 121.6278 | -0.40741 | -0.27924 | 0.36163 | 0.14648 | 121.4584 | 121.6003 | 121.6461 | 120.8359 | 120.6757 | 122.4152 | 121.5317 | -0.27924 | 120.8359 | 120.6757 | 121.5317 | 121.6461 | 122.4152 | -1.5244 | -122.3328
5898.3125 | 122.3007 | -119.5999 | 2.536 | -0.21324 | 0.014541 | -0.017036 | 0.057191 | -0.024441 | -0.014381 | 0.027382 | -0.036621 | 0.13275 | -0.16937 | 0.72327 | 0.75531 | 0.737 | 0.79651 | 0.88806 | 1.4557 | -120.9229 | 119.4305 | -2.4033 | 119.5633 | 120.3232 | -1.7807 | -1.3229 | -1.0803 | 0.13275 | 120.3964 | 120.488 | 120.3552 | 119.7327 | 119.5633 | 121.0556 | 120.3369 | -1.3229 | 119.7327 | 119.5633 | 120.3369 | 120.3552 | 121.0556 | -2.7054 | -123.4589
5900.0469 | 122.3877 | -120.7947 | 1.2772 | 0.069046 | 0.014969 | -0.014046 | 0.0589 | -0.019954 | -0.01374 | 0.026955 | -0.054932 | 0.14191 | -0.19226 | 0.70953 | 0.737 | 0.72784 | 0.73242 | 0.84686 | 1.4328 | -121.1243 | 120.6024 | -1.1353 | 120.7397 | 121.5042 | -0.54016 | -0.32959 | 0.15564 | 0.13733 | 121.5271 | 121.6415 | 121.5317 | 120.9366 | 120.7397 | 122.2275 | 121.5225 | -0.32959 | 120.9366 | 120.7397 | 121.5225 | 121.5317 | 122.2275 | -1.4694 | -122.4014
5901.7812 | 122.4014 | -120.7855 | 1.3229 | -0.022507 | 0.011764 | -0.017464 | 0.052064 | -0.02145 | -0.012458 | 0.025887 | -0.004578 | 0.091553 | -0.15564 | 0.7782 | 0.82398 | 0.85144 | 0.63629 | 0.96588 | 1.4374 | -121.106 | 120.6299 | -1.2314 | 120.7809 | 121.5637 | -0.49896 | -0.32044 | 0.11444 | 0.15106 | 121.4218 | 121.7514 | 121.6095 | 120.8771 | 120.7809 | 122.2229 | 121.637 | -0.32044 | 120.8771 | 120.7809 | 121.637 | 121.6095 | 122.2229 | -1.4786 | -122.4289
5903.5156 | 122.2687 | -120.8038 | 1.355 | -0.20561 | 0.012619 | -0.018104 | 0.055909 | -0.022304 | -0.015876 | 0.026528 | 0.054932 | 0.07782 | -0.15106 | 0.84228 | 0.86975 | 0.90637 | 0.65002 | 1.062 | 1.4282 | -121.0831 | 120.6528 | -1.2772 | 120.8588 | 121.6461 | -0.48523 | -0.27924 | 0.073243 | 0.20599 | 121.4539 | 121.8658 | 121.6736 | 120.8817 | 120.8588 | 122.2321 | 121.7102 | -0.27924 | 120.8817 | 120.8588 | 121.7102 | 121.6736 | 122.2321 | -1.506 | -122.438
5905.25 | 122.2733 | -120.8221 | 1.3687 | -0.17509 | 0.013473 | -0.018745 | 0.059114 | -0.023159 | -0.014167 | 0.02845 | 0.041199 | 0.09613 | -0.15564 | 0.83771 | 0.85602 | 0.88348 | 0.66376 | 1.03 | 1.4557 | -121.0648 | 120.6665 | -1.2726 | 120.8633 | 121.6599 | -0.5127 | -0.24261 | 0.086975 | 0.19684 | 121.4859 | 121.8521 | 121.6782 | 120.9183 | 120.8633 | 122.2778 | 121.7056 | -0.24261 | 120.9183 | 120.8633 | 121.7056 | 121.6782 | 122.2778 | -1.5244 | -122.4335
5906.9844 | 122.374 | -120.7489 | 1.3641 | -0.060654 | 0.011337 | -0.016823 | 0.059114 | -0.022945 | -0.012031 | 0.02845 | 0.004578 | 0.086975 | -0.16479 | 0.82855 | 0.8606 | 0.87891 | 0.65918 | 1.03 | 1.4603 | -121.0419 | 120.5841 | -1.2772 | 120.7535 | 121.5775 | -0.50354 | -0.29297 | 0.09613 | 0.16937 | 121.4081 | 121.7789 | 121.6095 | 120.8359 | 120.7535 | 122.2092 | 121.6278 | -0.29297 | 120.8359 | 120.7535 | 121.6278 | 121.6095 | 122.2092 | -1.5289 | -122.406
5908.7188 | 122.3419 | -120.7489 | 1.3824 | -0.25902 | 0.014328 | -0.0149 | 0.060609 | -0.022091 | -0.012886 | 0.029946 | -0.004578 | 0.09613 | -0.1831 | 0.76904 | 0.79193 | 0.81024 | 0.77362 | 0.94757 | 1.4877 | -121.0739 | 120.5658 | -1.2863 | 120.7443 | 121.5179 | -0.59052 | -0.32501 | 0.10529 | 0.17853 | 121.5225 | 121.6965 | 121.5408 | 120.845 | 120.7443 | 122.2366 | 121.5591 | -0.32501 | 120.845 | 120.7443 | 121.5591 | 121.5408 | 122.2366 | -1.5656 | -122.4564
5910.4688 | 122.287 | -120.7489 | 1.4191 | -0.15221 | 0.012832 | -0.012764 | 0.057618 | -0.023159 | -0.012672 | 0.029091 | 0.09613 | 0.073242 | -0.16022 | 0.87433 | 0.90637 | 0.94299 | 0.6546 | 1.0895 | 1.5106 | -121.0281 | 120.5887 | -1.3458 | 120.845 | 121.6232 | -0.5127 | -0.27924 | 0.091553 | 0.25635 | 121.4035 | 121.8384 | 121.6553 | 120.8221 | 120.845 | 122.2595 | 121.6919 | -0.27924 | 120.8221 | 120.845 | 121.6919 | 121.6553 | 122.2595 | -1.5793 | -122.4472
5912.1875 | 122.3969 | -120.6848 | 1.4328 | 0.11482 | 0.0139 | -0.013191 | 0.065522 | -0.022732 | -0.013954 | 0.030159 | -0.041199 | 0.10071 | -0.20599 | 0.76446 | 0.76446 | 0.79193 | 0.76446 | 0.89264 | 1.5976 | -120.9915 | 120.4788 | -1.3321 | 120.6436 | 121.4493 | -0.66834 | -0.3067 | 0.1648 | 0.1648 | 121.4493 | 121.5775 | 121.4493 | 120.7855 | 120.6436 | 122.2824 | 121.4767 | -0.3067 | 120.7855 | 120.6436 | 121.4767 | 121.4493 | 122.2824 | -1.6388 | -122.4243
5913.9062 | 122.2824 | -120.7123 | 1.4694 | -0.17509 | 0.014541 | -0.018745 | 0.059327 | -0.021023 | -0.01609 | 0.029732 | 0.050354 | 0.068665 | -0.17853 | 0.87433 | 0.88348 | 0.91553 | 0.70038 | 1.0529 | 1.5518 | -120.9686 | 120.5338 | -1.4008 | 120.7626 | 121.5866 | -0.58594 | -0.25635 | 0.082398 | 0.22888 | 121.4127 | 121.7651 | 121.5958 | 120.7809 | 120.7626 | 122.2641 | 121.6278 | -0.25635 | 120.7809 | 120.7626 | 121.6278 | 121.5958 | 122.2641 | -1.6479 | -122.438
5915.6406 | 122.3007 | -120.6802 | 1.4877 | -0.13695 | 0.012832 | -0.017464 | 0.058687 | -0.022518 | -0.012672 | 0.031227 | 0.059509 | 0.059509 | -0.16479 | 0.91553 | 0.94299 | 0.97504 | 0.64545 | 1.1124 | 1.5701 | -120.9137 | 120.5154 | -1.4282 | 120.7397 | 121.5958 | -0.54474 | -0.23346 | 0.082397 | 0.2243 | 121.3257 | 121.7926 | 121.6232 | 120.7397 | 120.7397 | 122.2504 | 121.6553 | -0.23346 | 120.7397 | 120.7397 | 121.6553 | 121.6232 | 122.2504 | -1.6525 | -122.4014
5917.375 | 122.3969 | -120.6116 | 1.474 | 0.099564 | 0.014541 | -0.016823 | 0.067018 | -0.020809 | -0.015449 | 0.031227 | -0.050354 | 0.10529 | -0.21057 | 0.81482 | 0.82855 | 0.84686 | 0.80109 | 0.94757 | 1.6159 | -120.9503 | 120.401 | -1.3687 | 120.5612 | 121.4264 | -0.64545 | -0.33875 | 0.14191 | 0.16022 | 121.4127 | 121.5591 | 121.4401 | 120.7169 | 120.5612 | 122.2275 | 121.4584 | -0.33875 | 120.7169 | 120.5612 | 121.4584 | 121.4401 | 122.2275 | -1.6846 | -122.4243
5919.1094 | 122.4472 | -120.607 | 1.4969 | 0.02327 | 0.014969 | -0.014259 | 0.060823 | -0.020382 | -0.010536 | 0.030373 | -0.004578 | 0.068665 | -0.17395 | 0.8606 | 0.89722 | 0.93384 | 0.72327 | 1.0391 | 1.6022 | -120.9137 | 120.433 | -1.4282 | 120.6024 | 121.4676 | -0.59967 | -0.3067 | 0.10529 | 0.16937 | 121.3303 | 121.6461 | 121.5042 | 120.6757 | 120.6024 | 122.2092 | 121.5408 | -0.3067 | 120.6757 | 120.6024 | 121.5408 | 121.5042 | 122.2092 | -1.6708 | -122.4106
5920.8438 | 122.4289 | -120.5795 | 1.5106 | 0.099564 | 0.015396 | -0.014473 | 0.069368 | -0.021663 | -0.016731 | 0.031868 | -0.068665 | 0.091553 | -0.2243 | 0.78735 | 0.81024 | 0.82855 | 0.8194 | 0.91095 | 1.68 | -120.8954 | 120.3552 | -1.4191 | 120.5109 | 121.3669 | -0.70038 | -0.31586 | 0.16937 | 0.15564 | 121.3989 | 121.4905 | 121.3898 | 120.6711 | 120.5109 | 122.2595 | 121.4081 | -0.31586 | 120.6711 | 120.5109 | 121.4081 | 121.3898 | 122.2595 | -1.7349 | -122.406
5922.625 | 122.4106 | -120.5612 | 1.561 | 0.038529 | 0.01625 | -0.011696 | 0.069581 | -0.019314 | -0.013313 | 0.037209 | -0.059509 | 0.10071 | -0.2243 | 0.78735 | 0.80109 | 0.82855 | 0.85602 | 0.92468 | 1.6754 | -120.9045 | 120.3369 | -1.4603 | 120.5017 | 121.3486 | -0.75989 | -0.34332 | 0.11444 | 0.16479 | 121.4172 | 121.4859 | 121.3623 | 120.6619 | 120.5017 | 122.2366 | 121.3898 | -0.34332 | 120.6619 | 120.5017 | 121.3898 | 121.3623 | 122.2366 | -1.7853 | -122.4655
5924.3438 | 122.4152 | -120.575 | 1.5289 | 0.11482 | 0.0139 | -0.014473 | 0.064882 | -0.022091 | -0.014381 | 0.032082 | -0.059509 | 0.082397 | -0.22888 | 0.85144 | 0.85602 | 0.89722 | 0.83771 | 0.98877 | 1.6846 | -120.9091 | 120.3461 | -1.4465 | 120.5154 | 121.4264 | -0.67291 | -0.33417 | 0.15564 | 0.16937 | 121.4127 | 121.5637 | 121.431 | 120.6573 | 120.5154 | 122.2595 | 121.4722 | -0.33417 | 120.6573 | 120.5154 | 121.4722 | 121.431 | 122.2595 | -1.7578 | -122.4381
5926.0781 | 122.2961 | -120.5246 | 1.6663 | -0.18272 | 0.011978 | -0.020241 | 0.061464 | -0.022945 | -0.01374 | 0.036141 | 0.009155 | 0.064087 | -0.19226 | 0.98419 | 1.0208 | 1.0391 | 0.81482 | 1.1765 | 1.7395 | -120.7352 | 120.3323 | -1.6022 | 120.5338 | 121.5088 | -0.64545 | -0.21057 | 0.073242 | 0.20142 | 121.3394 | 121.701 | 121.5454 | 120.5887 | 120.5338 | 122.2641 | 121.5637 | -0.21057 | 120.5887 | 120.5338 | 121.5637 | 121.5454 | 122.2641 | -1.8585 | -122.4014
5927.7812 | 122.3969 | -120.0714 | 2.0691 | 0.17586 | 0.0139 | -0.01255 | 0.07364 | -0.019741 | -0.013954 | 0.046822 | 0.013733 | 0.027466 | -0.19684 | 1.2268 | 1.2314 | 1.3 | 0.95215 | 1.3962 | 2.1378 | -120.3552 | 119.8746 | -2.0416 | 120.0851 | 121.2982 | -0.83771 | -0.28381 | 0.068664 | 0.21057 | 121.0236 | 121.4676 | 121.3028 | 120.0989 | 120.0851 | 122.2092 | 121.3715 | -0.28381 | 120.0989 | 120.0851 | 121.3715 | 121.3028 | 122.2092 | -2.2659 | -122.4243
5929.5 | 122.438 | -120.1813 | 1.9089 | 0.10719 | 0.016891 | -0.017464 | 0.070009 | -0.02145 | -0.015449 | 0.037209 | -0.082397 | 0.07782 | -0.24261 | 0.96588 | 0.98877 | 1.0162 | 0.98419 | 1.0941 | 2.0691 | -120.52 | 119.9387 | -1.8311 | 120.0989 | 121.1472 | -0.92011 | -0.33875 | 0.16022 | 0.16022 | 121.1655 | 121.2753 | 121.17 | 120.2591 | 120.0989 | 122.2504 | 121.1975 | -0.33875 | 120.2591 | 120.0989 | 121.1975 | 121.17 | 122.2504 | -2.1515 | -122.4289
5931.2031 | 122.3373 | -120.0439 | 2.1332 | -0.27428 | 0.016037 | -0.016609 | 0.07364 | -0.022945 | -0.014595 | 0.045326 | -0.036621 | 0.036621 | -0.22888 | 1.1993 | 1.2222 | 1.2497 | 1.1444 | 1.3641 | 2.2156 | -120.3873 | 119.8151 | -2.0966 | 120.0073 | 121.2433 | -0.91095 | -0.34332 | 0.082397 | 0.19226 | 121.1884 | 121.4081 | 121.2662 | 120.0806 | 120.0073 | 122.2595 | 121.2936 | -0.34332 | 120.0806 | 120.0073 | 121.2936 | 121.2662 | 122.2595 | -2.3621 | -122.5204
5932.9375 | 122.4426 | -120.2591 | 1.886 | -0.022507 | 0.014969 | -0.016609 | 0.067018 | -0.0238 | -0.012886 | 0.042336 | -0.064087 | 0.045776 | -0.19684 | 1.062 | 1.0941 | 1.1307 | 0.92926 | 1.2497 | 2.0004 | -120.5704 | 120.0623 | -1.8402 | 120.195 | 121.3211 | -0.79193 | -0.31128 | 0.11444 | 0.13275 | 121.1884 | 121.5088 | 121.3531 | 120.3049 | 120.195 | 122.2595 | 121.3898 | -0.31128 | 120.3049 | 120.195 | 121.3898 | 121.3531 | 122.2595 | -2.0828 | -122.4564
5934.6875 | 122.3602 | -120.3598 | 1.8356 | -0.2285 | 0.014328 | -0.017036 | 0.074281 | -0.024441 | -0.01075 | 0.044472 | -0.10071 | 0.068665 | -0.25177 | 0.95215 | 0.9613 | 0.96588 | 1.0162 | 1.1032 | 1.9501 | -120.6528 | 120.108 | -1.767 | 120.2591 | 121.3119 | -0.87433 | -0.29297 | 0.11444 | 0.15106 | 121.376 | 121.463 | 121.3211 | 120.4285 | 120.2591 | 122.3099 | 121.3257 | -0.29297 | 120.4285 | 120.2591 | 121.3257 | 121.3211 | 122.3099 | -2.0874 | -122.4884
5936.4219 | 122.3282 | -120.108 | 2.0828 | -0.14458 | 0.014969 | -0.017036 | 0.080049 | -0.021877 | -0.017585 | 0.042977 | -0.045776 | 0.064087 | -0.27466 | 1.1902 | 1.181 | 1.2177 | 1.1215 | 1.3367 | 2.2202 | -120.3964 | 119.8334 | -2.0187 | 120.0623 | 121.2982 | -0.9018 | -0.28839 | 0.13733 | 0.22888 | 121.2296 | 121.4447 | 121.2891 | 120.1721 | 120.0623 | 122.3282 | 121.3257 | -0.28839 | 120.1721 | 120.0623 | 121.3257 | 121.2891 | 122.3282 | -2.3575 | -122.4792
5938.1406 | 122.3419 | -120.0989 | 2.092 | -0.17509 | 0.012405 | -0.015327 | 0.076631 | -0.020809 | -0.015663 | 0.044258 | -0.10529 | 0.059509 | -0.25635 | 1.1856 | 1.1948 | 1.2039 | 1.2314 | 1.3229 | 2.2202 | -120.3827 | 119.8425 | -2.0325 | 119.9936 | 121.2845 | -0.89722 | -0.28381 | 0.12817 | 0.15106 | 121.3303 | 121.4218 | 121.2936 | 120.1584 | 119.9936 | 122.319 | 121.3028 | -0.28381 | 120.1584 | 119.9936 | 121.3028 | 121.2936 | 122.319 | -2.3483 | -122.4747
5939.8906 | 122.2733 | -119.4855 | 2.6917 | -0.075912 | 0.012619 | -0.0149 | 0.09308 | -0.0191 | -0.016731 | 0.059426 | -0.059509 | 0.050354 | -0.26093 | 1.5793 | 1.5884 | 1.6159 | 1.506 | 1.7349 | 2.8244 | -119.7235 | 119.2245 | -2.6413 | 119.426 | 121.0648 | -1.1032 | -0.23804 | 0.13275 | 0.20142 | 120.9915 | 121.2204 | 121.0739 | 119.5358 | 119.426 | 122.3099 | 121.1014 | -0.23804 | 119.5358 | 119.426 | 121.1014 | 121.0739 | 122.3099 | -2.9526 | -122.4152
5941.6406 | 122.3969 | -118.2266 | 3.8864 | 0.16823 | 0.012405 | -0.016182 | 0.11701 | -0.018886 | -0.014167 | 0.088051 | -0.059509 | 0.013733 | -0.25635 | 2.3209 | 2.3392 | 2.3941 | 2.1194 | 2.4765 | 3.978 | -118.5379 | 117.9703 | -3.8727 | 118.1671 | 120.5475 | -1.5472 | -0.31128 | 0.091552 | 0.19684 | 120.3461 | 120.7031 | 120.5658 | 118.2404 | 118.1671 | 122.2046 | 120.6207 | -0.31128 | 118.2404 | 118.1671 | 120.6207 | 120.5658 | 122.2046 | -4.1428 | -122.4243
5943.3594 | 122.3511 | -119.5633 | 2.6184 | -0.17509 | 0.013046 | -0.014473 | 0.087312 | -0.024013 | -0.012886 | 0.057717 | -0.1236 | 0.032043 | -0.27008 | 1.5106 | 1.5472 | 1.561 | 1.5793 | 1.6754 | 2.7603 | -119.8654 | 119.2932 | -2.5864 | 119.4397 | 121.0739 | -1.0712 | -0.30212 | 0.14191 | 0.14649 | 121.1426 | 121.2387 | 121.1105 | 119.5953 | 119.4397 | 122.3236 | 121.1243 | -0.30212 | 119.5953 | 119.4397 | 121.1243 | 121.1105 | 122.3236 | -2.8885 | -122.4838
5945.0625 | 122.4106 | -120.5154 | 1.6571 | 0.13771 | 0.014114 | -0.017677 | 0.066804 | -0.019741 | -0.013313 | 0.035927 | 0 | 0.013733 | -0.21057 | 0.99335 | 1.0025 | 1.0666 | 0.72784 | 1.1536 | 1.7487 | -120.7809 | 120.3049 | -1.6434 | 120.5154 | 121.5088 | -0.6546 | -0.2655 | 0.091553 | 0.21057 | 121.2433 | 121.669 | 121.5179 | 120.5292 | 120.5154 | 122.2641 | 121.582 | -0.2655 | 120.5292 | 120.5154 | 121.582 | 121.5179 | 122.2641 | -1.8677 | -122.438
5946.7812 | 122.3465 | -120.3278 | 1.8356 | -0.037765 | 0.014541 | -0.016823 | 0.074281 | -0.021877 | -0.017372 | 0.039772 | -0.064087 | 0.041199 | -0.27924 | 1.0391 | 1.0529 | 1.0986 | 1.0345 | 1.1902 | 1.9547 | -120.6619 | 120.0485 | -1.7944 | 120.2637 | 121.3669 | -0.78278 | -0.33417 | 0.11902 | 0.21515 | 121.3623 | 121.5179 | 121.3806 | 120.369 | 120.2637 | 122.2824 | 121.4264 | -0.33417 | 120.369 | 120.2637 | 121.4264 | 121.3806 | 122.2824 | -2.1149 | -122.4976
5948.5781 | 122.4197 | -120.6253 | 1.5381 | 0.091934 | 0.014328 | -0.012123 | 0.060609 | -0.022518 | -0.01139 | 0.0355 | -0.009155 | -0.009155 | -0.21057 | 0.94299 | 0.96588 | 1.0208 | 0.70496 | 1.0986 | 1.6479 | -120.9366 | 120.4147 | -1.5472 | 120.6161 | 121.5683 | -0.57221 | -0.31128 | 0.10986 | 0.20142 | 121.3303 | 121.7239 | 121.5912 | 120.6161 | 120.6161 | 122.2733 | 121.6461 | -0.31128 | 120.6161 | 120.6161 | 121.6461 | 121.5912 | 122.2733 | -1.7487 | -122.4747
5950.2969 | 122.4426 | -120.5887 | 1.5518 | 0.076676 | 0.014541 | -0.012764 | 0.069154 | -0.022945 | -0.014808 | 0.035286 | -0.13275 | 0.054932 | -0.27924 | 0.85602 | 0.86517 | 0.91095 | 0.89722 | 1.0208 | 1.712 | -120.9229 | 120.3094 | -1.4969 | 120.4559 | 121.4447 | -0.68665 | -0.33417 | 0.16022 | 0.14648 | 121.4859 | 121.6095 | 121.4539 | 120.6436 | 120.4559 | 122.3007 | 121.4996 | -0.33417 | 120.6436 | 120.4559 | 121.4996 | 121.4539 | 122.3007 | -1.8311 | -122.4747
5952.0781 | 122.4701 | -120.4605 | 1.6479 | 0.084305 | 0.013046 | -0.015541 | 0.066804 | -0.018673 | -0.016945 | 0.035073 | -0.13275 | 0.036621 | -0.28381 | 0.90637 | 0.92468 | 0.95673 | 0.90179 | 1.0437 | 1.7715 | -120.8176 | 120.1767 | -1.6113 | 120.3278 | 121.3669 | -0.72327 | -0.35706 | 0.1236 | 0.15106 | 121.3623 | 121.5042 | 121.3852 | 120.4971 | 120.3278 | 122.2321 | 121.4172 | -0.35706 | 120.4971 | 120.3278 | 121.4172 | 121.3852 | 122.2321 | -1.9318 | -122.4655
5953.7812 | 122.3419 | -120.5154 | 1.7075 | -0.17509 | 0.012832 | -0.015968 | 0.062104 | -0.021663 | -0.015022 | 0.034004 | -0.050354 | -0.018311 | -0.23804 | 1.0483 | 1.0757 | 1.0803 | 0.89264 | 1.2268 | 1.7715 | -120.7855 | 120.2774 | -1.7258 | 120.4651 | 121.5637 | -0.63171 | -0.27008 | 0.064087 | 0.18768 | 121.4081 | 121.7422 | 121.5912 | 120.4971 | 120.4651 | 122.287 | 121.5958 | -0.27008 | 120.4971 | 120.4651 | 121.5958 | 121.5912 | 122.287 | -1.9455 | -122.493
5955.5156 | 122.3602 | -120.4559 | 1.7578 | 0.00038159 | 0.017105 | -0.017036 | 0.071718 | -0.020595 | -0.016517 | 0.038704 | -0.10071 | -0.018311 | -0.31128 | 1.0071 | 0.9613 | 1.0071 | 0.98877 | 1.1169 | 1.8723 | -120.7489 | 120.1447 | -1.7761 | 120.3552 | 121.463 | -0.79651 | -0.29297 | 0.11444 | 0.21057 | 121.4447 | 121.5729 | 121.4172 | 120.4376 | 120.3552 | 122.3282 | 121.463 | -0.29297 | 120.4376 | 120.3552 | 121.463 | 121.4172 | 122.3282 | -2.0691 | -122.5067
5957.2188 | 122.374 | -120.4239 | 1.799 | -0.23613 | 0.013687 | -0.020454 | 0.06894 | -0.023586 | -0.014381 | 0.038918 | -0.11444 | -0.027466 | -0.27008 | 1.0117 | 1.0345 | 1.0529 | 1.0162 | 1.181 | 1.8768 | -120.7352 | 120.1538 | -1.8265 | 120.3094 | 121.4355 | -0.76446 | -0.31128 | 0.07782 | 0.15564 | 121.4401 | 121.6049 | 121.4584 | 120.3964 | 120.3094 | 122.3007 | 121.4767 | -0.31128 | 120.3964 | 120.3094 | 121.4767 | 121.4584 | 122.3007 | -2.0691 | -122.5342
5958.9219 | 122.4655 | -120.314 | 1.886 | -0.053024 | 0.014755 | -0.018104 | 0.06595 | -0.021236 | -0.012458 | 0.039772 | -0.17395 | -0.12817 | -0.35248 | 1.149 | 1.2085 | 1.2405 | 1.0071 | 1.3641 | 1.9547 | -120.5978 | 119.9615 | -2.0142 | 120.1401 | 121.463 | -0.67749 | -0.28381 | 0.068665 | 0.17853 | 121.3211 | 121.6782 | 121.5225 | 120.1859 | 120.1401 | 122.2687 | 121.5546 | -0.28381 | 120.1859 | 120.1401 | 121.5546 | 121.5225 | 122.2687 | -2.2385 | -122.4838
5960.6406 | 122.3511 | -119.8654 | 2.3987 | -0.2285 | 0.012191 | -0.019173 | 0.077913 | -0.0238 | -0.01374 | 0.05024 | -0.40741 | -0.37537 | -0.61798 | 1.5198 | 1.506 | 1.5381 | 1.3962 | 1.6937 | 2.4948 | -120.108 | 119.2474 | -2.774 | 119.458 | 121.3852 | -0.89264 | -0.24262 | 0.09613 | 0.21057 | 121.2616 | 121.5591 | 121.3715 | 119.4901 | 119.458 | 122.3602 | 121.4035 | -0.24262 | 119.4901 | 119.458 | 121.4035 | 121.3715 | 122.3602 | -3.0167 | -122.5067
5962.3438 | 122.4564 | -120.0943 | 2.0645 | 0.053787 | 0.014114 | -0.0095597 | 0.078126 | -0.018459 | -0.015876 | 0.043617 | -0.34332 | -0.16022 | -0.48981 | 1.181 | 1.1948 | 1.2268 | 1.2497 | 1.3367 | 2.2064 | -120.4056 | 119.6045 | -2.2247 | 119.751 | 121.2753 | -0.86975 | -0.31128 | 0.14191 | 0.14648 | 121.344 | 121.431 | 121.2891 | 119.9341 | 119.751 | 122.3007 | 121.3211 | -0.31128 | 119.9341 | 119.751 | 121.3211 | 121.2891 | 122.3007 | -2.5543 | -122.4701
5964.0469 | 122.3969 | -119.5267 | 2.6962 | -0.20561 | 0.014969 | -0.015755 | 0.084962 | -0.021877 | -0.014381 | 0.055153 | -0.69122 | -0.53101 | -0.84686 | 1.6571 | 1.6571 | 1.6754 | 1.7212 | 1.8219 | 2.8198 | -119.8471 | 118.6798 | -3.2272 | 118.8354 | 121.1838 | -1.0391 | -0.32043 | 0.1236 | 0.15564 | 121.2479 | 121.3486 | 121.1838 | 118.9957 | 118.8354 | 122.3465 | 121.2021 | -0.32043 | 118.9957 | 118.8354 | 121.2021 | 121.1838 | 122.3465 | -3.5431 | -122.5433
5965.75 | 122.4838 | -119.0643 | 3.0716 | 0.0080111 | 0.014541 | -0.017891 | 0.088594 | -0.019314 | -0.011604 | 0.062416 | -0.89722 | -0.82855 | -1.0574 | 2.005 | 2.0187 | 2.0416 | 1.8631 | 2.1606 | 3.1998 | -119.3802 | 118.0069 | -3.9001 | 118.1671 | 121.0693 | -1.0529 | -0.31586 | 0.12817 | 0.16022 | 120.9274 | 121.225 | 121.0831 | 118.2358 | 118.1671 | 122.2641 | 121.106 | -0.31586 | 118.2358 | 118.1671 | 121.106 | 121.0831 | 122.2641 | -4.129 | -122.4518
5967.5469 | 122.4335 | -119.0598 | 3.1265 | 0.030899 | 0.015182 | -0.012337 | 0.10312 | -0.0191 | -0.015236 | 0.06733 | -0.97046 | -0.84228 | -1.1536 | 1.9501 | 1.9318 | 1.9684 | 2.0004 | 2.0554 | 3.2547 | -119.3802 | 117.9062 | -3.9688 | 118.0893 | 121.0098 | -1.1948 | -0.32044 | 0.12817 | 0.18311 | 121.0602 | 121.1151 | 120.9915 | 118.2175 | 118.0893 | 122.3145 | 121.0281 | -0.32044 | 118.2175 | 118.0893 | 121.0281 | 120.9915 | 122.3145 | -4.2801 | -122.5067
5969.2812 | 122.4472 | -118.1213 | 4.01 | 0.14534 | 0.015823 | -0.016182 | 0.12149 | -0.022518 | -0.015022 | 0.088051 | -1.1169 | -0.97046 | -1.268 | 2.4811 | 2.4994 | 2.5681 | 2.4078 | 2.6413 | 4.1107 | -118.483 | 116.8533 | -4.9805 | 117.0044 | 120.6024 | -1.5106 | -0.36163 | 0.10071 | 0.15106 | 120.5292 | 120.7626 | 120.6207 | 117.1509 | 117.0044 | 122.2321 | 120.6894 | -0.36163 | 117.1509 | 117.0044 | 120.6894 | 120.6207 | 122.2321 | -5.278 | -122.493
5970.9844 | 122.3694 | -120.2179 | 2.0096 | -0.25902 | 0.01326 | -0.017036 | 0.075776 | -0.022518 | -0.013527 | 0.04789 | -0.21057 | -0.13733 | -0.3891 | 1.1536 | 1.2039 | 1.2131 | 1.0803 | 1.3458 | 2.124 | -120.4742 | 119.8288 | -2.1469 | 120.0073 | 121.3715 | -0.80567 | -0.25635 | 0.11444 | 0.17853 | 121.2982 | 121.5637 | 121.4218 | 120.0806 | 120.0073 | 122.3419 | 121.431 | -0.25635 | 120.0806 | 120.0073 | 121.431 | 121.4218 | 122.3419 | -2.3987 | -122.4838
5972.7188 | 122.4838 | -120.1355 | 2.0142 | 0.053787 | 0.015396 | -0.013832 | 0.0683 | -0.021877 | -0.012886 | 0.042977 | -0.2655 | -0.19684 | -0.44861 | 1.2405 | 1.268 | 1.3046 | 1.0986 | 1.4053 | 2.1469 | -120.4285 | 119.6869 | -2.211 | 119.87 | 121.376 | -0.74615 | -0.29297 | 0.13275 | 0.18311 | 121.2341 | 121.5408 | 121.4035 | 119.9387 | 119.87 | 122.2824 | 121.4401 | -0.29297 | 119.9387 | 119.87 | 121.4401 | 121.4035 | 122.2824 | -2.4628 | -122.4426
5974.4219 | 122.3923 | -119.6732 | 2.5131 | -0.19798 | 0.014969 | -0.017891 | 0.086885 | -0.022091 | -0.014808 | 0.054726 | -0.59052 | -0.41657 | -0.72784 | 1.5198 | 1.5244 | 1.5381 | 1.5656 | 1.6846 | 2.6642 | -119.9844 | 118.9453 | -2.9297 | 119.0826 | 121.1929 | -0.98877 | -0.31128 | 0.15106 | 0.13733 | 121.2387 | 121.3577 | 121.1975 | 119.2566 | 119.0826 | 122.3373 | 121.2112 | -0.31128 | 119.2566 | 119.0826 | 121.2112 | 121.1975 | 122.3373 | -3.241 | -122.4976
5976.125 | 122.3694 | -119.1238 | 3.1174 | -0.21324 | 0.012191 | -0.020668 | 0.093293 | -0.021023 | -0.013527 | 0.063271 | -0.6958 | -0.66376 | -0.91553 | 2.0187 | 2.0279 | 2.0599 | 1.8585 | 2.2156 | 3.2135 | -119.3802 | 118.2083 | -3.7811 | 118.428 | 121.1426 | -1.0895 | -0.25635 | 0.09613 | 0.21973 | 120.9824 | 121.3394 | 121.1517 | 118.4601 | 118.428 | 122.3373 | 121.1838 | -0.25635 | 118.4601 | 118.428 | 121.1838 | 121.1517 | 122.3373 | -4.0329 | -122.4976
5977.8594 | 122.3648 | -119.9295 | 2.2888 | -0.17509 | 0.013687 | -0.012337 | 0.076631 | -0.022091 | -0.013527 | 0.048317 | -0.38452 | -0.3479 | -0.5722 | 1.474 | 1.4877 | 1.5244 | 1.3229 | 1.6663 | 2.3849 | -120.2408 | 119.3573 | -2.6367 | 119.545 | 121.4035 | -0.80109 | -0.31128 | 0.096131 | 0.18768 | 121.2524 | 121.5958 | 121.4172 | 119.5816 | 119.545 | 122.3145 | 121.4539 | -0.31128 | 119.5816 | 119.545 | 121.4539 | 121.4172 | 122.3145 | -2.861 | -122.5296
5979.5625 | 122.3648 | -119.4763 | 2.7603 | -0.075912 | 0.01326 | -0.01725 | 0.091157 | -0.020382 | -0.015663 | 0.058357 | -0.65918 | -0.57678 | -0.89264 | 1.7487 | 1.7212 | 1.7532 | 1.6891 | 1.8768 | 2.8702 | -119.751 | 118.5837 | -3.3371 | 118.8171 | 121.225 | -1.0391 | -0.27466 | 0.10986 | 0.23346 | 121.1655 | 121.3531 | 121.1975 | 118.8995 | 118.8171 | 122.3465 | 121.2296 | -0.27466 | 118.8995 | 118.8171 | 121.2296 | 121.1975 | 122.3465 | -3.653 | -122.5113
5981.2812 | 122.3602 | -119.1284 | 3.1265 | -0.20561 | 0.014114 | -0.018532 | 0.090089 | -0.021236 | -0.012458 | 0.06733 | -0.7782 | -0.75531 | -0.97046 | 2.0325 | 2.0325 | 2.0599 | 1.7899 | 2.211 | 3.1769 | -119.3939 | 118.158 | -3.8818 | 118.3502 | 121.1609 | -1.0941 | -0.2655 | 0.050354 | 0.19226 | 120.9183 | 121.3394 | 121.1609 | 118.3731 | 118.3502 | 122.3053 | 121.1884 | -0.2655 | 118.3731 | 118.3502 | 121.1884 | 121.1609 | 122.3053 | -4.097 | -122.5204
5982.9844 | 122.4701 | -119.3069 | 2.8336 | 0.091934 | 0.0139 | -0.015755 | 0.10227 | -0.0191 | -0.016945 | 0.068398 | -0.66376 | -0.5127 | -0.82398 | 1.6022 | 1.6067 | 1.6479 | 1.6205 | 1.7349 | 2.9892 | -119.6365 | 118.483 | -3.3463 | 118.6432 | 120.9091 | -1.2268 | -0.32959 | 0.15564 | 0.16022 | 120.9274 | 121.0419 | 120.9137 | 118.7943 | 118.6432 | 122.2961 | 120.9549 | -0.32959 | 118.7943 | 118.6432 | 120.9549 | 120.9137 | 122.2961 | -3.6575 | -122.4701
5984.7188 | 122.4838 | -119.2703 | 2.9022 | 0.091934 | 0.014755 | -0.013618 | 0.094789 | -0.020168 | -0.013099 | 0.061775 | -0.80109 | -0.64087 | -0.93842 | 1.7899 | 1.7853 | 1.8402 | 1.7578 | 1.9272 | 3.0441 | -119.6045 | 118.3319 | -3.5431 | 118.4692 | 121.0602 | -1.1169 | -0.33417 | 0.14191 | 0.13733 | 121.0281 | 121.1975 | 121.0556 | 118.6295 | 118.4692 | 122.3145 | 121.1105 | -0.33417 | 118.6295 | 118.4692 | 121.1105 | 121.0556 | 122.3145 | -3.8406 | -122.5067
5986.4219 | 122.4014 | -119.5175 | 2.7191 | -0.23613 | 0.014114 | -0.019813 | 0.08368 | -0.022518 | -0.015236 | 0.059639 | -0.67291 | -0.53558 | -0.80566 | 1.6617 | 1.6846 | 1.6983 | 1.6983 | 1.8402 | 2.8198 | -119.8242 | 118.7119 | -3.2547 | 118.8446 | 121.1792 | -1.0345 | -0.3067 | 0.10071 | 0.13275 | 121.2158 | 121.3577 | 121.2021 | 118.9819 | 118.8446 | 122.3373 | 121.2158 | -0.3067 | 118.9819 | 118.8446 | 121.2158 | 121.2021 | 122.3373 | -3.5248 | -122.5433
5988.1562 | 122.5113 | -119.6091 | 2.5772 | -0.0072479 | 0.012191 | -0.019173 | 0.079835 | -0.023159 | -0.012458 | 0.054299 | -0.57678 | -0.46692 | -0.72327 | 1.5564 | 1.6296 | 1.6617 | 1.4511 | 1.7441 | 2.6642 | -119.9844 | 118.8858 | -3.0441 | 119.0323 | 121.1655 | -0.94757 | -0.37537 | 0.086976 | 0.14648 | 121.0602 | 121.3531 | 121.2387 | 119.1422 | 119.0323 | 122.2733 | 121.2708 | -0.37537 | 119.1422 | 119.0323 | 121.2708 | 121.2387 | 122.2733 | -3.3005 | -122.5616
5989.8594 | 122.374 | -117.4393 | 4.7333 | -0.22087 | 0.013473 | -0.014687 | 0.087312 | -0.021877 | -0.012458 | 0.059212 | -0.50812 | -0.31128 | -0.64087 | 1.5335 | 1.5381 | 1.5656 | 1.5244 | 1.6983 | 2.829 | -119.7144 | 116.7984 | -5.0446 | 116.9312 | 118.9728 | -3.1952 | -2.2751 | -1.9043 | 0.13275 | 118.9636 | 119.1376 | 118.9774 | 117.128 | 116.9312 | 120.2682 | 119.0048 | -2.2751 | 117.128 | 116.9312 | 119.0048 | 118.9774 | 120.2682 | -5.3741 | -124.4476
5991.6094 | 122.438 | -119.3802 | 2.7695 | 0.099564 | 0.013687 | -0.014687 | 0.085817 | -0.01675 | -0.013527 | 0.063484 | -0.45319 | -0.32044 | -0.6134 | 1.3733 | 1.4008 | 1.4328 | 1.3504 | 1.5198 | 2.9297 | -119.7876 | 118.7668 | -3.0899 | 118.927 | 120.7535 | -1.3687 | -0.40741 | 0.16022 | 0.16022 | 120.7306 | 120.9 | 120.7809 | 119.0598 | 118.927 | 122.3099 | 120.813 | -0.40741 | 119.0598 | 118.927 | 120.813 | 120.7809 | 122.3099 | -3.3829 | -122.5571
5993.2969 | 122.4152 | -119.5541 | 2.6871 | -0.23613 | 0.013046 | -0.020241 | 0.078767 | -0.021663 | -0.014595 | 0.051094 | -0.52185 | -0.34332 | -0.66834 | 1.4191 | 1.4374 | 1.4603 | 1.5244 | 1.6022 | 2.8061 | -119.8883 | 118.8858 | -3.0304 | 119.0323 | 120.9732 | -1.2497 | -0.33417 | 0.11902 | 0.14648 | 121.0785 | 121.1563 | 120.9915 | 119.2108 | 119.0323 | 122.3602 | 121.0144 | -0.33417 | 119.2108 | 119.0323 | 121.0144 | 120.9915 | 122.3602 | -3.3554 | -122.5754
5995.0312 | 122.3557 | -119.5908 | 2.6779 | -0.091171 | 0.015823 | -0.013832 | 0.085389 | -0.021023 | -0.014381 | 0.055367 | -0.63629 | -0.54932 | -0.85602 | 1.68 | 1.6754 | 1.6983 | 1.6159 | 1.8265 | 2.7649 | -119.8791 | 118.7347 | -3.2272 | 118.9545 | 121.2708 | -1.0025 | -0.28839 | 0.086976 | 0.21973 | 121.2067 | 121.4172 | 121.2662 | 119.0414 | 118.9545 | 122.3557 | 121.2891 | -0.28839 | 119.0414 | 118.9545 | 121.2891 | 121.2662 | 122.3557 | -3.5339 | -122.5571
5996.7812 | 122.3831 | -119.2841 | 2.98 | -0.15221 | 0.011337 | -0.017891 | 0.090303 | -0.022091 | -0.015236 | 0.063057 | -0.85144 | -0.74158 | -1.03 | 1.8494 | 1.8585 | 1.8906 | 1.8127 | 2.0187 | 3.0853 | -119.545 | 118.2541 | -3.7216 | 118.4326 | 121.1334 | -1.1215 | -0.26093 | 0.10528 | 0.17853 | 121.0968 | 121.3028 | 121.1426 | 118.5425 | 118.4326 | 122.3694 | 121.1746 | -0.26093 | 118.5425 | 118.4326 | 121.1746 | 121.1426 | 122.3694 | -4.01 | -122.525
5998.4844 | 122.406 | -119.5633 | 2.6642 | -0.11406 | 0.013473 | -0.017464 | 0.079622 | -0.022091 | -0.013954 | 0.055794 | -0.62256 | -0.57678 | -0.80109 | 1.7258 | 1.7578 | 1.7853 | 1.474 | 1.9135 | 2.8152 | -119.7784 | 118.7622 | -3.241 | 118.9407 | 121.2891 | -0.90637 | -0.21515 | 0.15106 | 0.17853 | 121.0373 | 121.4767 | 121.3211 | 118.9865 | 118.9407 | 122.3785 | 121.3486 | -0.21515 | 118.9865 | 118.9407 | 121.3486 | 121.3211 | 122.3785 | -3.4653 | -122.4426
6000.1875 | 122.4792 | -119.8196 | 2.3483 | 0.13771 | 0.013687 | -0.018318 | 0.084108 | -0.020595 | -0.014381 | 0.053871 | -0.48523 | -0.33417 | -0.65002 | 1.3824 | 1.4008 | 1.4374 | 1.3 | 1.5427 | 2.4765 | -120.1447 | 119.1696 | -2.6825 | 119.3344 | 121.2021 | -0.94757 | -0.32501 | 0.12817 | 0.1648 | 121.1197 | 121.3623 | 121.2204 | 119.4855 | 119.3344 | 122.2961 | 121.257 | -0.32501 | 119.4855 | 119.3344 | 121.257 | 121.2204 | 122.2961 | -2.9984 | -122.493
6001.8906 | 122.4152 | -120.0119 | 2.2705 | -0.23613 | 0.012405 | -0.019173 | 0.077913 | -0.023159 | -0.015022 | 0.049599 | -0.37079 | -0.29755 | -0.54474 | 1.3412 | 1.3641 | 1.4008 | 1.2634 | 1.5381 | 2.3392 | -120.2682 | 119.4672 | -2.5681 | 119.6411 | 121.3531 | -0.90637 | -0.25635 | 0.068664 | 0.17395 | 121.2753 | 121.55 | 121.376 | 119.7144 | 119.6411 | 122.3511 | 121.4127 | -0.25635 | 119.7144 | 119.6411 | 121.4127 | 121.376 | 122.3511 | -2.8152 | -122.5388
6003.6406 | 122.3877 | -119.8563 | 2.4307 | -0.15221 | 0.013473 | -0.016396 | 0.083894 | -0.022732 | -0.013527 | 0.058144 | -0.33875 | -0.33875 | -0.55389 | 1.4282 | 1.4282 | 1.4648 | 1.1993 | 1.6067 | 2.5223 | -120.076 | 119.3024 | -2.7695 | 119.5175 | 121.2845 | -1.0025 | -0.21973 | 0.091553 | 0.21515 | 121.0556 | 121.463 | 121.2845 | 119.5175 | 119.5175 | 122.3785 | 121.3211 | -0.21973 | 119.5175 | 119.5175 | 121.3211 | 121.2845 | 122.3785 | -2.9846 | -122.5067
6005.3438 | 122.4655 | -119.4122 | 2.7969 | 0.11482 | 0.012191 | -0.012764 | 0.09073 | -0.02145 | -0.01374 | 0.060494 | -0.5722 | -0.54932 | -0.79651 | 1.7029 | 1.7075 | 1.7624 | 1.4511 | 1.8723 | 2.8519 | -119.7327 | 118.6157 | -3.3463 | 118.84 | 121.1151 | -1.0895 | -0.32043 | 0.054932 | 0.2243 | 120.8633 | 121.2845 | 121.1197 | 118.8629 | 118.84 | 122.2641 | 121.1746 | -0.32043 | 118.8629 | 118.84 | 121.1746 | 121.1197 | 122.2641 | -3.5934 | -122.5296
6007.0469 | 122.4335 | -119.5496 | 2.7237 | -0.014877 | 0.014114 | -0.010841 | 0.09308 | -0.0191 | -0.016304 | 0.058357 | -0.6546 | -0.52643 | -0.84686 | 1.6251 | 1.6113 | 1.6434 | 1.5976 | 1.7578 | 2.8152 | -119.8425 | 118.7027 | -3.2501 | 118.895 | 121.1746 | -1.1124 | -0.29297 | 0.091553 | 0.19226 | 121.1472 | 121.3074 | 121.1609 | 119.0231 | 118.895 | 122.3648 | 121.1929 | -0.29297 | 119.0231 | 118.895 | 121.1929 | 121.1609 | 122.3648 | -3.5706 | -122.5662
6008.75 | 122.438 | -119.7418 | 2.449 | -0.23613 | 0.014328 | -0.0149 | 0.088166 | -0.0238 | -0.015449 | 0.058785 | -0.42572 | -0.25177 | -0.5722 | 1.3275 | 1.3596 | 1.4374 | 1.506 | 1.5656 | 2.5818 | -120.0485 | 119.1696 | -2.7008 | 119.3161 | 121.0693 | -1.0895 | -0.3067 | 0.13275 | 0.14648 | 121.2479 | 121.3074 | 121.1014 | 119.4901 | 119.3161 | 122.3236 | 121.1792 | -0.3067 | 119.4901 | 119.3161 | 121.1792 | 121.1014 | 122.3236 | -3.0212 | -122.4976
6010.4844 | 122.4243 | -119.8334 | 2.3941 | -0.27428 | 0.015823 | -0.018318 | 0.081331 | -0.024013 | -0.014808 | 0.056008 | -0.40741 | -0.21973 | -0.53101 | 1.3641 | 1.3824 | 1.3962 | 1.4374 | 1.5335 | 2.5406 | -120.1401 | 119.3024 | -2.6138 | 119.426 | 121.1975 | -1.0117 | -0.3067 | 0.14648 | 0.1236 | 121.2708 | 121.3669 | 121.2158 | 119.6136 | 119.426 | 122.374 | 121.2296 | -0.3067 | 119.6136 | 119.426 | 121.2296 | 121.2158 | 122.374 | -2.9251 | -122.5342
6012.1875 | 122.5204 | -120.0302 | 2.1835 | 0.046158 | 0.015823 | -0.017036 | 0.076204 | -0.022945 | -0.013527 | 0.048958 | -0.31128 | -0.26093 | -0.48523 | 1.3 | 1.3321 | 1.3733 | 1.1536 | 1.4694 | 2.298 | -120.3323 | 119.545 | -2.4445 | 119.7189 | 121.3303 | -0.85144 | -0.30212 | 0.11444 | 0.17395 | 121.1838 | 121.4996 | 121.3623 | 119.7693 | 119.7189 | 122.3282 | 121.4035 | -0.30212 | 119.7693 | 119.7189 | 121.4035 | 121.3623 | 122.3282 | -2.6688 | -122.5159
6013.8906 | 122.4152 | -119.9799 | 2.3071 | -0.045395 | 0.014328 | -0.017036 | 0.082612 | -0.020595 | -0.01609 | 0.049385 | -0.41657 | -0.31128 | -0.60883 | 1.3916 | 1.3779 | 1.4191 | 1.3412 | 1.5152 | 2.3987 | -120.2408 | 119.371 | -2.6184 | 119.5633 | 121.3715 | -0.92926 | -0.26093 | 0.091553 | 0.19226 | 121.3211 | 121.4951 | 121.3577 | 119.6686 | 119.5633 | 122.3785 | 121.3989 | -0.26093 | 119.6686 | 119.5633 | 121.3989 | 121.3577 | 122.3785 | -2.916 | -122.5479
6015.6406 | 122.438 | -119.8059 | 2.3895 | 0.16823 | 0.014541 | -0.017677 | 0.076844 | -0.018886 | -0.01374 | 0.049599 | -0.40283 | -0.40741 | -0.60425 | 1.5289 | 1.5335 | 1.5884 | 1.236 | 1.6891 | 2.4353 | -120.163 | 119.2017 | -2.7969 | 119.4031 | 121.3348 | -0.85602 | -0.35706 | 0.045777 | 0.20142 | 121.0419 | 121.4951 | 121.3394 | 119.3985 | 119.4031 | 122.2412 | 121.3943 | -0.35706 | 119.3985 | 119.4031 | 121.3943 | 121.3394 | 122.2412 | -2.9938 | -122.5525
6017.3438 | 122.438 | -119.9432 | 2.3346 | -0.26665 | 0.012619 | -0.018104 | 0.078126 | -0.024013 | -0.014595 | 0.047249 | -0.39368 | -0.27924 | -0.57678 | 1.4145 | 1.4236 | 1.4374 | 1.4236 | 1.5701 | 2.4307 | -120.2362 | 119.3665 | -2.6138 | 119.5496 | 121.3577 | -0.91095 | -0.29297 | 0.09613 | 0.18311 | 121.3669 | 121.5134 | 121.3669 | 119.664 | 119.5496 | 122.374 | 121.3806 | -0.29297 | 119.664 | 119.5496 | 121.3806 | 121.3669 | 122.374 | -2.9114 | -122.5708
6019.0781 | 122.5571 | -119.9112 | 2.3026 | 0.0080111 | 0.012619 | -0.016823 | 0.074281 | -0.022304 | -0.012672 | 0.051308 | -0.42572 | -0.32959 | -0.59509 | 1.4282 | 1.4603 | 1.5015 | 1.3 | 1.6067 | 2.417 | -120.1996 | 119.3161 | -2.6321 | 119.4855 | 121.3394 | -0.84228 | -0.28839 | 0.11444 | 0.16937 | 121.2112 | 121.5179 | 121.3715 | 119.5816 | 119.4855 | 122.3282 | 121.4127 | -0.28839 | 119.5816 | 119.4855 | 121.4127 | 121.3715 | 122.3282 | -2.8976 | -122.5021
6020.7812 | 122.525 | -119.8791 | 2.3712 | 0.061417 | 0.012619 | -0.012337 | 0.082612 | -0.020382 | -0.012245 | 0.057717 | -0.42572 | -0.3479 | -0.59509 | 1.3733 | 1.4008 | 1.4328 | 1.2314 | 1.5518 | 2.4673 | -120.1447 | 119.2841 | -2.7191 | 119.4534 | 121.2524 | -0.97046 | -0.2655 | 0.09613 | 0.16937 | 121.1105 | 121.431 | 121.2799 | 119.5312 | 119.4534 | 122.3465 | 121.3119 | -0.2655 | 119.5312 | 119.4534 | 121.3119 | 121.2799 | 122.3465 | -2.9663 | -122.5159
6022.4844 | 122.406 | -119.8151 | 2.4857 | -0.091171 | 0.014114 | -0.011055 | 0.084962 | -0.02145 | -0.01609 | 0.052376 | -0.54932 | -0.46692 | -0.77362 | 1.5518 | 1.5335 | 1.5701 | 1.4603 | 1.6937 | 2.5909 | -120.0668 | 119.0414 | -2.9526 | 119.2657 | 121.3669 | -0.95215 | -0.25177 | 0.10529 | 0.2243 | 121.2753 | 121.5088 | 121.3486 | 119.3481 | 119.2657 | 122.406 | 121.3852 | -0.25177 | 119.3481 | 119.2657 | 121.3852 | 121.3486 | 122.406 | -3.2593 | -122.5525
6024.2188 | 122.4472 | -120.1401 | 2.1103 | 0.00038159 | 0.014328 | -0.017036 | 0.082185 | -0.021236 | -0.015876 | 0.050026 | -0.36163 | -0.23346 | -0.54932 | 1.3046 | 1.2817 | 1.2955 | 1.268 | 1.3596 | 2.3163 | -120.4056 | 119.5908 | -2.3438 | 119.7784 | 121.4447 | -0.82855 | -0.2655 | 0.20599 | 0.18768 | 121.4081 | 121.4996 | 121.4218 | 119.9066 | 119.7784 | 122.4564 | 121.4355 | -0.2655 | 119.9066 | 119.7784 | 121.4355 | 121.4218 | 122.4564 | -2.6596 | -122.5159
6025.9219 | 122.5067 | -119.9295 | 2.2751 | 0.13771 | 0.015609 | -0.012978 | 0.08069 | -0.020168 | -0.012031 | 0.048104 | -0.44403 | -0.29297 | -0.62714 | 1.3733 | 1.4099 | 1.4374 | 1.2863 | 1.5152 | 2.4124 | -120.2728 | 119.3024 | -2.5681 | 119.4855 | 121.3028 | -0.86517 | -0.34332 | 0.13733 | 0.18311 | 121.2158 | 121.4447 | 121.3394 | 119.6365 | 119.4855 | 122.3419 | 121.3669 | -0.34332 | 119.6365 | 119.4855 | 121.3669 | 121.3394 | 122.3419 | -2.9022 | -122.5479
6027.625 | 122.5159 | -119.7784 | 2.449 | -0.045395 | 0.011978 | -0.020454 | 0.074922 | -0.022945 | -0.013099 | 0.051522 | -0.49896 | -0.41657 | -0.67291 | 1.5518 | 1.5839 | 1.6205 | 1.3641 | 1.7487 | 2.5406 | -120.0851 | 119.1055 | -2.8656 | 119.2795 | 121.3303 | -0.86517 | -0.3067 | 0.091552 | 0.17395 | 121.1426 | 121.5271 | 121.3623 | 119.3619 | 119.2795 | 122.319 | 121.3989 | -0.3067 | 119.3619 | 119.2795 | 121.3989 | 121.3623 | 122.319 | -3.1219 | -122.5342
6029.3438 | 122.3969 | -119.6548 | 2.6505 | -0.19798 | 0.012832 | -0.018318 | 0.081758 | -0.023586 | -0.01139 | 0.055367 | -0.55389 | -0.51727 | -0.75073 | 1.7807 | 1.7807 | 1.8219 | 1.5564 | 1.9638 | 2.6505 | -119.9936 | 118.9041 | -3.1677 | 119.101 | 121.4355 | -0.86975 | -0.33874 | 0 | 0.19684 | 121.2112 | 121.6187 | 121.4355 | 119.1376 | 119.101 | 122.3053 | 121.4767 | -0.33874 | 119.1376 | 119.101 | 121.4767 | 121.4355 | 122.3053 | -3.4012 | -122.644
6031.0781 | 122.4335 | -119.5633 | 2.7191 | -0.25902 | 0.011123 | -0.0149 | 0.084108 | -0.024013 | -0.013099 | 0.054939 | -0.59052 | -0.53558 | -0.78735 | 1.7761 | 1.7853 | 1.8173 | 1.7212 | 1.9455 | 2.774 | -119.9295 | 118.7759 | -3.2547 | 118.9728 | 121.3394 | -0.93384 | -0.36621 | 0.054932 | 0.19684 | 121.2845 | 121.5088 | 121.3486 | 119.0277 | 118.9728 | 122.3373 | 121.3806 | -0.36621 | 119.0277 | 118.9728 | 121.3806 | 121.3486 | 122.3373 | -3.5065 | -122.6486
6032.7969 | 122.3831 | -119.4168 | 2.8931 | -0.21324 | 0.01326 | -0.014046 | 0.085389 | -0.022945 | -0.011604 | 0.058571 | -0.70496 | -0.65918 | -0.90179 | 1.9501 | 1.9592 | 1.9867 | 1.7303 | 2.1332 | 2.9572 | -119.6594 | 118.515 | -3.5522 | 118.7119 | 121.3669 | -0.93384 | -0.24262 | 0.064087 | 0.19684 | 121.1472 | 121.55 | 121.376 | 118.7576 | 118.7119 | 122.374 | 121.4035 | -0.24262 | 118.7576 | 118.7119 | 121.4035 | 121.376 | 122.374 | -3.7949 | -122.5525
6034.5625 | 122.4197 | -120.3781 | 1.9135 | -0.21324 | 0.01091 | -0.021522 | 0.070222 | -0.022518 | -0.015449 | 0.044045 | -0.20599 | -0.16937 | -0.40741 | 1.387 | 1.4099 | 1.4328 | 1.1765 | 1.593 | 1.9821 | -120.6619 | 119.9707 | -2.0828 | 120.1721 | 121.7651 | -0.50354 | -0.28381 | 0.068665 | 0.20142 | 121.5546 | 121.9711 | 121.788 | 120.2087 | 120.1721 | 122.3602 | 121.8109 | -0.28381 | 120.2087 | 120.1721 | 121.8109 | 121.788 | 122.3602 | -2.3209 | -122.5754
6036.2656 | 122.493 | -120.2408 | 2.0142 | 0.11482 | 0.014541 | -0.013618 | 0.076417 | -0.023159 | -0.012245 | 0.046181 | -0.2243 | -0.22888 | -0.43945 | 1.4603 | 1.4557 | 1.5106 | 1.1765 | 1.6205 | 2.1149 | -120.52 | 119.8013 | -2.243 | 120.0165 | 121.7011 | -0.55847 | -0.27924 | 0.10071 | 0.21515 | 121.4172 | 121.8613 | 121.6965 | 120.0119 | 120.0165 | 122.3557 | 121.7514 | -0.27924 | 120.0119 | 120.0165 | 121.7514 | 121.6965 | 122.3557 | -2.4536 | -122.5342
6037.9688 | 122.4518 | -120.2591 | 2.0325 | -0.19035 | 0.01326 | -0.014473 | 0.079835 | -0.023372 | -0.015449 | 0.04789 | -0.33417 | -0.16479 | -0.46692 | 1.3458 | 1.3321 | 1.3504 | 1.3733 | 1.5015 | 2.1469 | -120.5658 | 119.7922 | -2.1973 | 119.9249 | 121.6049 | -0.70038 | -0.3067 | 0.11444 | 0.13275 | 121.6324 | 121.7606 | 121.5912 | 120.0943 | 119.9249 | 122.406 | 121.6095 | -0.3067 | 120.0943 | 119.9249 | 121.6095 | 121.5912 | 122.406 | -2.4994 | -122.5983
6039.7031 | 122.4335 | -120.2728 | 2.0325 | -0.20561 | 0.016678 | -0.0149 | 0.080476 | -0.022091 | -0.013527 | 0.04789 | -0.29755 | -0.15564 | -0.47607 | 1.355 | 1.3641 | 1.387 | 1.3504 | 1.5152 | 2.1423 | -120.575 | 119.7968 | -2.1881 | 119.9753 | 121.6278 | -0.66834 | -0.30212 | 0.10986 | 0.17853 | 121.6232 | 121.788 | 121.637 | 120.1172 | 119.9753 | 122.4152 | 121.6599 | -0.30212 | 120.1172 | 119.9753 | 121.6599 | 121.637 | 122.4152 | -2.5085 | -122.6074
6041.4062 | 122.4976 | -120.108 | 2.1378 | 0.1606 | 0.014969 | -0.015968 | 0.085817 | -0.020595 | -0.014595 | 0.05793 | -0.23346 | -0.23346 | -0.44403 | 1.4236 | 1.4328 | 1.4786 | 1.1398 | 1.5884 | 2.2064 | -120.3735 | 119.664 | -2.3712 | 119.8746 | 121.5317 | -0.70496 | -0.2655 | 0.068665 | 0.21057 | 121.2479 | 121.6965 | 121.5408 | 119.8746 | 119.8746 | 122.3145 | 121.5866 | -0.2655 | 119.8746 | 119.8746 | 121.5866 | 121.5408 | 122.3145 | -2.5818 | -122.5113
6043.1406 | 122.438 | -120.108 | 2.179 | -0.045395 | 0.016464 | -0.014687 | 0.089662 | -0.023372 | -0.015449 | 0.055367 | -0.31586 | -0.22888 | -0.51727 | 1.4191 | 1.4145 | 1.4236 | 1.3779 | 1.5335 | 2.298 | -120.4056 | 119.5908 | -2.4078 | 119.7922 | 121.5271 | -0.76447 | -0.29755 | 0.11902 | 0.20142 | 121.4859 | 121.6415 | 121.5225 | 119.8791 | 119.7922 | 122.406 | 121.5317 | -0.29755 | 119.8791 | 119.7922 | 121.5317 | 121.5225 | 122.406 | -2.6962 | -122.5845
6044.8438 | 122.4609 | -119.9707 | 2.3254 | -0.21324 | 0.014755 | -0.016823 | 0.090516 | -0.02145 | -0.013313 | 0.061989 | -0.41657 | -0.24261 | -0.57678 | 1.4282 | 1.4557 | 1.4648 | 1.4923 | 1.5884 | 2.4353 | -120.282 | 119.3939 | -2.5681 | 119.5541 | 121.3989 | -0.86975 | -0.31128 | 0.10986 | 0.16022 | 121.463 | 121.5591 | 121.4264 | 119.7281 | 119.5541 | 122.406 | 121.4355 | -0.31128 | 119.7281 | 119.5541 | 121.4355 | 121.4264 | 122.406 | -2.9022 | -122.6074
6046.5469 | 122.5571 | -119.9158 | 2.33 | -0.0072479 | 0.013473 | -0.0149 | 0.074067 | -0.022945 | -0.013099 | 0.05259 | -0.48981 | -0.37994 | -0.62714 | 1.6159 | 1.6663 | 1.6937 | 1.506 | 1.8036 | 2.417 | -120.2362 | 119.2886 | -2.71 | 119.426 | 121.5317 | -0.66376 | -0.32043 | 0.086975 | 0.13733 | 121.4218 | 121.7194 | 121.582 | 119.5358 | 119.426 | 122.3328 | 121.6095 | -0.32043 | 119.5358 | 119.426 | 121.6095 | 121.582 | 122.3328 | -2.9572 | -122.5662
6048.2656 | 122.5662 | -119.7601 | 2.4902 | 0.13008 | 0.014755 | -0.01255 | 0.08368 | -0.022091 | -0.012886 | 0.056435 | -0.53558 | -0.49896 | -0.75073 | 1.7624 | 1.799 | 1.8402 | 1.561 | 1.9363 | 2.5909 | -120.076 | 119.0094 | -2.9892 | 119.2245 | 121.5225 | -0.69122 | -0.31586 | 0.10071 | 0.21515 | 121.3211 | 121.6965 | 121.5591 | 119.2612 | 119.2245 | 122.3511 | 121.6003 | -0.31586 | 119.2612 | 119.2245 | 121.6003 | 121.5591 | 122.3511 | -3.241 | -122.5662
6049.9688 | 122.4243 | -120.2225 | 2.0828 | -0.083542 | 0.014541 | -0.0095597 | 0.078981 | -0.021663 | -0.015236 | 0.047463 | -0.31128 | -0.21515 | -0.51727 | 1.4465 | 1.4145 | 1.474 | 1.3641 | 1.5976 | 2.2064 | -120.5017 | 119.7052 | -2.298 | 119.9112 | 121.669 | -0.66834 | -0.27924 | 0.1236 | 0.20599 | 121.5866 | 121.8201 | 121.637 | 120.0073 | 119.9112 | 122.4289 | 121.6965 | -0.27924 | 120.0073 | 119.9112 | 121.6965 | 121.637 | 122.4289 | -2.6001 | -122.5845
6051.6719 | 122.4518 | -120.076 | 2.2339 | -0.23613 | 0.012191 | -0.015755 | 0.077699 | -0.022091 | -0.014595 | 0.049599 | -0.41657 | -0.33875 | -0.6134 | 1.5244 | 1.5518 | 1.5656 | 1.4969 | 1.6983 | 2.3254 | -120.3827 | 119.4626 | -2.5726 | 119.6594 | 121.6003 | -0.68207 | -0.3067 | 0.091552 | 0.19684 | 121.5729 | 121.7743 | 121.6278 | 119.7372 | 119.6594 | 122.4014 | 121.6415 | -0.3067 | 119.7372 | 119.6594 | 121.6415 | 121.6278 | 122.4014 | -2.8473 | -122.6166
6053.3906 | 122.4472 | -119.8837 | 2.3849 | -0.022507 | 0.012619 | -0.013832 | 0.089875 | -0.020809 | -0.015236 | 0.056862 | -0.47607 | -0.37537 | -0.68665 | 1.593 | 1.5656 | 1.6022 | 1.5656 | 1.712 | 2.4765 | -120.2042 | 119.1971 | -2.7603 | 119.4077 | 121.4767 | -0.8194 | -0.32043 | 0.091552 | 0.21057 | 121.4493 | 121.5958 | 121.4493 | 119.5084 | 119.4077 | 122.3602 | 121.4859 | -0.32043 | 119.5084 | 119.4077 | 121.4859 | 121.4493 | 122.3602 | -3.0716 | -122.5891
6055.0938 | 122.4289 | -119.9387 | 2.3804 | -0.18272 | 0.0139 | -0.017464 | 0.079194 | -0.022304 | -0.012886 | 0.056648 | -0.37079 | -0.3479 | -0.59052 | 1.68 | 1.6891 | 1.7258 | 1.4969 | 1.8677 | 2.4399 | -120.1996 | 119.3481 | -2.7283 | 119.5679 | 121.6187 | -0.69122 | -0.26093 | 0.059509 | 0.21973 | 121.4355 | 121.8063 | 121.6278 | 119.5908 | 119.5679 | 122.3785 | 121.6644 | -0.26093 | 119.5908 | 119.5679 | 121.6644 | 121.6278 | 122.3785 | -2.9709 | -122.58
6056.8125 | 122.5754 | -119.6045 | 2.6276 | 0.01564 | 0.011551 | -0.018318 | 0.086671 | -0.022304 | -0.012031 | 0.06263 | -0.42572 | -0.34332 | -0.59509 | 1.7807 | 1.8127 | 1.8539 | 1.6434 | 1.9684 | 2.7557 | -119.9341 | 119.0094 | -2.9709 | 119.1788 | 121.3852 | -0.81482 | -0.32959 | 0.12817 | 0.16937 | 121.2479 | 121.5729 | 121.4172 | 119.2612 | 119.1788 | 122.3602 | 121.4584 | -0.32959 | 119.2612 | 119.1788 | 121.4584 | 121.4172 | 122.3602 | -3.2227 | -122.5616
6058.5781 | 122.4197 | -119.5862 | 2.7649 | -0.18272 | 0.015182 | -0.019813 | 0.093934 | -0.022518 | -0.012031 | 0.06733 | -0.4303 | -0.41199 | -0.65002 | 1.9226 | 1.918 | 1.9638 | 1.6846 | 2.1011 | 2.8244 | -119.8151 | 118.9362 | -3.1769 | 119.1559 | 121.5088 | -0.84686 | -0.22888 | 0.059509 | 0.21973 | 121.2708 | 121.6873 | 121.5042 | 119.1742 | 119.1559 | 122.4106 | 121.55 | -0.22888 | 119.1742 | 119.1559 | 121.55 | 121.5042 | 122.4106 | -3.4149 | -122.58
6060.2812 | 122.493 | -119.3069 | 2.9388 | 0.17586 | 0.013046 | -0.012123 | 0.098207 | -0.021877 | -0.011818 | 0.069679 | -0.45319 | -0.44861 | -0.66834 | 2.1057 | 2.1194 | 2.1606 | 1.8036 | 2.2568 | 3.0304 | -119.5953 | 118.6386 | -3.3875 | 118.8538 | 121.4127 | -0.8194 | -0.28839 | 0.091553 | 0.21515 | 121.1105 | 121.5637 | 121.4264 | 118.8583 | 118.8538 | 122.3373 | 121.4676 | -0.28839 | 118.8583 | 118.8538 | 121.4676 | 121.4264 | 122.3373 | -3.6072 | -122.5342
6062 | 122.5067 | -119.8105 | 2.449 | 0.14534 | 0.013046 | -0.010841 | 0.084535 | -0.021877 | -0.015449 | 0.05793 | -0.33875 | -0.32044 | -0.55389 | 1.7395 | 1.7166 | 1.7899 | 1.4374 | 1.8951 | 2.5223 | -120.1172 | 119.2566 | -2.7695 | 119.4717 | 121.55 | -0.73242 | -0.3067 | 0.073242 | 0.21515 | 121.2479 | 121.7056 | 121.5271 | 119.4901 | 119.4717 | 122.3328 | 121.6003 | -0.3067 | 119.4901 | 119.4717 | 121.6003 | 121.5271 | 122.3328 | -3.0029 | -122.5662
6063.6875 | 122.4243 | -119.6915 | 2.623 | -0.15221 | 0.0186 | -0.0196 | 0.094789 | -0.021663 | -0.014595 | 0.058998 | -0.47607 | -0.37537 | -0.68665 | 1.7761 | 1.7761 | 1.7944 | 1.7166 | 1.9272 | 2.7145 | -119.9982 | 119.0048 | -2.9984 | 119.2154 | 121.4676 | -0.84686 | -0.3067 | 0.091553 | 0.21057 | 121.4081 | 121.6187 | 121.4676 | 119.3161 | 119.2154 | 122.406 | 121.4859 | -0.3067 | 119.3161 | 119.2154 | 121.4859 | 121.4676 | 122.406 | -3.3096 | -122.6212
6065.3906 | 122.5204 | -119.8196 | 2.4719 | 0.16823 | 0.012191 | -0.012978 | 0.090303 | -0.0191 | -0.01374 | 0.060066 | -0.07782 | -0.07782 | -0.29755 | 1.7075 | 1.7075 | 1.7624 | 1.4282 | 1.8631 | 2.5497 | -120.1126 | 119.5221 | -2.5497 | 119.7418 | 121.5271 | -0.76447 | -0.29297 | 0.07782 | 0.21973 | 121.2479 | 121.6827 | 121.5271 | 119.7418 | 119.7418 | 122.3694 | 121.582 | -0.29297 | 119.7418 | 119.7418 | 121.582 | 121.5271 | 122.3694 | -2.7695 | -122.5845
6067.0938 | 122.4472 | -119.5038 | 2.7969 | -0.068283 | 0.014114 | -0.015541 | 0.099275 | -0.019314 | -0.01609 | 0.067543 | -0.10071 | -0.018311 | -0.31128 | 1.8585 | 1.8265 | 1.8494 | 1.8082 | 1.9684 | 2.8885 | -119.7968 | 119.1925 | -2.8152 | 119.4031 | 121.3623 | -0.97046 | -0.29297 | 0.091553 | 0.21057 | 121.312 | 121.4722 | 121.3303 | 119.4855 | 119.4031 | 122.3923 | 121.3531 | -0.29297 | 119.4855 | 119.4031 | 121.3531 | 121.3303 | 122.3923 | -3.1082 | -122.5937
6068.7969 | 122.4518 | -119.8563 | 2.4399 | -0.12932 | 0.012619 | -0.014687 | 0.08304 | -0.024441 | -0.012672 | 0.060921 | -0.09613 | -0.073242 | -0.29297 | 1.7303 | 1.7532 | 1.799 | 1.5244 | 1.9455 | 2.5772 | -120.0851 | 119.5633 | -2.5131 | 119.7601 | 121.5866 | -0.68664 | -0.22888 | 0.13733 | 0.19684 | 121.3806 | 121.8018 | 121.6095 | 119.783 | 119.7601 | 122.4335 | 121.6553 | -0.22888 | 119.783 | 119.7601 | 121.6553 | 121.6095 | 122.4335 | -2.7328 | -122.525
6070.5625 | 122.5113 | -119.4672 | 2.8152 | -0.12169 | 0.013473 | -0.018318 | 0.088807 | -0.023372 | -0.013527 | 0.063057 | -0.064087 | -0.027466 | -0.27466 | 1.9821 | 2.0096 | 2.0462 | 1.7624 | 2.179 | 2.8976 | -119.7418 | 119.1925 | -2.8427 | 119.4031 | 121.4493 | -0.80566 | -0.27466 | 0.082397 | 0.21057 | 121.2296 | 121.6461 | 121.4767 | 119.4397 | 119.4031 | 122.3648 | 121.5134 | -0.27466 | 119.4397 | 119.4031 | 121.5134 | 121.4767 | 122.3648 | -3.0899 | -122.5571
6072.2656 | 122.5159 | -119.9936 | 2.2659 | 0.16823 | 0.013473 | -0.016609 | 0.08603 | -0.0238 | -0.014167 | 0.054939 | -0.10071 | -0.064087 | -0.31586 | 1.5747 | 1.5839 | 1.6388 | 1.3321 | 1.7303 | 2.3712 | -120.2545 | 119.6777 | -2.33 | 119.8929 | 121.5683 | -0.68207 | -0.26093 | 0.10529 | 0.21515 | 121.3257 | 121.7239 | 121.5775 | 119.9295 | 119.8929 | 122.3648 | 121.6324 | -0.26093 | 119.9295 | 119.8929 | 121.6324 | 121.5775 | 122.3648 | -2.5818 | -122.5204
6073.9688 | 122.5204 | -119.7739 | 2.5131 | 0.069046 | 0.0139 | -0.014473 | 0.095002 | -0.022518 | -0.016517 | 0.059639 | -0.19226 | -0.045776 | -0.3479 | 1.6159 | 1.6205 | 1.6708 | 1.6663 | 1.7624 | 2.623 | -120.0668 | 119.426 | -2.5589 | 119.5816 | 121.3898 | -0.89264 | -0.29297 | 0.10986 | 0.15564 | 121.4401 | 121.5363 | 121.3943 | 119.7281 | 119.5816 | 122.3969 | 121.4447 | -0.29297 | 119.7281 | 119.5816 | 121.4447 | 121.3943 | 122.3969 | -2.861 | -122.58
6075.6719 | 122.493 | -119.6045 | 2.7191 | -0.22087 | 0.015823 | -0.018318 | 0.089662 | -0.0238 | -0.013313 | 0.063271 | -0.14648 | 0 | -0.31586 | 1.7807 | 1.799 | 1.7944 | 1.8311 | 1.9455 | 2.8152 | -119.9341 | 119.2886 | -2.7191 | 119.458 | 121.3852 | -0.92011 | -0.32959 | 0.096131 | 0.16937 | 121.4355 | 121.55 | 121.4035 | 119.6045 | 119.458 | 122.4197 | 121.3989 | -0.32959 | 119.6045 | 119.458 | 121.3989 | 121.4035 | 122.4197 | -3.035 | -122.6532
6077.3906 | 122.493 | -119.4855 | 2.8152 | -0.24376 | 0.012619 | -0.017464 | 0.096071 | -0.023159 | -0.01609 | 0.066262 | -0.17395 | 0.004578 | -0.32501 | 1.8539 | 1.8585 | 1.8723 | 1.9272 | 2.0004 | 2.9297 | -119.8196 | 119.1605 | -2.8107 | 119.3115 | 121.3394 | -0.95673 | -0.33417 | 0.11444 | 0.15106 | 121.4127 | 121.4859 | 121.344 | 119.4901 | 119.3115 | 122.4152 | 121.3577 | -0.33417 | 119.4901 | 119.3115 | 121.3577 | 121.344 | 122.4152 | -3.1403 | -122.6349
6079.1094 | 122.4243 | -119.8425 | 2.4948 | -0.12169 | 0.014541 | -0.019813 | 0.093293 | -0.021877 | -0.015236 | 0.059853 | -0.13275 | -0.054932 | -0.3479 | 1.6617 | 1.6617 | 1.6846 | 1.5976 | 1.8173 | 2.5635 | -120.1309 | 119.4946 | -2.5497 | 119.7098 | 121.5042 | -0.83313 | -0.28839 | 0.068665 | 0.21515 | 121.4401 | 121.6599 | 121.5042 | 119.7876 | 119.7098 | 122.406 | 121.5271 | -0.28839 | 119.7876 | 119.7098 | 121.5271 | 121.5042 | 122.406 | -2.8427 | -122.6257
6080.8125 | 122.438 | -120.369 | 1.9958 | -0.2285 | 0.011978 | -0.016823 | 0.072572 | -0.023159 | -0.014595 | 0.04789 | -0.13275 | -0.10529 | -0.33417 | 1.3458 | 1.3596 | 1.4053 | 1.1444 | 1.5518 | 2.0737 | -120.6253 | 120.0348 | -2.1011 | 120.2362 | 121.7148 | -0.63629 | -0.25635 | 0.077819 | 0.20142 | 121.5134 | 121.9208 | 121.7285 | 120.2637 | 120.2362 | 122.4426 | 121.7743 | -0.25635 | 120.2637 | 120.2362 | 121.7743 | 121.7285 | 122.4426 | -2.33 | -122.6212
6082.5156 | 122.5525 | -119.751 | 2.5223 | 0.12245 | 0.014328 | -0.014259 | 0.077058 | -0.021236 | -0.012031 | 0.05024 | -0.13275 | -0.09613 | -0.33875 | 1.3458 | 1.3596 | 1.4145 | 1.1581 | 1.5106 | 2.6184 | -120.0394 | 119.4122 | -2.6184 | 119.6182 | 121.0968 | -1.1627 | -0.28839 | 0.09613 | 0.20599 | 120.9091 | 121.2616 | 121.1105 | 119.6548 | 119.6182 | 122.3694 | 121.1655 | -0.28839 | 119.6548 | 119.6182 | 121.1655 | 121.1105 | 122.3694 | -2.861 | -122.5616
6084.2188 | 122.4472 | -119.8563 | 2.4948 | -0.19798 | 0.013046 | -0.018959 | 0.077699 | -0.023159 | -0.013313 | 0.048531 | -0.11902 | -0.09613 | -0.35248 | 1.3596 | 1.3687 | 1.4008 | 1.149 | 1.5472 | 2.5635 | -120.108 | 119.5038 | -2.5909 | 119.7372 | 121.2158 | -1.1261 | -0.25177 | 0.068665 | 0.23346 | 121.0052 | 121.4035 | 121.225 | 119.7601 | 119.7372 | 122.4197 | 121.257 | -0.25177 | 119.7601 | 119.7372 | 121.257 | 121.225 | 122.4197 | -2.8473 | -122.6028
6085.9375 | 122.4655 | -119.8471 | 2.4994 | -0.15984 | 0.011123 | -0.015114 | 0.082826 | -0.0191 | -0.015663 | 0.049172 | -0.21057 | -0.082397 | -0.39368 | 1.2726 | 1.2909 | 1.3046 | 1.2497 | 1.4465 | 2.6001 | -120.108 | 119.4534 | -2.5818 | 119.6365 | 121.1197 | -1.2085 | -0.26093 | 0.10071 | 0.18311 | 121.0968 | 121.2936 | 121.138 | 119.7647 | 119.6365 | 122.4472 | 121.1517 | -0.26093 | 119.7647 | 119.6365 | 121.1517 | 121.138 | 122.4472 | -2.8931 | -122.6074
6087.6562 | 122.5662 | -119.6869 | 2.536 | 0.10719 | 0.012191 | -0.015968 | 0.084535 | -0.019741 | -0.013527 | 0.053231 | -0.23346 | -0.10986 | -0.38452 | 1.3 | 1.3046 | 1.3412 | 1.2451 | 1.442 | 2.6779 | -120.0256 | 119.3024 | -2.6459 | 119.4534 | 120.9869 | -1.2314 | -0.33874 | 0.14191 | 0.15106 | 120.932 | 121.1288 | 120.9915 | 119.577 | 119.4534 | 122.3648 | 121.0281 | -0.33874 | 119.577 | 119.4534 | 121.0281 | 120.9915 | 122.3648 | -2.9205 | -122.5616
6089.3594 | 122.5708 | -119.6732 | 2.5955 | -0.053024 | 0.011978 | -0.022163 | 0.075563 | -0.023372 | -0.01139 | 0.053017 | -0.20142 | -0.1236 | -0.37537 | 1.3779 | 1.4053 | 1.442 | 1.1993 | 1.5884 | 2.6779 | -120.0027 | 119.2978 | -2.7191 | 119.4717 | 121.051 | -1.1902 | -0.32959 | 0.082397 | 0.17395 | 120.8725 | 121.2616 | 121.0785 | 119.5496 | 119.4717 | 122.3511 | 121.1151 | -0.32959 | 119.5496 | 119.4717 | 121.1151 | 121.0785 | 122.3511 | -2.9709 | -122.5983
6091.0625 | 122.5616 | -119.3985 | 2.8427 | 0.15297 | 0.014541 | -0.016823 | 0.088166 | -0.019314 | -0.014167 | 0.060494 | -0.21515 | -0.10986 | -0.40283 | 1.4877 | 1.4969 | 1.5381 | 1.3733 | 1.6342 | 2.98 | -119.7189 | 118.9957 | -2.9526 | 119.1834 | 120.8862 | -1.3458 | -0.32043 | 0.13733 | 0.18768 | 120.7718 | 121.0327 | 120.8954 | 119.2886 | 119.1834 | 122.3785 | 120.9366 | -0.32043 | 119.2886 | 119.1834 | 120.9366 | 120.8954 | 122.3785 | -3.2455 | -122.5616
6092.7656 | 122.5067 | -119.8013 | 2.4948 | -0.25902 | 0.01326 | -0.019386 | 0.077699 | -0.022945 | -0.011818 | 0.053658 | -0.2655 | -0.10071 | -0.42572 | 1.2085 | 1.2177 | 1.2268 | 1.2863 | 1.387 | 2.6459 | -120.1355 | 119.3756 | -2.5955 | 119.5358 | 121.0098 | -1.2772 | -0.33417 | 0.15106 | 0.16022 | 121.0876 | 121.1884 | 121.019 | 119.7006 | 119.5358 | 122.4472 | 121.0281 | -0.33417 | 119.7006 | 119.5358 | 121.0281 | 121.019 | 122.4472 | -2.9205 | -122.6303
6094.4844 | 122.4564 | -119.7922 | 2.5589 | -0.13695 | 0.013046 | -0.013618 | 0.081544 | -0.019741 | -0.015022 | 0.051949 | -0.2243 | -0.10529 | -0.40283 | 1.2589 | 1.268 | 1.2863 | 1.2314 | 1.4145 | 2.6779 | -120.0027 | 119.3893 | -2.6642 | 119.5679 | 121.051 | -1.2909 | -0.21057 | 0.11902 | 0.17853 | 121.0236 | 121.2067 | 121.0602 | 119.6869 | 119.5679 | 122.4701 | 121.0785 | -0.21057 | 119.6869 | 119.5679 | 121.0785 | 121.0602 | 122.4701 | -2.9617 | -122.5616
6096.1875 | 121.8338 | -118.9362 | 2.1286 | -0.022507 | 0.010696 | -0.019386 | 0.059114 | -0.018673 | -0.011177 | 0.069679 | 0.059509 | 0.11902 | -0.12817 | 0.66834 | 0.73242 | 0.72784 | 0.54474 | 0.91553 | 1.9821 | -119.8654 | 118.808 | -2.0096 | 118.9957 | 119.6045 | -1.3962 | -0.92926 | -0.14648 | 0.18768 | 119.4809 | 119.8517 | 119.6686 | 119.0552 | 118.9957 | 120.9183 | 119.664 | -0.92926 | 119.0552 | 118.9957 | 119.664 | 119.6686 | 120.9183 | -2.2568 | -121.994
6097.8906 | 122.0901 | -108.9157 | 12.8677 | -0.15984 | 0.0139 | -0.0093461 | 0.35178 | -0.014614 | -0.010963 | 0.33714 | 0.12817 | 0.10071 | -0.11902 | 0.68207 | 11.9934 | 0.73242 | 0.4303 | 0.86975 | 12.8357 | -109.2957 | 108.7967 | -12.767 | 109.0439 | 109.5978 | -0.87433 | -0.37994 | -0.032044 | 0.24719 | 109.346 | 109.7855 | 120.9091 | 109.0164 | 109.0439 | 121.7514 | 109.6481 | -0.37994 | 109.0164 | 109.0439 | 109.6481 | 120.9091 | 121.7514 | -12.9868 | -122.1634
6099.6406 | 122.3145 | -120.4788 | 1.3779 | 0.10719 | 0.014328 | -0.014259 | 0.062104 | -0.019527 | -0.01374 | 0.027168 | 0 | 0.15564 | -0.1831 | 0.67291 | 1.0117 | 0.6958 | 0.65002 | 0.79651 | 1.5152 | -120.8679 | 120.2957 | -1.2222 | 120.4788 | 121.1517 | -0.36621 | -0.3891 | 0.13733 | 0.1831 | 121.1288 | 121.2753 | 121.4905 | 120.6345 | 120.4788 | 121.994 | 121.1746 | -0.3891 | 120.6345 | 120.4788 | 121.1746 | 121.4905 | 121.994 | -1.561 | -122.2458
6101.3438 | 122.2183 | -120.5612 | 1.4374 | -0.14458 | 0.013473 | -0.013618 | 0.059541 | -0.020382 | -0.012458 | 0.026741 | 0.027466 | 0.14191 | -0.16937 | 0.71869 | 0.99792 | 0.72784 | 0.68207 | 0.86517 | 1.5747 | -120.8771 | 120.3918 | -1.2955 | 120.5887 | 121.2799 | -0.43945 | -0.31586 | 0.13733 | 0.19684 | 121.2433 | 121.4264 | 121.5591 | 120.7031 | 120.5887 | 122.1359 | 121.2891 | -0.31586 | 120.7031 | 120.5887 | 121.2891 | 121.5591 | 122.1359 | -1.6068 | -122.3145
6103.0625 | 122.2458 | -120.6345 | 1.442 | -0.13695 | 0.0139 | -0.015541 | 0.052064 | -0.022091 | -0.012672 | 0.029732 | 0.091553 | 0.1236 | -0.1236 | 0.76446 | 1.0757 | 0.81482 | 0.55847 | 0.96588 | 1.5427 | -120.8908 | 120.5109 | -1.3184 | 120.726 | 121.3989 | -0.36621 | -0.25635 | 0.10071 | 0.21515 | 121.1929 | 121.6003 | 121.7102 | 120.7581 | 120.726 | 122.1771 | 121.4493 | -0.25635 | 120.7581 | 120.726 | 121.4493 | 121.7102 | 122.1771 | -1.5656 | -122.3328
6104.7656 | 122.3694 | -120.6024 | 1.442 | 0.091934 | 0.012832 | -0.014687 | 0.055909 | -0.021663 | -0.016304 | 0.029305 | 0.068665 | 0.11902 | -0.11444 | 0.71869 | 1.0162 | 0.76446 | 0.52185 | 0.89264 | 1.5427 | -120.9 | 120.488 | -1.3229 | 120.6711 | 121.3211 | -0.42572 | -0.29755 | 0.10071 | 0.18311 | 121.1243 | 121.4951 | 121.6187 | 120.7214 | 120.6711 | 122.1451 | 121.3669 | -0.29755 | 120.7214 | 120.6711 | 121.3669 | 121.6187 | 122.1451 | -1.5564 | -122.3419
6106.5 | 122.2916 | -118.5791 | 3.5202 | -0.25139 | 0.013473 | -0.015755 | 0.059327 | -0.02145 | -0.012458 | 0.031441 | 0 | 0.15106 | -0.14648 | 0.64545 | 1.4099 | 0.6546 | 0.67291 | 0.81482 | 3.6438 | -118.8675 | 118.4326 | -3.3691 | 118.5791 | 119.2245 | -2.1103 | -0.28839 | 0.1236 | 0.14648 | 119.252 | 119.3939 | 119.989 | 118.7302 | 118.5791 | 122.2229 | 119.2337 | -0.28839 | 118.7302 | 118.5791 | 119.2337 | 119.989 | 122.2229 | -3.6667 | -122.3877
6108.2031 | 122.3602 | -94.3588 | 27.5116 | 0.084305 | 0.01326 | -0.01255 | 0.47589 | -0.0092733 | 0.046501 | 0.48795 | 0.068665 | 0.086975 | -0.14191 | 0.52185 | -87.6434 | 0.55389 | 0.23346 | 0.64087 | 24.8428 | -97.1512 | 94.2169 | -27.4246 | 94.4275 | 94.8807 | -115.155 | -2.7924 | -2.6688 | 0.21057 | 94.5923 | 94.9997 | 6.7154 | 94.4458 | 94.4275 | 119.2017 | 94.9127 | -2.7924 | 94.4458 | 94.4275 | 94.9127 | 6.7154 | 119.2017 | -27.6535 | -124.6628
6109.9219 | 122.3419 | -120.6253 | 1.4923 | -0.22087 | 0.014541 | -0.020241 | 0.057618 | -0.02145 | 0.046501 | 0.089333 | 0.11444 | 0.10986 | -0.1236 | 0.75989 | -109.7305 | 0.79651 | 0.54016 | 0.97046 | 1.5518 | -120.9 | 120.5017 | -1.3824 | 120.7397 | 121.3852 | -111.2228 | -0.27466 | 0.059509 | 0.23804 | 121.1655 | 121.5958 | 10.8948 | 120.7352 | 120.7397 | 122.1771 | 121.4218 | -0.27466 | 120.7352 | 120.7397 | 121.4218 | 10.8948 | 122.1771 | -1.6159 | -122.3923
6111.6406 | 122.3511 | -113.7634 | 8.2535 | -0.014877 | 0.014328 | -0.012764 | 0.29047 | -0.017177 | 0.045433 | 0.30125 | 0.041199 | 0.11902 | -0.17853 | 0.58594 | -103.3951 | 0.60425 | 0.54474 | 0.70038 | 10.1028 | -112.3215 | 113.5849 | -8.1345 | 113.8046 | 114.3494 | -111.6486 | 1.442 | 1.8494 | 0.21973 | 114.3082 | 114.4638 | 10.3683 | 113.8824 | 113.8046 | 123.8663 | 114.3677 | 1.442 | 113.8824 | 113.8046 | 114.3677 | 10.3683 | 123.8663 | -8.432 | -120.575
6113.3438 | 122.3465 | -120.6207 | 1.5198 | -0.20561 | 0.012832 | -0.018318 | 0.056123 | -0.024227 | 0.047997 | 0.089974 | 0.086975 | 0.1236 | -0.1236 | 0.70038 | -110.6277 | 0.73242 | 0.58136 | 0.87891 | 1.5976 | -120.9091 | 120.4971 | -1.3962 | 120.7077 | 121.3211 | -112.1475 | -0.28839 | 0.07782 | 0.21057 | 121.2021 | 121.4996 | 9.993 | 120.7443 | 120.7077 | 122.2183 | 121.3531 | -0.28839 | 120.7443 | 120.7077 | 121.3531 | 9.993 | 122.2183 | -1.6434 | -122.4289
6115.0469 | 122.438 | -120.5933 | 1.5198 | -0.014877 | 0.012832 | -0.0196 | 0.054841 | -0.020809 | 0.047142 | 0.091683 | 0.032043 | 0.13733 | -0.15106 | 0.67749 | -111.4517 | 0.74158 | 0.54016 | 0.86975 | 1.6342 | -120.8862 | 120.4422 | -1.3824 | 120.6253 | 121.2708 | -112.9715 | -0.29297 | 0.11444 | 0.18311 | 121.1334 | 121.463 | 9.1415 | 120.7306 | 120.6253 | 122.2275 | 121.3348 | -0.29297 | 120.7306 | 120.6253 | 121.3348 | 9.1415 | 122.2275 | -1.6708 | -122.406
6116.75 | 122.3877 | -120.5704 | 1.5564 | 0.12245 | 0.014541 | -0.020668 | 0.061036 | -0.021663 | 0.047142 | 0.093819 | 0.086975 | 0.1236 | -0.10529 | 0.74158 | -111.3876 | 0.80109 | 0.4715 | 0.91553 | 1.6296 | -120.8633 | 120.4651 | -1.4328 | 120.6573 | 121.312 | -112.944 | -0.29297 | 0.073243 | 0.19226 | 121.0419 | 121.4859 | 9.1827 | 120.694 | 120.6573 | 122.2 | 121.3715 | -0.29297 | 120.694 | 120.6573 | 121.3715 | 9.1827 | 122.2 | -1.6617 | -122.4197
6118.4688 | 122.406 | -120.5475 | 1.5381 | 0.046158 | 0.012619 | -0.014687 | 0.063386 | -0.02145 | 0.04522 | 0.093392 | -0.022888 | 0.15106 | -0.19226 | 0.61798 | -112.6328 | 0.61798 | 0.66376 | 0.737 | 1.68 | -120.8679 | 120.3552 | -1.387 | 120.5246 | 121.1655 | -114.1708 | -0.32044 | 0.14191 | 0.16937 | 121.2112 | 121.2845 | 7.9147 | 120.6985 | 120.5246 | 122.2275 | 121.1655 | -0.32044 | 120.6985 | 120.5246 | 121.1655 | 7.9147 | 122.2275 | -1.7303 | -122.406
6120.1719 | 122.3236 | -120.5933 | 1.5793 | -0.26665 | 0.012405 | -0.016396 | 0.059755 | -0.023586 | 0.046288 | 0.093819 | 0.054932 | 0.13275 | -0.13733 | 0.66834 | -111.8729 | 0.68207 | 0.63171 | 0.83771 | 1.68 | -120.8908 | 120.4559 | -1.4465 | 120.6482 | 121.2616 | -113.4521 | -0.29755 | 0.10071 | 0.19226 | 121.225 | 121.431 | 8.7204 | 120.726 | 120.6482 | 122.2733 | 121.2753 | -0.29755 | 120.726 | 120.6482 | 121.2753 | 8.7204 | 122.2733 | -1.7166 | -122.4701
6121.8906 | 122.438 | -120.5475 | 1.5656 | 0.13771 | 0.014541 | -0.010841 | 0.064882 | -0.021023 | 0.048638 | 0.091469 | 0.009155 | 0.16022 | -0.17853 | 0.60425 | -111.2 | 0.64087 | 0.62714 | 0.72784 | 1.712 | -120.8679 | 120.369 | -1.4053 | 120.5566 | 121.1517 | -112.7655 | -0.32044 | 0.14648 | 0.18768 | 121.1746 | 121.2753 | 9.3475 | 120.7077 | 120.5566 | 122.2595 | 121.1884 | -0.32044 | 120.7077 | 120.5566 | 121.1884 | 9.3475 | 122.2595 | -1.7441 | -122.4335
6123.6406 | 122.3877 | -120.2682 | 1.8951 | 0.15297 | 0.012832 | -0.011909 | 0.058473 | -0.019741 | 0.04757 | 0.092964 | 0.10071 | 0.11902 | -0.11902 | 0.72327 | -111.4059 | 0.79193 | 0.46692 | 0.88806 | 1.9775 | -120.5429 | 120.1492 | -1.7761 | 120.369 | 120.9915 | -113.3011 | -0.27466 | 0.082397 | 0.21973 | 120.7352 | 121.1563 | 8.8623 | 120.3873 | 120.369 | 122.2458 | 121.0602 | -0.27466 | 120.3873 | 120.369 | 121.0602 | 8.8623 | 122.2458 | -2.0142 | -122.4381
6125.3281 | 122.3053 | -120.2911 | 1.9226 | -0.11406 | 0.017105 | -0.014046 | 0.063386 | -0.020168 | 0.046715 | 0.094246 | 0.041199 | 0.14191 | -0.15106 | 0.66376 | -110.9344 | 0.68665 | 0.60425 | 0.83313 | 1.9958 | -120.5887 | 120.1401 | -1.7807 | 120.3323 | 120.9549 | -112.8571 | -0.29755 | 0.073243 | 0.19226 | 120.8954 | 121.1243 | 9.3567 | 120.433 | 120.3323 | 122.287 | 120.9778 | -0.29755 | 120.433 | 120.3323 | 120.9778 | 9.3567 | 122.287 | -2.0737 | -122.5113
6127.0312 | 122.4197 | -120.2728 | 1.8768 | -0.030136 | 0.0139 | -0.018318 | 0.055482 | -0.025081 | 0.050988 | 0.093392 | 0.018311 | 0.11444 | -0.1236 | 0.66376 | -113.0127 | 0.74158 | 0.52643 | 0.88348 | 1.9684 | -120.6024 | 120.1492 | -1.7624 | 120.2911 | 120.9366 | -114.8895 | -0.32959 | 0.091553 | 0.14191 | 120.7993 | 121.1563 | 7.2601 | 120.3873 | 120.2911 | 122.2412 | 121.0144 | -0.32959 | 120.3873 | 120.2911 | 121.0144 | 7.2601 | 122.2412 | -2.0004 | -122.4792
6128.75 | 122.3053 | -120.3003 | 1.9089 | -0.098801 | 0.015182 | -0.016609 | 0.066377 | -0.021663 | 0.045861 | 0.097664 | 0.050354 | 0.1236 | -0.17853 | 0.66834 | -112.7335 | 0.71869 | 0.59967 | 0.82855 | 2.0233 | -120.5841 | 120.1218 | -1.7853 | 120.3506 | 120.9686 | -114.6423 | -0.28381 | 0.11444 | 0.22888 | 120.9 | 121.1288 | 7.5668 | 120.4239 | 120.3506 | 122.3236 | 121.019 | -0.28381 | 120.4239 | 120.3506 | 121.019 | 7.5668 | 122.3236 | -2.0874 | -122.493
6130.4531 | 122.4609 | -120.4559 | 1.6891 | 0.00038159 | 0.016464 | -0.018318 | 0.053346 | -0.022518 | -0.0096814 | 0.033364 | 0.036621 | 0.13733 | -0.14648 | 0.65918 | -3.5019 | 0.73242 | 0.52643 | 0.84686 | 1.7899 | -120.8084 | 120.3094 | -1.5518 | 120.4926 | 121.1151 | -5.191 | -0.35248 | 0.10071 | 0.18311 | 120.9824 | 121.3028 | 116.954 | 120.5933 | 120.4926 | 122.2458 | 121.1884 | -0.35248 | 120.5933 | 120.4926 | 121.1884 | 116.954 | 122.2458 | -1.8356 | -122.4976
6132.1562 | 122.2824 | -120.4147 | 1.7807 | -0.060654 | 0.014969 | -0.011696 | 0.36182 | -0.02145 | -0.009895 | 0.34098 | 0.059509 | 0.13733 | -0.16479 | 0.66376 | -6.7795 | 0.69122 | 0.61798 | 0.82855 | 1.8402 | -120.7169 | 120.2499 | -1.6434 | 120.4742 | 121.0785 | -8.5602 | -0.30212 | 0.059509 | 0.2243 | 121.0327 | 121.2433 | 113.6353 | 120.5521 | 120.4742 | 122.2549 | 121.106 | -0.30212 | 120.5521 | 120.4742 | 121.106 | 113.6353 | 122.2549 | -1.9455 | -122.4976
6133.8906 | 122.3236 | -120.282 | 1.9363 | -0.083542 | 0.016678 | -0.012764 | 0.064241 | -0.020809 | 0.048424 | 0.093178 | 0.050354 | 0.14191 | -0.15564 | 0.6546 | -109.4421 | 0.66834 | 0.62714 | 0.81482 | 2.0325 | -120.5978 | 120.1263 | -1.7944 | 120.3323 | 120.9366 | -111.3785 | -0.31586 | 0.096131 | 0.20599 | 120.9091 | 121.0968 | 10.8398 | 120.4239 | 120.3323 | 122.3145 | 120.9503 | -0.31586 | 120.4239 | 120.3323 | 120.9503 | 10.8398 | 122.3145 | -2.092 | -122.5342
6135.6406 | 122.3785 | -120.4971 | 1.6937 | -0.22087 | 0.013687 | -0.020882 | 0.050996 | -0.022304 | -0.014808 | 0.02845 | 0.009155 | 0.15106 | -0.16022 | 0.60425 | 0.17853 | 0.65918 | 0.68207 | 0.78735 | 1.8265 | -120.8542 | 120.3369 | -1.5427 | 120.5063 | 121.1014 | -1.5152 | -0.35706 | 0.13275 | 0.16937 | 121.1792 | 121.2845 | 120.6757 | 120.6482 | 120.5063 | 122.3236 | 121.1563 | -0.35706 | 120.6482 | 120.5063 | 121.1563 | 120.6757 | 122.3236 | -1.8539 | -122.5479
6137.3906 | 122.3785 | -120.5017 | 1.7029 | -0.27428 | 0.013687 | -0.018959 | 0.052491 | -0.022732 | -0.014167 | 0.027596 | 0.054932 | 0.14191 | -0.13733 | 0.64087 | 0.67291 | 0.6958 | 0.63171 | 0.82398 | 1.7944 | -120.7993 | 120.3644 | -1.561 | 120.5566 | 121.1426 | -1.03 | -0.29755 | 0.091553 | 0.19226 | 121.1334 | 121.3257 | 121.1746 | 120.6436 | 120.5566 | 122.2961 | 121.1975 | -0.29755 | 120.6436 | 120.5566 | 121.1975 | 121.1746 | 122.2961 | -1.8402 | -122.5021
6139.0938 | 122.3877 | -98.2086 | 23.9227 | 0.02327 | 0.0139 | -0.016182 | 0.43573 | -0.010128 | -0.014381 | 0.42921 | 0.041199 | 0.10529 | -0.15106 | 0.49439 | 20.9885 | 0.56763 | 0.29297 | 0.62714 | 21.3181 | -100.7309 | 98.0576 | -23.8174 | 98.2498 | 98.703 | -2.9343 | -2.5223 | -2.6047 | 0.19226 | 98.5016 | 98.8358 | 119.1971 | 98.3139 | 98.2498 | 119.5267 | 98.7762 | -2.5223 | 98.3139 | 98.2498 | 98.7762 | 119.1971 | 119.5267 | -24.0738 | -124.6536
6140.7969 | 122.3877 | -120.5704 | 1.6022 | -0.091171 | 0.013473 | -0.013405 | 0.060823 | -0.022732 | -0.015449 | 0.026955 | 0.068665 | 0.15106 | -0.16937 | 0.6546 | 1.3916 | 0.67749 | 0.59967 | 0.8194 | 1.6754 | -120.9366 | 120.401 | -1.4511 | 120.639 | 121.225 | -0.21057 | -0.36621 | 0.073242 | 0.23804 | 121.17 | 121.3898 | 121.962 | 120.7214 | 120.639 | 122.2458 | 121.2479 | -0.36621 | 120.7214 | 120.639 | 121.2479 | 121.962 | 122.2458 | -1.7715 | -122.5388
6142.5625 | 122.5113 | -120.5658 | 1.5701 | 0.053787 | 0.012832 | -0.015541 | 0.059968 | -0.020809 | -0.01374 | 0.028237 | -0.018311 | 0.14191 | -0.16937 | 0.59509 | 1.0803 | 0.63171 | 0.63629 | 0.72327 | 1.712 | -120.9595 | 120.3964 | -1.4282 | 120.5475 | 121.1609 | -0.48981 | -0.39368 | 0.14191 | 0.15106 | 121.2021 | 121.2891 | 121.6461 | 120.7077 | 120.5475 | 122.2778 | 121.1975 | -0.39368 | 120.7077 | 120.5475 | 121.1975 | 121.6461 | 122.2778 | -1.7395 | -122.5296
6144.2656 | 122.4335 | -120.6162 | 1.5884 | -0.25139 | 0.014969 | -0.019386 | 0.0542 | -0.021877 | -0.014167 | 0.027168 | -0.018311 | 0.16022 | -0.16937 | 0.59509 | 1.3733 | 0.62714 | 0.70038 | 0.76446 | 1.7212 | -120.9595 | 120.4468 | -1.4282 | 120.5978 | 121.2112 | -0.21515 | -0.34332 | 0.13275 | 0.15106 | 121.3165 | 121.3806 | 121.9894 | 120.7764 | 120.5978 | 122.3373 | 121.2433 | -0.34332 | 120.7764 | 120.5978 | 121.2433 | 121.9894 | 122.3373 | -1.7578 | -122.5479
6145.9844 | 122.4747 | -120.6024 | 1.5656 | 0.17586 | 0.012619 | -0.013191 | 0.05655 | -0.019954 | -0.014167 | 0.029732 | 0 | 0.14648 | -0.16022 | 0.62256 | 1.4145 | 0.67749 | 0.52643 | 0.81024 | 1.7029 | -120.932 | 120.4422 | -1.4191 | 120.6024 | 121.225 | -0.15106 | -0.32959 | 0.13733 | 0.16022 | 121.1288 | 121.4127 | 122.0169 | 120.7489 | 120.6024 | 122.3053 | 121.2799 | -0.32959 | 120.7489 | 120.6024 | 121.2799 | 122.0169 | 122.3053 | -1.7258 | -122.4976
6147.6875 | 121.7834 | -107.7026 | 13.9664 | -0.11406 | 0.015823 | -0.015755 | 0.41971 | -0.0094871 | -0.0086132 | 0.39823 | 0.059509 | 0.13275 | -0.16937 | 0.51727 | 8.7021 | 0.56763 | 0.45319 | 0.70038 | 14.4699 | -107.4463 | 107.5333 | -13.8336 | 107.7621 | 108.2199 | -5.2643 | 0.25635 | 0.50354 | 0.22888 | 108.1558 | 108.403 | 116.4047 | 107.8354 | 107.7621 | 122.1725 | 108.2703 | 0.25635 | 107.8354 | 107.7621 | 108.2703 | 116.4047 | 122.1725 | -14.1357 | -121.4127
6149.375 | 122.0261 | -65.5151 | 56.1584 | -0.28954 | 0.01326 | -0.020241 | 0.9621 | 0.0088845 | 0.005913 | 0.99659 | 0.022888 | 0.082397 | -0.1831 | 0.21973 | 23.6801 | 0.28839 | -0.086975 | 0.35248 | 54.2587 | -67.5201 | 65.332 | -56.0761 | 65.538 | 65.7349 | -32.4783 | -2.005 | -1.8997 | 0.20599 | 65.4282 | 65.8676 | 89.1953 | 65.5975 | 65.538 | 119.7739 | 65.8035 | -2.005 | 65.5975 | 65.538 | 65.8035 | 89.1953 | 119.7739 | -56.3416 | -123.6786
6151.0938 | 121.7606 | -12.0712 | 109.8953 | -0.022507 | 0.011123 | -0.013832 | 0.25116 | 0.030247 | 0.046288 | 0.2487 | -0.027466 | 0.073242 | -0.20599 | -0.45776 | -6.0196 | -0.13275 | -0.54932 | -0.4303 | 101.7975 | -21.5927 | 11.8652 | -109.8221 | 12.0438 | 11.6135 | -115.9149 | -9.5215 | -8.0978 | 0.17853 | 11.5219 | 11.6409 | 6.0516 | 12.1445 | 12.0438 | 113.8687 | 11.9385 | -9.5215 | 12.1445 | 12.0438 | 11.9385 | 6.0516 | 113.8687 | -110.1013 | -131.488
6152.8125 | 122.1039 | -10.112 | 111.113 | 0.0080111 | 0.014541 | -0.018318 | 0.036683 | 0.039646 | 0.05291 | 0.16752 | -0.064087 | 0.045776 | -0.23804 | -0.42572 | -5.1544 | -0.37079 | -0.62256 | -0.31586 | 111.969 | -10.35 | 9.874 | -111.0672 | 10.0479 | 9.6863 | -116.2674 | -0.23804 | 0.85602 | 0.17395 | 9.4894 | 9.7961 | 4.9576 | 10.1578 | 10.0479 | 122.081 | 9.7412 | -0.23804 | 10.1578 | 10.0479 | 9.7412 | 4.9576 | 122.081 | -111.351 | -121.463
6154.5 | 108.0002 | -12.1902 | 95.6268 | -0.030136 | 0.017105 | -0.015541 | 0.051423 | 0.039219 | 0.047997 | 0.16944 | -0.091553 | 0.045776 | -0.2655 | -0.44861 | -7.9651 | -0.42114 | -0.49896 | -0.39368 | 109.4421 | -12.9684 | 11.9247 | -95.5811 | 12.0987 | 11.7416 | -103.5919 | -0.7782 | 13.8153 | 0.17395 | 11.6913 | 11.7966 | 4.2252 | 12.236 | 12.0987 | 121.6324 | 11.7691 | -0.7782 | 12.236 | 12.0987 | 11.7691 | 4.2252 | 121.6324 | -95.8923 | -108.5953
6156.2031 | 91.2827 | -13.2202 | 80.8228 | -0.18272 | 0.013046 | -0.019813 | 0.03882 | 0.037083 | 0.049279 | 0.16431 | -0.009155 | 0.022888 | -0.2243 | -0.29297 | -7.6035 | -0.26093 | -0.60425 | -0.20142 | 109.433 | -12.9135 | 12.9959 | -80.7999 | 13.2111 | 12.9272 | -88.4262 | 0.3067 | 28.6102 | 0.21515 | 12.616 | 13.0188 | 5.6168 | 13.2431 | 13.2111 | 122.6532 | 12.9593 | 0.3067 | 13.2431 | 13.2111 | 12.9593 | 5.6168 | 122.6532 | -81.0471 | -93.7363
6157.9062 | 121.7468 | -12.1857 | 109.584 | 0.091934 | 0.014328 | -0.018318 | 0.041383 | 0.040287 | 0.050347 | 0.16431 | -0.009155 | 0.022888 | -0.21973 | -0.31128 | -7.0404 | -0.28381 | -0.65918 | -0.27466 | 109.9136 | -12.4146 | 11.9659 | -109.5612 | 12.1765 | 11.8744 | -116.6244 | -0.22888 | 0.32959 | 0.21057 | 11.5265 | 11.911 | 5.1453 | 12.2086 | 12.1765 | 122.0993 | 11.9019 | -0.22888 | 12.2086 | 12.1765 | 11.9019 | 5.1453 | 122.0993 | -109.8038 | -121.9986
6159.6094 | 122.3373 | -107.1671 | 14.653 | -0.098801 | 0.014328 | -0.016609 | 0.61923 | -0.017391 | 0.043724 | 0.66889 | 0.059509 | 0.11444 | -0.1236 | 0.59967 | -90.6876 | 0.65002 | 0.36621 | 0.79651 | 14.1266 | -108.2245 | 107.0435 | -14.5386 | 107.2266 | 107.7667 | -105.3406 | -1.0574 | -0.52643 | 0.1831 | 107.5333 | 107.9636 | 16.4795 | 107.2815 | 107.2266 | 121.2936 | 107.8171 | -1.0574 | 107.2815 | 107.2266 | 107.8171 | 16.4795 | 121.2936 | -14.7766 | -122.8775
6161.3281 | 122.3373 | -113.0447 | 8.8852 | -0.25139 | 0.014755 | -0.011269 | 0.50046 | -0.020168 | 0.047997 | 0.53346 | -0.018311 | 0.15564 | -0.1831 | 0.54932 | -101.9028 | 0.54932 | 0.59509 | 0.69122 | 8.963 | -113.1363 | 112.8616 | -8.7296 | 113.0264 | 113.5941 | -110.788 | -0.091553 | 0.07782 | 0.16479 | 113.6398 | 113.736 | 11.142 | 113.2004 | 113.0264 | 122.0078 | 113.5941 | -0.091553 | 113.2004 | 113.0264 | 113.5941 | 11.142 | 122.0078 | -9.0683 | -122.0215
6163.0312 | 122.3557 | -105.954 | 15.889 | -0.022507 | 0.014114 | -0.016609 | 1.4568 | -0.012905 | 0.044152 | 1.514 | 0.009155 | 0.1236 | -0.13275 | 0.52185 | -87.973 | 0.5722 | 0.37994 | 0.6958 | 15.7883 | -106.2698 | 105.8212 | -15.7654 | 105.9631 | 106.4758 | -103.862 | -0.31586 | -0.10071 | 0.14191 | 106.3339 | 106.6498 | 17.981 | 106.0776 | 105.9631 | 121.7422 | 106.5262 | -0.31586 | 106.0776 | 105.9631 | 106.5262 | 17.981 | 121.7422 | -16.0217 | -122.1588
6164.7656 | 122.2824 | -121.0556 | 0.94757 | -0.0072479 | 0.012405 | -0.013618 | 0.0636 | -0.020595 | 0.051201 | 0.097664 | 0.050354 | 0.14191 | -0.1831 | 0.6134 | -119.87 | 0.63629 | 0.6134 | 0.75531 | 1.062 | -121.3989 | 120.8725 | -0.80566 | 121.106 | 121.669 | -120.8176 | -0.34332 | 0.11444 | 0.23346 | 121.669 | 121.8109 | 1.1856 | 121.1975 | 121.106 | 122.1176 | 121.6919 | -0.34332 | 121.1975 | 121.106 | 121.6919 | 1.1856 | 122.1176 | -1.1307 | -122.3465
6166.5312 | 122.2504 | -115.8966 | 6.0974 | 0.11482 | 0.012191 | -0.016182 | 0.68054 | -0.016964 | 0.046929 | 0.6612 | 0.082397 | 0.09613 | -0.12817 | 0.64545 | -105.4321 | 0.71869 | 0.37537 | 0.8194 | 6.514 | -115.7501 | 115.7684 | -6.0013 | 115.979 | 116.5421 | -111.5295 | 0.14648 | 0.41656 | 0.21057 | 116.272 | 116.716 | 10.4645 | 115.9927 | 115.979 | 122.4106 | 116.6153 | 0.14648 | 115.9927 | 115.979 | 116.6153 | 10.4645 | 122.4106 | -6.2256 | -121.8475
6168.2344 | 122.1954 | -112.4634 | 9.4894 | -0.27428 | 0.01326 | -0.019173 | 1.3641 | -0.018245 | 0.045433 | 1.3988 | -0.045776 | 0.15564 | -0.1831 | 0.48523 | -97.7829 | 0.50812 | 0.59509 | 0.66834 | 10.3867 | -111.7676 | 112.2803 | -9.3338 | 112.4176 | 112.9486 | -107.2723 | 0.6958 | 0.89722 | 0.13733 | 113.0585 | 113.1317 | 14.6805 | 112.619 | 112.4176 | 122.85 | 112.9715 | 0.6958 | 112.619 | 112.4176 | 112.9715 | 14.6805 | 122.85 | -9.6725 | -121.257
6169.9375 | 122.3419 | -121.1243 | 0.88348 | -0.014877 | 0.0139 | -0.018104 | 0.056123 | -0.021023 | 0.054192 | 0.098946 | 0.050354 | 0.13275 | -0.10986 | 0.6546 | -120.2545 | 0.71411 | 0.50812 | 0.85602 | 0.96588 | -121.4355 | 121.0144 | -0.75073 | 121.1746 | 121.7789 | -121.138 | -0.31128 | 0.082397 | 0.16022 | 121.6324 | 121.9803 | 0.86975 | 121.257 | 121.1746 | 122.0901 | 121.8384 | -0.31128 | 121.257 | 121.1746 | 121.8384 | 0.86975 | 122.0901 | -0.99335 | -122.319
6171.6562 | 122.2183 | -121.1838 | 0.90637 | -0.22087 | 0.014114 | -0.015327 | 0.056764 | -0.02145 | 0.05291 | 0.098519 | 0.10071 | 0.12817 | -0.11902 | 0.71869 | -120.163 | 0.75989 | 0.50354 | 0.91553 | 0.97961 | -121.4676 | 121.0648 | -0.7782 | 121.2845 | 121.9025 | -121.0693 | -0.28381 | 0.073242 | 0.21973 | 121.6873 | 122.0993 | 1.0208 | 121.312 | 121.2845 | 122.1634 | 121.9437 | -0.28381 | 121.312 | 121.2845 | 121.9437 | 1.0208 | 122.1634 | -1.0254 | -122.374
6173.3438 | 122.3236 | -121.1792 | 0.85602 | 0.18349 | 0.012619 | -0.013191 | 0.059114 | -0.020595 | 0.051628 | 0.098946 | 0.036621 | 0.13733 | -0.16937 | 0.64545 | -120.2362 | 0.70496 | 0.48981 | 0.8194 | 0.98419 | -121.4401 | 121.0098 | -0.71869 | 121.2158 | 121.8246 | -121.0922 | -0.26093 | 0.12817 | 0.20599 | 121.669 | 121.9986 | 0.94299 | 121.3165 | 121.2158 | 122.1634 | 121.8842 | -0.26093 | 121.3165 | 121.2158 | 121.8842 | 0.94299 | 122.1634 | -1.0254 | -122.2961
6175.0625 | 122.3236 | -121.1929 | 0.8606 | 0.1606 | 0.012405 | -0.015327 | 0.061036 | -0.022518 | 0.051628 | 0.098732 | 0.068665 | 0.14648 | -0.14191 | 0.65918 | -120.1996 | 0.71869 | 0.46234 | 0.85602 | 0.98419 | -121.4539 | 121.051 | -0.71411 | 121.2616 | 121.8521 | -121.0602 | -0.26093 | 0.1236 | 0.21057 | 121.6553 | 122.049 | 0.99335 | 121.3394 | 121.2616 | 122.1771 | 121.9116 | -0.26093 | 121.3394 | 121.2616 | 121.9116 | 0.99335 | 122.1771 | -1.0025 | -122.3145
6176.7656 | 122.3053 | -121.1884 | 0.86975 | 0.046158 | 0.013687 | -0.014687 | 0.062959 | -0.021023 | 0.049706 | 0.10001 | 0.009155 | 0.16022 | -0.15106 | 0.56763 | -119.751 | 0.60883 | 0.60883 | 0.71411 | 1.0071 | -121.5042 | 121.0373 | -0.70953 | 121.1975 | 121.756 | -120.6207 | -0.31586 | 0.13733 | 0.16022 | 121.7972 | 121.9025 | 1.4374 | 121.3486 | 121.1975 | 122.1954 | 121.7972 | -0.31586 | 121.3486 | 121.1975 | 121.7972 | 1.4374 | 122.1954 | -1.0208 | -122.374
6178.4688 | 122.2549 | -121.1975 | 0.91095 | -0.21324 | 0.0139 | -0.013618 | 0.055055 | -0.021877 | 0.05291 | 0.098091 | 0.068665 | 0.1236 | -0.1236 | 0.68207 | -119.6365 | 0.72784 | 0.49896 | 0.89722 | 0.98419 | -121.5088 | 121.0739 | -0.78735 | 121.2662 | 121.8796 | -120.5475 | -0.31128 | 0.073242 | 0.19226 | 121.6965 | 122.0947 | 1.561 | 121.3211 | 121.2662 | 122.1817 | 121.9254 | -0.31128 | 121.3211 | 121.2662 | 121.9254 | 1.561 | 122.1817 | -1.0345 | -122.4197
6180.1719 | 122.3602 | -121.1975 | 0.89264 | 0.099564 | 0.011978 | -0.015327 | 0.056764 | -0.021663 | 0.05526 | 0.09745 | 0.086975 | 0.1236 | -0.10986 | 0.65918 | -119.664 | 0.71869 | 0.44861 | 0.83313 | 0.97961 | -121.5134 | 121.0876 | -0.76904 | 121.2845 | 121.8567 | -120.5566 | -0.31586 | 0.086975 | 0.19684 | 121.6461 | 122.0306 | 1.5335 | 121.3211 | 121.2845 | 122.1771 | 121.9162 | -0.31586 | 121.3211 | 121.2845 | 121.9162 | 1.5335 | 122.1771 | -1.0025 | -122.406
6181.8906 | 122.3785 | -121.1746 | 0.86975 | 0.030899 | 0.013473 | -0.020027 | 0.05655 | -0.022732 | 0.054192 | 0.10001 | 0.064087 | 0.12817 | -0.13275 | 0.65002 | -119.7052 | 0.70496 | 0.47607 | 0.8194 | 0.97504 | -121.5134 | 121.0419 | -0.74158 | 121.2387 | 121.8246 | -120.575 | -0.33875 | 0.10529 | 0.19684 | 121.6507 | 121.994 | 1.4694 | 121.3028 | 121.2387 | 122.1497 | 121.8796 | -0.33875 | 121.3028 | 121.2387 | 121.8796 | 1.4694 | 122.1497 | -1.0025 | -122.3831
6183.6406 | 122.3328 | -121.2067 | 0.86975 | 0.091934 | 0.01625 | -0.012978 | 0.062532 | -0.020382 | 0.050774 | 0.097023 | 0.009155 | 0.16937 | -0.16022 | 0.5722 | -119.7968 | 0.59052 | 0.61798 | 0.71411 | 1.0254 | -121.5271 | 121.0464 | -0.70038 | 121.2158 | 121.7789 | -120.6665 | -0.32044 | 0.15564 | 0.16937 | 121.8246 | 121.9208 | 1.4099 | 121.376 | 121.2158 | 122.2321 | 121.7972 | -0.32044 | 121.376 | 121.2158 | 121.7972 | 1.4099 | 122.2321 | -1.03 | -122.3969
6185.3906 | 122.2961 | -121.2479 | 0.87891 | -0.21324 | 0.012619 | -0.023231 | 0.058473 | -0.02145 | 0.05056 | 0.097664 | -0.022888 | 0.17395 | -0.16022 | 0.58594 | -119.783 | 0.60425 | 0.62714 | 0.76904 | 1.0071 | -121.5179 | 121.0876 | -0.70496 | 121.225 | 121.8338 | -120.6619 | -0.27008 | 0.12817 | 0.13733 | 121.875 | 122.0169 | 1.4648 | 121.4218 | 121.225 | 122.2549 | 121.8521 | -0.27008 | 121.4218 | 121.225 | 121.8521 | 1.4648 | 122.2549 | -1.0391 | -122.3969
6187.0938 | 122.3785 | -121.225 | 0.86975 | 0.00038159 | 0.013046 | -0.017891 | 0.054628 | -0.023159 | 0.05291 | 0.097664 | 0.032043 | 0.13275 | -0.13733 | 0.62714 | -119.7098 | 0.69122 | 0.48981 | 0.83313 | 0.97504 | -121.5271 | 121.0876 | -0.737 | 121.257 | 121.8521 | -120.5795 | -0.30212 | 0.10529 | 0.16937 | 121.7148 | 122.0581 | 1.5152 | 121.3577 | 121.257 | 122.2 | 121.9162 | -0.30212 | 121.3577 | 121.257 | 121.9162 | 1.5152 | 122.2 | -1.0071 | -122.3969
6188.7969 | 122.3785 | -121.225 | 0.86517 | 0.12245 | 0.014969 | -0.01255 | 0.061677 | -0.0191 | 0.050988 | 0.099373 | 0.009155 | 0.16479 | -0.16022 | 0.56763 | -119.8288 | 0.59967 | 0.59967 | 0.69122 | 1.0071 | -121.5408 | 121.0648 | -0.70038 | 121.2341 | 121.7926 | -120.694 | -0.31586 | 0.14191 | 0.16937 | 121.8246 | 121.9162 | 1.3962 | 121.3898 | 121.2341 | 122.2321 | 121.8246 | -0.31586 | 121.3898 | 121.2341 | 121.8246 | 1.3962 | 122.2321 | -1.0254 | -122.406
6190.5625 | 122.3419 | -121.2341 | 0.87891 | 0.17586 | 0.014114 | -0.016396 | 0.058687 | -0.021023 | 0.053551 | 0.097878 | 0.11444 | 0.1236 | -0.11902 | 0.6546 | -119.7281 | 0.73242 | 0.40283 | 0.83313 | 0.94757 | -121.5683 | 121.1151 | -0.75531 | 121.3486 | 121.8887 | -120.607 | -0.33417 | 0.068665 | 0.23346 | 121.637 | 122.0673 | 1.506 | 121.3577 | 121.3486 | 122.1817 | 121.9666 | -0.33417 | 121.3577 | 121.3486 | 121.9666 | 1.506 | 122.1817 | -0.99792 | -122.4472
6192.2656 | 122.2504 | -121.2479 | 0.89722 | -0.10643 | 0.0139 | -0.0097733 | 0.060182 | -0.022091 | 0.052483 | 0.096382 | 0.054932 | 0.13733 | -0.15106 | 0.62714 | -119.7876 | 0.66376 | 0.56763 | 0.78735 | 0.98877 | -121.5271 | 121.0968 | -0.75989 | 121.3028 | 121.875 | -120.6848 | -0.27924 | 0.091553 | 0.20599 | 121.8155 | 122.0352 | 1.4603 | 121.3852 | 121.3028 | 122.2366 | 121.9116 | -0.27924 | 121.3852 | 121.3028 | 121.9116 | 1.4603 | 122.2366 | -1.0483 | -122.4243
6193.9844 | 122.3785 | -121.2204 | 0.85602 | 0.046158 | 0.015396 | -0.015327 | 0.061036 | -0.020595 | 0.049065 | 0.098305 | -0.018311 | 0.15564 | -0.16479 | 0.54474 | -119.8563 | 0.57678 | 0.59052 | 0.70496 | 0.99792 | -121.5454 | 121.0556 | -0.70038 | 121.2021 | 121.7651 | -120.7123 | -0.32501 | 0.14191 | 0.14648 | 121.8109 | 121.9254 | 1.3641 | 121.376 | 121.2021 | 122.2183 | 121.7972 | -0.32501 | 121.376 | 121.2021 | 121.7972 | 1.3641 | 122.2183 | -1.0208 | -122.4014
6195.6875 | 122.319 | -121.2662 | 0.88806 | -0.2285 | 0.013687 | -0.017677 | 0.055269 | -0.02145 | 0.052697 | 0.097023 | 0 | 0.19684 | -0.16479 | 0.56305 | -119.8334 | 0.60425 | 0.6546 | 0.75073 | 1.0117 | -121.5729 | 121.1014 | -0.69122 | 121.2662 | 121.8292 | -120.7214 | -0.3067 | 0.1236 | 0.16479 | 121.9208 | 122.0169 | 1.4328 | 121.463 | 121.2662 | 122.2778 | 121.8704 | -0.3067 | 121.463 | 121.2662 | 121.8704 | 1.4328 | 122.2778 | -1.0529 | -122.4609
6197.4219 | 122.3969 | -121.2662 | 0.8606 | -0.022507 | 0.015396 | -0.016609 | 0.052705 | -0.02145 | 0.053124 | 0.097664 | 0.041199 | 0.11902 | -0.12817 | 0.59967 | -119.7968 | 0.68207 | 0.48981 | 0.79193 | 0.93842 | -121.5546 | 121.138 | -0.74158 | 121.3074 | 121.8658 | -120.6573 | -0.28839 | 0.07782 | 0.16937 | 121.756 | 122.0581 | 1.4694 | 121.3852 | 121.3074 | 122.2046 | 121.9482 | -0.28839 | 121.3852 | 121.3074 | 121.9482 | 1.4694 | 122.2046 | -0.98877 | -122.4152
6199.1406 | 122.2824 | -121.2067 | 0.94757 | -0.19035 | 0.015182 | -0.016396 | 0.060182 | -0.021023 | 0.051842 | 0.098519 | 0.018311 | 0.16022 | -0.15564 | 0.60425 | -119.7647 | 0.61798 | 0.58594 | 0.76446 | 1.03 | -121.5317 | 121.051 | -0.78735 | 121.225 | 121.8109 | -120.7123 | -0.32501 | 0.082397 | 0.17395 | 121.7926 | 121.9711 | 1.442 | 121.3669 | 121.225 | 122.2366 | 121.8246 | -0.32501 | 121.3669 | 121.225 | 121.8246 | 1.442 | 122.2366 | -1.1032 | -122.4792
6200.8438 | 122.2778 | -121.2708 | 0.92926 | -0.19035 | 0.014114 | -0.017891 | 0.054628 | -0.022945 | 0.05291 | 0.099159 | 0.07782 | 0.1236 | -0.1236 | 0.65918 | -119.7235 | 0.69122 | 0.48065 | 0.84686 | 1.0071 | -121.5317 | 121.1472 | -0.80566 | 121.3486 | 121.9299 | -120.6528 | -0.26093 | 0.07782 | 0.20142 | 121.7514 | 122.1176 | 1.5472 | 121.3943 | 121.3486 | 122.2778 | 121.962 | -0.26093 | 121.3943 | 121.3486 | 121.962 | 1.5472 | 122.2778 | -1.0529 | -122.4609
6202.5469 | 122.2916 | -121.2708 | 0.9201 | -0.2285 | 0.013473 | -0.01725 | 0.053987 | -0.022945 | 0.052056 | 0.097664 | 0.11902 | 0.10986 | -0.13733 | 0.66834 | -119.7098 | 0.70953 | 0.45319 | 0.8606 | 0.97961 | -121.5225 | 121.1334 | -0.81024 | 121.3898 | 121.9391 | -120.6299 | -0.25177 | 0.059509 | 0.25635 | 121.7239 | 122.1313 | 1.561 | 121.3806 | 121.3898 | 122.2504 | 121.9803 | -0.25177 | 121.3806 | 121.3898 | 121.9803 | 1.561 | 122.2504 | -1.0574 | -122.4426
6204.2812 | 122.2504 | -121.2662 | 0.9201 | -0.091171 | 0.013046 | -0.016823 | 0.060823 | -0.02145 | 0.050133 | 0.098305 | 0.059509 | 0.15106 | -0.15564 | 0.60883 | -119.8059 | 0.62714 | 0.54932 | 0.7782 | 1.0162 | -121.5637 | 121.1105 | -0.76904 | 121.3257 | 121.875 | -120.726 | -0.29755 | 0.09613 | 0.21515 | 121.8155 | 122.0444 | 1.4603 | 121.4172 | 121.3257 | 122.2824 | 121.8933 | -0.29755 | 121.4172 | 121.3257 | 121.8933 | 1.4603 | 122.2824 | -1.0757 | -122.4838
6206.0156 | 122.2961 | -121.2524 | 0.92926 | -0.19035 | 0.011764 | -0.014473 | 0.055909 | -0.022945 | 0.051842 | 0.095101 | 0.10071 | 0.11902 | -0.11444 | 0.6546 | -119.7098 | 0.70953 | 0.4715 | 0.8606 | 0.99335 | -121.5454 | 121.138 | -0.81024 | 121.3531 | 121.907 | -120.639 | -0.29297 | 0.064087 | 0.21515 | 121.7239 | 122.113 | 1.5427 | 121.3715 | 121.3531 | 122.2458 | 121.962 | -0.29297 | 121.3715 | 121.3531 | 121.962 | 1.5427 | 122.2458 | -1.0437 | -122.4747
6207.7188 | 122.4014 | -121.225 | 0.89264 | 0.046158 | 0.014541 | -0.01725 | 0.05356 | -0.024013 | 0.053765 | 0.095955 | 0.045776 | 0.11444 | -0.14191 | 0.59967 | -119.7601 | 0.66376 | 0.45776 | 0.78735 | 0.98419 | -121.5637 | 121.0831 | -0.7782 | 121.2708 | 121.8246 | -120.6528 | -0.33875 | 0.091553 | 0.18768 | 121.6827 | 122.0123 | 1.4648 | 121.3394 | 121.2708 | 122.2092 | 121.8887 | -0.33875 | 121.3394 | 121.2708 | 121.8887 | 1.4648 | 122.2092 | -1.0345 | -122.4564
6209.4219 | 122.2824 | -121.2708 | 0.93842 | -0.12169 | 0.013473 | -0.020882 | 0.061891 | -0.022518 | 0.051842 | 0.097023 | 0.041199 | 0.14191 | -0.17395 | 0.59509 | -119.7784 | 0.6134 | 0.54016 | 0.74616 | 1.0071 | -121.5454 | 121.0968 | -0.79651 | 121.312 | 121.8658 | -120.7169 | -0.27466 | 0.068664 | 0.21515 | 121.8109 | 122.0169 | 1.4923 | 121.4127 | 121.312 | 122.2778 | 121.8842 | -0.27466 | 121.4127 | 121.312 | 121.8842 | 1.4923 | 122.2778 | -1.1124 | -122.4838
6211.1562 | 122.3923 | -121.2662 | 0.87891 | 0.17586 | 0.013687 | -0.016396 | 0.058473 | -0.022732 | 0.05291 | 0.098519 | 0.032043 | 0.1236 | -0.15564 | 0.60883 | -119.7556 | 0.66376 | 0.40741 | 0.79193 | 0.97504 | -121.5775 | 121.1105 | -0.75531 | 121.2982 | 121.875 | -120.6345 | -0.31128 | 0.096131 | 0.18768 | 121.6736 | 122.0581 | 1.5106 | 121.3898 | 121.2982 | 122.2412 | 121.9299 | -0.31128 | 121.3898 | 121.2982 | 121.9299 | 1.5106 | 122.2412 | -1.0345 | -122.4564
6212.8594 | 122.3465 | -121.2753 | 0.90179 | -0.18272 | 0.011978 | -0.012123 | 0.053773 | -0.022945 | 0.053551 | 0.09745 | -0.004578 | 0.15564 | -0.16479 | 0.55847 | -119.8242 | 0.57678 | 0.59052 | 0.737 | 1.0208 | -121.6232 | 121.1105 | -0.74615 | 121.2708 | 121.8338 | -120.726 | -0.3479 | 0.11902 | 0.16022 | 121.8658 | 122.0123 | 1.4511 | 121.431 | 121.2708 | 122.2961 | 121.8521 | -0.3479 | 121.431 | 121.2708 | 121.8521 | 1.4511 | 122.2961 | -1.0666 | -122.525
6214.6094 | 122.3099 | -121.2753 | 0.89722 | -0.13695 | 0.014114 | -0.014046 | 0.059541 | -0.020809 | 0.051628 | 0.095528 | 0.050354 | 0.14648 | -0.16937 | 0.59052 | -119.751 | 0.59509 | 0.53101 | 0.74616 | 0.99335 | -121.55 | 121.106 | -0.75073 | 121.3257 | 121.8658 | -120.6482 | -0.27466 | 0.09613 | 0.21973 | 121.8063 | 122.0215 | 1.5244 | 121.4218 | 121.3257 | 122.2687 | 121.8704 | -0.27466 | 121.4218 | 121.3257 | 121.8704 | 1.5244 | 122.2687 | -1.0666 | -122.4472
6216.3125 | 122.3969 | -121.225 | 0.90179 | 0.12245 | 0.011978 | -0.015968 | 0.055482 | -0.02145 | 0.053124 | 0.098519 | 0.07782 | 0.10986 | -0.11902 | 0.61798 | -119.6915 | 0.68665 | 0.3891 | 0.81482 | 0.99335 | -121.5591 | 121.106 | -0.79193 | 121.3028 | 121.843 | -120.5933 | -0.33417 | 0.091553 | 0.19684 | 121.6141 | 122.0398 | 1.5335 | 121.3348 | 121.3028 | 122.2183 | 121.9116 | -0.33417 | 121.3348 | 121.3028 | 121.9116 | 1.5335 | 122.2183 | -1.0208 | -122.4609
6218.0469 | 122.3236 | -121.2753 | 0.91095 | -0.045395 | 0.014969 | -0.010841 | 0.060823 | -0.021023 | 0.051201 | 0.09745 | 0.050354 | 0.13275 | -0.15106 | 0.57678 | -119.8059 | 0.59967 | 0.54474 | 0.71869 | 1.0071 | -121.5683 | 121.1243 | -0.7782 | 121.3257 | 121.8521 | -120.7169 | -0.29297 | 0.09613 | 0.20142 | 121.8201 | 121.994 | 1.4694 | 121.4081 | 121.3257 | 122.2824 | 121.875 | -0.29297 | 121.4081 | 121.3257 | 121.875 | 1.4694 | 122.2824 | -1.062 | -122.4792
6219.7656 | 122.2961 | -121.2891 | 0.9201 | -0.11406 | 0.014114 | -0.01725 | 0.0589 | -0.022304 | 0.053124 | 0.09681 | 0.050354 | 0.14191 | -0.16479 | 0.59967 | -119.7922 | 0.62714 | 0.54016 | 0.76904 | 1.03 | -121.5729 | 121.1243 | -0.7782 | 121.3394 | 121.8887 | -120.7123 | -0.28381 | 0.10986 | 0.21515 | 121.8292 | 122.0581 | 1.4969 | 121.431 | 121.3394 | 122.319 | 121.9162 | -0.28381 | 121.431 | 121.3394 | 121.9162 | 1.4969 | 122.319 | -1.0849 | -122.493
6221.4688 | 122.3923 | -121.257 | 0.90179 | 0.10719 | 0.015823 | -0.013832 | 0.055269 | -0.019954 | 0.051415 | 0.099159 | 0.11444 | 0.1236 | -0.10986 | 0.64087 | -119.7235 | 0.70496 | 0.37537 | 0.81024 | 1.0025 | -121.5454 | 121.1472 | -0.7782 | 121.3715 | 121.8979 | -120.6253 | -0.28839 | 0.10071 | 0.2243 | 121.6324 | 122.0673 | 1.5335 | 121.3806 | 121.3715 | 122.2595 | 121.962 | -0.28839 | 121.3806 | 121.3715 | 121.962 | 1.5335 | 122.2595 | -1.0117 | -122.4472
6223.1719 | 122.319 | -121.2936 | 0.94757 | -0.18272 | 0.012619 | -0.021309 | 0.053987 | -0.022518 | 0.051201 | 0.09745 | 0.09613 | 0.10071 | -0.10986 | 0.63171 | -119.7098 | 0.67749 | 0.45319 | 0.85144 | 0.98877 | -121.6278 | 121.1838 | -0.84686 | 121.3898 | 121.9254 | -120.6573 | -0.33417 | 0.041199 | 0.20599 | 121.7468 | 122.1451 | 1.5839 | 121.3943 | 121.3898 | 122.2824 | 121.9711 | -0.33417 | 121.3943 | 121.3898 | 121.9711 | 1.5839 | 122.2824 | -1.0574 | -122.5754
6224.9062 | 122.4243 | -121.2662 | 0.89264 | 0.099564 | 0.015609 | -0.014046 | 0.056123 | -0.019314 | 0.053765 | 0.098946 | 0.10071 | 0.1236 | -0.10986 | 0.61798 | -119.7464 | 0.68665 | 0.39825 | 0.79651 | 0.99792 | -121.5546 | 121.1563 | -0.76904 | 121.3669 | 121.8842 | -120.639 | -0.28839 | 0.10529 | 0.21057 | 121.6644 | 122.0627 | 1.5198 | 121.3898 | 121.3669 | 122.2641 | 121.9528 | -0.28839 | 121.3898 | 121.3669 | 121.9528 | 1.5198 | 122.2641 | -1.0025 | -122.4472
6226.6094 | 122.3465 | -121.3211 | 0.89722 | -0.030136 | 0.01625 | -0.011269 | 0.061464 | -0.021023 | 0.050774 | 0.09745 | 0.041199 | 0.13275 | -0.16937 | 0.55847 | -119.751 | 0.58136 | 0.54016 | 0.70496 | 1.0071 | -121.6003 | 121.1517 | -0.76447 | 121.3623 | 121.8796 | -120.6482 | -0.27924 | 0.10986 | 0.21057 | 121.8613 | 122.0261 | 1.5701 | 121.4539 | 121.3623 | 122.3282 | 121.9025 | -0.27924 | 121.4539 | 121.3623 | 121.9025 | 1.5701 | 122.3282 | -1.0666 | -122.4976
6228.2969 | 122.3648 | -121.2799 | 0.90179 | -0.14458 | 0.013046 | -0.018745 | 0.051851 | -0.022732 | 0.055901 | 0.096596 | 0.086975 | 0.13275 | -0.11444 | 0.65002 | -119.6274 | 0.71411 | 0.42114 | 0.86975 | 0.98419 | -121.582 | 121.1655 | -0.76904 | 121.3669 | 121.9299 | -120.5292 | -0.30212 | 0.082398 | 0.20142 | 121.701 | 122.1497 | 1.6525 | 121.4127 | 121.3669 | 122.2641 | 121.994 | -0.30212 | 121.4127 | 121.3669 | 121.994 | 1.6525 | 122.2641 | -1.0162 | -122.4838
6230.0156 | 122.319 | -121.3074 | 0.90179 | -0.14458 | 0.011337 | -0.017677 | 0.061891 | -0.021877 | 0.049919 | 0.098732 | 0.050354 | 0.16479 | -0.16479 | 0.58594 | -119.7098 | 0.59509 | 0.53101 | 0.75073 | 0.99792 | -121.6141 | 121.1426 | -0.737 | 121.3577 | 121.8933 | -120.6116 | -0.3067 | 0.096131 | 0.21515 | 121.8384 | 122.0581 | 1.5976 | 121.4722 | 121.3577 | 122.3053 | 121.9025 | -0.3067 | 121.4722 | 121.3577 | 121.9025 | 1.5976 | 122.3053 | -1.0666 | -122.5159
6231.7188 | 122.3648 | -121.3028 | 0.90179 | -0.21324 | 0.014114 | -0.016396 | 0.055696 | -0.022732 | 0.052269 | 0.09745 | 0.082397 | 0.12817 | -0.10986 | 0.62256 | -119.664 | 0.64545 | 0.51727 | 0.78735 | 0.98877 | -121.6095 | 121.1929 | -0.77362 | 121.3852 | 121.9254 | -120.5658 | -0.3067 | 0.086976 | 0.19226 | 121.8201 | 122.0901 | 1.6388 | 121.431 | 121.3852 | 122.2916 | 121.9482 | -0.3067 | 121.431 | 121.3852 | 121.9482 | 1.6388 | 122.2916 | -1.0117 | -122.5113
6233.4062 | 122.4426 | -121.2616 | 0.87433 | 0.13008 | 0.014328 | -0.013832 | 0.059114 | -0.021663 | 0.051628 | 0.099159 | 0 | 0.15564 | -0.13733 | 0.51727 | -119.7739 | 0.55847 | 0.53558 | 0.66376 | 0.99792 | -121.6141 | 121.1243 | -0.71869 | 121.2616 | 121.7789 | -120.6482 | -0.35248 | 0.1236 | 0.13733 | 121.7972 | 121.9254 | 1.4877 | 121.4172 | 121.2616 | 122.2595 | 121.8201 | -0.35248 | 121.4172 | 121.2616 | 121.8201 | 1.4877 | 122.2595 | -1.0117 | -122.4884
6235.1406 | 122.3785 | -121.312 | 0.90179 | -0.2285 | 0.016037 | -0.016823 | 0.055482 | -0.02145 | 0.05291 | 0.09745 | -0.018311 | 0.16479 | -0.16479 | 0.54016 | -119.7556 | 0.56305 | 0.62256 | 0.71411 | 1.03 | -121.6415 | 121.1472 | -0.737 | 121.2936 | 121.8521 | -120.6573 | -0.32959 | 0.12817 | 0.14648 | 121.9345 | 122.0261 | 1.5564 | 121.4767 | 121.2936 | 122.3419 | 121.875 | -0.32959 | 121.4767 | 121.2936 | 121.875 | 1.5564 | 122.3419 | -1.0666 | -122.5433
6236.8438 | 122.438 | -121.2616 | 0.88348 | -0.083542 | 0.013687 | -0.018104 | 0.049714 | -0.022091 | 0.054833 | 0.094673 | 0.068665 | 0.13275 | -0.10529 | 0.61798 | -119.6274 | 0.69122 | 0.43945 | 0.83313 | 0.98419 | -121.5958 | 121.1563 | -0.75073 | 121.3303 | 121.8796 | -120.5109 | -0.33417 | 0.10071 | 0.17395 | 121.701 | 122.0947 | 1.6342 | 121.3943 | 121.3303 | 122.2458 | 121.9528 | -0.33417 | 121.3943 | 121.3303 | 121.9528 | 1.6342 | 122.2458 | -0.98877 | -122.4792
6238.6094 | 122.4426 | -121.2708 | 0.88806 | -0.075912 | 0.0139 | -0.01725 | 0.052705 | -0.022518 | 0.053551 | 0.097878 | 0.059509 | 0.1236 | -0.1236 | 0.63171 | -119.6411 | 0.68207 | 0.43945 | 0.82855 | 0.98419 | -121.5958 | 121.1472 | -0.76447 | 121.3303 | 121.9025 | -120.5292 | -0.32501 | 0.09613 | 0.1831 | 121.7102 | 122.0993 | 1.6296 | 121.3943 | 121.3303 | 122.2549 | 121.9528 | -0.32501 | 121.3943 | 121.3303 | 121.9528 | 1.6296 | 122.2549 | -1.0117 | -122.4838
6240.2969 | 122.4152 | -121.312 | 0.90179 | -0.12169 | 0.014969 | -0.019386 | 0.054841 | -0.0238 | 0.054833 | 0.096596 | 0.068665 | 0.1236 | -0.1236 | 0.63629 | -119.6365 | 0.69122 | 0.41657 | 0.83771 | 0.96588 | -121.6141 | 121.1884 | -0.7782 | 121.3806 | 121.9482 | -120.5383 | -0.30212 | 0.064087 | 0.19226 | 121.7285 | 122.1497 | 1.6754 | 121.4355 | 121.3806 | 122.2778 | 122.0032 | -0.30212 | 121.4355 | 121.3806 | 122.0032 | 1.6754 | 122.2778 | -1.0254 | -122.5159
6242.0625 | 122.406 | -121.3257 | 0.87433 | 0.061417 | 0.013687 | -0.012978 | 0.062745 | -0.019954 | 0.052056 | 0.09745 | 0.013733 | 0.13733 | -0.16022 | 0.5127 | -119.7739 | 0.54016 | 0.55389 | 0.67291 | 0.99335 | -121.6278 | 121.1655 | -0.737 | 121.3394 | 121.8384 | -120.6482 | -0.30212 | 0.11902 | 0.17395 | 121.8796 | 121.9986 | 1.5518 | 121.463 | 121.3394 | 122.319 | 121.8658 | -0.30212 | 121.463 | 121.3394 | 121.8658 | 1.5518 | 122.319 | -1.0345 | -122.5021
6243.7656 | 122.3648 | -121.3623 | 0.89722 | -0.19798 | 0.014114 | -0.017036 | 0.05356 | -0.023372 | 0.055046 | 0.098946 | 0.10071 | 0.10986 | -0.1236 | 0.64087 | -119.6365 | 0.68665 | 0.4303 | 0.84228 | 0.96588 | -121.6049 | 121.2387 | -0.78735 | 121.463 | 122.0032 | -120.5338 | -0.24261 | 0.068664 | 0.2243 | 121.7926 | 122.2046 | 1.7258 | 121.4722 | 121.463 | 122.3282 | 122.049 | -0.24261 | 121.4722 | 121.463 | 122.049 | 1.7258 | 122.3282 | -1.0208 | -122.5021
6245.5 | 122.3328 | -121.3394 | 0.90179 | -0.11406 | 0.014328 | -0.015541 | 0.061891 | -0.0238 | 0.053124 | 0.097237 | 0.054932 | 0.15106 | -0.13733 | 0.59052 | -119.6869 | 0.59052 | 0.5127 | 0.74158 | 0.98877 | -121.6507 | 121.2021 | -0.75073 | 121.3943 | 121.9299 | -120.5887 | -0.31128 | 0.086976 | 0.19226 | 121.8521 | 122.081 | 1.6525 | 121.4905 | 121.3943 | 122.3282 | 121.9299 | -0.31128 | 121.4905 | 121.3943 | 121.9299 | 1.6525 | 122.3282 | -1.0391 | -122.5525
6247.2188 | 122.4792 | -121.3348 | 0.85602 | 0.061417 | 0.015182 | -0.019173 | 0.053132 | -0.022304 | 0.052056 | 0.096382 | 0.064087 | 0.13275 | -0.12817 | 0.56305 | -119.6777 | 0.63629 | 0.4303 | 0.75531 | 0.97046 | -121.6232 | 121.2067 | -0.72327 | 121.3989 | 121.8979 | -120.5338 | -0.28839 | 0.11444 | 0.19226 | 121.7651 | 122.0901 | 1.6571 | 121.4676 | 121.3989 | 122.3053 | 121.9711 | -0.28839 | 121.4676 | 121.3989 | 121.9711 | 1.6571 | 122.3053 | -0.98419 | -122.4792
6248.9219 | 122.3923 | -121.3165 | 0.87891 | -0.19035 | 0.0139 | -0.016396 | 0.058259 | -0.021236 | 0.052269 | 0.096382 | 0.009155 | 0.16022 | -0.15106 | 0.54016 | -119.7144 | 0.55389 | 0.58594 | 0.71411 | 1.0071 | -121.6553 | 121.1655 | -0.71869 | 121.3257 | 121.8567 | -120.5933 | -0.33874 | 0.12817 | 0.16022 | 121.9025 | 122.0306 | 1.6022 | 121.4767 | 121.3257 | 122.3236 | 121.8704 | -0.33874 | 121.4767 | 121.3257 | 121.8704 | 1.6022 | 122.3236 | -1.03 | -122.5342
6250.6562 | 122.406 | -121.3531 | 0.89722 | -0.25902 | 0.016037 | -0.017891 | 0.055696 | -0.023586 | 0.053337 | 0.097023 | 0.032043 | 0.13275 | -0.14191 | 0.52643 | -119.6869 | 0.59052 | 0.56305 | 0.70496 | 0.99792 | -121.6736 | 121.2112 | -0.76447 | 121.3852 | 121.8796 | -120.5841 | -0.32044 | 0.10071 | 0.17395 | 121.9162 | 122.0581 | 1.6663 | 121.4859 | 121.3852 | 122.3511 | 121.9437 | -0.32044 | 121.4859 | 121.3852 | 121.9437 | 1.6663 | 122.3511 | -1.0391 | -122.5708
6252.3438 | 122.4472 | -121.312 | 0.86975 | 0.19875 | 0.013687 | -0.01725 | 0.058473 | -0.021023 | 0.052269 | 0.095741 | 0.054932 | 0.15106 | -0.14648 | 0.57678 | -119.6686 | 0.6134 | 0.4303 | 0.737 | 0.96588 | -121.6278 | 121.1655 | -0.71869 | 121.3669 | 121.8887 | -120.5383 | -0.31586 | 0.09613 | 0.20142 | 121.7422 | 122.049 | 1.6434 | 121.463 | 121.3669 | 122.2778 | 121.9254 | -0.31586 | 121.463 | 121.3669 | 121.9254 | 1.6434 | 122.2778 | -1.0162 | -122.4976
6254.0469 | 122.3648 | -121.3531 | 0.89722 | -0.068283 | 0.01326 | -0.014046 | 0.057832 | -0.022091 | 0.051415 | 0.097023 | 0.059509 | 0.15564 | -0.15106 | 0.5722 | -119.7006 | 0.59509 | 0.53101 | 0.72784 | 1.0071 | -121.6507 | 121.2021 | -0.74158 | 121.4127 | 121.9254 | -120.5978 | -0.29755 | 0.10986 | 0.21057 | 121.8842 | 122.081 | 1.6525 | 121.5088 | 121.4127 | 122.3602 | 121.9482 | -0.29755 | 121.5088 | 121.4127 | 121.9482 | 1.6525 | 122.3602 | -1.0483 | -122.5479
6255.7656 | 122.4792 | -121.3165 | 0.86975 | 0.076676 | 0.012832 | -0.014473 | 0.059114 | -0.020809 | 0.053124 | 0.099159 | -0.022888 | 0.15564 | -0.16479 | 0.51727 | -119.7968 | 0.54474 | 0.55389 | 0.66376 | 1.0025 | -121.6553 | 121.1517 | -0.71411 | 121.2936 | 121.8338 | -120.6665 | -0.33874 | 0.13275 | 0.14191 | 121.8704 | 121.9803 | 1.5198 | 121.4722 | 121.2936 | 122.319 | 121.8613 | -0.33874 | 121.4722 | 121.2936 | 121.8613 | 1.5198 | 122.319 | -1.0345 | -122.525
6257.4688 | 122.3831 | -121.344 | 0.8606 | -0.19035 | 0.016037 | -0.0102 | 0.056764 | -0.022091 | 0.054192 | 0.098305 | 0.018311 | 0.19226 | -0.15106 | 0.53101 | -119.7418 | 0.55389 | 0.59509 | 0.70038 | 1.03 | -121.6919 | 121.1929 | -0.66834 | 121.3623 | 121.875 | -120.6024 | -0.3479 | 0.16937 | 0.16937 | 121.9391 | 122.0444 | 1.6022 | 121.5363 | 121.3623 | 122.374 | 121.8979 | -0.3479 | 121.5363 | 121.3623 | 121.8979 | 1.6022 | 122.374 | -1.0117 | -122.5525
6259.1719 | 122.493 | -121.3303 | 0.86975 | -0.030136 | 0.013046 | -0.020882 | 0.049501 | -0.020809 | 0.054619 | 0.094887 | 0.050354 | 0.13275 | -0.1236 | 0.58136 | -119.6686 | 0.65002 | 0.42572 | 0.7782 | 0.97961 | -121.6232 | 121.2067 | -0.737 | 121.3806 | 121.9116 | -120.5383 | -0.29297 | 0.10986 | 0.17395 | 121.756 | 122.1085 | 1.6617 | 121.463 | 121.3806 | 122.3099 | 121.9803 | -0.29297 | 121.463 | 121.3806 | 121.9803 | 1.6617 | 122.3099 | -0.99335 | -122.493
6260.8906 | 122.5159 | -121.3303 | 0.8606 | -0.0072479 | 0.013687 | -0.018532 | 0.0542 | -0.022091 | 0.05291 | 0.096169 | 0.045776 | 0.14191 | -0.11444 | 0.58594 | -119.6732 | 0.64545 | 0.43945 | 0.76904 | 0.97046 | -121.637 | 121.2158 | -0.71869 | 121.376 | 121.9162 | -120.5338 | -0.3067 | 0.10986 | 0.16022 | 121.7697 | 122.0993 | 1.6571 | 121.4722 | 121.376 | 122.3007 | 121.9757 | -0.3067 | 121.4722 | 121.376 | 121.9757 | 1.6571 | 122.3007 | -0.97504 | -122.4976
6262.5781 | 122.5113 | -121.3165 | 0.8606 | 0.099564 | 0.014541 | -0.014046 | 0.058259 | -0.022304 | 0.053765 | 0.097664 | 0.009155 | 0.17853 | -0.15564 | 0.5127 | -119.7144 | 0.55389 | 0.52185 | 0.65002 | 0.98877 | -121.6782 | 121.1609 | -0.68207 | 121.3257 | 121.8292 | -120.575 | -0.36163 | 0.12817 | 0.16479 | 121.8384 | 121.9666 | 1.6022 | 121.4951 | 121.3257 | 122.3053 | 121.8704 | -0.36163 | 121.4951 | 121.3257 | 121.8704 | 1.6022 | 122.3053 | -1.0162 | -122.5388
6264.2812 | 122.4106 | -121.376 | 0.87891 | -0.26665 | 0.012191 | -0.016823 | 0.056123 | -0.023159 | 0.052056 | 0.096382 | 0.068665 | 0.14648 | -0.11902 | 0.57678 | -119.6686 | 0.60425 | 0.51727 | 0.76446 | 0.96588 | -121.6736 | 121.257 | -0.73242 | 121.4447 | 121.9528 | -120.5475 | -0.29755 | 0.086975 | 0.18768 | 121.8933 | 122.1405 | 1.7075 | 121.5225 | 121.4447 | 122.3419 | 121.9803 | -0.29755 | 121.5225 | 121.4447 | 121.9803 | 1.7075 | 122.3419 | -0.99792 | -122.5525
6266.0156 | 122.5067 | -121.3669 | 0.84686 | -0.014877 | 0.015609 | -0.018532 | 0.052491 | -0.02145 | 0.053978 | 0.094673 | 0.050354 | 0.12817 | -0.10529 | 0.55389 | -119.6869 | 0.6134 | 0.43488 | 0.74158 | 0.94757 | -121.669 | 121.2616 | -0.71869 | 121.4172 | 121.9208 | -120.5338 | -0.30212 | 0.10071 | 0.15564 | 121.8018 | 122.1085 | 1.68 | 121.4951 | 121.4172 | 122.3145 | 121.9803 | -0.30212 | 121.4951 | 121.4172 | 121.9803 | 1.68 | 122.3145 | -0.95215 | -122.5159
6267.7188 | 122.4655 | -121.3669 | 0.85602 | 0.14534 | 0.0139 | -0.019813 | 0.058687 | -0.019954 | 0.054192 | 0.098091 | 0.082397 | 0.14191 | -0.14191 | 0.59967 | -119.6686 | 0.6546 | 0.3891 | 0.76446 | 0.93384 | -121.6827 | 121.225 | -0.71411 | 121.4493 | 121.9666 | -120.5246 | -0.31586 | 0.07782 | 0.2243 | 121.756 | 122.1313 | 1.6983 | 121.5088 | 121.4493 | 122.3007 | 122.0215 | -0.31586 | 121.5088 | 121.4493 | 122.0215 | 1.6983 | 122.3007 | -0.99792 | -122.5388
6269.4219 | 122.5021 | -121.3486 | 0.83313 | 0.038529 | 0.014541 | -0.017036 | 0.060182 | -0.02145 | 0.052697 | 0.097237 | 0 | 0.16937 | -0.16479 | 0.49439 | -119.783 | 0.5127 | 0.55847 | 0.61798 | 0.97961 | -121.701 | 121.1838 | -0.66376 | 121.3486 | 121.843 | -120.6161 | -0.35248 | 0.14648 | 0.16479 | 121.907 | 121.9666 | 1.5656 | 121.5179 | 121.3486 | 122.3282 | 121.8613 | -0.35248 | 121.5179 | 121.3486 | 121.8613 | 1.5656 | 122.3282 | -0.99793 | -122.5342
6271.1406 | 122.4289 | -121.3531 | 0.87433 | -0.19035 | 0.012191 | -0.014046 | 0.053987 | -0.023159 | 0.053765 | 0.095955 | 0.018311 | 0.16022 | -0.14648 | 0.50812 | -119.7464 | 0.54474 | 0.56305 | 0.70496 | 0.99792 | -121.6965 | 121.2067 | -0.71411 | 121.3715 | 121.8613 | -120.6207 | -0.34332 | 0.1236 | 0.16479 | 121.9162 | 122.0581 | 1.6068 | 121.5134 | 121.3715 | 122.3511 | 121.8979 | -0.34332 | 121.5134 | 121.3715 | 121.8979 | 1.6068 | 122.3511 | -1.0208 | -122.5708
6272.8438 | 122.4747 | -121.3531 | 0.85602 | 0.091934 | 0.014541 | -0.015755 | 0.054414 | -0.023159 | 0.05291 | 0.098732 | 0.10529 | 0.12817 | -0.11444 | 0.59509 | -119.664 | 0.66376 | 0.35248 | 0.75531 | 0.95673 | -121.6553 | 121.2387 | -0.72784 | 121.4584 | 121.9482 | -120.52 | -0.30212 | 0.10071 | 0.21973 | 121.7056 | 122.1085 | 1.6891 | 121.4813 | 121.4584 | 122.3099 | 122.0169 | -0.30212 | 121.4813 | 121.4584 | 122.0169 | 1.6891 | 122.3099 | -0.97046 | -122.5113
6274.5469 | 122.5021 | -121.3348 | 0.86517 | 0.091934 | 0.014541 | -0.020668 | 0.059755 | -0.019741 | 0.053124 | 0.096596 | -0.018311 | 0.17395 | -0.15106 | 0.5127 | -119.7968 | 0.54474 | 0.53101 | 0.65002 | 0.99335 | -121.6919 | 121.1838 | -0.69122 | 121.3165 | 121.8475 | -120.6619 | -0.35706 | 0.12817 | 0.13275 | 121.8658 | 121.9849 | 1.5381 | 121.5088 | 121.3165 | 122.3282 | 121.8796 | -0.35706 | 121.5088 | 121.3165 | 121.8796 | 1.5381 | 122.3282 | -1.0162 | -122.5571
6276.2812 | 122.5159 | -121.3486 | 0.85602 | 0.11482 | 0.011551 | -0.01725 | 0.059327 | -0.022732 | 0.053337 | 0.097664 | 0.013733 | 0.1831 | -0.14648 | 0.48981 | -119.7784 | 0.54016 | 0.53101 | 0.64545 | 1.0025 | -121.7148 | 121.2021 | -0.67291 | 121.3623 | 121.8384 | -120.6345 | -0.36621 | 0.14648 | 0.16022 | 121.8796 | 121.994 | 1.5701 | 121.5317 | 121.3623 | 122.3511 | 121.8887 | -0.36621 | 121.5317 | 121.3623 | 121.8887 | 1.5701 | 122.3511 | -1.0025 | -122.5708
6277.9844 | 122.3511 | -121.3898 | 0.89264 | -0.083542 | 0.012191 | -0.016609 | 0.0589 | -0.021236 | 0.052483 | 0.09745 | 0.054932 | 0.17395 | -0.15106 | 0.55389 | -119.7144 | 0.60425 | 0.50812 | 0.72327 | 0.97961 | -121.6782 | 121.2387 | -0.71869 | 121.4447 | 121.9437 | -120.607 | -0.28839 | 0.086975 | 0.20599 | 121.8979 | 122.113 | 1.6754 | 121.5637 | 121.4447 | 122.3694 | 121.994 | -0.28839 | 121.5637 | 121.4447 | 121.994 | 1.6754 | 122.3694 | -1.0437 | -122.5708
6279.7031 | 122.5342 | -121.3715 | 0.83771 | 0.00038159 | 0.015182 | -0.011055 | 0.050355 | -0.022732 | 0.053124 | 0.098519 | 0.041199 | 0.12817 | -0.13275 | 0.55389 | -119.6777 | 0.64087 | 0.43488 | 0.737 | 0.94299 | -121.6461 | 121.2387 | -0.70953 | 121.4127 | 121.9254 | -120.5154 | -0.27466 | 0.10528 | 0.17395 | 121.8063 | 122.1085 | 1.6937 | 121.4996 | 121.4127 | 122.3145 | 122.0123 | -0.27466 | 121.4996 | 121.4127 | 122.0123 | 1.6937 | 122.3145 | -0.97046 | -122.4838
6281.4062 | 122.4335 | -121.4035 | 0.89264 | -0.25902 | 0.012191 | -0.015114 | 0.053987 | -0.024654 | 0.052269 | 0.095741 | 0.050354 | 0.14191 | -0.14648 | 0.53101 | -119.7052 | 0.56305 | 0.50354 | 0.72327 | 0.98419 | -121.6919 | 121.257 | -0.75073 | 121.4539 | 121.9345 | -120.5978 | -0.28839 | 0.091553 | 0.19684 | 121.907 | 122.1268 | 1.6983 | 121.5454 | 121.4539 | 122.3877 | 121.9666 | -0.28839 | 121.5454 | 121.4539 | 121.9666 | 1.6983 | 122.3877 | -1.0391 | -122.5845
6283.1406 | 122.5113 | -121.3531 | 0.84228 | 0.061417 | 0.015396 | -0.017891 | 0.053346 | -0.023159 | 0.053124 | 0.10001 | 0.064087 | 0.13275 | -0.11902 | 0.55389 | -119.664 | 0.61798 | 0.41199 | 0.74158 | 0.94299 | -121.7102 | 121.2341 | -0.70953 | 121.4172 | 121.907 | -120.5063 | -0.35706 | 0.10071 | 0.18311 | 121.7651 | 122.0947 | 1.6891 | 121.4859 | 121.4172 | 122.2961 | 121.9711 | -0.35706 | 121.4859 | 121.4172 | 121.9711 | 1.6891 | 122.2961 | -0.9613 | -122.5525
6284.8438 | 122.3694 | -121.3898 | 0.87891 | -0.098801 | 0.012619 | -0.015327 | 0.059327 | -0.020809 | 0.051415 | 0.096382 | 0.059509 | 0.14648 | -0.16479 | 0.58136 | -119.6823 | 0.58136 | 0.49896 | 0.72784 | 0.97961 | -121.7056 | 121.225 | -0.73242 | 121.4493 | 121.9711 | -120.5612 | -0.31586 | 0.10071 | 0.2243 | 121.8887 | 122.1176 | 1.7075 | 121.5363 | 121.4493 | 122.3694 | 121.9711 | -0.31586 | 121.5363 | 121.4493 | 121.9711 | 1.7075 | 122.3694 | -1.0437 | -122.5845
6286.5625 | 122.4747 | -121.3577 | 0.86517 | 0.16823 | 0.012832 | -0.017891 | 0.053987 | -0.02145 | 0.053337 | 0.096382 | 0.12817 | 0.11444 | -0.091553 | 0.60883 | -119.5999 | 0.6958 | 0.33875 | 0.79193 | 0.93842 | -121.6507 | 121.2662 | -0.75073 | 121.4859 | 121.9666 | -120.4651 | -0.29297 | 0.073243 | 0.21973 | 121.6965 | 122.1497 | 1.7578 | 121.4722 | 121.4859 | 122.2961 | 122.0535 | -0.29297 | 121.4722 | 121.4859 | 122.0535 | 1.7578 | 122.2961 | -0.95673 | -122.5159
6288.2656 | 122.4518 | -121.3943 | 0.8194 | -0.19035 | 0.014114 | -0.014259 | 0.054414 | -0.025936 | 0.052697 | 0.097664 | 0.09613 | 0.11902 | -0.1236 | 0.63171 | -119.5724 | 0.67749 | 0.37537 | 0.82855 | 0.92926 | -121.7285 | 121.2708 | -0.70038 | 121.4905 | 122.0261 | -120.3918 | -0.33417 | 0.10986 | 0.21973 | 121.7697 | 122.2229 | 1.8219 | 121.5134 | 121.4905 | 122.3236 | 122.0718 | -0.33417 | 121.5134 | 121.4905 | 122.0718 | 1.8219 | 122.3236 | -0.94299 | -122.5479
6289.9688 | 122.4655 | -121.4035 | 0.85144 | 0.14534 | 0.01326 | -0.0149 | 0.058046 | -0.020382 | 0.054192 | 0.096169 | 0.11902 | 0.11902 | -0.11444 | 0.60425 | -119.5999 | 0.65002 | 0.31128 | 0.76446 | 0.9201 | -121.7239 | 121.2891 | -0.73242 | 121.5225 | 122.0078 | -120.4514 | -0.32044 | 0.068665 | 0.23346 | 121.7148 | 122.168 | 1.8036 | 121.5225 | 121.5225 | 122.3236 | 122.0535 | -0.32044 | 121.5225 | 121.5225 | 122.0535 | 1.8036 | 122.3236 | -0.96588 | -122.5754
6291.6875 | 122.493 | -121.4218 | 0.82855 | 0.061417 | 0.014541 | -0.015541 | 0.061036 | -0.021236 | 0.05291 | 0.095101 | 0 | 0.17395 | -0.16937 | 0.47607 | -119.7372 | 0.49896 | 0.53101 | 0.62256 | 0.94757 | -121.7651 | 121.2524 | -0.6546 | 121.4218 | 121.8979 | -120.5658 | -0.34332 | 0.11902 | 0.16937 | 121.9528 | 122.0444 | 1.6846 | 121.5958 | 121.4218 | 122.3694 | 121.9208 | -0.34332 | 121.5958 | 121.4218 | 121.9208 | 1.6846 | 122.3694 | -0.99792 | -122.5937
6293.3906 | 122.5204 | -121.3943 | 0.82398 | -0.030136 | 0.0139 | -0.013405 | 0.049928 | -0.022091 | 0.053551 | 0.096169 | 0.045776 | 0.14191 | -0.11902 | 0.54474 | -119.6136 | 0.61798 | 0.40283 | 0.74616 | 0.92926 | -121.7331 | 121.2753 | -0.68207 | 121.4401 | 121.9391 | -120.4376 | -0.33875 | 0.10528 | 0.16479 | 121.7972 | 122.1405 | 1.7807 | 121.5363 | 121.4401 | 122.3236 | 122.0123 | -0.33875 | 121.5363 | 121.4401 | 122.0123 | 1.7807 | 122.3236 | -0.94299 | -122.5571
6295.1406 | 122.4426 | -121.4355 | 0.84686 | -0.17509 | 0.016037 | -0.013405 | 0.0589 | -0.022091 | 0.052269 | 0.096169 | 0.022888 | 0.17395 | -0.15564 | 0.51727 | -119.6274 | 0.53101 | 0.54474 | 0.67749 | 0.97046 | -121.7056 | 121.2799 | -0.67291 | 121.4584 | 121.9528 | -120.4742 | -0.27008 | 0.1236 | 0.17853 | 121.9803 | 122.113 | 1.8082 | 121.6095 | 121.4584 | 122.406 | 121.9666 | -0.27008 | 121.6095 | 121.4584 | 121.9666 | 1.8082 | 122.406 | -1.0025 | -122.5525
6296.8438 | 122.4243 | -121.4401 | 0.83771 | -0.14458 | 0.011337 | -0.018745 | 0.052278 | -0.023586 | 0.052697 | 0.095528 | 0.11444 | 0.13733 | -0.11444 | 0.6134 | -119.5084 | 0.6546 | 0.34332 | 0.83771 | 0.92926 | -121.6827 | 121.3257 | -0.70038 | 121.5546 | 122.0535 | -120.3461 | -0.24261 | 0.091552 | 0.22888 | 121.7834 | 122.2778 | 1.9318 | 121.5775 | 121.5546 | 122.3694 | 122.0947 | -0.24261 | 121.5775 | 121.5546 | 122.0947 | 1.9318 | 122.3694 | -0.95215 | -122.5204
6298.5625 | 122.5204 | -121.3989 | 0.82398 | 0.11482 | 0.015182 | -0.016609 | 0.0589 | -0.022091 | 0.050774 | 0.09745 | 0.022888 | 0.14191 | -0.15564 | 0.5127 | -119.6274 | 0.55847 | 0.41657 | 0.66376 | 0.9613 | -121.7102 | 121.2433 | -0.68207 | 121.4218 | 121.9116 | -120.4514 | -0.31128 | 0.13733 | 0.17853 | 121.8155 | 122.0627 | 1.7715 | 121.5408 | 121.4218 | 122.3602 | 121.9574 | -0.31128 | 121.5408 | 121.4218 | 121.9574 | 1.7715 | 122.3602 | -0.97962 | -122.5342
6300.2656 | 122.4518 | -121.4447 | 0.85602 | -0.15221 | 0.012191 | -0.016396 | 0.055482 | -0.022091 | 0.054192 | 0.09681 | 0.004578 | 0.14191 | -0.15106 | 0.5127 | -119.6182 | 0.53101 | 0.53558 | 0.67291 | 0.95673 | -121.7194 | 121.2936 | -0.71411 | 121.4493 | 121.9574 | -120.4742 | -0.27466 | 0.10071 | 0.15564 | 121.9803 | 122.1176 | 1.8265 | 121.5866 | 121.4493 | 122.4014 | 121.9757 | -0.27466 | 121.5866 | 121.4493 | 121.9757 | 1.8265 | 122.4014 | -1.0071 | -122.5754
6302 | 122.493 | -121.4401 | 0.83771 | 0.15297 | 0.012832 | -0.015755 | 0.058473 | -0.022091 | 0.051842 | 0.098305 | 0.10529 | 0.12817 | -0.11902 | 0.58594 | -119.5587 | 0.65002 | 0.33417 | 0.75073 | 0.91095 | -121.7239 | 121.3211 | -0.70953 | 121.5454 | 122.0261 | -120.3964 | -0.28381 | 0.073242 | 0.22431 | 121.7743 | 122.1909 | 1.8814 | 121.5683 | 121.5454 | 122.3511 | 122.0901 | -0.28381 | 121.5683 | 121.5454 | 122.0901 | 1.8814 | 122.3511 | -0.95673 | -122.5616
6303.7344 | 122.4152 | -121.4813 | 0.88348 | -0.15984 | 0.011978 | -0.020027 | 0.052064 | -0.022945 | 0.051415 | 0.095741 | 0.10986 | 0.11902 | -0.11444 | 0.57678 | -119.5267 | 0.62256 | 0.41657 | 0.7782 | 0.92468 | -121.7194 | 121.3669 | -0.76447 | 121.5912 | 122.0581 | -120.4102 | -0.23804 | 0.041199 | 0.2243 | 121.8979 | 122.2595 | 1.9547 | 121.6003 | 121.5912 | 122.406 | 122.1039 | -0.23804 | 121.6003 | 121.5912 | 122.1039 | 1.9547 | 122.406 | -0.99793 | -122.6028
6305.4375 | 122.4609 | -121.4493 | 0.8194 | -0.022507 | 0.014114 | -0.016609 | 0.059327 | -0.020809 | 0.051842 | 0.095741 | 0.032043 | 0.16479 | -0.15564 | 0.49896 | -119.632 | 0.49896 | 0.49896 | 0.60883 | 0.95215 | -121.7468 | 121.2936 | -0.6546 | 121.4813 | 121.9482 | -120.4514 | -0.29755 | 0.13275 | 0.18768 | 121.9482 | 122.0581 | 1.8173 | 121.6141 | 121.4813 | 122.4014 | 121.9482 | -0.29755 | 121.6141 | 121.4813 | 121.9482 | 1.8173 | 122.4014 | -0.97504 | -122.5662
6307.1406 | 122.4518 | -121.4447 | 0.82398 | -0.22087 | 0.0139 | -0.018532 | 0.055909 | -0.019527 | 0.053765 | 0.098305 | 0 | 0.16479 | -0.16479 | 0.48523 | -119.5587 | 0.52643 | 0.54932 | 0.6546 | 0.94757 | -121.7834 | 121.2799 | -0.65918 | 121.4447 | 121.9299 | -120.3827 | -0.33874 | 0.1236 | 0.16479 | 121.994 | 122.0993 | 1.886 | 121.6095 | 121.4447 | 122.3923 | 121.9711 | -0.33874 | 121.6095 | 121.4447 | 121.9711 | 1.886 | 122.3923 | -0.98877 | -122.6074
6308.8594 | 122.4197 | -121.4722 | 0.82855 | -0.075912 | 0.014541 | -0.015541 | 0.058259 | -0.0191 | 0.05291 | 0.097023 | 0.073242 | 0.16022 | -0.16022 | 0.52643 | -119.458 | 0.54932 | 0.45319 | 0.66834 | 0.92468 | -121.7606 | 121.312 | -0.66833 | 121.5454 | 121.9986 | -120.2866 | -0.28839 | 0.096131 | 0.23346 | 121.9254 | 122.1405 | 2.0142 | 121.6324 | 121.5454 | 122.3969 | 122.0215 | -0.28839 | 121.6324 | 121.5454 | 122.0215 | 2.0142 | 122.3969 | -0.98877 | -122.5891
6310.6094 | 122.4289 | -121.4676 | 0.85144 | -0.12932 | 0.0139 | -0.0149 | 0.050569 | -0.022518 | 0.054833 | 0.097878 | 0.10529 | 0.11902 | -0.09613 | 0.59052 | -119.4031 | 0.65918 | 0.3479 | 0.80566 | 0.90637 | -121.7422 | 121.3715 | -0.73242 | 121.5729 | 122.0581 | -120.2545 | -0.27466 | 0.054932 | 0.20142 | 121.8155 | 122.2733 | 2.0645 | 121.5866 | 121.5729 | 122.374 | 122.1268 | -0.27466 | 121.5866 | 121.5729 | 122.1268 | 2.0645 | 122.374 | -0.94757 | -122.5937
6312.2969 | 122.5296 | -121.4355 | 0.82398 | 0.076676 | 0.015396 | -0.018104 | 0.059755 | -0.019527 | 0.053337 | 0.0998 | 0.013733 | 0.15564 | -0.16022 | 0.4715 | -119.4489 | 0.53101 | 0.43945 | 0.63629 | 0.93842 | -121.7514 | 121.2753 | -0.66834 | 121.4493 | 121.907 | -120.2728 | -0.31586 | 0.11444 | 0.17395 | 121.875 | 122.0718 | 1.9867 | 121.5912 | 121.4493 | 122.374 | 121.9666 | -0.31586 | 121.5912 | 121.4493 | 121.9666 | 1.9867 | 122.374 | -0.98419 | -122.5754
6314 | 122.5662 | -121.4218 | 0.80109 | 0.11482 | 0.0139 | -0.013832 | 0.053132 | -0.020168 | 0.05526 | 0.09681 | 0.086975 | 0.11902 | -0.09613 | 0.54016 | -119.3985 | 0.60883 | 0.35706 | 0.71869 | 0.9201 | -121.7285 | 121.3257 | -0.68207 | 121.5088 | 121.962 | -120.1996 | -0.3067 | 0.11902 | 0.1831 | 121.7789 | 122.1405 | 2.0233 | 121.5408 | 121.5088 | 122.3419 | 122.0306 | -0.3067 | 121.5408 | 121.5088 | 122.0306 | 2.0233 | 122.3419 | -0.89722 | -122.5296
6315.7031 | 122.4335 | -121.4722 | 0.81482 | -0.21324 | 0.014541 | -0.016396 | 0.058259 | -0.022518 | 0.053124 | 0.095101 | 0.027466 | 0.16937 | -0.13733 | 0.50354 | -119.4397 | 0.52185 | 0.5127 | 0.66834 | 0.94299 | -121.7834 | 121.3348 | -0.64545 | 121.4996 | 121.9757 | -120.2545 | -0.31128 | 0.12817 | 0.16479 | 121.9849 | 122.1405 | 2.0325 | 121.6415 | 121.4996 | 122.4152 | 121.994 | -0.31128 | 121.6415 | 121.4996 | 121.994 | 2.0325 | 122.4152 | -0.95215 | -122.5983
6317.4062 | 122.3969 | -121.4493 | 0.84228 | -0.12169 | 0.013046 | -0.014687 | 0.058687 | -0.02145 | 0.049492 | 0.09745 | 0.073242 | 0.17395 | -0.16479 | 0.52643 | -119.4351 | 0.55847 | 0.4715 | 0.70496 | 0.93384 | -121.7514 | 121.2845 | -0.66833 | 121.5225 | 121.9757 | -120.2774 | -0.30212 | 0.091553 | 0.23804 | 121.9208 | 122.1542 | 2.0142 | 121.6232 | 121.5225 | 122.3831 | 122.0078 | -0.30212 | 121.6232 | 121.5225 | 122.0078 | 2.0142 | 122.3831 | -1.0071 | -122.5937
6319.125 | 122.5525 | -121.4539 | 0.82398 | 0.00038159 | 0.014541 | -0.018745 | 0.051423 | -0.021663 | 0.055046 | 0.097664 | 0.036621 | 0.14191 | -0.11444 | 0.5127 | -119.4809 | 0.60883 | 0.39368 | 0.72327 | 0.92926 | -121.7422 | 121.3394 | -0.68207 | 121.4905 | 121.9666 | -120.3049 | -0.28839 | 0.10528 | 0.15106 | 121.8475 | 122.1771 | 1.973 | 121.5958 | 121.4905 | 122.3831 | 122.0627 | -0.28839 | 121.5958 | 121.4905 | 122.0627 | 1.973 | 122.3831 | -0.93842 | -122.5662
6320.8281 | 122.5433 | -121.4172 | 0.78278 | 0.11482 | 0.014114 | -0.015541 | 0.058473 | -0.021023 | 0.052056 | 0.099587 | 0.022888 | 0.16479 | -0.16937 | 0.45776 | -119.5541 | 0.50812 | 0.4715 | 0.61798 | 0.94757 | -121.7743 | 121.2479 | -0.61798 | 121.4401 | 121.875 | -120.3369 | -0.35706 | 0.1648 | 0.19226 | 121.8887 | 122.0352 | 1.8631 | 121.582 | 121.4401 | 122.3648 | 121.9254 | -0.35706 | 121.582 | 121.4401 | 121.9254 | 1.8631 | 122.3648 | -0.95215 | -122.5571
6322.5469 | 122.4564 | -121.4905 | 0.8194 | -0.24376 | 0.014541 | -0.022804 | 0.057191 | -0.02145 | 0.053124 | 0.096596 | 0 | 0.16937 | -0.16937 | 0.4715 | -119.4534 | 0.49439 | 0.54016 | 0.65002 | 0.93384 | -121.8109 | 121.3211 | -0.65002 | 121.4905 | 121.962 | -120.2728 | -0.32043 | 0.11444 | 0.16937 | 122.0306 | 122.1405 | 2.037 | 121.6599 | 121.4905 | 122.4243 | 121.9849 | -0.32043 | 121.6599 | 121.4905 | 121.9849 | 2.037 | 122.4243 | -0.98877 | -122.6303
6324.25 | 122.5662 | -121.4584 | 0.81024 | 0.046158 | 0.014114 | -0.0196 | 0.05121 | -0.021236 | 0.052269 | 0.098732 | 0.064087 | 0.1236 | -0.1236 | 0.53101 | -119.4214 | 0.58136 | 0.39368 | 0.6958 | 0.91095 | -121.7651 | 121.3348 | -0.68665 | 121.5225 | 121.9894 | -120.2316 | -0.3067 | 0.10071 | 0.18768 | 121.8521 | 122.1542 | 2.037 | 121.582 | 121.5225 | 122.3694 | 122.0398 | -0.3067 | 121.582 | 121.5225 | 122.0398 | 2.037 | 122.3694 | -0.93384 | -122.5754
6325.9531 | 122.5342 | -121.4676 | 0.78278 | 0.13008 | 0.014328 | -0.016609 | 0.059755 | -0.021877 | 0.053978 | 0.095101 | 0.009155 | 0.16937 | -0.15106 | 0.48065 | -119.4992 | 0.54016 | 0.39825 | 0.64545 | 0.91553 | -121.7697 | 121.3165 | -0.6134 | 121.4767 | 121.9482 | -120.282 | -0.30212 | 0.13275 | 0.16022 | 121.8658 | 122.113 | 1.9684 | 121.637 | 121.4767 | 122.3831 | 122.0078 | -0.30212 | 121.637 | 121.4767 | 122.0078 | 1.9684 | 122.3831 | -0.93384 | -122.5525
6327.6562 | 122.58 | -121.4355 | 0.80109 | 0.01564 | 0.012832 | -0.019813 | 0.052491 | -0.02145 | 0.053124 | 0.097237 | 0.050354 | 0.14191 | -0.12817 | 0.5127 | -119.458 | 0.5722 | 0.37994 | 0.69122 | 0.89722 | -121.756 | 121.3074 | -0.65918 | 121.4859 | 121.9482 | -120.2591 | -0.32043 | 0.096131 | 0.17853 | 121.8155 | 122.1268 | 1.9775 | 121.5775 | 121.4859 | 122.3328 | 122.0078 | -0.32043 | 121.5775 | 121.4859 | 122.0078 | 1.9775 | 122.3328 | -0.92926 | -122.5571
6329.3906 | 122.5662 | -121.463 | 0.80109 | 0.038529 | 0.014755 | -0.014473 | 0.054628 | -0.021236 | 0.05526 | 0.095955 | 0.073242 | 0.13733 | -0.11902 | 0.5127 | -119.4717 | 0.58136 | 0.38452 | 0.69122 | 0.87891 | -121.7651 | 121.344 | -0.66376 | 121.5363 | 121.9757 | -120.2728 | -0.30212 | 0.07782 | 0.19226 | 121.8475 | 122.1542 | 1.9913 | 121.6003 | 121.5363 | 122.3419 | 122.0444 | -0.30212 | 121.6003 | 121.5363 | 122.0444 | 1.9913 | 122.3419 | -0.9201 | -122.5662
6331.0938 | 122.5067 | -121.4584 | 0.81482 | 0.15297 | 0.013687 | -0.014259 | 0.057191 | -0.021663 | 0.053765 | 0.09681 | 0.11444 | 0.1236 | -0.09613 | 0.56763 | -119.4626 | 0.62256 | 0.28381 | 0.73242 | 0.87891 | -121.7468 | 121.3623 | -0.69122 | 121.5729 | 122.0261 | -120.2774 | -0.28839 | 0.064087 | 0.21057 | 121.7422 | 122.1909 | 1.9958 | 121.582 | 121.5729 | 122.3373 | 122.081 | -0.28839 | 121.582 | 121.5729 | 122.081 | 1.9958 | 122.3373 | -0.91095 | -122.5616
6332.7969 | 122.4243 | -121.4859 | 0.83771 | -0.098801 | 0.015396 | -0.013405 | 0.059541 | -0.020595 | 0.049492 | 0.099587 | 0.064087 | 0.16479 | -0.14191 | 0.52643 | -119.5038 | 0.54474 | 0.44861 | 0.68665 | 0.91095 | -121.7926 | 121.344 | -0.67291 | 121.55 | 122.0123 | -120.3415 | -0.3067 | 0.073242 | 0.20599 | 121.9345 | 122.1725 | 1.9821 | 121.6507 | 121.55 | 122.3969 | 122.0306 | -0.3067 | 121.6507 | 121.55 | 122.0306 | 1.9821 | 122.3969 | -0.97962 | -122.6303
6334.5156 | 122.5571 | -121.4493 | 0.80109 | 0.10719 | 0.016464 | -0.015114 | 0.058046 | -0.02145 | 0.052269 | 0.098732 | 0.004578 | 0.16937 | -0.16479 | 0.45319 | -119.5587 | 0.49896 | 0.45319 | 0.59967 | 0.94299 | -121.7789 | 121.2845 | -0.63171 | 121.4539 | 121.9025 | -120.3598 | -0.32959 | 0.14191 | 0.16937 | 121.9025 | 122.049 | 1.8906 | 121.6187 | 121.4539 | 122.3923 | 121.9482 | -0.32959 | 121.6187 | 121.4539 | 121.9482 | 1.8906 | 122.3923 | -0.96588 | -122.58
6336.2188 | 122.4289 | -121.4813 | 0.81024 | -0.091171 | 0.012619 | -0.017464 | 0.058259 | -0.022732 | 0.052269 | 0.10044 | 0.073242 | 0.14191 | -0.14191 | 0.49896 | -119.5404 | 0.52643 | 0.44861 | 0.66376 | 0.93842 | -121.7422 | 121.3394 | -0.66834 | 121.5546 | 121.9803 | -120.3506 | -0.26093 | 0.12817 | 0.21515 | 121.9299 | 122.1451 | 1.9409 | 121.6232 | 121.5546 | 122.4197 | 122.0078 | -0.26093 | 121.6232 | 121.5546 | 122.0078 | 1.9409 | 122.4197 | -0.95215 | -122.5525
6337.9375 | 122.3969 | -121.4996 | 0.82855 | -0.098801 | 0.014541 | -0.0149 | 0.05655 | -0.020382 | 0.052056 | 0.098091 | 0.050354 | 0.14648 | -0.16022 | 0.5127 | -119.5587 | 0.54474 | 0.43945 | 0.67749 | 0.92926 | -121.788 | 121.3394 | -0.68207 | 121.55 | 122.0123 | -120.3873 | -0.28839 | 0.10071 | 0.21057 | 121.9391 | 122.1771 | 1.9409 | 121.6461 | 121.55 | 122.4289 | 122.0444 | -0.28839 | 121.6461 | 121.55 | 122.0444 | 1.9409 | 122.4289 | -0.98877 | -122.6166
6339.6562 | 122.5388 | -121.4767 | 0.7782 | 0.053787 | 0.013687 | -0.016396 | 0.057405 | -0.0191 | 0.051628 | 0.098946 | -0.004578 | 0.17395 | -0.14648 | 0.41199 | -119.6548 | 0.45776 | 0.49439 | 0.56305 | 0.91095 | -121.8155 | 121.3303 | -0.60425 | 121.4722 | 121.8887 | -120.433 | -0.33874 | 0.13275 | 0.14191 | 121.9711 | 122.0398 | 1.8219 | 121.6507 | 121.4722 | 122.3877 | 121.9345 | -0.33874 | 121.6507 | 121.4722 | 121.9345 | 1.8219 | 122.3877 | -0.92468 | -122.5937
6341.3594 | 122.4747 | -121.5179 | 0.80566 | -0.16747 | 0.013687 | -0.018318 | 0.056978 | -0.021877 | 0.05291 | 0.098091 | 0 | 0.16937 | -0.16479 | 0.43945 | -119.6091 | 0.49439 | 0.5127 | 0.62714 | 0.91553 | -121.8384 | 121.3531 | -0.63629 | 121.5179 | 121.9574 | -120.4147 | -0.32044 | 0.10986 | 0.16479 | 122.0306 | 122.1451 | 1.9089 | 121.6873 | 121.5179 | 122.4335 | 122.0123 | -0.32044 | 121.6873 | 121.5179 | 122.0123 | 1.9089 | 122.4335 | -0.97046 | -122.644
6343.0625 | 122.5845 | -121.4722 | 0.80109 | 0.00038159 | 0.013687 | -0.016396 | 0.050142 | -0.021877 | 0.055901 | 0.095741 | 0.036621 | 0.13733 | -0.11902 | 0.47607 | -119.6045 | 0.56305 | 0.37994 | 0.67749 | 0.89722 | -121.7972 | 121.3531 | -0.66376 | 121.5088 | 121.9482 | -120.4056 | -0.32501 | 0.096131 | 0.15564 | 121.8521 | 122.1497 | 1.8677 | 121.6095 | 121.5088 | 122.3694 | 122.0352 | -0.32501 | 121.6095 | 121.5088 | 122.0352 | 1.8677 | 122.3694 | -0.9201 | -122.5983
6344.7656 | 122.5296 | -121.4722 | 0.78278 | 0.16823 | 0.013687 | -0.016396 | 0.057618 | -0.019527 | 0.053551 | 0.098305 | 0.050354 | 0.13275 | -0.12817 | 0.5127 | -119.5724 | 0.5722 | 0.33875 | 0.6958 | 0.88806 | -121.7743 | 121.344 | -0.65003 | 121.5225 | 121.9849 | -120.3552 | -0.30212 | 0.10529 | 0.17853 | 121.8109 | 122.168 | 1.8997 | 121.6049 | 121.5225 | 122.3602 | 122.0444 | -0.30212 | 121.6049 | 121.5225 | 122.0444 | 1.8997 | 122.3602 | -0.91095 | -122.5571
6346.5 | 122.5708 | -121.4767 | 0.80566 | 0.0080111 | 0.014328 | -0.017891 | 0.05356 | -0.022732 | 0.056114 | 0.097664 | 0.050354 | 0.13733 | -0.1236 | 0.45319 | -119.5541 | 0.52643 | 0.38452 | 0.68207 | 0.89264 | -121.8155 | 121.3531 | -0.66834 | 121.5271 | 121.9299 | -120.3598 | -0.33874 | 0.086975 | 0.17395 | 121.8613 | 122.1588 | 1.9226 | 121.6141 | 121.5271 | 122.3694 | 122.0032 | -0.33874 | 121.6141 | 121.5271 | 122.0032 | 1.9226 | 122.3694 | -0.92926 | -122.6212
6348.2188 | 122.4655 | -121.5042 | 0.8194 | -0.19035 | 0.013046 | -0.016609 | 0.059327 | -0.024013 | 0.053337 | 0.095314 | 0 | 0.16479 | -0.16022 | 0.46692 | -119.632 | 0.47607 | 0.53101 | 0.65002 | 0.94757 | -121.8475 | 121.344 | -0.6546 | 121.5042 | 121.9711 | -120.4514 | -0.34332 | 0.12817 | 0.16022 | 122.0352 | 122.1542 | 1.8723 | 121.669 | 121.5042 | 122.4518 | 121.9803 | -0.34332 | 121.669 | 121.5042 | 121.9803 | 1.8723 | 122.4518 | -0.97961 | -122.6669
6349.9219 | 122.5662 | -121.4722 | 0.80109 | -0.030136 | 0.014755 | -0.020454 | 0.052064 | -0.023159 | 0.053337 | 0.094673 | 0.050354 | 0.16022 | -0.11902 | 0.50354 | -119.5541 | 0.58136 | 0.37079 | 0.72327 | 0.89264 | -121.7972 | 121.3531 | -0.64087 | 121.5225 | 121.9757 | -120.3552 | -0.32501 | 0.091553 | 0.16937 | 121.843 | 122.1954 | 1.918 | 121.6324 | 121.5225 | 122.3648 | 122.0535 | -0.32501 | 121.6324 | 121.5225 | 122.0535 | 1.918 | 122.3648 | -0.9201 | -122.5983
6351.6406 | 122.4884 | -121.5088 | 0.82398 | -0.24376 | 0.014755 | -0.021522 | 0.057191 | -0.022945 | 0.052697 | 0.096169 | -0.004578 | 0.17853 | -0.15106 | 0.45776 | -119.6732 | 0.48065 | 0.52643 | 0.63629 | 0.92926 | -121.8155 | 121.3577 | -0.64545 | 121.5042 | 121.9666 | -120.4971 | -0.3067 | 0.10528 | 0.14648 | 122.0352 | 122.1451 | 1.8356 | 121.6873 | 121.5042 | 122.438 | 121.9894 | -0.3067 | 121.6873 | 121.5042 | 121.9894 | 1.8356 | 122.438 | -0.97504 | -122.6395
6353.3438 | 122.5662 | -121.4767 | 0.81482 | -0.037765 | 0.01326 | -0.012978 | 0.054414 | -0.022732 | 0.055046 | 0.097023 | 0.059509 | 0.13275 | -0.1236 | 0.51727 | -119.6091 | 0.58594 | 0.35248 | 0.75073 | 0.89722 | -121.7972 | 121.3531 | -0.68207 | 121.5363 | 121.994 | -120.4239 | -0.32043 | 0.082398 | 0.1831 | 121.8292 | 122.2275 | 1.8677 | 121.6095 | 121.5363 | 122.374 | 122.0627 | -0.32043 | 121.6095 | 121.5363 | 122.0627 | 1.8677 | 122.374 | -0.93841 | -122.612
6355.0469 | 122.5433 | -121.4584 | 0.79651 | 0.084305 | 0.014541 | -0.014687 | 0.060395 | -0.020168 | 0.052483 | 0.096382 | 0.018311 | 0.14648 | -0.15564 | 0.46234 | -119.6411 | 0.48981 | 0.41199 | 0.60883 | 0.92926 | -121.7926 | 121.3028 | -0.65003 | 121.4767 | 121.9208 | -120.4376 | -0.33417 | 0.13275 | 0.17395 | 121.8704 | 122.0673 | 1.8173 | 121.6049 | 121.4767 | 122.3877 | 121.9482 | -0.33417 | 121.6049 | 121.4767 | 121.9482 | 1.8173 | 122.3877 | -0.95215 | -122.5891
6356.7812 | 122.4518 | -121.5408 | 0.8194 | -0.15984 | 0.012619 | -0.0149 | 0.052064 | -0.023372 | 0.052269 | 0.09745 | 0.11444 | 0.13275 | -0.11444 | 0.55847 | -119.5724 | 0.60425 | 0.33417 | 0.76446 | 0.87433 | -121.7972 | 121.4264 | -0.68665 | 121.6553 | 122.0993 | -120.3918 | -0.25635 | 0.054932 | 0.22888 | 121.875 | 122.3053 | 1.9684 | 121.6736 | 121.6553 | 122.4152 | 122.1451 | -0.25635 | 121.6736 | 121.6553 | 122.1451 | 1.9684 | 122.4152 | -0.93384 | -122.6166
6358.5312 | 122.58 | -121.4722 | 0.77362 | 0.12245 | 0.011764 | -0.013618 | 0.060609 | -0.020595 | 0.050988 | 0.098091 | 0.018311 | 0.16479 | -0.15106 | 0.43488 | -119.7189 | 0.48523 | 0.44403 | 0.57678 | 0.92468 | -121.8384 | 121.3211 | -0.60883 | 121.4905 | 121.907 | -120.4926 | -0.36621 | 0.15106 | 0.16937 | 121.9162 | 122.0489 | 1.7532 | 121.637 | 121.4905 | 122.3969 | 121.9574 | -0.36621 | 121.637 | 121.4905 | 121.9574 | 1.7532 | 122.3969 | -0.92468 | -122.612
6360.2344 | 122.4564 | -121.5317 | 0.81482 | -0.19035 | 0.011978 | -0.017891 | 0.058473 | -0.024013 | 0.050774 | 0.096169 | 0.027466 | 0.15564 | -0.16022 | 0.48065 | -119.6365 | 0.50354 | 0.47607 | 0.64545 | 0.9201 | -121.8246 | 121.3715 | -0.65918 | 121.5591 | 122.0123 | -120.4514 | -0.29297 | 0.10529 | 0.18768 | 122.0078 | 122.1771 | 1.8951 | 121.6873 | 121.5591 | 122.4518 | 122.0352 | -0.29297 | 121.6873 | 121.5591 | 122.0352 | 1.8951 | 122.4518 | -0.97504 | -122.6395
6361.9531 | 122.5845 | -121.4859 | 0.80109 | -0.0072479 | 0.01326 | -0.016182 | 0.050142 | -0.022304 | 0.054192 | 0.096169 | 0.054932 | 0.15564 | -0.09613 | 0.49439 | -119.5724 | 0.54932 | 0.35248 | 0.6958 | 0.88806 | -121.8521 | 121.3898 | -0.64545 | 121.5408 | 121.9803 | -120.3735 | -0.36621 | 0.086976 | 0.15106 | 121.8384 | 122.1817 | 1.9135 | 121.6415 | 121.5408 | 122.374 | 122.0352 | -0.36621 | 121.6415 | 121.5408 | 122.0352 | 1.9135 | 122.374 | -0.89722 | -122.6532
6363.6719 | 122.5067 | -121.5271 | 0.82398 | -0.16747 | 0.014969 | -0.014473 | 0.054841 | -0.02145 | 0.052269 | 0.096382 | 0.013733 | 0.15106 | -0.13275 | 0.46692 | -119.6503 | 0.46692 | 0.5127 | 0.63629 | 0.92468 | -121.8246 | 121.3943 | -0.67291 | 121.5408 | 121.994 | -120.4742 | -0.29755 | 0.10071 | 0.14648 | 122.0398 | 122.1634 | 1.8768 | 121.6782 | 121.5408 | 122.4518 | 121.994 | -0.29755 | 121.6782 | 121.5408 | 121.994 | 1.8768 | 122.4518 | -0.95673 | -122.6486
6365.375 | 122.5433 | -121.5179 | 0.78735 | 0.11482 | 0.014328 | -0.020241 | 0.0542 | -0.020168 | 0.052056 | 0.098732 | 0.10071 | 0.1236 | -0.11902 | 0.52643 | -119.5679 | 0.59967 | 0.27924 | 0.70038 | 0.88806 | -121.7926 | 121.3989 | -0.66376 | 121.6187 | 122.0444 | -120.3552 | -0.27466 | 0.10071 | 0.21973 | 121.7972 | 122.2183 | 1.9501 | 121.6415 | 121.6187 | 122.406 | 122.1176 | -0.27466 | 121.6415 | 121.6187 | 122.1176 | 1.9501 | 122.406 | -0.90637 | -122.58
6367.1094 | 122.5021 | -121.5225 | 0.80566 | -0.19035 | 0.011337 | -0.013191 | 0.058259 | -0.021236 | 0.053124 | 0.097664 | 0.022888 | 0.15564 | -0.15106 | 0.44861 | -119.6686 | 0.47607 | 0.49896 | 0.63629 | 0.9201 | -121.8338 | 121.3715 | -0.65002 | 121.5454 | 121.9711 | -120.4742 | -0.31128 | 0.11444 | 0.17395 | 122.0215 | 122.1588 | 1.8539 | 121.6782 | 121.5454 | 122.4426 | 121.9986 | -0.31128 | 121.6782 | 121.5454 | 121.9986 | 1.8539 | 122.4426 | -0.95673 | -122.6395
6368.8125 | 122.4884 | -121.5317 | 0.81482 | -0.15221 | 0.011337 | -0.016823 | 0.052705 | -0.021236 | 0.054192 | 0.097664 | 0.10986 | 0.12817 | -0.11444 | 0.56763 | -119.5404 | 0.60425 | 0.32044 | 0.78278 | 0.87433 | -121.7743 | 121.4172 | -0.68664 | 121.6415 | 122.0993 | -120.3552 | -0.24262 | 0.05951 | 0.2243 | 121.8521 | 122.3145 | 1.9913 | 121.6599 | 121.6415 | 122.406 | 122.1359 | -0.24262 | 121.6599 | 121.6415 | 122.1359 | 1.9913 | 122.406 | -0.92926 | -122.5891
6370.5625 | 122.4884 | -121.5408 | 0.82398 | -0.22087 | 0.01326 | -0.011909 | 0.055696 | -0.023372 | 0.051201 | 0.097023 | 0.091553 | 0.13733 | -0.13275 | 0.52643 | -119.6136 | 0.54016 | 0.42572 | 0.70953 | 0.89722 | -121.8246 | 121.4081 | -0.68665 | 121.6324 | 122.0673 | -120.4376 | -0.28381 | 0.073242 | 0.2243 | 121.9666 | 122.2504 | 1.9272 | 121.6782 | 121.6324 | 122.4381 | 122.081 | -0.28381 | 121.6782 | 121.6324 | 122.081 | 1.9272 | 122.4381 | -0.95673 | -122.6486
6372.2656 | 122.493 | -121.5454 | 0.81024 | -0.20561 | 0.015182 | -0.02195 | 0.056123 | -0.024227 | 0.053551 | 0.097237 | 0 | 0.16022 | -0.13733 | 0.44861 | -119.6732 | 0.4715 | 0.48981 | 0.63629 | 0.93384 | -121.8292 | 121.4081 | -0.65003 | 121.5454 | 121.994 | -120.4834 | -0.28381 | 0.1236 | 0.13733 | 122.0352 | 122.1817 | 1.8723 | 121.7056 | 121.5454 | 122.4792 | 122.0169 | -0.28381 | 121.7056 | 121.5454 | 122.0169 | 1.8723 | 122.4792 | -0.94757 | -122.6395
6373.9688 | 122.6028 | -121.4996 | 0.76446 | 0.061417 | 0.014114 | -0.0149 | 0.056123 | -0.021023 | 0.053978 | 0.097023 | 0.07782 | 0.13733 | -0.10986 | 0.49439 | -119.6503 | 0.54474 | 0.33417 | 0.65918 | 0.87891 | -121.8292 | 121.3898 | -0.62714 | 121.5775 | 121.994 | -120.4147 | -0.32959 | 0.11444 | 0.18768 | 121.8338 | 122.1588 | 1.8494 | 121.637 | 121.5775 | 122.3785 | 122.0444 | -0.32959 | 121.637 | 121.5775 | 122.0444 | 1.8494 | 122.3785 | -0.87433 | -122.5937
6375.6719 | 122.5891 | -121.4859 | 0.78735 | 0.091934 | 0.01326 | -0.013191 | 0.059968 | -0.020382 | 0.052269 | 0.098305 | -0.009155 | 0.15564 | -0.16937 | 0.44403 | -119.6777 | 0.45319 | 0.45776 | 0.56763 | 0.92926 | -121.8613 | 121.3165 | -0.63171 | 121.4767 | 121.9299 | -120.4651 | -0.37537 | 0.14191 | 0.16022 | 121.9437 | 122.0535 | 1.8082 | 121.6415 | 121.4767 | 122.4152 | 121.9391 | -0.37537 | 121.6415 | 121.4767 | 121.9391 | 1.8082 | 122.4152 | -0.95673 | -122.6486
6377.375 | 122.58 | -121.5042 | 0.78735 | -0.075912 | 0.013687 | -0.019173 | 0.052919 | -0.022091 | 0.053765 | 0.098091 | 0.050354 | 0.14648 | -0.11444 | 0.51727 | -119.5633 | 0.59052 | 0.33875 | 0.73242 | 0.88806 | -121.8246 | 121.3898 | -0.64087 | 121.5546 | 122.0215 | -120.3506 | -0.32044 | 0.10071 | 0.16479 | 121.843 | 122.2366 | 1.9409 | 121.6507 | 121.5546 | 122.3923 | 122.0947 | -0.32044 | 121.6507 | 121.5546 | 122.0947 | 1.9409 | 122.3923 | -0.9018 | -122.612
6379.125 | 122.493 | -121.5408 | 0.80109 | -0.13695 | 0.0139 | -0.018959 | 0.053346 | -0.022732 | 0.054619 | 0.098091 | 0.10986 | 0.11444 | -0.1236 | 0.56305 | -119.5404 | 0.60883 | 0.31128 | 0.76446 | 0.89264 | -121.7926 | 121.4172 | -0.68664 | 121.6507 | 122.1039 | -120.3415 | -0.25177 | 0.091553 | 0.23346 | 121.8521 | 122.3053 | 2.0004 | 121.6553 | 121.6507 | 122.4335 | 122.1497 | -0.25177 | 121.6553 | 121.6507 | 122.1497 | 2.0004 | 122.4335 | -0.92468 | -122.5937
6380.8281 | 122.5983 | -121.5042 | 0.7782 | 0.061417 | 0.015182 | -0.0196 | 0.055696 | -0.021877 | 0.05291 | 0.098091 | 0.082397 | 0.13275 | -0.1236 | 0.49896 | -119.6091 | 0.55389 | 0.31586 | 0.67749 | 0.86517 | -121.788 | 121.3806 | -0.64545 | 121.5866 | 122.0032 | -120.3873 | -0.28381 | 0.086975 | 0.20599 | 121.8201 | 122.1817 | 1.8951 | 121.637 | 121.5866 | 122.3694 | 122.0581 | -0.28381 | 121.637 | 121.5866 | 122.0581 | 1.8951 | 122.3694 | -0.90179 | -122.5662
6382.5938 | 122.5754 | -121.5454 | 0.79193 | -0.053024 | 0.012191 | -0.01725 | 0.0542 | -0.022304 | 0.056542 | 0.098732 | 0.064087 | 0.14648 | -0.11902 | 0.53101 | -119.5724 | 0.55389 | 0.33417 | 0.71869 | 0.86517 | -121.8201 | 121.4264 | -0.64545 | 121.6095 | 122.0764 | -120.3644 | -0.27466 | 0.073242 | 0.18311 | 121.8796 | 122.2641 | 1.973 | 121.6919 | 121.6095 | 122.4106 | 122.0993 | -0.27466 | 121.6919 | 121.6095 | 122.0993 | 1.973 | 122.4106 | -0.91095 | -122.612
6384.3438 | 122.5479 | -121.5363 | 0.78278 | 0.099564 | 0.013473 | -0.014259 | 0.058687 | -0.022732 | 0.054192 | 0.099373 | 0.11444 | 0.11444 | -0.11444 | 0.54016 | -119.5999 | 0.58136 | 0.27924 | 0.70953 | 0.87433 | -121.8384 | 121.4218 | -0.66834 | 121.6507 | 122.0764 | -120.3827 | -0.30212 | 0.091553 | 0.22888 | 121.8155 | 122.2458 | 1.9363 | 121.6507 | 121.6507 | 122.4106 | 122.1176 | -0.30212 | 121.6507 | 121.6507 | 122.1176 | 1.9363 | 122.4106 | -0.89722 | -122.6212
6386.0469 | 122.5845 | -121.4996 | 0.76904 | 0.084305 | 0.01326 | -0.017677 | 0.0589 | -0.022091 | 0.054619 | 0.098732 | 0.022888 | 0.15564 | -0.16479 | 0.45776 | -119.6915 | 0.46692 | 0.41657 | 0.57678 | 0.91553 | -121.8109 | 121.3348 | -0.6134 | 121.5225 | 121.9574 | -120.4605 | -0.31128 | 0.14648 | 0.18768 | 121.9162 | 122.0764 | 1.8082 | 121.6553 | 121.5225 | 122.4152 | 121.9666 | -0.31128 | 121.6553 | 121.5225 | 121.9666 | 1.8082 | 122.4152 | -0.93384 | -122.58
6387.7344 | 122.5845 | -121.5363 | 0.78278 | -0.060654 | 0.01326 | -0.018745 | 0.051423 | -0.022518 | 0.052697 | 0.097023 | 0.050354 | 0.12817 | -0.12817 | 0.51727 | -119.5816 | 0.58136 | 0.32959 | 0.72327 | 0.87891 | -121.8201 | 121.4081 | -0.6546 | 121.5866 | 122.0535 | -120.3644 | -0.28381 | 0.09613 | 0.17853 | 121.8658 | 122.2595 | 1.9547 | 121.6644 | 121.5866 | 122.4152 | 122.1176 | -0.28381 | 121.6644 | 121.5866 | 122.1176 | 1.9547 | 122.4152 | -0.91095 | -122.6028
6389.4531 | 122.58 | -121.5179 | 0.76904 | 0.02327 | 0.013687 | -0.015755 | 0.061036 | -0.020382 | 0.052056 | 0.098305 | 0 | 0.17395 | -0.16022 | 0.40741 | -119.751 | 0.43945 | 0.44403 | 0.54474 | 0.90637 | -121.8704 | 121.3577 | -0.59509 | 121.5179 | 121.9254 | -120.52 | -0.35248 | 0.13733 | 0.16022 | 121.962 | 122.0627 | 1.767 | 121.6919 | 121.5179 | 122.4243 | 121.9574 | -0.35248 | 121.6919 | 121.5179 | 121.9574 | 1.767 | 122.4243 | -0.92926 | -122.6395
6391.1719 | 122.5204 | -121.5454 | 0.78735 | -0.21324 | 0.013473 | -0.014259 | 0.057832 | -0.025295 | 0.053978 | 0.0998 | -0.004578 | 0.16022 | -0.16479 | 0.43945 | -119.7052 | 0.46234 | 0.48981 | 0.59967 | 0.91095 | -121.8704 | 121.3806 | -0.62714 | 121.5408 | 121.9849 | -120.4926 | -0.32501 | 0.1236 | 0.16022 | 122.0352 | 122.1451 | 1.8402 | 121.7056 | 121.5408 | 122.4564 | 122.0078 | -0.32501 | 121.7056 | 121.5408 | 122.0078 | 1.8402 | 122.4564 | -0.95215 | -122.6578
6392.875 | 122.5983 | -121.4905 | 0.7782 | -0.0072479 | 0.015182 | -0.02195 | 0.052919 | -0.023586 | 0.053978 | 0.096169 | 0.032043 | 0.12817 | -0.11902 | 0.48065 | -119.632 | 0.52643 | 0.35248 | 0.66376 | 0.86517 | -121.8475 | 121.3715 | -0.65002 | 121.5225 | 121.9711 | -120.4102 | -0.35706 | 0.086975 | 0.15106 | 121.843 | 122.1542 | 1.8585 | 121.6187 | 121.5225 | 122.3557 | 122.0169 | -0.35706 | 121.6187 | 121.5225 | 122.0169 | 1.8585 | 122.3557 | -0.89722 | -122.6257
6394.5938 | 122.5571 | -121.5225 | 0.79651 | 0.046158 | 0.014541 | -0.017036 | 0.058687 | -0.021236 | 0.053124 | 0.09745 | 0.12817 | 0.12817 | -0.13275 | 0.52643 | -119.6045 | 0.5722 | 0.27008 | 0.68207 | 0.85602 | -121.7972 | 121.3898 | -0.66834 | 121.6507 | 122.0489 | -120.401 | -0.27466 | 0.059509 | 0.26093 | 121.7926 | 122.2046 | 1.918 | 121.6507 | 121.6507 | 122.3785 | 122.0947 | -0.27466 | 121.6507 | 121.6507 | 122.0947 | 1.918 | 122.3785 | -0.92926 | -122.5937
6396.2969 | 122.5983 | -121.5042 | 0.7782 | 0.091934 | 0.014328 | -0.016182 | 0.062745 | -0.020595 | 0.052483 | 0.099587 | -0.013733 | 0.16479 | -0.16937 | 0.42114 | -119.7235 | 0.46234 | 0.44861 | 0.55389 | 0.91095 | -121.8567 | 121.3348 | -0.6134 | 121.4905 | 121.9254 | -120.5017 | -0.35248 | 0.13275 | 0.15564 | 121.9528 | 122.0581 | 1.7807 | 121.669 | 121.4905 | 122.4152 | 121.9666 | -0.35248 | 121.669 | 121.4905 | 121.9666 | 1.7807 | 122.4152 | -0.94757 | -122.6349
6398.0156 | 122.5983 | -121.5225 | 0.78735 | 0.0080111 | 0.012191 | -0.016609 | 0.052491 | -0.021877 | 0.05526 | 0.095528 | 0.045776 | 0.12817 | -0.12817 | 0.48523 | -119.6548 | 0.53558 | 0.3479 | 0.65002 | 0.88348 | -121.8338 | 121.3943 | -0.65918 | 121.5683 | 122.0078 | -120.4422 | -0.31128 | 0.09613 | 0.17395 | 121.8704 | 122.1725 | 1.8677 | 121.6507 | 121.5683 | 122.406 | 122.0581 | -0.31128 | 121.6507 | 121.5683 | 122.0581 | 1.8677 | 122.406 | -0.91553 | -122.6212
6399.7188 | 122.5479 | -121.5271 | 0.7782 | 0.20638 | 0.013046 | -0.015327 | 0.059327 | -0.023159 | 0.053765 | 0.099373 | 0.091553 | 0.12817 | -0.1236 | 0.52185 | -119.6274 | 0.59052 | 0.25177 | 0.6958 | 0.8606 | -121.8201 | 121.4035 | -0.65002 | 121.6187 | 122.049 | -120.4056 | -0.29297 | 0.082398 | 0.21515 | 121.7789 | 122.2229 | 1.8997 | 121.6553 | 121.6187 | 122.3877 | 122.1176 | -0.29297 | 121.6553 | 121.6187 | 122.1176 | 1.8997 | 122.3877 | -0.90179 | -122.5983
6401.4375 | 122.6166 | -121.5225 | 0.77362 | 0.02327 | 0.012832 | -0.018745 | 0.051851 | -0.024013 | 0.053124 | 0.098732 | 0.041199 | 0.13275 | -0.12817 | 0.48981 | -119.6274 | 0.53558 | 0.33875 | 0.67749 | 0.87891 | -121.8521 | 121.3943 | -0.64087 | 121.5637 | 122.0123 | -120.401 | -0.32959 | 0.10528 | 0.16937 | 121.8613 | 122.2 | 1.8951 | 121.6553 | 121.5637 | 122.4014 | 122.0581 | -0.32959 | 121.6553 | 121.5637 | 122.0581 | 1.8951 | 122.4014 | -0.9018 | -122.6257
6403.1406 | 122.5708 | -121.5179 | 0.78278 | 0.069046 | 0.015396 | -0.016823 | 0.06125 | -0.022091 | 0.053551 | 0.098519 | 0.018311 | 0.1831 | -0.16937 | 0.41199 | -119.7144 | 0.44403 | 0.45319 | 0.55847 | 0.92468 | -121.8475 | 121.3486 | -0.59967 | 121.5363 | 121.9299 | -120.4971 | -0.32959 | 0.14191 | 0.18768 | 121.9711 | 122.0764 | 1.8036 | 121.701 | 121.5363 | 122.4426 | 121.962 | -0.32959 | 121.701 | 121.5363 | 121.962 | 1.8036 | 122.4426 | -0.95215 | -122.6303
6404.8438 | 122.5571 | -121.5363 | 0.79193 | 0.16823 | 0.010269 | -0.016396 | 0.057405 | -0.021023 | 0.050774 | 0.099587 | 0.091553 | 0.11444 | -0.1236 | 0.52185 | -119.5999 | 0.59509 | 0.25177 | 0.71411 | 0.86975 | -121.8063 | 121.4127 | -0.67749 | 121.6278 | 122.0581 | -120.3918 | -0.27008 | 0.07782 | 0.21515 | 121.788 | 122.2504 | 1.9363 | 121.6507 | 121.6278 | 122.406 | 122.1313 | -0.27008 | 121.6507 | 121.6278 | 122.1313 | 1.9363 | 122.406 | -0.91553 | -122.5983
6406.6094 | 122.5479 | -121.5363 | 0.80109 | 0.19875 | 0.013473 | -0.020027 | 0.057405 | -0.023586 | 0.054406 | 0.097237 | 0.11444 | 0.11902 | -0.11444 | 0.54016 | -119.6274 | 0.59052 | 0.24261 | 0.6958 | 0.85144 | -121.8658 | 121.4218 | -0.68207 | 121.6507 | 122.0764 | -120.4285 | -0.32959 | 0.050354 | 0.22888 | 121.7789 | 122.2321 | 1.9089 | 121.6553 | 121.6507 | 122.3877 | 122.1268 | -0.32959 | 121.6553 | 121.6507 | 122.1268 | 1.9089 | 122.3877 | -0.91553 | -122.6669
6408.3594 | 122.525 | -121.5591 | 0.80109 | -0.24376 | 0.015396 | -0.020882 | 0.059327 | -0.026149 | 0.053978 | 0.098305 | 0 | 0.16022 | -0.16022 | 0.42572 | -119.664 | 0.45776 | 0.5127 | 0.61798 | 0.90637 | -121.8887 | 121.3989 | -0.64087 | 121.5591 | 121.9849 | -120.4651 | -0.32959 | 0.10529 | 0.16022 | 122.0718 | 122.1771 | 1.8951 | 121.7194 | 121.5591 | 122.4655 | 122.0169 | -0.32959 | 121.7194 | 121.5591 | 122.0169 | 1.8951 | 122.4655 | -0.9613 | -122.6898
6410.0625 | 122.5662 | -121.5683 | 0.78735 | 0.069046 | 0.014541 | -0.014687 | 0.058687 | -0.018886 | 0.050347 | 0.098305 | 0.091553 | 0.11902 | -0.14648 | 0.51727 | -119.5724 | 0.59052 | 0.27008 | 0.6958 | 0.88806 | -121.8063 | 121.4218 | -0.66834 | 121.6599 | 122.0856 | -120.3598 | -0.23804 | 0.10071 | 0.23804 | 121.8384 | 122.2641 | 1.9958 | 121.6873 | 121.6599 | 122.4564 | 122.1588 | -0.23804 | 121.6873 | 121.6599 | 122.1588 | 1.9958 | 122.4564 | -0.93384 | -122.5937
6411.7656 | 122.5342 | -121.5454 | 0.79651 | 0.046158 | 0.013687 | -0.016182 | 0.059541 | -0.021236 | 0.049706 | 0.099587 | 0.022888 | 0.14648 | -0.16022 | 0.42114 | -119.6869 | 0.44403 | 0.43945 | 0.58136 | 0.92926 | -121.843 | 121.3852 | -0.65003 | 121.5683 | 121.9666 | -120.4834 | -0.29755 | 0.13275 | 0.1831 | 121.9849 | 122.1268 | 1.8585 | 121.6919 | 121.5683 | 122.4747 | 121.9894 | -0.29755 | 121.6919 | 121.5683 | 121.9894 | 1.8585 | 122.4747 | -0.95673 | -122.6395
6413.4688 | 122.5754 | -121.5179 | 0.78278 | 0.17586 | 0.013687 | -0.013405 | 0.060823 | -0.020809 | 0.05291 | 0.098519 | 0.027466 | 0.15564 | -0.15106 | 0.44861 | -119.632 | 0.50354 | 0.35706 | 0.59967 | 0.90637 | -121.8292 | 121.3669 | -0.62714 | 121.5454 | 121.9666 | -120.4147 | -0.31128 | 0.1236 | 0.17853 | 121.875 | 122.1176 | 1.886 | 121.6736 | 121.5454 | 122.4243 | 122.0215 | -0.31128 | 121.6736 | 121.5454 | 122.0215 | 1.886 | 122.4243 | -0.93384 | -122.612
6415.1719 | 122.4976 | -121.5591 | 0.8194 | -0.075912 | 0.014755 | -0.015968 | 0.061464 | -0.021236 | 0.052056 | 0.097664 | 0.068665 | 0.14648 | -0.15106 | 0.45319 | -119.6365 | 0.48523 | 0.42572 | 0.60883 | 0.90637 | -121.8567 | 121.4081 | -0.67291 | 121.6278 | 122.0123 | -120.4559 | -0.29755 | 0.086975 | 0.21973 | 121.9849 | 122.168 | 1.9226 | 121.7056 | 121.6278 | 122.4655 | 122.0444 | -0.29755 | 121.7056 | 121.6278 | 122.0444 | 1.9226 | 122.4655 | -0.97046 | -122.6761
6416.875 | 122.5204 | -121.5775 | 0.81024 | -0.24376 | 0.012832 | -0.01725 | 0.053773 | -0.022732 | 0.053765 | 0.10108 | 0.027466 | 0.14648 | -0.14648 | 0.43945 | -119.6503 | 0.49439 | 0.46692 | 0.61798 | 0.90179 | -121.875 | 121.431 | -0.66376 | 121.6049 | 122.0169 | -120.4605 | -0.29755 | 0.091552 | 0.17395 | 122.0444 | 122.1954 | 1.9272 | 121.7239 | 121.6049 | 122.4792 | 122.0718 | -0.29755 | 121.7239 | 121.6049 | 122.0718 | 1.9272 | 122.4792 | -0.95673 | -122.6852
6418.5938 | 122.6166 | -121.5225 | 0.78735 | 0.00038159 | 0.011764 | -0.014473 | 0.055482 | -0.020595 | 0.055687 | 0.099587 | 0.059509 | 0.13275 | -0.10986 | 0.4715 | -119.6411 | 0.53101 | 0.33417 | 0.65002 | 0.8606 | -121.8338 | 121.4127 | -0.6546 | 121.582 | 121.994 | -120.4285 | -0.31128 | 0.073242 | 0.16937 | 121.8567 | 122.1725 | 1.8814 | 121.6553 | 121.582 | 122.3831 | 122.0535 | -0.31128 | 121.6553 | 121.582 | 122.0535 | 1.8814 | 122.3831 | -0.89722 | -122.6212
6420.2969 | 122.6166 | -121.5179 | 0.76904 | 0.084305 | 0.014755 | -0.014259 | 0.060609 | -0.020382 | 0.054192 | 0.098091 | 0.004578 | 0.16479 | -0.16937 | 0.41657 | -119.7052 | 0.44861 | 0.41657 | 0.55389 | 0.9201 | -121.8475 | 121.3486 | -0.60425 | 121.5225 | 121.9345 | -120.4742 | -0.32959 | 0.15106 | 0.17395 | 121.9345 | 122.0718 | 1.8127 | 121.6827 | 121.5225 | 122.438 | 121.9666 | -0.32959 | 121.6827 | 121.5225 | 121.9666 | 1.8127 | 122.438 | -0.93842 | -122.6166
6422 | 122.5342 | -121.5591 | 0.80566 | -0.28191 | 0.013473 | -0.017891 | 0.055482 | -0.021877 | 0.052269 | 0.097664 | 0 | 0.14191 | -0.15564 | 0.43488 | -119.6732 | 0.46234 | 0.46234 | 0.6134 | 0.91553 | -121.8567 | 121.4035 | -0.66376 | 121.5591 | 121.994 | -120.4788 | -0.29755 | 0.10986 | 0.15564 | 122.0215 | 122.1725 | 1.886 | 121.7011 | 121.5591 | 122.4747 | 122.0215 | -0.29755 | 121.7011 | 121.5591 | 122.0215 | 1.886 | 122.4747 | -0.9613 | -122.6624
6423.7031 | 122.6212 | -121.5454 | 0.76446 | -0.014877 | 0.014328 | -0.01725 | 0.052278 | -0.023372 | 0.053978 | 0.098732 | 0.027466 | 0.10529 | -0.13733 | 0.48523 | -119.6091 | 0.53558 | 0.33875 | 0.66376 | 0.88806 | -121.8521 | 121.4081 | -0.65918 | 121.5729 | 122.0306 | -120.3735 | -0.3067 | 0.1236 | 0.16479 | 121.8842 | 122.2092 | 1.9363 | 121.6507 | 121.5729 | 122.4335 | 122.081 | -0.3067 | 121.6507 | 121.5729 | 122.081 | 1.9363 | 122.4335 | -0.90179 | -122.6166
6425.4062 | 122.493 | -121.55 | 0.82855 | -0.13695 | 0.01326 | -0.012337 | 0.063173 | -0.022945 | 0.050347 | 0.097023 | 0.059509 | 0.15106 | -0.16022 | 0.48981 | -119.5908 | 0.48065 | 0.41657 | 0.63629 | 0.90637 | -121.8521 | 121.3898 | -0.67749 | 121.6095 | 122.0398 | -120.4193 | -0.30212 | 0.07782 | 0.21973 | 121.9666 | 122.1863 | 1.9592 | 121.701 | 121.6095 | 122.4564 | 122.0306 | -0.30212 | 121.701 | 121.6095 | 122.0306 | 1.9592 | 122.4564 | -0.98877 | -122.6807
6427.1094 | 122.5388 | -121.5363 | 0.82398 | -0.24376 | 0.012619 | -0.019813 | 0.058046 | -0.022732 | 0.049706 | 0.099373 | 0.032043 | 0.15106 | -0.15564 | 0.4303 | -119.6182 | 0.4715 | 0.47607 | 0.61798 | 0.91553 | -121.8933 | 121.3806 | -0.67291 | 121.5683 | 121.9666 | -120.4422 | -0.35706 | 0.091552 | 0.18768 | 122.0123 | 122.1542 | 1.918 | 121.6873 | 121.5683 | 122.4518 | 122.0078 | -0.35706 | 121.6873 | 121.5683 | 122.0078 | 1.918 | 122.4518 | -0.97962 | -122.7173
6428.8125 | 122.5616 | -121.5271 | 0.81024 | -0.16747 | 0.014755 | -0.019813 | 0.05356 | -0.022091 | 0.055901 | 0.098732 | 0.091553 | 0.1236 | -0.1236 | 0.54016 | -119.5312 | 0.59052 | 0.3067 | 0.73242 | 0.88806 | -121.8246 | 121.4035 | -0.68665 | 121.6187 | 122.0673 | -120.3415 | -0.29755 | 0.07782 | 0.21515 | 121.8338 | 122.2595 | 1.9959 | 121.6507 | 121.6187 | 122.4152 | 122.1176 | -0.29755 | 121.6507 | 121.6187 | 122.1176 | 1.9959 | 122.4152 | -0.93384 | -122.6349
6430.5625 | 122.5433 | -121.5408 | 0.82855 | -0.25139 | 0.015609 | -0.016396 | 0.057832 | -0.022732 | 0.05291 | 0.10108 | 0.054932 | 0.14191 | -0.13733 | 0.45776 | -119.6457 | 0.48065 | 0.42572 | 0.64087 | 0.94299 | -121.8613 | 121.4035 | -0.68664 | 121.5958 | 121.9986 | -120.4742 | -0.32043 | 0.11444 | 0.19226 | 121.9666 | 122.1817 | 1.8951 | 121.6827 | 121.5958 | 122.4838 | 122.0215 | -0.32043 | 121.6827 | 121.5958 | 122.0215 | 1.8951 | 122.4838 | -0.96588 | -122.6898
6432.2656 | 122.5708 | -121.5363 | 0.79651 | 0.13008 | 0.014755 | -0.018532 | 0.058473 | -0.021023 | 0.053124 | 0.10023 | 0.1236 | 0.11444 | -0.11902 | 0.53101 | -119.5724 | 0.5722 | 0.25635 | 0.6958 | 0.87433 | -121.8384 | 121.4172 | -0.68207 | 121.6599 | 122.0673 | -120.369 | -0.30212 | 0.07782 | 0.24261 | 121.7926 | 122.2321 | 1.9638 | 121.6507 | 121.6599 | 122.4106 | 122.1085 | -0.30212 | 121.6507 | 121.6599 | 122.1085 | 1.9638 | 122.4106 | -0.91553 | -122.6349
6433.9688 | 122.5845 | -121.5134 | 0.80566 | 0.046158 | 0.014969 | -0.0149 | 0.063173 | -0.020809 | 0.051628 | 0.098305 | 0 | 0.16479 | -0.15564 | 0.41657 | -119.6732 | 0.44403 | 0.44861 | 0.54016 | 0.92926 | -121.8658 | 121.3577 | -0.64087 | 121.5134 | 121.9299 | -120.4788 | -0.35248 | 0.1236 | 0.15564 | 121.962 | 122.0535 | 1.8402 | 121.6782 | 121.5134 | 122.4426 | 121.9574 | -0.35248 | 121.6782 | 121.5134 | 121.9574 | 1.8402 | 122.4426 | -0.9613 | -122.6715
6435.6875 | 122.5388 | -121.5271 | 0.82398 | -0.28191 | 0.015609 | -0.017036 | 0.059114 | -0.021877 | 0.050774 | 0.10044 | 0.009155 | 0.16937 | -0.16022 | 0.41657 | -119.6182 | 0.46234 | 0.50354 | 0.59509 | 0.93842 | -121.8658 | 121.3669 | -0.6546 | 121.5363 | 121.9437 | -120.4422 | -0.33874 | 0.11444 | 0.16937 | 122.0306 | 122.1222 | 1.9089 | 121.6965 | 121.5363 | 122.4655 | 121.9894 | -0.33874 | 121.6965 | 121.5363 | 121.9894 | 1.9089 | 122.4655 | -0.98419 | -122.6898
6437.3906 | 122.6303 | -121.5042 | 0.78735 | 0.046158 | 0.013473 | -0.017891 | 0.054841 | -0.020595 | 0.053551 | 0.099587 | 0.054932 | 0.14191 | -0.12817 | 0.48523 | -119.577 | 0.53101 | 0.32044 | 0.65918 | 0.88806 | -121.8567 | 121.376 | -0.64545 | 121.5591 | 121.9894 | -120.3644 | -0.35248 | 0.10071 | 0.18311 | 121.8246 | 122.1634 | 1.9272 | 121.6461 | 121.5591 | 122.3923 | 122.0352 | -0.35248 | 121.6461 | 121.5591 | 122.0352 | 1.9272 | 122.3923 | -0.91553 | -122.644
6439.1406 | 122.5021 | -121.5591 | 0.81482 | -0.075912 | 0.012832 | -0.017464 | 0.062104 | -0.019314 | 0.053978 | 0.10236 | 0.07782 | 0.12817 | -0.16479 | 0.47607 | -119.6411 | 0.49896 | 0.41657 | 0.62256 | 0.9201 | -121.8613 | 121.3943 | -0.68664 | 121.637 | 122.0352 | -120.4559 | -0.30212 | 0.10529 | 0.24261 | 121.9757 | 122.1817 | 1.918 | 121.6873 | 121.637 | 122.4792 | 122.0581 | -0.30212 | 121.6873 | 121.637 | 122.0581 | 1.918 | 122.4792 | -0.97961 | -122.6761
6440.8438 | 122.5067 | -121.5775 | 0.81482 | -0.15984 | 0.011764 | -0.018745 | 0.052919 | -0.0238 | 0.054619 | 0.099587 | 0.10529 | 0.10986 | -0.12817 | 0.52643 | -119.5496 | 0.59509 | 0.32044 | 0.72327 | 0.88348 | -121.8567 | 121.4493 | -0.70496 | 121.6827 | 122.1039 | -120.3644 | -0.27923 | 0.068665 | 0.23346 | 121.8979 | 122.3007 | 2.0279 | 121.6873 | 121.6827 | 122.4609 | 122.1725 | -0.27923 | 121.6873 | 121.6827 | 122.1725 | 2.0279 | 122.4609 | -0.94299 | -122.6715
6442.5625 | 122.493 | -121.5729 | 0.82398 | -0.11406 | 0.015182 | -0.015541 | 0.061677 | -0.020809 | 0.051628 | 0.097878 | 0.059509 | 0.15564 | -0.17395 | 0.48065 | -119.6411 | 0.50354 | 0.42572 | 0.64087 | 0.91095 | -121.8658 | 121.3989 | -0.66834 | 121.6324 | 122.0535 | -120.4651 | -0.29297 | 0.086975 | 0.23346 | 121.9986 | 122.2137 | 1.9318 | 121.7285 | 121.6324 | 122.4838 | 122.0764 | -0.29297 | 121.7285 | 121.6324 | 122.0764 | 1.9318 | 122.4838 | -0.99792 | -122.6898
6444.2656 | 122.5067 | -121.5866 | 0.83771 | -0.2285 | 0.0139 | -0.016823 | 0.052705 | -0.021877 | 0.053337 | 0.10001 | 0.10529 | 0.13275 | -0.10529 | 0.53101 | -119.5587 | 0.58594 | 0.33875 | 0.737 | 0.89722 | -121.843 | 121.4813 | -0.70496 | 121.6919 | 122.1176 | -120.3964 | -0.25635 | 0.059509 | 0.21057 | 121.9254 | 122.3236 | 2.0279 | 121.7194 | 121.6919 | 122.4838 | 122.1725 | -0.25635 | 121.7194 | 121.6919 | 122.1725 | 2.0279 | 122.4838 | -0.94299 | -122.6807
6445.9844 | 122.6257 | -121.5225 | 0.79193 | 0.1606 | 0.015823 | -0.013832 | 0.062959 | -0.021023 | 0.052483 | 0.099587 | 0.013733 | 0.16937 | -0.15564 | 0.42114 | -119.7052 | 0.44861 | 0.43488 | 0.54932 | 0.9201 | -121.8796 | 121.3669 | -0.62256 | 121.5363 | 121.9437 | -120.4971 | -0.35706 | 0.12817 | 0.16937 | 121.9574 | 122.0718 | 1.8173 | 121.6919 | 121.5363 | 122.4426 | 121.9711 | -0.35706 | 121.6919 | 121.5363 | 121.9711 | 1.8173 | 122.4426 | -0.94757 | -122.6715
6447.7031 | 122.6212 | -121.4996 | 0.79651 | 0.069046 | 0.01326 | -0.016182 | 0.061891 | -0.021877 | 0.052697 | 0.10023 | -0.009155 | 0.16937 | -0.16479 | 0.40283 | -119.7006 | 0.44861 | 0.44403 | 0.55389 | 0.93842 | -121.8842 | 121.3348 | -0.62714 | 121.4905 | 121.9025 | -120.4971 | -0.38452 | 0.14191 | 0.15564 | 121.9437 | 122.0535 | 1.799 | 121.669 | 121.4905 | 122.4381 | 121.9482 | -0.38452 | 121.669 | 121.4905 | 121.9482 | 1.799 | 122.4381 | -0.9613 | -122.6807
6449.4062 | 122.58 | -121.5363 | 0.80566 | 0.12245 | 0.012832 | -0.015541 | 0.057832 | -0.021023 | 0.054192 | 0.10108 | 0.11444 | 0.13733 | -0.10986 | 0.52185 | -119.6045 | 0.59509 | 0.26093 | 0.68207 | 0.88806 | -121.8292 | 121.4264 | -0.66834 | 121.6507 | 122.0581 | -120.4102 | -0.29297 | 0.082398 | 0.2243 | 121.7972 | 122.2183 | 1.9318 | 121.6736 | 121.6507 | 122.4243 | 122.1313 | -0.29297 | 121.6736 | 121.6507 | 122.1313 | 1.9318 | 122.4243 | -0.91553 | -122.6349
6451.1094 | 122.644 | -121.4996 | 0.79651 | 0.11482 | 0.014755 | -0.014473 | 0.0589 | -0.021877 | 0.05291 | 0.10151 | 0 | 0.13733 | -0.16937 | 0.39825 | -119.7189 | 0.44403 | 0.45319 | 0.55847 | 0.91553 | -121.8613 | 121.3303 | -0.65918 | 121.4996 | 121.8979 | -120.5154 | -0.36163 | 0.11902 | 0.16937 | 121.9528 | 122.0581 | 1.7807 | 121.637 | 121.4996 | 122.4152 | 121.9437 | -0.36163 | 121.637 | 121.4996 | 121.9437 | 1.7807 | 122.4152 | -0.96588 | -122.6578
6452.8125 | 122.5388 | -121.5729 | 0.84686 | -0.26665 | 0.012405 | -0.015968 | 0.05356 | -0.022945 | 0.051842 | 0.10215 | 0.045776 | 0.13275 | -0.14648 | 0.48981 | -119.6548 | 0.51727 | 0.44403 | 0.66834 | 0.91553 | -121.875 | 121.4264 | -0.71411 | 121.6187 | 122.0627 | -120.5017 | -0.30212 | 0.068664 | 0.19226 | 122.0169 | 122.2412 | 1.918 | 121.7056 | 121.6187 | 122.4884 | 122.0901 | -0.30212 | 121.7056 | 121.6187 | 122.0901 | 1.918 | 122.4884 | -0.99335 | -122.7219
6454.5312 | 122.5571 | -121.5729 | 0.79651 | -0.22087 | 0.011551 | -0.015968 | 0.055055 | -0.024441 | 0.053765 | 0.10023 | -0.032043 | 0.15564 | -0.16479 | 0.41657 | -119.7144 | 0.44861 | 0.52643 | 0.59967 | 0.93384 | -121.8933 | 121.4081 | -0.64087 | 121.5408 | 121.9894 | -120.5109 | -0.32044 | 0.13733 | 0.13275 | 122.0993 | 122.1725 | 1.8585 | 121.7285 | 121.5408 | 122.5067 | 122.0215 | -0.32044 | 121.7285 | 121.5408 | 122.0215 | 1.8585 | 122.5067 | -0.9613 | -122.6898
6456.2812 | 122.5204 | -121.5454 | 0.83771 | -0.25902 | 0.011978 | -0.015541 | 0.054414 | -0.022732 | 0.051415 | 0.10001 | 0.068665 | 0.13275 | -0.13733 | 0.48065 | -119.6503 | 0.54474 | 0.4303 | 0.65918 | 0.91095 | -121.8613 | 121.4081 | -0.70496 | 121.6141 | 122.0261 | -120.488 | -0.31586 | 0.073242 | 0.20599 | 121.9757 | 122.2046 | 1.8951 | 121.6782 | 121.6141 | 122.4564 | 122.0901 | -0.31586 | 121.6782 | 121.6141 | 122.0901 | 1.8951 | 122.4564 | -0.97504 | -122.699
6458.0469 | 122.5113 | -121.5775 | 0.83771 | -0.14458 | 0.016037 | -0.017891 | 0.058259 | -0.0238 | 0.053551 | 0.098946 | 0.10986 | 0.11444 | -0.11902 | 0.56763 | -119.5404 | 0.60883 | 0.31586 | 0.74158 | 0.89722 | -121.843 | 121.4584 | -0.72327 | 121.6873 | 122.1451 | -120.3781 | -0.2655 | 0.059509 | 0.22888 | 121.8933 | 122.319 | 2.037 | 121.6919 | 121.6873 | 122.4747 | 122.1863 | -0.2655 | 121.6919 | 121.6873 | 122.1863 | 2.037 | 122.4747 | -0.95673 | -122.6807
6459.75 | 122.644 | -121.5134 | 0.80109 | 0.061417 | 0.0139 | -0.019386 | 0.057191 | -0.024227 | 0.054192 | 0.1013 | 0.059509 | 0.11444 | -0.11902 | 0.47607 | -119.632 | 0.53558 | 0.32044 | 0.65918 | 0.88806 | -121.843 | 121.3943 | -0.68664 | 121.5729 | 121.9894 | -120.433 | -0.32959 | 0.086976 | 0.17853 | 121.8338 | 122.1725 | 1.8814 | 121.6278 | 121.5729 | 122.4014 | 122.049 | -0.32959 | 121.6278 | 121.5729 | 122.049 | 1.8814 | 122.4014 | -0.9201 | -122.644
6461.4531 | 122.5113 | -121.5591 | 0.85144 | -0.18272 | 0.010696 | -0.016182 | 0.055696 | -0.022304 | 0.053337 | 0.10172 | 0.11444 | 0.12817 | -0.13733 | 0.55389 | -119.5724 | 0.5722 | 0.3067 | 0.74616 | 0.89264 | -121.8384 | 121.4218 | -0.72327 | 121.6736 | 122.113 | -120.4239 | -0.27924 | 0.041199 | 0.25177 | 121.8658 | 122.3053 | 1.9867 | 121.6873 | 121.6736 | 122.4518 | 122.1313 | -0.27924 | 121.6873 | 121.6736 | 122.1313 | 1.9867 | 122.4518 | -0.98877 | -122.6898
6463.1562 | 122.6669 | -121.5271 | 0.80566 | 0.030899 | 0.011978 | -0.019386 | 0.057191 | -0.022945 | 0.052697 | 0.0998 | 0.059509 | 0.12817 | -0.1236 | 0.47607 | -119.6091 | 0.53101 | 0.34332 | 0.6546 | 0.90637 | -121.8658 | 121.4035 | -0.67749 | 121.5866 | 122.0032 | -120.4147 | -0.33874 | 0.10071 | 0.1831 | 121.8704 | 122.1817 | 1.918 | 121.6553 | 121.5866 | 122.4335 | 122.0581 | -0.33874 | 121.6553 | 121.5866 | 122.0581 | 1.918 | 122.4335 | -0.92926 | -122.6715
6464.8594 | 122.5891 | -121.5363 | 0.80566 | 0.15297 | 0.014541 | -0.018104 | 0.061677 | -0.020168 | 0.053337 | 0.10023 | 0.054932 | 0.12817 | -0.15106 | 0.50354 | -119.632 | 0.54474 | 0.29755 | 0.62714 | 0.89264 | -121.8475 | 121.3852 | -0.67749 | 121.5912 | 122.0398 | -120.4376 | -0.31128 | 0.086975 | 0.20599 | 121.8338 | 122.1634 | 1.9043 | 121.6644 | 121.5912 | 122.4289 | 122.081 | -0.31128 | 121.6644 | 121.5912 | 122.081 | 1.9043 | 122.4289 | -0.95673 | -122.6532
6466.6094 | 122.5525 | -121.6095 | 0.79193 | -0.19798 | 0.012405 | -0.0196 | 0.057405 | -0.022518 | 0.054619 | 0.0998 | 0.009155 | 0.18768 | -0.16479 | 0.43945 | -119.7327 | 0.45776 | 0.48065 | 0.60883 | 0.90637 | -121.9162 | 121.4447 | -0.60425 | 121.6187 | 122.049 | -120.5246 | -0.3067 | 0.11444 | 0.17395 | 122.0901 | 122.2183 | 1.8768 | 121.7972 | 121.6187 | 122.5159 | 122.0673 | -0.3067 | 121.7972 | 121.6187 | 122.0673 | 1.8768 | 122.5159 | -0.95673 | -122.7081
6468.2969 | 122.644 | -121.5775 | 0.75531 | 0.0080111 | 0.013473 | -0.015755 | 0.052919 | -0.021877 | 0.051842 | 0.097664 | 0.041199 | 0.1236 | -0.1236 | 0.48065 | -119.7098 | 0.52643 | 0.34332 | 0.65918 | 0.85602 | -121.9162 | 121.4539 | -0.63171 | 121.6187 | 122.0581 | -120.4651 | -0.33875 | 0.10071 | 0.16479 | 121.9208 | 122.2366 | 1.8677 | 121.7011 | 121.6187 | 122.4335 | 122.1039 | -0.33875 | 121.7011 | 121.6187 | 122.1039 | 1.8677 | 122.4335 | -0.87891 | -122.6715
6470 | 122.5891 | -121.5958 | 0.75989 | 0.14534 | 0.0098416 | -0.016823 | 0.057832 | -0.022304 | 0.052056 | 0.097878 | 0.10529 | 0.1236 | -0.10071 | 0.55389 | -119.6777 | 0.58594 | 0.26093 | 0.69122 | 0.82855 | -121.907 | 121.4951 | -0.63629 | 121.7011 | 122.1497 | -120.4376 | -0.31128 | 0.068664 | 0.20599 | 121.8567 | 122.287 | 1.918 | 121.7194 | 121.7011 | 122.4243 | 122.1817 | -0.31128 | 121.7194 | 121.7011 | 122.1817 | 1.918 | 122.4243 | -0.8606 | -122.6669
6471.7188 | 122.525 | -121.6232 | 0.78278 | -0.068283 | 0.0139 | -0.012764 | 0.060182 | -0.022518 | 0.051415 | 0.097023 | 0.073242 | 0.16022 | -0.15564 | 0.48523 | -119.7327 | 0.48981 | 0.40741 | 0.61798 | 0.87433 | -121.9345 | 121.4676 | -0.62256 | 121.6965 | 122.1085 | -120.5154 | -0.31128 | 0.091553 | 0.22888 | 122.0306 | 122.2412 | 1.8906 | 121.7834 | 121.6965 | 122.4976 | 122.113 | -0.31128 | 121.7834 | 121.6965 | 122.113 | 1.8906 | 122.4976 | -0.93842 | -122.7173
6473.4219 | 122.5021 | -121.6278 | 0.78278 | -0.17509 | 0.012191 | -0.017036 | 0.053132 | -0.020809 | 0.051628 | 0.095314 | 0.09613 | 0.1236 | -0.12817 | 0.53101 | -119.6503 | 0.58136 | 0.33875 | 0.71411 | 0.84686 | -121.8796 | 121.4996 | -0.65918 | 121.7239 | 122.1588 | -120.433 | -0.25177 | 0.064087 | 0.2243 | 121.9666 | 122.3419 | 1.9775 | 121.7514 | 121.7239 | 122.4747 | 122.2092 | -0.25177 | 121.7514 | 121.7239 | 122.2092 | 1.9775 | 122.4747 | -0.91095 | -122.6624
6475.125 | 122.5891 | -121.5866 | 0.77362 | -0.060654 | 0.012832 | -0.02195 | 0.050782 | -0.021236 | 0.054406 | 0.09681 | 0.082397 | 0.12817 | -0.11902 | 0.54016 | -119.6548 | 0.5722 | 0.29755 | 0.71869 | 0.85144 | -121.8887 | 121.4676 | -0.64545 | 121.669 | 122.1268 | -120.4285 | -0.30212 | 0.077819 | 0.20142 | 121.8842 | 122.3053 | 1.9318 | 121.7148 | 121.669 | 122.438 | 122.1588 | -0.30212 | 121.7148 | 121.669 | 122.1588 | 1.9318 | 122.438 | -0.89264 | -122.6624
6476.8281 | 122.6166 | -121.5912 | 0.75989 | 0.099564 | 0.014969 | -0.014687 | 0.0542 | -0.021236 | 0.055474 | 0.096169 | 0.10986 | 0.09613 | -0.10986 | 0.50812 | -119.6869 | 0.55847 | 0.27008 | 0.67749 | 0.8606 | -121.875 | 121.4813 | -0.66376 | 121.7011 | 122.0993 | -120.4468 | -0.28381 | 0.10071 | 0.21973 | 121.8613 | 122.2687 | 1.9043 | 121.6873 | 121.7011 | 122.4518 | 122.1497 | -0.28381 | 121.6873 | 121.7011 | 122.1497 | 1.9043 | 122.4518 | -0.86975 | -122.6349
6478.5938 | 122.644 | -121.5866 | 0.74158 | -0.014877 | 0.013473 | -0.019813 | 0.054628 | -0.021663 | 0.053978 | 0.094887 | 0.041199 | 0.12817 | -0.11444 | 0.4715 | -119.7281 | 0.51727 | 0.33417 | 0.64087 | 0.84228 | -121.9208 | 121.4722 | -0.6134 | 121.6278 | 122.0581 | -120.4697 | -0.33417 | 0.10071 | 0.15564 | 121.9208 | 122.2275 | 1.8585 | 121.7148 | 121.6278 | 122.4289 | 122.1039 | -0.33417 | 121.7148 | 121.6278 | 122.1039 | 1.8585 | 122.4289 | -0.85602 | -122.6624
6480.2969 | 122.612 | -121.5546 | 0.75989 | 0.14534 | 0.013687 | -0.019813 | 0.057832 | -0.02145 | 0.052269 | 0.098091 | 0.018311 | 0.17395 | -0.16479 | 0.45776 | -119.7418 | 0.49896 | 0.32501 | 0.59052 | 0.85602 | -121.9116 | 121.3898 | -0.58594 | 121.5729 | 122.0123 | -120.5017 | -0.35706 | 0.09613 | 0.18311 | 121.8796 | 122.1451 | 1.8127 | 121.7285 | 121.5729 | 122.4106 | 122.0535 | -0.35706 | 121.7285 | 121.5729 | 122.0535 | 1.8127 | 122.4106 | -0.92468 | -122.6715
6482 | 122.5662 | -121.6095 | 0.75531 | -0.21324 | 0.011123 | -0.016823 | 0.054628 | -0.024654 | 0.053551 | 0.097023 | -0.013733 | 0.15564 | -0.18768 | 0.41199 | -119.7739 | 0.43488 | 0.49896 | 0.59052 | 0.88806 | -121.9482 | 121.4218 | -0.59967 | 121.5958 | 122.0215 | -120.5292 | -0.33874 | 0.13275 | 0.17395 | 122.1085 | 122.2 | 1.8356 | 121.7651 | 121.5958 | 122.4976 | 122.0444 | -0.33874 | 121.7651 | 121.5958 | 122.0444 | 1.8356 | 122.4976 | -0.94299 | -122.7036
6483.75 | 122.5754 | -121.6232 | 0.75989 | 0.19112 | 0.016037 | -0.014687 | 0.058687 | -0.020595 | 0.049706 | 0.09681 | 0.036621 | 0.16022 | -0.16022 | 0.41199 | -119.7968 | 0.44403 | 0.42572 | 0.55389 | 0.85602 | -121.9437 | 121.463 | -0.59967 | 121.6599 | 122.0352 | -120.5566 | -0.32043 | 0.09613 | 0.19684 | 122.049 | 122.1771 | 1.8265 | 121.7834 | 121.6599 | 122.4792 | 122.0673 | -0.32043 | 121.7834 | 121.6599 | 122.0673 | 1.8265 | 122.4792 | -0.9201 | -122.7036
6485.4531 | 122.5662 | -121.6049 | 0.75989 | -0.20561 | 0.014755 | -0.020027 | 0.056123 | -0.020809 | 0.052269 | 0.096169 | -0.004578 | 0.16479 | -0.15564 | 0.41657 | -119.7693 | 0.44861 | 0.4715 | 0.58136 | 0.86517 | -121.9391 | 121.4493 | -0.59509 | 121.6003 | 122.0215 | -120.5292 | -0.33417 | 0.10528 | 0.15106 | 122.0764 | 122.1863 | 1.8356 | 121.7697 | 121.6003 | 122.4701 | 122.0535 | -0.33417 | 121.7697 | 121.6003 | 122.0535 | 1.8356 | 122.4701 | -0.91553 | -122.699
6487.1562 | 122.5296 | -121.6507 | 0.7782 | -0.16747 | 0.011764 | -0.015327 | 0.053346 | -0.023586 | 0.052697 | 0.097664 | 0.09613 | 0.13275 | -0.1236 | 0.49439 | -119.6823 | 0.54474 | 0.36163 | 0.70953 | 0.84686 | -121.9299 | 121.5271 | -0.64545 | 121.7468 | 122.1451 | -120.4605 | -0.27924 | 0.068665 | 0.21973 | 122.0123 | 122.3602 | 1.9684 | 121.7834 | 121.7468 | 122.4976 | 122.1954 | -0.27924 | 121.7834 | 121.7468 | 122.1954 | 1.9684 | 122.4976 | -0.90179 | -122.7081
6488.8594 | 122.6395 | -121.6278 | 0.74158 | 0.11482 | 0.013473 | -0.015114 | 0.05356 | -0.020382 | 0.054833 | 0.096596 | 0.10529 | 0.1236 | -0.12817 | 0.48523 | -119.696 | 0.54016 | 0.27008 | 0.6546 | 0.82398 | -121.9254 | 121.4996 | -0.61798 | 121.7331 | 122.113 | -120.4376 | -0.29755 | 0.082398 | 0.23346 | 121.8979 | 122.2824 | 1.9318 | 121.7514 | 121.7331 | 122.4518 | 122.168 | -0.29755 | 121.7514 | 121.7331 | 122.168 | 1.9318 | 122.4518 | -0.86975 | -122.6669
6490.625 | 122.6395 | -121.5912 | 0.75073 | 0.091934 | 0.014541 | -0.015755 | 0.058259 | -0.020168 | 0.053124 | 0.09681 | 0.018311 | 0.16479 | -0.16022 | 0.41199 | -119.7739 | 0.44861 | 0.3891 | 0.54932 | 0.8606 | -121.9849 | 121.431 | -0.58594 | 121.6095 | 122.0032 | -120.5246 | -0.39368 | 0.10986 | 0.17853 | 121.9803 | 122.1405 | 1.8173 | 121.756 | 121.6095 | 122.4518 | 122.0398 | -0.39368 | 121.756 | 121.6095 | 122.0398 | 1.8173 | 122.4518 | -0.91095 | -122.7356
6492.3281 | 122.5296 | -121.6507 | 0.75531 | -0.20561 | 0.011123 | -0.013191 | 0.051637 | -0.021663 | 0.053337 | 0.094887 | 0.082397 | 0.13733 | -0.11444 | 0.50354 | -119.6686 | 0.54474 | 0.34332 | 0.6958 | 0.82855 | -121.9254 | 121.5363 | -0.61798 | 121.7331 | 122.1542 | -120.4239 | -0.27466 | 0.073242 | 0.19684 | 121.994 | 122.3465 | 1.9821 | 121.788 | 121.7331 | 122.4792 | 122.1954 | -0.27466 | 121.788 | 121.7331 | 122.1954 | 1.9821 | 122.4792 | -0.86975 | -122.6807
6494.0312 | 122.6578 | -121.6095 | 0.71869 | 0.0080111 | 0.012832 | -0.0196 | 0.051423 | -0.022732 | 0.05291 | 0.097237 | 0.032043 | 0.13733 | -0.1236 | 0.44403 | -119.6869 | 0.50354 | 0.31586 | 0.63629 | 0.84228 | -121.9528 | 121.4859 | -0.58136 | 121.6415 | 122.0535 | -120.4056 | -0.34332 | 0.1236 | 0.15564 | 121.9254 | 122.2458 | 1.9226 | 121.7468 | 121.6415 | 122.4518 | 122.113 | -0.34332 | 121.7468 | 121.6415 | 122.113 | 1.9226 | 122.4518 | -0.84229 | -122.6715
6495.7344 | 122.6303 | -121.6187 | 0.73242 | 0.11482 | 0.014969 | -0.016609 | 0.059755 | -0.02145 | 0.053551 | 0.097664 | 0 | 0.16479 | -0.16022 | 0.42114 | -119.7464 | 0.46234 | 0.3479 | 0.56305 | 0.84228 | -121.9299 | 121.4584 | -0.56763 | 121.6187 | 122.0398 | -120.4788 | -0.31128 | 0.10986 | 0.16022 | 121.9666 | 122.1817 | 1.8723 | 121.7834 | 121.6187 | 122.4609 | 122.081 | -0.31128 | 121.7834 | 121.6187 | 122.081 | 1.8723 | 122.4609 | -0.89264 | -122.6624
6497.4375 | 122.5296 | -121.6461 | 0.76446 | -0.20561 | 0.011764 | -0.016823 | 0.058687 | -0.022304 | 0.049919 | 0.097237 | 0 | 0.16937 | -0.15106 | 0.43488 | -119.7281 | 0.45776 | 0.43488 | 0.59509 | 0.86517 | -121.9345 | 121.4951 | -0.59509 | 121.6461 | 122.081 | -120.4926 | -0.28839 | 0.10071 | 0.15106 | 122.081 | 122.2412 | 1.918 | 121.8155 | 121.6461 | 122.5113 | 122.1039 | -0.28839 | 121.8155 | 121.6461 | 122.1039 | 1.918 | 122.5113 | -0.91553 | -122.699
6499.1875 | 122.5479 | -121.6324 | 0.77362 | -0.045395 | 0.014541 | -0.018745 | 0.057618 | -0.021877 | 0.051628 | 0.097023 | 0.032043 | 0.15106 | -0.16022 | 0.44403 | -119.7464 | 0.44861 | 0.41199 | 0.58136 | 0.84686 | -121.9254 | 121.4722 | -0.62256 | 121.6644 | 122.0764 | -120.52 | -0.29297 | 0.073242 | 0.19226 | 122.0444 | 122.2137 | 1.886 | 121.7834 | 121.6644 | 122.4792 | 122.081 | -0.29297 | 121.7834 | 121.6644 | 122.081 | 1.886 | 122.4792 | -0.93384 | -122.699
6500.8906 | 122.58 | -121.6553 | 0.75531 | -0.28954 | 0.01326 | -0.015755 | 0.0542 | -0.02145 | 0.052483 | 0.097878 | -0.004578 | 0.17853 | -0.16479 | 0.39368 | -119.7464 | 0.41657 | 0.48981 | 0.56305 | 0.86975 | -121.9986 | 121.4905 | -0.57678 | 121.6507 | 122.0489 | -120.5017 | -0.34332 | 0.11444 | 0.16022 | 122.1451 | 122.2183 | 1.9089 | 121.8338 | 121.6507 | 122.525 | 122.0718 | -0.34332 | 121.8338 | 121.6507 | 122.0718 | 1.9089 | 122.525 | -0.92011 | -122.7539
6502.6406 | 122.6715 | -121.6461 | 0.72327 | 0.00038159 | 0.014541 | -0.020454 | 0.048005 | -0.021663 | 0.054406 | 0.09681 | 0.027466 | 0.13275 | -0.11902 | 0.43945 | -119.6915 | 0.50354 | 0.32501 | 0.61798 | 0.83771 | -121.962 | 121.5271 | -0.59052 | 121.6736 | 122.0856 | -120.4147 | -0.31586 | 0.11444 | 0.14649 | 121.9711 | 122.2641 | 1.9547 | 121.7789 | 121.6736 | 122.4838 | 122.1497 | -0.31586 | 121.7789 | 121.6736 | 122.1497 | 1.9547 | 122.4838 | -0.84229 | -122.6852
6504.3281 | 122.6532 | -121.637 | 0.72784 | 0.030899 | 0.013473 | -0.018104 | 0.052064 | -0.022732 | 0.056969 | 0.096169 | 0.045776 | 0.12817 | -0.14191 | 0.43945 | -119.7098 | 0.51727 | 0.31586 | 0.62714 | 0.80566 | -121.994 | 121.4951 | -0.59967 | 121.6827 | 122.0764 | -120.4376 | -0.35706 | 0.07782 | 0.18768 | 121.9528 | 122.2641 | 1.9272 | 121.7651 | 121.6827 | 122.4426 | 122.1542 | -0.35706 | 121.7651 | 121.6827 | 122.1542 | 1.9272 | 122.4426 | -0.86975 | -122.7219
6506.0469 | 122.6212 | -121.6324 | 0.72327 | 0.15297 | 0.012619 | -0.015114 | 0.057618 | -0.022518 | 0.053337 | 0.098732 | 0.09613 | 0.13275 | -0.11902 | 0.49896 | -119.6732 | 0.54016 | 0.27008 | 0.65002 | 0.8194 | -121.9574 | 121.5134 | -0.59052 | 121.7285 | 122.1313 | -120.3964 | -0.32501 | 0.09613 | 0.21515 | 121.9025 | 122.2824 | 1.9592 | 121.7651 | 121.7285 | 122.4518 | 122.1725 | -0.32501 | 121.7651 | 121.7285 | 122.1725 | 1.9592 | 122.4518 | -0.84229 | -122.6807
6507.75 | 122.6349 | -121.6095 | 0.72327 | 0.16823 | 0.014969 | -0.011909 | 0.057832 | -0.024013 | 0.052697 | 0.095528 | 0.036621 | 0.14191 | -0.14648 | 0.44861 | -119.7235 | 0.50354 | 0.31586 | 0.60883 | 0.82398 | -121.9803 | 121.463 | -0.58136 | 121.6461 | 122.0581 | -120.4468 | -0.37079 | 0.10071 | 0.18311 | 121.9254 | 122.2183 | 1.886 | 121.7514 | 121.6461 | 122.4335 | 122.113 | -0.37079 | 121.7514 | 121.6461 | 122.113 | 1.886 | 122.4335 | -0.86975 | -122.7036
6509.4688 | 122.6486 | -121.6278 | 0.72784 | 0.046158 | 0.012619 | -0.016823 | 0.05655 | -0.022518 | 0.052269 | 0.094887 | -0.013733 | 0.16937 | -0.17395 | 0.37537 | -119.7693 | 0.41657 | 0.43945 | 0.5127 | 0.83771 | -121.994 | 121.4539 | -0.55847 | 121.6141 | 122.0032 | -120.4971 | -0.36621 | 0.10986 | 0.16022 | 122.0673 | 122.1405 | 1.8585 | 121.7972 | 121.6141 | 122.4655 | 122.0444 | -0.36621 | 121.7972 | 121.6141 | 122.0444 | 1.8585 | 122.4655 | -0.90179 | -122.7219
6511.1875 | 122.58 | -121.6507 | 0.75531 | -0.24376 | 0.015396 | -0.018745 | 0.053132 | -0.022732 | 0.051628 | 0.095955 | 0 | 0.14648 | -0.13275 | 0.39825 | -119.7144 | 0.43945 | 0.45776 | 0.59967 | 0.85602 | -122.0123 | 121.5179 | -0.60883 | 121.6507 | 122.0489 | -120.4697 | -0.36163 | 0.10071 | 0.13275 | 122.1085 | 122.2504 | 1.9363 | 121.7972 | 121.6507 | 122.5067 | 122.0901 | -0.36163 | 121.7972 | 121.6507 | 122.0901 | 1.9363 | 122.5067 | -0.88806 | -122.7676
6512.8906 | 122.5388 | -121.669 | 0.75989 | -0.14458 | 0.012405 | -0.01725 | 0.052064 | -0.022732 | 0.055046 | 0.094887 | 0.11902 | 0.10986 | -0.10986 | 0.5127 | -119.6136 | 0.56305 | 0.28381 | 0.72327 | 0.82855 | -121.9391 | 121.5591 | -0.65002 | 121.788 | 122.1817 | -120.3735 | -0.27008 | 0.068664 | 0.22888 | 121.9528 | 122.3923 | 2.0554 | 121.7789 | 121.788 | 122.4976 | 122.2321 | -0.27008 | 121.7789 | 121.788 | 122.2321 | 2.0554 | 122.4976 | -0.86975 | -122.699
6514.6406 | 122.5296 | -121.6782 | 0.75989 | -0.075912 | 0.01326 | -0.015541 | 0.059327 | -0.019954 | 0.052269 | 0.096596 | 0.07782 | 0.15106 | -0.14191 | 0.45319 | -119.7098 | 0.4715 | 0.3891 | 0.58594 | 0.86975 | -121.9437 | 121.5363 | -0.60883 | 121.756 | 122.1313 | -120.4697 | -0.2655 | 0.10986 | 0.21973 | 122.0673 | 122.2641 | 1.9684 | 121.8292 | 121.756 | 122.5479 | 122.1497 | -0.2655 | 121.8292 | 121.756 | 122.1497 | 1.9684 | 122.5479 | -0.9018 | -122.7036
6516.3438 | 122.6395 | -121.6278 | 0.71869 | 0.038529 | 0.013046 | -0.021309 | 0.059755 | -0.018245 | 0.051628 | 0.097023 | -0.009155 | 0.16479 | -0.16937 | 0.37537 | -119.751 | 0.42572 | 0.40741 | 0.53101 | 0.85602 | -121.9482 | 121.4584 | -0.55389 | 121.6187 | 122.0032 | -120.4697 | -0.32043 | 0.13733 | 0.16022 | 122.0352 | 122.1588 | 1.8768 | 121.7926 | 121.6187 | 122.4838 | 122.0535 | -0.32043 | 121.7926 | 121.6187 | 122.0535 | 1.8768 | 122.4838 | -0.88806 | -122.6669
6518.0469 | 122.5388 | -121.6644 | 0.78735 | -0.15221 | 0.015182 | -0.015327 | 0.056123 | -0.020168 | 0.05056 | 0.095528 | 0.045776 | 0.15106 | -0.16479 | 0.45776 | -119.6457 | 0.46692 | 0.39825 | 0.60883 | 0.85602 | -121.9345 | 121.4996 | -0.63629 | 121.7102 | 122.1222 | -120.433 | -0.27008 | 0.068664 | 0.21057 | 122.0627 | 122.2733 | 2.0187 | 121.8155 | 121.7102 | 122.5204 | 122.1313 | -0.27008 | 121.8155 | 121.7102 | 122.1313 | 2.0187 | 122.5204 | -0.95215 | -122.7219
6519.7656 | 122.6212 | -121.6415 | 0.72784 | 0.12245 | 0.015609 | -0.0149 | 0.050782 | -0.019314 | 0.054619 | 0.097878 | 0.11444 | 0.11902 | -0.11444 | 0.48065 | -119.5862 | 0.56305 | 0.23804 | 0.67291 | 0.79651 | -121.9666 | 121.5271 | -0.60883 | 121.756 | 122.1222 | -120.314 | -0.32501 | 0.068665 | 0.22888 | 121.8796 | 122.3145 | 2.0554 | 121.7606 | 121.756 | 122.4381 | 122.2046 | -0.32501 | 121.7606 | 121.756 | 122.2046 | 2.0554 | 122.4381 | -0.84229 | -122.6944
6521.4688 | 122.5891 | -121.6827 | 0.74158 | -0.28954 | 0.013687 | -0.018745 | 0.052705 | -0.022518 | 0.052697 | 0.096596 | -0.027466 | 0.15106 | -0.18768 | 0.37537 | -119.7006 | 0.42114 | 0.48523 | 0.56763 | 0.86517 | -121.994 | 121.4951 | -0.59052 | 121.6553 | 122.0581 | -120.4422 | -0.31128 | 0.1236 | 0.16022 | 122.168 | 122.2504 | 1.9821 | 121.8338 | 121.6553 | 122.5479 | 122.1039 | -0.31128 | 121.8338 | 121.6553 | 122.1039 | 1.9821 | 122.5479 | -0.92926 | -122.7356
6523.1719 | 122.5388 | -121.6827 | 0.75989 | -0.15984 | 0.015182 | -0.018959 | 0.049287 | -0.020595 | 0.053551 | 0.093819 | 0.10071 | 0.12817 | -0.11902 | 0.49439 | -119.5633 | 0.55389 | 0.28381 | 0.71411 | 0.82398 | -121.9666 | 121.5637 | -0.63171 | 121.7834 | 122.1771 | -120.3232 | -0.28381 | 0.064087 | 0.21973 | 121.9666 | 122.3969 | 2.1194 | 121.8109 | 121.7834 | 122.5067 | 122.2366 | -0.28381 | 121.8109 | 121.7834 | 122.2366 | 2.1194 | 122.5067 | -0.87891 | -122.7264
6524.9062 | 122.5754 | -121.6965 | 0.75531 | -0.23613 | 0.016464 | -0.015968 | 0.054414 | -0.022091 | 0.053978 | 0.094887 | 0.027466 | 0.16479 | -0.14191 | 0.39368 | -119.6823 | 0.4303 | 0.43488 | 0.5722 | 0.86975 | -122.0215 | 121.5546 | -0.59052 | 121.7239 | 122.0901 | -120.4376 | -0.32501 | 0.11444 | 0.16937 | 122.1313 | 122.2687 | 2.0142 | 121.8613 | 121.7239 | 122.5662 | 122.1268 | -0.32501 | 121.8613 | 121.7239 | 122.1268 | 2.0142 | 122.5662 | -0.89722 | -122.7768
6526.6094 | 122.5616 | -121.6827 | 0.75531 | -0.25139 | 0.015823 | -0.018959 | 0.053773 | -0.022732 | 0.053765 | 0.095528 | 0.059509 | 0.1236 | -0.14191 | 0.41199 | -119.6686 | 0.44403 | 0.41657 | 0.59509 | 0.83313 | -121.9666 | 121.5408 | -0.63171 | 121.7422 | 122.0947 | -120.4239 | -0.28381 | 0.07782 | 0.20142 | 122.0993 | 122.2778 | 2.0142 | 121.8063 | 121.7422 | 122.5159 | 122.1268 | -0.28381 | 121.8063 | 121.7422 | 122.1268 | 2.0142 | 122.5159 | -0.89722 | -122.7219
6528.3281 | 122.6395 | -121.6278 | 0.71869 | 0.19112 | 0.015182 | -0.011909 | 0.058046 | -0.020168 | 0.051415 | 0.098519 | 0.027466 | 0.14191 | -0.14648 | 0.4303 | -119.6594 | 0.48523 | 0.29297 | 0.58594 | 0.82855 | -121.9849 | 121.4813 | -0.57678 | 121.6553 | 122.0581 | -120.3781 | -0.35706 | 0.10986 | 0.17395 | 121.9208 | 122.2137 | 1.9684 | 121.7697 | 121.6553 | 122.4564 | 122.113 | -0.35706 | 121.7697 | 121.6553 | 122.113 | 1.9684 | 122.4564 | -0.86517 | -122.7036
6530.0781 | 122.5342 | -121.6461 | 0.74616 | -0.098801 | 0.014328 | -0.013191 | 0.057191 | -0.020595 | 0.052697 | 0.096169 | 0.064087 | 0.14191 | -0.16479 | 0.45776 | -119.6594 | 0.4715 | 0.37537 | 0.60883 | 0.84686 | -121.9894 | 121.4813 | -0.60425 | 121.7102 | 122.1039 | -120.4056 | -0.34332 | 0.10071 | 0.22888 | 122.0215 | 122.2549 | 1.9867 | 121.788 | 121.7102 | 122.493 | 122.1176 | -0.34332 | 121.788 | 121.7102 | 122.1176 | 1.9867 | 122.493 | -0.91095 | -122.7356
6531.7812 | 122.5662 | -121.7056 | 0.75073 | -0.14458 | 0.012619 | -0.016823 | 0.050569 | -0.019314 | 0.051628 | 0.096382 | 0.11444 | 0.13275 | -0.11902 | 0.50354 | -119.5633 | 0.55847 | 0.28839 | 0.70496 | 0.81024 | -121.9757 | 121.5866 | -0.61798 | 121.8201 | 122.2092 | -120.314 | -0.27008 | 0.05951 | 0.23346 | 121.994 | 122.4106 | 2.1423 | 121.8384 | 121.8201 | 122.5159 | 122.2641 | -0.27008 | 121.8384 | 121.8201 | 122.2641 | 2.1423 | 122.5159 | -0.86975 | -122.7264
6533.5469 | 122.6532 | -121.6507 | 0.70038 | 0.084305 | 0.015396 | -0.017036 | 0.056764 | -0.02145 | 0.050133 | 0.096382 | 0.027466 | 0.16022 | -0.15564 | 0.39825 | -119.7006 | 0.43945 | 0.34332 | 0.54016 | 0.84686 | -121.9803 | 121.4951 | -0.54016 | 121.6782 | 122.0489 | -120.401 | -0.32959 | 0.14649 | 0.18311 | 121.994 | 122.1909 | 1.9501 | 121.8109 | 121.6782 | 122.4976 | 122.0901 | -0.32959 | 121.8109 | 121.6782 | 122.0901 | 1.9501 | 122.4976 | -0.85602 | -122.6807
6535.2969 | 122.6761 | -121.6278 | 0.70953 | 0.046158 | 0.013687 | -0.013405 | 0.050355 | -0.021877 | 0.055474 | 0.097237 | 0.059509 | 0.11444 | -0.14191 | 0.4303 | -119.6411 | 0.5127 | 0.29297 | 0.61798 | 0.80109 | -122.0261 | 121.4859 | -0.59509 | 121.6873 | 122.0581 | -120.3506 | -0.39825 | 0.091552 | 0.20142 | 121.9208 | 122.2458 | 1.9867 | 121.7422 | 121.6873 | 122.4289 | 122.1405 | -0.39825 | 121.7422 | 121.6873 | 122.1405 | 1.9867 | 122.4289 | -0.85144 | -122.7356
6537.0312 | 122.6669 | -121.6507 | 0.69122 | 0.13008 | 0.014328 | -0.018532 | 0.060182 | -0.021023 | 0.053551 | 0.097664 | -0.004578 | 0.16022 | -0.16022 | 0.37537 | -119.696 | 0.42114 | 0.3891 | 0.51727 | 0.83313 | -121.9849 | 121.4905 | -0.53101 | 121.6461 | 122.0261 | -120.3873 | -0.33417 | 0.14191 | 0.15564 | 122.0398 | 122.168 | 1.9547 | 121.8109 | 121.6461 | 122.4838 | 122.0718 | -0.33417 | 121.8109 | 121.6461 | 122.0718 | 1.9547 | 122.4838 | -0.85144 | -122.6761
6538.7344 | 122.5845 | -121.6919 | 0.75531 | -0.17509 | 0.014541 | -0.020454 | 0.055696 | -0.022091 | 0.052056 | 0.09745 | -0.004578 | 0.16022 | -0.16022 | 0.40283 | -119.6045 | 0.41657 | 0.45319 | 0.56763 | 0.85602 | -122.0123 | 121.5317 | -0.59509 | 121.6873 | 122.0947 | -120.3598 | -0.32043 | 0.10071 | 0.15564 | 122.1451 | 122.2595 | 2.0874 | 121.8521 | 121.6873 | 122.5479 | 122.1085 | -0.32043 | 121.8521 | 121.6873 | 122.1085 | 2.0874 | 122.5479 | -0.91553 | -122.7676
6540.4688 | 122.6578 | -121.6507 | 0.72784 | -0.037765 | 0.012191 | -0.021095 | 0.049287 | -0.024868 | 0.054406 | 0.098732 | 0.050354 | 0.14191 | -0.11902 | 0.44403 | -119.3344 | 0.50812 | 0.29297 | 0.65002 | 0.82398 | -121.962 | 121.5317 | -0.58594 | 121.701 | 122.0947 | -120.0623 | -0.31128 | 0.096131 | 0.16937 | 121.9437 | 122.3007 | 2.3163 | 121.7926 | 121.701 | 122.4747 | 122.1588 | -0.31128 | 121.7926 | 121.701 | 122.1588 | 2.3163 | 122.4747 | -0.84686 | -122.6898
6542.1719 | 122.7081 | -121.6415 | 0.73242 | 0.01564 | 0.011978 | -0.018532 | 0.05121 | -0.024868 | 0.053551 | 0.096382 | 0.054932 | 0.11902 | -0.1236 | 0.43945 | -119.3619 | 0.49439 | 0.3067 | 0.6134 | 0.82398 | -121.9849 | 121.5179 | -0.6134 | 121.6965 | 122.081 | -120.0943 | -0.34332 | 0.091553 | 0.17853 | 121.9482 | 122.2549 | 2.2797 | 121.7606 | 121.6965 | 122.4655 | 122.1359 | -0.34332 | 121.7606 | 121.6965 | 122.1359 | 2.2797 | 122.4655 | -0.85602 | -122.7173
6543.875 | 122.6715 | -121.6507 | 0.70038 | 0.053787 | 0.0139 | -0.0091325 | 0.060823 | -0.023159 | 0.05291 | 0.097878 | 0.004578 | 0.15564 | -0.16022 | 0.37079 | -119.4626 | 0.40741 | 0.39825 | 0.50812 | 0.85602 | -122.0123 | 121.4905 | -0.54474 | 121.6553 | 122.0215 | -120.163 | -0.36163 | 0.15564 | 0.16479 | 122.0489 | 122.1588 | 2.1881 | 121.8063 | 121.6553 | 122.5067 | 122.0581 | -0.36163 | 121.8063 | 121.6553 | 122.0581 | 2.1881 | 122.5067 | -0.86059 | -122.7127
6545.5781 | 122.5525 | -121.7102 | 0.74158 | -0.19035 | 0.014114 | -0.0149 | 0.051637 | -0.021877 | 0.051842 | 0.097023 | 0.082397 | 0.11444 | -0.11902 | 0.49439 | -119.3024 | 0.5127 | 0.29297 | 0.69122 | 0.7782 | -121.9803 | 121.5912 | -0.62714 | 121.7926 | 122.2046 | -120.0439 | -0.27008 | 0.036621 | 0.20142 | 122.0032 | 122.4014 | 2.4078 | 121.8246 | 121.7926 | 122.4884 | 122.2229 | -0.27008 | 121.8246 | 121.7926 | 122.2229 | 2.4078 | 122.4884 | -0.8606 | -122.7219
6547.2812 | 122.5616 | -121.6965 | 0.72784 | -0.037765 | 0.017532 | -0.018959 | 0.05655 | -0.021663 | 0.052483 | 0.09681 | 0.041199 | 0.15106 | -0.15106 | 0.39825 | -119.4214 | 0.44403 | 0.37079 | 0.54016 | 0.81482 | -122.0261 | 121.5454 | -0.57678 | 121.7377 | 122.0947 | -120.1492 | -0.32959 | 0.086975 | 0.19226 | 122.0673 | 122.2366 | 2.2751 | 121.8475 | 121.7377 | 122.5113 | 122.1405 | -0.32959 | 121.8475 | 121.7377 | 122.1405 | 2.2751 | 122.5113 | -0.87891 | -122.7539
6548.9844 | 122.58 | -121.701 | 0.72327 | -0.16747 | 0.0139 | -0.018532 | 0.054628 | -0.022304 | 0.05291 | 0.098091 | 0 | 0.16937 | -0.15564 | 0.40283 | -119.371 | 0.43488 | 0.43945 | 0.57678 | 0.82855 | -122.0215 | 121.5454 | -0.55389 | 121.701 | 122.1039 | -120.0943 | -0.32043 | 0.10528 | 0.15564 | 122.1405 | 122.2778 | 2.33 | 121.8704 | 121.701 | 122.5296 | 122.1359 | -0.32043 | 121.8704 | 121.701 | 122.1359 | 2.33 | 122.5296 | -0.87891 | -122.7448
6550.7188 | 122.6669 | -121.6507 | 0.70953 | 0.099564 | 0.014969 | -0.0089189 | 0.054628 | -0.021877 | 0.054192 | 0.097664 | -0.004578 | 0.15564 | -0.15106 | 0.35706 | -119.4168 | 0.43488 | 0.36163 | 0.51727 | 0.82398 | -122.0169 | 121.4996 | -0.55389 | 121.6461 | 122.0078 | -120.1263 | -0.36621 | 0.11444 | 0.14648 | 122.0123 | 122.168 | 2.2339 | 121.8063 | 121.6461 | 122.4747 | 122.0856 | -0.36621 | 121.8063 | 121.6461 | 122.0856 | 2.2339 | 122.4747 | -0.8606 | -122.7264
6552.4062 | 122.5937 | -121.6873 | 0.70496 | -0.2285 | 0.015396 | -0.016823 | 0.053987 | -0.0238 | 0.055046 | 0.096382 | 0.013733 | 0.15106 | -0.14191 | 0.37537 | -119.3939 | 0.42114 | 0.42114 | 0.56763 | 0.8194 | -122.0535 | 121.5454 | -0.55389 | 121.701 | 122.0627 | -120.0989 | -0.36621 | 0.11444 | 0.15564 | 122.1085 | 122.2549 | 2.2934 | 121.8384 | 121.701 | 122.5067 | 122.1085 | -0.36621 | 121.8384 | 121.701 | 122.1085 | 2.2934 | 122.5067 | -0.84686 | -122.7585
6554.1094 | 122.5662 | -121.7239 | 0.72327 | -0.20561 | 0.013687 | -0.020668 | 0.049714 | -0.020809 | 0.055901 | 0.095528 | 0.10986 | 0.1236 | -0.11444 | 0.48065 | -119.3115 | 0.54474 | 0.27008 | 0.70038 | 0.80109 | -122.0078 | 121.6095 | -0.59967 | 121.8338 | 122.2046 | -120.0348 | -0.28381 | 0.077819 | 0.2243 | 121.994 | 122.4243 | 2.4124 | 121.8475 | 121.8338 | 122.525 | 122.2687 | -0.28381 | 121.8475 | 121.8338 | 122.2687 | 2.4124 | 122.525 | -0.83771 | -122.731
6555.8125 | 122.6212 | -121.6782 | 0.71869 | 0.038529 | 0.014755 | -0.015755 | 0.055269 | -0.020382 | 0.055474 | 0.094246 | 0.10529 | 0.14191 | -0.11902 | 0.47607 | -119.3756 | 0.52643 | 0.20599 | 0.63629 | 0.7782 | -122.0352 | 121.5591 | -0.57678 | 121.7834 | 122.1542 | -120.0943 | -0.35706 | 0.059509 | 0.22431 | 121.8842 | 122.3145 | 2.3026 | 121.8201 | 121.7834 | 122.4564 | 122.2046 | -0.35706 | 121.8201 | 121.7834 | 122.2046 | 2.3026 | 122.4564 | -0.83771 | -122.7539
6557.5156 | 122.6852 | -121.6644 | 0.71869 | 0.13771 | 0.013687 | -0.016182 | 0.057405 | -0.020168 | 0.053124 | 0.095528 | -0.022888 | 0.17853 | -0.16479 | 0.36621 | -119.5084 | 0.39825 | 0.39368 | 0.49439 | 0.82398 | -122.0215 | 121.4996 | -0.54016 | 121.6415 | 122.0306 | -120.2271 | -0.35706 | 0.10529 | 0.14191 | 122.0581 | 122.1588 | 2.1561 | 121.843 | 121.6415 | 122.4884 | 122.0627 | -0.35706 | 121.843 | 121.6415 | 122.0627 | 2.1561 | 122.4884 | -0.88348 | -122.7402
6559.2344 | 122.6807 | -121.669 | 0.68665 | 0.10719 | 0.011764 | -0.014687 | 0.056764 | -0.021663 | 0.052483 | 0.096169 | 0 | 0.15564 | -0.16479 | 0.35706 | -119.5312 | 0.41657 | 0.3891 | 0.49896 | 0.82398 | -122.0306 | 121.5042 | -0.53101 | 121.669 | 122.0261 | -120.2179 | -0.36163 | 0.13733 | 0.16479 | 122.0581 | 122.168 | 2.1378 | 121.8246 | 121.669 | 122.493 | 122.0856 | -0.36163 | 121.8246 | 121.669 | 122.0856 | 2.1378 | 122.493 | -0.85144 | -122.7173
6560.9375 | 122.6578 | -121.6873 | 0.71869 | -0.083542 | 0.011551 | -0.019813 | 0.047364 | -0.024227 | 0.05291 | 0.096382 | 0.036621 | 0.12817 | -0.11902 | 0.45776 | -119.4077 | 0.52185 | 0.27466 | 0.66834 | 0.79651 | -121.9803 | 121.5683 | -0.59052 | 121.7239 | 122.1451 | -120.1263 | -0.29297 | 0.07782 | 0.15564 | 121.962 | 122.3557 | 2.2797 | 121.8155 | 121.7239 | 122.4838 | 122.2092 | -0.29297 | 121.8155 | 121.7239 | 122.2092 | 2.2797 | 122.4838 | -0.83771 | -122.699
6562.6406 | 122.6852 | -121.637 | 0.70496 | -0.0072479 | 0.01326 | -0.017891 | 0.050782 | -0.022732 | 0.05291 | 0.094673 | 0.050354 | 0.14648 | -0.11902 | 0.41657 | -119.5038 | 0.46692 | 0.29297 | 0.60883 | 0.80109 | -122.0032 | 121.5179 | -0.55847 | 121.6873 | 122.0535 | -120.2087 | -0.36621 | 0.09613 | 0.16937 | 121.9299 | 122.2458 | 2.1332 | 121.7834 | 121.6873 | 122.438 | 122.1039 | -0.36621 | 121.7834 | 121.6873 | 122.1039 | 2.1332 | 122.438 | -0.82398 | -122.7081
6564.3281 | 122.6761 | -121.6736 | 0.70038 | 0.11482 | 0.015396 | -0.015755 | 0.058046 | -0.022304 | 0.051628 | 0.096382 | 0 | 0.17853 | -0.16937 | 0.37537 | -119.4809 | 0.40283 | 0.37994 | 0.52185 | 0.82398 | -122.0581 | 121.5042 | -0.52185 | 121.6736 | 122.049 | -120.1813 | -0.38452 | 0.1236 | 0.16937 | 122.0535 | 122.1954 | 2.1927 | 121.8521 | 121.6736 | 122.4976 | 122.0764 | -0.38452 | 121.8521 | 121.6736 | 122.0764 | 2.1927 | 122.4976 | -0.86975 | -122.7585
6566.0938 | 122.6669 | -121.6782 | 0.70038 | 0.084305 | 0.013687 | -0.014259 | 0.052064 | -0.024227 | 0.053765 | 0.094673 | 0.091553 | 0.13275 | -0.12817 | 0.45319 | -119.4809 | 0.50354 | 0.23804 | 0.62256 | 0.79651 | -122.0169 | 121.55 | -0.56763 | 121.7697 | 122.1313 | -120.1813 | -0.33875 | 0.096131 | 0.21973 | 121.9162 | 122.3007 | 2.1973 | 121.8109 | 121.7697 | 122.4747 | 122.1817 | -0.33875 | 121.8109 | 121.7697 | 122.1817 | 2.1973 | 122.4747 | -0.82855 | -122.7173
6567.7969 | 122.6807 | -121.6736 | 0.70496 | 0.091934 | 0.0139 | -0.017036 | 0.057618 | -0.0238 | 0.054406 | 0.095955 | 0 | 0.16937 | -0.16479 | 0.36621 | -119.5724 | 0.42114 | 0.37079 | 0.50354 | 0.81024 | -122.0123 | 121.5088 | -0.53558 | 121.6736 | 122.0398 | -120.2774 | -0.33874 | 0.10529 | 0.16479 | 122.0444 | 122.1771 | 2.1011 | 121.843 | 121.6736 | 122.4838 | 122.0947 | -0.33874 | 121.843 | 121.6736 | 122.0947 | 2.1011 | 122.4838 | -0.86975 | -122.7173
6569.5156 | 122.6761 | -121.6782 | 0.68207 | 0.061417 | 0.014755 | -0.012978 | 0.052491 | -0.021877 | 0.054192 | 0.095101 | 0.073242 | 0.13733 | -0.10071 | 0.42572 | -119.4763 | 0.47607 | 0.27008 | 0.59967 | 0.7782 | -122.0078 | 121.5775 | -0.54474 | 121.7514 | 122.1039 | -120.1584 | -0.32959 | 0.09613 | 0.17395 | 121.9482 | 122.2778 | 2.2018 | 121.8155 | 121.7514 | 122.4564 | 122.1542 | -0.32959 | 121.8155 | 121.7514 | 122.1542 | 2.2018 | 122.4564 | -0.78278 | -122.6898
6571.2188 | 122.6486 | -121.6873 | 0.70953 | 0.053787 | 0.014328 | -0.011482 | 0.056978 | -0.02145 | 0.050988 | 0.095528 | 0.013733 | 0.13733 | -0.17395 | 0.36163 | -119.5633 | 0.38452 | 0.40741 | 0.49896 | 0.81024 | -122.0306 | 121.5134 | -0.5722 | 121.701 | 122.0489 | -120.2728 | -0.34332 | 0.10071 | 0.18768 | 122.0947 | 122.1863 | 2.124 | 121.8246 | 121.701 | 122.4976 | 122.0718 | -0.34332 | 121.8246 | 121.701 | 122.0718 | 2.124 | 122.4976 | -0.88348 | -122.7402
6572.9375 | 122.6944 | -121.6553 | 0.70496 | 0.00038159 | 0.013046 | -0.016609 | 0.050142 | -0.0238 | 0.055474 | 0.09681 | 0.027466 | 0.14191 | -0.13275 | 0.42572 | -119.4534 | 0.47607 | 0.27466 | 0.60425 | 0.7782 | -122.0306 | 121.5225 | -0.56305 | 121.6827 | 122.081 | -120.1584 | -0.37537 | 0.073242 | 0.16022 | 121.9299 | 122.2595 | 2.2018 | 121.7972 | 121.6827 | 122.4335 | 122.1313 | -0.37537 | 121.7972 | 121.6827 | 122.1313 | 2.2018 | 122.4335 | -0.83771 | -122.7356
6574.6719 | 122.5525 | -121.7102 | 0.73242 | -0.091171 | 0.013473 | -0.018532 | 0.058259 | -0.0238 | 0.052483 | 0.096382 | 0.07782 | 0.15564 | -0.16937 | 0.42114 | -119.4809 | 0.43945 | 0.36621 | 0.57678 | 0.81482 | -122.0444 | 121.5408 | -0.57678 | 121.788 | 122.1313 | -120.2133 | -0.33417 | 0.082397 | 0.24719 | 122.0764 | 122.287 | 2.2293 | 121.8658 | 121.788 | 122.525 | 122.1497 | -0.33417 | 121.8658 | 121.788 | 122.1497 | 2.2293 | 122.525 | -0.9018 | -122.7768
6576.375 | 122.5891 | -121.7194 | 0.72784 | -0.17509 | 0.015609 | -0.020668 | 0.054414 | -0.023586 | 0.052056 | 0.094887 | -0.004578 | 0.1831 | -0.16937 | 0.38452 | -119.5312 | 0.37994 | 0.4303 | 0.54016 | 0.82855 | -122.0215 | 121.55 | -0.54474 | 121.7148 | 122.1039 | -120.2591 | -0.30212 | 0.10071 | 0.16479 | 122.1497 | 122.2595 | 2.1881 | 121.9025 | 121.7148 | 122.5479 | 122.0993 | -0.30212 | 121.9025 | 121.7148 | 122.0993 | 2.1881 | 122.5479 | -0.89722 | -122.7493
6578.0781 | 122.5571 | -121.7606 | 0.73242 | -0.20561 | 0.0139 | -0.019173 | 0.049501 | -0.023586 | 0.051628 | 0.096382 | 0.11444 | 0.13275 | -0.10529 | 0.46692 | -119.4443 | 0.52185 | 0.26093 | 0.67291 | 0.79193 | -122.0352 | 121.6553 | -0.59967 | 121.875 | 122.2275 | -120.1767 | -0.27466 | 0.059509 | 0.21973 | 122.0215 | 122.4335 | 2.3163 | 121.8933 | 121.875 | 122.5525 | 122.2824 | -0.27466 | 121.8933 | 121.875 | 122.2824 | 2.3163 | 122.5525 | -0.83771 | -122.7676
6579.7812 | 122.6303 | -121.7102 | 0.68665 | 0.12245 | 0.015609 | -0.019173 | 0.053132 | -0.021877 | 0.055474 | 0.095955 | 0.11444 | 0.1236 | -0.11902 | 0.4715 | -119.4717 | 0.51727 | 0.20599 | 0.62714 | 0.75989 | -122.0032 | 121.5912 | -0.56305 | 121.8246 | 122.1817 | -120.1584 | -0.29297 | 0.073242 | 0.23346 | 121.9162 | 122.3373 | 2.2385 | 121.8338 | 121.8246 | 122.4701 | 122.2275 | -0.29297 | 121.8338 | 121.8246 | 122.2275 | 2.2385 | 122.4701 | -0.80566 | -122.6898
6581.4844 | 122.5845 | -121.7194 | 0.72784 | -0.037765 | 0.012832 | -0.017036 | 0.058259 | -0.021663 | 0.050133 | 0.096382 | 0.050354 | 0.16022 | -0.16022 | 0.3891 | -119.5404 | 0.41199 | 0.36621 | 0.53101 | 0.81482 | -122.0215 | 121.5591 | -0.56763 | 121.7697 | 122.1085 | -120.2682 | -0.30212 | 0.086975 | 0.21057 | 122.0856 | 122.2504 | 2.179 | 121.8796 | 121.7697 | 122.5342 | 122.1313 | -0.30212 | 121.8796 | 121.7697 | 122.1313 | 2.179 | 122.5342 | -0.88806 | -122.7493
6583.1875 | 122.6715 | -121.6644 | 0.69122 | 0.091934 | 0.016464 | -0.018104 | 0.057405 | -0.020382 | 0.051842 | 0.096382 | -0.004578 | 0.14648 | -0.17395 | 0.34332 | -119.5496 | 0.37537 | 0.37079 | 0.48523 | 0.82398 | -122.0581 | 121.4905 | -0.54474 | 121.6599 | 122.0078 | -120.2408 | -0.39368 | 0.13275 | 0.16937 | 122.0352 | 122.1497 | 2.1149 | 121.8109 | 121.6599 | 122.4884 | 122.0398 | -0.39368 | 121.8109 | 121.6599 | 122.0398 | 2.1149 | 122.4884 | -0.86517 | -122.7493
6584.8906 | 122.5525 | -121.7422 | 0.72327 | -0.091171 | 0.011337 | -0.013191 | 0.055055 | -0.022732 | 0.051415 | 0.09446 | 0.054932 | 0.15106 | -0.13733 | 0.41199 | -119.4443 | 0.44861 | 0.36163 | 0.56763 | 0.80566 | -122.0398 | 121.6049 | -0.5722 | 121.7972 | 122.1542 | -120.1675 | -0.29755 | 0.082397 | 0.19226 | 122.1039 | 122.3099 | 2.298 | 121.8933 | 121.7972 | 122.5479 | 122.1909 | -0.29755 | 121.8933 | 121.7972 | 122.1909 | 2.298 | 122.5479 | -0.8606 | -122.7631
6586.625 | 122.6028 | -121.7056 | 0.73242 | -0.21324 | 0.012832 | -0.019813 | 0.051423 | -0.021877 | 0.052483 | 0.095314 | -0.013733 | 0.15106 | -0.15564 | 0.34332 | -119.4534 | 0.39368 | 0.44403 | 0.53558 | 0.80566 | -122.0673 | 121.55 | -0.58136 | 121.6919 | 122.049 | -120.1859 | -0.36163 | 0.073242 | 0.14191 | 122.1497 | 122.2412 | 2.2522 | 121.8567 | 121.6919 | 122.5113 | 122.0993 | -0.36163 | 121.8567 | 121.6919 | 122.0993 | 2.2522 | 122.5113 | -0.88806 | -122.7997
6588.3281 | 122.7036 | -121.701 | 0.66834 | 0.0080111 | 0.014328 | -0.015114 | 0.049928 | -0.024227 | 0.055046 | 0.096169 | 0.064087 | 0.13275 | -0.1236 | 0.39825 | -119.3939 | 0.47607 | 0.2655 | 0.59052 | 0.79193 | -122.0123 | 121.5775 | -0.53558 | 121.7651 | 122.0993 | -120.0623 | -0.31128 | 0.1236 | 0.18768 | 121.9666 | 122.2916 | 2.3071 | 121.8338 | 121.7651 | 122.493 | 122.1771 | -0.31128 | 121.8338 | 121.7651 | 122.1771 | 2.3071 | 122.493 | -0.79193 | -122.6807
6590.0312 | 122.6532 | -121.6782 | 0.69122 | 0.19875 | 0.014969 | -0.012978 | 0.054841 | -0.020382 | 0.051628 | 0.094673 | 0.045776 | 0.14191 | -0.16022 | 0.41199 | -119.3527 | 0.45776 | 0.2655 | 0.55847 | 0.80109 | -122.0169 | 121.5179 | -0.54932 | 121.7239 | 122.0901 | -120.0439 | -0.33875 | 0.10986 | 0.20599 | 121.9437 | 122.2366 | 2.3254 | 121.8201 | 121.7239 | 122.4792 | 122.1359 | -0.33875 | 121.8201 | 121.7239 | 122.1359 | 2.3254 | 122.4792 | -0.85144 | -122.7081
6591.7344 | 122.6898 | -121.6782 | 0.6958 | 0.13771 | 0.01326 | -0.016396 | 0.056764 | -0.021236 | 0.051415 | 0.097023 | -0.004578 | 0.16937 | -0.14191 | 0.3479 | -119.4534 | 0.37079 | 0.37994 | 0.49439 | 0.81482 | -122.0352 | 121.5363 | -0.52643 | 121.6736 | 122.0261 | -120.1492 | -0.35706 | 0.11902 | 0.13733 | 122.0581 | 122.1725 | 2.2247 | 121.8475 | 121.6736 | 122.493 | 122.049 | -0.35706 | 121.8475 | 121.6736 | 122.049 | 2.2247 | 122.493 | -0.83771 | -122.731
6593.4531 | 122.6715 | -121.6965 | 0.70038 | -0.014877 | 0.013473 | -0.019173 | 0.046296 | -0.023159 | 0.056755 | 0.09681 | 0.045776 | 0.14648 | -0.11902 | 0.41657 | -119.3893 | 0.48523 | 0.2655 | 0.6134 | 0.78735 | -122.0444 | 121.5775 | -0.55389 | 121.7422 | 122.113 | -120.0897 | -0.3479 | 0.086976 | 0.16479 | 121.962 | 122.3099 | 2.3071 | 121.843 | 121.7422 | 122.4838 | 122.1817 | -0.3479 | 121.843 | 121.7422 | 122.1817 | 2.3071 | 122.4838 | -0.8194 | -122.7448
6595.1562 | 122.6852 | -121.701 | 0.68665 | 0.11482 | 0.013473 | -0.018104 | 0.052278 | -0.024441 | 0.053551 | 0.095741 | 0.086975 | 0.10529 | -0.11902 | 0.44403 | -119.3939 | 0.48523 | 0.24261 | 0.60883 | 0.77362 | -121.9986 | 121.582 | -0.58136 | 121.788 | 122.1451 | -120.0806 | -0.29755 | 0.086975 | 0.20599 | 121.9437 | 122.3099 | 2.3071 | 121.8063 | 121.788 | 122.4747 | 122.1863 | -0.29755 | 121.8063 | 121.788 | 122.1863 | 2.3071 | 122.4747 | -0.80566 | -122.6852
6596.8594 | 122.6898 | -121.6827 | 0.6958 | 0.12245 | 0.011337 | -0.011696 | 0.059114 | -0.021877 | 0.050988 | 0.096382 | 0.009155 | 0.15564 | -0.16937 | 0.34332 | -119.4489 | 0.3891 | 0.36621 | 0.48981 | 0.82855 | -122.0581 | 121.5134 | -0.54016 | 121.6919 | 122.0261 | -120.1447 | -0.37537 | 0.13275 | 0.17853 | 122.049 | 122.1725 | 2.2339 | 121.8384 | 121.6919 | 122.5113 | 122.0718 | -0.37537 | 121.8384 | 121.6919 | 122.0718 | 2.2339 | 122.5113 | -0.86517 | -122.7539
6598.6094 | 122.5845 | -121.7377 | 0.73242 | -0.13695 | 0.01326 | -0.017036 | 0.050142 | -0.024654 | 0.053978 | 0.095528 | 0.10986 | 0.11444 | -0.10986 | 0.4715 | -119.2978 | 0.54016 | 0.22888 | 0.68207 | 0.7782 | -122.0215 | 121.6278 | -0.61798 | 121.8475 | 122.2092 | -120.0302 | -0.28381 | 0.045776 | 0.21973 | 121.9666 | 122.4197 | 2.4399 | 121.8521 | 121.8475 | 122.5159 | 122.2778 | -0.28381 | 121.8521 | 121.8475 | 122.2778 | 2.4399 | 122.5159 | -0.84229 | -122.7539
6600.3125 | 122.7036 | -121.6919 | 0.67291 | 0.084305 | 0.012405 | -0.017036 | 0.057405 | -0.022945 | 0.050988 | 0.097023 | -0.018311 | 0.17395 | -0.16479 | 0.3479 | -119.4809 | 0.37994 | 0.37994 | 0.48981 | 0.8194 | -122.0581 | 121.5271 | -0.49896 | 121.6736 | 122.0398 | -120.1538 | -0.36621 | 0.14648 | 0.14648 | 122.0718 | 122.1817 | 2.211 | 121.8658 | 121.6736 | 122.5113 | 122.0718 | -0.36621 | 121.8658 | 121.6736 | 122.0718 | 2.211 | 122.5113 | -0.83771 | -122.731
6602.0156 | 122.6898 | -121.6553 | 0.67291 | 0.12245 | 0.014328 | -0.017036 | 0.058046 | -0.022091 | 0.053337 | 0.09745 | -0.004578 | 0.14648 | -0.16937 | 0.35248 | -119.4397 | 0.3891 | 0.35706 | 0.50354 | 0.81482 | -122.0444 | 121.4859 | -0.52643 | 121.6507 | 122.0078 | -120.1126 | -0.3891 | 0.14191 | 0.16479 | 122.0123 | 122.1588 | 2.2156 | 121.8018 | 121.6507 | 122.4701 | 122.0444 | -0.3891 | 121.8018 | 121.6507 | 122.0444 | 2.2156 | 122.4701 | -0.84229 | -122.7173
6603.7188 | 122.5937 | -121.7422 | 0.72327 | -0.030136 | 0.01625 | -0.015541 | 0.057832 | -0.018245 | 0.053337 | 0.094033 | 0.059509 | 0.16022 | -0.15564 | 0.37994 | -119.4122 | 0.40741 | 0.35706 | 0.53101 | 0.81482 | -122.049 | 121.5866 | -0.56305 | 121.8018 | 122.1222 | -120.1355 | -0.3067 | 0.091552 | 0.21515 | 122.0993 | 122.2733 | 2.33 | 121.9025 | 121.8018 | 122.5571 | 122.1497 | -0.3067 | 121.9025 | 121.8018 | 122.1497 | 2.33 | 122.5571 | -0.87891 | -122.7722
6605.4062 | 122.6532 | -121.6873 | 0.69122 | 0.076676 | 0.012619 | -0.01725 | 0.055909 | -0.019741 | 0.051628 | 0.09446 | 0.009155 | 0.16022 | -0.16022 | 0.33875 | -119.4397 | 0.37079 | 0.38452 | 0.4715 | 0.8194 | -122.049 | 121.5271 | -0.53101 | 121.6965 | 122.0261 | -120.1309 | -0.36163 | 0.12817 | 0.16937 | 122.0718 | 122.1588 | 2.2476 | 121.8475 | 121.6965 | 122.5067 | 122.0581 | -0.36163 | 121.8475 | 121.6965 | 122.0581 | 2.2476 | 122.5067 | -0.85144 | -122.7402
6607.1406 | 122.6166 | -121.7377 | 0.71869 | -0.26665 | 0.010696 | -0.018318 | 0.050782 | -0.021236 | 0.052269 | 0.097023 | -0.032043 | 0.16022 | -0.17395 | 0.3479 | -119.3939 | 0.38452 | 0.46234 | 0.52643 | 0.83313 | -122.0444 | 121.5637 | -0.55847 | 121.7056 | 122.0856 | -120.1126 | -0.3067 | 0.11444 | 0.14191 | 122.2 | 122.2641 | 2.3438 | 121.8979 | 121.7056 | 122.5708 | 122.1222 | -0.3067 | 121.8979 | 121.7056 | 122.1222 | 2.3438 | 122.5708 | -0.89264 | -122.7631
6608.8438 | 122.5662 | -121.7377 | 0.73242 | -0.17509 | 0.012619 | -0.020027 | 0.05121 | -0.023586 | 0.051628 | 0.095955 | 0.10986 | 0.1236 | -0.09613 | 0.43945 | -119.2932 | 0.49896 | 0.28381 | 0.64545 | 0.78278 | -122.0169 | 121.6415 | -0.60883 | 121.8475 | 122.1771 | -120.0256 | -0.27924 | 0.050354 | 0.20599 | 122.0215 | 122.3831 | 2.4445 | 121.8613 | 121.8475 | 122.5204 | 122.2366 | -0.27924 | 121.8613 | 121.8475 | 122.2366 | 2.4445 | 122.5204 | -0.82855 | -122.7493
6610.6094 | 122.5983 | -121.7239 | 0.70496 | -0.014877 | 0.012832 | -0.015755 | 0.058046 | -0.019954 | 0.051628 | 0.096596 | 0.041199 | 0.14648 | -0.16022 | 0.36163 | -119.4122 | 0.40283 | 0.36163 | 0.50354 | 0.83771 | -122.0261 | 121.5637 | -0.55847 | 121.7651 | 122.0856 | -120.1172 | -0.30212 | 0.13275 | 0.20142 | 122.0856 | 122.2275 | 2.3117 | 121.8704 | 121.7651 | 122.5616 | 122.1268 | -0.30212 | 121.8704 | 121.7651 | 122.1268 | 2.3117 | 122.5616 | -0.86517 | -122.731
6612.3281 | 122.6898 | -121.6873 | 0.69122 | 0.02327 | 0.014114 | -0.014046 | 0.057191 | -0.018886 | 0.049919 | 0.096596 | 0 | 0.17853 | -0.16479 | 0.35248 | -119.4397 | 0.37537 | 0.37079 | 0.47607 | 0.8194 | -122.0123 | 121.5225 | -0.5127 | 121.6873 | 122.0398 | -120.1309 | -0.32501 | 0.12817 | 0.16479 | 122.0581 | 122.1634 | 2.2476 | 121.8658 | 121.6873 | 122.5067 | 122.0627 | -0.32501 | 121.8658 | 121.6873 | 122.0627 | 2.2476 | 122.5067 | -0.85602 | -122.7036
6614.0781 | 122.5937 | -121.7422 | 0.72327 | -0.27428 | 0.013473 | -0.018745 | 0.048433 | -0.019954 | 0.051628 | 0.098732 | 0.050354 | 0.14191 | -0.1236 | 0.39368 | -119.3436 | 0.43945 | 0.37079 | 0.58136 | 0.81024 | -122.0581 | 121.6187 | -0.58136 | 121.7926 | 122.1359 | -120.0668 | -0.31586 | 0.086975 | 0.17395 | 122.113 | 122.3236 | 2.3987 | 121.8842 | 121.7926 | 122.5525 | 122.1817 | -0.31586 | 121.8842 | 121.7926 | 122.1817 | 2.3987 | 122.5525 | -0.84686 | -122.7814
6615.7812 | 122.6944 | -121.6919 | 0.70038 | -0.0072479 | 0.012832 | -0.014259 | 0.049714 | -0.022091 | 0.05526 | 0.097237 | 0.054932 | 0.14648 | -0.1236 | 0.3891 | -119.3207 | 0.46234 | 0.29755 | 0.59052 | 0.81024 | -122.0352 | 121.5683 | -0.55389 | 121.7468 | 122.081 | -120.0211 | -0.34332 | 0.10986 | 0.17853 | 121.9894 | 122.2824 | 2.3712 | 121.8384 | 121.7468 | 122.5021 | 122.1542 | -0.34332 | 121.8384 | 121.7468 | 122.1542 | 2.3712 | 122.5021 | -0.82397 | -122.7356
6617.5156 | 122.6624 | -121.7148 | 0.70496 | 0.091934 | 0.014328 | -0.015968 | 0.05356 | -0.020382 | 0.053978 | 0.095528 | 0.10071 | 0.12817 | -0.10986 | 0.44403 | -119.3115 | 0.49896 | 0.20142 | 0.61798 | 0.79193 | -122.0123 | 121.6049 | -0.57678 | 121.8155 | 122.1588 | -120.0165 | -0.29755 | 0.086975 | 0.21057 | 121.9162 | 122.3328 | 2.4033 | 121.843 | 121.8155 | 122.5067 | 122.2137 | -0.29755 | 121.843 | 121.8155 | 122.2137 | 2.4033 | 122.5067 | -0.81482 | -122.7173
6619.2188 | 122.6349 | -121.7239 | 0.72784 | 0.01564 | 0.015609 | -0.013405 | 0.058687 | -0.021877 | 0.052697 | 0.096169 | 0.022888 | 0.15106 | -0.16022 | 0.35248 | -119.4031 | 0.37994 | 0.36163 | 0.49439 | 0.80109 | -122.0444 | 121.5637 | -0.57678 | 121.7468 | 122.0764 | -120.1309 | -0.32043 | 0.073242 | 0.1831 | 122.0856 | 122.2183 | 2.3209 | 121.875 | 121.7468 | 122.525 | 122.1039 | -0.32043 | 121.875 | 121.7468 | 122.1039 | 2.3209 | 122.525 | -0.88806 | -122.7722
6620.9219 | 122.5983 | -121.7422 | 0.73242 | -0.17509 | 0.016891 | -0.016396 | 0.052278 | -0.022518 | 0.05056 | 0.097237 | -0.004578 | 0.16022 | -0.16479 | 0.36163 | -119.3665 | 0.39368 | 0.41199 | 0.54932 | 0.82398 | -122.0856 | 121.5775 | -0.57221 | 121.7377 | 122.1039 | -120.0989 | -0.34332 | 0.091553 | 0.16022 | 122.1542 | 122.2916 | 2.3758 | 121.9025 | 121.7377 | 122.5662 | 122.1359 | -0.34332 | 121.9025 | 121.7377 | 122.1359 | 2.3758 | 122.5662 | -0.89722 | -122.818
6622.6562 | 122.6166 | -121.7102 | 0.73242 | -0.25139 | 0.014755 | -0.018745 | 0.052705 | -0.021236 | 0.052697 | 0.095955 | -0.013733 | 0.16479 | -0.17853 | 0.34332 | -119.3848 | 0.37994 | 0.42572 | 0.5127 | 0.83771 | -122.0627 | 121.5317 | -0.56763 | 121.6965 | 122.0535 | -120.1172 | -0.35248 | 0.10529 | 0.16479 | 122.1359 | 122.2229 | 2.3254 | 121.875 | 121.6965 | 122.5479 | 122.0901 | -0.35248 | 121.875 | 121.6965 | 122.0901 | 2.3254 | 122.5479 | -0.91095 | -122.7951
6624.3594 | 122.5845 | -121.7468 | 0.73242 | -0.19798 | 0.013687 | -0.0196 | 0.050782 | -0.022304 | 0.054619 | 0.095101 | 0.09613 | 0.11902 | -0.1236 | 0.44403 | -119.2795 | 0.49896 | 0.26093 | 0.64545 | 0.80109 | -122.0352 | 121.6232 | -0.6134 | 121.843 | 122.1909 | -120.0119 | -0.28839 | 0.068664 | 0.21973 | 122.0078 | 122.3923 | 2.4673 | 121.8658 | 121.843 | 122.5479 | 122.2458 | -0.28839 | 121.8658 | 121.843 | 122.2458 | 2.4673 | 122.5479 | -0.85602 | -122.7676
6626.0625 | 122.6852 | -121.7056 | 0.70496 | 0.099564 | 0.013046 | -0.013832 | 0.052064 | -0.022091 | 0.053765 | 0.094246 | 0.10986 | 0.10986 | -0.1236 | 0.4303 | -119.3161 | 0.47607 | 0.2243 | 0.6134 | 0.79651 | -122.0398 | 121.582 | -0.59509 | 121.8155 | 122.1359 | -120.0211 | -0.33417 | 0.091553 | 0.23346 | 121.9299 | 122.319 | 2.3895 | 121.8155 | 121.8155 | 122.5021 | 122.1817 | -0.33417 | 121.8155 | 121.8155 | 122.1817 | 2.3895 | 122.5021 | -0.82855 | -122.7448
6627.7812 | 122.699 | -121.6919 | 0.69122 | 0.084305 | 0.015609 | -0.013832 | 0.0589 | -0.022091 | 0.052483 | 0.098091 | 0 | 0.15564 | -0.16479 | 0.32959 | -119.3939 | 0.37537 | 0.37079 | 0.48981 | 0.82855 | -122.0718 | 121.5271 | -0.53558 | 121.6919 | 122.0215 | -120.0851 | -0.37994 | 0.13733 | 0.16479 | 122.0627 | 122.1817 | 2.298 | 121.8475 | 121.6919 | 122.5204 | 122.0673 | -0.37994 | 121.8475 | 121.6919 | 122.0673 | 2.298 | 122.5204 | -0.85602 | -122.7631
6629.5469 | 122.5937 | -121.7239 | 0.72784 | -0.060654 | 0.015182 | -0.012764 | 0.056764 | -0.021023 | 0.049706 | 0.094033 | 0.050354 | 0.14648 | -0.15564 | 0.39825 | -119.3802 | 0.41657 | 0.35706 | 0.55389 | 0.82398 | -122.0306 | 121.5683 | -0.58136 | 121.7743 | 122.1222 | -120.108 | -0.3067 | 0.096131 | 0.20599 | 122.081 | 122.2778 | 2.3438 | 121.8704 | 121.7743 | 122.5479 | 122.1405 | -0.3067 | 121.8704 | 121.7743 | 122.1405 | 2.3438 | 122.5479 | -0.88348 | -122.7585
6631.2656 | 122.699 | -121.6782 | 0.70953 | -0.014877 | 0.01326 | -0.021309 | 0.048005 | -0.025081 | 0.053337 | 0.096382 | 0.022888 | 0.16479 | -0.10529 | 0.3891 | -119.3115 | 0.47607 | 0.26093 | 0.59052 | 0.81482 | -122.0535 | 121.5729 | -0.54474 | 121.701 | 122.0673 | -120.0211 | -0.37537 | 0.10528 | 0.12817 | 121.9391 | 122.2687 | 2.3666 | 121.843 | 121.701 | 122.493 | 122.1542 | -0.37537 | 121.843 | 121.701 | 122.1542 | 2.3666 | 122.493 | -0.81482 | -122.7631
6633.0312 | 122.5891 | -121.7285 | 0.72327 | -0.083542 | 0.012619 | -0.01725 | 0.059541 | -0.022518 | 0.050133 | 0.094887 | 0.059509 | 0.14648 | -0.16022 | 0.3891 | -119.3573 | 0.40741 | 0.35706 | 0.54016 | 0.82398 | -122.0352 | 121.5683 | -0.57678 | 121.788 | 122.1176 | -120.0806 | -0.3067 | 0.10071 | 0.21973 | 122.0856 | 122.2687 | 2.3712 | 121.875 | 121.788 | 122.5525 | 122.1359 | -0.3067 | 121.875 | 121.788 | 122.1359 | 2.3712 | 122.5525 | -0.88348 | -122.7585
6634.7344 | 122.5845 | -121.7468 | 0.72784 | -0.20561 | 0.011551 | -0.02195 | 0.055055 | -0.021663 | 0.051415 | 0.093392 | 0.009155 | 0.16022 | -0.16479 | 0.37537 | -119.3756 | 0.41199 | 0.39825 | 0.54016 | 0.83771 | -122.0856 | 121.582 | -0.56763 | 121.756 | 122.1222 | -120.1035 | -0.33875 | 0.10986 | 0.17395 | 122.1451 | 122.287 | 2.3712 | 121.907 | 121.756 | 122.5845 | 122.1588 | -0.33875 | 121.907 | 121.756 | 122.1588 | 2.3712 | 122.5845 | -0.89264 | -122.8134
6636.4531 | 122.5891 | -121.7285 | 0.73242 | -0.13695 | 0.0139 | -0.017464 | 0.046296 | -0.022945 | 0.055046 | 0.09745 | 0.10986 | 0.1236 | -0.13275 | 0.46692 | -119.2612 | 0.52643 | 0.21515 | 0.67749 | 0.78278 | -122.0123 | 121.5958 | -0.60883 | 121.8384 | 122.1954 | -119.9936 | -0.28381 | 0.050354 | 0.24261 | 121.9437 | 122.406 | 2.4673 | 121.8521 | 121.8384 | 122.5113 | 122.2549 | -0.28381 | 121.8521 | 121.8384 | 122.2549 | 2.4673 | 122.5113 | -0.86517 | -122.7448
6638.1562 | 122.7173 | -121.6919 | 0.70038 | -0.045395 | 0.013687 | -0.019813 | 0.048005 | -0.020809 | 0.054833 | 0.097664 | 0.064087 | 0.13275 | -0.1236 | 0.43488 | -119.3115 | 0.48523 | 0.2655 | 0.62256 | 0.79193 | -122.049 | 121.5683 | -0.56763 | 121.756 | 122.1268 | -120.0119 | -0.35706 | 0.091553 | 0.18768 | 121.9574 | 122.3145 | 2.3804 | 121.8246 | 121.756 | 122.4838 | 122.1771 | -0.35706 | 121.8246 | 121.756 | 122.1771 | 2.3804 | 122.4838 | -0.82397 | -122.7493
6639.8594 | 122.731 | -121.7102 | 0.68665 | -0.0072479 | 0.0139 | -0.022163 | 0.051423 | -0.0238 | 0.053124 | 0.095955 | 0.045776 | 0.14191 | -0.1236 | 0.40283 | -119.339 | 0.45776 | 0.27008 | 0.58594 | 0.79193 | -122.0535 | 121.5866 | -0.54474 | 121.756 | 122.113 | -120.0256 | -0.34332 | 0.10529 | 0.16937 | 121.9803 | 122.2961 | 2.3712 | 121.8521 | 121.756 | 122.5021 | 122.168 | -0.34332 | 121.8521 | 121.756 | 122.168 | 2.3712 | 122.5021 | -0.81024 | -122.7402
6641.6094 | 122.5845 | -121.7239 | 0.74158 | -0.18272 | 0.012619 | -0.020241 | 0.053987 | -0.025722 | 0.054192 | 0.095314 | 0.1236 | 0.1236 | -0.11902 | 0.48981 | -119.2657 | 0.5127 | 0.23804 | 0.66834 | 0.77362 | -122.0398 | 121.6049 | -0.61798 | 121.8475 | 122.2137 | -120.0073 | -0.31586 | 0.032044 | 0.24261 | 121.962 | 122.3923 | 2.4582 | 121.8475 | 121.8475 | 122.4976 | 122.2366 | -0.31586 | 121.8475 | 121.8475 | 122.2366 | 2.4582 | 122.4976 | -0.8606 | -122.7814
6643.3125 | 122.6944 | -121.7102 | 0.69122 | 0.11482 | 0.012191 | -0.018104 | 0.05356 | -0.022732 | 0.054406 | 0.098946 | 0.10529 | 0.12817 | -0.11902 | 0.42114 | -119.3207 | 0.4715 | 0.2243 | 0.59967 | 0.81024 | -122.049 | 121.5912 | -0.56305 | 121.8155 | 122.1313 | -120.0119 | -0.33875 | 0.11902 | 0.22431 | 121.9345 | 122.3099 | 2.3895 | 121.8384 | 121.8155 | 122.5204 | 122.1817 | -0.33875 | 121.8384 | 121.8155 | 122.1817 | 2.3895 | 122.5204 | -0.81024 | -122.7402
6645.0938 | 122.58 | -121.7468 | 0.74616 | -0.19798 | 0.014755 | -0.023445 | 0.05356 | -0.024013 | 0.053765 | 0.095955 | 0.10529 | 0.09613 | -0.1236 | 0.48523 | -119.2703 | 0.52643 | 0.24261 | 0.67291 | 0.78735 | -122.049 | 121.6232 | -0.65003 | 121.8521 | 122.2321 | -120.0165 | -0.30212 | 0.041199 | 0.22888 | 121.9894 | 122.4197 | 2.4765 | 121.843 | 121.8521 | 122.5342 | 122.2733 | -0.30212 | 121.843 | 121.8521 | 122.2733 | 2.4765 | 122.5342 | -0.86975 | -122.7951
6646.7969 | 122.6715 | -121.7194 | 0.68207 | 0.14534 | 0.01091 | -0.017036 | 0.053773 | -0.019741 | 0.054619 | 0.094887 | 0.1236 | 0.1236 | -0.10986 | 0.4715 | -119.2932 | 0.50812 | 0.18768 | 0.62256 | 0.79193 | -122.0078 | 121.6095 | -0.55847 | 121.843 | 122.1909 | -119.9753 | -0.28839 | 0.10986 | 0.23346 | 121.907 | 122.3419 | 2.4261 | 121.843 | 121.843 | 122.5113 | 122.2275 | -0.28839 | 121.843 | 121.843 | 122.2275 | 2.4261 | 122.5113 | -0.79193 | -122.6898
6648.5156 | 122.6303 | -121.7285 | 0.72784 | -0.24376 | 0.014541 | -0.019173 | 0.056123 | -0.022732 | 0.053551 | 0.096596 | -0.004578 | 0.16022 | -0.16479 | 0.36621 | -119.3436 | 0.37079 | 0.43945 | 0.52643 | 0.83313 | -122.0581 | 121.5637 | -0.56763 | 121.7239 | 122.0947 | -120.0714 | -0.32959 | 0.10529 | 0.16022 | 122.168 | 122.2549 | 2.3849 | 121.8887 | 121.7239 | 122.5616 | 122.0993 | -0.32959 | 121.8887 | 121.7239 | 122.0993 | 2.3849 | 122.5616 | -0.89264 | -122.7859
6650.2188 | 122.7036 | -121.7239 | 0.70496 | -0.014877 | 0.010055 | -0.017677 | 0.052278 | -0.021236 | 0.054192 | 0.095741 | 0.045776 | 0.14191 | -0.11444 | 0.41657 | -119.3161 | 0.43945 | 0.2655 | 0.60425 | 0.80109 | -122.0078 | 121.6095 | -0.56305 | 121.7697 | 122.1405 | -120.0211 | -0.28381 | 0.09613 | 0.16022 | 121.9894 | 122.3282 | 2.4078 | 121.8658 | 121.7697 | 122.525 | 122.1634 | -0.28381 | 121.8658 | 121.7697 | 122.1634 | 2.4078 | 122.525 | -0.8194 | -122.7127
6651.9375 | 122.7219 | -121.701 | 0.66834 | 0.13008 | 0.0139 | -0.018959 | 0.058687 | -0.021236 | 0.051842 | 0.095955 | 0.013733 | 0.16479 | -0.17395 | 0.35248 | -119.4077 | 0.36621 | 0.35248 | 0.48523 | 0.83313 | -122.0215 | 121.5271 | -0.50354 | 121.7148 | 122.0535 | -120.076 | -0.32043 | 0.1648 | 0.18768 | 122.0535 | 122.1863 | 2.2934 | 121.8658 | 121.7148 | 122.5342 | 122.0673 | -0.32043 | 121.8658 | 121.7148 | 122.0673 | 2.2934 | 122.5342 | -0.84228 | -122.6898
6653.7031 | 122.7173 | -121.7331 | 0.68207 | 0.10719 | 0.010482 | -0.013618 | 0.050569 | -0.02145 | 0.051842 | 0.097023 | 0.068665 | 0.10529 | -0.1236 | 0.41657 | -119.3344 | 0.4715 | 0.23346 | 0.58136 | 0.7782 | -122.0444 | 121.6095 | -0.57678 | 121.8018 | 122.1497 | -120.0165 | -0.31128 | 0.09613 | 0.19226 | 121.9666 | 122.3145 | 2.3987 | 121.8384 | 121.8018 | 122.5113 | 122.2046 | -0.31128 | 121.8384 | 121.8018 | 122.2046 | 2.3987 | 122.5113 | -0.80566 | -122.7264
6655.4062 | 122.6852 | -121.7102 | 0.70038 | 0.11482 | 0.014114 | -0.018959 | 0.052491 | -0.024013 | 0.05526 | 0.094887 | 0.10529 | 0.1236 | -0.10986 | 0.4303 | -119.3161 | 0.48523 | 0.21515 | 0.59509 | 0.77362 | -122.0215 | 121.6003 | -0.57678 | 121.8155 | 122.1405 | -120.0165 | -0.31128 | 0.073243 | 0.21515 | 121.9254 | 122.3053 | 2.3941 | 121.8338 | 121.8155 | 122.4838 | 122.1954 | -0.31128 | 121.8338 | 121.8155 | 122.1954 | 2.3941 | 122.4838 | -0.81024 | -122.7219
6657.1094 | 122.6898 | -121.7285 | 0.70953 | 0.099564 | 0.010269 | -0.01725 | 0.051851 | -0.024441 | 0.054833 | 0.096596 | 0.073242 | 0.10986 | -0.11444 | 0.44861 | -119.2978 | 0.48981 | 0.21515 | 0.60425 | 0.77362 | -122.0444 | 121.6141 | -0.59967 | 121.8018 | 122.1771 | -120.0073 | -0.31586 | 0.064087 | 0.18768 | 121.9437 | 122.3328 | 2.4307 | 121.8384 | 121.8018 | 122.5021 | 122.2183 | -0.31586 | 121.8384 | 121.8018 | 122.2183 | 2.4307 | 122.5021 | -0.82398 | -122.7539
6658.8125 | 122.6212 | -121.7422 | 0.71411 | -0.23613 | 0.01326 | -0.015541 | 0.054628 | -0.025081 | 0.054619 | 0.095314 | -0.009155 | 0.17395 | -0.1831 | 0.35706 | -119.3893 | 0.36621 | 0.44403 | 0.52185 | 0.83313 | -122.0947 | 121.5591 | -0.54016 | 121.7331 | 122.0993 | -120.1035 | -0.35248 | 0.11902 | 0.17395 | 122.1863 | 122.2641 | 2.3529 | 121.9162 | 121.7331 | 122.5754 | 122.1085 | -0.35248 | 121.9162 | 121.7331 | 122.1085 | 2.3529 | 122.5754 | -0.89722 | -122.8088
6660.5625 | 122.5891 | -121.7468 | 0.70496 | -0.075912 | 0.014328 | -0.018104 | 0.056764 | -0.0191 | 0.049279 | 0.095314 | 0.068665 | 0.15106 | -0.15106 | 0.40283 | -119.3527 | 0.40741 | 0.35248 | 0.54016 | 0.80566 | -122.049 | 121.5958 | -0.55389 | 121.8155 | 122.1497 | -120.0577 | -0.30212 | 0.10071 | 0.21973 | 122.0993 | 122.287 | 2.3941 | 121.8979 | 121.8155 | 122.5525 | 122.1542 | -0.30212 | 121.8979 | 121.8155 | 122.1542 | 2.3941 | 122.5525 | -0.85602 | -122.7539
6662.2656 | 122.699 | -121.7102 | 0.66834 | 0.084305 | 0.01091 | -0.013618 | 0.056123 | -0.020168 | 0.05056 | 0.097237 | 0.004578 | 0.15564 | -0.15564 | 0.33875 | -119.3893 | 0.36621 | 0.36163 | 0.46692 | 0.81024 | -122.0352 | 121.5546 | -0.5127 | 121.7148 | 122.049 | -120.0577 | -0.32501 | 0.14191 | 0.16022 | 122.0718 | 122.1771 | 2.3209 | 121.8658 | 121.7148 | 122.5204 | 122.0764 | -0.32501 | 121.8658 | 121.7148 | 122.0764 | 2.3209 | 122.5204 | -0.82398 | -122.7036
6664.0781 | 122.6028 | -121.7468 | 0.73242 | -0.26665 | 0.012405 | -0.020027 | 0.05121 | -0.022304 | 0.054192 | 0.095955 | 0.07782 | 0.14191 | -0.11444 | 0.42572 | -119.3115 | 0.44403 | 0.33417 | 0.58594 | 0.81482 | -122.113 | 121.6324 | -0.59052 | 121.8246 | 122.1725 | -120.0439 | -0.36621 | 0.082397 | 0.19226 | 122.081 | 122.3328 | 2.4353 | 121.8887 | 121.8246 | 122.5616 | 122.1909 | -0.36621 | 121.8887 | 121.8246 | 122.1909 | 2.4353 | 122.5616 | -0.84686 | -122.8455
6665.8438 | 122.699 | -121.7422 | 0.66376 | 0.13771 | 0.014755 | -0.016396 | 0.056337 | -0.022091 | 0.053124 | 0.095741 | 0.036621 | 0.16479 | -0.16937 | 0.36163 | -119.3893 | 0.41199 | 0.27008 | 0.53558 | 0.79193 | -122.0901 | 121.5729 | -0.49896 | 121.7789 | 122.1039 | -120.0531 | -0.3479 | 0.12817 | 0.20599 | 122.0123 | 122.2778 | 2.3529 | 121.907 | 121.7789 | 122.5342 | 122.1542 | -0.3479 | 121.907 | 121.7789 | 122.1542 | 2.3529 | 122.5342 | -0.83313 | -122.7539
6667.625 | 122.6349 | -121.7606 | 0.72784 | -0.18272 | 0.012405 | -0.018318 | 0.051851 | -0.022945 | 0.055474 | 0.095955 | 0.004578 | 0.16937 | -0.13733 | 0.36163 | -119.3481 | 0.37079 | 0.40283 | 0.52185 | 0.8194 | -122.0627 | 121.6232 | -0.55847 | 121.7651 | 122.1222 | -120.076 | -0.30212 | 0.091553 | 0.14191 | 122.1634 | 122.2824 | 2.4124 | 121.9299 | 121.7651 | 122.58 | 122.1313 | -0.30212 | 121.9299 | 121.7651 | 122.1313 | 2.4124 | 122.58 | -0.86517 | -122.7905
6669.4062 | 122.5891 | -121.7651 | 0.71869 | -0.14458 | 0.010269 | -0.0196 | 0.056764 | -0.019954 | 0.053337 | 0.09681 | 0.041199 | 0.14648 | -0.16479 | 0.40741 | -119.3161 | 0.41657 | 0.34332 | 0.55389 | 0.82855 | -122.0398 | 121.6003 | -0.57221 | 121.8063 | 122.1725 | -120.0348 | -0.27466 | 0.10986 | 0.20599 | 122.1085 | 122.319 | 2.449 | 121.9116 | 121.8063 | 122.5937 | 122.1817 | -0.27466 | 121.9116 | 121.8063 | 122.1817 | 2.449 | 122.5937 | -0.88348 | -122.7585
6671.1094 | 122.6166 | -121.7377 | 0.74616 | -0.28191 | 0.013687 | -0.019813 | 0.05121 | -0.022945 | 0.052483 | 0.09446 | 0.054932 | 0.15564 | -0.1236 | 0.39825 | -119.2932 | 0.43488 | 0.36621 | 0.5722 | 0.81024 | -122.0535 | 121.6141 | -0.59052 | 121.7926 | 122.1359 | -120.0394 | -0.31586 | 0.064087 | 0.17853 | 122.1039 | 122.3099 | 2.4445 | 121.8933 | 121.7926 | 122.5479 | 122.1725 | -0.31586 | 121.8933 | 121.7926 | 122.1725 | 2.4445 | 122.5479 | -0.86975 | -122.7997
6672.875 | 122.7173 | -121.6965 | 0.6958 | 0.11482 | 0.014114 | -0.015541 | 0.055696 | -0.022091 | 0.051842 | 0.096382 | 0 | 0.16937 | -0.16937 | 0.34332 | -119.3573 | 0.38452 | 0.36163 | 0.48065 | 0.82398 | -122.0673 | 121.5271 | -0.52643 | 121.6965 | 122.0398 | -120.0531 | -0.37079 | 0.12817 | 0.16937 | 122.0581 | 122.1771 | 2.3392 | 121.8658 | 121.6965 | 122.5204 | 122.081 | -0.37079 | 121.8658 | 121.6965 | 122.081 | 2.3392 | 122.5204 | -0.86517 | -122.7631
6674.6719 | 122.6303 | -121.7514 | 0.72327 | -0.0072479 | 0.013046 | -0.017677 | 0.058259 | -0.020168 | 0.051415 | 0.098519 | 0.022888 | 0.16479 | -0.16022 | 0.37079 | -119.339 | 0.40283 | 0.36621 | 0.51727 | 0.8194 | -122.0398 | 121.5912 | -0.55847 | 121.7743 | 122.1222 | -120.0623 | -0.28839 | 0.09613 | 0.1831 | 122.1176 | 122.2687 | 2.4124 | 121.9162 | 121.7743 | 122.5708 | 122.1542 | -0.28839 | 121.9162 | 121.7743 | 122.1542 | 2.4124 | 122.5708 | -0.88348 | -122.7631
6676.3906 | 122.6486 | -121.7331 | 0.70953 | 0.091934 | 0.014969 | -0.018104 | 0.058259 | -0.020809 | 0.053124 | 0.09681 | 0.013733 | 0.15106 | -0.15106 | 0.33875 | -119.4168 | 0.37079 | 0.38452 | 0.4715 | 0.8194 | -122.081 | 121.582 | -0.55847 | 121.7468 | 122.0718 | -120.1263 | -0.3479 | 0.10986 | 0.16479 | 122.1176 | 122.2046 | 2.3163 | 121.8842 | 121.7468 | 122.5525 | 122.1039 | -0.3479 | 121.8842 | 121.7468 | 122.1039 | 2.3163 | 122.5525 | -0.8606 | -122.7905
6678.1562 | 122.6212 | -121.7239 | 0.74158 | -0.13695 | 0.01326 | -0.018532 | 0.048005 | -0.022091 | 0.054192 | 0.095101 | 0.10071 | 0.13733 | -0.10986 | 0.4715 | -119.2291 | 0.53101 | 0.25177 | 0.65918 | 0.79651 | -122.0398 | 121.6141 | -0.60425 | 121.8246 | 122.1954 | -119.9707 | -0.31586 | 0.054932 | 0.21057 | 121.9757 | 122.3831 | 2.4948 | 121.8613 | 121.8246 | 122.5204 | 122.2549 | -0.31586 | 121.8613 | 121.8246 | 122.2549 | 2.4948 | 122.5204 | -0.85144 | -122.7814
6679.9219 | 122.5891 | -121.7789 | 0.737 | -0.17509 | 0.012832 | -0.019173 | 0.049714 | -0.022732 | 0.05291 | 0.096169 | 0.086975 | 0.13275 | -0.11902 | 0.45776 | -119.2429 | 0.49439 | 0.29755 | 0.64545 | 0.78735 | -122.049 | 121.6599 | -0.60425 | 121.8658 | 122.2366 | -119.9799 | -0.27008 | 0.050354 | 0.20599 | 122.0764 | 122.4243 | 2.536 | 121.9116 | 121.8658 | 122.5662 | 122.2733 | -0.27008 | 121.9116 | 121.8658 | 122.2733 | 2.536 | 122.5662 | -0.85602 | -122.7859
6681.7031 | 122.6257 | -121.7468 | 0.73242 | -0.28191 | 0.013473 | -0.013832 | 0.052278 | -0.023372 | 0.053978 | 0.095314 | 0.073242 | 0.14191 | -0.11902 | 0.40741 | -119.2932 | 0.44861 | 0.36163 | 0.58136 | 0.80566 | -122.113 | 121.6278 | -0.59052 | 121.8201 | 122.1542 | -120.0256 | -0.36621 | 0.073242 | 0.19226 | 122.1085 | 122.3282 | 2.4536 | 121.8887 | 121.8201 | 122.5525 | 122.1954 | -0.36621 | 121.8887 | 121.8201 | 122.1954 | 2.4536 | 122.5525 | -0.85144 | -122.8455
6683.4688 | 122.6898 | -121.7194 | 0.70953 | 0.076676 | 0.012832 | -0.015541 | 0.056123 | -0.020595 | 0.053551 | 0.095528 | 0.07782 | 0.11444 | -0.10986 | 0.45776 | -119.2932 | 0.50354 | 0.18768 | 0.6134 | 0.80109 | -122.0078 | 121.6095 | -0.59509 | 121.7972 | 122.1771 | -120.0027 | -0.28839 | 0.091552 | 0.18768 | 121.907 | 122.3328 | 2.4261 | 121.8338 | 121.7972 | 122.5204 | 122.2229 | -0.28839 | 121.8338 | 121.7972 | 122.2229 | 2.4261 | 122.5204 | -0.8194 | -122.7173
6685.1719 | 122.6532 | -121.7422 | 0.70496 | -0.091171 | 0.015396 | -0.016823 | 0.049287 | -0.022304 | 0.052697 | 0.095955 | 0.10529 | 0.1236 | -0.10529 | 0.45319 | -119.22 | 0.5127 | 0.23804 | 0.65002 | 0.79193 | -122.0306 | 121.637 | -0.58136 | 121.8475 | 122.1954 | -119.9249 | -0.28839 | 0.086975 | 0.21057 | 121.9803 | 122.3923 | 2.5223 | 121.8658 | 121.8475 | 122.5342 | 122.2549 | -0.28839 | 121.8658 | 121.8475 | 122.2549 | 2.5223 | 122.5342 | -0.81024 | -122.7356
6686.9375 | 122.6486 | -121.7285 | 0.71869 | -0.14458 | 0.014328 | -0.016182 | 0.050782 | -0.0238 | 0.053765 | 0.094887 | 0.091553 | 0.1236 | -0.12817 | 0.46234 | -119.2474 | 0.50812 | 0.21973 | 0.66376 | 0.7782 | -122.0535 | 121.6003 | -0.59509 | 121.8201 | 122.1909 | -119.9661 | -0.32501 | 0.059509 | 0.21973 | 121.9482 | 122.3923 | 2.4811 | 121.8521 | 121.8201 | 122.5067 | 122.2366 | -0.32501 | 121.8521 | 121.8201 | 122.2366 | 2.4811 | 122.5067 | -0.84686 | -122.7722
6688.7031 | 122.6852 | -121.6965 | 0.70038 | 0.19875 | 0.014114 | -0.0097733 | 0.059114 | -0.022091 | 0.053337 | 0.097023 | 0.032043 | 0.14648 | -0.13733 | 0.39825 | -119.3253 | 0.4303 | 0.24261 | 0.54016 | 0.79651 | -122.0581 | 121.5591 | -0.55389 | 121.7285 | 122.0947 | -120.0256 | -0.36163 | 0.096131 | 0.16937 | 121.9391 | 122.2366 | 2.3712 | 121.843 | 121.7285 | 122.493 | 122.1268 | -0.36163 | 121.843 | 121.7285 | 122.1268 | 2.3712 | 122.493 | -0.83771 | -122.7585
6690.4062 | 122.6578 | -121.7285 | 0.71869 | -0.068283 | 0.013046 | -0.016396 | 0.052278 | -0.0238 | 0.053978 | 0.095955 | 0.10529 | 0.12817 | -0.12817 | 0.45319 | -119.2291 | 0.50812 | 0.22888 | 0.66376 | 0.79193 | -122.0398 | 121.6003 | -0.59052 | 121.8338 | 122.1817 | -119.9478 | -0.31128 | 0.073242 | 0.23346 | 121.9574 | 122.3923 | 2.4994 | 121.8567 | 121.8338 | 122.5204 | 122.2366 | -0.31128 | 121.8567 | 121.8338 | 122.2366 | 2.4994 | 122.5204 | -0.84686 | -122.7585
6692.1719 | 122.7219 | -121.7285 | 0.70496 | -0.022507 | 0.011978 | -0.016182 | 0.050996 | -0.022518 | 0.05291 | 0.095528 | 0.059509 | 0.14648 | -0.12817 | 0.41657 | -119.2932 | 0.45319 | 0.25177 | 0.60425 | 0.79193 | -122.0718 | 121.6003 | -0.55847 | 121.788 | 122.1451 | -119.9982 | -0.34332 | 0.086975 | 0.18768 | 121.9803 | 122.3328 | 2.4353 | 121.875 | 121.788 | 122.5204 | 122.1817 | -0.34332 | 121.875 | 121.788 | 122.1817 | 2.4353 | 122.5204 | -0.83313 | -122.7768
6693.9375 | 122.5891 | -121.7651 | 0.73242 | -0.13695 | 0.013473 | -0.013191 | 0.057618 | -0.019314 | 0.05056 | 0.095528 | 0.068665 | 0.13733 | -0.17853 | 0.40283 | -119.3298 | 0.41199 | 0.32959 | 0.55847 | 0.81024 | -122.0444 | 121.5866 | -0.59509 | 121.8338 | 122.168 | -120.0623 | -0.27924 | 0.07782 | 0.24719 | 122.0947 | 122.3236 | 2.4353 | 121.9025 | 121.8338 | 122.5754 | 122.1771 | -0.27924 | 121.9025 | 121.8338 | 122.1771 | 2.4353 | 122.5754 | -0.91095 | -122.7768
6695.7188 | 122.7127 | -121.7056 | 0.67749 | 0.053787 | 0.015182 | -0.017677 | 0.058259 | -0.020595 | 0.05056 | 0.097878 | 0 | 0.16479 | -0.16937 | 0.34332 | -119.3527 | 0.36621 | 0.35248 | 0.48065 | 0.8194 | -122.0901 | 121.5363 | -0.5127 | 121.7056 | 122.049 | -120.0302 | -0.38452 | 0.14191 | 0.16937 | 122.0581 | 122.1863 | 2.3529 | 121.8704 | 121.7056 | 122.525 | 122.0718 | -0.38452 | 121.8704 | 121.7056 | 122.0718 | 2.3529 | 122.525 | -0.84686 | -122.7676
6697.4062 | 122.6578 | -121.7422 | 0.71411 | -0.22087 | 0.013473 | -0.018959 | 0.052278 | -0.023372 | 0.053124 | 0.095741 | -0.009155 | 0.16937 | -0.16479 | 0.34332 | -119.3207 | 0.37079 | 0.4303 | 0.53558 | 0.82855 | -122.0901 | 121.5775 | -0.54474 | 121.7331 | 122.0856 | -120.0348 | -0.3479 | 0.11444 | 0.15564 | 122.1725 | 122.2778 | 2.4216 | 121.9116 | 121.7331 | 122.5708 | 122.113 | -0.3479 | 121.9116 | 121.7331 | 122.113 | 2.4216 | 122.5708 | -0.87891 | -122.8043
6699.1719 | 122.6898 | -121.7239 | 0.68207 | 0.053787 | 0.01326 | -0.017677 | 0.057618 | -0.02145 | 0.052697 | 0.096169 | 0.009155 | 0.14648 | -0.15564 | 0.31586 | -119.3665 | 0.3479 | 0.37994 | 0.45776 | 0.80566 | -122.0764 | 121.5683 | -0.53558 | 121.7331 | 122.0398 | -120.0485 | -0.35248 | 0.1236 | 0.16479 | 122.1039 | 122.1817 | 2.3575 | 121.8704 | 121.7331 | 122.5296 | 122.0718 | -0.35248 | 121.8704 | 121.7331 | 122.0718 | 2.3575 | 122.5296 | -0.83771 | -122.7585
6700.9531 | 122.6578 | -121.7377 | 0.72327 | -0.25139 | 0.012619 | -0.017677 | 0.052491 | -0.022304 | 0.051628 | 0.096169 | -0.022888 | 0.17395 | -0.17853 | 0.34332 | -119.3665 | 0.36621 | 0.42114 | 0.52185 | 0.83771 | -122.0856 | 121.5591 | -0.54932 | 121.7148 | 122.081 | -120.0897 | -0.3479 | 0.11444 | 0.15564 | 122.1588 | 122.2595 | 2.3712 | 121.9116 | 121.7148 | 122.5754 | 122.1039 | -0.3479 | 121.9116 | 121.7148 | 122.1039 | 2.3712 | 122.5754 | -0.9018 | -122.8088
6702.7188 | 122.7219 | -121.7148 | 0.70496 | 0.11482 | 0.012619 | -0.017891 | 0.049073 | -0.02145 | 0.053765 | 0.095955 | 0.086975 | 0.1236 | -0.12817 | 0.40741 | -119.2383 | 0.49896 | 0.21057 | 0.59967 | 0.77362 | -122.0444 | 121.5866 | -0.58136 | 121.8018 | 122.1222 | -119.9432 | -0.32959 | 0.068665 | 0.21515 | 121.9254 | 122.3145 | 2.4765 | 121.8384 | 121.8018 | 122.4884 | 122.2137 | -0.32959 | 121.8384 | 121.8018 | 122.2137 | 2.4765 | 122.4884 | -0.83313 | -122.7493
6704.4219 | 122.7219 | -121.7102 | 0.69122 | -0.045395 | 0.014541 | -0.017891 | 0.051637 | -0.024013 | 0.056755 | 0.096596 | 0.059509 | 0.1236 | -0.11444 | 0.42114 | -119.252 | 0.48523 | 0.25635 | 0.62256 | 0.79193 | -122.0718 | 121.5958 | -0.56763 | 121.7697 | 122.1313 | -119.9432 | -0.36163 | 0.10071 | 0.17395 | 121.9666 | 122.3328 | 2.4582 | 121.8338 | 121.7697 | 122.5021 | 122.1954 | -0.36163 | 121.8338 | 121.7697 | 122.1954 | 2.4582 | 122.5021 | -0.80566 | -122.7631
6706.1875 | 122.7219 | -121.7422 | 0.6958 | -0.022507 | 0.014541 | -0.015968 | 0.052491 | -0.022304 | 0.056969 | 0.097237 | 0.045776 | 0.12817 | -0.1236 | 0.41199 | -119.2612 | 0.47607 | 0.2655 | 0.61798 | 0.77362 | -122.081 | 121.6187 | -0.56763 | 121.788 | 122.1542 | -119.957 | -0.33875 | 0.07782 | 0.16937 | 122.0078 | 122.3602 | 2.4811 | 121.8704 | 121.788 | 122.5159 | 122.2183 | -0.33875 | 121.8704 | 121.788 | 122.2183 | 2.4811 | 122.5159 | -0.8194 | -122.7768
6707.8906 | 122.6898 | -121.7514 | 0.71411 | -0.11406 | 0.01326 | -0.022163 | 0.05121 | -0.025081 | 0.054192 | 0.09446 | 0.091553 | 0.11902 | -0.13733 | 0.46234 | -119.22 | 0.49439 | 0.22888 | 0.65918 | 0.78278 | -122.0673 | 121.6141 | -0.59509 | 121.843 | 122.2137 | -119.9341 | -0.31586 | 0.068665 | 0.22888 | 121.9803 | 122.4106 | 2.5314 | 121.8704 | 121.843 | 122.5342 | 122.2458 | -0.31586 | 121.8704 | 121.843 | 122.2458 | 2.5314 | 122.5342 | -0.85144 | -122.7814
6709.6719 | 122.6028 | -121.8018 | 0.73242 | -0.17509 | 0.011337 | -0.019173 | 0.052064 | -0.022732 | 0.051415 | 0.096169 | 0.086975 | 0.11902 | -0.12817 | 0.48065 | -119.2245 | 0.49439 | 0.23804 | 0.66376 | 0.76446 | -122.0398 | 121.6736 | -0.6134 | 121.8887 | 122.2824 | -119.957 | -0.23804 | 0.032043 | 0.21515 | 122.0398 | 122.4655 | 2.5772 | 121.9208 | 121.8887 | 122.5662 | 122.2961 | -0.23804 | 121.9208 | 121.8887 | 122.2961 | 2.5772 | 122.5662 | -0.8606 | -122.7722
6711.4375 | 122.5983 | -121.7972 | 0.71411 | -0.15221 | 0.014969 | -0.016823 | 0.059327 | -0.022091 | 0.050988 | 0.094673 | 0.064087 | 0.15106 | -0.16937 | 0.39825 | -119.3161 | 0.39825 | 0.32044 | 0.56763 | 0.80566 | -122.0993 | 121.6278 | -0.56305 | 121.8613 | 122.1954 | -120.0302 | -0.30212 | 0.091553 | 0.23346 | 122.1176 | 122.3648 | 2.4811 | 121.9482 | 121.8613 | 122.6028 | 122.1954 | -0.30212 | 121.9482 | 121.8613 | 122.1954 | 2.4811 | 122.6028 | -0.88348 | -122.8134
6713.1562 | 122.5891 | -121.7743 | 0.70038 | -0.098801 | 0.014969 | -0.0149 | 0.059114 | -0.021877 | 0.050988 | 0.097023 | 0.064087 | 0.15106 | -0.15564 | 0.39825 | -119.2932 | 0.41657 | 0.32044 | 0.54016 | 0.78735 | -122.0444 | 121.6187 | -0.54932 | 121.8384 | 122.1725 | -119.9936 | -0.27008 | 0.086976 | 0.21973 | 122.0947 | 122.3145 | 2.4811 | 121.9254 | 121.8384 | 122.5616 | 122.1909 | -0.27008 | 121.9254 | 121.8384 | 122.1909 | 2.4811 | 122.5616 | -0.85602 | -122.7448
6714.9375 | 122.6532 | -121.756 | 0.72784 | -0.30479 | 0.011978 | -0.021309 | 0.050782 | -0.022518 | 0.052056 | 0.096169 | 0 | 0.12817 | -0.14648 | 0.33417 | -119.3344 | 0.37994 | 0.40283 | 0.53558 | 0.83771 | -122.0764 | 121.6095 | -0.59967 | 121.756 | 122.0901 | -120.0623 | -0.32043 | 0.10986 | 0.14648 | 122.1588 | 122.2916 | 2.4216 | 121.8842 | 121.756 | 122.5937 | 122.1359 | -0.32043 | 121.8842 | 121.756 | 122.1359 | 2.4216 | 122.5937 | -0.87433 | -122.8043
6716.7031 | 122.7402 | -121.7422 | 0.68665 | 0.053787 | 0.012619 | -0.020668 | 0.050355 | -0.023372 | 0.053978 | 0.096382 | 0.054932 | 0.11902 | -0.10986 | 0.40283 | -119.2749 | 0.4715 | 0.24719 | 0.58136 | 0.7782 | -122.0947 | 121.6324 | -0.56763 | 121.7972 | 122.1451 | -119.9615 | -0.35248 | 0.091552 | 0.16479 | 121.9894 | 122.3236 | 2.4673 | 121.8613 | 121.7972 | 122.5204 | 122.2137 | -0.35248 | 121.8613 | 121.7972 | 122.2137 | 2.4673 | 122.5204 | -0.79651 | -122.7814
6718.4688 | 122.731 | -121.7102 | 0.68207 | 0.099564 | 0.012619 | -0.013832 | 0.056123 | -0.018886 | 0.052056 | 0.096596 | 0 | 0.15564 | -0.15564 | 0.3479 | -119.339 | 0.37994 | 0.33875 | 0.48065 | 0.8194 | -122.0673 | 121.5546 | -0.52643 | 121.7102 | 122.0581 | -120.0211 | -0.35706 | 0.13733 | 0.15564 | 122.049 | 122.1909 | 2.3712 | 121.8658 | 121.7102 | 122.5296 | 122.0901 | -0.35706 | 121.8658 | 121.7102 | 122.0901 | 2.3712 | 122.5296 | -0.83771 | -122.7493
6720.1719 | 122.7448 | -121.7285 | 0.68665 | 0.00038159 | 0.014114 | -0.015968 | 0.050782 | -0.022518 | 0.053978 | 0.096382 | 0.050354 | 0.12817 | -0.13733 | 0.39825 | -119.2932 | 0.45319 | 0.26093 | 0.56763 | 0.78278 | -122.1085 | 121.5912 | -0.55847 | 121.7789 | 122.1268 | -119.9799 | -0.37994 | 0.09613 | 0.18768 | 121.9894 | 122.2961 | 2.4353 | 121.8567 | 121.7789 | 122.5113 | 122.1817 | -0.37994 | 121.8567 | 121.7789 | 122.1817 | 2.4353 | 122.5113 | -0.82398 | -122.7951

## Thermal Data
Fire Time | E Position - 3' | E Position - Middle | E Position - 7'
-0.824 | 14.8537 | 14.2659 | 14.4572
0.176 | 14.8534 | 14.2627 | 14.454
1.176 | 14.8622 | 14.2741 | 14.4687
2.176 | 14.8663 | 14.3012 | 14.4619
3.176 | 14.8791 | 14.2977 | 14.4847
4.176 | 14.8928 | 14.2616 | 14.5358
5.176 | 14.9316 | 13.9061 | 16.2633
6.176 | 16.7897 | 13.4158 | 21.0694
7.176 | 17.8707 | 11.8084 | 27.0592
8.176 | 21.224 | 9.1733 | 33.9264
9.176 | 25.8762 | 4.6745 | 42.1391
10.176 | 31.5112 | 0.1251 | 57.1708
11.176 | 37.6341 | -5.9773 | 66.8185
12.176 | 46.7591 | -13.2097 | 77.2058
13.176 | 53.8652 | -19.7261 | 87.3336
14.176 | 61.7862 | NaN | 100.0093
15.176 | 68.9896 | NaN | 113.4476
16.176 | 76.2741 | NaN | 124.757
17.176 | 83.0586 | NaN | 134.9742
18.176 | 89.6356 | NaN | 143.8573
19.176 | 95.9648 | NaN | 152.0978
20.1917 | 101.8904 | NaN | 159.9409
21.176 | 107.9658 | NaN | 164.8628
22.176 | 111.6352 | NaN | 171.3904
23.176 | 117.429 | NaN | 174.8511
24.176 | 120.7407 | NaN | 175.1873
25.176 | 125.2268 | NaN | 176.2721
26.176 | 127.3057 | NaN | 176.4627
27.176 | 128.6032 | NaN | 176.5121
28.176 | 129.0828 | NaN | 176.1531
29.176 | 129.9842 | NaN | 175.3742
30.176 | 130.749 | NaN | 174.4377
31.176 | 131.159 | NaN | 173.2736
32.176 | 131.3788 | NaN | 172.105
33.176 | 131.3678 | NaN | 170.7125
34.176 | 131.3732 | NaN | 169.194
35.176 | 131.0505 | NaN | 167.4963
36.176 | 130.4429 | NaN | 165.7142
37.176 | 129.5892 | NaN | 163.6485
38.176 | 128.5045 | NaN | 161.2221
39.176 | 127.4451 | NaN | 158.8691
40.176 | 126.156 | NaN | 156.6883
41.176 | 125.1559 | NaN | 154.5459
42.176 | 124.1995 | NaN | 152.2333
43.176 | 122.8771 | NaN | 149.8802
44.176 | 121.5072 | NaN | 147.7665
45.176 | 120.2967 | NaN | 145.7432
46.176 | 119.2445 | NaN | 143.6422
47.176 | 118.2798 | NaN | 141.2459
48.176 | 117.3992 | NaN | 138.7475
49.176 | 116.5076 | NaN | 136.4927
50.1917 | 115.6121 | NaN | 134.7252
51.176 | 114.5819 | NaN | 132.7739
52.176 | 113.3847 | NaN | 131.0146
53.176 | 112.282 | NaN | 129.49
54.176 | 111.3973 | NaN | 127.8053
55.176 | 110.4833 | NaN | 126.3884
56.176 | 109.5056 | NaN | 125.03
57.176 | 108.6866 | NaN | 123.7384
58.176 | 107.8439 | NaN | 122.6229
59.176 | 106.9125 | NaN | 121.6154
60.176 | 106.0037 | NaN | 120.2665
61.176 | 105.2592 | NaN | 119.0986
62.176 | 104.5411 | NaN | 117.7495
63.176 | 103.7021 | NaN | 116.5655
64.176 | 102.5424 | NaN | 115.4062
65.176 | 101.5939 | NaN | 114.4368
66.176 | 100.7084 | NaN | 113.508
67.176 | 99.6597 | NaN | 112.5594
68.176 | 98.8153 | NaN | 111.5961
69.176 | 98.2432 | NaN | 110.6316
70.176 | 97.5106 | NaN | 109.8746
71.176 | 96.6268 | NaN | 109.2235
72.176 | 95.7835 | NaN | 108.4924
73.176 | 95.0026 | NaN | 108.024
74.176 | 94.6455 | NaN | 107.4612
75.176 | 94.2951 | NaN | 107.0198
76.176 | 94.3079 | NaN | 106.719
77.176 | 94.2548 | NaN | 106.3694
78.176 | 94.6215 | NaN | 106.1029
79.176 | 94.7619 | NaN | 106.2726
80.176 | 94.2647 | NaN | 106.0011
81.176 | 94.4281 | NaN | 106.1437
82.176 | 94.867 | NaN | 106.112
83.176 | 95.3287 | NaN | 106.3423
84.176 | 95.6594 | NaN | 107.0107
85.176 | 95.4791 | NaN | 107.3752
86.176 | 95.6251 | NaN | 107.6885
87.176 | 96.0179 | NaN | 108.4774
88.176 | 96.565 | NaN | 109.2531
89.176 | 97.7916 | NaN | 110.1254
90.176 | 98.7516 | NaN | 110.4324
91.176 | 99.2644 | NaN | 110.6916
92.176 | 99.8783 | NaN | 110.8011
93.176 | 100.1163 | NaN | 111.2674
94.176 | 100.5087 | NaN | 111.8209
95.176 | 100.7401 | NaN | 112.1209
96.176 | 100.8893 | NaN | 109.0963
97.176 | 100.9265 | NaN | 113.1404
98.176 | 101.0898 | NaN | 115.1273
99.176 | 101.2368 | NaN | 115.6003
100.176 | 101.7652 | NaN | 116.7873
101.176 | 102.5939 | NaN | 117.5169
102.176 | 103.1286 | NaN | 118.1261
103.176 | 103.5656 | NaN | 117.7768
104.176 | 104.0676 | NaN | 119.8987
105.176 | 104.6866 | NaN | 120.5044
106.176 | 105.3054 | NaN | 122.0537
107.176 | 105.939 | NaN | 122.7164
108.176 | 106.4681 | NaN | 122.9718
109.176 | 106.8596 | NaN | 124.3866
110.176 | 107.0602 | NaN | 125.0108
111.176 | 107.9826 | NaN | 125.9399
112.176 | 108.5689 | NaN | 126.4835
113.176 | 109.2127 | NaN | 126.8186
114.176 | 109.8855 | NaN | 127.0507
115.176 | 110.1922 | NaN | 127.3088
116.176 | 110.7477 | NaN | 128.0674
117.176 | 111.3495 | NaN | 128.4376
118.176 | 110.9924 | NaN | 129.0545
119.176 | 110.9625 | NaN | 129.0539
120.176 | 111.303 | NaN | 128.7925
121.176 | 111.6213 | NaN | 128.4876
122.176 | 112.1076 | NaN | 128.5713
123.176 | 112.3538 | NaN | 128.9045
124.176 | 112.5713 | NaN | 129.0428
125.176 | 112.5126 | NaN | 129.2778
126.176 | 112.5276 | NaN | 129.0897
127.176 | 112.4734 | NaN | 129.1003
128.176 | 112.2437 | NaN | 129.2495
129.176 | 112.2682 | NaN | 130.1216
130.176 | 112.4964 | NaN | 129.7629
131.176 | 112.6032 | NaN | 129.8328
132.176 | 112.448 | NaN | 129.8505
133.176 | 112.2071 | NaN | 130.1682
134.176 | 112.032 | NaN | 130.4471
135.176 | 112.2221 | NaN | 130.4673
136.176 | 111.7299 | NaN | 130.4111
137.176 | 111.5991 | NaN | 130.5531
138.176 | 111.9969 | NaN | 130.428
139.176 | 112.4816 | NaN | 130.3397
140.176 | 113.2573 | NaN | 130.3477
141.176 | 113.4207 | NaN | 130.3824
142.176 | 113.4724 | NaN | 130.431
143.176 | 113.1953 | NaN | 130.5583
144.176 | 113.1485 | NaN | 130.2952
145.176 | 113.4583 | NaN | 130.6399
146.176 | 113.6918 | NaN | 130.5938
147.176 | 113.9686 | NaN | 130.5496
148.176 | 114.198 | NaN | 130.7796
149.176 | 114.137 | NaN | 130.9566
150.176 | 114.0373 | NaN | 130.931
151.176 | 114.1737 | NaN | 130.7098
152.176 | 113.8267 | NaN | 130.8361
153.176 | 114.1142 | NaN | 131.1425
154.176 | 114.2726 | NaN | 130.9723
155.176 | 114.515 | NaN | 131.5841
156.176 | 114.2469 | NaN | 131.6741
157.176 | 114.3839 | NaN | 131.7329
158.176 | 114.4996 | NaN | 131.7686
159.176 | 114.9061 | NaN | 132.063
160.176 | 115.5037 | NaN | 131.9096
161.176 | 115.8925 | NaN | 132.0101
162.176 | 116.3296 | NaN | 132.4737
163.176 | 116.4187 | NaN | 132.6529
164.176 | 116.4282 | NaN | 132.5849
165.176 | 116.6418 | NaN | 132.5495
166.176 | 116.8736 | NaN | 132.7086
167.176 | 117.2028 | NaN | 133.2746
168.176 | 117.5025 | NaN | 133.1959
169.176 | 117.5801 | NaN | 133.2004
170.176 | 117.9481 | NaN | 132.9151
171.176 | 118.0515 | NaN | 133.0175
172.176 | 118.0007 | NaN | 132.8148
173.176 | 117.8519 | NaN | 132.8115
174.176 | 117.6763 | NaN | 132.9068
175.176 | 117.9335 | NaN | 133.393
176.176 | 118.2874 | NaN | 133.5607
177.176 | 118.362 | NaN | 133.5275
178.176 | 118.4964 | NaN | 133.5646
179.176 | 118.4535 | NaN | 134.1773
180.176 | 118.8443 | NaN | 134.8958
181.176 | 119.1655 | NaN | 135.661
182.176 | 119.0043 | NaN | 136.3256
183.176 | 118.9771 | NaN | 136.8352
184.176 | 119.0559 | NaN | 137.3141
185.176 | 119.3655 | NaN | 137.6905
186.176 | 119.4976 | NaN | 137.878
187.176 | 119.9414 | NaN | 138.1868
188.176 | 120.1461 | NaN | 138.4978
189.176 | 120.0084 | NaN | 138.5943
190.176 | 120.3611 | NaN | 138.836
191.176 | 121.1874 | NaN | 138.782
192.176 | 121.3783 | NaN | 138.648
193.176 | 121.7827 | NaN | 138.6167
194.176 | 121.9916 | NaN | 138.6395
195.176 | 122.2166 | NaN | 138.4296
196.176 | 122.0147 | NaN | 139.0126
197.176 | 122.2452 | NaN | 139.0457
198.176 | 122.2475 | NaN | 139.098
199.176 | 122.0097 | NaN | 139.1053
200.1917 | 121.8396 | NaN | 138.8509
201.176 | 121.763 | NaN | 138.9705
202.176 | 121.7662 | NaN | 138.9358
203.176 | 121.3235 | NaN | 139.1323
204.176 | 121.1902 | NaN | 139.3066
205.176 | 120.852 | NaN | 139.5228
206.176 | 120.675 | NaN | 139.6951
207.176 | 120.5769 | NaN | 140.7082
208.176 | 120.6757 | NaN | 140.9176
209.176 | 120.8035 | NaN | 141.3432
210.176 | 121.1534 | NaN | 141.604
211.176 | 121.6272 | NaN | 141.9039
212.176 | 121.9245 | NaN | 141.6551
213.176 | 122.0614 | NaN | 141.5044
214.176 | 121.8852 | NaN | 141.635
215.176 | 121.953 | NaN | 141.6749
216.176 | 122.0204 | NaN | 141.3057
217.176 | 121.9927 | NaN | 141.096
218.176 | 121.9434 | NaN | 141.4585
219.176 | 122.2357 | NaN | 141.9365
220.176 | 122.1204 | NaN | 141.8697
221.176 | 122.3627 | NaN | 142.1549
222.176 | 122.7025 | NaN | 142.3605
223.176 | 123.2214 | NaN | 142.6495
224.176 | 123.8243 | NaN | 142.5621
225.176 | 123.9492 | NaN | 142.4721
226.176 | 123.7801 | NaN | 142.7344
227.176 | 123.8765 | NaN | 142.697
228.176 | 124.3425 | NaN | 142.8687
229.176 | 124.5562 | NaN | 143.0145
230.176 | 124.9546 | NaN | 142.8147
231.176 | 125.0017 | NaN | 142.8867
232.176 | 125.306 | NaN | 142.8882
233.176 | 125.5334 | NaN | 142.9702
234.176 | 125.505 | NaN | 142.7823
235.176 | 125.4917 | NaN | 142.4463
236.176 | 125.5969 | NaN | 142.1445
237.176 | 125.5885 | NaN | 141.893
238.176 | 125.5779 | NaN | 141.992
239.176 | 125.7895 | NaN | 141.7485
240.176 | 125.9834 | NaN | 141.4791
241.176 | 126.1937 | NaN | 141.459
242.176 | 126.4274 | NaN | 141.3443
243.176 | 126.0935 | NaN | 141.0922
244.176 | 126.3982 | NaN | 140.9013
245.176 | 126.5546 | NaN | 141.1889
246.176 | 126.9304 | NaN | 140.9409
247.176 | 127.0226 | NaN | 140.7621
248.176 | 127.2291 | NaN | 140.8596
249.176 | 127.6802 | NaN | 141.3533
250.176 | 127.3788 | NaN | 141.639
251.176 | 127.7136 | NaN | 141.806
252.176 | 127.7038 | NaN | 142.2312
253.176 | 127.1953 | NaN | 142.4816
254.176 | 126.8687 | NaN | 142.5554
255.176 | 126.6851 | NaN | 142.8398
256.176 | 126.6091 | NaN | 143.0786
257.176 | 125.8676 | NaN | 143.2733
258.176 | 125.7946 | NaN | 143.1893
259.176 | 126.0188 | NaN | 142.9207
260.176 | 126.4565 | NaN | 143.5018
261.176 | 127.1154 | NaN | 143.444
262.176 | 127.2974 | NaN | 143.4341
263.176 | 126.9287 | NaN | 143.0624
264.176 | 126.6514 | NaN | 143.0441
265.176 | 126.4989 | NaN | 143.1298
266.176 | 126.4681 | NaN | 142.996
267.176 | 126.2552 | NaN | 143.1685
268.176 | 126.3889 | NaN | 143.072
269.176 | 126.3102 | NaN | 143.3981
270.176 | 126.1968 | NaN | 143.8053
271.176 | 126.0348 | NaN | 144.0311
272.176 | 125.8129 | NaN | 144.7717
273.176 | 125.8229 | NaN | 144.7123
274.176 | 126.1952 | NaN | 144.7741
275.176 | 126.4359 | NaN | 144.9293
276.176 | 126.6186 | NaN | 144.6125
277.176 | 127.2614 | NaN | 144.2308
278.176 | 127.4664 | NaN | 143.8447
279.176 | 127.7222 | NaN | 143.5247
280.176 | 127.9617 | NaN | 143.6122
281.176 | 128.1112 | NaN | 143.8766
282.176 | 128.5772 | NaN | 144.299
283.176 | 128.2361 | NaN | 144.2306
284.176 | 128.2545 | NaN | 144.9853
285.176 | 128.3694 | NaN | 145.0619
286.176 | 128.6168 | NaN | 145.501
287.176 | 129.0409 | NaN | 146.0213
288.176 | 129.0779 | NaN | 146.1613
289.176 | 128.9949 | NaN | 146.3826
290.176 | 129.0918 | NaN | 146.252
291.176 | 129.1016 | NaN | 146.2933
292.176 | 128.7734 | NaN | 146.4982
293.176 | 128.6227 | NaN | 146.3191
294.176 | 128.5736 | NaN | 146.1194
295.176 | 128.7575 | NaN | 146.2124
296.176 | 128.6545 | NaN | 146.1918
297.176 | 128.6518 | NaN | 146.2296
298.176 | 128.9178 | NaN | 146.1539
299.176 | 129.9892 | NaN | 146.2582
300.176 | 130.2687 | NaN | 146.4718
301.176 | 130.4086 | NaN | 146.3259
302.176 | 130.5292 | NaN | 146.7061
303.176 | 130.5352 | NaN | 146.8801
304.176 | 130.5356 | NaN | 146.9084
305.176 | 130.3645 | NaN | 147.0336
306.176 | 131.0024 | NaN | 147.1991
307.176 | 131.2755 | NaN | 147.3707
308.176 | 131.3123 | NaN | 147.3032
309.176 | 131.2092 | NaN | 147.1986
310.176 | 131.2371 | NaN | 147.4164
311.176 | 131.4315 | NaN | 147.3465
312.176 | 132.0969 | NaN | 147.44
313.176 | 132.4511 | NaN | 147.4352
314.176 | 132.4231 | NaN | 147.5565
315.176 | 132.7638 | NaN | 147.5021
316.176 | 133.1143 | NaN | 148.0363
317.176 | 132.8646 | NaN | 147.6995
318.176 | 132.8606 | NaN | 147.5123
319.176 | 132.8559 | NaN | 147.7634
320.176 | 133.1292 | NaN | 147.8028
321.176 | 133.5781 | NaN | 147.9997
322.176 | 133.5781 | NaN | 147.7591
323.176 | 133.5359 | NaN | 148.0881
324.176 | 132.8825 | NaN | 148.0162
325.176 | 132.6614 | NaN | 148.3214
326.176 | 132.4735 | NaN | 148.4861
327.176 | 132.4723 | NaN | 148.5102
328.176 | 132.5541 | NaN | 148.3697
329.176 | 132.4858 | NaN | 148.177
330.176 | 132.7976 | NaN | 148.3218
331.176 | 133.2619 | NaN | 148.3313
332.176 | 133.0088 | NaN | 148.4178
333.176 | 132.8472 | NaN | 148.5075
334.176 | 132.7723 | NaN | 148.6297
335.176 | 133.2969 | NaN | 148.8287
336.176 | 133.7893 | NaN | 149.1559
337.176 | 133.8608 | NaN | 149.5116
338.176 | 133.8332 | NaN | 149.656
339.176 | 133.9131 | NaN | 150.2714
340.176 | 133.8034 | NaN | 150.4116
341.176 | 133.6373 | NaN | 150.2876
342.176 | 133.8512 | NaN | 150.1537
343.176 | 133.8263 | NaN | 150.1372
344.176 | 133.756 | NaN | 150.1253
345.176 | 133.6439 | NaN | 149.9933
346.176 | 133.6343 | NaN | 150.0128
347.176 | 133.7641 | NaN | 149.9826
348.176 | 133.8186 | NaN | 149.7442
349.176 | 133.7407 | NaN | 149.4365
350.176 | 133.6321 | NaN | 149.239
351.176 | 133.7822 | -19.4955 | 149.0918
352.176 | 134.0821 | -18.4544 | 149.1135
353.176 | 134.2771 | -17.6767 | 149.1341
354.176 | 134.5792 | -17.29 | 149.1535
355.176 | 135.0353 | -17.4058 | 149.0068
356.176 | 135.2714 | -17.7407 | 149.4519
357.176 | 135.5167 | -17.7146 | 149.5425
358.176 | 136.0732 | -17.0348 | 149.7215
359.176 | 136.0724 | -15.9106 | 149.7683
360.176 | 136.0536 | -15.2558 | 149.8507
361.176 | 136.3189 | -15.1494 | 150.4343
362.176 | 136.8426 | -15.852 | 150.5935
363.176 | 136.844 | -15.1649 | 151.204
364.176 | 136.7025 | -15.0099 | 151.0613
365.176 | 136.7359 | -13.5778 | 151.0743
366.176 | 136.3089 | -13.5151 | 150.9898
367.176 | 136.0501 | -13.8685 | 151.0185
368.176 | 136.0022 | -14.4886 | 151.1155
369.176 | 135.6981 | -14.8974 | 150.9246
370.176 | 135.3872 | -15.1525 | 150.4985
371.176 | 135.5205 | -15.1562 | 150.3032
372.176 | 135.2403 | -15.0485 | 150.3901
373.176 | 135.5783 | -14.9093 | 150.302
374.176 | 135.4511 | -15.1313 | 150.5951
375.176 | 135.2858 | -14.8709 | 150.9001
376.176 | 135.1311 | -14.4509 | 150.6013
377.176 | 135.453 | -14.0076 | 150.5191
378.176 | 135.4805 | -14.2519 | 150.2812
379.176 | 135.496 | -14.7653 | 150.1121
380.176 | 135.6792 | -15.0908 | 149.9166
381.176 | 135.4094 | -15.2128 | 150.5204
382.176 | 135.3915 | -15.4115 | 150.5019
383.176 | 135.5102 | -14.7474 | 150.6713
384.176 | 135.8639 | -14.4938 | 150.8257
385.176 | 135.8376 | -14.2645 | 150.9515
386.176 | 135.5649 | -14.447 | 150.9145
387.176 | 135.6776 | -14.4657 | 151.0007
388.176 | 135.8327 | -14.6457 | 150.885
389.176 | 135.9719 | -14.9622 | 150.908
390.176 | 136.0524 | -14.8455 | 151.0659
391.176 | 137.1563 | -14.9668 | 151.4045
392.176 | 137.8992 | -14.599 | 151.7016
393.176 | 137.9734 | -14.513 | 151.771
394.176 | 137.9749 | -13.7808 | 151.6365
395.176 | 138.2087 | -13.5671 | 151.9299
396.176 | 138.0579 | -13.4343 | 151.9561
397.176 | 138.5251 | -12.3926 | 152.1374
398.176 | 139.0207 | -11.7793 | 152.4006
399.176 | 139.6354 | -11.6164 | 152.2665
400.176 | 139.7406 | -11.1618 | 152.3441
401.176 | 139.6473 | -11.5655 | 152.4067
402.176 | 139.7421 | -11.8965 | 152.555
403.176 | 139.5943 | -11.7706 | 152.6562
404.176 | 139.5436 | -11.5736 | 152.8321
405.176 | 139.6311 | -11.811 | 153.0916
406.176 | 139.3796 | -11.7982 | 153.2956
407.176 | 139.1354 | -11.6914 | 153.3296
408.176 | 139.0091 | -11.0325 | 153.6902
409.176 | 139.325 | -10.4631 | 153.994
410.176 | 139.5808 | -10.7769 | 154.1053
411.176 | 139.5382 | -11.1857 | 153.9436
412.176 | 140.0139 | -11.6668 | 153.7375
413.176 | 140.3947 | -11.394 | 153.79
414.176 | 140.8195 | -11.1091 | 153.6621
415.176 | 141.4475 | -11.3313 | 153.2815
416.176 | 141.6053 | -11.5807 | 153.6806
417.1917 | 141.5726 | -11.7165 | 154.047
418.176 | 141.5667 | -11.5993 | 154.2264
419.176 | 141.6928 | -11.6549 | 154.4932
420.1917 | 141.2845 | -11.6916 | 154.2786
421.176 | 140.873 | -11.8519 | 153.9858
422.176 | 140.8379 | -11.8384 | 153.8568
423.1917 | 140.746 | -10.6843 | 153.4702
424.1917 | 140.5526 | -9.7397 | 153.5811
425.176 | 140.6533 | -10.0496 | 153.8642
426.176 | 140.4063 | -10.1601 | 153.7421
427.176 | 140.3306 | -10.6703 | 153.6036
428.176 | 139.9044 | -10.8233 | 153.8097
429.176 | 139.7478 | -10.6222 | 153.8588
430.176 | 139.6422 | -10.0916 | 153.8732
431.176 | 139.728 | -10.2275 | 153.9437
432.176 | 139.6205 | -10.5276 | 154.0965
433.176 | 139.6005 | -10.8655 | 154.7269
434.176 | 139.8183 | -10.6585 | 155.2104
435.176 | 139.3698 | -10.5686 | 155.2182
436.176 | 139.3104 | -10.5248 | 155.1382
437.1917 | 139.3363 | -9.7981 | 155.2274
438.176 | 139.4293 | -7.1211 | 155.1125
439.176 | 139.5051 | -6.2252 | 154.9426
440.176 | 139.561 | -6.1376 | 155.3797
441.176 | 139.5262 | -5.7434 | 155.7026
442.176 | 139.5679 | -5.3651 | 155.9848
443.176 | 140.0195 | -5.4811 | 156.3267
444.176 | 140.2986 | -5.1621 | 156.2908
445.176 | 139.994 | -4.8041 | 156.9434
446.176 | 140.2479 | -4.6256 | 157.0674
447.176 | 140.333 | -4.8845 | 157.0778
448.176 | 141.0352 | -5.1891 | 156.9317
449.176 | 141.4678 | -5.8269 | 156.964
450.176 | 141.3238 | -6.2308 | 157.2503
451.176 | 141.3926 | -6.2996 | 157.484
452.176 | 141.5053 | -6.4416 | 157.5252
453.176 | 142.0084 | -6.6922 | 157.6372
454.176 | 142.2333 | -6.3767 | 157.6489
455.176 | 142.3697 | -6.1021 | 157.9986
456.176 | 142.3786 | -6.2124 | 158.3423
457.176 | 142.1416 | -6.2369 | 158.5784
458.176 | 141.4502 | -6.3898 | 158.6425
459.176 | 141.3596 | -6 | 158.425
460.176 | 141.5559 | -5.537 | 158.7188
461.176 | 141.7745 | -5.4729 | 158.7964
462.176 | 141.7848 | -5.5268 | 158.7105
463.176 | 141.3862 | -5.5653 | 159.5652
464.176 | 141.5196 | -4.0723 | 159.4591
465.176 | 141.7147 | -2.8482 | 159.1584
466.176 | 141.8628 | -3.0162 | 159.383
467.176 | 141.9443 | -3.0649 | 159.3885
468.176 | 141.7001 | -2.5772 | 159.1698
469.176 | 141.9109 | -2.7233 | 158.9206
470.176 | 142.1241 | -2.8597 | 158.7911
471.176 | 142.6632 | -2.8711 | 158.7107
472.176 | 142.9191 | -2.4784 | 158.6792
473.176 | 142.2065 | -1.4155 | 158.6849
474.176 | 141.8941 | -1.8371 | 158.6388
475.1917 | 141.9393 | -2.353 | 158.4559
476.176 | 141.9056 | -2.6766 | 158.3184
477.176 | 142.3254 | -2.8855 | 158.5546
478.176 | 142.6102 | -2.9578 | 158.7615
479.176 | 142.818 | -2.7984 | 158.9396
480.1917 | 142.9845 | -2.5349 | 158.8389
481.1917 | 143.0371 | -3.1238 | 158.7328
482.176 | 142.794 | -2.69 | 158.6374
483.176 | 142.1805 | -3.4298 | 158.599
484.176 | 141.9 | -3.9193 | 158.3819
485.176 | 141.9704 | -3.0101 | 158.383
486.176 | 141.9793 | -3.1519 | 158.4225
487.176 | 141.8272 | -3.5432 | 158.6077
488.176 | 142.3038 | -3.7683 | 158.3288
489.176 | 142.2414 | -3.2747 | 158.6161
490.176 | 142.3115 | -2.7347 | 159.645
491.176 | 142.2247 | -1.9078 | 160.1093
492.176 | 141.9155 | -1.4862 | 160.7007
493.176 | 142.0395 | -1.0413 | 160.6963
494.176 | 142.748 | -0.9252 | 160.4683
495.176 | 143.1857 | -1.0616 | 160.5675
496.176 | 143.3942 | -0.8214 | 160.4156
497.176 | 143.2603 | -1.1747 | 160.0861
498.176 | 142.7472 | -1.6811 | 160.0444
499.176 | 142.6387 | -1.6691 | 159.8101
500.176 | 142.7605 | -1.9378 | 159.5788
501.176 | 143.5521 | -1.5853 | 159.295
502.176 | 143.3197 | -1.4617 | 158.9237
503.176 | 143.2373 | -1.0739 | 158.673
504.176 | 143.3043 | -0.6567 | 158.6938
505.176 | 143.5887 | -0.2318 | 159.1181
506.176 | 143.558 | 0.8496 | 159.4487
507.176 | 143.5312 | 1.6835 | 159.4728
508.176 | 143.6097 | 2.8258 | 159.5633
509.176 | 143.8003 | 2.1583 | 159.2308
510.176 | 144.0284 | 1.7622 | 159.0375
511.176 | 144.2032 | 1.0838 | 159.1017
512.176 | 144.3943 | 0.7848 | 159.2141
513.176 | 144.426 | 1.1019 | 159.4713
514.176 | 144.1413 | 1.2237 | 159.41
515.176 | 144.1939 | 1.2175 | 159.2345
516.176 | 144.5043 | 2.2208 | 159.3949
517.176 | 144.6598 | 2.6149 | 159.2687
518.176 | 144.5539 | 1.9877 | 159.582
519.176 | 144.2296 | 1.0688 | 159.4651
520.176 | 144.0194 | 0.9031 | 159.3469
521.176 | 143.8205 | 0.1911 | 159.1632
522.176 | 143.7777 | -0.6325 | 159.2385
523.176 | 143.966 | 0.154 | 158.9363
524.176 | 143.9982 | -0.0704 | 158.6668
525.176 | 143.6851 | -0.0659 | 158.5488
526.176 | 143.3351 | -0.2672 | 158.344
527.176 | 142.8723 | -0.0649 | 158.0851
528.176 | 142.9107 | -0.3711 | 157.9156
529.176 | 143.2714 | -0.5584 | 158.191
530.176 | 143.5803 | -0.272 | 158.1791
531.176 | 143.6527 | -0.214 | 158.2974
532.176 | 143.5704 | -0.0255 | 158.4652
533.176 | 143.7632 | -0.456 | 159.1849
534.176 | 143.8363 | -0.3658 | 159.797
535.176 | 144.0446 | 0.1903 | 159.8456
536.176 | 144.7118 | 0.5233 | 159.8112
537.176 | 144.7444 | 2.1443 | 159.8534
538.176 | 144.5326 | 2.5537 | 159.7405
539.176 | 144.6681 | 3.0166 | 159.4988
540.176 | 145.1034 | 3.9489 | 159.4136
541.176 | 145.5252 | 3.9222 | 158.9902
542.176 | 145.4128 | 3.2243 | 159.0607
543.176 | 145.1324 | 2.9534 | 158.9353
544.176 | 144.9156 | 2.1677 | 158.8148
545.176 | 145.0454 | 2.1851 | 158.736
546.176 | 144.9871 | 1.3605 | 158.6352
547.176 | 144.9011 | 0.6797 | 158.9213
548.176 | 145.145 | 0.62 | 159.0654
549.176 | 145.0962 | 0.6552 | 159.1031
550.176 | 145.2395 | 0.5877 | 159.0222
551.176 | 145.2704 | 0.761 | 158.79
552.176 | 145.0257 | 0.5788 | 159.167
553.176 | 144.6845 | 0.9103 | 159.2366
554.176 | 144.753 | 0.6202 | 159.3625
555.176 | 144.7493 | 1.1111 | 159.5675
556.176 | 144.9243 | 0.6068 | 159.6582
557.176 | 144.4738 | 0.5829 | 160.272
558.176 | 144.1672 | 3.4097 | 160.4827
559.176 | 144.2447 | 4.0768 | 160.6503
560.176 | 144.2745 | 4.0126 | 161.1507
561.176 | 143.687 | 3.4809 | 161.1047
562.176 | 143.3719 | 3.5982 | 160.8097
563.176 | 143.2514 | 2.8669 | 160.5193
564.176 | 143.2428 | 2.872 | 160.6302
565.176 | 143.017 | 2.2134 | 160.6972
566.176 | 142.9332 | 2.3165 | 160.3489
567.176 | 142.8707 | 3.8417 | 160.1238
568.176 | 143.1049 | 4.8378 | 159.8466
569.176 | 143.6285 | 6.5119 | 159.6701
570.176 | 143.3793 | 6.7528 | 159.9708
571.176 | 143.431 | 6.8712 | 159.9075
572.176 | 144.0245 | 7.1067 | 159.8458
573.176 | 144.182 | 6.364 | 160.1246
574.176 | 144.4357 | 5.3441 | 160.1386
575.176 | 144.0958 | 4.7185 | 160.2486
576.176 | 144.2949 | 4.1765 | 160.1835
577.176 | 144.5138 | 4.1677 | 159.9555
578.176 | 144.6642 | 4.9326 | 159.7433
579.176 | 144.1604 | 4.3232 | 159.7646
580.176 | 144.2315 | 4.0641 | 159.9721
581.176 | 144.6055 | 3.2246 | 160.1471
582.176 | 144.4577 | 4.1009 | 160.1412
583.176 | 144.4854 | 5.5463 | 160.3379
584.176 | 144.2311 | 4.7012 | 160.3406
585.176 | 144.4611 | 3.6988 | 160.4563
586.176 | 144.5999 | 3.2317 | 160.3091
587.176 | 144.9589 | 3.19 | 160.4266
588.176 | 145.3362 | 3.4297 | 160.4626
589.176 | 145.4346 | 3.4547 | 160.1703
590.176 | 145.4809 | 2.8214 | 160.1159
591.176 | 145.6317 | 3.502 | 159.7676
592.176 | 145.6055 | 4.0758 | 159.6916
593.176 | 145.6592 | 3.9813 | 159.7394
594.176 | 145.4891 | 3.327 | 159.6805
595.176 | 145.4224 | 3.1271 | 159.6051
596.176 | 145.5732 | 3.4452 | 159.7373
597.176 | 145.7615 | 3.4243 | 159.5863
598.176 | 145.3294 | 3.7807 | 159.262
599.176 | 145.0447 | 4.0166 | 159.4361
600.176 | 145.4019 | 5.0563 | 159.6123
601.176 | 145.6234 | 5.654 | 159.6916
602.176 | 145.7797 | 5.4219 | 159.8787
603.176 | 146.1116 | 4.5541 | 160.0301
604.176 | 146.4323 | 3.831 | 160.0302
605.176 | 146.8073 | 4.01 | 160.2652
606.176 | 147.1039 | 3.796 | 160.3777
607.176 | 147.134 | 4.1466 | 160.3217
608.176 | 147.1765 | 3.3214 | 160.3623
609.176 | 147.4037 | 3.6571 | 161.0189
610.176 | 147.1325 | 3.3132 | 161.0851
611.176 | 147.3181 | 3.0582 | 160.8601
612.176 | 147.435 | 2.2809 | 160.639
613.176 | 147.08 | 1.9089 | 161.0406
614.176 | 146.5928 | 1.736 | 161.1019
615.176 | 146.6196 | 1.8959 | 161.1463
616.176 | 146.6664 | 2.1183 | 161.1334
617.176 | 146.2976 | 1.2757 | 161.4386
618.176 | 146.0856 | 0.2743 | 161.4378
619.176 | 146.1649 | -0.4624 | 161.5625
620.176 | 146.5415 | -0.7341 | 161.5645
621.176 | 146.5685 | -1.1902 | 161.5063
622.176 | 146.5817 | -1.4734 | 161.5422
623.176 | 146.9109 | -1.6874 | 161.5391
624.176 | 146.6637 | -1.5972 | 161.5248
625.176 | 146.0813 | -1.5716 | 161.4802
626.176 | 145.8271 | -0.8881 | 161.3753
627.176 | 145.8901 | -0.3644 | 161.3243
628.176 | 145.9714 | 0.2101 | 161.0603
629.176 | 145.9657 | -0.0654 | 161.4048
630.176 | 146.6338 | -0.322 | 161.2861
631.176 | 147.0325 | -0.2102 | 161.3235
632.176 | 147.1467 | 0.0856 | 161.0594
633.176 | 147.1327 | -0.2215 | 160.7954
634.176 | 146.9556 | -0.1099 | 160.9529
635.176 | 146.6539 | -0.2782 | 161.0034
636.176 | 146.6757 | -0.6971 | 160.9725
637.176 | 146.5133 | -0.1815 | 160.9091
638.176 | 146.3282 | 0.5106 | 160.8659
639.176 | 146.4436 | 0.7398 | 160.5446
640.176 | 146.3592 | 0.6789 | 160.5158
641.176 | 146.2862 | 0.1829 | 160.4691
642.176 | 146.495 | -0.2875 | 160.5922
643.176 | 146.6875 | -0.7693 | 160.7535
644.176 | 146.8699 | -1.1371 | 160.9777
645.1917 | 146.8558 | -0.6344 | 160.7557
646.176 | 146.8905 | -0.4287 | 160.713
647.176 | 147.0088 | -0.2843 | 160.8255
648.176 | 147.931 | -0.5459 | 160.875
649.176 | 147.928 | -0.5704 | 160.75
650.176 | 148.0792 | 0.0817 | 161.1393
651.176 | 148.1177 | 1.2398 | 161.2346
652.176 | 147.4658 | 1.9511 | 161.2209
653.176 | 147.1558 | 2.0463 | 161.218
654.176 | 147.3559 | 2.5375 | 161.7944
655.176 | 147.5908 | 2.6282 | 162.2171
656.176 | 147.9305 | 5.544 | 162.3025
657.176 | 147.9819 | 5.8792 | 162.1695
658.176 | 147.8869 | 6.5114 | 161.9889
659.176 | 147.9356 | 7.1936 | 161.9922
660.176 | 148.7203 | 7.6021 | 162.1687
661.176 | 149.3911 | 7.2891 | 162.2016
662.176 | 149.6956 | 9.0867 | 162.2119
663.176 | 149.6757 | 9.8542 | 162.3035
664.176 | 150.2764 | 9.5931 | 162.4978
665.176 | 151.2144 | 9.7039 | 162.8537
666.176 | 151.0799 | 9.8696 | 162.6981
667.176 | 151.0181 | 11.0512 | 162.8856
668.176 | 150.8987 | 11.8308 | 163.1059
669.176 | 150.881 | 11.4059 | 163.4006
670.176 | 150.257 | 10.593 | 163.6347
671.176 | 150.3048 | 11.2259 | 163.9461
672.176 | 150.3064 | 11.2039 | 163.8782
673.176 | 150.5227 | 10.8991 | 163.8394
674.176 | 150.8746 | 11.1582 | 163.6452
675.176 | 150.9386 | 11.2384 | 164.2756
676.176 | 150.5441 | 10.7936 | 164.5998
677.176 | 150.5424 | 11.093 | 164.5764
678.176 | 150.5373 | 11.0795 | 164.6717
679.176 | 150.672 | 12.9469 | 164.8149
680.176 | 150.8342 | 13.407 | 164.8706
681.176 | 151.1949 | 14.2107 | 164.5536
682.176 | 151.2571 | 14.6454 | 164.6585
683.176 | 151.3252 | 14.3893 | 164.7909
684.176 | 151.3344 | 14.0552 | 164.5169
685.176 | 151.1312 | 13.8985 | 164.5777
686.176 | 150.9072 | 14.1865 | 164.8249
687.176 | 150.831 | 13.5678 | 164.9252
688.176 | 151.1283 | 13.7781 | 165.481
689.176 | 151.4872 | 14.5623 | 165.7641
690.176 | 151.4385 | 14.8931 | 165.6868
691.176 | 151.5717 | 15.2961 | 165.3769
692.176 | 151.3149 | 15.7065 | 165.0091
693.176 | 151.1274 | 15.0887 | 165.1835
694.176 | 151.0378 | 15.0272 | 165.4461
695.176 | 150.7847 | 14.9663 | 165.6447
696.176 | 150.7223 | 14.8896 | 165.8803
697.176 | 150.6257 | 13.9301 | 166.2281
698.176 | 150.7326 | 13.3753 | 166.2017
699.176 | 151.2362 | 12.9049 | 166.8961
700.176 | 151.2021 | 13.2237 | 166.7423
701.176 | 151.3424 | 13.714 | 166.8073
702.176 | 151.6791 | 16.0285 | 166.9072
703.176 | 151.7796 | 16.449 | 167.3179
704.176 | 151.8439 | 16.4031 | 167.4394
705.176 | 152.157 | 15.8114 | 167.6707
706.176 | 152.7277 | 15.3283 | 167.8133
707.176 | 153.309 | 16.7098 | 168.2862
708.176 | 154.0417 | 17.3488 | 168.4641
709.176 | 154.5278 | 17.7227 | 168.35
710.176 | 154.5197 | 17.7227 | 168.1584
711.176 | 154.6279 | 18.3362 | 168.3349
712.176 | 154.6432 | 18.0021 | 168.1212
713.176 | 154.2802 | 17.3109 | 168.3179
714.176 | 154.4835 | 16.0338 | 168.2155
715.176 | 154.6057 | 16.1042 | 168.7053
716.176 | 154.1363 | 15.3187 | 168.5536
717.176 | 153.812 | 15.9128 | 168.5382
718.176 | 153.8149 | 16.0802 | 168.2855
719.176 | 154.0873 | 16.2124 | 168.5229
720.176 | 153.5256 | 15.5281 | 168.4523
721.176 | 153.7932 | 15.3665 | 168.5219
722.176 | 153.7546 | 14.7919 | 168.5142
723.176 | 153.8867 | 15.7322 | 168.7794
724.176 | 154.0013 | 16.3187 | 169.0922
725.176 | 154.3011 | 16.2398 | 169.2037
726.176 | 153.7479 | 15.763 | 168.8925
727.176 | 153.7177 | 15.0365 | 169.2074
728.176 | 153.9832 | 15.0315 | 169.4562
729.176 | 154.1784 | 16.0006 | 169.4911
730.176 | 154.0353 | 16.1216 | 169.3346
731.176 | 154.0582 | 16.6322 | 169.1613
732.176 | 154.3435 | 17.1107 | 169.3416
733.176 | 154.0507 | 16.9839 | 169.473
734.176 | 154.0416 | 17.1321 | 169.5378
735.176 | 154.1333 | 16.6689 | 169.6483
736.176 | 154.0776 | 16.0842 | 169.516
737.176 | 154.4699 | 16.1317 | 169.0287
738.176 | 154.4192 | 16.0962 | 168.6571
739.176 | 154.0779 | 15.4148 | 168.4453
740.176 | 153.985 | 15.6311 | 168.7618
741.176 | 153.9607 | 14.913 | 169.2061
742.176 | 154.0947 | 14.5553 | 169.1939
743.176 | 153.646 | 14.3414 | 169.39
744.176 | 153.5532 | 14.9445 | 169.5761
745.176 | 154.0067 | 16.317 | 169.7777
746.176 | 154.1546 | 17.1241 | 169.5095
747.176 | 153.495 | 16.7663 | 169.8055
748.176 | 153.6184 | 16.8211 | 170.1184
749.176 | 153.4453 | 16.3831 | 170.2226
750.176 | 153.4453 | 16.0054 | 170.098
751.176 | 153.7601 | 16.6109 | 169.9226
752.176 | 154.1796 | 17.1041 | 170.0148
753.176 | 153.8754 | 18.7527 | 170.2294
754.176 | 153.7351 | 18.2217 | 170.4276
755.176 | 153.3309 | 18.3689 | 170.3595
756.176 | 153.3298 | 18.7803 | 170.4427
757.176 | 153.6526 | 18.9576 | 170.3852
758.176 | 153.6954 | 19.9344 | 170.6362
759.176 | 153.5652 | 21.1331 | 170.5304
760.176 | 153.6355 | 21.9252 | 170.3255
761.176 | 153.948 | 22.1169 | 170.2681
762.176 | 154.1167 | 22.0208 | 170.3182
763.176 | 154.4274 | 22.2755 | 170.5815
764.176 | 154.7562 | 26.1173 | 170.7307
765.176 | 155.0224 | 26.09 | 170.831
766.176 | 155.1182 | 25.2321 | 171.3236
767.176 | 155.3416 | 24.7544 | 171.5971
768.176 | 156.0526 | 24.1327 | 171.4498
769.176 | 156.2238 | 24.249 | 171.3144
770.176 | 156.1553 | 24.655 | 171.3286
771.176 | 156.0913 | 26.4019 | 171.2427
772.176 | 156.1981 | 26.8421 | 171.1848
773.176 | 156.0166 | 26.6905 | 171.0825
774.176 | 156.142 | 27.6947 | 171.1728
775.176 | 156.425 | 28.8246 | 171.4302
776.176 | 155.7891 | 29.1262 | 171.5158
777.176 | 155.3429 | 30.2547 | 171.3191
778.176 | 155.5166 | 31.9079 | 171.4304
779.176 | 155.22 | 32.6447 | 171.6356
780.176 | 155.4996 | 32.6857 | 171.7447
781.176 | 155.4329 | 35.8566 | 171.8801
782.176 | 154.9421 | 34.8927 | 172.2089
783.176 | 155.308 | 33.9434 | 172.7552
784.176 | 156.0238 | 32.8688 | 172.8322
785.176 | 155.9975 | 32.2024 | 172.7827
786.176 | 155.8818 | 31.2637 | 172.7795
787.176 | 155.9016 | 30.8126 | 172.8714
788.176 | 156.2875 | 30.6764 | 173.0465
789.176 | 156.3419 | 30.545 | 173.1186
790.176 | 156.2712 | 32.2182 | 173.3528
791.176 | 156.8793 | 32.7962 | 173.3217
792.176 | 157.1404 | 32.9034 | 173.6883
793.176 | 157.5854 | 34.8722 | 173.3061
794.176 | 158.0064 | 35.6715 | 173.14
795.176 | 158.0261 | 34.6389 | 173.1193
796.176 | 158.2774 | 33.795 | 173.2454
797.176 | 158.3113 | 35.736 | 173.0811
798.176 | 157.6449 | 37.8872 | 173.2675
799.176 | 158.0358 | 39.2693 | 173.2125
800.176 | 158.5455 | 38.7689 | 172.7119
801.176 | 158.8691 | 37.7178 | 172.4616
802.176 | 158.6677 | 36.6296 | 172.4231
803.176 | 158.7203 | 35.5313 | 172.2296
804.176 | 159.0871 | 35.1615 | 172.2391
805.176 | 159.3745 | 36.1164 | 172.2004
806.176 | 159.5094 | 36.5542 | 172.3145
807.176 | 159.3727 | 37.4052 | 172.1533
808.176 | 159.6547 | 36.3453 | 171.9262
809.176 | 159.8486 | 35.6878 | 172.2133
810.176 | 160.1961 | 35.8701 | 172.4581
811.176 | 160.5646 | 37.0032 | 172.8917
812.176 | 160.7888 | 36.6333 | 173.0026
813.176 | 161.1391 | 36.0623 | 173.0979
814.176 | 161.6281 | 35.5678 | 173.7707
815.176 | 161.9583 | 36.3524 | 174.4438
816.176 | 161.3467 | 36.9031 | 174.4175
817.176 | 161.2177 | 37.0075 | 174.2917
818.176 | 161.2315 | 38.0951 | 174.1529
819.176 | 161.1125 | 38.0287 | 174.2148
820.176 | 161.2305 | 38.144 | 174.7813
821.176 | 161.4688 | 37.7509 | 174.8992
822.176 | 161.5869 | 36.9722 | 175.1052
823.176 | 161.874 | 38.346 | 175.2252
824.176 | 161.9122 | 39.2543 | 175.6535
825.176 | 161.9608 | 38.9156 | 175.5608
826.176 | 162.5464 | 40.0327 | 175.3775
827.176 | 163.318 | 41.6728 | 175.5074
828.176 | 162.832 | 42.0254 | 175.7943
829.176 | 162.6393 | 42.8252 | 175.6228
830.176 | 162.854 | 43.6632 | 176.0013
831.176 | 162.4905 | 42.9951 | 176.0434
832.176 | 162.5659 | 42.461 | 176.1849
833.176 | 162.9737 | 42.6336 | 176.4457
834.176 | 162.7595 | 43.1168 | 176.4222
835.176 | 162.2694 | 43.3492 | 176.6954
836.176 | 162.4204 | 42.226 | 177.3228
837.176 | 162.6746 | 41.6587 | 177.5916
838.176 | 162.6027 | 42.6747 | 177.6044
839.176 | 162.9946 | 42.7116 | 177.733
840.176 | 163.3368 | 42.5297 | 177.8925
841.176 | 163.4141 | 42.4921 | 178.1456
842.176 | 163.8719 | 42.3452 | 178.0981
843.176 | 163.7398 | 42.5425 | 177.7486
844.176 | 163.8709 | 44.2801 | 177.5849
845.176 | 163.976 | 44.5195 | 177.2385
846.176 | 163.7197 | 45.3336 | 177.267
847.176 | 163.8391 | 45.8429 | 177.2897
848.176 | 164.6413 | 48.111 | 177.5273
849.176 | 164.8404 | 48.9917 | 177.9321
850.176 | 165.1758 | 49.8108 | 178.3227
851.176 | 165.3389 | 49.4413 | 178.9903
852.176 | 165.7872 | 52.3607 | 178.9337
853.176 | 166.0441 | 53.4997 | 179.1392
854.176 | 166.4078 | 53.9283 | 179.4556
855.176 | 166.3063 | 54.3362 | 179.4056
856.176 | 166.1003 | 53.0501 | 179.2623
857.176 | 165.9918 | 52.2605 | 179.0467
858.176 | 166.2623 | 53.2179 | 178.9563
859.176 | 166.1832 | 55.5654 | 179.798
860.176 | 165.6669 | 54.3944 | 179.8253
861.176 | 165.7 | 54.0288 | 179.8509
862.176 | 165.7869 | 54.1357 | 179.9458
863.176 | 166.3103 | 55.1184 | 180.2073
864.176 | 166.719 | 54.9509 | 180.5835
865.176 | 167.0507 | 55.4895 | 180.5761
866.176 | 167.0349 | 56.1708 | 180.3892
867.176 | 167.25 | 57.6549 | 179.8242
868.176 | 167.4766 | 61.4176 | 179.5698
869.176 | 167.508 | 60.7455 | 179.3314
870.176 | 167.0066 | 61.5715 | 179.1969
871.176 | 166.6963 | 61.4293 | 179.2166
872.176 | 166.6078 | 61.566 | 179.3138
873.176 | 166.7105 | 62.9113 | 179.4688
874.176 | 166.8619 | 63.5375 | 179.7149
875.176 | 167.1564 | 63.3357 | 179.8442
876.176 | 167.1546 | 63.8088 | 179.8419
877.176 | 166.7481 | 64.6068 | 179.6169
878.176 | 166.5904 | 67.535 | 180.1435
879.176 | 167.1174 | 65.5713 | 180.015
880.176 | 167.4195 | 64.2818 | 180.1374
881.176 | 167.8021 | 65.1602 | 180.6605
882.176 | 167.9938 | 66.6187 | 180.7619
883.176 | 168.0163 | 68.0499 | 181.301
884.176 | 168.1315 | 67.2267 | 181.4936
885.176 | 168.257 | 69.172 | 181.6707
886.176 | 168.1584 | 69.1287 | 182.026
887.176 | 168.4975 | 68.1179 | 181.651
888.176 | 168.2696 | 67.2392 | 181.5534
889.176 | 167.9653 | 67.4037 | 181.4514
890.176 | 167.0318 | 66.8293 | 181.3141
891.176 | 166.756 | 67.1859 | 181.3202
892.176 | 167.4409 | 67.59 | 181.0567
893.176 | 167.5237 | 70.2582 | 181.3465
894.176 | 167.8336 | 70.0643 | 181.465
895.176 | 168.3449 | 70.9293 | 181.4812
896.176 | 168.4515 | 71.8917 | 181.613
897.176 | 168.8384 | 71.6559 | 181.5323
898.176 | 169.0919 | 72.9596 | 181.895
899.176 | 169.0401 | 72.7752 | 181.6732
900.176 | 169.3226 | 73.8352 | 181.9006
901.176 | 169.4699 | 75.2092 | 182.1744
902.176 | 169.7335 | 76.9571 | 182.2803
903.176 | 170.263 | 79.5436 | 182.5861
904.176 | 170.6403 | 80.018 | 182.6864
905.176 | 171.1028 | 81.5031 | 183.1363
906.176 | 171.0942 | 81.7006 | 182.8629
907.176 | 171.1054 | 85.2236 | 183.3064
908.176 | 171.8312 | 85.7767 | 183.1574
909.176 | 171.9678 | 87.1706 | 183.3371
910.176 | 171.6189 | 87.1258 | 183.4839
911.176 | 171.4389 | 87.593 | 183.1535
912.176 | 171.4856 | 86.9951 | 182.9734
913.176 | 171.901 | 86.1619 | 183.2411
914.176 | 171.3767 | 85.6946 | 183.1005
915.176 | 171.2078 | 85.301 | 183.2032
916.176 | 171.2714 | 83.4458 | 183.4004
917.176 | 171.3535 | 84.4372 | 183.9203
918.176 | 171.1411 | 85.1368 | 183.905
919.176 | 171.4324 | 84.5445 | 183.9831
920.176 | 170.8356 | 85.975 | 183.6896
921.176 | 170.0157 | 85.642 | 183.8648
922.176 | 169.4515 | 84.7841 | 184.2108
923.176 | 169.4361 | 84.335 | 184.524
924.176 | 169.6514 | 83.417 | 184.6514
925.176 | 169.8274 | 85.1361 | 185.0089
926.176 | 170.6924 | 86.2205 | 185.0329
927.176 | 171.097 | 87.8766 | 185.1576
928.176 | 171.4566 | 87.8269 | 185.3725
929.176 | 171.5555 | 89.4171 | 185.3925
930.176 | 172.0304 | 90.5281 | 185.7826
931.176 | 172.3738 | 89.5355 | 185.7843
932.176 | 172.3814 | 89.1988 | 185.8415
933.176 | 172.5786 | 89.7721 | 185.5413
934.176 | 172.6473 | 90.7804 | 185.3457
935.176 | 172.2205 | 88.6294 | 185.5324
936.176 | 172.487 | 90.8876 | 185.6549
937.176 | 172.3038 | 92.4692 | 185.669
938.176 | 172.5073 | 95.8509 | 185.899
939.176 | 172.9395 | 98.9076 | 185.986
940.176 | 173.4345 | 99.0078 | 186.3708
941.176 | 172.9635 | 97.9533 | 186.5511
942.176 | 173.2522 | 99.7622 | 186.5821
943.176 | 173.1833 | 101.173 | 186.7318
944.176 | 173.2675 | 100.7478 | 186.5912
945.176 | 173.2976 | 98.781 | 186.7285
946.176 | 172.6281 | 96.9847 | 186.8885
947.176 | 172.6777 | 96.855 | 186.8103
948.176 | 172.8098 | 96.7515 | 186.976
949.176 | 172.9711 | 100.2566 | 187.1501
950.176 | 173.3115 | 100.6929 | 187.4675
951.176 | 173.7564 | 99.329 | 187.8544
952.176 | 174.0205 | 99.2505 | 188.4789
953.176 | 174.3948 | 99.3799 | 188.657
954.176 | 174.604 | 99.6337 | 188.7774
955.176 | 175.1213 | 100.8506 | 188.946
956.176 | 175.3801 | 101.3318 | 189.5077
957.176 | 175.6121 | 101.5424 | 189.9012
958.176 | 175.5962 | 105.0886 | 189.401
959.176 | 175.183 | 107.4162 | 189.0648
960.176 | 175.1715 | 106.3776 | 188.7671
961.176 | 175.4421 | 104.4805 | 189.259
962.176 | 175.2353 | 102.8962 | 189.3238
963.176 | 175.0153 | 102.3877 | 189.3031
964.176 | 175.0281 | 103.7404 | 189.7858
965.176 | 174.9082 | 103.5821 | 189.8062
966.176 | 174.992 | 103.6378 | 190.1829
967.176 | 175.182 | 105.024 | 190.4847
968.176 | 175.4692 | 106.879 | 190.572
969.176 | 175.6986 | 107.2484 | 190.6913
970.176 | 176.1279 | 107.1024 | 191.0066
971.176 | 175.7743 | 107.7755 | 191.1574
972.176 | 175.5475 | 110.3 | 190.8097
973.176 | 174.8172 | 111.3132 | 190.6843
974.176 | 175.1475 | 112.002 | 190.6322
975.176 | 175.3055 | 111.4034 | 190.7045
976.176 | 175.7212 | 110.6345 | 191.0716
977.176 | 175.7877 | 111.5818 | 191.7075
978.176 | 175.9749 | 111.7452 | 192.3431
979.176 | 176.4004 | 111.5112 | 192.0986
980.176 | 177.2988 | 111.1832 | 191.9688
981.176 | 176.9109 | 112.0105 | 192.2809
982.176 | 176.6552 | 115.2421 | 192.2715
983.176 | 176.3355 | 116.6337 | 192.3821
984.176 | 176.5115 | 118.5096 | 191.9788
985.176 | 176.4724 | 118.1628 | 191.6756
986.176 | 176.9353 | 116.6202 | 191.6848
987.176 | 177.3528 | 115.7603 | 191.78
988.176 | 177.3073 | 115.4263 | 191.9778
989.176 | 177.4543 | 117.6613 | 191.7436
990.176 | 177.9153 | 116.3424 | 191.7088
991.176 | 178.2641 | 116.4781 | 191.6372
992.176 | 178.9419 | 119.2765 | 191.6383
993.176 | 178.9636 | 120.7604 | 191.9915
994.176 | 179.016 | 119.5584 | 192.2944
995.176 | 179.1615 | 119.1137 | 192.2799
996.176 | 179.584 | 118.0454 | 191.9978
997.176 | 179.4872 | 117.12 | 191.6688
998.176 | 179.6874 | 115.3748 | 192.0094
999.176 | 179.2854 | 115.1464 | 192.0148
1000.176 | 179.4377 | 114.5189 | 192.0745
1001.176 | 179.8653 | 115.3601 | 191.8296
1002.176 | 179.7473 | 117.087 | 192.0598
1003.176 | 180.103 | 117.8852 | 192.3249
1004.176 | 180.4925 | 119.0375 | 192.2258
1005.176 | 180.8442 | 120.7934 | 192.6424
1006.176 | 181.2479 | 123.385 | 192.7408
1007.176 | 181.354 | 129.8748 | 193.4169
1008.176 | 181.0903 | 131.0966 | 193.7415
1009.176 | 181.003 | 130.2976 | 193.712
1010.176 | 180.7952 | 127.8292 | 194.1021
1011.176 | 180.924 | 128.1832 | 193.878
1012.176 | 181.2289 | 128.4243 | 193.6823
1013.176 | 181.042 | 126.2328 | 193.8872
1014.176 | 181.0802 | 125.1756 | 193.9927
1015.176 | 180.8882 | 124.8726 | 194.3649
1016.176 | 180.9987 | 128.3722 | 194.2011
1017.176 | 180.9893 | 127.9518 | 193.834
1018.176 | 180.2913 | 128.54 | 194.0143
1019.176 | 179.8449 | 128.4082 | 193.8384
1020.176 | 179.8341 | 128.2879 | 193.8552
1021.176 | 179.6951 | 129.1296 | 194.1022
1022.176 | 179.8283 | 129.9363 | 194.6644
1023.176 | 178.9479 | 130.5096 | 194.549
1024.176 | 179.0982 | 131.3525 | 194.8582
1025.176 | 179.2632 | 131.6296 | 194.8543
1026.176 | 179.5181 | 131.5725 | 195.2803
1027.176 | 179.4577 | 130.157 | 195.2861
1028.176 | 179.4596 | 128.5842 | 195.1568
1029.176 | 179.6772 | 126.7574 | 195.3084
1030.176 | 180.1045 | 125.9352 | 195.5377
1031.176 | 180.1344 | 125.0547 | 195.7501
1032.176 | 180.4442 | 123.9159 | 196.1755
1033.176 | 180.4402 | 123.0781 | 196.0682
1034.176 | 179.8241 | 122.1295 | 196.5003
1035.176 | 179.938 | 123.0117 | 196.1267
1036.176 | 180.0691 | 121.4956 | 195.9322
1037.176 | 180.2047 | 121.5004 | 195.6434
1038.176 | 179.8712 | 123.7542 | 195.2515
1039.176 | 180.2157 | 124.7185 | 195.1547
1040.176 | 180.6068 | 125.3264 | 195.1337
1041.176 | 180.9424 | 130.3912 | 195.0025
1042.176 | 181.0656 | 131.984 | 195.0626
1043.176 | 181.2721 | 131.834 | 195.1747
1044.176 | 181.2253 | 130.3322 | 195.8939
1045.176 | 181.6632 | 128.9779 | 196.1804
1046.176 | 182.0104 | 126.893 | 196.3274
1047.176 | 182.2519 | 125.8963 | 196.139
1048.176 | 182.1678 | 125.7218 | 196.2532
1049.176 | 182.5099 | 126.3507 | 196.3123
1050.176 | 181.3778 | 127.637 | 196.0451
1051.176 | 181.4223 | 128.8683 | 195.8613
1052.176 | 181.7783 | 130.4117 | 196.1111
1053.176 | 182.0829 | 131.3758 | 196.1931
1054.176 | 182.0263 | 132.5573 | 196.4168
1055.176 | 182.5163 | 134.0841 | 196.5472
1056.176 | 182.9533 | 135.3443 | 196.8791
1057.176 | 182.4371 | 135.1821 | 196.8451
1058.176 | 182.1089 | 135.2676 | 196.8426
1059.176 | 182.2456 | 135.1705 | 196.9682
1060.176 | 182.4727 | 135.0456 | 196.6126
1061.176 | 182.5212 | 134.3664 | 196.4557
1062.176 | 182.3783 | 135.5666 | 196.4311
1063.176 | 181.7595 | 134.0276 | 196.9052
1064.176 | 181.818 | 133.7918 | 197.3049
1065.176 | 181.0729 | 135.3179 | 197.9331
1066.176 | 181.1213 | 138.4339 | 198.2984
1067.176 | 181.4253 | 140.7138 | 198.3259
1068.176 | 181.54 | 144.1852 | 198.3438
1069.176 | 181.8441 | 145.6031 | 198.4512
1070.176 | 182.028 | 145.3062 | 198.5515
1071.1917 | 182.2621 | 143.7639 | 198.5246
1072.176 | 182.5487 | 143.2445 | 198.794
1073.176 | 183.0036 | 141.6415 | 198.6785
1074.176 | 183.1001 | 141.4435 | 198.5872
1075.176 | 183.4072 | 141.0607 | 198.6023
1076.176 | 183.5984 | 140.839 | 198.7852
1077.176 | 183.2289 | 140.3707 | 199.2054
1078.176 | 183.3876 | 147.1299 | 198.8013
1079.176 | 183.8084 | 148.327 | 198.6313
1080.176 | 184.3406 | 146.9108 | 198.5586
1081.176 | 184.089 | 145.0318 | 198.3741
1082.176 | 184.1426 | 142.6212 | 197.8354
1083.176 | 183.9848 | 140.9897 | 198.0506
1084.176 | 184.0838 | 138.3843 | 198.4018
1085.176 | 183.849 | 136.4994 | 198.1326
1086.176 | 183.8518 | 138.2601 | 198.3098
1087.176 | 184.3525 | 138.0517 | 198.3237
1088.176 | 184.4481 | 137.1895 | 198.2633
1089.176 | 184.781 | 136.6691 | 198.2635
1090.176 | 185.3308 | 135.9522 | 198.0551
1091.176 | 186.1345 | 137.5401 | 197.992
1092.176 | 186.2716 | 140.4938 | 197.9266
1093.176 | 186.4362 | 143.3605 | 197.6964
1094.176 | 186.3639 | 144.8417 | 197.6718
1095.176 | 186.5952 | 146.8079 | 197.8458
1096.176 | 185.4361 | 147.1881 | 197.6597
1097.176 | 185.4449 | 146.8706 | 197.3297
1098.176 | 185.7689 | 145.6971 | 197.7228
1099.176 | 185.62 | 143.0655 | 197.9891
1100.176 | 185.3432 | 141.35 | 198.395
1101.1917 | 185.2909 | 140.5109 | 198.5008
1102.176 | 184.994 | 139.8046 | 198.0425
1103.176 | 185.309 | 143.0415 | 198.1824
1104.176 | 185.842 | 142.587 | 197.8642
1105.176 | 186.1297 | 142.2613 | 197.858
1106.176 | 186.2158 | 141.6575 | 197.9951
1107.176 | 186.2731 | 142.1091 | 198.0747
1108.176 | 186.3406 | 143.4299 | 198.3273
1109.176 | 186.2054 | 147.6357 | 198.6218
1110.176 | 186.2135 | 148.1927 | 198.6367
1111.176 | 186.0046 | 147.8441 | 199.1945
1112.176 | 186.2526 | 148.8923 | 199.315
1113.176 | 186.111 | 151.1905 | 199.1845
1114.176 | 186.7245 | 151.2875 | 199.493
1115.176 | 186.6102 | 153.0222 | 199.4173
1116.176 | 186.5691 | 156.7167 | 199.7751
1117.176 | 186.5643 | 157.4175 | 199.6427
1118.176 | 186.6472 | 157.1688 | 199.6125
1119.176 | 186.2913 | 160.3306 | 199.4071
1120.176 | 186.4712 | 157.7763 | 199.6979
1121.176 | 186.7815 | 157.578 | 199.6378
1122.176 | 186.6889 | 157.3023 | 199.6699
1123.176 | 186.6177 | 159.4666 | 199.9473
1124.176 | 186.6768 | 160.9101 | 199.7081
1125.176 | 186.4492 | 165.584 | 199.3
1126.176 | 186.6866 | 163.3959 | 199.1586
1127.176 | 186.79 | 159.7866 | 199.328
1128.176 | 186.8583 | 157.4952 | 199.4531
1129.176 | 186.9188 | 156.0032 | 199.2685
1130.176 | 187.1694 | 155.6719 | 199.6525
1131.176 | 186.8464 | 152.9969 | 199.3216
1132.176 | 186.6814 | 153.6387 | 199.3005
1133.176 | 186.6462 | 154.109 | 199.546
1134.176 | 186.427 | 156.5201 | 199.3734
1135.176 | 186.3414 | 155.8936 | 199.6253
1136.176 | 186.2044 | 155.7758 | 199.6805
1137.176 | 186.128 | 157.5563 | 199.9468
1138.176 | 185.6264 | 163.7093 | 199.8444
1139.176 | 185.5439 | 161.2016 | 199.8819
1140.176 | 185.8789 | 162.3836 | 199.6726
1141.176 | 186.7027 | 162.4066 | 199.3402
1142.176 | 187.3136 | 162.7863 | 199.4714
1143.176 | 186.7236 | 161.5861 | 199.3489
1144.176 | 186.7516 | 162.6116 | 199.4443
1145.176 | 187.1222 | 164.8341 | 199.2481
1146.176 | 187.4187 | 166.8778 | 199.3427
1147.176 | 187.5423 | 169.536 | 199.4026
1148.176 | 187.6237 | 175.5705 | 199.7282
1149.176 | 187.7305 | 177.5503 | 200.2389
1150.176 | 187.8322 | 180.8443 | 200.903
1151.176 | 188.4524 | 183.2231 | 201.2986
1152.176 | 188.7757 | 182.1143 | 201.4704
1153.176 | 188.9147 | 181.1817 | 201.8378
1154.176 | 189.0519 | 178.9488 | 202.0183
1155.176 | 188.722 | 179.537 | 201.8161
1156.176 | 189.1536 | 181.8843 | 201.9754
1157.176 | 189.0589 | 181.5867 | 201.9085
1158.176 | 189.5768 | 182.3761 | 202.0454
1159.176 | 189.4548 | 180.1531 | 202.7157
1160.176 | 189.8027 | 178.9879 | 202.7313
1161.176 | 189.9 | 181.8571 | 203.2138
1162.176 | 190.0098 | 179.8272 | 202.9963
1163.176 | 189.7518 | 177.3012 | 203.0338
1164.176 | 190.0962 | 178.3075 | 202.7826
1165.176 | 190.3886 | 180.3113 | 202.6853
1166.176 | 190.1136 | 178.6011 | 203.0006
1167.176 | 190.2217 | 179.0559 | 202.8373
1168.176 | 190.251 | 180.9435 | 202.9446
1169.176 | 189.8755 | 183.7784 | 203.044
1170.176 | 189.9157 | 185.1919 | 203.3251
1171.176 | 190.3286 | 186.0227 | 203.416
1172.176 | 190.4928 | 186.6685 | 203.2649
1173.176 | 190.9545 | 185.1727 | 202.9628
1174.176 | 191.1112 | 188.2471 | 202.8558
1175.176 | 191.249 | 194.2962 | 202.544
1176.176 | 191.1334 | 196.7109 | 203.0289
1177.176 | 191.2859 | 196.3819 | 202.967
1178.176 | 191.494 | 195.6692 | 203.3823
1179.176 | 191.3846 | 194.5205 | 203.0844
1180.176 | 191.6365 | 194.3716 | 202.872
1181.176 | 192.1378 | 196.4904 | 202.7789
1182.176 | 192.0669 | 199.2584 | 203.125
1183.176 | 192.3223 | 202.5201 | 203.1109
1184.176 | 192.9328 | 202.1327 | 203.1775
1185.176 | 192.9847 | 200.4546 | 203.6823
1186.176 | 193.4433 | 202.4235 | 203.6614
1187.176 | 193.2589 | 203.0422 | 203.1794
1188.176 | 193.1606 | 206.3484 | 203.1453
1189.176 | 193.1792 | 207.1245 | 203.157
1190.176 | 193.1606 | 206.9138 | 203.2925
1191.1917 | 193.0903 | 204.0983 | 203.2445
1192.176 | 193.6503 | 201.948 | 203.4455
1193.176 | 193.7739 | 204.5264 | 203.5287
1194.176 | 193.1676 | 204.6619 | 203.9781
1195.176 | 192.7179 | 207.6185 | 203.9886
1196.176 | 193.0581 | 209.225 | 204.3696
1197.176 | 193.5655 | 213.0069 | 204.666
1198.176 | 193.6118 | 211.1784 | 204.8942
1199.176 | 194.1091 | 211.8318 | 205.7619
1200.176 | 193.6672 | 213.7264 | 206.2368
1201.176 | 193.6984 | 217.6996 | 206.0458
1202.176 | 193.4588 | 222.7865 | 205.5372
1203.176 | 193.5588 | 222.6433 | 205.2762
1204.176 | 192.968 | 220.73 | 205.4132
1205.176 | 192.7079 | 218.5157 | 205.7971
1206.176 | 192.8078 | 215.2507 | 205.9885
1207.176 | 192.8766 | 211.9991 | 206.0722
1208.176 | 192.3921 | 207.6484 | 205.9677
1209.176 | 192.3339 | 205.8589 | 205.6521
1210.176 | 192.5521 | 208.8949 | 205.3764
1211.176 | 193.1694 | 211.7208 | 205.3339
1212.176 | 193.2422 | 208.5311 | 205.2826
1213.176 | 193.3495 | 204.9229 | 205.6196
1214.176 | 193.4976 | 205.1334 | 205.7138
1215.176 | 193.3547 | 205.1932 | 205.6684
1216.176 | 193.5263 | 204.4939 | 205.6832
1217.176 | 193.6182 | 206.3403 | 205.5159
1218.176 | 193.1551 | 205.6688 | 205.7558
1219.176 | 192.4899 | 205.8038 | 205.3922
1220.176 | 192.3896 | 209.2474 | 205.2282
1221.176 | 191.838 | 209.7616 | 204.7896
1222.176 | 191.7928 | 207.7493 | 204.5718
1223.176 | 191.3299 | 205.7653 | 204.5942
1224.176 | 191.282 | 203.1907 | 205.0685
1225.176 | 190.6534 | 200.7243 | 205.1344
1226.176 | 190.5624 | 199.315 | 205.0579
1227.176 | 190.5814 | 200.5549 | 204.5404
1228.176 | 190.6689 | 200.7926 | 204.6385
1229.176 | 190.8795 | 198.4545 | 205.1177
1230.176 | 191.2455 | 195.3927 | 205.4886
1231.176 | 191.6964 | 194.121 | 205.6108
1232.176 | 191.4337 | 193.8819 | 205.7385
1233.176 | 191.5189 | 197.0835 | 205.4152
1234.176 | 191.4542 | 200.3881 | 205.2885
1235.176 | 191.0431 | 200.0584 | 205.4718
1236.176 | 190.9275 | 199.1062 | 205.7654
1237.176 | 191.6659 | 198.8951 | 206.0124
1238.176 | 191.536 | 201.5412 | 206.1161
1239.176 | 191.5608 | 203.8852 | 206.5345
1240.176 | 191.6627 | 205.2717 | 207.1643
1241.176 | 192.2749 | 212.0722 | 207.4387
1242.176 | 192.8055 | 214.6975 | 208.077
1243.176 | 193.1987 | 220.6425 | 208.0019
1244.176 | 193.7634 | 221.273 | 208.6658
1245.176 | 193.4191 | 225.1764 | 208.2475
1246.176 | 193.6987 | 224.608 | 208.6156
1247.176 | 193.7177 | 227.9043 | 209.255
1248.176 | 193.4638 | 227.7927 | 208.9378
1249.176 | 193.2064 | 226.3231 | 208.8969
1250.176 | 193.0728 | 222.7945 | 208.8692
1251.176 | 193.1715 | 220.7602 | 208.5444
1252.176 | 192.8897 | 219.8039 | 208.3938
1253.176 | 193.1292 | 220.4337 | 208.4993
1254.176 | 193.0226 | 217.8597 | 208.173
1255.176 | 192.8643 | 215.1535 | 208.2726
1256.176 | 192.6297 | 213.203 | 207.9618
1257.176 | 192.3702 | 211.0332 | 207.778
1258.176 | 192.2327 | 210.2753 | 207.2165
1259.176 | 192.2343 | 211.7977 | 207.1341
1260.176 | 192.2614 | 214.155 | 206.8042
1261.176 | 192.2944 | 213.3248 | 206.7445
1262.176 | 192.0962 | 211.9391 | 206.4636
1263.176 | 192.502 | 210.9777 | 206.5422
1264.176 | 192.934 | 213.2748 | 206.5119
1265.176 | 193.2132 | 212.4879 | 206.8667
1266.176 | 193.7238 | 211.5223 | 206.618
1267.176 | 194.057 | 207.4406 | 206.49
1268.176 | 194.3272 | 203.6826 | 206.9439
1269.176 | 194.3891 | 203.3369 | 206.5673
1270.176 | 194.786 | 204.7127 | 206.4303
1271.176 | 194.7886 | 206.0401 | 206.6411
1272.176 | 194.9134 | 208.2854 | 207.0362
1273.176 | 195.2081 | 209.6991 | 207.3159
1274.176 | 195.7206 | 210.7719 | 207.6389
1275.176 | 195.4071 | 209.5839 | 207.605
1276.176 | 195.3812 | 207.8167 | 208.0234
1277.176 | 195.2464 | 205.7155 | 207.999
1278.176 | 195.1626 | 203.2274 | 208.0943
1279.176 | 194.9095 | 201.2144 | 208.4899
1280.176 | 195.1481 | 200.944 | 208.471
1281.176 | 195.3706 | 200.2774 | 208.6552
1282.176 | 194.3503 | 195.5036 | 208.3874
1283.176 | 193.7579 | 193.1242 | 208.1897
1284.176 | 193.6975 | 190.5437 | 208.0185
1285.176 | 193.6473 | 189.6921 | 208.003
1286.176 | 193.5442 | 188.4036 | 207.751
1287.176 | 193.9492 | 189.4328 | 207.2694
1288.176 | 194.2192 | 191.2066 | 207.1611
1289.176 | 194.0711 | 191.7674 | 207.7134
1290.176 | 194.2804 | 194.4753 | 208.1977
1291.176 | 194.1177 | 196.6382 | 208.4075
1292.176 | 193.9008 | 197.694 | 208.669
1293.176 | 194.1061 | 199.4494 | 208.9856
1294.176 | 194.1751 | 197.5409 | 209.1737
1295.176 | 193.9257 | 196.679 | 209.3825
1296.176 | 194.0686 | 199.9019 | 209.0389
1297.176 | 194.4626 | 204.1616 | 208.957
1298.176 | 194.4462 | 208.4568 | 209.0064
1299.176 | 194.2235 | 210.8844 | 209.1325
1300.176 | 194.0992 | 211.18 | 209.0454
1301.176 | 194.0319 | 212.0662 | 209.4221
1302.176 | 193.9118 | 214.0824 | 209.3115
1303.176 | 193.6919 | 218.0609 | 209.2174
1304.176 | 193.3198 | 218.7413 | 209.2399
1305.176 | 193.4822 | 219.4536 | 208.9015
1306.176 | 193.2034 | 219.153 | 209.8853
1307.176 | 192.7774 | 217.1907 | 209.5932
1308.176 | 192.813 | 215.6193 | 209.6196
1309.176 | 192.6527 | 210.9955 | 210.3279
1310.176 | 192.5946 | 209.6131 | 210.3114
1311.176 | 192.2696 | 208.173 | 210.0237
1312.176 | 192.2471 | 207.9781 | 209.813
1313.176 | 192.5093 | 208.2616 | 209.9275
1314.176 | 192.4925 | 208.1512 | 210.1767
1315.176 | 192.1825 | 211.7186 | 210.2625
1316.176 | 192.3158 | 212.8939 | 210.379
1317.176 | 192.6662 | 214.1075 | 209.7828
1318.176 | 192.6311 | 215.2903 | 209.2452
1319.176 | 192.7014 | 214.5468 | 209.579
1320.176 | 192.8027 | 213.2613 | 209.3578
1321.176 | 192.973 | 215.1852 | 209.4754
1322.176 | 193.1782 | 214.2916 | 209.6529
1323.176 | 193.5305 | 213.2376 | 209.6203
1324.176 | 193.9397 | 216.4271 | 209.8098
1325.176 | 193.7448 | 218.4035 | 209.9714
1326.176 | 193.4567 | 218.5404 | 210.1822
1327.176 | 193.8202 | 216.7766 | 209.7069
1328.176 | 193.8847 | 215.078 | 209.8138
1329.176 | 194.0845 | 212.1804 | 209.4422
1330.176 | 194.1629 | 211.3232 | 209.2534
1331.176 | 194.4501 | 212.0611 | 209.7089
1332.176 | 193.9692 | 212.7416 | 209.8962
1333.176 | 194.283 | 215.1786 | 210.2705
1334.176 | 194.2884 | 217.2542 | 210.1496
1335.176 | 194.5553 | 218.351 | 210.1858
1336.176 | 194.3988 | 220.1384 | 210.0202
1337.176 | 193.9386 | 221.5736 | 209.6574
1338.176 | 193.537 | 221.8917 | 209.6511
1339.176 | 193.1888 | 222.15 | 209.599
1340.176 | 193.2201 | 222.9454 | 209.3887
1341.176 | 193.2992 | 224.9004 | 209.3935
1342.176 | 193.7259 | 227.4101 | 209.9078
1343.176 | 194.0351 | 230.2871 | 210.4025
1344.176 | 194.119 | 229.8429 | 211.1904
1345.176 | 194.3514 | 230.1436 | 211.4138
1346.176 | 194.4847 | 231.4952 | 211.7589
1347.176 | 194.3223 | 232.6738 | 211.7037
1348.176 | 194.3618 | 234.7207 | 211.7035
1349.176 | 194.4608 | 233.7674 | 211.5546
1350.176 | 194.6672 | 233.0416 | 211.3327
1351.176 | 194.4725 | 236.2205 | 210.9809
1352.176 | 194.5941 | 236.6759 | 210.8702
1353.176 | 194.4549 | 234.4785 | 210.4729
1354.176 | 193.9225 | 230.5465 | 210.3457
1355.176 | 194.2598 | 230.7918 | 210.0213
1356.176 | 194.5677 | 230.596 | 209.9857
1357.176 | 194.6668 | 229.8952 | 210.3116
1358.176 | 194.8483 | 228.6412 | 210.1338
1359.176 | 194.7716 | 229.2636 | 210.1819
1360.176 | 195.4448 | 227.9992 | 210.1122
1361.176 | 195.35 | 227.0859 | 209.7178
1362.176 | 195.589 | 225.5253 | 209.4335
1363.176 | 195.7317 | 225.6441 | 209.2453
1364.176 | 195.9681 | 225.7903 | 209.0473
1365.176 | 195.6235 | 223.8318 | 209.1195
1366.176 | 194.6951 | 224.3586 | 208.8937
1367.176 | 194.5308 | 224.2759 | 209.1935
1368.176 | 195.1323 | 223.4471 | 208.7928
1369.176 | 195.2568 | 231.3697 | 208.9861
1370.176 | 195.6386 | 236.5914 | 209.5336
1371.176 | 195.8102 | 239.5801 | 209.5851
1372.176 | 196.2506 | 244.8593 | 209.5249
1373.176 | 196.6604 | 243.609 | 209.5511
1374.176 | 197.1275 | 242.2692 | 209.5111
1375.176 | 196.8527 | 242.4185 | 209.4444
1376.176 | 196.6695 | 243.7979 | 209.8101
1377.176 | 196.636 | 247.1064 | 209.9019
1378.176 | 197.207 | 243.3878 | 210.4231
1379.176 | 197.1218 | 243.1642 | 210.6552
1380.176 | 196.7669 | 244.5056 | 210.9855
1381.176 | 196.9947 | 249.0679 | 211.0601
1382.176 | 196.9455 | 247.7542 | 210.9944
1383.176 | 197.4015 | 244.4353 | 210.9804
1384.176 | 197.1859 | 240.4393 | 211.5367
1385.176 | 197.0114 | 238.3899 | 211.5612
1386.176 | 197.0332 | 240.6731 | 212.0813
1387.176 | 197.0582 | 242.5353 | 211.9571
1388.176 | 198.2461 | 243.7454 | 211.5759
1389.176 | 198.334 | 241.3449 | 211.6148
1390.176 | 198.198 | 238.0724 | 211.3571
1391.176 | 198.5311 | 234.2286 | 211.292
1392.176 | 199.1006 | 235.8955 | 210.9722
1393.176 | 199.5203 | 236.9603 | 211.0276
1394.176 | 199.3229 | 238.2825 | 210.9455
1395.176 | 199.2481 | 241.9206 | 210.7196
1396.176 | 199.4894 | 243.2361 | 210.766
1397.176 | 199.374 | 242.9144 | 210.9482
1398.176 | 199.024 | 242.7544 | 210.9265
1399.176 | 199.0398 | 244.485 | 210.8913
1400.176 | 199.1859 | 243.1596 | 211.0888
1401.176 | 198.8518 | 242.1691 | 211.3888
1402.176 | 199.2049 | 243.9453 | 211.3306
1403.176 | 199.5121 | 244.2225 | 211.0256
1404.176 | 199.4518 | 240.9762 | 211.4069
1405.176 | 199.3428 | 240.9443 | 211.4425
1406.176 | 198.9308 | 243.5277 | 211.3711
1407.176 | 199.2456 | 246.0656 | 211.5008
1408.176 | 199.8925 | 247.0496 | 211.6583
1409.176 | 200.023 | 247.2676 | 211.8241
1410.176 | 199.5122 | 249.2275 | 211.827
1411.176 | 199.582 | 250.3049 | 211.8563
1412.176 | 199.7033 | 253.4421 | 211.7418
1413.176 | 199.8387 | 251.5628 | 211.5382
1414.176 | 199.6462 | 249.9453 | 212.0288
1415.176 | 199.7101 | 246.9111 | 212.4984
1416.176 | 199.4488 | 244.952 | 212.71
1417.176 | 199.7512 | 244.2354 | 212.6666
1418.176 | 199.8129 | 244.3041 | 212.9106
1419.176 | 199.9027 | 246.4803 | 213.2591
1420.176 | 200.4154 | 248.708 | 213.4374
1421.176 | 199.8706 | 249.514 | 213.4496
1422.176 | 199.4381 | 250.169 | 213.469
1423.176 | 199.6066 | 247.3601 | 213.5364
1424.176 | 199.4948 | 248.5569 | 213.6077
1425.176 | 199.7693 | 246.7598 | 213.7786
1426.176 | 199.9497 | 245.0119 | 213.6787
1427.176 | 200.3259 | 242.3037 | 213.5987
1428.176 | 200.4514 | 240.3679 | 213.4921
1429.176 | 200.8249 | 240.9129 | 213.4631
1430.176 | 200.9954 | 242.7236 | 213.5793
1431.176 | 200.968 | 242.1552 | 213.9955
1432.176 | 201.4171 | 243.1027 | 214.1627
1433.176 | 201.3296 | 242.7484 | 214.1327
1434.176 | 201.8738 | 242.0253 | 213.908
1435.176 | 202.0192 | 241.0199 | 214.2014
1436.176 | 201.782 | 241.1255 | 214.023
1437.176 | 201.7628 | 242.2994 | 213.8261
1438.176 | 201.9527 | 242.5728 | 213.3879
1439.176 | 201.6704 | 241.167 | 213.422
1440.176 | 201.7245 | 240.5851 | 213.6885
1441.176 | 201.7452 | 243.821 | 214.2135
1442.1917 | 201.9237 | 242.7254 | 213.9877
1443.176 | 202.1183 | 242.1876 | 214.0818
1444.176 | 201.9157 | 240.0547 | 214.0703
1445.176 | 202.448 | 245.2492 | 214.4304
1446.176 | 203.0228 | 246.6365 | 214.2877
1447.176 | 202.9785 | 246.1605 | 214.4286
1448.176 | 202.5929 | 250.5046 | 214.3202
1449.176 | 202.8724 | 250.3691 | 213.9551
1450.176 | 203.4556 | 252.3019 | 213.6804
1451.176 | 203.5518 | 249.8544 | 213.4032
1452.176 | 203.4914 | 247.1083 | 213.1526
1453.176 | 203.458 | 249.2749 | 213.4154
1454.176 | 203.2705 | 247.1631 | 213.6575
1455.176 | 203.0951 | 248.3235 | 213.3294
1456.176 | 203.0977 | 248.6187 | 213.5053
1457.176 | 203.4252 | 247.7035 | 213.6192
1458.176 | 203.3001 | 247.3299 | 213.6303
1459.176 | 203.5552 | 245.1176 | 213.441
1460.176 | 202.8807 | 244.3901 | 213.5343
1461.176 | 203.2125 | 247.4376 | 213.5959
1462.176 | 203.8436 | 246.6966 | 213.6756
1463.176 | 204.0394 | 244.426 | 213.9575
1464.176 | 204.0452 | 244.1809 | 214.0729
1465.176 | 203.8483 | 244.3824 | 214.4088
1466.176 | 203.7849 | 243.1755 | 214.665
1467.176 | 204.1662 | 240.6616 | 214.6993
1468.176 | 204.5059 | 241.4885 | 214.3758
1469.176 | 204.1123 | 242.7863 | 214.2732
1470.176 | 204.3311 | 244.2881 | 214.309
1471.176 | 204.8072 | 245.2649 | 214.4421
1472.176 | 205.0302 | 246.0086 | 214.5831
1473.176 | 204.8754 | 243.785 | 214.6922
1474.176 | 204.6492 | 241.607 | 214.3606
1475.176 | 204.7293 | 241.2849 | 214.5526
1476.176 | 204.5792 | 242.5873 | 214.8079
1477.176 | 204.7397 | 240.2275 | 214.4677
1478.176 | 204.7519 | 237.6673 | 214.2909
1479.176 | 204.6168 | 235.7647 | 214.0604
1480.176 | 204.7424 | 233.9131 | 213.7518
1481.176 | 204.6213 | 231.8152 | 214.0008
1482.176 | 204.8429 | 230.9761 | 214.0373
1483.176 | 204.7468 | 230.8062 | 214.143
1484.176 | 204.6903 | 232.1107 | 214.0923
1485.176 | 204.5623 | 233.0215 | 214.3063
1486.176 | 204.0867 | 231.5536 | 214.886
1487.176 | 204.3322 | 230.0477 | 215.2979
1488.176 | 204.4554 | 231.1473 | 216.0982
1489.176 | 204.8358 | 230.9485 | 215.9564
1490.176 | 205.0152 | 230.6654 | 215.9791
1491.176 | 205.4793 | 231.6568 | 216.1643
1492.176 | 205.3493 | 231.1336 | 216.6962
1493.176 | 205.6787 | 231.4572 | 217.0067
1494.176 | 205.4493 | 231.8841 | 217.4085
1495.176 | 205.0931 | 233.9462 | 217.431
1496.176 | 204.7677 | 234.6864 | 217.5725
1497.176 | 204.6697 | 235.063 | 217.535
1498.176 | 205.0587 | 235.6329 | 217.4442
1499.176 | 204.9285 | 233.967 | 216.966
1500.176 | 204.7792 | 230.4038 | 217.2574
1501.176 | 204.7096 | 228.8208 | 217.2949
1502.176 | 204.64 | 231.3743 | 217.2538
1503.176 | 204.3511 | 234.2724 | 217.4126
1504.176 | 204.0928 | 236.3059 | 217.3087
1505.176 | 204.1001 | 237.2419 | 216.9918
1506.176 | 204.2055 | 237.6861 | 216.9677
1507.176 | 204.4589 | 239.5924 | 217.0859
1508.176 | 204.7813 | 244.518 | 216.9705
1509.176 | 204.2665 | 250.8671 | 217.1335
1510.176 | 204.1073 | 251.1909 | 217.6183
1511.176 | 204.4084 | 250.251 | 217.8366
1512.176 | 204.9626 | 249.9711 | 217.7378
1513.176 | 204.8584 | 250.2116 | 217.5429
1514.176 | 205.0299 | 252.9333 | 217.86
1515.176 | 204.8523 | 254.1085 | 217.8885
1516.176 | 205.3755 | 252.8897 | 218.2103
1517.176 | 205.7319 | 252.3657 | 218.3246
1518.176 | 205.25 | 255.6517 | 218.196
1519.176 | 205.5416 | 261.6469 | 218.504
1520.176 | 205.7273 | 260.3462 | 219.348
1521.176 | 205.2707 | 258.3089 | 219.4386
1522.176 | 205.2528 | 259.6421 | 219.7584
1523.176 | 205.3015 | 262.5974 | 219.4989
1524.176 | 204.9308 | 261.4547 | 219.2202
1525.176 | 205.2998 | 260.3573 | 219.5808
1526.176 | 205.9192 | 259.4895 | 220.2808
1527.176 | 205.7794 | 258.6978 | 220.2198
1528.176 | 205.4643 | 260.1576 | 219.8584
1529.176 | 205.2567 | 263.7993 | 219.5724
1530.176 | 204.7809 | 263.4255 | 219.7424
1531.176 | 204.8219 | 264.6641 | 220.187
1532.176 | 205.1963 | 271.0689 | 220.5781
1533.176 | 205.439 | 274.0225 | 221.6495
1534.176 | 204.9988 | 274.3291 | 222.4025
1535.176 | 204.7913 | 272.7978 | 222.8564
1536.176 | 204.8279 | 271.1016 | 223.1477
1537.176 | 204.848 | 276.1193 | 223.121
1538.176 | 205.2724 | 277.6332 | 222.9953
1539.176 | 205.343 | 279.6564 | 222.4041
1540.176 | 205.6588 | 281.1074 | 222.0614
1541.176 | 205.837 | 281.1031 | 221.782
1542.176 | 206.2683 | 280.4151 | 221.4534
1543.176 | 206.0637 | 287.3181 | 221.1765
1544.176 | 206.4211 | 287.2037 | 221.2983
1545.176 | 206.6552 | 289.1928 | 220.8054
1546.176 | 206.8543 | 289.3655 | 221.2213
1547.176 | 206.8307 | 289.0933 | 221.305
1548.176 | 206.8412 | 284.5022 | 221.0631
1549.176 | 206.7531 | 282.2446 | 220.8617
1550.176 | 206.7315 | 284.4543 | 220.9759
1551.176 | 206.941 | 282.9058 | 221.2505
1552.176 | 206.3288 | 280.3283 | 221.0632
1553.176 | 206.7115 | 286.6723 | 221.2553
1554.176 | 206.7137 | 289.8167 | 221.4174
1555.176 | 206.6964 | 292.0408 | 221.7513
1556.176 | 207.0614 | 292.828 | 220.9058
1557.176 | 207.574 | 292.3964 | 221.031
1558.176 | 207.7558 | 290.3851 | 220.9759
1559.1917 | 207.8985 | 294.3506 | 221.1202
1560.176 | 207.9935 | 296.568 | 221.4869
1561.176 | 207.646 | 292.7533 | 221.5569
1562.176 | 207.4313 | 295.202 | 221.5676
1563.176 | 207.6548 | 299.5839 | 221.7765
1564.176 | 207.4388 | 296.9185 | 221.5516
1565.176 | 207.2438 | 294.1072 | 221.8871
1566.176 | 207.4293 | 294.9679 | 221.7119
1567.176 | 207.6771 | 300.826 | 222.3659
1568.176 | 207.8768 | 301.0943 | 222.7215
1569.176 | 207.6624 | 300.572 | 222.7865
1570.176 | 207.8606 | 298.7568 | 222.7042
1571.176 | 208.2144 | 297.6874 | 222.8157
1572.176 | 207.8946 | 297.9762 | 222.4804
1573.176 | 208.6396 | 297.8384 | 221.9797
1574.176 | 209.217 | 296.0403 | 222.1454
1575.176 | 209.3017 | 297.7117 | 222.328
1576.176 | 209.4498 | 298.8444 | 222.202
1577.176 | 209.7134 | 297.5912 | 222.0068
1578.176 | 209.8888 | 297.3735 | 221.9896
1579.176 | 209.8726 | 300.1185 | 222.0498
1580.176 | 210.4506 | 300.3839 | 222.5737
1581.176 | 210.0491 | 303.7977 | 223.1047
1582.176 | 209.9432 | 306.24 | 223.4479
1583.176 | 209.5055 | 305.7235 | 223.8201
1584.176 | 209.8791 | 305.6585 | 223.6679
1585.176 | 209.9771 | 303.262 | 223.6734
1586.176 | 210.5046 | 304.0581 | 224.1487
1587.176 | 210.3719 | 304.7813 | 224.4736
1588.176 | 209.86 | 303.6035 | 224.7964
1589.176 | 210.2046 | 302.373 | 224.4496
1590.176 | 210.5836 | 303.3245 | 224.6399
1591.176 | 210.5783 | 304.7469 | 225.0693
1592.176 | 210.8067 | 310.4099 | 225.0722
1593.176 | 210.9215 | 311.1577 | 224.6685
1594.176 | 211.083 | 312.3074 | 224.5211
1595.176 | 210.4715 | 311.4477 | 225.0991
1596.176 | 211.0749 | 314.3735 | 224.9279
1597.176 | 211.1795 | 318.2789 | 224.9501
1598.176 | 211.1323 | 319.3007 | 225.595
1599.176 | 211.0415 | 318.9339 | 225.9734
1600.176 | 210.5714 | 319.7933 | 226.3839
1601.176 | 211.008 | 320.5834 | 226.641
1602.176 | 210.8173 | 317.0038 | 226.3727
1603.176 | 210.7607 | 320.608 | 226.6395
1604.176 | 210.6256 | 321.9472 | 226.5235
1605.176 | 211.2145 | 322.6237 | 225.9806
1606.176 | 211.3497 | 325.1028 | 226.0558
1607.176 | 211.6254 | 324.2559 | 225.9219
1608.176 | 211.7443 | 321.5083 | 225.7085
1609.176 | 211.6459 | 334.4627 | 226.0166
1610.176 | 211.3586 | 337.3925 | 226.0045
1611.176 | 211.558 | 337.2805 | 225.6094
1612.176 | 211.8451 | 335.8581 | 225.5167
1613.176 | 211.3761 | 335.6463 | 225.4354
1614.176 | 211.4812 | 336.0073 | 225.7996
1615.176 | 211.4332 | 334.3984 | 225.8744
1616.176 | 211.4187 | 333.4523 | 225.8205
1617.176 | 211.6306 | 334.5135 | 226.0502
1618.176 | 211.7083 | 333.3306 | 226.3057
1619.176 | 211.8077 | 336.5552 | 227.0173
1620.176 | 211.6563 | 333.1841 | 227.5253
1621.176 | 211.5221 | 331.6564 | 227.804
1622.176 | 211.8862 | 339.0014 | 227.9898
1623.176 | 212.1932 | 340.266 | 227.9837
1624.176 | 213.0058 | 344.8743 | 228.2953
1625.176 | 213.2556 | 344.8929 | 228.3126
1626.176 | 213.2869 | 343.5625 | 228.2374
1627.176 | 214.1336 | 343.5099 | 228.3139
1628.176 | 214.0461 | 342.3516 | 228.0884
1629.176 | 213.7031 | 341.6207 | 227.6155
1630.176 | 213.9985 | 337.7469 | 227.221
1631.176 | 214.3924 | 346.7589 | 227.0024
1632.176 | 214.4586 | 340.2933 | 226.804
1633.176 | 214.165 | 341.0792 | 226.9014
1634.176 | 214.6176 | 348.4913 | 226.3446
1635.176 | 214.9623 | 349.3199 | 225.9483
1636.176 | 215.1023 | 347.377 | 226.1937
1637.176 | 215.1902 | 348.6093 | 226.2048
1638.176 | 214.724 | 346.8599 | 225.6103
1639.176 | 214.4944 | 343.8585 | 225.6801
1640.176 | 213.7849 | 341.1857 | 225.6572
1641.176 | 212.9837 | 338.3543 | 225.5864
1642.176 | 212.1797 | 335.5375 | 225.3235
1643.176 | 211.5658 | 336.8541 | 225.1606
1644.176 | 211.3999 | 335.0049 | 225.1803
1645.176 | 210.8902 | 334.8987 | 225.1966
1646.176 | 210.8354 | 332.1305 | 225.621
1647.176 | 210.8326 | 326.861 | 225.2821
1648.176 | 210.4115 | 332.2476 | 224.626
1649.176 | 209.9047 | 329.0797 | 224.2863
1650.176 | 210.133 | 325.3168 | 224.4185
1651.176 | 210.409 | 324.4139 | 224.4977
1652.176 | 210.1794 | 332.14 | 224.1785
1653.176 | 210.1881 | 336.9541 | 224.5118
1654.176 | 210.3213 | 338.6649 | 224.3599
1655.176 | 210.6846 | 336.3786 | 224.4427
1656.176 | 211.073 | 338.7992 | 224.5005
1657.176 | 211.2368 | 338.0689 | 223.9467
1658.176 | 210.9509 | 336.3261 | 223.8934
1659.176 | 211.0648 | 336.047 | 223.5279
1660.176 | 211.2727 | 334.5037 | 223.1708
1661.176 | 211.2129 | 332.8359 | 223.1157
1662.176 | 211.3679 | 332.5916 | 223.3505
1663.176 | 211.6146 | 336.0481 | 223.4312
1664.176 | 211.9602 | 343.2 | 223.5674
1665.176 | 211.8806 | 338.8107 | 224.0914
1666.176 | 211.7943 | 337.6835 | 223.5115
1667.176 | 211.3564 | 339.5592 | 223.3988
1668.176 | 210.9865 | 347.7218 | 223.2339
1669.176 | 211.2432 | 351.8705 | 223.6104
1670.176 | 211.5968 | 351.2583 | 224.2987
1671.176 | 211.8204 | 349.2946 | 224.4333
1672.176 | 212.927 | 352.5242 | 224.7665
1673.176 | 213.0497 | 353.0702 | 225.4546
1674.176 | 213.3536 | 351.7039 | 225.6909
1675.176 | 213.8603 | 351.7679 | 225.9869
1676.176 | 213.8728 | 350.7375 | 225.7282
1677.176 | 214.1145 | 348.9676 | 226.0138
1678.176 | 214.5715 | 347.4009 | 226.0709
1679.176 | 214.3629 | 347.5348 | 226.3769
1680.176 | 214.493 | 349.9551 | 226.613
1681.176 | 213.8654 | 345.1334 | 226.5716
1682.176 | 214.3399 | 342.1284 | 226.5161
1683.176 | 215.5766 | 340.0344 | 226.5736
1684.176 | 215.3026 | 336.0689 | 226.2858
1685.176 | 215.4088 | 337.6567 | 226.34
1686.176 | 215.6376 | 338.9028 | 226.0017
1687.176 | 215.4741 | 338.4057 | 225.816
1688.176 | 216.0256 | 340.444 | 225.6808
1689.176 | 215.8066 | 337.9559 | 225.7795
1690.176 | 215.8686 | 339.4307 | 226.3054
1691.176 | 215.8691 | 344.812 | 226.4858
1692.176 | 215.9364 | 347.6354 | 226.7814
1693.176 | 215.571 | 347.0158 | 226.8454
1694.176 | 215.4462 | 349.5938 | 226.9227
1695.176 | 214.5239 | 350.476 | 227.0224
1696.176 | 214.2987 | 345.6396 | 226.8851
1697.176 | 214.2144 | 340.8782 | 227.0338
1698.176 | 214.186 | 336.1549 | 226.7734
1699.176 | 215.4279 | 334.1433 | 226.6863
1700.176 | 215.3084 | 331.8228 | 226.7303
1701.176 | 215.6177 | 333.0146 | 227.0622
1702.176 | 216.1253 | 333.9307 | 226.7784
1703.176 | 216.4652 | 333.3182 | 226.5529
1704.176 | 216.0027 | 331.5652 | 226.5671
1705.176 | 215.8136 | 333.782 | 226.5562
1706.176 | 215.4595 | 333.4007 | 226.664
1707.176 | 215.6215 | 333.7755 | 226.4959
1708.176 | 215.8366 | 339.4771 | 226.4321
1709.176 | 215.4126 | 337.1854 | 226.6807
1710.176 | 215.5712 | 334.4833 | 226.5331
1711.176 | 215.5777 | 332.4555 | 226.496
1712.176 | 215.1325 | 330.3772 | 226.452
1713.176 | 215.3121 | 330.7339 | 226.5874
1714.176 | 215.2929 | 328.1939 | 226.6613
1715.176 | 215.4172 | 323.283 | 226.7627
1716.176 | 214.9084 | 320.3229 | 227.1113
1717.176 | 214.6549 | 320.0622 | 228.7686
1718.176 | 214.4168 | 318.5498 | 228.528
1719.176 | 214.4526 | 316.4577 | 228.1188
1720.176 | 214.6026 | 314.8625 | 227.766
1721.176 | 214.618 | 312.5723 | 227.3817
1722.176 | 214.5766 | 311.0691 | 227.361
1723.176 | 214.1818 | 310.7723 | 227.4819
1724.176 | 213.4907 | 311.0554 | 227.8844
1725.176 | 213.0062 | 308.1006 | 227.6268
1726.176 | 212.6881 | 305.2952 | 227.5406
1727.176 | 212.7108 | 305.4443 | 227.239
1728.176 | 212.8381 | 304.04 | 227.0712
1729.176 | 212.7187 | 301.6173 | 227
1730.176 | 213.1609 | 300.6674 | 226.9175
1731.176 | 212.9584 | 300.8632 | 226.8156
1732.176 | 212.6816 | 299.0266 | 226.5133
1733.176 | 212.6137 | 298.2996 | 226.1314
1734.176 | 212.3521 | 297.8371 | 226.2206
1735.176 | 212.1267 | 298.5363 | 226.1794
1736.176 | 211.9907 | 303.8819 | 225.7837
1737.176 | 212.1115 | 303.4677 | 225.2821
1738.176 | 212.3383 | 303.1603 | 225.0715
1739.176 | 212.9184 | 303.1738 | 225.0652
1740.176 | 212.8691 | 303.6531 | 224.7439
1741.176 | 212.195 | 305.0602 | 224.3068
1742.176 | 212.5197 | 304.4668 | 224.619
1743.176 | 212.5677 | 301.4481 | 225.0294
1744.176 | 213.0674 | 297.7301 | 224.9298
1745.176 | 213.3221 | 297.5079 | 224.9895
1746.176 | 213.3841 | 302.8982 | 225.0301
1747.176 | 213.9495 | 303.3733 | 225.5237
1748.176 | 214.0928 | 306.7898 | 225.5165
1749.176 | 213.859 | 309.2783 | 225.2881
1750.176 | 213.6933 | 311.335 | 224.7724
1751.176 | 213.5202 | 315.6341 | 224.4968
1752.176 | 213.3357 | 311.8645 | 225.1321
1753.176 | 213.1334 | 307.7957 | 225.354
1754.176 | 212.9383 | 303.0202 | 225.2837
1755.176 | 212.8702 | 299.6106 | 225.2101
1756.176 | 212.8775 | 297.1182 | 224.6624
1757.176 | 212.6746 | 296.0241 | 224.0688
1758.176 | 212.3018 | 294.4563 | 223.8185
1759.176 | 212.4948 | 294.5668 | 223.4457
1760.176 | 212.8987 | 295.7306 | 223.0157
1761.176 | 213.2667 | 298.001 | 223.2379
1762.176 | 213.2278 | 303.6535 | 223.5276
1763.176 | 213.6925 | 306.7272 | 223.7428
1764.176 | 213.9512 | 309.0496 | 223.7842
1765.176 | 214.0534 | 310.4517 | 223.7048
1766.176 | 214.1086 | 313.71 | 223.5887
1767.176 | 213.4712 | 315.0639 | 223.4923
1768.176 | 212.9001 | 313.5857 | 223.7659
1769.176 | 213.2819 | 310.8763 | 223.7957
1770.176 | 213.5996 | 310.6179 | 223.7407
1771.176 | 213.3666 | 308.4084 | 224.1337
1772.176 | 212.8458 | 310.205 | 223.7494
1773.176 | 212.8795 | 315.2756 | 223.5635
1774.176 | 212.3078 | 311.6528 | 223.5965
1775.176 | 212.4824 | 309.8971 | 223.5177
1776.176 | 212.7667 | 307.1254 | 223.4416
1777.176 | 213.123 | 304.5816 | 223.1984
1778.176 | 213.8113 | 304.5812 | 223.7942
1779.176 | 214.0393 | 303.6366 | 223.9325
1780.176 | 214.5417 | 304.0878 | 223.5323
1781.176 | 214.5057 | 307.8408 | 223.5637
1782.176 | 213.7974 | 308.1814 | 223.7609
1783.176 | 213.4855 | 307.9533 | 223.8433
1784.176 | 213.5785 | 306.3953 | 223.7206
1785.176 | 213.7826 | 307.0988 | 224.145
1786.176 | 214.2599 | 307.455 | 224.1358
1787.176 | 214.7949 | 306.5343 | 224.2905
1788.176 | 215.4851 | 307.845 | 224.2373
1789.176 | 215.4509 | 310.8176 | 224.3115
1790.176 | 215.4394 | 309.4752 | 224.5212
1791.176 | 215.3967 | 306.5924 | 224.5895
1792.176 | 215.2085 | 304.7861 | 224.803
1793.176 | 215.1971 | 305.9378 | 225.0777
1794.176 | 214.6412 | 307.6355 | 225.5574
1795.176 | 214.6332 | 308.0766 | 225.497
1796.176 | 214.4942 | 313.2282 | 225.0786
1797.176 | 214.505 | 313.7087 | 225.0889
1798.176 | 213.8383 | 313.37 | 225.1346
1799.176 | 213.8697 | 312.0146 | 225.0589
1800.176 | 213.6061 | 310.8452 | 224.8933
1801.176 | 213.6445 | 310.4127 | 225.1425
1802.1917 | 213.9323 | 308.9772 | 225.1158
1803.176 | 214.3212 | 307.189 | 225.241
1804.176 | 214.6933 | 308.9267 | 225.1989
1805.176 | 214.8862 | 310.5652 | 224.9321
1806.176 | 215.1056 | 314.2342 | 224.5793
1807.176 | 215.0597 | 315.7972 | 224.8694
1808.176 | 214.674 | 314.656 | 224.9075
1809.176 | 214.5021 | 312.3447 | 224.5757
1810.176 | 214.1605 | 309.4336 | 224.6406
1811.176 | 214.0357 | 305.139 | 225.2106
1812.176 | 214.1302 | 303.4572 | 225.7682
1813.176 | 214.0771 | 302.8981 | 226.2356
1814.176 | 214.2402 | 303.7242 | 226.1921
1815.176 | 214.3893 | 310.8882 | 226.2701
1816.176 | 214.4114 | 311.4697 | 225.9765
1817.176 | 213.7471 | 311.8949 | 225.8431
1818.176 | 213.125 | 307.7463 | 225.8413
1819.176 | 212.8474 | 302.2886 | 225.8928
1820.176 | 212.852 | 297.3851 | 225.5338
1821.176 | 212.4224 | 296.6514 | 225.4563
1822.176 | 212.3426 | 292.058 | 225.5737
1823.176 | 212.014 | 292.7895 | 224.9611
1824.176 | 212.1138 | 295.0203 | 224.8168
1825.176 | 211.4733 | 294.251 | 224.6361
1826.176 | 211.389 | 290.757 | 224.657
1827.176 | 210.9091 | 286.6478 | 224.2284
1828.176 | 210.1183 | 282.7992 | 224.1077
1829.176 | 209.4498 | 278.7316 | 224.2965
1830.176 | 209.5568 | 275.4779 | 224.1856
1831.176 | 209.4552 | 270.483 | 224.1752
1832.176 | 209.6464 | 268.1674 | 224.1854
1833.176 | 209.7225 | 266.4486 | 223.9757
1834.176 | 209.4091 | 270.1474 | 224.2164
1835.176 | 209.3509 | 272.9266 | 224.1985
1836.176 | 209.7867 | 274.5127 | 223.7065
1837.176 | 209.3496 | 273.7127 | 223.679
1838.176 | 208.8696 | 271.3741 | 224.0658
1839.176 | 208.4828 | 268.8089 | 224.174
1840.176 | 208.4079 | 266.8049 | 224.143
1841.176 | 208.3254 | 266.5208 | 223.8082
1842.176 | 208.6272 | 266.7466 | 223.6711
1843.176 | 208.7041 | 267.1814 | 223.6297
1844.176 | 209.009 | 265.2613 | 223.697
1845.176 | 209.3606 | 265.8437 | 223.6605
1846.176 | 210.0486 | 266.6541 | 223.72
1847.176 | 210.0273 | 266.4307 | 223.6379
1848.176 | 210.2473 | 267.6705 | 223.3916
1849.176 | 210.5102 | 266.407 | 223.2731
1850.176 | 210.6149 | 269.6408 | 223.4271
1851.176 | 210.9117 | 268.5237 | 223.1184
1852.176 | 210.9249 | 267.4679 | 222.8955
1853.176 | 210.9248 | 270.9173 | 222.5947
1854.176 | 211.0137 | 271.3626 | 222.4288
1855.176 | 210.9723 | 271.902 | 222.4176
1856.176 | 211.042 | 271.819 | 222.5115
1857.176 | 210.9689 | 271.2082 | 222.7475
1858.176 | 211.086 | 267.7434 | 222.9128
1859.176 | 211.2218 | 263.6357 | 222.7474
1860.176 | 211.3488 | 264.0244 | 223.0758
1861.176 | 211.5275 | 264.9624 | 223.2453
1862.176 | 211.6308 | 266.2688 | 222.9764
1863.176 | 212.1968 | 268.257 | 222.9014
1864.176 | 212.3539 | 267.4228 | 222.5187
1865.176 | 212.0941 | 270.7878 | 222.1095
1866.176 | 212.0599 | 273.8133 | 222.0688
1867.176 | 211.9882 | 273.2137 | 221.9515
1868.176 | 212.2448 | 271.4928 | 222.1892
1869.176 | 211.8321 | 270.3293 | 222.3101
1870.176 | 211.9078 | 272.9429 | 222.2649
1871.176 | 212.8591 | 275.2651 | 222.0822
1872.176 | 212.9322 | 275.6609 | 221.9213
1873.176 | 213.3545 | 280.5544 | 221.9227
1874.176 | 213.4404 | 279.5923 | 222.2846
1875.176 | 213.4483 | 278.8963 | 222.3906
1876.176 | 212.939 | 277.7151 | 222.1631
1877.176 | 212.5795 | 274.0488 | 222.1962
1878.176 | 213.0149 | 269.8489 | 222.0178
1879.176 | 213.2856 | 268.1344 | 222.0858
1880.176 | 213.3442 | 266.2007 | 221.8666
1881.176 | 212.9756 | 268.1545 | 222.0993
1882.176 | 213.9124 | 272.3727 | 222.1615
1883.176 | 214.1035 | 272.2568 | 222.0141
1884.176 | 214.1219 | 272.9164 | 222.0595
1885.176 | 213.7342 | 273.642 | 222.021
1886.176 | 213.3778 | 274.0225 | 222.3571
1887.176 | 212.9121 | 274.3647 | 222.0326
1888.176 | 212.6992 | 272.7625 | 222.1572
1889.176 | 212.5419 | 271.5949 | 221.5277
1890.176 | 212.6996 | 269.9324 | 221.3866
1891.176 | 212.7461 | 270.6225 | 221.1032
1892.176 | 212.5358 | 271.5585 | 220.8914
1893.176 | 212.3295 | 271.4023 | 221.335
1894.176 | 212.5809 | 272.5583 | 221.4796
1895.176 | 212.5915 | 271.4916 | 221.4401
1896.176 | 212.6941 | 270.6026 | 221.1111
1897.176 | 212.3442 | 270.1332 | 220.8597
1898.176 | 212.3006 | 269.6632 | 221.2026
1899.176 | 211.9134 | 271.0915 | 220.8053
1900.176 | 211.767 | 272.2307 | 220.3141
1901.176 | 211.4785 | 276.8841 | 219.9617
1902.176 | 211.5384 | 273.2893 | 219.774
1903.176 | 212.8289 | 272.939 | 220.2691
1904.176 | 212.939 | 273.4651 | 220.1207
1905.176 | 212.8771 | 276.0281 | 220.5929
1906.176 | 213.0493 | 276.5352 | 220.6841
1907.176 | 212.869 | 276.0828 | 220.9761
1908.176 | 213.0209 | 272.8302 | 220.8538
1909.176 | 213.137 | 276.5432 | 221.1225
1910.176 | 213.3025 | 276.8107 | 220.9992
1911.176 | 213.5087 | 276.7047 | 221.5598
1912.176 | 213.0414 | 273.8419 | 222.0761
1913.176 | 212.902 | 273.8433 | 222.4643
1914.176 | 212.9439 | 274.2828 | 222.4378
1915.176 | 212.6459 | 276.544 | 222.0955
1916.176 | 212.9812 | 276.8606 | 222.1001
1917.176 | 213.1046 | 276.0637 | 221.8531
1918.176 | 213.24 | 275.1429 | 222.129
1919.176 | 213.0333 | 272.7966 | 221.7798
1920.176 | 212.7977 | 270.538 | 221.8903
1921.176 | 212.5362 | 268.4482 | 221.9686
1922.1917 | 212.0954 | 268.4274 | 222.3524
1923.176 | 211.7096 | 267.5226 | 222.6048
1924.176 | 211.3515 | 266.6351 | 222.4604
1925.176 | 210.9535 | 267.9443 | 222.4714
1926.176 | 210.3632 | 272.32 | 222.6967
1927.176 | 210.1363 | 271.2891 | 222.7806
1928.176 | 209.719 | 270.953 | 222.6822
1929.176 | 209.7041 | 269.067 | 222.8527
1930.176 | 209.6478 | 270.0128 | 223.4115
1931.176 | 209.0824 | 269.0482 | 223.2234
1932.176 | 209.2138 | 268.8459 | 223.479
1933.176 | 209.154 | 265.9526 | 223.7256
1934.176 | 208.6337 | 265.8327 | 224.0376
1935.176 | 208.4689 | 262.566 | 224.499
1936.176 | 208.6971 | 276.3241 | 224.5312
1937.176 | 208.6717 | 271.8167 | 224.8337
1938.176 | 209.1604 | 269.7039 | 224.5241
1939.176 | 208.8616 | 267.686 | 224.0732
1940.176 | 208.7287 | 261.9441 | 224.0556
1941.176 | 208.7207 | 257.0069 | 223.8418
1942.176 | 208.2783 | 252.018 | 223.3314
1943.176 | 207.848 | 248.354 | 223.0546
1944.176 | 207.5818 | 245.7844 | 222.6842
1945.176 | 207.4135 | 243.9074 | 221.9601
1946.176 | 207.509 | 241.8729 | 221.6844
1947.176 | 207.3704 | 240.6693 | 221.3907
1948.176 | 207.6205 | 238.0976 | 221.535
1949.176 | 208.035 | 235.0019 | 221.8921
1950.176 | 208.0302 | 236.4305 | 221.797
1951.176 | 208.0534 | 238.2468 | 222.2838
1952.176 | 208.5895 | 237.891 | 222.7753
1953.176 | 208.7527 | 237.1342 | 222.9132
1954.176 | 208.9269 | 236.5028 | 222.7127
1955.176 | 208.8303 | 241.1409 | 222.3063
1956.176 | 208.8109 | 241.8643 | 222.4456
1957.176 | 209.1072 | 244.1603 | 222.6795
1958.176 | 209.177 | 247.4168 | 222.8336
1959.176 | 209.2728 | 245.821 | 222.8788
1960.176 | 209.5854 | 248.7513 | 222.5711
1961.176 | 210.0737 | 245.4181 | 222.4404
1962.176 | 211.7266 | 243.1806 | 222.6238
1963.176 | 212.2063 | 242.5389 | 222.5063
1964.176 | 212.0725 | 240.8363 | 222.7724
1965.176 | 211.7252 | 237.1026 | 222.764
1966.176 | 212.2558 | 234.0008 | 222.3912
1967.176 | 213.025 | 232.4399 | 222.3625
1968.176 | 213.0446 | 231.2413 | 222.0355
1969.176 | 212.498 | 229.4701 | 222.4215
1970.176 | 212.481 | 228.0981 | 222.0669
1971.176 | 212.6426 | 232.2801 | 222.0123
1972.176 | 212.5318 | 230.6203 | 222.275
1973.176 | 212.2069 | 230.9137 | 222.2274
1974.176 | 212.272 | 231.3172 | 222.2308
1975.176 | 211.8611 | 233.569 | 222.7724
1976.176 | 211.4809 | 236.1273 | 222.7738
1977.176 | 211.0959 | 237.7427 | 222.6364
1978.176 | 210.7338 | 236.5829 | 222.9327
1979.176 | 210.802 | 236.3071 | 222.8744
1980.176 | 210.5818 | 237.2384 | 222.4968
1981.176 | 210.5684 | 236.8595 | 222.2165
1982.176 | 210.0201 | 237.7683 | 221.71
1983.176 | 210.1554 | 236.4689 | 222.1573
1984.176 | 210.2627 | 233.9211 | 221.9271
1985.176 | 210.3532 | 231.6498 | 221.6185
1986.176 | 209.8972 | 229.6109 | 221.1663
1987.176 | 210.2339 | 228.0272 | 221.1707
1988.176 | 210.6528 | 228.1798 | 221.1379
1989.176 | 210.7017 | 228.9853 | 221.1978
1990.176 | 211.1364 | 230.4458 | 221.7146
1991.176 | 210.8324 | 230.3804 | 222.0372
1992.176 | 210.8085 | 231.406 | 221.7521
1993.176 | 210.9131 | 231.8576 | 221.6211
1994.176 | 210.9864 | 229.7539 | 221.5704
1995.176 | 211.2415 | 228.5206 | 221.8431
1996.176 | 211.9328 | 228.1657 | 222.0808
1997.176 | 211.4149 | 231.914 | 221.8899
1998.176 | 211.2505 | 237.2571 | 221.6526
1999.176 | 211.6113 | 238.0323 | 221.6742
2000.176 | 211.8372 | 236.9173 | 221.756
2001.176 | 211.7793 | 236.9055 | 221.8686
2002.176 | 211.9758 | 239.5901 | 221.9636
2003.176 | 211.9531 | 238.4346 | 221.8586
2004.176 | 211.8822 | 235.3032 | 222.1002
2005.176 | 211.5106 | 233.6488 | 221.8705
2006.176 | 211.5561 | 231.63 | 221.793
2007.176 | 211.4181 | 232.6066 | 221.9824
2008.176 | 211.3021 | 237.073 | 222.2052
2009.176 | 211.7027 | 238.2078 | 222.1991
2010.176 | 211.3798 | 238.0664 | 222.3909
2011.176 | 211.5122 | 239.0461 | 222.2304
2012.176 | 211.2547 | 239.4886 | 222.0786
2013.176 | 210.8776 | 238.1411 | 222.249
2014.176 | 211.1313 | 235.957 | 222.3947
2015.176 | 211.2222 | 233.7955 | 222.1997
2016.176 | 211.409 | 231.4252 | 222.4047
2017.176 | 211.566 | 229.3313 | 222.339
2018.176 | 211.4195 | 231.0258 | 222.3037
2019.176 | 211.3852 | 234.5907 | 222.1687
2020.176 | 211.5813 | 232.9138 | 222.3585
2021.176 | 211.5528 | 231.2877 | 222.4335
2022.176 | 211.4219 | 229.1176 | 222.581
2023.176 | 211.6674 | 227.5328 | 223.1376
2024.176 | 211.347 | 226.9067 | 222.8305
2025.176 | 211.0599 | 227.3482 | 223.0208
2026.176 | 211.0699 | 226.5229 | 222.9501
2027.176 | 211.1026 | 224.8545 | 222.5866
2028.176 | 211.3005 | 225.7345 | 222.8104
2029.176 | 211.6813 | 225.5453 | 222.5633
2030.176 | 211.5374 | 227.7388 | 222.1414
2031.176 | 211.297 | 228.2959 | 222.1272
2032.176 | 210.9989 | 227.4279 | 222.0057
2033.176 | 210.5743 | 226.4048 | 221.8527
2034.176 | 210.2745 | 226.1369 | 221.8879
2035.176 | 209.9838 | 225.3392 | 222.1435
2036.176 | 209.6582 | 225.1407 | 221.574
2037.176 | 209.4414 | 224.4108 | 222.0029
2038.176 | 209.7004 | 226.4113 | 221.697
2039.176 | 209.9272 | 225.8709 | 221.9204
2040.176 | 210.0939 | 224.1482 | 221.9282
2041.176 | 209.885 | 225.028 | 221.3504
2042.176 | 209.5358 | 225.669 | 221.2708
2043.176 | 209.2044 | 224.3913 | 221.0268
2044.176 | 208.7353 | 223.2339 | 220.7299
2045.176 | 208.2762 | 222.073 | 221.3757
2046.176 | 207.766 | 221.6467 | 221.4732
2047.176 | 207.7612 | 219.49 | 221.5927
2048.176 | 207.9453 | 217.8406 | 222.2805
2049.176 | 208.1438 | 217.6296 | 222.2021
2050.176 | 208.3586 | 218.7869 | 222.7771
2051.176 | 208.4894 | 220.382 | 223.0567
2052.176 | 208.8934 | 223.5416 | 223.0899
2053.176 | 208.8623 | 224.5055 | 223.1307
2054.176 | 209.3241 | 227.4173 | 223.0523
2055.176 | 209.5218 | 234.2188 | 223.107
2056.176 | 209.5779 | 233.721 | 222.9073
2057.176 | 209.1958 | 234.1543 | 223.015
2058.176 | 209.8365 | 233.7131 | 223.0614
2059.176 | 209.5925 | 233.2038 | 223.0129
2060.176 | 209.633 | 234.5775 | 223.0704
2061.176 | 209.6335 | 233.6163 | 223.2686
2062.1917 | 209.7567 | 233.2653 | 224.4892
2063.176 | 209.8559 | 234.7524 | 224.5176
2064.176 | 209.6567 | 235.3238 | 224.3161
2065.176 | 209.5546 | 239.4436 | 224.2488
2066.176 | 209.6657 | 239.7454 | 224.4096
2067.176 | 209.3957 | 242.6414 | 224.7812
2068.176 | 209.543 | 243.7801 | 224.4952
2069.176 | 209.2296 | 244.8458 | 224.7193
2070.176 | 208.908 | 244.9269 | 224.1299
2071.176 | 208.8863 | 242.654 | 224.2583
2072.176 | 208.516 | 241.0973 | 224.1317
2073.176 | 208.0421 | 240.339 | 224.5635
2074.176 | 207.6228 | 241.3999 | 224.5032
2075.176 | 207.5424 | 239.9986 | 224.6228
2076.176 | 207.3598 | 240.2133 | 224.7395
2077.176 | 207.4564 | 238.5474 | 224.5899
2078.176 | 207.391 | 239.6686 | 224.246
2079.176 | 207.314 | 239.7158 | 223.7394
2080.176 | 207.1717 | 239.7132 | 223.7674
2081.176 | 207.264 | 238.2282 | 223.3237
2082.176 | 207.1 | 240.461 | 222.9648
2083.176 | 206.8477 | 244.4812 | 223.208
2084.176 | 207.0201 | 242.5375 | 223.334
2085.176 | 206.8666 | 240.0645 | 223.1368
2086.176 | 206.9778 | 237.7296 | 222.9693
2087.176 | 206.8995 | 236.8663 | 222.8316
2088.176 | 206.9298 | 238.4172 | 222.6161
2089.176 | 207.1638 | 238.3187 | 222.8461
2090.176 | 207.4585 | 236.6945 | 223.0177
2091.176 | 207.6653 | 235.3303 | 223.3666
2092.176 | 207.5371 | 233.494 | 223.3048
2093.176 | 207.9351 | 233.157 | 223.418
2094.176 | 208.1283 | 230.7241 | 223.1517
2095.176 | 208.0955 | 228.3365 | 222.9154
2096.176 | 208.0546 | 227.7736 | 222.7533
2097.176 | 208.6044 | 230.8952 | 222.4983
2098.176 | 208.8298 | 231.3852 | 222.6908
2099.176 | 209.2839 | 231.0271 | 222.8422
2100.176 | 209.9394 | 233.0567 | 222.9103
2101.176 | 210.3883 | 233.6518 | 222.8252
2102.176 | 211.056 | 233.8205 | 222.7969
2103.176 | 211.1817 | 231.5906 | 222.8895
2104.176 | 210.7186 | 228.9083 | 223.556
2105.176 | 211.0869 | 226.1718 | 223.7045
2106.176 | 211.6708 | 225.5456 | 223.588
2107.176 | 211.8557 | 225.0007 | 223.894
2108.176 | 212.0398 | 226.8951 | 223.7131
2109.176 | 212.0019 | 229.3781 | 223.9501
2110.176 | 212.2315 | 231.0161 | 224.1191
2111.176 | 212.0439 | 233.6419 | 224.4782
2112.176 | 212.1689 | 235.0662 | 224.1661
2113.176 | 212.241 | 234.365 | 224.8846
2114.176 | 212.4653 | 234.5539 | 224.6925
2115.176 | 212.0292 | 233.7039 | 224.4918
2116.176 | 212.0228 | 234.1928 | 224.6515
2117.176 | 212.3177 | 233.8523 | 224.3014
2118.176 | 212.7664 | 236.3033 | 223.7069
2119.176 | 212.5143 | 236.0883 | 223.4772
2120.176 | 212.2163 | 234.3247 | 222.8481
2121.176 | 212.2268 | 233.0409 | 222.7196
2122.176 | 212.4535 | 230.0867 | 222.8086
2123.176 | 212.3211 | 227.1183 | 222.4058
2124.176 | 212.1545 | 224.8012 | 222.0334
2125.176 | 212.2105 | 223.0415 | 221.9076
2126.176 | 212.4784 | 220.565 | 222.1253
2127.176 | 212.6536 | 220.2062 | 222.1495
2128.176 | 212.8562 | 219.2742 | 222.3816
2129.176 | 213.2339 | 219.7709 | 222.5118
2130.176 | 213.5986 | 223.2018 | 222.5788
2131.176 | 213.7749 | 228.2827 | 222.6603
2132.176 | 213.9051 | 231.8091 | 223.1123
2133.176 | 214.1403 | 232.0284 | 223.6351
2134.176 | 214.3312 | 232.1098 | 224.0595
2135.176 | 213.7954 | 231.6324 | 224.1672
2136.176 | 213.6037 | 233.5852 | 224.2107
2137.176 | 213.2326 | 237.0378 | 224.3559
2138.176 | 213.6596 | 235.8414 | 224.5375
2139.176 | 213.2174 | 234.3724 | 224.5141
2140.176 | 212.6197 | 232.5992 | 224.4832
2141.176 | 212.5895 | 230.3566 | 224.3495
2142.176 | 212.5806 | 228.7466 | 224.3654
2143.176 | 212.6102 | 237.938 | 224.7533
2144.176 | 212.2223 | 234.5448 | 224.9784
2145.176 | 212.0703 | 233.6789 | 225.2288
2146.176 | 211.5225 | 231.6425 | 225.8086
2147.176 | 211.2455 | 233.1011 | 225.7462
2148.176 | 211.1556 | 234.9743 | 226.3191
2149.176 | 210.7107 | 244.992 | 226.5379
2150.176 | 210.34 | 244.7681 | 226.4987
2151.176 | 210.116 | 244.749 | 226.1065
2152.176 | 209.8525 | 247.1452 | 225.9711
2153.176 | 209.6711 | 245.7169 | 226.025
2154.176 | 209.7779 | 242.212 | 225.7422
2155.176 | 209.747 | 239.0601 | 225.5056
2156.176 | 209.8794 | 236.0398 | 225.0608
2157.176 | 209.5281 | 233.2459 | 224.7187
2158.176 | 209.2504 | 231.8244 | 224.7789
2159.176 | 209.0255 | 229.0054 | 224.7546
2160.176 | 209.0525 | 230.1303 | 224.851
2161.176 | 208.7071 | 228.7146 | 224.7027
2162.176 | 208.7897 | 229.6799 | 224.4128
2163.176 | 208.4412 | 232.5215 | 223.8885
2164.176 | 208.3344 | 229.1831 | 223.4648
2165.176 | 208.3929 | 225.7381 | 223.1336
2166.176 | 208.8397 | 223.0917 | 222.715
2167.176 | 209.2714 | 218.9998 | 222.6565
2168.176 | 209.5812 | 215.2302 | 222.579
2169.176 | 209.381 | 214.0589 | 222.2315
2170.176 | 209.6144 | 214.7764 | 222.2102
2171.176 | 209.8488 | 213.3864 | 222.1833
2172.176 | 210.5259 | 213.8129 | 221.9321
2173.176 | 210.6468 | 215.4212 | 222.3025
2174.176 | 210.8587 | 216.0556 | 222.3885
2175.176 | 210.8609 | 215.6292 | 222.5204
2176.176 | 211.1848 | 215.1357 | 222.578
2177.176 | 211.6765 | 214.1792 | 222.7328
2178.176 | 211.5964 | 212.7296 | 222.5189
2179.176 | 211.8379 | 212.6424 | 222.82
2180.176 | 211.945 | 213.9167 | 222.819
2181.176 | 211.745 | 213.8627 | 222.7801
2182.176 | 212.22 | 217.0136 | 222.9451
2183.176 | 212.6265 | 219.3413 | 222.8318
2184.176 | 213.2594 | 223.5276 | 222.6617
2185.176 | 213.4163 | 226.4197 | 222.9644
2186.176 | 213.5965 | 225.3273 | 223.261
2187.176 | 213.6369 | 223.3429 | 223.4454
2188.176 | 214.0044 | 220.5668 | 223.2585
2189.176 | 214.3474 | 217.1956 | 223.1446
2190.176 | 214.3925 | 213.5312 | 223.1763
2191.176 | 214.1046 | 210.8291 | 223.0166
2192.176 | 214.0004 | 208.1888 | 223.2198
2193.176 | 213.9114 | 208.807 | 223.2897
2194.176 | 214.0136 | 208.0751 | 223.1665
2195.176 | 213.9061 | 207.6415 | 222.6932
2196.176 | 213.9805 | 203.8581 | 222.4026
2197.176 | 213.5796 | 202.1909 | 222.1411
2198.176 | 213.5315 | 199.9258 | 222.4096
2199.176 | 213.561 | 202.6334 | 222.5346
2200.176 | 213.1923 | 202.4323 | 222.9497
2201.176 | 212.9205 | 202.0815 | 223.2759
2202.176 | 212.5309 | 201.8431 | 223.207
2203.176 | 212.6054 | 200.8425 | 223.1578
2204.176 | 212.3013 | 201.3902 | 222.8441
2205.176 | 212.1219 | 203.271 | 222.5772
2206.176 | 211.7967 | 205.2696 | 222.3564
2207.176 | 211.5054 | 205.5908 | 222.5529
2208.176 | 211.2215 | 205.7427 | 222.0854
2209.176 | 211.0384 | 206.9488 | 222.3854
2210.176 | 211.0416 | 209.0315 | 222.0647
2211.176 | 210.653 | 209.6826 | 222.734
2212.1917 | 211.1171 | 208.3484 | 223.1882
2213.176 | 211.4861 | 207.9717 | 223.5854
2214.176 | 211.0337 | 207.931 | 223.9443
2215.176 | 210.6427 | 207.4895 | 224.4251
2216.176 | 210.7924 | 209.0715 | 224.1392
2217.176 | 210.6701 | 207.8094 | 223.7884
2218.176 | 210.6831 | 205.1699 | 223.468
2219.176 | 210.5134 | 206.0258 | 223.1948
2220.176 | 210.2115 | 206.4965 | 223.084
2221.176 | 209.8823 | 206.7738 | 222.7259
2222.176 | 209.6981 | 204.3171 | 222.681
2223.176 | 209.677 | 204.7656 | 222.0383
2224.176 | 209.5006 | 204.2191 | 221.9085
2225.176 | 209.5396 | 210.0214 | 222.3137
2226.176 | 209.4913 | 213.3206 | 222.6477
2227.176 | 209.3677 | 213.9186 | 222.4177
2228.176 | 209.1752 | 215.7639 | 222.286
2229.176 | 209.282 | 216.306 | 222.025
2230.176 | 209.1603 | 217.2557 | 221.8587
2231.176 | 208.9321 | 216.5596 | 222.114
2232.176 | 209.1204 | 216.7355 | 221.8203
2233.176 | 209.0009 | 214.87 | 221.815
2234.176 | 209.0006 | 212.779 | 221.8102
2235.176 | 208.8937 | 210.6357 | 221.5128
2236.176 | 208.902 | 210.6197 | 221.3996
2237.176 | 208.857 | 208.6462 | 221.2995
2238.176 | 208.6137 | 205.8758 | 220.9372
2239.176 | 208.3314 | 202.2565 | 220.8726
2240.176 | 208.1517 | 198.5445 | 220.6281
2241.176 | 208.052 | 195.9963 | 220.3377
2242.176 | 207.6714 | 193.9542 | 220.5981
2243.176 | 207.8121 | 191.8946 | 220.5611
2244.176 | 207.8504 | 192.008 | 220.5646
2245.176 | 207.8716 | 192.1362 | 220.3415
2246.176 | 207.7466 | 192.0766 | 220.2783
2247.176 | 207.7698 | 194.6705 | 220.2777
2248.176 | 207.6694 | 194.7235 | 220.4446
2249.176 | 207.7281 | 195.4935 | 220.9471
2250.176 | 207.81 | 196.9051 | 221.2325
2251.176 | 207.6423 | 198.1543 | 221.6452
2252.176 | 207.5428 | 200.2269 | 221.7067
2253.176 | 207.4432 | 203.3973 | 221.6205
2254.176 | 207.2694 | 203.4599 | 221.904
2255.176 | 207.1297 | 202.7053 | 222.1772
2256.176 | 207.2193 | 200.5321 | 222.1958
2257.176 | 207.615 | 199.6898 | 222.218
2258.176 | 207.6683 | 199.7056 | 222.4586
2259.176 | 207.7593 | 197.5954 | 222.218
2260.176 | 207.7711 | 198.0769 | 222.0747
2261.176 | 207.9642 | 197.338 | 222.1597
2262.176 | 208.0683 | 197.9559 | 221.9198
2263.176 | 208.1192 | 197.3146 | 222.1538
2264.176 | 208.081 | 196.1024 | 221.7233
2265.176 | 208.2091 | 195.9357 | 221.849
2266.176 | 208.2391 | 196.3201 | 221.7004
2267.176 | 207.9496 | 196.8747 | 222.2191
2268.176 | 208.2826 | 197.3199 | 222.4236
2269.176 | 208.1451 | 196.6482 | 222.8579
2270.176 | 208.25 | 194.9915 | 222.5798
2271.176 | 208.044 | 194.8988 | 223.4847
2272.1917 | 207.9117 | 197.0075 | 223.6871
2273.176 | 208.067 | 196.6302 | 223.5617
2274.176 | 207.792 | 197.1772 | 223.4003
2275.176 | 207.9521 | 199.9846 | 223.0151
2276.176 | 208.0533 | 201.0037 | 222.4095
2277.176 | 207.8966 | 199.4063 | 222.4086
2278.176 | 208.274 | 197.8869 | 222.0902
2279.176 | 207.9942 | 195.8319 | 222.2311
2280.176 | 208.1094 | 195.3231 | 221.7158
2281.176 | 207.9254 | 194.0715 | 221.4853
2282.176 | 208.2751 | 194.1428 | 221.4372
2283.176 | 208.1161 | 194.2543 | 221.7182
2284.176 | 208.7298 | 192.1334 | 221.5136
2285.176 | 209.3398 | 190.8861 | 221.4267
2286.176 | 209.8178 | 189.7038 | 221.4934
2287.176 | 209.9691 | 188.1532 | 221.4933
2288.176 | 210.0646 | 188.4063 | 221.3671
2289.176 | 210.1922 | 188.9159 | 221.1736
2290.176 | 210.6442 | 191.5785 | 221.2883
2291.176 | 210.9031 | 192.5986 | 221.6634
2292.176 | 210.9945 | 192.5446 | 222.0896
2293.176 | 210.9141 | 193.4978 | 222.0583
2294.176 | 211.0754 | 194.8433 | 222.3861
2295.176 | 210.749 | 198.4615 | 222.6876
2296.176 | 210.7354 | 202.1498 | 222.8557
2297.176 | 210.9512 | 206.7119 | 222.9077
2298.176 | 211.2084 | 206.9052 | 222.8372
2299.176 | 211.2684 | 207.5311 | 222.5715
2300.176 | 210.8536 | 210.168 | 222.911
2301.176 | 210.6774 | 209.3309 | 223.7763
2302.176 | 210.6834 | 207.835 | 223.8048
2303.176 | 210.5689 | 207.4872 | 224.4082
2304.176 | 210.3957 | 205.9682 | 224.7242
2305.176 | 210.594 | 205.7262 | 225.078
2306.176 | 210.4421 | 205.6629 | 225.4152
2307.176 | 210.6228 | 205.6681 | 225.425
2308.176 | 210.2906 | 208.8579 | 225.1973
2309.176 | 210.1229 | 209.0281 | 225.4335
2310.176 | 210.2491 | 206.8253 | 225.9169
2311.176 | 210.0956 | 206.0641 | 225.9268
2312.176 | 209.7793 | 205.936 | 225.6501
2313.176 | 209.7771 | 204.7269 | 225.9411
2314.176 | 209.9128 | 206.1502 | 226.0904
2315.176 | 210.0991 | 204.5942 | 226.3231
2316.176 | 210.2839 | 204.5698 | 226.5122
2317.176 | 210.3308 | 204.9009 | 226.1716
2318.176 | 210.1898 | 205.0251 | 226.0411
2319.176 | 210.3027 | 204.1914 | 226.1957
2320.176 | 210.2643 | 204.0551 | 226.8833
2321.176 | 210.1238 | 204.5051 | 226.9694
2322.176 | 210.0073 | 204.2491 | 226.9637
2323.176 | 209.8429 | 204.1504 | 227.1143
2324.176 | 209.9078 | 204.8921 | 226.8967
2325.176 | 210.0735 | 205.1926 | 226.9274
2326.176 | 209.7676 | 203.5376 | 227.0858
2327.176 | 209.5386 | 202.0064 | 227.2039
2328.176 | 209.6748 | 201.4062 | 227.0226
2329.176 | 209.8924 | 202.507 | 226.6872
2330.176 | 209.7231 | 202.4235 | 226.4378
2331.176 | 209.533 | 201.037 | 226.6608
2332.176 | 209.3722 | 200.6903 | 226.434
2333.176 | 209.1844 | 199.797 | 226.4063
2334.176 | 209.1196 | 199.9004 | 226.2693
2335.176 | 209.1095 | 199.7149 | 226.6201
2336.176 | 208.9874 | 199.6377 | 226.3414
2337.176 | 208.5878 | 200.6306 | 226.0924
2338.176 | 208.3543 | 203.1747 | 226.1052
2339.176 | 208.2577 | 203.1379 | 226.0185
2340.176 | 208.1953 | 202.9593 | 225.5664
2341.176 | 208.1945 | 201.4502 | 225.348
2342.176 | 208.1543 | 197.4401 | 225.172
2343.176 | 207.9115 | 195.5144 | 224.8467
2344.176 | 207.8194 | 194.4778 | 225.0606
2345.176 | 207.9795 | 193.1675 | 225.0258
2346.1917 | 207.9278 | 191.1514 | 224.5969
2347.1917 | 207.6281 | 190.2336 | 224.5225
2348.176 | 207.4629 | 187.1241 | 224.1151
2349.176 | 207.4757 | 183.9844 | 224.0312
2350.176 | 207.3287 | 182.0309 | 223.8671
2351.176 | 206.9397 | 179.2092 | 223.5492
2352.176 | 206.5453 | 178.5471 | 223.5185
2353.176 | 206.5511 | 178.9177 | 223.206
2354.176 | 206.6873 | 177.9381 | 223.2384
2355.176 | 206.7981 | 176.5467 | 223.4194
2356.176 | 206.6443 | 174.5864 | 223.2329
2357.176 | 206.8788 | 173.27 | 223.0165
2358.176 | 206.9974 | 173.048 | 222.9793
2359.176 | 207.131 | 173.5586 | 222.3639
2360.176 | 207.0344 | 174.4023 | 222.0142
2361.176 | 207.1679 | 173.2837 | 221.5693
2362.176 | 207.5831 | 171.501 | 221.2718
2363.176 | 207.9922 | 170.0923 | 221.401
2364.176 | 208.3801 | 168.6983 | 221.6006
2365.176 | 208.933 | 170.7802 | 221.477
2366.176 | 209.5786 | 172.3005 | 221.312
2367.176 | 209.7608 | 172.3237 | 221.4972
2368.176 | 209.5143 | 171.5414 | 221.4609
2369.176 | 210.1986 | 171.2091 | 221.3691
2370.176 | 210.4258 | 170.8035 | 221.1568
2371.176 | 211.0236 | 172.4695 | 221.2585
2372.176 | 211.469 | 174.392 | 221.5831
2373.176 | 211.7581 | 174.3312 | 221.6499
2374.176 | 211.7743 | 174.3834 | 221.6635
2375.176 | 211.6477 | 175.7351 | 222.0392
2376.176 | 211.2944 | 175.2662 | 222.4414
2377.176 | 211.2788 | 175.6115 | 222.6485
2378.176 | 211.4257 | 175.1547 | 222.5578
2379.176 | 211.286 | 174.3075 | 222.382
2380.176 | 211.6485 | 173.5732 | 222.3876
2381.176 | 212.2111 | 175.5865 | 222.5723
2382.176 | 211.9779 | 175.837 | 223.0349
2383.176 | 212.1498 | 178.8104 | 222.9664
2384.176 | 211.8271 | 181.8921 | 223.3079
2385.176 | 211.4916 | 181.2723 | 223.1304
2386.176 | 211.2559 | 181.1594 | 222.9378
2387.176 | 211.3341 | 180.9786 | 223.0094
2388.176 | 211.6183 | 178.247 | 222.8572
2389.176 | 211.658 | 176.3897 | 222.8433
2390.176 | 211.7269 | 173.8422 | 222.7363
2391.176 | 211.4162 | 173.0497 | 222.995
2392.176 | 211.0819 | 173.049 | 223.2406
2393.176 | 210.8552 | 174.5418 | 222.9234
2394.176 | 211.0857 | 179.3526 | 222.7535
2395.176 | 211.5678 | 181.1965 | 222.639
2396.176 | 211.5397 | 182.4665 | 222.6635
2397.176 | 211.1006 | 181.3057 | 223.0729
2398.176 | 210.8059 | 179.6891 | 223.3199
2399.176 | 210.8504 | 178.6066 | 223.114
2400.176 | 210.546 | 178.4592 | 223.0069
2401.176 | 210.4151 | 178.1154 | 222.9826
2402.176 | 210.1314 | 177.8446 | 222.6373
2403.176 | 210.1978 | 177.7526 | 222.7241
2404.176 | 210.77 | 177.8281 | 222.4506
2405.176 | 210.8176 | 178.2511 | 222.2259
2406.176 | 210.7312 | 179.0527 | 222.416
2407.176 | 210.4413 | 186.7971 | 222.7124
2408.176 | 210.5087 | 184.1709 | 222.8763
2409.176 | 210.5788 | 183.7431 | 223.1343
2410.176 | 211.0344 | 181.7193 | 222.9197
2411.176 | 211.0963 | 180.0205 | 223.0414
2412.176 | 210.8331 | 179.0964 | 222.7639
2413.176 | 210.4369 | 177.6717 | 222.3782
2414.176 | 210.2001 | 176.8623 | 222.1099
2415.176 | 210.0175 | 177.6485 | 221.8485
2416.176 | 209.8162 | 177.9871 | 221.7877
2417.176 | 209.7538 | 177.7177 | 222.1483
2418.176 | 209.8938 | 178.2035 | 222.0764
2419.176 | 209.9115 | 176.6892 | 222.5836
2420.176 | 209.6313 | 175.5369 | 222.6215
2421.176 | 209.6223 | 173.6052 | 222.7114
2422.176 | 209.4223 | 172.4198 | 222.5401
2423.176 | 209.113 | 170.559 | 222.428
2424.176 | 208.9073 | 169.7664 | 222.3942
2425.176 | 209.0002 | 167.7808 | 221.8611
2426.176 | 209.0706 | 167.0494 | 221.7877
2427.176 | 208.6931 | 167.2211 | 221.936
2428.176 | 208.6208 | 165.1471 | 221.7511
2429.176 | 208.4643 | 163.8493 | 221.9322
2430.176 | 208.4156 | 163.7435 | 221.6035
2431.176 | 208.4666 | 163.0185 | 221.2322
2432.176 | 208.6371 | 161.3954 | 220.9902
2433.176 | 208.74 | 159.4388 | 221.083
2434.176 | 208.664 | 159.0873 | 220.7843
2435.176 | 208.1626 | 158.4246 | 220.8066
2436.176 | 207.8844 | 158.0951 | 220.9117
2437.176 | 207.8931 | 157.2312 | 220.6041
2438.176 | 207.6393 | 156.2011 | 221.0704
2439.176 | 207.2939 | 157.7329 | 220.9985
2440.176 | 207.1673 | 158.5437 | 221.1795
2441.176 | 207.1023 | 158.0714 | 221.4243
2442.176 | 207.2062 | 156.5484 | 221.1327
2443.176 | 207.4544 | 155.3266 | 220.9092
2444.176 | 207.6303 | 154.7438 | 220.9236
2445.176 | 207.9838 | 155.0758 | 221.0988
2446.176 | 207.9847 | 154.783 | 221.4487
2447.176 | 207.8974 | 158.2812 | 221.7486
2448.176 | 207.8923 | 160.389 | 221.6607
2449.176 | 207.8269 | 158.1785 | 221.3325
2450.176 | 207.8665 | 156.9229 | 221.0578
2451.176 | 207.8953 | 155.3455 | 221.1183
2452.176 | 208.8045 | 154.6233 | 221.0086
2453.176 | 209.0156 | 155.3957 | 221.2897
2454.176 | 209.0121 | 155.8555 | 222.4282
2455.176 | 209.4725 | 157.3257 | 222.661
2456.176 | 209.583 | 159.4386 | 223.4284
2457.176 | 209.4414 | 159.8679 | 223.2385
2458.176 | 209.6192 | 161.5471 | 223.1656
2459.176 | 209.4762 | 162.773 | 223.3448
2460.176 | 209.7244 | 163.598 | 223.5093
2461.176 | 209.7724 | 163.9356 | 223.035
2462.176 | 209.8425 | 164.3079 | 223.2385
2463.176 | 210.2528 | 163.5282 | 222.8367
2464.176 | 210.1415 | 161.3125 | 222.6871
2465.176 | 209.9699 | 161.1339 | 222.7086
2466.176 | 210.1663 | 160.7198 | 222.789
2467.176 | 210.2314 | 160.5361 | 222.8016
2468.176 | 210.1986 | 160.904 | 222.8417
2469.176 | 210.2403 | 160.1399 | 222.8373
2470.176 | 210.3496 | 160.0282 | 223.0275
2471.176 | 210.0356 | 159.7522 | 223.1718
2472.176 | 209.9289 | 159.3162 | 223.4107
2473.176 | 209.7538 | 159.1447 | 223.5197
2474.176 | 209.8556 | 157.8438 | 223.8659
2475.176 | 209.8616 | 156.723 | 223.77
2476.176 | 209.7274 | 157.5497 | 223.6443
2477.176 | 209.7836 | 158.1122 | 223.5193
2478.176 | 209.6287 | 159.0387 | 223.3445
2479.176 | 209.379 | 158.7356 | 223.5343
2480.176 | 209.18 | 161.4345 | 223.4455
2481.176 | 209.1319 | 160.3625 | 223.1876
2482.176 | 209.0412 | 160.8954 | 222.975
2483.176 | 209.2941 | 159.635 | 222.6587
2484.176 | 209.1892 | 158.2065 | 222.6469
2485.176 | 209.2523 | 156.3646 | 222.5628
2486.176 | 209.275 | 154.5459 | 222.1816
2487.176 | 209.0118 | 153.0979 | 221.9328
2488.176 | 209.0085 | 151.531 | 221.6939
2489.176 | 209.0629 | 152.6757 | 222.1469
2490.176 | 209.0259 | 152.6162 | 222.1968
2491.176 | 209.0173 | 153.7975 | 221.9236
2492.176 | 208.9858 | 155.0079 | 221.827
2493.176 | 208.9275 | 158.8769 | 221.7838
2494.176 | 208.7969 | 160.5952 | 221.7827
2495.176 | 208.5486 | 161.2988 | 221.9184
2496.176 | 208.4026 | 161.912 | 221.9343
2497.176 | 208.4802 | 161.4547 | 221.6124
2498.176 | 208.3418 | 160.7233 | 222.1143
2499.176 | 208.3677 | 159.9764 | 221.8523
2500.176 | 208.5014 | 162.6621 | 221.8323
2501.176 | 208.4988 | 160.7758 | 221.9632
2502.176 | 208.3672 | 159.3396 | 221.7498
2503.176 | 208.421 | 158.6944 | 221.4415
2504.176 | 208.2643 | 157.9871 | 221.5055
2505.176 | 208.0982 | 156.6738 | 221.2472
2506.176 | 207.9784 | 155.5552 | 220.909
2507.176 | 207.7302 | 155.0219 | 220.7573
2508.176 | 207.5617 | 153.1064 | 220.4128
2509.176 | 207.8412 | 151.0981 | 220.3787
2510.176 | 207.8776 | 148.7493 | 220.3565
2511.176 | 208.1345 | 147.3675 | 220.526
2512.176 | 208.4321 | 149.3058 | 220.6143
2513.176 | 208.363 | 149.6112 | 220.8299
2514.176 | 208.2876 | 148.9239 | 220.9172
2515.176 | 208.5436 | 149.8326 | 220.9776
2516.176 | 208.4425 | 150.0236 | 221.2575
2517.176 | 208.4898 | 150.0627 | 221.8328
2518.176 | 208.6152 | 150.5285 | 221.8273
2519.176 | 208.6384 | 150.4692 | 221.7276
2520.176 | 208.2296 | 149.6069 | 221.6639
2521.176 | 208.1362 | 148.0762 | 221.5896
2522.176 | 208.3311 | 146.0026 | 221.3958
2523.176 | 208.0327 | 143.7249 | 221.2526
2524.176 | 208.1298 | 143.4313 | 220.9065
2525.176 | 208.3042 | 143.3657 | 220.7022
2526.176 | 208.251 | 144.6122 | 220.9208
2527.176 | 208.3443 | 143.3651 | 221.0223
2528.176 | 208.2251 | 142.3377 | 221.0283
2529.176 | 208.3779 | 141.4447 | 220.5263
2530.176 | 208.3382 | 141.649 | 220.2675
2531.176 | 208.4703 | 141.4886 | 220.0819
2532.176 | 208.7653 | 139.6479 | 219.8656
2533.176 | 208.7416 | 137.7108 | 219.5885
2534.176 | 209.0569 | 136.3069 | 219.6503
2535.176 | 209.2554 | 134.8922 | 219.4213
2536.176 | 209.39 | 134.799 | 219.2281
2537.176 | 209.5852 | 134.4099 | 219.1874
2538.176 | 209.7481 | 133.9177 | 219.314
2539.176 | 210.0074 | 134.9395 | 219.1287
2540.176 | 210.3158 | 136.9791 | 218.9427
2541.176 | 210.4925 | 137.3668 | 218.8162
2542.176 | 210.6617 | 137.52 | 218.694
2543.176 | 210.9796 | 137.5005 | 218.8501
2544.176 | 210.8659 | 137.3527 | 218.7549
2545.176 | 210.9123 | 136.4604 | 218.7856
2546.176 | 210.9884 | 136.2799 | 218.862
2547.176 | 210.7571 | 138.3037 | 218.9065
2548.176 | 210.4394 | 138.4404 | 219.3091
2549.176 | 209.9648 | 140.7812 | 219.1602
2550.176 | 209.9476 | 141.4796 | 219.0263
2551.176 | 209.9834 | 140.7027 | 219.1949
2552.176 | 210.6466 | 141.1594 | 219.4099
2553.176 | 210.5404 | 140.0857 | 219.4504
2554.176 | 210.5533 | 139.045 | 219.8605
2555.176 | 210.7355 | 138.6805 | 219.8918
2556.176 | 211.1053 | 138.8331 | 219.8949
2557.176 | 211.2099 | 138.9205 | 219.8807
2558.176 | 211.4599 | 138.8195 | 219.9835
2559.176 | 211.6779 | 138.4486 | 220.4693
2560.176 | 211.4098 | 138.5778 | 220.872
2561.176 | 211.4088 | 138.9052 | 221.158
2562.176 | 211.2817 | 140.8433 | 221.2839
2563.176 | 211.3035 | 141.6264 | 221.4548
2564.176 | 211.3282 | 141.606 | 221.3155
2565.176 | 211.2036 | 141.907 | 221.366
2566.176 | 211.1109 | 141.0932 | 221.7299
2567.176 | 211.0987 | 140.8407 | 221.7661
2568.176 | 211.0949 | 141.2287 | 221.7595
2569.176 | 211.6816 | 141.6998 | 221.7958
2570.176 | 211.7315 | 141.2323 | 221.6964
2571.176 | 212.0771 | 141.1714 | 221.4655
2572.176 | 211.9471 | 140.5605 | 221.3925
2573.176 | 212.0422 | 140.7741 | 221.3683
2574.176 | 212.1269 | 139.8032 | 221.4945
2575.176 | 212.3386 | 138.7797 | 221.5871
2576.176 | 212.4 | 138.1254 | 221.6605
2577.176 | 212.2964 | 137.8838 | 221.7329
2578.176 | 212.1073 | 138.0385 | 221.5912
2579.176 | 212.0418 | 138.4552 | 221.63
2580.176 | 212.2029 | 139.3596 | 221.5424
2581.176 | 211.9356 | 140.8138 | 221.9248
2582.176 | 211.8095 | 142.8416 | 221.9299
2583.176 | 211.8495 | 142.4089 | 222.5823
2584.176 | 211.7576 | 142.5418 | 222.8546
2585.176 | 211.531 | 142.2498 | 222.7289
2586.176 | 211.5795 | 141.2201 | 222.8311
2587.176 | 211.7538 | 140.6329 | 222.6545
2588.176 | 211.4913 | 141.5333 | 222.6047
2589.176 | 211.7547 | 144.4661 | 222.8809
2590.176 | 211.9967 | 144.2426 | 223.166
2591.176 | 212.0227 | 146.9355 | 222.921
2592.176 | 211.9751 | 147.9129 | 222.8045
2593.176 | 211.7058 | 147.0563 | 222.7021
2594.176 | 211.7433 | 145.4956 | 222.7296
2595.176 | 211.7987 | 144.2956 | 222.7291
2596.176 | 211.6255 | 143.5573 | 222.4488
2597.176 | 211.6214 | 143.7826 | 222.2838
2598.176 | 211.4235 | 144.1075 | 222.3238
2599.176 | 211.5515 | 143.4384 | 222.1925
2600.176 | 211.5839 | 142.8481 | 221.7961
2601.176 | 211.4503 | 143.1518 | 221.8718
2602.176 | 211.5409 | 143.8808 | 221.7465
2603.176 | 211.5229 | 142.1973 | 221.6835
2604.176 | 211.8632 | 140.3596 | 221.6966
2605.176 | 212.0488 | 139.1608 | 221.6206
2606.176 | 212.5228 | 138.017 | 221.5278
2607.176 | 212.5979 | 137.3321 | 221.8022
2608.176 | 212.4793 | 136.3294 | 221.8867
2609.176 | 212.1237 | 135.3935 | 221.8796
2610.176 | 212.1369 | 134.1895 | 222.4172
2611.176 | 212.6385 | 133.6489 | 222.4647
2612.176 | 212.9655 | 133.2487 | 222.4368
2613.176 | 213.076 | 133.6793 | 222.4783
2614.176 | 212.9993 | 134.08 | 222.4556
2615.176 | 213.0225 | 134.0539 | 222.1856
2616.176 | 213.1254 | 135.6694 | 222.44
2617.176 | 213.4716 | 135.2276 | 222.6514
2618.176 | 213.4525 | 134.2492 | 222.5624
2619.176 | 213.7495 | 134.4965 | 222.8112
2620.176 | 213.9048 | 134.8618 | 222.8668
2621.176 | 213.5387 | 137.6576 | 223.1337
2622.176 | 213.3736 | 137.2462 | 223.0065
2623.176 | 212.9264 | 137.8488 | 222.5279
2624.176 | 212.6809 | 137.2509 | 222.3042
2625.176 | 212.465 | 136.3947 | 222.2672
2626.176 | 212.4149 | 135.6565 | 222.3919
2627.176 | 212.0573 | 135.4415 | 221.9196
2628.176 | 212.1165 | 134.4872 | 221.7687
2629.176 | 212.2726 | 133.4668 | 221.6288
2630.176 | 212.2289 | 132.1833 | 221.6262
2631.176 | 212.2268 | 130.9101 | 221.6511
2632.176 | 212.3627 | 129.5808 | 221.8737
2633.176 | 212.2578 | 128.0426 | 222.0183
2634.176 | 212.241 | 127.7382 | 221.8766
2635.176 | 212.0997 | 128.3746 | 221.9327
2636.176 | 212.1561 | 128.4633 | 222.0331
2637.176 | 212.5365 | 127.4735 | 222.0933
2638.176 | 212.5357 | 126.9831 | 221.8675
2639.176 | 212.2455 | 126.4092 | 221.7474
2640.176 | 212.2837 | 126.7347 | 221.9094
2641.176 | 212.1096 | 128.668 | 222.1012
2642.176 | 212.1009 | 132.6123 | 222.1021
2643.176 | 212.4558 | 134.598 | 221.8269
2644.176 | 212.2672 | 135.6421 | 221.7049
2645.176 | 212.2229 | 134.8449 | 221.9285
2646.176 | 212.3647 | 133.454 | 222.1896
2647.176 | 212.1723 | 131.1958 | 222.2204
2648.176 | 211.9264 | 129.3367 | 222.3496
2649.176 | 211.9689 | 128.8827 | 222.2966
2650.176 | 211.8234 | 131.7826 | 222.1335
2651.176 | 211.7399 | 132.6003 | 222.1793
2652.176 | 211.5878 | 132.0715 | 222.04
2653.176 | 211.4377 | 131.3302 | 222.088
2654.176 | 211.4927 | 131.6766 | 221.9582
2655.176 | 211.4742 | 131.9029 | 222.4698
2656.176 | 211.3636 | 133.112 | 222.5554
2657.176 | 211.3645 | 134.735 | 222.645
2658.176 | 211.0988 | 134.9154 | 222.8471
2659.176 | 211.1572 | 136.1441 | 222.8319
2660.176 | 210.8919 | 137.1449 | 222.9031
2661.176 | 210.6647 | 139.2904 | 222.8854
2662.176 | 210.3492 | 140.0636 | 222.9955
2663.176 | 210.0773 | 139.2464 | 223.0363
2664.176 | 210.0112 | 137.7346 | 222.9126
2665.176 | 210.4163 | 138.4968 | 222.9645
2666.176 | 210.4309 | 138.4547 | 222.8509
2667.176 | 210.5656 | 140.1456 | 223.4208
2668.176 | 210.5159 | 142.6051 | 224.4428
2669.176 | 210.4813 | 143.0569 | 224.7931
2670.176 | 210.9025 | 143.7961 | 225.2103
2671.176 | 211.0382 | 147.9441 | 225.4078
2672.176 | 211.1166 | 148.5353 | 225.197
2673.176 | 210.9701 | 149.1423 | 225.0649
2674.176 | 210.9508 | 149.3983 | 225.2133
2675.176 | 210.5943 | 148.1276 | 224.9023
2676.176 | 210.6012 | 147.5874 | 225.2782
2677.176 | 210.4177 | 147.728 | 225.5304
2678.176 | 210.2226 | 146.4468 | 225.4471
2679.176 | 210.1995 | 144.6893 | 225.1871
2680.176 | 210.1807 | 144.4177 | 225.1615
2681.176 | 209.9702 | 143.4004 | 224.8429
2682.176 | 209.9597 | 141.7767 | 224.2139
2683.176 | 209.8954 | 141.8543 | 224.1617
2684.176 | 209.5103 | 142.6654 | 223.7168
2685.176 | 209.3114 | 142.6302 | 223.5467
2686.176 | 209.1209 | 144.7156 | 223.2482
2687.176 | 209.1064 | 146.4959 | 223.3606
2688.176 | 208.882 | 146.2492 | 223.9111
2689.176 | 208.8616 | 146.1596 | 223.6748
2690.176 | 208.8559 | 145.4018 | 223.9917
2691.176 | 208.6738 | 144.8463 | 223.9128
2692.176 | 209.0195 | 144.8624 | 223.8736
2693.176 | 209.325 | 144.7061 | 223.7085
2694.176 | 209.4547 | 143.5455 | 223.4798
2695.176 | 209.5132 | 141.9192 | 223.5912
2696.176 | 209.4982 | 139.2934 | 223.4271
2697.176 | 209.1626 | 137.7971 | 222.9006
2698.176 | 208.9239 | 137.4311 | 222.4959
2699.176 | 208.9822 | 136.6171 | 222.4719
2700.176 | 208.8461 | 136.1065 | 222.0928
2701.176 | 208.8673 | 136.1415 | 221.8296
2702.176 | 208.8047 | 135.1068 | 221.9726
2703.176 | 208.9024 | 133.1329 | 221.8326
2704.176 | 208.8675 | 134.2269 | 221.6064
2705.176 | 208.783 | 133.3804 | 221.2357
2706.176 | 208.4866 | 133.116 | 220.7628
2707.176 | 208.4184 | 132.7115 | 220.5093
2708.176 | 208.4087 | 132.6257 | 220.6555
2709.176 | 208.3521 | 130.3629 | 220.3704
2710.176 | 208.375 | 128.2597 | 219.9395
2711.176 | 208.5098 | 126.735 | 219.9351
2712.176 | 208.6724 | 125.3098 | 219.7501
2713.176 | 208.7678 | 125.7907 | 219.7377
2714.176 | 208.7816 | 124.2147 | 219.5619
2715.176 | 209.1914 | 122.7165 | 219.6612
2716.176 | 209.4891 | 122.7594 | 219.7942
2717.176 | 209.6699 | 122.866 | 220.1465
2718.176 | 209.439 | 122.521 | 220.6586
2719.176 | 209.6287 | 122.5117 | 220.8831
2720.176 | 209.5464 | 122.9205 | 220.9047
2721.176 | 209.4559 | 122.2684 | 220.8766
2722.176 | 209.1965 | 121.6123 | 220.8467
2723.176 | 209.1591 | 120.1566 | 220.9045
2724.176 | 209.2273 | 119.0519 | 220.6159
2725.176 | 209.1837 | 118.6534 | 220.4802
2726.176 | 209.2437 | 118.1761 | 220.4145
2727.176 | 209.047 | 117.375 | 220.8852
2728.176 | 208.9888 | 117.2818 | 220.5112
2729.176 | 208.906 | 118.0106 | 220.1003
2730.176 | 208.9311 | 116.4625 | 219.8556
2731.176 | 208.5709 | 115.6413 | 219.9958
2732.176 | 208.5158 | 113.9436 | 219.6763
2733.176 | 208.4455 | 112.3199 | 219.6525
2734.176 | 208.6238 | 111.5875 | 219.5598
2735.176 | 208.6283 | 111.0234 | 219.8113
2736.176 | 208.6897 | 110.679 | 220.0828
2737.176 | 208.7242 | 109.6551 | 219.9715
2738.176 | 208.7318 | 110.3362 | 219.9975
2739.176 | 208.8142 | 110.304 | 220.1974
2740.176 | 208.9688 | 110.1537 | 220.0149
2741.176 | 209.0049 | 110.3444 | 220.2436
2742.176 | 208.9893 | 111.2364 | 219.8198
2743.176 | 209.0347 | 113.2879 | 219.9667
2744.176 | 208.956 | 113.2847 | 219.5984
2745.176 | 208.8504 | 112.5513 | 219.4481
2746.176 | 208.7486 | 111.5606 | 219.5207
2747.176 | 208.6369 | 110.9503 | 219.5602
2748.176 | 208.6382 | 111.5989 | 219.561
2749.176 | 208.8287 | 112.8128 | 219.6799
2750.176 | 208.9962 | 113.4123 | 219.7572
2751.176 | 209.0349 | 112.8302 | 220.2398
2752.176 | 208.7311 | 112.6257 | 220.1432
2753.176 | 208.5359 | 112.39 | 220.3852
2754.176 | 208.387 | 112.9154 | 220.7034
2755.176 | 208.5182 | 113.2134 | 221.3532
2756.176 | 208.605 | 117.9197 | 221.2027
2757.176 | 208.4188 | 117.2993 | 221.7391
2758.176 | 208.4058 | 119.0717 | 221.7569
2759.176 | 208.3179 | 120.4023 | 221.5752
2760.176 | 208.5295 | 120.3293 | 221.802
2761.176 | 208.5877 | 120.0955 | 221.7909
2762.176 | 208.6078 | 120.6338 | 222.0166
2763.176 | 208.5209 | 121.1773 | 222.2232
2764.176 | 208.8202 | 120.6278 | 221.8388
2765.176 | 208.7145 | 121.4488 | 221.7707
2766.176 | 208.891 | 122.2865 | 221.4474
2767.176 | 209.045 | 122.974 | 222.0159
2768.176 | 209.0523 | 123.2889 | 222.4251
2769.176 | 209.4063 | 123.584 | 222.4912
2770.176 | 209.5167 | 124.5738 | 222.8284
2771.176 | 209.6056 | 125.2338 | 223.0416
2772.176 | 209.4128 | 124.5891 | 223.1406
2773.176 | 209.1089 | 123.838 | 223.1125
2774.176 | 208.8745 | 123.8099 | 223.2671
2775.176 | 208.7463 | 124.5845 | 223.4612
2776.176 | 208.7356 | 123.8114 | 223.5755
2777.176 | 208.4883 | 124.3654 | 223.2075
2778.176 | 208.3237 | 123.3537 | 222.8291
2779.176 | 208.1087 | 122.0446 | 222.8572
2780.176 | 208.1998 | 121.7805 | 222.5786
2781.176 | 208.3418 | 121.4213 | 222.3528
2782.176 | 208.1216 | 120.9637 | 222.33
2783.176 | 208.0639 | 120.5813 | 222.2149
2784.176 | 208.4226 | 119.853 | 222.1002
2785.176 | 209.0022 | 119.9448 | 222.0006
2786.176 | 209.447 | 120.4347 | 221.8556
2787.176 | 209.699 | 120.3599 | 221.6804
2788.176 | 209.6481 | 120.857 | 221.7619
2789.176 | 209.4975 | 120.3309 | 221.8802
2790.176 | 209.6348 | 120.5899 | 221.8855
2791.176 | 209.93 | 121.8729 | 221.8663
2792.176 | 210.4209 | 122.2411 | 221.8141
2793.176 | 210.8678 | 122.6581 | 221.7265
2794.176 | 210.925 | 122.312 | 221.6728
2795.176 | 210.8153 | 121.6347 | 221.997
2796.176 | 211.0565 | 124.3445 | 222.1082
2797.176 | 211.3584 | 124.8417 | 221.9314
2798.176 | 211.6186 | 126.5209 | 221.7073
2799.176 | 212.1668 | 127.3014 | 222.0185
2800.176 | 211.6988 | 130.67 | 222.3571
2801.176 | 211.8953 | 136.3636 | 222.8411
2802.176 | 211.9884 | 136.2927 | 223.3463
2803.176 | 211.6976 | 136.2175 | 223.4432
2804.176 | 211.6764 | 135.5193 | 223.4349
2805.176 | 211.57 | 133.8156 | 223.2281
2806.176 | 211.6417 | 131.6398 | 222.9839
2807.176 | 211.5799 | 129.9139 | 223.1501
2808.176 | 211.2648 | 128.2603 | 222.6537
2809.176 | 211.2363 | 126.8641 | 222.4008
2810.176 | 211.4255 | 127.3464 | 222.0797
2811.176 | 211.6514 | 126.1029 | 222.7996
2812.176 | 211.9309 | 125.197 | 222.5366
2813.176 | 211.9311 | 126.4244 | 222.7497
2814.176 | 211.8467 | 127.202 | 222.7035
2815.176 | 211.775 | 127.9118 | 222.77
2816.176 | 211.7993 | 129.229 | 222.9212
2817.176 | 211.7167 | 129.5287 | 223.3825
2818.176 | 211.5914 | 129.1773 | 223.428
2819.176 | 211.6428 | 128.7887 | 223.4837
2820.176 | 211.7804 | 128.9678 | 223.6164
2821.176 | 211.7736 | 128.833 | 223.5328
2822.176 | 211.9365 | 130.5675 | 223.7193
2823.176 | 211.6059 | 131.8038 | 223.8438
2824.176 | 211.6476 | 131.8211 | 224.3795
2825.176 | 211.3718 | 132.7916 | 223.9579
2826.176 | 211.4237 | 131.2601 | 223.5937
2827.176 | 211.2704 | 129.2272 | 223.5107
2828.176 | 211.1377 | 127.4645 | 223.2497
2829.176 | 211.0364 | 128.3522 | 223.0459
2830.176 | 211.5205 | 127.784 | 222.906
2831.176 | 211.9869 | 126.3224 | 222.9682
2832.176 | 212.1982 | 124.7193 | 222.8135
2833.176 | 212.042 | 123.7856 | 222.6313
2834.176 | 212.3469 | 122.6668 | 222.7295
2835.176 | 212.3213 | 122.5436 | 222.6462
2836.176 | 212.7978 | 122.1527 | 222.77
2837.176 | 213.4365 | 120.9043 | 222.7964
2838.176 | 213.4122 | 119.3494 | 222.9864
2839.176 | 213.4027 | 118.7648 | 222.9792
2840.176 | 213.8254 | 117.4356 | 222.8334
2841.176 | 213.5128 | 115.7616 | 222.6283
2842.176 | 213.6122 | 115.0565 | 222.5
2843.176 | 214.0397 | 114.8098 | 222.4014
2844.176 | 213.8593 | 114.7238 | 222.5502
2845.176 | 213.9119 | 116.2508 | 222.3232
2846.176 | 213.7521 | 116.8527 | 222.5478
2847.176 | 213.8446 | 117.9183 | 222.5711
2848.176 | 213.7129 | 118.9019 | 222.8008
2849.176 | 213.7643 | 119.2797 | 222.9521
2850.176 | 213.6441 | 120.4998 | 222.7735
2851.176 | 213.4443 | 120.8269 | 223.3455
2852.176 | 213.2609 | 120.7186 | 223.4072
2853.176 | 212.9769 | 119.9038 | 223.2013
2854.176 | 212.668 | 122.6567 | 223.1576
2855.176 | 212.3418 | 122.5191 | 223.2248
2856.176 | 212.1416 | 122.3095 | 223.2652
2857.176 | 211.9837 | 122.5627 | 223.2478
2858.176 | 211.9119 | 122.0832 | 223.4289
2859.176 | 211.8559 | 121.9867 | 223.3463
2860.176 | 211.7392 | 122.4326 | 223.3738
2861.176 | 211.9909 | 122.5168 | 223.0393
2862.176 | 212.0251 | 121.7002 | 223.1952
2863.176 | 212.237 | 120.4529 | 223.1293
2864.176 | 212.4648 | 119.2923 | 223.1133
2865.176 | 212.3604 | 117.552 | 222.8658
2866.176 | 212.2197 | 117.1847 | 222.7089
2867.176 | 212.3185 | 117.2079 | 222.7699
2868.176 | 212.7482 | 117.2241 | 222.8013
2869.176 | 213.1948 | 116.8485 | 222.9313
2870.176 | 213.1018 | 116.6296 | 223.1158
2871.176 | 213.1117 | 116.5654 | 223.2534
2872.176 | 213.1607 | 115.7878 | 223.3391
2873.176 | 213.1568 | 116.0334 | 223.2676
2874.176 | 213.0916 | 114.6532 | 223.053
2875.176 | 213.099 | 113.5171 | 222.9203
2876.176 | 213.2214 | 113.6586 | 222.8254
2877.176 | 212.9503 | 115.7904 | 222.7689
2878.176 | 212.794 | 118.6719 | 223.3009
2879.176 | 212.6816 | 118.2682 | 223.6967
2880.176 | 212.6623 | 116.5881 | 223.7307
2881.176 | 212.6977 | 115.0627 | 223.6069
2882.176 | 212.7282 | 115.6313 | 223.5076
2883.176 | 212.6527 | 114.0129 | 223.2769
2884.176 | 212.5093 | 113.0077 | 223.3565
2885.176 | 212.4997 | 112.3649 | 222.9886
2886.176 | 212.5652 | 112.2124 | 222.8696
2887.176 | 212.3481 | 112.05 | 222.5999
2888.176 | 212.2564 | 111.9095 | 222.2301
2889.176 | 212.408 | 110.8108 | 222.0695
2890.176 | 212.668 | 109.8893 | 221.7957
2891.176 | 212.6447 | 107.79 | 221.6611
2892.176 | 213.4383 | 106.1568 | 221.3491
2893.176 | 213.5135 | 104.5045 | 221.1886
2894.176 | 213.475 | 104.0234 | 221.1305
2895.176 | 213.6746 | 105.7918 | 221.3254
2896.176 | 213.8689 | 109.1149 | 221.2436
2897.176 | 214.2684 | 110.1316 | 221.3268
2898.176 | 214.6052 | 110.7992 | 221.183
2899.176 | 214.5406 | 111.9438 | 221.5219
2900.176 | 214.2969 | 113.5061 | 221.6306
2901.176 | 214.47 | 115.662 | 221.5968
2902.176 | 214.3539 | 116.6199 | 222.5224
2903.176 | 214.5576 | 118.2154 | 222.9307
2904.176 | 214.3922 | 118.0305 | 223.276
2905.176 | 214.3923 | 117.4189 | 223.0962
2906.176 | 214.2641 | 118.0412 | 223.234
2907.176 | 214.2506 | 118.0632 | 223.1162
2908.176 | 214.113 | 117.709 | 223.4964
2909.176 | 214.3149 | 116.0924 | 223.2757
2910.176 | 214.496 | 116.3324 | 223.3785
2911.176 | 214.4702 | 118.5364 | 223.0719
2912.176 | 214.328 | 118.3411 | 222.6696
2913.176 | 214.4127 | 117.1668 | 222.3263
2914.176 | 214.4568 | 117.55 | 222.2371
2915.176 | 214.3593 | 116.8201 | 221.9354
2916.176 | 214.1396 | 115.8814 | 221.5832
2917.176 | 213.9608 | 114.5735 | 221.3212
2918.176 | 213.8365 | 114.1362 | 221.3111
2919.176 | 213.6361 | 113.5222 | 221.0122
2920.176 | 213.7517 | 112.7883 | 220.8196
2921.176 | 213.9693 | 112.3918 | 220.9977
2922.176 | 214.0037 | 111.7128 | 221.0229
2923.176 | 213.8563 | 111.1085 | 221.501
2924.176 | 213.7296 | 110.7823 | 221.6804
2925.176 | 213.5257 | 110.5233 | 221.8141
2926.176 | 213.0835 | 110.7254 | 222.1886
2927.176 | 212.8952 | 111.0961 | 222.1912
2928.176 | 212.7137 | 111.1504 | 222.2947
2929.176 | 212.8381 | 110.1999 | 222.2487
2930.176 | 213.1773 | 110.7244 | 221.9832
2931.176 | 213.2246 | 109.865 | 221.8286
2932.176 | 213.358 | 109.3868 | 221.6278
2933.176 | 213.3415 | 110.1172 | 222.0337
2934.176 | 213.0358 | 109.6473 | 221.7647
2935.176 | 213.0233 | 109.5656 | 221.8182
2936.176 | 213.1582 | 109.4952 | 221.9424
2937.176 | 213.0753 | 110.3422 | 221.8772
2938.176 | 212.8594 | 110.846 | 222.0478
2939.176 | 212.5206 | 110.8428 | 221.9945
2940.176 | 212.2413 | 111.2987 | 221.7341
2941.176 | 212.0707 | 112.4813 | 221.4617
2942.176 | 212.3334 | 113.5633 | 221.4878
2943.176 | 212.277 | 115.2329 | 221.1536
2944.176 | 212.302 | 115.0106 | 221.3308
2945.176 | 212.3711 | 113.8439 | 221.1826
2946.176 | 212.2495 | 113.0711 | 221.3448
2947.176 | 212.3512 | 111.6062 | 221.4368
2948.176 | 212.6297 | 110.5522 | 221.598
2949.176 | 213.2503 | 109.5275 | 221.5028
2950.176 | 213.2475 | 108.8164 | 221.4746
2951.176 | 213.1282 | 109.8014 | 221.3938
2952.176 | 213.0916 | 109.2332 | 221.2583
2953.176 | 213.0566 | 108.6963 | 221.0239
2954.176 | 213.3335 | 107.5157 | 221.0426
2955.176 | 213.6335 | 106.3533 | 221.1492
2956.176 | 213.7602 | 105.3806 | 221.1004
2957.176 | 213.5184 | 105.2225 | 221.1788
2958.176 | 213.1599 | 106.0529 | 221.853
2959.176 | 213.2517 | 107.7186 | 221.8519
2960.176 | 213.394 | 108.7696 | 221.9724
2961.176 | 213.4053 | 108.0103 | 222.2939
2962.176 | 213.0911 | 108.5906 | 222.2341
2963.176 | 212.9501 | 109.4632 | 222.2957
2964.176 | 212.851 | 108.1941 | 222.1443
2965.176 | 212.8507 | 106.4961 | 221.8176
2966.176 | 212.7166 | 105.3299 | 221.7498
2967.176 | 212.6959 | 105.1288 | 221.9203
2968.176 | 212.75 | 105.1491 | 221.6933
2969.176 | 212.4621 | 104.2014 | 221.6368
2970.176 | 212.3268 | 105.8195 | 221.6311
2971.176 | 212.2343 | 105.5326 | 221.5177
2972.176 | 211.9699 | 105.6247 | 221.194
2973.176 | 212.1116 | 104.5116 | 220.9625
2974.176 | 212.0896 | 104.0216 | 220.8288
2975.1917 | 211.9432 | 103.17 | 221.3499
2976.1917 | 211.9474 | 102.0632 | 221.9209
2977.176 | 211.8589 | 103.9354 | 221.8832
2978.176 | 212.013 | 105.2218 | 222.0625
2979.176 | 212.1429 | 105.6907 | 222.4419
2980.176 | 212.2863 | 105.6513 | 222.7992
2981.176 | 212.6674 | 106.2479 | 222.6445
2982.176 | 212.6986 | 107.7073 | 222.8012
2983.1917 | 212.8405 | 109.4764 | 223.3907
2984.1917 | 212.6835 | 109.8622 | 223.5603
2985.1917 | 212.6224 | 110.7566 | 223.7873
2986.176 | 212.321 | 111.1631 | 223.6552
2987.176 | 212.3069 | 111.34 | 223.671
2988.176 | 212.3125 | 111.0468 | 223.7421
2989.176 | 212.3754 | 110.124 | 224.1617
2990.176 | 212.1 | 109.9457 | 224.1936
2991.176 | 212.1039 | 111.9101 | 224.1961
2992.176 | 211.9943 | 110.9853 | 224.0487
2993.176 | 211.9633 | 110.9915 | 223.7192
2994.176 | 212.0438 | 110.6464 | 223.557
2995.176 | 212.2655 | 109.7789 | 223.2238
2996.176 | 212.6659 | 109.4078 | 223.3195
2997.176 | 212.6955 | 108.3905 | 223.4392
2998.176 | 212.8188 | 107.9866 | 223.2797
2999.176 | 212.9936 | 108.1406 | 222.8581
3000.176 | 212.9893 | 106.3004 | 222.6838
3001.176 | 212.7216 | 104.4439 | 222.4356
3002.176 | 212.5753 | 103.1916 | 222.8802
3003.176 | 212.2714 | 102.5867 | 223.1625
3004.176 | 212.1727 | 101.2051 | 223.0939
3005.176 | 212.4385 | 99.7942 | 222.9962
3006.176 | 212.7711 | 98.9746 | 223.1833
3007.176 | 212.8918 | 98.0154 | 223.28
3008.176 | 213.2795 | 98.6662 | 223.3873
3009.176 | 213.6688 | 101.3597 | 223.3983
3010.176 | 213.8181 | 102.2105 | 223.4047
3011.176 | 213.9541 | 102.0387 | 223.4581
3012.176 | 213.6473 | 101.6827 | 223.528
3013.176 | 213.4846 | 101.5797 | 223.3696
3014.176 | 213.4243 | 100.9691 | 223.4656
3015.176 | 213.8136 | 99.9855 | 223.6585
3016.176 | 214.0221 | 99.3715 | 223.7114
3017.176 | 213.8026 | 99.0031 | 223.6945
3018.176 | 213.6236 | 99.1923 | 223.6317
3019.176 | 213.3721 | 98.8982 | 223.364
3020.176 | 213.569 | 98.5731 | 223.1825
3021.176 | 213.7115 | 97.4045 | 223.0393
3022.176 | 213.7698 | 96.1729 | 222.9811
3023.176 | 213.6674 | 95.3346 | 223.0138
3024.176 | 213.8632 | 94.2678 | 222.8081
3025.176 | 213.8496 | 93.2212 | 222.8807
3026.176 | 213.947 | 93.1892 | 222.8141
3027.176 | 214.1326 | 92.8837 | 222.9215
3028.176 | 214.3065 | 93.5054 | 222.6707
3029.176 | 214.2703 | 94.0149 | 223.3021
3030.176 | 214.5986 | 95.6466 | 223.4174
3031.176 | 214.6507 | 95.9536 | 223.6353
3032.176 | 214.4532 | 94.9539 | 223.6641
3033.176 | 214.1166 | 94.3324 | 223.4533
3034.176 | 214.1062 | 94.3934 | 223.3041
3035.176 | 213.9403 | 94.9704 | 222.956
3036.176 | 213.8095 | 95.6045 | 222.6264
3037.176 | 213.6288 | 95.7385 | 222.4699
3038.176 | 213.4578 | 95.3001 | 222.2469
3039.176 | 213.5738 | 95.854 | 222.3816
3040.176 | 213.5171 | 96.1376 | 222.1169
3041.176 | 213.5599 | 96.2949 | 222.9997
3042.176 | 213.3873 | 96.7786 | 223.3341
3043.176 | 213.3951 | 98.0181 | 223.3653
3044.176 | 213.075 | 98.8886 | 223.779
3045.176 | 212.9309 | 99.9518 | 223.9605
3046.176 | 212.8834 | 100.9003 | 224.2515
3047.176 | 212.9398 | 100.4918 | 224.4814
3048.176 | 212.5793 | 100.9487 | 224.1704
3049.176 | 212.5188 | 102.1566 | 224.2288
3050.176 | 212.4756 | 102.3816 | 224.3957
3051.176 | 212.2184 | 102.5578 | 224.649
3052.176 | 212.0463 | 101.8952 | 224.4841
3053.176 | 212.0366 | 101.6236 | 224.2506
3054.176 | 211.9277 | 101.2888 | 223.9034
3055.176 | 211.9434 | 100.8175 | 223.8027
3056.176 | 212.0162 | 100.3953 | 223.3567
3057.176 | 212.179 | 99.5354 | 223.1005
3058.176 | 212.1068 | 98.677 | 223.0697
3059.176 | 212.1951 | 99.3434 | 222.9387
3060.176 | 212.1398 | 101.1551 | 222.9395
3061.176 | 212.0583 | 101.2852 | 223.2287
3062.176 | 212.0337 | 100.9052 | 223.6688
3063.176 | 212.1269 | 100.1532 | 224.0972
3064.176 | 212.2717 | 100.27 | 224.079
3065.176 | 212.2853 | 100.5462 | 224.1565
3066.176 | 212.0884 | 99.5417 | 224.0968
3067.176 | 211.9239 | 97.848 | 224.188
3068.176 | 212.1869 | 96.214 | 223.826
3069.176 | 212.3397 | 94.7828 | 223.6581
3070.176 | 212.7741 | 93.5775 | 223.4055
3071.176 | 213.0483 | 92.2622 | 223.6009
3072.176 | 213.1733 | 93.1254 | 223.6047
3073.176 | 213.0702 | 92.5813 | 223.5225
3074.176 | 212.8965 | 91.8984 | 223.3953
3075.176 | 212.9428 | 92.3797 | 223.468
3076.176 | 213.4328 | 92.559 | 223.2373
3077.176 | 214.0283 | 93.0662 | 223.1619
3078.176 | 214.3779 | 93.9093 | 223.4485
3079.176 | 214.5907 | 93.7172 | 223.7698
3080.176 | 214.5689 | 94.9773 | 224.1572
3081.176 | 214.7845 | 97.0647 | 224.4909
3082.176 | 214.728 | 99.4109 | 224.0333
3083.176 | 214.8124 | 100.5635 | 224.2991
3084.176 | 214.401 | 100.3059 | 223.8777
3085.176 | 214.1923 | 101.6936 | 223.5864
3086.176 | 214.2101 | 102.2767 | 223.4051
3087.176 | 215.1213 | 101.5657 | 223.1411
3088.176 | 215.3037 | 100.7462 | 223.0239
3089.176 | 215.2014 | 99.8055 | 223.2352
3090.176 | 215.1769 | 100.1969 | 223.4539
3091.176 | 215.3491 | 100.9955 | 223.6937
3092.176 | 215.3928 | 101.1008 | 224.8886
3093.176 | 215.359 | 101.9573 | 225.4615
3094.176 | 215.3948 | 102.6588 | 225.6014
3095.176 | 215.4265 | 103.7947 | 225.7959
3096.176 | 215.4497 | 105.1798 | 225.7237
3097.176 | 215.2658 | 104.7266 | 225.6417
3098.176 | 215.1553 | 103.9371 | 226.5211
3099.176 | 215.2561 | 103.4616 | 226.2373
3100.176 | 215.1183 | 102.8863 | 226.3876
3101.176 | 215.25 | 102.4147 | 226.1497
3102.176 | 215.1888 | 101.9569 | 225.9433
3103.176 | 214.9789 | 101.8824 | 225.5686
3104.176 | 214.7753 | 103.7123 | 225.2221
3105.176 | 214.7311 | 104.2191 | 225.429
3106.176 | 214.4254 | 105.4986 | 225.2091
3107.176 | 214.3573 | 105.1074 | 224.9121
3108.176 | 214.0455 | 104.0435 | 224.9067
3109.176 | 213.8586 | 103.3233 | 224.5543
3110.176 | 213.871 | 102.3268 | 224.5612
3111.176 | 214.0144 | 101.3453 | 224.34
3112.176 | 214.1271 | 99.9183 | 224.4086
3113.176 | 213.9279 | 99.5443 | 224.4942
3114.176 | 214.0539 | 99.9266 | 224.2884
3115.176 | 213.9769 | 101.2682 | 224.1212
3116.176 | 213.9582 | 101.8023 | 224.5076
3117.176 | 214.0165 | 102.0474 | 224.5438
3118.176 | 213.9714 | 103.4059 | 224.8636
3119.176 | 213.8604 | 104.1018 | 224.607
3120.176 | 213.832 | 104.0522 | 224.5124
3121.176 | 213.6614 | 103.5994 | 224.433
3122.176 | 213.6807 | 103.187 | 224.3962
3123.176 | 213.6184 | 102.8806 | 224.4561
3124.176 | 213.6558 | 102.1527 | 224.3659
3125.176 | 213.4552 | 102.5311 | 224.1871
3126.176 | 213.2616 | 102.5267 | 224.1835
3127.176 | 213.143 | 101.8709 | 224.0037
3128.176 | 213.0651 | 100.8017 | 224.262
3129.176 | 212.9476 | 99.9562 | 224.283
3130.176 | 212.9026 | 99.157 | 224.6016
3131.176 | 212.8807 | 98.9164 | 224.706
3132.176 | 212.9084 | 97.9843 | 224.5375
3133.176 | 212.991 | 97.5635 | 224.5734
3134.176 | 213.3625 | 97.2149 | 224.5963
3135.176 | 213.4647 | 96.6185 | 224.4734
3136.176 | 213.4333 | 96.9149 | 224.2644
3137.176 | 213.3619 | 98.2641 | 224.0247
3138.176 | 213.2319 | 99.8376 | 223.5304
3139.176 | 213.2021 | 101.2911 | 223.4694
3140.176 | 213.0651 | 100.0906 | 223.6452
3141.176 | 213.031 | 100.4033 | 223.7627
3142.176 | 212.8644 | 99.1298 | 223.9304
3143.1917 | 212.6594 | 97.9085 | 223.6523
3144.176 | 212.7949 | 97.2065 | 223.4768
3145.176 | 212.5826 | 95.7425 | 223.3705
3146.176 | 212.4188 | 94.2543 | 223.3994
3147.176 | 212.3552 | 93.3182 | 223.2159
3148.176 | 212.1829 | 92.9984 | 223.0401
3149.176 | 212.0033 | 92.9498 | 222.8805
3150.176 | 211.9349 | 92.9355 | 223.3317
3151.176 | 211.9615 | 93.1106 | 223.0062
3152.176 | 211.7853 | 92.2613 | 222.7042
3153.176 | 211.7157 | 91.1675 | 222.5776
3154.176 | 211.7813 | 90.1102 | 222.2681
3155.176 | 211.7845 | 90.3922 | 221.7791
3156.176 | 211.7947 | 89.5287 | 221.7259
3157.176 | 211.9049 | 88.0266 | 221.5785
3158.176 | 211.8364 | 86.673 | 221.5851
3159.176 | 211.6023 | 85.9065 | 222.0001
3160.176 | 211.6569 | 85.1536 | 222.556
3161.176 | 211.5072 | 84.185 | 222.3916
3162.176 | 211.3807 | 83.8213 | 222.4378
3163.176 | 211.3661 | 82.7454 | 222.4794
3164.176 | 211.3224 | 81.7064 | 222.4942
3165.176 | 211.5426 | 81.3848 | 222.9195
3166.176 | 211.6242 | 80.5188 | 223.234
3167.176 | 211.7264 | 79.8163 | 223.7248
3168.176 | 211.7585 | 81.0122 | 223.8945
3169.176 | 211.6718 | 82.0379 | 223.9548
3170.176 | 211.67 | 82.0319 | 224.4505
3171.176 | 211.7301 | 82.8803 | 224.5225
3172.176 | 211.5195 | 82.0724 | 224.2762
3173.1917 | 211.2553 | 81.3069 | 224.3367
3174.176 | 211.181 | 82.7823 | 223.8477
3175.176 | 211.3788 | 83.2393 | 223.5663
3176.176 | 211.3377 | 84.6504 | 223.4664
3177.176 | 211.3094 | 84.6229 | 223.6182
3178.176 | 211.2558 | 84.6352 | 223.7002
3179.176 | 211.1932 | 84.3593 | 223.9629
3180.176 | 211.2037 | 84.6969 | 223.8293
3181.176 | 211.3515 | 86.9021 | 223.6962
3182.176 | 211.3749 | 86.2941 | 223.3202
3183.176 | 211.2276 | 85.7612 | 223.0935
3184.176 | 211.2397 | 86.7925 | 222.7106
3185.176 | 211.4154 | 86.7566 | 222.3325
3186.176 | 211.4206 | 86.8611 | 221.9587
3187.176 | 211.4206 | 86.3721 | 221.5457
3188.176 | 211.4708 | 86.3631 | 221.23
3189.176 | 211.8652 | 86.8824 | 221.0435
3190.176 | 211.8515 | 87.1422 | 220.7931
3191.176 | 211.8462 | 86.858 | 220.8144
3192.176 | 211.958 | 86.2951 | 221.1939
3193.176 | 211.9527 | 87.9739 | 221.1263
3194.176 | 212.4874 | 87.1144 | 221.0606
3195.176 | 212.4958 | 86.7197 | 221.2786
3196.176 | 212.716 | 86.7834 | 221.1444
3197.176 | 212.736 | 85.7006 | 221.2647
3198.176 | 212.696 | 85.6569 | 221.1128
3199.176 | 212.8261 | 84.8918 | 221.1504
3200.176 | 212.9855 | 83.7704 | 221.049
3201.176 | 212.8071 | 84.2799 | 220.8708
3202.176 | 212.7526 | 83.808 | 221.112
3203.1917 | 212.5466 | 83.6583 | 221.6874
3204.176 | 212.4877 | 82.664 | 221.7112
3205.176 | 212.4485 | 81.6178 | 221.7874
3206.176 | 212.4435 | 82.9024 | 221.7236
3207.176 | 212.3239 | 84.8723 | 221.7287
3208.176 | 212.3128 | 88.9234 | 222.2837
3209.176 | 212.5767 | 88.6936 | 222.3378
3210.176 | 212.4866 | 89.7937 | 222.2813
3211.176 | 212.3517 | 90.4658 | 222.6143
3212.176 | 212.2152 | 91.0447 | 222.6375
3213.176 | 212.045 | 90.7761 | 222.7428
3214.176 | 211.9146 | 90.5693 | 223.1895
3215.176 | 211.7718 | 90.3264 | 223.1214
3216.176 | 211.6557 | 89.7903 | 223.3076
3217.176 | 211.4696 | 88.9692 | 223.5883
3218.176 | 211.7222 | 88.1766 | 223.4862
3219.176 | 211.7184 | 87.2402 | 223.9545
3220.176 | 211.7338 | 86.3125 | 223.8806
3221.176 | 211.5622 | 86.3156 | 223.6953
3222.176 | 211.4818 | 86.8945 | 223.6012
3223.176 | 211.7189 | 87.401 | 223.5751
3224.176 | 211.9935 | 88.0751 | 223.3997
3225.176 | 212.231 | 87.4399 | 223.4912
3226.2229 | 212.3578 | 86.4576 | 223.3718
3227.176 | 212.8666 | 85.9635 | 223.4257
3228.176 | 213.367 | 85.2622 | 223.2203
3229.176 | 213.5906 | 84.3204 | 223.4258
3230.176 | 213.3531 | 83.673 | 223.5148
3231.176 | 213.2974 | 83.1458 | 223.4758
3232.176 | 213.2893 | 82.7015 | 223.5819
3233.1917 | 213.2466 | 83.1091 | 223.5662
3234.176 | 213.4545 | 81.9466 | 223.6133
3235.176 | 213.3996 | 82.047 | 223.5227
3236.176 | 213.4891 | 82.5416 | 224.0435
3237.176 | 213.6558 | 82.3243 | 224.1067
3238.176 | 213.8111 | 81.2787 | 224.0885
3239.176 | 213.462 | 80.6275 | 223.807
3240.176 | 213.3707 | 80.1085 | 223.4894
3241.176 | 213.2783 | 79.202 | 223.483
3242.176 | 213.401 | 78.6173 | 223.3687
3243.176 | 213.8324 | 77.7278 | 223.4412
3244.176 | 214.0026 | 76.538 | 223.7147
3245.176 | 214.0952 | 75.6508 | 223.5435
3246.176 | 214.0396 | 75.4108 | 223.3897
3247.176 | 214.1309 | 76.6675 | 223.4301
3248.176 | 214.4789 | 77.5344 | 223.6741
3249.176 | 214.615 | 77.3728 | 223.6558
3250.176 | 214.7822 | 78.3589 | 223.7366
3251.176 | 215.0175 | 81.4011 | 223.6243
3252.176 | 214.9118 | 82.4936 | 223.5717
3253.176 | 214.8298 | 83.9832 | 223.5288
3254.176 | 214.8037 | 83.7153 | 223.4392
3255.176 | 214.9398 | 82.9337 | 223.2074
3256.176 | 215.3301 | 82.139 | 223.3627
3257.176 | 215.1873 | 81.1545 | 223.4188
3258.176 | 215.4536 | 81.9781 | 223.2173
3259.176 | 215.7148 | 82.6214 | 223.2267
3260.176 | 215.7934 | 82.9827 | 223.3841
3261.176 | 215.3754 | 82.8975 | 223.3422
3262.176 | 215.4122 | 83.3779 | 223.3322
3263.176 | 215.6573 | 84.323 | 222.9729
3264.176 | 215.4608 | 84.819 | 222.9095
3265.176 | 215.3495 | 84.7023 | 223.0809
3266.176 | 215.4889 | 83.5036 | 223.3308
3267.176 | 215.3703 | 82.4253 | 223.1112
3268.176 | 215.3758 | 83.2627 | 222.9712
3269.176 | 215.7703 | 82.8461 | 223.0436
3270.176 | 215.9849 | 82.3853 | 223.0589
3271.1917 | 216.1501 | 82.6402 | 222.9636
3272.176 | 215.9312 | 82.9636 | 222.884
3273.176 | 215.6802 | 82.6543 | 222.6818
3274.1917 | 215.7539 | 81.8907 | 222.3986
3275.1917 | 215.7301 | 80.9682 | 222.246
3276.176 | 215.5356 | 80.2974 | 222.161
3277.176 | 215.6 | 79.6085 | 222.1878
3278.176 | 215.7211 | 79.8697 | 222.1726
3279.176 | 215.87 | 78.561 | 222.036
3280.176 | 216.16 | 77.6849 | 221.9762
3281.176 | 216.5326 | 77.97 | 222.1541
3282.176 | 216.6078 | 77.8059 | 222.348
3283.176 | 216.5168 | 77.2052 | 222.387
3284.176 | 216.2768 | 76.9686 | 222.5471
3285.176 | 216.139 | 77.0962 | 222.9031
3286.176 | 216.1211 | 76.8617 | 223.38
3287.176 | 216.0712 | 76.5546 | 223.4323
3288.176 | 215.7273 | 76.7999 | 223.8397
3289.176 | 215.3909 | 77.6719 | 224.1073
3290.176 | 215.379 | 77.6155 | 224.0939
3291.176 | 215.3678 | 78.1328 | 223.9683
3292.176 | 215.3533 | 78.5759 | 223.9367
3293.1917 | 215.3029 | 77.3818 | 223.9809
3294.176 | 215.0301 | 77.7643 | 224.0977
3295.176 | 214.8653 | 77.8303 | 223.9526
3296.176 | 214.6545 | 78.4696 | 224.0854
3297.176 | 214.5809 | 80.9269 | 224.0671
3298.176 | 214.7908 | 82.1131 | 224.1572
3299.176 | 214.9126 | 84.5744 | 224.2697
3300.176 | 214.9389 | 85.969 | 224.454
3301.176 | 214.9533 | 86.5567 | 224.4399
3302.176 | 215.0591 | 85.963 | 224.6321
3303.176 | 215.0908 | 86.3408 | 224.5428
3304.176 | 214.8968 | 86.5298 | 224.6266
3305.176 | 214.8018 | 86.5696 | 224.368
3306.176 | 214.7218 | 85.5991 | 223.991
3307.176 | 214.5321 | 83.9993 | 223.9071
3308.176 | 214.3772 | 82.9174 | 223.5675
3309.176 | 214.2068 | 82.4474 | 223.2771
3310.176 | 214.1471 | 81.1635 | 223.0018
3311.176 | 214.2099 | 79.9184 | 222.5695
3312.176 | 214.4348 | 78.82 | 222.2523
3313.176 | 215.0379 | 78.8051 | 222.0322
3314.176 | 215.5938 | 78.7531 | 222.1309
3315.176 | 215.6934 | 78.8344 | 222.3782
3316.176 | 215.8358 | 80.3682 | 222.9592
3317.176 | 216.996 | 83.4557 | 223.709
3318.176 | 217.2714 | 87.0753 | 224.6345
3319.176 | 218.5349 | 92.2777 | 225.5465
3320.176 | 218.8054 | 97.3059 | 226.7746
3321.176 | 219.4785 | 100.8815 | 227.744
3322.176 | 220.2188 | 105.7629 | 228.9137
3323.176 | 220.9568 | 109.7811 | 229.3526
3324.176 | 221.7902 | 113.0822 | 230.0064
3325.176 | 222.8569 | 116.2628 | 230.6195
3326.176 | 223.558 | 120.2227 | 231.2529
3327.176 | 223.4067 | 123.1123 | 231.5917
3328.176 | 223.8104 | 126.308 | 231.8627
3329.176 | 224.2909 | 131.7571 | 232.1924
3330.176 | 224.3434 | 133.4888 | 232.7831
3331.176 | 224.1794 | 135.792 | 232.7244
3332.176 | 224.4601 | 138.9207 | 233.4343
3333.176 | 225.0171 | 142.8429 | 233.92
3334.176 | 225.507 | 145.7702 | 234.3379
3335.176 | 225.6696 | 148.1238 | 234.7617
3336.176 | 225.8822 | 151.6857 | 235.4524
3337.176 | 226.3519 | 152.5984 | 236.3339
3338.176 | 226.7943 | 155.9209 | 236.6327
3339.176 | 226.7389 | 158.8444 | 237.0774
3340.176 | 227.1333 | 160.1066 | 237.2775
3341.176 | 227.4385 | 161.1998 | 237.4701
3342.176 | 227.4238 | 165.5548 | 237.8748
3343.176 | 227.8433 | 170.3022 | 238.3137
3344.176 | 228.1401 | 174.3692 | 238.7315
3345.176 | 228.3323 | 178.4864 | 238.7333
3346.176 | 228.5646 | 180.33 | 238.889
3347.176 | 228.6759 | 193.4867 | 239.5566
3348.176 | 228.8991 | 195.2755 | 239.9942
3349.176 | 229.1682 | 198.8277 | 240.286
3350.176 | 229.5551 | 198.8724 | 240.4158
3351.176 | 229.9319 | 199.8033 | 240.8744
3352.176 | 230.4481 | 200.871 | 241.1809
3353.176 | 230.6459 | 201.6327 | 241.2788
3354.176 | 230.8101 | 201.0721 | 241.3823
3355.176 | 231.0994 | 201.7196 | 241.2515
3356.176 | 231.5549 | 205.0644 | 241.1717
3357.176 | 231.6669 | 207.5039 | 241.4056
3358.176 | 231.716 | 210.553 | 241.8643
3359.176 | 232.4203 | 211.1608 | 242.1911
3360.176 | 233.0286 | 211.1166 | 242.5546
3361.176 | 233.0048 | 210.3029 | 243.0165
3362.176 | 233.5953 | 211.4932 | 243.3628
3363.176 | 234.223 | 212.5013 | 243.197
3364.176 | 234.1359 | 211.54 | 243.1288
3365.176 | 233.9536 | 213.3515 | 243.1875
3366.176 | 233.6651 | 214.9731 | 243.0604
3367.176 | 234.0305 | 214.1413 | 242.9454
3368.176 | 234.0131 | 213.4832 | 243.1085
3369.176 | 233.8817 | 213.3179 | 243.5488
3370.176 | 234.3158 | 212.6781 | 243.6098
3371.176 | 234.2658 | 213.3164 | 243.8612
3372.176 | 234.5316 | 213.5731 | 244.1465
3373.176 | 234.721 | 213.3807 | 244.2985
3374.176 | 234.8777 | 214.534 | 244.7934
3375.176 | 234.863 | 218.915 | 245.1254
3376.176 | 234.7664 | 223.549 | 245.5178
3377.176 | 234.9419 | 227.2872 | 245.7327
3378.176 | 234.77 | 229.1579 | 246.6093
3379.176 | 234.9146 | 229.3385 | 246.9594
3380.176 | 235.58 | 231.3312 | 247.2846
3381.176 | 236.027 | 230.0898 | 246.9278
3382.176 | 236.6679 | 229.5522 | 247.3115
3383.176 | 237.1743 | 229.5689 | 247.8288
3384.176 | 238.3951 | 233.9797 | 248.1808
3385.176 | 238.9377 | 238.1729 | 249.4512
3386.176 | 238.9357 | 243.0023 | 250.6169
3387.176 | 239.1332 | 252.8529 | 251.2616
3388.176 | 239.1366 | 260.8062 | 252.0437
3389.176 | 239.6359 | 267.9968 | 252.6184
3390.176 | 239.3468 | 280.8296 | 253.1786
3391.176 | 239.899 | 284.6301 | 253.1296
3392.176 | 240.6156 | 288.3446 | 253.1592
3393.176 | 241.2071 | 291.173 | 253.6754
3394.176 | 241.2926 | 297.7618 | 254.216
3395.176 | 241.4371 | 309.6684 | 255.4088
3396.176 | 242.1171 | 316.275 | 257.4618
3397.176 | 242.8166 | 324.39 | 257.8878
3398.176 | 242.9066 | 332.6414 | 258.9202
3399.176 | 243.6844 | 359.2111 | 260.4196
3400.176 | 244.5678 | 366.4629 | 262.0058
3401.176 | 245.5875 | 375.1903 | 264.2935
3402.176 | 246.2297 | 378.9674 | 266.24
3403.176 | 246.5775 | 388.7166 | 267.633
3404.176 | 247.0817 | 416.8684 | 268.6745
3405.176 | 247.0885 | 432.0683 | 270.3483
3406.176 | 247.162 | 448.3172 | 271.7533
3407.176 | 247.5966 | 457.6229 | 272.415
3408.176 | 247.8916 | 470.6883 | 273.8474
3409.176 | 248.3368 | 497.2355 | 275.2989
3410.176 | 248.6317 | 525.395 | 276.7581
3411.176 | 249.4187 | 548.9229 | 278.0499
3412.176 | 250.0791 | 572.2991 | 278.7376
3413.176 | 250.4793 | 588.8096 | 278.5501
3414.176 | 251.3164 | 599.7654 | 278.1897
3415.176 | 251.8663 | 597.3516 | 277.8208
3416.176 | 251.8469 | 588.3094 | 277.7036
3417.176 | 252.8552 | 586.4076 | 277.5943
3418.176 | 253.4598 | 586.8987 | 277.8468
3419.176 | 253.3684 | 584.7364 | 277.6652
3420.176 | 253.6365 | 586.1875 | 277.4716
3421.176 | 254.3874 | 589.575 | 277.4009
3422.176 | 254.5948 | 591.5773 | 278.6358
3423.176 | 255.0394 | 600.2523 | 278.4568
3424.176 | 256.3838 | 604.7635 | 278.9173
3425.176 | 256.9847 | 597.9182 | 279.1413
3426.176 | 257.662 | 609.3399 | 279.4867
3427.176 | 257.6618 | 612.1157 | 279.4131
3428.176 | 257.5503 | 611.1692 | 279.3081
3429.176 | 257.509 | 624.3487 | 278.9129
3430.176 | 257.4183 | 625.8798 | 278.2749
3431.176 | 257.6108 | 631.0017 | 277.6265
3432.176 | 258.2696 | 627.3828 | 277.661
3433.176 | 258.0436 | 619.366 | 277.4812
3434.176 | 258.2746 | 615.3658 | 277.3446
3435.176 | 258.0056 | 610.9217 | 277.326
3436.176 | 258.6227 | 605.4419 | 277.7663
3437.176 | 258.485 | 601.0235 | 278.2258
3438.176 | 258.7043 | 604.322 | 278.5709
3439.176 | 259.0979 | 611.1303 | 278.2564
3440.176 | 259.2919 | 613.6772 | 278.3328
3441.176 | 260.8195 | 624.5605 | 278.3531
3442.176 | 261.1258 | 627.5595 | 279.9939
3443.176 | 260.8871 | 625.63 | 280.8649
3444.176 | 260.603 | 621.7594 | 280.9366
3445.176 | 260.1383 | 632.393 | 282.3358
3446.176 | 260.5631 | 641.3819 | 283.5529
3447.176 | 260.7457 | 679.8243 | 283.9903
3448.176 | 261.4121 | 687.4251 | 284.1771
3449.176 | 261.4867 | 699.2476 | 284.1735
3450.176 | 261.2341 | 696.7117 | 283.7708
3451.176 | 261.2891 | 717.3012 | 284.0828
3452.176 | 261.3527 | 718.8961 | 283.9892
3453.176 | 261.0025 | 722.4567 | 283.782
3454.176 | 261.6533 | 722.1882 | 283.4117
3455.176 | 261.0778 | 739.3666 | 284.6394
3456.1917 | 261.4102 | 738.9006 | 285.4273
3457.1917 | 261.2009 | 738.8244 | 285.202
3458.1917 | 261.2995 | 738.1649 | 284.8038
3459.176 | 261.4749 | 736.2876 | 284.4456
3460.176 | 261.6532 | 738.6709 | 285.0835
3461.176 | 262.2266 | 742.9566 | 285.4809
3462.176 | 262.7131 | 758.8186 | 285.5673
3463.176 | 264.1648 | 770.4774 | 286.0435
3464.176 | 265.1506 | 794.2101 | 285.6986
3465.176 | 265.3895 | 790.7351 | 286.3366
3466.176 | 266.1231 | 787.5782 | 286.2379
3467.176 | 266.0284 | 782.1016 | 285.9956
3468.176 | 266.5506 | 781.8318 | 285.7616
3469.176 | 266.2476 | 781.7699 | 286.5928
3470.176 | 266.8657 | 780.5182 | 287.3352
3471.176 | 267.166 | 778.5265 | 287.3662
3472.176 | 267.0375 | 779.7655 | 287.0892
3473.176 | 266.7968 | 781.2381 | 286.9312
3474.176 | 266.218 | 781.2608 | 286.6034
3475.176 | 265.55 | 778.0615 | 286.5108
3476.176 | 265.4454 | 821.1798 | 286.12
3477.176 | 265.9356 | 813.5515 | 286.4083
3478.176 | 266.2562 | 809.1112 | 286.3145
3479.176 | 266.5875 | 807.0477 | 287.0305
3480.176 | 266.3343 | 808.2064 | 287.6115
3481.176 | 267.1013 | 848.4038 | 288.3409
3482.176 | 267.5151 | 872.433 | 289.8
3483.176 | 268.8798 | 885.5411 | 291.1914
3484.176 | 269.2414 | 892.8512 | 291.5408
3485.176 | 269.1626 | 895.6279 | 292.4351
3486.176 | 268.5294 | 891.883 | 291.9879
3487.176 | 268.3583 | 893.6709 | 292.3505
3488.176 | 268.384 | 905.1576 | 292.5127
3489.176 | 268.5478 | 912.7458 | 291.8817
3490.176 | 269.0561 | 921.8009 | 292.4635
3491.176 | 269.5071 | 926.4614 | 292.0052
3492.176 | 269.4374 | 935.6377 | 291.6241
3493.176 | 270.3277 | 939.1631 | 292.4485
3494.176 | 270.6533 | 938.7525 | 292.8875
3495.176 | 270.5315 | 947.1532 | 293.4711
3496.176 | 271.0769 | 953.4549 | 293.9163
3497.176 | 271.432 | 951.1135 | 294.1968
3498.176 | 272.0588 | 947.1439 | 294.1694
3499.176 | 272.7813 | 945.8941 | 293.9694
3500.176 | 274.0483 | 940.4343 | 293.6218
3501.176 | 275.0598 | 942.349 | 294.3169
3502.176 | 275.2068 | 936.9299 | 294.8354
3503.176 | 275.6744 | 931.9862 | 294.1826
3504.176 | 275.8066 | 935.2961 | 293.8427
3505.176 | 276.0088 | 937.7191 | 293.8159
3506.176 | 275.9509 | 948.4443 | 294.3133
3507.176 | 276.5027 | 979.7212 | 295.0864
3508.176 | 277.2772 | 993.2014 | 295.2213
3509.176 | 278.2868 | 995.6078 | 295.2931
3510.176 | 278.1684 | 997.5818 | 296.3799
3511.176 | 277.7548 | 1000.9357 | 296.6616
3512.176 | 277.8497 | 1015.5302 | 297.2213
3513.176 | 277.4093 | 1025.7321 | 298.4165
3514.176 | 277.0365 | 1043.1121 | 298.8313
3515.176 | 277.5614 | 1107.9423 | 298.7827
3516.176 | 277.8415 | 1111.1535 | 298.8316
3517.176 | 278.2061 | 1109.4716 | 298.5956
3518.176 | 278.2738 | 1103.1074 | 298.627
3519.176 | 278.729 | 1106.541 | 298.456
3520.176 | 278.5688 | 1106.9875 | 299.248
3521.176 | 278.7634 | 1113.2844 | 299.3249
3522.176 | 278.7733 | 1134.4235 | 299.1691
3523.176 | 279.0098 | 1137.2756 | 299.0151
3524.176 | 278.5648 | 1136.6132 | 299.3186
3525.176 | 278.602 | 1145.1913 | 300.5771
3526.176 | 279.22 | 1168.606 | 301.4722
3527.176 | 279.3988 | 1167.4707 | 300.7198
3528.176 | 279.3057 | 1156.2173 | 300.4802
3529.176 | 279.4241 | 1155.264 | 299.8107
3530.176 | 278.9443 | 1137.0851 | 300.3399
3531.176 | 278.3787 | 1132.6603 | 299.8325
3532.176 | 277.915 | 1138.1758 | 299.5837
3533.176 | 277.839 | 1139.3815 | 299.5416
3534.176 | 277.9286 | 1138.9001 | 299.7553
3535.176 | 277.7614 | 1153.2979 | 299.877
3536.176 | 277.7201 | 1150.6593 | 300.7758
3537.176 | 278.2449 | 1153.4375 | 300.9066
3538.176 | 277.8624 | 1163.9219 | 301.8137
3539.176 | 277.9649 | 1177.8211 | 302.0321
3540.176 | 278.0152 | 1176.6847 | 302.306
3541.176 | 277.9348 | 1185.7932 | 301.7475
3542.176 | 278.3308 | 1186.9748 | 301.6441
3543.176 | 278.2908 | 1187.9141 | 301.4062
3544.176 | 278.2709 | 1182.9218 | 301.3557
3545.176 | 278.8328 | 1181.7644 | 302.0061
3546.176 | 278.8414 | 1183.3926 | 301.2507
3547.176 | 278.8224 | 1182.9829 | 301.7146
3548.176 | 278.7632 | 1177.083 | 301.165
3549.176 | 278.1685 | 1178.9612 | 301.1543
3550.176 | 277.7395 | 1173.2685 | 300.9233
3551.176 | 278.6837 | 1182.941 | 301.1774
3552.176 | 278.7227 | 1191.4213 | 300.6571
3553.176 | 279.0142 | 1200.1236 | 301.827
3554.176 | 279.3595 | 1216.4959 | 303.8078
3555.176 | 279.7753 | 1247.792 | 305.5186
3556.176 | 280.1358 | 1287.6767 | 306.3169
3557.176 | 280.6212 | 1323.1706 | 307.0439
3558.176 | 281.3183 | 1357.0673 | 307.8379
3559.176 | 281.7188 | NaN | 308.0081
3560.176 | 281.9559 | NaN | 307.332
3561.176 | 282.8572 | NaN | 306.8855
3562.176 | 282.9611 | NaN | 307.4326
3563.176 | 283.6812 | NaN | 308.1515
3564.176 | 284.7118 | NaN | 308.9362
3565.176 | 285.3896 | NaN | 309.7157
3566.176 | 285.7295 | NaN | 309.2874
3567.176 | 286.278 | NaN | 308.386
3568.176 | 287.2993 | NaN | 308.9796
3569.176 | 287.2294 | NaN | 308.9189
3570.176 | 288.231 | NaN | 309.4059
3571.176 | 288.4888 | NaN | 310.3034
3572.176 | 288.1394 | NaN | 310.2966
3573.176 | 288.7794 | NaN | 310.097
3574.176 | 288.8814 | NaN | 310.216
3575.176 | 288.1547 | NaN | 310.1425
3576.176 | 287.4864 | NaN | 311.9816
3577.176 | 287.2682 | NaN | 312.7557
3578.176 | 287.5868 | NaN | 312.4013
3579.176 | 288.1493 | NaN | 312.336
3580.176 | 289.5978 | NaN | 313.7811
3581.176 | 289.9449 | NaN | 314.058
3582.176 | 289.7951 | NaN | 315.3813
3583.176 | 291.1399 | NaN | 316.0255
3584.176 | 291.0149 | NaN | 316.8026
3585.176 | 290.9041 | NaN | 316.7998
3586.176 | 290.869 | NaN | 318.0328
3587.176 | 290.8434 | NaN | 318.3173
3588.176 | 291.1937 | NaN | 319.0662
3589.176 | 291.4377 | NaN | 320.5161
3590.176 | 291.7491 | NaN | 321.5726
3591.176 | 292.2899 | NaN | 321.9795
3592.176 | 293.1111 | NaN | 321.7459
3593.176 | 293.1548 | NaN | 321.4074
3594.176 | 293.7005 | NaN | 321.2305
3595.176 | 294.1714 | NaN | 321.6212
3596.176 | 294.6651 | NaN | 322.8311
3597.176 | 294.8751 | NaN | 323.0238
3598.176 | 294.9916 | NaN | 323.1326
3599.176 | 294.2435 | NaN | 323.6148
3600.176 | 294.6536 | NaN | 323.1379
3601.176 | 295.1779 | NaN | 322.8982
3602.176 | 295.2409 | NaN | 322.9609
3603.176 | 295.2534 | NaN | 322.0124
3604.176 | 296.1687 | NaN | 321.1673
3605.176 | 296.6139 | NaN | 320.4552
3606.176 | 297.3776 | NaN | 319.4992
3607.176 | 297.4519 | NaN | 320.6601
3608.176 | 298.0431 | NaN | 320.7692
3609.176 | 298.1088 | NaN | 321.3973
3610.176 | 298.2491 | NaN | 322.6339
3611.176 | 298.2588 | NaN | 322.3765
3612.176 | 298.4733 | NaN | 321.5408
3613.176 | 298.4528 | NaN | 321.1112
3614.176 | 299.3291 | NaN | 320.3566
3615.176 | 300.1711 | NaN | 320.259
3616.176 | 300.2659 | NaN | 320.5089
3617.176 | 300.5595 | NaN | 320.8692
3618.176 | 300.652 | NaN | 322.2161
3619.176 | 301.2914 | NaN | 322.1403
3620.176 | 301.0611 | NaN | 322.1716
3621.176 | 301.5054 | NaN | 322.2882
3622.176 | 301.4914 | NaN | 322.7479
3623.176 | 301.2545 | NaN | 322.97
3624.176 | 301.5927 | NaN | 322.9756
3625.176 | 302.5756 | NaN | 323.2347
3626.176 | 303.1233 | NaN | 323.095
3627.176 | 303.4951 | NaN | 324.3413
3628.176 | 303.3463 | NaN | 324.6049
3629.176 | 303.0996 | NaN | 323.8067
3630.176 | 303.2511 | NaN | 322.8634
3631.176 | 303.5521 | NaN | 323.3022
3632.176 | 303.4402 | NaN | 322.6201
3633.176 | 303.2468 | NaN | 321.9348
3634.176 | 303.5995 | NaN | 321.903
3635.176 | 303.3877 | NaN | 321.9655
3636.176 | 303.4185 | NaN | 321.1068
3637.176 | 304.3487 | NaN | 320.8126
3638.176 | 304.2729 | NaN | 321.0078
3639.176 | 304.621 | NaN | 321.4493
3640.176 | 305.152 | NaN | 321.3177
3641.176 | 305.3739 | NaN | 322.1213
3642.176 | 305.7569 | NaN | 322.8521
3643.176 | 305.6436 | NaN | 322.9453
3644.176 | 305.5464 | NaN | 323.0055
3645.176 | 306.5669 | NaN | 322.9119
3646.176 | 306.9083 | NaN | 323.0777
3647.176 | 307.2658 | NaN | 323.0063
3648.176 | 308.7531 | NaN | 322.6755
3649.176 | 310.0069 | NaN | 322.2969
3650.176 | 310.3598 | NaN | 322.4348
3651.176 | 310.8738 | NaN | 322.0943
3652.176 | 310.3213 | NaN | 322.6034
3653.176 | 311.0311 | NaN | 323.5448
3654.176 | 311.3909 | NaN | 324.8946
3655.176 | 311.362 | NaN | 326.0727
3656.176 | 311.7409 | NaN | 325.8298
3657.176 | 312.7296 | NaN | 326.3431
3658.176 | 313.302 | NaN | 326.0166
3659.176 | 313.1681 | NaN | 327.5707
3660.176 | 313.2061 | NaN | 329.229
3661.176 | 314.1417 | NaN | 330.3569
3662.176 | 314.6969 | NaN | 331.2427
3663.176 | 315.3994 | NaN | 333.0217
3664.176 | 316.815 | NaN | 333.4137
3665.176 | 316.5317 | NaN | 333.7513
3666.176 | 316.2701 | NaN | 333.5218
3667.176 | 316.3122 | NaN | 333.2053
3668.176 | 316.3666 | NaN | 333.8681
3669.176 | 316.3049 | NaN | 334.6994
3670.176 | 315.976 | NaN | 334.6407
3671.176 | 316.3982 | NaN | 334.7678
3672.176 | 316.0769 | NaN | 334.9548
3673.176 | 315.4291 | NaN | 334.2401
3674.176 | 315.0334 | NaN | 334.0531
3675.176 | 314.5928 | NaN | 333.9205
3676.176 | 314.4643 | NaN | 333.9499
3677.176 | 314.3875 | NaN | 334.0738
3678.176 | 315.1317 | NaN | 333.8407
3679.176 | 315.5252 | NaN | 334.0806
3680.176 | 316.1522 | NaN | 334.258
3681.176 | 316.6553 | NaN | 335.0922
3682.176 | 316.7867 | NaN | 334.8616
3683.176 | 316.4771 | NaN | 335.501
3684.176 | 317.1272 | NaN | 335.7968
3685.176 | 317.3933 | NaN | 335.9618
3686.176 | 317.4776 | NaN | 336.2865
3687.176 | 317.7012 | NaN | 337.1519
3688.176 | 317.6069 | NaN | 337.1402
3689.176 | 318.2851 | NaN | 337.9717
3690.176 | 319.0495 | NaN | 339.5326
3691.176 | 319.2906 | NaN | 340.2059
3692.176 | 319.5379 | NaN | 340.2581
3693.176 | 320.1905 | NaN | 340.7939
3694.176 | 321.1081 | NaN | 341.1604
3695.176 | 321.1033 | NaN | 341.6337
3696.176 | 321.1997 | NaN | 342.138
3697.176 | 321.7683 | NaN | 341.8585
3698.176 | 322.6265 | NaN | 341.7866
3699.176 | 325.3354 | NaN | 341.2361
3700.176 | 325.8585 | NaN | 341.3753
3701.176 | 325.684 | NaN | 342.3393
3702.176 | 325.0111 | NaN | 342.0852
3703.176 | 325.4963 | NaN | 342.5807
3704.176 | 325.8618 | NaN | 342.3767
3705.176 | 325.1454 | NaN | 343.1288
3706.176 | 325.4187 | NaN | 342.764
3707.176 | 325.9315 | NaN | 342.0025
3708.176 | 326.1516 | NaN | 342.6847
3709.176 | 327.2942 | NaN | 342.549
3710.176 | 327.1745 | NaN | 342.5203
3711.176 | 327.0254 | NaN | 343.1668
3712.176 | 326.6026 | NaN | 343.3774
3713.176 | 326.903 | NaN | 343.2056
3714.176 | 327.9867 | NaN | 343.7753
3715.176 | 328.6484 | NaN | 344.7536
3716.176 | 328.8423 | NaN | 345.8153
3717.176 | 329.5119 | NaN | 346.6606
3718.176 | 330.2287 | NaN | 348.6651
3719.176 | 330.8052 | NaN | 349.3327
3720.176 | 330.7435 | NaN | 350.1515
3721.176 | 330.5862 | NaN | 350.0473
3722.176 | 330.5285 | NaN | 351.4748
3723.176 | 330.8528 | NaN | 351.8588
3724.176 | 330.7836 | NaN | 351.6706
3725.176 | 331.3406 | NaN | 351.3235
3726.176 | 332.9235 | NaN | 351.7235
3727.176 | 333.4882 | NaN | 351.6573
3728.176 | 334.1221 | NaN | 353.6677
3729.176 | 336.2539 | NaN | 354.3794
3730.176 | 337.0218 | NaN | 355.0673
3731.176 | 338.6539 | NaN | 356.1483
3732.176 | 338.6603 | NaN | 357.2644
3733.176 | 338.6968 | NaN | 357.5307
3734.176 | 339.4692 | NaN | 358.2927
3735.176 | 340.8378 | NaN | 359.175
3736.176 | 341.7089 | NaN | 359.8815
3737.176 | 342.7914 | NaN | 359.0998
3738.176 | 343.3888 | NaN | 359.6513
3739.176 | 343.8044 | NaN | 358.8777
3740.176 | 344.6808 | NaN | 357.9358
3741.176 | 344.3502 | NaN | 357.0039
3742.176 | 343.7002 | NaN | 357.5954
3743.176 | 344.0438 | NaN | 356.497
3744.176 | 343.9432 | NaN | 356.4471
3745.176 | 345.5184 | NaN | 357.6408
3746.176 | 345.6993 | NaN | 357.4152
3747.176 | 346.2092 | NaN | 357.917
3748.176 | 347.2082 | NaN | 359.4201
3749.176 | 347.9687 | NaN | 359.4819
3750.176 | 347.9209 | NaN | 359.5492
3751.176 | 348.5236 | NaN | 360.3291
3752.176 | 348.7905 | NaN | 362.0434
3753.176 | 348.4337 | NaN | 361.587
3754.176 | 348.8804 | NaN | 361.5643
3755.176 | 349.0918 | NaN | 361.9004
3756.176 | 349.9008 | NaN | 362.518
3757.176 | 350.215 | NaN | 362.0821
3758.176 | 350.4424 | NaN | 363.4134
3759.176 | 349.1665 | NaN | 362.8329
3760.176 | 348.6512 | NaN | 362.5723
3761.176 | 348.7775 | NaN | 361.5955
3762.176 | 348.8126 | NaN | 360.9776
3763.176 | 349.4957 | NaN | 362.5294
3764.176 | 349.3736 | NaN | 362.949
3765.176 | 349.6969 | NaN | 362.5936
3766.176 | 350.7537 | NaN | 362.5472
3767.176 | 350.9125 | NaN | 362.2981
3768.176 | 350.6433 | NaN | 362.4744
3769.176 | 350.4075 | NaN | 362.3512
3770.176 | 350.7233 | NaN | 362.1462
3771.176 | 350.7929 | NaN | 361.9762
3772.176 | 352.3615 | NaN | 361.7435
3773.176 | 352.4103 | NaN | 361.5779
3774.176 | 352.0376 | NaN | 362.2668
3775.176 | 351.8584 | NaN | 362.0204
3776.176 | 351.5709 | NaN | 361.5121
3777.176 | 351.0296 | NaN | 361.8011
3778.176 | 351.351 | NaN | 362.0421
3779.176 | 351.6044 | NaN | 362.0454
3780.176 | 351.9726 | NaN | 362.822
3781.176 | 352.6854 | NaN | 364.3819
3782.176 | 353.4688 | NaN | 363.9676
3783.176 | 353.1492 | NaN | 364.1336
3784.176 | 353.972 | NaN | 364.2226
3785.176 | 353.7614 | NaN | 363.8264
3786.176 | 353.6977 | NaN | 364.5574
3787.176 | 353.4535 | NaN | 364.6694
3788.176 | 354.1427 | NaN | 364.7238
3789.176 | 354.9302 | NaN | 365.0352
3790.176 | 354.6169 | NaN | 365.1348
3791.176 | 354.7932 | NaN | 364.1751
3792.176 | 354.0966 | NaN | 363.6137
3793.176 | 355.0198 | NaN | 363.5474
3794.176 | 355.2322 | NaN | 363.0301
3795.176 | 355.9009 | NaN | 362.2441
3796.176 | 356.1372 | NaN | 362.4898
3797.176 | 355.6976 | NaN | 362.7637
3798.176 | 355.4908 | NaN | 362.9906
3799.176 | 355.0513 | NaN | 362.6464
3800.176 | 355.5082 | NaN | 363.0387
3801.176 | 355.6469 | NaN | 362.8458
3802.176 | 355.553 | NaN | 363.3242
3803.176 | 355.915 | NaN | 363.2916
3804.176 | 356.516 | NaN | 364.4518
3805.176 | 355.8626 | NaN | 365.1294
3806.176 | 356.2156 | NaN | 365.3398
3807.176 | 356.6279 | NaN | 364.4839
3808.176 | 356.7618 | NaN | 364.1348
3809.176 | 356.5502 | NaN | 364.8687
3810.176 | 357.0113 | NaN | 365.6856
3811.176 | 357.0001 | NaN | 365.5024
3812.176 | 357.792 | NaN | 365.582
3813.176 | 358.382 | NaN | 365.9799
3814.176 | 358.6549 | NaN | 365.7048
3815.176 | 359.2572 | NaN | 365.2145
3816.176 | 359.5833 | NaN | 365.7605
3817.176 | 358.9574 | NaN | 365.9864
3818.176 | 358.8525 | NaN | 366.2942
3819.176 | 358.7211 | NaN | 366.5144
3820.176 | 358.7929 | NaN | 366.86
3821.176 | 358.9793 | NaN | 366.6821
3822.176 | 358.5321 | NaN | 367.3815
3823.176 | 358.6676 | NaN | 367.5753
3824.176 | 359.0721 | NaN | 367.5636
3825.176 | 359.5755 | NaN | 368.4981
3826.176 | 360.0339 | NaN | 369.0603
3827.176 | 360.0639 | NaN | 369.1057
3828.176 | 360.3912 | NaN | 368.701
3829.176 | 360.6445 | NaN | 368.1177
3830.176 | 360.3184 | NaN | 368.2365
3831.176 | 359.9364 | NaN | 368.339
3832.176 | 360.1096 | NaN | 368.0385
3833.176 | 360.0738 | NaN | 368.1577
3834.176 | 359.3947 | NaN | 368.3536
3835.176 | 359.7464 | NaN | 367.7362
3836.176 | 359.6717 | NaN | 367.7855
3837.176 | 359.7031 | NaN | 367.9424
3838.176 | 360.685 | NaN | 368.3696
3839.176 | 359.9331 | NaN | 368.1478
3840.176 | 360.3211 | NaN | 368.3059
3841.176 | 360.7101 | NaN | 370.0062
3842.176 | 360.8687 | NaN | 371.4017
3843.176 | 361.7264 | NaN | 371.1085
3844.176 | 361.838 | NaN | 370.9114
3845.176 | 361.8259 | NaN | 371.1306
3846.176 | 361.8365 | NaN | 371.5048
3847.176 | 361.9417 | NaN | 371.6653
3848.176 | 361.8311 | NaN | 371.9894
3849.176 | 363.0536 | NaN | 372.5142
3850.176 | 363.8343 | NaN | 373.1094
3851.176 | 364.0164 | NaN | 373.1234
3852.176 | 364.8709 | NaN | 373.4849
3853.176 | 365.6055 | NaN | 373.8271
3854.176 | 365.8766 | NaN | 374.557
3855.176 | 365.6016 | NaN | 374.9608
3856.176 | 365.2151 | NaN | 374.3873
3857.176 | 364.7849 | NaN | 374.619
3858.176 | 364.8639 | NaN | 374.8483
3859.176 | 365.4865 | NaN | 376.2793
3860.176 | 366.002 | NaN | 377.2638
3861.176 | 366.4647 | NaN | 378.3989
3862.176 | 365.8799 | NaN | 378.853
3863.176 | 365.366 | NaN | 379.1128
3864.176 | 365.5393 | NaN | 378.1655
3865.176 | 365.6181 | NaN | 377.5434
3866.176 | 365.4436 | NaN | 376.7859
3867.176 | 365.5678 | NaN | 376.7043
3868.176 | 365.8045 | NaN | 377.1604
3869.176 | 366.521 | NaN | 377.8603
3870.176 | 366.9374 | NaN | 379.6253
3871.176 | 367.6606 | NaN | 380.3097
3872.176 | 368.4746 | NaN | 380.9283
3873.176 | 368.3313 | NaN | 380.9252
3874.176 | 368.475 | NaN | 381.3039
3875.176 | 370.396 | NaN | 381.1168
3876.176 | 370.9159 | NaN | 381.8094
3877.176 | 371.127 | NaN | 382.2189
3878.176 | 371.7938 | NaN | 381.4497
3879.176 | 372.4893 | NaN | 381.4682
3880.176 | 372.876 | NaN | 381.4997
3881.176 | 373.307 | NaN | 381.1568
3882.176 | 372.7273 | NaN | 382.3796
3883.176 | 373.167 | NaN | 382.4214
3884.176 | 373.1273 | NaN | 382.2824
3885.176 | 373.4563 | NaN | 382.5948
3886.176 | 374.3826 | NaN | 383.1067
3887.176 | 374.9007 | NaN | 383.4958
3888.176 | 375.0884 | NaN | 383.7533
3889.176 | 376.2646 | NaN | 384.516
3890.176 | 376.9882 | NaN | 385.2544
3891.176 | 377.9224 | NaN | 385.3272
3892.176 | 378.3565 | NaN | 386.288
3893.176 | 378.777 | NaN | 387.057
3894.176 | 379.0904 | NaN | 386.4767
3895.176 | 379.2464 | NaN | 386.2522
3896.176 | 379.8608 | NaN | 386.9075
3897.176 | 379.9447 | NaN | 385.912
3898.176 | 379.7595 | NaN | 386.1841
3899.176 | 380.6306 | NaN | 385.533
3900.176 | 381.1007 | NaN | 385.8712
3901.176 | 380.8286 | NaN | 386.2421
3902.176 | 380.9094 | NaN | 385.6741
3903.176 | 381.5103 | NaN | 385.9487
3904.176 | 381.4277 | NaN | 387.3859
3905.176 | 381.3678 | NaN | 387.9988
3906.176 | 381.4555 | NaN | 386.9119
3907.176 | 381.3663 | NaN | 386.7053
3908.176 | 380.9904 | NaN | 387.2707
3909.176 | 381.0699 | NaN | 387.844
3910.176 | 381.3862 | NaN | 387.9592
3911.176 | 381.7441 | NaN | 389.0291
3912.176 | 382.9714 | NaN | 389.436
3913.176 | 383.9454 | NaN | 389.958
3914.176 | 384.4721 | NaN | 391.6283
3915.176 | 385.8255 | NaN | 392.3591
3916.176 | 386.2024 | NaN | 394.2804
3917.176 | 386.0978 | NaN | 393.9587
3918.176 | 388.5032 | NaN | 394.4645
3919.176 | 389.0165 | NaN | 395.8305
3920.176 | 389.7761 | NaN | 394.7984
3921.176 | 390.7645 | NaN | 394.9227
3922.176 | 391.6534 | NaN | 394.4912
3923.176 | 392.1404 | NaN | 394.6524
3924.176 | 393.7311 | NaN | 396.3853
3925.176 | 394.531 | NaN | 397.7276
3926.176 | 395.0126 | NaN | 399.9694
3927.176 | 395.9103 | NaN | 401.2387
3928.176 | 396.6068 | NaN | 403.0933
3929.176 | 397.2899 | NaN | 402.9945
3930.176 | 397.7098 | NaN | 403.1301
3931.176 | 398.8664 | NaN | 402.9724
3932.176 | 399.3669 | NaN | 403.433
3933.176 | 400.5492 | NaN | 403.7924
3934.176 | 400.7297 | NaN | 404.9117
3935.176 | 401.5076 | NaN | 405.0332
3936.176 | 402.1042 | NaN | 406.9325
3937.176 | 402.4028 | NaN | 406.9926
3938.176 | 402.975 | NaN | 406.957
3939.176 | 403.5081 | NaN | 408.1565
3940.176 | 403.4411 | NaN | 407.8716
3941.176 | 403.9983 | NaN | 408.1766
3942.176 | 404.2877 | NaN | 408.0578
3943.176 | 404.0591 | NaN | 406.8298
3944.176 | 404.2717 | NaN | 406.5501
3945.176 | 404.9909 | NaN | 406.2608
3946.176 | 405.2673 | NaN | 405.8736
3947.176 | 406.1911 | NaN | 406.3067
3948.176 | 406.7253 | NaN | 406.3722
3949.176 | 407.2455 | NaN | 406.5784
3950.176 | 407.7658 | NaN | 406.6956
3951.176 | 408.6508 | NaN | 406.6593
3952.176 | 408.5612 | NaN | 405.8521
3953.176 | 409.076 | NaN | 405.021
3954.176 | 409.678 | NaN | 404.2013
3955.176 | 409.6469 | NaN | 405.2286
3956.176 | 409.6153 | NaN | 405.0781
3957.176 | 410.4891 | NaN | 405.4727
3958.176 | 410.5084 | NaN | 405.2384
3959.176 | 410.6481 | NaN | 406.4119
3960.176 | 410.0642 | NaN | 406.0153
3961.176 | 410.0341 | NaN | 405.544
3962.176 | 410.3792 | NaN | 405.5373
3963.176 | 410.3808 | NaN | 406.4937
3964.176 | 410.5145 | NaN | 406.6116
3965.176 | 410.8083 | NaN | 406.5014
3966.176 | 410.8277 | NaN | 406.4737
3967.176 | 410.3873 | NaN | 406.8921
3968.176 | 410.3984 | NaN | 406.1809
3969.176 | 410.2853 | NaN | 405.9259
3970.176 | 410.6928 | NaN | 406.595
3971.176 | 410.9076 | NaN | 406.7529
3972.176 | 410.7961 | NaN | 406.5975
3973.176 | 410.9822 | NaN | 406.6152
3974.176 | 410.6038 | NaN | 405.3225
3975.176 | 411.3383 | NaN | 405.6476
3976.176 | 411.5794 | NaN | 406.0728
3977.176 | 411.7481 | NaN | 406.1846
3978.176 | 412.0133 | NaN | 406.1821
3979.176 | 413.5962 | NaN | 406.4457
3980.176 | 413.4623 | NaN | 406.7229
3981.176 | 413.8976 | NaN | 406.3027
3982.176 | 413.6454 | NaN | 405.9631
3983.176 | 413.5789 | NaN | 405.2107
3984.176 | 413.6297 | NaN | 406.0785
3985.176 | 413.4851 | NaN | 406.9523
3986.176 | 414.2134 | NaN | 408.3149
3987.176 | 414.3542 | NaN | 408.4143
3988.176 | 414.9351 | NaN | 408.875
3989.176 | 415.4536 | NaN | 409.2101
3990.176 | 415.7262 | NaN | 410.0232
3991.176 | 415.3614 | NaN | 409.2725
3992.176 | 414.9052 | NaN | 409.0088
3993.176 | 414.6364 | NaN | 408.0807
3994.176 | 414.4456 | NaN | 406.8044
3995.176 | 414.0779 | NaN | 406.9052
3996.176 | 414.7993 | NaN | 407.5246
3997.176 | 415.6909 | NaN | 408.7742
3998.176 | 416.3899 | NaN | 409.6797
3999.176 | 416.1011 | NaN | 409.4354
4000.176 | 416.1305 | NaN | 409.357
4001.176 | 416.4951 | NaN | 409.9364
4002.176 | 417.1302 | NaN | 410.8227
4003.176 | 417.3528 | NaN | 410.7385
4004.176 | 417.5751 | NaN | 410.3914
4005.176 | 417.4755 | NaN | 411.1731
4006.176 | 417.2827 | NaN | 411.428
4007.176 | 419.1689 | NaN | 411.703
4008.176 | 418.6407 | NaN | 410.8177
4009.176 | 418.7488 | NaN | 410.5184
4010.176 | 418.7628 | NaN | 409.8837
4011.176 | 419.2376 | NaN | 410.3721
4012.176 | 419.461 | NaN | 410.8165
4013.176 | 419.7103 | NaN | 411.6244
4014.176 | 419.9207 | NaN | 411.7772
4015.176 | 420.6594 | NaN | 412.7296
4016.176 | 421.5621 | NaN | 412.8019
4017.176 | 421.6136 | NaN | 413.1143
4018.176 | 421.3766 | NaN | 412.9322
4019.176 | 421.3507 | NaN | 413.4719
4020.176 | 421.6499 | NaN | 413.9027
4021.176 | 421.059 | NaN | 413.1803
4022.176 | 421.6242 | NaN | 413.0521
4023.176 | 421.7023 | NaN | 414.4644
4024.176 | 421.6048 | NaN | 414.0999
4025.176 | 421.9641 | NaN | 414.2229
4026.176 | 422.3798 | NaN | 413.8284
4027.176 | 422.6043 | NaN | 414.1552
4028.176 | 423.0811 | NaN | 414.7673
4029.176 | 423.2907 | NaN | 415.9445
4030.176 | 423.1566 | NaN | 415.9939
4031.176 | 423.048 | NaN | 415.4676
4032.176 | 422.7119 | NaN | 414.8313
4033.176 | 423.5828 | NaN | 413.7944
4034.176 | 423.0761 | NaN | 413.6498
4035.176 | 422.8139 | NaN | 413.2823
4036.176 | 423.3177 | NaN | 412.9098
4037.176 | 423.3354 | NaN | 412.3451
4038.176 | 423.1757 | NaN | 412.0344
4039.176 | 423.5495 | NaN | 412.8227
4040.176 | 423.5889 | NaN | 413.6098
4041.176 | 423.0859 | NaN | 413.7397
4042.176 | 422.9085 | NaN | 414.6131
4043.176 | 422.3106 | NaN | 413.9952
4044.176 | 422.2735 | NaN | 413.6143
4045.176 | 422.6511 | NaN | 412.5033
4046.176 | 422.2275 | NaN | 412.6165
4047.176 | 422.924 | NaN | 413.6447
4048.176 | 423.0743 | NaN | 414.4785
4049.176 | 423.1322 | NaN | 413.9896
4050.176 | 422.8519 | NaN | 413.8897
4051.176 | 423.3697 | NaN | 415.1598
4052.176 | 424.0628 | NaN | 415.9283
4053.176 | 424.2303 | NaN | 416.704
4054.176 | 425.8261 | NaN | 417.9582
4055.176 | 426.3594 | NaN | 418.7594
4056.176 | 427.3536 | NaN | 419.5235
4057.176 | 427.7714 | NaN | 420.2225
4058.176 | 428.1321 | NaN | 420.1747
4059.176 | 428.2474 | NaN | 420.1854
4060.176 | 428.1905 | NaN | 419.639
4061.176 | 429.0524 | NaN | 419.3403
4062.176 | 429.5803 | NaN | 419.8026
4063.176 | 430.8382 | NaN | 419.331
4064.176 | 430.8714 | NaN | 419.6784
4065.176 | 431.2172 | NaN | 420.5782
4066.176 | 432.1525 | NaN | 420.9139
4067.176 | 431.9953 | NaN | 420.748
4068.176 | 432.034 | NaN | 420.265
4069.176 | 431.878 | NaN | 420.0373
4070.176 | 431.9728 | NaN | 420.0489
4071.176 | 431.9944 | NaN | 420.0717
4072.176 | 431.7725 | NaN | 420.4012
4073.176 | 431.9998 | NaN | 419.8094
4074.176 | 431.5625 | NaN | 419.6311
4075.176 | 431.114 | NaN | 419.7636
4076.176 | 431.0278 | NaN | 420.8328
4077.176 | 430.6947 | NaN | 420.98
4078.176 | 430.9745 | NaN | 420.7821
4079.176 | 430.7694 | NaN | 421.434
4080.176 | 430.7022 | NaN | 421.8846
4081.176 | 431.0357 | NaN | 422.3041
4082.176 | 431.5438 | NaN | 421.746
4083.176 | 431.4439 | NaN | 421.1356
4084.176 | 431.9188 | NaN | 420.126
4085.176 | 431.8712 | NaN | 420.4994
4086.176 | 431.5996 | NaN | 420.4949
4087.176 | 433.0512 | NaN | 420.7888
4088.176 | 433.1836 | NaN | 421.03
4089.176 | 432.9631 | NaN | 421.2694
4090.176 | 433.0575 | NaN | 420.3758
4091.176 | 433.7924 | NaN | 420.0772
4092.176 | 433.998 | NaN | 419.2335
4093.176 | 434.4425 | NaN | 419.4414
4094.176 | 434.3496 | NaN | 420.7725
4095.176 | 433.7241 | NaN | 420.852
4096.176 | 433.7941 | NaN | 421.8809
4097.176 | 433.9396 | NaN | 422.534
4098.176 | 434.1688 | NaN | 422.0235
4099.176 | 434.4659 | NaN | 422.9054
4100.176 | 434.8563 | NaN | 422.952
4101.176 | 435.6484 | NaN | 424.0136
4102.176 | 436.1013 | NaN | 424.2114
4103.176 | 436.6306 | NaN | 424.2972
4104.176 | 436.6974 | NaN | 424.3974
4105.176 | 436.8588 | NaN | 424.0588
4106.176 | 436.6924 | NaN | 423.7939
4107.176 | 437.1214 | NaN | 424.2593
4108.176 | 437.1516 | NaN | 423.9188
4109.176 | 437.69 | NaN | 423.2347
4110.176 | 437.7798 | NaN | 424.1661
4111.176 | 438.587 | NaN | 424.2332
4112.176 | 438.3658 | NaN | 423.823
4113.176 | 438.1792 | NaN | 423.5157
4114.176 | 438.5757 | NaN | 422.8392
4115.176 | 438.574 | NaN | 423.0522
4116.176 | 438.6063 | NaN | 423.6356
4117.176 | 438.7594 | NaN | 424.2959
4118.176 | 439.6532 | NaN | 426.0641
4119.176 | 440.5394 | NaN | 428.8588
4120.176 | 441.2708 | NaN | 430.9274
4121.176 | 441.7392 | NaN | 431.3953
4122.176 | 442.3588 | NaN | 431.3899
4123.176 | 443.5005 | NaN | 431.4409
4124.176 | 443.2709 | NaN | 430.8804
4125.176 | 443.3349 | NaN | 430.5774
4126.176 | 445.0152 | NaN | 430.7033
4127.176 | 445.2869 | NaN | 431.0344
4128.176 | 445.3672 | NaN | 431.7332
4129.176 | 446.2631 | NaN | 433.1687
4130.176 | 446.2 | NaN | 432.5576
4131.176 | 446.3196 | NaN | 432.4123
4132.176 | 446.5423 | NaN | 432.4597
4133.176 | 447.4401 | NaN | 432.5766
4134.176 | 447.6986 | NaN | 432.6146
4135.176 | 448.9614 | NaN | 433.4977
4136.176 | 449.4352 | NaN | 434.2716
4137.176 | 449.5986 | NaN | 435.3193
4138.176 | 450.1114 | NaN | 436.3495
4139.176 | 450.5114 | NaN | 436.7208
4140.176 | 450.0088 | NaN | 436.8575
4141.176 | 449.6617 | NaN | 436.4202
4142.176 | 449.3042 | NaN | 435.8092
4143.176 | 449.505 | NaN | 436.3975
4144.176 | 450.0412 | NaN | 435.5838
4145.176 | 449.9272 | NaN | 435.5022
4146.176 | 450.5226 | NaN | 435.8242
4147.176 | 450.4175 | NaN | 435.6246
4148.176 | 451.0748 | NaN | 435.443
4149.176 | 451.004 | NaN | 435.4204
4150.176 | 451.3409 | NaN | 435.4527
4151.176 | 451.693 | NaN | 435.6349
4152.176 | 451.2323 | NaN | 435.297
4153.176 | 451.238 | NaN | 435.4787
4154.176 | 451.2094 | NaN | 436.0068
4155.176 | 450.8261 | NaN | 436.7343
4156.176 | 451.0097 | NaN | 437.391
4157.176 | 451.91 | NaN | 438.4777
4158.176 | 452.5651 | NaN | 439.5928
4159.176 | 452.7301 | NaN | 440.7804
4160.176 | 451.9642 | NaN | 440.3326
4161.176 | 451.7187 | NaN | 439.761
4162.176 | 451.5561 | NaN | 442.2547
4163.176 | 451.6213 | NaN | 443.8402
4164.176 | 452.029 | NaN | 444.047
4165.176 | 452.1767 | NaN | 443.7456
4166.176 | 452.2248 | NaN | 444.18
4167.176 | 452.3213 | NaN | 442.9897
4168.176 | 453.2263 | NaN | 442.5299
4169.176 | 453.4416 | NaN | 442.6701
4170.176 | 453.9631 | NaN | 443.1418
4171.176 | 453.8575 | NaN | 442.9201
4172.176 | 454.2503 | NaN | 442.7173
4173.176 | 455.4787 | NaN | 443.2039
4174.176 | 456.7393 | NaN | 443.8105
4175.176 | 456.4971 | NaN | 443.7357
4176.176 | 455.8953 | NaN | 443.5453
4177.176 | 456.3691 | NaN | 443.5945
4178.176 | 456.4025 | NaN | 443.6807
4179.176 | 456.1091 | NaN | 443.3682
4180.176 | 456.5766 | NaN | 443.1778
4181.176 | 456.0465 | NaN | 444.0853
4182.176 | 456.0633 | NaN | 445.3524
4183.176 | 455.9922 | NaN | 445.9995
4184.176 | 455.9954 | NaN | 447.1037
4185.176 | 457.4924 | NaN | 447.6495
4186.176 | 457.0613 | NaN | 447.634
4187.176 | 457.42 | NaN | 447.0453
4188.176 | 458.2377 | NaN | 448.1199
4189.176 | 458.2881 | NaN | 448.5845
4190.176 | 457.7748 | NaN | 449.2396
4191.176 | 458.3288 | NaN | 448.8392
4192.176 | 458.4272 | NaN | 448.2923
4193.176 | 458.3228 | NaN | 447.3472
4194.176 | 459.5131 | NaN | 445.7709
4195.176 | 459.3597 | NaN | 445.9129
4196.176 | 460.0149 | NaN | 445.2301
4197.176 | 459.6512 | NaN | 444.6402
4198.176 | 460.6188 | NaN | 445.3518
4199.176 | 460.9744 | NaN | 445.3903
4200.176 | 461.093 | NaN | 445.1956
4201.176 | 461.1985 | NaN | 445.5714
4202.176 | 461.1753 | NaN | 445.654
4203.1917 | 461.5548 | NaN | 447.2022
4204.176 | 461.5868 | NaN | 447.9405
4205.176 | 461.0073 | NaN | 447.8114
4206.176 | 460.6619 | NaN | 447.7213
4207.176 | 460.5959 | NaN | 447.448
4208.176 | 460.4539 | NaN | 447.3452
4209.176 | 462.3406 | NaN | 447.918
4210.176 | 462.5849 | NaN | 448.8627
4211.176 | 463.4777 | NaN | 449.5112
4212.176 | 463.9477 | NaN | 450.4177
4213.176 | 464.1359 | NaN | 449.5597
4214.176 | 465.0145 | NaN | 449.9503
4215.176 | 465.3149 | NaN | 450.1821
4216.176 | 466.2047 | NaN | 450.591
4217.176 | 466.6691 | NaN | 450.8201
4218.176 | 466.8242 | NaN | 449.8807
4219.176 | 467.0734 | NaN | 449.299
4220.176 | 467.4997 | NaN | 449.2895
4221.176 | 467.441 | NaN | 449.5819
4222.176 | 467.5252 | NaN | 449.9116
4223.176 | 467.7687 | NaN | 450.3819
4224.176 | 467.5673 | NaN | 450.6583
4225.176 | 468.9676 | NaN | 451.801
4226.176 | 469.8939 | NaN | 452.417
4227.176 | 469.8172 | NaN | 451.9162
4228.176 | 470.363 | NaN | 452.8641
4229.176 | 470.415 | NaN | 452.6262
4230.176 | 471.2718 | NaN | 452.8318
4231.176 | 471.8088 | NaN | 451.941
4232.176 | 472.8956 | NaN | 453.5596
4233.176 | 473.1161 | NaN | 454.4183
4234.176 | 473.7314 | NaN | 454.4606
4235.176 | 473.4441 | NaN | 454.0877
4236.176 | 474.1657 | NaN | 454.1244
4237.176 | 474.3699 | NaN | 454.5556
4238.176 | 474.6162 | NaN | 454.9154
4239.176 | 474.8573 | NaN | 454.5202
4240.176 | 474.6285 | NaN | 455.9102
4241.176 | 475.1416 | NaN | 456.1028
4242.176 | 476.0554 | NaN | 457.0863
4243.176 | 475.4437 | NaN | 457.646
4244.176 | 475.4226 | NaN | 459.0302
4245.176 | 475.4161 | NaN | 458.9723
4246.176 | 474.866 | NaN | 459.2329
4247.176 | 475.0952 | NaN | 458.3206
4248.176 | 474.5208 | NaN | 458.4498
4249.176 | 475.3382 | NaN | 458.601
4250.176 | 475.0466 | NaN | 458.6018
4251.176 | 475.0199 | NaN | 459.8169
4252.176 | 475.1327 | NaN | 460.9767
4253.176 | 475.6552 | NaN | 461.5037
4254.176 | 476.4192 | NaN | 462.3323
4255.176 | 476.3258 | NaN | 461.91
4256.176 | 476.7399 | NaN | 460.8042
4257.176 | 476.6597 | NaN | 460.6254
4258.176 | 476.3371 | NaN | 460.7522
4259.176 | 476.6049 | NaN | 463.1606
4260.176 | 477.0135 | NaN | 463.0905
4261.176 | 476.5953 | NaN | 462.5246
4262.1917 | 477.3035 | NaN | 461.602
4263.1917 | 477.735 | NaN | 462.4564
4264.176 | 477.8612 | NaN | 463.3627
4265.176 | 478.1563 | NaN | 464.2371
4266.176 | 478.5321 | NaN | 464.4328
4267.176 | 478.374 | NaN | 463.4324
4268.176 | 478.8884 | NaN | 463.5941
4269.176 | 479.0334 | NaN | 464.0458
4270.176 | 479.5986 | NaN | 464.8963
4271.176 | 480.266 | NaN | 464.5304
4272.176 | 480.4361 | NaN | 465.7864
4273.176 | 481.0109 | NaN | 464.9144
4274.176 | 480.7723 | NaN | 464.4003
4275.176 | 480.5456 | NaN | 463.2758
4276.176 | 480.744 | NaN | 463.321
4277.176 | 481.3892 | NaN | 463.922
4278.176 | 481.6678 | NaN | 464.3193
4279.176 | 481.0776 | NaN | 465.0564
4280.176 | 481.3429 | NaN | 464.9544
4281.176 | 480.9764 | NaN | 465.1194
4282.176 | 481.4417 | NaN | 464.3872
4283.176 | 481.7437 | NaN | 464.433
4284.176 | 482.3071 | NaN | 464.8361
4285.176 | 482.4253 | NaN | 465.1818
4286.176 | 482.7952 | NaN | 466.3898
4287.176 | 483.1366 | NaN | 466.1782
4288.176 | 483.027 | NaN | 466.5176
4289.176 | 483.3078 | NaN | 467.3967
4290.176 | 484.1455 | NaN | 468.061
4291.176 | 484.662 | NaN | 469.5848
4292.176 | 484.8213 | NaN | 470.0158
4293.176 | 485.1748 | NaN | 470.004
4294.176 | 485.7756 | NaN | 469.8253
4295.176 | 486.3217 | NaN | 469.6689
4296.176 | 486.942 | NaN | 469.3887
4297.176 | 487.2358 | NaN | 469.5234
4298.176 | 488.1499 | NaN | 469.7368
4299.176 | 488.5494 | NaN | 470.8208
4300.176 | 488.69 | NaN | 470.3084
4301.176 | 488.6293 | NaN | 470.8815
4302.176 | 488.6036 | NaN | 470.7365
4303.176 | 489.2751 | NaN | 471.4179
4304.176 | 489.7934 | NaN | 471.1002
4305.176 | 490.9853 | NaN | 472.409
4306.176 | 491.8421 | NaN | 471.8835
4307.176 | 492.4266 | NaN | 471.9533
4308.176 | 492.6398 | NaN | 472.0165
4309.176 | 493.7173 | NaN | 472.9153
4310.176 | 493.8912 | NaN | 472.3928
4311.176 | 493.8314 | NaN | 471.3528
4312.176 | 493.3953 | NaN | 471.2012
4313.176 | 493.1941 | NaN | 470.5409
4314.176 | 493.7473 | NaN | 470.3941
4315.176 | 493.7109 | NaN | 470.1634
4316.176 | 493.4899 | NaN | 470.5247
4317.176 | 493.5047 | NaN | 471.6514
4318.176 | 493.9779 | NaN | 472.5482
4319.176 | 493.7802 | NaN | 472.2658
4320.176 | 493.8157 | NaN | 472.177
4321.176 | 494.5105 | NaN | 471.9806
4322.176 | 494.675 | NaN | 473.3317
4323.176 | 494.9482 | NaN | 474.2347
4324.176 | 495.2884 | NaN | 474.3023
4325.176 | 496.0477 | NaN | 475.0162
4326.176 | 496.2938 | NaN | 476.0562
4327.176 | 496.6205 | NaN | 476.2963
4328.176 | 496.8492 | NaN | 476.7331
4329.176 | 497.2363 | NaN | 475.2807
4330.176 | 497.9275 | NaN | 473.6822
4331.176 | 498.2905 | NaN | 473.3856
4332.176 | 498.644 | NaN | 473.8179
4333.176 | 499.3125 | NaN | 475.1098
4334.176 | 499.9032 | NaN | 475.9754
4335.176 | 499.927 | NaN | 476.2151
4336.176 | 500.7482 | NaN | 476.7766
4337.176 | 501.9498 | NaN | 476.3485
4338.176 | 502.5146 | NaN | 477.6669
4339.176 | 502.2752 | NaN | 476.3871
4340.176 | 502.4488 | NaN | 475.1365
4341.176 | 501.8281 | NaN | 474.1828
4342.176 | 501.0794 | NaN | 475.6684
4343.176 | 501.1595 | NaN | 475.5899
4344.176 | 500.9819 | NaN | 475.458
4345.176 | 501.4849 | NaN | 475.6176
4346.176 | 501.6731 | NaN | 476.7781
4347.176 | 502.2599 | NaN | 476.963
4348.176 | 502.6282 | NaN | 476.2037
4349.176 | 503.4637 | NaN | 476.6789
4350.176 | 503.6903 | NaN | 477.0177
4351.176 | 504.3238 | NaN | 477.0149
4352.176 | 504.9581 | NaN | 478.0251
4353.176 | 505.0565 | NaN | 478.2836
4354.176 | 505.1274 | NaN | 478.8461
4355.176 | 505.579 | NaN | 479.2458
4356.176 | 506.2751 | NaN | 478.3194
4357.176 | 507.0136 | NaN | 479.6835
4358.176 | 507.4617 | NaN | 481.5038
4359.176 | 508.0104 | NaN | 482.2167
4360.176 | 508.5861 | NaN | 482.5851
4361.176 | 509.127 | NaN | 483.5419
4362.176 | 509.6406 | NaN | 483.2118
4363.176 | 510.3091 | NaN | 482.9025
4364.176 | 509.98 | NaN | 482.2075
4365.176 | 510.1418 | NaN | 482.9486
4366.176 | 510.3444 | NaN | 482.3039
4367.176 | 510.3878 | NaN | 482.2194
4368.176 | 510.2675 | NaN | 482.7047
4369.176 | 510.3472 | NaN | 482.6136
4370.176 | 510.9848 | NaN | 482.5534
4371.176 | 511.1088 | NaN | 483.5814
4372.176 | 511.0349 | NaN | 482.8973
4373.176 | 511.5115 | NaN | 482.9424
4374.176 | 512.0238 | NaN | 482.8468
4375.176 | 512.5933 | NaN | 481.9446
4376.176 | 512.6345 | NaN | 481.5572
4377.176 | 513.1306 | NaN | 482.6528
4378.176 | 514.8296 | NaN | 483.436
4379.176 | 515.2837 | NaN | 482.875
4380.176 | 515.1807 | NaN | 482.1335
4381.176 | 516.7249 | NaN | 482.2418
4382.176 | 517.7743 | NaN | 482.5846
4383.176 | 518.4666 | NaN | 482.0133
4384.176 | 519.2938 | NaN | 481.3594
4385.176 | 521.3261 | NaN | 481.4905
4386.176 | 521.2441 | NaN | 480.6153
4387.176 | 521.1148 | NaN | 480.0767
4388.176 | 521.2663 | NaN | 479.4509
4389.176 | 521.2563 | NaN | 480.1458
4390.176 | 521.2685 | NaN | 480.5266
4391.176 | 521.6219 | NaN | 480.4358
4392.176 | 521.5425 | NaN | 481.848
4393.176 | 522.2868 | NaN | 482.1956
4394.176 | 522.5661 | NaN | 483.0468
4395.176 | 524.4078 | NaN | 484.0355
4396.176 | 525.1092 | NaN | 484.1233
4397.176 | 525.3499 | NaN | 485.3428
4398.176 | 525.3267 | NaN | 484.852
4399.176 | 525.8985 | NaN | 484.2598
4400.176 | 527.3072 | NaN | 483.7762
4401.176 | 527.6678 | NaN | 483.0847
4402.176 | 528.542 | NaN | 482.8491
4403.176 | 529.1634 | NaN | 483.1922
4404.176 | 530.7539 | NaN | 483.5592
4405.176 | 530.7602 | NaN | 484.2195
4406.176 | 530.8682 | NaN | 485.2288
4407.176 | 532.0381 | NaN | 486.1786
4408.176 | 532.4416 | NaN | 487.4102
4409.176 | 532.9442 | NaN | 486.9832
4410.176 | 533.1815 | NaN | 487.6243
4411.176 | 532.7731 | NaN | 487.5063
4412.176 | 532.966 | NaN | 488.0805
4413.176 | 533.4105 | NaN | 488.9777
4414.176 | 534.5551 | NaN | 489.3368
4415.176 | 535.734 | NaN | 490.6462
4416.176 | 537.0699 | NaN | 490.0027
4417.176 | 537.3876 | NaN | 488.5404
4418.176 | 537.6397 | NaN | 488.1341
4419.176 | 538.4772 | NaN | 487.4216
4420.176 | 539.4092 | NaN | 487.5701
4421.176 | 539.4879 | NaN | 487.2366
4422.176 | 538.7725 | NaN | 487.266
4423.176 | 538.1957 | NaN | 486.0837
4424.176 | 537.8762 | NaN | 485.5642
4425.176 | 537.296 | NaN | 485.067
4426.176 | 537.324 | NaN | 483.9359
4427.176 | 537.4696 | NaN | 483.614
4428.176 | 537.0912 | NaN | 483.1
4429.176 | 536.8014 | NaN | 482.8864
4430.176 | 536.2304 | NaN | 483.4457
4431.176 | 536.8293 | NaN | 484.075
4432.176 | 536.2621 | NaN | 485.7411
4433.176 | 536.3414 | NaN | 487.4421
4434.1917 | 535.7831 | NaN | 488.4426
4435.176 | 535.2451 | NaN | 488.3782
4436.176 | 535.038 | NaN | 488.7923
4437.176 | 534.3374 | NaN | 489.5887
4438.176 | 533.8513 | NaN | 490.7103
4439.176 | 534.0803 | NaN | 490.7033
4440.176 | 533.3589 | NaN | 490.654
4441.176 | 533.4568 | NaN | 490.0774
4442.176 | 533.7339 | NaN | 489.8856
4443.176 | 534.5375 | NaN | 489.4736
4444.176 | 534.4134 | NaN | 489.2528
4445.176 | 534.8303 | NaN | 490.3225
4446.176 | 534.2646 | NaN | 489.9831
4447.176 | 534.9388 | NaN | 490.8509
4448.176 | 534.7618 | NaN | 492.5425
4449.176 | 535.8034 | NaN | 493.0696
4450.176 | 536.8948 | NaN | 493.0036
4451.176 | 536.7864 | NaN | 492.6753
4452.176 | 537.1959 | NaN | 491.9722
4453.176 | 537.664 | NaN | 491.3842
4454.176 | 537.1336 | NaN | 490.993
4455.176 | 538.3012 | NaN | 491.8691
4456.176 | 539.4699 | NaN | 493.3957
4457.176 | 539.9083 | NaN | 493.5302
4458.176 | 539.7411 | NaN | 494.222
4459.176 | 541.0122 | NaN | 495.5737
4460.176 | 541.5901 | NaN | 497.6892
4461.176 | 541.8671 | NaN | 499.034
4462.176 | 542.2669 | NaN | 499.0877
4463.176 | 542.0735 | NaN | 498.5455
4464.176 | 542.6604 | NaN | 497.5833
4465.176 | 543.1945 | NaN | 498.2425
4466.176 | 543.4575 | NaN | 498.191
4467.176 | 543.775 | NaN | 497.7398
4468.176 | 543.9594 | NaN | 497.1422
4469.176 | 543.8058 | NaN | 496.5816
4470.176 | 543.6757 | NaN | 497.1142
4471.176 | 542.9208 | NaN | 496.1058
4472.176 | 542.6781 | NaN | 495.5026
4473.176 | 541.8386 | NaN | 495.093
4474.176 | 540.9005 | NaN | 494.2528
4475.176 | 540.4313 | NaN | 495.4485
4476.176 | 539.9051 | NaN | 496.5366
4477.176 | 539.3673 | NaN | 497.3416
4478.1917 | 538.922 | NaN | 498.1184
4479.176 | 537.895 | NaN | 497.6315
4480.176 | 539.269 | NaN | 497.8708
4481.176 | 540.8969 | NaN | 498.3077
4482.176 | 541.1086 | NaN | 497.9722
4483.176 | 540.8571 | NaN | 498.1783
4484.176 | 541.1671 | NaN | 498.5844
4485.176 | 542.0558 | NaN | 498.9064
4486.176 | 542.3979 | NaN | 499.1084
4487.176 | 542.8007 | NaN | 498.8923
4488.176 | 543.3513 | NaN | 498.6001
4489.176 | 544.2565 | NaN | 497.3414
4490.176 | 543.8608 | NaN | 497.0794
4491.176 | 545.1424 | NaN | 495.9345
4492.176 | 545.2049 | NaN | 495.8346
4493.176 | 545.1323 | NaN | 496.368
4494.176 | 544.4813 | NaN | 495.9224
4495.176 | 544.737 | NaN | 495.0128
4496.176 | 544.4832 | NaN | 495.8103
4497.176 | 544.1446 | NaN | 496.316
4498.176 | 544.9548 | NaN | 497.0868
4499.176 | 544.8327 | NaN | 497.6554
4500.176 | 544.918 | NaN | 498.1104
4501.176 | 545.104 | NaN | 497.2659
4502.176 | 544.2078 | NaN | 496.8506
4503.176 | 543.5954 | NaN | 496.6988
4504.176 | 543.7197 | NaN | 497.289
4505.176 | 543.501 | NaN | 498.279
4506.176 | 544.2191 | NaN | 499.644
4507.176 | 545.1849 | NaN | 499.0154
4508.176 | 545.6899 | NaN | 498.3487
4509.176 | 546.5972 | NaN | 498.2388
4510.176 | 547.5966 | NaN | 499.4035
4511.176 | 547.7973 | NaN | 498.9449
4512.176 | 547.6038 | NaN | 498.1997
4513.176 | 546.9976 | NaN | 497.8362
4514.176 | 547.1104 | NaN | 498.1656
4515.176 | 546.9843 | NaN | 499.1549
4516.176 | 546.7639 | NaN | 498.6376
4517.176 | 547.1078 | NaN | 498.4384
4518.176 | 547.6602 | NaN | 498.2983
4519.176 | 547.8058 | NaN | 499.2412
4520.176 | 547.5973 | NaN | 500.7129
4521.176 | 547.9044 | NaN | 501.246
4522.176 | 548.1204 | NaN | 502.8184
4523.176 | 547.7213 | NaN | 502.1559
4524.176 | 546.9278 | NaN | 502.4116
4525.176 | 546.8437 | NaN | 502.32
4526.176 | 546.5596 | NaN | 502.682
4527.176 | 546.7236 | NaN | 503.5335
4528.176 | 546.8548 | NaN | 503.8336
4529.176 | 546.3956 | NaN | 503.7429
4530.176 | 546.6398 | NaN | 505.0602
4531.176 | 547.0805 | NaN | 504.942
4532.176 | 546.8919 | NaN | 505.5471
4533.176 | 546.594 | NaN | 506.5164
4534.176 | 546.8132 | NaN | 507.6173
4535.176 | 547.008 | NaN | 508.3141
4536.176 | 546.7915 | NaN | 509.1371
4537.176 | 546.7816 | NaN | 509.2573
4538.176 | 546.4917 | NaN | 509.0478
4539.176 | 547.0827 | NaN | 508.6469
4540.176 | 546.9326 | NaN | 507.6501
4541.176 | 546.9863 | NaN | 508.7766
4542.176 | 547.3866 | NaN | 508.6756
4543.176 | 547.1741 | NaN | 507.4156
4544.176 | 547.7532 | NaN | 506.6197
4545.176 | 546.9936 | NaN | 506.8548
4546.176 | 546.9431 | NaN | 507.2449
4547.176 | 547.7683 | NaN | 507.5927
4548.176 | 549.3191 | NaN | 508.1387
4549.176 | 550.0387 | NaN | 509.5576
4550.176 | 551.0179 | NaN | 509.7511
4551.176 | 552.1122 | NaN | 509.3662
4552.176 | 553.7187 | NaN | 508.4165
4553.176 | 553.8886 | NaN | 507.8093
4554.176 | 554.8888 | NaN | 507.539
4555.176 | 556.1387 | NaN | 506.2999
4556.176 | 556.3584 | NaN | 505.5555
4557.176 | 555.224 | NaN | 505.6159
4558.176 | 555.4465 | NaN | 504.868
4559.176 | 555.2747 | NaN | 504.3568
4560.176 | 556.4897 | NaN | 504.6775
4561.176 | 557.2937 | NaN | 503.9552
4562.176 | 557.6703 | NaN | 502.8993
4563.1917 | 558.11 | NaN | 503.4378
4564.176 | 558.8233 | NaN | 503.0348
4565.176 | 560.029 | NaN | 503.2792
4566.176 | 560.123 | NaN | 503.7264
4567.176 | 560.5429 | NaN | 504.3201
4568.176 | 560.9538 | NaN | 504.9207
4569.176 | 560.9791 | NaN | 505.5979
4570.176 | 560.4787 | NaN | 505.859
4571.176 | 561.3794 | NaN | 506.3746
4572.176 | 561.1583 | NaN | 506.7705
4573.176 | 560.3466 | NaN | 506.5249
4574.176 | 559.8313 | NaN | 506.3733
4575.176 | 559.9951 | NaN | 505.7226
4576.176 | 560.2267 | NaN | 506.3026
4577.176 | 560.9217 | NaN | 506.9134
4578.176 | 561.2695 | NaN | 507.0899
4579.176 | 561.9885 | NaN | 506.8247
4580.176 | 561.6921 | NaN | 506.0377
4581.176 | 561.4014 | NaN | 505.675
4582.176 | 560.7104 | NaN | 505.5269
4583.176 | 560.3533 | NaN | 505.3159
4584.176 | 559.6908 | NaN | 505.2956
4585.176 | 558.7763 | NaN | 504.3551
4586.176 | 558.4097 | NaN | 503.2704
4587.176 | 557.4587 | NaN | 502.5727
4588.176 | 556.8252 | NaN | 502.815
4589.176 | 556.7747 | NaN | 503.0712
4590.176 | 556.1019 | NaN | 503.1452
4591.176 | 555.2222 | NaN | 502.1773
4592.176 | 554.3551 | NaN | 501.6289
4593.176 | 553.5607 | NaN | 502.081
4594.176 | 553.7021 | NaN | 501.7581
4595.176 | 554.2744 | NaN | 502.547
4596.176 | 555.541 | NaN | 502.8138
4597.176 | 555.8077 | NaN | 502.4654
4598.176 | 556.5157 | NaN | 501.437
4599.176 | 556.7319 | NaN | 500.2281
4600.176 | 556.3685 | NaN | 500.8317
4601.176 | 555.9623 | NaN | 501.5492
4602.176 | 556.9205 | NaN | 502.3092
4603.176 | 556.4732 | NaN | 503.621
4604.176 | 556.2599 | NaN | 503.6653
4605.176 | 556.1862 | NaN | 504.1521
4606.176 | 556.7093 | NaN | 504.5725
4607.176 | 556.2881 | NaN | 504.9344
4608.176 | 556.3441 | NaN | 505.5144
4609.176 | 556.0491 | NaN | 506.2534
4610.176 | 556.2575 | NaN | 506.6408
4611.176 | 556.9065 | NaN | 507.2517
4612.176 | 556.5705 | NaN | 507.7069
4613.176 | 557.7499 | NaN | 507.7493
4614.176 | 557.8827 | NaN | 507.4918
4615.176 | 557.5892 | NaN | 507.72
4616.176 | 557.6784 | NaN | 508.4933
4617.176 | 556.752 | NaN | 508.2417
4618.176 | 555.5675 | NaN | 507.0569
4619.176 | 555.0481 | NaN | 505.7342
4620.176 | 555.1774 | NaN | 504.557
4621.176 | 555.8014 | NaN | 503.6937
4622.176 | 555.6555 | NaN | 504.0455
4623.1917 | 556.3216 | NaN | 504.6754
4624.176 | 557.2116 | NaN | 505.6457
4625.176 | 557.7249 | NaN | 505.4846
4626.176 | 558.1128 | NaN | 507.2079
4627.176 | 558.271 | NaN | 507.3197
4628.176 | 557.9595 | NaN | 507.7127
4629.176 | 558.3851 | NaN | 509.1451
4630.176 | 559.4745 | NaN | 509.537
4631.176 | 559.6737 | NaN | 510.334
4632.176 | 560.1526 | NaN | 511.0264
4633.176 | 560.8967 | NaN | 511.7507
4634.176 | 561.8187 | NaN | 512.9374
4635.176 | 560.9162 | NaN | 512.5279
4636.176 | 561.2675 | NaN | 512.1066
4637.176 | 561.346 | NaN | 512.2942
4638.176 | 562.5575 | NaN | 513.6013
4639.176 | 562.8822 | NaN | 513.9786
4640.176 | 562.6539 | NaN | 514.3597
4641.176 | 562.7444 | NaN | 514.0088
4642.176 | 563.2132 | NaN | 513.5383
4643.176 | 564.5238 | NaN | 513.8709
4644.176 | 566.3709 | NaN | 513.8335
4645.176 | 566.6831 | NaN | 515.7733
4646.176 | 568.1231 | NaN | 517.4615
4647.176 | 568.6002 | NaN | 516.9322
4648.176 | 568.7832 | NaN | 516.6869
4649.176 | 569.187 | NaN | 516.7868
4650.176 | 569.33 | NaN | 516.8305
4651.176 | 569.005 | NaN | 516.059
4652.176 | 568.2974 | NaN | 514.7706
4653.176 | 568.0069 | NaN | 514.142
4654.176 | 566.8701 | NaN | 513.5883
4655.176 | 565.5402 | NaN | 512.6783
4656.176 | 565.5603 | NaN | 511.4014
4657.176 | 565.531 | NaN | 510.6797
4658.176 | 564.8368 | NaN | 511.1296
4659.176 | 565.1774 | NaN | 512.1198
4660.176 | 564.0616 | NaN | 511.5015
4661.176 | 563.622 | NaN | 510.9174
4662.176 | 564.3611 | NaN | 509.9971
4663.176 | 564.5312 | NaN | 509.3181
4664.176 | 564.3794 | NaN | 508.3075
4665.176 | 563.4544 | NaN | 507.4686
4666.176 | 562.6899 | NaN | 506.4722
4667.176 | 561.3279 | NaN | 505.3186
4668.176 | 560.0594 | NaN | 505.2107
4669.176 | 560.483 | NaN | 505.4261
4670.176 | 560.2229 | NaN | 505.7628
4671.176 | 560.0533 | NaN | 506.5811
4672.176 | 559.7294 | NaN | 506.8399
4673.176 | 560.6014 | NaN | 507.8347
4674.176 | 561.2293 | NaN | 509.6657
4675.176 | 562.3067 | NaN | 510.4926
4676.176 | 562.9664 | NaN | 510.3857
4677.176 | 563.3071 | NaN | 510.1262
4678.176 | 562.9088 | NaN | 510.7736
4679.176 | 563.2487 | NaN | 510.9359
4680.176 | 564.0002 | NaN | 511.6512
4681.176 | 564.7661 | NaN | 511.3453
4682.176 | 565.6626 | NaN | 510.9006
4683.176 | 566.8088 | NaN | 510.9803
4684.176 | 566.7364 | NaN | 511.2209
4685.176 | 566.9456 | NaN | 511.6394
4686.176 | 566.9451 | NaN | 512.8368
4687.176 | 567.3594 | NaN | 513.8761
4688.176 | 567.8143 | NaN | 514.6543
4689.176 | 567.7207 | NaN | 514.6837
4690.176 | 567.4868 | NaN | 514.2015
4691.176 | 567.0173 | NaN | 513.7883
4692.176 | 567.4192 | NaN | 514.8202
4693.176 | 567.2264 | NaN | 516.1178
4694.176 | 567.6558 | NaN | 516.3723
4695.176 | 567.2636 | NaN | 516.1918
4696.176 | 567.4658 | NaN | 516.2863
4697.176 | 568.7369 | NaN | 517.6561
4698.176 | 569.9658 | NaN | 518.0883
4699.176 | 570.6167 | NaN | 516.413
4700.176 | 570.1748 | NaN | 514.7827
4701.176 | 570.1173 | NaN | 513.6674
4702.176 | 570.6018 | NaN | 513.8497
4703.176 | 571.9372 | NaN | 514.863
4704.176 | 571.4072 | NaN | 514.4994
4705.176 | 571.0736 | NaN | 513.6954
4706.176 | 569.8392 | NaN | 512.2492
4707.176 | 569.8033 | NaN | 510.941
4708.176 | 569.6127 | NaN | 511.3683
4709.176 | 569.1481 | NaN | 512.0271
4710.176 | 568.5921 | NaN | 512.8721
4711.176 | 568.6944 | NaN | 513.2026
4712.176 | 570.1441 | NaN | 514.5311
4713.176 | 570.7962 | NaN | 514.687
4714.176 | 570.9714 | NaN | 514.4035
4715.176 | 571.691 | NaN | 514.2169
4716.176 | 572.0687 | NaN | 514.2306
4717.176 | 572.6888 | NaN | 514.5807
4718.176 | 572.7126 | NaN | 514.7038
4719.176 | 572.2706 | NaN | 514.7882
4720.176 | 572.5407 | NaN | 514.4222
4721.176 | 572.0902 | NaN | 515.0972
4722.176 | 572.6937 | NaN | 515.7904
4723.176 | 573.3331 | NaN | 515.9395
4724.176 | 572.5984 | NaN | 515.2754
4725.176 | 572.0668 | NaN | 514.609
4726.176 | 571.4695 | NaN | 515.1812
4727.176 | 571.064 | NaN | 514.6879
4728.176 | 570.9205 | NaN | 515.2251
4729.176 | 570.5394 | NaN | 514.7326
4730.176 | 571.7287 | NaN | 514.9306
4731.176 | 571.9706 | NaN | 514.8799
4732.176 | 572.6631 | NaN | 516.5691
4733.176 | 572.8677 | NaN | 517.5416
4734.176 | 572.7734 | NaN | 517.2633
4735.176 | 572.6098 | NaN | 517.8496
4736.176 | 573.6238 | NaN | 518.0717
4737.176 | 574.0683 | NaN | 517.9072
4738.176 | 573.9898 | NaN | 517.1543
4739.176 | 574.4141 | NaN | 516.3183
4740.176 | 574.1879 | NaN | 516.2975
4741.176 | 573.5509 | NaN | 516.3548
4742.176 | 572.2504 | NaN | 516.6965
4743.176 | 572.1923 | NaN | 518.953
4744.176 | 572.7078 | NaN | 520.2751
4745.176 | 572.1279 | NaN | 520.4472
4746.176 | 573.0464 | NaN | 520.7464
4747.176 | 573.6248 | NaN | 520.9401
4748.176 | 573.0513 | NaN | 520.5343
4749.176 | 572.8479 | NaN | 520.0708
4750.176 | 572.5186 | NaN | 520.26
4751.176 | 572.4331 | NaN | 520.0866
4752.176 | 572.2278 | NaN | 519.4507
4753.176 | 572.9837 | NaN | 518.278
4754.176 | 572.6345 | NaN | 517.5952
4755.176 | 571.9441 | NaN | 517.042
4756.176 | 570.9467 | NaN | 516.5958
4757.176 | 570.2912 | NaN | 516.7554
4758.176 | 570.6234 | NaN | 516.8324
4759.176 | 570.0607 | NaN | 518.6346
4760.176 | 569.4693 | NaN | 518.0851
4761.176 | 568.9488 | NaN | 516.9267
4762.176 | 568.5566 | NaN | 515.4737
4763.176 | 567.8511 | NaN | 514.2506
4764.176 | 567.6133 | NaN | 514.077
4765.176 | 567.0111 | NaN | 514.5846
4766.176 | 566.6294 | NaN | 515.1648
4767.176 | 565.5813 | NaN | 515.6663
4768.176 | 565.0034 | NaN | 514.8886
4769.176 | 564.4049 | NaN | 514.3775
4770.176 | 564.5217 | NaN | 513.9612
4771.176 | 563.6723 | NaN | 515.2838
4772.176 | 563.286 | NaN | 516.2141
4773.176 | 562.7336 | NaN | 516.8271
4774.176 | 562.8831 | NaN | 516.7261
4775.176 | 563.3313 | NaN | 517.2463
4776.176 | 564.4855 | NaN | 517.0724
4777.176 | 564.9149 | NaN | 517.3967
4778.176 | 565.3751 | NaN | 516.7343
4779.176 | 566.5472 | NaN | 516.4879
4780.176 | 565.9947 | NaN | 516.7332
4781.176 | 566.0618 | NaN | 516.0616
4782.176 | 565.6217 | NaN | 515.3485
4783.176 | 565.2052 | NaN | 515.1613
4784.176 | 564.4326 | NaN | 514.8293
4785.176 | 564.5089 | NaN | 514.6071
4786.176 | 563.8333 | NaN | 513.9955
4787.176 | 563.7971 | NaN | 514.5654
4788.176 | 563.6379 | NaN | 514.5679
4789.176 | 563.8108 | NaN | 514.9356
4790.176 | 564.1136 | NaN | 516.491
4791.176 | 564.2568 | NaN | 516.7875
4792.176 | 565.6259 | NaN | 517.1586
4793.176 | 564.902 | NaN | 516.1659
4794.176 | 564.0072 | NaN | 515.3801
4795.176 | 563.4191 | NaN | 515.5176
4796.176 | 563.1332 | NaN | 516.1657
4797.176 | 563.0412 | NaN | 516.7825
4798.176 | 562.893 | NaN | 517.0217
4799.176 | 563.04 | NaN | 518.3069
4800.176 | 563.1924 | NaN | 519.1635
4801.176 | 563.9691 | NaN | 520.8426
4802.176 | 564.1647 | NaN | 520.2131
4803.176 | 564.0515 | NaN | 518.6765
4804.176 | 563.4968 | NaN | 517.773
4805.176 | 563.4875 | NaN | 517.718
4806.176 | 562.2323 | NaN | 517.0594
4807.176 | 561.8959 | NaN | 516.7085
4808.176 | 562.0642 | NaN | 516.2836
4809.176 | 561.9935 | NaN | 516.1207
4810.176 | 562.1528 | NaN | 516.1124
4811.176 | 562.5342 | NaN | 516.3149
4812.176 | 562.2937 | NaN | 518.2661
4813.176 | 562.5525 | NaN | 518.7489
4814.176 | 562.9667 | NaN | 518.5882
4815.176 | 564.003 | NaN | 519.9876
4816.176 | 564.1123 | NaN | 520.176
4817.176 | 564.2383 | NaN | 520.0328
4818.176 | 563.8781 | NaN | 519.1201
4819.176 | 563.2919 | NaN | 518.1087
4820.176 | 564.4639 | NaN | 519.5902
4821.176 | 564.5998 | NaN | 519.7982
4822.176 | 564.2425 | NaN | 519.4814
4823.176 | 565.0709 | NaN | 520.287
4824.176 | 566.3179 | NaN | 520.3033
4825.176 | 567.0727 | NaN | 521.3277
4826.176 | 567.0806 | NaN | 520.6706
4827.176 | 566.27 | NaN | 520.2368
4828.176 | 565.9688 | NaN | 519.9143
4829.176 | 566.0914 | NaN | 520.9795
4830.176 | 565.5776 | NaN | 521.7479
4831.176 | 565.2915 | NaN | 523.6248
4832.176 | 565.8602 | NaN | 523.8728
4833.176 | 566.5169 | NaN | 524.2863
4834.176 | 566.9312 | NaN | 524.7821
4835.176 | 567.4949 | NaN | 524.0777
4836.176 | 568.451 | NaN | 524.2949
4837.176 | 568.9049 | NaN | 524.3007
4838.176 | 569.4918 | NaN | 524.8873
4839.176 | 569.8216 | NaN | 525.5043
4840.176 | 570.2516 | NaN | 526.1571
4841.176 | 571.2588 | NaN | 527.684
4842.176 | 571.223 | NaN | 527.3892
4843.176 | 571.4237 | NaN | 527.1968
4844.176 | 571.9915 | NaN | 526.7724
4845.176 | 571.8607 | NaN | 527.0191
4846.176 | 571.8484 | NaN | 527.4311
4847.176 | 571.9562 | NaN | 526.8092
4848.176 | 571.6909 | NaN | 527.5347
4849.176 | 572.1577 | NaN | 528.7155
4850.176 | 572.2195 | NaN | 529.3032
4851.176 | 571.274 | NaN | 529.5605
4852.176 | 570.9765 | NaN | 530.4824
4853.176 | 570.4191 | NaN | 530.6097
4854.176 | 570.4544 | NaN | 531.2759
4855.176 | 570.3942 | NaN | 530.9397
4856.176 | 570.5691 | NaN | 530.784
4857.176 | 571.0236 | NaN | 530.0666
4858.176 | 570.9655 | NaN | 529.4646
4859.176 | 571.2798 | NaN | 528.9525
4860.176 | 572.2765 | NaN | 529.0376
4861.176 | 574.1788 | NaN | 529.8364
4862.176 | 574.6923 | NaN | 531.3072
4863.176 | 574.7557 | NaN | 530.7544
4864.176 | 573.806 | NaN | 530.1138
4865.176 | 573.5407 | NaN | 529.2693
4866.176 | 572.8472 | NaN | 528.7749
4867.176 | 572.442 | NaN | 528.4705
4868.176 | 572.2842 | NaN | 528.0287
4869.176 | 574.1824 | NaN | 527.4553
4870.176 | 574.6646 | NaN | 527.3921
4871.176 | 574.4753 | NaN | 527.3384
4872.176 | 575.5467 | NaN | 526.7835
4873.176 | 576.3516 | NaN | 527.1572
4874.176 | 576.2679 | NaN | 527.4774
4875.176 | 575.6987 | NaN | 527.4172
4876.176 | 574.7635 | NaN | 527.635
4877.176 | 573.8214 | NaN | 527.0883
4878.176 | 573.4812 | NaN | 525.9179
4879.176 | 573.0654 | NaN | 526.2717
4880.176 | 574.1156 | NaN | 526.3532
4881.176 | 574.9598 | NaN | 527.5245
4882.176 | 574.4213 | NaN | 526.8476
4883.176 | 574.7645 | NaN | 526.9444
4884.176 | 575.7214 | NaN | 528.6136
4885.176 | 575.7647 | NaN | 528.5811
4886.176 | 575.4847 | NaN | 529.8765
4887.176 | 575.913 | NaN | 529.6067
4888.176 | 575.1701 | NaN | 528.5099
4889.176 | 574.6928 | NaN | 529.5516
4890.176 | 575.1819 | NaN | 530.3919
4891.176 | 574.9184 | NaN | 530.2066
4892.176 | 574.8334 | NaN | 529.4814
4893.176 | 574.2784 | NaN | 528.7842
4894.176 | 574.3885 | NaN | 528.3918
4895.176 | 574.3394 | NaN | 529.1135
4896.176 | 574.5902 | NaN | 529.6151
4897.176 | 574.6342 | NaN | 530.5704
4898.176 | 574.7806 | NaN | 530.505
4899.176 | 574.6372 | NaN | 529.7919
4900.176 | 576.1557 | NaN | 530.3429
4901.176 | 576.0231 | NaN | 531.1508
4902.176 | 576.7675 | NaN | 531.5327
4903.176 | 577.4196 | NaN | 532.3544
4904.176 | 578.8976 | NaN | 533.4993
4905.176 | 579.4003 | NaN | 532.6807
4906.176 | 581.1005 | NaN | 532.5548
4907.176 | 580.622 | NaN | 531.6463
4908.176 | 581.7652 | NaN | 532.8766
4909.176 | 581.7691 | NaN | 533.2353
4910.176 | 582.8546 | NaN | 534.565
4911.176 | 584.029 | NaN | 536.9564
4912.176 | 584.107 | NaN | 536.6622
4913.176 | 583.6361 | NaN | 534.9541
4914.176 | 583.547 | NaN | 533.4345
4915.176 | 582.5422 | NaN | 532.2939
4916.176 | 581.7814 | NaN | 531.6477
4917.176 | 582.2735 | NaN | 531.3771
4918.176 | 582.3924 | NaN | 531.3731
4919.176 | 581.2734 | NaN | 531.4764
4920.176 | 581.3126 | NaN | 533.201
4921.176 | 581.4301 | NaN | 534.8404
4922.176 | 581.9658 | NaN | 536.5177
4923.176 | 583.0474 | NaN | 536.0245
4924.176 | 582.342 | NaN | 536.1423
4925.176 | 583.1397 | NaN | 536.7534
4926.176 | 583.4037 | NaN | 536.6453
4927.176 | 582.278 | NaN | 537.6159
4928.176 | 582.0248 | NaN | 536.6188
4929.176 | 581.5912 | NaN | 535.4589
4930.176 | 581.9748 | NaN | 535.6114
4931.176 | 581.1159 | NaN | 536.3323
4932.176 | 579.3815 | NaN | 535.5746
4933.176 | 578.7775 | NaN | 534.8772
4934.176 | 577.9326 | NaN | 533.7691
4935.176 | 577.7732 | NaN | 532.7305
4936.176 | 577.4961 | NaN | 532.1036
4937.176 | 576.8001 | NaN | 532.1769
4938.176 | 576.3318 | NaN | 532.8469
4939.176 | 575.598 | NaN | 533.7107
4940.176 | 574.8331 | NaN | 533.7279
4941.176 | 574.0929 | NaN | 534.0903
4942.176 | 574.3164 | NaN | 533.3902
4943.176 | 574.1761 | NaN | 532.595
4944.176 | 572.6716 | NaN | 531.9478
4945.176 | 572.5377 | NaN | 531.5273
4946.176 | 572.2563 | NaN | 531.8003
4947.176 | 571.3612 | NaN | 531.9444
4948.176 | 571.3876 | NaN | 531.4721
4949.176 | 571.2779 | NaN | 530.4074
4950.176 | 571.033 | NaN | 530.153
4951.176 | 571.297 | NaN | 530.9759
4952.176 | 570.5417 | NaN | 531.4422
4953.176 | 569.9724 | NaN | 530.812
4954.176 | 569.5945 | NaN | 530.6356
4955.176 | 569.0676 | NaN | 530.5631
4956.176 | 568.2888 | NaN | 531.1396
4957.176 | 566.9794 | NaN | 531.5912
4958.176 | 566.3342 | NaN | 531.3993
4959.176 | 567.2408 | NaN | 531.4516
4960.176 | 566.9305 | NaN | 531.3429
4961.176 | 567.2804 | NaN | 531.1401
4962.176 | 568.0875 | NaN | 531.0198
4963.176 | 568.0799 | NaN | 530.7084
4964.176 | 567.4703 | NaN | 530.6869
4965.176 | 566.9663 | NaN | 530.7828
4966.176 | 567.5908 | NaN | 530.0142
4967.176 | 567.9117 | NaN | 529.771
4968.176 | 567.3717 | NaN | 529.709
4969.176 | 568.8001 | NaN | 530.0187
4970.176 | 568.5202 | NaN | 530.2504
4971.176 | 569.8295 | NaN | 529.9599
4972.176 | 570.5286 | NaN | 529.3744
4973.176 | 569.4795 | NaN | 528.5053
4974.176 | 570.261 | NaN | 527.269
4975.176 | 570.6522 | NaN | 526.2966
4976.176 | 569.8586 | NaN | 525.9965
4977.176 | 569.0187 | NaN | 524.9741
4978.176 | 569.8722 | NaN | 525.1949
4979.176 | 570.6098 | NaN | 526.0141
4980.176 | 571.5622 | NaN | 526.8791
4981.176 | 572.6429 | NaN | 527.2158
4982.176 | 573.898 | NaN | 527.7764
4983.176 | 574.0732 | NaN | 528.4184
4984.176 | 574.7667 | NaN | 528.8285
4985.176 | 576.9731 | NaN | 529.7141
4986.176 | 577.9617 | NaN | 530.7031
4987.176 | 577.5046 | NaN | 531.163
4988.176 | 578.5556 | NaN | 531.1511
4989.176 | 578.2647 | NaN | 530.9911
4990.176 | 578.3014 | NaN | 530.7366
4991.176 | 579.2292 | NaN | 531.5843
4992.176 | 580.0313 | NaN | 532.5405
4993.176 | 580.9803 | NaN | 532.8329
4994.176 | 580.5218 | NaN | 533.1919
4995.176 | 580.5761 | NaN | 533.8857
4996.176 | 580.8092 | NaN | 534.9506
4997.176 | 580.3512 | NaN | 534.6758
4998.176 | 580.1869 | NaN | 534.7038
4999.176 | 580.202 | NaN | 535.1634
5000.176 | 580.0118 | NaN | 535.4552
5001.176 | 579.7248 | NaN | 534.9089
5002.176 | 578.6639 | NaN | 534.6346
5003.176 | 578.4371 | NaN | 536.5706
5004.176 | 577.9158 | NaN | 536.7134
5005.176 | 577.1304 | NaN | 536.4924
5006.176 | 576.9012 | NaN | 536.1946
5007.176 | 578.0887 | NaN | 536.1916
5008.176 | 578.9984 | NaN | 536.6316
5009.176 | 578.5779 | NaN | 536.5829
5010.176 | 578.0726 | NaN | 536.0019
5011.176 | 577.499 | NaN | 535.3513
5012.176 | 578.053 | NaN | 535.2118
5013.176 | 577.5054 | NaN | 535.6863
5014.176 | 576.3929 | NaN | 535.3948
5015.176 | 575.803 | NaN | 535.1208
5016.176 | 575.1148 | NaN | 534.4038
5017.176 | 574.0953 | NaN | 533.4633
5018.176 | 573.1342 | NaN | 532.9363
5019.176 | 572.7908 | NaN | 532.1138
5020.176 | 571.8761 | NaN | 531.3838
5021.176 | 571.0671 | NaN | 531.0127
5022.176 | 570.8692 | NaN | 530.729
5023.176 | 571.0837 | NaN | 532.2241
5024.176 | 571.6259 | NaN | 532.078
5025.176 | 570.6779 | NaN | 533.0022
5026.176 | 570.4621 | NaN | 533.4334
5027.176 | 571.4099 | NaN | 533.6142
5028.176 | 571.9301 | NaN | 533.8501
5029.176 | 572.0267 | NaN | 533.8961
5030.176 | 571.5862 | NaN | 533.1306
5031.176 | 571.6744 | NaN | 532.9755
5032.176 | 572.4694 | NaN | 534.1886
5033.176 | 571.8776 | NaN | 534.6364
5034.176 | 571.0645 | NaN | 534.0736
5035.176 | 571.0284 | NaN | 534.5428
5036.176 | 571.9735 | NaN | 534.844
5037.176 | 572.2137 | NaN | 535.4636
5038.176 | 572.1632 | NaN | 535.3007
5039.176 | 571.2901 | NaN | 534.6804
5040.176 | 570.2621 | NaN | 534.8038
5041.176 | 569.7264 | NaN | 534.3706
5042.176 | 569.8103 | NaN | 534.7377
5043.176 | 569.8509 | NaN | 535.8035
5044.176 | 569.5305 | NaN | 535.8552
5045.176 | 570.5433 | NaN | 536.2651
5046.176 | 570.3324 | NaN | 537.2581
5047.176 | 569.9937 | NaN | 537.5632
5048.176 | 569.1066 | NaN | 536.4337
5049.176 | 568.2325 | NaN | 534.624
5050.176 | 566.6518 | NaN | 532.6232
5051.176 | 565.2274 | NaN | 530.8365
5052.176 | 564.6596 | NaN | 529.9223
5053.176 | 565.2347 | NaN | 529.7076
5054.176 | 565.0466 | NaN | 529.1545
5055.176 | 564.9609 | NaN | 529.2377
5056.176 | 565.2856 | NaN | 529.3345
5057.176 | 565.0574 | NaN | 530.1435
5058.176 | 564.4319 | NaN | 530.1968
5059.176 | 563.7974 | NaN | 530.5991
5060.176 | 564.3051 | NaN | 531.4776
5061.176 | 564.837 | NaN | 532.4508
5062.176 | 565.1603 | NaN | 532.612
5063.176 | 565.4719 | NaN | 532.6016
5064.176 | 566.4983 | NaN | 532.8671
5065.176 | 567.2814 | NaN | 533.4129
5066.176 | 567.5898 | NaN | 533.0791
5067.176 | 567.7252 | NaN | 532.7384
5068.176 | 568.3275 | NaN | 533.7573
5069.176 | 568.7972 | NaN | 535.4986
5070.176 | 569.622 | NaN | 535.4215
5071.176 | 570.0547 | NaN | 534.8108
5072.176 | 570.4473 | NaN | 534.1225
5073.176 | 570.8231 | NaN | 534.205
5074.176 | 570.8832 | NaN | 534.4571
5075.176 | 570.5168 | NaN | 533.9295
5076.176 | 569.7187 | NaN | 533.0523
5077.176 | 568.708 | NaN | 532.2668
5078.176 | 568.4299 | NaN | 531.7091
5079.176 | 567.8668 | NaN | 531.6025
5080.176 | 568.6407 | NaN | 531.5705
5081.176 | 568.5806 | NaN | 532.5895
5082.176 | 568.2521 | NaN | 532.6913
5083.176 | 568.7332 | NaN | 533.7612
5084.176 | 568.9363 | NaN | 535.6655
5085.176 | 568.9306 | NaN | 536.4587
5086.176 | 569.0123 | NaN | 536.254
5087.176 | 569.033 | NaN | 535.245
5088.176 | 569.2229 | NaN | 534.513
5089.176 | 570.221 | NaN | 534.6573
5090.176 | 570.4485 | NaN | 534.1335
5091.176 | 570.6081 | NaN | 533.6777
5092.176 | 570.4901 | NaN | 532.8629
5093.176 | 569.8756 | NaN | 532.346
5094.176 | 568.7935 | NaN | 531.3595
5095.176 | 568.3819 | NaN | 531.4547
5096.176 | 568.3816 | NaN | 531.7375
5097.176 | 568.2802 | NaN | 531.5768
5098.176 | 567.8072 | NaN | 531.2796
5099.176 | 567.3737 | NaN | 530.4374
5100.176 | 567.4644 | NaN | 531.1524
5101.176 | 567.8408 | NaN | 532.6863
5102.176 | 568.3906 | NaN | 533.8215
5103.176 | 568.6229 | NaN | 533.7937
5104.176 | 568.2024 | NaN | 534.7389
5105.176 | 568.0244 | NaN | 534.7048
5106.176 | 568.2569 | NaN | 534.5995
5107.176 | 567.8911 | NaN | 534.7319
5108.176 | 567.994 | NaN | 535.1071
5109.176 | 568.1413 | NaN | 534.8609
5110.176 | 567.955 | NaN | 534.969
5111.176 | 567.6597 | NaN | 534.4371
5112.176 | 567.9346 | NaN | 533.4231
5113.176 | 567.4197 | NaN | 533.6175
5114.176 | 567.2655 | NaN | 532.3226
5115.176 | 568.0514 | NaN | 532.612
5116.176 | 568.7825 | NaN | 533.6722
5117.176 | 568.9446 | NaN | 535.2835
5118.176 | 569.2266 | NaN | 536.4086
5119.176 | 569.5673 | NaN | 537.8152
5120.176 | 570.1237 | NaN | 539.1491
5121.176 | 570.3146 | NaN | 539.4071
5122.176 | 570.4166 | NaN | 539.6655
5123.176 | 569.9769 | NaN | 540.3573
5124.176 | 569.6962 | NaN | 540.5315
5125.176 | 569.3972 | NaN | 540.1658
5126.176 | 569.6535 | NaN | 540.0617
5127.176 | 569.3882 | NaN | 539.4992
5128.176 | 569.6872 | NaN | 539.0144
5129.1917 | 569.6249 | NaN | 538.2354
5130.176 | 568.7808 | NaN | 537.0219
5131.176 | 568.5224 | NaN | 536.1847
5132.176 | 569.9166 | NaN | 535.7346
5133.176 | 571.8685 | NaN | 535.802
5134.1917 | 572.275 | NaN | 536.4765
5135.1917 | 571.8813 | NaN | 536.1015
5136.176 | 572.2231 | NaN | 536.5044
5137.176 | 573.0062 | NaN | 537.4771
5138.176 | 573.0959 | NaN | 537.4652
5139.176 | 573.3867 | NaN | 537.1339
5140.176 | 573.5377 | NaN | 537.2865
5141.176 | 572.8296 | NaN | 536.9136
5142.176 | 571.6155 | NaN | 537.3587
5143.176 | 570.6387 | NaN | 536.5946
5144.176 | 570.1687 | NaN | 535.8726
5145.176 | 569.6914 | NaN | 535.4706
5146.176 | 569.2492 | NaN | 534.287
5147.176 | 568.2668 | NaN | 534.2087
5148.176 | 568.0136 | NaN | 533.5136
5149.176 | 567.6973 | NaN | 533.3274
5150.176 | 567.3397 | NaN | 533.2058
5151.176 | 567.3601 | NaN | 532.7868
5152.176 | 566.8199 | NaN | 533.3324
5153.176 | 566.0725 | NaN | 532.5369
5154.176 | 565.1256 | NaN | 532.1708
5155.176 | 564.2742 | NaN | 532.6413
5156.176 | 564.2848 | NaN | 532.5946
5157.176 | 563.942 | NaN | 531.7947
5158.176 | 564.2063 | NaN | 531.8623
5159.176 | 563.9654 | NaN | 531.092
5160.176 | 563.6172 | NaN | 530.4407
5161.176 | 563.7024 | NaN | 530.2726
5162.176 | 562.8851 | NaN | 530.7329
5163.176 | 561.3029 | NaN | 529.8043
5164.176 | 560.3082 | NaN | 528.976
5165.176 | 559.6601 | NaN | 528.7268
5166.176 | 559.3421 | NaN | 527.9323
5167.176 | 559.0903 | NaN | 527.2515
5168.176 | 559.3096 | NaN | 526.3136
5169.176 | 558.9268 | NaN | 525.6372
5170.176 | 558.2563 | NaN | 525.123
5171.176 | 558.0467 | NaN | 525.4891
5172.176 | 559.5541 | NaN | 525.3026
5173.176 | 560.1684 | NaN | 526.3784
5174.176 | 560.3441 | NaN | 527.7406
5175.176 | 559.3279 | NaN | 527.8427
5176.176 | 559.4778 | NaN | 526.8686
5177.176 | 558.5731 | NaN | 526.2196
5178.176 | 558.8715 | NaN | 526.6299
5179.176 | 559.2993 | NaN | 526.6151
5180.176 | 560.0065 | NaN | 526.8223
5181.176 | 560.512 | NaN | 527.3879
5182.176 | 560.6872 | NaN | 528.8784
5183.176 | 560.8405 | NaN | 529.9948
5184.176 | 560.2417 | NaN | 530.0829
5185.176 | 559.3949 | NaN | 529.4896
5186.176 | 559.1139 | NaN | 529.5186
5187.176 | 558.4158 | NaN | 529.1624
5188.176 | 558.1992 | NaN | 528.6647
5189.176 | 557.2865 | NaN | 527.9013
5190.176 | 556.6422 | NaN | 527.0066
5191.176 | 555.7592 | NaN | 526.1715
5192.176 | 554.9714 | NaN | 526.0785
5193.176 | 554.6841 | NaN | 525.9018
5194.176 | 554.2259 | NaN | 525.4529
5195.176 | 553.6903 | NaN | 525.343
5196.176 | 553.9885 | NaN | 526.6077
5197.176 | 554.1561 | NaN | 528.0095
5198.176 | 553.9524 | NaN | 528.8729
5199.176 | 553.3878 | NaN | 527.8125
5200.176 | 553.0138 | NaN | 526.9458
5201.176 | 553.207 | NaN | 526.6072
5202.176 | 552.6805 | NaN | 526.397
5203.176 | 552.2933 | NaN | 525.5437
5204.176 | 552.1243 | NaN | 524.4111
5205.176 | 551.6392 | NaN | 524.3628
5206.176 | 551.5832 | NaN | 524.4695
5207.176 | 550.9986 | NaN | 523.6428
5208.176 | 550.3474 | NaN | 522.9507
5209.176 | 550.2317 | NaN | 523.4121
5210.176 | 550.2778 | NaN | 524.5126
5211.176 | 550.2837 | NaN | 524.1108
5212.176 | 550.2127 | NaN | 524.1346
5213.176 | 551.1743 | NaN | 524.0496
5214.176 | 551.9725 | NaN | 524.554
5215.176 | 551.9006 | NaN | 525.4235
5216.176 | 552.3076 | NaN | 525.7966
5217.176 | 552.9354 | NaN | 525.3853
5218.176 | 553.2595 | NaN | 525.0964
5219.176 | 555.221 | NaN | 525.2643
5220.176 | 556.1013 | NaN | 525.9934
5221.176 | 556.4109 | NaN | 526.3438
5222.176 | 556.3225 | NaN | 526.6948
5223.176 | 556.1414 | NaN | 527.6218
5224.176 | 555.915 | NaN | 528.4349
5225.176 | 555.2868 | NaN | 528.4039
5226.176 | 554.9081 | NaN | 528.9326
5227.176 | 554.2772 | NaN | 528.9488
5228.176 | 553.9162 | NaN | 528.4502
5229.176 | 554.0777 | NaN | 528.0697
5230.176 | 553.9176 | NaN | 527.6321
5231.176 | 554.0938 | NaN | 527.3909
5232.176 | 553.9792 | NaN | 527.8036
5233.176 | 553.9634 | NaN | 528.7865
5234.176 | 553.8451 | NaN | 528.2311
5235.176 | 553.1516 | NaN | 527.1955
5236.176 | 552.3644 | NaN | 526.2742
5237.176 | 551.5335 | NaN | 525.6504
5238.176 | 552.0952 | NaN | 525.4385
5239.176 | 553.0666 | NaN | 527.1258
5240.176 | 553.9604 | NaN | 527.3668
5241.176 | 554.3617 | NaN | 527.6899
5242.176 | 553.8684 | NaN | 528.2795
5243.176 | 553.2835 | NaN | 527.1596
5244.176 | 552.1661 | NaN | 525.7014
5245.176 | 551.7337 | NaN | 524.5286
5246.176 | 551.3502 | NaN | 523.8125
5247.176 | 551.026 | NaN | 523.6443
5248.176 | 551.3674 | NaN | 524.0586
5249.176 | 551.6771 | NaN | 524.9717
5250.176 | 552.1652 | NaN | 525.7762
5251.176 | 552.6214 | NaN | 527.1075
5252.176 | 552.588 | NaN | 528.4523
5253.176 | 553.8864 | NaN | 528.5742
5254.176 | 555.0927 | NaN | 528.9249
5255.176 | 555.4125 | NaN | 528.11
5256.176 | 555.012 | NaN | 526.9939
5257.176 | 554.3958 | NaN | 526.4015
5258.176 | 554.383 | NaN | 526.0813
5259.176 | 554.408 | NaN | 526.4269
5260.176 | 553.9009 | NaN | 525.2807
5261.176 | 553.8226 | NaN | 524.3352
5262.176 | 554.3454 | NaN | 524.905
5263.176 | 555.0773 | NaN | 526.5186
5264.176 | 555.6668 | NaN | 527.8932
5265.176 | 556.575 | NaN | 528.6789
5266.176 | 556.5985 | NaN | 529.8745
5267.176 | 556.2428 | NaN | 529.5752
5268.176 | 555.6274 | NaN | 528.7119
5269.176 | 554.9941 | NaN | 527.4768
5270.176 | 554.6605 | NaN | 526.7441
5271.176 | 553.5729 | NaN | 526.328
5272.176 | 552.9894 | NaN | 525.7085
5273.176 | 552.4029 | NaN | 525.1326
5274.176 | 551.9029 | NaN | 524.4369
5275.176 | 551.4925 | NaN | 525.2412
5276.176 | 551.0851 | NaN | 526.1699
5277.176 | 550.7499 | NaN | 525.6331
5278.176 | 550.9522 | NaN | 524.9334
5279.176 | 551.8504 | NaN | 524.637
5280.176 | 551.8748 | NaN | 524.0281
5281.176 | 551.7583 | NaN | 523.2542
5282.176 | 551.8253 | NaN | 522.1217
5283.176 | 551.0609 | NaN | 522.0615
5284.176 | 550.9067 | NaN | 521.8269
5285.176 | 550.7035 | NaN | 522.2499
5286.176 | 550.7044 | NaN | 522.2764
5287.176 | 551.8942 | NaN | 521.99
5288.176 | 551.865 | NaN | 521.5294
5289.176 | 551.6859 | NaN | 521.3684
5290.176 | 558.7332 | NaN | 521.4528
5291.176 | 556.7488 | NaN | 521.0961
5292.176 | 556.1161 | NaN | 521.2861
5293.176 | 555.7655 | NaN | 522.5174
5294.176 | 555.456 | NaN | 523.4114
5295.176 | 555.628 | NaN | 523.7922
5296.176 | 555.4516 | NaN | 523.4391
5297.176 | 554.5109 | NaN | 522.5973
5298.176 | 553.9062 | NaN | 522.3134
5299.176 | 552.9639 | NaN | 521.4235
5300.176 | 552.1325 | NaN | 520.7681
5301.176 | 551.4271 | NaN | 520.3147
5302.176 | 551.8579 | NaN | 520.6525
5303.176 | 551.7136 | NaN | 520.6353
5304.176 | 551.4664 | NaN | 520.2683
5305.1917 | 551.0837 | NaN | 519.6182
5306.176 | 550.46 | NaN | 518.911
5307.176 | 550.1287 | NaN | 518.7111
5308.176 | 549.5812 | NaN | 519.0862
5309.176 | 549.2152 | NaN | 519.5395
5310.176 | 548.5365 | NaN | 519.0927
5311.176 | 548.2462 | NaN | 518.5638
5312.176 | 547.6787 | NaN | 518.0122
5313.176 | 546.9758 | NaN | 517.827
5314.176 | 546.9929 | NaN | 518.0019
5315.176 | 547.0847 | NaN | 518.1409
5316.176 | 547.2828 | NaN | 518.3079
5317.176 | 546.859 | NaN | 518.0112
5318.176 | 546.3259 | NaN | 517.8235
5319.176 | 545.9505 | NaN | 517.5338
5320.176 | 545.7472 | NaN | 517.4712
5321.176 | 546.1535 | NaN | 517.0907
5322.176 | 545.788 | NaN | 516.7293
5323.176 | 546.1463 | NaN | 516.9338
5324.176 | 546.0378 | NaN | 517.8011
5325.176 | 545.832 | NaN | 518.5031
5326.176 | 545.4394 | NaN | 518.4223
5327.176 | 545.4388 | NaN | 518.0388
5328.176 | 544.9724 | NaN | 518.4474
5329.176 | 544.8011 | NaN | 519.7697
5330.176 | 544.7988 | NaN | 520.7422
5331.176 | 544.781 | NaN | 520.5309
5332.176 | 544.8359 | NaN | 520.0345
5333.176 | 545.0705 | NaN | 520.3083
5334.176 | 544.9496 | NaN | 520.5497
5335.1917 | 544.5299 | NaN | 519.9972
5336.176 | 543.9565 | NaN | 519.3147
5337.176 | 544.1077 | NaN | 518.9558
5338.176 | 543.6498 | NaN | 519.1733
5339.176 | 543.2189 | NaN | 518.64
5340.176 | 542.4298 | NaN | 518.2208
5341.176 | 541.7479 | NaN | 517.9619
5342.176 | 541.1598 | NaN | 517.2207
5343.176 | 540.3371 | NaN | 516.9342
5344.176 | 540.0197 | NaN | 516.4526
5345.176 | 539.411 | NaN | 516.3944
5346.176 | 538.8828 | NaN | 515.8196
5347.176 | 538.5943 | NaN | 514.6769
5348.176 | 538.2051 | NaN | 513.8738
5349.176 | 538.7501 | NaN | 512.3081
5350.176 | 537.8975 | NaN | 513.2655
5351.176 | 538.5254 | NaN | 513.8239
5352.176 | 538.5407 | NaN | 514.6007
5353.176 | 538.3372 | NaN | 515.2715
5354.176 | 537.9498 | NaN | 515.1322
5355.176 | 537.856 | NaN | 514.7489
5356.176 | 537.4997 | NaN | 513.7417
5357.176 | 537.4931 | NaN | 513.8064
5358.176 | 537.2448 | NaN | 513.1378
5359.176 | 537.1727 | NaN | 513.2025
5360.176 | 536.9635 | NaN | 513.7649
5361.176 | 536.7548 | NaN | 514.4557
5362.176 | 537.1549 | NaN | 515.4177
5363.176 | 537.8677 | NaN | 517.8227
5364.176 | 539.1555 | NaN | 521.3777
5365.176 | 539.6472 | NaN | 521.8796
5366.176 | 539.8087 | NaN | 521.3935
5367.176 | 540.2878 | NaN | 520.479
5368.176 | 540.5168 | NaN | 520.0974
5369.176 | 540.4299 | NaN | 519.1078
5370.176 | 540.2886 | NaN | 517.7484
5371.176 | 540.1634 | NaN | 516.1745
5372.176 | 540.7147 | NaN | 515.7192
5373.176 | 541.4746 | NaN | 516.0277
5374.176 | 540.7061 | NaN | 515.7574
5375.176 | 539.9706 | NaN | 514.3955
5376.176 | 539.5465 | NaN | 513.9664
5377.176 | 539.9194 | NaN | 513.3582
5378.176 | 540.2783 | NaN | 513.5394
5379.176 | 540.4797 | NaN | 513.7816
5380.176 | 540.3455 | NaN | 513.5887
5381.176 | 539.9479 | NaN | 512.8632
5382.176 | 539.7908 | NaN | 512.2128
5383.176 | 540.0387 | NaN | 511.4533
5384.176 | 540.1935 | NaN | 511.0524
5385.176 | 539.9814 | NaN | 510.5839
5386.176 | 539.9556 | NaN | 510.9501
5387.176 | 540.1292 | NaN | 511.3558
5388.176 | 540.5912 | NaN | 512.1852
5389.176 | 541.0678 | NaN | 512.7449
5390.176 | 541.2864 | NaN | 513.1688
5391.176 | 541.1705 | NaN | 512.6819
5392.176 | 541.1584 | NaN | 511.6258
5393.176 | 540.9374 | NaN | 510.9848
5394.176 | 540.3712 | NaN | 510.0685
5395.1917 | 540.3936 | NaN | 510.0064
5396.176 | 541.203 | NaN | 510.9814
5397.176 | 541.6793 | NaN | 511.1659
5398.176 | 542.3035 | NaN | 511.7106
5399.176 | 542.8263 | NaN | 513.9236
5400.176 | 543.2368 | NaN | 515.9372
5401.176 | 543.5702 | NaN | 517.6337
5402.176 | 544.1243 | NaN | 517.9261
5403.176 | 544.388 | NaN | 517.5076
5404.176 | 544.1589 | NaN | 516.6203
5405.176 | 543.6809 | NaN | 516.2295
5406.176 | 545.0184 | NaN | 516.3531
5407.176 | 547.512 | NaN | 517.3088
5408.176 | 548.4029 | NaN | 517.0464
5409.176 | 549.2654 | NaN | 517.7078
5410.176 | 549.808 | NaN | 517.9501
5411.176 | 551.5725 | NaN | 519.3082
5412.176 | 552.1532 | NaN | 518.955
5413.176 | 554.1963 | NaN | 519.8405
5414.176 | 556.5015 | NaN | 520.0886
5415.176 | 556.4123 | NaN | 519.4813
5416.176 | 555.6148 | NaN | 518.5649
5417.176 | 554.6067 | NaN | 518.5951
5418.176 | 553.6891 | NaN | 518.6904
5419.176 | 553.0034 | NaN | 518.4247
5420.176 | 551.4338 | NaN | 517.4615
5421.176 | 550.2358 | NaN | 516.4027
5422.176 | 549.2857 | NaN | 515.7034
5423.176 | 548.7503 | NaN | 515.3536
5424.176 | 548.2586 | NaN | 515.2853
5425.1917 | 547.6912 | NaN | 515.1427
5426.176 | 546.7827 | NaN | 514.2998
5427.176 | 546.5069 | NaN | 514.0774
5428.176 | 546.233 | NaN | 514.7042
5429.176 | 545.878 | NaN | 514.6262
5430.176 | 545.0263 | NaN | 514.542
5431.176 | 544.3366 | NaN | 514.3623
5432.176 | 543.6186 | NaN | 514.4399
5433.176 | 543.6704 | NaN | 514.2426
5434.176 | 543.3896 | NaN | 513.7351
5435.176 | 542.6124 | NaN | 512.7628
5436.176 | 541.9374 | NaN | 511.9637
5437.176 | 541.9001 | NaN | 511.7172
5438.176 | 541.5391 | NaN | 512.9172
5439.176 | 541.3513 | NaN | 513.1866
5440.176 | 541.4006 | NaN | 513.6057
5441.176 | 540.433 | NaN | 513.3405
5442.176 | 539.7959 | NaN | 512.8799
5443.176 | 539.3015 | NaN | 512.4322
5444.176 | 539.0503 | NaN | 512.8902
5445.176 | 538.558 | NaN | 512.9984
5446.176 | 538.1483 | NaN | 513.2677
5447.176 | 538.3571 | NaN | 512.726
5448.176 | 537.7366 | NaN | 512.8476
5449.176 | 537.1925 | NaN | 512.7904
5450.176 | 537.02 | NaN | 513.1405
5451.176 | 536.7437 | NaN | 513.3347
5452.176 | 536.2398 | NaN | 513.2866
5453.176 | 535.8203 | NaN | 513.099
5454.176 | 535.6066 | NaN | 513.4119
5455.176 | 535.8046 | NaN | 513.7445
5456.176 | 535.9997 | NaN | 513.5945
5457.176 | 536.1502 | NaN | 513.0624
5458.176 | 535.9395 | NaN | 512.8903
5459.176 | 536.1683 | NaN | 512.9464
5460.176 | 535.8214 | NaN | 512.7659
5461.176 | 536.0119 | NaN | 512.6404
5462.176 | 535.9386 | NaN | 512.2816
5463.176 | 535.4847 | NaN | 511.6753
5464.176 | 534.5245 | NaN | 510.9356
5465.176 | 534.1131 | NaN | 510.546
5466.176 | 534.259 | NaN | 510.5364
5467.176 | 534.6784 | NaN | 511.0403
5468.176 | 534.4303 | NaN | 510.7742
5469.176 | 534.1918 | NaN | 510.1823
5470.176 | 534.366 | NaN | 510.7828
5471.176 | 534.6425 | NaN | 511.8251
5472.176 | 534.2436 | NaN | 512.3788
5473.176 | 534.1157 | NaN | 512.85
5474.176 | 534.0878 | NaN | 513.3175
5475.176 | 533.8722 | NaN | 513.8094
5476.176 | 534.0548 | NaN | 513.5727
5477.176 | 534.1445 | NaN | 512.9257
5478.176 | 534.3207 | NaN | 512.1774
5479.176 | 535.0691 | NaN | 512.2148
5480.176 | 535.8013 | NaN | 512.2275
5481.176 | 535.7232 | NaN | 512.3685
5482.176 | 535.546 | NaN | 512.2062
5483.176 | 535.269 | NaN | 511.0225
5484.176 | 534.9597 | NaN | 510.0116
5485.176 | 534.5309 | NaN | 509.2105
5486.176 | 534.729 | NaN | 508.8498
5487.176 | 534.7613 | NaN | 509.1039
5488.176 | 534.86 | NaN | 508.8354
5489.176 | 535.0813 | NaN | 508.6116
5490.176 | 535.3341 | NaN | 508.7319
5491.176 | 535.3422 | NaN | 509.8992
5492.176 | 535.5794 | NaN | 509.9884
5493.176 | 535.4717 | NaN | 509.8945
5494.176 | 535.6341 | NaN | 509.858
5495.176 | 535.2279 | NaN | 509.286
5496.176 | 535.0401 | NaN | 508.5323
5497.176 | 534.4992 | NaN | 507.8731
5498.176 | 534.3553 | NaN | 507.9648
5499.176 | 534.6934 | NaN | 507.8686
5500.176 | 534.6639 | NaN | 507.8466
5501.176 | 534.3285 | NaN | 507.2538
5502.176 | 534.1962 | NaN | 507.1551
5503.176 | 534.0433 | NaN | 506.8975
5504.176 | 534.2126 | NaN | 506.4051
5505.176 | 534.3066 | NaN | 506.603
5506.176 | 534.5752 | NaN | 506.8368
5507.176 | 534.7448 | NaN | 506.7049
5508.176 | 534.5614 | NaN | 506.7312
5509.176 | 534.026 | NaN | 505.9813
5510.176 | 534.5286 | NaN | 505.1342
5511.176 | 534.599 | NaN | 505.4685
5512.176 | 534.5298 | NaN | 506.9812
5513.176 | 534.4677 | NaN | 507.6899
5514.176 | 534.5712 | NaN | 508.0377
5515.176 | 534.9618 | NaN | 509.2948
5516.176 | 535.7446 | NaN | 509.9921
5517.176 | 535.6492 | NaN | 509.8537
5518.176 | 535.1394 | NaN | 509.1864
5519.176 | 534.5914 | NaN | 509.2763
5520.176 | 534.83 | NaN | 508.9835
5521.176 | 534.2172 | NaN | 509.1076
5522.176 | 533.4504 | NaN | 508.5696
5523.176 | 532.6292 | NaN | 507.8197
5524.176 | 531.8568 | NaN | 506.9882
5525.176 | 531.9402 | NaN | 505.9451
5526.176 | 531.1499 | NaN | 506.0744
5527.176 | 530.7373 | NaN | 505.443
5528.176 | 530.1257 | NaN | 504.891
5529.176 | 530.0616 | NaN | 504.5854
5530.176 | 529.7865 | NaN | 505.0448
5531.176 | 529.6314 | NaN | 505.4709
5532.176 | 529.151 | NaN | 505.3647
5533.176 | 528.7599 | NaN | 504.7574
5534.176 | 528.4181 | NaN | 504.2207
5535.176 | 528.2326 | NaN | 503.6531
5536.176 | 528.5102 | NaN | 502.9374
5537.176 | 528.9452 | NaN | 502.3163
5538.176 | 528.9099 | NaN | 501.885
5539.176 | 528.7986 | NaN | 501.6472
5540.176 | 528.5893 | NaN | 501.9743
5541.176 | 528.594 | NaN | 501.7265
5542.176 | 528.5612 | NaN | 502.426
5543.176 | 527.9987 | NaN | 502.0654
5544.176 | 527.8905 | NaN | 501.468
5545.176 | 528.5922 | NaN | 501.2932
5546.176 | 528.5089 | NaN | 500.8808
5547.176 | 528.1785 | NaN | 500.2088
5548.176 | 527.7641 | NaN | 499.6719
5549.176 | 527.1481 | NaN | 499.3236
5550.176 | 526.6165 | NaN | 498.8053
5551.176 | 526.2765 | NaN | 498.4623
5552.176 | 526.5458 | NaN | 498.4185
5553.176 | 526.1707 | NaN | 498.3031
5554.176 | 525.7689 | NaN | 498.0232
5555.176 | 525.9038 | NaN | 497.9453
5556.176 | 525.5716 | NaN | 497.9728
5557.176 | 525.651 | NaN | 497.6045
5558.176 | 525.2455 | NaN | 497.2464
5559.176 | 524.9968 | NaN | 496.7703
5560.176 | 524.6919 | NaN | 496.7308
5561.176 | 524.6422 | NaN | 496.2619
5562.176 | 524.3732 | NaN | 495.8586
5563.176 | 524.065 | NaN | 495.5602
5564.176 | 524.2384 | NaN | 495.8664
5565.176 | 524.9402 | NaN | 496.7612
5566.176 | 525.2681 | NaN | 497.4396
5567.176 | 525.6355 | NaN | 497.9541
5568.176 | 525.4773 | NaN | 497.9017
5569.176 | 525.1421 | NaN | 497.4428
5570.176 | 525.1232 | NaN | 497.1835
5571.176 | 525.9259 | NaN | 497.7452
5572.176 | 526.3657 | NaN | 499.9267
5573.176 | 526.3872 | NaN | 499.9745
5574.176 | 526.5775 | NaN | 499.3424
5575.176 | 526.5969 | NaN | 498.9288
5576.176 | 526.1986 | NaN | 498.3905
5577.176 | 526.1249 | NaN | 497.9292
5578.176 | 525.9574 | NaN | 497.3254
5579.176 | 525.6939 | NaN | 496.6419
5580.176 | 525.7061 | NaN | 495.6954
5581.176 | 525.5562 | NaN | 494.9633
5582.176 | 525.469 | NaN | 495.0207
5583.176 | 525.6793 | NaN | 496.5276
5584.176 | 525.7693 | NaN | 496.9214
5585.176 | 525.7541 | NaN | 497.157
5586.176 | 526.1576 | NaN | 496.8755
5587.176 | 525.5692 | NaN | 496.516
5588.176 | 525.3497 | NaN | 495.4104
5589.176 | 525.0654 | NaN | 494.4976
5590.176 | 524.7587 | NaN | 493.7335
5591.176 | 524.3817 | NaN | 493.763
5592.176 | 524.0909 | NaN | 493.5015
5593.176 | 523.6968 | NaN | 494.0935
5594.176 | 523.8603 | NaN | 494.343
5595.176 | 523.8231 | NaN | 494.2316
5596.176 | 523.0324 | NaN | 493.9826
5597.176 | 522.562 | NaN | 493.7107
5598.176 | 522.6159 | NaN | 493.6478
5599.176 | 522.753 | NaN | 493.7029
5600.176 | 523.3637 | NaN | 494.4627
5601.176 | 523.8569 | NaN | 495.2756
5602.176 | 524.2762 | NaN | 496.6478
5603.176 | 524.8163 | NaN | 498.1412
5604.176 | 525.1033 | NaN | 498.3367
5605.176 | 525.0274 | NaN | 498.0693
5606.176 | 525.2359 | NaN | 497.4998
5607.176 | 526.1137 | NaN | 497.9184
5608.176 | 526.2571 | NaN | 498.3573
5609.176 | 526.1547 | NaN | 499.2296
5610.176 | 525.816 | NaN | 498.4674
5611.176 | 525.0937 | NaN | 497.5297
5612.176 | 524.6622 | NaN | 496.7333
5613.176 | 524.2178 | NaN | 496.1635
5614.176 | 523.6312 | NaN | 496.1838
5615.176 | 522.9848 | NaN | 495.7288
5616.176 | 522.6512 | NaN | 494.943
5617.176 | 522.4364 | NaN | 494.0698
5618.176 | 522.0181 | NaN | 493.3244
5619.176 | 521.3092 | NaN | 492.9094
5620.176 | 520.7135 | NaN | 492.3963
5621.176 | 520.274 | NaN | 492.5996
5622.176 | 519.8483 | NaN | 492.2862
5623.176 | 519.3331 | NaN | 492.5412
5624.176 | 518.7683 | NaN | 492.4698
5625.176 | 518.4384 | NaN | 492.2747
5626.176 | 518.314 | NaN | 492.0959
5627.2073 | 518.2327 | NaN | 492.1228
5628.176 | 518.5667 | NaN | 492.3044
5629.176 | 518.535 | NaN | 491.9367
5630.176 | 519.0716 | NaN | 491.3259
5631.176 | 519.0773 | NaN | 492.2762
5632.176 | 518.8832 | NaN | 492.5418
5633.176 | 518.8614 | NaN | 492.1768
5634.176 | 518.9169 | NaN | 491.6972
5635.176 | 518.584 | NaN | 491.569
5636.176 | 518.15 | NaN | 491.3161
5637.176 | 517.9711 | NaN | 490.6872
5638.176 | 517.5902 | NaN | 490.0073
5639.176 | 517.4028 | NaN | 489.7012
5640.176 | 517.5013 | NaN | 489.4819
5641.176 | 517.0966 | NaN | 489.6066
5642.176 | 516.7064 | NaN | 489.4861
5643.176 | 516.3604 | NaN | 489.8191
5644.176 | 516.21 | NaN | 490.0243
5645.176 | 516.4111 | NaN | 489.7422
5646.176 | 516.5628 | NaN | 489.5553
5647.176 | 516.573 | NaN | 489.1717
5648.176 | 516.3107 | NaN | 489.1757
5649.176 | 515.9662 | NaN | 489.2305
5650.176 | 515.2841 | NaN | 488.7929
5651.176 | 515.1608 | NaN | 488.6048
5652.176 | 515.096 | NaN | 487.9789
5653.176 | 514.9355 | NaN | 487.7058
5654.176 | 514.7916 | NaN | 487.3796
5655.176 | 514.6861 | NaN | 487.4794
5656.176 | 514.5747 | NaN | 488.5102
5657.176 | 514.7202 | NaN | 488.7239
5658.176 | 514.7689 | NaN | 488.638
5659.176 | 514.3979 | NaN | 488.975
5660.176 | 514.123 | NaN | 488.9559
5661.176 | 514.032 | NaN | 489.2711
5662.176 | 513.8414 | NaN | 489.5321
5663.176 | 513.9845 | NaN | 489.9832
5664.176 | 513.9616 | NaN | 490.2855
5665.176 | 513.848 | NaN | 489.9265
5666.176 | 513.5929 | NaN | 489.0038
5667.176 | 513.3136 | NaN | 489.0369
5668.176 | 513.3295 | NaN | 489.0597
5669.176 | 513.1121 | NaN | 489.2727
5670.176 | 513.0213 | NaN | 488.9298
5671.176 | 512.9058 | NaN | 488.6502
5672.176 | 512.9329 | NaN | 488.4854
5673.176 | 513.024 | NaN | 488.4238
5674.176 | 513.1737 | NaN | 488.3086
5675.176 | 512.9554 | NaN | 488.2211
5676.176 | 512.7672 | NaN | 488.342
5677.176 | 512.5296 | NaN | 487.9951
5678.176 | 512.2094 | NaN | 487.6095
5679.176 | 511.9007 | NaN | 487.9812
5680.176 | 511.5775 | NaN | 487.5769
5681.176 | 511.2616 | NaN | 487.5429
5682.176 | 511.067 | NaN | 487.5967
5683.176 | 510.7714 | NaN | 488.4425
5684.176 | 511.0825 | NaN | 489.1749
5685.176 | 511.2401 | NaN | 489.3286
5686.176 | 511.255 | NaN | 489.4483
5687.176 | 511.185 | NaN | 490.0015
5688.176 | 511.1873 | NaN | 489.9596
5689.176 | 511.0064 | NaN | 489.798
5690.176 | 510.8342 | NaN | 489.4165
5691.176 | 510.479 | NaN | 488.9708
5692.176 | 510.3042 | NaN | 489.0469
5693.176 | 509.897 | NaN | 489.4012
5694.176 | 509.5953 | NaN | 488.9331
5695.176 | 509.2928 | NaN | 488.7504
5696.176 | 509.0955 | NaN | 488.2757
5697.176 | 508.8911 | NaN | 488.6695
5698.176 | 508.6049 | NaN | 488.8037
5699.176 | 508.4069 | NaN | 488.8436
5700.176 | 508.1837 | NaN | 488.2805
5701.176 | 507.9858 | NaN | 487.75
5702.176 | 507.9122 | NaN | 488.0675
5703.176 | 508.3501 | NaN | 488.0922
5704.176 | 508.4524 | NaN | 488.0754
5705.176 | 508.1074 | NaN | 488.0934
5706.176 | 507.6281 | NaN | 487.6708
5707.176 | 507.163 | NaN | 487.3088
5708.176 | 506.8525 | NaN | 486.4605
5709.176 | 506.6969 | NaN | 487.0984
5710.176 | 506.6939 | NaN | 486.7634
5711.176 | 506.5162 | NaN | 487.0996
5712.176 | 506.3765 | NaN | 487.6651
5713.176 | 506.0528 | NaN | 487.6451
5714.176 | 505.7192 | NaN | 487.1548
5715.176 | 505.4669 | NaN | 487.1454
5716.176 | 505.0124 | NaN | 486.4447
5717.176 | 505.0141 | NaN | 486.2161
5718.176 | 504.8202 | NaN | 486.3259
5719.176 | 504.6993 | NaN | 486.6412
5720.176 | 504.5312 | NaN | 486.4388
5721.176 | 504.7128 | NaN | 486.3288
5722.176 | 504.7169 | NaN | 485.7569
5723.176 | 504.5889 | NaN | 485.0454
5724.176 | 504.4503 | NaN | 484.2435
5725.176 | 504.6898 | NaN | 483.6751
5726.176 | 505.2948 | NaN | 483.123
5727.176 | 505.7398 | NaN | 482.3898
5728.176 | 506.4186 | NaN | 480.5812
5729.176 | 505.9447 | NaN | 481.0551
5730.176 | 505.9765 | NaN | 480.8163
5731.176 | 505.677 | NaN | 480.696
5732.176 | 505.5691 | NaN | 480.292
5733.176 | 505.8811 | NaN | 480.6711
5734.176 | 506.1895 | NaN | 480.696
5735.176 | 506.1981 | NaN | 480.6815
5736.176 | 505.9001 | NaN | 480.2794
5737.176 | 506.0706 | NaN | 480.582
5738.176 | 505.7773 | NaN | 480.569
5739.176 | 505.6381 | NaN | 480.4245
5740.176 | 505.6388 | NaN | 480.1941
5741.176 | 505.3069 | NaN | 479.9754
5742.176 | 505.1017 | NaN | 479.9031
5743.176 | 505.2569 | NaN | 480.1044
5744.176 | 505.2076 | NaN | 480.9038
5745.176 | 505.0027 | NaN | 481.6609
5746.176 | 504.64 | NaN | 482.1619
5747.176 | 504.6146 | NaN | 482.2595
5748.176 | 504.6968 | NaN | 481.6259
5749.176 | 504.6757 | NaN | 481.4332
5750.176 | 504.4087 | NaN | 481.5464
5751.176 | 503.6995 | NaN | 482.3864
5752.176 | 503.4154 | NaN | 482.7794
5753.176 | 503.0867 | NaN | 483.0938
5754.176 | 502.6002 | NaN | 483.5826
5755.176 | 502.2587 | NaN | 483.3978
5756.176 | 502.1385 | NaN | 483.2457
5757.176 | 501.8204 | NaN | 483.2252
5758.176 | 501.4532 | NaN | 483.4266
5759.176 | 501.3705 | NaN | 484.0262
5760.176 | 501.3371 | NaN | 484.2602
5761.176 | 500.9859 | NaN | 483.8221
5762.176 | 500.7637 | NaN | 483.3168
5763.176 | 500.2552 | NaN | 483.7026
5764.176 | 500.0281 | NaN | 483.3228
5765.176 | 499.8908 | NaN | 482.8207
5766.176 | 499.7435 | NaN | 482.1925
5767.176 | 499.8534 | NaN | 481.9675
5768.176 | 500.058 | NaN | 482.3304
5769.176 | 500.6162 | NaN | 482.0701
5770.176 | 501.2852 | NaN | 482.6086
5771.176 | 501.5498 | NaN | 482.1672
5772.176 | 501.63 | NaN | 481.8204
5773.176 | 501.2187 | NaN | 481.4092
5774.176 | 500.7988 | NaN | 480.7945
5775.176 | 500.4664 | NaN | 480.1235
5776.176 | 500.2201 | NaN | 479.609
5777.176 | 500.0599 | NaN | 479.4791
5778.176 | 500.0938 | NaN | 479.4432
5779.176 | 500.1773 | NaN | 479.6502
5780.176 | 500.0776 | NaN | 480.2026
5781.176 | 500.0775 | NaN | 480.7762
5782.176 | 499.9079 | NaN | 481.7727
5783.176 | 499.8981 | NaN | 481.8986
5784.176 | 500.0068 | NaN | 482.3566
5785.176 | 500.1582 | NaN | 482.2793
5786.176 | 500.1824 | NaN | 482.1765
5787.176 | 500.1368 | NaN | 481.7059
5788.176 | 500.2084 | NaN | 481.1271
5789.176 | 500.3086 | NaN | 480.6163
5790.176 | 500.5397 | NaN | 480.3108
5791.176 | 500.5463 | NaN | 480.1409
5792.176 | 500.4131 | NaN | 479.9441
5793.176 | 500.2349 | NaN | 479.4701
5794.176 | 500.1378 | NaN | 479.6322
5795.176 | 499.8995 | NaN | 479.2897
5796.176 | 499.4623 | NaN | 478.7744
5797.176 | 499.1278 | NaN | 477.7238
5798.176 | 498.7932 | NaN | 477.3936
5799.176 | 498.4175 | NaN | 477.1235
5800.176 | 498.3752 | NaN | 477.1313
5801.176 | 498.4025 | NaN | 477.607
5802.176 | 498.1015 | NaN | 477.8536
5803.176 | 497.8863 | NaN | 477.7217
5804.176 | 497.6716 | NaN | 477.2728
5805.176 | 497.4362 | NaN | 476.5189
5806.176 | 497.1077 | NaN | 475.8187
5807.176 | 497.0007 | NaN | 475.3147
5808.176 | 497.004 | NaN | 475.946
5809.176 | 496.9472 | NaN | 476.6116
5810.176 | 497.1422 | NaN | 476.0129
5811.176 | 497.1334 | NaN | 476.2537
5812.176 | 496.9666 | NaN | 476.2973
5813.176 | 496.9812 | NaN | 476.1393
5814.176 | 496.9316 | NaN | 475.6727
5815.176 | 497.5099 | NaN | 475.4255
5816.176 | 497.8167 | NaN | 475.7486
5817.176 | 497.9174 | NaN | 475.8152
5818.176 | 498.0305 | NaN | 475.54
5819.176 | 498.1753 | NaN | 475.2087
5820.176 | 497.9375 | NaN | 474.649
5821.176 | 498.0854 | NaN | 474.7886
5822.176 | 498.2266 | NaN | 475.4842
5823.176 | 498.6737 | NaN | 475.8752
5824.176 | 499.2898 | NaN | 476.4028
5825.176 | 499.7283 | NaN | 476.232
5826.176 | 500.5208 | NaN | 476.1338
5827.176 | 501.0474 | NaN | 476.7532
5828.176 | 501.075 | NaN | 476.9236
5829.176 | 501.0348 | NaN | 476.9475
5830.176 | 501.5482 | NaN | 477.7665
5831.176 | 502.0971 | NaN | 477.9692
5832.176 | 502.4233 | NaN | 477.4675
5833.176 | 502.6872 | NaN | 477.1419
5834.176 | 502.7276 | NaN | 476.6579
5835.176 | 502.6425 | NaN | 476.4803
5836.176 | 502.8616 | NaN | 476.9038
5837.176 | 502.8153 | NaN | 478.0748
5838.176 | 502.5594 | NaN | 477.2699
5839.176 | 502.1213 | NaN | 476.8613
5840.176 | 501.6086 | NaN | 476.0017
5841.176 | 501.6014 | NaN | 475.4807
5842.176 | 501.5385 | NaN | 475.9996
5843.176 | 501.4017 | NaN | 476.6624
5844.176 | 500.646 | NaN | 476.0759
5845.176 | 500.0304 | NaN | 475.23
5846.176 | 499.6492 | NaN | 474.7499
5847.176 | 499.1406 | NaN | 474.2656
5848.176 | 499.0196 | NaN | 473.9384
5849.176 | 498.6699 | NaN | 473.7217
5850.176 | 498.5314 | NaN | 473.6335
5851.176 | 498.0419 | NaN | 473.3777
5852.176 | 497.4978 | NaN | 473.4742
5853.176 | 497.2282 | NaN | 473.1693
5854.176 | 497.0379 | NaN | 473.5635
5855.176 | 496.7962 | NaN | 473.3826
5856.176 | 496.5936 | NaN | 472.7161
5857.176 | 496.4942 | NaN | 471.8729
5858.176 | 496.3839 | NaN | 471.7288
5859.176 | 496.1408 | NaN | 472.7036
5860.176 | 495.8219 | NaN | 473.0287
5861.176 | 495.6046 | NaN | 473.8125
5862.176 | 495.6323 | NaN | 473.8154
5863.176 | 495.7991 | NaN | 473.5554
5864.176 | 495.6148 | NaN | 473.6506
5865.176 | 495.3675 | NaN | 473.4316
5866.176 | 495.1119 | NaN | 473.9729
5867.176 | 495.1611 | NaN | 474.1885
5868.176 | 495.0011 | NaN | 474.0939
5869.176 | 494.9434 | NaN | 473.8987
5870.176 | 494.6674 | NaN | 473.3343
5871.176 | 494.5304 | NaN | 472.87
5872.176 | 494.4623 | NaN | 472.5113
5873.176 | 494.3561 | NaN | 471.9547
5874.176 | 493.9333 | NaN | 471.4878
5875.176 | 493.8124 | NaN | 471.6011
5876.176 | 493.612 | NaN | 471.23
5877.176 | 492.876 | NaN | 471.2481
5878.176 | 492.5573 | NaN | 470.9395
5879.176 | 492.3092 | NaN | 470.6448
5880.176 | 492.2443 | NaN | 470.2629
5881.176 | 492.3596 | NaN | 470.7485
5882.176 | 492.1545 | NaN | 470.6673
5883.176 | 492.0202 | NaN | 470.4327
5884.176 | 492.2103 | NaN | 470.531
5885.176 | 492.1583 | NaN | 470.503
5886.176 | 491.9183 | NaN | 470.3733
5887.176 | 491.317 | NaN | 470.4125
5888.176 | 491.2422 | NaN | 470.1575
5889.176 | 490.9941 | NaN | 469.6103
5890.176 | 490.6501 | NaN | 469.1357
5891.176 | 490.3513 | NaN | 469.8095
5892.176 | 490.3623 | NaN | 469.9415
5893.176 | 490.4007 | NaN | 470.1676
5894.176 | 490.4903 | NaN | 469.8234
5895.176 | 490.469 | NaN | 470.001
5896.176 | 490.3665 | NaN | 470.0613
5897.176 | 490.3952 | NaN | 469.5356
5898.176 | 490.4458 | NaN | 469.3714
5899.176 | 490.2446 | NaN | 469.1977
5900.176 | 490.0211 | NaN | 468.8568
5901.176 | 489.9582 | NaN | 469.0861
5902.176 | 489.7529 | NaN | 469.0818
5903.176 | 489.6976 | NaN | 468.4237
5904.176 | 490.1237 | NaN | 468.1219
5905.176 | 489.9013 | NaN | 468.1548
5906.176 | 489.8539 | NaN | 468.0595
5907.176 | 489.8654 | NaN | 467.7332
5908.176 | 489.8322 | NaN | 467.4079
5909.176 | 489.5281 | NaN | 467.0979
5910.176 | 489.6615 | NaN | 466.8887
5911.176 | 489.8532 | NaN | 466.7858
5912.176 | 489.9856 | NaN | 466.2955
5913.176 | 490.0156 | NaN | 466.0075
5914.176 | 489.8462 | NaN | 466.0802
5915.176 | 489.5873 | NaN | 466.5177
5916.176 | 489.6435 | NaN | 466.5668
5917.176 | 489.5487 | NaN | 466.1876
5918.176 | 489.7518 | NaN | 466.0952
5919.176 | 489.813 | NaN | 466.1835
5920.176 | 489.9698 | NaN | 465.9112
5921.176 | 490.0699 | NaN | 465.6142
5922.176 | 489.7907 | NaN | 465.2048
5923.176 | 489.3342 | NaN | 464.3682
5924.176 | 489.197 | NaN | 464.152
5925.176 | 488.7475 | NaN | 464.5967
5926.176 | 488.3587 | NaN | 464.889
5927.176 | 488.182 | NaN | 464.8282
5928.176 | 488.0965 | NaN | 464.935
5929.176 | 488.3513 | NaN | 464.9933
5930.176 | 488.6014 | NaN | 465.9618
5931.176 | 488.4967 | NaN | 465.8345
5932.176 | 488.3053 | NaN | 465.2995
5933.176 | 488.0046 | NaN | 464.9565
5934.176 | 487.6161 | NaN | 464.4423
5935.176 | 487.4497 | NaN | 464.292
5936.176 | 487.2381 | NaN | 464.495
5937.176 | 486.9839 | NaN | 464.6879
5938.176 | 487.022 | NaN | 464.8318
5939.176 | 487.0713 | NaN | 465.0529
5940.176 | 487.0241 | NaN | 465.5073
5941.176 | 486.9307 | NaN | 465.761
5942.176 | 486.8555 | NaN | 465.9659
5943.176 | 486.4004 | NaN | 465.8823
5944.176 | 486.0371 | NaN | 465.8005
5945.176 | 485.7434 | NaN | 465.7193
5946.176 | 485.3371 | NaN | 465.7569
5947.176 | 485.0544 | NaN | 465.8595
5948.176 | 485.0048 | NaN | 465.9107
5949.176 | 484.9079 | NaN | 465.8189
5950.176 | 484.7466 | NaN | 465.7854
5951.176 | 484.5757 | NaN | 465.8965
5952.176 | 484.7372 | NaN | 465.8413
5953.176 | 484.8788 | NaN | 465.8535
5954.176 | 484.7362 | NaN | 465.8821
5955.176 | 484.6372 | NaN | 465.6757
5956.176 | 484.2426 | NaN | 465.492
5957.176 | 484.0032 | NaN | 465.2834
5958.176 | 484.3823 | NaN | 464.8939
5959.176 | 484.317 | NaN | 465.0127
5960.176 | 484.5118 | NaN | 464.8668
5961.176 | 484.767 | NaN | 464.6659
5962.176 | 485.0256 | NaN | 464.5984
5963.176 | 485.0691 | NaN | 464.492
5964.176 | 485.2282 | NaN | 464.4146
5965.176 | 485.1769 | NaN | 464.5323
5966.176 | 485.2746 | NaN | 464.8209
5967.176 | 485.1202 | NaN | 464.5572
5968.176 | 484.8827 | NaN | 464.1501
5969.176 | 484.5567 | NaN | 463.7897
5970.176 | 484.3496 | NaN | 463.4351
5971.176 | 484.0649 | NaN | 463.268
5972.176 | 483.7697 | NaN | 463.3014
5973.176 | 483.6406 | NaN | 462.977
5974.176 | 483.4733 | NaN | 463.1043
5975.176 | 483.2705 | NaN | 462.9119
5976.176 | 483.1988 | NaN | 462.7651
5977.176 | 482.9294 | NaN | 462.7009
5978.176 | 482.9911 | NaN | 462.6978
5979.176 | 483.0506 | NaN | 462.6884
5980.176 | 482.9025 | NaN | 462.3674
5981.176 | 482.9221 | NaN | 462.1887
5982.176 | 482.8141 | NaN | 461.8889
5983.176 | 482.8447 | NaN | 462.0579
5984.176 | 482.5998 | NaN | 461.8934
5985.176 | 482.4625 | NaN | 462.0034
5986.176 | 482.3372 | NaN | 462.2735
5987.176 | 482.2134 | NaN | 462.0998
5988.176 | 482.072 | NaN | 462.1139
5989.176 | 482.0484 | NaN | 462.0716
5990.176 | 482.2479 | NaN | 461.5817
5991.176 | 482.1423 | NaN | 461.1673
5992.176 | 481.8857 | NaN | 460.8699
5993.176 | 481.4217 | NaN | 460.7473
5994.176 | 481.2455 | NaN | 461.0296
5995.176 | 481.3413 | NaN | 461.8068
5996.176 | 481.3574 | NaN | 461.9591
5997.176 | 481.1704 | NaN | 462.5194
5998.176 | 481.3063 | NaN | 462.5561
5999.176 | 481.4226 | NaN | 462.6124
6000.1917 | 481.4741 | NaN | 462.5523
6001.176 | 481.3561 | NaN | 462.8227
6002.176 | 481.2055 | NaN | 462.6973
6003.176 | 481.0936 | NaN | 462.4102
6004.176 | 480.9524 | NaN | 462.3551
6005.176 | 480.8893 | NaN | 461.9905
6006.176 | 480.533 | NaN | 461.8661
6007.176 | 480.1927 | NaN | 461.8967
6008.176 | 479.8502 | NaN | 461.9031
6009.176 | 479.542 | NaN | 461.4881
6010.176 | 479.287 | NaN | 461.7156
6011.176 | 479.0585 | NaN | 461.8949
6012.176 | 478.761 | NaN | 461.6579
6013.176 | 478.4049 | NaN | 461.1674
6014.176 | 478.436 | NaN | 460.2894
6015.176 | 478.2541 | NaN | 459.8109
6016.176 | 478.0841 | NaN | 459.5746
6017.176 | 477.9208 | NaN | 459.8894
6018.176 | 477.7909 | NaN | 460.675
6019.176 | 477.8578 | NaN | 460.8188
6020.176 | 477.7818 | NaN | 460.7297
6021.176 | 477.8415 | NaN | 460.936
6022.176 | 477.729 | NaN | 460.9896
6023.176 | 477.5391 | NaN | 461.9809
6024.176 | 477.4783 | NaN | 462.2592
6025.176 | 477.268 | NaN | 462.3528
6026.176 | 477.0914 | NaN | 462.4881
6027.176 | 476.9343 | NaN | 462.6685
6028.176 | 476.6719 | NaN | 462.0264
6029.176 | 476.2359 | NaN | 461.4565
6030.176 | 476.0591 | NaN | 460.8837
6031.176 | 475.8558 | NaN | 460.5537
6032.176 | 475.4077 | NaN | 460.3616
6033.176 | 475.2874 | NaN | 459.8343
6034.176 | 475.1703 | NaN | 459.5394
6035.176 | 475.0377 | NaN | 459.7984
6036.176 | 474.8069 | NaN | 459.4082
6037.176 | 474.6593 | NaN | 459.2428
6038.176 | 474.6359 | NaN | 459.5157
6039.176 | 474.5006 | NaN | 459.665
6040.176 | 474.3139 | NaN | 459.4333
6041.176 | 474.2164 | NaN | 458.802
6042.176 | 474.2232 | NaN | 458.8137
6043.176 | 473.986 | NaN | 458.8189
6044.176 | 474.0451 | NaN | 458.243
6045.176 | 474.2584 | NaN | 458.3894
6046.176 | 474.3208 | NaN | 459.5518
6047.176 | 474.3761 | NaN | 459.0228
6048.176 | 474.6505 | NaN | 459.1523
6049.176 | 474.9332 | NaN | 459.2582
6050.176 | 474.8936 | NaN | 458.7133
6051.176 | 475.102 | NaN | 458.2227
6052.176 | 475.2193 | NaN | 457.691
6053.176 | 475.137 | NaN | 457.2363
6054.176 | 475.0815 | NaN | 457.3471
6055.176 | 475.0778 | NaN | 457.646
6056.176 | 475.082 | NaN | 457.9425
6057.176 | 475.4838 | NaN | 458.0032
6058.176 | 475.5767 | NaN | 457.8077
6059.176 | 475.3921 | NaN | 457.8616
6060.176 | 475.1906 | NaN | 458.4177
6061.176 | 475.2713 | NaN | 459.012
6062.176 | 475.2582 | NaN | 458.9614
6063.176 | 475.0604 | NaN | 458.7083
6064.176 | 474.9329 | NaN | 458.2293
6065.176 | 474.9355 | NaN | 458.2346
6066.176 | 474.742 | NaN | 457.9169
6067.176 | 474.8316 | NaN | 457.7872
6068.176 | 474.7778 | NaN | 458.0822
6069.176 | 474.9421 | NaN | 457.7347
6070.176 | 474.9378 | NaN | 457.334
6071.176 | 475.2572 | NaN | 456.6413
6072.176 | 474.8123 | NaN | 456.2863
6073.176 | 474.7775 | NaN | 455.877
6074.176 | 474.6256 | NaN | 455.4648
6075.176 | 474.6348 | NaN | 455.314
6076.176 | 474.7523 | NaN | 455.128
6077.176 | 475.0419 | NaN | 454.8966
6078.176 | 475.225 | NaN | 454.8688
6079.176 | 475.6109 | NaN | 454.8207
6080.176 | 475.9111 | NaN | 454.4733
6081.176 | 475.9336 | NaN | 454.9976
6082.176 | 475.8944 | NaN | 454.7978
6083.176 | 475.6965 | NaN | 454.7728
6084.176 | 475.7375 | NaN | 455.1262
6085.176 | 475.7115 | NaN | 454.8637
6086.176 | 475.8553 | NaN | 454.3201
6087.176 | 475.8996 | NaN | 453.6842
6088.176 | 476.0135 | NaN | 453.8558
6089.176 | 475.9044 | NaN | 453.7096
6090.176 | 476.0599 | NaN | 453.3636
6091.176 | 476.3219 | NaN | 453.0514
6092.176 | 476.2804 | NaN | 454.6874
6093.176 | 475.9547 | NaN | 454.3647
6094.176 | 475.7666 | NaN | 454.4006
6095.176 | 475.5856 | NaN | 454.6122
6096.176 | 475.4215 | NaN | 454.5093
6097.176 | 475.2597 | NaN | 454.0495
6098.176 | 475.132 | NaN | 453.8028
6099.176 | 475.0785 | NaN | 454.2328
6100.176 | 475.0819 | NaN | 454.2724
6101.176 | 475.0832 | NaN | 453.9441
6102.176 | 475.1141 | NaN | 453.5175
6103.176 | 475.1376 | NaN | 453.2592
6104.176 | 474.9605 | NaN | 452.9076
6105.176 | 474.99 | NaN | 452.4923
6106.176 | 474.6665 | NaN | 452.0937
6107.176 | 474.5793 | NaN | 451.7034
6108.176 | 474.4678 | NaN | 451.3361
6109.176 | 474.0382 | NaN | 450.7078
6110.176 | 474.0708 | NaN | 450.5327
6111.176 | 474.0121 | NaN | 450.8262
6112.176 | 473.9455 | NaN | 451.1357
6113.176 | 473.845 | NaN | 450.7466
6114.176 | 473.7424 | NaN | 451.0144
6115.176 | 473.6716 | NaN | 451.3208
6116.176 | 473.7455 | NaN | 451.1866
6117.176 | 473.7256 | NaN | 451.1515
6118.176 | 473.4767 | NaN | 450.8627
6119.176 | 473.2842 | NaN | 450.9658
6120.176 | 472.9733 | NaN | 451.005
6121.176 | 472.4398 | NaN | 451.0519
6122.176 | 472.2059 | NaN | 451.0175
6123.176 | 472.0757 | NaN | 451.1472
6124.176 | 472.3237 | NaN | 451.3888
6125.176 | 472.6657 | NaN | 451.3994
6126.176 | 472.8199 | NaN | 451.5509
6127.176 | 473.0885 | NaN | 452.3888
6128.176 | 473.1036 | NaN | 452.1594
6129.176 | 472.936 | NaN | 451.8356
6130.176 | 472.8698 | NaN | 452.4376
6131.176 | 472.9433 | NaN | 452.5727
6132.176 | 473.0614 | NaN | 452.4544
6133.176 | 473.0692 | NaN | 452.6117
6134.176 | 472.926 | NaN | 452.5345
6135.176 | 472.7173 | NaN | 451.7527
6136.176 | 472.7151 | NaN | 451.2478
6137.1917 | 472.9319 | NaN | 451.3437
6138.176 | 473.2937 | NaN | 451.8275
6139.176 | 473.4236 | NaN | 451.6309
6140.176 | 473.4075 | NaN | 451.7221
6141.176 | 473.4826 | NaN | 452.687
6142.176 | 473.4462 | NaN | 453.2098
6143.176 | 473.4823 | NaN | 453.243
6144.176 | 473.905 | NaN | 453.1154
6145.176 | 474.0004 | NaN | 452.9666
6146.176 | 474.0807 | NaN | 452.4522
6147.176 | 474.3331 | NaN | 451.8186
6148.176 | 474.5605 | NaN | 451.0876
6149.176 | 474.5864 | NaN | 450.3738
6150.176 | 474.496 | NaN | 451.0686
6151.176 | 474.428 | NaN | 450.9585
6152.176 | 474.2409 | NaN | 450.6005
6153.176 | 474.5374 | NaN | 450.074
6154.176 | 474.782 | NaN | 449.6215
6155.176 | 474.6337 | NaN | 449.3504
6156.176 | 474.6401 | NaN | 449.3024
6157.176 | 474.2942 | NaN | 450.6181
6158.176 | 474.0804 | NaN | 451.2256
6159.176 | 473.856 | NaN | 450.9912
6160.176 | 473.8517 | NaN | 451.3728
6161.176 | 473.7875 | NaN | 451.4601
6162.176 | 473.5116 | NaN | 452.5303
6163.176 | 473.3228 | NaN | 452.4382
6164.176 | 473.3736 | NaN | 453.317
6165.176 | 473.4675 | NaN | 453.0513
6166.176 | 473.6352 | NaN | 452.6715
6167.176 | 473.7959 | NaN | 452.7925
6168.176 | 473.7273 | NaN | 452.9531
6169.176 | 473.4394 | NaN | 452.8009
6170.176 | 473.3451 | NaN | 452.5577
6171.176 | 473.3058 | NaN | 452.2477
6172.176 | 473.2652 | NaN | 451.8437
6173.176 | 473.2929 | NaN | 451.9049
6174.176 | 473.2519 | NaN | 451.4842
6175.176 | 472.9959 | NaN | 450.9959
6176.176 | 472.9036 | NaN | 450.4608
6177.176 | 472.9886 | NaN | 449.9301
6178.176 | 473.0365 | NaN | 449.4929
6179.176 | 473.1587 | NaN | 449.3516
6180.176 | 472.8827 | NaN | 449.376
6181.176 | 472.728 | NaN | 449.5446
6182.176 | 472.6244 | NaN | 450.3975
6183.176 | 472.5802 | NaN | 449.9669
6184.176 | 472.4768 | NaN | 449.653
6185.176 | 472.42 | NaN | 449.4888
6186.176 | 472.3584 | NaN | 449.8929
6187.176 | 472.457 | NaN | 449.5707
6188.176 | 472.461 | NaN | 449.0269
6189.176 | 472.5271 | NaN | 448.6767
6190.176 | 472.1542 | NaN | 448.2537
6191.176 | 471.9602 | NaN | 448.1096
6192.176 | 471.7048 | NaN | 448.27
6193.176 | 471.5808 | NaN | 449.0524
6194.176 | 471.3622 | NaN | 448.9572
6195.176 | 471.4412 | NaN | 448.6857
6196.176 | 471.5802 | NaN | 448.3571
6197.176 | 471.6248 | NaN | 447.6898
6198.176 | 471.7566 | NaN | 447.1739
6199.176 | 471.7885 | NaN | 446.8689
6200.176 | 471.8245 | NaN | 446.406
6201.176 | 471.8536 | NaN | 446.0336
6202.176 | 472.1309 | NaN | 445.4751
6203.176 | 472.2212 | NaN | 445.0065
6204.176 | 472.2693 | NaN | 444.6632
6205.176 | 472.1996 | NaN | 444.3996
6206.176 | 472.5306 | NaN | 444.0601
6207.176 | 472.7022 | NaN | 444.0965
6208.176 | 473.2529 | NaN | 444.4558
6209.176 | 473.1888 | NaN | 444.942
6210.176 | 473.07 | NaN | 445.2816
6211.176 | 473.1053 | NaN | 445.8724
6212.176 | 473.1469 | NaN | 446.1653
6213.176 | 473.4336 | NaN | 445.9932
6214.176 | 473.5859 | NaN | 445.8435
6215.176 | 473.616 | NaN | 445.6307
6216.176 | 473.4946 | NaN | 445.4923
6217.176 | 473.2087 | NaN | 445.3111
6218.176 | 473.0724 | NaN | 445.4644
6219.176 | 473.0457 | NaN | 445.4844
6220.176 | 472.7604 | NaN | 445.1975
6221.176 | 472.5904 | NaN | 444.6324
6222.176 | 472.4474 | NaN | 445.1722
6223.176 | 472.1743 | NaN | 445.6874
6224.176 | 471.8227 | NaN | 445.4806
6225.176 | 471.5561 | NaN | 445.6017
6226.176 | 471.4911 | NaN | 445.7295
6227.2073 | 471.4887 | NaN | 445.5861
6228.176 | 471.1875 | NaN | 445.5965
6229.176 | 471.0173 | NaN | 445.0629
6230.176 | 470.9986 | NaN | 444.5544
6231.176 | 470.932 | NaN | 444.0778
6232.176 | 471.0069 | NaN | 444.155
6233.176 | 470.8305 | NaN | 443.9978
6234.176 | 470.5289 | NaN | 443.507
6235.176 | 470.3192 | NaN | 443.3884
6236.176 | 470.2261 | NaN | 443.8329
6237.176 | 469.937 | NaN | 444.4382
6238.176 | 469.8282 | NaN | 444.2148
6239.176 | 469.9845 | NaN | 443.9756
6240.176 | 469.9268 | NaN | 444.0572
6241.176 | 470.1026 | NaN | 443.9182
6242.176 | 470.4429 | NaN | 443.3527
6243.176 | 470.5336 | NaN | 442.9313
6244.176 | 470.6577 | NaN | 443.0468
6245.176 | 470.8069 | NaN | 442.611
6246.176 | 470.8254 | NaN | 442.2485
6247.176 | 470.6455 | NaN | 442.1924
6248.176 | 470.529 | NaN | 441.8267
6249.176 | 470.3656 | NaN | 441.9378
6250.176 | 470.286 | NaN | 441.5675
6251.176 | 470.2176 | NaN | 441.2442
6252.176 | 470.0639 | NaN | 441.4458
6253.176 | 469.7461 | NaN | 441.7154
6254.176 | 469.5851 | NaN | 441.7683
6255.176 | 469.545 | NaN | 441.8823
6256.176 | 469.3684 | NaN | 441.5792
6257.176 | 469.5264 | NaN | 441.0804
6258.176 | 469.494 | NaN | 440.9292
6259.176 | 469.0273 | NaN | 440.8311
6260.176 | 469.0235 | NaN | 441.2269
6261.176 | 468.7306 | NaN | 441.1622
6262.176 | 468.5807 | NaN | 440.887
6263.176 | 468.4764 | NaN | 440.542
6264.176 | 468.4266 | NaN | 440.0879
6265.176 | 468.5051 | NaN | 440.0481
6266.176 | 468.4407 | NaN | 441.1025
6267.176 | 468.4307 | NaN | 441.0379
6268.176 | 468.5634 | NaN | 441.2456
6269.176 | 468.6761 | NaN | 441.0899
6270.176 | 468.5466 | NaN | 441.1043
6271.176 | 468.2667 | NaN | 441.3651
6272.176 | 467.8874 | NaN | 440.9384
6273.176 | 467.3261 | NaN | 440.5214
6274.176 | 466.8069 | NaN | 440.0974
6275.176 | 466.7431 | NaN | 440.2656
6276.176 | 466.4109 | NaN | 440.0957
6277.176 | 466.0821 | NaN | 439.8822
6278.176 | 465.9842 | NaN | 440.0582
6279.176 | 465.9046 | NaN | 439.9556
6280.176 | 465.8422 | NaN | 440.3886
6281.176 | 465.4745 | NaN | 440.9313
6282.176 | 465.3424 | NaN | 441.6662
6283.176 | 465.3263 | NaN | 441.604
6284.176 | 465.2154 | NaN | 441.3612
6285.176 | 465.2293 | NaN | 441.3378
6286.176 | 465.4703 | NaN | 440.9419
6287.176 | 465.4976 | NaN | 440.5633
6288.176 | 465.6753 | NaN | 440.769
6289.176 | 465.5807 | NaN | 440.5804
6290.176 | 465.5982 | NaN | 440.6615
6291.176 | 465.476 | NaN | 441.1537
6292.176 | 465.2823 | NaN | 441.4003
6293.176 | 465.1365 | NaN | 441.3824
6294.176 | 465.148 | NaN | 441.3195
6295.176 | 465.2349 | NaN | 440.941
6296.1917 | 465.1816 | NaN | 440.3035
6297.176 | 465.2246 | NaN | 440.1785
6298.176 | 465.2347 | NaN | 439.9965
6299.176 | 465.188 | NaN | 439.8929
6300.176 | 465.2746 | NaN | 440.0311
6301.176 | 465.1952 | NaN | 439.5937
6302.176 | 466.2744 | NaN | 439.5855
6303.176 | 466.1594 | NaN | 439.5306
6304.176 | 466.1782 | NaN | 440.2469
6305.176 | 465.8977 | NaN | 440.9478
6306.176 | 465.695 | NaN | 441.3291
6307.176 | 465.6026 | NaN | 440.8517
6308.176 | 465.7078 | NaN | 440.4266
6309.176 | 465.796 | NaN | 440.1894
6310.176 | 465.8825 | NaN | 439.7354
6311.176 | 466.126 | NaN | 439.2329
6312.176 | 466.0068 | NaN | 438.6202
6313.176 | 465.9474 | NaN | 438.4667
6314.176 | 465.7438 | NaN | 439.3468
6315.176 | 465.6725 | NaN | 439.5893
6316.176 | 465.2827 | NaN | 439.6487
6317.176 | 465.1005 | NaN | 439.3261
6318.176 | 465.3457 | NaN | 438.9352
6319.176 | 465.2388 | NaN | 438.7138
6320.176 | 464.9726 | NaN | 438.5338
6321.176 | 464.7818 | NaN | 438.4697
6322.176 | 464.5727 | NaN | 438.6485
6323.176 | 464.6 | NaN | 439.4766
6324.176 | 464.5078 | NaN | 439.6737
6325.176 | 464.2017 | NaN | 440.0981
6326.1917 | 463.9135 | NaN | 439.8417
6327.176 | 463.688 | NaN | 439.46
6328.176 | 463.6706 | NaN | 439.0444
6329.176 | 463.5342 | NaN | 439.079
6330.176 | 463.464 | NaN | 439.3417
6331.176 | 463.4105 | NaN | 439.1895
6332.176 | 463.3556 | NaN | 438.8964
6333.176 | 463.6128 | NaN | 439.6469
6334.176 | 463.6845 | NaN | 439.659
6335.176 | 463.5142 | NaN | 440.216
6336.176 | 463.5043 | NaN | 440.9616
6337.176 | 463.5477 | NaN | 441.5638
6338.176 | 463.2072 | NaN | 441.2364
6339.176 | 463.2459 | NaN | 440.6733
6340.176 | 463.3006 | NaN | 440.1095
6341.176 | 463.4587 | NaN | 439.8283
6342.176 | 463.3523 | NaN | 439.574
6343.176 | 463.2268 | NaN | 439.5175
6344.176 | 463.2177 | NaN | 439.6138
6345.176 | 462.9842 | NaN | 439.6804
6346.176 | 463.2998 | NaN | 439.8519
6347.176 | 463.1996 | NaN | 439.3817
6348.176 | 462.9283 | NaN | 438.843
6349.176 | 463.2144 | NaN | 438.6898
6350.176 | 463.2421 | NaN | 438.2466
6351.176 | 463.1151 | NaN | 438.4969
6352.176 | 463.1175 | NaN | 438.5742
6353.176 | 463.1727 | NaN | 439.2456
6354.176 | 463.5995 | NaN | 439.3417
6355.176 | 464.1054 | NaN | 439.7539
6356.176 | 464.1962 | NaN | 439.6331
6357.176 | 464.0536 | NaN | 439.4151
6358.176 | 463.8379 | NaN | 439.0003
6359.176 | 463.5367 | NaN | 438.7382
6360.176 | 463.4071 | NaN | 438.1603
6361.176 | 463.2426 | NaN | 438.1716
6362.176 | 463.3917 | NaN | 437.7324
6363.176 | 463.3858 | NaN | 437.328
6364.176 | 463.2529 | NaN | 437.543
6365.176 | 463.1412 | NaN | 437.2726
6366.176 | 462.9842 | NaN | 436.7034
6367.176 | 462.7827 | NaN | 436.9131
6368.176 | 462.4897 | NaN | 436.9469
6369.176 | 462.5049 | NaN | 436.8468
6370.176 | 462.4237 | NaN | 436.7691
6371.176 | 462.3467 | NaN | 436.4187
6372.176 | 462.1412 | NaN | 436.2964
6373.176 | 462.0793 | NaN | 436.4505
6374.176 | 461.8936 | NaN | 436.5913
6375.176 | 461.6781 | NaN | 436.277
6376.176 | 461.6755 | NaN | 435.9698
6377.176 | 461.6236 | NaN | 435.6958
6378.176 | 461.3157 | NaN | 436.0107
6379.176 | 461.2823 | NaN | 436.4474
6380.176 | 461.5091 | NaN | 437.0989
6381.176 | 461.4035 | NaN | 437.355
6382.176 | 461.5354 | NaN | 437.7866
6383.176 | 461.9508 | NaN | 438.0093
6384.176 | 462.2246 | NaN | 438.2104
6385.176 | 462.3122 | NaN | 438.3398
6386.176 | 462.1619 | NaN | 437.8607
6387.176 | 462.2719 | NaN | 437.2686
6388.176 | 462.1249 | NaN | 437.2565
6389.176 | 462.048 | NaN | 437.5545
6390.176 | 461.9228 | NaN | 437.4752
6391.176 | 461.4932 | NaN | 436.842
6392.176 | 461.3601 | NaN | 436.186
6393.176 | 461.2636 | NaN | 436.4661
6394.176 | 461.1762 | NaN | 436.475
6395.176 | 461.1646 | NaN | 436.1599
6396.176 | 461.0019 | NaN | 436.1686
6397.176 | 460.9431 | NaN | 435.7935
6398.176 | 460.9474 | NaN | 435.5645
6399.176 | 460.9251 | NaN | 435.7416
6400.176 | 460.85 | NaN | 435.6295
6401.176 | 460.77 | NaN | 435.7166
6402.176 | 460.6956 | NaN | 435.8097
6403.176 | 460.4514 | NaN | 435.8265
6404.176 | 460.3108 | NaN | 435.8062
6405.176 | 459.9726 | NaN | 435.6071
6406.176 | 459.7407 | NaN | 435.3312
6407.176 | 459.8788 | NaN | 435.0586
6408.176 | 459.9698 | NaN | 435.2143
6409.176 | 459.9606 | NaN | 434.9407
6410.176 | 459.9946 | NaN | 434.7692
6411.176 | 460.0853 | NaN | 434.7163
6412.176 | 460.4013 | NaN | 434.9991
6413.176 | 460.656 | NaN | 435.4287
6414.176 | 460.6924 | NaN | 435.9929
6415.176 | 460.6772 | NaN | 435.776
6416.176 | 460.5905 | NaN | 435.5736
6417.176 | 460.532 | NaN | 435.1759
6418.176 | 460.7113 | NaN | 434.785
6419.176 | 460.7102 | NaN | 435.388
6420.176 | 460.5561 | NaN | 435.3905
6421.176 | 460.2813 | NaN | 434.9232
6422.176 | 460.2177 | NaN | 434.6587
6423.176 | 460.413 | NaN | 434.8588
6424.176 | 460.5025 | NaN | 434.4975
6425.176 | 460.3684 | NaN | 434.1954
6426.176 | 460.4135 | NaN | 434.5325
6427.176 | 460.3634 | NaN | 434.7325
6428.176 | 460.6227 | NaN | 434.2045
6429.176 | 460.5094 | NaN | 433.8125
6430.176 | 460.4306 | NaN | 433.7533
6431.176 | 460.5115 | NaN | 433.3835
6432.176 | 460.5661 | NaN | 432.8603
6433.176 | 460.5076 | NaN | 432.4352
6434.176 | 460.2896 | NaN | 432.3758
6435.176 | 460.0232 | NaN | 432.737
6436.176 | 459.8914 | NaN | 433.0768
6437.176 | 459.9326 | NaN | 432.98
6438.176 | 459.9644 | NaN | 433.5889
6439.176 | 459.9358 | NaN | 433.5225
6440.176 | 459.9324 | NaN | 433.3017
6441.176 | 459.8216 | NaN | 433.0808
6442.176 | 459.7731 | NaN | 432.7136
6443.176 | 459.8781 | NaN | 432.8442
6444.176 | 459.8749 | NaN | 433.0319
6445.176 | 459.7791 | NaN | 433.4881
6446.176 | 459.7753 | NaN | 433.8851
6447.176 | 459.8358 | NaN | 433.7445
6448.176 | 459.7226 | NaN | 433.4293
6449.176 | 459.6359 | NaN | 433.0341
6450.176 | 459.5662 | NaN | 432.7999
6451.176 | 459.5623 | NaN | 432.3292
6452.176 | 459.5405 | NaN | 432.1221
6453.176 | 459.5848 | NaN | 432.4453
6454.176 | 459.5848 | NaN | 432.5486
6455.176 | 459.7469 | NaN | 432.8178
6456.176 | 459.7232 | NaN | 433.2305
6457.176 | 459.6614 | NaN | 433.1658
6458.176 | 459.5492 | NaN | 433.2272
6459.176 | 459.7661 | NaN | 432.8597
6460.176 | 459.9523 | NaN | 432.8355
6461.176 | 460.328 | NaN | 432.5246
6462.176 | 460.5143 | NaN | 432.2706
6463.176 | 460.4454 | NaN | 432.7085
6464.176 | 460.2141 | NaN | 432.2987
6465.176 | 459.7837 | NaN | 432.7345
6466.176 | 459.715 | NaN | 432.8344
6467.176 | 459.8761 | NaN | 433.5421
6468.176 | 459.9522 | NaN | 433
6469.176 | 459.7018 | NaN | 432.8164
6470.176 | 459.372 | NaN | 433.4319
6471.176 | 459.3303 | NaN | 432.8986
6472.176 | 459.121 | NaN | 432.5905
6473.176 | 458.8854 | NaN | 432.6216
6474.176 | 458.6151 | NaN | 432.6749
6475.176 | 458.4959 | NaN | 432.6714
6476.1917 | 458.2898 | NaN | 432.8426
6477.176 | 457.8327 | NaN | 433.2358
6478.176 | 457.799 | NaN | 434.2462
6479.176 | 457.6282 | NaN | 434.2338
6480.176 | 457.3367 | NaN | 434.2218
6481.176 | 457.0482 | NaN | 434.2645
6482.176 | 457.0779 | NaN | 434.1179
6483.176 | 457.604 | NaN | 433.8957
6484.176 | 457.9173 | NaN | 434.0127
6485.176 | 458.33 | NaN | 434.0288
6486.176 | 458.4952 | NaN | 433.8594
6487.176 | 458.4938 | NaN | 434.0832
6488.176 | 458.214 | NaN | 433.9355
6489.176 | 458.1598 | NaN | 434.2463
6490.176 | 457.9563 | NaN | 434.12
6491.176 | 457.6777 | NaN | 433.9561
6492.176 | 457.3844 | NaN | 433.7587
6493.176 | 457.3468 | NaN | 433.6995
6494.176 | 457.3958 | NaN | 433.1038
6495.176 | 457.6758 | NaN | 433.273
6496.176 | 457.7377 | NaN | 433.165
6497.176 | 457.7062 | NaN | 432.6606
6498.176 | 457.8892 | NaN | 432.5203
6499.176 | 457.8912 | NaN | 432.4644
6500.176 | 457.7935 | NaN | 432.5403
6501.176 | 457.5471 | NaN | 432.1243
6502.176 | 457.457 | NaN | 431.5724
6503.176 | 457.4937 | NaN | 431.4023
6504.176 | 457.3861 | NaN | 430.6846
6505.176 | 457.5996 | NaN | 430.7287
6506.176 | 457.5736 | NaN | 430.984
6507.176 | 457.5264 | NaN | 430.876
6508.176 | 457.3741 | NaN | 431.5546
6509.176 | 457.1124 | NaN | 431.4637
6510.176 | 457.0864 | NaN | 431.1418
6511.176 | 456.7486 | NaN | 431.1608
6512.176 | 456.5331 | NaN | 430.811
6513.176 | 456.2837 | NaN | 430.7743
6514.176 | 456.3063 | NaN | 430.8487
6515.176 | 456.2546 | NaN | 430.4987
6516.176 | 456.1501 | NaN | 430.9297
6517.176 | 456.1349 | NaN | 431.2427
6518.176 | 456.2249 | NaN | 430.8947
6519.176 | 456.3399 | NaN | 431.162
6520.176 | 456.2804 | NaN | 430.8185
6521.176 | 456.148 | NaN | 430.4146
6522.176 | 455.9843 | NaN | 429.9323
6523.176 | 455.9274 | NaN | 429.3829
6524.176 | 455.9737 | NaN | 428.8312
6525.176 | 456.0287 | NaN | 428.258
6526.176 | 455.8832 | NaN | 428.8822
6527.176 | 455.654 | NaN | 428.8122
6528.176 | 455.5149 | NaN | 428.6465
6529.176 | 455.573 | NaN | 428.7565
6530.176 | 455.5906 | NaN | 429.2629
6531.176 | 455.2365 | NaN | 429.3679
6532.176 | 455.1014 | NaN | 429.2546
6533.176 | 455.1357 | NaN | 429.3416
6534.176 | 455.0532 | NaN | 429.3602
6535.176 | 455.014 | NaN | 429.6162
6536.176 | 454.9516 | NaN | 429.3978
6537.176 | 455.0511 | NaN | 429.2346
6538.176 | 454.9809 | NaN | 429.8844
6539.176 | 454.8922 | NaN | 429.7353
6540.176 | 454.7913 | NaN | 430.0233
6541.176 | 454.6392 | NaN | 430.7567
6542.176 | 454.2581 | NaN | 430.6371
6543.176 | 454.0887 | NaN | 430.3224
6544.176 | 454.0046 | NaN | 429.9627
6545.176 | 453.7486 | NaN | 429.2363
6546.176 | 453.7681 | NaN | 428.9693
6547.176 | 453.9131 | NaN | 430.1943
6548.176 | 454.0209 | NaN | 430.1651
6549.176 | 453.7677 | NaN | 430.614
6550.176 | 453.4407 | NaN | 430.2367
6551.176 | 453.2432 | NaN | 430.5657
6552.176 | 453.2102 | NaN | 430.5997
6553.176 | 452.9602 | NaN | 430.3838
6554.176 | 453.0908 | NaN | 430.6622
6555.176 | 453.2798 | NaN | 430.6076
6556.176 | 453.3858 | NaN | 430.6072
6557.176 | 453.3169 | NaN | 430.1681
6558.176 | 453.5124 | NaN | 430.0186
6559.176 | 453.5807 | NaN | 430.0351
6560.176 | 453.7284 | NaN | 429.6846
6561.176 | 453.9102 | NaN | 429.5137
6562.176 | 453.9994 | NaN | 429.9908
6563.176 | 453.7671 | NaN | 430.1177
6564.176 | 453.9073 | NaN | 430.6851
6565.176 | 453.9205 | NaN | 430.4268
6566.176 | 454.0636 | NaN | 430.3154
6567.176 | 454.0865 | NaN | 430.27
6568.176 | 453.9942 | NaN | 430.287
6569.176 | 453.9553 | NaN | 430.4199
6570.176 | 453.979 | NaN | 430.1348
6571.176 | 453.9561 | NaN | 429.5975
6572.176 | 453.7599 | NaN | 429.4719
6573.176 | 453.5295 | NaN | 429.3881
6574.176 | 453.7568 | NaN | 429.4659
6575.176 | 453.9828 | NaN | 429.2404
6576.176 | 453.8185 | NaN | 428.7712
6577.176 | 453.7461 | NaN | 428.7718
6578.176 | 453.2644 | NaN | 428.5325
6579.176 | 453.066 | NaN | 428.6243
6580.176 | 452.9666 | NaN | 429.0595
6581.176 | 452.8685 | NaN | 429.5897
6582.176 | 452.6598 | NaN | 429.4665
6583.176 | 452.6804 | NaN | 429.0935
6584.176 | 452.4691 | NaN | 429.8251
6585.176 | 452.1715 | NaN | 429.8969
6586.176 | 452.1269 | NaN | 429.7741
6587.176 | 451.8156 | NaN | 429.3
6588.176 | 451.8565 | NaN | 428.4964
6589.176 | 451.8236 | NaN | 428.4613
6590.176 | 451.9268 | NaN | 428.0361
6591.176 | 452.3376 | NaN | 427.7448
6592.176 | 452.4215 | NaN | 427.6892
6593.176 | 452.5429 | NaN | 427.9125
6594.176 | 452.6471 | NaN | 427.5294
6595.176 | 452.8274 | NaN | 427.3457
6596.176 | 453.2065 | NaN | 427.8216
6597.176 | 453.3854 | NaN | 427.6703
6598.176 | 453.5077 | NaN | 427.6019
6599.176 | 453.6058 | NaN | 427.1821
6600.176 | 453.7837 | NaN | 427.1442
6601.176 | 453.7598 | NaN | 426.6674
6602.176 | 453.7776 | NaN | 426.1217
6603.176 | 453.7788 | NaN | 425.6078
6604.176 | 453.8002 | NaN | 425.9128
6605.176 | 453.7869 | NaN | 426.8925
6606.176 | 453.7984 | NaN | 427.0677
6607.176 | 453.7949 | NaN | 427.1772
6608.176 | 453.4735 | NaN | 426.6825
6609.176 | 453.1872 | NaN | 426.2719
6610.176 | 452.8991 | NaN | 426.3589
6611.176 | 452.5734 | NaN | 427.1811
6612.176 | 452.4023 | NaN | 427.2213
6613.176 | 452.6038 | NaN | 427.1098
6614.176 | 452.5997 | NaN | 427.2797
6615.176 | 452.8452 | NaN | 426.7421
6616.176 | 452.8703 | NaN | 426.8903
6617.176 | 452.8133 | NaN | 427.4646
6618.176 | 452.5196 | NaN | 427.1834
6619.176 | 452.659 | NaN | 426.4823
6620.176 | 452.6321 | NaN | 426.3596
6621.176 | 452.417 | NaN | 426.2073
6622.176 | 452.4675 | NaN | 425.8722
6623.176 | 452.2709 | NaN | 425.394
6624.176 | 452.6704 | NaN | 424.7539
6625.176 | 452.8155 | NaN | 424.8161
6626.176 | 452.8666 | NaN | 424.8079
6627.176 | 452.6263 | NaN | 424.8672
6628.176 | 452.8385 | NaN | 424.5927
6629.176 | 452.8651 | NaN | 424.4301
6630.176 | 452.8868 | NaN | 424.5955
6631.176 | 452.5384 | NaN | 424.179
6632.176 | 452.5123 | NaN | 424.2843
6633.176 | 452.6144 | NaN | 424.3846
6634.176 | 452.6853 | NaN | 425.2011
6635.176 | 452.6953 | NaN | 426.1035
6636.176 | 452.6549 | NaN | 425.7842
6637.176 | 452.5021 | NaN | 425.1607
6638.176 | 452.4163 | NaN | 424.6978
6639.176 | 452.2739 | NaN | 424.4002
6640.176 | 452.1565 | NaN | 424.9244
6641.176 | 451.9037 | NaN | 424.8629
6642.176 | 451.8031 | NaN | 424.4456
6643.176 | 451.8824 | NaN | 424.5582
6644.176 | 451.8262 | NaN | 424.7116
6645.176 | 451.7732 | NaN | 424.3404
6646.176 | 452.1454 | NaN | 424.0065
6647.176 | 452.2136 | NaN | 424.0971
6648.176 | 452.0542 | NaN | 423.9897
6649.176 | 451.8552 | NaN | 424.0758
6650.176 | 451.888 | NaN | 424.2509
6651.176 | 452.3149 | NaN | 424.1354
6652.176 | 452.438 | NaN | 423.7062
6653.176 | 452.3974 | NaN | 423.0697
6654.176 | 452.3688 | NaN | 422.8843
6655.176 | 452.4394 | NaN | 422.9753
6656.176 | 452.3854 | NaN | 423.0236
6657.176 | 452.573 | NaN | 423.047
6658.176 | 452.5877 | NaN | 423.1081
6659.176 | 452.2844 | NaN | 423.1128
6660.176 | 452.2108 | NaN | 423.009
6661.176 | 452.1722 | NaN | 423.9423
6662.176 | 451.7638 | NaN | 423.7458
6663.176 | 451.3901 | NaN | 423.443
6664.176 | 451.3856 | NaN | 423.2764
6665.176 | 451.3488 | NaN | 423.4898
6666.176 | 451.6338 | NaN | 423.2081
6667.176 | 451.8195 | NaN | 423.03
6668.176 | 451.716 | NaN | 423.375
6669.176 | 451.5625 | NaN | 423.7028
6670.176 | 451.2516 | NaN | 424.1608
6671.176 | 451.1784 | NaN | 424.3348
6672.176 | 451.2174 | NaN | 424.5061
6673.176 | 451.3386 | NaN | 424.5407
6674.176 | 451.3662 | NaN | 424.5848
6675.176 | 451.4139 | NaN | 424.6088
6676.176 | 451.583 | NaN | 424.8895
6677.176 | 451.6739 | NaN | 425.2464
6678.176 | 451.6915 | NaN | 425.2853
6679.176 | 451.4793 | NaN | 425.5994
6680.176 | 451.4151 | NaN | 425.5003
6681.176 | 451.3429 | NaN | 424.7522
6682.176 | 451.3931 | NaN | 424.025
6683.176 | 451.4868 | NaN | 424.3708
6684.176 | 451.7944 | NaN | 424.4976
6685.176 | 451.8249 | NaN | 424.0582
6686.176 | 451.7591 | NaN | 423.3333
6687.176 | 451.5314 | NaN | 423.6889
6688.176 | 451.3469 | NaN | 423.6581
6689.176 | 451.0994 | NaN | 423.3149
6690.176 | 450.8537 | NaN | 422.8569
6691.176 | 450.7905 | NaN | 422.3941
6692.176 | 450.4972 | NaN | 422.7087
6693.176 | 450.3022 | NaN | 423.3261
6694.176 | 450.1944 | NaN | 423.8862
6695.176 | 450.1377 | NaN | 423.2833
6696.176 | 450.2473 | NaN | 422.9705
6697.176 | 450.2575 | NaN | 423.4753
6698.176 | 450.257 | NaN | 423.5042
6699.176 | 450.0436 | NaN | 423.1147
6700.176 | 450.0908 | NaN | 422.5683
6701.176 | 450.2018 | NaN | 422.3987
6702.176 | 450.226 | NaN | 422.2599
6703.176 | 450.4792 | NaN | 421.9265
6704.176 | 450.7235 | NaN | 421.4614
6705.176 | 450.6563 | NaN | 421.4133
6706.176 | 450.4906 | NaN | 421.0611
6707.176 | 450.5742 | NaN | 420.8409
6708.176 | 450.6779 | NaN | 421.3555
6709.176 | 450.8665 | NaN | 421.1789
6710.176 | 450.984 | NaN | 421.0773
6711.176 | 451.0529 | NaN | 421.6202
6712.176 | 450.8742 | NaN | 421.5114
6713.176 | 450.7151 | NaN | 422.2583
6714.176 | 450.6057 | NaN | 422.9172
6715.176 | 450.3479 | NaN | 423.7456
6716.1917 | 450.0327 | NaN | 423.7455
6717.176 | 450.2996 | NaN | 423.8552
6718.176 | 450.3835 | NaN | 423.7216
6719.176 | 450.4571 | NaN | 423.4791
6720.176 | 450.3817 | NaN | 423.1581